## version control
version number | use / purpose | date | changes made
Template CBA RIIO ED1 v1.xls | initial draft RIIO-GD1 model issued for demo purposes |  | -
Template CBA RIIO ED1 v2.xls | draft RIIO-ED1 model demonstrated during the CBA meeting held on the 19 March | 2013-03-19 | updated the model to reflect ED1 rather than GD1
Template CBA RIIO ED1 v3.xls | issued to DNOs to complete the 2 worked examples (leaking cable and QoS) | 28/03/2013 03/04/2013 | updated to reflect discussions at the CBA meeting including straight line depreciation assumption for ED1, addition of fixed parameter assumptions for non-monetary items re-issued on 3 April to correct CI/CML fixed data transpose error
Template CBA RIIO ED1 v4.xls | final version of CBA spreadsheet to take into account worked examples | 2013-04-16 | updated to reflect DNO feedback following completion of worked examples main changes include: - included baseline scenario worksheet - removed VOLL as CI/CML method of monetising loss of supply was viewed as robust method - amended the CO2 conversion factor associated with losses to take into account assumptions regarding future decarbonisation of electricity - updated fixed data parameters to 2012/13 prices
|  | 2013-04-29 | removed 'do minimum' text in cell B9 of Option summary worksheet
|  | 2014-01-10 | Inserted clarification comment in cell C9 of the Option 1 worksheet.
|  | 2014-01-10 | Clarified text in cell B1 of Option summary worksheet.
|  | 2014-01-10 | Clarified text in cell F26 of Option summary worksheet.

## Guidance
Guidance for CBA spreadsheet model
Tab | Instructions
Option summary | Provide a description of the stated aim / investment decision contained within this CBA analysis workbook, along with a list of options considered to meet the aim. Also include here the short list of options contained within this workbook which have been fully costed and specify which option has been adopted following CBA and included in your business plan submission.
Fixed data | Enter pre-tax WACC and prices consistent with your business plan
Baseline scenario | Enter costs and benefits associated with the baseline scenario. The baseline scenario represents status quo; that is the cost of business as usual in the absence of any investment intervention. Where business as usual is not an option i.e. an investment intervention of some kind is required DNOs should chose the option with the lowest investment to represent the baseline scenario.
Working baseline | Show any calculation used to derive the values in your baseline scenario
Option 1 | Enter costs and benefits over and above the baseline scenario i.e. the marginal or incremental costs / benefits of the option being considered. Enter capitalisation rates consistent with your business plan.
Working 1 | Show any calculation used to derive the values in your CBA
Colour code:
User populated cells
Fixed data
Summation formula
Other formula
The user should populate the light blue cells. All other cells are either fixed or auto-populated.
Enter costs / benefits in 2012/13 prices (£m).
Costs should be entered as negative values.
Benefits (i.e. avoided costs) should be entered a positive values.
Costs entered should correspond to values set out in company business plans i.e. should exclude RPEs and include ongoing efficiencies consistent with assumptions contained in your business plan submission.
Copy Option 1 worksheet & workings 1 for each CBA option and label these option 2 & workings 2 etc.
Where a 'do minimum option' exists, Option 1 should represent your 'do minimum' or 'reference scenario' e.g. do nothing, ongoing maintenance of existing asset or the option which requires the minimum investment .
Use the relevant Workings worksheet to demonstrate any calculation/information that can support the costs and benefits you have entered for each option. This is free fill and provides you with an opportunity to show additional underlying data you believe will assist Ofgem in evaluating/understanding your CBA.
Please highlight your chosen option by colouring the worksheet tab yellow.

## Option summary
Purpose of CBA: describe the primary driver of the investment decision | [9 empty] | Adopted
Live Line Harvester: Harvester is able to cut down trees adjacent to live lines without the need for an outage, thus reducing customer outages. | [9 empty] | Rejected
If investment is to replace an existing asset / asset class, please state the condition of the asset / asset class (HI / CI etc.)
List below all options considered to meet the stated aim
Options considered / project name |  | Comment
Option 1 (Baseline) |  | Do Nothing Scenario. Normal tree cutting operations take place here by third parties. Generation and associated CI / CML costs have been included
Option 2 |  | Currently one hired live line tree cutter makes up the costs. Benefits are the reduction in diesel generation along with associated CI CML costs of generation activities.
List below the short list of those options which have been costed within this CBA workbook
Option no. | Options considered | Decision | Comment | For the chosen option only, provide detail of where CBA expenditure included in this CBA is reported in the BPDT pack. e.g. LV swtichgear BPDT CV3 rows 15 to 22. | NPVs based on payback periods
[5 empty] | 16 years | 24 years | 32 years | 45 years | DNO view
1 | Baseline Contractors & Hand Felling Harvesting | Rejected |  |  | -6.9495 | -7.3929 | -7.6885 | -7.9907
2 | Live Line Tree Harvesting | Adopted |  |  | -1.3147 | -1.5686 | -1.7377 | -1.9106
3
4
5
6
7
8
If more options are costed, please copy Option 1 and workings 1 worksheets and add detail to the short list table above.

## Fixed data
Parameters |  |  |  | Prices
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52
pre-tax WACC | 4% | enter DNO specific pre-tax WACC figure |  |  | 2012/13 prices | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067
Discount Rate <= 30 years | 3.5% |  |  | Traded carbon price (£/t 2010/11)1 |  | 6.76 | 7.1 | 7.55 | 8.03 | 8.55 | 15.26 | 21.97 | 28.68 | 35.39 | 42.1 | 48.81 | 55.52 | 62.23 | 68.94 | 75.65 | 81 | 88 | 95 | 102 | 109 | 116 | 122 | 129 | 136 | 143 | 150 | 157 | 164 | 171 | 178 | 184 | 191 | 198 | 205 | 212 | 220 | 227 | 234 | 241 | 248 | 256 | 262 | 269 | 276 | 282 | 287 | 292 | 297 | 301 | 305 | 309 | 312
Discount Rate > 30 years | 3% |  |  | traded carbon price (£/t 2012/13 prices) |  | 7.3032 | 7.6706 | 8.1567 | 8.6753 | 9.2371 | 16.4863 | 23.7356 | 30.9848 | 38.234 | 45.4832 | 52.7325 | 59.9817 | 67.2309 | 74.4802 | 81.7294 | 87.5093 | 95.0719 | 102.6344 | 110.1969 | 117.7595 | 125.322 | 131.8042 | 139.3667 | 146.9292 | 154.4918 | 162.0543 | 169.6168 | 177.1794 | 184.7419 | 192.3044 | 198.7866 | 206.3492 | 213.9117 | 221.4742 | 229.0368 | 237.6797 | 245.2422 | 252.8047 | 260.3673 | 267.9298 | 276.5727 | 283.0549 | 290.6174 | 298.1799 | 304.6621 | 310.0639 | 315.4657 | 320.8675 | 325.189 | 329.5104 | 333.8319 | 337.073
Discount rate for safety | 1.5% |  |  | Losses (£/MWh) | 48.4213
Assumed Asset Life (Years) | 45 |  |  | CI (£s per interruption) | 15.4435
|  |  |  | CML (£s per minute lost) | 0.37667
|  |  |  | Cost per fatality (£m)2 | 1.7925
|  |  |  | Cost per major injury (£m)2 | 0.027488
RPI INDICES |  |  |  | Cost per litre oil (£/litre) | 36.0814
Using yearly averages (April to March) |  |  |  | Electricity GHG conversion factor (tonnes per MWh)3 |  | 0.50285 | 0.48835 | 0.47386 | 0.45936 | 0.44487 | 0.43037 | 0.41587 | 0.40138 | 0.38688 | 0.37239 | 0.35789 | 0.3434 | 0.3289 | 0.31441 | 0.29991 | 0.28541 | 0.27092 | 0.25642 | 0.24193 | 0.22743 | 0.21294 | 0.19844 | 0.18395 | 0.16945 | 0.15496 | 0.14046 | 0.12596 | 0.11147 | 0.096973 | 0.082478 | 0.067982 | 0.053487 | 0.038991 | 0.024496 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Index |  | convert to
2012/13
Convert from | 2003/04 | 1.3409 |  | 1 https://www.gov.uk/carbon-valuation |  | 2 2017: note: 2016 to 2030 DECC's updated traded sector carbon values published Oct 2012, 2031 onwards based on DECC carbon values published Oct 2011.
| 2004/05 | 1.3004 |  | 2 http://www.hse.gov.uk/risk/theory/alarpcheck.htm |  | 2 2017: note: HSE values as at Q3 2003
| 2005/06 | 1.267 |  | 3 http://www.defra.gov.uk/publications/2012/05/30/pb13773-2012-ghg-conversion/ |  | 2 2017: note: figures taken from 2012 Guideline to Defra / DECC's GHG conversion factors for company reporting, 'new 2010' factor annex 3 table 3(c).
| 2006/07 | 1.2214
| 2007/08 | 1.173 |  |  | FALSE
| 2008/09 | 1.1392
| 2009/10 | 1.134
| 2010/11 | 1.0804
| 2011/12 | 1.0309
| 2012/13 | 1
Decarbonisation of electricity assumption:
Power sector emissions are anticipated to reduce to 10g/kWh by 2050
assume a linear decarbonisation pathway from 2009/10 until 2050
Power sector emissions reduce by 14.5 g/kWh p.a. between now and 2030.
Beyond 2050 keep emissions at 10g/kWh
g CO2e per kWh
1,000 kg = 1 tonne | 2009/10 | 589.82 | (Defra)
1,000 kWh = 1 MWh | 2010/11 | 575.3245
1 kg = 1,000g | 2011/12 | 560.829
| 2012/13 | 546.3335
| 2013/14 | 531.838
| 2014/15 | 517.3425
| 2015/16 | 502.847
| 2016/17 | 488.3515
| 2017/18 | 473.856
| 2018/19 | 459.3605
| 2019/20 | 444.865
| 2012/21 | 430.3695
| 2021/22 | 415.874
| 2022/23 | 401.3785
| 2023/24 | 386.883
| 2024/25 | 372.3875
| 2025/26 | 357.892
| 2026/27 | 343.3965
| 2027/28 | 328.901
| 2028/29 | 314.4055
| 2029/30 | 299.91
| 2030/31 | 285.4145
| 2031/32 | 270.919
| 2032/33 | 256.4235
| 2033/34 | 241.928
| 2034/35 | 227.4325
| 2035/36 | 212.937
| 2036/37 | 198.4415
| 2037/38 | 183.946
| 2038/39 | 169.4505
| 2039/40 | 154.955
| 2040/41 | 140.4595
| 2041/42 | 125.964
| 2042/43 | 111.4685
| 2043/44 | 96.973
| 2044/45 | 82.4775
| 2045/46 | 67.982
| 2046/47 | 53.4865
| 2047/48 | 38.991
| 2048/49 | 24.4955
| 2049/50 | 10
| check | 10 | assumption; power sector should reduce to 10 g CO2e/kWh
|  | 14.4955 | p.a. reduction in carbon intensity
Exclude societal benefits

## Workings baseline 2015.16
Workings / assumptions used for costing Baseline | [15 empty] | Days to geny trip | 55
Use this sheet to provide details of assumptions and calculation methodology used in CBA model | [10 empty] | Planned Outage |  |  |  |  | Duration of genny trip | 4 | [8 empty] | Unplanned Outage
| BOLD RED = ESTIMATE | [9 empty] | CI |  | 5.58 |  |  | Staff cost | 500 | [8 empty] | CI |  | 11.15
[11 empty] | CHL |  | 7.8 | [12 empty] | CHL |  | 15.6
Live Line Harvesting | [8 empty] | Conventional Harvesting under outage with generation | [15 empty] | System Security Liability
Depot | Wodland name / ref | location | landowner details | date completed | Actual duration of works (days) | Live harvesting costs (contractor) | live harvesting costs (SSE) | Total costs | Customers | Duration of outage | CI's Assumed 2 disconections per customer | CHL's Based on the total estimated time to connect and disconnect generation | Cost of Generation | SSE Staff Cost | CI cost | CHL cost | Likelyhood of genny trip | Likely genny trip staff cost | Likely genny trip CICHL costs | Likely gen trip CI cost | Likely gen trip CHL cost | Number of likely Cis | Number Of likely CHL's | Total cost of generation | Customers Potentially Affected outside of outage area (number) | Estimated ERTS (Hours) based on access and staff coverage | Customer hours lost if fault occurs | CI cost | CHL cost | Total potential cost | Likelyhood | Number of likely CIs | Number of likely CHLs | Potential Cost vs likelyhood | Likely CI Cost | Likely CHL Cost | Potential total cost under generation | Potential saving
Argyll | Tarbert | Tarbert |  | 2015-05-08 | 5 | 10450 | 1305 | 11755 | 24 | 4 | 48 | 192 | 2685.7143 | 3244 | 267.84 | 1497.6 | 7.273% | 36.3636 | 128.3782 | 19.4618 | 108.9164 | 1.7455 | 6.9818 | 7859.8961 | 1839 | 4 | 7356 | 20504.85 | 114753.6 | 135258.45 | 5% | 91.95 | 367.8 | 6762.9225 | 1025.2425 | 5737.68 | 14622.8186 | 2867.8186
Argyll | Greenland CC1 | Cambeltown | Egger | 2015-05-22 | 7 | 8500 | 1827 | 10327 | 40 | 6 | 80 | 240 | 12955.3129 | 3094 | 446.4 | 1872 | 10.91% | 54.5455 | 320.9455 | 48.6545 | 272.2909 | 4.3636 | 17.4545 | 18743.2038 | 4811 | 6 | 28866 | 53642.65 | 450309.6 | 503952.25 | 5% | 240.55 | 1443.3 | 25197.6125 | 2682.1325 | 22515.48 | 43940.8163 | 33613.8163
Argyll | Greenland CC2 | Cambeltown | Egger | 2015-05-22 | 5 | 10000 | 1305 | 11305 | 0 | 0 | 0 | 0 | 0 | 2106 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 2106 | 4851 | 4 | 19404 | 54088.65 | 302702.4 | 356791.05 | 5% | 242.55 | 970.2 | 17839.5525 | 2704.4325 | 15135.12 | 19945.5525 | 8640.5525
Higland | Trinloist | Errogie | Forestry Commission | 2015-07-01 | 25 | 37500 | 6525 | 44025 | 34 | 21 | 68 | 34 | 41079.0863 | 7988 | 379.44 | 265.2 | 38.18% | 190.9091 | 954.8127 | 144.7473 | 810.0655 | 12.9818 | 51.9273 | 50857.4481 | 940 | 4 | 3760 | 10481 | 58656 | 69137 | 5% | 47 | 188 | 3456.85 | 524.05 | 2932.8 | 54314.2981 | 10289.2981
Argyll | Broadford Hospital | Skye | HIE | 2015-08-07 | 15 | 22500 | 3915 | 26415 | 89 | 14 | 178 | 356 | 59884.3529 | 5044 | 993.24 | 2776.8 | 25.45% | 127.2727 | 1666.2418 | 252.5982 | 1413.6436 | 22.6545 | 90.6182 | 70491.9075 | 89 | 8 | 712 | 992.35 | 11107.2 | 12099.55 | 5% | 4.45 | 35.6 | 604.9775 | 49.6175 | 555.36 | 71096.885 | 44681.885
Argyll | Ardchyline | Strachur | Scottish Woodlands | 2015-09-04 | 4 | 9300 | 1044 | 10344 | 118 | 5 | 236 | 708 | 10618.9916 | 3060 | 1316.88 | 5522.4 | 9.091% | 45.4545 | 788.9909 | 119.6091 | 669.3818 | 10.7273 | 42.9091 | 21352.7171 | 1350 | 5 | 6750 | 15052.5 | 40500 | 55552.5 | 5% | 67.5 | 337.5 | 2777.625 | 752.625 | 2025 | 24130.3421 | 13786.3421
Argyll | Pennyghael | Isle of Mull | Tilhill | 2015-09-11 | 4 | 12600 | 1044 | 13644 | 610 | 3 | 1220 | 4880 | 17784 | 3244 | 6807.6 | 38064 | 5.455% | 27.2727 | 2447.2091 | 370.9909 | 2076.2182 | 33.2727 | 133.0909 | 68374.0818 | 610 | 8 | 4880 | 6801.5 | 29280 | 36081.5 | 5% | 30.5 | 244 | 1804.075 | 340.075 | 1464 | 70178.1568 | 56534.1568
Argyll | Fank Cottage | Isle of Mull | Tilhill | 2015-09-18 | 7 | 18300 | 1827 | 20127 | 620 | 5 | 1240 | 2480 | 28572.1429 | 3444 | 6919.2 | 19344 | 9.091% | 45.4545 | 4145.5455 | 628.4545 | 3517.0909 | 56.3636 | 225.4545 | 62470.3429 | 620 | 8 | 4960 | 6913 | 29760 | 36673 | 5% | 31 | 248 | 1833.65 | 345.65 | 1488 | 64303.9929 | 44176.9929
Argyll | Kilfinichan | Isle of Mull | Dixons | 2015-09-25 | 9 | 22100 | 2349 | 24449 | 635 | 10 | 1270 | 2540 | 50180 | 3444 | 7086.6 | 19812 | 18.18% | 90.9091 | 8491.6818 | 1287.3182 | 7204.3636 | 115.4545 | 461.8182 | 89105.1909 | 635 | 8 | 5080 | 7080.25 | 30480 | 37560.25 | 5% | 31.75 | 254 | 1878.0125 | 354.0125 | 1524 | 90983.2034 | 66534.2034
Highland | Strome Carronach | Loch Carron | Tilhill | 2015-10-20 | 4 | 7200 | 1044 | 8244 | 91 | 3 | 130 | 130 | 22819.6155 | 5270 | 725.4 | 1014 | 5.455% | 27.2727 | 365.0755 | 55.3445 | 309.7309 | 4.9636 | 19.8545 | 30221.3636 | 91 | 4 | 364 | 1014.65 | 2184 | 3198.65 | 5% | 4.55 | 18.2 | 159.9325 | 50.7325 | 109.2 | 30381.2961 | 22137.2961
Argyll | Dallinlongart | Strachur | Tilhill | 2015-11-30 | 15 | 22500 | 3915 | 26415 | 22000 | 8 | 22000 | 44000 | 347925.6303 | 20128 | 122760 | 343200 | 14.55% | 72.7273 | 235360 | 35680 | 199680 | 3200 | 12800 | 1069446.3575 | 22000 | 4 | 88000 | 245300 | 528000 | 773300 | 5% | 1100 | 4400 | 38665 | 12265 | 26400 | 1108111.3575 | 1081696.3575
Highland | Kirkton Wood | Loch Carron | Munros timber | 2015-12-15 | 4 | 7500 | 1044 | 8544 | 591 | 1 | 1182 | 591 | 54689 | 5782 | 6595.56 | 4609.8 | 1.818% | 9.0909 | 790.3282 | 119.8118 | 670.5164 | 10.7455 | 42.9818 | 72475.7791 | 63301 | 4 | 253204 | 705806.15 | 1519224 | 2225030.15 | 5% | 3165.05 | 12660.2 | 111251.5075 | 35290.3075 | 75961.2 | 183727.2866 | 175183.2866
Argyll | Glen Douglas | Glen Douglas | Tilhill | 2016-02-26 | 15 | 25000 | 3915 | 28915 | [9 empty] | 0 | [19 empty] | -28915
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[8 empty] | 244509 |  | 80 | 27652 | 56151 | 649193.8466 | 65848 | 154298.16 | 437977.8 |  | 727.2727 | 255459.2091 | 38726.9909 | 216732.2182 | 3473.2727 | 13893.0909 | 1563504.2884 | [5 empty] | 4244634.35 |  | 5056.85 | 21166.8 | 212231.7175 | 56383.8775 | 155847.84 | 1775736.0059 | 1531227.0059
|  |  | No of days completed to date |  | 119 | [6 empty] | Generation total |  | 715769.1193 | [13 empty] | Network Sec Total |  | 4244634.35 |  |  |  | 212231.7175
|  |  | LLH Costs to date |  |  | 213450 | [5 empty] | Average Per day |  | 6014.8665 | [13 empty] | Average per day |  | 35669.1962 |  |  |  | 1783.4598
|  |  | Average costs per day |  |  | 1793.6975
[12 empty] | CI/CHL Total |  |  |  | 847735.1691
[12 empty] | Average per day |  |  |  | 7123.825 | [11 empty] | Number of likely CI's |  | 5056.85
[28 empty] | Number of likely CHL's |  | 21166.8
[12 empty] | Number of generation related CIs |  |  | 3473.2727 | [12 empty] | Cost of likely CI's |  | 56383.8775
| Total Litres of diesel avoided |  | 254127.9233 | *Calculated by dividing cost of diesel per litre (£0.5) from number of litres used per hour per generator | [7 empty] | Number of generation related CHLs |  |  | 13893.0909 | [12 empty] | Cost of likely CHL's |  | 155847.84
| CO2e |  | 2.6761 | *Source: DCF Carbon Calculation Factors 29_9_2015 based on Fuels - Diesel - 100% mineral oil
| Total CO2 Avoided (kg co2e) |  | 680081.9006 | [8 empty] | Total Cost of generation (excluding CI / CMLs) |  |  | 715769.1193
| Total CO2 Avoided (tonnes co2e) |  | 680.0819 | [8 empty] | Total Cost of CIs |  |  | 249409.0284
[12 empty] | Total Cost of CHLs |  |  | 810557.8582
1775736.0059
CBA figures
| Investment: Tree Cutting |  | 715769.1193 | 0.71577
| Customer interruptions (CI) |  | 249409.0284 | 0.24941
| Customer minutes lost (CML) |  | 810557.8582 | 0.81056
| Reduced number of customers interrupted |  | 36182.1227 | 36182.1227
| Reduced customer minutes lost |  | 91210.8909 | 5472653.4545
| Reduced emissions (not associated with losses)1 |  | 680.0819 | 680.0819
Note on R1: Stirling, Graham: Advice from Geny desk. A geny will trip every 50 to 60 days.

## Workings baseline 2016.17
| Workings / assumptions used for costing Baseline | [16 empty] | Days to geny trip | 55
| Use this sheet to provide details of assumptions and calculation methodology used in CBA model | [11 empty] | Planned Outage |  |  |  |  | Duration of genny trip | 4 | [8 empty] | Unplanned Outage
|  | BOLD RED = ESTIMATE | [10 empty] | CI |  | 5.58 |  |  | Staff cost | 500 | [8 empty] | CI |  | 11.15
[13 empty] | CHL |  | 7.8 | [12 empty] | CHL |  | 15.6
[5 empty] | Monthly hire Rate |  |  |  | 24000
[5 empty] | SSE supervisor |  |  |  | 261 | [18 empty] | Likelyhood |  | 5%
[5 empty] | Potential availability (days per year) |  |  |  | 230
[5 empty] | Days unavailable (off hire) |  |  |  | 20
[5 empty] | Months available |  |  |  | 11
| Live Line Harvesting | [9 empty] | Conventional Harvesting under outage with generation | [15 empty] | System Security Liability
Month | Depot | Wodland name / ref | location | landowner details | date completed | Duration | Total days utilised | Utilisation | Machine Costs | Harmony Cost including Fuel, Accomodatiom, Staff costs and Sundries | Customers | Duration of outage | CI's Assumed 2 disconections per customer | CHL's Based on the total estimated time to connect and disconnect generation | Cost of Generation | SSE Staff Cost | CI cost | CHL cost | Likelyhood of genny trip | Likely genny trip staff cost | Number of likely Cis | Number Of likely CHL's | Likely gen trip CI cost | Likely gen trip CHL cost | Likely genny trip CICHL costs | Total cost of generation | Customers Potentially Affected outside of outage area (number) | Estimated ERTS (Hours) based on access and staff coverage | Customer hours lost if fault occurs | CI cost | CHL cost | Total potential cost | Likelyhood | Number of likely CIs | Number of likely CHLs | Potential Cost vs likelyhood | Likely CI Cost | Likely CHL Cost | Potential total cost under generation | Potential saving | Likely total cost under generation | Minimum saving
2016-04-01 | Argyll | Ardmarnock | Loch Ascog | RTS | 2016-04-22 | 18 |  |  | 24000 | 279.5 | 24 | 18 | 48 | 192 | 43582 | 3244 | 267.84 | 1497.6 | 32.73% | 163.6364 | 7.8545 | 31.4182 | 87.5782 | 490.1236 | 577.7018 | 49332.7782 | 500 | 4 | 2000 | 5575 | 31200 | 36775 | 5% | 25 | 100 | 1838.75 | 278.75 | 1560 | 86107.7782 | 49832.9568 | 51171.5282 | 14896.7068
[5 empty] | Planning | 0 | [33 empty] | 0 |  | 0
[5 empty] | Total |  | 18 | 94.29%
2016-05-01 | Off Hire for entire month due to operator and supervisor leave + workshop time. |  |  |  |  | 0 |  |  | 0 | 2103.72 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 5% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Planning | 0 | [33 empty] | 0 |  | 0
[5 empty] | Total |  | 0 | [32 empty] | 0 |  | 0
2016-07-01 | North east | Tillypronnie Estate | Tarland | Tillypronie sawmill |  | 20 |  |  | 24000 | 25118.33 | 8 | 20 | 8 | 32 | 46956.0869 | 26296 | 44.64 | 249.6 | 36.36% | 181.8182 | 2.9091 | 11.6364 | 32.4364 | 181.5273 | 213.9636 | 73942.1087 | 2392 | 4 | 9568 | 26670.8 | 149260.8 | 175931.6 | 5% | 119.6 | 478.4 | 8796.58 | 1333.54 | 7463.04 | 249873.7087 | 209568.3515 | 82738.6887 | -397566.6685
[5 empty] | Planning | 0 | [33 empty] | 0 |  | 0
[5 empty] | Total |  | 20 | 104.8%
2016-08-01 | North east | Tillypronnie Estate | Tarland | Tillypronie Coro' wood | 2016-08-19 | 15 |  |  | 24000 | 17459.27 | 0 | 10 | 0 | 0 | 5000 | 0 | 0 | 0 | 18.18% | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 2392 | 4 | 9568 | 26670.8 | 149260.8 | 175931.6 | 5% | 119.6 | 478.4 | 8796.58 | 1333.54 | 7463.04 | 180931.6 | 150702.5821 | 13796.58 | -16432.4379
| Tayside | Kinniard Village | Kinniard | Willy Laing | 2016-08-26 | 4 |  |  |  |  | 25 | 10 | 50 | 300 | 5402 | 5370 | 279 | 2340 | 18.18% | 90.9091 | 4.5455 | 18.1818 | 50.6818 | 283.6364 | 334.3182 | 13816.2273 | 120 | 4 | 480 | 1338 | 7488 | 8826 | 5% | 6 | 24 | 441.3 | 66.9 | 374.4 | 22642.2273 | 14581.1558 | 14257.5273 | 6196.4558
| Argyll | Achnaba | Achnaba | Scottish Woodlands | 2016-08-31 | 2 |  |  |  |  | 115 | 3 | 230 | 1150 | 16845 | 2440 | 1283.4 | 8970 | 5.455% | 27.2727 | 6.2727 | 25.0909 | 69.9409 | 391.4182 | 461.3591 | 30027.0318 | 6728 | 5 | 33640 | 75017.2 | 524784 | 599801.2 | 5% | 336.4 | 1682 | 29990.06 | 3750.86 | 26239.2 | 629828.2318 | 625797.6961 | 60017.0918 | 55986.5561
[5 empty] | Planning | 0 | [33 empty] | 0 |  | 0
[5 empty] | Total |  | 21 | 110%
2016-09-01 | Perth | Drymen | Gortocharn | Egger | 2016-09-30 | 6 |  |  | 24000 | 4076.39 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5091 | 4 | 20364 | 56764.65 | 317678.4 | 374443.05 | 5% | 254.55 | 1018.2 | 18722.1525 | 2838.2325 | 15883.92 | 374443.05 | 362351.4429 | 18722.1525 | 6630.5454
[5 empty] | Planning | 2 | [33 empty] | -4030.5357 |  | -4030.5357
[5 empty] | Total |  | 8 | 41.9%
2016-10-01 | Argyll | Cnochan A Chorra | Kames | Scottish Woodlands | 2016-10-10 | 5 |  |  | 24000 | 16436.36 | 30 | 8 | 60 | 240 | 71100 | 11560 | 334.8 | 1872 | 14.55% | 72.7273 | 4.3636 | 17.4545 | 48.6545 | 272.2909 | 320.9455 | 85260.4727 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 85260.4727 | 75184.1334 | 85260.4727 | 75184.1334
| Argyll | Kyles View | Glendaruel | Euroforest | 2016-10-26 | 8 |  |  |  |  | 122 | 8 | 244 | 984 | 33557.9337 | 7376 | 1361.52 | 7675.2 | 14.55% | 72.7273 | 17.7455 | 70.9818 | 197.8618 | 1107.3164 | 1305.1782 | 51348.5592 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 51348.5592 | 35226.4163 | 51348.5592 | 35226.4163
[5 empty] | Planning | 4 | [33 empty] | -8061.0714 |  | -8061.0714
[5 empty] | Total |  | 17 | 89.05%
2016-11-01 | Argyll | Hells Glen | Ardno | DSH Woodlands | 2016-11-15 | 12 |  |  | 24000 | 5711.97 | 513 | 10 | 1026 | 4104 | 59268.5714 | 9476 | 5725.08 | 32011.2 | 18.18% | 90.9091 | 93.2727 | 373.0909 | 1039.9909 | 5820.2182 | 6860.2091 | 113431.9696 | 513 | 4 | 2052 | 5719.95 | 32011.2 | 37731.15 | 5% | 25.65 | 102.6 | 1886.5575 | 285.9975 | 1600.56 | 151163.1196 | 126979.9053 | 115318.5271 | 91135.3128
[5 empty] | Planning | 5 | [33 empty] | -10076.3393 |  | -10076.3393
[5 empty] | Total |  | 17 | 89.05% | [17 empty] | 0
2016-12-01 | Tayside | Ardoch | Murthly | Adam Ritchie | 2016-12-21 | 8 |  |  | 24000 | 6101.89 | 6 | 14 | 12 | 96 | 21036.9097 | 5120 | 66.96 | 748.8 | 25.45% | 127.2727 | 1.5273 | 6.1091 | 17.0291 | 95.3018 | 112.3309 | 27212.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 27212.2734 | 11090.1305 | 27212.2734 | 11090.1305
[5 empty] | Planning | 5 | [32 empty] | 0 | -10076.3393 | 0 | -10076.3393
[39 empty] | 0 | 0 | 0 | 0
[7 empty] | 13 | 68.1% | [8 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 5% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
2017-01-01 | Argyll | Littleport | St Fillans | RTS | 2017-01-07 | 4 |  |  | 24000 | 8259.19 | 245 | 12 | 490 | 1960 | 14099.4286 | 7088 | 2734.2 | 15288 | 21.82% | 109.0909 | 53.4545 | 213.8182 | 596.0182 | 3335.5636 | 3931.5818 | 43250.3013 | 845 | 6 | 5070 | 9421.75 | 79092 | 88513.75 | 5% | 42.25 | 253.5 | 4425.6875 | 471.0875 | 3954.6 | 131764.0513 | 123702.9799 | 47675.9888 | 39614.9174
| Tayside | Tiroran | Isle Of Mull | Tilhill | 2017-01-27 | 17 |  |  |  |  | 645 | 14 | 1290 | 5160 | 85888 | 17104 | 7198.2 | 40248 | 25.45% | 127.2727 | 164.1818 | 656.7273 | 1830.6273 | 10244.9455 | 12075.5727 | 162641.0455 | 645 | 6 | 3870 | 7191.75 | 60372 | 67563.75 | 5% | 32.25 | 193.5 | 3378.1875 | 359.5875 | 3018.6 | 230204.7955 | 195945.2419 | 166019.233 | 131759.6794
[39 empty] | 0 | 0 | 0 | 0
[7 empty] | 21 | 110% | [8 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 5% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
2017-02-01 | Highland | Dalchork | Lairg | Forestry Commission | 2017-02-23 | 14 |  |  | 24000 | 13018.38 | 927 | 18 | 0 | 0 | 194420 | 22992 | 0 | 0 | 32.73% | 163.6364 | 303.3818 | 1213.5273 | 3382.7073 | 18931.0255 | 22313.7327 | 239889.3691 | 927 | 8 | 7416 | 10336.05 | 115689.6 | 126025.65 | 5% | 46.35 | 370.8 | 6301.2825 | 516.8025 | 5784.48 | 365915.0191 | 337701.2691 | 246190.6516 | 217976.9016
[5 empty] | Planning | 3 | [26 empty] | 5% | [5 empty] | 0 | -6045.8036 | 0 | -6045.8036
[33 empty] | 5% | [5 empty] | 0 | 0 | 0 | 0
[7 empty] | 17 | 89.05% | [8 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 5% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
2017-03-01 | Highland | Achfarry | Lairg | Euroforest | 2017-03-10 | 11 |  |  | 24000 | [7 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -22167.9464 | 0 | -22167.9464
|  | Shinnach | Strathdon | James Jones | 2017-03-31 | 5 |  |  |  |  | 30 | 5 | 70 | 140 | 36359 | 3100 | 390.6 | 1092 | 9.091% | 45.4545 | 2.7273 | 10.9091 | 30.4091 | 170.1818 | 200.5909 | 41187.6455 | 35 | 2 | 70 | 390.25 | 1092 | 1482.25 | 5% | 1.75 | 3.5 | 74.1125 | 19.5125 | 54.6 | 42669.8955 | 32593.5562 | 41261.758 | 31185.4187
[33 empty] | 5% | [5 empty] | 0 | 0 | 0 | 0
[7 empty] | 16 | 83.81% | [8 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 168 | 88% | 240000 | 98565 |  | 160 | 3528 | 14358 | 633514.9303 | 121166 | 19686.24 | 111992.4 |  | 1272.7273 | 662.2364 | 2648.9455 | 7383.9355 | 41323.5491 | 48707.4845 | 936339.7821 | 20188 |  | 94098 | 225096.2 | 1467928.8 | 1693025 |  | 1009.4 | 4704.9 | 84651.25 | 11254.81 | 73396.44 | 2629364.7821 | 2290799.7821 | 1020991.0321 | 242426.0321
[5 empty] | Machine Days |  |  |  | 168 |  |  |  | Generation total |  |  | 804661.1421 | [13 empty] | Network Sec Total |  | 1693025 |  |  |  | 84651.25
[5 empty] | Total Cost |  |  |  | 338565 |  |  |  | Average Per day |  |  | 5029.1321 | [13 empty] | Average per day |  | 10077.5298 |  |  |  | 503.8765
[5 empty] | Cost per day |  |  |  | 2015.2679
[13 empty] | CI/CHL Total |  |  | 180386.1245
[5 empty] | Total available days per year |  |  |  | 230 |  |  |  | Average per day |  |  | 1127.4133
[5 empty] | Utilisation To Date |  |  |  | 88%
|  | Total Litres of diesel avoided |  | 228353.4651
|  | CO2e |  | 2.6761
|  | Total CO2 Avoided (kg co2e) |  | 611105.8422
|  | Total CO2 Avoided (tonnes co2e) |  | 611.1058
CBA figures
|  | Investment: Tree Cutting |  | 755953.6576 | 0.75595
|  | Customer interruptions (CI) |  | 38324.9855 | 0.038325
|  | Customer minutes lost (CML) |  | 226712.3891 | 0.22671
|  | Reduced number of customers interrupted |  | 5199.6364 | 5199.6364
|  | Reduced customer minutes lost |  | 21711.8455 | 1302710.7273
|  | Reduced emissions (not associated with losses)1 |  | 611.1058 | 611.1058
Note on T1: Stirling, Graham: Advice from Geny desk. A geny will trip every 50 to 60 days.
Note on AQ20: Williams, Rhys (Future Networks): New live line harvester purchased in July
Note on P23: Stirling, Graham: HV set on standby

## Workings baseline 2017.18
|  | Workings / assumptions used for costing Baseline | [16 empty] | Days to geny trip | 55
|  | Use this sheet to provide details of assumptions and calculation methodology used in CBA model | [11 empty] | Planned Outage |  |  |  |  | Duration of genny trip | 4 | [8 empty] | Unplanned Outage
|  |  | BOLD RED = ESTIMATE | [10 empty] | CI |  | 6.01 |  |  | Staff cost | 500 | [8 empty] | CI |  | 12.02
[14 empty] | CHL |  | 8.415 | [12 empty] | CHL |  | 16.83
[6 empty] | Monthly hire Rate |  |  |  | 24000
[6 empty] | SSE supervisor |  |  |  | 261 | [18 empty] | Likelyhood |  | 5%
[6 empty] | Potential availability (days per year) |  |  |  | 500
[6 empty] | Days unavailable (off hire) |  |  |  | 0
[6 empty] | Months available |  |  |  | 12
| Live Line Harvester Costs | [10 empty] | Conventional Harvesting under outage with generation | [15 empty] | System Security Liability
Month | Machine Type | Depot | Woodland name / ref | location | landowner details | date completed | Duration | Total days utilised | Utilisation | Machine Costs | Harmony Cost including Fuel, Accomodatiom, Staff costs and Sundries | Customers | Duration of outage | CI's Assumed 2 disconections per customer | CHL's Based on the total estimated time to connect and disconnect generation | Cost of Generation | SSE Staff Cost | CI cost | CHL cost | Likelyhood of genny trip | Likely genny trip staff cost | Number of likely Cis | Number Of likely CHL's | Likely gen trip CI cost | Likely gen trip CHL cost | Likely genny trip CICHL costs | Total cost of generation | Customers Potentially Affected outside of outage area (number) | Estimated ERTS (Hours) based on access and staff coverage | Customer hours lost if fault occurs | CI cost | CHL cost | Total potential cost | Likelyhood | Number of likely CIs | Number of likely CHLs | Potential Cost vs likelyhood | Likely CI Cost | Likely CHL Cost | Potential total cost under generation | Potential saving | Likely total cost under generation | Minimum saving
April | Contract Harvester | NE | Conerock | Aberlour | Gordons | 2017-05-14 | 6 | 6 | 52.8% | 24000 | 6672.4 | 8 | 3 | 16 | 432 | 3722.736 | 2084 | 96.16 | 3635.28 | 5.455% | 27.2727 | 0.43636 | 1.7455 | 5.2451 | 29.376 | 34.6211 | 9600.0698 | 2472 | 4 | 9888 | 29713.44 | 166415.04 | 196128.48 | 5% | 123.6 | 494.4 | 9806.424 | 1485.672 | 8320.752 | 205728.5498 | 197026.5603 | 19406.4938 | 10704.5043
| Contract Harvester | TW | Balquidder | Balquidder | Tilhill | 2017-04-19 | 2 | 2 |  |  |  | 160 | 3 | 320 | 1920 | 18917.736 | 2900 | 1923.2 | 16156.8 | 5.455% | 27.2727 | 8.7273 | 34.9091 | 104.9018 | 587.52 | 692.4218 | 40617.4305 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 40617.4305 | 37716.7674 | 40617.4305 | 37716.7674
| SSE Harvester | TW | Rannoch | Rannoch Lodge | Tilhill/FCS | 2017-04-30 | 9 | 9 |  |  |  | 120 | 10 | 240 | 1016 | 49890.064 | 10696 | 1442.4 | 8549.64 | 18.18% | 90.9091 | 21.8182 | 87.2727 | 262.2545 | 1468.8 | 1731.0545 | 72400.0676 | 2100 | 8 | 16800 | 25242 | 282744 | 307986 | 5% | 105 | 840 | 15399.3 | 1262.1 | 14137.2 | 380386.0676 | 367333.0834 | 87799.3676 | 74746.3834
| SSE Harvester | Training | Marykirk | Workshop | Treetop Forestry | 2017-04-30 | 5 | 5 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -7251.6579 | 0 | -7251.6579
May | SSE Harvester | TW | Rannoch | Rannoch Lodge | Tilhill/FCS | 2017-05-05 | 4 | 4 | 55.2% | 24000 | 18462.72 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -5801.3263 | 0 | -5801.3263
| SSE Harvester | AS | Kennelhill | Lochgilphead | Egger | 2017-05-31 | 13 | 13 |  |  |  | 115 | 20 | 230 | 1380 | 89664.2656 | 20256 | 1382.3 | 11612.7 | 36.36% | 181.8182 | 41.8182 | 167.2727 | 502.6545 | 2815.2 | 3317.8545 | 126414.9383 | 874 | 6 | 5244 | 10505.48 | 88256.52 | 98762 | 5% | 43.7 | 262.2 | 4938.1 | 525.274 | 4412.826 | 225176.9383 | 206322.6278 | 131353.0383 | 112498.7278
| Contract Harvester | TW | Balquidder | Balquidder | Tilhill | 2017-05-04 | 1 | 1 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -1450.3316 | 0 | -1450.3316
| Contract Harvester | Training | Rannoch | Barracks | Treetop Forestry | 2017-05-20 | 5 | 5 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -7251.6579 | 0 | -7251.6579
June | SSE Harvester | AS | Kennelhill | Lochgilphead | Egger | 2017-06-09 | 7 | 7 | 88.8% | 24000 | 19321.94 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -10152.3211 | 0 | -10152.3211
| SSE Harvester | HI | Ord | Nairn | Tilhill | 2017-06-30 | 15 | 15 |  |  |  | 423 | 15 | 846 | 5076 | 88338.208 | 7388 | 5084.46 | 42714.54 | 27.27% | 136.3636 | 115.3636 | 461.4545 | 1386.6709 | 7766.28 | 9152.9509 | 152814.5225 | 569 | 8 | 4552 | 6839.38 | 76610.16 | 83449.54 | 5% | 28.45 | 227.6 | 4172.477 | 341.969 | 3830.508 | 236264.0625 | 214509.0889 | 156986.9995 | 135232.0259
| Contract Harvester | Training | Rannoch | Barracks | Treetop Forestry | 2017-06-25 | 15 | 15 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -21754.9737 | 0 | -21754.9737
July | SSE Harvester | AS | Argyll | Ormidale | Tilhill | 2017-07-28 | 20 | 20 | 74.4% | 24000 | 22425.29 | 508 | 25 | 1016 | 4064 | 63925 | 8068 | 6106.16 | 34198.56 | 45.45% | 227.2727 | 230.9091 | 923.6364 | 2775.5273 | 15544.8 | 18320.3273 | 130845.32 | 602 | 12 | 7224 | 7236.04 | 121579.92 | 128815.96 | 5% | 30.1 | 361.2 | 6440.798 | 361.802 | 6078.996 | 259661.28 | 230654.6484 | 137286.118 | 108279.4864
| SSE Harvester | HI | Nairn | Balnafoich | Cawdor | 2017-07-31 | 1 | 1 |  |  |  | 62 | 10 | 124 | 496 | 46298.4 | 39480 | 745.24 | 4173.84 | 18.18% | 90.9091 | 11.2727 | 45.0909 | 135.4982 | 758.88 | 894.3782 | 91682.7673 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 91682.7673 | 90232.4357 | 91682.7673 | 90232.4357
| Contract Harvester | Training | Rannoch | Barracks | Treetop Forestry | 2017-07-28 | 10 | 10 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -14503.3158 | 0 | -14503.3158
August | Contract Harvester | HI | Nairn | Balnafoich | Cawdor | 2017-08-11 | 11 | 11 | 81.6% | 24000 | 12310.98 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -15953.6474 | 0 | -15953.6474
| Contract Harvester | AS | Argyll | Ardlamont | Euroforest | 2017-08-18 | 5 | 5 |  |  |  | 30 | 10 | 60 | 360 | 34745.536 | 14344 | 360.6 | 3029.4 | 18.18% | 90.9091 | 5.4545 | 21.8182 | 65.5636 | 367.2 | 432.7636 | 53003.2087 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 53003.2087 | 45751.5508 | 53003.2087 | 45751.5508
| SSE Harvester | Training | Nairn | Balnafoich | Cawdor | 2017-08-31 | 18 | 18 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -26105.9684 | 0 | -26105.9684
September | Contract Harvester | AS | Argyll | Ardlamont | Euroforest | 2017-09-08 | 5 | 5 | 84% | 24000 | 9337.4 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -7251.6579 | 0 | -7251.6579
| Contract Harvester | AS | Argyll | Ormidale | Tilhill | 2017-09-22 | 10 | 10 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -14503.3158 | 0 | -14503.3158
| Contract Harvester | HI | Nairn | Barevan | Gordons | 2017-09-29 | 5 | 5 |  |  |  | 90 | 10 | 180 | 1080 | 64089.12 | 9064 | 1081.8 | 9088.2 | 18.18% | 90.9091 | 16.3636 | 65.4545 | 196.6909 | 1101.6 | 1298.2909 | 84712.32 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 84712.32 | 77460.6621 | 84712.32 | 77460.6621
| SSE Harvester | Training | Nairn | Barevan | Gordons | 2017-09-29 | 15 | 15 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -21754.9737 | 0 | -21754.9737
October | Contract Harvester | NE | Nairn | Barevan | Gordons | 2017-10-06 | 5 | 5 | 48% | 24000 | 20164.38 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -7251.6579 | 0 | -7251.6579
| Contract Harvester | NE | North East | Kildrummy | James Jones | 2017-10-13 | 5 | 5 |  |  |  | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 27.27% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5312 | 12 | 63744 | 63850.24 | 1072811.52 | 1136661.76 | 5% | 265.6 | 3187.2 | 56833.088 | 3192.512 | 53640.576 | 1136661.76 | 1129410.1021 | 56833.088 | 49581.4301
| Contract Harvester | AS | Argyll | Lindsaig | Tilhill | 2017-10-20 | 5 | 5 |  |  |  | 36 | 4 | 72 | 288 | 13985.912 | 2084 | 432.72 | 2423.52 | 7.273% | 36.3636 | 2.6182 | 10.4727 | 31.4705 | 176.256 | 207.7265 | 19170.2422 | 247 | 8 | 1976 | 2968.94 | 33256.08 | 36225.02 | 5% | 12.35 | 98.8 | 1811.251 | 148.447 | 1662.804 | 55395.2622 | 48143.6043 | 20981.4932 | 13729.8353
| Contract Harvester | AS | Argyll | Ardlamont | Scottish Woodlands | 2017-10-27 | 5 | 5 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -7251.6579 | 0 | -7251.6579
| Contract Harvester | TS | Tayside | Inver | Forestry Commission | 2017-10-31 | 2 | 2 |  |  |  | 204 | 15 | 406 | 1632 | 50648.68 | 5916 | 2440.06 | 13733.28 | 27.27% | 136.3636 | 55.6364 | 222.5455 | 668.7491 | 3745.44 | 4414.1891 | 77288.5727 | 328 | 4 | 1312 | 3942.56 | 22080.96 | 26023.52 | 5% | 16.4 | 65.6 | 1301.176 | 197.128 | 1104.048 | 103312.0927 | 100411.4296 | 78589.7487 | 75689.0856
November | Contract Harvester | TS | Tayside | Inver | Forestry Commission | 2017-11-10 | 8 | 8 | 81.6% | 24000 | 12885.99 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -11602.6526 | 0 | -11602.6526
| Contract Harvester | AN | Argyll | Dalmally | Scottish Woodlands | 2017-11-30 | 14 | 14 |  |  |  | 138 | 24 | 276 | 2208 | 71995.1328 | 6432 | 1658.76 | 18580.32 | 43.64% | 218.1818 | 60.2182 | 240.8727 | 723.8225 | 4053.888 | 4777.7105 | 103662.1052 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 103662.1052 | 83357.4631 | 103662.1052 | 83357.4631
| SSE Harvester | Training | Highland | Roy Bridge | Tilhill | 2017-11-30 | 12 | 12 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -17403.9789 | 0 | -17403.9789
December | Contract Harvester | AN | Argyll | Dalmally | Scottish Woodlands | 2017-12-08 | 6 | 6 | 50.4% | 24000 | 14490.63 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -8701.9895 | 0 | -8701.9895
| SSE Harvester | NE | Highland | Roy Bridge | Tilhill | 2017-12-15 | 10 | 10 |  |  |  | 252 | 10 | 504 | 2016 | 57857.296 | 5416 | 3029.04 | 16964.64 | 18.18% | 90.9091 | 45.8182 | 183.2727 | 550.7345 | 3084.48 | 3635.2145 | 86993.0996 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 86993.0996 | 72489.7838 | 86993.0996 | 72489.7838
| Contract Harvester | AN | Argyll | Dalmally 2 | Egger | 2017-12-15 | 5 | 5 |  |  |  | 138 | 8 | 276 | 2208 | 27298.3776 | 4832 | 1658.76 | 18580.32 | 14.55% | 72.7273 | 20.0727 | 80.2909 | 241.2742 | 1351.296 | 1592.5702 | 54034.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 54034.7551 | 46783.0972 | 54034.7551 | 46783.0972
January | Contract Harvester | TS | Tayside | Duncrub | RTS | 2018-01-19 | 13 | 13 | 50.4% | 24000 | 22917.12 | 31 | 10 | 62 | 372 | 31235.472 | 3944 | 372.62 | 3130.38 | 18.18% | 90.9091 | 5.6364 | 22.5455 | 67.7491 | 379.44 | 447.1891 | 39220.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 39220.5702 | 20366.2597 | 39220.5702 | 20366.2597
| Contract Harvester | AS | Argyll | Clachaig | Micheal Swailes | 2018-01-31 | 8 | 8 |  |  |  | 16 | 10 | 32 | 192 | 1889.0944 | 1612 | 192.32 | 1615.68 | 18.18% | 90.9091 | 2.9091 | 11.6364 | 34.9673 | 195.84 | 230.8073 | 5630.8108 | 1774 | 8 | 14192 | 21323.48 | 238851.36 | 260174.84 | 5% | 88.7 | 709.6 | 13008.742 | 1066.174 | 11942.568 | 265805.6508 | 254202.9981 | 18639.5528 | 7036.9001
February | Contract Harvester | AS | Argyll | Clachaig | Micheal Swailes | 2018-02-09 | 7 | 7 | 48% | 24000 | 8031.22 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -10152.3211 | 0 | -10152.3211
| SSE Harvester | AS | Argyll | Rowardennan | Forestry Commission | 2018-02-23 | 10 | 10 |  |  |  | 13 | 10 | 26 | 156 | 29753.648 | 4712 | 156.26 | 1312.74 | 18.18% | 90.9091 | 2.3636 | 9.4545 | 28.4109 | 159.12 | 187.5309 | 36213.088 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 36213.088 | 21709.7722 | 36213.088 | 21709.7722
| SSE Harvester | AS | Argyll | Culdrain | Forestry Commission | 2018-02-28 | 3 | 3 |  |  |  | 6 | 3 | 12 | 72 | 1889.0944 | 1612 | 72.12 | 605.88 | 5.455% | 27.2727 | 0.32727 | 1.3091 | 3.9338 | 22.032 | 25.9658 | 4232.3329 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 4232.3329 | -118.6618 | 4232.3329 | -118.6618
March | Contract Harvester | NE | Moray | Culdrain | Forestry Commission | 2018-03-09 | 8 | 8 | 55.2% | 24000 | 13437.03 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -11602.6526 | 0 | -11602.6526
| Contract Harvester | TS | Tayside | Glen Eagles | Iggesund | 2018-03-16 | 5 | 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4034 | 8 | 32272 | 48488.68 | 543137.76 | 591626.44 | 5% | 201.7 | 1613.6 | 29581.322 | 2424.434 | 27156.888 | 591626.44 | 584374.7821 | 29581.322 | 22329.6641
| Contract Harvester | HI | Highland | Dores | Gordons | 2018-03-31 | 10 | 10 |  |  |  | 49 | 10 | 98 | 784 | 52880 | 4712 | 588.98 | 6597.36 | 18.18% | 90.9091 | 8.9091 | 35.6364 | 107.0873 | 599.76 | 706.8473 | 65576.0964 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 65576.0964 | 51072.7806 | 65576.0964 | 51072.7806
[8 empty] | 323 | 65.24% | 288000 | 180457.1 |  | 225 | 4796 | 25752 | 799023.7728 | 155552 | 28823.96 | 216703.08 |  | 1909.0909 | 656.6727 | 2626.6909 | 7893.2062 | 44207.208 | 52100.4142 | 1254112.3179 | [5 empty] | 2865853.56 | 2 | 915.6 | 7860.2 | 143292.678 | 11005.512 | 132287.166 | 4119965.8779 | 3651508.7779 | 1397404.9959 | 928947.8959
[6 empty] | Machine Days |  |  |  | 323 |  |  |  | Generation total |  |  | 1008585.2779 | [13 empty] | Network Sec Total |  | 2865853.56 |  |  |  | 143292.678
[6 empty] | Total Cost |  |  |  | 468457.1 |  |  |  | Average Per day |  |  | 4482.6012 | [13 empty] | Average per day |  | 8872.6116 |  |  |  | 443.6306
[6 empty] | Cost per day |  |  |  | 1450.3316
[14 empty] | CI/CHL Total |  |  | 297627.4542
[6 empty] | Total available days per year |  |  |  | 230 |  |  |  | Average per day |  |  | 1322.7887
[6 empty] | Utilisation To Date |  |  |  | 65.24%
|  | Total Litres of diesel avoided |  | 302453.8112
|  | CO2e |  | 2.6761
|  | Total CO2 Avoided (kg co2e) |  | 809408.7423
|  | Total CO2 Avoided (tonnes co2e) |  | 809.4087
CBA figures
|  | Investment: Tree Cutting |  | 956484.8637 | 0.95648
|  | Customer interruptions (CI) |  | 47722.6782 | 0.047723
|  | Customer minutes lost (CML) |  | 393197.454 | 0.3932
|  | Reduced number of customers interrupted |  | 6368.2727 | 6368.2727
|  | Reduced customer minutes lost |  | 36238.8909 | 2174333.4545
|  | Reduced emissions (not associated with losses)1 |  | 809.4087 | 809.4087
Note on U1: Stirling, Graham: Advice from Geny desk. A geny will trip every 50 to 60 days.
Note on M36: Stirling, Graham: 3 windfarms only
Note on M50: Stirling, Graham: WindfarmCustome on 33kv. 11kv cut live due to proximity.

## Working baseline 2018.19
|  | Workings / assumptions used for costing Baseline | [16 empty] | Days to geny trip | 55
|  | Use this sheet to provide details of assumptions and calculation methodology used in CBA model | [11 empty] | Planned Outage |  |  |  |  | Duration of genny trip | 4 | [8 empty] | Unplanned Outage
|  |  | BOLD RED = ESTIMATE | [10 empty] | CI |  | 6.01 |  |  | Staff cost | 500 | [8 empty] | CI |  | 12.02
[14 empty] | CHL |  | 8.415 | [12 empty] | CHL |  | 16.83
[6 empty] | Monthly hire Rate |  |  |  | 24000
[6 empty] | SSE supervisor |  |  |  | 261 | [18 empty] | Likelyhood |  | 5%
[6 empty] | Potential availability (days per year) |  |  |  | 500
[6 empty] | Days unavailable (off hire) |  |  |  | 0
[6 empty] | Months available |  |  |  | 12
| Live Line Harvester Costs | [10 empty] | Conventional Harvesting under outage with generation | [15 empty] | System Security Liability
Month | Machine Type | Depot | Woodland name / ref | location | landowner details | date completed | Duration | Total days utilised | Utilisation | Machine Costs | Harmony Cost including Fuel, Accomodatiom, Staff costs and Sundries | Customers | Duration of outage | CI's Assumed 2 disconections per customer | CHL's Based on the total estimated time to connect and disconnect generation | Cost of Generation | SSE Staff Cost | CI cost | CHL cost | Likelyhood of genny trip | Likely genny trip staff cost | Number of likely Cis | Number Of likely CHL's | Likely gen trip CI cost | Likely gen trip CHL cost | Likely genny trip CICHL costs | Total cost of generation | Customers Potentially Affected outside of outage area (number) | Estimated ERTS (Hours) based on access and staff coverage | Customer hours lost if fault occurs | CI cost | CHL cost | Total potential cost | Likelyhood | Number of likely CIs | Number of likely CHLs | Potential Cost vs likelyhood | Likely CI Cost | Likely CHL Cost | Potential total cost under generation | Potential saving | Likely total cost under generation | Minimum saving
April | Contract Harvester |  | Dores | Dores |  |  | 5 | 5 | 48% | 24840 | 13424.25 | 132 | 5 | 264 | 2112 | 22972.296 | 7796 | 1586.64 | 17772.48 | 9.091% | 45.4545 | 12 | 48 | 144.24 | 807.84 | 952.08 | 51124.9505 | 234 | 8 | 1872 | 2812.68 | 31505.76 | 34318.44 | 5% | 11.7 | 93.6 | 1715.922 | 140.634 | 1575.288 | 85443.3905 | 75317.8451 | 52840.8725 | 42715.3271
| Contract Harvester |  | Ardlamont |  |  |  | 15 | 15 |  |  |  | 30 | 15 | 60 | 360 | 45118.304 | 14844 | 360.6 | 3029.4 | 27.27% | 136.3636 | 8.1818 | 32.7273 | 98.3455 | 550.8 | 649.1455 | 64137.8131 | 2472 | 6 | 14832 | 29713.44 | 249622.56 | 279336 | 5% | 123.6 | 741.6 | 13966.8 | 1485.672 | 12481.128 | 343473.8131 | 313097.1767 | 78104.6131 | 47727.9767
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | Contract Harvester |  | Ford | Argyll |  |  | 18 | 15 | 36% | 24840 | 11159.9 | 46 | 15 | 92 | 552 | 74270.096 | 14844 | 552.92 | 4645.08 | 27.27% | 136.3636 | 12.5455 | 50.1818 | 150.7964 | 844.56 | 995.3564 | 95443.816 | 432 | 6 | 2592 | 5192.64 | 43623.36 | 48816 | 5% | 21.6 | 129.6 | 2440.8 | 259.632 | 2181.168 | 144259.816 | 107807.8523 | 97884.616 | 61432.6523
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June |  |  | Cnoch na Dail - East |  |  |  | 18 | 18 | 43.2% | 24840 | 8819.44 | 147 | 18 | 294 | 2352 | 97515.8496 | 4744 | 1766.94 | 19792.08 | 32.73% | 163.6364 | 48.1091 | 192.4364 | 578.2713 | 3238.704 | 3816.9753 | 127799.4812 | 147 | 8 | 1176 | 1766.94 | 19792.08 | 21559.02 | 5% | 7.35 | 58.8 | 1077.951 | 88.347 | 989.604 | 149358.5012 | 112906.5375 | 128877.4322 | 92425.4685
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July |  |  | Cnoch na Dail - West |  |  |  | 15 | 13 | 31.2% | 24840 | 12243.89 | 147 | 15 | 294 | 2352 | 82088.208 | 4444 | 1766.94 | 19792.08 | 27.27% | 136.3636 | 40.0909 | 160.3636 | 481.8927 | 2698.92 | 3180.8127 | 111408.4044 | 147 | 8 | 1176 | 1766.94 | 19792.08 | 21559.02 | 5% | 7.35 | 58.8 | 1077.951 | 88.347 | 989.604 | 132967.4244 | 102590.7879 | 112486.3554 | 82109.7189
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August |  |  | Tarbert | Argyll |  |  | 5 | 5 | 55.2% | 24840 | 8345.61 | 3 | 5 | 6 | 36 | 16694 | 2356 | 36.06 | 302.94 | 9.091% | 45.4545 | 0.27273 | 1.0909 | 3.2782 | 18.36 | 21.6382 | 19456.0927 | 722 | 8 | 5776 | 8678.44 | 97210.08 | 105888.52 | 5% | 36.1 | 288.8 | 5294.426 | 433.922 | 4860.504 | 125344.6127 | 115219.0673 | 24750.5187 | 14624.9733
|  |  | The heights 33kv | Arran |  |  | 20 | 18 |  |  |  | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 32.73% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1303 | 8 | 10424 | 15662.06 | 175435.92 | 191097.98 | 5% | 65.15 | 521.2 | 9554.899 | 783.103 | 8771.796 | 191097.98 | 150595.7981 | 9554.899 | -30947.2829
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September |  |  | Garth Wood | Aberfeldy |  |  | 10 | 9 | 64.8% | 24840 | 19214.88 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 16.36% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1560 | 8 | 12480 | 18751.2 | 210038.4 | 228789.6 | 5% | 78 | 624 | 11439.48 | 937.56 | 10501.92 | 228789.6 | 208538.509 | 11439.48 | -8811.611
|  |  | The Heights 11kv | Arran |  |  | 20 | 18 |  |  |  | 83 | 20 | 166 | 996 | 117378.24 | 8120 | 997.66 | 8381.34 | 36.36% | 181.8182 | 30.1818 | 120.7273 | 362.7855 | 2031.84 | 2394.6255 | 137453.6836 | 1303 | 8 | 10424 | 15662.06 | 175435.92 | 191097.98 | 5% | 65.15 | 521.2 | 9554.899 | 783.103 | 8771.796 | 328551.6636 | 288049.4817 | 147008.5826 | 106506.4007
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October |  |  | Attadale | Loch Carron |  |  | 10 | 9 | 40.8% | 24840 | 18805.76 | 36 | 10 | 36 | 216 | 11927.296 | 4016 | 216.36 | 1817.64 | 18.18% | 90.9091 | 6.5455 | 26.1818 | 78.6764 | 440.64 | 519.3164 | 18587.5215 | 350 | 4 | 1400 | 4207 | 23562 | 27769 | 5% | 17.5 | 70 | 1388.45 | 210.35 | 1178.1 | 46356.5215 | 26105.4305 | 19975.9715 | -275.1195
|  |  | Tom Doune | Highland |  |  | 10 | 8 |  |  |  | 12 | 10 | 24 | 144 | 17854.592 | 4216 | 144.24 | 1211.76 | 18.18% | 90.9091 | 2.1818 | 8.7273 | 26.2255 | 146.88 | 173.1055 | 23690.6065 | 462 | 4 | 1848 | 5553.24 | 31101.84 | 36655.08 | 5% | 23.1 | 92.4 | 1832.754 | 277.662 | 1555.092 | 60345.6865 | 40094.5956 | 25523.3605 | 5272.2696
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November |  |  | Training | Highland |  |  | 20 | 0 | 0% | 24840 | 10686.93 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -40502.1819 | 0 | -40502.1819
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December |  |  | Craibstone |  |  |  | 5 | 5 | 36% | 24840 | 17177.23 | 8 | 5 | 432 | 3456 | 39619.5104 | 7792 | 2596.32 | 29082.24 | 9.091% | 45.4545 | 0.72727 | 2.9091 | 8.7418 | 48.96 | 57.7018 | 79193.2268 | 614 | 8 | 4912 | 7380.28 | 82668.96 | 90049.24 | 5% | 30.7 | 245.6 | 4502.462 | 369.014 | 4133.448 | 169242.4668 | 159116.9213 | 83695.6888 | 73570.1433
| SSE Harvester |  | Balmaha | Clackmannanshire |  |  | 5 | 5 |  |  |  | 114 | 8 | 228 | 1368 | 30833.8368 | 4532 | 1370.28 | 11511.72 | 14.55% | 72.7273 | 16.5818 | 66.3273 | 199.3135 | 1116.288 | 1315.6015 | 49636.1655 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 49636.1655 | 39510.6201 | 49636.1655 | 39510.6201
|  |  | Sandbank | Argyll |  |  | 5 | 5 |  |  |  | 187 | 8 | 374 | 2992 | 26728.5664 | 4632 | 2247.74 | 25177.68 | 14.55% | 72.7273 | 27.2 | 108.8 | 326.944 | 1831.104 | 2158.048 | 61016.7617 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 61016.7617 | 50891.2162 | 61016.7617 | 50891.2162
[30 empty] | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
January |  |  | Cruach Tarbiet | Argyll |  |  | 8 | 7 | 48% | 24840 | 9591.22 | 105 | 10 | 210 | 840 | 33699.12 | 4372 | 1262.1 | 7068.6 | 18.18% | 90.9091 | 19.0909 | 76.3636 | 229.4727 | 1285.2 | 1514.6727 | 48007.4018 | 402 | 6 | 2412 | 4832.04 | 40593.96 | 45426 | 5% | 20.1 | 120.6 | 2271.3 | 241.602 | 2029.698 | 93433.4018 | 77232.5291 | 50278.7018 | 34077.8291
|  |  | Brenfield |  |  |  | 4 | 3 |  |  |  | 8 | 5 | 16 | 512 | 5945.472 | 2900 | 96.16 | 4308.48 | 9.091% | 45.4545 | 0.72727 | 2.9091 | 8.7418 | 48.96 | 57.7018 | 13353.2684 | 187 | 6 | 1122 | 2247.74 | 18883.26 | 21131 | 5% | 9.35 | 56.1 | 1056.55 | 112.387 | 944.163 | 34484.2684 | 26383.832 | 14409.8184 | 6309.382
|  |  | Bridge of Gaur - 1 | Rannoch |  |  | 10 | 10 |  |  |  | 38 | 20 | 76 | 456 | 83783.776 | 4400 | 456.76 | 3837.24 | 36.36% | 181.8182 | 13.8182 | 55.2727 | 166.0945 | 930.24 | 1096.3345 | 93755.9287 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 93755.9287 | 73504.8378 | 93755.9287 | 73504.8378
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February |  |  | Bridge of Gaur - 1 | Rannoch |  |  | 5 | 5 | 79.2% | 24840 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -10125.5455 | 0 | -10125.5455
| SSE Harvester |  | Kinloch Rannoch | Rannoch |  |  | 10 | 10 |  |  |  | 52 | 5 | 104 | 832 | 20641.416 | 7796 | 625.04 | 7001.28 | 9.091% | 45.4545 | 4.7273 | 18.9091 | 56.8218 | 318.24 | 375.0618 | 36484.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 36484.2524 | 16233.1614 | 36484.2524 | 16233.1614
| SSE Harvester |  | Callander | Stirlingshire |  |  | 5 | 5 |  |  |  | 12 | 5 | 24 | 1152 | 5204.56 | 2900 | 144.24 | 9694.08 | 9.091% | 45.4545 | 1.0909 | 4.3636 | 13.1127 | 73.44 | 86.5527 | 18074.8873 | 396 | 4 | 1584 | 4759.92 | 26658.72 | 31418.64 | 5% | 19.8 | 79.2 | 1570.932 | 237.996 | 1332.936 | 49493.5273 | 39367.9818 | 19645.8193 | 9520.2738
|  |  | Bridge of Gaur - 2 | Rannoch |  |  | 5 | 3 |  |  |  | 38 | 10 | 76 | 456 | 23781.888 | 5032 | 456.76 | 3837.24 | 18.18% | 90.9091 | 6.9091 | 27.6364 | 83.0473 | 465.12 | 548.1673 | 33746.9644 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 33746.9644 | 23621.4189 | 33746.9644 | 23621.4189
|  |  | Point sands | Argyll |  |  | 10 | 10 |  |  |  | 147 | 10 | 294 | 7938 | 52730.472 | 3944 | 1766.94 | 66798.27 | 18.18% | 90.9091 | 26.7273 | 106.9091 | 321.2618 | 1799.28 | 2120.5418 | 127451.1329 | 162 | 8 | 1296 | 1947.24 | 21811.68 | 23758.92 | 5% | 8.1 | 64.8 | 1187.946 | 97.362 | 1090.584 | 151210.0529 | 130958.962 | 128639.0789 | 108387.988
March |  |  | Tain |  |  |  | 15 | 15 | 48% | 24840 | 10000 | 28 | 15 | 56 | 336 | 5532 | 5532 | 336.56 | 2827.44 | 27.27% | 136.3636 | 7.6364 | 30.5455 | 91.7891 | 514.08 | 605.8691 | 14970.2327 | 2543 | 6 | 15258 | 30566.86 | 256792.14 | 287359 | 5% | 127.15 | 762.9 | 14367.95 | 1528.343 | 12839.607 | 302329.2327 | 271952.5963 | 29338.1827 | -1038.4537
|  |  | Bute |  |  |  | 5 | 5 |  |  |  | 45 | 5 | 90 | 360 | 34824.1646 | 4532 | 540.9 | 3029.4 | 9.091% | 45.4545 | 4.0909 | 16.3636 | 49.1727 | 275.4 | 324.5727 | 43296.4918 | 372 | 4 | 1488 | 4471.44 | 25043.04 | 29514.48 | 5% | 18.6 | 74.4 | 1475.724 | 223.572 | 1252.152 | 72810.9718 | 62685.4264 | 44772.2158 | 34646.6704
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 258 | 221 | 48.24% | 298080 | 149469.11 |  | 246 | 3216 | 29818 | 849143.6638 | 123744 | 19328.16 | 250918.47 |  | 1990.9091 | 289.4364 | 1157.7455 | 3479.0251 | 19484.856 | 22963.8811 | 1268089.084 | [5 empty] | 1715543.92 | 2.25 | 690.4 | 4603.6 | 85777.196 | 8298.608 | 77478.588 | 2983633.004 | 2461154.8574 | 1353866.28 | 831388.1334
[6 empty] | Machine Days |  |  |  | 221 |  |  |  | Generation total |  |  | 997842.454 | [13 empty] | Network Sec Total |  | 1715543.92 |  |  |  | 85777.196
[6 empty] | Total Cost |  |  |  | 447549.11 |  |  |  | Average Per day |  |  | 4056.2701 | [13 empty] | Average per day |  | 7762.6422 |  |  |  | 388.1321
[6 empty] | Cost per day |  |  |  | 2025.1091
[14 empty] | CI/CHL Total |  |  | 293210.5111
[6 empty] | Total available days per year |  |  |  | 230 |  |  |  | Average per day |  |  | 1191.9126
[6 empty] | Utilisation To Date |  |  |  | 48.24%
|  | Total Litres of diesel avoided |  | 409922.1862
|  | CO2e |  | 2.6761
|  | Total CO2 Saved (kg co2e) |  | 1097009.1595
|  | Total CO2 Saved (tonnes co2e) |  | 1097.0092
CBA figures
|  | Investment: Tree Cutting |  | 974878.5729 | 0.97488
|  | Customer interruptions (CI) |  | 31105.7931 | 0.031106
|  | Customer minutes lost (CML) |  | 347881.914 | 0.34788
|  | Reduced number of customers interrupted |  | 4195.8364 | 4195.8364
|  | Reduced customer minutes lost |  | 35579.3455 | 2134760.7273
|  | Reduced emissions (not associated with losses)1 |  | 1097.0092 | 1097.0092
Note on U1: Stirling, Graham: Advice from Geny desk. A geny will trip every 50 to 60 days.

## Option 1 (Baseline)
| CBA Option 1 - Baseline | Traditional Reinforcement
| Term (years from first out flow) | NPV (£m)
| 16 | -6.9495
| 24 | -7.3929
| 32 | -7.6885
| 45 | -7.9907
| first year of investment out flow | 1
|  |  |  | RIIO-ED1 | [7 empty] | RIIO-ED2 | [7 empty] | RIIO-ED3 | [7 empty] | RIIO-ED4 | [7 empty] | RIIO-ED5 | [7 empty] | RIIO-ED6 | [7 empty] | RIIO-ED7
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52
|  | Calculation | Units | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067
Investment | Tree Cutting |  | £m | -0.71577 | -0.75595 | -0.95648 | -0.97488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Total investment |  | £m | -0.71577 | -0.75595 | -0.95648 | -0.97488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided DNO costs | Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Total avoided DNO costs |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total DNO net benefits before capitalisation | (1) = investment + DNO benefits | £m | -0.71577 | -0.75595 | -0.95648 | -0.97488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capitalisation rates | (2) | % | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70%
| Capitalised investment | (3)=(1)x(2) | £m | -0.50104 | -0.52917 | -0.66954 | -0.68242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Investment to be expensed | (4)=(1)-(3) | £m | -0.21473 | -0.22679 | -0.28695 | -0.29246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2016 Depreciation | (5)2016=(3)2016*Dep_ratet | £m |  | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134 | -0.011134
| 2017 Depreciation | (5)2017=(3)2017*Dep_ratet | £m |  |  | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759 | -0.011759
| 2018 Depreciation | (5)2018=(3)2018*Dep_ratet | £m |  |  |  | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879 | -0.014879
| 2019 Depreciation | (5)2019=(3)2019*Dep_ratet | £m |  |  |  |  | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165 | -0.015165
| 2020 Depreciation | (5)2020=(3)2020*Dep_ratet | £m | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2021 Depreciation | (5)2021=(3)2021*Dep_ratet | £m | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2022 Depreciation | (5)2022=(3)2022*Dep_ratet | £m | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2023 Depreciation | (5)2023=(3)2023*Dep_ratet | £m | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2024 Depreciation | (5)2024=(3)2024*Dep_ratet | £m | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2025 Depreciation | (5)2025=(3)2025*Dep_ratet | £m | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2026 Depreciation | (5)2026=(3)2026*Dep_ratet | £m | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2027 Depreciation | (5)2027=(3)2027*Dep_ratet | £m | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2028 Depreciation | (5)2028=(3)2028*Dep_ratet | £m | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2029 Depreciation | (5)2029=(3)2029*Dep_ratet | £m | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2030 Depreciation | (5)2030=(3)2030*Dep_ratet | £m | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2031 Depreciation | (5)2031=(3)2031*Dep_ratet | £m | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2032 Depreciation | (5)2032=(3)2032*Dep_ratet | £m | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2033 Depreciation | (5)2033=(3)2033*Dep_ratet | £m | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2034 Depreciation | (5)2034=(3)2034*Dep_ratet | £m | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2035 Depreciation | (5)2035=(3)2035*Dep_ratet | £m | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2036 Depreciation | (5)2036=(3)2036*Dep_ratet | £m | RIIO-ED3 22: 0; RIIO-ED3 23: 0; RIIO-ED3 24: 0; RIIO-ED4 25: 0; RIIO-ED4 26: 0; RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2037 Depreciation | (5)2037=(3)2037*Dep_ratet | £m | RIIO-ED3 23: 0; RIIO-ED3 24: 0; RIIO-ED4 25: 0; RIIO-ED4 26: 0; RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2038 Depreciation | (5)2038=(3)2038*Dep_ratet | £m | RIIO-ED3 24: 0; RIIO-ED4 25: 0; RIIO-ED4 26: 0; RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2039 Depreciation | (5)2039=(3)2039*Dep_ratet | £m | RIIO-ED4 25: 0; RIIO-ED4 26: 0; RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2040 Depreciation | (5)2040=(3)2040*Dep_ratet | £m | RIIO-ED4 26: 0; RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2041 Depreciation | (5)2041=(3)2041*Dep_ratet | £m | RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2042 Depreciation | (5)2042=(3)2042*Dep_ratet | £m | RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2043 Depreciation | (5)2043=(3)2043*Dep_ratet | £m | RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2044 Depreciation | (5)2044=(3)2044*Dep_ratet | £m | RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2045 Depreciation | (5)2045=(3)2045*Dep_ratet | £m | RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| Depreciation | (5)=∑(5)t | £m | 0 | -0.011134 | -0.022893 | -0.037772 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.052937 | -0.041803 | -0.030043 | -0.015165 | 0 | 0 | 0
| Opening RAV balance | (6op)t=(6cl)t-1 | £m | 0 | -0.50104 | -1.0191 | -1.6657 | -2.3104 | -2.2574 | -2.2045 | -2.1515 | -2.0986 | -2.0457 | -1.9927 | -1.9398 | -1.8869 | -1.8339 | -1.781 | -1.7281 | -1.6751 | -1.6222 | -1.5692 | -1.5163 | -1.4634 | -1.4104 | -1.3575 | -1.3046 | -1.2516 | -1.1987 | -1.1457 | -1.0928 | -1.0399 | -0.98694 | -0.934 | -0.88106 | -0.82813 | -0.77519 | -0.72225 | -0.66932 | -0.61638 | -0.56344 | -0.51051 | -0.45757 | -0.40463 | -0.3517 | -0.29876 | -0.24582 | -0.19288 | -0.13995 | -0.087011 | -0.045208 | -0.015165 | 1.0703e-15 | 1.0703e-15 | 1.0703e-15
| Closing RAV balance | (6cl)=(3)-(5)+(6op) | £m | -0.50104 | -1.0191 | -1.6657 | -2.3104 | -2.2574 | -2.2045 | -2.1515 | -2.0986 | -2.0457 | -1.9927 | -1.9398 | -1.8869 | -1.8339 | -1.781 | -1.7281 | -1.6751 | -1.6222 | -1.5692 | -1.5163 | -1.4634 | -1.4104 | -1.3575 | -1.3046 | -1.2516 | -1.1987 | -1.1457 | -1.0928 | -1.0399 | -0.98694 | -0.934 | -0.88106 | -0.82813 | -0.77519 | -0.72225 | -0.66932 | -0.61638 | -0.56344 | -0.51051 | -0.45757 | -0.40463 | -0.3517 | -0.29876 | -0.24582 | -0.19288 | -0.13995 | -0.087011 | -0.045208 | -0.015165 | 1.0703e-15 | 1.0703e-15 | 1.0703e-15 | 1.0703e-15
| Cost of Capital | (6)=avg[(6cl),(6op)]xWACC | £m | -0.010021 | -0.030402 | -0.053696 | -0.079522 | -0.091356 | -0.089238 | -0.087121 | -0.085003 | -0.082886 | -0.080768 | -0.078651 | -0.076533 | -0.074416 | -0.072298 | -0.070181 | -0.068063 | -0.065946 | -0.063828 | -0.061711 | -0.059594 | -0.057476 | -0.055359 | -0.053241 | -0.051124 | -0.049006 | -0.046889 | -0.044771 | -0.042654 | -0.040536 | -0.038419 | -0.036301 | -0.034184 | -0.032066 | -0.029949 | -0.027831 | -0.025714 | -0.023596 | -0.021479 | -0.019362 | -0.017244 | -0.015127 | -0.013009 | -0.010892 | -0.0087741 | -0.0066567 | -0.0045392 | -0.0026444 | -0.0012075 | -0.0003033 | 4.2813e-17 | 4.2813e-17 | 4.2813e-17
| Total Net DNO benefits | (7)=(4)+(5)+(6) | £m | -0.22475 | -0.26832 | -0.36353 | -0.40976 | -0.14429 | -0.14218 | -0.14006 | -0.13794 | -0.13582 | -0.13371 | -0.13159 | -0.12947 | -0.12735 | -0.12524 | -0.12312 | -0.121 | -0.11888 | -0.11677 | -0.11465 | -0.11253 | -0.11041 | -0.1083 | -0.10618 | -0.10406 | -0.10194 | -0.099826 | -0.097708 | -0.095591 | -0.093473 | -0.091356 | -0.089238 | -0.087121 | -0.085003 | -0.082886 | -0.080768 | -0.078651 | -0.076533 | -0.074416 | -0.072298 | -0.070181 | -0.068063 | -0.065946 | -0.063828 | -0.061711 | -0.059594 | -0.057476 | -0.044447 | -0.031251 | -0.015468 | 4.2813e-17 | 4.2813e-17 | 4.2813e-17
Societal benefits (£m) i.e. costs avoided | Losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2e associated with losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer interruptions (CI) |  | £m | -0.55878 | -0.080301 | -0.098349 | -0.064798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer minutes lost (CML) |  | £m | -2.0614 | -0.49069 | -0.81901 | -0.8041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other GHG emissions (CO2e) i.e. not associated with losses |  | £m | -0.0049668 | -0.0046875 | -0.0066021 | -0.0095169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fatality |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Major injury |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oil leakage |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other 1 (specify) |  | £m
| Other 2 (specify) |  | £m
| Other 3 (specify) |  | £m
| Total societal net benefits |  | £m | -2.6251 | -0.57568 | -0.92396 | -0.87842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  | £m | -2.8499 | -0.844 | -1.2875 | -1.2882 | -0.14429 | -0.14218 | -0.14006 | -0.13794 | -0.13582 | -0.13371 | -0.13159 | -0.12947 | -0.12735 | -0.12524 | -0.12312 | -0.121 | -0.11888 | -0.11677 | -0.11465 | -0.11253 | -0.11041 | -0.1083 | -0.10618 | -0.10406 | -0.10194 | -0.099826 | -0.097708 | -0.095591 | -0.093473 | -0.091356 | -0.089238 | -0.087121 | -0.085003 | -0.082886 | -0.080768 | -0.078651 | -0.076533 | -0.074416 | -0.072298 | -0.070181 | -0.068063 | -0.065946 | -0.063828 | -0.061711 | -0.059594 | -0.057476 | -0.044447 | -0.031251 | -0.015468 | 4.2813e-17 | 4.2813e-17 | 4.2813e-17
| Discount factor | =1/[(1+SRTP)^n] |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501
| Discount factor (safety) | =1/[(1+PTPR)^n] |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.63031 | 0.62099 | 0.61182 | 0.60277 | 0.59387 | 0.58509 | 0.57644 | 0.56792 | 0.55953 | 0.55126 | 0.54312 | 0.53509 | 0.52718 | 0.51939 | 0.51171 | 0.50415 | 0.4967 | 0.48936 | 0.48213 | 0.475 | 0.46798 | 0.46107
| Discounted net benefits |  | £m | -2.7535 | -0.78789 | -1.1612 | -1.1226 | -0.12149 | -0.11566 | -0.11008 | -0.10475 | -0.099657 | -0.094786 | -0.09013 | -0.085681 | -0.08143 | -0.077368 | -0.073488 | -0.069782 | -0.066242 | -0.062862 | -0.059635 | -0.056554 | -0.053613 | -0.050807 | -0.048129 | -0.045574 | -0.043137 | -0.040812 | -0.038596 | -0.036483 | -0.034468 | -0.032548 | -0.035694 | -0.033832 | -0.032048 | -0.03034 | -0.028704 | -0.027137 | -0.025637 | -0.024202 | -0.022828 | -0.021514 | -0.020258 | -0.019056 | -0.017907 | -0.016808 | -0.015759 | -0.014756 | -0.011079 | -0.0075627 | -0.0036342 | 9.7659e-18 | 9.4815e-18 | 9.2053e-18
| Cumulative discounted net benefits |  | £m | -2.7535 | -3.5414 | -4.7026 | -5.8252 | -5.9467 | -6.0624 | -6.1725 | -6.2772 | -6.3769 | -6.4717 | -6.5618 | -6.6475 | -6.7289 | -6.8063 | -6.8797 | -6.9495 | -7.0158 | -7.0786 | -7.1383 | -7.1948 | -7.2484 | -7.2992 | -7.3474 | -7.3929 | -7.4361 | -7.4769 | -7.5155 | -7.552 | -7.5864 | -7.619 | -7.6547 | -7.6885 | -7.7206 | -7.7509 | -7.7796 | -7.8067 | -7.8324 | -7.8566 | -7.8794 | -7.9009 | -7.9212 | -7.9402 | -7.9581 | -7.975 | -7.9907 | -8.0055 | -8.0165 | -8.0241 | -8.0277 | -8.0277 | -8.0277 | -8.0277
Non-DNO (eg societal) benefits
Enter values as increments (delta) relative to your reference scenario. If this is your reference scenario enter 0. Reductions are entered as positive numbers and increases as negative numbers.
Societal net benefits (impact relative to business as usual scenario) | Reduced losses |  | MWh
| Reduced emissions associated with losses |  | tCO2e | bar: RIIO-ED1 1 to RIIO-ED3 24
| Reduced number of customers interrupted |  | no. | RIIO-ED1 1: -36182.1227; RIIO-ED1 2: -5199.6364; RIIO-ED1 3: -6368.2727; RIIO-ED1 4: -4195.8364
| Reduced customer minutes lost |  | Mins | RIIO-ED1 1: -5472653.4545; RIIO-ED1 2: -1302710.7273; RIIO-ED1 3: -2174333.4545; RIIO-ED1 4: -2134760.7273
| Reduced emissions (not associated with losses)1 |  | tCO2e | RIIO-ED1 1: -680.0819; RIIO-ED1 2: -611.1058; RIIO-ED1 3: -809.4087; RIIO-ED1 4: -1097.0092
| Reduced probability of fatality2 |  | %
| Reduced probability of major injury2 |  | %
| Reduced oil leakage |  | Litres
1 | Includes all GHG not associated with losses e.g. SF6 converted to tCO2e using Defra conversion factors
http://www.defra.gov.uk/publications/2012/05/30/pb13773-2012-ghg-conversion/
Where losses are entered in terms of MWh, the CO2e associated with those losses will be calculated based on an assumed GHG conversion factor. The tCO2e are monetised using DECC traded carbon values.
All other GHG emissions not associated with losses should be entered in row 90 to avoid double counting.
2 | http://www.hse.gov.uk/risk/theory/alarpcheck.htm
Please specify
Total investment
Connections
Diversions
Reinforcement
ESQCR
Asset Replacement
Refurbishment
Civil Works
Operational IT & Telecoms
Legal & Safety
QoS
High Value Projects
Flooding
BT21CN
Technical losses and other environmental
High impact Low Probability (HILP)
Critical National Infrastructure
Black Start
Rising Mains and Laterals
Undergrounding Within/ Outside designated areas
Worst Served Customers
Trouble Call / faults
ONIs
Inspections & Maintenance
Tree Cutting
NOC's Other
Network Design & Engineering
Project Management
Engineering Mgt & Clerical Support
System Mapping - Cartographical
Control Centre
Call Centre
Stores
Operational Training
Vehicles & Transport
Atypicals Non Sev Weather
Smart Meters
Network Policy
HR & Non-operational Training
Finance & Regulation
CEO
IT & Telecoms
Property Mgt
Non Op Capex
Note on C9: Ofgem: Check that this is the first year of investment across all options (including baseline). If this is not the first year of investment across all options hardcode the first year of investment in cell C9. For further guidance please refer to Appendix A of the Supplementary guidance: queries and clarification document.

## Option 2
| CBA Option 2 | S,T
| Term (years from first out flow) | NPV (£m)
| 16 | -1.3147
| 24 | -1.5686
| 32 | -1.7377
| 45 | -1.9106
| first year of investment out flow | 1
|  |  |  | RIIO-ED1 | [7 empty] | RIIO-ED2 | [7 empty] | RIIO-ED3 | [7 empty] | RIIO-ED4 | [7 empty] | RIIO-ED5 | [7 empty] | RIIO-ED6 | [7 empty] | RIIO-ED7
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52
|  | Calculation | Units | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067
Investment | Tree Cutting |  | £m | -0.25641 | -0.77856 | -0.46846 | -0.44755 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Please specify |  | £m | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Please specify |  | £m | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Total investment |  | £m | -0.25641 | -0.77856 | -0.46846 | -0.44755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided DNO costs | Tree Cutting |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Total avoided DNO costs |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total DNO net benefits before capitalisation | (1) = investment + DNO benefits | £m | -0.25641 | -0.77856 | -0.46846 | -0.44755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capitalisation rates | (2) | % | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70%
| Capitalised investment | (3)=(1)x(2) | £m | -0.17949 | -0.545 | -0.32792 | -0.31328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Investment to be expensed | (4)=(1)-(3) | £m | -0.076923 | -0.23357 | -0.14054 | -0.13426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2016 Depreciation | (5)2016=(3)2016*Dep_ratet | £m |  | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886 | -0.0039886
| 2017 Depreciation | (5)2017=(3)2017*Dep_ratet | £m |  |  | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111 | -0.012111
| 2018 Depreciation | (5)2018=(3)2018*Dep_ratet | £m |  |  |  | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871 | -0.0072871
| 2019 Depreciation | (5)2019=(3)2019*Dep_ratet | £m |  |  |  |  | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619 | -0.0069619
| 2020 Depreciation | (5)2020=(3)2020*Dep_ratet | £m | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2021 Depreciation | (5)2021=(3)2021*Dep_ratet | £m | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2022 Depreciation | (5)2022=(3)2022*Dep_ratet | £m | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2023 Depreciation | (5)2023=(3)2023*Dep_ratet | £m | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2024 Depreciation | (5)2024=(3)2024*Dep_ratet | £m | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2025 Depreciation | (5)2025=(3)2025*Dep_ratet | £m | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2026 Depreciation | (5)2026=(3)2026*Dep_ratet | £m | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2027 Depreciation | (5)2027=(3)2027*Dep_ratet | £m | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2028 Depreciation | (5)2028=(3)2028*Dep_ratet | £m | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2029 Depreciation | (5)2029=(3)2029*Dep_ratet | £m | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2030 Depreciation | (5)2030=(3)2030*Dep_ratet | £m | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2031 Depreciation | (5)2031=(3)2031*Dep_ratet | £m | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2032 Depreciation | (5)2032=(3)2032*Dep_ratet | £m | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2033 Depreciation | (5)2033=(3)2033*Dep_ratet | £m | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2034 Depreciation | (5)2034=(3)2034*Dep_ratet | £m | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2035 Depreciation | (5)2035=(3)2035*Dep_ratet | £m | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2036 Depreciation | (5)2036=(3)2036*Dep_ratet | £m | RIIO-ED3 22: 0; RIIO-ED3 23: 0; RIIO-ED3 24: 0; RIIO-ED4 25: 0; RIIO-ED4 26: 0; RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2037 Depreciation | (5)2037=(3)2037*Dep_ratet | £m | RIIO-ED3 23: 0; RIIO-ED3 24: 0; RIIO-ED4 25: 0; RIIO-ED4 26: 0; RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2038 Depreciation | (5)2038=(3)2038*Dep_ratet | £m | RIIO-ED3 24: 0; RIIO-ED4 25: 0; RIIO-ED4 26: 0; RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2039 Depreciation | (5)2039=(3)2039*Dep_ratet | £m | RIIO-ED4 25: 0; RIIO-ED4 26: 0; RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2040 Depreciation | (5)2040=(3)2040*Dep_ratet | £m | RIIO-ED4 26: 0; RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2041 Depreciation | (5)2041=(3)2041*Dep_ratet | £m | RIIO-ED4 27: 0; RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2042 Depreciation | (5)2042=(3)2042*Dep_ratet | £m | RIIO-ED4 28: 0; RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2043 Depreciation | (5)2043=(3)2043*Dep_ratet | £m | RIIO-ED4 29: 0; RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2044 Depreciation | (5)2044=(3)2044*Dep_ratet | £m | RIIO-ED4 30: 0; RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| 2045 Depreciation | (5)2045=(3)2045*Dep_ratet | £m | RIIO-ED4 31: 0; RIIO-ED4 32: 0; RIIO-ED5 33: 0; RIIO-ED5 34: 0; RIIO-ED5 35: 0; RIIO-ED5 36: 0; RIIO-ED5 37: 0; RIIO-ED5 38: 0; RIIO-ED5 39: 0; RIIO-ED5 40: 0; RIIO-ED6 41: 0; RIIO-ED6 42: 0; RIIO-ED6 43: 0; RIIO-ED6 44: 0; RIIO-ED6 45: 0; RIIO-ED6 46: 0; RIIO-ED6 47: 0; RIIO-ED6 48: 0; RIIO-ED7 49: 0; RIIO-ED7 50: 0; RIIO-ED7 51: 0; RIIO-ED7 52: 0
| Depreciation | (5)=∑(5)t | £m | 0 | -0.0039886 | -0.0161 | -0.023387 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.030349 | -0.02636 | -0.014249 | -0.0069619 | 0 | 0 | 0
| Opening RAV balance | (6op)t=(6cl)t-1 | £m | 0 | -0.17949 | -0.72049 | -1.0323 | -1.3222 | -1.2919 | -1.2615 | -1.2312 | -1.2008 | -1.1705 | -1.1401 | -1.1098 | -1.0794 | -1.0491 | -1.0187 | -0.98838 | -0.95803 | -0.92768 | -0.89733 | -0.86698 | -0.83663 | -0.80629 | -0.77594 | -0.74559 | -0.71524 | -0.68489 | -0.65454 | -0.62419 | -0.59385 | -0.5635 | -0.53315 | -0.5028 | -0.47245 | -0.4421 | -0.41175 | -0.38141 | -0.35106 | -0.32071 | -0.29036 | -0.26001 | -0.22966 | -0.19931 | -0.16897 | -0.13862 | -0.10827 | -0.077919 | -0.047571 | -0.021211 | -0.0069619 | 3.0097e-16 | 3.0097e-16 | 3.0097e-16
| Closing RAV balance | (6cl)=(3)-(5)+(6op) | £m | -0.17949 | -0.72049 | -1.0323 | -1.3222 | -1.2919 | -1.2615 | -1.2312 | -1.2008 | -1.1705 | -1.1401 | -1.1098 | -1.0794 | -1.0491 | -1.0187 | -0.98838 | -0.95803 | -0.92768 | -0.89733 | -0.86698 | -0.83663 | -0.80629 | -0.77594 | -0.74559 | -0.71524 | -0.68489 | -0.65454 | -0.62419 | -0.59385 | -0.5635 | -0.53315 | -0.5028 | -0.47245 | -0.4421 | -0.41175 | -0.38141 | -0.35106 | -0.32071 | -0.29036 | -0.26001 | -0.22966 | -0.19931 | -0.16897 | -0.13862 | -0.10827 | -0.077919 | -0.047571 | -0.021211 | -0.0069619 | 3.0097e-16 | 3.0097e-16 | 3.0097e-16 | 3.0097e-16
| Cost of Capital | (6)=avg[(6cl),(6op)]xWACC | £m | -0.0035897 | -0.018 | -0.035056 | -0.04709 | -0.052281 | -0.051068 | -0.049854 | -0.04864 | -0.047426 | -0.046212 | -0.044998 | -0.043784 | -0.04257 | -0.041356 | -0.040142 | -0.038928 | -0.037714 | -0.0365 | -0.035286 | -0.034072 | -0.032858 | -0.031644 | -0.030431 | -0.029217 | -0.028003 | -0.026789 | -0.025575 | -0.024361 | -0.023147 | -0.021933 | -0.020719 | -0.019505 | -0.018291 | -0.017077 | -0.015863 | -0.014649 | -0.013435 | -0.012221 | -0.011007 | -0.0097935 | -0.0085795 | -0.0073656 | -0.0061516 | -0.0049377 | -0.0037237 | -0.0025098 | -0.0013756 | -0.00056345 | -0.00013924 | 1.2039e-17 | 1.2039e-17 | 1.2039e-17
| Total Net DNO benefits | (7)=(4)+(5)+(6) | £m | -0.080512 | -0.25556 | -0.19169 | -0.20474 | -0.08263 | -0.081416 | -0.080202 | -0.078988 | -0.077774 | -0.07656 | -0.075346 | -0.074132 | -0.072919 | -0.071705 | -0.070491 | -0.069277 | -0.068063 | -0.066849 | -0.065635 | -0.064421 | -0.063207 | -0.061993 | -0.060779 | -0.059565 | -0.058351 | -0.057137 | -0.055923 | -0.054709 | -0.053495 | -0.052281 | -0.051068 | -0.049854 | -0.04864 | -0.047426 | -0.046212 | -0.044998 | -0.043784 | -0.04257 | -0.041356 | -0.040142 | -0.038928 | -0.037714 | -0.0365 | -0.035286 | -0.034072 | -0.032858 | -0.027736 | -0.014812 | -0.0071011 | 1.2039e-17 | 1.2039e-17 | 1.2039e-17
Societal benefits (£m) i.e. costs avoided | Losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2e associated with losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer interruptions (CI) |  | £m |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer minutes lost (CML) |  | £m |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other GHG emissions (CO2e) i.e. not associated with losses |  | £m | -0.00046516 | -0.00068972 | -0.0014101 | -0.0010262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fatality |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Major injury |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oil leakage |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other 1 (specify) |  | £m
| Other 2 (specify) |  | £m
| Other 3 (specify) |  | £m
| Total societal net benefits |  | £m | -0.00046516 | -0.00068972 | -0.0014101 | -0.0010262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  | £m | -0.080978 | -0.25625 | -0.1931 | -0.20577 | -0.08263 | -0.081416 | -0.080202 | -0.078988 | -0.077774 | -0.07656 | -0.075346 | -0.074132 | -0.072919 | -0.071705 | -0.070491 | -0.069277 | -0.068063 | -0.066849 | -0.065635 | -0.064421 | -0.063207 | -0.061993 | -0.060779 | -0.059565 | -0.058351 | -0.057137 | -0.055923 | -0.054709 | -0.053495 | -0.052281 | -0.051068 | -0.049854 | -0.04864 | -0.047426 | -0.046212 | -0.044998 | -0.043784 | -0.04257 | -0.041356 | -0.040142 | -0.038928 | -0.037714 | -0.0365 | -0.035286 | -0.034072 | -0.032858 | -0.027736 | -0.014812 | -0.0071011 | 1.2039e-17 | 1.2039e-17 | 1.2039e-17
| Discount factor | =1/[(1+SRTP)^n] |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501
| Discount factor (safety) | =1/[(1+PTPR)^n] |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.63031 | 0.62099 | 0.61182 | 0.60277 | 0.59387 | 0.58509 | 0.57644 | 0.56792 | 0.55953 | 0.55126 | 0.54312 | 0.53509 | 0.52718 | 0.51939 | 0.51171 | 0.50415 | 0.4967 | 0.48936 | 0.48213 | 0.475 | 0.46798 | 0.46107
| Discounted net benefits |  | £m | -0.078239 | -0.23921 | -0.17417 | -0.17932 | -0.069572 | -0.066232 | -0.063038 | -0.059985 | -0.057065 | -0.054275 | -0.051608 | -0.04906 | -0.046624 | -0.044298 | -0.042075 | -0.039952 | -0.037925 | -0.035989 | -0.03414 | -0.032376 | -0.030691 | -0.029084 | -0.02755 | -0.026087 | -0.024691 | -0.02336 | -0.02209 | -0.02088 | -0.019726 | -0.018627 | -0.020426 | -0.01936 | -0.018338 | -0.01736 | -0.016423 | -0.015526 | -0.014667 | -0.013845 | -0.013058 | -0.012306 | -0.011586 | -0.010898 | -0.01024 | -0.009611 | -0.00901 | -0.0084359 | -0.0069133 | -0.0035846 | -0.0016684 | 2.7462e-18 | 2.6662e-18 | 2.5885e-18
| Cumulative discounted net benefits |  | £m | -0.078239 | -0.31745 | -0.49162 | -0.67093 | -0.7405 | -0.80674 | -0.86977 | -0.92976 | -0.98682 | -1.0411 | -1.0927 | -1.1418 | -1.1884 | -1.2327 | -1.2748 | -1.3147 | -1.3526 | -1.3886 | -1.4228 | -1.4551 | -1.4858 | -1.5149 | -1.5425 | -1.5686 | -1.5933 | -1.6166 | -1.6387 | -1.6596 | -1.6793 | -1.6979 | -1.7184 | -1.7377 | -1.7561 | -1.7734 | -1.7898 | -1.8054 | -1.82 | -1.8339 | -1.8469 | -1.8592 | -1.8708 | -1.8817 | -1.892 | -1.9016 | -1.9106 | -1.919 | -1.9259 | -1.9295 | -1.9312 | -1.9312 | -1.9312 | -1.9312
Non-DNO (eg societal) benefits
Enter values as increments (delta) relative to your reference scenario. If this is your reference scenario enter 0. Reductions are entered as positive numbers and increases as negative numbers.
Societal net benefits (impact relative to business as usual scenario) | Reduced losses |  | MWh
| Reduced emissions associated with losses |  | tCO2e | bar: RIIO-ED1 1 to RIIO-ED3 24
| Reduced number of customers interrupted |  | no.
| Reduced customer minutes lost |  | Mins
| Reduced emissions (not associated with losses)1 |  | tCO2e | RIIO-ED1 1: -63.6921; RIIO-ED1 2: -89.9183; RIIO-ED1 3: -172.8786; RIIO-ED1 4: -118.2854
| Reduced probability of fatality2 |  | %
| Reduced probability of major injury2 |  | %
| Reduced oil leakage |  | Litres
1 | Includes all GHG not associated with losses e.g. SF6 converted to tCO2e using Defra conversion factors
http://www.defra.gov.uk/publications/2012/05/30/pb13773-2012-ghg-conversion/
Where losses are entered in terms of MWh, the CO2e associated with those losses will be calculated based on an assumed GHG conversion factor. The tCO2e are monetised using DECC traded carbon values.
All other GHG emissions not associated with losses should be entered in row 90 to avoid double counting.
2 | http://www.hse.gov.uk/risk/theory/alarpcheck.htm
Please specify
Total investment
Connections
Diversions
Reinforcement
ESQCR
Asset Replacement
Refurbishment
Civil Works
Operational IT & Telecoms
Legal & Safety
QoS
High Value Projects
Flooding
BT21CN
Technical losses and other environmental
High impact Low Probability (HILP)
Critical National Infrastructure
Black Start
Rising Mains and Laterals
Undergrounding Within/ Outside designated areas
Worst Served Customers
Trouble Call / faults
ONIs
Inspections & Maintenance
Tree Cutting
NOC's Other
Network Design & Engineering
Project Management
Engineering Mgt & Clerical Support
System Mapping - Cartographical
Control Centre
Call Centre
Stores
Operational Training
Vehicles & Transport
Atypicals Non Sev Weather
Smart Meters
Network Policy
HR & Non-operational Training
Finance & Regulation
CEO
IT & Telecoms
Property Mgt
Non Op Capex
Note on C9: Ofgem: Check that this is the first year of investment across all options (including baseline). If this is not the first year of investment across all options hardcode the first year of investment in cell C9. For further guidance please refer to Appendix A of the Supplementary guidance: queries and clarification document.

## Workings template 2015.16
Workings / assumptions used for costing Option 2 | [15 empty] | Days to geny trip | 55
Use this sheet to provide details of assumptions and calculation methodology used in CBA model | [10 empty] | Planned Outage |  |  |  |  | Duration of genny trip | 4 | [8 empty] | Unplanned Outage
| BOLD RED = ESTIMATE | [9 empty] | CI |  | 5.58 |  |  | Staff cost | 500 | [8 empty] | CI |  | 11.15
[11 empty] | CHL |  | 7.8 | [12 empty] | CHL |  | 15.6
Live Line Harvesting | [8 empty] | Conventional Harvesting under outage with generation | [15 empty] | System Security Liability
Depot | Wodland name / ref | location | landowner details | date completed | Actual duration of works (days) | Live harvesting costs (contractor) | live harvesting costs (SSE) | Total costs | Customers | Duration of outage | CI's Assumed 2 disconections per customer | CHL's Based on the total estimated time to connect and disconnect generation | Cost of Generation | SSE Staff Cost | CI cost | CHL cost | Likelyhood of genny trip | Likely genny trip staff cost | Likely genny trip CICHL costs | Likely gen trip CI cost | Likely gen trip CHL cost | Number of likely Cis | Number Of likely CHL's | Total cost of generation | Customers Potentially Affected outside of outage area (number) | Estimated ERTS (Hours) based on access and staff coverage | Customer hours lost if fault occurs | CI cost | CHL cost | Total potential cost | Likelyhood | Number of likely CIs | Number of likely CHLs | Potential Cost vs likelyhood | Likely CI Cost | Likely CHL Cost | Potential total cost under generation | Potential saving
Argyll | Tarbert | Tarbert |  | 2015-05-08 | 5 | 10450 | 1305 | 11755 | 24 | 4 | 48 | 192 | 2685.7143 | 3244 | 267.84 | 1497.6 | 7.273% | 36.3636 | 128.3782 | 19.4618 | 108.9164 | 1.7455 | 6.9818 | 7859.8961 | 1839 | 4 | 7356 | 20504.85 | 114753.6 | 135258.45 | 5% | 91.95 | 367.8 | 6762.9225 | 1025.2425 | 5737.68 | 14622.8186 | 2867.8186
Argyll | Greenland CC1 | Cambeltown | Egger | 2015-05-22 | 7 | 8500 | 1827 | 10327 | 40 | 6 | 80 | 240 | 12955.3129 | 3094 | 446.4 | 1872 | 10.91% | 54.5455 | 320.9455 | 48.6545 | 272.2909 | 4.3636 | 17.4545 | 18743.2038 | 4811 | 6 | 28866 | 53642.65 | 450309.6 | 503952.25 | 5% | 240.55 | 1443.3 | 25197.6125 | 2682.1325 | 22515.48 | 43940.8163 | 33613.8163
Argyll | Greenland CC2 | Cambeltown | Egger | 2015-05-22 | 5 | 10000 | 1305 | 11305 | 0 | 0 | 0 | 0 | 0 | 2106 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 2106 | 4851 | 4 | 19404 | 54088.65 | 302702.4 | 356791.05 | 5% | 242.55 | 970.2 | 17839.5525 | 2704.4325 | 15135.12 | 19945.5525 | 8640.5525
Higland | Trinloist | Errogie | Forestry Commission | 2015-07-01 | 25 | 37500 | 6525 | 44025 | 34 | 21 | 68 | 34 | 41079.0863 | 7988 | 379.44 | 265.2 | 38.18% | 190.9091 | 954.8127 | 144.7473 | 810.0655 | 12.9818 | 51.9273 | 50857.4481 | 940 | 4 | 3760 | 10481 | 58656 | 69137 | 5% | 47 | 188 | 3456.85 | 524.05 | 2932.8 | 54314.2981 | 10289.2981
Argyll | Broadford Hospital | Skye | HIE | 2015-08-07 | 15 | 22500 | 3915 | 26415 | 89 | 14 | 178 | 356 | 59884.3529 | 5044 | 993.24 | 2776.8 | 25.45% | 127.2727 | 1666.2418 | 252.5982 | 1413.6436 | 22.6545 | 90.6182 | 70491.9075 | 89 | 8 | 712 | 992.35 | 11107.2 | 12099.55 | 5% | 4.45 | 35.6 | 604.9775 | 49.6175 | 555.36 | 71096.885 | 44681.885
Argyll | Ardchyline | Strachur | Scottish Woodlands | 2015-09-04 | 4 | 9300 | 1044 | 10344 | 118 | 5 | 236 | 708 | 10618.9916 | 3060 | 1316.88 | 5522.4 | 9.091% | 45.4545 | 788.9909 | 119.6091 | 669.3818 | 10.7273 | 42.9091 | 21352.7171 | 1350 | 5 | 6750 | 15052.5 | 40500 | 55552.5 | 5% | 67.5 | 337.5 | 2777.625 | 752.625 | 2025 | 24130.3421 | 13786.3421
Argyll | Pennyghael | Isle of Mull | Tilhill | 2015-09-11 | 4 | 12600 | 1044 | 13644 | 610 | 3 | 1220 | 4880 | 17784 | 3244 | 6807.6 | 38064 | 5.455% | 27.2727 | 2447.2091 | 370.9909 | 2076.2182 | 33.2727 | 133.0909 | 68374.0818 | 610 | 8 | 4880 | 6801.5 | 29280 | 36081.5 | 5% | 30.5 | 244 | 1804.075 | 340.075 | 1464 | 70178.1568 | 56534.1568
Argyll | Fank Cottage | Isle of Mull | Tilhill | 2015-09-18 | 7 | 18300 | 1827 | 20127 | 620 | 5 | 1240 | 2480 | 28572.1429 | 3444 | 6919.2 | 19344 | 9.091% | 45.4545 | 4145.5455 | 628.4545 | 3517.0909 | 56.3636 | 225.4545 | 62470.3429 | 620 | 8 | 4960 | 6913 | 29760 | 36673 | 5% | 31 | 248 | 1833.65 | 345.65 | 1488 | 64303.9929 | 44176.9929
Argyll | Kilfinichan | Isle of Mull | Dixons | 2015-09-25 | 9 | 22100 | 2349 | 24449 | 635 | 10 | 1270 | 2540 | 50180 | 3444 | 7086.6 | 19812 | 18.18% | 90.9091 | 8491.6818 | 1287.3182 | 7204.3636 | 115.4545 | 461.8182 | 89105.1909 | 635 | 8 | 5080 | 7080.25 | 30480 | 37560.25 | 5% | 31.75 | 254 | 1878.0125 | 354.0125 | 1524 | 90983.2034 | 66534.2034
Highland | Strome Carronach | Loch Carron | Tilhill | 2015-10-20 | 4 | 7200 | 1044 | 8244 | 91 | 3 | 130 | 130 | 22819.6155 | 5270 | 725.4 | 1014 | 5.455% | 27.2727 | 365.0755 | 55.3445 | 309.7309 | 4.9636 | 19.8545 | 30221.3636 | 91 | 4 | 364 | 1014.65 | 2184 | 3198.65 | 5% | 4.55 | 18.2 | 159.9325 | 50.7325 | 109.2 | 30381.2961 | 22137.2961
Argyll | Dallinlongart | Strachur | Tilhill | 2015-11-30 | 15 | 22500 | 3915 | 26415 | 22000 | 8 | 22000 | 44000 | 347925.6303 | 20128 | 122760 | 343200 | 14.55% | 72.7273 | 235360 | 35680 | 199680 | 3200 | 12800 | 1069446.3575 | 22000 | 4 | 88000 | 245300 | 528000 | 773300 | 5% | 1100 | 4400 | 38665 | 12265 | 26400 | 1108111.3575 | 1081696.3575
Highland | Kirkton Wood | Loch Carron | Munros timber | 2015-12-15 | 4 | 7500 | 1044 | 8544 | 591 | 1 | 1182 | 591 | 54689 | 5782 | 6595.56 | 4609.8 | 1.818% | 9.0909 | 790.3282 | 119.8118 | 670.5164 | 10.7455 | 42.9818 | 72475.7791 | 63301 | 4 | 253204 | 705806.15 | 1519224 | 2225030.15 | 5% | 3165.05 | 12660.2 | 111251.5075 | 35290.3075 | 75961.2 | 183727.2866 | 175183.2866
Argyll | Glen Douglas | Glen Douglas | Tilhill | 2016-02-26 | 15 | 25000 | 3915 | 28915 | [9 empty] | 0 | [19 empty] | -28915
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
| Total Litres of diesel used by harvester per day |  | 200 |  |  |  | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
| Total number of days used |  | 119 |  |  |  | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
| Total Litres of diesel used by harvester |  | 23800 |  |  |  | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
| CO2e |  | 2.6761 |  |  |  | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
| Total CO2 emitted (kg co2e) |  | 63692.132 |  |  |  | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
| Total CO2 emitted (tonnes co2e) |  | 63.6921 |  |  |  | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[7 empty] | 0 | 0 | [6 empty] | 0 | 0 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0
[8 empty] | 244509 |  | 80 | 27652 | 56151 | 649193.8466 | 65848 | 154298.16 | 437977.8 |  | 727.2727 | 255459.2091 | 38726.9909 | 216732.2182 | 3473.2727 | 13893.0909 | 1563504.2884 | [5 empty] | 4244634.35 |  | 5056.85 | 21166.8 | 212231.7175 | 56383.8775 | 155847.84 | 1775736.0059 | 1531227.0059
|  |  | No of days completed to date |  | 119 | [6 empty] | Generation total |  | 715769.1193 | [13 empty] | Network Sec Total |  | 4244634.35 |  |  |  | 212231.7175
|  |  | LLH Costs to date |  |  | 213450 | [5 empty] | Average Per day |  | 6014.8665 | [13 empty] | Average per day |  | 35669.1962 |  |  |  | 1783.4598
|  |  | Average costs per day |  |  | 1793.6975
[12 empty] | CI/CHL Total |  |  |  | 847735.1691
[12 empty] | Average per day |  |  |  | 7123.825 | [11 empty] | Number of likely CI's |  | 5056.85
[28 empty] | Number of likely CHL's |  | 21166.8
[12 empty] | Number of generation related CIs |  |  | 3473.2727 | [12 empty] | Cost of likely CI's |  | 56383.8775
|  |  | Ofgem CBA Figure | [8 empty] | Number of generation related CHLs |  |  | 13893.0909 | [12 empty] | Cost of likely CHL's |  | 155847.84
| Total Cost of diesel | 11900 | 0.0119 | *£0.5 used as cost of diesel per litre (same as workings baseline)
| Investment Tree Cutting | 256409 | 0.25641 | [8 empty] | Total Cost of generation (excluding CI / CMLs) |  |  | 715769.1193
| CO2 Emitted | 63692.132 | 63.6921 | [8 empty] | Total Cost of CIs |  |  | 249409.0284
[12 empty] | Total Cost of CHLs |  |  | 810557.8582
1775736.0059
Note on R1: Stirling, Graham: Advice from Geny desk. A geny will trip every 50 to 60 days.

## Workings template 2016.17
| Workings / assumptions used for costing Baseline | [16 empty] | Days to geny trip | 55
| Use this sheet to provide details of assumptions and calculation methodology used in CBA model | [11 empty] | Planned Outage |  |  |  |  | Duration of genny trip | 4 | [8 empty] | Unplanned Outage
|  | BOLD RED = ESTIMATE | [10 empty] | CI |  | 5.58 |  |  | Staff cost | 500 | [8 empty] | CI |  | 11.15
[13 empty] | CHL |  | 7.8 | [12 empty] | CHL |  | 15.6
[5 empty] | Monthly hire Rate |  |  |  | 24000
[5 empty] | SSE supervisor |  |  |  | 261 | [18 empty] | Likelyhood |  | 5%
[5 empty] | Potential availability (days per year) |  |  |  | 230
[5 empty] | Days unavailable (off hire) |  |  |  | 20
[5 empty] | Months available |  |  |  | 11
| Live Line Harvesting | [9 empty] | Conventional Harvesting under outage with generation | [15 empty] | System Security Liability
Month | Depot | Wodland name / ref | location | landowner details | date completed | Duration | Total days utilised | Utilisation | Machine Costs | Harmony Cost including Fuel, Accomodatiom, Staff costs and Sundries | Customers | Duration of outage | CI's Assumed 2 disconections per customer | CHL's Based on the total estimated time to connect and disconnect generation | Cost of Generation | SSE Staff Cost | CI cost | CHL cost | Likelyhood of genny trip | Likely genny trip staff cost | Number of likely Cis | Number Of likely CHL's | Likely gen trip CI cost | Likely gen trip CHL cost | Likely genny trip CICHL costs | Total cost of generation | Customers Potentially Affected outside of outage area (number) | Estimated ERTS (Hours) based on access and staff coverage | Customer hours lost if fault occurs | CI cost | CHL cost | Total potential cost | Likelyhood | Number of likely CIs | Number of likely CHLs | Potential Cost vs likelyhood | Likely CI Cost | Likely CHL Cost | Potential total cost under generation | Potential saving | Likely total cost under generation | Minimum saving
2016-04-01 | Argyll | Ardmarnock | Loch Ascog | RTS | 2016-04-22 | 18 |  |  | 24000 | 279.5 | 24 | 18 | 48 | 192 | 43582 | 3244 | 267.84 | 1497.6 | 32.73% | 163.6364 | 7.8545 | 31.4182 | 87.5782 | 490.1236 | 577.7018 | 49332.7782 | 500 | 4 | 2000 | 5575 | 31200 | 36775 | 5% | 25 | 100 | 1838.75 | 278.75 | 1560 | 86107.7782 | 49832.9568 | 51171.5282 | 14896.7068
[5 empty] | Planning | 0 | [33 empty] | 0 |  | 0
[5 empty] | Total |  | 18 | 94.29%
2016-05-01 | Off Hire for entire month due to operator and supervisor leave + workshop time. |  |  |  |  | 0 |  |  | 0 | 2103.72 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 5% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Planning | 0 | [33 empty] | 0 |  | 0
[5 empty] | Total |  | 0 | [32 empty] | 0 |  | 0
2016-07-01 | North east | Tillypronnie Estate | Tarland | Tillypronie sawmill |  | 20 |  |  | 24000 | 25118.33 | 8 | 20 | 8 | 32 | 46956.0869 | 26296 | 44.64 | 249.6 | 36.36% | 181.8182 | 2.9091 | 11.6364 | 32.4364 | 181.5273 | 213.9636 | 73942.1087 | 2392 | 4 | 9568 | 26670.8 | 149260.8 | 175931.6 | 5% | 119.6 | 478.4 | 8796.58 | 1333.54 | 7463.04 | 249873.7087 | 209568.3515 | 82738.6887 | -397566.6685
[5 empty] | Planning | 0 | [33 empty] | 0 |  | 0
[5 empty] | Total |  | 20 | 104.8%
2016-08-01 | North east | Tillypronnie Estate | Tarland | Tillypronie Coro' wood | 2016-08-19 | 15 |  |  | 24000 | 17459.27 | 0 | 10 | 0 | 0 | 5000 | 0 | 0 | 0 | 18.18% | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 2392 | 4 | 9568 | 26670.8 | 149260.8 | 175931.6 | 5% | 119.6 | 478.4 | 8796.58 | 1333.54 | 7463.04 | 180931.6 | 150702.5821 | 13796.58 | -16432.4379
| Tayside | Kinniard Village | Kinniard | Willy Laing | 2016-08-26 | 4 |  |  |  |  | 25 | 10 | 50 | 300 | 5402 | 5370 | 279 | 2340 | 18.18% | 90.9091 | 4.5455 | 18.1818 | 50.6818 | 283.6364 | 334.3182 | 13816.2273 | 120 | 4 | 480 | 1338 | 7488 | 8826 | 5% | 6 | 24 | 441.3 | 66.9 | 374.4 | 22642.2273 | 14581.1558 | 14257.5273 | 6196.4558
| Argyll | Achnaba | Achnaba | Scottish Woodlands | 2016-08-31 | 2 |  |  |  |  | 115 | 3 | 230 | 1150 | 16845 | 2440 | 1283.4 | 8970 | 5.455% | 27.2727 | 6.2727 | 25.0909 | 69.9409 | 391.4182 | 461.3591 | 30027.0318 | 6728 | 5 | 33640 | 75017.2 | 524784 | 599801.2 | 5% | 336.4 | 1682 | 29990.06 | 3750.86 | 26239.2 | 629828.2318 | 625797.6961 | 60017.0918 | 55986.5561
[5 empty] | Planning | 0 | [33 empty] | 0 |  | 0
[5 empty] | Total |  | 21 | 110%
2016-09-01 | Perth | Drymen | Gortocharn | Egger | 2016-09-30 | 6 |  |  | 24000 | 4076.39 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5091 | 4 | 20364 | 56764.65 | 317678.4 | 374443.05 | 5% | 254.55 | 1018.2 | 18722.1525 | 2838.2325 | 15883.92 | 374443.05 | 362351.4429 | 18722.1525 | 6630.5454
[5 empty] | Planning | 2 | [33 empty] | -4030.5357 |  | -4030.5357
[5 empty] | Total |  | 8 | 41.9%
2016-10-01 | Argyll | Cnochan A Chorra | Kames | Scottish Woodlands | 2016-10-10 | 5 |  |  | 24000 | 16436.36 | 30 | 8 | 60 | 240 | 71100 | 11560 | 334.8 | 1872 | 14.55% | 72.7273 | 4.3636 | 17.4545 | 48.6545 | 272.2909 | 320.9455 | 85260.4727 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 85260.4727 | 75184.1334 | 85260.4727 | 75184.1334
| Argyll | Kyles View | Glendaruel | Euroforest | 2016-10-26 | 8 |  |  |  |  | 122 | 8 | 244 | 984 | 33557.9337 | 7376 | 1361.52 | 7675.2 | 14.55% | 72.7273 | 17.7455 | 70.9818 | 197.8618 | 1107.3164 | 1305.1782 | 51348.5592 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 51348.5592 | 35226.4163 | 51348.5592 | 35226.4163
[5 empty] | Planning | 4 | [33 empty] | -8061.0714 |  | -8061.0714
[5 empty] | Total |  | 17 | 89.05%
2016-11-01 | Argyll | Hells Glen | Ardno | DSH Woodlands | 2016-11-15 | 12 |  |  | 24000 | 5711.97 | 513 | 10 | 1026 | 4104 | 59268.5714 | 9476 | 5725.08 | 32011.2 | 18.18% | 90.9091 | 93.2727 | 373.0909 | 1039.9909 | 5820.2182 | 6860.2091 | 113431.9696 | 513 | 4 | 2052 | 5719.95 | 32011.2 | 37731.15 | 5% | 25.65 | 102.6 | 1886.5575 | 285.9975 | 1600.56 | 151163.1196 | 126979.9053 | 115318.5271 | 91135.3128
[5 empty] | Planning | 5 | [33 empty] | -10076.3393 |  | -10076.3393
[5 empty] | Total |  | 17 | 89.05% | [17 empty] | 0
2016-12-01 | Tayside | Ardoch | Murthly | Adam Ritchie | 2016-12-21 | 8 |  |  | 24000 | 6101.89 | 6 | 14 | 12 | 96 | 21036.9097 | 5120 | 66.96 | 748.8 | 25.45% | 127.2727 | 1.5273 | 6.1091 | 17.0291 | 95.3018 | 112.3309 | 27212.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 27212.2734 | 11090.1305 | 27212.2734 | 11090.1305
[5 empty] | Planning | 5 | [32 empty] | 0 | -10076.3393 | 0 | -10076.3393
[39 empty] | 0 | 0 | 0 | 0
[7 empty] | 13 | 68.1% | [8 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 5% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
2017-01-01 | Argyll | Littleport | St Fillans | RTS | 2017-01-07 | 4 |  |  | 24000 | 8259.19 | 245 | 12 | 490 | 1960 | 14099.4286 | 7088 | 2734.2 | 15288 | 21.82% | 109.0909 | 53.4545 | 213.8182 | 596.0182 | 3335.5636 | 3931.5818 | 43250.3013 | 845 | 6 | 5070 | 9421.75 | 79092 | 88513.75 | 5% | 42.25 | 253.5 | 4425.6875 | 471.0875 | 3954.6 | 131764.0513 | 123702.9799 | 47675.9888 | 39614.9174
| Tayside | Tiroran | Isle Of Mull | Tilhill | 2017-01-27 | 17 |  |  |  |  | 645 | 14 | 1290 | 5160 | 85888 | 17104 | 7198.2 | 40248 | 25.45% | 127.2727 | 164.1818 | 656.7273 | 1830.6273 | 10244.9455 | 12075.5727 | 162641.0455 | 645 | 6 | 3870 | 7191.75 | 60372 | 67563.75 | 5% | 32.25 | 193.5 | 3378.1875 | 359.5875 | 3018.6 | 230204.7955 | 195945.2419 | 166019.233 | 131759.6794
[39 empty] | 0 | 0 | 0 | 0
[7 empty] | 21 | 110% | [8 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 5% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
2017-02-01 | Highland | Dalchork | Lairg | Forestry Commission | 2017-02-23 | 14 |  |  | 24000 | 13018.38 | 927 | 18 | 0 | 0 | 194420 | 22992 | 0 | 0 | 32.73% | 163.6364 | 303.3818 | 1213.5273 | 3382.7073 | 18931.0255 | 22313.7327 | 239889.3691 | 927 | 8 | 7416 | 10336.05 | 115689.6 | 126025.65 | 5% | 46.35 | 370.8 | 6301.2825 | 516.8025 | 5784.48 | 365915.0191 | 337701.2691 | 246190.6516 | 217976.9016
[5 empty] | Planning | 3 | [26 empty] | 5% | [5 empty] | 0 | -6045.8036 | 0 | -6045.8036
[33 empty] | 5% | [5 empty] | 0 | 0 | 0 | 0
[7 empty] | 17 | 89.05% | [8 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 5% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
2017-03-01 | Highland | Achfarry | Lairg | Euroforest | 2017-03-10 | 11 |  |  | 24000 | [7 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -22167.9464 | 0 | -22167.9464
|  | Shinnach | Strathdon | James Jones | 2017-03-31 | 5 |  |  |  |  | 30 | 5 | 70 | 140 | 36359 | 3100 | 390.6 | 1092 | 9.091% | 45.4545 | 2.7273 | 10.9091 | 30.4091 | 170.1818 | 200.5909 | 41187.6455 | 35 | 2 | 70 | 390.25 | 1092 | 1482.25 | 5% | 1.75 | 3.5 | 74.1125 | 19.5125 | 54.6 | 42669.8955 | 32593.5562 | 41261.758 | 31185.4187
[33 empty] | 5% | [5 empty] | 0 | 0 | 0 | 0
[7 empty] | 16 | 83.81% | [8 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 168 | 88% | 240000 | 98565 |  | 160 | 3528 | 14358 | 633514.9303 | 121166 | 19686.24 | 111992.4 |  | 1272.7273 | 662.2364 | 2648.9455 | 7383.9355 | 41323.5491 | 48707.4845 | 936339.7821 | 20188 |  | 94098 | 225096.2 | 1467928.8 | 1693025 |  | 1009.4 | 4704.9 | 84651.25 | 11254.81 | 73396.44 | 2629364.7821 | 2290799.7821 | 1020991.0321 | 242426.0321
[5 empty] | Machine Days |  |  |  | 168 |  |  |  | Generation total |  |  | 804661.1421 | [13 empty] | Network Sec Total |  | 1693025 |  |  |  | 84651.25
[5 empty] | Total Cost |  |  |  | 338565 |  |  |  | Average Per day |  |  | 5029.1321 | [13 empty] | Average per day |  | 10077.5298 |  |  |  | 503.8765
[5 empty] | Cost per day |  |  |  | 2015.2679
[13 empty] | CI/CHL Total |  |  | 180386.1245
[5 empty] | Total available days per year |  |  |  | 230 |  |  |  | Average per day |  |  | 1127.4133
[5 empty] | Utilisation To Date |  |  |  | 88%
|  | Total Litres of diesel used by harvester per day |  | 200
|  | Total number of days used |  | 168
|  | Total Litres of diesel used by harvester |  | 33600
|  | CO2e |  | 2.6761
|  | Total CO2 emitted (kg co2e) |  | 89918.304
|  | Total CO2 emitted (tonnes co2e) |  | 89.9183
CBA figures
|  | Total Cost of diesel | 16800 | 0.0168 | *£0.5 used as cost of diesel per litre (same as workings baseline). Note that fuel costs are already included in harmony costs and so are not added to "investment tree cutting costs" as in previous year.
|  | Investment Tree Cutting | 778565 | 0.77856
|  | CO2 Emitted | 89.9183 | 89.9183
Note on T1: Stirling, Graham: Advice from Geny desk. A geny will trip every 50 to 60 days.
Note on AQ20: Williams, Rhys (Future Networks): New live line harvester purchased in July
Note on P23: Stirling, Graham: HV set on standby

## Workings template 2017.18
|  | Workings / assumptions used for costing Baseline | [16 empty] | Days to geny trip | 55
|  | Use this sheet to provide details of assumptions and calculation methodology used in CBA model | [11 empty] | Planned Outage |  |  |  |  | Duration of genny trip | 4 | [8 empty] | Unplanned Outage
|  |  | BOLD RED = ESTIMATE | [10 empty] | CI |  | 6.01 |  |  | Staff cost | 500 | [8 empty] | CI |  | 12.02
[14 empty] | CHL |  | 8.415 | [12 empty] | CHL |  | 16.83
[6 empty] | Monthly hire Rate |  |  |  | 24000
[6 empty] | SSE supervisor |  |  |  | 261 | [18 empty] | Likelyhood |  | 5%
[6 empty] | Potential availability (days per year) |  |  |  | 500
[6 empty] | Days unavailable (off hire) |  |  |  | 0
[6 empty] | Months available |  |  |  | 12
| Live Line Harvester Costs | [10 empty] | Conventional Harvesting under outage with generation | [15 empty] | System Security Liability
Month | Machine Type | Depot | Woodland name / ref | location | landowner details | date completed | Duration | Total days utilised | Utilisation | Machine Costs | Harmony Cost including Fuel, Accomodatiom, Staff costs and Sundries | Customers | Duration of outage | CI's Assumed 2 disconections per customer | CHL's Based on the total estimated time to connect and disconnect generation | Cost of Generation | SSE Staff Cost | CI cost | CHL cost | Likelyhood of genny trip | Likely genny trip staff cost | Number of likely Cis | Number Of likely CHL's | Likely gen trip CI cost | Likely gen trip CHL cost | Likely genny trip CICHL costs | Total cost of generation | Customers Potentially Affected outside of outage area (number) | Estimated ERTS (Hours) based on access and staff coverage | Customer hours lost if fault occurs | CI cost | CHL cost | Total potential cost | Likelyhood | Number of likely CIs | Number of likely CHLs | Potential Cost vs likelyhood | Likely CI Cost | Likely CHL Cost | Potential total cost under generation | Potential saving | Likely total cost under generation | Minimum saving
April | Contract Harvester | NE | Conerock | Aberlour | Gordons | 2017-05-14 | 6 | 6 | 52.8% | 24000 | 6672.4 | 8 | 3 | 16 | 432 | 3722.736 | 2084 | 96.16 | 3635.28 | 5.455% | 27.2727 | 0.43636 | 1.7455 | 5.2451 | 29.376 | 34.6211 | 9600.0698 | 2472 | 4 | 9888 | 29713.44 | 166415.04 | 196128.48 | 5% | 123.6 | 494.4 | 9806.424 | 1485.672 | 8320.752 | 205728.5498 | 197026.5603 | 19406.4938 | 10704.5043
| Contract Harvester | TW | Balquidder | Balquidder | Tilhill | 2017-04-19 | 2 | 2 |  |  |  | 160 | 3 | 320 | 1920 | 18917.736 | 2900 | 1923.2 | 16156.8 | 5.455% | 27.2727 | 8.7273 | 34.9091 | 104.9018 | 587.52 | 692.4218 | 40617.4305 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 40617.4305 | 37716.7674 | 40617.4305 | 37716.7674
| SSE Harvester | TW | Rannoch | Rannoch Lodge | Tilhill/FCS | 2017-04-30 | 9 | 9 |  |  |  | 120 | 10 | 240 | 1016 | 49890.064 | 10696 | 1442.4 | 8549.64 | 18.18% | 90.9091 | 21.8182 | 87.2727 | 262.2545 | 1468.8 | 1731.0545 | 72400.0676 | 2100 | 8 | 16800 | 25242 | 282744 | 307986 | 5% | 105 | 840 | 15399.3 | 1262.1 | 14137.2 | 380386.0676 | 367333.0834 | 87799.3676 | 74746.3834
| SSE Harvester | Training | Marykirk | Workshop | Treetop Forestry | 2017-04-30 | 5 | 5 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -7251.6579 | 0 | -7251.6579
May | SSE Harvester | TW | Rannoch | Rannoch Lodge | Tilhill/FCS | 2017-05-05 | 4 | 4 | 55.2% | 24000 | 18462.72 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -5801.3263 | 0 | -5801.3263
| SSE Harvester | AS | Kennelhill | Lochgilphead | Egger | 2017-05-31 | 13 | 13 |  |  |  | 115 | 20 | 230 | 1380 | 89664.2656 | 20256 | 1382.3 | 11612.7 | 36.36% | 181.8182 | 41.8182 | 167.2727 | 502.6545 | 2815.2 | 3317.8545 | 126414.9383 | 874 | 6 | 5244 | 10505.48 | 88256.52 | 98762 | 5% | 43.7 | 262.2 | 4938.1 | 525.274 | 4412.826 | 225176.9383 | 206322.6278 | 131353.0383 | 112498.7278
| Contract Harvester | TW | Balquidder | Balquidder | Tilhill | 2017-05-04 | 1 | 1 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -1450.3316 | 0 | -1450.3316
| Contract Harvester | Training | Rannoch | Barracks | Treetop Forestry | 2017-05-20 | 5 | 5 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -7251.6579 | 0 | -7251.6579
June | SSE Harvester | AS | Kennelhill | Lochgilphead | Egger | 2017-06-09 | 7 | 7 | 88.8% | 24000 | 19321.94 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -10152.3211 | 0 | -10152.3211
| SSE Harvester | HI | Ord | Nairn | Tilhill | 2017-06-30 | 15 | 15 |  |  |  | 423 | 15 | 846 | 5076 | 88338.208 | 7388 | 5084.46 | 42714.54 | 27.27% | 136.3636 | 115.3636 | 461.4545 | 1386.6709 | 7766.28 | 9152.9509 | 152814.5225 | 569 | 8 | 4552 | 6839.38 | 76610.16 | 83449.54 | 5% | 28.45 | 227.6 | 4172.477 | 341.969 | 3830.508 | 236264.0625 | 214509.0889 | 156986.9995 | 135232.0259
| Contract Harvester | Training | Rannoch | Barracks | Treetop Forestry | 2017-06-25 | 15 | 15 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -21754.9737 | 0 | -21754.9737
July | SSE Harvester | AS | Argyll | Ormidale | Tilhill | 2017-07-28 | 20 | 20 | 74.4% | 24000 | 22425.29 | 508 | 25 | 1016 | 4064 | 63925 | 8068 | 6106.16 | 34198.56 | 45.45% | 227.2727 | 230.9091 | 923.6364 | 2775.5273 | 15544.8 | 18320.3273 | 130845.32 | 602 | 12 | 7224 | 7236.04 | 121579.92 | 128815.96 | 5% | 30.1 | 361.2 | 6440.798 | 361.802 | 6078.996 | 259661.28 | 230654.6484 | 137286.118 | 108279.4864
| SSE Harvester | HI | Nairn | Balnafoich | Cawdor | 2017-07-31 | 1 | 1 |  |  |  | 62 | 10 | 124 | 496 | 46298.4 | 39480 | 745.24 | 4173.84 | 18.18% | 90.9091 | 11.2727 | 45.0909 | 135.4982 | 758.88 | 894.3782 | 91682.7673 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 91682.7673 | 90232.4357 | 91682.7673 | 90232.4357
| Contract Harvester | Training | Rannoch | Barracks | Treetop Forestry | 2017-07-28 | 10 | 10 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -14503.3158 | 0 | -14503.3158
August | Contract Harvester | HI | Nairn | Balnafoich | Cawdor | 2017-08-11 | 11 | 11 | 81.6% | 24000 | 12310.98 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -15953.6474 | 0 | -15953.6474
| Contract Harvester | AS | Argyll | Ardlamont | Euroforest | 2017-08-18 | 5 | 5 |  |  |  | 30 | 10 | 60 | 360 | 34745.536 | 14344 | 360.6 | 3029.4 | 18.18% | 90.9091 | 5.4545 | 21.8182 | 65.5636 | 367.2 | 432.7636 | 53003.2087 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 53003.2087 | 45751.5508 | 53003.2087 | 45751.5508
| SSE Harvester | Training | Nairn | Balnafoich | Cawdor | 2017-08-31 | 18 | 18 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -26105.9684 | 0 | -26105.9684
September | Contract Harvester | AS | Argyll | Ardlamont | Euroforest | 2017-09-08 | 5 | 5 | 84% | 24000 | 9337.4 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -7251.6579 | 0 | -7251.6579
| Contract Harvester | AS | Argyll | Ormidale | Tilhill | 2017-09-22 | 10 | 10 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -14503.3158 | 0 | -14503.3158
| Contract Harvester | HI | Nairn | Barevan | Gordons | 2017-09-29 | 5 | 5 |  |  |  | 90 | 10 | 180 | 1080 | 64089.12 | 9064 | 1081.8 | 9088.2 | 18.18% | 90.9091 | 16.3636 | 65.4545 | 196.6909 | 1101.6 | 1298.2909 | 84712.32 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 84712.32 | 77460.6621 | 84712.32 | 77460.6621
| SSE Harvester | Training | Nairn | Barevan | Gordons | 2017-09-29 | 15 | 15 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -21754.9737 | 0 | -21754.9737
October | Contract Harvester | NE | Nairn | Barevan | Gordons | 2017-10-06 | 5 | 5 | 48% | 24000 | 20164.38 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -7251.6579 | 0 | -7251.6579
| Contract Harvester | NE | North East | Kildrummy | James Jones | 2017-10-13 | 5 | 5 |  |  |  | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 27.27% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5312 | 12 | 63744 | 63850.24 | 1072811.52 | 1136661.76 | 5% | 265.6 | 3187.2 | 56833.088 | 3192.512 | 53640.576 | 1136661.76 | 1129410.1021 | 56833.088 | 49581.4301
| Contract Harvester | AS | Argyll | Lindsaig | Tilhill | 2017-10-20 | 5 | 5 |  |  |  | 36 | 4 | 72 | 288 | 13985.912 | 2084 | 432.72 | 2423.52 | 7.273% | 36.3636 | 2.6182 | 10.4727 | 31.4705 | 176.256 | 207.7265 | 19170.2422 | 247 | 8 | 1976 | 2968.94 | 33256.08 | 36225.02 | 5% | 12.35 | 98.8 | 1811.251 | 148.447 | 1662.804 | 55395.2622 | 48143.6043 | 20981.4932 | 13729.8353
| Contract Harvester | AS | Argyll | Ardlamont | Scottish Woodlands | 2017-10-27 | 5 | 5 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -7251.6579 | 0 | -7251.6579
| Contract Harvester | TS | Tayside | Inver | Forestry Commission | 2017-10-31 | 2 | 2 |  |  |  | 204 | 15 | 406 | 1632 | 50648.68 | 5916 | 2440.06 | 13733.28 | 27.27% | 136.3636 | 55.6364 | 222.5455 | 668.7491 | 3745.44 | 4414.1891 | 77288.5727 | 328 | 4 | 1312 | 3942.56 | 22080.96 | 26023.52 | 5% | 16.4 | 65.6 | 1301.176 | 197.128 | 1104.048 | 103312.0927 | 100411.4296 | 78589.7487 | 75689.0856
November | Contract Harvester | TS | Tayside | Inver | Forestry Commission | 2017-11-10 | 8 | 8 | 81.6% | 24000 | 12885.99 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -11602.6526 | 0 | -11602.6526
| Contract Harvester | AN | Argyll | Dalmally | Scottish Woodlands | 2017-11-30 | 14 | 14 |  |  |  | 138 | 24 | 276 | 2208 | 71995.1328 | 6432 | 1658.76 | 18580.32 | 43.64% | 218.1818 | 60.2182 | 240.8727 | 723.8225 | 4053.888 | 4777.7105 | 103662.1052 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 103662.1052 | 83357.4631 | 103662.1052 | 83357.4631
| SSE Harvester | Training | Highland | Roy Bridge | Tilhill | 2017-11-30 | 12 | 12 | [9 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -17403.9789 | 0 | -17403.9789
December | Contract Harvester | AN | Argyll | Dalmally | Scottish Woodlands | 2017-12-08 | 6 | 6 | 50.4% | 24000 | 14490.63 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -8701.9895 | 0 | -8701.9895
| SSE Harvester | NE | Highland | Roy Bridge | Tilhill | 2017-12-15 | 10 | 10 |  |  |  | 252 | 10 | 504 | 2016 | 57857.296 | 5416 | 3029.04 | 16964.64 | 18.18% | 90.9091 | 45.8182 | 183.2727 | 550.7345 | 3084.48 | 3635.2145 | 86993.0996 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 86993.0996 | 72489.7838 | 86993.0996 | 72489.7838
| Contract Harvester | AN | Argyll | Dalmally 2 | Egger | 2017-12-15 | 5 | 5 |  |  |  | 138 | 8 | 276 | 2208 | 27298.3776 | 4832 | 1658.76 | 18580.32 | 14.55% | 72.7273 | 20.0727 | 80.2909 | 241.2742 | 1351.296 | 1592.5702 | 54034.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 54034.7551 | 46783.0972 | 54034.7551 | 46783.0972
January | Contract Harvester | TS | Tayside | Duncrub | RTS | 2018-01-19 | 13 | 13 | 50.4% | 24000 | 22917.12 | 31 | 10 | 62 | 372 | 31235.472 | 3944 | 372.62 | 3130.38 | 18.18% | 90.9091 | 5.6364 | 22.5455 | 67.7491 | 379.44 | 447.1891 | 39220.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 39220.5702 | 20366.2597 | 39220.5702 | 20366.2597
| Contract Harvester | AS | Argyll | Clachaig | Micheal Swailes | 2018-01-31 | 8 | 8 |  |  |  | 16 | 10 | 32 | 192 | 1889.0944 | 1612 | 192.32 | 1615.68 | 18.18% | 90.9091 | 2.9091 | 11.6364 | 34.9673 | 195.84 | 230.8073 | 5630.8108 | 1774 | 8 | 14192 | 21323.48 | 238851.36 | 260174.84 | 5% | 88.7 | 709.6 | 13008.742 | 1066.174 | 11942.568 | 265805.6508 | 254202.9981 | 18639.5528 | 7036.9001
February | Contract Harvester | AS | Argyll | Clachaig | Micheal Swailes | 2018-02-09 | 7 | 7 | 48% | 24000 | 8031.22 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -10152.3211 | 0 | -10152.3211
| SSE Harvester | AS | Argyll | Rowardennan | Forestry Commission | 2018-02-23 | 10 | 10 |  |  |  | 13 | 10 | 26 | 156 | 29753.648 | 4712 | 156.26 | 1312.74 | 18.18% | 90.9091 | 2.3636 | 9.4545 | 28.4109 | 159.12 | 187.5309 | 36213.088 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 36213.088 | 21709.7722 | 36213.088 | 21709.7722
| SSE Harvester | AS | Argyll | Culdrain | Forestry Commission | 2018-02-28 | 3 | 3 |  |  |  | 6 | 3 | 12 | 72 | 1889.0944 | 1612 | 72.12 | 605.88 | 5.455% | 27.2727 | 0.32727 | 1.3091 | 3.9338 | 22.032 | 25.9658 | 4232.3329 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 4232.3329 | -118.6618 | 4232.3329 | -118.6618
March | Contract Harvester | NE | Moray | Culdrain | Forestry Commission | 2018-03-09 | 8 | 8 | 55.2% | 24000 | 13437.03 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -11602.6526 | 0 | -11602.6526
| Contract Harvester | TS | Tayside | Glen Eagles | Iggesund | 2018-03-16 | 5 | 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4034 | 8 | 32272 | 48488.68 | 543137.76 | 591626.44 | 5% | 201.7 | 1613.6 | 29581.322 | 2424.434 | 27156.888 | 591626.44 | 584374.7821 | 29581.322 | 22329.6641
| Contract Harvester | HI | Highland | Dores | Gordons | 2018-03-31 | 10 | 10 |  |  |  | 49 | 10 | 98 | 784 | 52880 | 4712 | 588.98 | 6597.36 | 18.18% | 90.9091 | 8.9091 | 35.6364 | 107.0873 | 599.76 | 706.8473 | 65576.0964 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 65576.0964 | 51072.7806 | 65576.0964 | 51072.7806
[8 empty] | 323 | 65.24% | 288000 | 180457.1 |  | 225 | 4796 | 25752 | 799023.7728 | 155552 | 28823.96 | 216703.08 |  | 1909.0909 | 656.6727 | 2626.6909 | 7893.2062 | 44207.208 | 52100.4142 | 1254112.3179 | [5 empty] | 2865853.56 | 2 | 915.6 | 7860.2 | 143292.678 | 11005.512 | 132287.166 | 4119965.8779 | 3651508.7779 | 1397404.9959 | 928947.8959
[6 empty] | Machine Days |  |  |  | 323 |  |  |  | Generation total |  |  | 1008585.2779 | [13 empty] | Network Sec Total |  | 2865853.56 |  |  |  | 143292.678
[6 empty] | Total Cost |  |  |  | 468457.1 |  |  |  | Average Per day |  |  | 4482.6012 | [13 empty] | Average per day |  | 8872.6116 |  |  |  | 443.6306
[6 empty] | Cost per day |  |  |  | 1450.3316
[14 empty] | CI/CHL Total |  |  | 297627.4542
[6 empty] | Total available days per year |  |  |  | 230 |  |  |  | Average per day |  |  | 1322.7887
[6 empty] | Utilisation To Date |  |  |  | 65.24%
|  | Total Litres of diesel used by harvester per day |  | 200
|  | Total number of days used |  | 323
|  | Total Litres of diesel used by harvester |  | 64600
|  | CO2e |  | 2.6761
|  | Total CO2 emitted (kg co2e) |  | 172878.644
|  | Total CO2 emitted (tonnes co2e) |  | 172.8786
CBA figures
|  | Total Cost of diesel | 32300 | 0.0323 | *£0.5 used as cost of diesel per litre (same as workings baseline). Note that fuel costs are already included in harmony costs and so are not added to "investment tree cutting costs" as in previous year.
|  | Investment Tree Cutting | 468457.1 | 0.46846
|  | CO2 Emitted | 172.8786 | 172.8786
Note on U1: Stirling, Graham: Advice from Geny desk. A geny will trip every 50 to 60 days.
Note on M36: Stirling, Graham: 3 windfarms only
Note on M50: Stirling, Graham: WindfarmCustome on 33kv. 11kv cut live due to proximity.

## Working template 2018.19
|  | Workings / assumptions used for costing Baseline | [16 empty] | Days to geny trip | 55
|  | Use this sheet to provide details of assumptions and calculation methodology used in CBA model | [11 empty] | Planned Outage |  |  |  |  | Duration of genny trip | 4 | [8 empty] | Unplanned Outage
|  |  | BOLD RED = ESTIMATE | [10 empty] | CI |  | 6.01 |  |  | Staff cost | 500 | [8 empty] | CI |  | 12.02
[14 empty] | CHL |  | 8.415 | [12 empty] | CHL |  | 16.83
[6 empty] | Monthly hire Rate |  |  |  | 24000
[6 empty] | SSE supervisor |  |  |  | 261 | [18 empty] | Likelyhood |  | 5%
[6 empty] | Potential availability (days per year) |  |  |  | 500
[6 empty] | Days unavailable (off hire) |  |  |  | 0
[6 empty] | Months available |  |  |  | 12
| Live Line Harvester Costs | [10 empty] | Conventional Harvesting under outage with generation | [15 empty] | System Security Liability
Month | Machine Type | Depot | Woodland name / ref | location | landowner details | date completed | Duration | Total days utilised | Utilisation | Machine Costs | Harmony Cost including Fuel, Accomodatiom, Staff costs and Sundries | Customers | Duration of outage | CI's Assumed 2 disconections per customer | CHL's Based on the total estimated time to connect and disconnect generation | Cost of Generation | SSE Staff Cost | CI cost | CHL cost | Likelyhood of genny trip | Likely genny trip staff cost | Number of likely Cis | Number Of likely CHL's | Likely gen trip CI cost | Likely gen trip CHL cost | Likely genny trip CICHL costs | Total cost of generation | Customers Potentially Affected outside of outage area (number) | Estimated ERTS (Hours) based on access and staff coverage | Customer hours lost if fault occurs | CI cost | CHL cost | Total potential cost | Likelyhood | Number of likely CIs | Number of likely CHLs | Potential Cost vs likelyhood | Likely CI Cost | Likely CHL Cost | Potential total cost under generation | Potential saving | Likely total cost under generation | Minimum saving
April | Contract Harvester |  | Dores | Dores |  |  | 5 | 5 | 48% | 24840 | 13424.25 | 132 | 5 | 264 | 2112 | 22972.296 | 7796 | 1586.64 | 17772.48 | 9.091% | 45.4545 | 12 | 48 | 144.24 | 807.84 | 952.08 | 51124.9505 | 234 | 8 | 1872 | 2812.68 | 31505.76 | 34318.44 | 5% | 11.7 | 93.6 | 1715.922 | 140.634 | 1575.288 | 85443.3905 | 75317.8451 | 52840.8725 | 42715.3271
| Contract Harvester |  | Ardlamont |  |  |  | 15 | 15 |  |  |  | 30 | 15 | 60 | 360 | 45118.304 | 14844 | 360.6 | 3029.4 | 27.27% | 136.3636 | 8.1818 | 32.7273 | 98.3455 | 550.8 | 649.1455 | 64137.8131 | 2472 | 6 | 14832 | 29713.44 | 249622.56 | 279336 | 5% | 123.6 | 741.6 | 13966.8 | 1485.672 | 12481.128 | 343473.8131 | 313097.1767 | 78104.6131 | 47727.9767
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | Contract Harvester |  | Ford | Argyll |  |  | 18 | 15 | 36% | 24840 | 11159.9 | 46 | 15 | 92 | 552 | 74270.096 | 14844 | 552.92 | 4645.08 | 27.27% | 136.3636 | 12.5455 | 50.1818 | 150.7964 | 844.56 | 995.3564 | 95443.816 | 432 | 6 | 2592 | 5192.64 | 43623.36 | 48816 | 5% | 21.6 | 129.6 | 2440.8 | 259.632 | 2181.168 | 144259.816 | 107807.8523 | 97884.616 | 61432.6523
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June |  |  | Cnoch na Dail - East |  |  |  | 18 | 18 | 43.2% | 24840 | 8819.44 | 147 | 18 | 294 | 2352 | 97515.8496 | 4744 | 1766.94 | 19792.08 | 32.73% | 163.6364 | 48.1091 | 192.4364 | 578.2713 | 3238.704 | 3816.9753 | 127799.4812 | 147 | 8 | 1176 | 1766.94 | 19792.08 | 21559.02 | 5% | 7.35 | 58.8 | 1077.951 | 88.347 | 989.604 | 149358.5012 | 112906.5375 | 128877.4322 | 92425.4685
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July |  |  | Cnoch na Dail - West |  |  |  | 15 | 13 | 31.2% | 24840 | 12243.89 | 147 | 15 | 294 | 2352 | 82088.208 | 4444 | 1766.94 | 19792.08 | 27.27% | 136.3636 | 40.0909 | 160.3636 | 481.8927 | 2698.92 | 3180.8127 | 111408.4044 | 147 | 8 | 1176 | 1766.94 | 19792.08 | 21559.02 | 5% | 7.35 | 58.8 | 1077.951 | 88.347 | 989.604 | 132967.4244 | 102590.7879 | 112486.3554 | 82109.7189
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August |  |  | Tarbert | Argyll |  |  | 5 | 5 | 55.2% | 24840 | 8345.61 | 3 | 5 | 6 | 36 | 16694 | 2356 | 36.06 | 302.94 | 9.091% | 45.4545 | 0.27273 | 1.0909 | 3.2782 | 18.36 | 21.6382 | 19456.0927 | 722 | 8 | 5776 | 8678.44 | 97210.08 | 105888.52 | 5% | 36.1 | 288.8 | 5294.426 | 433.922 | 4860.504 | 125344.6127 | 115219.0673 | 24750.5187 | 14624.9733
|  |  | The heights 33kv | Arran |  |  | 20 | 18 |  |  |  | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 32.73% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1303 | 8 | 10424 | 15662.06 | 175435.92 | 191097.98 | 5% | 65.15 | 521.2 | 9554.899 | 783.103 | 8771.796 | 191097.98 | 150595.7981 | 9554.899 | -30947.2829
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September |  |  | Garth Wood | Aberfeldy |  |  | 10 | 9 | 64.8% | 24840 | 19214.88 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 16.36% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1560 | 8 | 12480 | 18751.2 | 210038.4 | 228789.6 | 5% | 78 | 624 | 11439.48 | 937.56 | 10501.92 | 228789.6 | 208538.509 | 11439.48 | -8811.611
|  |  | The Heights 11kv | Arran |  |  | 20 | 18 |  |  |  | 83 | 20 | 166 | 996 | 117378.24 | 8120 | 997.66 | 8381.34 | 36.36% | 181.8182 | 30.1818 | 120.7273 | 362.7855 | 2031.84 | 2394.6255 | 137453.6836 | 1303 | 8 | 10424 | 15662.06 | 175435.92 | 191097.98 | 5% | 65.15 | 521.2 | 9554.899 | 783.103 | 8771.796 | 328551.6636 | 288049.4817 | 147008.5826 | 106506.4007
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October |  |  | Attadale | Loch Carron |  |  | 10 | 9 | 40.8% | 24840 | 18805.76 | 36 | 10 | 36 | 216 | 11927.296 | 4016 | 216.36 | 1817.64 | 18.18% | 90.9091 | 6.5455 | 26.1818 | 78.6764 | 440.64 | 519.3164 | 18587.5215 | 350 | 4 | 1400 | 4207 | 23562 | 27769 | 5% | 17.5 | 70 | 1388.45 | 210.35 | 1178.1 | 46356.5215 | 26105.4305 | 19975.9715 | -275.1195
|  |  | Tom Doune | Highland |  |  | 10 | 8 |  |  |  | 12 | 10 | 24 | 144 | 17854.592 | 4216 | 144.24 | 1211.76 | 18.18% | 90.9091 | 2.1818 | 8.7273 | 26.2255 | 146.88 | 173.1055 | 23690.6065 | 462 | 4 | 1848 | 5553.24 | 31101.84 | 36655.08 | 5% | 23.1 | 92.4 | 1832.754 | 277.662 | 1555.092 | 60345.6865 | 40094.5956 | 25523.3605 | 5272.2696
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November |  |  | Training | Highland |  |  | 20 | 0 | 0% | 24840 | 10686.93 | [6 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -40502.1819 | 0 | -40502.1819
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December |  |  | Craibstone |  |  |  | 5 | 5 | 36% | 24840 | 17177.23 | 8 | 5 | 432 | 3456 | 39619.5104 | 7792 | 2596.32 | 29082.24 | 9.091% | 45.4545 | 0.72727 | 2.9091 | 8.7418 | 48.96 | 57.7018 | 79193.2268 | 614 | 8 | 4912 | 7380.28 | 82668.96 | 90049.24 | 5% | 30.7 | 245.6 | 4502.462 | 369.014 | 4133.448 | 169242.4668 | 159116.9213 | 83695.6888 | 73570.1433
| SSE Harvester |  | Balmaha | Clackmannanshire |  |  | 5 | 5 |  |  |  | 114 | 8 | 228 | 1368 | 30833.8368 | 4532 | 1370.28 | 11511.72 | 14.55% | 72.7273 | 16.5818 | 66.3273 | 199.3135 | 1116.288 | 1315.6015 | 49636.1655 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 49636.1655 | 39510.6201 | 49636.1655 | 39510.6201
|  |  | Sandbank | Argyll |  |  | 5 | 5 |  |  |  | 187 | 8 | 374 | 2992 | 26728.5664 | 4632 | 2247.74 | 25177.68 | 14.55% | 72.7273 | 27.2 | 108.8 | 326.944 | 1831.104 | 2158.048 | 61016.7617 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 61016.7617 | 50891.2162 | 61016.7617 | 50891.2162
[30 empty] | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
January |  |  | Cruach Tarbiet | Argyll |  |  | 8 | 7 | 48% | 24840 | 9591.22 | 105 | 10 | 210 | 840 | 33699.12 | 4372 | 1262.1 | 7068.6 | 18.18% | 90.9091 | 19.0909 | 76.3636 | 229.4727 | 1285.2 | 1514.6727 | 48007.4018 | 402 | 6 | 2412 | 4832.04 | 40593.96 | 45426 | 5% | 20.1 | 120.6 | 2271.3 | 241.602 | 2029.698 | 93433.4018 | 77232.5291 | 50278.7018 | 34077.8291
|  |  | Brenfield |  |  |  | 4 | 3 |  |  |  | 8 | 5 | 16 | 512 | 5945.472 | 2900 | 96.16 | 4308.48 | 9.091% | 45.4545 | 0.72727 | 2.9091 | 8.7418 | 48.96 | 57.7018 | 13353.2684 | 187 | 6 | 1122 | 2247.74 | 18883.26 | 21131 | 5% | 9.35 | 56.1 | 1056.55 | 112.387 | 944.163 | 34484.2684 | 26383.832 | 14409.8184 | 6309.382
|  |  | Bridge of Gaur - 1 | Rannoch |  |  | 10 | 10 |  |  |  | 38 | 20 | 76 | 456 | 83783.776 | 4400 | 456.76 | 3837.24 | 36.36% | 181.8182 | 13.8182 | 55.2727 | 166.0945 | 930.24 | 1096.3345 | 93755.9287 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 93755.9287 | 73504.8378 | 93755.9287 | 73504.8378
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February |  |  | Bridge of Gaur - 1 | Rannoch |  |  | 5 | 5 | 79.2% | 24840 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | -10125.5455 | 0 | -10125.5455
| SSE Harvester |  | Kinloch Rannoch | Rannoch |  |  | 10 | 10 |  |  |  | 52 | 5 | 104 | 832 | 20641.416 | 7796 | 625.04 | 7001.28 | 9.091% | 45.4545 | 4.7273 | 18.9091 | 56.8218 | 318.24 | 375.0618 | 36484.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 36484.2524 | 16233.1614 | 36484.2524 | 16233.1614
| SSE Harvester |  | Callander | Stirlingshire |  |  | 5 | 5 |  |  |  | 12 | 5 | 24 | 1152 | 5204.56 | 2900 | 144.24 | 9694.08 | 9.091% | 45.4545 | 1.0909 | 4.3636 | 13.1127 | 73.44 | 86.5527 | 18074.8873 | 396 | 4 | 1584 | 4759.92 | 26658.72 | 31418.64 | 5% | 19.8 | 79.2 | 1570.932 | 237.996 | 1332.936 | 49493.5273 | 39367.9818 | 19645.8193 | 9520.2738
|  |  | Bridge of Gaur - 2 | Rannoch |  |  | 5 | 3 |  |  |  | 38 | 10 | 76 | 456 | 23781.888 | 5032 | 456.76 | 3837.24 | 18.18% | 90.9091 | 6.9091 | 27.6364 | 83.0473 | 465.12 | 548.1673 | 33746.9644 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 33746.9644 | 23621.4189 | 33746.9644 | 23621.4189
|  |  | Point sands | Argyll |  |  | 10 | 10 |  |  |  | 147 | 10 | 294 | 7938 | 52730.472 | 3944 | 1766.94 | 66798.27 | 18.18% | 90.9091 | 26.7273 | 106.9091 | 321.2618 | 1799.28 | 2120.5418 | 127451.1329 | 162 | 8 | 1296 | 1947.24 | 21811.68 | 23758.92 | 5% | 8.1 | 64.8 | 1187.946 | 97.362 | 1090.584 | 151210.0529 | 130958.962 | 128639.0789 | 108387.988
March |  |  | Tain |  |  |  | 15 | 15 | 48% | 24840 | 10000 | 28 | 15 | 56 | 336 | 5532 | 5532 | 336.56 | 2827.44 | 27.27% | 136.3636 | 7.6364 | 30.5455 | 91.7891 | 514.08 | 605.8691 | 14970.2327 | 2543 | 6 | 15258 | 30566.86 | 256792.14 | 287359 | 5% | 127.15 | 762.9 | 14367.95 | 1528.343 | 12839.607 | 302329.2327 | 271952.5963 | 29338.1827 | -1038.4537
|  |  | Bute |  |  |  | 5 | 5 |  |  |  | 45 | 5 | 90 | 360 | 34824.1646 | 4532 | 540.9 | 3029.4 | 9.091% | 45.4545 | 4.0909 | 16.3636 | 49.1727 | 275.4 | 324.5727 | 43296.4918 | 372 | 4 | 1488 | 4471.44 | 25043.04 | 29514.48 | 5% | 18.6 | 74.4 | 1475.724 | 223.572 | 1252.152 | 72810.9718 | 62685.4264 | 44772.2158 | 34646.6704
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 258 | 221 | 48.24% | 298080 | 149469.11 |  | 246 | 3216 | 29818 | 849143.6638 | 123744 | 19328.16 | 250918.47 |  | 1990.9091 | 289.4364 | 1157.7455 | 3479.0251 | 19484.856 | 22963.8811 | 1268089.084 | [5 empty] | 1715543.92 | 2.25 | 690.4 | 4603.6 | 85777.196 | 8298.608 | 77478.588 | 2983633.004 | 2461154.8574 | 1353866.28 | 831388.1334
[6 empty] | Machine Days |  |  |  | 221 |  |  |  | Generation total |  |  | 997842.454 | [13 empty] | Network Sec Total |  | 1715543.92 |  |  |  | 85777.196
[6 empty] | Total Cost |  |  |  | 447549.11 |  |  |  | Average Per day |  |  | 4056.2701 | [13 empty] | Average per day |  | 7762.6422 |  |  |  | 388.1321
[6 empty] | Cost per day |  |  |  | 2025.1091
[14 empty] | CI/CHL Total |  |  | 293210.5111
[6 empty] | Total available days per year |  |  |  | 230 |  |  |  | Average per day |  |  | 1191.9126
[6 empty] | Utilisation To Date |  |  |  | 48.24%
|  | Total Litres of diesel used by harvester per day |  | 200
|  | Total number of days used |  | 221
|  | Total Litres of diesel used by harvester |  | 44200
|  | CO2e |  | 2.6761
|  | Total CO2 emitted (kg co2e) |  | 118285.388
|  | Total CO2 emitted (tonnes co2e) |  | 118.2854
CBA figures
|  | Total Cost of diesel | 30940 | 0.03094
|  | Investment Tree Cutting | 447549.11 | 0.44755
|  | CO2 Emitted | 118.2854 | 118.2854
Note on U1: Stirling, Graham: Advice from Geny desk. A geny will trip every 50 to 60 days.