## Sheet1
Section | Change | Reason for change | Effect on losses | SSEN Opinion on Change
1.1 Challenges over RIIO-ED1 | Minor wording update | Minor sentence changes so that section reads better and reflects most up to date view of losses | None | Most up to date information has been supplied to create most accurate report
1.2 Smart meters | Minor wording update | Minor sentence changes so that section reads better and reflects most up to date view of losses | None | Most up to date information has been supplied to create most accurate report
1.3 Measures to be implemented | Changed wording from 'outperform' to 'exceed minimum' EU Eco Directive requirements for 'all voltages' | Wording change so that the EU Eco directive is followed for all transformers in case Directive is updated. This ensures future proofing. | None | The description "outperform" is deemed too broad and can lead to confusion. "Exceed minimum" requirements better reflects the policy that SSEN is taking
1.3 Measures to be implemented | Removed early replacement of pre 1960 transformers. | These transformers are being replaced based on health & criticality rather than solely from a losses perspective and we expect this will continue to be the main driver for replacement. | Reduction in reported losses (E4 losses submission) but not actual losses as this activity has not been taking place. | SSEN is not currently replacing pre 1960s transformers due to losses. It is replacing them as per CBRM methodology, which is deemed to provide more benefits for the customer
1.3 Measures to be implemented | Removed mitigating phase imbalance on low voltage networks | CBAs suggest this losses reduction activity produces very marginal benefits and requires a large amount of prior investigation work to locate optimal installation sites, hence the measure has not been used to date | Reduction in reported losses (E4 losses submission) but not actual losses as this activity has not been taking place. | CBAs suggest this losses reduction activity produces very marginal benefits and requires a large amount of prior investigation work to locate optimal installation sites. Presently this is not occurring due to unfavourable CBAs, but could be done in the future as part of a wider losses analysis project.
1.5 Non-technical losses | Numbers updated to reflect 2017/18. | Updated numbers show most up to date losses performance in 2017/18 | None | Most up to date information has been supplied to create most accurate report
1.6 Summary numbers | Section on replacement of historical secondary transformers removed | These transformers are being replaced based on health & criticality rather than solely from a losses perspective and we expect this will continue to be the main driver for replacement. | Reduction in reported losses (E4 losses submission) but not actual losses as this activity have not been taking place. | SSEN is not currently replacing pre 1960s transformers due to losses. It is replacing them as per CBRM methodology, which is deemed to provide more benefits for the customer
1.6 Summary numbers | Section on low voltage balancing equipment losses savings removed | CBAs suggest this losses reduction activity produces very marginal benefits and requires a large amount of prior investigation work to locate optimal installation sites, hence the measure has not been used to date | Reduction in reported losses (E4 losses submission) but not actual losses as this activity have not been taking place. | CBAs suggest this losses reduction activity produces very marginal benefits to the customer and requires a large amount of prior investigation work to locate optimal installation sites. Presently this is not occurring due to unfavourable CBAs, but could be done in the future as part of a wider losses analysis project.
1.6 Summary numbers | Low loss high voltage transformers replaced with Transformers that exceed eco directive. Forecast losses savings replaced with statement claiming this is the new baseline and so no forecast is generated. | Name change provides greater clarity. Losses saving forecasts removed as this is considered the new baseline (due to changes in legislation) | Reduction in reported losses (E4 losses submission), but complying with the EU Eco Directive ensures losses are as low as reasonably practicable | Wording has been changed to provide conformity and reduce confusion. The losses reduction numbers have been removed as the EU Eco directive is now considered the 'baseline'. Although losses are still being reduced, SSEN does not think it fair to represent loss reductions here as this is a new law that must be adhered to. Therefore the new baseline requirements mean CBAs are updated to reflect this change and show no change in losses reductions. It should be clearly stated here that losses will remain as low as reasonably practicable as SSEN is following best practice when it comes to replacing transformers in order to reduce losses.
1.6 Summary numbers | Added section on MWh savings for upsizing 500kVA and 50kVA transformers | This was missing from last years report | Increase in reported losses (E4 losses submission) | This better reflects the losses savings from upsizing transformers based upon most recent CBAs that was missing from last years report
1.6 Summary numbers | HV and LV cable losses forecast savings updated to reflect most recent CBAs | CBAs updated using more accurate data | Increase in LV cable losses reported and decrease in HV cable losses reported (E4 losses submission) | This uses the most up to date data and CBAs to reflect the most accurate forecasts
1.6 Summary numbers | Paragraph added on why losses associated with EU Eco transformer losses has been removed from the table | To provide an explanation as why the numbers have changed significantly from previous year | None | Provides additional clarity on how losses are kept as low as reasonably practicable even though reported losses (E4 losses submission) reductions appear lower.
1.6 Summary numbers | Total change in GWhrs of losses savings changed from 88GWhrs to 34GWhrs | This reflects a more accurate number of what is to be saved as a direct result of the losses strategy | Reduction in reported losses (E4 losses submission), but complying with the EU Eco Directive ensures losses are as low as reasonably practicable | There has been a reduction in reported losses (E4 losses submission) but overall no change in actual losses. We have not been installing LV balancers (1GWh of losses no longer forecast) as they are not cost effective. Historic transformers (13GWh of losses no longer forecast) have not been replaced due to losses, they are being replaced via the CBRM methodology, which provides greater customer benefit than replacing for losses alone. It should be noted that replacement of transformers via the CBRM methodology will still reduce losses as new transformers will be more efficient from a losses perspective. However, as losses isn’t the main reason for the change we are no longer including it within the strategy. The major reduction in the reporting of forecast losses is attributed to the removal of the section on transformers that exceed the EU Eco directive requirements (>40GWhrs of losses savings attributed here). These savings have been removed as the EU Eco Directive is considered the new baseline. Previously we calculated losses savings on a like for like transformer replacement vs a transformer replacement that exceeded the EU Eco Directive. Although significant losses savings reductions will still be realised by replacing transformers that exceed the EU Eco directive (keeping losses as low as reasonably practicable), we now consider this a regulatory requirement and thus haven't included the savings here as this requirement is the new 'baseline'.
2.3 Historical approach and performance | Graph and numbers updated to reflect 2017/18 changes. Paragraph added to explain changes. | Graph and number updated to show reported losses in 2017/18. | Reported annual losses reduced (as per line loss factor report) | Reflects more up to date data
3.1 Transformers | Lifetime of transformers decreased from 65 years to 60 years as per CNAIM methodology. Minor word updates to the rest of the section. | More accurate data used from CNAIM source and updated to reflect 2017/18 changes | None | Reflects more up to date data
3.1.1 Low loss transformers | Minor wording update | Minor sentence changes so that section reads better and reflects most up to date view of losses | 2017/18 update | Most up to date information has been supplied to create most accurate report
3.1.2 Replacement of historical transformers | Minor wording update | Wording has been updated to now show CBRM (health and criticality) is taken into account when replacing transformers. This is current practice and so ensures information provided is kept up to date. | 2017/18 update | Minor wording update to reflect that replacement of historical transformers due to losses may occur during RIIO-ED1. This will occur if a positive CBA can be produced that is more beneficial than the CBRM approach we currently employ.
3.2.1 Conductor type | Minor wording update | Minor sentence changes so that section reads better and reflects most up to date view of losses | 2017/18 update | Minor wording update so that sentence reads better
4 Potential methods of improving losses | Minor wording update to each section | Minor sentence changes so that section reads better and reflects most up to date view of losses | None | Most up to date information has been supplied to create most accurate report
5.1 Time of use tariffs | Section removed | Does not agree with smart metering strategy. | None | Most up to date information has been supplied to create most accurate report
6.1 Low loss transformers | Section updated to show we are applying this policy. Forecast savings removed. | Section updated to show we are still following the policy as before, but are no longer forecasting savings, as this is considered the new baseline. | Reduction in reported losses (E4 losses submission), but complying with the EU Eco Directive ensures losses are as low as reasonably practicable | Reflects most up to date policy implemented by SSEN. Losses remain as low as reasonably practicable as transformer replacement follows best practice for losses reductions
6.1 Minimum sizing of transformers | Section updated to show exclusions | Exclusions included to show that not all transformers must follow this policy as in some case it is not practical/feasible to do so. | None | Exclusions are necessary to show that in some cases it is not possible to obtain 100% compliance with this policy. Although losses are kept as low as reasonably practicable by following this policy for the majority of transformers.
6.1 Replacement of historical high loss transformers | Early replacement of pre 1960 transformers changed to amber with rationale for change included | These transformers are being replaced based on health & criticality rather than solely from a losses perspective and we expect this will continue to be the main driver for replacement. We have left this as amber as this policy will be reviewed to see if there is benefit to include it in the future. | Reduction in reported losses (E4 losses submission) from activities specifically targeting losses | SSEN is not currently replacing pre 1960s transformers due to losses. It is replacing them as per CBRM methodology, which is deemed to provide more benefits for the customer. We believe this method is most beneficial to the customer. We will review this policy over RIIO-ED1 to see if there is benefit for implementing it in specific situations.
6.1 Minimum sizing of LV and 11kV cables | Section updated to include exclusions. Forecast savings removed | 2017/18 update & forecasts included in tables so not repeated here. | None | Most up to date information has been supplied to create most accurate report
6.2 Low voltage static balancers | Section changed to amber with rationale for change included | CBAs suggest this losses reduction activity produces very marginal benefits and requires a large amount of prior investigation work to locate optimal installation sites, hence the measure has not been used to date. Possible to use this in the future if a positive business case can be found. | Reduction in reported losses (E4 losses submission) from activities specifically targeting losses | CBAs suggest this losses reduction activity produces very marginal benefits and requires a large amount of prior investigation work to locate optimal installation sites. Presently this is not occurring due to unfavourable CBAs, but could be done in the future as part of a wider losses analysis project.
6.2 Switching out of under utilised plant | Minor wording update | Minor sentence changes so that section reads better and reflects most up to date view of losses | None | Most up to date information has been supplied to create most accurate report
6.2 Power Quality | Minor wording update | Minor sentence changes so that section reads better and reflects most up to date view of losses | None | Most up to date information has been supplied to create most accurate report
6.2 Dedicated losses team | Section updated to reflect 2017/18 and colour changed to amber | Section updated to reflect most up to date view on losses teams with indication that this could still take place in the future. | None | SSEN believes that the creation of a losses team or network efficiency team could take place in the future to help identify areas where further reduction of losses can take place. This ensures best practice in keeping losses as low as reasonably practicable.
6.3 EV smart charging | Minor wording update | Updated section to show that DNOs may not be able to control power flows, but could still take place if this is done by 3rd parties. This reflects the most recent view in this specific area. | None | Most up to date information has been supplied to create most accurate report
6.3 Energy storage | Section removed | Storage can't be utilised by the DNO and so has been removed | None | Energy Storage is not considered to be a key part in the losses reduction strategy due to Regulatory restrictions and so this section has been removed.
7.1 Revenue protection team | Minor wording update | Minor sentence changes so that section reads better and reflects most up to date view of losses | None | Most up to date information has been supplied to create most accurate report
7.4 Identification of theft | Section updated to reflect 2017/18 | Section updated to reflect most up to date view on identification of theft | None | Most up to date information has been supplied to create most accurate report
8 Conclusions | Table updated as per section 1.6 | All numbers updated to reflect more accurate CBAs | Reduction in reported losses (E4 losses submission), but complying with the EU Eco Directive ensures losses are as low as reasonably practicable | This reflects the most up to date CBAs available