## Contents
SEPD Network Scenario Headroom Report 2026 Consultation Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations and Bulk Supply Points (BSP) up to 2050. In consultation version, SSEN have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN's best view of the future demand and generation needs on our network is aligned to the Holistic Transition scenario, moving from Consumer Transformation which was our best view in the 2024 NSHR. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Dem | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Gen | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
LEP Reference | This tab provides information on the LEPs, local authorities and the connected GSPs, BSPs and Primaries that support those areas
ESID | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
Mar 2026 Version 1.3

## Key Information
SEPD Network Scenario Headroom Report 2026 Consultation Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our other documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation or BSP as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. In order to identify future overloaded network assets, forecasts are created which combine our long term DFES projections with the estimated contribution from our connections pipeline after appropriate diversity factors have been applied. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SEPD. Please note that our DFES scenario naming convention has been updated since 2024 to more closely align with the updated NESO Future Energy Scenario (FES) pathways framework. Published annually, the FES framework outlines different scenarios for the future of the whole energy system. SSEN's DFES builds on the FES scenarios by engaging a diverse and expert range of stakeholders, undertaking detailed investigations into the pipeline of projects seeking to connect, and reflecting extensive industry and local area insight to forecast future load on SSEN’s network.
New DFES Scenario | Previous DFES Scenario | FES Pathway Description
Electric Engagement (EE) | Consumer Transformation (CT) | Net zero met through mainly electrified demand. Consumers are highly engaged in the energy transition through smart technologies that reduce energy demands, utilising technologies such as electric heat pumps and electric vehicles.
Holistic Transition (HT) | Leading the Way (LW) | Net zero met through a mix of electrification and hydrogen, with hydrogen mainly around industrial clusters. Consumer engagement in the transition is very strong with demand shifting, with smart homes and electric vehicles providing flexibility to the grid.
Hydrogen Evolution (HE) | System Transformation (ST) | Net zero met through fast progress for hydrogen in industry and heat. Many consumers will have hydrogen boilers, though energy efficiency will be key to reducing cost. There are low levels of consumer engagement. Hydrogen will be prevalent for heavy goods vehicles but electric car uptake is strong.
Counterfactual (CF) | Falling Short (FS) | Net zero missed, though some progress is made for decarbonisation compared to today. While home insulation improves, there is still a heavy reliance on gas across all sectors, particularly power and space heating. Electric vehicle uptake is slower than the net zero pathways, but still displaces petrol and diesel.
Mar 2026
Version 1.3

## BSP Generation Headroom
Scenario | Bulk Supply Point |  | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Generation (MVA) | Generation Headroom Winter (MVA) | [11 empty] | Generation Headroom Summer (MVA) | [11 empty] | Generation Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT BSP | MINIMUM HEADROOM | SU 85922 48779 | NO | YES | 0.42526 | 130.8168 | 128.6211 | 126.2779 | 123.7621 | 117.0084 | 111.4126 | 106.5305 | 101.9642 | 97.7411 | 80.0789 | 65.0326 | 51.7074 | 99.1032 | 92.8979 | 85.0568 | 76.8884 | 69.3284 | 63.2021 | 57.8663 | 52.8642 | 48.2453 | 28.9063 | 12.3305 | -2.5 | 107.0874 | 100.9126 | 93.0411 | 84.8674 | 77.2958 | 71.1642 | 65.82 | 60.8105 | 56.1779 | 36.7768 | 20.1253 | 5.2611
|  | ALDERSHOT BSP | EE |  |  |  |  | 132.1368 | 130.3326 | 128.4137 | 126.4158 | 123.1316 | 118.06 | 113.8189 | 109.76 | 106.0768 | 91.6316 | 80.0884 | 70.0642 | 101.7484 | 96.5179 | 89.8253 | 82.6537 | 75.9989 | 70.4063 | 65.7768 | 61.3484 | 57.3295 | 41.5474 | 28.8463 | 17.6379 | 109.6716 | 104.5937 | 97.8084 | 90.6305 | 83.9695 | 78.3705 | 73.7253 | 69.2821 | 65.2526 | 49.3747 | 36.5758 | 25.3316
|  | ALDERSHOT BSP | HT |  |  |  |  | 130.8168 | 128.6211 | 126.2779 | 123.7621 | 117.0084 | 111.4126 | 106.5305 | 101.9642 | 97.7411 | 80.0789 | 65.0326 | 51.7074 | 99.1032 | 92.8979 | 85.0568 | 76.8884 | 69.3284 | 63.2021 | 57.8663 | 52.8642 | 48.2453 | 28.9063 | 12.3305 | -2.5 | 107.0874 | 100.9126 | 93.0411 | 84.8674 | 77.2958 | 71.1642 | 65.82 | 60.8105 | 56.1779 | 36.7768 | 20.1253 | 5.2611
|  | ALDERSHOT BSP | HE |  |  |  |  | 133.8253 | 132.54 | 131.1221 | 129.6 | 127.9568 | 126.2768 | 122.9842 | 119.8295 | 117.0379 | 106.9432 | 99.5432 | 93.1947 | 105.1989 | 101.0284 | 95.7842 | 89.7011 | 84.0053 | 79.4032 | 75.7305 | 72.2758 | 69.2137 | 58.1147 | 49.8789 | 42.7137 | 112.2526 | 109.0021 | 103.8137 | 97.6832 | 91.9789 | 87.3758 | 83.6947 | 80.2337 | 77.1621 | 66.0274 | 57.7621 | 50.5695
|  | ALDERSHOT BSP | CF |  |  |  |  | 134.9821 | 134.3 | 133.5884 | 132.8568 | 132.0853 | 131.3021 | 130.5305 | 129.7695 | 129.0084 | 125.5968 | 122.7242 | 118.2337 | 108.1 | 105.8874 | 103.4379 | 101.0232 | 98.7937 | 96.6095 | 94.5621 | 92.4895 | 90.4347 | 81.7 | 75.6326 | 70.5453 | 113.4337 | 112.7389 | 111.3516 | 109.0116 | 106.8432 | 104.6526 | 102.5621 | 100.4632 | 98.4074 | 89.6579 | 83.5716 | 78.4684
FLEET-BRAMLEY GSP | ALTON BSP | ALTON BSP | MINIMUM HEADROOM | SU 72730 39772 | NO | YES | 89.5653 | -26.4084 | -39.4116 | -48.5547 | -70.9326 | -75.8116 | -93.8116 | -111.1526 | -142.2674 | -145.3558 | -174.2579 | -196.7368 | -215.5284 | -81.8926 | -97.7968 | -107.7589 | -133.7147 | -138.9537 | -158.7453 | -180.5653 | -216.8379 | -220.1589 | -250.1126 | -274.3368 | -295.1663 | -77.3189 | -93.2474 | -103.2179 | -129.1326 | -134.4358 | -154.2095 | -176.0347 | -212.2979 | -215.6726 | -246.4758 | -271.4053 | -292.5032
|  | ALTON BSP | EE |  |  |  |  | 35.8832 | -10.0895 | -48.5547 | -70.9326 | -75.8116 | -80.6389 | -100.6842 | -132.9768 | -137.2537 | -158.6663 | -179.4137 | -194.5958 | -0.81895 | -62.8642 | -107.7589 | -133.7147 | -138.9537 | -144.1 | -167.1547 | -204.62 | -209.1368 | -231.7495 | -254.4537 | -271.2579 | 4.7579 | -58.3958 | -103.2179 | -129.1326 | -134.4358 | -139.6821 | -162.8084 | -200.3263 | -204.9726 | -228.4505 | -252.2916 | -269.3937
|  | ALTON BSP | HT |  |  |  |  | -26.4084 | -31.6611 | -36.9284 | -42.2189 | -48.1989 | -93.8116 | -101.2053 | -106.0947 | -145.0916 | -174.2579 | -196.7368 | -215.5284 | -81.8926 | -87.6611 | -93.42 | -99.1905 | -105.6558 | -158.7453 | -166.9063 | -172.1474 | -217.5337 | -250.1126 | -274.3368 | -295.1663 | -77.3189 | -83.0853 | -88.8442 | -94.6147 | -101.1421 | -154.2095 | -162.4421 | -167.7716 | -213.1737 | -246.4758 | -271.4053 | -292.5032
|  | ALTON BSP | HE |  |  |  |  | 13.2968 | -39.4116 | -42.6663 | -45.9442 | -49.8116 | -92.2389 | -111.1526 | -142.2674 | -145.3558 | -160.7537 | -175.6158 | -186.7232 | -36.0084 | -97.7968 | -101.3684 | -104.9453 | -109.1074 | -158.6653 | -180.5653 | -216.8379 | -220.1589 | -236.9758 | -254.7526 | -267.1358 | -31.3958 | -93.2474 | -96.8179 | -100.3895 | -104.6021 | -154.1189 | -176.0347 | -212.2979 | -215.6726 | -232.84 | -251.1211 | -263.7442
|  | ALTON BSP | CF |  |  |  |  | 17.0032 | 15.5105 | -19.9789 | -21.7432 | -23.8368 | -26.1989 | -28.5432 | -30.6053 | -32.5895 | -42.6684 | -50.9558 | -58.1042 | -31.6579 | -33.3579 | -75.1337 | -77.0779 | -79.3611 | -81.9589 | -84.5379 | -86.7905 | -88.9589 | -100.0095 | -109.2 | -117.1611 | -26.9895 | -28.7063 | -70.6263 | -72.5663 | -74.8726 | -77.4926 | -80.0947 | -82.3695 | -84.5526 | -95.7147 | -105.0463 | -113.1716
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | AMESBURY BSP | MINIMUM HEADROOM | SU 15842 42724 | NO | YES | 0.22737 | 43.0653 | 41.9821 | 40.84 | 0.61579 | -1.2526 | -3.2579 | -5.4347 | -6.3505 | -7.3084 | -13.84 | -21.3116 | -26.4516 | 15.9937 | 14.8337 | 13.6095 | -33.7147 | -35.7621 | -37.9663 | -40.3821 | -41.3221 | -42.3147 | -49.3558 | -57.5589 | -63.2716 | 19.1958 | 18.0358 | 16.8095 | -30.5337 | -32.5968 | -34.8211 | -37.2621 | -38.2232 | -39.2421 | -46.4558 | -54.8632 | -60.6526
|  | AMESBURY BSP | EE |  |  |  |  | 74.62 | 42.8863 | 41.9716 | 41.0526 | 40.0442 | 39.0337 | 38.0095 | 37.0568 | 36.2147 | 30.5747 | 23.8737 | 18.6632 | 53.1537 | 15.8137 | 14.8389 | 13.8642 | 12.8116 | 11.7663 | 10.7042 | 9.7274 | 8.8811 | 2.9232 | -4.3263 | -10.1811 | 56.3674 | 19.0158 | 18.0358 | 17.0589 | 15.9916 | 14.9168 | 13.8242 | 12.8179 | 11.9337 | 5.7337 | -1.7916 | -7.7368
|  | AMESBURY BSP | HT |  |  |  |  | 43.0653 | 41.9821 | 40.84 | 0.61579 | -1.2526 | -3.2579 | -5.4347 | -6.3505 | -7.3084 | -13.84 | -21.3116 | -26.4516 | 15.9937 | 14.8337 | 13.6095 | -33.7147 | -35.7621 | -37.9663 | -40.3821 | -41.3221 | -42.3147 | -49.3558 | -57.5589 | -63.2716 | 19.1958 | 18.0358 | 16.8095 | -30.5337 | -32.5968 | -34.8211 | -37.2621 | -38.2232 | -39.2421 | -46.4558 | -54.8632 | -60.6526
|  | AMESBURY BSP | HE |  |  |  |  | 75.5326 | 44.0905 | 43.4505 | 42.8011 | 42.0516 | 41.3179 | 40.5758 | 39.94 | 39.4074 | 35.9442 | 31.3589 | 27.38 | 54.14 | 17.1116 | 16.4305 | 15.7411 | 14.9653 | 14.2042 | 13.4253 | 12.7705 | 12.2263 | 8.5074 | 3.3442 | -1.1632 | 57.3547 | 20.3147 | 19.6337 | 18.9432 | 18.1526 | 17.3789 | 16.5842 | 15.9158 | 15.3558 | 11.5379 | 6.2947 | 1.7147
|  | AMESBURY BSP | CF |  |  |  |  | 77.0895 | 75.7621 | 75.4442 | 75.1211 | 74.7232 | 74.3084 | 73.9221 | 73.5274 | 73.1389 | 40.2116 | 37.6926 | 35.0137 | 55.9116 | 54.3811 | 54.0411 | 53.6958 | 53.2747 | 52.8358 | 52.4284 | 52.0126 | 51.5968 | 12.9747 | 10.1558 | 7.1179 | 59.1274 | 57.5958 | 57.2558 | 56.9105 | 56.4853 | 56.0368 | 55.6221 | 55.2 | 54.7779 | 16.1105 | 13.2484 | 10.1621
MELKSHAM GSP | ANDOVER BSP | ANDOVER BSP | MINIMUM HEADROOM | SU 35334 46598 | NO | YES | 43.0747 | 62.0916 | 5.5158 | -28.8611 | 57.4484 | 56.2453 | 45.4611 | 42.9463 | 38.5063 | 26.8621 | -3.2347 | -15.0895 | -24.4032 | 40.4821 | -25.6032 | -65.7421 | 20.1579 | 19.1705 | 5.8758 | 3.0811 | -0.93895 | -14.4084 | -48.8095 | -61.9611 | -72.3863 | 43.12 | -22.9863 | -63.1389 | 22.7621 | 21.3926 | 8.4558 | 5.6505 | 1.2305 | -12.2568 | -46.7811 | -60.0726 | -70.5537
|  | ANDOVER BSP | EE |  |  |  |  | 62.0916 | 60.0674 | 19.9495 | 60.1253 | 57.1547 | 54.2653 | 51.3537 | 48.1232 | 44.8326 | 30.5516 | 11.1758 | 2.7411 | 40.4821 | 38.2853 | -7.9 | 23.7979 | 20.5326 | 17.3674 | 14.1621 | 10.5811 | 6.9158 | -8.82 | -30.86 | -40.3863 | 43.12 | 40.9189 | -5.7095 | 25.9695 | 22.6905 | 19.5053 | 16.2789 | 12.6779 | 8.9853 | -7.2758 | -29.5105 | -39.0979
|  | ANDOVER BSP | HT |  |  |  |  | 64.6232 | 5.5158 | -28.8611 | 57.4484 | 56.2453 | 51.8737 | 47.5768 | 38.5063 | 26.8621 | -3.2347 | -15.0895 | -24.4032 | 45.4453 | -25.6032 | -65.7421 | 20.1579 | 19.1705 | 14.3 | 9.4905 | -0.93895 | -14.4084 | -48.8095 | -61.9611 | -72.3863 | 48.0863 | -22.9863 | -63.1389 | 22.7621 | 21.3926 | 16.5032 | 11.68 | 1.2305 | -12.2568 | -46.7811 | -60.0726 | -70.5537
|  | ANDOVER BSP | HE |  |  |  |  | 66.4695 | 65.6758 | 50.3126 | 124.1253 | 88.4968 | 45.4611 | 42.9463 | 40.2105 | 37.4863 | 25.7053 | 9.2263 | 2.8421 | 48.8263 | 47.4832 | 26.7526 | 97.8926 | 56.2379 | 5.8758 | 3.0811 | 0.017895 | -3.0484 | -16.2326 | -35.2674 | -42.5432 | 51.7558 | 50.1916 | 29.3832 | 100.5211 | 58.8411 | 8.4558 | 5.6505 | 2.5768 | -0.5 | -14.1379 | -33.2337 | -40.56
|  | ANDOVER BSP | CF |  |  |  |  | 67.1379 | 66.7516 | 37.3189 | 93.2474 | 92.2358 | 91.2705 | 90.3632 | 89.4463 | 88.3989 | 78.9811 | 77.3158 | 73.0337 | 49.8537 | 49.1589 | 11.2589 | 61.3263 | 60.22 | 59.1716 | 58.1821 | 57.1842 | 56.0358 | 45.3358 | 43.76 | 38.8758 | 52.6516 | 52.1032 | 13.8863 | 63.9411 | 62.8295 | 61.7747 | 60.7832 | 59.7811 | 58.6274 | 47.9063 | 45.9274 | 41.0084
MANNINGTON GSP | ARNEWOOD BSP | ARNEWOOD BSP | MINIMUM HEADROOM | SZ 26094 97294 | NO | YES | 13 | 62.1368 | 60.5589 | 51.0863 | 92.7589 | 90.1221 | 87.2842 | 84.8295 | 82.3905 | 80.2537 | 72.8337 | 65.24 | 58.5663 | 45.3105 | 42.6084 | 31.4011 | 69.9926 | 67.1158 | 64.0074 | 61.3463 | 58.6926 | 56.3811 | 48.5084 | 40.2674 | 32.7926 | 47.6074 | 44.9916 | 33.4611 | 72.0432 | 69.1568 | 66.0284 | 63.3442 | 60.6684 | 58.3295 | 50.2958 | 41.8653 | 34.3295
|  | ARNEWOOD BSP | EE |  |  |  |  | 62.9305 | 61.8726 | 51.0863 | 92.7589 | 90.1221 | 87.2842 | 84.8295 | 82.3905 | 80.2537 | 72.8337 | 65.24 | 58.5663 | 47.0063 | 44.8747 | 31.4011 | 69.9926 | 67.1158 | 64.0074 | 61.3463 | 58.6926 | 56.3811 | 48.5084 | 40.2674 | 32.7926 | 49.1116 | 47.2053 | 33.4611 | 72.0432 | 69.1568 | 66.0284 | 63.3442 | 60.6684 | 58.3295 | 50.2958 | 41.8653 | 34.3295
|  | ARNEWOOD BSP | HT |  |  |  |  | 62.1368 | 60.5589 | 57.8768 | 115.0116 | 112.0474 | 108.7737 | 106.0368 | 102.7421 | 100.9347 | 91.0684 | 82.32 | 73.5947 | 45.3105 | 42.6084 | 39.6358 | 96.4453 | 93.1632 | 89.6305 | 86.7032 | 83.1042 | 81.1926 | 70.5253 | 61.0042 | 51.2558 | 47.6074 | 44.9916 | 41.9674 | 98.7232 | 95.3726 | 91.7653 | 88.7747 | 85.1063 | 83.1779 | 72.3916 | 62.7337 | 52.9284
|  | ARNEWOOD BSP | HE |  |  |  |  | 63.9379 | 63.1968 | 54.3432 | 96.5916 | 94.4926 | 92.2074 | 90.2884 | 88.4179 | 86.8726 | 82.2326 | 77.3874 | 72.8358 | 49.1853 | 47.7274 | 34.92 | 74.1642 | 71.8758 | 69.3547 | 67.2568 | 65.2095 | 63.5242 | 58.5737 | 53.1853 | 48.0411 | 51.0421 | 49.7358 | 37.0116 | 76.2211 | 73.92 | 71.3895 | 69.2842 | 67.2242 | 65.5305 | 60.5126 | 55.0684 | 49.8737
|  | ARNEWOOD BSP | CF |  |  |  |  | 64.6305 | 64.2453 | 63.8432 | 123.4274 | 122.9811 | 122.5242 | 122.0768 | 121.3463 | 120.2884 | 116.3179 | 113.2695 | 110.1863 | 50.4179 | 49.6211 | 48.7379 | 107.7842 | 106.7484 | 105.6411 | 104.5705 | 103.4084 | 102.2116 | 97.8158 | 94.3579 | 90.9505 | 52.1705 | 51.4495 | 50.6684 | 109.8284 | 108.9147 | 107.94 | 106.9484 | 105.7768 | 104.5537 | 100.0632 | 96.5053 | 92.9821
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | BASINGSTOKE (T1A & T2A) BSP | MINIMUM HEADROOM | SU 65132 52710 | YES | YES | 29.4737 | 75.4958 | 75.02 | 74.4811 | 73.6979 | 72.8853 | 71.4432 | 70.0684 | 68.7337 | 67.4484 | 54.5989 | 53.9053 | 53.3768 | 63.9705 | 63.0968 | 62.2074 | 61.3179 | 60.4116 | 58.6284 | 56.9179 | 55.2484 | 53.6389 | 42.8853 | 38.0505 | 34.4484 | 67.1432 | 66.2747 | 65.3768 | 64.4821 | 63.5611 | 61.7484 | 60.0042 | 58.3053 | 56.6621 | 40.6484 | 39.7947 | 37.1947
|  | BASINGSTOKE (T1A & T2A) BSP | EE |  |  |  |  | 75.7558 | 75.3579 | 74.9368 | 74.4968 | 73.9158 | 73.2495 | 72.1779 | 70.9011 | 69.6337 | 65.8442 | 63.7642 | 61.4642 | 64.5358 | 63.8326 | 63.1084 | 62.3811 | 61.6263 | 60.8937 | 59.5926 | 58 | 56.4063 | 51.8895 | 49.6916 | 46.8358 | 67.6674 | 67.0063 | 66.2884 | 65.5526 | 64.7863 | 64.0368 | 62.7074 | 61.0811 | 59.4505 | 54.7863 | 52.5074 | 49.6221
|  | BASINGSTOKE (T1A & T2A) BSP | HT |  |  |  |  | 75.4958 | 75.02 | 74.4811 | 73.6979 | 72.8853 | 71.4432 | 70.0684 | 68.7337 | 67.4484 | 64.1653 | 56.5989 | 53.6547 | 63.9705 | 63.0968 | 62.2074 | 61.3179 | 60.4116 | 58.6284 | 56.9179 | 55.2484 | 53.6389 | 49.9337 | 38.0505 | 34.4484 | 67.1432 | 66.2747 | 65.3768 | 64.4821 | 63.5611 | 61.7484 | 60.0042 | 58.3053 | 56.6621 | 52.8947 | 40.8716 | 37.1947
|  | BASINGSTOKE (T1A & T2A) BSP | HE |  |  |  |  | 76.12 | 75.8411 | 75.5358 | 75.2074 | 74.84 | 74.4905 | 74.0432 | 73.0526 | 72.1063 | 54.5989 | 53.9053 | 53.3768 | 64.9042 | 64.6253 | 64.3211 | 63.8642 | 63.3232 | 62.8116 | 61.7589 | 60.5063 | 59.3011 | 42.8853 | 41.6811 | 40.1705 | 68.0789 | 67.8 | 67.4916 | 67.0126 | 66.4905 | 65.9821 | 64.9105 | 63.6347 | 62.4042 | 40.6484 | 39.7947 | 38.9716
|  | BASINGSTOKE (T1A & T2A) BSP | CF |  |  |  |  | 76.32 | 76.1463 | 75.9663 | 75.7821 | 75.5832 | 75.3811 | 75.1821 | 74.9863 | 74.7895 | 72.0842 | 71.0558 | 70.1821 | 65.1042 | 64.9305 | 64.7505 | 64.5663 | 64.3705 | 64.0884 | 63.7558 | 63.3642 | 62.9389 | 59.1368 | 57.9432 | 56.9116 | 68.2789 | 68.1053 | 67.9253 | 67.7411 | 67.5432 | 67.2263 | 66.9095 | 66.5368 | 66.1042 | 62.2368 | 61.0137 | 59.9516
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BASINGSTOKE (T1B & T2B) BSP | MINIMUM HEADROOM | SU 65132 52711 | NO | YES | 0.94737 | 82.6832 | 80.1537 | 77.3916 | 74.1011 | 70.4842 | 63.2042 | 56.3768 | 50.4589 | 45.4421 | 27.9021 | 17.4758 | 10.7832 | 65.9516 | 63.1137 | 60.0095 | 56.2726 | 52.1568 | 43.6274 | 35.6179 | 28.6832 | 22.8253 | 2.4579 | -9.5 | -17.0158 | 68.8158 | 65.9779 | 62.8726 | 59.1337 | 55.0126 | 46.4768 | 38.46 | 31.5221 | 25.6547 | 5.2474 | -6.7537 | -14.2853
|  | BASINGSTOKE (T1B & T2B) BSP | EE |  |  |  |  | 98.2316 | 81.6968 | 79.2947 | 76.3368 | 73.0621 | 70.2232 | 65.3905 | 59.5263 | 54.0537 | 35.9484 | 25.8716 | 20.1011 | 84.5253 | 64.8158 | 62.1053 | 58.7358 | 54.9937 | 51.7716 | 46.1411 | 39.2621 | 32.8358 | 11.6716 | 0.012632 | -6.6305 | 88.1032 | 67.68 | 64.9674 | 61.5947 | 57.8484 | 54.6232 | 48.9842 | 42.0968 | 35.6611 | 14.4432 | 2.7263 | -3.9358
|  | BASINGSTOKE (T1B & T2B) BSP | HT |  |  |  |  | 82.6832 | 80.1537 | 77.3916 | 74.1011 | 70.4842 | 63.2042 | 56.3768 | 50.4589 | 45.4421 | 27.9021 | 17.4758 | 10.7832 | 65.9516 | 63.1137 | 60.0095 | 56.2726 | 52.1568 | 43.6274 | 35.6179 | 28.6832 | 22.8253 | 2.4579 | -9.5 | -17.0158 | 68.8158 | 65.9779 | 62.8726 | 59.1337 | 55.0126 | 46.4768 | 38.46 | 31.5221 | 25.6547 | 5.2474 | -6.7537 | -14.2853
|  | BASINGSTOKE (T1B & T2B) BSP | HE |  |  |  |  | 99.0242 | 98.4253 | 81.8505 | 79.3442 | 76.4884 | 74.0663 | 70.2537 | 65.9389 | 62.2105 | 48.1853 | 37.3011 | 32.1042 | 86.0421 | 84.4653 | 64.9242 | 62.0474 | 58.7684 | 56.0042 | 51.5547 | 46.4905 | 42.1189 | 25.6326 | 12.7674 | 6.6684 | 89.7926 | 87.98 | 67.7874 | 64.9116 | 61.6263 | 58.8611 | 54.4063 | 49.3389 | 44.9611 | 28.4516 | 15.5674 | 9.4516
|  | BASINGSTOKE (T1B & T2B) BSP | CF |  |  |  |  | 99.5674 | 99.2474 | 85.5326 | 84.5621 | 83.0779 | 80.9432 | 79.3684 | 78.0389 | 76.8053 | 68.0589 | 58.6305 | 53.1705 | 87.4789 | 86.8158 | 69.1263 | 68.0263 | 66.3116 | 63.8158 | 61.9947 | 60.4653 | 59.0537 | 48.8474 | 37.6611 | 31.1884 | 91.0116 | 90.6653 | 71.9916 | 70.8895 | 69.1747 | 66.6758 | 64.8526 | 63.3232 | 61.9105 | 51.6937 | 40.4968 | 34.0105
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | BASINGSTOKE (T3 & T4) BSP | MINIMUM HEADROOM | SU 65132 52712 | NO | YES | 73.3811 | 29.2442 | 28.7621 | -3.8779 | -5.8916 | -8.2074 | -10.4684 | -13.2053 | -16.1863 | -19.1895 | -28.5168 | -31.3495 | -35.2168 | 19.1958 | 17.8411 | -25.5305 | -27.8179 | -30.4442 | -33.0021 | -36.1242 | -39.5326 | -42.9695 | -53.4937 | -56.4379 | -60.6126 | 21.1916 | 20.6316 | -22.1411 | -24.4253 | -27.0568 | -29.6253 | -32.7558 | -36.1726 | -39.6211 | -50.24 | -53.3126 | -57.4347
|  | BASINGSTOKE (T3 & T4) BSP | EE |  |  |  |  | 29.5137 | 29.1095 | -3.8779 | -5.8916 | -8.2074 | -10.4684 | -13.2053 | -16.1863 | -19.1895 | -28.5168 | -31.3495 | -34.5526 | 19.5158 | 18.6274 | -25.5305 | -27.8179 | -30.4442 | -33.0021 | -36.1242 | -39.5326 | -42.9695 | -53.4937 | -56.4379 | -60.0084 | 21.4811 | 21.0042 | -22.1411 | -24.4253 | -27.0568 | -29.6253 | -32.7558 | -36.1726 | -39.6211 | -50.24 | -53.3126 | -56.9221
|  | BASINGSTOKE (T3 & T4) BSP | HT |  |  |  |  | 29.2442 | 28.7621 | -1.3421 | -3.5158 | -5.9811 | -9.1316 | -12.2095 | -15.2211 | -17.6221 | -27.3095 | -31.12 | -35.2168 | 19.1958 | 17.8411 | -22.4726 | -24.9337 | -27.7221 | -31.3168 | -34.8316 | -38.2768 | -41.0095 | -51.9495 | -56.0442 | -60.6126 | 21.1916 | 20.6316 | -19.0863 | -21.5453 | -24.34 | -27.9358 | -31.4579 | -34.9074 | -37.6484 | -48.6495 | -52.8337 | -57.4347
|  | BASINGSTOKE (T3 & T4) BSP | HE |  |  |  |  | 29.8463 | 29.5432 | 11.2432 | -4.5253 | -6.6442 | -8.6937 | -11.0547 | -13.5253 | -15.9389 | -24.8326 | -26.1695 | -27.9989 | 19.9095 | 19.4053 | -7.8337 | -26.3242 | -28.7389 | -31.0726 | -33.7789 | -36.6179 | -39.3958 | -49.6305 | -51.0411 | -53.0768 | 21.84 | 21.4737 | -4.4737 | -22.9305 | -25.3463 | -27.6853 | -30.3916 | -33.2337 | -36.0137 | -46.2832 | -47.7305 | -49.7947
|  | BASINGSTOKE (T3 & T4) BSP | CF |  |  |  |  | 30.0853 | 29.9116 | 29.7305 | 29.5432 | 29.3389 | 29.1305 | 28.9263 | 28.7221 | 28.5242 | 21.0011 | 19.8316 | 18.7958 | 20.2011 | 19.9958 | 19.7684 | 19.5189 | 19.0737 | 17.8211 | 16.36 | 14.8032 | 13.1326 | 3.9632 | 2.6979 | 1.5568 | 22.1021 | 21.9147 | 21.7126 | 21.4979 | 21.2474 | 20.9789 | 19.7621 | 18.1758 | 16.48 | 7.2653 | 5.9811 | 4.82
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH BSP | MINIMUM HEADROOM | SP5972023735 | NO | YES | 62.4832 | 40.3526 | 39.6526 | 50.5874 | 48.14 | 34.1316 | 31.1074 | 28.0726 | 25.2768 | 22.5474 | 11.1168 | 35.7495 | 29.1063 | 32.3053 | 30.4611 | 31.7242 | 28.9568 | 12.5737 | 9.1558 | 5.7211 | 2.5663 | -0.51684 | -13.3642 | 10.2168 | 2.6526 | 31.7432 | 31.0432 | 33.54 | 30.7695 | 14.3653 | 10.9253 | 7.4663 | 4.2895 | 1.1789 | -11.8558 | 11.5147 | 3.8853
|  | BICESTER NORTH BSP | EE |  |  |  |  | 40.7432 | 40.1611 | 50.5874 | 48.14 | 34.1316 | 31.1074 | 28.0726 | 25.2768 | 22.5474 | 11.1168 | 35.7495 | 29.1063 | 33.0347 | 31.4105 | 31.7242 | 28.9568 | 12.5737 | 9.1558 | 5.7211 | 2.5663 | -0.51684 | -13.3642 | 10.2168 | 2.6526 | 32.1337 | 31.5526 | 33.54 | 30.7695 | 14.3653 | 10.9253 | 7.4663 | 4.2895 | 1.1789 | -11.8558 | 11.5147 | 3.8853
|  | BICESTER NORTH BSP | HT |  |  |  |  | 40.3526 | 39.6526 | 68.9147 | 68.1495 | 66.3747 | 62.7526 | 59.1147 | 54.2537 | 51.4411 | 40.1179 | 63.8379 | 56.3337 | 32.3053 | 30.4611 | 57.8842 | 54.7189 | 50.9568 | 46.7832 | 42.5737 | 36.9295 | 33.7463 | 21.02 | 43.5137 | 35.0084 | 31.7432 | 31.0432 | 59.7084 | 56.5421 | 52.7632 | 48.5726 | 44.3442 | 38.6832 | 35.4789 | 22.6221 | 44.9621 | 36.3937
|  | BICESTER NORTH BSP | HE |  |  |  |  | 41.2811 | 40.8695 | 70.4168 | 69.9242 | 69.3632 | 67.7421 | 65.0758 | 62.6958 | 60.3842 | 51.16 | 77.9389 | 72.5684 | 34.02 | 32.7116 | 60.6484 | 58.1579 | 55.4295 | 52.2979 | 49.2042 | 46.4484 | 43.7621 | 33.1874 | 58.9547 | 52.7884 | 32.6716 | 32.26 | 61.8074 | 59.9821 | 57.2421 | 54.1 | 50.9937 | 48.2253 | 45.5284 | 34.8758 | 60.5821 | 54.36
|  | BICESTER NORTH BSP | CF |  |  |  |  | 41.6516 | 41.4316 | 71.2032 | 70.9663 | 70.7021 | 70.4326 | 70.1684 | 69.9063 | 69.6495 | 63.5158 | 58.8916 | 55.5042 | 34.9463 | 34.4958 | 63.9295 | 63.2126 | 62.2295 | 60.7221 | 58.7821 | 56.7958 | 54.8516 | 47.3105 | 41.9095 | 38.0242 | 33.0421 | 32.8221 | 62.5937 | 62.3568 | 62.0937 | 61.8253 | 60.5884 | 58.5989 | 56.6505 | 49.0821 | 43.6505 | 39.7274
BOTLEY WOOD GSP | BOTLEY WOOD BSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU 54073 09759 | NO | YES | 82.0937 | 18.2358 | 18.0895 | 17.9368 | 17.7768 | 25.1884 | 23.7137 | 22.5295 | 21.4737 | 20.4968 | 16.1968 | 12.2653 | 8.68 | 9.3284 | 7.1442 | 6.8905 | 6.6411 | 16.14 | 14.5347 | 13.2568 | 12.1179 | 11.0632 | 6.3158 | 1.9253 | -2.1116 | 11.3253 | 8.9937 | 8.7389 | 8.4874 | 16.1821 | 14.5463 | 13.2411 | 12.08 | 11.0032 | 6.2421 | 1.8411 | -2.1989
|  | BOTLEY WOOD BSP | EE |  |  |  |  | 28.9 | 28.4989 | 28.0747 | 27.6305 | 26.4421 | 25.1358 | 24.0968 | 23.1411 | 22.2758 | 18.8684 | 15.7958 | 13.0389 | 23.3537 | 22.5084 | 21.0968 | 19.2326 | 17.4737 | 16.0484 | 14.9253 | 13.8937 | 12.96 | 9.2358 | 5.7947 | 2.6758 | 23.5505 | 22.6916 | 21.2484 | 19.3389 | 17.5368 | 16.08 | 14.9337 | 13.8811 | 12.9295 | 9.1579 | 5.7063 | 2.5821
|  | BOTLEY WOOD BSP | HT |  |  |  |  | 28.6021 | 28.1105 | 27.5905 | 26.9495 | 25.1884 | 23.7137 | 22.5295 | 21.4737 | 20.4968 | 16.1968 | 12.2653 | 8.68 | 22.7411 | 21.8063 | 20.0916 | 18.0642 | 16.14 | 14.5347 | 13.2568 | 12.1179 | 11.0632 | 6.3158 | 1.9253 | -2.1116 | 22.9274 | 21.9789 | 20.2274 | 18.1516 | 16.1821 | 14.5463 | 13.2411 | 12.08 | 11.0032 | 6.2421 | 1.8411 | -2.1989
|  | BOTLEY WOOD BSP | HE |  |  |  |  | 29.2874 | 29.0074 | 28.6979 | 28.3642 | 28.0063 | 27.0137 | 26.1705 | 25.4116 | 24.7411 | 22.2358 | 20.0253 | 18.0568 | 24.0337 | 23.3958 | 22.4295 | 20.8011 | 19.2642 | 18.0547 | 17.1379 | 16.3179 | 15.5905 | 12.8632 | 10.3842 | 8.1295 | 24.2389 | 23.5905 | 22.6032 | 20.9347 | 19.3589 | 18.1211 | 17.1874 | 16.3484 | 15.6063 | 12.8168 | 10.3116 | 8.0537
|  | BOTLEY WOOD BSP | CF |  |  |  |  | 18.2358 | 18.0895 | 17.9368 | 17.7768 | 28.9232 | 28.7558 | 28.5905 | 28.4274 | 28.2653 | 27.5347 | 26.8074 | 25.4958 | 9.3284 | 7.1442 | 6.8905 | 6.6411 | 23.6053 | 23.1958 | 22.6684 | 22.1221 | 21.5716 | 19.5274 | 17.8916 | 16.4284 | 11.3253 | 8.9937 | 8.7389 | 8.4874 | 23.8084 | 23.3916 | 22.8505 | 22.2926 | 21.7295 | 19.6442 | 17.9674 | 16.4611
MANNINGTON GSP | BOURNEMOUTH BSP | BOURNEMOUTH BSP | MINIMUM HEADROOM | SZ 06265 92437 | NO | YES | 0.078947 | 128.8158 | 126.5568 | 101.3821 | 97.8474 | 92.1274 | 86.7316 | 81.9158 | 77.2147 | 72.6884 | 52.1579 | 33.0958 | 15.2989 | 98.7684 | 93.8874 | 64.9074 | 59.1147 | 52.8463 | 46.9589 | 41.7063 | 36.5547 | 31.5726 | 8.8716 | -12.44 | -32.4821 | 104.4105 | 100.5916 | 71.5463 | 65.72 | 59.4579 | 53.5768 | 48.3263 | 43.18 | 38.2063 | 15.5242 | -5.7684 | -25.7863
|  | BOURNEMOUTH BSP | EE |  |  |  |  | 130.2305 | 128.4053 | 103.6863 | 101.6337 | 98.1274 | 93.6853 | 89.8526 | 86.3516 | 82.6432 | 66.6474 | 51.8632 | 38.2916 | 100.26 | 98.1 | 70.2547 | 64.8758 | 59.3358 | 54.4758 | 50.3211 | 46.5463 | 42.4874 | 24.8211 | 8.2411 | -7.1263 | 105.8695 | 103.9442 | 76.9474 | 71.5084 | 65.9421 | 61.0863 | 56.9337 | 53.1621 | 49.1053 | 31.4495 | 14.8832 | -0.46737
|  | BOURNEMOUTH BSP | HT |  |  |  |  | 128.8158 | 126.5568 | 101.3821 | 97.8474 | 92.1274 | 86.7316 | 81.9158 | 77.2147 | 72.6884 | 52.1579 | 33.0958 | 15.2989 | 98.7684 | 93.8874 | 64.9074 | 59.1147 | 52.8463 | 46.9589 | 41.7063 | 36.5547 | 31.5726 | 8.8716 | -12.44 | -32.4821 | 104.4105 | 100.5916 | 71.5463 | 65.72 | 59.4579 | 53.5768 | 48.3263 | 43.18 | 38.2063 | 15.5242 | -5.7684 | -25.7863
|  | BOURNEMOUTH BSP | HE |  |  |  |  | 131.7 | 130.3011 | 105.9779 | 104.3137 | 102.5368 | 100.8379 | 98.5579 | 95.8937 | 93.0537 | 81.5379 | 71.1389 | 61.84 | 101.8242 | 100.3368 | 75.8221 | 71.4432 | 66.8853 | 63.0063 | 59.8874 | 57.0189 | 53.9063 | 41.1432 | 29.3874 | 18.7526 | 107.3389 | 105.94 | 81.5242 | 78.1463 | 73.5389 | 69.6189 | 66.4916 | 63.6232 | 60.5137 | 47.7632 | 36.0211 | 25.3979
|  | BOURNEMOUTH BSP | CF |  |  |  |  | 132.7716 | 131.9589 | 108.3358 | 107.4632 | 106.5579 | 105.6326 | 104.7253 | 103.8263 | 102.9295 | 98.26 | 90.9705 | 84.6684 | 102.9379 | 102.08 | 78.4095 | 77.48 | 76.5074 | 74.7484 | 72.4684 | 70.3516 | 68.3189 | 59.5947 | 51.3758 | 44.1621 | 108.4105 | 107.5979 | 83.9747 | 83.1021 | 82.1474 | 81.1368 | 79.1821 | 77.0421 | 74.9895 | 66.1979 | 57.9884 | 50.7842
FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL BSP | MINIMUM HEADROOM | SU 86026 69422 | NO | YES | 1.2179 | 223.0389 | 222.3547 | 221.6389 | 220.9032 | 220.1305 | 219.0232 | 212.7684 | 206.4632 | 201.2421 | 179.9453 | 156.2674 | 140.7516 | 189.6579 | 188.7758 | 183.5242 | 177.7379 | 170.7568 | 164.8832 | 157.8495 | 150.7558 | 145.14 | 121.9211 | 92.9347 | 75.4474 | 194.9979 | 194.2516 | 190.4495 | 184.6653 | 177.6726 | 171.7895 | 164.7484 | 157.6411 | 152.0116 | 128.6516 | 98.3821 | 80.8632
|  | BRACKNELL BSP | EE |  |  |  |  | 232.0874 | 230.3242 | 228.4505 | 226.4905 | 224.3105 | 219.0232 | 212.7684 | 206.4632 | 201.4495 | 190.2979 | 176.3684 | 164.2495 | 201.8179 | 197.3747 | 183.5242 | 177.7379 | 170.7568 | 164.8832 | 157.8495 | 150.7558 | 145.14 | 135.5105 | 119.9884 | 106.3105 | 206.5263 | 204.3042 | 190.4495 | 184.6653 | 177.6726 | 171.7895 | 164.7484 | 157.6411 | 152.0116 | 143.4211 | 127.8063 | 114.1
|  | BRACKNELL BSP | HT |  |  |  |  | 230.8316 | 228.6958 | 226.4263 | 224.0779 | 222.3126 | 219.8579 | 214.3011 | 207.6895 | 201.2421 | 179.9453 | 156.2674 | 140.7516 | 199.2242 | 193.7947 | 187.5368 | 180.9179 | 174.4063 | 167.9516 | 160.3432 | 152.9032 | 145.6326 | 121.9211 | 92.9347 | 75.4474 | 205.2705 | 200.7253 | 194.4653 | 187.8442 | 181.2295 | 174.7684 | 167.1516 | 159.7011 | 152.4211 | 128.6516 | 98.3821 | 80.8632
|  | BRACKNELL BSP | HE |  |  |  |  | 233.7095 | 232.4474 | 231.0495 | 229.5495 | 227.9316 | 226.3842 | 224.9253 | 223.0474 | 218.9526 | 196.7737 | 186.9516 | 178.5032 | 204.4126 | 202.2253 | 197.8979 | 192.8305 | 186.7979 | 181.8905 | 175.5221 | 169.4337 | 164.8211 | 136.2789 | 125.1421 | 115.4663 | 208.1484 | 206.8863 | 204.8295 | 199.7621 | 193.7211 | 188.8074 | 182.4347 | 176.3411 | 171.7221 | 141.2263 | 130.0621 | 120.3579
|  | BRACKNELL BSP | CF |  |  |  |  | 223.0389 | 222.3547 | 221.6389 | 220.9032 | 220.1305 | 231.12 | 230.3463 | 229.5821 | 228.8179 | 225.4 | 222.9305 | 217.3579 | 189.6579 | 188.7758 | 187.0253 | 184.8926 | 182.1884 | 196.9474 | 193.6832 | 190.2084 | 187.1453 | 175.9116 | 169.3421 | 162.9537 | 194.9979 | 194.2516 | 193.4747 | 192.6568 | 190.7779 | 203.8726 | 200.6084 | 197.1326 | 194.06 | 182.8221 | 176.1358 | 169.7295
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | BURGHFIELD (MAIN) BSP | MINIMUM HEADROOM | SU 69442 70509 | NO | YES | 3.1579 | 109.9621 | 108.6968 | 71.2705 | 67.8221 | 22.5916 | 18.5242 | 15.5537 | 12.9274 | 10.8347 | 2.1074 | -6.8589 | -15.3747 | 89.0726 | 86.5253 | 36.5695 | 32.7568 | -19.4305 | -23.96 | -27.2316 | -30.1168 | -32.3916 | -41.8937 | -51.8684 | -61.4337 | 93.8895 | 91.7842 | 42.1684 | 38.3611 | -14.2053 | -18.7305 | -21.9989 | -24.88 | -27.1537 | -36.6463 | -46.6084 | -56.1611
|  | BURGHFIELD (MAIN) BSP | EE |  |  |  |  | 110.7126 | 109.6758 | 108.5747 | 107.4221 | 104.6674 | 101.1821 | 98.3853 | 95.8905 | 94.1221 | 87.5979 | 80.9274 | 74.6358 | 90.5042 | 88.7516 | 85.9937 | 82.7884 | 77.0158 | 72.8958 | 69.8042 | 67.0589 | 65.1453 | 58.0853 | 50.6621 | 43.5747 | 94.6811 | 93.6011 | 91.26 | 88.1263 | 82.1211 | 78.0011 | 74.9074 | 72.1621 | 70.2474 | 63.1863 | 55.76 | 48.6726
|  | BURGHFIELD (MAIN) BSP | HT |  |  |  |  | 109.9621 | 108.6968 | 71.2705 | 67.8221 | 22.5916 | 18.5242 | 15.5537 | 12.9274 | 10.8347 | 2.1074 | -6.8589 | -15.3747 | 89.0726 | 86.5253 | 36.5695 | 32.7568 | -19.4305 | -23.96 | -27.2316 | -30.1168 | -32.3916 | -41.8937 | -51.8684 | -61.4337 | 93.8895 | 91.7842 | 42.1684 | 38.3611 | -14.2053 | -18.7305 | -21.9989 | -24.88 | -27.1537 | -36.6463 | -46.6084 | -56.1611
|  | BURGHFIELD (MAIN) BSP | HE |  |  |  |  | 111.6558 | 110.9053 | 110.0789 | 109.1842 | 71.2168 | 68.0379 | 65.7937 | 63.7968 | 62.5284 | 58.4021 | 53.9821 | 49.8274 | 92.3421 | 91.22 | 89.3474 | 86.7789 | 36.7432 | 33.1621 | 30.6726 | 28.4642 | 27.0947 | 22.6505 | 17.6947 | 12.9537 | 95.6768 | 94.9053 | 94.0147 | 92.0411 | 42.1053 | 38.5295 | 36.0442 | 33.8368 | 32.4684 | 28.0284 | 23.0779 | 18.3463
|  | BURGHFIELD (MAIN) BSP | CF |  |  |  |  | 112.3116 | 111.9074 | 111.4842 | 111.0463 | 110.5947 | 110.1326 | 109.6779 | 109.2305 | 108.7832 | 106.7821 | 104.6568 | 101.9779 | 93.2695 | 92.8189 | 92.0211 | 91.0232 | 89.68 | 88.1811 | 86.8232 | 85.4453 | 84.2147 | 79.3389 | 76.12 | 73.0716 | 96.3663 | 95.9474 | 95.4968 | 95.0242 | 94.52 | 93.4326 | 92.0979 | 90.7526 | 89.5505 | 84.7789 | 81.6421 | 78.6011
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | BURGHFIELD (RESERVE) BSP | MINIMUM HEADROOM | SU 69442 70509 | NO | YES | 41.8737 | 47.9842 | 46.0811 | 44.1474 | 41.8232 | 39.0042 | 35.7947 | 32.4347 | 31.1568 | 29.3126 | 7.9147 | -4.5084 | -9.6316 | 26.5905 | 24.52 | 22.4284 | 19.8832 | 16.7674 | 13.2021 | 9.4337 | 8.1032 | 6.0947 | -18.3821 | -32.4189 | -38.0558 | 29.8726 | 27.8063 | 25.7126 | 23.1684 | 20.0516 | 16.4789 | 12.7053 | 11.3621 | 9.3442 | -15.1758 | -29.2884 | -34.9579
|  | BURGHFIELD (RESERVE) BSP | EE |  |  |  |  | 49.1337 | 47.58 | 44.4116 | 42.9516 | 41.3937 | 39.8368 | 38.4379 | 37.1305 | 35.9653 | 30.4516 | 15.6947 | 8.3074 | 27.8411 | 26.1516 | 22.5768 | 21.0074 | 19.3516 | 17.6968 | 16.2158 | 14.8432 | 13.6242 | 7.7779 | -9.0632 | -17.4705 | 31.1211 | 29.4347 | 25.86 | 24.2989 | 22.6316 | 20.9621 | 19.4705 | 18.08 | 16.8463 | 10.8874 | -6.0611 | -14.4979
|  | BURGHFIELD (RESERVE) BSP | HT |  |  |  |  | 47.9842 | 46.0811 | 44.1474 | 41.8232 | 39.0042 | 35.7947 | 32.4347 | 31.1568 | 29.3126 | 7.9147 | -4.5084 | -9.6316 | 26.5905 | 24.52 | 22.4284 | 19.8832 | 16.7674 | 13.2021 | 9.4337 | 8.1032 | 6.0947 | -18.3821 | -32.4189 | -38.0558 | 29.8726 | 27.8063 | 25.7126 | 23.1684 | 20.0516 | 16.4789 | 12.7053 | 11.3621 | 9.3442 | -15.1758 | -29.2884 | -34.9579
|  | BURGHFIELD (RESERVE) BSP | HE |  |  |  |  | 66.5642 | 49.5821 | 47.6274 | 46.2926 | 44.9537 | 43.7684 | 42.7411 | 41.8274 | 41.0389 | 37.7411 | 25.4379 | 19.6168 | 51.7495 | 28.3316 | 26.1389 | 24.6832 | 23.2432 | 21.98 | 20.8916 | 19.9284 | 19.1053 | 15.6021 | 1.3632 | -5.3242 | 54.6568 | 31.6105 | 29.4221 | 27.9684 | 26.5232 | 25.2516 | 24.1579 | 23.1905 | 22.3579 | 18.8126 | 4.5611 | -2.1537
|  | BURGHFIELD (RESERVE) BSP | CF |  |  |  |  | 67.08 | 51.1389 | 50.5158 | 49.8674 | 49.24 | 48.6653 | 48.0674 | 47.4453 | 46.8211 | 43.9347 | 41.12 | 37.8705 | 52.6263 | 30.0253 | 29.3442 | 28.6347 | 27.96 | 27.3463 | 26.7042 | 26.0358 | 25.36 | 22.2389 | 19.0821 | 15.3674 | 55.2137 | 33.3053 | 32.6253 | 31.9158 | 31.2379 | 30.6189 | 29.9779 | 29.3063 | 28.6253 | 25.4958 | 22.3211 | 18.5874
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY (MAIN) BSP | MINIMUM HEADROOM | SU 86530 59483 | NO | YES | 0.24211 | 106.6537 | 103.1989 | 99.1568 | 94.8526 | 90.5568 | 86.5968 | 83.0937 | 79.92 | 76.9295 | 63.7632 | 51.9242 | 41.2326 | 70.4558 | 66.6726 | 62.2158 | 57.4611 | 52.7305 | 48.3958 | 44.5568 | 41.0863 | 37.8074 | 23.3168 | 10.1453 | -1.86 | 76.2716 | 72.4926 | 68.0411 | 63.2916 | 58.5621 | 54.2284 | 50.3926 | 46.9189 | 43.6389 | 29.1379 | 15.9463 | 3.9421
|  | CAMBERLEY (MAIN) BSP | EE |  |  |  |  | 108.7011 | 105.7853 | 102.5526 | 98.9937 | 95.3137 | 92.0305 | 88.8411 | 85.7316 | 83.1326 | 72.7032 | 63.6505 | 55.6295 | 72.6905 | 69.4895 | 65.9305 | 61.9979 | 57.9358 | 54.3326 | 50.8242 | 47.4063 | 44.5642 | 33.1032 | 23.0389 | 13.9853 | 78.5042 | 75.3063 | 71.7495 | 67.8221 | 63.7632 | 60.1568 | 56.6495 | 53.2284 | 50.3821 | 38.8895 | 28.7916 | 19.7347
|  | CAMBERLEY (MAIN) BSP | HT |  |  |  |  | 106.6537 | 103.1989 | 99.1568 | 94.8526 | 90.5568 | 86.5968 | 83.0937 | 79.92 | 76.9295 | 63.7632 | 51.9242 | 41.2326 | 70.4558 | 66.6726 | 62.2158 | 57.4611 | 52.7305 | 48.3958 | 44.5568 | 41.0863 | 37.8074 | 23.3168 | 10.1453 | -1.86 | 76.2716 | 72.4926 | 68.0411 | 63.2916 | 58.5621 | 54.2284 | 50.3926 | 46.9189 | 43.6389 | 29.1379 | 15.9463 | 3.9421
|  | CAMBERLEY (MAIN) BSP | HE |  |  |  |  | 117.3421 | 109.0737 | 106.5705 | 103.7063 | 100.6895 | 98.0526 | 95.46 | 93.0137 | 91.0937 | 83.7021 | 77.4495 | 71.9716 | 93.6653 | 73.0695 | 70.3 | 67.1232 | 63.7789 | 60.8789 | 58.0147 | 55.3147 | 53.2053 | 45.0368 | 37.9779 | 31.7295 | 99.2326 | 78.8832 | 76.1179 | 72.9432 | 69.6011 | 66.7011 | 63.8379 | 61.1358 | 59.0295 | 50.8516 | 43.7863 | 37.5358
|  | CAMBERLEY (MAIN) BSP | CF |  |  |  |  | 117.8442 | 117.3653 | 116.8674 | 116.3547 | 115.82 | 115.2716 | 114.7358 | 114.2011 | 113.6684 | 95.7579 | 91.5095 | 88.0053 | 95.7453 | 94.4895 | 93.1863 | 91.7874 | 90.3674 | 88.9758 | 87.6263 | 86.0979 | 84.5232 | 58.26 | 53.4811 | 49.4863 | 99.7484 | 99.2211 | 98.6779 | 97.5537 | 96.1968 | 94.8358 | 93.4853 | 91.9579 | 90.3832 | 64.0811 | 59.3 | 55.3042
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | CAMBERLEY (RESERVE) BSP | MINIMUM HEADROOM | SU 86530 59483 | NO | YES | 0.26421 | 108.2842 | 107.1379 | 105.9211 | 104.6684 | 100.9232 | 97.6589 | 94.7821 | 92.1189 | 89.5653 | 64.8663 | 59.2979 | 52.5168 | 91.0221 | 87.3168 | 83.6305 | 80.08 | 75.6116 | 72.0126 | 68.8411 | 65.8958 | 63.0674 | 38.0905 | 23.5937 | 16.1421 | 95.4305 | 92.1095 | 88.7937 | 85.5874 | 81.3189 | 77.7989 | 74.6958 | 71.8211 | 69.06 | 40.7442 | 28.4032 | 21.0389
|  | CAMBERLEY (RESERVE) BSP | EE |  |  |  |  | 108.9726 | 108.0368 | 107.0358 | 105.9958 | 103.8663 | 101.0179 | 98.8432 | 96.4063 | 94.1095 | 92.7621 | 86.8537 | 81.7937 | 92.5421 | 89.2947 | 86.0232 | 82.8726 | 78.7989 | 75.6421 | 73.4295 | 70.7411 | 68.2021 | 70.9368 | 64.4432 | 58.7926 | 96.8274 | 93.9253 | 90.9937 | 88.1611 | 84.4453 | 81.36 | 79.3358 | 76.7074 | 74.2242 | 78.9284 | 72.38 | 66.7147
|  | CAMBERLEY (RESERVE) BSP | HT |  |  |  |  | 108.2842 | 107.1379 | 105.9211 | 104.6684 | 100.9232 | 97.6589 | 94.7821 | 92.1189 | 89.5653 | 77.0063 | 59.2979 | 52.5168 | 91.0221 | 87.3168 | 83.6305 | 80.08 | 75.6116 | 72.0126 | 68.8411 | 65.8958 | 63.0674 | 49.0316 | 23.5937 | 16.1421 | 95.4305 | 92.1095 | 88.7937 | 85.5874 | 81.3189 | 77.7989 | 74.6958 | 71.8211 | 69.06 | 55.0358 | 28.4032 | 21.0389
|  | CAMBERLEY (RESERVE) BSP | HE |  |  |  |  | 109.8589 | 109.1947 | 108.4632 | 107.6737 | 106.8221 | 105.36 | 103.2347 | 101.2674 | 99.4316 | 64.8663 | 63.3747 | 62.3674 | 94.5032 | 91.8558 | 89.1663 | 86.5716 | 83.0095 | 80.36 | 78.0032 | 75.8211 | 73.7789 | 38.0905 | 33.9495 | 30.4253 | 98.6242 | 96.2758 | 93.8811 | 91.5589 | 88.4 | 85.9884 | 83.6874 | 81.5568 | 79.5642 | 40.7442 | 38.1495 | 34.6663
|  | CAMBERLEY (RESERVE) BSP | CF |  |  |  |  | 110.4621 | 110.1105 | 109.7442 | 109.3653 | 108.9684 | 108.5632 | 108.1653 | 107.7737 | 107.3811 | 103.4716 | 100.7116 | 98.46 | 96.2916 | 94.9916 | 93.6642 | 92.4042 | 90.7747 | 89.3747 | 88.06 | 86.7632 | 85.4189 | 78.22 | 75.1379 | 72.5926 | 100.2863 | 99.0779 | 97.8947 | 96.7663 | 95.3221 | 94.0716 | 92.8926 | 91.7305 | 90.5305 | 83.9074 | 80.9011 | 78.4221
IVER 132KV GSP | CHALVEY BSP | CHALVEY BSP | MINIMUM HEADROOM | SU 96669 79364 | NO | YES | 4.1684 | 104.5947 | 103.5421 | 102.3463 | 98.5516 | 93.9947 | 180.5432 | 178.3947 | 176.3516 | 174.4242 | 165.9253 | 158.5442 | 151.7358 | 84.5874 | 80.2189 | 75.5032 | 70.1611 | 64.9663 | 151.0789 | 148.7053 | 146.4432 | 144.3074 | 134.8495 | 126.58 | 118.9011 | 89.3411 | 84.9105 | 80.1811 | 74.8368 | 69.6411 | 155.7516 | 153.3779 | 151.1158 | 148.98 | 139.52 | 131.2484 | 123.5674
|  | CHALVEY BSP | EE |  |  |  |  | 105.0937 | 104.2474 | 103.2211 | 100.4926 | 96.2158 | 183.0779 | 181.2379 | 179.4526 | 177.8 | 170.9337 | 165.1779 | 159.9705 | 85.7011 | 81.6674 | 77.3032 | 72.2789 | 67.3874 | 153.8347 | 151.8053 | 149.8368 | 148.0095 | 140.3705 | 133.8989 | 127.9968 | 90.4642 | 86.3726 | 81.98 | 76.9558 | 72.0621 | 158.5084 | 156.4789 | 154.5095 | 152.6821 | 145.0421 | 138.5684 | 132.6642
|  | CHALVEY BSP | HT |  |  |  |  | 104.5947 | 103.5421 | 102.3463 | 98.5516 | 93.9947 | 180.5432 | 178.3947 | 176.3516 | 174.4242 | 165.9253 | 158.5442 | 151.7358 | 84.5874 | 80.2189 | 75.5032 | 70.1611 | 64.9663 | 151.0789 | 148.7053 | 146.4432 | 144.3074 | 134.8495 | 126.58 | 118.9011 | 89.3411 | 84.9105 | 80.1811 | 74.8368 | 69.6411 | 155.7516 | 153.3779 | 151.1158 | 148.98 | 139.52 | 131.2484 | 123.5674
|  | CHALVEY BSP | HE |  |  |  |  | 105.6863 | 105.0884 | 104.2379 | 102.9253 | 98.9842 | 186.1832 | 184.6884 | 183.2926 | 182.0253 | 176.9895 | 172.9547 | 169.4358 | 87.1158 | 83.5095 | 79.5716 | 74.9547 | 70.4326 | 157.2495 | 155.5979 | 154.0589 | 152.6558 | 147.0284 | 142.4589 | 138.4274 | 91.8926 | 88.2347 | 84.2505 | 79.6316 | 75.1084 | 161.9242 | 160.2737 | 158.7326 | 157.3305 | 151.7011 | 147.1316 | 143.0979
|  | CHALVEY BSP | CF |  |  |  |  | 106.1232 | 105.8042 | 105.4726 | 105.1295 | 104.7716 | 194.1411 | 193.58 | 193.1663 | 192.2558 | 188.4379 | 185.5916 | 183.1947 | 90.4147 | 89.8505 | 88.7758 | 86.92 | 83.6737 | 169.5116 | 166.2084 | 165.2642 | 164.2537 | 160.0316 | 156.8168 | 154.0684 | 93.0558 | 92.6747 | 92.2716 | 91.6979 | 88.4084 | 174.1895 | 170.8853 | 169.9421 | 168.9316 | 164.7084 | 161.4916 | 158.7411
LOVEDEAN GSP | CHICHESTER BSP | CHICHESTER BSP | MINIMUM HEADROOM | SU 92281 07417 | NO | YES | 81.5337 | 36.2179 | 31.18 | 5.8947 | -0.36421 | -7.9232 | -15.7642 | -23.1 | -29.2621 | -35.0684 | -69.9411 | -91.6105 | -112.6863 | -0.22105 | -5.4695 | -35.3326 | -42.3895 | -50.9653 | -59.8758 | -68.2116 | -75.1726 | -81.7442 | -121.2032 | -145.7968 | -169.8926 | 6.6684 | 1.4253 | -28.3895 | -35.4432 | -44.0095 | -52.9179 | -61.2463 | -68.2074 | -74.7789 | -114.2126 | -138.8042 | -162.8842
|  | CHICHESTER BSP | EE |  |  |  |  | 36.2179 | 31.5253 | 5.8947 | -0.36421 | -7.9232 | -15.7642 | -23.1 | -29.2621 | -35.0684 | -63.4853 | -87.0389 | -103.9095 | -0.22105 | -5.4695 | -35.3326 | -42.3895 | -50.9653 | -59.8758 | -68.2116 | -75.1726 | -81.7442 | -114.1863 | -142.6632 | -162.0221 | 6.6684 | 1.4253 | -28.3895 | -35.4432 | -44.0095 | -52.9179 | -61.2463 | -68.2074 | -74.7789 | -107.2211 | -136.0105 | -155.3684
|  | CHICHESTER BSP | HT |  |  |  |  | 36.7726 | 31.18 | 24.4726 | 17.3905 | 8.8316 | -0.088421 | -8.1611 | -14.8958 | -27.0705 | -69.9411 | -91.6105 | -112.6863 | 1.7137 | -4.3947 | -11.9137 | -19.8832 | -29.5737 | -39.6842 | -48.8453 | -56.4579 | -70.48 | -121.2032 | -145.7968 | -169.8926 | 9.0242 | 2.7811 | -4.7463 | -12.7053 | -22.3842 | -32.4853 | -41.6379 | -49.2453 | -63.2442 | -114.2126 | -138.8042 | -162.8842
|  | CHICHESTER BSP | HE |  |  |  |  | 38.8474 | 34.9674 | 30.28 | 24.8421 | 18.0253 | 10.9242 | 4.2895 | -1.1232 | -6.1611 | -35.7716 | -52.8653 | -66.4947 | 2.6116 | -1.7589 | -7.06 | -13.2242 | -20.9958 | -29.1084 | -36.6895 | -42.8474 | -48.5895 | -85.1526 | -104.8905 | -120.6884 | 9.5105 | 5.1484 | -0.14421 | -6.3 | -14.0579 | -22.1653 | -29.7337 | -35.8811 | -41.6211 | -78.6168 | -98.3316 | -114.1116
|  | CHICHESTER BSP | CF |  |  |  |  | 41.6126 | 39.4811 | 37.2674 | 34.9537 | 32.3958 | 29.5484 | 26.72 | 23.9505 | 21.1116 | 3.9632 | -3.5853 | -11.9295 | 5.6905 | 3.2884 | 0.79474 | -1.8147 | -4.7042 | -7.9347 | -11.14 | -14.2832 | -17.5053 | -37.1537 | -45.7684 | -55.4295 | 12.5884 | 10.1905 | 7.6989 | 5.0937 | 2.2063 | -1.02 | -4.2221 | -7.36 | -10.5789 | -30.1979 | -38.8053 | -48.4579
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL BSP | MINIMUM HEADROOM | SY 65479 80511 | NO | YES | 131.7158 | -11.7547 | -16.9147 | -22.5516 | -28.4916 | -34.5842 | -40.0084 | -46.0989 | -51.0558 | -55.8863 | -90.8947 | -112.6747 | -132.5063 | -44.0326 | -48.1768 | -54.4484 | -61.0684 | -67.8095 | -73.74 | -80.5137 | -85.9695 | -91.2916 | -130.8726 | -155.0684 | -177.5116 | -38.3284 | -44.4316 | -50.7063 | -57.3305 | -64.1053 | -70.0737 | -76.8884 | -82.3874 | -87.7579 | -127.6474 | -152.2042 | -174.7895
|  | CHICKERELL BSP | EE |  |  |  |  | -1.1884 | -6.2421 | -13.8537 | -18.9653 | -24.0526 | -28.4389 | -32.9147 | -37.5758 | -42.1011 | -70.4684 | -94.3147 | -111.0347 | -30.1779 | -35.8411 | -43.46 | -49.1568 | -54.7653 | -59.5411 | -64.4232 | -69.5263 | -74.4979 | -106.28 | -132.9463 | -151.9189 | -26.4274 | -32.0937 | -40.3526 | -46.0547 | -51.7011 | -56.5253 | -61.4642 | -66.6263 | -71.6611 | -103.8695 | -131.0347 | -150.1737
|  | CHICKERELL BSP | HT |  |  |  |  | -11.1842 | -16.9147 | -22.5516 | -28.4916 | -34.5842 | -40.0084 | -46.0989 | -51.0558 | -55.8863 | -90.8947 | -112.6747 | -132.5063 | -41.7684 | -48.1768 | -54.4484 | -61.0684 | -67.8095 | -73.74 | -80.5137 | -85.9695 | -91.2916 | -130.8726 | -155.0684 | -177.5116 | -38.0211 | -44.4316 | -50.7063 | -57.3305 | -64.1053 | -70.0737 | -76.8884 | -82.3874 | -87.7579 | -127.6474 | -152.2042 | -174.7895
|  | CHICKERELL BSP | HE |  |  |  |  | 1.1053 | -2.2937 | -6.3579 | -10.6147 | -14.8863 | -18.3979 | -21.9905 | -25.7232 | -29.3232 | -52.8211 | -71.9505 | -85.1947 | -26.8789 | -31.5274 | -36.0905 | -40.8579 | -45.5853 | -49.4337 | -53.3905 | -57.5295 | -61.5347 | -88.3042 | -110.2653 | -125.4432 | -23.1263 | -27.7747 | -32.3411 | -37.1105 | -41.8642 | -45.7389 | -49.72 | -53.8832 | -57.9179 | -84.8705 | -106.9842 | -122.2916
|  | CHICKERELL BSP | CF |  |  |  |  | -11.7547 | 1.4695 | -0.10737 | -2.2011 | -4.2789 | -6.1653 | -8.1968 | -10.4242 | -12.7463 | -31.5021 | -40.4853 | -49.2642 | -44.0326 | -26.7821 | -29.1063 | -31.4526 | -33.7516 | -35.8284 | -38.0737 | -40.5526 | -43.1526 | -64.6095 | -74.8011 | -84.8568 | -38.3284 | -23.0295 | -25.3537 | -27.7021 | -30.0126 | -32.1 | -34.3621 | -36.8526 | -39.4611 | -60.9832 | -71.2495 | -81.3968
MELKSHAM GSP | CHIPPENHAM BSP | CHIPPENHAM BSP | MINIMUM HEADROOM | ST 92629 74275 | NO | YES | 219.2884 | -160.9274 | -137.2158 | -180.1863 | -202.9621 | -238.4821 | -281.2811 | -285.5221 | -290.4895 | -293.6958 | -325.0337 | -346.0947 | -361.0621 | -202.2189 | -189.7495 | -239.9 | -266.6947 | -308.1284 | -358.0968 | -362.6947 | -368.1379 | -370.7189 | -405.6895 | -427.5179 | -444.3379 | -197.3379 | -184.8979 | -235.0589 | -261.8116 | -303.2242 | -353.1789 | -357.8526 | -363.38 | -365.8979 | -401.4926 | -423.5179 | -440.5611
|  | CHIPPENHAM BSP | EE |  |  |  |  | -128.7126 | -103.8126 | -144.3495 | -202.9621 | -238.4821 | -281.2811 | -285.5221 | -290.4895 | -293.6958 | -325.0337 | -346.0947 | -361.0621 | -164.4358 | -150.7463 | -198.0789 | -266.6947 | -308.1284 | -358.0968 | -362.6947 | -368.1379 | -370.7189 | -405.6895 | -427.5179 | -444.3379 | -159.5463 | -145.8895 | -193.24 | -261.8116 | -303.2242 | -353.1789 | -357.8526 | -363.38 | -365.8979 | -401.4926 | -423.5179 | -440.5611
|  | CHIPPENHAM BSP | HT |  |  |  |  | -160.9274 | -137.2158 | -180.1863 | -185.1379 | -191.3989 | -201.2189 | -208.5347 | -213.2295 | -239.2232 | -268.3326 | -298.2832 | -311.3368 | -202.2189 | -189.7495 | -239.9 | -245.4 | -252.3547 | -263.4737 | -271.6926 | -276.8421 | -307.06 | -339.5316 | -375.3284 | -389.7411 | -197.3379 | -184.8979 | -235.0589 | -240.5547 | -247.5516 | -258.7084 | -266.9737 | -272.1842 | -302.4274 | -335.3337 | -372.0947 | -386.7095
|  | CHIPPENHAM BSP | HE |  |  |  |  | -126.5937 | -100.8032 | -102.9989 | -124.2021 | -159.3168 | -171.1 | -174.6074 | -178.8316 | -182.7684 | -208.72 | -233.1347 | -245.0779 | -162.1684 | -147.5179 | -149.9095 | -174.6042 | -215.5558 | -229.1337 | -232.9926 | -237.7095 | -242.1147 | -271.6474 | -303.0432 | -316.5832 | -157.2768 | -142.6505 | -145.0463 | -169.7474 | -210.7495 | -224.3642 | -228.2621 | -233.0179 | -237.4611 | -267.2368 | -299.4853 | -313.2011
|  | CHIPPENHAM BSP | CF |  |  |  |  | -100.3695 | -98.0526 | -99.1095 | -100.2568 | -132.5379 | -134.1811 | -135.8684 | -137.4937 | -139.3895 | -149.4284 | -160.1768 | -167.16 | -124.6579 | -144.5232 | -145.6726 | -146.9274 | -184.6947 | -186.5 | -188.3495 | -190.1326 | -192.2389 | -203.4516 | -215.6695 | -223.5453 | -118.9874 | -139.6558 | -140.8053 | -142.0611 | -179.8611 | -181.68 | -183.5505 | -185.3484 | -187.4695 | -198.7653 | -211.0989 | -219.0947
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ 15716 93165 | NO | YES | 93.6832 | 13.5305 | 11.8968 | 10.1579 | 8.3568 | 8.4137 | 5.2642 | 2.12 | -69.0063 | -72.0211 | -94.42 | -107.1842 | -118.7979 | -6.4768 | -9.8032 | -13.4021 | -17.1979 | -17.2979 | -20.7526 | -24.1526 | -107.8853 | -111.1547 | -136.5011 | -150.6905 | -163.7579 | -2.0232 | -5.4021 | -9.0621 | -12.8716 | -13.3137 | -16.8095 | -20.2158 | -103.8768 | -107.1474 | -132.5284 | -146.7821 | -159.8621
|  | CHRISTCHURCH BSP | EE |  |  |  |  | 14.5021 | 13.1579 | 11.7295 | 10.2305 | 8.6547 | 7.1242 | 5.42 | 3 | 1.2832 | -8.1632 | -22.5916 | -31.46 | -4.5642 | -7.3126 | -10.3284 | -13.5274 | -15.9211 | -18.4663 | -20.9684 | -23.5579 | -25.2337 | -35.2937 | -51.6011 | -61.6105 | -0.078947 | -2.8747 | -5.9421 | -9.1916 | -11.6053 | -14.16 | -16.6716 | -19.2737 | -21.1232 | -31.4695 | -47.8832 | -57.9253
|  | CHRISTCHURCH BSP | HT |  |  |  |  | 13.5305 | 11.8968 | 10.1579 | 8.3568 | 8.4137 | 5.2642 | 2.12 | -69.0063 | -72.0211 | -94.42 | -107.1842 | -118.7979 | -6.4768 | -9.8032 | -13.4021 | -17.1979 | -17.2979 | -20.7526 | -24.1526 | -107.8853 | -111.1547 | -136.5011 | -150.6905 | -163.7579 | -2.0232 | -5.4021 | -9.0621 | -12.8716 | -13.3137 | -16.8095 | -20.2158 | -103.8768 | -107.1474 | -132.5284 | -146.7821 | -159.8621
|  | CHRISTCHURCH BSP | HE |  |  |  |  | 15.7168 | 14.7432 | 13.6674 | 12.5084 | 11.2547 | 10.0579 | 8.9253 | 7.8653 | 7.6558 | -27.8358 | -38.9653 | -44.9989 | -2.0853 | -4.0737 | -6.3663 | -8.8716 | -10.6042 | -12.4611 | -14.2147 | -15.9421 | -16.7347 | -59.6389 | -72.4221 | -79.3053 | 1.8968 | 0.41684 | -1.9126 | -4.46 | -6.2147 | -8.0968 | -9.8726 | -11.6242 | -12.5474 | -55.7579 | -68.5537 | -75.4579
|  | CHRISTCHURCH BSP | CF |  |  |  |  | 16.5705 | 16.0421 | 15.4905 | 14.9232 | 14.3253 | 13.7158 | 13.1168 | 12.5263 | 11.9347 | 9.9926 | 9.5421 | 5.4747 | -0.39263 | -1.5211 | -2.7484 | -4.0368 | -5.0895 | -6.2642 | -7.4579 | -8.5632 | -9.6263 | -13.2147 | -16.3042 | -20.9253 | 2.8011 | 2.2358 | 1.6442 | 0.45158 | -0.61789 | -1.8137 | -3.0274 | -4.1526 | -5.2316 | -8.9853 | -12.3632 | -17.0232
IVER 132KV GSP | CIPPENHAM BSP | CIPPENHAM BSP | MINIMUM HEADROOM | SU 96266 79634 | NO | YES | 0 | 99.3347 | 98.8 | 98.2305 | 97.6411 | 97.0305 | 96.4137 | 95.8705 | 95.2126 | 94.1389 | 89.2042 | 84.7432 | 80.6084 | 91.2832 | 89.8179 | 87.9895 | 86.0737 | 84.6347 | 83.6074 | 82.3884 | 81.1379 | 79.9558 | 74.4737 | 69.4726 | 64.7989 | 92.5547 | 91.9642 | 90.4821 | 88.5663 | 87.1253 | 86.0989 | 84.8779 | 83.6284 | 82.4442 | 76.9579 | 71.9526 | 67.2758
|  | CIPPENHAM BSP | EE |  |  |  |  | 99.6463 | 99.2042 | 98.7347 | 98.24 | 97.7274 | 97.2316 | 96.7558 | 96.2979 | 95.8905 | 92.1032 | 88.6253 | 85.4632 | 91.6221 | 90.7189 | 89.2863 | 87.5642 | 86.3116 | 85.2126 | 84.1442 | 83.0684 | 82.0705 | 77.6537 | 73.7442 | 70.1516 | 92.8884 | 92.3979 | 91.7789 | 90.0568 | 88.8021 | 87.7053 | 86.6347 | 85.5579 | 84.5589 | 80.1368 | 76.2221 | 72.6274
|  | CIPPENHAM BSP | HT |  |  |  |  | 99.3347 | 98.8 | 98.2305 | 97.6411 | 97.0305 | 96.4137 | 95.8705 | 95.2126 | 94.1389 | 89.2042 | 84.7432 | 80.6084 | 91.2832 | 89.8179 | 87.9895 | 86.0737 | 84.6347 | 83.6074 | 82.3884 | 81.1379 | 79.9558 | 74.4737 | 69.4726 | 64.7989 | 92.5547 | 91.9642 | 90.4821 | 88.5663 | 87.1253 | 86.0989 | 84.8779 | 83.6284 | 82.4442 | 76.9579 | 71.9526 | 67.2758
|  | CIPPENHAM BSP | HE |  |  |  |  | 100.0337 | 99.7074 | 99.3484 | 98.9611 | 98.5484 | 98.1526 | 97.7789 | 97.4305 | 97.1316 | 96.0242 | 93.5537 | 91.3484 | 92.0379 | 91.6726 | 90.7126 | 89.4758 | 88.4726 | 87.6284 | 86.5337 | 85.76 | 85.0863 | 81.9663 | 79.1621 | 76.6305 | 93.3053 | 92.9389 | 92.5326 | 91.9684 | 90.9653 | 90.12 | 89.0253 | 88.2505 | 87.5768 | 84.4547 | 81.6484 | 79.1147
|  | CIPPENHAM BSP | CF |  |  |  |  | 100.2989 | 100.1158 | 99.9242 | 99.7274 | 99.5221 | 99.3137 | 99.1095 | 98.9063 | 98.7032 | 97.7968 | 97.3432 | 97.0905 | 92.3326 | 92.1326 | 91.9211 | 91.6926 | 91.1621 | 90.5095 | 89.9232 | 89.5411 | 89.08 | 86.7537 | 84.7905 | 83.0789 | 93.6011 | 93.4 | 93.1884 | 92.9589 | 92.7232 | 92.4884 | 92.2621 | 92.0326 | 91.5716 | 89.2442 | 87.28 | 85.5674
MINETY GSP | CIRENCESTER BSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP 02701 00368 | NO | YES | 127.2632 | -108.4379 | -122.0663 | -169.6642 | -251.2232 | -254.6116 | -258.0453 | -261.5737 | -264.8432 | -273.7842 | -311.4505 | -327.7189 | -336.7389 | -146.74 | -162.6947 | -218.2621 | -313.9242 | -317.6747 | -321.4726 | -325.4011 | -329.0358 | -339.3526 | -382.6989 | -400.9558 | -411.0505 | -142.3558 | -158.32 | -213.9042 | -309.4947 | -313.2663 | -317.0895 | -321.0411 | -324.7053 | -335.04 | -378.5484 | -397.0495 | -407.2358
|  | CIRENCESTER BSP | EE |  |  |  |  | -105.9874 | -122.0663 | -132.0368 | -176.5526 | -179.4368 | -182.2642 | -185.02 | -187.6611 | -190.24 | -204.5442 | -226.6905 | -234.4863 | -143.9611 | -162.6947 | -174.2463 | -226.3516 | -229.5326 | -232.6411 | -235.6684 | -238.5558 | -241.3832 | -257.2147 | -282.3253 | -291.0737 | -139.5768 | -158.32 | -169.88 | -222.0011 | -225.2084 | -228.3505 | -231.4126 | -234.3474 | -237.2158 | -253.3421 | -278.8032 | -287.6537
|  | CIRENCESTER BSP | HT |  |  |  |  | -108.4379 | -110.6547 | -169.6642 | -251.2232 | -254.6116 | -258.0453 | -261.5737 | -264.8432 | -273.7842 | -311.4505 | -327.7189 | -336.7389 | -146.74 | -149.1695 | -218.2621 | -313.9242 | -317.6747 | -321.4726 | -325.4011 | -329.0358 | -339.3526 | -382.6989 | -400.9558 | -411.0505 | -142.3558 | -144.7853 | -213.9042 | -309.4947 | -313.2663 | -317.0895 | -321.0411 | -324.7053 | -335.04 | -378.5484 | -397.0495 | -407.2358
|  | CIRENCESTER BSP | HE |  |  |  |  | -92.9505 | -93.8021 | -103.3379 | -104.6442 | -107.0147 | -109.3316 | -111.6158 | -113.7632 | -115.8463 | -142.2589 | -161.6905 | -167.8179 | -128.7926 | -129.6926 | -140.7779 | -142.1926 | -144.8168 | -147.3884 | -149.9274 | -152.3095 | -154.6326 | -185.1263 | -207.5979 | -214.5305 | -124.4042 | -125.3042 | -136.3916 | -137.8084 | -140.4484 | -143.0389 | -145.5979 | -147.9968 | -150.3389 | -180.9663 | -203.5379 | -210.56
|  | CIRENCESTER BSP | CF |  |  |  |  | -49.5937 | -91.3242 | -92.1253 | -93.0526 | -94.1295 | -95.2432 | -96.3737 | -97.5032 | -98.7379 | -118.8179 | -122.4316 | -126.1874 | -77.9295 | -126.9537 | -127.8379 | -128.8695 | -130.0611 | -131.2947 | -132.5495 | -133.8042 | -135.1853 | -158.4316 | -162.4274 | -166.6684 | -73.4589 | -122.4989 | -123.3842 | -124.4158 | -125.6168 | -126.8611 | -128.1211 | -129.3853 | -130.7716 | -154.0674 | -158.18 | -162.48
FAWLEY GSP | COWES BSP | COWES BSP | MINIMUM HEADROOM | SZ 50486 94250 | NO | YES | 15.7895 | -34.4989 | -37.7389 | -41.1811 | -43.3958 | 4.1747 | 0.47474 | -2.8684 | -6.1842 | -9.9158 | -13.9968 | -7.8716 | -18.0137 | -77.5095 | -81.1084 | -84.9368 | -87.0737 | -30.8189 | -34.9284 | -38.6147 | -42.2716 | -46.7358 | -51.6516 | -38.8579 | -47.2211 | -74.1347 | -77.7305 | -81.5547 | -84.0305 | -27.9158 | -32.0558 | -35.7789 | -39.4779 | -44.0516 | -48.9884 | -45.5137 | -56.9653
|  | COWES BSP | EE |  |  |  |  | 14.8105 | 12.3242 | 9.6074 | 8.0737 | 4.1747 | 0.47474 | -2.8684 | -6.1842 | -9.9158 | 69.4274 | 57.1474 | 48.8126 | -19.3421 | -22.0916 | -25.0979 | -26.4695 | -30.8189 | -34.9284 | -38.6147 | -42.2716 | -46.7358 | 53.9874 | 40.4874 | 31.1326 | -16.0758 | -18.8242 | -21.8305 | -23.5432 | -27.9158 | -32.0558 | -35.7789 | -39.4779 | -44.0516 | 44.4916 | 30.6368 | 21.1726
|  | COWES BSP | HT |  |  |  |  | -34.4989 | -37.7389 | -41.1811 | -43.3958 | 44.9989 | 38.2989 | 31.9484 | 25.0221 | 21.8463 | 4.5379 | -7.8716 | -18.0137 | -77.5095 | -81.1084 | -84.9368 | -87.0737 | 23.5642 | 15.7284 | 8.5063 | 0.59053 | -2.9126 | -22.2158 | -35.8716 | -47.2211 | -74.1347 | -77.7305 | -81.5547 | -84.0305 | 14.6568 | 6.6579 | -0.59368 | -8.5421 | -12.0789 | -31.6032 | -45.5137 | -56.9653
|  | COWES BSP | HE |  |  |  |  | 16.7632 | 14.8758 | 12.7337 | 11.7526 | 8.4347 | 5.2926 | 2.5095 | -0.88 | -3.2747 | -13.9968 | 69.8347 | 63.6074 | -17.2063 | -19.3053 | -21.6895 | -22.4611 | -26.1789 | -29.7021 | -32.8074 | -36.9389 | -39.6137 | -51.6516 | 53.6663 | 46.6147 | -13.9453 | -16.0379 | -18.42 | -19.5326 | -23.2663 | -26.8032 | -29.9232 | -34.1368 | -36.8295 | -48.9884 | 44.3474 | 37.2032
|  | COWES BSP | CF |  |  |  |  | 45.5042 | 17.64 | 16.6926 | 15.5853 | 14.3179 | 12.9863 | 11.6453 | 10.1968 | 8.6642 | 0.12842 | -2.8053 | -6.8379 | 16.6526 | -16.2221 | -17.2695 | -18.5021 | -19.9063 | -21.3842 | -22.8747 | -24.4947 | -26.2168 | -35.8853 | -38.8579 | -43.4232 | 19.8537 | -12.9589 | -14.0063 | -15.2389 | -16.6505 | -18.1368 | -19.6347 | -21.26 | -22.9874 | -32.6884 | -36.0579 | -40.6811
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | COWLEY LOCAL (RESERVE) BSP | MINIMUM HEADROOM | SP 56113 03074 | NO | YES | 68.2842 | 13.7653 | 11.9758 | 9.5779 | -41.9411 | -43.6505 | -45.2474 | -48.0232 | -53.9737 | -59.4558 | -81.3537 | -97.5105 | -101.2958 | 4.7179 | 2.68 | -0.085263 | -61.4611 | -63.3495 | -65.0484 | -68.2074 | -75.1126 | -81.4716 | -106.8632 | -127.4063 | -131.6453 | 5.4821 | 3.4484 | 0.68737 | -60.5726 | -62.4611 | -64.1484 | -67.3032 | -74.1989 | -80.5474 | -105.9095 | -126.8074 | -131.0474
|  | COWLEY LOCAL (RESERVE) BSP | EE |  |  |  |  | 14.3958 | 12.7979 | 10.5895 | 7.4789 | 6.0863 | 4.7 | 2.3526 | -3.3579 | -8.6379 | -25.9179 | -37.4032 | -40.1295 | 5.4021 | 3.5747 | 1.0158 | -2.6263 | -4.1895 | -5.7474 | -8.4737 | -15.2621 | -21.5474 | -40.46 | -53.6789 | -56.7368 | 6.1684 | 4.3432 | 1.7874 | -1.8495 | -3.4126 | -4.9705 | -7.6947 | -14.4747 | -20.7505 | -39.0232 | -52.2421 | -55.3084
|  | COWLEY LOCAL (RESERVE) BSP | HT |  |  |  |  | 13.7653 | 11.9758 | 9.5779 | -41.9411 | -43.6505 | -45.2474 | -48.0232 | -53.9737 | -59.4558 | -81.3537 | -97.5105 | -101.2958 | 4.7179 | 2.68 | -0.085263 | -61.4611 | -63.3495 | -65.0484 | -68.2074 | -75.1126 | -81.4716 | -106.8632 | -127.4063 | -131.6453 | 5.4821 | 3.4484 | 0.68737 | -60.5726 | -62.4611 | -64.1484 | -67.3032 | -74.1989 | -80.5474 | -105.9095 | -126.8074 | -131.0474
|  | COWLEY LOCAL (RESERVE) BSP | HE |  |  |  |  | 15.2368 | 13.8989 | 11.9421 | 9.0653 | 4.8421 | 3.6379 | 2.4611 | -0.89789 | -5.9263 | -30.9537 | -41.7274 | -43.3705 | 6.32 | 4.7768 | 2.4905 | -0.89895 | -5.9084 | -7.2737 | -8.6126 | -12.5926 | -18.5989 | -50.8484 | -63.4958 | -65.3537 | 7.0842 | 5.5432 | 3.26 | -0.12316 | -5.1253 | -6.4905 | -7.8274 | -11.8021 | -17.7979 | -50.5284 | -63.1779 | -65.0389
|  | COWLEY LOCAL (RESERVE) BSP | CF |  |  |  |  | 26.4979 | 25.8211 | 14.5695 | 13.3105 | 11.5495 | 9.2358 | 6.4821 | 3.5042 | 0.53684 | -12.0611 | -18.6642 | -19.7432 | 19.7495 | 18.9811 | 5.5211 | 4.0411 | 1.9568 | -0.79474 | -4.0779 | -7.6316 | -11.1768 | -26.2053 | -34.0863 | -35.3116 | 20.5947 | 19.8147 | 6.2874 | 4.8105 | 2.7284 | -0.02 | -3.2979 | -6.8463 | -10.3832 | -25.3895 | -33.2589 | -34.4874
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL (MAIN) BSP | MINIMUM HEADROOM | SP 56113 03074 | NO | YES | 44.2105 | 65.8379 | 64.9821 | 28.1116 | 116.2442 | 114.3389 | 105.5768 | 102.4842 | 99.5737 | 96.7905 | 82.7305 | 72.7442 | 61.5674 | 47.2653 | 45.6379 | -4.4853 | 83.4579 | 81.3811 | 71.0316 | 67.4937 | 64.1611 | 60.9684 | 44.7358 | 33.3884 | 19.4137 | 51.7432 | 50.1168 | -0.024211 | 87.9189 | 85.7895 | 75.4326 | 71.8895 | 68.5495 | 65.3505 | 49.0853 | 37.6937 | 23.3884
|  | COWLEY LOCAL (MAIN) BSP | EE |  |  |  |  | 66.3032 | 65.5874 | 64.8221 | 154.0168 | 153.1663 | 149.5684 | 145.3632 | 142.0221 | 139.42 | 129.5579 | 120.8916 | 113.8421 | 49.3063 | 47.3032 | 45.5747 | 133.5768 | 131.1863 | 123.7916 | 118.8968 | 115.0358 | 112.0537 | 101.7232 | 91.7568 | 83.5611 | 53.1358 | 51.7811 | 50.0537 | 138.0547 | 135.6579 | 128.2568 | 123.3526 | 119.4853 | 116.4947 | 106.6 | 96.5747 | 88.3579
|  | COWLEY LOCAL (MAIN) BSP | HT |  |  |  |  | 65.8379 | 64.9821 | 28.1116 | 116.2442 | 114.3389 | 105.5768 | 102.4842 | 99.5737 | 96.7905 | 82.7305 | 72.7442 | 61.5674 | 47.2653 | 45.6379 | -4.4853 | 83.4579 | 81.3811 | 71.0316 | 67.4937 | 64.1611 | 60.9684 | 44.7358 | 33.3884 | 19.4137 | 51.7432 | 50.1168 | -0.024211 | 87.9189 | 85.7895 | 75.4326 | 71.8895 | 68.5495 | 65.3505 | 49.0853 | 37.6937 | 23.3884
|  | COWLEY LOCAL (MAIN) BSP | HE |  |  |  |  | 66.8968 | 66.3547 | 65.7568 | 155.1105 | 154.4137 | 152.5516 | 148.6453 | 145.8263 | 143.5821 | 130.2084 | 123.3495 | 117.9242 | 50.6989 | 49.1084 | 47.8084 | 136.2337 | 134.2389 | 127.0937 | 122.5189 | 119.2463 | 116.6505 | 99.9137 | 91.8663 | 85.4789 | 53.7768 | 53.1737 | 52.2863 | 140.7126 | 138.7147 | 131.5621 | 126.9842 | 123.7084 | 121.1074 | 103.8411 | 95.7874 | 89.3926
|  | COWLEY LOCAL (MAIN) BSP | CF |  |  |  |  | 67.3347 | 67.0274 | 66.7095 | 156.38 | 156.0337 | 155.68 | 155.3316 | 154.9884 | 154.6432 | 145.4558 | 141.0811 | 137.4063 | 51.4547 | 51.1358 | 50.8063 | 140.4 | 139.4568 | 138.0537 | 136.2863 | 133.9242 | 131.3821 | 118.6821 | 113.5926 | 109.2684 | 54.28 | 53.9579 | 53.6253 | 143.2726 | 142.8916 | 142.4758 | 140.76 | 138.3968 | 135.8526 | 123.1432 | 117.9926 | 113.6579
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU 78324 50817 | NO | YES | 33.5789 | 75.3232 | 73.9105 | 72.4042 | 160.8547 | 158.9958 | 155.5232 | 151.8389 | 149.6716 | 137.3211 | 128.2853 | 118.1853 | 109.8653 | 54.5179 | 51.6158 | 48.6558 | 135.7242 | 132.5589 | 128.78 | 124.7221 | 122.4295 | 107.6726 | 98.0663 | 87.0326 | 77.6811 | 59.5579 | 56.7105 | 53.8021 | 140.92 | 137.7895 | 134.0737 | 130.0779 | 127.7621 | 112.9568 | 103.1084 | 91.8158 | 82.38
|  | COXMOOR WOOD BSP | EE |  |  |  |  | 76.1789 | 75.0189 | 73.7821 | 162.4989 | 161.1095 | 159.7421 | 158.4358 | 156.3537 | 137.3211 | 128.2853 | 118.1853 | 109.8653 | 56.2347 | 53.8737 | 51.5074 | 139.2674 | 136.9137 | 134.4853 | 132.2147 | 129.8863 | 107.6726 | 98.0663 | 87.0326 | 77.6811 | 61.2463 | 58.9274 | 56.6021 | 144.3895 | 142.0589 | 139.6516 | 137.3937 | 135.0779 | 112.9568 | 103.1084 | 91.8158 | 82.38
|  | COXMOOR WOOD BSP | HT |  |  |  |  | 75.3232 | 73.9105 | 72.4042 | 160.8547 | 158.9958 | 155.5232 | 151.8389 | 149.6716 | 147.4695 | 133.2389 | 120.6684 | 113.9505 | 54.5179 | 51.6158 | 48.6558 | 135.7242 | 132.5589 | 128.78 | 124.7221 | 122.4295 | 120.0842 | 104.4126 | 90.5274 | 83.2211 | 59.5579 | 56.7105 | 53.8021 | 140.92 | 137.7895 | 134.0737 | 130.0779 | 127.7621 | 125.3916 | 109.5579 | 95.4853 | 88.1011
|  | COXMOOR WOOD BSP | HE |  |  |  |  | 77.2811 | 76.4684 | 75.5674 | 164.5979 | 163.5189 | 162.4874 | 161.5095 | 160.5926 | 159.7905 | 155.74 | 148.9747 | 142.9863 | 58.4674 | 56.84 | 55.1516 | 143.5484 | 141.8547 | 140.1979 | 138.6726 | 137.0884 | 135.5695 | 129.2642 | 121.6632 | 114.8653 | 63.0821 | 61.8389 | 60.1789 | 148.5989 | 146.9168 | 145.2726 | 143.7558 | 142.1863 | 140.68 | 134.4232 | 126.84 | 119.9737
|  | COXMOOR WOOD BSP | CF |  |  |  |  | 78.0316 | 77.6011 | 77.1579 | 166.6989 | 166.1989 | 165.6884 | 165.1874 | 164.6905 | 164.2011 | 161.9811 | 160.1126 | 156.04 | 60.0126 | 59.1179 | 58.2484 | 147.4105 | 146.5221 | 145.5853 | 144.6705 | 143.7358 | 142.8063 | 138.14 | 133.6705 | 129.0442 | 63.8789 | 63.4211 | 62.9526 | 152.3979 | 151.5179 | 150.5895 | 149.6874 | 148.7611 | 147.8474 | 143.2432 | 138.8558 | 134.3147
IVER 132KV GSP | DENHAM B BSP | DENHAM B BSP | MINIMUM HEADROOM | TQ 01785 87618 | NO | YES | 0 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | DENHAM B BSP | EE | [7 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | DENHAM B BSP | HT | [7 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | DENHAM B BSP | HE | [7 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | DENHAM B BSP | CF | [7 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
IVER 132KV GSP | DENHAM BSP | DENHAM BSP | MINIMUM HEADROOM | TQ 01785 87618 | NO | YES | 40.0432 | 69.0295 | 68.0947 | 59.1147 | 57.4653 | 56.0263 | 31.3432 | 29.9484 | 28.5105 | 27.1653 | 21.2895 | 16.2032 | 11.9179 | 51.9505 | 49.8063 | 29.0368 | 27.2463 | 25.7211 | -3.0979 | -4.5779 | -6.1147 | -7.5579 | -13.8916 | -19.4253 | -24.1905 | 57.3463 | 55.2884 | 34.7495 | 32.9589 | 31.4263 | 2.5947 | 1.1011 | -0.44421 | -1.9032 | -8.3126 | -13.9337 | -18.7316
|  | DENHAM BSP | EE |  |  |  |  | 69.5863 | 68.8211 | 59.1147 | 57.4653 | 56.0263 | 31.3432 | 29.9484 | 28.5105 | 27.1653 | 21.2895 | 16.2032 | 11.9179 | 52.7547 | 51.4074 | 29.0368 | 27.2463 | 25.7211 | -3.0979 | -4.5779 | -6.1147 | -7.5579 | -13.8916 | -19.4253 | -24.1905 | 58.3232 | 56.8263 | 34.7495 | 32.9589 | 31.4263 | 2.5947 | 1.1011 | -0.44421 | -1.9032 | -8.3126 | -13.9337 | -18.7316
|  | DENHAM BSP | HT |  |  |  |  | 69.0295 | 68.0947 | 82.1053 | 81.0832 | 80.0053 | 78.9253 | 77.9716 | 77.1042 | 76.2989 | 69.5411 | 63.1263 | 57.4253 | 51.9505 | 49.8063 | 62.5642 | 60.3853 | 58.4821 | 56.5684 | 54.6989 | 52.9674 | 51.2411 | 43.2653 | 36.1358 | 29.7737 | 57.3463 | 55.2884 | 68.1379 | 66.0411 | 64.1916 | 62.28 | 60.4042 | 58.6653 | 56.9284 | 48.9011 | 41.7032 | 35.3126
|  | DENHAM BSP | HE |  |  |  |  | 70.3137 | 69.7768 | 84.1779 | 83.5347 | 82.8347 | 65.16 | 64.1568 | 63.1168 | 62.1621 | 58.2179 | 55.0126 | 52.2758 | 53.7589 | 52.9926 | 67.1305 | 65.7895 | 64.6853 | 36.2863 | 35.2242 | 34.1105 | 33.0832 | 28.8032 | 25.2463 | 22.1768 | 59.0779 | 58.5211 | 72.5221 | 71.2316 | 70.1484 | 41.9947 | 40.9263 | 39.8095 | 38.7779 | 34.4632 | 30.8821 | 27.7874
|  | DENHAM BSP | CF |  |  |  |  | 70.8042 | 70.5179 | 85.22 | 84.9095 | 84.5842 | 84.2516 | 83.9232 | 83.5968 | 83.2737 | 81.8211 | 81.0716 | 80.6316 | 54.4053 | 53.9947 | 68.5579 | 68.12 | 67.7084 | 67.2842 | 66.7432 | 66.0568 | 65.3505 | 61.9926 | 59.4179 | 57.2632 | 59.5684 | 59.2821 | 73.9842 | 73.6516 | 73.3105 | 72.7558 | 72.1368 | 71.4737 | 70.7968 | 67.5663 | 65.1084 | 62.94
COWLEY GSP | DRAYTON BSP | DRAYTON BSP | MINIMUM HEADROOM | SU 46684 92706 | NO | YES | 88.4842 | 28.3495 | 22.34 | 11.0453 | -130.1021 | -134.4895 | -140.9789 | -147.1432 | -124.1989 | -152.8032 | -190.7989 | -208.1011 | -225.8105 | -7.2674 | -14.0442 | -27.3653 | -192.7874 | -197.3379 | -204.6453 | -211.6053 | -172.9168 | -206.2589 | -249.8916 | -269.4768 | -289.6926 | -1.2211 | -7.9916 | -21.1779 | -186.4053 | -191.3779 | -198.6758 | -205.6253 | -161.64 | -194.9926 | -238.6484 | -258.2474 | -278.4758
|  | DRAYTON BSP | EE |  |  |  |  | 29.6179 | 24.1916 | 11.0453 | -12.8695 | -18.2674 | -37.48 | -43.2126 | -48.5747 | -53.4716 | -55.3747 | -73.8337 | -88.1853 | -6.0179 | -12.1568 | -27.3653 | -55.2368 | -61.2242 | -83.2832 | -89.7737 | -95.8389 | -101.38 | -91.5726 | -112.7021 | -129.1463 | 0.14526 | -5.9926 | -21.1779 | -49.0042 | -55.1168 | -77.5653 | -84.0495 | -90.1105 | -95.6484 | -80.3305 | -101.4937 | -117.9653
|  | DRAYTON BSP | HT |  |  |  |  | 28.3495 | 22.34 | 16.3695 | -130.1021 | -134.4895 | -140.9789 | -147.1432 | -124.1989 | -152.8032 | -190.7989 | -208.1011 | -225.8105 | -7.2674 | -14.0442 | -20.7589 | -192.7874 | -197.3379 | -204.6453 | -211.6053 | -172.9168 | -206.2589 | -249.8916 | -269.4768 | -289.6926 | -1.2211 | -7.9916 | -14.6989 | -186.4053 | -191.3779 | -198.6758 | -205.6253 | -161.64 | -194.9926 | -238.6484 | -258.2474 | -278.4758
|  | DRAYTON BSP | HE |  |  |  |  | 32.5284 | 31.5684 | 23.1168 | 17.5895 | 12.8768 | -5.6611 | -10.7432 | -15.4368 | -19.6863 | -18.4011 | -33.9316 | -45.5389 | 6 | 0.77789 | -13.5495 | -19.8484 | -25.0926 | -46.4232 | -52.2053 | -57.5495 | -62.3874 | -49.1853 | -67.1116 | -80.5484 | 12.1284 | 6.94 | -7.3632 | -13.6547 | -19.0211 | -40.7379 | -46.5116 | -51.8484 | -56.6811 | -37.8747 | -55.8126 | -69.2589
|  | DRAYTON BSP | CF |  |  |  |  | 32.6095 | 32.1011 | 29.3716 | 26.8305 | 24.4063 | 22.7726 | 20.0853 | 17.4 | 14.7379 | 4.3116 | -2.4863 | -9.7568 | 7.6589 | 5.0042 | -6.6389 | -9.5305 | -12.2832 | -13.9853 | -17.0474 | -20.1074 | -23.14 | -34.6874 | -42.3842 | -50.8147 | 12.2663 | 11.3126 | -0.27789 | -3.1632 | -5.9147 | -7.7958 | -10.8505 | -13.9084 | -16.9358 | -28.8874 | -36.7 | -45.1179
EALING GSP | EALING BSP | EALING BSP | MINIMUM HEADROOM | TQ 18371 79475 | NO | YES | 0.014737 | 98.0905 | 97.4253 | 96.72 | 94.4684 | 91.6905 | 89.1063 | 87.2032 | 85.6421 | 84.1389 | 77.0442 | 70.2358 | 64.3063 | 80.0558 | 77.1926 | 74.3495 | 71.2242 | 68.08 | 65.1684 | 63.0463 | 61.3189 | 59.6505 | 51.7242 | 43.82 | 37.1063 | 84.1779 | 81.2779 | 78.3979 | 75.2779 | 72.1389 | 69.2316 | 67.1116 | 65.3863 | 63.72 | 55.8032 | 47.8611 | 41.1568
|  | EALING BSP | EE |  |  |  |  | 98.4811 | 97.9326 | 97.3505 | 96.7274 | 95.7695 | 93.6811 | 91.5253 | 89.4084 | 87.9179 | 82.5063 | 77.9421 | 73.7211 | 81.3074 | 79.3421 | 77.5379 | 75.3042 | 72.7442 | 70.3905 | 67.9537 | 65.5589 | 63.8958 | 58.0874 | 52.9589 | 48.1705 | 85.4453 | 83.4537 | 81.6295 | 79.3674 | 76.7947 | 74.4442 | 72.0116 | 69.62 | 67.9589 | 62.2074 | 57.0853 | 52.3053
|  | EALING BSP | HT |  |  |  |  | 98.0905 | 97.4253 | 96.72 | 94.4684 | 91.6905 | 89.1063 | 87.2032 | 85.6421 | 84.1389 | 77.0442 | 70.2358 | 64.3063 | 80.0558 | 77.1926 | 74.3495 | 71.2242 | 68.08 | 65.1684 | 63.0463 | 61.3189 | 59.6505 | 51.7242 | 43.82 | 37.1063 | 84.1779 | 81.2779 | 78.3979 | 75.2779 | 72.1389 | 69.2316 | 67.1116 | 65.3863 | 63.72 | 55.8032 | 47.8611 | 41.1568
|  | EALING BSP | HE |  |  |  |  | 98.86 | 98.4168 | 97.9253 | 97.3979 | 96.8358 | 95.7337 | 93.7937 | 92.0368 | 90.8758 | 86.4221 | 82.5221 | 79.7189 | 82.3263 | 80.5747 | 79.0263 | 77.0621 | 74.7505 | 72.6611 | 70.46 | 68.4674 | 67.1705 | 62.1642 | 57.3853 | 54.1758 | 86.4537 | 84.7011 | 83.1347 | 81.1432 | 78.8032 | 76.7137 | 74.5147 | 72.5253 | 71.2295 | 66.2305 | 61.3853 | 58.1811
|  | EALING BSP | CF |  |  |  |  | 99.1326 | 98.8516 | 98.5589 | 98.2568 | 97.9442 | 97.6253 | 97.3126 | 97.0011 | 96.6916 | 92.6221 | 90.1158 | 88.1863 | 83.9411 | 83.1884 | 82.5779 | 81.9379 | 81.2632 | 80.5716 | 79.7842 | 78.5968 | 77.2905 | 69.16 | 66.3263 | 64.1168 | 87.5021 | 87.1937 | 86.6947 | 86.0611 | 85.3947 | 84.7095 | 83.9158 | 82.7137 | 81.3895 | 73.2168 | 70.3874 | 68.1811
LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT BSP | MINIMUM HEADROOM | TQ 08394 73826 | NO | YES | 1.7895 | 80.6789 | 96.0053 | 94.4242 | 92.3611 | 89.7653 | 87.3032 | 84.4547 | 81.6263 | 79.2305 | 69.5253 | 63.3221 | 57.9095 | 61.8747 | 75.8526 | 73.5958 | 71.2137 | 68.2979 | 65.5389 | 62.3074 | 59.0874 | 56.3716 | 45.3726 | 38.3895 | 32.2747 | 66.3758 | 80.4042 | 78.2063 | 75.8895 | 73.0537 | 70.3705 | 67.2379 | 64.1158 | 61.4274 | 50.4463 | 43.4737 | 37.3674
|  | EAST BEDFONT BSP | EE |  |  |  |  | 81.0632 | 96.5042 | 95.9095 | 94.9926 | 93.1642 | 91.3537 | 88.9242 | 85.9842 | 83.4084 | 74.3137 | 69.6453 | 65.7011 | 63.1211 | 77.7053 | 76.1568 | 74.3253 | 72.1621 | 70.1242 | 67.3716 | 64.0168 | 61.0758 | 50.7116 | 45.4484 | 40.98 | 67.2295 | 82.2053 | 80.6926 | 78.9084 | 76.8021 | 74.8179 | 72.1495 | 68.9 | 66.0526 | 55.7779 | 50.5242 | 46.0611
|  | EAST BEDFONT BSP | HT |  |  |  |  | 80.6789 | 96.0053 | 94.4242 | 92.3611 | 89.7653 | 87.3032 | 84.4547 | 81.6263 | 79.2305 | 69.5253 | 63.3221 | 57.9095 | 61.8747 | 75.8526 | 73.5958 | 71.2137 | 68.2979 | 65.5389 | 62.3074 | 59.0874 | 56.3716 | 45.3726 | 38.3895 | 32.2747 | 66.3758 | 80.4042 | 78.2063 | 75.8895 | 73.0537 | 70.3705 | 67.2379 | 64.1158 | 61.4274 | 50.4463 | 43.4737 | 37.3674
|  | EAST BEDFONT BSP | HE |  |  |  |  | 81.5474 | 97.1337 | 96.6747 | 96.1811 | 95.1989 | 93.7116 | 91.4737 | 88.7716 | 86.5137 | 78.9442 | 75.5368 | 72.8232 | 64.2368 | 79.1453 | 77.8979 | 76.3821 | 74.4842 | 72.7168 | 70.1453 | 67.0463 | 64.4547 | 55.7789 | 51.9042 | 48.7968 | 67.7537 | 83.2968 | 82.3958 | 80.9211 | 79.0758 | 77.3568 | 74.8653 | 71.8674 | 69.3621 | 60.84 | 56.9716 | 53.8684
|  | EAST BEDFONT BSP | CF |  |  |  |  | 81.8916 | 97.6611 | 97.4179 | 97.1705 | 96.9126 | 96.6484 | 96.3895 | 96.1347 | 95.8789 | 87.0611 | 84.1737 | 82.34 | 64.6453 | 80.4011 | 80.1411 | 79.7811 | 79.1116 | 78.4495 | 77.4937 | 76.4505 | 75.4263 | 64.9453 | 61.6484 | 59.5453 | 68.1526 | 83.9063 | 83.6442 | 83.3726 | 83.0884 | 82.7979 | 81.9979 | 80.9832 | 79.9895 | 69.8663 | 66.6726 | 64.6011
LOVEDEAN GSP | FAREHAM (MAIN) BSP | FAREHAM (MAIN) BSP | MINIMUM HEADROOM | SU 56534 04031 | NO | YES | 33.7726 | 77.8242 | 76.4074 | 72.2758 | 67.7084 | 26.6295 | 20.9389 | 15.0432 | -4.9853 | -10.0558 | -29.3095 | -42.0421 | -53.5316 | 51.52 | 47.8968 | 43.18 | 37.9326 | -13.6126 | -19.9274 | -26.5611 | -49.84 | -55.5389 | -77.1021 | -91.1537 | -104.0221 | 56.9011 | 53.4674 | 49.1737 | 44.0789 | -7.2737 | -13.5905 | -20.2232 | -43.48 | -49.1853 | -70.8358 | -84.9926 | -97.8884
|  | FAREHAM (MAIN) BSP | EE |  |  |  |  | 77.8242 | 76.4937 | 73.9379 | 70.14 | 65.8958 | 61.4453 | 56.6189 | 34.3105 | 29.16 | 4.4347 | -5.7937 | -14.5389 | 51.52 | 47.9642 | 44.1116 | 39.7095 | 34.7811 | 29.5895 | 23.8305 | -4.4011 | -10.6337 | -38.9547 | -50.24 | -60.0632 | 56.9011 | 53.4674 | 49.7558 | 45.5168 | 40.7674 | 35.6379 | 29.86 | 1.6642 | -4.5811 | -33.0116 | -44.4611 | -54.3221
|  | FAREHAM (MAIN) BSP | HT |  |  |  |  | 78.0537 | 76.4074 | 72.2758 | 67.7084 | 26.6295 | 20.9389 | 15.0432 | -4.9853 | -10.0558 | -29.3095 | -42.0421 | -53.5316 | 52.3095 | 47.8968 | 43.18 | 37.9326 | -13.6126 | -19.9274 | -26.5611 | -49.84 | -55.5389 | -77.1021 | -91.1537 | -104.0221 | 58.0516 | 53.7611 | 49.1737 | 44.0789 | -7.2737 | -13.5905 | -20.2232 | -43.48 | -49.1853 | -70.8358 | -84.9926 | -97.8884
|  | FAREHAM (MAIN) BSP | HE |  |  |  |  | 79.0589 | 78.1074 | 77.0589 | 74.6589 | 71.0189 | 67.2 | 62.8779 | 41.1095 | 36.7221 | 15.8274 | 7.7895 | 1.7926 | 54.1526 | 51.5137 | 48.4547 | 44.7968 | 40.5421 | 36.0421 | 30.8947 | 3.1884 | -2.1863 | -26.7768 | -36.4558 | -43.2537 | 59.5421 | 56.9105 | 53.9653 | 50.4516 | 46.3568 | 42.0358 | 36.9379 | 9.2726 | 3.8947 | -20.72 | -30.5579 | -37.3874
|  | FAREHAM (MAIN) BSP | CF |  |  |  |  | 79.9116 | 79.4032 | 78.8737 | 78.3263 | 77.7463 | 77.1547 | 76.4842 | 74.6147 | 72.3789 | 59.1168 | 54.5621 | 50.8032 | 56.1063 | 54.9737 | 53.6568 | 52.2042 | 50.5716 | 48.8968 | 46.9453 | 44.7442 | 42.0758 | 25.9421 | 20.5 | 15.9253 | 61.5642 | 60.3947 | 59.0274 | 57.5726 | 55.9947 | 54.3779 | 52.4979 | 50.3874 | 47.8347 | 31.9832 | 26.5232 | 21.9232
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | FAREHAM (RESERVE) BSP | MINIMUM HEADROOM | SU 56534 04031 | NO | YES | 52.5263 | 18.2632 | 17.3821 | 16.4474 | 15.4737 | 14.1768 | 12.0895 | 10.2832 | 8.6958 | 7.4042 | 0.97368 | -5.6474 | -11.7463 | 6.48 | 4.6411 | 2.6674 | 0.38947 | -1.2516 | -3.6411 | -5.6579 | -7.3747 | -8.7589 | -15.7505 | -23.0958 | -29.9284 | 8.5011 | 6.7337 | 4.8389 | 2.6589 | 1.0326 | -1.2547 | -3.2116 | -4.9305 | -6.3168 | -13.3179 | -20.6737 | -27.5042
|  | FAREHAM (RESERVE) BSP | EE |  |  |  |  | 18.7726 | 18.0453 | 17.2695 | 16.4537 | 15.6011 | 14.3411 | 12.7095 | 11.2505 | 10.1674 | 5.6189 | 0.48737 | -4.1189 | 7.6368 | 6.1705 | 4.6 | 2.7295 | 0.93368 | -1.1295 | -3 | -4.6516 | -5.8295 | -10.66 | -16.3495 | -21.5326 | 9.6084 | 8.1968 | 6.6874 | 4.8947 | 3.1663 | 1.1968 | -0.59789 | -2.1853 | -3.3295 | -8.2432 | -13.9526 | -19.1368
|  | FAREHAM (RESERVE) BSP | HT |  |  |  |  | 18.2632 | 17.3821 | 16.4474 | 15.4737 | 14.1768 | 12.0895 | 10.2832 | 8.6958 | 7.4042 | 0.97368 | -5.6474 | -11.7463 | 6.48 | 4.6411 | 2.6674 | 0.38947 | -1.2516 | -3.6411 | -5.6579 | -7.3747 | -8.7589 | -15.7505 | -23.0958 | -29.9284 | 8.5011 | 6.7337 | 4.8389 | 2.6589 | 1.0326 | -1.2547 | -3.2116 | -4.9305 | -6.3168 | -13.3179 | -20.6737 | -27.5042
|  | FAREHAM (RESERVE) BSP | HE |  |  |  |  | 19.4063 | 18.8663 | 18.2716 | 17.6305 | 16.9421 | 16.2842 | 15.6653 | 15.0147 | 14.2937 | 11.6358 | 8.2842 | 5.2821 | 9.1084 | 8.0842 | 6.9463 | 5.4874 | 4.0811 | 2.4063 | 0.88947 | -0.35263 | -1.1326 | -4.0463 | -7.8632 | -11.2779 | 11.0189 | 10.0316 | 8.9316 | 7.5347 | 6.1811 | 4.5821 | 3.1295 | 1.9358 | 1.1758 | -1.6853 | -5.4337 | -8.8505
|  | FAREHAM (RESERVE) BSP | CF |  |  |  |  | 19.8516 | 19.5495 | 19.2347 | 18.9105 | 18.5726 | 18.2274 | 17.8905 | 17.5526 | 17.2189 | 15.7221 | 14.1674 | 12.1674 | 9.8558 | 9.4968 | 8.8421 | 8.1116 | 7.3463 | 6.4905 | 5.7116 | 4.8674 | 4.1463 | 0.83579 | -1.3979 | -3.7821 | 11.8 | 11.3884 | 10.7579 | 10.0589 | 9.3242 | 8.5074 | 7.7589 | 6.9526 | 6.26 | 3.0832 | 0.92632 | -1.3463
FLEET-BRAMLEY GSP | FERNHURST BSP | FERNHURST BSP | MINIMUM HEADROOM | SU 72730 39772 | NO | YES | 50.7968 | 48.66 | 47.5063 | 46.1726 | 44.7505 | 31.1947 | 14.3053 | 13.2126 | 12.1 | 11.0221 | 5.2958 | -1.0295 | -5.1179 | 38.5095 | 37.2421 | 35.7663 | 34.1874 | 18.9137 | -0.80526 | -1.9832 | -3.1842 | -4.3526 | -10.6526 | -17.7305 | -22.3453 | 39.6926 | 38.4242 | 36.9484 | 35.3684 | 20.4505 | 0.71579 | -0.47263 | -1.6874 | -2.8684 | -9.2589 | -16.4358 | -21.0821
|  | FERNHURST BSP | EE |  |  |  |  | 49.4242 | 48.4779 | 48.4821 | 47.6537 | 31.1947 | 14.3053 | 13.2126 | 12.1 | 11.0221 | 5.2958 | -1.0295 | -5.1179 | 39.3537 | 38.3147 | 39.0705 | 38.1821 | 18.9137 | -0.80526 | -1.9832 | -3.1842 | -4.3526 | -10.6526 | -17.7305 | -22.3453 | 40.5368 | 39.4968 | 40.62 | 39.7326 | 20.4505 | 0.71579 | -0.47263 | -1.6874 | -2.8684 | -9.2589 | -16.4358 | -21.0821
|  | FERNHURST BSP | HT |  |  |  |  | 48.66 | 47.5063 | 46.1726 | 44.7505 | 41.6158 | 39.4684 | 37.2832 | 36.3905 | 35.5221 | 27.6326 | 19.0863 | 15.4147 | 38.5095 | 37.2421 | 35.7663 | 34.1874 | 30.5853 | 28.1958 | 25.7453 | 24.8063 | 23.8895 | 15.0779 | 4.6358 | 0.57368 | 39.6926 | 38.4242 | 36.9484 | 35.3684 | 31.76 | 29.3611 | 26.9011 | 25.9537 | 25.0284 | 16.1516 | 5.3495 | 1.26
|  | FERNHURST BSP | HE |  |  |  |  | 50.1263 | 49.7095 | 48.9232 | 47.9926 | 46.8579 | 30.3053 | 29.46 | 28.62 | 27.8011 | 23.3916 | 17.3305 | 14.4032 | 40.3842 | 39.6695 | 38.7979 | 37.7611 | 36.4926 | 17.0568 | 16.1421 | 15.2295 | 14.3305 | 9.3979 | 1.1737 | -2.1579 | 41.4463 | 40.8211 | 39.9821 | 38.9442 | 37.6695 | 18.2242 | 17.3021 | 16.3842 | 15.48 | 10.5095 | 1.9063 | -1.4516
|  | FERNHURST BSP | CF |  |  |  |  | 50.4495 | 50.2747 | 50.0926 | 49.9042 | 49.4063 | 48.9126 | 48.4621 | 47.9863 | 47.4842 | 44.4779 | 44.1632 | 42.2695 | 41.1589 | 40.7968 | 40.3821 | 39.8947 | 39.3253 | 38.7747 | 38.2768 | 37.7484 | 37.1863 | 33.7632 | 34.1747 | 32.0221 | 42.1274 | 41.7968 | 41.4379 | 41.02 | 40.5053 | 39.9526 | 39.4537 | 38.9221 | 38.3579 | 34.9221 | 35.6853 | 33.5137
LOVEDEAN GSP | FORT WIDLEY BSP | FORT WIDLEY BSP | MINIMUM HEADROOM | SU 64948 05441 | NO | YES | 0 | 67.3905 | 96.6663 | 95.5853 | 93.2821 | 90.7442 | 88.4389 | 86.3295 | 84.3137 | 82.3326 | 57.7747 | 51.2021 | 44.72 | 57.96 | 85.8358 | 83.5263 | 80.9526 | 78.1063 | 75.5411 | 73.1853 | 70.9316 | 68.7095 | 40.2137 | 32.8326 | 25.4589 | 60.0947 | 88.06 | 85.7505 | 83.1768 | 80.3295 | 77.7589 | 75.3989 | 73.1421 | 70.9147 | 42.3853 | 34.9726 | 27.5874
|  | FORT WIDLEY BSP | EE |  |  |  |  | 67.8316 | 97.2421 | 96.6189 | 95.2884 | 93.1253 | 91.1737 | 89.3284 | 87.5242 | 85.7453 | 78.6684 | 65.2663 | 60.1726 | 59.0768 | 87.2916 | 85.3284 | 83.1642 | 80.7411 | 78.56 | 76.5 | 74.4863 | 72.4905 | 64.5411 | 49.0274 | 43.2074 | 61.1621 | 89.4642 | 87.5516 | 85.3884 | 82.9611 | 80.7758 | 78.7116 | 76.6926 | 74.6926 | 66.7074 | 51.1474 | 45.3126
|  | FORT WIDLEY BSP | HT |  |  |  |  | 67.3905 | 96.6663 | 95.5853 | 93.2821 | 90.7442 | 88.4389 | 86.3295 | 84.3137 | 82.3326 | 57.7747 | 51.2021 | 44.72 | 57.96 | 85.8358 | 83.5263 | 80.9526 | 78.1063 | 75.5411 | 73.1853 | 70.9316 | 68.7095 | 40.2137 | 32.8326 | 25.4589 | 60.0947 | 88.06 | 85.7505 | 83.1768 | 80.3295 | 77.7589 | 75.3989 | 73.1421 | 70.9147 | 42.3853 | 34.9726 | 27.5874
|  | FORT WIDLEY BSP | HE |  |  |  |  | 68.3884 | 97.9726 | 97.5126 | 97.0179 | 95.5411 | 93.8895 | 92.3389 | 90.8463 | 89.3747 | 83.6905 | 71.7021 | 67.7895 | 60.3032 | 88.8895 | 87.2832 | 85.4663 | 83.3716 | 81.5158 | 79.7758 | 78.1011 | 76.4347 | 69.9842 | 55.9937 | 51.4768 | 62.2105 | 90.9989 | 89.4758 | 87.6916 | 85.5947 | 83.7358 | 81.9947 | 80.3158 | 78.6474 | 72.1821 | 58.1758 | 53.6484
|  | FORT WIDLEY BSP | CF |  |  |  |  | 68.7758 | 98.5589 | 98.3316 | 98.0958 | 97.8505 | 97.6 | 97.3526 | 97.1105 | 96.6632 | 91.6484 | 89.1274 | 86.6695 | 61.4674 | 90.8232 | 90.0842 | 89.2853 | 88.4189 | 87.5432 | 86.6158 | 85.6537 | 84.6305 | 78.9137 | 76.0453 | 73.2105 | 62.6432 | 92.4011 | 92.1326 | 91.3747 | 90.5537 | 89.7221 | 88.84 | 87.8747 | 86.8505 | 81.1284 | 78.2537 | 75.4095
MELKSHAM GSP | FROME BSP | FROME BSP | MINIMUM HEADROOM | ST 78803 48019 | NO | YES | 9.4737 | 96.7979 | 83.4547 | 36.9853 | 123.2126 | 118.9779 | 115.0474 | 110.5 | 95.1011 | 63.3253 | 26.6747 | -1.5253 | -13.6516 | 64.14 | 48.6989 | 0.12737 | 85.9274 | 81.2884 | 77.0274 | 72.0368 | 54.2937 | 16.9189 | -24.1747 | -57.9705 | -71.3505 | 68.4495 | 53.0316 | 4.0084 | 89.8084 | 85.1126 | 80.7758 | 75.7032 | 57.8937 | 20.8137 | -20.64 | -55.4158 | -69.0105
|  | FROME BSP | EE |  |  |  |  | 98.5126 | 85.7653 | 36.9853 | 123.2126 | 118.9779 | 115.0474 | 110.5 | 95.1011 | 91.8863 | 78.4263 | 58.3884 | 44.4916 | 66.0168 | 51.2358 | 0.12737 | 85.9274 | 81.2884 | 77.0274 | 72.0368 | 54.2937 | 50.8758 | 38.9137 | 17.4126 | 1.8263 | 70.3211 | 55.5611 | 4.0084 | 89.8084 | 85.1126 | 80.7758 | 75.7032 | 57.8937 | 54.3737 | 41.8347 | 19.7021 | 3.8758
|  | FROME BSP | HT |  |  |  |  | 96.7979 | 83.4547 | 49.2758 | 134.2442 | 129.8853 | 124.54 | 118.7947 | 112.7063 | 63.3253 | 26.6747 | -1.5253 | -13.6516 | 64.14 | 48.6989 | 14.0368 | 98.3947 | 93.8126 | 87.9074 | 81.5042 | 74.6874 | 16.9189 | -24.1747 | -57.9705 | -71.3505 | 68.4495 | 53.0316 | 18.3705 | 102.7358 | 97.8442 | 91.8874 | 85.4295 | 78.5526 | 20.8137 | -20.64 | -55.4158 | -69.0105
|  | FROME BSP | HE |  |  |  |  | 100.7989 | 98.1116 | 56.0811 | 142.9589 | 139.38 | 136.1874 | 132.3642 | 117.8526 | 115.4642 | 103.0505 | 82.9232 | 71.9116 | 68.5053 | 65.4905 | 21.4811 | 107.9832 | 104.0326 | 100.5189 | 96.2579 | 79.4116 | 76.8147 | 63.3158 | 38.2368 | 25.7842 | 72.8147 | 69.8053 | 25.8179 | 112.3242 | 108.3337 | 104.7926 | 100.4937 | 83.6347 | 80.9968 | 66.9674 | 41.2916 | 28.6526
|  | FROME BSP | CF |  |  |  |  | 110.0105 | 102.6347 | 71.5284 | 150.8916 | 149.3347 | 147.8695 | 146.0737 | 144.1095 | 142.2147 | 133.8621 | 128.4516 | 122.68 | 83.7126 | 69.5295 | 38.3063 | 115.8758 | 114.1642 | 112.5589 | 110.5705 | 108.3811 | 106.26 | 96.9779 | 91.1789 | 84.7232 | 88.0674 | 73.64 | 42.3979 | 119.9905 | 118.2632 | 116.64 | 114.6326 | 112.4253 | 110.2947 | 100.9305 | 94.7589 | 88.1747
LOVEDEAN GSP | HAVANT BSP | HAVANT BSP | MINIMUM HEADROOM | SU 70625 05720 | NO | YES | 22.1063 | 95.7968 | 95.1674 | 94.5095 | 93.6368 | 87.5832 | 81.7053 | 76.1632 | 70.62 | 65.3147 | 42.8589 | 22.5074 | 4.5726 | 70.0147 | 67.7895 | 66.3937 | 63.4042 | 56.8358 | 50.4674 | 44.4421 | 38.3884 | 32.5937 | 8.0232 | -14.3832 | -34.2168 | 78.4947 | 76.1695 | 74.7284 | 70.0821 | 63.3726 | 56.8737 | 50.72 | 44.5326 | 38.5979 | 13.4495 | -9.5284 | -29.8695
|  | HAVANT BSP | EE |  |  |  |  | 104.8105 | 103.1505 | 101.3863 | 98.6116 | 93.5063 | 88.5611 | 83.8242 | 79.0389 | 74.6232 | 56.5832 | 40.0874 | 26.0947 | 81.8368 | 77.8221 | 73.7526 | 68.7568 | 63.2032 | 57.8337 | 52.6916 | 47.4832 | 42.6747 | 22.9547 | 4.7547 | -10.78 | 88.3758 | 84.4653 | 80.4968 | 75.5295 | 69.8589 | 64.3758 | 59.12 | 53.7947 | 48.8779 | 28.6726 | 9.9779 | -5.9716
|  | HAVANT BSP | HT |  |  |  |  | 103.6042 | 101.5842 | 99.1905 | 93.6368 | 87.5832 | 81.7053 | 76.1632 | 70.62 | 65.3147 | 42.8589 | 22.5074 | 4.5726 | 79.62 | 74.9137 | 69.4526 | 63.4042 | 56.8358 | 50.4674 | 44.4421 | 38.3884 | 32.5937 | 8.0232 | -14.3832 | -34.2168 | 86.2053 | 81.6168 | 76.2505 | 70.0821 | 63.3726 | 56.8737 | 50.72 | 44.5326 | 38.5979 | 13.4495 | -9.5284 | -29.8695
|  | HAVANT BSP | HE |  |  |  |  | 106.3474 | 105.1621 | 103.8526 | 102.4411 | 100.2442 | 96.0747 | 92.1232 | 88.2063 | 84.5526 | 70.6295 | 57.9158 | 47.3284 | 84.6674 | 81.5895 | 78.4432 | 74.8526 | 70.4368 | 65.8716 | 61.5663 | 57.2853 | 53.28 | 37.9642 | 23.8053 | 11.9547 | 91.2042 | 88.1558 | 85.0895 | 81.5947 | 77.2168 | 72.5505 | 68.1495 | 63.7716 | 59.6716 | 43.9758 | 29.4295 | 17.2368
|  | HAVANT BSP | CF |  |  |  |  | 95.7968 | 95.1674 | 94.5095 | 93.8305 | 93.1274 | 104.0305 | 103.3232 | 102.6211 | 100.7674 | 91.9832 | 81.9947 | 75.2453 | 70.0147 | 67.7895 | 66.3937 | 64.8947 | 63.2474 | 78.6842 | 76.3526 | 73.7495 | 70.8821 | 61.3137 | 50.1674 | 42.6158 | 78.4947 | 76.1695 | 74.7284 | 73.1789 | 71.4705 | 85.3263 | 83.0642 | 80.5432 | 77.6432 | 67.8663 | 56.4095 | 48.64
COWLEY GSP | HEADINGTON BSP | HEADINGTON BSP | MINIMUM HEADROOM | SP 54454 08145 | NO | YES | 19.9463 | 46.5789 | 45.2442 | 5.9379 | -6.5189 | -47.2968 | -54.3032 | -58.0589 | -61.4442 | -64.2811 | -75.6537 | -77.4874 | -81.0695 | 20.5421 | 19.1063 | -26.9979 | -42.64 | -90.4589 | -98.5347 | -102.7842 | -106.5937 | -109.7684 | -121.4284 | -120.9053 | -124.7863 | 24.4611 | 23.0232 | -22.9958 | -38.8211 | -86.5716 | -94.6642 | -98.9389 | -102.7789 | -105.9874 | -117.7053 | -117.0347 | -121.0032
|  | HEADINGTON BSP | EE |  |  |  |  | 78.9021 | 78.2621 | 30.4316 | -6.5189 | -47.2968 | -54.3032 | -58.0589 | -61.4442 | -64.2811 | -75.6537 | -77.4874 | -81.0695 | 64.1926 | 62.3726 | 0.70737 | -42.64 | -90.4589 | -98.5347 | -102.7842 | -106.5937 | -109.7684 | -121.4284 | -120.9053 | -124.7863 | 66.4895 | 65.4389 | 4.4505 | -38.8211 | -86.5716 | -94.6642 | -98.9389 | -102.7789 | -105.9874 | -117.7053 | -117.0347 | -121.0032
|  | HEADINGTON BSP | HT |  |  |  |  | 46.5789 | 45.2442 | 5.9379 | 2.3147 | -1.7484 | -9.4768 | -13.1453 | -23.5474 | -26.5284 | -40.1011 | -52.9579 | -59.5695 | 20.5421 | 19.1063 | -26.9979 | -31.1105 | -35.7063 | -44.6126 | -48.7547 | -60.8295 | -64.1758 | -79.3842 | -93.8137 | -102.1053 | 24.4611 | 23.0232 | -22.9958 | -27.1042 | -31.7116 | -40.6263 | -44.7853 | -56.8663 | -60.2368 | -75.6042 | -90.2242 | -98.7758
|  | HEADINGTON BSP | HE |  |  |  |  | 79.4821 | 79.0305 | 78.5295 | 40.7326 | 23.1768 | -20.3337 | -23.7211 | -26.6905 | -29.1526 | -42.16 | -47.9379 | -50.1484 | 65.2642 | 63.8526 | 61.5842 | 12.7505 | -7.7768 | -58.8558 | -62.7284 | -66.1095 | -68.9053 | -84.7074 | -92.2189 | -94.6042 | 67.2411 | 66.4568 | 64.7442 | 16.4789 | -4.0263 | -55.0211 | -58.9032 | -62.2958 | -65.1032 | -81.1737 | -88.9579 | -91.4168
|  | HEADINGTON BSP | CF |  |  |  |  | 79.8874 | 79.6453 | 47.8968 | 47.4242 | 9.2811 | 6.5747 | 4.7116 | 2.5895 | 0.51895 | -7.3032 | -10.1337 | -11.7179 | 66.7358 | 66.3863 | 20.9358 | 20.4232 | -24.3989 | -27.5221 | -29.6526 | -32.0916 | -34.4716 | -43.4074 | -46.5558 | -48.2789 | 68.0653 | 67.7737 | 24.6526 | 24.14 | -20.6042 | -23.7295 | -25.8663 | -28.3084 | -30.6853 | -39.6442 | -42.8337 | -44.6042
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU 84773 92191 | NO | YES | 0 | 58.7495 | 17.5947 | 14.8937 | 12.1674 | 9.2316 | 6.2621 | 3.2863 | 0.85684 | -1.4674 | -21.0232 | -31.7968 | -40.5358 | 17.9663 | -30.3189 | -33.2189 | -36.1421 | -39.2989 | -42.4895 | -45.7274 | -48.3453 | -50.8558 | -72.9611 | -84.9295 | -94.68 | 23.9768 | -24.3232 | -27.2253 | -30.1505 | -33.3074 | -36.5053 | -39.7474 | -42.3705 | -44.8842 | -67.0242 | -79.0326 | -88.7947
|  | HIGH WYCOMBE BSP | EE |  |  |  |  | 59.7895 | 57.6726 | 55.4832 | 53.2516 | 50.98 | 48.9021 | 47.5305 | 45.4242 | 43.4063 | 34.6105 | 22.1389 | 14.9558 | 18.9968 | 16.7158 | 14.3695 | 11.9789 | 9.5568 | 7.3547 | 6.0158 | 3.7621 | 1.5895 | -7.9863 | -22.1274 | -30.2158 | 25.0895 | 22.8084 | 20.4589 | 18.0716 | 15.6421 | 13.4368 | 12.0095 | 9.7484 | 7.5695 | -2.0516 | -16.2453 | -24.3537
|  | HIGH WYCOMBE BSP | HT |  |  |  |  | 58.7495 | 17.5947 | 14.8937 | 12.1674 | 9.2316 | 6.2621 | 3.2863 | 0.85684 | -1.4674 | -21.0232 | -31.7968 | -40.5358 | 17.9663 | -30.3189 | -33.2189 | -36.1421 | -39.2989 | -42.4895 | -45.7274 | -48.3453 | -50.8558 | -72.9611 | -84.9295 | -94.68 | 23.9768 | -24.3232 | -27.2253 | -30.1505 | -33.3074 | -36.5053 | -39.7474 | -42.3705 | -44.8842 | -67.0242 | -79.0326 | -88.7947
|  | HIGH WYCOMBE BSP | HE |  |  |  |  | 77.4368 | 60.5947 | 59.0695 | 57.4695 | 55.7842 | 54.2905 | 53.4958 | 51.9863 | 50.5968 | 44.8253 | 35.24 | 30.5526 | 39.6137 | 19.9021 | 18.2737 | 16.5705 | 14.7884 | 13.2179 | 12.5053 | 10.8958 | 9.4053 | 3.1074 | -7.8916 | -13.2263 | 45.7126 | 25.9947 | 24.3653 | 22.6632 | 20.8768 | 19.3053 | 18.5063 | 16.8958 | 15.4021 | 9.0789 | -1.9379 | -7.2874
|  | HIGH WYCOMBE BSP | CF |  |  |  |  | 78.6747 | 62.4232 | 61.5905 | 60.7168 | 59.8011 | 58.9232 | 58.0432 | 57.0926 | 56.1253 | 51.5874 | 48.5758 | 45.2484 | 40.9337 | 21.8453 | 20.9474 | 20.0105 | 19.0242 | 18.0853 | 17.1421 | 16.1147 | 15.0663 | 10.1389 | 6.8442 | 3.0421 | 47.0337 | 27.9389 | 27.0411 | 26.1032 | 25.1158 | 24.1716 | 23.2316 | 22.2021 | 21.1526 | 16.2147 | 12.8316 | 9.0189
LOVEDEAN GSP | HUNSTON BSP | HUNSTON BSP | MINIMUM HEADROOM | SU 86946 02627 | NO | YES | 45.0053 | 53.1095 | 51.7316 | 50.2674 | 47.9884 | 1.6242 | -2.2558 | -6.9621 | -10.0684 | -13.0295 | -39.7221 | -54.4632 | -67.2979 | 32.5253 | 29.3305 | 25.2484 | 21.2053 | -33.2968 | -37.5926 | -42.9011 | -46.3421 | -49.6263 | -80.2979 | -96.9779 | -111.5832 | 34.3211 | 30.6937 | 27.0832 | 23.1326 | -29.3705 | -33.5653 | -38.7253 | -42.0853 | -45.2926 | -75.6853 | -92.3768 | -106.9705
|  | HUNSTON BSP | EE |  |  |  |  | 53.9495 | 51.7537 | 50.5568 | 49.3074 | 39.5042 | 36.2168 | 32.9653 | 29.7232 | 26.7284 | 11.9442 | -1.4221 | -12.1295 | 34.5 | 29.3611 | 26.3379 | 23.1568 | 10.3811 | 6.7284 | 3.1053 | -0.51579 | -3.8621 | -20.6147 | -35.8968 | -48.2095 | 36.2863 | 30.6937 | 27.7074 | 24.6021 | 12.2632 | 8.6989 | 5.1642 | 1.6347 | -1.6274 | -17.9147 | -32.7495 | -44.6716
|  | HUNSTON BSP | HT |  |  |  |  | 53.1095 | 51.7316 | 50.2674 | 47.9884 | 1.6242 | -2.2558 | -6.9621 | -10.0684 | -13.0295 | -39.7221 | -54.4632 | -67.2979 | 32.5253 | 29.3305 | 25.2484 | 21.2053 | -33.2968 | -37.5926 | -42.9011 | -46.3421 | -49.6263 | -80.2979 | -96.9779 | -111.5832 | 34.3211 | 31.1358 | 27.0832 | 23.1326 | -29.3705 | -33.5653 | -38.7253 | -42.0853 | -45.2926 | -75.6853 | -92.3768 | -106.9705
|  | HUNSTON BSP | HE |  |  |  |  | 55.0263 | 53.1621 | 52.2884 | 51.3463 | 16.7589 | 14.0432 | 11.4789 | 8.8537 | 6.4305 | -13.2063 | -24.0653 | -32.5442 | 36.4011 | 32.0926 | 29.8126 | 27.2547 | -16.9358 | -19.9684 | -22.8316 | -25.7789 | -28.5063 | -51.2484 | -63.8095 | -73.6568 | 38.1821 | 33.3895 | 31.1379 | 28.6221 | -13.9147 | -16.8716 | -19.66 | -22.5284 | -25.1821 | -47.1653 | -59.3789 | -69.2221
|  | HUNSTON BSP | CF |  |  |  |  | 55.7726 | 54.2905 | 53.8611 | 53.42 | 52.9579 | 52.4895 | 52.0253 | 51.5674 | 51.1105 | 46.2474 | 29.5684 | 24.3379 | 37.5368 | 33.9958 | 33.2442 | 32.4989 | 31.6789 | 30.8705 | 30.0611 | 28.9463 | 27.5853 | 18.1684 | -1.3568 | -7.4274 | 39.3126 | 34.9884 | 34.3621 | 33.7358 | 33.0558 | 32.2516 | 31.4168 | 30.2558 | 28.9253 | 19.7884 | 0.96632 | -4.9011
FAWLEY GSP | LANGLEY BSP | LANGLEY BSP | MINIMUM HEADROOM | SU 45185 01376 | NO | YES | 0 | 46.6474 | 45.5684 | 45.1716 | 44.0705 | 42.9484 | 41.4874 | 39.9905 | 38.8642 | 37.3905 | 33.6432 | 29.1505 | 24.8842 | 40.3421 | 39.1611 | 38.8305 | 37.6474 | 36.4579 | 34.8642 | 33.2137 | 31.9905 | 30.3463 | 26.3232 | 21.3221 | 16.5189 | 41.1074 | 39.9505 | 39.5758 | 38.4032 | 37.2053 | 35.6105 | 33.9589 | 32.7326 | 31.0884 | 27.0526 | 22.0389 | 17.2295
|  | LANGLEY BSP | EE |  |  |  |  | 47.3863 | 46.5347 | 45.6589 | 44.7726 | 44.5737 | 43.6968 | 42.6137 | 41.4347 | 40.2737 | 36.9189 | 33.4663 | 30.2337 | 41.1621 | 40.2358 | 39.2874 | 38.3305 | 38.2263 | 37.2853 | 36.1179 | 34.8221 | 33.54 | 29.9074 | 26.06 | 22.4021 | 41.9074 | 40.9989 | 40.0674 | 39.1295 | 38.9726 | 38.0411 | 36.8621 | 35.5653 | 34.2789 | 30.6305 | 26.7674 | 23.1021
|  | LANGLEY BSP | HT |  |  |  |  | 46.6474 | 45.5684 | 45.1716 | 44.0705 | 42.9484 | 41.4874 | 39.9905 | 38.8642 | 37.3905 | 33.6432 | 29.1505 | 24.8842 | 40.3421 | 39.1611 | 38.8305 | 37.6474 | 36.4579 | 34.8642 | 33.2137 | 31.9905 | 30.3463 | 26.3232 | 21.3221 | 16.5189 | 41.1074 | 39.9505 | 39.5758 | 38.4032 | 37.2053 | 35.6105 | 33.9589 | 32.7326 | 31.0884 | 27.0526 | 22.0389 | 17.2295
|  | LANGLEY BSP | HE |  |  |  |  | 48.3505 | 47.7968 | 47.2074 | 46.5947 | 46.6463 | 46.0211 | 45.2916 | 44.5411 | 43.8526 | 41.2726 | 38.9421 | 36.7326 | 42.2316 | 41.6347 | 41.0042 | 40.3505 | 40.5221 | 39.8568 | 39.0568 | 38.2263 | 37.46 | 34.6389 | 32.0137 | 29.4853 | 42.8811 | 42.3347 | 41.7453 | 41.1 | 41.2137 | 40.5589 | 39.7768 | 38.9632 | 38.2158 | 35.3779 | 32.7463 | 30.2126
|  | LANGLEY BSP | CF |  |  |  |  | 48.9105 | 48.5884 | 48.2579 | 47.9179 | 47.5716 | 47.2179 | 46.8726 | 46.5084 | 46.8316 | 44.7432 | 43.2147 | 41.7347 | 42.84 | 42.4884 | 42.1274 | 41.7579 | 41.3789 | 40.9937 | 40.62 | 40.2221 | 40.6674 | 38.3295 | 36.6221 | 34.9242 | 43.3232 | 43.1158 | 42.7905 | 42.4568 | 42.1137 | 41.74 | 41.3716 | 40.98 | 41.3684 | 39.0842 | 37.3642 | 35.6632
IVER 132KV GSP | LONGFORD BSP | LONGFORD BSP | MINIMUM HEADROOM | TQ 03910 76751 | NO | YES | 2 | 45.4021 | 45.3368 | 45.2684 | 45.1989 | 45.1253 | 45.0505 | 44.9779 | 44.9063 | 44.8337 | 44.5116 | 44.3589 | 44.2684 | 40.1558 | 40.0789 | 39.9958 | 39.8968 | 39.7821 | 39.6663 | 39.5526 | 39.4379 | 39.1337 | 38.5042 | 38.0705 | 37.7074 | 31.5653 | 31.4968 | 31.4242 | 31.3463 | 31.2611 | 31.1737 | 31.0895 | 31.0053 | 30.8663 | 30.4547 | 30.22 | 29.9663
|  | LONGFORD BSP | EE |  |  |  |  | 69.0705 | 68.9105 | 68.7389 | 68.5589 | 68.3726 | 68.1926 | 68.0211 | 67.8526 | 67.7053 | 67.1758 | 100.4863 | 100.2095 | 58.4842 | 58.3242 | 58.1526 | 57.9726 | 57.7863 | 57.6032 | 57.4274 | 57.1747 | 56.4221 | 55.2158 | 87.5032 | 86.2011 | 59.2811 | 59.1211 | 58.9495 | 58.7695 | 58.5832 | 58.4032 | 58.2316 | 58.0632 | 57.9158 | 57.0242 | 89.3495 | 88.0853
|  | LONGFORD BSP | HT |  |  |  |  | 68.9537 | 68.7568 | 68.5474 | 68.3316 | 68.1116 | 67.8853 | 67.6863 | 67.5053 | 67.3368 | 66.6632 | 99.8274 | 99.4116 | 58.3674 | 58.1705 | 57.9611 | 57.7453 | 57.5263 | 57.3 | 57.0968 | 56.7495 | 55.8495 | 53.7895 | 85.6095 | 83.8684 | 59.1642 | 58.9674 | 58.7579 | 58.5421 | 58.3232 | 58.0968 | 57.8979 | 57.7168 | 57.5484 | 55.6316 | 87.5011 | 85.7695
|  | LONGFORD BSP | HE |  |  |  |  | 69.2116 | 69.0926 | 68.9621 | 68.82 | 68.6695 | 68.5263 | 68.3905 | 68.2642 | 68.1547 | 67.7874 | 101.2368 | 101.1011 | 58.6253 | 58.5063 | 58.3758 | 58.2337 | 58.0832 | 57.94 | 57.8042 | 57.6779 | 57.5684 | 56.6232 | 89.3126 | 88.4 | 59.4221 | 59.3032 | 59.1726 | 59.0305 | 58.88 | 58.7368 | 58.6011 | 58.4747 | 58.3653 | 57.9989 | 91.1084 | 90.2242
|  | LONGFORD BSP | CF |  |  |  |  | 45.4021 | 45.3368 | 45.2684 | 45.1989 | 45.1253 | 45.0505 | 44.9779 | 44.9063 | 44.8337 | 44.5116 | 44.3589 | 44.2684 | 40.1558 | 40.0789 | 39.9958 | 39.8968 | 39.7821 | 39.6663 | 39.5526 | 39.4379 | 39.1337 | 38.5042 | 38.0705 | 37.7074 | 31.5653 | 31.4968 | 31.4242 | 31.3463 | 31.2611 | 31.1737 | 31.0895 | 31.0053 | 30.8663 | 30.4547 | 30.22 | 29.9663
AMERSHAM GSP | LOUDWATER BSP | LOUDWATER BSP | MINIMUM HEADROOM | SU 90644 91247 | NO | YES | 1.0516 | 99.5916 | 97.4905 | 95.4474 | 93.4147 | 91.4063 | 89.4011 | 87.1379 | 84.76 | 82.6053 | 72.7863 | 64.1263 | 56.3863 | 87.8968 | 83.6126 | 78.7126 | 75.5716 | 72.6274 | 69.3432 | 66.3147 | 63.7316 | 61.3958 | 50.6589 | 41.0811 | 32.4453 | 92.0653 | 87.7284 | 82.7442 | 79.5674 | 76.6032 | 73.32 | 70.2905 | 67.7105 | 65.3768 | 54.6389 | 45.0611 | 36.4326
|  | LOUDWATER BSP | EE |  |  |  |  | 100.6189 | 98.8895 | 96.1821 | 94.4768 | 92.7895 | 90.6242 | 88.2537 | 86.2053 | 84.3947 | 76.6663 | 70.0979 | 64.3358 | 89.4726 | 85.9 | 78.7126 | 75.5716 | 72.6274 | 69.7863 | 67.2021 | 64.9874 | 63.0316 | 54.5853 | 47.3011 | 40.8358 | 93.6526 | 90.0358 | 82.7442 | 79.5674 | 76.6032 | 73.7642 | 71.1821 | 68.9674 | 67.0126 | 58.5611 | 51.2695 | 44.8074
|  | LOUDWATER BSP | HT |  |  |  |  | 99.5916 | 97.4905 | 95.4474 | 93.4147 | 91.4063 | 89.4011 | 87.1379 | 84.76 | 82.6053 | 72.7863 | 64.1263 | 56.3863 | 87.8968 | 83.6126 | 79.7958 | 76.1505 | 72.7379 | 69.3432 | 66.3147 | 63.7316 | 61.3958 | 50.6589 | 41.0811 | 32.4453 | 92.0653 | 87.7284 | 83.8695 | 80.1863 | 76.7389 | 73.32 | 70.2905 | 67.7105 | 65.3768 | 54.6389 | 45.0611 | 36.4326
|  | LOUDWATER BSP | HE |  |  |  |  | 101.92 | 100.6737 | 99.3716 | 98.0495 | 96.7211 | 95.4558 | 94.2874 | 93.2663 | 92.3895 | 89.1674 | 85.0642 | 81.4705 | 91.5147 | 88.8863 | 86.2695 | 83.7695 | 81.4316 | 79.2032 | 77.2168 | 75.6232 | 74.2684 | 68.6347 | 63.9053 | 59.8337 | 95.1442 | 93.0505 | 90.4021 | 87.8768 | 85.5116 | 83.26 | 81.2537 | 79.6463 | 78.2789 | 72.6042 | 67.8758 | 63.8063
|  | LOUDWATER BSP | CF |  |  |  |  | 102.9 | 102.2621 | 101.6758 | 101.0895 | 100.4632 | 99.7926 | 99.1611 | 98.5842 | 98.0126 | 95.3947 | 93.7811 | 92.6379 | 93.2284 | 91.9189 | 90.8389 | 89.8147 | 88.6705 | 87.3832 | 86.2221 | 85.2568 | 84.3263 | 79.8758 | 76.4484 | 73.5863 | 95.9242 | 95.4674 | 95.0116 | 93.9937 | 92.8358 | 91.5316 | 90.3568 | 89.3821 | 88.4432 | 83.9463 | 80.4758 | 77.5695
MANNINGTON GSP | LYTCHETT BSP | LYTCHETT BSP | MINIMUM HEADROOM | SY 97796 94214 | NO | YES | 84.42 | 1.6568 | -20.86 | -23.6579 | -26.9958 | -31.0653 | -35.8 | -40.5516 | -80.5358 | -89.9547 | -126.2621 | -140.9663 | -150.0937 | -18.98 | -50.5558 | -53.6211 | -57.3095 | -61.6832 | -66.9147 | -72.1905 | -118.9316 | -129.7084 | -170.8958 | -186.7126 | -196.6568 | -14.3137 | -45.7779 | -48.84 | -52.5295 | -57.0832 | -62.3663 | -67.6979 | -114.4253 | -125.2632 | -166.8821 | -183.2579 | -193.42
|  | LYTCHETT BSP | EE |  |  |  |  | 12.5011 | 30.8442 | 15.2147 | 12.7168 | 9.6832 | 6.6632 | 3.8253 | 1.4074 | -0.75158 | -16.9526 | -38.0937 | -47.4084 | -6.3495 | 10.1179 | -7.3053 | -10.0516 | -13.3084 | -16.54 | -19.5579 | -22.0726 | -24.2842 | -41.5463 | -64.7116 | -74.9842 | -1.7053 | 14.78 | -3.0884 | -5.8326 | -9.1526 | -12.46 | -15.5632 | -18.1674 | -20.4832 | -38.5537 | -62.4926 | -73.0011
|  | LYTCHETT BSP | HT |  |  |  |  | 1.6568 | -20.86 | -23.6579 | -26.9958 | -31.0653 | -35.8 | -40.5516 | -80.5358 | -89.9547 | -126.2621 | -140.9663 | -150.0937 | -18.98 | -50.5558 | -53.6211 | -57.3095 | -61.6832 | -66.9147 | -72.1905 | -118.9316 | -129.7084 | -170.8958 | -186.7126 | -196.6568 | -14.3137 | -45.7779 | -48.84 | -52.5295 | -57.0832 | -62.3663 | -67.6979 | -114.4253 | -125.2632 | -166.8821 | -183.2579 | -193.42
|  | LYTCHETT BSP | HE |  |  |  |  | 14.3968 | 33.3863 | 31.7463 | 29.8021 | 27.3726 | 24.9916 | 22.7842 | -16.5053 | -17.9526 | -29.2495 | -45.1768 | -52.1011 | -4.2853 | 12.8811 | 11.0874 | 8.9463 | 6.3126 | 3.7253 | 1.3347 | -44.6958 | -46.2147 | -58.5653 | -76.7179 | -84.3916 | 0.35684 | 17.5453 | 15.7526 | 13.6126 | 10.9379 | 8.3158 | 5.8874 | -40.1021 | -41.6621 | -54.4168 | -72.7653 | -80.6326
|  | LYTCHETT BSP | CF |  |  |  |  | 15.6358 | 44.8021 | 34.7758 | 33.9211 | 32.8368 | 31.6895 | 30.6337 | 29.5611 | 28.4842 | 22.6989 | 18.0116 | 13.2421 | -2.9432 | 26.14 | 14.4074 | 13.4705 | 12.2979 | 11.0526 | 9.9179 | 8.7495 | 7.58 | 1.24 | -3.8284 | -9.1305 | 1.6958 | 30.78 | 19.0695 | 18.1337 | 16.9432 | 15.6768 | 14.5232 | 13.3411 | 12.1537 | 5.7274 | 0.41263 | -5.02
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | MAIDENHEAD BSP | MINIMUM HEADROOM | SU 86592 79883 | NO | YES | 19.4737 | 93.8211 | 85.5337 | 81.2789 | 75.8305 | 71.0874 | 67.1105 | 63.8958 | 61.9063 | 60.0653 | 52.0516 | 44.8137 | 38.4042 | 71.5084 | 54.1232 | 49.2811 | 43.0358 | 37.6347 | 33.1347 | 29.5189 | 27.3505 | 25.3347 | 16.4811 | 8.4242 | 1.1811 | 76.6021 | 59.5747 | 54.7305 | 48.4832 | 43.0779 | 38.5726 | 34.9516 | 32.7768 | 30.7547 | 21.8632 | 13.7705 | 6.5105
|  | MAIDENHEAD BSP | EE |  |  |  |  | 94.5 | 85.5337 | 81.2789 | 75.8305 | 71.0874 | 67.1105 | 63.8958 | 61.9063 | 60.0653 | 52.0516 | 44.8137 | 38.4042 | 72.8695 | 54.1232 | 49.2811 | 43.0358 | 37.6347 | 33.1347 | 29.5189 | 27.3505 | 25.3347 | 16.4811 | 8.4242 | 1.1811 | 77.9495 | 59.5747 | 54.7305 | 48.4832 | 43.0779 | 38.5726 | 34.9516 | 32.7768 | 30.7547 | 21.8632 | 13.7705 | 6.5105
|  | MAIDENHEAD BSP | HT |  |  |  |  | 93.8211 | 92.6979 | 91.5063 | 86.7958 | 81.5337 | 77.6442 | 73.8832 | 71.6389 | 69.5253 | 59.5095 | 50.2811 | 42.3389 | 71.5084 | 68.0232 | 62.8084 | 56.2074 | 50.2337 | 45.8821 | 41.6474 | 39.1895 | 36.8695 | 25.7958 | 15.4663 | 6.5347 | 76.6021 | 73.1642 | 68.0274 | 61.5632 | 55.6821 | 51.3253 | 47.0863 | 44.6263 | 42.3021 | 31.2053 | 20.8442 | 11.9
|  | MAIDENHEAD BSP | HE |  |  |  |  | 95.3579 | 94.7042 | 93.9842 | 93.2063 | 89.5516 | 86.1674 | 83.0379 | 81.3663 | 79.8063 | 73.7189 | 68.5811 | 64.0705 | 74.6874 | 72.9621 | 69.1726 | 63.9747 | 59.0821 | 55.2358 | 51.6842 | 49.8411 | 48.1095 | 41.32 | 35.4779 | 30.3032 | 79.0611 | 78.0432 | 74.3158 | 69.2042 | 64.4095 | 60.6716 | 57.1284 | 55.2821 | 53.5516 | 46.7421 | 40.88 | 35.6937
|  | MAIDENHEAD BSP | CF |  |  |  |  | 95.9453 | 95.5947 | 95.2316 | 94.8558 | 94.4621 | 94.06 | 93.6674 | 93.2768 | 92.6579 | 88.0463 | 84.6474 | 81.6074 | 76.1074 | 75.2979 | 74.3421 | 73.0411 | 70.7779 | 67.92 | 65.0084 | 63.7411 | 62.6274 | 57.5347 | 53.6895 | 50.2011 | 79.6968 | 79.32 | 78.9211 | 78.1242 | 75.8968 | 73.0863 | 70.2242 | 68.9726 | 67.8695 | 62.8684 | 59.1242 | 55.6284
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON BSP | MINIMUM HEADROOM | SU 07523 05221 | NO | YES | 0 | 128.0621 | 123.9442 | 119.7674 | 115.2347 | 110.4126 | 105.0842 | 99.7432 | 95.3821 | 86.7832 | 44.22 | 25.3042 | 13.3611 | 96.8305 | 92.1168 | 87.3632 | 82.1705 | 76.6474 | 70.4874 | 64.4074 | 59.5537 | 49.5642 | 0.046316 | -21.6116 | -34.8695 | 102.8505 | 98.1358 | 93.3789 | 88.1832 | 82.6505 | 76.4716 | 70.3737 | 65.5011 | 55.4916 | 5.84 | -16.2611 | -29.5821
|  | MANNINGTON BSP | EE |  |  |  |  | 140.82 | 126.9979 | 123.5537 | 119.7832 | 115.8537 | 111.8211 | 107.8463 | 103.7747 | 99.8726 | 80.6821 | 58.9695 | 46.9463 | 117.4947 | 95.5737 | 91.6442 | 87.3168 | 82.8347 | 78.2105 | 73.6347 | 68.9263 | 64.5705 | 42.8537 | 17.8053 | 3.4453 | 123.0337 | 101.5916 | 97.6611 | 93.3316 | 88.8337 | 84.1884 | 79.5884 | 74.8579 | 70.4726 | 48.5737 | 23.3221 | 8.6
|  | MANNINGTON BSP | HT |  |  |  |  | 128.0621 | 123.9442 | 119.7674 | 115.2347 | 110.4126 | 105.0842 | 99.7432 | 95.3821 | 86.7832 | 44.22 | 25.3042 | 13.3611 | 96.8305 | 92.1168 | 87.3632 | 82.1705 | 76.6474 | 70.4874 | 64.4074 | 59.5537 | 49.5642 | 0.046316 | -21.6116 | -34.8695 | 102.8505 | 98.1358 | 93.3789 | 88.1832 | 82.6505 | 76.4716 | 70.3737 | 65.5011 | 55.4916 | 5.84 | -16.2611 | -29.5821
|  | MANNINGTON BSP | HE |  |  |  |  | 133.4242 | 130.9716 | 128.4368 | 125.4705 | 122.3074 | 119.1011 | 115.9105 | 112.6821 | 109.7705 | 94.7421 | 74.8632 | 67.3895 | 102.9063 | 100.08 | 97.18 | 93.7568 | 90.1284 | 86.4232 | 82.7179 | 78.9432 | 75.5232 | 58.1 | 33.9053 | 25.2495 | 108.9284 | 106.1 | 103.2 | 99.7758 | 96.1337 | 92.4211 | 88.7042 | 84.9168 | 81.4874 | 63.9842 | 39.2863 | 30.5737
|  | MANNINGTON BSP | CF |  |  |  |  | 143.4905 | 134.3853 | 133.0821 | 131.6653 | 130.2095 | 128.6684 | 127.0537 | 125.3432 | 123.5789 | 113.8116 | 107.7326 | 102.7695 | 123.4516 | 103.9968 | 102.4926 | 100.8558 | 99.1779 | 97.4021 | 95.5242 | 93.5179 | 91.4463 | 79.7747 | 72.5695 | 66.8179 | 128.6032 | 110.0179 | 108.5137 | 106.8768 | 105.1947 | 103.4105 | 101.5295 | 99.5189 | 97.4389 | 85.7421 | 78.5042 | 72.7137
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU 47559 12003 | NO | YES | 40.4368 | 146.0358 | 141.3242 | 92.3632 | 86.3147 | 95.0295 | 90.0779 | 85.5621 | 80.4695 | 76.1 | 38.2189 | 13.2432 | -4.0547 | 108.7642 | 103.6789 | 47.3137 | 40.6853 | 52.1474 | 46.8347 | 41.9758 | 36.4032 | 31.6411 | -11.2842 | -39.4232 | -58.82 | 115.0989 | 109.92 | 53.2147 | 46.5853 | 56.42 | 51.0989 | 46.2326 | 40.6516 | 35.8853 | -7.0853 | -35.2789 | -54.6989
|  | NETLEY COMMON BSP | EE |  |  |  |  | 146.0358 | 141.3242 | 128.0211 | 122.7758 | 118.4747 | 113.9863 | 110.1958 | 106.4137 | 102.7116 | 97.5484 | 78.6158 | 62.5347 | 108.7642 | 103.6789 | 88.76 | 82.9947 | 78.3611 | 73.4979 | 69.4337 | 65.3663 | 61.3558 | 57.2937 | 35.9674 | 17.7084 | 115.0989 | 109.92 | 94.6737 | 88.9095 | 84.2695 | 79.3979 | 75.3263 | 71.2516 | 67.2295 | 61.4832 | 40.0905 | 21.8074
|  | NETLEY COMMON BSP | HT |  |  |  |  | 154.4126 | 150.3379 | 92.3632 | 86.3147 | 95.0295 | 90.0779 | 85.5621 | 80.4695 | 76.1 | 38.2189 | 13.2432 | -4.0547 | 120.2832 | 114.2084 | 47.3137 | 40.6853 | 52.1474 | 46.8347 | 41.9758 | 36.4032 | 31.6411 | -11.2842 | -39.4232 | -58.82 | 126.0474 | 120.1326 | 53.2147 | 46.5853 | 56.42 | 51.0989 | 46.2326 | 40.6516 | 35.8853 | -7.0853 | -35.2789 | -54.6989
|  | NETLEY COMMON BSP | HE |  |  |  |  | 149.8284 | 146.3589 | 141.9295 | 137.7663 | 134.4705 | 130.9905 | 128.2305 | 125.4642 | 122.7579 | 123.26 | 108.1737 | 96.1095 | 112.8232 | 109.0747 | 104.2568 | 99.7589 | 96.2705 | 92.56 | 89.6537 | 86.7232 | 83.8284 | 85.9853 | 68.7684 | 54.9179 | 119.0653 | 115.4084 | 110.4895 | 105.9042 | 102.3611 | 98.5874 | 95.6411 | 92.6653 | 89.7253 | 90.2316 | 72.9947 | 59.1211
|  | NETLEY COMMON BSP | CF |  |  |  |  | 159.0695 | 158.2832 | 151.9126 | 150.0105 | 148.4621 | 146.7611 | 145.0137 | 143.2158 | 141.3084 | 131.9253 | 137.7168 | 131.0863 | 130.0958 | 128.0526 | 115.2358 | 113.1874 | 111.5463 | 109.7379 | 107.8705 | 105.9442 | 103.8926 | 93.76 | 101.6989 | 94.2516 | 135.6347 | 133.6463 | 121.3589 | 119.3611 | 117.7537 | 115.9821 | 114.1589 | 112.2737 | 110.1853 | 99.8474 | 106.0968 | 98.5042
MELKSHAM GSP | NORRINGTON BSP | NORRINGTON BSP | MINIMUM HEADROOM | ST 88273 64983 | NO | YES | 145.8 | -27.4537 | -28.9695 | -35.3768 | -121.1916 | -130.2526 | -140.1137 | -149.4495 | -155.6516 | -167.4684 | -248.7084 | -279.2474 | -297.9653 | -78.5979 | -95.8084 | -102.8547 | -203.1137 | -213.1916 | -224.1905 | -234.6368 | -241.4326 | -254.8453 | -348.0453 | -383.5389 | -404.3537 | -69.1832 | -86.5989 | -93.6495 | -193.9411 | -204.0579 | -215.1011 | -225.5958 | -232.44 | -245.9074 | -339.4147 | -376.0484 | -397.0347
|  | NORRINGTON BSP | EE |  |  |  |  | -17.4937 | 36.9379 | 2.9484 | -63.7663 | -77.2379 | -83.9158 | -90.9968 | -98.2695 | -111.7884 | -136.7758 | -184.0958 | -201.7105 | -66.5695 | -18.7674 | -58.2758 | -136.1874 | -151.5189 | -158.8632 | -166.6916 | -174.7547 | -190.1726 | -216.9032 | -270.6126 | -290.4084 | -56.8263 | -9.5337 | -49.06 | -126.9989 | -142.3726 | -149.7747 | -157.6674 | -165.7937 | -181.2905 | -208.1895 | -262.4042 | -282.3768
|  | NORRINGTON BSP | HT |  |  |  |  | -27.4537 | -28.9695 | -35.3768 | -121.1916 | -130.2526 | -140.1137 | -149.4495 | -155.6516 | -167.4684 | -248.7084 | -279.2474 | -297.9653 | -78.5979 | -95.8084 | -102.8547 | -203.1137 | -213.1916 | -224.1905 | -234.6368 | -241.4326 | -254.8453 | -348.0453 | -383.5389 | -404.3537 | -69.1832 | -86.5989 | -93.6495 | -193.9411 | -204.0579 | -215.1011 | -225.5958 | -232.44 | -245.9074 | -339.4147 | -376.0484 | -397.0347
|  | NORRINGTON BSP | HE |  |  |  |  | -0.37263 | 57.52 | 53.3316 | -18.1274 | -79.0937 | -84.6863 | -90.76 | -96.7547 | -101.28 | -144.5737 | -190.6232 | -203.4326 | -42.2421 | 4.94 | 0.30632 | -83.2758 | -154.4716 | -160.6832 | -167.4621 | -174.1842 | -179.1979 | -228.8905 | -284.0642 | -298.5811 | -31.7895 | 14.1853 | 9.5526 | -74.06 | -145.3095 | -151.5442 | -158.3589 | -165.1063 | -170.1537 | -220.06 | -276.3589 | -291.0253
|  | NORRINGTON BSP | CF |  |  |  |  | -5.1821 | 70.6958 | 68.9326 | 50.5379 | 48.3663 | 53.5579 | 51.16 | 48.3032 | 45.0916 | -25.0642 | -34.0474 | -42.5968 | -48.82 | 20.8042 | 18.8095 | -3.7379 | -6.1116 | 0.56526 | -2.0695 | -5.2537 | -8.8558 | -90.4347 | -100.5063 | -110.1989 | -37.5168 | 31.4895 | 29.4568 | 6.4074 | 4.02 | 9.7842 | 7.1347 | 3.9411 | 0.32632 | -81.3484 | -91.4979 | -101.2895
MELKSHAM GSP | NORRINGTON B BSP | NORRINGTON B BSP | MINIMUM HEADROOM | ST 88273 64983 | NO | YES | 0 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | NORRINGTON B BSP | EE | [6 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | NORRINGTON B BSP | HT | [6 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | NORRINGTON B BSP | HE | [6 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | NORRINGTON B BSP | CF | [6 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
NORTH HYDE GSP | NORTH HYDE BSP | NORTH HYDE BSP | MINIMUM HEADROOM | TQ 10367 79001 | NO | NO | 0.015789 | 104.7558 | 104.3958 | 99.76 | 94.2516 | 89.32 | 84.7232 | 81.5242 | 80.6642 | 79.8505 | 76.0537 | 72.2253 | 68.5589 | 94.02 | 90.2326 | 83.6274 | 77.2305 | 71.5063 | 66.1726 | 62.4747 | 61.5263 | 60.6232 | 56.4295 | 52.1095 | 47.9495 | 96.1211 | 92.2737 | 85.5937 | 79.1926 | 73.4747 | 68.1484 | 64.4589 | 63.5105 | 62.6084 | 58.4284 | 54.1158 | 49.9611
|  | NORTH HYDE BSP | EE |  |  |  |  | 104.9611 | 104.6632 | 101.1905 | 96.4316 | 92.3547 | 88.2968 | 85.4853 | 84.7747 | 84.1147 | 81.2032 | 78.5084 | 75.9 | 94.5705 | 91.1642 | 85.2505 | 79.7221 | 74.9968 | 70.2832 | 67.0316 | 66.2547 | 65.5295 | 62.2947 | 59.2968 | 56.3326 | 96.6779 | 93.2179 | 87.2168 | 81.6853 | 76.9589 | 72.2537 | 69.0105 | 68.2326 | 67.5084 | 64.2789 | 61.2916 | 58.3316
|  | NORTH HYDE BSP | HT |  |  |  |  | 104.7558 | 104.3958 | 99.76 | 94.2516 | 89.32 | 84.7232 | 81.5242 | 80.6642 | 79.8505 | 76.0537 | 72.2253 | 68.5589 | 94.02 | 90.2326 | 83.6274 | 77.2305 | 71.5063 | 66.1726 | 62.4747 | 61.5263 | 60.6232 | 56.4295 | 52.1095 | 47.9495 | 96.1211 | 92.2737 | 85.5937 | 79.1926 | 73.4747 | 68.1484 | 64.4589 | 63.5105 | 62.6084 | 58.4284 | 54.1158 | 49.9611
|  | NORTH HYDE BSP | HE |  |  |  |  | 105.1789 | 104.94 | 101.9958 | 97.3747 | 93.4316 | 89.5021 | 86.8221 | 86.2558 | 85.7453 | 83.5937 | 81.5453 | 79.6863 | 95.1253 | 91.8832 | 86.1389 | 80.7621 | 76.1853 | 71.6137 | 68.5074 | 67.8874 | 67.3242 | 64.9274 | 62.5832 | 60.4474 | 97.2389 | 93.9442 | 88.1053 | 82.7263 | 78.1484 | 73.5832 | 70.4821 | 69.8621 | 69.3 | 66.9063 | 64.5611 | 62.4305
|  | NORTH HYDE BSP | CF |  |  |  |  | 105.3505 | 105.2095 | 105.0642 | 104.9126 | 103.8926 | 102.0758 | 100.7147 | 100.3726 | 100.02 | 98.3179 | 97.0074 | 95.8316 | 96.6032 | 95.0284 | 92.4611 | 90.1958 | 88.3168 | 86.2442 | 84.6758 | 84.3 | 83.9158 | 82.0389 | 80.56 | 79.2147 | 98.5884 | 97.14 | 94.5284 | 92.2274 | 90.3179 | 88.2126 | 86.6411 | 86.2653 | 85.8811 | 84.0032 | 82.5242 | 81.1789
COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD (OSNEY) BSP | MINIMUM HEADROOM | SP 50054 05983 | NO | YES | 66.2105 | 35.1261 | -4.4413 | -44.8971 | -47.2971 | 64.9382 | 58.9055 | 55.1866 | 51.4992 | 48.015 | 33.8739 | 22.1287 | 16.1613 | 5.2713 | -43.5582 | -91.0118 | -93.6434 | 13.9639 | 7.0882 | 2.9103 | -1.2455 | -5.1729 | -21.0234 | -34.2108 | -40.8034 | 12.7934 | -36.0529 | -83.5234 | -86.1571 | 23.1555 | 16.2682 | 12.0808 | 7.9113 | 3.9703 | -11.9582 | -25.2445 | -31.8782
|  | OXFORD (OSNEY) BSP | EE |  |  |  |  | 35.6934 | 34.9029 | 33.2734 | 3.6345 | 115.8771 | 112.0045 | 108.7571 | 105.8824 | 103.3645 | 90.5213 | 80.2466 | 75.4508 | 5.2713 | 2.9924 | 1.0524 | -33.8508 | 73.6903 | 69.3018 | 65.6439 | 62.425 | 59.6124 | 45.2008 | 33.6313 | 28.3061 | 12.7934 | 10.5124 | 8.5713 | -26.3455 | 82.985 | 78.5829 | 74.9092 | 71.6734 | 68.8439 | 54.2376 | 42.5261 | 37.1566
|  | OXFORD (OSNEY) BSP | HT |  |  |  |  | 35.1261 | -4.4413 | -44.8971 | -47.2971 | 64.9382 | 58.9055 | 55.1866 | 51.4992 | 48.015 | 33.8739 | 22.1287 | 16.1613 | 6.0629 | -43.5582 | -91.0118 | -93.6434 | 13.9639 | 7.0882 | 2.9103 | -1.2455 | -5.1729 | -21.0234 | -34.2108 | -40.8034 | 13.5829 | -36.0529 | -83.5234 | -86.1571 | 23.1555 | 16.2682 | 12.0808 | 7.9113 | 3.9703 | -11.9582 | -25.2445 | -31.8782
|  | OXFORD (OSNEY) BSP | HE |  |  |  |  | 36.3934 | 35.8187 | 35.1818 | 22.1471 | 96.2287 | 92.6529 | 89.7266 | 87.2739 | 85.1129 | 74.9224 | 66.9539 | 63.8834 | 6.5597 | 4.6797 | 3.1387 | -12.2508 | 50.2345 | 46.1524 | 42.8282 | 40.0587 | 37.6176 | 26.0576 | 16.9503 | 13.5208 | 14.0818 | 12.2008 | 10.6597 | -4.7339 | 59.5271 | 55.4366 | 52.105 | 49.3271 | 46.8797 | 35.1629 | 26.0187 | 22.5524
|  | OXFORD (OSNEY) BSP | CF |  |  |  |  | 36.8745 | 36.5534 | 36.2187 | 35.8745 | 149.8129 | 149.4382 | 149.0655 | 148.6992 | 147.4413 | 137.1718 | 132.5897 | 130.5213 | 11.3334 | 10.6039 | 9.9018 | 9.0776 | 117.9566 | 116.7176 | 115.0724 | 112.9597 | 110.705 | 98.805 | 93.6187 | 91.2934 | 17.2576 | 16.9124 | 16.5576 | 16.185 | 127.2766 | 126.0334 | 124.385 | 122.2671 | 120.0092 | 108.0892 | 102.7945 | 100.4461
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | POOLE (HAMWORTHY) BSP | MINIMUM HEADROOM | SZ 00203 90789 | NO | YES | 0.39368 | 67.7432 | 66.9389 | 64.8232 | 62.6453 | 61.4789 | 59.0032 | 56.3116 | 54.5284 | 53.0295 | 47.2621 | 43.4789 | 39.9011 | 59.1853 | 57.2621 | 54.9221 | 52.5158 | 51.3621 | 48.5947 | 45.5211 | 43.5063 | 41.8221 | 35.3705 | 31.1853 | 27.1747 | 61.5316 | 59.5632 | 57.1642 | 54.6968 | 53.3358 | 50.5242 | 47.4474 | 45.4295 | 43.7411 | 37.2684 | 33.0589 | 29.0389
|  | POOLE (HAMWORTHY) BSP | EE |  |  |  |  | 68.0147 | 67.6337 | 66.4547 | 64.8011 | 62.8295 | 60.8316 | 58.16 | 55.4747 | 55.1611 | 49.4168 | 46.46 | 43.7221 | 59.9011 | 58.3737 | 56.72 | 54.8979 | 52.7158 | 50.5053 | 47.4884 | 44.4063 | 44.1821 | 37.7158 | 34.4568 | 31.3768 | 62.2611 | 60.6979 | 59.0032 | 57.1379 | 54.9 | 52.6305 | 49.5674 | 46.4853 | 46.0979 | 39.6021 | 36.3095 | 33.2189
|  | POOLE (HAMWORTHY) BSP | HT |  |  |  |  | 67.7432 | 66.9389 | 64.8232 | 62.6453 | 61.4789 | 59.0032 | 56.3116 | 54.5284 | 53.0295 | 47.2621 | 43.4789 | 39.9011 | 59.1853 | 57.2621 | 54.9221 | 52.5158 | 51.3621 | 48.5947 | 45.5211 | 43.5063 | 41.8221 | 35.3705 | 31.1853 | 27.1747 | 61.5316 | 59.5632 | 57.1642 | 54.6968 | 53.3358 | 50.5242 | 47.4474 | 45.4295 | 43.7411 | 37.2684 | 33.0589 | 29.0389
|  | POOLE (HAMWORTHY) BSP | HE |  |  |  |  | 68.3389 | 68.0526 | 67.5242 | 66.0432 | 64.2105 | 62.3779 | 59.7853 | 57.3905 | 57.3421 | 52.6674 | 50.6853 | 48.8084 | 60.6442 | 59.3305 | 57.8663 | 56.2263 | 54.1937 | 52.1568 | 49.2432 | 46.4821 | 46.5484 | 41.2358 | 39.0168 | 36.8853 | 62.8947 | 61.6726 | 60.1716 | 58.4895 | 56.4021 | 54.3116 | 51.3263 | 48.5653 | 48.4737 | 43.1474 | 40.92 | 38.78
|  | POOLE (HAMWORTHY) BSP | CF |  |  |  |  | 68.5726 | 68.4126 | 68.2453 | 68.0737 | 67.8926 | 67.7084 | 67.5263 | 67.2158 | 66.1653 | 60.4695 | 58.9242 | 57.6737 | 61.4463 | 60.9021 | 60.4653 | 60.1011 | 59.6968 | 59.2526 | 58.4947 | 57.5726 | 56.4011 | 50.1147 | 48.3768 | 46.9579 | 63.1621 | 62.9789 | 62.7958 | 62.4663 | 62.0547 | 61.6011 | 60.8253 | 59.8779 | 58.6747 | 52.0421 | 50.2989 | 48.8747
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ 63405 99685 | NO | YES | 5.2 | 127.5863 | 125.4726 | 123.2295 | 210.8653 | 217.4747 | 216.5084 | 211.2968 | 205.06 | 200.1684 | 177.2053 | 156.9579 | 138.2937 | 88.7674 | 83.4758 | 77.0905 | 158.8116 | 166.8821 | 159.4126 | 152.2495 | 145.2779 | 139.8632 | 114.2926 | 91.6179 | 70.5747 | 97.9632 | 93.1137 | 86.7821 | 168.5158 | 176.5958 | 169.1337 | 161.9716 | 155.0063 | 149.5937 | 124.0253 | 101.3505 | 80.3253
|  | PORTSMOUTH BSP | EE |  |  |  |  | 128.8211 | 127.0737 | 125.2211 | 213.2411 | 228.0063 | 225.9853 | 220.2716 | 214.3032 | 208.7863 | 190.02 | 174.1274 | 159.7589 | 91.8705 | 87.5516 | 82.0895 | 166.1463 | 175.1263 | 168.6663 | 162.1905 | 155.5137 | 149.3305 | 128.4484 | 110.6316 | 94.3589 | 99.3126 | 97.0053 | 91.7737 | 175.84 | 184.8274 | 178.3716 | 171.9 | 165.2242 | 159.0442 | 138.1474 | 120.3084 | 104.0432
|  | PORTSMOUTH BSP | HT |  |  |  |  | 127.5863 | 125.4726 | 123.2295 | 210.8653 | 224.4516 | 217.7263 | 211.2968 | 205.06 | 200.1684 | 177.2053 | 156.9579 | 138.2937 | 88.7674 | 83.4758 | 77.0905 | 158.8116 | 166.8821 | 159.4126 | 152.2495 | 145.2779 | 139.8632 | 114.2926 | 91.6179 | 70.5747 | 97.9632 | 93.1137 | 86.7821 | 168.5158 | 176.5958 | 169.1337 | 161.9716 | 155.0063 | 149.5937 | 124.0253 | 101.3505 | 80.3253
|  | PORTSMOUTH BSP | HE |  |  |  |  | 130.0937 | 128.7053 | 127.1674 | 215.5168 | 230.5916 | 228.8979 | 227.3053 | 225.8147 | 222.8253 | 208.22 | 196.4632 | 186.5674 | 93.8326 | 91.7884 | 87.5 | 172.6221 | 183.3863 | 178.7337 | 174.0611 | 169.2842 | 165.1042 | 148.7326 | 135.1916 | 123.88 | 100.6989 | 99.1989 | 96.9642 | 182.3105 | 193.0768 | 188.4274 | 183.7611 | 178.9884 | 174.8116 | 158.4442 | 144.8674 | 133.5579
|  | PORTSMOUTH BSP | CF |  |  |  |  | 131.0484 | 130.2032 | 129.3221 | 218.4168 | 217.4747 | 216.5084 | 215.5621 | 214.6242 | 213.6905 | 226.3579 | 219.4663 | 212.8874 | 95.06 | 93.9737 | 92.64 | 180.6737 | 178.2126 | 175.8053 | 173.2684 | 170.5958 | 167.6379 | 170.4 | 161.2168 | 153.6926 | 101.7189 | 100.8158 | 99.8484 | 188.8579 | 187.6453 | 185.3432 | 182.9242 | 180.2811 | 177.3232 | 180.1021 | 170.9211 | 163.4053
FLEET-BRAMLEY GSP | PYESTOCK BSP | PYESTOCK BSP | MINIMUM HEADROOM | SU 82940 54553 | YES | YES | 0 | 96.8495 | 96.4821 | 96.0895 | 95.6863 | 95.2726 | 94.5179 | 93.8147 | 93.1295 | 92.4621 | 89.6232 | 86.6432 | 83.9526 | 90.5653 | 89.8274 | 89.0147 | 88.1653 | 87.2926 | 86.4 | 85.6147 | 84.8653 | 84.1484 | 81.0821 | 77.8084 | 74.8347 | 92.2421 | 91.4926 | 90.6663 | 89.8032 | 88.9158 | 88.0074 | 87.2084 | 86.4463 | 85.7147 | 82.5853 | 79.2326 | 76.1832
|  | PYESTOCK BSP | EE |  |  |  |  | 97.0863 | 96.7905 | 96.4737 | 96.1463 | 95.8063 | 95.48 | 95.1558 | 94.5842 | 94.0537 | 91.8863 | 89.5558 | 87.4768 | 91.0495 | 90.4547 | 89.8095 | 89.1284 | 88.4389 | 87.7432 | 87.1158 | 86.4811 | 85.8853 | 83.5253 | 80.9621 | 78.6537 | 92.5832 | 92.1295 | 91.4747 | 90.7832 | 90.0811 | 89.3726 | 88.7347 | 88.0884 | 87.4821 | 85.0695 | 82.4389 | 80.0695
|  | PYESTOCK BSP | HT |  |  |  |  | 96.8495 | 96.4821 | 96.0895 | 95.6863 | 95.2726 | 94.5179 | 93.8147 | 93.1295 | 92.4621 | 89.6232 | 86.6432 | 83.9526 | 90.5653 | 89.8274 | 89.0147 | 88.1653 | 87.2926 | 86.4 | 85.6147 | 84.8653 | 84.1484 | 81.0821 | 77.8084 | 74.8347 | 92.2421 | 91.4926 | 90.6663 | 89.8032 | 88.9158 | 88.0074 | 87.2084 | 86.4463 | 85.7147 | 82.5853 | 79.2326 | 76.1832
|  | PYESTOCK BSP | HE |  |  |  |  | 97.38 | 97.1758 | 96.9495 | 96.7074 | 96.4463 | 96.1968 | 95.9611 | 95.7411 | 95.5526 | 94.3884 | 92.7179 | 91.2084 | 91.6737 | 91.2716 | 90.8137 | 90.3095 | 89.7811 | 89.2442 | 88.7726 | 88.2926 | 87.8516 | 86.2263 | 84.3453 | 82.6526 | 92.8958 | 92.6811 | 92.44 | 91.9821 | 91.4463 | 90.9011 | 90.42 | 89.9326 | 89.4832 | 87.8242 | 85.8916 | 84.1495
|  | PYESTOCK BSP | CF |  |  |  |  | 97.5747 | 97.4695 | 97.3589 | 97.2463 | 97.1274 | 97.0084 | 96.8895 | 96.7726 | 96.6547 | 96.1326 | 95.5674 | 94.6147 | 92.0779 | 91.8474 | 91.6032 | 91.3474 | 91.0789 | 90.7947 | 90.5316 | 90.2495 | 89.9621 | 88.7326 | 87.46 | 86.3421 | 93.1042 | 92.9916 | 92.8726 | 92.7516 | 92.6232 | 92.4737 | 92.2063 | 91.92 | 91.6242 | 90.3726 | 89.0674 | 87.9158
BRAMLEY (BASI) GSP | READING BSP | READING BSP | MINIMUM HEADROOM | SU 74642 73856 | NO | YES | 54.5263 | 169.4968 | 166.9611 | 160.5211 | 140.0842 | 134.4768 | 128.5032 | 121.78 | 115.3011 | 109.7242 | 85.6432 | 65.3316 | 47.7232 | 126.6147 | 121.0842 | 102.5347 | 78.8389 | 72.6621 | 66.0368 | 58.5295 | 51.3063 | 45.1 | 18.2853 | -4.6168 | -24.6558 | 136.5189 | 131.0958 | 112.6242 | 88.92 | 82.7347 | 76.0989 | 68.5768 | 61.3421 | 55.1221 | 28.2989 | 5.3032 | -14.7716
|  | READING BSP | EE |  |  |  |  | 171.0347 | 168.9705 | 160.5211 | 140.0842 | 134.4768 | 128.5032 | 121.78 | 115.3011 | 109.7242 | 85.6432 | 65.3316 | 47.7232 | 129.9505 | 125.64 | 102.5347 | 78.8389 | 72.6621 | 66.0368 | 58.5295 | 51.3063 | 45.1 | 18.2853 | -4.6168 | -24.6558 | 139.8516 | 135.5579 | 112.6242 | 88.92 | 82.7347 | 76.0989 | 68.5768 | 61.3421 | 55.1221 | 28.2989 | 5.3032 | -14.7716
|  | READING BSP | HT |  |  |  |  | 169.4968 | 166.9611 | 164.2705 | 161.4895 | 156.4958 | 149.0579 | 141.0747 | 134.5042 | 128.2884 | 95.9684 | 70.9484 | 48.9547 | 126.6147 | 121.0842 | 114.28 | 107.1758 | 99.3411 | 91.0063 | 82.0537 | 74.7305 | 67.7947 | 31.3716 | 3.08 | -21.8158 | 136.5189 | 131.0958 | 124.38 | 117.2716 | 109.4284 | 101.0895 | 92.1274 | 84.7958 | 77.8453 | 41.3653 | 12.9379 | -11.9895
|  | READING BSP | HE |  |  |  |  | 172.9642 | 171.4905 | 169.8547 | 168.1 | 166.2116 | 164.4063 | 161.9558 | 156.7558 | 152.2653 | 132.4747 | 116.9537 | 103.6326 | 133.6326 | 130.9347 | 126.4758 | 122.1789 | 117.3516 | 111.8137 | 105.1474 | 99.1516 | 94.0737 | 71.4642 | 53.6832 | 38.3663 | 141.9526 | 140.4011 | 136.3979 | 132.1916 | 127.4463 | 121.9032 | 115.2347 | 109.2305 | 104.1474 | 81.4232 | 63.6105 | 48.2642
|  | READING BSP | CF |  |  |  |  | 174.2832 | 173.4916 | 172.6663 | 171.8158 | 170.9232 | 170.0147 | 169.1274 | 168.2432 | 167.3621 | 160.0842 | 147.3779 | 137.5653 | 136.8137 | 135.9474 | 132.6463 | 130.4789 | 128.3632 | 126.1579 | 123.9053 | 121.4537 | 118.9695 | 102.6884 | 88.0105 | 76.6516 | 143.4568 | 142.6295 | 141.6116 | 140.3674 | 138.2547 | 136.0947 | 133.8863 | 131.4947 | 129.0611 | 112.7653 | 98.0726 | 86.6968
FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN BSP | MINIMUM HEADROOM | SU 71580 74111 | NO | YES | 0 | 107.4895 | 106.6884 | 105.7653 | 103.8221 | 98.9758 | 93.4768 | 88.2926 | 82.1758 | 75.9326 | 66.0389 | 60.6547 | 55.5663 | 90.3389 | 88.6474 | 86.0484 | 82.2747 | 76.7042 | 70.3853 | 64.4253 | 57.3526 | 50.1221 | 38.9632 | 32.9989 | 27.3084 | 94.8874 | 93.1947 | 90.5968 | 86.8274 | 81.2632 | 74.9537 | 69.0011 | 61.9368 | 54.7179 | 43.5674 | 37.6 | 31.9095
|  | READING TOWN BSP | EE |  |  |  |  | 107.9463 | 107.3305 | 106.5653 | 105.5126 | 101.3295 | 96.9074 | 92.2989 | 85.8789 | 79.3821 | 70.0042 | 65.9242 | 62.0842 | 91.3211 | 89.9295 | 87.6189 | 84.1284 | 79.3168 | 74.2305 | 68.9316 | 61.4937 | 53.9526 | 43.3168 | 38.8042 | 34.5063 | 95.4726 | 94.46 | 92.1495 | 88.66 | 83.8516 | 78.7684 | 73.4705 | 66.0432 | 58.5126 | 47.8653 | 43.3326 | 39.0158
|  | READING TOWN BSP | HT |  |  |  |  | 107.4895 | 106.6884 | 105.7653 | 103.8221 | 98.9758 | 93.4768 | 88.2926 | 82.1758 | 75.9326 | 66.0389 | 60.6547 | 55.5663 | 90.3389 | 88.6474 | 86.0484 | 82.2747 | 76.7042 | 70.3853 | 64.4253 | 57.3526 | 50.1221 | 38.9632 | 32.9989 | 27.3084 | 94.8874 | 93.1947 | 90.5968 | 86.8274 | 81.2632 | 74.9537 | 69.0011 | 61.9368 | 54.7179 | 43.5674 | 37.6 | 31.9095
|  | READING TOWN BSP | HE |  |  |  |  | 108.4663 | 108.0084 | 107.4642 | 106.7358 | 103.6716 | 99.5074 | 95.0463 | 88.9263 | 82.8305 | 75.0895 | 72.4568 | 70.0347 | 92.4968 | 91.5116 | 89.5442 | 86.3916 | 81.86 | 77.0421 | 71.8863 | 64.7705 | 57.6737 | 48.8189 | 45.8811 | 43.1295 | 96.0379 | 95.5505 | 94.0968 | 90.9484 | 86.4221 | 81.6126 | 76.4663 | 69.3621 | 62.2789 | 53.4368 | 50.4968 | 47.7474
|  | READING TOWN BSP | CF |  |  |  |  | 108.8211 | 108.5568 | 108.2821 | 107.9979 | 107.6379 | 107.2463 | 106.8411 | 104.7937 | 102.4411 | 92.2579 | 90.2737 | 88.5653 | 94.1263 | 93.6158 | 92.5221 | 91.0042 | 89.36 | 87.7484 | 85.8895 | 83.1042 | 80.3758 | 68.6179 | 66.3968 | 64.4495 | 96.4726 | 96.1895 | 95.8674 | 95.5116 | 93.9137 | 92.3053 | 90.4484 | 87.6684 | 84.9442 | 73.2053 | 70.9884 | 69.0442
MANNINGTON GSP | REDHILL BSP | REDHILL BSP | MINIMUM HEADROOM | SZ 08581 96162 | NO | YES | 105.3274 | -3.86 | -38.0547 | -45.2474 | -47.8316 | -50.3926 | -52.9737 | -55.2011 | -57.3463 | -87.98 | -103.8958 | -115.0579 | -125.2253 | -26.6168 | -66.2853 | -74.7063 | -77.5032 | -80.2632 | -83.0526 | -85.4432 | -87.74 | -123.0274 | -140.8158 | -153.24 | -164.6547 | -22.6042 | -62.5032 | -70.9242 | -73.7232 | -76.4842 | -79.2789 | -81.6716 | -83.9726 | -119.2716 | -137.0768 | -149.5221 | -160.9463
|  | REDHILL BSP | EE |  |  |  |  | -2.0811 | -8.1053 | -45.2474 | -47.8316 | -50.3926 | -52.9737 | -55.2011 | -57.3463 | -62.8063 | -86.9368 | -95.5905 | -103.3137 | -24.7 | -31.4674 | -74.7063 | -77.5032 | -80.2632 | -83.0526 | -85.4432 | -87.74 | -93.9568 | -121.56 | -131.2147 | -139.9305 | -20.6695 | -27.5326 | -70.9242 | -73.7232 | -76.4842 | -79.2789 | -81.6716 | -83.9726 | -90.1926 | -117.8263 | -127.5084 | -136.2326
|  | REDHILL BSP | HT |  |  |  |  | -3.86 | -38.0547 | -41.2242 | -44.3126 | -47.4168 | -50.6221 | -53.4589 | -56.3484 | -87.98 | -103.8958 | -115.0579 | -125.2253 | -26.6168 | -66.2853 | -69.7305 | -73.0737 | -76.4221 | -79.8884 | -82.9568 | -86.1126 | -123.0274 | -140.8158 | -153.24 | -164.6547 | -22.6042 | -62.5032 | -65.9495 | -69.2916 | -72.6421 | -76.1105 | -79.1832 | -82.3411 | -119.2716 | -137.0768 | -149.5221 | -160.9463
|  | REDHILL BSP | HE |  |  |  |  | 0.27263 | -1.6326 | -34.5874 | -36.5084 | -38.4558 | -40.4316 | -42.0263 | -43.6137 | -45.3242 | -69.78 | -75.78 | -81.0505 | -22.1621 | -24.2284 | -62.5158 | -64.5905 | -66.6853 | -68.82 | -70.5189 | -72.2179 | -74.0863 | -102.32 | -109.08 | -115.0947 | -18.1074 | -20.1947 | -58.7316 | -60.8074 | -62.9032 | -65.04 | -66.7389 | -68.4421 | -70.3116 | -98.5611 | -105.3316 | -111.3516
|  | REDHILL BSP | CF |  |  |  |  | 1.7316 | 0.91579 | -1.0053 | -33.02 | -34.0968 | -35.2632 | -36.3316 | -37.3126 | -38.2516 | -42.2642 | -46.3526 | -49.8611 | -12.7737 | -21.4789 | -24.1811 | -61.2421 | -62.4211 | -63.7011 | -64.8684 | -65.9326 | -66.9463 | -71.2737 | -75.8768 | -79.8832 | -9.1242 | -17.4179 | -20.1263 | -57.6421 | -58.82 | -60.1021 | -61.2695 | -62.3347 | -63.3505 | -67.68 | -72.2895 | -76.3
NURSLING GSP | ROWNHAMS BSP | ROWNHAMS BSP | MINIMUM HEADROOM | SU 37168 16854 | NO | YES | 57.8421 | 43.3053 | 39.3242 | -72.9358 | 12.1863 | -27.7663 | -37.4853 | -42.0326 | -46.7232 | -38.3189 | -60.6516 | -79.4547 | -91.2326 | -0.95789 | -5.3063 | -137.3337 | -52.6937 | -99.6305 | -110.6989 | -115.7084 | -120.8947 | -113.3084 | -139.0179 | -161.3821 | -174.6347 | 5.6916 | 1.3463 | -130.7263 | -46.0853 | -93.0526 | -104.1474 | -109.1779 | -114.3916 | -106.9516 | -133.4221 | -156.6484 | -169.9674
|  | ROWNHAMS BSP | EE |  |  |  |  | 54.7568 | 42.3221 | -14.1105 | 53.6653 | -27.7663 | -37.4853 | -42.0326 | -46.7232 | -38.3189 | -60.6516 | -79.4547 | -91.2326 | 12.3463 | -2.0326 | -68.3032 | -4.2 | -99.6305 | -110.6989 | -115.7084 | -120.8947 | -113.3084 | -139.0179 | -161.3821 | -174.6347 | 19.0032 | 4.62 | -61.6726 | 2.42 | -93.0526 | -104.1474 | -109.1779 | -114.3916 | -106.9516 | -133.4221 | -156.6484 | -169.9674
|  | ROWNHAMS BSP | HT |  |  |  |  | 43.3053 | 39.3242 | -72.9358 | 12.1863 | 8.2189 | 1.7589 | -3.7232 | -8.4411 | -1.5653 | -27.6316 | -45.1789 | -59.5084 | -0.95789 | -5.3063 | -137.3337 | -52.6937 | -56.8684 | -64.2779 | -70.3516 | -75.5547 | -70.2937 | -100.7916 | -120.2811 | -136.3147 | 5.6916 | 1.3463 | -130.7263 | -46.0853 | -50.4505 | -57.9958 | -64.0853 | -69.3074 | -64.4768 | -95.7621 | -115.3989 | -131.4937
|  | ROWNHAMS BSP | HE |  |  |  |  | 57.4684 | 45.9358 | 30.5158 | 117.6589 | 6.2947 | -2.5663 | -6.2274 | -10.5842 | -0.65789 | -19.7116 | -35.8516 | -44.2716 | 15.2853 | 1.8821 | -16.08 | 70.7926 | -60.2032 | -70.3474 | -74.4021 | -79.5179 | -70.0074 | -92.7316 | -113.1063 | -122.6811 | 21.9432 | 8.5358 | -9.4337 | 77.44 | -53.6105 | -63.7674 | -67.8337 | -73.0811 | -63.5842 | -87.1705 | -108.5905 | -118.2221
|  | ROWNHAMS BSP | CF |  |  |  |  | 64.7484 | 64.1263 | 41.3274 | 129.9832 | 128.4632 | 49.6032 | 47.8063 | 45.6274 | 43.3432 | 8.3695 | 15.8495 | 10.1347 | 37.6905 | 34.0095 | -3.7095 | 84.8253 | 83.1653 | -9.7379 | -11.72 | -14.16 | -16.7284 | -57.3074 | -50.4684 | -56.9642 | 42.4389 | 40.6737 | 2.9432 | 91.4758 | 89.8105 | -3.1284 | -5.1168 | -7.5611 | -10.1337 | -50.7526 | -44.1147 | -50.6453
MANNINGTON GSP | SALISBURY BSP | SALISBURY BSP | MINIMUM HEADROOM | SU 11049 31395 | NO | YES | 71.1053 | 56.5189 | 55.0758 | 42.1789 | 26.8053 | 22.9547 | 19.2147 | 15.3126 | 11.3463 | 8.3926 | -0.24 | -12.2168 | -22.2032 | 32.8916 | 30.0695 | 12.1579 | -5.6895 | -9.9316 | -14.0221 | -18.3116 | -22.6747 | -25.86 | -34.3695 | -47.24 | -58.4011 | 39.8937 | 37.0589 | 18.8653 | 1.0421 | -3.2242 | -7.3621 | -11.6937 | -16.1074 | -19.3537 | -28.8147 | -42.1179 | -53.4168
|  | SALISBURY BSP | EE |  |  |  |  | 57.3726 | 56.1832 | 42.1789 | 26.8053 | 22.9547 | 19.2147 | 15.3126 | 11.3463 | 8.3926 | -0.24 | -12.2168 | -22.2032 | 34.7632 | 32.4189 | 12.1579 | -5.6895 | -9.9316 | -14.0221 | -18.3116 | -22.6747 | -25.86 | -34.3695 | -47.24 | -58.4011 | 41.72 | 39.4253 | 18.8653 | 1.0421 | -3.2242 | -7.3621 | -11.6937 | -16.1074 | -19.3537 | -28.8147 | -42.1179 | -53.4168
|  | SALISBURY BSP | HT |  |  |  |  | 56.5189 | 55.0758 | 53.5474 | 50.3179 | 49.6105 | 44.4421 | 39.1453 | 33.0684 | 30.3842 | 12.1411 | -1.8621 | -13.1084 | 32.8916 | 30.0695 | 26.8368 | 22.1411 | 21.9305 | 16.2937 | 10.3684 | 3.5158 | 0.64526 | -19.4537 | -34.7547 | -47.2463 | 39.8937 | 37.0589 | 33.7716 | 28.9758 | 28.2 | 22.4179 | 16.4463 | 9.5547 | 6.6432 | -13.7389 | -29.34 | -41.9611
|  | SALISBURY BSP | HE |  |  |  |  | 58.4726 | 57.6337 | 45.7242 | 30.9642 | 27.7179 | 24.6337 | 21.4758 | 18.4579 | 16.3863 | 10.7842 | 2.7937 | -4.76 | 37.1063 | 35.5032 | 16.0053 | -1.1842 | -4.7737 | -8.1811 | -11.6916 | -15.0389 | -17.2979 | -22.8463 | -31.7484 | -40.2674 | 43.2189 | 42.38 | 22.7126 | 5.5547 | 1.9442 | -1.4821 | -5.0105 | -8.38 | -10.6632 | -16.9442 | -25.9758 | -34.6042
|  | SALISBURY BSP | CF |  |  |  |  | 59.2379 | 58.7968 | 58.3347 | 57.8537 | 57.3211 | 56.7789 | 56.2421 | 55.7158 | 55.1958 | 48.0874 | 47.5316 | 42.5716 | 38.7411 | 37.9011 | 37.0284 | 35.7495 | 34.3358 | 32.7989 | 31.2389 | 29.6874 | 28.2589 | 19.5411 | 19.4779 | 13.8947 | 43.9842 | 43.5432 | 43.0811 | 42.6 | 41.3011 | 39.7979 | 38.2032 | 36.6105 | 35.1505 | 26.1863 | 25.5242 | 19.8305
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST 85442 23791 | NO | YES | 96.7379 | -0.27158 | -3.5316 | -6.8916 | -11.2853 | -21.7642 | -24.7989 | -27.6095 | -30.0842 | -36.8642 | -52.6 | -62.42 | -69.4989 | -20.4 | -23.9337 | -27.5726 | -32.4316 | -44.7568 | -48.0926 | -51.1726 | -53.8642 | -61.2432 | -78.7547 | -89.5274 | -97.3274 | -17.1242 | -20.7316 | -24.4484 | -29.3674 | -41.7147 | -45.0674 | -48.1705 | -50.8832 | -58.3032 | -75.9568 | -86.8611 | -94.7168
|  | SHAFTESBURY BSP | EE |  |  |  |  | 1.2221 | -1.5832 | -4.4842 | -8.4389 | -21.7642 | -24.7989 | -27.6095 | -30.0842 | -32.3958 | -43.9126 | -53.4168 | -60.2768 | -18.8032 | -21.8421 | -24.9958 | -29.3432 | -44.7568 | -48.0926 | -51.1726 | -53.8642 | -56.3768 | -68.9937 | -79.4642 | -87.1389 | -15.5011 | -18.6105 | -21.8295 | -26.2779 | -41.7147 | -45.0674 | -48.1705 | -50.8832 | -53.42 | -66.2716 | -76.9242 | -84.6589
|  | SHAFTESBURY BSP | HT |  |  |  |  | -0.27158 | -3.5316 | -6.8916 | -11.2853 | -15.3358 | -18.8274 | -22.2821 | -27.2021 | -36.8642 | -52.6 | -62.42 | -69.4989 | -20.4 | -23.9337 | -27.5726 | -32.4316 | -36.9084 | -40.7326 | -44.5547 | -50.1063 | -61.2432 | -78.7547 | -89.5274 | -97.3274 | -17.1242 | -20.7316 | -24.4484 | -29.3674 | -33.8989 | -37.74 | -41.5779 | -47.1442 | -58.3032 | -75.9568 | -86.8611 | -94.7168
|  | SHAFTESBURY BSP | HE |  |  |  |  | 3.22 | 1.0495 | -1.2905 | -4.6842 | -8.1684 | -10.66 | -12.9347 | -14.8526 | -16.6274 | -25.8958 | -32.8021 | -37.7874 | -16.6653 | -19.0326 | -21.5926 | -25.3379 | -29.1853 | -31.9411 | -34.4547 | -36.56 | -38.5095 | -48.8547 | -56.6558 | -62.2979 | -13.3274 | -15.7474 | -18.3611 | -22.2 | -26.1232 | -28.8905 | -31.4158 | -33.5284 | -35.4874 | -45.9568 | -53.8116 | -59.5
|  | SHAFTESBURY BSP | CF |  |  |  |  | 12.8653 | 11.7842 | 10.6611 | 9.0505 | 7.3853 | 6.0611 | 4.8074 | 3.6526 | 2.4621 | -10.4337 | -13.0905 | -16.5242 | -5.78 | -6.96 | -8.1832 | -9.9642 | -11.7916 | -13.2337 | -14.6032 | -15.8547 | -17.1505 | -31.6032 | -34.4989 | -38.3895 | -2.4926 | -3.5053 | -4.5737 | -6.3968 | -8.2747 | -9.7537 | -11.1558 | -12.4358 | -13.7621 | -28.5768 | -31.5411 | -35.4684
IVER 132KV GSP | SLOUGH BSP | SLOUGH BSP | MINIMUM HEADROOM | SU 95574 81752 | NO | YES | 0 | 108.9558 | 108.0442 | 107.0779 | 196.0789 | 195.0368 | 193.9895 | 193.0884 | 192.2463 | 191.4663 | 185.3337 | 178.8589 | 173.06 | 104.5284 | 103.32 | 101.4853 | 189.7232 | 187.9684 | 186.2263 | 184.4368 | 182.6305 | 180.8989 | 172.8263 | 165.7547 | 159.3674 | 104.6442 | 103.7326 | 102.7137 | 190.9937 | 189.2768 | 187.5726 | 185.8074 | 183.9811 | 182.2305 | 174.0484 | 166.8716 | 160.3937
|  | SLOUGH BSP | EE |  |  |  |  | 109.4842 | 108.7326 | 107.9316 | 197.0958 | 196.22 | 195.3705 | 194.5632 | 193.7842 | 193.1084 | 190.2305 | 185.2232 | 180.8653 | 105.0568 | 104.3063 | 103.3358 | 191.9 | 190.4611 | 189.0779 | 187.5442 | 185.9895 | 184.6021 | 178.1442 | 172.6832 | 167.8663 | 105.1726 | 104.4211 | 103.62 | 192.7842 | 191.6947 | 190.3389 | 188.8432 | 187.3295 | 185.9632 | 179.4074 | 173.8453 | 168.9537
|  | SLOUGH BSP | HT |  |  |  |  | 108.9558 | 108.0442 | 107.0779 | 196.0789 | 195.0368 | 193.9895 | 193.0884 | 192.2463 | 191.4663 | 185.3337 | 178.8589 | 173.06 | 104.5284 | 103.32 | 101.4853 | 189.7232 | 187.9684 | 186.2263 | 184.4368 | 182.6305 | 180.8989 | 172.8263 | 165.7547 | 159.3674 | 104.6442 | 103.7326 | 102.7137 | 190.9937 | 189.2768 | 187.5726 | 185.8074 | 183.9811 | 182.2305 | 174.0484 | 166.8716 | 160.3937
|  | SLOUGH BSP | HE |  |  |  |  | 110.1621 | 109.6168 | 109.0147 | 198.3642 | 197.6684 | 197.0021 | 196.3726 | 195.7842 | 195.2758 | 193.5189 | 192.4895 | 190.4432 | 105.7347 | 105.1895 | 104.5874 | 193.9368 | 193.2432 | 192.58 | 191.5979 | 190.4432 | 189.38 | 184.8042 | 181.2053 | 178.1221 | 105.8505 | 105.3053 | 104.7032 | 194.0526 | 193.3568 | 192.6905 | 192.0621 | 191.4737 | 190.6158 | 186.1621 | 182.5074 | 179.3716
|  | SLOUGH BSP | CF |  |  |  |  | 110.6463 | 110.3526 | 110.0474 | 199.7316 | 199.4011 | 199.0653 | 198.7358 | 198.4084 | 198.0832 | 196.6232 | 195.8821 | 195.4663 | 106.2189 | 105.9253 | 105.62 | 195.3042 | 194.9758 | 194.64 | 194.3116 | 193.9863 | 193.6621 | 190.2621 | 187.6547 | 185.4863 | 106.3347 | 106.0411 | 105.7358 | 195.42 | 195.0895 | 194.7537 | 194.4242 | 194.0979 | 193.7726 | 191.5253 | 189.0189 | 186.8221
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | SOUTHAMPTON (RESERVE) BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | YES | 3.7905 | 71.2442 | 70.9411 | 70.6189 | 70.2737 | 66.7695 | 61.0095 | 58.7726 | 57.1032 | 55.6274 | 51.7147 | 48.3874 | 45.2663 | 57.7326 | 57.0042 | 56.0874 | 54.6674 | 49.9684 | 42.1832 | 39.6411 | 37.7537 | 36.1179 | 31.7789 | 28.0779 | 24.5368 | 61.3053 | 60.5705 | 59.6432 | 58.2053 | 53.4295 | 45.5895 | 43.0105 | 41.0937 | 39.4337 | 35.04 | 31.2905 | 27.7537
|  | SOUTHAMPTON (RESERVE) BSP | EE |  |  |  |  | 71.4611 | 71.2242 | 70.9737 | 70.7011 | 70.4126 | 69.7989 | 65.9147 | 62.3484 | 58.1537 | 53.9832 | 51.3758 | 48.9653 | 58.1484 | 57.5474 | 56.7989 | 55.5579 | 54.5663 | 53.5484 | 48.9863 | 44.8632 | 38.9053 | 34.2505 | 31.34 | 28.6316 | 61.7253 | 61.1179 | 60.3611 | 59.1032 | 58.0989 | 57.0684 | 52.4316 | 48.2737 | 42.2568 | 37.5379 | 34.5884 | 31.8442
|  | SOUTHAMPTON (RESERVE) BSP | HT |  |  |  |  | 71.2442 | 70.9411 | 70.6189 | 70.2737 | 66.7695 | 61.0095 | 58.7726 | 57.1032 | 55.6274 | 51.7147 | 48.3874 | 45.2663 | 57.7326 | 57.0042 | 56.0874 | 54.6674 | 49.9684 | 42.1832 | 39.6411 | 37.7537 | 36.1179 | 31.7789 | 28.0779 | 24.5368 | 61.3053 | 60.5705 | 59.6432 | 58.2053 | 53.4295 | 45.5895 | 43.0105 | 41.0937 | 39.4337 | 35.04 | 31.2905 | 27.7537
|  | SOUTHAMPTON (RESERVE) BSP | HE |  |  |  |  | 71.5842 | 71.3768 | 71.1484 | 70.9 | 70.6379 | 67.82 | 65.9011 | 63.2221 | 61.1768 | 56.4147 | 54.2432 | 52.5337 | 58.5358 | 58.0505 | 57.4084 | 56.2716 | 55.3821 | 50.9274 | 47.8084 | 44.6884 | 42.3453 | 36.9011 | 34.4526 | 32.5179 | 62.1179 | 61.6274 | 60.9789 | 59.8253 | 58.9253 | 54.4737 | 51.3021 | 48.1316 | 45.7516 | 40.2253 | 37.7421 | 35.7768
|  | SOUTHAMPTON (RESERVE) BSP | CF |  |  |  |  | 71.6958 | 71.5589 | 71.4168 | 71.2705 | 71.1179 | 70.9632 | 70.8105 | 70.66 | 68.9726 | 65.1305 | 65.5147 | 64.3684 | 59.3905 | 59.1747 | 58.8884 | 58.4305 | 57.7495 | 57.0832 | 56.4821 | 54.6221 | 52.4326 | 48.08 | 49.3537 | 48.0442 | 62.5253 | 62.38 | 62.2284 | 62.0168 | 61.3253 | 60.6505 | 60.0421 | 58.1516 | 55.9284 | 51.5095 | 53.1684 | 51.8579
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | SOUTHAMPTON (MAIN) BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | YES | 0.26316 | 115.3968 | 114.5484 | 113.6463 | 111.7074 | 108.2695 | 105.0663 | 102.2821 | 99.5632 | 97.4021 | 88.3305 | 80.6632 | 73.5989 | 93.0789 | 91.0853 | 88.3442 | 85.6705 | 81.84 | 78.2842 | 75.1947 | 72.1684 | 69.7821 | 59.6874 | 51.0726 | 43.0895 | 98.12 | 96.0821 | 93.3768 | 90.6789 | 86.7979 | 83.1979 | 80.0695 | 77.0032 | 74.5884 | 64.4895 | 55.8737 | 47.8874
|  | SOUTHAMPTON (MAIN) BSP | EE |  |  |  |  | 115.9147 | 115.2242 | 114.4874 | 113.7063 | 111.3863 | 108.9442 | 105.8663 | 103.0568 | 101.3874 | 93.7116 | 87.7558 | 82.3705 | 93.9558 | 92.4874 | 90.1926 | 87.9389 | 85.2674 | 82.56 | 79.1126 | 75.9695 | 74.1421 | 65.6179 | 58.9105 | 52.7958 | 98.8063 | 97.5 | 95.2063 | 92.9705 | 90.2663 | 87.5253 | 84.0305 | 80.8463 | 78.9968 | 70.4168 | 63.7126 | 57.5958
|  | SOUTHAMPTON (MAIN) BSP | HT |  |  |  |  | 115.3968 | 114.5484 | 113.6463 | 111.7074 | 108.2695 | 105.0663 | 102.2821 | 99.5632 | 97.4021 | 88.3305 | 80.6632 | 73.5989 | 93.0789 | 91.0853 | 88.3442 | 85.6705 | 81.84 | 78.2842 | 75.1947 | 72.1684 | 69.7821 | 59.6874 | 51.0726 | 43.0895 | 98.12 | 96.0821 | 93.3768 | 90.6789 | 86.7979 | 83.1979 | 80.0695 | 77.0032 | 74.5884 | 64.4895 | 55.8737 | 47.8874
|  | SOUTHAMPTON (MAIN) BSP | HE |  |  |  |  | 116.4526 | 115.9137 | 115.32 | 114.6789 | 113.9537 | 111.8242 | 109.4779 | 107.1726 | 106.1105 | 100.2789 | 95.8537 | 92.1263 | 94.9568 | 94.0411 | 92.2789 | 90.3958 | 88.0684 | 85.7032 | 83.0789 | 80.4968 | 79.3442 | 72.82 | 67.8368 | 63.5579 | 99.4253 | 98.82 | 97.2726 | 95.4095 | 93.0968 | 90.7011 | 88.0411 | 85.4253 | 84.26 | 77.6526 | 72.6074 | 68.3274
|  | SOUTHAMPTON (MAIN) BSP | CF |  |  |  |  | 116.8611 | 116.5484 | 116.2211 | 115.8853 | 115.5358 | 115.1811 | 114.8316 | 114.4842 | 113.6284 | 109.6326 | 106.5042 | 104.0158 | 95.5337 | 95.0779 | 94.6042 | 94.1232 | 93.6253 | 92.4589 | 91.0663 | 89.2758 | 87.6684 | 83.2789 | 79.7779 | 76.96 | 99.8621 | 99.5253 | 99.1726 | 98.8116 | 98.4368 | 97.4716 | 96.0695 | 94.3084 | 92.6874 | 88.2495 | 84.6968 | 81.8389
NURSLING GSP | SOUTHAMPTON C BSP | SOUTHAMPTON C BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | YES | 0 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | SOUTHAMPTON C BSP | EE | [7 empty] | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | SOUTHAMPTON C BSP | HT | [7 empty] | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | SOUTHAMPTON C BSP | HE | [7 empty] | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | SOUTHAMPTON C BSP | CF | [7 empty] | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
LALEHAM GSP | STAINES BSP | STAINES BSP | MINIMUM HEADROOM | TQ 04585 72135 | NO | YES | 105.3158 | 29.1505 | 27.6168 | 25.9863 | 24.2989 | 22.5495 | 110.7863 | 109.2358 | 74.0274 | 70.2632 | 57.1232 | 45.1158 | 34.0642 | -5.9358 | -10.4705 | -18.6274 | -21.8632 | -25.2547 | 61.1347 | 57.5768 | 9.5411 | 5.3537 | -9.1147 | -22.4716 | -34.8747 | 0.96947 | -0.56316 | -7.6095 | -10.8 | -14.1979 | 72.1821 | 68.6211 | 20.5842 | 16.3916 | 1.8958 | -11.4916 | -23.9126
|  | STAINES BSP | EE |  |  |  |  | 30.0432 | 28.7747 | 27.4274 | 26.0179 | 24.5442 | 113.1221 | 111.7642 | 110.4526 | 109.1579 | 98.6853 | 89.3863 | 80.9863 | -4.7042 | -8.4968 | -18.6274 | -21.8632 | -25.2547 | 61.1347 | 57.5768 | 54.3316 | 50.5579 | 39.0621 | 28.7189 | 19.2589 | 1.8589 | 0.59053 | -7.6095 | -10.8 | -14.1979 | 72.1821 | 68.6211 | 65.3674 | 61.5842 | 50.0432 | 39.6495 | 30.1621
|  | STAINES BSP | HT |  |  |  |  | 29.1505 | 27.6168 | 25.9863 | 24.2989 | 22.5495 | 110.7863 | 109.2358 | 74.0274 | 70.2632 | 57.1232 | 45.1158 | 34.0642 | -5.9358 | -10.4705 | -15.3137 | -19.3463 | -23.4789 | 62.1695 | 58.5295 | 9.5411 | 5.3537 | -9.1147 | -22.4716 | -34.8747 | 0.96947 | -0.56316 | -4.4611 | -8.4074 | -12.4558 | 73.2389 | 69.5958 | 20.5842 | 16.3916 | 1.8958 | -11.4916 | -23.9126
|  | STAINES BSP | HE |  |  |  |  | 31.1884 | 30.2695 | 29.2516 | 28.1568 | 26.9863 | 115.8663 | 114.8084 | 86.4726 | 83.7158 | 76.3063 | 69.9084 | 64.2074 | -3.5011 | -4.5105 | -7.6937 | -10.2695 | -12.9916 | 74.0674 | 71.1432 | 23.0989 | 20.0147 | 11.8389 | 4.64 | -1.8537 | 3.0084 | 2.0895 | 1.0716 | -0.023158 | -2.1863 | 84.9368 | 82.08 | 34.1526 | 31.0663 | 22.8716 | 15.6579 | 9.1474
|  | STAINES BSP | CF |  |  |  |  | 31.9758 | 31.4716 | 30.9474 | 30.4042 | 29.8442 | 119.2674 | 118.6989 | 118.1389 | 117.58 | 115.0853 | 113.8263 | 113.1179 | -2.68 | -3.1979 | -3.7674 | -4.3421 | -4.94 | 83.4463 | 81.8389 | 80.1474 | 77.8232 | 70.6316 | 65.6011 | 61.2158 | 3.7968 | 3.2926 | 2.7684 | 2.2253 | 1.6653 | 91.0884 | 90.5211 | 89.9611 | 88.6253 | 81.6021 | 76.6695 | 72.28
MINETY GSP | STRATTON (RESERVE) BSP | STRATTON (RESERVE) BSP | MINIMUM HEADROOM | SU 17028 88748 | NO | YES | 109.7789 | -81.3189 | -83.7116 | -88.3379 | -90.5084 | -150.9421 | -155.9305 | -160.9495 | -165.9747 | -196.1126 | -236.3337 | -248.7632 | -256.3758 | -116.2705 | -118.9105 | -124.34 | -126.7242 | -197.24 | -202.8558 | -208.5305 | -213.2747 | -248.4611 | -294.7495 | -308.5063 | -316.94 | -116.48 | -119.12 | -124.5547 | -126.9421 | -197.5095 | -203.1516 | -208.8516 | -214.1747 | -249.4032 | -295.9084 | -309.8989 | -318.4263
|  | STRATTON (RESERVE) BSP | EE |  |  |  |  | -41.7326 | -82.3316 | -88.3379 | -90.5084 | -93.5337 | -118.1316 | -121.1137 | -126.8579 | -129.5537 | -153.8358 | -177.4474 | -185.7611 | -69.6779 | -117.4221 | -124.34 | -126.7242 | -130.0716 | -158.7379 | -162.0232 | -167.3758 | -170.3358 | -197.8916 | -224.7453 | -234.1032 | -69.8695 | -117.6305 | -124.5547 | -126.9421 | -130.3105 | -159.0168 | -162.34 | -168.4189 | -171.4263 | -199.28 | -226.4611 | -235.9253
|  | STRATTON (RESERVE) BSP | HT |  |  |  |  | -81.3189 | -83.7116 | -86.1937 | -89.32 | -150.9421 | -155.9305 | -160.9495 | -165.9747 | -196.1126 | -236.3337 | -248.7632 | -256.3758 | -116.2705 | -118.9105 | -121.6442 | -125.1305 | -197.24 | -202.8558 | -208.5305 | -213.2747 | -248.4611 | -294.7495 | -308.5063 | -316.94 | -116.48 | -119.12 | -121.8547 | -125.3432 | -197.5095 | -203.1516 | -208.8516 | -214.1747 | -249.4032 | -295.9084 | -309.8989 | -318.4263
|  | STRATTON (RESERVE) BSP | HE |  |  |  |  | -40.3389 | -80.4526 | -82.1653 | -83.8558 | -86.2389 | -88.5084 | -90.9695 | -94.7453 | -96.9358 | -117.9895 | -138.6516 | -145.0642 | -68.1768 | -115.3937 | -117.3 | -119.1695 | -121.8168 | -124.3389 | -127.0842 | -130.7863 | -133.2337 | -157.4305 | -181.3505 | -188.6242 | -68.3674 | -115.6011 | -117.5074 | -119.3768 | -122.0432 | -124.5821 | -127.3442 | -131.4074 | -133.8716 | -158.2095 | -182.2274 | -189.5874
|  | STRATTON (RESERVE) BSP | CF |  |  |  |  | -39.3295 | -39.9789 | -79.3116 | -80.1189 | -81.12 | -82.1295 | -83.1968 | -85.8095 | -87.1442 | -91.7968 | -95.8684 | -100.36 | -67.0905 | -67.8 | -114.1453 | -115.0379 | -116.1453 | -117.2558 | -118.4379 | -120.86 | -122.3547 | -127.4905 | -132.0526 | -137.1547 | -67.2758 | -67.9842 | -114.3442 | -115.2379 | -116.3537 | -117.4811 | -118.6695 | -121.4442 | -122.9463 | -128.1221 | -132.7474 | -137.9084
MINETY GSP | STRATTON (MAIN) BSP | STRATTON (MAIN) BSP | MINIMUM HEADROOM | SU 17028 88748 | NO | YES | 50.8421 | 52.7368 | 51.9095 | 51.0295 | 50.1179 | 49.1768 | 47.8526 | 45.2463 | 42.7905 | 40.6695 | 30.5589 | 21.7916 | 13.5663 | 40.8011 | 39.1274 | 37.5158 | 35.8095 | 33.6147 | 30.8926 | 28.0421 | 25.3516 | 22.9979 | 11.6242 | 1.7032 | -7.6568 | 43.9242 | 42.2863 | 40.7063 | 39.0358 | 36.8958 | 34.2537 | 31.4905 | 28.8842 | 26.5895 | 15.2137 | 5.2905 | -4.0716
|  | STRATTON (MAIN) BSP | EE |  |  |  |  | 52.94 | 52.2547 | 51.5253 | 50.7621 | 49.9716 | 49.2084 | 48.0453 | 45.7011 | 43.5295 | 34.7179 | 27.6621 | 21.7021 | 41.1884 | 39.8411 | 37.8337 | 36.6368 | 35.0411 | 33.1158 | 30.8705 | 28.2989 | 25.9137 | 15.9811 | 7.9674 | 1.3337 | 44.2147 | 42.8874 | 40.9368 | 39.76 | 38.1989 | 36.3242 | 34.1463 | 31.6558 | 29.3484 | 19.4842 | 11.4653 | 4.9211
|  | STRATTON (MAIN) BSP | HT |  |  |  |  | 52.7368 | 51.9095 | 51.0295 | 50.1179 | 49.1768 | 47.8526 | 45.2463 | 42.7905 | 40.6695 | 30.5589 | 21.7916 | 13.5663 | 40.8011 | 39.1274 | 37.5158 | 35.8095 | 33.6147 | 30.8926 | 28.0421 | 25.3516 | 22.9979 | 11.6242 | 1.7032 | -7.6568 | 43.9242 | 42.2863 | 40.7063 | 39.0358 | 36.8958 | 34.2537 | 31.4905 | 28.8842 | 26.5895 | 15.2137 | 5.2905 | -4.0716
|  | STRATTON (MAIN) BSP | HE |  |  |  |  | 53.5611 | 53.0642 | 52.5147 | 51.9253 | 51.2947 | 50.6926 | 50.1253 | 49.2316 | 47.3821 | 40.3032 | 34.8211 | 29.8768 | 42.4937 | 41.6074 | 40.7474 | 39.82 | 38.4021 | 36.5832 | 34.3789 | 32.0663 | 30.0242 | 22.0653 | 15.7863 | 10.0779 | 45.5421 | 44.6526 | 43.7747 | 42.8547 | 41.4695 | 39.7053 | 37.5737 | 35.3379 | 33.3663 | 25.5684 | 19.2884 | 13.5779
|  | STRATTON (MAIN) BSP | CF |  |  |  |  | 54.0032 | 53.7368 | 53.4589 | 53.1726 | 52.8747 | 52.5716 | 52.2747 | 51.9811 | 51.6842 | 49.2032 | 45.1442 | 42.0758 | 43.2568 | 42.7853 | 42.3105 | 41.8063 | 41.1853 | 40.5242 | 39.6632 | 38.7042 | 37.6305 | 31.9284 | 27.3779 | 23.8411 | 46.0063 | 45.7253 | 45.3758 | 44.8568 | 44.2158 | 43.5558 | 42.7189 | 41.7895 | 40.7495 | 35.24 | 30.8789 | 27.3453
MINETY GSP | SWINDON BSP | SWINDON BSP | MINIMUM HEADROOM | SU 12447 87062 | NO | YES | 3.3684 | 108.4842 | 106.9611 | 105.3526 | 88.1747 | 83.6253 | 79.0905 | 74.1105 | 67.9853 | 69.3547 | 34.8642 | 17.6 | 4.2295 | 87.5726 | 84.3937 | 81.1263 | 59.7832 | 54.5884 | 49.4095 | 43.6811 | 36.56 | 38.6147 | -0.64632 | -20.9642 | -36.1537 | 92.4116 | 89.2295 | 85.9632 | 64.6095 | 59.4042 | 54.2126 | 48.4716 | 41.3442 | 42.5442 | 3.2074 | -17.6516 | -32.8853
|  | SWINDON BSP | EE |  |  |  |  | 109.3663 | 108.1389 | 106.7021 | 88.1747 | 83.6253 | 79.0905 | 74.1105 | 67.9853 | 69.3547 | 53.2758 | 33.1968 | 22.6453 | 89.3642 | 87.1126 | 82.9989 | 59.7832 | 54.5884 | 49.4095 | 43.6811 | 36.56 | 38.6147 | 20.5295 | -1.7 | -13.7274 | 93.8589 | 91.9495 | 87.8347 | 64.6095 | 59.4042 | 54.2126 | 48.4716 | 41.3442 | 42.5442 | 24.3368 | 2.4042 | -9.6695
|  | SWINDON BSP | HT |  |  |  |  | 108.4842 | 106.9611 | 105.3526 | 102.0968 | 102.5284 | 96.2084 | 90.2579 | 85.0432 | 76.2495 | 34.8642 | 17.6 | 4.2295 | 87.5726 | 84.3937 | 81.1263 | 76.8789 | 77.8768 | 70.6063 | 63.7421 | 57.74 | 47.4116 | -0.64632 | -20.9642 | -36.1537 | 92.4116 | 89.2295 | 85.9632 | 81.7126 | 81.8789 | 74.5968 | 67.7211 | 61.7053 | 51.36 | 3.2074 | -17.6516 | -32.8853
|  | SWINDON BSP | HE |  |  |  |  | 110.4368 | 109.5663 | 108.5958 | 107.4916 | 105.7695 | 101.5558 | 96.6484 | 90.8653 | 92.8811 | 80.2295 | 57.8211 | 49.6295 | 91.0526 | 89.7663 | 88.2295 | 85.7568 | 80.8221 | 75.9653 | 70.2611 | 63.4895 | 66.2274 | 51.6084 | 24.1011 | 14.6663 | 94.92 | 94.0558 | 93.0684 | 90.5947 | 85.6526 | 80.7874 | 75.0737 | 68.2926 | 70.2021 | 55.5305 | 27.3179 | 17.8463
|  | SWINDON BSP | CF |  |  |  |  | 111.1684 | 110.6958 | 110.2063 | 109.6947 | 109.1516 | 108.5937 | 107.9979 | 107.3621 | 106.6853 | 98.0126 | 91.7284 | 86.7411 | 92.0126 | 91.3853 | 90.7337 | 90.0284 | 89.2463 | 88.3632 | 86.8979 | 84.8189 | 82.1558 | 72.0147 | 64.7137 | 58.8758 | 95.6505 | 95.1789 | 94.6916 | 94.1842 | 93.6432 | 93.0895 | 91.7263 | 89.6453 | 86.9758 | 75.9947 | 68.6695 | 62.8074
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM BSP | MINIMUM HEADROOM | SU 52824 66435 | NO | YES | 24.2105 | 82.9116 | 170.6211 | 163.5537 | 103.1116 | 98.0853 | 92.9432 | 87.6526 | 82.5095 | 78.1663 | 62.1811 | 54.8632 | 43.7884 | 30.1516 | 114.9453 | 103.4147 | 33.9758 | 28.5126 | 22.9063 | 17.1137 | 11.4832 | 6.7379 | -10.6516 | -15.6211 | -28.0716 | 37.7305 | 122.5811 | 111.1863 | 40.5632 | 35.04 | 29.3642 | 23.4968 | 17.7926 | 12.9884 | -4.6579 | -9.2126 | -21.6842
|  | THATCHAM BSP | EE |  |  |  |  | 84.2853 | 172.4053 | 163.5537 | 103.1116 | 98.0853 | 92.9432 | 87.6526 | 82.5095 | 78.1663 | 62.1811 | 54.8632 | 43.7884 | 32.6905 | 118.3832 | 103.4147 | 33.9758 | 28.5126 | 22.9063 | 17.1137 | 11.4832 | 6.7379 | -10.6516 | -15.6211 | -28.0716 | 40.2442 | 125.9884 | 111.1863 | 40.5632 | 35.04 | 29.3642 | 23.4968 | 17.7926 | 12.9884 | -4.6579 | -9.2126 | -21.6842
|  | THATCHAM BSP | HT |  |  |  |  | 82.9116 | 170.6211 | 168.0147 | 161.8032 | 155.76 | 149.1916 | 142.3905 | 137.1137 | 132.42 | 113.2516 | 96.8126 | 83.1632 | 30.1516 | 114.9453 | 108.9063 | 102.1221 | 95.5558 | 88.38 | 80.8916 | 75.1274 | 70.0137 | 49.1895 | 31.1663 | 16.1432 | 37.7305 | 122.5811 | 116.6095 | 109.9116 | 103.3095 | 96.0516 | 88.4642 | 82.6326 | 77.4547 | 56.3611 | 38.08 | 22.8537
|  | THATCHAM BSP | HE |  |  |  |  | 86.06 | 174.7316 | 173.2611 | 155.7116 | 151.8789 | 147.6137 | 143.1463 | 138.8884 | 135.4737 | 124.0979 | 112.8516 | 105.72 | 35.7126 | 122.7463 | 118.9421 | 94.1642 | 90.0084 | 85.34 | 80.4221 | 75.7284 | 71.9842 | 59.4863 | 45.1716 | 37.1863 | 43.4979 | 130.3095 | 126.5495 | 101.7484 | 97.5474 | 92.8211 | 87.84 | 83.0905 | 79.2926 | 66.6316 | 52.1979 | 44.0853
|  | THATCHAM BSP | CF |  |  |  |  | 87.2853 | 176.5853 | 175.8537 | 175.0979 | 174.3137 | 173.5137 | 172.7253 | 171.9463 | 171.1632 | 162.7295 | 155.3589 | 150.5168 | 37.6979 | 126.2421 | 124.6053 | 122.6105 | 120.7747 | 118.6589 | 116.5958 | 114.7495 | 112.6684 | 102.8968 | 94.6705 | 89.2411 | 45.7063 | 134.0316 | 132.1558 | 130.1842 | 128.3642 | 126.2779 | 124.2379 | 122.4084 | 120.3516 | 110.6905 | 102.3411 | 96.8242
MINETY GSP | TOOTHILL BSP | TOOTHILL BSP | MINIMUM HEADROOM | SU 13191 83945 | NO | YES | 41.0526 | 154.7032 | 153.9621 | 151.2211 | 146.8158 | 141.4495 | 96.9832 | 92.1947 | 87.6116 | 83.7042 | 69.3253 | 61.0779 | 53.52 | 136.3737 | 133.7505 | 130.2179 | 125.2621 | 119.2011 | 68.0126 | 62.6074 | 57.3979 | 52.9179 | 36.6263 | 27.1337 | 18.5295 | 142.9684 | 139.8126 | 135.4716 | 130.4411 | 124.2874 | 72.2147 | 66.7211 | 61.46 | 56.9832 | 40.7242 | 31.1874 | 22.5842
|  | TOOTHILL BSP | EE |  |  |  |  | 155.1389 | 154.5284 | 152.5568 | 148.48 | 143.7484 | 138.5126 | 133.8074 | 129.1505 | 125.1747 | 115.1558 | 109.1537 | 103.1789 | 137.0958 | 134.7211 | 131.5674 | 127.0537 | 121.7032 | 115.7716 | 110.4484 | 105.1737 | 100.68 | 89.5189 | 83.0432 | 76.3242 | 143.7621 | 140.92 | 136.9179 | 132.2505 | 126.8158 | 120.7884 | 115.3779 | 110.0168 | 105.4505 | 94.0916 | 87.4779 | 80.6442
|  | TOOTHILL BSP | HT |  |  |  |  | 154.7032 | 153.9621 | 151.2211 | 146.8158 | 141.4495 | 96.9832 | 92.1947 | 87.6116 | 83.7042 | 69.3253 | 61.0779 | 53.52 | 136.3737 | 133.7505 | 130.2179 | 125.2621 | 119.2011 | 68.0126 | 62.6074 | 57.3979 | 52.9179 | 36.6263 | 27.1337 | 18.5295 | 142.9684 | 139.8126 | 135.4716 | 130.4411 | 124.2874 | 72.2147 | 66.7211 | 61.46 | 56.9832 | 40.7242 | 31.1874 | 22.5842
|  | TOOTHILL BSP | HE |  |  |  |  | 155.6905 | 155.2474 | 154.1189 | 150.3189 | 145.8284 | 102.4179 | 98.0768 | 93.7 | 90.0895 | 81.4495 | 76.6032 | 71.9242 | 138.0253 | 135.9305 | 133.0442 | 129.0137 | 123.92 | 73.9011 | 68.9737 | 64.0011 | 59.8684 | 49.9253 | 44.3842 | 38.9821 | 144.7821 | 142.2895 | 138.5989 | 134.2284 | 129.0526 | 78.1642 | 73.1579 | 68.1021 | 63.9316 | 53.9853 | 48.4411 | 43.04
|  | TOOTHILL BSP | CF |  |  |  |  | 156.0716 | 155.8305 | 155.5768 | 155.3158 | 154.8821 | 152.8779 | 150.94 | 148.8042 | 146.7242 | 139.9758 | 137.1937 | 134.2716 | 139.76 | 138.0547 | 136.7516 | 135.3084 | 133.7505 | 131.8853 | 129.6916 | 127.2705 | 124.9158 | 117.3179 | 114.2074 | 110.8937 | 145.8989 | 144.7832 | 143.2295 | 141.44 | 139.4453 | 137.1389 | 134.9116 | 132.4516 | 130.0579 | 122.3421 | 119.1811 | 115.8095
IVER 132KV GSP | UPTON BSP | UPTON BSP | MINIMUM HEADROOM | TQ 00838 79445 | NO | YES | 0 | 50.9263 | 50.0116 | 48.7589 | 47.7726 | 46.2663 | 45.0453 | 43.9884 | 43.0158 | 42.1 | 37.5968 | 33.1737 | 29.1568 | 39.9147 | 38.9379 | 37.5674 | 36.5179 | 34.8558 | 33.5316 | 32.3895 | 31.3358 | 30.3421 | 25.3863 | 20.4526 | 15.9389 | 42.4 | 41.4526 | 40.1389 | 39.1211 | 37.4663 | 36.1421 | 35.0011 | 33.9484 | 32.9558 | 28.0053 | 23.0789 | 18.5716
|  | UPTON BSP | EE |  |  |  |  | 51.5274 | 50.7937 | 49.4747 | 48.8979 | 47.6463 | 46.6526 | 45.8074 | 44.9726 | 44.1958 | 40.7568 | 37.4989 | 34.4695 | 40.5621 | 39.78 | 38.3126 | 37.7263 | 36.3453 | 35.2663 | 34.3579 | 33.46 | 32.62 | 28.8453 | 25.1968 | 21.7768 | 43.0253 | 42.2653 | 40.8705 | 40.2884 | 38.9537 | 37.8747 | 36.9674 | 36.0716 | 35.2305 | 31.46 | 27.8179 | 24.4021
|  | UPTON BSP | HT |  |  |  |  | 50.9263 | 50.0116 | 48.7589 | 47.7726 | 46.2663 | 45.0453 | 43.9884 | 43.0158 | 42.1 | 37.5968 | 33.1737 | 29.1568 | 39.9147 | 38.9379 | 37.5674 | 36.5179 | 34.8558 | 33.5316 | 32.3895 | 31.3358 | 30.3421 | 25.3863 | 20.4526 | 15.9389 | 42.4 | 41.4526 | 40.1389 | 39.1211 | 37.4663 | 36.1421 | 35.0011 | 33.9484 | 32.9558 | 28.0053 | 23.0789 | 18.5716
|  | UPTON BSP | HE |  |  |  |  | 52.0432 | 51.6811 | 50.2505 | 49.8074 | 49.2379 | 48.4337 | 47.7832 | 47.1463 | 46.5684 | 44.1179 | 42.2295 | 40.4274 | 41.3705 | 40.8358 | 39.1116 | 38.6621 | 38.0684 | 37.1958 | 36.4979 | 35.8126 | 35.1884 | 32.4884 | 30.3747 | 28.3168 | 43.8032 | 43.2811 | 41.6579 | 41.2116 | 40.6295 | 39.7916 | 39.1053 | 38.4221 | 37.7979 | 35.1011 | 32.9884 | 30.9347
|  | UPTON BSP | CF |  |  |  |  | 51.5063 | 51.3053 | 51.0905 | 50.8421 | 50.3463 | 49.7937 | 49.3947 | 49.0242 | 48.6568 | 46.7442 | 46.2505 | 45.1589 | 40.6947 | 40.3758 | 40.0053 | 39.6211 | 39.0737 | 38.46 | 38.0295 | 37.6274 | 37.2326 | 35.1421 | 34.7589 | 33.5168 | 43.2695 | 42.9621 | 42.6032 | 42.2316 | 41.7095 | 41.1263 | 40.7105 | 40.3232 | 39.9432 | 37.92 | 37.3695 | 36.1295
NURSLING GSP | VELMORE BSP | VELMORE BSP | MINIMUM HEADROOM | SU 42855 19215 | NO | YES | 60 | 55.4547 | 143.7179 | 141.8747 | 138.2474 | 132.8453 | 127.5305 | 122.3958 | 108.5874 | 104.5589 | 88.5189 | 76.3168 | 64.3232 | 28.8453 | 113.3842 | 107.2053 | 102.1432 | 96.1695 | 90.2916 | 84.6084 | 68.1295 | 63.6274 | 45.6874 | 31.9716 | 19.4874 | 35.2105 | 119.9095 | 113.6821 | 108.5221 | 102.4158 | 96.4158 | 90.6779 | 74.1884 | 69.6811 | 51.7179 | 37.9716 | 25.4968
|  | VELMORE BSP | EE |  |  |  |  | 56.5095 | 145.0905 | 143.5832 | 142.0063 | 137.7611 | 133.4263 | 129.2 | 108.5874 | 104.5589 | 88.5189 | 76.3168 | 65.4095 | 31.0842 | 116.2905 | 110.8063 | 106.5168 | 101.5126 | 96.7147 | 92.0305 | 68.1295 | 63.6274 | 45.6874 | 31.9716 | 19.5811 | 37.3979 | 122.7505 | 117.3442 | 112.9674 | 107.8547 | 102.9547 | 98.1674 | 74.1884 | 69.6811 | 51.7179 | 37.9716 | 25.5663
|  | VELMORE BSP | HT |  |  |  |  | 55.4547 | 143.7179 | 141.8747 | 138.2474 | 132.8453 | 127.5305 | 122.3958 | 117.6495 | 113.1042 | 93.9284 | 78.4221 | 64.3232 | 28.8453 | 113.3842 | 107.2053 | 102.1432 | 96.1695 | 90.2916 | 84.6084 | 79.3147 | 74.2358 | 52.8221 | 35.42 | 19.4874 | 35.2105 | 119.9095 | 113.6821 | 108.5221 | 102.4158 | 96.4158 | 90.6779 | 85.38 | 80.2958 | 58.8779 | 41.4474 | 25.4968
|  | VELMORE BSP | HE |  |  |  |  | 57.8442 | 146.8389 | 145.7232 | 144.5253 | 143.2453 | 139.8621 | 136.2568 | 132.6842 | 113.1389 | 100.5074 | 91.4347 | 83.4063 | 34.0021 | 120.1137 | 115.4863 | 112.0147 | 107.7547 | 103.6905 | 99.6747 | 95.68 | 72.9474 | 58.6516 | 48.3211 | 39.1063 | 39.7947 | 126.4832 | 122.0105 | 118.5621 | 114.2042 | 110.0495 | 105.9421 | 101.8558 | 79.0084 | 64.6832 | 54.3347 | 45.1053
|  | VELMORE BSP | CF |  |  |  |  | 58.7653 | 148.2295 | 146.3716 | 145.7989 | 145.2011 | 144.5926 | 143.9926 | 143.4042 | 142.8105 | 134.6337 | 128.7032 | 123.4979 | 36.5368 | 124.4979 | 118.9179 | 117.2516 | 115.4358 | 113.6968 | 111.9179 | 110.1295 | 108.2789 | 96.8126 | 90.0421 | 84.1558 | 40.8095 | 130.1842 | 124.8358 | 123.2168 | 121.4568 | 119.7632 | 118.0316 | 116.2042 | 114.3158 | 102.66 | 95.7874 | 89.8032
MANNINGTON GSP | WAREHAM BSP | WAREHAM BSP | MINIMUM HEADROOM | SY 91548 88451 | NO | YES | 0 | 49.9111 | 40.3647 | 39.2332 | 37.3974 | 35.4847 | 33.8689 | 32.0037 | 28.0984 | 22.1247 | 15.3037 | 9.7426 | 6.7089 | 42.0384 | 34.2016 | 32.9826 | 30.9468 | 28.8268 | 27.0563 | 24.9826 | 20.5174 | 13.5542 | 5.8226 | -0.48053 | -3.8595 | 42.75 | 33.1247 | 31.9321 | 29.9542 | 27.8489 | 26.0416 | 23.9153 | 19.3205 | 12.2237 | 4.4437 | -1.9132 | -5.3142
|  | WAREHAM BSP | EE |  |  |  |  | 50.5816 | 41.2374 | 40.3058 | 38.6626 | 36.93 | 35.5111 | 34.0753 | 32.8058 | 31.6016 | 25.1753 | 20.0521 | 16.7995 | 42.7247 | 35.1089 | 34.1468 | 32.3142 | 30.39 | 28.8321 | 27.2489 | 25.8647 | 24.5416 | 17.3942 | 11.6563 | 7.9405 | 43.4595 | 34.0468 | 33.0647 | 31.2911 | 29.4226 | 27.8405 | 26.2195 | 24.7953 | 23.4374 | 16.0689 | 10.1753 | 6.4363
|  | WAREHAM BSP | HT |  |  |  |  | 49.9111 | 40.3647 | 39.2332 | 37.3974 | 35.4847 | 33.8689 | 32.0037 | 28.0984 | 22.1247 | 15.3037 | 9.7426 | 6.7089 | 42.0384 | 34.2016 | 32.9826 | 30.9468 | 28.8268 | 27.0563 | 24.9826 | 20.5174 | 13.5542 | 5.8226 | -0.48053 | -3.8595 | 42.75 | 33.1247 | 31.9321 | 29.9542 | 27.8489 | 26.0416 | 23.9153 | 19.3205 | 12.2237 | 4.4437 | -1.9132 | -5.3142
|  | WAREHAM BSP | HE |  |  |  |  | 51.3542 | 42.4026 | 41.7353 | 40.3426 | 38.8479 | 37.6679 | 36.4753 | 35.4584 | 34.4953 | 29.17 | 25.4016 | 23.0847 | 43.6384 | 36.3047 | 35.6195 | 34.1353 | 32.4668 | 31.1637 | 29.8395 | 28.7163 | 27.6521 | 21.6447 | 17.3784 | 14.7289 | 44.4037 | 35.2816 | 34.5784 | 33.0721 | 31.4532 | 30.1847 | 28.8626 | 27.7121 | 26.6195 | 20.4374 | 16.0426 | 13.3458
|  | WAREHAM BSP | CF |  |  |  |  | 51.6616 | 51.4816 | 51.2742 | 40.0174 | 39.3268 | 38.7205 | 38.0668 | 37.4626 | 36.8426 | 34.67 | 33.3195 | 31.9921 | 44.1826 | 43.8121 | 43.4353 | 32.4226 | 31.71 | 31.0826 | 30.4079 | 29.7868 | 29.1447 | 26.9153 | 25.4574 | 23.9637 | 44.9616 | 44.5816 | 44.1921 | 30.5195 | 29.9921 | 29.5195 | 29.0174 | 28.5511 | 27.8942 | 25.4647 | 23.9405 | 22.3995
MELKSHAM GSP | WEST GRAFTON BSP | WEST GRAFTON BSP | MINIMUM HEADROOM | SU 24302 59215 | NO | YES | 15 | 38.9179 | 37.4358 | 35.8211 | 33.8947 | 31.9463 | 29.8611 | 27.8863 | 21.8095 | 19.5642 | 7.4179 | 1.0789 | -4.5474 | 29.1937 | 27.5242 | 25.6958 | 23.4526 | 21.2 | 18.7768 | 16.4726 | 8.9779 | 6.3105 | -8.2779 | -15.6474 | -22.0263 | 30.9684 | 29.2632 | 27.3979 | 25.1526 | 22.8874 | 20.4526 | 18.1358 | 10.6263 | 7.9432 | -6.7484 | -14.2326 | -20.6579
|  | WEST GRAFTON BSP | EE |  |  |  |  | 39.7263 | 38.3968 | 36.9926 | 35.4084 | 33.8021 | 32.2211 | 30.5579 | 27.9726 | 25.8684 | 13.4242 | 8.44 | 4.5789 | 30.1011 | 28.5916 | 27 | 25.1768 | 23.3305 | 21.5105 | 19.5874 | 16.4958 | 14.0021 | -1.0032 | -6.6989 | -11.2621 | 31.8916 | 30.3484 | 28.7263 | 26.8747 | 25.0179 | 23.1811 | 21.2421 | 18.1316 | 15.6147 | 0.46737 | -5.3853 | -9.9989
|  | WEST GRAFTON BSP | HT |  |  |  |  | 38.9179 | 37.4358 | 35.8211 | 33.8947 | 31.9463 | 29.8611 | 27.8863 | 21.8095 | 19.5642 | 7.4179 | 1.0789 | -4.5474 | 29.1937 | 27.5242 | 25.6958 | 23.4526 | 21.2 | 18.7768 | 16.4726 | 8.9779 | 6.3105 | -8.2779 | -15.6474 | -22.0263 | 30.9684 | 29.2632 | 27.3979 | 25.1526 | 22.8874 | 20.4526 | 18.1358 | 10.6263 | 7.9432 | -6.7484 | -14.2326 | -20.6579
|  | WEST GRAFTON BSP | HE |  |  |  |  | 40.6 | 39.6442 | 38.5063 | 37.1895 | 35.84 | 34.5137 | 33.0684 | 30.7705 | 28.9853 | 17.8463 | 14.3084 | 11.4137 | 31.06 | 29.9747 | 28.6737 | 27.16 | 25.6137 | 24.0716 | 22.3737 | 19.5937 | 17.4453 | 3.7947 | -0.41579 | -3.8863 | 32.8663 | 31.7579 | 30.4284 | 28.8811 | 27.3063 | 25.7558 | 24.0484 | 21.2611 | 19.1032 | 5.3905 | 1.1358 | -2.3768
|  | WEST GRAFTON BSP | CF |  |  |  |  | 41.2684 | 40.8295 | 40.2989 | 39.7568 | 39.3474 | 38.9411 | 38.4737 | 37.8526 | 37.1526 | 29.6063 | 26.1179 | 24.06 | 31.8021 | 31.3095 | 30.7053 | 30.0895 | 29.6411 | 29.2 | 28.6821 | 27.9747 | 27.1705 | 17.9611 | 13.7295 | 11.2537 | 33.6211 | 33.1189 | 32.5011 | 31.8726 | 31.4137 | 30.9653 | 30.4347 | 29.7074 | 28.8821 | 19.6232 | 15.3663 | 12.86
NURSLING GSP | WINCHESTER BSP | WINCHESTER BSP | MINIMUM HEADROOM | SU 44965 26671 | NO | YES | 75.8074 | 33.8295 | 32.1884 | -10.1011 | -14.0432 | 70.6463 | 65.4 | 59.9653 | 57.3674 | 55.1284 | 13.5326 | -30.9874 | -41.0253 | 18.2821 | 11.4684 | -37.8168 | -42.2211 | 41.84 | 35.9884 | 29.8916 | 27.1189 | 24.76 | -25.1589 | -76.1968 | -87.2663 | 27.0221 | 22.1537 | -27.2979 | -31.7032 | 52.3137 | 46.4137 | 40.2663 | 37.4379 | 35.0189 | -16.1842 | -67.6358 | -78.8905
|  | WINCHESTER BSP | EE |  |  |  |  | 34.9242 | 33.9663 | 14.4495 | 0.089474 | 87.0547 | 84.1768 | 81.6642 | 79.2021 | 77.0916 | 63.6358 | 31.7189 | 6.8432 | 19.7337 | 17.7789 | -9.18 | -25.8484 | 60.8474 | 57.7568 | 55.0937 | 52.4968 | 50.3063 | 35.9884 | -2.3158 | -30.9505 | 28.5674 | 27.6116 | 1.3463 | -15.3326 | 71.3221 | 68.1674 | 65.4379 | 62.7653 | 60.4926 | 45.6232 | 5.6432 | -23.1558
|  | WINCHESTER BSP | HT |  |  |  |  | 34.2421 | 32.1884 | -10.1011 | -14.0432 | 70.6463 | 65.4 | 59.9653 | 57.3674 | 55.1284 | 13.5326 | -30.9874 | -41.0253 | 18.2821 | 11.4684 | -37.8168 | -42.2211 | 41.84 | 35.9884 | 29.8916 | 27.1189 | 24.76 | -25.1589 | -76.1968 | -87.2663 | 27.8863 | 22.1537 | -27.2979 | -31.7032 | 52.3137 | 46.4137 | 40.2663 | 37.4379 | 35.0189 | -16.1842 | -67.6358 | -78.8905
|  | WINCHESTER BSP | HE |  |  |  |  | 35.7979 | 35.1232 | 34.3758 | 20.3758 | 107.7916 | 105.4558 | 103.5558 | 101.7474 | 100.5032 | 91.9632 | 62.0526 | 39.6168 | 21.5284 | 20.2389 | 18.1516 | -2.3421 | 84.8284 | 82.2821 | 80.24 | 78.2979 | 77.0063 | 67.7284 | 29.3716 | 3.4011 | 29.4421 | 28.7674 | 28.02 | 8.1947 | 95.3337 | 92.7547 | 90.6821 | 88.7042 | 87.3789 | 77.8747 | 38.0526 | 11.9474
|  | WINCHESTER BSP | CF |  |  |  |  | 33.8295 | 33.4642 | 33.0842 | 32.6947 | 121.6768 | 123.4337 | 122.3495 | 121.3032 | 120.4 | 115.1695 | 108.5316 | 102.52 | 18.7137 | 18.1253 | 17.3042 | 11.7632 | 100.4547 | 102.74 | 101.58 | 100.4663 | 99.5095 | 93.9042 | 86.4326 | 79.6463 | 27.0221 | 26.6568 | 26.2768 | 22.8389 | 111.4874 | 113.4011 | 112.2074 | 111.0589 | 110.0758 | 104.2989 | 96.7274 | 89.8326
COWLEY GSP | WITNEY BSP | WITNEY BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | YES | 95.7895 | -69.2547 | -72.2463 | 14.6263 | -21.2568 | -26.0411 | -31.0621 | -35.8116 | -40.1021 | -43.6684 | -62.2158 | -76.4779 | -88.6568 | -111.9726 | -115.2316 | -28.6347 | -70.5695 | -75.8737 | -81.4568 | -86.7568 | -91.5274 | -95.4684 | -116.1389 | -131.9358 | -145.88 | -110.22 | -113.4811 | -26.8863 | -68.7537 | -74.0737 | -79.6705 | -84.9853 | -89.7758 | -93.7389 | -114.5611 | -130.5442 | -144.6074
|  | WITNEY BSP | EE |  |  |  |  | -41.9368 | -44.4116 | 43.0589 | 4.8568 | -22.3716 | -26.4084 | -30.2937 | -34.4989 | -38.0232 | -49.74 | -59.1074 | -69.6263 | -80.0463 | -82.7453 | 4.5074 | -40.1274 | -71.8905 | -76.3632 | -80.6589 | -85.3389 | -89.2379 | -101.9211 | -111.7463 | -123.6411 | -78.2863 | -80.9853 | 6.2653 | -38.3663 | -70.0947 | -74.5905 | -78.9126 | -83.6211 | -87.5516 | -100.4737 | -110.5305 | -122.4979
|  | WITNEY BSP | HT |  |  |  |  | -69.2547 | -72.2463 | 14.6263 | -21.2568 | -26.0411 | -31.0621 | -35.8116 | -40.1021 | -43.6684 | -62.2158 | -76.4779 | -88.6568 | -111.9726 | -115.2316 | -28.6347 | -70.5695 | -75.8737 | -81.4568 | -86.7568 | -91.5274 | -95.4684 | -116.1389 | -131.9358 | -145.88 | -110.22 | -113.4811 | -26.8863 | -68.7537 | -74.0737 | -79.6705 | -84.9853 | -89.7758 | -93.7389 | -114.5611 | -130.5442 | -144.6074
|  | WITNEY BSP | HE |  |  |  |  | -39.6337 | -41.3884 | 46.7779 | 28.6042 | 1.9811 | -1.4368 | -4.7558 | -8.32 | -11.1547 | -19.5 | -26.6495 | -34.1611 | -77.5432 | -79.4579 | 8.5484 | -12.6105 | -43.6884 | -47.5074 | -51.2158 | -55.2263 | -58.3979 | -67.5853 | -75.8537 | -84.4053 | -75.78 | -77.6947 | 10.3126 | -10.8558 | -41.9305 | -45.7579 | -49.4789 | -53.4968 | -56.6789 | -65.9621 | -74.3537 | -82.9632
|  | WITNEY BSP | CF |  |  |  |  | 17.62 | -11.5916 | 77.4474 | 76.1758 | 47.6242 | 46.1242 | 44.6958 | 43.1747 | 41.8642 | 33.4021 | 29.3337 | 24.4653 | -9.8632 | -44.6821 | 44.2705 | 42.8611 | 9.4347 | 7.7737 | 6.1905 | 4.5 | 3.0558 | -6.4495 | -10.9695 | -16.5042 | -8.0768 | -42.9084 | 46.0432 | 44.6316 | 11.1895 | 9.5211 | 7.9337 | 6.2347 | 4.7853 | -4.7495 | -9.3147 | -14.8979
FLEET-BRAMLEY GSP | WOKINGHAM BSP | WOKINGHAM BSP | MINIMUM HEADROOM | SU 79589 67665 | NO | YES | 0.13789 | 99.0779 | 98.3726 | 97.6242 | 96.4937 | 94.5474 | 92.4874 | 90.5411 | 88.6368 | 86.8442 | 79.8937 | 75.0484 | 70.4989 | 88.3389 | 86.4642 | 84.4274 | 82.4663 | 80.3189 | 78.04 | 75.8779 | 73.7495 | 71.7495 | 64 | 58.62 | 53.5189 | 91.2716 | 89.4411 | 87.4474 | 85.4874 | 83.3411 | 81.0589 | 78.8958 | 76.7684 | 74.7674 | 67.0147 | 61.6316 | 56.5263
|  | WOKINGHAM BSP | EE |  |  |  |  | 99.5074 | 98.9337 | 98.3242 | 97.6874 | 96.7768 | 95.1789 | 93.6253 | 91.9695 | 90.3737 | 84.5684 | 81.1158 | 77.9389 | 89.3053 | 87.7947 | 86.0863 | 84.4895 | 82.7674 | 81.0042 | 79.2842 | 77.4411 | 75.6558 | 69.1674 | 65.3316 | 61.76 | 92.2211 | 90.7432 | 89.0747 | 87.5105 | 85.7895 | 84.0242 | 82.3032 | 80.46 | 78.6737 | 72.1811 | 68.3421 | 64.7705
|  | WOKINGHAM BSP | HT |  |  |  |  | 99.0779 | 98.3726 | 97.6242 | 96.4937 | 94.5474 | 92.4874 | 90.5411 | 88.6368 | 86.8442 | 79.8937 | 75.0484 | 70.4989 | 88.3389 | 86.4642 | 84.4274 | 82.4663 | 80.3189 | 78.04 | 75.8779 | 73.7495 | 71.7495 | 64 | 58.62 | 53.5189 | 91.2716 | 89.4411 | 87.4474 | 85.4874 | 83.3411 | 81.0589 | 78.8958 | 76.7684 | 74.7674 | 67.0147 | 61.6316 | 56.5263
|  | WOKINGHAM BSP | HE |  |  |  |  | 100.0611 | 99.6568 | 99.2126 | 98.7337 | 98.2221 | 97.7326 | 96.5305 | 95.1537 | 93.8337 | 89.3863 | 87.1326 | 85.0526 | 90.4884 | 89.3779 | 88.0284 | 86.7726 | 85.36 | 83.8968 | 82.4389 | 80.8958 | 79.4126 | 74.4095 | 71.8884 | 69.5232 | 93.38 | 92.2958 | 90.9768 | 89.7505 | 88.3705 | 86.9189 | 85.46 | 83.9158 | 82.4305 | 77.4253 | 74.9032 | 72.5368
|  | WOKINGHAM BSP | CF |  |  |  |  | 100.4274 | 100.2137 | 99.9895 | 99.76 | 99.5221 | 99.2789 | 99.0411 | 98.8042 | 98.5663 | 95.2611 | 93.8347 | 92.7821 | 91.5568 | 90.9853 | 90.2937 | 89.6589 | 88.9642 | 88.2505 | 87.5453 | 86.86 | 86.1558 | 80.9053 | 79.3221 | 78.1368 | 93.8158 | 93.5811 | 93.1895 | 92.5684 | 91.8905 | 91.1937 | 90.5063 | 89.8368 | 89.1505 | 83.9253 | 82.3411 | 81.1547
FAWLEY GSP | WOOTTON COMMON BSP | WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ52785 90310 | NO | YES | 50.88 | -5.8126 | -8.9547 | -12.1642 | -15.4611 | -35.6611 | -39.3432 | -42.9221 | -46.3874 | -53.3147 | -134.7105 | -148.2274 | -160.3874 | -37.1053 | -40.5316 | -44.0253 | -47.6095 | -68.1011 | -72.1021 | -76.0147 | -79.8147 | -87.6958 | -176.9905 | -191.9358 | -205.6011 | -34.1663 | -37.5958 | -41.0916 | -44.6768 | -65.1853 | -69.2021 | -73.1326 | -76.9537 | -84.8579 | -175.7537 | -190.8526 | -204.5705
|  | WOOTTON COMMON BSP | EE |  |  |  |  | 53.7621 | 52.54 | 29.5316 | 26.8011 | 7.3926 | 4.5242 | 1.6358 | -1.1305 | -3.8484 | -82.0253 | -93.3347 | -102.84 | 35.9705 | 33.2368 | 4.68 | 1.7105 | -17.8989 | -20.9937 | -24.1211 | -27.1084 | -30.06 | -115.6737 | -127.9495 | -138.6547 | 39.0442 | 36.3758 | 7.6295 | 4.66 | -14.9642 | -18.0832 | -21.2368 | -24.2495 | -27.2295 | -114.4874 | -127.1411 | -137.9084
|  | WOOTTON COMMON BSP | HT |  |  |  |  | -5.8126 | -8.9547 | -12.1642 | -15.4611 | -35.6611 | -39.3432 | -42.9221 | -46.3874 | -53.3147 | -134.7105 | -148.2274 | -160.3874 | -37.1053 | -40.5316 | -44.0253 | -47.6095 | -68.1011 | -72.1021 | -76.0147 | -79.8147 | -87.6958 | -176.9905 | -191.9358 | -205.6011 | -34.1663 | -37.5958 | -41.0916 | -44.6768 | -65.1853 | -69.2021 | -73.1326 | -76.9537 | -84.8579 | -175.7537 | -190.8526 | -204.5705
|  | WOOTTON COMMON BSP | HE |  |  |  |  | 54.8905 | 54.02 | 33.2589 | 31.1905 | 29.0484 | 10.1347 | 7.8958 | 5.7768 | 3.64 | -16.4737 | -79.2337 | -86.1926 | 38.3916 | 36.48 | 8.7347 | 6.4884 | 4.1853 | -14.9105 | -17.3463 | -19.6526 | -22 | -49.5432 | -113.1779 | -120.9537 | 41.4084 | 39.5411 | 11.6884 | 9.4411 | 7.1284 | -11.9821 | -14.4274 | -16.7453 | -19.1053 | -48.0316 | -111.8705 | -119.8316
|  | WOOTTON COMMON BSP | CF |  |  |  |  | 55.6884 | 55.2284 | 53.88 | 53.3863 | 52.8526 | 52.3116 | 51.7779 | 29.0337 | 27.8474 | 21.4642 | 16.1432 | 11.6537 | 40.02 | 39.0389 | 35.8695 | 34.5926 | 33.2537 | 31.8505 | 30.46 | 3.4568 | 2.16 | -4.8958 | -10.8874 | -15.9863 | 42.5 | 42.0095 | 38.6621 | 37.4211 | 36.1126 | 34.74 | 33.3863 | 6.1232 | 4.8221 | -2.2621 | -8.2884 | -13.4253
LOVEDEAN GSP | WYMERING BSP | WYMERING BSP | MINIMUM HEADROOM | SU 64948 05441 | NO | YES | 5.8305 | 92.9116 | 92.6832 | 92.4684 | 92.2495 | 92.02 | 98.2074 | 97.0895 | 96.0105 | 95.3453 | 92.1853 | 88.9284 | 86.0526 | 89.76 | 89.5021 | 89.2632 | 89.02 | 88.7695 | 97.4253 | 96.2095 | 95.0326 | 94.3253 | 91.0084 | 87.4874 | 84.3421 | 91.4095 | 91.1526 | 90.9147 | 90.6705 | 90.4189 | 97.2653 | 96.0179 | 94.8126 | 94.0895 | 90.7137 | 87.0853 | 83.8547
|  | WYMERING BSP | EE |  |  |  |  | 103.3537 | 102.84 | 102.3137 | 101.7705 | 100.7095 | 99.6611 | 98.6305 | 97.6126 | 96.6347 | 94.1242 | 91.6 | 89.3853 | 102.9737 | 102.4326 | 101.8768 | 101.3053 | 100.1505 | 99.0105 | 97.8895 | 96.7832 | 95.7158 | 93.0789 | 90.4211 | 87.9958 | 102.9263 | 102.3758 | 101.8126 | 101.2347 | 100.0505 | 98.8821 | 97.7316 | 96.5958 | 95.4989 | 92.7874 | 90.0516 | 87.5558
|  | WYMERING BSP | HT |  |  |  |  | 102.9326 | 102.2958 | 101.6442 | 100.5516 | 99.3779 | 98.2074 | 97.0895 | 96.0105 | 95.3453 | 92.1853 | 88.9284 | 86.0526 | 102.5232 | 101.8463 | 101.16 | 99.9705 | 98.6947 | 97.4253 | 96.2095 | 95.0326 | 94.3253 | 91.0084 | 87.4874 | 84.3421 | 102.4674 | 101.7811 | 101.0832 | 99.8695 | 98.5642 | 97.2653 | 96.0179 | 94.8126 | 94.0895 | 90.7137 | 87.0853 | 83.8547
|  | WYMERING BSP | HE |  |  |  |  | 103.8947 | 103.5505 | 103.1811 | 102.7926 | 102.0368 | 101.3042 | 100.5916 | 99.9032 | 99.2526 | 97.1263 | 95.4211 | 93.8905 | 103.5558 | 103.1947 | 102.8084 | 102.4032 | 101.5853 | 100.7926 | 100.0211 | 99.2747 | 98.5663 | 96.2516 | 94.3453 | 92.6568 | 103.5189 | 103.1537 | 102.7621 | 102.3526 | 101.5168 | 100.7053 | 99.9158 | 99.1505 | 98.4242 | 96.0389 | 94.0516 | 92.3105
|  | WYMERING BSP | CF |  |  |  |  | 92.9116 | 92.6832 | 92.4684 | 92.2495 | 92.02 | 102.9137 | 102.5116 | 102.0958 | 101.6663 | 99.8779 | 98.8705 | 97.8411 | 89.76 | 89.5021 | 89.2632 | 89.02 | 88.7695 | 102.5105 | 102.0737 | 101.6221 | 101.1547 | 99.2137 | 98.1211 | 96.9842 | 91.4095 | 91.1526 | 90.9147 | 90.6705 | 90.4189 | 102.4547 | 102.0074 | 101.5453 | 101.0653 | 99.0779 | 97.9558 | 96.7821
COWLEY GSP | YARNTON BSP | YARNTON BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | YES | 123.6726 | -38.7684 | 48.5421 | 6.8368 | 3.6358 | -27.3726 | -31.4221 | -35.8558 | -40.5042 | -45.3 | -58.8274 | -74.9832 | -83.5305 | -75.3621 | 11.7095 | -37.1137 | -40.6221 | -77.1474 | -81.6916 | -86.6968 | -91.96 | -97.42 | -112.4642 | -130.9716 | -140.6937 | -71.2011 | 15.8747 | -32.86 | -36.3663 | -72.8263 | -77.3684 | -82.3726 | -87.6337 | -93.0916 | -108.1337 | -126.6611 | -136.3863
|  | YARNTON BSP | EE |  |  |  |  | -37.1937 | 50.5884 | 16.1989 | 14.0274 | -27.3726 | -31.4221 | -35.8558 | -40.5042 | -45.3 | -58.8274 | -74.9832 | -83.5305 | -73.6442 | 13.9358 | -26.3189 | -28.66 | -77.1474 | -81.6916 | -86.6968 | -91.96 | -97.42 | -112.4642 | -130.9716 | -140.6937 | -69.4853 | 18.0968 | -22.0853 | -24.4253 | -72.8263 | -77.3684 | -82.3726 | -87.6337 | -93.0916 | -108.1337 | -126.6611 | -136.3863
|  | YARNTON BSP | HT |  |  |  |  | -38.7684 | 48.5421 | 6.8368 | 3.6358 | -0.65474 | -6.5684 | -11.7842 | -16.1505 | -25.2284 | -53.8379 | -65.3137 | -76.1011 | -75.3621 | 11.7095 | -37.1137 | -40.6221 | -45.4011 | -52.0905 | -57.9853 | -62.8863 | -73.3621 | -106.1874 | -119.0389 | -131.3968 | -71.2011 | 15.8747 | -32.86 | -36.3663 | -41.1432 | -47.8242 | -53.7137 | -58.6095 | -69.0758 | -101.8821 | -114.7558 | -127.1379
|  | YARNTON BSP | HE |  |  |  |  | -35.0842 | 53.3474 | 51.5147 | 49.5653 | 46.6516 | 4.1926 | 0.10211 | -3.9979 | -8.1042 | -19.6263 | -33.5421 | -39.58 | -71.3474 | 16.9463 | 14.9337 | 12.8053 | 9.5484 | -40.2368 | -44.8916 | -49.5653 | -54.2674 | -67.5411 | -83.6453 | -90.5789 | -67.1926 | 21.1042 | 19.0947 | 16.9674 | 13.7137 | -35.9832 | -40.6326 | -45.3032 | -49.9989 | -63.3042 | -79.4 | -86.3358
|  | YARNTON BSP | CF |  |  |  |  | -28.7642 | 60.4716 | 55.0905 | 54.2947 | 14.7232 | 13.8642 | 12.8505 | 11.7442 | 10.2158 | -0.99474 | -7.5611 | -11.6958 | -63.9684 | 25.1937 | 18.7947 | 17.9358 | -28.5432 | -29.4737 | -30.5811 | -31.8032 | -33.5211 | -46.3516 | -53.8084 | -58.5642 | -59.7 | 29.4632 | 23.0768 | 22.2168 | -24.1758 | -25.1074 | -26.2168 | -27.4389 | -29.1537 | -41.9705 | -49.5484 | -54.3021
AXMINSTER GSP | YEOVIL BSP | YEOVIL BSP | MINIMUM HEADROOM | ST 57586 16894 | NO | YES | 90.5053 | -12.6179 | -20.4905 | -90.3842 | -96.4389 | -103.6 | -110.6358 | -57.8695 | -62.1432 | -66.4137 | -98.2653 | -121.6063 | -133.6326 | -44.92 | -54.0884 | -135.6947 | -142.5021 | -150.4811 | -158.3326 | -106.4505 | -111.1011 | -115.7568 | -151.42 | -179.4105 | -192.5926 | -40.1137 | -49.2905 | -130.86 | -137.6589 | -145.7295 | -153.6316 | -101.8021 | -106.52 | -111.2495 | -147.3684 | -176.3653 | -189.7684
|  | YEOVIL BSP | EE |  |  |  |  | -10.7011 | -20.4905 | -29.4474 | -33.7663 | -38.4695 | -67.7979 | -11.8705 | -16.0505 | -20.2084 | -36.5989 | -51.5621 | -64.6789 | -42.8379 | -54.0884 | -64.3526 | -69.1526 | -74.3116 | -108.3663 | -52.7695 | -57.2884 | -61.7916 | -79.1558 | -93.1768 | -107.7926 | -38.0295 | -49.2905 | -59.5579 | -64.3653 | -69.5821 | -103.7158 | -48.1968 | -52.8105 | -57.4158 | -75.4495 | -89.2916 | -104.1453
|  | YEOVIL BSP | HT |  |  |  |  | -12.6179 | -16.4853 | -90.3842 | -96.4389 | -103.6 | -110.6358 | -57.8695 | -62.1432 | -66.4137 | -98.2653 | -121.6063 | -133.6326 | -44.92 | -49.1747 | -135.6947 | -142.5021 | -150.4811 | -158.3326 | -106.4505 | -111.1011 | -115.7568 | -151.42 | -179.4105 | -192.5926 | -40.1137 | -44.3737 | -130.86 | -137.6589 | -145.7295 | -153.6316 | -101.8021 | -106.52 | -111.2495 | -147.3684 | -176.3653 | -189.7684
|  | YEOVIL BSP | HE |  |  |  |  | -8.1474 | -10.6589 | -13.4232 | -17.0021 | -20.9916 | -24.6084 | 32.1368 | 28.8011 | 25.5211 | 14.8432 | -5.5432 | -15.2274 | -40.0558 | -42.84 | -45.8979 | -49.9021 | -54.3063 | -58.2884 | -1.8632 | -5.5284 | -9.1579 | -20.7063 | -47.2095 | -58.0674 | -35.2474 | -38.0316 | -41.0916 | -45.1 | -49.5442 | -53.5632 | 2.8253 | -0.88105 | -4.5484 | -16.4 | -43.9189 | -54.9705
|  | YEOVIL BSP | CF |  |  |  |  | -5.8895 | -7.1042 | -8.3926 | -10.0737 | -12.0105 | -14.0337 | 43.9516 | 41.8179 | 39.5411 | 31.9168 | 25.4516 | 18.6979 | -37.5568 | -38.8947 | -40.3168 | -42.1979 | -44.34 | -46.5832 | 11.1811 | 8.8011 | 6.2463 | -2.12 | -9.2853 | -16.8768 | -32.7484 | -34.0853 | -35.5095 | -37.3895 | -39.5537 | -41.8158 | 15.9305 | 13.5358 | 10.9653 | 2.5105 | -4.8011 | -12.5232

## BSP Demand Headroom
Grid Supply Point | Bulk Supply Point |  | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Demand (MVA) | Demand Headroom Winter (MVA) | [11 empty] | Demand Headroom Summer (MVA) | [11 empty] | Demand Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT BSP | MINIMUM HEADROOM | SU 85922 48779 | NO | NO | 36.106 | -21.6728 | -27.4513 | -33.084 | -38.7666 | -45.6544 | -53.7697 | -62.5534 | -71.0146 | -77.3789 | -106.9564 | -128.1575 | -139.7166 | 9.6252 | 5.4568 | 1.6303 | -2.1697 | -7.0605 | -12.7013 | -19.0381 | -25.2952 | -29.9983 | -53.7973 | -81.7054 | -147.4095 | -16.9677 | -22.2626 | -27.283 | -32.3146 | -38.6279 | -46.0993 | -54.3003 | -62.2166 | -68.0636 | -94.7452 | -113.283 | -122.7942
|  | ALDERSHOT BSP | EE |  |  |  |  | -21.6728 | -27.4513 | -33.084 | -38.7666 | -45.6544 | -53.7697 | -62.5534 | -71.0146 | -77.3789 | -106.9564 | -125.6564 | -138.6462 | 9.6252 | 5.4568 | 1.6303 | -2.1697 | -7.0605 | -12.7013 | -19.0381 | -25.2952 | -29.9983 | -53.7973 | -76.6238 | -109.9371 | -16.9677 | -22.2626 | -27.283 | -32.3146 | -38.6279 | -46.0993 | -54.3003 | -62.2166 | -68.0636 | -94.7452 | -111.1442 | -122.032
|  | ALDERSHOT BSP | HT |  |  |  |  | -18.636 | -23.3054 | -28.7728 | -34.7922 | -40.234 | -46.6177 | -52.8258 | -60.1636 | -67.6381 | -104.6891 | -128.1575 | -139.7166 | 12.7517 | 9.9211 | 6.7242 | 3.1956 | 0.067024 | -3.4422 | -6.9064 | -11.3238 | -15.882 | -37.1289 | -48.9503 | -53.8769 | -13.9503 | -18.135 | -22.9605 | -28.3146 | -33.1666 | -38.9064 | -44.5309 | -51.2962 | -58.2064 | -92.2218 | -113.283 | -122.7942
|  | ALDERSHOT BSP | HE |  |  |  |  | -18.9289 | -23.6769 | -29.134 | -35.2044 | -40.7534 | -46.7524 | -52.6473 | -59.6401 | -66.7789 | -101.6615 | -122.7707 | -130.9483 | 11.7966 | 8.4538 | 4.7497 | 0.63437 | -3.184 | -7.3269 | -11.5473 | -16.8197 | -22.3269 | -51.7462 | -76.9687 | -108.183 | -14.2615 | -18.536 | -23.386 | -28.8054 | -33.7911 | -39.2126 | -44.5942 | -51.1044 | -57.7585 | -89.983 | -108.786 | -115.4248
|  | ALDERSHOT BSP | CF |  |  |  |  | -16.1554 | -19.4605 | -23.2126 | -27.1422 | -31.0177 | -33.6289 | -36.8952 | -39.2615 | -42.8962 | -67.0034 | -91.0646 | -111.3615 | 13.2487 | 10.6231 | 7.7476 | 4.6915 | 1.3742 | -1.4911 | -5.083 | -8.0075 | -12.1279 | -40.535 | -81.7054 | -147.4095 | -11.7044 | -14.6381 | -17.9258 | -21.383 | -24.882 | -27.2228 | -30.2595 | -32.3962 | -35.8126 | -58.4126 | -80.4615 | -98.6503
FLEET-BRAMLEY GSP | ALTON BSP | ALTON BSP | MINIMUM HEADROOM | SU 72730 39772 | NO | NO | 47.692 | -31.3736 | -35.9777 | -41.194 | -45.7583 | -50.5971 | -57.0971 | -64.8583 | -71.9134 | -77.1664 | -107.1256 | -128.0542 | -139.9909 | 3.0246 | -0.16211 | -3.9978 | -7.2764 | -10.7193 | -14.9733 | -20.3672 | -25.2672 | -28.8825 | -50.5509 | -72.0407 | -126.3958 | -29.3233 | -33.6029 | -38.6356 | -42.8478 | -47.2958 | -53.2866 | -60.4233 | -66.9417 | -71.8509 | -98.5386 | -116.7142 | -126.7335
|  | ALTON BSP | EE |  |  |  |  | -31.3736 | -35.9777 | -41.194 | -45.7583 | -50.5971 | -57.0971 | -64.8583 | -71.9134 | -77.1664 | -107.1011 | -124.4583 | -137.0879 | 3.0246 | -0.16211 | -3.9978 | -7.2764 | -10.7193 | -14.9733 | -20.3672 | -25.2672 | -28.8825 | -50.5509 | -69.8703 | -97.757 | -29.3233 | -33.6029 | -38.6356 | -42.8478 | -47.2958 | -53.2866 | -60.4233 | -66.9417 | -71.8509 | -98.5386 | -113.5591 | -124.3091
|  | ALTON BSP | HT |  |  |  |  | -29.1164 | -33.5971 | -38.5491 | -42.0144 | -46.0399 | -51.8552 | -58.2032 | -64.8399 | -71.4971 | -107.1256 | -128.0542 | -139.9909 | 5.5389 | 2.8318 | -0.43048 | -2.2784 | -4.5713 | -7.5519 | -11.0101 | -14.8193 | -18.7386 | -38.7968 | -49.0488 | -54.3978 | -27.1386 | -31.2182 | -35.958 | -39.0693 | -42.708 | -47.9509 | -53.7305 | -59.8182 | -65.9162 | -98.258 | -116.7142 | -126.7335
|  | ALTON BSP | HE |  |  |  |  | -29.0093 | -33.3971 | -38.2246 | -41.5215 | -45.3113 | -50.3389 | -55.9175 | -61.7685 | -67.3807 | -100.2011 | -117.9879 | -126.2368 | 5.1052 | 2.1205 | -1.3948 | -3.504 | -6.0386 | -9.2601 | -13.0897 | -17.2376 | -21.308 | -46.8142 | -66.9397 | -93.2437 | -27.0376 | -31.0529 | -35.6897 | -38.6376 | -42.0835 | -46.6325 | -51.7458 | -57.1458 | -62.3121 | -92.1376 | -107.704 | -114.4111
|  | ALTON BSP | CF |  |  |  |  | -25.1552 | -27.9338 | -31.4981 | -34.4909 | -36.9287 | -39.7317 | -43.246 | -46.192 | -49.1654 | -70.0664 | -92.7685 | -111.1613 | 6.8879 | 4.6073 | 1.6297 | -0.77232 | -2.6407 | -5.0733 | -8.3458 | -11.2254 | -14.3356 | -37.1774 | -72.0407 | -126.3958 | -23.8213 | -26.4111 | -29.8693 | -32.5652 | -34.6805 | -37.1488 | -40.355 | -43.0672 | -45.8101 | -65.0774 | -85.555 | -101.7917
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | AMESBURY BSP | MINIMUM HEADROOM | SU 15842 42724 | NO | NO | 4.048 | 60.0835 | 59.0693 | 58.0233 | 57.2478 | 56.0988 | 54.7682 | 53.3958 | 51.6876 | 50.5856 | 44.9213 | 41.2478 | 39.0988 | 67.7899 | 67.1368 | 66.4654 | 65.9685 | 65.2256 | 64.4358 | 63.6144 | 62.5532 | 61.796 | 57.343 | 51.4736 | 37.9726 | 58.592 | 57.5675 | 56.5379 | 55.8379 | 54.6828 | 53.495 | 52.2777 | 50.6368 | 49.6971 | 45.2797 | 42.4103 | 40.7542
|  | AMESBURY BSP | EE |  |  |  |  | 60.0835 | 59.0693 | 58.0233 | 57.2478 | 56.0988 | 54.7682 | 53.3958 | 51.6876 | 50.5856 | 44.9213 | 41.6733 | 40.0437 | 67.7899 | 67.1368 | 66.4654 | 65.9685 | 65.2256 | 64.4358 | 63.6144 | 62.5532 | 61.796 | 57.343 | 52.743 | 46.0501 | 58.592 | 57.5675 | 56.5379 | 55.8379 | 54.6828 | 53.495 | 52.2777 | 50.6368 | 49.6971 | 45.2797 | 42.8022 | 41.4858
|  | AMESBURY BSP | HT |  |  |  |  | 60.655 | 59.8254 | 59.055 | 58.1866 | 57.2805 | 56.206 | 54.6978 | 53.2121 | 52.3142 | 45.2121 | 41.2478 | 39.0988 | 68.295 | 67.8522 | 67.442 | 66.9715 | 66.4828 | 65.9828 | 65.1991 | 64.4328 | 64.0522 | 60.4603 | 58.4593 | 57.3175 | 59.2807 | 58.4889 | 57.7868 | 56.9583 | 56.0981 | 55.2236 | 53.8328 | 52.4389 | 51.7909 | 45.5777 | 42.4103 | 40.7542
|  | AMESBURY BSP | HE |  |  |  |  | 60.7111 | 59.9356 | 59.2325 | 58.3988 | 57.5427 | 56.6356 | 55.2631 | 53.907 | 53.1846 | 46.6458 | 43.5091 | 42.0488 | 68.1695 | 67.6634 | 67.192 | 66.6358 | 66.0613 | 65.5011 | 64.6317 | 63.744 | 63.2624 | 58.2409 | 53.6573 | 47.0603 | 59.3103 | 58.5705 | 57.9236 | 57.1277 | 56.3256 | 55.5787 | 54.3001 | 53.0185 | 52.5195 | 46.8338 | 44.3858 | 43.2256
|  | AMESBURY BSP | CF |  |  |  |  | 61.0897 | 60.5886 | 60.0662 | 59.5713 | 58.9611 | 58.2999 | 57.557 | 57.0988 | 56.2805 | 52.2091 | 47.955 | 44.0713 | 68.3256 | 67.946 | 67.5277 | 67.1103 | 66.5787 | 65.9797 | 65.292 | 64.7909 | 64.0124 | 59.3817 | 51.4736 | 37.9726 | 59.6348 | 59.1522 | 58.6399 | 58.1726 | 57.5613 | 56.9277 | 56.1899 | 55.8052 | 54.9899 | 51.293 | 47.7766 | 44.8113
MELKSHAM GSP | ANDOVER BSP | ANDOVER BSP | MINIMUM HEADROOM | SU 35334 46598 | NO | NO | 23.985 | 33.7638 | 31.3454 | 28.6719 | 140.7597 | 137.5699 | 133.1168 | 128.0383 | 122.3495 | 118.0413 | 95.3046 | 79.6383 | 68.3883 | 47.8515 | 45.9525 | 43.8383 | 151.3556 | 148.976 | 145.9617 | 142.4576 | 137.9679 | 133.4199 | 114.2699 | 97.0893 | 68.5332 | 33.5923 | 31.4638 | 29.0801 | 137.9811 | 135.1474 | 131.1617 | 126.4801 | 121.0903 | 116.323 | 93.2148 | 79.3576 | 69.2015
|  | ANDOVER BSP | EE |  |  |  |  | 33.7638 | 31.3454 | 28.6719 | 140.7597 | 137.5699 | 133.1168 | 128.0383 | 122.3495 | 118.0413 | 98.3842 | 82.2648 | 72.6199 | 47.8515 | 45.9525 | 43.8383 | 151.3556 | 148.976 | 145.9617 | 142.4576 | 138.2515 | 135.2525 | 120.1362 | 101.5811 | 81.726 | 33.5923 | 31.4638 | 29.0801 | 137.9811 | 135.1474 | 131.1617 | 126.4801 | 121.0903 | 117.1607 | 98.926 | 82.9556 | 73.9699
|  | ANDOVER BSP | HT |  |  |  |  | 34.6944 | 32.5934 | 30.1546 | 142.5393 | 138.773 | 134.123 | 129.4281 | 125.5597 | 120.7321 | 97.5964 | 79.6383 | 68.3883 | 49.0525 | 47.6423 | 45.927 | 154.0076 | 151.2076 | 148.3505 | 145.4189 | 143.323 | 140.2117 | 125.9689 | 113.5546 | 105.7097 | 34.4464 | 32.5628 | 30.3525 | 139.5576 | 136.0362 | 131.774 | 127.4168 | 123.9699 | 119.4372 | 97.8179 | 80.2087 | 69.2015
|  | ANDOVER BSP | HE |  |  |  |  | 34.874 | 32.7158 | 30.1352 | 142.5209 | 138.5883 | 134.4699 | 130.1362 | 124.3342 | 118.8444 | 95.3046 | 80.3076 | 70.4781 | 48.8556 | 47.1444 | 44.9964 | 152.6485 | 149.225 | 146.2025 | 143.0199 | 137.9679 | 133.4199 | 114.2699 | 97.0893 | 74.676 | 34.6005 | 32.626 | 30.2056 | 139.2934 | 135.4607 | 131.676 | 127.6128 | 121.724 | 116.323 | 93.2148 | 79.3576 | 69.477
|  | ANDOVER BSP | CF |  |  |  |  | 36.1515 | 34.9668 | 33.4566 | 146.8964 | 145.1015 | 143.2842 | 141.4474 | 139.6515 | 137.3781 | 119.7576 | 105.0893 | 91.7383 | 49.5362 | 48.4903 | 47.1454 | 155.3025 | 153.4842 | 151.4964 | 149.4821 | 147.4628 | 145.0515 | 127.9005 | 104.5485 | 68.5332 | 35.7485 | 34.7281 | 33.3852 | 143.4036 | 141.7648 | 140.074 | 138.3985 | 136.7464 | 134.677 | 118.9036 | 103.7148 | 91.3679
MANNINGTON GSP | ARNEWOOD BSP | ARNEWOOD BSP | MINIMUM HEADROOM | SZ 26094 97294 | NO | NO | 7.611 | 17.8126 | 16.0187 | 14.2524 | 80.8192 | 78.2539 | 74.1845 | 70.207 | 65.9345 | 62.81 | 46.6325 | 34.1416 | 27.0621 | 32.6779 | 31.281 | 29.9544 | 96.9804 | 94.9549 | 92.2151 | 89.4845 | 86.4274 | 84.3192 | 73.3008 | 59.9457 | 26.8335 | 20.4269 | 18.7096 | 17.0544 | 83.7508 | 81.2804 | 77.5121 | 73.8294 | 69.8039 | 67.0386 | 53.2927 | 42.2059 | 36.3396
|  | ARNEWOOD BSP | EE |  |  |  |  | 17.8126 | 16.0187 | 14.2524 | 80.8192 | 78.2539 | 74.1845 | 70.207 | 65.9345 | 62.81 | 47.6416 | 36.7927 | 28.211 | 32.6779 | 31.281 | 29.9544 | 96.9804 | 94.9549 | 92.2151 | 89.4845 | 86.4274 | 84.3192 | 73.3008 | 61.5049 | 44.0906 | 20.4269 | 18.7096 | 17.0544 | 83.7508 | 81.2804 | 77.5121 | 73.8294 | 69.8039 | 67.0386 | 54.061 | 44.5855 | 37.3325
|  | ARNEWOOD BSP | HT |  |  |  |  | 18.8259 | 17.2279 | 15.4014 | 82.2243 | 80.3529 | 76.9988 | 73.2172 | 69.308 | 65.3937 | 46.6325 | 34.1416 | 27.0621 | 33.9851 | 32.9749 | 31.8075 | 99.3549 | 98.2651 | 96.6161 | 94.5049 | 92.2804 | 89.9978 | 80.0468 | 74.3692 | 71.5416 | 21.6024 | 20.0922 | 18.383 | 85.3753 | 83.6988 | 80.7968 | 77.358 | 73.7896 | 70.1804 | 53.2927 | 42.2059 | 36.3396
|  | ARNEWOOD BSP | HE |  |  |  |  | 19.0687 | 17.5075 | 15.8483 | 82.8263 | 81.0978 | 78.3539 | 75.1396 | 71.8049 | 68.4825 | 52.4212 | 41.258 | 35.8774 | 33.8085 | 32.5912 | 31.3106 | 98.6876 | 97.4049 | 95.6753 | 93.4365 | 91.0355 | 88.5478 | 75.7172 | 63.4304 | 47.3335 | 21.7993 | 20.3218 | 18.7453 | 85.8814 | 84.3284 | 81.9478 | 78.9896 | 75.9121 | 72.81 | 58.357 | 48.5947 | 44.1651
|  | ARNEWOOD BSP | CF |  |  |  |  | 20.1738 | 19.3004 | 18.1953 | 85.6804 | 84.7284 | 83.7049 | 82.5702 | 80.9784 | 79.2957 | 68.5437 | 56.7416 | 45.8437 | 34.3177 | 33.4391 | 32.3687 | 99.8549 | 98.808 | 97.6151 | 96.2468 | 94.4406 | 92.5008 | 79.609 | 59.9457 | 26.8335 | 22.7993 | 21.934 | 20.8657 | 88.3896 | 87.5274 | 86.61 | 85.5733 | 84.0314 | 82.409 | 72.2304 | 61.8508 | 52.5794
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | BASINGSTOKE (T1A & T2A) BSP | MINIMUM HEADROOM | SU 65132 52710 | YES | NO | 19.406 | 53.9935 | 53.1537 | 52.2639 | 51.4088 | 50.2588 | 48.9078 | 46.8496 | 44.6588 | 42.7323 | 35.3568 | 31.0455 | 28.8353 | 47.0343 | 46.3945 | 45.7792 | 45.3425 | 44.5455 | 43.7404 | 42.421 | 41.0027 | 39.8435 | 34.5955 | 29.3047 | 15.9262 | 50.1608 | 49.4455 | 48.7486 | 48.2762 | 47.2527 | 45.9802 | 44.219 | 42.4231 | 40.8741 | 34.4343 | 29.8915 | 27.3731
|  | BASINGSTOKE (T1A & T2A) BSP | EE |  |  |  |  | 53.9935 | 53.1537 | 52.2639 | 51.4088 | 50.2588 | 48.9078 | 46.8496 | 44.6588 | 42.7323 | 35.568 | 32.47 | 30.0517 | 47.0343 | 46.3945 | 45.7792 | 45.3425 | 44.5455 | 43.7404 | 42.421 | 41.0027 | 39.8435 | 34.5955 | 29.7894 | 22.7496 | 50.1608 | 49.4455 | 48.7486 | 48.2762 | 47.2527 | 45.9802 | 44.219 | 42.4231 | 40.8741 | 34.6721 | 30.721 | 27.8006
|  | BASINGSTOKE (T1A & T2A) BSP | HT |  |  |  |  | 54.4496 | 53.9762 | 53.3098 | 52.4557 | 51.4149 | 50.0792 | 48.2364 | 46.3394 | 44.368 | 35.7598 | 31.3466 | 28.8843 | 47.3853 | 47.0731 | 46.7078 | 46.1762 | 45.5506 | 44.7813 | 43.6751 | 42.7894 | 41.7221 | 37.0721 | 35.1006 | 33.9262 | 50.4751 | 49.9557 | 49.4098 | 48.7027 | 47.8904 | 46.5486 | 44.8251 | 43.3445 | 41.6945 | 34.4343 | 29.8915 | 27.3731
|  | BASINGSTOKE (T1A & T2A) BSP | HE |  |  |  |  | 54.5047 | 53.9221 | 53.2353 | 52.4435 | 51.4598 | 50.2966 | 48.5884 | 46.667 | 44.5731 | 35.3568 | 31.0455 | 28.8353 | 47.3527 | 46.9343 | 46.4955 | 45.9588 | 45.3364 | 44.7098 | 43.6282 | 42.669 | 41.4659 | 35.6751 | 30.7466 | 24.1853 | 50.5731 | 50.0496 | 49.5466 | 48.9629 | 48.2884 | 47.317 | 45.7568 | 44.1731 | 42.4384 | 34.4639 | 30.5078 | 28.467
|  | BASINGSTOKE (T1A & T2A) BSP | CF |  |  |  |  | 54.8394 | 54.6496 | 54.3792 | 54.0517 | 53.567 | 52.9833 | 52.1608 | 51.3476 | 50.3353 | 43.3813 | 37.2047 | 32.4272 | 47.5741 | 47.3129 | 46.9262 | 46.5466 | 46.068 | 45.5017 | 44.7557 | 44.2057 | 43.3506 | 37.3741 | 29.3047 | 15.9262 | 50.9966 | 50.7384 | 50.4159 | 50.1139 | 49.7578 | 49.3404 | 48.7639 | 48.2884 | 47.3221 | 41.1568 | 36.1343 | 31.7323
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BASINGSTOKE (T1B & T2B) BSP | MINIMUM HEADROOM | SU 65132 52711 | NO | NO | 11.527 | 53.442 | 51.492 | 49.2104 | 46.5604 | 43.8972 | 40.14 | 35.0553 | 30.2665 | 25.492 | 5.6339 | -5.6345 | -11.9284 | 57.4352 | 56.0678 | 54.4576 | 52.6719 | 50.9658 | 48.5576 | 45.3984 | 42.5719 | 39.9576 | 26.5556 | 15.6209 | -13.0965 | 49.0923 | 47.3454 | 45.2903 | 42.9229 | 40.5678 | 37.1382 | 32.5443 | 28.4525 | 24.7607 | 7.2943 | -2.1802 | -7.2873
|  | BASINGSTOKE (T1B & T2B) BSP | EE |  |  |  |  | 53.442 | 51.492 | 49.2104 | 46.5604 | 43.8972 | 40.14 | 35.0553 | 30.2665 | 25.9625 | 7.1808 | -3.5814 | -11.0967 | 57.4352 | 56.0678 | 54.4576 | 52.6719 | 50.9658 | 48.5576 | 45.3984 | 42.5719 | 39.9576 | 26.5556 | 16.0137 | 0.90148 | 49.0923 | 47.3454 | 45.2903 | 42.9229 | 40.5678 | 37.1382 | 32.5443 | 28.4525 | 24.7607 | 8.4015 | -0.35669 | -6.5975
|  | BASINGSTOKE (T1B & T2B) BSP | HT |  |  |  |  | 54.0625 | 52.2298 | 50.541 | 48.3043 | 45.5757 | 40.3359 | 35.1778 | 30.3992 | 25.492 | 5.6339 | -5.6345 | -11.9284 | 58.3188 | 57.2596 | 56.3903 | 55.18 | 53.6086 | 50.9627 | 48.2454 | 45.7484 | 42.9545 | 32.08 | 26.979 | 24.4505 | 49.7239 | 48.1137 | 46.6525 | 44.7056 | 42.2637 | 37.7739 | 33.3005 | 29.1505 | 24.8015 | 7.2943 | -2.1802 | -7.2873
|  | BASINGSTOKE (T1B & T2B) BSP | HE |  |  |  |  | 54.1686 | 52.4257 | 50.84 | 48.7145 | 46.2247 | 43.3002 | 39.4747 | 35.6808 | 31.8288 | 13.5216 | 1.4961 | -3.5488 | 58.0739 | 56.8994 | 55.88 | 54.526 | 52.9188 | 51.0474 | 48.6382 | 46.279 | 43.7015 | 29.8168 | 18.4219 | 4.2576 | 49.8117 | 48.277 | 46.9117 | 45.0678 | 42.8831 | 40.2627 | 36.8852 | 33.5821 | 30.1535 | 13.9127 | 4.1352 | 0.065763
|  | BASINGSTOKE (T1B & T2B) BSP | CF |  |  |  |  | 55.6247 | 54.7747 | 53.8043 | 52.8859 | 51.0747 | 48.6267 | 46.7512 | 45.0298 | 43.3206 | 30.792 | 15.3818 | 5.441 | 58.6923 | 57.9158 | 57.0188 | 56.2831 | 54.8984 | 53.0688 | 51.3637 | 49.6882 | 47.9015 | 35.4535 | 15.6209 | -13.0965 | 51.0484 | 50.276 | 49.4035 | 48.6413 | 47.1076 | 45.0668 | 43.3892 | 41.8331 | 40.2188 | 28.9637 | 15.7352 | 7.2219
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | BASINGSTOKE (T3 & T4) BSP | MINIMUM HEADROOM | SU 65132 52712 | NO | NO | 35.672 | 60.0662 | 58.4111 | 56.2897 | 54.2989 | 51.7887 | 49.2295 | 45.9173 | 42.4764 | 39.5254 | 27.7152 | 21.2866 | 17.3122 | 62.8295 | 61.6326 | 60.1815 | 58.8836 | 57.1734 | 55.5122 | 53.3173 | 51.0244 | 49.1193 | 40.5928 | 31.7693 | 10.7091 | 57.6683 | 56.2193 | 54.3846 | 52.6887 | 50.4611 | 48.202 | 45.2968 | 42.2856 | 39.6999 | 29.1642 | 23.753 | 20.3805
|  | BASINGSTOKE (T3 & T4) BSP | EE |  |  |  |  | 60.0662 | 58.4111 | 56.2897 | 54.2989 | 51.7887 | 49.2295 | 45.9173 | 42.4764 | 39.5254 | 27.7152 | 21.8234 | 17.3591 | 62.8295 | 61.6326 | 60.1815 | 58.8836 | 57.1734 | 55.5122 | 53.3173 | 51.0244 | 49.1193 | 40.5928 | 33.6428 | 22.7346 | 57.6683 | 56.2193 | 54.3846 | 52.6887 | 50.4611 | 48.202 | 45.2968 | 42.2856 | 39.6999 | 29.1642 | 24.1795 | 20.3805
|  | BASINGSTOKE (T3 & T4) BSP | HT |  |  |  |  | 60.5948 | 59.1754 | 57.3948 | 55.4999 | 53.4377 | 50.6244 | 47.9264 | 44.9162 | 42.4683 | 28.5132 | 21.2866 | 17.3122 | 63.4611 | 62.5928 | 61.5601 | 60.4183 | 59.2244 | 57.7377 | 56.356 | 54.7193 | 53.4387 | 46.0193 | 42.4785 | 40.8703 | 58.2111 | 56.9968 | 55.5009 | 53.8315 | 52.0193 | 49.603 | 47.306 | 44.6448 | 42.504 | 30.1611 | 23.753 | 20.453
|  | BASINGSTOKE (T3 & T4) BSP | HE |  |  |  |  | 60.6213 | 59.1683 | 57.3193 | 55.3856 | 53.2254 | 50.8213 | 48.3234 | 45.4428 | 42.806 | 29.2417 | 22.7999 | 20.4417 | 63.2836 | 62.252 | 61.0224 | 59.7224 | 58.2683 | 56.7101 | 55.1264 | 53.2244 | 51.4979 | 41.6071 | 33.9499 | 23.9724 | 58.2203 | 56.9683 | 55.3938 | 53.7142 | 51.804 | 49.6907 | 47.5254 | 45.003 | 42.7244 | 30.8387 | 25.1152 | 23.105
|  | BASINGSTOKE (T3 & T4) BSP | CF |  |  |  |  | 61.5458 | 60.9968 | 60.1254 | 59.0713 | 57.6458 | 56.1264 | 54.3917 | 52.5968 | 51.0275 | 39.6928 | 32.6693 | 26.3336 | 63.7632 | 63.2224 | 62.4387 | 61.5193 | 60.3509 | 59.0713 | 57.602 | 56.0683 | 54.6917 | 44.5122 | 31.7693 | 10.7091 | 59.0326 | 58.5468 | 57.7805 | 56.8611 | 55.6407 | 54.3632 | 52.8601 | 51.2958 | 49.9662 | 40.1285 | 33.7326 | 28.1897
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH BSP | MINIMUM HEADROOM | SP5972023735 | NO | NO | 184.689 | -63.9366 | -65.5172 | -27.8914 | -29.7037 | -32.5792 | -36.9986 | -41.2557 | -45.2761 | -48.5047 | -61.3833 | -70.1465 | -74.8741 | -58.8496 | -59.8996 | -24.3108 | -25.321 | -27.3527 | -30.3282 | -33.1976 | -35.9578 | -37.9129 | -45.2976 | -50.9639 | -61.2169 | -66.6027 | -67.9363 | -32.1843 | -33.7241 | -36.5578 | -40.5363 | -44.4241 | -48.1445 | -50.8874 | -61.921 | -69.4812 | -73.42
|  | BICESTER NORTH BSP | EE |  |  |  |  | -63.9366 | -65.5172 | -27.8914 | -29.7037 | -32.5792 | -36.9986 | -41.2557 | -45.2761 | -48.5047 | -61.12 | -69.1945 | -74.2802 | -58.8496 | -59.8996 | -24.3108 | -25.321 | -27.3527 | -30.3282 | -33.1976 | -35.9578 | -37.9129 | -45.2976 | -50.9639 | -57.4822 | -66.6027 | -67.9363 | -32.1843 | -33.7241 | -36.5578 | -40.5363 | -44.4241 | -48.1445 | -50.8874 | -61.7537 | -68.7047 | -72.9904
|  | BICESTER NORTH BSP | HT |  |  |  |  | -63.4121 | -64.7641 | -27.1976 | -29.2455 | -31.7496 | -36.068 | -40.4506 | -44.4751 | -47.7322 | -61.3833 | -70.1465 | -74.8741 | -58.2506 | -58.9853 | -23.2904 | -24.3863 | -26.0047 | -28.9241 | -31.869 | -34.4976 | -36.3139 | -42.9537 | -46.9761 | -49.1363 | -66.1384 | -67.2741 | -31.5037 | -33.2302 | -35.5914 | -39.5476 | -43.5139 | -47.1455 | -49.9935 | -61.921 | -69.4812 | -73.42
|  | BICESTER NORTH BSP | HE |  |  |  |  | -63.3427 | -64.6386 | -27.0067 | -28.9761 | -31.3455 | -34.9578 | -38.6802 | -42.2016 | -45.4669 | -58.5425 | -66.6414 | -70.0149 | -58.3761 | -59.171 | -23.5374 | -24.6731 | -26.2629 | -28.7455 | -31.3149 | -33.7476 | -35.9251 | -44.0618 | -49.8404 | -55.5374 | -66.0863 | -67.1751 | -31.3557 | -33.0169 | -35.2404 | -38.522 | -41.8649 | -45.0292 | -47.9333 | -59.4669 | -66.3914 | -69.1455
|  | BICESTER NORTH BSP | CF |  |  |  |  | -62.4243 | -63.1202 | -24.5812 | -25.5078 | -28.0404 | -30.2629 | -32.8874 | -35.0537 | -37.3322 | -48.5843 | -57.5394 | -64.6945 | -57.9425 | -58.47 | -22.4312 | -23.07 | -25.3843 | -27.0618 | -28.972 | -30.5476 | -32.2129 | -40.6639 | -49.2833 | -61.2169 | -65.2863 | -65.8669 | -29.2986 | -30.0782 | -32.7302 | -34.6363 | -36.8761 | -38.7067 | -40.6414 | -50.4527 | -58.1731 | -64.5037
BOTLEY WOOD GSP | BOTLEY WOOD BSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU 54073 09759 | NO | NO | 20.306 | 77.6259 | 75.8759 | 74.5218 | 72.8126 | 71.08 | 69.4565 | 67.5157 | 65.632 | 64.1616 | 56.78 | 51.5585 | 48.6677 | 81.0374 | 79.8904 | 79.1098 | 78.0731 | 77.0016 | 75.9608 | 74.6057 | 73.2884 | 72.2445 | 67.1169 | 60.9955 | 46.4343 | 76.2129 | 74.7006 | 73.5629 | 72.0772 | 70.4976 | 69.0772 | 67.2394 | 65.4639 | 64.1629 | 57.82 | 53.2374 | 50.7598
|  | BOTLEY WOOD BSP | EE |  |  |  |  | 77.6259 | 75.8759 | 74.5218 | 72.8126 | 71.08 | 69.4565 | 67.5157 | 65.632 | 64.1616 | 57.3412 | 52.6769 | 49.2534 | 81.0374 | 79.8904 | 79.1098 | 78.0731 | 77.0016 | 75.9608 | 74.6057 | 73.2884 | 72.2445 | 67.1169 | 61.9731 | 54.5425 | 76.2129 | 74.7006 | 73.5629 | 72.0772 | 70.4976 | 69.0772 | 67.2394 | 65.4639 | 64.1629 | 58.2343 | 54.1986 | 51.2516
|  | BOTLEY WOOD BSP | HT |  |  |  |  | 77.7657 | 76.3443 | 74.8575 | 73.2392 | 71.3504 | 69.784 | 67.984 | 66.2075 | 64.8208 | 56.78 | 51.5585 | 48.6677 | 81.3108 | 80.5659 | 79.7976 | 78.9547 | 77.8588 | 77.0404 | 76.0088 | 74.9843 | 74.2823 | 70.119 | 67.6557 | 66.3251 | 76.3782 | 75.1884 | 73.9251 | 72.5343 | 70.8608 | 69.4986 | 67.8772 | 66.2649 | 65.0384 | 57.82 | 53.2374 | 50.7598
|  | BOTLEY WOOD BSP | HE |  |  |  |  | 78.0351 | 76.4983 | 75.0106 | 73.4228 | 72.1218 | 70.5636 | 68.9524 | 67.3555 | 66.1075 | 58.2626 | 53.6187 | 51.3289 | 81.3629 | 80.3802 | 79.4935 | 78.5527 | 77.8251 | 76.771 | 75.6098 | 74.4394 | 73.5241 | 67.7374 | 62.2874 | 55.2139 | 76.6169 | 75.3108 | 74.0445 | 72.6761 | 71.571 | 70.1823 | 68.7169 | 67.2608 | 66.1404 | 58.3669 | 54.1067 | 52.0016
|  | BOTLEY WOOD BSP | CF |  |  |  |  | 78.7698 | 77.7412 | 76.5738 | 75.4575 | 74.3381 | 73.6106 | 73.0432 | 72.132 | 71.2392 | 66.2269 | 60.1463 | 55.1514 | 81.7047 | 81.0149 | 80.1802 | 79.4333 | 78.6363 | 77.9414 | 77.3037 | 76.3669 | 75.4129 | 69.6567 | 60.9955 | 46.4343 | 77.2618 | 76.4159 | 75.4282 | 74.4812 | 73.5149 | 72.8823 | 72.3925 | 71.5649 | 70.7169 | 66.022 | 60.0792 | 55.4904
MANNINGTON GSP | BOURNEMOUTH BSP | BOURNEMOUTH BSP | MINIMUM HEADROOM | SZ 06265 92437 | NO | NO | 31.19 | -66.4466 | -70.5701 | -76.2497 | -82.2211 | -88.0578 | -96.5231 | -105.9119 | -115.0956 | -122.3425 | -153.9119 | -179.5435 | -189.269 | -34.3037 | -37.6639 | -42.2935 | -47.217 | -52.017 | -58.4354 | -65.8242 | -73.2578 | -79.0946 | -108.5201 | -149.3548 | -248.7323 | -62.6884 | -66.2272 | -71.2048 | -76.8895 | -82.3639 | -90.3109 | -99.2833 | -108.0864 | -114.717 | -142.8333 | -165.0354 | -173.3211
|  | BOURNEMOUTH BSP | EE |  |  |  |  | -66.4466 | -70.5701 | -76.2497 | -82.2211 | -88.0578 | -96.5231 | -105.9119 | -115.0956 | -122.3425 | -153.9119 | -173.366 | -184.9078 | -34.3037 | -37.6639 | -42.2935 | -47.217 | -52.017 | -58.4354 | -65.8242 | -73.2578 | -79.0946 | -108.5201 | -139.6037 | -188.4915 | -62.6884 | -66.2272 | -71.2048 | -76.8895 | -82.3639 | -90.3109 | -99.2833 | -108.0864 | -114.717 | -142.8333 | -159.765 | -169.9007
|  | BOURNEMOUTH BSP | HT |  |  |  |  | -63.3364 | -67.3058 | -71.766 | -75.9313 | -81.1344 | -88.2823 | -95.0405 | -102.9762 | -111.1456 | -152.7262 | -179.5435 | -189.269 | -30.6282 | -33.2578 | -36.1068 | -38.7639 | -42.2476 | -46.4854 | -50.366 | -55.3588 | -60.5395 | -85.1793 | -99.3833 | -103.9435 | -59.915 | -63.3578 | -67.1966 | -70.8027 | -75.3507 | -81.7037 | -87.8078 | -95.1395 | -102.7017 | -140.8895 | -165.0354 | -173.3211
|  | BOURNEMOUTH BSP | HE |  |  |  |  | -63.1905 | -66.8078 | -70.8415 | -74.9333 | -79.8017 | -85.8915 | -91.8466 | -98.1966 | -105.1486 | -138.2527 | -158.2895 | -165.1517 | -31.5405 | -34.5588 | -37.7772 | -41.1109 | -45.1793 | -49.8793 | -54.5864 | -59.8333 | -65.7507 | -98.5272 | -131.2354 | -177.6364 | -59.8252 | -63.0027 | -66.5139 | -70.0823 | -74.3701 | -79.7997 | -85.116 | -90.9946 | -97.4864 | -127.965 | -145.668 | -151.4201
|  | BOURNEMOUTH BSP | CF |  |  |  |  | -60.5803 | -62.7323 | -65.2374 | -67.7507 | -70.4486 | -73.2619 | -76.5252 | -79.6711 | -82.8639 | -105.3599 | -130.1997 | -152.9986 | -30.2578 | -32.5976 | -35.2742 | -38.0588 | -41.2231 | -45.0201 | -49.4578 | -53.9119 | -58.6119 | -92.8976 | -149.3548 | -248.7323 | -57.4854 | -59.3599 | -61.5537 | -63.7272 | -66.0262 | -68.417 | -71.2435 | -74.2027 | -77.2752 | -98.7476 | -120.9456 | -141.2027
FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL BSP | MINIMUM HEADROOM | SU 86026 69422 | NO | NO | 75.816 | 64.1289 | 59.3503 | 55.6727 | 50.1799 | 44.4983 | 36.1901 | 26.9289 | 17.7472 | 10.8615 | -19.564 | -43.7222 | -56.6762 | 84.7676 | 81.2625 | 78.7452 | 74.7156 | 70.6666 | 64.5564 | 57.7401 | 50.9095 | 45.7666 | 21.6156 | -3.2977 | -69.815 | 60.9146 | 56.5932 | 53.3503 | 48.3462 | 43.2176 | 35.4074 | 26.7268 | 18.1789 | 11.7789 | -15.7926 | -37.8589 | -49.2732
|  | BRACKNELL BSP | EE |  |  |  |  | 64.1289 | 59.3503 | 55.6727 | 50.1799 | 44.4983 | 36.1901 | 26.9289 | 17.7472 | 10.8615 | -18.4497 | -38.1773 | -52.6558 | 84.7676 | 81.2625 | 78.7452 | 74.7156 | 70.6666 | 64.5564 | 57.7401 | 50.9095 | 45.7666 | 21.6156 | -2.2181 | -37.6752 | 60.9146 | 56.5932 | 53.3503 | 48.3462 | 43.2176 | 35.4074 | 26.7268 | 18.1789 | 11.7789 | -14.8834 | -32.3936 | -45.2568
|  | BRACKNELL BSP | HT |  |  |  |  | 66.3472 | 62.4656 | 58.1748 | 53.0074 | 48.3615 | 41.4289 | 33.7432 | 25.4911 | 17.8646 | -19.564 | -43.7222 | -56.6762 | 87.287 | 85.0197 | 82.4911 | 79.3085 | 76.686 | 72.4432 | 67.734 | 62.6248 | 57.7932 | 35.4156 | 22.2105 | 15.6381 | 63.0697 | 59.7391 | 55.9227 | 51.2921 | 47.2207 | 40.7676 | 33.6717 | 26.0554 | 18.9472 | -15.7926 | -37.8589 | -49.2732
|  | BRACKNELL BSP | HE |  |  |  |  | 66.6411 | 62.8707 | 58.784 | 54.2544 | 49.736 | 43.6748 | 36.7748 | 29.583 | 23.135 | -8.017 | -28.7752 | -38.5844 | 86.7248 | 84.084 | 81.2125 | 78.0176 | 74.8799 | 70.5146 | 65.5534 | 60.3391 | 55.4095 | 28.1697 | 3.0962 | -30.7099 | 63.2993 | 60.0534 | 56.4197 | 52.3656 | 48.3993 | 42.8176 | 36.5013 | 29.9574 | 24.0278 | -4.7875 | -23.3405 | -32.1936
|  | BRACKNELL BSP | CF |  |  |  |  | 68.8881 | 66.1574 | 63.5809 | 60.4717 | 56.8697 | 54.037 | 50.2881 | 46.5125 | 42.5768 | 20.5809 | -0.8895 | -20.0568 | 87.7881 | 85.5513 | 83.3748 | 80.784 | 77.687 | 74.5656 | 70.6483 | 66.6717 | 62.3309 | 35.7217 | -3.2977 | -69.815 | 65.3789 | 63.0564 | 60.8044 | 58.0758 | 54.8921 | 52.2932 | 48.8574 | 45.4146 | 41.7513 | 21.3523 | 1.884 | -15.1599
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | BURGHFIELD (MAIN) BSP | MINIMUM HEADROOM | SU 69442 70509 | NO | NO | 44.59 | 5.4964 | 2.7515 | -0.17706 | -3.3607 | -7.2485 | -14.473 | -20.0342 | -25.4934 | -29.5342 | -50.4016 | -63.0852 | -69.626 | 16.964 | 14.7599 | 12.3824 | 9.8416 | 6.8518 | 0.99461 | -3.3115 | -7.6789 | -10.9952 | -30.138 | -52.036 | -98.7299 | 2.8762 | 0.39665 | -2.236 | -5.0217 | -200.8727 | -207.4217 | -211.8533 | -216.2901 | -221.1227 | -243.486 | -256.2431 | -261.7687
|  | BURGHFIELD (MAIN) BSP | EE |  |  |  |  | 5.4964 | 2.7515 | -0.17706 | -3.3607 | -7.2485 | -14.473 | -20.0342 | -25.4934 | -29.5342 | -50.4016 | -61.6669 | -68.9016 | 16.964 | 14.7599 | 12.3824 | 9.8416 | 6.8518 | 0.99461 | -3.3115 | -7.6789 | -10.9952 | -30.138 | -46.4033 | -70.2299 | 2.8762 | 0.39665 | -2.236 | -5.0217 | -8.5115 | -15.5829 | -20.685 | -25.7462 | -29.6748 | -49.8891 | -60.338 | -66.5217
|  | BURGHFIELD (MAIN) BSP | HT |  |  |  |  | 6.7821 | 4.5678 | 2.1903 | -0.75869 | -4.2179 | -10.7791 | -15.4832 | -20.1056 | -25.1567 | -49.2281 | -63.0852 | -69.626 | 18.4844 | 16.9334 | 15.362 | 13.4028 | 11.1375 | 6.1477 | 3.1273 | 0.045633 | -3.4033 | -18.4238 | -25.6074 | -28.5156 | 21.0099 | 18.9681 | 16.815 | 14.1518 | -200.8727 | -207.4217 | -211.8533 | -216.2901 | -221.1227 | -243.486 | -256.2431 | -261.7687
|  | BURGHFIELD (MAIN) BSP | HE |  |  |  |  | 6.6801 | 4.5066 | 2.1597 | -0.34033 | -3.6158 | -9.8199 | -14.1873 | -18.3913 | -22.7995 | -46.2281 | -58.6771 | -63.5138 | 17.862 | 15.9946 | 14.066 | 12.1681 | 9.6681 | 4.3518 | 0.9742 | -2.4442 | -6.1789 | -28.4136 | -45.7707 | -68.4748 | 3.866 | 1.8354 | -0.30743 | -2.4503 | -5.4299 | -11.6136 | -15.6952 | -19.685 | -23.8993 | -46.287 | -57.7156 | -61.7258
|  | BURGHFIELD (MAIN) BSP | CF |  |  |  |  | 8.2617 | 6.8025 | 5.0678 | 3.8638 | 1.6699 | -2.3199 | -4.1771 | -6.626 | -8.9832 | -24.6464 | -41.3199 | -52.4322 | 18.6375 | 17.066 | 15.3211 | 14.0762 | 11.964 | 7.5048 | 5.1885 | 2.3518 | -0.57682 | -21.1789 | -52.036 | -98.7299 | 5.315 | 3.9375 | 2.366 | 1.3864 | -0.50131 | -4.6033 | -6.3074 | -8.5931 | -10.8176 | -25.9605 | -41.4707 | -51.736
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | BURGHFIELD (RESERVE) BSP | MINIMUM HEADROOM | SU 69442 70509 | NO | NO | 19.667 | 50.2081 | 48.2173 | 46.0101 | 43.3765 | 41.304 | 38.154 | 34.7061 | 30.854 | 27.3601 | -86.7735 | -94.5684 | -96.8541 | 59.4992 | 57.8349 | 56.0543 | 53.9941 | 52.4339 | 50.2084 | 47.6981 | 44.8369 | 42.5492 | -91.1355 | -99.5019 | -126.5855 | 49.141 | 47.2339 | 45.1859 | 42.8237 | 40.39 | 37.1981 | 33.4104 | 29.642 | 26.3114 | -111.257 | -118.5753 | -120.5957
|  | BURGHFIELD (RESERVE) BSP | EE |  |  |  |  | 50.2081 | 48.2173 | 46.0101 | 43.3765 | 41.304 | 38.154 | 34.7061 | 30.854 | 27.3601 | -83.499 | -90.8031 | -96.1929 | 59.4992 | 57.8349 | 56.0543 | 53.9941 | 52.4339 | 50.2084 | 47.6981 | 44.8369 | 42.5492 | -88.8019 | -98.7488 | -112.1712 | 49.141 | 47.2339 | 45.1859 | 42.8237 | 40.39 | 37.1981 | 33.4104 | 29.642 | 26.3114 | -108.0121 | -114.2488 | -117.5559
|  | BURGHFIELD (RESERVE) BSP | HT |  |  |  |  | 51.305 | 49.6499 | 47.9204 | 45.8704 | 43.7101 | 40.7826 | 37.851 | 34.8316 | 31.7214 | -80.9694 | -90.9817 | -95.9184 | 60.9032 | 59.7849 | 58.6032 | 57.2043 | 55.6675 | 53.8798 | 52.0941 | 49.8441 | 47.3175 | -85.0488 | -90.6049 | -92.8447 | 50.34 | 48.8032 | 47.1757 | 45.2737 | 43.2165 | 40.5063 | 37.7788 | 34.9726 | 31.943 | -104.7059 | -113.4631 | -117.511
|  | BURGHFIELD (RESERVE) BSP | HE |  |  |  |  | 51.2622 | 49.5867 | 47.8265 | 45.8897 | 43.6652 | 40.951 | 37.6428 | 33.6204 | 29.6112 | -86.7735 | -94.5684 | -96.8541 | 60.5563 | 59.2441 | 57.8573 | 56.3492 | 54.5237 | 52.4961 | 50.1022 | 47.14 | 44.1879 | -91.1355 | -98.1416 | -110.659 | 50.2777 | 48.7145 | 47.0553 | 45.241 | 42.8114 | 39.7747 | 36.1471 | 32.3053 | 28.4777 | -111.257 | -118.5753 | -120.5957
|  | BURGHFIELD (RESERVE) BSP | CF |  |  |  |  | 52.4918 | 51.3908 | 50.2591 | 49.0897 | 47.9673 | 46.7969 | 45.2959 | 43.5316 | 42.404 | -68.0399 | -80.7378 | -89.5194 | 61.2563 | 60.2349 | 59.1655 | 58.0502 | 56.8737 | 55.4553 | 53.7655 | 51.8828 | 50.5563 | -82.5937 | -99.5019 | -126.5855 | 51.4328 | 50.4053 | 49.3226 | 48.2165 | 47.1441 | 45.9869 | 44.5716 | 42.9665 | 41.041 | -93.4651 | -105.5304 | -113.7825
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY (MAIN) BSP | MINIMUM HEADROOM | SU 86530 59483 | NO | NO | 18.185 | 29.8216 | 27.5594 | 24.6614 | 21.1339 | 17.6155 | 12.6002 | 7.0145 | 1.4155 | -2.6753 | -24.2722 | -40.3508 | -49.0529 | 45.0402 | 43.4484 | 41.38 | 38.8351 | 36.2576 | 32.8056 | 28.8219 | 24.7504 | 21.8994 | 6.3035 | -13.9455 | -60.1771 | 30.9443 | 28.9576 | 26.3219 | 23.0229 | 19.7851 | 15.1372 | 9.8923 | 4.6188 | 0.9831 | -17.2118 | -30.8567 | -38.5149
|  | CAMBERLEY (MAIN) BSP | EE |  |  |  |  | 29.8216 | 27.5594 | 24.6614 | 21.1339 | 17.6155 | 12.6002 | 7.0145 | 1.4155 | -2.6753 | -22.7304 | -36.8508 | -47.5416 | 45.0402 | 43.4484 | 41.38 | 38.8351 | 36.2576 | 32.8056 | 28.8219 | 24.7504 | 21.8994 | 6.3035 | -9.7598 | -33.6557 | 30.9443 | 28.9576 | 26.3219 | 23.0229 | 19.7851 | 15.1372 | 9.8923 | 4.6188 | 0.9831 | -16.1791 | -27.8251 | -37.3159
|  | CAMBERLEY (MAIN) BSP | HT |  |  |  |  | 31.2124 | 28.6767 | 26.039 | 23.1135 | 19.7135 | 15.4165 | 10.4869 | 5.8278 | 0.75122 | -24.2722 | -40.3508 | -49.0529 | 46.7402 | 45.2586 | 43.8056 | 42.1525 | 40.1137 | 37.8749 | 35.08 | 32.4719 | 29.526 | 16.0719 | 8.6433 | 4.9433 | 32.5402 | 30.2249 | 27.93 | 25.3668 | 22.2556 | 18.4882 | 13.9994 | 9.8015 | 5.127 | -17.2118 | -30.8567 | -38.5149
|  | CAMBERLEY (MAIN) BSP | HE |  |  |  |  | 31.4757 | 28.9839 | 26.5931 | 24.038 | 20.7859 | 17.2573 | 12.9492 | 8.8676 | 4.5053 | -17.5773 | -32.4161 | -39.2947 | 46.3576 | 44.5698 | 42.9045 | 41.1382 | 38.7739 | 36.3494 | 33.277 | 30.3107 | 26.977 | 8.6127 | -8.3077 | -30.7893 | 32.7443 | 30.4535 | 28.3484 | 26.1249 | 23.1484 | 20.0249 | 16.0566 | 12.3627 | 8.2862 | -11.6842 | -23.971 | -30.0567
|  | CAMBERLEY (MAIN) BSP | CF |  |  |  |  | 33.242 | 31.7124 | 30.0655 | 28.5931 | 27.1839 | 25.5135 | 23.9073 | 21.7145 | 19.7543 | 2.9716 | -12.5029 | -26.4559 | 47.1474 | 45.8035 | 44.3229 | 42.9607 | 41.4841 | 39.5086 | 37.4892 | 34.9902 | 32.5841 | 13.3627 | -13.9455 | -60.1771 | 34.2709 | 32.8627 | 31.3209 | 30.0045 | 28.778 | 27.1658 | 25.6617 | 23.5382 | 21.6953 | 5.9841 | -7.5628 | -19.2965
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | CAMBERLEY (RESERVE) BSP | MINIMUM HEADROOM | SU 86530 59483 | NO | NO | 32.697 | 36.592 | 33.1737 | 30.2114 | 27.1818 | 23.2798 | 18.6359 | 13.9094 | 9.0706 | 5.2961 | -12.4937 | -25.2722 | -32.208 | 46.6505 | 44.1872 | 42.1219 | 39.9923 | 37.2545 | 33.8994 | 30.426 | 26.7627 | 23.9607 | 9.7454 | -7.4159 | -46.9955 | 35.1402 | 32.1117 | 29.4382 | 26.7198 | 23.1749 | 18.8413 | 14.4423 | 9.8821 | 6.478 | -10.4914 | -22.6649 | -26.7302
|  | CAMBERLEY (RESERVE) BSP | EE |  |  |  |  | 36.592 | 33.1737 | 30.2114 | 27.1818 | 23.2798 | 18.6359 | 13.9094 | 9.0706 | 5.2961 | -12.4937 | -23.1692 | -31.6294 | 46.6505 | 44.1872 | 42.1219 | 39.9923 | 37.2545 | 33.8994 | 30.426 | 26.7627 | 23.9607 | 9.7454 | -3.8791 | -24.2791 | 35.1402 | 32.1117 | 29.4382 | 26.7198 | 23.1749 | 18.8413 | 14.4423 | 9.8821 | 6.478 | -9.1414 | -18.6128 | -26.0434
|  | CAMBERLEY (RESERVE) BSP | HT |  |  |  |  | 38.0757 | 34.9155 | 32.1737 | 29.6431 | 26.5757 | 22.5145 | 18.5135 | 14.1757 | 9.7186 | -12.2498 | -25.2722 | -32.208 | 48.3505 | 46.3474 | 44.7127 | 43.3025 | 41.6331 | 39.2321 | 36.8872 | 34.2096 | 31.4137 | 18.9423 | 12.127 | 8.8331 | 36.7198 | 33.9464 | 31.4698 | 29.2627 | 26.6209 | 22.9341 | 19.3311 | 15.3372 | 11.2147 | -8.7434 | -20.5863 | -26.6434
|  | CAMBERLEY (RESERVE) BSP | HE |  |  |  |  | 37.938 | 34.7461 | 31.9329 | 29.3318 | 26.1686 | 22.4788 | 18.7839 | 14.7818 | 10.6451 | -11.2855 | -24.3406 | -28.6814 | 47.8035 | 45.5188 | 43.5576 | 41.7862 | 39.7066 | 37.0617 | 34.3658 | 31.3433 | 28.1372 | 10.7545 | -4.3577 | -23.5985 | 36.5678 | 33.7637 | 31.2249 | 28.9454 | 26.2229 | 22.8658 | 19.5239 | 15.8392 | 12.0209 | -10.4914 | -22.6649 | -26.7302
|  | CAMBERLEY (RESERVE) BSP | CF |  |  |  |  | 39.5216 | 37.1196 | 35.1849 | 33.2931 | 31.2196 | 29.2767 | 27.4665 | 25.5971 | 23.3512 | 8.6798 | -5.8855 | -18.1641 | 48.6076 | 46.6658 | 45.0913 | 43.53 | 41.8698 | 39.8331 | 37.8178 | 35.7035 | 33.1739 | 16.48 | -7.4159 | -46.9955 | 37.9831 | 35.8719 | 34.1025 | 32.4086 | 30.6525 | 28.8249 | 27.1698 | 25.4443 | 23.3066 | 9.3974 | -5.4057 | -16.7924
IVER 132KV GSP | CHALVEY BSP | CHALVEY BSP | MINIMUM HEADROOM | SU 96669 79364 | NO | YES | 45.189 | 32.4572 | 28.8796 | 25.0011 | 21.0541 | 16.5398 | 127.047 | 122.4735 | 118.2011 | 114.6653 | 102.1419 | 91.7653 | 88.6511 | 45.7368 | 43.4878 | 41.0562 | 38.6296 | 35.7306 | 141.697 | 137.6153 | 133.8286 | 130.5184 | 116.9439 | 104.3755 | 69.1592 | 33.0694 | 29.9674 | 26.5633 | 23.2041 | 19.2062 | 126.2082 | 121.5245 | 117.2235 | 113.7092 | 101.7133 | 91.7664 | 88.5041
|  | CHALVEY BSP | EE |  |  |  |  | 32.4572 | 28.8796 | 25.0011 | 21.0541 | 16.5398 | 127.047 | 122.4735 | 118.2011 | 114.6653 | 102.2357 | 95.2317 | 93.196 | 45.7368 | 43.4878 | 41.0562 | 38.6296 | 35.7306 | 141.697 | 137.6153 | 133.8286 | 130.5184 | 116.9439 | 104.3755 | 86.1388 | 33.0694 | 29.9674 | 26.5633 | 23.2041 | 19.2062 | 126.2082 | 121.5245 | 117.2235 | 113.7092 | 101.9113 | 95.5255 | 93.0602
|  | CHALVEY BSP | HT |  |  |  |  | 33.4021 | 30.1378 | 27.0255 | 23.0908 | 19.0031 | 130.4306 | 126.5878 | 122.8408 | 118.8949 | 102.1419 | 91.7653 | 88.6511 | 46.8521 | 45.0735 | 43.499 | 41.3694 | 39.1368 | 146.1939 | 143.0735 | 140.1347 | 136.9796 | 124.4266 | 117.0174 | 113.9378 | 34.0623 | 31.2949 | 28.7511 | 25.3929 | 21.8633 | 129.8664 | 125.9704 | 122.2368 | 118.2643 | 101.7133 | 91.7664 | 88.5041
|  | CHALVEY BSP | HE |  |  |  |  | 33.4704 | 30.299 | 27.3011 | 23.5919 | 19.6439 | 131.6827 | 128.5021 | 125.646 | 122.6062 | 109.8643 | 102.8102 | 99.7429 | 46.5296 | 44.598 | 42.8623 | 40.6286 | 38.2031 | 145.4439 | 142.4796 | 139.946 | 137.1735 | 122.7776 | 109.7623 | 91.0755 | 34.1133 | 31.4317 | 28.9898 | 25.8541 | 22.4888 | 131.15 | 127.9092 | 125.1541 | 122.1919 | 109.6949 | 103.1092 | 99.9031
|  | CHALVEY BSP | CF |  |  |  |  | 37.3143 | 35.8194 | 34.0796 | 32.0602 | 28.4031 | 139.2908 | 135.8062 | 134.2653 | 132.4011 | 122.6857 | 113.1582 | 104.847 | 48.4 | 47.2347 | 45.8919 | 44.4551 | 42.0204 | 148.5725 | 145.4041 | 143.2388 | 140.8041 | 126.5919 | 105.6 | 69.1592 | 37.1633 | 35.8837 | 34.3745 | 32.7735 | 29.7704 | 137.6725 | 134.4235 | 132.8602 | 130.9592 | 121.5072 | 112.9276 | 105.7704
LOVEDEAN GSP | CHICHESTER BSP | CHICHESTER BSP | MINIMUM HEADROOM | SU 92281 07417 | NO | YES | 93.391 | -53.6744 | -58.8397 | -63.7744 | -69.7856 | -76.3744 | -83.8581 | -92.3734 | -100.403 | -106.6999 | -140.0305 | -162.4275 | -175.5622 | -48.105 | -50.3377 | -52.5254 | -55.2213 | -58.9622 | -63.2203 | -68.1713 | -72.8907 | -76.8315 | -99.4397 | -122.4366 | -180.2601 | -64.7856 | -68.9448 | -72.953 | -77.8581 | -83.2611 | -89.4918 | -96.4928 | -103.6713 | -108.8918 | -137.4499 | -156.956 | -167.9244
|  | CHICHESTER BSP | EE |  |  |  |  | -53.6744 | -58.8397 | -63.7744 | -69.7856 | -76.3744 | -83.8581 | -92.3734 | -100.403 | -106.6999 | -139.353 | -158.1285 | -172.8203 | -48.105 | -50.3377 | -52.5254 | -55.2213 | -58.9622 | -63.2203 | -68.1713 | -72.8907 | -76.8315 | -99.4397 | -120.252 | -150.7244 | -64.7856 | -68.9448 | -72.953 | -77.8581 | -83.2611 | -89.4918 | -96.4928 | -103.6713 | -108.8918 | -137.3326 | -153.4009 | -165.8907
|  | CHICHESTER BSP | HT |  |  |  |  | -52.0132 | -56.7193 | -61.7754 | -66.8652 | -72.8877 | -80.254 | -87.7611 | -95.0285 | -101.602 | -140.0305 | -162.4275 | -175.5622 | -46.9897 | -48.6071 | -50.5693 | -52.5152 | -54.806 | -57.9734 | -61.653 | -65.303 | -68.5662 | -87.3224 | -98.0469 | -104.254 | -63.5009 | -67.2377 | -71.3101 | -75.4795 | -80.4213 | -86.5509 | -92.7999 | -98.8622 | -104.3999 | -137.4499 | -156.956 | -167.9244
|  | CHICHESTER BSP | HE |  |  |  |  | -51.8193 | -56.5571 | -61.4999 | -66.4285 | -72.203 | -78.7081 | -85.4448 | -92.0009 | -97.8632 | -132.3469 | -151.703 | -161.0591 | -47.1397 | -49.2224 | -51.4295 | -53.6581 | -56.3601 | -60.1091 | -64.1377 | -68.2356 | -72.0428 | -96.3499 | -117.8111 | -145.7938 | -63.3203 | -67.154 | -71.1591 | -75.255 | -80.0489 | -85.4775 | -91.1122 | -96.606 | -101.5958 | -131.0224 | -148.006 | -155.855
|  | CHICHESTER BSP | CF |  |  |  |  | -49.6111 | -53.2448 | -56.9693 | -60.7928 | -64.7152 | -68.2356 | -72.0173 | -75.6448 | -78.9775 | -103.8734 | -124.0489 | -143.4193 | -46.3591 | -47.8418 | -49.7724 | -51.6469 | -53.6458 | -56.2744 | -59.3662 | -62.5173 | -65.6366 | -88.8744 | -122.4366 | -180.2601 | -61.4336 | -64.2152 | -67.2071 | -70.2815 | -73.4724 | -76.2591 | -79.2836 | -82.2101 | -84.9254 | -105.4713 | -123.3673 | -140.203
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL BSP | MINIMUM HEADROOM | SY 65479 80511 | NO | NO | 20.316 | 13.2435 | 8.1639 | 3.1802 | -2.4973 | -8.0667 | -14.5361 | -22.679 | -30.6994 | -36.6178 | -66.7198 | -87.8137 | -99.5014 | 32.6029 | 29.3998 | 26.2172 | 22.6417 | 19.106 | 15.1427 | 9.8519 | 4.207 | 0.16718 | -22.0726 | -44.9542 | -102.2328 | 13.0702 | 8.7182 | 4.406 | -0.5471 | -5.4226 | -11.3093 | -18.8777 | -26.2981 | -31.6369 | -58.392 | -77.2726 | -87.5777
|  | CHICKERELL BSP | EE |  |  |  |  | 13.2435 | 8.1639 | 3.1802 | -2.4973 | -8.0667 | -14.5361 | -22.679 | -30.6994 | -36.6178 | -66.7198 | -85.1402 | -97.1065 | 32.6029 | 29.3998 | 26.2172 | 22.6417 | 19.106 | 15.1427 | 9.8519 | 4.207 | 0.16718 | -22.0726 | -42.3257 | -70.9818 | 13.0702 | 8.7182 | 4.406 | -0.5471 | -5.4226 | -11.3093 | -18.8777 | -26.2981 | -31.6369 | -58.392 | -75.0114 | -85.5216
|  | CHICKERELL BSP | HT |  |  |  |  | 15.7373 | 11.2608 | 6.521 | 2.1486 | -2.4331 | -8.1371 | -14.5851 | -21.5861 | -28.2249 | -64.7667 | -87.8137 | -99.5014 | 34.7202 | 32.2182 | 29.5111 | 27.1876 | 24.7274 | 21.7886 | 18.36 | 14.6284 | 11.1029 | -8.6379 | -20.3104 | -25.7175 | 15.2672 | 11.4284 | 7.2804 | 3.4753 | -0.5471 | -5.6563 | -11.4114 | -17.6461 | -23.5369 | -56.4226 | -77.2726 | -87.5777
|  | CHICKERELL BSP | HE |  |  |  |  | 15.6159 | 11.1618 | 6.4761 | 2.1404 | -2.3892 | -7.629 | -13.9678 | -20.2055 | -26.2902 | -59.4524 | -79.031 | -88.3178 | 34.0907 | 31.2366 | 28.1866 | 25.4253 | 22.4845 | 19.1468 | 15.0111 | 10.9162 | 6.8407 | -18.2961 | -40.5012 | -67.7889 | 15.1386 | 11.3121 | 7.1937 | 3.3927 | -0.60833 | -5.3063 | -10.993 | -16.5685 | -21.9798 | -51.9849 | -69.8675 | -77.5502
|  | CHICKERELL BSP | CF |  |  |  |  | 17.7812 | 14.4802 | 11.2598 | 7.8261 | 4.7424 | 1.9527 | -0.83816 | -4.4586 | -7.8463 | -31.079 | -54.3137 | -75.1688 | 35.1284 | 32.7988 | 30.4774 | 27.9498 | 25.4743 | 22.8947 | 20.1866 | 16.9121 | 13.6856 | -9.6532 | -44.9542 | -102.2328 | 17.1304 | 14.3529 | 11.5896 | 8.6131 | 5.9253 | 3.4978 | 1.0866 | -2.0696 | -5.0032 | -25.8777 | -46.744 | -65.4961
MELKSHAM GSP | CHIPPENHAM BSP | CHIPPENHAM BSP | MINIMUM HEADROOM | ST 92629 74275 | NO | NO | 71.305 | -12.8107 | 96.734 | 93.036 | 88.4993 | 82.738 | 76.8309 | 70.1625 | 62.8585 | 57.1248 | 31.0044 | 12.9727 | 2.737 | 4.813 | 111.1028 | 108.5355 | 105.3498 | 101.1967 | 97.311 | 92.7375 | 87.7079 | 83.8896 | 65.7865 | 49.7814 | 9.3018 | -11.2594 | 95.8202 | 92.4804 | 88.2569 | 82.8783 | 77.6161 | 71.4702 | 64.7232 | 59.7181 | 37.011 | 22.1447 | 13.7202
|  | CHIPPENHAM BSP | EE |  |  |  |  | -12.8107 | 96.734 | 93.036 | 88.4993 | 82.738 | 76.8309 | 70.1625 | 62.8585 | 57.1248 | 31.0044 | 14.2166 | 3.7462 | 4.813 | 111.1028 | 108.5355 | 105.3498 | 101.1967 | 97.311 | 92.7375 | 87.7079 | 83.8896 | 65.7865 | 49.7814 | 29.0549 | -11.2594 | 95.8202 | 92.4804 | 88.2569 | 82.8783 | 77.6161 | 71.4702 | 64.7232 | 59.7181 | 37.011 | 23.1569 | 14.3681
|  | CHIPPENHAM BSP | HT |  |  |  |  | -11.2433 | 98.9932 | 95.3768 | 91.237 | 86.6503 | 80.8676 | 74.6309 | 68.4534 | 62.4044 | 32.138 | 12.9727 | 2.737 | 6.7987 | 113.963 | 111.7579 | 109.2559 | 106.4804 | 103.2477 | 99.4977 | 95.8477 | 92.2804 | 75.4294 | 66.0273 | 61.5079 | -9.2125 | 98.7059 | 95.4304 | 91.6202 | 87.6283 | 82.5202 | 76.8028 | 71.1845 | 65.663 | 38.4712 | 22.1447 | 13.7202
|  | CHIPPENHAM BSP | HE |  |  |  |  | -11.0688 | 99.3054 | 95.7125 | 91.4146 | 86.9442 | 81.738 | 75.9483 | 69.9278 | 64.034 | 34.5666 | 17.3493 | 10.6166 | 6.4079 | 113.3794 | 110.8998 | 107.9661 | 104.9314 | 101.5365 | 97.4916 | 93.3355 | 89.1906 | 67.4651 | 50.86 | 31.7457 | -9.1268 | 98.9028 | 95.6426 | 91.7181 | 87.7926 | 83.1549 | 77.7896 | 72.2977 | 66.8957 | 39.4426 | 25.662 | 20.4865
|  | CHIPPENHAM BSP | CF |  |  |  |  | -9.2576 | 102.2064 | 99.7952 | 97.0013 | 92.4778 | 90.0993 | 87.637 | 85.0125 | 81.8176 | 61.7319 | 40.837 | 25.1574 | 7.4038 | 114.914 | 113.0518 | 110.9079 | 107.2038 | 105.0477 | 102.6692 | 100.0661 | 96.964 | 77.2936 | 49.8702 | 9.3018 | -7.4533 | 101.5202 | 99.3447 | 96.8069 | 92.7396 | 90.6028 | 88.3038 | 85.8243 | 82.711 | 64.3794 | 45.8681 | 32.261
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ 15716 93165 | NO | NO | 25.573 | 36.3838 | 34.1185 | 31.3675 | 28.0032 | 25.1991 | 20.4348 | 15.0726 | 9.7328 | 5.744 | -13.6019 | -29.0937 | -35.3468 | 54.4484 | 52.7106 | 50.5871 | 47.933 | 45.5698 | 42.1126 | 38.1239 | 34.0647 | 31.033 | 14.4861 | -8.6649 | -63.6731 | 41.4134 | 39.3471 | 36.7971 | 33.6512 | 30.9859 | 26.544 | 21.5032 | 16.4848 | 12.8369 | -4.1519 | -17.9203 | -23.2376
|  | CHRISTCHURCH BSP | EE |  |  |  |  | 36.3838 | 34.1185 | 31.3675 | 28.0032 | 25.1991 | 20.4348 | 15.0726 | 9.7328 | 5.744 | -13.2427 | -26.0968 | -32.7376 | 54.4484 | 52.7106 | 50.5871 | 47.933 | 45.5698 | 42.1126 | 38.1239 | 34.0647 | 31.033 | 14.4861 | -3.521 | -30.4761 | 41.4134 | 39.3471 | 36.7971 | 33.6512 | 30.9859 | 26.544 | 21.5032 | 16.4848 | 12.8369 | -4.1519 | -15.3345 | -21.1172
|  | CHRISTCHURCH BSP | HT |  |  |  |  | 37.8869 | 35.5022 | 32.9073 | 30.892 | 28.6777 | 24.5777 | 20.395 | 15.6991 | 10.8471 | -13.6019 | -29.0937 | -35.3468 | 56.4004 | 54.9351 | 53.2443 | 52.1116 | 50.7126 | 48.4188 | 46.0739 | 43.3279 | 40.4514 | 26.8382 | 19.1004 | 16.1126 | 43.1185 | 40.9297 | 38.4583 | 36.6267 | 34.545 | 30.7848 | 26.9624 | 22.645 | 18.1777 | -4.1356 | -17.9203 | -23.2376
|  | CHRISTCHURCH BSP | HE |  |  |  |  | 38.0889 | 35.8859 | 33.4838 | 31.6644 | 29.6797 | 26.2828 | 22.8267 | 18.9206 | 14.8175 | -5.0468 | -17.7805 | -22.7131 | 55.9228 | 54.2086 | 52.281 | 50.8269 | 49.0912 | 46.5535 | 43.9208 | 40.8382 | 37.533 | 19.0004 | 0.5555 | -25.718 | 43.2879 | 41.2379 | 38.9389 | 37.294 | 35.4165 | 32.2797 | 29.0869 | 25.4532 | 21.6399 | 3.4502 | -7.7468 | -11.8305
|  | CHRISTCHURCH BSP | CF |  |  |  |  | 39.6216 | 38.2471 | 36.7665 | 35.4185 | 34.3655 | 32.9226 | 31.5655 | 29.7797 | 28.2695 | 15.0573 | -0.045767 | -14.0356 | 56.5647 | 55.2259 | 53.729 | 52.2535 | 50.7596 | 48.7279 | 46.6494 | 44.1463 | 41.7422 | 22.5555 | -8.6649 | -63.6731 | 44.6838 | 43.4144 | 41.9716 | 40.7002 | 39.7124 | 38.3583 | 37.0859 | 35.3746 | 33.942 | 21.4726 | 7.8318 | -4.5376
IVER 132KV GSP | CIPPENHAM BSP | CIPPENHAM BSP | MINIMUM HEADROOM | SU 96266 79634 | NO | YES | 22.271 | 73.9787 | 73.0471 | 71.7124 | 70.1685 | 68.6818 | 66.7848 | 64.6246 | 62.5961 | 61.0124 | 54.0706 | 49.245 | 47.745 | 76.4899 | 75.8328 | 74.945 | 73.9491 | 72.9257 | 71.7155 | 70.3042 | 68.9348 | 67.7767 | 61.8195 | 55.2216 | 38.7706 | 70.795 | 69.9797 | 68.8226 | 67.5012 | 66.1838 | 64.4797 | 62.4593 | 60.5348 | 59.0502 | 52.6889 | 48.4634 | 47.1869
|  | CIPPENHAM BSP | EE |  |  |  |  | 73.9787 | 73.0471 | 71.7124 | 70.1685 | 68.6818 | 66.7848 | 64.6246 | 62.5961 | 61.0124 | 54.0706 | 50.1593 | 49.0767 | 76.4899 | 75.8328 | 74.945 | 73.9491 | 72.9257 | 71.7155 | 70.3042 | 68.9348 | 67.7767 | 61.8195 | 56.2971 | 48.6328 | 70.795 | 69.9797 | 68.8226 | 67.5012 | 66.1838 | 64.4797 | 62.4593 | 60.5348 | 59.0502 | 52.6889 | 49.2542 | 48.3542
|  | CIPPENHAM BSP | HT |  |  |  |  | 74.5144 | 73.4787 | 72.2206 | 71.1736 | 69.9879 | 68.5124 | 66.7328 | 64.9767 | 63.1767 | 54.4808 | 49.245 | 47.745 | 77.044 | 76.4012 | 75.6644 | 75.0777 | 74.3644 | 73.5318 | 72.5073 | 71.4644 | 70.4042 | 65.6583 | 62.9471 | 62.0981 | 71.3287 | 70.3971 | 69.2879 | 68.3859 | 67.3063 | 65.9604 | 64.344 | 62.7379 | 61.0971 | 53.1512 | 48.4634 | 47.1869
|  | CIPPENHAM BSP | HE |  |  |  |  | 74.5338 | 73.5379 | 72.4216 | 71.592 | 70.4797 | 69.0757 | 67.3532 | 65.8002 | 64.2063 | 56.9797 | 53.093 | 51.8848 | 76.8818 | 76.1532 | 75.3746 | 74.8104 | 73.9899 | 73.044 | 71.8777 | 70.7644 | 69.5797 | 63.2818 | 57.6675 | 50.0369 | 71.343 | 70.442 | 69.445 | 68.7481 | 67.7318 | 66.4583 | 64.9063 | 63.4859 | 62.0226 | 55.3797 | 51.8236 | 50.7859
|  | CIPPENHAM BSP | CF |  |  |  |  | 75.2859 | 74.6818 | 74.0063 | 73.0614 | 72.4695 | 71.6808 | 70.8297 | 70.1348 | 69.3746 | 64.0328 | 58.5532 | 53.5808 | 77.244 | 76.6848 | 76.094 | 75.3665 | 74.8328 | 74.0604 | 73.2104 | 72.4144 | 71.5389 | 65.0818 | 55.2216 | 38.7706 | 71.9991 | 71.445 | 70.842 | 70.0338 | 69.5624 | 68.8726 | 68.1277 | 67.5032 | 66.8185 | 61.7655 | 56.794 | 52.3757
MINETY GSP | CIRENCESTER BSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP 02701 00368 | NO | NO | 15.706 | 23.9795 | 22.2499 | 20.2479 | 17.8306 | 15.4142 | 12.0346 | 8.4775 | 3.9275 | -0.47965 | -17.5256 | -30.9439 | -41.0082 | 45.4275 | 44.101 | 42.5744 | 40.7275 | 38.6693 | 36.1642 | 33.3816 | 28.5918 | 24.5367 | 10.0693 | -4.4317 | -23.9215 | 28.2622 | 26.7081 | 24.9163 | 22.7183 | 20.1999 | 17.1122 | 13.7408 | 8.505 | 3.9622 | -12.3317 | -24.7194 | -35.2297
|  | CIRENCESTER BSP | EE |  |  |  |  | 23.9795 | 22.2499 | 20.2479 | 17.8306 | 15.4142 | 12.0346 | 8.7295 | 4.603 | 1.5448 | -13.0878 | -27.446 | -35.0521 | 45.4275 | 44.101 | 42.5744 | 40.7275 | 38.9081 | 36.4938 | 34.2601 | 31.0591 | 28.8326 | 17.1581 | 0.19994 | -15.2582 | 28.2622 | 26.7081 | 24.9163 | 22.7183 | 20.4959 | 17.3234 | 14.2969 | 10.2336 | 7.4428 | -6.096 | -20.8786 | -28.2327
|  | CIRENCESTER BSP | HT |  |  |  |  | 24.7081 | 23.0826 | 21.0836 | 19.1357 | 15.8795 | 12.3101 | 8.4775 | 5.7163 | 1.9357 | -15.5327 | -30.9439 | -41.0082 | 46.4438 | 45.3744 | 43.9887 | 42.8224 | 40.1897 | 37.7642 | 35.0397 | 33.4826 | 30.802 | 19.303 | 7.052 | -1.0582 | 28.9989 | 27.5295 | 25.6928 | 23.9918 | 20.7591 | 17.3999 | 13.7408 | 11.2622 | 7.5969 | -9.0082 | -24.7194 | -34.9286
|  | CIRENCESTER BSP | HE |  |  |  |  | 24.7734 | 23.154 | 21.0459 | 19.0081 | 15.5765 | 12.3285 | 8.853 | 3.9275 | -0.47965 | -17.5256 | -29.7225 | -39.4705 | 46.2459 | 45.005 | 43.2816 | 41.7714 | 38.6693 | 36.1642 | 33.3816 | 28.5918 | 24.5367 | 10.0693 | -4.4317 | -23.9215 | 29.0448 | 27.5561 | 25.5448 | 23.6969 | 20.1999 | 17.1122 | 13.7846 | 8.505 | 3.9622 | -12.3317 | -24.598 | -35.2297
|  | CIRENCESTER BSP | CF |  |  |  |  | 25.551 | 24.4418 | 23.2734 | 21.7377 | 20.0744 | 18.3479 | 16.5714 | 14.6652 | 12.6101 | 2.2418 | -8.7062 | -19.2797 | 46.6703 | 45.7714 | 44.8642 | 43.5928 | 42.1836 | 40.5326 | 38.7826 | 36.8775 | 34.7928 | 22.9316 | 5.3061 | -22.1684 | 29.7663 | 28.801 | 27.7836 | 26.405 | 24.9122 | 23.3193 | 21.6867 | 19.9254 | 17.9744 | 8.0428 | -2.6072 | -12.6143
FAWLEY GSP | COWES BSP | COWES BSP | MINIMUM HEADROOM | SZ 50486 94250 | NO | NO | 5.182 | -48.75 | -50.651 | -53.2439 | -56.2735 | -59.4959 | -63.9816 | -68.4235 | -73.1724 | -76.9173 | -94.7653 | -109.0776 | -117.0184 | -15.5561 | -16.6714 | -18.1122 | -19.8622 | -22.0245 | -24.8796 | -27.7786 | -30.9378 | -33.3816 | -45.7306 | -57.1163 | -86.5173 | -40.149 | -41.8031 | -44.1306 | -46.8296 | -49.6582 | -53.5888 | -57.7878 | -62.2888 | -65.6561 | -81.0306 | -93.2224 | -99.9592
|  | COWES BSP | EE |  |  |  |  | -48.75 | -50.651 | -53.2439 | -56.2735 | -59.4959 | -63.9816 | -68.4235 | -73.1724 | -76.9173 | -94.7245 | -106.6796 | -115.6296 | -15.5561 | -16.6714 | -18.1122 | -19.8622 | -22.0245 | -24.8796 | -27.7786 | -30.9378 | -33.3816 | -45.7306 | -57.1163 | -73.0061 | -40.149 | -41.8031 | -44.1306 | -46.8296 | -49.6582 | -53.5888 | -57.7878 | -62.2888 | -65.6561 | -81.0306 | -91.2857 | -98.9765
|  | COWES BSP | HT |  |  |  |  | -47.799 | -50.0592 | -52.5929 | -55.5092 | -58.0684 | -62.0755 | -66.1673 | -70.0235 | -74.1582 | -94.7653 | -109.0776 | -117.0184 | -14.4969 | -15.4939 | -16.6235 | -17.9276 | -19.1663 | -21.2582 | -23.552 | -25.6592 | -28.0541 | -39.0888 | -45.9459 | -49.3102 | -39.1459 | -41.0918 | -43.2969 | -45.8408 | -48.0102 | -51.5235 | -55.1633 | -58.5827 | -62.2837 | -80.6143 | -93.2224 | -99.9592
|  | COWES BSP | HE |  |  |  |  | -47.6459 | -49.6429 | -51.8929 | -54.5571 | -56.9857 | -60.55 | -64.2776 | -67.8714 | -71.6378 | -90.451 | -103.1449 | -108.6908 | -14.7122 | -15.7786 | -16.999 | -18.4459 | -19.8898 | -22.0163 | -24.5071 | -26.8898 | -29.5551 | -43.4878 | -55.698 | -70.1337 | -39.0531 | -40.8061 | -42.7908 | -45.1357 | -47.2061 | -50.3418 | -53.6776 | -56.8653 | -60.2602 | -77.1184 | -88.1969 | -92.8531
|  | COWES BSP | CF |  |  |  |  | -46.099 | -47.2286 | -48.3745 | -49.7776 | -51.3327 | -52.2898 | -53.998 | -55.8786 | -57.9041 | -72.1949 | -85.3847 | -97.3684 | -13.7469 | -14.3398 | -15.0102 | -15.9949 | -17.4071 | -18.4255 | -20.1592 | -22.0245 | -24.0582 | -37.7602 | -56.6878 | -86.5173 | -37.6878 | -38.7 | -39.7092 | -40.9459 | -42.3082 | -43.0898 | -44.6061 | -46.2796 | -48.0888 | -60.8582 | -72.6286 | -83.0092
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | COWLEY LOCAL (RESERVE) BSP | MINIMUM HEADROOM | SP 56113 03074 | NO | NO | 32.929 | 41.3201 | 39.6701 | 36.4874 | 33.5221 | 25.9517 | 20.7109 | 14.6721 | 2.3956 | -7.185 | -33.9748 | -58.9116 | -82.1911 | 51.6507 | 50.4099 | 47.5425 | 45.517 | 38.3619 | 34.1119 | 29.2517 | 16.3558 | 6.8486 | -16.735 | -43.5116 | -76.3871 | 42.4772 | 41.0242 | 37.8027 | 35.1333 | 27.0374 | 21.9813 | 16.0395 | 2.2782 | -8.2024 | -35.0656 | -62.233 | -90.3585
|  | COWLEY LOCAL (RESERVE) BSP | EE |  |  |  |  | 41.3201 | 39.6701 | 37.6017 | 35.2997 | 31.0538 | 25.8323 | 21.7619 | 15.4895 | 10.7619 | -12.1677 | -44.4758 | -56.3993 | 51.6507 | 50.6925 | 49.4986 | 48.2609 | 45.1435 | 41.2813 | 38.9517 | 33.916 | 30.5089 | 12.1578 | -23.6799 | -41.3565 | 42.4772 | 41.0242 | 39.2344 | 37.4007 | 33.4038 | 28.4038 | 24.967 | 18.7619 | 14.4558 | -7.1197 | -43.4411 | -56.8983
|  | COWLEY LOCAL (RESERVE) BSP | HT |  |  |  |  | 41.7323 | 39.8568 | 37.1813 | 34.7527 | 28.0915 | 22.517 | 16.014 | 11.6854 | 4.9538 | -21.3942 | -52.7044 | -71.6738 | 52.0854 | 50.8344 | 48.866 | 47.6599 | 41.8017 | 37.5048 | 32.4354 | 29.8844 | 24.3476 | 3.9589 | -27.3962 | -48.5299 | 43.0456 | 41.3038 | 38.7609 | 36.7711 | 29.8293 | 24.4772 | 18.0762 | 14.3497 | 7.5374 | -18.4054 | -53.386 | -75.7616
|  | COWLEY LOCAL (RESERVE) BSP | HE |  |  |  |  | 41.8058 | 39.7782 | 36.4874 | 33.5221 | 25.9517 | 20.7109 | 14.6721 | 2.3956 | -7.185 | -33.9748 | -58.9116 | -82.1911 | 51.9772 | 50.4099 | 47.5425 | 45.517 | 38.3619 | 34.1119 | 29.2517 | 16.3558 | 6.8486 | -16.735 | -43.5116 | -76.3871 | 43.0884 | 41.1384 | 37.8027 | 35.1333 | 27.0374 | 21.9813 | 16.0395 | 2.2782 | -8.2024 | -35.0656 | -62.233 | -90.3585
|  | COWLEY LOCAL (RESERVE) BSP | CF |  |  |  |  | 42.3548 | 41.2833 | 39.8354 | 37.5252 | 34.4129 | 30.8956 | 27.265 | 23.8833 | 20.4446 | 1.5129 | -16.5779 | -29.9952 | 52.214 | 51.5435 | 50.6589 | 49.0211 | 46.8629 | 44.1742 | 41.5303 | 39.0558 | 36.3446 | 19.8803 | -0.98911 | -25.2289 | 43.5364 | 42.6333 | 41.416 | 39.3762 | 36.667 | 33.4466 | 30.1956 | 27.2548 | 24.1548 | 6.0538 | -12.2942 | -27.0391
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL (MAIN) BSP | MINIMUM HEADROOM | SP 56113 03074 | NO | NO | 70.432 | 6.0933 | 3.8178 | 1.4046 | 114.4148 | 111.0107 | 105.0729 | 99.3097 | 93.7995 | 89.5015 | 74.127 | 67.1413 | 65.4046 | 19.6944 | 17.926 | 15.977 | 124.0546 | 121.2893 | 117.4576 | 113.2607 | 108.9893 | 105.4923 | 90.6709 | 73.4842 | 36.6944 | 7.778 | 5.779 | 3.5688 | 113.1454 | 109.9086 | 104.7882 | 99.5148 | 94.3811 | 90.475 | 76.6597 | 70.875 | 69.5178
|  | COWLEY LOCAL (MAIN) BSP | EE |  |  |  |  | 6.0933 | 3.8178 | 1.4046 | 114.4148 | 111.0107 | 105.0729 | 99.3097 | 93.7995 | 89.5015 | 74.127 | 67.8056 | 67.3178 | 19.6944 | 17.926 | 15.977 | 124.0546 | 121.2893 | 117.4576 | 113.2607 | 108.9893 | 105.4923 | 90.6709 | 78.9046 | 61.9576 | 7.778 | 5.779 | 3.5688 | 113.1454 | 109.9086 | 104.7882 | 99.5148 | 94.3811 | 90.475 | 76.6597 | 71.327 | 71.0188
|  | COWLEY LOCAL (MAIN) BSP | HT |  |  |  |  | 6.8586 | 5.1056 | 3.378 | 116.1025 | 113.427 | 106.8872 | 102.3321 | 97.7046 | 93.1495 | 75.9852 | 67.1413 | 65.4046 | 20.7688 | 19.5923 | 18.4699 | 126.5137 | 124.6158 | 120.8842 | 117.7484 | 114.4209 | 111.2301 | 100.2984 | 95.2423 | 94.028 | 8.5668 | 6.976 | 5.425 | 114.7362 | 112.2709 | 106.6301 | 102.4586 | 98.177 | 94.0199 | 78.6923 | 70.875 | 69.5178
|  | COWLEY LOCAL (MAIN) BSP | HE |  |  |  |  | 7.4229 | 5.3586 | 3.5076 | 116.727 | 114.2995 | 108.8117 | 104.3495 | 99.7301 | 95.6342 | 78.8076 | 72.078 | 70.1913 | 20.629 | 19.0372 | 17.5719 | 125.8474 | 123.8586 | 120.2597 | 116.9944 | 113.3107 | 109.8556 | 93.0862 | 80.6556 | 63.3301 | 8.9484 | 7.1168 | 5.4546 | 115.2821 | 113.0607 | 108.2719 | 104.277 | 100.0444 | 96.2678 | 81.026 | 75.1097 | 73.6158
|  | COWLEY LOCAL (MAIN) BSP | CF |  |  |  |  | 8.9362 | 7.8688 | 6.9525 | 121.1209 | 119.678 | 118.0321 | 115.3709 | 112.5362 | 109.2872 | 90.5852 | 80.0484 | 71.7872 | 21.3954 | 20.2586 | 19.229 | 127.9342 | 126.4342 | 124.6739 | 122.0995 | 119.3648 | 116.2025 | 95.5046 | 73.4842 | 36.6944 | 10.2923 | 9.3015 | 8.4668 | 119.1617 | 117.8933 | 116.4688 | 114.1331 | 111.6535 | 108.777 | 91.8474 | 82.4525 | 75.2188
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU 78324 50817 | NO | NO | 23.249 | 40.3291 | 37.7883 | 35.8179 | 148.1626 | 145.3513 | 141.0095 | 136.5064 | 131.685 | 128.0207 | 108.6044 | 93.2779 | 84.6687 | 56.2243 | 54.2753 | 52.759 | 160.9916 | 158.712 | 155.7018 | 152.5192 | 149.0324 | 146.412 | 132.0498 | 116.2967 | 77.7018 | 40.3386 | 37.8539 | 36.0416 | 145.8345 | 143.0794 | 138.9998 | 134.8018 | 130.2304 | 126.9732 | 110.209 | 96.5406 | 89.0824
|  | COXMOOR WOOD BSP | EE |  |  |  |  | 40.3291 | 37.7883 | 35.8179 | 148.1626 | 145.3513 | 141.0095 | 136.5064 | 131.685 | 128.0207 | 109.1024 | 95.6585 | 85.7197 | 56.2243 | 54.2753 | 52.759 | 160.9916 | 158.712 | 155.7018 | 152.5192 | 149.0324 | 146.412 | 132.0498 | 117.709 | 97.511 | 40.3386 | 37.8539 | 36.0416 | 145.8345 | 143.0794 | 138.9998 | 134.8018 | 130.2304 | 126.9732 | 110.4181 | 98.5865 | 89.9151
|  | COXMOOR WOOD BSP | HT |  |  |  |  | 41.823 | 39.7863 | 37.7781 | 149.8166 | 147.6758 | 144.4319 | 140.5472 | 136.133 | 131.5493 | 108.6044 | 93.2779 | 84.6687 | 57.8773 | 56.6049 | 55.3488 | 163.6539 | 162.2661 | 160.6151 | 158.4569 | 155.8712 | 153.1569 | 140.5661 | 133.1641 | 129.3855 | 41.9753 | 40.0569 | 38.1773 | 147.5947 | 145.5957 | 142.812 | 139.3355 | 135.2845 | 131.059 | 110.209 | 96.5406 | 89.0824
|  | COXMOOR WOOD BSP | HE |  |  |  |  | 41.875 | 39.922 | 37.9914 | 150.1197 | 148.1024 | 145.4034 | 142.0707 | 138.2024 | 134.2381 | 113.7575 | 100.1248 | 94.0564 | 57.4579 | 55.9743 | 54.4855 | 162.5355 | 160.8988 | 159.0549 | 156.661 | 153.7906 | 150.7784 | 134.2477 | 119.4998 | 100.9804 | 41.9988 | 40.1477 | 38.3396 | 147.8263 | 145.9528 | 143.6079 | 140.5906 | 136.9804 | 133.2743 | 114.6508 | 102.5345 | 97.3008
|  | COXMOOR WOOD BSP | CF |  |  |  |  | 43.2965 | 42.1301 | 40.9791 | 154.083 | 152.6595 | 151.5207 | 150.4911 | 149.0585 | 147.2177 | 133.9381 | 119.0585 | 105.6901 | 58.1549 | 57.0508 | 55.913 | 164.461 | 162.912 | 161.4518 | 160.0059 | 158.1865 | 155.9681 | 140.2671 | 116.2967 | 77.7018 | 43.2773 | 42.1447 | 41.0345 | 151.4447 | 150.0284 | 148.9437 | 148.0324 | 146.6743 | 144.8579 | 132.3488 | 119.2886 | 107.4794
IVER 132KV GSP | DENHAM B BSP | DENHAM B BSP | MINIMUM HEADROOM | TQ 01785 87618 | NO | YES | 4.821 |  |  |  | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 |  |  |  | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 |  |  |  | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6
|  | DENHAM B BSP | EE | [7 empty] | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 |  |  |  | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 |  |  |  | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6
|  | DENHAM B BSP | HT | [7 empty] | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 |  |  |  | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 |  |  |  | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6
|  | DENHAM B BSP | HE | [7 empty] | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 |  |  |  | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 |  |  |  | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6
|  | DENHAM B BSP | CF | [7 empty] | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 |  |  |  | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 |  |  |  | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6
IVER 132KV GSP | DENHAM BSP | DENHAM BSP | MINIMUM HEADROOM | TQ 01785 87618 | NO | YES | 11.488 | 54.7013 | 52.9523 | 69.6215 | 67.993 | 66.4644 | 63.5246 | 61.0878 | 58.3134 | 56.1348 | 43.9562 | 34.1562 | 28.6552 | 70.3809 | 69.0799 | 85.9983 | 84.8299 | 83.7105 | 81.7768 | 80.2666 | 78.4115 | 77.0166 | 70.2503 | 63.6758 | 49.433 | 55.1013 | 53.5207 | 70.4136 | 68.9003 | 67.4666 | 64.7503 | 62.4666 | 59.8789 | 57.8289 | 47.0054 | 38.5003 | 33.9738
|  | DENHAM BSP | EE |  |  |  |  | 54.7013 | 52.9523 | 69.6215 | 67.993 | 66.4644 | 63.5246 | 61.0878 | 58.3134 | 56.1348 | 44.8583 | 36.1001 | 29.4817 | 70.3809 | 69.0799 | 85.9983 | 84.8299 | 83.7105 | 81.7768 | 80.2666 | 78.4115 | 77.0166 | 70.2503 | 63.6758 | 54.8891 | 55.1013 | 53.5207 | 70.4136 | 68.9003 | 67.4666 | 64.7503 | 62.4666 | 59.8789 | 57.8289 | 47.7125 | 40.2197 | 34.7003
|  | DENHAM BSP | HT |  |  |  |  | 55.5605 | 54.1758 | 71.2756 | 69.7878 | 68.2358 | 65.9368 | 63.1256 | 60.5154 | 57.4797 | 43.9562 | 34.1562 | 28.6552 | 71.383 | 70.5176 | 87.9003 | 86.9523 | 85.9074 | 84.7901 | 83.1891 | 81.7605 | 79.9442 | 73.235 | 68.9472 | 66.7564 | 55.935 | 54.6809 | 71.9299 | 70.5574 | 69.1125 | 67.0105 | 64.4095 | 62.0278 | 59.2156 | 47.0054 | 38.5003 | 33.9738
|  | DENHAM BSP | HE |  |  |  |  | 55.685 | 54.3442 | 71.5644 | 70.1634 | 68.645 | 66.845 | 64.8348 | 62.3613 | 60.1491 | 48.047 | 39.6623 | 35.5889 | 71.2523 | 70.2646 | 87.6136 | 86.6176 | 85.4666 | 84.3819 | 83.0901 | 81.3605 | 79.8503 | 71.6146 | 65.1615 | 57.4707 | 56.0513 | 54.8187 | 72.1921 | 70.9054 | 69.4799 | 67.8044 | 65.9544 | 63.6483 | 61.6003 | 50.5799 | 43.3921 | 40.0789
|  | DENHAM BSP | CF |  |  |  |  | 56.5625 | 55.7605 | 73.3297 | 72.445 | 71.5521 | 70.5919 | 69.4501 | 68.6123 | 67.7654 | 60.2032 | 51.7746 | 43.3532 | 71.6605 | 70.9625 | 88.4023 | 87.6585 | 86.8299 | 85.887 | 84.7768 | 83.9299 | 83.0472 | 75.6003 | 65.4493 | 49.433 | 56.8615 | 56.1381 | 73.8299 | 73.0268 | 72.2074 | 71.337 | 70.2962 | 69.5156 | 68.7258 | 61.6585 | 53.8983 | 46.4064
COWLEY GSP | DRAYTON BSP | DRAYTON BSP | MINIMUM HEADROOM | SU 46684 92706 | NO | NO | 76.875 | -42.4835 | -47.6284 | -52.3366 | -67.8325 | -74.2468 | -82.0927 | -89.709 | -97.4478 | -103.6345 | -136.7539 | -163.7815 | -181.9988 | -24.2713 | -27.657 | -30.6713 | -46.4794 | -50.9529 | -56.8876 | -62.6213 | -68.7815 | -74.7886 | -101.2223 | -126.0192 | -163.2662 | -46.559 | -51.0468 | -55.1651 | -72.3508 | -78.2376 | -85.7631 | -93.0304 | -100.6284 | -106.4151 | -137.0692 | -163.811 | -181.4539
|  | DRAYTON BSP | EE |  |  |  |  | -42.4835 | -47.6284 | -52.3366 | -67.8325 | -74.2468 | -82.0927 | -89.709 | -97.4478 | -103.6345 | -132.3896 | -157.2029 | -174.3825 | -24.2713 | -27.657 | -30.6713 | -46.4794 | -50.9529 | -56.8876 | -62.6213 | -68.7815 | -73.5274 | -96.0651 | -122.961 | -152.2682 | -46.559 | -51.0468 | -55.1651 | -72.3508 | -78.2376 | -85.7631 | -93.0304 | -100.6284 | -106.4151 | -132.2723 | -156.708 | -172.5968
|  | DRAYTON BSP | HT |  |  |  |  | -41.1498 | -46.261 | -51.9794 | -66.8549 | -73.9192 | -81.0304 | -88.4804 | -95.3284 | -103.1355 | -136.7539 | -163.7815 | -181.9988 | -22.5121 | -25.5427 | -29.158 | -43.9947 | -48.8519 | -53.6029 | -58.7825 | -63.2213 | -68.9529 | -90.8682 | -110.0988 | -123.0059 | -45.1121 | -49.5182 | -54.6315 | -71.1304 | -77.7672 | -84.4682 | -91.5427 | -97.8621 | -105.4131 | -137.0692 | -163.811 | -181.4539
|  | DRAYTON BSP | HE |  |  |  |  | -41.008 | -46.0376 | -51.1641 | -65.7284 | -73.2376 | -79.4702 | -86.0376 | -94.608 | -102.1733 | -133.2121 | -156.1794 | -173.4753 | -22.9396 | -26.2753 | -29.8029 | -44.7702 | -50.5478 | -55.2294 | -60.3702 | -68.1131 | -74.7886 | -101.2223 | -126.0192 | -158.8519 | -45.008 | -49.3825 | -53.9906 | -70.2304 | -77.4213 | -83.2702 | -89.4947 | -98.2457 | -105.7825 | -135.0988 | -157.1651 | -174.6804
|  | DRAYTON BSP | CF |  |  |  |  | -39.308 | -43.1396 | -46.7692 | -60.96 | -65.3457 | -69.6039 | -73.5325 | -77.2641 | -80.86 | -102.6988 | -123.0447 | -141.8968 | -22.1539 | -24.7927 | -27.3274 | -42.5376 | -45.8008 | -49.7059 | -53.458 | -57.1172 | -60.8172 | -83.9049 | -114.6723 | -163.2662 | -43.4641 | -46.6692 | -49.7631 | -65.7264 | -69.5968 | -73.5457 | -77.1733 | -80.6243 | -84.0315 | -104.709 | -123.5202 | -140.5121
EALING GSP | EALING BSP | EALING BSP | MINIMUM HEADROOM | TQ 18371 79475 | NO | NO | 20.869 | 27.3015 | 24.8505 | 22.4148 | 19.5556 | 15.9903 | 12.8434 | 8.8709 | 4.9525 | 2.0495 | -8.9536 | -18.1189 | -22.2679 | 40.2556 | 38.3903 | 36.4893 | 34.2678 | 31.3872 | 28.725 | 25.3352 | 21.8964 | 19.0913 | 5.2117 | -19.3883 | -71.3434 | 29.1495 | 26.9066 | 24.6413 | 21.9862 | 18.6321 | 15.6862 | 11.926 | 8.224 | 5.476 | -4.6158 | -12.576 | -16.1454
|  | EALING BSP | EE |  |  |  |  | 27.3015 | 24.8505 | 22.4148 | 19.5556 | 15.9903 | 12.8434 | 8.8709 | 4.9525 | 2.0495 | -8.9536 | -16.1556 | -20.6985 | 40.2556 | 38.3903 | 36.4893 | 34.2678 | 31.3872 | 28.725 | 25.3352 | 21.8964 | 19.0913 | 5.2117 | -10.4362 | -36.7311 | 29.1495 | 26.9066 | 24.6413 | 21.9862 | 18.6321 | 15.6862 | 11.926 | 8.224 | 5.476 | -4.6158 | -10.7822 | -14.8311
|  | EALING BSP | HT |  |  |  |  | 28.1413 | 26.0229 | 23.7985 | 20.4658 | 17.1821 | 14.2148 | 11.1832 | 8.6015 | 6.2842 | -7.4179 | -18.1189 | -22.2679 | 41.4791 | 40.2852 | 38.9903 | 36.7413 | 34.5107 | 32.4974 | 30.327 | 28.476 | 26.8638 | 18.1403 | 12.3627 | 10.3658 | 30.024 | 28.1648 | 26.1627 | 23.0485 | 19.9678 | 17.2076 | 14.3444 | 11.8995 | 9.7219 | -2.9985 | -12.576 | -16.1454
|  | EALING BSP | HE |  |  |  |  | 28.3985 | 26.4219 | 24.5525 | 22.4556 | 19.3025 | 16.5301 | 13.4189 | 11.1627 | 8.5117 | -2.4515 | -9.1128 | -11.2056 | 41.1719 | 39.7087 | 38.2801 | 36.674 | 34.0811 | 31.6872 | 28.9607 | 26.6944 | 24.0423 | 9.7474 | -6.2689 | -31.4444 | 30.2362 | 28.475 | 26.7791 | 24.8821 | 21.9413 | 19.3546 | 16.4423 | 14.3801 | 11.875 | 1.7434 | -4.126 | -5.8913
|  | EALING BSP | CF |  |  |  |  | 29.5291 | 28.4515 | 27.3474 | 26.2832 | 25.1862 | 24.0148 | 22.324 | 20.3015 | 18.6485 | 7.6087 | 0.074988 | -7.0862 | 41.6372 | 40.5658 | 39.3413 | 38.1066 | 36.6668 | 34.725 | 32.3036 | 29.6117 | 27.0566 | 8.7546 | -19.3883 | -71.3434 | 31.2495 | 30.278 | 29.2454 | 28.2495 | 27.2291 | 26.0852 | 24.4566 | 22.5403 | 21.0005 | 10.8056 | 3.8321 | -2.5454
LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT BSP | MINIMUM HEADROOM | TQ 08394 73826 | NO | NO | 28.849 | 7.8947 | 6.3294 | 4.9457 | 2.859 | 0.095743 | -2.292 | -5.9461 | -9.6828 | -12.4165 | -23.189 | -30.9798 | -35.2512 | 14.4173 | 16.0735 | 14.9143 | 13.2857 | 11.0469 | 9.1969 | 6.451 | 3.6102 | 1.4582 | -9.0296 | -26.4714 | -62.3541 | 6.6316 | 6.8092 | 5.6449 | 4.0428 | 1.703 | -0.50205 | -3.747 | -7.0408 | -9.4827 | -19.1725 | -26.1929 | -30.1439
|  | EAST BEDFONT BSP | EE |  |  |  |  | 7.8947 | 6.3294 | 4.9457 | 2.859 | 0.095743 | -2.292 | -5.9461 | -9.6828 | -12.4165 | -23.189 | -29.9685 | -35.1318 | 14.4173 | 16.0735 | 14.9143 | 13.2857 | 11.0469 | 9.1969 | 6.451 | 3.6102 | 1.4582 | -9.0296 | -20.5388 | -39.1653 | 6.6316 | 6.8092 | 5.6449 | 4.0428 | 1.703 | -0.50205 | -3.747 | -7.0408 | -9.4827 | -19.1725 | -25.4163 | -30.1439
|  | EAST BEDFONT BSP | HT |  |  |  |  | 8.1815 | 6.8253 | 5.307 | 3.1631 | 1.0672 | -1.6287 | -4.6808 | -7.793 | -9.8777 | -22.7451 | -30.9798 | -35.2512 | 14.9735 | 17.0684 | 16.2796 | 14.8816 | 13.5755 | 11.9204 | 10.0612 | 8.1653 | 7.0337 | -0.27552 | -4.4306 | -6.3939 | 6.9857 | 7.4224 | 6.1102 | 4.1214 | 2.2133 | -0.19593 | -2.799 | -5.4439 | -7.2429 | -18.6439 | -26.1929 | -30.1296
|  | EAST BEDFONT BSP | HE |  |  |  |  | 8.5274 | 7.2141 | 5.9213 | 4.3978 | 2.5039 | 0.12942 | -2.793 | -6.0043 | -8.2063 | -19.9267 | -27.0441 | -29.942 | 14.8704 | 16.7112 | 15.801 | 14.6867 | 13.1347 | 11.1949 | 8.8796 | 6.4 | 4.5979 | -7.1643 | -19.2663 | -36.8847 | 7.2622 | 7.6928 | 6.553 | 5.1979 | 3.4643 | 1.3041 | -1.2765 | -3.9612 | -5.8959 | -16.2551 | -22.8123 | -25.5031
|  | EAST BEDFONT BSP | CF |  |  |  |  | 9.7845 | 9.1937 | 8.4815 | 7.7978 | 7.0723 | 6.4253 | 5.0743 | 3.3947 | 1.7702 | -9.8441 | -17.5451 | -24.0675 | 15.4204 | 17.6133 | 16.853 | 16.101 | 15.0796 | 13.901 | 12.0673 | 10.053 | 8.0214 | -6.1347 | -26.4714 | -62.3541 | 8.3275 | 9.3898 | 8.7428 | 8.1133 | 7.4449 | 6.8275 | 5.5806 | 4.1928 | 2.8867 | -6.8735 | -13.8031 | -19.8194
LOVEDEAN GSP | FAREHAM (MAIN) BSP | FAREHAM (MAIN) BSP | MINIMUM HEADROOM | SU 56534 04031 | NO | YES | 55.596 | 3.7744 | 0.35912 | -2.4297 | -5.7654 | -9.7062 | -15.9062 | -22.9746 | -30.3664 | -36.2072 | -62.3939 | -79.2593 | -88.5552 | 14.94 | 12.4839 | 10.5073 | 8.1155 | 5.3022 | 1.1185 | -3.7978 | -8.9855 | -12.9121 | -32.8794 | -57.2764 | -112.6774 | 4.242 | 1.1267 | -1.3488 | -4.3243 | -7.8733 | -13.4825 | -19.8998 | -26.5835 | -31.7437 | -54.407 | -69.709 | -78.2039
|  | FAREHAM (MAIN) BSP | EE |  |  |  |  | 3.7744 | 0.35912 | -2.4297 | -5.7654 | -9.7062 | -15.9062 | -22.9746 | -30.3664 | -36.2072 | -61.4195 | -76.2133 | -87.3072 | 14.94 | 12.4839 | 10.5073 | 8.1155 | 5.3022 | 1.1185 | -3.7978 | -8.9855 | -12.9121 | -32.8794 | -51.7886 | -80.9294 | 4.242 | 1.1267 | -1.3488 | -4.3243 | -7.8733 | -13.4825 | -19.8998 | -26.5835 | -31.7437 | -53.9182 | -67.1672 | -77.2906
|  | FAREHAM (MAIN) BSP | HT |  |  |  |  | 5.1724 | 2.203 | -0.98578 | -4.6899 | -8.9735 | -14.0082 | -19.9041 | -26.4623 | -33.0144 | -62.3939 | -79.2593 | -88.5552 | 16.4196 | 14.8247 | 13.1104 | 11.1196 | 8.5522 | 6.0573 | 2.8981 | -0.91819 | -4.7172 | -20.6559 | -28.6886 | -32.8457 | 5.7094 | 3.1073 | 0.28589 | -2.9978 | -6.8294 | -11.1937 | -16.3672 | -22.257 | -28.1264 | -54.407 | -69.709 | -78.2039
|  | FAREHAM (MAIN) BSP | HE |  |  |  |  | 5.4907 | 2.7785 | -0.099047 | -3.5225 | -7.0797 | -11.1858 | -16.2429 | -22.3337 | -28.4144 | -55.299 | -70.4776 | -77.5858 | 16.0063 | 14.1726 | 12.2308 | 9.9134 | 7.4267 | 4.7543 | 1.3716 | -2.9059 | -7.309 | -29.7304 | -49.407 | -76.8008 | 5.9379 | 3.5339 | 0.9614 | -2.0957 | -5.26 | -8.8243 | -13.2651 | -18.6988 | -24.1498 | -48.2498 | -61.9825 | -68.2406
|  | FAREHAM (MAIN) BSP | CF |  |  |  |  | 7.3254 | 5.7561 | 4.0061 | 2.0744 | -0.19803 | -2.3929 | -3.8817 | -6.1837 | -9.4235 | -33.0593 | -49.4286 | -63.9327 | 16.8247 | 15.4961 | 13.9839 | 12.2839 | 10.1349 | 7.7104 | 5.7869 | 3.1645 | -0.2437 | -25.1427 | -57.2764 | -112.6774 | 7.5767 | 6.1767 | 4.6104 | 2.8798 | 0.8165 | -1.1753 | -2.4202 | -4.4386 | -7.3417 | -28.3213 | -42.9957 | -55.7896
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | FAREHAM (RESERVE) BSP | MINIMUM HEADROOM | SU 56534 04031 | NO | YES | 39.545 | 14.1728 | 12.2626 | 10.9922 | 8.8126 | 6.982 | 3.7034 | 0.22179 | -3.1282 | -5.4976 | -17.4098 | -27.8802 | -33.8211 | 21.3585 | 19.8779 | 18.9024 | 17.0912 | 15.533 | 13.1249 | 10.4912 | 7.8749 | 5.9391 | -4.8588 | -21.5272 | -58.4649 | 14.3473 | 12.43 | 11.3075 | 9.2095 | 7.4881 | 4.4422 | 1.1453 | -2.0507 | -4.1956 | -14.567 | -23.7047 | -28.5476
|  | FAREHAM (RESERVE) BSP | EE |  |  |  |  | 14.1728 | 12.2626 | 10.9922 | 8.8126 | 6.982 | 3.7034 | 0.22179 | -3.1282 | -5.4976 | -17.4098 | -26.2027 | -33.2935 | 21.3585 | 19.8779 | 18.9024 | 17.0912 | 15.533 | 13.1249 | 10.4912 | 7.8749 | 5.9391 | -4.8588 | -17.0629 | -36.6098 | 14.3473 | 12.43 | 11.3075 | 9.2095 | 7.4881 | 4.4422 | 1.1453 | -2.0507 | -4.1956 | -14.567 | -22.1905 | -28.1211
|  | FAREHAM (RESERVE) BSP | HT |  |  |  |  | 14.9595 | 13.5891 | 12.0493 | 10.3004 | 8.7055 | 6.1269 | 3.2391 | 0.72281 | -2.0425 | -17.3119 | -27.8802 | -33.8211 | 22.2646 | 21.3983 | 20.4361 | 19.3575 | 18.3698 | 16.9769 | 15.2993 | 13.8463 | 12.1667 | 3.7198 | -1.4476 | -3.9058 | 15.3973 | 14.08 | 12.5698 | 10.8657 | 9.3861 | 7.1432 | 4.483 | 2.2269 | -0.368 | -14.2894 | -23.7047 | -28.5476
|  | FAREHAM (RESERVE) BSP | HE |  |  |  |  | 15.0595 | 13.6218 | 12.1585 | 10.4514 | 9.3646 | 6.8432 | 4.1953 | 1.9238 | -0.5578 | -13.4833 | -22.6711 | -26.6384 | 21.9922 | 20.8136 | 19.6473 | 18.2636 | 17.3218 | 15.5034 | 13.5228 | 11.7249 | 9.6249 | -2.5854 | -15.4598 | -33.6578 | 15.4657 | 14.0993 | 12.6585 | 11.0075 | 10.0891 | 7.7779 | 5.3208 | 3.282 | 0.93914 | -10.8772 | -18.8139 | -22.0456
|  | FAREHAM (RESERVE) BSP | CF |  |  |  |  | 16.1208 | 15.1973 | 14.2779 | 13.1861 | 12.1289 | 11.2687 | 10.4157 | 9.0922 | 7.831 | -0.72821 | -9.8476 | -17.9986 | 22.4565 | 21.5136 | 20.5187 | 19.3483 | 18.1187 | 16.884 | 15.5718 | 13.8606 | 12.0861 | -0.51596 | -21.5272 | -58.4649 | 16.4269 | 15.5014 | 14.6055 | 13.5106 | 12.434 | 11.6555 | 10.883 | 9.6004 | 8.3544 | 0.282 | -7.7935 | -14.8588
FLEET-BRAMLEY GSP | FERNHURST BSP | FERNHURST BSP | MINIMUM HEADROOM | SU 72730 39772 | NO | NO | 41.363 | 68.5284 | 67.5182 | 66.7631 | 65.5835 | 64.2978 | 62.5417 | 61.107 | 59.3733 | 58.1325 | 51.2151 | 46.3845 | 43.908 | 74.5766 | 73.8715 | 73.3756 | 72.5746 | 71.6899 | 70.5225 | 69.5613 | 68.3368 | 67.4827 | 62.7011 | 58.1256 | 45.8378 | 69.0501 | 68.1021 | 67.4297 | 66.3368 | 65.1409 | 63.4909 | 62.1735 | 60.5154 | 59.4092 | 53.4317 | 49.2756 | 47.2348
|  | FERNHURST BSP | EE |  |  |  |  | 68.5284 | 67.5182 | 66.7631 | 65.5835 | 64.2978 | 62.5417 | 61.107 | 59.3733 | 58.1325 | 51.2151 | 47.2325 | 44.7417 | 74.5766 | 73.8715 | 73.3756 | 72.5746 | 71.6899 | 70.5225 | 69.5613 | 68.3368 | 67.4827 | 62.7011 | 58.2888 | 52.045 | 69.0501 | 68.1021 | 67.4297 | 66.3368 | 65.1409 | 63.4909 | 62.1735 | 60.5154 | 59.4092 | 53.4317 | 50.0062 | 47.9195
|  | FERNHURST BSP | HT |  |  |  |  | 68.9764 | 68.1764 | 67.2559 | 66.2733 | 65.4172 | 63.861 | 62.3784 | 60.7906 | 59.1437 | 51.2182 | 46.3845 | 43.908 | 75.0348 | 74.5746 | 74.0266 | 73.4521 | 73.0113 | 72.2001 | 71.3868 | 70.495 | 69.5113 | 65.2909 | 62.946 | 61.9327 | 69.5072 | 68.7746 | 67.9388 | 67.0501 | 66.3072 | 64.9123 | 63.5572 | 62.1052 | 60.5909 | 53.5011 | 49.2756 | 47.2348
|  | FERNHURST BSP | HE |  |  |  |  | 69.0406 | 68.2774 | 67.4212 | 66.4702 | 65.6896 | 64.3631 | 63.0621 | 61.6886 | 60.2723 | 53.0294 | 49.4927 | 47.6743 | 74.9337 | 74.4052 | 73.8144 | 73.1613 | 72.6644 | 71.8317 | 70.9797 | 70.0562 | 69.0501 | 63.7654 | 59.5021 | 53.4562 | 69.5572 | 68.8603 | 68.0807 | 67.2195 | 66.5399 | 65.3511 | 64.1623 | 62.895 | 61.5888 | 55.1256 | 52.1164 | 50.6031
|  | FERNHURST BSP | CF |  |  |  |  | 69.4682 | 68.909 | 68.3366 | 67.6692 | 66.907 | 66.1325 | 65.7549 | 64.9651 | 64.1743 | 59.1457 | 54.8855 | 50.7539 | 75.1348 | 74.6735 | 74.2021 | 73.6725 | 73.047 | 72.3674 | 71.9409 | 71.196 | 70.4297 | 65.2674 | 58.1256 | 45.8378 | 69.949 | 69.4307 | 68.9072 | 68.3021 | 67.6164 | 66.9123 | 66.5868 | 65.8541 | 65.1235 | 60.4939 | 56.8092 | 53.2041
LOVEDEAN GSP | FORT WIDLEY BSP | FORT WIDLEY BSP | MINIMUM HEADROOM | SU 64948 05441 | NO | YES | 16.472 | 38.3427 | 75.5529 | 73.9274 | 72.2937 | 70.8692 | 68.606 | 66.159 | 63.7101 | 61.7978 | 52.1631 | 45.4111 | 42.4417 | 43.9652 | 79.7376 | 78.5488 | 77.3182 | 76.2856 | 74.7152 | 72.9509 | 71.1437 | 69.8172 | 62.4743 | 51.6223 | 27.9203 | 37.8958 | 74.0886 | 72.6509 | 71.1948 | 69.955 | 67.9264 | 65.7152 | 63.4958 | 61.8162 | 53.5325 | 47.6458 | 45.1794
|  | FORT WIDLEY BSP | EE |  |  |  |  | 38.3427 | 75.5529 | 73.9274 | 72.2937 | 70.8692 | 68.606 | 66.159 | 63.7101 | 61.7978 | 52.7284 | 46.6896 | 43.8254 | 43.9652 | 79.7376 | 78.5488 | 77.3182 | 76.2856 | 74.7152 | 72.9509 | 71.1437 | 69.8172 | 62.4743 | 54.6641 | 42.8713 | 37.8958 | 74.0886 | 72.6509 | 71.1948 | 69.955 | 67.9264 | 65.7152 | 63.4958 | 61.8162 | 53.8886 | 48.6907 | 46.2825
|  | FORT WIDLEY BSP | HT |  |  |  |  | 38.8019 | 75.7448 | 74.1713 | 73.0366 | 71.4203 | 69.3019 | 67.3917 | 65.1907 | 62.9192 | 52.1631 | 45.4111 | 42.4417 | 44.7223 | 80.4774 | 79.5458 | 79.0019 | 78.0682 | 76.9427 | 75.9692 | 74.7335 | 73.4101 | 67.5274 | 64.3692 | 62.9407 | 38.3958 | 74.3437 | 72.9723 | 72.0325 | 70.6233 | 68.7621 | 67.0907 | 65.1366 | 63.109 | 53.5325 | 47.6458 | 45.1794
|  | FORT WIDLEY BSP | HE |  |  |  |  | 39.0141 | 76.0703 | 74.605 | 73.6029 | 72.1264 | 70.3101 | 68.6672 | 66.7213 | 64.7631 | 55.508 | 49.4927 | 47.0203 | 44.5713 | 80.2284 | 79.1999 | 78.5356 | 77.4723 | 76.2274 | 75.0968 | 73.6662 | 72.1703 | 63.8703 | 55.8305 | 44.2458 | 38.5611 | 74.6009 | 73.3233 | 72.4927 | 71.1999 | 69.5907 | 68.157 | 66.4182 | 64.6662 | 56.407 | 51.1907 | 49.1427
|  | FORT WIDLEY BSP | CF |  |  |  |  | 39.8662 | 77.4713 | 76.5376 | 75.9774 | 75.1407 | 74.309 | 73.3325 | 72.2907 | 71.5499 | 64.3499 | 57.209 | 50.8366 | 44.9458 | 80.8417 | 80.0203 | 79.4743 | 78.6203 | 77.6488 | 76.5141 | 75.2968 | 74.2835 | 65.3243 | 51.6223 | 27.9203 | 39.2978 | 75.8192 | 75.0162 | 74.5611 | 73.8386 | 73.1131 | 72.255 | 71.3223 | 70.6937 | 64.3274 | 57.9815 | 52.4294
MELKSHAM GSP | FROME BSP | FROME BSP | MINIMUM HEADROOM | ST 78803 48019 | NO | NO | 28.094 | 3.8969 | 0.81631 | -2.6888 | 108.0701 | 103.9763 | 98.9844 | 93.4722 | 87.9355 | 84.0304 | 64.7395 | 49.2967 | 41.0161 | 16.6808 | 14.6227 | 12.3176 | 119.8859 | 117.3033 | 114.2523 | 110.9115 | 107.3461 | 104.7339 | 90.8778 | 76.0319 | 39.8727 | 0.3339 | -2.5477 | -5.7232 | 102.6502 | 98.8329 | 94.2043 | 89.137 | 83.941 | 80.4502 | 64.0737 | 51.1176 | 44.2859
|  | FROME BSP | EE |  |  |  |  | 3.8969 | 0.81631 | -2.6888 | 108.0701 | 103.9763 | 98.9844 | 93.4722 | 87.9355 | 84.0304 | 64.8467 | 51.515 | 42.664 | 16.6808 | 14.6227 | 12.3176 | 119.8859 | 117.3033 | 114.2523 | 110.9115 | 107.3461 | 104.7339 | 90.8778 | 77.3033 | 58.3972 | 0.3339 | -2.5477 | -5.7232 | 102.6502 | 98.8329 | 94.2043 | 89.137 | 83.941 | 80.4502 | 64.0737 | 53.1625 | 45.6686
|  | FROME BSP | HT |  |  |  |  | 4.9602 | 2.0643 | -1.4531 | 109.7538 | 106.3997 | 101.8814 | 97.2406 | 92.4885 | 87.8018 | 64.7395 | 49.2967 | 41.0161 | 17.7023 | 16.0676 | 13.987 | 122.087 | 120.2421 | 117.8288 | 115.3431 | 112.7064 | 110.1584 | 98.4319 | 91.1237 | 87.3451 | 1.4635 | -1.0294 | -4.0181 | 104.8696 | 101.9023 | 97.8288 | 93.6829 | 89.2645 | 84.8492 | 64.2176 | 51.1176 | 44.2859
|  | FROME BSP | HE |  |  |  |  | 5.1357 | 2.3337 | -0.98879 | 110.4252 | 107.2844 | 103.3293 | 98.9926 | 94.6518 | 90.4426 | 69.5038 | 56.0783 | 50.3855 | 17.5706 | 15.6941 | 13.4615 | 121.4125 | 119.4115 | 116.8961 | 114.1798 | 111.3135 | 108.4186 | 93.0706 | 79.0829 | 61.7217 | 1.6533 | -0.79467 | -3.6263 | 105.4625 | 102.7084 | 99.1196 | 95.2655 | 91.238 | 87.2135 | 68.5951 | 57.3778 | 52.4247
|  | FROME BSP | CF |  |  |  |  | 6.4857 | 4.6061 | 2.3684 | 114.4875 | 112.5406 | 110.913 | 108.514 | 106.1589 | 103.5446 | 88.0048 | 73.6457 | 61.0977 | 18.1757 | 16.8329 | 15.0206 | 123.1359 | 121.5461 | 119.9757 | 117.8696 | 115.7584 | 113.3951 | 98.1819 | 76.0319 | 39.8727 | 2.8604 | 1.2268 | -0.75589 | 108.9472 | 107.2635 | 105.787 | 103.5135 | 101.3533 | 98.8737 | 84.4421 | 71.8788 | 61.3257
LOVEDEAN GSP | HAVANT BSP | HAVANT BSP | MINIMUM HEADROOM | SU 70625 05720 | NO | YES | 33.21 | 13.6929 | 9.45 | 5.6061 | 1.4959 | -3.3898 | -10.4602 | -18.0745 | -25.6112 | -31.5347 | -60.7786 | -82.698 | -92.1796 | 36.3104 | 33.0502 | 30.0513 | 26.7023 | 22.6125 | 17.5258 | 11.8166 | 6.3298 | 2.2053 | -19.5569 | -51.4732 | -120.2691 | 18.6755 | 14.7112 | 11.1102 | 7.1735 | 2.352 | -4.3051 | -11.6674 | -18.6735 | -23.8469 | -48.048 | -66.7041 | -74.449
|  | HAVANT BSP | EE |  |  |  |  | 13.6929 | 9.45 | 5.6061 | 1.4959 | -3.3898 | -10.4602 | -18.0745 | -25.6112 | -31.5347 | -59.3469 | -78.7225 | -88.4847 | 36.3104 | 33.0502 | 30.0513 | 26.7023 | 22.6125 | 17.5258 | 11.8166 | 6.3298 | 2.2053 | -19.5569 | -43.3794 | -77.8385 | 18.6755 | 14.7112 | 11.1102 | 7.1735 | 2.352 | -4.3051 | -11.6674 | -18.6735 | -23.8469 | -47.4255 | -63.3378 | -71.5225
|  | HAVANT BSP | HT |  |  |  |  | 14.5204 | 10.8235 | 7.2173 | 3.4582 | -0.93266 | -6.3531 | -13.0602 | -20.1112 | -27.1265 | -60.7786 | -82.698 | -92.1796 | 37.736 | 35.4033 | 33.2064 | 30.8992 | 28.1237 | 25.4513 | 21.7655 | 17.6798 | 13.5043 | -4.8294 | -15.0294 | -19.3477 | 19.6949 | 16.4194 | 13.2184 | 9.8704 | 5.8112 | 1.1265 | -4.9571 | -11.3806 | -17.8286 | -48.048 | -66.7041 | -74.449
|  | HAVANT BSP | HE |  |  |  |  | 15.3102 | 11.4224 | 8.0163 | 4.55 | 0.30408 | -4.4357 | -10.3663 | -16.6571 | -22.9276 | -52.15 | -72.2031 | -79.8857 | 37.639 | 34.6298 | 32.0778 | 29.4115 | 26.0931 | 22.887 | 18.6809 | 14.136 | 9.439 | -16.0018 | -41.0436 | -74.5253 | 20.3949 | 16.9265 | 13.8949 | 10.7775 | 6.8439 | 2.7153 | -2.7245 | -8.5235 | -14.3378 | -40.7265 | -57.4643 | -63.7398
|  | HAVANT BSP | CF |  |  |  |  | 17.5235 | 15.7388 | 13.0194 | 11.0194 | 8.7429 | 5.7816 | 2.7337 | 0.098976 | -3.3153 | -22.3418 | -46.7296 | -65.9939 | 38.637 | 36.8758 | 34.2839 | 32.1951 | 29.6962 | 26.4492 | 23.0196 | 19.8655 | 15.9472 | -9.3079 | -51.4732 | -120.2691 | 22.3878 | 20.8245 | 18.3143 | 16.4786 | 14.4051 | 11.6704 | 8.8224 | 6.4439 | 3.1337 | -15.3 | -36.1867 | -52.348
COWLEY GSP | HEADINGTON BSP | HEADINGTON BSP | MINIMUM HEADROOM | SP 54454 08145 | NO | NO | 78.635 | 10.1267 | 7.8542 | 5.6032 | 2.4563 | -1.2346 | -8.5835 | -14.557 | -20.8172 | -28.4356 | -47.9529 | -59.157 | -67.5621 | 10.5779 | 8.9055 | 7.382 | 5.3004 | 1.4861 | -3.3772 | -7.7057 | -14.6792 | -21.7864 | -40.7394 | -57.2761 | -81.1455 | 7.1249 | 5.0371 | 2.8953 | 0.012629 | -4.2425 | -10.3149 | -15.867 | -22.8261 | -30.2874 | -49.2721 | -61.0017 | -70.97
|  | HEADINGTON BSP | EE |  |  |  |  | 10.1267 | 7.8542 | 5.6032 | 2.4563 | -1.2039 | -8.2539 | -13.658 | -19.159 | -25.0784 | -42.4417 | -56.1274 | -59.5254 | 10.5779 | 8.9055 | 7.382 | 5.3004 | 2.4565 | -2.37 | -6.2455 | -10.6251 | -15.4374 | -31.6374 | -51.017 | -68.3006 | 7.1249 | 5.0371 | 2.8953 | 0.012629 | -3.6772 | -9.9006 | -14.7343 | -19.8935 | -25.3282 | -41.467 | -56.1639 | -60.2455
|  | HEADINGTON BSP | HT |  |  |  |  | 10.5583 | 8.8012 | 6.391 | 3.4705 | -0.97537 | -8.5835 | -14.557 | -19.4835 | -27.7172 | -44.2774 | -58.5784 | -65.7692 | 11.4075 | 10.1932 | 8.6228 | 6.8616 | 3.3545 | -1.7598 | -6.2221 | -9.5812 | -16.4476 | -27.8874 | -40.5333 | -48.3241 | 7.5779 | 5.8932 | 3.5973 | 0.86977 | -3.6721 | -10.3149 | -15.867 | -20.219 | -27.9527 | -43.9761 | -59.2282 | -67.471
|  | HEADINGTON BSP | HE |  |  |  |  | 11.1889 | 9.1542 | 6.4042 | 3.543 | -1.2346 | -8.0315 | -13.4897 | -20.8172 | -28.4356 | -47.9529 | -59.157 | -67.5621 | 11.4014 | 9.8147 | 7.6892 | 5.6504 | 1.4861 | -3.3772 | -7.7057 | -14.6792 | -21.7864 | -40.7394 | -57.2761 | -80.0466 | 8.0494 | 6.0902 | 3.3932 | 0.69426 | -4.2425 | -10.2057 | -15.2833 | -22.8261 | -30.2874 | -49.2721 | -61.0017 | -70.97
|  | HEADINGTON BSP | CF |  |  |  |  | 12.5399 | 11.643 | 10.4726 | 8.7052 | 6.5236 | 2.4277 | -0.67741 | -4.2856 | -8.5795 | -27.7488 | -38.7846 | -48.6539 | 12.0953 | 11.1994 | 10.2218 | 8.783 | 6.9677 | 3.4443 | 0.54426 | -2.5925 | -6.5476 | -27.0078 | -47.9466 | -81.1455 | 9.3228 | 8.4749 | 7.4412 | 5.7973 | 3.7667 | -0.16492 | -3.0353 | -6.2445 | -10.1445 | -27.9598 | -38.8149 | -48.4374
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU 84773 92191 | NO | NO | 26.979 | -3.3526 | -5.6281 | -7.4669 | -10.0995 | -13.1189 | -17.2842 | -21.8903 | -27.4301 | -31.3893 | -55.3209 | -77.2812 | -90.6424 | 18.5375 | 16.6017 | 15.0262 | 12.762 | 10.0905 | 7.0007 | 3.664 | -1.6064 | -6.7064 | -27.7564 | -49.4156 | -89.1687 | -4.936 | -7.238 | -9.084 | -11.7268 | -14.7105 | -18.688 | -22.9952 | -28.3911 | -33.2829 | -55.9278 | -76.4952 | -89.7952
|  | HIGH WYCOMBE BSP | EE |  |  |  |  | -3.3526 | -5.6281 | -7.4669 | -10.0995 | -13.1189 | -17.2842 | -21.8903 | -27.4301 | -31.3893 | -52.3505 | -72.673 | -84.6822 | 18.5375 | 16.6017 | 15.0262 | 12.762 | 10.0905 | 7.0007 | 3.664 | -0.75029 | -3.8115 | -21.3666 | -45.5993 | -71.4472 | -4.936 | -7.238 | -9.084 | -11.7268 | -14.7105 | -18.688 | -22.9952 | -28.3911 | -32.1268 | -51.6891 | -71.5993 | -82.9432
|  | HIGH WYCOMBE BSP | HT |  |  |  |  | -2.0414 | -3.9781 | -6.1893 | -8.3271 | -11.3975 | -15.5475 | -20.2077 | -24.4363 | -29.4271 | -55.3209 | -77.2812 | -90.6424 | 19.7252 | 18.9038 | 17.2568 | 15.8017 | 13.0905 | 10.4252 | 7.2864 | 4.7303 | 1.2364 | -14.8942 | -30.4421 | -40.1544 | -3.5207 | -5.3452 | -7.5278 | -9.6268 | -12.9217 | -16.9176 | -21.4707 | -25.4625 | -30.4023 | -54.9778 | -76.4952 | -89.7952
|  | HIGH WYCOMBE BSP | HE |  |  |  |  | -1.9414 | -3.7924 | -6.124 | -8.3179 | -11.5465 | -15.1016 | -19.4301 | -25.4301 | -30.8189 | -54.4648 | -72.4781 | -84.875 | 19.5201 | 18.2354 | 16.0864 | 14.1354 | 10.7671 | 7.9283 | 4.3293 | -1.6064 | -6.7064 | -27.7564 | -49.4156 | -78.9921 | -3.4421 | -5.2176 | -7.5758 | -9.7789 | -13.3136 | -16.7932 | -21.1105 | -27.6054 | -33.2829 | -55.9278 | -73.1238 | -86.2156
|  | HIGH WYCOMBE BSP | CF |  |  |  |  | -0.59544 | -1.676 | -2.7281 | -4.1383 | -5.6373 | -7.2832 | -8.4863 | -10.4373 | -12.3148 | -26.6893 | -43.1658 | -58.5587 | 20.0579 | 19.3426 | 18.1915 | 16.6181 | 14.7936 | 12.6671 | 10.862 | 8.3538 | 5.8191 | -12.636 | -41.6983 | -89.1687 | -2.2023 | -3.2187 | -4.2095 | -5.6564 | -7.2176 | -8.9452 | -10.1666 | -12.2054 | -14.1146 | -28.0574 | -43.887 | -58.3442
LOVEDEAN GSP | HUNSTON BSP | HUNSTON BSP | MINIMUM HEADROOM | SU 86946 02627 | NO | YES | 36.915 | 22.0176 | 19.9442 | 17.5584 | 15.0595 | 11.8462 | 7.7003 | 2.8646 | -1.9977 | -5.6252 | -26.9436 | -42.3375 | -50.7191 | 28.4564 | 27.0146 | 25.3799 | 23.8074 | 21.534 | 18.8554 | 15.5197 | 12.1237 | 9.7493 | -3.6467 | -20.2048 | -58.2742 | 18.5278 | 16.5584 | 14.2819 | 12.1635 | 9.0554 | 5.3248 | 0.81762 | -3.6967 | -6.8507 | -24.3977 | -37.6314 | -44.7956
|  | HUNSTON BSP | EE |  |  |  |  | 22.0176 | 19.9442 | 17.5584 | 15.1748 | 11.8462 | 7.7003 | 2.8646 | -1.9977 | -5.6252 | -24.9314 | -39.1569 | -48.9926 | 28.4564 | 27.0146 | 25.3799 | 23.8074 | 21.534 | 18.8554 | 15.5197 | 12.1237 | 9.7493 | -3.6467 | -18.2609 | -38.6038 | 18.5278 | 16.5584 | 14.2819 | 12.1635 | 9.0554 | 5.3248 | 0.81762 | -3.6967 | -6.8507 | -23.114 | -35.0732 | -43.5681
|  | HUNSTON BSP | HT |  |  |  |  | 22.7993 | 20.6554 | 17.9686 | 15.0595 | 12.6391 | 8.436 | 4.7615 | 0.39722 | -3.6967 | -26.9436 | -42.3375 | -50.7191 | 29.5799 | 28.3982 | 26.9217 | 25.2717 | 24.0829 | 21.9309 | 20.1829 | 17.8697 | 15.7625 | 3.8799 | -3.1344 | -6.9436 | 19.2462 | 17.4299 | 15.1666 | 12.6686 | 10.6095 | 6.9166 | 3.6737 | -0.17013 | -3.864 | -24.3977 | -37.6314 | -44.7956
|  | HUNSTON BSP | HE |  |  |  |  | 23.2237 | 21.3411 | 19.1074 | 16.5544 | 14.3666 | 10.8054 | 7.7442 | 3.9697 | 0.52069 | -19.9048 | -34.316 | -40.9058 | 29.4166 | 28.1207 | 26.6207 | 24.8523 | 23.4329 | 21.134 | 19.185 | 16.6105 | 14.2003 | -1.2181 | -16.1936 | -35.2181 | 19.5809 | 17.9635 | 16.0605 | 13.8686 | 11.9931 | 8.8309 | 6.1809 | 2.7125 | -0.41809 | -18.462 | -30.7528 | -36.3293
|  | HUNSTON BSP | CF |  |  |  |  | 24.737 | 23.538 | 22.4207 | 21.2186 | 19.9207 | 18.9452 | 17.6401 | 16.4105 | 14.4942 | -0.12421 | -16.5691 | -29.363 | 30.1115 | 29.087 | 28.0625 | 26.9013 | 25.5197 | 24.2176 | 22.6513 | 21.1615 | 19.1125 | 3.8819 | -20.2048 | -58.2742 | 20.8942 | 19.8952 | 18.936 | 17.9003 | 16.5799 | 15.6146 | 14.3482 | 13.2809 | 11.4584 | -1.7222 | -15.6477 | -26.3456
FAWLEY GSP | LANGLEY BSP | LANGLEY BSP | MINIMUM HEADROOM | SU 45185 01376 | NO | NO | 10.167 | 14.4152 | 13.8601 | 12.9672 | 12.3356 | 11.2162 | 9.3458 | 7.3376 | 4.9897 | 3.3029 | -6.9399 | -15.7879 | -21.3195 | 13.2223 | 12.8458 | 12.254 | 11.8111 | 10.6305 | 9.4968 | 8.1815 | 5.9866 | 3.9162 | -4.5358 | -13.0971 | -26.2154 | 10.006 | 9.5489 | 8.8652 | 8.3305 | 7.2091 | 5.4254 | 3.5621 | 1.3101 | -0.7389 | -10.2634 | -18.7705 | -24.3042
|  | LANGLEY BSP | EE |  |  |  |  | 14.4152 | 13.8601 | 12.9672 | 12.3356 | 11.2162 | 9.3458 | 7.3376 | 4.9897 | 3.3029 | -5.042 | -13.6379 | -18.9338 | 13.2223 | 12.8458 | 12.254 | 11.8111 | 10.8876 | 9.5376 | 8.1815 | 6.4295 | 5.256 | -1.4246 | -10.9001 | -20.7134 | 10.006 | 9.5489 | 8.8652 | 8.3305 | 7.2131 | 5.4254 | 3.5621 | 1.3101 | -0.24196 | -8.1042 | -16.5787 | -21.5379
|  | LANGLEY BSP | HT |  |  |  |  | 14.8387 | 14.1387 | 13.2876 | 12.8621 | 11.6223 | 9.6009 | 7.7795 | 5.8489 | 3.6703 | -6.9399 | -15.7879 | -21.3195 | 13.6887 | 13.2652 | 12.704 | 12.5029 | 11.4958 | 10.308 | 9.2397 | 8.2346 | 6.8029 | 0.32437 | -5.8011 | -9.7664 | 10.3193 | 9.704 | 8.9427 | 8.556 | 7.3376 | 5.4897 | 3.754 | 2.0774 | -0.0093061 | -10.0889 | -18.7705 | -24.3042
|  | LANGLEY BSP | HE |  |  |  |  | 14.955 | 14.2703 | 13.3876 | 12.9387 | 11.6264 | 10.0846 | 8.6744 | 5.9866 | 3.6336 | -6.1848 | -13.9971 | -19.4787 | 13.5999 | 13.057 | 12.308 | 11.9101 | 10.6305 | 9.4968 | 8.4366 | 5.9866 | 3.9162 | -4.5358 | -13.0971 | -24.4399 | 10.4254 | 9.7999 | 8.9764 | 8.5356 | 7.2091 | 5.7825 | 4.4223 | 1.6733 | -0.7389 | -10.2634 | -17.9022 | -23.7205
|  | LANGLEY BSP | CF |  |  |  |  | 15.5203 | 15.2009 | 14.7958 | 14.304 | 14.1182 | 13.5264 | 12.8591 | 12.1213 | 11.6927 | 5.4458 | -1.6083 | -7.9634 | 13.8489 | 13.5346 | 13.1376 | 12.6295 | 12.2764 | 11.5866 | 10.8376 | 10.0244 | 9.3642 | 2.1917 | -8.8777 | -26.2154 | 10.9213 | 10.6591 | 10.3182 | 9.9019 | 9.7029 | 9.1968 | 8.655 | 7.9917 | 7.5601 | 1.5346 | -5.2991 | -11.292
IVER 132KV GSP | LONGFORD BSP | LONGFORD BSP | MINIMUM HEADROOM | TQ 03910 76751 | NO | YES | 19.067 | 88.3488 | 87.1315 | 85.6968 | 84.0039 | 82.1162 | 80.1723 | 77.6733 | 75.2794 | 73.1049 | 64.7376 | 60.3427 | 58.4651 | 78.345 | 77.6348 | 76.6787 | 75.5562 | 74.296 | 73.0368 | 71.4031 | 69.8297 | 68.2246 | 61.9633 | 58.745 | 57.2603 | 77.1827 | 76.0184 | 74.6358 | 73.0103 | 71.196 | 69.3368 | 66.9389 | 64.644 | 62.5776 | 54.544 | 50.3531 | 48.5644
|  | LONGFORD BSP | EE |  |  |  |  | 88.3488 | 87.1315 | 85.6968 | 84.0039 | 82.1162 | 80.1723 | 77.6733 | 75.2794 | 73.1049 | 66.2141 | 64.6427 | 64.1794 | 78.345 | 77.6348 | 76.6787 | 75.5562 | 74.296 | 73.0368 | 71.4031 | 69.8297 | 68.2246 | 63.148 | 62.2399 | 61.9633 | 77.1827 | 76.0184 | 74.6358 | 73.0103 | 71.196 | 69.3368 | 66.9389 | 64.644 | 62.5776 | 56.0072 | 54.7042 | 54.4021
|  | LONGFORD BSP | HT |  |  |  |  | 89.5407 | 88.76 | 87.8611 | 86.7641 | 85.5356 | 84.0835 | 82.2723 | 80.3386 | 78.358 | 69.3866 | 65.3917 | 63.7856 | 78.9164 | 78.5899 | 78.1582 | 77.4736 | 76.6725 | 75.7654 | 74.6154 | 73.3776 | 72.1266 | 65.8031 | 63.1603 | 62.1562 | 78.2368 | 77.5848 | 76.7195 | 75.6736 | 74.4909 | 73.1021 | 71.3623 | 69.5093 | 67.6256 | 59.0399 | 55.5297 | 54.2103
|  | LONGFORD BSP | HE |  |  |  |  | 89.2784 | 88.3641 | 87.2988 | 86.009 | 84.5437 | 82.806 | 80.6264 | 78.2845 | 75.8376 | 64.7376 | 60.3427 | 58.4651 | 78.7746 | 78.347 | 77.7491 | 76.894 | 75.9174 | 74.7878 | 73.3623 | 71.8205 | 70.2225 | 61.9633 | 58.745 | 57.2603 | 78.0082 | 77.2042 | 76.1807 | 74.946 | 73.5389 | 71.8736 | 69.7776 | 67.5317 | 65.198 | 54.544 | 50.3531 | 48.5644
|  | LONGFORD BSP | CF |  |  |  |  | 90.2641 | 89.7815 | 89.209 | 88.5284 | 87.7376 | 86.8753 | 85.7162 | 84.4029 | 82.856 | 74.3519 | 66.8151 | 61.9978 | 79.1246 | 78.897 | 78.645 | 78.3266 | 77.9399 | 77.3909 | 76.6154 | 75.7317 | 74.697 | 69.044 | 63.3174 | 59.6072 | 78.8072 | 78.4052 | 77.9297 | 77.3603 | 76.6011 | 75.7736 | 74.6593 | 73.394 | 71.9184 | 63.7327 | 56.5062 | 51.9144
AMERSHAM GSP | LOUDWATER BSP | LOUDWATER BSP | MINIMUM HEADROOM | SU 90644 91247 | NO | YES | 15.511 | 47.7105 | 43.7309 | 41.8432 | 39.5779 | 37.0269 | 33.1289 | 28.9044 | 24.8636 | 21.986 | 5.8126 | -6.5344 | -13.3303 | 62.1169 | 60.1169 | 58.0557 | 56.5455 | 54.7291 | 52.1067 | 49.1271 | 46.1577 | 44.1883 | 33.3414 | 20.1271 | -13.077 | 48.2536 | 45.6006 | 42.8761 | 40.8761 | 38.5393 | 34.9169 | 30.9271 | 27.07 | 24.5087 | 10.9373 | 0.018939 | -5.6647
|  | LOUDWATER BSP | EE |  |  |  |  | 47.7105 | 43.7309 | 41.8432 | 39.5779 | 37.0269 | 33.1289 | 28.9044 | 24.8636 | 21.986 | 6.9554 | -3.9731 | -12.1262 | 62.1169 | 60.1169 | 58.0557 | 56.5455 | 54.7291 | 52.1067 | 49.1271 | 46.1577 | 44.1883 | 33.3414 | 21.9128 | 4.9434 | 48.2536 | 45.6006 | 42.8761 | 40.8761 | 38.5393 | 34.9169 | 30.9271 | 27.07 | 24.5087 | 11.7332 | 2.3047 | -4.6137
|  | LOUDWATER BSP | HT |  |  |  |  | 48.5779 | 45.833 | 43.7003 | 41.2309 | 38.6595 | 35.282 | 31.833 | 28.486 | 24.782 | 5.8126 | -6.5344 | -13.3303 | 63.2802 | 61.7189 | 60.6271 | 59.1985 | 57.6475 | 55.9332 | 54.1271 | 52.3414 | 50.1985 | 40.1169 | 34.6577 | 32.0761 | 49.2536 | 46.8353 | 45.0189 | 42.7842 | 40.4067 | 37.4373 | 34.3659 | 31.3863 | 27.9679 | 10.9373 | 0.018939 | -5.6647
|  | LOUDWATER BSP | HE |  |  |  |  | 48.7309 | 46.1085 | 44.1187 | 41.8024 | 39.384 | 36.6595 | 33.8432 | 31.1493 | 28.1085 | 12.0983 | 1.0371 | -4.1874 | 63.0047 | 61.2904 | 60.0557 | 58.4638 | 56.7291 | 54.9638 | 53.0659 | 51.1373 | 48.8108 | 35.9434 | 24.1577 | 8.2904 | 49.3761 | 47.0598 | 45.3761 | 43.274 | 41.0291 | 38.6108 | 36.0802 | 33.6414 | 30.774 | 16.3047 | 6.8251 | 2.4577
|  | LOUDWATER BSP | CF |  |  |  |  | 50.0167 | 48.1595 | 46.5473 | 45.2616 | 43.5881 | 42.0779 | 40.4656 | 39.6901 | 38.2513 | 27.9452 | 16.2922 | 5.5371 | 63.5659 | 62.1985 | 60.9026 | 59.9128 | 58.4536 | 56.8618 | 55.0557 | 53.923 | 52.0761 | 39.3924 | 20.1271 | -13.077 | 50.4475 | 48.8149 | 47.3455 | 46.3251 | 44.8149 | 43.3863 | 41.8047 | 41.1414 | 39.6924 | 29.9067 | 19.6822 | 10.6312
MANNINGTON GSP | LYTCHETT BSP | LYTCHETT BSP | MINIMUM HEADROOM | SY 97796 94214 | NO | NO | 13.96 | 19.0634 | 51.4981 | 50.2001 | 48.0277 | 45.6011 | 41.6389 | 38.0317 | 34.4389 | 31.6205 | 14.6624 | 2.7113 | -3.9529 | 27.4746 | 66.2593 | 65.3297 | 63.9715 | 62.4522 | 60.296 | 58.292 | 55.4746 | 53.4797 | 42.1858 | 28.0113 | -5.4407 | 17.5624 | 52.8981 | 51.7685 | 49.7981 | 47.6032 | 43.9624 | 40.4001 | 36.7052 | 34.1511 | 20.1797 | 9.6736 | 3.9328
|  | LYTCHETT BSP | EE |  |  |  |  | 19.0634 | 51.4981 | 50.2001 | 48.0277 | 45.6011 | 41.6389 | 38.0317 | 34.4389 | 31.6205 | 15.6868 | 4.7236 | -2.9999 | 27.4746 | 66.2593 | 65.3297 | 63.9715 | 62.4522 | 60.296 | 58.292 | 55.4746 | 53.4797 | 42.1858 | 30.3307 | 13.0981 | 17.5624 | 52.8981 | 51.7685 | 49.7981 | 47.6032 | 43.9624 | 40.4001 | 36.7052 | 34.1511 | 20.8532 | 11.3552 | 4.6644
|  | LYTCHETT BSP | HT |  |  |  |  | 19.7297 | 52.3971 | 50.5532 | 48.5317 | 46.692 | 43.1705 | 39.645 | 36.3113 | 32.8858 | 14.6624 | 2.7113 | -3.9529 | 28.3185 | 67.4532 | 66.5695 | 65.5389 | 64.5175 | 62.8654 | 61.246 | 59.5991 | 57.8889 | 49.396 | 43.9032 | 40.9154 | 18.2624 | 53.8644 | 52.2215 | 50.4062 | 48.8175 | 45.6909 | 42.543 | 39.5328 | 36.4317 | 20.1797 | 9.6736 | 3.9328
|  | LYTCHETT BSP | HE |  |  |  |  | 19.9093 | 52.7297 | 51.0654 | 49.1062 | 47.3685 | 44.394 | 41.3113 | 38.4266 | 35.5175 | 19.2134 | 7.894 | 2.7695 | 28.1726 | 67.2389 | 66.2777 | 65.1042 | 63.9471 | 62.1654 | 60.3164 | 58.4205 | 56.4481 | 43.9368 | 31.5328 | 15.3583 | 18.395 | 54.1175 | 52.6185 | 50.8583 | 49.346 | 46.693 | 43.9277 | 41.3032 | 38.645 | 24.0348 | 14.1246 | 9.7266
|  | LYTCHETT BSP | CF |  |  |  |  | 21.0379 | 54.4828 | 53.6144 | 52.5144 | 51.1256 | 49.9695 | 48.9113 | 47.546 | 46.1501 | 35.442 | 23.944 | 13.0695 | 28.7981 | 68.1644 | 67.6562 | 67.0368 | 65.8675 | 64.6073 | 63.4328 | 62.0195 | 60.3909 | 47.642 | 28.0113 | -5.4407 | 19.4175 | 55.6858 | 54.892 | 53.9022 | 52.6593 | 51.6399 | 50.7032 | 49.4562 | 48.1858 | 38.0562 | 27.9032 | 18.7022
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | MAIDENHEAD BSP | MINIMUM HEADROOM | SU 86592 79883 | NO | NO | 37.466 | 31.3779 | 28.6779 | 25.3279 | 20.9932 | 17.0626 | 12.5504 | 8.0861 | 4.4402 | 1.7759 | -10.2558 | -19.0762 | -21.9884 | 44.269 | 42.3567 | 40.2312 | 37.52 | 35.0669 | 32.1108 | 29.0353 | 26.2761 | 24.369 | 14.822 | 2.1384 | -28.4545 | 27.97 | 25.5149 | 22.5996 | 18.7904 | 15.3476 | 11.2578 | 7.1302 | 3.6506 | 1.2761 | -9.1167 | -16.6229 | -18.9841
|  | MAIDENHEAD BSP | EE |  |  |  |  | 31.3779 | 28.6779 | 25.3279 | 20.9932 | 17.0626 | 12.5504 | 8.0861 | 4.4402 | 1.7759 | -10.2558 | -17.8333 | -19.6884 | 44.269 | 42.3567 | 40.2312 | 37.52 | 35.0669 | 32.1108 | 29.0353 | 26.2761 | 24.369 | 14.822 | 4.9118 | -9.2045 | 27.97 | 25.5149 | 22.5996 | 18.7904 | 15.3476 | 11.2578 | 7.1302 | 3.6506 | 1.2761 | -9.1167 | -15.4637 | -17.1014
|  | MAIDENHEAD BSP | HT |  |  |  |  | 32.08 | 29.3922 | 26.0738 | 22.2116 | 18.2024 | 14.834 | 11.4055 | 8.3606 | 5.2912 | -9.917 | -19.0762 | -21.9884 | 45.4639 | 43.7812 | 41.9088 | 39.9292 | 37.6751 | 35.92 | 34.0853 | 32.1884 | 30.2363 | 21.4904 | 17.0159 | 15.5282 | 29.0027 | 26.5792 | 23.6894 | 20.5108 | 16.9996 | 14.0955 | 11.0629 | 8.1986 | 5.2843 | -8.6341 | -16.6229 | -18.9841
|  | MAIDENHEAD BSP | HE |  |  |  |  | 32.4534 | 30.0412 | 27.0718 | 23.7075 | 19.8851 | 16.4983 | 13.1259 | 10.2167 | 7.2524 | -5.9272 | -13.5649 | -15.9782 | 45.2986 | 43.5414 | 41.6302 | 39.6986 | 37.2904 | 35.1659 | 33.0047 | 30.8761 | 28.5598 | 17.0098 | 6.6394 | -7.5718 | 29.2629 | 27.0506 | 24.4547 | 21.672 | 18.3251 | 15.4312 | 12.4874 | 9.7496 | 6.9333 | -5.1708 | -11.5973 | -13.5239
|  | MAIDENHEAD BSP | CF |  |  |  |  | 33.8891 | 32.4891 | 30.8096 | 28.5902 | 26.1667 | 23.0759 | 20.4136 | 19.0677 | 17.48 | 7.4218 | -2.8802 | -12.3241 | 45.9884 | 44.6741 | 43.3027 | 41.6649 | 40.0149 | 37.7129 | 35.6159 | 34.1231 | 32.3506 | 20.1476 | 2.1384 | -28.4545 | 30.5078 | 29.1363 | 27.5792 | 25.6118 | 23.6241 | 20.9496 | 18.6955 | 17.4537 | 15.9129 | 6.3914 | -2.6402 | -10.7555
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON BSP | MINIMUM HEADROOM | SU 07523 05221 | NO | NO | 24.193 | 21.9873 | 18.7291 | 15.4516 | 10.9403 | 4.8373 | -2.5392 | -8.9546 | -21.2882 | -31.276 | -72.7158 | -103.6148 | -127.5995 | 36.9312 | 34.5638 | 31.9026 | 28.9485 | 21.9271 | 16.9342 | 11.0628 | -1.725 | -11.3005 | -47.0556 | -80.8188 | -124.128 | 19.3363 | 16.2903 | 13.3056 | 9.122 | 2.1108 | -4.029 | -11.2086 | -25.2964 | -35.9821 | -76.4352 | -107.3209 | -134.4301
|  | MANNINGTON BSP | EE |  |  |  |  | 21.9873 | 18.7291 | 15.4516 | 10.9403 | 4.8812 | -2.5392 | -8.9546 | -17.7148 | -23.8444 | -58.1311 | -93.2076 | -111.1025 | 36.9312 | 34.5638 | 32.2475 | 28.9485 | 23.9005 | 18.322 | 14.0403 | 7.0261 | 2.5556 | -24.7331 | -64.1709 | -96.4382 | 19.3363 | 16.2903 | 13.3056 | 9.122 | 3.1842 | -3.9668 | -9.8505 | -18.4566 | -24.2586 | -56.5158 | -92.9648 | -111.0658
|  | MANNINGTON BSP | HT |  |  |  |  | 23.6281 | 20.2291 | 16.2179 | 13.0893 | 6.4577 | -0.6219 | -8.6505 | -15.4362 | -23.9403 | -65.6566 | -101.7739 | -123.6903 | 39.0087 | 36.7495 | 33.8485 | 32.0628 | 26.2669 | 21.4914 | 15.7842 | 11.675 | 5.4046 | -22.8015 | -52.4974 | -71.8382 | 21.2699 | 18.0332 | 14.1097 | 11.2995 | 4.3495 | -2.4923 | -10.4107 | -16.7637 | -25.1892 | -65.1729 | -102.429 | -126.2086
|  | MANNINGTON BSP | HE |  |  |  |  | 23.8761 | 20.2516 | 15.7914 | 12.1403 | 4.8373 | -1.3515 | -8.5117 | -21.2882 | -31.276 | -72.7158 | -103.6148 | -127.5995 | 38.6169 | 35.7597 | 31.9026 | 29.0628 | 21.9271 | 16.9342 | 11.0628 | -1.725 | -11.3005 | -47.0556 | -80.8188 | -124.128 | 21.4444 | 17.9332 | 13.4138 | 9.9465 | 2.1108 | -4.029 | -11.2086 | -25.2964 | -35.9821 | -76.4352 | -107.3209 | -134.4301
|  | MANNINGTON BSP | CF |  |  |  |  | 25.7944 | 23.7567 | 21.5454 | 18.5954 | 15.4159 | 12.875 | 10.124 | 6.6689 | 2.8597 | -22.9556 | -51.6831 | -75.2525 | 39.5812 | 37.8842 | 35.9883 | 33.3138 | 30.2648 | 27.4312 | 24.4638 | 20.9159 | 16.9159 | -10.277 | -50.0341 | -105.6484 | 23.2087 | 21.3128 | 19.2526 | 16.3832 | 13.3689 | 10.7924 | 8.0914 | 4.7414 | 1.0036 | -24.0648 | -52.3127 | -75.2882
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU 47559 12003 | NO | NO | 16.767 | 117.4317 | 113.6378 | 110.0388 | 105.3623 | 100.8858 | 93.5103 | 85.4194 | 77.6827 | 71.8021 | 39.3552 | 13.5439 | -0.37443 | 143.7863 | 140.7465 | 137.8781 | 133.9944 | 130.0648 | 124.5924 | 118.421 | 112.3199 | 107.7016 | 80.1138 | 35.9006 | -60.7107 | 122.6133 | 118.9909 | 115.8031 | 111.3082 | 106.996 | 100.095 | 92.3205 | 84.9633 | 79.6939 | 52.0725 | 29.2552 | 17.3256
|  | NETLEY COMMON BSP | EE |  |  |  |  | 117.4317 | 113.6378 | 110.0388 | 105.3623 | 100.8858 | 93.5103 | 85.4194 | 77.6827 | 71.8021 | 41.0011 | 18.995 | 2.1827 | 143.7863 | 140.7465 | 137.8781 | 133.9944 | 130.0648 | 124.5924 | 118.421 | 112.3199 | 107.7016 | 80.1138 | 48.5506 | -2.2597 | 122.6133 | 118.9909 | 115.8031 | 111.3082 | 106.996 | 100.095 | 92.3205 | 84.9633 | 79.6939 | 53.1154 | 34.0184 | 19.3888
|  | NETLEY COMMON BSP | HT |  |  |  |  | 119.6001 | 116.1643 | 112.6123 | 108.995 | 105.4327 | 99.6939 | 92.8133 | 85.9674 | 78.5052 | 39.3552 | 13.5439 | -0.37443 | 146.2567 | 144.2465 | 142.2557 | 140.0689 | 137.7312 | 134.7179 | 130.7791 | 126.8771 | 122.5097 | 101.3199 | 88.8189 | 82.5118 | 125.0909 | 121.9092 | 118.7756 | 115.4797 | 112.1511 | 106.9643 | 100.6286 | 94.3541 | 87.4868 | 52.0725 | 29.2552 | 17.3256
|  | NETLEY COMMON BSP | HE |  |  |  |  | 119.8123 | 116.548 | 113.3266 | 110.0837 | 106.7052 | 101.9756 | 96.2225 | 90.545 | 84.3276 | 51.5694 | 29.0439 | 18.9133 | 145.4199 | 142.8332 | 140.3597 | 137.7097 | 134.7281 | 131.1179 | 126.5618 | 121.9373 | 116.722 | 85.8791 | 53.0159 | 5.0465 | 125.2807 | 122.2092 | 119.3725 | 116.4327 | 113.2929 | 109.0164 | 103.6756 | 98.4266 | 92.5888 | 62.8623 | 43.1133 | 34.4633
|  | NETLEY COMMON BSP | CF |  |  |  |  | 122.1143 | 120.0623 | 117.8011 | 115.9062 | 114.2174 | 112.2848 | 110.2052 | 107.4337 | 104.4643 | 82.846 | 59.9092 | 38.5807 | 146.372 | 144.2975 | 141.972 | 139.7444 | 137.2628 | 134.1985 | 130.8169 | 126.6924 | 122.2108 | 89.721 | 35.9006 | -60.7107 | 127.2052 | 125.2205 | 123.0388 | 121.2858 | 119.6929 | 117.8572 | 115.9327 | 113.1868 | 110.2286 | 89.9705 | 69.897 | 51.3888
MELKSHAM GSP | NORRINGTON BSP | NORRINGTON BSP | MINIMUM HEADROOM | ST 88273 64983 | NO | NO | 44.934 | -39.5636 | 46.668 | 9.3058 | 3.3404 | -2.9198 | -11.7677 | -21.781 | -31.9279 | -39.3177 | -74.3851 | -102.0667 | -117.8483 | -15.032 | 60.9272 | 16.7527 | 12.5027 | 8.1813 | 2.0251 | -5.1157 | -12.3096 | -17.6259 | -42.9391 | -67.483 | -130.0769 | -41.7861 | 35.1629 | -9.881 | -15.3106 | -20.9626 | -29.2014 | -38.581 | -48.0055 | -54.8442 | -86.4596 | -110.9442 | -124.2106
|  | NORRINGTON BSP | EE |  |  |  |  | -39.5636 | 46.668 | 9.3058 | 3.3404 | -2.9198 | -11.7677 | -21.781 | -31.9279 | -39.3177 | -72.8269 | -96.1636 | -113.3647 | -15.032 | 60.9272 | 16.7527 | 12.5027 | 8.1813 | 2.0251 | -5.1157 | -12.3096 | -17.6259 | -42.9391 | -67.483 | -102.3259 | -41.7861 | 35.1629 | -9.881 | -15.3106 | -20.9626 | -29.2014 | -38.581 | -48.0055 | -54.8442 | -85.0871 | -105.1545 | -119.8534
|  | NORRINGTON BSP | HT |  |  |  |  | -37.1555 | 49.2241 | 11.468 | 6.7833 | 0.92922 | -7.0208 | -15.8677 | -24.6381 | -32.9963 | -74.3851 | -102.0667 | -117.8483 | -12.3881 | 64.1425 | 20.1302 | 17.5578 | 14.2629 | 9.6762 | 4.2517 | -1.1351 | -6.3147 | -30.3228 | -44.6524 | -52.4055 | -39.3412 | 37.7711 | -7.6147 | -11.7065 | -16.8514 | -24.1075 | -32.3085 | -40.4647 | -48.2657 | -86.4596 | -110.9442 | -124.2106
|  | NORRINGTON BSP | HE |  |  |  |  | -36.9167 | 49.6517 | 12.1986 | 7.916 | 2.6833 | -3.7626 | -11.6126 | -19.5942 | -26.7718 | -62.8147 | -86.7922 | -98.482 | -12.9116 | 63.3139 | 19.0762 | 16.1802 | 12.7027 | 8.3435 | 2.8374 | -2.6953 | -7.9106 | -36.5891 | -62.0575 | -95.0269 | -39.1565 | 38.1211 | -7.0034 | -10.7647 | -15.38 | -21.2442 | -28.4585 | -35.7198 | -42.3024 | -75.3779 | -96.0381 | -105.9514
|  | NORRINGTON BSP | CF |  |  |  |  | -34.7289 | 53.1925 | 17.2843 | 14.3292 | 11.9466 | 9.018 | 5.6343 | 1.1578 | -3.1994 | -30.8534 | -55.1014 | -75.88 | -11.8647 | 65.0149 | 21.4558 | 18.8986 | 16.6353 | 13.4904 | 9.8466 | 5.4251 | 1.0884 | -27.3994 | -66.1738 | -130.0769 | -37.1555 | 41.3568 | -2.3861 | -5.0769 | -7.1759 | -9.9096 | -13.1055 | -17.2769 | -21.2657 | -46.3218 | -68.0728 | -86.3545
MELKSHAM GSP | NORRINGTON B BSP | NORRINGTON B BSP | MINIMUM HEADROOM | ST 88273 64983 | NO | YES | 5.868 |  | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 |  | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 |  | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012
|  | NORRINGTON B BSP | EE | [5 empty] | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 |  | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 |  | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012
|  | NORRINGTON B BSP | HT | [5 empty] | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 |  | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 |  | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012
|  | NORRINGTON B BSP | HE | [5 empty] | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 |  | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 |  | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012
|  | NORRINGTON B BSP | CF | [5 empty] | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 |  | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 |  | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012
NORTH HYDE GSP | NORTH HYDE BSP | NORTH HYDE BSP | MINIMUM HEADROOM | TQ 10367 79001 | NO | YES | 10.339 | 59.9179 | 56.8311 | 52.5821 | 48.4505 | 44.7199 | 41.5536 | 38.8648 | 37.3719 | 36.5209 | 33.4791 | 28.9689 | 27.6689 | 70.2832 | 68.2362 | 65.8046 | 63.2913 | 61.0811 | 58.4342 | 55.7954 | 53.8546 | 52.3699 | 44.527 | 30.527 | -0.78826 | 62.2444 | 59.6189 | 56.125 | 52.6587 | 49.4852 | 46.4709 | 43.6954 | 41.9515 | 40.9954 | 37.424 | 32.8332 | 31.2577
|  | NORTH HYDE BSP | EE |  |  |  |  | 59.9179 | 56.8311 | 52.5821 | 48.4505 | 44.7199 | 41.5536 | 38.8648 | 37.3719 | 36.5209 | 33.5821 | 30.9005 | 30.4944 | 70.2832 | 68.2362 | 65.8046 | 63.2913 | 61.0811 | 58.4342 | 55.7954 | 53.8546 | 52.3699 | 44.527 | 34.5985 | 18.2944 | 62.2444 | 59.6189 | 56.125 | 52.6587 | 49.4852 | 46.4709 | 43.6954 | 41.9515 | 40.9954 | 37.624 | 35.0056 | 34.1179
|  | NORTH HYDE BSP | HT |  |  |  |  | 60.1995 | 57.5719 | 53.5526 | 49.4495 | 45.9189 | 42.9617 | 40.9536 | 39.8352 | 38.6179 | 33.4791 | 28.9689 | 27.6689 | 70.8036 | 69.3964 | 67.3321 | 65.0852 | 63.3219 | 61.1934 | 59.5311 | 58.324 | 56.9148 | 51.4526 | 47.5811 | 45.7199 | 62.6117 | 60.473 | 57.2505 | 53.7954 | 50.8015 | 48.0566 | 46.1015 | 44.7668 | 43.2893 | 37.424 | 32.8332 | 31.2577
|  | NORTH HYDE BSP | HE |  |  |  |  | 60.475 | 57.6342 | 53.6648 | 49.5954 | 46.1362 | 43.5505 | 41.8209 | 41.223 | 40.5413 | 37.8832 | 35.8117 | 34.3332 | 70.773 | 68.9097 | 66.6638 | 64.1781 | 62.1679 | 60.0464 | 58.2944 | 57.1964 | 55.9464 | 48.024 | 38.1924 | 21.5454 | 62.8638 | 60.5311 | 57.3577 | 53.9148 | 50.9821 | 48.6556 | 47.0219 | 46.3536 | 45.5138 | 42.0597 | 40.0056 | 38.3046
|  | NORTH HYDE BSP | CF |  |  |  |  | 61.123 | 58.9536 | 55.3526 | 51.9168 | 49.1811 | 47.1372 | 45.5209 | 44.8679 | 44.6015 | 41.9321 | 38.8485 | 36.1719 | 71.0219 | 69.5689 | 67.2577 | 64.9444 | 63.0862 | 61.0821 | 59.0934 | 57.5607 | 56.3036 | 47.226 | 30.527 | -0.78826 | 63.4505 | 61.7117 | 58.8362 | 55.9709 | 53.7168 | 51.9321 | 50.3954 | 49.5556 | 49.1903 | 46.124 | 43.2413 | 40.925
COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD (OSNEY) BSP | MINIMUM HEADROOM | SP 50054 05983 | NO | NO | 48.255 | -38.2679 | -40.974 | -43.2801 | -46.1128 | 21.6526 | 16.3363 | 10.5139 | 5.0292 | 0.26998 | -19.0402 | -30.0372 | -33.3433 | -17.525 | -18.8179 | -20.0322 | -22.2842 | 46.2884 | 42.7424 | 38.6159 | 34.6455 | 31.17 | 15.6843 | -0.42389 | -36.3698 | -35.6271 | -37.322 | -38.9781 | -41.2669 | 26.9445 | 22.3475 | 17.0853 | 12.1598 | 7.9465 | -9.7657 | -18.4239 | -21.3198
|  | OXFORD (OSNEY) BSP | EE |  |  |  |  | -38.2679 | -40.974 | -43.2801 | -46.1128 | 21.6526 | 16.3363 | 10.5139 | 5.0292 | 0.26998 | -19.0402 | -29.0657 | -32.4249 | -17.525 | -18.8179 | -20.0322 | -22.2842 | 46.2884 | 42.7424 | 38.6159 | 34.6455 | 31.17 | 15.6843 | 3.2669 | -14.1484 | -35.6271 | -37.322 | -38.9781 | -41.2669 | 26.9445 | 22.3475 | 17.0853 | 12.1598 | 7.9465 | -9.0555 | -17.8106 | -20.7035
|  | OXFORD (OSNEY) BSP | HT |  |  |  |  | -37.7138 | -39.5352 | -41.4628 | -44.3077 | 24.2077 | 18.6281 | 13.7098 | 8.5792 | 3.3863 | -17.5974 | -30.0372 | -33.3433 | -16.6158 | -17.3352 | -18.1179 | -19.7495 | 49.8475 | 47.073 | 43.9516 | 40.7404 | 37.4414 | 25.1475 | 18.6771 | 16.9965 | -34.7332 | -35.7801 | -37.0648 | -39.6097 | 29.1975 | 24.4169 | 20.0506 | 15.4884 | 10.9006 | -7.5147 | -18.4239 | -21.3198
|  | OXFORD (OSNEY) BSP | HE |  |  |  |  | -37.0352 | -39.2556 | -41.3801 | -43.7852 | 24.9649 | 20.3241 | 15.5159 | 10.9302 | 5.971 | -17.0586 | -25.8178 | -28.4984 | -16.8097 | -17.874 | -18.9781 | -20.2424 | 49.1741 | 46.072 | 42.6271 | 39.2384 | 35.4486 | 17.8792 | 4.3924 | -12.5576 | -34.7209 | -36.1403 | -37.573 | -39.3046 | 29.6761 | 25.7547 | 21.5088 | 17.4098 | 12.1373 | -9.7657 | -17.7341 | -19.4647
|  | OXFORD (OSNEY) BSP | CF |  |  |  |  | -35.3179 | -36.3985 | -37.4444 | -38.7311 | 31.2037 | 29.6179 | 26.8894 | 23.7118 | 20.3241 | -0.37083 | -13.0086 | -22.3178 | -16.0403 | -16.7026 | -17.4005 | -18.2158 | 52.1771 | 50.5149 | 47.9424 | 45.0577 | 41.9424 | 22.2608 | -0.42389 | -36.3698 | -33.474 | -34.1944 | -34.9454 | -35.8444 | 34.5669 | 33.2669 | 31.0618 | 28.4588 | 25.6445 | 6.0281 | -5.6423 | -12.4178
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | POOLE (HAMWORTHY) BSP | MINIMUM HEADROOM | SZ 00203 90789 | NO | NO | 7 | 24.1602 | 22.7765 | 21.3398 | 19.6449 | 17.8 | 15.4918 | 12.6173 | 9.7867 | 7.8979 | -0.53982 | -6.3378 | -10.1327 | 28.0336 | 27.0285 | 26.0194 | 24.7255 | 23.3102 | 21.7765 | 19.8887 | 17.8581 | 16.399 | 9.1224 | -0.65411 | -22.0827 | 25.5143 | 24.2857 | 23.0602 | 21.4816 | 19.5285 | 17.2785 | 14.5592 | 11.8745 | 10.1214 | 2.7969 | -1.8388 | -5.0725
|  | POOLE (HAMWORTHY) BSP | EE |  |  |  |  | 24.1602 | 22.7765 | 21.3398 | 19.6449 | 17.8 | 15.4918 | 12.6173 | 9.7867 | 7.8979 | -0.53982 | -5.8419 | -10.1327 | 28.0336 | 27.0285 | 26.0194 | 24.7255 | 23.3102 | 21.7765 | 19.8887 | 17.8581 | 16.399 | 9.1224 | 1.8949 | -9.4143 | 25.5143 | 24.2857 | 23.0602 | 21.4816 | 19.5285 | 17.2785 | 14.5592 | 11.8745 | 10.1214 | 2.7969 | -1.4245 | -5.0725
|  | POOLE (HAMWORTHY) BSP | HT |  |  |  |  | 25.1469 | 24.1316 | 22.499 | 20.5194 | 18.6153 | 16.4622 | 14.0275 | 11.9938 | 10.0683 | 0.16018 | -6.3378 | -9.8735 | 28.7234 | 28.002 | 26.9928 | 25.953 | 25.0102 | 23.899 | 22.6061 | 21.4775 | 20.3979 | 14.8653 | 11.6102 | 10.1132 | 26.4816 | 25.4602 | 23.8551 | 22.1479 | 20.5306 | 18.6755 | 16.5683 | 14.7581 | 13.0285 | 3.8041 | -1.8388 | -4.7429
|  | POOLE (HAMWORTHY) BSP | HE |  |  |  |  | 24.7898 | 23.6163 | 22.1969 | 20.6153 | 18.9571 | 17.15 | 14.6306 | 12.1571 | 10.151 | 0.45201 | -5.5725 | -7.8959 | 28.4622 | 27.6214 | 26.5581 | 25.3704 | 24.2581 | 22.9602 | 21.3143 | 19.6459 | 18.1449 | 9.5653 | 1.5459 | -8.9164 | 26.1275 | 25.0643 | 23.8632 | 22.3704 | 20.8347 | 19.1092 | 16.901 | 14.7387 | 12.7061 | 3.4224 | -1.1959 | -3.1806
|  | POOLE (HAMWORTHY) BSP | CF |  |  |  |  | 25.601 | 24.9143 | 24.251 | 23.5683 | 22.7775 | 22.1592 | 21.0694 | 19.8245 | 18.4816 | 9.9826 | 3.9949 | -1.1266 | 28.9367 | 28.2887 | 27.6132 | 26.8969 | 26.102 | 25.4714 | 24.4071 | 23.2245 | 21.9234 | 12.1969 | -0.65411 | -22.0827 | 26.899 | 26.252 | 25.6224 | 24.9704 | 24.2867 | 23.7398 | 22.7816 | 21.6357 | 20.3673 | 12.4285 | 6.8785 | 2.5245
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ 63405 99685 | NO | YES | 14.162 | -31.3849 | -36.1114 | -42.1012 | 41.0264 | 33.1743 | 24.0172 | 13.4478 | 2.9519 | -5.7553 | -35.4318 | -55.8134 | -56.8328 | -2.1216 | -6.1798 | -11.1124 | 73.107 | 66.758 | 59.7804 | 51.5151 | 43.0733 | 35.7947 | 0.0028816 | -57.9053 | -189.2563 | -30.1798 | -34.5859 | -40.1247 | 43.46 | 36.2406 | 27.8376 | 18.0345 | 8.3192 | 0.33962 | -26.6961 | -44.3594 | -44.9869
|  | PORTSMOUTH BSP | EE |  |  |  |  | -31.3849 | -36.1114 | -42.1012 | 41.0264 | 33.1743 | 24.0172 | 13.4478 | 2.9519 | -5.7553 | -35.4318 | -48.7736 | -47.8032 | -2.1216 | -6.1798 | -11.1124 | 73.107 | 66.758 | 59.7804 | 51.5151 | 43.0733 | 35.7947 | 0.0028816 | -37.6614 | -97.5247 | -30.1798 | -34.5859 | -40.1247 | 43.46 | 36.2406 | 27.8376 | 18.0345 | 8.3192 | 0.33962 | -26.6961 | -38.2512 | -37.4767
|  | PORTSMOUTH BSP | HT |  |  |  |  | -28.7481 | -32.4685 | -37.0145 | 47.3631 | 40.7049 | 32.9059 | 24.5182 | 15.5355 | 7.5774 | -32.6481 | -55.8134 | -56.8328 | 1.61 | -0.94814 | -3.9859 | 82.5468 | 78.3835 | 73.7794 | 68.6774 | 63.0396 | 57.9447 | 32.4825 | 18.1968 | 16.3753 | -27.2104 | -30.6502 | -34.9053 | 50.1019 | 44.1284 | 37.0723 | 29.4376 | 21.1896 | 13.8488 | -23.2288 | -44.3594 | -44.9869
|  | PORTSMOUTH BSP | HE |  |  |  |  | -28.4308 | -31.8288 | -35.9206 | 49.757 | 44.1743 | 37.6233 | 30.4651 | 22.6978 | 15.6764 | -13.9634 | -27.3696 | -29.6441 | 0.49166 | -2.6288 | -6.2043 | 79.9406 | 75.2508 | 69.9968 | 64.1304 | 57.56 | 51.3029 | 14.3386 | -24.3818 | -84.6716 | -27.0298 | -30.1247 | -33.9461 | 52.0641 | 47.01 | 41.0498 | 34.5029 | 27.3651 | 20.9264 | -6.3481 | -18.1849 | -19.8849
|  | PORTSMOUTH BSP | CF |  |  |  |  | -25.7859 | -27.6951 | -30.2971 | 56.8712 | 53.9733 | 51.0121 | 47.4264 | 43.4825 | 39.5519 | 15.5866 | -10.5349 | -32.8879 | 1.7212 | -0.79916 | -3.8553 | 82.6712 | 78.7876 | 74.2621 | 68.9631 | 63.1957 | 57.2029 | 14.9866 | -57.9053 | -189.2563 | -24.6532 | -26.2869 | -28.7236 | 58.5784 | 55.9274 | 53.2202 | 49.9029 | 46.2284 | 42.611 | 20.5202 | -3.2675 | -23.2532
FLEET-BRAMLEY GSP | PYESTOCK BSP | PYESTOCK BSP | MINIMUM HEADROOM | SU 82940 54553 | YES | NO | 77.45 | 45.1767 | 44.6665 | 44.4481 | 43.9502 | 43.4236 | 42.5318 | 41.5675 | 40.5951 | 39.8349 | 35.1277 | 31.693 | 29.7389 | -11.0424 | -11.3884 | -11.5496 | -11.9027 | -12.2792 | -12.8169 | -13.4282 | -14.1241 | -14.6302 | -17.5904 | -21.8373 | -31.2067 | 42.9586 | 42.5351 | 42.3371 | 41.9024 | 41.4147 | 40.6147 | 39.732 | 38.8443 | 38.1718 | 34.079 | 31.0984 | 29.4422
|  | PYESTOCK BSP | EE |  |  |  |  | 45.1767 | 44.6665 | 44.4481 | 43.9502 | 43.4236 | 42.5318 | 41.5675 | 40.5951 | 39.8349 | 35.7451 | 32.4859 | 30.0767 | -11.0424 | -11.3884 | -11.5496 | -11.9027 | -12.2792 | -12.8169 | -13.4282 | -14.1241 | -14.6302 | -17.5904 | -21.0241 | -26.019 | 42.9586 | 42.5351 | 42.3371 | 41.9024 | 41.4147 | 40.6147 | 39.732 | 38.8443 | 38.1718 | 34.5749 | 31.7627 | 29.6994
|  | PYESTOCK BSP | HT |  |  |  |  | 45.3542 | 44.9451 | 44.4777 | 43.9706 | 43.743 | 42.841 | 41.9144 | 40.9542 | 39.9991 | 35.1277 | 31.693 | 29.7389 | -10.7976 | -11.0037 | -11.2527 | -11.5312 | -11.618 | -12.0384 | -12.4731 | -12.9435 | -13.4078 | -15.7098 | -17.2067 | -18.0608 | 43.0892 | 42.7606 | 42.3831 | 41.9484 | 41.7576 | 40.9698 | 40.1382 | 39.28 | 38.4269 | 34.079 | 31.0984 | 29.4422
|  | PYESTOCK BSP | HE |  |  |  |  | 45.4114 | 45.0461 | 44.6226 | 44.1593 | 43.9808 | 43.294 | 42.5787 | 41.8267 | 41.0808 | 36.944 | 33.6461 | 32.0308 | -10.8782 | -11.1292 | -11.4261 | -11.7537 | -11.8924 | -12.3241 | -12.7863 | -13.2914 | -13.8078 | -17.1047 | -20.6169 | -25.3098 | 43.1351 | 42.8392 | 42.4943 | 42.1024 | 41.9412 | 41.3524 | 40.7055 | 40.0249 | 39.3484 | 35.6371 | 32.778 | 31.4167
|  | PYESTOCK BSP | CF |  |  |  |  | 45.7216 | 45.4798 | 45.243 | 44.9706 | 44.6706 | 44.6685 | 44.3828 | 44.0798 | 43.7553 | 41.244 | 38.0196 | 34.8818 | -10.7537 | -10.9822 | -11.2047 | -11.4578 | -11.7659 | -11.9067 | -12.2649 | -12.6414 | -13.0547 | -16.3322 | -21.8373 | -31.2067 | 43.4014 | 43.2055 | 43.0259 | 42.8106 | 42.5576 | 42.5433 | 42.3106 | 42.0402 | 41.7402 | 39.429 | 36.6086 | 33.8729
BRAMLEY (BASI) GSP | READING BSP | READING BSP | MINIMUM HEADROOM | SU 74642 73856 | NO | NO | 66.733 | 59.9132 | 55.9122 | 50.6112 | 45.6918 | 40.6398 | 32.8132 | 23.4377 | 14.5388 | 7.7336 | -24.6592 | -50.1623 | -61.6449 | 86.5673 | 83.1908 | 78.803 | 75.0132 | 70.9918 | 65.4836 | 58.7132 | 52.2153 | 47.3581 | 21.9255 | -13.5368 | -95.8735 | 57.7979 | 53.9224 | 48.8775 | 44.3898 | 39.7183 | 32.5806 | 23.8949 | 15.651 | 9.6551 | -18.2806 | -40.2817 | -49.5031
|  | READING BSP | EE |  |  |  |  | 59.9132 | 55.9122 | 50.6112 | 45.6918 | 40.6398 | 32.8132 | 23.4377 | 14.5388 | 7.7336 | -23.8643 | -45.7419 | -56.5776 | 86.5673 | 83.1908 | 78.803 | 75.0132 | 70.9918 | 65.4836 | 58.7132 | 52.2153 | 47.3581 | 21.9255 | -5.5306 | -45.447 | 57.7979 | 53.9224 | 48.8775 | 44.3898 | 39.7183 | 32.5806 | 23.8949 | 15.651 | 9.6551 | -18.0949 | -36.3684 | -45.4092
|  | READING BSP | HT |  |  |  |  | 61.4449 | 57.5745 | 53.3051 | 49.0806 | 44.1102 | 37.1398 | 28.9469 | 21.7969 | 14.1724 | -24.6592 | -50.1623 | -61.6449 | 89.2112 | 86.5908 | 83.849 | 81.2296 | 77.9408 | 74.2561 | 69.4643 | 65.403 | 60.9041 | 39.2949 | 27.0622 | 21.8285 | 59.7449 | 56.1418 | 52.2806 | 48.402 | 43.7296 | 37.5632 | 30.1183 | 23.6061 | 16.6367 | -18.2806 | -40.2817 | -49.5031
|  | READING BSP | HE |  |  |  |  | 61.9918 | 58.3918 | 54.4275 | 50.6061 | 46.2173 | 40.6061 | 33.7663 | 26.9949 | 20.3449 | -12.1408 | -33.6449 | -43.4704 | 88.602 | 85.6255 | 82.5316 | 79.5928 | 75.95 | 72.0683 | 67.1816 | 62.1398 | 57.0041 | 28.45 | 0.6612 | -38.5837 | 60.1439 | 56.7785 | 53.1969 | 49.7194 | 45.553 | 40.5153 | 34.2949 | 28.0796 | 21.9734 | -7.2561 | -25.2174 | -33.0255
|  | READING BSP | CF |  |  |  |  | 64.9071 | 62.7755 | 59.9398 | 57.9745 | 55.8367 | 53.4877 | 50.6418 | 47.3908 | 44.0347 | 18.9836 | -7.9908 | -32.4031 | 89.9132 | 87.5918 | 84.7132 | 82.651 | 79.8857 | 76.6061 | 72.9112 | 68.9683 | 64.7785 | 34.0265 | -13.5368 | -95.8735 | 62.6898 | 60.6469 | 58.0153 | 56.2612 | 54.1643 | 51.849 | 49.1367 | 46.1479 | 43.0775 | 20.0541 | -3.3766 | -24.6174
FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN BSP | MINIMUM HEADROOM | SU 71580 74111 | NO | NO | 19.646 | 49.1005 | 47.1811 | 45.2413 | 41.1321 | 37.4352 | 33.7566 | 29.7433 | 25.179 | 21.3474 | 14.0117 | 8.4209 | 6.9841 | 59.1987 | 57.7517 | 56.4875 | 53.3334 | 51.0324 | 48.664 | 45.867 | 42.8966 | 40.3221 | 31.1079 | 15.3793 | -16.9962 | 51.4762 | 49.6058 | 47.8691 | 44.1109 | 40.7854 | 37.4721 | 33.8395 | 29.7691 | 26.517 | 19.665 | 14.8109 | 13.6375
|  | READING TOWN BSP | EE |  |  |  |  | 49.1005 | 47.1811 | 45.2413 | 41.1321 | 37.4352 | 33.7566 | 29.7433 | 25.179 | 21.3474 | 14.0117 | 9.9209 | 8.9352 | 59.1987 | 57.7517 | 56.4875 | 53.3334 | 51.0324 | 48.664 | 45.867 | 42.8966 | 40.3221 | 31.1079 | 21.3364 | 5.7466 | 51.4762 | 49.6058 | 47.8691 | 44.1109 | 40.7854 | 37.4721 | 33.8395 | 29.7691 | 26.517 | 19.665 | 16.2405 | 15.2283
|  | READING TOWN BSP | HT |  |  |  |  | 49.927 | 48.3729 | 46.3841 | 42.5811 | 39.3739 | 35.7801 | 31.8474 | 27.9525 | 24.0709 | 14.6076 | 8.4209 | 6.9841 | 60.1375 | 59.1783 | 58.117 | 55.4466 | 53.8324 | 51.966 | 49.6272 | 47.4946 | 45.3099 | 39.0252 | 35.6058 | 34.6681 | 52.2048 | 50.817 | 49.1466 | 45.7589 | 43.0834 | 40.066 | 36.6079 | 33.217 | 29.816 | 20.5079 | 14.8109 | 13.6375
|  | READING TOWN BSP | HE |  |  |  |  | 49.9566 | 48.478 | 46.5678 | 42.8617 | 39.9617 | 36.9984 | 33.4086 | 29.5495 | 25.8086 | 18.5392 | 14.2739 | 12.8841 | 59.7915 | 58.6426 | 57.3885 | 54.5068 | 52.763 | 50.8395 | 48.2864 | 45.7385 | 43.1548 | 33.5211 | 23.615 | 8.116 | 52.2242 | 50.8915 | 49.2752 | 45.9599 | 43.5272 | 41.0864 | 37.9568 | 34.6528 | 31.4242 | 24.2415 | 20.4915 | 19.3834
|  | READING TOWN BSP | CF |  |  |  |  | 51.1566 | 50.078 | 48.625 | 45.5403 | 43.3331 | 42.1362 | 40.1076 | 37.7933 | 35.6566 | 25.1178 | 19.1403 | 13.8046 | 60.3313 | 59.3181 | 58.1977 | 55.5436 | 53.866 | 52.6089 | 50.5497 | 48.5068 | 46.4538 | 33.4272 | 15.3793 | -16.9962 | 53.2232 | 52.2813 | 51.0936 | 48.3558 | 46.5099 | 45.5854 | 43.7977 | 41.8089 | 39.9242 | 30.3201 | 24.5875 | 19.8252
MANNINGTON GSP | REDHILL BSP | REDHILL BSP | MINIMUM HEADROOM | SZ 08581 96162 | NO | NO | 16.422 | 19.1899 | 17.3991 | 14.9715 | 12.544 | 9.8787 | 5.6899 | 1.1889 | -3.2989 | -6.5468 | -24.1989 | -37.6132 | -43.6703 | 30.1899 | 28.8399 | 26.9021 | 24.9195 | 22.8195 | 19.9705 | 16.7797 | 13.4623 | 11.2042 | -1.5601 | -18.3581 | -59.1928 | 18.9185 | 17.2664 | 14.8909 | 12.5093 | 10.0052 | 6.1389 | 1.9358 | -2.256 | -5.1897 | -20.505 | -31.8489 | -36.7764
|  | REDHILL BSP | EE |  |  |  |  | 19.1899 | 17.3991 | 14.9715 | 12.544 | 9.8787 | 5.6899 | 1.1889 | -3.2989 | -6.5468 | -22.857 | -35.157 | -41.5489 | 30.1899 | 28.8399 | 26.9021 | 24.9195 | 22.8195 | 19.9705 | 16.7797 | 13.4623 | 11.2042 | -1.5601 | -15.6111 | -35.7366 | 18.9185 | 17.2664 | 14.8909 | 12.5093 | 10.0052 | 6.1389 | 1.9358 | -2.256 | -5.1897 | -19.653 | -29.7785 | -35.0989
|  | REDHILL BSP | HT |  |  |  |  | 19.9623 | 17.7399 | 15.7021 | 14.2715 | 12.1379 | 8.4419 | 4.6113 | 0.6103 | -3.4642 | -24.1989 | -37.6132 | -43.6703 | 31.4552 | 30.0562 | 28.8113 | 28.0838 | 26.744 | 24.7848 | 22.6348 | 20.347 | 17.9828 | 6.9593 | 0.90724 | -1.7938 | 19.9287 | 17.8787 | 16.0083 | 14.743 | 12.7134 | 9.3593 | 5.8154 | 2.1021 | -1.7142 | -20.505 | -31.8489 | -36.7764
|  | REDHILL BSP | HE |  |  |  |  | 20.2542 | 18.2195 | 16.3715 | 15.1174 | 13.2113 | 10.2368 | 7.1481 | 3.9266 | 0.56847 | -16.5081 | -28.4581 | -33.4428 | 31.1776 | 29.6276 | 28.2307 | 27.2705 | 25.7072 | 23.6419 | 21.3501 | 18.8879 | 16.2532 | 1.646 | -12.5397 | -32.1366 | 20.1603 | 18.2736 | 16.5776 | 15.4674 | 13.6419 | 10.9032 | 7.9756 | 4.9083 | 1.7083 | -13.8591 | -23.7897 | -27.8121
|  | REDHILL BSP | CF |  |  |  |  | 21.5623 | 20.2572 | 18.8491 | 17.8899 | 17.2889 | 16.1052 | 14.8583 | 13.5654 | 12.0838 | 0.945 | -12.1111 | -24.5275 | 31.7532 | 30.5256 | 29.1603 | 28.1011 | 27.2103 | 25.644 | 23.8664 | 21.9828 | 19.9593 | 5.2052 | -18.3581 | -59.1928 | 21.347 | 20.1236 | 18.7787 | 17.8695 | 17.3521 | 16.2001 | 14.9236 | 13.5725 | 12.1583 | 1.7042 | -9.9979 | -20.8183
NURSLING GSP | ROWNHAMS BSP | ROWNHAMS BSP | MINIMUM HEADROOM | SU 37168 16854 | NO | NO | 53.076 | -3.3038 | -7.3293 | -10.6956 | 99.2705 | 94.0541 | 85.8307 | 77.4654 | 68.0909 | 60.8746 | 17.5878 | -8.7285 | -26.5336 | 26.3618 | 23.1138 | 20.474 | 126.7108 | 122.2852 | 116.3618 | 110.5097 | 103.2659 | 94.9893 | 59.5812 | 28.4842 | -27.1137 | -3.6341 | -7.4035 | -10.4974 | 96.8424 | 91.6455 | 83.9342 | 76.2057 | 67.3097 | 60.6455 | 19.1271 | -5.8015 | -23.2515
|  | ROWNHAMS BSP | EE |  |  |  |  | -3.3038 | -7.3293 | -10.6956 | 99.2705 | 94.0541 | 85.8307 | 77.4654 | 68.0909 | 60.8746 | 23.9715 | -4.4867 | -21.552 | 26.3618 | 23.1138 | 20.474 | 126.7108 | 122.2852 | 116.3618 | 110.5097 | 103.3955 | 98.2455 | 68.0077 | 35.2179 | -1.2382 | -3.6341 | -7.4035 | -10.4974 | 96.8424 | 91.6455 | 83.9342 | 76.2057 | 67.3097 | 60.6455 | 26.1444 | -1.3566 | -17.2678
|  | ROWNHAMS BSP | HT |  |  |  |  | -1.2446 | -4.5834 | -8.2936 | 102.3858 | 96.7337 | 90.0766 | 82.3317 | 75.0276 | 65.9062 | 22.3011 | -8.7285 | -26.5336 | 28.4352 | 26.3781 | 23.974 | 131.521 | 127.0526 | 123.2138 | 118.222 | 113.6485 | 107.0934 | 78.8679 | 58.6516 | 46.4455 | -1.5913 | -4.6739 | -8.1392 | 100.1485 | 94.5618 | 88.4118 | 81.1455 | 74.472 | 65.6444 | 24.322 | -5.8015 | -23.2515
|  | ROWNHAMS BSP | HE |  |  |  |  | -1.017 | -4.7538 | -8.6283 | 101.847 | 95.8848 | 89.797 | 82.4746 | 72.2429 | 62.2399 | 17.5878 | -6.2336 | -21.9969 | 28.072 | 25.1159 | 21.9699 | 128.7312 | 123.3934 | 118.7312 | 112.6434 | 103.2659 | 94.9893 | 59.5812 | 28.4842 | -10.9699 | -1.378 | -4.9219 | -8.6535 | 99.3587 | 93.3363 | 87.6597 | 80.7363 | 70.6271 | 61.5526 | 19.1271 | -5.3219 | -21.6454
|  | ROWNHAMS BSP | CF |  |  |  |  | 1.4789 | -0.29765 | -2.613 | 109.4286 | 107.0317 | 103.9041 | 100.9531 | 97.5633 | 93.6817 | 65.8205 | 35.0939 | 14.4592 | 29.3791 | 27.7812 | 25.571 | 133.0801 | 130.5016 | 127.1332 | 123.8424 | 120.2046 | 115.9699 | 85.9975 | 39.5495 | -27.1137 | 0.94035 | -0.69332 | -2.8821 | 106.5659 | 104.3159 | 101.3638 | 98.6342 | 95.4261 | 91.6659 | 66.075 | 37.174 | 16.5424
MANNINGTON GSP | SALISBURY BSP | SALISBURY BSP | MINIMUM HEADROOM | SU 11049 31395 | NO | NO | 31.786 | 44.1349 | 41.4298 | 38.7625 | 35.3462 | 32.3166 | 27.5186 | 22.0554 | 17.2258 | 13.486 | -2.9998 | -13.9834 | -19.1191 | 64.4635 | 62.4758 | 60.388 | 57.8176 | 55.6768 | 52.4584 | 48.6819 | 45.3778 | 42.74 | 29.6074 | 14.5839 | -23.0651 | 49.887 | 47.3554 | 44.8247 | 41.5584 | 38.8431 | 34.387 | 29.2227 | 24.8043 | 21.4441 | 6.7319 | -2.7324 | -6.9069
|  | SALISBURY BSP | EE |  |  |  |  | 44.1349 | 41.4298 | 38.7625 | 35.3462 | 32.3166 | 27.5186 | 22.0554 | 17.2258 | 13.486 | -2.9998 | -12.2059 | -16.3498 | 64.4635 | 62.4758 | 60.388 | 57.8176 | 55.6768 | 52.4584 | 48.6819 | 45.3778 | 42.74 | 29.6074 | 17.2237 | -0.99261 | 49.887 | 47.3554 | 44.8247 | 41.5584 | 38.8431 | 34.387 | 29.2227 | 24.8043 | 21.4441 | 6.7319 | -1.1651 | -4.6589
|  | SALISBURY BSP | HT |  |  |  |  | 45.3349 | 43.2135 | 40.7125 | 37.6329 | 34.6033 | 30.2564 | 25.7268 | 21.4411 | 17.1809 | -2.5508 | -13.9834 | -19.1191 | 65.6788 | 64.3411 | 62.739 | 60.9135 | 59.188 | 56.8462 | 54.2411 | 51.736 | 49.1492 | 38.0237 | 32.1696 | 29.6135 | 51.2431 | 49.2482 | 46.8666 | 44.0349 | 41.3166 | 37.4421 | 33.3064 | 29.3656 | 25.3849 | 7.3492 | -2.7324 | -6.9069
|  | SALISBURY BSP | HE |  |  |  |  | 45.5258 | 43.487 | 41.2105 | 38.1839 | 35.4656 | 31.6196 | 28.0625 | 24.1094 | 20.2054 | 2.8707 | -6.1232 | -9.9069 | 65.387 | 63.8594 | 62.136 | 59.8778 | 58.0584 | 55.586 | 53.2523 | 50.5064 | 47.5911 | 33.0645 | 20.4696 | 2.4656 | 51.3941 | 49.4798 | 47.2941 | 44.439 | 42.0013 | 38.5349 | 35.337 | 31.7482 | 28.0962 | 12.2084 | 4.6023 | 1.6176
|  | SALISBURY BSP | CF |  |  |  |  | 46.888 | 45.4513 | 43.9951 | 42.0247 | 40.1951 | 38.5411 | 36.2982 | 34.3819 | 32.5156 | 18.0166 | 6.6013 | -4.561 | 66.0156 | 64.7329 | 63.3594 | 61.5247 | 59.8849 | 58.2982 | 56.1421 | 54.1737 | 52.1288 | 36.0829 | 14.5839 | -23.0651 | 52.6156 | 51.2482 | 49.8278 | 47.8778 | 46.2105 | 44.739 | 42.6533 | 40.8962 | 39.1615 | 25.5094 | 15.5278 | 5.7502
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST 85442 23791 | NO | NO | 41.856 | 22.1837 | 18.6041 | 15.0898 | 11.8919 | 8.4674 | 4.797 | 0.46125 | -3.351 | -6.2969 | -21.2132 | -29.9887 | -35.8051 | 35.8309 | 33.3554 | 30.9839 | 29.0921 | 27.0309 | 24.7503 | 21.9625 | 19.4829 | 17.4962 | 6.3105 | -6.0018 | -34.5875 | 23.7062 | 20.4398 | 17.1643 | 14.3796 | 11.348 | 7.9806 | 3.8531 | 0.2888 | -2.3173 | -15.3051 | -22.9377 | -27.6551
|  | SHAFTESBURY BSP | EE |  |  |  |  | 22.1837 | 18.6041 | 15.0898 | 11.8919 | 8.4674 | 4.797 | 0.46125 | -3.351 | -6.2969 | -21.2132 | -28.9979 | -34.6367 | 35.8309 | 33.3554 | 30.9839 | 29.0921 | 27.0309 | 24.7503 | 21.9625 | 19.4829 | 17.4962 | 6.3105 | -3.5538 | -18.1181 | 23.7062 | 20.4398 | 17.1643 | 14.3796 | 11.348 | 7.9806 | 3.8531 | 0.2888 | -2.3173 | -15.3051 | -21.9826 | -26.6653
|  | SHAFTESBURY BSP | HT |  |  |  |  | 23.4817 | 20.349 | 17.3572 | 14.1908 | 10.8062 | 7.4602 | 4.4429 | 0.85309 | -2.6398 | -20.3704 | -29.9887 | -35.8051 | 37.035 | 35.0431 | 33.2339 | 31.5615 | 29.7482 | 28.0135 | 26.5095 | 24.5401 | 22.6268 | 13.0278 | 8.2829 | 5.6666 | 25 | 22.2296 | 19.5572 | 16.7898 | 13.8 | 10.8123 | 8.1133 | 4.8276 | 1.6459 | -14.4571 | -22.9377 | -27.6551
|  | SHAFTESBURY BSP | HE |  |  |  |  | 23.4786 | 20.3949 | 17.4368 | 14.3153 | 10.9817 | 7.6357 | 5.1868 | 1.8776 | -1.2214 | -18.803 | -26.999 | -30.7979 | 36.738 | 34.5931 | 32.6095 | 30.737 | 28.6972 | 26.5533 | 25.0523 | 22.8237 | 20.6911 | 7.2982 | -2.915 | -16.6773 | 24.9847 | 22.2541 | 19.6143 | 16.8919 | 13.947 | 10.9113 | 8.75 | 5.7153 | 2.8766 | -13.099 | -20.0132 | -23.152
|  | SHAFTESBURY BSP | CF |  |  |  |  | 24.6276 | 22.2021 | 20.0715 | 17.4439 | 14.5306 | 12.5949 | 10.4806 | 8.7041 | 7.3255 | -4.6816 | -14.6469 | -23.7387 | 37.2993 | 35.4625 | 33.9319 | 32.1523 | 30.0523 | 28.4237 | 26.5952 | 24.9727 | 23.5778 | 11.2431 | -6.0018 | -34.5875 | 26.0296 | 23.8949 | 22.0072 | 19.7378 | 17.2 | 15.4725 | 13.5347 | 11.9021 | 10.7113 | -0.52752 | -9.3816 | -17.4265
IVER 132KV GSP | SLOUGH BSP | SLOUGH BSP | MINIMUM HEADROOM | SU 95574 81752 | NO | YES | 94.823 | -86.5383 | -201.8577 | -325.6138 | -286.4314 | -445.3926 | -523.7457 | -528.7069 | -533.0569 | -536.7569 | -653.6783 | -664.8885 | -669.3089 | -94.1033 | -237.4972 | -391.7584 | -375.5656 | -573.6187 | -670.1982 | -674.8584 | -678.7901 | -682.4625 | -824.3003 | -837.1533 | -862.7391 | -103.1176 | -246.7717 | -401.1809 | -383.2503 | -581.4176 | -678.5054 | -683.7136 | -688.1503 | -692.1197 | -835.4207 | -846.8105 | -851.8044
|  | SLOUGH BSP | EE |  |  |  |  | -86.5383 | -201.8577 | -325.6138 | -286.4314 | -445.3926 | -523.7457 | -528.7069 | -533.0569 | -536.7569 | -652.0824 | -660.2732 | -663.1885 | -94.1033 | -237.4972 | -391.7584 | -375.5656 | -573.6187 | -670.1982 | -674.8584 | -678.7901 | -682.4625 | -824.3003 | -837.1533 | -855.1125 | -103.1176 | -246.7717 | -401.1809 | -383.2503 | -581.4176 | -678.5054 | -683.7136 | -688.1503 | -692.1197 | -833.437 | -841.3258 | -845.1452
|  | SLOUGH BSP | HT |  |  |  |  | -86.075 | -201.2505 | -324.4087 | -285.2273 | -443.7222 | -521.2957 | -525.5457 | -529.3447 | -533.46 | -653.6783 | -664.8885 | -669.3089 | -93.6962 | -236.6197 | -389.9207 | -373.3595 | -570.8625 | -666.5493 | -670.384 | -673.6217 | -677.2431 | -819.3819 | -828.188 | -832.9768 | -102.735 | -246.2431 | -399.9258 | -381.8442 | -579.5952 | -675.9666 | -680.586 | -684.6238 | -689.0605 | -835.4207 | -846.8105 | -851.8044
|  | SLOUGH BSP | HE |  |  |  |  | -85.9556 | -201.0434 | -324.1097 | -284.8263 | -443.1998 | -519.9222 | -523.364 | -525.9579 | -528.7528 | -644.0344 | -651.7987 | -656.1671 | -93.8268 | -236.8309 | -390.386 | -374.1023 | -571.8084 | -666.935 | -670.3105 | -672.6278 | -675.237 | -817.2656 | -830.1982 | -848.6238 | -102.638 | -246.0717 | -399.6738 | -381.5074 | -579.1217 | -674.5095 | -678.2095 | -680.8319 | -683.7003 | -824.7299 | -832.3523 | -837.2391
|  | SLOUGH BSP | CF |  |  |  |  | -84.9536 | -199.4893 | -322.5311 | -282.5385 | -440.5038 | -516.062 | -518.0569 | -519.5589 | -521.2773 | -631.5151 | -639.5559 | -646.8916 | -93.5564 | -236.4319 | -389.8799 | -373.188 | -570.8084 | -665.4829 | -668.2625 | -670.5615 | -672.9329 | -812.586 | -830.7829 | -862.7391 | -101.7901 | -244.7319 | -398.2799 | -379.4687 | -576.6738 | -670.9115 | -673.2431 | -674.9931 | -676.8146 | -812.1809 | -819.7554 | -826.4574
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | SOUTHAMPTON (RESERVE) BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | NO | 29.698 | 7.9635 | 6.9727 | 5.7523 | 4.1788 | 1.0053 | -2.2161 | -5.0426 | -8.81 | -13.0732 | -25.0222 | -35.1579 | -44.3926 | 12.4809 | 11.7472 | 10.5288 | 9.3778 | 6.1033 | 4.086 | 1.4278 | -4.4804 | -8.8998 | -22.6018 | -39.961 | -66.5885 | 2.9809 | 1.989 | 0.838 | -0.63139 | -3.9283 | -7.061 | -9.9283 | -14.9763 | -19.6314 | -31.5732 | -42.4865 | -53.4885
|  | SOUTHAMPTON (RESERVE) BSP | EE |  |  |  |  | 7.9635 | 6.9727 | 5.7523 | 4.1788 | 1.89 | -0.27629 | -3.6171 | -7.5304 | -10.0436 | -19.1212 | -31.4212 | -37.8416 | 12.4809 | 11.7472 | 10.9176 | 9.8686 | 7.886 | 5.9972 | 3.837 | 0.80228 | -1.2998 | -12.9763 | -33.3691 | -53.4753 | 2.9809 | 1.989 | 0.838 | -0.63139 | -2.9763 | -5.1936 | -8.2538 | -12.1059 | -14.5559 | -23.5947 | -37.1865 | -43.9487
|  | SOUTHAMPTON (RESERVE) BSP | HT |  |  |  |  | 8.4309 | 7.6135 | 6.5482 | 5.0533 | 1.0053 | -2.2161 | -5.0426 | -7.0498 | -9.814 | -20.9171 | -34.8926 | -43.4559 | 13.1625 | 12.5778 | 11.7176 | 10.7278 | 7.54 | 5.289 | 3.1604 | 1.9594 | -0.21302 | -8.3834 | -21.5008 | -30.2671 | 3.7125 | 2.8125 | 1.5747 | 0.15534 | -3.9283 | -7.061 | -9.9283 | -11.8365 | -14.71 | -26.064 | -40.9998 | -50.6406
|  | SOUTHAMPTON (RESERVE) BSP | HE |  |  |  |  | 8.3094 | 7.3747 | 6.0033 | 4.7043 | 1.7645 | -0.13649 | -3.1671 | -8.81 | -13.0732 | -25.0222 | -35.1579 | -44.3926 | 12.8115 | 11.9258 | 10.5288 | 9.3778 | 6.1033 | 4.086 | 1.4278 | -4.4804 | -8.8998 | -22.6018 | -39.961 | -65.1487 | 3.6411 | 2.6574 | 1.1339 | -0.21098 | -3.5681 | -5.6232 | -8.6855 | -14.9763 | -19.6314 | -31.5732 | -42.4865 | -53.4885
|  | SOUTHAMPTON (RESERVE) BSP | CF |  |  |  |  | 9.3992 | 8.9431 | 8.4482 | 7.6309 | 6.5941 | 5.5053 | 4.3451 | 2.3502 | 0.11759 | -8.3957 | -16.211 | -23.4181 | 13.4145 | 12.8635 | 12.2543 | 11.3084 | 10.1227 | 8.6696 | 7.1931 | 5.236 | 3.0574 | -9.6324 | -31.0457 | -66.5885 | 4.736 | 4.1962 | 3.6135 | 2.7074 | 1.6002 | 0.42167 | -0.73037 | -2.611 | -4.7232 | -13.2681 | -21.4467 | -28.6202
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | SOUTHAMPTON (MAIN) BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | NO | 37.202 | 21.5848 | 18.9093 | 16.442 | 13.4971 | 7.6512 | 2.992 | -2.8243 | -13.2478 | -21.1049 | -45.9856 | -67.8131 | -88.4376 | 30.4861 | 28.6984 | 26.3045 | 24.0902 | 17.2667 | 13.0106 | 7.9188 | -3.9547 | -12.6333 | -39.422 | -69.7272 | -111.6078 | 21.1698 | 18.7157 | 16.4769 | 13.7014 | 6.8382 | 2.33 | -3.3067 | -15.6465 | -24.4241 | -49.8465 | -73.768 | -97.7976
|  | SOUTHAMPTON (MAIN) BSP | EE |  |  |  |  | 21.5848 | 18.9093 | 16.442 | 13.4971 | 8.7042 | 3.9012 | -0.82433 | -7.308 | -11.6396 | -32.0243 | -59.3784 | -73.7774 | 30.4861 | 28.6984 | 27.029 | 24.8402 | 20.5116 | 16.278 | 12.6188 | 6.6892 | 2.6086 | -18.7976 | -55.5659 | -86.771 | 21.1698 | 18.7157 | 16.4769 | 13.7014 | 8.8616 | 4.1075 | -0.24858 | -6.8323 | -11.0935 | -30.9312 | -61.3894 | -76.5792
|  | SOUTHAMPTON (MAIN) BSP | HT |  |  |  |  | 22.9022 | 20.4461 | 17.6104 | 14.5808 | 8.0471 | 2.992 | -2.8243 | -7.1662 | -13.1784 | -37.5376 | -66.8039 | -85.71 | 31.7973 | 30.2208 | 28.1943 | 26.0973 | 20.1728 | 16.1014 | 11.3341 | 8.278 | 3.1259 | -16.1945 | -43.5108 | -61.7078 | 22.5075 | 20.2637 | 17.5198 | 14.7096 | 7.8341 | 2.8157 | -3.0884 | -7.1272 | -13.3812 | -37.8006 | -69.7496 | -91.0241
|  | SOUTHAMPTON (MAIN) BSP | HE |  |  |  |  | 22.8053 | 20.2297 | 16.9461 | 14.2277 | 7.6512 | 3.2083 | -2.3284 | -13.2478 | -21.1049 | -45.9856 | -67.8131 | -88.4376 | 31.2963 | 29.2565 | 26.3045 | 24.0902 | 17.2667 | 13.0106 | 7.9188 | -3.9547 | -12.6333 | -39.422 | -69.7272 | -111.6078 | 22.4045 | 19.978 | 16.6463 | 14.0382 | 6.8382 | 2.33 | -3.3067 | -15.6465 | -24.4241 | -49.8465 | -73.768 | -97.7976
|  | SOUTHAMPTON (MAIN) BSP | CF |  |  |  |  | 25.1583 | 23.9716 | 22.5838 | 20.6757 | 18.3185 | 15.7287 | 13.4134 | 10.3308 | 7.2257 | -9.6325 | -26.5978 | -42.2366 | 32.3953 | 31.3769 | 30.1708 | 28.3606 | 26.0759 | 23.1841 | 20.4147 | 17.0555 | 13.4443 | -9.7537 | -43.2843 | -95.3874 | 24.2126 | 23.331 | 22.1249 | 20.3014 | 18.029 | 15.4586 | 13.2535 | 10.2514 | 7.1371 | -9.9894 | -27.4567 | -43.4037
NURSLING GSP | SOUTHAMPTON C BSP | SOUTHAMPTON C BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | NO | 5.698 |  |  |  | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 |  |  |  | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 |  |  |  | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482
|  | SOUTHAMPTON C BSP | EE | [7 empty] | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 |  |  |  | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 |  |  |  | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482
|  | SOUTHAMPTON C BSP | HT | [7 empty] | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 |  |  |  | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 |  |  |  | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482
|  | SOUTHAMPTON C BSP | HE | [7 empty] | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 |  |  |  | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 |  |  |  | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482
|  | SOUTHAMPTON C BSP | CF | [7 empty] | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 |  |  |  | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 |  |  |  | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482
LALEHAM GSP | STAINES BSP | STAINES BSP | MINIMUM HEADROOM | TQ 04585 72135 | NO | NO | 35.415 | -20.7889 | -24.3971 | -28.1501 | -31.4869 | -35.6726 | 73.0019 | 66.0325 | 58.9723 | 52.958 | 27.5958 | 6.2744 | -5.5052 | 2.4366 | -0.24096 | -2.994 | -5.6165 | -9.092 | 95.5988 | 90.0264 | 84.3805 | 79.6662 | 58.5213 | 35.7213 | -22.3073 | -20.4705 | -23.6828 | -27.0389 | -30.0756 | -33.9073 | 71.5223 | 64.6468 | 57.7131 | 52.1529 | 29.308 | 9.9264 | -0.67055
|  | STAINES BSP | EE |  |  |  |  | -20.7889 | -24.3971 | -28.1501 | -31.4869 | -35.6726 | 73.0019 | 66.0325 | 58.9723 | 52.958 | 27.6386 | 10.1315 | -3.5032 | 2.4366 | -0.24096 | -2.994 | -5.6165 | -9.092 | 95.5988 | 90.0264 | 84.3805 | 79.6662 | 58.5213 | 37.7437 | 6.1897 | -20.4705 | -23.6828 | -27.0389 | -30.0756 | -33.9073 | 71.5223 | 64.6468 | 57.7131 | 52.1529 | 29.308 | 13.6774 | 1.4131
|  | STAINES BSP | HT |  |  |  |  | -19.2552 | -22.4246 | -25.5481 | -28.8134 | -32.4216 | 77.1897 | 71.5601 | 65.3039 | 58.658 | 27.5958 | 6.2744 | -5.5052 | 4.4121 | 2.5172 | 0.77231 | -1.2369 | -3.5165 | 102.7835 | 99.1488 | 94.8652 | 90.3958 | 71.5407 | 60.2509 | 54.5397 | -18.9338 | -21.6848 | -24.3869 | -27.3338 | -30.6114 | 75.7346 | 70.3907 | 64.4407 | 58.2101 | 29.3825 | 9.9264 | -0.67055
|  | STAINES BSP | HE |  |  |  |  | -19.4318 | -22.5746 | -25.6736 | -28.9012 | -32.5552 | 77.7815 | 72.5488 | 67.0223 | 61.0305 | 30.2825 | 12.9744 | 5.2284 | 3.6407 | 1.3764 | -0.78585 | -3.2501 | -6.1042 | 100.0162 | 95.9611 | 91.5897 | 86.8284 | 62.2356 | 39.3264 | 9.7978 | -19.1308 | -21.8818 | -24.594 | -27.5287 | -30.8828 | 76.1733 | 71.2458 | 66.0713 | 60.4948 | 32.4652 | 17.155 | 9.3764
|  | STAINES BSP | CF |  |  |  |  | -17.3022 | -19.1389 | -21.2042 | -22.7032 | -24.9471 | 87.8295 | 85.206 | 82.7009 | 79.3244 | 60.1192 | 39.7713 | 23.7448 | 4.7111 | 3.055 | 1.1866 | -0.343 | -2.6889 | 104.1958 | 100.9407 | 97.759 | 93.8968 | 70.6927 | 35.7213 | -22.3073 | -17.195 | -18.7991 | -20.6175 | -21.9532 | -24.0022 | 85.2927 | 82.758 | 80.3478 | 77.206 | 58.5468 | 40.407 | 27.8152
MINETY GSP | STRATTON (RESERVE) BSP | STRATTON (RESERVE) BSP | MINIMUM HEADROOM | SU 17028 88748 | NO | NO | 45.49 | -85.7692 | -88.2458 | -90.9886 | -93.26 | -96.5805 | -100.9284 | -106.106 | -111.2427 | -114.4458 | -129.4305 | -139.6498 | -145.1264 | -105.2254 | -106.9866 | -108.7672 | -110.2386 | -112.5652 | -115.5856 | -119.2937 | -123.0366 | -125.2376 | -136.2652 | -147.3621 | -173.7713 | -118.0376 | -120.4468 | -123.0223 | -124.9845 | -127.9274 | -131.9029 | -136.6896 | -141.4519 | -144.0692 | -159.5958 | -167.9835 | -171.1131
|  | STRATTON (RESERVE) BSP | EE |  |  |  |  | -85.7692 | -88.2458 | -90.9886 | -93.26 | -96.5805 | -100.9284 | -106.106 | -111.2427 | -114.4458 | -129.4305 | -138.5498 | -143.606 | -105.2254 | -106.9866 | -108.7672 | -110.2386 | -112.5652 | -115.5856 | -119.2937 | -123.0366 | -125.2376 | -136.2652 | -146.0743 | -158.9182 | -118.0376 | -120.4468 | -123.0223 | -124.9845 | -127.9274 | -131.9029 | -136.6896 | -141.4519 | -144.0692 | -157.1519 | -164.5866 | -168.7407
|  | STRATTON (RESERVE) BSP | HT |  |  |  |  | -84.7386 | -86.8856 | -89.1866 | -92.2468 | -96.0845 | -100.1641 | -104.2396 | -108.7621 | -112.7764 | -129.4213 | -139.6498 | -145.1264 | -104.2743 | -105.6458 | -106.9509 | -108.957 | -111.5223 | -114.0529 | -116.507 | -119.3345 | -121.6917 | -130.8764 | -135.9784 | -138.5203 | -116.8927 | -118.9264 | -120.9743 | -123.7121 | -127.1723 | -130.7447 | -134.2396 | -138.3662 | -142.056 | -156.8662 | -165.4447 | -169.9315
|  | STRATTON (RESERVE) BSP | HE |  |  |  |  | -84.6856 | -86.7682 | -88.9345 | -91.1978 | -94.5754 | -97.9937 | -101.7529 | -106.0754 | -110.2458 | -128.106 | -137.1835 | -140.6162 | -104.5478 | -106.0672 | -107.4845 | -108.956 | -111.3621 | -113.7315 | -116.3611 | -119.5223 | -122.5682 | -135.3968 | -145.0998 | -157.409 | -116.8641 | -118.8437 | -120.7876 | -122.8029 | -125.8519 | -128.8447 | -132.0141 | -136.3815 | -141.0866 | -159.5958 | -167.9835 | -171.1131
|  | STRATTON (RESERVE) BSP | CF |  |  |  |  | -83.6335 | -85.158 | -86.7723 | -88.4754 | -90.3866 | -92.3866 | -95.0325 | -97.256 | -99.5754 | -113.4692 | -125.2978 | -135.5294 | -104.0121 | -105.2754 | -106.46 | -107.7233 | -109.1743 | -110.9131 | -113.1978 | -115.308 | -117.5305 | -131.4529 | -147.3621 | -173.7713 | -115.909 | -117.3927 | -118.8396 | -120.3519 | -122.0305 | -123.8529 | -126.2866 | -128.1723 | -130.1917 | -144.7335 | -157.0845 | -166.5131
MINETY GSP | STRATTON (MAIN) BSP | STRATTON (MAIN) BSP | MINIMUM HEADROOM | SU 17028 88748 | NO | NO | 15.693 | 50.3933 | 49.2352 | 47.8209 | 45.7882 | 42.5984 | 38.8811 | 34.3178 | 29.8403 | 26.2331 | 11.7923 | 5.0944 | 3.6168 | 51.5303 | 50.6099 | 49.4793 | 48.1926 | 45.8364 | 43.4252 | 40.4569 | 37.2313 | 34.566 | 23.8303 | 8.3854 | -24.7217 | 44.9773 | 43.7487 | 42.1671 | 40.3334 | 37.3099 | 33.7762 | 29.4385 | 25.1732 | 21.7497 | 7.9997 | 1.6895 | 0.33849
|  | STRATTON (MAIN) BSP | EE |  |  |  |  | 50.3933 | 49.2352 | 47.8209 | 45.7882 | 42.5984 | 38.8811 | 34.3178 | 29.8403 | 26.2331 | 15.2107 | 10.1158 | 10.6995 | 51.5303 | 50.6099 | 49.4793 | 48.1926 | 45.8364 | 43.4252 | 40.4569 | 37.2313 | 34.566 | 23.8303 | 13.5334 | -1.035 | 44.9773 | 43.7487 | 42.1671 | 40.3334 | 37.3099 | 33.7762 | 29.4385 | 25.1732 | 21.7497 | 11.4354 | 6.6109 | 7.2007
|  | STRATTON (MAIN) BSP | HT |  |  |  |  | 51.4413 | 50.4893 | 49.4372 | 47.1913 | 44.6933 | 41.1719 | 37.7066 | 34.0362 | 30.9189 | 17.6627 | 10.1117 | 8.7331 | 52.4722 | 51.7967 | 51.0354 | 48.8426 | 46.562 | 44.4273 | 42.2875 | 40.0956 | 38.4967 | 31.2171 | 27.6967 | 26.7844 | 46.0069 | 44.866 | 43.612 | 41.3313 | 38.6334 | 35.2538 | 32.0742 | 28.5905 | 25.6711 | 13.4211 | 6.6824 | 5.6211
|  | STRATTON (MAIN) BSP | HE |  |  |  |  | 51.2015 | 50.128 | 48.9321 | 47.7627 | 44.5944 | 41.1638 | 36.9627 | 32.5872 | 28.2474 | 11.7923 | 5.0944 | 3.6168 | 52.1569 | 51.3018 | 50.3426 | 49.3844 | 46.9375 | 44.7181 | 42.0313 | 39.2518 | 36.515 | 24.364 | 13.3691 | -1.6758 | 45.9334 | 44.7773 | 43.4885 | 42.3048 | 39.2446 | 35.9834 | 31.9864 | 27.816 | 23.6813 | 7.9997 | 1.6895 | 0.33849
|  | STRATTON (MAIN) BSP | CF |  |  |  |  | 52.0301 | 51.327 | 50.5842 | 49.7536 | 49.0138 | 47.7852 | 45.8923 | 43.3362 | 40.7025 | 26.2842 | 15.1995 | 7.5097 | 52.6813 | 52.0569 | 51.3752 | 50.5956 | 49.8609 | 48.4844 | 46.564 | 44.3671 | 42.1722 | 28.0579 | 8.3854 | -24.7217 | 46.9864 | 46.3038 | 45.5956 | 44.7916 | 44.0099 | 42.8211 | 40.6364 | 38.0058 | 35.4895 | 21.7069 | 11.2303 | 4.0446
MINETY GSP | SWINDON BSP | SWINDON BSP | MINIMUM HEADROOM | SU 12447 87062 | NO | NO | 21.663 | 31.9211 | 29.5303 | 26.7099 | 24.1038 | 18.9007 | 12.2385 | 4.3497 | -3.9146 | -10.0166 | -29.7248 | -43.1146 | -48.6544 | 44.1163 | 42.1448 | 39.8571 | 37.6601 | 33.551 | 28.8234 | 23.1561 | 17.2499 | 12.852 | -4.1888 | -27.3123 | -77.1113 | 29.5581 | 27.3326 | 24.6632 | 22.153 | 17.151 | 10.9826 | 3.6765 | -3.8909 | -9.2654 | -26.3735 | -37.5195 | -42.0786
|  | SWINDON BSP | EE |  |  |  |  | 31.9211 | 29.5303 | 26.7099 | 24.1038 | 18.9007 | 12.2385 | 4.3497 | -3.9146 | -10.0166 | -29.7248 | -41.2779 | -46.3809 | 44.1163 | 42.1448 | 39.8571 | 37.6601 | 33.551 | 28.8234 | 23.1561 | 17.2499 | 12.852 | -4.1888 | -20.4001 | -44.445 | 29.5581 | 27.3326 | 24.6632 | 22.153 | 17.151 | 10.9826 | 3.6765 | -3.8909 | -9.2654 | -26.3735 | -36.0531 | -40.3297
|  | SWINDON BSP | HT |  |  |  |  | 33.1527 | 31.3803 | 29.3109 | 25.6436 | 20.3895 | 14.2568 | 7.4925 | 1.2436 | -4.4952 | -28.4228 | -43.1146 | -48.6544 | 45.6428 | 44.5948 | 43.3244 | 40.6805 | 37.2377 | 33.754 | 29.6377 | 25.7673 | 22.2622 | 8.002 | 0.27034 | -2.5205 | 30.8265 | 29.2448 | 27.3754 | 23.9581 | 19.2744 | 13.9234 | 7.7999 | 2.1101 | -3.0572 | -24.6531 | -37.5195 | -42.0786
|  | SWINDON BSP | HE |  |  |  |  | 33.0874 | 31.4017 | 29.3599 | 26.7681 | 22.1691 | 16.7405 | 10.3834 | 3.3436 | -2.9962 | -25.9064 | -38.9268 | -43.6177 | 45.0254 | 43.6765 | 42.0581 | 40.005 | 36.4448 | 32.6877 | 28.1938 | 23.0795 | 18.2918 | -2.3797 | -20.498 | -44.0593 | 30.703 | 29.1693 | 27.2918 | 24.9387 | 20.7601 | 15.9193 | 10.251 | 3.8999 | -1.8939 | -22.7664 | -34.1593 | -37.9368
|  | SWINDON BSP | CF |  |  |  |  | 34.8752 | 33.9323 | 33.117 | 32.0089 | 30.6925 | 28.815 | 25.9752 | 23.0538 | 19.2436 | -5.0207 | -21.6983 | -35.7687 | 45.9418 | 44.8714 | 43.8683 | 42.5305 | 40.7999 | 38.404 | 35.2714 | 32.1265 | 28.252 | 3.2101 | -27.3123 | -77.1113 | 32.3499 | 31.452 | 30.6948 | 29.6479 | 28.4071 | 26.6071 | 23.9846 | 21.3346 | 17.7744 | -4.3348 | -18.9746 | -31.246
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM BSP | MINIMUM HEADROOM | SU 52824 66435 | NO | NO | 54.972 | -93.645 | 16.0928 | 10.5122 | 4.302 | -2.7286 | -11.9542 | -22.1348 | -32.2378 | -44.3633 | -98.0052 | -123.6776 | -136.797 | -48.8746 | 57.1693 | 53.0469 | 48.4234 | 42.8458 | 36.2356 | 29.0622 | 18.9683 | 8.4132 | -32.4582 | -56.3011 | -102.5633 | -87.0593 | 20.1244 | 15.2111 | 9.5285 | 2.5938 | -6.097 | -15.6715 | -27.7889 | -40.7042 | -93.1103 | -119.2174 | -134.0552
|  | THATCHAM BSP | EE |  |  |  |  | -93.645 | 16.0928 | 10.5122 | 4.302 | -2.7286 | -11.9542 | -22.1348 | -32.2378 | -40.8501 | -79.5276 | -109.7735 | -125.7042 | -48.8746 | 57.1693 | 53.0469 | 48.4234 | 42.8458 | 36.2356 | 29.0622 | 21.5734 | 15.2652 | -14.3001 | -48.6786 | -82.3582 | -87.0593 | 20.1244 | 15.2111 | 9.5285 | 2.5938 | -6.097 | -15.6715 | -25.8909 | -34.9297 | -72.2674 | -99.548 | -114.2603
|  | THATCHAM BSP | HT |  |  |  |  | -90.5613 | 19.752 | 14.4836 | 9.2693 | 2.4714 | -5.9256 | -15.3021 | -24.2807 | -34.0317 | -78.7235 | -111.8511 | -130.8164 | -45.3786 | 61.4826 | 57.9111 | 54.7316 | 49.6214 | 44.2836 | 37.8081 | 31.4091 | 23.653 | -8.745 | -33.4664 | -47.2838 | -84.2103 | 23.3928 | 18.6346 | 14.0458 | 7.502 | -0.26947 | -8.9776 | -17.1184 | -26.5511 | -69.0154 | -101.4297 | -120.6562
|  | THATCHAM BSP | HE |  |  |  |  | -90.7684 | 19.3499 | 13.6989 | 8.1652 | 0.79278 | -7.2072 | -17.3868 | -31.5756 | -44.3633 | -98.0052 | -123.6776 | -136.797 | -46.1582 | 60.1499 | 55.7785 | 51.805 | 45.606 | 39.2489 | 31.1265 | 18.9683 | 8.4132 | -32.4582 | -56.3011 | -93.6725 | -84.4378 | 22.9469 | 17.7142 | 12.7214 | 5.4734 | -2.7991 | -13.2144 | -27.7889 | -40.7042 | -93.1103 | -119.2174 | -134.0552
|  | THATCHAM BSP | CF |  |  |  |  | -87.9786 | 23.806 | 20.4673 | 16.5438 | 12.9438 | 9.2958 | 4.7224 | 0.3938 | -4.2542 | -39.4368 | -74.8286 | -100.098 | -44.5246 | 62.8509 | 60.2193 | 57.003 | 53.902 | 50.3856 | 45.9356 | 41.6428 | 36.8958 | 4.454 | -39.1082 | -102.5633 | -81.8307 | 27.1571 | 24.255 | 20.7642 | 17.502 | 14.1632 | 10.0336 | 6.0611 | 1.7234 | -34.1705 | -68.7725 | -93.5889
MINETY GSP | TOOTHILL BSP | TOOTHILL BSP | MINIMUM HEADROOM | SU 13191 83945 | NO | NO | 40.257 | 85.1894 | 77.9333 | 73.5139 | 69.7547 | 65.1598 | 58.9669 | 52.7557 | 46.4302 | 41.3445 | 27.5527 | 18.9639 | 15.7761 | 86.7006 | 79.0404 | 76.2231 | 73.818 | 70.9129 | 66.7608 | 61.7639 | 57.0323 | 53.072 | 40.8435 | 30.9302 | 8.8231 | 80.5057 | 72.4118 | 68.321 | 65.0016 | 61.0476 | 55.5608 | 49.5067 | 43.5782 | 38.8823 | 26.169 | 18.0139 | 14.9547
|  | TOOTHILL BSP | EE |  |  |  |  | 88.3669 | 80.819 | 73.5139 | 69.7547 | 65.1598 | 59.368 | 52.7557 | 46.4302 | 41.3445 | 27.5527 | 21.2312 | 18.9231 | 91.1741 | 83.2935 | 76.2231 | 73.818 | 70.9129 | 66.7608 | 61.7639 | 57.0323 | 53.072 | 40.8435 | 30.9302 | 16.8741 | 84.7527 | 76.2465 | 68.321 | 65.0016 | 61.0476 | 55.7506 | 49.5067 | 43.5782 | 38.8823 | 26.2425 | 20.4843 | 18.1639
|  | TOOTHILL BSP | HT |  |  |  |  | 85.2067 | 77.9333 | 75.0057 | 70.5904 | 65.169 | 58.9669 | 53.4812 | 47.9282 | 43.5874 | 27.5792 | 18.9639 | 15.7761 | 87.022 | 79.5292 | 77.9772 | 75.1292 | 71.6843 | 67.4374 | 63.4996 | 59.6792 | 56.7853 | 46.4231 | 40.6955 | 37.9761 | 80.5394 | 72.422 | 69.9649 | 66.0639 | 61.2731 | 55.5608 | 50.4312 | 45.2578 | 41.2261 | 26.169 | 18.0139 | 14.9547
|  | TOOTHILL BSP | HE |  |  |  |  | 85.1894 | 77.9506 | 75.0894 | 71.8853 | 67.0312 | 61.6527 | 56.3904 | 50.922 | 46.3578 | 31.5067 | 24.6149 | 21.469 | 86.7006 | 79.0404 | 77.3251 | 75.4302 | 72.1996 | 68.3955 | 64.4139 | 60.3925 | 56.9333 | 43.5649 | 33.0976 | 18.8302 | 80.5057 | 72.4118 | 70.0047 | 67.2945 | 63.021 | 58.1455 | 53.3067 | 48.3312 | 44.1598 | 30.2649 | 23.8731 | 20.8343
|  | TOOTHILL BSP | CF |  |  |  |  | 90.221 | 83.5486 | 81.42 | 78.968 | 76.3567 | 73.0884 | 69.3118 | 65.1741 | 62.019 | 47.5629 | 39.0894 | 31.2506 | 92.2547 | 84.8476 | 83.4476 | 81.8465 | 80.1078 | 77.419 | 74.1394 | 70.5384 | 67.619 | 52.5363 | 36.2261 | 8.8231 | 86.4812 | 78.8965 | 77.1506 | 75.1088 | 72.9323 | 70.0159 | 66.522 | 62.6965 | 59.8465 | 46.5302 | 38.8669 | 31.9476
IVER 132KV GSP | UPTON BSP | UPTON BSP | MINIMUM HEADROOM | TQ 00838 79445 | NO | YES | 6.347 | 11.668 | 10.6618 | 9.6792 | 8.4271 | 6.7833 | 4.8945 | 2.4465 | 0.46184 | -1.2892 | -8.3739 | -13.6269 | -14.7871 | 20.0333 | 19.1292 | 18.3945 | 17.3496 | 16.0639 | 14.619 | 12.6333 | 11.0527 | 9.6098 | 2.7353 | -5.5973 | -27.1943 | 12.6353 | 11.5904 | 10.7404 | 9.5404 | 7.9904 | 6.1853 | 3.7843 | 1.8792 | 0.19041 | -6.1953 | -10.9443 | -12.082
|  | UPTON BSP | EE |  |  |  |  | 11.668 | 10.6618 | 9.6792 | 8.4271 | 6.7833 | 4.8945 | 2.4465 | 0.46184 | -1.2892 | -8.3739 | -12.2667 | -12.6759 | 20.0333 | 19.1292 | 18.3945 | 17.3496 | 16.0639 | 14.619 | 12.6333 | 11.0527 | 9.6098 | 2.7353 | -4.18 | -14.1922 | 12.6353 | 11.5904 | 10.7404 | 9.5404 | 7.9904 | 6.1853 | 3.7843 | 1.8792 | 0.19041 | -6.1953 | -9.5667 | -10.1535
|  | UPTON BSP | HT |  |  |  |  | 12.3588 | 11.6322 | 10.62 | 9.6506 | 8.3282 | 6.7822 | 4.8139 | 2.8006 | 1.0394 | -8.1933 | -13.6269 | -14.7871 | 20.869 | 20.3322 | 19.6945 | 19.0169 | 18.1537 | 17.2261 | 15.8516 | 14.4639 | 13.322 | 7.4537 | 4.1047 | 3.0231 | 13.4047 | 12.6833 | 11.7547 | 10.8241 | 9.5955 | 8.1741 | 6.2618 | 4.3078 | 2.6567 | -5.9922 | -10.9443 | -12.082
|  | UPTON BSP | HE |  |  |  |  | 12.4251 | 11.7373 | 10.7955 | 9.8935 | 8.6567 | 7.3486 | 5.6241 | 3.9067 | 2.4588 | -4.7759 | -8.6861 | -9.9198 | 20.7067 | 20.0608 | 19.3322 | 18.5496 | 17.5853 | 16.6394 | 15.2271 | 13.8363 | 12.6669 | 5.1047 | -2.0576 | -12.4688 | 13.4608 | 12.769 | 11.9027 | 11.0353 | 9.8853 | 8.7057 | 7.0343 | 5.3884 | 4.0608 | -2.6963 | -6.1637 | -7.6984
|  | UPTON BSP | CF |  |  |  |  | 13.0006 | 12.6547 | 12.1924 | 11.6761 | 10.8873 | 9.8884 | 9.3271 | 8.4373 | 7.4935 | 2.5639 | -3.1851 | -8.4331 | 20.9527 | 20.4843 | 19.9486 | 19.3302 | 18.5149 | 17.4241 | 16.5873 | 15.4251 | 14.1986 | 6.7782 | -5.5973 | -27.1943 | 13.97 | 13.6088 | 13.1353 | 12.5986 | 11.8435 | 10.8588 | 10.3751 | 9.4567 | 8.5037 | 3.8894 | -1.2831 | -5.7667
NURSLING GSP | VELMORE BSP | VELMORE BSP | MINIMUM HEADROOM | SU 42855 19215 | NO | NO | 51.14 | -30.8718 | 78.9282 | 74.3905 | 70.2303 | 65.0813 | 58.716 | 51.9987 | 45.0721 | 39.9129 | 15.8497 | -4.4167 | -15.5411 | -6.2197 | 100.5966 | 97.4354 | 94.3221 | 90.5476 | 86.1221 | 81.3742 | 76.3456 | 72.6048 | 53.5099 | 29.0599 | -26.7197 | -25.485 | 82.2864 | 78.1099 | 74.1242 | 69.2813 | 63.4415 | 57.2558 | 50.8701 | 46.217 | 25.1589 | 8.5609 | -0.61971
|  | VELMORE BSP | EE |  |  |  |  | -30.8718 | 78.9282 | 74.3905 | 70.2303 | 65.0813 | 58.716 | 51.9987 | 45.0721 | 39.9129 | 16.1344 | -1.3667 | -14.4595 | -6.2197 | 100.5966 | 97.4354 | 94.3221 | 90.5476 | 86.1221 | 81.3742 | 76.3456 | 72.6048 | 53.5099 | 34.2905 | 5.0987 | -25.485 | 82.2864 | 78.1099 | 74.1242 | 69.2813 | 63.4415 | 57.2558 | 50.8701 | 46.217 | 25.1589 | 10.9691 | -0.0013469
|  | VELMORE BSP | HT |  |  |  |  | -29.4738 | 80.7048 | 76.7476 | 73.0762 | 68.5211 | 63.3956 | 57.3823 | 51.4395 | 45.7078 | 15.8497 | -4.4167 | -15.5411 | -4.4116 | 103.2344 | 101.1007 | 99.0456 | 96.3936 | 93.7874 | 90.2905 | 86.7231 | 83.2987 | 66.5109 | 57.0609 | 52.4415 | -23.9799 | 84.2762 | 80.8823 | 77.5936 | 73.4833 | 69.0303 | 63.6017 | 58.1752 | 52.8762 | 25.8415 | 8.5609 | -0.61971
|  | VELMORE BSP | HE |  |  |  |  | -29.4513 | 80.5742 | 76.5976 | 72.9364 | 68.4548 | 64.0568 | 58.617 | 53.065 | 47.7946 | 19.9823 | 0.59151 | -7.7779 | -4.9881 | 102.0507 | 99.4874 | 96.9609 | 93.818 | 90.8476 | 86.8884 | 82.618 | 78.4721 | 54.964 | 33.6813 | 6.3436 | -23.9513 | 84.0874 | 80.6497 | 77.368 | 73.2874 | 69.4027 | 64.4007 | 59.1884 | 54.214 | 28.7925 | 12.5323 | 5.6538
|  | VELMORE BSP | CF |  |  |  |  | -27.3197 | 84.0691 | 80.9405 | 78.6925 | 76.2201 | 74.216 | 72.0905 | 69.8762 | 67.2221 | 46.8211 | 27.468 | 10.6293 | -3.9473 | 103.8201 | 101.3895 | 99.5007 | 97.2701 | 94.8599 | 92.2323 | 89.4476 | 86.1527 | 62.9129 | 29.0599 | -26.7197 | -22.0054 | 87.3293 | 84.5507 | 82.5568 | 80.3548 | 78.465 | 76.3609 | 74.1313 | 71.5007 | 52.917 | 35.414 | 20.8762
MANNINGTON GSP | WAREHAM BSP | WAREHAM BSP | MINIMUM HEADROOM | SY 91548 88451 | NO | NO | 2.913 | 12.18 | 11.4208 | 10.8024 | 9.1657 | 8.279 | 6.432 | 4.3922 | 2.7606 | 1.2361 | -7.022 | -12.8598 | -16.1414 | 12.6612 | 11.9827 | 11.4459 | 10.6408 | 10.399 | 9.7602 | 8.502 | 7.4173 | 6.4551 | 1.2551 | -3.3776 | -14.9051 | 10.902 | 9.8255 | 8.7673 | 7.2102 | 6.4745 | 4.8041 | 2.9306 | 1.4102 | 0.045918 | -7.1939 | -12.3765 | -15.202
|  | WAREHAM BSP | EE |  |  |  |  | 12.18 | 11.4208 | 10.8024 | 9.1657 | 8.279 | 6.432 | 4.3922 | 2.7606 | 1.2361 | -6.6914 | -11.7588 | -15.6139 | 12.6612 | 11.9827 | 11.4459 | 10.6408 | 10.399 | 9.7602 | 8.502 | 7.4173 | 6.4551 | 1.2551 | -3.3776 | -10.0245 | 10.902 | 9.8255 | 8.7673 | 7.2102 | 6.4745 | 4.8041 | 2.9306 | 1.4102 | 0.045918 | -6.9388 | -11.3735 | -14.7347
|  | WAREHAM BSP | HT |  |  |  |  | 12.4422 | 11.7565 | 11.2331 | 10.4698 | 9.1147 | 7.3065 | 5.7239 | 4.1831 | 2.178 | -7.022 | -12.8598 | -16.1414 | 12.9163 | 12.3337 | 11.9184 | 11.5918 | 11.2092 | 10.7714 | 10.3306 | 9.5929 | 8.4878 | 3.7398 | 1.0735 | -0.37449 | 11.1531 | 10.402 | 9.5378 | 8.5378 | 7.3418 | 5.7173 | 4.3306 | 2.9673 | 1.1449 | -7.1939 | -12.3765 | -15.202
|  | WAREHAM BSP | HE |  |  |  |  | 12.4402 | 11.7667 | 11.2565 | 10.4371 | 9.1708 | 7.6412 | 6.3382 | 5.0922 | 3.5443 | -4.169 | -9.0741 | -11.3424 | 12.8735 | 12.2694 | 11.8327 | 11.1551 | 10.7469 | 10.2888 | 9.7908 | 9.0418 | 8.0612 | 2.6327 | -2.0908 | -7.9633 | 11.1755 | 10.4755 | 9.698 | 8.4827 | 7.3592 | 5.9898 | 4.85 | 3.7531 | 2.352 | -4.5918 | -8.9143 | -10.8602
|  | WAREHAM BSP | CF |  |  |  |  | 12.7035 | 12.1443 | 11.8443 | 11.0831 | 10.431 | 9.8912 | 8.9841 | 8.1086 | 7.6137 | 3.0076 | -1.9027 | -6.7506 | 13.0184 | 12.4541 | 12.1643 | 11.4653 | 10.9163 | 10.5949 | 10.198 | 9.7837 | 9.2602 | 4.5786 | -2.7071 | -14.9051 | 11.4276 | 10.8255 | 10.4898 | 9.6102 | 8.7235 | 8.048 | 7.2347 | 6.4357 | 6.0173 | 1.801 | -2.599 | -6.8724
MELKSHAM GSP | WEST GRAFTON BSP | WEST GRAFTON BSP | MINIMUM HEADROOM | SU 24302 59215 | NO | NO | 7.68 | 24.2121 | 22.8764 | 21.3489 | 19.6764 | 18.6866 | 16.7336 | 14.4734 | 11.7009 | 10.0907 | -0.33275 | -5.9664 | -9.2236 | 30.9509 | 30.0305 | 28.9683 | 27.7897 | 27.2856 | 25.9877 | 24.4264 | 22.6346 | 21.8142 | 14.9846 | 8.5672 | -6.9532 | 23.9519 | 22.703 | 21.2693 | 19.6887 | 18.9009 | 17.0897 | 14.9601 | 12.4356 | 11.156 | 2.554 | -2.1338 | -4.744
|  | WEST GRAFTON BSP | EE |  |  |  |  | 24.2121 | 22.8764 | 21.3489 | 19.6764 | 18.6866 | 16.7336 | 14.4734 | 11.7009 | 10.0907 | -0.33275 | -5.1164 | -8.3593 | 30.9509 | 30.0305 | 28.9683 | 27.7897 | 27.2856 | 25.9877 | 24.4264 | 22.6346 | 21.8142 | 14.9846 | 9.5234 | 1.5224 | 23.9519 | 22.703 | 21.2693 | 19.6887 | 18.9009 | 17.0897 | 14.9601 | 12.4356 | 11.156 | 2.554 | -1.3409 | -4.0276
|  | WEST GRAFTON BSP | HT |  |  |  |  | 24.6234 | 23.5091 | 22.2734 | 20.9101 | 19.4213 | 17.4377 | 15.9815 | 13.7764 | 11.4815 | -0.26847 | -5.9664 | -9.2236 | 31.6193 | 31.0019 | 30.2652 | 29.5356 | 28.6642 | 27.5652 | 26.9948 | 25.7744 | 24.4938 | 18.403 | 15.6734 | 14.2305 | 24.5417 | 23.555 | 22.406 | 21.1897 | 19.8193 | 18.0162 | 16.8703 | 14.8846 | 12.8213 | 2.6917 | -2.1338 | -4.744
|  | WEST GRAFTON BSP | HE |  |  |  |  | 24.7724 | 23.7213 | 22.4672 | 21.2121 | 19.8662 | 18.2407 | 16.7305 | 14.8081 | 12.7428 | 1.6693 | -3.1062 | -5.2644 | 31.5448 | 30.8724 | 30.0581 | 29.2724 | 28.3754 | 27.2907 | 26.3479 | 25.206 | 23.8224 | 16.2703 | 10.6877 | 3.1152 | 24.653 | 23.7244 | 22.5744 | 21.456 | 20.2101 | 18.7019 | 17.3836 | 15.7928 | 13.9285 | 4.5448 | 0.61929 | -1.1328
|  | WEST GRAFTON BSP | CF |  |  |  |  | 25.3468 | 24.6336 | 23.7754 | 22.8683 | 22.2632 | 21.6428 | 20.7877 | 19.6734 | 19.1826 | 9.2897 | 3.3468 | -1.444 | 31.8377 | 31.303 | 30.6713 | 29.9785 | 29.407 | 28.703 | 27.7968 | 26.7519 | 26.2866 | 17.9377 | 8.5672 | -6.9532 | 25.1948 | 24.555 | 23.7713 | 22.9407 | 22.3601 | 21.7315 | 20.8632 | 19.7989 | 19.4989 | 10.8856 | 5.854 | 1.905
NURSLING GSP | WINCHESTER BSP | WINCHESTER BSP | MINIMUM HEADROOM | SU 44965 26671 | NO | NO | 15.502 | 40.4017 | 37.7762 | 35.066 | 32.0282 | 139.3545 | 134.1729 | 128.3433 | 115.4086 | 105.3831 | 75.3168 | 47.9913 | 21.5974 | 54.1795 | 52.4979 | 48.9591 | 46.7479 | 149.305 | 144.754 | 139.5213 | 125.1152 | 114.3958 | 87.2754 | 60.053 | 22.2305 | 41.8764 | 39.4152 | 36.3316 | 33.3428 | 137.005 | 131.6213 | 125.5203 | 110.503 | 99.1213 | 67.6693 | 37.4979 | 6.2509
|  | WINCHESTER BSP | EE |  |  |  |  | 40.4017 | 37.7762 | 35.5987 | 32.6782 | 142.527 | 137.2392 | 133.0015 | 126.2913 | 121.8219 | 97.5698 | 62.3566 | 46.3158 | 54.1795 | 52.4979 | 50.9856 | 49.1367 | 155.3305 | 151.4887 | 148.903 | 143.5173 | 139.853 | 121.6764 | 82.7407 | 58.9632 | 41.8764 | 39.4152 | 37.4469 | 34.7448 | 141.7795 | 136.5122 | 132.5887 | 125.652 | 121.1693 | 96.7611 | 56.8071 | 39.6326
|  | WINCHESTER BSP | HT |  |  |  |  | 41.5915 | 39.1415 | 35.9456 | 33.5527 | 141.8239 | 136.3137 | 129.9719 | 125.6474 | 118.727 | 89.0004 | 53.7821 | 30.0107 | 54.8693 | 53.1489 | 50.654 | 49.4826 | 153.4938 | 149.1662 | 144.0132 | 141.1111 | 135.0764 | 112.5122 | 79.2418 | 55.4162 | 43.0754 | 40.6836 | 37.4764 | 35.305 | 140.1907 | 134.5316 | 127.9397 | 123.8377 | 116.4958 | 86.0826 | 46.6652 | 19.7367
|  | WINCHESTER BSP | HE |  |  |  |  | 41.6925 | 38.9538 | 35.066 | 32.0282 | 139.3545 | 134.1729 | 128.3433 | 115.4086 | 105.3831 | 75.3168 | 47.9913 | 21.5974 | 54.8111 | 52.5101 | 48.9591 | 46.7479 | 149.305 | 144.754 | 139.5213 | 125.1152 | 114.3958 | 87.2754 | 60.053 | 22.2305 | 43.1489 | 40.4203 | 36.3316 | 33.3428 | 137.005 | 131.6213 | 125.5203 | 110.503 | 99.1213 | 67.6693 | 37.4979 | 6.2509
|  | WINCHESTER BSP | CF |  |  |  |  | 42.867 | 41.4456 | 39.7231 | 37.6242 | 149.4188 | 147.1525 | 145.0423 | 142.4658 | 139.7525 | 121.6484 | 100.4178 | 80.9076 | 55.356 | 54.2775 | 52.9162 | 51.2693 | 159.0611 | 157.0132 | 155.156 | 152.9897 | 150.4897 | 133.3142 | 108.0928 | 71.0887 | 44.2407 | 42.9254 | 41.3734 | 39.3203 | 148.4407 | 146.1377 | 144.0275 | 141.4356 | 138.6009 | 119.8397 | 97.5234 | 77.0224
COWLEY GSP | WITNEY BSP | WITNEY BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | NO | 34.335 | 19.1323 | 16.9037 | 129.0116 | 125.7463 | 122.0249 | 117.6198 | 113.1759 | 108.032 | 104.5228 | 88.9953 | 76.3453 | 68.5953 | 40.1947 | 38.6468 | 146.809 | 144.4703 | 141.8876 | 139.0213 | 136.0539 | 132.5019 | 130.0856 | 118.3111 | 103.3213 | 67.0927 | 23.1152 | 20.9774 | 130.458 | 127.41 | 124.0274 | 120.0549 | 116.0396 | 111.3468 | 108.2284 | 94.6978 | 83.8396 | 77.6029
|  | WITNEY BSP | EE |  |  |  |  | 19.1323 | 16.9037 | 129.0116 | 125.7463 | 122.0249 | 117.6198 | 113.1759 | 108.032 | 104.5228 | 89.3473 | 78.6065 | 70.2616 | 40.1947 | 38.6468 | 146.809 | 144.4703 | 141.8876 | 139.0213 | 136.0539 | 132.5019 | 130.0856 | 118.3111 | 105.909 | 86.8774 | 23.1152 | 20.9774 | 130.458 | 127.41 | 124.0274 | 120.0549 | 116.0396 | 111.3468 | 108.2284 | 94.808 | 85.8376 | 78.9621
|  | WITNEY BSP | HT |  |  |  |  | 20.2169 | 18.1292 | 130.2279 | 127.3392 | 124.3361 | 120.3157 | 115.8126 | 111.6371 | 107.3565 | 88.9953 | 76.3453 | 68.5953 | 41.4927 | 40.3172 | 148.8529 | 147.2141 | 145.6325 | 143.5672 | 141.009 | 138.6805 | 136.109 | 126.0968 | 120.0978 | 116.71 | 24.409 | 22.4815 | 132.0356 | 129.3968 | 126.7488 | 123.2233 | 119.1356 | 115.3509 | 111.36 | 94.6978 | 83.8396 | 77.6029
|  | WITNEY BSP | HE |  |  |  |  | 20.3618 | 18.3955 | 130.6596 | 128.0116 | 125.2892 | 121.9902 | 118.1432 | 114.4667 | 110.7075 | 94.3514 | 83.3943 | 77.8147 | 41.1835 | 39.8305 | 148.206 | 146.4254 | 144.6692 | 142.6039 | 139.9478 | 137.3978 | 134.5539 | 121.0886 | 108.3315 | 90.3284 | 24.5213 | 22.6927 | 132.3958 | 129.9652 | 127.5621 | 124.6437 | 121.1029 | 117.7713 | 114.2437 | 99.4672 | 90.3264 | 85.8815
|  | WITNEY BSP | CF |  |  |  |  | 21.5598 | 20.1292 | 133.1106 | 131.3636 | 129.3789 | 127.8892 | 126.2892 | 124.2136 | 122.2534 | 108.8616 | 97.6167 | 86.8147 | 41.7213 | 40.5825 | 149.2549 | 147.8549 | 146.1866 | 144.6917 | 143.01 | 140.8958 | 138.709 | 124.0152 | 103.3213 | 67.0927 | 25.6192 | 24.2886 | 134.6376 | 133.0529 | 131.2396 | 129.909 | 128.4233 | 126.4254 | 124.5611 | 112.5264 | 102.41 | 92.9539
FLEET-BRAMLEY GSP | WOKINGHAM BSP | WOKINGHAM BSP | MINIMUM HEADROOM | SU 79589 67665 | NO | NO | 12.124 | 79.6129 | 78.2068 | 76.9537 | 75.7435 | 74.1874 | 71.5497 | 68.5823 | 65.6752 | 63.2843 | 51.7609 | 43.8425 | 39.2578 | 84.3407 | 83.3111 | 82.4519 | 81.6152 | 80.4234 | 78.3703 | 75.9795 | 73.7121 | 71.8805 | 63.855 | 55.8509 | 35.2101 | 79.1132 | 77.8346 | 76.7213 | 75.6387 | 74.1601 | 71.5856 | 68.654 | 65.8366 | 63.603 | 53.1856 | 45.5652 | 41.2866
|  | WOKINGHAM BSP | EE |  |  |  |  | 79.6129 | 78.2068 | 76.9537 | 75.7435 | 74.1874 | 71.5497 | 68.5823 | 65.6752 | 63.2843 | 53.1527 | 46.5833 | 41.1354 | 84.3407 | 83.3111 | 82.4519 | 81.6152 | 80.4234 | 78.3703 | 75.9795 | 73.7121 | 71.8805 | 63.855 | 55.8509 | 43.7856 | 79.1132 | 77.8346 | 76.7213 | 75.6387 | 74.1601 | 71.5856 | 68.654 | 65.8366 | 63.603 | 54.4621 | 48.2295 | 43.1785
|  | WOKINGHAM BSP | HT |  |  |  |  | 80.1792 | 78.9762 | 77.6497 | 76.2527 | 75.0609 | 72.4721 | 70.0803 | 67.3537 | 64.5343 | 51.7609 | 43.8425 | 39.2578 | 85.1387 | 84.455 | 83.6856 | 82.8295 | 82.203 | 80.5132 | 78.9754 | 77.1948 | 75.307 | 67.5805 | 63.0764 | 60.4805 | 79.6111 | 78.5652 | 77.4193 | 76.1723 | 75.1397 | 72.6815 | 70.3989 | 67.854 | 65.205 | 53.1856 | 45.5652 | 41.2866
|  | WOKINGHAM BSP | HE |  |  |  |  | 80.3109 | 79.1711 | 77.9282 | 76.6762 | 75.6048 | 73.5792 | 71.7272 | 69.5639 | 67.3231 | 56.7088 | 49.9629 | 46.3374 | 84.9754 | 84.1805 | 83.3081 | 82.3938 | 81.6417 | 80.0621 | 78.6285 | 77.003 | 75.2744 | 66.3019 | 58.0285 | 46.6499 | 79.7172 | 78.7234 | 77.6428 | 76.5315 | 75.5826 | 73.6815 | 71.9213 | 69.957 | 67.8693 | 58.0152 | 51.5509 | 48.1223
|  | WOKINGHAM BSP | CF |  |  |  |  | 81.219 | 80.4446 | 79.6129 | 78.8252 | 78.0241 | 77.0354 | 76.1711 | 75.3364 | 74.2282 | 65.8231 | 59.5201 | 53.5507 | 85.3591 | 84.6897 | 83.9764 | 83.2601 | 82.4346 | 81.2468 | 80.1458 | 79.0509 | 77.6897 | 68.555 | 56.5203 | 35.2101 | 80.5264 | 79.8703 | 79.1703 | 78.5019 | 77.7417 | 76.7142 | 75.856 | 75.0397 | 73.9305 | 66.1938 | 60.7152 | 55.3774
FAWLEY GSP | WOOTTON COMMON BSP | WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ52785 90310 | NO | NO | 20.412 | 51.3396 | 48.6447 | 46.0232 | 43.6763 | 40.8681 | 36.7753 | 31.6804 | 26.5936 | 22.8651 | 3.0896 | -13.1992 | -22.2196 | 61.2255 | 59.2469 | 57.3408 | 55.5367 | 53.3663 | 50.5643 | 46.9918 | 43.3816 | 40.6908 | 26.2827 | 11.5735 | -26.8214 | 52.61 | 50.113 | 47.71 | 45.5202 | 42.9049 | 39.0977 | 34.3242 | 29.5436 | 26.1181 | 8.7977 | -5.4727 | -12.8258
|  | WOOTTON COMMON BSP | EE |  |  |  |  | 51.3396 | 48.6447 | 46.0232 | 43.6763 | 40.8681 | 36.7753 | 31.6804 | 26.5936 | 22.8651 | 3.3089 | -9.8033 | -20.5349 | 61.2255 | 59.2469 | 57.3408 | 55.5367 | 53.3663 | 50.5643 | 46.9918 | 43.3816 | 40.6908 | 26.2827 | 12.3714 | -7.9204 | 52.61 | 50.113 | 47.71 | 45.5202 | 42.9049 | 39.0977 | 34.3242 | 29.5436 | 26.1181 | 8.7977 | -2.5523 | -11.4992
|  | WOOTTON COMMON BSP | HT |  |  |  |  | 52.8079 | 50.7936 | 48.6314 | 46.1896 | 43.9212 | 40.0691 | 35.9028 | 31.9589 | 27.2947 | 3.0896 | -13.1992 | -22.2196 | 62.8673 | 61.6102 | 60.2255 | 58.6847 | 57.2837 | 55.2051 | 52.8888 | 50.7633 | 48.0347 | 34.7061 | 26.7714 | 23.0276 | 54.2171 | 52.3283 | 50.2865 | 48.0253 | 45.9498 | 42.4691 | 38.6885 | 35.1385 | 30.864 | 8.9304 | -5.4727 | -12.8258
|  | WOOTTON COMMON BSP | HE |  |  |  |  | 52.8212 | 50.8885 | 48.7936 | 46.4518 | 44.3447 | 41.162 | 37.6232 | 34.3171 | 30.2742 | 8.7661 | -5.2911 | -11.7319 | 62.5071 | 61.0714 | 59.502 | 57.7163 | 56.0786 | 53.9082 | 51.4255 | 49.0888 | 46.0969 | 29.2663 | 14.3449 | -4.3163 | 54.2018 | 52.3844 | 50.4069 | 48.2375 | 46.2947 | 43.3926 | 40.1436 | 37.1365 | 33.4038 | 13.8773 | 1.6579 | -3.5064
|  | WOOTTON COMMON BSP | CF |  |  |  |  | 54.2681 | 53.0375 | 51.7232 | 50.2804 | 48.7151 | 47.4508 | 45.5283 | 44.2742 | 42.2763 | 28.7202 | 14.1814 | 1.1987 | 63.2245 | 62.1204 | 60.9357 | 59.5724 | 57.9837 | 56.4857 | 54.4041 | 52.7745 | 50.502 | 34.9837 | 11.5735 | -26.8214 | 55.5263 | 54.3651 | 53.1283 | 51.7957 | 50.361 | 49.2242 | 47.4396 | 46.2834 | 44.4089 | 31.7926 | 18.7712 | 7.3049
LOVEDEAN GSP | WYMERING BSP | WYMERING BSP | MINIMUM HEADROOM | SU 64948 05441 | NO | YES | 79.287 | 15.5014 | 14.8024 | 13.5432 | 11.9279 | 10.0197 | 7.8248 | 5.2299 | 2.7463 | 0.67789 | -10.766 | -15.5833 | -16.3609 | 11.4585 | 10.8075 | 9.6636 | 8.3718 | 6.9554 | 5.382 | 3.5024 | 1.7034 | 0.22789 | -8.6864 | -12.3364 | -19.1507 | 11.9024 | 11.0983 | 9.6636 | 8.0442 | 6.2228 | 4.1371 | 1.6656 | -0.6966 | -2.6609 | -13.6599 | -18.2599 | -18.9895
|  | WYMERING BSP | EE |  |  |  |  | 15.5014 | 14.8024 | 13.5432 | 11.9279 | 10.0197 | 7.8248 | 5.2299 | 2.7463 | 0.67789 | -6.7925 | -8.5578 | -8.6752 | 11.4585 | 10.8075 | 9.6636 | 8.3718 | 6.9554 | 5.382 | 3.5024 | 1.7034 | 0.22789 | -5.4476 | -6.6701 | -11.1139 | 11.9024 | 11.0983 | 9.6636 | 8.0442 | 6.2228 | 4.1371 | 1.6656 | -0.6966 | -2.6609 | -9.718 | -11.317 | -11.4364
|  | WYMERING BSP | HT |  |  |  |  | 16.4269 | 15.7371 | 14.9371 | 13.8779 | 13.2616 | 11.7524 | 9.934 | 8.0208 | 5.9759 | -3.2292 | -7.2507 | -7.9384 | 12.2299 | 11.7881 | 11.2759 | 10.6452 | 9.7861 | 8.7391 | 7.4595 | 6.1014 | 4.5116 | -2.4007 | -5.1374 | -5.7792 | 12.6391 | 12.0432 | 11.3575 | 10.4861 | 9.6381 | 8.1922 | 6.4616 | 4.632 | 2.6238 | -6.2211 | -9.8782 | -10.5599
|  | WYMERING BSP | HE |  |  |  |  | 16.2728 | 15.5381 | 14.5054 | 13.2299 | 11.5922 | 9.6075 | 7.1779 | 4.5963 | 1.9065 | -10.766 | -15.5833 | -16.3609 | 11.9187 | 11.3177 | 10.5412 | 9.3728 | 8.1595 | 6.7279 | 4.9514 | 3.0595 | 1.081 | -8.6864 | -12.3364 | -13.2313 | 12.4269 | 11.7361 | 10.7677 | 9.3065 | 7.7401 | 5.8483 | 3.5269 | 1.0565 | -1.5201 | -13.6599 | -18.2599 | -18.9895
|  | WYMERING BSP | CF |  |  |  |  | 16.9208 | 16.4136 | 15.9626 | 15.3728 | 14.735 | 14.034 | 12.9738 | 11.6187 | 10.1269 | 1.5952 | -6.8517 | -11.0884 | 12.3932 | 11.984 | 11.5769 | 11.0401 | 10.4646 | 10.0401 | 9.1136 | 8.0514 | 6.9248 | 0.50647 | -6.8956 | -19.1507 | 13.0993 | 12.6779 | 12.2401 | 11.6667 | 11.0575 | 10.3197 | 9.1075 | 7.7616 | 6.334 | -1.8609 | -9.9088 | -13.8915
COWLEY GSP | YARNTON BSP | YARNTON BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | NO | 141.954 | -36.9756 | 75.7162 | 73.2519 | 69.9152 | 65.6764 | 60.8448 | 55.7907 | 49.5141 | 44.3703 | 22.2692 | 8.9856 | 1.7774 | -18.1797 | 89.5386 | 87.6611 | 85.1488 | 82.0203 | 78.8662 | 75.555 | 71.2641 | 67.9978 | 52.6999 | 37.6039 | 2.5376 | -39.0144 | 69.955 | 67.5733 | 64.4203 | 60.4703 | 56.0927 | 51.5223 | 45.8019 | 41.3795 | 23.0152 | 12.0335 | 6.1029
|  | YARNTON BSP | EE |  |  |  |  | -36.9756 | 75.7162 | 73.2519 | 69.9152 | 65.6764 | 60.8448 | 55.7907 | 49.5141 | 44.3703 | 22.2692 | 10.0662 | 2.5795 | -18.1797 | 89.5386 | 87.6611 | 85.1488 | 82.0203 | 78.8662 | 75.555 | 71.2641 | 67.9978 | 52.6999 | 40.2386 | 22.5856 | -39.0144 | 69.955 | 67.5733 | 64.4203 | 60.4703 | 56.0927 | 51.5223 | 45.8019 | 41.3795 | 23.0152 | 12.9815 | 6.6897
|  | YARNTON BSP | HT |  |  |  |  | -35.5481 | 77.6539 | 75.4244 | 72.5631 | 69.3539 | 63.8631 | 58.1937 | 52.8978 | 47.4039 | 23.2601 | 8.9856 | 1.7774 | -16.3736 | 92.158 | 90.7182 | 88.7886 | 86.9141 | 83.9223 | 80.6131 | 77.5254 | 74.2866 | 61.1835 | 54.5917 | 51.4468 | -37.1624 | 72.4978 | 70.359 | 67.6244 | 64.8111 | 60.0264 | 54.9305 | 50.1988 | 45.3039 | 24.3162 | 12.0335 | 6.1029
|  | YARNTON BSP | HE |  |  |  |  | -35.6961 | 77.457 | 75.1948 | 72.6866 | 69.5315 | 64.9805 | 59.7274 | 54.4866 | 49.0897 | 24.6019 | 11.1907 | 5.8917 | -16.8828 | 91.4141 | 89.706 | 87.7499 | 85.5539 | 82.5825 | 79.0121 | 75.4641 | 71.808 | 53.5539 | 39.5407 | 22.6907 | -37.3369 | 72.2886 | 70.1172 | 67.6662 | 64.8601 | 60.8111 | 56.0039 | 51.3009 | 46.5152 | 24.3356 | 13.7335 | 9.4611
|  | YARNTON BSP | CF |  |  |  |  | -34.2552 | 79.555 | 78.1539 | 76.7305 | 75.0284 | 73.6509 | 71.5897 | 69.107 | 66.1723 | 47.5917 | 29.709 | 17.4397 | -16.1379 | 92.4703 | 91.2039 | 89.8315 | 88.1611 | 86.5999 | 84.4039 | 81.8805 | 79.0978 | 61.6131 | 37.6039 | 2.5376 | -36.0001 | 74.1958 | 72.8131 | 71.3703 | 69.6733 | 68.3417 | 66.2672 | 63.8386 | 61.1192 | 44.6029 | 29.4876 | 19.3284
AXMINSTER GSP | YEOVIL BSP | YEOVIL BSP | MINIMUM HEADROOM | ST 57586 16894 | NO | NO | 64.506 | 13.3686 | 9.9493 | 7.0584 | 2.8942 | -1.6058 | -5.9671 | 64.8962 | 59.2084 | 55.0431 | 34.3003 | 19.087 | 10.3788 | 30.8329 | 28.6013 | 26.7574 | 24.0584 | 94.2962 | 91.6605 | 87.9717 | 84.1921 | 81.4166 | 65.9697 | 46.6095 | 1.8125 | 11.8003 | 8.7064 | 6.1411 | 2.387 | 72.7186 | 68.8717 | 63.6227 | 58.6544 | 54.9217 | 36.2278 | 22.9717 | 15.485
|  | YEOVIL BSP | EE |  |  |  |  | 13.3686 | 9.9493 | 7.0584 | 2.8942 | -1.6058 | -5.9671 | 64.8962 | 59.2084 | 55.0431 | 34.3003 | 20.8819 | 12.0156 | 30.8329 | 28.6013 | 26.7574 | 24.0584 | 94.2962 | 91.6605 | 87.9717 | 84.1921 | 81.4166 | 65.9697 | 50.0278 | 27.2727 | 11.8003 | 8.7064 | 6.1411 | 2.387 | 72.7186 | 68.8717 | 63.6227 | 58.6544 | 54.9217 | 36.2278 | 24.5544 | 16.8595
|  | YEOVIL BSP | HT |  |  |  |  | 14.8421 | 11.9727 | 9.0717 | 5.4013 | 1.536 | -2.8018 | 68.9054 | 63.5829 | 59.3278 | 34.8768 | 19.087 | 10.3788 | 31.9942 | 30.7605 | 29.2105 | 27.2166 | 98.3054 | 96.1952 | 93.488 | 90.6411 | 88.5676 | 76.0737 | 68.4533 | 64.4125 | 13.2819 | 10.7411 | 8.1697 | 4.9197 | 75.8952 | 72.0819 | 67.4931 | 62.688 | 58.9656 | 36.9207 | 22.9717 | 15.485
|  | YEOVIL BSP | HE |  |  |  |  | 14.8993 | 12.086 | 9.2605 | 5.7146 | 1.936 | -1.9293 | 70.2299 | 65.3666 | 61.5829 | 39.0533 | 25.5319 | 19.9248 | 31.8207 | 30.1023 | 28.3074 | 26.0391 | 96.785 | 94.3952 | 91.3646 | 88.1309 | 85.6176 | 68.2319 | 51.8268 | 30.3891 | 13.3258 | 10.8207 | 8.3278 | 5.184 | 76.234 | 72.8503 | 68.6544 | 64.2544 | 60.9533 | 40.6319 | 28.7697 | 23.9921
|  | YEOVIL BSP | CF |  |  |  |  | 16.7278 | 14.9288 | 13.0676 | 10.635 | 7.8401 | 5.1605 | 79.7962 | 76.836 | 73.7064 | 59.2156 | 44.2921 | 30.9788 | 32.6207 | 31.436 | 30.0329 | 28.2064 | 99.2431 | 96.934 | 94.885 | 92.1993 | 89.3554 | 72.8156 | 46.6095 | 1.8125 | 14.9176 | 13.3278 | 11.6972 | 9.5697 | 81.5258 | 79.185 | 77.3197 | 74.6758 | 71.8952 | 58.7258 | 45.3452 | 33.6044

## Primary Generation Headroom
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Generation (MVA) | Generation Headroom Winter (MVA) | [11 empty] | Generation Headroom Summer (MVA) | [11 empty] | Generation Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH BSP | ALDERNEY PRIMARY | MINIMUM HEADROOM | SZ 04270 95141 | NO | YES | 0 | 23.3042 | 22.9147 | 22.0926 | 21.6916 | 21.2779 | 20.84 | 20.4179 | 20.0158 | 19.6326 | 17.9211 | 16.3853 | -10.5484 | 21.3442 | 20.9274 | 20.0126 | 19.5853 | 19.1453 | 18.6726 | 18.2147 | 17.7758 | 17.3579 | 15.4779 | 13.7726 | 12.2168 | 21.5179 | 21.1 | 20.1832 | 19.7558 | 19.3147 | 18.8442 | 18.3905 | 17.9547 | 17.5389 | 15.6726 | 13.98 | 12.4389
|  | ALDERNEY PRIMARY | EE |  |  |  |  | 23.5663 | 23.26 | 22.7253 | 22.2505 | 21.8453 | 21.4716 | 21.1189 | 20.7421 | 20.4211 | 19.0705 | 17.8705 | 16.8095 | 21.6284 | 21.3011 | 20.7126 | 20.1947 | 19.7589 | 19.3589 | 18.9789 | 18.5684 | 18.2179 | 16.74 | 15.4063 | 14.2116 | 21.8021 | 21.4747 | 20.8853 | 20.3663 | 19.9284 | 19.5274 | 19.1484 | 18.74 | 18.3926 | 16.9232 | 15.5979 | 14.4147
|  | ALDERNEY PRIMARY | HT |  |  |  |  | 23.3042 | 22.9147 | 22.0926 | 21.6916 | 21.2779 | 20.84 | 20.4179 | 20.0158 | 19.6326 | 17.9211 | 16.3853 | 14.9958 | 21.3442 | 20.9274 | 20.0126 | 19.5853 | 19.1453 | 18.6726 | 18.2147 | 17.7758 | 17.3579 | 15.4779 | 13.7726 | 12.2168 | 21.5179 | 21.1 | 20.1832 | 19.7558 | 19.3147 | 18.8442 | 18.3905 | 17.9547 | 17.5389 | 15.6726 | 13.98 | 12.4389
|  | ALDERNEY PRIMARY | HE |  |  |  |  | 23.9032 | 23.6989 | 23.2526 | 22.8779 | 22.5642 | 22.28 | 22.0189 | 21.7211 | 21.4832 | 20.5411 | 19.7284 | -10.5484 | 21.9916 | 21.7747 | 21.2811 | 20.8705 | 20.5337 | 20.2305 | 19.9516 | 19.6284 | 19.3705 | 18.3368 | 17.4232 | 16.6242 | 22.1663 | 21.9495 | 21.4547 | 21.0432 | 20.7053 | 20.4011 | 20.1211 | 19.7968 | 19.5389 | 18.5116 | 17.6063 | 16.8147
|  | ALDERNEY PRIMARY | CF |  |  |  |  | 24.1021 | 23.9884 | 23.8705 | 23.7516 | 23.6179 | 23.4695 | 23.2958 | 23.0916 | 22.8863 | 21.9989 | 21.4305 | 20.9558 | 22.2032 | 22.0811 | 21.9558 | 21.8295 | 21.6874 | 21.5274 | 21.3389 | 21.1137 | 20.8884 | 19.9137 | 19.2811 | 18.7389 | 22.3779 | 22.2568 | 22.1305 | 22.0042 | 21.8621 | 21.7011 | 21.5116 | 21.2863 | 21.06 | 20.0821 | 19.4505 | 18.9147
FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT PRIMARY | MINIMUM HEADROOM | SU 85976 48834 | NO | YES | 0.12211 | 17.7208 | 17.4093 | 17.0766 | 16.7335 | 16.3777 | 16.0208 | 15.5061 | 14.9798 | 14.484 | 12.2735 | 10.2619 | -15.0034 | 14.4008 | 13.8114 | 13.1272 | 12.3251 | 11.4956 | 10.9093 | 10.3293 | 9.7598 | 9.2251 | 6.8177 | 4.6008 | 2.6103 | 15.4008 | 14.8282 | 14.144 | 13.3429 | 12.5114 | 11.9261 | 11.344 | 10.7745 | 10.2377 | 7.8219 | 5.5935 | 3.6008
|  | ALDERSHOT PRIMARY | EE |  |  |  |  | 17.9124 | 17.6566 | 17.384 | 17.1029 | 16.8072 | 16.5198 | 16.2482 | 15.9872 | 15.6703 | 13.9166 | 12.3577 | 11.0219 | 14.8103 | 14.3429 | 13.8187 | 13.2051 | 12.5324 | 11.9535 | 11.4577 | 10.9672 | 10.5198 | 8.6208 | 6.9072 | 5.4093 | 15.6103 | 15.3408 | 14.8356 | 14.2208 | 13.5482 | 12.9682 | 12.4703 | 11.9787 | 11.5282 | 9.6156 | 7.8851 | 6.3829
|  | ALDERSHOT PRIMARY | HT |  |  |  |  | 17.7208 | 17.4093 | 17.0766 | 16.7335 | 16.3777 | 16.0208 | 15.5061 | 14.9798 | 14.484 | 12.2735 | 10.2619 | 8.4787 | 14.4008 | 13.8114 | 13.1272 | 12.3251 | 11.4956 | 10.9093 | 10.3293 | 9.7598 | 9.2251 | 6.8177 | 4.6008 | 2.6103 | 15.4008 | 14.8282 | 14.144 | 13.3429 | 12.5114 | 11.9261 | 11.344 | 10.7745 | 10.2377 | 7.8219 | 5.5935 | 3.6008
|  | ALDERSHOT PRIMARY | HE |  |  |  |  | 18.1598 | 17.9819 | 17.7851 | 17.5745 | 17.3461 | 17.1261 | 16.9219 | 16.7293 | 16.5608 | 15.9914 | 15.1198 | -15.0034 | 15.3503 | 15.0514 | 14.6851 | 14.2187 | 13.6808 | 13.2493 | 12.8966 | 12.5429 | 12.2293 | 10.9872 | 9.8935 | 8.944 | 15.8756 | 15.6903 | 15.4829 | 15.2219 | 14.6966 | 14.264 | 13.9114 | 13.5566 | 13.2419 | 11.9945 | 10.8977 | 9.9429
|  | ALDERSHOT PRIMARY | CF |  |  |  |  | 18.3293 | 18.2377 | 18.1419 | 18.0429 | 17.9398 | 17.8335 | 17.7303 | 17.6272 | 17.5229 | 17.0619 | 16.8293 | 16.6398 | 15.6777 | 15.4998 | 15.3177 | 15.1324 | 14.9419 | 14.7451 | 14.5356 | 14.2998 | 14.0619 | 12.9693 | 12.164 | 11.4945 | 16.0556 | 15.9587 | 15.8577 | 15.7524 | 15.644 | 15.5324 | 15.4219 | 15.2987 | 15.0714 | 13.9819 | 13.1745 | 12.5029
MELKSHAM GSP | CHIPPENHAM BSP | ALDERTON PRIMARY | MINIMUM HEADROOM | ST 84609 84059 | NO | YES | 0 | 2.8695 | 2.7768 | 2.68 | 14.5832 | 14.4747 | 14.2947 | 14.1421 | 14.0474 | 13.9505 | 13.4474 | 12.9505 | 9.8284 | 2.7726 | 2.6758 | 2.5747 | 14.4505 | 14.3168 | 14.0326 | 13.7958 | 13.68 | 13.5579 | 12.8737 | 12.1663 | 11.5074 | 3.0042 | 2.8842 | 2.7611 | 14.6389 | 14.5074 | 14.2337 | 14.0053 | 13.8884 | 13.7653 | 13.0811 | 12.3474 | 11.6747
|  | ALDERTON PRIMARY | EE |  |  |  |  | 2.9295 | 2.8537 | 2.7768 | 14.6968 | 14.6053 | 15.6105 | 15.4158 | 15.1789 | 15.0747 | 14.5211 | 13.9253 | 13.4526 | 2.8368 | 2.7579 | 2.6789 | 14.5947 | 14.4979 | 14.3853 | 14.1726 | 13.9147 | 13.8074 | 13.2516 | 12.6463 | 12.1274 | 3.0874 | 2.9905 | 2.8926 | 14.7916 | 14.68 | 14.6337 | 14.4168 | 14.1537 | 14.0411 | 13.4484 | 12.7989 | 12.2674
|  | ALDERTON PRIMARY | HT |  |  |  |  | 2.8695 | 2.7768 | 2.68 | 14.5832 | 14.4747 | 14.2947 | 14.1421 | 14.0474 | 13.9505 | 13.4474 | 12.9505 | 12.5453 | 2.7726 | 2.6758 | 2.5747 | 14.4505 | 14.3168 | 14.0326 | 13.7958 | 13.68 | 13.5579 | 12.8737 | 12.1663 | 11.5074 | 3.0042 | 2.8842 | 2.7611 | 14.6389 | 14.5074 | 14.2337 | 14.0053 | 13.8884 | 13.7653 | 13.0811 | 12.3474 | 11.6747
|  | ALDERTON PRIMARY | HE |  |  |  |  | 3.0105 | 2.9611 | 2.9084 | 14.8526 | 14.7853 | 15.8768 | 15.7242 | 15.5126 | 15.4505 | 15.1084 | 14.7505 | 9.8284 | 2.9221 | 2.8705 | 2.8158 | 14.7589 | 14.6926 | 14.6684 | 14.5021 | 14.2632 | 14.1989 | 13.8453 | 13.4568 | 13.0579 | 3.1968 | 3.1347 | 3.0695 | 15 | 14.9189 | 14.9211 | 14.7505 | 14.5116 | 14.4453 | 14.0758 | 13.6747 | 13.2642
|  | ALDERTON PRIMARY | CF |  |  |  |  | 3.0568 | 3.0305 | 3.0042 | 14.9747 | 14.94 | 14.9011 | 14.8684 | 14.8284 | 14.7821 | 14.5716 | 14.4253 | 14.2737 | 2.9716 | 2.9432 | 2.9147 | 14.8842 | 14.8495 | 14.8105 | 14.7789 | 14.7379 | 14.6916 | 14.3916 | 14.1695 | 13.9147 | 3.2558 | 3.2211 | 3.1853 | 15.1484 | 15.1032 | 15.0516 | 15.0095 | 14.9547 | 14.8874 | 14.5779 | 14.36 | 14.1116
FLEET-BRAMLEY GSP | ALTON BSP | ALRESFORD PRIMARY | MINIMUM HEADROOM | SU 59684 32511 | NO | YES | 5.0179 | 8.813 | 28.2246 | 27.5846 | 26.8941 | 26.1151 | 25.3835 | 24.7256 | 24.2856 | 23.7393 | 20.8183 | 17.9604 | 3.7509 | 4.8635 | 24.1962 | 23.4741 | 22.6888 | 21.8214 | 21.013 | 20.2909 | 19.8362 | 19.2467 | 16.1962 | 13.2362 | 10.9477 | 5.7088 | 25.0383 | 24.3004 | 23.4993 | 22.6035 | 21.7677 | 21.0204 | 20.5456 | 19.9309 | 16.7246 | 13.5877 | 11.2204
|  | ALRESFORD PRIMARY | EE |  |  |  |  | 8.9804 | 28.6319 | 28.0877 | 27.4888 | 26.8067 | 26.1572 | 25.6425 | 25.1846 | 24.693 | 22.1004 | 19.5593 | 17.7698 | 5.1951 | 24.6519 | 24.0341 | 23.3519 | 22.5898 | 21.8814 | 21.3362 | 20.8656 | 20.3509 | 17.6635 | 15.1151 | 13.2119 | 6.0488 | 25.4962 | 24.8688 | 24.1719 | 23.3846 | 22.6456 | 22.0751 | 21.5783 | 21.0362 | 18.1583 | 15.3983 | 13.4004
|  | ALRESFORD PRIMARY | HT |  |  |  |  | 8.813 | 28.2246 | 27.5846 | 26.8941 | 26.1151 | 25.3835 | 24.7256 | 24.2856 | 23.7393 | 20.8183 | 17.9604 | 15.8341 | 4.8635 | 24.1962 | 23.4741 | 22.6888 | 21.8214 | 21.013 | 20.2909 | 19.8362 | 19.2467 | 16.1962 | 13.2362 | 10.9477 | 5.7088 | 25.0383 | 24.3004 | 23.4993 | 22.6035 | 21.7677 | 21.0204 | 20.5456 | 19.9309 | 16.7246 | 13.5877 | 11.2204
|  | ALRESFORD PRIMARY | HE |  |  |  |  | 9.2004 | 29.0467 | 28.7688 | 28.293 | 27.7319 | 27.2319 | 26.8698 | 26.5709 | 26.2425 | 24.5877 | 23.1519 | 3.7509 | 5.6372 | 25.2435 | 24.7898 | 24.2435 | 23.613 | 23.0541 | 22.6656 | 22.3541 | 22.0014 | 20.1941 | 18.6235 | 17.2151 | 6.3709 | 26.0972 | 25.6362 | 25.0814 | 24.4288 | 23.853 | 23.4477 | 23.1246 | 22.7572 | 20.8551 | 19.2035 | 17.7193
|  | ALRESFORD PRIMARY | CF |  |  |  |  | 9.3477 | 29.2698 | 29.1888 | 29.1035 | 28.9404 | 28.6846 | 28.4783 | 28.3141 | 28.1288 | 27.0804 | 26.1719 | 25.3688 | 5.9319 | 25.7225 | 25.4962 | 25.2551 | 24.9793 | 24.693 | 24.4656 | 24.2919 | 24.0888 | 22.9235 | 21.8972 | 20.9898 | 6.5288 | 26.4414 | 26.3509 | 26.1056 | 25.8172 | 25.5309 | 25.2962 | 25.1151 | 24.9056 | 23.6983 | 22.6246 | 21.6656
FLEET-BRAMLEY GSP | ALTON BSP | ALTON LOCAL PRIMARY | MINIMUM HEADROOM | SU 72434 39606 | NO | YES | 0.42105 | 55.9753 | 56.6563 | 55.6489 | 54.5374 | 53.3121 | 52.1753 | 51.1595 | 50.11 | 49.0068 | 43.3858 | 37.9605 | -2.1889 | 46.8216 | 45.2384 | 44.1532 | 42.95 | 41.6605 | 40.4763 | 39.4268 | 38.3353 | 37.1795 | 31.3289 | 25.6689 | 20.8868 | 47.5026 | 45.9184 | 44.8332 | 43.6289 | 42.3121 | 41.0995 | 40.0174 | 38.89 | 37.6963 | 31.6016 | 25.65 | 20.7563
|  | ALTON LOCAL PRIMARY | EE |  |  |  |  | 55.9753 | 57.4647 | 56.6584 | 55.77 | 54.7721 | 53.8468 | 52.9826 | 52.0479 | 51.0574 | 45.9932 | 41.0763 | 37.5553 | 47.1458 | 46.0016 | 45.2553 | 44.2984 | 43.2584 | 42.3205 | 41.4553 | 40.5132 | 39.5037 | 34.4163 | 29.27 | 25.4553 | 48.1816 | 46.7963 | 45.9311 | 44.9732 | 43.9047 | 42.9268 | 42.0184 | 41.0289 | 39.9647 | 34.5279 | 29.1805 | 25.2479
|  | ALTON LOCAL PRIMARY | HT |  |  |  |  | 58.0837 | 56.6563 | 55.6489 | 54.5374 | 53.3121 | 52.1753 | 51.1595 | 50.11 | 49.0068 | 43.3858 | 37.9605 | 33.5753 | 46.8216 | 45.2384 | 44.1532 | 42.95 | 41.6605 | 40.4763 | 39.4268 | 38.3353 | 37.1795 | 31.3289 | 25.6689 | 20.8868 | 47.5026 | 45.9184 | 44.8332 | 43.6289 | 42.3121 | 41.0995 | 40.0174 | 38.89 | 37.6963 | 31.6016 | 25.65 | 20.7563
|  | ALTON LOCAL PRIMARY | HE |  |  |  |  | 59.5342 | 58.5542 | 58.0026 | 57.3532 | 56.5963 | 55.9584 | 55.39 | 54.7668 | 54.0942 | 50.6984 | 47.8121 | -2.1889 | 48.2816 | 47.3016 | 46.7132 | 46.0111 | 45.2268 | 44.5732 | 43.9995 | 43.3595 | 42.6574 | 39.0437 | 35.9353 | 33.1342 | 49.0795 | 47.9816 | 47.3921 | 46.6921 | 45.8858 | 45.2121 | 44.6184 | 43.9574 | 43.2311 | 39.4679 | 36.2468 | 33.3437
|  | ALTON LOCAL PRIMARY | CF |  |  |  |  | 60.5911 | 60.1868 | 59.7153 | 59.2153 | 58.6363 | 58.1174 | 57.7195 | 57.3774 | 57.0426 | 55.0216 | 53.1205 | 51.4342 | 49.4742 | 49.0279 | 48.6226 | 48.0647 | 47.4321 | 46.87 | 46.4511 | 46.0953 | 45.7468 | 43.5879 | 41.5268 | 39.6963 | 50.2721 | 49.8258 | 49.3005 | 48.7437 | 48.1016 | 47.53 | 47.1016 | 46.7353 | 46.3795 | 44.1742 | 42.0511 | 40.1532
MELKSHAM GSP | ANDOVER BSP | ANDOVER PRIMARY | MINIMUM HEADROOM | SU 35240 46643 | NO | YES | 0 | 32.2116 | 32.0158 | 31.8074 | 31.5874 | 31.6253 | 31.2316 | 30.6011 | 29.7874 | 28.9663 | 27.2284 | 25.64 | 11.6916 | 29.86 | 29.5126 | 29.0758 | 28.2663 | 28.2674 | 27.58 | 26.8274 | 25.8411 | 24.8411 | 23.0663 | 21.2884 | 19.5716 | 30.4063 | 30.1526 | 29.7011 | 28.8716 | 28.8747 | 28.1863 | 27.4347 | 26.4505 | 25.4516 | 23.4779 | 21.6989 | 19.9821
|  | ANDOVER PRIMARY | EE |  |  |  |  | 32.3284 | 32.1684 | 31.9968 | 31.8179 | 31.6253 | 31.2316 | 30.6011 | 29.7874 | 28.9663 | 28.2305 | 27.0063 | 25.8463 | 30.1 | 29.8242 | 29.4863 | 28.9305 | 28.2674 | 27.58 | 26.8274 | 25.8411 | 24.8411 | 24.1547 | 22.7789 | 21.4632 | 30.5305 | 30.3632 | 30.1253 | 29.5453 | 28.8747 | 28.1863 | 27.4347 | 26.4505 | 25.4516 | 24.5663 | 23.1905 | 21.8747
|  | ANDOVER PRIMARY | HT |  |  |  |  | 32.2116 | 32.0158 | 31.8074 | 31.5874 | 32.5347 | 31.7263 | 30.9484 | 30.1979 | 29.4442 | 27.2284 | 25.64 | 24.1189 | 29.86 | 29.5126 | 29.0758 | 28.2663 | 29.22 | 28.2579 | 27.3284 | 26.4274 | 25.5432 | 23.0663 | 21.2884 | 19.5716 | 30.4063 | 30.1526 | 29.7011 | 28.8716 | 29.6295 | 28.6663 | 27.7358 | 26.8347 | 25.9516 | 23.4779 | 21.6989 | 19.9821
|  | ANDOVER PRIMARY | HE |  |  |  |  | 32.4779 | 32.3632 | 32.2358 | 32.0989 | 31.9537 | 31.7979 | 31.3116 | 30.56 | 29.8253 | 29.5305 | 28.6505 | 11.6916 | 30.3905 | 30.2295 | 29.9832 | 29.5053 | 28.9274 | 28.3358 | 27.6211 | 26.7021 | 25.8021 | 25.5526 | 24.5558 | 23.6032 | 30.6916 | 30.5716 | 30.4368 | 30.1389 | 29.5347 | 28.9411 | 28.2274 | 27.3105 | 26.4116 | 25.9558 | 24.9579 | 24.0053
|  | ANDOVER PRIMARY | CF |  |  |  |  | 32.5821 | 32.52 | 32.4558 | 32.3905 | 32.3221 | 32.2526 | 32.1832 | 32.1158 | 32.0474 | 30.2432 | 31.1832 | 30.6663 | 30.4979 | 30.4337 | 30.3463 | 30.2105 | 30.0621 | 29.92 | 29.7453 | 29.5484 | 29.3 | 26.2526 | 27.4558 | 26.8253 | 30.8 | 30.7347 | 30.6663 | 30.5958 | 30.5221 | 30.4484 | 30.3716 | 30.1842 | 29.9242 | 26.8621 | 27.8642 | 27.2337
MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST PRIMARY | MINIMUM HEADROOM | SU 37953 46433 | NO | YES | 0.42105 | 35.5632 | 35.2947 | 35.5568 | 35.36 | 35.1463 | 35.9589 | 35.5526 | 35.1389 | 34.7642 | 33.1779 | 30.0095 | -4.2463 | 30.36 | 29.4663 | 28.5758 | 27.7579 | 27.8105 | 27.2642 | 26.8326 | 26.3937 | 25.9937 | 24.4821 | 20.9147 | 17.3737 | 31.86 | 31.26 | 30.3684 | 29.5505 | 29.6011 | 29.0526 | 28.6189 | 28.1768 | 27.7726 | 26.0747 | 22.4905 | 18.9411
|  | ANDOVER EAST PRIMARY | EE |  |  |  |  | 35.7053 | 35.4779 | 37.6432 | 36.9905 | 36.4653 | 35.9589 | 35.5526 | 35.1389 | 34.7642 | 34.6368 | 32.0874 | 29.6095 | 30.7074 | 29.9137 | 29.1021 | 28.38 | 27.8105 | 27.2642 | 26.8326 | 26.3937 | 25.9937 | 26.1053 | 23.2432 | 20.4137 | 32.0137 | 31.7074 | 30.8937 | 30.1716 | 29.6011 | 29.0526 | 28.6189 | 28.1768 | 27.7726 | 27.6895 | 24.8032 | 21.9653
|  | ANDOVER EAST PRIMARY | HT |  |  |  |  | 35.5632 | 35.2947 | 37.1621 | 36.4211 | 37.28 | 36.6747 | 36.1979 | 35.7505 | 35.3263 | 33.1779 | 30.0095 | 26.9 | 30.36 | 29.4663 | 28.5758 | 27.7579 | 28.9032 | 28.2495 | 27.7389 | 27.26 | 26.8053 | 24.4821 | 20.9147 | 17.3737 | 31.86 | 31.26 | 30.3684 | 29.5505 | 30.5137 | 29.8568 | 29.3463 | 28.8653 | 28.4084 | 26.0747 | 22.4905 | 18.9411
|  | ANDOVER EAST PRIMARY | HE |  |  |  |  | 35.9053 | 35.74 | 35.5568 | 35.36 | 35.1463 | 36.9821 | 36.6832 | 36.3895 | 36.1284 | 36.5074 | 34.5368 | -4.2463 | 31.1674 | 30.5147 | 29.8453 | 29.2537 | 28.8042 | 28.3789 | 28.0632 | 27.7516 | 27.4737 | 28.0937 | 25.8442 | 23.5547 | 32.2284 | 32.0347 | 31.6379 | 31.0474 | 30.5968 | 30.1695 | 29.8516 | 29.54 | 29.2611 | 29.6842 | 27.4274 | 25.1305
|  | ANDOVER EAST PRIMARY | CF |  |  |  |  | 36.0474 | 35.9568 | 39.1916 | 38.8674 | 38.5653 | 38.2832 | 38.0989 | 37.9242 | 37.7442 | 36.8442 | 37.1211 | 35.8958 | 31.4021 | 31.1789 | 30.8095 | 30.4463 | 30.1105 | 29.7989 | 29.6011 | 29.4126 | 29.22 | 28.2463 | 28.6979 | 27.2895 | 32.3789 | 32.2779 | 32.6032 | 32.24 | 31.9021 | 31.5905 | 31.3916 | 31.2042 | 31.0105 | 30.0337 | 30.3011 | 28.8874
MELKSHAM GSP | ANDOVER BSP | ANDOVER TOWN PRIMARY | MINIMUM HEADROOM | SU 36207 45078 | NO | YES | 0 | 17.0505 | 16.8463 | 16.6284 | 16.4032 | 16.1716 | 15.94 | 15.7316 | 15.5421 | 15.3684 | 13.9874 | 12.0937 | -0.87158 | 14.9074 | 14.5453 | 14.1621 | 13.7863 | 13.4063 | 13.0305 | 12.6832 | 12.3589 | 12.0526 | 10.5274 | 8.4274 | 6.3484 | 15.3863 | 15.1716 | 14.7821 | 14.4011 | 14.0158 | 13.6347 | 13.2821 | 12.9516 | 12.6411 | 11.0832 | 8.9484 | 6.8663
|  | ANDOVER TOWN PRIMARY | EE |  |  |  |  | 17.1758 | 17.0084 | 16.8274 | 16.6421 | 16.4484 | 16.26 | 16.0821 | 15.9074 | 15.7526 | 15.0347 | 13.5474 | 12.1074 | 15.1463 | 14.8737 | 14.5495 | 14.2442 | 13.9368 | 13.6389 | 13.3516 | 13.0642 | 12.8011 | 11.6726 | 10.0242 | 8.3947 | 15.5095 | 15.3432 | 15.1642 | 14.8663 | 14.5547 | 14.2516 | 13.96 | 13.6674 | 13.4 | 12.2463 | 10.5505 | 8.9074
|  | ANDOVER TOWN PRIMARY | HT |  |  |  |  | 17.0505 | 16.8463 | 16.6284 | 16.4032 | 16.1716 | 15.94 | 15.7316 | 15.5421 | 15.3684 | 13.9874 | 12.0937 | 10.2611 | 14.9074 | 14.5453 | 14.1621 | 13.7863 | 13.4063 | 13.0305 | 12.6832 | 12.3589 | 12.0526 | 10.5274 | 8.4274 | 6.3484 | 15.3863 | 15.1716 | 14.7821 | 14.4011 | 14.0158 | 13.6347 | 13.2821 | 12.9516 | 12.6411 | 11.0832 | 8.9484 | 6.8663
|  | ANDOVER TOWN PRIMARY | HE |  |  |  |  | 17.3347 | 17.2158 | 17.0832 | 16.9421 | 16.7905 | 16.6453 | 16.5095 | 16.3789 | 16.2674 | 15.8758 | 15.2495 | -0.87158 | 15.3158 | 15.1926 | 15.0537 | 14.8558 | 14.6326 | 14.4189 | 14.2095 | 14.0042 | 13.8274 | 13.0979 | 11.8432 | 10.6 | 15.6663 | 15.5474 | 15.4168 | 15.2758 | 15.1263 | 14.9832 | 14.8347 | 14.6253 | 14.4463 | 13.7021 | 12.4126 | 11.1316
|  | ANDOVER TOWN PRIMARY | CF |  |  |  |  | 17.4379 | 17.3758 | 17.3063 | 17.2337 | 17.1568 | 17.0789 | 17.0053 | 16.9316 | 16.8611 | 16.5305 | 16.3305 | 15.7537 | 15.4274 | 15.3589 | 15.2842 | 15.2053 | 15.0642 | 14.8968 | 14.7653 | 14.6421 | 14.5189 | 13.8895 | 13.1074 | 12.3253 | 15.7716 | 15.7074 | 15.6379 | 15.5663 | 15.4916 | 15.4147 | 15.3421 | 15.2663 | 15.1421 | 14.5021 | 13.6989 | 12.8926
BRAMLEY (BASI) GSP | READING BSP | ARBORFIELD PRIMARY | MINIMUM HEADROOM | SU 75949 65766 | NO | YES | 0.21053 | 25.7961 | 25.6329 | 25.4603 | 24.6645 | 23.8613 | 23.0413 | 21.974 | 20.6866 | 19.4245 | 12.0613 | 4.8108 | -8.1829 | 20.8603 | 20.6982 | 20.5245 | 19.6213 | 18.7077 | 17.7761 | 16.5487 | 15.0603 | 13.5992 | 5.034 | -3.426 | -10.645 | 21.6929 | 21.5298 | 21.3561 | 20.4624 | 19.5498 | 18.6203 | 17.394 | 15.9077 | 14.4477 | 5.895 | -2.5502 | -9.7597
|  | ARBORFIELD PRIMARY | EE |  |  |  |  | 25.8919 | 25.7582 | 25.615 | 25.4656 | 24.9171 | 24.1466 | 23.3435 | 22.1035 | 20.8466 | 13.5403 | 6.3129 | 0.060295 | 20.9571 | 20.8245 | 20.6824 | 20.534 | 19.9182 | 19.0361 | 18.1182 | 16.6835 | 15.2256 | 6.7119 | -1.7355 | -9.0502 | 21.7877 | 21.654 | 21.5192 | 21.3687 | 20.7529 | 19.8719 | 18.9529 | 17.5213 | 16.0645 | 7.5592 | -0.87971 | -8.186
|  | ARBORFIELD PRIMARY | HT |  |  |  |  | 25.7961 | 25.6329 | 25.4603 | 24.6645 | 23.8613 | 23.0413 | 21.974 | 20.6866 | 19.4245 | 12.0613 | 4.8108 | -1.3744 | 20.8603 | 20.6982 | 20.5245 | 19.6213 | 18.7077 | 17.7761 | 16.5487 | 15.0603 | 13.5992 | 5.034 | -3.426 | -10.645 | 21.6929 | 21.5298 | 21.3561 | 20.4624 | 19.5498 | 18.6203 | 17.394 | 15.9077 | 14.4477 | 5.895 | -2.5502 | -9.7597
|  | ARBORFIELD PRIMARY | HE |  |  |  |  | 26.0256 | 25.934 | 25.8319 | 25.7224 | 25.4656 | 24.7561 | 23.9708 | 22.7666 | 21.5792 | 14.6003 | 7.6824 | -8.1829 | 21.0887 | 20.9971 | 20.895 | 20.7856 | 20.5045 | 19.6898 | 18.7835 | 17.3856 | 16.0024 | 7.8424 | -0.26918 | -7.2102 | 21.9224 | 21.8308 | 21.7287 | 21.6192 | 21.3445 | 20.5329 | 19.6287 | 18.2329 | 16.8519 | 8.7056 | 0.60977 | -6.3187
|  | ARBORFIELD PRIMARY | CF |  |  |  |  | 26.4529 | 26.4045 | 26.015 | 25.9645 | 25.9108 | 25.8571 | 25.8035 | 25.7508 | 25.6982 | 22.9792 | 17.0013 | 11.3687 | 23.3129 | 23.2087 | 21.0782 | 21.0277 | 20.974 | 20.9203 | 20.8666 | 20.814 | 20.7613 | 17.6056 | 10.5908 | 3.975 | 23.9845 | 23.9329 | 21.9119 | 21.8613 | 21.8077 | 21.754 | 21.7003 | 21.6477 | 21.595 | 18.4529 | 11.4508 | 4.8477
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ARGYLE ROAD PRIMARY | MINIMUM HEADROOM | SZ 93193 99152 | NO | YES | 0 | 35.0032 | 34.7326 | 34.4442 | 34.1442 | 33.8316 | 33.5168 | 33.2368 | 32.9811 | 32.7442 | 30.6158 | 26.7316 | 0.77053 | 30.4189 | 30.14 | 29.5895 | 29.0379 | 28.4747 | 27.9147 | 27.4105 | 26.9189 | 26.4379 | 22.9095 | 18.4811 | 13.8063 | 30.8505 | 30.5642 | 30.26 | 29.8842 | 29.3126 | 28.7442 | 28.2337 | 27.7337 | 27.2526 | 23.7232 | 19.2947 | 14.6179
|  | ARGYLE ROAD PRIMARY | EE |  |  |  |  | 35.1779 | 34.9611 | 34.7295 | 34.4842 | 34.2295 | 33.9821 | 33.7432 | 33.5126 | 33.3063 | 32.5347 | 29.7211 | 26.4347 | 30.5937 | 30.3768 | 30.1389 | 29.7232 | 29.2611 | 28.8158 | 28.3947 | 27.9863 | 27.6116 | 25.18 | 21.8189 | 18.0305 | 31.0358 | 30.8063 | 30.5632 | 30.3053 | 30.0389 | 29.66 | 29.2326 | 28.8189 | 28.4379 | 25.9947 | 22.6316 | 18.8432
|  | ARGYLE ROAD PRIMARY | HT |  |  |  |  | 35.0032 | 34.7326 | 34.4442 | 34.1442 | 33.8316 | 33.5168 | 33.2368 | 32.9811 | 32.7442 | 30.6158 | 26.7316 | 22.6589 | 30.4189 | 30.14 | 29.5895 | 29.0379 | 28.4747 | 27.9147 | 27.4105 | 26.9189 | 26.4379 | 22.9095 | 18.4811 | 13.8063 | 30.8505 | 30.5642 | 30.26 | 29.8842 | 29.3126 | 28.7442 | 28.2337 | 27.7337 | 27.2526 | 23.7232 | 19.2947 | 14.6179
|  | ARGYLE ROAD PRIMARY | HE |  |  |  |  | 35.3505 | 35.1821 | 34.9968 | 34.7979 | 34.5853 | 34.3821 | 34.1905 | 34.0116 | 33.8568 | 33.3253 | 31.9674 | 0.77053 | 30.7663 | 30.5979 | 30.4126 | 30.2137 | 30 | 29.7905 | 29.4884 | 29.2 | 28.94 | 27.0811 | 24.28 | 21.0589 | 31.2232 | 31.0463 | 30.8537 | 30.6474 | 30.4253 | 30.2137 | 30.0158 | 29.8305 | 29.6695 | 27.8958 | 25.0947 | 21.8726
|  | ARGYLE ROAD PRIMARY | CF |  |  |  |  | 35.4789 | 35.3821 | 35.2811 | 35.1768 | 35.0684 | 34.9589 | 34.8505 | 34.7432 | 34.6358 | 34.1579 | 33.9158 | 33.4905 | 30.8947 | 30.7979 | 30.6968 | 30.5926 | 30.4842 | 30.3747 | 30.2663 | 30.1589 | 30.0484 | 29.0684 | 27.8642 | 25.9337 | 31.3579 | 31.2558 | 31.1505 | 31.0411 | 30.9274 | 30.8126 | 30.6989 | 30.5863 | 30.4737 | 29.9147 | 28.68 | 26.7474
COWLEY GSP | HEADINGTON BSP | ARNCOTT PRIMARY | MINIMUM HEADROOM | SP 60730 18095 | NO | YES | 0.47368 | 22.8984 | 22.6447 | 21.4311 | 20.05 | 18.4595 | 17.1026 | 15.9237 | 14.7584 | 13.6005 | 8.6942 | 6.3437 | -12.8679 | 22.4553 | 22.1763 | 20.7679 | 19.1637 | 17.3142 | 15.7405 | 14.3763 | 13.0258 | 11.6816 | 6.0026 | 3.3237 | 2.1542 | 22.6016 | 22.3247 | 20.9374 | 19.3563 | 17.5332 | 15.9816 | 14.6353 | 13.3542 | 12.0111 | 6.3247 | 3.6268 | 2.45
|  | ARNCOTT PRIMARY | EE |  |  |  |  | 22.9774 | 22.8068 | 21.6279 | 20.2816 | 18.7247 | 17.4005 | 16.2479 | 15.0984 | 13.9584 | 9.1532 | 6.9384 | 6.1047 | 22.5374 | 22.3521 | 20.9837 | 19.4153 | 17.6026 | 16.0658 | 14.7289 | 13.3974 | 12.0753 | 6.5195 | 4.0047 | 3.0658 | 22.6837 | 22.5005 | 21.1489 | 19.7384 | 17.9279 | 16.3911 | 15.0553 | 13.7226 | 12.3995 | 6.8279 | 4.2826 | 3.3332
|  | ARNCOTT PRIMARY | HT |  |  |  |  | 22.8984 | 22.6447 | 21.4311 | 20.05 | 18.4595 | 17.1026 | 15.9237 | 14.7584 | 13.6005 | 8.6942 | 6.3437 | 5.3047 | 22.4553 | 22.1763 | 20.7679 | 19.1637 | 17.3142 | 15.7405 | 14.3763 | 13.0258 | 11.6816 | 6.0026 | 3.3237 | 2.1542 | 22.6016 | 22.3247 | 20.9374 | 19.3563 | 17.5332 | 15.9816 | 14.6353 | 13.3542 | 12.0111 | 6.3247 | 3.6268 | 2.45
|  | ARNCOTT PRIMARY | HE |  |  |  |  | 23.0763 | 22.9932 | 21.8995 | 20.6037 | 19.0889 | 17.8163 | 16.7142 | 15.6142 | 14.5268 | 9.99 | 8.0563 | -12.8679 | 22.6384 | 22.5521 | 21.2784 | 19.7637 | 17.9974 | 16.5142 | 15.23 | 13.9489 | 12.6816 | 7.3932 | 5.15 | 4.3995 | 22.7847 | 22.6995 | 21.4426 | 19.9521 | 18.2121 | 16.7511 | 15.4847 | 14.2226 | 12.9742 | 7.7289 | 5.4816 | 4.7237
|  | ARNCOTT PRIMARY | CF |  |  |  |  | 23.1626 | 23.1279 | 23.0889 | 23.0426 | 22.6468 | 22.0542 | 21.3416 | 20.5679 | 19.7353 | 15.7521 | 14.3542 | 13.9405 | 22.7311 | 22.6953 | 22.6553 | 22.6068 | 22.1479 | 21.4605 | 20.6289 | 19.7247 | 18.7511 | 14.0942 | 12.47 | 11.9995 | 22.8774 | 22.8416 | 22.8016 | 22.7521 | 22.2995 | 21.6195 | 20.8005 | 19.9111 | 18.9511 | 14.3658 | 12.7616 | 12.2921
FLEET-BRAMLEY GSP | BRACKNELL BSP | ASCOT PRIMARY | MINIMUM HEADROOM | SU 91615 68855 | NO | YES | 0 | 35.3547 | 35.1263 | 34.8853 | 34.6347 | 34.6737 | 34.4579 | 34.2505 | 34.0474 | 33.8653 | 32.0221 | 29.8674 | 7.3474 | 30.9674 | 30.5284 | 29.6968 | 28.9274 | 29.0379 | 28.4189 | 28.0684 | 27.6832 | 27.3263 | 25.3011 | 22.9011 | 20.7379 | 31.1895 | 30.9484 | 30.2284 | 29.4611 | 29.5695 | 28.9474 | 28.5937 | 28.2042 | 27.8442 | 25.7074 | 23.2842 | 21.1126
|  | ASCOT PRIMARY | EE |  |  |  |  | 35.4916 | 35.3032 | 35.1063 | 34.8958 | 34.6737 | 34.4579 | 34.2505 | 34.0474 | 33.8653 | 33.1947 | 31.4453 | 29.9558 | 31.2642 | 30.9126 | 30.3495 | 29.6621 | 29.0379 | 28.4189 | 28.0684 | 27.6832 | 27.3263 | 26.5979 | 24.6589 | 22.9716 | 31.3347 | 31.1368 | 30.8642 | 30.1958 | 29.5695 | 28.9474 | 28.5937 | 28.2042 | 27.8442 | 26.9926 | 25.0221 | 23.3253
|  | ASCOT PRIMARY | HT |  |  |  |  | 35.3547 | 35.1263 | 34.8853 | 34.6347 | 35.0421 | 34.7758 | 34.5368 | 34.3221 | 34.0116 | 32.0221 | 29.8674 | 27.9537 | 30.9674 | 30.5284 | 29.6968 | 28.9274 | 29.2 | 28.7547 | 28.34 | 27.8937 | 27.48 | 25.3011 | 22.9011 | 20.7379 | 31.1895 | 30.9484 | 30.2284 | 29.4611 | 29.6347 | 29.1884 | 28.7705 | 28.3211 | 27.9042 | 25.7074 | 23.2842 | 21.1126
|  | ASCOT PRIMARY | HE |  |  |  |  | 35.6642 | 35.5295 | 35.3811 | 35.2232 | 35.0474 | 34.8811 | 34.7221 | 34.5737 | 34.4442 | 34.6621 | 33.5895 | 7.3474 | 31.5453 | 31.4063 | 30.9621 | 30.6021 | 30.0842 | 29.5853 | 29.0926 | 28.8011 | 28.5653 | 28.3737 | 26.9474 | 25.6895 | 31.52 | 31.38 | 31.2137 | 31.0442 | 30.6063 | 30.1168 | 29.6221 | 29.3284 | 29.0916 | 28.7916 | 27.3579 | 26.0916
|  | ASCOT PRIMARY | CF |  |  |  |  | 35.7811 | 35.7074 | 35.6316 | 35.5537 | 35.4695 | 35.3853 | 35.3011 | 35.2179 | 35.1347 | 34.7642 | 35.2411 | 35.0347 | 31.6621 | 31.5884 | 31.5126 | 31.2653 | 30.9632 | 30.6611 | 30.4789 | 30.3211 | 30.1558 | 29.2789 | 29.3179 | 28.5095 | 31.6421 | 31.5642 | 31.4832 | 31.3937 | 31.2968 | 31.1747 | 30.9958 | 30.8411 | 30.6768 | 29.8063 | 29.7432 | 28.9295
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ASHLING ROAD PRIMARY | MINIMUM HEADROOM | SU 84085 06737 | NO | YES | 0.0063158 | 28.2098 | 27.6635 | 26.2119 | 42.6108 | 40.5972 | 38.3098 | 36.1645 | 34.5645 | 33.0614 | 26.3719 | 21.1277 | -17.0365 | 18.7087 | 17.0614 | 15.3635 | 31.5582 | 29.3393 | 26.7572 | 24.3277 | 22.5329 | 20.8624 | 13.3151 | 7.3845 | 1.9372 | 20.1529 | 18.554 | 16.9056 | 33.0835 | 30.8266 | 28.2477 | 25.8224 | 24.0298 | 22.3656 | 14.8287 | 8.9066 | 3.4677
|  | ASHLING ROAD PRIMARY | EE |  |  |  |  | 28.5393 | 28.0929 | 27.2624 | 43.9561 | 42.214 | 40.1856 | 38.1856 | 36.7845 | 35.4424 | 29.9235 | 25.7698 | 22.0119 | 19.4077 | 17.9708 | 16.5403 | 33.0108 | 31.0887 | 28.8108 | 26.5403 | 24.9708 | 23.4624 | 17.2403 | 12.5235 | 8.2266 | 20.8351 | 19.4424 | 18.054 | 34.5624 | 32.5961 | 30.2982 | 28.0319 | 26.4645 | 24.9582 | 18.7498 | 14.0403 | 9.7508
|  | ASHLING ROAD PRIMARY | HT |  |  |  |  | 28.2098 | 27.6635 | 26.2119 | 42.6108 | 40.5972 | 38.3098 | 36.1645 | 34.5645 | 33.0614 | 26.3719 | 21.1277 | 16.3382 | 18.7087 | 17.0614 | 15.3635 | 31.5582 | 29.3393 | 26.7572 | 24.3277 | 22.5329 | 20.8624 | 13.3151 | 7.3845 | 1.9372 | 20.1529 | 18.554 | 16.9056 | 33.0835 | 30.8266 | 28.2477 | 25.8224 | 24.0298 | 22.3656 | 14.8287 | 8.9066 | 3.4677
|  | ASHLING ROAD PRIMARY | HE |  |  |  |  | 28.9656 | 28.6508 | 28.3035 | 45.5129 | 44.0645 | 42.2561 | 40.4708 | 39.2877 | 38.1582 | 33.5772 | 30.3582 | -17.0365 | 20.3298 | 19.1772 | 18.0214 | 34.7519 | 33.0687 | 31.0624 | 29.0287 | 27.6951 | 26.4172 | 21.1803 | 17.4919 | 14.1729 | 21.7361 | 20.6203 | 19.5003 | 36.274 | 34.6087 | 32.5508 | 30.5172 | 29.1866 | 27.9098 | 22.6761 | 18.994 | 15.6814
|  | ASHLING ROAD PRIMARY | CF |  |  |  |  | 29.2593 | 29.0951 | 28.9235 | 46.8466 | 46.6635 | 46.3477 | 45.4698 | 44.8635 | 44.2066 | 41.1129 | 39.0235 | 37.2119 | 21.0835 | 20.4793 | 19.9172 | 37.3593 | 36.6045 | 35.6803 | 34.634 | 33.9224 | 33.1898 | 29.7435 | 27.3551 | 25.2624 | 22.4498 | 21.8845 | 21.3393 | 38.8024 | 38.0729 | 37.1814 | 36.1729 | 35.474 | 34.7235 | 31.2319 | 28.8477 | 26.7582
MELKSHAM GSP | NORRINGTON BSP | ASHTON PARK PRIMARY | MINIMUM HEADROOM | ST 87141 57741 | NO | YES | 0 | 33.56 | 32.2021 | 30.9484 | 28.9326 | 26.1 | 23.4874 | 20.5032 | 17.8032 | 15.3084 | 5.9747 | -1.4074 | -23.5442 | 27.7011 | 26.3137 | 24.9316 | 22.6547 | 19.4168 | 16.4411 | 13.0116 | 9.9095 | 7.0432 | -3.6558 | -12.1326 | -16.9905 | 29.26 | 27.7505 | 26.3684 | 24.0916 | 20.8526 | 17.8747 | 14.4442 | 11.3411 | 8.4747 | -2.2284 | -10.7095 | -15.5695
|  | ASHTON PARK PRIMARY | EE |  |  |  |  | 34.2137 | 33.0663 | 31.9758 | 30.3537 | 28.0611 | 25.8653 | 23.1432 | 20.0189 | 17.3895 | 10.4916 | 4.1021 | 0.79263 | 28.4063 | 27.2611 | 26.0558 | 24.2263 | 21.6084 | 19.1032 | 15.9726 | 12.3621 | 9.3284 | 1.9884 | -5.3811 | -9.1653 | 29.9768 | 28.6989 | 27.4926 | 25.6632 | 23.0442 | 20.5379 | 17.4053 | 13.7947 | 10.76 | 3.7295 | -3.6442 | -7.4295
|  | ASHTON PARK PRIMARY | HT |  |  |  |  | 33.56 | 32.2021 | 30.9484 | 28.9326 | 26.1 | 23.4874 | 20.5032 | 17.8032 | 15.3084 | 5.9747 | -1.4074 | -5.6789 | 27.7011 | 26.3137 | 24.9316 | 22.6547 | 19.4168 | 16.4411 | 13.0116 | 9.9095 | 7.0432 | -3.6558 | -12.1326 | -16.9905 | 29.26 | 27.7505 | 26.3684 | 24.0916 | 20.8526 | 17.8747 | 14.4442 | 11.3411 | 8.4747 | -2.2284 | -10.7095 | -15.5695
|  | ASHTON PARK PRIMARY | HE |  |  |  |  | 35.0295 | 34.1305 | 33.2811 | 31.8832 | 29.7726 | 27.7758 | 25.1768 | 22.3042 | 19.9442 | 12.4389 | 6.9368 | -23.5442 | 29.28 | 28.4221 | 27.4789 | 25.8926 | 23.4716 | 21.1811 | 18.1779 | 14.8453 | 12.1105 | 3.4221 | -2.9726 | -5.8305 | 30.8663 | 29.8589 | 28.9158 | 27.3295 | 24.9074 | 22.6168 | 19.6105 | 16.2779 | 13.5421 | 4.8505 | -1.5463 | -4.4053
|  | ASHTON PARK PRIMARY | CF |  |  |  |  | 35.6158 | 35.1916 | 34.7916 | 34.3432 | 33.7768 | 33.1663 | 32.2905 | 31.1263 | 29.7474 | 22.2537 | 18.8726 | 17.2895 | 29.9116 | 29.5968 | 29.1547 | 28.6547 | 28.0189 | 27.3295 | 26.3284 | 24.9853 | 23.3895 | 14.6874 | 10.7653 | 8.9368 | 31.5084 | 31.0347 | 30.5926 | 30.0926 | 29.4558 | 28.7663 | 27.7653 | 26.4221 | 24.8263 | 16.1189 | 12.1979 | 10.3674
FLEET-BRAMLEY GSP | BRACKNELL BSP | BAGSHOT PRIMARY | MINIMUM HEADROOM | SU 91122 63523 | NO | YES | 0 | 27.595 | 27.2613 | 26.9045 | 26.5371 | 26.1624 | 25.7845 | 25.4518 | 25.1508 | 24.8718 | 22.9045 | 20.9087 | -0.55237 | 23.8034 | 23.2076 | 22.5592 | 21.9045 | 21.2539 | 20.615 | 20.0276 | 19.5108 | 19.0308 | 16.7403 | 14.5045 | 12.5161 | 24.6455 | 24.1876 | 23.5403 | 22.8855 | 22.235 | 21.5961 | 21.0087 | 20.4908 | 20.0097 | 17.7161 | 15.4739 | 13.4855
|  | BAGSHOT PRIMARY | EE |  |  |  |  | 27.8045 | 27.5318 | 27.2413 | 26.9413 | 26.6297 | 26.3287 | 26.0445 | 25.7666 | 25.5224 | 24.4539 | 22.9161 | 21.6055 | 24.2139 | 23.7434 | 23.2382 | 22.7161 | 22.1866 | 21.6803 | 21.1813 | 20.6655 | 20.2603 | 18.4455 | 16.7203 | 15.2276 | 24.8539 | 24.5824 | 24.2182 | 23.6971 | 23.1676 | 22.6592 | 22.1592 | 21.6434 | 21.2371 | 19.415 | 17.6803 | 16.1855
|  | BAGSHOT PRIMARY | HT |  |  |  |  | 27.595 | 27.2613 | 26.9045 | 26.5371 | 26.1624 | 25.7845 | 25.4518 | 25.1508 | 24.8718 | 22.9045 | 20.9087 | 19.1539 | 23.8034 | 23.2076 | 22.5592 | 21.9045 | 21.2539 | 20.615 | 20.0276 | 19.5108 | 19.0308 | 16.7403 | 14.5045 | 12.5161 | 24.6455 | 24.1876 | 23.5403 | 22.8855 | 22.235 | 21.5961 | 21.0087 | 20.4908 | 20.0097 | 17.7161 | 15.4739 | 13.4855
|  | BAGSHOT PRIMARY | HE |  |  |  |  | 28.0739 | 27.8876 | 27.6792 | 27.4571 | 27.2182 | 26.9887 | 26.7729 | 26.5666 | 26.395 | 25.7908 | 25.4076 | -0.55237 | 24.5276 | 24.3329 | 24.1118 | 23.7455 | 23.3592 | 22.9918 | 22.6224 | 22.2539 | 21.9918 | 20.8339 | 19.7097 | 18.7655 | 25.1224 | 24.9361 | 24.7287 | 24.5076 | 24.2697 | 23.9718 | 23.6003 | 23.2318 | 22.9708 | 21.8087 | 20.6834 | 19.7382
|  | BAGSHOT PRIMARY | CF |  |  |  |  | 28.2508 | 28.1529 | 28.0487 | 27.9424 | 27.8329 | 27.7192 | 27.6076 | 27.4971 | 27.3855 | 26.8845 | 26.6129 | 26.4455 | 24.7108 | 24.6076 | 24.4982 | 24.3876 | 24.2739 | 24.0961 | 23.8982 | 23.6855 | 23.4666 | 22.4508 | 21.6424 | 20.9708 | 25.2971 | 25.2003 | 25.0961 | 24.9908 | 24.8824 | 24.7687 | 24.6582 | 24.5476 | 24.4382 | 23.4297 | 22.6203 | 21.9476
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BALL HILL PRIMARY | MINIMUM HEADROOM | SU 42417 63142 | NO | YES | 0 | 16.7568 | 16.5758 | 16.3916 | 16.2084 | 16.0253 | 15.8379 | 15.6705 | 15.5137 | 15.3674 | 14.7484 | 14.1474 | 0.99789 | 14.7863 | 14.5905 | 14.3916 | 14.1937 | 13.9968 | 13.7958 | 13.6137 | 13.4453 | 13.2853 | 12.6105 | 11.9368 | 11.2358 | 15.2747 | 15.0789 | 14.88 | 14.6811 | 14.4853 | 14.2842 | 14.1021 | 13.9337 | 13.7737 | 13.0979 | 12.4253 | 11.7242
|  | BALL HILL PRIMARY | EE |  |  |  |  | 16.8832 | 16.7389 | 16.5926 | 16.4453 | 16.2979 | 16.1558 | 16.0137 | 15.88 | 15.7558 | 15.2758 | 14.8695 | 14.4053 | 14.9263 | 14.7695 | 14.6116 | 14.4526 | 14.2937 | 14.1421 | 13.9895 | 13.8453 | 13.7105 | 13.1853 | 12.7316 | 12.1989 | 15.4 | 15.2579 | 15.1 | 14.9411 | 14.7821 | 14.6305 | 14.4779 | 14.3337 | 14.1989 | 13.6737 | 13.22 | 12.6863
|  | BALL HILL PRIMARY | HT |  |  |  |  | 16.7568 | 16.5758 | 16.3916 | 16.2084 | 16.0253 | 15.8379 | 15.6705 | 15.5137 | 15.3674 | 14.7484 | 14.1474 | 13.5337 | 14.7863 | 14.5905 | 14.3916 | 14.1937 | 13.9968 | 13.7958 | 13.6137 | 13.4453 | 13.2853 | 12.6105 | 11.9368 | 11.2358 | 15.2747 | 15.0789 | 14.88 | 14.6811 | 14.4853 | 14.2842 | 14.1021 | 13.9337 | 13.7737 | 13.0979 | 12.4253 | 11.7242
|  | BALL HILL PRIMARY | HE |  |  |  |  | 17.0421 | 16.9579 | 16.8579 | 16.7558 | 16.6516 | 16.5505 | 16.4558 | 16.3621 | 16.2832 | 15.9884 | 15.7737 | 0.99789 | 15.1084 | 15.0095 | 14.9032 | 14.7937 | 14.6832 | 14.5758 | 14.4758 | 14.3747 | 14.2895 | 13.9716 | 13.7337 | 13.4253 | 15.4916 | 15.4305 | 15.3632 | 15.2821 | 15.1716 | 15.0642 | 14.9642 | 14.8632 | 14.7779 | 14.46 | 14.2221 | 13.9137
|  | BALL HILL PRIMARY | CF |  |  |  |  | 17.0989 | 17.0705 | 17.0368 | 16.9832 | 16.9274 | 16.8705 | 16.8126 | 16.7579 | 16.7021 | 16.4463 | 16.2642 | 16.1095 | 15.2053 | 15.1505 | 15.0937 | 15.0347 | 14.9747 | 14.9126 | 14.8495 | 14.7905 | 14.7305 | 14.4495 | 14.2453 | 14.0663 | 15.5505 | 15.52 | 15.4884 | 15.4558 | 15.4221 | 15.3874 | 15.3379 | 15.2779 | 15.2189 | 14.9379 | 14.7337 | 14.5547
MELKSHAM GSP | ANDOVER BSP | BARTON STACEY PRIMARY | MINIMUM HEADROOM | SU 42075 42720 | NO | YES | 12.8421 | 4.4695 | 4.5463 | 4.4905 | 4.4295 | 4.3379 | 3.9874 | 3.5726 | 3.6179 | 3.54 | 1.9074 | 0.95263 | -11.8211 | 2.9326 | 2.8716 | 2.6937 | 2.5211 | 2.3105 | 1.9179 | 1.4442 | 1.3621 | 1.2853 | -0.51789 | -1.6 | -2.2842 | 3.2579 | 3.0916 | 2.9137 | 2.7411 | 2.5305 | 2.1358 | 1.6632 | 1.5789 | 1.5011 | -0.25579 | -1.3484 | -2.0368
|  | BARTON STACEY PRIMARY | EE |  |  |  |  | 5.1232 | 5 | 4.8684 | 4.7368 | 4.6042 | 4.4726 | 4.3495 | 4.2253 | 4.1042 | 1.9074 | 0.95263 | 0.35053 | 3.0989 | 2.9674 | 2.8263 | 2.6853 | 2.5453 | 2.4074 | 2.2758 | 2.1442 | 2.0168 | -0.51789 | -1.6 | -2.2842 | 3.3779 | 3.2463 | 3.1042 | 2.9642 | 2.8221 | 2.6832 | 2.5516 | 2.4189 | 2.2895 | -0.25579 | -1.3484 | -2.0368
|  | BARTON STACEY PRIMARY | HT |  |  |  |  | 4.4695 | 4.8579 | 4.6926 | 4.5316 | 4.3379 | 3.9874 | 3.5726 | 3.6179 | 3.54 | 2.7484 | 1.7537 | 1.4453 | 2.9326 | 2.8716 | 2.6937 | 2.5211 | 2.3105 | 1.9179 | 1.4442 | 1.3621 | 1.2853 | 0.41579 | -0.7 | -1.0274 | 3.2579 | 3.0916 | 2.9137 | 2.7411 | 2.5305 | 2.1358 | 1.6632 | 1.5789 | 1.5011 | 0.62526 | -0.49684 | -0.82842
|  | BARTON STACEY PRIMARY | HE |  |  |  |  | 4.5968 | 4.5463 | 4.4905 | 4.4295 | 4.3642 | 4.8232 | 4.7358 | 4.6495 | 4.5653 | 2.4884 | 1.8968 | -11.8211 | 3.1916 | 3.1116 | 3.0211 | 2.9284 | 2.8347 | 2.8453 | 2.7547 | 2.6621 | 2.5726 | 0.15263 | -0.66737 | -1.2126 | 3.5358 | 3.4516 | 3.3558 | 3.2589 | 3.16 | 3.0642 | 2.9726 | 2.88 | 2.7895 | 0.36842 | -0.45263 | -1.0011
|  | BARTON STACEY PRIMARY | CF |  |  |  |  | 4.6463 | 4.62 | 4.5937 | 4.5653 | 4.5358 | 4.5053 | 4.4758 | 4.4463 | 4.4168 | 4.2863 | 4.2168 | 4.0558 | 3.2716 | 3.2253 | 3.1726 | 3.1137 | 3.0505 | 2.9895 | 2.9358 | 2.8853 | 2.8274 | 2.5453 | 2.2347 | 1.9305 | 3.6116 | 3.5705 | 3.5147 | 3.4516 | 3.3821 | 3.3158 | 3.2611 | 3.2053 | 3.1432 | 2.8379 | 2.5095 | 2.2021
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | BASINGSTOKE PRIMARY | MINIMUM HEADROOM | SU 65155 52705 | NO | YES | 0 | 31.4653 | 31.1168 | 30.7632 | 30.4074 | 30.0558 | 28.96 | 27.8947 | 26.8463 | 25.8211 | 24.2158 | 24.24 | 7.0663 | 29.2926 | 28.9221 | 28.5484 | 28.1726 | 27.8021 | 26.5568 | 25.34 | 24.1411 | 22.9663 | 21.3189 | 20.1105 | 18.6758 | 29.6421 | 29.2695 | 28.8926 | 28.5147 | 28.1421 | 26.8968 | 25.6811 | 24.4853 | 23.3116 | 21.6884 | 21.7158 | 20.5884
|  | BASINGSTOKE PRIMARY | EE |  |  |  |  | 31.6811 | 31.3989 | 31.1095 | 30.8168 | 30.5232 | 30.2389 | 29.4653 | 28.4421 | 27.3989 | 24.9179 | 24.24 | 23.2179 | 29.5242 | 29.2253 | 28.92 | 28.6126 | 28.3042 | 28.0053 | 27.1326 | 25.96 | 24.76 | 21.9516 | 21.3453 | 20.2168 | 29.8368 | 29.5758 | 29.2684 | 28.9579 | 28.6484 | 28.3474 | 27.4716 | 26.3011 | 25.1032 | 22.2989 | 21.7158 | 20.5884
|  | BASINGSTOKE PRIMARY | HT |  |  |  |  | 31.4653 | 31.1168 | 30.7632 | 30.4074 | 30.0558 | 28.96 | 27.8947 | 26.8463 | 25.8211 | 24.2158 | 28.7189 | 28.0958 | 29.2926 | 28.9221 | 28.5484 | 28.1726 | 27.8021 | 26.5568 | 25.34 | 24.1411 | 22.9663 | 21.3189 | 20.1105 | 18.6758 | 29.6421 | 29.2695 | 28.8926 | 28.5147 | 28.1421 | 26.8968 | 25.6811 | 24.4853 | 23.3116 | 21.6884 | 25.0232 | 24.1653
|  | BASINGSTOKE PRIMARY | HE |  |  |  |  | 31.9042 | 31.7747 | 31.6211 | 31.4221 | 31.2168 | 31.02 | 30.3526 | 29.5053 | 28.6768 | 30.1126 | 29.8495 | 7.0663 | 29.8495 | 29.6674 | 29.4674 | 29.2589 | 29.0442 | 28.8389 | 28.0895 | 27.1147 | 26.1589 | 23.9958 | 23.5453 | 23.0263 | 30.0632 | 29.9189 | 29.7663 | 29.6032 | 29.3947 | 29.1884 | 28.4274 | 27.4537 | 26.5 | 26.9547 | 26.6316 | 26.3358
|  | BASINGSTOKE PRIMARY | CF |  |  |  |  | 31.9758 | 31.8821 | 31.7853 | 31.6874 | 31.5789 | 31.4368 | 31.2979 | 31.1063 | 30.8811 | 28.2863 | 27.7368 | 27.2958 | 29.9611 | 29.8379 | 29.7116 | 29.5705 | 29.4263 | 29.2768 | 29.1316 | 28.9232 | 28.6789 | 25.7105 | 25.1147 | 24.6389 | 30.1474 | 30.0442 | 29.9379 | 29.8295 | 29.7189 | 29.6053 | 29.4821 | 29.2726 | 29.0253 | 26.0516 | 25.4579 | 24.9821
NURSLING GSP | VELMORE BSP | BASSETT PRIMARY | MINIMUM HEADROOM | SU 42193 15958 | NO | YES | 0 | 33.7853 | 33.5179 | 33.2347 | 32.9411 | 32.6347 | 32.3274 | 32.0558 | 31.8074 | 31.5789 | 29.0884 | 26.9579 | 2.8526 | 30.3137 | 29.8116 | 29.2326 | 28.6484 | 28.1211 | 27.6063 | 27.1358 | 26.6895 | 26.1947 | 23.3516 | 21 | 18.8653 | 31.04 | 30.7726 | 30.4389 | 29.8705 | 29.3547 | 28.8516 | 28.3821 | 27.9326 | 27.4316 | 24.5505 | 22.1632 | 20.0032
|  | BASSETT PRIMARY | EE |  |  |  |  | 33.9474 | 33.7295 | 33.4979 | 33.2537 | 33 | 32.7547 | 32.52 | 32.2926 | 32.0905 | 30.7 | 29.0389 | 27.5905 | 30.5705 | 30.2611 | 29.8053 | 29.3474 | 28.8126 | 28.2737 | 27.8726 | 27.4874 | 27.1432 | 25.1116 | 23.2768 | 21.6611 | 31.2021 | 30.9842 | 30.7526 | 30.4979 | 30.0284 | 29.5053 | 29.1126 | 28.7337 | 28.3874 | 26.3242 | 24.46 | 22.8179
|  | BASSETT PRIMARY | HT |  |  |  |  | 33.7853 | 33.5179 | 33.2347 | 32.9411 | 32.6347 | 32.3274 | 32.0558 | 31.8074 | 31.5789 | 29.0884 | 26.9579 | 25.0411 | 30.3137 | 29.8116 | 29.2326 | 28.6484 | 28.1211 | 27.6063 | 27.1358 | 26.6895 | 26.1947 | 23.3516 | 21 | 18.8653 | 31.04 | 30.7726 | 30.4389 | 29.8705 | 29.3547 | 28.8516 | 28.3821 | 27.9326 | 27.4316 | 24.5505 | 22.1632 | 20.0032
|  | BASSETT PRIMARY | HE |  |  |  |  | 34.1421 | 33.9832 | 33.8063 | 33.6168 | 33.4147 | 33.22 | 33.0358 | 32.8663 | 32.7168 | 32.2116 | 31.6168 | 2.8526 | 30.7737 | 30.6126 | 30.4284 | 30.1758 | 29.7558 | 29.3295 | 29.0516 | 28.7905 | 28.5611 | 27.3074 | 26.0779 | 24.9695 | 31.3968 | 31.2379 | 31.0611 | 30.8716 | 30.6695 | 30.4653 | 30.2558 | 29.9989 | 29.7726 | 28.5505 | 27.3042 | 26.1758
|  | BASSETT PRIMARY | CF |  |  |  |  | 34.2821 | 34.1958 | 34.1053 | 34.0126 | 33.9158 | 33.8179 | 33.72 | 33.6253 | 33.5295 | 33.1 | 32.8842 | 32.7621 | 30.9137 | 30.8274 | 30.7368 | 30.6411 | 30.5421 | 30.4389 | 30.3158 | 30.14 | 29.9621 | 29.0747 | 28.2568 | 27.4979 | 31.5368 | 31.4505 | 31.36 | 31.2674 | 31.1705 | 31.0726 | 30.9747 | 30.88 | 30.7842 | 30.28 | 29.4947 | 28.7358
NORTH HYDE GSP | NORTH HYDE BSP | BATH ROAD EAST PRIMARY | MINIMUM HEADROOM | TQ 09097 76885 | NO | NO | 0 | 13.1474 | 13.0747 | 12.9989 | 41.0179 | 40.9337 | 40.8495 | 40.7737 | 40.7032 | 40.6389 | 40.2421 | 39.4632 | 23.74 | 10.5253 | 10.3589 | 10.18 | 38.0853 | 37.8811 | 37.7 | 37.5295 | 37.3642 | 37.2074 | 36.4684 | 35.6 | 34.7516 | 11.04 | 10.8716 | 10.6916 | 38.5937 | 38.3884 | 38.2053 | 38.0326 | 37.8663 | 37.7074 | 36.96 | 36.0789 | 35.2189
|  | BATH ROAD EAST PRIMARY | EE |  |  |  |  | 13.1884 | 13.1284 | 13.0642 | 41.0968 | 41.0253 | 40.9568 | 40.8895 | 40.8253 | 40.7674 | 40.5484 | 40.2684 | 39.7305 | 10.6284 | 10.5105 | 10.3832 | 38.3463 | 38.1916 | 38.0463 | 37.9105 | 37.7726 | 37.6474 | 37.0642 | 36.4958 | 35.8916 | 11.1442 | 11.0253 | 10.8968 | 38.8579 | 38.7021 | 38.5558 | 38.4189 | 38.28 | 38.1537 | 37.5642 | 36.9874 | 36.3737
|  | BATH ROAD EAST PRIMARY | HT |  |  |  |  | 13.1474 | 13.0747 | 12.9989 | 41.0179 | 40.9337 | 40.8495 | 40.7737 | 40.7032 | 40.6389 | 40.2421 | 39.4632 | 38.7084 | 10.5253 | 10.3589 | 10.18 | 38.0853 | 37.8811 | 37.7 | 37.5295 | 37.3642 | 37.2074 | 36.4684 | 35.6 | 34.7516 | 11.04 | 10.8716 | 10.6916 | 38.5937 | 38.3884 | 38.2053 | 38.0326 | 37.8663 | 37.7074 | 36.96 | 36.0789 | 35.2189
|  | BATH ROAD EAST PRIMARY | HE |  |  |  |  | 13.2337 | 13.1853 | 13.1337 | 41.1768 | 41.1168 | 41.0589 | 41.0053 | 40.9537 | 40.9116 | 40.76 | 40.6663 | 23.74 | 10.7421 | 10.6568 | 10.5621 | 38.5547 | 38.4316 | 38.3158 | 38.2042 | 38.0968 | 38.0053 | 37.5884 | 37.1042 | 36.6642 | 11.1968 | 11.1484 | 11.0779 | 39.0695 | 38.9453 | 38.8274 | 38.7158 | 38.6063 | 38.5147 | 38.0937 | 37.6021 | 37.1558
|  | BATH ROAD EAST PRIMARY | CF |  |  |  |  | 13.2674 | 13.2389 | 13.2105 | 41.28 | 41.2484 | 41.2158 | 41.1853 | 41.1537 | 41.1232 | 40.9832 | 40.9137 | 40.8737 | 10.8505 | 10.8158 | 10.7474 | 38.7716 | 38.6905 | 38.6042 | 38.5389 | 38.4705 | 38.4042 | 38.06 | 37.7537 | 37.46 | 11.2305 | 11.2021 | 11.1737 | 39.2432 | 39.2053 | 39.1189 | 39.0537 | 38.9842 | 38.9168 | 38.5684 | 38.2589 | 37.9611
IVER 132KV GSP | LONGFORD BSP | BATH ROAD WEST PRIMARY | MINIMUM HEADROOM | TQ 05814 76820 | NO | NO | 2 | 34.4189 | 34.3726 | 34.3232 | 34.2726 | 34.2189 | 34.1663 | 34.1189 | 34.0758 | 34.0358 | 33.8779 | 33.3126 | 1.1137 | 30.1295 | 30.0589 | 29.2158 | 29.1726 | 29.1284 | 29.0853 | 29.0432 | 29.0032 | 28.9632 | 28.2263 | 27.5579 | 26.9326 | 30.7432 | 30.6968 | 30.1 | 30.0568 | 30.0126 | 29.9695 | 29.9274 | 29.8874 | 29.8474 | 29.1147 | 28.4463 | 27.8221
|  | BATH ROAD WEST PRIMARY | EE |  |  |  |  | 34.4453 | 34.4074 | 34.3663 | 34.3232 | 34.2789 | 34.2358 | 34.1937 | 34.1537 | 34.1179 | 33.9989 | 33.9084 | 33.5642 | 30.1695 | 30.1137 | 29.2158 | 29.1726 | 29.1284 | 29.0853 | 29.0432 | 29.0032 | 28.9674 | 28.7874 | 28.3158 | 27.8411 | 30.7695 | 30.7316 | 30.1 | 30.0568 | 30.0126 | 29.9695 | 29.9274 | 29.8874 | 29.8516 | 29.6737 | 29.2032 | 28.7295
|  | BATH ROAD WEST PRIMARY | HT |  |  |  |  | 34.4189 | 34.3726 | 34.3232 | 34.2726 | 34.2189 | 34.1663 | 34.1189 | 34.0758 | 34.0358 | 33.8779 | 33.3126 | 32.7684 | 30.1295 | 30.0589 | 29.9589 | 29.84 | 29.6747 | 29.4821 | 29.3021 | 29.1274 | 28.9632 | 28.2263 | 27.5579 | 26.9326 | 30.7432 | 30.6968 | 30.6474 | 30.5968 | 30.5432 | 30.3653 | 30.1853 | 30.0116 | 29.8474 | 29.1147 | 28.4463 | 27.8221
|  | BATH ROAD WEST PRIMARY | HE |  |  |  |  | 34.4789 | 34.4495 | 34.4179 | 34.3842 | 34.3474 | 34.3126 | 34.28 | 34.2495 | 34.2232 | 34.1337 | 34.0663 | 1.1137 | 30.2168 | 30.1747 | 30.1242 | 30.0674 | 29.9842 | 29.9011 | 29.82 | 29.7211 | 29.6116 | 29.1295 | 28.6916 | 28.3116 | 30.8032 | 30.7737 | 30.7421 | 30.7084 | 30.6716 | 30.6368 | 30.6042 | 30.5737 | 30.4958 | 30.0137 | 29.5737 | 29.1947
|  | BATH ROAD WEST PRIMARY | CF |  |  |  |  | 36.3979 | 36.3821 | 36.3653 | 36.3484 | 36.3305 | 36.3126 | 36.2947 | 36.2779 | 36.26 | 36.1821 | 36.1432 | 36.1211 | 30.2947 | 30.2674 | 30.2358 | 30.2 | 30.16 | 30.1189 | 30.0779 | 30.0358 | 29.9916 | 29.7853 | 29.6305 | 29.4916 | 31.4895 | 31.4705 | 31.4495 | 31.4274 | 31.4032 | 31.3779 | 31.3537 | 31.3295 | 31.3042 | 31.0842 | 30.9705 | 30.8747
IVER 132KV GSP | DENHAM BSP | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | MINIMUM HEADROOM | SU 93668 91219 | NO | NO | 0.043158 | 12.8285 | 12.6695 | 12.5022 | 12.3295 | 42.1432 | 41.9558 | 41.7895 | 41.6369 | 41.4948 | 40.7958 | 39.7295 | 20.4653 | 10.1064 | 9.6443 | 9.1369 | 8.5537 | 38.2558 | 37.9485 | 37.6601 | 37.3653 | 37.0811 | 35.7643 | 34.5643 | 33.5116 | 10.6937 | 10.5169 | 10.0706 | 9.4864 | 39.1864 | 38.8758 | 38.5864 | 38.2895 | 38.0011 | 36.6643 | 35.4411 | 34.379
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | EE |  |  |  |  | 12.9264 | 12.7979 | 12.6611 | 12.5179 | 42.3632 | 42.2106 | 42.0643 | 41.9222 | 41.7937 | 41.2769 | 40.7001 | 40.0074 | 10.3137 | 9.9148 | 9.4685 | 8.9432 | 38.7011 | 38.4601 | 38.2222 | 37.9674 | 37.7243 | 36.6464 | 35.6874 | 34.8853 | 10.7979 | 10.6537 | 10.4011 | 9.8758 | 39.6306 | 39.3874 | 39.1453 | 38.8874 | 38.639 | 37.5348 | 36.5432 | 35.7306
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | HT |  |  |  |  | 12.8285 | 12.6695 | 12.5022 | 12.3295 | 42.1432 | 41.9558 | 41.7895 | 41.6369 | 41.4948 | 40.7958 | 39.7295 | 38.8085 | 10.1064 | 9.6443 | 9.1369 | 8.5537 | 38.2558 | 37.9485 | 37.6601 | 37.3653 | 37.0811 | 35.7643 | 34.5643 | 33.5116 | 10.6937 | 10.5169 | 10.0706 | 9.4864 | 39.1864 | 38.8758 | 38.5864 | 38.2895 | 38.0011 | 36.6643 | 35.4411 | 34.379
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | HE |  |  |  |  | 13.0485 | 12.959 | 12.859 | 12.7516 | 42.6316 | 42.5158 | 42.4074 | 42.3053 | 42.2148 | 41.8948 | 41.7011 | 20.4653 | 10.5822 | 10.2685 | 9.9022 | 9.4527 | 39.2832 | 39.1127 | 38.9495 | 38.7695 | 38.599 | 37.8927 | 37.3032 | 36.7853 | 10.9253 | 10.8253 | 10.7106 | 10.3853 | 40.2148 | 40.0432 | 39.8769 | 39.6958 | 39.5243 | 38.8064 | 38.2074 | 37.6811
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | CF |  |  |  |  | 13.1316 | 13.0832 | 13.0337 | 12.9822 | 42.9264 | 42.8685 | 42.8137 | 42.7579 | 42.7032 | 42.4527 | 42.319 | 42.2358 | 10.7222 | 10.6506 | 10.4674 | 10.2537 | 40.1558 | 40.0569 | 39.9569 | 39.8453 | 39.7295 | 39.1801 | 38.7506 | 38.3853 | 11.0085 | 10.9601 | 10.9074 | 10.8464 | 40.7885 | 40.7285 | 40.6706 | 40.6127 | 40.5548 | 40.1064 | 39.6716 | 39.3011
IVER 132KV GSP | UPTON BSP | BEACONSFIELD (END BUSBARS) PRIMARY | MINIMUM HEADROOM | SU 93668 91219 | NO | NO | 0 | 6.1811 | 6.0758 | 5.9653 | 5.8505 | 0.73368 | 0.61579 | 0.49474 | 0.33684 | 0.18842 | -0.47053 | -1.0389 | -7.8842 | 4.94 | 4.7463 | 4.5547 | 4.3632 | -0.82526 | -1.0168 | -1.1905 | -1.3642 | -1.5274 | -2.2716 | -2.9316 | -3.5158 | 5.2221 | 5.0316 | 4.8432 | 4.6558 | -0.52947 | -0.71789 | -0.88842 | -1.0589 | -1.2232 | -1.9726 | -2.6305 | -3.2147
|  | BEACONSFIELD (END BUSBARS) PRIMARY | EE |  |  |  |  | 6.2484 | 6.1653 | 6.0758 | 5.9832 | 0.88737 | 0.79579 | 0.70947 | 0.62737 | 0.55368 | 0.066316 | -0.34421 | -0.69579 | 5.0737 | 4.9253 | 4.7747 | 4.6221 | -0.52947 | -0.67368 | -0.81684 | -0.95895 | -1.0958 | -1.6684 | -2.1453 | -2.5611 | 5.3358 | 5.2074 | 5.0589 | 4.9095 | -0.23895 | -0.38211 | -0.52211 | -0.66105 | -0.79579 | -1.3674 | -1.8453 | -2.2621
|  | BEACONSFIELD (END BUSBARS) PRIMARY | HT |  |  |  |  | 6.1811 | 6.0758 | 5.9653 | 5.8505 | 0.73368 | 0.61579 | 0.49474 | 0.33684 | 0.18842 | -0.47053 | -1.0389 | -1.5484 | 4.94 | 4.7463 | 4.5547 | 4.3632 | -0.82526 | -1.0168 | -1.1905 | -1.3642 | -1.5274 | -2.2716 | -2.9316 | -3.5158 | 5.2221 | 5.0316 | 4.8432 | 4.6558 | -0.52947 | -0.71789 | -0.88842 | -1.0589 | -1.2232 | -1.9726 | -2.6305 | -3.2147
|  | BEACONSFIELD (END BUSBARS) PRIMARY | HE |  |  |  |  | 6.3337 | 6.2758 | 6.2126 | 6.1442 | 1.0716 | 1.0021 | 0.93684 | 0.87579 | 0.82316 | 0.64737 | 0.49263 | -7.8842 | 5.2411 | 5.1495 | 5.0547 | 4.9558 | -0.14632 | -0.24526 | -0.34526 | -0.44421 | -0.53895 | -0.91368 | -1.2011 | -1.4389 | 5.4211 | 5.3632 | 5.3 | 5.2316 | 0.13474 | 0.036842 | -0.062105 | -0.15895 | -0.25263 | -0.61789 | -0.89684 | -1.1368
|  | BEACONSFIELD (END BUSBARS) PRIMARY | CF |  |  |  |  | 6.3905 | 6.3621 | 6.3316 | 6.3011 | 1.2695 | 1.2368 | 1.2042 | 1.1726 | 1.1411 | 0.99895 | 0.92947 | 0.85579 | 5.3011 | 5.2705 | 5.2295 | 5.1758 | 0.12105 | 0.065263 | 0.0073684 | -0.053684 | -0.11684 | -0.42632 | -0.65158 | -0.83368 | 5.4779 | 5.4495 | 5.4189 | 5.3884 | 0.35684 | 0.32421 | 0.28842 | 0.22737 | 0.16632 | -0.13579 | -0.35474 | -0.53053
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BEENHAM PRIMARY | MINIMUM HEADROOM | SU 58204 69025 | NO | YES | 0 | 11.7526 | 11.6642 | 11.5695 | 11.4726 | 11.3726 | 11.2716 | 11.1821 | 11.1021 | 11.0274 | 10.5937 | 9.8547 | -0.44 | 10.0663 | 9.9095 | 9.1716 | 9.0916 | 9.0084 | 8.9274 | 8.8526 | 8.7768 | 8.7032 | 7.9989 | 7.1316 | 6.6579 | 10.4484 | 10.3547 | 9.6747 | 9.5947 | 9.5105 | 9.4305 | 9.3547 | 9.2779 | 9.2032 | 8.4979 | 7.6295 | 7.1516
|  | BEENHAM PRIMARY | EE |  |  |  |  | 11.8084 | 11.7358 | 11.66 | 11.58 | 11.4968 | 11.4158 | 11.3411 | 11.2674 | 11.2032 | 10.6463 | 9.9453 | 9.4905 | 10.1768 | 10.0505 | 9.1716 | 9.0916 | 9.0084 | 8.9274 | 8.8526 | 8.78 | 8.7158 | 8.0021 | 7.1832 | 6.6579 | 10.5084 | 10.4316 | 9.6747 | 9.5947 | 9.5105 | 9.4305 | 9.3547 | 9.2811 | 9.2158 | 8.4989 | 7.6768 | 7.1516
|  | BEENHAM PRIMARY | HT |  |  |  |  | 11.7526 | 11.6642 | 11.5695 | 11.4726 | 11.3726 | 11.2716 | 11.1821 | 11.1021 | 11.0274 | 10.5937 | 9.8547 | 9.5916 | 10.0663 | 9.9095 | 9.7474 | 9.5863 | 9.4316 | 9.2253 | 8.8579 | 8.7768 | 8.7032 | 7.9989 | 7.1316 | 6.8505 | 10.4484 | 10.3547 | 10.2316 | 10.0768 | 9.9179 | 9.7168 | 9.3589 | 9.2779 | 9.2032 | 8.4979 | 7.6295 | 7.3463
|  | BEENHAM PRIMARY | HE |  |  |  |  | 11.8789 | 11.8295 | 11.7747 | 11.7158 | 11.6516 | 11.5905 | 11.5326 | 11.4789 | 11.4326 | 11.2737 | 11.1821 | -0.44 | 10.3189 | 10.2379 | 10.1526 | 10.0632 | 9.9747 | 9.8905 | 9.8053 | 9.7316 | 9.6663 | 9.4168 | 8.9958 | 8.5853 | 10.5842 | 10.5316 | 10.4747 | 10.4137 | 10.3474 | 10.2853 | 10.2253 | 10.1695 | 10.1232 | 9.9074 | 9.4937 | 9.0842
|  | BEENHAM PRIMARY | CF |  |  |  |  | 11.9274 | 11.9021 | 11.8758 | 11.8484 | 11.8189 | 11.7905 | 11.7621 | 11.7337 | 11.7053 | 11.5768 | 11.5126 | 11.4768 | 10.3716 | 10.3432 | 10.3032 | 10.2537 | 10.2042 | 10.1558 | 10.1084 | 10.06 | 10.0126 | 9.7916 | 9.6158 | 9.4126 | 10.6347 | 10.6074 | 10.58 | 10.5505 | 10.52 | 10.4895 | 10.46 | 10.4305 | 10.4 | 10.2632 | 10.1053 | 9.9032
MANNINGTON GSP | SALISBURY BSP | BEMERTON PRIMARY | MINIMUM HEADROOM | SU 11583 31233 | NO | YES | 0 | 33.1547 | 32.9274 | 32.6526 | 31.6937 | 31.3389 | 30.4726 | 29.7463 | 29.4389 | 29.1579 | 30.0137 | 27.8832 | 6.9726 | 30.1474 | 29.7305 | 29.2495 | 28.2589 | 27.8505 | 26.8916 | 26.0926 | 25.7705 | 25.4768 | 26.9337 | 24.5547 | 22.1684 | 30.9074 | 30.6789 | 30.2958 | 29.2695 | 28.8505 | 27.8653 | 27.0442 | 26.7147 | 26.4137 | 27.4021 | 25 | 22.6042
|  | BEMERTON PRIMARY | EE |  |  |  |  | 33.2768 | 33.0947 | 32.8905 | 32.1621 | 31.3389 | 30.4726 | 29.7463 | 29.4389 | 29.1579 | 31.2726 | 29.56 | 27.8895 | 30.3958 | 30.0558 | 29.6537 | 28.7453 | 27.8505 | 26.8916 | 26.0926 | 25.7705 | 25.4768 | 28.3263 | 26.4484 | 24.5505 | 31.0347 | 30.8463 | 30.6432 | 29.7589 | 28.8505 | 27.8653 | 27.0442 | 26.7147 | 26.4137 | 28.8011 | 26.8716 | 24.9611
|  | BEMERTON PRIMARY | HT |  |  |  |  | 33.1547 | 32.9274 | 32.6526 | 31.6937 | 34.4568 | 33.5137 | 32.7368 | 32.3958 | 32.0305 | 30.0137 | 27.8832 | 25.7811 | 30.1474 | 29.7305 | 29.2495 | 28.2589 | 31.7642 | 30.7221 | 29.8674 | 29.5084 | 29.12 | 26.9337 | 24.5547 | 22.1684 | 30.9074 | 30.6789 | 30.2958 | 29.2695 | 32.3453 | 31.2768 | 30.4021 | 30.0358 | 29.6368 | 27.4021 | 25 | 22.6042
|  | BEMERTON PRIMARY | HE |  |  |  |  | 33.4347 | 33.3074 | 33.1663 | 32.7811 | 32.0442 | 31.2684 | 30.6326 | 30.4253 | 30.2368 | 32.8284 | 31.5968 | 6.9726 | 30.7284 | 30.4916 | 30.1874 | 29.3716 | 28.6063 | 27.7453 | 27.04 | 26.8232 | 26.6274 | 29.9737 | 28.6084 | 27.1358 | 31.2053 | 31.0695 | 30.9179 | 30.4084 | 29.6179 | 28.7358 | 28.0116 | 27.7926 | 27.5926 | 30.4989 | 29.0916 | 27.6011
|  | BEMERTON PRIMARY | CF |  |  |  |  | 33.5474 | 33.4789 | 33.4074 | 33.3232 | 33.2221 | 32.8916 | 32.5463 | 32.4137 | 32.28 | 31.6537 | 34.6147 | 33.7979 | 30.8684 | 30.7737 | 30.6147 | 30.2463 | 29.8905 | 29.4821 | 29.1284 | 28.9968 | 28.8611 | 28.2021 | 31.9295 | 31.0158 | 31.32 | 31.2495 | 31.1716 | 31.0758 | 30.9453 | 30.5147 | 30.1432 | 30.0063 | 29.8674 | 29.2074 | 32.5053 | 31.5611
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | BERINSFIELD PRIMARY | MINIMUM HEADROOM | SU 58382 95467 | NO | YES | 0.13158 | 23.1563 | 22.3489 | 21.0511 | 19.4089 | 16.8468 | 16.71 | 16.5805 | 14.79 | 12.1974 | 0.86684 | -5.0353 | -52.7426 | 21.7089 | 20.7784 | 19.2626 | 17.0184 | 14.1816 | 14.0447 | 13.9153 | 11.6763 | 8.5763 | -5.2121 | -12.0553 | -12.45 | 21.8647 | 20.9321 | 19.41 | 16.9416 | 14.3068 | 14.17 | 14.0405 | 11.79 | 8.6774 | -5.1689 | -12.0763 | -12.4711
|  | BERINSFIELD PRIMARY | EE |  |  |  |  | 23.39 | 22.6553 | 21.4258 | 19.4089 | 19.2237 | 19.0447 | 18.8774 | 18.7163 | 18.5721 | 18.7542 | 15.8953 | 15.0511 | 21.9647 | 21.1153 | 19.6742 | 17.2889 | 17.1037 | 16.9247 | 16.7574 | 16.5963 | 16.4521 | 16.1511 | 12.8468 | 11.8974 | 22.1216 | 21.2689 | 19.8226 | 17.4289 | 17.2437 | 17.0647 | 16.8974 | 16.7363 | 16.5921 | 16.0742 | 12.7763 | 11.8279
|  | BERINSFIELD PRIMARY | HT |  |  |  |  | 23.1563 | 22.3489 | 21.0511 | 19.6605 | 19.4384 | 19.2142 | 19.0184 | 18.8395 | 18.6774 | 18.0195 | 14.9037 | 13.71 | 21.7089 | 20.7784 | 19.2626 | 17.0184 | 16.7963 | 16.5721 | 16.3763 | 16.1974 | 16.0353 | 15.3774 | 11.7974 | 10.4595 | 21.8647 | 20.9321 | 19.41 | 16.9416 | 16.7195 | 16.4953 | 16.2995 | 16.1205 | 15.9584 | 15.3005 | 11.7268 | 10.3911
|  | BERINSFIELD PRIMARY | HE |  |  |  |  | 23.7047 | 23.0647 | 21.9311 | 20.0016 | 16.8468 | 16.71 | 16.5805 | 16.4605 | 16.3574 | 16.6374 | 14.0342 | -52.7426 | 22.31 | 21.5658 | 20.2289 | 17.9395 | 14.1816 | 14.0447 | 13.9153 | 13.7953 | 13.6921 | 13.5405 | 10.5121 | 9.9079 | 22.4679 | 21.7205 | 20.3784 | 18.0805 | 14.3068 | 14.17 | 14.0405 | 13.9205 | 13.8174 | 13.47 | 10.4468 | 9.8437
|  | BERINSFIELD PRIMARY | CF |  |  |  |  | 24.1405 | 23.8237 | 23.3068 | 22.4837 | 21.1995 | 19.4005 | 17.1932 | 14.79 | 12.1974 | 0.86684 | -5.0353 | -5.3837 | 22.8121 | 22.4437 | 21.8342 | 20.8595 | 19.33 | 17.1837 | 14.5479 | 11.6763 | 8.5763 | -5.2121 | -12.0553 | -12.45 | 22.9721 | 22.6016 | 21.99 | 21.0111 | 19.4763 | 17.3205 | 14.6732 | 11.79 | 8.6774 | -5.1689 | -12.0763 | -12.4711
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | BEVOIS VALLEY PRIMARY | MINIMUM HEADROOM | SU 42648 13187 | NO | YES | 0 | 28.1677 | 28.0235 | 27.8698 | 27.4277 | 27.1498 | 26.875 | 26.6245 | 26.3824 | 26.1171 | 24.5803 | 23.2561 | -0.95549 | 22.8445 | 22.5708 | 22.2498 | 21.4782 | 21.1792 | 20.8835 | 20.6129 | 20.3508 | 20.0592 | 18.3245 | 16.8235 | 15.415 | 24.0045 | 23.7403 | 23.4308 | 22.6708 | 22.3708 | 22.075 | 21.8056 | 21.5424 | 21.2508 | 19.5161 | 18.014 | 16.6056
|  | BEVOIS VALLEY PRIMARY | EE |  |  |  |  | 28.2624 | 28.1466 | 28.0235 | 27.7887 | 27.515 | 27.234 | 27.0161 | 26.8087 | 26.6171 | 25.515 | 24.495 | 23.5656 | 23.0361 | 22.8235 | 22.5729 | 21.8761 | 21.574 | 21.2645 | 21.0298 | 20.8045 | 20.5992 | 19.3645 | 18.2035 | 17.1361 | 24.1908 | 23.9835 | 23.7424 | 23.0677 | 22.7656 | 22.4561 | 22.2213 | 21.9971 | 21.7908 | 20.5561 | 19.394 | 18.3266
|  | BEVOIS VALLEY PRIMARY | HT |  |  |  |  | 28.1677 | 28.0235 | 27.8698 | 27.4277 | 27.1498 | 26.875 | 26.6245 | 26.3824 | 26.1171 | 24.5803 | 23.2561 | 22.0235 | 22.8445 | 22.5708 | 22.2498 | 21.4782 | 21.1792 | 20.8835 | 20.6129 | 20.3508 | 20.0592 | 18.3245 | 16.8235 | 15.415 | 24.0045 | 23.7403 | 23.4308 | 22.6708 | 22.3708 | 22.075 | 21.8056 | 21.5424 | 21.2508 | 19.5161 | 18.014 | 16.6056
|  | BEVOIS VALLEY PRIMARY | HE |  |  |  |  | 28.3308 | 28.2319 | 28.1235 | 27.994 | 27.8561 | 27.6561 | 27.495 | 27.3435 | 27.2119 | 26.5203 | 25.8466 | -0.95549 | 23.2329 | 23.0792 | 22.8877 | 22.2466 | 21.9971 | 21.7424 | 21.5719 | 21.4098 | 21.2708 | 20.5035 | 19.7329 | 19.0287 | 24.3824 | 24.2308 | 24.0424 | 23.4382 | 23.1887 | 22.934 | 22.7635 | 22.6024 | 22.4624 | 21.695 | 20.9245 | 20.2192
|  | BEVOIS VALLEY PRIMARY | CF |  |  |  |  | 28.3898 | 28.3266 | 28.2613 | 28.194 | 28.1235 | 28.0519 | 27.9824 | 27.9129 | 27.8403 | 27.4708 | 26.9961 | 26.5645 | 23.5329 | 23.4698 | 23.4045 | 23.214 | 22.8687 | 22.5813 | 22.4098 | 22.2898 | 22.1687 | 21.5656 | 21.0256 | 20.5245 | 24.6719 | 24.6087 | 24.5435 | 24.3582 | 24.0245 | 23.7529 | 23.5877 | 23.4719 | 23.355 | 22.7571 | 22.2182 | 21.7161
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER PRIMARY | MINIMUM HEADROOM | SP 58381 21988 | NO | YES | 1.0568 | 64.8476 | 64.4518 | 64.0055 | 63.5349 | 62.6465 | 60.7802 | 58.9665 | 57.4413 | 55.9465 | 48.796 | 42.5992 | 11.3023 | 59.6265 | 58.4486 | 56.8381 | 55.0286 | 53.0265 | 50.8686 | 48.7528 | 46.976 | 45.2339 | 36.8549 | 29.5665 | 23.6181 | 60.7655 | 59.6876 | 58.056 | 56.2213 | 54.1897 | 52.0192 | 49.9023 | 48.1276 | 46.3834 | 38.0013 | 30.7086 | 24.7571
|  | BICESTER PRIMARY | EE |  |  |  |  | 65.0444 | 64.7171 | 66.596 | 65.1202 | 63.4749 | 61.7255 | 59.996 | 58.536 | 57.1118 | 50.8728 | 45.2602 | 41.0581 | 60.036 | 58.9981 | 57.5813 | 55.8676 | 53.9507 | 51.9076 | 49.8844 | 48.1834 | 46.5192 | 38.6486 | 32.1455 | 27.2707 | 60.9665 | 60.2434 | 58.7349 | 57.0213 | 55.1034 | 53.0581 | 51.0349 | 49.3339 | 47.6686 | 39.7939 | 33.2855 | 28.4086
|  | BICESTER PRIMARY | HT |  |  |  |  | 64.8476 | 64.4518 | 64.0055 | 63.5349 | 62.6465 | 60.7802 | 58.9665 | 57.4413 | 55.9465 | 48.796 | 42.5992 | 37.5444 | 59.6265 | 58.4486 | 56.8381 | 55.0286 | 53.0265 | 50.8686 | 48.7528 | 46.976 | 45.2339 | 36.8549 | 29.5665 | 23.6181 | 60.7655 | 59.6876 | 58.056 | 56.2213 | 54.1897 | 52.0192 | 49.9023 | 48.1276 | 46.3834 | 38.0013 | 30.7086 | 24.7571
|  | BICESTER PRIMARY | HE |  |  |  |  | 65.3023 | 65.0823 | 64.7823 | 64.4507 | 64.0897 | 62.9844 | 61.3876 | 60.0634 | 58.7718 | 52.7276 | 47.8265 | 11.3023 | 60.3297 | 59.7476 | 58.4318 | 56.9013 | 55.1602 | 53.2928 | 51.4202 | 49.8686 | 48.3518 | 41.196 | 35.3655 | 31.1328 | 61.2434 | 60.9992 | 59.6644 | 58.1118 | 56.3444 | 54.4486 | 52.5718 | 51.0192 | 49.5013 | 42.3434 | 36.5107 | 32.276
|  | BICESTER PRIMARY | CF |  |  |  |  | 65.4781 | 65.3686 | 65.2549 | 65.1307 | 64.9739 | 64.7928 | 64.5981 | 64.4044 | 64.2192 | 59.9181 | 56.3592 | 54.2497 | 60.5213 | 60.3992 | 60.2718 | 59.9381 | 59.3244 | 58.4286 | 57.2802 | 56.1413 | 55.0949 | 49.6339 | 45.3981 | 42.8876 | 61.4349 | 61.3128 | 61.1844 | 61.0476 | 60.5707 | 59.6613 | 58.4939 | 57.3381 | 56.276 | 50.7834 | 46.5486 | 44.036
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH PRIMARY | MINIMUM HEADROOM | SP 59720 23735 | NO | YES | 0 | 34.4821 | 34.2421 | 33.9884 | 33.7253 | 33.4526 | 33.18 | 32.9389 | 32.72 | 32.5168 | 31.6916 | 31.0674 | 6.0189 | 34.1137 | 33.8505 | 33.5758 | 33.2716 | 32.8242 | 32.38 | 31.9747 | 31.5958 | 31.24 | 29.6389 | 28.2653 | 27.0505 | 30.28 | 30.04 | 29.7863 | 29.5232 | 29.2516 | 28.9779 | 28.7368 | 28.5179 | 28.3158 | 27.4905 | 26.8674 | 26.3789
|  | BICESTER NORTH PRIMARY | EE |  |  |  |  | 34.6126 | 34.4126 | 36.3168 | 36.0789 | 35.8211 | 35.5716 | 35.2926 | 34.98 | 34.6958 | 33.5158 | 32.5684 | 31.7726 | 34.26 | 34.0432 | 33.8126 | 33.5726 | 33.3126 | 33.0579 | 32.7684 | 32.44 | 32.14 | 30.8832 | 29.8621 | 28.9926 | 30.4105 | 30.2105 | 34.4947 | 34.2537 | 33.9916 | 33.7379 | 33.4463 | 33.1158 | 32.8147 | 31.5463 | 30.5147 | 29.6379
|  | BICESTER NORTH PRIMARY | HT |  |  |  |  | 34.4821 | 34.2421 | 33.9884 | 33.7253 | 33.4526 | 33.18 | 32.9389 | 32.72 | 32.5168 | 31.6916 | 31.0674 | 29.9821 | 34.1137 | 33.8505 | 33.5758 | 33.2716 | 32.8242 | 32.38 | 31.9747 | 31.5958 | 31.24 | 29.6389 | 28.2653 | 27.0505 | 30.28 | 30.04 | 29.7863 | 29.5232 | 29.2516 | 28.9779 | 28.7368 | 28.5179 | 28.3158 | 27.4905 | 26.8674 | 26.3789
|  | BICESTER NORTH PRIMARY | HE |  |  |  |  | 34.7989 | 34.6558 | 34.4968 | 34.3263 | 34.1432 | 33.9684 | 33.8042 | 33.6484 | 33.5158 | 33.0642 | 32.8011 | 6.0189 | 34.4621 | 34.3158 | 34.1474 | 33.9663 | 33.7621 | 33.5642 | 33.3789 | 33.2053 | 33.0558 | 32.5695 | 32.1653 | 31.7474 | 30.5968 | 30.4537 | 30.2947 | 30.1242 | 29.9411 | 29.7674 | 29.6021 | 29.4463 | 29.3147 | 28.8632 | 28.6 | 28.4368
|  | BICESTER NORTH PRIMARY | CF |  |  |  |  | 34.9274 | 34.8505 | 34.7705 | 34.6884 | 34.6011 | 34.5137 | 34.4274 | 34.3421 | 34.2568 | 33.8768 | 33.6853 | 33.5789 | 34.5905 | 34.5137 | 34.4337 | 34.3463 | 34.2526 | 34.1537 | 34.0568 | 33.96 | 33.8632 | 33.4358 | 33.2126 | 32.8737 | 30.7253 | 30.6484 | 30.5684 | 30.4863 | 30.3989 | 30.3116 | 30.2263 | 30.1411 | 30.0547 | 29.6747 | 29.4832 | 29.3768
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BILLINGSHURST PRIMARY | MINIMUM HEADROOM | TQ 08305 26315 | YES | YES | 0 | 12.8232 | 12.5621 | 12.2705 | 11.96 | 11.66 | 11.3411 | 10.9863 | 10.6495 | 10.3253 | 7.8968 | 5.6295 | -2.1547 | 11.6274 | 11.2053 | 10.7232 | 10.1937 | 9.6947 | 9.1463 | 8.4663 | 7.8053 | 7.16 | 4.2621 | 1.6653 | -0.76105 | 12.1453 | 11.7347 | 11.2463 | 10.7126 | 10.2147 | 9.6663 | 8.9874 | 8.3274 | 7.6832 | 4.7895 | 2.1968 | -0.22632
|  | BILLINGSHURST PRIMARY | EE |  |  |  |  | 12.9674 | 12.7505 | 12.5032 | 12.2663 | 12.0379 | 11.7916 | 11.4863 | 11.1947 | 10.9168 | 9.3032 | 7.4547 | 5.7537 | 11.8484 | 11.4958 | 11.0811 | 10.6989 | 10.3474 | 9.9337 | 9.3505 | 8.7905 | 8.2442 | 5.8484 | 3.72 | 1.7558 | 12.3611 | 12.0179 | 11.6116 | 11.2221 | 10.8663 | 10.4526 | 9.8705 | 9.3116 | 8.7653 | 6.3737 | 4.2484 | 2.2884
|  | BILLINGSHURST PRIMARY | HT |  |  |  |  | 12.8232 | 12.5621 | 12.2705 | 11.96 | 11.66 | 11.3411 | 10.9863 | 10.6495 | 10.3253 | 7.8968 | 5.6295 | 3.5189 | 11.6274 | 11.2053 | 10.7232 | 10.1937 | 9.6947 | 9.1463 | 8.4663 | 7.8053 | 7.16 | 4.2621 | 1.6653 | -0.76105 | 12.1453 | 11.7347 | 11.2463 | 10.7126 | 10.2147 | 9.6663 | 8.9874 | 8.3274 | 7.6832 | 4.7895 | 2.1968 | -0.22632
|  | BILLINGSHURST PRIMARY | HE |  |  |  |  | 13.1526 | 12.9895 | 12.7989 | 12.6126 | 12.4316 | 12.2316 | 11.9737 | 11.7284 | 11.4968 | 10.4116 | 8.8453 | -2.1547 | 12.1253 | 11.8537 | 11.5253 | 11.22 | 10.9379 | 10.6 | 10.0905 | 9.5989 | 9.1211 | 7.0589 | 5.2389 | 3.5684 | 12.5926 | 12.3674 | 12.0484 | 11.7516 | 11.4642 | 11.12 | 10.6095 | 10.1189 | 9.6421 | 7.5832 | 5.7663 | 4.0979
|  | BILLINGSHURST PRIMARY | CF |  |  |  |  | 13.2789 | 13.1926 | 13.0916 | 13 | 12.9158 | 12.82 | 12.6926 | 12.5674 | 12.4379 | 11.8221 | 11.3358 | 10.8242 | 12.3179 | 12.1716 | 11.9937 | 11.84 | 11.7084 | 11.5495 | 11.3095 | 11.0705 | 10.8211 | 9.5811 | 8.4779 | 7.4832 | 12.6779 | 12.6284 | 12.5042 | 12.3558 | 12.2274 | 12.0726 | 11.84 | 11.5979 | 11.3411 | 10.1011 | 9 | 8.0063
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BILSHAM PRIMARY | MINIMUM HEADROOM | SU 97366 01594 | NO | YES | 4.2526 | 23.0116 | 21.0189 | 18.44 | 45.6347 | 45.2684 | 44.8989 | 41.8916 | 39.6495 | 37.4337 | 33.0653 | 29.6463 | 8.3179 | 21.2442 | 18.8042 | 15.9421 | 42.6947 | 42.3305 | 41.9642 | 38.4695 | 35.8747 | 33.3084 | 28.3642 | 24.4926 | 20.5632 | 21.4874 | 19.0147 | 16.1621 | 42.9147 | 42.5474 | 42.1779 | 38.6863 | 36.0926 | 33.5295 | 28.5747 | 24.6895 | 20.7516
|  | BILSHAM PRIMARY | EE |  |  |  |  | 23.0116 | 21.0895 | 18.62 | 45.9158 | 45.6042 | 45.2989 | 42.5705 | 40.3463 | 38.1211 | 34.14 | 31.4989 | 28.7274 | 21.2442 | 18.8042 | 15.9421 | 42.8032 | 42.4947 | 42.1958 | 39.0263 | 36.4537 | 33.8726 | 29.3684 | 26.4032 | 23.2337 | 23.6621 | 19.0147 | 16.2474 | 42.9642 | 42.6516 | 42.3463 | 39.1768 | 36.6011 | 34.0189 | 29.4842 | 26.4853 | 23.2947
|  | BILSHAM PRIMARY | HT |  |  |  |  | 23.0526 | 21.0189 | 18.44 | 45.6347 | 45.2684 | 44.8989 | 41.8916 | 39.6495 | 37.4337 | 33.0653 | 29.6463 | 26.2095 | 21.2779 | 18.9337 | 15.9474 | 42.6947 | 42.3305 | 41.9642 | 38.4695 | 35.8747 | 33.3084 | 28.3642 | 24.4926 | 20.5632 | 21.4874 | 19.1442 | 16.1621 | 42.9147 | 42.5474 | 42.1779 | 38.6863 | 36.0926 | 33.5295 | 28.5747 | 24.6895 | 20.7516
|  | BILSHAM PRIMARY | HE |  |  |  |  | 23.5379 | 21.7779 | 19.4663 | 46.9116 | 46.6716 | 46.4432 | 43.8021 | 41.6916 | 39.6137 | 36.2895 | 34.28 | 8.3179 | 21.9253 | 19.5411 | 16.8442 | 43.8653 | 43.6253 | 43.3989 | 40.3147 | 37.8568 | 35.4326 | 31.6168 | 29.3105 | 26.7484 | 24.0453 | 19.7537 | 17.1537 | 44.0526 | 43.8126 | 43.5842 | 40.5063 | 38.0516 | 35.6305 | 31.8158 | 29.5074 | 26.9463
|  | BILSHAM PRIMARY | CF |  |  |  |  | 24.7726 | 23.8 | 22.7432 | 51.6274 | 50.3505 | 48.9495 | 47.8568 | 46.9853 | 46.0253 | 42.4737 | 41.4042 | 40.0463 | 23.2295 | 22.2 | 20.6537 | 49.3537 | 47.8653 | 46.2295 | 44.9579 | 43.9495 | 42.8337 | 38.7253 | 37.5105 | 35.9326 | 24.6442 | 24.1937 | 20.8295 | 49.5758 | 48.14 | 46.5632 | 45.3347 | 44.1347 | 43.0211 | 38.9179 | 37.7032 | 36.1253
FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD PRIMARY | MINIMUM HEADROOM | SZ 56409 91399 | NO | YES | 0 | 16.1621 | 15.8484 | 15.5337 | 15.2021 | 14.8137 | 14.4095 | 14.0168 | 13.6368 | 13.2537 | 10.9832 | 9.5453 | -0.28526 | 14.6074 | 14.2716 | 13.9347 | 13.58 | 13.1695 | 12.7442 | 12.3274 | 11.9242 | 11.5158 | 9.0621 | 7.5758 | 5.9937 | 14.7653 | 14.4274 | 14.0916 | 13.7358 | 13.3179 | 12.8842 | 12.46 | 12.0474 | 11.6295 | 9.1116 | 7.5505 | 5.9389
|  | BINSTEAD PRIMARY | EE |  |  |  |  | 16.3053 | 16.0611 | 15.8589 | 15.5874 | 15.2842 | 14.9547 | 14.6284 | 14.3263 | 14.0168 | 12.4084 | 10.8137 | 9.6579 | 14.8 | 14.54 | 14.2863 | 13.9968 | 13.6821 | 13.34 | 13.0011 | 12.6926 | 12.3737 | 10.72 | 9.0789 | 7.8137 | 14.9947 | 14.7305 | 14.4432 | 14.1526 | 13.8305 | 13.4779 | 13.1284 | 12.8074 | 12.4758 | 10.7316 | 8.9863 | 7.6895
|  | BINSTEAD PRIMARY | HT |  |  |  |  | 16.1621 | 15.8484 | 15.5337 | 15.2021 | 14.8137 | 14.4095 | 14.0168 | 13.6368 | 13.2537 | 10.9832 | 9.5453 | 8.1063 | 14.6074 | 14.2716 | 13.9347 | 13.58 | 13.1695 | 12.7442 | 12.3274 | 11.9242 | 11.5158 | 9.0621 | 7.5758 | 5.9937 | 14.7653 | 14.4274 | 14.0916 | 13.7358 | 13.3179 | 12.8842 | 12.46 | 12.0474 | 11.6295 | 9.1116 | 7.5505 | 5.9389
|  | BINSTEAD PRIMARY | HE |  |  |  |  | 16.5842 | 16.4284 | 16.32 | 16.1305 | 15.9042 | 15.6726 | 15.4453 | 15.24 | 15.02 | 13.9526 | 12.9642 | -0.28526 | 15.1021 | 14.9368 | 14.7863 | 14.5842 | 14.3495 | 14.1074 | 13.8695 | 13.6568 | 13.4253 | 12.2884 | 11.2084 | 10.2663 | 15.3021 | 15.1347 | 14.9442 | 14.7421 | 14.5021 | 14.2547 | 14.0105 | 13.7937 | 13.5558 | 12.38 | 11.2716 | 10.3032
|  | BINSTEAD PRIMARY | CF |  |  |  |  | 16.6821 | 16.6326 | 16.5453 | 16.4263 | 16.2853 | 16.1379 | 15.9979 | 15.9284 | 15.7989 | 15.2926 | 14.6684 | 14.1242 | 15.26 | 15.1737 | 15.0568 | 14.9274 | 14.7758 | 14.6189 | 14.4663 | 14.3558 | 14.2179 | 13.6884 | 13.0042 | 12.4063 | 15.4147 | 15.3632 | 15.2558 | 15.1232 | 14.9663 | 14.8032 | 14.6484 | 14.5042 | 14.3642 | 13.8211 | 13.1221 | 12.5063
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BIRDHAM PRIMARY | MINIMUM HEADROOM | SZ 81965 99422 | NO | YES | 0 | 14.0411 | 13.7768 | 13.1105 | 32.48 | 31.7432 | 31.0516 | 30.42 | 29.8653 | 29.3979 | 27.3095 | 25.08 | 9.0853 | 9.7905 | 9.2063 | 8.4811 | 27.8011 | 26.9989 | 26.2358 | 25.5389 | 24.9263 | 24.4147 | 22.1063 | 19.5916 | 17.2916 | 10.2189 | 9.6474 | 8.9421 | 28.2779 | 27.4621 | 26.6979 | 26.0011 | 25.3884 | 24.8758 | 22.5674 | 20.0526 | 17.7516
|  | BIRDHAM PRIMARY | EE |  |  |  |  | 14.2074 | 13.9937 | 13.6453 | 33.1326 | 32.5137 | 31.9379 | 31.3811 | 30.9116 | 30.5337 | 28.9537 | 27.2084 | 25.6389 | 10.1337 | 9.6526 | 9.0537 | 28.5011 | 27.8284 | 27.2042 | 26.5863 | 26.0705 | 25.6589 | 23.9158 | 21.9379 | 20.1453 | 10.5537 | 10.0842 | 9.5011 | 28.9632 | 28.3032 | 27.6663 | 27.0484 | 26.5326 | 26.1211 | 24.3779 | 22.3989 | 20.6063
|  | BIRDHAM PRIMARY | HT |  |  |  |  | 14.0411 | 13.7768 | 13.1105 | 32.48 | 31.7432 | 31.0516 | 30.42 | 29.8653 | 29.3979 | 27.3095 | 25.08 | 23.0537 | 9.7905 | 9.2063 | 8.4811 | 27.8011 | 26.9989 | 26.2358 | 25.5389 | 24.9263 | 24.4147 | 22.1063 | 19.5916 | 17.2916 | 10.2189 | 9.6474 | 8.9421 | 28.2779 | 27.4621 | 26.6979 | 26.0011 | 25.3884 | 24.8758 | 22.5674 | 20.0526 | 17.7516
|  | BIRDHAM PRIMARY | HE |  |  |  |  | 14.4179 | 14.2695 | 14.1063 | 33.9232 | 33.4126 | 32.9432 | 32.4884 | 32.1232 | 31.8453 | 30.7421 | 29.4305 | 9.0853 | 10.5832 | 10.2379 | 9.7726 | 29.3474 | 28.7905 | 28.28 | 27.7842 | 27.3884 | 27.0863 | 25.8663 | 24.3663 | 23.0232 | 10.9926 | 10.6558 | 10.2042 | 29.7895 | 29.2495 | 28.7526 | 28.2537 | 27.8505 | 27.5484 | 26.3284 | 24.8274 | 23.4842
|  | BIRDHAM PRIMARY | CF |  |  |  |  | 14.5611 | 14.4863 | 14.4074 | 34.3263 | 34.2421 | 34.1568 | 33.98 | 33.78 | 33.6158 | 32.8284 | 31.9611 | 31.2179 | 10.8316 | 10.6442 | 10.4137 | 30.1958 | 29.9295 | 29.6653 | 29.3926 | 29.1758 | 29 | 28.1526 | 27.1758 | 26.3189 | 11.1421 | 11.0537 | 10.8295 | 30.6189 | 30.36 | 30.1042 | 29.8389 | 29.6284 | 29.4568 | 28.6295 | 27.6389 | 26.78
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM PRIMARY | MINIMUM HEADROOM | SU 56691 16683 | NO | YES | 0 | 23.9253 | 39.2074 | 38.3547 | 37.5568 | 36.8811 | 36.2168 | 35.5895 | 34.3768 | 34.0632 | 31.1589 | 27.0716 | 7.5137 | 22.3337 | 37.6074 | 37.0347 | 36.1674 | 35.4484 | 34.7442 | 34.0726 | 32.7063 | 32.3937 | 29.2053 | 24.5695 | 21.4168 | 22.1726 | 37.4242 | 37.2368 | 36.3716 | 35.6526 | 34.9463 | 34.2758 | 32.9105 | 32.5968 | 29.4095 | 24.7747 | 21.6221
|  | BISHOPS WALTHAM PRIMARY | EE |  |  |  |  | 24.3832 | 39.8032 | 39.0853 | 38.42 | 37.8705 | 37.3432 | 36.8484 | 36.3505 | 35.8147 | 33.2832 | 28.2937 | 24.5032 | 22.8716 | 38.2495 | 37.8263 | 37.1042 | 36.5211 | 35.9621 | 35.4368 | 34.9074 | 34.3263 | 31.5337 | 25.7905 | 21.4168 | 22.7463 | 38.1263 | 37.3526 | 36.6411 | 36.0632 | 35.5095 | 34.9895 | 34.4642 | 33.8916 | 31.14 | 25.9884 | 21.6221
|  | BISHOPS WALTHAM PRIMARY | HT |  |  |  |  | 23.9253 | 39.2074 | 38.3547 | 37.5568 | 36.8811 | 36.2168 | 35.5895 | 34.3768 | 34.0632 | 31.1589 | 27.0716 | 25.8116 | 22.3337 | 37.6074 | 37.0347 | 36.1674 | 35.4484 | 34.7442 | 34.0726 | 32.7063 | 32.3937 | 29.2053 | 24.5695 | 23.2179 | 22.1726 | 37.4242 | 37.2368 | 36.3716 | 35.6526 | 34.9463 | 34.2758 | 32.9105 | 32.5968 | 29.4095 | 24.7747 | 23.4221
|  | BISHOPS WALTHAM PRIMARY | HE |  |  |  |  | 24.9853 | 40.5916 | 40.0547 | 39.5589 | 39.1653 | 38.7958 | 38.4495 | 38.1042 | 37.7168 | 35.8937 | 30.5484 | 7.5137 | 23.52 | 39.0979 | 38.5147 | 37.9811 | 37.5695 | 37.1832 | 36.8221 | 36.4589 | 36.0442 | 34.0474 | 28.14 | 24.1347 | 23.3916 | 38.9716 | 38.3916 | 37.86 | 37.4495 | 37.0632 | 36.7032 | 36.34 | 35.9253 | 33.9358 | 27.8789 | 23.98
|  | BISHOPS WALTHAM PRIMARY | CF |  |  |  |  | 25.3211 | 41.0979 | 40.8189 | 40.5632 | 40.3484 | 40.1337 | 39.9242 | 39.7168 | 39.4653 | 38.1242 | 37.0705 | 36.1821 | 23.7453 | 39.5189 | 39.3305 | 39.0526 | 38.8242 | 38.5958 | 38.3726 | 38.1526 | 37.88 | 36.4189 | 35.2463 | 34.2463 | 23.6253 | 39.3916 | 39.2042 | 38.9274 | 38.7 | 38.4716 | 38.2495 | 38.0295 | 37.7589 | 36.3042 | 35.1368 | 34.1442
NURSLING GSP | VELMORE BSP | BISHOPSTOKE PRIMARY | MINIMUM HEADROOM | SU 46463 18472 | NO | YES | 0 | 15.6821 | 15.6653 | 15.6463 | 15.6263 | 15.6084 | 15.6 | 15.5895 | 15.5811 | 15.5737 | 15.54 | 15.4979 | 6.3516 | 15.4905 | 15.4705 | 15.4484 | 15.4253 | 15.4042 | 15.3937 | 15.3832 | 15.3726 | 15.3642 | 15.3263 | 15.2758 | 15.2284 | 15.3432 | 15.3232 | 15.3011 | 15.2779 | 15.2568 | 15.2474 | 15.2358 | 15.2263 | 15.2168 | 15.1789 | 15.1295 | 15.0811
|  | BISHOPSTOKE PRIMARY | EE |  |  |  |  | 15.6905 | 15.6737 | 15.6568 | 15.6411 | 15.6253 | 15.6168 | 15.6105 | 15.6032 | 15.5968 | 15.5747 | 15.5421 | 15.5116 | 15.5 | 15.4811 | 15.4611 | 15.4421 | 15.4232 | 15.4147 | 15.4074 | 15.3989 | 15.3916 | 15.3653 | 15.3274 | 15.2916 | 15.3526 | 15.3337 | 15.3137 | 15.2947 | 15.2768 | 15.2674 | 15.26 | 15.2516 | 15.2442 | 15.2179 | 15.1811 | 15.1453
|  | BISHOPSTOKE PRIMARY | HT |  |  |  |  | 15.6821 | 15.6653 | 15.6463 | 15.6263 | 15.6084 | 15.6 | 15.5895 | 15.5811 | 15.5737 | 15.54 | 15.4979 | 15.4568 | 15.4905 | 15.4705 | 15.4484 | 15.4253 | 15.4042 | 15.3937 | 15.3832 | 15.3726 | 15.3642 | 15.3263 | 15.2758 | 15.2284 | 15.3432 | 15.3232 | 15.3011 | 15.2779 | 15.2568 | 15.2474 | 15.2358 | 15.2263 | 15.2168 | 15.1789 | 15.1295 | 15.0811
|  | BISHOPSTOKE PRIMARY | HE |  |  |  |  | 15.6968 | 15.6874 | 15.6726 | 15.6589 | 15.6463 | 15.6421 | 15.6368 | 15.6326 | 15.6316 | 15.6211 | 15.6021 | 6.3516 | 15.5074 | 15.4968 | 15.48 | 15.4632 | 15.4484 | 15.4442 | 15.4379 | 15.4326 | 15.4316 | 15.42 | 15.3979 | 15.3789 | 15.36 | 15.3495 | 15.3326 | 15.3158 | 15.3011 | 15.2968 | 15.2916 | 15.2853 | 15.2842 | 15.2726 | 15.2516 | 15.2316
|  | BISHOPSTOKE PRIMARY | CF |  |  |  |  | 15.7105 | 15.7063 | 16.1074 | 16.1074 | 16.1063 | 16.1063 | 16.1053 | 16.1053 | 16.1042 | 16.1021 | 16.1011 | 16.1011 | 15.5232 | 15.5189 | 15.5242 | 15.5221 | 15.5179 | 15.5147 | 15.5105 | 15.5074 | 15.5032 | 15.4905 | 15.4811 | 15.4737 | 15.3726 | 15.3716 | 15.3779 | 15.3779 | 15.3758 | 15.3747 | 15.3726 | 15.3716 | 15.3695 | 15.3642 | 15.3611 | 15.3411
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE PRIMARY | MINIMUM HEADROOM | SU 45116 13082 | NO | YES | 0 | 12.6326 | 12.3442 | 12.0368 | 11.7211 | 11.3947 | 11.0663 | 10.7242 | 10.2863 | 9.8179 | 7.2884 | 5.2158 | -11.1379 | 9.9 | 9.3642 | 8.7558 | 8.1453 | 7.5926 | 7.0432 | 6.5516 | 6.0842 | 5.5779 | 2.7863 | 0.48842 | -1.58 | 10.5874 | 10.0632 | 9.4579 | 8.8389 | 8.2789 | 7.7221 | 7.2242 | 6.7505 | 6.2358 | 3.3874 | 1.04 | -1.0758
|  | BITTERNE PRIMARY | EE |  |  |  |  | 12.8021 | 12.5653 | 12.3126 | 12.0495 | 11.7768 | 11.5137 | 11.2642 | 11.0242 | 10.7695 | 8.9379 | 7.34 | 5.9368 | 10.2653 | 9.8389 | 9.3611 | 8.8789 | 8.3337 | 7.7884 | 7.3674 | 6.9621 | 6.5989 | 4.5905 | 2.8116 | 1.2368 | 10.9442 | 10.5274 | 10.0579 | 9.5842 | 9.0316 | 8.4768 | 8.0505 | 7.64 | 7.2726 | 5.2242 | 3.4063 | 1.7947
|  | BITTERNE PRIMARY | HT |  |  |  |  | 12.6326 | 12.3442 | 12.0368 | 11.7211 | 11.3947 | 11.0663 | 10.7242 | 10.2863 | 9.8179 | 7.2884 | 5.2158 | 3.3621 | 9.9 | 9.3642 | 8.7558 | 8.1453 | 7.5926 | 7.0432 | 6.5516 | 6.0842 | 5.5779 | 2.7863 | 0.48842 | -1.58 | 10.5874 | 10.0632 | 9.4579 | 8.8389 | 8.2789 | 7.7221 | 7.2242 | 6.7505 | 6.2358 | 3.3874 | 1.04 | -1.0758
|  | BITTERNE PRIMARY | HE |  |  |  |  | 13.0232 | 12.8547 | 12.6663 | 12.4653 | 12.2505 | 12.0432 | 11.8505 | 11.6684 | 11.5137 | 10.9863 | 9.9979 | -11.1379 | 10.6863 | 10.4737 | 10.1368 | 9.7916 | 9.3726 | 8.9484 | 8.6568 | 8.38 | 8.14 | 6.8979 | 5.72 | 4.6705 | 11.2558 | 11.0874 | 10.8158 | 10.4768 | 10.0674 | 9.6516 | 9.3621 | 9.0821 | 8.8389 | 7.5747 | 6.3695 | 5.2926
|  | BITTERNE PRIMARY | CF |  |  |  |  | 13.18 | 13.0895 | 12.9968 | 12.9011 | 12.8011 | 12.6989 | 12.6 | 12.5 | 12.4021 | 11.9611 | 11.7421 | 11.4042 | 10.8768 | 10.7621 | 10.6442 | 10.5021 | 10.3242 | 10.1421 | 9.9547 | 9.7737 | 9.5937 | 8.6989 | 7.9105 | 7.2042 | 11.4126 | 11.3221 | 11.2295 | 11.1337 | 11.0011 | 10.8232 | 10.6389 | 10.4611 | 10.2853 | 9.4021 | 8.5958 | 7.8705
MINETY GSP | STRATTON (RESERVE) BSP | BLACK BOURTON PRIMARY | MINIMUM HEADROOM | SP 28349 03818 | NO | YES | 0 | 11.5537 | 11.4316 | 11.2389 | 11.0547 | 10.6242 | 10.12 | 9.5105 | 9.4189 | 9.3347 | 8.26 | 6.8421 | -4.8632 | 9.9316 | 9.7474 | 9.5411 | 9.3442 | 8.8579 | 8.2853 | 7.5853 | 7.4937 | 7.4095 | 6.2042 | 4.5811 | 4.1505 | 10.0589 | 9.8642 | 9.6568 | 9.4611 | 8.9758 | 8.4032 | 7.7053 | 7.6137 | 7.5295 | 6.3253 | 4.7042 | 4.2747
|  | BLACK BOURTON PRIMARY | EE |  |  |  |  | 11.62 | 11.5316 | 11.4368 | 11.2895 | 11.14 | 10.9968 | 10.8537 | 10.7179 | 10.5926 | 10.0789 | 8.7274 | 7.8495 | 10.0558 | 9.9095 | 9.7568 | 9.5989 | 9.44 | 9.2874 | 9.1358 | 8.9895 | 8.8558 | 8.2979 | 6.7389 | 5.7295 | 10.1926 | 10.0368 | 9.8747 | 9.7158 | 9.5568 | 9.4042 | 9.2526 | 9.1063 | 8.9726 | 8.4158 | 6.86 | 5.8516
|  | BLACK BOURTON PRIMARY | HT |  |  |  |  | 11.5537 | 11.4316 | 11.2389 | 11.0547 | 10.6242 | 10.12 | 9.5105 | 9.4189 | 9.3347 | 8.26 | 6.8421 | 6.4474 | 9.9316 | 9.7474 | 9.5411 | 9.3442 | 8.8579 | 8.2853 | 7.5853 | 7.4937 | 7.4095 | 6.2042 | 4.5811 | 4.1505 | 10.0589 | 9.8642 | 9.6568 | 9.4611 | 8.9758 | 8.4032 | 7.7053 | 7.6137 | 7.5295 | 6.3253 | 4.7042 | 4.2747
|  | BLACK BOURTON PRIMARY | HE |  |  |  |  | 11.7105 | 11.6495 | 11.5821 | 11.5095 | 11.4337 | 11.36 | 11.2905 | 11.1958 | 11.1095 | 10.7842 | 9.7611 | -4.8632 | 10.2232 | 10.1284 | 10.0253 | 9.9211 | 9.8137 | 9.7105 | 9.6084 | 9.5095 | 9.4168 | 9.0653 | 7.88 | 7.0589 | 10.36 | 10.2695 | 10.1632 | 10.0537 | 9.9421 | 9.8337 | 9.7274 | 9.6253 | 9.5337 | 9.1821 | 7.9989 | 7.1789
|  | BLACK BOURTON PRIMARY | CF |  |  |  |  | 11.7705 | 11.7389 | 11.7053 | 11.6705 | 11.6358 | 11.6 | 11.5653 | 11.5305 | 11.4958 | 11.2495 | 10.8516 | 10.3263 | 10.3179 | 10.2632 | 10.2053 | 10.1432 | 10.0811 | 10.0147 | 9.9568 | 9.8989 | 9.8421 | 9.5516 | 9.0958 | 8.4853 | 10.4495 | 10.3979 | 10.3442 | 10.2853 | 10.2189 | 10.1484 | 10.0874 | 10.0253 | 9.9642 | 9.6684 | 9.2126 | 8.6032
MANNINGTON GSP | LYTCHETT BSP | BLANDFORD PRIMARY | MINIMUM HEADROOM | ST 88810 05536 | NO | YES | 0 | 44.3745 | 43.6019 | 42.8545 | 41.9366 | 41.5945 | 40.6903 | 39.9787 | 39.2924 | 38.6345 | 35.7451 | 33.1619 | 7.4387 | 38.0208 | 37.1682 | 36.3461 | 35.3272 | 35.0366 | 34.0503 | 33.2829 | 32.544 | 31.8345 | 28.7493 | 26.0008 | 23.3008 | 39.7324 | 38.8787 | 38.0566 | 37.0366 | 36.6545 | 35.6608 | 34.8851 | 34.1335 | 33.4135 | 30.2535 | 27.4177 | 24.6819
|  | BLANDFORD PRIMARY | EE |  |  |  |  | 44.7303 | 44.0619 | 43.4177 | 42.5987 | 41.6819 | 40.8735 | 40.2272 | 39.5903 | 38.9787 | 37.0587 | 34.9177 | 33.0419 | 38.4082 | 37.6682 | 36.9608 | 36.0493 | 35.0387 | 34.1566 | 33.4661 | 32.7872 | 32.1366 | 30.2408 | 28.0314 | 25.9651 | 40.1198 | 39.3787 | 38.6703 | 37.7577 | 36.7377 | 35.8451 | 35.1408 | 34.4482 | 33.7819 | 31.6998 | 29.3693 | 27.2651
|  | BLANDFORD PRIMARY | HT |  |  |  |  | 44.3745 | 43.6019 | 42.8545 | 41.9366 | 41.5945 | 40.6903 | 39.9787 | 39.2924 | 38.6345 | 35.7451 | 33.1619 | 30.7208 | 38.0208 | 37.1682 | 36.3461 | 35.3272 | 35.0366 | 34.0503 | 33.2829 | 32.544 | 31.8345 | 28.7493 | 26.0008 | 23.3008 | 39.7324 | 38.8787 | 38.0566 | 37.0366 | 36.6545 | 35.6608 | 34.8851 | 34.1335 | 33.4135 | 30.2535 | 27.4177 | 24.6819
|  | BLANDFORD PRIMARY | HE |  |  |  |  | 45.2072 | 44.6903 | 44.1882 | 43.5051 | 42.7229 | 42.0608 | 41.5629 | 41.0819 | 40.6303 | 39.5514 | 38.3198 | 7.4387 | 38.9282 | 38.3524 | 37.7977 | 37.0345 | 36.1661 | 35.4377 | 34.8998 | 34.3787 | 33.8893 | 32.8293 | 31.5008 | 30.0293 | 40.6398 | 40.064 | 39.5093 | 38.7451 | 37.8693 | 37.1356 | 36.5914 | 36.064 | 35.5672 | 34.384 | 33.0198 | 31.5177
|  | BLANDFORD PRIMARY | CF |  |  |  |  | 45.5008 | 45.2229 | 44.9619 | 44.6324 | 44.2661 | 43.9251 | 43.6419 | 43.3556 | 43.0629 | 41.7766 | 41.6093 | 40.7503 | 39.2451 | 38.9345 | 38.6461 | 38.2766 | 37.8714 | 37.4945 | 37.1872 | 36.8735 | 36.5524 | 35.1503 | 35.0619 | 34.1103 | 40.9556 | 40.6461 | 40.3577 | 39.9882 | 39.5798 | 39.1998 | 38.8893 | 38.5724 | 38.2493 | 36.8324 | 36.6451 | 35.6724
COWLEY GSP | WITNEY BSP | BLEDINGTON PRIMARY | MINIMUM HEADROOM | SP 25641 22580 | YES | YES | 0 | 7.34 | 7.2263 | 7.0758 | 6.9284 | 6.7811 | 6.6347 | 6.5032 | 6.38 | 6.2663 | 5.7295 | 5.1505 | 0.36211 | 7.9158 | 7.7621 | 7.5989 | 7.4389 | 7.28 | 7.1232 | 6.9811 | 6.8474 | 6.7242 | 6.1316 | 5.4737 | 4.7958 | 7.3158 | 7.2284 | 7.1347 | 7.0389 | 6.9411 | 6.8421 | 6.7558 | 6.6768 | 6.6063 | 6.1884 | 5.5347 | 4.8579
|  | BLEDINGTON PRIMARY | EE |  |  |  |  | 7.3989 | 7.3221 | 7.2347 | 7.1179 | 6.9989 | 6.8832 | 6.7726 | 6.6663 | 6.5684 | 6.1684 | 5.7411 | 5.28 | 8.0242 | 7.9011 | 7.7737 | 7.6484 | 7.5211 | 7.3958 | 7.2768 | 7.1632 | 7.0568 | 6.6179 | 6.1316 | 5.5947 | 7.3705 | 7.2979 | 7.2221 | 7.1432 | 7.0621 | 6.9853 | 6.9105 | 6.8389 | 6.7758 | 6.5442 | 6.1895 | 5.6558
|  | BLEDINGTON PRIMARY | HT |  |  |  |  | 7.34 | 7.2263 | 7.0758 | 6.9284 | 6.7811 | 6.6347 | 6.5032 | 6.38 | 6.2663 | 5.7295 | 5.1505 | 4.5621 | 7.9158 | 7.7621 | 7.5989 | 7.4389 | 7.28 | 7.1232 | 6.9811 | 6.8474 | 6.7242 | 6.1316 | 5.4737 | 4.7958 | 7.3158 | 7.2284 | 7.1347 | 7.0389 | 6.9411 | 6.8421 | 6.7558 | 6.6768 | 6.6063 | 6.1884 | 5.5347 | 4.8579
|  | BLEDINGTON PRIMARY | HE |  |  |  |  | 7.4779 | 7.4253 | 7.3695 | 7.3084 | 7.2442 | 7.1832 | 7.12 | 7.0463 | 6.98 | 6.7337 | 6.4421 | 0.36211 | 8.1695 | 8.0895 | 8.0063 | 7.9211 | 7.8295 | 7.7421 | 7.6589 | 7.5811 | 7.5105 | 7.2421 | 6.9063 | 6.5137 | 7.4368 | 7.3895 | 7.3389 | 7.2811 | 7.22 | 7.1611 | 7.1042 | 7.0526 | 7.0074 | 6.8547 | 6.7516 | 6.5705
|  | BLEDINGTON PRIMARY | CF |  |  |  |  | 7.5284 | 7.5021 | 7.4737 | 7.4432 | 7.4126 | 7.3821 | 7.3526 | 7.3221 | 7.2926 | 7.0947 | 6.9105 | 6.6937 | 8.2495 | 8.2053 | 8.1558 | 8.1032 | 8.0495 | 7.9968 | 7.9495 | 7.9011 | 7.8505 | 7.62 | 7.4095 | 7.1537 | 7.4821 | 7.4589 | 7.4337 | 7.4084 | 7.3811 | 7.3547 | 7.3263 | 7.2979 | 7.2695 | 7.1442 | 7.0737 | 7.0242
FLEET-BRAMLEY GSP | ALTON BSP | BORDON PRIMARY | MINIMUM HEADROOM | SU 82256 35269 | NO | YES | 0 | 24.1147 | 23.5916 | 23.0326 | 21.8453 | 20.2926 | 18.5084 | 16.7632 | 15.3189 | 14.1432 | 8.8147 | 4.6768 | -27.3737 | 17.6274 | 16.3021 | 14.8368 | 13.4179 | 11.6968 | 9.7053 | 7.7368 | 6.0895 | 4.7674 | -1.1737 | -5.7768 | -10.0063 | 18.6537 | 17.3011 | 15.8032 | 14.3568 | 12.5947 | 10.5558 | 8.5463 | 6.8979 | 5.5726 | -0.39263 | -5.0263 | -9.2653
|  | BORDON PRIMARY | EE |  |  |  |  | 24.4042 | 23.9663 | 23.4989 | 22.8958 | 21.5632 | 19.9937 | 18.4126 | 17.1105 | 16.0821 | 11.5905 | 8.2421 | 5.3147 | 18.2084 | 17.0558 | 15.7821 | 14.5789 | 13.08 | 11.3263 | 9.5537 | 8.0968 | 6.9379 | 1.9221 | -1.7832 | -5.0947 | 19.2453 | 18.0674 | 16.7663 | 15.5368 | 14.0042 | 12.2042 | 10.3853 | 8.8979 | 7.7347 | 2.6789 | -1.0737 | -4.3958
|  | BORDON PRIMARY | HT |  |  |  |  | 24.1147 | 23.5916 | 23.0326 | 21.8453 | 20.2926 | 18.5084 | 16.7632 | 15.3189 | 14.1432 | 8.8147 | 4.6768 | 0.92316 | 17.6274 | 16.3021 | 14.8368 | 13.4179 | 11.6968 | 9.7053 | 7.7368 | 6.0895 | 4.7674 | -1.1737 | -5.7768 | -10.0063 | 18.6537 | 17.3011 | 15.8032 | 14.3568 | 12.5947 | 10.5558 | 8.5463 | 6.8979 | 5.5726 | -0.39263 | -5.0263 | -9.2653
|  | BORDON PRIMARY | HE |  |  |  |  | 24.76 | 24.4747 | 24.1221 | 23.7526 | 23.1011 | 21.7337 | 20.3453 | 19.2389 | 18.4032 | 14.9158 | 12.52 | -27.3737 | 18.9874 | 18.0768 | 17.0337 | 16.0505 | 14.7558 | 13.2084 | 11.6411 | 10.4011 | 9.4716 | 5.4947 | 2.7863 | 0.33368 | 20.0368 | 19.1063 | 18.0389 | 17.0358 | 15.7095 | 14.1211 | 12.5126 | 11.24 | 10.2874 | 6.2895 | 3.5695 | 1.1084
|  | BORDON PRIMARY | CF |  |  |  |  | 25.0074 | 24.8621 | 24.7137 | 24.5589 | 24.3958 | 24.2242 | 23.9874 | 23.7621 | 23.2632 | 20.0147 | 18.4495 | 17.0916 | 20.82 | 20.3789 | 19.9653 | 19.5116 | 18.8926 | 17.9789 | 16.8032 | 15.7779 | 14.9063 | 11.2337 | 9.4747 | 7.8905 | 21.9189 | 21.4695 | 21.0474 | 20.5842 | 19.9495 | 19.0126 | 17.8032 | 16.7495 | 15.8558 | 12.0842 | 10.2768 | 8.6853
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | BOSCOMBE DOWN PRIMARY | MINIMUM HEADROOM | SU 17186 41044 | NO | YES | 0 | 32.8158 | 32.6821 | 32.54 | 32.1789 | 31.8053 | 31.4368 | 31.0211 | 30.8905 | 30.7684 | 29.8526 | 28.8074 | 5.48 | 28.3505 | 28.2642 | 28.1221 | 27.7232 | 27.3126 | 26.9084 | 26.4453 | 26.3168 | 26.1979 | 25.2274 | 24.0916 | 23.2326 | 28.5347 | 28.4011 | 28.2589 | 27.8632 | 27.4537 | 27.0516 | 26.5905 | 26.46 | 26.3379 | 25.3558 | 24.2084 | 23.3495
|  | BOSCOMBE DOWN PRIMARY | EE |  |  |  |  | 32.8979 | 32.7884 | 32.6716 | 32.5505 | 32.4168 | 32.2853 | 32.16 | 32.0358 | 31.9232 | 31.0011 | 30.0011 | 29.26 | 28.3505 | 28.3705 | 28.2547 | 28.1326 | 28.0021 | 27.8737 | 27.7505 | 27.6295 | 27.5211 | 26.54 | 25.4526 | 24.6242 | 28.6168 | 28.5074 | 28.3905 | 28.2695 | 28.1358 | 28.0042 | 27.8789 | 27.7547 | 27.6421 | 26.6442 | 25.5389 | 24.7105
|  | BOSCOMBE DOWN PRIMARY | HT |  |  |  |  | 32.8158 | 32.6821 | 32.54 | 32.1789 | 31.8053 | 31.4368 | 31.0211 | 30.8905 | 30.7684 | 29.8526 | 28.8074 | 28.0274 | 28.3979 | 28.2642 | 28.1221 | 27.7232 | 27.3126 | 26.9084 | 26.4453 | 26.3168 | 26.1979 | 25.2274 | 24.0916 | 23.2326 | 28.5347 | 28.4011 | 28.2589 | 27.8632 | 27.4537 | 27.0516 | 26.5905 | 26.46 | 26.3379 | 25.3558 | 24.2084 | 23.3495
|  | BOSCOMBE DOWN PRIMARY | HE |  |  |  |  | 33.0053 | 32.9305 | 32.8474 | 32.7579 | 32.6558 | 32.5579 | 32.4663 | 32.3789 | 32.3021 | 31.7632 | 31.0768 | 5.48 | 28.4579 | 28.5126 | 28.4295 | 28.34 | 28.24 | 28.1432 | 28.0526 | 27.9674 | 27.8916 | 27.3147 | 26.5453 | 26.0295 | 28.7242 | 28.6495 | 28.5663 | 28.4768 | 28.3747 | 28.2768 | 28.1853 | 28.0979 | 28.0211 | 27.4389 | 26.6674 | 26.1505
|  | BOSCOMBE DOWN PRIMARY | CF |  |  |  |  | 33.9463 | 33.0411 | 33.0021 | 32.9611 | 32.9158 | 32.8684 | 32.8242 | 32.7779 | 32.7347 | 32.4358 | 32.0411 | 31.7063 | 29.6821 | 28.4937 | 28.4547 | 28.4137 | 28.3695 | 28.3232 | 28.2789 | 28.2347 | 28.1916 | 28.0063 | 27.5663 | 27.1905 | 29.9905 | 28.76 | 28.7211 | 28.68 | 28.6347 | 28.5874 | 28.5432 | 28.4968 | 28.4537 | 28.1389 | 27.6979 | 27.3211
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST PRIMARY | MINIMUM HEADROOM | SZ 11636 92447 | NO | YES | 0 | 33.3947 | 33.1421 | 32.8726 | 32.5916 | 32.3011 | 32.0074 | 31.7474 | 31.5095 | 31.16 | 28.8358 | 26.66 | 7.0705 | 29.1642 | 28.9116 | 28.6421 | 28.3589 | 28.0537 | 27.4884 | 26.9263 | 26.3326 | 25.8579 | 23.2611 | 20.8158 | 18.5105 | 30.3137 | 30.0611 | 29.7916 | 29.5084 | 29.2042 | 28.6484 | 28.0979 | 27.5179 | 27.0674 | 24.4821 | 22.04 | 19.7379
|  | BOSCOMBE EAST PRIMARY | EE |  |  |  |  | 33.5484 | 33.3411 | 33.1211 | 32.8884 | 32.6463 | 32.4116 | 32.1874 | 31.9695 | 31.7747 | 30.4947 | 28.8032 | 27.24 | 29.3179 | 29.1105 | 28.8905 | 28.6579 | 28.4158 | 28.1811 | 27.9158 | 27.4926 | 27.0274 | 25.1 | 23.1926 | 21.4126 | 30.4674 | 30.26 | 30.04 | 29.8074 | 29.5653 | 29.3305 | 29.0663 | 28.6505 | 28.1968 | 26.3179 | 24.4137 | 22.6358
|  | BOSCOMBE EAST PRIMARY | HT |  |  |  |  | 33.3947 | 33.1421 | 32.8726 | 32.5916 | 32.3011 | 32.0074 | 31.7474 | 31.5095 | 31.16 | 28.8358 | 26.66 | 24.6242 | 29.1642 | 28.9116 | 28.6421 | 28.3589 | 28.0537 | 27.4884 | 26.9263 | 26.3326 | 25.8579 | 23.2611 | 20.8158 | 18.5105 | 30.3137 | 30.0611 | 29.7916 | 29.5084 | 29.2042 | 28.6484 | 28.0979 | 27.5179 | 27.0674 | 24.4821 | 22.04 | 19.7379
|  | BOSCOMBE EAST PRIMARY | HE |  |  |  |  | 33.7189 | 33.5621 | 33.3884 | 33.2021 | 33.0032 | 32.8126 | 32.6326 | 32.4653 | 32.3211 | 31.7884 | 30.8579 | 7.0705 | 29.4884 | 29.3316 | 29.1579 | 28.9716 | 28.7726 | 28.5821 | 28.4021 | 28.2347 | 28.0905 | 26.7642 | 25.3916 | 24.1379 | 30.6379 | 30.4811 | 30.3074 | 30.1211 | 29.9221 | 29.7316 | 29.5516 | 29.3842 | 29.24 | 27.9316 | 26.5989 | 25.3474
|  | BOSCOMBE EAST PRIMARY | CF |  |  |  |  | 33.8442 | 33.7558 | 33.6621 | 33.5663 | 33.4663 | 33.3653 | 33.2653 | 33.1663 | 33.0674 | 32.6274 | 32.4053 | 32.2221 | 29.6137 | 29.5253 | 29.4316 | 29.3358 | 29.2358 | 29.1347 | 29.0347 | 28.9358 | 28.8368 | 28.3958 | 27.7537 | 26.9158 | 30.7632 | 30.6747 | 30.5811 | 30.4853 | 30.3853 | 30.2842 | 30.1842 | 30.0853 | 29.9863 | 29.5453 | 28.9189 | 28.1084
EALING GSP |  | BOSTON MANOR PRIMARY | MINIMUM HEADROOM | TQ 17043 78092 | NO | YES | 0 | 48.8514 | 48.7451 | 70.5274 | 70.4074 | 69.56 | 68.7389 | 68.5295 | 68.3368 | 68.1526 | 67.3084 | 66.4158 | 25.0579 | 40.8914 | 40.0493 | 61.0695 | 59.9368 | 58.6263 | 57.62 | 57.3853 | 57.1674 | 56.9589 | 55.9958 | 54.9453 | 53.9221 | 43.1577 | 42.3714 | 63.3453 | 62.2516 | 60.9863 | 60.0137 | 59.7832 | 59.5705 | 59.3663 | 58.4137 | 57.3653 | 56.3432
|  | BOSTON MANOR PRIMARY | EE |  |  |  |  | 48.9103 | 48.8208 | 70.6232 | 70.5221 | 70.4168 | 70.0116 | 69.1726 | 68.6937 | 68.5295 | 67.9032 | 67.2568 | 66.6316 | 41.1535 | 40.6072 | 62.0137 | 61.2895 | 60.2579 | 59.1884 | 58.1537 | 57.5737 | 57.3874 | 56.6779 | 55.9211 | 55.1737 | 43.2324 | 42.9935 | 64.3421 | 63.5758 | 62.56 | 61.5274 | 60.5295 | 59.9674 | 59.7853 | 59.0916 | 58.3389 | 57.5926
|  | BOSTON MANOR PRIMARY | HT |  |  |  |  | 48.8514 | 48.7451 | 70.5274 | 70.4074 | 69.56 | 68.7389 | 68.5295 | 68.3368 | 68.1526 | 67.3084 | 66.4158 | 65.5568 | 40.8914 | 40.0493 | 61.0695 | 59.9368 | 58.6263 | 57.62 | 57.3853 | 57.1674 | 56.9589 | 55.9958 | 54.9453 | 53.9221 | 43.1577 | 42.3714 | 63.3453 | 62.2516 | 60.9863 | 60.0137 | 59.7832 | 59.5705 | 59.3663 | 58.4137 | 57.3653 | 56.3432
|  | BOSTON MANOR PRIMARY | HE |  |  |  |  | 48.9829 | 48.9145 | 70.7347 | 70.6537 | 70.5674 | 70.2989 | 69.5011 | 69.1547 | 69.0389 | 68.6295 | 68.1895 | 25.0579 | 41.2987 | 40.7882 | 62.24 | 61.5442 | 60.5495 | 59.5074 | 58.5189 | 58.1 | 57.9716 | 57.5105 | 56.9884 | 56.4716 | 43.3103 | 43.1872 | 64.5747 | 63.8389 | 62.8463 | 61.8411 | 60.8874 | 60.4821 | 60.3558 | 59.9042 | 59.3968 | 58.8895
|  | BOSTON MANOR PRIMARY | CF |  |  |  |  | 49.0335 | 48.9935 | 70.8474 | 70.8042 | 70.7589 | 70.7126 | 70.6674 | 70.6232 | 70.5789 | 70.3463 | 70.02 | 69.7347 | 41.5314 | 41.3777 | 63.1947 | 63.1095 | 63.0221 | 62.9295 | 62.7474 | 62.3684 | 61.8947 | 59.5958 | 59.2084 | 58.8632 | 43.3756 | 43.3261 | 65.1768 | 65.1305 | 65.0821 | 65.0326 | 64.9768 | 64.7421 | 64.2179 | 61.9221 | 61.5463 | 61.2116
MANNINGTON GSP | BOURNEMOUTH BSP | BOURNE VALLEY PRIMARY | MINIMUM HEADROOM | SZ 06207 92415 | NO | YES | 0 | 35.7263 | 35.2074 | 34.6558 | 34.0842 | 33.4947 | 32.9011 | 32.2526 | 31.1747 | 30.1337 | 25.4811 | 21.1989 | -14.6505 | 29.6958 | 28.7211 | 27.7253 | 26.7284 | 25.7179 | 24.5895 | 23.4737 | 22.3095 | 21.1811 | 16.0747 | 11.2579 | 6.7863 | 30.9621 | 29.9726 | 28.9621 | 27.9526 | 26.9284 | 25.7842 | 24.6495 | 23.4632 | 22.3137 | 17.1474 | 12.3368 | 7.8716
|  | BOURNE VALLEY PRIMARY | EE |  |  |  |  | 36.0347 | 35.6084 | 35.1558 | 34.68 | 34.1874 | 33.7126 | 33.2589 | 32.8221 | 32.4326 | 28.8179 | 25.4926 | 22.46 | 30.3589 | 29.5821 | 28.7884 | 27.98 | 27.1768 | 26.2937 | 25.4347 | 24.6074 | 23.6905 | 19.7421 | 16.0211 | 12.5674 | 31.4316 | 30.8484 | 30.0432 | 29.2253 | 28.4116 | 27.5158 | 26.6432 | 25.8042 | 24.8705 | 20.8432 | 17.0947 | 13.6453
|  | BOURNE VALLEY PRIMARY | HT |  |  |  |  | 35.7263 | 35.2074 | 34.6558 | 34.0842 | 33.4947 | 32.9011 | 32.2526 | 31.1747 | 30.1337 | 25.4811 | 21.1989 | 17.2495 | 29.6958 | 28.7211 | 27.7253 | 26.7284 | 25.7179 | 24.5895 | 23.4737 | 22.3095 | 21.1811 | 16.0747 | 11.2579 | 6.7863 | 30.9621 | 29.9726 | 28.9621 | 27.9526 | 26.9284 | 25.7842 | 24.6495 | 23.4632 | 22.3137 | 17.1474 | 12.3368 | 7.8716
|  | BOURNE VALLEY PRIMARY | HE |  |  |  |  | 36.4147 | 36.1042 | 35.76 | 35.3895 | 34.9958 | 34.6189 | 34.2632 | 33.9316 | 33.6453 | 32.3095 | 29.9274 | -14.6505 | 30.9937 | 30.6568 | 30.1537 | 29.5842 | 29.0032 | 28.3389 | 27.7147 | 27.0884 | 26.3789 | 23.4958 | 20.8526 | 18.4368 | 31.84 | 31.5179 | 31.1611 | 30.7789 | 30.2705 | 29.5968 | 28.9642 | 28.3284 | 27.6053 | 24.6621 | 21.9547 | 19.5084
|  | BOURNE VALLEY PRIMARY | CF |  |  |  |  | 36.6863 | 36.5168 | 36.3411 | 36.1589 | 35.9705 | 35.7779 | 35.5895 | 35.4021 | 35.2158 | 34.3821 | 33.9653 | 32.6137 | 31.2916 | 31.1042 | 30.9095 | 30.7084 | 30.3568 | 29.9242 | 29.4758 | 29.0716 | 28.6905 | 27.0726 | 25.2747 | 23.6916 | 32.1232 | 31.9453 | 31.7611 | 31.5705 | 31.3716 | 31.1642 | 30.74 | 30.3284 | 29.94 | 28.2979 | 26.4568 | 24.8305
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON PRIMARY | MINIMUM HEADROOM | ST 77363 30262 | NO | YES | 0.21053 | 10.8621 | 10.4095 | 9.9495 | 9.4884 | 9.3958 | 8.9453 | 8.5337 | 8.1495 | 7.7853 | 6.0716 | 4.2632 | -11.1737 | 8.3916 | 7.9063 | 7.4147 | 6.9232 | 6.8926 | 6.4158 | 5.9779 | 5.5684 | 5.1779 | 3.32 | 1.3 | -0.75579 | 8.8253 | 8.3537 | 7.8758 | 7.3968 | 7.3379 | 6.8716 | 6.4453 | 6.04 | 5.6474 | 3.7779 | 1.7568 | -0.29368
|  | BOURTON PRIMARY | EE |  |  |  |  | 11.1674 | 10.8074 | 10.4379 | 10.0653 | 9.6884 | 9.3326 | 8.9937 | 8.6663 | 8.3684 | 7.4274 | 6.0874 | 4.7242 | 8.7221 | 8.3368 | 7.9432 | 7.5463 | 7.1474 | 6.7705 | 6.4105 | 6.0642 | 5.7474 | 4.7905 | 3.3021 | 1.7484 | 9.1411 | 8.7695 | 8.3874 | 8.0011 | 7.6116 | 7.2442 | 6.8926 | 6.5547 | 6.2463 | 5.2579 | 3.7568 | 2.2063
|  | BOURTON PRIMARY | HT |  |  |  |  | 10.8621 | 10.4095 | 9.9495 | 9.4884 | 9.3958 | 8.9453 | 8.5337 | 8.1495 | 7.7853 | 6.0716 | 4.2632 | 2.4505 | 8.3916 | 7.9063 | 7.4147 | 6.9232 | 6.8926 | 6.4158 | 5.9779 | 5.5684 | 5.1779 | 3.32 | 1.3 | -0.75579 | 8.8253 | 8.3537 | 7.8758 | 7.3968 | 7.3379 | 6.8716 | 6.4453 | 6.04 | 5.6474 | 3.7779 | 1.7568 | -0.29368
|  | BOURTON PRIMARY | HE |  |  |  |  | 11.5768 | 11.3421 | 11.0926 | 10.8337 | 10.5653 | 10.3126 | 10.0726 | 9.8495 | 9.6484 | 9.1832 | 8.2716 | -11.1737 | 9.1526 | 8.9095 | 8.6516 | 8.3779 | 8.0958 | 7.8305 | 7.5789 | 7.3442 | 7.1326 | 6.6937 | 5.6737 | 4.5811 | 9.5295 | 9.3032 | 9.0632 | 8.8053 | 8.5284 | 8.2695 | 8.0221 | 7.7926 | 7.5853 | 7.1326 | 6.1442 | 5.04
|  | BOURTON PRIMARY | CF |  |  |  |  | 11.8484 | 11.7147 | 11.5758 | 11.4337 | 11.2842 | 11.1326 | 10.9874 | 10.8453 | 10.7042 | 10.0516 | 9.8168 | 9.1863 | 9.4368 | 9.2979 | 9.1537 | 9.0042 | 8.8484 | 8.6905 | 8.5358 | 8.3832 | 8.2316 | 7.5316 | 7.3179 | 6.5989 | 9.7884 | 9.6611 | 9.5284 | 9.3916 | 9.2484 | 9.1042 | 8.9611 | 8.8126 | 8.6653 | 7.9863 | 7.7611 | 7.0705
MANNINGTON GSP | WAREHAM BSP | BOVINGTON PRIMARY | MINIMUM HEADROOM | SY 83933 87831 | NO | YES | 0 | 7.5274 | 7.2832 | 7.1263 | 6.7316 | 6.1547 | 5.6716 | 4.9432 | 4.3053 | 3.2789 | 2.0726 | 0.64632 | -2.5653 | 7.1726 | 6.9063 | 6.7411 | 6.3042 | 5.6158 | 5.0379 | 4.18 | 3.4474 | 2.2579 | 0.90842 | -0.70947 | -1.1463 | 7.1032 | 6.8484 | 6.6863 | 6.2684 | 5.5821 | 5.0011 | 4.14 | 3.4063 | 2.2147 | 0.85684 | -0.77053 | -1.2116
|  | BOVINGTON PRIMARY | EE |  |  |  |  | 7.6284 | 7.4126 | 7.2874 | 6.92 | 6.3705 | 5.9168 | 5.2179 | 4.5947 | 3.98 | 2.4779 | 1.9421 | 1.44 | 7.28 | 7.0453 | 6.9126 | 6.5074 | 5.8558 | 5.3126 | 4.4779 | 3.7632 | 3.0579 | 1.36 | 0.78947 | 0.22737 | 7.2021 | 6.9832 | 6.8537 | 6.4642 | 5.8253 | 5.2737 | 4.4368 | 3.72 | 3.0126 | 1.3 | 0.71158 | 0.14526
|  | BOVINGTON PRIMARY | HT |  |  |  |  | 7.5274 | 7.2832 | 7.1263 | 6.7316 | 6.1547 | 5.6716 | 4.9432 | 4.3053 | 3.2789 | 2.0726 | 0.64632 | 0.24 | 7.1726 | 6.9063 | 6.7411 | 6.3042 | 5.6158 | 5.0379 | 4.18 | 3.4474 | 2.2579 | 0.90842 | -0.70947 | -1.1463 | 7.1032 | 6.8484 | 6.6863 | 6.2684 | 5.5821 | 5.0011 | 4.14 | 3.4063 | 2.2147 | 0.85684 | -0.77053 | -1.2116
|  | BOVINGTON PRIMARY | HE |  |  |  |  | 7.7642 | 7.5937 | 7.5074 | 7.1811 | 6.6674 | 6.2516 | 5.6042 | 5.0221 | 4.4495 | 3.1526 | 2.8242 | -2.5653 | 7.4263 | 7.2379 | 7.1484 | 6.7842 | 6.1863 | 5.6874 | 4.8947 | 4.2232 | 3.56 | 2.0758 | 1.7147 | 1.32 | 7.3358 | 7.1695 | 7.0832 | 6.7347 | 6.1589 | 5.6516 | 4.8579 | 4.1832 | 3.52 | 2.0295 | 1.6642 | 1.2653
|  | BOVINGTON PRIMARY | CF |  |  |  |  | 7.8442 | 7.7568 | 7.7095 | 7.5621 | 7.3453 | 7.1495 | 6.8263 | 6.5284 | 6.2095 | 5.3684 | 5.1442 | 4.9116 | 7.5095 | 7.4137 | 7.3632 | 7.2 | 6.9579 | 6.74 | 6.3568 | 5.9947 | 5.6053 | 4.6137 | 4.3663 | 4.1053 | 7.4147 | 7.3295 | 7.2821 | 7.1358 | 6.9042 | 6.6937 | 6.3316 | 5.9621 | 5.5674 | 4.5737 | 4.3242 | 4.06
AMERSHAM GSP | LOUDWATER BSP | BOWERDEAN PRIMARY | MINIMUM HEADROOM | SU 87718 93880 | NO | YES | 0 | 24.5463 | 22.8926 | 21.2379 | 19.5779 | 18.0263 | 16.5032 | 15.2432 | 14.2821 | 13.3621 | 9.1947 | 5.5368 | -23.5032 | 18.0863 | 15.9389 | 14.0389 | 12.1726 | 10.4411 | 8.7432 | 7.3484 | 6.3126 | 5.3189 | 0.77684 | -3.2547 | -6.8768 | 19.6484 | 17.4853 | 15.5842 | 13.7179 | 11.9842 | 10.2874 | 8.8905 | 7.8547 | 6.86 | 2.3116 | -1.7263 | -5.3526
|  | BOWERDEAN PRIMARY | EE |  |  |  |  | 25.0232 | 23.7947 | 22.38 | 20.9274 | 19.5716 | 18.2842 | 17.2 | 16.3884 | 15.6274 | 12.3579 | 9.6011 | 7.1979 | 18.8568 | 16.9579 | 15.2916 | 13.6505 | 12.1305 | 10.6884 | 9.4874 | 8.6084 | 7.7789 | 4.2137 | 1.1663 | -1.5211 | 20.4316 | 18.5042 | 16.8379 | 15.1958 | 13.6747 | 12.2326 | 11.0295 | 10.1495 | 9.3189 | 5.7463 | 2.6905 | 0
|  | BOWERDEAN PRIMARY | HT |  |  |  |  | 24.5463 | 22.8926 | 21.2379 | 19.5779 | 18.0263 | 16.5032 | 15.2432 | 14.2821 | 13.3621 | 9.1947 | 5.5368 | 2.28 | 18.0863 | 15.9389 | 14.0389 | 12.1726 | 10.4411 | 8.7432 | 7.3484 | 6.3126 | 5.3189 | 0.77684 | -3.2547 | -6.8768 | 19.6484 | 17.4853 | 15.5842 | 13.7179 | 11.9842 | 10.2874 | 8.8905 | 7.8547 | 6.86 | 2.3116 | -1.7263 | -5.3526
|  | BOWERDEAN PRIMARY | HE |  |  |  |  | 25.4979 | 24.9758 | 23.8326 | 22.6821 | 21.5695 | 20.5211 | 19.6674 | 19.0895 | 18.5537 | 16.4053 | 14.6705 | -23.5032 | 19.8632 | 18.2916 | 16.9358 | 15.5811 | 14.3284 | 13.1474 | 12.1979 | 11.5768 | 10.9937 | 8.6221 | 6.6758 | 5.0105 | 21.4558 | 19.8442 | 18.4821 | 17.1274 | 15.8726 | 14.6926 | 13.7421 | 13.1189 | 12.5368 | 10.1611 | 8.2126 | 6.5453
|  | BOWERDEAN PRIMARY | CF |  |  |  |  | 25.8221 | 25.6516 | 25.4737 | 25.1958 | 24.8758 | 24.3579 | 23.9053 | 23.5653 | 23.2147 | 21.5358 | 20.2747 | 19.2453 | 20.86 | 20.0632 | 19.4063 | 18.7716 | 18.1832 | 17.5811 | 17.0547 | 16.6705 | 16.2737 | 14.3884 | 12.9558 | 11.7642 | 22.0611 | 21.6568 | 20.9853 | 20.3358 | 19.7347 | 19.1263 | 18.6 | 18.2158 | 17.82 | 15.9316 | 14.4979 | 13.3053
FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL PRIMARY | MINIMUM HEADROOM | SU 86075 69397 | NO | YES | 0.11684 | 90.6107 | 90.4781 | 90.3402 | 90.1981 | 90.0496 | 99.4223 | 99.0402 | 97.4012 | 94.8938 | 87.1623 | 83.9875 | 8.2181 | 79.557 | 79.4223 | 79.2833 | 79.0581 | 78.4402 | 88.6623 | 85.8917 | 82.7465 | 79.8465 | 70.9675 | 67.4086 | 64.1654 | 81.5517 | 81.4181 | 81.2791 | 81.1286 | 80.9475 | 89.957 | 87.1686 | 84.0223 | 81.1212 | 72.2381 | 68.6759 | 65.4307
|  | BRACKNELL PRIMARY | EE |  |  |  |  | 101.6959 | 101.3854 | 101.0549 | 100.7075 | 100.3444 | 99.9928 | 99.657 | 98.6675 | 96.2423 | 89.1844 | 86.7096 | 84.497 | 94.0886 | 93.7781 | 93.4475 | 93.0749 | 91.397 | 89.8265 | 87.1833 | 84.1244 | 81.3159 | 73.1854 | 70.4033 | 67.8949 | 94.6644 | 94.3538 | 94.0233 | 93.6759 | 92.7496 | 91.1402 | 88.4612 | 85.4002 | 82.5896 | 74.4549 | 71.6686 | 69.1591
|  | BRACKNELL PRIMARY | HT |  |  |  |  | 101.4791 | 101.1033 | 100.7033 | 100.2875 | 99.857 | 99.4223 | 99.0402 | 97.4012 | 94.8938 | 87.1623 | 83.9875 | 81.1138 | 93.8717 | 93.4959 | 93.0959 | 92.1791 | 90.3728 | 88.6623 | 85.8917 | 82.7465 | 79.8465 | 70.9675 | 67.4086 | 64.1654 | 94.4475 | 94.0717 | 93.6717 | 93.2559 | 91.7086 | 89.957 | 87.1686 | 84.0223 | 81.1212 | 72.2381 | 68.6759 | 65.4307
|  | BRACKNELL PRIMARY | HE |  |  |  |  | 101.9602 | 101.7275 | 101.4707 | 101.1938 | 100.8991 | 100.6159 | 100.3507 | 100.1012 | 98.0475 | 91.7412 | 89.9875 | 8.2181 | 94.3528 | 94.1202 | 93.8633 | 93.5865 | 92.6938 | 91.2844 | 88.8286 | 85.9338 | 83.2907 | 75.9854 | 73.9959 | 72.257 | 94.9286 | 94.6959 | 94.4391 | 94.1623 | 93.8675 | 92.6244 | 90.1054 | 87.2096 | 84.5675 | 77.2581 | 75.2686 | 73.5265
|  | BRACKNELL PRIMARY | CF |  |  |  |  | 90.6107 | 90.4781 | 90.3402 | 90.1981 | 90.0496 | 101.4328 | 101.2854 | 101.1391 | 100.9917 | 100.1086 | 98.8717 | 97.8402 | 79.557 | 79.4223 | 79.2833 | 79.0581 | 78.4402 | 93.8265 | 93.6402 | 92.0781 | 90.5223 | 85.6423 | 84.2433 | 83.0602 | 81.5517 | 81.4181 | 81.2791 | 81.1286 | 80.9475 | 94.4012 | 94.2538 | 93.4275 | 91.8265 | 86.9191 | 85.5191 | 84.3349
MELKSHAM GSP | NORRINGTON BSP | BRADFORD-ON-AVON PRIMARY | MINIMUM HEADROOM | ST 81260 60564 | NO | YES | 0 | 33.5284 | 33.2095 | 32.8695 | 32.52 | 32.0358 | 30.1705 | 28.5737 | 28.2316 | 27.9105 | 25.4979 | 22.7253 | 6.7147 | 28.8063 | 28.3821 | 27.9389 | 27.4916 | 27.0021 | 24.8937 | 23.0926 | 22.7684 | 22.4642 | 19.9884 | 17.0674 | 15.8579 | 29.6505 | 29.2221 | 28.7758 | 28.3232 | 27.8211 | 25.7011 | 23.8874 | 23.5453 | 23.2242 | 20.6432 | 17.6063 | 16.3463
|  | BRADFORD-ON-AVON PRIMARY | EE |  |  |  |  | 33.7137 | 33.4474 | 33.1663 | 32.8726 | 32.5337 | 32.1747 | 31.7653 | 31.3579 | 30.9737 | 28.5789 | 26.0232 | 23.9326 | 29.0726 | 28.7253 | 28.3653 | 27.9947 | 27.5832 | 27.1705 | 26.7674 | 26.3663 | 25.9895 | 23.5779 | 20.9579 | 18.6663 | 29.9189 | 29.5663 | 29.2042 | 28.8284 | 28.4053 | 27.9747 | 27.5537 | 27.1347 | 26.7358 | 24.1705 | 21.3811 | 19.0358
|  | BRADFORD-ON-AVON PRIMARY | HT |  |  |  |  | 33.5284 | 33.2095 | 32.8695 | 32.52 | 32.0358 | 30.1705 | 28.5737 | 28.2316 | 27.9105 | 25.4979 | 22.7253 | 21.5337 | 28.8063 | 28.3821 | 27.9389 | 27.4916 | 27.0021 | 24.8937 | 23.0926 | 22.7684 | 22.4642 | 19.9884 | 17.0674 | 15.8579 | 29.6505 | 29.2221 | 28.7758 | 28.3232 | 27.8211 | 25.7011 | 23.8874 | 23.5453 | 23.2242 | 20.6432 | 17.6063 | 16.3463
|  | BRADFORD-ON-AVON PRIMARY | HE |  |  |  |  | 33.9611 | 33.78 | 33.5758 | 33.3579 | 33.0947 | 32.8453 | 32.6053 | 32.3789 | 32.1768 | 31.2621 | 29.5084 | 6.7147 | 29.3905 | 29.1947 | 28.9453 | 28.6821 | 28.3768 | 28.0853 | 27.8053 | 27.54 | 27.2989 | 26.3042 | 24.4032 | 22.9768 | 30.2389 | 30.0432 | 29.7937 | 29.5284 | 29.2126 | 28.9126 | 28.6253 | 28.3505 | 28.1 | 27.0484 | 25.0789 | 23.6105
|  | BRADFORD-ON-AVON PRIMARY | CF |  |  |  |  | 34.1232 | 34.0284 | 33.9295 | 33.8242 | 33.7 | 33.5747 | 33.4505 | 33.3284 | 33.2116 | 32.6558 | 32.1926 | 31.1821 | 29.5526 | 29.4579 | 29.3589 | 29.2347 | 29.0758 | 28.92 | 28.7642 | 28.6095 | 28.4589 | 27.7495 | 27.1989 | 26.0968 | 30.4021 | 30.3074 | 30.2084 | 30.0832 | 29.9211 | 29.7589 | 29.5989 | 29.4411 | 29.2863 | 28.5547 | 27.9768 | 26.8326
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BRAMLEY GREEN PRIMARY | MINIMUM HEADROOM | SU 67431 58511 | NO | YES | 0 | 16.2432 | 16.2695 | 15.9811 | 15.7758 | 15.5495 | 14.9253 | 14.1642 | 14.0632 | 13.9705 | 12.66 | 10.8926 | 6.1274 | 14.7979 | 14.4221 | 14 | 13.78 | 13.5768 | 12.8653 | 11.9895 | 11.8884 | 11.7958 | 10.3189 | 8.2874 | 7.7726 | 15.0179 | 14.6421 | 14.22 | 14 | 13.7558 | 13.0463 | 12.1716 | 12.0705 | 11.9779 | 10.5032 | 8.4747 | 7.96
|  | BRAMLEY GREEN PRIMARY | EE |  |  |  |  | 16.2432 | 16.5326 | 16.1989 | 16.0316 | 15.8632 | 15.7011 | 15.5421 | 15.3832 | 15.2358 | 14.6632 | 13.2421 | 12.1442 | 14.9442 | 14.6116 | 14.2368 | 14.0589 | 13.92 | 13.7463 | 13.5358 | 13.4053 | 13.2474 | 12.6242 | 10.9863 | 9.7189 | 15.1642 | 14.8316 | 14.4568 | 14.2779 | 14.0979 | 13.9253 | 13.7558 | 13.5853 | 13.4263 | 12.8042 | 11.1695 | 9.9042
|  | BRAMLEY GREEN PRIMARY | HT |  |  |  |  | 16.6947 | 16.3579 | 15.9811 | 15.7758 | 15.5495 | 14.9253 | 14.1642 | 14.0632 | 13.9705 | 12.66 | 10.8926 | 10.4221 | 14.7979 | 14.4221 | 14 | 13.78 | 13.5768 | 12.8653 | 11.9895 | 11.8884 | 11.7958 | 10.3189 | 8.2874 | 7.7726 | 15.0179 | 14.6421 | 14.22 | 14 | 13.7558 | 13.0463 | 12.1716 | 12.0705 | 11.9779 | 10.5032 | 8.4747 | 7.96
|  | BRAMLEY GREEN PRIMARY | HE |  |  |  |  | 16.3326 | 16.2695 | 16.4874 | 16.3705 | 16.2495 | 16.1326 | 16.0179 | 15.9095 | 15.8105 | 15.4432 | 14.4832 | 6.1274 | 15.1411 | 14.8684 | 14.5505 | 14.4263 | 14.2979 | 14.2158 | 14.0526 | 13.9379 | 13.8716 | 13.4747 | 12.3642 | 11.3263 | 15.3611 | 15.0884 | 14.7705 | 14.6463 | 14.5179 | 14.3947 | 14.2716 | 14.1568 | 14.0505 | 13.6537 | 12.5453 | 11.5084
|  | BRAMLEY GREEN PRIMARY | CF |  |  |  |  | 16.3937 | 16.36 | 16.9968 | 16.8789 | 16.7495 | 16.6337 | 16.5526 | 16.4853 | 16.4189 | 16.1053 | 15.7958 | 15.1326 | 15.3232 | 15.2505 | 15.1274 | 14.9937 | 14.8484 | 14.7189 | 14.6305 | 14.5579 | 14.4863 | 14.1453 | 13.8368 | 13.0642 | 15.5611 | 15.4705 | 15.3474 | 15.2137 | 15.0684 | 14.9389 | 14.8495 | 14.7779 | 14.7063 | 14.3653 | 14.0158 | 13.2442
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD PRIMARY | MINIMUM HEADROOM | SZ 64712 98665 | NO | YES | 0.057895 | 35.0871 | 34.7682 | 34.4303 | 34.0703 | 33.6945 | 33.3103 | 32.9661 | 32.6461 | 32.3503 | 29.3713 | 26.2397 | 0.87132 | 30.2503 | 29.7071 | 28.9745 | 28.2397 | 27.5976 | 26.9545 | 26.3576 | 25.7861 | 25.1071 | 21.6397 | 18.1397 | 14.865 | 30.985 | 30.6429 | 30.105 | 29.3587 | 28.7061 | 28.0566 | 27.4492 | 26.8724 | 26.1945 | 22.7271 | 19.2271 | 15.9555
|  | BRANDON ROAD PRIMARY | EE |  |  |  |  | 35.2924 | 35.0366 | 34.7639 | 34.4703 | 34.1608 | 33.8576 | 33.5597 | 33.2692 | 33.0061 | 31.5429 | 29.0903 | 26.8703 | 30.5261 | 30.1661 | 29.6534 | 29.0545 | 28.5303 | 28.0229 | 27.5229 | 27.0334 | 26.5776 | 24.0376 | 21.2934 | 18.7818 | 31.2029 | 30.9282 | 30.6355 | 30.1861 | 29.6534 | 29.1408 | 28.6334 | 28.1376 | 27.6734 | 25.1187 | 22.3713 | 19.8618
|  | BRANDON ROAD PRIMARY | HT |  |  |  |  | 35.0871 | 34.7682 | 34.4303 | 34.0703 | 33.6945 | 33.3103 | 32.9661 | 32.6461 | 32.3503 | 29.3713 | 26.2397 | 23.3292 | 30.2503 | 29.7071 | 28.9745 | 28.2397 | 27.5976 | 26.9545 | 26.3576 | 25.7861 | 25.1071 | 21.6397 | 18.1397 | 14.865 | 30.985 | 30.6429 | 30.105 | 29.3587 | 28.7061 | 28.0566 | 27.4492 | 26.8724 | 26.1945 | 22.7271 | 19.2271 | 15.9555
|  | BRANDON ROAD PRIMARY | HE |  |  |  |  | 35.4461 | 35.2292 | 34.9903 | 34.7324 | 34.4566 | 34.1924 | 33.9439 | 33.7113 | 33.5113 | 32.8008 | 32.3482 | 0.87132 | 30.7513 | 30.4797 | 30.1618 | 29.8334 | 29.4597 | 29.0766 | 28.7124 | 28.3734 | 28.0703 | 26.8103 | 25.1197 | 23.4082 | 31.3734 | 31.1429 | 30.8903 | 30.6187 | 30.3355 | 30.0639 | 29.8082 | 29.5071 | 29.1997 | 27.9197 | 26.2018 | 24.4913
|  | BRANDON ROAD PRIMARY | CF |  |  |  |  | 35.5692 | 35.4282 | 35.2808 | 35.1303 | 34.9724 | 34.8124 | 34.6545 | 34.4976 | 34.3418 | 33.6461 | 33.2882 | 33.0861 | 30.8903 | 30.7261 | 30.5376 | 30.3408 | 30.1513 | 29.9587 | 29.7671 | 29.5618 | 29.3018 | 28.0924 | 26.9724 | 25.8061 | 31.5039 | 31.3524 | 31.1955 | 31.0366 | 30.8734 | 30.7071 | 30.5429 | 30.3797 | 30.2176 | 29.2187 | 28.0745 | 26.8913
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | BRAYWICK ROAD PRIMARY | MINIMUM HEADROOM | SU 88887 80726 | NO | YES | 0 | 25.9189 | 25.6768 | 24.76 | 21.9232 | 18.8179 | 17.0695 | 15.3832 | 14.8789 | 14.4042 | 12.2326 | 10.2895 | -24.2789 | 18.0811 | 16.7421 | 14.0926 | 10.8095 | 7.1947 | 5.1821 | 3.2358 | 2.6821 | 2.1568 | -0.25579 | -2.4379 | -4.4642 | 19.8453 | 18.4874 | 15.7958 | 12.4958 | 8.8811 | 6.8674 | 4.92 | 4.3663 | 3.8411 | 1.4274 | -0.75474 | -2.7811
|  | BRAYWICK ROAD PRIMARY | EE |  |  |  |  | 26.0695 | 25.8726 | 25.5021 | 22.7495 | 19.7295 | 17.4242 | 15.8053 | 15.3726 | 14.9716 | 13.2347 | 11.7305 | 10.3632 | 18.3021 | 17.4653 | 14.9147 | 11.7316 | 8.2095 | 5.5284 | 3.6558 | 3.1821 | 2.7411 | 0.80737 | -0.88737 | -2.4432 | 20.0621 | 19.2189 | 16.6274 | 13.4189 | 9.8958 | 7.2137 | 5.34 | 4.8663 | 4.4253 | 2.4916 | 0.79579 | -0.76105
|  | BRAYWICK ROAD PRIMARY | HT |  |  |  |  | 25.9189 | 25.6768 | 24.76 | 21.9232 | 18.8179 | 17.0695 | 15.3832 | 14.8789 | 14.4042 | 12.2326 | 10.2895 | 8.4979 | 18.0811 | 16.7421 | 14.0926 | 10.8095 | 7.1947 | 5.1821 | 3.2358 | 2.6821 | 2.1568 | -0.25579 | -2.4379 | -4.4642 | 19.8453 | 18.4874 | 15.7958 | 12.4958 | 8.8811 | 6.8674 | 4.92 | 4.3663 | 3.8411 | 1.4274 | -0.75474 | -2.7811
|  | BRAYWICK ROAD PRIMARY | HE |  |  |  |  | 26.2516 | 26.1105 | 25.9547 | 24.0979 | 21.4768 | 19.5726 | 17.7063 | 17.0789 | 16.4768 | 14.7379 | 13.6558 | -24.2789 | 18.5463 | 18.0979 | 16.0105 | 13.26 | 10.2 | 7.9842 | 5.8116 | 5.1 | 4.4116 | 2.4389 | 1.2095 | 0.098947 | 20.3032 | 19.8579 | 17.7379 | 14.9474 | 11.8863 | 9.6705 | 7.4968 | 6.7842 | 6.0968 | 4.1232 | 2.8937 | 1.7821
|  | BRAYWICK ROAD PRIMARY | CF |  |  |  |  | 26.3747 | 26.2979 | 26.2179 | 26.1358 | 26.0495 | 25.8158 | 24.1063 | 23.6358 | 23.26 | 21.8253 | 21.0779 | 20.4368 | 18.9168 | 18.7589 | 18.6042 | 18.3379 | 17.0747 | 15.2316 | 13.2547 | 12.7147 | 12.2863 | 10.6621 | 9.8137 | 9.0758 | 20.6305 | 20.5063 | 20.3558 | 20.0989 | 18.8189 | 16.9442 | 14.9421 | 14.4021 | 13.9737 | 12.3495 | 11.5 | 10.7621
EALING GSP | EALING BSP | BRENTFORD PRIMARY | MINIMUM HEADROOM | TQ 17659 78277 | NO | YES | 0 | 37.0558 | 36.6621 | 35.4547 | 33.8779 | 32.1937 | 30.6147 | 29.5989 | 28.6189 | 27.6684 | 23.3789 | 20.1495 | -15.1074 | 28.3621 | 26.8684 | 25.1811 | 23.3863 | 21.4695 | 19.6768 | 18.5411 | 17.4432 | 16.3747 | 11.5326 | 7.8947 | 4.5842 | 29.9684 | 28.4621 | 26.7737 | 24.9789 | 23.0611 | 21.2684 | 20.1316 | 19.0337 | 17.9653 | 13.1295 | 9.4968 | 6.1905
|  | BRENTFORD PRIMARY | EE |  |  |  |  | 37.2516 | 36.9811 | 36.6474 | 35.9674 | 34.6432 | 33.3895 | 32.0842 | 30.8558 | 29.8379 | 25.9579 | 23.6042 | 21.5137 | 29.0716 | 28.1232 | 27.0968 | 25.7842 | 24.28 | 22.8579 | 21.3726 | 19.9758 | 18.8232 | 14.4242 | 11.7737 | 9.4032 | 30.6811 | 29.7263 | 28.6905 | 27.3768 | 25.8726 | 24.4495 | 22.9642 | 21.5663 | 20.4137 | 16.0179 | 13.3705 | 11.0042
|  | BRENTFORD PRIMARY | HT |  |  |  |  | 37.0558 | 36.6621 | 35.4547 | 33.8779 | 32.1937 | 30.6147 | 29.5989 | 28.6189 | 27.6684 | 23.3789 | 20.1495 | 17.2253 | 28.3621 | 26.8684 | 25.1811 | 23.3863 | 21.4695 | 19.6768 | 18.5411 | 17.4432 | 16.3747 | 11.5326 | 7.8947 | 4.5842 | 29.9684 | 28.4621 | 26.7737 | 24.9789 | 23.0611 | 21.2684 | 20.1316 | 19.0337 | 17.9653 | 13.1295 | 9.4968 | 6.1905
|  | BRENTFORD PRIMARY | HE |  |  |  |  | 37.4368 | 37.2168 | 36.9579 | 36.6326 | 35.5063 | 34.3653 | 33.1611 | 32.12 | 31.2789 | 28.1347 | 26.4758 | -15.1074 | 29.5884 | 28.7137 | 27.8042 | 26.6242 | 25.2316 | 23.9337 | 22.5589 | 21.3726 | 20.4158 | 16.8337 | 14.9526 | 13.3674 | 31.1916 | 30.3242 | 29.4032 | 28.2168 | 26.8242 | 25.5263 | 24.1505 | 22.9642 | 22.0074 | 18.4242 | 16.5453 | 14.9632
|  | BRENTFORD PRIMARY | CF |  |  |  |  | 37.5726 | 37.4337 | 37.2884 | 37.1389 | 36.9853 | 36.8274 | 36.6726 | 36.5189 | 36.3526 | 32.3589 | 30.9337 | 29.9832 | 30.6947 | 30.3705 | 30.0695 | 29.7558 | 29.4274 | 29.0895 | 28.6568 | 27.9968 | 27.2474 | 21.6537 | 20.0337 | 18.9484 | 32.2779 | 31.9579 | 31.66 | 31.3495 | 31.0253 | 30.6905 | 30.2632 | 29.6063 | 28.8463 | 23.2453 | 21.6253 | 20.54
EALING GSP |  | BRIDGE ROAD PRIMARY | MINIMUM HEADROOM | TQ 14778 75741 | NO | YES | 0.40737 | 87.4052 | 86.7915 | 85.9652 | 160.8498 | 160.1425 | 156.7235 | 153.4162 | 150.1783 | 146.9951 | 138.3214 | 131.8256 | 84.6572 | 76.2631 | 73.4505 | 70.0736 | 66.261 | 141.7456 | 137.8498 | 134.0698 | 130.3625 | 126.713 | 116.9046 | 109.5667 | 102.6214 | 78.9673 | 76.3926 | 73.021 | 69.2147 | 144.6993 | 140.8088 | 137.0351 | 133.3341 | 129.6898 | 119.8951 | 112.5688 | 105.6341
|  | BRIDGE ROAD PRIMARY | EE |  |  |  |  | 87.7589 | 87.2526 | 86.7136 | 162.2298 | 161.4435 | 159.4446 | 156.5972 | 156.0583 | 155.5751 | 146.3593 | 141.4614 | 137.0383 | 77.5126 | 75.9799 | 73.9021 | 71.1115 | 143.9783 | 140.8867 | 137.6351 | 137.0962 | 136.613 | 126.0888 | 120.5498 | 115.5141 | 79.321 | 78.8147 | 76.8431 | 74.0578 | 146.9288 | 143.8414 | 140.5962 | 140.0572 | 139.5741 | 129.0656 | 123.5341 | 118.5067
|  | BRIDGE ROAD PRIMARY | HT |  |  |  |  | 87.4052 | 86.7915 | 85.9652 | 160.8498 | 160.1425 | 156.7235 | 153.4162 | 150.1783 | 146.9951 | 138.3214 | 131.8256 | 125.713 | 76.2631 | 73.4505 | 70.0736 | 66.261 | 141.7456 | 137.8498 | 134.0698 | 130.3625 | 126.713 | 116.9046 | 109.5667 | 102.6214 | 78.9673 | 76.3926 | 73.021 | 69.2147 | 144.6993 | 140.8088 | 137.0351 | 133.3341 | 129.6898 | 119.8951 | 112.5688 | 105.6341
|  | BRIDGE ROAD PRIMARY | HE |  |  |  |  | 88.1557 | 87.7631 | 87.3294 | 163.0172 | 162.3362 | 161.3751 | 158.6404 | 155.2109 | 151.9035 | 144.2035 | 140.5898 | 84.6572 | 78.0852 | 77.1263 | 75.3631 | 72.7957 | 145.853 | 142.9962 | 139.8572 | 135.8962 | 132.0688 | 123.2277 | 119.1098 | 115.4172 | 79.7178 | 79.3252 | 78.3031 | 75.7389 | 148.8014 | 145.9498 | 142.8162 | 138.8614 | 135.0404 | 126.213 | 122.1014 | 118.4151
|  | BRIDGE ROAD PRIMARY | CF |  |  |  |  | 88.4463 | 88.2126 | 87.9715 | 163.9151 | 163.6562 | 163.393 | 163.1341 | 162.8783 | 162.6214 | 153.9677 | 150.5951 | 148.4877 | 78.5452 | 78.2978 | 77.9494 | 77.5821 | 153.3846 | 152.833 | 152.0488 | 150.9162 | 149.4214 | 134.3867 | 130.5193 | 128.0962 | 80.0084 | 79.7747 | 79.5336 | 79.2852 | 155.2183 | 154.9551 | 154.6962 | 153.8562 | 152.3635 | 137.3541 | 133.4941 | 131.0751
LOVEDEAN GSP | HAVANT BSP | BROCKHAMPTON PRIMARY | MINIMUM HEADROOM | SU 70868 05828 | NO | YES | 0.21053 | 34.3305 | 34.3011 | 34.2695 | 34.2368 | 34.2032 | 44.5568 | 44.4579 | 44.3674 | 44.2832 | 43.9442 | 43.6895 | 4.1232 | 31.3284 | 31.2989 | 31.2274 | 31.1589 | 31.0884 | 45.2242 | 45.1253 | 45.0347 | 44.9516 | 44.6147 | 44.3632 | 44.1663 | 32.0242 | 31.9947 | 31.9632 | 31.9305 | 31.8968 | 44.4884 | 44.3884 | 44.2979 | 44.2137 | 43.8747 | 43.6211 | 43.4221
|  | BROCKHAMPTON PRIMARY | EE |  |  |  |  | 45.1579 | 45.0758 | 44.9895 | 44.8989 | 44.8042 | 44.7126 | 44.6274 | 44.5432 | 44.4695 | 44.1968 | 44.0105 | 43.8768 | 45.8242 | 45.7421 | 45.6558 | 45.5653 | 45.4716 | 45.38 | 45.2947 | 45.2116 | 45.1389 | 44.8695 | 44.6874 | 44.5568 | 45.0884 | 45.0063 | 44.92 | 44.8295 | 44.7347 | 44.6442 | 44.5579 | 44.4737 | 44.4011 | 44.1284 | 43.9421 | 43.8095
|  | BROCKHAMPTON PRIMARY | HT |  |  |  |  | 45.0989 | 44.9989 | 44.8926 | 44.7842 | 44.6705 | 44.5568 | 44.4579 | 44.3674 | 44.2832 | 43.9442 | 43.6895 | 43.4905 | 45.7653 | 45.6653 | 45.5589 | 45.4505 | 45.3379 | 45.2242 | 45.1253 | 45.0347 | 44.9516 | 44.6147 | 44.3632 | 44.1663 | 45.0295 | 44.9295 | 44.8232 | 44.7147 | 44.6011 | 44.4884 | 44.3884 | 44.2979 | 44.2137 | 43.8747 | 43.6211 | 43.4221
|  | BROCKHAMPTON PRIMARY | HE |  |  |  |  | 45.2358 | 45.1779 | 45.1147 | 45.0463 | 44.9716 | 44.9021 | 44.8358 | 44.7737 | 44.7211 | 44.54 | 44.4337 | 4.1232 | 45.9021 | 45.8442 | 45.7811 | 45.7126 | 45.6389 | 45.5695 | 45.5032 | 45.4411 | 45.3884 | 45.2084 | 45.1042 | 45.04 | 45.1663 | 45.1084 | 45.0453 | 44.9768 | 44.9021 | 44.8326 | 44.7674 | 44.7053 | 44.6516 | 44.4705 | 44.3642 | 44.2989
|  | BROCKHAMPTON PRIMARY | CF |  |  |  |  | 34.3305 | 34.3011 | 34.2695 | 34.2368 | 34.2032 | 45.1274 | 45.0937 | 45.06 | 45.0263 | 44.8768 | 44.8011 | 44.76 | 31.3284 | 31.2989 | 31.2274 | 31.1589 | 31.0884 | 45.7947 | 45.7611 | 45.7274 | 45.6937 | 45.5442 | 45.4695 | 45.4284 | 32.0242 | 31.9947 | 31.9632 | 31.9305 | 31.8968 | 45.0579 | 45.0242 | 44.9905 | 44.9568 | 44.8074 | 44.7316 | 44.6905
LOVEDEAN GSP | FAREHAM (MAIN) BSP | BROCKHURST PRIMARY | MINIMUM HEADROOM | SU 59381 02061 | NO | YES | 0.1 | 34.7882 | 34.5124 | 34.2187 | 33.9134 | 33.5945 | 63.1492 | 61.9861 | 61.0976 | 60.2608 | 56.8818 | 54.8313 | 26.7345 | 31.0366 | 30.2103 | 29.3966 | 28.385 | 27.1829 | 56.2818 | 54.9671 | 53.9703 | 53.0313 | 49.2492 | 46.985 | 44.8734 | 32.0545 | 31.2692 | 30.4934 | 29.4934 | 28.2903 | 57.3882 | 56.0713 | 55.0734 | 54.1334 | 50.3418 | 48.0671 | 45.9524
|  | BROCKHURST PRIMARY | EE |  |  |  |  | 34.9439 | 34.7145 | 34.4692 | 34.2113 | 33.9418 | 63.6776 | 63.4261 | 62.3471 | 61.0808 | 58.0545 | 56.4566 | 55.0324 | 31.4797 | 30.8934 | 30.2997 | 29.5303 | 28.5766 | 57.8124 | 56.6745 | 55.3597 | 53.9134 | 50.5155 | 48.7566 | 47.1629 | 32.4776 | 31.9166 | 31.3482 | 30.6166 | 29.6839 | 58.9187 | 57.7787 | 56.4608 | 55.0134 | 51.6029 | 49.8313 | 48.2324
|  | BROCKHURST PRIMARY | HT |  |  |  |  | 34.7882 | 34.5124 | 34.2187 | 33.9134 | 33.5945 | 63.1492 | 61.9861 | 61.0976 | 60.2608 | 56.8818 | 54.8313 | 52.9387 | 31.0366 | 30.2103 | 29.3966 | 28.385 | 27.1829 | 56.2818 | 54.9671 | 53.9703 | 53.0313 | 49.2492 | 46.985 | 44.8734 | 32.0545 | 31.2692 | 30.4934 | 29.4934 | 28.2903 | 57.3882 | 56.0713 | 55.0734 | 54.1334 | 50.3418 | 48.0671 | 45.9524
|  | BROCKHURST PRIMARY | HE |  |  |  |  | 35.1408 | 34.9692 | 34.7808 | 34.5776 | 34.3587 | 64.1492 | 63.9513 | 63.5029 | 62.4282 | 59.9934 | 58.9608 | 26.7345 | 31.9376 | 31.4818 | 31.0145 | 30.3661 | 29.5113 | 58.8639 | 57.785 | 56.6103 | 55.3787 | 52.6208 | 51.4713 | 50.4418 | 32.8071 | 32.4808 | 32.0345 | 31.4176 | 30.6103 | 59.9713 | 58.8913 | 57.7166 | 56.4839 | 53.7197 | 52.5661 | 51.5324
|  | BROCKHURST PRIMARY | CF |  |  |  |  | 35.2808 | 35.185 | 35.085 | 34.9808 | 34.8724 | 64.7629 | 64.6534 | 64.5461 | 64.4397 | 63.025 | 62.1787 | 61.5513 | 32.1303 | 32.0345 | 31.9018 | 31.7124 | 31.5039 | 61.3145 | 61.0366 | 60.6766 | 60.0418 | 56.0187 | 55.0682 | 54.3587 | 32.9471 | 32.8513 | 32.7513 | 32.6471 | 32.4945 | 62.3103 | 62.0439 | 61.7029 | 61.105 | 57.1229 | 56.1713 | 55.4587
MELKSHAM GSP | NORRINGTON BSP | BROMHAM PRIMARY | MINIMUM HEADROOM | ST 98670 65994 | YES | YES | 0 | 5.9484 | 5.8821 | 5.8116 | 5.74 | 5.5284 | 5.2126 | 4.8347 | 4.7526 | 4.6737 | 3.8705 | 2.8474 | -0.49158 | 4.8737 | 4.7863 | 4.6937 | 4.6011 | 4.3274 | 3.9695 | 3.5358 | 3.46 | 3.3874 | 2.5421 | 1.4305 | 1.1126 | 5.1432 | 5.0589 | 4.9695 | 4.8789 | 4.6084 | 4.2537 | 3.8158 | 3.7347 | 3.6558 | 2.7674 | 1.6074 | 1.2705
|  | BROMHAM PRIMARY | EE |  |  |  |  | 5.9874 | 5.9337 | 5.8747 | 5.8147 | 5.7389 | 5.6589 | 5.5232 | 5.38 | 5.2674 | 4.6621 | 3.7821 | 3.1842 | 4.9295 | 4.8589 | 4.7842 | 4.7084 | 4.6189 | 4.5274 | 4.3526 | 4.2053 | 4.0968 | 3.5116 | 2.6 | 1.9347 | 5.1968 | 5.1274 | 5.0558 | 4.9811 | 4.8916 | 4.7947 | 4.6189 | 4.4663 | 4.3526 | 3.7084 | 2.7284 | 2.0432
|  | BROMHAM PRIMARY | HT |  |  |  |  | 5.9484 | 5.8821 | 5.8116 | 5.74 | 5.5284 | 5.2126 | 4.8347 | 4.7526 | 4.6737 | 3.8705 | 2.8474 | 2.5316 | 4.8737 | 4.7863 | 4.6937 | 4.6011 | 4.3274 | 3.9695 | 3.5358 | 3.46 | 3.3874 | 2.5421 | 1.4305 | 1.1126 | 5.1432 | 5.0589 | 4.9695 | 4.8789 | 4.6084 | 4.2537 | 3.8158 | 3.7347 | 3.6558 | 2.7674 | 1.6074 | 1.2705
|  | BROMHAM PRIMARY | HE |  |  |  |  | 6.04 | 6.0042 | 5.9632 | 5.9189 | 5.8611 | 5.8063 | 5.7537 | 5.7021 | 5.6558 | 5.3221 | 4.8053 | -0.49158 | 4.9968 | 4.9579 | 4.9074 | 4.8537 | 4.7884 | 4.7263 | 4.6653 | 4.5716 | 4.5116 | 4.16 | 3.5853 | 3.0474 | 5.2611 | 5.2232 | 5.1737 | 5.1221 | 5.0547 | 4.9916 | 4.9305 | 4.8389 | 4.7758 | 4.4116 | 3.8189 | 3.2621
|  | BROMHAM PRIMARY | CF |  |  |  |  | 6.0758 | 6.0579 | 6.0389 | 6.0189 | 5.9916 | 5.9663 | 5.94 | 5.9137 | 5.8895 | 5.7716 | 5.5926 | 5.2432 | 5.0326 | 5.0147 | 4.9958 | 4.9716 | 4.9379 | 4.9063 | 4.8737 | 4.8432 | 4.8105 | 4.6589 | 4.4211 | 4.0253 | 5.2968 | 5.2789 | 5.26 | 5.2368 | 5.2042 | 5.1716 | 5.14 | 5.1074 | 5.0768 | 4.9242 | 4.6832 | 4.2821
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | BROOK STREET PRIMARY | MINIMUM HEADROOM | SU 63480 52228 | NO | YES | 0 | 33.6768 | 33.5779 | 33.4726 | 33.3632 | 33.2484 | 33.1316 | 33.0274 | 32.9305 | 32.8411 | 32.4863 | 32.1737 | 10.7895 | 30.8589 | 30.7389 | 30.6126 | 30.4832 | 30.3495 | 30.1979 | 30.0537 | 29.9179 | 29.7895 | 29.2905 | 28.6326 | 27.7463 | 31.4126 | 31.3137 | 31.2084 | 31.1 | 30.9853 | 30.8695 | 30.7653 | 30.6695 | 30.58 | 30.2495 | 29.9211 | 29.0484
|  | BROOK STREET PRIMARY | EE |  |  |  |  | 33.7411 | 33.66 | 33.5758 | 33.4863 | 33.3926 | 33.3011 | 33.2105 | 33.1221 | 33.0442 | 32.7674 | 32.5432 | 32.3526 | 30.9379 | 30.8421 | 30.7411 | 30.6358 | 30.5274 | 30.4211 | 30.3137 | 30.2 | 30.0905 | 29.7147 | 29.32 | 28.7389 | 31.4758 | 31.3958 | 31.3116 | 31.2221 | 31.1284 | 31.0368 | 30.9474 | 30.86 | 30.7821 | 30.5284 | 30.3074 | 30.0295
|  | BROOK STREET PRIMARY | HT |  |  |  |  | 33.6768 | 33.5779 | 33.4726 | 33.3632 | 33.2484 | 33.1316 | 33.0274 | 32.9305 | 32.8411 | 32.4863 | 32.1737 | 31.8705 | 30.8589 | 30.7389 | 30.6126 | 30.4832 | 30.3495 | 30.1979 | 30.0537 | 29.9179 | 29.7895 | 29.2905 | 28.6326 | 27.7463 | 31.4126 | 31.3137 | 31.2084 | 31.1 | 30.9853 | 30.8695 | 30.7653 | 30.6695 | 30.58 | 30.2495 | 29.9211 | 29.0484
|  | BROOK STREET PRIMARY | HE |  |  |  |  | 33.7989 | 33.7358 | 33.6653 | 33.5905 | 33.5095 | 33.4337 | 33.36 | 33.2916 | 33.2326 | 32.9979 | 32.8642 | 10.7895 | 31.0179 | 30.9453 | 30.8642 | 30.78 | 30.6905 | 30.6053 | 30.5221 | 30.4421 | 30.3747 | 30.0547 | 29.8463 | 29.6032 | 31.5337 | 31.4705 | 31.4 | 31.3253 | 31.2453 | 31.1684 | 31.0958 | 31.0274 | 30.9695 | 30.7011 | 30.5684 | 30.4705
|  | BROOK STREET PRIMARY | CF |  |  |  |  | 33.8411 | 33.8011 | 33.76 | 33.7168 | 33.6737 | 33.6284 | 33.5842 | 33.5389 | 33.4958 | 33.2979 | 33.1926 | 33.1284 | 31.0663 | 31.0189 | 30.9705 | 30.92 | 30.8695 | 30.8158 | 30.7632 | 30.7105 | 30.66 | 30.42 | 30.2705 | 30.1253 | 31.5758 | 31.5358 | 31.4947 | 31.4516 | 31.4084 | 31.3632 | 31.3189 | 31.2747 | 31.2316 | 31.0347 | 30.9305 | 30.8663
MELKSHAM GSP | FROME BSP | BRUTON PRIMARY | MINIMUM HEADROOM | ST 69094 35148 | NO | YES | 0 | 8.7558 | 8.6179 | 8.4768 | 8.3368 | 8.0316 | 7.6316 | 7.1579 | 7.0168 | 6.8747 | 5.6221 | 4.0684 | 0.11895 | 7.7095 | 7.5632 | 7.4137 | 7.2642 | 6.9442 | 6.5147 | 5.9989 | 5.8737 | 5.7495 | 4.5347 | 2.9884 | 2.5021 | 8.0947 | 7.9474 | 7.7958 | 7.6463 | 7.3116 | 6.8674 | 6.3358 | 6.1947 | 6.0516 | 4.7137 | 3.0242 | 2.4821
|  | BRUTON PRIMARY | EE |  |  |  |  | 8.8432 | 8.7305 | 8.6126 | 8.4958 | 8.3221 | 8.1368 | 7.9484 | 7.7526 | 7.5558 | 6.4211 | 4.7537 | 3.9021 | 7.8063 | 7.6853 | 7.5611 | 7.4389 | 7.2726 | 7.1 | 6.9253 | 6.7495 | 6.5716 | 5.5716 | 3.9779 | 3.1032 | 8.1905 | 8.0695 | 7.9442 | 7.82 | 7.6389 | 7.4474 | 7.2505 | 7.0495 | 6.8474 | 5.6737 | 3.8811 | 2.9432
|  | BRUTON PRIMARY | HT |  |  |  |  | 8.7558 | 8.6179 | 8.4768 | 8.3368 | 8.0316 | 7.6316 | 7.1579 | 7.0168 | 6.8747 | 5.6221 | 4.0684 | 3.5505 | 7.7095 | 7.5632 | 7.4137 | 7.2642 | 6.9442 | 6.5147 | 5.9989 | 5.8737 | 5.7495 | 4.5347 | 2.9884 | 2.5021 | 8.0947 | 7.9474 | 7.7958 | 7.6463 | 7.3116 | 6.8674 | 6.3358 | 6.1947 | 6.0516 | 4.7137 | 3.0242 | 2.4821
|  | BRUTON PRIMARY | HE |  |  |  |  | 8.9642 | 8.8926 | 8.8179 | 8.7379 | 8.6116 | 8.4979 | 8.3874 | 8.2758 | 8.1716 | 7.6116 | 6.7347 | 0.11895 | 7.9368 | 7.8611 | 7.7811 | 7.6979 | 7.5758 | 7.4684 | 7.3642 | 7.26 | 7.1642 | 6.6526 | 5.7326 | 5.0263 | 8.3221 | 8.2463 | 8.1663 | 8.0821 | 7.9495 | 7.8337 | 7.7189 | 7.6042 | 7.4968 | 6.9137 | 5.9389 | 5.18
|  | BRUTON PRIMARY | CF |  |  |  |  | 9.0337 | 8.9937 | 8.9526 | 8.9084 | 8.8432 | 8.7779 | 8.7116 | 8.6474 | 8.5905 | 8.2747 | 7.9063 | 7.4158 | 8.0116 | 7.9684 | 7.9242 | 7.8758 | 7.8137 | 7.7484 | 7.6842 | 7.6221 | 7.5642 | 7.2547 | 6.8863 | 6.3737 | 8.3968 | 8.3537 | 8.3095 | 8.2611 | 8.1926 | 8.1242 | 8.0547 | 7.9874 | 7.9263 | 7.5926 | 7.1926 | 6.6463
COWLEY GSP | WITNEY BSP | BURFORD PRIMARY | MINIMUM HEADROOM | SP 25671 12529 | NO | YES | 0 | 7.7242 | 7.6758 | 7.6253 | 7.5705 | 7.5137 | 7.4558 | 7.4053 | 7.3589 | 7.3158 | 7.1126 | 6.7695 | -0.032632 | 6.5337 | 6.4547 | 6.3642 | 6.2758 | 6.18 | 6.0853 | 5.9979 | 5.9158 | 5.8379 | 5.4842 | 5.1011 | 4.7137 | 6.7158 | 6.6674 | 6.6095 | 6.5179 | 6.4221 | 6.3274 | 6.2411 | 6.1589 | 6.0811 | 5.7274 | 5.3453 | 4.9579
|  | BURFORD PRIMARY | EE |  |  |  |  | 7.7516 | 7.7105 | 7.6684 | 7.6242 | 7.5779 | 7.5326 | 7.4884 | 7.4453 | 7.4074 | 7.2663 | 7.1084 | 6.8274 | 6.5716 | 6.52 | 6.4558 | 6.3853 | 6.3137 | 6.2453 | 6.1716 | 6.1 | 6.0347 | 5.7611 | 5.4747 | 5.1558 | 6.7432 | 6.7021 | 6.66 | 6.6158 | 6.5589 | 6.4884 | 6.4147 | 6.3421 | 6.2768 | 6.0042 | 5.7179 | 5.3989
|  | BURFORD PRIMARY | HT |  |  |  |  | 7.7242 | 7.6758 | 7.6253 | 7.5705 | 7.5137 | 7.4558 | 7.4053 | 7.3589 | 7.3158 | 7.1126 | 6.7695 | 6.4253 | 6.5337 | 6.4547 | 6.3642 | 6.2758 | 6.18 | 6.0853 | 5.9979 | 5.9158 | 5.8379 | 5.4842 | 5.1011 | 4.7137 | 6.7158 | 6.6674 | 6.6095 | 6.5179 | 6.4221 | 6.3274 | 6.2411 | 6.1589 | 6.0811 | 5.7274 | 5.3453 | 4.9579
|  | BURFORD PRIMARY | HE |  |  |  |  | 7.7884 | 7.76 | 7.7284 | 7.6947 | 7.6589 | 7.6242 | 7.5916 | 7.5611 | 7.5347 | 7.4432 | 7.3821 | -0.032632 | 6.6147 | 6.5842 | 6.5495 | 6.5116 | 6.4705 | 6.4295 | 6.3789 | 6.3316 | 6.2874 | 6.1274 | 5.9337 | 5.7042 | 6.78 | 6.7516 | 6.72 | 6.6863 | 6.6505 | 6.6158 | 6.5832 | 6.5526 | 6.5263 | 6.3695 | 6.1758 | 5.9484
|  | BURFORD PRIMARY | CF |  |  |  |  | 7.8147 | 7.7989 | 7.7832 | 7.7674 | 7.7495 | 7.7326 | 7.7158 | 7.6989 | 7.6821 | 7.6063 | 7.5642 | 7.5347 | 6.6432 | 6.6253 | 6.6084 | 6.5905 | 6.5705 | 6.5495 | 6.5284 | 6.5074 | 6.4853 | 6.3442 | 6.2263 | 6.0821 | 6.8063 | 6.7905 | 6.7747 | 6.7589 | 6.7411 | 6.7242 | 6.7074 | 6.6905 | 6.6737 | 6.5905 | 6.4695 | 6.3253
MANNINGTON GSP | WAREHAM BSP | BUSHEY PRIMARY | MINIMUM HEADROOM | SY 97671 83532 | YES | YES | 0 | 5.0916 | 5.0495 | 4.9295 | 4.8863 | 4.8432 | 4.8011 | 4.7621 | 4.7253 | 4.6916 | 4.5411 | 4.4147 | 2.4021 | 5.1053 | 5.0747 | 4.9505 | 4.9063 | 4.8611 | 4.8158 | 4.7747 | 4.7358 | 4.7 | 4.5379 | 4.4011 | 4.2789 | 4.8705 | 4.8242 | 4.6853 | 4.6379 | 4.5926 | 4.5474 | 4.5053 | 4.4653 | 4.4295 | 4.2653 | 4.1253 | 4.0011
|  | BUSHEY PRIMARY | EE |  |  |  |  | 5.12 | 5.0863 | 4.9758 | 4.94 | 4.9032 | 4.8695 | 4.8368 | 4.8042 | 4.7768 | 4.6589 | 4.5653 | 4.4863 | 5.1211 | 5.0989 | 4.9979 | 4.9611 | 4.9242 | 4.8895 | 4.8547 | 4.8221 | 4.7926 | 4.6653 | 4.5642 | 4.4779 | 4.9011 | 4.8642 | 4.7358 | 4.6968 | 4.6589 | 4.6232 | 4.5874 | 4.5526 | 4.5232 | 4.3947 | 4.2916 | 4.2032
|  | BUSHEY PRIMARY | HT |  |  |  |  | 5.0916 | 5.0495 | 4.9295 | 4.8863 | 4.8432 | 4.8011 | 4.7621 | 4.7253 | 4.6916 | 4.5411 | 4.4147 | 4.3032 | 5.1053 | 5.0747 | 4.9505 | 4.9063 | 4.8611 | 4.8158 | 4.7747 | 4.7358 | 4.7 | 4.5379 | 4.4011 | 4.2789 | 4.8705 | 4.8242 | 4.6853 | 4.6379 | 4.5926 | 4.5474 | 4.5053 | 4.4653 | 4.4295 | 4.2653 | 4.1253 | 4.0011
|  | BUSHEY PRIMARY | HE |  |  |  |  | 5.1589 | 5.1368 | 5.0368 | 5.0137 | 4.9874 | 4.9632 | 4.94 | 4.9189 | 4.8989 | 4.8295 | 4.7789 | 2.4021 | 5.1442 | 5.1284 | 5.0611 | 5.0368 | 5.0105 | 4.9853 | 4.9621 | 4.9411 | 4.9211 | 4.8495 | 4.7968 | 4.7558 | 4.9442 | 4.9211 | 4.8042 | 4.7789 | 4.7516 | 4.7253 | 4.7011 | 4.6789 | 4.6579 | 4.5832 | 4.5284 | 4.4863
|  | BUSHEY PRIMARY | CF |  |  |  |  | 5.1811 | 5.1674 | 5.1221 | 5.1084 | 5.0947 | 5.08 | 5.0653 | 5.0516 | 5.0379 | 4.9747 | 4.9326 | 4.9011 | 5.16 | 5.1505 | 5.1368 | 5.1274 | 5.1189 | 5.1053 | 5.0905 | 5.0758 | 5.0621 | 4.9979 | 4.9547 | 4.9221 | 4.9684 | 4.9537 | 4.9011 | 4.8853 | 4.8705 | 4.8547 | 4.8389 | 4.8242 | 4.8095 | 4.7411 | 4.6937 | 4.6579
FAWLEY GSP | LANGLEY BSP | BUTTS ASH PRIMARY | MINIMUM HEADROOM | SU 41923 05772 | NO | YES | 0 | 31.5874 | 31.1505 | 30.6895 | 30.2168 | 29.7295 | 29.24 | 28.7147 | 28.0926 | 27.5126 | 24.6589 | 21.6926 | -2.1505 | 27.1947 | 26.4421 | 25.6674 | 24.8947 | 24.1242 | 23.3411 | 22.6284 | 21.9632 | 21.3411 | 18.2337 | 14.9316 | 11.7526 | 27.8389 | 27.0842 | 26.3242 | 25.5653 | 24.8084 | 24.0453 | 23.3547 | 22.7084 | 22.1 | 18.9853 | 15.6737 | 12.4905
|  | BUTTS ASH PRIMARY | EE |  |  |  |  | 31.8505 | 31.4937 | 31.1147 | 30.7232 | 30.3168 | 29.9232 | 29.5484 | 29.1895 | 28.8674 | 26.7947 | 24.5105 | 22.3684 | 27.6989 | 27.1211 | 26.5221 | 25.8968 | 25.2663 | 24.6505 | 24.0621 | 23.4947 | 22.9674 | 20.5737 | 18.0284 | 15.6032 | 28.36 | 27.7674 | 27.1579 | 26.5453 | 25.9242 | 25.3179 | 24.7379 | 24.1811 | 23.6674 | 21.32 | 18.7642 | 16.3347
|  | BUTTS ASH PRIMARY | HT |  |  |  |  | 31.5874 | 31.1505 | 30.6895 | 30.2168 | 29.7295 | 29.24 | 28.7147 | 28.0926 | 27.5126 | 24.6589 | 21.6926 | 18.8695 | 27.1947 | 26.4421 | 25.6674 | 24.8947 | 24.1242 | 23.3411 | 22.6284 | 21.9632 | 21.3411 | 18.2337 | 14.9316 | 11.7526 | 27.8389 | 27.0842 | 26.3242 | 25.5653 | 24.8084 | 24.0453 | 23.3547 | 22.7084 | 22.1 | 18.9853 | 15.6737 | 12.4905
|  | BUTTS ASH PRIMARY | HE |  |  |  |  | 32.1979 | 31.9495 | 31.6747 | 31.3811 | 31.0674 | 30.7653 | 30.4811 | 30.2147 | 29.9842 | 29.1779 | 28.0895 | -2.1505 | 28.3568 | 27.9832 | 27.5842 | 27.1705 | 26.7347 | 26.3126 | 25.9105 | 25.52 | 25.1726 | 23.6516 | 21.9189 | 20.24 | 28.8474 | 28.6 | 28.2495 | 27.8263 | 27.3821 | 26.9526 | 26.5453 | 26.16 | 25.8179 | 24.3263 | 22.6726 | 20.9895
|  | BUTTS ASH PRIMARY | CF |  |  |  |  | 32.4316 | 32.3 | 32.1632 | 32.02 | 31.8737 | 31.7221 | 31.5747 | 31.4274 | 31.2811 | 30.6242 | 30.2568 | 29.6411 | 28.7316 | 28.5105 | 28.2821 | 28.0484 | 27.8105 | 27.5653 | 27.3274 | 27.0884 | 26.8495 | 25.7284 | 24.6284 | 23.5021 | 29.08 | 28.9495 | 28.8126 | 28.6716 | 28.4768 | 28.2253 | 27.9821 | 27.7358 | 27.4905 | 26.3779 | 25.3116 | 24.2505
MELKSHAM GSP | CHIPPENHAM BSP | CALNE PRIMARY | MINIMUM HEADROOM | SU 00521 72497 | NO | YES | 0 | 20.7495 | 20.1168 | 19.5095 | 18.4705 | 17.2179 | 16.0611 | 15.2116 | 14.3768 | 13.5358 | 10.6421 | 8.4663 | -7.8684 | 19.5937 | 18.9526 | 18.3368 | 17.1558 | 15.6937 | 14.32 | 13.3295 | 12.3484 | 11.3537 | 7.9958 | 4.7242 | 0.94632 | 20.3705 | 19.8442 | 19.1916 | 18.0274 | 16.6116 | 15.2389 | 14.2484 | 13.2674 | 12.2716 | 8.9053 | 5.3758 | 1.8463
|  | CALNE PRIMARY | EE |  |  |  |  | 21.0547 | 20.6453 | 20.1063 | 20.8758 | 19.8779 | 18.9589 | 18.1453 | 17.1421 | 17.6084 | 15.3168 | 15.7526 | 13.2947 | 19.9021 | 19.4884 | 18.9432 | 18.2137 | 17.0989 | 16.0768 | 15.1768 | 14.0505 | 15.3589 | 12.9526 | 14.6232 | 11.8263 | 20.6284 | 20.2716 | 19.8347 | 19.1295 | 18.0147 | 16.9926 | 16.0916 | 14.9642 | 16.5305 | 14.0137 | 16.3432 | 13.5421
|  | CALNE PRIMARY | HT |  |  |  |  | 20.7495 | 20.1168 | 19.5095 | 18.4705 | 17.2179 | 16.0611 | 15.2116 | 14.3768 | 13.5358 | 10.6421 | 8.4663 | 5.3663 | 19.5937 | 18.9526 | 18.3368 | 17.1558 | 15.6937 | 14.32 | 13.3295 | 12.3484 | 11.3537 | 7.9958 | 4.7242 | 0.94632 | 20.3705 | 19.8442 | 19.1916 | 18.0274 | 16.6116 | 15.2389 | 14.2484 | 13.2674 | 12.2716 | 8.9053 | 5.3758 | 1.8463
|  | CALNE PRIMARY | HE |  |  |  |  | 21.3811 | 21.1653 | 20.9021 | 20.3263 | 19.4968 | 18.7579 | 18.1 | 17.2947 | 16.3758 | 14.8653 | 18.3211 | -7.8684 | 20.2305 | 20.0147 | 19.7505 | 19.1642 | 18.2821 | 17.4242 | 16.6653 | 15.7063 | 14.5821 | 12.8347 | 10.9726 | 8.8589 | 20.9295 | 20.7189 | 20.4716 | 20.04 | 19.1316 | 18.3 | 17.5621 | 16.6221 | 15.4989 | 13.7453 | 16.0358 | 13.9611
|  | CALNE PRIMARY | CF |  |  |  |  | 21.5674 | 21.46 | 21.3474 | 21.2147 | 21.0642 | 20.9126 | 20.6611 | 20.3779 | 19.9021 | 17.8326 | 16.8474 | 15.7453 | 20.4168 | 20.3095 | 20.1968 | 20.0632 | 19.9137 | 19.76 | 19.5053 | 19.2189 | 18.7316 | 16.3 | 15.1168 | 13.7484 | 21.1158 | 21.0084 | 20.8958 | 20.7695 | 20.6316 | 20.4916 | 20.2968 | 20.0832 | 19.58 | 17.2158 | 16.0295 | 14.66
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY PRIMARY | MINIMUM HEADROOM | SU 86584 59452 | NO | YES | 0 | 86.4669 | 86.1259 | 85.7627 | 85.3869 | 85.0006 | 84.6112 | 84.2701 | 83.9606 | 83.6743 | 81.7627 | 79.2048 | 35.568 | 78.2238 | 77.5038 | 76.8427 | 76.1796 | 75.5227 | 74.8764 | 74.2859 | 73.7364 | 73.2164 | 70.5796 | 67.7059 | 65.1143 | 80.1912 | 79.6206 | 78.9712 | 78.3175 | 77.6606 | 77.0143 | 76.4238 | 75.8733 | 75.3533 | 72.7154 | 69.8406 | 67.248
|  | CAMBERLEY PRIMARY | EE |  |  |  |  | 86.6754 | 86.3975 | 86.1006 | 85.7922 | 85.4712 | 85.1617 | 84.868 | 84.5869 | 84.3354 | 83.4227 | 81.6069 | 79.8827 | 78.6691 | 78.0848 | 77.5554 | 77.0217 | 76.4848 | 75.9712 | 75.4817 | 75.0048 | 74.5712 | 72.5459 | 70.3333 | 68.3796 | 80.3996 | 80.1217 | 79.6701 | 79.1448 | 78.6154 | 78.1091 | 77.6206 | 77.1427 | 76.7091 | 74.6827 | 72.468 | 70.5143
|  | CAMBERLEY PRIMARY | HT |  |  |  |  | 86.4669 | 86.1259 | 85.7627 | 85.3869 | 85.0006 | 84.6112 | 84.2701 | 83.9606 | 83.6743 | 81.7627 | 79.2048 | 76.8964 | 78.2238 | 77.5038 | 76.8427 | 76.1796 | 75.5227 | 74.8764 | 74.2859 | 73.7364 | 73.2164 | 70.5796 | 67.7059 | 65.1143 | 80.1912 | 79.6206 | 78.9712 | 78.3175 | 77.6606 | 77.0143 | 76.4238 | 75.8733 | 75.3533 | 72.7154 | 69.8406 | 67.248
|  | CAMBERLEY PRIMARY | HE |  |  |  |  | 86.9364 | 86.7385 | 86.5196 | 86.2838 | 86.0333 | 85.7912 | 85.5638 | 85.3522 | 85.1691 | 84.5543 | 84.1943 | 35.568 | 79.1764 | 78.8438 | 78.488 | 78.1143 | 77.7312 | 77.3669 | 77.0217 | 76.6922 | 76.4027 | 75.0806 | 73.5217 | 72.1912 | 80.6606 | 80.4627 | 80.2438 | 80.008 | 79.7575 | 79.4764 | 79.1354 | 78.8101 | 78.5248 | 77.2175 | 75.6596 | 74.3269
|  | CAMBERLEY PRIMARY | CF |  |  |  |  | 86.7754 | 86.6691 | 86.5585 | 86.4448 | 86.3269 | 86.2059 | 86.088 | 85.9691 | 85.8512 | 85.6691 | 85.408 | 85.2648 | 78.9175 | 78.8059 | 78.6712 | 78.4585 | 78.2396 | 78.0059 | 77.7912 | 77.5722 | 77.3554 | 76.8091 | 75.7248 | 74.7985 | 80.4627 | 80.3564 | 80.2459 | 80.1322 | 80.0143 | 79.8933 | 79.7754 | 79.6564 | 79.4985 | 78.9343 | 77.8617 | 76.9354
WILLESDEN GSP |  | CANAL BANK 11KV PRIMARY | MINIMUM HEADROOM | TQ 20927 83082 | NO | NO | 0 | 71.1821 | 70.38 | 68.6916 | 66.7221 | 64.1 | 61.5916 | 59.3126 | 59.2895 | 59.2695 | 56.7937 | 52.4211 | -9.9579 | 62.8474 | 61.3905 | 59.5926 | 57.4947 | 54.7021 | 51.9179 | 49.2274 | 49.2042 | 49.1842 | 46.2211 | 41.1137 | 36.6137 | 65.2905 | 64.5916 | 62.8989 | 60.8263 | 57.8474 | 54.9411 | 52.2558 | 52.2326 | 52.2126 | 49.2558 | 44.1484 | 39.6758
|  | CANAL BANK 11KV PRIMARY | EE |  |  |  |  | 71.1979 | 71.1474 | 69.8568 | 68.0874 | 65.8358 | 63.8326 | 61.7274 | 61.7074 | 61.6895 | 56.8379 | 52.6905 | 49.2042 | 63.1958 | 62.2063 | 60.8326 | 58.9474 | 56.5505 | 54.4168 | 52.0737 | 52.0537 | 52.0358 | 46.2811 | 41.4611 | 37.3653 | 65.3316 | 65.2442 | 64.0674 | 62.2926 | 59.8168 | 57.5421 | 55.0979 | 55.0779 | 55.06 | 49.3158 | 44.5147 | 40.4263
|  | CANAL BANK 11KV PRIMARY | HT |  |  |  |  | 71.1821 | 70.38 | 68.6916 | 66.7221 | 64.1 | 61.5916 | 59.3126 | 59.2895 | 59.2695 | 57.1442 | 52.4211 | 48.5484 | 62.8474 | 61.3905 | 59.5926 | 57.4947 | 54.7021 | 51.9179 | 49.2274 | 49.2042 | 49.1842 | 46.7042 | 41.16 | 36.6137 | 65.2905 | 64.5916 | 62.8989 | 60.8263 | 57.8474 | 54.9411 | 52.2558 | 52.2326 | 52.2126 | 49.7474 | 44.2137 | 39.6758
|  | CANAL BANK 11KV PRIMARY | HE |  |  |  |  | 71.2074 | 71.1505 | 69.8463 | 68.0832 | 65.8095 | 63.7947 | 61.6063 | 61.5905 | 61.5768 | 56.7937 | 52.4916 | -9.9579 | 63.2158 | 62.2084 | 60.82 | 58.9421 | 56.5211 | 54.3758 | 51.9274 | 51.9116 | 51.8979 | 46.2211 | 41.1137 | 37.0758 | 65.3421 | 65.2547 | 64.0558 | 62.2884 | 59.7853 | 57.4968 | 54.9516 | 54.9358 | 54.9221 | 49.2558 | 44.1484 | 40.1179
|  | CANAL BANK 11KV PRIMARY | CF |  |  |  |  | 71.2158 | 71.2063 | 71.1958 | 71.1853 | 71.1737 | 71.1621 | 70.9705 | 69.6832 | 68.0747 | 57.7421 | 54.4011 | 51.8516 | 63.6432 | 63.5989 | 63.5316 | 63.4389 | 63.26 | 62.8168 | 62.0189 | 60.6495 | 58.9358 | 47.3611 | 43.4 | 40.4032 | 65.4211 | 65.4021 | 65.3811 | 65.3558 | 65.3147 | 65.2695 | 65.1832 | 63.8937 | 62.2811 | 50.3937 | 46.44 | 43.4484
COWLEY GSP | WITNEY BSP | CARTERTON PRIMARY | MINIMUM HEADROOM | SP 28261 07823 | NO | YES | 0.14737 | 35.9611 | 35.2063 | 34.4863 | 33.7484 | 33.0884 | 32.5474 | 32.0516 | 31.5916 | 31.1579 | 29.0737 | 26.6105 | 0.82737 | 32.5726 | 31.5421 | 30.7526 | 29.9905 | 29.2737 | 28.6947 | 28.1632 | 27.6695 | 27.2032 | 24.9611 | 22.1947 | 19.2463 | 33.0726 | 32.0337 | 31.2389 | 30.4253 | 29.7063 | 29.1274 | 28.5947 | 28.1011 | 27.6326 | 25.3547 | 22.5853 | 19.64
|  | CARTERTON PRIMARY | EE |  |  |  |  | 36.4716 | 35.6474 | 35.0305 | 34.3947 | 33.8316 | 33.4 | 32.9821 | 32.5747 | 32.1916 | 30.6168 | 28.7589 | 26.7253 | 32.9411 | 32.02 | 31.3432 | 30.6958 | 30.0842 | 29.6242 | 29.1789 | 28.7432 | 28.3337 | 26.6316 | 24.5547 | 22.2316 | 33.4442 | 32.5158 | 31.8326 | 31.1305 | 30.5168 | 30.0558 | 29.6084 | 29.1716 | 28.76 | 27.0495 | 24.96 | 22.6316
|  | CARTERTON PRIMARY | HT |  |  |  |  | 36.1316 | 35.2063 | 34.4863 | 33.7484 | 33.0884 | 32.5474 | 32.0516 | 31.5916 | 31.1579 | 29.0737 | 26.6105 | 24.0242 | 32.5726 | 31.5421 | 30.7526 | 29.9905 | 29.2737 | 28.6947 | 28.1632 | 27.6695 | 27.2032 | 24.9611 | 22.1947 | 19.2463 | 33.0726 | 32.0337 | 31.2389 | 30.4253 | 29.7063 | 29.1274 | 28.5947 | 28.1011 | 27.6326 | 25.3547 | 22.5853 | 19.64
|  | CARTERTON PRIMARY | HE |  |  |  |  | 36.9305 | 36.2484 | 35.7705 | 35.2632 | 34.82 | 34.5095 | 34.2084 | 33.9211 | 33.6558 | 32.6568 | 31.3305 | 0.82737 | 33.4389 | 32.6716 | 32.1463 | 31.5884 | 31.1084 | 30.8326 | 30.5147 | 30.2084 | 29.9263 | 28.8484 | 27.3453 | 25.56 | 33.9453 | 33.1705 | 32.6421 | 32.08 | 31.5958 | 31.2663 | 30.9474 | 30.6411 | 30.3568 | 29.2758 | 27.7684 | 25.9789
|  | CARTERTON PRIMARY | CF |  |  |  |  | 35.9611 | 37.2726 | 37.0242 | 36.7505 | 36.5137 | 36.3158 | 36.1442 | 35.9716 | 35.7979 | 34.9516 | 34.1768 | 33.1916 | 34.2221 | 33.8274 | 33.5526 | 33.2495 | 32.9916 | 32.7779 | 32.5937 | 32.4116 | 32.2253 | 31.3147 | 30.4495 | 29.3653 | 34.7305 | 34.3379 | 34.0611 | 33.7558 | 33.4947 | 33.2789 | 33.0958 | 32.9105 | 32.7242 | 31.8063 | 30.9316 | 29.7926
AXMINSTER GSP | YEOVIL BSP | CASTLE CARY PRIMARY | MINIMUM HEADROOM | ST 64534 31039 | NO | YES | 0 | 15.3989 | 15.2874 | 15.0137 | 14.6684 | 14.2947 | 14.1011 | 13.9432 | 13.7947 | 13.6621 | 12.98 | 12.3832 | 5.0011 | 14.4611 | 14.1442 | 13.7916 | 13.4042 | 12.9842 | 12.7758 | 12.6074 | 12.4495 | 12.3084 | 11.5653 | 10.9095 | 10.2547 | 14.5305 | 14.2284 | 13.8758 | 13.4884 | 13.0684 | 12.8611 | 12.6916 | 12.5337 | 12.3916 | 11.6474 | 10.9905 | 10.3347
|  | CASTLE CARY PRIMARY | EE |  |  |  |  | 15.4589 | 15.3653 | 15.1947 | 14.8811 | 14.5379 | 14.3779 | 14.2432 | 14.1158 | 14.0042 | 13.4747 | 13.0337 | 12.5958 | 14.5832 | 14.3042 | 13.9884 | 13.6368 | 13.2505 | 13.0768 | 12.9347 | 12.8011 | 12.6821 | 12.1074 | 11.6242 | 11.1358 | 14.6495 | 14.3853 | 14.0726 | 13.72 | 13.3326 | 13.16 | 13.0179 | 12.8811 | 12.7621 | 12.1874 | 11.7 | 11.2105
|  | CASTLE CARY PRIMARY | HT |  |  |  |  | 15.3989 | 15.2874 | 15.0137 | 14.6684 | 14.2947 | 14.1011 | 13.9432 | 13.7947 | 13.6621 | 12.98 | 12.3832 | 11.7958 | 14.4611 | 14.1442 | 13.7916 | 13.4042 | 12.9842 | 12.7758 | 12.6074 | 12.4495 | 12.3084 | 11.5653 | 10.9095 | 10.2547 | 14.5305 | 14.2284 | 13.8758 | 13.4884 | 13.0684 | 12.8611 | 12.6916 | 12.5337 | 12.3916 | 11.6474 | 10.9905 | 10.3347
|  | CASTLE CARY PRIMARY | HE |  |  |  |  | 15.5411 | 15.4737 | 15.3958 | 15.1726 | 14.8705 | 14.7505 | 14.6558 | 14.5674 | 14.4926 | 14.1516 | 13.8863 | 5.0011 | 14.7358 | 14.5242 | 14.2568 | 13.9526 | 13.6105 | 13.4811 | 13.3821 | 13.2874 | 13.2095 | 12.8411 | 12.5463 | 12.2379 | 14.7958 | 14.5968 | 14.3421 | 14.0368 | 13.6947 | 13.5663 | 13.4663 | 13.3726 | 13.2947 | 12.9242 | 12.6316 | 12.3211
|  | CASTLE CARY PRIMARY | CF |  |  |  |  | 15.5926 | 15.5611 | 15.5221 | 15.4832 | 15.4411 | 15.4042 | 15.3579 | 15.3 | 15.2421 | 14.9684 | 14.7611 | 14.5579 | 14.7874 | 14.7274 | 14.5968 | 14.4547 | 14.3 | 14.2242 | 14.1621 | 14.1 | 14.0379 | 13.7421 | 13.5126 | 13.2821 | 14.8474 | 14.7895 | 14.6663 | 14.5337 | 14.3853 | 14.3095 | 14.2474 | 14.1842 | 14.1232 | 13.8263 | 13.5958 | 13.3653
LALEHAM GSP | STAINES BSP | CAUSEWAY PRIMARY | MINIMUM HEADROOM | TQ 02763 71680 | NO | YES | 0 | 58.7242 | 58.4821 | 58.2242 | 57.9579 | 57.4674 | 56.4432 | 55.4642 | 54.5021 | 52.8263 | 50.8074 | 49.0168 | 23.0284 | 54.9032 | 53.8326 | 53.1832 | 52.0916 | 51.0305 | 49.8758 | 48.7695 | 47.6779 | 45.7463 | 43.5189 | 41.5242 | 39.6958 | 56.0737 | 55.3821 | 54.7463 | 53.7158 | 52.7116 | 51.6221 | 50.5779 | 49.5253 | 47.5926 | 45.3653 | 43.3695 | 41.5411
|  | CAUSEWAY PRIMARY | EE |  |  |  |  | 58.8705 | 58.6705 | 58.46 | 58.2389 | 58.0095 | 57.1874 | 56.2853 | 55.3853 | 53.7758 | 52.1516 | 50.7547 | 49.4989 | 55.1968 | 53.8326 | 53.6221 | 52.6853 | 51.7242 | 50.6842 | 49.66 | 48.64 | 46.78 | 44.9874 | 43.4242 | 42.0074 | 56.22 | 55.3821 | 55.1716 | 54.2863 | 53.3789 | 52.3979 | 51.4337 | 50.4726 | 48.6274 | 46.8347 | 45.2705 | 43.8526
|  | CAUSEWAY PRIMARY | HT |  |  |  |  | 58.7242 | 58.4821 | 58.2242 | 57.9579 | 57.4674 | 56.4432 | 55.4642 | 54.5021 | 52.8263 | 50.8074 | 49.0168 | 47.3874 | 54.9032 | 54.1779 | 53.1832 | 52.0916 | 51.0305 | 49.8758 | 48.7695 | 47.6779 | 45.7463 | 43.5189 | 41.5242 | 39.6958 | 56.0737 | 55.6884 | 54.7463 | 53.7158 | 52.7116 | 51.6221 | 50.5779 | 49.5253 | 47.5926 | 45.3653 | 43.3695 | 41.5411
|  | CAUSEWAY PRIMARY | HE |  |  |  |  | 59.0547 | 58.9126 | 58.7547 | 58.5853 | 58.4053 | 58.0958 | 57.2863 | 56.4916 | 54.98 | 53.8253 | 52.8568 | 23.0284 | 55.58 | 55.0621 | 54.3463 | 53.4621 | 52.6084 | 51.6726 | 50.7505 | 49.8442 | 48.0926 | 46.8137 | 45.7211 | 44.7516 | 56.4042 | 56.2621 | 55.8642 | 55.0316 | 54.2274 | 53.3463 | 52.48 | 51.6295 | 49.94 | 48.6611 | 47.5674 | 46.5979
|  | CAUSEWAY PRIMARY | CF |  |  |  |  | 59.1811 | 59.1042 | 59.0242 | 58.9421 | 58.8579 | 58.7705 | 58.6853 | 58.6 | 58.2495 | 57.3768 | 56.7105 | 56.16 | 55.8116 | 55.6453 | 55.4158 | 55.0979 | 54.6432 | 54.0705 | 53.4989 | 52.9453 | 51.8032 | 50.8442 | 50.0958 | 49.4663 | 56.5305 | 56.4537 | 56.3737 | 56.2916 | 56.1579 | 55.6095 | 55.0737 | 54.5537 | 53.4895 | 52.5726 | 51.8642 | 51.2737
FLEET-BRAMLEY GSP | READING TOWN BSP | CAVERSHAM PRIMARY | MINIMUM HEADROOM | SU 71512 75747 | NO | YES | 0 | 32.6653 | 32.2747 | 31.6126 | 30.9042 | 30.1789 | 29.4516 | 28.7895 | 28.1726 | 27.5947 | 25.0663 | 22.5 | 4.4558 | 28.9074 | 28.1758 | 27.42 | 26.6632 | 25.8884 | 25.1105 | 24.4032 | 23.74 | 23.1179 | 20.3789 | 17.5358 | 14.8874 | 29.6811 | 28.9747 | 28.2337 | 27.4768 | 26.7021 | 25.9242 | 25.2158 | 24.5516 | 23.9295 | 21.1895 | 18.3453 | 15.6958
|  | CAVERSHAM PRIMARY | EE |  |  |  |  | 32.9032 | 32.5853 | 32.2474 | 31.7905 | 31.1989 | 30.6242 | 30.0726 | 29.5274 | 29.0337 | 27.1053 | 25.1779 | 23.3905 | 29.4168 | 28.8389 | 28.2358 | 27.6232 | 26.9916 | 26.3779 | 25.7905 | 25.2053 | 24.6747 | 22.5926 | 20.4516 | 18.4432 | 30.1705 | 29.6116 | 29.0274 | 28.4337 | 27.8063 | 27.1926 | 26.6032 | 26.0189 | 25.4884 | 23.4042 | 21.2621 | 19.2516
|  | CAVERSHAM PRIMARY | HT |  |  |  |  | 32.6653 | 32.2747 | 31.6126 | 30.9042 | 30.1789 | 29.4516 | 28.7895 | 28.1726 | 27.5947 | 25.0663 | 22.5 | 20.1295 | 28.9074 | 28.1758 | 27.42 | 26.6632 | 25.8884 | 25.1105 | 24.4032 | 23.74 | 23.1179 | 20.3789 | 17.5358 | 14.8874 | 29.6811 | 28.9747 | 28.2337 | 27.4768 | 26.7021 | 25.9242 | 25.2158 | 24.5516 | 23.9295 | 21.1895 | 18.3453 | 15.6958
|  | CAVERSHAM PRIMARY | HE |  |  |  |  | 33.2063 | 32.9821 | 32.7347 | 32.4674 | 32.1832 | 31.9095 | 31.6537 | 31.3105 | 30.9674 | 29.7684 | 28.5074 | 4.4558 | 30.0853 | 29.7137 | 29.3063 | 28.8811 | 28.4263 | 27.98 | 27.5537 | 27.1432 | 26.7779 | 25.4895 | 24.08 | 22.7695 | 30.7579 | 30.4505 | 30.0558 | 29.6421 | 29.1989 | 28.7663 | 28.3516 | 27.9537 | 27.5905 | 26.3042 | 24.8926 | 23.5811
|  | CAVERSHAM PRIMARY | CF |  |  |  |  | 33.4116 | 33.2926 | 33.1684 | 33.0411 | 32.9084 | 32.7737 | 32.64 | 32.5084 | 32.3768 | 31.5063 | 30.6379 | 29.8379 | 30.4442 | 30.2179 | 29.9789 | 29.7347 | 29.4842 | 29.2326 | 28.98 | 28.7253 | 28.4726 | 27.3084 | 26.34 | 25.4263 | 30.9726 | 30.8474 | 30.7105 | 30.4747 | 30.2337 | 29.9895 | 29.7463 | 29.5 | 29.2558 | 28.1221 | 27.1526 | 26.24
MANNINGTON GSP | BOURNEMOUTH BSP | CENTRAL PRIMARY | MINIMUM HEADROOM | SZ 10293 91931 | NO | YES | 0 | 37.7347 | 37.3726 | 36.9884 | 36.5789 | 36.1505 | 35.7158 | 35.3232 | 34.6453 | 33.7695 | 29.7084 | 25.7695 | -9.9947 | 30.94 | 30.0811 | 29.3705 | 28.6421 | 27.8863 | 26.9968 | 26.0863 | 25.0926 | 24.1211 | 19.5989 | 15.1695 | 10.8789 | 31.9032 | 31.5032 | 31.04 | 30.36 | 29.6537 | 28.7653 | 27.8537 | 26.8611 | 25.8916 | 21.3747 | 16.9505 | 12.6642
|  | CENTRAL PRIMARY | EE |  |  |  |  | 37.9853 | 37.7011 | 37.3989 | 37.0726 | 36.7274 | 36.3905 | 36.06 | 35.7358 | 35.4421 | 32.5095 | 29.4168 | 26.5042 | 31.2011 | 30.7284 | 30.1758 | 29.5989 | 29.0158 | 28.3337 | 27.6547 | 26.9874 | 26.2021 | 22.6947 | 19.2063 | 15.8937 | 32.1684 | 31.8505 | 31.5337 | 31.1926 | 30.7 | 30.0695 | 29.4211 | 28.7547 | 27.9705 | 24.4663 | 20.9811 | 17.6716
|  | CENTRAL PRIMARY | HT |  |  |  |  | 37.7347 | 37.3726 | 36.9884 | 36.5789 | 36.1505 | 35.7158 | 35.3232 | 34.6453 | 33.7695 | 29.7084 | 25.7695 | 21.9789 | 30.94 | 30.0811 | 29.3705 | 28.6421 | 27.8863 | 26.9968 | 26.0863 | 25.0926 | 24.1211 | 19.5989 | 15.1695 | 10.8789 | 31.9032 | 31.5032 | 31.04 | 30.36 | 29.6537 | 28.7653 | 27.8537 | 26.8611 | 25.8916 | 21.3747 | 16.9505 | 12.6642
|  | CENTRAL PRIMARY | HE |  |  |  |  | 38.1484 | 37.9042 | 37.6337 | 37.3432 | 37.0337 | 36.7368 | 36.4579 | 36.1968 | 35.9726 | 34.7368 | 32.4505 | -9.9947 | 31.3789 | 31.1137 | 30.8368 | 30.5011 | 30.0463 | 29.4968 | 28.98 | 28.4505 | 27.8232 | 25.1621 | 22.5621 | 20.1568 | 32.3505 | 32.0779 | 31.7989 | 31.5 | 31.1821 | 30.8705 | 30.5779 | 30.1389 | 29.5726 | 26.9316 | 24.3347 | 21.9337
|  | CENTRAL PRIMARY | CF |  |  |  |  | 38.2884 | 38.1305 | 37.9653 | 37.7958 | 37.62 | 37.44 | 37.2632 | 37.0884 | 36.9137 | 36.1347 | 35.7295 | 34.3421 | 31.5232 | 31.3537 | 31.1832 | 31.0095 | 30.8263 | 30.6095 | 30.1947 | 29.8232 | 29.4747 | 27.9905 | 26.2316 | 24.6379 | 32.4958 | 32.3221 | 32.1505 | 31.9747 | 31.7895 | 31.5968 | 31.4063 | 31.22 | 31.0358 | 29.7389 | 28 | 26.4095
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CENTRAL BRIDGE PRIMARY | MINIMUM HEADROOM | SU 42591 11255 | NO | YES | 0 | 43.9924 | 43.8998 | 43.7945 | 43.6514 | 41.2229 | 38.8829 | 37.3545 | 36.3482 | 35.2493 | 34.0251 | 32.9756 | -14.176 | 38.8261 | 38.5135 | 38.1219 | 37.6587 | 34.8156 | 32.1198 | 30.3629 | 29.2114 | 27.9503 | 26.5935 | 25.4272 | 24.3124 | 40.2935 | 40.0124 | 39.6377 | 39.1619 | 36.2714 | 33.5303 | 31.7451 | 30.5745 | 29.2935 | 27.9187 | 26.7377 | 25.6082
|  | CENTRAL BRIDGE PRIMARY | EE |  |  |  |  | 44.0672 | 43.9977 | 43.9251 | 43.8135 | 43.5135 | 43.064 | 40.6398 | 38.344 | 36.8135 | 34.764 | 33.9429 | 33.1777 | 38.9377 | 38.6808 | 38.3408 | 37.9429 | 37.444 | 36.9356 | 34.1251 | 31.4261 | 29.7251 | 27.3945 | 26.4777 | 25.6187 | 40.404 | 40.1756 | 39.8514 | 39.4493 | 38.9429 | 38.4272 | 35.5819 | 32.8882 | 31.0945 | 28.7282 | 27.7998 | 26.9282
|  | CENTRAL BRIDGE PRIMARY | HT |  |  |  |  | 43.9924 | 43.8998 | 43.7945 | 43.6514 | 41.2229 | 38.8829 | 37.3545 | 36.3482 | 35.2493 | 34.0251 | 32.9756 | 31.9798 | 38.8261 | 38.5135 | 38.1219 | 37.6587 | 34.8156 | 32.1198 | 30.3629 | 29.2114 | 27.9503 | 26.5935 | 25.4272 | 24.3124 | 40.2935 | 40.0124 | 39.6377 | 39.1619 | 36.2714 | 33.5303 | 31.7451 | 30.5745 | 29.2935 | 27.9187 | 26.7377 | 25.6082
|  | CENTRAL BRIDGE PRIMARY | HE |  |  |  |  | 44.0956 | 44.0324 | 43.9619 | 43.8703 | 43.7093 | 45.2872 | 44.9766 | 40.0103 | 38.6703 | 35.7429 | 34.8187 | -14.176 | 39.0082 | 38.8093 | 38.4945 | 38.1345 | 37.664 | 37.2482 | 35.2977 | 33.4093 | 31.8629 | 28.5029 | 27.4524 | 26.8366 | 40.4808 | 40.2945 | 39.9987 | 39.644 | 39.1661 | 40.6987 | 36.9187 | 34.8398 | 33.2682 | 29.8524 | 28.7861 | 28.1608
|  | CENTRAL BRIDGE PRIMARY | CF |  |  |  |  | 44.1229 | 44.0787 | 44.0324 | 43.9851 | 43.9366 | 43.8861 | 43.8303 | 43.1503 | 41.9082 | 39.6166 | 40.8545 | 40.4945 | 39.344 | 39.2324 | 39.1114 | 38.9724 | 38.7998 | 38.5072 | 38.1661 | 37.0177 | 35.5851 | 32.9282 | 35.1282 | 34.7156 | 40.8461 | 40.7408 | 40.6093 | 40.4566 | 40.2661 | 40.0051 | 39.6819 | 38.5093 | 37.0524 | 34.3872 | 36.9756 | 36.564
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS PRIMARY | MINIMUM HEADROOM | ST 66140 01039 | YES | YES | 0 | 4.4084 | 4.3747 | 4.34 | 4.3063 | 4.2716 | 4.2379 | 4.2074 | 4.1789 | 4.1516 | 4.0305 | 3.9295 | 1.8084 | 3.9295 | 3.8968 | 3.8632 | 3.8305 | 3.7958 | 3.7632 | 3.7326 | 3.7053 | 3.6789 | 3.5653 | 3.4705 | 3.3884 | 3.9568 | 3.9347 | 3.9116 | 3.8884 | 3.8632 | 3.8389 | 3.8168 | 3.7979 | 3.7789 | 3.7042 | 3.5958 | 3.5
|  | CERNE ABBAS PRIMARY | EE |  |  |  |  | 4.4305 | 4.4032 | 4.3758 | 4.3474 | 4.32 | 4.2926 | 4.2674 | 4.2421 | 4.22 | 4.1274 | 4.0526 | 3.9905 | 3.9516 | 3.9253 | 3.8979 | 3.8705 | 3.8432 | 3.8158 | 3.7916 | 3.7663 | 3.7442 | 3.6558 | 3.5853 | 3.5284 | 3.9705 | 3.9516 | 3.9316 | 3.9126 | 3.8926 | 3.8716 | 3.8537 | 3.8358 | 3.8189 | 3.7589 | 3.7179 | 3.6621
|  | CERNE ABBAS PRIMARY | HT |  |  |  |  | 4.4084 | 4.3747 | 4.34 | 4.3063 | 4.2716 | 4.2379 | 4.2074 | 4.1789 | 4.1516 | 4.0305 | 3.9295 | 3.8411 | 3.9295 | 3.8968 | 3.8632 | 3.8305 | 3.7958 | 3.7632 | 3.7326 | 3.7053 | 3.6789 | 3.5653 | 3.4705 | 3.3884 | 3.9568 | 3.9347 | 3.9116 | 3.8884 | 3.8632 | 3.8389 | 3.8168 | 3.7979 | 3.7789 | 3.7042 | 3.5958 | 3.5
|  | CERNE ABBAS PRIMARY | HE |  |  |  |  | 4.4611 | 4.4442 | 4.4263 | 4.4063 | 4.3853 | 4.3674 | 4.3484 | 4.3326 | 4.3168 | 4.2621 | 4.2242 | 1.8084 | 3.9821 | 3.9642 | 3.9463 | 3.9274 | 3.9063 | 3.8895 | 3.8705 | 3.8547 | 3.8389 | 3.7863 | 3.7484 | 3.7211 | 3.9884 | 3.9758 | 3.9621 | 3.9463 | 3.9305 | 3.9168 | 3.9021 | 3.8895 | 3.8779 | 3.8389 | 3.8147 | 3.8
|  | CERNE ABBAS PRIMARY | CF |  |  |  |  | 4.4789 | 4.4684 | 4.4568 | 4.4463 | 4.4347 | 4.4232 | 4.4116 | 4.4011 | 4.3905 | 4.34 | 4.3074 | 4.2832 | 3.9979 | 3.9874 | 3.9768 | 3.9663 | 3.9547 | 3.9442 | 3.9326 | 3.9232 | 3.9116 | 3.8621 | 3.8316 | 3.8074 | 4 | 3.9926 | 3.9863 | 3.9789 | 3.9705 | 3.9632 | 3.9558 | 3.9484 | 3.9411 | 3.9063 | 3.8895 | 3.8779
LOVEDEAN GSP |  | CHALCRAFT LANE PRIMARY | MINIMUM HEADROOM | TBC | NO | YES | 0 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | CHALCRAFT LANE PRIMARY | EE | [7 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | CHALCRAFT LANE PRIMARY | HT | [7 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | CHALCRAFT LANE PRIMARY | HE | [7 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | CHALCRAFT LANE PRIMARY | CF | [7 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IVER 132KV GSP | CHALVEY BSP | CHALVEY PRIMARY | MINIMUM HEADROOM | SU 96669 79364 | NO | NO | 0 | 87.5806 | 86.8343 | 86.0669 | 85.2575 | 84.0891 | 81.9259 | 80.3364 | 78.8301 | 77.4133 | 71.3322 | 66.0343 | 2.7227 | 75.8785 | 73.4638 | 71.2522 | 68.8322 | 65.9354 | 63.5133 | 61.7533 | 60.0806 | 58.5069 | 51.7354 | 45.7954 | 40.2722 | 79.0469 | 76.6238 | 74.4122 | 71.9912 | 69.0943 | 66.6712 | 64.9101 | 63.2375 | 61.6638 | 54.8912 | 48.9491 | 43.4248
|  | CHALVEY PRIMARY | EE |  |  |  |  | 87.9691 | 87.3375 | 86.6912 | 85.9996 | 85.2512 | 83.728 | 82.3564 | 81.0364 | 79.8175 | 74.9091 | 70.7775 | 67.0301 | 76.6712 | 74.5027 | 72.5333 | 70.3396 | 67.6564 | 65.4722 | 63.9543 | 62.4943 | 61.1427 | 55.6775 | 51.0291 | 46.7775 | 79.8312 | 77.6627 | 75.6933 | 73.4996 | 70.8154 | 68.6301 | 67.1122 | 65.6512 | 64.2996 | 58.8343 | 54.1838 | 49.9312
|  | CHALVEY PRIMARY | HT |  |  |  |  | 87.5806 | 86.8343 | 86.0669 | 85.2575 | 84.0891 | 81.9259 | 80.3364 | 78.8301 | 77.4133 | 71.3322 | 66.0343 | 61.1417 | 75.8785 | 73.4638 | 71.2522 | 68.8322 | 65.9354 | 63.5133 | 61.7533 | 60.0806 | 58.5069 | 51.7354 | 45.7954 | 40.2722 | 79.0469 | 76.6238 | 74.4122 | 71.9912 | 69.0943 | 66.6712 | 64.9101 | 63.2375 | 61.6638 | 54.8912 | 48.9491 | 43.4248
|  | CHALVEY PRIMARY | HE |  |  |  |  | 88.4301 | 87.9333 | 87.4122 | 86.8459 | 86.2133 | 85.6354 | 84.8006 | 83.7669 | 82.828 | 79.2259 | 76.3091 | 2.7227 | 77.6722 | 75.8217 | 74.1406 | 72.2364 | 69.8154 | 67.8912 | 66.6406 | 65.4975 | 64.4543 | 60.4269 | 57.1196 | 54.1891 | 80.3712 | 78.9817 | 77.3017 | 75.3964 | 72.9743 | 71.0501 | 69.7996 | 68.6554 | 67.6133 | 63.5838 | 60.2764 | 57.3448
|  | CHALVEY PRIMARY | CF |  |  |  |  | 88.7385 | 88.5133 | 88.2796 | 88.0375 | 87.7322 | 87.3775 | 86.9743 | 86.6933 | 86.408 | 85.168 | 83.5964 | 81.8669 | 79.2185 | 78.8406 | 78.3143 | 77.5575 | 76.2427 | 74.5691 | 72.1491 | 71.4333 | 70.6448 | 67.6427 | 65.328 | 63.3438 | 80.8101 | 80.5522 | 80.2838 | 79.9975 | 79.4069 | 77.7291 | 75.3091 | 74.5933 | 73.8048 | 70.8017 | 68.4859 | 66.5006
NURSLING GSP | VELMORE BSP | CHANDLERS FORD PRIMARY | MINIMUM HEADROOM | SU 43494 21552 | NO | YES | 0 | 33.3716 | 32.9537 | 32.4716 | 31.6853 | 30.7589 | 29.5989 | 28.4874 | 27.5474 | 26.5411 | 22.6126 | 19.0979 | -14.9505 | 28.9747 | 28.0947 | 27.0389 | 26.1505 | 25.1484 | 23.8632 | 22.6305 | 21.5926 | 20.4705 | 16.1158 | 12.1684 | 8.5684 | 29.7579 | 28.8979 | 27.8326 | 26.9316 | 25.9116 | 24.6158 | 23.3821 | 22.3442 | 21.2221 | 16.8747 | 12.9263 | 9.3253
|  | CHANDLERS FORD PRIMARY | EE |  |  |  |  | 33.6316 | 33.2905 | 32.9232 | 32.5221 | 31.8958 | 30.9368 | 30.0147 | 29.2168 | 28.3463 | 25.2221 | 22.48 | 20.0263 | 29.4874 | 28.7947 | 27.9053 | 27.1758 | 26.3779 | 25.32 | 24.2947 | 23.4168 | 22.4463 | 18.9842 | 15.8905 | 13.1021 | 30.2863 | 29.5821 | 28.7137 | 27.9726 | 27.1621 | 26.0821 | 25.0474 | 24.1695 | 23.1989 | 19.7442 | 16.6484 | 13.86
|  | CHANDLERS FORD PRIMARY | HT |  |  |  |  | 33.3716 | 32.9537 | 32.4716 | 31.6853 | 30.7589 | 29.5989 | 28.4874 | 27.5474 | 26.5411 | 22.6126 | 19.0979 | 15.9126 | 28.9747 | 28.0947 | 27.0389 | 26.1505 | 25.1484 | 23.8632 | 22.6305 | 21.5926 | 20.4705 | 16.1158 | 12.1684 | 8.5684 | 29.7579 | 28.8979 | 27.8326 | 26.9316 | 25.9116 | 24.6158 | 23.3821 | 22.3442 | 21.2221 | 16.8747 | 12.9263 | 9.3253
|  | CHANDLERS FORD PRIMARY | HE |  |  |  |  | 33.9621 | 33.7253 | 33.4632 | 33.1811 | 32.8789 | 32.5063 | 31.7484 | 31.1211 | 30.4263 | 27.9726 | 25.9305 | -14.9505 | 30.1579 | 29.6842 | 29.0421 | 28.5116 | 27.8979 | 27.0189 | 26.18 | 25.4884 | 24.7063 | 21.9368 | 19.6116 | 17.5516 | 30.9305 | 30.4895 | 29.8263 | 29.3074 | 28.7063 | 27.8095 | 26.9526 | 26.2484 | 25.4579 | 22.68 | 20.3547 | 18.2937
|  | CHANDLERS FORD PRIMARY | CF |  |  |  |  | 34.1842 | 34.0611 | 33.9337 | 33.8021 | 33.6642 | 33.5242 | 33.3863 | 33.2368 | 33.0821 | 31.4526 | 30.0937 | 28.9211 | 30.5568 | 30.2884 | 29.9537 | 29.6789 | 29.3663 | 28.9179 | 28.4705 | 28.1137 | 27.7147 | 25.8021 | 24.2537 | 22.9063 | 31.1642 | 31.0316 | 30.7632 | 30.4779 | 30.1558 | 29.7105 | 29.2758 | 28.9179 | 28.5116 | 26.5579 | 25.0063 | 23.6579
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CHAPEL PRIMARY | MINIMUM HEADROOM | SU 42849 11983 | NO | YES | 0 | 27.4263 | 27.36 | 27.2895 | 27.2137 | 26.4589 | 25.3674 | 24.9116 | 24.4926 | 24.3832 | 23.2537 | 22.3179 | 4.1737 | 24.6253 | 24.4989 | 24.3158 | 24.1263 | 22.5411 | 21.2684 | 20.7442 | 20.2611 | 20.1632 | 18.8789 | 17.8137 | 16.8147 | 25.1053 | 25.0389 | 24.9684 | 24.8926 | 23.3537 | 22.08 | 21.5558 | 21.0726 | 20.9853 | 19.7011 | 18.6347 | 17.6358
|  | CHAPEL PRIMARY | EE |  |  |  |  | 27.4737 | 27.4221 | 27.3674 | 27.3074 | 27.2442 | 27.1832 | 26.3221 | 25.2621 | 24.8411 | 23.8368 | 23.0853 | 22.3842 | 24.6905 | 24.6189 | 24.48 | 24.34 | 24.1442 | 23.9389 | 22.3832 | 21.1432 | 20.6568 | 19.5274 | 18.6684 | 17.8642 | 25.1526 | 25.1011 | 25.0463 | 24.9863 | 24.9232 | 24.7516 | 23.1947 | 21.9547 | 21.4674 | 20.3495 | 19.4905 | 18.6853
|  | CHAPEL PRIMARY | HT |  |  |  |  | 27.4263 | 27.36 | 27.2895 | 27.2137 | 26.4589 | 25.3674 | 24.9116 | 24.4926 | 24.3832 | 23.2537 | 22.3179 | 21.4442 | 24.6253 | 24.4989 | 24.3158 | 24.1263 | 22.5411 | 21.2684 | 20.7442 | 20.2611 | 20.1632 | 18.8789 | 17.8137 | 16.8147 | 25.1053 | 25.0389 | 24.9684 | 24.8926 | 23.3537 | 22.08 | 21.5558 | 21.0726 | 20.9853 | 19.7011 | 18.6347 | 17.6358
|  | CHAPEL PRIMARY | HE |  |  |  |  | 27.5 | 27.4547 | 27.4053 | 27.3505 | 27.2937 | 27.2379 | 26.9074 | 25.9779 | 25.4053 | 24.2695 | 23.7063 | 4.1737 | 24.7168 | 24.6716 | 24.6158 | 24.4968 | 24.3242 | 24.1421 | 23.0621 | 21.9737 | 21.3053 | 19.9737 | 19.3263 | 18.6926 | 25.1789 | 25.1337 | 25.0842 | 25.0295 | 24.9726 | 24.9168 | 23.8737 | 22.7853 | 22.1168 | 20.7737 | 20.1274 | 19.4926
|  | CHAPEL PRIMARY | CF |  |  |  |  | 27.5253 | 27.4958 | 27.4653 | 27.4337 | 27.4 | 27.3674 | 27.3337 | 27.3011 | 27.0895 | 26.0989 | 25.7568 | 25.4137 | 24.7421 | 24.7126 | 24.6821 | 24.6505 | 24.6168 | 24.5737 | 24.5095 | 23.9147 | 23.2684 | 22.12 | 21.7284 | 21.3326 | 25.2042 | 25.1747 | 25.1442 | 25.1126 | 25.0789 | 25.0463 | 25.0126 | 24.7274 | 24.0811 | 22.9316 | 22.5411 | 22.1442
COWLEY GSP | YARNTON BSP | CHARLBURY PRIMARY | MINIMUM HEADROOM | SP 36034 18376 | NO | YES | 0 | 16.5874 | 16.3558 | 16.0674 | 15.7905 | 15.3874 | 15.0989 | 14.8358 | 14.5905 | 14.3589 | 13.26 | 12.0074 | 4.0874 | 15.2768 | 14.9821 | 14.6684 | 14.3684 | 13.92 | 13.6137 | 13.3326 | 13.0695 | 12.8211 | 11.6337 | 10.2411 | 8.7842 | 15.6758 | 15.3874 | 15.0768 | 14.7789 | 14.3347 | 14.0284 | 13.7484 | 13.4853 | 13.2358 | 12.0389 | 10.6389 | 9.18
|  | CHARLBURY PRIMARY | EE |  |  |  |  | 16.6789 | 16.5495 | 16.3589 | 16.1337 | 15.78 | 15.5526 | 15.3305 | 15.1147 | 14.9084 | 14.0684 | 13.1158 | 12.1284 | 15.4789 | 15.2421 | 14.9895 | 14.7474 | 14.3526 | 14.1105 | 13.8726 | 13.6432 | 13.4232 | 12.5284 | 11.4779 | 10.3537 | 15.8684 | 15.6411 | 15.3947 | 15.1537 | 14.7611 | 14.52 | 14.2821 | 14.0526 | 13.8326 | 12.9263 | 11.8621 | 10.7347
|  | CHARLBURY PRIMARY | HT |  |  |  |  | 16.5874 | 16.3558 | 16.0674 | 15.7905 | 15.3874 | 15.0989 | 14.8358 | 14.5905 | 14.3589 | 13.26 | 12.0074 | 10.7242 | 15.2768 | 14.9821 | 14.6684 | 14.3684 | 13.92 | 13.6137 | 13.3326 | 13.0695 | 12.8211 | 11.6337 | 10.2411 | 8.7842 | 15.6758 | 15.3874 | 15.0768 | 14.7789 | 14.3347 | 14.0284 | 13.7484 | 13.4853 | 13.2358 | 12.0389 | 10.6389 | 9.18
|  | CHARLBURY PRIMARY | HE |  |  |  |  | 16.8042 | 16.7147 | 16.6158 | 16.5095 | 16.3168 | 16.1547 | 15.9979 | 15.8495 | 15.7147 | 15.1958 | 14.5516 | 4.0874 | 15.7516 | 15.6 | 15.4326 | 15.2684 | 14.9432 | 14.7726 | 14.6053 | 14.4463 | 14.3042 | 13.7442 | 13.0158 | 12.1684 | 16.1305 | 15.9842 | 15.8221 | 15.6611 | 15.3484 | 15.1779 | 15.0116 | 14.8516 | 14.7095 | 14.1495 | 13.4221 | 12.5737
|  | CHARLBURY PRIMARY | CF |  |  |  |  | 16.8895 | 16.8432 | 16.7947 | 16.7453 | 16.6916 | 16.6389 | 16.5853 | 16.5095 | 16.4168 | 15.9884 | 15.6053 | 15.1274 | 15.9032 | 15.8126 | 15.7147 | 15.6116 | 15.4505 | 15.3389 | 15.2421 | 15.1484 | 15.0474 | 14.58 | 14.1453 | 13.5947 | 16.2768 | 16.1905 | 16.0958 | 15.9968 | 15.8432 | 15.7368 | 15.6432 | 15.5505 | 15.4505 | 14.9863 | 14.5537 | 14.0074
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER PRIMARY | MINIMUM HEADROOM | SY 67309 93186 | NO | YES | 0 | 17.8558 | 17.1737 | 16.6874 | 16.1926 | 15.8463 | 15.5032 | 14.6874 | 13.1726 | 11.6705 | 5.3737 | -1.1326 | -11.8295 | 14.2063 | 13.4432 | 12.9105 | 12.3663 | 12.0042 | 11.6432 | 10.7253 | 8.9789 | 7.2484 | 0.010526 | -7.4895 | -14.9789 | 14.9242 | 14.2158 | 13.6789 | 13.1326 | 12.7642 | 12.4 | 11.4779 | 9.7305 | 7.9979 | 0.73789 | -6.7905 | -14.2779
|  | CHARMINSTER PRIMARY | EE |  |  |  |  | 18.0168 | 17.4495 | 17.0263 | 16.5916 | 16.3032 | 16.0158 | 15.2432 | 13.7537 | 12.2811 | 6.1705 | -0.052632 | -6.1589 | 14.4347 | 13.7432 | 13.2758 | 12.7989 | 12.4989 | 12.2021 | 11.3316 | 9.6189 | 7.9242 | 0.91263 | -6.2432 | -13.3589 | 15.0284 | 14.5168 | 14.0474 | 13.5653 | 13.26 | 12.9568 | 12.08 | 10.3632 | 8.6642 | 1.6126 | -5.5916 | -12.7084
|  | CHARMINSTER PRIMARY | HT |  |  |  |  | 17.8558 | 17.1737 | 16.6874 | 16.1926 | 15.8463 | 15.5032 | 14.6874 | 13.1726 | 11.6705 | 5.3737 | -1.1326 | -7.5737 | 14.2063 | 13.4432 | 12.9105 | 12.3663 | 12.0042 | 11.6432 | 10.7253 | 8.9789 | 7.2484 | 0.010526 | -7.4895 | -14.9789 | 14.9242 | 14.2158 | 13.6789 | 13.1326 | 12.7642 | 12.4 | 11.4779 | 9.7305 | 7.9979 | 0.73789 | -6.7905 | -14.2779
|  | CHARMINSTER PRIMARY | HE |  |  |  |  | 18.1558 | 17.8221 | 17.4842 | 17.1295 | 16.9189 | 16.7189 | 16.0316 | 14.6347 | 13.2547 | 7.6232 | 1.9168 | -11.8295 | 14.7432 | 14.1442 | 13.7705 | 13.38 | 13.1642 | 12.9568 | 12.18 | 10.5611 | 8.9589 | 2.4263 | -4.2295 | -10.9947 | 15.1674 | 14.9221 | 14.5453 | 14.1516 | 13.9305 | 13.72 | 12.9358 | 11.3179 | 9.7168 | 3.1768 | -3.4779 | -10.2411
|  | CHARMINSTER PRIMARY | CF |  |  |  |  | 18.2505 | 18.1926 | 18.1326 | 18.0305 | 17.9126 | 17.7937 | 17.4337 | 16.6674 | 15.8495 | 12.2053 | 8.5968 | 4.9621 | 15.0747 | 14.7705 | 14.5768 | 14.3821 | 14.2589 | 14.1347 | 13.7295 | 12.8526 | 11.9021 | 7.6737 | 3.4663 | -0.78211 | 15.2621 | 15.2042 | 15.1442 | 15.0821 | 15.0126 | 14.9105 | 14.4989 | 13.6116 | 12.6621 | 8.4379 | 4.2316 | -0.015789
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | CHICHESTER PRIMARY | MINIMUM HEADROOM | SU 92198 07420 | NO | YES | 0.017895 | 20.3272 | 19.6619 | 33.7072 | 32.6367 | 31.3609 | 30.1156 | 28.8556 | 27.5777 | 26.4346 | 21.5262 | 17.0798 | -0.82332 | 18.7956 | 18.0767 | 32.0041 | 30.8146 | 29.3883 | 27.9967 | 26.5798 | 25.1377 | 23.8483 | 18.6135 | 13.5683 | 8.5051 | 19.2746 | 18.5567 | 32.4872 | 31.2998 | 29.8746 | 28.4851 | 27.0693 | 25.6283 | 24.3398 | 18.9146 | 13.8609 | 8.7998
|  | CHICHESTER PRIMARY | EE |  |  |  |  | 20.5409 | 20.2293 | 34.4241 | 33.4914 | 32.3525 | 31.2514 | 30.0841 | 28.9135 | 27.8872 | 23.8041 | 20.5419 | 16.9683 | 19.0093 | 18.6956 | 32.7872 | 31.7483 | 30.4704 | 29.2367 | 27.9209 | 26.6009 | 25.4441 | 20.8367 | 17.4567 | 13.3462 | 19.4883 | 19.1756 | 33.2683 | 32.2314 | 30.9546 | 29.7209 | 28.4072 | 27.0872 | 25.9304 | 21.3167 | 17.7304 | 13.6209
|  | CHICHESTER PRIMARY | HT |  |  |  |  | 20.3272 | 19.6619 | 33.7072 | 32.6367 | 31.3609 | 30.1156 | 28.8556 | 27.5777 | 26.4346 | 21.5262 | 17.0798 | 12.6609 | 18.7956 | 18.0767 | 32.0041 | 30.8146 | 29.3883 | 27.9967 | 26.5798 | 25.1377 | 23.8483 | 18.6135 | 13.5683 | 8.5051 | 19.2746 | 18.5567 | 32.4872 | 31.2998 | 29.8746 | 28.4851 | 27.0693 | 25.6283 | 24.3398 | 18.9146 | 13.8609 | 8.7998
|  | CHICHESTER PRIMARY | HE |  |  |  |  | 20.8304 | 20.6177 | 35.3641 | 34.5967 | 33.6125 | 32.6641 | 31.6462 | 30.6346 | 29.7577 | 34.6325 | 23.5914 | -0.82332 | 19.2988 | 19.0862 | 33.8104 | 32.9525 | 31.8419 | 30.7735 | 29.6177 | 28.4683 | 27.4735 | 23.9809 | 20.8472 | 17.4577 | 19.7777 | 19.5651 | 34.2904 | 33.4335 | 32.3251 | 31.2567 | 30.1041 | 28.9567 | 27.9609 | 24.4956 | 20.9093 | 17.4588
|  | CHICHESTER PRIMARY | CF |  |  |  |  | 21.0304 | 20.9198 | 35.9051 | 35.7862 | 35.6619 | 35.5346 | 35.3977 | 34.7746 | 34.1472 | 31.9619 | 30.5988 | 28.8104 | 19.4988 | 19.3883 | 34.3735 | 34.2546 | 34.1314 | 34.0041 | 33.8662 | 33.1535 | 32.4377 | 29.9641 | 28.4114 | 26.3388 | 19.9777 | 19.8672 | 34.8525 | 34.7335 | 34.6093 | 34.4819 | 34.343 | 33.6325 | 32.9177 | 30.4483 | 28.8956 | 26.8241
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL PRIMARY | MINIMUM HEADROOM | SY 65479 80511 | NO | YES | 0 | 14.2379 | 13.7874 | 13.3284 | 12.7221 | 11.9368 | 11.1505 | 10.3874 | 9.7347 | 8.9926 | 6.5558 | 5.4232 | -1.0011 | 13.9179 | 13.4116 | 12.8958 | 12.2063 | 11.3147 | 10.4232 | 9.5558 | 8.8179 | 7.9747 | 5.2589 | 4.0758 | 2.9821 | 13.9642 | 13.48 | 12.9737 | 12.3 | 11.4232 | 10.5305 | 9.6579 | 8.9137 | 8.0632 | 5.3021 | 4.06 | 2.9442
|  | CHICKERELL PRIMARY | EE |  |  |  |  | 14.3979 | 13.9937 | 13.5832 | 13.0211 | 12.2789 | 11.5358 | 10.7968 | 10.1611 | 9.44 | 7.1105 | 6.1379 | 5.3579 | 14.0926 | 13.6379 | 13.1747 | 12.5347 | 11.6895 | 10.8463 | 10.0105 | 9.2947 | 8.4768 | 5.9053 | 4.9295 | 4.0832 | 14.1326 | 13.7011 | 13.2474 | 12.6211 | 11.7895 | 10.9484 | 10.1042 | 9.3811 | 8.5526 | 5.9126 | 4.8568 | 3.9842
|  | CHICKERELL PRIMARY | HT |  |  |  |  | 14.2379 | 13.7874 | 13.3284 | 12.7221 | 11.9368 | 11.1505 | 10.3874 | 9.7347 | 8.9926 | 6.5558 | 5.4232 | 4.4242 | 13.9179 | 13.4116 | 12.8958 | 12.2063 | 11.3147 | 10.4232 | 9.5558 | 8.8179 | 7.9747 | 5.2589 | 4.0758 | 2.9821 | 13.9642 | 13.48 | 12.9737 | 12.3 | 11.4232 | 10.5305 | 9.6579 | 8.9137 | 8.0632 | 5.3021 | 4.06 | 2.9442
|  | CHICKERELL PRIMARY | HE |  |  |  |  | 14.6189 | 14.2853 | 13.9411 | 13.4411 | 12.7611 | 12.0884 | 11.4232 | 10.8632 | 10.2179 | 8.3063 | 7.7926 | -1.0011 | 14.3263 | 13.9537 | 13.5621 | 12.9895 | 12.2116 | 11.44 | 10.6768 | 10.0379 | 9.2958 | 7.1263 | 6.5821 | 6.0021 | 14.3632 | 14.0063 | 13.6316 | 13.0716 | 12.3074 | 11.5505 | 10.7842 | 10.1421 | 9.3968 | 7.2021 | 6.6358 | 6.0347
|  | CHICKERELL PRIMARY | CF |  |  |  |  | 14.7779 | 14.6074 | 14.4389 | 14.2137 | 13.9189 | 13.6011 | 13.2579 | 12.9474 | 12.5621 | 11.2979 | 10.9379 | 10.5884 | 14.4884 | 14.3137 | 14.1232 | 13.8642 | 13.5284 | 13.1642 | 12.7705 | 12.4147 | 11.9716 | 10.5284 | 10.1421 | 9.76 | 14.5305 | 14.3474 | 14.1674 | 13.9253 | 13.5989 | 13.24 | 12.8547 | 12.5053 | 12.0705 | 10.6284 | 10.2316 | 9.8368
AXMINSTER GSP | YEOVIL BSP | CHILTON CANTELO PRIMARY | MINIMUM HEADROOM | ST 57910 21616 | NO | YES | 0 | 15.3147 | 14.7126 | 13.9979 | 13.0737 | 11.9579 | 10.9663 | 10.2621 | 9.5684 | 8.8968 | 7.8147 | 6.9074 | -4.1747 | 14.0379 | 13.3516 | 12.5347 | 11.4726 | 10.1979 | 9.0684 | 8.2726 | 7.4895 | 6.7274 | 5.5958 | 4.6663 | 3.8011 | 14.1832 | 13.5474 | 12.7274 | 11.6611 | 10.3758 | 9.2358 | 8.4295 | 7.6368 | 6.8674 | 5.6884 | 4.7074 | 3.82
|  | CHILTON CANTELO PRIMARY | EE |  |  |  |  | 15.4368 | 14.8705 | 14.1905 | 13.2979 | 12.2147 | 11.2516 | 10.5674 | 9.8832 | 9.2232 | 8.2442 | 7.4295 | 6.8084 | 14.1695 | 13.5642 | 12.7811 | 11.7495 | 10.5011 | 9.3979 | 8.6232 | 7.8495 | 7.1032 | 6.12 | 5.3074 | 4.6421 | 14.3053 | 13.7189 | 12.9368 | 11.9063 | 10.6537 | 9.5453 | 8.7621 | 7.98 | 7.2253 | 6.1705 | 5.2989 | 4.6095
|  | CHILTON CANTELO PRIMARY | HT |  |  |  |  | 15.3147 | 14.7126 | 13.9979 | 13.0737 | 11.9579 | 10.9663 | 10.2621 | 9.5684 | 8.8968 | 7.8147 | 6.9074 | 6.1084 | 14.0379 | 13.3516 | 12.5347 | 11.4726 | 10.1979 | 9.0684 | 8.2726 | 7.4895 | 6.7274 | 5.5958 | 4.6663 | 3.8011 | 14.1832 | 13.5474 | 12.7274 | 11.6611 | 10.3758 | 9.2358 | 8.4295 | 7.6368 | 6.8674 | 5.6884 | 4.7074 | 3.82
|  | CHILTON CANTELO PRIMARY | HE |  |  |  |  | 15.6021 | 15.0874 | 14.4579 | 13.6137 | 12.5789 | 11.6726 | 11.0484 | 10.4232 | 9.8284 | 9.2032 | 8.7937 | -4.1747 | 14.3484 | 13.7579 | 13.0326 | 12.0579 | 10.8684 | 9.8274 | 9.1158 | 8.4053 | 7.7253 | 7.0695 | 6.6442 | 6.18 | 14.4705 | 13.9537 | 13.2274 | 12.2484 | 11.0505 | 10.0011 | 9.2821 | 8.5632 | 7.8768 | 7.1937 | 6.7474 | 6.2642
|  | CHILTON CANTELO PRIMARY | CF |  |  |  |  | 16.0737 | 15.8726 | 15.6474 | 15.3053 | 14.8484 | 14.3537 | 13.9242 | 13.4821 | 13.0211 | 12.3905 | 12.1137 | 11.8232 | 14.8842 | 14.6568 | 14.4011 | 14.0095 | 13.4853 | 12.9147 | 12.4221 | 11.9158 | 11.3842 | 10.6884 | 10.4021 | 10.0926 | 14.9453 | 14.7432 | 14.5158 | 14.1726 | 13.68 | 13.1053 | 12.6084 | 12.0979 | 11.5621 | 10.8537 | 10.5526 | 10.2263
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | CHINEHAM PRIMARY | MINIMUM HEADROOM | SU 65105 55805 | NO | YES | 0.73684 | 32.9042 | 32.7074 | 32.4989 | 32.2189 | 31.2116 | 29.1063 | 27.0326 | 24.9842 | 23.4558 | 21.1347 | 19.8516 | 0.0052632 | 29.5705 | 28.9274 | 28.1495 | 27.0284 | 25.8832 | 23.4453 | 21.04 | 18.66 | 16.8916 | 14.2789 | 12.8558 | 11.2484 | 30.2168 | 29.6705 | 28.8705 | 27.7358 | 26.5916 | 24.1579 | 21.7568 | 19.3821 | 17.6158 | 15.0063 | 13.5863 | 11.98
|  | CHINEHAM PRIMARY | EE |  |  |  |  | 33.0126 | 32.8495 | 32.6747 | 32.4926 | 31.7011 | 30.9158 | 29.2979 | 27.2526 | 25.6726 | 22.0937 | 21.2284 | 20.1389 | 29.7453 | 29.2284 | 28.54 | 27.4958 | 26.4147 | 25.5232 | 23.6505 | 21.2737 | 19.44 | 15.3232 | 14.3695 | 13.1347 | 30.3326 | 29.9947 | 29.2674 | 28.2021 | 27.1232 | 26.2326 | 24.3632 | 21.9905 | 20.16 | 16.0505 | 15.0979 | 13.8642
|  | CHINEHAM PRIMARY | HT |  |  |  |  | 32.9042 | 32.7074 | 32.4989 | 32.2189 | 31.2116 | 29.1063 | 27.0326 | 24.9842 | 23.4558 | 21.1347 | 19.8516 | 18.4253 | 29.5705 | 28.9274 | 28.1495 | 27.0284 | 25.8832 | 23.4453 | 21.04 | 18.66 | 16.8916 | 14.2789 | 12.8558 | 11.2484 | 30.2168 | 29.6705 | 28.8705 | 27.7358 | 26.5916 | 24.1579 | 21.7568 | 19.3821 | 17.6158 | 15.0063 | 13.5863 | 11.98
|  | CHINEHAM PRIMARY | HE |  |  |  |  | 33.1663 | 33.0484 | 32.9189 | 32.78 | 32.3716 | 31.6663 | 30.4895 | 29.1453 | 28.3179 | 25.3305 | 23.2137 | 0.0052632 | 29.9579 | 29.6421 | 29.0768 | 28.1326 | 27.1474 | 26.3411 | 24.9811 | 23.4211 | 22.4674 | 19.0158 | 16.5621 | 15.68 | 30.4979 | 30.3558 | 29.8137 | 28.8442 | 27.8547 | 27.0505 | 25.6926 | 24.1347 | 23.1821 | 19.7368 | 17.2884 | 16.4074
|  | CHINEHAM PRIMARY | CF |  |  |  |  | 33.2684 | 33.2042 | 33.1379 | 33.0705 | 32.9989 | 32.9274 | 32.8558 | 32.7463 | 32.4305 | 30.3737 | 28.4874 | 27.5421 | 30.0958 | 30.0021 | 29.8989 | 29.7568 | 29.2474 | 28.6737 | 28.1368 | 27.56 | 27.2021 | 24.8358 | 22.6453 | 21.5474 | 30.6063 | 30.5368 | 30.4642 | 30.3842 | 29.9947 | 29.3968 | 28.8453 | 28.2674 | 27.9095 | 25.5474 | 23.36 | 22.2653
COWLEY GSP | YARNTON BSP | CHIPPING NORTON PRIMARY | MINIMUM HEADROOM | SP 31382 26792 | NO | YES | 0 | 19.4926 | 19.3379 | 19.1737 | 18.9547 | 18.3621 | 17.5421 | 16.4284 | 15.3253 | 14.18 | 11.9253 | 10.7011 | -5.3537 | 15.6137 | 15.2042 | 14.7474 | 14.3011 | 13.5895 | 12.5853 | 11.1958 | 9.8874 | 8.5305 | 5.9168 | 4.52 | 3.0368 | 16.3811 | 15.9716 | 15.5158 | 15.0695 | 14.3589 | 13.3558 | 11.9705 | 10.6663 | 9.3116 | 6.7021 | 5.3074 | 3.8263
|  | CHIPPING NORTON PRIMARY | EE |  |  |  |  | 19.5789 | 19.4505 | 19.3126 | 19.1695 | 18.8842 | 18.3147 | 17.4684 | 16.3137 | 15.0611 | 12.7263 | 11.82 | 10.8126 | 15.8095 | 15.46 | 15.06 | 14.7263 | 14.2042 | 13.5137 | 12.4642 | 11.0168 | 9.5221 | 6.8074 | 5.7726 | 4.5989 | 16.5295 | 16.2274 | 15.8274 | 15.4947 | 14.9737 | 14.2842 | 13.2358 | 11.7916 | 10.2989 | 7.5926 | 6.5579 | 5.3863
|  | CHIPPING NORTON PRIMARY | HT |  |  |  |  | 19.4926 | 19.3379 | 19.1737 | 18.9547 | 18.3621 | 17.5421 | 16.4284 | 15.3253 | 14.18 | 11.9253 | 10.7011 | 9.42 | 15.6137 | 15.2042 | 14.7474 | 14.3011 | 13.5895 | 12.5853 | 11.1958 | 9.8874 | 8.5305 | 5.9168 | 4.52 | 3.0368 | 16.3811 | 15.9716 | 15.5158 | 15.0695 | 14.3589 | 13.3558 | 11.9705 | 10.6663 | 9.3116 | 6.7021 | 5.3074 | 3.8263
|  | CHIPPING NORTON PRIMARY | HE |  |  |  |  | 19.6979 | 19.6063 | 19.5042 | 19.3947 | 19.2779 | 18.8674 | 18.0274 | 16.9179 | 15.7811 | 13.7126 | 13.0695 | -5.3537 | 16.0337 | 15.8084 | 15.4937 | 15.2295 | 14.7695 | 14.1421 | 13.0916 | 11.6937 | 10.3126 | 7.8558 | 7.1137 | 6.2326 | 16.6568 | 16.5558 | 16.2611 | 15.9968 | 15.5379 | 14.9116 | 13.8632 | 12.4674 | 11.0884 | 8.6326 | 7.8916 | 7.0126
|  | CHIPPING NORTON PRIMARY | CF |  |  |  |  | 19.7811 | 19.7326 | 19.68 | 19.6274 | 19.5726 | 19.5168 | 19.4621 | 19.4084 | 19.3537 | 16.5368 | 16.0916 | 15.6189 | 16.1284 | 16.0674 | 15.9358 | 15.8284 | 15.7211 | 15.6084 | 15.44 | 15.2053 | 14.8789 | 11.1768 | 10.6642 | 10.1074 | 16.7453 | 16.6916 | 16.6326 | 16.5768 | 16.4884 | 16.3758 | 16.2074 | 15.9726 | 15.6474 | 11.9516 | 11.4389 | 10.8842
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE PRIMARY | MINIMUM HEADROOM | SU 80226 89155 | NO | YES | 0 | 7.1189 | 7.0316 | 6.9421 | 6.8526 | 6.7642 | 6.6758 | 6.5916 | 6.5095 | 6.4295 | 6.0768 | 5.7737 | -0.48947 | 7.5147 | 7.4263 | 7.3358 | 7.2463 | 7.1568 | 7.0684 | 6.9842 | 6.8989 | 6.82 | 6.4642 | 6.1579 | 5.8905 | 7.8884 | 7.7947 | 7.7 | 7.6063 | 7.5126 | 7.42 | 7.3316 | 7.2442 | 7.1589 | 6.7811 | 6.4537 | 6.1653
|  | CHISBRIDGE PRIMARY | EE |  |  |  |  | 7.1821 | 7.1137 | 7.0421 | 6.9705 | 6.8989 | 6.8284 | 6.7642 | 6.6958 | 6.6337 | 6.3463 | 6.1084 | 5.9084 | 7.5789 | 7.5095 | 7.4368 | 7.3653 | 7.2926 | 7.2232 | 7.1579 | 7.0895 | 7.0263 | 6.7379 | 6.4989 | 6.2968 | 7.9558 | 7.8821 | 7.8074 | 7.7326 | 7.6568 | 7.5842 | 7.5158 | 7.4432 | 7.3779 | 7.0695 | 6.8116 | 6.5916
|  | CHISBRIDGE PRIMARY | HT |  |  |  |  | 7.1189 | 7.0316 | 6.9421 | 6.8526 | 6.7642 | 6.6758 | 6.5916 | 6.5095 | 6.4295 | 6.0768 | 5.7737 | 5.5095 | 7.5147 | 7.4263 | 7.3358 | 7.2463 | 7.1568 | 7.0684 | 6.9842 | 6.8989 | 6.82 | 6.4642 | 6.1579 | 5.8905 | 7.8884 | 7.7947 | 7.7 | 7.6063 | 7.5126 | 7.42 | 7.3316 | 7.2442 | 7.1589 | 6.7811 | 6.4537 | 6.1653
|  | CHISBRIDGE PRIMARY | HE |  |  |  |  | 7.2632 | 7.22 | 7.1737 | 7.1253 | 7.0747 | 7.0274 | 6.9811 | 6.9358 | 6.8916 | 6.7021 | 6.5558 | -0.48947 | 7.6611 | 7.6168 | 7.5705 | 7.5221 | 7.4716 | 7.4232 | 7.3779 | 7.3316 | 7.2874 | 7.0958 | 6.9474 | 6.8232 | 8.0421 | 7.9968 | 7.9484 | 7.8979 | 7.8453 | 7.7958 | 7.7484 | 7.7 | 7.6537 | 7.4495 | 7.2895 | 7.1547
|  | CHISBRIDGE PRIMARY | CF |  |  |  |  | 7.3095 | 7.2832 | 7.2568 | 7.2305 | 7.2032 | 7.1758 | 7.1484 | 7.1189 | 7.0895 | 6.9526 | 6.8442 | 6.7526 | 7.7084 | 7.6811 | 7.6547 | 7.6274 | 7.6 | 7.5716 | 7.5453 | 7.5147 | 7.4853 | 7.3474 | 7.2368 | 7.1442 | 8.0916 | 8.0632 | 8.0347 | 8.0074 | 7.9779 | 7.9484 | 7.92 | 7.8884 | 7.8579 | 7.7105 | 7.5926 | 7.4905
MINETY GSP | TOOTHILL BSP | CHISLEDON PRIMARY | MINIMUM HEADROOM | SU 18894 79934 | NO | YES | 0 | 15.8063 | 14.6905 | 12.7937 | 10.4295 | 7.6189 | 4.5063 | 1.6432 | -1.2305 | -3.7379 | -9.3937 | -10.1989 | -13.0695 | 14.4874 | 13.2126 | 11.0663 | 8.3126 | 5.0242 | 1.38 | -1.9726 | -5.34 | -8.2758 | -14.8768 | -15.7853 | -16.6474 | 14.8232 | 13.6432 | 11.4547 | 8.6968 | 5.4137 | 1.7768 | -1.5705 | -4.9305 | -7.8611 | -14.4505 | -15.3579 | -16.2189
|  | CHISLEDON PRIMARY | EE |  |  |  |  | 15.9179 | 14.8379 | 12.9747 | 10.6442 | 7.8642 | 4.7853 | 1.9463 | -0.90632 | -3.3916 | -8.8821 | -9.5105 | -10.1032 | 14.6042 | 13.3705 | 11.26 | 8.5463 | 5.2895 | 1.6811 | -1.6453 | -4.9895 | -7.9021 | -14.32 | -15.0316 | -15.7095 | 14.9368 | 13.7968 | 11.6516 | 8.9295 | 5.6789 | 2.0779 | -1.2432 | -4.5811 | -7.4874 | -13.8947 | -14.6053 | -15.2821
|  | CHISLEDON PRIMARY | HT |  |  |  |  | 15.8063 | 14.6905 | 12.7937 | 10.4295 | 7.6189 | 4.5063 | 1.6432 | -1.2305 | -3.7379 | -9.3937 | -10.1989 | -10.9579 | 14.4874 | 13.2126 | 11.0663 | 8.3126 | 5.0242 | 1.38 | -1.9726 | -5.34 | -8.2758 | -14.8768 | -15.7853 | -16.6474 | 14.8232 | 13.6432 | 11.4547 | 8.6968 | 5.4137 | 1.7768 | -1.5705 | -4.9305 | -7.8611 | -14.4505 | -15.3579 | -16.2189
|  | CHISLEDON PRIMARY | HE |  |  |  |  | 16.0663 | 15.0326 | 13.2147 | 10.9263 | 8.1853 | 5.1442 | 2.3421 | -0.47474 | -2.9242 | -8.2526 | -8.7274 | -13.0695 | 14.7589 | 13.5789 | 11.5168 | 8.8516 | 5.6379 | 2.0716 | -1.2147 | -4.52 | -7.3947 | -13.6347 | -14.1779 | -14.7 | 15.0863 | 14.0011 | 11.9116 | 9.2347 | 6.0274 | 2.4663 | -0.81263 | -4.1116 | -6.9811 | -13.2105 | -13.7526 | -14.2737
|  | CHISLEDON PRIMARY | CF |  |  |  |  | 16.1421 | 15.9032 | 15.1242 | 14.1674 | 13.0653 | 11.7095 | 10.3337 | 8.8242 | 7.3968 | 4.0347 | 3.7589 | 3.4811 | 15.1074 | 14.5789 | 13.6758 | 12.5905 | 11.34 | 9.7589 | 8.1453 | 6.3747 | 4.7 | 0.76737 | 0.45368 | 0.13263 | 15.4168 | 14.9179 | 14.0958 | 13.0179 | 11.7284 | 10.14 | 8.5295 | 6.7621 | 5.0916 | 1.1653 | 0.85263 | 0.53158
FLEET-BRAMLEY GSP | BRACKNELL BSP | CHOBHAM PRIMARY | MINIMUM HEADROOM | SU 97173 63223 | NO | YES | 0 | 25.9653 | 25.7463 | 25.5137 | 24.8853 | 24.1695 | 23.7 | 23.2642 | 22.9316 | 22.6179 | 21.1463 | 19.7326 | 4.5084 | 23.42 | 22.6463 | 21.8453 | 20.9611 | 20.1621 | 19.6537 | 19.1779 | 18.8211 | 18.4842 | 16.8811 | 15.3116 | 13.9084 | 24.1958 | 23.4042 | 22.5958 | 21.7116 | 20.9116 | 20.4032 | 19.9274 | 19.5705 | 19.2326 | 17.6274 | 16.0537 | 14.6495
|  | CHOBHAM PRIMARY | EE |  |  |  |  | 26.1053 | 25.9274 | 25.7379 | 25.4537 | 24.6 | 24.2284 | 23.8074 | 23.4579 | 23.1916 | 22.0316 | 20.9495 | 20.0158 | 23.7074 | 23.0168 | 22.3484 | 21.5832 | 20.6147 | 20.2095 | 19.7463 | 19.3684 | 19.0811 | 17.82 | 16.6158 | 15.5642 | 24.4874 | 23.7811 | 23.1 | 22.3337 | 21.3642 | 20.96 | 20.4958 | 20.1168 | 19.8295 | 18.5632 | 17.3547 | 16.3021
|  | CHOBHAM PRIMARY | HT |  |  |  |  | 25.9653 | 25.7463 | 25.5137 | 24.8853 | 24.1695 | 23.7 | 23.2642 | 22.9316 | 22.6179 | 21.1463 | 19.7326 | 18.4779 | 23.42 | 22.6463 | 21.8453 | 20.9611 | 20.1621 | 19.6537 | 19.1779 | 18.8211 | 18.4842 | 16.8811 | 15.3116 | 13.9084 | 24.1958 | 23.4042 | 22.5958 | 21.7116 | 20.9116 | 20.4032 | 19.9274 | 19.5705 | 19.2326 | 17.6274 | 16.0537 | 14.6495
|  | CHOBHAM PRIMARY | HE |  |  |  |  | 26.2821 | 26.1611 | 26.0263 | 25.8032 | 25.0368 | 24.7526 | 24.4126 | 24.1695 | 23.9947 | 23.2474 | 22.5316 | 4.5084 | 24.0821 | 23.5084 | 22.8632 | 21.9347 | 21.0579 | 20.7516 | 20.3747 | 20.1105 | 19.9263 | 19.1126 | 18.3084 | 17.6242 | 24.8684 | 24.2811 | 23.62 | 22.6863 | 21.8084 | 21.5011 | 21.1242 | 20.8611 | 20.6747 | 19.8611 | 19.0547 | 18.3684
|  | CHOBHAM PRIMARY | CF |  |  |  |  | 26.4011 | 26.34 | 26.2747 | 26.2095 | 26.1389 | 26.0705 | 26 | 25.9326 | 25.8642 | 25.5579 | 25.3221 | 24.9137 | 24.5 | 24.2105 | 23.9589 | 23.6832 | 23.4432 | 23.3042 | 23.1642 | 22.9989 | 22.8221 | 22.0158 | 21.4558 | 20.9895 | 25.2589 | 24.9989 | 24.7411 | 24.46 | 24.2137 | 24.0726 | 23.9295 | 23.7611 | 23.58 | 22.7663 | 22.2042 | 21.7379
COWLEY GSP | DRAYTON BSP | CHOLSEY PRIMARY | MINIMUM HEADROOM | SU 58223 84685 | NO | YES | 0 | 16.5295 | 16.3105 | 16.0642 | 15.8116 | 15.5632 | 15.3116 | 15.0832 | 14.8653 | 14.6589 | 13.7663 | 12.9632 | -9.8789 | 14.7084 | 14.4432 | 14.1726 | 13.8968 | 13.6253 | 13.3516 | 13.1 | 12.8653 | 12.6442 | 11.6726 | 10.7747 | 9.7968 | 14.8253 | 14.5568 | 14.2821 | 14.0021 | 13.7274 | 13.4495 | 13.1958 | 12.9568 | 12.7326 | 11.7516 | 10.8537 | 9.8779
|  | CHOLSEY PRIMARY | EE |  |  |  |  | 16.6211 | 16.5 | 16.3211 | 16.1168 | 15.9116 | 15.7095 | 15.5168 | 15.3305 | 15.16 | 14.4589 | 13.8874 | 13.2853 | 14.8853 | 14.6779 | 14.4579 | 14.2358 | 14.0126 | 13.7916 | 13.58 | 13.3768 | 13.1895 | 12.4263 | 11.7926 | 11.1021 | 15.0063 | 14.7947 | 14.5726 | 14.3474 | 14.1211 | 13.8968 | 13.6832 | 13.4758 | 13.2863 | 12.5105 | 11.8716 | 11.1811
|  | CHOLSEY PRIMARY | HT |  |  |  |  | 16.5295 | 16.3105 | 16.0642 | 15.8116 | 15.5632 | 15.3116 | 15.0832 | 14.8653 | 14.6589 | 13.7663 | 12.9632 | 12.1084 | 14.7084 | 14.4432 | 14.1726 | 13.8968 | 13.6253 | 13.3516 | 13.1 | 12.8653 | 12.6442 | 11.6726 | 10.7747 | 9.7968 | 14.8253 | 14.5568 | 14.2821 | 14.0021 | 13.7274 | 13.4495 | 13.1958 | 12.9568 | 12.7326 | 11.7516 | 10.8537 | 9.8779
|  | CHOLSEY PRIMARY | HE |  |  |  |  | 16.7421 | 16.6579 | 16.5663 | 16.4674 | 16.3632 | 16.2263 | 16.0853 | 15.9516 | 15.8326 | 15.3926 | 15.0632 | -9.8789 | 15.1253 | 14.9895 | 14.8421 | 14.6863 | 14.5263 | 14.3674 | 14.2137 | 14.0695 | 13.94 | 13.4505 | 13.0758 | 12.6389 | 15.2505 | 15.1126 | 14.9621 | 14.8053 | 14.6432 | 14.4821 | 14.3274 | 14.1811 | 14.0484 | 13.5526 | 13.1705 | 12.7221
|  | CHOLSEY PRIMARY | CF |  |  |  |  | 16.8242 | 16.7821 | 16.7358 | 16.6884 | 16.64 | 16.5895 | 16.54 | 16.4905 | 16.4421 | 16.0758 | 15.8263 | 15.58 | 15.3011 | 15.2295 | 15.1516 | 15.0653 | 14.9768 | 14.8832 | 14.7905 | 14.6979 | 14.6053 | 14.1874 | 13.9021 | 13.6084 | 15.4442 | 15.3632 | 15.2768 | 15.1895 | 15.1 | 15.0042 | 14.9105 | 14.8158 | 14.7221 | 14.2979 | 14.0063 | 13.7053
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH PRIMARY | MINIMUM HEADROOM | SZ 15698 93141 | NO | YES | 0.46316 | 35.7979 | 35.3032 | 34.7779 | 34.2347 | 34.3095 | 33.7484 | 32.7947 | 31.8232 | 30.8874 | 26.6842 | 22.8558 | -13.2316 | 29.7158 | 28.7905 | 27.8505 | 26.9105 | 26.9863 | 25.9358 | 24.9074 | 23.9042 | 22.8842 | 18.2905 | 14.0737 | 10.2684 | 30.74 | 29.8011 | 28.8474 | 27.8979 | 27.8611 | 26.8042 | 25.7716 | 24.7105 | 23.6842 | 19.0505 | 14.7884 | 10.9674
|  | CHRISTCHURCH PRIMARY | EE |  |  |  |  | 36.0884 | 35.68 | 35.2474 | 34.7937 | 34.3095 | 33.8379 | 33.3863 | 32.8832 | 32.9347 | 29.5611 | 26.4884 | 23.8842 | 30.3442 | 29.6095 | 28.8558 | 28.0958 | 27.3263 | 26.4958 | 25.6863 | 24.9011 | 25.0968 | 21.4474 | 18.0895 | 15.1684 | 31.1779 | 30.6326 | 29.8695 | 29.1 | 28.3168 | 27.4705 | 26.6537 | 25.86 | 25.9411 | 22.2347 | 18.8105 | 15.8695
|  | CHRISTCHURCH PRIMARY | HT |  |  |  |  | 35.7979 | 35.3032 | 34.7779 | 34.2347 | 34.3674 | 33.7484 | 32.7947 | 31.8232 | 30.8874 | 26.6842 | 22.8558 | 19.4579 | 29.7158 | 28.7905 | 27.8505 | 26.9105 | 26.9863 | 25.9358 | 24.9074 | 23.9042 | 22.8842 | 18.2905 | 14.0737 | 10.2684 | 30.74 | 29.8011 | 28.8474 | 27.8979 | 27.8611 | 26.8042 | 25.7716 | 24.7105 | 23.6842 | 19.0505 | 14.7884 | 10.9674
|  | CHRISTCHURCH PRIMARY | HE |  |  |  |  | 36.4684 | 36.1789 | 35.8589 | 35.5126 | 35.1337 | 34.7716 | 34.4284 | 34.1063 | 34.5337 | 33.1337 | 31.1179 | -13.2316 | 31.0568 | 30.6989 | 30.1916 | 29.6653 | 29.1147 | 28.5147 | 27.9463 | 27.3842 | 27.8 | 25.34 | 23.0842 | 21.0853 | 31.5853 | 31.2842 | 30.9526 | 30.5958 | 30.1379 | 29.5274 | 28.9505 | 28.3779 | 28.6842 | 26.1211 | 23.8484 | 21.8337
|  | CHRISTCHURCH PRIMARY | CF |  |  |  |  | 36.7337 | 36.58 | 36.42 | 36.2558 | 36.0779 | 35.8979 | 35.7211 | 35.5474 | 35.3716 | 35.2947 | 34.84 | 33.6516 | 31.3389 | 31.1779 | 31.0095 | 30.8379 | 30.5053 | 30.1211 | 29.7263 | 29.3674 | 29.0232 | 28.5747 | 27.0411 | 25.6958 | 31.8674 | 31.7053 | 31.5379 | 31.3653 | 31.1779 | 30.9863 | 30.7495 | 30.3832 | 30.0326 | 29.4621 | 27.8947 | 26.5379
LALEHAM GSP | EAST BEDFONT BSP | CHURCH ROAD PRIMARY | MINIMUM HEADROOM | TQ 06820 71722 | NO | YES | 0 | 15.1379 | 14.8116 | 14.4642 | 14.1063 | 13.7358 | 13.3653 | 12.4726 | 11.6737 | 11.2095 | 8.6505 | 6.3758 | -13.3853 | 11.6779 | 11.0547 | 10.4221 | 9.7926 | 9.1684 | 8.5611 | 7.4158 | 6.5126 | 6.0084 | 3.1463 | 0.56947 | -1.8189 | 12.4295 | 11.8284 | 11.2168 | 10.6084 | 9.9926 | 9.3863 | 8.2421 | 7.34 | 6.8358 | 3.9779 | 1.4042 | -0.98105
|  | CHURCH ROAD PRIMARY | EE |  |  |  |  | 15.3326 | 15.0653 | 14.7811 | 14.4842 | 14.1758 | 13.88 | 13.5347 | 12.7989 | 12.4074 | 10.3863 | 8.6579 | 7.1021 | 12.1063 | 11.6158 | 11.1168 | 10.6158 | 10.1116 | 9.6316 | 8.5821 | 7.7495 | 7.3263 | 5.0674 | 3.1011 | 1.3116 | 12.84 | 12.3663 | 11.8832 | 11.3979 | 10.9084 | 10.4421 | 9.4074 | 8.5758 | 8.1537 | 5.8968 | 3.9337 | 2.1463
|  | CHURCH ROAD PRIMARY | HT |  |  |  |  | 15.1379 | 14.8116 | 14.4642 | 14.1063 | 13.7358 | 13.3653 | 12.4726 | 11.6737 | 11.2095 | 8.6505 | 6.3758 | 4.2632 | 11.6779 | 11.0547 | 10.4221 | 9.7926 | 9.1684 | 8.5611 | 7.4158 | 6.5126 | 6.0084 | 3.1463 | 0.56947 | -1.8189 | 12.4295 | 11.8284 | 11.2168 | 10.6084 | 9.9926 | 9.3863 | 8.2421 | 7.34 | 6.8358 | 3.9779 | 1.4042 | -0.98105
|  | CHURCH ROAD PRIMARY | HE |  |  |  |  | 15.5853 | 15.3947 | 15.1853 | 14.9579 | 14.7179 | 14.4863 | 14.2695 | 14.0653 | 13.8916 | 12.5895 | 11.4211 | -13.3853 | 12.6663 | 12.3484 | 12.0137 | 11.6684 | 11.3105 | 10.9726 | 10.0642 | 9.3716 | 9.0895 | 7.5021 | 6.1621 | 4.9705 | 13.3768 | 13.0684 | 12.7432 | 12.4063 | 12.0579 | 11.7284 | 10.8716 | 10.1968 | 9.9147 | 8.3284 | 6.9905 | 5.8011
|  | CHURCH ROAD PRIMARY | CF |  |  |  |  | 15.7558 | 15.6547 | 15.5484 | 15.4389 | 15.3253 | 15.2095 | 15.0958 | 14.9842 | 14.8716 | 14.3705 | 13.6347 | 12.92 | 13.0979 | 12.9884 | 12.8253 | 12.5368 | 12.2305 | 11.9474 | 11.4316 | 11.0242 | 10.8126 | 9.5589 | 8.5947 | 7.76 | 13.5547 | 13.4537 | 13.3474 | 13.2379 | 12.9537 | 12.6842 | 12.1989 | 11.8126 | 11.6084 | 10.3842 | 9.4211 | 8.5874
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN PRIMARY | MINIMUM HEADROOM | SP 02761 00827 | NO | YES | 1.0979 | 35.5654 | 35.257 | 34.9159 | 34.4265 | 33.9044 | 33.3791 | 32.8759 | 32.3938 | 31.9991 | 29.4381 | 26.6138 | -20.6188 | 29.217 | 28.8917 | 28.5286 | 27.9949 | 27.4265 | 26.8549 | 26.3023 | 25.7728 | 25.3444 | 22.4875 | 19.2928 | 16.3402 | 30.6086 | 30.2833 | 29.9202 | 29.3854 | 28.8149 | 28.2402 | 27.6865 | 27.1549 | 26.7233 | 23.8517 | 20.6412 | 17.6802
|  | CIRENCESTER TOWN PRIMARY | EE |  |  |  |  | 35.757 | 35.5065 | 35.2465 | 34.9802 | 34.6086 | 34.2138 | 33.8212 | 33.4307 | 33.1317 | 31.0812 | 28.7507 | 26.6675 | 29.4233 | 29.1591 | 28.8875 | 28.6065 | 28.2075 | 27.7812 | 27.3559 | 26.9338 | 26.6149 | 24.3444 | 21.717 | 19.3359 | 30.8138 | 30.5496 | 30.2759 | 29.9959 | 29.5959 | 29.1686 | 28.7402 | 28.3128 | 27.9928 | 25.7002 | 23.0475 | 20.6591
|  | CIRENCESTER TOWN PRIMARY | HT |  |  |  |  | 35.5654 | 35.257 | 34.9159 | 34.4265 | 33.9044 | 33.3791 | 32.8759 | 32.3938 | 31.9991 | 29.4381 | 26.6138 | 24.0233 | 29.217 | 28.8917 | 28.5286 | 27.9949 | 27.4265 | 26.8549 | 26.3023 | 25.7728 | 25.3444 | 22.4875 | 19.2928 | 16.3402 | 30.6086 | 30.2833 | 29.9202 | 29.3854 | 28.8149 | 28.2402 | 27.6865 | 27.1549 | 26.7233 | 23.8517 | 20.6412 | 17.6802
|  | CIRENCESTER TOWN PRIMARY | HE |  |  |  |  | 35.9791 | 35.8402 | 35.6559 | 35.4633 | 35.257 | 34.9907 | 34.6833 | 34.3833 | 34.1759 | 32.5812 | 30.7054 | -20.6188 | 29.6559 | 29.5149 | 29.3233 | 29.1233 | 28.9107 | 28.6254 | 28.2928 | 27.9665 | 27.7444 | 25.9549 | 23.8054 | 21.8349 | 31.0475 | 30.9065 | 30.7149 | 30.5138 | 30.3012 | 30.0149 | 29.6802 | 29.3528 | 29.1296 | 27.3317 | 25.1738 | 23.197
|  | CIRENCESTER TOWN PRIMARY | CF |  |  |  |  | 36.0875 | 36.0181 | 35.9465 | 35.8528 | 35.7412 | 35.6286 | 35.517 | 35.4086 | 35.297 | 34.3675 | 33.1991 | 32.1507 | 29.7644 | 29.6949 | 29.6233 | 29.5265 | 29.4107 | 29.2917 | 29.177 | 29.0623 | 28.9454 | 27.9191 | 26.5833 | 25.3749 | 31.1559 | 31.0865 | 31.0149 | 30.9181 | 30.8012 | 30.6823 | 30.5665 | 30.4517 | 30.3349 | 29.3044 | 27.9644 | 26.7528
IVER 132KV GSP | CIPPENHAM BSP | CLARENCE ROAD PRIMARY | MINIMUM HEADROOM | SU 95654 76652 | NO | NO | 0 | 52.3347 | 51.8 | 51.2305 | 50.6411 | 50.0305 | 49.4137 | 48.8705 | 48.2126 | 47.1389 | 42.2042 | 37.7432 | -10.5779 | 44.2832 | 42.8179 | 40.9895 | 39.0737 | 37.6347 | 36.6074 | 35.3884 | 34.1379 | 32.9558 | 27.4737 | 22.4726 | 17.7989 | 45.5547 | 44.9642 | 43.4821 | 41.5663 | 40.1253 | 39.0989 | 37.8779 | 36.6284 | 35.4442 | 29.9579 | 24.9526 | 20.2758
|  | CLARENCE ROAD PRIMARY | EE |  |  |  |  | 52.6463 | 52.2042 | 51.7347 | 51.24 | 50.7274 | 50.2316 | 49.7558 | 49.2979 | 48.8905 | 45.1032 | 41.6253 | 38.4632 | 44.6221 | 43.7189 | 42.2863 | 40.5642 | 39.3116 | 38.2126 | 37.1442 | 36.0684 | 35.0705 | 30.6537 | 26.7442 | 23.1516 | 45.8884 | 45.3979 | 44.7789 | 43.0568 | 41.8021 | 40.7053 | 39.6347 | 38.5579 | 37.5589 | 33.1368 | 29.2221 | 25.6274
|  | CLARENCE ROAD PRIMARY | HT |  |  |  |  | 52.3347 | 51.8 | 51.2305 | 50.6411 | 50.0305 | 49.4137 | 48.8705 | 48.2126 | 47.1389 | 42.2042 | 37.7432 | 33.6084 | 44.2832 | 42.8179 | 40.9895 | 39.0737 | 37.6347 | 36.6074 | 35.3884 | 34.1379 | 32.9558 | 27.4737 | 22.4726 | 17.7989 | 45.5547 | 44.9642 | 43.4821 | 41.5663 | 40.1253 | 39.0989 | 37.8779 | 36.6284 | 35.4442 | 29.9579 | 24.9526 | 20.2758
|  | CLARENCE ROAD PRIMARY | HE |  |  |  |  | 53.0337 | 52.7074 | 52.3484 | 51.9611 | 51.5484 | 51.1526 | 50.7789 | 50.4305 | 50.1316 | 49.0242 | 46.5537 | -10.5779 | 45.0379 | 44.6726 | 43.7126 | 42.4758 | 41.4726 | 40.6284 | 39.5337 | 38.76 | 38.0863 | 34.9663 | 32.1621 | 29.6305 | 46.3053 | 45.9389 | 45.5326 | 44.9684 | 43.9653 | 43.12 | 42.0253 | 41.2505 | 40.5768 | 37.4547 | 34.6484 | 32.1147
|  | CLARENCE ROAD PRIMARY | CF |  |  |  |  | 53.2989 | 53.1158 | 52.9242 | 52.7274 | 52.5221 | 52.3137 | 52.1095 | 51.9063 | 51.7032 | 50.7968 | 50.3432 | 50.0905 | 45.3326 | 45.1326 | 44.9211 | 44.6926 | 44.1621 | 43.5095 | 42.9232 | 42.5411 | 42.08 | 39.7537 | 37.7905 | 36.0789 | 46.6011 | 46.4 | 46.1884 | 45.9589 | 45.7232 | 45.4884 | 45.2621 | 45.0326 | 44.5716 | 42.2442 | 40.28 | 38.5674
MELKSHAM GSP | CHIPPENHAM BSP | COCKLEBURY PRIMARY | MINIMUM HEADROOM | ST 92447 73890 | NO | YES | 0 | 53.7537 | 54.0505 | 53.1663 | 52.0926 | 50.7874 | 49.3811 | 48.2211 | 47.2674 | 46.2937 | 43.1737 | 40.5842 | 17.4895 | 47.4147 | 47.1284 | 46.1411 | 44.9295 | 43.4516 | 41.8547 | 40.5421 | 39.4716 | 38.3716 | 34.5663 | 31.7158 | 28.9168 | 48.9053 | 48.6179 | 47.6305 | 46.4211 | 44.9421 | 43.3432 | 42.0295 | 40.9558 | 39.8516 | 36.0147 | 33.1274 | 30.3168
|  | COCKLEBURY PRIMARY | EE |  |  |  |  | 53.7537 | 54.1263 | 53.6663 | 52.6958 | 51.8211 | 50.5147 | 49.4253 | 48.5168 | 47.6442 | 44.7811 | 42.6989 | 40.7379 | 47.4147 | 47.1768 | 46.6789 | 45.58 | 44.2105 | 42.7295 | 41.5 | 40.4863 | 39.5095 | 36.3589 | 34.0947 | 31.8842 | 48.9053 | 48.6663 | 48.1695 | 47.0716 | 45.6989 | 44.2147 | 42.9821 | 41.9621 | 40.9789 | 37.7832 | 35.4642 | 33.2389
|  | COCKLEBURY PRIMARY | HT |  |  |  |  | 54.9568 | 54.0505 | 53.1663 | 52.0926 | 50.7874 | 49.3811 | 48.2211 | 47.2674 | 46.2937 | 43.1737 | 40.5842 | 38.0958 | 48.1453 | 47.1284 | 46.1411 | 44.9295 | 43.4516 | 41.8547 | 40.5421 | 39.4716 | 38.3716 | 34.5663 | 31.7158 | 28.9168 | 49.6347 | 48.6179 | 47.6305 | 46.4211 | 44.9421 | 43.3432 | 42.0295 | 40.9558 | 39.8516 | 36.0147 | 33.1274 | 30.3168
|  | COCKLEBURY PRIMARY | HE |  |  |  |  | 53.9768 | 54.42 | 54.2326 | 53.5232 | 52.4379 | 51.2642 | 50.3021 | 49.5295 | 48.7884 | 46.5895 | 45.1674 | 17.4895 | 47.6379 | 47.4695 | 47.2821 | 46.48 | 45.2411 | 43.8937 | 42.7958 | 41.92 | 41.0779 | 38.6053 | 37.0053 | 35.3368 | 49.1284 | 48.96 | 48.7726 | 47.9716 | 46.7316 | 45.3842 | 44.2853 | 43.4074 | 42.5632 | 40.0747 | 38.4611 | 36.78
|  | COCKLEBURY PRIMARY | CF |  |  |  |  | 54.1316 | 54.6537 | 54.5611 | 54.4653 | 54.36 | 53.9021 | 53.3916 | 52.9547 | 52.4926 | 51.1295 | 50.2989 | 49.3684 | 47.7926 | 47.7032 | 47.6105 | 47.5147 | 47.4105 | 46.8895 | 46.3063 | 45.8095 | 45.2842 | 43.7621 | 42.8347 | 41.7726 | 49.2832 | 49.1937 | 49.1011 | 49.0053 | 48.9 | 48.3789 | 47.7947 | 47.2968 | 46.7716 | 45.2453 | 44.3095 | 43.24
MELKSHAM GSP | FROME BSP | CODFORD PRIMARY | MINIMUM HEADROOM | ST 97372 39559 | YES | YES | 0 | 4.9474 | 4.9095 | 4.8695 | 4.8263 | 4.8358 | 4.8011 | 4.7621 | 2.8611 | 2.8305 | 0.11368 | -1.4126 | -1.4863 | 4.9926 | 4.9295 | 4.8663 | 4.8032 | 4.8305 | 4.7821 | 4.7337 | 2.5916 | 2.5611 | -0.60737 | -2.3842 | -2.4579 | 4.9011 | 4.8516 | 4.8 | 4.7484 | 4.7663 | 4.7253 | 4.6853 | 2.5095 | 2.4789 | -0.69053 | -2.4674 | -2.5411
|  | CODFORD PRIMARY | EE |  |  |  |  | 4.9695 | 4.9389 | 4.9053 | 4.8716 | 4.8358 | 4.8011 | 4.7621 | 4.7147 | 4.6716 | 4.1274 | 2.7653 | -0.016842 | 5.0284 | 4.9853 | 4.9337 | 4.8832 | 4.8305 | 4.7821 | 4.7337 | 4.6842 | 4.6389 | 4.0884 | 2.5 | -0.75789 | 4.9326 | 4.8926 | 4.8516 | 4.8095 | 4.7663 | 4.7253 | 4.6853 | 4.6484 | 4.6147 | 4.0063 | 2.4179 | -0.84105
|  | CODFORD PRIMARY | HT |  |  |  |  | 4.9474 | 4.9095 | 4.8695 | 4.8263 | 5.4053 | 5.3621 | 5.3105 | 2.8611 | 2.8305 | 0.11368 | -1.4126 | -1.4863 | 4.9926 | 4.9295 | 4.8663 | 4.8032 | 5.5863 | 5.5189 | 5.4568 | 2.5916 | 2.5611 | -0.60737 | -2.3842 | -2.4579 | 4.9011 | 4.8516 | 4.8 | 4.7484 | 5.4968 | 5.4326 | 5.3737 | 2.5095 | 2.4789 | -0.69053 | -2.4674 | -2.5411
|  | CODFORD PRIMARY | HE |  |  |  |  | 5 | 4.9779 | 4.9547 | 4.9295 | 4.9021 | 4.8758 | 4.8505 | 4.8284 | 4.8084 | 4.2568 | 2.9232 | 0.64105 | 5.0684 | 5.0421 | 5.0158 | 4.9874 | 4.9547 | 4.9189 | 4.8863 | 4.8568 | 4.8284 | 4.2179 | 2.6579 | -0.57474 | 4.9758 | 4.9484 | 4.9211 | 4.8905 | 4.8589 | 4.8284 | 4.8 | 4.7737 | 4.7505 | 4.1358 | 2.5758 | -0.65789
|  | CODFORD PRIMARY | CF |  |  |  |  | 5.0211 | 5.0105 | 4.9989 | 4.9874 | 4.9747 | 4.9621 | 4.9505 | 4.9379 | 4.9263 | 4.8726 | 5.4653 | 5.4084 | 5.0937 | 5.08 | 5.0663 | 5.0516 | 5.0358 | 5.0211 | 5.0063 | 4.9874 | 4.9674 | 4.8811 | 5.6537 | 5.5516 | 5.0021 | 4.9884 | 4.9726 | 4.9579 | 4.9411 | 4.9242 | 4.9095 | 4.8937 | 4.8779 | 4.8095 | 5.56 | 5.4726
IVER 132KV GSP | DENHAM BSP | COKES LANE PRIMARY | MINIMUM HEADROOM | SU 99240 97483 | NO | NO | 0 | 14.2821 | 14.1758 | 13.9221 | 13.7421 | 13.5621 | 13.3811 | 13.2116 | 13.0505 | 12.8947 | 12.2053 | 11.6137 | 0.71053 | 12.6411 | 12.2916 | 11.92 | 11.7221 | 11.5263 | 11.3274 | 11.14 | 10.9621 | 10.7874 | 10.0021 | 9.3168 | 8.72 | 13.1505 | 12.8053 | 12.4505 | 12.2579 | 12.0674 | 11.8747 | 11.6937 | 11.52 | 11.3516 | 10.5979 | 9.9432 | 9.3705
|  | COKES LANE PRIMARY | EE |  |  |  |  | 14.3537 | 14.2674 | 14.1263 | 13.9842 | 13.8411 | 13.7042 | 13.5684 | 13.4284 | 13.3011 | 12.7684 | 12.3211 | 11.9411 | 12.7758 | 12.4747 | 12.1495 | 11.9937 | 11.8379 | 11.6884 | 11.5411 | 11.3863 | 11.2442 | 10.6368 | 10.1158 | 9.6653 | 13.2895 | 12.9853 | 12.6716 | 12.52 | 12.3684 | 12.2232 | 12.0789 | 11.9295 | 11.7916 | 11.2084 | 10.7116 | 10.2832
|  | COKES LANE PRIMARY | HT |  |  |  |  | 14.2821 | 14.1758 | 13.9221 | 13.7421 | 13.5621 | 13.3811 | 13.2116 | 13.0505 | 12.8947 | 12.2053 | 11.6137 | 11.0832 | 12.6411 | 12.2916 | 11.92 | 11.7221 | 11.5263 | 11.3274 | 11.14 | 10.9621 | 10.7874 | 10.0021 | 9.3168 | 8.72 | 13.1505 | 12.8053 | 12.4505 | 12.2579 | 12.0674 | 11.8747 | 11.6937 | 11.52 | 11.3516 | 10.5979 | 9.9432 | 9.3705
|  | COKES LANE PRIMARY | HE |  |  |  |  | 14.4389 | 14.3811 | 14.3158 | 14.2463 | 14.1726 | 14.0947 | 13.9989 | 13.9011 | 13.8126 | 13.4621 | 13.1821 | 0.71053 | 12.9474 | 12.7095 | 12.4442 | 12.34 | 12.2347 | 12.1305 | 12.0274 | 11.92 | 11.8211 | 11.4232 | 11.0937 | 10.8158 | 13.4663 | 13.2179 | 12.9568 | 12.8547 | 12.7505 | 12.6484 | 12.5474 | 12.4432 | 12.3484 | 11.9642 | 11.6516 | 11.3895
|  | COKES LANE PRIMARY | CF |  |  |  |  | 14.4968 | 14.4663 | 14.4347 | 14.4021 | 14.3695 | 14.3358 | 14.3021 | 14.2674 | 14.2347 | 14.0874 | 13.9358 | 13.7758 | 13.1179 | 12.9947 | 12.8726 | 12.8158 | 12.7589 | 12.7011 | 12.6411 | 12.5779 | 12.5105 | 12.1905 | 11.9516 | 11.7589 | 13.6442 | 13.5158 | 13.3874 | 13.3295 | 13.2705 | 13.2116 | 13.1495 | 13.0842 | 13.0168 | 12.7053 | 12.4758 | 12.2937
LOVEDEAN GSP | PORTSMOUTH BSP | COLLEGE PARK PRIMARY | MINIMUM HEADROOM | SU 65893 02686 | NO | YES | 0 | 17.2368 | 17.0284 | 16.8063 | 16.5747 | 16.3337 | 16.0905 | 15.8737 | 15.6758 | 15.4926 | 14.2 | 12.2758 | -2.2305 | 15.0211 | 14.6168 | 14.2042 | 13.7768 | 13.3505 | 12.9305 | 12.5421 | 12.1758 | 11.7411 | 9.5505 | 7.3674 | 5.3653 | 15.44 | 15.22 | 14.8884 | 14.4768 | 14.0642 | 13.6568 | 13.2811 | 12.9284 | 12.5126 | 10.3316 | 8.1516 | 6.1516
|  | COLLEGE PARK PRIMARY | EE |  |  |  |  | 17.3474 | 17.1705 | 16.9832 | 16.7842 | 16.5768 | 16.3758 | 16.1832 | 15.9958 | 15.8284 | 15.2021 | 13.9842 | 12.6137 | 15.2211 | 14.9611 | 14.6263 | 14.2832 | 13.9253 | 13.5832 | 13.2537 | 12.9337 | 12.6358 | 11.0105 | 9.2832 | 7.7137 | 15.5589 | 15.3737 | 15.1779 | 14.96 | 14.6137 | 14.2821 | 13.9632 | 13.6526 | 13.3642 | 11.7905 | 10.0642 | 8.4968
|  | COLLEGE PARK PRIMARY | HT |  |  |  |  | 17.2368 | 17.0284 | 16.8063 | 16.5747 | 16.3337 | 16.0905 | 15.8737 | 15.6758 | 15.4926 | 14.2 | 12.2758 | 10.5011 | 15.0211 | 14.6168 | 14.2042 | 13.7768 | 13.3505 | 12.9305 | 12.5421 | 12.1758 | 11.7411 | 9.5505 | 7.3674 | 5.3653 | 15.44 | 15.22 | 14.8884 | 14.4768 | 14.0642 | 13.6568 | 13.2811 | 12.9284 | 12.5126 | 10.3316 | 8.1516 | 6.1516
|  | COLLEGE PARK PRIMARY | HE |  |  |  |  | 17.4884 | 17.3526 | 17.2021 | 17.04 | 16.8684 | 16.7032 | 16.5474 | 16.4032 | 16.2779 | 15.8474 | 15.5874 | -2.2305 | 15.3821 | 15.2411 | 15.08 | 14.9063 | 14.66 | 14.4137 | 14.1789 | 13.96 | 13.7632 | 12.9632 | 11.8674 | 10.7621 | 15.7126 | 15.5716 | 15.4158 | 15.2484 | 15.0716 | 14.9021 | 14.7421 | 14.5926 | 14.4411 | 13.6684 | 12.6368 | 11.5421
|  | COLLEGE PARK PRIMARY | CF |  |  |  |  | 17.5874 | 17.5074 | 17.4232 | 17.3368 | 17.2474 | 17.1558 | 17.0663 | 16.9768 | 16.8884 | 16.4916 | 16.2926 | 16.1811 | 15.4853 | 15.4 | 15.3116 | 15.2168 | 15.1189 | 15.0063 | 14.8474 | 14.6884 | 14.5305 | 13.7979 | 13.0989 | 12.3558 | 15.8147 | 15.7305 | 15.6421 | 15.5516 | 15.4579 | 15.3632 | 15.2695 | 15.1758 | 15.0832 | 14.4895 | 13.8284 | 13.1326
EALING GSP |  | COPLEY DENE PRIMARY | MINIMUM HEADROOM | TQ 17445 80798 | NO | YES | 0 | 46.6189 | 46.1589 | 45.6705 | 83.8568 | 83.3221 | 82.7811 | 82.0326 | 81.2421 | 80.4905 | 76.9832 | 73.3768 | 25.0495 | 38.5042 | 37.4379 | 36.0316 | 73.2189 | 71.7284 | 70.7168 | 69.7895 | 68.9379 | 68.1263 | 64.3042 | 60.3011 | 56.4442 | 39.9989 | 39.5032 | 38.5642 | 75.7621 | 74.2705 | 73.26 | 72.3337 | 71.4832 | 70.6716 | 66.8537 | 62.8547 | 59.0032
|  | COPLEY DENE PRIMARY | EE |  |  |  |  | 46.8926 | 46.5158 | 46.1137 | 84.3863 | 83.9389 | 83.5042 | 83.0832 | 82.6737 | 82.3053 | 80.0484 | 77.5263 | 75.1832 | 39.0358 | 38.3895 | 37.2989 | 74.8074 | 73.5284 | 72.7137 | 71.9495 | 71.2211 | 70.5505 | 67.6979 | 64.9063 | 62.28 | 40.2958 | 39.8947 | 39.4516 | 77.3316 | 76.0747 | 75.2547 | 74.4905 | 73.7621 | 73.0937 | 70.2432 | 67.4547 | 64.8326
|  | COPLEY DENE PRIMARY | HT |  |  |  |  | 46.6189 | 46.1589 | 45.6705 | 83.8568 | 83.3221 | 82.7811 | 82.0326 | 81.2421 | 80.4905 | 76.9832 | 73.3768 | 69.9347 | 38.5042 | 37.4379 | 36.0316 | 73.2189 | 71.7284 | 70.7168 | 69.7895 | 68.9379 | 68.1263 | 64.3042 | 60.3011 | 56.4442 | 39.9989 | 39.5032 | 38.5642 | 75.7621 | 74.2705 | 73.26 | 72.3337 | 71.4832 | 70.6716 | 66.8537 | 62.8547 | 59.0032
|  | COPLEY DENE PRIMARY | HE |  |  |  |  | 47.1663 | 46.8653 | 46.5316 | 84.8737 | 84.4916 | 84.1263 | 83.7821 | 83.4611 | 83.1832 | 82.2211 | 81.5284 | 25.0495 | 39.4716 | 39.0842 | 38.3926 | 76.0937 | 75.0084 | 74.38 | 73.8084 | 73.2937 | 72.8337 | 71.0484 | 69.3147 | 67.7453 | 40.5947 | 40.2768 | 39.9095 | 78.2137 | 77.5189 | 76.9263 | 76.3621 | 75.8442 | 75.3811 | 73.5895 | 71.8579 | 70.2916
|  | COPLEY DENE PRIMARY | CF |  |  |  |  | 47.3611 | 47.1726 | 46.9779 | 85.4758 | 85.2674 | 85.0547 | 84.8453 | 84.6379 | 84.4305 | 83.5074 | 83.0411 | 82.78 | 39.6779 | 39.48 | 39.2211 | 77.5621 | 77.1463 | 76.7684 | 76.3705 | 75.9432 | 75.5095 | 73.4695 | 72.2011 | 71.1 | 40.8011 | 40.6032 | 40.3926 | 78.8726 | 78.6463 | 78.4242 | 78.2042 | 77.9832 | 77.7621 | 76.0221 | 74.7421 | 73.6421
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | CORDWALLIS PRIMARY | MINIMUM HEADROOM | SU 88285 81857 | NO | YES | 0 | 36.6947 | 36.3716 | 36.0284 | 35.6726 | 35.2958 | 34.7368 | 34.2253 | 33.5937 | 32.9979 | 30.2316 | 27.7116 | 1.7211 | 30.4368 | 29.5421 | 28.5526 | 27.4589 | 26.8305 | 26.2221 | 25.6621 | 24.9421 | 24.2632 | 21.1295 | 18.2989 | 15.6453 | 31.8411 | 30.9789 | 30.0263 | 28.9747 | 28.3611 | 27.7674 | 27.2032 | 26.4758 | 25.7895 | 22.6211 | 19.7558 | 17.0947
|  | CORDWALLIS PRIMARY | EE |  |  |  |  | 36.8853 | 36.6189 | 36.3368 | 36.04 | 35.7337 | 35.4379 | 35.1558 | 34.66 | 34.1526 | 31.9789 | 30.0347 | 28.2737 | 30.8516 | 30.0811 | 29.2147 | 28.2389 | 27.7221 | 27.2274 | 26.7579 | 26.14 | 25.5621 | 23.0526 | 20.8558 | 18.8505 | 32.2442 | 31.5011 | 30.6684 | 29.7316 | 29.2263 | 28.7432 | 28.2853 | 27.6842 | 27.1011 | 24.5632 | 22.3389 | 20.3063
|  | CORDWALLIS PRIMARY | HT |  |  |  |  | 36.6947 | 36.3716 | 36.0284 | 35.6726 | 35.2958 | 34.7368 | 34.2253 | 33.5937 | 32.9979 | 30.2316 | 27.7116 | 25.3663 | 30.4368 | 29.5421 | 28.5526 | 27.4589 | 26.8305 | 26.2221 | 25.6621 | 24.9421 | 24.2632 | 21.1295 | 18.2989 | 15.6453 | 31.8411 | 30.9789 | 30.0263 | 28.9747 | 28.3611 | 27.7674 | 27.2032 | 26.4758 | 25.7895 | 22.6211 | 19.7558 | 17.0947
|  | CORDWALLIS PRIMARY | HE |  |  |  |  | 37.1253 | 36.9326 | 36.72 | 36.4905 | 36.2463 | 36.0126 | 35.7926 | 35.5863 | 35.4095 | 34.0526 | 32.7411 | 1.7211 | 31.4726 | 30.9326 | 30.3095 | 29.6074 | 28.8474 | 28.2853 | 27.9474 | 27.5316 | 27.1495 | 25.3926 | 23.8316 | 22.4358 | 32.5621 | 32.3221 | 31.7221 | 31.0484 | 30.3168 | 29.7737 | 29.4421 | 29.0389 | 28.6674 | 26.9253 | 25.3432 | 23.9274
|  | CORDWALLIS PRIMARY | CF |  |  |  |  | 37.2916 | 37.1863 | 37.0768 | 36.9632 | 36.8463 | 36.7263 | 36.6084 | 36.4926 | 36.3758 | 35.8558 | 35.5779 | 34.7958 | 31.7579 | 31.58 | 31.2579 | 30.9084 | 30.5347 | 30.2147 | 29.9947 | 29.7768 | 29.5158 | 28.2063 | 27.1095 | 26.1611 | 32.74 | 32.6263 | 32.5042 | 32.3011 | 31.9421 | 31.6337 | 31.4189 | 31.2074 | 30.9547 | 29.6905 | 28.6411 | 27.6968
MANNINGTON GSP | LYTCHETT BSP | CORFE MULLEN PRIMARY | MINIMUM HEADROOM | SY 98583 96071 | NO | YES | 13.8947 | 18.7295 | 18.6674 | 18.2337 | 17.3716 | 16.2442 | 15.0137 | 13.9758 | 13.4074 | 12.8674 | 8.9937 | 6.0389 | -8.7705 | 16.2684 | 15.3547 | 14.5442 | 13.5979 | 12.3526 | 10.9884 | 9.8432 | 9.2442 | 8.6768 | 4.5768 | 1.2474 | -1.3053 | 16.6053 | 15.7116 | 14.9032 | 13.9547 | 12.7021 | 11.3295 | 10.1747 | 9.5653 | 8.9874 | 4.68 | 1.4095 | -1.1758
|  | CORFE MULLEN PRIMARY | EE |  |  |  |  | 18.9421 | 18.6674 | 19.0621 | 18.3337 | 17.3253 | 16.2095 | 15.1126 | 14.42 | 13.9368 | 10.4305 | 7.9316 | 6.1516 | 16.7716 | 16.0842 | 15.4589 | 14.6568 | 13.5411 | 12.3011 | 11.0832 | 10.3389 | 9.8379 | 6.0358 | 3.3916 | 1.4347 | 17.0958 | 16.4263 | 15.8158 | 15.0137 | 13.8895 | 12.6389 | 11.4074 | 10.6505 | 10.1347 | 6.2368 | 3.4821 | 1.4884
|  | CORFE MULLEN PRIMARY | HT |  |  |  |  | 18.7295 | 18.9758 | 18.2337 | 17.3716 | 16.2442 | 15.0137 | 13.9758 | 13.4074 | 12.8674 | 8.9937 | 6.0389 | 3.7242 | 16.2684 | 15.3547 | 14.5442 | 13.5979 | 12.3526 | 10.9884 | 9.8432 | 9.2442 | 8.6768 | 4.5768 | 1.2474 | -1.3053 | 16.6053 | 15.7116 | 14.9032 | 13.9547 | 12.7021 | 11.3295 | 10.1747 | 9.5653 | 8.9874 | 4.68 | 1.4095 | -1.1758
|  | CORFE MULLEN PRIMARY | HE |  |  |  |  | 19.2116 | 19.0242 | 18.8158 | 18.5916 | 18.3116 | 17.4747 | 16.5189 | 16.0305 | 15.7189 | 13.0737 | 11.4716 | -8.7705 | 17.3421 | 16.8274 | 16.3621 | 15.7379 | 14.7853 | 13.7095 | 12.6316 | 12.1011 | 11.7737 | 8.8221 | 7.0432 | 5.6747 | 17.6074 | 17.1537 | 16.6989 | 16.0926 | 15.1379 | 14.0568 | 12.9716 | 12.4358 | 12.1021 | 9.1095 | 7.2989 | 5.9021
|  | CORFE MULLEN PRIMARY | CF |  |  |  |  | 19.3947 | 19.3 | 19.2011 | 19.0979 | 18.9811 | 18.8632 | 18.7463 | 18.6316 | 18.5137 | 16.4021 | 15.3232 | 14.5305 | 17.5989 | 17.4895 | 17.3116 | 17.0779 | 16.7295 | 16.3116 | 15.9537 | 15.5895 | 15.2063 | 12.4737 | 11.2726 | 10.3895 | 17.8021 | 17.7 | 17.5947 | 17.3958 | 17.0558 | 16.6484 | 16.2979 | 15.9432 | 15.5505 | 12.8053 | 11.5863 | 10.6842
MELKSHAM GSP | NORRINGTON BSP | CORSHAM PRIMARY | MINIMUM HEADROOM | ST 86766 69583 | NO | YES | 0.20842 | 11.8715 | 11.6631 | 11.442 | 11.2041 | 10.7525 | 10.3546 | 9.9925 | 9.6494 | 9.2904 | 7.3936 | 5.4515 | -11.3443 | 9.0641 | 8.5736 | 8.0157 | 7.5178 | 7.0367 | 6.622 | 6.2431 | 5.8831 | 5.5009 | 3.4557 | 1.3315 | -0.68011 | 9.8231 | 9.3599 | 8.8209 | 8.3388 | 7.8641 | 7.4494 | 7.0641 | 6.6967 | 6.3062 | 4.2083 | 2.0283 | -0.0064211
|  | CORSHAM PRIMARY | EE |  |  |  |  | 11.9915 | 11.8178 | 11.6336 | 11.4399 | 11.2231 | 10.9473 | 10.6283 | 10.3125 | 10.0199 | 8.4599 | 6.8167 | 5.3999 | 9.3188 | 8.9104 | 8.4367 | 8.0125 | 7.6073 | 7.2725 | 6.9462 | 6.6231 | 6.3241 | 4.6925 | 2.942 | 1.3388 | 9.9431 | 9.6936 | 9.2294 | 8.8167 | 8.4157 | 8.0767 | 7.7462 | 7.4178 | 7.1136 | 5.4167 | 3.5883 | 1.9599
|  | CORSHAM PRIMARY | HT |  |  |  |  | 11.8715 | 11.6631 | 11.442 | 11.2041 | 10.7525 | 10.3546 | 9.9925 | 9.6494 | 9.2904 | 7.3936 | 5.4515 | 3.6746 | 9.0641 | 8.5736 | 8.0157 | 7.5178 | 7.0367 | 6.622 | 6.2431 | 5.8831 | 5.5009 | 3.4557 | 1.3315 | -0.68011 | 9.8231 | 9.3599 | 8.8209 | 8.3388 | 7.8641 | 7.4494 | 7.0641 | 6.6967 | 6.3062 | 4.2083 | 2.0283 | -0.0064211
|  | CORSHAM PRIMARY | HE |  |  |  |  | 12.1525 | 12.0304 | 11.8946 | 11.7494 | 11.5778 | 11.4167 | 11.2631 | 11.1167 | 10.9873 | 10.1515 | 9.1125 | -11.3443 | 9.5883 | 9.3557 | 8.9988 | 8.6841 | 8.3746 | 8.1409 | 7.9188 | 7.7062 | 7.5157 | 6.4662 | 5.3041 | 4.0988 | 10.1041 | 9.982 | 9.7841 | 9.4704 | 9.1631 | 8.9294 | 8.7052 | 8.4915 | 8.2967 | 7.2473 | 6.0694 | 4.8431
|  | CORSHAM PRIMARY | CF |  |  |  |  | 12.2652 | 12.2009 | 12.1336 | 12.0641 | 11.9852 | 11.9041 | 11.8252 | 11.7462 | 11.6704 | 11.3188 | 10.9831 | 10.3136 | 9.7009 | 9.6367 | 9.4978 | 9.3388 | 9.1715 | 9.0188 | 8.882 | 8.7494 | 8.6136 | 7.9788 | 7.3167 | 6.5588 | 10.2167 | 10.1525 | 10.0852 | 10.0157 | 9.9367 | 9.7978 | 9.6567 | 9.5209 | 9.3883 | 8.7567 | 8.1041 | 7.3515
EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD PRIMARY | MINIMUM HEADROOM | SP 59021 31128 | YES | YES | 0.12105 | 4.3218 | 4.2239 | 4.1197 | 3.8755 | 3.3608 | 2.8576 | 2.2334 | 0.079737 | -0.043421 | -1.4666 | -3.3508 | -3.8908 | 3.5892 | 3.4829 | 3.3734 | 3.0966 | 2.525 | 1.9671 | 1.2682 | -1.2382 | -1.3424 | -2.7718 | -4.7203 | -5.2382 | 3.6176 | 3.5124 | 3.4008 | 3.1282 | 2.5492 | 1.9829 | 1.2766 | -1.2097 | -1.3329 | -2.8771 | -4.9497 | -5.5224
|  | COTTISFORD PRIMARY | EE |  |  |  |  | 4.3882 | 4.3082 | 4.2197 | 4.1345 | 3.9924 | 3.8334 | 3.6682 | 3.4966 | 3.3208 | 0.925 | -1.1792 | -2.2476 | 3.6608 | 3.5755 | 3.4839 | 3.3934 | 3.2597 | 3.1166 | 2.9682 | 2.8134 | 2.6524 | 0.16289 | -1.9497 | -3.0887 | 3.6892 | 3.6029 | 3.5103 | 3.4197 | 3.2724 | 3.1082 | 2.9387 | 2.7629 | 2.5818 | -0.065526 | -2.3613 | -3.5497
|  | COTTISFORD PRIMARY | HT |  |  |  |  | 4.3218 | 4.2239 | 4.1197 | 3.8755 | 3.3608 | 2.8576 | 2.2334 | 0.079737 | -0.043421 | -1.4666 | -3.3508 | -3.8908 | 3.5892 | 3.4829 | 3.3734 | 3.0966 | 2.525 | 1.9671 | 1.2682 | -1.2382 | -1.3424 | -2.7718 | -4.7203 | -5.2382 | 3.6176 | 3.5124 | 3.4008 | 3.1282 | 2.5492 | 1.9829 | 1.2766 | -1.2097 | -1.3329 | -2.8771 | -4.9497 | -5.5224
|  | COTTISFORD PRIMARY | HE |  |  |  |  | 4.4745 | 4.4271 | 4.3734 | 4.3145 | 4.2113 | 4.1155 | 4.0197 | 3.9239 | 3.8313 | 2.1439 | 0.90816 | -3.4466 | 3.7555 | 3.7039 | 3.6471 | 3.585 | 3.4892 | 3.3997 | 3.3113 | 3.2218 | 3.1376 | 1.2892 | -0.061316 | -1.0087 | 3.7766 | 3.7282 | 3.6745 | 3.6124 | 3.5061 | 3.4082 | 3.3092 | 3.2092 | 3.1155 | 1.2155 | -0.17605 | -1.1634
|  | COTTISFORD PRIMARY | CF |  |  |  |  | 4.5208 | 4.4882 | 4.4608 | 4.4313 | 4.3797 | 4.3271 | 4.2734 | 4.2229 | 4.1745 | 3.9313 | 3.2545 | 2.6124 | 3.8039 | 3.7692 | 3.7397 | 3.7071 | 3.6576 | 3.6071 | 3.5576 | 3.5092 | 3.4597 | 3.2313 | 2.4913 | 1.7976 | 3.8229 | 3.7903 | 3.7629 | 3.7324 | 3.6797 | 3.625 | 3.5703 | 3.5176 | 3.4661 | 3.2124 | 2.4513 | 1.7313
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | COURAGES PRIMARY | MINIMUM HEADROOM | SU 70990 69570 | NO | YES | 2.1053 | 33.6484 | 33.5979 | 33.5463 | 33.4147 | 31.0853 | 30.5 | 29.9211 | 29.3179 | 29.1042 | 28.6579 | 28.1453 | -18.5042 | 29.7305 | 29.6768 | 29.3116 | 28.7084 | 26.66 | 25.9347 | 25.2158 | 24.5116 | 24.2684 | 23.7747 | 23.1968 | 22.6179 | 30.5074 | 30.4537 | 30.3737 | 29.8116 | 27.3716 | 26.6726 | 25.9568 | 25.2537 | 25.0105 | 24.5179 | 23.94 | 23.3621
|  | COURAGES PRIMARY | EE |  |  |  |  | 33.6768 | 33.6358 | 33.5926 | 33.5368 | 31.2389 | 30.6705 | 30.1084 | 29.5316 | 29.3421 | 29.0326 | 28.6642 | 28.3032 | 29.7611 | 29.7179 | 29.4274 | 28.8463 | 26.8316 | 26.1295 | 25.4305 | 24.7484 | 24.5316 | 24.1937 | 23.7768 | 23.3663 | 30.5379 | 30.4947 | 30.4242 | 29.9484 | 27.5432 | 26.8621 | 26.1716 | 25.4895 | 25.2737 | 24.9358 | 24.52 | 24.1105
|  | COURAGES PRIMARY | HT |  |  |  |  | 33.6484 | 33.5979 | 33.5463 | 33.4147 | 31.0853 | 30.5 | 29.9211 | 29.3179 | 29.1042 | 28.6579 | 28.1453 | 27.6368 | 29.7305 | 29.6768 | 29.3116 | 28.7084 | 26.66 | 25.9347 | 25.2158 | 24.5116 | 24.2684 | 23.7747 | 23.1968 | 22.6179 | 30.5074 | 30.4537 | 30.3737 | 29.8116 | 27.3716 | 26.6726 | 25.9568 | 25.2537 | 25.0105 | 24.5179 | 23.94 | 23.3621
|  | COURAGES PRIMARY | HE |  |  |  |  | 33.7095 | 33.6768 | 33.6432 | 33.6042 | 32.2484 | 31.6979 | 31.1579 | 30.6305 | 30.4705 | 30.2663 | 29.9895 | -18.5042 | 29.7958 | 29.7621 | 29.5505 | 28.9905 | 27.6716 | 26.9853 | 26.3116 | 25.6537 | 25.4589 | 25.2274 | 24.9137 | 24.5821 | 30.5726 | 30.5389 | 30.4789 | 30.0916 | 28.5684 | 27.9074 | 27.2568 | 26.6242 | 26.4347 | 26.2063 | 25.8926 | 25.5621
|  | COURAGES PRIMARY | CF |  |  |  |  | 33.7326 | 33.7137 | 33.6937 | 33.6747 | 33.6537 | 33.6326 | 33.4126 | 33.1263 | 33.0295 | 32.8568 | 32.7253 | 32.5905 | 29.82 | 29.8 | 29.7684 | 29.6158 | 29.3274 | 29.0116 | 28.6768 | 28.3253 | 28.2105 | 28.0189 | 27.8674 | 27.7053 | 30.5968 | 30.5768 | 30.5453 | 30.5126 | 30.4221 | 30.1116 | 29.7842 | 29.4389 | 29.3263 | 29.1358 | 28.9863 | 28.8274
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | COVE PRIMARY | MINIMUM HEADROOM | SU 85415 55937 | NO | YES | 0 | 26.1526 | 25.9168 | 25.2053 | 24.3389 | 23.32 | 22.5063 | 21.6842 | 20.9705 | 20.28 | 17.1053 | 22.8968 | 0.10211 | 23.5284 | 22.5011 | 21.6979 | 20.7253 | 19.5758 | 18.6684 | 17.7442 | 16.9442 | 16.1663 | 12.5789 | 11.0305 | 9.4895 | 24.0674 | 23.0968 | 22.2947 | 21.3221 | 20.1726 | 19.2642 | 18.3389 | 17.5389 | 16.7621 | 13.1716 | 18.3632 | 17.5221
|  | COVE PRIMARY | EE |  |  |  |  | 26.2916 | 26.0979 | 25.6568 | 24.8695 | 23.9316 | 23.2105 | 22.4484 | 21.7884 | 21.1526 | 27.9474 | 26.7589 | 25.7179 | 23.8337 | 22.8968 | 22.1884 | 21.3021 | 20.24 | 19.4316 | 18.5726 | 17.8305 | 17.1147 | 27.4232 | 26.9979 | 26.4316 | 24.3611 | 23.4779 | 22.7853 | 21.8989 | 20.8358 | 20.0263 | 19.1674 | 18.4274 | 17.7105 | 29.5221 | 29.0926 | 28.7821
|  | COVE PRIMARY | HT |  |  |  |  | 26.1526 | 25.9168 | 25.2053 | 24.3389 | 23.32 | 22.5063 | 21.6842 | 20.9705 | 20.28 | 17.1053 | 24.6232 | 24.0684 | 23.5284 | 22.5011 | 21.6979 | 20.7253 | 19.5758 | 18.6684 | 17.7442 | 16.9442 | 16.1663 | 12.5789 | 11.0305 | 9.4895 | 24.0674 | 23.0968 | 22.2947 | 21.3221 | 20.1726 | 19.2642 | 18.3389 | 17.5389 | 16.7621 | 13.1716 | 18.3632 | 17.5221
|  | COVE PRIMARY | HE |  |  |  |  | 26.4779 | 26.34 | 26.1884 | 25.5779 | 24.7368 | 24.1126 | 23.4442 | 22.8789 | 22.3379 | 27.4505 | 27.2032 | 0.10211 | 24.2432 | 23.4305 | 22.8432 | 22.0726 | 21.1158 | 20.4116 | 19.6558 | 19.0168 | 18.4042 | 17.4642 | 16.7558 | 16.1642 | 24.7358 | 23.9905 | 23.4347 | 22.6695 | 21.7126 | 21.0084 | 20.2505 | 19.6126 | 18.9989 | 21.3179 | 20.8589 | 20.5053
|  | COVE PRIMARY | CF |  |  |  |  | 26.6042 | 26.5326 | 26.4579 | 26.3811 | 26.3011 | 26.1611 | 25.8084 | 25.4842 | 25.1421 | 23.4695 | 22.8968 | 22.4274 | 24.48 | 24.1442 | 23.8568 | 23.4989 | 23.0758 | 22.7232 | 22.3242 | 21.9558 | 21.5695 | 19.6684 | 19.0253 | 18.4916 | 24.8853 | 24.6663 | 24.3937 | 24.0568 | 23.6589 | 23.3211 | 22.9211 | 22.5537 | 22.1663 | 20.2642 | 19.6221 | 19.0874
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES PRIMARY | MINIMUM HEADROOM | SP 56113 03074 | NO | YES | 0 | 35.8495 | 34.7189 | 33.5537 | 32.2147 | 32.3137 | 31.0895 | 30.0105 | 28.8853 | 27.7411 | 27.1305 | 29.9411 | -15.1053 | 28.0063 | 26.74 | 25.4368 | 23.9305 | 24.0453 | 22.6874 | 21.5011 | 20.26 | 18.9863 | 18.2295 | 21.2958 | 19.6379 | 29.1021 | 27.8358 | 26.5337 | 25.0295 | 25.1358 | 23.7737 | 22.58 | 21.3295 | 20.0474 | 19.2842 | 22.3674 | 20.6979
|  | COWES PRIMARY | EE |  |  |  |  | 36.2621 | 35.6221 | 34.6926 | 33.5737 | 32.3137 | 31.0895 | 30.0105 | 28.8853 | 27.7411 | 104.0705 | 102.9284 | 102.2084 | 28.7389 | 27.7579 | 26.7211 | 25.4611 | 24.0453 | 22.6874 | 21.5011 | 20.26 | 18.9863 | 121.88 | 120.8779 | 120.2011 | 29.8358 | 28.8526 | 27.8168 | 26.5568 | 25.1358 | 23.7737 | 22.58 | 21.3295 | 20.0474 | 113.7589 | 112.6284 | 111.5158
|  | COWES PRIMARY | HT |  |  |  |  | 35.8495 | 34.7189 | 33.5537 | 32.2147 | 106.6937 | 106.1389 | 105.6474 | 105.1937 | 104.7737 | 103.0021 | 101.6021 | 100.5747 | 28.0063 | 26.74 | 25.4368 | 23.9305 | 124.3168 | 123.7716 | 123.2916 | 122.8505 | 122.4432 | 120.7579 | 119.4589 | 116.3895 | 29.1021 | 27.8358 | 26.5337 | 25.0295 | 116.3653 | 115.8116 | 115.32 | 114.8684 | 114.4495 | 112.6853 | 110.8442 | 106.4284
|  | COWES PRIMARY | HE |  |  |  |  | 36.6221 | 36.3442 | 35.8547 | 34.9421 | 33.8695 | 32.8779 | 32.0074 | 31.1084 | 30.1758 | 27.1305 | 105.2716 | -15.1053 | 29.5263 | 28.8042 | 28.0032 | 26.9695 | 25.7558 | 24.6347 | 23.6695 | 22.6674 | 21.6189 | 18.2295 | 123.0095 | 122.6642 | 30.6368 | 29.9011 | 29.0979 | 28.0663 | 26.8495 | 25.7263 | 24.7579 | 23.7516 | 22.7 | 19.2842 | 114.9537 | 114.5747
|  | COWES PRIMARY | CF |  |  |  |  | 36.8737 | 36.7253 | 36.5716 | 36.4126 | 36.24 | 36.0295 | 35.5842 | 35.1116 | 34.5884 | 31.6358 | 29.9411 | 28.4874 | 30.3821 | 30.0432 | 29.6737 | 29.2358 | 28.7411 | 28.2147 | 27.7147 | 27.1811 | 26.5863 | 23.2126 | 21.2958 | 19.6379 | 31.5126 | 31.1674 | 30.7905 | 30.3442 | 29.8379 | 29.3053 | 28.8042 | 28.2695 | 27.6737 | 24.2947 | 22.3674 | 20.6979
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL PRIMARY | MINIMUM HEADROOM | SP 56113 03074 | NO | YES | 0 | 87.6853 | 87.2832 | 86.8589 | 86.4158 | 86.2737 | 83.9389 | 82.0095 | 80.4295 | 79.1474 | 74.6747 | 71.0379 | 20.3537 | 79.6611 | 78.8979 | 78.1116 | 76.9495 | 75.7642 | 72.9084 | 70.6684 | 68.8484 | 67.3821 | 62.4211 | 58.3958 | 56.0758 | 81.4905 | 80.7284 | 79.94 | 78.7789 | 77.54 | 74.7253 | 72.4779 | 70.6516 | 69.1779 | 64.1379 | 60.0684 | 57.5484
|  | COWLEY LOCAL PRIMARY | EE |  |  |  |  | 87.9063 | 87.5716 | 87.2137 | 86.8379 | 86.4347 | 83.9389 | 82.0095 | 80.4295 | 79.1474 | 75.7926 | 72.7305 | 71.0768 | 80.5989 | 79.6747 | 78.8737 | 77.7442 | 76.1589 | 72.9084 | 70.6684 | 68.8484 | 67.3821 | 64.6116 | 61.1989 | 59.3747 | 82.3663 | 81.5032 | 80.7032 | 79.5726 | 77.9821 | 74.7253 | 72.4779 | 70.6516 | 69.1779 | 66.8411 | 63.3674 | 61.5253
|  | COWLEY LOCAL PRIMARY | HT |  |  |  |  | 87.6853 | 87.2832 | 86.8589 | 86.4158 | 86.2737 | 85.8137 | 84.3116 | 82.8895 | 81.5284 | 74.6747 | 71.0379 | 68.7611 | 79.6611 | 78.8979 | 78.1116 | 76.9495 | 75.7642 | 75.2905 | 73.5737 | 71.9463 | 70.3874 | 62.4211 | 58.3958 | 56.0758 | 81.4905 | 80.7284 | 79.94 | 78.7789 | 77.54 | 77.0621 | 75.34 | 73.7063 | 72.1411 | 64.1379 | 60.0684 | 57.5484
|  | COWLEY LOCAL PRIMARY | HE |  |  |  |  | 88.1905 | 87.9411 | 87.6663 | 87.3674 | 87.04 | 85.3674 | 83.5905 | 82.2505 | 81.1463 | 76.0874 | 73.9337 | 20.3537 | 81.2558 | 80.5295 | 79.9316 | 79.0021 | 77.6032 | 74.4821 | 72.4053 | 70.8516 | 69.5737 | 63.8284 | 61.3958 | 60.4042 | 82.6716 | 82.36 | 81.7611 | 80.8326 | 79.4295 | 76.3042 | 74.2242 | 72.6663 | 71.3853 | 65.3884 | 62.9421 | 61.9337
|  | COWLEY LOCAL PRIMARY | CF |  |  |  |  | 88.4 | 88.2621 | 88.1179 | 87.9695 | 87.8105 | 87.6484 | 87.4874 | 87.3295 | 87.1716 | 82.26 | 81.1211 | 80.4505 | 81.8979 | 81.7453 | 81.5453 | 81.1232 | 80.5021 | 79.8242 | 78.9874 | 77.8968 | 76.7221 | 70.8011 | 69.5253 | 68.7747 | 82.9158 | 82.7716 | 82.62 | 82.4558 | 82.2705 | 81.6505 | 80.8126 | 79.72 | 78.5442 | 72.6147 | 71.28 | 70.52
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | COXMOOR WOOD PRIMARY | MINIMUM HEADROOM | SU 78275 50779 | YES | YES | 0 | 13.4828 | 13.3407 | 13.1891 | 13.0343 | 12.8607 | 12.5764 | 12.1101 | 11.9638 | 11.6743 | 10.2933 | 8.7122 | -1.5972 | 11.3743 | 11.0101 | 10.7059 | 10.3754 | 10.0322 | 9.6607 | 9.1438 | 9.0017 | 8.688 | 7.1975 | 5.4596 | 3.9964 | 12.2491 | 11.8859 | 11.5807 | 11.2501 | 10.9028 | 10.527 | 10.0059 | 9.8585 | 9.5407 | 8.0164 | 6.2407 | 4.7617
|  | COXMOOR WOOD PRIMARY | EE |  |  |  |  | 13.5691 | 13.4512 | 13.327 | 13.1975 | 13.0512 | 12.9038 | 12.7628 | 12.5343 | 12.287 | 11.1133 | 9.7901 | 8.6985 | 11.5585 | 11.2501 | 11.0154 | 10.7575 | 10.4859 | 10.1891 | 9.9196 | 9.6354 | 9.3743 | 8.1343 | 6.7059 | 5.4775 | 12.4343 | 12.1249 | 11.8901 | 11.6322 | 11.3564 | 11.0554 | 10.7785 | 10.4891 | 10.2196 | 8.9333 | 7.4512 | 6.2059
|  | COXMOOR WOOD PRIMARY | HT |  |  |  |  | 13.4828 | 13.3407 | 13.1891 | 13.0343 | 12.8607 | 12.5764 | 12.1101 | 11.9638 | 11.6743 | 10.2933 | 8.7122 | 7.408 | 11.3743 | 11.0101 | 10.7059 | 10.3754 | 10.0322 | 9.6607 | 9.1438 | 9.0017 | 8.688 | 7.1975 | 5.4596 | 3.9964 | 12.2491 | 11.8859 | 11.5807 | 11.2501 | 10.9028 | 10.527 | 10.0059 | 9.8585 | 9.5407 | 8.0164 | 6.2407 | 4.7617
|  | COXMOOR WOOD PRIMARY | HE |  |  |  |  | 13.6807 | 13.6007 | 13.5112 | 13.4133 | 13.3007 | 13.1933 | 13.0901 | 12.9933 | 12.908 | 12.2585 | 11.3333 | -1.5972 | 11.8028 | 11.5722 | 11.4112 | 11.2207 | 11.0185 | 10.7933 | 10.5922 | 10.3817 | 10.1922 | 9.328 | 8.288 | 7.3175 | 12.6785 | 12.448 | 12.287 | 12.0964 | 11.8901 | 11.6638 | 11.4596 | 11.2459 | 11.0522 | 10.1701 | 9.1143 | 8.1301
|  | COXMOOR WOOD PRIMARY | CF |  |  |  |  | 13.7564 | 13.7143 | 13.6701 | 13.6249 | 13.5733 | 13.5196 | 13.4691 | 13.4164 | 13.3659 | 13.1333 | 12.8501 | 12.3143 | 12.0585 | 11.9322 | 11.847 | 11.7512 | 11.6501 | 11.5343 | 11.4259 | 11.307 | 11.187 | 10.6007 | 9.9396 | 9.3312 | 12.7807 | 12.7385 | 12.6943 | 12.627 | 12.5249 | 12.407 | 12.2985 | 12.1764 | 12.0564 | 11.4638 | 10.7943 | 10.1775
MANNINGTON GSP | LYTCHETT BSP | CREEKMOOR PRIMARY | MINIMUM HEADROOM | SZ 00552 94121 | NO | YES | 0 | 32.0453 | 31.7168 | 31.3674 | 31.0084 | 30.4989 | 29.8768 | 29.2811 | 28.6653 | 28.0579 | 25.3758 | 22.9716 | -2.4579 | 27.3674 | 26.7316 | 25.8242 | 25.1726 | 24.5084 | 23.7916 | 23.0926 | 22.4168 | 21.7642 | 18.8653 | 16.1863 | 13.7326 | 28.44 | 27.8179 | 26.9347 | 26.2968 | 25.6453 | 24.9432 | 24.26 | 23.6011 | 22.9568 | 20 | 17.32 | 14.8695
|  | CREEKMOOR PRIMARY | EE |  |  |  |  | 32.2463 | 31.9779 | 31.6926 | 31.3958 | 31.0874 | 30.7916 | 30.32 | 29.8432 | 29.3926 | 27.3316 | 25.4684 | 23.8116 | 27.8063 | 27.3095 | 26.6642 | 26.0463 | 25.4632 | 24.8832 | 24.3074 | 23.7537 | 23.2221 | 20.9716 | 18.9326 | 17.0579 | 28.8695 | 28.3821 | 27.7526 | 27.1484 | 26.5779 | 26.0095 | 25.4474 | 24.9053 | 24.3863 | 22.1453 | 20.0611 | 18.1884
|  | CREEKMOOR PRIMARY | HT |  |  |  |  | 32.0453 | 31.7168 | 31.3674 | 31.0084 | 30.4989 | 29.8768 | 29.2811 | 28.6653 | 28.0579 | 25.3758 | 22.9716 | 20.7895 | 27.3674 | 26.7316 | 25.8242 | 25.1726 | 24.5084 | 23.7916 | 23.0926 | 22.4168 | 21.7642 | 18.8653 | 16.1863 | 13.7326 | 28.44 | 27.8179 | 26.9347 | 26.2968 | 25.6453 | 24.9432 | 24.26 | 23.6011 | 22.9568 | 20 | 17.32 | 14.8695
|  | CREEKMOOR PRIMARY | HE |  |  |  |  | 32.5042 | 32.3168 | 32.1084 | 31.8853 | 31.6453 | 31.4179 | 31.2032 | 31.0021 | 30.8274 | 29.5768 | 28.2968 | -2.4579 | 28.3611 | 28.0337 | 27.5484 | 27.0905 | 26.6579 | 26.2147 | 25.7716 | 25.3821 | 24.9853 | 23.3863 | 21.9621 | 20.7042 | 29.3758 | 29.0895 | 28.6158 | 28.1684 | 27.7453 | 27.3105 | 26.8768 | 26.4958 | 26.1084 | 24.5526 | 23.1432 | 21.8516
|  | CREEKMOOR PRIMARY | CF |  |  |  |  | 32.6853 | 32.5874 | 32.4874 | 32.3832 | 32.2747 | 32.1632 | 32.0558 | 31.9495 | 31.8411 | 31.3632 | 30.8168 | 30.1453 | 28.7495 | 28.5747 | 28.3884 | 28.2011 | 27.9863 | 27.74 | 27.4737 | 27.1895 | 26.9137 | 25.74 | 24.7621 | 23.9158 | 29.5684 | 29.4663 | 29.3611 | 29.2516 | 29.0421 | 28.8011 | 28.5421 | 28.2663 | 27.9968 | 26.8526 | 25.9074 | 25.0926
MINETY GSP | CIRENCESTER BSP | CRICKLADE PRIMARY | MINIMUM HEADROOM | SU 09400 93270 | NO | YES | 0 | 17.8305 | 18.06 | 17.7779 | 17.4989 | 17.2189 | 16.82 | 16.1832 | 15.6295 | 15.4937 | 14.2463 | 12.7242 | -1.5 | 14.8863 | 14.5916 | 14.2905 | 13.9926 | 13.6958 | 13.26 | 12.5421 | 11.9189 | 11.7842 | 10.4968 | 8.7926 | 7.7884 | 15.6832 | 15.3884 | 15.0874 | 14.7895 | 14.4916 | 14.0547 | 13.3347 | 12.7095 | 12.5737 | 11.2063 | 9.4926 | 8.5442
|  | CRICKLADE PRIMARY | EE |  |  |  |  | 18.52 | 18.3 | 18.0789 | 17.8516 | 17.6221 | 17.4 | 17.1853 | 16.9789 | 16.7895 | 15.8505 | 12.8737 | 11.9547 | 15.0895 | 14.8537 | 14.6168 | 14.3758 | 14.1326 | 13.8979 | 13.6726 | 13.4568 | 13.2568 | 12.2474 | 8.8253 | 7.7884 | 15.8863 | 15.6495 | 15.4126 | 15.1716 | 14.9284 | 14.6926 | 14.4653 | 14.2463 | 14.0442 | 13.0232 | 9.5853 | 8.5442
|  | CRICKLADE PRIMARY | HT |  |  |  |  | 18.3337 | 18.06 | 17.7779 | 17.4989 | 17.2189 | 16.82 | 16.1832 | 15.6295 | 15.4937 | 14.2463 | 12.7242 | 12.2168 | 14.8863 | 14.5916 | 14.2905 | 13.9926 | 13.6958 | 13.26 | 12.5421 | 11.9189 | 11.7842 | 10.4968 | 8.7926 | 8.2568 | 15.6832 | 15.3884 | 15.0874 | 14.7895 | 14.4916 | 14.0547 | 13.3347 | 12.7095 | 12.5737 | 11.2063 | 9.4926 | 8.9526
|  | CRICKLADE PRIMARY | HE |  |  |  |  | 18.7695 | 18.6295 | 18.4789 | 18.3232 | 18.1589 | 18.0021 | 17.8537 | 17.7126 | 17.5884 | 16.9747 | 14.2642 | -1.5 | 15.36 | 15.2105 | 15.0516 | 14.8863 | 14.7147 | 14.5516 | 14.3958 | 14.2495 | 14.1179 | 13.4547 | 10.3084 | 9.4905 | 16.1568 | 16.0074 | 15.8484 | 15.6832 | 15.5116 | 15.3463 | 15.1905 | 15.0421 | 14.9116 | 14.2421 | 11.0905 | 10.2674
|  | CRICKLADE PRIMARY | CF |  |  |  |  | 17.8305 | 18.8453 | 18.7589 | 18.6726 | 18.5758 | 18.4747 | 18.3832 | 18.2926 | 18.2042 | 17.7968 | 17.4116 | 17.0095 | 15.3758 | 15.4421 | 15.3495 | 15.2568 | 15.1537 | 15.0421 | 14.9453 | 14.8495 | 14.7547 | 14.3189 | 13.8916 | 13.4337 | 16.1095 | 16.2389 | 16.1463 | 16.0537 | 15.9495 | 15.8389 | 15.7411 | 15.6442 | 15.5495 | 15.1116 | 14.6811 | 14.2221
MELKSHAM GSP | FROME BSP | CROCKERTON PRIMARY | MINIMUM HEADROOM | ST 87736 43371 | NO | YES | 0 | 17.0579 | 16.8074 | 16.54 | 16.2653 | 15.9779 | 15.6884 | 15.4337 | 15.2011 | 14.8379 | 12.7842 | 10.6579 | -8.1105 | 13.7263 | 13.1463 | 12.5295 | 11.9811 | 11.4989 | 11.0242 | 10.5863 | 10.1832 | 9.7537 | 7.4537 | 5.0979 | 2.7632 | 14.5021 | 14.1463 | 13.5242 | 12.9674 | 12.4779 | 11.9958 | 11.5516 | 11.1421 | 10.7032 | 8.3516 | 5.9305 | 3.5347
|  | CROCKERTON PRIMARY | EE |  |  |  |  | 17.2063 | 17 | 16.78 | 16.5505 | 16.3095 | 16.0758 | 15.8537 | 15.6389 | 15.4442 | 14.1568 | 12.5116 | 10.8789 | 14.0484 | 13.6137 | 13.1474 | 12.6253 | 12.1684 | 11.7632 | 11.3905 | 11.0305 | 10.7084 | 8.9895 | 7.1463 | 5.3053 | 14.66 | 14.44 | 14.1432 | 13.6232 | 13.1589 | 12.7453 | 12.3653 | 12 | 11.6716 | 9.9074 | 8.0074 | 6.1137
|  | CROCKERTON PRIMARY | HT |  |  |  |  | 17.0579 | 16.8074 | 16.54 | 16.2653 | 15.9779 | 15.6884 | 15.4337 | 15.2011 | 14.8379 | 12.7842 | 10.6579 | 8.5811 | 13.7263 | 13.1463 | 12.5295 | 11.9811 | 11.4989 | 11.0242 | 10.5863 | 10.1832 | 9.7537 | 7.4537 | 5.0979 | 2.7632 | 14.5021 | 14.1463 | 13.5242 | 12.9674 | 12.4779 | 11.9958 | 11.5516 | 11.1421 | 10.7032 | 8.3516 | 5.9305 | 3.5347
|  | CROCKERTON PRIMARY | HE |  |  |  |  | 17.4 | 17.2547 | 17.0926 | 16.9189 | 16.7295 | 16.5495 | 16.3789 | 16.22 | 16.0832 | 15.6074 | 14.7347 | -8.1105 | 14.4484 | 14.1653 | 13.82 | 13.4221 | 13.0758 | 12.7874 | 12.5232 | 12.2737 | 12.0621 | 10.8811 | 9.5495 | 8.16 | 14.8589 | 14.7137 | 14.5411 | 14.3537 | 14.0737 | 13.7884 | 13.5211 | 13.2684 | 13.0537 | 11.8442 | 10.4758 | 9.0442
|  | CROCKERTON PRIMARY | CF |  |  |  |  | 17.5368 | 17.46 | 17.38 | 17.2979 | 17.2116 | 17.1221 | 17.0358 | 16.9495 | 16.8642 | 16.4789 | 16.2811 | 15.8884 | 14.5853 | 14.5084 | 14.4137 | 14.2642 | 14.0905 | 13.9042 | 13.7274 | 13.5337 | 13.3379 | 12.4347 | 11.6611 | 10.7737 | 14.9958 | 14.9189 | 14.8389 | 14.7568 | 14.6684 | 14.5737 | 14.4821 | 14.3895 | 14.2968 | 13.4253 | 12.6316 | 11.7179
FLEET-BRAMLEY GSP | PYESTOCK BSP | CROOKHAM PRIMARY | MINIMUM HEADROOM | SU 81702 53403 | NO | YES | 0 | 32.3253 | 31.9811 | 31.4463 | 30.7632 | 30.0821 | 29.3663 | 28.7326 | 28.1105 | 27.5274 | 24.8716 | 22.1453 | 6.7305 | 28.8537 | 28.2179 | 27.5253 | 26.7979 | 26.0747 | 25.3126 | 24.6368 | 23.9705 | 23.3463 | 20.4768 | 17.4863 | 14.7347 | 29.6863 | 29.0474 | 28.3442 | 27.6063 | 26.8716 | 26.0979 | 25.4105 | 24.7326 | 24.0958 | 21.1684 | 18.1042 | 15.2842
|  | CROOKHAM PRIMARY | EE |  |  |  |  | 32.5495 | 32.2737 | 31.9789 | 31.6126 | 31.0768 | 30.52 | 30.0063 | 29.4842 | 29.0105 | 26.9558 | 24.8284 | 22.9168 | 29.3074 | 28.8063 | 28.2747 | 27.7063 | 27.14 | 26.5474 | 26.0021 | 25.4453 | 24.9389 | 22.7242 | 20.3863 | 18.2632 | 30.1379 | 29.6379 | 29.1063 | 28.5295 | 27.9547 | 27.3526 | 26.7979 | 26.2316 | 25.7158 | 23.4526 | 21.0516 | 18.8726
|  | CROOKHAM PRIMARY | HT |  |  |  |  | 32.3253 | 31.9811 | 31.4463 | 30.7632 | 30.0821 | 29.3663 | 28.7326 | 28.1105 | 27.5274 | 24.8716 | 22.1453 | 19.6558 | 28.8537 | 28.2179 | 27.5253 | 26.7979 | 26.0747 | 25.3126 | 24.6368 | 23.9705 | 23.3463 | 20.4768 | 17.4863 | 14.7347 | 29.6863 | 29.0474 | 28.3442 | 27.6063 | 26.8716 | 26.0979 | 25.4105 | 24.7326 | 24.0958 | 21.1684 | 18.1042 | 15.2842
|  | CROOKHAM PRIMARY | HE |  |  |  |  | 32.8263 | 32.6368 | 32.4274 | 32.2021 | 31.96 | 31.7284 | 31.4537 | 31.0674 | 30.7274 | 29.3011 | 27.7558 | 6.7305 | 29.8916 | 29.5705 | 29.2126 | 28.8095 | 28.3947 | 27.9516 | 27.5495 | 27.1379 | 26.7726 | 25.2305 | 23.5137 | 21.9516 | 30.6695 | 30.3779 | 30.0432 | 29.6411 | 29.2263 | 28.7811 | 28.3716 | 27.9537 | 27.5832 | 26.0074 | 24.2442 | 22.6368
|  | CROOKHAM PRIMARY | CF |  |  |  |  | 33.0084 | 32.9116 | 32.8105 | 32.7063 | 32.5968 | 32.4874 | 32.3779 | 32.2695 | 32.1611 | 31.2537 | 30.2042 | 29.2916 | 30.2032 | 30.0137 | 29.8179 | 29.6063 | 29.3905 | 29.1537 | 28.9284 | 28.6874 | 28.4484 | 27.2958 | 26.1316 | 25.1084 | 30.9042 | 30.7842 | 30.6084 | 30.42 | 30.2211 | 29.9842 | 29.7611 | 29.5211 | 29.2779 | 28.1042 | 26.9095 | 25.8568
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CROWTHORNE PRIMARY | MINIMUM HEADROOM | SU 84470 64352 | NO | YES | 0.24211 | 35.4395 | 33.9805 | 32.2974 | 30.4647 | 28.7132 | 27.3068 | 26.1732 | 25.2984 | 24.4963 | 20.8689 | 17.31 | -16.5363 | 26.9037 | 25.3184 | 23.4321 | 21.3732 | 19.4132 | 17.8605 | 16.6153 | 15.6689 | 14.8016 | 10.85 | 6.9058 | 3.2879 | 28.4626 | 26.8363 | 24.9521 | 22.8963 | 20.9374 | 19.3847 | 18.1395 | 17.1911 | 16.3216 | 12.3584 | 8.4005 | 4.7805
|  | CROWTHORNE PRIMARY | EE |  |  |  |  | 36.1732 | 34.8605 | 33.3942 | 31.7647 | 30.1311 | 28.8847 | 27.9037 | 27.2005 | 26.5689 | 23.9321 | 21.2921 | 18.9489 | 27.7089 | 26.2384 | 24.6311 | 22.7921 | 20.9532 | 19.5679 | 18.4911 | 17.7384 | 17.0637 | 14.2226 | 11.3068 | 8.67 | 29.2679 | 27.7963 | 26.15 | 24.3132 | 22.4753 | 21.0889 | 20.0111 | 19.2553 | 18.5784 | 15.7163 | 12.7795 | 10.1374
|  | CROWTHORNE PRIMARY | HT |  |  |  |  | 35.4395 | 33.9805 | 32.2974 | 30.4647 | 28.7132 | 27.3068 | 26.1732 | 25.2984 | 24.4963 | 20.8689 | 17.31 | 14.0837 | 26.9037 | 25.3184 | 23.4321 | 21.3732 | 19.4132 | 17.8605 | 16.6153 | 15.6689 | 14.8016 | 10.85 | 6.9058 | 3.2879 | 28.4626 | 26.8363 | 24.9521 | 22.8963 | 20.9374 | 19.3847 | 18.1395 | 17.1911 | 16.3216 | 12.3584 | 8.4005 | 4.7805
|  | CROWTHORNE PRIMARY | HE |  |  |  |  | 36.6163 | 35.8911 | 34.6605 | 33.2511 | 31.8342 | 30.7921 | 30.0195 | 29.5279 | 29.0889 | 27.3816 | 25.6163 | -16.5363 | 28.5616 | 27.3574 | 26.0058 | 24.4047 | 22.8026 | 21.6363 | 20.7858 | 20.2626 | 19.7932 | 17.9489 | 15.97 | 14.1563 | 30.1205 | 28.9163 | 27.5237 | 25.9247 | 24.3226 | 23.1584 | 22.3068 | 21.7816 | 21.3121 | 19.4605 | 17.4763 | 15.6605
|  | CROWTHORNE PRIMARY | CF |  |  |  |  | 36.8816 | 36.7395 | 36.5911 | 36.3258 | 35.7068 | 35.1574 | 34.6711 | 34.2289 | 33.7911 | 32.0921 | 30.9995 | 30.1258 | 30.1247 | 29.5342 | 28.89 | 28.1826 | 27.4711 | 26.8416 | 26.29 | 25.79 | 25.2942 | 23.1847 | 21.9679 | 20.9784 | 31.69 | 31.0932 | 30.4489 | 29.7416 | 29.0289 | 28.3995 | 27.8468 | 27.3458 | 26.85 | 24.6995 | 23.4795 | 22.4889
COWLEY GSP |  | CULHAM PRIMARY | MINIMUM HEADROOM | SU 50731 95053 | NO | YES | 0 | 41.0389 | 40.9832 | 40.9284 | 40.8716 | 40.8716 | 40.8705 | 40.8695 | 40.8684 | 40.8684 | 40.8632 | 40.8589 | 34.8884 | 40.0137 | 39.9484 | 39.8842 | 39.8179 | 39.8168 | 39.8158 | 39.8147 | 39.8137 | 39.8126 | 39.8074 | 39.8032 | 39.7979 | 40.3474 | 40.2821 | 40.2179 | 40.1516 | 40.1505 | 40.1495 | 40.1484 | 40.1474 | 40.1463 | 40.1411 | 40.1368 | 40.1316
|  | CULHAM PRIMARY | EE |  |  |  |  | 41.04 | 40.9853 | 40.9305 | 40.8747 | 40.8747 | 40.8747 | 40.8747 | 40.8747 | 40.8747 | 40.8737 | 40.8674 | 40.8621 | 40.0147 | 39.9505 | 39.8863 | 39.8211 | 39.8211 | 39.8211 | 39.8211 | 39.8211 | 39.8211 | 39.82 | 39.8126 | 39.8063 | 40.3484 | 40.2842 | 40.2189 | 40.1547 | 40.1547 | 40.1547 | 40.1547 | 40.1547 | 40.1547 | 40.1537 | 40.1463 | 40.14
|  | CULHAM PRIMARY | HT |  |  |  |  | 41.0389 | 40.9832 | 40.9284 | 40.8716 | 40.8716 | 40.8705 | 40.8695 | 40.8684 | 40.8684 | 40.8632 | 40.8589 | 40.8558 | 40.0137 | 39.9484 | 39.8842 | 39.8179 | 39.8168 | 39.8158 | 39.8147 | 39.8137 | 39.8126 | 39.8074 | 39.8032 | 39.7979 | 40.3474 | 40.2821 | 40.2179 | 40.1516 | 40.1505 | 40.1495 | 40.1484 | 40.1474 | 40.1463 | 40.1411 | 40.1368 | 40.1316
|  | CULHAM PRIMARY | HE |  |  |  |  | 41.0411 | 40.9874 | 40.9337 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 34.8884 | 40.0158 | 39.9537 | 39.8895 | 39.8253 | 39.8253 | 39.8253 | 39.8253 | 39.8253 | 39.8253 | 39.8253 | 39.8253 | 39.8253 | 40.3495 | 40.2863 | 40.2232 | 40.1579 | 40.1579 | 40.1579 | 40.1579 | 40.1579 | 40.1579 | 40.1579 | 40.1579 | 40.1579
|  | CULHAM PRIMARY | CF |  |  |  |  | 41.1189 | 41.1042 | 41.0895 | 41.0758 | 41.06 | 41.0453 | 41.0305 | 41.0147 | 40.9989 | 40.9821 | 40.98 | 40.9779 | 40.1084 | 40.0905 | 40.0737 | 40.0568 | 40.0389 | 40.0211 | 40.0032 | 39.9853 | 39.9674 | 39.9474 | 39.9442 | 39.9411 | 40.4421 | 40.4242 | 40.4074 | 40.3905 | 40.3726 | 40.3547 | 40.3368 | 40.3189 | 40.3 | 40.28 | 40.2779 | 40.2747
EALING GSP | EALING BSP | DEAN GARDENS PRIMARY | MINIMUM HEADROOM | TQ 16546 80368 | YES | YES | 0.014737 | 10.2713 | 10.1744 | 10.1018 | 10.0239 | 9.9439 | 9.8649 | 9.7934 | 9.7281 | 9.6671 | 9.4007 | 9.1355 | 2.8923 | 9.6344 | 9.1607 | 9.0071 | 8.8471 | 8.6839 | 8.5513 | 8.4281 | 8.3102 | 8.1986 | 7.6713 | 7.1271 | 6.5986 | 9.9702 | 9.4902 | 9.3344 | 9.1734 | 9.0081 | 8.8744 | 8.7502 | 8.6313 | 8.5186 | 7.986 | 7.4418 | 6.9134
|  | DEAN GARDENS PRIMARY | EE |  |  |  |  | 10.3134 | 10.2313 | 10.1734 | 10.1102 | 10.0449 | 9.9818 | 9.9207 | 9.8597 | 9.806 | 9.5934 | 9.4323 | 9.306 | 9.7323 | 9.3134 | 9.2113 | 9.1028 | 8.9934 | 8.8913 | 8.7923 | 8.6944 | 8.6049 | 8.2071 | 7.8355 | 7.4913 | 10.0692 | 9.6439 | 9.5407 | 9.4323 | 9.3218 | 9.2186 | 9.1197 | 9.0207 | 8.9302 | 8.5292 | 8.1534 | 7.806
|  | DEAN GARDENS PRIMARY | HT |  |  |  |  | 10.2713 | 10.1744 | 10.1018 | 10.0239 | 9.9439 | 9.8649 | 9.7934 | 9.7281 | 9.6671 | 9.4007 | 9.1355 | 8.6628 | 9.6344 | 9.1607 | 9.0071 | 8.8471 | 8.6839 | 8.5513 | 8.4281 | 8.3102 | 8.1986 | 7.6713 | 7.1271 | 6.5986 | 9.9702 | 9.4902 | 9.3344 | 9.1734 | 9.0081 | 8.8744 | 8.7502 | 8.6313 | 8.5186 | 7.986 | 7.4418 | 6.9134
|  | DEAN GARDENS PRIMARY | HE |  |  |  |  | 10.3502 | 10.2797 | 10.2292 | 10.1765 | 10.1197 | 10.066 | 10.0155 | 9.9681 | 9.9271 | 9.7818 | 9.6849 | 2.8923 | 9.8113 | 9.4313 | 9.3534 | 9.2713 | 9.1849 | 9.1071 | 9.0334 | 8.9628 | 8.9007 | 8.6523 | 8.4292 | 8.2365 | 10.1597 | 9.7639 | 9.6849 | 9.6018 | 9.5155 | 9.4365 | 9.3628 | 9.2913 | 9.2292 | 8.9786 | 8.7534 | 8.5586
|  | DEAN GARDENS PRIMARY | CF |  |  |  |  | 10.3913 | 10.3502 | 10.3197 | 10.2881 | 10.2555 | 10.2239 | 10.1913 | 10.1586 | 10.1271 | 9.9828 | 9.9071 | 9.8597 | 9.9534 | 9.8197 | 9.7776 | 9.7355 | 9.6828 | 9.6313 | 9.5776 | 9.5239 | 9.4723 | 9.2239 | 9.0523 | 8.9113 | 10.2702 | 10.1765 | 10.1249 | 10.0734 | 10.0197 | 9.9681 | 9.9144 | 9.8607 | 9.8081 | 9.5576 | 9.3849 | 9.2407
COWLEY GSP | YARNTON BSP | DEDDINGTON PRIMARY | MINIMUM HEADROOM | SP 46729 30325 | NO | YES | 0 | 6.38 | 6.2421 | 6.0979 | 5.9516 | 5.8063 | 5.6611 | 5.5284 | 5.4063 | 5.2905 | 3.6095 | 3.3947 | -2.4495 | 5.0316 | 4.8832 | 4.7284 | 4.5716 | 4.4158 | 4.2611 | 4.12 | 3.9884 | 3.8642 | 1.9347 | 1.7158 | 1.56 | 4.9737 | 4.8253 | 4.6705 | 4.5137 | 4.3579 | 4.2032 | 4.0611 | 3.9295 | 3.8053 | 1.8758 | 1.6568 | 1.5011
|  | DEDDINGTON PRIMARY | EE |  |  |  |  | 6.4758 | 6.3632 | 6.2474 | 6.1284 | 6.0074 | 5.8926 | 5.7811 | 5.6737 | 5.5758 | 5.1916 | 4.6968 | 4.1737 | 5.1358 | 5.0147 | 4.8905 | 4.7632 | 4.6347 | 4.5116 | 4.3916 | 4.2779 | 4.1726 | 3.7568 | 3.1989 | 2.6021 | 5.0779 | 4.9568 | 4.8326 | 4.7053 | 4.5758 | 4.4526 | 4.3337 | 4.22 | 4.1147 | 3.6989 | 3.1411 | 2.5432
|  | DEDDINGTON PRIMARY | HT |  |  |  |  | 6.38 | 6.2421 | 6.0979 | 5.9516 | 5.8063 | 5.6611 | 5.5284 | 5.4063 | 5.2905 | 3.6095 | 3.3947 | 3.24 | 5.0316 | 4.8832 | 4.7284 | 4.5716 | 4.4158 | 4.2611 | 4.12 | 3.9884 | 3.8642 | 1.9347 | 1.7158 | 1.56 | 4.9737 | 4.8253 | 4.6705 | 4.5137 | 4.3579 | 4.2032 | 4.0611 | 3.9295 | 3.8053 | 1.8758 | 1.6568 | 1.5011
|  | DEDDINGTON PRIMARY | HE |  |  |  |  | 6.5937 | 6.5284 | 6.4495 | 6.3642 | 6.2758 | 6.1926 | 6.1126 | 6.0379 | 5.9684 | 5.7295 | 5.0326 | -2.4495 | 5.2642 | 5.1947 | 5.1095 | 5.02 | 4.9253 | 4.8379 | 4.7526 | 4.6726 | 4.5979 | 4.3411 | 3.5368 | 3.4663 | 5.2053 | 5.1368 | 5.0516 | 4.9621 | 4.8674 | 4.78 | 4.6947 | 4.6137 | 4.54 | 4.2832 | 3.4779 | 3.4084
|  | DEDDINGTON PRIMARY | CF |  |  |  |  | 6.6368 | 6.6137 | 6.5779 | 6.5316 | 6.4863 | 6.44 | 6.3916 | 6.3442 | 6.2968 | 6.0842 | 5.8811 | 5.5863 | 5.3074 | 5.2842 | 5.2463 | 5.1958 | 5.1474 | 5.0958 | 5.0442 | 4.9926 | 4.9421 | 4.7116 | 4.4832 | 4.1421 | 5.2484 | 5.2253 | 5.1884 | 5.1379 | 5.0895 | 5.0379 | 4.9863 | 4.9347 | 4.8842 | 4.6537 | 4.4253 | 4.0842
IVER 132KV GSP | DENHAM BSP | DENHAM AVENUE PRIMARY | MINIMUM HEADROOM | TQ 03761 86587 | NO | NO | 0 | 13.5926 | 13.4579 | 13.3147 | 13.1663 | 43.0126 | 42.8589 | 42.7232 | 42.6011 | 42.4874 | 41.5453 | 40.6063 | 24.3568 | 10.8137 | 10.5621 | 10.2979 | 10.0295 | 39.7611 | 39.4905 | 39.1642 | 38.96 | 38.7053 | 37.5053 | 36.4474 | 35.4905 | 11.4337 | 11.2989 | 11.1558 | 10.8989 | 40.6263 | 40.3526 | 40.0368 | 39.84 | 39.5937 | 38.3968 | 37.3358 | 36.3779
|  | DENHAM AVENUE PRIMARY | EE |  |  |  |  | 13.6747 | 13.5653 | 14.5168 | 14.3116 | 44.1011 | 43.8947 | 43.6926 | 43.4821 | 43.2884 | 42.4442 | 41.7158 | 41.0779 | 10.9526 | 10.7842 | 10.6305 | 10.4105 | 40.1853 | 40.0053 | 39.7874 | 39.5611 | 39.3505 | 38.4232 | 37.6105 | 36.8926 | 11.5158 | 11.4063 | 11.5221 | 11.3021 | 41.0768 | 40.8558 | 40.6389 | 40.4116 | 40.2011 | 39.2737 | 38.4621 | 37.7442
|  | DENHAM AVENUE PRIMARY | HT |  |  |  |  | 13.5926 | 13.4579 | 13.3147 | 13.1663 | 43.0126 | 42.8589 | 42.7232 | 42.6011 | 42.4874 | 41.5453 | 40.6063 | 39.7653 | 10.8137 | 10.5621 | 10.2979 | 10.0295 | 39.7611 | 39.4905 | 39.1642 | 38.96 | 38.7053 | 37.5053 | 36.4474 | 35.4905 | 11.4337 | 11.2989 | 11.1558 | 10.8989 | 40.6263 | 40.3526 | 40.0368 | 39.84 | 39.5937 | 38.3968 | 37.3358 | 36.3779
|  | DENHAM AVENUE PRIMARY | HE |  |  |  |  | 13.7768 | 13.6979 | 13.6105 | 13.5158 | 43.4158 | 44.3968 | 44.2484 | 44.0926 | 43.9495 | 43.3632 | 42.8758 | 24.3568 | 11.0716 | 10.9842 | 10.8895 | 10.7695 | 40.6084 | 40.5526 | 40.3937 | 40.2253 | 40.0705 | 39.4253 | 38.8758 | 38.4126 | 11.6179 | 11.5389 | 11.4516 | 11.3568 | 41.2568 | 41.4021 | 41.2442 | 41.0758 | 40.9211 | 40.2758 | 39.7284 | 39.2642
|  | DENHAM AVENUE PRIMARY | CF |  |  |  |  | 13.8474 | 13.8063 | 13.7621 | 13.7158 | 43.6695 | 43.6211 | 43.5737 | 43.5263 | 43.4789 | 43.2705 | 43.1674 | 43.1095 | 11.1484 | 11.1021 | 11.0526 | 11.0011 | 40.9495 | 40.8947 | 40.8095 | 40.7126 | 40.6126 | 40.1421 | 39.7863 | 39.4653 | 11.6884 | 11.6474 | 11.6032 | 11.5568 | 41.5105 | 41.4621 | 41.4147 | 41.3674 | 41.32 | 41.0105 | 40.6474 | 40.3432
MELKSHAM GSP | NORRINGTON BSP | DEVIZES PRIMARY | MINIMUM HEADROOM | SU 00106 60986 | NO | YES | 0 | 47.2295 | 46.9021 | 46.0695 | 45.0084 | 43.9084 | 42.9411 | 42.1642 | 41.5568 | 40.9211 | 37.9326 | 34.6189 | 0.63684 | 39.6242 | 38.3968 | 37.1147 | 35.7421 | 34.5253 | 33.4663 | 32.6232 | 31.9747 | 31.2863 | 28.0863 | 24.3968 | 20.7537 | 42.9053 | 41.6789 | 40.3979 | 39.0263 | 37.8105 | 36.7505 | 35.9053 | 35.2547 | 34.5663 | 31.3779 | 27.6747 | 24.0284
|  | DEVIZES PRIMARY | EE |  |  |  |  | 47.2295 | 46.9021 | 46.5547 | 45.6853 | 44.8 | 44.0453 | 43.4063 | 42.7495 | 42.3853 | 39.8895 | 37.6032 | 35.08 | 40.0021 | 38.9495 | 37.8442 | 36.6916 | 35.6853 | 34.8389 | 34.1347 | 33.4158 | 32.8916 | 30.1737 | 27.7126 | 24.8516 | 43.4147 | 42.34 | 41.2105 | 40.0326 | 39.0053 | 38.1421 | 37.4232 | 36.6926 | 36.1663 | 33.4284 | 30.9684 | 28.1042
|  | DEVIZES PRIMARY | HT |  |  |  |  | 48.2884 | 47.2042 | 46.0695 | 45.0084 | 43.9084 | 42.9411 | 42.1642 | 41.5568 | 40.9211 | 37.9326 | 34.6189 | 31.3905 | 39.6242 | 38.3968 | 37.1147 | 35.7421 | 34.5253 | 33.4663 | 32.6232 | 31.9747 | 31.2863 | 28.0863 | 24.3968 | 20.7537 | 42.9053 | 41.6789 | 40.3979 | 39.0263 | 37.8105 | 36.7505 | 35.9053 | 35.2547 | 34.5663 | 31.3779 | 27.6747 | 24.0284
|  | DEVIZES PRIMARY | HE |  |  |  |  | 47.5284 | 47.2937 | 47.0337 | 46.7547 | 46.0632 | 45.4642 | 44.9684 | 44.4989 | 44.1832 | 42.6789 | 40.8789 | 0.63684 | 40.6632 | 39.8147 | 38.9042 | 37.9379 | 37.0989 | 36.4253 | 35.8758 | 35.3547 | 35.0168 | 33.1989 | 31.1611 | 29.0537 | 44.0853 | 43.2211 | 42.2905 | 41.3011 | 40.4442 | 39.7589 | 39.1979 | 38.6684 | 38.3253 | 36.4726 | 34.4316 | 32.3189
|  | DEVIZES PRIMARY | CF |  |  |  |  | 47.7389 | 47.6137 | 47.4832 | 47.3484 | 47.2063 | 47.0621 | 46.92 | 46.7789 | 46.6379 | 45.7653 | 44.8505 | 43.6674 | 40.9832 | 40.6232 | 40.1674 | 39.7358 | 39.3463 | 38.9926 | 38.7116 | 38.4126 | 38.1116 | 36.7895 | 35.5737 | 34.2116 | 44.3926 | 44.0453 | 43.5779 | 43.1379 | 42.7389 | 42.3789 | 42.0937 | 41.7905 | 41.4821 | 40.0674 | 38.8505 | 37.4863
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH PRIMARY | MINIMUM HEADROOM | SU 19288 83540 | NO | YES | 0 | 26.1158 | 26.0558 | 25.9916 | 25.9253 | 25.8579 | 25.7884 | 25.7284 | 25.6653 | 25.6011 | 25.4979 | 24.8495 | 12.4516 | 23.1821 | 23.0747 | 22.9642 | 22.8537 | 22.7411 | 22.6232 | 22.5147 | 22.4179 | 22.3284 | 22.1716 | 21.1695 | 20.5147 | 25.0295 | 24.9547 | 24.8758 | 24.7968 | 24.7158 | 24.6326 | 24.5579 | 24.4895 | 24.4095 | 24.2516 | 23.2389 | 22.5821
|  | DORCAN SOUTH PRIMARY | EE |  |  |  |  | 26.1484 | 26.0979 | 26.0453 | 25.9884 | 25.9305 | 25.8737 | 25.8211 | 25.7684 | 25.7211 | 25.4979 | 25.5611 | 25.1211 | 23.2442 | 23.1642 | 23.0768 | 22.9832 | 22.8916 | 22.8011 | 22.7137 | 22.6232 | 22.5453 | 22.1716 | 22.1389 | 21.6274 | 25.0737 | 25.0116 | 24.9474 | 24.88 | 24.8116 | 24.7453 | 24.6811 | 24.6179 | 24.5621 | 24.2516 | 24.2242 | 23.7105
|  | DORCAN SOUTH PRIMARY | HT |  |  |  |  | 26.1158 | 26.0558 | 25.9916 | 25.9253 | 25.8579 | 25.7884 | 25.7284 | 25.6653 | 25.6011 | 25.6232 | 24.8495 | 24.2726 | 23.1821 | 23.0747 | 22.9642 | 22.8537 | 22.7411 | 22.6232 | 22.5147 | 22.4179 | 22.3284 | 22.3358 | 21.1695 | 20.5147 | 25.0295 | 24.9547 | 24.8758 | 24.7968 | 24.7158 | 24.6326 | 24.5579 | 24.4895 | 24.4095 | 24.4221 | 23.2389 | 22.5821
|  | DORCAN SOUTH PRIMARY | HE |  |  |  |  | 26.1947 | 26.1579 | 26.1179 | 26.0737 | 26.0274 | 25.9821 | 25.94 | 25.8989 | 25.8663 | 25.7474 | 25.5768 | 12.4516 | 23.3211 | 23.2737 | 23.2158 | 23.1558 | 23.0905 | 23.0263 | 22.9589 | 22.8663 | 22.8242 | 22.5926 | 22.1832 | 21.7926 | 25.1347 | 25.0916 | 25.0432 | 24.9926 | 24.94 | 24.8884 | 24.8389 | 24.7821 | 24.7463 | 24.5937 | 24.2621 | 23.8642
|  | DORCAN SOUTH PRIMARY | CF |  |  |  |  | 26.2263 | 26.2042 | 26.1832 | 26.1611 | 26.1379 | 26.1137 | 26.0905 | 26.0684 | 26.0442 | 25.9421 | 25.8789 | 25.7716 | 23.3621 | 23.3337 | 23.3032 | 23.2716 | 23.2358 | 23.2 | 23.1632 | 23.1253 | 23.0853 | 22.9011 | 22.6621 | 22.4105 | 25.1716 | 25.1453 | 25.1189 | 25.0916 | 25.0632 | 25.0347 | 25.0063 | 24.9789 | 24.9505 | 24.8221 | 24.7074 | 24.4905
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER PRIMARY | MINIMUM HEADROOM | SY 69113 90401 | NO | YES | 0 | 35.4411 | 47.2158 | 46.8284 | 46.4274 | 45.9905 | 45.5474 | 45.1516 | 44.7853 | 44.4432 | 42.9768 | 40.9042 | -13.9611 | 30.8895 | 46.5295 | 46.1421 | 45.7421 | 45.3168 | 44.8337 | 44.1716 | 43.5463 | 42.9568 | 39.6874 | 36.5126 | 33.3189 | 30.1716 | 45.3621 | 44.9737 | 44.5737 | 44.1389 | 43.6989 | 43.3063 | 42.9442 | 42.5137 | 39.1432 | 35.8495 | 32.6063
|  | DORCHESTER PRIMARY | EE |  |  |  |  | 47.7874 | 47.4842 | 47.16 | 46.8211 | 46.4474 | 46.0747 | 45.7158 | 45.3632 | 45.04 | 43.7326 | 42.6832 | 40.9537 | 47.1 | 46.7979 | 46.4758 | 46.1379 | 45.7768 | 45.4211 | 45.0821 | 44.7505 | 44.3095 | 41.5168 | 39.0168 | 36.5989 | 45.9326 | 45.6295 | 45.3063 | 44.9674 | 44.5958 | 44.2274 | 43.8737 | 43.5253 | 43.2074 | 40.9768 | 38.3516 | 35.8516
|  | DORCHESTER PRIMARY | HT |  |  |  |  | 47.5811 | 47.2158 | 46.8284 | 46.4274 | 45.9905 | 45.5474 | 45.1516 | 44.7853 | 44.4432 | 42.9768 | 40.9042 | 38.0253 | 46.8937 | 46.5295 | 46.1421 | 45.7421 | 45.3168 | 44.8337 | 44.1716 | 43.5463 | 42.9568 | 39.6874 | 36.5126 | 33.3189 | 45.7263 | 45.3621 | 44.9737 | 44.5737 | 44.1389 | 43.6989 | 43.3063 | 42.9442 | 42.5137 | 39.1432 | 35.8495 | 32.6063
|  | DORCHESTER PRIMARY | HE |  |  |  |  | 48.0547 | 47.8337 | 47.5874 | 47.3242 | 47.0253 | 46.74 | 46.4695 | 46.2137 | 45.9905 | 45.1737 | 44.6474 | -13.9611 | 47.3674 | 47.1463 | 46.9011 | 46.6379 | 46.3484 | 46.0716 | 45.8095 | 45.5642 | 45.3516 | 44.4053 | 42.8211 | 41.1253 | 46.2 | 45.9789 | 45.7326 | 45.4695 | 45.1726 | 44.8895 | 44.6211 | 44.3674 | 44.1463 | 43.3432 | 42.3232 | 40.5642
|  | DORCHESTER PRIMARY | CF |  |  |  |  | 35.4411 | 48.1158 | 47.9874 | 47.8547 | 47.7084 | 47.56 | 47.4137 | 47.2695 | 47.1263 | 46.4768 | 46.12 | 45.8916 | 30.8895 | 47.4284 | 47.3 | 47.1674 | 47.0253 | 46.8811 | 46.74 | 46.5989 | 46.46 | 45.8326 | 45.5032 | 44.6179 | 30.1716 | 46.2611 | 46.1326 | 46 | 45.8547 | 45.7074 | 45.5621 | 45.4179 | 45.2768 | 44.6326 | 44.2811 | 44.06
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | DOWN GRANGE PRIMARY | MINIMUM HEADROOM | SU 61604 50238 | NO | YES | 0 | 33.6021 | 33.0084 | 31.6232 | 29.78 | 27.8053 | 25.6968 | 24.0358 | 22.4589 | 21.2674 | 16.8958 | 13.0905 | -16.4747 | 28.1989 | 26.6684 | 25.0126 | 22.9558 | 20.7495 | 18.3842 | 16.5347 | 14.7747 | 13.4621 | 8.6884 | 4.4947 | -0.096842 | 28.7347 | 27.2737 | 25.6926 | 23.7326 | 21.5242 | 19.1568 | 17.3042 | 15.5442 | 14.2274 | 9.44 | 5.2295 | 0.63053
|  | DOWN GRANGE PRIMARY | EE |  |  |  |  | 33.9484 | 33.4579 | 32.74 | 31.0968 | 29.3126 | 27.8032 | 26.4189 | 24.9211 | 23.4347 | 19.8137 | 17.1937 | 14.0684 | 28.9621 | 27.66 | 26.2316 | 24.3905 | 22.3884 | 20.7084 | 19.1716 | 17.4979 | 15.8284 | 11.8758 | 9.0147 | 5.4821 | 29.4684 | 28.2253 | 26.8632 | 25.1147 | 23.1632 | 21.4811 | 19.9411 | 18.2642 | 16.5926 | 12.62 | 9.7368 | 6.1958
|  | DOWN GRANGE PRIMARY | HT |  |  |  |  | 33.6021 | 33.0084 | 31.6232 | 29.78 | 27.8053 | 25.6968 | 24.0358 | 22.4589 | 21.2674 | 16.8958 | 13.0905 | 9.0074 | 28.1989 | 26.6684 | 25.0126 | 22.9558 | 20.7495 | 18.3842 | 16.5347 | 14.7747 | 13.4621 | 8.6884 | 4.4947 | -0.096842 | 28.7347 | 27.2737 | 25.6926 | 23.7326 | 21.5242 | 19.1568 | 17.3042 | 15.5442 | 14.2274 | 9.44 | 5.2295 | 0.63053
|  | DOWN GRANGE PRIMARY | HE |  |  |  |  | 34.4053 | 34.0558 | 33.6695 | 32.8558 | 31.3147 | 30.0484 | 28.9926 | 27.9011 | 26.8737 | 24.0126 | 22.6905 | -16.4747 | 29.9811 | 28.9937 | 27.8653 | 26.3084 | 24.5726 | 23.1568 | 21.9842 | 20.7653 | 19.6137 | 16.4453 | 15.0105 | 13.0537 | 30.4453 | 29.5053 | 28.4305 | 26.9579 | 25.3147 | 23.9316 | 22.7579 | 21.5379 | 20.3842 | 17.2074 | 15.7653 | 13.8032
|  | DOWN GRANGE PRIMARY | CF |  |  |  |  | 34.7221 | 34.5358 | 34.3421 | 34.1421 | 33.9337 | 33.7095 | 32.9116 | 32.3495 | 31.7611 | 29.1074 | 27.9695 | 26.9758 | 30.9211 | 30.5884 | 30.1695 | 29.5958 | 28.7811 | 27.24 | 26.3316 | 25.7032 | 25.0484 | 22.0863 | 20.8316 | 19.7116 | 31.2874 | 31.0484 | 30.6168 | 30.0695 | 29.2979 | 27.8547 | 26.9958 | 26.3979 | 25.7758 | 22.8579 | 21.6 | 20.4747
MINETY GSP | STRATTON (MAIN) BSP | DRAKES WAY PRIMARY | MINIMUM HEADROOM | SU 16899 85647 | NO | YES | 0 | 16.5758 | 16.5263 | 16.4726 | 16.4168 | 16.3589 | 16.3011 | 16.2505 | 16.2032 | 16.16 | 15.9147 | 15.6232 | 4.1105 | 15.2358 | 15.1842 | 15.1284 | 14.9916 | 14.6758 | 14.4505 | 14.2421 | 14.0632 | 14.0158 | 13.7495 | 13.4305 | 12.9495 | 15.4305 | 15.3747 | 15.3147 | 15.2421 | 15.0379 | 14.8126 | 14.6053 | 14.4263 | 14.3789 | 14.1137 | 13.7947 | 13.3137
|  | DRAKES WAY PRIMARY | EE |  |  |  |  | 16.6042 | 16.5621 | 16.5168 | 16.4695 | 16.4211 | 16.3737 | 16.3284 | 16.2842 | 16.2453 | 16.1011 | 15.9421 | 15.7147 | 15.2653 | 15.2221 | 15.1747 | 15.1263 | 15.0137 | 14.8232 | 14.6074 | 14.4032 | 14.3274 | 14.0168 | 13.7789 | 13.5242 | 15.4632 | 15.4168 | 15.3663 | 15.3137 | 15.2484 | 15.1821 | 14.9695 | 14.7663 | 14.6905 | 14.38 | 14.1421 | 13.8874
|  | DRAKES WAY PRIMARY | HT |  |  |  |  | 16.5758 | 16.5263 | 16.4726 | 16.4168 | 16.3589 | 16.3011 | 16.2505 | 16.2032 | 16.16 | 15.9147 | 15.6232 | 15.1979 | 15.2358 | 15.1842 | 15.1284 | 14.9916 | 14.6758 | 14.4505 | 14.2421 | 14.0632 | 14.0158 | 13.7495 | 13.4305 | 12.9495 | 15.4305 | 15.3747 | 15.3147 | 15.2421 | 15.0379 | 14.8126 | 14.6053 | 14.4263 | 14.3789 | 14.1137 | 13.7947 | 13.3137
|  | DRAKES WAY PRIMARY | HE |  |  |  |  | 16.64 | 16.6084 | 16.5747 | 16.5368 | 16.4968 | 16.4589 | 16.4232 | 16.3895 | 16.3611 | 16.2632 | 16.2042 | 4.1105 | 15.3032 | 15.2705 | 15.2358 | 15.1968 | 15.1516 | 15.0189 | 14.8263 | 14.6432 | 14.5895 | 14.3832 | 14.2463 | 14.1074 | 15.5053 | 15.4705 | 15.4347 | 15.3937 | 15.3379 | 15.2821 | 15.1884 | 15.0063 | 14.9526 | 14.7463 | 14.6095 | 14.4705
|  | DRAKES WAY PRIMARY | CF |  |  |  |  | 16.6663 | 16.6495 | 16.6316 | 16.6126 | 16.5937 | 16.5737 | 16.5547 | 16.5358 | 16.5158 | 16.4305 | 16.3884 | 16.3642 | 15.3305 | 15.3137 | 15.2947 | 15.2747 | 15.2558 | 15.2347 | 15.2147 | 15.1937 | 15.1705 | 14.8526 | 14.7495 | 14.6663 | 15.5347 | 15.5158 | 15.4958 | 15.4747 | 15.4537 | 15.4316 | 15.4105 | 15.3842 | 15.3537 | 15.2147 | 15.1116 | 15.0284
NURSLING GSP | WINCHESTER BSP | DUNBRIDGE PRIMARY | MINIMUM HEADROOM | SU 31520 26244 | NO | YES | 0 | 10.2989 | 10.0484 | 9.9105 | 9.3463 | 8.1632 | 7.1968 | 5.7558 | 5.5821 | 5.4168 | 2.8368 | -0.72526 | -31.9537 | 7.6716 | 7.3926 | 7.1179 | 6.4832 | 5.2326 | 3.9137 | 2.26 | 2.0968 | 1.9432 | -0.88737 | -4.98 | -5.9337 | 8.1189 | 7.8558 | 7.5632 | 6.9284 | 5.5674 | 4.2421 | 2.5821 | 2.4084 | 2.2432 | -0.65474 | -4.7221 | -5.7074
|  | DUNBRIDGE PRIMARY | EE |  |  |  |  | 10.4032 | 10.2716 | 10.0653 | 9.8547 | 9.6189 | 9.3779 | 9.1421 | 8.9021 | 8.6747 | 6.7621 | 3.1674 | 1.0116 | 7.8716 | 7.6495 | 7.4158 | 7.1874 | 6.9421 | 6.6937 | 6.4516 | 6.2053 | 5.9747 | 3.8474 | -0.19789 | -2.6547 | 8.2968 | 8.0947 | 7.8789 | 7.6474 | 7.3926 | 7.1337 | 6.88 | 6.6211 | 6.3768 | 4.1432 | -0.0084211 | -2.4979
|  | DUNBRIDGE PRIMARY | HT |  |  |  |  | 10.2989 | 10.0484 | 9.9105 | 9.3463 | 8.1632 | 7.1968 | 5.7558 | 5.5821 | 5.4168 | 2.8368 | -0.72526 | -1.6253 | 7.6716 | 7.3926 | 7.1179 | 6.4832 | 5.2326 | 3.9137 | 2.26 | 2.0968 | 1.9432 | -0.88737 | -4.98 | -5.9337 | 8.1189 | 7.8558 | 7.5632 | 6.9284 | 5.5674 | 4.2421 | 2.5821 | 2.4084 | 2.2432 | -0.65474 | -4.7221 | -5.7074
|  | DUNBRIDGE PRIMARY | HE |  |  |  |  | 10.5326 | 10.4484 | 10.3516 | 10.2495 | 10.1211 | 9.9716 | 9.8168 | 9.6653 | 9.5242 | 8.4832 | 5.9442 | -31.9537 | 8.1021 | 7.9895 | 7.8347 | 7.6832 | 7.5095 | 7.3421 | 7.1832 | 7.0263 | 6.88 | 5.7189 | 2.7021 | 0.66105 | 8.5042 | 8.3979 | 8.2558 | 8.1168 | 7.9463 | 7.7863 | 7.6316 | 7.4716 | 7.3189 | 6.1021 | 3.0526 | 0.98211
|  | DUNBRIDGE PRIMARY | CF |  |  |  |  | 10.6168 | 10.5747 | 10.5326 | 10.4842 | 10.4242 | 10.3642 | 10.3063 | 10.2242 | 10.14 | 9.7253 | 8.4326 | 7.1463 | 8.1863 | 8.1442 | 8.0947 | 8.0053 | 7.8916 | 7.7821 | 7.6874 | 7.5947 | 7.5042 | 7.0621 | 5.4863 | 3.9716 | 8.5884 | 8.5463 | 8.4989 | 8.4189 | 8.3147 | 8.2137 | 8.1253 | 8.0389 | 7.9547 | 7.5011 | 5.8905 | 4.3579
EALING GSP |  | EALING PRIMARY | MINIMUM HEADROOM | SZ 06789 95116 | NO | YES | 0 | 90.3663 | 89.9568 | 89.5211 | 89.0642 | 87.9137 | 86.2789 | 85.1716 | 84.1232 | 83.4495 | 80.2947 | 77.0116 | 24.3463 | 80.4484 | 78.8232 | 76.9242 | 74.7811 | 73.0916 | 71.2526 | 70.0253 | 68.8621 | 68.1337 | 64.6905 | 61.0379 | 57.5274 | 82.9568 | 81.3337 | 79.4379 | 77.2979 | 75.5589 | 73.7232 | 72.4968 | 71.3347 | 70.6074 | 67.1674 | 63.52 | 60.0137
|  | EALING PRIMARY | EE |  |  |  |  | 90.5958 | 90.2526 | 89.8895 | 89.5021 | 89.0968 | 88.7053 | 87.3337 | 86.0116 | 85.0358 | 82.9432 | 80.6358 | 78.48 | 81.2484 | 80.1779 | 78.94 | 77.3916 | 75.5758 | 74.0137 | 72.4211 | 70.9305 | 69.8411 | 67.6316 | 65.0726 | 62.6526 | 83.6495 | 82.6874 | 81.4505 | 79.9042 | 78.0916 | 76.5316 | 74.9421 | 73.4526 | 72.3642 | 70.1053 | 67.5495 | 65.1326
|  | EALING PRIMARY | HT |  |  |  |  | 90.3663 | 89.9568 | 89.5211 | 89.0642 | 87.9137 | 86.2789 | 85.1716 | 84.1232 | 83.4495 | 80.2947 | 77.0116 | 73.8832 | 80.4484 | 78.8232 | 76.9242 | 74.7811 | 73.0916 | 71.2526 | 70.0253 | 68.8621 | 68.1337 | 64.6905 | 61.0379 | 57.5274 | 82.9568 | 81.3337 | 79.4379 | 77.2979 | 75.5589 | 73.7232 | 72.4968 | 71.3347 | 70.6074 | 67.1674 | 63.52 | 60.0137
|  | EALING PRIMARY | HE |  |  |  |  | 90.8526 | 90.5832 | 90.2853 | 89.9632 | 89.6221 | 89.2947 | 88.8232 | 87.7242 | 86.9684 | 85.74 | 84.2884 | 24.3463 | 81.8947 | 81.0042 | 79.9337 | 78.5547 | 76.8979 | 75.5063 | 74.0579 | 72.8158 | 71.9695 | 70.7095 | 69.0937 | 67.6095 | 83.9295 | 83.5126 | 82.4432 | 81.0663 | 79.4126 | 78.0232 | 76.5758 | 75.3358 | 74.4905 | 73.18 | 71.5663 | 70.0842
|  | EALING PRIMARY | CF |  |  |  |  | 91.0347 | 90.8695 | 90.6979 | 90.52 | 90.3358 | 90.1484 | 89.9642 | 89.7811 | 89.5989 | 88.7853 | 88.0884 | 87.1832 | 82.5968 | 82.3926 | 82.0758 | 81.7326 | 81.3821 | 81.0305 | 80.5095 | 79.7253 | 78.6979 | 74.2105 | 73.3347 | 72.3105 | 84.1316 | 83.9663 | 83.7937 | 83.6063 | 83.4126 | 83.2158 | 83.0116 | 82.2347 | 81.2095 | 76.7284 | 75.8011 | 74.7779
LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT PRIMARY | MINIMUM HEADROOM | TQ 08394 73826 | NO | YES | 0 | 46.7516 | 46.4726 | 46.1779 | 45.8705 | 45.5537 | 45.2347 | 44.9526 | 44.6947 | 44.4579 | 42.4874 | 40.0632 | -6.9368 | 40.5853 | 40.2105 | 39.8179 | 39.2053 | 38.5916 | 38.0137 | 37.4937 | 37.0032 | 36.54 | 34.1526 | 31.4347 | 28.7958 | 82.0421 | 81.6821 | 81.2916 | 80.6789 | 80.0653 | 79.4874 | 78.9674 | 78.4758 | 78.0126 | 75.6274 | 72.9084 | 70.2695
|  | EAST BEDFONT PRIMARY | EE |  |  |  |  | 46.9126 | 46.6821 | 46.4379 | 46.1811 | 45.9147 | 45.6568 | 45.4105 | 45.1726 | 44.9611 | 44.1811 | 42.6011 | 40.9379 | 40.7958 | 40.4821 | 40.1589 | 39.8263 | 39.4095 | 39.0495 | 38.6832 | 38.2811 | 37.8937 | 36.2 | 34.2568 | 32.3737 | 82.2032 | 81.9495 | 81.6316 | 81.3 | 80.8821 | 80.5221 | 80.1558 | 79.7537 | 79.3663 | 77.6726 | 75.7316 | 73.8474
|  | EAST BEDFONT PRIMARY | HT |  |  |  |  | 46.7516 | 46.4726 | 46.1779 | 45.8705 | 45.5537 | 45.2347 | 44.9526 | 44.6947 | 44.4579 | 42.4874 | 40.0632 | 37.7284 | 40.5853 | 40.2105 | 39.8179 | 39.2053 | 38.5916 | 38.0137 | 37.4937 | 37.0032 | 36.54 | 34.1526 | 31.4347 | 28.7958 | 82.0421 | 81.6821 | 81.2916 | 80.6789 | 80.0653 | 79.4874 | 78.9674 | 78.4758 | 78.0126 | 75.6274 | 72.9084 | 70.2695
|  | EAST BEDFONT PRIMARY | HE |  |  |  |  | 47.1137 | 46.9442 | 46.7568 | 46.5547 | 46.3389 | 46.1337 | 45.94 | 45.7579 | 45.6032 | 45.0716 | 44.7547 | -6.9368 | 41.0411 | 40.8305 | 40.5842 | 40.3242 | 39.9779 | 39.6916 | 39.3958 | 39.0905 | 38.7979 | 37.9179 | 36.8842 | 35.5516 | 82.4042 | 82.2347 | 82.0474 | 81.7937 | 81.4516 | 81.1653 | 80.8695 | 80.5632 | 80.2716 | 79.3905 | 78.3547 | 77.0221
|  | EAST BEDFONT PRIMARY | CF |  |  |  |  | 47.26 | 47.1663 | 47.0695 | 46.9695 | 46.8663 | 46.76 | 46.6558 | 46.5526 | 46.4495 | 45.9905 | 45.7611 | 45.6326 | 41.2305 | 41.1284 | 41.0232 | 40.9021 | 40.7695 | 40.6232 | 40.4716 | 40.3084 | 40.14 | 39.2505 | 38.4442 | 37.5537 | 82.5505 | 82.4568 | 82.36 | 82.26 | 82.1568 | 82.0505 | 81.9379 | 81.7789 | 81.6126 | 80.7242 | 79.9168 | 79.0263
MANNINGTON GSP | REDHILL BSP | EAST HOWE PRIMARY | MINIMUM HEADROOM | SZ 06789 95116 | NO | YES | 0 | 27.7811 | 26.6105 | 25.3653 | 24.0579 | 22.6674 | 21.3126 | 20.2653 | 19.1937 | 18.1674 | 13.6042 | 9.4895 | -16.7705 | 22.2884 | 20.9895 | 19.6074 | 18.1621 | 16.6368 | 15.1568 | 14.0232 | 12.8526 | 11.7274 | 6.7011 | 2.1211 | -2.0695 | 23.1232 | 21.8789 | 20.5232 | 19.0789 | 17.5537 | 16.0716 | 14.9368 | 13.7632 | 12.6379 | 7.6032 | 3.0147 | -1.18
|  | EAST HOWE PRIMARY | EE |  |  |  |  | 28.1789 | 27.4568 | 26.4347 | 25.3042 | 24.1158 | 22.9958 | 22.1779 | 21.3884 | 20.5474 | 16.9811 | 13.7811 | 10.9305 | 23.0011 | 21.92 | 20.7537 | 19.5126 | 18.2084 | 16.9811 | 16.1032 | 15.2568 | 14.3421 | 10.4221 | 6.8516 | 3.6347 | 23.8084 | 22.7737 | 21.6716 | 20.4295 | 19.1242 | 17.8947 | 17.0158 | 16.1684 | 15.2516 | 11.3211 | 7.7379 | 4.5168
|  | EAST HOWE PRIMARY | HT |  |  |  |  | 27.7811 | 26.6105 | 25.3653 | 24.0579 | 22.6674 | 21.3126 | 20.2653 | 19.1937 | 18.1674 | 13.6042 | 9.4895 | 5.7579 | 22.2884 | 20.9895 | 19.6074 | 18.1621 | 16.6368 | 15.1568 | 14.0232 | 12.8526 | 11.7274 | 6.7011 | 2.1211 | -2.0695 | 23.1232 | 21.8789 | 20.5232 | 19.0789 | 17.5537 | 16.0716 | 14.9368 | 13.7632 | 12.6379 | 7.6032 | 3.0147 | -1.18
|  | EAST HOWE PRIMARY | HE |  |  |  |  | 28.6063 | 28.2926 | 27.7758 | 26.9011 | 25.9537 | 25.0684 | 24.4874 | 23.9032 | 23.2684 | 20.7305 | 18.4979 | -16.7705 | 23.9389 | 23.1495 | 22.2611 | 21.2842 | 20.2242 | 19.2368 | 18.6147 | 17.9874 | 17.2937 | 14.4895 | 11.9726 | 9.7316 | 24.7105 | 23.9537 | 23.1053 | 22.1716 | 21.14 | 20.1526 | 19.5295 | 18.9011 | 18.2063 | 15.3979 | 12.8768 | 10.6326
|  | EAST HOWE PRIMARY | CF |  |  |  |  | 28.9116 | 28.7516 | 28.5853 | 28.4137 | 28.2074 | 27.7126 | 27.3284 | 26.9747 | 26.6389 | 25.2021 | 23.7053 | 22.4137 | 24.6084 | 24.1947 | 23.7484 | 23.2674 | 22.7221 | 22.1632 | 21.7368 | 21.3484 | 20.98 | 19.4116 | 17.7158 | 16.2411 | 25.3684 | 24.9621 | 24.5305 | 24.0716 | 23.5537 | 23.0211 | 22.6137 | 22.2389 | 21.8853 | 20.3263 | 18.6274 | 17.1505
MELKSHAM GSP | NORRINGTON BSP | EASTERTON PRIMARY | MINIMUM HEADROOM | SU 01568 54730 | NO | YES | 0 | 17.2495 | 16.9653 | 16.6758 | 16.34 | 15.7811 | 15.0253 | 14.0716 | 13.8621 | 13.6589 | 9.5726 | 6.9663 | 2.4453 | 14.6663 | 14.3547 | 14.04 | 13.6684 | 13.0379 | 12.1674 | 11.1137 | 10.9147 | 10.7253 | 6.2368 | 3.4611 | 2.6589 | 15.1179 | 14.8011 | 14.4811 | 14.1042 | 13.4505 | 12.5505 | 11.4568 | 11.2474 | 11.0442 | 6.4116 | 3.5074 | 2.6537
|  | EASTERTON PRIMARY | EE |  |  |  |  | 17.4421 | 17.2147 | 16.9811 | 16.7179 | 16.3684 | 16.0253 | 15.6295 | 15.1905 | 14.9116 | 13.4189 | 10.3516 | 8.8379 | 14.8811 | 14.6347 | 14.3811 | 14.0937 | 13.7158 | 13.3547 | 12.9305 | 12.4547 | 12.1758 | 10.6937 | 7.4695 | 5.8453 | 15.3358 | 15.0842 | 14.8263 | 14.5337 | 14.1411 | 13.7621 | 13.3158 | 12.8137 | 12.5158 | 10.8979 | 7.4611 | 5.7558
|  | EASTERTON PRIMARY | HT |  |  |  |  | 17.2495 | 16.9653 | 16.6758 | 16.34 | 15.7811 | 15.0253 | 14.0716 | 13.8621 | 13.6589 | 9.5726 | 6.9663 | 6.1653 | 14.6663 | 14.3547 | 14.04 | 13.6684 | 13.0379 | 12.1674 | 11.1137 | 10.9147 | 10.7253 | 6.2368 | 3.4611 | 2.6589 | 15.1179 | 14.8011 | 14.4811 | 14.1042 | 13.4505 | 12.5505 | 11.4568 | 11.2474 | 11.0442 | 6.4116 | 3.5074 | 2.6537
|  | EASTERTON PRIMARY | HE |  |  |  |  | 17.6674 | 17.5537 | 17.4032 | 17.2168 | 16.9442 | 16.6989 | 16.4021 | 16.0758 | 15.9137 | 15.0695 | 12.9758 | 2.4453 | 15.1295 | 15.0105 | 14.8474 | 14.6442 | 14.3495 | 14.0874 | 13.7589 | 13.3937 | 13.2316 | 12.3632 | 10.0147 | 8.7032 | 15.5874 | 15.4674 | 15.3032 | 15.0958 | 14.7895 | 14.5168 | 14.1768 | 13.7958 | 13.6242 | 12.6937 | 10.2442 | 8.8642
|  | EASTERTON PRIMARY | CF |  |  |  |  | 17.7589 | 17.7126 | 17.6642 | 17.5947 | 17.4832 | 17.3684 | 17.2547 | 17.1263 | 16.9853 | 16.3284 | 15.8505 | 15.1105 | 15.2211 | 15.1747 | 15.1263 | 15.0516 | 14.9326 | 14.8116 | 14.6905 | 14.5505 | 14.3937 | 13.6684 | 13.1505 | 12.2968 | 15.6789 | 15.6326 | 15.5842 | 15.5084 | 15.3853 | 15.2579 | 15.1316 | 14.9874 | 14.8242 | 14.0695 | 13.52 | 12.6232
FLEET-BRAMLEY GSP | BRACKNELL BSP | EASTHAMPSTEAD PRIMARY | MINIMUM HEADROOM | SU 86148 67194 | NO | YES | 0 | 34.9263 | 34.5242 | 34.0958 | 33.6495 | 33.1863 | 32.3863 | 31.3747 | 30.7032 | 30.0832 | 26.6232 | 22.4916 | -10.4905 | 29.7695 | 28.9789 | 28.1747 | 27.2642 | 26.0179 | 24.7853 | 23.6832 | 22.9695 | 22.3084 | 18.5463 | 13.9021 | 9.6358 | 30.9379 | 30.1411 | 29.3295 | 28.4105 | 27.1505 | 25.9032 | 24.7874 | 24.0653 | 23.3989 | 19.5905 | 14.9379 | 10.6663
|  | EASTHAMPSTEAD PRIMARY | EE |  |  |  |  | 35.1274 | 34.7821 | 34.4147 | 34.0284 | 33.6232 | 33.2305 | 32.5642 | 31.9653 | 31.4242 | 28.7389 | 25.4232 | 22.46 | 30.26 | 29.6126 | 28.9516 | 28.1779 | 27.0589 | 25.9695 | 24.9716 | 24.3389 | 23.7663 | 20.8695 | 17.1621 | 13.7958 | 31.4305 | 30.7811 | 30.1147 | 29.3347 | 28.2011 | 27.0979 | 26.0874 | 25.4484 | 24.8705 | 21.9316 | 18.1905 | 14.8189
|  | EASTHAMPSTEAD PRIMARY | HT |  |  |  |  | 34.9263 | 34.5242 | 34.0958 | 33.6495 | 33.1863 | 32.3863 | 31.3747 | 30.7032 | 30.0832 | 26.6232 | 22.4916 | 18.7221 | 29.7695 | 28.9789 | 28.1747 | 27.2642 | 26.0179 | 24.7853 | 23.6832 | 22.9695 | 22.3084 | 18.5463 | 13.9021 | 9.6358 | 30.9379 | 30.1411 | 29.3295 | 28.4105 | 27.1505 | 25.9032 | 24.7874 | 24.0653 | 23.3989 | 19.5905 | 14.9379 | 10.6663
|  | EASTHAMPSTEAD PRIMARY | HE |  |  |  |  | 35.4168 | 35.1579 | 34.8716 | 34.5632 | 34.2326 | 33.9168 | 33.6179 | 33.34 | 33.0989 | 31.5589 | 29.0789 | -10.4905 | 31.0105 | 30.4905 | 29.9768 | 29.3874 | 28.4453 | 27.5337 | 26.7158 | 26.2674 | 25.8789 | 23.9053 | 21.1253 | 18.6358 | 31.8505 | 31.5758 | 31.1495 | 30.5558 | 29.6011 | 28.68 | 27.8516 | 27.4 | 27.0074 | 25.0095 | 22.1842 | 19.6789
|  | EASTHAMPSTEAD PRIMARY | CF |  |  |  |  | 35.62 | 35.4716 | 35.3168 | 35.1568 | 34.9895 | 34.82 | 34.6526 | 34.4874 | 34.3221 | 33.5832 | 32.58 | 31.1589 | 31.2316 | 31.0674 | 30.7832 | 30.4474 | 29.9716 | 29.4779 | 29.0011 | 28.6905 | 28.3884 | 26.8042 | 24.9358 | 23.3316 | 32.0653 | 31.9063 | 31.7432 | 31.5726 | 31.1421 | 30.6421 | 30.16 | 29.8474 | 29.5421 | 27.9411 | 26.0442 | 24.4126
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH PRIMARY | MINIMUM HEADROOM | SU 45426 18958 | NO | YES | 0.031579 | 45.7593 | 45.1666 | 44.5372 | 43.3603 | 41.3666 | 39.7824 | 38.4393 | 37.0972 | 35.7382 | 29.4024 | 23.8603 | -23.7755 | 37.0551 | 34.4793 | 31.614 | 29.7161 | 27.4993 | 25.7614 | 24.2919 | 22.8224 | 21.3235 | 14.2477 | 8.0056 | 2.2814 | 39.2887 | 36.7993 | 34.0214 | 32.0835 | 29.8182 | 28.0466 | 26.5498 | 25.0508 | 23.5424 | 16.4719 | 10.2287 | 4.5024
|  | EASTLEIGH NORTH PRIMARY | EE |  |  |  |  | 46.1108 | 45.6245 | 45.1066 | 44.5656 | 43.0245 | 41.7887 | 40.6108 | 39.4951 | 38.3498 | 33.1856 | 28.8372 | 24.9066 | 37.8087 | 35.4603 | 32.8235 | 31.1403 | 29.3035 | 27.9498 | 26.6603 | 25.4635 | 24.1961 | 18.414 | 13.5087 | 9.0751 | 40.0245 | 37.7572 | 35.214 | 33.5319 | 31.654 | 30.2751 | 28.9614 | 27.6845 | 26.4161 | 20.6319 | 15.7329 | 11.2572
|  | EASTLEIGH NORTH PRIMARY | HT |  |  |  |  | 45.7593 | 45.1666 | 44.5372 | 43.3603 | 41.3666 | 39.7824 | 38.4393 | 37.0972 | 35.7382 | 29.4024 | 23.8603 | 18.8056 | 37.0551 | 34.4793 | 31.614 | 29.7161 | 27.4993 | 25.7614 | 24.2919 | 22.8224 | 21.3235 | 14.2477 | 8.0056 | 2.2814 | 39.2887 | 36.7993 | 34.0214 | 32.0835 | 29.8182 | 28.0466 | 26.5498 | 25.0508 | 23.5424 | 16.4719 | 10.2287 | 4.5024
|  | EASTLEIGH NORTH PRIMARY | HE |  |  |  |  | 46.5572 | 46.2066 | 45.8193 | 45.4024 | 44.9582 | 43.9561 | 43.014 | 42.1056 | 41.2572 | 37.2235 | 33.8761 | -23.7755 | 38.7961 | 36.7498 | 34.4035 | 32.9972 | 31.4098 | 30.3035 | 29.2698 | 28.2708 | 27.3624 | 22.8161 | 18.9856 | 15.6677 | 40.6519 | 39.0161 | 36.7561 | 35.3929 | 33.7972 | 32.6687 | 31.6161 | 30.5972 | 29.5824 | 25.0361 | 21.1982 | 17.8372
|  | EASTLEIGH NORTH PRIMARY | CF |  |  |  |  | 46.8687 | 46.6793 | 46.4824 | 46.2793 | 46.0698 | 45.854 | 45.6435 | 45.4351 | 45.2266 | 44.2961 | 42.2624 | 40.4203 | 39.7751 | 38.7403 | 37.6277 | 36.9414 | 36.2508 | 35.7319 | 35.1887 | 34.5919 | 33.9508 | 30.8824 | 28.4414 | 26.3319 | 41.0024 | 40.7624 | 39.8666 | 39.2024 | 38.534 | 38.0277 | 37.4982 | 36.9182 | 36.2972 | 33.2751 | 30.7708 | 28.6024
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY PRIMARY | MINIMUM HEADROOM | SZ 66357 99040 | NO | YES | 0 | 24.7529 | 24.6098 | 24.455 | 24.2856 | 24.1098 | 23.9329 | 23.7729 | 23.6256 | 23.454 | 21.954 | 20.4235 | 9.5203 | 23.0056 | 22.7445 | 22.4624 | 22.1687 | 21.874 | 21.5856 | 21.315 | 21.0613 | 20.7371 | 19.0635 | 17.3413 | 15.7298 | 23.3066 | 23.0887 | 22.8645 | 22.6013 | 22.335 | 22.0729 | 21.8287 | 21.5835 | 21.2698 | 19.5792 | 17.834 | 16.2003
|  | EASTNEY PRIMARY | EE |  |  |  |  | 24.8308 | 24.7108 | 24.5835 | 24.4477 | 24.2982 | 24.1529 | 24.0108 | 23.8729 | 23.7466 | 22.9108 | 21.6971 | 20.6035 | 23.115 | 22.9635 | 22.7508 | 22.514 | 22.2666 | 22.0329 | 21.8035 | 21.5803 | 21.3719 | 20.1361 | 18.7603 | 17.5203 | 23.4403 | 23.2645 | 23.0803 | 22.8887 | 22.6782 | 22.4666 | 22.2561 | 22.054 | 21.8645 | 20.6645 | 19.2687 | 18.0098
|  | EASTNEY PRIMARY | HT |  |  |  |  | 24.7529 | 24.6098 | 24.455 | 24.2856 | 24.1098 | 23.9329 | 23.7729 | 23.6256 | 23.454 | 21.954 | 20.4235 | 18.9845 | 23.0056 | 22.7445 | 22.4624 | 22.1687 | 21.874 | 21.5856 | 21.315 | 21.0613 | 20.7371 | 19.0635 | 17.3413 | 15.7298 | 23.3066 | 23.0887 | 22.8645 | 22.6013 | 22.335 | 22.0729 | 21.8287 | 21.5835 | 21.2698 | 19.5792 | 17.834 | 16.2003
|  | EASTNEY PRIMARY | HE |  |  |  |  | 24.914 | 24.8171 | 24.7098 | 24.594 | 24.4708 | 24.3529 | 24.2413 | 24.1382 | 24.0487 | 23.7161 | 23.3519 | 9.5203 | 23.2413 | 23.1245 | 22.9982 | 22.8635 | 22.7203 | 22.555 | 22.3866 | 22.2287 | 22.0856 | 21.5013 | 20.615 | 19.7161 | 23.5645 | 23.4635 | 23.3277 | 23.1771 | 23.0203 | 22.8698 | 22.7266 | 22.5919 | 22.4719 | 21.9561 | 21.1508 | 20.2361
|  | EASTNEY PRIMARY | CF |  |  |  |  | 24.975 | 24.914 | 24.8508 | 24.7856 | 24.7182 | 24.6487 | 24.5792 | 24.5129 | 24.4456 | 24.134 | 23.9529 | 23.6256 | 23.315 | 23.2329 | 23.154 | 23.074 | 22.9908 | 22.9056 | 22.8119 | 22.694 | 22.5761 | 22.0298 | 21.4792 | 20.8729 | 23.6287 | 23.5635 | 23.495 | 23.4024 | 23.3077 | 23.2098 | 23.1129 | 23.0182 | 22.9224 | 22.4582 | 21.995 | 21.4066
LALEHAM GSP | STAINES BSP | EGHAM PRIMARY | MINIMUM HEADROOM | TQ 01030 71404 | NO | YES | 0 | 39.2747 | 38.9516 | 68.6074 | 68.0853 | 67.4537 | 66.6558 | 65.9147 | 65.2189 | 64.5716 | 61.5989 | 58.8958 | 2.1726 | 30.0568 | 28.7021 | 57.1895 | 56.5684 | 55.8905 | 55.0211 | 54.2084 | 53.4463 | 52.7389 | 49.4674 | 46.4695 | 43.7347 | 32.1011 | 30.7453 | 59.2337 | 58.6116 | 57.9326 | 57.0589 | 56.2442 | 55.4779 | 54.7663 | 51.4716 | 48.4484 | 45.7021
|  | EGHAM PRIMARY | EE |  |  |  |  | 39.4568 | 39.1874 | 68.9021 | 68.6021 | 68.2832 | 67.6242 | 66.9895 | 66.3821 | 65.8274 | 63.3768 | 61.2011 | 59.3126 | 30.4684 | 29.2337 | 57.8442 | 57.3389 | 56.8095 | 56.0937 | 55.4042 | 54.7463 | 54.1463 | 51.4758 | 49.0874 | 46.9695 | 32.5053 | 31.2684 | 59.8779 | 59.3695 | 58.8358 | 58.1137 | 57.4189 | 56.7537 | 56.1474 | 53.4316 | 50.9968 | 48.8547
|  | EGHAM PRIMARY | HT |  |  |  |  | 39.2747 | 38.9516 | 68.6074 | 68.0853 | 67.4537 | 66.6558 | 65.9147 | 65.2189 | 64.5716 | 61.5989 | 58.8958 | 56.4621 | 30.0568 | 28.7021 | 57.1895 | 56.5684 | 55.8905 | 55.0211 | 54.2084 | 53.4463 | 52.7389 | 49.4674 | 46.4695 | 43.7347 | 32.1011 | 30.7453 | 59.2337 | 58.6116 | 57.9326 | 57.0589 | 56.2442 | 55.4779 | 54.7663 | 51.4716 | 48.4484 | 45.7021
|  | EGHAM PRIMARY | HE |  |  |  |  | 39.7042 | 39.5105 | 69.2958 | 69.0653 | 68.8126 | 68.5726 | 68.3453 | 67.8916 | 67.4789 | 65.7316 | 64.2537 | 2.1726 | 31.0179 | 29.9526 | 58.7232 | 58.3716 | 57.9842 | 57.4179 | 56.8737 | 56.3653 | 55.9158 | 53.9863 | 52.3242 | 50.8432 | 33.0621 | 31.9979 | 60.7695 | 60.4179 | 60.0274 | 59.4568 | 58.9116 | 58.4021 | 57.9505 | 56.0053 | 54.3305 | 52.8368
|  | EGHAM PRIMARY | CF |  |  |  |  | 39.8705 | 39.7642 | 69.6547 | 69.5411 | 69.42 | 69.2968 | 69.1737 | 69.0547 | 68.9347 | 68.3989 | 67.9789 | 67.1147 | 31.82 | 31.2737 | 60.6863 | 60.4779 | 60.2653 | 59.9653 | 59.6589 | 59.3558 | 59.0558 | 57.6232 | 56.4726 | 55.4874 | 33.6253 | 33.3074 | 62.7316 | 62.5242 | 62.3105 | 62.0095 | 61.7042 | 61.4 | 61.0989 | 59.6642 | 58.5084 | 57.5189
MANNINGTON GSP | BOURNEMOUTH BSP | ELECTRIC HOUSE PRIMARY | MINIMUM HEADROOM | SZ 08757 91379 | NO | YES | 0.063158 | 26.0937 | 26.0084 | 25.9189 | 25.6105 | 24.5621 | 23.8853 | 23.7032 | 23.5137 | 23.3295 | 22.4547 | 21.6032 | -2.8337 | 25.1021 | 25.0168 | 24.9274 | 24.8295 | 24.7284 | 24.5979 | 24.4032 | 24.1979 | 23.9989 | 23.0516 | 22.12 | 21.2021 | 25.0853 | 25 | 24.9105 | 24.8126 | 24.6516 | 24.5095 | 24.4095 | 24.3137 | 24.1726 | 23.2547 | 22.3074 | 21.3758
|  | ELECTRIC HOUSE PRIMARY | EE |  |  |  |  | 26.1632 | 26.1 | 26.0337 | 25.8379 | 24.8242 | 24.1926 | 24.0558 | 23.9189 | 23.7705 | 23.1 | 22.4484 | 21.8168 | 25.1716 | 25.1084 | 25.0421 | 24.9684 | 24.8905 | 24.8137 | 24.7379 | 24.6305 | 24.4705 | 23.7442 | 23.0274 | 22.3263 | 25.1547 | 25.0916 | 25.0253 | 24.9516 | 24.8211 | 24.7074 | 24.6274 | 24.5463 | 24.4726 | 23.9274 | 23.2284 | 22.5137
|  | ELECTRIC HOUSE PRIMARY | HT |  |  |  |  | 26.0937 | 26.0084 | 25.9189 | 25.6105 | 24.5621 | 23.8853 | 23.7032 | 23.5137 | 23.3295 | 22.4547 | 21.6032 | 20.7779 | 25.1021 | 25.0168 | 24.9274 | 24.8295 | 24.7284 | 24.5979 | 24.4032 | 24.1979 | 23.9989 | 23.0516 | 22.12 | 21.2021 | 25.0853 | 25 | 24.9105 | 24.8126 | 24.6516 | 24.5095 | 24.4095 | 24.3137 | 24.1726 | 23.2547 | 22.3074 | 21.3758
|  | ELECTRIC HOUSE PRIMARY | HE |  |  |  |  | 26.1884 | 26.1305 | 26.0663 | 25.9947 | 25.0021 | 24.3947 | 24.2916 | 24.1874 | 24.0726 | 23.5863 | 23.1316 | -2.8337 | 25.1968 | 25.1389 | 25.0747 | 25.0053 | 24.9305 | 24.86 | 24.7937 | 24.7316 | 24.6779 | 24.2758 | 23.7737 | 23.2968 | 25.18 | 25.1221 | 25.0579 | 24.9884 | 24.8695 | 24.7632 | 24.6947 | 24.6295 | 24.5726 | 24.3579 | 23.9579 | 23.5
|  | ELECTRIC HOUSE PRIMARY | CF |  |  |  |  | 26.2137 | 26.1726 | 26.1305 | 26.0863 | 26.0411 | 25.9947 | 25.9495 | 25.9042 | 25.86 | 25.5263 | 25.1926 | 24.8937 | 25.2221 | 25.1811 | 25.1389 | 25.0947 | 25.0495 | 25.0032 | 24.9579 | 24.9126 | 24.8684 | 24.6674 | 24.5642 | 24.5053 | 25.2053 | 25.1642 | 25.1221 | 25.0779 | 25.0326 | 24.9863 | 24.9411 | 24.8958 | 24.8516 | 24.6505 | 24.54 | 24.4653
FLEET-BRAMLEY GSP | WOKINGHAM BSP | ELMS ROAD PRIMARY | MINIMUM HEADROOM | SU 81057 68532 | NO | YES | 0.34737 | 29.6447 | 29.2911 | 28.7889 | 27.7079 | 26.5289 | 25.1879 | 23.9079 | 22.6058 | 21.3668 | 16.8574 | 14.2795 | -11.1511 | 23.5005 | 22.4458 | 21.1679 | 19.9658 | 18.6511 | 17.1468 | 15.7047 | 14.2321 | 12.8289 | 7.7416 | 4.8711 | 2.0763 | 25.0237 | 23.9953 | 22.75 | 21.5774 | 20.2963 | 18.8311 | 17.4268 | 15.9532 | 14.55 | 9.4616 | 6.59 | 3.7942
|  | ELMS ROAD PRIMARY | EE |  |  |  |  | 29.8584 | 29.57 | 29.2637 | 28.6847 | 27.7479 | 26.7332 | 25.7237 | 24.55 | 23.3921 | 19.3711 | 17.5605 | 15.8511 | 24.0079 | 23.1395 | 22.0279 | 21.0405 | 19.9974 | 18.8626 | 17.73 | 16.4026 | 15.0889 | 10.5311 | 8.5153 | 6.59 | 25.5216 | 24.6742 | 23.5921 | 22.6279 | 21.6111 | 20.5058 | 19.4026 | 18.1132 | 16.81 | 12.2521 | 10.2353 | 8.3089
|  | ELMS ROAD PRIMARY | HT |  |  |  |  | 29.6447 | 29.2911 | 28.7889 | 27.7079 | 26.5289 | 25.1879 | 23.9079 | 22.6058 | 21.3668 | 16.8574 | 14.2795 | 11.7953 | 23.5005 | 22.4458 | 21.1679 | 19.9658 | 18.6511 | 17.1468 | 15.7047 | 14.2321 | 12.8289 | 7.7416 | 4.8711 | 2.0763 | 25.0237 | 23.9953 | 22.75 | 21.5774 | 20.2963 | 18.8311 | 17.4268 | 15.9532 | 14.55 | 9.4616 | 6.59 | 3.7942
|  | ELMS ROAD PRIMARY | HE |  |  |  |  | 30.1311 | 29.9258 | 29.6995 | 29.4553 | 28.9226 | 28.0458 | 27.1426 | 26.1016 | 25.0889 | 21.7847 | 20.5837 | -11.1511 | 24.6089 | 23.9258 | 22.9921 | 22.1689 | 21.2763 | 20.29 | 19.27 | 18.0858 | 16.9311 | 13.1616 | 11.8153 | 10.4963 | 26.1111 | 25.4447 | 24.5363 | 23.7342 | 22.8647 | 21.9047 | 20.9142 | 19.7647 | 18.6437 | 14.8826 | 13.5353 | 12.2163
|  | ELMS ROAD PRIMARY | CF |  |  |  |  | 30.3121 | 30.2016 | 30.0858 | 29.9668 | 29.8437 | 29.7184 | 29.5953 | 29.4732 | 29.35 | 25.7711 | 25.0153 | 24.4942 | 25.3395 | 24.9521 | 24.4668 | 24.0584 | 23.6605 | 23.2521 | 22.8226 | 22.3742 | 21.8942 | 17.6437 | 16.8037 | 16.2174 | 26.3879 | 26.2605 | 25.9721 | 25.5732 | 25.1858 | 24.7879 | 24.3689 | 23.9332 | 23.4658 | 19.35 | 18.5247 | 17.9384
LOVEDEAN GSP | HAVANT BSP | EMSWORTH PRIMARY | MINIMUM HEADROOM | SU 74861 05807 | NO | YES | 0.84211 | 11.8389 | 11.5705 | 11.1042 | 30.4863 | 29.6642 | 28.5947 | 27.3537 | 25.8884 | 24.4968 | 18.1484 | 13.3168 | -2.5274 | 8.0684 | 7.8 | 7.2958 | 26.6105 | 25.6979 | 24.4937 | 23.08 | 21.3979 | 19.8011 | 12.4905 | 6.9242 | 4.1758 | 8.5716 | 8.3032 | 7.8158 | 27.16 | 26.2926 | 25.1558 | 23.7937 | 22.1147 | 20.5189 | 13.2211 | 7.6653 | 4.92
|  | EMSWORTH PRIMARY | EE |  |  |  |  | 11.9979 | 11.7768 | 11.5421 | 31.1305 | 30.4547 | 29.5947 | 28.5926 | 27.2432 | 25.9358 | 20.0484 | 15.6663 | 13.7758 | 8.2274 | 8.0063 | 7.7716 | 27.3253 | 26.5642 | 25.5958 | 24.4579 | 22.9084 | 21.4053 | 14.6042 | 9.5326 | 7.3705 | 8.7305 | 8.5095 | 8.2747 | 27.8432 | 27.1211 | 26.2063 | 25.1368 | 23.6232 | 22.1221 | 15.3326 | 10.2705 | 8.1116
|  | EMSWORTH PRIMARY | HT |  |  |  |  | 11.8389 | 11.5705 | 11.1042 | 30.4863 | 29.6642 | 28.5947 | 27.3537 | 25.8884 | 24.4968 | 18.1484 | 13.3168 | 10.9011 | 8.0684 | 7.8 | 7.2958 | 26.6105 | 25.6979 | 24.4937 | 23.08 | 21.3979 | 19.8011 | 12.4905 | 6.9242 | 4.1758 | 8.5716 | 8.3032 | 7.8158 | 27.16 | 26.2926 | 25.1558 | 23.7937 | 22.1147 | 20.5189 | 13.2211 | 7.6653 | 4.92
|  | EMSWORTH PRIMARY | HE |  |  |  |  | 12.2074 | 12.0505 | 11.8789 | 31.6926 | 31.3579 | 30.6116 | 29.6905 | 28.4284 | 27.2379 | 21.9232 | 17.9779 | -2.5274 | 8.4368 | 8.28 | 8.1084 | 27.9221 | 27.56 | 26.7032 | 25.6516 | 24.1958 | 22.82 | 16.6516 | 12.0589 | 10.3842 | 8.94 | 8.7832 | 8.6116 | 28.4253 | 28.0747 | 27.2684 | 26.2821 | 24.9084 | 23.5347 | 17.3779 | 12.7926 | 11.1211
|  | EMSWORTH PRIMARY | CF |  |  |  |  | 12.3495 | 12.2674 | 12.1811 | 32.0916 | 32 | 31.9053 | 31.6411 | 31.2611 | 30.8716 | 28.1389 | 23.9158 | 23 | 8.5789 | 8.4968 | 8.4105 | 28.3211 | 28.2295 | 28.1347 | 27.8347 | 27.3947 | 26.9526 | 23.8095 | 18.8747 | 17.8168 | 9.0821 | 9 | 8.9137 | 28.8242 | 28.7326 | 28.6379 | 28.3537 | 27.9389 | 27.5232 | 24.5232 | 19.5979 | 18.5421
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | ENFORD PRIMARY | MINIMUM HEADROOM | SU 13728 51712 | NO | YES | 0 | 8.5726 | 8.4695 | 8.3642 | 8.2579 | 8.1463 | 7.9284 | 7.6684 | 7.6042 | 7.5421 | 6.9863 | 6.3074 | 2.4926 | 7.9432 | 7.8316 | 7.7168 | 7.6042 | 7.4853 | 7.2421 | 6.9453 | 6.8842 | 6.8253 | 6.2337 | 5.4895 | 5.2547 | 8.1758 | 8.0642 | 7.9495 | 7.8358 | 7.7168 | 7.4705 | 7.1726 | 7.1074 | 7.0453 | 6.4347 | 5.6674 | 5.4242
|  | ENFORD PRIMARY | EE |  |  |  |  | 8.6421 | 8.5589 | 8.4737 | 8.3874 | 8.2947 | 8.2 | 8.1084 | 8.0189 | 7.9326 | 7.5032 | 6.9884 | 6.5884 | 8.02 | 7.9305 | 7.8389 | 7.7474 | 7.6495 | 7.5537 | 7.46 | 7.3684 | 7.2821 | 6.8474 | 6.3084 | 5.8632 | 8.2526 | 8.1632 | 8.0716 | 7.9789 | 7.88 | 7.7811 | 7.6832 | 7.5884 | 7.4979 | 7.0368 | 6.4663 | 6.0116
|  | ENFORD PRIMARY | HT |  |  |  |  | 8.5726 | 8.4695 | 8.3642 | 8.2579 | 8.1463 | 7.9284 | 7.6684 | 7.6042 | 7.5421 | 6.9863 | 6.3074 | 6.08 | 7.9432 | 7.8316 | 7.7168 | 7.6042 | 7.4853 | 7.2421 | 6.9453 | 6.8842 | 6.8253 | 6.2337 | 5.4895 | 5.2547 | 8.1758 | 8.0642 | 7.9495 | 7.8358 | 7.7168 | 7.4705 | 7.1726 | 7.1074 | 7.0453 | 6.4347 | 5.6674 | 5.4242
|  | ENFORD PRIMARY | HE |  |  |  |  | 8.7368 | 8.6832 | 8.6284 | 8.5695 | 8.5021 | 8.4379 | 8.3789 | 8.32 | 8.2674 | 8.0147 | 7.6611 | 2.4926 | 8.1253 | 8.0674 | 8.0084 | 7.9463 | 7.8779 | 7.8116 | 7.7495 | 7.6905 | 7.6379 | 7.3768 | 6.9789 | 6.6263 | 8.3453 | 8.3 | 8.2411 | 8.1789 | 8.1084 | 8.0411 | 7.9779 | 7.9168 | 7.8621 | 7.5905 | 7.1842 | 6.8232
|  | ENFORD PRIMARY | CF |  |  |  |  | 8.7916 | 8.76 | 8.7284 | 8.6958 | 8.6579 | 8.62 | 8.58 | 8.5474 | 8.5116 | 8.3484 | 8.2042 | 7.9895 | 8.1832 | 8.1495 | 8.1147 | 8.08 | 8.0379 | 7.9979 | 7.9579 | 7.9221 | 7.8842 | 7.7137 | 7.5579 | 7.3147 | 8.3789 | 8.3611 | 8.3421 | 8.3126 | 8.2716 | 8.2295 | 8.1884 | 8.1516 | 8.1137 | 7.9389 | 7.7779 | 7.5295
COWLEY GSP | YARNTON BSP | EYNSHAM PRIMARY | MINIMUM HEADROOM | SP 42236 10266 | NO | YES | 0.21053 | 28.8382 | 28.3539 | 26.8171 | 26.6529 | 25.6697 | 23.7929 | 21.6466 | 19.9655 | 18.3361 | 11.9634 | 8.4824 | -4.3692 | 24.2539 | 23.7171 | 21.9592 | 21.795 | 20.7139 | 18.5434 | 16.055 | 14.1097 | 12.2234 | 4.8624 | 0.88026 | -0.90289 | 25.3034 | 24.7666 | 22.9645 | 22.8003 | 21.7182 | 19.5508 | 17.0634 | 15.1192 | 13.2329 | 5.8655 | 1.8676 | 0.078158
|  | EYNSHAM PRIMARY | EE |  |  |  |  | 29.0518 | 28.6318 | 26.8171 | 26.6529 | 26.4782 | 25.4087 | 23.7634 | 21.8234 | 19.5518 | 13.1445 | 9.7192 | 8.4645 | 24.4866 | 24.0192 | 21.9592 | 21.795 | 21.6213 | 20.3971 | 18.495 | 16.2445 | 13.6013 | 6.1908 | 2.2655 | 0.84553 | 25.5361 | 25.0676 | 22.9645 | 22.8003 | 22.6255 | 21.3992 | 19.4971 | 17.2476 | 14.6055 | 7.1803 | 3.2318 | 1.8034
|  | EYNSHAM PRIMARY | HT |  |  |  |  | 28.8382 | 28.3539 | 27.6982 | 26.9487 | 25.6697 | 23.7929 | 21.6466 | 19.9655 | 18.3361 | 11.9634 | 8.4824 | 6.9024 | 24.2539 | 23.7171 | 23.0255 | 22.1792 | 20.7139 | 18.5434 | 16.055 | 14.1097 | 12.2234 | 4.8624 | 0.88026 | -0.90289 | 25.3034 | 24.7666 | 24.0297 | 23.1834 | 21.7182 | 19.5508 | 17.0634 | 15.1192 | 13.2329 | 5.8655 | 1.8676 | 0.078158
|  | EYNSHAM PRIMARY | HE |  |  |  |  | 29.3413 | 29.0108 | 28.5603 | 28.115 | 27.2529 | 26.0424 | 24.3466 | 22.4718 | 20.3845 | 14.415 | 11.4255 | -4.3692 | 24.8013 | 24.4318 | 23.9224 | 23.4203 | 22.4782 | 21.0771 | 19.1055 | 16.9224 | 14.4845 | 7.535 | 4.0655 | 2.9666 | 25.8508 | 25.4813 | 24.9718 | 24.4697 | 23.4813 | 22.0813 | 20.1118 | 17.9308 | 15.4971 | 8.5476 | 5.075 | 3.9708
|  | EYNSHAM PRIMARY | CF |  |  |  |  | 29.5339 | 29.3603 | 29.1645 | 29.0529 | 28.9371 | 28.8161 | 28.5729 | 28.2497 | 27.6013 | 22.8055 | 18.435 | 17.8392 | 25.0108 | 24.8161 | 24.595 | 24.475 | 24.3508 | 24.2192 | 23.9455 | 23.5771 | 22.8276 | 17.2824 | 12.1708 | 11.4908 | 26.0603 | 25.8655 | 25.6445 | 25.5234 | 25.3992 | 25.2676 | 24.9929 | 24.6245 | 23.8729 | 18.2897 | 13.1824 | 12.4982
MINETY GSP | CIRENCESTER BSP | FAIRFORD PRIMARY | MINIMUM HEADROOM | SP 14418 00559 | NO | YES | 0.014737 | 18.3713 | 18.2039 | 18.026 | 17.7534 | 17.3692 | 16.9828 | 16.6197 | 16.2681 | 15.9671 | 14.1986 | 12.3439 | 0.346 | 15.0449 | 14.726 | 14.3628 | 13.9818 | 13.5723 | 13.1597 | 12.7692 | 12.3923 | 12.0734 | 10.1618 | 8.1344 | 6.3618 | 15.6544 | 15.3197 | 14.9502 | 14.5765 | 14.1702 | 13.7597 | 13.3723 | 12.9986 | 12.6797 | 10.7513 | 8.6692 | 6.8755
|  | FAIRFORD PRIMARY | EE |  |  |  |  | 18.9713 | 18.7271 | 18.5376 | 18.266 | 17.966 | 17.6628 | 17.3618 | 17.066 | 16.8197 | 15.3155 | 13.7018 | 12.4155 | 15.3071 | 15.0449 | 14.7555 | 14.4649 | 14.1481 | 13.8292 | 13.5144 | 13.2071 | 12.9555 | 11.3765 | 9.6607 | 8.226 | 15.9744 | 15.7102 | 15.4228 | 15.1302 | 14.8092 | 14.4828 | 14.1597 | 13.8418 | 13.5807 | 11.9334 | 10.1407 | 8.6828
|  | FAIRFORD PRIMARY | HT |  |  |  |  | 18.3713 | 18.2039 | 18.026 | 17.7534 | 17.3692 | 16.9828 | 16.6197 | 16.2681 | 15.9671 | 14.1986 | 12.3439 | 10.7649 | 15.0449 | 14.726 | 14.3628 | 13.9818 | 13.5723 | 13.1597 | 12.7692 | 12.3923 | 12.0734 | 10.1618 | 8.1344 | 6.3618 | 15.6544 | 15.3197 | 14.9502 | 14.5765 | 14.1702 | 13.7597 | 13.3723 | 12.9986 | 12.6797 | 10.7513 | 8.6692 | 6.8755
|  | FAIRFORD PRIMARY | HE |  |  |  |  | 18.6071 | 18.5123 | 18.8913 | 18.6965 | 18.4723 | 18.2523 | 18.0344 | 17.826 | 17.666 | 16.6271 | 15.5155 | 0.346 | 15.5249 | 15.3628 | 15.2249 | 15.0155 | 14.7786 | 14.5449 | 14.3144 | 14.0934 | 13.9271 | 12.7965 | 11.5492 | 10.4123 | 15.9755 | 15.8765 | 15.8923 | 15.6828 | 15.4428 | 15.2049 | 14.9692 | 14.7439 | 14.5744 | 13.4155 | 12.1481 | 10.9934
|  | FAIRFORD PRIMARY | CF |  |  |  |  | 18.6986 | 18.6502 | 18.6007 | 18.5492 | 18.4892 | 18.4281 | 18.3671 | 18.3081 | 18.2502 | 17.9039 | 17.1986 | 16.5818 | 15.6723 | 15.5902 | 15.4955 | 15.3986 | 15.2944 | 15.1849 | 15.0723 | 14.9586 | 14.8628 | 14.1523 | 13.3597 | 12.6639 | 16.0713 | 16.0197 | 15.9671 | 15.9123 | 15.8513 | 15.7871 | 15.6818 | 15.5607 | 15.4607 | 14.7323 | 13.9534 | 13.2692
MINETY GSP | STRATTON (RESERVE) BSP | FARINGDON PRIMARY | MINIMUM HEADROOM | SU 28819 94924 | NO | YES | 0 | 43.9147 | 43.5926 | 43.0053 | 42.6 | 42.3211 | 41.2242 | 40.4653 | 40.2232 | 39.9937 | 38.2189 | 36.1547 | 19.5379 | 39.6495 | 38.9347 | 38.2747 | 37.8368 | 37.4558 | 36.2253 | 35.3874 | 35.1568 | 34.94 | 33.1179 | 30.9453 | 29.8895 | 40.4611 | 39.7653 | 39.1053 | 38.6663 | 38.1958 | 36.9579 | 36.1116 | 35.8684 | 35.6389 | 33.7358 | 31.4695 | 30.3768
|  | FARINGDON PRIMARY | EE |  |  |  |  | 44.0411 | 43.8568 | 43.4063 | 43.0716 | 42.7011 | 42.4874 | 42.1147 | 41.7547 | 41.4137 | 39.8432 | 38.3737 | 36.8537 | 39.9284 | 39.2947 | 38.7179 | 38.3568 | 37.9695 | 37.5779 | 37.1968 | 36.8284 | 36.4853 | 34.9221 | 33.4705 | 31.8011 | 40.7295 | 40.1253 | 39.5474 | 39.1853 | 38.7895 | 38.3874 | 37.9916 | 37.6105 | 37.2505 | 35.5821 | 34.0116 | 32.3042
|  | FARINGDON PRIMARY | HT |  |  |  |  | 43.9147 | 43.5926 | 43.0053 | 42.6 | 42.3211 | 41.2242 | 40.4653 | 40.2232 | 39.9937 | 38.2189 | 36.1547 | 35.1379 | 39.6495 | 38.9347 | 38.2747 | 37.8368 | 37.4558 | 36.2253 | 35.3874 | 35.1568 | 34.94 | 33.1179 | 30.9453 | 29.8895 | 40.4611 | 39.7653 | 39.1053 | 38.6663 | 38.1958 | 36.9579 | 36.1116 | 35.8684 | 35.6389 | 33.7358 | 31.4695 | 30.3768
|  | FARINGDON PRIMARY | HE |  |  |  |  | 44.2105 | 44.0832 | 43.9411 | 43.7242 | 43.4516 | 43.1874 | 42.9326 | 42.6937 | 42.4789 | 41.5853 | 40.7705 | 19.5379 | 40.3053 | 39.7916 | 39.3263 | 39.0737 | 38.7905 | 38.5147 | 38.2505 | 38.0021 | 37.7811 | 36.8695 | 35.9989 | 34.8747 | 41.0916 | 40.6053 | 40.1579 | 39.9053 | 39.6147 | 39.3337 | 39.0621 | 38.8084 | 38.5811 | 37.6253 | 36.7211 | 35.5642
|  | FARINGDON PRIMARY | CF |  |  |  |  | 44.3284 | 44.2611 | 44.1905 | 44.1179 | 44.0316 | 43.9442 | 43.8579 | 43.7726 | 43.6905 | 43.1495 | 42.6653 | 41.9989 | 40.66 | 40.3916 | 40.1558 | 40.0147 | 39.8589 | 39.6979 | 39.5379 | 39.3811 | 39.2284 | 38.5137 | 38 | 37.2558 | 41.2253 | 41.1463 | 40.9516 | 40.8147 | 40.6611 | 40.5021 | 40.3432 | 40.1895 | 40.04 | 39.3168 | 38.7832 | 38.0189
LOVEDEAN GSP | PORTSMOUTH BSP | FARLINGTON PRIMARY | MINIMUM HEADROOM | SU 67400 04843 | NO | YES | 1.0516 | 21.0126 | 20.9221 | 20.8252 | 20.7252 | 20.6231 | 20.5199 | 20.4284 | 20.3463 | 20.2705 | 19.5926 | 18.8073 | 6.4147 | 19.2147 | 19.0484 | 18.8789 | 18.7042 | 18.5305 | 18.3631 | 18.2094 | 18.0673 | 17.8968 | 17.0452 | 16.1726 | 15.3621 | 18.8042 | 18.7136 | 18.6168 | 18.5168 | 18.4147 | 18.3115 | 18.2199 | 18.1378 | 18.0621 | 17.4178 | 16.5326 | 15.7231
|  | FARLINGTON PRIMARY | EE |  |  |  |  | 21.0642 | 20.9884 | 20.9084 | 20.8231 | 20.7368 | 20.6526 | 20.5726 | 20.4957 | 20.4284 | 20.1621 | 19.5473 | 19.0031 | 19.3273 | 19.1957 | 19.0599 | 18.9189 | 18.7757 | 18.6389 | 18.5105 | 18.3863 | 18.2726 | 17.6547 | 16.9863 | 16.3757 | 18.8557 | 18.7799 | 18.6999 | 18.6147 | 18.5284 | 18.4442 | 18.3642 | 18.2873 | 18.2199 | 17.9715 | 17.3547 | 16.7357
|  | FARLINGTON PRIMARY | HT |  |  |  |  | 21.0126 | 20.9221 | 20.8252 | 20.7252 | 20.6231 | 20.5199 | 20.4284 | 20.3463 | 20.2705 | 19.5926 | 18.8073 | 18.0926 | 19.2147 | 19.0484 | 18.8789 | 18.7042 | 18.5305 | 18.3631 | 18.2094 | 18.0673 | 17.8968 | 17.0452 | 16.1726 | 15.3621 | 18.8042 | 18.7136 | 18.6168 | 18.5168 | 18.4147 | 18.3115 | 18.2199 | 18.1378 | 18.0621 | 17.4178 | 16.5326 | 15.7231
|  | FARLINGTON PRIMARY | HE |  |  |  |  | 21.1336 | 21.0799 | 21.0199 | 20.9557 | 20.8873 | 20.8221 | 20.7599 | 20.701 | 20.6515 | 20.4842 | 20.3873 | 6.4147 | 19.4736 | 19.3863 | 19.2926 | 19.1968 | 19.0947 | 18.9989 | 18.9073 | 18.8199 | 18.7431 | 18.4431 | 18.0305 | 17.6157 | 18.9252 | 18.8715 | 18.8115 | 18.7473 | 18.6789 | 18.6136 | 18.5515 | 18.4926 | 18.4431 | 18.2757 | 18.1789 | 17.9947
|  | FARLINGTON PRIMARY | CF |  |  |  |  | 21.1821 | 21.1526 | 21.1221 | 21.0915 | 21.0589 | 21.0252 | 20.9926 | 20.9599 | 20.9284 | 20.7842 | 20.7126 | 20.6736 | 19.5526 | 19.4926 | 19.4378 | 19.3821 | 19.3242 | 19.2652 | 19.2084 | 19.1494 | 19.0926 | 18.8315 | 18.5757 | 18.3031 | 18.9736 | 18.9442 | 18.9136 | 18.8831 | 18.8505 | 18.8168 | 18.7842 | 18.7515 | 18.7199 | 18.5757 | 18.5042 | 18.4652
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FARNBOROUGH PRIMARY | MINIMUM HEADROOM | SU 88404 53930 | NO | YES | 0.26421 | 33.8543 | 33.5048 | 33.1343 | 32.7501 | 32.0522 | 30.6595 | 29.5722 | 28.5216 | 27.5058 | 22.6469 | 20.289 | -7.9521 | 29.2111 | 28.4322 | 27.609 | 26.7922 | 25.1869 | 23.6195 | 22.4037 | 21.2248 | 20.0848 | 14.5932 | 11.9901 | 9.6237 | 30.2479 | 29.4858 | 28.6806 | 27.8806 | 26.3195 | 24.7974 | 23.6143 | 22.4658 | 21.3385 | 15.8458 | 13.2385 | 10.8701
|  | FARNBOROUGH PRIMARY | EE |  |  |  |  | 34.0585 | 33.7722 | 33.4648 | 33.1448 | 32.8111 | 31.6764 | 30.6743 | 29.6879 | 28.7543 | 24.3753 | 22.5564 | 20.9753 | 29.6606 | 29.0195 | 28.3279 | 27.6395 | 26.1553 | 24.7216 | 23.5985 | 22.4922 | 21.4416 | 16.4764 | 14.4722 | 12.7037 | 30.689 | 30.0606 | 29.3837 | 28.7101 | 27.269 | 25.8764 | 24.7837 | 23.7079 | 22.6869 | 17.7227 | 15.7079 | 13.9374
|  | FARNBOROUGH PRIMARY | HT |  |  |  |  | 33.8543 | 33.5048 | 33.1343 | 32.7501 | 32.0522 | 30.6595 | 29.5722 | 28.5216 | 27.5058 | 22.6469 | 20.289 | 18.1669 | 29.2111 | 28.4322 | 27.609 | 26.7922 | 25.1869 | 23.6195 | 22.4037 | 21.2248 | 20.0848 | 14.5932 | 11.9901 | 9.6237 | 30.2479 | 29.4858 | 28.6806 | 27.8806 | 26.3195 | 24.7974 | 23.6143 | 22.4658 | 21.3385 | 15.8458 | 13.2385 | 10.8701
|  | FARNBOROUGH PRIMARY | HE |  |  |  |  | 34.3227 | 34.1164 | 33.889 | 33.6427 | 33.3785 | 32.9869 | 32.1258 | 31.2827 | 30.4901 | 26.8027 | 25.6427 | -7.9521 | 30.2543 | 29.7974 | 29.2816 | 28.7595 | 27.429 | 26.1501 | 25.1795 | 24.2269 | 23.3301 | 19.1122 | 17.8216 | 16.7101 | 31.0364 | 30.8143 | 30.3174 | 29.8058 | 28.5164 | 27.2753 | 26.3332 | 25.4079 | 24.5374 | 20.3669 | 19.0732 | 17.9616
|  | FARNBOROUGH PRIMARY | CF |  |  |  |  | 34.5037 | 34.3922 | 34.2753 | 34.1543 | 34.029 | 33.9006 | 33.7743 | 33.6501 | 33.5258 | 31.1658 | 30.3101 | 29.6048 | 30.6522 | 30.4258 | 30.1437 | 29.8637 | 29.2648 | 28.6269 | 28.1016 | 27.5479 | 26.9753 | 24.0374 | 23.0816 | 22.2827 | 31.2343 | 31.1122 | 30.9848 | 30.8543 | 30.3058 | 29.6879 | 29.1774 | 28.6406 | 28.0848 | 25.2374 | 24.3058 | 23.529
FLEET-BRAMLEY GSP | PYESTOCK BSP | FARNBORO AIRFIELD PRIMARY | MINIMUM HEADROOM | SU 85838 54449 | NO | YES | 0 | 41.0135 | 40.9903 | 40.9651 | 40.9387 | 40.9124 | 40.8851 | 40.8608 | 40.8398 | 40.8187 | 40.7366 | 40.6735 | 26.7535 | 39.0019 | 38.9545 | 38.8998 | 38.844 | 38.7272 | 38.6208 | 38.5398 | 38.4608 | 38.3661 | 38.2019 | 37.9703 | 37.7524 | 39.5345 | 39.5072 | 39.4766 | 39.4451 | 39.4124 | 39.3672 | 39.2798 | 39.1956 | 39.1008 | 38.9366 | 38.7061 | 38.4872
|  | FARNBORO AIRFIELD PRIMARY | EE |  |  |  |  | 41.0261 | 41.0061 | 40.984 | 40.9619 | 40.9387 | 40.9166 | 40.8945 | 40.8745 | 40.8556 | 40.7882 | 40.7408 | 40.7061 | 39.0198 | 38.9777 | 38.9272 | 38.8766 | 38.7851 | 38.6882 | 38.6114 | 38.5387 | 38.4535 | 38.324 | 38.1535 | 38.0008 | 39.5482 | 39.524 | 39.4966 | 39.4693 | 39.4408 | 39.4135 | 39.3566 | 39.2777 | 39.1872 | 39.0587 | 38.8882 | 38.7356
|  | FARNBORO AIRFIELD PRIMARY | HT |  |  |  |  | 41.0135 | 40.9903 | 40.9651 | 40.9387 | 40.9124 | 40.8851 | 40.8608 | 40.8398 | 40.8187 | 40.7366 | 40.6735 | 40.6229 | 39.0019 | 38.9545 | 38.8998 | 38.844 | 38.7272 | 38.6208 | 38.5398 | 38.4608 | 38.3661 | 38.2019 | 37.9703 | 37.7524 | 39.5345 | 39.5072 | 39.4766 | 39.4451 | 39.4124 | 39.3672 | 39.2798 | 39.1956 | 39.1008 | 38.9366 | 38.7061 | 38.4872
|  | FARNBORO AIRFIELD PRIMARY | HE |  |  |  |  | 41.0429 | 41.0282 | 41.0114 | 40.9945 | 40.9756 | 40.9577 | 40.9408 | 40.9251 | 40.9114 | 40.8651 | 40.8377 | 26.7535 | 39.044 | 39.0093 | 38.9661 | 38.9229 | 38.8672 | 38.7787 | 38.7135 | 38.6493 | 38.5766 | 38.5029 | 38.3829 | 38.2808 | 39.5661 | 39.5482 | 39.5261 | 39.5051 | 39.4798 | 39.4577 | 39.4377 | 39.3945 | 39.3156 | 39.2387 | 39.1177 | 39.0156
|  | FARNBORO AIRFIELD PRIMARY | CF |  |  |  |  | 41.0556 | 41.0472 | 41.0377 | 41.0293 | 41.0198 | 41.0103 | 41.0008 | 40.9924 | 40.9829 | 40.9419 | 40.9208 | 40.9103 | 39.0808 | 39.0629 | 39.0408 | 39.0208 | 38.9977 | 38.9766 | 38.9577 | 38.9398 | 38.9177 | 38.8661 | 38.8251 | 38.7587 | 39.584 | 39.5735 | 39.5619 | 39.5514 | 39.5387 | 39.5272 | 39.5166 | 39.5061 | 39.4945 | 39.4514 | 39.4261 | 39.4124
FLEET-BRAMLEY GSP | ALDERSHOT BSP | FARNHAM PRIMARY | MINIMUM HEADROOM | SU 84517 47217 | NO | YES | 0 | 24.5695 | 24.2516 | 23.8989 | 23.5221 | 22.8442 | 22.0242 | 21.5232 | 21.0305 | 20.5726 | 18.5126 | 16.6526 | -22.4032 | 20.0221 | 19.2221 | 18.1453 | 16.8589 | 15.4526 | 14.5453 | 14.0074 | 13.4737 | 12.9789 | 10.7295 | 8.6758 | 6.7874 | 21.2768 | 20.4768 | 19.4 | 18.1126 | 16.7053 | 15.7979 | 15.26 | 14.7253 | 14.2295 | 11.9779 | 9.92 | 8.0295
|  | FARNHAM PRIMARY | EE |  |  |  |  | 24.7463 | 24.4916 | 24.2032 | 23.8874 | 23.5537 | 22.9505 | 22.4832 | 22.0347 | 21.6516 | 20.0232 | 18.6095 | 17.3632 | 20.3874 | 19.6979 | 18.8095 | 17.6947 | 16.4263 | 15.5547 | 15.0495 | 14.5653 | 14.1505 | 12.3789 | 10.8126 | 9.4168 | 21.6421 | 20.9516 | 20.0632 | 18.9484 | 17.6789 | 16.8084 | 16.3021 | 15.8158 | 15.4021 | 13.6242 | 12.0537 | 10.6558
|  | FARNHAM PRIMARY | HT |  |  |  |  | 24.5695 | 24.2516 | 23.8989 | 23.5221 | 22.8442 | 22.0242 | 21.5232 | 21.0305 | 20.5726 | 18.5126 | 16.6526 | 14.9589 | 20.0221 | 19.2221 | 18.1453 | 16.8589 | 15.4526 | 14.5453 | 14.0074 | 13.4737 | 12.9789 | 10.7295 | 8.6758 | 6.7874 | 21.2768 | 20.4768 | 19.4 | 18.1126 | 16.7053 | 15.7979 | 15.26 | 14.7253 | 14.2295 | 11.9779 | 9.92 | 8.0295
|  | FARNHAM PRIMARY | HE |  |  |  |  | 24.9621 | 24.7968 | 24.5768 | 24.3284 | 24.0537 | 23.8179 | 23.6147 | 23.3105 | 23.0379 | 21.9495 | 21.0358 | -22.4032 | 20.8663 | 20.3232 | 19.5726 | 18.5916 | 17.4411 | 16.6958 | 16.3032 | 15.9516 | 15.6568 | 14.4695 | 13.4526 | 12.5705 | 22.1211 | 21.5768 | 20.8274 | 19.8453 | 18.6937 | 17.9484 | 17.5558 | 17.2042 | 16.9095 | 15.7211 | 14.7011 | 13.8168
|  | FARNHAM PRIMARY | CF |  |  |  |  | 25.1074 | 25.02 | 24.9295 | 24.8284 | 24.7063 | 24.5937 | 24.4884 | 24.3811 | 24.2726 | 23.7884 | 23.5316 | 23.3747 | 21.2621 | 20.9979 | 20.6674 | 20.2674 | 19.8337 | 19.5558 | 19.3495 | 19.1032 | 18.8516 | 17.6958 | 16.9284 | 16.2853 | 22.4547 | 22.2526 | 21.9221 | 21.5211 | 21.0884 | 20.8105 | 20.6032 | 20.3558 | 20.1042 | 18.9484 | 18.18 | 17.5368
IVER 132KV GSP | SLOUGH BSP | FARNHAM ROYAL PRIMARY | MINIMUM HEADROOM | SU 95597 82844 | NO | NO | 0 | 41.2926 | 40.6632 | 39.9937 | 39.3032 | 38.5863 | 37.8663 | 37.2547 | 36.4979 | 35.4032 | 30.1674 | 25.6526 | -20.8105 | 37.0326 | 35.5926 | 34.2853 | 33.0505 | 31.82 | 30.6074 | 29.34 | 28.0516 | 26.8232 | 21.0558 | 16.0421 | 11.4684 | 38.5653 | 37.1842 | 35.8768 | 34.6421 | 33.4116 | 32.1989 | 30.9379 | 29.6495 | 28.4211 | 22.6516 | 17.6368 | 13.0621
|  | FARNHAM ROYAL PRIMARY | EE |  |  |  |  | 41.6558 | 41.1347 | 40.58 | 40 | 39.3979 | 38.8158 | 38.2621 | 37.7295 | 37.2768 | 33.6032 | 30.1347 | 27.0611 | 37.8158 | 36.6411 | 35.5747 | 34.5663 | 33.5547 | 32.5937 | 31.4958 | 30.3916 | 29.4179 | 24.8168 | 20.9537 | 17.4979 | 39.1211 | 38.1916 | 37.1621 | 36.1579 | 35.1463 | 34.1842 | 33.0874 | 31.9821 | 31.0147 | 26.4137 | 22.5484 | 19.0905
|  | FARNHAM ROYAL PRIMARY | HT |  |  |  |  | 41.2926 | 40.6632 | 39.9937 | 39.3032 | 38.5863 | 37.8663 | 37.2547 | 36.4979 | 35.4032 | 30.1674 | 25.6526 | 21.5642 | 37.0326 | 35.5926 | 34.2853 | 33.0505 | 31.82 | 30.6074 | 29.34 | 28.0516 | 26.8232 | 21.0558 | 16.0421 | 11.4684 | 38.5653 | 37.1842 | 35.8768 | 34.6421 | 33.4116 | 32.1989 | 30.9379 | 29.6495 | 28.4211 | 22.6516 | 17.6368 | 13.0621
|  | FARNHAM ROYAL PRIMARY | HE |  |  |  |  | 42.1232 | 41.7432 | 41.3253 | 40.8737 | 40.3937 | 39.9337 | 39.4989 | 39.0937 | 38.7453 | 37.54 | 35.5253 | -20.8105 | 38.7305 | 37.9821 | 37.2789 | 36.5684 | 35.8326 | 35.1463 | 34.3179 | 33.4895 | 32.7263 | 29.4053 | 26.8084 | 24.5716 | 39.5884 | 39.2084 | 38.7905 | 38.1042 | 37.3884 | 36.7179 | 35.9095 | 35.0811 | 34.3179 | 30.9874 | 28.3895 | 26.1537
|  | FARNHAM ROYAL PRIMARY | CF |  |  |  |  | 42.4621 | 42.2589 | 42.0474 | 41.8295 | 41.6021 | 41.3716 | 41.1442 | 40.92 | 40.6947 | 39.6926 | 39.1916 | 38.5253 | 39.1716 | 38.9389 | 38.6674 | 38.2453 | 37.7947 | 37.3211 | 36.8726 | 36.3916 | 35.9116 | 33.4168 | 31.5579 | 30.0095 | 39.9274 | 39.7242 | 39.5126 | 39.2947 | 39.0674 | 38.8368 | 38.4074 | 37.9442 | 37.4832 | 35.0084 | 33.1484 | 31.5989
LALEHAM GSP | EAST BEDFONT BSP | FELTHAM PRIMARY | MINIMUM HEADROOM | TQ 10628 72811 | NO | YES | 0 | 29.0705 | 28.9221 | 28.7442 | 28.1937 | 27.16 | 26.1463 | 25.1368 | 23.9147 | 22.7 | 18.4274 | 16.7568 | 2.9179 | 25.4926 | 24.7758 | 23.8621 | 22.7621 | 21.5 | 20.3053 | 19.14 | 17.7211 | 16.3084 | 11.3684 | 9.4747 | 7.9432 | 26.4779 | 25.7347 | 24.8232 | 23.7589 | 22.5389 | 21.3832 | 20.2274 | 18.8116 | 17.4011 | 12.4695 | 10.5789 | 9.0484
|  | FELTHAM PRIMARY | EE |  |  |  |  | 29.1526 | 29.0284 | 28.8968 | 28.7568 | 28.5642 | 27.9263 | 27.1158 | 25.7663 | 24.3463 | 19.7516 | 18.4968 | 17.5358 | 25.7695 | 25.4484 | 24.9316 | 24.2411 | 23.3347 | 22.4589 | 21.4684 | 19.8663 | 18.2084 | 12.8642 | 11.4411 | 10.3505 | 26.5832 | 26.4347 | 25.9032 | 25.1874 | 24.3095 | 23.4621 | 22.5053 | 20.9526 | 19.2979 | 13.9621 | 12.5421 | 11.4526
|  | FELTHAM PRIMARY | HT |  |  |  |  | 29.0705 | 28.9221 | 28.7442 | 28.1937 | 27.16 | 26.1463 | 25.1368 | 23.9147 | 22.7 | 18.4274 | 16.7568 | 15.4042 | 25.4926 | 24.7758 | 23.8621 | 22.7621 | 21.5 | 20.3053 | 19.14 | 17.7211 | 16.3084 | 11.3684 | 9.4747 | 7.9432 | 26.4779 | 25.7347 | 24.8232 | 23.7589 | 22.5389 | 21.3832 | 20.2274 | 18.8116 | 17.4011 | 12.4695 | 10.5789 | 9.0484
|  | FELTHAM PRIMARY | HE |  |  |  |  | 29.2526 | 29.1579 | 29.0526 | 28.94 | 28.7895 | 28.3695 | 27.5674 | 26.2674 | 24.9442 | 20.7758 | 19.8126 | 2.9179 | 25.9411 | 25.6663 | 25.26 | 24.6358 | 23.7789 | 22.9558 | 21.9705 | 20.4063 | 18.8568 | 13.9874 | 12.8853 | 12.1168 | 26.6916 | 26.5747 | 26.2421 | 25.5832 | 24.7453 | 23.9495 | 22.9979 | 21.4884 | 19.9463 | 15.0842 | 13.9853 | 13.2168
|  | FELTHAM PRIMARY | CF |  |  |  |  | 29.3274 | 29.2726 | 29.2147 | 29.1568 | 29.0958 | 29.0337 | 28.9716 | 28.9116 | 28.8505 | 24.7568 | 23.7505 | 23.3053 | 26.0979 | 26.0179 | 25.9211 | 25.8189 | 25.7105 | 25.5968 | 25.4505 | 25.2179 | 24.8326 | 18.6032 | 17.4379 | 16.9263 | 26.7768 | 26.7179 | 26.6558 | 26.5926 | 26.5253 | 26.4579 | 26.3853 | 26.2074 | 25.7989 | 19.6926 | 18.5295 | 18.0179
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN PRIMARY | MINIMUM HEADROOM | SU 06593 00685 | NO | YES | 0 | 48.7595 | 48.2564 | 47.7227 | 47.1743 | 46.5964 | 45.8101 | 45.088 | 44.2532 | 43.3732 | 37.8374 | 33.0037 | -27.712 | 45.1606 | 44.1543 | 43.1069 | 41.9932 | 41.0501 | 39.869 | 38.7301 | 37.6353 | 36.6237 | 30.0532 | 24.5659 | 20.7101 | 46.5048 | 45.5206 | 44.4964 | 43.4069 | 42.4795 | 41.3259 | 40.2248 | 39.1743 | 38.189 | 31.6111 | 26.0427 | 22.1911
|  | FERNDOWN PRIMARY | EE |  |  |  |  | 49.0732 | 48.6669 | 48.2343 | 47.7827 | 47.3164 | 46.8659 | 46.289 | 45.6859 | 45.1416 | 40.3469 | 36.4416 | 33.9353 | 45.8111 | 45.0006 | 44.149 | 43.2195 | 42.4553 | 41.469 | 40.4869 | 39.5311 | 38.6427 | 32.8416 | 28.2848 | 25.4764 | 47.1406 | 46.349 | 45.5153 | 44.6069 | 43.8543 | 42.8911 | 41.9332 | 41.0016 | 40.1501 | 34.3995 | 29.8353 | 26.9469
|  | FERNDOWN PRIMARY | HT |  |  |  |  | 48.7595 | 48.2564 | 47.7227 | 47.1743 | 46.5964 | 45.8101 | 45.088 | 44.2532 | 43.3732 | 37.8374 | 33.0037 | 29.6406 | 45.1606 | 44.1543 | 43.1069 | 41.9932 | 41.0501 | 39.869 | 38.7301 | 37.6353 | 36.6237 | 30.0532 | 24.5659 | 20.7101 | 46.5048 | 45.5206 | 44.4964 | 43.4069 | 42.4795 | 41.3259 | 40.2248 | 39.1743 | 38.189 | 31.6111 | 26.0427 | 22.1911
|  | FERNDOWN PRIMARY | HE |  |  |  |  | 49.4659 | 49.1806 | 48.8659 | 48.5269 | 48.1637 | 47.8174 | 47.4901 | 47.1848 | 46.8932 | 43.6237 | 40.6711 | -27.712 | 46.6553 | 46.1059 | 45.5048 | 44.8122 | 44.268 | 43.4964 | 42.7248 | 41.9827 | 41.3164 | 36.5606 | 33.0322 | 31.0237 | 47.7437 | 47.428 | 46.8385 | 46.1616 | 45.6237 | 44.8711 | 44.1195 | 43.3964 | 42.748 | 38.1237 | 34.5069 | 32.5006
|  | FERNDOWN PRIMARY | CF |  |  |  |  | 49.7353 | 49.5869 | 49.4332 | 49.2743 | 49.109 | 48.9406 | 48.7753 | 48.6122 | 48.449 | 47.208 | 45.3027 | 44.2395 | 47.0459 | 46.8164 | 46.4848 | 46.1206 | 45.8164 | 45.4006 | 44.9616 | 44.5111 | 44.0648 | 40.7385 | 38.3385 | 37.0353 | 48.0259 | 47.868 | 47.7037 | 47.4459 | 47.148 | 46.7416 | 46.3143 | 45.8764 | 45.4427 | 42.2448 | 39.9037 | 38.5974
FLEET-BRAMLEY GSP | FERNHURST BSP | FIVE OAKS PRIMARY | MINIMUM HEADROOM | TQ 10647 29057 | NO | YES | 0 | 15.6537 | 15.2874 | 14.8158 | 14.2684 | 12.2337 | 11.4347 | 10.46 | 10.3053 | 10.16 | 6.3074 | 3.8895 | 0.59263 | 14.3168 | 13.9116 | 13.3821 | 12.7642 | 10.4011 | 9.4958 | 8.38 | 8.2316 | 8.0926 | 3.7042 | 1.1053 | 0.39895 | 14.2926 | 13.9232 | 13.4211 | 12.8032 | 10.4347 | 9.5232 | 8.4011 | 8.2463 | 8.1011 | 3.6663 | 0.90842 | 0.18
|  | FIVE OAKS PRIMARY | EE |  |  |  |  | 15.8389 | 15.5484 | 16.2663 | 16.1368 | 15.9021 | 15.3168 | 14.8958 | 14.4842 | 14.0874 | 12.2726 | 8.9526 | 7.4853 | 14.5189 | 14.1979 | 15.7116 | 15.5832 | 15.3253 | 14.6705 | 14.2105 | 13.7611 | 13.3295 | 11.3705 | 7.6358 | 5.9811 | 14.4789 | 14.1863 | 16.12 | 15.9905 | 15.7274 | 15.0674 | 14.5989 | 14.14 | 13.6989 | 11.6758 | 7.8695 | 6.1926
|  | FIVE OAKS PRIMARY | HT |  |  |  |  | 15.6537 | 15.2874 | 14.8158 | 14.2684 | 12.2337 | 11.4347 | 10.46 | 10.3053 | 10.16 | 6.3074 | 3.8895 | 3.22 | 14.3168 | 13.9116 | 13.3821 | 12.7642 | 10.4011 | 9.4958 | 8.38 | 8.2316 | 8.0926 | 3.7042 | 1.1053 | 0.39895 | 14.2926 | 13.9232 | 13.4211 | 12.8032 | 10.4347 | 9.5232 | 8.4011 | 8.2463 | 8.1011 | 3.6663 | 0.90842 | 0.18
|  | FIVE OAKS PRIMARY | HE |  |  |  |  | 16.0663 | 15.8484 | 15.5432 | 15.1053 | 14.5168 | 14.0053 | 13.6568 | 13.3221 | 13.0053 | 11.6095 | 10.4579 | 0.59263 | 14.7663 | 14.5242 | 14.1789 | 13.68 | 13.0095 | 12.4295 | 12.0411 | 11.6674 | 11.3126 | 9.7537 | 8.5653 | 7.3874 | 14.7063 | 14.4884 | 14.18 | 13.72 | 13.0453 | 12.4611 | 12.0684 | 11.6916 | 11.3326 | 9.7474 | 8.4242 | 7.2263
|  | FIVE OAKS PRIMARY | CF |  |  |  |  | 16.2221 | 16.1168 | 15.9958 | 15.8168 | 15.5758 | 15.3453 | 15.1674 | 14.9811 | 14.7863 | 13.8674 | 15.0274 | 14.38 | 14.9358 | 14.8189 | 14.6832 | 14.48 | 14.2074 | 13.9463 | 13.7474 | 13.5389 | 13.32 | 12.2832 | 14.3316 | 13.5989 | 14.8632 | 14.7579 | 14.6358 | 14.4547 | 14.2126 | 13.9789 | 13.7821 | 13.5716 | 13.3516 | 12.3053 | 14.7116 | 13.9653
AMERSHAM GSP | LOUDWATER BSP | FLACKWELL HEATH PRIMARY | MINIMUM HEADROOM | SU 90667 89318 | NO | YES | 0 | 30.6284 | 30.3505 | 30.0568 | 29.7537 | 29.4411 | 29.1263 | 28.84 | 28.5295 | 28.2379 | 26.5411 | 24.8053 | 8.3274 | 28.9295 | 28.4063 | 27.8821 | 27.36 | 26.8432 | 26.32 | 25.8295 | 25.3432 | 24.8758 | 22.7316 | 20.8189 | 19.1116 | 29.6021 | 29.0916 | 28.5758 | 28.0611 | 27.5505 | 27.0358 | 26.5516 | 26.0716 | 25.6042 | 23.4547 | 21.5389 | 19.8295
|  | FLACKWELL HEATH PRIMARY | EE |  |  |  |  | 30.8 | 30.5758 | 31.8621 | 31.4674 | 31.0726 | 30.6926 | 30.3179 | 29.9347 | 29.5695 | 28.0179 | 26.6979 | 25.5442 | 29.2926 | 28.88 | 28.4653 | 28.0453 | 27.6274 | 27.2242 | 26.8274 | 26.4158 | 26.0242 | 24.3358 | 22.8811 | 21.5916 | 29.7737 | 29.5495 | 29.1958 | 28.7758 | 28.3579 | 27.9547 | 27.5568 | 27.1453 | 26.7516 | 25.0579 | 23.5968 | 22.3053
|  | FLACKWELL HEATH PRIMARY | HT |  |  |  |  | 30.6284 | 30.3505 | 30.0568 | 29.7537 | 29.4411 | 29.1263 | 28.84 | 28.5295 | 28.2379 | 26.5411 | 24.8053 | 23.2684 | 28.9295 | 28.4063 | 27.8821 | 27.36 | 26.8432 | 26.32 | 25.8295 | 25.3432 | 24.8758 | 22.7316 | 20.8189 | 19.1116 | 29.6021 | 29.0916 | 28.5758 | 28.0611 | 27.5505 | 27.0358 | 26.5516 | 26.0716 | 25.6042 | 23.4547 | 21.5389 | 19.8295
|  | FLACKWELL HEATH PRIMARY | HE |  |  |  |  | 31.0158 | 30.8579 | 30.6842 | 30.4958 | 30.2958 | 30.1032 | 29.9221 | 29.7526 | 29.6063 | 29.1116 | 28.7284 | 8.3274 | 29.7653 | 29.4989 | 29.2242 | 28.9368 | 28.6432 | 28.36 | 28.0832 | 27.7916 | 27.5158 | 26.3937 | 25.4684 | 24.6663 | 29.9895 | 29.8316 | 29.6579 | 29.4695 | 29.2695 | 29.0379 | 28.7632 | 28.4758 | 28.2042 | 27.1032 | 26.1926 | 25.3895
|  | FLACKWELL HEATH PRIMARY | CF |  |  |  |  | 31.1632 | 31.0811 | 30.9958 | 30.9074 | 30.8147 | 30.7211 | 30.6295 | 30.5379 | 30.4463 | 30.0379 | 29.8347 | 29.6632 | 30.0158 | 29.8642 | 29.7042 | 29.5411 | 29.3737 | 29.2074 | 29.0379 | 28.8547 | 28.6653 | 27.7642 | 27.0768 | 26.5116 | 30.1368 | 30.0547 | 29.9695 | 29.8811 | 29.7884 | 29.6947 | 29.6032 | 29.5116 | 29.3442 | 28.46 | 27.7884 | 27.2389
NURSLING GSP | ROWNHAMS BSP | FLETCHWOOD PRIMARY | MINIMUM HEADROOM | SU 33800 12142 | NO | YES | 5.7368 | 29.2847 | 28.8553 | 28.3995 | 27.9311 | 27.4489 | 26.49 | 25.3268 | 24.0689 | 22.9005 | 18.8311 | 15.5163 | -10.13 | 24.2679 | 23.2774 | 22.1479 | 21.1468 | 20.0047 | 18.6384 | 17.33 | 15.8932 | 14.5574 | 10.2658 | 6.6026 | 3.29 | 25.3721 | 24.4068 | 23.2879 | 22.27 | 21.1068 | 19.7132 | 18.3974 | 16.9605 | 15.6247 | 11.0511 | 7.3416 | 3.9858
|  | FLETCHWOOD PRIMARY | EE |  |  |  |  | 29.5437 | 29.1932 | 30.6911 | 29.9016 | 28.9837 | 27.8868 | 26.8174 | 25.6226 | 24.5226 | 21.1111 | 18.5405 | 16.2774 | 24.83 | 24.0153 | 23.1384 | 22.2784 | 21.2711 | 20.05 | 18.8584 | 17.5153 | 16.2784 | 12.4679 | 9.8732 | 7.3447 | 25.77 | 25.1268 | 24.2068 | 23.3468 | 22.3395 | 21.1184 | 19.9258 | 18.5826 | 17.3458 | 13.5342 | 10.6447 | 8.0805
|  | FLETCHWOOD PRIMARY | HT |  |  |  |  | 29.2847 | 28.8553 | 28.3995 | 27.9311 | 27.4489 | 26.49 | 25.3268 | 24.0689 | 22.9005 | 18.8311 | 15.5163 | 12.5363 | 24.2679 | 23.2774 | 22.1479 | 21.1468 | 20.0047 | 18.6384 | 17.33 | 15.8932 | 14.5574 | 10.2658 | 6.6026 | 3.29 | 25.3721 | 24.4068 | 23.2879 | 22.27 | 21.1068 | 19.7132 | 18.3974 | 16.9605 | 15.6247 | 11.0511 | 7.3416 | 3.9858
|  | FLETCHWOOD PRIMARY | HE |  |  |  |  | 29.8858 | 29.6426 | 29.3732 | 29.0837 | 28.7742 | 28.4784 | 28.1995 | 27.5079 | 26.5942 | 24.0532 | 22.1974 | -10.13 | 25.3826 | 24.9753 | 24.2289 | 23.5911 | 22.7921 | 21.7826 | 20.7953 | 19.6647 | 18.6163 | 15.6679 | 13.8205 | 12.0311 | 26.1363 | 25.8721 | 25.3395 | 24.7163 | 23.9395 | 22.9079 | 21.8984 | 20.7405 | 19.6837 | 16.7342 | 14.63 | 12.8132
|  | FLETCHWOOD PRIMARY | CF |  |  |  |  | 30.1216 | 29.9963 | 29.8658 | 29.7321 | 29.5932 | 29.4511 | 29.3121 | 29.1742 | 29.0353 | 28.0847 | 26.9332 | 25.8974 | 25.63 | 25.4932 | 25.2784 | 24.9511 | 24.5616 | 24.0542 | 23.5237 | 22.8826 | 22.2363 | 20.2574 | 18.9426 | 17.73 | 26.3826 | 26.2458 | 26.1005 | 25.9553 | 25.6668 | 25.1753 | 24.6626 | 24.0216 | 23.3595 | 21.3363 | 20.01 | 18.7974
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE PRIMARY | MINIMUM HEADROOM | SU 14069 15523 | NO | YES | 0 | 16.9611 | 16.4968 | 15.9747 | 15.2811 | 14.3547 | 13.4663 | 12.8263 | 12.2032 | 11.5947 | 9.6032 | 8.5411 | -0.25263 | 14.5821 | 14.0305 | 13.4074 | 12.5642 | 11.4905 | 10.4789 | 9.7537 | 9.0453 | 8.3526 | 6.1032 | 4.9221 | 3.7926 | 15.0463 | 14.5232 | 13.9337 | 13.1126 | 12.0389 | 11.0274 | 10.3011 | 9.5937 | 8.9 | 6.6505 | 5.4695 | 4.3389
|  | FORDINGBRIDGE PRIMARY | EE |  |  |  |  | 17.1432 | 16.7347 | 16.2674 | 15.6242 | 14.7632 | 13.9358 | 13.3379 | 12.7484 | 12.1747 | 10.4274 | 9.6232 | 8.8642 | 14.7895 | 14.3011 | 13.7379 | 12.9526 | 11.9337 | 10.9863 | 10.3063 | 9.6347 | 8.9811 | 6.9989 | 6.1021 | 5.2432 | 15.2453 | 14.7832 | 14.2526 | 13.5011 | 12.4821 | 11.5347 | 10.8547 | 10.1832 | 9.5284 | 7.5463 | 6.6484 | 5.7905
|  | FORDINGBRIDGE PRIMARY | HT |  |  |  |  | 16.9611 | 16.4968 | 15.9747 | 15.2811 | 14.3547 | 13.4663 | 12.8263 | 12.2032 | 11.5947 | 9.6032 | 8.5411 | 7.5358 | 14.5821 | 14.0305 | 13.4074 | 12.5642 | 11.4905 | 10.4789 | 9.7537 | 9.0453 | 8.3526 | 6.1032 | 4.9221 | 3.7926 | 15.0463 | 14.5232 | 13.9337 | 13.1126 | 12.0389 | 11.0274 | 10.3011 | 9.5937 | 8.9 | 6.6505 | 5.4695 | 4.3389
|  | FORDINGBRIDGE PRIMARY | HE |  |  |  |  | 17.3747 | 17.0379 | 16.64 | 16.0621 | 15.2811 | 14.5168 | 13.9779 | 13.4495 | 12.9337 | 11.4663 | 10.92 | -0.25263 | 15.0526 | 14.6442 | 14.1611 | 13.4484 | 12.4968 | 11.6179 | 11.0021 | 10.3968 | 9.8053 | 8.1295 | 7.5147 | 6.9221 | 15.4979 | 15.1137 | 14.6579 | 13.9905 | 13.0453 | 12.1653 | 11.5505 | 10.9453 | 10.3526 | 8.6768 | 8.0621 | 7.4695
|  | FORDINGBRIDGE PRIMARY | CF |  |  |  |  | 17.46 | 17.4147 | 17.2295 | 16.9716 | 16.6442 | 16.3116 | 16.0516 | 15.7758 | 15.4779 | 14.4916 | 14.1358 | 13.7811 | 15.3063 | 15.0989 | 14.8684 | 14.5516 | 14.1453 | 13.7326 | 13.4137 | 13.0737 | 12.7116 | 11.5926 | 11.1937 | 10.7874 | 15.7021 | 15.5442 | 15.3263 | 15.0295 | 14.6495 | 14.2632 | 13.9621 | 13.6221 | 13.26 | 12.14 | 11.7411 | 11.3358
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK PRIMARY | MINIMUM HEADROOM | SU 66139 00180 | NO | YES | 0 | 26.7937 | 26.3726 | 25.9263 | 25.4558 | 24.9653 | 24.4695 | 24.0253 | 23.6168 | 23.2389 | 19.6611 | 15.48 | -22.5568 | 20.1811 | 19.3084 | 18.3747 | 17.3263 | 16.3179 | 15.4611 | 14.6642 | 13.9105 | 12.9937 | 8.3632 | 3.6747 | -0.67263 | 21.58 | 20.9621 | 20.0495 | 19.0274 | 18.0347 | 17.1768 | 16.3789 | 15.6253 | 14.7095 | 10.0747 | 5.3832 | 1.0337
|  | FRATTON PARK PRIMARY | EE |  |  |  |  | 27.0147 | 26.6589 | 26.2811 | 25.8768 | 25.4547 | 25.0432 | 24.6453 | 24.2579 | 23.9095 | 22.3853 | 19.08 | 16.1011 | 20.7032 | 19.9937 | 19.2137 | 18.3316 | 17.4663 | 16.7758 | 16.1042 | 15.4421 | 14.8263 | 11.3968 | 7.6842 | 4.3116 | 21.8189 | 21.4421 | 20.8674 | 20.0063 | 19.16 | 18.4811 | 17.8211 | 17.1568 | 16.54 | 13.1084 | 9.3916 | 6.0168
|  | FRATTON PARK PRIMARY | HT |  |  |  |  | 26.7937 | 26.3726 | 25.9263 | 25.4558 | 24.9653 | 24.4695 | 24.0253 | 23.6168 | 23.2389 | 19.6611 | 15.48 | 11.6253 | 20.1811 | 19.3084 | 18.3747 | 17.3263 | 16.3179 | 15.4611 | 14.6642 | 13.9105 | 12.9937 | 8.3632 | 3.6747 | -0.67263 | 21.58 | 20.9621 | 20.0495 | 19.0274 | 18.0347 | 17.1768 | 16.3789 | 15.6253 | 14.7095 | 10.0747 | 5.3832 | 1.0337
|  | FRATTON PARK PRIMARY | HE |  |  |  |  | 27.2737 | 26.9895 | 26.6758 | 26.3379 | 25.9768 | 25.6326 | 25.3084 | 25.0042 | 24.7421 | 23.8326 | 23.2716 | -22.5568 | 21.2537 | 20.8379 | 20.2432 | 19.5432 | 18.8579 | 18.3526 | 17.8684 | 17.4147 | 17.0095 | 15.3547 | 13.0074 | 10.6316 | 22.1011 | 21.8032 | 21.4726 | 21.1126 | 20.5137 | 20.0147 | 19.5368 | 19.0905 | 18.6926 | 17.0684 | 14.7221 | 12.3421
|  | FRATTON PARK PRIMARY | CF |  |  |  |  | 27.4621 | 27.2863 | 27.1042 | 26.9158 | 26.7211 | 26.5211 | 26.3263 | 26.1326 | 25.9389 | 25.0758 | 24.6379 | 24.3916 | 21.46 | 21.2726 | 21.08 | 20.7116 | 20.32 | 19.9811 | 19.6474 | 19.3126 | 18.9779 | 17.4316 | 15.9505 | 14.3432 | 22.3084 | 22.1211 | 21.9274 | 21.7263 | 21.52 | 21.3116 | 21.1084 | 20.9063 | 20.6263 | 19.1095 | 17.6653 | 16.0568
COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD PRIMARY | MINIMUM HEADROOM | SP 50426 08256 | NO | YES | 0 | 18.0168 | 17.8737 | 17.7221 | 17.5632 | 17.4 | 16.9 | 16.6495 | 16.4137 | 16.2 | 15.2295 | 14.4168 | 0.89895 | 15.2379 | 14.9684 | 14.6895 | 14.4095 | 14.1316 | 13.0147 | 12.7189 | 12.4621 | 12.2305 | 11.1642 | 10.2632 | 9.4295 | 16.0116 | 15.7463 | 15.4726 | 15.1979 | 14.9242 | 13.8442 | 13.5537 | 13.3011 | 13.0737 | 12.0284 | 11.1474 | 10.3337
|  | FRENCHAY ROAD PRIMARY | EE |  |  |  |  | 18.0989 | 17.98 | 17.8537 | 17.72 | 17.5821 | 17.3558 | 17.0874 | 16.8821 | 16.7305 | 15.9716 | 15.3716 | 14.8337 | 15.5116 | 15.2305 | 14.9737 | 14.7253 | 14.4916 | 13.7505 | 13.3211 | 13.0211 | 12.8232 | 11.9863 | 11.3211 | 10.7158 | 16.1495 | 16.0032 | 15.7516 | 15.5074 | 15.2768 | 14.56 | 14.1421 | 13.8484 | 13.6537 | 12.8337 | 12.1821 | 11.5926
|  | FRENCHAY ROAD PRIMARY | HT |  |  |  |  | 18.0168 | 17.8737 | 17.7221 | 17.5632 | 17.4 | 16.9 | 16.6495 | 16.4137 | 16.2 | 15.2295 | 14.4168 | 13.6726 | 15.2379 | 14.9684 | 14.6895 | 14.4095 | 14.1316 | 13.0147 | 12.7189 | 12.4621 | 12.2305 | 11.1642 | 10.2632 | 9.4295 | 16.0116 | 15.7463 | 15.4726 | 15.1979 | 14.9242 | 13.8442 | 13.5537 | 13.3011 | 13.0737 | 12.0284 | 11.1474 | 10.3337
|  | FRENCHAY ROAD PRIMARY | HE |  |  |  |  | 18.1979 | 18.1084 | 18.0095 | 17.9032 | 17.7905 | 17.6821 | 17.5074 | 17.3547 | 17.2495 | 16.8568 | 16.5989 | 0.89895 | 15.7453 | 15.5326 | 15.3474 | 15.1653 | 14.9989 | 14.3074 | 13.9274 | 13.7084 | 13.5747 | 13.0526 | 12.6916 | 12.3842 | 16.2568 | 16.16 | 16.0558 | 15.9379 | 15.7737 | 15.1042 | 14.7347 | 14.52 | 14.3884 | 13.8758 | 13.5221 | 13.2221
|  | FRENCHAY ROAD PRIMARY | CF |  |  |  |  | 18.2653 | 18.2126 | 18.1579 | 18.1011 | 18.0432 | 17.9832 | 17.9253 | 17.8663 | 17.8084 | 17.5053 | 17.2863 | 17.1337 | 15.8653 | 15.8011 | 15.7032 | 15.6 | 15.4989 | 15.3905 | 15.2547 | 15.06 | 14.8547 | 13.9558 | 13.6316 | 13.3874 | 16.3305 | 16.2747 | 16.2168 | 16.1568 | 16.0968 | 16.0337 | 15.9705 | 15.8347 | 15.6347 | 14.7611 | 14.4442 | 14.2063
FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER PRIMARY | MINIMUM HEADROOM | SZ 34325 86965 | NO | YES | 0 | 16.8726 | 16.5126 | 16.1484 | 15.7684 | 15.3579 | 14.9305 | 14.5211 | 14.1295 | 13.7421 | 11.8853 | 10.2063 | 1.2158 | 14.4611 | 14.0726 | 13.6811 | 13.2726 | 12.8295 | 12.3663 | 11.92 | 11.4905 | 11.0642 | 8.9937 | 7.1011 | 5.4011 | 14.6758 | 14.2884 | 13.8968 | 13.4895 | 13.0463 | 12.5832 | 12.1368 | 11.7084 | 11.2821 | 9.2137 | 7.3242 | 5.6274
|  | FRESHWATER PRIMARY | EE |  |  |  |  | 17.1179 | 16.8326 | 16.5274 | 16.2105 | 15.8916 | 15.5632 | 15.2368 | 14.9421 | 14.6495 | 13.2495 | 11.9389 | 10.78 | 14.7295 | 14.4221 | 14.0937 | 13.7537 | 13.4116 | 13.0568 | 12.7032 | 12.3853 | 12.0663 | 10.5105 | 9.0274 | 7.7053 | 14.9442 | 14.6368 | 14.3095 | 13.9695 | 13.6274 | 13.2726 | 12.92 | 12.6021 | 12.2842 | 10.7295 | 9.2484 | 7.9284
|  | FRESHWATER PRIMARY | HT |  |  |  |  | 16.8726 | 16.5126 | 16.1484 | 15.7684 | 15.3579 | 14.9305 | 14.5211 | 14.1295 | 13.7421 | 11.8853 | 10.2063 | 8.7063 | 14.4611 | 14.0726 | 13.6811 | 13.2726 | 12.8295 | 12.3663 | 11.92 | 11.4905 | 11.0642 | 8.9937 | 7.1011 | 5.4011 | 14.6758 | 14.2884 | 13.8968 | 13.4895 | 13.0463 | 12.5832 | 12.1368 | 11.7084 | 11.2821 | 9.2137 | 7.3242 | 5.6274
|  | FRESHWATER PRIMARY | HE |  |  |  |  | 17.44 | 17.2537 | 17.0474 | 16.8263 | 16.5842 | 16.3442 | 16.1032 | 15.8895 | 15.6716 | 14.5663 | 13.6853 | 1.2158 | 15.0811 | 14.8821 | 14.6621 | 14.4263 | 14.1684 | 13.9105 | 13.6505 | 13.4211 | 13.1832 | 11.9421 | 10.9389 | 9.9874 | 15.2947 | 15.0968 | 14.8768 | 14.6411 | 14.3832 | 14.1253 | 13.8663 | 13.6368 | 13.3989 | 12.16 | 11.1579 | 10.2084
|  | FRESHWATER PRIMARY | CF |  |  |  |  | 17.6621 | 17.5516 | 17.4242 | 17.2853 | 17.1316 | 16.9737 | 16.8211 | 16.6779 | 16.5347 | 15.9884 | 15.3632 | 14.8316 | 15.3242 | 15.2042 | 15.0642 | 14.9126 | 14.7432 | 14.5695 | 14.4021 | 14.2442 | 14.0884 | 13.4979 | 12.7853 | 12.1716 | 15.5379 | 15.4189 | 15.2789 | 15.1263 | 14.9579 | 14.7842 | 14.6168 | 14.46 | 14.3042 | 13.7137 | 13.0021 | 12.3895
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FRIMLEY PRIMARY | MINIMUM HEADROOM | SU 87745 57942 | NO | YES | 0 | 35.8705 | 35.4474 | 34.9989 | 33.7053 | 32.4221 | 31.6126 | 30.8674 | 30.1747 | 29.52 | 26.4789 | 23.2221 | -11.5011 | 28.9126 | 27.2958 | 25.9147 | 24.42 | 23 | 22.1368 | 21.3389 | 20.5979 | 19.8947 | 16.6074 | 12.8495 | 10.1168 | 30.4905 | 28.8568 | 27.4747 | 25.9789 | 24.5568 | 23.6905 | 22.8905 | 22.1453 | 21.44 | 18.1295 | 14.2611 | 11.5168
|  | FRIMLEY PRIMARY | EE |  |  |  |  | 36.1284 | 35.7842 | 35.4168 | 34.6547 | 33.4979 | 32.8358 | 32.6095 | 31.9947 | 31.4284 | 28.9558 | 26.7242 | 24.8737 | 29.4874 | 28.0537 | 26.8074 | 25.4463 | 24.1632 | 23.4558 | 23.4189 | 22.7642 | 22.1611 | 19.5032 | 17.0737 | 15.0147 | 31.0726 | 29.6147 | 28.3674 | 27.0074 | 25.72 | 25.0084 | 25.0516 | 24.3926 | 23.7853 | 21.0958 | 18.6284 | 16.5568
|  | FRIMLEY PRIMARY | HT |  |  |  |  | 35.8705 | 35.4474 | 34.9989 | 33.7053 | 32.4221 | 31.6126 | 30.8674 | 30.1747 | 29.52 | 26.4789 | 23.2221 | 20.7589 | 28.9126 | 27.2958 | 25.9147 | 24.42 | 23 | 22.1368 | 21.3389 | 20.5979 | 19.8947 | 16.6074 | 12.8495 | 10.1168 | 30.4905 | 28.8568 | 27.4747 | 25.9789 | 24.5568 | 23.6905 | 22.8905 | 22.1453 | 21.44 | 18.1295 | 14.2611 | 11.5168
|  | FRIMLEY PRIMARY | HE |  |  |  |  | 36.4611 | 36.2211 | 35.9558 | 35.6695 | 34.9411 | 34.4558 | 33.9905 | 33.5537 | 33.1611 | 31.1316 | 29.7211 | -11.5011 | 30.2021 | 28.9947 | 27.9737 | 26.8221 | 25.7295 | 25.2126 | 24.7179 | 24.2526 | 23.8347 | 21.4421 | 19.8789 | 18.5621 | 31.7705 | 30.5642 | 29.5347 | 28.3832 | 27.2874 | 26.7695 | 26.2726 | 25.8063 | 25.3853 | 22.8968 | 21.3232 | 19.9979
|  | FRIMLEY PRIMARY | CF |  |  |  |  | 36.6863 | 36.5611 | 36.4316 | 36.2968 | 36.1537 | 36.0084 | 35.8653 | 35.7242 | 35.5832 | 34.9505 | 34.3084 | 33.4895 | 31.0411 | 30.4558 | 29.9737 | 29.4505 | 28.9558 | 28.6421 | 28.3432 | 28.0537 | 27.7547 | 26.2463 | 25.1263 | 24.2042 | 32.4884 | 32.0179 | 31.5516 | 31.0326 | 30.5263 | 30.2053 | 29.9021 | 29.6105 | 29.3116 | 27.7989 | 26.6726 | 25.7442
MELKSHAM GSP | FROME BSP | FROME PRIMARY | MINIMUM HEADROOM | ST 78850 48051 | NO | YES | 0 | 53.8132 | 53.2606 | 51.9037 | 50.6406 | 49.0564 | 47.7206 | 45.8659 | 44.168 | 42.7522 | 35.9564 | 28.7511 | -10.6457 | 44.0237 | 42.028 | 40.1385 | 38.4174 | 36.6311 | 35.2016 | 33.1532 | 31.2637 | 29.7006 | 22.5374 | 14.1353 | 9.3953 | 44.1659 | 42.9069 | 41.6669 | 39.9237 | 38.1048 | 36.6469 | 34.569 | 32.668 | 31.0922 | 23.9111 | 15.3332 | 10.5522
|  | FROME PRIMARY | EE |  |  |  |  | 54.1059 | 53.6659 | 53.2364 | 51.8395 | 50.3585 | 49.1922 | 47.4553 | 45.8416 | 44.5227 | 37.8111 | 32.848 | 29.5037 | 44.6827 | 42.8827 | 41.2816 | 39.7269 | 38.0932 | 36.8332 | 34.9006 | 33.1143 | 31.6669 | 24.2595 | 19.2153 | 15.4974 | 44.6374 | 43.5185 | 42.7185 | 41.1627 | 39.5185 | 38.2437 | 36.2953 | 34.4901 | 33.0227 | 25.4816 | 20.3511 | 16.5795
|  | FROME PRIMARY | HT |  |  |  |  | 53.8132 | 53.2606 | 51.9037 | 50.6406 | 49.0564 | 47.7206 | 45.8659 | 44.168 | 42.7522 | 35.9564 | 28.7511 | 24.4953 | 44.0237 | 42.028 | 40.1385 | 38.4174 | 36.6311 | 35.2016 | 33.1532 | 31.2637 | 29.7006 | 22.5374 | 14.1353 | 9.3953 | 44.1659 | 42.9069 | 41.6669 | 39.9237 | 38.1048 | 36.6469 | 34.569 | 32.668 | 31.0922 | 23.9111 | 15.3332 | 10.5522
|  | FROME PRIMARY | HE |  |  |  |  | 54.509 | 54.1943 | 53.8437 | 52.9237 | 51.9248 | 51.1585 | 49.7437 | 48.3848 | 47.3206 | 41.9459 | 37.2901 | -10.6457 | 45.5764 | 44.0511 | 42.6227 | 41.3385 | 39.969 | 38.9732 | 37.3206 | 35.8185 | 34.6416 | 28.5837 | 23.1016 | 20.4227 | 45.2901 | 44.3732 | 43.488 | 42.6606 | 41.4806 | 40.468 | 38.7837 | 37.2522 | 36.0585 | 29.9532 | 24.4006 | 21.6859
|  | FROME PRIMARY | CF |  |  |  |  | 54.7859 | 54.6153 | 54.4374 | 54.2543 | 54.0501 | 53.8448 | 53.3774 | 52.7701 | 52.2374 | 48.9269 | 46.1153 | 44.5448 | 46.5048 | 45.7627 | 45.1037 | 44.3743 | 43.5701 | 42.9206 | 42.0006 | 41.1259 | 40.3743 | 36.3806 | 33.1964 | 31.4343 | 45.8911 | 45.4364 | 45.0195 | 44.5648 | 44.0595 | 43.6332 | 43.0711 | 42.5343 | 41.8795 | 37.8101 | 34.5964 | 32.8111
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE PRIMARY | MINIMUM HEADROOM | SU 84935 93873 | NO | YES | 0 | 23.4105 | 23.0537 | 22.6747 | 22.2832 | 21.8779 | 21.4695 | 21.1105 | 20.7832 | 20.4821 | 18.0274 | 15.5779 | -9.7874 | 19.7021 | 19.0274 | 18.3463 | 17.6695 | 17 | 16.3179 | 15.6695 | 15.0095 | 14.3726 | 11.4042 | 8.7116 | 6.2126 | 20.5063 | 19.8863 | 19.2221 | 18.5463 | 17.8726 | 17.1853 | 16.5316 | 15.8653 | 15.2221 | 12.2232 | 9.4979 | 7.0021
|  | FRYERS LANE PRIMARY | EE |  |  |  |  | 23.6179 | 23.3242 | 23.0105 | 22.6832 | 22.3421 | 22.0147 | 21.7021 | 21.4011 | 21.1316 | 19.9253 | 18.0516 | 16.3863 | 20.1474 | 19.6179 | 19.0716 | 18.5242 | 17.9758 | 17.4432 | 16.9126 | 16.3505 | 15.8137 | 13.4632 | 11.3979 | 9.5463 | 20.7295 | 20.42 | 19.9253 | 19.3905 | 18.8547 | 18.3211 | 17.7853 | 17.2189 | 16.6779 | 14.3011 | 12.2116 | 10.3347
|  | FRYERS LANE PRIMARY | HT |  |  |  |  | 23.4105 | 23.0537 | 22.6747 | 22.2832 | 21.8779 | 21.4695 | 21.1105 | 20.7832 | 20.4821 | 18.0274 | 15.5779 | 13.3495 | 19.7021 | 19.0274 | 18.3463 | 17.6695 | 17 | 16.3179 | 15.6695 | 15.0095 | 14.3726 | 11.4042 | 8.7116 | 6.2126 | 20.5063 | 19.8863 | 19.2221 | 18.5463 | 17.8726 | 17.1853 | 16.5316 | 15.8653 | 15.2221 | 12.2232 | 9.4979 | 7.0021
|  | FRYERS LANE PRIMARY | HE |  |  |  |  | 23.8832 | 23.6695 | 23.4326 | 23.1789 | 22.9074 | 22.6474 | 22.4032 | 22.1747 | 21.9779 | 21.3116 | 20.9168 | -9.7874 | 20.5042 | 20.2726 | 20.0053 | 19.6453 | 19.2537 | 18.8726 | 18.4947 | 18.0863 | 17.7042 | 16.1011 | 14.7453 | 13.5716 | 21.0158 | 20.7937 | 20.5474 | 20.2853 | 20.0063 | 19.7168 | 19.3474 | 18.9484 | 18.5768 | 16.9663 | 15.5937 | 14.4032
|  | FRYERS LANE PRIMARY | CF |  |  |  |  | 24.0705 | 23.9547 | 23.8337 | 23.7095 | 23.58 | 23.4484 | 23.3189 | 23.1895 | 23.0621 | 22.4905 | 22.2053 | 22.0463 | 20.7095 | 20.5811 | 20.4463 | 20.3095 | 20.1663 | 19.9611 | 19.7316 | 19.4705 | 19.2053 | 17.9189 | 16.9211 | 16.0821 | 21.2126 | 21.0905 | 20.9621 | 20.8316 | 20.6958 | 20.5579 | 20.4221 | 20.2842 | 20.0537 | 18.7968 | 17.7853 | 16.9347
COWLEY GSP | DRAYTON BSP | FULSCOT PRIMARY | MINIMUM HEADROOM | SU 54413 89511 | NO | YES | 0.21053 | 34.0516 | 33.6863 | 32.5874 | 31.3663 | 30.5305 | 29.6842 | 28.7484 | 27.7116 | 26.7095 | 22.5516 | 20.2179 | -11.7842 | 29.4558 | 27.7632 | 26.5284 | 25.1505 | 24.2295 | 23.2947 | 22.2474 | 21.0768 | 19.9432 | 15.2337 | 12.6242 | 10.2832 | 30.0558 | 28.3632 | 27.1284 | 25.7526 | 24.8326 | 23.8989 | 22.8537 | 21.6842 | 20.5526 | 15.8495 | 13.2442 | 10.9063
|  | FULSCOT PRIMARY | EE |  |  |  |  | 34.2326 | 33.9421 | 33.1705 | 32.0526 | 31.3168 | 30.5811 | 29.7263 | 28.7537 | 27.8189 | 24.0821 | 22.2663 | 20.7905 | 29.8526 | 28.2789 | 27.1621 | 25.8968 | 25.0821 | 24.2663 | 23.3074 | 22.2074 | 21.1484 | 16.8968 | 14.8568 | 13.1937 | 30.4537 | 28.8789 | 27.7621 | 26.4989 | 25.6842 | 24.8695 | 23.9126 | 22.8137 | 21.7558 | 17.5116 | 15.4747 | 13.8126
|  | FULSCOT PRIMARY | HT |  |  |  |  | 34.0516 | 33.6863 | 32.5874 | 31.3663 | 30.5305 | 29.6842 | 28.7484 | 27.7116 | 26.7095 | 22.5516 | 20.2179 | 18.1368 | 29.4558 | 27.7632 | 26.5284 | 25.1505 | 24.2295 | 23.2947 | 22.2474 | 21.0768 | 19.9432 | 15.2337 | 12.6242 | 10.2832 | 30.0558 | 28.3632 | 27.1284 | 25.7526 | 24.8326 | 23.8989 | 22.8537 | 21.6842 | 20.5526 | 15.8495 | 13.2442 | 10.9063
|  | FULSCOT PRIMARY | HE |  |  |  |  | 34.4695 | 34.2811 | 33.9505 | 32.9684 | 32.3568 | 31.7463 | 31.0126 | 30.1632 | 29.3474 | 26.1905 | 24.9126 | -11.7842 | 30.3789 | 28.9716 | 28.0116 | 26.8947 | 26.2158 | 25.5358 | 24.7084 | 23.7432 | 22.8126 | 19.1958 | 17.7505 | 16.6463 | 30.8568 | 29.5716 | 28.6116 | 27.4947 | 26.8168 | 26.1379 | 25.3116 | 24.3474 | 23.4189 | 19.8084 | 18.3642 | 17.2632
|  | FULSCOT PRIMARY | CF |  |  |  |  | 34.5505 | 34.4547 | 34.3558 | 34.2442 | 34.1211 | 34.0853 | 33.9189 | 33.4326 | 32.9221 | 30.7032 | 29.8032 | 29.1916 | 30.5221 | 29.9737 | 29.5074 | 28.9926 | 28.6642 | 28.4347 | 27.9884 | 27.4347 | 26.8537 | 24.3263 | 23.3074 | 22.6105 | 30.9295 | 30.5884 | 30.1232 | 29.6095 | 29.28 | 29.0358 | 28.5884 | 28.0347 | 27.4537 | 24.9305 | 23.9137 | 23.2179
COWLEY GSP | WITNEY BSP | FYFIELD PRIMARY | MINIMUM HEADROOM | SU 42256 99551 | NO | YES | 0 | 18.04 | 17.8589 | 17.6653 | 17.2326 | 16.3221 | 15.4053 | 14.52 | 13.6558 | 13.3726 | 12.0705 | 9.2474 | -1.38 | 15.0495 | 14.7084 | 14.2411 | 13.3526 | 12.3253 | 11.2926 | 10.2916 | 9.3147 | 9.02 | 7.6684 | 4.5137 | 3.6021 | 15.6505 | 15.3042 | 14.8274 | 13.9084 | 12.8768 | 11.84 | 10.8337 | 9.8516 | 9.5505 | 8.1526 | 4.9484 | 4.0168
|  | FYFIELD PRIMARY | EE |  |  |  |  | 18.1537 | 18.0063 | 17.8474 | 17.4958 | 16.66 | 15.8232 | 14.9937 | 14.1747 | 13.9253 | 12.8021 | 11.8011 | 10.2032 | 15.2842 | 15.0137 | 14.6137 | 13.7832 | 12.8358 | 11.8716 | 10.9168 | 9.9737 | 9.7168 | 8.5789 | 7.5737 | 5.7337 | 15.8884 | 15.6126 | 15.2063 | 14.3547 | 13.3853 | 12.4147 | 11.4526 | 10.5042 | 10.2368 | 9.0347 | 7.9537 | 6.0937
|  | FYFIELD PRIMARY | HT |  |  |  |  | 18.04 | 17.8589 | 17.6653 | 17.2326 | 16.3221 | 15.4053 | 14.52 | 13.6558 | 13.3726 | 12.0705 | 9.2474 | 8.3916 | 15.0495 | 14.7084 | 14.2411 | 13.3526 | 12.3253 | 11.2926 | 10.2916 | 9.3147 | 9.02 | 7.6684 | 4.5137 | 3.6021 | 15.6505 | 15.3042 | 14.8274 | 13.9084 | 12.8768 | 11.84 | 10.8337 | 9.8516 | 9.5505 | 8.1526 | 4.9484 | 4.0168
|  | FYFIELD PRIMARY | HE |  |  |  |  | 18.3 | 18.2 | 18.0884 | 17.9684 | 17.2842 | 16.5347 | 15.7905 | 15.0632 | 14.9011 | 14.2505 | 13.7495 | -1.38 | 15.5905 | 15.42 | 15.1147 | 14.3716 | 13.5158 | 12.6453 | 11.7779 | 10.9274 | 10.76 | 10.0874 | 9.56 | 8.7347 | 16.1453 | 16.0274 | 15.7158 | 14.9526 | 14.0716 | 13.1947 | 12.3253 | 11.4726 | 11.3011 | 10.6011 | 10.0516 | 9.2095
|  | FYFIELD PRIMARY | CF |  |  |  |  | 18.3979 | 18.3474 | 18.2947 | 18.24 | 18.1758 | 18.0842 | 17.7021 | 17.3 | 17.1916 | 16.6916 | 16.3368 | 15.7663 | 15.6968 | 15.6453 | 15.5095 | 15.1758 | 14.8053 | 14.4011 | 13.9674 | 13.5084 | 13.3916 | 12.8558 | 12.4758 | 11.8242 | 16.2432 | 16.1926 | 16.1179 | 15.7747 | 15.3916 | 14.9758 | 14.5295 | 14.0568 | 13.9389 | 13.3958 | 13.0042 | 12.34
LOVEDEAN GSP | HAVANT BSP | GABLE HEAD PRIMARY | MINIMUM HEADROOM | SZ 72204 99904 | NO | YES | 0 | 33.2116 | 32.6105 | 31.9432 | 30.9347 | 29.8274 | 28.8368 | 27.9495 | 27.1221 | 26.2695 | 23.3463 | 21 | 4.9179 | 29.0011 | 28.3621 | 27.6442 | 26.5211 | 25.2832 | 24.1853 | 23.2 | 22.28 | 21.3253 | 18.0947 | 15.4926 | 12.2926 | 29.5053 | 28.88 | 28.1684 | 27.0463 | 25.8095 | 24.7116 | 23.7274 | 22.8074 | 21.8516 | 18.6158 | 16.0084 | 12.8095
|  | GABLE HEAD PRIMARY | EE |  |  |  |  | 33.5958 | 33.1537 | 32.6253 | 31.7832 | 30.8495 | 30.0053 | 29.2253 | 28.5316 | 27.8263 | 25.6579 | 23.94 | 21.7453 | 29.4484 | 28.9432 | 28.3811 | 27.4484 | 26.4032 | 25.4632 | 24.5979 | 23.8305 | 23.0453 | 20.6653 | 18.7674 | 16.2611 | 29.9421 | 29.4474 | 28.8968 | 27.9726 | 26.9295 | 25.9884 | 25.1221 | 24.3537 | 23.5684 | 21.1789 | 19.2684 | 16.7621
|  | GABLE HEAD PRIMARY | HT |  |  |  |  | 33.2116 | 32.6105 | 31.9432 | 30.9347 | 29.8274 | 28.8368 | 27.9495 | 27.1221 | 26.2695 | 23.3463 | 21 | 18.1832 | 29.0011 | 28.3621 | 27.6442 | 26.5211 | 25.2832 | 24.1853 | 23.2 | 22.28 | 21.3253 | 18.0947 | 15.4926 | 12.2926 | 29.5053 | 28.88 | 28.1684 | 27.0463 | 25.8095 | 24.7116 | 23.7274 | 22.8074 | 21.8516 | 18.6158 | 16.0084 | 12.8095
|  | GABLE HEAD PRIMARY | HE |  |  |  |  | 33.86 | 33.6621 | 33.4453 | 32.7916 | 31.9905 | 31.2863 | 30.6526 | 30.0979 | 29.5189 | 27.9916 | 26.9074 | 4.9179 | 30.0221 | 29.6926 | 29.3021 | 28.5442 | 27.6495 | 26.86 | 26.1537 | 25.5379 | 24.8874 | 23.2 | 21.9895 | 20.1011 | 30.5032 | 30.1789 | 29.7958 | 29.0611 | 28.1737 | 27.3853 | 26.6789 | 26.0632 | 25.4116 | 23.7221 | 22.5084 | 20.62
|  | GABLE HEAD PRIMARY | CF |  |  |  |  | 34.0421 | 33.9389 | 33.8316 | 33.72 | 33.4168 | 33.04 | 32.6642 | 32.3011 | 31.9063 | 30.8611 | 30.1211 | 29.0684 | 30.4126 | 30.2189 | 29.9916 | 29.6158 | 29.2042 | 28.7905 | 28.3705 | 27.9621 | 27.5168 | 26.3768 | 25.5516 | 24.3358 | 30.8611 | 30.6937 | 30.4726 | 30.1084 | 29.7095 | 29.3074 | 28.8947 | 28.4863 | 28.0411 | 26.9 | 26.0737 | 24.8579
MINETY GSP |  | GALILEO PRIMARY | MINIMUM HEADROOM | SU 10596 83733 | NO | YES | 0 | 51.0705 | 50.9442 | 50.8095 | 50.6705 | 50.5274 | 50.3832 | 50.2579 | 50.1421 | 50.0347 | 49.64 | 48.9347 | 26.3747 | 46.7747 | 46.6032 | 46.3547 | 46.1042 | 45.8579 | 45.6053 | 45.3758 | 45.1642 | 44.9642 | 44.0526 | 42.7747 | 41.5589 | 48.0053 | 47.8789 | 47.7379 | 47.4968 | 47.2495 | 46.9979 | 46.7674 | 46.5558 | 46.3568 | 45.4495 | 44.1716 | 42.9579
|  | GALILEO PRIMARY | EE |  |  |  |  | 51.1432 | 51.0379 | 50.9263 | 50.8105 | 50.6895 | 50.5737 | 50.4632 | 50.3558 | 50.2611 | 49.9505 | 49.7147 | 49.0232 | 46.8579 | 46.7411 | 46.6189 | 46.4147 | 46.2105 | 46.0137 | 45.8232 | 45.6337 | 45.4663 | 44.7916 | 43.7895 | 42.84 | 48.0779 | 47.9726 | 47.8611 | 47.7421 | 47.6021 | 47.4053 | 47.2147 | 47.0263 | 46.8579 | 46.1874 | 45.1842 | 44.2358
|  | GALILEO PRIMARY | HT |  |  |  |  | 51.0705 | 50.9442 | 50.8095 | 50.6705 | 50.5274 | 50.3832 | 50.2579 | 50.1421 | 50.0347 | 49.64 | 48.9347 | 47.8663 | 46.7747 | 46.6032 | 46.3547 | 46.1042 | 45.8579 | 45.6053 | 45.3758 | 45.1642 | 44.9642 | 44.0526 | 42.7747 | 41.5589 | 48.0053 | 47.8789 | 47.7379 | 47.4968 | 47.2495 | 46.9979 | 46.7674 | 46.5558 | 46.3568 | 45.4495 | 44.1716 | 42.9579
|  | GALILEO PRIMARY | HE |  |  |  |  | 51.2411 | 51.1663 | 51.0842 | 50.9958 | 50.9011 | 50.8105 | 50.7253 | 50.6453 | 50.5768 | 50.3063 | 50.1705 | 26.3747 | 46.9663 | 46.8895 | 46.8 | 46.7053 | 46.48 | 46.3137 | 46.1442 | 45.9842 | 45.9063 | 45.5368 | 44.7979 | 44.0863 | 48.1758 | 48.1011 | 48.0189 | 47.9305 | 47.8316 | 47.7053 | 47.5358 | 47.3768 | 47.2968 | 46.9221 | 46.1842 | 45.4726
|  | GALILEO PRIMARY | CF |  |  |  |  | 51.3095 | 51.2705 | 51.2295 | 51.1874 | 51.1442 | 51.0989 | 51.0547 | 51.0105 | 50.9674 | 50.7747 | 50.6758 | 50.6221 | 47.0347 | 46.9958 | 46.9547 | 46.9084 | 46.8621 | 46.7926 | 46.7168 | 46.6316 | 46.5484 | 46.2242 | 45.8842 | 45.4295 | 48.2442 | 48.2053 | 48.1642 | 48.1221 | 48.0789 | 48.0337 | 47.9895 | 47.9432 | 47.8979 | 47.6147 | 47.2768 | 46.8211
LOVEDEAN GSP | PORTSMOUTH BSP | GAMBLE ROAD PRIMARY | MINIMUM HEADROOM | SU 64771 01769 | NO | YES | 0 | 35.5926 | 35.1979 | 34.7705 | 33.6126 | 31.2905 | 28.9684 | 26.6916 | 24.4463 | 22.8589 | 16.7568 | 13.5526 | -9.18 | 30.2316 | 28.9884 | 27.5705 | 25.2316 | 22.6105 | 19.9905 | 17.3863 | 14.8021 | 12.9863 | 6.0326 | 2.4421 | -0.91789 | 31.2705 | 30.0116 | 28.5747 | 26.2011 | 23.5411 | 20.8821 | 18.2695 | 15.6895 | 13.8768 | 6.9337 | 3.3484 | -0.0063158
|  | GAMBLE ROAD PRIMARY | EE |  |  |  |  | 35.8284 | 35.4916 | 35.1284 | 34.7305 | 33.1705 | 30.9705 | 28.7821 | 26.6053 | 24.4611 | 18.2232 | 15.7095 | 13.4158 | 30.9105 | 29.9884 | 28.6968 | 27.2263 | 24.7179 | 22.2274 | 19.7495 | 17.2463 | 14.7705 | 7.6158 | 4.7916 | 2.1947 | 31.8421 | 31.0242 | 29.7147 | 28.2242 | 25.6779 | 23.1495 | 20.6337 | 18.1295 | 15.6589 | 8.5147 | 5.6947 | 3.1021
|  | GAMBLE ROAD PRIMARY | HT |  |  |  |  | 35.5926 | 35.1979 | 34.7705 | 33.6126 | 31.2905 | 28.9684 | 26.6916 | 24.4463 | 22.8589 | 16.7568 | 13.5526 | 10.5726 | 30.2316 | 28.9884 | 27.5705 | 25.2316 | 22.6105 | 19.9905 | 17.3863 | 14.8021 | 12.9863 | 6.0326 | 2.4421 | -0.91789 | 31.2705 | 30.0116 | 28.5747 | 26.2011 | 23.5411 | 20.8821 | 18.2695 | 15.6895 | 13.8768 | 6.9337 | 3.3484 | -0.0063158
|  | GAMBLE ROAD PRIMARY | HE |  |  |  |  | 36.0284 | 35.7547 | 35.4463 | 35.1095 | 34.7168 | 33.4895 | 31.9989 | 30.5284 | 29.0937 | 22.2189 | 19.1621 | -9.18 | 31.1863 | 30.7147 | 29.6821 | 28.4989 | 26.7758 | 25.0737 | 23.3937 | 21.7337 | 20.1105 | 12.16 | 8.6432 | 6.8653 | 32.0379 | 31.76 | 30.7137 | 29.5137 | 27.7653 | 26.0389 | 24.3337 | 22.6484 | 21 | 13.0537 | 9.5421 | 7.7663
|  | GAMBLE ROAD PRIMARY | CF |  |  |  |  | 36.1779 | 36.0263 | 35.8495 | 35.6642 | 35.4716 | 35.26 | 35.0463 | 34.8295 | 34.3905 | 29.7011 | 27.0242 | 25.9568 | 31.3589 | 31.1747 | 30.9042 | 30.4379 | 29.8095 | 28.9653 | 28.0621 | 27.1021 | 26.0811 | 20.7758 | 17.7095 | 16.4895 | 32.1853 | 32.0358 | 31.8642 | 31.4789 | 30.8421 | 29.9863 | 29.0705 | 28.0958 | 27.06 | 21.6747 | 18.5926 | 17.3747
IVER 132KV GSP | DENHAM BSP | GERRARDS CROSS PRIMARY | MINIMUM HEADROOM | SU 99973 87964 | NO | NO | 0 | 16.9674 | 16.7495 | 16.5168 | 16.2789 | 16.0316 | 15.7842 | 15.5674 | 15.3705 | 15.1895 | 14.0853 | 12.7179 | -8.2547 | 13.1516 | 12.7453 | 12.3347 | 11.9274 | 11.5295 | 11.1253 | 10.7463 | 10.3632 | 9.9947 | 8.32 | 6.82 | 5.4632 | 14.1411 | 13.8989 | 13.6368 | 13.2389 | 12.8495 | 12.4474 | 12.0642 | 11.6768 | 11.3053 | 9.6084 | 8.0926 | 6.7337
|  | GERRARDS CROSS PRIMARY | EE |  |  |  |  | 17.1074 | 16.9316 | 18.3716 | 18.0632 | 17.7589 | 17.4611 | 17.1684 | 16.8653 | 16.5811 | 15.3547 | 14.3137 | 13.4179 | 13.3916 | 13.1179 | 12.8453 | 12.5168 | 12.1958 | 11.88 | 11.5695 | 11.2442 | 10.94 | 9.6074 | 8.46 | 7.46 | 14.3011 | 14.1063 | 14.1305 | 13.8011 | 13.48 | 13.1642 | 12.8526 | 12.5274 | 12.22 | 10.8821 | 9.7284 | 8.7253
|  | GERRARDS CROSS PRIMARY | HT |  |  |  |  | 16.9674 | 16.7495 | 16.5168 | 16.2789 | 16.0316 | 15.7842 | 15.5674 | 15.3705 | 15.1895 | 14.0853 | 12.7179 | 11.5011 | 13.1516 | 12.7453 | 12.3347 | 11.9274 | 11.5295 | 11.1253 | 10.7463 | 10.3632 | 9.9947 | 8.32 | 6.82 | 5.4632 | 14.1411 | 13.8989 | 13.6368 | 13.2389 | 12.8495 | 12.4474 | 12.0642 | 11.6768 | 11.3053 | 9.6084 | 8.0926 | 6.7337
|  | GERRARDS CROSS PRIMARY | HE |  |  |  |  | 17.2811 | 17.16 | 17.0253 | 16.8811 | 16.7253 | 16.5779 | 16.4379 | 16.3074 | 16.1947 | 15.8126 | 15.5905 | -8.2547 | 13.6168 | 13.48 | 13.32 | 13.1516 | 12.9484 | 12.7316 | 12.5147 | 12.2863 | 12.0747 | 11.1916 | 10.46 | 9.8368 | 14.5011 | 14.3684 | 14.2232 | 14.0695 | 13.9053 | 13.7474 | 13.5979 | 13.4537 | 13.3284 | 12.5095 | 11.7674 | 11.1326
|  | GERRARDS CROSS PRIMARY | CF |  |  |  |  | 17.3947 | 17.3316 | 17.2663 | 17.1979 | 17.1263 | 17.0537 | 16.9832 | 16.9137 | 16.8421 | 16.5274 | 16.3695 | 16.2821 | 13.7411 | 13.6705 | 13.5968 | 13.5126 | 13.4242 | 13.3326 | 13.2368 | 13.0926 | 12.9442 | 12.2316 | 11.6874 | 11.2379 | 14.6253 | 14.5537 | 14.4811 | 14.4042 | 14.3253 | 14.2463 | 14.1674 | 14.0874 | 14.0053 | 13.5379 | 13.0074 | 12.5505
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM PRIMARY | MINIMUM HEADROOM | ST 80185 25765 | NO | YES | 0 | 30.6853 | 30.1937 | 29.6126 | 28.9063 | 28.0168 | 27.1263 | 26.2505 | 25.6305 | 25.0168 | 22.1305 | 21.5642 | 11.9716 | 28.9716 | 28.4063 | 27.7453 | 26.94 | 25.9105 | 24.8737 | 23.8537 | 23.1337 | 22.4211 | 19.0716 | 18.4432 | 17.7842 | 29.4011 | 28.8274 | 28.1568 | 27.3389 | 26.3063 | 25.2726 | 24.2537 | 23.5347 | 22.8232 | 19.4789 | 18.8505 | 18.1926
|  | GILLINGHAM PRIMARY | EE |  |  |  |  | 30.7737 | 30.3168 | 29.7705 | 29.0863 | 28.2221 | 27.3632 | 26.5084 | 25.9021 | 25.3084 | 22.5358 | 22.1158 | 21.6905 | 29.0747 | 28.5389 | 27.9168 | 27.1347 | 26.1347 | 25.1337 | 24.1347 | 23.4326 | 22.7411 | 19.5137 | 19.0474 | 18.5684 | 29.5074 | 28.9611 | 28.3295 | 27.5358 | 26.5295 | 25.5295 | 24.5326 | 23.8316 | 23.1411 | 19.9179 | 19.4516 | 18.9726
|  | GILLINGHAM PRIMARY | HT |  |  |  |  | 30.6853 | 30.1937 | 29.6126 | 28.9063 | 28.0168 | 27.1263 | 26.2505 | 25.6305 | 25.0168 | 22.1305 | 21.5642 | 20.98 | 28.9716 | 28.4063 | 27.7453 | 26.94 | 25.9105 | 24.8737 | 23.8537 | 23.1337 | 22.4211 | 19.0716 | 18.4432 | 17.7842 | 29.4011 | 28.8274 | 28.1568 | 27.3389 | 26.3063 | 25.2726 | 24.2537 | 23.5347 | 22.8232 | 19.4789 | 18.8505 | 18.1926
|  | GILLINGHAM PRIMARY | HE |  |  |  |  | 30.8905 | 30.4853 | 29.9747 | 29.3274 | 28.4968 | 27.6695 | 26.8463 | 26.2768 | 25.7137 | 23.1021 | 22.8326 | 11.9716 | 29.2137 | 28.72 | 28.1358 | 27.3947 | 26.4337 | 25.4663 | 24.5042 | 23.8389 | 23.1821 | 20.1295 | 19.8274 | 19.5053 | 29.6474 | 29.1453 | 28.5526 | 27.7989 | 26.8295 | 25.8642 | 24.9032 | 24.24 | 23.5842 | 20.5368 | 20.2347 | 19.9137
|  | GILLINGHAM PRIMARY | CF |  |  |  |  | 31.1642 | 30.9832 | 30.7863 | 30.5126 | 30.1674 | 29.7884 | 29.3747 | 29.0611 | 28.7242 | 27.0295 | 26.8368 | 26.6495 | 29.5789 | 29.3379 | 29.0716 | 28.7495 | 28.3537 | 27.92 | 27.4442 | 27.0863 | 26.6958 | 24.7168 | 24.5 | 24.2863 | 30.0179 | 29.7726 | 29.5032 | 29.1758 | 28.7737 | 28.3326 | 27.8495 | 27.4842 | 27.0916 | 25.1158 | 24.9 | 24.6853
FLEET-BRAMLEY GSP | ALDERSHOT BSP | GODALMING PRIMARY | MINIMUM HEADROOM | SU 96743 44375 | NO | YES | 0.018947 | 35.0841 | 34.6873 | 34.2652 | 33.8304 | 33.3799 | 32.9273 | 32.5294 | 31.9167 | 31.2578 | 28.2831 | 25.5536 | -15.1906 | 29.5957 | 28.8473 | 28.0831 | 27.3178 | 26.5557 | 25.8125 | 25.0357 | 24.262 | 23.5378 | 20.2367 | 17.1873 | 14.3788 | 30.9009 | 30.1778 | 29.4399 | 28.6978 | 27.9567 | 27.2167 | 26.4388 | 25.6652 | 24.9399 | 21.6325 | 18.5767 | 15.7652
|  | GODALMING PRIMARY | EE |  |  |  |  | 35.3209 | 34.9946 | 34.6483 | 34.2852 | 33.9115 | 33.5483 | 33.2031 | 32.8715 | 32.5757 | 30.4441 | 28.3473 | 26.4799 | 30.1073 | 29.5167 | 28.9062 | 28.2831 | 27.6683 | 27.0767 | 26.5009 | 25.8694 | 25.2588 | 22.6378 | 20.2725 | 18.1504 | 31.2188 | 30.822 | 30.2304 | 29.6262 | 29.0273 | 28.4536 | 27.8925 | 27.2715 | 26.6599 | 24.0315 | 21.6588 | 19.5315
|  | GODALMING PRIMARY | HT |  |  |  |  | 35.0841 | 34.6873 | 34.2652 | 33.8304 | 33.3799 | 32.9273 | 32.5294 | 31.9167 | 31.2578 | 28.2831 | 25.5536 | 23.0409 | 29.5957 | 28.8473 | 28.0831 | 27.3178 | 26.5557 | 25.8125 | 25.0357 | 24.262 | 23.5378 | 20.2367 | 17.1873 | 14.3788 | 30.9009 | 30.1778 | 29.4399 | 28.6978 | 27.9567 | 27.2167 | 26.4388 | 25.6652 | 24.9399 | 21.6325 | 18.5767 | 15.7652
|  | GODALMING PRIMARY | HE |  |  |  |  | 35.6273 | 35.3957 | 35.1399 | 34.8652 | 34.5715 | 34.2894 | 34.0241 | 33.7757 | 33.5609 | 32.8346 | 31.7515 | -15.1906 | 30.7757 | 30.3946 | 29.9894 | 29.5631 | 29.1262 | 28.7094 | 28.3052 | 27.8367 | 27.3957 | 25.6031 | 24.0199 | 22.6188 | 31.5473 | 31.3062 | 31.042 | 30.7578 | 30.4273 | 30.022 | 29.6262 | 29.1725 | 28.7483 | 27.0031 | 25.4178 | 24.0136
|  | GODALMING PRIMARY | CF |  |  |  |  | 35.8346 | 35.7115 | 35.5831 | 35.4504 | 35.3125 | 35.1725 | 35.0325 | 34.8957 | 34.7588 | 34.1483 | 33.842 | 33.5862 | 31.1031 | 30.9736 | 30.7525 | 30.5083 | 30.2599 | 30.0031 | 29.7473 | 29.502 | 29.2578 | 28.0873 | 26.9441 | 25.9683 | 31.7683 | 31.6388 | 31.5041 | 31.3652 | 31.2199 | 31.0736 | 30.9262 | 30.7831 | 30.5641 | 29.4325 | 28.3462 | 27.3694
WILLESDEN GSP | ACTON LANE BSP | GOLDSMITHS PRIMARY | MINIMUM HEADROOM | TQ 21089 80758 | NO | NO | 0 | 13.54 | 12.7611 | 11.4663 | 9.6253 | 7.4621 | 5.3811 | 3.4053 | 1.9653 | 0.88632 | -2.7705 | -3.8684 | -13.8979 | 11.5642 | 10.6705 | 9.1684 | 7.0253 | 4.5021 | 2.0768 | -0.22842 | -1.9032 | -3.1568 | -7.3842 | -8.6063 | -10.8842 | 12.3179 | 11.5189 | 10.0316 | 7.8874 | 5.3642 | 2.9379 | 0.63263 | -1.0421 | -2.2937 | -6.5147 | -7.7347 | -10.0758
|  | GOLDSMITHS PRIMARY | EE |  |  |  |  | 13.88 | 13.4063 | 12.6811 | 11.5211 | 10.0284 | 8.5495 | 6.6758 | 4.4021 | 2.8937 | -0.61684 | -1.3811 | -2.1032 | 11.9505 | 11.4105 | 10.5779 | 9.2316 | 7.4947 | 5.7737 | 3.5863 | 0.92632 | -0.83368 | -4.6663 | -5.5137 | -6.3253 | 12.42 | 12.2137 | 11.4326 | 10.0947 | 8.3568 | 6.6358 | 4.4474 | 1.7863 | 0.026316 | -3.6747 | -4.5211 | -5.3326
|  | GOLDSMITHS PRIMARY | HT |  |  |  |  | 13.54 | 12.7611 | 11.4663 | 9.6253 | 7.4621 | 5.3811 | 3.4053 | 1.9653 | 0.88632 | -2.7705 | -3.8684 | -5.5937 | 11.5642 | 10.6705 | 9.1684 | 7.0253 | 4.5021 | 2.0768 | -0.22842 | -1.9032 | -3.1568 | -7.3842 | -8.6063 | -10.8842 | 12.3179 | 11.5189 | 10.0316 | 7.8874 | 5.3642 | 2.9379 | 0.63263 | -1.0421 | -2.2937 | -6.5147 | -7.7347 | -10.0758
|  | GOLDSMITHS PRIMARY | HE |  |  |  |  | 14.0632 | 13.6284 | 12.9295 | 11.7874 | 10.2958 | 8.8421 | 6.8874 | 4.7084 | 3.3958 | -0.35895 | -1.8484 | -13.8979 | 12.0547 | 11.6558 | 10.8495 | 9.5211 | 7.7832 | 6.0874 | 3.8 | 1.2474 | -0.28632 | -4.6705 | -6.8495 | -7.3368 | 12.5053 | 12.3905 | 11.6926 | 10.3842 | 8.6463 | 6.9495 | 4.6621 | 2.1084 | 0.57368 | -3.8042 | -6.08 | -6.5663
|  | GOLDSMITHS PRIMARY | CF |  |  |  |  | 14.2358 | 14.1379 | 14.0347 | 13.9316 | 13.8253 | 13.7211 | 13.3968 | 12.7874 | 11.9716 | 4.9379 | 4.3874 | 4.1 | 12.1326 | 12.0695 | 12.0032 | 11.9368 | 11.8674 | 11.7916 | 11.4211 | 10.7137 | 9.7621 | 1.5147 | 0.88947 | 0.56526 | 12.5653 | 12.5084 | 12.4495 | 12.3884 | 12.3221 | 12.2558 | 12.1747 | 11.5537 | 10.6253 | 2.3747 | 1.7505 | 1.4253
NURSLING GSP | WINCHESTER BSP | GORDON ROAD PRIMARY | MINIMUM HEADROOM | SU 48217 29991 | NO | YES | 0 | 35.8926 | 35.6611 | 35.4158 | 35.16 | 34.8937 | 34.6253 | 34.3863 | 34.1684 | 33.9663 | 31.7768 | 29.6211 | -8.54 | 31.0379 | 30.7411 | 30.0926 | 29.2516 | 28.2326 | 27.1926 | 26.6284 | 26.1821 | 25.6821 | 23.0705 | 20.6389 | 18.3547 | 31.8053 | 31.5737 | 31.3126 | 30.9832 | 29.9537 | 28.9137 | 28.3495 | 27.9042 | 27.4042 | 24.7968 | 22.3695 | 20.0874
|  | GORDON ROAD PRIMARY | EE |  |  |  |  | 36.0232 | 35.8316 | 35.6263 | 35.4105 | 35.1853 | 34.9674 | 34.7568 | 34.5537 | 34.3716 | 33.1379 | 31.4337 | 29.8663 | 31.1758 | 30.9695 | 30.5547 | 29.7968 | 28.8568 | 27.9168 | 27.4484 | 27.0895 | 26.6758 | 24.5779 | 22.6505 | 20.8621 | 31.9347 | 31.7432 | 31.5389 | 31.2916 | 30.5905 | 29.6368 | 29.1684 | 28.8105 | 28.3968 | 26.3011 | 24.3758 | 22.5905
|  | GORDON ROAD PRIMARY | HT |  |  |  |  | 35.8926 | 35.6611 | 35.4158 | 35.16 | 34.8937 | 34.6253 | 34.3863 | 34.1684 | 33.9663 | 31.7768 | 29.6211 | 27.6074 | 31.0379 | 30.7411 | 30.0926 | 29.2516 | 28.2326 | 27.1926 | 26.6284 | 26.1821 | 25.6821 | 23.0705 | 20.6389 | 18.3547 | 31.8053 | 31.5737 | 31.3126 | 30.9832 | 29.9537 | 28.9137 | 28.3495 | 27.9042 | 27.4042 | 24.7968 | 22.3695 | 20.0874
|  | GORDON ROAD PRIMARY | HE |  |  |  |  | 36.1779 | 36.0305 | 35.8674 | 35.6916 | 35.5053 | 35.3263 | 35.1579 | 35.0011 | 34.8653 | 34.4 | 33.4589 | -8.54 | 31.3358 | 31.1821 | 31.0053 | 30.4842 | 29.64 | 28.8053 | 28.4432 | 28.1884 | 27.8768 | 26.2989 | 24.8789 | 23.5916 | 32.0905 | 31.9432 | 31.78 | 31.5968 | 31.3705 | 30.5326 | 30.1642 | 29.9095 | 29.5979 | 28.0221 | 26.6042 | 25.3189
|  | GORDON ROAD PRIMARY | CF |  |  |  |  | 36.2874 | 36.2 | 36.1095 | 36.0168 | 35.92 | 35.8221 | 35.7253 | 35.6295 | 35.5337 | 35.1063 | 34.8916 | 34.7726 | 31.4453 | 31.3579 | 31.2642 | 31.1611 | 31.0389 | 30.6168 | 30.3926 | 30.2284 | 30.0179 | 28.8579 | 27.9 | 27.0558 | 32.2 | 32.1126 | 32.0221 | 31.9295 | 31.8326 | 31.7274 | 31.6232 | 31.5232 | 31.42 | 30.5937 | 29.6211 | 28.7779
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | GORING PRIMARY | MINIMUM HEADROOM | SU 60305 82895 | NO | YES | 0 | 16.78 | 16.6189 | 16.4547 | 16.2895 | 16.1263 | 15.96 | 15.8084 | 15.6663 | 15.5358 | 14.9674 | 14.4421 | 6.1684 | 15.2526 | 15.1 | 14.9389 | 14.7632 | 14.5895 | 14.4126 | 14.2495 | 14.0968 | 13.9558 | 13.3411 | 12.7632 | 12.1937 | 15.5737 | 15.4621 | 15.3453 | 15.2274 | 15.1074 | 14.9811 | 14.8211 | 14.6716 | 14.5326 | 13.9211 | 13.3432 | 12.7747
|  | GORING PRIMARY | EE |  |  |  |  | 16.8926 | 16.7642 | 16.6347 | 16.5032 | 16.3684 | 16.2368 | 16.1105 | 15.9895 | 15.8768 | 15.4368 | 15.0537 | 14.6874 | 15.3579 | 15.2368 | 15.1126 | 14.9874 | 14.8516 | 14.7105 | 14.5747 | 14.4453 | 14.3253 | 13.8484 | 13.4263 | 13.0137 | 15.6463 | 15.5579 | 15.4642 | 15.3695 | 15.2705 | 15.1747 | 15.0842 | 14.9979 | 14.8958 | 14.4274 | 14.0063 | 13.5947
|  | GORING PRIMARY | HT |  |  |  |  | 16.78 | 16.6189 | 16.4547 | 16.2895 | 16.1263 | 15.96 | 15.8084 | 15.6663 | 15.5358 | 14.9674 | 14.4421 | 13.9326 | 15.2526 | 15.1 | 14.9389 | 14.7632 | 14.5895 | 14.4126 | 14.2495 | 14.0968 | 13.9558 | 13.3411 | 12.7632 | 12.1937 | 15.5737 | 15.4621 | 15.3453 | 15.2274 | 15.1074 | 14.9811 | 14.8211 | 14.6716 | 14.5326 | 13.9211 | 13.3432 | 12.7747
|  | GORING PRIMARY | HE |  |  |  |  | 17.0053 | 16.9537 | 16.8684 | 16.7768 | 16.6832 | 16.5874 | 16.4968 | 16.4116 | 16.3347 | 16.0579 | 15.8263 | 6.1684 | 15.4947 | 15.4158 | 15.3326 | 15.2453 | 15.1547 | 15.0632 | 14.9768 | 14.8947 | 14.8221 | 14.5242 | 14.2684 | 14.0105 | 15.7411 | 15.68 | 15.6158 | 15.5463 | 15.4737 | 15.4021 | 15.3337 | 15.2705 | 15.2147 | 15.0242 | 14.84 | 14.5905
|  | GORING PRIMARY | CF |  |  |  |  | 17.0537 | 17.0274 | 16.9989 | 16.9684 | 16.9147 | 16.8611 | 16.8053 | 16.7526 | 16.6979 | 16.4568 | 16.28 | 16.1232 | 15.5705 | 15.5253 | 15.4768 | 15.4295 | 15.3789 | 15.3284 | 15.2758 | 15.2263 | 15.1737 | 14.9411 | 14.7432 | 14.5663 | 15.7979 | 15.7653 | 15.7305 | 15.6968 | 15.66 | 15.6242 | 15.5863 | 15.5516 | 15.5147 | 15.3537 | 15.2579 | 15.1379
IVER 132KV GSP | DENHAM BSP | GRASSINGHAM ROAD PRIMARY | MINIMUM HEADROOM | TQ 00165 90988 | NO | NO | 0 | 18.957 | 18.7307 | 18.4938 | 18.2465 | 17.9812 | 17.7149 | 17.4791 | 17.2612 | 17.0591 | 15.4149 | 13.8644 | -8.4641 | 13.7149 | 13.4244 | 13.1254 | 12.8202 | 12.5075 | 12.1675 | 11.7507 | 11.3359 | 10.9349 | 9.0465 | 7.3286 | 5.8086 | 15.7928 | 15.3738 | 14.9549 | 14.5328 | 14.1107 | 13.6802 | 13.2749 | 12.8654 | 12.4591 | 10.5486 | 8.8012 | 7.2717
|  | GRASSINGHAM ROAD PRIMARY | EE |  |  |  |  | 19.0759 | 18.8854 | 18.6833 | 18.4717 | 18.2444 | 18.0202 | 17.8044 | 17.5949 | 17.4044 | 16.4212 | 15.1844 | 14.1591 | 13.8844 | 13.6444 | 13.3959 | 13.1402 | 12.8759 | 12.6159 | 12.3644 | 12.1128 | 11.7823 | 10.2317 | 8.857 | 7.6917 | 16.0612 | 15.7223 | 15.3791 | 15.0349 | 14.6844 | 14.3349 | 13.9865 | 13.6265 | 13.2844 | 11.7138 | 10.298 | 9.1212
|  | GRASSINGHAM ROAD PRIMARY | HT |  |  |  |  | 18.957 | 18.7307 | 18.4938 | 18.2465 | 17.9812 | 17.7149 | 17.4791 | 17.2612 | 17.0591 | 15.4149 | 13.8644 | 12.5096 | 13.7149 | 13.4244 | 13.1254 | 12.8202 | 12.5075 | 12.1675 | 11.7507 | 11.3359 | 10.9349 | 9.0465 | 7.3286 | 5.8086 | 15.7928 | 15.3738 | 14.9549 | 14.5328 | 14.1107 | 13.6802 | 13.2749 | 12.8654 | 12.4591 | 10.5486 | 8.8012 | 7.2717
|  | GRASSINGHAM ROAD PRIMARY | HE |  |  |  |  | 19.2496 | 19.1138 | 18.9633 | 18.8012 | 18.6202 | 18.4486 | 18.2865 | 18.1317 | 17.9991 | 17.5244 | 17.2338 | -8.4641 | 14.1265 | 13.9612 | 13.7844 | 13.5949 | 13.3949 | 13.2023 | 13.017 | 12.8328 | 12.6696 | 12.0507 | 11.2212 | 10.497 | 16.4359 | 16.2149 | 15.9844 | 15.7433 | 15.4896 | 15.2475 | 15.0044 | 14.7507 | 14.5159 | 13.537 | 12.7244 | 11.9917
|  | GRASSINGHAM ROAD PRIMARY | CF |  |  |  |  | 19.3665 | 19.2917 | 19.2149 | 19.1349 | 19.0486 | 18.9612 | 18.8728 | 18.7875 | 18.7033 | 18.3191 | 18.1128 | 17.9854 | 14.257 | 14.1728 | 14.0749 | 13.9749 | 13.8696 | 13.7633 | 13.6549 | 13.5454 | 13.4359 | 12.9244 | 12.5444 | 12.0296 | 16.5928 | 16.4917 | 16.3528 | 16.2117 | 16.0654 | 15.9159 | 15.7633 | 15.6012 | 15.438 | 14.6496 | 14.0475 | 13.5475
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | GREEN PARK PRIMARY | MINIMUM HEADROOM | SU 70508 70222 | NO | YES | 0 | 40.8429 | 40.8419 | 40.6861 | 40.5314 | 40.3766 | 40.3766 | 40.3745 | 40.3745 | 40.3745 | 40.3724 | 40.3724 | 29.204 | 38.6429 | 38.6419 | 38.4598 | 38.2766 | 38.0945 | 38.0945 | 38.0924 | 38.0924 | 38.0924 | 38.0903 | 38.0903 | 38.0893 | 39.2272 | 39.2261 | 39.0672 | 38.8914 | 38.7166 | 38.7166 | 38.7145 | 38.7145 | 38.7145 | 38.7124 | 38.7124 | 38.7114
|  | GREEN PARK PRIMARY | EE |  |  |  |  | 40.844 | 40.8419 | 40.6861 | 40.5314 | 40.3766 | 40.3766 | 40.3766 | 40.3756 | 40.3756 | 40.3745 | 40.3745 | 40.3724 | 38.644 | 38.6419 | 38.4598 | 38.2766 | 38.0945 | 38.0945 | 38.0945 | 38.0935 | 38.0935 | 38.0924 | 38.0924 | 38.0903 | 39.2282 | 39.2261 | 39.0672 | 38.8914 | 38.7166 | 38.7166 | 38.7166 | 38.7156 | 38.7156 | 38.7145 | 38.7145 | 38.7124
|  | GREEN PARK PRIMARY | HT |  |  |  |  | 40.8429 | 40.8419 | 40.6861 | 40.5314 | 40.3766 | 40.3766 | 40.3745 | 40.3745 | 40.3745 | 40.3724 | 40.3724 | 40.3724 | 38.6429 | 38.6419 | 38.4598 | 38.2766 | 38.0945 | 38.0945 | 38.0924 | 38.0924 | 38.0924 | 38.0903 | 38.0903 | 38.0893 | 39.2272 | 39.2261 | 39.0672 | 38.8914 | 38.7166 | 38.7166 | 38.7145 | 38.7145 | 38.7145 | 38.7124 | 38.7124 | 38.7114
|  | GREEN PARK PRIMARY | HE |  |  |  |  | 40.844 | 40.844 | 40.6882 | 40.5324 | 40.3766 | 40.3766 | 40.3766 | 40.3766 | 40.3766 | 40.3756 | 40.3756 | 29.204 | 38.644 | 38.644 | 38.4619 | 38.2777 | 38.0945 | 38.0945 | 38.0945 | 38.0945 | 38.0945 | 38.0935 | 38.0935 | 38.0935 | 39.2282 | 39.2282 | 39.0693 | 38.8924 | 38.7166 | 38.7166 | 38.7166 | 38.7166 | 38.7166 | 38.7156 | 38.7156 | 38.7156
|  | GREEN PARK PRIMARY | CF |  |  |  |  | 41.0293 | 41.0293 | 41.0293 | 41.0293 | 41.0293 | 41.0293 | 40.9493 | 40.9493 | 40.8724 | 40.7945 | 40.7945 | 40.7945 | 38.8619 | 38.8619 | 38.8619 | 38.8619 | 38.8619 | 38.8619 | 38.7693 | 38.7693 | 38.6777 | 38.5861 | 38.5861 | 38.5861 | 39.4135 | 39.4135 | 39.4135 | 39.4135 | 39.4135 | 39.4135 | 39.3345 | 39.3345 | 39.2566 | 39.1798 | 39.1798 | 39.1798
WILLESDEN GSP |  | GREENFORD PRIMARY | MINIMUM HEADROOM | TQ 14695 83785 | NO | NO | 0 | 73.6579 | 73.1758 | 72.6632 | 72.1295 | 72.1368 | 70.72 | 69.6853 | 68.9768 | 68.3242 | 64.7568 | 61.08 | 3.1116 | 61.0758 | 59.2453 | 56.3274 | 54.1137 | 54.0295 | 52.4305 | 51.2884 | 50.5305 | 49.8337 | 46.2389 | 42.1421 | 38.2316 | 64.0874 | 62.2568 | 59.3379 | 57.1242 | 57.04 | 55.44 | 54.2979 | 53.54 | 52.8021 | 48.9053 | 44.8084 | 40.8968
|  | GREENFORD PRIMARY | EE |  |  |  |  | 73.9126 | 73.5053 | 73.0716 | 72.6137 | 72.1368 | 70.72 | 69.6853 | 68.9768 | 68.3274 | 68.4053 | 65.8274 | 63.4463 | 61.7642 | 60.2495 | 57.7495 | 55.9684 | 54.0295 | 52.4305 | 51.2884 | 50.5305 | 49.8337 | 50.3474 | 47.4853 | 44.8095 | 64.7758 | 63.26 | 60.76 | 58.9779 | 57.04 | 55.44 | 54.2979 | 53.54 | 52.8421 | 53.0147 | 50.1516 | 47.4758
|  | GREENFORD PRIMARY | HT |  |  |  |  | 73.6579 | 73.1758 | 72.6632 | 72.1295 | 72.8505 | 71.1495 | 69.9274 | 69.1042 | 68.3242 | 64.7568 | 61.08 | 57.6 | 61.0758 | 59.2453 | 56.3274 | 54.1137 | 55.1274 | 53.2211 | 51.8695 | 50.98 | 50.1358 | 46.2389 | 42.1421 | 38.2316 | 64.0874 | 62.2568 | 59.3379 | 57.1242 | 57.7958 | 55.8884 | 54.5368 | 53.6463 | 52.8021 | 48.9053 | 44.8084 | 40.8968
|  | GREENFORD PRIMARY | HE |  |  |  |  | 74.2442 | 73.9337 | 73.5905 | 73.2221 | 72.8284 | 72.4526 | 71.6105 | 71.1021 | 70.6495 | 71.7232 | 70.1095 | 3.1116 | 62.5632 | 61.2905 | 59.0211 | 57.4632 | 55.7326 | 54.3411 | 53.4042 | 52.8642 | 52.3821 | 53.9905 | 52.1926 | 50.5621 | 65.5747 | 64.3021 | 62.0316 | 60.4737 | 58.7421 | 57.3505 | 56.4137 | 55.8737 | 55.3916 | 56.6589 | 54.8611 | 53.2295
|  | GREENFORD PRIMARY | CF |  |  |  |  | 74.4863 | 74.3084 | 74.1232 | 73.9305 | 73.7316 | 73.5295 | 73.3305 | 73.1337 | 72.9368 | 72.0579 | 73.7884 | 73.5421 | 63.5095 | 62.8337 | 61.8379 | 61.1674 | 60.4105 | 59.6737 | 59.0389 | 58.5074 | 58.1421 | 56.3916 | 58.5832 | 57.4937 | 66.4505 | 65.8463 | 64.8495 | 64.1789 | 63.4221 | 62.6853 | 62.0495 | 61.5179 | 61.1537 | 59.4021 | 61.2526 | 60.1632
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET PRIMARY | MINIMUM HEADROOM | SU 64445 00178 | NO | YES | 0 | 34.4495 | 34.3632 | 34.2716 | 33.6158 | 31.9726 | 31.2705 | 30.5789 | 29.8768 | 29.6874 | 28.6895 | 27.6579 | 11.8074 | 30.9726 | 30.8758 | 30.1884 | 28.5368 | 26.6221 | 25.8147 | 25.0179 | 24.2063 | 23.9979 | 22.8863 | 21.7221 | 20.6316 | 31.6811 | 31.5905 | 31.3032 | 29.6821 | 27.7705 | 26.9642 | 26.1695 | 25.3589 | 25.1505 | 24.04 | 22.8779 | 21.7895
|  | GREETHAM STREET PRIMARY | EE |  |  |  |  | 34.5095 | 34.4411 | 34.3695 | 34.2863 | 32.6758 | 32.0105 | 31.3463 | 30.6853 | 30.0116 | 29.2968 | 28.4863 | 27.7368 | 31.04 | 30.9642 | 30.3821 | 29.3053 | 27.4253 | 26.6558 | 25.8895 | 25.1253 | 24.3453 | 23.5526 | 22.6358 | 21.7821 | 31.7442 | 31.6726 | 31.4821 | 30.4495 | 28.5726 | 27.8053 | 27.0389 | 26.2758 | 25.4979 | 24.7063 | 23.7905 | 22.9379
|  | GREETHAM STREET PRIMARY | HT |  |  |  |  | 34.4495 | 34.3632 | 34.2716 | 33.6158 | 31.9726 | 31.2705 | 30.5789 | 29.8768 | 29.6874 | 28.6895 | 27.6579 | 26.6958 | 30.9726 | 30.8758 | 30.1884 | 28.5368 | 26.6221 | 25.8147 | 25.0179 | 24.2063 | 23.9979 | 22.8863 | 21.7221 | 20.6316 | 31.6811 | 31.5905 | 31.3032 | 29.6821 | 27.7705 | 26.9642 | 26.1695 | 25.3589 | 25.1505 | 24.04 | 22.8779 | 21.7895
|  | GREETHAM STREET PRIMARY | HE |  |  |  |  | 34.5453 | 34.4853 | 34.4189 | 34.3484 | 33.0863 | 32.6516 | 32.2232 | 31.7989 | 31.3853 | 30.0253 | 29.4979 | 11.8074 | 31.0863 | 31.0211 | 30.5579 | 29.5147 | 27.8968 | 27.3979 | 26.9063 | 26.4179 | 25.94 | 24.3758 | 23.7768 | 23.1463 | 31.7842 | 31.7232 | 31.6095 | 30.6589 | 29.0432 | 28.5453 | 28.0547 | 27.5663 | 27.0905 | 25.5284 | 24.9295 | 24.3011
|  | GREETHAM STREET PRIMARY | CF |  |  |  |  | 34.5811 | 34.5432 | 34.5032 | 34.4621 | 34.42 | 34.3768 | 34.3337 | 34.2916 | 34.0811 | 32.9305 | 32.6168 | 32.2663 | 31.1253 | 31.0821 | 30.9368 | 30.6632 | 30.1537 | 29.9105 | 29.6484 | 29.3695 | 29.0716 | 27.7505 | 27.3989 | 26.9958 | 31.8221 | 31.7821 | 31.7211 | 31.6558 | 31.2958 | 31.0526 | 30.7926 | 30.5137 | 30.2158 | 28.8968 | 28.5453 | 28.1442
COWLEY GSP | DRAYTON BSP | GROVE PRIMARY | MINIMUM HEADROOM | SU 39515 89611 | NO | YES | 0.37895 | 15.9526 | 15.6589 | 15.3316 | 14.1137 | 12.4242 | 10.7379 | 9.2663 | 7.9653 | 6.94 | 2.0179 | -2.8979 | -21.7053 | 11.5305 | 10.6095 | 9.4326 | 7.8211 | 5.8832 | 3.9484 | 2.26 | 0.76842 | -0.40316 | -6.0495 | -11.7253 | -17.8368 | 12.5621 | 11.6916 | 10.5832 | 8.9937 | 7.0579 | 5.1274 | 3.4411 | 1.9516 | 0.78316 | -4.8547 | -10.5211 | -16.6221
|  | GROVE PRIMARY | EE |  |  |  |  | 16.1105 | 15.8663 | 15.5905 | 14.5495 | 13.0053 | 11.4147 | 10.0158 | 8.7695 | 7.8021 | 3.2453 | -1.1411 | -5.8916 | 11.8495 | 11.0253 | 9.9432 | 8.4232 | 6.5695 | 4.7295 | 3.1126 | 1.6768 | 0.56632 | -4.7168 | -9.8021 | -15.3358 | 12.8684 | 12.0905 | 11.0737 | 9.5947 | 7.7442 | 5.9074 | 4.2937 | 2.86 | 1.7505 | -3.5232 | -8.6 | -14.1232
|  | GROVE PRIMARY | HT |  |  |  |  | 15.9526 | 15.6589 | 15.3316 | 14.1137 | 12.4242 | 10.7379 | 9.2663 | 7.9653 | 6.94 | 2.0179 | -2.8979 | -8.1632 | 11.5305 | 10.6095 | 9.4326 | 7.8211 | 5.8832 | 3.9484 | 2.26 | 0.76842 | -0.40316 | -6.0495 | -11.7253 | -17.8368 | 12.5621 | 11.6916 | 10.5832 | 8.9937 | 7.0579 | 5.1274 | 3.4411 | 1.9516 | 0.78316 | -4.8547 | -10.5211 | -16.6221
|  | GROVE PRIMARY | HE |  |  |  |  | 16.3063 | 16.1421 | 15.9295 | 15.2568 | 13.8442 | 12.3547 | 11.0495 | 9.9032 | 9.0316 | 4.9347 | 0.96947 | -21.7053 | 12.2758 | 11.5842 | 10.6274 | 9.2274 | 7.4853 | 5.7547 | 4.2421 | 2.9137 | 1.9074 | -2.8768 | -7.4979 | -12.5947 | 13.2768 | 12.6263 | 11.7295 | 10.3979 | 8.6589 | 6.9316 | 5.4211 | 4.0958 | 3.0905 | -1.6853 | -6.2979 | -11.3853
|  | GROVE PRIMARY | CF |  |  |  |  | 16.4389 | 16.3642 | 16.2779 | 16.1611 | 16.0326 | 15.7042 | 15.0853 | 14.4926 | 13.9768 | 11.2158 | 8.6895 | 5.9947 | 12.7168 | 12.3621 | 11.9105 | 11.2905 | 10.5516 | 9.7453 | 8.9726 | 8.2337 | 7.6179 | 4.4189 | 1.4653 | -1.7032 | 13.6253 | 13.3611 | 12.9379 | 12.3589 | 11.6684 | 10.9147 | 10.1442 | 9.4063 | 8.7916 | 5.5989 | 2.6495 | -0.51263
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL PRIMARY | MINIMUM HEADROOM | ST 98638 11417 | YES | YES | 0 | 5.2253 | 5.2 | 5.1737 | 5.1463 | 5.12 | 5.0926 | 5.0674 | 5.0453 | 5.0242 | 4.9316 | 4.82 | 3.1853 | 5.0274 | 5.0042 | 4.98 | 4.9558 | 4.9316 | 4.9063 | 4.8789 | 4.8547 | 4.8316 | 4.7305 | 4.6042 | 4.4726 | 5.0305 | 5.0084 | 4.9853 | 4.9611 | 4.9379 | 4.9147 | 4.8926 | 4.8737 | 4.8558 | 4.78 | 4.6979 | 4.5947
|  | GUSSAGE ST MICHAEL PRIMARY | EE |  |  |  |  | 5.2432 | 5.2221 | 5.2021 | 5.18 | 5.1589 | 5.1389 | 5.1189 | 5.1 | 5.0821 | 5.0105 | 4.9253 | 4.8305 | 5.0432 | 5.0242 | 5.0053 | 4.9853 | 4.9663 | 4.9474 | 4.9295 | 4.9126 | 4.8947 | 4.8179 | 4.7211 | 4.6105 | 5.0463 | 5.0274 | 5.0095 | 4.9895 | 4.9705 | 4.9526 | 4.9347 | 4.9189 | 4.9032 | 4.8442 | 4.7832 | 4.7189
|  | GUSSAGE ST MICHAEL PRIMARY | HT |  |  |  |  | 5.2253 | 5.2 | 5.1737 | 5.1463 | 5.12 | 5.0926 | 5.0674 | 5.0453 | 5.0242 | 4.9316 | 4.82 | 4.7053 | 5.0274 | 5.0042 | 4.98 | 4.9558 | 4.9316 | 4.9063 | 4.8789 | 4.8547 | 4.8316 | 4.7305 | 4.6042 | 4.4726 | 5.0305 | 5.0084 | 4.9853 | 4.9611 | 4.9379 | 4.9147 | 4.8926 | 4.8737 | 4.8558 | 4.78 | 4.6979 | 4.5947
|  | GUSSAGE ST MICHAEL PRIMARY | HE |  |  |  |  | 5.2663 | 5.2526 | 5.2389 | 5.2253 | 5.2105 | 5.1958 | 5.1821 | 5.1705 | 5.1589 | 5.1179 | 5.06 | 3.1853 | 5.0642 | 5.0516 | 5.0389 | 5.0253 | 5.0116 | 4.9979 | 4.9853 | 4.9737 | 4.9632 | 4.9253 | 4.8695 | 4.7863 | 5.0663 | 5.0537 | 5.0421 | 5.0284 | 5.0147 | 5.0011 | 4.9884 | 4.9779 | 4.9674 | 4.9305 | 4.8895 | 4.8442
|  | GUSSAGE ST MICHAEL PRIMARY | CF |  |  |  |  | 5.2789 | 5.2726 | 5.2663 | 5.2579 | 5.2505 | 5.2421 | 5.2347 | 5.2263 | 5.22 | 5.1853 | 5.1537 | 5.1211 | 5.0758 | 5.0705 | 5.0642 | 5.0558 | 5.0505 | 5.0421 | 5.0347 | 5.0284 | 5.0221 | 4.9895 | 4.9632 | 4.9316 | 5.0779 | 5.0716 | 5.0663 | 5.0589 | 5.0526 | 5.0453 | 5.0379 | 5.0305 | 5.0253 | 4.9937 | 4.9695 | 4.9474
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE PRIMARY | MINIMUM HEADROOM | SU 47370 08794 | NO | YES | 0 | 35.7642 | 35.5789 | 35.3821 | 35.18 | 34.9684 | 34.7558 | 34.5663 | 34.14 | 33.7011 | 31.6442 | 29.8432 | 5.8421 | 31.5158 | 31.1768 | 30.8305 | 30.4905 | 30.1116 | 29.6295 | 29.1874 | 28.7168 | 28.24 | 25.9947 | 23.98 | 22.1326 | 32.5926 | 32.2442 | 31.8758 | 31.5158 | 31.1211 | 30.6295 | 30.1789 | 29.6968 | 29.2095 | 26.9084 | 24.8811 | 23.0326
|  | HAMBLE PRIMARY | EE |  |  |  |  | 35.8684 | 35.7158 | 35.5516 | 35.3811 | 35.2011 | 35.0284 | 34.8621 | 34.7021 | 34.5021 | 32.8095 | 31.3589 | 30.0726 | 31.7347 | 31.4621 | 31.18 | 30.9011 | 30.62 | 30.2558 | 29.8926 | 29.5116 | 29.1095 | 27.2653 | 25.6737 | 24.2126 | 32.8179 | 32.5379 | 32.2495 | 31.9568 | 31.66 | 31.2663 | 30.8958 | 30.5063 | 30.0947 | 28.2021 | 26.5642 | 25.1
|  | HAMBLE PRIMARY | HT |  |  |  |  | 35.7642 | 35.5789 | 35.3821 | 35.18 | 34.9684 | 34.7558 | 34.5663 | 34.14 | 33.7011 | 31.6442 | 29.8432 | 28.2126 | 31.5158 | 31.1768 | 30.8305 | 30.4905 | 30.1116 | 29.6295 | 29.1874 | 28.7168 | 28.24 | 25.9947 | 23.98 | 22.1326 | 32.5926 | 32.2442 | 31.8758 | 31.5158 | 31.1211 | 30.6295 | 30.1789 | 29.6968 | 29.2095 | 26.9084 | 24.8811 | 23.0326
|  | HAMBLE PRIMARY | HE |  |  |  |  | 36.0116 | 35.9021 | 35.7811 | 35.6505 | 35.5105 | 35.3747 | 35.2474 | 35.1284 | 35.0263 | 34.1242 | 33.0379 | 5.8421 | 31.9716 | 31.8495 | 31.6547 | 31.46 | 31.2568 | 30.9684 | 30.7074 | 30.4211 | 30.1095 | 28.6642 | 27.4589 | 26.3705 | 33.0621 | 32.9379 | 32.7389 | 32.54 | 32.3326 | 32.0347 | 31.7537 | 31.4421 | 31.1147 | 29.6316 | 28.3926 | 27.2768
|  | HAMBLE PRIMARY | CF |  |  |  |  | 36.1116 | 36.0526 | 35.9926 | 35.9295 | 35.8642 | 35.7968 | 35.7305 | 35.6653 | 35.6011 | 35.3074 | 34.8568 | 34.2495 | 32.0716 | 32.0126 | 31.9526 | 31.8695 | 31.7537 | 31.5979 | 31.4379 | 31.2747 | 31.0989 | 30.2116 | 29.4274 | 28.7505 | 33.1621 | 33.1032 | 33.0432 | 32.9579 | 32.8389 | 32.6768 | 32.5126 | 32.3411 | 32.1505 | 31.2116 | 30.4063 | 29.7084
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | HAMWORTHY PRIMARY | MINIMUM HEADROOM | SZ 00104 90800 | NO | YES | 0 | 44.0895 | 43.6726 | 42.6179 | 41.4674 | 41.4747 | 40.1937 | 38.6821 | 37.4053 | 36.1579 | 31.4537 | 28.6779 | -4.0484 | 39.2726 | 38.4126 | 37.2421 | 35.9642 | 36.1 | 34.6737 | 32.9705 | 31.5221 | 30.0926 | 24.8126 | 21.7505 | 18.8116 | 40.3084 | 39.4326 | 38.2368 | 36.9295 | 36.8947 | 35.4337 | 33.6863 | 32.2168 | 30.7832 | 25.4821 | 22.3958 | 19.4474
|  | HAMWORTHY PRIMARY | EE |  |  |  |  | 44.2884 | 43.9979 | 43.4716 | 42.6253 | 41.6684 | 40.7126 | 39.4747 | 38.2147 | 38.1695 | 33.2842 | 31.1021 | 29.1 | 39.7116 | 38.9832 | 38.1884 | 37.2537 | 36.1947 | 35.1368 | 33.7474 | 32.3305 | 32.3863 | 26.8337 | 24.4411 | 22.1916 | 40.7547 | 40.0126 | 39.2011 | 38.2474 | 37.1653 | 36.0811 | 34.6547 | 33.2011 | 33.0768 | 27.4916 | 25.0653 | 22.8053
|  | HAMWORTHY PRIMARY | HT |  |  |  |  | 44.0895 | 43.6726 | 42.6179 | 41.4674 | 41.4747 | 40.1937 | 38.6821 | 37.4053 | 36.1579 | 31.4537 | 28.6779 | 26.0558 | 39.2726 | 38.4126 | 37.2421 | 35.9642 | 36.1 | 34.6737 | 32.9705 | 31.5221 | 30.0926 | 24.8126 | 21.7505 | 18.8116 | 40.3084 | 39.4326 | 38.2368 | 36.9295 | 36.8947 | 35.4337 | 33.6863 | 32.2168 | 30.7832 | 25.4821 | 22.3958 | 19.4474
|  | HAMWORTHY PRIMARY | HE |  |  |  |  | 44.5547 | 44.3442 | 44.1137 | 43.6263 | 42.7947 | 41.9747 | 40.8379 | 39.7116 | 39.8347 | 35.8021 | 34.3516 | -4.0484 | 40.3011 | 39.7526 | 39.1147 | 38.3368 | 37.4147 | 36.5 | 35.2147 | 33.94 | 34.1758 | 29.5442 | 27.9232 | 26.3484 | 41.2768 | 40.7968 | 40.1453 | 39.3505 | 38.4053 | 37.4695 | 36.1505 | 34.84 | 34.9032 | 30.2274 | 28.5979 | 27.0147
|  | HAMWORTHY PRIMARY | CF |  |  |  |  | 44.7421 | 44.6305 | 44.5126 | 44.3926 | 44.2653 | 44.1347 | 44.0063 | 43.8811 | 43.4695 | 40.4558 | 39.3558 | 38.4516 | 40.7547 | 40.4558 | 40.2421 | 40.0242 | 39.7832 | 39.5211 | 39.0926 | 38.6611 | 38.1779 | 34.8116 | 33.58 | 32.5368 | 41.6737 | 41.4137 | 41.2211 | 41.0242 | 40.8053 | 40.5621 | 40.1242 | 39.6811 | 39.1863 | 35.5421 | 34.2768 | 33.2242
IVER 132KV GSP | DENHAM BSP | HAREFIELD PRIMARY | MINIMUM HEADROOM | TQ 04001 91227 | NO | NO | 0 | 14.1316 | 14.0411 | 13.9463 | 13.8474 | 13.7432 | 13.6337 | 13.4053 | 13.1779 | 12.9642 | 11.9811 | 11.1221 | 3.1368 | 12.6611 | 12.4505 | 12.2126 | 11.9421 | 11.6463 | 11.3684 | 11.1032 | 10.8495 | 10.6095 | 9.5158 | 8.5568 | 7.6737 | 12.9611 | 12.8632 | 12.6368 | 12.3695 | 12.0716 | 11.7947 | 11.5284 | 11.2737 | 11.0337 | 9.9347 | 8.9705 | 8.0853
|  | HAREFIELD PRIMARY | EE |  |  |  |  | 14.1779 | 14.1032 | 14.0211 | 13.9368 | 13.8474 | 13.7611 | 13.6779 | 13.5968 | 13.4547 | 12.7042 | 12.0558 | 11.4937 | 12.78 | 12.6211 | 12.4389 | 12.2337 | 12.0095 | 11.7916 | 11.5768 | 11.3684 | 11.1737 | 10.3358 | 9.6158 | 8.9832 | 13.0116 | 12.9316 | 12.8442 | 12.6558 | 12.4358 | 12.2179 | 12.0021 | 11.7926 | 11.5979 | 10.7516 | 10.0253 | 9.3895
|  | HAREFIELD PRIMARY | HT |  |  |  |  | 14.1316 | 14.0411 | 13.9463 | 13.8474 | 13.7432 | 13.6337 | 13.4053 | 13.1779 | 12.9642 | 11.9811 | 11.1221 | 10.3389 | 12.6611 | 12.4505 | 12.2126 | 11.9421 | 11.6463 | 11.3684 | 11.1032 | 10.8495 | 10.6095 | 9.5158 | 8.5568 | 7.6737 | 12.9611 | 12.8632 | 12.6368 | 12.3695 | 12.0716 | 11.7947 | 11.5284 | 11.2737 | 11.0337 | 9.9347 | 8.9705 | 8.0853
|  | HAREFIELD PRIMARY | HE |  |  |  |  | 14.2484 | 14.1947 | 14.1337 | 14.0684 | 13.9979 | 13.9316 | 13.8663 | 13.8074 | 13.7558 | 13.3568 | 12.8989 | 3.1368 | 12.8632 | 12.8063 | 12.6916 | 12.5295 | 12.3474 | 12.1695 | 11.9968 | 11.8295 | 11.6789 | 11.0421 | 10.5221 | 10.0642 | 13.0874 | 13.0295 | 12.9642 | 12.8937 | 12.7663 | 12.5947 | 12.4232 | 12.2558 | 12.1042 | 11.4642 | 10.9421 | 10.4832
|  | HAREFIELD PRIMARY | CF |  |  |  |  | 14.2968 | 14.2684 | 14.2379 | 14.2063 | 14.1737 | 14.14 | 14.1063 | 14.0737 | 14.0411 | 13.8937 | 13.8168 | 13.5684 | 12.9137 | 12.8832 | 12.8505 | 12.8105 | 12.7253 | 12.6358 | 12.5442 | 12.4505 | 12.3558 | 11.9053 | 11.56 | 11.2568 | 13.1379 | 13.1074 | 13.0747 | 13.04 | 13.0042 | 12.9674 | 12.9305 | 12.8695 | 12.7779 | 12.3305 | 11.9842 | 11.68
NURSLING GSP | WINCHESTER BSP | HARESTOCK PRIMARY | MINIMUM HEADROOM | SU 45908 31300 | NO | YES | 0.070526 | 35.6541 | 35.5488 | 35.4383 | 35.3256 | 34.7656 | 33.4898 | 32.2298 | 30.9751 | 30.2098 | 26.2204 | 22.4698 | -18.5217 | 31.1109 | 30.8867 | 30.4962 | 30.0509 | 28.8404 | 27.4667 | 26.1025 | 24.7456 | 23.9446 | 19.753 | 15.7825 | 12.3867 | 32.0214 | 31.9162 | 31.6825 | 31.2214 | 29.8677 | 28.4772 | 27.0709 | 25.6656 | 24.8351 | 20.4519 | 16.3109 | 12.853
|  | HARESTOCK PRIMARY | EE |  |  |  |  | 37.6741 | 37.3741 | 37.0572 | 36.8562 | 35.6941 | 34.5288 | 33.3846 | 32.2235 | 31.5456 | 28.0151 | 24.6783 | 22.1972 | 33.8351 | 33.2214 | 32.2056 | 31.2909 | 30.0088 | 28.7341 | 27.4825 | 26.2141 | 25.5109 | 21.8498 | 18.4077 | 15.6909 | 34.4288 | 34.1288 | 33.1509 | 32.193 | 30.8972 | 29.5993 | 28.3246 | 27.0309 | 26.2993 | 22.4509 | 18.7941 | 16.0077
|  | HARESTOCK PRIMARY | HT |  |  |  |  | 37.4541 | 37.0888 | 36.7025 | 36.0456 | 34.7656 | 33.4898 | 32.2298 | 30.9751 | 30.2098 | 26.2204 | 22.4698 | 19.3856 | 33.373 | 32.6214 | 31.4688 | 30.2204 | 28.8404 | 27.4667 | 26.1025 | 24.7456 | 23.9446 | 19.753 | 15.7825 | 12.3867 | 34.2088 | 33.5519 | 32.4319 | 31.2214 | 29.8677 | 28.4772 | 27.0709 | 25.6656 | 24.8351 | 20.4519 | 16.3109 | 12.853
|  | HARESTOCK PRIMARY | HE |  |  |  |  | 37.9625 | 37.7583 | 37.533 | 37.9625 | 36.9614 | 35.9877 | 35.0341 | 34.0762 | 33.6046 | 31.1993 | 29.1162 | -18.5217 | 34.3383 | 34.0319 | 33.2025 | 32.4856 | 31.3741 | 30.2919 | 29.2319 | 28.1646 | 27.6646 | 25.0804 | 22.8014 | 20.7456 | 34.7172 | 34.513 | 34.1288 | 33.393 | 32.2709 | 31.1783 | 30.1077 | 29.0267 | 28.5162 | 25.8551 | 23.5141 | 21.4014
|  | HARESTOCK PRIMARY | CF |  |  |  |  | 35.6541 | 35.5488 | 35.4383 | 35.3256 | 35.1888 | 37.5519 | 37.4162 | 37.2825 | 37.0288 | 35.4435 | 34.0962 | 32.9025 | 31.1109 | 30.8867 | 30.4962 | 30.0509 | 29.553 | 32.6688 | 32.1172 | 31.5425 | 31.2414 | 29.5446 | 28.0919 | 26.8046 | 32.0214 | 31.9162 | 31.6825 | 31.2519 | 30.7646 | 33.6098 | 33.0719 | 32.5119 | 32.2162 | 30.5435 | 29.0562 | 27.7056
EALING GSP | EALING BSP | HARVARD LANE PRIMARY | MINIMUM HEADROOM | TQ 20021 78030 | NO | YES | 0 | 34.6958 | 34.4221 | 85.1316 | 84.8253 | 84.5074 | 84.0484 | 83.2768 | 82.8053 | 82.3568 | 80.04 | 76.9516 | 35.7568 | 27.06 | 26.1568 | 76.1232 | 74.9579 | 73.9 | 72.9179 | 72.0579 | 71.5484 | 71.0632 | 68.5116 | 64.7905 | 61.9168 | 28.9579 | 28.3263 | 78.2905 | 77.1263 | 76.0705 | 75.0895 | 74.2305 | 73.7221 | 73.2368 | 70.6884 | 66.9232 | 64.0537
|  | HARVARD LANE PRIMARY | EE |  |  |  |  | 34.8537 | 34.6274 | 85.3863 | 85.1295 | 84.8611 | 84.6 | 84.3463 | 83.9884 | 83.6011 | 82.4389 | 80.5684 | 78.7484 | 27.5042 | 26.9063 | 77.2284 | 76.3926 | 75.4337 | 74.6084 | 73.7589 | 72.8621 | 72.4442 | 71.44 | 69.3389 | 67.2684 | 29.1158 | 28.8895 | 79.3958 | 78.5589 | 77.6011 | 76.7768 | 75.9284 | 75.0337 | 74.6158 | 73.6611 | 71.5621 | 69.4958
|  | HARVARD LANE PRIMARY | HT |  |  |  |  | 34.6958 | 34.4221 | 85.1316 | 84.8253 | 84.5074 | 84.0484 | 83.2768 | 82.8053 | 82.3568 | 80.04 | 76.9516 | 74.4189 | 27.06 | 26.1568 | 76.1232 | 74.9579 | 73.9 | 72.9179 | 72.0579 | 71.5484 | 71.0632 | 68.5116 | 64.7905 | 61.9168 | 28.9579 | 28.3263 | 78.2905 | 77.1263 | 76.0705 | 75.0895 | 74.2305 | 73.7221 | 73.2368 | 70.6884 | 66.9232 | 64.0537
|  | HARVARD LANE PRIMARY | HE |  |  |  |  | 35.0147 | 34.8337 | 85.6326 | 85.4168 | 85.1863 | 84.9663 | 84.7589 | 84.5653 | 84.3979 | 83.7716 | 81.7337 | 35.7568 | 27.8421 | 27.4305 | 77.8695 | 77.1568 | 76.2968 | 75.5832 | 74.8337 | 74.1011 | 73.8242 | 72.6568 | 69.9821 | 68.5558 | 29.2768 | 29.0958 | 79.8947 | 79.3253 | 78.4642 | 77.7516 | 77.0021 | 76.2705 | 75.9937 | 74.8284 | 72.0874 | 70.66
|  | HARVARD LANE PRIMARY | CF |  |  |  |  | 35.1263 | 35.0116 | 85.8926 | 85.7695 | 85.6411 | 85.5105 | 85.3832 | 85.2558 | 85.1295 | 84.5632 | 84.2779 | 83.4558 | 27.9621 | 27.8421 | 78.7168 | 78.4474 | 78.1537 | 77.8516 | 77.5505 | 77.0768 | 76.5695 | 74.2453 | 73.2063 | 72.2284 | 29.3884 | 29.2737 | 80.1547 | 80.0316 | 79.9032 | 79.7726 | 79.6453 | 79.2453 | 78.7358 | 76.4147 | 75.3779 | 74.4011
COWLEY GSP |  | HARWELL PRIMARY | MINIMUM HEADROOM | SU 47395 86969 | NO | YES | 0.21053 | 39.4682 | 39.4535 | 38.9514 | 38.9461 | 38.9419 | 39.4103 | 39.3977 | 39.3851 | 39.3745 | 39.4345 | 40.6029 | 30.7693 | 36.6693 | 36.6545 | 36.0314 | 36.0261 | 36.0219 | 36.6114 | 36.5987 | 36.5861 | 36.5756 | 36.6356 | 38.1156 | 38.0861 | 37.1472 | 37.1324 | 36.5745 | 36.5693 | 36.5651 | 37.0893 | 37.0766 | 37.064 | 37.0535 | 37.1135 | 38.4303 | 38.4008
|  | HARWELL PRIMARY | EE |  |  |  |  | 39.4766 | 39.4651 | 39.4514 | 39.4377 | 39.424 | 39.4103 | 39.3977 | 39.3851 | 39.3745 | 40.6745 | 40.6482 | 40.6293 | 36.6777 | 36.6661 | 36.6524 | 36.6387 | 36.6251 | 36.6114 | 36.5987 | 36.5861 | 36.5756 | 38.1872 | 38.1608 | 38.1419 | 37.1556 | 37.144 | 37.1303 | 37.1166 | 37.1029 | 37.0893 | 37.0766 | 37.064 | 37.0535 | 38.5019 | 38.4756 | 38.4566
|  | HARWELL PRIMARY | HT |  |  |  |  | 39.4682 | 39.4535 | 39.4377 | 39.4219 | 40.7451 | 40.7282 | 40.7145 | 40.7008 | 40.6882 | 40.6387 | 40.6029 | 40.5735 | 36.6693 | 36.6545 | 36.6387 | 36.6229 | 38.2577 | 38.2408 | 38.2272 | 38.2135 | 38.2008 | 38.1514 | 38.1156 | 38.0861 | 37.1472 | 37.1324 | 37.1166 | 37.1008 | 38.5724 | 38.5556 | 38.5419 | 38.5282 | 38.5156 | 38.4661 | 38.4303 | 38.4008
|  | HARWELL PRIMARY | HE |  |  |  |  | 39.4882 | 39.4798 | 39.4703 | 39.4608 | 39.4493 | 39.4387 | 39.4293 | 39.4198 | 39.4124 | 40.7251 | 40.7103 | 30.7693 | 36.6893 | 36.6808 | 36.6714 | 36.6619 | 36.6503 | 36.6398 | 36.6303 | 36.6208 | 36.6135 | 38.2377 | 38.2229 | 38.2135 | 37.1672 | 37.1587 | 37.1493 | 37.1398 | 37.1282 | 37.1177 | 37.1082 | 37.0987 | 37.0914 | 38.5524 | 38.5377 | 38.5282
|  | HARWELL PRIMARY | CF |  |  |  |  | 40.9787 | 40.9693 | 38.9514 | 38.9461 | 38.9419 | 39.4724 | 39.4672 | 39.4619 | 39.4566 | 39.4345 | 40.7629 | 40.7566 | 38.8177 | 38.8051 | 36.0314 | 36.0261 | 36.0219 | 36.6735 | 36.6682 | 36.6629 | 36.6577 | 36.6356 | 38.2756 | 38.2693 | 39.3819 | 39.3661 | 36.5745 | 36.5693 | 36.5651 | 37.1514 | 37.1461 | 37.1408 | 37.1356 | 37.1135 | 38.5903 | 38.584
FLEET-BRAMLEY GSP | FERNHURST BSP | HASLEMERE PRIMARY | MINIMUM HEADROOM | SU 89300 31710 | NO | YES | 0.11579 | 25.0258 | 24.6689 | 24.2879 | 23.8963 | 23.4858 | 23.0742 | 22.71 | 22.2195 | 21.5784 | 18.5868 | 15.6584 | -11.0226 | 20.0132 | 19.3363 | 18.6089 | 17.8637 | 17.05 | 16.1132 | 15.4458 | 14.7437 | 14.0468 | 10.7732 | 7.5237 | 4.5826 | 20.9437 | 20.2679 | 19.5395 | 18.7932 | 17.9784 | 17.0395 | 16.3689 | 15.6647 | 14.9658 | 11.6732 | 8.4037 | 5.4521
|  | HASLEMERE PRIMARY | EE |  |  |  |  | 25.2447 | 24.9511 | 24.6405 | 24.3184 | 23.9774 | 23.6437 | 23.3289 | 23.0226 | 22.7489 | 20.6837 | 18.3574 | 16.3437 | 20.5226 | 19.9532 | 19.3668 | 18.7689 | 18.1311 | 17.4247 | 16.8437 | 16.2437 | 15.6626 | 13.0889 | 10.5153 | 8.2468 | 21.4532 | 20.8837 | 20.2963 | 19.6995 | 19.0595 | 18.35 | 17.7658 | 17.1626 | 16.5774 | 13.9784 | 11.3763 | 9.0995
|  | HASLEMERE PRIMARY | HT |  |  |  |  | 25.0258 | 24.6689 | 24.2879 | 23.8963 | 23.4858 | 23.0742 | 22.71 | 22.2195 | 21.5784 | 18.5868 | 15.6584 | 13.0374 | 20.0132 | 19.3363 | 18.6089 | 17.8637 | 17.05 | 16.1132 | 15.4458 | 14.7437 | 14.0468 | 10.7732 | 7.5237 | 4.5826 | 20.9437 | 20.2679 | 19.5395 | 18.7932 | 17.9784 | 17.0395 | 16.3689 | 15.6647 | 14.9658 | 11.6732 | 8.4037 | 5.4521
|  | HASLEMERE PRIMARY | HE |  |  |  |  | 25.5237 | 25.3195 | 25.0921 | 24.8479 | 24.5826 | 24.3289 | 24.0879 | 23.8626 | 23.6679 | 22.9963 | 21.5816 | -11.0226 | 21.0921 | 20.7532 | 20.3489 | 19.9237 | 19.4458 | 18.9026 | 18.4721 | 18.0405 | 17.6132 | 15.8132 | 13.9732 | 12.35 | 21.9226 | 21.6879 | 21.2805 | 20.8542 | 20.3742 | 19.8321 | 19.3984 | 18.9647 | 18.5363 | 16.7258 | 14.8784 | 13.2468
|  | HASLEMERE PRIMARY | CF |  |  |  |  | 25.7142 | 25.6068 | 25.4953 | 25.3795 | 25.2584 | 25.1332 | 25.01 | 24.89 | 24.7689 | 24.2268 | 23.9468 | 23.5574 | 21.3016 | 21.1889 | 21.0711 | 20.9489 | 20.7658 | 20.5489 | 20.3089 | 20.0479 | 19.7721 | 18.3921 | 17.1532 | 16.0774 | 22.1332 | 22.0195 | 21.9026 | 21.7805 | 21.6532 | 21.4805 | 21.2384 | 20.9763 | 20.6995 | 19.3163 | 18.0721 | 16.9911
FLEET-BRAMLEY GSP | FERNHURST BSP | HASLINGBOURNE PRIMARY | MINIMUM HEADROOM | SU 98188 20276 | NO | YES | 0 | 12.0326 | 11.9011 | 11.7632 | 11.6211 | 11.4747 | 11.2337 | 11.0253 | 10.7926 | 10.5453 | 9.4368 | 8.2084 | -0.91474 | 9.9632 | 9.7158 | 9.4211 | 9.1368 | 8.8453 | 8.5842 | 8.3621 | 8.1095 | 7.8389 | 6.6137 | 5.2284 | 3.9621 | 10.4168 | 10.18 | 9.8968 | 9.6168 | 9.3242 | 9.0632 | 8.8421 | 8.5884 | 8.3168 | 7.0916 | 5.7042 | 4.4379
|  | HASLINGBOURNE PRIMARY | EE |  |  |  |  | 12.1084 | 12.0021 | 11.8884 | 11.7705 | 11.6495 | 11.5305 | 11.4189 | 11.3126 | 11.12 | 10.2716 | 9.2905 | 8.4137 | 10.1211 | 9.9358 | 9.7074 | 9.4905 | 9.2674 | 9.0726 | 8.8884 | 8.6884 | 8.4726 | 7.5389 | 6.4305 | 5.4326 | 10.5474 | 10.3884 | 10.1684 | 9.9579 | 9.7432 | 9.5495 | 9.3653 | 9.1642 | 8.9484 | 8.0116 | 6.9 | 5.9
|  | HASLINGBOURNE PRIMARY | HT |  |  |  |  | 12.0326 | 11.9011 | 11.7632 | 11.6211 | 11.4747 | 11.2337 | 11.0253 | 10.7926 | 10.5453 | 9.4368 | 8.2084 | 7.0926 | 9.9632 | 9.7158 | 9.4211 | 9.1368 | 8.8453 | 8.5842 | 8.3621 | 8.1095 | 7.8389 | 6.6137 | 5.2284 | 3.9621 | 10.4168 | 10.18 | 9.8968 | 9.6168 | 9.3242 | 9.0632 | 8.8421 | 8.5884 | 8.3168 | 7.0916 | 5.7042 | 4.4379
|  | HASLINGBOURNE PRIMARY | HE |  |  |  |  | 12.2126 | 12.1379 | 12.0558 | 11.9674 | 11.8726 | 11.7821 | 11.6968 | 11.6179 | 11.5495 | 11.1705 | 10.4158 | -0.91474 | 10.3305 | 10.2116 | 10.06 | 9.9147 | 9.7495 | 9.6126 | 9.4853 | 9.3411 | 9.1811 | 8.5105 | 7.6474 | 6.8842 | 10.6579 | 10.5811 | 10.4937 | 10.3695 | 10.2084 | 10.0758 | 9.9505 | 9.8116 | 9.6579 | 8.9916 | 8.1284 | 7.3642
|  | HASLINGBOURNE PRIMARY | CF |  |  |  |  | 12.2842 | 12.2453 | 12.2053 | 12.1642 | 12.1211 | 12.0779 | 12.0347 | 11.9926 | 11.9495 | 11.76 | 11.4674 | 11.0453 | 10.4495 | 10.38 | 10.3011 | 10.2211 | 10.1358 | 10.0611 | 9.9863 | 9.9084 | 9.8126 | 9.3558 | 8.7989 | 8.3116 | 10.7326 | 10.6916 | 10.6495 | 10.6053 | 10.56 | 10.5147 | 10.44 | 10.3653 | 10.2726 | 9.8358 | 9.28 | 8.7926
MELKSHAM GSP | FROME BSP | HAWKERIDGE PRIMARY | MINIMUM HEADROOM | ST 86422 53026 | NO | YES | 8 | 11.0347 | 10.9632 | 10.8916 | 10.8221 | 10.7526 | 10.6842 | 10.62 | 10.5568 | 10.4947 | 10.1937 | 8.2505 | -7.0768 | 8.9042 | 8.8221 | 8.74 | 8.6611 | 8.5821 | 8.5042 | 8.4305 | 8.3589 | 8.2874 | 7.9411 | 5.6568 | 5.5305 | 9.2863 | 9.2042 | 9.1221 | 9.0432 | 8.9642 | 8.8863 | 8.8126 | 8.74 | 8.6684 | 8.3232 | 6.0379 | 5.9116
|  | HAWKERIDGE PRIMARY | EE |  |  |  |  | 11.0874 | 11.0316 | 10.9758 | 10.9221 | 10.8684 | 10.8158 | 10.7642 | 10.7147 | 10.6653 | 10.4358 | 8.2505 | 8.14 | 8.9642 | 8.9011 | 8.8379 | 8.7758 | 8.7147 | 8.6547 | 8.5958 | 8.5389 | 8.4832 | 8.22 | 5.6568 | 5.5305 | 9.3463 | 9.2832 | 9.22 | 9.1579 | 9.0968 | 9.0368 | 8.9779 | 8.9211 | 8.8653 | 8.6011 | 6.0379 | 5.9116
|  | HAWKERIDGE PRIMARY | HT |  |  |  |  | 11.0347 | 10.9632 | 10.8916 | 10.8221 | 10.7526 | 10.6842 | 10.62 | 10.5568 | 10.4947 | 10.1937 | 9.9074 | 9.6295 | 8.9042 | 8.8221 | 8.74 | 8.6611 | 8.5821 | 8.5042 | 8.4305 | 8.3589 | 8.2874 | 7.9411 | 7.6095 | 7.2874 | 9.2863 | 9.2042 | 9.1221 | 9.0432 | 8.9642 | 8.8863 | 8.8126 | 8.74 | 8.6684 | 8.3232 | 7.9916 | 7.6695
|  | HAWKERIDGE PRIMARY | HE |  |  |  |  | 11.1253 | 11.1147 | 11.0895 | 11.0558 | 11.0232 | 10.9905 | 10.9579 | 10.9274 | 10.8989 | 10.7663 | 8.3789 | -7.0768 | 9.0074 | 8.9958 | 8.9684 | 8.9295 | 8.8926 | 8.8558 | 8.8189 | 8.7842 | 8.7516 | 8.6 | 5.7989 | 5.6947 | 9.3895 | 9.3779 | 9.3505 | 9.3116 | 9.2747 | 9.2379 | 9.2011 | 9.1663 | 9.1337 | 8.9811 | 6.18 | 6.0758
|  | HAWKERIDGE PRIMARY | CF |  |  |  |  | 11.1368 | 11.36 | 11.3568 | 11.3537 | 11.3463 | 11.3389 | 11.3326 | 11.3253 | 11.3189 | 11.2874 | 11.2653 | 11.2463 | 9.0189 | 9.0663 | 9.0611 | 9.0547 | 9.0337 | 9.0074 | 8.9832 | 8.9579 | 8.9337 | 8.8126 | 8.7053 | 8.6042 | 9.4011 | 9.3947 | 9.3895 | 9.3832 | 9.3621 | 9.3368 | 9.3126 | 9.2874 | 9.2642 | 9.1463 | 9.04 | 8.9411
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | HAWLEY PRIMARY | MINIMUM HEADROOM | SU 85973 57691 | NO | YES | 0 | 32.3663 | 32.0779 | 31.7705 | 31.4516 | 31.1232 | 30.7926 | 30.3832 | 29.9421 | 29.5316 | 27.6947 | 25.7874 | 6.2832 | 29.5537 | 28.9916 | 28.4105 | 27.8389 | 27.2737 | 26.7116 | 26.2011 | 25.7242 | 25.2789 | 23.2705 | 21.1253 | 19.1611 | 30.3147 | 29.7568 | 29.1768 | 28.6053 | 28.0389 | 27.4768 | 26.9674 | 26.4895 | 26.0453 | 24.0347 | 21.8905 | 19.9253
|  | HAWLEY PRIMARY | EE |  |  |  |  | 32.5326 | 32.2937 | 32.0379 | 31.7705 | 31.4937 | 31.2263 | 30.9726 | 30.7263 | 30.5084 | 29.1095 | 27.6526 | 26.3589 | 29.9253 | 29.4716 | 29.0011 | 28.5358 | 28.0684 | 27.6168 | 27.1895 | 26.7758 | 26.4021 | 24.8284 | 23.1842 | 21.7074 | 30.5832 | 30.2337 | 29.7674 | 29.3011 | 28.8337 | 28.3832 | 27.9547 | 27.5411 | 27.1674 | 25.5937 | 23.9495 | 22.4716
|  | HAWLEY PRIMARY | HT |  |  |  |  | 32.3663 | 32.0779 | 31.7705 | 31.4516 | 31.1232 | 30.7926 | 30.3832 | 29.9421 | 29.5316 | 27.6947 | 25.7874 | 24.0568 | 29.5537 | 28.9916 | 28.4105 | 27.8389 | 27.2737 | 26.7116 | 26.2011 | 25.7242 | 25.2789 | 23.2705 | 21.1253 | 19.1611 | 30.3147 | 29.7568 | 29.1768 | 28.6053 | 28.0389 | 27.4768 | 26.9674 | 26.4895 | 26.0453 | 24.0347 | 21.8905 | 19.9253
|  | HAWLEY PRIMARY | HE |  |  |  |  | 32.7516 | 32.5768 | 32.3853 | 32.1789 | 31.9589 | 31.7474 | 31.5484 | 31.3642 | 31.2042 | 30.6632 | 30.1368 | 6.2832 | 30.3853 | 30.1158 | 29.7905 | 29.4642 | 29.1242 | 28.7989 | 28.4958 | 28.2105 | 27.9632 | 27.0011 | 25.9358 | 25.0158 | 30.8189 | 30.6358 | 30.4368 | 30.2179 | 29.8874 | 29.5653 | 29.2611 | 28.9768 | 28.7284 | 27.7663 | 26.7011 | 25.7811
|  | HAWLEY PRIMARY | CF |  |  |  |  | 32.9053 | 32.8116 | 32.7147 | 32.6147 | 32.5095 | 32.4032 | 32.3 | 32.1968 | 32.0926 | 31.6326 | 31.4021 | 31.0821 | 30.5547 | 30.4495 | 30.3242 | 30.1379 | 29.9432 | 29.7495 | 29.5589 | 29.3705 | 29.1832 | 28.3232 | 27.5389 | 26.8853 | 30.9789 | 30.88 | 30.7779 | 30.6737 | 30.5632 | 30.4516 | 30.3147 | 30.1326 | 29.9495 | 29.0884 | 28.3042 | 27.6505
NORTH HYDE GSP |  | HAYES PRIMARY | MINIMUM HEADROOM | TQ 09519 79541 | NO | NO | 0.99474 | 72.4624 | 71.9982 | 71.5045 | 70.9908 | 70.4592 | 69.4413 | 67.9203 | 66.4487 | 65.0624 | 58.6645 | 53.0666 | -8.6166 | 60.6392 | 59.2129 | 57.4182 | 55.7024 | 53.7697 | 51.9676 | 50.2634 | 48.6118 | 47.0539 | 39.8308 | 33.4782 | 27.5171 | 63.6013 | 62.1624 | 60.3676 | 58.6518 | 56.7182 | 54.9161 | 53.2118 | 51.5603 | 50.0013 | 42.7771 | 36.4224 | 30.4603
|  | HAYES PRIMARY | EE |  |  |  |  | 72.7287 | 72.3445 | 71.9361 | 71.5055 | 71.0571 | 70.6234 | 70.2087 | 69.4855 | 68.3813 | 63.4834 | 59.3182 | 55.4729 | 61.2918 | 60.1855 | 58.7971 | 57.5287 | 56.1097 | 54.7118 | 53.3655 | 52.0392 | 50.8055 | 45.2866 | 40.5571 | 36.1624 | 64.1076 | 63.1413 | 61.7466 | 60.4782 | 59.0592 | 57.6613 | 56.315 | 54.9876 | 53.7539 | 48.2329 | 43.5024 | 39.1066
|  | HAYES PRIMARY | HT |  |  |  |  | 72.4624 | 71.9982 | 71.5045 | 70.9908 | 70.4592 | 69.4413 | 67.9203 | 66.4487 | 65.0624 | 58.6645 | 53.0666 | 47.8392 | 60.6392 | 59.2129 | 57.4182 | 55.7024 | 53.7697 | 51.9676 | 50.2634 | 48.6118 | 47.0539 | 39.8308 | 33.4782 | 27.5171 | 63.6013 | 62.1624 | 60.3676 | 58.6518 | 56.7182 | 54.9161 | 53.2118 | 51.5603 | 50.0013 | 42.7771 | 36.4224 | 30.4603
|  | HAYES PRIMARY | HE |  |  |  |  | 73.0508 | 72.7624 | 72.4424 | 72.0982 | 71.7318 | 71.3813 | 71.0508 | 70.7424 | 70.4761 | 66.6382 | 63.3676 | -8.6166 | 61.9929 | 61.1708 | 60.0108 | 58.9571 | 57.7361 | 56.5371 | 55.3876 | 54.2697 | 53.2392 | 48.7382 | 44.9929 | 41.5592 | 64.4297 | 64.1371 | 62.9624 | 61.9066 | 60.6855 | 59.4866 | 58.3371 | 57.2182 | 56.1876 | 51.6855 | 47.9392 | 44.5045
|  | HAYES PRIMARY | CF |  |  |  |  | 73.2929 | 73.1329 | 72.9645 | 72.7918 | 72.6129 | 72.4308 | 72.2508 | 72.0739 | 71.8961 | 71.1045 | 70.4834 | 68.6297 | 62.7455 | 62.3561 | 61.8866 | 61.4434 | 60.8982 | 60.3245 | 59.735 | 59.1161 | 58.4897 | 55.455 | 53.0539 | 50.9171 | 64.6718 | 64.5118 | 64.3434 | 64.1708 | 63.8624 | 63.2813 | 62.6855 | 62.0655 | 61.4403 | 58.4034 | 56.0024 | 53.8655
COWLEY GSP | HEADINGTON BSP | HEADINGTON PRIMARY | MINIMUM HEADROOM | SP 54440 08085 | NO | YES | 0 | 42.0777 | 41.7714 | 41.4472 | 41.1082 | 40.7451 | 38.4451 | 37.8693 | 37.3556 | 36.8777 | 34.704 | 32.8429 | 8.6345 | 36.6429 | 36.0651 | 35.4756 | 34.8851 | 34.2914 | 30.8535 | 30.2387 | 29.6935 | 29.1872 | 26.8819 | 24.9114 | 23.3229 | 38.0651 | 37.4872 | 36.8966 | 36.3072 | 35.7082 | 32.264 | 31.644 | 31.0914 | 30.5798 | 28.2314 | 26.2114 | 24.4966
|  | HEADINGTON PRIMARY | EE |  |  |  |  | 42.2524 | 41.9966 | 43.0566 | 42.5998 | 42.0756 | 39.2377 | 38.7419 | 38.2861 | 37.8745 | 37.9398 | 36.4251 | 35.2714 | 37.5093 | 36.7029 | 36.0408 | 35.4377 | 34.8829 | 31.6114 | 31.0882 | 30.6124 | 30.1861 | 31.2398 | 29.6798 | 28.4345 | 38.9303 | 38.124 | 37.4629 | 36.8587 | 36.2987 | 33.0187 | 32.4882 | 32.0061 | 31.5703 | 32.9451 | 31.3156 | 30.0503
|  | HEADINGTON PRIMARY | HT |  |  |  |  | 42.0777 | 41.7714 | 41.4472 | 41.1082 | 40.7451 | 38.4451 | 37.8693 | 37.3556 | 36.8777 | 34.704 | 32.8429 | 31.2829 | 36.6429 | 36.0651 | 35.4756 | 34.8851 | 34.2914 | 30.8535 | 30.2387 | 29.6935 | 29.1872 | 26.8819 | 24.9114 | 23.3229 | 38.0651 | 37.4872 | 36.8966 | 36.3072 | 35.7082 | 32.264 | 31.644 | 31.0914 | 30.5798 | 28.2314 | 26.2114 | 24.4966
|  | HEADINGTON PRIMARY | HE |  |  |  |  | 42.4787 | 42.2945 | 42.0903 | 41.8703 | 43.0103 | 40.3135 | 39.9629 | 39.6608 | 39.3851 | 37.6882 | 36.9451 | 8.6345 | 38.0135 | 37.3566 | 36.8608 | 36.4135 | 36.0082 | 32.8735 | 32.5029 | 32.1872 | 31.8987 | 29.8693 | 29.0882 | 28.4535 | 39.4145 | 38.7798 | 38.2829 | 37.8356 | 37.4272 | 34.2882 | 33.9135 | 33.5935 | 33.3019 | 31.0861 | 30.284 | 29.6303
|  | HEADINGTON PRIMARY | CF |  |  |  |  | 42.6419 | 42.5408 | 42.4356 | 42.3282 | 42.2093 | 42.0893 | 41.9714 | 41.8556 | 41.7387 | 41.2145 | 40.8914 | 40.4103 | 39.0503 | 38.864 | 38.6714 | 38.4766 | 38.2745 | 36.8966 | 36.6408 | 36.2935 | 35.9303 | 34.3187 | 33.6566 | 33.1335 | 40.0514 | 39.9461 | 39.8356 | 39.7229 | 39.5998 | 38.3166 | 38.0566 | 37.7082 | 37.344 | 35.724 | 35.0524 | 34.5156
NURSLING GSP | VELMORE BSP | HEDGE END PRIMARY | MINIMUM HEADROOM | SU 49035 15685 | NO | YES | 0 | 31.8737 | 31.1811 | 30.2579 | 29.5242 | 28.5305 | 27.7337 | 26.8789 | 26.2126 | 25.8432 | 24.1611 | 22.6642 | 13.6011 | 29.2463 | 28.4611 | 27.4084 | 26.5779 | 25.4453 | 24.5411 | 23.5621 | 22.8032 | 22.3884 | 20.5179 | 18.8232 | 17.2758 | 29.7747 | 28.9684 | 27.8874 | 27.0358 | 25.8705 | 24.9432 | 23.9526 | 23.1926 | 22.78 | 20.9116 | 19.2158 | 17.6684
|  | HEDGE END PRIMARY | EE |  |  |  |  | 32.0442 | 31.4032 | 30.5316 | 29.8453 | 28.9432 | 28.2274 | 27.5084 | 26.8305 | 26.5179 | 25.1432 | 23.9379 | 22.86 | 29.4316 | 28.7021 | 27.7042 | 26.9242 | 25.8937 | 25.0789 | 24.26 | 23.4832 | 23.1337 | 21.6095 | 20.2432 | 19.0084 | 29.9621 | 29.2126 | 28.1884 | 27.3874 | 26.3274 | 25.4926 | 24.6505 | 23.8726 | 23.5242 | 22 | 20.6295 | 19.3947
|  | HEDGE END PRIMARY | HT |  |  |  |  | 31.8737 | 31.1811 | 30.2579 | 29.5242 | 28.5305 | 27.7337 | 26.8789 | 26.2126 | 25.8432 | 24.1611 | 22.6642 | 21.3042 | 29.2463 | 28.4611 | 27.4084 | 26.5779 | 25.4453 | 24.5411 | 23.5621 | 22.8032 | 22.3884 | 20.5179 | 18.8232 | 17.2758 | 29.7747 | 28.9684 | 27.8874 | 27.0358 | 25.8705 | 24.9432 | 23.9526 | 23.1926 | 22.78 | 20.9116 | 19.2158 | 17.6684
|  | HEDGE END PRIMARY | HE |  |  |  |  | 32.2737 | 31.7021 | 30.8989 | 30.2789 | 29.4358 | 28.7758 | 28.0926 | 27.4947 | 27.2432 | 26.0663 | 25.1137 | 13.6011 | 29.6789 | 29.0253 | 28.1021 | 27.3926 | 26.4253 | 25.6726 | 24.8895 | 24.2021 | 23.92 | 22.5642 | 21.4705 | 20.4832 | 30.2137 | 29.5421 | 28.5926 | 27.8642 | 26.8695 | 26.0947 | 25.2895 | 24.5926 | 24.3105 | 22.9516 | 21.8589 | 20.8716
|  | HEDGE END PRIMARY | CF |  |  |  |  | 32.6474 | 32.3653 | 32 | 31.7232 | 31.3779 | 31.0874 | 30.8253 | 30.5547 | 30.3674 | 29.5074 | 28.9147 | 28.3958 | 30.1032 | 29.7811 | 29.3611 | 29.0453 | 28.6495 | 28.3179 | 28.02 | 27.7116 | 27.5011 | 26.5316 | 25.8579 | 25.2611 | 30.6484 | 30.3179 | 29.8863 | 29.5621 | 29.1558 | 28.8147 | 28.5074 | 28.1905 | 27.9747 | 26.9821 | 26.2884 | 25.6758
BRAMLEY (BASI) GSP | READING BSP | HENLEY PRIMARY | MINIMUM HEADROOM | SU 76070 82422 | NO | YES | 0 | 29.1792 | 28.8845 | 28.5739 | 28.2508 | 27.9087 | 27.5666 | 27.2613 | 26.9824 | 26.7255 | 24.9171 | 23.115 | -5.2113 | 24.2908 | 23.7361 | 22.9518 | 22.1129 | 21.5139 | 20.9192 | 20.3571 | 19.8266 | 19.3318 | 17.1192 | 15.075 | 13.0434 | 25.0613 | 24.7508 | 24.0897 | 23.2329 | 22.6245 | 22.0203 | 21.4529 | 20.9203 | 20.4213 | 18.1866 | 16.1171 | 14.075
|  | HENLEY PRIMARY | EE |  |  |  |  | 29.3518 | 29.1108 | 28.8529 | 28.5834 | 28.2961 | 28.015 | 27.7487 | 27.4876 | 27.2518 | 26.2655 | 24.8561 | 23.6087 | 24.6445 | 24.2234 | 23.5508 | 22.8129 | 22.3171 | 21.8266 | 21.3508 | 20.8908 | 20.4676 | 18.6655 | 17.0897 | 15.6266 | 25.2445 | 24.9918 | 24.6845 | 23.9455 | 23.4413 | 22.9403 | 22.4561 | 21.9855 | 21.5529 | 19.7203 | 18.1076 | 16.6329
|  | HENLEY PRIMARY | HT |  |  |  |  | 29.1792 | 28.8845 | 28.5739 | 28.2508 | 27.9087 | 27.5666 | 27.2613 | 26.9824 | 26.7255 | 24.9171 | 23.115 | 21.3308 | 24.2908 | 23.7361 | 22.9518 | 22.1129 | 21.5139 | 20.9192 | 20.3571 | 19.8266 | 19.3318 | 17.1192 | 15.075 | 13.0434 | 25.0613 | 24.7508 | 24.0897 | 23.2329 | 22.6245 | 22.0203 | 21.4529 | 20.9203 | 20.4213 | 18.1866 | 16.1171 | 14.075
|  | HENLEY PRIMARY | HE |  |  |  |  | 29.5761 | 29.4055 | 29.2129 | 29.0076 | 28.7813 | 28.5655 | 28.3624 | 28.1697 | 28.0034 | 27.4224 | 27.0718 | -5.2113 | 24.8845 | 24.7066 | 24.3361 | 23.7392 | 23.3697 | 23.015 | 22.6718 | 22.3434 | 22.0518 | 20.9329 | 20.0224 | 19.1108 | 25.4866 | 25.3087 | 25.0961 | 24.8676 | 24.5087 | 24.1518 | 23.8034 | 23.4687 | 23.1718 | 22.0245 | 21.0961 | 20.175
|  | HENLEY PRIMARY | CF |  |  |  |  | 29.7276 | 29.6339 | 29.5361 | 29.4361 | 29.3276 | 29.2171 | 29.1108 | 29.0024 | 28.8961 | 28.4171 | 28.1676 | 28.0192 | 25.0413 | 24.9434 | 24.835 | 24.655 | 24.4466 | 24.2339 | 24.0234 | 23.8055 | 23.595 | 22.6339 | 21.9403 | 21.3361 | 25.6445 | 25.5455 | 25.4371 | 25.3245 | 25.2108 | 25.0939 | 24.9824 | 24.8676 | 24.7276 | 23.7592 | 23.0476 | 22.4234
AXMINSTER GSP | YEOVIL BSP | HENSTRIDGE PRIMARY | MINIMUM HEADROOM | ST 72676 19263 | NO | YES | 0 | 23.0126 | 22.5874 | 22.1358 | 21.5021 | 20.7884 | 20.3011 | 19.8337 | 19.5821 | 19.3421 | 18.1705 | 16.9937 | 8.2379 | 22.4547 | 21.9821 | 21.48 | 20.7632 | 19.9621 | 19.4274 | 18.9126 | 18.6516 | 18.4032 | 17.1863 | 15.9516 | 14.7758 | 22.6568 | 22.1895 | 21.6926 | 20.9842 | 20.1874 | 19.6526 | 19.1389 | 18.8747 | 18.62 | 17.3716 | 16.1021 | 14.92
|  | HENSTRIDGE PRIMARY | EE |  |  |  |  | 23.1937 | 22.8189 | 22.4232 | 21.8389 | 21.1737 | 20.7337 | 20.3 | 20.0716 | 19.8547 | 18.8526 | 17.8589 | 17.0442 | 22.6516 | 22.2347 | 21.7916 | 21.1284 | 20.3811 | 19.8979 | 19.4242 | 19.1905 | 18.9705 | 17.9642 | 16.9621 | 16.0758 | 22.8526 | 22.4389 | 22.0021 | 21.3463 | 20.6021 | 20.1189 | 19.6421 | 19.4021 | 19.1737 | 18.1189 | 17.0579 | 16.16
|  | HENSTRIDGE PRIMARY | HT |  |  |  |  | 23.0126 | 22.5874 | 22.1358 | 21.5021 | 20.7884 | 20.3011 | 19.8337 | 19.5821 | 19.3421 | 18.1705 | 16.9937 | 15.9211 | 22.4547 | 21.9821 | 21.48 | 20.7632 | 19.9621 | 19.4274 | 18.9126 | 18.6516 | 18.4032 | 17.1863 | 15.9516 | 14.7758 | 22.6568 | 22.1895 | 21.6926 | 20.9842 | 20.1874 | 19.6526 | 19.1389 | 18.8747 | 18.62 | 17.3716 | 16.1021 | 14.92
|  | HENSTRIDGE PRIMARY | HE |  |  |  |  | 23.4505 | 23.1274 | 22.8032 | 22.2884 | 21.6905 | 21.3263 | 20.9695 | 20.8158 | 20.68 | 20.0947 | 19.5547 | 8.2379 | 22.9326 | 22.5684 | 22.2032 | 21.6158 | 20.9379 | 20.5337 | 20.1358 | 19.9789 | 19.84 | 19.2421 | 18.6663 | 18.0526 | 23.1316 | 22.7705 | 22.4105 | 21.8295 | 21.1579 | 20.7547 | 20.3579 | 20.1979 | 20.0568 | 19.4379 | 18.8495 | 18.2263
|  | HENSTRIDGE PRIMARY | CF |  |  |  |  | 23.7379 | 23.5716 | 23.4158 | 23.1821 | 22.9221 | 22.74 | 22.5516 | 22.4579 | 22.3684 | 21.9453 | 21.5811 | 21.2158 | 23.2558 | 23.0684 | 22.8926 | 22.6263 | 22.3316 | 22.1295 | 21.9189 | 21.8211 | 21.7263 | 21.2811 | 20.8884 | 20.4895 | 23.4505 | 23.2653 | 23.0916 | 22.8284 | 22.5358 | 22.3347 | 22.1253 | 22.0263 | 21.9305 | 21.4811 | 21.0821 | 20.6758
FLEET-BRAMLEY GSP | ALTON BSP | HERRIARD PRIMARY | MINIMUM HEADROOM | SU 66770 44972 | YES | YES | 0 | 7.4032 | 7.3568 | 7.3084 | 7.2568 | 7.0558 | 6.8537 | 4.6779 | 4.5863 | 4.4895 | 3.6989 | 2.7242 | 1.9158 | 7.4147 | 7.3653 | 7.3158 | 7.2621 | 7.0558 | 6.8495 | 4.3768 | 4.3021 | 4.2242 | 3.5084 | 2.5947 | 2.2968 | 7.4074 | 7.3621 | 7.3105 | 7.2568 | 7.0379 | 6.8189 | 4.2937 | 4.2011 | 4.1042 | 3.2758 | 2.2379 | 1.8937
|  | HERRIARD PRIMARY | EE |  |  |  |  | 7.4347 | 7.3958 | 7.3547 | 7.3137 | 7.2221 | 7.1095 | 6.9947 | 6.8642 | 6.7284 | 4.8989 | 3.7158 | 3.2147 | 7.4484 | 7.4084 | 7.3663 | 7.3895 | 7.3116 | 7.2147 | 7.1189 | 7.0095 | 6.8968 | 5.0484 | 4 | 3.5221 | 7.4368 | 7.4011 | 7.3611 | 7.3421 | 7.2484 | 7.1326 | 7.0158 | 6.8832 | 6.7432 | 4.7232 | 3.4737 | 2.9337
|  | HERRIARD PRIMARY | HT |  |  |  |  | 7.4032 | 7.3568 | 7.3084 | 7.2568 | 7.0558 | 6.8537 | 4.6779 | 4.5863 | 4.4895 | 3.6989 | 2.7242 | 2.3926 | 7.4147 | 7.3653 | 7.3158 | 7.2621 | 7.0558 | 6.8495 | 4.3768 | 4.3021 | 4.2242 | 3.5084 | 2.5947 | 2.2968 | 7.4074 | 7.3621 | 7.3105 | 7.2568 | 7.0379 | 6.8189 | 4.2937 | 4.2011 | 4.1042 | 3.2758 | 2.2379 | 1.8937
|  | HERRIARD PRIMARY | HE |  |  |  |  | 7.4758 | 7.4537 | 7.4295 | 7.4042 | 7.3368 | 7.2758 | 7.2116 | 7.1495 | 7.0842 | 5.7242 | 5.1926 | 1.9158 | 7.48 | 7.4653 | 7.4432 | 7.4179 | 7.3579 | 7.3032 | 7.3179 | 7.2653 | 7.2095 | 5.7368 | 5.2105 | 4.8211 | 7.4726 | 7.4526 | 7.4295 | 7.4074 | 7.3411 | 7.28 | 7.2432 | 7.1789 | 7.1126 | 5.5695 | 4.9895 | 4.5474
|  | HERRIARD PRIMARY | CF |  |  |  |  | 7.4968 | 7.4842 | 7.4705 | 7.4568 | 7.4221 | 7.3916 | 7.3579 | 7.3263 | 7.2979 | 7.1442 | 6.8737 | 6.5832 | 7.4947 | 7.4874 | 7.4779 | 7.4695 | 7.4411 | 7.4126 | 7.3821 | 7.3547 | 7.3274 | 7.1884 | 6.9232 | 6.6389 | 7.4926 | 7.4811 | 7.4684 | 7.4558 | 7.4242 | 7.3937 | 7.3611 | 7.3295 | 7.3011 | 7.1474 | 6.8632 | 6.5505
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE PRIMARY | MINIMUM HEADROOM | SU 84733 92200 | NO | YES | 0.73684 | 36.0968 | 35.8958 | 35.6832 | 35.4642 | 35.2358 | 35.0053 | 34.8042 | 34.6189 | 34.4495 | 33.56 | 32.1989 | -4.6211 | 30.5716 | 30.2453 | 29.9105 | 29.5716 | 29.2274 | 28.9053 | 28.5674 | 28.2021 | 27.8495 | 26.2484 | 24.7495 | 23.3895 | 31.88 | 31.6716 | 31.3937 | 31.0621 | 30.7242 | 30.4063 | 30.0758 | 29.7189 | 29.3779 | 27.8221 | 26.3505 | 24.9874
|  | HIGH WYCOMBE PRIMARY | EE |  |  |  |  | 36.2147 | 36.0505 | 35.8758 | 35.6916 | 35.5021 | 35.3168 | 35.1411 | 34.9716 | 34.82 | 34.2716 | 33.5516 | 32.6263 | 30.7474 | 30.5011 | 30.2263 | 29.9442 | 29.66 | 29.4042 | 29.16 | 28.9211 | 28.6505 | 27.3811 | 26.2305 | 25.1958 | 32.0021 | 31.8326 | 31.6516 | 31.4274 | 31.1474 | 30.8958 | 30.6526 | 30.4168 | 30.1516 | 28.9158 | 27.8 | 26.7895
|  | HIGH WYCOMBE PRIMARY | HT |  |  |  |  | 36.0968 | 35.8958 | 35.6832 | 35.4642 | 35.2358 | 35.0053 | 34.8042 | 34.6189 | 34.4495 | 33.56 | 32.1989 | 30.9811 | 30.5716 | 30.2453 | 29.9105 | 29.5716 | 29.2274 | 28.9053 | 28.5674 | 28.2021 | 27.8495 | 26.2484 | 24.7495 | 23.3895 | 31.88 | 31.6716 | 31.3937 | 31.0621 | 30.7242 | 30.4063 | 30.0758 | 29.7189 | 29.3779 | 27.8221 | 26.3505 | 24.9874
|  | HIGH WYCOMBE PRIMARY | HE |  |  |  |  | 36.3684 | 36.2505 | 36.12 | 35.9811 | 35.8295 | 35.6863 | 35.5505 | 35.4242 | 35.3147 | 34.9274 | 34.7074 | -4.6211 | 30.9389 | 30.8011 | 30.6347 | 30.4316 | 30.2158 | 30.0295 | 29.8526 | 29.6874 | 29.5389 | 28.7989 | 28.0463 | 27.3884 | 32.16 | 32.04 | 31.9063 | 31.7632 | 31.6084 | 31.4621 | 31.3242 | 31.1684 | 31.02 | 30.2968 | 29.5747 | 28.9442
|  | HIGH WYCOMBE PRIMARY | CF |  |  |  |  | 36.4768 | 36.4158 | 36.3516 | 36.2853 | 36.2147 | 36.1442 | 36.0747 | 36.0074 | 35.9379 | 35.6316 | 35.4758 | 35.3884 | 31.0653 | 31.0011 | 30.9326 | 30.8537 | 30.7621 | 30.6705 | 30.5768 | 30.4695 | 30.3642 | 29.8979 | 29.3663 | 28.92 | 32.2705 | 32.2095 | 32.1442 | 32.0768 | 32.0042 | 31.9326 | 31.8611 | 31.7905 | 31.7179 | 31.3768 | 30.8653 | 30.4379
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN PRIMARY | MINIMUM HEADROOM | SU 86304 92972 | NO | YES | 0 | 66.4653 | 66.3021 | 66.1274 | 65.9432 | 65.7516 | 65.5663 | 65.6011 | 65.4116 | 65.2379 | 64.5189 | 63.5484 | 30.8179 | 60.7368 | 60.5379 | 60.3211 | 60.0905 | 59.8337 | 59.5853 | 59.6484 | 59.3042 | 58.9747 | 57.1705 | 55.4663 | 53.8789 | 61.7758 | 61.6042 | 61.4221 | 61.2305 | 61.0316 | 60.84 | 60.9916 | 60.7905 | 60.6042 | 59.0179 | 57.3126 | 55.7263
|  | HIGH WYCOMBE TOWN PRIMARY | EE |  |  |  |  | 66.4653 | 66.3021 | 66.1274 | 65.9432 | 65.7516 | 65.5663 | 65.9589 | 65.7874 | 65.6337 | 65.0642 | 64.6695 | 63.9758 | 60.7368 | 60.5379 | 60.3211 | 60.0905 | 59.8337 | 59.5853 | 60.2537 | 59.9926 | 59.7179 | 58.4116 | 57.1042 | 55.8989 | 61.7758 | 61.6042 | 61.4221 | 61.2305 | 61.0316 | 60.84 | 61.3716 | 61.1905 | 61.0274 | 60.2589 | 58.9516 | 57.7453
|  | HIGH WYCOMBE TOWN PRIMARY | HT |  |  |  |  | 66.9116 | 66.7095 | 66.4947 | 66.2716 | 66.0411 | 65.8074 | 65.6011 | 65.4116 | 65.2379 | 64.5189 | 63.5484 | 62.2 | 61.4105 | 61.1853 | 60.94 | 60.6274 | 60.3137 | 59.9874 | 59.6484 | 59.3042 | 58.9747 | 57.1705 | 55.4663 | 53.8789 | 62.3358 | 62.1337 | 61.9189 | 61.6916 | 61.4516 | 61.2084 | 60.9916 | 60.7905 | 60.6042 | 59.0179 | 57.3126 | 55.7263
|  | HIGH WYCOMBE TOWN PRIMARY | HE |  |  |  |  | 66.6032 | 66.4789 | 66.3421 | 66.1947 | 66.0379 | 65.8884 | 66.3168 | 66.1853 | 66.0716 | 65.6821 | 65.4474 | 30.8179 | 60.8989 | 60.7642 | 60.6168 | 60.46 | 60.2811 | 60.1095 | 60.7989 | 60.6526 | 60.5105 | 59.7505 | 58.9989 | 58.2053 | 61.9137 | 61.7895 | 61.6526 | 61.5032 | 61.3421 | 61.1884 | 61.7411 | 61.6095 | 61.4958 | 61.0747 | 60.8021 | 60.0526
|  | HIGH WYCOMBE TOWN PRIMARY | CF |  |  |  |  | 66.7011 | 66.6305 | 66.5568 | 66.4811 | 66.4032 | 66.3232 | 66.2442 | 66.1663 | 66.0884 | 65.7411 | 66.1368 | 66.04 | 61.0063 | 60.9274 | 60.8463 | 60.7632 | 60.6779 | 60.5905 | 60.4937 | 60.3895 | 60.2832 | 59.7095 | 60.1453 | 59.7105 | 62.0116 | 61.9411 | 61.8674 | 61.7916 | 61.7137 | 61.6316 | 61.5495 | 61.4663 | 61.3832 | 61.0084 | 61.5242 | 61.4021
IVER 66KV GSP |  | HILLINGDON PRIMARY | MINIMUM HEADROOM | TQ 07470 82827 | NO | NO | 0 | 47.4903 | 46.8251 | 46.1187 | 45.3882 | 45.4945 | 44.5945 | 43.1082 | 41.3745 | 39.7261 | 32.1819 | 25.6566 | -27.7465 | 37.0451 | 35.4524 | 33.6135 | 31.5156 | 32.1608 | 30.4924 | 28.8819 | 27.1608 | 25.324 | 16.8651 | 9.504 | 2.6819 | 39.5893 | 37.9808 | 36.1408 | 34.0429 | 34.6882 | 33.0198 | 31.2335 | 29.2798 | 27.4419 | 18.9819 | 11.6187 | 4.7956
|  | HILLINGDON PRIMARY | EE |  |  |  |  | 47.8756 | 47.3261 | 46.7408 | 46.1293 | 45.4945 | 44.5945 | 43.1587 | 41.7556 | 40.4577 | 38.1051 | 33.3029 | 28.944 | 37.9608 | 36.7829 | 35.4335 | 33.8714 | 32.1608 | 30.4924 | 28.8819 | 27.3061 | 25.8451 | 23.5293 | 18.1072 | 13.1493 | 40.5019 | 39.3251 | 37.9619 | 36.3987 | 34.6882 | 33.0198 | 31.4093 | 29.8324 | 28.3714 | 25.6472 | 20.224 | 15.2651
|  | HILLINGDON PRIMARY | HT |  |  |  |  | 47.4903 | 46.8251 | 46.1187 | 45.3882 | 46.8261 | 44.9051 | 43.1082 | 41.3745 | 39.7261 | 32.1819 | 25.6566 | 19.644 | 37.0451 | 35.4524 | 33.6135 | 31.5156 | 33.3029 | 31.1419 | 29.1135 | 27.1608 | 25.324 | 16.8651 | 9.504 | 2.6819 | 39.5893 | 37.9808 | 36.1408 | 34.0429 | 35.4229 | 33.2619 | 31.2335 | 29.2798 | 27.4419 | 18.9819 | 11.6187 | 4.7956
|  | HILLINGDON PRIMARY | HE |  |  |  |  | 48.3735 | 47.9756 | 47.5356 | 47.0619 | 46.5566 | 46.0735 | 45.6187 | 44.7261 | 43.6903 | 42.6651 | 39.0693 | -27.7465 | 39.0703 | 38.2335 | 37.2198 | 35.9935 | 34.5756 | 33.1956 | 31.8724 | 30.5882 | 29.4156 | 28.5029 | 24.4082 | 20.7251 | 41.4535 | 40.7672 | 39.7682 | 38.5219 | 37.1029 | 35.7229 | 34.3998 | 33.1156 | 31.9419 | 30.6229 | 26.5261 | 22.8419
|  | HILLINGDON PRIMARY | CF |  |  |  |  | 48.7229 | 48.5072 | 48.2819 | 48.0493 | 47.8093 | 47.564 | 47.3229 | 47.084 | 46.8451 | 45.7082 | 46.7061 | 44.6903 | 40.2566 | 39.7935 | 39.2651 | 38.6629 | 38.0103 | 37.3272 | 36.6335 | 35.9103 | 35.1735 | 31.6514 | 33.0303 | 30.6608 | 41.8535 | 41.6229 | 41.3787 | 41.124 | 40.5461 | 39.8787 | 39.1703 | 38.4387 | 37.7019 | 34.1777 | 35.1503 | 32.7808
LOVEDEAN GSP | PORTSMOUTH BSP | HILSEA PRIMARY | MINIMUM HEADROOM | SU 66394 03806 | NO | YES | 0 | 25.5203 | 25.5035 | 25.4856 | 25.4656 | 25.5245 | 25.5171 | 25.5108 | 25.5035 | 25.4971 | 41.8729 | 41.6498 | 6.9361 | 23.7066 | 23.634 | 23.5613 | 23.4877 | 23.7487 | 23.7329 | 23.7098 | 23.6856 | 23.6613 | 39.7582 | 39.5045 | 39.2635 | 24.155 | 24.1077 | 24.0392 | 23.9698 | 24.1624 | 24.154 | 24.1466 | 24.1382 | 24.1308 | 40.2445 | 39.9919 | 39.7508
|  | HILSEA PRIMARY | EE |  |  |  |  | 25.5287 | 25.514 | 25.4982 | 25.4813 | 42.3066 | 42.2898 | 42.2729 | 42.2571 | 42.2287 | 42.0498 | 41.8803 | 41.7224 | 23.7498 | 23.6908 | 23.6319 | 23.5719 | 40.355 | 40.3045 | 40.254 | 40.2066 | 40.1613 | 39.9603 | 39.7656 | 39.5856 | 24.1656 | 24.1487 | 24.1056 | 24.0498 | 40.835 | 40.7866 | 40.7403 | 40.694 | 40.6477 | 40.4466 | 40.254 | 40.0729
|  | HILSEA PRIMARY | HT |  |  |  |  | 25.5203 | 25.5035 | 25.4856 | 25.4656 | 42.2887 | 42.2624 | 42.2077 | 42.155 | 42.1045 | 41.8729 | 41.6498 | 41.4392 | 23.7066 | 23.634 | 23.5613 | 23.4877 | 40.2582 | 40.195 | 40.135 | 40.0761 | 40.0192 | 39.7582 | 39.5045 | 39.2635 | 24.155 | 24.1077 | 24.0392 | 23.9698 | 40.7445 | 40.6824 | 40.6213 | 40.5635 | 40.5066 | 40.2445 | 39.9919 | 39.7508
|  | HILSEA PRIMARY | HE |  |  |  |  | 25.5424 | 25.5308 | 25.5182 | 25.5056 | 42.334 | 42.3203 | 42.3077 | 42.2961 | 42.2856 | 42.2498 | 42.2098 | 6.9361 | 23.7666 | 23.755 | 23.7298 | 23.6887 | 40.4887 | 40.455 | 40.4235 | 40.3929 | 40.3635 | 40.2487 | 40.1413 | 40.0435 | 24.1813 | 24.1687 | 24.155 | 24.1403 | 40.9613 | 40.9287 | 40.8982 | 40.8698 | 40.8424 | 40.7329 | 40.6277 | 40.5298
|  | HILSEA PRIMARY | CF |  |  |  |  | 25.5508 | 25.5445 | 25.5382 | 25.5319 | 25.5245 | 25.5171 | 25.5108 | 25.5035 | 25.4971 | 42.3087 | 42.2919 | 42.2835 | 23.775 | 23.7687 | 23.7624 | 23.7561 | 23.7487 | 23.7329 | 23.7098 | 23.6856 | 23.6613 | 40.3992 | 40.3129 | 40.2371 | 24.1898 | 24.1835 | 24.1771 | 24.1708 | 24.1624 | 24.154 | 24.1466 | 24.1382 | 24.1308 | 40.8761 | 40.795 | 40.7245
MANNINGTON GSP | ARNEWOOD BSP | HINCHESLEA PRIMARY | MINIMUM HEADROOM | SU 27805 00447 | NO | YES | 0 | 15.2716 | 15.0611 | 14.8463 | 14.6305 | 14.4147 | 14.2021 | 14.0105 | 13.8316 | 13.6674 | 12.8968 | 12.1558 | 3.9358 | 15.3347 | 15.0789 | 14.82 | 14.5621 | 14.3074 | 14.0568 | 13.8284 | 13.6158 | 13.4168 | 12.4432 | 11.4432 | 10.5105 | 15.64 | 15.4032 | 15.1442 | 14.8863 | 14.6316 | 14.3811 | 14.1526 | 13.9389 | 13.7411 | 12.7674 | 11.7663 | 10.8337
|  | HINCHESLEA PRIMARY | EE |  |  |  |  | 15.4179 | 15.2537 | 15.0832 | 14.9095 | 14.7347 | 14.5674 | 14.4084 | 14.2568 | 14.1179 | 13.5326 | 12.98 | 12.4726 | 15.4821 | 15.32 | 15.1158 | 14.9095 | 14.7032 | 14.5063 | 14.3189 | 14.14 | 13.9747 | 13.2379 | 12.4811 | 11.76 | 15.7895 | 15.6232 | 15.44 | 15.2326 | 15.0274 | 14.8305 | 14.6432 | 14.4632 | 14.2979 | 13.5621 | 12.8053 | 12.0832
|  | HINCHESLEA PRIMARY | HT |  |  |  |  | 15.2716 | 15.0611 | 14.8463 | 14.6305 | 14.4147 | 14.2021 | 14.0105 | 13.8316 | 13.6674 | 12.8968 | 12.1558 | 11.4832 | 15.3347 | 15.0789 | 14.82 | 14.5621 | 14.3074 | 14.0568 | 13.8284 | 13.6158 | 13.4168 | 12.4432 | 11.4432 | 10.5105 | 15.64 | 15.4032 | 15.1442 | 14.8863 | 14.6316 | 14.3811 | 14.1526 | 13.9389 | 13.7411 | 12.7674 | 11.7663 | 10.8337
|  | HINCHESLEA PRIMARY | HE |  |  |  |  | 15.6053 | 15.5011 | 15.3853 | 15.2653 | 15.14 | 15.0211 | 14.9063 | 14.8011 | 14.7084 | 14.3284 | 13.9611 | 3.9358 | 15.5926 | 15.5179 | 15.4347 | 15.3453 | 15.2116 | 15.0747 | 14.9432 | 14.8211 | 14.7137 | 14.2411 | 13.7253 | 13.2305 | 15.9 | 15.8253 | 15.7421 | 15.6442 | 15.5116 | 15.3853 | 15.2642 | 15.1453 | 15.0379 | 14.5653 | 14.0495 | 13.5537
|  | HINCHESLEA PRIMARY | CF |  |  |  |  | 15.7179 | 15.6579 | 15.5968 | 15.5337 | 15.4684 | 15.4032 | 15.3379 | 15.2747 | 15.2105 | 14.9189 | 14.6789 | 14.4537 | 15.6674 | 15.6295 | 15.5905 | 15.5505 | 15.5084 | 15.4653 | 15.4232 | 15.3474 | 15.2695 | 14.9116 | 14.58 | 14.2442 | 15.9747 | 15.9368 | 15.8979 | 15.8579 | 15.8158 | 15.7726 | 15.7158 | 15.6463 | 15.5768 | 15.2358 | 14.9042 | 14.5684
FLEET-BRAMLEY GSP | ALDERSHOT BSP | HINDHEAD PRIMARY | MINIMUM HEADROOM | SU 88631 36479 | NO | YES | 0.21053 | 33.6684 | 33.4032 | 33.1116 | 32.8105 | 32.4263 | 32.0042 | 31.5926 | 31.1863 | 30.7674 | 28.8116 | 27.0389 | 9.1074 | 29.6884 | 29.2516 | 28.6547 | 27.9905 | 27.2189 | 26.7421 | 26.2663 | 25.7884 | 25.3295 | 23.2032 | 21.2589 | 19.5105 | 30.3874 | 29.9242 | 29.3305 | 28.6737 | 27.9189 | 27.4463 | 26.9779 | 26.5063 | 26.0547 | 23.9621 | 22.0063 | 20.2526
|  | HINDHEAD PRIMARY | EE |  |  |  |  | 33.8358 | 33.62 | 33.3884 | 33.1421 | 32.8737 | 32.6232 | 32.3653 | 32.0021 | 31.6695 | 30.1305 | 28.7337 | 27.5547 | 29.9432 | 29.6484 | 29.2474 | 28.7284 | 28.0979 | 27.5947 | 27.1842 | 26.7611 | 26.3726 | 24.6526 | 23.1305 | 21.8137 | 30.7232 | 30.3537 | 29.92 | 29.4032 | 28.7779 | 28.2832 | 27.8758 | 27.4589 | 27.0747 | 25.3737 | 23.86 | 22.5358
|  | HINDHEAD PRIMARY | HT |  |  |  |  | 33.6684 | 33.4032 | 33.1116 | 32.8105 | 32.4263 | 32.0042 | 31.5926 | 31.1863 | 30.7674 | 28.8116 | 27.0389 | 25.4705 | 29.6884 | 29.2516 | 28.6547 | 27.9905 | 27.2189 | 26.7421 | 26.2663 | 25.7884 | 25.3295 | 23.2032 | 21.2589 | 19.5105 | 30.3874 | 29.9242 | 29.3305 | 28.6737 | 27.9189 | 27.4463 | 26.9779 | 26.5063 | 26.0547 | 23.9621 | 22.0063 | 20.2526
|  | HINDHEAD PRIMARY | HE |  |  |  |  | 34.0379 | 33.8958 | 33.7347 | 33.5495 | 33.34 | 33.1505 | 32.9747 | 32.8074 | 32.6621 | 31.8558 | 31.0084 | 9.1074 | 30.2684 | 30.0705 | 29.8284 | 29.52 | 28.9937 | 28.6221 | 28.3242 | 28.0211 | 27.7421 | 26.5621 | 25.5579 | 24.6758 | 31.0189 | 30.8705 | 30.5947 | 30.1926 | 29.6674 | 29.2958 | 28.9979 | 28.6989 | 28.4242 | 27.2621 | 26.28 | 25.4179
|  | HINDHEAD PRIMARY | CF |  |  |  |  | 34.1716 | 34.1 | 34.0232 | 33.9463 | 33.8621 | 33.7768 | 33.6916 | 33.6 | 33.5095 | 33.0884 | 32.86 | 32.4242 | 30.5158 | 30.4074 | 30.2947 | 30.1811 | 30.0611 | 29.9379 | 29.8042 | 29.6537 | 29.5 | 28.4705 | 27.7484 | 27.1284 | 31.1663 | 31.0905 | 31.0084 | 30.9274 | 30.8389 | 30.7495 | 30.5832 | 30.3768 | 30.1705 | 29.1432 | 28.4358 | 27.8295
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL PRIMARY | MINIMUM HEADROOM | SU 00702 06030 | YES | YES | 0 | 6.6242 | 6.5568 | 6.4937 | 6.3968 | 6.1453 | 5.9 | 5.5968 | 5.5495 | 5.5053 | 4.9642 | 4.1779 | 3.3347 | 6.1526 | 6.0811 | 6.0137 | 5.9105 | 5.6316 | 5.3547 | 5.0116 | 4.9684 | 4.9274 | 4.3758 | 3.5147 | 3.2947 | 6.1116 | 6.0453 | 5.9811 | 5.8853 | 5.6347 | 5.3789 | 5.0316 | 4.9842 | 4.94 | 4.3684 | 3.48 | 3.2495
|  | HINTON MARTELL PRIMARY | EE |  |  |  |  | 6.6695 | 6.6158 | 6.5632 | 6.5074 | 6.4453 | 6.3811 | 6.3179 | 6.2537 | 6.1926 | 5.7389 | 4.9684 | 4.5 | 6.1989 | 6.1432 | 6.0895 | 6.0295 | 5.9674 | 5.9032 | 5.8421 | 5.7789 | 5.72 | 5.2632 | 4.4642 | 3.9432 | 6.1568 | 6.1032 | 6.0516 | 5.9947 | 5.9337 | 5.8716 | 5.8084 | 5.7453 | 5.6863 | 5.2442 | 4.4053 | 3.8705
|  | HINTON MARTELL PRIMARY | HT |  |  |  |  | 6.6242 | 6.5568 | 6.4937 | 6.3968 | 6.1453 | 5.9 | 5.5968 | 5.5495 | 5.5053 | 4.9642 | 4.1779 | 3.9642 | 6.1526 | 6.0811 | 6.0137 | 5.9105 | 5.6316 | 5.3547 | 5.0116 | 4.9684 | 4.9274 | 4.3758 | 3.5147 | 3.2947 | 6.1116 | 6.0453 | 5.9811 | 5.8853 | 5.6347 | 5.3789 | 5.0316 | 4.9842 | 4.94 | 4.3684 | 3.48 | 3.2495
|  | HINTON MARTELL PRIMARY | HE |  |  |  |  | 6.7284 | 6.6947 | 6.6621 | 6.6232 | 6.5779 | 6.5358 | 6.4968 | 6.4568 | 6.4232 | 6.1811 | 5.6232 | 3.3347 | 6.2589 | 6.2253 | 6.1916 | 6.1516 | 6.1074 | 6.0653 | 6.0274 | 5.9884 | 5.9537 | 5.7074 | 5.0884 | 4.6579 | 6.2158 | 6.1821 | 6.1495 | 6.1105 | 6.0663 | 6.0242 | 5.9863 | 5.9474 | 5.9137 | 5.6768 | 5.0789 | 4.6379
|  | HINTON MARTELL PRIMARY | CF |  |  |  |  | 6.7621 | 6.7442 | 6.7253 | 6.7053 | 6.6821 | 6.66 | 6.6358 | 6.6147 | 6.5926 | 6.4884 | 6.1968 | 5.9147 | 6.2937 | 6.2747 | 6.2558 | 6.2358 | 6.2137 | 6.1916 | 6.1674 | 6.1463 | 6.1232 | 6.0189 | 5.6979 | 5.3832 | 6.2495 | 6.2316 | 6.2126 | 6.1926 | 6.1695 | 6.1484 | 6.1242 | 6.1032 | 6.0811 | 5.98 | 5.6905 | 5.3895
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HITCHES LANE PRIMARY | MINIMUM HEADROOM | SU 79461 54769 | NO | YES | 0 | 45.2777 | 44.8608 | 44.1956 | 43.3735 | 42.6545 | 41.7903 | 41.0229 | 40.2714 | 39.564 | 34.384 | 31.1324 | -8.9002 | 37.3598 | 36.4114 | 35.3851 | 34.4966 | 33.7419 | 32.8093 | 31.9808 | 31.1629 | 30.3956 | 24.5524 | 20.9251 | 19.6472 | 38.8693 | 37.9251 | 36.9008 | 36.0282 | 35.2766 | 34.3598 | 33.5451 | 32.7429 | 31.9882 | 26.2966 | 22.7524 | 21.4861
|  | HITCHES LANE PRIMARY | EE |  |  |  |  | 45.5314 | 45.1893 | 44.8272 | 44.3629 | 43.704 | 43.0219 | 42.3893 | 41.7514 | 41.1629 | 38.7251 | 36.1335 | 33.8356 | 37.8945 | 37.1061 | 36.2651 | 35.5724 | 34.8714 | 34.1366 | 33.4556 | 32.7693 | 32.1324 | 29.4851 | 26.5893 | 23.9861 | 39.4029 | 38.6166 | 37.7787 | 37.0861 | 36.3914 | 35.6693 | 34.9987 | 34.3219 | 33.6956 | 31.0861 | 28.2535 | 25.7198
|  | HITCHES LANE PRIMARY | HT |  |  |  |  | 45.2777 | 44.8608 | 44.1956 | 43.3735 | 42.6545 | 41.7903 | 41.0229 | 40.2714 | 39.564 | 34.384 | 31.1324 | 29.9166 | 37.3598 | 36.4114 | 35.3851 | 34.4966 | 33.7419 | 32.8093 | 31.9808 | 31.1629 | 30.3956 | 24.5524 | 20.9251 | 19.6472 | 38.8693 | 37.9251 | 36.9008 | 36.0282 | 35.2766 | 34.3598 | 33.5451 | 32.7429 | 31.9882 | 26.2966 | 22.7524 | 21.4861
|  | HITCHES LANE PRIMARY | HE |  |  |  |  | 45.8514 | 45.6103 | 45.3429 | 45.0556 | 44.7461 | 44.4493 | 44.1229 | 43.6566 | 43.2335 | 41.6093 | 39.7882 | -8.9002 | 38.584 | 38.0219 | 37.3861 | 36.8893 | 36.3756 | 35.8303 | 35.3387 | 34.8419 | 34.3861 | 32.6198 | 30.5577 | 28.7124 | 40.0819 | 39.5293 | 38.8966 | 38.3998 | 37.8882 | 37.3429 | 36.8524 | 36.3566 | 35.9082 | 34.1693 | 32.1608 | 30.3693
|  | HITCHES LANE PRIMARY | CF |  |  |  |  | 46.0672 | 45.9366 | 45.8019 | 45.6619 | 45.5166 | 45.3672 | 45.2208 | 45.0756 | 44.9303 | 44.0672 | 42.9156 | 41.8293 | 39.0787 | 38.7724 | 38.4577 | 38.1872 | 37.9124 | 37.6093 | 37.3208 | 37.0166 | 36.7135 | 35.2598 | 33.9693 | 32.724 | 40.5429 | 40.2577 | 39.9651 | 39.6945 | 39.4187 | 39.1177 | 38.8293 | 38.5261 | 38.224 | 36.7735 | 35.5093 | 34.2998
LOVEDEAN GSP | FAREHAM (MAIN) BSP | HOEFORD PRIMARY | MINIMUM HEADROOM | SU 57855 04433 | NO | YES | 1.0516 | 18.6863 | 18.3905 | 17.9136 | 17.4294 | 46.9505 | 46.4747 | 46.0357 | 45.6273 | 45.2452 | 43.1778 | 41.2315 | 16.9568 | 14.4568 | 13.9642 | 13.4589 | 12.9484 | 42.4442 | 41.9463 | 41.4842 | 41.081 | 40.6726 | 38.3421 | 36.1873 | 34.2073 | 15.3726 | 15.0199 | 14.5252 | 14.0231 | 43.5284 | 43.0378 | 42.5842 | 42.2726 | 41.8642 | 39.5136 | 37.3536 | 35.3736
|  | HOEFORD PRIMARY | EE |  |  |  |  | 19.6705 | 19.4505 | 19.2157 | 18.9715 | 48.7157 | 48.3494 | 48.0999 | 46.5052 | 46.1789 | 44.7084 | 43.0494 | 41.7136 | 14.9105 | 14.5915 | 14.2621 | 13.9242 | 43.4515 | 43.0915 | 42.7421 | 42.0378 | 41.6905 | 40.1073 | 38.1936 | 36.6905 | 16.481 | 16.1989 | 15.9031 | 15.5999 | 45.2873 | 44.9852 | 44.6926 | 43.2284 | 42.8799 | 41.2863 | 39.3484 | 37.8442
|  | HOEFORD PRIMARY | HT |  |  |  |  | 18.6863 | 18.3905 | 17.9136 | 17.4294 | 46.9505 | 46.4747 | 46.0357 | 45.6273 | 45.2452 | 43.1778 | 41.2315 | 39.4642 | 14.4568 | 13.9642 | 13.4589 | 12.9484 | 42.4442 | 41.9463 | 41.4842 | 41.081 | 40.6726 | 38.3421 | 36.1873 | 34.2073 | 15.3726 | 15.0199 | 14.5252 | 14.0231 | 43.5284 | 43.0378 | 42.5842 | 42.2726 | 41.8642 | 39.5136 | 37.3536 | 35.3736
|  | HOEFORD PRIMARY | HE |  |  |  |  | 19.8715 | 19.7126 | 19.5389 | 19.3505 | 49.1484 | 48.9547 | 48.7715 | 47.7252 | 47.5063 | 46.561 | 45.341 | 16.9568 | 15.2473 | 15.0305 | 14.801 | 14.5578 | 44.3031 | 44.0599 | 43.8252 | 43.3642 | 43.1336 | 42.1157 | 40.6326 | 39.6347 | 16.7684 | 16.5736 | 16.3642 | 16.141 | 45.9042 | 45.6789 | 45.4621 | 44.5557 | 44.3242 | 43.3021 | 41.7968 | 40.7968
|  | HOEFORD PRIMARY | CF |  |  |  |  | 20.0147 | 19.9305 | 19.8421 | 19.7515 | 49.6568 | 49.5599 | 49.4642 | 49.3705 | 49.2768 | 48.8568 | 48.4978 | 48.3294 | 15.4473 | 15.321 | 15.1884 | 15.0568 | 44.9157 | 44.7799 | 44.6431 | 44.5094 | 44.3747 | 43.6399 | 43.0273 | 42.0094 | 16.9484 | 16.8368 | 16.721 | 16.6042 | 46.4799 | 46.3578 | 46.2357 | 46.1157 | 45.9968 | 45.4494 | 45.0442 | 44.7273
MANNINGTON GSP | LYTCHETT BSP | HOLES BAY PRIMARY | MINIMUM HEADROOM | SZ 00725 91955 | NO | YES | 0 | 24.4011 | 24.3126 | 24.18 | 23.9821 | 23.7842 | 23.5958 | 23.42 | 23.2547 | 23.0968 | 22.3853 | 21.7453 | 0.0021053 | 23.8579 | 23.6463 | 23.4263 | 23.2105 | 22.9958 | 22.7905 | 22.5989 | 22.4189 | 22.2474 | 21.4611 | 20.7463 | 20.0832 | 24.0495 | 23.9421 | 23.8295 | 23.7147 | 23.5979 | 23.4811 | 23.3779 | 23.2832 | 23.1958 | 22.6958 | 22.2589 | 21.7158
|  | HOLES BAY PRIMARY | EE |  |  |  |  | 24.4558 | 24.3842 | 24.3084 | 24.2263 | 24.0674 | 23.92 | 23.7779 | 23.6411 | 23.5116 | 22.9663 | 22.4926 | 22.0642 | 23.9895 | 23.8305 | 23.6558 | 23.4789 | 23.3074 | 23.1474 | 22.9937 | 22.8442 | 22.7032 | 22.1032 | 21.5726 | 21.0884 | 24.1179 | 24.0316 | 23.94 | 23.8463 | 23.7505 | 23.66 | 23.5726 | 23.4895 | 23.4137 | 23.1126 | 22.7937 | 22.5168
|  | HOLES BAY PRIMARY | HT |  |  |  |  | 24.4011 | 24.3126 | 24.18 | 23.9821 | 23.7842 | 23.5958 | 23.42 | 23.2547 | 23.0968 | 22.3853 | 21.7453 | 21.1558 | 23.8579 | 23.6463 | 23.4263 | 23.2105 | 22.9958 | 22.7905 | 22.5989 | 22.4189 | 22.2474 | 21.4611 | 20.7463 | 20.0832 | 24.0495 | 23.9421 | 23.8295 | 23.7147 | 23.5979 | 23.4811 | 23.3779 | 23.2832 | 23.1958 | 22.6958 | 22.2589 | 21.7158
|  | HOLES BAY PRIMARY | HE |  |  |  |  | 24.5242 | 24.4747 | 24.4189 | 24.36 | 24.2958 | 24.2358 | 24.1789 | 24.1253 | 24.06 | 23.7316 | 23.4632 | 0.0021053 | 24.0653 | 24.0137 | 23.9516 | 23.8316 | 23.7095 | 23.6021 | 23.4989 | 23.4011 | 23.3095 | 22.9516 | 22.6505 | 22.3653 | 24.1989 | 24.1453 | 24.08 | 24.0116 | 23.9379 | 23.8705 | 23.8063 | 23.7463 | 23.6926 | 23.5063 | 23.3842 | 23.2947
|  | HOLES BAY PRIMARY | CF |  |  |  |  | 24.5726 | 24.5463 | 24.52 | 24.4916 | 24.4632 | 24.4337 | 24.4053 | 24.3768 | 24.3474 | 24.2 | 23.9947 | 23.8242 | 24.1137 | 24.0874 | 24.0611 | 24.0305 | 23.9979 | 23.9526 | 23.8863 | 23.8189 | 23.7526 | 23.4495 | 23.22 | 23.0242 | 24.2484 | 24.2211 | 24.1947 | 24.1621 | 24.1274 | 24.0926 | 24.0579 | 24.0232 | 23.9884 | 23.8347 | 23.7453 | 23.6863
MELKSHAM GSP | FROME BSP | HOLWELL PRIMARY | MINIMUM HEADROOM | ST 72191 44633 | NO | YES | 1.0516 | 15.6136 | 15.5905 | 13.8263 | 13.7621 | 13.5999 | 12.9421 | 11.7673 | 11.6326 | 11.4936 | 7.1442 | 3.8842 | 1.9431 | 14.1157 | 14.0242 | 12.6926 | 12.6242 | 12.0484 | 10.9968 | 9.6526 | 9.541 | 9.4273 | 4.5926 | 1.0705 | 0.24521 | 14.1347 | 14.121 | 12.3378 | 12.2694 | 12.1021 | 11.0789 | 9.7136 | 9.5768 | 9.4357 | 4.4326 | 0.70942 | -0.87058
|  | HOLWELL PRIMARY | EE |  |  |  |  | 15.7305 | 15.6578 | 13.8263 | 13.7621 | 13.5999 | 13.4347 | 13.2621 | 13.1305 | 12.9368 | 8.7242 | 4.0799 | 2.1389 | 14.1736 | 14.0989 | 12.6926 | 12.6242 | 12.4821 | 12.3378 | 12.1894 | 12.0326 | 11.8726 | 7.3484 | 2.3715 | 0.24521 | 14.2936 | 14.2168 | 12.3378 | 12.2694 | 12.1021 | 11.9305 | 11.7505 | 11.561 | 11.3631 | 6.5957 | 1.341 | -0.87058
|  | HOLWELL PRIMARY | HT |  |  |  |  | 15.6768 | 15.5905 | 15.5042 | 14.8126 | 13.8673 | 12.9421 | 11.7673 | 11.6326 | 11.4936 | 7.1442 | 3.8842 | 3.0768 | 14.1157 | 14.0242 | 13.9315 | 13.1263 | 12.0484 | 10.9968 | 9.6526 | 9.541 | 9.4273 | 4.5926 | 1.0705 | 0.26837 | 14.2357 | 14.1431 | 14.0494 | 13.2452 | 12.1484 | 11.0789 | 9.7136 | 9.5768 | 9.4357 | 4.4326 | 0.70942 | -0.17268
|  | HOLWELL PRIMARY | HE |  |  |  |  | 15.8031 | 15.7589 | 15.7126 | 15.6663 | 15.5652 | 15.4694 | 15.3747 | 15.2789 | 15.1842 | 12.3168 | 8.9663 | 1.9431 | 14.2536 | 14.2063 | 14.1578 | 14.1094 | 14.0189 | 13.9336 | 13.8494 | 13.7663 | 13.6852 | 10.3894 | 6.5873 | 4.7905 | 14.3736 | 14.3263 | 14.2768 | 14.2284 | 14.1221 | 14.0252 | 13.9252 | 13.8273 | 13.7294 | 10.3368 | 6.461 | 4.5936
|  | HOLWELL PRIMARY | CF |  |  |  |  | 15.6136 | 15.5905 | 15.5663 | 15.5399 | 15.4852 | 15.4368 | 15.3831 | 15.3336 | 15.2905 | 14.7947 | 13.6042 | 12.4842 | 14.1778 | 14.1578 | 14.1378 | 14.1147 | 14.0768 | 14.0421 | 14.0052 | 13.9705 | 13.9399 | 13.4421 | 12.0126 | 10.6821 | 14.1347 | 14.121 | 14.1063 | 14.0915 | 14.0526 | 14.0168 | 13.9778 | 13.9421 | 13.9105 | 13.4936 | 12.0242 | 10.6463
MANNINGTON GSP | SALISBURY BSP | HOMINGTON PRIMARY | MINIMUM HEADROOM | SU 11742 26037 | NO | YES | 9.4737 | 8.02 | 7.9484 | 7.8726 | 7.7947 | 7.7147 | 7.6337 | 7.5632 | 7.4989 | 7.44 | 6.9463 | 6.38 | -3.5905 | 6.2432 | 6.1095 | 5.9726 | 5.8358 | 5.7011 | 5.5653 | 5.3295 | 5.2653 | 5.2063 | 4.5958 | 3.9737 | 3.3684 | 6.5768 | 6.5011 | 6.4 | 6.2621 | 6.1253 | 5.9884 | 5.7463 | 5.6821 | 5.6232 | 5 | 4.3642 | 3.7442
|  | HOMINGTON PRIMARY | EE |  |  |  |  | 8.0642 | 8.0053 | 8.3768 | 8.2716 | 8.1674 | 8.0663 | 7.9695 | 7.8758 | 7.7895 | 7.3653 | 6.9284 | 6.4937 | 6.3379 | 6.2305 | 6.2716 | 6.1589 | 6.0474 | 5.94 | 5.8368 | 5.7368 | 5.6442 | 5.1789 | 4.6863 | 4.1905 | 6.6242 | 6.5621 | 6.5516 | 6.4389 | 6.3284 | 6.22 | 6.1179 | 6.0179 | 5.9253 | 5.4589 | 4.9684 | 4.4726
|  | HOMINGTON PRIMARY | HT |  |  |  |  | 8.02 | 7.9484 | 7.8726 | 7.7947 | 7.7147 | 7.6337 | 7.5632 | 7.4989 | 7.44 | 6.9463 | 6.38 | 5.8316 | 6.2432 | 6.1095 | 5.9726 | 5.8358 | 5.7011 | 5.5653 | 5.3295 | 5.2653 | 5.2063 | 4.5958 | 3.9737 | 3.3684 | 6.5768 | 6.5011 | 6.4 | 6.2621 | 6.1253 | 5.9884 | 5.7463 | 5.6821 | 5.6232 | 5 | 4.3642 | 3.7442
|  | HOMINGTON PRIMARY | HE |  |  |  |  | 8.1211 | 8.0811 | 8.5621 | 8.4895 | 8.4137 | 8.3411 | 8.2747 | 8.2095 | 8.1516 | 7.8579 | 7.5379 | -3.5905 | 6.46 | 6.3905 | 6.4716 | 6.3947 | 6.3147 | 6.2389 | 6.1674 | 6.0989 | 6.0368 | 5.7137 | 5.3516 | 4.9758 | 6.6853 | 6.6432 | 6.7516 | 6.6758 | 6.5958 | 6.5189 | 6.4484 | 6.3789 | 6.3179 | 5.9937 | 5.6316 | 5.2568
|  | HOMINGTON PRIMARY | CF |  |  |  |  | 8.1611 | 8.1411 | 8.1211 | 8.0989 | 8.0768 | 8.0537 | 8.0316 | 8.0095 | 7.9874 | 7.8874 | 7.8379 | 7.8116 | 6.5295 | 6.4916 | 6.4516 | 6.4126 | 6.3653 | 6.3179 | 6.2747 | 6.2337 | 6.1916 | 5.9947 | 5.7926 | 5.5611 | 6.7274 | 6.7063 | 6.6842 | 6.6611 | 6.6379 | 6.6126 | 6.5895 | 6.5663 | 6.5421 | 6.4232 | 6.2158 | 5.9779
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HOOK PRIMARY | MINIMUM HEADROOM | SU 72602 53780 | NO | YES | 0 | 34.2505 | 33.9832 | 33.6979 | 33.4063 | 33.0863 | 32.44 | 31.0295 | 30.7621 | 30.5105 | 27.8179 | 24.3537 | 1.2737 | 29.8747 | 29.5042 | 29.0684 | 28.5421 | 27.6484 | 26.3211 | 24.7147 | 24.4537 | 24.2095 | 21.2768 | 17.4032 | 16.3011 | 31.0442 | 30.7011 | 30.2568 | 29.7221 | 28.86 | 27.5274 | 25.9147 | 25.6474 | 25.3947 | 22.4147 | 18.4821 | 17.3568
|  | HOOK PRIMARY | EE |  |  |  |  | 34.4147 | 34.1947 | 33.96 | 33.7189 | 33.4505 | 33.1832 | 32.9263 | 32.6747 | 32.9284 | 31.14 | 28.4326 | 26.3442 | 30.0947 | 29.7895 | 29.4695 | 29.1432 | 28.7495 | 28.2947 | 27.8516 | 27.4011 | 26.9853 | 25.1168 | 22.1421 | 19.7789 | 31.2126 | 30.9863 | 30.6642 | 30.3337 | 29.9263 | 29.4621 | 29.0232 | 28.5779 | 28.1621 | 26.2221 | 23.1695 | 20.7821
|  | HOOK PRIMARY | HT |  |  |  |  | 34.2505 | 33.9832 | 33.6979 | 33.4063 | 33.0863 | 32.44 | 31.0295 | 30.7621 | 30.5105 | 27.8179 | 24.3537 | 23.3105 | 29.8747 | 29.5042 | 29.0684 | 28.5421 | 27.6484 | 26.3211 | 24.7147 | 24.4537 | 24.2095 | 21.2768 | 17.4032 | 16.3011 | 31.0442 | 30.7011 | 30.2568 | 29.7221 | 28.86 | 27.5274 | 25.9147 | 25.6474 | 25.3947 | 22.4147 | 18.4821 | 17.3568
|  | HOOK PRIMARY | HE |  |  |  |  | 34.6274 | 34.4758 | 34.3084 | 34.1274 | 33.9211 | 33.7253 | 33.5379 | 33.3621 | 33.2063 | 32.6368 | 31.3432 | 1.2737 | 30.3579 | 30.1684 | 29.9389 | 29.6968 | 29.4316 | 29.2053 | 28.9884 | 28.7632 | 28.4926 | 27.3063 | 25.1695 | 23.2663 | 31.4295 | 31.2747 | 31.1032 | 30.8979 | 30.6242 | 30.3926 | 30.1695 | 29.9379 | 29.6568 | 28.4695 | 26.3126 | 24.3874
|  | HOOK PRIMARY | CF |  |  |  |  | 34.7716 | 34.6926 | 34.6126 | 34.5295 | 34.4358 | 34.3389 | 34.2442 | 34.1505 | 34.0611 | 33.6432 | 33.4084 | 32.8347 | 30.5442 | 30.4568 | 30.3695 | 30.2642 | 30.1379 | 30.0126 | 29.8874 | 29.7632 | 29.6421 | 28.9042 | 28.0747 | 26.7326 | 31.5768 | 31.4968 | 31.4158 | 31.3316 | 31.2358 | 31.1379 | 31.04 | 30.9453 | 30.8358 | 30.0674 | 29.2579 | 27.9063
LALEHAM GSP | EAST BEDFONT BSP | HOPE AND ANCHOR PRIMARY | MINIMUM HEADROOM | TQ 12710 72057 | YES | YES | 0 | 10.2421 | 10.1474 | 10.0474 | 9.9432 | 9.8358 | 9.7347 | 9.6463 | 9.5632 | 9.4832 | 9.0495 | 8.5274 | 4.2011 | 9.9137 | 9.8063 | 9.6926 | 9.5737 | 9.4526 | 9.34 | 9.2411 | 9.1474 | 9.0568 | 8.5526 | 7.9232 | 7.3063 | 10.1347 | 10.0295 | 9.9179 | 9.8021 | 9.6832 | 9.5716 | 9.4747 | 9.3832 | 9.2947 | 8.8021 | 8.1789 | 7.5632
|  | HOPE AND ANCHOR PRIMARY | EE |  |  |  |  | 10.3295 | 10.2379 | 10.1547 | 10.0674 | 9.9821 | 9.9032 | 9.8242 | 9.7484 | 9.6789 | 9.3684 | 8.9832 | 8.6105 | 10.0179 | 9.9126 | 9.8189 | 9.7189 | 9.6232 | 9.5347 | 9.4474 | 9.3632 | 9.2853 | 8.9284 | 8.4642 | 8.0084 | 10.1926 | 10.1326 | 10.0411 | 9.9432 | 9.8495 | 9.7621 | 9.6768 | 9.5937 | 9.5168 | 9.1684 | 8.7179 | 8.2642
|  | HOPE AND ANCHOR PRIMARY | HT |  |  |  |  | 10.2421 | 10.1474 | 10.0474 | 9.9432 | 9.8358 | 9.7347 | 9.6463 | 9.5632 | 9.4832 | 9.0495 | 8.5274 | 8.0221 | 9.9137 | 9.8063 | 9.6926 | 9.5737 | 9.4526 | 9.34 | 9.2411 | 9.1474 | 9.0568 | 8.5526 | 7.9232 | 7.3063 | 10.1347 | 10.0295 | 9.9179 | 9.8021 | 9.6832 | 9.5716 | 9.4747 | 9.3832 | 9.2947 | 8.8021 | 8.1789 | 7.5632
|  | HOPE AND ANCHOR PRIMARY | HE |  |  |  |  | 10.3968 | 10.3263 | 10.2621 | 10.1937 | 10.1242 | 10.0632 | 10.0053 | 9.9484 | 9.8979 | 9.6895 | 9.4032 | 4.2011 | 10.0958 | 10.0147 | 9.9432 | 9.8663 | 9.7884 | 9.7211 | 9.6568 | 9.5947 | 9.5379 | 9.3 | 8.9505 | 8.6074 | 10.2253 | 10.1905 | 10.1516 | 10.0874 | 10.0105 | 9.9442 | 9.8811 | 9.82 | 9.7642 | 9.5305 | 9.1926 | 8.8611
|  | HOPE AND ANCHOR PRIMARY | CF |  |  |  |  | 10.4726 | 10.4358 | 10.3905 | 10.3442 | 10.2926 | 10.2389 | 10.2 | 10.1495 | 10.0958 | 9.8337 | 9.6547 | 9.4768 | 10.1358 | 10.1158 | 10.0916 | 10.0379 | 9.9789 | 9.9158 | 9.8716 | 9.8137 | 9.7505 | 9.4411 | 9.2253 | 9.0042 | 10.2495 | 10.2305 | 10.2095 | 10.1884 | 10.1653 | 10.1358 | 10.0926 | 10.0347 | 9.9737 | 9.6726 | 9.4632 | 9.2495
LOVEDEAN GSP | HAVANT BSP | HORNDEAN PRIMARY | MINIMUM HEADROOM | SU 70271 12802 | NO | YES | 0 | 33.4853 | 31.8758 | 30.1632 | 28.2558 | 56.3442 | 54.5979 | 53.0116 | 51.4495 | 50.0305 | 44.4895 | 39.6705 | 14.1684 | 27.1758 | 25.3358 | 23.4042 | 21.2779 | 49.1547 | 47.2274 | 45.4747 | 43.7389 | 42.1663 | 36.0453 | 30.6853 | 25.0916 | 28.2684 | 26.5189 | 24.6305 | 22.5032 | 50.3779 | 48.4484 | 46.6916 | 44.9547 | 43.3768 | 37.2368 | 31.8537 | 26.2495
|  | HORNDEAN PRIMARY | EE |  |  |  |  | 34.1916 | 32.82 | 31.3463 | 29.7389 | 58.1189 | 56.6432 | 55.2737 | 53.9347 | 52.7432 | 48.4305 | 44.7316 | 40.8832 | 27.9737 | 26.3726 | 24.7053 | 22.8926 | 51.0905 | 49.4579 | 47.9453 | 46.4642 | 45.1495 | 40.4084 | 36.3 | 31.9337 | 29.0358 | 27.5158 | 25.9305 | 24.1179 | 52.3147 | 50.6789 | 49.1621 | 47.6768 | 46.3568 | 41.5874 | 37.4495 | 33.0716
|  | HORNDEAN PRIMARY | HT |  |  |  |  | 33.4853 | 31.8758 | 30.1632 | 28.2558 | 56.3442 | 54.5979 | 53.0116 | 51.4495 | 50.0305 | 44.4895 | 39.6705 | 34.7189 | 27.1758 | 25.3358 | 23.4042 | 21.2779 | 49.1547 | 47.2274 | 45.4747 | 43.7389 | 42.1663 | 36.0453 | 30.6853 | 25.0916 | 28.2684 | 26.5189 | 24.6305 | 22.5032 | 50.3779 | 48.4484 | 46.6916 | 44.9547 | 43.3768 | 37.2368 | 31.8537 | 26.2495
|  | HORNDEAN PRIMARY | HE |  |  |  |  | 35.1063 | 34.0337 | 32.8695 | 31.5358 | 60.1821 | 58.9547 | 57.8358 | 56.7453 | 55.7916 | 52.6495 | 50.0716 | 14.1684 | 29.0137 | 27.7337 | 26.3821 | 24.8589 | 53.3337 | 51.9674 | 50.7242 | 49.5105 | 48.4495 | 44.9653 | 42.0589 | 38.76 | 30.0326 | 28.8232 | 27.5421 | 26.0863 | 54.5579 | 53.1905 | 51.9463 | 50.7295 | 49.6663 | 46.1705 | 43.2558 | 39.9474
|  | HORNDEAN PRIMARY | CF |  |  |  |  | 35.8579 | 35.4495 | 35.0105 | 34.5053 | 63.9495 | 63.2611 | 62.4211 | 61.5611 | 60.5105 | 58.4568 | 56.7337 | 54.8884 | 29.8842 | 29.4116 | 28.9011 | 28.3063 | 57.6505 | 56.8368 | 55.8695 | 54.8737 | 53.6621 | 51.4095 | 49.4695 | 47.3537 | 30.7758 | 30.3716 | 29.9274 | 29.3632 | 58.74 | 57.9695 | 57.0558 | 56.0968 | 54.8842 | 52.6274 | 50.6832 | 48.5611
NURSLING GSP | WINCHESTER BSP | HOUGHTON PRIMARY | MINIMUM HEADROOM | SU 33784 31741 | NO | YES | 0 | 16.4579 | 16.2905 | 16.1137 | 15.2326 | 13.9095 | 12.6147 | 10.9811 | 10.8074 | 10.6347 | 8.1674 | 3.8632 | -15.7526 | 15.0611 | 14.8832 | 14.6947 | 13.6811 | 12.1726 | 10.7011 | 8.8316 | 8.6779 | 8.5274 | 6 | 1.2137 | 0.13895 | 14.8168 | 14.7884 | 14.8326 | 14.1358 | 12.6116 | 11.1211 | 9.2326 | 9.0589 | 8.8853 | 6.1463 | 1.2547 | 0.11368
|  | HOUGHTON PRIMARY | EE |  |  |  |  | 16.5726 | 16.4337 | 16.2853 | 16.14 | 15.9358 | 15.7063 | 15.4705 | 15.2284 | 14.9863 | 11.96 | 8.0368 | 5.4526 | 15.1863 | 15.0411 | 14.8832 | 14.7326 | 14.5347 | 14.3179 | 14.0989 | 13.8758 | 13.6568 | 10.5 | 6.3263 | 3.4421 | 14.8726 | 14.7884 | 15.3379 | 15.1842 | 14.9716 | 14.7316 | 14.4874 | 14.2368 | 13.9863 | 10.6232 | 6.2137 | 3.2547
|  | HOUGHTON PRIMARY | HT |  |  |  |  | 16.4579 | 16.2905 | 16.1137 | 15.2326 | 13.9095 | 12.6147 | 10.9811 | 10.8074 | 10.6347 | 8.1674 | 3.8632 | 2.8221 | 15.0611 | 14.8832 | 14.6947 | 13.6811 | 12.1726 | 10.7011 | 8.8316 | 8.6779 | 8.5274 | 6 | 1.2137 | 0.13895 | 14.8168 | 15.34 | 15.1505 | 14.1358 | 12.6116 | 11.1211 | 9.2326 | 9.0589 | 8.8853 | 6.1463 | 1.2547 | 0.11368
|  | HOUGHTON PRIMARY | HE |  |  |  |  | 16.7242 | 16.6389 | 16.5432 | 16.4495 | 16.2968 | 16.1537 | 16.0126 | 15.8737 | 15.7421 | 14.1495 | 11.6821 | -15.7526 | 15.3411 | 15.2547 | 15.1589 | 15.0611 | 14.9147 | 14.7779 | 14.6442 | 14.5126 | 14.3895 | 12.6937 | 9.9274 | 7.4989 | 14.9484 | 14.8937 | 14.8326 | 15.5179 | 15.36 | 15.2116 | 15.0653 | 14.9211 | 14.7853 | 13.0042 | 10.1716 | 7.6811
|  | HOUGHTON PRIMARY | CF |  |  |  |  | 16.8084 | 16.7589 | 16.7021 | 16.6442 | 16.5558 | 16.4726 | 16.3916 | 16.3179 | 16.2484 | 15.6421 | 13.9126 | 12.3126 | 15.4263 | 15.3758 | 15.3189 | 15.2642 | 15.1758 | 15.0937 | 15.0147 | 14.9421 | 14.8737 | 14.2347 | 12.2789 | 10.4768 | 15.0011 | 14.9726 | 14.9421 | 15.7221 | 15.6274 | 15.54 | 15.4547 | 15.3768 | 15.3032 | 14.6368 | 12.6442 | 10.8011
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | HOUNDMILLS PRIMARY | MINIMUM HEADROOM | SU 62187 52886 | NO | YES | 0 | 44.2851 | 44.1366 | 43.9766 | 43.2851 | 41.6093 | 39.8451 | 38.0598 | 36.2882 | 34.5324 | 27.2387 | 25.9651 | 1.1377 | 39.6587 | 38.7766 | 37.0124 | 35.2524 | 33.2272 | 31.1629 | 29.104 | 27.0587 | 25.0314 | 16.6514 | 15.3503 | 14.0303 | 40.7314 | 40.2493 | 38.5008 | 36.7124 | 34.6451 | 32.5598 | 30.4956 | 28.4451 | 26.4103 | 17.9766 | 16.5987 | 15.2482
|  | HOUNDMILLS PRIMARY | EE |  |  |  |  | 44.3672 | 44.2419 | 45.2577 | 43.7577 | 42.0135 | 40.264 | 38.5124 | 36.7566 | 35.0135 | 27.8072 | 26.7261 | 25.7514 | 39.7545 | 39.0177 | 37.3956 | 35.6566 | 33.6419 | 31.6272 | 29.6072 | 27.5851 | 25.5766 | 17.3261 | 16.284 | 15.2324 | 40.8198 | 40.4819 | 38.7966 | 37.0598 | 35.0408 | 33.0177 | 30.9903 | 28.9598 | 26.9408 | 18.6093 | 17.4598 | 16.3724
|  | HOUNDMILLS PRIMARY | HT |  |  |  |  | 44.2851 | 44.1366 | 43.9766 | 43.2851 | 41.6093 | 39.8451 | 38.0598 | 36.2882 | 34.5324 | 27.2387 | 25.9651 | 24.7535 | 39.6587 | 38.7766 | 37.0124 | 35.2524 | 33.2272 | 31.1629 | 29.104 | 27.0587 | 25.0314 | 16.6514 | 15.3503 | 14.0303 | 40.7314 | 40.2493 | 38.5008 | 36.7124 | 34.6451 | 32.5598 | 30.4956 | 28.4451 | 26.4103 | 17.9766 | 16.5987 | 15.2482
|  | HOUNDMILLS PRIMARY | HE |  |  |  |  | 44.4808 | 44.3914 | 45.6387 | 44.2082 | 42.5314 | 40.864 | 39.1987 | 37.5366 | 35.8872 | 29.1861 | 28.7345 | 1.1377 | 39.8872 | 39.3503 | 37.8093 | 36.144 | 34.1998 | 32.2661 | 30.3345 | 28.4051 | 26.4893 | 18.7187 | 18.2672 | 17.6556 | 40.9408 | 40.8061 | 39.2114 | 37.5493 | 35.604 | 33.6682 | 31.7345 | 29.8019 | 27.884 | 20.0872 | 19.6051 | 18.9682
|  | HOUNDMILLS PRIMARY | CF |  |  |  |  | 44.5598 | 44.5124 | 44.4619 | 44.4103 | 44.3472 | 44.284 | 44.2208 | 43.664 | 42.5619 | 36.9608 | 36.6008 | 36.2703 | 39.984 | 39.9219 | 39.8408 | 39.5956 | 38.9819 | 38.0819 | 36.9061 | 35.6493 | 34.2977 | 27.7093 | 27.3345 | 26.9882 | 41.0282 | 40.9745 | 40.9103 | 40.8387 | 40.4524 | 39.5787 | 38.3787 | 37.0977 | 35.7229 | 29.104 | 28.7124 | 28.3482
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | HUNGERFORD PRIMARY | MINIMUM HEADROOM | SU 34066 68957 | NO | YES | 0 | 17.1684 | 17.0484 | 16.9211 | 16.7895 | 16.6526 | 16.5158 | 16.3958 | 16.2853 | 16.1853 | 15.6874 | 14.9274 | 2.2916 | 15.1116 | 14.8821 | 14.6495 | 14.4168 | 14.1842 | 13.9558 | 13.7463 | 13.5495 | 13.3663 | 12.5505 | 11.7126 | 10.9253 | 15.5737 | 15.4537 | 15.2558 | 15.0474 | 14.8242 | 14.5947 | 14.3853 | 14.1895 | 14.0063 | 13.1895 | 12.3516 | 11.5642
|  | HUNGERFORD PRIMARY | EE |  |  |  |  | 17.2368 | 17.1368 | 17.0305 | 16.92 | 16.8032 | 16.6926 | 16.5874 | 16.4863 | 16.3958 | 16.0663 | 15.7168 | 15.1726 | 15.2653 | 15.0811 | 14.8937 | 14.7042 | 14.5126 | 14.3284 | 14.1526 | 13.9842 | 13.8274 | 13.2032 | 12.5737 | 11.9632 | 15.6421 | 15.5421 | 15.4358 | 15.2979 | 15.1242 | 14.9568 | 14.7926 | 14.6242 | 14.4674 | 13.8432 | 13.2126 | 12.6021
|  | HUNGERFORD PRIMARY | HT |  |  |  |  | 17.1684 | 17.0484 | 16.9211 | 16.7895 | 16.6526 | 16.5158 | 16.3958 | 16.2853 | 16.1853 | 15.6874 | 14.9274 | 14.2211 | 15.1116 | 14.8821 | 14.6495 | 14.4168 | 14.1842 | 13.9558 | 13.7463 | 13.5495 | 13.3663 | 12.5505 | 11.7126 | 10.9253 | 15.5737 | 15.4537 | 15.2558 | 15.0474 | 14.8242 | 14.5947 | 14.3853 | 14.1895 | 14.0063 | 13.1895 | 12.3516 | 11.5642
|  | HUNGERFORD PRIMARY | HE |  |  |  |  | 17.3295 | 17.2579 | 17.1779 | 17.0926 | 17.0021 | 16.9158 | 16.8337 | 16.7568 | 16.6905 | 16.4684 | 16.3389 | 2.2916 | 15.4063 | 15.3326 | 15.2253 | 15.0926 | 14.9558 | 14.8263 | 14.7021 | 14.5863 | 14.4811 | 14.1105 | 13.7189 | 13.3337 | 15.7347 | 15.6632 | 15.5832 | 15.4979 | 15.4074 | 15.3211 | 15.2389 | 15.1621 | 15.0737 | 14.7379 | 14.3589 | 13.9737
|  | HUNGERFORD PRIMARY | CF |  |  |  |  | 17.3937 | 17.3558 | 17.3158 | 17.2737 | 17.2326 | 17.1884 | 17.1453 | 17.1032 | 17.06 | 16.8716 | 16.7779 | 16.7253 | 15.4705 | 15.4326 | 15.3916 | 15.3474 | 15.2853 | 15.2053 | 15.1305 | 15.0558 | 14.9811 | 14.6347 | 14.3442 | 14.0737 | 15.7989 | 15.7611 | 15.7211 | 15.6789 | 15.6379 | 15.5937 | 15.5505 | 15.5084 | 15.4653 | 15.2337 | 14.9842 | 14.7137
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | HUNSTON PRIMARY | MINIMUM HEADROOM | SU 86949 02632 | NO | YES | 0.21053 | 33.9253 | 33.7716 | 33.6084 | 33.44 | 33.6579 | 33.2411 | 31.5926 | 31.4526 | 31.3232 | 27.8884 | 27.3916 | 5.5453 | 29.5937 | 29.44 | 29.2768 | 29.0684 | 28.5726 | 28.1126 | 26.1916 | 26.0516 | 25.9221 | 21.9568 | 21.4411 | 20.5032 | 30.4568 | 30.3032 | 30.14 | 29.9347 | 29.6884 | 29.2284 | 27.3105 | 27.1705 | 27.0411 | 23.0821 | 22.5674 | 21.6305
|  | HUNSTON PRIMARY | EE |  |  |  |  | 34.0126 | 35.3537 | 35.2179 | 35.0758 | 34.9284 | 34.7863 | 34.6516 | 34.5211 | 34.4053 | 33.9821 | 29.5221 | 28.2684 | 29.6811 | 29.5926 | 29.4568 | 29.4253 | 29.1189 | 28.7432 | 28.3789 | 27.9863 | 27.5653 | 25.5368 | 23.9874 | 22.5674 | 30.5442 | 31.7926 | 31.6568 | 31.5147 | 31.3505 | 31.1263 | 30.9116 | 30.6905 | 30.4684 | 26.5653 | 24.9947 | 23.5537
|  | HUNSTON PRIMARY | HT |  |  |  |  | 33.9253 | 33.7716 | 33.6084 | 33.44 | 33.6579 | 33.2411 | 31.5926 | 31.4526 | 31.3232 | 27.8884 | 27.3916 | 26.5495 | 29.5937 | 29.44 | 29.2768 | 29.0684 | 28.5726 | 28.1126 | 26.1916 | 26.0516 | 25.9221 | 21.9568 | 21.4411 | 20.5032 | 30.4568 | 30.3032 | 30.14 | 29.9347 | 29.6884 | 29.2284 | 27.3105 | 27.1705 | 27.0411 | 23.0821 | 22.5674 | 21.6305
|  | HUNSTON PRIMARY | HE |  |  |  |  | 34.1295 | 35.5053 | 35.4032 | 35.2937 | 34.4063 | 34.2947 | 34.0758 | 33.7832 | 33.4653 | 31.9537 | 30.8579 | 5.5453 | 29.7979 | 29.7442 | 29.6421 | 29.5326 | 29.3768 | 29.2653 | 29.0263 | 28.6968 | 28.3379 | 26.6032 | 25.3368 | 24.1895 | 30.6611 | 31.9442 | 31.8421 | 31.7326 | 30.4916 | 30.38 | 30.1411 | 29.8126 | 29.4537 | 27.7211 | 26.4579 | 25.3116
|  | HUNSTON PRIMARY | CF |  |  |  |  | 34.2116 | 35.6305 | 35.5779 | 35.5253 | 35.4695 | 35.4137 | 35.3579 | 35.3032 | 35.2484 | 35.0042 | 34.8821 | 34.8147 | 29.88 | 29.8695 | 29.8168 | 29.7642 | 29.7084 | 29.6526 | 29.5968 | 29.5421 | 29.4874 | 28.7947 | 28.0074 | 27.3147 | 30.7432 | 32.0695 | 32.0168 | 31.9642 | 31.9084 | 31.8526 | 31.7968 | 31.7421 | 31.6874 | 31.2863 | 30.9337 | 28.2379
MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT PRIMARY | MINIMUM HEADROOM | SU 39384 52476 | NO | YES | 0.70421 | 5.511 | 5.4363 | 3.7521 | 3.6468 | 3.5394 | 3.4363 | 3.3321 | 3.2268 | 3.1299 | 2.7363 | 2.3373 | -1.9279 | 4.4247 | 4.2857 | 2.911 | 2.7994 | 2.6857 | 2.5773 | 2.4678 | 2.3573 | 2.2521 | 1.8352 | 1.3794 | 0.92784 | 4.4036 | 4.2657 | 2.4636 | 2.3521 | 2.2384 | 2.1289 | 2.0173 | 1.9057 | 1.8005 | 1.3763 | 0.911 | 0.45626
|  | HURSTBOURNE TARRANT PRIMARY | EE |  |  |  |  | 5.5573 | 5.4973 | 3.7521 | 3.6468 | 3.5394 | 3.4363 | 3.3321 | 3.2268 | 3.1299 | 2.7363 | 2.3373 | 1.9352 | 4.5047 | 4.4131 | 2.911 | 2.7994 | 2.6857 | 2.5773 | 2.4678 | 2.3573 | 2.2521 | 1.8352 | 1.3794 | 0.92784 | 4.5026 | 4.3921 | 2.4636 | 2.3521 | 2.2384 | 2.1289 | 2.0173 | 1.9057 | 1.8005 | 1.3763 | 0.911 | 0.45626
|  | HURSTBOURNE TARRANT PRIMARY | HT |  |  |  |  | 5.511 | 5.4363 | 5.3573 | 5.2394 | 5.1047 | 4.9647 | 4.8373 | 4.7184 | 4.6068 | 4.1215 | 3.5899 | 3.0899 | 4.4247 | 4.2857 | 4.1415 | 4.0005 | 3.8573 | 3.7068 | 3.571 | 3.4426 | 3.3215 | 2.7984 | 2.2142 | 1.6542 | 4.4036 | 4.2657 | 4.1205 | 3.9805 | 3.8363 | 3.6857 | 3.5478 | 3.4194 | 3.2973 | 2.7678 | 2.1773 | 1.6152
|  | HURSTBOURNE TARRANT PRIMARY | HE |  |  |  |  | 5.6173 | 5.5763 | 5.5299 | 5.4805 | 5.4257 | 5.3731 | 5.3247 | 5.2773 | 5.2384 | 5.0521 | 4.7984 | -1.9279 | 4.5857 | 4.5363 | 4.4805 | 4.4226 | 4.3542 | 4.2794 | 4.2036 | 4.1257 | 4.0605 | 3.8184 | 3.531 | 3.2278 | 4.6321 | 4.5626 | 4.4868 | 4.4121 | 4.3321 | 4.2584 | 4.1815 | 4.1026 | 4.0384 | 3.7931 | 3.5026 | 3.1984
|  | HURSTBOURNE TARRANT PRIMARY | CF |  |  |  |  | 5.6594 | 5.6394 | 5.6173 | 5.5942 | 5.5699 | 5.5457 | 5.5215 | 5.4973 | 5.4731 | 5.3668 | 5.2015 | 5.0415 | 4.6352 | 4.6121 | 4.5826 | 4.5521 | 4.5194 | 4.4857 | 4.4426 | 4.3994 | 4.3573 | 4.1478 | 3.9531 | 3.7678 | 4.6952 | 4.6657 | 4.6226 | 4.5731 | 4.5205 | 4.4657 | 4.4205 | 4.3784 | 4.3363 | 4.1247 | 3.9278 | 3.7426
EALING GSP |  | IRONBRIDGE PRIMARY | MINIMUM HEADROOM | TQ 14226 80171 | NO | YES | 0 | 47.6945 | 47.3387 | 46.9608 | 46.5629 | 46.6082 | 45.7124 | 44.6672 | 43.4545 | 42.2714 | 38.6514 | 35.7019 | -10.2571 | 39.9324 | 38.524 | 36.1472 | 33.8861 | 34.2335 | 32.6008 | 31.4293 | 30.0566 | 28.7145 | 24.984 | 21.6998 | 18.5124 | 41.4503 | 40.6829 | 38.3114 | 36.0535 | 36.3998 | 34.7693 | 33.5987 | 32.2293 | 30.8893 | 26.7914 | 23.5072 | 20.3187
|  | IRONBRIDGE PRIMARY | EE |  |  |  |  | 47.8987 | 47.604 | 47.2893 | 46.9566 | 46.6082 | 45.7124 | 44.6672 | 43.4545 | 42.2714 | 41.3251 | 39.2556 | 37.2956 | 40.4587 | 39.6314 | 37.8661 | 36.1798 | 34.2335 | 32.6008 | 31.4293 | 30.0566 | 28.7145 | 27.9672 | 25.6693 | 23.4682 | 41.6787 | 41.3472 | 40.0261 | 38.3429 | 36.3998 | 34.7693 | 33.5987 | 32.2293 | 30.8893 | 29.7756 | 27.4766 | 25.2745
|  | IRONBRIDGE PRIMARY | HT |  |  |  |  | 47.6945 | 47.3387 | 46.9608 | 46.5629 | 47.8261 | 46.104 | 44.8661 | 43.6851 | 42.5356 | 38.6514 | 35.7019 | 32.864 | 39.9324 | 38.524 | 36.1472 | 33.8861 | 35.2735 | 33.324 | 31.9366 | 30.6082 | 29.3145 | 24.984 | 21.6998 | 18.5124 | 41.4503 | 40.6829 | 38.3114 | 36.0535 | 37.084 | 35.1335 | 33.7451 | 32.4177 | 31.1229 | 26.7914 | 23.5072 | 20.3187
|  | IRONBRIDGE PRIMARY | HE |  |  |  |  | 48.124 | 47.8914 | 47.6345 | 47.3587 | 47.0661 | 46.7851 | 45.9398 | 44.8714 | 43.8672 | 43.7577 | 42.4187 | -10.2571 | 40.7029 | 40.3451 | 38.724 | 37.1745 | 35.364 | 33.8777 | 32.824 | 31.6103 | 30.4661 | 30.6408 | 29.1482 | 27.7482 | 41.924 | 41.6598 | 40.884 | 39.3366 | 37.5293 | 36.0451 | 34.9935 | 33.7808 | 32.6387 | 32.4493 | 30.9566 | 29.5556
|  | IRONBRIDGE PRIMARY | CF |  |  |  |  | 48.2914 | 48.1535 | 48.0103 | 47.8619 | 47.7082 | 47.5524 | 47.3987 | 47.2461 | 47.0935 | 45.484 | 47.3051 | 46.5114 | 40.8914 | 40.7461 | 40.5777 | 40.364 | 39.9051 | 39.4166 | 38.9903 | 38.4272 | 37.7851 | 32.3061 | 34.6756 | 33.7766 | 42.1124 | 41.9672 | 41.7977 | 41.6335 | 41.4619 | 41.2861 | 41.1166 | 40.5872 | 39.9451 | 34.4756 | 36.4861 | 35.5861
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | JAYS CLOSE PRIMARY | MINIMUM HEADROOM | SU 63055 50105 | NO | YES | 0 | 44.6461 | 44.3819 | 44.0998 | 43.8093 | 43.4851 | 43.1587 | 42.8651 | 42.5914 | 42.2419 | 40.3872 | 38.5545 | 5.7093 | 39.5987 | 39.3345 | 38.9208 | 38.4072 | 37.8714 | 37.3166 | 36.8029 | 36.3135 | 35.8598 | 33.8061 | 31.7261 | 29.5587 | 41.2998 | 41.0208 | 40.7251 | 40.2787 | 39.7303 | 39.1629 | 38.6345 | 38.1314 | 37.6619 | 35.5177 | 33.3293 | 31.1019
|  | JAYS CLOSE PRIMARY | EE |  |  |  |  | 44.7966 | 44.5756 | 44.3408 | 44.0935 | 43.8156 | 43.5377 | 43.2682 | 43.0029 | 42.7577 | 41.4303 | 39.9651 | 38.5808 | 39.7493 | 39.5293 | 39.2945 | 39.0303 | 38.584 | 38.1503 | 37.7135 | 37.2745 | 36.8608 | 35.1198 | 33.5577 | 31.8587 | 41.4608 | 41.2293 | 40.984 | 40.7272 | 40.4408 | 40.0008 | 39.5472 | 39.0914 | 38.6587 | 36.7987 | 35.1029 | 33.3451
|  | JAYS CLOSE PRIMARY | HT |  |  |  |  | 44.6461 | 44.3819 | 44.0998 | 43.8093 | 43.4851 | 43.1587 | 42.8651 | 42.5914 | 42.2419 | 40.3872 | 38.5545 | 36.7914 | 39.5987 | 39.3345 | 38.9208 | 38.4072 | 37.8714 | 37.3166 | 36.8029 | 36.3135 | 35.8598 | 33.8061 | 31.7261 | 29.5587 | 41.2998 | 41.0208 | 40.7251 | 40.2787 | 39.7303 | 39.1629 | 38.6345 | 38.1314 | 37.6619 | 35.5177 | 33.3293 | 31.1019
|  | JAYS CLOSE PRIMARY | HE |  |  |  |  | 44.9924 | 44.8324 | 44.6556 | 44.4661 | 44.2451 | 44.0356 | 43.8356 | 43.6461 | 43.4798 | 42.8577 | 42.4651 | 5.7093 | 39.9451 | 39.7851 | 39.6093 | 39.4198 | 39.2051 | 39.0019 | 38.8082 | 38.6261 | 38.3714 | 37.3314 | 36.5966 | 35.6366 | 41.664 | 41.504 | 41.3219 | 41.1261 | 40.9008 | 40.6851 | 40.4798 | 40.2861 | 40.1156 | 39.1261 | 38.3503 | 37.3472
|  | JAYS CLOSE PRIMARY | CF |  |  |  |  | 45.1303 | 45.0429 | 44.9524 | 44.8587 | 44.7524 | 44.6451 | 44.5398 | 44.4356 | 44.3324 | 43.8619 | 43.5945 | 43.4156 | 40.0829 | 39.9956 | 39.9051 | 39.8114 | 39.7082 | 39.604 | 39.5019 | 39.4019 | 39.3008 | 38.6493 | 38.0451 | 37.4851 | 41.8019 | 41.7145 | 41.624 | 41.5293 | 41.4198 | 41.3072 | 41.1987 | 41.0903 | 40.9829 | 40.4914 | 39.8672 | 39.2808
MINETY GSP | CIRENCESTER BSP | KEMBLE RAF PRIMARY | MINIMUM HEADROOM | ST 96064 96012 | YES | YES | 0 | 10.0916 | 10.0726 | 10.0537 | 10.0347 | 10.0147 | 9.9958 | 9.9758 | 9.9537 | 9.9326 | 9.8242 | 9.7095 | 7.4358 | 9.6989 | 9.6779 | 9.6558 | 9.6337 | 9.6116 | 9.5905 | 9.5684 | 9.5453 | 9.5232 | 9.4084 | 9.2905 | 9.1905 | 9.7105 | 9.7474 | 9.7253 | 9.7032 | 9.68 | 9.6579 | 9.6358 | 9.6105 | 9.5874 | 9.4653 | 9.3368 | 9.2337
|  | KEMBLE RAF PRIMARY | EE |  |  |  |  | 10.1042 | 10.0895 | 10.0747 | 10.0611 | 10.0442 | 10.0274 | 10.0095 | 9.9905 | 9.9716 | 9.8674 | 9.76 | 9.6874 | 9.7147 | 9.6968 | 9.68 | 9.6642 | 9.6463 | 9.6295 | 9.6105 | 9.5905 | 9.5716 | 9.4684 | 9.3621 | 9.2853 | 9.7832 | 9.7663 | 9.7495 | 9.7337 | 9.7137 | 9.6947 | 9.6747 | 9.6537 | 9.6337 | 9.52 | 9.4011 | 9.32
|  | KEMBLE RAF PRIMARY | HT |  |  |  |  | 10.0916 | 10.0726 | 10.0537 | 10.0347 | 10.0147 | 9.9958 | 9.9758 | 9.9537 | 9.9326 | 9.8242 | 9.7095 | 9.62 | 9.6989 | 9.6779 | 9.6558 | 9.6337 | 9.6116 | 9.5905 | 9.5684 | 9.5453 | 9.5232 | 9.4084 | 9.2905 | 9.1905 | 9.7684 | 9.7474 | 9.7253 | 9.7032 | 9.68 | 9.6579 | 9.6358 | 9.6105 | 9.5874 | 9.4653 | 9.3368 | 9.2337
|  | KEMBLE RAF PRIMARY | HE |  |  |  |  | 10.1168 | 10.1137 | 10.1063 | 10.0979 | 10.0863 | 10.0768 | 10.0663 | 10.0568 | 10.0463 | 9.9947 | 9.9474 | 7.4358 | 9.7295 | 9.7253 | 9.7158 | 9.7074 | 9.6947 | 9.6842 | 9.6737 | 9.6632 | 9.6526 | 9.5989 | 9.5505 | 9.5053 | 9.7979 | 9.7947 | 9.7853 | 9.7758 | 9.7632 | 9.7526 | 9.7411 | 9.7295 | 9.7179 | 9.6611 | 9.6084 | 9.56
|  | KEMBLE RAF PRIMARY | CF |  |  |  |  | 10.1179 | 10.1168 | 10.1168 | 10.1137 | 10.1063 | 10.1 | 10.0937 | 10.0842 | 10.0779 | 10.0453 | 10.0116 | 9.9779 | 9.7179 | 9.7295 | 9.7295 | 9.7253 | 9.7168 | 9.7105 | 9.7021 | 9.6926 | 9.6874 | 9.6505 | 9.6147 | 9.5789 | 9.7105 | 9.7979 | 9.7979 | 9.7947 | 9.7863 | 9.7789 | 9.7716 | 9.7611 | 9.7547 | 9.7168 | 9.6789 | 9.6411
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | KENNINGTON PRIMARY | MINIMUM HEADROOM | SP 52881 01094 | YES | YES | 1.0516 | 6.9326 | 6.8021 | 6.6631 | 6.381 | 6.0894 | 5.801 | 5.4873 | 5.3631 | 5.2484 | 4.5094 | 3.7231 | -3.099 | 5.2168 | 5.0863 | 4.9473 | 4.6357 | 4.3168 | 4.001 | 3.6526 | 3.5315 | 3.4189 | 2.641 | 1.7873 | 0.78837 | 5.5494 | 5.4189 | 5.2799 | 4.9694 | 4.6484 | 4.3315 | 3.9821 | 3.8578 | 3.7442 | 2.9515 | 2.0821 | 1.0768
|  | KENNINGTON PRIMARY | EE |  |  |  |  | 7.0136 | 6.9073 | 6.7957 | 6.6778 | 6.5526 | 6.4273 | 6.3105 | 6.1947 | 6.0515 | 5.3484 | 4.6505 | 3.9999 | 5.2978 | 5.1915 | 5.0799 | 4.9631 | 4.8389 | 4.7168 | 4.6021 | 4.4894 | 4.3399 | 3.5978 | 2.8421 | 2.1031 | 5.6305 | 5.5242 | 5.4126 | 5.2947 | 5.1694 | 5.0452 | 4.9273 | 4.8126 | 4.6599 | 3.8978 | 3.121 | 2.3757
|  | KENNINGTON PRIMARY | HT |  |  |  |  | 6.9326 | 6.8021 | 6.6631 | 6.381 | 6.0894 | 5.801 | 5.4873 | 5.3631 | 5.2484 | 4.5094 | 3.7231 | 2.8431 | 5.2168 | 5.0863 | 4.9473 | 4.6357 | 4.3168 | 4.001 | 3.6526 | 3.5315 | 3.4189 | 2.641 | 1.7873 | 0.78837 | 5.5494 | 5.4189 | 5.2799 | 4.9694 | 4.6484 | 4.3315 | 3.9821 | 3.8578 | 3.7442 | 2.9515 | 2.0821 | 1.0768
|  | KENNINGTON PRIMARY | HE |  |  |  |  | 7.1189 | 7.0463 | 6.9663 | 6.881 | 6.7842 | 6.6926 | 6.6052 | 6.5231 | 6.4515 | 6.0263 | 5.5389 | -3.099 | 5.4031 | 5.3305 | 5.2505 | 5.1652 | 5.0694 | 4.9799 | 4.8926 | 4.8126 | 4.7421 | 4.2905 | 3.7389 | 3.3715 | 5.7357 | 5.6631 | 5.5831 | 5.4978 | 5.401 | 5.3094 | 5.2221 | 5.1399 | 5.0694 | 4.6084 | 4.0515 | 3.6789
|  | KENNINGTON PRIMARY | CF |  |  |  |  | 7.1894 | 7.1536 | 7.1147 | 7.0757 | 7.0315 | 6.9894 | 6.9452 | 6.9031 | 6.861 | 6.5947 | 6.3094 | 6.0747 | 5.4736 | 5.4378 | 5.3989 | 5.3599 | 5.3168 | 5.2747 | 5.2315 | 5.1905 | 5.1473 | 4.8694 | 4.5484 | 4.2831 | 5.8063 | 5.7705 | 5.7315 | 5.6926 | 5.6484 | 5.6063 | 5.5621 | 5.5199 | 5.4778 | 5.1957 | 4.8726 | 4.6042
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | KENTWOOD HILL PRIMARY | MINIMUM HEADROOM | SU 67102 74048 | NO | YES | 0 | 31.7811 | 31.1611 | 30.5032 | 29.8242 | 28.7579 | 27.3905 | 26.3842 | 25.4495 | 24.5663 | 20.6821 | 16.7316 | -13.68 | 26.6821 | 25.5284 | 24.3505 | 23.1684 | 21.6832 | 20.2021 | 19.1305 | 18.1316 | 17.1947 | 13 | 8.6211 | 4.4905 | 27.8284 | 26.6579 | 25.4642 | 24.2663 | 22.7558 | 21.2505 | 20.1642 | 19.1516 | 18.2011 | 14 | 9.6274 | 5.5021
|  | KENTWOOD HILL PRIMARY | EE |  |  |  |  | 32.1537 | 31.6474 | 31.1084 | 30.5474 | 29.9663 | 29.2095 | 28.3695 | 27.5516 | 26.8084 | 23.8547 | 20.8832 | 18.1147 | 27.4737 | 26.5589 | 25.6179 | 24.6621 | 23.3937 | 22.1621 | 21.2705 | 20.4011 | 19.6074 | 16.4474 | 13.1432 | 10.0253 | 28.6211 | 27.7063 | 26.7516 | 25.7832 | 24.4937 | 23.2411 | 22.3379 | 21.4568 | 20.6526 | 17.4432 | 14.1432 | 11.0305
|  | KENTWOOD HILL PRIMARY | HT |  |  |  |  | 31.7811 | 31.1611 | 30.5032 | 29.8242 | 28.7579 | 27.3905 | 26.3842 | 25.4495 | 24.5663 | 20.6821 | 16.7316 | 13.04 | 26.6821 | 25.5284 | 24.3505 | 23.1684 | 21.6832 | 20.2021 | 19.1305 | 18.1316 | 17.1947 | 13 | 8.6211 | 4.4905 | 27.8284 | 26.6579 | 25.4642 | 24.2663 | 22.7558 | 21.2505 | 20.1642 | 19.1516 | 18.2011 | 14 | 9.6274 | 5.5021
|  | KENTWOOD HILL PRIMARY | HE |  |  |  |  | 32.6432 | 32.2884 | 31.8968 | 31.4737 | 31.0253 | 30.5947 | 30.1895 | 29.8095 | 29.4832 | 28.0705 | 26.1821 | -13.68 | 28.5263 | 27.9368 | 27.3084 | 26.6463 | 25.6547 | 24.6905 | 24.06 | 23.4589 | 22.9274 | 21.0032 | 18.9053 | 16.9158 | 29.2337 | 28.8632 | 28.4516 | 27.8 | 26.7926 | 25.8116 | 25.1747 | 24.5663 | 24.0284 | 22.0779 | 19.9326 | 17.9137
|  | KENTWOOD HILL PRIMARY | CF |  |  |  |  | 32.98 | 32.7968 | 32.6053 | 32.4074 | 32.2032 | 31.9937 | 31.7884 | 31.5853 | 31.3832 | 30.4789 | 29.78 | 28.5663 | 28.9116 | 28.7063 | 28.4032 | 28.0326 | 27.5347 | 27.0179 | 26.6432 | 26.2684 | 25.8947 | 24.1705 | 22.7253 | 21.3484 | 29.5863 | 29.3926 | 29.1895 | 28.98 | 28.6821 | 28.1684 | 27.7884 | 27.4084 | 27.0295 | 25.2789 | 23.8032 | 22.3895
COWLEY GSP | YARNTON BSP | KIDDINGTON PRIMARY | MINIMUM HEADROOM | SP 43362 24301 | NO | YES | 0.12105 | 26.1011 | 26.0737 | 26.0442 | 26.0137 | 25.9821 | 25.9347 | 25.8389 | 25.7516 | 25.6442 | 25.0253 | 24.3484 | 11.4263 | 23.6232 | 23.58 | 23.5358 | 23.48 | 23.3053 | 23.1179 | 22.9474 | 22.7937 | 22.6505 | 21.9821 | 21.2316 | 20.3905 | 24.2874 | 24.2558 | 24.2232 | 24.1884 | 24.0568 | 23.8726 | 23.7063 | 23.5558 | 23.4147 | 22.7579 | 21.9905 | 21.1295
|  | KIDDINGTON PRIMARY | EE |  |  |  |  | 26.52 | 26.44 | 26.7989 | 26.66 | 26.5116 | 26.3716 | 26.2379 | 26.1137 | 25.9989 | 25.5347 | 25.0368 | 24.4832 | 24.1811 | 24.0389 | 24.0126 | 23.8632 | 23.7032 | 23.5526 | 23.4074 | 23.2747 | 23.1516 | 22.6442 | 22.0779 | 21.4358 | 24.8874 | 24.7758 | 24.6895 | 24.5389 | 24.38 | 24.2295 | 24.0842 | 23.9516 | 23.8284 | 23.32 | 22.7537 | 22.1116
|  | KIDDINGTON PRIMARY | HT |  |  |  |  | 26.4621 | 26.3642 | 26.2611 | 26.1537 | 26.0442 | 25.9347 | 25.8389 | 25.7516 | 25.6442 | 25.0253 | 24.3484 | 23.6021 | 24.0568 | 23.8768 | 23.6842 | 23.4916 | 23.3053 | 23.1179 | 22.9474 | 22.7937 | 22.6505 | 21.9821 | 21.2316 | 20.3905 | 24.7937 | 24.6179 | 24.4284 | 24.24 | 24.0568 | 23.8726 | 23.7063 | 23.5558 | 23.4147 | 22.7579 | 21.9905 | 21.1295
|  | KIDDINGTON PRIMARY | HE |  |  |  |  | 26.5989 | 26.5432 | 26.4821 | 26.4168 | 26.3474 | 26.2789 | 26.2168 | 26.1579 | 26.1074 | 25.9368 | 25.84 | 11.4263 | 24.3484 | 24.2579 | 24.1547 | 24.0526 | 23.9421 | 23.8326 | 23.7326 | 23.6421 | 23.5621 | 23.2526 | 22.8695 | 22.4074 | 24.9663 | 24.9105 | 24.8495 | 24.7842 | 24.6789 | 24.5716 | 24.4737 | 24.3842 | 24.3053 | 24.0021 | 23.6316 | 23.1832
|  | KIDDINGTON PRIMARY | CF |  |  |  |  | 26.1011 | 26.0737 | 26.0442 | 26.0137 | 25.9821 | 25.9505 | 25.9189 | 25.8874 | 25.8558 | 25.7179 | 26.2 | 26.1253 | 23.6232 | 23.58 | 23.5358 | 23.48 | 23.42 | 23.3568 | 23.2979 | 23.2389 | 23.1779 | 22.9053 | 23.4495 | 23.1305 | 24.2874 | 24.2558 | 24.2232 | 24.1884 | 24.1537 | 24.1179 | 24.0821 | 24.0379 | 23.9779 | 23.7105 | 24.2021 | 23.8958
BRAMLEY (BASI) GSP | READING BSP | KIDMORE END PRIMARY | MINIMUM HEADROOM | SU 69953 78205 | NO | YES | 0 | 25.9716 | 25.7632 | 25.5063 | 25.1453 | 24.7758 | 24.3979 | 24.0516 | 23.7295 | 23.4305 | 22.1242 | 20.9432 | 9.4411 | 23.5789 | 23.1937 | 22.5611 | 22.1674 | 21.7674 | 21.3589 | 20.9821 | 20.6316 | 20.3063 | 18.8832 | 17.5684 | 16.3021 | 24.0821 | 23.6916 | 23.0453 | 22.6453 | 22.2389 | 21.8232 | 21.44 | 21.0821 | 20.7495 | 19.2874 | 17.9379 | 16.6642
|  | KIDMORE END PRIMARY | EE |  |  |  |  | 26.1053 | 25.9379 | 25.7611 | 25.5768 | 25.3074 | 25.0021 | 24.7105 | 24.4242 | 24.1674 | 23.1021 | 22.1758 | 21.4232 | 23.8505 | 23.5474 | 22.9947 | 22.6789 | 22.3558 | 22.0263 | 21.7105 | 21.4032 | 21.1263 | 19.9789 | 18.9695 | 18.1116 | 24.3579 | 24.0495 | 23.4853 | 23.1653 | 22.8368 | 22.5 | 22.1768 | 21.8621 | 21.5779 | 20.3905 | 19.3379 | 18.4537
|  | KIDMORE END PRIMARY | HT |  |  |  |  | 25.9716 | 25.7632 | 25.5063 | 25.1453 | 24.7758 | 24.3979 | 24.0516 | 23.7295 | 23.4305 | 22.1242 | 20.9432 | 19.84 | 23.5789 | 23.1937 | 22.5611 | 22.1674 | 21.7674 | 21.3589 | 20.9821 | 20.6316 | 20.3063 | 18.8832 | 17.5684 | 16.3021 | 24.0821 | 23.6916 | 23.0453 | 22.6453 | 22.2389 | 21.8232 | 21.44 | 21.0821 | 20.7495 | 19.2874 | 17.9379 | 16.6642
|  | KIDMORE END PRIMARY | HE |  |  |  |  | 26.2747 | 26.1621 | 26.0358 | 25.9021 | 25.7526 | 25.6095 | 25.4758 | 25.3495 | 25.2021 | 24.5558 | 24.04 | 9.4411 | 24.2042 | 24.0126 | 23.5684 | 23.3537 | 23.1253 | 22.8895 | 22.6653 | 22.4547 | 22.2653 | 21.5674 | 20.9895 | 20.4674 | 24.7021 | 24.5242 | 24.0695 | 23.8516 | 23.62 | 23.3789 | 23.1516 | 22.9358 | 22.7432 | 22.0253 | 21.4305 | 20.8884
|  | KIDMORE END PRIMARY | CF |  |  |  |  | 26.3863 | 26.3295 | 26.2716 | 26.2105 | 26.1442 | 26.0768 | 26.0116 | 25.9463 | 25.8821 | 25.5884 | 25.3032 | 24.9916 | 24.4389 | 24.3274 | 24.1105 | 23.9916 | 23.8663 | 23.7358 | 23.6053 | 23.4779 | 23.3505 | 22.7737 | 22.3474 | 21.9884 | 24.8221 | 24.7611 | 24.62 | 24.5 | 24.3726 | 24.2389 | 24.1074 | 23.9747 | 23.8463 | 23.2568 | 22.8179 | 22.4463
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | KINGS RIDE PRIMARY | MINIMUM HEADROOM | SU 87551 61530 | NO | YES | 0 | 28.2221 | 27.9968 | 27.7558 | 27.5084 | 27.2484 | 26.9874 | 26.7189 | 25.8537 | 25.0084 | 21.9168 | 20.3905 | 0.59895 | 24.9611 | 24.5684 | 23.7274 | 22.8053 | 21.7989 | 20.8011 | 19.8263 | 18.8484 | 17.8905 | 14.4189 | 12.7495 | 11.2705 | 25.4526 | 25.2158 | 24.7779 | 23.9053 | 22.9537 | 21.9989 | 21.0253 | 20.0463 | 19.0884 | 15.6116 | 13.9295 | 12.4463
|  | KINGS RIDE PRIMARY | EE |  |  |  |  | 28.3621 | 28.1779 | 27.9842 | 27.7811 | 27.5653 | 27.3558 | 27.1547 | 26.6179 | 25.7684 | 22.9537 | 21.78 | 20.7758 | 25.1316 | 24.9179 | 24.4063 | 23.7316 | 22.9295 | 22.1253 | 21.0232 | 19.6758 | 18.7095 | 15.5347 | 14.2705 | 13.1516 | 25.6011 | 25.4084 | 25.1937 | 24.7821 | 24.0232 | 23.2611 | 22.2189 | 20.8716 | 19.9042 | 16.7158 | 15.4347 | 14.3116
|  | KINGS RIDE PRIMARY | HT |  |  |  |  | 28.2221 | 27.9968 | 27.7558 | 27.5084 | 27.2484 | 26.9874 | 26.7189 | 25.8537 | 25.0084 | 21.9168 | 20.3905 | 19.0558 | 24.9611 | 24.5684 | 23.7274 | 22.8053 | 21.7989 | 20.8011 | 19.8263 | 18.8484 | 17.8905 | 14.4189 | 12.7495 | 11.2705 | 25.4526 | 25.2158 | 24.7779 | 23.9053 | 22.9537 | 21.9989 | 21.0253 | 20.0463 | 19.0884 | 15.6116 | 13.9295 | 12.4463
|  | KINGS RIDE PRIMARY | HE |  |  |  |  | 28.5295 | 28.3968 | 28.2516 | 28.0947 | 27.9232 | 27.76 | 27.6063 | 27.4632 | 26.8726 | 24.5379 | 23.7779 | 0.59895 | 25.2989 | 25.1663 | 24.9821 | 24.42 | 23.7084 | 23.0032 | 21.9484 | 20.7105 | 19.9063 | 17.2442 | 16.3916 | 15.6958 | 25.7811 | 25.6432 | 25.48 | 25.2989 | 24.7716 | 24.1053 | 23.1179 | 21.9084 | 21.1042 | 18.4389 | 17.58 | 16.88
|  | KINGS RIDE PRIMARY | CF |  |  |  |  | 28.6453 | 28.5747 | 28.5 | 28.4242 | 28.3442 | 28.2611 | 28.18 | 28.1 | 28.0189 | 27.4579 | 26.8663 | 26.4179 | 25.4147 | 25.3442 | 25.2695 | 25.1937 | 25.1137 | 25.0326 | 24.9158 | 24.5074 | 24.0158 | 20.5358 | 19.8758 | 19.3726 | 25.9021 | 25.8274 | 25.7495 | 25.6695 | 25.5863 | 25.4989 | 25.4095 | 25.3095 | 25.0611 | 21.7347 | 21.0726 | 20.5663
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINGSCLERE PRIMARY | MINIMUM HEADROOM | SU 51982 59358 | NO | YES | 0 | 11.9074 | 11.7168 | 11.5242 | 11.3274 | 10.9789 | 10.5021 | 9.9295 | 9.8295 | 9.7358 | 8.6821 | 7.3274 | 0.46316 | 9.5737 | 9.3684 | 9.1621 | 8.9516 | 8.5621 | 8.0253 | 7.3705 | 7.2726 | 7.18 | 6.0137 | 4.4789 | 4.0463 | 10.1568 | 9.9526 | 9.7453 | 9.5358 | 9.1474 | 8.6095 | 7.9558 | 7.8558 | 7.7621 | 6.5926 | 5.0526 | 4.6179
|  | KINGSCLERE PRIMARY | EE |  |  |  |  | 11.9768 | 11.8853 | 11.7284 | 11.5716 | 11.4105 | 11.2537 | 11.1042 | 10.9621 | 10.8263 | 10.2695 | 9.0537 | 8.2242 | 9.7147 | 9.5516 | 9.3842 | 9.2168 | 9.0453 | 8.8811 | 8.7232 | 8.5726 | 8.4305 | 7.8421 | 6.4621 | 5.5147 | 10.2979 | 10.1347 | 9.9674 | 9.8 | 9.6295 | 9.4621 | 9.3042 | 9.1526 | 9.0084 | 8.4116 | 7.0232 | 6.0758
|  | KINGSCLERE PRIMARY | HT |  |  |  |  | 11.9074 | 11.7168 | 11.5242 | 11.3274 | 10.9789 | 10.5021 | 9.9295 | 9.8295 | 9.7358 | 8.6821 | 7.3274 | 6.9232 | 9.5737 | 9.3684 | 9.1621 | 8.9516 | 8.5621 | 8.0253 | 7.3705 | 7.2726 | 7.18 | 6.0137 | 4.4789 | 4.0463 | 10.1568 | 9.9526 | 9.7453 | 9.5358 | 9.1474 | 8.6095 | 7.9558 | 7.8558 | 7.7621 | 6.5926 | 5.0526 | 4.6179
|  | KINGSCLERE PRIMARY | HE |  |  |  |  | 12.0611 | 12 | 11.9316 | 11.8947 | 11.78 | 11.6705 | 11.5653 | 11.4684 | 11.38 | 11.0432 | 10.1158 | 0.46316 | 9.9021 | 9.7968 | 9.6863 | 9.5684 | 9.4484 | 9.3337 | 9.2232 | 9.1221 | 9.0284 | 8.6726 | 7.6053 | 6.8411 | 10.4842 | 10.3789 | 10.2695 | 10.1516 | 10.0305 | 9.9158 | 9.8042 | 9.7021 | 9.6084 | 9.2495 | 8.1821 | 7.4168
|  | KINGSCLERE PRIMARY | CF |  |  |  |  | 12.12 | 12.0884 | 12.0547 | 12.02 | 11.9842 | 11.9474 | 11.9095 | 11.8737 | 11.8126 | 11.5263 | 11.1768 | 10.6863 | 10.0011 | 9.9411 | 9.8779 | 9.8147 | 9.7484 | 9.68 | 9.6105 | 9.5453 | 9.4768 | 9.1695 | 8.7747 | 8.2084 | 10.5832 | 10.5232 | 10.4611 | 10.3979 | 10.3305 | 10.2621 | 10.1937 | 10.1274 | 10.0589 | 9.7505 | 9.3547 | 8.7874
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINTBURY PRIMARY | MINIMUM HEADROOM | SU 37657 67143 | NO | YES | 0 | 10.9084 | 10.7716 | 10.6326 | 10.4916 | 10.3505 | 10.2137 | 10.0895 | 9.9716 | 9.8674 | 9.4021 | 8.9432 | 2.6232 | 10.0063 | 9.8495 | 9.6895 | 9.5284 | 9.3684 | 9.2137 | 9.0726 | 8.9379 | 8.8189 | 8.2779 | 7.7158 | 7.1832 | 10.2537 | 10.0958 | 9.9368 | 9.7747 | 9.6158 | 9.4611 | 9.3189 | 9.1853 | 9.0663 | 8.5253 | 7.9632 | 7.4305
|  | KINTBURY PRIMARY | EE |  |  |  |  | 11.0011 | 10.8905 | 10.7789 | 10.6653 | 10.5495 | 10.4389 | 10.3347 | 10.2347 | 10.1463 | 9.7947 | 9.4474 | 9.12 | 10.1158 | 9.9884 | 9.8621 | 9.7326 | 9.6021 | 9.4768 | 9.3589 | 9.2453 | 9.1463 | 8.74 | 8.3116 | 7.8947 | 10.3632 | 10.2358 | 10.1095 | 9.98 | 9.8484 | 9.7242 | 9.6063 | 9.4926 | 9.3937 | 8.9874 | 8.5589 | 8.1421
|  | KINTBURY PRIMARY | HT |  |  |  |  | 10.9084 | 10.7716 | 10.6326 | 10.4916 | 10.3505 | 10.2137 | 10.0895 | 9.9716 | 9.8674 | 9.4021 | 8.9432 | 8.5168 | 10.0063 | 9.8495 | 9.6895 | 9.5284 | 9.3684 | 9.2137 | 9.0726 | 8.9379 | 8.8189 | 8.2779 | 7.7158 | 7.1832 | 10.2537 | 10.0958 | 9.9368 | 9.7747 | 9.6158 | 9.4611 | 9.3189 | 9.1853 | 9.0663 | 8.5253 | 7.9632 | 7.4305
|  | KINTBURY PRIMARY | HE |  |  |  |  | 11.0905 | 11.04 | 10.9768 | 10.8958 | 10.8147 | 10.7368 | 10.6611 | 10.5895 | 10.5316 | 10.32 | 10.0979 | 2.6232 | 10.2137 | 10.1621 | 10.0937 | 10.0042 | 9.9137 | 9.8274 | 9.7432 | 9.6632 | 9.5989 | 9.3611 | 9.0832 | 8.8095 | 10.4611 | 10.4095 | 10.3411 | 10.2516 | 10.1611 | 10.0737 | 9.9905 | 9.9105 | 9.8463 | 9.6074 | 9.3305 | 9.0558
|  | KINTBURY PRIMARY | CF |  |  |  |  | 11.1389 | 11.1147 | 11.0895 | 11.0611 | 11.0284 | 10.9863 | 10.9453 | 10.9021 | 10.8632 | 10.6716 | 10.5158 | 10.3747 | 10.2632 | 10.2379 | 10.2126 | 10.1842 | 10.1495 | 10.1011 | 10.0537 | 10.0053 | 9.96 | 9.7389 | 9.5442 | 9.36 | 10.5116 | 10.4863 | 10.4611 | 10.4316 | 10.3968 | 10.3484 | 10.3011 | 10.2526 | 10.2074 | 9.9863 | 9.7916 | 9.6074
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | KNOWL HILL PRIMARY | MINIMUM HEADROOM | SU 82849 79105 | NO | YES | 0.68421 | 6.6689 | 6.6121 | 6.5532 | 6.4932 | 6.4195 | 6.2089 | 5.8668 | 5.8037 | 5.7437 | 5.0553 | 4.1637 | -0.12789 | 5.6995 | 5.5932 | 5.4868 | 5.3816 | 5.1016 | 4.7868 | 4.3995 | 4.3395 | 4.2816 | 3.5553 | 2.5795 | 2.3111 | 5.8405 | 5.7816 | 5.7079 | 5.5995 | 5.31 | 4.9868 | 4.5868 | 4.5237 | 4.4637 | 3.7037 | 2.6984 | 2.4205
|  | KNOWL HILL PRIMARY | EE |  |  |  |  | 6.7037 | 7.0521 | 6.97 | 6.8868 | 6.7942 | 6.6995 | 6.6121 | 6.5005 | 6.3932 | 5.8805 | 5.0995 | 4.5689 | 5.7711 | 5.7226 | 5.6363 | 5.5458 | 5.4521 | 5.3563 | 5.2689 | 5.1532 | 5.0447 | 4.5279 | 3.6963 | 3.1068 | 5.8774 | 5.9111 | 5.8237 | 5.7353 | 5.6374 | 5.5374 | 5.4447 | 5.3247 | 5.2111 | 4.6563 | 3.7837 | 3.1805
|  | KNOWL HILL PRIMARY | HT |  |  |  |  | 6.6689 | 6.6121 | 6.5532 | 6.4932 | 6.4195 | 6.2089 | 5.8668 | 5.8037 | 5.7437 | 5.0553 | 4.1637 | 3.9037 | 5.6995 | 5.5932 | 5.4868 | 5.3816 | 5.1016 | 4.7868 | 4.3995 | 4.3395 | 4.2816 | 3.5553 | 2.5795 | 2.3111 | 5.8405 | 5.7816 | 5.7079 | 5.5995 | 5.31 | 4.9868 | 4.5868 | 4.5237 | 4.4637 | 3.7037 | 2.6984 | 2.4205
|  | KNOWL HILL PRIMARY | HE |  |  |  |  | 6.7489 | 6.7174 | 6.6858 | 6.6489 | 6.6016 | 6.5584 | 6.5163 | 6.4753 | 6.4395 | 6.2953 | 5.9121 | -0.12789 | 5.8584 | 5.8121 | 5.7563 | 5.6974 | 5.6279 | 5.5637 | 5.5005 | 5.43 | 5.3637 | 5.0363 | 4.4847 | 4.0132 | 5.9258 | 5.8932 | 5.8605 | 5.8216 | 5.7732 | 5.73 | 5.6868 | 5.6437 | 5.5753 | 5.2311 | 4.6542 | 4.1637
|  | KNOWL HILL PRIMARY | CF |  |  |  |  | 6.7795 | 6.7637 | 6.7479 | 6.7311 | 6.7089 | 6.6889 | 6.6689 | 6.6479 | 6.6289 | 6.5363 | 6.4774 | 6.2637 | 5.8921 | 5.8742 | 5.8563 | 5.8258 | 5.7889 | 5.7532 | 5.7142 | 5.6795 | 5.6374 | 5.4226 | 5.1995 | 4.8511 | 5.9584 | 5.9416 | 5.9247 | 5.9068 | 5.8847 | 5.8637 | 5.8416 | 5.8205 | 5.8005 | 5.6342 | 5.4005 | 5.0363
FLEET-BRAMLEY GSP | ALDERSHOT BSP | LABURNUM ROAD PRIMARY | MINIMUM HEADROOM | SU 86017 50475 | NO | YES | 0 | 54.81 | 54.5047 | 53.7879 | 51.9384 | 50.5868 | 49.3837 | 48.4332 | 47.51 | 46.6268 | 43.7679 | 41.5353 | 6.6763 | 48.0647 | 46.0374 | 43.6279 | 41.4689 | 39.9132 | 38.5363 | 37.4563 | 36.4068 | 35.4174 | 32.2553 | 29.7837 | 27.49 | 49.7605 | 47.8363 | 45.4268 | 43.2668 | 41.71 | 40.3321 | 39.2511 | 38.2037 | 37.2121 | 34.0479 | 31.5742 | 29.2774
|  | LABURNUM ROAD PRIMARY | EE |  |  |  |  | 54.9879 | 54.7363 | 54.3595 | 52.6121 | 51.3605 | 50.2668 | 49.3963 | 48.5405 | 47.7321 | 45.3163 | 43.6079 | 42.0805 | 48.4584 | 46.5489 | 44.2584 | 42.2111 | 40.7626 | 39.5047 | 38.5111 | 37.5353 | 36.6184 | 33.9405 | 32.0447 | 30.3321 | 50.0479 | 48.3416 | 46.0563 | 44.0089 | 42.5605 | 41.3005 | 40.3079 | 39.33 | 38.4142 | 35.7321 | 33.8342 | 32.1205
|  | LABURNUM ROAD PRIMARY | HT |  |  |  |  | 54.81 | 54.5047 | 53.7879 | 51.9384 | 50.5868 | 49.3837 | 48.4332 | 47.51 | 46.6268 | 43.7679 | 41.5353 | 39.4795 | 48.0647 | 46.0374 | 43.6279 | 41.4689 | 39.9132 | 38.5363 | 37.4563 | 36.4068 | 35.4174 | 32.2553 | 29.7837 | 27.49 | 49.7605 | 47.8363 | 45.4268 | 43.2668 | 41.71 | 40.3321 | 39.2511 | 38.2037 | 37.2121 | 34.0479 | 31.5742 | 29.2774
|  | LABURNUM ROAD PRIMARY | HE |  |  |  |  | 55.1953 | 55.0037 | 54.7921 | 53.4468 | 52.3111 | 51.3353 | 50.5816 | 49.8489 | 49.1721 | 47.3889 | 46.2847 | 6.6763 | 48.9553 | 47.1953 | 45.0479 | 43.1395 | 41.8195 | 40.6911 | 39.83 | 38.9889 | 38.2089 | 36.2068 | 34.9742 | 33.9026 | 50.2553 | 48.9679 | 46.8458 | 44.9374 | 43.6174 | 42.4889 | 41.6258 | 40.7847 | 40.0047 | 38.0005 | 36.7679 | 35.6953
|  | LABURNUM ROAD PRIMARY | CF |  |  |  |  | 55.3458 | 55.2353 | 55.1205 | 55.0026 | 54.8805 | 54.7542 | 54.6321 | 54.51 | 54.2837 | 52.8826 | 52.0668 | 51.4005 | 49.4721 | 48.6784 | 47.6858 | 46.8311 | 46.2342 | 45.6679 | 45.1921 | 44.6911 | 44.1837 | 42.6079 | 41.6805 | 40.9089 | 50.4058 | 50.2953 | 49.4311 | 48.6226 | 48.0332 | 47.4668 | 46.99 | 46.4889 | 45.9826 | 44.4047 | 43.4774 | 42.7047
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LAMBOURN PRIMARY | MINIMUM HEADROOM | SU 33280 78217 | NO | YES | 0 | 9.6484 | 26.0421 | 25.9295 | 25.8137 | 25.6926 | 25.5726 | 25.4674 | 25.3726 | 25.2842 | 24.9295 | 24.3632 | -32.9137 | 7.8053 | 24.1147 | 23.9221 | 23.7274 | 23.5295 | 23.3284 | 23.1442 | 22.9768 | 22.8211 | 22.1211 | 21.3958 | 20.7126 | 7.9747 | 24.3632 | 24.2453 | 24.1242 | 23.9295 | 23.7284 | 23.5453 | 23.3779 | 23.2221 | 22.5221 | 21.7958 | 21.1126
|  | LAMBOURN PRIMARY | EE |  |  |  |  | 9.7116 | 26.1242 | 26.0295 | 25.9347 | 25.8337 | 25.7379 | 25.6463 | 25.5589 | 25.4811 | 25.2011 | 25.0126 | 24.6116 | 7.9316 | 24.2811 | 24.1242 | 23.9684 | 23.8105 | 23.66 | 23.5105 | 23.3653 | 23.2305 | 22.7 | 22.1579 | 21.6516 | 8.0421 | 24.4505 | 24.3516 | 24.2526 | 24.1484 | 24.0484 | 23.9116 | 23.7663 | 23.6305 | 23.1 | 22.5589 | 22.0516
|  | LAMBOURN PRIMARY | HT |  |  |  |  | 9.6484 | 26.0421 | 25.9295 | 25.8137 | 25.6926 | 25.5726 | 25.4674 | 25.3726 | 25.2842 | 24.9295 | 24.3632 | 23.7505 | 7.8053 | 24.1147 | 23.9221 | 23.7274 | 23.5295 | 23.3284 | 23.1442 | 22.9768 | 22.8211 | 22.1211 | 21.3958 | 20.7126 | 7.9747 | 24.3632 | 24.2453 | 24.1242 | 23.9295 | 23.7284 | 23.5453 | 23.3779 | 23.2221 | 22.5221 | 21.7958 | 21.1126
|  | LAMBOURN PRIMARY | HE |  |  |  |  | 9.7958 | 26.2337 | 26.1674 | 26.0947 | 26.0168 | 25.9421 | 25.8716 | 25.8084 | 25.7505 | 25.5632 | 25.4547 | -32.9137 | 8.0211 | 24.4568 | 24.3874 | 24.2937 | 24.1811 | 24.0726 | 23.9705 | 23.8758 | 23.7937 | 23.4968 | 23.1621 | 22.8411 | 8.1326 | 24.5674 | 24.4989 | 24.4242 | 24.3442 | 24.2663 | 24.1937 | 24.1284 | 24.0695 | 23.8747 | 23.5632 | 23.2421
|  | LAMBOURN PRIMARY | CF |  |  |  |  | 9.8547 | 26.3232 | 26.2895 | 26.2568 | 26.2211 | 26.1853 | 26.1505 | 26.1147 | 26.0789 | 25.9242 | 25.8463 | 25.8042 | 8.0821 | 24.5495 | 24.5137 | 24.48 | 24.4421 | 24.4053 | 24.3474 | 24.2874 | 24.2284 | 23.9568 | 23.7263 | 23.4905 | 8.1937 | 24.6611 | 24.6253 | 24.5905 | 24.5537 | 24.5158 | 24.48 | 24.4421 | 24.4053 | 24.2421 | 24.1274 | 23.8916
FAWLEY GSP | LANGLEY BSP | LANGLEY PRIMARY | MINIMUM HEADROOM | SU 45158 01418 | NO | YES | 0 | 13.4263 | 13.0789 | 13.1074 | 12.8105 | 12.6747 | 12.0253 | 11.2411 | 10.7347 | 9.8379 | 8.9432 | 7.4116 | -12.0463 | 13.0232 | 12.6063 | 12.6547 | 12.3189 | 12.24 | 11.4379 | 10.5074 | 9.9537 | 8.9389 | 8.0221 | 6.3221 | 4.6947 | 13.1989 | 12.7895 | 12.8368 | 12.5011 | 12.3168 | 11.5084 | 10.5695 | 10.0105 | 8.9884 | 8.0674 | 6.3653 | 4.7389
|  | LANGLEY PRIMARY | EE |  |  |  |  | 13.6568 | 13.3874 | 13.1074 | 12.8105 | 13.2084 | 12.9168 | 12.4453 | 11.8779 | 11.2337 | 10.0863 | 8.9116 | 7.8189 | 13.3147 | 12.9874 | 12.6547 | 12.3189 | 12.8642 | 12.5368 | 11.96 | 11.2442 | 10.4958 | 9.2653 | 7.9663 | 6.7316 | 13.4179 | 13.1621 | 12.8368 | 12.5011 | 12.9442 | 12.6158 | 12.0337 | 11.3116 | 10.5547 | 9.3105 | 8.0032 | 6.7674
|  | LANGLEY PRIMARY | HT |  |  |  |  | 13.4263 | 13.0789 | 13.4095 | 13.0442 | 12.6747 | 12.0253 | 11.2411 | 10.7347 | 9.8379 | 8.9432 | 7.4116 | 5.9632 | 13.0232 | 12.6063 | 13.0684 | 12.6547 | 12.24 | 11.4379 | 10.5074 | 9.9537 | 8.9389 | 8.0221 | 6.3221 | 4.6947 | 13.1989 | 12.7895 | 13.1495 | 12.7337 | 12.3168 | 11.5084 | 10.5695 | 10.0105 | 8.9884 | 8.0674 | 6.3653 | 4.7389
|  | LANGLEY PRIMARY | HE |  |  |  |  | 13.9589 | 13.7811 | 13.5926 | 13.3958 | 13.8863 | 13.6853 | 13.3684 | 13.0074 | 12.6684 | 11.6063 | 10.8158 | -12.0463 | 13.6316 | 13.4505 | 13.2537 | 13.0368 | 13.6747 | 13.4442 | 13.0537 | 12.6074 | 12.1821 | 10.9021 | 10.0211 | 9.18 | 13.6842 | 13.5211 | 13.3474 | 13.1642 | 13.7611 | 13.5284 | 13.1358 | 12.6853 | 12.2568 | 10.9632 | 10.0737 | 9.2232
|  | LANGLEY PRIMARY | CF |  |  |  |  | 14.1411 | 14.0411 | 13.94 | 13.8358 | 13.7274 | 13.62 | 13.5137 | 13.3937 | 13.9642 | 12.9968 | 12.5274 | 12.0589 | 13.8158 | 13.7147 | 13.6116 | 13.5063 | 13.3916 | 13.2789 | 13.1537 | 13.0032 | 13.7147 | 12.4947 | 11.9074 | 11.3442 | 13.8484 | 13.7589 | 13.6684 | 13.5747 | 13.4768 | 13.3789 | 13.2821 | 13.1737 | 13.7989 | 12.5684 | 11.9747 | 11.4042
FLEET-BRAMLEY GSP | FERNHURST BSP | LANGLEY COURT PRIMARY | MINIMUM HEADROOM | SU 80847 29056 | NO | YES | 0 | 26.4863 | 26.3126 | 26.1263 | 25.9368 | 25.7389 | 25.4116 | 25.1189 | 24.8084 | 24.4737 | 22.8263 | 21.2316 | 7.6158 | 23.6832 | 23.3579 | 23.0053 | 22.6021 | 22.1884 | 21.8253 | 21.5137 | 21.1768 | 20.8105 | 18.9989 | 17.2432 | 15.5874 | 24.2558 | 23.9621 | 23.6442 | 23.2663 | 22.8453 | 22.4768 | 22.16 | 21.8168 | 21.4432 | 19.5926 | 17.7947 | 16.1105
|  | LANGLEY COURT PRIMARY | EE |  |  |  |  | 26.5947 | 26.4526 | 26.3021 | 26.1453 | 25.9821 | 25.8274 | 25.68 | 25.5274 | 25.2516 | 23.96 | 22.7011 | 21.5368 | 23.9084 | 23.6495 | 23.3779 | 23.0579 | 22.7389 | 22.4705 | 22.2316 | 21.9621 | 21.6611 | 20.2305 | 18.8347 | 17.5411 | 24.4558 | 24.2221 | 23.9758 | 23.6905 | 23.4042 | 23.1337 | 22.8905 | 22.6168 | 22.3116 | 20.8484 | 19.4168 | 18.0884
|  | LANGLEY COURT PRIMARY | HT |  |  |  |  | 26.4863 | 26.3126 | 26.1263 | 25.9368 | 25.7389 | 25.4116 | 25.1189 | 24.8084 | 24.4737 | 22.8263 | 21.2316 | 19.7484 | 23.6832 | 23.3579 | 23.0053 | 22.6021 | 22.1884 | 21.8253 | 21.5137 | 21.1768 | 20.8105 | 18.9989 | 17.2432 | 15.5874 | 24.2558 | 23.9621 | 23.6442 | 23.2663 | 22.8453 | 22.4768 | 22.16 | 21.8168 | 21.4432 | 19.5926 | 17.7947 | 16.1105
|  | LANGLEY COURT PRIMARY | HE |  |  |  |  | 26.7358 | 26.6368 | 26.5295 | 26.4126 | 26.2874 | 26.1684 | 26.0558 | 25.9516 | 25.8611 | 25.1442 | 24.1916 | 7.6158 | 24.2074 | 24.0411 | 23.8579 | 23.62 | 23.38 | 23.1874 | 23.0211 | 22.8253 | 22.5968 | 21.5116 | 20.4284 | 19.4284 | 24.7221 | 24.5695 | 24.4021 | 24.1905 | 23.9737 | 23.7979 | 23.6421 | 23.4642 | 23.2611 | 22.1516 | 21.04 | 20.0105
|  | LANGLEY COURT PRIMARY | CF |  |  |  |  | 26.8305 | 26.7811 | 26.7295 | 26.6768 | 26.6211 | 26.5642 | 26.5084 | 26.4526 | 26.3979 | 26.1526 | 25.7674 | 25.2337 | 24.4579 | 24.3463 | 24.2274 | 24.1032 | 23.9716 | 23.8484 | 23.7379 | 23.6337 | 23.5242 | 22.8547 | 22.1589 | 21.5463 | 24.9 | 24.8411 | 24.7358 | 24.6263 | 24.5105 | 24.4021 | 24.3042 | 24.2095 | 24.1116 | 23.5179 | 22.8053 | 22.1758
AXMINSTER GSP | YEOVIL BSP | LARKHILL PRIMARY | MINIMUM HEADROOM | ST 53677 16914 | NO | YES | 0 | 32.5989 | 32.3179 | 32.0116 | 31.5042 | 30.9968 | 30.4979 | 30.04 | 29.6095 | 29.2116 | 27.0484 | 25.1 | 7.5979 | 29.4 | 28.86 | 28.3095 | 27.7611 | 27.2179 | 26.6832 | 26.1895 | 25.7263 | 25.2979 | 22.9011 | 20.7137 | 18.3947 | 30.1179 | 29.5958 | 29.0642 | 28.5337 | 28.0053 | 27.4853 | 27.0063 | 26.5568 | 26.14 | 23.8232 | 21.6284 | 19.3042
|  | LARKHILL PRIMARY | EE |  |  |  |  | 32.7621 | 32.5295 | 32.2811 | 32.0221 | 31.7 | 31.2989 | 30.9105 | 30.5358 | 30.1968 | 28.5211 | 27.0463 | 25.4842 | 29.7621 | 29.3284 | 28.8842 | 28.4379 | 27.9905 | 27.5621 | 27.1474 | 26.7463 | 26.3821 | 24.54 | 22.8916 | 21.0926 | 30.4653 | 30.0463 | 29.6158 | 29.1842 | 28.7474 | 28.3305 | 27.9263 | 27.5358 | 27.1821 | 25.4042 | 23.7979 | 21.9937
|  | LARKHILL PRIMARY | HT |  |  |  |  | 32.5989 | 32.3179 | 32.0116 | 31.5042 | 30.9968 | 30.4979 | 30.04 | 29.6095 | 29.2116 | 27.0484 | 25.1 | 23.0737 | 29.4 | 28.86 | 28.3095 | 27.7611 | 27.2179 | 26.6832 | 26.1895 | 25.7263 | 25.2979 | 22.9011 | 20.7137 | 18.3947 | 30.1179 | 29.5958 | 29.0642 | 28.5337 | 28.0053 | 27.4853 | 27.0063 | 26.5568 | 26.14 | 23.8232 | 21.6284 | 19.3042
|  | LARKHILL PRIMARY | HE |  |  |  |  | 32.9789 | 32.8137 | 32.6305 | 32.4326 | 32.2211 | 32.0179 | 31.8253 | 31.6463 | 31.4916 | 30.4726 | 29.5284 | 7.5979 | 30.2474 | 29.9632 | 29.6621 | 29.3526 | 29.0316 | 28.7295 | 28.4368 | 28.1611 | 27.92 | 26.6821 | 25.6095 | 24.3337 | 30.8716 | 30.6558 | 30.3632 | 30.0611 | 29.7474 | 29.4516 | 29.1653 | 28.8968 | 28.6621 | 27.4705 | 26.4495 | 25.2505
|  | LARKHILL PRIMARY | CF |  |  |  |  | 33.1326 | 33.0463 | 32.9558 | 32.8621 | 32.7642 | 32.6642 | 32.5663 | 32.4695 | 32.3726 | 31.8832 | 31.22 | 30.4937 | 30.5232 | 30.3558 | 30.1853 | 30.0084 | 29.8263 | 29.6453 | 29.4621 | 29.2832 | 29.1042 | 28.1737 | 27.4221 | 26.5758 | 31.0326 | 30.9411 | 30.8453 | 30.7011 | 30.5242 | 30.3484 | 30.1726 | 29.9989 | 29.8263 | 28.9305 | 28.2158 | 27.4189
COWLEY GSP | WITNEY BSP | LEAFIELD PRIMARY | MINIMUM HEADROOM | SP 30282 15270 | NO | YES | 0 | 6.1295 | 6.0337 | 5.8811 | 5.7095 | 5.5389 | 5.3716 | 5.2179 | 5.0768 | 4.9432 | 4.3274 | 3.6768 | -2.2474 | 4.9453 | 4.7684 | 4.5821 | 4.3989 | 4.2179 | 4.04 | 3.8779 | 3.7263 | 3.5842 | 2.9179 | 2.1968 | 1.4726 | 5.0716 | 4.8926 | 4.7032 | 4.5179 | 4.3347 | 4.1547 | 3.9895 | 3.8368 | 3.6926 | 3.0147 | 2.2789 | 1.5368
|  | LEAFIELD PRIMARY | EE |  |  |  |  | 6.1874 | 6.1095 | 6.0253 | 5.9284 | 5.7884 | 5.6547 | 5.5274 | 5.4053 | 5.2884 | 4.8242 | 4.3495 | 3.8484 | 5.0684 | 4.9284 | 4.7779 | 4.6358 | 4.4874 | 4.3453 | 4.2105 | 4.0811 | 3.9568 | 3.4558 | 2.9295 | 2.3632 | 5.1968 | 5.0547 | 4.9021 | 4.7589 | 4.6084 | 4.4642 | 4.3274 | 4.1968 | 4.0705 | 3.5621 | 3.0242 | 2.4442
|  | LEAFIELD PRIMARY | HT |  |  |  |  | 6.1295 | 6.0337 | 5.8811 | 5.7095 | 5.5389 | 5.3716 | 5.2179 | 5.0768 | 4.9432 | 4.3274 | 3.6768 | 3.0305 | 4.9453 | 4.7684 | 4.5821 | 4.3989 | 4.2179 | 4.04 | 3.8779 | 3.7263 | 3.5842 | 2.9179 | 2.1968 | 1.4726 | 5.0716 | 4.8926 | 4.7032 | 4.5179 | 4.3347 | 4.1547 | 3.9895 | 3.8368 | 3.6926 | 3.0147 | 2.2789 | 1.5368
|  | LEAFIELD PRIMARY | HE |  |  |  |  | 6.2653 | 6.2105 | 6.1505 | 6.0853 | 6.0168 | 5.9505 | 5.8884 | 5.8305 | 5.7747 | 5.4842 | 5.1684 | -2.2474 | 5.1674 | 5.1084 | 5.0432 | 4.9505 | 4.8463 | 4.7463 | 4.6505 | 4.5621 | 4.4821 | 4.1726 | 3.8189 | 3.4158 | 5.36 | 5.2747 | 5.1758 | 5.0779 | 4.9737 | 4.8716 | 4.7758 | 4.6863 | 4.6053 | 4.2905 | 3.9295 | 3.5158
|  | LEAFIELD PRIMARY | CF |  |  |  |  | 6.3179 | 6.2905 | 6.2611 | 6.2316 | 6.2 | 6.1684 | 6.1379 | 6.1074 | 6.0768 | 5.9011 | 5.6958 | 5.4621 | 5.2253 | 5.1947 | 5.1621 | 5.1284 | 5.0926 | 5.0347 | 4.9811 | 4.9263 | 4.8695 | 4.6042 | 4.3758 | 4.1095 | 5.4147 | 5.3863 | 5.3474 | 5.2863 | 5.2253 | 5.1632 | 5.1084 | 5.0526 | 4.9947 | 4.7263 | 4.4916 | 4.2179
WILLESDEN GSP | ACTON LANE BSP | LEAMINGTON PARK PRIMARY | MINIMUM HEADROOM | TQ 20539 81536 | NO | NO | 0 | 49.6674 | 47.9737 | 45.7189 | 44.1474 | 41.8084 | 40.7842 | 39.7684 | 38.7611 | 37.6095 | 34.6147 | 33.7916 | 20.8442 | 50.9568 | 48.8474 | 46.1937 | 44.3495 | 41.5979 | 40.4011 | 39.2137 | 38.0358 | 36.6853 | 33.1947 | 32.2663 | 31.5547 | 48.4916 | 46.4116 | 43.7653 | 41.9263 | 39.1832 | 37.9895 | 36.8053 | 35.6305 | 34.2853 | 30.8042 | 29.8768 | 29.1674
|  | LEAMINGTON PARK PRIMARY | EE |  |  |  |  | 49.8126 | 48.2747 | 46.2537 | 44.9379 | 43.1063 | 42.3663 | 41.5642 | 40.5768 | 39.4137 | 36.5853 | 35.9747 | 35.5432 | 51.1295 | 49.1926 | 46.8126 | 45.2674 | 43.1126 | 42.2495 | 41.3126 | 40.1558 | 38.7905 | 35.4853 | 34.7937 | 34.3053 | 48.6621 | 46.7558 | 44.3821 | 42.8421 | 40.6937 | 39.8326 | 38.8989 | 37.7453 | 36.3842 | 33.0884 | 32.3979 | 31.9105
|  | LEAMINGTON PARK PRIMARY | HT |  |  |  |  | 49.6674 | 47.9737 | 45.7189 | 44.1474 | 41.8084 | 40.7842 | 39.7684 | 38.7611 | 37.6095 | 34.6147 | 33.7916 | 33.1589 | 50.9568 | 48.8474 | 46.1937 | 44.3495 | 41.5979 | 40.4011 | 39.2137 | 38.0358 | 36.6853 | 33.1947 | 32.2663 | 31.5547 | 48.4916 | 46.4116 | 43.7653 | 41.9263 | 39.1832 | 37.9895 | 36.8053 | 35.6305 | 34.2853 | 30.8042 | 29.8768 | 29.1674
|  | LEAMINGTON PARK PRIMARY | HE |  |  |  |  | 49.9095 | 48.4042 | 46.4116 | 45.1232 | 43.3032 | 42.5789 | 41.7758 | 40.8137 | 39.7105 | 37.0726 | 36.6232 | 20.8442 | 51.2421 | 49.3368 | 46.9874 | 45.4726 | 43.3305 | 42.4853 | 41.5453 | 40.4158 | 39.1189 | 36.0253 | 35.5116 | 35.2042 | 48.7737 | 46.8989 | 44.5568 | 43.0474 | 40.9116 | 40.0684 | 39.1305 | 38.0042 | 36.7116 | 33.6274 | 33.1147 | 32.8074
|  | LEAMINGTON PARK PRIMARY | CF |  |  |  |  | 50.5526 | 49.8474 | 49.0368 | 48.5274 | 47.9137 | 47.7158 | 47.4632 | 47.1568 | 46.5316 | 43.3937 | 43.0526 | 42.8821 | 52.0611 | 51.1621 | 50.1274 | 49.4842 | 48.7642 | 48.5358 | 48.2432 | 47.8863 | 47.1526 | 43.4674 | 43.0779 | 42.8842 | 49.58 | 48.6947 | 47.6779 | 47.0442 | 46.3295 | 46.1011 | 45.8084 | 45.4537 | 44.7221 | 41.0474 | 40.6589 | 40.4653
MINETY GSP | STRATTON (RESERVE) BSP | LECHLADE PRIMARY | MINIMUM HEADROOM | SP 22074 00496 | NO | YES | 0.094737 | 9.9005 | 9.7984 | 9.69 | 9.1111 | 8.0342 | 6.9837 | 5.6647 | 5.5226 | 5.39 | 3.0121 | -0.33105 | -1.1447 | 7.8689 | 7.7374 | 7.5816 | 6.9047 | 5.7079 | 4.5311 | 3.0184 | 2.8879 | 2.7668 | 0.17211 | -3.5489 | -4.4058 | 8.0984 | 7.9647 | 7.8068 | 7.1132 | 5.8753 | 4.6668 | 3.1437 | 3.0026 | 2.8689 | 0.19211 | -3.6237 | -4.5184
|  | LECHLADE PRIMARY | EE |  |  |  |  | 9.9595 | 9.8742 | 9.7816 | 9.6868 | 9.5574 | 9.3532 | 9.1374 | 8.9205 | 8.7184 | 7.2205 | 3.7363 | 1.7047 | 7.9542 | 7.8426 | 7.7279 | 7.6111 | 7.4321 | 7.2237 | 7.01 | 6.7963 | 6.5984 | 5.1542 | 1.3174 | -0.97526 | 8.1837 | 8.0721 | 7.9542 | 7.8363 | 7.6489 | 7.4268 | 7.1984 | 6.97 | 6.7563 | 5.1258 | 1.1584 | -1.1763
|  | LECHLADE PRIMARY | HT |  |  |  |  | 9.9005 | 9.7984 | 9.69 | 9.1111 | 8.0342 | 6.9837 | 5.6647 | 5.5226 | 5.39 | 3.0121 | -0.33105 | -1.1447 | 7.8689 | 7.7374 | 7.5816 | 6.9047 | 5.7079 | 4.5311 | 3.0184 | 2.8879 | 2.7668 | 0.17211 | -3.5489 | -4.4058 | 8.0984 | 7.9647 | 7.8068 | 7.1132 | 5.8753 | 4.6668 | 3.1437 | 3.0026 | 2.8689 | 0.19211 | -3.6237 | -4.5184
|  | LECHLADE PRIMARY | HE |  |  |  |  | 10.0405 | 9.9826 | 9.9174 | 9.8489 | 9.75 | 9.6563 | 9.5637 | 9.4753 | 9.3816 | 8.6132 | 6.1363 | -1.0511 | 8.0553 | 7.9942 | 7.9142 | 7.8332 | 7.7216 | 7.6174 | 7.5142 | 7.3868 | 7.2679 | 6.5521 | 3.7258 | 1.8058 | 8.2858 | 8.2247 | 8.1447 | 8.0626 | 7.9458 | 7.8342 | 7.7258 | 7.5921 | 7.4658 | 6.6268 | 3.7626 | 1.8089
|  | LECHLADE PRIMARY | CF |  |  |  |  | 10.0963 | 10.0668 | 10.0363 | 10.0026 | 9.9563 | 9.9111 | 9.8668 | 9.8205 | 9.7795 | 9.5226 | 8.15 | 6.8953 | 8.1111 | 8.0816 | 8.0511 | 8.0111 | 7.9563 | 7.9026 | 7.85 | 7.7932 | 7.7426 | 7.3995 | 5.8763 | 4.4826 | 8.3416 | 8.3121 | 8.2816 | 8.2416 | 8.1837 | 8.1258 | 8.0711 | 8.0121 | 7.9595 | 7.5995 | 6.0142 | 4.5647
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LECKHAMPSTEAD PRIMARY | MINIMUM HEADROOM | SU 43962 77635 | NO | YES | 0 | 8.0989 | 8.0074 | 7.9095 | 7.8126 | 7.7137 | 7.6168 | 7.5295 | 7.4505 | 7.3768 | 7.0705 | 6.8242 | -0.86526 | 6.6695 | 6.5358 | 6.3937 | 6.2547 | 6.1179 | 5.9821 | 5.8579 | 5.7432 | 5.6347 | 5.1579 | 4.7158 | 4.3147 | 7.0295 | 6.8895 | 6.7453 | 6.6053 | 6.4663 | 6.3305 | 6.2063 | 6.0916 | 5.9832 | 5.5063 | 5.0653 | 4.6653
|  | LECKHAMPSTEAD PRIMARY | EE |  |  |  |  | 8.16 | 8.0863 | 8.0095 | 7.9284 | 7.8484 | 7.7726 | 7.6989 | 7.6284 | 7.5663 | 7.3305 | 7.1579 | 7.02 | 6.7632 | 6.6589 | 6.5526 | 6.4389 | 6.3305 | 6.2253 | 6.1242 | 6.0274 | 5.9379 | 5.5747 | 5.2642 | 4.9926 | 7.1305 | 7.02 | 6.9074 | 6.7926 | 6.6821 | 6.5758 | 6.4737 | 6.3758 | 6.2863 | 5.9232 | 5.6126 | 5.3421
|  | LECKHAMPSTEAD PRIMARY | HT |  |  |  |  | 8.0989 | 8.0074 | 7.9095 | 7.8126 | 7.7137 | 7.6168 | 7.5295 | 7.4505 | 7.3768 | 7.0705 | 6.8242 | 6.6179 | 6.6695 | 6.5358 | 6.3937 | 6.2547 | 6.1179 | 5.9821 | 5.8579 | 5.7432 | 5.6347 | 5.1579 | 4.7158 | 4.3147 | 7.0295 | 6.8895 | 6.7453 | 6.6053 | 6.4663 | 6.3305 | 6.2063 | 6.0916 | 5.9832 | 5.5063 | 5.0653 | 4.6653
|  | LECKHAMPSTEAD PRIMARY | HE |  |  |  |  | 8.2389 | 8.1895 | 8.1368 | 8.0811 | 8.0221 | 7.9642 | 7.9105 | 7.8611 | 7.8168 | 7.6663 | 7.5684 | -0.86526 | 6.8853 | 6.8189 | 6.7495 | 6.6779 | 6.6053 | 6.5326 | 6.4663 | 6.4032 | 6.3463 | 6.1337 | 5.9621 | 5.8189 | 7.2611 | 7.1916 | 7.1189 | 7.0442 | 6.9674 | 6.8926 | 6.8232 | 6.7579 | 6.7 | 6.4853 | 6.3105 | 6.1674
|  | LECKHAMPSTEAD PRIMARY | CF |  |  |  |  | 8.2884 | 8.2621 | 8.2368 | 8.2084 | 8.1811 | 8.1526 | 8.1253 | 8.0968 | 8.0695 | 7.9432 | 7.8695 | 7.8211 | 6.9547 | 6.9168 | 6.8789 | 6.8389 | 6.7989 | 6.7589 | 6.72 | 6.68 | 6.6411 | 6.4579 | 6.3221 | 6.2105 | 7.3347 | 7.2937 | 7.2537 | 7.2116 | 7.1695 | 7.1274 | 7.0853 | 7.0432 | 7.0021 | 6.8116 | 6.6726 | 6.5579
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | LEE-ON-SOLENT PRIMARY | MINIMUM HEADROOM | SU 56858 00293 | NO | YES | 0 | 26.8305 | 26.4916 | 25.8232 | 24.9526 | 24.1284 | 23.0568 | 22.2695 | 21.5526 | 21.0863 | 18.6926 | 16.2537 | -1.1158 | 23.0779 | 22.3705 | 21.6158 | 20.6558 | 19.7547 | 18.5611 | 17.6947 | 16.9063 | 16.4084 | 13.8074 | 11.1063 | 8.6537 | 23.6242 | 22.9337 | 22.2095 | 21.2947 | 20.4305 | 19.2663 | 18.3989 | 17.6105 | 17.1095 | 14.4989 | 11.7863 | 9.3316
|  | LEE-ON-SOLENT PRIMARY | EE |  |  |  |  | 27.0295 | 26.7632 | 26.4368 | 25.7105 | 24.9947 | 24.04 | 23.34 | 22.6842 | 22.2874 | 20.4484 | 18.5484 | 16.8832 | 23.5032 | 22.9232 | 22.3084 | 21.4811 | 20.6947 | 19.6274 | 18.8547 | 18.1358 | 17.7137 | 15.7326 | 13.6347 | 11.7611 | 24.04 | 23.4737 | 22.8737 | 22.0853 | 21.3337 | 20.3221 | 19.5568 | 18.8358 | 18.4126 | 16.4147 | 14.2979 | 12.4211
|  | LEE-ON-SOLENT PRIMARY | HT |  |  |  |  | 26.8305 | 26.4916 | 25.8232 | 24.9526 | 24.1284 | 23.0568 | 22.2695 | 21.5526 | 21.0863 | 18.6926 | 16.2537 | 14.0653 | 23.0779 | 22.3705 | 21.6158 | 20.6558 | 19.7547 | 18.5611 | 17.6947 | 16.9063 | 16.4084 | 13.8074 | 11.1063 | 8.6537 | 23.6242 | 22.9337 | 22.2095 | 21.2947 | 20.4305 | 19.2663 | 18.3989 | 17.6105 | 17.1095 | 14.4989 | 11.7863 | 9.3316
|  | LEE-ON-SOLENT PRIMARY | HE |  |  |  |  | 27.2842 | 27.0958 | 26.8874 | 26.6579 | 26.1032 | 25.2842 | 24.7168 | 24.1947 | 23.9316 | 22.7358 | 21.4526 | -1.1158 | 24.0558 | 23.6442 | 23.1947 | 22.5389 | 21.9011 | 20.9789 | 20.3505 | 19.7747 | 19.4968 | 18.2053 | 16.7653 | 15.4821 | 24.5789 | 24.1779 | 23.7389 | 23.1021 | 22.4916 | 21.6211 | 21.0221 | 20.4716 | 20.1989 | 18.9011 | 17.4568 | 16.1705
|  | LEE-ON-SOLENT PRIMARY | CF |  |  |  |  | 27.4558 | 27.3558 | 27.2516 | 27.1442 | 27.0316 | 26.9158 | 26.7011 | 26.4095 | 26.2189 | 25.3284 | 24.4484 | 23.6832 | 24.4958 | 24.2568 | 24.0042 | 23.6747 | 23.3537 | 22.9021 | 22.5579 | 22.2147 | 22.0105 | 21.0526 | 20.0663 | 19.1958 | 25.0074 | 24.7747 | 24.5284 | 24.2084 | 23.8958 | 23.46 | 23.1274 | 22.8021 | 22.6032 | 21.6779 | 20.7421 | 19.8916
LOVEDEAN GSP | HAVANT BSP | LEIGH PARK PRIMARY | MINIMUM HEADROOM | SU 72144 07875 | NO | YES | 0 | 35.9411 | 35.6747 | 35.3926 | 35.0968 | 34.7642 | 34.1084 | 33.5505 | 33.0337 | 32.4726 | 29.6126 | 27.2326 | 2.76 | 30.1747 | 29.8853 | 29.1105 | 28.2684 | 27.4179 | 26.72 | 26.1284 | 25.5789 | 24.9768 | 21.8853 | 19.3053 | 15.9453 | 35.0463 | 34.7547 | 33.9432 | 33.0621 | 32.1705 | 31.4442 | 30.8284 | 30.2568 | 29.6284 | 26.38 | 23.6653 | 20.1021
|  | LEIGH PARK PRIMARY | EE |  |  |  |  | 36.0811 | 35.8558 | 35.6168 | 35.3632 | 35.1011 | 34.8442 | 34.4947 | 34.1053 | 33.68 | 31.5389 | 29.7758 | 27.3579 | 30.3147 | 30.0895 | 29.7884 | 29.0084 | 28.2389 | 27.6411 | 27.14 | 26.7316 | 26.2811 | 23.9747 | 22.0632 | 19.4 | 35.1863 | 34.9611 | 34.6547 | 33.8358 | 33.0295 | 32.4063 | 31.8863 | 31.4653 | 30.9968 | 28.5789 | 26.5684 | 23.7389
|  | LEIGH PARK PRIMARY | HT |  |  |  |  | 35.9411 | 35.6747 | 35.3926 | 35.0968 | 34.7642 | 34.1084 | 33.5505 | 33.0337 | 32.4726 | 29.6126 | 27.2326 | 24.1737 | 30.1747 | 29.8853 | 29.1105 | 28.2684 | 27.4179 | 26.72 | 26.1284 | 25.5789 | 24.9768 | 21.8853 | 19.3053 | 15.9453 | 35.0463 | 34.7547 | 33.9432 | 33.0621 | 32.1705 | 31.4442 | 30.8284 | 30.2568 | 29.6284 | 26.38 | 23.6653 | 20.1021
|  | LEIGH PARK PRIMARY | HE |  |  |  |  | 36.26 | 36.0874 | 35.8947 | 35.6905 | 35.4716 | 35.2611 | 35.0632 | 34.8789 | 34.72 | 33.3463 | 32.1274 | 2.76 | 30.4937 | 30.3211 | 30.1284 | 29.7863 | 29.1242 | 28.6421 | 28.2558 | 27.9642 | 27.6211 | 25.9032 | 24.5737 | 22.4716 | 35.3653 | 35.1926 | 35 | 34.6474 | 33.9516 | 33.4495 | 33.0495 | 32.7505 | 32.3937 | 30.5895 | 29.1863 | 26.9442
|  | LEIGH PARK PRIMARY | CF |  |  |  |  | 36.3979 | 36.2989 | 36.1958 | 36.0895 | 35.9811 | 35.8674 | 35.7579 | 35.6484 | 35.5389 | 35.0537 | 34.5821 | 33.4042 | 31.5168 | 30.5326 | 30.4295 | 30.3232 | 30.2147 | 30.1011 | 29.9916 | 29.7421 | 29.4284 | 28.0726 | 27.2126 | 25.9063 | 36.2863 | 35.4042 | 35.3011 | 35.1947 | 35.0863 | 34.9726 | 34.8632 | 34.6032 | 34.2747 | 32.8537 | 31.9484 | 30.5568
BRAMLEY (BASI) GSP | READING BSP | LITTLE HUNGERFORD PRIMARY | MINIMUM HEADROOM | SU 75372 72019 | NO | YES | 0 | 37.3063 | 36.6611 | 35.9758 | 35.2716 | 33.7779 | 32.2968 | 30.9263 | 29.6853 | 28.5537 | 23.7474 | 19.3042 | -17.0589 | 29.4926 | 28.1274 | 26.5989 | 25.0737 | 23.2863 | 21.6695 | 20.1674 | 18.8063 | 17.5684 | 12.2863 | 7.3316 | 2.6137 | 31.3947 | 30.0558 | 28.5579 | 27.0621 | 25.3116 | 23.7284 | 22.2558 | 20.9242 | 19.7105 | 14.4632 | 9.5042 | 4.7853
|  | LITTLE HUNGERFORD PRIMARY | EE |  |  |  |  | 37.7 | 37.1737 | 36.6137 | 36.0316 | 35.4295 | 34.4895 | 33.3589 | 32.4095 | 31.5505 | 28.1916 | 25.0716 | 22.1621 | 30.4242 | 29.38 | 28.1432 | 26.8926 | 25.4084 | 24.0695 | 22.8347 | 21.8105 | 20.8811 | 17.2263 | 13.7495 | 10.4653 | 32.3074 | 31.2811 | 30.0695 | 28.8421 | 27.3884 | 26.0789 | 24.8684 | 23.8611 | 22.9484 | 19.3621 | 15.9221 | 12.6358
|  | LITTLE HUNGERFORD PRIMARY | HT |  |  |  |  | 37.3063 | 36.6611 | 35.9758 | 35.2716 | 33.7779 | 32.2968 | 30.9263 | 29.6853 | 28.5537 | 23.7474 | 19.3042 | 15.1147 | 29.4926 | 28.1274 | 26.5989 | 25.0737 | 23.2863 | 21.6695 | 20.1674 | 18.8063 | 17.5684 | 12.2863 | 7.3316 | 2.6137 | 31.3947 | 30.0558 | 28.5579 | 27.0621 | 25.3116 | 23.7284 | 22.2558 | 20.9242 | 19.7105 | 14.4632 | 9.5042 | 4.7853
|  | LITTLE HUNGERFORD PRIMARY | HE |  |  |  |  | 38.2158 | 37.8505 | 37.4463 | 37.0126 | 36.5484 | 36.1042 | 35.6863 | 35.2958 | 34.8105 | 32.6137 | 30.5737 | -17.0589 | 31.5421 | 30.8474 | 29.9421 | 29.0116 | 27.8221 | 26.7758 | 25.8221 | 25.0989 | 24.4295 | 22.0411 | 19.7537 | 17.5695 | 33.4032 | 32.72 | 31.8337 | 30.92 | 29.7579 | 28.7316 | 27.7979 | 27.0874 | 26.4284 | 24.0853 | 21.8558 | 19.7358
|  | LITTLE HUNGERFORD PRIMARY | CF |  |  |  |  | 38.5621 | 38.3737 | 38.1768 | 37.9737 | 37.7621 | 37.5474 | 37.3358 | 37.1263 | 36.9179 | 35.9853 | 34.8863 | 34.0042 | 32.1674 | 31.9358 | 31.4189 | 30.8621 | 30.1905 | 29.5011 | 28.8779 | 28.3316 | 27.8211 | 25.6726 | 24.4189 | 23.4242 | 33.8168 | 33.6253 | 33.2821 | 32.7389 | 32.0842 | 31.4116 | 30.8021 | 30.2674 | 29.7684 | 27.6642 | 26.4379 | 25.4695
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW PRIMARY | MINIMUM HEADROOM | SU 86037 87794 | NO | YES | 0 | 29.3108 | 28.995 | 28.6592 | 28.3129 | 27.9561 | 27.5971 | 27.2834 | 26.9971 | 26.7339 | 25.3034 | 23.2729 | -7.8818 | 28.2182 | 27.8813 | 27.5255 | 27.1571 | 26.7792 | 26.2371 | 25.6771 | 25.1118 | 24.5708 | 22.0771 | 19.8403 | 17.8108 | 28.8266 | 28.5108 | 28.175 | 27.8287 | 27.4718 | 26.9076 | 26.3508 | 25.7897 | 25.2518 | 22.7803 | 20.5645 | 18.5561
|  | LITTLE MARLOW PRIMARY | EE |  |  |  |  | 29.5003 | 29.2413 | 28.9655 | 28.6782 | 28.3813 | 28.0961 | 27.8245 | 27.5634 | 27.3318 | 26.4897 | 25.4382 | 24.0718 | 28.4203 | 28.1445 | 27.8508 | 27.5455 | 27.2297 | 26.935 | 26.6529 | 26.3076 | 25.855 | 23.8887 | 22.1918 | 20.6676 | 29.0161 | 28.7571 | 28.4813 | 28.1939 | 27.8971 | 27.6118 | 27.3403 | 26.9761 | 26.5266 | 24.5771 | 22.8971 | 21.3887
|  | LITTLE MARLOW PRIMARY | HT |  |  |  |  | 29.3108 | 28.995 | 28.6592 | 28.3129 | 27.9561 | 27.5971 | 27.2834 | 26.9971 | 26.7339 | 25.3034 | 23.2729 | 21.4424 | 28.2182 | 27.8813 | 27.5255 | 27.1571 | 26.7792 | 26.2371 | 25.6771 | 25.1118 | 24.5708 | 22.0771 | 19.8403 | 17.8108 | 28.8266 | 28.5108 | 28.175 | 27.8287 | 27.4718 | 26.9076 | 26.3508 | 25.7897 | 25.2518 | 22.7803 | 20.5645 | 18.5561
|  | LITTLE MARLOW PRIMARY | HE |  |  |  |  | 29.7445 | 29.5613 | 29.3582 | 29.1403 | 28.9076 | 28.6845 | 28.475 | 28.2792 | 28.1108 | 27.5434 | 27.2129 | -7.8818 | 28.6803 | 28.4855 | 28.2708 | 28.0392 | 27.7918 | 27.5634 | 27.3476 | 27.1434 | 26.9655 | 26.2266 | 25.1266 | 24.1708 | 29.2603 | 29.0771 | 28.8739 | 28.6561 | 28.4234 | 28.2003 | 27.9908 | 27.795 | 27.6266 | 26.895 | 25.8076 | 24.8634
|  | LITTLE MARLOW PRIMARY | CF |  |  |  |  | 29.9097 | 29.8118 | 29.7097 | 29.6045 | 29.495 | 29.3845 | 29.275 | 29.1666 | 29.0582 | 28.5761 | 28.3361 | 28.2045 | 28.8529 | 28.7476 | 28.6382 | 28.5245 | 28.4066 | 28.2918 | 28.1771 | 28.0624 | 27.9476 | 27.4318 | 27.1582 | 26.5108 | 29.4255 | 29.3276 | 29.2255 | 29.1203 | 29.0108 | 28.9003 | 28.7908 | 28.6824 | 28.5739 | 28.0918 | 27.8518 | 27.1855
NURSLING GSP | ROWNHAMS BSP | LORDSHILL PRIMARY | MINIMUM HEADROOM | SU 38746 16055 | NO | YES | 0 | 32.9495 | 32.7726 | 32.7432 | 32.8116 | 32.7663 | 32.4368 | 32.1389 | 31.8558 | 31.5621 | 29.9379 | 28.3084 | 10.7779 | 30.1874 | 29.8474 | 29.6021 | 29.2189 | 28.8663 | 28.5158 | 28.1979 | 27.8916 | 27.5737 | 25.7768 | 23.9474 | 22.2126 | 30.9189 | 30.6232 | 30.2958 | 29.9137 | 29.5611 | 29.2095 | 28.8916 | 28.5874 | 28.2684 | 26.4716 | 24.6421 | 22.9095
|  | LORDSHILL PRIMARY | EE |  |  |  |  | 33.0474 | 32.9 | 32.7432 | 33.5032 | 33.1884 | 32.8716 | 32.6158 | 32.3589 | 32.1295 | 30.9389 | 29.6611 | 28.4789 | 30.4137 | 30.14 | 29.8316 | 29.5263 | 29.3242 | 28.9821 | 28.7074 | 28.4347 | 28.1905 | 26.8821 | 25.4453 | 24.1021 | 31.0168 | 30.8695 | 30.6063 | 30.3589 | 30.0189 | 29.6758 | 29.4032 | 29.1284 | 28.8832 | 27.5747 | 26.1368 | 24.7947
|  | LORDSHILL PRIMARY | HT |  |  |  |  | 32.9495 | 32.7726 | 33.4505 | 33.0968 | 32.7663 | 32.4368 | 32.1389 | 31.8558 | 31.5621 | 29.9379 | 28.3084 | 26.7768 | 30.1874 | 29.8474 | 29.6021 | 29.2189 | 28.8663 | 28.5158 | 28.1979 | 27.8916 | 27.5737 | 25.7768 | 23.9474 | 22.2126 | 30.9189 | 30.6232 | 30.2958 | 29.9137 | 29.5611 | 29.2095 | 28.8916 | 28.5874 | 28.2684 | 26.4716 | 24.6421 | 22.9095
|  | LORDSHILL PRIMARY | HE |  |  |  |  | 33.1726 | 33.0632 | 32.9421 | 32.8116 | 33.7632 | 33.5179 | 33.3358 | 33.1589 | 33.0021 | 32.2537 | 31.3484 | 10.7779 | 30.6379 | 30.5253 | 30.3021 | 30.0789 | 29.9537 | 29.6884 | 29.4979 | 29.3105 | 29.1432 | 28.3253 | 27.2979 | 26.3158 | 31.1421 | 31.0326 | 30.9116 | 30.7811 | 30.6474 | 30.3832 | 30.1905 | 30.0032 | 29.8368 | 29.0189 | 27.9926 | 27.0105
|  | LORDSHILL PRIMARY | CF |  |  |  |  | 33.2621 | 33.2 | 33.1368 | 33.0695 | 33.0011 | 34.1295 | 34.0074 | 33.8895 | 33.7695 | 33.1832 | 32.5884 | 32.0179 | 30.7295 | 30.6653 | 30.5989 | 30.4863 | 30.3421 | 30.3389 | 30.2074 | 30.0811 | 29.9537 | 29.3168 | 28.6453 | 27.9895 | 31.2316 | 31.1695 | 31.1063 | 31.0389 | 30.9705 | 31.0326 | 30.9011 | 30.7747 | 30.6463 | 30.0105 | 29.3389 | 28.6832
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LOVE LANE PRIMARY | MINIMUM HEADROOM | SU 47334 68495 | NO | YES | 0 | 44.964 | 44.6798 | 44.3777 | 44.0651 | 43.7419 | 43.4166 | 43.1314 | 42.8703 | 42.6282 | 40.8398 | 38.8924 | -32.0034 | 38.6166 | 37.8903 | 36.8819 | 35.8366 | 35.2924 | 34.7451 | 34.2451 | 33.7808 | 33.344 | 31.3756 | 29.2135 | 27.0998 | 40.0787 | 39.4482 | 38.4503 | 37.4072 | 36.8619 | 36.3156 | 35.8166 | 35.3524 | 34.9166 | 32.9493 | 30.7903 | 28.6798
|  | LOVE LANE PRIMARY | EE |  |  |  |  | 45.1293 | 44.8945 | 46.4651 | 45.6261 | 45.2061 | 44.7998 | 44.4051 | 44.0303 | 43.6872 | 42.2808 | 40.8029 | 39.3819 | 38.9829 | 38.3661 | 37.4651 | 36.524 | 36.0787 | 35.6461 | 35.2261 | 34.8272 | 34.4608 | 32.9451 | 31.2998 | 29.6966 | 40.2556 | 39.9051 | 39.0335 | 38.0935 | 37.6482 | 37.2166 | 36.7966 | 36.3977 | 36.0314 | 34.5166 | 32.8745 | 31.2724
|  | LOVE LANE PRIMARY | HT |  |  |  |  | 44.964 | 44.6798 | 44.3777 | 44.0651 | 43.7419 | 43.4166 | 43.1314 | 42.8703 | 42.6282 | 40.8398 | 38.8924 | 37.0082 | 38.6166 | 37.8903 | 36.8819 | 35.8366 | 35.2924 | 34.7451 | 34.2451 | 33.7808 | 33.344 | 31.3756 | 29.2135 | 27.0998 | 40.0787 | 39.4482 | 38.4503 | 37.4072 | 36.8619 | 36.3156 | 35.8166 | 35.3524 | 34.9166 | 32.9493 | 30.7903 | 28.6798
|  | LOVE LANE PRIMARY | HE |  |  |  |  | 45.3429 | 45.1724 | 44.984 | 44.7819 | 44.5661 | 44.3598 | 44.1651 | 43.984 | 43.8272 | 43.2977 | 42.9861 | -32.0034 | 39.4661 | 38.9987 | 38.2398 | 37.4345 | 37.1124 | 36.8061 | 36.5082 | 36.2345 | 35.9893 | 35.0756 | 34.004 | 32.9461 | 40.4851 | 40.2966 | 39.7945 | 39.0029 | 38.6808 | 38.3745 | 38.0766 | 37.804 | 37.5587 | 36.6461 | 35.5756 | 34.5198
|  | LOVE LANE PRIMARY | CF |  |  |  |  | 45.4914 | 45.3998 | 45.3029 | 45.204 | 45.1008 | 44.9966 | 44.8935 | 44.7914 | 44.6893 | 44.2345 | 44.0072 | 43.8819 | 39.6998 | 39.5872 | 39.3198 | 38.9345 | 38.7482 | 38.5608 | 38.3745 | 38.1924 | 38.0114 | 37.1661 | 36.4208 | 35.6798 | 40.6535 | 40.5514 | 40.4387 | 40.3229 | 40.2156 | 40.0924 | 39.9124 | 39.7356 | 39.5608 | 38.7335 | 37.9893 | 37.2503
COWLEY GSP | YARNTON BSP | LOVELACE ROAD PRIMARY | MINIMUM HEADROOM | SP 50395 10376 | YES | YES | 1.0516 | 15.1463 | 29.9094 | 29.661 | 29.4168 | 29.1726 | 27.8589 | 27.6199 | 27.4052 | 27.2084 | 26.3221 | 25.5863 | 16.6199 | 13.4073 | 28.1484 | 27.881 | 27.621 | 27.361 | 25.8399 | 25.5821 | 25.3526 | 25.141 | 24.1821 | 23.3821 | 22.6663 | 13.0547 | 27.7957 | 27.5284 | 27.2673 | 27.0073 | 25.4863 | 25.2284 | 24.9989 | 24.7873 | 23.8284 | 23.0273 | 22.3126
|  | LOVELACE ROAD PRIMARY | EE |  |  |  |  | 15.2315 | 30.1178 | 29.9252 | 29.7273 | 29.5294 | 28.6821 | 28.2126 | 27.9084 | 27.7378 | 27.0557 | 26.5189 | 26.0568 | 13.5915 | 28.3831 | 28.1705 | 27.9589 | 27.7494 | 26.7715 | 26.2399 | 25.9021 | 25.7189 | 24.9821 | 24.3957 | 23.8863 | 13.2389 | 28.0305 | 27.8168 | 27.6063 | 27.3968 | 26.4178 | 25.8863 | 25.5484 | 25.3652 | 24.6284 | 24.0421 | 23.5326
|  | LOVELACE ROAD PRIMARY | HT |  |  |  |  | 15.1463 | 29.9094 | 29.661 | 29.4168 | 29.1726 | 27.8589 | 27.6199 | 27.4052 | 27.2084 | 26.3221 | 25.5863 | 24.9357 | 13.4073 | 28.1484 | 27.881 | 27.621 | 27.361 | 25.8399 | 25.5821 | 25.3526 | 25.141 | 24.1821 | 23.3821 | 22.6663 | 13.0547 | 27.7957 | 27.5284 | 27.2673 | 27.0073 | 25.4863 | 25.2284 | 24.9989 | 24.7873 | 23.8284 | 23.0273 | 22.3126
|  | LOVELACE ROAD PRIMARY | HE |  |  |  |  | 15.3336 | 30.2505 | 30.1599 | 30.0621 | 29.9578 | 29.1715 | 28.7463 | 28.5263 | 28.4136 | 27.9978 | 27.7094 | 16.6199 | 13.8242 | 28.6863 | 28.5421 | 28.3957 | 28.2463 | 27.3052 | 26.821 | 26.5768 | 26.4578 | 26.0126 | 25.6999 | 25.4557 | 13.4705 | 28.3336 | 28.1884 | 28.0431 | 27.8936 | 26.9526 | 26.4673 | 26.2231 | 26.1052 | 25.6599 | 25.3473 | 25.1021
|  | LOVELACE ROAD PRIMARY | CF |  |  |  |  | 15.4042 | 30.3589 | 30.3115 | 30.2631 | 30.2126 | 30.1621 | 30.1115 | 30.061 | 29.8978 | 29.1094 | 28.8536 | 28.6673 | 14.0947 | 29.0115 | 28.9252 | 28.8389 | 28.7494 | 28.6589 | 28.5305 | 28.3357 | 28.1347 | 27.2442 | 26.9631 | 26.7536 | 13.7421 | 28.6578 | 28.5726 | 28.4863 | 28.3968 | 28.3052 | 28.1778 | 27.9831 | 27.7821 | 26.8905 | 26.6105 | 26.401
MANNINGTON GSP | ARNEWOOD BSP | LYMINGTON PRIMARY | MINIMUM HEADROOM | SZ 31720 96856 | NO | YES | 0 | 35.0021 | 34.2242 | 33.3021 | 32.2358 | 31.2074 | 30.1295 | 29.4621 | 28.8411 | 28.2621 | 25.4242 | 22.4968 | -3.6484 | 29.0368 | 28.2063 | 27.2137 | 26.0579 | 24.9495 | 23.7853 | 23.0821 | 22.4274 | 21.8158 | 18.7821 | 15.5432 | 12.4326 | 29.8347 | 29.0926 | 28.1947 | 27.0168 | 25.8874 | 24.7 | 23.9863 | 23.3211 | 22.6989 | 19.6053 | 16.3432 | 13.2263
|  | LYMINGTON PRIMARY | EE |  |  |  |  | 35.4274 | 34.9063 | 34.2221 | 33.3716 | 32.4505 | 31.4379 | 30.78 | 30.1916 | 29.6958 | 27.4947 | 25.2368 | 23.1474 | 29.5747 | 28.9389 | 28.2084 | 27.4389 | 26.4232 | 25.2958 | 24.5874 | 23.9568 | 23.4305 | 21.0537 | 18.5484 | 16.1895 | 30.3105 | 29.7389 | 29.0874 | 28.2705 | 27.2547 | 26.1253 | 25.4137 | 24.7811 | 24.2516 | 21.86 | 19.3368 | 16.9726
|  | LYMINGTON PRIMARY | HT |  |  |  |  | 35.0021 | 34.2242 | 33.3021 | 32.2358 | 31.2074 | 30.1295 | 29.4621 | 28.8411 | 28.2621 | 25.4242 | 22.4968 | 19.7295 | 29.0368 | 28.2063 | 27.2137 | 26.0579 | 24.9495 | 23.7853 | 23.0821 | 22.4274 | 21.8158 | 18.7821 | 15.5432 | 12.4326 | 29.8347 | 29.0926 | 28.1947 | 27.0168 | 25.8874 | 24.7 | 23.9863 | 23.3211 | 22.6989 | 19.6053 | 16.3432 | 13.2263
|  | LYMINGTON PRIMARY | HE |  |  |  |  | 35.7463 | 35.5105 | 35.2495 | 34.5821 | 33.8305 | 32.9779 | 32.4863 | 32.0821 | 31.7547 | 30.3463 | 28.8379 | -3.6484 | 30.2663 | 29.8453 | 29.3105 | 28.7568 | 27.9263 | 26.9737 | 26.4421 | 26.0126 | 25.6663 | 24.1484 | 22.4526 | 20.8326 | 30.9232 | 30.5411 | 30.0653 | 29.5895 | 28.7579 | 27.8042 | 27.2737 | 26.8411 | 26.4947 | 24.9695 | 23.2684 | 21.6432
|  | LYMINGTON PRIMARY | CF |  |  |  |  | 35.9663 | 35.8432 | 35.7137 | 35.5811 | 35.4421 | 35.1684 | 34.9063 | 34.5937 | 34.2758 | 32.8568 | 31.8621 | 30.9084 | 30.6537 | 30.4242 | 30.1853 | 29.9021 | 29.5642 | 29.2084 | 28.9305 | 28.5926 | 28.2495 | 26.7168 | 25.6263 | 24.5632 | 31.2758 | 31.0684 | 30.8526 | 30.6011 | 30.3042 | 29.9947 | 29.7453 | 29.4495 | 29.1484 | 27.6811 | 26.5632 | 25.4695
MELKSHAM GSP | CHIPPENHAM BSP | LYNEHAM PRIMARY | MINIMUM HEADROOM | ST 99348 80481 | NO | YES | 0.31579 | 13.4411 | 13.1968 | 12.6979 | 12.4211 | 11.5611 | 10.3326 | 8.8116 | 8.5937 | 8.38 | 5.4221 | 1.3958 | -4.2463 | 9.9684 | 9.4179 | 8.8611 | 8.5642 | 7.6116 | 6.2263 | 4.4947 | 4.2979 | 4.1074 | 0.96947 | -3.4074 | -4.4947 | 10.5526 | 10.0021 | 9.4442 | 9.1474 | 8.1789 | 6.7779 | 5.0284 | 4.8105 | 4.5958 | 1.3084 | -3.2411 | -4.3968
|  | LYNEHAM PRIMARY | EE |  |  |  |  | 14.0116 | 13.5684 | 13.1074 | 12.6053 | 12.3211 | 12.0137 | 11.7074 | 11.4 | 11.0979 | 9.3547 | 5.2137 | 2.8179 | 10.3305 | 9.8347 | 9.3189 | 8.7547 | 8.4726 | 8.1768 | 7.8832 | 7.5905 | 7.3074 | 5.6832 | 1.2684 | -1.3884 | 10.9147 | 10.4179 | 9.9 | 9.3347 | 9.0358 | 8.7158 | 8.3958 | 8.0747 | 7.7589 | 5.92 | 1.2621 | -1.4684
|  | LYNEHAM PRIMARY | HT |  |  |  |  | 13.6895 | 13.1968 | 12.6979 | 12.4211 | 11.5611 | 10.3326 | 8.8116 | 8.5937 | 8.38 | 5.4221 | 1.3958 | 0.32947 | 9.9684 | 9.4179 | 8.8611 | 8.5642 | 7.6116 | 6.2263 | 4.4947 | 4.2979 | 4.1074 | 0.96947 | -3.4074 | -4.4947 | 10.5526 | 10.0021 | 9.4442 | 9.1474 | 8.1789 | 6.7779 | 5.0284 | 4.8105 | 4.5958 | 1.3084 | -3.2411 | -4.3968
|  | LYNEHAM PRIMARY | HE |  |  |  |  | 14.2526 | 13.9705 | 13.6853 | 13.3611 | 12.9537 | 12.5589 | 12.3653 | 12.1779 | 12.0095 | 11.0284 | 8.8137 | -4.2463 | 10.5937 | 10.2768 | 9.9589 | 9.5958 | 9.1568 | 8.7295 | 8.5411 | 8.3579 | 8.1958 | 7.2368 | 4.7737 | 2.5684 | 11.1768 | 10.8611 | 10.5421 | 10.1789 | 9.7284 | 9.2895 | 9.0895 | 8.8926 | 8.7168 | 7.6684 | 5.14 | 2.8747
|  | LYNEHAM PRIMARY | CF |  |  |  |  | 13.4411 | 14.3558 | 14.2137 | 14.0621 | 13.8653 | 13.6558 | 13.4453 | 13.3421 | 13.2421 | 12.7432 | 11.6705 | 10.2158 | 10.7347 | 10.7074 | 10.5484 | 10.3779 | 10.1663 | 9.9368 | 9.7105 | 9.6063 | 9.5042 | 9.0032 | 7.8242 | 6.1926 | 11.1505 | 11.2905 | 11.1326 | 10.9621 | 10.7442 | 10.5095 | 10.2758 | 10.1663 | 10.06 | 9.5305 | 8.3137 | 6.6432
FLEET-BRAMLEY GSP | BRACKNELL BSP | MVEE PRIMARY | MINIMUM HEADROOM | SU 98120 65945 | NO | YES | 0 | 29.9053 | 29.8221 | 29.7295 | 29.6421 | 29.5516 | 29.4516 | 29.3442 | 29.2747 | 28.2589 | 27.9347 | 27.5579 | 24.0389 | 29.8284 | 29.7326 | 29.6316 | 29.5379 | 29.44 | 29.3316 | 29.2126 | 29.1379 | 27.9253 | 27.5716 | 27.1505 | 27.0053 | 29.8074 | 29.7137 | 29.6147 | 29.5221 | 29.4242 | 29.3158 | 29.1958 | 29.1221 | 27.9116 | 27.5579 | 27.1379 | 26.9926
|  | MVEE PRIMARY | EE |  |  |  |  | 29.9642 | 29.8979 | 29.8579 | 29.7895 | 29.72 | 29.6432 | 29.5705 | 29.5 | 29.4358 | 28.9379 | 28.5947 | 28.3716 | 29.8979 | 29.8211 | 29.7421 | 29.6695 | 29.5958 | 29.5126 | 29.4358 | 29.3589 | 29.2895 | 28.7263 | 28.3368 | 28.0853 | 29.8758 | 29.8011 | 29.7263 | 29.6526 | 29.5789 | 29.4968 | 29.4189 | 29.3432 | 29.2737 | 28.7105 | 28.3221 | 28.0705
|  | MVEE PRIMARY | HT |  |  |  |  | 29.9053 | 29.8221 | 29.7295 | 29.6421 | 29.5516 | 29.4516 | 29.3442 | 29.2747 | 28.2589 | 27.9347 | 27.5579 | 27.4211 | 29.8284 | 29.7326 | 29.6316 | 29.5379 | 29.44 | 29.3316 | 29.2126 | 29.1379 | 27.9253 | 27.5716 | 27.1505 | 27.0053 | 29.8074 | 29.7137 | 29.6147 | 29.5221 | 29.4242 | 29.3158 | 29.1958 | 29.1221 | 27.9116 | 27.5579 | 27.1379 | 26.9926
|  | MVEE PRIMARY | HE |  |  |  |  | 30.04 | 29.9968 | 29.9516 | 29.9063 | 29.86 | 29.8074 | 29.7579 | 29.7084 | 29.6632 | 29.1779 | 28.9263 | 24.0389 | 29.9863 | 29.9379 | 29.8853 | 29.8368 | 29.7853 | 29.7253 | 29.6684 | 29.6147 | 29.5653 | 28.9968 | 28.7021 | 28.5074 | 29.9632 | 29.9147 | 29.8632 | 29.8147 | 29.7642 | 29.7053 | 29.6495 | 29.5968 | 29.5484 | 28.9811 | 28.6874 | 28.4926
|  | MVEE PRIMARY | CF |  |  |  |  | 30.0789 | 30.0568 | 30.0326 | 30.0084 | 29.9832 | 29.9547 | 29.9263 | 29.8968 | 29.8684 | 29.7242 | 29.6189 | 29.5337 | 30.0337 | 30.0053 | 29.9768 | 29.9484 | 29.92 | 29.8863 | 29.8526 | 29.8179 | 29.7842 | 29.6211 | 29.5011 | 29.4021 | 30.0105 | 29.9811 | 29.9537 | 29.9263 | 29.8979 | 29.8642 | 29.8316 | 29.7979 | 29.7653 | 29.6053 | 29.4853 | 29.3853
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON PRIMARY | MINIMUM HEADROOM | SY 59138 97747 | NO | YES | 0 | 11.5 | 11.3263 | 11.1505 | 10.9779 | 10.8063 | 10.6358 | 10.4811 | 10.3379 | 10.2042 | 9.6105 | 6.0874 | 1.5211 | 9.8884 | 9.7011 | 9.5126 | 9.3284 | 9.1453 | 8.9653 | 8.8 | 8.6463 | 8.5032 | 7.8642 | 3.6937 | 3.5663 | 10.2053 | 10.0179 | 9.8295 | 9.6453 | 9.4621 | 9.2821 | 9.1158 | 8.9632 | 8.82 | 8.1789 | 4.0084 | 3.88
|  | MAIDEN NEWTON PRIMARY | EE |  |  |  |  | 11.6158 | 11.4747 | 11.3347 | 11.1926 | 11.0526 | 10.9168 | 10.7884 | 10.6632 | 10.5505 | 10.0895 | 6.0874 | 5.9589 | 10.0147 | 9.8642 | 9.7147 | 9.5642 | 9.4147 | 9.2716 | 9.1347 | 9.0021 | 8.8821 | 8.3842 | 3.6937 | 3.5663 | 10.3316 | 10.1811 | 10.0305 | 9.88 | 9.7305 | 9.5874 | 9.4505 | 9.3179 | 9.1979 | 8.7011 | 4.0084 | 3.88
|  | MAIDEN NEWTON PRIMARY | HT |  |  |  |  | 11.5 | 11.3263 | 11.1505 | 10.9779 | 10.8063 | 10.6358 | 10.4811 | 10.3379 | 10.2042 | 9.6105 | 9.0453 | 8.5137 | 9.8884 | 9.7011 | 9.5126 | 9.3284 | 9.1453 | 8.9653 | 8.8 | 8.6463 | 8.5032 | 7.8642 | 7.2411 | 6.6484 | 10.2053 | 10.0179 | 9.8295 | 9.6453 | 9.4621 | 9.2821 | 9.1158 | 8.9632 | 8.82 | 8.1789 | 7.5558 | 6.9632
|  | MAIDEN NEWTON PRIMARY | HE |  |  |  |  | 11.7726 | 11.6821 | 11.5884 | 11.4916 | 11.3916 | 11.2958 | 11.2074 | 11.1232 | 11.0484 | 10.7726 | 6.4979 | 1.5211 | 10.1863 | 10.0895 | 9.9905 | 9.8884 | 9.7842 | 9.6832 | 9.5895 | 9.5011 | 9.4232 | 9.1295 | 4.1042 | 4.0432 | 10.5032 | 10.4063 | 10.3074 | 10.2053 | 10.1011 | 10 | 9.9063 | 9.8179 | 9.74 | 9.4463 | 4.4189 | 4.3579
|  | MAIDEN NEWTON PRIMARY | CF |  |  |  |  | 11.8611 | 11.8063 | 11.7537 | 11.7 | 11.6453 | 11.5895 | 11.5337 | 11.4789 | 11.4263 | 11.1779 | 10.9874 | 10.82 | 10.2811 | 10.2221 | 10.1653 | 10.1074 | 10.0484 | 9.9884 | 9.9284 | 9.8705 | 9.8137 | 9.5474 | 9.3347 | 9.1453 | 10.5979 | 10.5389 | 10.4821 | 10.4242 | 10.3653 | 10.3053 | 10.2453 | 10.1874 | 10.1305 | 9.8642 | 9.6516 | 9.4611
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | MAIDENHEAD PRIMARY | MINIMUM HEADROOM | SU 86485 79800 | NO | YES | 0 | 36.3389 | 35.86 | 35.3516 | 33.6726 | 32.4168 | 31.1905 | 30.0316 | 29.0453 | 28.1168 | 23.9326 | 20.1832 | -6.6926 | 30.0716 | 28.9579 | 27.5137 | 25.4074 | 24.0063 | 22.6411 | 21.3505 | 20.2674 | 19.2474 | 14.6337 | 10.4432 | 6.5705 | 31.6579 | 30.5905 | 29.2137 | 27.2232 | 25.8747 | 24.5084 | 23.2179 | 22.1358 | 21.1147 | 16.5042 | 12.3116 | 8.4368
|  | MAIDENHEAD PRIMARY | EE |  |  |  |  | 36.6295 | 36.2368 | 35.82 | 34.7495 | 33.6505 | 32.5853 | 31.5611 | 30.7232 | 29.9421 | 26.5537 | 23.6726 | 21.0305 | 30.7032 | 29.7747 | 28.5189 | 26.5916 | 25.36 | 24.1653 | 23.0147 | 22.0884 | 21.2326 | 17.48 | 14.2642 | 11.2737 | 32.2642 | 31.3747 | 30.18 | 28.3611 | 27.1863 | 26.0337 | 24.8832 | 23.9558 | 23.0989 | 19.3432 | 16.1316 | 13.1379
|  | MAIDENHEAD PRIMARY | HT |  |  |  |  | 36.3389 | 35.86 | 35.3516 | 33.6726 | 32.4168 | 31.1905 | 30.0316 | 29.0453 | 28.1168 | 23.9326 | 20.1832 | 16.7432 | 30.0716 | 28.9579 | 27.5137 | 25.4074 | 24.0063 | 22.6411 | 21.3505 | 20.2674 | 19.2474 | 14.6337 | 10.4432 | 6.5705 | 31.6579 | 30.5905 | 29.2137 | 27.2232 | 25.8747 | 24.5084 | 23.2179 | 22.1358 | 21.1147 | 16.5042 | 12.3116 | 8.4368
|  | MAIDENHEAD PRIMARY | HE |  |  |  |  | 37.0021 | 36.7263 | 36.42 | 36.0905 | 35.26 | 34.3926 | 33.5453 | 32.98 | 32.4621 | 30.1011 | 27.9789 | -6.6926 | 31.5305 | 30.86 | 29.8474 | 28.1537 | 27.1347 | 26.1579 | 25.2021 | 24.5821 | 24.0095 | 21.3621 | 18.9421 | 16.8116 | 32.7989 | 32.4168 | 31.4547 | 29.8611 | 28.8905 | 27.9611 | 27.0505 | 26.4495 | 25.8779 | 23.2284 | 20.8 | 18.6674
|  | MAIDENHEAD PRIMARY | CF |  |  |  |  | 37.2579 | 37.1116 | 36.96 | 36.8042 | 36.6421 | 36.4747 | 36.3126 | 36.1516 | 35.9632 | 34.2653 | 32.8611 | 31.66 | 31.9863 | 31.7916 | 31.3505 | 30.7042 | 30.1189 | 29.4642 | 28.7853 | 28.3105 | 27.9316 | 26.0316 | 24.4137 | 23.0116 | 33.0726 | 32.9168 | 32.7484 | 32.2768 | 31.7232 | 31.1032 | 30.4632 | 30.0105 | 29.6463 | 27.8326 | 26.2811 | 24.8768
MELKSHAM GSP | CHIPPENHAM BSP | MALMESBURY PRIMARY | MINIMUM HEADROOM | ST 92288 87493 | NO | YES | 0.063158 | 14.3705 | 13.8905 | 13.5253 | 13.1947 | 12.8568 | 11.44 | 10.6442 | 10.4621 | 10.4032 | 8.7832 | 4.1242 | -9.0379 | 9.4968 | 8.8305 | 8.4379 | 8.0853 | 7.7284 | 6.0768 | 5.1621 | 4.9832 | 4.8179 | 3.0695 | -2.2663 | -2.9516 | 10.4189 | 9.7368 | 9.3358 | 8.9789 | 8.6179 | 6.9663 | 6.0484 | 5.8653 | 5.6958 | 3.9189 | -1.4495 | -2.1484
|  | MALMESBURY PRIMARY | EE |  |  |  |  | 14.4789 | 14.1705 | 13.8684 | 13.6 | 13.3179 | 13.0432 | 12.7747 | 12.5337 | 12.2926 | 9.5189 | 7.5989 | 5.1242 | 9.7305 | 9.1347 | 8.8095 | 8.5232 | 8.2295 | 7.9411 | 7.6621 | 7.4232 | 7.1705 | 4.0032 | 1.8421 | -1.0653 | 10.6558 | 10.0442 | 9.7137 | 9.4242 | 9.1242 | 8.8295 | 8.5442 | 8.3011 | 8.0432 | 4.8358 | 2.6295 | -0.29158
|  | MALMESBURY PRIMARY | HT |  |  |  |  | 14.3705 | 13.8905 | 13.5253 | 13.1947 | 12.8568 | 11.44 | 10.6442 | 10.4621 | 10.4032 | 8.7832 | 4.1242 | 3.4674 | 9.4968 | 8.8305 | 8.4379 | 8.0853 | 7.7284 | 6.0768 | 5.1621 | 4.9832 | 4.8179 | 3.0695 | -2.2663 | -2.9516 | 10.4189 | 9.7368 | 9.3358 | 8.9789 | 8.6179 | 6.9663 | 6.0484 | 5.8653 | 5.6958 | 3.9189 | -1.4495 | -2.1484
|  | MALMESBURY PRIMARY | HE |  |  |  |  | 14.6221 | 14.5158 | 14.3326 | 14.1442 | 13.9421 | 13.7463 | 13.5632 | 13.3863 | 13.2295 | 10.7074 | 9.3116 | -9.0379 | 10.04 | 9.5442 | 9.3116 | 9.1126 | 8.9032 | 8.7 | 8.5095 | 8.3253 | 8.1632 | 5.2337 | 3.6074 | 0.98105 | 10.9705 | 10.4632 | 10.2263 | 10.0253 | 9.8105 | 9.6042 | 9.4095 | 9.2211 | 9.0558 | 6.0979 | 4.4547 | 1.8168
|  | MALMESBURY PRIMARY | CF |  |  |  |  | 14.7211 | 14.6653 | 14.6074 | 14.5474 | 14.4821 | 14.4137 | 14.3474 | 14.2832 | 14.2179 | 13.8421 | 13.3221 | 12.7442 | 10.4832 | 10.2295 | 10.1011 | 9.9916 | 9.8621 | 9.7253 | 9.6021 | 9.4874 | 9.3716 | 8.8284 | 8.2547 | 7.5989 | 11.4242 | 11.1642 | 11.0347 | 10.9221 | 10.7905 | 10.6505 | 10.5242 | 10.4084 | 10.2884 | 9.7347 | 9.1411 | 8.4674
MINETY GSP | SWINDON BSP | MANCHESTER ROAD PRIMARY | MINIMUM HEADROOM | SU 15254 85130 | NO | YES | 0.13158 | 68.0718 | 67.7855 | 67.4803 | 67.1603 | 66.3118 | 63.4424 | 60.2992 | 57.5718 | 54.8129 | 47.1139 | 42.7845 | 7.8108 | 61.5013 | 60.955 | 60.1645 | 58.8855 | 55.3582 | 51.8382 | 48.2003 | 45.0466 | 41.8529 | 33.0024 | 28.0666 | 24.3571 | 62.6866 | 62.3655 | 62.0213 | 60.9497 | 57.475 | 53.9539 | 50.315 | 47.1603 | 43.9655 | 35.1129 | 30.1761 | 26.4645
|  | MANCHESTER ROAD PRIMARY | EE |  |  |  |  | 68.2403 | 68.0045 | 67.7539 | 67.4866 | 67.2076 | 66.1266 | 63.5624 | 63.3055 | 60.1182 | 52.0929 | 48.4129 | 45.8434 | 61.6824 | 61.4297 | 60.9508 | 60.1866 | 57.6308 | 55.0571 | 51.9476 | 51.6908 | 47.9887 | 38.7182 | 34.5076 | 31.5718 | 62.8718 | 62.6139 | 62.3371 | 62.0287 | 59.7424 | 57.1739 | 54.0634 | 53.8066 | 50.1034 | 40.8297 | 36.6182 | 33.6813
|  | MANCHESTER ROAD PRIMARY | HT |  |  |  |  | 68.0718 | 67.7855 | 67.4803 | 67.1603 | 66.3118 | 63.4424 | 60.2992 | 57.5718 | 54.8129 | 47.1139 | 42.7845 | 39.5213 | 61.5013 | 60.955 | 60.1645 | 58.8855 | 55.3582 | 51.8382 | 48.2003 | 45.0466 | 41.8529 | 33.0024 | 28.0666 | 24.3571 | 62.6866 | 62.3655 | 62.0213 | 60.9497 | 57.475 | 53.9539 | 50.315 | 47.1603 | 43.9655 | 35.1129 | 30.1761 | 26.4645
|  | MANCHESTER ROAD PRIMARY | HE |  |  |  |  | 68.4087 | 68.2192 | 68.0097 | 67.7845 | 67.5445 | 66.8887 | 64.3097 | 64.1076 | 61.1571 | 53.9034 | 50.8529 | 7.8108 | 61.8624 | 61.6592 | 61.4318 | 60.8466 | 58.4687 | 55.9708 | 52.7508 | 52.5487 | 49.115 | 40.7034 | 37.1876 | 34.9171 | 63.0561 | 62.8487 | 62.6171 | 62.355 | 60.5624 | 58.0876 | 54.8666 | 54.6645 | 51.2297 | 42.8161 | 39.2982 | 37.0276
|  | MANCHESTER ROAD PRIMARY | CF |  |  |  |  | 68.5361 | 68.4192 | 68.2982 | 68.1739 | 68.0445 | 67.9129 | 67.7834 | 67.655 | 67.5266 | 59.8297 | 57.1087 | 55.8582 | 61.9961 | 61.875 | 61.7497 | 61.6213 | 61.4876 | 61.3518 | 61.1676 | 60.4876 | 59.2161 | 47.515 | 44.3708 | 42.9308 | 63.1908 | 63.0687 | 62.9424 | 62.8129 | 62.6771 | 62.5403 | 62.3876 | 62.2076 | 61.2824 | 49.6297 | 46.4845 | 45.0445
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON PRIMARY | MINIMUM HEADROOM | SU 07592 05256 | NO | YES | 0 | 16.4779 | 16.3326 | 16.1779 | 16.0189 | 15.7884 | 15.2895 | 14.7095 | 14.5758 | 14.6526 | 12.9821 | 11.8789 | 2.6232 | 14.7526 | 14.4832 | 14.2105 | 13.9389 | 13.6653 | 13.0811 | 12.3884 | 12.2558 | 12.1432 | 10.2926 | 8.9716 | 7.9695 | 15.1389 | 14.8768 | 14.6116 | 14.3463 | 14.0779 | 13.5158 | 12.8505 | 12.7158 | 12.5947 | 10.7337 | 9.4011 | 8.3958
|  | MANNINGTON PRIMARY | EE |  |  |  |  | 16.5747 | 16.4589 | 16.3337 | 16.2063 | 16.0726 | 15.9421 | 15.7905 | 15.6147 | 15.4516 | 12.9821 | 11.8789 | 10.9958 | 14.9453 | 14.7358 | 14.5189 | 14.3042 | 14.0895 | 13.88 | 13.6811 | 13.4905 | 13.3147 | 10.2926 | 8.9716 | 7.9695 | 15.3274 | 15.1232 | 14.9116 | 14.7011 | 14.4895 | 14.2832 | 14.0874 | 13.9 | 13.7263 | 10.7337 | 9.4011 | 8.3958
|  | MANNINGTON PRIMARY | HT |  |  |  |  | 16.4779 | 16.3326 | 16.1779 | 16.0189 | 15.7884 | 15.2895 | 14.7095 | 14.5758 | 14.6526 | 13.4684 | 12.0032 | 11.5389 | 14.7526 | 14.4832 | 14.2105 | 13.9389 | 13.6653 | 13.0811 | 12.3884 | 12.2558 | 12.1432 | 10.8453 | 9.1979 | 8.7042 | 15.1389 | 14.8768 | 14.6116 | 14.3463 | 14.0779 | 13.5158 | 12.8505 | 12.7158 | 12.5947 | 11.2916 | 9.6358 | 9.1379
|  | MANNINGTON PRIMARY | HE |  |  |  |  | 16.6937 | 16.6147 | 16.5274 | 16.4347 | 16.3326 | 16.2358 | 16.1442 | 16.0589 | 15.9842 | 13.8358 | 13.0042 | 2.6232 | 15.1958 | 15.0632 | 14.9221 | 14.7147 | 14.5316 | 14.4105 | 14.2947 | 14.1853 | 14.1011 | 11.2274 | 10.1621 | 9.3653 | 15.5705 | 15.44 | 15.3021 | 15.1011 | 14.9221 | 14.8021 | 14.6874 | 14.5779 | 14.4937 | 11.6768 | 10.6084 | 9.8084
|  | MANNINGTON PRIMARY | CF |  |  |  |  | 16.7737 | 16.7358 | 16.6947 | 16.6537 | 16.6095 | 16.5663 | 16.5211 | 16.4779 | 16.4347 | 16.24 | 16.1263 | 15.6537 | 15.3368 | 15.2621 | 15.1842 | 15.1053 | 15.0232 | 14.9432 | 14.8611 | 14.7811 | 14.6989 | 14.3326 | 14.0211 | 13.4421 | 15.7032 | 15.6347 | 15.5589 | 15.4821 | 15.4021 | 15.3232 | 15.2432 | 15.1653 | 15.0853 | 14.7274 | 14.4242 | 13.8737
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | MARKET PRIMARY | MINIMUM HEADROOM | SU 86479 04732 | NO | YES | 0 | 32.0063 | 31.7979 | 31.5758 | 31.3284 | 31.0705 | 30.8126 | 30.4958 | 29.9958 | 29.5884 | 27.2737 | 24.9221 | 3.4305 | 28.4053 | 28.0242 | 27.4326 | 26.9484 | 26.4495 | 26.0032 | 25.3726 | 24.7516 | 24.2547 | 21.3189 | 18.6053 | 16.06 | 29.0284 | 28.7989 | 28.5537 | 28.1116 | 27.6316 | 27.1863 | 26.5558 | 25.9358 | 25.4389 | 22.5074 | 19.7979 | 17.2558
|  | MARKET PRIMARY | EE |  |  |  |  | 32.1253 | 31.9516 | 31.7674 | 31.5716 | 31.3642 | 31.1579 | 30.9411 | 30.7337 | 30.4484 | 28.5642 | 26.8453 | 25.0768 | 28.5442 | 28.3116 | 27.8895 | 27.5168 | 27.1358 | 26.8063 | 26.2358 | 25.7095 | 25.3105 | 22.9179 | 20.7495 | 18.7263 | 29.1568 | 28.9653 | 28.7621 | 28.5547 | 28.2747 | 27.9642 | 27.4179 | 26.8926 | 26.4937 | 24.1042 | 21.9389 | 19.9189
|  | MARKET PRIMARY | HT |  |  |  |  | 32.0063 | 31.7979 | 31.5758 | 31.3284 | 31.0705 | 30.8126 | 30.4958 | 29.9958 | 29.5884 | 27.2737 | 24.9221 | 22.6874 | 28.4053 | 28.0242 | 27.4326 | 26.9484 | 26.4495 | 26.0032 | 25.3726 | 24.7516 | 24.2547 | 21.3189 | 18.6053 | 16.06 | 29.0284 | 28.7989 | 28.5537 | 28.1116 | 27.6316 | 27.1863 | 26.5558 | 25.9358 | 25.4389 | 22.5074 | 19.7979 | 17.2558
|  | MARKET PRIMARY | HE |  |  |  |  | 32.2632 | 32.1295 | 31.9811 | 31.8221 | 31.6526 | 31.4905 | 31.3358 | 31.1726 | 31.0368 | 29.8526 | 28.5621 | 3.4305 | 28.7074 | 28.5453 | 28.3537 | 28.1316 | 27.8526 | 27.6116 | 27.1305 | 26.6968 | 26.3926 | 24.4705 | 22.7653 | 21.1968 | 29.3074 | 29.16 | 28.9968 | 28.8295 | 28.6526 | 28.4853 | 28.2653 | 27.8758 | 27.5737 | 25.6547 | 23.9526 | 22.3874
|  | MARKET PRIMARY | CF |  |  |  |  | 32.3632 | 32.2842 | 32.2032 | 32.1179 | 32.0305 | 31.9421 | 31.8547 | 31.7674 | 31.6811 | 31.2495 | 30.6179 | 29.8811 | 28.8253 | 28.7305 | 28.6337 | 28.5379 | 28.4389 | 28.3421 | 28.1863 | 27.98 | 27.7958 | 26.4832 | 25.3621 | 24.3726 | 29.4168 | 29.3295 | 29.2411 | 29.1505 | 29.0568 | 28.9642 | 28.8653 | 28.7674 | 28.6758 | 27.6653 | 26.5453 | 25.5579
MELKSHAM GSP | WEST GRAFTON BSP | MARLBOROUGH SOUTH PRIMARY | MINIMUM HEADROOM | SU 19293 68264 | NO | YES | 0 | 20.1589 | 19.9389 | 19.6958 | 19.0663 | 18.6768 | 18.2895 | 17.9411 | 17.6179 | 17.2821 | 15.4947 | 13.6979 | -5.5611 | 15.1768 | 14.8137 | 14.2611 | 13.5389 | 13.1147 | 12.6958 | 12.3147 | 11.9621 | 11.5874 | 9.6074 | 7.5853 | 5.56 | 16.1821 | 15.8158 | 15.2579 | 14.5284 | 14.1011 | 13.6779 | 13.2947 | 12.94 | 12.5642 | 10.5863 | 8.5674 | 6.5453
|  | MARLBOROUGH SOUTH PRIMARY | EE |  |  |  |  | 20.2895 | 20.1074 | 19.9147 | 19.6526 | 19.2347 | 18.8979 | 18.5926 | 18.2979 | 18.04 | 16.7295 | 15.3558 | 13.9884 | 15.4147 | 15.1221 | 14.7989 | 14.2053 | 13.7379 | 13.3674 | 13.0347 | 12.7126 | 12.4326 | 10.9663 | 9.4147 | 7.8505 | 16.4221 | 16.1274 | 15.8021 | 15.2021 | 14.7295 | 14.3558 | 14.0211 | 13.6968 | 13.4137 | 11.9432 | 10.3947 | 8.8326
|  | MARLBOROUGH SOUTH PRIMARY | HT |  |  |  |  | 20.1589 | 19.9389 | 19.6958 | 19.0663 | 18.6768 | 18.2895 | 17.9411 | 17.6179 | 17.2821 | 15.4947 | 13.6979 | 11.9179 | 15.1768 | 14.8137 | 14.2611 | 13.5389 | 13.1147 | 12.6958 | 12.3147 | 11.9621 | 11.5874 | 9.6074 | 7.5853 | 5.56 | 16.1821 | 15.8158 | 15.2579 | 14.5284 | 14.1011 | 13.6779 | 13.2947 | 12.94 | 12.5642 | 10.5863 | 8.5674 | 6.5453
|  | MARLBOROUGH SOUTH PRIMARY | HE |  |  |  |  | 20.46 | 20.3316 | 20.1895 | 20.0358 | 19.8726 | 19.7011 | 19.48 | 19.2758 | 19.1021 | 18.2242 | 17.2621 | -5.5611 | 15.6821 | 15.5358 | 15.3305 | 14.9011 | 14.5411 | 14.2653 | 14.0263 | 13.8063 | 13.62 | 12.6263 | 11.5042 | 10.3463 | 16.6768 | 16.5442 | 16.3379 | 15.9042 | 15.54 | 15.2621 | 15.0221 | 14.8011 | 14.6126 | 13.6084 | 12.4821 | 11.3263
|  | MARLBOROUGH SOUTH PRIMARY | CF |  |  |  |  | 20.5789 | 20.5105 | 20.44 | 20.3674 | 20.2916 | 20.2147 | 20.1389 | 20.0632 | 19.9874 | 19.4895 | 18.9263 | 18.3126 | 15.8011 | 15.7326 | 15.6621 | 15.5621 | 15.4411 | 15.3189 | 15.1989 | 15.0789 | 14.9589 | 14.0179 | 13.3589 | 12.6168 | 16.7958 | 16.7274 | 16.6568 | 16.5705 | 16.4495 | 16.3263 | 16.2053 | 16.0842 | 15.9642 | 15.0116 | 14.3442 | 13.5937
NURSLING GSP | ROWNHAMS BSP | MAYBUSH PRIMARY | MINIMUM HEADROOM | SU 38426 14930 | NO | YES | 0 | 24.9989 | 24.6853 | 24.3526 | 23.8947 | 24.0389 | 22.8474 | 21.9916 | 21.3705 | 20.5874 | 17.9295 | 15.4684 | -11.8979 | 18.34 | 17.74 | 17.0642 | 16.38 | 16.5642 | 15.1547 | 14.2021 | 13.5232 | 12.3821 | 9.7421 | 7.0032 | 4.4832 | 19.6474 | 19.0495 | 18.3737 | 17.6895 | 17.8737 | 16.1632 | 15.2105 | 14.5316 | 13.6463 | 10.8137 | 7.9779 | 5.4495
|  | MAYBUSH PRIMARY | EE |  |  |  |  | 25.1747 | 24.9137 | 24.6368 | 24.3442 | 24.0389 | 23.4874 | 22.7021 | 21.9326 | 20.5874 | 19.7263 | 17.8221 | 16.1168 | 18.7368 | 18.2589 | 17.7232 | 17.1779 | 16.5642 | 15.9463 | 15.0705 | 14.2095 | 12.3821 | 11.82 | 9.5947 | 7.6758 | 20.0442 | 19.5674 | 19.0316 | 18.4863 | 17.8737 | 17.2558 | 16.3811 | 15.5221 | 13.6463 | 12.8779 | 10.6684 | 8.6505
|  | MAYBUSH PRIMARY | HT |  |  |  |  | 24.9989 | 24.6853 | 24.3526 | 23.8947 | 24.3768 | 22.8474 | 21.9916 | 21.3705 | 20.84 | 17.9295 | 15.4684 | 13.2179 | 18.34 | 17.74 | 17.0642 | 16.38 | 17.1053 | 15.1547 | 14.2021 | 13.5232 | 13.0526 | 9.7421 | 7.0032 | 4.4832 | 19.6474 | 19.0495 | 18.3737 | 17.6895 | 18.2347 | 16.1632 | 15.2105 | 14.5316 | 16.5642 | 10.8137 | 7.9779 | 5.4495
|  | MAYBUSH PRIMARY | HE |  |  |  |  | 25.3832 | 25.1832 | 24.9621 | 24.7242 | 24.4716 | 24.2284 | 24.0011 | 22.8947 | 22.4032 | 26.28 | 25.8158 | -11.8979 | 19.2095 | 18.9105 | 18.5305 | 18.1263 | 17.6442 | 17.1589 | 16.5537 | 14.9368 | 14.3947 | 14.4042 | 12.9653 | 11.7316 | 20.5516 | 20.2284 | 19.8389 | 19.4337 | 18.9526 | 18.4684 | 17.8632 | 16.2126 | 15.6684 | 17.3905 | 16.6653 | 16.0779
|  | MAYBUSH PRIMARY | CF |  |  |  |  | 25.5411 | 25.4284 | 25.3095 | 25.1863 | 25.06 | 24.9305 | 24.8032 | 24.6768 | 24.5505 | 23.4663 | 23.9989 | 23.2421 | 19.4579 | 19.2737 | 19.0821 | 18.8853 | 18.6684 | 18.4474 | 18.2147 | 17.8516 | 17.4758 | 15.8768 | 16.6495 | 15.7842 | 20.8211 | 20.6189 | 20.4105 | 20.1947 | 19.9758 | 19.7547 | 19.5232 | 19.16 | 18.7853 | 17.1874 | 17.7789 | 16.9137
MELKSHAM GSP | NORRINGTON BSP | MELKSHAM TOWN PRIMARY | MINIMUM HEADROOM | ST 90170 64096 | NO | YES | 0 | 41.1503 | 40.8029 | 40.4261 | 40.7629 | 40.3798 | 40.8651 | 39.7177 | 38.7735 | 37.8893 | 33.9366 | 29.8693 | -3.7497 | 37.7924 | 37.3682 | 36.9029 | 36.4987 | 36.0535 | 35.3219 | 34.0566 | 33.0251 | 32.0566 | 27.7187 | 23.1629 | 18.5872 | 39.2619 | 38.8514 | 38.4029 | 38.5693 | 38.1229 | 36.2556 | 34.9903 | 33.9566 | 32.9882 | 28.6514 | 24.0861 | 19.5051
|  | MELKSHAM TOWN PRIMARY | EE |  |  |  |  | 48.124 | 49.224 | 47.8724 | 46.3587 | 44.5956 | 43.0787 | 41.6787 | 40.4893 | 39.5851 | 36.5651 | 33.4493 | 30.2966 | 45.7651 | 44.7029 | 43.1882 | 41.4861 | 39.4956 | 37.7914 | 36.2187 | 34.8924 | 33.8945 | 30.5829 | 27.1072 | 23.5177 | 46.7029 | 45.6419 | 44.1261 | 42.424 | 40.4314 | 38.7261 | 37.1524 | 35.824 | 34.824 | 31.5029 | 28.0229 | 24.4303
|  | MELKSHAM TOWN PRIMARY | HT |  |  |  |  | 47.5808 | 48.484 | 46.6861 | 44.7208 | 42.5672 | 40.8651 | 39.7177 | 38.7735 | 37.8893 | 33.9366 | 29.8693 | 25.8293 | 45.1482 | 43.8977 | 41.8756 | 39.6587 | 37.2229 | 35.3219 | 34.0566 | 33.0251 | 32.0566 | 27.7187 | 23.1629 | 18.5872 | 46.0872 | 44.8356 | 42.8135 | 40.5956 | 38.1598 | 36.2556 | 34.9903 | 33.9566 | 32.9882 | 28.6514 | 24.0861 | 19.5051
|  | MELKSHAM TOWN PRIMARY | HE |  |  |  |  | 48.1851 | 48.1514 | 47.0808 | 47.7451 | 46.1577 | 44.8335 | 43.5766 | 42.6293 | 41.9272 | 39.8745 | 37.5682 | -3.7497 | 46.244 | 45.7724 | 44.484 | 42.9914 | 41.1903 | 39.6924 | 38.2724 | 37.2114 | 36.4324 | 34.1766 | 31.5587 | 28.8208 | 47.3208 | 46.7114 | 45.4219 | 43.9293 | 42.1261 | 40.6282 | 39.2072 | 38.1461 | 37.3661 | 35.1051 | 32.4851 | 29.7408
|  | MELKSHAM TOWN PRIMARY | CF |  |  |  |  | 41.1503 | 40.8029 | 40.4261 | 40.7629 | 40.3798 | 47.4356 | 47.0598 | 46.5429 | 45.9093 | 44.8598 | 43.5103 | 41.9987 | 37.7924 | 37.3682 | 36.9029 | 36.4987 | 36.0535 | 44.9219 | 44.4829 | 43.8651 | 43.0977 | 39.7419 | 38.2219 | 36.4851 | 39.2619 | 38.8514 | 38.4029 | 38.5693 | 38.1229 | 45.8587 | 45.4208 | 44.8019 | 44.0345 | 40.6766 | 39.1545 | 37.4145
NURSLING GSP |  | MARCHWOOD PRIMARY | MINIMUM HEADROOM | SU 39234 11008 | NO | YES | 0 | 17.7147 | 17.6474 | 17.5768 | 17.5032 | 17.3242 | 17.0116 | 16.7074 | 15.5895 | 15.5337 | 15.2632 | 15.0221 | 9.0568 | 16.8579 | 16.7884 | 16.7147 | 16.6389 | 16.5505 | 16.3274 | 15.9747 | 14.64 | 14.5842 | 14.3053 | 14.0505 | 13.7568 | 17.4958 | 17.3747 | 17.2526 | 17.1295 | 16.8063 | 16.46 | 16.1074 | 14.7716 | 14.7158 | 14.4368 | 14.1821 | 13.8884
|  | MARCHWOOD PRIMARY | EE |  |  |  |  | 17.7526 | 17.6979 | 17.6389 | 17.5779 | 17.4989 | 17.2084 | 16.9221 | 16.6874 | 16.6053 | 16.2179 | 15.7884 | 15.3526 | 16.8989 | 16.8421 | 16.7811 | 16.7179 | 16.6411 | 16.5379 | 16.2116 | 15.9389 | 15.8505 | 15.4221 | 14.9295 | 14.4232 | 17.5611 | 17.4842 | 17.3853 | 17.2842 | 16.9832 | 16.6768 | 16.3432 | 16.0716 | 15.9832 | 15.5537 | 15.0621 | 14.5547
|  | MARCHWOOD PRIMARY | HT |  |  |  |  | 17.7147 | 17.6474 | 17.5768 | 17.5032 | 17.3242 | 17.0116 | 16.7074 | 15.5895 | 15.5337 | 15.2632 | 15.0221 | 14.7558 | 16.8579 | 16.7884 | 16.7147 | 16.6389 | 16.5505 | 16.3274 | 15.9747 | 14.64 | 14.5842 | 14.3053 | 14.0505 | 13.7568 | 17.4958 | 17.3747 | 17.2526 | 17.1295 | 16.8063 | 16.46 | 16.1074 | 14.7716 | 14.7158 | 14.4368 | 14.1821 | 13.8884
|  | MARCHWOOD PRIMARY | HE |  |  |  |  | 17.8032 | 17.7632 | 17.72 | 17.6726 | 17.6221 | 17.4558 | 17.1947 | 16.9863 | 16.9295 | 16.6705 | 16.3589 | 9.0568 | 16.9516 | 16.9105 | 16.8663 | 16.8179 | 16.7558 | 16.6958 | 16.5126 | 16.2695 | 16.2095 | 15.9221 | 15.5621 | 15.1821 | 17.6116 | 17.5716 | 17.5284 | 17.4811 | 17.2074 | 16.9368 | 16.6442 | 16.4021 | 16.3411 | 16.0547 | 15.6937 | 15.3147
|  | MARCHWOOD PRIMARY | CF |  |  |  |  | 17.8379 | 17.8168 | 17.7937 | 17.7705 | 17.7474 | 17.7221 | 17.6979 | 17.6295 | 17.5874 | 17.3958 | 17.2063 | 16.9968 | 16.9874 | 16.9663 | 16.9421 | 16.9179 | 16.8895 | 16.8589 | 16.8284 | 16.8011 | 16.7758 | 16.6642 | 16.5305 | 16.2874 | 17.6463 | 17.6253 | 17.6021 | 17.5789 | 17.5063 | 17.3737 | 17.2347 | 17.1126 | 17.0705 | 16.8768 | 16.6663 | 16.42
LOVEDEAN GSP | HAVANT BSP | MEYRICK ROAD PRIMARY | MINIMUM HEADROOM | SU 70849 06469 | NO | YES | 0 | 28.4895 | 27.9863 | 27.4705 | 26.8589 | 25.6747 | 24.4674 | 23.3853 | 22.3821 | 21.4758 | 17.5042 | 12.1905 | -10.5137 | 22.8358 | 21.4126 | 20.2011 | 19.0737 | 17.7716 | 16.44 | 15.2463 | 14.14 | 13.1389 | 8.7411 | 2.7032 | -1.7726 | 23.8663 | 22.5158 | 21.3579 | 20.2789 | 19.0337 | 17.7505 | 16.5568 | 15.4484 | 14.4474 | 10.0453 | 4.0011 | -0.47789
|  | MEYRICK ROAD PRIMARY | EE |  |  |  |  | 28.7674 | 28.3453 | 27.92 | 27.4842 | 26.9484 | 25.9179 | 24.9768 | 24.1474 | 23.4484 | 20.5074 | 16.0589 | 12.9937 | 23.4021 | 22.1526 | 21.1337 | 20.2337 | 19.1674 | 18.0274 | 16.9905 | 16.0789 | 15.3179 | 12.0789 | 7.0063 | 3.5137 | 24.4095 | 23.2253 | 22.2526 | 21.3895 | 20.3695 | 19.2842 | 18.2937 | 17.3884 | 16.6263 | 13.3811 | 8.3011 | 4.8053
|  | MEYRICK ROAD PRIMARY | HT |  |  |  |  | 28.4895 | 27.9863 | 27.4705 | 26.8589 | 25.6747 | 24.4674 | 23.3853 | 22.3821 | 21.4758 | 17.5042 | 12.1905 | 8.2442 | 22.8358 | 21.4126 | 20.2011 | 19.0737 | 17.7716 | 16.44 | 15.2463 | 14.14 | 13.1389 | 8.7411 | 2.7032 | -1.7726 | 23.8663 | 22.5158 | 21.3579 | 20.2789 | 19.0337 | 17.7505 | 16.5568 | 15.4484 | 14.4474 | 10.0453 | 4.0011 | -0.47789
|  | MEYRICK ROAD PRIMARY | HE |  |  |  |  | 29.1274 | 28.8179 | 28.4968 | 28.1642 | 27.7979 | 27.4411 | 26.7916 | 26.14 | 25.6042 | 23.5979 | 20.0084 | -10.5137 | 24.1463 | 23.1221 | 22.3232 | 21.6316 | 20.7547 | 19.8042 | 18.9653 | 18.2474 | 17.6611 | 15.4474 | 11.3179 | 8.64 | 25.1242 | 24.1558 | 23.3937 | 22.7305 | 21.8937 | 20.9895 | 20.1895 | 19.5042 | 18.9421 | 16.7558 | 12.6232 | 9.9421
|  | MEYRICK ROAD PRIMARY | CF |  |  |  |  | 29.3895 | 29.2242 | 29.0611 | 28.8979 | 28.7263 | 28.5442 | 28.3663 | 28.1895 | 28.0179 | 27.28 | 25.0189 | 23.5284 | 24.7926 | 24.2526 | 23.8242 | 23.4526 | 23.02 | 22.5011 | 21.9905 | 21.4989 | 21.0642 | 19.5516 | 16.9189 | 15.2042 | 25.5653 | 25.2295 | 24.8221 | 24.4674 | 24.0547 | 23.5611 | 23.0758 | 22.6095 | 22.1958 | 20.7442 | 18.2284 | 16.5116
MELKSHAM GSP | ANDOVER BSP | MIDDLE WALLOP PRIMARY | MINIMUM HEADROOM | SU 30984 40155 | YES | YES | 0 | 7.1621 | 7.0442 | 6.92 | 6.7232 | 6.2432 | 5.7716 | 5.1916 | 5.1084 | 5.0253 | 3.92 | 2.4242 | 0.013684 | 7.2126 | 7.1011 | 6.9832 | 6.78 | 6.2337 | 5.7 | 5.0358 | 4.9579 | 4.8821 | 3.6905 | 2.04 | 1.6274 | 7.2768 | 7.1537 | 7.0253 | 6.8168 | 6.2937 | 5.7537 | 5.0853 | 5 | 4.9179 | 3.68 | 1.9758 | 1.5421
|  | MIDDLE WALLOP PRIMARY | EE |  |  |  |  | 7.2453 | 7.1505 | 7.0495 | 6.9484 | 6.8326 | 6.7116 | 6.5905 | 6.4705 | 6.3547 | 5.7316 | 4.1821 | 3.2895 | 7.2905 | 7.2021 | 7.1063 | 7.0116 | 6.9063 | 6.7916 | 6.6758 | 6.5589 | 6.4453 | 5.8463 | 4.1568 | 3.1537 | 7.3632 | 7.2653 | 7.16 | 7.0558 | 6.9358 | 6.8105 | 6.6853 | 6.5611 | 6.44 | 5.8021 | 4.0389 | 3.0126
|  | MIDDLE WALLOP PRIMARY | HT |  |  |  |  | 7.1621 | 7.0442 | 6.92 | 6.7232 | 6.2432 | 5.7716 | 5.1916 | 5.1084 | 5.0253 | 3.92 | 2.4242 | 2.0274 | 7.2126 | 7.1011 | 6.9832 | 6.78 | 6.2337 | 5.7 | 5.0358 | 4.9579 | 4.8821 | 3.6905 | 2.04 | 1.6274 | 7.2768 | 7.1537 | 7.0253 | 6.8168 | 6.2937 | 5.7537 | 5.0853 | 5 | 4.9179 | 3.68 | 1.9758 | 1.5421
|  | MIDDLE WALLOP PRIMARY | HE |  |  |  |  | 7.3516 | 7.2947 | 7.2253 | 7.1579 | 7.0737 | 6.9905 | 6.9147 | 6.84 | 6.7695 | 6.4432 | 5.3716 | 0.013684 | 7.3916 | 7.3368 | 7.2705 | 7.2063 | 7.1305 | 7.0558 | 6.9874 | 6.92 | 6.8547 | 6.5495 | 5.3284 | 4.4968 | 7.4642 | 7.4137 | 7.3442 | 7.2747 | 7.1863 | 7.1021 | 7.0221 | 6.9453 | 6.8737 | 6.5653 | 5.3242 | 4.4747
|  | MIDDLE WALLOP PRIMARY | CF |  |  |  |  | 7.4126 | 7.38 | 7.3411 | 7.2979 | 7.2421 | 7.1947 | 7.1484 | 7.1053 | 7.0632 | 6.8558 | 6.3347 | 5.7947 | 7.4495 | 7.4189 | 7.3821 | 7.3421 | 7.2926 | 7.2495 | 7.2084 | 7.1695 | 7.1316 | 6.9389 | 6.3589 | 5.7442 | 7.5168 | 7.4895 | 7.4579 | 7.4179 | 7.36 | 7.3095 | 7.2611 | 7.2168 | 7.1726 | 6.9568 | 6.3937 | 5.7674
FLEET-BRAMLEY GSP | FERNHURST BSP | MIDHURST PRIMARY | MINIMUM HEADROOM | SU 88127 19555 | NO | YES | 2.1053 | 31.5726 | 31.3716 | 31.1579 | 30.9347 | 30.6421 | 30.1937 | 29.8032 | 29.3853 | 28.9526 | 27.0137 | 24.9611 | 7.8737 | 27.2547 | 26.9368 | 26.5768 | 26.1884 | 25.7853 | 25.4211 | 25.0168 | 24.5653 | 24.0937 | 22.1147 | 19.7632 | 17.6232 | 27.6421 | 27.3853 | 27.1011 | 26.8168 | 26.5253 | 26.1968 | 25.8558 | 25.4853 | 25.0105 | 22.9863 | 20.4947 | 18.3568
|  | MIDHURST PRIMARY | EE |  |  |  |  | 31.5726 | 31.3716 | 31.1579 | 30.9347 | 30.7042 | 30.4116 | 30.0853 | 29.7411 | 29.3895 | 27.9126 | 28.6758 | 24.8632 | 27.2547 | 26.9368 | 26.5768 | 26.1884 | 25.7853 | 25.4211 | 25.0747 | 24.7074 | 24.3274 | 22.7116 | 21.1042 | 19.2874 | 27.6421 | 27.3853 | 27.1011 | 26.8168 | 26.5253 | 26.1968 | 25.8558 | 25.4958 | 25.1242 | 23.4832 | 21.7326 | 19.9632
|  | MIDHURST PRIMARY | HT |  |  |  |  | 31.7716 | 31.5274 | 31.2674 | 31 | 30.6421 | 30.1937 | 29.8032 | 29.3853 | 28.9526 | 27.0137 | 24.9611 | 23.1053 | 27.9221 | 27.4684 | 26.9432 | 26.4316 | 25.9095 | 25.4316 | 25.0168 | 24.5653 | 24.0937 | 22.1147 | 19.7632 | 17.6232 | 28.7726 | 28.3284 | 27.8147 | 27.3137 | 26.8021 | 26.3337 | 25.9263 | 25.4853 | 25.0105 | 22.9863 | 20.4947 | 18.3568
|  | MIDHURST PRIMARY | HE |  |  |  |  | 31.7621 | 31.6189 | 31.4621 | 31.2926 | 31.1116 | 30.9389 | 30.7768 | 30.6242 | 30.4937 | 29.5674 | 29 | 7.8737 | 27.6095 | 27.3989 | 27.1442 | 26.8937 | 26.6263 | 26.3916 | 26.1663 | 25.9063 | 25.6284 | 24.5053 | 23.1389 | 21.6632 | 27.9105 | 27.7358 | 27.5316 | 27.3232 | 27.1011 | 26.8989 | 26.7084 | 26.5168 | 26.3337 | 25.3032 | 24.1295 | 23.6084
|  | MIDHURST PRIMARY | CF |  |  |  |  | 31.8937 | 31.8179 | 31.74 | 31.66 | 31.5758 | 31.4905 | 31.4074 | 31.3242 | 31.2411 | 30.8716 | 30.1137 | 29.4305 | 27.8105 | 27.6863 | 27.5516 | 27.4147 | 27.2705 | 27.1347 | 27.0021 | 26.8684 | 26.7211 | 25.9358 | 25.0368 | 24.2558 | 28.0758 | 27.9768 | 27.8716 | 27.7642 | 27.6516 | 27.5421 | 27.4347 | 27.3284 | 27.2137 | 26.6874 | 25.8379 | 25.0347
AXMINSTER GSP | YEOVIL BSP | MILBORNE PORT PRIMARY | MINIMUM HEADROOM | ST 67929 19741 | YES | YES | 0 | 4.6263 | 4.4895 | 4.3495 | 4.2074 | 4.0463 | 3.8926 | 3.7421 | 3.6 | 3.4684 | 1.9947 | 1.5958 | -0.87158 | 4.5747 | 4.4263 | 4.2726 | 4.1221 | 3.9579 | 3.8011 | 3.6484 | 3.5042 | 3.3705 | 1.7842 | 1.4221 | 1.2053 | 4.6168 | 4.4684 | 4.3126 | 4.16 | 3.9895 | 3.8274 | 3.6695 | 3.5179 | 3.3779 | 1.7221 | 1.32 | 1.0884
|  | MILBORNE PORT PRIMARY | EE |  |  |  |  | 4.7158 | 4.6042 | 4.4979 | 4.3789 | 4.2442 | 4.1095 | 3.9737 | 3.8379 | 3.7126 | 3.0537 | 2.4263 | 1.9768 | 4.6747 | 4.5537 | 4.4958 | 4.3705 | 4.2337 | 4.1 | 3.9632 | 3.8295 | 3.7074 | 3.0716 | 2.4747 | 2.0021 | 4.7158 | 4.5947 | 4.4737 | 4.3474 | 4.2053 | 4.0642 | 3.92 | 3.7779 | 3.6463 | 2.9484 | 2.2821 | 1.7874
|  | MILBORNE PORT PRIMARY | HT |  |  |  |  | 4.6263 | 4.4895 | 4.3495 | 4.2074 | 4.0463 | 3.8926 | 3.7421 | 3.6 | 3.4684 | 1.9947 | 1.5958 | 1.3653 | 4.5747 | 4.4263 | 4.2726 | 4.1221 | 3.9579 | 3.8011 | 3.6484 | 3.5042 | 3.3705 | 1.7842 | 1.4221 | 1.2053 | 4.6168 | 4.4684 | 4.3126 | 4.16 | 3.9895 | 3.8274 | 3.6695 | 3.5179 | 3.3779 | 1.7221 | 1.32 | 1.0884
|  | MILBORNE PORT PRIMARY | HE |  |  |  |  | 4.8368 | 4.7674 | 4.6905 | 4.6116 | 4.5137 | 4.4295 | 4.3411 | 4.2579 | 4.1842 | 3.8105 | 3.24 | -0.87158 | 4.8095 | 4.7337 | 4.6516 | 4.5663 | 4.4653 | 4.3789 | 4.2874 | 4.2011 | 4.1274 | 3.7505 | 3.1379 | 3.0263 | 4.8474 | 4.7747 | 4.6926 | 4.6084 | 4.5042 | 4.4168 | 4.3221 | 4.2326 | 4.1537 | 3.7547 | 3.1116 | 2.9863
|  | MILBORNE PORT PRIMARY | CF |  |  |  |  | 4.9095 | 4.8695 | 4.8284 | 4.7853 | 4.7337 | 4.6842 | 4.6326 | 4.5821 | 4.5347 | 4.2937 | 4.0916 | 3.8874 | 4.8884 | 4.8442 | 4.7989 | 4.7526 | 4.6979 | 4.6453 | 4.5905 | 4.5368 | 4.4863 | 4.2295 | 4.0211 | 3.8084 | 4.9147 | 4.8768 | 4.8389 | 4.7926 | 4.7379 | 4.6842 | 4.6284 | 4.5737 | 4.5232 | 4.2579 | 4.0368 | 3.8116
FLEET-BRAMLEY GSP | ALDERSHOT BSP | MILFORD PRIMARY | MINIMUM HEADROOM | SU 94719 43018 | NO | YES | 0 | 27.2139 | 26.9476 | 26.6624 | 25.7697 | 25.0076 | 24.3424 | 23.6739 | 23.2192 | 22.7939 | 20.8887 | 19.1708 | 1.0371 | 23.4729 | 23.0055 | 22.0592 | 20.9655 | 20.1224 | 19.395 | 18.6571 | 18.1666 | 17.7076 | 15.6371 | 13.7476 | 12.0445 | 23.6445 | 23.1918 | 22.295 | 21.2613 | 20.4308 | 19.7034 | 18.9655 | 18.4729 | 18.0139 | 15.9361 | 14.0382 | 12.3329
|  | MILFORD PRIMARY | EE |  |  |  |  | 27.3782 | 27.1592 | 26.9276 | 26.3813 | 25.7055 | 25.1371 | 24.5782 | 24.2045 | 23.8476 | 22.3297 | 21.0055 | 19.8613 | 23.6371 | 23.4182 | 22.6234 | 21.6308 | 20.8792 | 20.255 | 19.6392 | 19.2403 | 18.8582 | 17.2171 | 15.7645 | 14.4855 | 23.8087 | 23.5897 | 22.8371 | 21.9003 | 21.1855 | 20.5624 | 19.9455 | 19.5455 | 19.1613 | 17.5087 | 16.0424 | 14.7613
|  | MILFORD PRIMARY | HT |  |  |  |  | 27.2139 | 26.9476 | 26.6624 | 25.7697 | 25.0076 | 24.3424 | 23.6739 | 23.2192 | 22.7939 | 20.8887 | 19.1708 | 17.6403 | 23.4729 | 23.0055 | 22.0592 | 20.9655 | 20.1224 | 19.395 | 18.6571 | 18.1666 | 17.7076 | 15.6371 | 13.7476 | 12.0445 | 23.6445 | 23.1918 | 22.295 | 21.2613 | 20.4308 | 19.7034 | 18.9655 | 18.4729 | 18.0139 | 15.9361 | 14.0382 | 12.3329
|  | MILFORD PRIMARY | HE |  |  |  |  | 27.5908 | 27.4392 | 27.2718 | 27.0929 | 26.6203 | 26.1634 | 25.7139 | 25.4434 | 25.1929 | 24.195 | 23.3561 | 1.0371 | 23.8497 | 23.6982 | 23.3676 | 22.5045 | 21.875 | 21.3687 | 20.8718 | 20.5834 | 20.3161 | 19.2318 | 18.2992 | 17.4876 | 24.0213 | 23.8697 | 23.5518 | 22.7392 | 22.1424 | 21.6592 | 21.1792 | 20.8897 | 20.6213 | 19.5329 | 18.5971 | 17.7834
|  | MILFORD PRIMARY | CF |  |  |  |  | 27.735 | 27.6571 | 27.5761 | 27.4929 | 27.4045 | 27.3161 | 27.2266 | 27.1413 | 27.0539 | 26.6634 | 26.0855 | 25.5708 | 23.9939 | 23.9161 | 23.835 | 23.7518 | 23.6108 | 23.3434 | 23.0634 | 22.9055 | 22.7518 | 22.015 | 21.3266 | 20.7424 | 24.1655 | 24.0876 | 24.0066 | 23.9234 | 23.7855 | 23.5318 | 23.2655 | 23.1139 | 22.9634 | 22.2508 | 21.5971 | 21.0424
MANNINGTON GSP | ARNEWOOD BSP | MILFORD-ON-SEA PRIMARY | MINIMUM HEADROOM | SZ 28252 93347 | NO | YES | 0 | 26.3411 | 26.02 | 25.2358 | 24.4063 | 23.5442 | 22.6137 | 21.7253 | 20.8653 | 20.2295 | 17.9968 | 15.6389 | 2.6095 | 23.3611 | 22.6116 | 21.7579 | 20.8537 | 19.9242 | 18.9084 | 17.9253 | 16.9737 | 16.2842 | 13.9411 | 11.4305 | 9.1621 | 23.3674 | 23.0421 | 22.2137 | 21.3347 | 20.4158 | 19.3821 | 18.3895 | 17.4263 | 16.7263 | 14.3095 | 11.7126 | 9.4095
|  | MILFORD-ON-SEA PRIMARY | EE |  |  |  |  | 26.5147 | 26.2821 | 25.8021 | 25.0642 | 24.3232 | 23.5558 | 22.7779 | 21.9221 | 21.2105 | 19.3116 | 17.2958 | 15.6811 | 23.7326 | 23.1116 | 22.3653 | 21.56 | 20.7611 | 19.9326 | 19.0905 | 18.1442 | 17.3663 | 15.4295 | 13.3432 | 11.5747 | 23.5411 | 23.3084 | 22.8074 | 22.0242 | 21.24 | 20.4126 | 19.5474 | 18.5874 | 17.7926 | 15.7537 | 13.5474 | 11.7421
|  | MILFORD-ON-SEA PRIMARY | HT |  |  |  |  | 26.3411 | 26.02 | 25.2358 | 24.4063 | 23.5442 | 22.6137 | 21.7253 | 20.8653 | 20.2295 | 17.9968 | 15.6389 | 13.5758 | 23.3611 | 22.6116 | 21.7579 | 20.8537 | 19.9242 | 18.9084 | 17.9253 | 16.9737 | 16.2842 | 13.9411 | 11.4305 | 9.1621 | 23.3674 | 23.0421 | 22.2137 | 21.3347 | 20.4158 | 19.3821 | 18.3895 | 17.4263 | 16.7263 | 14.3095 | 11.7126 | 9.4095
|  | MILFORD-ON-SEA PRIMARY | HE |  |  |  |  | 26.7358 | 26.5747 | 26.3968 | 25.9084 | 25.2895 | 24.6589 | 24.0063 | 23.2884 | 22.7505 | 21.6232 | 20.4389 | 2.6095 | 24.2095 | 23.7347 | 23.1316 | 22.4621 | 21.7926 | 21.1063 | 20.3937 | 19.6 | 19.0032 | 17.8316 | 16.5421 | 15.2916 | 23.7621 | 23.6011 | 23.4232 | 22.9074 | 22.2516 | 21.5811 | 20.8789 | 20.0663 | 19.4642 | 18.2505 | 16.9263 | 15.6453
|  | MILFORD-ON-SEA PRIMARY | CF |  |  |  |  | 26.8853 | 26.8021 | 26.7147 | 26.6242 | 26.52 | 26.4137 | 26.1684 | 25.86 | 25.5242 | 24.3958 | 23.6326 | 22.8789 | 24.4674 | 24.2495 | 23.9484 | 23.6295 | 23.3432 | 23.0611 | 22.7505 | 22.4147 | 22.0463 | 20.8347 | 20.0158 | 19.1916 | 23.9116 | 23.8284 | 23.7411 | 23.6505 | 23.5463 | 23.4411 | 23.18 | 22.8516 | 22.4937 | 21.3021 | 20.4726 | 19.6168
MANNINGTON GSP | MANNINGTON BSP | MILL LANE PRIMARY | MINIMUM HEADROOM | SU 14691 05633 | NO | YES | 0 | 35.3495 | 36.3347 | 45.5947 | 44.7474 | 43.5758 | 42.2053 | 40.8937 | 39.7705 | 38.6895 | 34.5179 | 31.7905 | -4.2716 | 29.7926 | 29.0758 | 38.2758 | 37.3547 | 36.0558 | 34.5253 | 33.0537 | 31.7989 | 30.5884 | 25.9421 | 22.9421 | 20.0305 | 31.0684 | 30.3516 | 39.5516 | 38.6295 | 37.3284 | 35.7937 | 34.32 | 33.0632 | 31.8495 | 27.1821 | 24.1579 | 21.2368
|  | MILL LANE PRIMARY | EE |  |  |  |  | 35.3495 | 36.9421 | 46.3726 | 45.7263 | 44.7726 | 43.7116 | 42.6095 | 41.3747 | 40.2947 | 36.4368 | 34.3253 | 32.3547 | 30.2042 | 29.7347 | 39.1242 | 38.4242 | 37.3705 | 36.1874 | 34.9547 | 33.5642 | 32.3505 | 28.04 | 25.7274 | 23.5137 | 31.5 | 31.0105 | 40.3979 | 39.6989 | 38.6421 | 37.4558 | 36.2189 | 34.8263 | 33.6063 | 29.2674 | 26.9232 | 24.6989
|  | MILL LANE PRIMARY | HT |  |  |  |  | 37.0021 | 36.3347 | 45.5947 | 44.7474 | 43.5758 | 42.2053 | 40.8937 | 39.7705 | 38.6895 | 34.5179 | 31.7905 | 29.1905 | 29.7926 | 29.0758 | 38.2758 | 37.3547 | 36.0558 | 34.5253 | 33.0537 | 31.7989 | 30.5884 | 25.9421 | 22.9421 | 20.0305 | 31.0684 | 30.3516 | 39.5516 | 38.6295 | 37.3284 | 35.7937 | 34.32 | 33.0632 | 31.8495 | 27.1821 | 24.1579 | 21.2368
|  | MILL LANE PRIMARY | HE |  |  |  |  | 38.0621 | 37.7253 | 47.3316 | 46.8495 | 46.0411 | 45.1316 | 44.1463 | 43.0811 | 42.18 | 39.1137 | 37.7305 | -4.2716 | 30.9442 | 30.5863 | 40.1642 | 39.6442 | 38.7453 | 37.7232 | 36.6126 | 35.4053 | 34.3832 | 30.9179 | 29.3747 | 27.8189 | 32.22 | 31.8611 | 41.44 | 40.9189 | 40.0179 | 38.9958 | 37.8821 | 36.6716 | 35.6484 | 32.1716 | 30.6189 | 29.0537
|  | MILL LANE PRIMARY | CF |  |  |  |  | 35.8526 | 38.2095 | 48.0095 | 47.8053 | 47.5105 | 47.2042 | 46.8537 | 46.4463 | 46.0032 | 42.9305 | 41.9895 | 41.0979 | 31.2042 | 31.1011 | 40.8863 | 40.6663 | 40.3432 | 40.0074 | 39.6168 | 39.1621 | 38.6642 | 35.1568 | 34.1074 | 33.0937 | 32.0326 | 32.3768 | 42.1621 | 41.9421 | 41.6179 | 41.28 | 40.8905 | 40.4347 | 39.9347 | 36.4232 | 35.3684 | 34.3505
COWLEY GSP | DRAYTON BSP | MILTON PRIMARY | MINIMUM HEADROOM | SU 49992 92060 | NO | YES | 0 | 70.1147 | 68.56 | 66.4116 | 64.0179 | 62.6516 | 61.5253 | 59.3295 | 58.8211 | 57.0905 | 62.36 | 60.2884 | -9.2432 | 61.0053 | 58.9379 | 56.6042 | 53.8832 | 52.2895 | 51.2442 | 48.7432 | 48.12 | 46.1484 | 51.9379 | 49.5968 | 46.9474 | 62.8411 | 60.7726 | 58.3389 | 55.6074 | 53.9916 | 52.7 | 50.1958 | 49.5389 | 47.5621 | 53.4874 | 51.0653 | 48.4147
|  | MILTON PRIMARY | EE |  |  |  |  | 70.3737 | 68.56 | 66.5158 | 64.2579 | 62.6516 | 62.7084 | 60.6189 | 58.8211 | 57.0905 | 78.0126 | 73.0905 | 68.7611 | 61.0053 | 58.9379 | 56.6042 | 54.02 | 52.2895 | 52.5505 | 50.1663 | 48.12 | 46.1484 | 81.9516 | 76.3295 | 71.3695 | 62.8411 | 60.7726 | 58.4389 | 55.8526 | 53.9916 | 53.98 | 51.5895 | 49.5389 | 47.5621 | 89.1126 | 83.4621 | 78.4768
|  | MILTON PRIMARY | HT |  |  |  |  | 70.5579 | 68.5989 | 66.4116 | 64.0179 | 63.8168 | 61.5253 | 59.3295 | 86.0874 | 84.2726 | 76.0116 | 70.3495 | 65.2316 | 61.3379 | 59.1105 | 56.6179 | 53.8832 | 53.8495 | 51.2442 | 48.7432 | 78.3947 | 88.6947 | 79.7305 | 73.2737 | 67.4168 | 63.0558 | 60.8295 | 58.3389 | 55.6074 | 55.3084 | 52.7 | 50.1958 | 84.7737 | 96.3989 | 86.9442 | 80.4758 | 74.6095
|  | MILTON PRIMARY | HE |  |  |  |  | 70.5958 | 69.5442 | 67.7463 | 65.4958 | 64.0726 | 64.3084 | 62.3926 | 60.7695 | 59.2116 | 80.9495 | 76.7832 | -9.2432 | 61.7684 | 60 | 57.9337 | 55.3389 | 53.8042 | 54.2526 | 52.0537 | 50.1937 | 48.4074 | 84.7632 | 80.2768 | 76.0853 | 63.6484 | 61.8505 | 59.7863 | 57.1947 | 55.5316 | 55.7137 | 53.5137 | 51.6516 | 49.8632 | 92.3053 | 87.4874 | 83.2874
|  | MILTON PRIMARY | CF |  |  |  |  | 70.1147 | 69.9874 | 69.6316 | 68.64 | 67.7358 | 67.6389 | 66.6526 | 65.7421 | 64.7916 | 62.36 | 60.2884 | 58.0063 | 61.7432 | 60.9179 | 59.9579 | 58.8147 | 57.7779 | 57.7937 | 56.6579 | 55.6126 | 54.5189 | 51.9379 | 49.5968 | 46.9474 | 63.8221 | 62.9316 | 61.9726 | 60.8316 | 59.7958 | 59.6505 | 58.5168 | 57.4726 | 56.3811 | 53.4874 | 51.0653 | 48.4147
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON PRIMARY | MINIMUM HEADROOM | ST 96164 14520 | YES | YES | 0 | 5.5189 | 5.4389 | 5.3589 | 5.2779 | 5.1989 | 5.12 | 5.0495 | 4.9842 | 4.9221 | 4.6505 | 4.3737 | 1.28 | 4.9421 | 4.8568 | 4.7716 | 4.6863 | 4.6021 | 4.5189 | 4.4432 | 4.3747 | 4.3084 | 4.0168 | 3.7116 | 3.4137 | 5.1495 | 5.0695 | 4.9884 | 4.9074 | 4.8274 | 4.7474 | 4.6758 | 4.6105 | 4.5474 | 4.2737 | 3.9926 | 3.7211
|  | MINCHINGTON PRIMARY | EE |  |  |  |  | 5.5737 | 5.5105 | 5.4463 | 5.3821 | 5.3168 | 5.2547 | 5.1958 | 5.1389 | 5.0884 | 4.8779 | 4.6863 | 4.5011 | 5.0021 | 4.9347 | 4.8663 | 4.7979 | 4.7295 | 4.6642 | 4.6011 | 4.5411 | 4.4874 | 4.2621 | 4.0516 | 3.8453 | 5.2053 | 5.1421 | 5.0768 | 5.0116 | 4.9463 | 4.8842 | 4.8242 | 4.7674 | 4.7158 | 4.5032 | 4.3084 | 4.1211
|  | MINCHINGTON PRIMARY | HT |  |  |  |  | 5.5189 | 5.4389 | 5.3589 | 5.2779 | 5.1989 | 5.12 | 5.0495 | 4.9842 | 4.9221 | 4.6505 | 4.3737 | 4.1063 | 4.9421 | 4.8568 | 4.7716 | 4.6863 | 4.6021 | 4.5189 | 4.4432 | 4.3747 | 4.3084 | 4.0168 | 3.7116 | 3.4137 | 5.1495 | 5.0695 | 4.9884 | 4.9074 | 4.8274 | 4.7474 | 4.6758 | 4.6105 | 4.5474 | 4.2737 | 3.9926 | 3.7211
|  | MINCHINGTON PRIMARY | HE |  |  |  |  | 5.6474 | 5.6074 | 5.5642 | 5.52 | 5.4747 | 5.4316 | 5.3905 | 5.3516 | 5.3168 | 5.1926 | 5.0758 | 1.28 | 5.0821 | 5.0389 | 4.9937 | 4.9484 | 4.9 | 4.8558 | 4.8126 | 4.7716 | 4.7347 | 4.6032 | 4.4747 | 4.3484 | 5.28 | 5.2389 | 5.1958 | 5.1516 | 5.1063 | 5.0632 | 5.0221 | 4.9821 | 4.9474 | 4.8211 | 4.7032 | 4.5895
|  | MINCHINGTON PRIMARY | CF |  |  |  |  | 5.6895 | 5.6663 | 5.6432 | 5.6189 | 5.5947 | 5.5695 | 5.5453 | 5.5211 | 5.4968 | 5.3884 | 5.2979 | 5.2158 | 5.1263 | 5.1021 | 5.0768 | 5.0516 | 5.0253 | 4.9989 | 4.9726 | 4.9463 | 4.9211 | 4.8053 | 4.7053 | 4.6116 | 5.3232 | 5.2989 | 5.2758 | 5.2516 | 5.2263 | 5.2021 | 5.1768 | 5.1516 | 5.1284 | 5.0189 | 4.9263 | 4.8421
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE PRIMARY | MINIMUM HEADROOM | SU 01647 91932 | NO | YES | 0 | 14.3368 | 14.2589 | 14.1726 | 13.4916 | 12.1326 | 10.8495 | 9.6232 | 8.5021 | 7.16 | 3.6968 | 2.5316 | 0.70105 | 12.6347 | 12.5579 | 12.4737 | 11.7074 | 10.1484 | 8.68 | 7.28 | 6.0053 | 4.4705 | 0.65579 | -0.43474 | -1.2411 | 12.7242 | 12.6463 | 12.56 | 11.7947 | 10.2253 | 8.7442 | 7.3305 | 6.0411 | 4.4895 | 0.55474 | -0.68105 | -1.5442
|  | MINETY VILLAGE PRIMARY | EE |  |  |  |  | 14.3368 | 14.2589 | 14.1726 | 13.6937 | 12.3621 | 11.0947 | 9.8747 | 8.7442 | 7.4063 | 3.9105 | 2.6884 | 2.0105 | 12.6347 | 12.5579 | 12.4737 | 11.9274 | 10.3989 | 8.9547 | 7.5684 | 6.2895 | 4.7716 | 0.99053 | -0.086316 | -0.75789 | 12.7242 | 12.6463 | 12.56 | 12.0137 | 10.4737 | 9.0105 | 7.6063 | 6.3053 | 4.7632 | 0.81263 | -0.46737 | -1.2011
|  | MINETY VILLAGE PRIMARY | HT |  |  |  |  | 16.0305 | 15.4211 | 14.5884 | 13.4916 | 12.1326 | 10.8495 | 9.6232 | 8.5021 | 7.16 | 3.6968 | 2.5316 | 1.74 | 14.6032 | 13.9158 | 12.9779 | 11.7074 | 10.1484 | 8.68 | 7.28 | 6.0053 | 4.4705 | 0.65579 | -0.43474 | -1.2411 | 14.7232 | 14.0242 | 13.0642 | 11.7947 | 10.2253 | 8.7442 | 7.3305 | 6.0411 | 4.4895 | 0.55474 | -0.68105 | -1.5442
|  | MINETY VILLAGE PRIMARY | HE |  |  |  |  | 14.4116 | 14.3611 | 14.3042 | 13.9884 | 12.7063 | 11.5137 | 10.3716 | 9.3263 | 8.0811 | 5.1389 | 4.6147 | 0.70105 | 12.7095 | 12.6589 | 12.6021 | 12.2432 | 10.7632 | 9.3853 | 8.0705 | 6.8674 | 5.4284 | 2.1147 | 1.6095 | 1.12 | 12.7989 | 12.7484 | 12.6916 | 12.3316 | 10.8453 | 9.46 | 8.1358 | 6.9253 | 5.4768 | 2.0947 | 1.5326 | 0.99263
|  | MINETY VILLAGE PRIMARY | CF |  |  |  |  | 16.5053 | 16.2505 | 15.9168 | 15.4853 | 14.9568 | 14.4105 | 13.8442 | 13.2853 | 12.5653 | 10.7916 | 10.4789 | 10.1495 | 15.1242 | 14.8337 | 14.4526 | 13.9589 | 13.3632 | 12.7421 | 12.0895 | 11.4442 | 10.6084 | 8.5821 | 8.2768 | 7.9526 | 15.2495 | 14.9547 | 14.5674 | 14.0653 | 13.4537 | 12.82 | 12.1632 | 11.5147 | 10.6768 | 8.6305 | 8.2947 | 7.9358
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | MORTIMER PRIMARY | MINIMUM HEADROOM | SU 62236 64103 | NO | YES | 0 | 17.2274 | 17.0242 | 16.8084 | 16.5853 | 16.1484 | 15.2853 | 14.2474 | 14.0495 | 13.8632 | 11.8695 | 9.3211 | -0.44 | 14.5358 | 14.1737 | 13.7884 | 13.4032 | 12.8179 | 11.8316 | 10.6347 | 10.4411 | 10.2589 | 8.0758 | 5.2168 | 4.4032 | 15.1463 | 14.7716 | 14.3916 | 14.0126 | 13.4368 | 12.4737 | 11.2779 | 11.0789 | 10.8926 | 8.6789 | 5.7853 | 4.9558
|  | MORTIMER PRIMARY | EE |  |  |  |  | 17.3516 | 17.1853 | 17.0095 | 16.8263 | 16.6253 | 16.4263 | 16.2358 | 15.9621 | 15.6968 | 14.5737 | 12.4042 | 10.8642 | 14.7821 | 14.4989 | 14.2084 | 13.9021 | 13.5863 | 13.2747 | 12.9716 | 12.6716 | 12.3937 | 11.2295 | 8.7821 | 7.0358 | 15.4053 | 15.1095 | 14.8063 | 14.5021 | 14.1874 | 13.8768 | 13.5726 | 13.2726 | 12.9947 | 11.8147 | 9.3189 | 7.5558
|  | MORTIMER PRIMARY | HT |  |  |  |  | 17.2274 | 17.0242 | 16.8084 | 16.5853 | 16.1484 | 15.2853 | 14.2474 | 14.0495 | 13.8632 | 11.8695 | 9.3211 | 8.5537 | 14.5358 | 14.1737 | 13.7884 | 13.4032 | 12.8179 | 11.8316 | 10.6347 | 10.4411 | 10.2589 | 8.0758 | 5.2168 | 4.4032 | 15.1463 | 14.7716 | 14.3916 | 14.0126 | 13.4368 | 12.4737 | 11.2779 | 11.0789 | 10.8926 | 8.6789 | 5.7853 | 4.9558
|  | MORTIMER PRIMARY | HE |  |  |  |  | 17.5147 | 17.4021 | 17.2758 | 17.14 | 16.9863 | 16.8389 | 16.7 | 16.5684 | 16.4537 | 16.04 | 14.5326 | -0.44 | 15.1116 | 14.9316 | 14.7389 | 14.5379 | 14.3253 | 14.1189 | 13.92 | 13.7305 | 13.5526 | 12.8716 | 11.0316 | 9.6232 | 15.5832 | 15.4663 | 15.3358 | 15.1579 | 14.9358 | 14.7232 | 14.5147 | 14.32 | 14.1421 | 13.4579 | 11.6411 | 10.2211
|  | MORTIMER PRIMARY | CF |  |  |  |  | 17.6253 | 17.5674 | 17.5074 | 17.4442 | 17.3737 | 17.3032 | 17.2337 | 17.1653 | 17.0979 | 16.7905 | 16.5137 | 15.6242 | 15.3179 | 15.2126 | 15.1042 | 14.9926 | 14.8737 | 14.7537 | 14.6358 | 14.5211 | 14.4063 | 13.8579 | 13.2189 | 12.1789 | 15.7 | 15.6389 | 15.5758 | 15.5095 | 15.4358 | 15.3632 | 15.2526 | 15.1326 | 15.0126 | 14.4505 | 13.8221 | 12.8053
MANNINGTON GSP | SALISBURY BSP | NETHERHAMPTON PRIMARY | MINIMUM HEADROOM | SU 12478 29102 | NO | YES | 9.4737 | 1.9126 | 1.6126 | 1.4316 | 0.76316 | -0.16211 | -1.16 | -2.0842 | -2.8526 | -3.2526 | -4.2558 | -4.9063 | -12.5863 | 0.30737 | -0.029474 | -0.22211 | -0.99263 | -2.0663 | -3.2232 | -4.2979 | -5.1895 | -5.6474 | -6.7726 | -7.4905 | -8.1621 | 0.66842 | 0.33158 | 0.13895 | -0.63053 | -1.7021 | -2.8579 | -3.9305 | -4.8211 | -5.2779 | -6.4032 | -7.1221 | -7.7947
|  | NETHERHAMPTON PRIMARY | EE |  |  |  |  | 2.0716 | 1.78 | 1.6211 | 1.0411 | 0.23474 | -0.52421 | -1.3705 | -2.3568 | -2.7716 | -3.7411 | -4.2284 | -4.6726 | 0.48316 | 0.15474 | -0.016842 | -0.68526 | -1.6221 | -2.5 | -3.4853 | -4.6368 | -5.1126 | -6.2053 | -6.7453 | -7.2442 | 0.84421 | 0.51579 | 0.34421 | -0.32316 | -1.2579 | -2.1358 | -3.1189 | -4.2684 | -4.7442 | -5.8368 | -6.3789 | -6.8789
|  | NETHERHAMPTON PRIMARY | HT |  |  |  |  | 1.9126 | 1.6126 | 1.4316 | 0.76316 | -0.16211 | -1.16 | -2.0842 | -2.8526 | -3.2526 | -4.2558 | -4.9063 | -5.5095 | 0.30737 | -0.029474 | -0.22211 | -0.99263 | -2.0663 | -3.2232 | -4.2979 | -5.1895 | -5.6474 | -6.7726 | -7.4905 | -8.1621 | 0.66842 | 0.33158 | 0.13895 | -0.63053 | -1.7021 | -2.8579 | -3.9305 | -4.8211 | -5.2779 | -6.4032 | -7.1221 | -7.7947
|  | NETHERHAMPTON PRIMARY | HE |  |  |  |  | 2.1674 | 1.9916 | 1.8821 | 1.3432 | 0.56632 | -0.16842 | -0.97368 | -1.8611 | -2.2895 | -3.0316 | -3.3379 | -12.5863 | 0.66 | 0.38632 | 0.26737 | -0.35684 | -1.26 | -2.1168 | -3.0547 | -4.0926 | -4.5884 | -5.4326 | -5.7747 | -6.0916 | 1.0211 | 0.74632 | 0.62842 | 0.0052632 | -0.89684 | -1.7516 | -2.6895 | -3.7253 | -4.2211 | -5.0632 | -5.4063 | -5.7221
|  | NETHERHAMPTON PRIMARY | CF |  |  |  |  | 2.2232 | 2.1926 | 2.1611 | 2.1274 | 1.9958 | 1.7579 | 1.4568 | 1.0705 | 0.84526 | -0.63579 | -0.87474 | -1.08 | 1.0305 | 0.91789 | 0.86211 | 0.64421 | 0.39368 | 0.11789 | -0.23158 | -0.68105 | -0.94105 | -2.6642 | -2.9337 | -3.1674 | 1.4137 | 1.2884 | 1.2295 | 1.0042 | 0.75368 | 0.47895 | 0.13053 | -0.31895 | -0.57789 | -2.3 | -2.5674 | -2.8021
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON PRIMARY | MINIMUM HEADROOM | SU 47615 12025 | NO | YES | 0 | 47.9537 | 47.2842 | 46.1211 | 43.6947 | 42.4189 | 40.9884 | 39.6863 | 38.3621 | 36.9937 | 30.1758 | 24.2979 | -17.6895 | 39.1211 | 36.5547 | 33.1032 | 30.4442 | 29.0979 | 27.5768 | 26.1705 | 24.7263 | 23.2211 | 15.6505 | 9.0874 | 3.1179 | 40.9558 | 38.4053 | 34.8674 | 32.1474 | 30.7821 | 29.2368 | 27.8263 | 26.38 | 24.8716 | 17.2811 | 10.6937 | 4.7137
|  | NETLEY COMMON PRIMARY | EE |  |  |  |  | 48.3516 | 50.3126 | 47.72 | 45.4011 | 44.1337 | 42.8379 | 41.7274 | 40.6105 | 39.5074 | 34.1453 | 29.4979 | 25.4274 | 39.9726 | 37.7053 | 34.8358 | 32.3516 | 30.9768 | 29.5684 | 28.3705 | 27.1642 | 25.9632 | 20.0295 | 14.8411 | 10.2379 | 41.8979 | 39.5768 | 36.6337 | 34.0168 | 32.64 | 31.2274 | 30.0263 | 28.8158 | 27.6095 | 21.6484 | 16.4284 | 11.8147
|  | NETLEY COMMON PRIMARY | HT |  |  |  |  | 47.9537 | 47.2842 | 46.1211 | 43.6947 | 42.4189 | 40.9884 | 39.6863 | 38.3621 | 36.9937 | 30.1758 | 24.2979 | 18.9968 | 39.1211 | 36.5547 | 33.1032 | 30.4442 | 29.0979 | 27.5768 | 26.1705 | 24.7263 | 23.2211 | 15.6505 | 9.0874 | 3.1179 | 40.9558 | 38.4053 | 34.8674 | 32.1474 | 30.7821 | 29.2368 | 27.8263 | 26.38 | 24.8716 | 17.2811 | 10.6937 | 4.7137
|  | NETLEY COMMON PRIMARY | HE |  |  |  |  | 48.8484 | 51.6642 | 49.3611 | 47.3316 | 46.3337 | 45.3189 | 44.4958 | 43.6579 | 42.8211 | 38.9632 | 35.6621 | -17.6895 | 41.0789 | 39.1537 | 36.5926 | 34.4558 | 33.3747 | 32.2695 | 31.3853 | 30.4779 | 29.5632 | 25.2674 | 21.5316 | 18.2053 | 43.0242 | 41.0505 | 38.4232 | 36.1211 | 35.0379 | 33.9316 | 33.0453 | 32.1368 | 31.2189 | 26.9116 | 23.1663 | 19.8305
|  | NETLEY COMMON PRIMARY | CF |  |  |  |  | 49.2011 | 48.9884 | 48.7663 | 48.5368 | 48.2968 | 48.0505 | 47.8095 | 47.5705 | 47.3326 | 45.8389 | 43.6253 | 41.6905 | 41.6789 | 40.9189 | 39.8737 | 39.0147 | 38.5811 | 38.0684 | 37.5032 | 36.8547 | 36.16 | 32.8305 | 30.3895 | 28.2211 | 42.6989 | 42.4516 | 41.7116 | 40.88 | 40.4547 | 39.9421 | 39.3674 | 38.7032 | 37.9937 | 34.5905 | 32.0853 | 29.8684
MANNINGTON GSP | ARNEWOOD BSP | NEW MILTON PRIMARY | MINIMUM HEADROOM | SZ 23049 94942 | NO | YES | 0 | 35.3621 | 34.7526 | 33.9253 | 33.0947 | 32.1547 | 31.1063 | 30.1358 | 28.5168 | 28.1084 | 24.1926 | 21.6137 | -7.9263 | 29.4737 | 28.5905 | 27.7063 | 26.8189 | 25.8126 | 24.6789 | 23.6274 | 21.8032 | 21.4011 | 17.1305 | 14.3695 | 10.9295 | 30.1 | 29.2189 | 28.3337 | 27.4484 | 26.4379 | 25.3021 | 24.2463 | 22.42 | 22.0116 | 17.7095 | 14.9116 | 11.4589
|  | NEW MILTON PRIMARY | EE |  |  |  |  | 35.6474 | 35.2663 | 34.8379 | 34.1674 | 33.3832 | 32.5105 | 31.6642 | 30.8347 | 30.0579 | 27.4042 | 24.7432 | 22.3926 | 30.0905 | 29.4011 | 28.6968 | 27.9853 | 27.1442 | 26.2021 | 25.2863 | 24.3884 | 23.5463 | 20.7263 | 17.8358 | 15.2063 | 30.7168 | 30.0263 | 29.3242 | 28.6116 | 27.7684 | 26.82 | 25.9 | 24.9968 | 24.1474 | 21.28 | 18.3358 | 15.6916
|  | NEW MILTON PRIMARY | HT |  |  |  |  | 35.3621 | 34.7526 | 33.9253 | 33.0947 | 32.1547 | 31.1063 | 30.1358 | 28.5168 | 28.1084 | 24.1926 | 21.6137 | 18.5284 | 29.4737 | 28.5905 | 27.7063 | 26.8189 | 25.8126 | 24.6789 | 23.6274 | 21.8032 | 21.4011 | 17.1305 | 14.3695 | 10.9295 | 30.1 | 29.2189 | 28.3337 | 27.4484 | 26.4379 | 25.3021 | 24.2463 | 22.42 | 22.0116 | 17.7095 | 14.9116 | 11.4589
|  | NEW MILTON PRIMARY | HE |  |  |  |  | 36.0042 | 35.7347 | 36.0042 | 35.5389 | 34.9453 | 34.2716 | 33.6189 | 32.9842 | 32.4032 | 30.7305 | 29.0295 | -7.9263 | 30.8453 | 30.4221 | 29.9684 | 29.4779 | 28.8453 | 28.1126 | 27.4042 | 26.7137 | 26.0789 | 24.2916 | 22.4021 | 20.6221 | 31.4453 | 31.0411 | 30.5937 | 30.1042 | 29.4684 | 28.7337 | 28.0242 | 27.3316 | 26.6937 | 24.8874 | 22.9842 | 21.1916
|  | NEW MILTON PRIMARY | CF |  |  |  |  | 36.2526 | 36.1116 | 35.9653 | 35.8126 | 35.6516 | 35.4863 | 35.3232 | 35.0842 | 34.7063 | 33.4716 | 32.3463 | 31.2568 | 31.2642 | 31.0137 | 30.7579 | 30.4947 | 30.1716 | 29.7716 | 29.3611 | 28.9411 | 28.5242 | 27.2063 | 25.9579 | 24.7274 | 31.7116 | 31.5705 | 31.3632 | 31.1137 | 30.7958 | 30.3958 | 29.9842 | 29.5621 | 29.1463 | 27.8221 | 26.5653 | 25.3274
FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT PRIMARY | MINIMUM HEADROOM | SZ 50076 89544 | NO | YES | 0 | 64.6789 | 64.3168 | 63.9326 | 64.7779 | 62.5179 | 60.5 | 58.7916 | 57.2358 | 55.8442 | 49.9463 | 45.08 | 8.3663 | 57.0821 | 55.4074 | 53.5463 | 53.4568 | 50.9042 | 48.6358 | 46.7232 | 44.9853 | 43.4358 | 36.9042 | 31.5411 | 26.8147 | 59.1305 | 57.4579 | 55.6 | 55.3168 | 52.7558 | 50.4779 | 48.5537 | 46.8053 | 45.2432 | 38.6326 | 33.1779 | 28.4147
|  | NEWPORT PRIMARY | EE |  |  |  |  | 64.6789 | 64.3168 | 63.9326 | 65.0053 | 64.3979 | 62.5632 | 60.8926 | 59.2547 | 57.9042 | 52.6274 | 48.5253 | 45.1642 | 57.7189 | 56.4768 | 55.0632 | 55.3968 | 53.0663 | 50.9526 | 49.0832 | 47.2484 | 45.7484 | 39.9495 | 35.4895 | 31.7158 | 59.3021 | 58.2663 | 57.0947 | 57.2568 | 54.9179 | 52.7905 | 50.9063 | 49.0558 | 47.54 | 41.6305 | 37.0432 | 33.2305
|  | NEWPORT PRIMARY | HT |  |  |  |  | 68.1284 | 66.6389 | 64.9884 | 64.7779 | 62.5179 | 60.5 | 58.7916 | 57.2358 | 55.8442 | 49.9463 | 45.08 | 40.8695 | 57.0821 | 55.4074 | 53.5463 | 53.4568 | 50.9042 | 48.6358 | 46.7232 | 44.9853 | 43.4358 | 36.9042 | 31.5411 | 26.8147 | 59.1305 | 57.4579 | 55.6 | 55.3168 | 52.7558 | 50.4779 | 48.5537 | 46.8053 | 45.2432 | 38.6326 | 33.1779 | 28.4147
|  | NEWPORT PRIMARY | HE |  |  |  |  | 65.0032 | 64.7432 | 64.4547 | 65.6221 | 65.2674 | 64.2147 | 62.7211 | 61.2884 | 60.2105 | 56.0263 | 53.0947 | 8.3663 | 58.4526 | 57.4263 | 56.2126 | 56.7411 | 54.6905 | 52.7389 | 51.0484 | 49.4263 | 48.2147 | 43.52 | 40.2221 | 37.3063 | 59.8989 | 59.0937 | 58.0979 | 58.6042 | 56.5463 | 54.5874 | 52.8905 | 51.2611 | 50.0411 | 45.3021 | 41.9674 | 39.0189
|  | NEWPORT PRIMARY | CF |  |  |  |  | 65.2358 | 65.0958 | 64.9505 | 64.8 | 64.6316 | 64.4621 | 64.2947 | 64.1284 | 63.9663 | 60.9116 | 60.7747 | 59.14 | 58.9937 | 58.7189 | 58.2768 | 57.7421 | 57.1284 | 56.4747 | 55.7684 | 54.9516 | 54.0863 | 48.8232 | 48.8516 | 47.0032 | 60.1568 | 60.0021 | 59.7926 | 59.3484 | 58.8368 | 58.2937 | 57.7105 | 57.0168 | 56.1495 | 50.8695 | 50.6632 | 48.7916
FLEET-BRAMLEY GSP | ALDERSHOT BSP | NORMANDY PRIMARY | MINIMUM HEADROOM | SU 93221 52894 | YES | YES | 0 | 6.2337 | 6.1095 | 5.9716 | 5.8221 | 5.6653 | 5.5021 | 5.3421 | 5.1842 | 5.1137 | 4.8189 | 4.3842 | 1.8947 | 6.1695 | 6.0242 | 5.8611 | 5.6842 | 5.4989 | 5.3137 | 5.1358 | 4.9579 | 4.8832 | 4.5716 | 4.0905 | 3.9084 | 6.2968 | 6.1579 | 6.0021 | 5.8263 | 5.64 | 5.4547 | 5.2758 | 5.0979 | 5.0221 | 4.7053 | 4.2189 | 4.0347
|  | NORMANDY PRIMARY | EE |  |  |  |  | 6.2884 | 6.1811 | 6.06 | 5.9274 | 5.7853 | 5.6432 | 5.4968 | 5.3474 | 5.2916 | 5.0568 | 4.7968 | 4.5789 | 6.2316 | 6.1042 | 5.96 | 5.8021 | 5.6337 | 5.4653 | 5.3021 | 5.1347 | 5.0768 | 4.8347 | 4.5537 | 4.3126 | 6.3558 | 6.2347 | 6.0979 | 5.9442 | 5.7747 | 5.6063 | 5.4421 | 5.2737 | 5.2147 | 4.9642 | 4.6768 | 4.4337
|  | NORMANDY PRIMARY | HT |  |  |  |  | 6.2337 | 6.1095 | 5.9716 | 5.8221 | 5.6653 | 5.5021 | 5.3421 | 5.1842 | 5.1137 | 4.8189 | 4.3842 | 4.2137 | 6.1695 | 6.0242 | 5.8611 | 5.6842 | 5.4989 | 5.3137 | 5.1358 | 4.9579 | 4.8832 | 4.5716 | 4.0905 | 3.9084 | 6.2968 | 6.1579 | 6.0021 | 5.8263 | 5.64 | 5.4547 | 5.2758 | 5.0979 | 5.0221 | 4.7053 | 4.2189 | 4.0347
|  | NORMANDY PRIMARY | HE |  |  |  |  | 6.3611 | 6.2768 | 6.1779 | 6.0653 | 5.9421 | 5.8211 | 5.7011 | 5.5726 | 5.5358 | 5.4011 | 5.2379 | 1.8947 | 6.3137 | 6.2116 | 6.0937 | 5.9579 | 5.8105 | 5.6642 | 5.5221 | 5.3768 | 5.3389 | 5.2 | 5.02 | 4.8579 | 6.4347 | 6.3389 | 6.2263 | 6.0979 | 5.9516 | 5.8063 | 5.6621 | 5.5168 | 5.4779 | 5.3358 | 5.1537 | 4.9895
|  | NORMANDY PRIMARY | CF |  |  |  |  | 6.4168 | 6.3842 | 6.3368 | 6.2853 | 6.2284 | 6.1705 | 6.1084 | 6.0421 | 6.02 | 5.9105 | 5.8032 | 5.7211 | 6.3768 | 6.3389 | 6.2821 | 6.22 | 6.1526 | 6.0832 | 6.0074 | 5.9253 | 5.9 | 5.7811 | 5.6558 | 5.5568 | 6.4811 | 6.4589 | 6.4053 | 6.3474 | 6.2832 | 6.2168 | 6.1453 | 6.0674 | 6.0421 | 5.9211 | 5.7947 | 5.6947
NURSLING GSP | ROWNHAMS BSP | NORTH BADDESLEY PRIMARY | MINIMUM HEADROOM | SU 38080 20568 | NO | YES | 0 | 35.6884 | 35.4842 | 34.6368 | 33.6568 | 32.6874 | 31.92 | 31.3958 | 30.9032 | 30.4389 | 28.1558 | 25.2979 | -46.3947 | 29.8832 | 28.8442 | 27.9042 | 26.8074 | 25.7347 | 24.8979 | 24.3432 | 23.8221 | 23.3284 | 20.8874 | 17.7316 | 14.7589 | 30.9179 | 30.0705 | 29.1295 | 28.0326 | 26.9526 | 26.1126 | 25.5516 | 25.0242 | 24.5242 | 22.0421 | 18.8368 | 15.8442
|  | NORTH BADDESLEY PRIMARY | EE |  |  |  |  | 36.7811 | 36.0137 | 35.3905 | 34.6505 | 33.8274 | 32.9558 | 32.3305 | 31.8105 | 31.3905 | 29.5958 | 27.2568 | 25.1737 | 30.2874 | 29.4284 | 28.7411 | 27.92 | 27.0074 | 26.0389 | 25.3611 | 24.8042 | 24.3642 | 22.4895 | 19.9347 | 17.5853 | 31.5126 | 30.6537 | 29.9663 | 29.1432 | 28.2263 | 27.2505 | 26.5653 | 26.0011 | 25.5526 | 23.6179 | 20.9968 | 18.6253
|  | NORTH BADDESLEY PRIMARY | HT |  |  |  |  | 36.4105 | 35.4842 | 34.6368 | 33.6568 | 32.6874 | 31.92 | 31.3958 | 30.9032 | 30.4389 | 28.1558 | 25.2979 | 22.6621 | 29.8832 | 28.8442 | 27.9042 | 26.8074 | 25.7347 | 24.8979 | 24.3432 | 23.8221 | 23.3284 | 20.8874 | 17.7316 | 14.7589 | 31.1084 | 30.0705 | 29.1295 | 28.0326 | 26.9526 | 26.1126 | 25.5516 | 25.0242 | 24.5242 | 22.0421 | 18.8368 | 15.8442
|  | NORTH BADDESLEY PRIMARY | HE |  |  |  |  | 37.2653 | 36.6474 | 36.1632 | 35.5558 | 34.8558 | 34.1274 | 33.6358 | 33.2758 | 33.0053 | 31.9063 | 30.2895 | -46.3947 | 30.8158 | 30.1168 | 29.5821 | 28.9032 | 28.1221 | 27.3095 | 26.7695 | 26.3832 | 26.1 | 24.9411 | 23.12 | 21.3253 | 32.0421 | 31.3432 | 30.8074 | 30.1284 | 29.3442 | 28.5263 | 27.9842 | 27.5947 | 27.3084 | 26.1232 | 24.2842 | 22.4705
|  | NORTH BADDESLEY PRIMARY | CF |  |  |  |  | 35.6884 | 35.5958 | 35.5011 | 35.4011 | 35.2926 | 35.1811 | 35.0737 | 34.9663 | 34.8579 | 34.08 | 33.0358 | 32.0326 | 31.3084 | 30.9768 | 30.7611 | 30.5253 | 30.2558 | 30.0011 | 29.74 | 29.3779 | 29 | 27.28 | 26.1053 | 24.9642 | 30.9179 | 30.7947 | 30.6842 | 30.5663 | 30.4368 | 30.3063 | 30.1789 | 30.0389 | 29.8947 | 28.4884 | 27.3042 | 26.1505
LOVEDEAN GSP | FAREHAM (MAIN) BSP | NORTH FAREHAM PRIMARY | MINIMUM HEADROOM | SU 56427 07430 | NO | YES | 0 | 16.7253 | 16.4 | 16.0526 | 15.6032 | 15.0295 | 14.4516 | 13.9221 | 13.4232 | 12.9547 | 10.3947 | 7.8011 | -13.4874 | 12.4326 | 11.82 | 11.1979 | 10.5758 | 9.9516 | 9.3253 | 8.7463 | 8.2 | 7.6842 | 4.8484 | 2.0053 | -0.55895 | 13.7368 | 13.1421 | 12.5358 | 11.9305 | 11.3189 | 10.7053 | 10.1389 | 9.6053 | 9.1011 | 6.2705 | 3.3895 | 0.81368
|  | NORTH FAREHAM PRIMARY | EE |  |  |  |  | 16.9232 | 16.6568 | 16.3747 | 16.08 | 15.7642 | 15.3768 | 14.9337 | 14.5 | 14.0884 | 12.0726 | 9.9832 | 8.2 | 12.8558 | 12.3695 | 11.8737 | 11.3726 | 10.8621 | 10.3621 | 9.8874 | 9.42 | 8.9747 | 6.7253 | 4.4337 | 2.4389 | 14.1453 | 13.6726 | 13.1905 | 12.7011 | 12.2 | 11.7084 | 11.2379 | 10.7758 | 10.3358 | 8.1284 | 5.7853 | 3.7747
|  | NORTH FAREHAM PRIMARY | HT |  |  |  |  | 16.7253 | 16.4 | 16.0526 | 15.6032 | 15.0295 | 14.4516 | 13.9221 | 13.4232 | 12.9547 | 10.3947 | 7.8011 | 5.5053 | 12.4326 | 11.82 | 11.1979 | 10.5758 | 9.9516 | 9.3253 | 8.7463 | 8.2 | 7.6842 | 4.8484 | 2.0053 | -0.55895 | 13.7368 | 13.1421 | 12.5358 | 11.9305 | 11.3189 | 10.7053 | 10.1389 | 9.6053 | 9.1011 | 6.2705 | 3.3895 | 0.81368
|  | NORTH FAREHAM PRIMARY | HE |  |  |  |  | 17.1779 | 16.9926 | 16.7874 | 16.5663 | 16.32 | 16.0863 | 15.8653 | 15.6568 | 15.4758 | 14.34 | 13.02 | -13.4874 | 13.4116 | 13.0968 | 12.7663 | 12.4211 | 12.0568 | 11.7084 | 11.3726 | 11.0547 | 10.7579 | 9.2379 | 7.6705 | 6.2589 | 14.6821 | 14.3768 | 14.0526 | 13.7158 | 13.3558 | 13.0126 | 12.6821 | 12.3674 | 12.0758 | 10.5937 | 9.0958 | 7.6747
|  | NORTH FAREHAM PRIMARY | CF |  |  |  |  | 17.3526 | 17.2547 | 17.1537 | 17.0495 | 16.9368 | 16.8221 | 16.7095 | 16.5989 | 16.4874 | 15.9874 | 15.2526 | 14.4842 | 13.7505 | 13.5632 | 13.3726 | 13.1779 | 12.9758 | 12.7716 | 12.5716 | 12.3695 | 12.1632 | 11.1789 | 10.1453 | 9.2147 | 14.9221 | 14.8189 | 14.6442 | 14.4558 | 14.2579 | 14.0589 | 13.8611 | 13.6642 | 13.4632 | 12.5032 | 11.5105 | 10.6263
LALEHAM GSP | EAST BEDFONT BSP | NORTH FELTHAM PRIMARY | MINIMUM HEADROOM | TQ 10987 74875 | NO | YES | 0 | 29.1874 | 28.7432 | 28.2453 | 27.7747 | 26.9926 | 26.2642 | 25.5568 | 24.8663 | 24.2495 | 21.8789 | 20.2158 | -11.4632 | 24.8758 | 24.3705 | 23.8021 | 23.2684 | 22.36 | 21.5158 | 20.6937 | 19.8895 | 19.1811 | 16.4884 | 14.6053 | 13.0274 | 26.4474 | 26.0432 | 25.4758 | 24.9432 | 24.0358 | 23.1926 | 22.3726 | 21.5695 | 20.8611 | 18.1726 | 16.2926 | 14.7179
|  | NORTH FELTHAM PRIMARY | EE |  |  |  |  | 29.4232 | 29.1295 | 28.7821 | 28.3516 | 27.7811 | 27.2663 | 26.7253 | 26.0095 | 25.3421 | 23.2453 | 22.0011 | 21.0042 | 25.1442 | 24.8158 | 24.4242 | 23.9326 | 23.2758 | 22.6821 | 22.0568 | 21.2211 | 20.4389 | 18.0347 | 16.6253 | 15.4926 | 26.5274 | 26.4021 | 26.0968 | 25.6063 | 24.9495 | 24.3579 | 23.7337 | 22.8979 | 22.1179 | 19.7168 | 18.3105 | 17.1789
|  | NORTH FELTHAM PRIMARY | HT |  |  |  |  | 29.1874 | 28.7432 | 28.2453 | 27.7747 | 26.9926 | 26.2642 | 25.5568 | 24.8663 | 24.2495 | 21.8789 | 20.2158 | 18.8242 | 24.8758 | 24.3705 | 23.8021 | 23.2684 | 22.36 | 21.5158 | 20.6937 | 19.8895 | 19.1811 | 16.4884 | 14.6053 | 13.0274 | 26.4474 | 26.0432 | 25.4758 | 24.9432 | 24.0358 | 23.1926 | 22.3726 | 21.5695 | 20.8611 | 18.1726 | 16.2926 | 14.7179
|  | NORTH FELTHAM PRIMARY | HE |  |  |  |  | 29.6432 | 29.4095 | 29.1189 | 28.7568 | 28.2432 | 27.7768 | 27.2495 | 26.5863 | 25.9884 | 24.2821 | 23.3337 | -11.4632 | 25.3295 | 25.1263 | 24.7979 | 24.3842 | 23.7895 | 23.2505 | 22.6368 | 21.8568 | 21.1537 | 19.1726 | 18.0895 | 17.2853 | 26.6284 | 26.5326 | 26.4253 | 26.0579 | 25.4632 | 24.9253 | 24.3126 | 23.5347 | 22.8316 | 20.8547 | 19.7716 | 18.9695
|  | NORTH FELTHAM PRIMARY | CF |  |  |  |  | 29.7937 | 29.7379 | 29.6537 | 29.5242 | 29.3863 | 29.2442 | 29.0863 | 28.8474 | 28.5663 | 26.3274 | 25.5147 | 25.0579 | 25.4095 | 25.3537 | 25.2937 | 25.2305 | 25.1116 | 24.9526 | 24.7758 | 24.5 | 24.1726 | 21.5253 | 20.5737 | 20.0379 | 26.7032 | 26.6474 | 26.5895 | 26.5305 | 26.4684 | 26.4053 | 26.3432 | 26.1726 | 25.8463 | 23.2032 | 22.2526 | 21.7179
COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY PRIMARY | MINIMUM HEADROOM | SP 48645 04403 | NO | YES | 0 | 6.8568 | 6.8179 | 6.6537 | 6.1716 | 5.6558 | 5.1495 | 4.5758 | 4.3821 | 4.1989 | 2.8421 | 1.2895 | -4.6253 | 4.4316 | 4.2526 | 4.0621 | 3.5316 | 2.9716 | 2.4232 | 1.7926 | 1.6074 | 1.4337 | 0.041053 | -1.5937 | -2.1853 | 4.5442 | 4.3642 | 4.1747 | 3.6421 | 3.0768 | 2.52 | 1.8832 | 1.6905 | 1.5074 | 0.055789 | -1.6463 | -2.2642
|  | NORTH HINKSEY PRIMARY | EE |  |  |  |  | 6.9653 | 6.8179 | 6.6632 | 6.6674 | 6.4758 | 6.2789 | 6.0884 | 5.8979 | 5.72 | 4.2968 | 2.7421 | 1.8579 | 4.54 | 4.3937 | 4.2389 | 4.0779 | 3.8926 | 3.7042 | 3.5232 | 3.3442 | 3.1779 | 1.7263 | 0.11368 | -0.83579 | 4.6526 | 4.5053 | 4.3505 | 4.1884 | 3.9968 | 3.8 | 3.6084 | 3.4179 | 3.24 | 1.7074 | 0.0010526 | -0.97895
|  | NORTH HINKSEY PRIMARY | HT |  |  |  |  | 6.8568 | 6.8432 | 6.6537 | 6.1716 | 5.6558 | 5.1495 | 4.5758 | 4.3821 | 4.1989 | 2.8421 | 1.2895 | 0.69684 | 4.4316 | 4.2526 | 4.0621 | 3.5316 | 2.9716 | 2.4232 | 1.7926 | 1.6074 | 1.4337 | 0.041053 | -1.5937 | -2.1853 | 4.5442 | 4.3642 | 4.1747 | 3.6421 | 3.0768 | 2.52 | 1.8832 | 1.6905 | 1.5074 | 0.055789 | -1.6463 | -2.2642
|  | NORTH HINKSEY PRIMARY | HE |  |  |  |  | 7.1084 | 7.0095 | 6.8989 | 6.9463 | 6.8 | 6.66 | 6.5274 | 6.3989 | 6.2863 | 5.4863 | 4.5095 | -4.6253 | 4.6832 | 4.5842 | 4.4737 | 4.3547 | 4.2137 | 4.0779 | 3.9495 | 3.8263 | 3.7189 | 2.8916 | 1.82 | 1.0895 | 4.7958 | 4.6968 | 4.5863 | 4.4674 | 4.32 | 4.18 | 4.0474 | 3.92 | 3.8063 | 2.9453 | 1.8474 | 1.0926
|  | NORTH HINKSEY PRIMARY | CF |  |  |  |  | 7.2053 | 7.1547 | 7.1011 | 7.0474 | 6.98 | 6.9137 | 6.8463 | 6.7811 | 6.7168 | 6.2684 | 5.7147 | 5.2389 | 4.78 | 4.7295 | 4.6758 | 4.6221 | 4.5568 | 4.4926 | 4.4284 | 4.3653 | 4.3032 | 3.8358 | 3.2221 | 2.6926 | 4.8926 | 4.8421 | 4.7884 | 4.7347 | 4.6674 | 4.6011 | 4.5347 | 4.4684 | 4.4042 | 3.9263 | 3.2979 | 2.7526
NORTH HYDE GSP |  | NORTH HYDE PRIMARY | MINIMUM HEADROOM | TQ 10367 79001 | NO | NO | 0 | 103.3627 | 102.9396 | 145.6463 | 142.8116 | 140.8284 | 139.0505 | 137.3484 | 135.6979 | 134.0958 | 126.22 | 121.5484 | 23.4663 | 80.1669 | 77.8985 | 118.9337 | 115.6737 | 113.4221 | 111.4116 | 109.4832 | 107.6074 | 105.7832 | 96.7884 | 91.5095 | 86.7211 | 84.7627 | 82.4933 | 123.5274 | 120.2663 | 118.0147 | 116.0042 | 114.0737 | 112.1979 | 110.3737 | 101.3758 | 96.0968 | 91.3063
|  | NORTH HYDE PRIMARY | EE |  |  |  |  | 103.6006 | 103.2491 | 146.6674 | 144.5895 | 143.0863 | 141.6042 | 140.1547 | 138.7168 | 137.3347 | 130.9211 | 127.4768 | 124.4453 | 80.8185 | 78.9069 | 120.3926 | 117.6895 | 115.9905 | 114.3137 | 112.6716 | 111.0432 | 109.4726 | 102.1295 | 98.2358 | 94.7905 | 85.4143 | 83.5017 | 124.9863 | 122.2832 | 120.5832 | 118.9063 | 117.2642 | 115.6347 | 114.0642 | 106.7189 | 102.8242 | 99.3779
|  | NORTH HYDE PRIMARY | HT |  |  |  |  | 103.3627 | 102.9396 | 145.6463 | 142.8116 | 140.8284 | 139.0505 | 137.3484 | 135.6979 | 134.0958 | 126.22 | 121.5484 | 117.3274 | 80.1669 | 77.8985 | 118.9337 | 115.6737 | 113.4221 | 111.4116 | 109.4832 | 107.6074 | 105.7832 | 96.7884 | 91.5095 | 86.7211 | 84.7627 | 82.4933 | 123.5274 | 120.2663 | 118.0147 | 116.0042 | 114.0737 | 112.1979 | 110.3737 | 101.3758 | 96.0968 | 91.3063
|  | NORTH HYDE PRIMARY | HE |  |  |  |  | 103.8785 | 103.6091 | 147.1021 | 145.7474 | 144.3979 | 143.0789 | 141.7895 | 140.5263 | 139.3168 | 133.7674 | 131.1716 | 23.4663 | 81.5006 | 79.7943 | 121.4768 | 118.9632 | 117.4337 | 115.9368 | 114.4705 | 113.0316 | 111.6495 | 105.2568 | 102.2884 | 99.7632 | 86.0954 | 84.3901 | 126.0705 | 123.5568 | 122.0274 | 120.5295 | 119.0632 | 117.6242 | 116.2421 | 109.8474 | 106.8779 | 104.3516
|  | NORTH HYDE PRIMARY | CF |  |  |  |  | 104.0943 | 103.9385 | 147.5695 | 147.4042 | 147.2316 | 147.0568 | 146.8832 | 146.7126 | 146.4211 | 142.8432 | 140.8884 | 139.4884 | 83.0733 | 82.1933 | 124.9558 | 123.7916 | 123.0432 | 122.2421 | 121.4726 | 120.6589 | 119.8011 | 115.7168 | 113.4811 | 111.8674 | 87.6691 | 86.7891 | 129.5516 | 128.3874 | 127.6379 | 126.8368 | 126.0674 | 125.2537 | 124.3947 | 120.3105 | 118.0726 | 116.4589
MINETY GSP | CIRENCESTER BSP | NORTHLEACH PRIMARY | MINIMUM HEADROOM | SP 10557 14251 | NO | YES | 0 | 12.16 | 11.9684 | 11.76 | 11.5442 | 11.3126 | 11.0811 | 10.8589 | 10.6389 | 10.4558 | 9.3611 | 8.22 | 0.91263 | 10.0474 | 9.8316 | 9.5947 | 9.3526 | 9.0926 | 8.8347 | 8.5895 | 8.3537 | 8.1568 | 6.9642 | 5.7053 | 4.6 | 10.5042 | 10.2895 | 10.0526 | 9.8095 | 9.5484 | 9.2874 | 9.04 | 8.8 | 8.6 | 7.3863 | 6.1021 | 4.9874
|  | NORTHLEACH PRIMARY | EE |  |  |  |  | 12.2832 | 12.1337 | 11.9695 | 11.8063 | 11.6242 | 11.4453 | 11.2663 | 11.0916 | 10.9432 | 10.04 | 9.0684 | 8.2663 | 10.1884 | 10.0211 | 9.8368 | 9.6537 | 9.4537 | 9.2579 | 9.0621 | 8.8716 | 8.7126 | 7.7379 | 6.6811 | 5.7747 | 10.6453 | 10.4789 | 10.2937 | 10.1116 | 9.9084 | 9.7095 | 9.5105 | 9.3137 | 9.1505 | 8.1463 | 7.0558 | 6.1389
|  | NORTHLEACH PRIMARY | HT |  |  |  |  | 12.16 | 11.9684 | 11.76 | 11.5442 | 11.3126 | 11.0811 | 10.8589 | 10.6389 | 10.4558 | 9.3611 | 8.22 | 7.2411 | 10.0474 | 9.8316 | 9.5947 | 9.3526 | 9.0926 | 8.8347 | 8.5895 | 8.3537 | 8.1568 | 6.9642 | 5.7053 | 4.6 | 10.5042 | 10.2895 | 10.0526 | 9.8095 | 9.5484 | 9.2874 | 9.04 | 8.8 | 8.6 | 7.3863 | 6.1021 | 4.9874
|  | NORTHLEACH PRIMARY | HE |  |  |  |  | 12.4463 | 12.3474 | 12.2326 | 12.1147 | 11.9779 | 11.8453 | 11.7147 | 11.5895 | 11.4916 | 10.8747 | 10.18 | 0.91263 | 10.3726 | 10.2632 | 10.1347 | 10.0032 | 9.8526 | 9.7074 | 9.5632 | 9.4242 | 9.3189 | 8.6137 | 7.8274 | 7.1095 | 10.7863 | 10.7211 | 10.5926 | 10.4611 | 10.3084 | 10.1611 | 10.0147 | 9.8758 | 9.7663 | 9.0495 | 8.2537 | 7.5263
|  | NORTHLEACH PRIMARY | CF |  |  |  |  | 12.5411 | 12.4884 | 12.4305 | 12.3747 | 12.3116 | 12.2453 | 12.1789 | 12.1105 | 12.0516 | 11.6505 | 11.24 | 10.8589 | 10.4789 | 10.4189 | 10.3547 | 10.2916 | 10.2211 | 10.1484 | 10.0737 | 9.9989 | 9.9337 | 9.4705 | 8.9789 | 8.5453 | 10.8442 | 10.8137 | 10.7821 | 10.7484 | 10.6779 | 10.6032 | 10.5295 | 10.4526 | 10.3874 | 9.9189 | 9.4232 | 8.9842
IVER 66KV GSP |  | NORTHOLT PRIMARY | MINIMUM HEADROOM | TQ 11550 83230 | NO | NO | 0.56105 | 84.6533 | 84.0449 | 83.3975 | 82.7196 | 82.0144 | 81.3007 | 80.6565 | 79.9744 | 78.8881 | 73.8312 | 68.8175 | 21.5249 | 75.7744 | 74.4281 | 72.9617 | 71.4333 | 69.8565 | 68.4017 | 67.0617 | 65.8217 | 64.6396 | 59.0881 | 53.5007 | 48.1544 | 77.5112 | 76.8607 | 75.4449 | 73.9186 | 72.3428 | 70.8902 | 69.5512 | 68.3123 | 67.1312 | 61.587 | 56.0059 | 50.667
|  | NORTHOLT PRIMARY | EE |  |  |  |  | 85.0102 | 84.5081 | 83.9744 | 83.407 | 82.8154 | 82.2386 | 81.6817 | 81.1428 | 80.6575 | 78.0986 | 74.5523 | 71.2617 | 76.587 | 75.6102 | 74.5123 | 73.3712 | 72.2059 | 71.0817 | 69.9986 | 68.9533 | 67.9838 | 63.8344 | 59.8902 | 56.1902 | 77.8975 | 77.3649 | 76.7986 | 75.8544 | 74.6891 | 73.5659 | 72.4849 | 71.4396 | 70.4712 | 66.3259 | 62.387 | 58.6923
|  | NORTHOLT PRIMARY | HT |  |  |  |  | 84.6533 | 84.0449 | 83.3975 | 82.7196 | 82.0144 | 81.3007 | 80.6565 | 79.9744 | 78.8881 | 73.8312 | 68.8175 | 64.0586 | 75.7744 | 74.4281 | 72.9617 | 71.4333 | 69.8565 | 68.4017 | 67.0617 | 65.8217 | 64.6396 | 59.0881 | 53.5007 | 48.1544 | 77.5112 | 76.8607 | 75.4449 | 73.9186 | 72.3428 | 70.8902 | 69.5512 | 68.3123 | 67.1312 | 61.587 | 56.0059 | 50.667
|  | NORTHOLT PRIMARY | HE |  |  |  |  | 85.3859 | 84.9902 | 84.5533 | 84.0828 | 83.5807 | 83.1007 | 82.6491 | 82.2281 | 81.8638 | 80.6049 | 79.7902 | 21.5249 | 77.1112 | 76.6438 | 76.0238 | 75.147 | 74.2207 | 73.3491 | 72.5249 | 71.7512 | 71.0554 | 68.2996 | 65.7323 | 63.407 | 78.3059 | 77.8912 | 77.4323 | 76.9375 | 76.4112 | 75.8312 | 75.0081 | 74.2354 | 73.5396 | 70.7859 | 68.2228 | 65.9007
|  | NORTHOLT PRIMARY | CF |  |  |  |  | 85.6786 | 85.4449 | 85.2017 | 84.9512 | 84.6912 | 84.4259 | 84.1649 | 83.907 | 83.6491 | 82.5007 | 81.9175 | 81.5923 | 77.4354 | 77.1744 | 76.8965 | 76.5712 | 76.1923 | 75.6838 | 75.1754 | 74.6712 | 74.1628 | 71.7165 | 69.9228 | 68.3502 | 78.6133 | 78.367 | 78.1102 | 77.8459 | 77.5712 | 77.2923 | 77.0165 | 76.7449 | 76.4723 | 74.2007 | 72.4091 | 70.8396
BRAMLEY (BASI) GSP | READING BSP | NORTHUMBERLAND AVENUE PRIMARY | MINIMUM HEADROOM | SU 72207 71092 | NO | YES | 0.31579 | 25.7863 | 25.6063 | 25.4179 | 25.2189 | 24.8379 | 24.2674 | 22.8758 | 21.9674 | 21.0758 | 16.2958 | 13.8263 | -1.6505 | 21.7421 | 21.4337 | 21.1137 | 20.7842 | 19.9137 | 19.0379 | 17.3989 | 16.3547 | 15.3263 | 9.7821 | 6.7853 | 5.34 | 22.4726 | 22.2958 | 22.1084 | 21.9116 | 21.34 | 20.4495 | 18.8432 | 17.8 | 16.7726 | 11.2379 | 8.2116 | 6.7684
|  | NORTHUMBERLAND AVENUE PRIMARY | EE |  |  |  |  | 25.8863 | 25.7358 | 25.5768 | 25.4074 | 25.2063 | 24.8421 | 23.8705 | 22.7379 | 21.8463 | 17.5758 | 15.7147 | 14.7253 | 21.8747 | 21.6937 | 21.4316 | 21.1579 | 20.5305 | 19.8895 | 18.5295 | 17.2168 | 16.1863 | 11.3695 | 9.2337 | 8.1095 | 22.5705 | 22.4221 | 22.2653 | 22.0979 | 21.9032 | 21.32 | 19.9547 | 18.66 | 17.6316 | 12.8726 | 10.7358 | 9.6126
|  | NORTHUMBERLAND AVENUE PRIMARY | HT |  |  |  |  | 25.7863 | 25.6063 | 25.4179 | 25.2189 | 24.8379 | 24.2674 | 22.8758 | 21.9674 | 21.0758 | 16.2958 | 13.8263 | 12.5495 | 21.7421 | 21.4337 | 21.1137 | 20.7842 | 19.9137 | 19.0379 | 17.3989 | 16.3547 | 15.3263 | 9.7821 | 6.7853 | 5.34 | 22.4726 | 22.2958 | 22.1084 | 21.9116 | 21.34 | 20.4495 | 18.8432 | 17.8 | 16.7726 | 11.2379 | 8.2116 | 6.7684
|  | NORTHUMBERLAND AVENUE PRIMARY | HE |  |  |  |  | 26.0232 | 25.9126 | 25.7916 | 25.6611 | 25.4937 | 25.3211 | 24.4621 | 23.4232 | 22.6168 | 17.9916 | 16.48 | -1.6505 | 22.0179 | 21.9074 | 21.7811 | 21.6474 | 21.0947 | 20.5179 | 19.1684 | 17.9611 | 17.0242 | 11.4568 | 9.7042 | 8.92 | 22.7053 | 22.5958 | 22.4758 | 22.3474 | 22.1863 | 21.9284 | 20.5821 | 19.4042 | 18.4695 | 12.8768 | 11.1274 | 10.3442
|  | NORTHUMBERLAND AVENUE PRIMARY | CF |  |  |  |  | 26.12 | 26.0611 | 25.9968 | 25.9316 | 25.8663 | 25.7968 | 25.7242 | 25.6421 | 25.5547 | 23.2158 | 20.9116 | 20.4589 | 22.1137 | 22.0558 | 21.9926 | 21.9253 | 21.8568 | 21.7842 | 21.6526 | 21.3389 | 20.9821 | 17.6874 | 14.9884 | 14.4674 | 22.8011 | 22.7421 | 22.68 | 22.6158 | 22.5505 | 22.4821 | 22.4105 | 22.3326 | 22.2505 | 19.1316 | 16.4379 | 15.9168
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD PRIMARY | MINIMUM HEADROOM | SU 68329 86784 | YES | YES | 0 | 8.7716 | 8.7053 | 8.6347 | 8.5611 | 8.4863 | 8.4105 | 8.3453 | 8.2863 | 8.2316 | 7.8453 | 7.4811 | -12.78 | 7.6442 | 7.5168 | 7.3895 | 7.2589 | 7.1316 | 6.9989 | 6.8779 | 6.7653 | 6.6579 | 6.2116 | 5.8116 | 5.4232 | 7.8295 | 7.7063 | 7.5821 | 7.4568 | 7.3326 | 7.2042 | 7.0874 | 6.9779 | 6.8758 | 6.4453 | 6.0632 | 5.6937
|  | NUFFIELD PRIMARY | EE |  |  |  |  | 8.8147 | 8.76 | 8.7032 | 8.6432 | 8.5821 | 8.5232 | 8.4684 | 8.4137 | 8.3663 | 8.1853 | 7.9179 | 7.6779 | 7.7263 | 7.6316 | 7.5295 | 7.4253 | 7.3221 | 7.2168 | 7.1168 | 7.0179 | 6.9274 | 6.58 | 6.2853 | 6.0168 | 7.9011 | 7.8168 | 7.7179 | 7.6158 | 7.5158 | 7.4147 | 7.3168 | 7.2221 | 7.1347 | 6.8 | 6.5189 | 6.2642
|  | NUFFIELD PRIMARY | HT |  |  |  |  | 8.7716 | 8.7053 | 8.6347 | 8.5611 | 8.4863 | 8.4105 | 8.3453 | 8.2863 | 8.2316 | 7.8453 | 7.4811 | 7.1326 | 7.6442 | 7.5168 | 7.3895 | 7.2589 | 7.1316 | 6.9989 | 6.8779 | 6.7653 | 6.6579 | 6.2116 | 5.8116 | 5.4232 | 7.8295 | 7.7063 | 7.5821 | 7.4568 | 7.3326 | 7.2042 | 7.0874 | 6.9779 | 6.8758 | 6.4453 | 6.0632 | 5.6937
|  | NUFFIELD PRIMARY | HE |  |  |  |  | 8.8695 | 8.8326 | 8.7905 | 8.7474 | 8.7 | 8.6558 | 8.6137 | 8.5747 | 8.54 | 8.4263 | 8.3621 | -12.78 | 7.7863 | 7.7474 | 7.7032 | 7.6463 | 7.5716 | 7.4958 | 7.4232 | 7.3547 | 7.2916 | 7.0737 | 6.9 | 6.74 | 7.9589 | 7.9211 | 7.8779 | 7.8284 | 7.7558 | 7.6832 | 7.6116 | 7.5463 | 7.4853 | 7.2747 | 7.1084 | 6.9579
|  | NUFFIELD PRIMARY | CF |  |  |  |  | 8.9063 | 8.8874 | 8.8684 | 8.8484 | 8.8284 | 8.8074 | 8.7863 | 8.7653 | 8.7453 | 8.6547 | 8.6095 | 8.5853 | 7.8242 | 7.8042 | 7.7842 | 7.7632 | 7.7421 | 7.7179 | 7.6758 | 7.6316 | 7.5895 | 7.4053 | 7.2663 | 7.1463 | 7.9958 | 7.9768 | 7.9579 | 7.9368 | 7.9158 | 7.8937 | 7.8589 | 7.8168 | 7.7758 | 7.5979 | 7.4674 | 7.3537
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | OAKRIDGE PRIMARY | MINIMUM HEADROOM | SU 63496 53664 | NO | YES | 0 | 32.5947 | 32.3547 | 32.3053 | 31.9211 | 31.4189 | 30.2579 | 29.1358 | 28.0589 | 27.5684 | 25.8189 | 23.9821 | 4.9716 | 29.7958 | 29.1747 | 28.6821 | 28.1968 | 27.6579 | 26.3421 | 25.0695 | 23.8453 | 23.3074 | 21.4242 | 19.4053 | 17.0432 | 30.4474 | 29.8137 | 29.2979 | 28.8126 | 28.2716 | 26.9579 | 25.6842 | 24.46 | 23.9211 | 22.0274 | 19.9937 | 17.6284
|  | OAKRIDGE PRIMARY | EE |  |  |  |  | 32.7232 | 32.52 | 32.3053 | 32.0779 | 31.8358 | 31.6011 | 30.7937 | 29.7105 | 28.5821 | 26.9684 | 25.6947 | 24.0737 | 30.0916 | 29.5568 | 29.1368 | 28.7421 | 28.2863 | 27.8926 | 26.9579 | 25.7242 | 24.4368 | 22.6926 | 21.3179 | 19.4863 | 30.6695 | 30.2032 | 29.7758 | 29.3758 | 28.9137 | 28.5158 | 27.5684 | 26.3347 | 25.0463 | 23.2842 | 21.8884 | 20.0526
|  | OAKRIDGE PRIMARY | HT |  |  |  |  | 32.5947 | 32.3547 | 32.3737 | 31.9211 | 31.4189 | 30.2579 | 29.1358 | 28.0589 | 27.5684 | 25.8189 | 23.9821 | 21.8842 | 29.7958 | 29.1747 | 28.6821 | 28.1968 | 27.6579 | 26.3421 | 25.0695 | 23.8453 | 23.3074 | 21.4242 | 19.4053 | 17.0432 | 30.4474 | 29.8137 | 29.2979 | 28.8126 | 28.2716 | 26.9579 | 25.6842 | 24.46 | 23.9211 | 22.0274 | 19.9937 | 17.6284
|  | OAKRIDGE PRIMARY | HE |  |  |  |  | 32.8895 | 32.7368 | 32.5674 | 32.3853 | 32.1874 | 31.9979 | 31.82 | 31.2147 | 30.5389 | 28.7284 | 28.1011 | 4.9716 | 30.4642 | 30.0695 | 29.7611 | 29.4758 | 29.1263 | 28.8368 | 28.1884 | 27.4021 | 26.6337 | 24.6032 | 23.9263 | 22.8863 | 30.8495 | 30.6811 | 30.4116 | 30.1242 | 29.7684 | 29.4747 | 28.8137 | 28.0147 | 27.2463 | 25.2105 | 24.5274 | 23.4842
|  | OAKRIDGE PRIMARY | CF |  |  |  |  | 33.0095 | 32.9211 | 32.8295 | 32.7347 | 32.6347 | 32.5326 | 32.4337 | 32.3337 | 32.2358 | 30.7242 | 30.1368 | 29.6305 | 30.62 | 30.5179 | 30.4147 | 30.2695 | 29.9716 | 29.6958 | 29.4863 | 29.2621 | 29.0179 | 26.8011 | 26.1547 | 25.5853 | 30.9832 | 30.8884 | 30.7916 | 30.6916 | 30.5789 | 30.3442 | 30.1316 | 29.9032 | 29.6547 | 27.4137 | 26.7653 | 26.1926
COWLEY GSP | HEADINGTON BSP | OLD ROAD PRIMARY | MINIMUM HEADROOM | SP 55274 06426 | NO | YES | 0.063158 | 40.1221 | 39.9326 | 39.7316 | 39.5232 | 39.3021 | 38.1768 | 37.8274 | 37.5179 | 37.2326 | 35.7568 | 34.6368 | 5.6958 | 31.8295 | 31.4747 | 31.1063 | 30.74 | 30.3737 | 28.6516 | 28.2621 | 27.9179 | 27.6074 | 26.0074 | 24.8042 | 23.7284 | 33.5463 | 33.1979 | 32.8347 | 32.4737 | 32.1105 | 30.4411 | 30.0579 | 29.7179 | 29.4095 | 27.8316 | 26.6368 | 25.5789
|  | OLD ROAD PRIMARY | EE |  |  |  |  | 40.2305 | 40.0716 | 39.9053 | 39.7284 | 39.5411 | 38.8716 | 38.3242 | 37.9442 | 37.7011 | 36.4853 | 35.6095 | 34.8874 | 32.6042 | 31.9326 | 31.4295 | 30.9884 | 30.6158 | 29.4705 | 28.8211 | 28.3874 | 28.1211 | 26.8074 | 25.8779 | 25.0916 | 34.28 | 33.64 | 33.1495 | 32.7147 | 32.3484 | 31.2347 | 30.5989 | 30.1716 | 29.9074 | 28.6 | 27.6663 | 26.8884
|  | OLD ROAD PRIMARY | HT |  |  |  |  | 40.1221 | 39.9326 | 39.7316 | 39.5232 | 39.3021 | 38.1768 | 37.8274 | 37.5179 | 37.2326 | 35.7568 | 34.6368 | 33.6537 | 31.8295 | 31.4747 | 31.1063 | 30.74 | 30.3737 | 28.6516 | 28.2621 | 27.9179 | 27.6074 | 26.0074 | 24.8042 | 23.7284 | 33.5463 | 33.1979 | 32.8347 | 32.4737 | 32.1105 | 30.4411 | 30.0579 | 29.7179 | 29.4095 | 27.8316 | 26.6368 | 25.5789
|  | OLD ROAD PRIMARY | HE |  |  |  |  | 40.3674 | 40.2516 | 40.1242 | 39.9863 | 39.8347 | 39.5389 | 39.0621 | 38.7874 | 38.6221 | 37.8537 | 37.4189 | 5.6958 | 32.9053 | 32.3221 | 31.92 | 31.5821 | 31.3042 | 30.2221 | 29.6495 | 29.3347 | 29.1547 | 28.2884 | 27.8053 | 27.4032 | 34.5053 | 34.0274 | 33.6347 | 33.3042 | 33.0305 | 31.9811 | 31.4242 | 31.1147 | 30.9368 | 30.0821 | 29.6021 | 29.2053
|  | OLD ROAD PRIMARY | CF |  |  |  |  | 40.4642 | 40.4 | 40.3326 | 40.2642 | 40.1905 | 40.1147 | 40.0411 | 39.9674 | 39.8968 | 39.1705 | 38.7916 | 38.5084 | 33.2179 | 33.1505 | 33.0779 | 32.9547 | 32.8305 | 32.6968 | 32.4779 | 32.0916 | 31.6789 | 29.7874 | 29.3526 | 29.0242 | 34.6221 | 34.5547 | 34.4832 | 34.4116 | 34.3358 | 34.2568 | 34.1474 | 33.7937 | 33.3926 | 31.5558 | 31.1284 | 30.8042
COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD PRIMARY | MINIMUM HEADROOM | SP 50148 05901 | NO | YES | 0 | 35.6832 | 35.5779 | 35.4642 | 35.3442 | 35.2211 | 35.1 | 34.9832 | 34.8716 | 34.0295 | 32.8958 | 32.0011 | -23.82 | 28.5768 | 28.4716 | 28.3579 | 28.2379 | 28.1147 | 27.9937 | 27.8768 | 27.7653 | 26.8495 | 25.5968 | 24.6053 | 23.6895 | 30.2495 | 30.1442 | 30.0305 | 29.9105 | 29.7874 | 29.6663 | 29.5495 | 29.4379 | 28.4789 | 27.2253 | 26.2337 | 25.3179
|  | OXFORD PRIMARY | EE |  |  |  |  | 35.6832 | 35.5779 | 35.4642 | 35.3442 | 35.2211 | 35.1 | 34.9832 | 34.8716 | 34.7705 | 33.6368 | 32.9653 | 32.3653 | 28.5768 | 28.4716 | 28.3579 | 28.2379 | 28.1147 | 27.9937 | 27.8768 | 27.7653 | 27.6642 | 26.4147 | 25.6705 | 24.9979 | 30.2495 | 30.1442 | 30.0305 | 29.9105 | 29.7874 | 29.6663 | 29.5495 | 29.4379 | 29.3368 | 28.0442 | 27.2989 | 26.6263
|  | OXFORD PRIMARY | HT |  |  |  |  | 36.9189 | 36.7926 | 37.4558 | 37.2221 | 37.1947 | 36.3558 | 35.8568 | 34.8916 | 34.0295 | 32.8958 | 32.0011 | 31.1821 | 31.1116 | 30.8979 | 30.7284 | 30.4779 | 30.4926 | 29.5284 | 28.9642 | 27.8474 | 26.8495 | 25.5968 | 24.6053 | 23.6895 | 32.3874 | 32.2611 | 32.4011 | 32.1505 | 32.1221 | 31.1589 | 30.5947 | 29.4768 | 28.4789 | 27.2253 | 26.2337 | 25.3179
|  | OXFORD PRIMARY | HE |  |  |  |  | 35.7684 | 35.6874 | 35.5968 | 35.4989 | 35.3958 | 35.2968 | 35.2042 | 35.1158 | 35.04 | 34.6242 | 34.2411 | -23.82 | 28.6621 | 28.5811 | 28.4905 | 28.3926 | 28.3853 | 28.2863 | 28.1937 | 28.1053 | 28.0305 | 27.5126 | 27.0874 | 26.7274 | 30.3347 | 30.2537 | 30.1632 | 30.0653 | 29.9621 | 29.8632 | 29.7705 | 29.6821 | 29.6063 | 29.14 | 28.7158 | 28.3558
|  | OXFORD PRIMARY | CF |  |  |  |  | 37.1337 | 37.0842 | 37.0337 | 36.9821 | 36.9274 | 36.8716 | 36.8168 | 36.7632 | 36.7084 | 35.9768 | 36.0263 | 35.7853 | 31.5905 | 31.5411 | 31.4905 | 31.4389 | 31.3842 | 31.3284 | 31.2737 | 31.1242 | 30.9147 | 29.0168 | 29.1179 | 28.8453 | 32.6021 | 32.5526 | 32.5021 | 32.4505 | 32.3958 | 32.34 | 32.2853 | 32.2316 | 32.1768 | 30.6895 | 30.7474 | 30.4747
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | OXFORD SCIENCE PARK PRIMARY | MINIMUM HEADROOM | TBC | NO | YES | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | OXFORD SCIENCE PARK PRIMARY | EE |  |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | OXFORD SCIENCE PARK PRIMARY | HT |  |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | OXFORD SCIENCE PARK PRIMARY | HE |  |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | OXFORD SCIENCE PARK PRIMARY | CF |  |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | OVERTON PRIMARY | MINIMUM HEADROOM | SU 52061 50913 | NO | YES | 0 | 29.92 | 29.7116 | 29.5 | 29.2021 | 28.7358 | 26.1379 | 23.66 | 21.3411 | 19.0326 | 9.1389 | 5.3853 | 4.6526 | 29.4084 | 29.1842 | 28.9568 | 28.6305 | 28.1084 | 25.0768 | 22.1821 | 19.4758 | 16.78 | 5.2316 | 0.90526 | 0.1 | 29.4968 | 29.2768 | 29.0516 | 28.7305 | 28.2168 | 25.1926 | 22.3042 | 19.6021 | 16.9105 | 5.3747 | 1.0326 | 0.22105
|  | OVERTON PRIMARY | EE |  |  |  |  | 30.0589 | 29.8926 | 29.7221 | 29.4632 | 29.0337 | 28.6063 | 26.8358 | 24.5474 | 22.1695 | 11.4505 | 6.08 | 5.5211 | 29.5558 | 29.3811 | 29.2 | 28.9137 | 28.4316 | 27.9537 | 25.8916 | 23.22 | 20.4421 | 7.9242 | 1.6958 | 1.0821 | 29.6463 | 29.4705 | 29.2905 | 29.0095 | 28.5358 | 28.0611 | 26.0011 | 23.3337 | 20.5589 | 8.0453 | 1.7989 | 1.1768
|  | OVERTON PRIMARY | HT |  |  |  |  | 29.92 | 29.7116 | 29.5 | 29.2021 | 28.7358 | 26.1379 | 23.66 | 21.3411 | 19.0326 | 9.1389 | 5.3853 | 4.6526 | 29.4084 | 29.1842 | 28.9568 | 28.6305 | 28.1084 | 25.0768 | 22.1821 | 19.4758 | 16.78 | 5.2316 | 0.90526 | 0.1 | 29.4968 | 29.2768 | 29.0516 | 28.7305 | 28.2168 | 25.1926 | 22.3042 | 19.6021 | 16.9105 | 5.3747 | 1.0326 | 0.22105
|  | OVERTON PRIMARY | HE |  |  |  |  | 30.2463 | 30.1368 | 30.0232 | 29.8189 | 29.44 | 29.0674 | 27.5221 | 25.6589 | 23.8053 | 15.6842 | 8.9463 | 11.2642 | 29.7484 | 29.6368 | 29.5211 | 29.3 | 28.8726 | 28.4516 | 26.6484 | 24.4684 | 22.3 | 12.7926 | 4.8947 | 2.6621 | 29.8474 | 29.7316 | 29.6126 | 29.3905 | 28.9705 | 28.5579 | 26.7611 | 24.5863 | 22.4211 | 12.9305 | 5.0453 | 2.8095
|  | OVERTON PRIMARY | CF |  |  |  |  | 30.4611 | 30.3779 | 30.2905 | 30.1842 | 30.0253 | 29.8221 | 29.5832 | 29.3632 | 29.0779 | 25.1768 | 18.8568 | 15.8726 | 29.9695 | 29.8863 | 29.7958 | 29.6853 | 29.52 | 29.2905 | 29.0168 | 28.7663 | 28.4379 | 23.8832 | 16.4621 | 12.9653 | 30.0832 | 29.9947 | 29.8989 | 29.7832 | 29.6074 | 29.3811 | 29.1147 | 28.8695 | 28.5484 | 24 | 16.5979 | 13.1032
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PADWORTH PRIMARY | MINIMUM HEADROOM | SU 62243 66052 | YES | YES | 0 | 8.2979 | 8.2674 | 8.2347 | 8.1474 | 7.8747 | 7.6126 | 7.2768 | 7.2368 | 7.1958 | 6.6305 | 5.7179 | 3.0632 | 7.7063 | 7.6737 | 7.64 | 7.5505 | 7.2168 | 6.8958 | 6.4874 | 6.4505 | 6.4137 | 5.8105 | 4.8032 | 4.5674 | 7.6884 | 7.6579 | 7.6263 | 7.4737 | 7.1368 | 6.8137 | 6.4021 | 6.3611 | 6.3211 | 5.6916 | 4.6537 | 4.4053
|  | PADWORTH PRIMARY | EE |  |  |  |  | 8.3158 | 8.2905 | 8.2642 | 8.2368 | 8.1979 | 8.1579 | 8.1168 | 8.0747 | 8.0337 | 7.4789 | 6.7568 | 6.2042 | 7.7263 | 7.6989 | 7.6705 | 7.6432 | 7.6053 | 7.5684 | 7.5316 | 7.4937 | 7.4589 | 6.8653 | 6.0558 | 5.4284 | 7.7063 | 7.6811 | 7.6547 | 7.6274 | 7.5895 | 7.5495 | 7.5021 | 7.4421 | 7.3842 | 6.7326 | 5.8747 | 5.2421
|  | PADWORTH PRIMARY | HT |  |  |  |  | 8.2979 | 8.2674 | 8.2347 | 8.1474 | 7.8747 | 7.6126 | 7.2768 | 7.2368 | 7.1958 | 6.6305 | 5.7179 | 5.4916 | 7.7063 | 7.6737 | 7.64 | 7.5505 | 7.2168 | 6.8958 | 6.4874 | 6.4505 | 6.4137 | 5.8105 | 4.8032 | 4.5674 | 7.6884 | 7.6579 | 7.6263 | 7.4737 | 7.1368 | 6.8137 | 6.4021 | 6.3611 | 6.3211 | 5.6916 | 4.6537 | 4.4053
|  | PADWORTH PRIMARY | HE |  |  |  |  | 8.34 | 8.3232 | 8.3042 | 8.2842 | 8.2537 | 8.2274 | 8.2 | 8.1747 | 8.1505 | 7.9263 | 7.4632 | 3.0632 | 7.7526 | 7.7347 | 7.7147 | 7.6937 | 7.6653 | 7.64 | 7.6147 | 7.5905 | 7.5695 | 7.34 | 6.7568 | 6.24 | 7.7305 | 7.7137 | 7.6947 | 7.6747 | 7.6453 | 7.6179 | 7.5916 | 7.5663 | 7.5432 | 7.2379 | 6.6421 | 6.1137
|  | PADWORTH PRIMARY | CF |  |  |  |  | 8.3558 | 8.3463 | 8.3379 | 8.3284 | 8.3126 | 8.3011 | 8.2874 | 8.2737 | 8.2611 | 8.2 | 7.9011 | 7.5884 | 7.7695 | 7.7589 | 7.7505 | 7.74 | 7.7253 | 7.7137 | 7.7 | 7.6863 | 7.6758 | 7.6137 | 7.2653 | 6.8832 | 7.7463 | 7.7368 | 7.7284 | 7.7189 | 7.7042 | 7.6926 | 7.6779 | 7.6642 | 7.6526 | 7.5926 | 7.1726 | 6.7832
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PANGBOURNE PRIMARY | MINIMUM HEADROOM | SU 62960 76144 | NO | YES | 0 | 26.3455 | 26.2024 | 26.0213 | 25.7687 | 25.5192 | 25.2697 | 25.0445 | 24.835 | 24.6403 | 23.7866 | 22.9508 | 9.7466 | 24.0013 | 23.7897 | 23.5455 | 23.2655 | 22.9908 | 22.7171 | 22.4687 | 22.2361 | 22.0192 | 21.0571 | 20.0824 | 19.1224 | 24.5571 | 24.3971 | 24.1224 | 23.8434 | 23.5687 | 23.295 | 23.0466 | 22.8139 | 22.5982 | 21.6361 | 20.6634 | 19.7045
|  | PANGBOURNE PRIMARY | EE |  |  |  |  | 26.4361 | 26.3192 | 26.195 | 26.0655 | 25.8824 | 25.6855 | 25.4982 | 25.3171 | 25.1539 | 24.5034 | 23.8897 | 23.3266 | 24.1455 | 23.9761 | 23.8013 | 23.6213 | 23.4003 | 23.1834 | 22.9771 | 22.7782 | 22.5971 | 21.8666 | 21.1476 | 20.475 | 24.6529 | 24.5308 | 24.4003 | 24.2013 | 23.9771 | 23.7603 | 23.555 | 23.3561 | 23.175 | 22.4455 | 21.7276 | 21.055
|  | PANGBOURNE PRIMARY | HT |  |  |  |  | 26.3455 | 26.2024 | 26.0213 | 25.7687 | 25.5192 | 25.2697 | 25.0445 | 24.835 | 24.6403 | 23.7866 | 22.9508 | 22.1434 | 24.0013 | 23.7897 | 23.5455 | 23.2655 | 22.9908 | 22.7171 | 22.4687 | 22.2361 | 22.0192 | 21.0571 | 20.0824 | 19.1224 | 24.5571 | 24.3971 | 24.1224 | 23.8434 | 23.5687 | 23.295 | 23.0466 | 22.8139 | 22.5982 | 21.6361 | 20.6634 | 19.7045
|  | PANGBOURNE PRIMARY | HE |  |  |  |  | 26.5518 | 26.4697 | 26.3813 | 26.2845 | 26.1834 | 26.0845 | 25.9918 | 25.9066 | 25.8329 | 25.4413 | 25.0539 | 9.7466 | 24.3329 | 24.2213 | 24.1024 | 23.975 | 23.8424 | 23.7139 | 23.5929 | 23.4813 | 23.3792 | 22.9329 | 22.4761 | 22.0487 | 24.7761 | 24.6908 | 24.5992 | 24.4992 | 24.395 | 24.2929 | 24.1971 | 24.0782 | 23.9561 | 23.5108 | 23.0539 | 22.6276
|  | PANGBOURNE PRIMARY | CF |  |  |  |  | 26.6276 | 26.5855 | 26.5424 | 26.4971 | 26.4508 | 26.4045 | 26.3561 | 26.3108 | 26.2645 | 26.0392 | 25.755 | 25.4939 | 24.4392 | 24.3761 | 24.3108 | 24.2424 | 24.1729 | 24.1034 | 24.0318 | 23.9655 | 23.8971 | 23.5655 | 23.2287 | 22.9097 | 24.8561 | 24.8108 | 24.7655 | 24.7182 | 24.6687 | 24.6203 | 24.5697 | 24.5213 | 24.4729 | 24.1424 | 23.8066 | 23.4876
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE PRIMARY | MINIMUM HEADROOM | SU 51369 08259 | NO | YES | 0 | 33.8179 | 33.7095 | 33.6021 | 33.4916 | 43.1832 | 42.8147 | 42.4916 | 42.1989 | 41.9284 | 40.8179 | 38.3 | 5.3211 | 30.5505 | 30.3074 | 30.1189 | 29.9347 | 43.2926 | 42.9242 | 42.4337 | 41.9147 | 41.4284 | 38.7316 | 35.9811 | 33.4042 | 31.1189 | 31.0126 | 30.8958 | 30.7074 | 42.5063 | 42.1368 | 41.6242 | 41.0989 | 40.6042 | 37.8547 | 35.0389 | 32.4474
|  | PARK GATE PRIMARY | EE |  |  |  |  | 44.7758 | 44.5105 | 44.2295 | 43.9358 | 43.6316 | 43.3389 | 43.0632 | 42.7958 | 42.5579 | 41.6947 | 40.5758 | 38.8126 | 44.8842 | 44.6189 | 44.3379 | 44.0453 | 43.7411 | 43.4495 | 43.1737 | 42.9084 | 42.6432 | 40.5695 | 38.4242 | 36.4779 | 44.0979 | 43.8326 | 43.5516 | 43.2579 | 42.9547 | 42.6611 | 42.3853 | 42.1189 | 41.8379 | 39.7211 | 37.5232 | 35.5263
|  | PARK GATE PRIMARY | HT |  |  |  |  | 44.5768 | 44.2516 | 43.9063 | 43.5505 | 43.1832 | 42.8147 | 42.4916 | 42.1989 | 41.9284 | 40.8179 | 38.3 | 35.9979 | 44.6853 | 44.36 | 44.0147 | 43.6589 | 43.2926 | 42.9242 | 42.4337 | 41.9147 | 41.4284 | 38.7316 | 35.9811 | 33.4042 | 43.8989 | 43.5737 | 43.2284 | 42.8726 | 42.5063 | 42.1368 | 41.6242 | 41.0989 | 40.6042 | 37.8547 | 35.0389 | 32.4474
|  | PARK GATE PRIMARY | HE |  |  |  |  | 45.0326 | 44.8484 | 44.6442 | 44.4242 | 44.1895 | 43.9642 | 43.7526 | 43.5547 | 43.3832 | 42.8074 | 42.4737 | 5.3211 | 45.1411 | 44.9568 | 44.7526 | 44.5326 | 44.2989 | 44.0737 | 43.8621 | 43.6653 | 43.4937 | 42.9221 | 41.4 | 40.0116 | 44.3547 | 44.1705 | 43.9663 | 43.7463 | 43.5116 | 43.2863 | 43.0747 | 42.8768 | 42.7053 | 42.1305 | 40.5547 | 39.1284
|  | PARK GATE PRIMARY | CF |  |  |  |  | 33.8179 | 33.7095 | 33.6021 | 33.4916 | 44.7968 | 44.6874 | 44.5789 | 44.4726 | 44.3663 | 43.8884 | 43.6505 | 43.5189 | 30.5505 | 30.3074 | 30.1189 | 29.9347 | 44.9063 | 44.7968 | 44.6884 | 44.5821 | 44.4758 | 44 | 43.7632 | 42.9063 | 31.1189 | 31.0126 | 30.8958 | 30.7074 | 44.1189 | 44.0095 | 43.9021 | 43.7958 | 43.6884 | 43.2116 | 42.9737 | 42.0779
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PARK HOUSE PRIMARY | MINIMUM HEADROOM | SU 23138 43780 | NO | YES | 0 | 4.5053 | 4.4368 | 4.3632 | 3.9779 | 3.3979 | 2.8263 | 2.1095 | 2.0211 | 1.9305 | 0.51158 | -1.4726 | -1.9684 | 3.8611 | 3.7884 | 3.7105 | 3.2653 | 2.6074 | 1.9611 | 1.1432 | 1.0684 | 0.99263 | -0.49368 | -2.6253 | -3.1211 | 4.0042 | 3.9305 | 3.8526 | 3.4074 | 2.7411 | 2.0853 | 1.2568 | 1.1684 | 1.0779 | -0.50105 | -2.7411 | -3.28
|  | PARK HOUSE PRIMARY | EE |  |  |  |  | 4.5526 | 4.4947 | 4.4326 | 4.3726 | 4.2768 | 4.1653 | 4.0505 | 3.9295 | 3.8063 | 2.3211 | 0.16211 | -1.0095 | 3.9126 | 3.8526 | 3.7884 | 3.7253 | 3.6368 | 3.5368 | 3.4347 | 3.3305 | 3.2242 | 1.7211 | -0.54737 | -1.8368 | 4.0558 | 3.9947 | 3.9284 | 3.8642 | 3.7663 | 3.6516 | 3.5326 | 3.4084 | 3.2832 | 1.6463 | -0.77368 | -2.1074
|  | PARK HOUSE PRIMARY | HT |  |  |  |  | 4.5053 | 4.4368 | 4.3632 | 3.9779 | 3.3979 | 2.8263 | 2.1095 | 2.0211 | 1.9305 | 0.51158 | -1.4726 | -1.9684 | 3.8611 | 3.7884 | 3.7105 | 3.2653 | 2.6074 | 1.9611 | 1.1432 | 1.0684 | 0.99263 | -0.49368 | -2.6253 | -3.1211 | 4.0042 | 3.9305 | 3.8526 | 3.4074 | 2.7411 | 2.0853 | 1.2568 | 1.1684 | 1.0779 | -0.50105 | -2.7411 | -3.28
|  | PARK HOUSE PRIMARY | HE |  |  |  |  | 4.6126 | 4.5789 | 4.54 | 4.5011 | 4.4305 | 4.3642 | 4.2979 | 4.2326 | 4.1695 | 3.4032 | 2 | 0.91579 | 3.9789 | 3.9432 | 3.9 | 3.8611 | 3.7968 | 3.7358 | 3.6758 | 3.6179 | 3.56 | 2.7642 | 1.1926 | 0.10842 | 4.1221 | 4.0863 | 4.0442 | 4.0032 | 3.9305 | 3.8632 | 3.7958 | 3.7284 | 3.6632 | 2.8116 | 1.2011 | 0.077895
|  | PARK HOUSE PRIMARY | CF |  |  |  |  | 4.6484 | 4.6284 | 4.6053 | 4.5811 | 4.5368 | 4.4958 | 4.4611 | 4.4253 | 4.3926 | 4.1084 | 3.3347 | 2.6137 | 4.0158 | 3.9947 | 3.9695 | 3.9432 | 3.9 | 3.8621 | 3.8284 | 3.7937 | 3.7653 | 3.4705 | 2.6053 | 1.8021 | 4.1589 | 4.1379 | 4.1126 | 4.0863 | 4.0411 | 3.9968 | 3.96 | 3.9221 | 3.8895 | 3.5779 | 2.6895 | 1.8621
MINETY GSP | STRATTON (MAIN) BSP | PARK NORTH PRIMARY | MINIMUM HEADROOM | SU 18052 84542 | NO | YES | 0 | 34.3579 | 34.0295 | 33.62 | 33.1242 | 32.4011 | 31.1705 | 30.0021 | 28.8789 | 27.7958 | 22.2642 | 17.7789 | -8.5147 | 29.7368 | 29.04 | 28.3484 | 27.5779 | 26.7947 | 25.4253 | 24.1189 | 22.8589 | 21.6421 | 15.3695 | 10.2705 | 5.7505 | 30.9074 | 30.2389 | 29.6211 | 28.8779 | 28.12 | 26.82 | 25.5589 | 24.3021 | 23.0863 | 16.8232 | 11.7316 | 7.2179
|  | PARK NORTH PRIMARY | EE |  |  |  |  | 34.3579 | 34.0389 | 33.6989 | 33.3432 | 32.9432 | 32.0642 | 31.1389 | 30.0642 | 29.02 | 24.0211 | 20.3295 | 17.6337 | 29.7368 | 29.04 | 28.4263 | 27.7968 | 27.1516 | 26.1632 | 25.1337 | 23.9274 | 22.7505 | 17.0579 | 12.8432 | 9.9789 | 30.9074 | 30.2389 | 29.6463 | 29.0368 | 28.4126 | 27.4716 | 26.4937 | 25.3253 | 24.1505 | 18.4674 | 14.2579 | 11.4421
|  | PARK NORTH PRIMARY | HT |  |  |  |  | 34.4147 | 34.0295 | 33.62 | 33.1242 | 32.4011 | 31.1705 | 30.0021 | 28.8789 | 27.7958 | 22.2642 | 17.7789 | 13.8158 | 29.9611 | 29.1126 | 28.3484 | 27.5779 | 26.7947 | 25.4253 | 24.1189 | 22.8589 | 21.6421 | 15.3695 | 10.2705 | 5.7505 | 31.1726 | 30.3589 | 29.6211 | 28.8779 | 28.12 | 26.82 | 25.5589 | 24.3021 | 23.0863 | 16.8232 | 11.7316 | 7.2179
|  | PARK NORTH PRIMARY | HE |  |  |  |  | 34.6432 | 34.4095 | 34.1505 | 33.8737 | 33.5768 | 33.2937 | 32.68 | 31.7463 | 30.8621 | 26.6358 | 23.6737 | -8.5147 | 30.3884 | 29.8916 | 29.4674 | 29.0211 | 28.5432 | 27.7116 | 26.8147 | 25.76 | 24.7579 | 19.9137 | 16.5042 | 13.6716 | 31.5326 | 31.0547 | 30.6432 | 30.2095 | 29.7453 | 28.9547 | 28.1053 | 27.1105 | 26.1558 | 21.3189 | 17.9147 | 15.0874
|  | PARK NORTH PRIMARY | CF |  |  |  |  | 34.8463 | 34.7189 | 34.5863 | 34.4505 | 34.3084 | 34.1642 | 34.0221 | 33.8821 | 33.7411 | 31.5232 | 28.8189 | 27.2958 | 30.8179 | 30.5589 | 30.3095 | 30.0558 | 29.7937 | 29.5295 | 29.2284 | 28.8979 | 28.5358 | 25.4379 | 22.3105 | 20.5505 | 31.8663 | 31.6947 | 31.4547 | 31.2095 | 30.9568 | 30.7011 | 30.4126 | 30.0958 | 29.7505 | 26.8358 | 23.7137 | 21.9558
WILLESDEN GSP | ACTON LANE BSP | PARK ROYAL PRIMARY | MINIMUM HEADROOM | TQ 20137 82215 | NO | NO | 0 | 13.62 | 13.2453 | 41.2632 | 40.6726 | 39.9674 | 39.3032 | 38.6389 | 37.9811 | 37.3232 | 36.6453 | 36.5316 | 21.8421 | 11.7337 | 11.2947 | 39.2284 | 38.5347 | 37.7063 | 36.9242 | 36.1432 | 35.3695 | 34.5958 | 33.8253 | 33.6979 | 33.5642 | 12.3063 | 11.8821 | 39.8358 | 39.1663 | 38.3674 | 37.6126 | 36.84 | 36.0663 | 35.2926 | 34.5326 | 34.4063 | 34.2716
|  | PARK ROYAL PRIMARY | EE |  |  |  |  | 13.6484 | 13.3042 | 41.3737 | 40.8547 | 40.2526 | 39.6516 | 39.0484 | 38.4526 | 37.8579 | 37.2074 | 37.18 | 37.0968 | 11.7663 | 11.3632 | 39.3568 | 38.7474 | 38.0389 | 37.3316 | 36.6232 | 35.9221 | 35.2221 | 34.4621 | 34.4558 | 34.3611 | 12.3368 | 11.9484 | 39.9589 | 39.3716 | 38.6884 | 38.0063 | 37.3211 | 36.62 | 35.92 | 35.1589 | 35.1642 | 35.0695
|  | PARK ROYAL PRIMARY | HT |  |  |  |  | 13.62 | 13.2453 | 41.2632 | 40.6726 | 39.9674 | 39.3032 | 38.6389 | 37.9811 | 37.3232 | 36.6453 | 36.5316 | 36.4137 | 11.7337 | 11.2947 | 39.2284 | 38.5347 | 37.7063 | 36.9242 | 36.1432 | 35.3695 | 34.5958 | 33.8253 | 33.6979 | 33.5642 | 12.3063 | 11.8821 | 39.8358 | 39.1663 | 38.3674 | 37.6126 | 36.84 | 36.0663 | 35.2926 | 34.5326 | 34.4063 | 34.2716
|  | PARK ROYAL PRIMARY | HE |  |  |  |  | 13.6589 | 13.3284 | 41.4021 | 40.8895 | 40.2905 | 39.6937 | 39.0979 | 38.5063 | 37.9168 | 37.2947 | 37.2368 | 21.8421 | 11.7863 | 11.3895 | 39.3884 | 38.7853 | 38.0811 | 37.3789 | 36.6779 | 35.9821 | 35.2874 | 34.5589 | 34.4937 | 34.4295 | 12.3568 | 11.9737 | 39.9905 | 39.4095 | 38.7295 | 38.0526 | 37.3758 | 36.6789 | 35.9853 | 35.2558 | 35.1905 | 35.1263
|  | PARK ROYAL PRIMARY | CF |  |  |  |  | 13.6653 | 13.66 | 42.1537 | 42.1484 | 42.1421 | 41.8337 | 41.3611 | 40.8474 | 40.2916 | 39.1705 | 39.1337 | 39.1032 | 12.1484 | 12.1316 | 40.6158 | 40.5211 | 40.2874 | 39.8979 | 39.3421 | 38.7368 | 38.0821 | 36.7642 | 36.7242 | 36.6884 | 12.5263 | 12.5211 | 41.0147 | 41.0095 | 40.8579 | 40.4821 | 39.9453 | 39.3632 | 38.7305 | 37.46 | 37.4211 | 37.3863
MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE NORTH PRIMARY | MINIMUM HEADROOM | SZ 03222 92233 | NO | YES | 0 | 35.839 | 35.2779 | 34.68 | 34.0643 | 33.1611 | 32.1053 | 31.0895 | 30.0474 | 29.0253 | 24.4443 | 20.3243 | -18.0357 | 29.7369 | 28.3558 | 26.5621 | 25.2558 | 23.7874 | 22.6295 | 21.5032 | 20.3506 | 19.2443 | 14.2295 | 9.6337 | 5.399 | 31.2327 | 29.8874 | 28.1316 | 26.8032 | 25.3085 | 24.1337 | 22.9895 | 21.8169 | 20.6895 | 15.6443 | 11.0548 | 6.8264
|  | PARKSTONE NORTH PRIMARY | EE |  |  |  |  | 36.1779 | 35.719 | 35.2306 | 34.72 | 34.1906 | 33.6811 | 32.8821 | 32.1021 | 31.2969 | 27.7821 | 24.6064 | 21.7432 | 30.4579 | 29.3369 | 27.9716 | 26.6779 | 25.3316 | 24.3937 | 23.4969 | 22.64 | 21.739 | 17.8906 | 14.3411 | 11.1053 | 31.7979 | 30.8443 | 29.5179 | 28.2485 | 26.8769 | 25.9253 | 25.0158 | 24.1464 | 23.2295 | 19.3064 | 15.7569 | 12.5253
|  | PARKSTONE NORTH PRIMARY | HT |  |  |  |  | 35.839 | 35.2779 | 34.68 | 34.0643 | 33.1611 | 32.1053 | 31.0895 | 30.0474 | 29.0253 | 24.4443 | 20.3243 | 16.5537 | 29.7369 | 28.3558 | 26.5621 | 25.2558 | 23.7874 | 22.6295 | 21.5032 | 20.3506 | 19.2443 | 14.2295 | 9.6337 | 5.399 | 31.2327 | 29.8874 | 28.1316 | 26.8032 | 25.3085 | 24.1337 | 22.9895 | 21.8169 | 20.6895 | 15.6443 | 11.0548 | 6.8264
|  | PARKSTONE NORTH PRIMARY | HE |  |  |  |  | 36.6021 | 36.2727 | 35.9085 | 35.5169 | 35.099 | 34.699 | 34.3221 | 33.9706 | 33.6664 | 31.5506 | 29.4116 | -18.0357 | 31.3927 | 30.5569 | 29.4537 | 28.4264 | 27.3285 | 26.6358 | 25.9916 | 25.3643 | 24.6853 | 21.9748 | 19.5737 | 17.4032 | 32.2527 | 31.8927 | 30.9643 | 29.9643 | 28.8969 | 28.2064 | 27.5537 | 26.9179 | 26.2264 | 23.4632 | 21.0043 | 18.8158
|  | PARKSTONE NORTH PRIMARY | CF |  |  |  |  | 36.9 | 36.7253 | 36.5421 | 36.3527 | 36.1579 | 35.9579 | 35.7621 | 35.5674 | 35.3737 | 34.5074 | 33.9379 | 32.7253 | 31.7664 | 31.5021 | 31.0653 | 30.6274 | 30.0906 | 29.6611 | 29.1979 | 28.7221 | 28.2611 | 26.279 | 24.5948 | 23.1443 | 32.5653 | 32.3748 | 32.1769 | 31.9716 | 31.5843 | 31.1643 | 30.7127 | 30.2495 | 29.8 | 27.8443 | 26.12 | 24.6316
MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE SOUTH PRIMARY | MINIMUM HEADROOM | SZ 04762 89848 | NO | YES | 0 | 32.9863 | 32.6705 | 32.3305 | 31.8168 | 31.2989 | 30.7463 | 30.2158 | 29.6811 | 29.1737 | 26.8832 | 24.8137 | 7.9411 | 29.7653 | 29.0316 | 28.4842 | 27.9358 | 27.3842 | 26.7905 | 26.2179 | 25.6358 | 25.0811 | 22.5621 | 20.2611 | 18.1358 | 30.3116 | 29.5747 | 29.0284 | 28.48 | 27.9284 | 27.3358 | 26.7632 | 26.1811 | 25.6274 | 23.1105 | 20.8105 | 18.6884
|  | PARKSTONE SOUTH PRIMARY | EE |  |  |  |  | 33.1674 | 32.9147 | 32.6484 | 32.3737 | 32.0126 | 31.5737 | 31.1495 | 30.7421 | 30.3211 | 28.5347 | 26.9474 | 25.5242 | 30.1147 | 29.6011 | 29.1042 | 28.6221 | 28.1568 | 27.6863 | 27.2326 | 26.7958 | 26.3368 | 24.3779 | 22.6084 | 21.0053 | 30.6758 | 30.1442 | 29.6474 | 29.1653 | 28.7011 | 28.2305 | 27.7758 | 27.34 | 26.8832 | 24.9232 | 23.1547 | 21.5526
|  | PARKSTONE SOUTH PRIMARY | HT |  |  |  |  | 32.9863 | 32.6705 | 32.3305 | 31.8168 | 31.2989 | 30.7463 | 30.2158 | 29.6811 | 29.1737 | 26.8832 | 24.8137 | 22.9168 | 29.7653 | 29.0316 | 28.4842 | 27.9358 | 27.3842 | 26.7905 | 26.2179 | 25.6358 | 25.0811 | 22.5621 | 20.2611 | 18.1358 | 30.3116 | 29.5747 | 29.0284 | 28.48 | 27.9284 | 27.3358 | 26.7632 | 26.1811 | 25.6274 | 23.1105 | 20.8105 | 18.6884
|  | PARKSTONE SOUTH PRIMARY | HE |  |  |  |  | 33.3832 | 33.2042 | 33.0032 | 32.7905 | 32.5642 | 32.3453 | 32.14 | 31.9474 | 31.6937 | 30.4589 | 29.3979 | 7.9411 | 30.4042 | 30.1621 | 29.8474 | 29.5063 | 29.1716 | 28.8211 | 28.4926 | 28.1768 | 27.8379 | 26.48 | 25.2884 | 24.2411 | 31.0063 | 30.7537 | 30.3958 | 30.0495 | 29.7147 | 29.3642 | 29.0368 | 28.7189 | 28.3811 | 27.0242 | 25.8337 | 24.7884
|  | PARKSTONE SOUTH PRIMARY | CF |  |  |  |  | 33.5221 | 33.4253 | 33.3253 | 33.22 | 33.1042 | 32.9874 | 32.8684 | 32.7516 | 32.6347 | 31.9547 | 31.1737 | 30.5232 | 30.5726 | 30.4505 | 30.3242 | 30.1947 | 30.0558 | 29.8505 | 29.6095 | 29.3653 | 29.1211 | 28.0821 | 27.2063 | 26.4632 | 31.1453 | 31.0484 | 30.9453 | 30.8347 | 30.6274 | 30.3989 | 30.1537 | 29.9074 | 29.6642 | 28.6263 | 27.7505 | 27.0095
FLEET-BRAMLEY GSP | WOKINGHAM BSP | PEACOCK FARM PRIMARY | MINIMUM HEADROOM | SU 84770 68709 | NO | YES | 0.053684 | 16.4711 | 16.3806 | 16.2501 | 16.0722 | 15.8711 | 15.6858 | 15.5132 | 15.3553 | 15.2132 | 14.5543 | 13.8048 | 2.6932 | 14.5743 | 14.2806 | 14.0774 | 13.8722 | 13.6395 | 13.4258 | 13.2258 | 13.0437 | 12.8795 | 12.1027 | 11.2795 | 10.5101 | 15.2385 | 14.9374 | 14.729 | 14.5206 | 14.2827 | 14.0658 | 13.8616 | 13.6764 | 13.5079 | 12.7143 | 11.8701 | 11.0785
|  | PEACOCK FARM PRIMARY | EE |  |  |  |  | 16.5216 | 16.4469 | 16.3669 | 16.2711 | 16.1058 | 15.9543 | 15.8111 | 15.6848 | 15.569 | 15.0879 | 14.5858 | 14.0774 | 14.6879 | 14.4395 | 14.2764 | 14.1048 | 13.9153 | 13.7395 | 13.5753 | 13.4332 | 13.3016 | 12.7416 | 12.1279 | 11.5669 | 15.3532 | 15.0985 | 14.9322 | 14.7585 | 14.5648 | 14.3858 | 14.2195 | 14.0743 | 13.9406 | 13.369 | 12.7395 | 12.1616
|  | PEACOCK FARM PRIMARY | HT |  |  |  |  | 16.4711 | 16.3806 | 16.2501 | 16.0722 | 15.8711 | 15.6858 | 15.5132 | 15.3553 | 15.2132 | 14.5543 | 13.8048 | 13.0995 | 14.5743 | 14.2806 | 14.0774 | 13.8722 | 13.6395 | 13.4258 | 13.2258 | 13.0437 | 12.8795 | 12.1027 | 11.2795 | 10.5101 | 15.2385 | 14.9374 | 14.729 | 14.5206 | 14.2827 | 14.0658 | 13.8616 | 13.6764 | 13.5079 | 12.7143 | 11.8701 | 11.0785
|  | PEACOCK FARM PRIMARY | HE |  |  |  |  | 16.5932 | 16.5395 | 16.4806 | 16.4174 | 16.3501 | 16.2774 | 16.1669 | 16.0764 | 15.9932 | 15.6648 | 15.3069 | 2.6932 | 14.8153 | 14.6416 | 14.5227 | 14.4016 | 14.2501 | 14.1132 | 13.9869 | 13.8848 | 13.7911 | 13.409 | 12.9637 | 12.5669 | 15.4837 | 15.3048 | 15.1837 | 15.0606 | 14.9069 | 14.7669 | 14.6385 | 14.5343 | 14.4385 | 14.049 | 13.5922 | 13.1816
|  | PEACOCK FARM PRIMARY | CF |  |  |  |  | 16.6406 | 16.6111 | 16.5806 | 16.5501 | 16.5174 | 16.4848 | 16.4532 | 16.4206 | 16.3879 | 16.2416 | 16.0279 | 15.8511 | 14.8627 | 14.8332 | 14.8027 | 14.7616 | 14.6743 | 14.5848 | 14.5058 | 14.4364 | 14.3722 | 14.0785 | 13.8174 | 13.5943 | 15.5311 | 15.5016 | 15.4711 | 15.429 | 15.3406 | 15.2479 | 15.1669 | 15.0964 | 15.0311 | 14.7322 | 14.4648 | 14.2353
WILLESDEN GSP |  | PERIVALE PRIMARY | MINIMUM HEADROOM | TQ 17544 82947 | NO | NO | 0.19263 | 82.5724 | 82.3671 | 82.1492 | 81.9218 | 81.685 | 81.4471 | 81.2345 | 81.0397 | 80.8597 | 80.1113 | 79.0039 | 24.6292 | 77.6892 | 77.265 | 76.8113 | 76.3482 | 75.8787 | 75.4334 | 75.0218 | 74.6461 | 74.2882 | 72.6218 | 70.8776 | 69.2145 | 78.9945 | 78.7755 | 78.5418 | 78.0903 | 77.605 | 77.165 | 76.7545 | 76.3787 | 76.0208 | 74.3566 | 72.6145 | 70.9534
|  | PERIVALE PRIMARY | EE |  |  |  |  | 82.6808 | 82.5071 | 82.3229 | 82.1282 | 81.925 | 81.7271 | 81.5376 | 81.3545 | 81.1892 | 80.5755 | 80.145 | 79.7008 | 77.9439 | 77.6229 | 77.2745 | 76.9197 | 76.5682 | 76.2292 | 75.9082 | 75.6008 | 75.3103 | 74.0482 | 72.8239 | 71.6808 | 79.1124 | 78.9292 | 78.7345 | 78.5292 | 78.3166 | 77.9766 | 77.6471 | 77.3313 | 77.0366 | 75.7808 | 74.5587 | 73.4166
|  | PERIVALE PRIMARY | HT |  |  |  |  | 82.5724 | 82.3671 | 82.1492 | 81.9218 | 81.685 | 81.4471 | 81.2345 | 81.0397 | 80.8597 | 80.1113 | 79.0039 | 77.5913 | 77.6892 | 77.265 | 76.8113 | 76.3482 | 75.8787 | 75.4334 | 75.0218 | 74.6461 | 74.2882 | 72.6218 | 70.8776 | 69.2145 | 78.9945 | 78.7755 | 78.5418 | 78.0903 | 77.605 | 77.165 | 76.7545 | 76.3787 | 76.0208 | 74.3566 | 72.6145 | 70.9534
|  | PERIVALE PRIMARY | HE |  |  |  |  | 82.8187 | 82.685 | 82.5376 | 82.3787 | 82.2092 | 82.0482 | 81.8955 | 81.7534 | 81.6303 | 81.2092 | 80.9534 | 24.6292 | 78.1197 | 77.9818 | 77.7787 | 77.5124 | 77.2366 | 76.9829 | 76.745 | 76.5261 | 76.3282 | 75.5734 | 74.8313 | 74.1408 | 79.2618 | 79.1218 | 78.9682 | 78.8018 | 78.6261 | 78.4587 | 78.3008 | 78.1534 | 78.0261 | 77.3113 | 76.5629 | 75.8734
|  | PERIVALE PRIMARY | CF |  |  |  |  | 82.9176 | 82.8387 | 82.7566 | 82.6724 | 82.585 | 82.4955 | 82.4082 | 82.3218 | 82.2345 | 81.8482 | 81.6534 | 81.545 | 78.2229 | 78.1397 | 78.0545 | 77.9639 | 77.8334 | 77.6766 | 77.5239 | 77.3734 | 77.2218 | 76.4987 | 75.9913 | 75.5471 | 79.3661 | 79.2829 | 79.1966 | 79.1071 | 79.0155 | 78.9218 | 78.8303 | 78.7397 | 78.6482 | 78.2408 | 77.7271 | 77.2776
FLEET-BRAMLEY GSP | FERNHURST BSP | PETERSFIELD PRIMARY | MINIMUM HEADROOM | SU 74173 23420 | NO | YES | 0.15474 | 36.4772 | 36.093 | 35.6856 | 35.2656 | 34.7404 | 33.9877 | 33.3319 | 32.6488 | 31.9341 | 28.3972 | 25.1098 | -6.2649 | 30.0783 | 29.3909 | 28.6572 | 27.7688 | 26.8677 | 26.0572 | 25.3519 | 24.6067 | 23.8204 | 19.8751 | 16.1656 | 12.7414 | 31.2962 | 30.5646 | 29.8025 | 28.9151 | 28.0151 | 27.2046 | 26.5014 | 25.7562 | 24.9709 | 21.0309 | 17.3267 | 13.9067
|  | PETERSFIELD PRIMARY | EE |  |  |  |  | 36.7056 | 36.3909 | 36.0551 | 35.7067 | 35.3446 | 34.9972 | 34.6656 | 34.1951 | 33.6046 | 30.8077 | 28.2151 | 25.8562 | 30.5404 | 29.993 | 29.4298 | 28.7698 | 28.0677 | 27.4583 | 26.9119 | 26.3109 | 25.6646 | 22.5456 | 19.6056 | 16.9098 | 31.6941 | 31.2119 | 30.6151 | 29.9151 | 29.213 | 28.6046 | 28.0593 | 27.4583 | 26.813 | 23.6983 | 20.7625 | 18.0709
|  | PETERSFIELD PRIMARY | HT |  |  |  |  | 36.4772 | 36.093 | 35.6856 | 35.2656 | 34.7404 | 33.9877 | 33.3319 | 32.6488 | 31.9341 | 28.3972 | 25.1098 | 22.0951 | 30.0783 | 29.3909 | 28.6572 | 27.7688 | 26.8677 | 26.0572 | 25.3519 | 24.6067 | 23.8204 | 19.8751 | 16.1656 | 12.7414 | 31.2962 | 30.5646 | 29.8025 | 28.9151 | 28.0151 | 27.2046 | 26.5014 | 25.7562 | 24.9709 | 21.0309 | 17.3267 | 13.9067
|  | PETERSFIELD PRIMARY | HE |  |  |  |  | 37.0004 | 36.7772 | 36.5288 | 36.2614 | 35.9783 | 35.7056 | 35.4498 | 35.9393 | 35.5014 | 33.4235 | 31.5035 | -6.2649 | 31.1393 | 30.7919 | 30.4098 | 29.9225 | 29.4235 | 29.0025 | 28.6383 | 28.2162 | 27.7362 | 25.4067 | 23.2088 | 21.2151 | 31.9898 | 31.7667 | 31.5183 | 31.1498 | 30.6193 | 30.1762 | 29.7962 | 29.3625 | 28.8814 | 26.5551 | 24.3614 | 22.3709
|  | PETERSFIELD PRIMARY | CF |  |  |  |  | 37.2025 | 37.0835 | 36.9583 | 36.8298 | 36.6972 | 36.5614 | 36.4277 | 36.2951 | 36.1625 | 35.5741 | 34.6825 | 33.5709 | 31.3498 | 31.2246 | 31.0362 | 30.8109 | 30.5772 | 30.3404 | 30.1088 | 29.8793 | 29.6446 | 28.1814 | 26.7172 | 25.4319 | 32.1919 | 32.073 | 31.9477 | 31.8193 | 31.6867 | 31.5456 | 31.3383 | 31.0951 | 30.8456 | 29.3277 | 27.8656 | 26.5825
IVER 132KV GSP | CHALVEY BSP | PETERSFIELD AVENUE PRIMARY | MINIMUM HEADROOM | SU 98108 80286 | NO | NO | 0.058947 | 58.2272 | 57.9135 | 55.7387 | 53.2187 | 51.2261 | 49.9377 | 49.3787 | 48.8419 | 48.3314 | 45.9135 | 43.8303 | 13.6629 | 50.0293 | 48.0472 | 45.5251 | 42.5977 | 40.2945 | 38.8261 | 38.2124 | 37.6219 | 37.0598 | 34.3693 | 32.0366 | 29.8766 | 51.6145 | 49.6072 | 47.0893 | 44.1661 | 41.8672 | 40.4008 | 39.7882 | 39.1987 | 38.6366 | 35.9493 | 33.6198 | 31.4629
|  | PETERSFIELD AVENUE PRIMARY | EE |  |  |  |  | 58.3693 | 58.1566 | 56.2135 | 53.7777 | 51.8672 | 50.6703 | 50.2019 | 49.7366 | 49.3029 | 47.3451 | 45.7208 | 44.2608 | 50.3503 | 48.4714 | 46.044 | 43.2082 | 40.9956 | 39.624 | 39.1124 | 38.6029 | 38.1272 | 35.9493 | 34.124 | 32.4703 | 51.9377 | 50.0303 | 47.6072 | 44.7766 | 42.5672 | 41.1987 | 40.6872 | 40.1787 | 39.7029 | 37.5282 | 35.7051 | 34.0535
|  | PETERSFIELD AVENUE PRIMARY | HT |  |  |  |  | 58.2272 | 57.9135 | 55.7387 | 53.2187 | 51.2261 | 49.9377 | 49.3787 | 48.8419 | 48.3314 | 45.9135 | 43.8303 | 41.9145 | 50.0293 | 48.0472 | 45.5251 | 42.5977 | 40.2945 | 38.8261 | 38.2124 | 37.6219 | 37.0598 | 34.3693 | 32.0366 | 29.8766 | 51.6145 | 49.6072 | 47.0893 | 44.1661 | 41.8672 | 40.4008 | 39.7882 | 39.1987 | 38.6366 | 35.9493 | 33.6198 | 31.4629
|  | PETERSFIELD AVENUE PRIMARY | HE |  |  |  |  | 58.5419 | 58.3787 | 56.8145 | 54.4861 | 52.6735 | 51.5756 | 51.2082 | 50.8461 | 50.5177 | 49.084 | 47.9661 | 13.6629 | 50.764 | 49.0082 | 46.7072 | 43.9882 | 41.8829 | 40.6208 | 40.2208 | 39.824 | 39.4629 | 37.8608 | 36.5966 | 35.4935 | 52.3556 | 50.5735 | 48.2693 | 45.5556 | 43.4545 | 42.1945 | 41.7945 | 41.3977 | 41.0377 | 39.4377 | 38.1756 | 37.0735
|  | PETERSFIELD AVENUE PRIMARY | CF |  |  |  |  | 58.6703 | 58.5766 | 58.4787 | 58.3777 | 58.2745 | 56.3966 | 55.6314 | 55.4229 | 55.2187 | 54.1145 | 53.3156 | 52.6482 | 52.4745 | 52.2377 | 51.6703 | 50.6777 | 48.7514 | 46.2177 | 45.3324 | 45.104 | 44.8808 | 43.6598 | 42.7577 | 41.9914 | 53.5661 | 53.4429 | 53.3082 | 52.2714 | 50.3135 | 47.7808 | 46.8966 | 46.6693 | 46.4472 | 45.2272 | 44.3261 | 43.5608
MANNINGTON GSP | SALISBURY BSP | PETERSFINGER PRIMARY | MINIMUM HEADROOM | SU 15608 29334 | NO | YES | 0 | 26.2898 | 26.0182 | 25.7308 | 25.275 | 24.5424 | 23.8108 | 23.1224 | 22.5571 | 22.0592 | 19.3308 | 16.575 | 0.62135 | 22.4519 | 21.9382 | 21.2519 | 20.5266 | 19.7392 | 18.955 | 18.215 | 17.6192 | 17.1024 | 14.2582 | 11.3329 | 8.5708 | 23.8256 | 23.3677 | 22.7203 | 21.9961 | 21.1961 | 20.3992 | 19.6456 | 19.034 | 18.5003 | 15.5329 | 12.4919 | 9.6803
|  | PETERSFINGER PRIMARY | EE |  |  |  |  | 26.4519 | 26.2287 | 25.9908 | 25.9961 | 25.4003 | 24.8003 | 24.1698 | 23.3792 | 22.954 | 20.6813 | 18.214 | 16.1929 | 22.8445 | 22.4035 | 21.8845 | 21.3235 | 20.6866 | 20.0519 | 19.3835 | 18.5287 | 18.1024 | 15.8182 | 13.3035 | 11.0824 | 24.0035 | 23.7687 | 23.3192 | 22.7887 | 22.1413 | 21.4887 | 20.8013 | 19.9266 | 19.4761 | 17.0329 | 14.3371 | 12.0624
|  | PETERSFINGER PRIMARY | HT |  |  |  |  | 26.2898 | 26.0182 | 25.7308 | 25.275 | 24.5424 | 23.8108 | 23.1224 | 22.5571 | 22.0592 | 19.3308 | 16.575 | 14.075 | 22.4519 | 21.9382 | 21.2519 | 20.5266 | 19.7392 | 18.955 | 18.215 | 17.6192 | 17.1024 | 14.2582 | 11.3329 | 8.5708 | 23.8256 | 23.3677 | 22.7203 | 21.9961 | 21.1961 | 20.3992 | 19.6456 | 19.034 | 18.5003 | 15.5329 | 12.4919 | 9.6803
|  | PETERSFINGER PRIMARY | HE |  |  |  |  | 26.6603 | 26.5056 | 26.335 | 26.8024 | 26.3213 | 25.8561 | 25.355 | 24.7371 | 24.4824 | 23.0666 | 21.5571 | 0.62135 | 23.3045 | 23.0108 | 22.6298 | 22.195 | 21.6803 | 21.1813 | 20.6371 | 19.9571 | 19.6971 | 18.2256 | 16.5845 | 14.8729 | 24.2256 | 24.0635 | 23.8803 | 23.6635 | 23.1392 | 22.6329 | 22.0803 | 21.3908 | 21.1213 | 19.5845 | 17.894 | 16.1382
|  | PETERSFINGER PRIMARY | CF |  |  |  |  | 26.8035 | 26.7224 | 26.6382 | 26.5498 | 26.4445 | 26.3382 | 26.2308 | 26.1277 | 26.0256 | 25.094 | 24.2203 | 23.2403 | 23.5687 | 23.4835 | 23.3561 | 23.1919 | 22.9919 | 22.7803 | 22.5466 | 22.2192 | 21.875 | 20.335 | 19.3908 | 18.3077 | 24.3824 | 24.2971 | 24.2087 | 24.115 | 24.0066 | 23.894 | 23.7813 | 23.5919 | 23.3024 | 21.7645 | 20.7908 | 19.6792
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PEWSEY PRIMARY | MINIMUM HEADROOM | SU 14710 59252 | NO | YES | 0 | 15.5232 | 15.2505 | 14.9726 | 14.6905 | 14.3495 | 13.9621 | 13.6021 | 13.3579 | 13.0968 | 11.7326 | 10.3442 | 1.6337 | 13.7189 | 13.4253 | 13.1295 | 12.9 | 12.5358 | 12.1158 | 11.7242 | 11.4695 | 11.1916 | 9.7232 | 8.2116 | 6.7674 | 14.12 | 13.8274 | 13.5295 | 13.2284 | 12.86 | 12.4379 | 12.0442 | 11.7853 | 11.5021 | 10.0084 | 8.4653 | 7.0095
|  | PEWSEY PRIMARY | EE |  |  |  |  | 15.7084 | 15.4895 | 15.2663 | 15.0368 | 14.7621 | 14.4611 | 14.1326 | 13.8632 | 13.6621 | 12.5768 | 11.4337 | 10.4105 | 13.92 | 13.6853 | 13.4474 | 13.2042 | 12.9095 | 12.5874 | 12.2326 | 11.9474 | 11.74 | 10.5979 | 9.3726 | 8.2284 | 14.3211 | 14.0874 | 13.8484 | 13.6042 | 13.3084 | 12.9821 | 12.6232 | 12.3326 | 12.12 | 10.9411 | 9.6747 | 8.5158
|  | PEWSEY PRIMARY | HT |  |  |  |  | 15.5232 | 15.2505 | 14.9726 | 14.6905 | 14.3495 | 13.9621 | 13.6021 | 13.3579 | 13.0968 | 11.7326 | 10.3442 | 9.0526 | 13.7189 | 13.4253 | 13.1295 | 12.9 | 12.5358 | 12.1158 | 11.7242 | 11.4695 | 11.1916 | 9.7232 | 8.2116 | 6.7674 | 14.12 | 13.8274 | 13.5295 | 13.2284 | 12.86 | 12.4379 | 12.0442 | 11.7853 | 11.5021 | 10.0084 | 8.4653 | 7.0095
|  | PEWSEY PRIMARY | HE |  |  |  |  | 15.9547 | 15.8147 | 15.6663 | 15.5074 | 15.2989 | 15.0684 | 14.8 | 14.6168 | 14.4863 | 13.7768 | 13.0158 | 1.6337 | 14.1863 | 14.0389 | 13.8821 | 13.7137 | 13.4916 | 13.2432 | 12.9505 | 12.7547 | 12.6189 | 11.8589 | 11.0137 | 10.1484 | 14.5853 | 14.44 | 14.2842 | 14.1158 | 13.8916 | 13.6411 | 13.3453 | 13.1474 | 13.0105 | 12.2358 | 11.3768 | 10.5011
|  | PEWSEY PRIMARY | CF |  |  |  |  | 16.0958 | 16.0147 | 15.9305 | 15.8463 | 15.7453 | 15.6368 | 15.5326 | 15.4232 | 15.3095 | 14.7989 | 14.3579 | 13.8621 | 14.3347 | 14.2484 | 14.16 | 14.0705 | 13.9621 | 13.8453 | 13.7347 | 13.6147 | 13.4926 | 12.94 | 12.4537 | 11.8926 | 14.7305 | 14.6463 | 14.5589 | 14.4716 | 14.3632 | 14.2453 | 14.1326 | 14.0126 | 13.8895 | 13.3316 | 12.8389 | 12.2716
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE PRIMARY | MINIMUM HEADROOM | SY 70169 99809 | NO | YES | 0 | 6.5358 | 6.4547 | 3.7484 | 3.6853 | 3.6179 | 3.5516 | 3.4863 | 3.4253 | 3.3663 | 2.0695 | 1.3095 | 1.2326 | 6.2642 | 6.1789 | 3.9842 | 3.9189 | 3.8495 | 3.7821 | 3.7168 | 3.6537 | 3.5937 | 1.1326 | 0.98737 | 0.88842 | 6.3 | 6.2137 | 3.4611 | 3.3979 | 3.3295 | 3.2621 | 3.1958 | 3.1326 | 3.0716 | 1.16 | 0.73579 | 0.65895
|  | PIDDLETRENTHIDE PRIMARY | EE |  |  |  |  | 6.5895 | 6.5253 | 3.7484 | 3.6853 | 3.6179 | 3.5516 | 3.4863 | 3.4253 | 3.3663 | 2.9832 | 1.3095 | 1.2326 | 6.3221 | 6.2537 | 3.9842 | 3.9189 | 3.8495 | 3.7821 | 3.7168 | 3.6537 | 3.5937 | 3.1979 | 1.3253 | 1.2516 | 6.3568 | 6.2884 | 3.4611 | 3.3979 | 3.3295 | 3.2621 | 3.1958 | 3.1326 | 3.0716 | 2.6558 | 0.73579 | 0.65895
|  | PIDDLETRENTHIDE PRIMARY | HT |  |  |  |  | 6.5358 | 6.4547 | 6.3758 | 6.2958 | 6.2137 | 6.1326 | 5.4095 | 5.3632 | 5.32 | 2.0695 | 1.9116 | 1.8074 | 6.2642 | 6.1789 | 6.0947 | 6.0105 | 5.9263 | 5.8421 | 5.0032 | 4.9579 | 4.9168 | 1.1326 | 0.98737 | 0.88842 | 6.3 | 6.2137 | 6.1295 | 6.0453 | 5.96 | 5.8747 | 5.0347 | 4.9874 | 4.9442 | 1.16 | 1.0021 | 0.89789
|  | PIDDLETRENTHIDE PRIMARY | HE |  |  |  |  | 6.6621 | 6.62 | 6.58 | 6.5368 | 6.4895 | 6.4432 | 6.4011 | 6.36 | 6.3232 | 5.8989 | 4.3042 | 2.0832 | 6.3989 | 6.3547 | 6.3126 | 6.2674 | 6.2189 | 6.1716 | 6.1284 | 6.0884 | 6.0505 | 5.5811 | 3.7211 | 3.6811 | 6.4326 | 6.3895 | 6.3474 | 6.3032 | 6.2537 | 6.2063 | 6.1621 | 6.12 | 6.0821 | 5.6053 | 3.7442 | 3.6989
|  | PIDDLETRENTHIDE PRIMARY | CF |  |  |  |  | 6.7032 | 6.68 | 6.6558 | 6.6326 | 6.6063 | 6.5811 | 6.5558 | 6.5305 | 6.5063 | 6.3937 | 6.2863 | 6.1768 | 6.4421 | 6.4168 | 6.3916 | 6.3674 | 6.3411 | 6.3137 | 6.2874 | 6.2611 | 6.2368 | 6.1189 | 6.0053 | 5.8863 | 6.4737 | 6.4495 | 6.4263 | 6.4011 | 6.3747 | 6.3484 | 6.3211 | 6.2947 | 6.2695 | 6.1495 | 6.0347 | 5.9126
FLEET-BRAMLEY GSP | FERNHURST BSP | PLAISTOW PRIMARY | MINIMUM HEADROOM | TQ 02071 29626 | NO | YES | 0 | 16.5389 | 16.3684 | 16.1684 | 15.9716 | 15.6 | 15.1263 | 14.5558 | 14.4674 | 14.3863 | 13.3779 | 12.0526 | 6.2916 | 14.8284 | 14.6453 | 14.4295 | 14.2179 | 13.8 | 13.2516 | 12.5832 | 12.4947 | 12.4137 | 11.2621 | 9.7116 | 9.3011 | 15.0053 | 14.8263 | 14.6158 | 14.4084 | 14.0053 | 13.4853 | 12.8179 | 12.7295 | 12.6484 | 11.4989 | 9.9505 | 9.5411
|  | PLAISTOW PRIMARY | EE |  |  |  |  | 16.6589 | 16.5221 | 16.3653 | 16.2168 | 16.0674 | 16.0063 | 15.8779 | 15.7368 | 15.5947 | 14.0516 | 13.3726 | 12.7653 | 14.9589 | 14.8126 | 14.6432 | 14.4842 | 14.3253 | 14.1884 | 14.0526 | 13.9 | 13.7453 | 11.9737 | 11.2032 | 10.5105 | 15.1326 | 14.9895 | 14.8242 | 14.6674 | 14.5116 | 14.4211 | 14.2853 | 14.1326 | 13.9779 | 12.2095 | 11.4411 | 10.7484
|  | PLAISTOW PRIMARY | HT |  |  |  |  | 16.5389 | 16.3684 | 16.1684 | 15.9716 | 15.6 | 15.1263 | 14.5558 | 14.4674 | 14.3863 | 13.3779 | 12.0526 | 11.6758 | 14.8284 | 14.6453 | 14.4295 | 14.2179 | 13.8 | 13.2516 | 12.5832 | 12.4947 | 12.4137 | 11.2621 | 9.7116 | 9.3011 | 15.0053 | 14.8263 | 14.6158 | 14.4084 | 14.0053 | 13.4853 | 12.8179 | 12.7295 | 12.6484 | 11.4989 | 9.9505 | 9.5411
|  | PLAISTOW PRIMARY | HE |  |  |  |  | 16.8137 | 16.7274 | 16.6189 | 16.5137 | 16.4032 | 16.3884 | 16.2979 | 16.1968 | 16.0905 | 14.7253 | 14.2053 | 6.2916 | 15.1274 | 15.0347 | 14.9168 | 14.8053 | 14.6874 | 14.6042 | 14.5084 | 14.4 | 14.2832 | 12.7063 | 12.1116 | 11.5832 | 15.2979 | 15.2063 | 15.0916 | 14.9821 | 14.8663 | 14.8358 | 14.74 | 14.6326 | 14.5158 | 12.9411 | 12.3484 | 11.82
|  | PLAISTOW PRIMARY | CF |  |  |  |  | 16.9 | 16.8516 | 16.7968 | 16.7421 | 16.6832 | 16.6295 | 16.5768 | 16.5221 | 16.4611 | 15.6032 | 15.2611 | 14.9695 | 15.2211 | 15.1674 | 15.1074 | 15.0463 | 14.9842 | 14.9253 | 14.8684 | 14.8105 | 14.7442 | 13.7526 | 13.3547 | 13.0095 | 15.3895 | 15.3368 | 15.2779 | 15.2189 | 15.1579 | 15.1011 | 15.0453 | 14.9884 | 14.9232 | 13.9811 | 13.5884 | 13.2442
MINETY GSP | STRATTON (MAIN) BSP | PLESSEY PRIMARY | MINIMUM HEADROOM | SU 16381 86720 | NO | YES | 0 | 18.4316 | 18.2379 | 18.0337 | 17.82 | 17.5968 | 17.3674 | 17.1653 | 16.9811 | 16.8221 | 15.5063 | 13.2284 | -7.6358 | 15.3284 | 14.9916 | 14.2642 | 14.0947 | 13.8179 | 13.3337 | 12.8874 | 12.4968 | 12.2947 | 10.7832 | 8.1768 | 5.6232 | 16.1505 | 15.8063 | 15.1305 | 14.9611 | 14.6758 | 14.2126 | 13.7863 | 13.4116 | 13.2137 | 11.7674 | 9.3211 | 6.8758
|  | PLESSEY PRIMARY | EE |  |  |  |  | 18.5411 | 18.3779 | 18.1516 | 17.9821 | 17.8053 | 17.6347 | 17.4726 | 17.3021 | 17.1463 | 16.5095 | 14.6884 | 12.8947 | 15.5274 | 15.2747 | 14.2642 | 14.0947 | 13.9179 | 13.7474 | 13.5853 | 13.2432 | 12.9063 | 11.8958 | 9.8042 | 7.7305 | 16.3737 | 16.0968 | 15.1305 | 14.9611 | 14.7842 | 14.6137 | 14.4516 | 14.1242 | 13.8021 | 12.8284 | 10.8674 | 8.9295
|  | PLESSEY PRIMARY | HT |  |  |  |  | 18.4316 | 18.2379 | 18.0337 | 17.82 | 17.5968 | 17.3674 | 17.1653 | 16.9811 | 16.8221 | 15.5063 | 13.2284 | 11.0095 | 15.3284 | 14.9916 | 14.6284 | 14.2547 | 13.8179 | 13.3337 | 12.8874 | 12.4968 | 12.2947 | 10.7832 | 8.1768 | 5.6232 | 16.1505 | 15.8063 | 15.4558 | 15.0958 | 14.6758 | 14.2126 | 13.7863 | 13.4116 | 13.2137 | 11.7674 | 9.3211 | 6.8758
|  | PLESSEY PRIMARY | HE |  |  |  |  | 18.6874 | 18.5705 | 18.44 | 18.3011 | 18.1484 | 17.9979 | 17.8526 | 17.7158 | 17.6011 | 17.2432 | 16.2895 | -7.6358 | 15.7905 | 15.6211 | 15.4337 | 15.2389 | 14.9968 | 14.6642 | 14.3011 | 13.9568 | 13.6853 | 13.2105 | 11.5621 | 9.8526 | 16.5316 | 16.4095 | 16.2747 | 16.0716 | 15.8063 | 15.4863 | 15.1411 | 14.8137 | 14.5547 | 14.0895 | 12.5495 | 10.9579
|  | PLESSEY PRIMARY | CF |  |  |  |  | 18.7874 | 18.7274 | 18.6621 | 18.5926 | 18.5211 | 18.4484 | 18.3768 | 18.3053 | 18.2305 | 17.9032 | 17.7063 | 17.1863 | 15.8937 | 15.8337 | 15.7463 | 15.6389 | 15.5284 | 15.4158 | 15.3021 | 15.1884 | 15.0295 | 14.3147 | 13.5432 | 12.5126 | 16.6316 | 16.5716 | 16.5053 | 16.4326 | 16.3568 | 16.2568 | 16.1316 | 16.0063 | 15.8411 | 15.1579 | 14.4326 | 13.4737
LOVEDEAN GSP | FAREHAM (MAIN) BSP | PLESSEY TITCHFIELD PRIMARY | MINIMUM HEADROOM | SU 53390 06922 | NO | YES | 0 | 35.5179 | 35.14 | 34.7558 | 34.3705 | 33.9874 | 33.6621 | 33.3126 | 32.9895 | 32.6905 | 31.0937 | 29.5263 | 1.8789 | 31.6179 | 31.2211 | 30.8189 | 30.4168 | 30.0179 | 29.7137 | 29.3316 | 28.9789 | 28.6526 | 26.8379 | 25.0095 | 23.3253 | 32.9116 | 32.5032 | 32.0916 | 31.6789 | 31.2716 | 30.9653 | 30.5916 | 30.2442 | 29.9242 | 28.1642 | 26.4042 | 24.72
|  | PLESSEY TITCHFIELD PRIMARY | EE |  |  |  |  | 35.7789 | 35.4779 | 35.1716 | 34.8621 | 34.5495 | 34.2484 | 33.96 | 33.7389 | 33.4832 | 32.2579 | 31.0495 | 29.9863 | 31.8937 | 31.5768 | 31.2579 | 30.9347 | 30.6095 | 30.2968 | 29.9958 | 29.8074 | 29.5305 | 28.1537 | 26.7368 | 25.4695 | 33.1958 | 32.8705 | 32.5432 | 32.2126 | 31.88 | 31.56 | 31.2516 | 31.0568 | 30.7821 | 29.4368 | 28.0747 | 26.8621
|  | PLESSEY TITCHFIELD PRIMARY | HT |  |  |  |  | 35.5179 | 35.14 | 34.7558 | 34.3705 | 33.9874 | 33.6621 | 33.3126 | 32.9895 | 32.6905 | 31.0937 | 29.5263 | 28.1011 | 31.6179 | 31.2211 | 30.8189 | 30.4168 | 30.0179 | 29.7137 | 29.3316 | 28.9789 | 28.6526 | 26.8379 | 25.0095 | 23.3253 | 32.9116 | 32.5032 | 32.0916 | 31.6789 | 31.2716 | 30.9653 | 30.5916 | 30.2442 | 29.9242 | 28.1642 | 26.4042 | 24.72
|  | PLESSEY TITCHFIELD PRIMARY | HE |  |  |  |  | 36.1179 | 35.9221 | 35.7168 | 35.5011 | 35.2779 | 35.0653 | 34.8579 | 34.6042 | 34.4316 | 33.5874 | 32.7389 | 1.8789 | 32.2516 | 32.0474 | 31.8337 | 31.6105 | 31.38 | 31.1589 | 30.9453 | 30.6421 | 30.4611 | 29.5632 | 28.5526 | 27.6621 | 33.5653 | 33.3558 | 33.1368 | 32.9095 | 32.6747 | 32.4495 | 32.2305 | 31.9211 | 31.7368 | 30.8063 | 29.84 | 28.9916
|  | PLESSEY TITCHFIELD PRIMARY | CF |  |  |  |  | 36.2768 | 36.1989 | 36.0853 | 35.9695 | 35.8505 | 35.7295 | 35.6095 | 35.4905 | 35.3705 | 34.8105 | 34.2432 | 33.7495 | 32.4147 | 32.3347 | 32.2168 | 32.0947 | 31.9695 | 31.8432 | 31.7168 | 31.5926 | 31.4674 | 30.8789 | 30.2621 | 29.6684 | 33.7305 | 33.6505 | 33.5284 | 33.4032 | 33.2747 | 33.1453 | 33.0158 | 32.8874 | 32.7589 | 32.1537 | 31.5074 | 30.9379
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | POOLE PRIMARY | MINIMUM HEADROOM | SZ 01091 90595 | NO | YES | 0 | 24 | 23.4989 | 22.4558 | 21.4495 | 20.3011 | 19.1305 | 17.98 | 17.4979 | 17.2653 | 16.2021 | 15.1947 | -0.65895 | 20.2958 | 19.2432 | 18.0737 | 16.9253 | 15.5979 | 14.2442 | 12.9126 | 12.3642 | 12.1095 | 10.9358 | 9.8116 | 8.7379 | 21.2305 | 20.5242 | 19.3211 | 18.1611 | 16.8347 | 15.4842 | 14.1547 | 13.6063 | 13.3516 | 12.18 | 11.0568 | 9.9853
|  | POOLE PRIMARY | EE |  |  |  |  | 24.0726 | 23.9821 | 23.2189 | 22.4263 | 21.4274 | 20.4021 | 18.9926 | 17.5916 | 17.3537 | 16.5263 | 15.7516 | 15.0158 | 20.5579 | 19.7842 | 18.9253 | 18.0379 | 16.8937 | 15.7063 | 14.0663 | 12.4358 | 12.1716 | 11.26 | 10.3926 | 9.5611 | 21.3158 | 21.0789 | 20.1958 | 19.2842 | 18.1284 | 16.9432 | 15.3063 | 13.6779 | 13.4147 | 12.5042 | 11.6379 | 10.8074
|  | POOLE PRIMARY | HT |  |  |  |  | 24 | 23.4989 | 22.4558 | 21.4495 | 20.3011 | 19.1305 | 17.98 | 17.4979 | 17.2653 | 16.2021 | 15.1947 | 14.2389 | 20.2958 | 19.2432 | 18.0737 | 16.9253 | 15.5979 | 14.2442 | 12.9126 | 12.3642 | 12.1095 | 10.9358 | 9.8116 | 8.7379 | 21.2305 | 20.5242 | 19.3211 | 18.1611 | 16.8347 | 15.4842 | 14.1547 | 13.6063 | 13.3516 | 12.18 | 11.0568 | 9.9853
|  | POOLE PRIMARY | HE |  |  |  |  | 24.1305 | 24.0547 | 23.4221 | 22.6537 | 21.6674 | 20.6705 | 19.2379 | 17.9916 | 17.8495 | 17.2589 | 16.7274 | -0.65895 | 20.7053 | 19.9716 | 19.1453 | 18.2832 | 17.1558 | 15.9989 | 14.3295 | 12.8768 | 12.7221 | 12.0705 | 11.4716 | 10.9147 | 21.38 | 21.2621 | 20.42 | 19.5326 | 18.3905 | 17.2358 | 15.5695 | 14.1189 | 13.9642 | 13.3137 | 12.7158 | 12.1589
|  | POOLE PRIMARY | CF |  |  |  |  | 24.1768 | 24.1284 | 24.0789 | 24.0274 | 23.9737 | 23.92 | 23.8663 | 23.5442 | 22.9326 | 20.3537 | 19.9284 | 19.6021 | 20.9558 | 20.8011 | 20.5895 | 20.4505 | 20.2947 | 20.1211 | 19.7958 | 19.3053 | 18.6168 | 15.6568 | 15.1779 | 14.8053 | 21.4442 | 21.3842 | 21.3242 | 21.2663 | 21.2063 | 21.1453 | 21.0747 | 20.5905 | 19.8821 | 16.8937 | 16.4158 | 16.0442
LOVEDEAN GSP | PORTSMOUTH BSP | PORTCHESTER PRIMARY | MINIMUM HEADROOM | SU 62043 05575 | NO | YES | 0.042105 | 34.2326 | 33.7484 | 32.6947 | 31.5589 | 30.3495 | 29.14 | 27.9926 | 26.8853 | 26.2989 | 23.2011 | 20.1632 | -2.2011 | 29.1547 | 28.0842 | 26.9905 | 25.7547 | 24.4126 | 23.0726 | 21.7958 | 20.56 | 19.9347 | 16.5568 | 13.1989 | 10.1505 | 30.4316 | 29.3432 | 28.2316 | 27.0347 | 25.74 | 24.4021 | 23.1232 | 21.8863 | 21.2579 | 17.8632 | 14.4821 | 11.4295
|  | PORTCHESTER PRIMARY | EE |  |  |  |  | 34.4632 | 34.14 | 33.5253 | 32.6853 | 31.7337 | 30.8063 | 29.8116 | 28.5853 | 27.6558 | 25.2305 | 22.8211 | 20.7137 | 29.6347 | 28.7137 | 27.8505 | 26.9811 | 25.9505 | 24.9284 | 23.8242 | 22.4463 | 21.4105 | 18.7937 | 16.1411 | 13.7716 | 30.9179 | 29.9811 | 29.1032 | 28.2211 | 27.2189 | 26.2379 | 25.1474 | 23.7674 | 22.7274 | 20.0842 | 17.3979 | 15.0211
|  | PORTCHESTER PRIMARY | HT |  |  |  |  | 34.2326 | 33.7484 | 32.6947 | 31.5589 | 30.3495 | 29.14 | 27.9926 | 26.8853 | 26.2989 | 23.2011 | 20.1632 | 17.4411 | 29.1547 | 28.0842 | 26.9905 | 25.7547 | 24.4126 | 23.0726 | 21.7958 | 20.56 | 19.9347 | 16.5568 | 13.1989 | 10.1505 | 30.4316 | 29.3432 | 28.2316 | 27.0347 | 25.74 | 24.4021 | 23.1232 | 21.8863 | 21.2579 | 17.8632 | 14.4821 | 11.4295
|  | PORTCHESTER PRIMARY | HE |  |  |  |  | 34.7653 | 34.5379 | 34.2832 | 33.8389 | 33.0411 | 32.2768 | 31.4147 | 30.3611 | 29.6579 | 28.1053 | 26.5074 | -2.2011 | 30.2705 | 29.5474 | 28.8674 | 28.1695 | 27.3432 | 26.5253 | 25.5589 | 24.3653 | 23.58 | 21.8989 | 20.1074 | 18.4589 | 31.5621 | 30.8263 | 30.1358 | 29.4263 | 28.5842 | 27.7768 | 26.8621 | 25.6916 | 24.9053 | 23.2137 | 21.4147 | 19.7589
|  | PORTCHESTER PRIMARY | CF |  |  |  |  | 34.9758 | 34.8558 | 34.7295 | 34.6 | 34.4632 | 34.3211 | 34.1842 | 34.0474 | 33.9126 | 31.6811 | 30.5811 | 29.6095 | 30.8642 | 30.4758 | 30.1705 | 29.9411 | 29.7074 | 29.4653 | 29.1716 | 28.8221 | 28.2853 | 25.8526 | 24.62 | 23.5147 | 32.1663 | 31.7705 | 31.4611 | 31.2295 | 30.9905 | 30.7453 | 30.4453 | 30.0905 | 29.5411 | 27.14 | 25.9379 | 24.8295
CHICKERELL GSP | CHICKERELL BSP | PORTLAND PRIMARY | MINIMUM HEADROOM | SY 68307 73941 | NO | YES | 0 | 25.9908 | 25.774 | 25.5435 | 25.3035 | 24.9666 | 24.5656 | 24.1961 | 23.8445 | 23.5182 | 20.5624 | 18.4708 | -1.1408 | 22.4013 | 21.9403 | 21.4087 | 20.8729 | 20.2213 | 19.794 | 19.4013 | 19.0235 | 18.6719 | 15.3403 | 12.9908 | 10.9287 | 23.2371 | 22.794 | 22.2835 | 21.7687 | 21.1477 | 20.7329 | 20.3508 | 19.9866 | 19.6477 | 16.3413 | 13.9908 | 11.9277
|  | PORTLAND PRIMARY | EE |  |  |  |  | 26.0992 | 25.914 | 25.7171 | 25.5087 | 25.2919 | 25.0824 | 24.8403 | 24.535 | 24.2519 | 21.6024 | 19.955 | 18.5677 | 22.6687 | 22.2866 | 21.8329 | 21.3698 | 20.7887 | 20.4403 | 20.1045 | 19.7792 | 19.4771 | 16.4813 | 14.6277 | 13.0582 | 23.4919 | 23.1245 | 22.6898 | 22.2456 | 21.6908 | 21.3508 | 21.0256 | 20.7098 | 20.4171 | 17.4835 | 15.6266 | 14.055
|  | PORTLAND PRIMARY | HT |  |  |  |  | 25.9908 | 25.774 | 25.5435 | 25.3035 | 24.9666 | 24.5656 | 24.1961 | 23.8445 | 23.5182 | 20.5624 | 18.4708 | 16.6435 | 22.4013 | 21.9403 | 21.4087 | 20.8729 | 20.2213 | 19.794 | 19.4013 | 19.0235 | 18.6719 | 15.3403 | 12.9908 | 10.9287 | 23.2371 | 22.794 | 22.2835 | 21.7687 | 21.1477 | 20.7329 | 20.3508 | 19.9866 | 19.6477 | 16.3413 | 13.9908 | 11.9277
|  | PORTLAND PRIMARY | HE |  |  |  |  | 26.255 | 26.115 | 25.9613 | 25.795 | 25.6171 | 25.4477 | 25.2887 | 25.1392 | 25.0108 | 23.1319 | 21.9224 | -1.1408 | 23.0371 | 22.7666 | 22.4192 | 22.0603 | 21.5729 | 21.3213 | 21.0824 | 20.855 | 20.6529 | 18.1529 | 16.7803 | 15.674 | 23.714 | 23.5656 | 23.2508 | 22.9056 | 22.4413 | 22.195 | 21.9624 | 21.7403 | 21.5435 | 19.1561 | 17.7813 | 16.675
|  | PORTLAND PRIMARY | CF |  |  |  |  | 26.3656 | 26.2856 | 26.2035 | 26.1171 | 26.0287 | 25.9382 | 25.8487 | 25.7603 | 25.6719 | 24.8571 | 24.0277 | 23.3992 | 23.2898 | 23.1245 | 22.9287 | 22.7308 | 22.4856 | 22.3266 | 22.1677 | 22.0098 | 21.8519 | 20.055 | 19.114 | 18.3971 | 23.8329 | 23.7477 | 23.6582 | 23.5508 | 23.3171 | 23.1624 | 23.0098 | 22.8571 | 22.7045 | 21.0077 | 20.1182 | 19.3992
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH PRIMARY | MINIMUM HEADROOM | SZ 63405 99685 | NO | YES | 0 | 41.3335 | 41.224 | 41.1082 | 40.9829 | 40.8514 | 40.7177 | 40.5966 | 40.484 | 40.3787 | 39.9208 | 39.5514 | 20.0019 | 37.1682 | 37.0187 | 36.864 | 36.7008 | 36.5324 | 36.3629 | 36.1956 | 36.0187 | 35.8503 | 34.8787 | 33.6019 | 32.3945 | 37.7977 | 37.6629 | 37.5219 | 37.3724 | 37.2177 | 37.0608 | 36.9177 | 36.7819 | 36.6545 | 35.9682 | 34.6945 | 33.4703
|  | PORTSMOUTH PRIMARY | EE |  |  |  |  | 41.4187 | 41.3356 | 41.2482 | 41.1514 | 41.0493 | 40.9493 | 40.8493 | 40.7514 | 40.6629 | 40.3124 | 40.0493 | 39.844 | 37.2829 | 37.1693 | 37.0524 | 36.9261 | 36.7956 | 36.6682 | 36.5398 | 36.4156 | 36.2998 | 35.7198 | 34.7893 | 33.8703 | 37.9019 | 37.7987 | 37.6924 | 37.5777 | 37.4577 | 37.3398 | 37.2219 | 37.1072 | 37.0008 | 36.5661 | 35.8829 | 34.9608
|  | PORTSMOUTH PRIMARY | HT |  |  |  |  | 41.3335 | 41.224 | 41.1082 | 40.9829 | 40.8514 | 40.7177 | 40.5966 | 40.484 | 40.3787 | 39.9208 | 39.5514 | 38.5556 | 37.1682 | 37.0187 | 36.864 | 36.7008 | 36.5324 | 36.3629 | 36.1956 | 36.0187 | 35.8503 | 34.8787 | 33.6019 | 32.3945 | 37.7977 | 37.6629 | 37.5219 | 37.3724 | 37.2177 | 37.0608 | 36.9177 | 36.7819 | 36.6545 | 35.9682 | 34.6945 | 33.4703
|  | PORTSMOUTH PRIMARY | HE |  |  |  |  | 41.4556 | 41.3798 | 41.2966 | 41.2061 | 41.1103 | 41.0187 | 40.9324 | 40.8524 | 40.7829 | 40.5335 | 42.744 | 20.0019 | 37.3472 | 37.2661 | 37.1661 | 37.0577 | 36.9461 | 36.8377 | 36.7345 | 36.6387 | 36.5545 | 36.2303 | 37.7093 | 36.9314 | 37.9556 | 37.8766 | 37.7829 | 37.6808 | 37.5745 | 37.4724 | 37.3756 | 37.2861 | 37.2072 | 36.9103 | 39.3472 | 39.0724
|  | PORTSMOUTH PRIMARY | CF |  |  |  |  | 41.4935 | 41.4419 | 41.3893 | 41.3345 | 41.2787 | 41.2208 | 41.164 | 41.1082 | 41.0514 | 40.8019 | 40.6724 | 40.5998 | 37.3851 | 37.3335 | 37.2808 | 37.2187 | 37.1503 | 37.0798 | 37.0103 | 36.9429 | 36.8735 | 36.564 | 36.3756 | 36.1808 | 37.9935 | 37.9419 | 37.8893 | 37.8303 | 37.7661 | 37.6998 | 37.6356 | 37.5724 | 37.5072 | 37.2198 | 37.0535 | 36.9135
MELKSHAM GSP | ANDOVER BSP | PORTWAY PRIMARY | MINIMUM HEADROOM | SU 34402 46001 | NO | YES | 8.4758 | 23.3101 | 23.1459 | 22.9722 | 22.7954 | 22.6154 | 22.4343 | 22.2743 | 17.9627 | 16.8617 | 16.1101 | 15.3312 | -14.6036 | 21.3217 | 21.0796 | 20.7059 | 20.4343 | 20.1648 | 19.8975 | 19.6533 | 16.908 | 15.6343 | 14.8375 | 13.9848 | 13.6133 | 21.7396 | 21.5501 | 21.3501 | 21.148 | 20.9438 | 20.7406 | 20.5585 | 17.0206 | 15.7491 | 14.9522 | 14.1006 | 13.7291
|  | PORTWAY PRIMARY | EE |  |  |  |  | 23.4101 | 23.2764 | 23.1343 | 22.988 | 22.8385 | 22.6933 | 22.5564 | 22.4217 | 22.3038 | 18.8133 | 18.1291 | 17.6722 | 21.4859 | 21.2922 | 21.0827 | 20.7733 | 20.5512 | 20.3375 | 20.1333 | 19.9301 | 19.7491 | 18.1185 | 17.3059 | 16.808 | 21.8617 | 21.708 | 21.5438 | 21.3785 | 21.2101 | 21.0469 | 20.8922 | 20.7396 | 20.6048 | 18.0617 | 17.3038 | 16.8006
|  | PORTWAY PRIMARY | HT |  |  |  |  | 23.3101 | 23.1459 | 22.9722 | 22.7954 | 22.6154 | 22.4343 | 22.2743 | 17.9627 | 16.8617 | 16.1101 | 15.3312 | 14.9722 | 21.3217 | 21.0796 | 20.7059 | 20.4343 | 20.1648 | 19.8975 | 19.6533 | 16.908 | 15.6343 | 14.8375 | 13.9848 | 13.6133 | 21.7396 | 21.5501 | 21.3501 | 21.148 | 20.9438 | 20.7406 | 20.5585 | 17.0206 | 15.7491 | 14.9522 | 14.1006 | 13.7291
|  | PORTWAY PRIMARY | HE |  |  |  |  | 23.5417 | 23.4491 | 23.3448 | 23.2354 | 23.1196 | 23.0101 | 22.9048 | 22.8069 | 22.7217 | 19.4301 | 18.9375 | -14.6036 | 21.7006 | 21.5733 | 21.4248 | 21.2827 | 21.1312 | 20.9869 | 20.8501 | 20.7154 | 20.4912 | 18.7438 | 18.1469 | 17.7901 | 22.0206 | 21.9164 | 21.7975 | 21.6775 | 21.5501 | 21.4291 | 21.3133 | 21.2027 | 21.108 | 18.7017 | 18.1491 | 17.788
|  | PORTWAY PRIMARY | CF |  |  |  |  | 23.6269 | 23.5775 | 23.5217 | 23.4659 | 23.4048 | 23.3448 | 23.2891 | 23.2333 | 23.1775 | 22.9238 | 22.7575 | 22.6343 | 21.8217 | 21.7469 | 21.6575 | 21.5648 | 21.4606 | 21.3617 | 21.2785 | 21.1985 | 21.1185 | 20.5964 | 20.1238 | 19.6669 | 22.1175 | 22.0596 | 21.9933 | 21.9248 | 21.8501 | 21.7775 | 21.7112 | 21.648 | 21.5848 | 21.2848 | 21.0385 | 20.828
IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY | MINIMUM HEADROOM | TQ 03425 75555 | NO | NO | 0 | 36.0526 | 35.9021 | 35.7421 | 35.5768 | 35.4105 | 35.2368 | 35.0853 | 34.9474 | 34.8189 | 34.2968 | 35.5358 | -8.8916 | 31.6053 | 31.3474 | 31.0821 | 30.6947 | 30.4189 | 30.1379 | 29.8653 | 29.5958 | 28.7526 | 27.4116 | 30.0695 | 29.7116 | 32.3895 | 32.2389 | 32.0789 | 31.8368 | 31.5621 | 31.28 | 31.0084 | 30.7389 | 29.8947 | 28.5537 | 31.2116 | 30.8537
|  | POYLE PRIMARY | EE |  |  |  |  | 36.1432 | 36.0211 | 35.8905 | 35.7537 | 35.6116 | 35.4747 | 35.3453 | 35.2168 | 35.1053 | 34.6947 | 68.0958 | 67.78 | 31.7505 | 31.5716 | 31.3611 | 31.0663 | 30.8389 | 30.6189 | 30.3926 | 30.1558 | 29.3516 | 28.2779 | 61.0358 | 60.2084 | 32.48 | 32.3579 | 32.2274 | 32.0905 | 31.9484 | 31.7621 | 31.5347 | 31.2989 | 30.4947 | 29.42 | 62.1779 | 61.3505
|  | POYLE PRIMARY | HT |  |  |  |  | 36.0526 | 35.9021 | 35.7421 | 35.5768 | 35.4105 | 35.2368 | 35.0853 | 34.9474 | 34.8189 | 34.2968 | 67.4726 | 66.4937 | 31.6053 | 31.3474 | 31.0821 | 30.6947 | 30.4189 | 30.1379 | 29.8653 | 29.5958 | 28.7526 | 27.4116 | 59.9 | 58.7821 | 32.3895 | 32.2389 | 32.0789 | 31.8368 | 31.5621 | 31.28 | 31.0084 | 30.7389 | 29.8947 | 28.5537 | 61.0421 | 59.9242
|  | POYLE PRIMARY | HE |  |  |  |  | 36.2505 | 36.1611 | 36.0621 | 35.9537 | 35.84 | 35.7316 | 35.6284 | 35.5326 | 35.4495 | 35.1716 | 68.6884 | -8.8916 | 31.8611 | 31.7716 | 31.6705 | 31.5326 | 31.3695 | 31.2147 | 31.0484 | 30.8874 | 30.1526 | 29.4074 | 62.4663 | 61.9326 | 32.5874 | 32.4979 | 32.3989 | 32.2905 | 32.1768 | 32.0684 | 31.9653 | 31.8695 | 31.2947 | 30.5495 | 63.6084 | 63.0747
|  | POYLE PRIMARY | CF |  |  |  |  | 36.3284 | 36.2789 | 36.2274 | 36.1747 | 36.1189 | 36.0621 | 36.0074 | 35.9526 | 35.8979 | 35.6537 | 35.5358 | 35.4674 | 31.9389 | 31.8895 | 31.8379 | 31.7842 | 31.7274 | 31.6695 | 31.5905 | 31.5032 | 31.0674 | 30.4916 | 30.0695 | 29.7116 | 32.6653 | 32.6158 | 32.5642 | 32.5116 | 32.4558 | 32.3989 | 32.3442 | 32.2895 | 32.2105 | 31.6337 | 31.2116 | 30.8537
MINETY GSP | STRATTON (MAIN) BSP | PRESSED STEEL SWINDON PRIMARY | MINIMUM HEADROOM | SU 16963 86368 | NO | YES | 0 | 44.9642 | 93.7526 | 93.5274 | 93.2958 | 93.0411 | 92.42 | 91.5737 | 90.7579 | 89.9611 | 87.0147 | 85.3105 | 63.1074 | 41.7074 | 90.3063 | 89.9 | 89.4937 | 88.7947 | 88.0947 | 87.1368 | 86.2095 | 85.3032 | 81.96 | 80.0463 | 78.2274 | 42.3547 | 90.9684 | 90.5747 | 90.1821 | 89.5179 | 88.8516 | 87.9495 | 87.0779 | 86.1789 | 82.8421 | 80.9305 | 79.1137
|  | PRESSED STEEL SWINDON PRIMARY | EE |  |  |  |  | 45.0968 | 93.9253 | 93.7432 | 93.5526 | 93.3568 | 93.0621 | 92.2789 | 91.5032 | 90.7537 | 88.1642 | 86.8463 | 85.6116 | 41.9874 | 90.6716 | 90.3495 | 90.0221 | 89.3989 | 88.7884 | 87.8989 | 87.0158 | 86.1611 | 83.2105 | 81.7253 | 80.3189 | 42.6242 | 91.3189 | 91.0063 | 90.6895 | 90.0989 | 89.5189 | 88.6842 | 87.8537 | 87.0368 | 84.0905 | 82.6074 | 81.2042
|  | PRESSED STEEL SWINDON PRIMARY | HT |  |  |  |  | 44.9642 | 93.7526 | 93.5274 | 93.2958 | 93.0411 | 92.42 | 91.5737 | 90.7579 | 89.9611 | 87.0147 | 85.3105 | 83.7021 | 41.7074 | 90.3063 | 89.9 | 89.4937 | 88.7947 | 88.0947 | 87.1368 | 86.2095 | 85.3032 | 81.96 | 80.0463 | 78.2274 | 42.3547 | 90.9684 | 90.5747 | 90.1821 | 89.5179 | 88.8516 | 87.9495 | 87.0779 | 86.1789 | 82.8421 | 80.9305 | 79.1137
|  | PRESSED STEEL SWINDON PRIMARY | HE |  |  |  |  | 45.2632 | 94.1432 | 94.0105 | 93.8684 | 93.7168 | 93.5716 | 93.1579 | 92.4663 | 91.7979 | 89.5916 | 88.6284 | 63.1074 | 42.3379 | 91.1453 | 90.9316 | 90.7084 | 90.18 | 89.66 | 88.8547 | 88.0621 | 87.2958 | 84.7642 | 83.6695 | 82.6305 | 42.9726 | 91.7747 | 91.5653 | 91.3484 | 90.8474 | 90.3568 | 89.6011 | 88.8589 | 88.1411 | 85.6432 | 84.5495 | 83.5126
|  | PRESSED STEEL SWINDON PRIMARY | CF |  |  |  |  | 45.3768 | 94.3147 | 94.2495 | 94.1832 | 94.1137 | 94.0432 | 93.9747 | 93.9032 | 93.6347 | 92.1484 | 91.5653 | 90.9832 | 42.5274 | 91.4137 | 91.2968 | 91.1779 | 90.9337 | 90.6726 | 90.2589 | 89.8147 | 89.3442 | 87.6484 | 86.9895 | 86.32 | 43.1663 | 92.0495 | 91.9295 | 91.8074 | 91.5747 | 91.3284 | 90.94 | 90.5253 | 90.0842 | 88.4926 | 87.8653 | 87.1968
FLEET-BRAMLEY GSP | ALTON BSP | PRESTON CANDOVER PRIMARY | MINIMUM HEADROOM | SU 60879 41131 | NO | YES | 0 | 16.5526 | 16.2684 | 15.8853 | 15.7326 | 15.5547 | 15.3684 | 15.1895 | 15.0147 | 14.8442 | 13.9779 | 13.1063 | 2.8179 | 14.4053 | 14.08 | 13.6411 | 13.48 | 13.3 | 13.1126 | 12.9326 | 12.7579 | 12.5874 | 11.7337 | 10.8821 | 10.1674 | 14.5305 | 14.2042 | 13.7674 | 13.6042 | 13.4168 | 13.22 | 13.0305 | 12.8442 | 12.6632 | 11.7421 | 10.8105 | 10.0653
|  | PRESTON CANDOVER PRIMARY | EE |  |  |  |  | 16.6316 | 16.4 | 16.0432 | 15.92 | 15.7653 | 15.6032 | 15.4421 | 15.2779 | 15.1042 | 14.2253 | 13.3874 | 12.8232 | 14.4895 | 14.2189 | 13.8147 | 13.6832 | 13.5295 | 13.3716 | 13.2168 | 13.0589 | 12.8926 | 12.0716 | 11.3126 | 10.7305 | 14.6147 | 14.3442 | 13.9389 | 13.8074 | 13.6453 | 13.4758 | 13.3063 | 13.1347 | 12.9516 | 12.0253 | 11.1442 | 10.5242
|  | PRESTON CANDOVER PRIMARY | HT |  |  |  |  | 16.5526 | 16.2684 | 15.8853 | 15.7326 | 15.5547 | 15.3684 | 15.1895 | 15.0147 | 14.8442 | 13.9779 | 13.1063 | 12.4284 | 14.4053 | 14.08 | 13.6411 | 13.48 | 13.3 | 13.1126 | 12.9326 | 12.7579 | 12.5874 | 11.7337 | 10.8821 | 10.1674 | 14.5305 | 14.2042 | 13.7674 | 13.6042 | 13.4168 | 13.22 | 13.0305 | 12.8442 | 12.6632 | 11.7421 | 10.8105 | 10.0653
|  | PRESTON CANDOVER PRIMARY | HE |  |  |  |  | 16.7147 | 16.5768 | 16.2621 | 16.1789 | 16.0663 | 15.9621 | 15.8621 | 15.7621 | 15.6621 | 15.0105 | 14.7474 | 2.8179 | 14.5768 | 14.4116 | 14.0505 | 13.9632 | 13.8526 | 13.7474 | 13.6505 | 13.5526 | 13.4526 | 12.7863 | 12.5474 | 12.2537 | 14.7021 | 14.5368 | 14.1758 | 14.0884 | 13.9716 | 13.8611 | 13.7568 | 13.6526 | 13.5463 | 12.8358 | 12.5632 | 12.2389
|  | PRESTON CANDOVER PRIMARY | CF |  |  |  |  | 16.76 | 16.7368 | 16.7095 | 16.6779 | 16.6305 | 16.4779 | 16.3874 | 16.3305 | 16.2705 | 15.9674 | 15.6242 | 15.4747 | 14.6221 | 14.5989 | 14.5705 | 14.5379 | 14.4916 | 14.32 | 14.22 | 14.1621 | 14.0989 | 13.7842 | 13.4189 | 13.28 | 14.7474 | 14.7242 | 14.6947 | 14.6621 | 14.6137 | 14.4389 | 14.3358 | 14.2747 | 14.2095 | 13.88 | 13.4989 | 13.3411
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN PRIMARY | MINIMUM HEADROOM | SY 74226 95039 | NO | YES | 0 | 6.8379 | 6.7695 | 6.6758 | 6.3916 | 5.8453 | 5.3074 | 4.6389 | 4.5168 | 4.3884 | 2.8779 | 0.85474 | 0.28842 | 6.1105 | 6.0126 | 5.9158 | 5.6095 | 5.0137 | 4.4158 | 3.6663 | 3.5632 | 3.4568 | 1.9421 | -0.14316 | -0.68526 | 6.2979 | 6.2021 | 6.1053 | 5.7884 | 5.1632 | 4.5505 | 3.7842 | 3.6611 | 3.5337 | 1.8811 | -0.36421 | -0.96947
|  | PUDDLETOWN PRIMARY | EE |  |  |  |  | 6.8674 | 6.8211 | 6.7684 | 6.6863 | 6.5463 | 6.3947 | 6.2347 | 6.0674 | 5.8958 | 4.3579 | 2.0968 | 0.94632 | 6.1674 | 6.0947 | 6.0147 | 5.9305 | 5.7979 | 5.6579 | 5.5116 | 5.3589 | 5.2053 | 3.7505 | 1.5274 | 0.30316 | 6.3274 | 6.2821 | 6.2021 | 6.1179 | 5.9726 | 5.8147 | 5.6484 | 5.4758 | 5.2979 | 3.6537 | 1.1653 | -0.12632
|  | PUDDLETOWN PRIMARY | HT |  |  |  |  | 6.8379 | 6.7695 | 6.6758 | 6.3916 | 5.8453 | 5.3074 | 4.6389 | 4.5168 | 4.3884 | 2.8779 | 0.85474 | 0.28842 | 6.1105 | 6.0126 | 5.9158 | 5.6095 | 5.0137 | 4.4158 | 3.6663 | 3.5632 | 3.4568 | 1.9421 | -0.14316 | -0.68526 | 6.2979 | 6.2021 | 6.1053 | 5.7884 | 5.1632 | 4.5505 | 3.7842 | 3.6611 | 3.5337 | 1.8811 | -0.36421 | -0.96947
|  | PUDDLETOWN PRIMARY | HE |  |  |  |  | 6.9084 | 6.8789 | 6.8463 | 6.8116 | 6.7326 | 6.6611 | 6.5726 | 6.4842 | 6.3958 | 5.6421 | 4.3074 | 2.0547 | 6.2421 | 6.1968 | 6.1516 | 6.1021 | 6.0084 | 5.9242 | 5.8389 | 5.7568 | 5.6768 | 4.9432 | 3.5316 | 2.5116 | 6.3684 | 6.3389 | 6.3063 | 6.2726 | 6.1874 | 6.0958 | 6.0011 | 5.9095 | 5.8189 | 5.0116 | 3.4958 | 2.4211
|  | PUDDLETOWN PRIMARY | CF |  |  |  |  | 6.9358 | 6.9211 | 6.9053 | 6.8884 | 6.8516 | 6.8158 | 6.78 | 6.7453 | 6.7147 | 6.4474 | 5.7147 | 5.02 | 6.2853 | 6.26 | 6.2347 | 6.2063 | 6.16 | 6.1179 | 6.0737 | 6.0274 | 5.9863 | 5.7179 | 4.9537 | 4.2105 | 6.3958 | 6.3811 | 6.3653 | 6.3484 | 6.3137 | 6.28 | 6.2453 | 6.2 | 6.1558 | 5.8663 | 5.0389 | 4.2526
AXMINSTER GSP | YEOVIL BSP | PULHAM PRIMARY | MINIMUM HEADROOM | ST 71579 09451 | NO | YES | 0 | 8.8316 | 8.6821 | 8.5305 | 7.5789 | 6.2674 | 4.9747 | 3.3263 | 3.22 | 3.1179 | 0.40632 | -3.5695 | -4.4284 | 7.7232 | 7.5621 | 7.3989 | 6.2705 | 4.7295 | 3.2305 | 1.3137 | 1.2137 | 1.1179 | -1.9474 | -6.5021 | -7.4484 | 7.9621 | 7.8063 | 7.6484 | 6.5589 | 5.0105 | 3.5063 | 1.5821 | 1.4737 | 1.3705 | -1.7453 | -6.3611 | -7.3316
|  | PULHAM PRIMARY | EE |  |  |  |  | 8.9337 | 8.8158 | 8.6947 | 8.5726 | 8.4295 | 8.28 | 8.1358 | 7.9905 | 7.8505 | 5.24 | 1.1653 | -1.3053 | 7.8358 | 7.7084 | 7.5789 | 7.4495 | 7.3042 | 7.1547 | 7.0126 | 6.8705 | 6.7347 | 3.7726 | -0.88 | -3.7347 | 8.0716 | 7.9474 | 7.8211 | 7.6937 | 7.5463 | 7.3926 | 7.2432 | 7.0937 | 6.9505 | 3.9453 | -0.79053 | -3.6716
|  | PULHAM PRIMARY | HT |  |  |  |  | 8.8316 | 8.6821 | 8.5305 | 7.5789 | 6.2674 | 4.9747 | 3.3263 | 3.22 | 3.1179 | 0.40632 | -3.5695 | -4.4284 | 7.7232 | 7.5621 | 7.3989 | 6.2705 | 4.7295 | 3.2305 | 1.3137 | 1.2137 | 1.1179 | -1.9474 | -6.5021 | -7.4484 | 7.9621 | 7.8063 | 7.6484 | 6.5589 | 5.0105 | 3.5063 | 1.5821 | 1.4737 | 1.3705 | -1.7453 | -6.3611 | -7.3316
|  | PULHAM PRIMARY | HE |  |  |  |  | 9.0716 | 8.9947 | 8.9168 | 8.8358 | 8.7326 | 8.6368 | 8.5453 | 8.4547 | 8.3747 | 6.9253 | 3.8705 | 1.2389 | 7.9863 | 7.9042 | 7.8211 | 7.7347 | 7.6316 | 7.5368 | 7.4432 | 7.3558 | 7.2768 | 5.6168 | 2.0421 | -0.37158 | 8.2158 | 8.1368 | 8.0547 | 7.9716 | 7.8663 | 7.7674 | 7.6726 | 7.58 | 7.4989 | 5.8547 | 2.2558 | -0.17895
|  | PULHAM PRIMARY | CF |  |  |  |  | 9.1495 | 9.1063 | 9.0632 | 9.02 | 8.9653 | 8.9126 | 8.86 | 8.8074 | 8.7579 | 8.1663 | 6.5032 | 4.9537 | 8.0716 | 8.0232 | 7.9768 | 7.9305 | 7.8737 | 7.8189 | 7.7653 | 7.7105 | 7.6589 | 6.9895 | 5.0221 | 3.2211 | 8.2979 | 8.2516 | 8.2074 | 8.1621 | 8.1053 | 8.0495 | 7.9958 | 7.9411 | 7.8895 | 7.2463 | 5.2789 | 3.4632
LOVEDEAN GSP | FORT WIDLEY BSP | PURBROOK PRIMARY | MINIMUM HEADROOM | SU 67047 07819 | NO | YES | 0 | 16.6347 | 16.4484 | 16.0579 | 15.3968 | 14.6411 | 13.9568 | 13.3337 | 12.7316 | 12.0989 | 9.5074 | 7.8695 | 1.0147 | 14.4884 | 13.9674 | 13.3568 | 12.6021 | 11.7495 | 10.9874 | 10.2884 | 9.6147 | 8.9011 | 5.9926 | 4.1863 | 1.9842 | 14.9442 | 14.4474 | 13.86 | 13.1053 | 12.2516 | 11.4853 | 10.7832 | 10.1063 | 9.3895 | 6.4579 | 4.6253 | 2.4137
|  | PURBROOK PRIMARY | EE |  |  |  |  | 16.7474 | 16.5937 | 16.4337 | 16.1179 | 15.5221 | 14.9737 | 14.4358 | 13.8295 | 13.1684 | 10.6347 | 9.3495 | 7.8032 | 14.8179 | 14.44 | 14.0063 | 13.4295 | 12.7463 | 12.1347 | 11.5347 | 10.8537 | 10.1063 | 7.2558 | 5.8568 | 4.0958 | 15.2579 | 14.8958 | 14.4811 | 13.9326 | 13.2463 | 12.6305 | 12.0274 | 11.3421 | 10.5905 | 7.7095 | 6.2747 | 4.5011
|  | PURBROOK PRIMARY | HT |  |  |  |  | 16.6347 | 16.4484 | 16.0579 | 15.3968 | 14.6411 | 13.9568 | 13.3337 | 12.7316 | 12.0989 | 9.5074 | 7.8695 | 5.9337 | 14.4884 | 13.9674 | 13.3568 | 12.6021 | 11.7495 | 10.9874 | 10.2884 | 9.6147 | 8.9011 | 5.9926 | 4.1863 | 1.9842 | 14.9442 | 14.4474 | 13.86 | 13.1053 | 12.2516 | 11.4853 | 10.7832 | 10.1063 | 9.3895 | 6.4579 | 4.6253 | 2.4137
|  | PURBROOK PRIMARY | HE |  |  |  |  | 16.8895 | 16.7821 | 16.6621 | 16.5347 | 16.1305 | 15.6737 | 15.2095 | 14.7011 | 14.1547 | 12.0116 | 11.1589 | 1.0147 | 15.1316 | 14.8474 | 14.4958 | 14.0116 | 13.4116 | 12.8926 | 12.3716 | 11.7968 | 11.1716 | 8.7242 | 7.7695 | 6.3516 | 15.4926 | 15.2874 | 14.9526 | 14.4947 | 13.9137 | 13.3926 | 12.8695 | 12.2926 | 11.6653 | 9.2053 | 8.24 | 6.8137
|  | PURBROOK PRIMARY | CF |  |  |  |  | 16.9895 | 16.9326 | 16.8726 | 16.8116 | 16.7442 | 16.6779 | 16.6095 | 16.5442 | 16.4789 | 14.2221 | 13.6442 | 12.8884 | 15.3432 | 15.2832 | 15.1832 | 15.0168 | 14.8347 | 14.66 | 14.4547 | 14.2474 | 13.9842 | 11.1989 | 10.5505 | 9.6832 | 15.6042 | 15.5442 | 15.48 | 15.4126 | 15.2726 | 15.1042 | 14.9095 | 14.7116 | 14.4611 | 11.6937 | 11.04 | 10.1653
FLEET-BRAMLEY GSP | PYESTOCK BSP | PYESTOCK PRIMARY | MINIMUM HEADROOM | SU 82940 54553 | NO | YES | 0 | 25.3361 | 25.3318 | 25.3287 | 25.3255 | 25.3087 | 25.2908 | 25.2697 | 25.2697 | 25.2697 | 25.2382 | 25.1887 | 20.9971 | 24.3108 | 24.3076 | 24.3066 | 24.3045 | 24.2939 | 24.2845 | 24.2718 | 24.2718 | 24.2718 | 24.2539 | 24.2255 | 24.2203 | 24.5139 | 24.5097 | 24.5055 | 24.5013 | 24.4813 | 24.4613 | 24.4371 | 24.4371 | 24.4371 | 24.3992 | 24.3413 | 24.3308
|  | PYESTOCK PRIMARY | EE |  |  |  |  | 25.3371 | 25.3339 | 25.3297 | 25.3266 | 25.3255 | 25.3245 | 25.3234 | 25.3234 | 25.3224 | 25.3055 | 25.255 | 25.2224 | 24.3108 | 24.3087 | 24.3066 | 24.3045 | 24.3045 | 24.3034 | 24.3034 | 24.3024 | 24.3024 | 24.2929 | 24.2634 | 24.2445 | 24.515 | 24.5108 | 24.5066 | 24.5034 | 24.5013 | 24.5003 | 24.4992 | 24.4982 | 24.4982 | 24.4771 | 24.4182 | 24.3803
|  | PYESTOCK PRIMARY | HT |  |  |  |  | 25.3361 | 25.3318 | 25.3287 | 25.3255 | 25.3087 | 25.2908 | 25.2697 | 25.2697 | 25.2697 | 25.2382 | 25.1887 | 25.1803 | 24.3108 | 24.3076 | 24.3066 | 24.3045 | 24.2939 | 24.2845 | 24.2718 | 24.2718 | 24.2718 | 24.2539 | 24.2255 | 24.2203 | 24.5139 | 24.5097 | 24.5055 | 24.5013 | 24.4813 | 24.4613 | 24.4371 | 24.4371 | 24.4371 | 24.3992 | 24.3413 | 24.3308
|  | PYESTOCK PRIMARY | HE |  |  |  |  | 25.3382 | 25.335 | 25.3318 | 25.3297 | 25.3276 | 25.3276 | 25.3266 | 25.3266 | 25.3266 | 25.3213 | 25.2803 | 20.9971 | 24.3108 | 24.3097 | 24.3076 | 24.3066 | 24.3055 | 24.3055 | 24.3045 | 24.3045 | 24.3045 | 24.3013 | 24.2782 | 24.2624 | 24.5161 | 24.5129 | 24.5097 | 24.5066 | 24.5045 | 24.5045 | 24.5034 | 24.5034 | 24.5034 | 24.4971 | 24.4487 | 24.4161
|  | PYESTOCK PRIMARY | CF |  |  |  |  | 25.3413 | 25.3413 | 25.3403 | 25.3392 | 25.3382 | 25.3371 | 25.3371 | 25.335 | 25.335 | 25.3318 | 25.3108 | 25.2908 | 24.3129 | 24.3129 | 24.3129 | 24.3118 | 24.3108 | 24.3108 | 24.3108 | 24.3097 | 24.3097 | 24.3076 | 24.2961 | 24.2834 | 24.5192 | 24.5192 | 24.5182 | 24.5182 | 24.5161 | 24.515 | 24.515 | 24.5129 | 24.5118 | 24.5087 | 24.4845 | 24.4603
MINETY GSP | TOOTHILL BSP | QUARRY ROAD PRIMARY | MINIMUM HEADROOM | SU 15334 83380 | NO | YES | 0 | 24.2011 | 23.9579 | 23.6989 | 23.4095 | 23.0463 | 22.1347 | 21.4895 | 20.8716 | 20.5053 | 18.5642 | 15.6758 | -4.0211 | 18.8158 | 18.3337 | 17.7526 | 17.1326 | 16.2484 | 15.3611 | 14.7326 | 14.1305 | 13.7705 | 11.8874 | 8.8168 | 5.5989 | 20.9589 | 20.6947 | 20.0368 | 19.3232 | 18.2337 | 17.1421 | 16.3842 | 15.6547 | 15.2442 | 13.0126 | 9.7211 | 6.5021
|  | QUARRY ROAD PRIMARY | EE |  |  |  |  | 24.3453 | 24.1453 | 23.9316 | 23.7074 | 23.4484 | 23.1768 | 22.4821 | 21.76 | 21.2916 | 19.8284 | 17.58 | 15.3411 | 19.0916 | 18.7232 | 18.2937 | 17.8084 | 17.1137 | 16.42 | 15.7021 | 15.0011 | 14.5442 | 13.1137 | 10.9 | 8.34 | 21.1137 | 20.9 | 20.6526 | 20.1042 | 19.2821 | 18.4305 | 17.5421 | 16.6747 | 16.1263 | 14.4421 | 11.8242 | 9.2442
|  | QUARRY ROAD PRIMARY | HT |  |  |  |  | 24.2011 | 23.9579 | 23.6989 | 23.4095 | 23.0463 | 22.1347 | 21.4895 | 20.8716 | 20.5053 | 18.5642 | 15.6758 | 12.8663 | 18.8158 | 18.3337 | 17.7526 | 17.1326 | 16.2484 | 15.3611 | 14.7326 | 14.1305 | 13.7705 | 11.8874 | 8.8168 | 5.5989 | 20.9589 | 20.6947 | 20.0368 | 19.3232 | 18.2337 | 17.1421 | 16.3842 | 15.6547 | 15.2442 | 13.0126 | 9.7211 | 6.5021
|  | QUARRY ROAD PRIMARY | HE |  |  |  |  | 24.5179 | 24.3684 | 24.2042 | 24.0263 | 23.8379 | 23.6221 | 23.3663 | 22.7484 | 22.4137 | 21.3989 | 19.6758 | -4.0211 | 19.4368 | 19.1695 | 18.8379 | 18.4474 | 17.8326 | 17.22 | 16.5684 | 15.9684 | 15.6421 | 14.6495 | 12.9979 | 11.1211 | 21.3011 | 21.1421 | 20.9632 | 20.7674 | 20.1032 | 19.3621 | 18.5484 | 17.8 | 17.4095 | 16.24 | 14.1242 | 12.0347
|  | QUARRY ROAD PRIMARY | CF |  |  |  |  | 24.6368 | 24.5526 | 24.4642 | 24.3726 | 24.2789 | 24.1821 | 24.0874 | 23.9937 | 23.9 | 23.3516 | 22.3821 | 21.3537 | 19.6211 | 19.48 | 19.3337 | 19.1842 | 19.0284 | 18.8705 | 18.6642 | 18.3495 | 18.0179 | 16.5537 | 15.6158 | 14.6242 | 21.4263 | 21.3368 | 21.2432 | 21.1474 | 21.0484 | 20.9463 | 20.8421 | 20.7063 | 20.3179 | 18.5305 | 17.3453 | 16.0579
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | QUEENSMEAD PRIMARY | MINIMUM HEADROOM | SU 87062 55683 | NO | YES | 0 | 11.9874 | 11.8495 | 11.7032 | 11.5526 | 11.3968 | 11.24 | 11.1021 | 10.9768 | 10.8621 | 9.4116 | 8.5379 | -15.0621 | 10.0811 | 9.8137 | 9.1326 | 8.8653 | 8.5695 | 8.3053 | 8.0684 | 7.8474 | 7.64 | 5.9768 | 4.9937 | 4.1042 | 10.5358 | 10.3958 | 9.7547 | 9.4947 | 9.2105 | 8.9537 | 8.7242 | 8.5105 | 8.3105 | 6.7368 | 5.8011 | 4.9579
|  | QUEENSMEAD PRIMARY | EE |  |  |  |  | 12.0747 | 11.9632 | 11.8442 | 11.7211 | 11.5926 | 11.4695 | 11.3516 | 11.2389 | 11.1389 | 10.1126 | 9.4537 | 8.8768 | 10.2632 | 10.0516 | 9.4242 | 9.2084 | 8.9621 | 8.7526 | 8.5568 | 8.3695 | 8.1979 | 6.7442 | 6 | 5.3411 | 10.6232 | 10.5116 | 10.0347 | 9.8253 | 9.5884 | 9.3853 | 9.1958 | 9.0137 | 8.8463 | 7.4758 | 6.7674 | 6.1453
|  | QUEENSMEAD PRIMARY | HT |  |  |  |  | 11.9874 | 11.8495 | 11.7032 | 11.5526 | 11.3968 | 11.24 | 11.1021 | 10.9768 | 10.8621 | 9.4116 | 8.5379 | 7.7537 | 10.0811 | 9.8137 | 9.1326 | 8.8653 | 8.5695 | 8.3053 | 8.0684 | 7.8474 | 7.64 | 5.9768 | 4.9937 | 4.1042 | 10.5358 | 10.3958 | 9.7547 | 9.4947 | 9.2105 | 8.9537 | 8.7242 | 8.5105 | 8.3105 | 6.7368 | 5.8011 | 4.9579
|  | QUEENSMEAD PRIMARY | HE |  |  |  |  | 12.1779 | 12.0979 | 12.0105 | 11.9158 | 11.8147 | 11.7179 | 11.6263 | 11.5421 | 11.4684 | 11.0263 | 10.6032 | -15.0621 | 10.4705 | 10.3537 | 9.7958 | 9.6442 | 9.4579 | 9.3074 | 9.1705 | 9.0421 | 8.9263 | 7.7547 | 7.2747 | 6.8663 | 10.7263 | 10.6463 | 10.3905 | 10.2432 | 10.0642 | 9.9168 | 9.7832 | 9.6589 | 9.5463 | 8.4432 | 7.9884 | 7.6042
|  | QUEENSMEAD PRIMARY | CF |  |  |  |  | 12.2484 | 12.2053 | 12.16 | 12.1137 | 12.0653 | 12.0168 | 11.9684 | 11.9211 | 11.8737 | 11.6611 | 11.5558 | 11.4968 | 10.5989 | 10.5421 | 10.3863 | 10.2979 | 10.1958 | 10.1042 | 10.0158 | 9.9295 | 9.8432 | 8.9842 | 8.6211 | 8.3284 | 10.7968 | 10.7537 | 10.7084 | 10.6621 | 10.6137 | 10.5653 | 10.5168 | 10.4695 | 10.4221 | 9.6137 | 9.2695 | 8.9947
MELKSHAM GSP | WEST GRAFTON BSP | RAMSBURY PRIMARY | MINIMUM HEADROOM | SU 27380 72108 | NO | YES | 0 | 8.9116 | 8.7105 | 8.5421 | 8.3937 | 8.2474 | 8.1011 | 7.9684 | 7.8453 | 7.7168 | 6.3684 | 6.2253 | 1.0495 | 7.8105 | 7.5937 | 7.4126 | 7.2558 | 7.1011 | 6.9453 | 6.8032 | 6.6716 | 6.5316 | 4.9516 | 4.8084 | 4.2547 | 8.0074 | 7.7905 | 7.6105 | 7.4526 | 7.2968 | 7.1411 | 6.9989 | 6.8674 | 6.7274 | 5.1463 | 5.0032 | 4.4495
|  | RAMSBURY PRIMARY | EE |  |  |  |  | 9.0168 | 8.8705 | 8.7168 | 8.5758 | 8.4389 | 8.3189 | 8.2095 | 8.1011 | 8.0042 | 6.3684 | 6.2253 | 6.1221 | 7.9253 | 7.7674 | 7.6011 | 7.4505 | 7.3063 | 7.1789 | 7.0621 | 6.9474 | 6.8432 | 4.9516 | 4.8084 | 4.7053 | 8.1211 | 7.9642 | 7.7979 | 7.6484 | 7.5032 | 7.3758 | 7.2579 | 7.1432 | 7.0389 | 5.1463 | 5.0032 | 4.9
|  | RAMSBURY PRIMARY | HT |  |  |  |  | 8.9116 | 8.7105 | 8.5421 | 8.3937 | 8.2474 | 8.1011 | 7.9684 | 7.8453 | 7.7168 | 7.0421 | 6.3632 | 5.6916 | 7.8105 | 7.5937 | 7.4126 | 7.2558 | 7.1011 | 6.9453 | 6.8032 | 6.6716 | 6.5316 | 5.7842 | 5.0189 | 4.2547 | 8.0074 | 7.7905 | 7.6105 | 7.4526 | 7.2968 | 7.1411 | 6.9989 | 6.8674 | 6.7274 | 5.98 | 5.2147 | 4.4495
|  | RAMSBURY PRIMARY | HE |  |  |  |  | 9.1484 | 9.04 | 8.9253 | 8.8189 | 8.7242 | 8.6368 | 8.5589 | 8.4853 | 8.4189 | 6.6484 | 6.5663 | 1.0495 | 8.0663 | 7.9484 | 7.8242 | 7.7116 | 7.6116 | 7.5189 | 7.4379 | 7.3611 | 7.2905 | 5.2316 | 5.1495 | 5.0989 | 8.2189 | 8.1442 | 8.0211 | 7.9084 | 7.8084 | 7.7168 | 7.6347 | 7.5579 | 7.4884 | 5.4263 | 5.3442 | 5.2937
|  | RAMSBURY PRIMARY | CF |  |  |  |  | 9.2284 | 9.1863 | 9.1421 | 9.0968 | 9.0453 | 8.9905 | 8.9368 | 8.8789 | 8.8168 | 8.5411 | 8.3168 | 8.0642 | 8.1505 | 8.1053 | 8.0589 | 8.0116 | 7.9558 | 7.8968 | 7.84 | 7.7768 | 7.7095 | 7.4116 | 7.16 | 6.8684 | 8.2632 | 8.24 | 8.2158 | 8.1905 | 8.1516 | 8.0937 | 8.0358 | 7.9737 | 7.9063 | 7.6084 | 7.3558 | 7.0632
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | RATFYN PRIMARY | MINIMUM HEADROOM | SU 16215 42533 | NO | YES | 0 | 27.2042 | 26.9516 | 26.6842 | 26.3611 | 25.9074 | 25.4505 | 25.0263 | 24.6358 | 24.2116 | 21.9211 | 19.5295 | 5.4821 | 23.7853 | 23.2495 | 22.6558 | 22.1621 | 21.6653 | 21.1737 | 20.7221 | 20.3053 | 19.8463 | 17.3253 | 14.6484 | 11.9726 | 24.5674 | 24.0189 | 23.4253 | 22.9295 | 22.4316 | 21.9389 | 21.4832 | 21.0653 | 20.6042 | 18.0642 | 15.3674 | 12.6832
|  | RATFYN PRIMARY | EE |  |  |  |  | 27.3484 | 27.14 | 26.9179 | 26.6863 | 26.44 | 26.1379 | 25.7842 | 25.4411 | 25.1211 | 23.3821 | 21.4758 | 19.5916 | 24.0863 | 23.6916 | 23.2347 | 22.78 | 22.34 | 21.9411 | 21.5537 | 21.1821 | 20.8453 | 18.9547 | 16.8316 | 14.6832 | 24.7368 | 24.4695 | 24.0032 | 23.5484 | 23.1074 | 22.7042 | 22.3137 | 21.9411 | 21.5989 | 19.6842 | 17.5326 | 15.3737
|  | RATFYN PRIMARY | HT |  |  |  |  | 27.2042 | 26.9516 | 26.6842 | 26.3611 | 25.9074 | 25.4505 | 25.0263 | 24.6358 | 24.2116 | 21.9211 | 19.5295 | 17.1747 | 23.7853 | 23.2495 | 22.6558 | 22.1621 | 21.6653 | 21.1737 | 20.7221 | 20.3053 | 19.8463 | 17.3253 | 14.6484 | 11.9726 | 24.5674 | 24.0189 | 23.4253 | 22.9295 | 22.4316 | 21.9389 | 21.4832 | 21.0653 | 20.6042 | 18.0642 | 15.3674 | 12.6832
|  | RATFYN PRIMARY | HE |  |  |  |  | 27.5484 | 27.4021 | 27.24 | 27.0663 | 26.8758 | 26.6926 | 26.52 | 26.3589 | 26.2179 | 25.2126 | 23.8221 | 5.4821 | 24.4495 | 24.2263 | 23.9084 | 23.5989 | 23.2853 | 22.9968 | 22.7232 | 22.4684 | 22.2453 | 20.9232 | 19.3432 | 17.6537 | 24.9516 | 24.7968 | 24.6232 | 24.3747 | 24.0537 | 23.7632 | 23.4874 | 23.2326 | 23.0063 | 21.6737 | 20.0853 | 18.3895
|  | RATFYN PRIMARY | CF |  |  |  |  | 27.6874 | 27.6126 | 27.5337 | 27.4526 | 27.3653 | 27.2768 | 27.1905 | 27.1042 | 27.0189 | 26.6347 | 26.0021 | 25.0853 | 24.6021 | 24.5179 | 24.4305 | 24.3063 | 24.1347 | 23.9526 | 23.7853 | 23.6168 | 23.4368 | 22.5937 | 21.7221 | 20.6653 | 25.0979 | 25.0179 | 24.9347 | 24.8495 | 24.7558 | 24.66 | 24.5684 | 24.3874 | 24.2032 | 23.3547 | 22.4811 | 21.4189
BRAMLEY (BASI) GSP | READING BSP | READING PRIMARY | MINIMUM HEADROOM | SU 74591 73788 | NO | YES | 0 | 50.6053 | 50.0021 | 49.3453 | 48.6958 | 48.0158 | 47.0011 | 45.8863 | 44.8642 | 43.9242 | 39.9074 | 36.0179 | -3.0189 | 42.2937 | 41.0474 | 39.4758 | 38.2316 | 36.8326 | 35.5253 | 34.3137 | 33.2021 | 32.1789 | 27.8021 | 23.4832 | 19.3484 | 44.2063 | 42.9211 | 41.3484 | 40.1042 | 38.7032 | 37.3979 | 36.1842 | 35.0716 | 34.0484 | 29.6716 | 25.3484 | 21.2116
|  | READING PRIMARY | EE |  |  |  |  | 50.9674 | 50.48 | 49.9411 | 49.4032 | 48.8421 | 48.3011 | 47.7905 | 47.0947 | 46.3516 | 43.4558 | 40.64 | 37.9926 | 42.9768 | 42.0368 | 40.7442 | 39.7389 | 38.5874 | 37.5221 | 36.5232 | 35.6463 | 34.8453 | 31.72 | 28.5937 | 25.6147 | 44.8937 | 43.9337 | 42.6168 | 41.6116 | 40.4589 | 39.3937 | 38.3926 | 37.5158 | 36.7137 | 33.5884 | 30.4558 | 27.4737
|  | READING PRIMARY | HT |  |  |  |  | 50.6053 | 50.0021 | 49.3453 | 48.6958 | 48.0158 | 47.0011 | 45.8863 | 44.8642 | 43.9242 | 39.9074 | 36.0179 | 32.3326 | 42.2937 | 41.0474 | 39.4758 | 38.2316 | 36.8326 | 35.5253 | 34.3137 | 33.2021 | 32.1789 | 27.8021 | 23.4832 | 19.3484 | 44.2063 | 42.9211 | 41.3484 | 40.1042 | 38.7032 | 37.3979 | 36.1842 | 35.0716 | 34.0484 | 29.6716 | 25.3484 | 21.2116
|  | READING PRIMARY | HE |  |  |  |  | 51.4084 | 51.0811 | 50.6789 | 50.2726 | 49.8305 | 49.4105 | 49.0158 | 48.6537 | 48.34 | 47.16 | 45.3053 | -3.0189 | 43.6189 | 43.2 | 42.2274 | 41.5095 | 40.6011 | 39.7768 | 39.0105 | 38.3853 | 37.8137 | 35.7274 | 33.6558 | 31.66 | 45.3474 | 45.0147 | 44.1232 | 43.3832 | 42.4716 | 41.6463 | 40.8811 | 40.2526 | 39.6821 | 37.5853 | 35.5084 | 33.5105
|  | READING PRIMARY | CF |  |  |  |  | 51.6989 | 51.5305 | 51.3484 | 51.1474 | 50.9337 | 50.7168 | 50.5074 | 50.3053 | 50.1032 | 49.2095 | 48.7326 | 48.3379 | 43.9095 | 43.7411 | 43.4874 | 43.0695 | 42.5863 | 42.0916 | 41.6242 | 41.22 | 40.8421 | 39.1895 | 37.9684 | 36.9105 | 45.6389 | 45.4705 | 45.2842 | 45.0095 | 44.4947 | 43.9684 | 43.4958 | 43.0916 | 42.7137 | 41.06 | 39.8389 | 38.7789
FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN PRIMARY | MINIMUM HEADROOM | SU 71540 74122 | NO | YES | 0 | 99.7084 | 99.4653 | 99.1863 | 97.3653 | 94.8558 | 92.4326 | 92.2074 | 91.9916 | 91.7947 | 87.0811 | 86.3411 | 40.68 | 88.9158 | 88.2789 | 87.1726 | 85.0632 | 82.1495 | 79.2895 | 79.0684 | 78.8558 | 78.6632 | 72.92 | 72.0884 | 71.4179 | 91.2916 | 90.6674 | 89.5926 | 87.5516 | 84.6589 | 81.7768 | 81.5505 | 81.3337 | 81.1368 | 75.4579 | 74.6284 | 73.9589
|  | READING TOWN PRIMARY | EE |  |  |  |  | 99.8505 | 99.6537 | 99.4347 | 97.8947 | 95.6368 | 92.4326 | 92.2074 | 91.9916 | 91.7947 | 88.9368 | 87.5242 | 86.1768 | 89.2263 | 88.6853 | 87.6737 | 85.6558 | 83.0326 | 79.2895 | 79.0684 | 78.8558 | 78.6632 | 75.44 | 73.8895 | 72.3937 | 91.5842 | 91.0516 | 90.0663 | 88.1126 | 85.5179 | 81.7768 | 81.5505 | 81.3337 | 81.1368 | 77.8947 | 76.3211 | 74.8032
|  | READING TOWN PRIMARY | HT |  |  |  |  | 99.7084 | 99.4653 | 99.1863 | 97.3653 | 94.8558 | 94.5705 | 94.3158 | 94.0821 | 93.8642 | 90.7274 | 88.8895 | 87.1284 | 88.9158 | 88.2789 | 87.1726 | 85.0632 | 82.1495 | 81.8653 | 81.6126 | 81.38 | 81.1632 | 77.6274 | 75.5916 | 73.6232 | 91.2916 | 90.6674 | 89.5926 | 87.5516 | 84.6589 | 84.3726 | 84.1179 | 83.8832 | 83.6653 | 80.1284 | 78.0863 | 76.1116
|  | READING TOWN PRIMARY | HE |  |  |  |  | 100.0053 | 99.8495 | 99.6789 | 98.5411 | 96.3547 | 93.2221 | 93.0453 | 92.88 | 92.7368 | 90.3621 | 89.4768 | 40.68 | 89.5958 | 89.1653 | 88.2589 | 86.3453 | 83.7979 | 80.1263 | 79.9505 | 79.7853 | 79.6421 | 76.9263 | 75.9379 | 75.0074 | 91.96 | 91.54 | 90.6611 | 88.8137 | 86.3137 | 82.6495 | 82.4737 | 82.3074 | 82.1653 | 79.4516 | 78.4621 | 77.5305
|  | READING TOWN PRIMARY | CF |  |  |  |  | 100.1063 | 100.0105 | 99.9116 | 99.8084 | 99.7021 | 99.0347 | 97.8042 | 95.8516 | 94.0242 | 87.0811 | 86.3411 | 85.7537 | 90.8211 | 90.5484 | 90.0495 | 89.1453 | 88.1716 | 86.9095 | 85.4747 | 83.1853 | 81.0432 | 72.92 | 72.0884 | 71.4179 | 93.1421 | 92.8768 | 92.3926 | 91.52 | 90.5789 | 89.3621 | 87.9768 | 85.7053 | 83.5674 | 75.4579 | 74.6284 | 73.9589
MANNINGTON GSP | REDHILL BSP | REDHILL PRIMARY | MINIMUM HEADROOM | SZ 08512 96149 | NO | YES | 0 | 42.9777 | 41.964 | 40.9314 | 40.0324 | 39.1987 | 38.3061 | 37.4461 | 36.5735 | 35.7356 | 32.0314 | 28.6661 | 0.32295 | 35.5587 | 34.8114 | 33.6851 | 32.7166 | 31.8303 | 30.8724 | 29.9429 | 28.9903 | 28.0756 | 23.9987 | 20.2503 | 16.8008 | 37.0935 | 35.8493 | 34.7229 | 33.7545 | 32.8672 | 31.9093 | 30.9787 | 30.0261 | 29.1103 | 25.0303 | 21.2777 | 17.8251
|  | REDHILL PRIMARY | EE |  |  |  |  | 43.6461 | 42.6861 | 41.8251 | 41.0808 | 40.4208 | 39.7198 | 39.0429 | 38.3935 | 37.7072 | 34.8272 | 32.2345 | 29.9282 | 36.1556 | 35.104 | 34.6535 | 33.8535 | 33.1545 | 32.4029 | 31.6777 | 30.9829 | 30.2345 | 27.0703 | 24.1756 | 21.5724 | 37.6956 | 36.6335 | 35.6924 | 34.8914 | 34.1914 | 33.4398 | 32.7135 | 32.0177 | 31.2693 | 28.0998 | 25.1998 | 22.5956
|  | REDHILL PRIMARY | HT |  |  |  |  | 43.0914 | 41.964 | 40.9314 | 40.0324 | 39.1987 | 38.3061 | 37.4461 | 36.5735 | 35.7356 | 32.0314 | 28.6661 | 25.5924 | 35.5587 | 34.8114 | 33.6851 | 32.7166 | 31.8303 | 30.8724 | 29.9429 | 28.9903 | 28.0756 | 23.9987 | 20.2503 | 16.8008 | 37.0935 | 35.8493 | 34.7229 | 33.7545 | 32.8672 | 31.9093 | 30.9787 | 30.0261 | 29.1103 | 25.0303 | 21.2777 | 17.8251
|  | REDHILL PRIMARY | HE |  |  |  |  | 44.3787 | 43.644 | 42.9998 | 42.4651 | 41.9945 | 41.4798 | 40.9956 | 40.5166 | 40.0051 | 37.9787 | 36.1808 | 0.32295 | 36.9451 | 36.1377 | 35.9314 | 35.3577 | 34.8629 | 34.3156 | 33.7987 | 33.2872 | 32.7282 | 30.4935 | 28.4672 | 26.6756 | 38.4924 | 37.6756 | 36.9693 | 36.3956 | 35.9019 | 35.3524 | 34.8366 | 34.324 | 33.7651 | 31.5282 | 29.4998 | 27.7072
|  | REDHILL PRIMARY | CF |  |  |  |  | 42.9777 | 44.6082 | 43.3672 | 43.0872 | 42.8093 | 42.4956 | 42.1724 | 41.8798 | 41.5956 | 40.3851 | 39.1608 | 38.1082 | 37.4156 | 37.1914 | 35.2229 | 35.6156 | 35.3145 | 34.9724 | 34.6208 | 34.3029 | 33.9966 | 32.6893 | 31.3114 | 30.1072 | 38.844 | 38.7408 | 36.7756 | 36.4703 | 36.1703 | 35.8282 | 35.4756 | 35.1577 | 34.8503 | 33.5429 | 32.1629 | 30.9587
CHICKERELL GSP | CHICKERELL BSP | REDLANDS PRIMARY | MINIMUM HEADROOM | SY 67131 82321 | NO | YES | 0.031579 | 15.9774 | 15.17 | 14.2784 | 13.3089 | 12.4489 | 11.5974 | 10.8889 | 10.3016 | 9.7468 | 7.8058 | 5.7795 | -7.9595 | 13.3711 | 12.4574 | 11.4468 | 10.3426 | 9.3753 | 8.4195 | 7.6279 | 6.9774 | 6.3616 | 4.2542 | 2.0216 | -0.24158 | 13.9268 | 13.0142 | 12.0026 | 10.8984 | 9.93 | 8.9721 | 8.1795 | 7.5268 | 6.9089 | 4.79 | 2.5458 | 0.27632
|  | REDLANDS PRIMARY | EE |  |  |  |  | 16.3142 | 15.6079 | 14.8184 | 13.9447 | 13.1763 | 12.4258 | 11.79 | 11.2637 | 10.7679 | 9.2174 | 7.7068 | 6.1889 | 13.7426 | 12.9405 | 12.0405 | 11.0437 | 10.1753 | 9.3279 | 8.6163 | 8.0363 | 7.4858 | 5.8079 | 4.1416 | 2.4374 | 14.2984 | 13.4974 | 12.5963 | 11.5984 | 10.7289 | 9.8795 | 9.1668 | 8.5837 | 8.0321 | 6.3374 | 4.6542 | 2.9426
|  | REDLANDS PRIMARY | HT |  |  |  |  | 15.9774 | 15.17 | 14.2784 | 13.3089 | 12.4489 | 11.5974 | 10.8889 | 10.3016 | 9.7468 | 7.8058 | 5.7795 | 3.7574 | 13.3711 | 12.4574 | 11.4468 | 10.3426 | 9.3753 | 8.4195 | 7.6279 | 6.9774 | 6.3616 | 4.2542 | 2.0216 | -0.24158 | 13.9268 | 13.0142 | 12.0026 | 10.8984 | 9.93 | 8.9721 | 8.1795 | 7.5268 | 6.9089 | 4.79 | 2.5458 | 0.27632
|  | REDLANDS PRIMARY | HE |  |  |  |  | 16.7553 | 16.1995 | 15.5426 | 14.7953 | 14.1468 | 13.5142 | 12.9953 | 12.5889 | 12.2111 | 11.2384 | 10.2932 | -7.9595 | 14.2395 | 13.5921 | 12.8395 | 11.9805 | 11.2437 | 10.5258 | 9.9416 | 9.4911 | 9.0689 | 8.0174 | 6.9511 | 5.7795 | 14.7963 | 14.1489 | 13.3953 | 12.5363 | 11.7984 | 11.0795 | 10.4942 | 10.0426 | 9.6195 | 8.5616 | 7.4889 | 6.3121
|  | REDLANDS PRIMARY | CF |  |  |  |  | 17.1921 | 16.9079 | 16.5984 | 16.2489 | 15.9426 | 15.6216 | 15.3342 | 15.0879 | 14.8353 | 14.0142 | 13.3479 | 12.6847 | 14.7563 | 14.4174 | 14.0458 | 13.6426 | 13.2953 | 12.9279 | 12.6047 | 12.3289 | 12.0458 | 11.1489 | 10.3974 | 9.6289 | 15.1658 | 14.9742 | 14.6026 | 14.1984 | 13.8511 | 13.4847 | 13.1595 | 12.8837 | 12.5995 | 11.7005 | 10.9468 | 10.1742
MANNINGTON GSP | SALISBURY BSP | REDLYNCH PRIMARY | MINIMUM HEADROOM | SU 19073 20576 | NO | YES | 0 | 16.9189 | 16.5853 | 16.2495 | 15.9074 | 15.5305 | 15.1074 | 14.3789 | 11.4737 | 11.2611 | 9.5526 | 7.5242 | 0.54 | 14.0084 | 13.6526 | 13.2926 | 12.9295 | 12.5411 | 12.1 | 11.2926 | 7.9105 | 7.7116 | 5.9611 | 3.8274 | 3.1116 | 15.1105 | 14.76 | 14.4032 | 14.0442 | 13.6505 | 13.2063 | 12.4116 | 9.0232 | 8.8084 | 6.9642 | 4.72 | 3.9589
|  | REDLYNCH PRIMARY | EE |  |  |  |  | 17.1505 | 16.8863 | 16.6147 | 16.3368 | 16.0211 | 15.7011 | 15.3863 | 15.0737 | 14.7758 | 12.6989 | 10.6158 | 9.4684 | 14.2579 | 13.9768 | 13.6895 | 13.3958 | 13.0747 | 12.7516 | 12.4368 | 12.1274 | 11.8326 | 9.6884 | 7.5295 | 6.2916 | 15.3579 | 15.0789 | 14.7926 | 14.5021 | 14.1737 | 13.8421 | 13.5168 | 13.1947 | 12.8863 | 10.6211 | 8.3147 | 7.0305
|  | REDLYNCH PRIMARY | HT |  |  |  |  | 16.9189 | 16.5853 | 16.2495 | 15.9074 | 15.5305 | 15.1074 | 14.3789 | 11.4737 | 11.2611 | 9.5526 | 7.5242 | 6.8021 | 14.0084 | 13.6526 | 13.2926 | 12.9295 | 12.5411 | 12.1 | 11.2926 | 7.9105 | 7.7116 | 5.9611 | 3.8274 | 3.1116 | 15.1105 | 14.76 | 14.4032 | 14.0442 | 13.6505 | 13.2063 | 12.4116 | 9.0232 | 8.8084 | 6.9642 | 4.72 | 3.9589
|  | REDLYNCH PRIMARY | HE |  |  |  |  | 17.4179 | 17.2863 | 17.1084 | 16.92 | 16.6947 | 16.4789 | 16.2737 | 16.0737 | 15.8989 | 14.1926 | 12.9053 | 0.54 | 14.5842 | 14.4074 | 14.22 | 14.0221 | 13.7958 | 13.5789 | 13.3716 | 13.1716 | 12.9979 | 11.1347 | 9.7179 | 8.7453 | 15.6811 | 15.5053 | 15.32 | 15.1232 | 14.8905 | 14.6674 | 14.4547 | 14.2495 | 14.0684 | 12.1905 | 10.7316 | 9.7211
|  | REDLYNCH PRIMARY | CF |  |  |  |  | 17.5211 | 17.4695 | 17.4137 | 17.3326 | 17.2053 | 17.0716 | 16.9495 | 16.8337 | 16.7232 | 16.1853 | 15.6137 | 14.9863 | 14.7642 | 14.6653 | 14.5611 | 14.4537 | 14.3232 | 14.1842 | 14.0589 | 13.94 | 13.8253 | 13.2705 | 12.66 | 11.9737 | 15.8632 | 15.7632 | 15.6589 | 15.5526 | 15.4179 | 15.2779 | 15.1495 | 15.0284 | 14.9116 | 14.3474 | 13.7316 | 13.04
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | REGENTS PARK PRIMARY | MINIMUM HEADROOM | SU 39267 13050 | NO | YES | 0.16842 | 34.7505 | 34.6116 | 34.4653 | 34.3116 | 34.1526 | 33.9926 | 33.8505 | 33.7211 | 33.6011 | 32.5495 | 31.3747 | -23.5611 | 30.8621 | 30.6432 | 30.3768 | 30.0747 | 29.7947 | 29.5242 | 29.2737 | 29.0389 | 28.7747 | 27.2063 | 25.8884 | 24.6737 | 31.5263 | 31.3874 | 31.1684 | 30.8663 | 30.5968 | 30.3337 | 30.0905 | 29.8632 | 29.6095 | 28.12 | 26.8263 | 25.6116
|  | REGENTS PARK PRIMARY | EE |  |  |  |  | 34.8379 | 34.7263 | 34.6074 | 34.4811 | 34.3505 | 34.2242 | 34.1032 | 33.9853 | 33.88 | 33.4126 | 32.5021 | 31.6811 | 30.9747 | 30.8389 | 30.6411 | 30.4263 | 30.1611 | 29.8705 | 29.6568 | 29.4547 | 29.2737 | 28.1547 | 27.1295 | 26.1979 | 31.6137 | 31.5021 | 31.3832 | 31.2253 | 30.9505 | 30.6716 | 30.4653 | 30.2684 | 30.0937 | 29.0274 | 28.0568 | 27.1358
|  | REGENTS PARK PRIMARY | HT |  |  |  |  | 34.7505 | 34.6116 | 34.4653 | 34.3116 | 34.1526 | 33.9926 | 33.8505 | 33.7211 | 33.6011 | 32.5495 | 31.3747 | 30.2989 | 30.8621 | 30.6432 | 30.3768 | 30.0747 | 29.7947 | 29.5242 | 29.2737 | 29.0389 | 28.7747 | 27.2063 | 25.8884 | 24.6737 | 31.5263 | 31.3874 | 31.1684 | 30.8663 | 30.5968 | 30.3337 | 30.0905 | 29.8632 | 29.6095 | 28.12 | 26.8263 | 25.6116
|  | REGENTS PARK PRIMARY | HE |  |  |  |  | 34.9295 | 34.8442 | 34.7505 | 34.6495 | 34.5421 | 34.4389 | 34.3421 | 34.2516 | 34.1726 | 33.9053 | 33.7432 | -23.5611 | 31.0821 | 30.9905 | 30.8863 | 30.7632 | 30.5779 | 30.3768 | 30.24 | 30.1042 | 29.9821 | 29.2853 | 28.5832 | 27.9358 | 31.7053 | 31.62 | 31.5263 | 31.4253 | 31.3179 | 31.1747 | 31.0284 | 30.8905 | 30.7705 | 30.1063 | 29.4432 | 28.8358
|  | REGENTS PARK PRIMARY | CF |  |  |  |  | 34.9989 | 34.9516 | 34.9011 | 34.8505 | 34.7968 | 34.7432 | 34.6895 | 34.6368 | 34.5842 | 34.3495 | 34.2305 | 34.1642 | 31.1579 | 31.1063 | 31.0505 | 30.9947 | 30.9358 | 30.8768 | 30.8105 | 30.7442 | 30.6642 | 30.24 | 29.7832 | 29.3589 | 31.7747 | 31.7274 | 31.6768 | 31.6263 | 31.5726 | 31.5189 | 31.4653 | 31.4126 | 31.36 | 31.0274 | 30.5905 | 30.1926
COWLEY GSP | WITNEY BSP | RISSINGTON PRIMARY | MINIMUM HEADROOM | SP 19225 19563 | YES | YES | 1.0842 | 12.6805 | 12.5468 | 12.4058 | 12.2616 | 12.0805 | 11.7616 | 11.4553 | 11.1626 | 10.9089 | 9.3774 | 7.7384 | -0.26263 | 10.8058 | 10.5963 | 10.3626 | 10.1089 | 9.8311 | 9.5574 | 9.2984 | 9.0521 | 8.8384 | 7.6047 | 6.2437 | 4.8089 | 10.5879 | 10.3995 | 10.1195 | 9.8237 | 9.4889 | 9.1584 | 8.8332 | 8.5226 | 8.2553 | 6.5921 | 4.7689 | 3.1974
|  | RISSINGTON PRIMARY | EE |  |  |  |  | 12.7553 | 12.6458 | 12.5258 | 12.4037 | 12.2605 | 12.1153 | 11.9742 | 11.7384 | 11.5289 | 10.2174 | 8.7847 | 7.6563 | 10.9353 | 10.77 | 10.5889 | 10.4047 | 10.1911 | 9.9742 | 9.7584 | 9.5489 | 9.3732 | 8.3416 | 7.2532 | 6.2658 | 10.6711 | 10.5532 | 10.3984 | 10.1763 | 9.9289 | 9.6668 | 9.4047 | 9.1468 | 8.9311 | 7.5342 | 5.9574 | 4.6805
|  | RISSINGTON PRIMARY | HT |  |  |  |  | 12.6805 | 12.5468 | 12.4058 | 12.2616 | 12.0805 | 11.7616 | 11.4553 | 11.1626 | 10.9089 | 9.3774 | 7.7384 | 6.35 | 10.8058 | 10.5963 | 10.3626 | 10.1089 | 9.8311 | 9.5574 | 9.2984 | 9.0521 | 8.8384 | 7.6047 | 6.2437 | 4.8089 | 10.5879 | 10.3995 | 10.1195 | 9.8237 | 9.4889 | 9.1584 | 8.8332 | 8.5226 | 8.2553 | 6.5921 | 4.7689 | 3.1974
|  | RISSINGTON PRIMARY | HE |  |  |  |  | 12.8616 | 12.7847 | 12.6984 | 12.6058 | 12.4963 | 12.39 | 12.29 | 12.1942 | 12.1089 | 11.3658 | 10.3753 | -0.26263 | 11.1089 | 10.9974 | 10.8668 | 10.7321 | 10.5784 | 10.4268 | 10.2753 | 10.1226 | 10.0058 | 9.2774 | 8.5079 | 7.8247 | 10.7879 | 10.7058 | 10.6121 | 10.5132 | 10.3932 | 10.2068 | 10.0216 | 9.8426 | 9.7037 | 8.7384 | 7.6405 | 6.6332
|  | RISSINGTON PRIMARY | CF |  |  |  |  | 12.9332 | 12.8932 | 12.8511 | 12.8079 | 12.7553 | 12.7037 | 12.6521 | 12.6016 | 12.5532 | 12.3247 | 11.8142 | 11.2563 | 11.1932 | 11.15 | 11.0837 | 11.0184 | 10.9447 | 10.8668 | 10.79 | 10.7142 | 10.6468 | 10.1784 | 9.6889 | 9.2616 | 10.8605 | 10.8205 | 10.7753 | 10.7279 | 10.6732 | 10.6163 | 10.5605 | 10.5058 | 10.4553 | 9.8626 | 9.1889 | 8.5732
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | RIVERSIDE PRIMARY | MINIMUM HEADROOM | SU 47846 67187 | NO | YES | 0.025263 | 23.0518 | 22.9571 | 22.856 | 22.4602 | 22.0865 | 21.6634 | 21.2644 | 21.1118 | 20.9728 | 20.3823 | 19.7234 | 2.1202 | 19.9223 | 19.5844 | 19.2349 | 18.8118 | 18.4107 | 17.9307 | 17.4771 | 17.3139 | 17.1644 | 16.5549 | 15.8244 | 15.1139 | 20.6476 | 20.3402 | 19.9634 | 19.5055 | 19.0844 | 18.6055 | 18.1518 | 17.9886 | 17.8402 | 17.236 | 16.5065 | 15.7971
|  | RIVERSIDE PRIMARY | EE |  |  |  |  | 23.1065 | 23.0276 | 22.9444 | 22.6707 | 22.3276 | 21.9392 | 21.5655 | 21.4339 | 21.316 | 20.8749 | 20.3749 | 19.8865 | 20.0371 | 19.7339 | 19.4202 | 19.0297 | 18.6697 | 18.2307 | 17.8055 | 17.6644 | 17.5392 | 17.0939 | 16.5392 | 15.9886 | 20.7065 | 20.4981 | 20.1592 | 19.736 | 19.3476 | 18.9055 | 18.4802 | 18.3392 | 18.2139 | 17.7749 | 17.2202 | 16.6707
|  | RIVERSIDE PRIMARY | HT |  |  |  |  | 23.0518 | 22.9571 | 22.856 | 22.4602 | 22.0865 | 21.6634 | 21.2644 | 21.1118 | 20.9728 | 20.3823 | 19.7234 | 19.0886 | 19.9223 | 19.5844 | 19.2349 | 18.8118 | 18.4107 | 17.9307 | 17.4771 | 17.3139 | 17.1644 | 16.5549 | 15.8244 | 15.1139 | 20.6476 | 20.3402 | 19.9634 | 19.5055 | 19.0844 | 18.6055 | 18.1518 | 17.9886 | 17.8402 | 17.236 | 16.5065 | 15.7971
|  | RIVERSIDE PRIMARY | HE |  |  |  |  | 23.1676 | 23.1076 | 23.0392 | 22.9286 | 22.6213 | 22.2697 | 21.9328 | 21.8381 | 21.7602 | 21.4002 | 21.0928 | 2.1202 | 20.1802 | 19.9213 | 19.6465 | 19.2971 | 18.9739 | 18.5949 | 18.2097 | 18.1097 | 18.0276 | 17.6118 | 17.2697 | 16.9265 | 20.7739 | 20.696 | 20.3992 | 20.0202 | 19.6707 | 19.2686 | 18.8844 | 18.7844 | 18.7023 | 18.2813 | 17.9392 | 17.5971
|  | RIVERSIDE PRIMARY | CF |  |  |  |  | 23.2118 | 23.1749 | 23.1371 | 23.0971 | 23.0571 | 23.0149 | 22.9571 | 22.8928 | 22.8286 | 22.5255 | 22.2855 | 22.0707 | 20.3002 | 20.1602 | 20.0202 | 19.8518 | 19.7023 | 19.5171 | 19.3265 | 19.2602 | 19.1949 | 18.8834 | 18.6339 | 18.4044 | 20.8234 | 20.7792 | 20.7339 | 20.6202 | 20.4592 | 20.2581 | 20.0528 | 19.9834 | 19.9149 | 19.5897 | 19.3234 | 19.0781
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE PRIMARY | MINIMUM HEADROOM | SU 11617 17810 | YES | YES | 0 | 4.0916 | 4.0368 | 3.9811 | 3.9263 | 3.8716 | 3.8179 | 3.7695 | 3.7242 | 3.6832 | 3.4747 | 3.2632 | 0.93684 | 3.9084 | 3.8526 | 3.7947 | 3.7379 | 3.6811 | 3.6263 | 3.5758 | 3.5295 | 3.4874 | 3.2705 | 3.0505 | 2.8305 | 3.8926 | 3.8358 | 3.7779 | 3.72 | 3.6632 | 3.6084 | 3.5579 | 3.5105 | 3.4684 | 3.2495 | 3.0263 | 2.8105
|  | ROCKBOURNE PRIMARY | EE |  |  |  |  | 4.1316 | 4.0895 | 4.0453 | 4.0021 | 3.9579 | 3.9147 | 3.8758 | 3.8368 | 3.8032 | 3.6484 | 3.4958 | 3.3547 | 3.9505 | 3.9063 | 3.8611 | 3.8168 | 3.7716 | 3.7274 | 3.6874 | 3.6463 | 3.6126 | 3.4505 | 3.2905 | 3.1432 | 3.9347 | 3.8905 | 3.8453 | 3.8 | 3.7547 | 3.7095 | 3.6695 | 3.6284 | 3.5947 | 3.4316 | 3.2695 | 3.12
|  | ROCKBOURNE PRIMARY | HT |  |  |  |  | 4.0916 | 4.0368 | 3.9811 | 3.9263 | 3.8716 | 3.8179 | 3.7695 | 3.7242 | 3.6832 | 3.4747 | 3.2632 | 3.0589 | 3.9084 | 3.8526 | 3.7947 | 3.7379 | 3.6811 | 3.6263 | 3.5758 | 3.5295 | 3.4874 | 3.2705 | 3.0505 | 2.8305 | 3.8926 | 3.8358 | 3.7779 | 3.72 | 3.6632 | 3.6084 | 3.5579 | 3.5105 | 3.4684 | 3.2495 | 3.0263 | 2.8105
|  | ROCKBOURNE PRIMARY | HE |  |  |  |  | 4.1663 | 4.1495 | 4.1242 | 4.0958 | 4.0663 | 4.0368 | 4.0084 | 3.9832 | 3.9589 | 3.8632 | 3.7621 | 0.93684 | 3.9874 | 3.9695 | 3.9442 | 3.9147 | 3.8842 | 3.8537 | 3.8253 | 3.7989 | 3.7747 | 3.6747 | 3.5674 | 3.4684 | 3.9716 | 3.9537 | 3.9284 | 3.8989 | 3.8684 | 3.8379 | 3.8095 | 3.7832 | 3.7579 | 3.6568 | 3.5484 | 3.4484
|  | ROCKBOURNE PRIMARY | CF |  |  |  |  | 4.1853 | 4.1768 | 4.1674 | 4.1558 | 4.1442 | 4.1305 | 4.1158 | 4.1 | 4.0842 | 4.0116 | 3.9453 | 3.8789 | 4.0063 | 3.9979 | 3.9884 | 3.9758 | 3.9642 | 3.9505 | 3.9347 | 3.9179 | 3.9021 | 3.8274 | 3.7558 | 3.6853 | 3.9905 | 3.9821 | 3.9726 | 3.96 | 3.9484 | 3.9347 | 3.9189 | 3.9021 | 3.8863 | 3.8105 | 3.7379 | 3.6663
NURSLING GSP | ROWNHAMS BSP | ROMSEY PRIMARY | MINIMUM HEADROOM | SU 36092 21110 | NO | YES | 0 | 14.2863 | 44.0042 | 44.0253 | 43.2232 | 42.3358 | 41.1495 | 40.0042 | 38.8895 | 37.7979 | 33.68 | 31.2421 | 11.9905 | 9.88 | 39.2316 | 38.4716 | 37.5747 | 36.5821 | 35.2379 | 33.9337 | 32.6642 | 31.4168 | 26.7337 | 23.9958 | 21.4411 | 10.4179 | 39.8621 | 39.2674 | 38.3716 | 37.3768 | 36.0305 | 34.7263 | 33.4537 | 32.2042 | 27.5084 | 24.7579 | 22.1979
|  | ROMSEY PRIMARY | EE |  |  |  |  | 14.4516 | 44.2211 | 44.6368 | 43.8221 | 42.9674 | 41.8579 | 40.7768 | 39.7032 | 38.66 | 34.98 | 33.0074 | 31.2189 | 10.2189 | 39.7453 | 39.1484 | 38.2305 | 37.2674 | 36.0011 | 34.7705 | 33.5463 | 32.3526 | 28.1611 | 25.9474 | 23.9084 | 10.7126 | 40.3 | 39.9453 | 39.0263 | 38.0621 | 36.7937 | 35.5611 | 34.3337 | 33.1379 | 28.9295 | 26.6979 | 24.6526
|  | ROMSEY PRIMARY | HT |  |  |  |  | 14.2863 | 44.0042 | 44.0253 | 43.2232 | 42.3358 | 41.1495 | 40.0042 | 38.8895 | 37.7979 | 33.68 | 31.2421 | 28.9905 | 9.88 | 39.2316 | 38.4716 | 37.5747 | 36.5821 | 35.2379 | 33.9337 | 32.6642 | 31.4168 | 26.7337 | 23.9958 | 21.4411 | 10.4179 | 39.8621 | 39.2674 | 38.3716 | 37.3768 | 36.0305 | 34.7263 | 33.4537 | 32.2042 | 27.5084 | 24.7579 | 22.1979
|  | ROMSEY PRIMARY | HE |  |  |  |  | 14.6611 | 44.4979 | 44.3084 | 44.0863 | 43.8168 | 42.8158 | 41.8411 | 40.8811 | 39.9432 | 36.7768 | 35.3095 | 11.9905 | 10.6516 | 40.3126 | 39.8389 | 39.0432 | 38.1937 | 37.0474 | 35.9295 | 34.8263 | 33.7463 | 30.1074 | 28.4337 | 26.8768 | 11.0084 | 40.7947 | 40.3926 | 39.7421 | 38.9884 | 37.8411 | 36.7232 | 35.6179 | 34.5368 | 30.8895 | 29.2105 | 27.6484
|  | ROMSEY PRIMARY | CF |  |  |  |  | 14.8011 | 44.7147 | 45.9126 | 45.5926 | 45.2253 | 44.7179 | 44.1895 | 43.6063 | 42.9884 | 40.5895 | 39.6326 | 38.7568 | 10.7979 | 40.7063 | 40.5474 | 40.1853 | 39.7695 | 39.1863 | 38.5811 | 37.9105 | 37.1968 | 34.4442 | 33.3558 | 32.3474 | 11.1484 | 41.0621 | 41.3442 | 40.9811 | 40.5642 | 39.9821 | 39.3758 | 38.7042 | 37.9905 | 35.2347 | 34.1432 | 33.1326
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ROSE GREEN PRIMARY | MINIMUM HEADROOM | SZ 89974 99335 | NO | YES | 1.0516 | 20.6873 | 20.2999 | 18.6326 | 17.0368 | 15.2347 | 13.6631 | 12.301 | 10.9631 | 9.6536 | 2.5989 | -2.5043 | -9.0737 | 15.8136 | 14.5526 | 12.6389 | 10.8199 | 8.7631 | 6.9768 | 5.4284 | 3.9063 | 2.4126 | -5.6979 | -11.5537 | -15.1769 | 16.3873 | 15.1631 | 13.3073 | 11.5126 | 9.4831 | 7.7199 | 6.1905 | 4.6873 | 3.2126 | -4.7874 | -10.5695 | -14.1474
|  | ROSE GREEN PRIMARY | EE |  |  |  |  | 20.8821 | 20.6263 | 20.1736 | 18.9284 | 17.2557 | 15.8368 | 14.3684 | 12.8368 | 11.4568 | 4.4463 | -0.51058 | -3.0348 | 16.5442 | 15.6473 | 14.4052 | 12.9831 | 11.0642 | 9.4452 | 7.7663 | 6.0105 | 4.4294 | -3.6622 | -9.3811 | -12.2758 | 17.0957 | 16.2252 | 15.021 | 13.6442 | 11.7536 | 10.1547 | 8.4978 | 6.7652 | 5.2052 | -2.7779 | -8.4243 | -11.2822
|  | ROSE GREEN PRIMARY | HT |  |  |  |  | 20.6873 | 20.2999 | 18.6326 | 17.0368 | 15.2347 | 13.6631 | 12.301 | 10.9631 | 9.6536 | 2.5989 | -2.5043 | -5.6779 | 15.8136 | 14.5526 | 12.6389 | 10.8199 | 8.7631 | 6.9768 | 5.4284 | 3.9063 | 2.4126 | -5.6979 | -11.5537 | -15.1769 | 16.3873 | 15.1631 | 13.3073 | 11.5126 | 9.4831 | 7.7199 | 6.1905 | 4.6873 | 3.2126 | -4.7874 | -10.5695 | -14.1474
|  | ROSE GREEN PRIMARY | HE |  |  |  |  | 21.1347 | 20.9557 | 20.7599 | 19.7978 | 18.2115 | 16.7599 | 15.5042 | 14.161 | 12.9326 | 6.6021 | 2.2515 | -9.0737 | 16.7968 | 16.3336 | 15.2178 | 13.9252 | 12.0926 | 10.4231 | 8.9821 | 7.4347 | 6.0178 | -1.3348 | -6.3948 | -8.7453 | 17.3484 | 16.8968 | 15.8168 | 14.5673 | 12.7736 | 11.1273 | 9.7063 | 8.1799 | 6.7852 | -0.46005 | -5.4453 | -7.7622
|  | ROSE GREEN PRIMARY | CF |  |  |  |  | 21.3073 | 21.2168 | 21.1221 | 21.0242 | 20.9221 | 20.8178 | 20.7136 | 20.6126 | 20.5115 | 15.9894 | 10.5126 | 9.2736 | 16.9694 | 16.8789 | 16.7842 | 16.6863 | 16.5842 | 16.4799 | 16.3768 | 15.8842 | 15.1768 | 9.5242 | 3.1157 | 1.6831 | 17.521 | 17.4305 | 17.3357 | 17.2378 | 17.1347 | 17.0315 | 16.9273 | 16.4494 | 15.7663 | 10.241 | 3.9336 | 2.521
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | ROSE HILL PRIMARY | MINIMUM HEADROOM | SP 53637 03027 | NO | YES | 0 | 24.5379 | 44.2979 | 44.2474 | 44.0211 | 43.7853 | 42.0063 | 40.2684 | 38.9105 | 37.8695 | 32.8558 | 28.2042 | 8.0505 | 19.8716 | 39.4147 | 38.9453 | 38.4716 | 38.0011 | 35.2695 | 33.2211 | 31.6274 | 30.4116 | 24.5116 | 19.0053 | 13.6105 | 21.1 | 40.7779 | 40.3084 | 39.8347 | 39.3642 | 36.6326 | 34.5832 | 32.9895 | 31.7726 | 25.8705 | 20.3632 | 14.9663
|  | ROSE HILL PRIMARY | EE |  |  |  |  | 24.6653 | 44.4632 | 44.2474 | 44.0211 | 43.7853 | 42.0063 | 40.2684 | 38.9105 | 37.8695 | 32.8558 | 28.2042 | 23.6674 | 20.6189 | 39.9274 | 39.3674 | 38.8642 | 38.4116 | 35.2695 | 33.2211 | 31.6274 | 30.4116 | 24.5116 | 19.0053 | 13.6105 | 21.2632 | 41.0326 | 40.7316 | 40.2284 | 39.7747 | 36.6326 | 34.5832 | 32.9895 | 31.7726 | 25.8705 | 20.3632 | 14.9663
|  | ROSE HILL PRIMARY | HT |  |  |  |  | 24.5379 | 44.2979 | 45.1379 | 44.7 | 44.2621 | 43.9853 | 42.8137 | 41.6916 | 40.6042 | 35.2505 | 31.1653 | 26.1937 | 19.8716 | 39.4147 | 38.9453 | 38.4716 | 38.0011 | 37.7242 | 36.3611 | 35.0558 | 33.7874 | 27.5105 | 21.7326 | 15.9495 | 21.1 | 40.7779 | 40.3084 | 39.8347 | 39.3642 | 39.0874 | 37.7242 | 36.4179 | 35.1495 | 28.8705 | 22.9842 | 17.2116
|  | ROSE HILL PRIMARY | HE |  |  |  |  | 24.8379 | 44.6863 | 44.5189 | 44.3389 | 44.1484 | 42.8411 | 41.1716 | 39.9842 | 39.0442 | 34.5105 | 30.32 | 8.0505 | 20.8495 | 40.4389 | 40.0011 | 39.62 | 39.2895 | 36.1937 | 34.2168 | 32.8189 | 31.7147 | 26.3484 | 21.3558 | 16.4611 | 21.4495 | 41.2726 | 41.0895 | 40.8979 | 40.6537 | 37.5558 | 35.5789 | 34.1811 | 33.0758 | 27.7084 | 22.7137 | 17.8179
|  | ROSE HILL PRIMARY | CF |  |  |  |  | 24.9653 | 44.88 | 44.7937 | 44.7032 | 44.6095 | 44.5137 | 44.42 | 44.3274 | 43.9242 | 39.4516 | 36.6842 | 34.0432 | 20.9905 | 40.9021 | 40.8126 | 40.7189 | 40.6221 | 40.2737 | 39.54 | 38.5347 | 37.4432 | 32.1379 | 28.8453 | 25.6853 | 21.5947 | 41.5053 | 41.4158 | 41.3211 | 41.2232 | 41.1 | 40.9042 | 39.8989 | 38.8063 | 33.5 | 30.2063 | 27.0453
MELKSHAM GSP | CHIPPENHAM BSP | ROWDEN PRIMARY | MINIMUM HEADROOM | ST 90805 72608 | NO | YES | 0.094737 | 25.7237 | 25.3879 | 25.0332 | 23.9995 | 22.8416 | 21.5195 | 29.2605 | 27.4405 | 25.6626 | 16.3005 | 10.1784 | -13.1395 | 20.3447 | 19.3795 | 18.1605 | 16.7289 | 15.4426 | 13.9647 | 21.55 | 19.4511 | 17.4174 | 6.6563 | -0.34368 | -3.6153 | 21.7795 | 20.8426 | 19.6616 | 18.2089 | 16.8932 | 15.3784 | 22.9342 | 20.8321 | 18.7942 | 8.0132 | 0.98895 | -2.2942
|  | ROWDEN PRIMARY | EE |  |  |  |  | 25.9163 | 25.6384 | 25.3437 | 24.7311 | 23.6805 | 22.5679 | 30.5405 | 28.8195 | 27.1384 | 18.3163 | 12.7247 | 10.4416 | 20.7679 | 19.93 | 18.8353 | 17.5205 | 16.3489 | 15.1058 | 22.9605 | 20.9742 | 19.0542 | 8.9016 | 2.4953 | -0.087895 | 22.1911 | 21.3784 | 20.3184 | 19.0153 | 17.8153 | 16.5405 | 24.3658 | 22.3521 | 20.4268 | 10.2447 | 3.8058 | 1.2111
|  | ROWDEN PRIMARY | HT |  |  |  |  | 25.7237 | 25.3879 | 25.0332 | 23.9995 | 22.8416 | 21.5195 | 29.2605 | 27.4405 | 25.6626 | 16.3005 | 10.1784 | 7.2774 | 20.3447 | 19.3795 | 18.1605 | 16.7289 | 15.4426 | 13.9647 | 21.55 | 19.4511 | 17.4174 | 6.6563 | -0.34368 | -3.6153 | 21.7795 | 20.8426 | 19.6616 | 18.2089 | 16.8932 | 15.3784 | 22.9342 | 20.8321 | 18.7942 | 8.0132 | 0.98895 | -2.2942
|  | ROWDEN PRIMARY | HE |  |  |  |  | 26.1711 | 25.9732 | 25.7532 | 25.5163 | 24.7942 | 23.8174 | 31.8984 | 30.2795 | 28.7689 | 20.7153 | 15.8342 | -13.1395 | 21.33 | 20.6679 | 19.7384 | 18.5826 | 17.5574 | 16.4584 | 24.4247 | 22.5658 | 20.8089 | 11.4795 | 5.8268 | 3.8795 | 22.5711 | 22.0995 | 21.2016 | 20.0868 | 19.0458 | 17.9184 | 25.8574 | 23.9521 | 22.1932 | 12.85 | 7.1858 | 5.23
|  | ROWDEN PRIMARY | CF |  |  |  |  | 26.35 | 26.2447 | 26.1332 | 26.0195 | 25.8984 | 25.7753 | 34.6542 | 34.5342 | 34.4016 | 30.5616 | 25.0658 | 23.9826 | 21.8826 | 21.5321 | 21.0753 | 20.5447 | 20.05 | 19.5521 | 28.1763 | 27.7111 | 27.2416 | 22.8426 | 16.4258 | 15.1879 | 22.7679 | 22.6521 | 22.4963 | 21.9837 | 21.5058 | 21.0226 | 29.6574 | 29.2079 | 28.7447 | 24.2279 | 17.8047 | 16.5605
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ROWNER PARK PRIMARY | MINIMUM HEADROOM | SU 58018 00782 | NO | YES | 0 | 23.7632 | 23.5811 | 23.3895 | 23.1895 | 22.9832 | 22.7421 | 22.46 | 22.1937 | 21.9421 | 20.72 | 19.4842 | 3.0642 | 20.9884 | 20.6611 | 20.3295 | 19.9947 | 19.6621 | 19.3305 | 19.0253 | 18.7389 | 18.4663 | 17.1253 | 15.7358 | 14.4421 | 21.4442 | 21.1284 | 20.8084 | 20.4853 | 20.1611 | 19.8389 | 19.5442 | 19.2653 | 19.0032 | 17.7084 | 16.3168 | 15.0232
|  | ROWNER PARK PRIMARY | EE |  |  |  |  | 23.8674 | 23.7168 | 23.5568 | 23.3874 | 23.2116 | 23.0411 | 22.8779 | 22.7189 | 22.5379 | 21.6032 | 20.6421 | 19.7747 | 21.2074 | 20.9463 | 20.6779 | 20.4042 | 20.1295 | 19.8621 | 19.6053 | 19.3568 | 19.1253 | 18.1095 | 17.0305 | 16.0389 | 21.6537 | 21.4011 | 21.1421 | 20.8768 | 20.6084 | 20.3505 | 20.1 | 19.8579 | 19.6337 | 18.6495 | 17.6074 | 16.6158
|  | ROWNER PARK PRIMARY | HT |  |  |  |  | 23.7632 | 23.5811 | 23.3895 | 23.1895 | 22.9832 | 22.7421 | 22.46 | 22.1937 | 21.9421 | 20.72 | 19.4842 | 18.3463 | 20.9884 | 20.6611 | 20.3295 | 19.9947 | 19.6621 | 19.3305 | 19.0253 | 18.7389 | 18.4663 | 17.1253 | 15.7358 | 14.4421 | 21.4442 | 21.1284 | 20.8084 | 20.4853 | 20.1611 | 19.8389 | 19.5442 | 19.2653 | 19.0032 | 17.7084 | 16.3168 | 15.0232
|  | ROWNER PARK PRIMARY | HE |  |  |  |  | 23.9989 | 23.8853 | 23.7621 | 23.6295 | 23.4874 | 23.3526 | 23.2242 | 23.1032 | 23 | 22.6337 | 22.1526 | 3.0642 | 21.4916 | 21.3147 | 21.1284 | 20.9358 | 20.7337 | 20.5421 | 20.3589 | 20.1874 | 20.0337 | 19.3979 | 18.6989 | 18.0663 | 21.9179 | 21.7547 | 21.5726 | 21.3842 | 21.1874 | 21 | 20.82 | 20.6537 | 20.5032 | 19.8874 | 19.2232 | 18.6274
|  | ROWNER PARK PRIMARY | CF |  |  |  |  | 24.0895 | 24.0253 | 23.9568 | 23.8874 | 23.8137 | 23.74 | 23.6695 | 23.5979 | 23.5253 | 23.2042 | 23.0211 | 22.6316 | 21.6274 | 21.5263 | 21.4063 | 21.2874 | 21.1547 | 21.0358 | 20.9158 | 20.7979 | 20.6768 | 20.1232 | 19.6168 | 19.1642 | 22.0126 | 21.9453 | 21.8442 | 21.7295 | 21.6011 | 21.4853 | 21.3684 | 21.2537 | 21.1379 | 20.6021 | 20.1221 | 19.6958
FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE PRIMARY | MINIMUM HEADROOM | SZ 59554 91973 | NO | YES | 0 | 34.9695 | 34.4853 | 33.9726 | 32.7905 | 31.4126 | 29.9411 | 28.4979 | 27.0926 | 25.7821 | 19.5211 | 14.8968 | -12.4726 | 28.8537 | 27.4074 | 25.9305 | 24.3789 | 22.8558 | 21.2232 | 19.6126 | 18.0389 | 16.5726 | 9.5084 | 4.3432 | -0.32211 | 29.9063 | 28.5295 | 27.1221 | 25.5747 | 24.0495 | 22.4147 | 20.8 | 19.2232 | 17.7526 | 10.6632 | 5.4716 | 0.79474
|  | RYDE PRIMARY | EE |  |  |  |  | 35.2568 | 34.86 | 34.4379 | 33.9884 | 33.0126 | 31.8758 | 30.7053 | 29.5032 | 28.3705 | 22.7884 | 19.0905 | 15.8684 | 29.5516 | 28.3526 | 27.0947 | 25.8 | 24.6263 | 23.3716 | 22.0737 | 20.7358 | 19.4716 | 13.1768 | 9.0379 | 5.3821 | 30.5737 | 29.4337 | 28.2358 | 26.9979 | 25.8211 | 24.5621 | 23.2589 | 21.9168 | 20.6474 | 14.3189 | 10.1421 | 6.4737
|  | RYDE PRIMARY | HT |  |  |  |  | 34.9695 | 34.4853 | 33.9726 | 32.7905 | 31.4126 | 29.9411 | 28.4979 | 27.0926 | 25.7821 | 19.5211 | 14.8968 | 10.76 | 28.8537 | 27.4074 | 25.9305 | 24.3789 | 22.8558 | 21.2232 | 19.6126 | 18.0389 | 16.5726 | 9.5084 | 4.3432 | -0.32211 | 29.9063 | 28.5295 | 27.1221 | 25.5747 | 24.0495 | 22.4147 | 20.8 | 19.2232 | 17.7526 | 10.6632 | 5.4716 | 0.79474
|  | RYDE PRIMARY | HE |  |  |  |  | 35.6137 | 35.3253 | 35.0074 | 34.6653 | 34.2926 | 33.6337 | 32.6516 | 31.6432 | 30.6905 | 26.1768 | 23.4611 | -12.4726 | 30.3463 | 29.4042 | 28.3842 | 27.3189 | 26.3274 | 25.2863 | 24.1905 | 23.0589 | 21.9874 | 16.8453 | 13.7537 | 11.0295 | 31.3474 | 30.4421 | 29.4737 | 28.46 | 27.5126 | 26.48 | 25.3821 | 24.2484 | 23.1737 | 18.0168 | 14.9137 | 12.18
|  | RYDE PRIMARY | CF |  |  |  |  | 35.8684 | 35.7137 | 35.5516 | 35.3853 | 35.2084 | 35.0295 | 34.8526 | 34.6779 | 34.5042 | 31.6705 | 29.7674 | 28.2484 | 31.0537 | 30.6495 | 30.1389 | 29.6211 | 29.1305 | 28.6147 | 28.0705 | 27.54 | 27.0442 | 23.0137 | 20.8463 | 19.1021 | 31.6326 | 31.4589 | 31.1453 | 30.6474 | 30.1789 | 29.6863 | 29.1695 | 28.6621 | 28.1895 | 24.2021 | 22.0274 | 20.2779
MANNINGTON GSP | SALISBURY BSP | SALISBURY CENTRAL PRIMARY | MINIMUM HEADROOM | SU 14215 30481 | NO | YES | 0 | 46.8895 | 46.4547 | 45.9937 | 45.5147 | 45.2137 | 44.7147 | 44.0263 | 42.8168 | 41.8811 | 37.1516 | 33.3347 | 0.19579 | 40.5789 | 39.7611 | 38.6653 | 37.2937 | 36.48 | 35.0063 | 33.5989 | 32.2442 | 31.2084 | 25.9074 | 21.6179 | 17.2968 | 41.6937 | 41.2589 | 40.74 | 39.3737 | 38.5453 | 37.0768 | 35.68 | 34.3263 | 33.2895 | 27.9821 | 23.6863 | 19.3621
|  | SALISBURY CENTRAL PRIMARY | EE |  |  |  |  | 47.1411 | 46.7821 | 46.4 | 45.9989 | 45.5832 | 45.1789 | 44.7947 | 44.4221 | 43.3989 | 39.6632 | 36.7 | 33.7211 | 41.0495 | 40.4758 | 39.6705 | 38.5758 | 37.5495 | 36.6611 | 35.5411 | 34.2021 | 32.8442 | 28.6789 | 25.3442 | 21.9432 | 41.9453 | 41.5863 | 41.2042 | 40.6505 | 39.6284 | 38.7421 | 37.6263 | 36.2937 | 34.9537 | 30.7516 | 27.4084 | 24.0053
|  | SALISBURY CENTRAL PRIMARY | HT |  |  |  |  | 46.8895 | 46.4547 | 45.9937 | 45.5147 | 45.2137 | 44.7147 | 44.0263 | 42.8168 | 41.8811 | 37.1516 | 33.3347 | 29.5263 | 40.5789 | 39.7611 | 38.6653 | 37.2937 | 36.48 | 35.0063 | 33.5989 | 32.2442 | 31.2084 | 25.9074 | 21.6179 | 17.2968 | 41.6937 | 41.2589 | 40.74 | 39.3737 | 38.5453 | 37.0768 | 35.68 | 34.3263 | 33.2895 | 27.9821 | 23.6863 | 19.3621
|  | SALISBURY CENTRAL PRIMARY | HE |  |  |  |  | 47.4579 | 47.1947 | 46.9042 | 46.5916 | 46.2568 | 45.9358 | 45.6337 | 45.3526 | 45.1084 | 42.6642 | 40.5221 | 0.19579 | 41.3842 | 41.1137 | 40.8074 | 39.9042 | 39.0632 | 38.3611 | 37.5032 | 36.5242 | 35.6074 | 31.9568 | 29.5221 | 26.9768 | 42.2621 | 41.9989 | 41.7084 | 41.3958 | 41.04 | 40.4368 | 39.5821 | 38.6074 | 37.6947 | 34.0368 | 31.5979 | 29.0505
|  | SALISBURY CENTRAL PRIMARY | CF |  |  |  |  | 47.6789 | 47.5337 | 47.3821 | 47.2253 | 47.0621 | 46.8958 | 46.7326 | 46.5716 | 46.4095 | 45.6874 | 45.06 | 43.6484 | 41.6126 | 41.4621 | 41.3053 | 41.1421 | 40.9726 | 40.7368 | 40.3821 | 39.9642 | 39.5074 | 35.7905 | 34.5947 | 32.9674 | 42.4832 | 42.3379 | 42.1863 | 42.0295 | 41.8663 | 41.7 | 41.5368 | 41.3758 | 41.2095 | 37.8789 | 36.6768 | 35.0463
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | SANDHURST PRIMARY | MINIMUM HEADROOM | SU 83597 60930 | NO | YES | 0 | 35.2221 | 34.6926 | 34.1295 | 33.5516 | 32.9368 | 32.1874 | 31.2347 | 30.3168 | 29.4579 | 25.4284 | 21.2516 | -12.4632 | 29.12 | 28.1295 | 27.0779 | 25.9863 | 24.8947 | 23.7611 | 22.7337 | 21.7379 | 20.8042 | 16.3779 | 11.6968 | 7.3842 | 30.1137 | 29.1421 | 28.1126 | 27.0126 | 25.9053 | 24.7684 | 23.7421 | 22.7463 | 21.8137 | 17.3905 | 12.7137 | 8.4053
|  | SANDHURST PRIMARY | EE |  |  |  |  | 35.5379 | 35.1032 | 34.6421 | 34.1611 | 33.6642 | 33.1853 | 32.7189 | 32.2558 | 31.5768 | 28.4589 | 25.1979 | 22.2547 | 29.7958 | 29.0053 | 28.1811 | 27.3084 | 26.4389 | 25.5526 | 24.7242 | 23.8905 | 23.1232 | 19.7053 | 16.0389 | 12.6968 | 30.7726 | 29.9979 | 29.1895 | 28.3347 | 27.4758 | 26.5758 | 25.7368 | 24.8968 | 24.1284 | 20.7126 | 17.0474 | 13.7095
|  | SANDHURST PRIMARY | HT |  |  |  |  | 35.2221 | 34.6926 | 34.1295 | 33.5516 | 32.9368 | 32.1874 | 31.2347 | 30.3168 | 29.4579 | 25.4284 | 21.2516 | 17.4295 | 29.12 | 28.1295 | 27.0779 | 25.9863 | 24.8947 | 23.7611 | 22.7337 | 21.7379 | 20.8042 | 16.3779 | 11.6968 | 7.3842 | 30.1137 | 29.1421 | 28.1126 | 27.0126 | 25.9053 | 24.7684 | 23.7421 | 22.7463 | 21.8137 | 17.3905 | 12.7137 | 8.4053
|  | SANDHURST PRIMARY | HE |  |  |  |  | 35.9589 | 35.6547 | 35.3189 | 34.9589 | 34.5726 | 34.2042 | 33.8568 | 33.5316 | 33.2516 | 32.0989 | 29.7505 | -12.4632 | 30.6989 | 30.1884 | 29.6263 | 29.0095 | 28.3726 | 27.7168 | 27.1137 | 26.5116 | 25.9747 | 23.6674 | 21 | 18.5947 | 31.3905 | 31.0737 | 30.6011 | 29.9958 | 29.3695 | 28.7253 | 28.1337 | 27.5442 | 27.0105 | 24.6726 | 22.0084 | 19.6063
|  | SANDHURST PRIMARY | CF |  |  |  |  | 36.2411 | 36.0811 | 35.9168 | 35.7453 | 35.5674 | 35.3863 | 35.2084 | 35.0326 | 34.8568 | 34.0716 | 33.3305 | 31.9589 | 31.1695 | 30.8768 | 30.5632 | 30.2284 | 29.8884 | 29.5242 | 29.1726 | 28.8011 | 28.4368 | 26.6611 | 24.8716 | 23.2979 | 31.6853 | 31.5158 | 31.3432 | 31.1621 | 30.8632 | 30.5063 | 30.1621 | 29.8 | 29.4432 | 27.6926 | 25.8789 | 24.3063
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN PRIMARY | MINIMUM HEADROOM | SZ 59877 85052 | NO | YES | 0 | 18.0179 | 17.74 | 17.4442 | 17.1389 | 16.8253 | 16.5074 | 16.2295 | 15.7674 | 15.1947 | 12.3863 | 9.8158 | -8.72 | 14.9189 | 14.3253 | 13.7084 | 13.1463 | 12.5221 | 11.8653 | 11.2284 | 10.6105 | 9.9905 | 6.8684 | 3.9758 | 1.3547 | 15.6979 | 15.0947 | 14.4674 | 13.8968 | 13.2621 | 12.5958 | 11.9474 | 11.3168 | 10.6853 | 7.5526 | 4.6579 | 2.0358
|  | SANDOWN PRIMARY | EE |  |  |  |  | 18.1811 | 17.9516 | 17.7074 | 17.4526 | 17.1895 | 16.9347 | 16.6937 | 16.4611 | 16.2537 | 14.3905 | 12.3589 | 10.5642 | 15.2737 | 14.7884 | 14.2568 | 13.7895 | 13.3158 | 12.8116 | 12.3137 | 11.8705 | 11.4116 | 9.1011 | 6.8042 | 4.7632 | 16.0021 | 15.5663 | 15.0242 | 14.5505 | 14.0705 | 13.5579 | 13.0516 | 12.6011 | 12.1347 | 9.7832 | 7.4863 | 5.4442
|  | SANDOWN PRIMARY | HT |  |  |  |  | 18.0179 | 17.74 | 17.4442 | 17.1389 | 16.8253 | 16.5074 | 16.2295 | 15.7674 | 15.1947 | 12.3863 | 9.8158 | 7.5011 | 14.9189 | 14.3253 | 13.7084 | 13.1463 | 12.5221 | 11.8653 | 11.2284 | 10.6105 | 9.9905 | 6.8684 | 3.9758 | 1.3547 | 15.6979 | 15.0947 | 14.4674 | 13.8968 | 13.2621 | 12.5958 | 11.9474 | 11.3168 | 10.6853 | 7.5526 | 4.6579 | 2.0358
|  | SANDOWN PRIMARY | HE |  |  |  |  | 18.3937 | 18.2305 | 18.0495 | 17.8537 | 17.6463 | 17.4463 | 17.26 | 17.0853 | 16.9337 | 16.2768 | 14.7411 | -8.72 | 15.6463 | 15.4011 | 15.0063 | 14.6747 | 14.3116 | 13.9326 | 13.5589 | 13.2347 | 12.8768 | 11.1284 | 9.4011 | 7.8768 | 16.2263 | 16.0558 | 15.7821 | 15.4516 | 15.0832 | 14.6979 | 14.3189 | 13.9895 | 13.6253 | 11.8368 | 10.0853 | 8.56
|  | SANDOWN PRIMARY | CF |  |  |  |  | 18.5442 | 18.4579 | 18.3674 | 18.2747 | 18.1789 | 18.08 | 17.9842 | 17.8874 | 17.7916 | 17.3663 | 17.1537 | 16.4895 | 15.7968 | 15.7105 | 15.5947 | 15.3747 | 15.1284 | 14.8705 | 14.6242 | 14.3937 | 14.1674 | 13.3347 | 12.2442 | 11.2863 | 16.3768 | 16.2905 | 16.1958 | 16.0958 | 15.9063 | 15.6463 | 15.3947 | 15.16 | 14.9295 | 14.0842 | 12.9653 | 11.98
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | SELSEY PRIMARY | MINIMUM HEADROOM | SZ 85667 94289 | NO | YES | 10.2632 | 8.1089 | 7.8742 | 7.6184 | 7.3426 | 7.0079 | 6.5742 | 6.1984 | 5.7879 | 5.3595 | 3.45 | 1.3805 | -12.0184 | 4.7426 | 4.3216 | 3.8311 | 3.3479 | 3.5553 | 3.0921 | 2.6911 | 2.2458 | 1.7763 | -0.33316 | -2.6658 | -4.8068 | 5.8763 | 5.4511 | 4.9532 | 4.4647 | 3.9711 | 3.5089 | 3.1079 | 2.6626 | 2.1942 | 0.086842 | -2.2426 | -4.3805
|  | SELSEY PRIMARY | EE |  |  |  |  | 8.2532 | 8.0616 | 7.8574 | 7.6447 | 7.6911 | 7.3626 | 7.05 | 6.7184 | 6.3753 | 4.9247 | 3.3037 | 1.8416 | 5.0353 | 4.7005 | 4.3153 | 3.9437 | 4.3037 | 3.9542 | 3.6205 | 3.2647 | 2.89 | 1.2921 | -0.54263 | -2.21 | 6.1668 | 5.8353 | 5.4437 | 5.0689 | 4.7184 | 4.3689 | 4.0363 | 3.6805 | 3.3058 | 1.71 | -0.12158 | -1.7858
|  | SELSEY PRIMARY | HT |  |  |  |  | 8.1089 | 7.8742 | 7.6184 | 7.3426 | 7.0079 | 6.5742 | 6.1984 | 5.7879 | 5.3595 | 3.45 | 1.3805 | -0.50789 | 4.7426 | 4.3216 | 3.8311 | 3.3479 | 3.5553 | 3.0921 | 2.6911 | 2.2458 | 1.7763 | -0.33316 | -2.6658 | -4.8068 | 5.8763 | 5.4511 | 4.9532 | 4.4647 | 3.9711 | 3.5089 | 3.1079 | 2.6626 | 2.1942 | 0.086842 | -2.2426 | -4.3805
|  | SELSEY PRIMARY | HE |  |  |  |  | 8.4384 | 8.3047 | 8.1563 | 7.9963 | 7.8268 | 7.6647 | 7.5111 | 7.3679 | 7.2363 | 6.5289 | 5.3058 | -12.0184 | 5.4184 | 5.2037 | 4.9311 | 4.6679 | 4.3942 | 4.1563 | 3.9311 | 3.6879 | 3.4258 | 3.0405 | 1.6426 | 0.39 | 6.3668 | 6.2268 | 6.0689 | 5.8026 | 5.5258 | 5.2858 | 5.0584 | 4.8132 | 4.5479 | 3.4563 | 2.0616 | 0.81
|  | SELSEY PRIMARY | CF |  |  |  |  | 8.5679 | 8.4995 | 8.4279 | 8.3542 | 8.2784 | 8.2005 | 8.1237 | 8.0479 | 7.9721 | 7.6237 | 7.1005 | 6.4132 | 5.6374 | 5.5132 | 5.3721 | 5.2311 | 5.0805 | 4.9437 | 4.8079 | 4.6742 | 4.5216 | 3.7795 | 3.5995 | 2.8079 | 6.5026 | 6.43 | 6.3532 | 6.2753 | 6.1942 | 6.0805 | 5.9437 | 5.8079 | 5.6521 | 4.9005 | 4.0163 | 3.2258
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY PRIMARY | MINIMUM HEADROOM | ST 85605 23325 | NO | YES | 0 | 27.5371 | 26.9508 | 26.4487 | 25.6276 | 24.8203 | 24.2592 | 23.8592 | 23.4803 | 23.1129 | 21.0329 | 19.3666 | 2.6771 | 23.2687 | 22.6045 | 22.0582 | 21.1403 | 20.2603 | 19.6655 | 19.2476 | 18.8539 | 18.4718 | 16.2708 | 14.5234 | 12.5182 | 24.3203 | 23.6582 | 23.1024 | 22.1645 | 21.2603 | 20.6518 | 20.2245 | 19.8203 | 19.4276 | 17.1508 | 15.3297 | 13.2866
|  | SHAFTESBURY PRIMARY | EE |  |  |  |  | 27.6803 | 27.3003 | 26.8739 | 26.1276 | 25.3992 | 24.915 | 24.5655 | 24.2234 | 23.9034 | 22.4329 | 20.8403 | 19.3908 | 23.5603 | 22.9834 | 22.5192 | 21.6834 | 20.9855 | 20.4645 | 20.1024 | 19.7487 | 19.4182 | 17.9024 | 16.2224 | 14.6118 | 24.5782 | 24.0434 | 23.5718 | 22.7161 | 21.8897 | 21.3624 | 20.9918 | 20.6308 | 20.2918 | 18.7139 | 16.9655 | 15.3329
|  | SHAFTESBURY PRIMARY | HT |  |  |  |  | 27.5371 | 26.9508 | 26.4487 | 25.6276 | 24.8203 | 24.2592 | 23.8592 | 23.4803 | 23.1129 | 21.0329 | 19.3666 | 17.5466 | 23.2687 | 22.6045 | 22.0582 | 21.1403 | 20.2603 | 19.6655 | 19.2476 | 18.8539 | 18.4718 | 16.2708 | 14.5234 | 12.5182 | 24.3203 | 23.6582 | 23.1024 | 22.1645 | 21.2603 | 20.6518 | 20.2245 | 19.8203 | 19.4276 | 17.1508 | 15.3297 | 13.2866
|  | SHAFTESBURY PRIMARY | HE |  |  |  |  | 27.875 | 27.7182 | 27.4455 | 26.8024 | 26.1739 | 25.8024 | 25.5613 | 25.3329 | 25.1255 | 24.2403 | 23.2613 | 2.6771 | 23.9592 | 23.5161 | 23.1371 | 22.4129 | 21.7139 | 21.3118 | 21.0624 | 20.8255 | 20.6129 | 19.6971 | 18.6434 | 17.4971 | 24.9297 | 24.5518 | 24.2003 | 23.4582 | 22.7403 | 22.3287 | 22.0718 | 21.8308 | 21.6129 | 20.6634 | 19.5697 | 18.3792
|  | SHAFTESBURY PRIMARY | CF |  |  |  |  | 28.015 | 27.9318 | 27.8487 | 27.7539 | 27.5118 | 27.3076 | 27.1624 | 27.0203 | 26.8782 | 26.2266 | 25.6055 | 24.9424 | 24.2939 | 24.0592 | 23.8603 | 23.5255 | 23.2003 | 22.9771 | 22.8245 | 22.6739 | 22.5224 | 21.8339 | 21.155 | 20.4213 | 25.1403 | 25.0192 | 24.8466 | 24.5676 | 24.2603 | 24.0318 | 23.875 | 23.7213 | 23.5666 | 22.8624 | 22.1603 | 21.3971
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET PRIMARY | MINIMUM HEADROOM | SZ 40828 88643 | NO | YES | 0 | 16.3084 | 16.0568 | 15.8021 | 15.5389 | 15.2221 | 12.4253 | 9.4347 | 9.2526 | 9.0768 | 7.8179 | 6.3789 | 5.1495 | 14.5632 | 14.2947 | 14.0232 | 13.7421 | 13.4147 | 9.9232 | 6.4558 | 6.2874 | 6.1253 | 4.8842 | 3.4379 | 2.9042 | 14.9463 | 14.6768 | 14.4042 | 14.1232 | 13.7863 | 10.1484 | 6.6684 | 6.4863 | 6.3105 | 4.9779 | 3.4242 | 2.8484
|  | SHALFLEET PRIMARY | EE |  |  |  |  | 16.4811 | 16.28 | 16.0674 | 15.8526 | 15.5958 | 15.3168 | 15.0411 | 14.7737 | 13.8368 | 11.1147 | 7.8526 | 7.0705 | 14.7505 | 14.5368 | 14.3105 | 14.0821 | 13.8221 | 13.54 | 13.2642 | 13.0011 | 11.6958 | 8.7842 | 5.2516 | 4.4432 | 15.1337 | 14.9189 | 14.6916 | 14.4611 | 14.1905 | 13.8947 | 13.6021 | 13.3221 | 11.8642 | 8.8232 | 5.14 | 4.2853
|  | SHALFLEET PRIMARY | HT |  |  |  |  | 16.3084 | 16.0568 | 15.8021 | 15.5389 | 15.2221 | 12.4253 | 9.4347 | 9.2526 | 9.0768 | 7.8179 | 6.3789 | 5.8232 | 14.5632 | 14.2947 | 14.0232 | 13.7421 | 13.4147 | 9.9232 | 6.4558 | 6.2874 | 6.1253 | 4.8842 | 3.4379 | 2.9042 | 14.9463 | 14.6768 | 14.4042 | 14.1232 | 13.7863 | 10.1484 | 6.6684 | 6.4863 | 6.3105 | 4.9779 | 3.4242 | 2.8484
|  | SHALFLEET PRIMARY | HE |  |  |  |  | 16.7074 | 16.5821 | 16.4453 | 16.2968 | 16.1074 | 15.92 | 15.7347 | 14.9011 | 14.7295 | 12.3053 | 9.7263 | 5.1495 | 14.9968 | 14.8632 | 14.7179 | 14.5611 | 14.3674 | 14.1779 | 13.9895 | 12.7832 | 12.6074 | 9.8968 | 6.9642 | 6.34 | 15.38 | 15.2463 | 15.1011 | 14.9432 | 14.7421 | 14.5453 | 14.3495 | 13.0011 | 12.8179 | 10.0526 | 7.0768 | 6.4147
|  | SHALFLEET PRIMARY | CF |  |  |  |  | 16.8411 | 16.7684 | 16.6874 | 16.5968 | 16.4863 | 16.3726 | 16.2632 | 16.1558 | 16.0568 | 15.6326 | 15.1579 | 14.7337 | 15.1389 | 15.0611 | 14.9726 | 14.8747 | 14.7579 | 14.64 | 14.5232 | 14.4126 | 14.3074 | 13.8737 | 13.3716 | 12.9274 | 15.2874 | 15.4442 | 15.3558 | 15.2579 | 15.1379 | 15.0147 | 14.8947 | 14.7811 | 14.6726 | 14.2211 | 13.6968 | 13.2274
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN PRIMARY | MINIMUM HEADROOM | SZ 57809 81912 | NO | YES | 0 | 30.2474 | 29.7021 | 29.1505 | 28.5674 | 27.9116 | 27.2295 | 26.5674 | 25.9284 | 25.2937 | 22.1568 | 19.2516 | 6.5137 | 26.9863 | 26.4011 | 25.8105 | 25.1842 | 24.4853 | 23.7547 | 23.0421 | 22.3526 | 21.6642 | 18.4705 | 15.3463 | 12.6084 | 27.5105 | 26.9242 | 26.3326 | 25.7074 | 25.0021 | 24.2663 | 23.5474 | 22.8505 | 22.1547 | 18.6874 | 15.4537 | 12.6516
|  | SHANKLIN PRIMARY | EE |  |  |  |  | 30.6179 | 30.1842 | 29.7221 | 29.2432 | 28.7379 | 28.2011 | 27.6632 | 27.1705 | 26.6737 | 31.0916 | 30.2232 | 29.1305 | 27.3358 | 26.8789 | 26.3895 | 25.8832 | 25.3558 | 24.7937 | 24.2295 | 23.7179 | 23.1979 | 21.2474 | 18.1684 | 16.0116 | 27.7421 | 27.2926 | 26.8137 | 26.3168 | 25.7937 | 25.2358 | 24.6768 | 24.1653 | 23.6474 | 24.5895 | 23.0916 | 21.9979
|  | SHANKLIN PRIMARY | HT |  |  |  |  | 30.2474 | 29.7021 | 29.1505 | 28.5674 | 27.9116 | 27.2295 | 26.5674 | 25.9284 | 25.2937 | 22.1568 | 19.2516 | 16.76 | 26.9863 | 26.4011 | 25.8105 | 25.1842 | 24.4853 | 23.7547 | 23.0421 | 22.3526 | 21.6642 | 18.4705 | 15.3463 | 12.6084 | 27.5105 | 26.9242 | 26.3326 | 25.7074 | 25.0021 | 24.2663 | 23.5474 | 22.8505 | 22.1547 | 18.6874 | 15.4537 | 12.6516
|  | SHANKLIN PRIMARY | HE |  |  |  |  | 31.0958 | 30.8137 | 30.4968 | 30.1537 | 29.7684 | 29.3747 | 28.9853 | 28.6389 | 28.2726 | 32.3484 | 31.9337 | 6.5137 | 27.8474 | 27.5505 | 27.2179 | 26.8579 | 26.4568 | 26.0442 | 25.6337 | 25.2726 | 24.8842 | 24.2558 | 21.8821 | 20.4105 | 28.22 | 27.9484 | 27.6221 | 27.2684 | 26.8705 | 26.4621 | 26.0579 | 25.6989 | 25.3147 | 26.2874 | 25.3768 | 24.6337
|  | SHANKLIN PRIMARY | CF |  |  |  |  | 31.3863 | 31.2137 | 31.0147 | 30.7968 | 30.5474 | 30.2895 | 30.0411 | 29.8074 | 29.58 | 28.6937 | 27.6347 | 26.7021 | 28.1547 | 27.9716 | 27.9316 | 27.6947 | 27.4284 | 27.1505 | 26.8842 | 26.6347 | 26.3905 | 25.4568 | 24.2926 | 23.2621 | 28.4979 | 28.3337 | 28.5211 | 28.3432 | 28.1432 | 27.9358 | 27.7358 | 27.5453 | 27.3589 | 26.6084 | 24.6274 | 23.5653
AXMINSTER GSP | YEOVIL BSP | SHERBORNE PRIMARY | MINIMUM HEADROOM | ST 63978 18163 | NO | YES | 0 | 14.38 | 14.1074 | 13.8326 | 13.3768 | 13.0653 | 12.5032 | 11.9621 | 11.1147 | 10.1411 | 7.4611 | 5.9179 | -3.1074 | 14.9484 | 14.6642 | 14.3758 | 13.8768 | 13.5463 | 12.8947 | 12.2653 | 11.2432 | 10.0568 | 6.9379 | 5.2674 | 3.6558 | 14.6568 | 14.4821 | 14.2211 | 13.6979 | 13.3653 | 12.7232 | 12.1021 | 11.1021 | 9.9442 | 6.8516 | 5.1474 | 3.5505
|  | SHERBORNE PRIMARY | EE |  |  |  |  | 14.5516 | 14.3305 | 14.1053 | 13.6968 | 13.4316 | 12.9095 | 12.3937 | 11.5579 | 10.5979 | 7.9979 | 6.6126 | 5.5084 | 15.1316 | 14.8989 | 14.6642 | 14.2263 | 13.9589 | 13.3611 | 12.7663 | 11.7642 | 10.6011 | 7.6232 | 6.2 | 4.9305 | 14.7589 | 14.6116 | 14.4568 | 14.0558 | 13.7737 | 13.1779 | 12.5874 | 11.6042 | 10.4632 | 7.4832 | 5.9905 | 4.7242
|  | SHERBORNE PRIMARY | HT |  |  |  |  | 14.38 | 14.1074 | 13.8326 | 13.3768 | 13.0653 | 12.5032 | 11.9621 | 11.1147 | 10.1411 | 7.4611 | 5.9179 | 4.5305 | 14.9484 | 14.6642 | 14.3758 | 13.8768 | 13.5463 | 12.8947 | 12.2653 | 11.2432 | 10.0568 | 6.9379 | 5.2674 | 3.6558 | 14.6568 | 14.4821 | 14.2211 | 13.6979 | 13.3653 | 12.7232 | 12.1021 | 11.1021 | 9.9442 | 6.8516 | 5.1474 | 3.5505
|  | SHERBORNE PRIMARY | HE |  |  |  |  | 14.78 | 14.6316 | 14.4758 | 14.1347 | 13.9379 | 13.5011 | 13.0705 | 12.3305 | 11.4684 | 9.4242 | 8.6842 | -3.1074 | 15.3726 | 15.2179 | 15.0568 | 14.6884 | 14.4916 | 14.0211 | 13.5126 | 12.6063 | 11.54 | 9.0979 | 8.2747 | 7.3347 | 14.8905 | 14.7874 | 14.6737 | 14.5221 | 14.3379 | 13.8326 | 13.3326 | 12.4495 | 11.4126 | 9.0084 | 8.1768 | 7.24
|  | SHERBORNE PRIMARY | CF |  |  |  |  | 14.9105 | 14.8221 | 14.7305 | 14.5642 | 14.4547 | 14.2347 | 14.0042 | 13.5937 | 13.0811 | 11.7253 | 11.2389 | 10.7179 | 15.5095 | 15.4168 | 15.32 | 15.1411 | 15.0305 | 14.7947 | 14.5474 | 14.0726 | 13.4358 | 11.8021 | 11.2558 | 10.6537 | 14.98 | 14.9221 | 14.8611 | 14.7874 | 14.7116 | 14.6158 | 14.3811 | 13.8905 | 13.2726 | 11.6768 | 11.1274 | 10.5263
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE PRIMARY | MINIMUM HEADROOM | SP 03884 19102 | NO | YES | 0 | 4.8526 | 4.7695 | 4.68 | 4.5884 | 4.4926 | 4.3968 | 4.3074 | 4.2253 | 4.1537 | 3.7653 | 3.3726 | -0.94 | 3.9284 | 3.8368 | 3.7379 | 3.6379 | 3.5316 | 3.4253 | 3.3274 | 3.2347 | 3.1579 | 2.7158 | 2.2558 | 1.8432 | 4.0937 | 4.0011 | 3.9 | 3.7989 | 3.6905 | 3.5832 | 3.4832 | 3.3895 | 3.3105 | 2.8589 | 2.3926 | 1.9737
|  | SHIPTON OLIFFE PRIMARY | EE |  |  |  |  | 4.9053 | 4.8411 | 4.7705 | 4.6989 | 4.6263 | 4.5558 | 4.4884 | 4.4242 | 4.3684 | 4.0621 | 3.7516 | 3.4811 | 3.9863 | 3.9158 | 3.8389 | 3.7611 | 3.6821 | 3.6042 | 3.5305 | 3.4611 | 3.4 | 3.0516 | 2.6895 | 2.3684 | 4.1526 | 4.0811 | 4.0032 | 3.9242 | 3.8432 | 3.7653 | 3.6905 | 3.6189 | 3.5579 | 3.2021 | 2.8305 | 2.5053
|  | SHIPTON OLIFFE PRIMARY | HT |  |  |  |  | 4.8526 | 4.7695 | 4.68 | 4.5884 | 4.4926 | 4.3968 | 4.3074 | 4.2253 | 4.1537 | 3.7653 | 3.3726 | 3.0221 | 3.9284 | 3.8368 | 3.7379 | 3.6379 | 3.5316 | 3.4253 | 3.3274 | 3.2347 | 3.1579 | 2.7158 | 2.2558 | 1.8432 | 4.0937 | 4.0011 | 3.9 | 3.7989 | 3.6905 | 3.5832 | 3.4832 | 3.3895 | 3.3105 | 2.8589 | 2.3926 | 1.9737
|  | SHIPTON OLIFFE PRIMARY | HE |  |  |  |  | 4.9442 | 4.9189 | 4.8863 | 4.8337 | 4.78 | 4.7284 | 4.6779 | 4.6316 | 4.5937 | 4.3695 | 4.1316 | -0.94 | 4.0653 | 4.02 | 3.9674 | 3.9105 | 3.8516 | 3.7958 | 3.74 | 3.6905 | 3.6495 | 3.3926 | 3.1116 | 2.8705 | 4.2326 | 4.1874 | 4.1337 | 4.0758 | 4.0168 | 3.96 | 3.9032 | 3.8526 | 3.8105 | 3.5484 | 3.26 | 3.0137
|  | SHIPTON OLIFFE PRIMARY | CF |  |  |  |  | 4.9705 | 4.9568 | 4.9432 | 4.9284 | 4.9137 | 4.8937 | 4.8674 | 4.8379 | 4.8147 | 4.6579 | 4.5053 | 4.3821 | 4.1126 | 4.0874 | 4.06 | 4.0316 | 4.0032 | 3.9747 | 3.9453 | 3.9126 | 3.8874 | 3.7105 | 3.5305 | 3.3832 | 4.2811 | 4.2558 | 4.2274 | 4.1979 | 4.1695 | 4.14 | 4.1116 | 4.0779 | 4.0526 | 3.8716 | 3.6874 | 3.5358
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | SHIRLEY PRIMARY | MINIMUM HEADROOM | SU 39988 13808 | NO | YES | 0 | 34.7958 | 34.4316 | 34.0263 | 33.6063 | 33.1832 | 32.6758 | 32.1937 | 31.7368 | 31.2168 | 27.5768 | 24.5537 | -1.1295 | 30.0032 | 29.4032 | 28.6421 | 27.8674 | 27.1884 | 26.5189 | 25.9116 | 25.3253 | 24.6621 | 20.5947 | 17.2032 | 14.0895 | 30.8958 | 30.4895 | 29.7158 | 28.9295 | 28.2411 | 27.5632 | 26.9474 | 26.3526 | 25.6779 | 21.6147 | 18.2274 | 15.1179
|  | SHIRLEY PRIMARY | EE |  |  |  |  | 35.0011 | 34.7221 | 34.4021 | 34.0568 | 33.6895 | 33.3284 | 32.9316 | 32.5316 | 32.1737 | 29.7379 | 27.3874 | 25.28 | 30.3642 | 29.9305 | 29.3747 | 28.7695 | 28.0474 | 27.3137 | 26.7895 | 26.2874 | 25.8389 | 22.9789 | 20.3326 | 17.9421 | 31.1147 | 30.8221 | 30.4611 | 29.8474 | 29.1126 | 28.3653 | 27.8337 | 27.3253 | 26.8716 | 23.9958 | 21.3526 | 18.9663
|  | SHIRLEY PRIMARY | HT |  |  |  |  | 34.7958 | 34.4316 | 34.0263 | 33.6063 | 33.1832 | 32.6758 | 32.1937 | 31.7368 | 31.2168 | 27.5768 | 24.5537 | 21.7947 | 30.0032 | 29.4032 | 28.6421 | 27.8674 | 27.1884 | 26.5189 | 25.9116 | 25.3253 | 24.6621 | 20.5947 | 17.2032 | 14.0895 | 30.8958 | 30.4895 | 29.7158 | 28.9295 | 28.2411 | 27.5632 | 26.9474 | 26.3526 | 25.6779 | 21.6147 | 18.2274 | 15.1179
|  | SHIRLEY PRIMARY | HE |  |  |  |  | 35.2337 | 35.0221 | 34.7884 | 34.5368 | 34.2453 | 33.9537 | 33.6979 | 33.46 | 33.2547 | 32.2032 | 30.7189 | -1.1295 | 30.7537 | 30.4842 | 30.1358 | 29.7432 | 29.2053 | 28.6116 | 28.2411 | 27.8916 | 27.5905 | 25.8253 | 24.02 | 22.3358 | 31.3663 | 31.1463 | 30.9 | 30.6368 | 30.2905 | 29.6874 | 29.3126 | 28.9589 | 28.6547 | 26.8547 | 25.0358 | 23.3547
|  | SHIRLEY PRIMARY | CF |  |  |  |  | 35.4021 | 35.2821 | 35.1568 | 35.0274 | 34.8937 | 34.7568 | 34.6232 | 34.4895 | 34.3463 | 33.6863 | 33.1905 | 32.4779 | 30.9368 | 30.8032 | 30.6453 | 30.4611 | 30.2705 | 30.0789 | 29.8579 | 29.64 | 29.4221 | 28.1853 | 27.0095 | 25.9095 | 31.5411 | 31.4147 | 31.2842 | 31.1484 | 31.0084 | 30.8663 | 30.7253 | 30.5842 | 30.4453 | 29.2558 | 28.0516 | 26.9242
MINETY GSP | STRATTON (RESERVE) BSP | SHRIVENHAM PRIMARY | MINIMUM HEADROOM | SU 23782 87902 | NO | YES | 0 | 16.6168 | 16.52 | 16.4158 | 16.3105 | 16.2011 | 16.0916 | 15.9947 | 13.4126 | 13.3242 | 12.8853 | 11.8053 | 3.2168 | 14.6853 | 14.4811 | 14.2926 | 14.1021 | 13.9105 | 13.7221 | 13.5484 | 11.4116 | 11.2905 | 10.7884 | 9.5568 | 9.3789 | 15.2674 | 15.0632 | 14.8747 | 14.6842 | 14.4926 | 14.3042 | 14.1305 | 11.3789 | 11.26 | 10.7558 | 9.4874 | 9.3074
|  | SHRIVENHAM PRIMARY | EE |  |  |  |  | 16.6768 | 16.5958 | 16.5116 | 16.4242 | 16.3326 | 16.2453 | 16.1632 | 13.4126 | 13.3242 | 12.8853 | 11.8053 | 11.6347 | 14.8137 | 14.6453 | 14.4968 | 14.3411 | 14.1821 | 14.0316 | 13.8874 | 11.4116 | 11.2905 | 10.7916 | 9.5568 | 9.3789 | 15.3958 | 15.2274 | 15.0779 | 14.9221 | 14.7642 | 14.6137 | 14.4695 | 11.3789 | 11.26 | 10.7558 | 9.4874 | 9.3074
|  | SHRIVENHAM PRIMARY | HT |  |  |  |  | 16.6168 | 16.52 | 16.4158 | 16.3105 | 16.2011 | 16.0916 | 15.9947 | 13.7295 | 13.5947 | 13.0253 | 12.4495 | 11.7884 | 14.6853 | 14.4811 | 14.2926 | 14.1021 | 13.9105 | 13.7221 | 13.5484 | 11.5305 | 11.3863 | 10.7884 | 10.1537 | 9.4095 | 15.2674 | 15.0632 | 14.8747 | 14.6842 | 14.4926 | 14.3042 | 14.1305 | 11.6137 | 11.4684 | 10.8179 | 10.1832 | 9.4389
|  | SHRIVENHAM PRIMARY | HE |  |  |  |  | 16.7547 | 16.7 | 16.6389 | 16.5737 | 16.5042 | 16.4368 | 16.3737 | 15.0432 | 14.9937 | 14.8242 | 13.7295 | 3.2168 | 14.9821 | 14.8684 | 14.7695 | 14.66 | 14.5495 | 14.44 | 14.3379 | 13.0811 | 13.0011 | 12.6937 | 11.1747 | 11.0663 | 15.56 | 15.4505 | 15.3516 | 15.2421 | 15.1305 | 15.0221 | 14.9189 | 13.3463 | 13.2674 | 12.9579 | 11.4105 | 11.3021
|  | SHRIVENHAM PRIMARY | CF |  |  |  |  | 16.8084 | 16.7811 | 16.7516 | 16.7211 | 16.6905 | 16.6589 | 16.6274 | 15.3253 | 15.2937 | 15.1558 | 15.0874 | 15.0505 | 15.2189 | 15.1547 | 15.0979 | 15.0368 | 14.9779 | 14.9147 | 14.8537 | 13.6242 | 13.5653 | 13.3 | 13.1147 | 12.8832 | 15.7821 | 15.7211 | 15.6663 | 15.6084 | 15.5505 | 15.4905 | 15.4305 | 13.8779 | 13.82 | 13.5611 | 13.38 | 13.1453
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON PRIMARY | MINIMUM HEADROOM | ST 85356 13659 | NO | YES | 0 | 25.2389 | 24.6495 | 24.0284 | 23.1295 | 22.22 | 21.8032 | 21.4232 | 19.1611 | 18.9505 | 16.9095 | 14.3737 | -0.39895 | 22.5326 | 21.8937 | 21.2221 | 20.2337 | 19.2389 | 18.8063 | 18.4105 | 15.8337 | 15.6295 | 13.4432 | 10.6579 | 9.8116 | 22.6716 | 22.0832 | 21.4116 | 20.4 | 19.3789 | 18.9368 | 18.5316 | 15.9147 | 15.7042 | 13.4663 | 10.6147 | 9.7453
|  | SHROTON PRIMARY | EE |  |  |  |  | 25.5074 | 24.9968 | 24.4579 | 23.6379 | 22.7989 | 22.4579 | 22.1295 | 21.8095 | 21.5105 | 20.1979 | 18.6747 | 17.1526 | 22.8221 | 22.2695 | 21.6821 | 20.7768 | 19.8579 | 19.5063 | 19.1695 | 18.84 | 18.5358 | 17.2 | 15.6011 | 13.9147 | 22.94 | 22.4305 | 21.8789 | 20.9495 | 20.0042 | 19.6442 | 19.2958 | 18.9568 | 18.6411 | 17.24 | 15.5621 | 13.8389
|  | SHROTON PRIMARY | HT |  |  |  |  | 25.2389 | 24.6495 | 24.0284 | 23.1295 | 22.22 | 21.8032 | 21.4232 | 19.1611 | 18.9505 | 16.9095 | 14.3737 | 13.5589 | 22.5326 | 21.8937 | 21.2221 | 20.2337 | 19.2389 | 18.8063 | 18.4105 | 15.8337 | 15.6295 | 13.4432 | 10.6579 | 9.8116 | 22.6716 | 22.0832 | 21.4116 | 20.4 | 19.3789 | 18.9368 | 18.5316 | 15.9147 | 15.7042 | 13.4663 | 10.6147 | 9.7453
|  | SHROTON PRIMARY | HE |  |  |  |  | 25.8695 | 25.4747 | 25.0453 | 24.3263 | 23.5874 | 23.3516 | 23.1274 | 22.9147 | 22.7242 | 21.9621 | 20.9495 | -0.39895 | 23.2074 | 22.7768 | 22.3063 | 21.5084 | 20.6947 | 20.4516 | 20.2211 | 20.0021 | 19.8063 | 19.0242 | 17.9263 | 16.5905 | 23.3021 | 22.9084 | 22.4779 | 21.6979 | 20.86 | 20.6126 | 20.3779 | 20.1526 | 19.9537 | 19.1421 | 18.0042 | 16.6358
|  | SHROTON PRIMARY | CF |  |  |  |  | 26.2011 | 25.9937 | 25.7811 | 25.4537 | 25.1263 | 24.9916 | 24.86 | 24.7284 | 24.5968 | 23.9926 | 23.4284 | 22.8368 | 23.5674 | 23.3411 | 23.1074 | 22.7453 | 22.3842 | 22.2442 | 22.1063 | 21.9674 | 21.8295 | 21.1958 | 20.5895 | 19.9421 | 23.6326 | 23.4253 | 23.2126 | 22.8874 | 22.5611 | 22.4263 | 22.2958 | 22.1642 | 22.0242 | 21.3747 | 20.7484 | 20.0747
LALEHAM GSP | STAINES BSP | SIDNEY ROAD PRIMARY | MINIMUM HEADROOM | TQ 04100 71760 | NO | YES | 0 | 34.0611 | 33.8263 | 33.5768 | 33.3179 | 33.0516 | 32.7832 | 32.5474 | 32.3326 | 32.1211 | 30.4621 | 28.7495 | 6.44 | 30.2779 | 29.5779 | 29.0274 | 28.58 | 28.1389 | 27.7011 | 27.2958 | 26.9158 | 26.5463 | 24.3221 | 22.3168 | 20.4337 | 31.2137 | 30.8958 | 30.3505 | 29.9074 | 29.4695 | 29.0358 | 28.6326 | 28.2568 | 27.8905 | 25.6495 | 23.6474 | 21.7663
|  | SIDNEY ROAD PRIMARY | EE |  |  |  |  | 34.2021 | 34.0105 | 33.8053 | 33.5916 | 33.3695 | 33.1558 | 32.9516 | 32.7558 | 32.5811 | 31.6853 | 30.3653 | 29.1779 | 30.5811 | 29.9716 | 29.5105 | 29.1505 | 28.7916 | 28.4453 | 28.1074 | 27.7821 | 27.4695 | 25.6968 | 24.1516 | 22.7358 | 31.3642 | 31.1474 | 30.8295 | 30.4726 | 30.1158 | 29.7726 | 29.4368 | 29.1137 | 28.8042 | 27.0326 | 25.48 | 24.0663
|  | SIDNEY ROAD PRIMARY | HT |  |  |  |  | 34.0611 | 33.8263 | 33.5768 | 33.3179 | 33.0516 | 32.7832 | 32.5474 | 32.3326 | 32.1211 | 30.4621 | 28.7495 | 27.1589 | 30.2779 | 29.5779 | 29.0274 | 28.58 | 28.1389 | 27.7011 | 27.2958 | 26.9158 | 26.5463 | 24.3221 | 22.3168 | 20.4337 | 31.2137 | 30.8958 | 30.3505 | 29.9074 | 29.4695 | 29.0358 | 28.6326 | 28.2568 | 27.8905 | 25.6495 | 23.6474 | 21.7663
|  | SIDNEY ROAD PRIMARY | HE |  |  |  |  | 34.3758 | 34.2368 | 34.0821 | 33.9168 | 33.74 | 33.5705 | 33.4116 | 33.2632 | 33.1347 | 32.7011 | 32.3053 | 6.44 | 30.8358 | 30.4821 | 30.1347 | 29.8853 | 29.6274 | 29.3811 | 29.1421 | 28.9179 | 28.7053 | 27.4179 | 26.3442 | 25.3874 | 31.5505 | 31.3905 | 31.2253 | 31.0547 | 30.8726 | 30.6968 | 30.46 | 30.2368 | 30.0263 | 28.7558 | 27.6821 | 26.7147
|  | SIDNEY ROAD PRIMARY | CF |  |  |  |  | 34.4947 | 34.4179 | 34.3389 | 34.2558 | 34.1705 | 34.0842 | 33.9979 | 33.9137 | 33.8284 | 33.4516 | 33.2632 | 33.1389 | 30.9705 | 30.8842 | 30.8 | 30.7105 | 30.54 | 30.3421 | 30.1726 | 30.0189 | 29.8589 | 28.8789 | 28.1221 | 27.4663 | 31.6863 | 31.5989 | 31.5147 | 31.4253 | 31.3316 | 31.2389 | 31.1474 | 31.0589 | 30.9695 | 30.2021 | 29.4568 | 28.8116
NURSLING GSP | ROWNHAMS BSP | SILKSTEAD PRIMARY | MINIMUM HEADROOM | SU 44578 24565 | NO | YES | 0 | 10.3979 | 10.2337 | 10.0611 | 9.4105 | 8.7221 | 8.0442 | 7.2421 | 7.0537 | 6.8747 | 3.1021 | 0.93368 | -25.5084 | 8.0126 | 7.8495 | 7.6768 | 6.9432 | 6.18 | 5.4295 | 4.5316 | 4.3537 | 4.1842 | -0.028421 | -2.3589 | -3.1137 | 8.5632 | 8.3989 | 8.2263 | 7.4926 | 6.7221 | 5.9621 | 5.0547 | 4.8674 | 4.6874 | 0.40421 | -2.0074 | -2.7937
|  | SILKSTEAD PRIMARY | EE |  |  |  |  | 10.4895 | 10.3526 | 10.2074 | 10.0579 | 9.8747 | 9.6832 | 9.4937 | 9.3053 | 9.1242 | 7.2347 | 3.9937 | 2.6842 | 8.1042 | 7.9674 | 7.8242 | 7.6747 | 7.4989 | 7.3189 | 7.1411 | 6.9653 | 6.7989 | 4.8253 | 1.2705 | -0.16 | 8.6547 | 8.5179 | 8.3726 | 8.2232 | 8.04 | 7.8484 | 7.6589 | 7.4695 | 7.2884 | 5.2179 | 1.5495 | 0.084211
|  | SILKSTEAD PRIMARY | HT |  |  |  |  | 10.3979 | 10.2337 | 10.0611 | 9.4105 | 8.7221 | 8.0442 | 7.2421 | 7.0537 | 6.8747 | 3.1021 | 0.93368 | 0.18947 | 8.0126 | 7.8495 | 7.6768 | 6.9432 | 6.18 | 5.4295 | 4.5316 | 4.3537 | 4.1842 | -0.028421 | -2.3589 | -3.1137 | 8.5632 | 8.3989 | 8.2263 | 7.4926 | 6.7221 | 5.9621 | 5.0547 | 4.8674 | 4.6874 | 0.40421 | -2.0074 | -2.7937
|  | SILKSTEAD PRIMARY | HE |  |  |  |  | 10.6211 | 10.5305 | 10.4305 | 10.3263 | 10.1884 | 10.0579 | 9.9316 | 9.8105 | 9.7011 | 8.6642 | 6.1937 | -25.5084 | 8.2358 | 8.1453 | 8.0453 | 7.9411 | 7.8095 | 7.6832 | 7.5632 | 7.4474 | 7.3453 | 6.2463 | 3.4305 | 2.3274 | 8.7863 | 8.6958 | 8.5958 | 8.4916 | 8.3537 | 8.2232 | 8.0958 | 7.9747 | 7.8653 | 6.7274 | 3.8789 | 2.7463
|  | SILKSTEAD PRIMARY | CF |  |  |  |  | 11.8274 | 10.6263 | 10.5674 | 10.5063 | 10.4305 | 10.3558 | 10.2821 | 10.2074 | 10.1379 | 9.54 | 8.6642 | 7.8747 | 10.5305 | 8.2411 | 8.1821 | 8.1211 | 8.0484 | 7.9758 | 7.9053 | 7.8337 | 7.7653 | 7.1368 | 6.1684 | 5.2979 | 10.8684 | 8.7916 | 8.7326 | 8.6716 | 8.5958 | 8.5211 | 8.4474 | 8.3726 | 8.3032 | 7.66 | 6.6747 | 5.7842
BRAMLEY (BASI) GSP | READING BSP | SILVER STREET PRIMARY | MINIMUM HEADROOM | SU 71957 72821 | NO | YES | 0 | 32.7642 | 32.5421 | 32.3063 | 32.0568 | 31.7137 | 30.1347 | 28.5695 | 27.8011 | 27.0495 | 24.9379 | 22.9789 | 0.99895 | 28.5989 | 27.9895 | 26.98 | 25.7905 | 24.7453 | 22.9042 | 21.1042 | 20.2389 | 19.3905 | 17.06 | 14.8758 | 12.7084 | 29.1905 | 28.9421 | 28.1432 | 26.9547 | 25.9116 | 24.0726 | 22.2768 | 21.4116 | 20.5642 | 18.2368 | 16.0558 | 13.8916
|  | SILVER STREET PRIMARY | EE |  |  |  |  | 32.9063 | 32.7284 | 32.5389 | 32.3347 | 32.12 | 31.3979 | 30.0168 | 28.8221 | 28.0421 | 26.2116 | 24.7158 | 23.2505 | 28.8232 | 28.3716 | 27.4526 | 26.3537 | 25.5916 | 24.3411 | 22.7347 | 21.3642 | 20.4779 | 18.4453 | 16.7747 | 15.1179 | 29.3411 | 29.14 | 28.6189 | 27.5179 | 26.7568 | 25.5074 | 23.9042 | 22.5358 | 21.6505 | 19.6211 | 17.9526 | 16.2989
|  | SILVER STREET PRIMARY | HT |  |  |  |  | 32.7642 | 32.5421 | 32.3063 | 32.0568 | 31.7137 | 30.1347 | 28.5695 | 27.8011 | 27.0495 | 24.9379 | 22.9789 | 21.0516 | 28.5989 | 27.9895 | 26.98 | 25.7905 | 24.7453 | 22.9042 | 21.1042 | 20.2389 | 19.3905 | 17.06 | 14.8758 | 12.7084 | 29.1905 | 28.9421 | 28.1432 | 26.9547 | 25.9116 | 24.0726 | 22.2768 | 21.4116 | 20.5642 | 18.2368 | 16.0558 | 13.8916
|  | SILVER STREET PRIMARY | HE |  |  |  |  | 33.0179 | 32.8684 | 32.7032 | 32.5253 | 32.3358 | 32.0347 | 30.6579 | 29.6158 | 28.9516 | 27.6221 | 26.6063 | 0.99895 | 29.0137 | 28.7074 | 27.9432 | 26.94 | 26.2474 | 25.0589 | 23.4389 | 22.2421 | 21.4842 | 20.0053 | 18.8642 | 17.7537 | 29.4653 | 29.2958 | 29.0905 | 28.1032 | 27.4116 | 26.2253 | 24.6074 | 23.4126 | 22.6568 | 21.18 | 20.04 | 18.9316
|  | SILVER STREET PRIMARY | CF |  |  |  |  | 33.1063 | 33.0095 | 32.9095 | 32.8063 | 32.7 | 32.5905 | 32.4832 | 32.3779 | 32.2716 | 30.8726 | 30.1474 | 29.4758 | 29.1095 | 28.9968 | 28.7263 | 28.2979 | 28.1126 | 27.9263 | 27.6484 | 27.2084 | 26.6979 | 23.7284 | 22.9137 | 22.1474 | 29.5611 | 29.4526 | 29.3337 | 29.2084 | 29.0979 | 28.9832 | 28.82 | 28.3747 | 27.8611 | 24.8968 | 24.0832 | 23.3179
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD PRIMARY | MINIMUM HEADROOM | SZ 18262 93590 | NO | YES | 0 | 24.8621 | 24.3389 | 23.7811 | 22.54 | 21.5884 | 20.5758 | 19.6116 | 18.6495 | 17.7316 | 13.5516 | 9.6821 | -21.1526 | 18.5074 | 17.0432 | 15.3526 | 13.5253 | 12.5253 | 11.4589 | 10.4358 | 9.4116 | 8.4253 | 3.8568 | -0.42105 | -4.3368 | 20.1863 | 18.7126 | 16.9842 | 15.1168 | 14.1042 | 13.02 | 11.98 | 10.9358 | 9.9358 | 5.3495 | 1.0495 | -2.8705
|  | SOMERFORD PRIMARY | EE |  |  |  |  | 25.1758 | 24.7463 | 24.2895 | 23.7284 | 22.9611 | 22.16 | 21.3863 | 20.64 | 19.8716 | 16.5705 | 13.5347 | 10.8705 | 19.1768 | 17.9158 | 16.4305 | 14.7926 | 13.9895 | 13.1484 | 12.3347 | 11.5505 | 10.7347 | 7.1916 | 3.8474 | 0.85263 | 20.84 | 19.5989 | 18.08 | 16.4074 | 15.5926 | 14.7368 | 13.9105 | 13.1105 | 12.2789 | 8.6663 | 5.2884 | 2.2874
|  | SOMERFORD PRIMARY | HT |  |  |  |  | 24.8621 | 24.3389 | 23.7811 | 22.54 | 21.5884 | 20.5758 | 19.6116 | 18.6495 | 17.7316 | 13.5516 | 9.6821 | 6.1821 | 18.5074 | 17.0432 | 15.3526 | 13.5253 | 12.5253 | 11.4589 | 10.4358 | 9.4116 | 8.4253 | 3.8568 | -0.42105 | -4.3368 | 20.1863 | 18.7126 | 16.9842 | 15.1168 | 14.1042 | 13.02 | 11.98 | 10.9358 | 9.9358 | 5.3495 | 1.0495 | -2.8705
|  | SOMERFORD PRIMARY | HE |  |  |  |  | 25.5821 | 25.2779 | 24.9421 | 24.5811 | 24.1884 | 23.8147 | 23.4611 | 23.0621 | 22.5032 | 20.2516 | 18.2263 | -21.1526 | 20.0611 | 19.0726 | 17.8474 | 16.4579 | 15.8853 | 15.2758 | 14.7011 | 14.1337 | 13.54 | 11.1232 | 8.8968 | 6.8579 | 21.6558 | 20.7442 | 19.5221 | 18.1011 | 17.52 | 16.9021 | 16.3189 | 15.7432 | 15.1379 | 12.6663 | 10.3905 | 8.3432
|  | SOMERFORD PRIMARY | CF |  |  |  |  | 25.8621 | 25.7011 | 25.5337 | 25.3611 | 25.18 | 24.9947 | 24.8126 | 24.6326 | 24.4537 | 23.6474 | 23.0368 | 21.82 | 20.7716 | 20.2442 | 19.6379 | 18.98 | 18.6326 | 18.2474 | 17.8579 | 17.4947 | 17.1453 | 15.6168 | 14.0968 | 12.7484 | 21.9611 | 21.7779 | 21.2958 | 20.66 | 20.32 | 19.9326 | 19.5358 | 19.1653 | 18.8105 | 17.2558 | 15.6958 | 14.3084
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | SOUTH BERSTED PRIMARY | MINIMUM HEADROOM | SU 94025 00705 | NO | YES | 0 | 33.8695 | 33.46 | 33.0253 | 32.5758 | 32.1063 | 31.6337 | 31.2168 | 30.8347 | 30.4821 | 26.78 | 21.9463 | -4.3579 | 29.4295 | 28.6242 | 27.8011 | 26.9779 | 26.1484 | 25.3242 | 24.5832 | 23.8621 | 23.1821 | 18.6053 | 13.14 | 7.54 | 27.6768 | 26.8779 | 26.06 | 25.2421 | 24.4168 | 23.5958 | 22.8568 | 22.14 | 21.4611 | 16.9147 | 11.4979 | 5.9632
|  | SOUTH BERSTED PRIMARY | EE |  |  |  |  | 34.1168 | 33.7811 | 33.4253 | 33.0516 | 32.66 | 32.2789 | 31.9158 | 31.5653 | 31.2505 | 29.4705 | 25.7611 | 21.8274 | 29.9674 | 29.3253 | 28.6642 | 27.9979 | 27.3116 | 26.6442 | 26.02 | 25.4221 | 24.8684 | 21.6021 | 17.4211 | 12.9074 | 28.2105 | 27.5726 | 26.9158 | 26.2537 | 25.5705 | 24.9053 | 24.2811 | 23.6853 | 23.1305 | 19.8716 | 15.7126 | 11.2495
|  | SOUTH BERSTED PRIMARY | HT |  |  |  |  | 33.8695 | 33.46 | 33.0253 | 32.5758 | 32.1063 | 31.6337 | 31.2168 | 30.8347 | 30.4821 | 26.78 | 21.9463 | 17.0516 | 29.4295 | 28.6242 | 27.8011 | 26.9779 | 26.1484 | 25.3242 | 24.5832 | 23.8621 | 23.1821 | 18.6053 | 13.14 | 7.54 | 27.6768 | 26.8779 | 26.06 | 25.2421 | 24.4168 | 23.5958 | 22.8568 | 22.14 | 21.4611 | 16.9147 | 11.4979 | 5.9632
|  | SOUTH BERSTED PRIMARY | HE |  |  |  |  | 34.4284 | 34.1895 | 33.9253 | 33.6411 | 33.3316 | 33.0379 | 32.76 | 32.5 | 32.2737 | 31.4947 | 29.4 | -4.3579 | 30.6642 | 30.2368 | 29.7811 | 29.3116 | 28.8063 | 28.3221 | 27.8779 | 27.4632 | 27.0895 | 24.6684 | 21.3295 | 17.5758 | 28.9011 | 28.4768 | 28.0242 | 27.5579 | 27.0526 | 26.5705 | 26.1274 | 25.7137 | 25.3411 | 22.9358 | 19.6326 | 15.9253
|  | SOUTH BERSTED PRIMARY | CF |  |  |  |  | 34.6474 | 34.52 | 34.3884 | 34.2526 | 34.1084 | 33.9632 | 33.82 | 33.6768 | 33.5347 | 32.9 | 32.5726 | 31.6547 | 30.9421 | 30.8074 | 30.5653 | 30.3063 | 30.0368 | 29.7653 | 29.4979 | 29.2179 | 28.9547 | 27.5347 | 26.0147 | 23.7326 | 29.3105 | 29.0568 | 28.8032 | 28.5463 | 28.2779 | 28.0074 | 27.7421 | 27.4632 | 27.2011 | 25.7884 | 24.2832 | 22.0295
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE PRIMARY | MINIMUM HEADROOM | SZ 13563 92074 | NO | YES | 0 | 17.5926 | 17.2295 | 16.8432 | 16.4063 | 16.5032 | 16.1095 | 15.5589 | 15.0126 | 14.3284 | 11.1579 | 8.2453 | -8.5621 | 14.2926 | 13.5989 | 12.8895 | 12.1789 | 12.4958 | 11.8768 | 11.2737 | 10.6874 | 10.0537 | 6.6379 | 3.3937 | 0.35789 | 14.9 | 14.2063 | 13.4979 | 12.7874 | 13.1032 | 12.4853 | 11.8821 | 11.2958 | 10.5589 | 7.06 | 3.8105 | 0.77368
|  | SOUTHBOURNE PRIMARY | EE |  |  |  |  | 17.8063 | 17.5074 | 17.1884 | 16.8526 | 16.5032 | 16.1095 | 15.5589 | 15.0126 | 14.4316 | 13.4189 | 11.1568 | 9.1011 | 14.7558 | 14.2095 | 13.6442 | 13.0684 | 12.4958 | 11.8768 | 11.2737 | 10.6874 | 10.0537 | 9.1347 | 6.6084 | 4.2874 | 15.3695 | 14.8168 | 14.2516 | 13.6768 | 13.1032 | 12.4853 | 11.8821 | 11.2958 | 10.6611 | 9.5547 | 7.0242 | 4.7021
|  | SOUTHBOURNE PRIMARY | HT |  |  |  |  | 17.5926 | 17.2295 | 16.8432 | 16.4063 | 17.2147 | 16.4821 | 15.7705 | 15.0358 | 14.3284 | 11.1579 | 8.2453 | 5.5421 | 14.2926 | 13.5989 | 12.8895 | 12.1789 | 13.2726 | 12.4853 | 11.7126 | 10.9095 | 10.1347 | 6.6379 | 3.3937 | 0.35789 | 14.9 | 14.2063 | 13.4979 | 12.7874 | 13.7 | 12.9105 | 12.1389 | 11.3347 | 10.5589 | 7.06 | 3.8105 | 0.77368
|  | SOUTHBOURNE PRIMARY | HE |  |  |  |  | 18.0642 | 17.8411 | 17.5947 | 17.3295 | 17.0463 | 16.7758 | 16.52 | 16.2811 | 16.0747 | 15.8916 | 14.3253 | -8.5621 | 15.2705 | 14.9695 | 14.5926 | 14.1968 | 13.7811 | 13.3189 | 12.8832 | 12.4453 | 11.9663 | 11.8316 | 10.0674 | 8.4779 | 15.6642 | 15.4316 | 15.1758 | 14.8042 | 14.3884 | 13.9253 | 13.4895 | 13.0537 | 12.5737 | 12.2568 | 10.4895 | 8.8989
|  | SOUTHBOURNE PRIMARY | CF |  |  |  |  | 18.2474 | 18.1221 | 17.9916 | 17.8568 | 17.7179 | 17.5747 | 17.4347 | 17.2968 | 17.1589 | 16.54 | 16.9284 | 15.9842 | 15.4611 | 15.3305 | 15.1821 | 14.9516 | 14.6947 | 14.3937 | 14.0789 | 13.7905 | 13.5158 | 12.3263 | 12.9 | 11.8221 | 15.8558 | 15.7242 | 15.5863 | 15.4453 | 15.2979 | 15.0011 | 14.6863 | 14.3968 | 14.1221 | 12.9347 | 13.3253 | 12.2463
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | SOUTHCOTE PRIMARY | MINIMUM HEADROOM | SU 68199 71325 | NO | YES | 5.2632 | 12.1979 | 11.9916 | 11.7726 | 11.4663 | 10.84 | 10.2684 | 9.9179 | 9.5895 | 9.2811 | 7.9221 | 6.4926 | -6.6863 | 9.7842 | 9.3916 | 8.9895 | 8.3326 | 7.6368 | 7.0074 | 6.6326 | 6.28 | 5.9474 | 4.4747 | 2.8905 | 1.3737 | 10.3011 | 9.9084 | 9.5063 | 8.8484 | 8.1537 | 7.5232 | 7.1484 | 6.7958 | 6.4632 | 4.9905 | 3.4053 | 1.8884
|  | SOUTHCOTE PRIMARY | EE |  |  |  |  | 12.3116 | 12.14 | 11.9558 | 11.7653 | 11.5021 | 10.9832 | 10.5905 | 10.2589 | 9.9937 | 8.9505 | 7.8663 | 6.8442 | 10.0295 | 9.7305 | 9.4042 | 8.9211 | 8.3705 | 7.7947 | 7.3663 | 7.0074 | 6.7232 | 5.5979 | 4.3926 | 3.2432 | 10.56 | 10.2463 | 9.92 | 9.4379 | 8.8874 | 8.3105 | 7.8821 | 7.5232 | 7.2389 | 6.1137 | 4.9084 | 3.7579
|  | SOUTHCOTE PRIMARY | HT |  |  |  |  | 12.1979 | 11.9916 | 11.7726 | 11.4663 | 10.84 | 10.2684 | 9.9179 | 9.5895 | 9.2811 | 7.9221 | 6.4926 | 5.1379 | 9.7842 | 9.3916 | 8.9895 | 8.3326 | 7.6368 | 7.0074 | 6.6326 | 6.28 | 5.9474 | 4.4747 | 2.8905 | 1.3737 | 10.3011 | 9.9084 | 9.5063 | 8.8484 | 8.1537 | 7.5232 | 7.1484 | 6.7958 | 6.4632 | 4.9905 | 3.4053 | 1.8884
|  | SOUTHCOTE PRIMARY | HE |  |  |  |  | 12.4674 | 12.3421 | 12.2032 | 12.0547 | 11.8968 | 11.7442 | 11.4368 | 11.2 | 11.0168 | 10.3768 | 9.6716 | -6.6863 | 10.3579 | 10.1611 | 9.9495 | 9.5779 | 9.1126 | 8.6263 | 8.2884 | 8.0326 | 7.8379 | 7.1537 | 6.3653 | 5.6158 | 10.8463 | 10.6853 | 10.4832 | 10.0937 | 9.6295 | 9.1432 | 8.8042 | 8.5484 | 8.3537 | 7.6705 | 6.8811 | 6.1316
|  | SOUTHCOTE PRIMARY | CF |  |  |  |  | 12.5758 | 12.5074 | 12.4368 | 12.3632 | 12.2884 | 12.2105 | 12.1347 | 12.06 | 11.9853 | 11.5316 | 11.04 | 10.5863 | 10.4937 | 10.4074 | 10.2937 | 10.1653 | 10.0368 | 9.9042 | 9.7526 | 9.5463 | 9.3326 | 8.3916 | 7.8421 | 7.3263 | 10.96 | 10.8884 | 10.8126 | 10.6916 | 10.5695 | 10.4316 | 10.2684 | 10.0632 | 9.8484 | 8.9074 | 8.3589 | 7.8421
EALING GSP |  | SOUTHFIELD ROAD PRIMARY | MINIMUM HEADROOM | TQ 20533 79746 | NO | YES | 0 | 69.3305 | 68.8947 | 67.5389 | 64.2832 | 62.8947 | 60.6411 | 58.4137 | 57.7495 | 57.1189 | 53.5189 | 49.5337 | 0.29789 | 60.3863 | 57.5505 | 54.08 | 50.3432 | 48.6989 | 46.1263 | 43.5811 | 42.8705 | 42.2063 | 38.3989 | 33.9495 | 29.5768 | 62.5084 | 60.1684 | 56.6968 | 52.9589 | 51.3147 | 48.7411 | 46.1947 | 45.4842 | 44.82 | 41.0126 | 36.5621 | 32.1884
|  | SOUTHFIELD ROAD PRIMARY | EE |  |  |  |  | 69.5895 | 69.2326 | 68.7947 | 66.0263 | 62.8947 | 60.6411 | 58.4137 | 57.7495 | 57.1316 | 54.4747 | 51.6653 | 48.9621 | 61.0116 | 58.5011 | 55.48 | 52.3011 | 48.6989 | 46.1263 | 43.5811 | 42.8705 | 42.2063 | 39.3221 | 36.1926 | 33.1474 | 62.7895 | 61.12 | 58.0979 | 54.9179 | 51.3147 | 48.7411 | 46.1947 | 45.4842 | 44.82 | 41.9358 | 38.8063 | 35.76
|  | SOUTHFIELD ROAD PRIMARY | HT |  |  |  |  | 69.3305 | 68.8947 | 67.5389 | 64.2832 | 63.7737 | 61.1611 | 58.6305 | 57.8558 | 57.1189 | 53.5189 | 49.5337 | 45.6484 | 60.3863 | 57.5505 | 54.08 | 50.3432 | 49.8337 | 46.8558 | 43.9653 | 43.1305 | 42.3337 | 38.3989 | 33.9495 | 29.5768 | 62.5084 | 60.1684 | 56.6968 | 52.9589 | 52.4495 | 49.4705 | 46.58 | 45.7453 | 44.9484 | 41.0126 | 36.5621 | 32.1884
|  | SOUTHFIELD ROAD PRIMARY | HE |  |  |  |  | 69.8295 | 69.5358 | 69.2126 | 67.1137 | 64.1326 | 62.0368 | 59.9705 | 59.4842 | 59.0526 | 57.3274 | 55.4589 | 0.29789 | 61.66 | 59.3432 | 56.5032 | 53.5053 | 50.0705 | 47.6716 | 45.3032 | 44.7863 | 44.3274 | 42.4653 | 40.3747 | 38.3758 | 63.0526 | 61.9621 | 59.1211 | 56.1221 | 52.6863 | 50.2863 | 47.9179 | 47.4011 | 46.9421 | 45.08 | 42.9884 | 40.9884
|  | SOUTHFIELD ROAD PRIMARY | CF |  |  |  |  | 70.0032 | 69.8158 | 69.6211 | 69.42 | 69.2116 | 68.9989 | 67.92 | 67.5695 | 67.2158 | 65.4958 | 64.1916 | 63.0137 | 62.1716 | 61.2526 | 59.8779 | 58.4853 | 56.9516 | 55.7274 | 54.4653 | 54.0895 | 53.7105 | 51.8516 | 50.4021 | 49.0642 | 63.2389 | 63.0158 | 62.4968 | 61.1042 | 59.5695 | 58.3442 | 57.0821 | 56.7074 | 56.3284 | 54.4684 | 53.0189 | 51.6811
AXMINSTER GSP | YEOVIL BSP | SPARKFORD PRIMARY | MINIMUM HEADROOM | ST 60767 25496 | NO | YES | 0 | 6.04 | 5.9326 | 5.8232 | 5.7137 | 5.6042 | 5.4937 | 5.3958 | 5.3032 | 5.2158 | 3.2242 | 3.0695 | -0.81789 | 4.9916 | 4.8758 | 4.7579 | 4.6411 | 4.5242 | 4.4084 | 4.3032 | 4.2032 | 4.1105 | 1.8095 | 1.6568 | 1.54 | 5.3611 | 5.2453 | 5.1274 | 5.0105 | 4.8937 | 4.7768 | 4.6705 | 4.5716 | 4.4779 | 2.1747 | 2.02 | 1.9021
|  | SPARKFORD PRIMARY | EE |  |  |  |  | 6.1126 | 6.0284 | 5.94 | 5.8495 | 5.76 | 5.6716 | 5.5895 | 5.5095 | 5.4347 | 5.0811 | 4.3937 | 4.3158 | 5.0705 | 4.9789 | 4.8842 | 4.7884 | 4.6926 | 4.6 | 4.5116 | 4.4263 | 4.3474 | 3.9642 | 3.1811 | 3.1042 | 5.44 | 5.3484 | 5.2537 | 5.1579 | 5.0621 | 4.9684 | 4.8811 | 4.7947 | 4.7147 | 4.3295 | 3.5432 | 3.4653
|  | SPARKFORD PRIMARY | HT |  |  |  |  | 6.04 | 5.9326 | 5.8232 | 5.7137 | 5.6042 | 5.4937 | 5.3958 | 5.3032 | 5.2158 | 3.2242 | 3.0695 | 2.9516 | 4.9916 | 4.8758 | 4.7579 | 4.6411 | 4.5242 | 4.4084 | 4.3032 | 4.2032 | 4.1105 | 1.8095 | 1.6568 | 1.54 | 5.3611 | 5.2453 | 5.1274 | 5.0105 | 4.8937 | 4.7768 | 4.6705 | 4.5716 | 4.4779 | 2.1747 | 2.02 | 1.9021
|  | SPARKFORD PRIMARY | HE |  |  |  |  | 6.2095 | 6.1547 | 6.0958 | 6.0337 | 5.9674 | 5.9053 | 5.8484 | 5.7905 | 5.7421 | 5.5042 | 4.6653 | -0.81789 | 5.1747 | 5.1168 | 5.0537 | 4.9884 | 4.9179 | 4.8537 | 4.7926 | 4.7326 | 4.68 | 4.4211 | 3.4474 | 3.4095 | 5.5442 | 5.4863 | 5.4232 | 5.3568 | 5.2874 | 5.2221 | 5.1611 | 5.1 | 5.0495 | 4.7884 | 3.8147 | 3.7747
|  | SPARKFORD PRIMARY | CF |  |  |  |  | 6.2684 | 6.2358 | 6.2042 | 6.1705 | 6.1358 | 6.1 | 6.0653 | 6.0316 | 5.9968 | 5.8179 | 5.6747 | 5.5095 | 5.2379 | 5.2032 | 5.1684 | 5.1326 | 5.0947 | 5.0568 | 5.02 | 4.9832 | 4.9463 | 4.7495 | 4.5916 | 4.4021 | 5.6074 | 5.5726 | 5.5379 | 5.5021 | 5.4642 | 5.4263 | 5.3895 | 5.3526 | 5.3147 | 5.1189 | 4.96 | 4.7695
MELKSHAM GSP | NORRINGTON BSP | SPRING QUARRY WEST PRIMARY | MINIMUM HEADROOM | ST 84368 68717 | NO | YES | 0 | 32.3863 | 32.16 | 31.9274 | 31.5832 | 31.1421 | 30.7011 | 30.2789 | 29.9747 | 29.7526 | 26.9905 | 25.9663 | 12.8684 | 29.1958 | 28.9526 | 28.7074 | 28.3295 | 27.8463 | 27.3621 | 26.8989 | 26.5674 | 26.3316 | 23.1853 | 22.0842 | 21.68 | 29.5411 | 29.3705 | 29.1558 | 28.7737 | 28.2811 | 27.7884 | 27.3158 | 26.9789 | 26.7411 | 23.5726 | 22.4411 | 22.0232
|  | SPRING QUARRY WEST PRIMARY | EE |  |  |  |  | 32.5379 | 32.3558 | 32.1705 | 31.8684 | 31.4663 | 31.0737 | 30.6811 | 30.3916 | 30.2179 | 29.2726 | 28.2653 | 27.3684 | 29.3589 | 29.1653 | 28.9968 | 28.6611 | 28.2126 | 27.7758 | 27.34 | 27.0263 | 26.8474 | 25.8526 | 24.7726 | 23.7653 | 29.6474 | 29.5105 | 29.42 | 29.0853 | 28.6337 | 28.1937 | 27.7537 | 27.4347 | 27.2495 | 26.2189 | 25.0958 | 24.0758
|  | SPRING QUARRY WEST PRIMARY | HT |  |  |  |  | 32.3863 | 32.16 | 31.9274 | 31.5832 | 31.1421 | 30.7011 | 30.2789 | 29.9747 | 29.7526 | 26.9905 | 25.9663 | 25.5674 | 29.1958 | 28.9526 | 28.7074 | 28.3295 | 27.8463 | 27.3621 | 26.8989 | 26.5674 | 26.3316 | 23.1853 | 22.0842 | 21.68 | 29.5411 | 29.3705 | 29.1558 | 28.7737 | 28.2811 | 27.7884 | 27.3158 | 26.9789 | 26.7411 | 23.5726 | 22.4411 | 22.0232
|  | SPRING QUARRY WEST PRIMARY | HE |  |  |  |  | 32.7411 | 32.6242 | 32.5 | 32.2558 | 31.9095 | 31.5716 | 31.2379 | 31.0105 | 30.9011 | 30.2884 | 29.5537 | 12.8684 | 29.5789 | 29.4547 | 29.3232 | 29.0842 | 28.6947 | 28.3147 | 27.94 | 27.6895 | 27.5758 | 26.9189 | 26.0947 | 25.4021 | 29.7916 | 29.7 | 29.6 | 29.5074 | 29.1168 | 28.7358 | 28.3579 | 28.1063 | 27.9895 | 27.3189 | 26.4832 | 25.7789
|  | SPRING QUARRY WEST PRIMARY | CF |  |  |  |  | 32.8568 | 32.7863 | 32.7158 | 32.5979 | 32.4337 | 32.2537 | 32.0737 | 31.9432 | 31.8674 | 31.5074 | 31.1253 | 30.6916 | 29.7011 | 29.6263 | 29.5505 | 29.4211 | 29.2389 | 29.04 | 28.84 | 28.6968 | 28.6168 | 28.2379 | 27.8211 | 27.3379 | 29.8811 | 29.8295 | 29.7758 | 29.7021 | 29.6063 | 29.4874 | 29.2832 | 29.1379 | 29.0558 | 28.6684 | 28.2389 | 27.74
NORTH HYDE GSP | NORTH HYDE BSP | SPRINGFIELD ROAD PRIMARY | MINIMUM HEADROOM | TQ 11409 80620 | NO | NO | 0.015789 | 26.9955 | 26.7692 | 26.5239 | 48.965 | 48.6924 | 48.4197 | 48.1745 | 47.9471 | 47.7366 | 46.0387 | 43.7397 | 18.9513 | 23.5924 | 23.1934 | 22.6387 | 44.7166 | 44.0008 | 43.3113 | 42.6597 | 42.0366 | 41.445 | 38.6882 | 36.0818 | 33.5955 | 24.0745 | 23.8513 | 23.5966 | 45.6313 | 44.8934 | 44.1997 | 43.5482 | 42.9239 | 42.3334 | 39.5755 | 36.9692 | 34.4818
|  | SPRINGFIELD ROAD PRIMARY | EE |  |  |  |  | 27.1197 | 26.9324 | 26.7303 | 49.2134 | 48.9871 | 48.765 | 48.5513 | 48.345 | 48.1587 | 47.4345 | 46.1861 | 44.625 | 23.7429 | 23.5155 | 23.1387 | 45.3587 | 44.8387 | 44.3271 | 43.8145 | 43.3155 | 42.8461 | 40.7471 | 38.8524 | 37.0703 | 24.1976 | 24.0124 | 23.8134 | 46.3008 | 45.765 | 45.225 | 44.7071 | 44.205 | 43.7355 | 41.6345 | 39.7397 | 37.9576
|  | SPRINGFIELD ROAD PRIMARY | HT |  |  |  |  | 26.9955 | 26.7692 | 26.5239 | 48.965 | 48.6924 | 48.4197 | 48.1745 | 47.9471 | 47.7366 | 46.0387 | 43.7397 | 41.5587 | 23.5924 | 23.1934 | 22.6387 | 44.7166 | 44.0008 | 43.3113 | 42.6597 | 42.0366 | 41.445 | 38.6882 | 36.0818 | 33.5955 | 24.0745 | 23.8513 | 23.5966 | 45.6313 | 44.8934 | 44.1997 | 43.5482 | 42.9239 | 42.3334 | 39.5755 | 36.9692 | 34.4818
|  | SPRINGFIELD ROAD PRIMARY | HE |  |  |  |  | 27.2503 | 27.1145 | 26.9545 | 49.4745 | 49.2839 | 49.0987 | 48.9261 | 48.7629 | 48.6208 | 48.1082 | 47.7661 | 18.9513 | 23.885 | 23.7408 | 23.5513 | 45.9345 | 45.4945 | 45.0629 | 44.6608 | 44.2671 | 43.8934 | 42.2724 | 40.8503 | 39.5334 | 24.3387 | 24.1945 | 24.0334 | 46.5566 | 46.3692 | 46.0029 | 45.5734 | 45.1639 | 44.7861 | 43.1608 | 41.7376 | 40.4208
|  | SPRINGFIELD ROAD PRIMARY | CF |  |  |  |  | 27.3513 | 27.2724 | 27.1903 | 49.8029 | 49.7061 | 49.6061 | 49.5071 | 49.4092 | 49.3103 | 48.865 | 48.6176 | 48.4566 | 23.9913 | 23.9071 | 23.8187 | 46.4271 | 46.3018 | 46.1429 | 45.9303 | 45.7039 | 45.4703 | 44.3439 | 43.4292 | 42.6008 | 24.445 | 24.3608 | 24.2734 | 46.8808 | 46.785 | 46.6861 | 46.5892 | 46.4945 | 46.3966 | 45.2408 | 44.3176 | 43.4892
NURSLING GSP | WINCHESTER BSP | ST CROSS PRIMARY | MINIMUM HEADROOM | SU 47287 28156 | NO | YES | 0 | 28.2811 | 27.7232 | 27.1474 | 26.5663 | 25.9737 | 25.3821 | 24.7968 | 24.2137 | 23.5337 | 21.7526 | 16.7326 | -2.3126 | 28.0916 | 27.4905 | 26.8737 | 26.2495 | 25.6232 | 25 | 24.3768 | 23.7526 | 23.0095 | 19.3284 | 15.5632 | 12.2095 | 34.5789 | 34.1905 | 33.5726 | 32.9505 | 32.3189 | 31.6895 | 31.0611 | 30.4305 | 29.6811 | 27.6916 | 22.0832 | 18.6947
|  | ST CROSS PRIMARY | EE |  |  |  |  | 28.6474 | 28.1968 | 27.7295 | 27.2368 | 26.6611 | 26.2705 | 25.8084 | 25.3305 | 24.7516 | 21.7526 | 19.08 | 16.6589 | 28.4905 | 28.0074 | 27.5137 | 26.9842 | 26.3684 | 25.9705 | 25.4895 | 24.9874 | 24.3632 | 21.0937 | 18.2305 | 15.5632 | 34.7579 | 34.5 | 34.2063 | 33.6768 | 33.0568 | 32.6526 | 32.1642 | 31.6526 | 31.02 | 27.6916 | 24.7032 | 22.0011
|  | ST CROSS PRIMARY | HT |  |  |  |  | 28.2811 | 27.7232 | 27.1474 | 26.5663 | 25.9737 | 25.3821 | 24.7968 | 24.2137 | 23.5337 | 24.7263 | 16.7326 | 13.7526 | 28.0916 | 27.4905 | 26.8737 | 26.2495 | 25.6232 | 25 | 24.3768 | 23.7526 | 23.0095 | 19.3284 | 15.5632 | 12.2095 | 34.5789 | 34.1905 | 33.5726 | 32.9505 | 32.3189 | 31.6895 | 31.0611 | 30.4305 | 29.6811 | 31.2821 | 22.0832 | 18.6947
|  | ST CROSS PRIMARY | HE |  |  |  |  | 29.1305 | 28.7726 | 28.2684 | 27.7832 | 27.2905 | 26.9905 | 26.6821 | 26.3653 | 26.1547 | 24.12 | 26.4537 | -2.3126 | 29.0189 | 28.6305 | 28.0737 | 27.5421 | 27.0105 | 26.7032 | 26.3863 | 26.0547 | 25.8442 | 23.5989 | 23.3779 | 19.3989 | 34.9905 | 34.8042 | 34.5979 | 34.2421 | 33.7074 | 33.3968 | 33.0747 | 32.74 | 32.5253 | 30.2558 | 32.7926 | 26.2947
|  | ST CROSS PRIMARY | CF |  |  |  |  | 29.3968 | 29.2147 | 29.0263 | 28.8337 | 28.6284 | 28.4211 | 28.2221 | 28.0221 | 27.7558 | 26.2126 | 24.9084 | 23.7516 | 29.3021 | 29.1074 | 28.9042 | 28.6968 | 28.4789 | 28.2589 | 28.0463 | 27.8347 | 27.5432 | 25.8337 | 24.3611 | 23.0474 | 35.1526 | 35.0505 | 34.9442 | 34.8347 | 34.7158 | 34.5937 | 34.4747 | 34.3558 | 34.2337 | 32.5168 | 31.0347 | 29.7095
COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES PRIMARY | MINIMUM HEADROOM | SP 51259 05741 | NO | YES | 0 | 36.1116 | 36.0084 | 35.8989 | 35.7832 | 35.8042 | 34.8095 | 34.48 | 34.1389 | 33.9947 | 33.3958 | 32.7253 | 4.5295 | 31.1958 | 31.0011 | 30.7947 | 30.5863 | 30.32 | 28.7716 | 28.3495 | 27.9642 | 27.8084 | 27.2305 | 26.4947 | 25.7547 | 32.0021 | 31.8926 | 31.7779 | 31.6568 | 31.6611 | 30.6274 | 30.2474 | 29.8621 | 29.7063 | 29.0853 | 28.3505 | 27.6095
|  | ST EBBES PRIMARY | EE |  |  |  |  | 36.1747 | 36.0895 | 36 | 35.9032 | 35.8042 | 35.0505 | 34.48 | 34.1389 | 33.9947 | 33.7147 | 33.2126 | 32.7505 | 31.3516 | 31.2347 | 30.9316 | 30.5863 | 30.32 | 29.0053 | 28.3495 | 27.9642 | 27.8084 | 27.5558 | 27.0063 | 26.4926 | 32.1074 | 31.9905 | 31.8811 | 31.7695 | 31.6611 | 30.9032 | 30.2474 | 29.8621 | 29.7063 | 29.4116 | 28.8611 | 28.3474
|  | ST EBBES PRIMARY | HT |  |  |  |  | 36.1116 | 36.0084 | 35.8989 | 35.7832 | 35.9368 | 34.8095 | 34.5747 | 34.3747 | 34.2 | 33.3958 | 32.7253 | 32.0579 | 31.1958 | 31.0011 | 30.7947 | 30.5884 | 30.8137 | 28.7716 | 28.5147 | 28.2968 | 28.1074 | 27.2305 | 26.4947 | 25.7547 | 32.0021 | 31.8926 | 31.7779 | 31.6568 | 31.9032 | 30.6274 | 30.3705 | 30.1526 | 29.9632 | 29.0853 | 28.3505 | 27.6095
|  | ST EBBES PRIMARY | HE |  |  |  |  | 36.2316 | 36.1621 | 36.0863 | 36.0042 | 35.9158 | 35.3726 | 34.8274 | 34.5758 | 34.4726 | 34.4147 | 34.1358 | 4.5295 | 31.4126 | 31.3137 | 31.1579 | 30.8747 | 30.6747 | 29.3632 | 28.7337 | 28.4505 | 28.34 | 28.3326 | 28.0274 | 27.7611 | 32.1695 | 32.0684 | 31.9758 | 31.8821 | 31.7874 | 31.2611 | 30.6316 | 30.3484 | 30.2379 | 30.1874 | 29.8832 | 29.6158
|  | ST EBBES PRIMARY | CF |  |  |  |  | 36.2737 | 36.2305 | 36.1853 | 36.1379 | 36.0895 | 36.04 | 35.9905 | 35.9432 | 35.8947 | 35.1011 | 35.1811 | 34.9821 | 31.4737 | 31.4295 | 31.3821 | 31.3326 | 31.2821 | 31.2305 | 31.1726 | 31.1042 | 31.0211 | 29.0705 | 29.2053 | 28.9811 | 32.2305 | 32.1853 | 32.1389 | 32.0895 | 32.0389 | 31.9874 | 31.9284 | 31.8589 | 31.7874 | 30.9684 | 31.0611 | 30.8368
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | ST JOHNS PRIMARY | MINIMUM HEADROOM | SU 47113 66363 | NO | YES | 1.0516 | 16.8627 | 16.4122 | 15.2553 | 13.6785 | 11.9269 | 10.1669 | 8.4638 | 6.9553 | 5.7048 | 3.1606 | 0.75008 | -26.4889 | 10.709 | 9.1164 | 7.3701 | 5.528 | 3.5627 | 1.5701 | -0.36466 | -2.0762 | -3.4899 | -6.2552 | -8.9194 | -11.512 | 12.0543 | 10.5153 | 8.7932 | 6.9048 | 4.9164 | 2.9227 | 0.98797 | -0.72466 | -2.1383 | -4.9036 | -7.5689 | -10.1615
|  | ST JOHNS PRIMARY | EE |  |  |  |  | 17.0869 | 16.728 | 15.9406 | 14.5017 | 12.8922 | 11.2774 | 9.6732 | 8.2448 | 7.0774 | 5.068 | 3.2627 | 1.5206 | 11.1848 | 9.7343 | 8.1332 | 6.4259 | 4.6069 | 2.7701 | 0.94376 | -0.6794 | -2.0015 | -4.1857 | -6.1857 | -8.1436 | 12.4301 | 11.1195 | 9.569 | 7.8185 | 5.9606 | 4.1238 | 2.2964 | 0.67218 | -0.64992 | -2.8341 | -4.8352 | -6.7931
|  | ST JOHNS PRIMARY | HT |  |  |  |  | 16.8627 | 16.4122 | 15.2553 | 13.6785 | 11.9269 | 10.1669 | 8.4638 | 6.9553 | 5.7048 | 3.1606 | 0.75008 | -1.5699 | 10.709 | 9.1164 | 7.3701 | 5.528 | 3.5627 | 1.5701 | -0.36466 | -2.0762 | -3.4899 | -6.2552 | -8.9194 | -11.512 | 12.0543 | 10.5153 | 8.7932 | 6.9048 | 4.9164 | 2.9227 | 0.98797 | -0.72466 | -2.1383 | -4.9036 | -7.5689 | -10.1615
|  | ST JOHNS PRIMARY | HE |  |  |  |  | 17.3648 | 17.1238 | 16.7964 | 15.5385 | 14.1269 | 12.6595 | 11.209 | 9.928 | 8.9111 | 7.6153 | 6.4817 | -26.4889 | 11.8027 | 10.5427 | 9.1238 | 7.589 | 5.9385 | 4.2774 | 2.6174 | 1.1543 | -0.0036084 | -1.4068 | -2.6678 | -3.9015 | 12.729 | 11.908 | 10.5406 | 9.0006 | 7.3069 | 5.6311 | 3.9701 | 2.5069 | 1.348 | -0.055187 | -1.3152 | -2.5499
|  | ST JOHNS PRIMARY | CF |  |  |  |  | 17.5574 | 17.4385 | 17.3101 | 17.1395 | 16.9638 | 16.5122 | 15.808 | 15.1343 | 14.5259 | 13.389 | 12.5711 | 11.8017 | 12.1711 | 11.6353 | 10.9574 | 10.2543 | 9.5227 | 8.7332 | 7.889 | 7.0827 | 6.3764 | 5.1585 | 4.2532 | 3.3785 | 12.9385 | 12.788 | 12.3122 | 11.6343 | 10.929 | 10.1669 | 9.3059 | 8.4795 | 7.7543 | 6.5164 | 5.6069 | 4.7322
COWLEY GSP | WITNEY BSP | STANDLAKE PRIMARY | MINIMUM HEADROOM | SP 38923 02349 | NO | YES | 0 | 6.1884 | 6.1063 | 6.0189 | 5.9295 | 5.8379 | 5.6505 | 5.2958 | 5.2232 | 5.1558 | 4.4895 | 3.6621 | -4.1442 | 5.0537 | 4.9063 | 4.7516 | 4.6 | 4.4516 | 4.1432 | 3.7442 | 3.6716 | 3.6042 | 2.8632 | 1.8558 | 1.5621 | 5.3811 | 5.2263 | 5.0642 | 4.9063 | 4.7516 | 4.42 | 3.9874 | 3.9147 | 3.8474 | 3.0684 | 2.0621 | 1.7695
|  | STANDLAKE PRIMARY | EE |  |  |  |  | 6.24 | 6.1737 | 6.1032 | 6.0295 | 5.9537 | 5.8811 | 5.8126 | 5.7474 | 5.6895 | 5.3316 | 4.7789 | 4.2747 | 5.1579 | 5.0389 | 4.9158 | 4.7937 | 4.6726 | 4.5547 | 4.4442 | 4.3316 | 4.2284 | 3.8147 | 3.1968 | 2.5916 | 5.4905 | 5.3663 | 5.2368 | 5.1105 | 4.9832 | 4.8621 | 4.7463 | 4.6284 | 4.5211 | 4.0853 | 3.4158 | 2.7968
|  | STANDLAKE PRIMARY | HT |  |  |  |  | 6.1884 | 6.1063 | 6.0189 | 5.9295 | 5.8379 | 5.6505 | 5.2958 | 5.2232 | 5.1558 | 4.4895 | 3.6621 | 3.3989 | 5.0537 | 4.9063 | 4.7516 | 4.6 | 4.4516 | 4.1432 | 3.7442 | 3.6716 | 3.6042 | 2.8632 | 1.8558 | 1.5621 | 5.3811 | 5.2263 | 5.0642 | 4.9063 | 4.7516 | 4.42 | 3.9874 | 3.9147 | 3.8474 | 3.0684 | 2.0621 | 1.7695
|  | STANDLAKE PRIMARY | HE |  |  |  |  | 6.3063 | 6.2611 | 6.2105 | 6.1558 | 6.0979 | 6.0432 | 5.9905 | 5.9421 | 5.9 | 5.76 | 5.4463 | -4.1442 | 5.2926 | 5.2168 | 5.1326 | 5.0484 | 4.9632 | 4.88 | 4.8011 | 4.7221 | 4.6516 | 4.3895 | 3.9168 | 3.4642 | 5.6116 | 5.5537 | 5.4663 | 5.3789 | 5.2895 | 5.2042 | 5.1221 | 5.04 | 4.9663 | 4.6916 | 4.1758 | 3.68
|  | STANDLAKE PRIMARY | CF |  |  |  |  | 6.3516 | 6.3284 | 6.3053 | 6.2811 | 6.2547 | 6.2295 | 6.2042 | 6.1789 | 6.1537 | 6.0411 | 5.9853 | 5.8411 | 5.3968 | 5.3526 | 5.3074 | 5.2589 | 5.2095 | 5.1589 | 5.1126 | 5.0695 | 5.0232 | 4.8 | 4.5989 | 4.3305 | 5.6611 | 5.6368 | 5.6116 | 5.5863 | 5.5463 | 5.4926 | 5.4442 | 5.3989 | 5.3505 | 5.1158 | 4.8989 | 4.6042
MINETY GSP | STRATTON (RESERVE) BSP | STANTON FITZWARREN PRIMARY | MINIMUM HEADROOM | SU 17585 90987 | NO | YES | 0.21053 | 22.3382 | 21.9403 | 21.5487 | 20.8876 | 20.0076 | 19.3129 | 18.4466 | 17.5434 | 16.6676 | 12.7634 | 10.4045 | -4.0955 | 21.2761 | 20.8529 | 20.4382 | 19.7087 | 18.7266 | 17.9645 | 16.995 | 15.9782 | 14.9918 | 10.595 | 7.9887 | 5.5055 | 21.4055 | 20.9824 | 20.5687 | 19.8392 | 18.8561 | 18.0918 | 17.1203 | 16.1013 | 15.1118 | 10.6918 | 8.0529 | 5.5603
|  | STANTON FITZWARREN PRIMARY | EE |  |  |  |  | 22.5382 | 22.2013 | 21.8729 | 21.4592 | 20.6708 | 20.1361 | 19.2624 | 18.4013 | 17.5687 | 14.1066 | 12.1466 | 10.4318 | 21.3129 | 21.1255 | 20.7761 | 20.3308 | 19.4487 | 18.8676 | 17.8855 | 16.9171 | 15.9813 | 12.095 | 9.955 | 8.0182 | 21.615 | 21.255 | 20.9066 | 20.4603 | 19.5771 | 18.9908 | 18.0066 | 17.0339 | 16.0918 | 12.1687 | 9.9803 | 8.0308
|  | STANTON FITZWARREN PRIMARY | HT |  |  |  |  | 22.3382 | 21.9403 | 21.5487 | 20.8876 | 20.0076 | 19.3129 | 18.4466 | 17.5434 | 16.6676 | 12.7634 | 10.4045 | 8.2013 | 21.2761 | 20.8529 | 20.4382 | 19.7087 | 18.7266 | 17.9645 | 16.995 | 15.9782 | 14.9918 | 10.595 | 7.9887 | 5.5055 | 21.4055 | 20.9824 | 20.5687 | 19.8392 | 18.8561 | 18.0918 | 17.1203 | 16.1013 | 15.1118 | 10.6918 | 8.0529 | 5.5603
|  | STANTON FITZWARREN PRIMARY | HE |  |  |  |  | 22.7782 | 22.5476 | 22.2982 | 22.0266 | 21.5192 | 21.0929 | 20.3297 | 19.5792 | 18.8624 | 15.9592 | 14.5729 | -4.0955 | 21.5603 | 21.4866 | 21.2213 | 20.9318 | 20.3708 | 19.9034 | 19.0371 | 18.1855 | 17.3676 | 14.0592 | 12.4939 | 11.0034 | 21.8634 | 21.6161 | 21.3508 | 21.0613 | 20.4992 | 20.0297 | 19.1634 | 18.3108 | 17.4929 | 14.1718 | 12.5971 | 11.095
|  | STANTON FITZWARREN PRIMARY | CF |  |  |  |  | 22.8782 | 22.7824 | 22.6887 | 22.5782 | 22.4445 | 22.3603 | 22.1939 | 21.9066 | 21.4697 | 19.5624 | 18.7434 | 17.9087 | 21.6518 | 21.5518 | 21.6266 | 21.5108 | 21.3697 | 21.2918 | 21.1129 | 20.7918 | 20.2929 | 18.1213 | 17.2024 | 16.2518 | 21.9613 | 21.8613 | 21.7645 | 21.6487 | 21.5066 | 21.4192 | 21.2403 | 20.9171 | 20.4192 | 18.2466 | 17.3203 | 16.3634
LALEHAM GSP | STAINES BSP | STANWELL PRIMARY | MINIMUM HEADROOM | TQ 06003 72766 | NO | YES | 0 | 33.8579 | 33.7305 | 33.5958 | 33.4558 | 33.3095 | 33.1632 | 33.0347 | 33.1158 | 33.0158 | 32.3905 | 31.3958 | 9.5232 | 30.5642 | 30.32 | 30.0705 | 29.8211 | 29.5695 | 29.3232 | 29.0979 | 28.9505 | 28.7432 | 27.5189 | 26.4105 | 25.3779 | 31.1221 | 30.9884 | 30.7632 | 30.5221 | 30.2779 | 30.0389 | 29.8179 | 29.6021 | 29.3947 | 28.1726 | 27.0653 | 26.0337
|  | STANWELL PRIMARY | EE |  |  |  |  | 33.9274 | 33.82 | 33.7063 | 33.5863 | 33.4621 | 33.3411 | 33.2263 | 33.1158 | 33.0158 | 32.6484 | 32.2737 | 31.5632 | 30.7211 | 30.5274 | 30.3274 | 30.1211 | 29.9168 | 29.7168 | 29.5253 | 29.34 | 29.1621 | 28.1705 | 27.3095 | 26.5084 | 31.1968 | 31.0842 | 30.9663 | 30.8095 | 30.6105 | 30.4158 | 30.2305 | 30.0505 | 29.8779 | 28.8905 | 28.0284 | 27.2274
|  | STANWELL PRIMARY | HT |  |  |  |  | 33.8579 | 33.7305 | 33.5958 | 33.4558 | 33.3095 | 33.1632 | 33.0347 | 33.6905 | 33.4979 | 32.3905 | 31.3958 | 30.4768 | 30.5642 | 30.32 | 30.0705 | 29.8211 | 29.5695 | 29.3232 | 29.0979 | 28.9505 | 28.7432 | 27.5189 | 26.4105 | 25.3779 | 31.1221 | 30.9884 | 30.7632 | 30.5221 | 30.2779 | 30.0389 | 29.8179 | 29.6021 | 29.3947 | 28.1726 | 27.0653 | 26.0337
|  | STANWELL PRIMARY | HE |  |  |  |  | 34.0179 | 33.9379 | 33.8495 | 33.7537 | 33.6537 | 33.5568 | 33.4653 | 34.6789 | 34.5663 | 33.9242 | 33.4 | 9.5232 | 30.84 | 30.7537 | 30.6589 | 30.5179 | 30.3705 | 30.2284 | 30.0916 | 30.0316 | 29.9126 | 29.2011 | 28.6095 | 28.0716 | 31.2947 | 31.2116 | 31.12 | 31.0221 | 30.9189 | 30.8189 | 30.7253 | 30.6821 | 30.5632 | 29.8526 | 29.2621 | 28.7242
|  | STANWELL PRIMARY | CF |  |  |  |  | 34.0832 | 34.0389 | 33.9916 | 33.9432 | 33.8947 | 33.8432 | 33.7926 | 33.7432 | 33.6937 | 33.4737 | 33.3621 | 33.3 | 30.9126 | 30.8632 | 30.8105 | 30.7579 | 30.7042 | 30.6211 | 30.5326 | 30.4453 | 30.3547 | 29.8011 | 29.3737 | 29 | 31.3632 | 31.3168 | 31.2674 | 31.2168 | 31.1663 | 31.1116 | 31.0589 | 31.0074 | 30.9558 | 30.5042 | 30.0937 | 29.7189
MANNINGTON GSP | SALISBURY BSP | STAPLEFORD PRIMARY | MINIMUM HEADROOM | SU 06871 37078 | NO | YES | 0.10526 | 16.2811 | 16.1558 | 16.0063 | 15.8295 | 15.4168 | 14.9284 | 14.34 | 14.2242 | 14.1126 | 12.9158 | 11.3737 | 6.2484 | 14.8084 | 14.68 | 14.5242 | 14.3368 | 13.8874 | 13.3421 | 12.6789 | 12.5695 | 12.4653 | 11.1989 | 9.5253 | 9.0537 | 14.9663 | 14.8379 | 14.6853 | 14.5021 | 14.0653 | 13.5442 | 12.8863 | 12.7695 | 12.6579 | 11.3432 | 9.6126 | 9.1189
|  | STAPLEFORD PRIMARY | EE |  |  |  |  | 16.3579 | 16.2547 | 16.1484 | 16.0379 | 15.8832 | 15.7147 | 15.5495 | 15.3821 | 15.2253 | 14.3211 | 12.8958 | 11.9863 | 14.8884 | 14.7832 | 14.6737 | 14.5621 | 14.4063 | 14.2389 | 14.0779 | 13.9095 | 13.7547 | 12.8547 | 11.3442 | 10.3389 | 15.0442 | 14.9389 | 14.8316 | 14.7189 | 14.5589 | 14.3863 | 14.2168 | 14.0432 | 13.8811 | 12.94 | 11.3821 | 10.3516
|  | STAPLEFORD PRIMARY | HT |  |  |  |  | 16.2811 | 16.1558 | 16.0063 | 15.8295 | 15.4168 | 14.9284 | 14.34 | 14.2242 | 14.1126 | 12.9158 | 11.3737 | 10.9126 | 14.8084 | 14.68 | 14.5242 | 14.3368 | 13.8874 | 13.3421 | 12.6789 | 12.5695 | 12.4653 | 11.1989 | 9.5253 | 9.0537 | 14.9663 | 14.8379 | 14.6853 | 14.5021 | 14.0653 | 13.5442 | 12.8863 | 12.7695 | 12.6579 | 11.3432 | 9.6126 | 9.1189
|  | STAPLEFORD PRIMARY | HE |  |  |  |  | 16.4516 | 16.3916 | 16.3189 | 16.2411 | 16.1421 | 16.0484 | 15.96 | 15.8747 | 15.7968 | 15.2589 | 14.3526 | 6.2484 | 14.9853 | 14.9242 | 14.8484 | 14.7695 | 14.6737 | 14.5842 | 14.5 | 14.4168 | 14.3421 | 13.7916 | 12.7832 | 11.9663 | 15.14 | 15.0789 | 15.0053 | 14.9274 | 14.8263 | 14.7316 | 14.6421 | 14.5558 | 14.4747 | 13.9137 | 12.9368 | 12.1011
|  | STAPLEFORD PRIMARY | CF |  |  |  |  | 16.5095 | 16.4821 | 16.4526 | 16.4179 | 16.3695 | 16.3221 | 16.2758 | 16.2295 | 16.1853 | 15.9453 | 15.5358 | 15 | 15.0432 | 15.0158 | 14.9853 | 14.9495 | 14.9042 | 14.8568 | 14.8116 | 14.7663 | 14.7232 | 14.4842 | 14.0411 | 13.4389 | 15.1979 | 15.1705 | 15.14 | 15.1053 | 15.0568 | 15.0074 | 14.9611 | 14.9147 | 14.8684 | 14.6221 | 14.1874 | 13.6095
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH PRIMARY | MINIMUM HEADROOM | SU 77124 94355 | NO | YES | 0 | 9.4958 | 9.3305 | 9.1432 | 8.8516 | 8.5621 | 8.2716 | 7.9958 | 7.7242 | 7.4684 | 6.2926 | 5.2568 | -6.9021 | 7.44 | 7.1316 | 6.8189 | 6.5126 | 6.2084 | 5.9042 | 5.6137 | 5.3253 | 5.0537 | 3.7916 | 2.6716 | 1.6368 | 7.9063 | 7.5937 | 7.2768 | 6.9663 | 6.6589 | 6.3505 | 6.0547 | 5.7621 | 5.4863 | 4.2021 | 3.0589 | 2.0189
|  | STOKENCHURCH PRIMARY | EE |  |  |  |  | 9.5926 | 9.4579 | 9.3126 | 9.1621 | 8.9842 | 8.7516 | 8.5263 | 8.2916 | 8.0737 | 7.1442 | 6.3568 | 5.6653 | 7.6484 | 7.4053 | 7.1547 | 6.9063 | 6.6589 | 6.4158 | 6.1789 | 5.9316 | 5.6989 | 4.7053 | 3.8505 | 3.0937 | 8.1189 | 7.8726 | 7.6179 | 7.3674 | 7.1158 | 6.8705 | 6.6295 | 6.3789 | 6.1432 | 5.1305 | 4.2568 | 3.4832
|  | STOKENCHURCH PRIMARY | HT |  |  |  |  | 9.4958 | 9.3305 | 9.1432 | 8.8516 | 8.5621 | 8.2716 | 7.9958 | 7.7242 | 7.4684 | 6.2926 | 5.2568 | 4.3232 | 7.44 | 7.1316 | 6.8189 | 6.5126 | 6.2084 | 5.9042 | 5.6137 | 5.3253 | 5.0537 | 3.7916 | 2.6716 | 1.6368 | 7.9063 | 7.5937 | 7.2768 | 6.9663 | 6.6589 | 6.3505 | 6.0547 | 5.7621 | 5.4863 | 4.2021 | 3.0589 | 2.0189
|  | STOKENCHURCH PRIMARY | HE |  |  |  |  | 9.7232 | 9.6274 | 9.5211 | 9.4074 | 9.2863 | 9.1684 | 9.06 | 8.9568 | 8.8695 | 8.2874 | 7.7884 | -6.9021 | 7.9305 | 7.7716 | 7.6042 | 7.4358 | 7.2632 | 7.0905 | 6.9232 | 6.7474 | 6.5853 | 5.9263 | 5.3832 | 4.9168 | 8.3105 | 8.2105 | 8.0758 | 7.9042 | 7.7305 | 7.5568 | 7.3874 | 7.2095 | 7.0432 | 6.3737 | 5.8189 | 5.34
|  | STOKENCHURCH PRIMARY | CF |  |  |  |  | 9.8126 | 9.7621 | 9.7105 | 9.6568 | 9.6011 | 9.5432 | 9.4874 | 9.4316 | 9.3758 | 9.0758 | 8.7084 | 8.4084 | 8.08 | 7.9905 | 7.8937 | 7.7979 | 7.6989 | 7.5989 | 7.4979 | 7.3895 | 7.2758 | 6.7474 | 6.3463 | 6.0137 | 8.4042 | 8.3505 | 8.2958 | 8.2389 | 8.1705 | 8.0695 | 7.9663 | 7.8558 | 7.7411 | 7.2032 | 6.7926 | 6.4526
MINETY GSP | STRATTON (RESERVE) BSP | STRATTON PRIMARY | MINIMUM HEADROOM | SU 16998 88837 | NO | YES | 0 | 35.28 | 34.9832 | 34.66 | 34.3211 | 34.0263 | 32.9137 | 31.6463 | 30.4989 | 29.3768 | 26.6568 | 23.9979 | -5.3832 | 28.5295 | 27.5684 | 26.4705 | 25.2421 | 23.7084 | 22.0558 | 20.5853 | 19.2863 | 18.0158 | 15.0053 | 12.0326 | 9.1916 | 28.1832 | 27.2137 | 26.1063 | 24.8663 | 23.3011 | 21.6305 | 20.1432 | 18.8316 | 17.5463 | 14.4958 | 11.4821 | 8.6084
|  | STRATTON PRIMARY | EE |  |  |  |  | 35.4326 | 35.1811 | 34.9063 | 34.6147 | 34.2789 | 33.5137 | 32.3326 | 31.2263 | 30.1505 | 27.9642 | 25.8316 | 23.8421 | 28.8474 | 27.9789 | 26.9747 | 25.84 | 24.2705 | 22.7147 | 21.3116 | 20.06 | 18.8411 | 16.4411 | 14.0632 | 11.8084 | 28.5032 | 27.6263 | 26.6126 | 25.4663 | 23.8811 | 22.3074 | 20.8884 | 19.6221 | 18.3874 | 15.9347 | 13.5137 | 11.2295
|  | STRATTON PRIMARY | HT |  |  |  |  | 35.28 | 34.9832 | 34.66 | 34.3211 | 34.0263 | 32.9137 | 31.6463 | 30.4989 | 29.3768 | 26.6568 | 23.9979 | 21.4842 | 28.5295 | 27.5684 | 26.4705 | 25.2421 | 23.7084 | 22.0558 | 20.5853 | 19.2863 | 18.0158 | 15.0053 | 12.0326 | 9.1916 | 28.1832 | 27.2137 | 26.1063 | 24.8663 | 23.3011 | 21.6305 | 20.1432 | 18.8316 | 17.5463 | 14.4958 | 11.4821 | 8.6084
|  | STRATTON PRIMARY | HE |  |  |  |  | 35.6411 | 35.4526 | 35.24 | 35.0074 | 34.7274 | 34.4274 | 33.3568 | 32.3811 | 31.4084 | 29.7411 | 28.1042 | -5.3832 | 29.2716 | 28.5347 | 27.6547 | 26.6379 | 25.1811 | 23.7368 | 22.4453 | 21.3053 | 20.1968 | 18.3484 | 16.4937 | 14.6989 | 28.9295 | 28.1863 | 27.2979 | 26.2716 | 24.7979 | 23.3379 | 22.0316 | 20.88 | 19.7589 | 17.8716 | 15.9916 | 14.1726
|  | STRATTON PRIMARY | CF |  |  |  |  | 35.7821 | 35.6947 | 35.5905 | 35.4789 | 35.3516 | 35.22 | 35.0895 | 34.9642 | 34.8347 | 34.3737 | 33.7221 | 32.7863 | 29.5168 | 29.3295 | 28.9084 | 28.4453 | 27.8211 | 27.1432 | 26.4811 | 25.8505 | 25.1821 | 23.8474 | 22.9389 | 21.8105 | 29.1768 | 28.9884 | 28.5632 | 28.0947 | 27.4632 | 26.7789 | 26.1095 | 25.4726 | 24.7968 | 23.4474 | 22.5126 | 21.3695
LALEHAM GSP | STAINES BSP | SUNBURY CROSS PRIMARY | MINIMUM HEADROOM | TQ 10053 69996 | NO | YES | 0.052632 | 67.1342 | 66.5279 | 65.8847 | 65.2174 | 64.5289 | 63.8363 | 63.2258 | 62.67 | 62.1553 | 58.1163 | 53.4047 | -10.0763 | 59.8721 | 58.4658 | 56.9595 | 55.3679 | 53.6995 | 52.0858 | 51.0132 | 50.0184 | 49.0637 | 43.5774 | 38.3195 | 33.3868 | 61.3626 | 60.7037 | 59.2163 | 57.6311 | 55.9689 | 54.3605 | 53.2911 | 52.2984 | 51.3468 | 45.9637 | 40.8395 | 35.91
|  | SUNBURY CROSS PRIMARY | EE |  |  |  |  | 67.4879 | 66.9879 | 71.9426 | 70.8153 | 69.5911 | 68.3953 | 67.1995 | 66.2247 | 65.4574 | 61.59 | 58.0321 | 54.7458 | 60.6732 | 59.6247 | 58.6963 | 57.47 | 56.1342 | 54.8268 | 53.5153 | 52.4605 | 51.6374 | 47.3889 | 43.41 | 39.6974 | 61.7426 | 61.21 | 60.7679 | 59.5647 | 58.2563 | 56.9763 | 55.6932 | 54.6584 | 53.8489 | 49.9153 | 45.9353 | 42.2226
|  | SUNBURY CROSS PRIMARY | HT |  |  |  |  | 67.1342 | 66.5279 | 65.8847 | 65.2174 | 64.5289 | 63.8363 | 63.2258 | 62.67 | 62.1553 | 58.1163 | 53.4047 | 49.0174 | 59.8721 | 58.4658 | 56.9595 | 55.3679 | 53.6995 | 52.0858 | 51.0132 | 50.0184 | 49.0637 | 43.5774 | 38.3195 | 33.3868 | 61.3626 | 60.7037 | 59.2163 | 57.6311 | 55.9689 | 54.3605 | 53.2911 | 52.2984 | 51.3468 | 45.9637 | 40.8395 | 35.91
|  | SUNBURY CROSS PRIMARY | HE |  |  |  |  | 67.9374 | 67.5732 | 67.1711 | 66.7374 | 66.2763 | 65.8353 | 65.4184 | 65.0311 | 64.6953 | 63.5626 | 62.8932 | -10.0763 | 61.2111 | 60.83 | 60.11 | 59.1837 | 58.1279 | 57.0995 | 56.0395 | 55.3037 | 54.7595 | 51.8574 | 49.1542 | 46.6132 | 62.2163 | 61.8384 | 61.4111 | 60.9479 | 60.3689 | 59.3563 | 58.3005 | 57.5658 | 57.0226 | 54.1321 | 51.4416 | 48.9784
|  | SUNBURY CROSS PRIMARY | CF |  |  |  |  | 68.2479 | 68.0479 | 67.8395 | 67.6237 | 67.4026 | 67.1742 | 66.9511 | 66.7289 | 66.5089 | 65.5237 | 65.0321 | 64.7595 | 61.5332 | 61.3247 | 61.1068 | 60.8816 | 60.5753 | 60.1205 | 59.6584 | 59.0763 | 58.4605 | 55.2721 | 53.3763 | 51.6889 | 62.5268 | 62.3268 | 62.1184 | 61.8911 | 61.6574 | 61.4153 | 61.1774 | 60.9342 | 60.69 | 57.5384 | 55.65 | 53.9721
FLEET-BRAMLEY GSP | BRACKNELL BSP | SUNNINGHILL PRIMARY | MINIMUM HEADROOM | SU 93757 67606 | NO | YES | 0 | 27.6768 | 27.5063 | 27.3232 | 27.1347 | 26.9411 | 26.7453 | 26.5737 | 26.4168 | 26.2726 | 24.9758 | 23.7874 | 7.9832 | 24.3989 | 24.0747 | 23.7368 | 23.4 | 23.0695 | 22.7484 | 22.4558 | 22.0937 | 21.7495 | 20.1842 | 18.7874 | 17.5084 | 24.9989 | 24.8 | 24.4747 | 24.1484 | 23.8295 | 23.5063 | 23.2147 | 22.8537 | 22.5074 | 20.9432 | 19.5442 | 18.2642
|  | SUNNINGHILL PRIMARY | EE |  |  |  |  | 27.7821 | 27.6432 | 27.4947 | 27.3389 | 27.1768 | 27.0232 | 26.8737 | 26.7326 | 26.6042 | 25.8695 | 24.9547 | 24.1411 | 24.6253 | 24.3674 | 24.0979 | 23.8242 | 23.5558 | 23.2958 | 23.0516 | 22.7432 | 22.4579 | 21.2063 | 20.1274 | 19.1495 | 25.1116 | 24.9663 | 24.8105 | 24.5568 | 24.2958 | 24.0432 | 23.8063 | 23.5 | 23.2147 | 21.9621 | 20.8789 | 19.9011
|  | SUNNINGHILL PRIMARY | HT |  |  |  |  | 27.6768 | 27.5063 | 27.3232 | 27.1347 | 26.9411 | 26.7453 | 26.5737 | 26.4168 | 26.2726 | 24.9758 | 23.7874 | 22.66 | 24.3989 | 24.0747 | 23.7368 | 23.4 | 23.0695 | 22.7484 | 22.4558 | 22.0937 | 21.7495 | 20.1842 | 18.7874 | 17.5084 | 24.9989 | 24.8 | 24.4747 | 24.1484 | 23.8295 | 23.5063 | 23.2147 | 22.8537 | 22.5074 | 20.9432 | 19.5442 | 18.2642
|  | SUNNINGHILL PRIMARY | HE |  |  |  |  | 27.9137 | 27.8158 | 27.7063 | 27.5884 | 27.4621 | 27.3411 | 27.2284 | 27.1221 | 27.0295 | 26.72 | 26.4137 | 7.9832 | 24.8126 | 24.7084 | 24.5368 | 24.3453 | 24.1516 | 23.9674 | 23.7916 | 23.5874 | 23.3989 | 22.5389 | 21.7916 | 21.1232 | 25.2558 | 25.1484 | 25.0347 | 24.9126 | 24.7832 | 24.6589 | 24.5168 | 24.3211 | 24.1389 | 23.2968 | 22.5484 | 21.88
|  | SUNNINGHILL PRIMARY | CF |  |  |  |  | 28.0021 | 27.9484 | 27.8926 | 27.8358 | 27.7768 | 27.7147 | 27.6558 | 27.5947 | 27.5358 | 27.2726 | 27.14 | 27.0642 | 24.9053 | 24.8484 | 24.7905 | 24.7305 | 24.6695 | 24.5758 | 24.4621 | 24.3495 | 24.2179 | 23.5705 | 23.0389 | 22.5895 | 25.3505 | 25.2916 | 25.2326 | 25.1726 | 25.1105 | 25.0453 | 24.9832 | 24.92 | 24.8568 | 24.3168 | 23.7968 | 23.3463
MELKSHAM GSP | CHIPPENHAM BSP | SUTTON BENGER PRIMARY | MINIMUM HEADROOM | ST 93394 80051 | NO | YES | 0 | 16.3116 | 16.2421 | 15.8347 | 15.7789 | 15.7189 | 14.0442 | 13.6779 | 13.6168 | 10.7053 | 9.9884 | 9.0421 | 7.6863 | 14.9832 | 14.8042 | 14.1832 | 14.1284 | 14.0695 | 12 | 11.5579 | 11.4979 | 8.1095 | 7.3211 | 6.2568 | 5.9768 | 15.4695 | 15.3168 | 14.7726 | 14.7168 | 14.6568 | 12.5537 | 12.1032 | 12.0421 | 8.6305 | 7.8316 | 6.7537 | 6.4695
|  | SUTTON BENGER PRIMARY | EE |  |  |  |  | 16.3526 | 16.2989 | 15.8347 | 15.7789 | 15.7189 | 15.6568 | 15.5979 | 15.5411 | 15.4884 | 12.5863 | 11.6495 | 11.0726 | 15.0389 | 14.9537 | 14.1832 | 14.1284 | 14.0695 | 14.0095 | 13.9537 | 13.8989 | 13.8484 | 10.3537 | 9.3 | 8.6442 | 15.5211 | 15.4432 | 14.7726 | 14.7168 | 14.6568 | 14.5947 | 14.5358 | 14.48 | 14.4263 | 10.8579 | 9.7863 | 9.1253
|  | SUTTON BENGER PRIMARY | HT |  |  |  |  | 16.3116 | 16.2421 | 16.1232 | 15.9737 | 15.8611 | 14.0442 | 13.6779 | 13.6168 | 10.7053 | 9.9884 | 9.0421 | 8.7789 | 14.9832 | 14.8042 | 14.5621 | 14.3916 | 14.2705 | 12 | 11.5579 | 11.4979 | 8.1095 | 7.3211 | 6.2568 | 5.9768 | 15.4695 | 15.3168 | 15.1126 | 14.9558 | 14.84 | 12.5537 | 12.1032 | 12.0421 | 8.6305 | 7.8316 | 6.7537 | 6.4695
|  | SUTTON BENGER PRIMARY | HE |  |  |  |  | 16.4032 | 16.3695 | 16.3274 | 16.2779 | 16.2074 | 16.1305 | 16.0663 | 16.0084 | 15.9579 | 13.9284 | 13.2537 | 7.6863 | 15.1011 | 15.0621 | 14.9547 | 14.7821 | 14.6537 | 14.5705 | 14.5011 | 14.44 | 14.3863 | 11.8684 | 11.0863 | 10.5611 | 15.5811 | 15.5432 | 15.4516 | 15.3084 | 15.1968 | 15.1211 | 15.0526 | 14.9947 | 14.9432 | 12.4095 | 11.6084 | 11.0695
|  | SUTTON BENGER PRIMARY | CF |  |  |  |  | 16.4379 | 16.4211 | 16.4032 | 16.3853 | 16.3653 | 16.3432 | 16.3232 | 16.3011 | 16.2779 | 16.1211 | 15.9326 | 15.7137 | 15.1411 | 15.1232 | 15.1042 | 15.0821 | 15.0547 | 15.0263 | 15 | 14.9684 | 14.8968 | 14.5642 | 14.3432 | 14.08 | 15.6189 | 15.6021 | 15.5832 | 15.5621 | 15.5347 | 15.5084 | 15.4832 | 15.4547 | 15.3926 | 15.1105 | 14.9116 | 14.6579
IVER 132KV GSP | UPTON BSP | SUTTON LANE PRIMARY | MINIMUM HEADROOM | TQ 02185 78595 | NO | NO | 0 | 24.455 | 24.3076 | 24.1497 | 23.9508 | 23.7476 | 23.5434 | 23.3476 | 23.2097 | 23.0834 | 22.2666 | 21.0203 | 7.4213 | 21.6876 | 21.5403 | 21.3824 | 21.1771 | 20.9676 | 20.7571 | 20.5539 | 20.4161 | 20.2897 | 19.4213 | 18.0276 | 16.7529 | 22.3361 | 22.1887 | 22.0308 | 21.8255 | 21.6161 | 21.4055 | 21.2024 | 21.0645 | 20.9382 | 20.0697 | 18.6761 | 17.4003
|  | SUTTON LANE PRIMARY | EE |  |  |  |  | 24.5434 | 24.4224 | 24.2929 | 24.1571 | 24.0171 | 23.8803 | 23.7487 | 23.6234 | 23.5108 | 23.0182 | 22.1792 | 21.3097 | 21.7761 | 21.655 | 21.5255 | 21.3897 | 21.2497 | 21.1129 | 20.9813 | 20.8561 | 20.7434 | 20.2371 | 19.3013 | 18.3192 | 22.4245 | 22.3034 | 22.1739 | 22.0382 | 21.8982 | 21.7613 | 21.6297 | 21.5045 | 21.3918 | 20.8855 | 19.9497 | 18.9666
|  | SUTTON LANE PRIMARY | HT |  |  |  |  | 24.455 | 24.3076 | 24.1497 | 23.9508 | 23.7476 | 23.5434 | 23.3476 | 23.2097 | 23.0834 | 22.2666 | 21.0203 | 19.8876 | 21.6876 | 21.5403 | 21.3824 | 21.1771 | 20.9676 | 20.7571 | 20.5539 | 20.4161 | 20.2897 | 19.4213 | 18.0276 | 16.7529 | 22.3361 | 22.1887 | 22.0308 | 21.8255 | 21.6161 | 21.4055 | 21.2024 | 21.0645 | 20.9382 | 20.0697 | 18.6761 | 17.4003
|  | SUTTON LANE PRIMARY | HE |  |  |  |  | 24.6476 | 24.5571 | 24.4571 | 24.3487 | 24.235 | 24.1234 | 24.0213 | 23.9245 | 23.8424 | 23.5139 | 23.2603 | 7.4213 | 21.8803 | 21.7897 | 21.6897 | 21.5813 | 21.4676 | 21.3561 | 21.2539 | 21.1571 | 21.075 | 20.7382 | 20.4697 | 20.0129 | 22.5287 | 22.4382 | 22.3382 | 22.2297 | 22.1161 | 22.0045 | 21.9024 | 21.8055 | 21.7234 | 21.3876 | 21.1182 | 20.6613
|  | SUTTON LANE PRIMARY | CF |  |  |  |  | 24.7213 | 24.6708 | 24.6182 | 24.5655 | 24.5087 | 24.4497 | 24.3929 | 24.3371 | 24.2813 | 24.0139 | 23.8424 | 23.7287 | 21.9539 | 21.9034 | 21.8508 | 21.7982 | 21.7413 | 21.6824 | 21.6255 | 21.5697 | 21.5139 | 21.2424 | 21.0634 | 20.9424 | 22.6024 | 22.5518 | 22.4992 | 22.4466 | 22.3897 | 22.3308 | 22.2739 | 22.2182 | 22.1624 | 21.8908 | 21.7118 | 21.5908
MANNINGTON GSP | WAREHAM BSP | SWANAGE PRIMARY | MINIMUM HEADROOM | SZ 02010 79296 | NO | YES | 0 | 13.0642 | 42.7916 | 42.5021 | 42.1937 | 41.4063 | 40.6716 | 40.1779 | 39.7642 | 39.3737 | 37.62 | 35.7579 | 19.2158 | 9.6779 | 39.1642 | 38.6463 | 37.9779 | 37.12 | 36.3116 | 35.78 | 35.3368 | 34.9189 | 33.0242 | 30.96 | 28.8842 | 10.0632 | 39.5432 | 39.0179 | 38.3368 | 37.4663 | 36.6579 | 36.1263 | 35.6832 | 35.2653 | 33.3705 | 31.3053 | 29.2284
|  | SWANAGE PRIMARY | EE |  |  |  |  | 13.2263 | 43.0032 | 42.7653 | 42.5158 | 42.1084 | 41.4726 | 41.0526 | 40.6947 | 40.3663 | 39.0011 | 37.6432 | 36.2632 | 10.0242 | 39.6168 | 39.2021 | 38.6316 | 37.8737 | 37.1779 | 36.7253 | 36.3453 | 35.9958 | 34.5221 | 33.0168 | 31.4621 | 10.4158 | 40.0021 | 39.5821 | 39.0021 | 38.2284 | 37.5253 | 37.0726 | 36.6916 | 36.3421 | 34.8674 | 33.3621 | 31.8074
|  | SWANAGE PRIMARY | HT |  |  |  |  | 13.0642 | 42.7916 | 42.5021 | 42.1937 | 41.4063 | 40.6716 | 40.1779 | 39.7642 | 39.3737 | 37.62 | 35.7579 | 33.9063 | 9.6779 | 39.1642 | 38.6463 | 37.9779 | 37.12 | 36.3116 | 35.78 | 35.3368 | 34.9189 | 33.0242 | 30.96 | 28.8842 | 10.0632 | 39.5432 | 39.0179 | 38.3368 | 37.4663 | 36.6579 | 36.1263 | 35.6832 | 35.2653 | 33.3705 | 31.3053 | 29.2284
|  | SWANAGE PRIMARY | HE |  |  |  |  | 13.4284 | 43.2663 | 43.0874 | 42.8947 | 42.6884 | 42.4811 | 42.1663 | 41.9189 | 41.6979 | 40.8547 | 39.9884 | 19.2158 | 10.4747 | 40.2053 | 39.9232 | 39.4811 | 38.8368 | 38.2642 | 37.9326 | 37.6737 | 37.4432 | 36.5442 | 35.58 | 34.5453 | 10.8505 | 40.6021 | 40.3168 | 39.8663 | 39.2084 | 38.6242 | 38.2874 | 38.0263 | 37.7926 | 36.8905 | 35.9263 | 34.8916
|  | SWANAGE PRIMARY | CF |  |  |  |  | 13.5695 | 43.4811 | 43.3895 | 43.2937 | 43.1958 | 43.0947 | 42.9968 | 42.8989 | 42.8011 | 42.3653 | 41.7716 | 41.1568 | 10.6789 | 40.5695 | 40.4011 | 40.1663 | 39.8568 | 39.5537 | 39.3505 | 39.1758 | 39.0011 | 38.1958 | 37.5053 | 36.8032 | 11.0853 | 40.9358 | 40.7842 | 40.5611 | 40.2442 | 39.9347 | 39.7284 | 39.5516 | 39.3747 | 38.5579 | 37.8516 | 37.1495
MINETY GSP | SWINDON BSP | SWINDON PRIMARY | MINIMUM HEADROOM | SU 12449 86967 | NO | YES | 0 | 68.0579 | 67.2968 | 65.9589 | 64.5789 | 63.1758 | 61.7779 | 60.4968 | 59.3032 | 58.1695 | 52.3495 | 44.9589 | -2.6621 | 59.2926 | 57.7147 | 56.24 | 54.7579 | 53.2558 | 51.7611 | 50.3842 | 49.1011 | 47.8779 | 41.4758 | 33.1011 | 25.0242 | 61.0663 | 59.4884 | 58.0158 | 56.5347 | 55.0326 | 53.5368 | 52.1611 | 50.8768 | 49.6537 | 43.2495 | 34.8758 | 26.8063
|  | SWINDON PRIMARY | EE |  |  |  |  | 68.4947 | 67.8737 | 67.2116 | 66.2042 | 65.0505 | 63.9274 | 62.8484 | 61.7947 | 60.8347 | 56.4168 | 50.6032 | 45.0179 | 60.1379 | 59.0832 | 57.7305 | 56.5274 | 55.2937 | 54.0947 | 52.94 | 51.8116 | 50.78 | 45.9505 | 39.3495 | 32.9368 | 61.9095 | 60.8558 | 59.5042 | 58.3011 | 57.0695 | 55.8684 | 54.7137 | 53.5842 | 52.5516 | 47.7126 | 41.1063 | 34.6989
|  | SWINDON PRIMARY | HT |  |  |  |  | 68.0579 | 67.2968 | 65.9589 | 64.5789 | 63.1758 | 61.7779 | 60.4968 | 59.3032 | 58.1695 | 52.3495 | 44.9589 | 37.8895 | 59.2926 | 57.7147 | 56.24 | 54.7579 | 53.2558 | 51.7611 | 50.3842 | 49.1011 | 47.8779 | 41.4758 | 33.1011 | 25.0242 | 61.0663 | 59.4884 | 58.0158 | 56.5347 | 55.0326 | 53.5368 | 52.1611 | 50.8768 | 49.6537 | 43.2495 | 34.8758 | 26.8063
|  | SWINDON PRIMARY | HE |  |  |  |  | 69.0779 | 68.6368 | 68.1484 | 67.6232 | 67.06 | 66.5221 | 65.9589 | 65.2116 | 64.5516 | 61.5821 | 57.1211 | -2.6621 | 60.7821 | 60.3305 | 59.8021 | 58.9326 | 58.0305 | 57.1663 | 56.3316 | 55.5347 | 54.8316 | 51.5768 | 46.4547 | 41.4316 | 62.5537 | 62.1021 | 61.5747 | 60.7053 | 59.8042 | 58.9379 | 58.1021 | 57.3074 | 56.6032 | 53.3463 | 48.2274 | 43.2084
|  | SWINDON PRIMARY | CF |  |  |  |  | 69.4811 | 69.2463 | 69.0042 | 68.7516 | 68.4905 | 68.2242 | 67.9611 | 67.7021 | 67.4421 | 65.7105 | 63.1705 | 60.4653 | 61.1853 | 60.9505 | 60.7084 | 60.4389 | 60.1505 | 59.8074 | 59.3084 | 58.8074 | 58.3042 | 55.9895 | 53.0968 | 49.96 | 62.9568 | 62.7221 | 62.48 | 62.2116 | 61.9211 | 61.5779 | 61.08 | 60.5779 | 60.0758 | 57.7611 | 54.8705 | 51.7358
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | TADLEY PRIMARY | MINIMUM HEADROOM | SU 57753 62717 | NO | YES | 0 | 27.9358 | 27.7211 | 27.4947 | 27.2589 | 27.0147 | 26.7674 | 26.5516 | 26.3516 | 26.1695 | 25.4168 | 24.84 | 7.6768 | 23.8905 | 23.5726 | 23.2474 | 22.9168 | 22.5853 | 22.2432 | 21.9368 | 21.6505 | 21.3863 | 19.7042 | 18.0063 | 16.6084 | 24.6053 | 24.3253 | 24.0358 | 23.7389 | 23.4389 | 23.1305 | 22.8547 | 22.5979 | 22.3621 | 21.3589 | 20.4874 | 19.6863
|  | TADLEY PRIMARY | EE |  |  |  |  | 28.0653 | 27.8895 | 27.7011 | 27.5074 | 27.3042 | 27.1053 | 26.9168 | 26.7337 | 26.5684 | 25.9505 | 28.5389 | 27.5411 | 24.1 | 23.8453 | 23.5811 | 23.3126 | 23.04 | 22.7758 | 22.5168 | 22.2653 | 22.0337 | 20.6968 | 27.7116 | 26.6158 | 24.7863 | 24.56 | 24.3232 | 24.0811 | 23.8326 | 23.5905 | 23.3558 | 23.1263 | 22.9158 | 22.0979 | 30.1579 | 29.0653
|  | TADLEY PRIMARY | HT |  |  |  |  | 27.9358 | 27.7211 | 27.4947 | 27.2589 | 27.0147 | 26.7674 | 26.5516 | 26.3516 | 26.1695 | 25.4168 | 24.84 | 24.0589 | 23.8905 | 23.5726 | 23.2474 | 22.9168 | 22.5853 | 22.2432 | 21.9368 | 21.6505 | 21.3863 | 19.7042 | 18.0063 | 16.6084 | 24.6053 | 24.3253 | 24.0358 | 23.7389 | 23.4389 | 23.1305 | 22.8547 | 22.5979 | 22.3621 | 21.3589 | 20.4874 | 19.6863
|  | TADLEY PRIMARY | HE |  |  |  |  | 28.2337 | 28.1116 | 27.9768 | 27.8305 | 27.6716 | 27.52 | 27.3758 | 27.2421 | 27.1263 | 26.7253 | 26.4895 | 7.6768 | 24.3768 | 24.2084 | 24.0284 | 23.8379 | 23.6368 | 23.4442 | 23.26 | 23.0842 | 22.9274 | 22.3653 | 21.9968 | 21.6032 | 25.0232 | 24.8716 | 24.7084 | 24.5337 | 24.3474 | 24.1684 | 23.9979 | 23.8368 | 23.6926 | 23.1821 | 22.8558 | 22.5474
|  | TADLEY PRIMARY | CF |  |  |  |  | 28.3495 | 28.2853 | 28.2189 | 28.1516 | 28.0779 | 28.0042 | 27.9316 | 27.86 | 27.7874 | 27.4674 | 27.3011 | 27.2042 | 24.5358 | 24.44 | 24.3421 | 24.2421 | 24.1358 | 24.0263 | 23.92 | 23.8147 | 23.7105 | 23.2284 | 22.9221 | 22.6811 | 25.1663 | 25.0821 | 24.9958 | 24.9074 | 24.8126 | 24.7158 | 24.6211 | 24.5274 | 24.4347 | 24.0095 | 23.7516 | 23.5579
IVER 132KV GSP | SLOUGH BSP | TAPLOW PRIMARY | MINIMUM HEADROOM | SU 91721 81234 | NO | NO | 0 | 34.3537 | 34.0716 | 33.7747 | 33.4663 | 33.1411 | 32.8137 | 32.5242 | 32.26 | 32.0126 | 30.7179 | 28.7579 | 6.4853 | 30.4168 | 29.8789 | 29.3347 | 28.7937 | 28.2568 | 27.7147 | 27.1674 | 26.6305 | 26.1116 | 23.7158 | 21.5737 | 19.6779 | 31.3189 | 31.0211 | 30.5684 | 30.0337 | 29.4958 | 28.9516 | 28.4021 | 27.8642 | 27.3421 | 24.9295 | 22.7674 | 20.8642
|  | TAPLOW PRIMARY | EE |  |  |  |  | 34.5189 | 34.2884 | 34.0421 | 33.7863 | 33.5126 | 33.2453 | 32.9916 | 32.7453 | 32.5211 | 31.6695 | 30.64 | 29.3558 | 30.7032 | 30.3516 | 29.9137 | 29.4758 | 29.0368 | 28.6063 | 28.1568 | 27.6926 | 27.2568 | 25.3274 | 23.6589 | 22.2326 | 31.4947 | 31.2537 | 30.9958 | 30.7042 | 30.2705 | 29.84 | 29.3884 | 28.9221 | 28.4811 | 26.5263 | 24.8295 | 23.3958
|  | TAPLOW PRIMARY | HT |  |  |  |  | 34.3537 | 34.0716 | 33.7747 | 33.4663 | 33.1411 | 32.8137 | 32.5242 | 32.26 | 32.0126 | 30.7179 | 28.7579 | 27.0474 | 30.4168 | 29.8789 | 29.3347 | 28.7937 | 28.2568 | 27.7147 | 27.1674 | 26.6305 | 26.1116 | 23.7158 | 21.5737 | 19.6779 | 31.3189 | 31.0211 | 30.5684 | 30.0337 | 29.4958 | 28.9516 | 28.4021 | 27.8642 | 27.3421 | 24.9295 | 22.7674 | 20.8642
|  | TAPLOW PRIMARY | HE |  |  |  |  | 34.7295 | 34.5642 | 34.38 | 34.1811 | 33.9653 | 33.7589 | 33.5642 | 33.3811 | 33.2211 | 32.6684 | 32.3368 | 6.4853 | 30.9484 | 30.7684 | 30.5695 | 30.3558 | 30.0579 | 29.7516 | 29.4284 | 29.0926 | 28.7832 | 27.4853 | 26.4347 | 25.5432 | 31.7211 | 31.5495 | 31.3579 | 31.1526 | 30.9316 | 30.72 | 30.5179 | 30.3147 | 30.0084 | 28.7074 | 27.6505 | 26.7505
|  | TAPLOW PRIMARY | CF |  |  |  |  | 34.8747 | 34.7842 | 34.6905 | 34.5926 | 34.4895 | 34.3842 | 34.2821 | 34.1789 | 34.0789 | 33.6211 | 33.3811 | 33.2421 | 31.1074 | 31.0063 | 30.9021 | 30.7926 | 30.6811 | 30.5653 | 30.4147 | 30.2053 | 29.9958 | 28.9653 | 28.1832 | 27.5316 | 31.8726 | 31.7768 | 31.6789 | 31.5758 | 31.4684 | 31.3579 | 31.2505 | 31.1421 | 31.0358 | 30.1989 | 29.4126 | 28.7558
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON PRIMARY | MINIMUM HEADROOM | ST 94510 07307 | NO | YES | 0 | 7.76 | 7.6737 | 7.4484 | 7.1842 | 6.8895 | 6.5758 | 6.2695 | 5.9632 | 5.6653 | 5.1958 | 4.9221 | -0.037895 | 6.4263 | 6.1874 | 5.9095 | 5.5842 | 5.2179 | 4.8558 | 4.5011 | 4.1453 | 3.7989 | 3.2684 | 2.9621 | 2.6358 | 6.7389 | 6.5074 | 6.2389 | 5.9232 | 5.5684 | 5.2158 | 4.8611 | 4.5063 | 4.1589 | 3.6284 | 3.3221 | 2.9958
|  | TARRANT RUSHTON PRIMARY | EE |  |  |  |  | 7.7832 | 7.7295 | 7.5179 | 7.2674 | 6.9832 | 6.6863 | 6.3916 | 6.0968 | 5.8074 | 5.3947 | 5.1916 | 4.9768 | 6.4758 | 6.2516 | 5.9884 | 5.6768 | 5.3232 | 4.9758 | 4.6337 | 4.2916 | 3.9547 | 3.4853 | 3.2579 | 3.0126 | 6.7874 | 6.5705 | 6.3158 | 6.0147 | 5.6716 | 5.3358 | 4.9937 | 4.6516 | 4.3147 | 3.8453 | 3.6179 | 3.3726
|  | TARRANT RUSHTON PRIMARY | HT |  |  |  |  | 7.76 | 7.6737 | 7.4484 | 7.1842 | 6.8895 | 6.5758 | 6.2695 | 5.9632 | 5.6653 | 5.1958 | 4.9221 | 4.6337 | 6.4263 | 6.1874 | 5.9095 | 5.5842 | 5.2179 | 4.8558 | 4.5011 | 4.1453 | 3.7989 | 3.2684 | 2.9621 | 2.6358 | 6.7389 | 6.5074 | 6.2389 | 5.9232 | 5.5684 | 5.2158 | 4.8611 | 4.5063 | 4.1589 | 3.6284 | 3.3221 | 2.9958
|  | TARRANT RUSHTON PRIMARY | HE |  |  |  |  | 7.8137 | 7.7916 | 7.6105 | 7.3758 | 7.1084 | 6.8326 | 6.5516 | 6.2716 | 5.9968 | 5.6547 | 5.5168 | -0.037895 | 6.5411 | 6.3379 | 6.0937 | 5.8 | 5.4642 | 5.1347 | 4.8074 | 4.4821 | 4.16 | 3.7684 | 3.6137 | 3.4358 | 6.8526 | 6.6558 | 6.4189 | 6.1358 | 5.8105 | 5.4916 | 5.1674 | 4.8421 | 4.5211 | 4.1295 | 3.9737 | 3.7958
|  | TARRANT RUSHTON PRIMARY | CF |  |  |  |  | 7.8347 | 7.8232 | 7.8116 | 7.7726 | 7.6611 | 7.54 | 7.4084 | 7.2674 | 7.1168 | 6.8832 | 6.7937 | 6.7011 | 6.6242 | 6.5305 | 6.4189 | 6.2926 | 6.1526 | 6.0011 | 5.8358 | 5.6589 | 5.4684 | 5.1947 | 5.0937 | 4.9874 | 6.9368 | 6.8411 | 6.7347 | 6.6116 | 6.4768 | 6.3295 | 6.1705 | 5.9989 | 5.8158 | 5.5495 | 5.4516 | 5.3474
MANNINGTON GSP | SALISBURY BSP | TEFFONT PRIMARY | MINIMUM HEADROOM | ST 99837 30994 | NO | YES | 0 | 6.2853 | 6.1779 | 6.0674 | 5.9547 | 5.8453 | 5.7358 | 5.6368 | 5.5442 | 5.4516 | 4.9705 | 4.4947 | -0.48632 | 4.7705 | 4.6537 | 4.5368 | 4.4168 | 4.3 | 4.1832 | 4.0779 | 3.9789 | 3.8789 | 3.3505 | 2.8179 | 2.2747 | 5.1084 | 4.9989 | 4.8895 | 4.7726 | 4.6568 | 4.5411 | 4.4368 | 4.3389 | 4.24 | 3.7179 | 3.1958 | 2.66
|  | TEFFONT PRIMARY | EE |  |  |  |  | 6.36 | 6.2779 | 6.1926 | 6.1032 | 6.0116 | 5.9253 | 5.8432 | 5.7632 | 5.6905 | 5.3305 | 4.9674 | 4.6147 | 4.8516 | 4.7632 | 4.6716 | 4.5768 | 4.48 | 4.3884 | 4.3 | 4.2147 | 4.1379 | 3.7432 | 3.3358 | 2.9347 | 5.1832 | 5.1 | 5.0147 | 4.9242 | 4.8337 | 4.7432 | 4.6568 | 4.5726 | 4.4958 | 4.1063 | 3.7063 | 3.3137
|  | TEFFONT PRIMARY | HT |  |  |  |  | 6.2853 | 6.1779 | 6.0674 | 5.9547 | 5.8453 | 5.7358 | 5.6368 | 5.5442 | 5.4516 | 4.9705 | 4.4947 | 4.0168 | 4.7705 | 4.6537 | 4.5368 | 4.4168 | 4.3 | 4.1832 | 4.0779 | 3.9789 | 3.8789 | 3.3505 | 2.8179 | 2.2747 | 5.1084 | 4.9989 | 4.8895 | 4.7726 | 4.6568 | 4.5411 | 4.4368 | 4.3389 | 4.24 | 3.7179 | 3.1958 | 2.66
|  | TEFFONT PRIMARY | HE |  |  |  |  | 6.4579 | 6.4042 | 6.3484 | 6.2874 | 6.2211 | 6.1589 | 6.1011 | 6.0453 | 5.9958 | 5.7526 | 5.4895 | -0.48632 | 4.9568 | 4.9 | 4.8421 | 4.7758 | 4.7063 | 4.6411 | 4.58 | 4.5211 | 4.4684 | 4.2011 | 3.9032 | 3.6063 | 5.28 | 5.2274 | 5.1716 | 5.1095 | 5.0432 | 4.9811 | 4.9232 | 4.8674 | 4.8179 | 4.5589 | 4.2663 | 3.9747
|  | TEFFONT PRIMARY | CF |  |  |  |  | 6.5011 | 6.4842 | 6.4516 | 6.4189 | 6.3832 | 6.3453 | 6.3105 | 6.2789 | 6.2442 | 6.0895 | 5.9368 | 5.7568 | 5.0168 | 4.9842 | 4.9495 | 4.9147 | 4.8758 | 4.8347 | 4.7979 | 4.7642 | 4.7274 | 4.56 | 4.3874 | 4.1821 | 5.3368 | 5.3074 | 5.2747 | 5.2421 | 5.2063 | 5.1674 | 5.1326 | 5.1011 | 5.0674 | 4.9116 | 4.7453 | 4.5432
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | TEMPLE FARM PRIMARY | MINIMUM HEADROOM | SU 84178 83872 | YES | YES | 0 | 5.0811 | 5.0589 | 5.0358 | 5.0116 | 4.9874 | 4.9621 | 4.94 | 4.92 | 4.9021 | 4.8274 | 4.7737 | 0.028421 | 4.2379 | 4.2042 | 4.1632 | 4.1221 | 4.0832 | 4.0421 | 4.0063 | 3.9726 | 3.9411 | 3.7989 | 3.6842 | 3.5811 | 3.8895 | 3.8495 | 3.8084 | 3.7674 | 3.7284 | 3.6884 | 3.6526 | 3.6189 | 3.5884 | 3.4474 | 3.3326 | 3.2305
|  | TEMPLE FARM PRIMARY | EE |  |  |  |  | 5.0937 | 5.0758 | 5.0568 | 5.0368 | 5.0158 | 4.9968 | 4.9768 | 4.9589 | 4.9432 | 4.8842 | 4.8432 | 4.8158 | 4.2505 | 4.2326 | 4.2084 | 4.1758 | 4.1421 | 4.1116 | 4.0811 | 4.0526 | 4.0263 | 3.9179 | 3.8305 | 3.7579 | 3.9168 | 3.8853 | 3.8537 | 3.82 | 3.7874 | 3.7568 | 3.7263 | 3.6979 | 3.6716 | 3.5642 | 3.4768 | 3.4053
|  | TEMPLE FARM PRIMARY | HT |  |  |  |  | 5.0811 | 5.0589 | 5.0358 | 5.0116 | 4.9874 | 4.9621 | 4.94 | 4.92 | 4.9021 | 4.8274 | 4.7737 | 4.6811 | 4.2379 | 4.2042 | 4.1632 | 4.1221 | 4.0832 | 4.0421 | 4.0063 | 3.9726 | 3.9411 | 3.7989 | 3.6842 | 3.5811 | 3.8895 | 3.8495 | 3.8084 | 3.7674 | 3.7284 | 3.6884 | 3.6526 | 3.6189 | 3.5884 | 3.4474 | 3.3326 | 3.2305
|  | TEMPLE FARM PRIMARY | HE |  |  |  |  | 5.1116 | 5.0989 | 5.0853 | 5.0705 | 5.0547 | 5.04 | 5.0253 | 5.0116 | 5 | 4.96 | 4.9389 | 0.028421 | 4.2684 | 4.2558 | 4.2421 | 4.2274 | 4.2116 | 4.1968 | 4.1821 | 4.1621 | 4.1453 | 4.0811 | 4.0368 | 4.0021 | 3.9558 | 3.9347 | 3.9137 | 3.8916 | 3.8684 | 3.8474 | 3.8274 | 3.8074 | 3.7905 | 3.7253 | 3.6821 | 3.6484
|  | TEMPLE FARM PRIMARY | CF |  |  |  |  | 5.1232 | 5.1168 | 5.1105 | 5.1032 | 5.0968 | 5.0895 | 5.0821 | 5.0747 | 5.0674 | 5.0347 | 5.0189 | 5.0105 | 4.28 | 4.2737 | 4.2674 | 4.26 | 4.2537 | 4.2463 | 4.2389 | 4.2316 | 4.2242 | 4.1716 | 4.1326 | 4.1032 | 3.9747 | 3.9621 | 3.9505 | 3.9368 | 3.9253 | 3.9126 | 3.9 | 3.8874 | 3.8747 | 3.8158 | 3.7779 | 3.7495
MELKSHAM GSP | CHIPPENHAM BSP | TETBURY PRIMARY | MINIMUM HEADROOM | ST 89708 93444 | NO | YES | 0.061053 | 9.5294 | 9.2652 | 8.9778 | 8.6388 | 8.2515 | 7.9399 | 7.6441 | 7.3631 | 5.9073 | 5.2325 | 4.2694 | -2.3159 | 7.3294 | 7.0483 | 6.7409 | 6.3778 | 5.9588 | 5.6283 | 5.3136 | 5.0136 | 3.3757 | 2.6925 | 1.6683 | 0.24726 | 8.0799 | 7.7946 | 7.482 | 7.1104 | 6.6831 | 6.3462 | 6.0252 | 5.7178 | 4.0294 | 3.3304 | 2.2704 | 0.80937
|  | TETBURY PRIMARY | EE |  |  |  |  | 9.6999 | 9.4957 | 9.2694 | 9.0157 | 8.7178 | 8.4578 | 8.2125 | 7.9767 | 7.7894 | 6.6567 | 5.4599 | 4.4483 | 7.5115 | 7.2946 | 7.2809 | 7.0052 | 6.6799 | 6.4009 | 6.1367 | 5.8852 | 5.6894 | 4.4609 | 3.1399 | 1.9957 | 8.2662 | 8.0452 | 7.802 | 7.5262 | 7.1999 | 6.9178 | 6.6536 | 6.3988 | 6.1978 | 4.9483 | 3.602 | 2.4515
|  | TETBURY PRIMARY | HT |  |  |  |  | 9.5294 | 9.2652 | 8.9778 | 8.6388 | 8.2515 | 7.9399 | 7.6441 | 7.3631 | 5.9073 | 5.2325 | 4.2694 | 2.9799 | 7.3294 | 7.0483 | 6.7409 | 6.3778 | 5.9588 | 5.6283 | 5.3136 | 5.0136 | 3.3757 | 2.6925 | 1.6683 | 0.24726 | 8.0799 | 7.7946 | 7.482 | 7.1104 | 6.6831 | 6.3462 | 6.0252 | 5.7178 | 4.0294 | 3.3304 | 2.2704 | 0.80937
|  | TETBURY PRIMARY | HE |  |  |  |  | 9.8157 | 9.7357 | 9.6252 | 9.4346 | 9.1894 | 8.9915 | 8.8094 | 8.6357 | 8.5104 | 7.6925 | 6.8073 | -2.3159 | 7.7473 | 7.6041 | 7.4346 | 7.2315 | 6.9683 | 6.7588 | 6.5652 | 6.3809 | 6.2515 | 5.3662 | 4.3873 | 3.522 | 8.5052 | 8.3599 | 8.1883 | 7.982 | 7.7125 | 7.4978 | 7.3009 | 7.1125 | 6.9788 | 6.0683 | 5.0588 | 4.1641
|  | TETBURY PRIMARY | CF |  |  |  |  | 9.8904 | 9.8494 | 9.8052 | 9.7599 | 9.7115 | 9.6294 | 9.5304 | 9.4283 | 9.3357 | 8.7304 | 8.1609 | 7.6588 | 7.8515 | 7.7978 | 7.7115 | 7.6241 | 7.5325 | 7.4378 | 7.3336 | 7.2231 | 7.1252 | 6.4704 | 5.842 | 5.2841 | 8.6104 | 8.5567 | 8.4683 | 8.3799 | 8.2862 | 8.1904 | 8.0831 | 7.9715 | 7.8704 | 7.1988 | 6.5515 | 5.9746
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM PRIMARY | MINIMUM HEADROOM | SU 52758 66466 | NO | YES | 0.10526 | 36.7916 | 36.3074 | 35.7926 | 35.2621 | 34.6737 | 33.2674 | 31.3926 | 29.7 | 28.1811 | 20.9916 | 16.9947 | -16.1168 | 29.5179 | 28.8947 | 27.9705 | 26.8011 | 25.6084 | 24.0779 | 22.0053 | 20.0947 | 18.3768 | 10.1979 | 5.7095 | 2.34 | 30.7316 | 30.1084 | 29.1874 | 28.0211 | 26.8316 | 25.3074 | 23.2432 | 21.3789 | 19.7084 | 11.7579 | 7.2642 | 3.8947
|  | THATCHAM PRIMARY | EE |  |  |  |  | 37.0768 | 36.68 | 36.2547 | 35.8137 | 35.3547 | 34.9116 | 33.5642 | 31.7116 | 30.2347 | 23.4621 | 20.1642 | 17.8853 | 29.8032 | 29.4063 | 28.9516 | 28.0579 | 27.1147 | 25.9874 | 24.3737 | 22.3147 | 20.6411 | 12.8905 | 9.1853 | 6.6116 | 31.0168 | 30.62 | 30.1653 | 29.2726 | 28.3326 | 27.2095 | 25.6011 | 23.5505 | 21.9211 | 14.4032 | 10.7263 | 8.1505
|  | THATCHAM PRIMARY | HT |  |  |  |  | 36.7916 | 36.3074 | 35.7926 | 35.2621 | 34.6737 | 33.2674 | 31.3926 | 29.7 | 28.1811 | 20.9916 | 16.9947 | 13.9926 | 29.5179 | 28.8947 | 27.9705 | 26.8011 | 25.6084 | 24.0779 | 22.0053 | 20.0947 | 18.3768 | 10.1979 | 5.7095 | 2.34 | 30.7316 | 30.1084 | 29.1874 | 28.0211 | 26.8316 | 25.3074 | 23.2432 | 21.3789 | 19.7084 | 11.7579 | 7.2642 | 3.8947
|  | THATCHAM PRIMARY | HE |  |  |  |  | 37.4611 | 37.1811 | 36.8726 | 36.54 | 36.1832 | 35.8421 | 35.5211 | 33.8558 | 32.6032 | 26.8347 | 24.3737 | -16.1168 | 30.1874 | 29.9074 | 29.5989 | 29.2663 | 28.8705 | 27.9453 | 26.4642 | 24.6 | 23.2053 | 16.56 | 13.7347 | 12.0684 | 31.4011 | 31.1211 | 30.8126 | 30.48 | 30.0842 | 29.1611 | 27.6863 | 25.8316 | 24.4442 | 18.0063 | 15.2589 | 13.6211
|  | THATCHAM PRIMARY | CF |  |  |  |  | 37.7242 | 37.5789 | 37.4274 | 37.2705 | 37.1084 | 36.9421 | 36.7779 | 36.6179 | 36.4547 | 33.7474 | 30.3474 | 29.3568 | 30.4505 | 30.3053 | 30.1537 | 29.9968 | 29.8347 | 29.6684 | 29.5053 | 29.3442 | 28.8505 | 24.4032 | 20.4737 | 19.3421 | 31.6642 | 31.5189 | 31.3674 | 31.2105 | 31.0474 | 30.8821 | 30.7179 | 30.5568 | 30.0642 | 25.6389 | 21.8232 | 20.7253
NORTH HYDE GSP | NORTH HYDE BSP | THE GREEN PRIMARY | MINIMUM HEADROOM | TQ 12414 79503 | NO | NO | 0 | 14.5579 | 11.9105 | 11.8242 | 11.0211 | 9.6832 | 8.1968 | 7.14 | 7.0789 | 7.0158 | 6.7074 | 6.4895 | -10.5474 | 10.2242 | 7.0589 | 6.9726 | 5.9642 | 4.3611 | 2.5768 | 1.3105 | 1.2453 | 1.1768 | 0.84 | 0.59368 | 0.37474 | 10.8905 | 7.7158 | 7.6295 | 6.6211 | 5.0168 | 3.2326 | 1.9653 | 1.9 | 1.8316 | 1.4947 | 1.2484 | 1.0295
|  | THE GREEN PRIMARY | EE |  |  |  |  | 14.7147 | 12.2537 | 12.1832 | 12.2547 | 12.1758 | 12.0989 | 9.8832 | 9.7558 | 9.6368 | 9.14 | 8.6579 | 8.1568 | 10.4 | 7.4589 | 7.3884 | 7.3137 | 7.2632 | 7.1863 | 4.5926 | 4.4568 | 4.3284 | 3.7874 | 3.2684 | 2.7032 | 11.0684 | 8.1158 | 8.0453 | 7.9705 | 7.8916 | 7.8147 | 5.2263 | 5.0895 | 4.9611 | 4.4221 | 3.9063 | 3.3421
|  | THE GREEN PRIMARY | HT |  |  |  |  | 14.5579 | 11.9105 | 11.8242 | 11.8716 | 11.7768 | 11.6789 | 9.2253 | 9.0789 | 8.9389 | 8.3011 | 7.5611 | 6.8421 | 10.2242 | 7.0589 | 6.9726 | 6.8811 | 6.8147 | 6.7168 | 3.8453 | 3.6874 | 3.5347 | 2.8568 | 2.0295 | 1.2211 | 10.8905 | 7.7158 | 7.6295 | 7.5379 | 7.4432 | 7.3453 | 4.48 | 4.3221 | 4.1695 | 3.4947 | 2.6695 | 1.8621
|  | THE GREEN PRIMARY | HE |  |  |  |  | 14.8189 | 12.3884 | 12.3284 | 12.4116 | 12.3421 | 12.2758 | 10.0874 | 9.9926 | 9.9063 | 9.5842 | 9.2168 | -10.5474 | 10.5168 | 7.6105 | 7.5505 | 7.4853 | 7.4453 | 7.3789 | 4.8137 | 4.7137 | 4.6211 | 4.2737 | 3.8453 | 3.4768 | 11.1863 | 8.2684 | 8.2084 | 8.1432 | 8.0737 | 8.0074 | 5.4474 | 5.3463 | 5.2537 | 4.9063 | 4.4758 | 4.1084
|  | THE GREEN PRIMARY | CF |  |  |  |  | 15.1126 | 14.6568 | 12.6989 | 11.0211 | 9.6832 | 8.1968 | 7.14 | 7.0789 | 7.0158 | 6.7074 | 6.4895 | 6.2989 | 11.6726 | 10.3242 | 7.98 | 5.9642 | 4.3611 | 2.5768 | 1.3105 | 1.2453 | 1.1768 | 0.84 | 0.59368 | 0.37474 | 12.3621 | 10.9905 | 8.6368 | 6.6211 | 5.0168 | 3.2326 | 1.9653 | 1.9 | 1.8316 | 1.4947 | 1.2484 | 1.0295
FLEET-BRAMLEY GSP | READING TOWN BSP | THE MALL PRIMARY | MINIMUM HEADROOM | SU 71319 73293 | NO | YES | 0 | 35.3716 | 35.2537 | 35.1211 | 34.9337 | 34.0095 | 33.0832 | 32.1727 | 31.2737 | 30.3885 | 29.4958 | 28.5243 | 7.5716 | 31.5327 | 31.4148 | 31.2548 | 30.7021 | 28.9137 | 27.8432 | 26.7906 | 25.7485 | 24.72 | 23.7485 | 22.6664 | 21.5979 | 32.1611 | 32.0432 | 31.9032 | 31.7274 | 30.3853 | 29.3179 | 28.2664 | 27.2253 | 26.2 | 25.2285 | 24.1474 | 23.0811
|  | THE MALL PRIMARY | EE |  |  |  |  | 35.4485 | 35.3537 | 35.2527 | 35.0927 | 34.5537 | 33.9316 | 33.2106 | 32.199 | 31.1558 | 30.1653 | 29.4327 | 28.7337 | 31.6095 | 31.5148 | 31.3864 | 30.9495 | 29.539 | 28.8095 | 27.9758 | 26.8 | 25.5832 | 24.4779 | 23.659 | 22.8695 | 32.2379 | 32.1432 | 32.0348 | 31.8843 | 31.0106 | 30.2821 | 29.4495 | 28.2758 | 27.0621 | 25.9569 | 25.14 | 24.3516
|  | THE MALL PRIMARY | HT |  |  |  |  | 35.3716 | 35.2537 | 35.1211 | 34.9337 | 34.0095 | 33.0832 | 32.1727 | 31.2737 | 30.3885 | 29.4958 | 28.5243 | 27.5758 | 31.5327 | 31.4148 | 31.2548 | 30.7021 | 28.9137 | 27.8432 | 26.7906 | 25.7485 | 24.72 | 23.7485 | 22.6664 | 21.5979 | 32.1611 | 32.0432 | 31.9032 | 31.7274 | 30.3853 | 29.3179 | 28.2664 | 27.2253 | 26.2 | 25.2285 | 24.1474 | 23.0811
|  | THE MALL PRIMARY | HE |  |  |  |  | 35.5095 | 35.4316 | 35.3453 | 35.2137 | 34.8495 | 34.2664 | 33.5369 | 32.5643 | 31.6043 | 30.9127 | 30.4316 | 7.5716 | 31.6706 | 31.5927 | 31.4885 | 31.1685 | 29.8811 | 29.18 | 28.3348 | 27.199 | 26.0769 | 25.3053 | 24.7664 | 24.259 | 32.299 | 32.2211 | 32.1348 | 32.0021 | 31.3516 | 30.6516 | 29.8085 | 28.6748 | 27.5548 | 26.7843 | 26.2453 | 25.739
|  | THE MALL PRIMARY | CF |  |  |  |  | 35.5579 | 35.5085 | 35.4569 | 35.4032 | 35.3432 | 35.2843 | 35.22 | 35.1516 | 35.0769 | 33.779 | 33.4053 | 33.0885 | 31.719 | 31.6695 | 31.6179 | 31.5516 | 31.4769 | 31.4179 | 31.3064 | 31.1516 | 30.9474 | 28.6358 | 28.2169 | 27.8548 | 32.3474 | 32.2979 | 32.2464 | 32.1927 | 32.1253 | 32.0664 | 32.0043 | 31.939 | 31.8674 | 30.1085 | 29.6906 | 29.3285
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | THEALE PRIMARY | MINIMUM HEADROOM | SU 64755 71015 | NO | YES | 2.1053 | 24.2771 | 24.1497 | 23.1424 | 23.0908 | 23.0382 | 22.9866 | 22.9371 | 22.8908 | 22.8487 | 22.5276 | 22.1887 | 4.1855 | 22.0518 | 21.7297 | 20.5276 | 20.4761 | 20.4234 | 20.3718 | 20.3224 | 20.2761 | 20.2339 | 19.8782 | 19.4961 | 19.2013 | 22.475 | 22.135 | 20.955 | 20.9034 | 20.8508 | 20.7992 | 20.7497 | 20.7034 | 20.6613 | 20.3139 | 19.9413 | 19.6466
|  | THEALE PRIMARY | EE |  |  |  |  | 24.3087 | 24.2308 | 23.1424 | 23.0908 | 23.0382 | 22.9866 | 22.9371 | 22.8908 | 22.8487 | 22.5276 | 22.1887 | 21.9634 | 22.1192 | 21.8171 | 20.5276 | 20.4761 | 20.4234 | 20.3718 | 20.3224 | 20.2761 | 20.2339 | 19.8782 | 19.4961 | 19.2445 | 22.5445 | 22.2255 | 20.955 | 20.9034 | 20.8508 | 20.7992 | 20.7497 | 20.7034 | 20.6613 | 20.3139 | 19.9413 | 19.6961
|  | THEALE PRIMARY | HT |  |  |  |  | 24.2771 | 24.1497 | 23.8561 | 23.5055 | 23.2687 | 23.1718 | 23.0834 | 23.0013 | 22.9255 | 22.5813 | 22.2276 | 21.895 | 22.0518 | 21.7297 | 21.3982 | 20.9887 | 20.715 | 20.6118 | 20.5161 | 20.4287 | 20.3455 | 19.9718 | 19.5739 | 19.2013 | 22.475 | 22.135 | 21.7929 | 21.3961 | 21.1297 | 21.0276 | 20.9339 | 20.8476 | 20.7666 | 20.3982 | 20.0097 | 19.6466
|  | THEALE PRIMARY | HE |  |  |  |  | 24.3508 | 24.3171 | 24.0939 | 23.7929 | 23.5961 | 23.5403 | 23.4887 | 23.4392 | 23.3971 | 23.235 | 23.0624 | 4.1855 | 22.2097 | 21.935 | 21.655 | 21.3055 | 21.0761 | 21.0182 | 20.9634 | 20.9118 | 20.8666 | 20.6929 | 20.4971 | 20.3118 | 22.6382 | 22.3476 | 22.0518 | 21.7066 | 21.4834 | 21.4266 | 21.3718 | 21.3203 | 21.2761 | 21.1055 | 20.915 | 20.7339
|  | THEALE PRIMARY | CF |  |  |  |  | 24.3803 | 24.3624 | 24.3434 | 24.3245 | 24.3045 | 24.2824 | 24.2497 | 24.2192 | 24.1876 | 24.0434 | 23.9287 | 23.8129 | 22.4118 | 22.2761 | 22.1476 | 22.0024 | 21.9087 | 21.8729 | 21.8392 | 21.8066 | 21.7729 | 21.6203 | 21.495 | 21.3655 | 22.7897 | 22.6918 | 22.5718 | 22.4192 | 22.3203 | 22.2845 | 22.2487 | 22.215 | 22.1813 | 22.0245 | 21.8929 | 21.7582
MELKSHAM GSP | ANDOVER BSP | THRUXTON PRIMARY | MINIMUM HEADROOM | SU 29134 45674 | NO | YES | 0 | 7.2811 | 7.2674 | 7.4011 | 6.5116 | 5.3558 | 4.2011 | 3.0568 | 2.1684 | 1.1621 | -0.88737 | -1.6789 | -4.94 | 6.2811 | 6.2221 | 5.9547 | 4.9221 | 3.5874 | 2.2516 | 0.92737 | -0.094737 | -1.2579 | -3.5579 | -4.3821 | -5.0979 | 6.4726 | 6.3747 | 6.1074 | 5.0779 | 3.7389 | 2.4021 | 1.0747 | 0.049474 | -1.1179 | -3.4526 | -4.32 | -5.0526
|  | THRUXTON PRIMARY | EE |  |  |  |  | 7.3558 | 7.2674 | 7.6074 | 7.0368 | 6.2305 | 5.4463 | 4.5632 | 3.5611 | 2.4021 | -0.59263 | -1.3042 | -1.8179 | 6.3926 | 6.2726 | 6.1811 | 5.5242 | 4.5968 | 3.6968 | 2.68 | 1.5253 | 0.18632 | -3.2126 | -3.9221 | -4.4768 | 6.5779 | 6.4632 | 6.3337 | 5.6768 | 4.7463 | 3.8432 | 2.8221 | 1.6611 | 0.31579 | -3.1305 | -3.9011 | -4.4758
|  | THRUXTON PRIMARY | HT |  |  |  |  | 7.2811 | 7.6421 | 7.4011 | 6.5116 | 5.3558 | 4.2011 | 3.0568 | 2.1684 | 1.1621 | -0.88737 | -1.6789 | -2.3358 | 6.2811 | 6.2221 | 5.9547 | 4.9221 | 3.5874 | 2.2516 | 0.92737 | -0.094737 | -1.2579 | -3.5579 | -4.3821 | -5.0979 | 6.4726 | 6.3747 | 6.1074 | 5.0779 | 3.7389 | 2.4021 | 1.0747 | 0.049474 | -1.1179 | -3.4526 | -4.32 | -5.0526
|  | THRUXTON PRIMARY | HE |  |  |  |  | 7.4516 | 7.3947 | 7.8179 | 7.2695 | 6.4705 | 5.7137 | 4.8021 | 3.8242 | 2.7274 | 0.15368 | -0.25263 | -4.94 | 6.5347 | 6.4589 | 6.4095 | 5.7737 | 4.8495 | 3.9747 | 2.9158 | 1.7779 | 0.50105 | -2.4653 | -2.9011 | -3.3105 | 6.6874 | 6.6242 | 6.5621 | 5.9284 | 5.0021 | 4.1253 | 3.0653 | 1.9274 | 0.64842 | -2.3337 | -2.7874 | -3.2126
|  | THRUXTON PRIMARY | CF |  |  |  |  | 7.5095 | 7.48 | 8.0084 | 7.9579 | 7.8937 | 7.8347 | 7.6874 | 7.5305 | 7.3042 | 3.4368 | 2.9074 | 2.66 | 6.6063 | 6.5695 | 6.6158 | 6.5611 | 6.4937 | 6.4305 | 6.2632 | 6.0863 | 5.8263 | 1.3095 | 0.70947 | 0.44316 | 6.7516 | 6.7179 | 6.7695 | 6.7137 | 6.6453 | 6.5811 | 6.4126 | 6.2347 | 5.9737 | 1.4568 | 0.84842 | 0.57158
MELKSHAM GSP | WEST GRAFTON BSP | TIDWORTH PRIMARY | MINIMUM HEADROOM | SU 24088 49593 | NO | YES | 0 | 12.8537 | 12.08 | 11.3032 | 10.3368 | 9.1284 | 7.7095 | 6.3221 | 4.5568 | 2.9084 | -6.3232 | -9.3779 | -16.9821 | 9.1053 | 8.2011 | 7.2937 | 6.1537 | 4.7274 | 3.1253 | 1.5411 | -0.48632 | -2.3789 | -13.0137 | -16.4 | -18.9126 | 9.7811 | 8.8632 | 7.9432 | 6.7884 | 5.3337 | 3.7053 | 2.1179 | 0.086316 | -1.8126 | -12.4842 | -15.9295 | -18.4653
|  | TIDWORTH PRIMARY | EE |  |  |  |  | 13.22 | 12.4484 | 11.6411 | 10.86 | 9.9758 | 9.0168 | 7.8737 | 5.7253 | 4.0779 | -5.1368 | -7.8463 | -9.6421 | 9.5295 | 8.6168 | 7.6653 | 6.7463 | 5.7137 | 4.5916 | 3.3137 | 0.83684 | -1.0526 | -11.6579 | -14.6221 | -16.6358 | 10.2095 | 9.2832 | 8.3189 | 7.3853 | 6.3326 | 5.1842 | 3.8821 | 1.3989 | -0.49895 | -11.1642 | -14.2147 | -16.2526
|  | TIDWORTH PRIMARY | HT |  |  |  |  | 12.8537 | 12.08 | 11.3032 | 10.3368 | 9.1284 | 7.7095 | 6.3221 | 4.5568 | 2.9084 | -6.3232 | -9.3779 | -11.6189 | 9.1053 | 8.2011 | 7.2937 | 6.1537 | 4.7274 | 3.1253 | 1.5411 | -0.48632 | -2.3789 | -13.0137 | -16.4 | -18.9126 | 9.7811 | 8.8632 | 7.9432 | 6.7884 | 5.3337 | 3.7053 | 2.1179 | 0.086316 | -1.8126 | -12.4842 | -15.9295 | -18.4653
|  | TIDWORTH PRIMARY | HE |  |  |  |  | 13.4495 | 12.94 | 12.2042 | 11.4674 | 10.6547 | 9.7832 | 8.7063 | 6.66 | 5.1621 | -3.3537 | -5.4147 | -16.9821 | 9.9032 | 9.1747 | 8.2979 | 7.4221 | 6.4632 | 5.4295 | 4.1905 | 1.8211 | 0.088421 | -9.8053 | -12.1463 | -13.7168 | 10.5874 | 9.8484 | 8.9589 | 8.0705 | 7.0926 | 6.0389 | 4.7747 | 2.4 | 0.66526 | -9.2421 | -11.6042 | -13.1968
|  | TIDWORTH PRIMARY | CF |  |  |  |  | 13.6495 | 13.5137 | 13.2916 | 12.9432 | 12.7663 | 12.6011 | 12.3653 | 11.9737 | 11.5116 | 5.1337 | 2.5874 | 1.7 | 10.3442 | 10.0189 | 9.5853 | 9.1726 | 8.9758 | 8.7958 | 8.5253 | 8.0632 | 7.5116 | -0.0084211 | -2.9505 | -3.9505 | 11.0337 | 10.7042 | 10.2642 | 9.8453 | 9.6442 | 9.46 | 9.1842 | 8.7126 | 8.1505 | 0.57263 | -2.3779 | -3.3926
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY PRIMARY | MINIMUM HEADROOM | ST 93438 29127 | NO | YES | 0.21053 | 9.1758 | 8.98 | 8.7705 | 8.5189 | 8.2547 | 7.9916 | 7.8411 | 7.7053 | 7.5684 | 6.9032 | 6.2821 | 0.036842 | 7.7653 | 7.5484 | 7.3168 | 7.0337 | 6.7358 | 6.44 | 6.2768 | 6.1305 | 5.9821 | 5.2432 | 4.5411 | 3.8547 | 8.0747 | 7.8611 | 7.6305 | 7.3505 | 7.0558 | 6.7642 | 6.6021 | 6.4568 | 6.3084 | 5.5768 | 4.8821 | 4.2053
|  | TISBURY PRIMARY | EE |  |  |  |  | 9.2863 | 9.14 | 8.9747 | 8.7674 | 8.5421 | 8.3274 | 8.1421 | 7.9968 | 7.8905 | 7.3895 | 6.9232 | 6.4684 | 7.8874 | 7.7263 | 7.5442 | 7.3105 | 7.0579 | 6.8147 | 6.6095 | 6.4484 | 6.3347 | 5.7811 | 5.2516 | 4.7274 | 8.1958 | 8.0368 | 7.8558 | 7.6242 | 7.3747 | 7.1347 | 6.9305 | 6.7716 | 6.6589 | 6.1095 | 5.5874 | 5.0684
|  | TISBURY PRIMARY | HT |  |  |  |  | 9.1758 | 8.98 | 8.7705 | 8.5189 | 8.2547 | 7.9916 | 7.8411 | 7.7053 | 7.5684 | 6.9032 | 6.2821 | 5.6832 | 7.7653 | 7.5484 | 7.3168 | 7.0337 | 6.7358 | 6.44 | 6.2768 | 6.1305 | 5.9821 | 5.2432 | 4.5411 | 3.8547 | 8.0747 | 7.8611 | 7.6305 | 7.3505 | 7.0558 | 6.7642 | 6.6021 | 6.4568 | 6.3084 | 5.5768 | 4.8821 | 4.2053
|  | TISBURY PRIMARY | HE |  |  |  |  | 9.4021 | 9.3337 | 9.2105 | 9.0442 | 8.8589 | 8.6811 | 8.5347 | 8.4316 | 8.3611 | 8.0379 | 7.7305 | 0.036842 | 8.0505 | 7.94 | 7.8042 | 7.6158 | 7.4063 | 7.2053 | 7.0411 | 6.9284 | 6.8537 | 6.4979 | 6.1463 | 5.7884 | 8.3579 | 8.2474 | 8.1137 | 7.9274 | 7.72 | 7.5211 | 7.3589 | 7.2474 | 7.1726 | 6.82 | 6.4726 | 6.12
|  | TISBURY PRIMARY | CF |  |  |  |  | 9.4537 | 9.4263 | 9.3968 | 9.3674 | 9.3147 | 9.2579 | 9.1905 | 9.1063 | 9.0168 | 8.6263 | 8.4189 | 8.2147 | 8.1242 | 8.0884 | 8.0347 | 7.9811 | 7.92 | 7.8579 | 7.7832 | 7.6874 | 7.5853 | 7.1421 | 6.9063 | 6.6674 | 8.4316 | 8.3958 | 8.3421 | 8.2884 | 8.2284 | 8.1663 | 8.0926 | 7.9979 | 7.8968 | 7.4589 | 7.2253 | 6.9905
LOVEDEAN GSP | FAREHAM (MAIN) BSP | TITCHFIELD PRIMARY | MINIMUM HEADROOM | SU 54104 05695 | NO | YES | 1.0421 | 14.9447 | 13.6605 | 12.0532 | 10.13 | 7.9353 | 20.7416 | 18.5795 | 16.4405 | 14.2984 | 8.1963 | 6.0679 | -1.4721 | 11.83 | 10.2479 | 8.37 | 6.1532 | 3.6289 | 16.1068 | 13.6163 | 11.1479 | 8.6763 | 1.7353 | -0.56789 | -2.6163 | 12.1805 | 10.6237 | 8.7479 | 6.5353 | 4.0089 | 16.4847 | 13.9921 | 11.5205 | 9.0468 | 2.0711 | -0.28684 | -2.3553
|  | TITCHFIELD PRIMARY | EE |  |  |  |  | 15.3584 | 14.2668 | 12.9374 | 11.2247 | 9.2195 | 22.2279 | 20.1774 | 17.9153 | 15.6237 | 9.0195 | 7.27 | 5.8542 | 12.3195 | 10.9753 | 9.3679 | 7.3942 | 5.0837 | 17.7911 | 15.4289 | 12.8174 | 10.17 | 2.6268 | 0.78895 | -0.77842 | 12.6563 | 11.3479 | 9.7447 | 7.7721 | 5.4605 | 18.1647 | 15.7984 | 13.1805 | 10.5279 | 2.9268 | 1.0153 | -0.57526
|  | TITCHFIELD PRIMARY | HT |  |  |  |  | 14.9447 | 13.6605 | 12.0532 | 10.13 | 7.9353 | 20.7416 | 18.5795 | 16.4405 | 14.2984 | 8.1963 | 6.0679 | 4.2247 | 11.83 | 10.2479 | 8.37 | 6.1532 | 3.6289 | 16.1068 | 13.6163 | 11.1479 | 8.6763 | 1.7353 | -0.56789 | -2.6163 | 12.1805 | 10.6237 | 8.7479 | 6.5353 | 4.0089 | 16.4847 | 13.9921 | 11.5205 | 9.0468 | 2.0711 | -0.28684 | -2.3553
|  | TITCHFIELD PRIMARY | HE |  |  |  |  | 15.7237 | 14.7395 | 13.5384 | 11.9247 | 10.0026 | 23.1142 | 21.1374 | 18.97 | 16.8058 | 10.9184 | 9.7458 | -1.4721 | 12.7353 | 11.51 | 10.0205 | 8.1511 | 5.9279 | 18.7416 | 16.45 | 13.9332 | 11.4163 | 4.6142 | 3.3005 | 2.1753 | 13.0637 | 11.8805 | 10.3963 | 8.5311 | 6.3068 | 19.1205 | 16.8289 | 14.3132 | 11.7953 | 4.9753 | 3.6384 | 2.4953
|  | TITCHFIELD PRIMARY | CF |  |  |  |  | 16.1658 | 15.9963 | 15.5311 | 14.9984 | 14.4016 | 28.7542 | 27.9395 | 27.0374 | 26.0111 | 20.2405 | 19.3858 | 18.7226 | 13.5795 | 13.0689 | 12.4932 | 11.83 | 11.0911 | 25.2858 | 24.3342 | 23.29 | 22.0984 | 15.3889 | 14.4363 | 13.6953 | 13.8805 | 13.3868 | 12.83 | 12.19 | 11.4637 | 25.6584 | 24.7068 | 23.6626 | 22.47 | 15.7637 | 14.8005 | 14.0458
FLEET-BRAMLEY GSP | ALDERSHOT BSP | TONGHAM PRIMARY | MINIMUM HEADROOM | SU 88310 49487 | NO | YES | 0.073684 | 32.6732 | 32.3353 | 31.9732 | 31.0153 | 29.9458 | 28.9437 | 28.0795 | 27.2521 | 26.4647 | 23.1121 | 20.8563 | -4.5332 | 29.0268 | 27.9574 | 26.7489 | 25.5447 | 24.3521 | 23.2395 | 22.2816 | 21.3605 | 20.4858 | 16.7774 | 14.3047 | 12.0816 | 30.2679 | 29.1847 | 27.9616 | 26.7426 | 25.5332 | 24.4058 | 23.4353 | 22.5026 | 21.6153 | 17.89 | 15.4005 | 13.1711
|  | TONGHAM PRIMARY | EE |  |  |  |  | 32.8689 | 32.5879 | 32.2889 | 31.7553 | 30.7921 | 29.9068 | 29.13 | 28.3658 | 27.6542 | 24.7689 | 23.0258 | 21.5458 | 29.4563 | 28.5142 | 27.4353 | 26.3532 | 25.2742 | 24.2868 | 23.4247 | 22.5774 | 21.7868 | 18.5911 | 16.6868 | 15.0405 | 30.7005 | 29.7479 | 28.6553 | 27.5574 | 26.4637 | 25.4637 | 24.5879 | 23.7279 | 22.9247 | 19.6932 | 17.7679 | 16.1132
|  | TONGHAM PRIMARY | HT |  |  |  |  | 32.6732 | 32.3353 | 31.9732 | 31.0153 | 29.9458 | 28.9437 | 28.0795 | 27.2521 | 26.4647 | 23.1121 | 20.8563 | 18.8532 | 29.0268 | 27.9574 | 26.7489 | 25.5447 | 24.3521 | 23.2395 | 22.2816 | 21.3605 | 20.4858 | 16.7774 | 14.3047 | 12.0816 | 30.2679 | 29.1847 | 27.9616 | 26.7426 | 25.5332 | 24.4058 | 23.4353 | 22.5026 | 21.6153 | 17.89 | 15.4005 | 13.1711
|  | TONGHAM PRIMARY | HE |  |  |  |  | 33.13 | 32.9289 | 32.7068 | 32.4689 | 31.9258 | 31.1774 | 30.5384 | 29.9163 | 29.3437 | 27.17 | 26.09 | -4.5332 | 30.0332 | 29.2689 | 28.3584 | 27.4384 | 26.51 | 25.6721 | 24.9595 | 24.2647 | 23.6216 | 21.1826 | 19.9889 | 18.9837 | 31.0658 | 30.51 | 29.5879 | 28.6553 | 27.7142 | 26.8637 | 26.1416 | 25.4384 | 24.7847 | 22.3058 | 21.1037 | 20.0932
|  | TONGHAM PRIMARY | CF |  |  |  |  | 33.3111 | 33.2037 | 33.0921 | 32.9774 | 32.8563 | 32.7332 | 32.6132 | 32.4932 | 32.3732 | 30.8858 | 30.0974 | 29.4658 | 30.6258 | 30.2068 | 29.7374 | 29.2542 | 28.8195 | 28.3911 | 27.9953 | 27.5837 | 27.1626 | 25.3532 | 24.4742 | 23.7595 | 31.2742 | 31.1458 | 30.9837 | 30.4942 | 30.0532 | 29.6195 | 29.2174 | 28.7995 | 28.3753 | 26.5384 | 25.6437 | 24.9153
MINETY GSP | TOOTHILL BSP | TOOTHILL PRIMARY | MINIMUM HEADROOM | SU 13215 83986 | NO | YES | 0 | 34.6874 | 34.4811 | 34.2621 | 34.0358 | 33.8 | 33.5632 | 33.3537 | 33.0126 | 32.4463 | 30.6389 | 28.38 | 2.26 | 30.1337 | 29.9274 | 29.7084 | 29.4379 | 28.9368 | 28.2242 | 27.5421 | 26.8884 | 26.2537 | 24.2558 | 21.6674 | 19.2337 | 31.3684 | 31.1621 | 30.9432 | 30.6632 | 30.1105 | 29.4232 | 28.7579 | 28.1232 | 27.4937 | 25.4979 | 22.9074 | 20.4758
|  | TOOTHILL PRIMARY | EE |  |  |  |  | 34.8063 | 34.6358 | 34.4547 | 34.2642 | 34.0663 | 33.8747 | 33.6926 | 33.5158 | 33.3137 | 31.8421 | 30.1 | 28.4305 | 30.2526 | 30.0821 | 29.9011 | 29.7105 | 29.5126 | 29.0758 | 28.5263 | 27.8621 | 27.2063 | 25.6095 | 23.6337 | 21.7232 | 31.4874 | 31.3168 | 31.1358 | 30.9453 | 30.7474 | 30.2516 | 29.7179 | 29.0726 | 28.4368 | 26.8547 | 24.88 | 22.9716
|  | TOOTHILL PRIMARY | HT |  |  |  |  | 34.6874 | 34.4811 | 34.2621 | 34.0358 | 33.8 | 33.5632 | 33.3537 | 33.0126 | 32.4463 | 30.6389 | 28.38 | 26.2442 | 30.1337 | 29.9274 | 29.7084 | 29.4379 | 28.9368 | 28.2242 | 27.5421 | 26.8884 | 26.2537 | 24.2558 | 21.6674 | 19.2337 | 31.3684 | 31.1621 | 30.9432 | 30.6632 | 30.1105 | 29.4232 | 28.7579 | 28.1232 | 27.4937 | 25.4979 | 22.9074 | 20.4758
|  | TOOTHILL PRIMARY | HE |  |  |  |  | 34.9537 | 34.8274 | 34.6874 | 34.5379 | 34.3779 | 34.2242 | 34.08 | 33.9453 | 33.8295 | 33.1011 | 31.7516 | 2.26 | 30.4 | 30.2737 | 30.1337 | 29.9842 | 29.8242 | 29.6705 | 29.3684 | 28.8211 | 28.2642 | 26.9021 | 25.3579 | 23.8611 | 31.6347 | 31.5084 | 31.3684 | 31.2189 | 31.0589 | 30.9053 | 30.5653 | 30.0116 | 29.4705 | 28.1242 | 26.5905 | 25.0958
|  | TOOTHILL PRIMARY | CF |  |  |  |  | 35.0579 | 34.9874 | 34.9137 | 34.8379 | 34.76 | 34.68 | 34.6 | 34.5221 | 34.4442 | 34.0968 | 33.9221 | 33.1989 | 31.1242 | 30.4337 | 30.36 | 30.2842 | 30.2063 | 30.1263 | 30.0463 | 29.9684 | 29.8905 | 28.8347 | 27.94 | 26.9895 | 31.9474 | 31.6684 | 31.5947 | 31.5189 | 31.4411 | 31.3611 | 31.2811 | 31.2032 | 31.1253 | 30.0295 | 29.1642 | 28.2305
NURSLING GSP | ROWNHAMS BSP | TOTTON PRIMARY | MINIMUM HEADROOM | SU 35835 13428 | NO | YES | 0 | 23.9905 | 23.7021 | 23.3958 | 23.08 | 22.7537 | 22.4263 | 22.1379 | 21.8758 | 23.7589 | 23.3189 | 28.3547 | -8.2389 | 19.8842 | 19.3337 | 18.7821 | 18.2326 | 17.6842 | 16.9021 | 16.1705 | 15.3568 | 19.5042 | 17.4989 | 20.4705 | 18.3326 | 20.66 | 20.1284 | 19.5947 | 19.0632 | 18.5295 | 17.7811 | 17.0579 | 16.2432 | 20.2905 | 18.3853 | 21.3547 | 19.2158
|  | TOTTON PRIMARY | EE |  |  |  |  | 24.16 | 23.9221 | 23.6695 | 23.4053 | 23.1316 | 22.8684 | 22.6189 | 22.3779 | 35.6379 | 32.5537 | 30.3484 | 28.9242 | 20.2337 | 19.8305 | 19.3905 | 18.9463 | 18.4968 | 17.9232 | 17.34 | 16.5853 | 29.2084 | 25.1463 | 22.6484 | 21.0432 | 20.9726 | 20.6053 | 20.1789 | 19.7474 | 19.3105 | 18.76 | 18.2011 | 17.4716 | 30.0947 | 26.0316 | 23.5326 | 21.9274
|  | TOTTON PRIMARY | HT |  |  |  |  | 23.9905 | 23.7021 | 23.3958 | 23.08 | 22.7537 | 22.4263 | 22.1379 | 21.8758 | 34.8916 | 31.0042 | 28.3547 | 26.4484 | 19.8842 | 19.3337 | 18.7821 | 18.2326 | 17.6842 | 16.9021 | 16.1705 | 15.3568 | 27.9274 | 23.4537 | 20.4705 | 18.3326 | 20.66 | 20.1284 | 19.5947 | 19.0632 | 18.5295 | 17.7811 | 17.0579 | 16.2432 | 28.8137 | 24.3389 | 21.3547 | 19.2158
|  | TOTTON PRIMARY | HE |  |  |  |  | 24.3821 | 24.2126 | 24.0253 | 23.8232 | 23.6084 | 23.4032 | 23.2095 | 23.0284 | 36.3463 | 34.4779 | 32.8232 | -8.2389 | 20.5326 | 20.2905 | 20.0347 | 19.7632 | 19.4821 | 19.1042 | 18.6326 | 17.9926 | 30.7389 | 27.2632 | 25.3484 | 24.2747 | 21.2526 | 21.0274 | 20.7884 | 20.5337 | 20.2589 | 19.8937 | 19.4432 | 18.8368 | 31.6242 | 28.1495 | 26.2337 | 25.16
|  | TOTTON PRIMARY | CF |  |  |  |  | 24.5368 | 24.4474 | 24.3547 | 24.2579 | 24.1589 | 24.0568 | 23.9568 | 23.8579 | 23.7589 | 23.3189 | 35.8853 | 35.2484 | 20.6874 | 20.5979 | 20.4842 | 20.3611 | 20.22 | 20.0768 | 19.9368 | 19.7484 | 19.5042 | 17.4989 | 28.8042 | 28.0621 | 21.4074 | 21.3179 | 21.2095 | 21.0926 | 20.9611 | 20.8284 | 20.6979 | 20.5242 | 20.2905 | 18.3853 | 29.6905 | 28.9484
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK PRIMARY | MINIMUM HEADROOM | SU 45156 14783 | NO | YES | 0.52632 | 34.0611 | 33.4716 | 32.4358 | 31.3926 | 31.7337 | 30.7684 | 29.9747 | 29.1884 | 28.4442 | 31.8747 | 30.4379 | -9.4495 | 27.9 | 26.8453 | 25.7316 | 24.6116 | 24.9905 | 23.9453 | 23.0968 | 22.2547 | 21.4505 | 25.1095 | 25.3242 | 21.0484 | 29.1842 | 28.1516 | 27.0621 | 25.9347 | 26.3232 | 25.26 | 24.3979 | 23.5432 | 22.7274 | 26.4358 | 24.8621 | 20.4842
|  | TOWNHILL PARK PRIMARY | EE |  |  |  |  | 34.3863 | 33.9453 | 33.4779 | 32.6463 | 31.7337 | 30.7684 | 29.9747 | 29.1884 | 28.4442 | 37.9979 | 34.6505 | 31.6884 | 28.5895 | 27.74 | 26.8611 | 25.9705 | 24.9905 | 23.9453 | 23.0968 | 22.2547 | 21.4505 | 33.5442 | 29.8726 | 26.6032 | 29.8568 | 29.0263 | 28.1653 | 27.2926 | 26.3232 | 25.26 | 24.3979 | 23.5432 | 22.7274 | 33.2537 | 29.4958 | 26.1453
|  | TOWNHILL PARK PRIMARY | HT |  |  |  |  | 34.0611 | 33.4716 | 32.4358 | 31.3926 | 42.5084 | 41.8947 | 41.3537 | 40.8621 | 39.8968 | 34.7463 | 30.4379 | 26.5463 | 27.9 | 26.8453 | 25.7316 | 24.6116 | 39.8326 | 38.7137 | 37.7042 | 36.7032 | 35.6442 | 30.0368 | 25.3242 | 21.0484 | 29.1842 | 28.1516 | 27.0621 | 25.9347 | 39.6621 | 38.5274 | 37.5011 | 36.4842 | 35.4063 | 29.6811 | 24.8621 | 20.4842
|  | TOWNHILL PARK PRIMARY | HE |  |  |  |  | 34.7884 | 34.4705 | 34.1189 | 33.7411 | 33.3389 | 32.7411 | 32.1632 | 31.5926 | 31.0621 | 41.7274 | 39.5968 | -9.4495 | 29.4811 | 28.9063 | 28.2884 | 27.6495 | 26.9074 | 26.0884 | 25.4747 | 24.8663 | 24.2947 | 37.7568 | 35.2011 | 32.9263 | 30.6589 | 30.1379 | 29.5579 | 28.9305 | 28.2032 | 27.4032 | 26.8 | 26.2 | 25.6189 | 37.5442 | 34.9263 | 32.5895
|  | TOWNHILL PARK PRIMARY | CF |  |  |  |  | 35.0726 | 34.9021 | 34.7242 | 34.5421 | 34.3526 | 34.16 | 33.9684 | 33.78 | 33.5926 | 31.8747 | 43.0958 | 42.3853 | 30.1621 | 29.8095 | 29.4389 | 29.0621 | 28.6653 | 28.2484 | 27.8453 | 27.4579 | 27.0589 | 25.1095 | 39.6716 | 38.1368 | 31.0021 | 30.8316 | 30.6126 | 30.2758 | 29.9232 | 29.5211 | 29.1274 | 28.7484 | 28.36 | 26.4358 | 39.4768 | 37.9011
MINETY GSP | SWINDON BSP | TRADING ESTATE PRIMARY | MINIMUM HEADROOM | SU 13490 85868 | NO | YES | 0 | 17.3116 | 17.2337 | 16.6358 | 16.5684 | 16.4979 | 16.4305 | 16.1737 | 15.8747 | 15.7705 | 15.1853 | 14.5368 | -21.0053 | 15.28 | 15.1189 | 13.9011 | 13.8337 | 13.7632 | 13.6958 | 13.4021 | 13.0095 | 12.8895 | 12.2432 | 11.5158 | 10.8337 | 15.7 | 15.6305 | 14.3968 | 14.3295 | 14.2589 | 14.1916 | 13.8979 | 13.5063 | 13.3863 | 12.74 | 12.0147 | 11.3337
|  | TRADING ESTATE PRIMARY | EE |  |  |  |  | 17.3547 | 17.2874 | 16.6358 | 16.5684 | 16.4979 | 16.4305 | 16.3642 | 16.3011 | 16.1579 | 15.6905 | 15.2074 | 14.76 | 15.3832 | 15.2537 | 13.9011 | 13.8337 | 13.7632 | 13.6958 | 13.6295 | 13.5663 | 13.3895 | 12.8189 | 12.2695 | 11.7621 | 15.7358 | 15.6758 | 14.3968 | 14.3295 | 14.2589 | 14.1916 | 14.1253 | 14.0621 | 13.8863 | 13.3168 | 12.7674 | 12.2611
|  | TRADING ESTATE PRIMARY | HT |  |  |  |  | 17.3116 | 17.2337 | 17.1516 | 17.0516 | 16.84 | 16.5137 | 16.1737 | 15.8747 | 15.7705 | 15.1853 | 14.5368 | 13.9326 | 15.28 | 15.1189 | 14.9568 | 14.6558 | 14.2663 | 13.8484 | 13.4021 | 13.0095 | 12.8895 | 12.2432 | 11.5158 | 10.8337 | 15.7 | 15.6305 | 15.4884 | 15.1568 | 14.7253 | 14.3442 | 13.8979 | 13.5063 | 13.3863 | 12.74 | 12.0147 | 11.3337
|  | TRADING ESTATE PRIMARY | HE |  |  |  |  | 17.4063 | 17.3589 | 17.3042 | 17.2453 | 17.1684 | 17.0968 | 17.0232 | 16.82 | 16.6063 | 16.3242 | 16.0768 | -21.0053 | 15.4905 | 15.4326 | 15.3421 | 15.2474 | 15.0116 | 14.7937 | 14.5263 | 14.24 | 13.9579 | 13.6221 | 13.3105 | 12.8432 | 15.7821 | 15.7358 | 15.6842 | 15.6295 | 15.5484 | 15.3084 | 15.0126 | 14.7 | 14.4537 | 14.1179 | 13.8074 | 13.34
|  | TRADING ESTATE PRIMARY | CF |  |  |  |  | 17.4389 | 17.4116 | 17.3821 | 17.3505 | 17.3168 | 17.28 | 17.2432 | 17.2021 | 17.1611 | 16.9484 | 16.7526 | 16.5937 | 15.5232 | 15.4958 | 15.4642 | 15.4168 | 15.36 | 15.2779 | 15.1758 | 15.0484 | 14.9116 | 14.3789 | 14.1642 | 13.9568 | 15.8147 | 15.7874 | 15.7579 | 15.7284 | 15.6968 | 15.6653 | 15.6347 | 15.5853 | 15.4347 | 14.8484 | 14.6284 | 14.4463
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | TRASH GREEN PRIMARY | MINIMUM HEADROOM | SU 66254 68745 | NO | YES | 0 | 18.3032 | 18.0663 | 17.7726 | 17.4758 | 16.9011 | 16.0695 | 15.06 | 14.9011 | 14.1 | 12.2653 | 10.3716 | -24.1516 | 15.0442 | 14.7274 | 14.4126 | 14.0968 | 13.4547 | 12.5137 | 11.36 | 11.2053 | 10.2926 | 8.2663 | 6.1526 | 5.4305 | 15.2874 | 14.9716 | 14.6568 | 14.34 | 13.6979 | 12.7547 | 11.6 | 11.4411 | 10.5263 | 8.4811 | 6.3421 | 5.6105
|  | TRASH GREEN PRIMARY | EE |  |  |  |  | 18.5589 | 18.3284 | 18.0863 | 17.8495 | 17.6063 | 17.3674 | 17.1326 | 16.9074 | 16.7011 | 15.56 | 13.5611 | 10.6126 | 15.26 | 15.0126 | 14.7547 | 14.5 | 14.2453 | 13.9979 | 13.7516 | 13.5179 | 13.3032 | 12.0874 | 9.8484 | 6.4326 | 15.5032 | 15.2558 | 14.9968 | 14.7442 | 14.4863 | 14.2347 | 13.9853 | 13.7463 | 13.5284 | 12.2811 | 10.0074 | 6.5874
|  | TRASH GREEN PRIMARY | HT |  |  |  |  | 18.36 | 18.0663 | 17.7726 | 17.4758 | 16.9011 | 16.0695 | 15.06 | 14.9011 | 14.1 | 12.2653 | 10.3716 | 9.6968 | 15.0442 | 14.7274 | 14.4126 | 14.0968 | 13.4547 | 12.5137 | 11.36 | 11.2053 | 10.2926 | 8.2663 | 6.1526 | 5.4305 | 15.2874 | 14.9716 | 14.6568 | 14.34 | 13.6979 | 12.7547 | 11.6 | 11.4411 | 10.5263 | 8.4811 | 6.3421 | 5.6105
|  | TRASH GREEN PRIMARY | HE |  |  |  |  | 18.3032 | 18.6716 | 18.5137 | 18.3516 | 18.1768 | 18.0126 | 17.8505 | 17.6979 | 17.5642 | 16.8495 | 15.2737 | -24.1516 | 15.4232 | 15.3853 | 15.2179 | 15.0453 | 14.8653 | 14.6937 | 14.5242 | 14.3653 | 14.2274 | 13.4568 | 11.6484 | 8.5453 | 15.7863 | 15.6284 | 15.4611 | 15.2884 | 15.1063 | 14.9326 | 14.7621 | 14.6011 | 14.4611 | 13.6789 | 11.8632 | 8.7547
|  | TRASH GREEN PRIMARY | CF |  |  |  |  | 18.3937 | 18.96 | 18.8684 | 18.7811 | 18.6874 | 18.5937 | 18.5011 | 18.4095 | 18.3179 | 17.8884 | 17.2389 | 16.3568 | 15.6568 | 15.7 | 15.6021 | 15.5074 | 15.4074 | 15.3084 | 15.2095 | 15.1126 | 15.0147 | 14.5579 | 13.8232 | 12.8063 | 16.0305 | 15.9432 | 15.8453 | 15.7505 | 15.6495 | 15.5495 | 15.4505 | 15.3526 | 15.2537 | 14.7937 | 14.0537 | 13.0316
MELKSHAM GSP | NORRINGTON BSP | TROWBRIDGE TOWN PRIMARY | MINIMUM HEADROOM | ST 84668 58036 | NO | YES | 0.10526 | 30.3695 | 30.2916 | 30.0347 | 29.7653 | 29.4842 | 29.2147 | 28.9558 | 28.5295 | 28.0495 | 25.4989 | 22.8779 | -5.3716 | 25.9042 | 25.48 | 24.7874 | 24.1379 | 23.3326 | 22.5305 | 21.7811 | 21.0611 | 20.54 | 17.72 | 14.7716 | 11.7716 | 26.8779 | 26.3411 | 25.6495 | 25.0011 | 24.1958 | 23.3937 | 22.6463 | 21.9263 | 21.4053 | 18.5874 | 15.6442 | 12.6484
|  | TROWBRIDGE TOWN PRIMARY | EE |  |  |  |  | 30.5326 | 30.2916 | 30.0347 | 29.7653 | 29.4842 | 29.2147 | 28.9558 | 28.7063 | 28.4842 | 26.9853 | 25.1105 | 23.0495 | 26.3611 | 25.7337 | 25.1516 | 24.5611 | 23.9021 | 23.2821 | 22.6547 | 21.9453 | 21.4042 | 19.3558 | 17.24 | 14.8916 | 27.1526 | 26.7116 | 26.1421 | 25.5663 | 24.9242 | 24.3189 | 23.7074 | 23.0179 | 22.4832 | 20.3937 | 18.1042 | 15.7579
|  | TROWBRIDGE TOWN PRIMARY | HT |  |  |  |  | 30.3695 | 32.5642 | 31.9305 | 31.3305 | 30.5958 | 29.8632 | 29.1821 | 28.5295 | 28.0495 | 25.4989 | 22.8779 | 20.2358 | 25.9042 | 25.48 | 24.7874 | 24.1379 | 23.3326 | 22.5305 | 21.7811 | 21.0611 | 20.54 | 17.72 | 14.7716 | 11.7716 | 26.8779 | 26.3411 | 25.6495 | 25.0011 | 24.1958 | 23.3937 | 22.6463 | 21.9263 | 21.4053 | 18.5874 | 15.6442 | 12.6484
|  | TROWBRIDGE TOWN PRIMARY | HE |  |  |  |  | 30.7442 | 30.5663 | 30.3705 | 32.7958 | 32.2947 | 31.8358 | 31.3547 | 30.8147 | 30.46 | 29.1305 | 27.5179 | -5.3716 | 26.8379 | 26.3853 | 25.9032 | 25.7379 | 25.1874 | 24.6863 | 24.1558 | 23.5547 | 23.1663 | 21.6989 | 19.86 | 18.2432 | 27.3653 | 27.1874 | 26.8789 | 26.5989 | 26.0495 | 25.5484 | 25.0189 | 24.4179 | 24.0305 | 22.5653 | 20.7295 | 19.1147
|  | TROWBRIDGE TOWN PRIMARY | CF |  |  |  |  | 30.8958 | 30.7968 | 30.6937 | 30.5884 | 30.4789 | 30.3674 | 30.2568 | 30.1484 | 30.04 | 29.5547 | 29.3126 | 29.0463 | 27.0737 | 26.9695 | 26.7695 | 26.5589 | 26.3421 | 26.1126 | 25.8611 | 25.5611 | 25.1947 | 23.5821 | 22.6074 | 21.5042 | 27.5168 | 27.4179 | 27.3147 | 27.2095 | 27.1 | 26.9884 | 26.8337 | 26.5411 | 26.1874 | 24.6232 | 23.6811 | 22.5684
BRAMLEY (BASI) GSP | READING BSP | TWYFORD PRIMARY | MINIMUM HEADROOM | SU 78430 76339 | NO | YES | 0 | 18.1958 | 17.9116 | 17.3084 | 16.7368 | 16.0895 | 15.4884 | 14.9368 | 14.4326 | 13.9737 | 11.9 | 10.1263 | -9.9789 | 14.5074 | 13.7737 | 13.0453 | 12.3989 | 11.6611 | 10.98 | 10.3526 | 9.78 | 9.26 | 6.8726 | 4.8021 | 2.8663 | 15.2632 | 14.5063 | 13.7779 | 13.1316 | 12.3926 | 11.7126 | 11.0842 | 10.5105 | 9.9895 | 7.5979 | 5.5242 | 3.5853
|  | TWYFORD PRIMARY | EE |  |  |  |  | 18.3716 | 18.1411 | 17.8958 | 17.78 | 17.1863 | 16.6695 | 16.1958 | 15.7926 | 15.4263 | 14.2505 | 12.9179 | 11.7042 | 14.9737 | 14.4032 | 13.7684 | 13.1484 | 12.4884 | 11.9179 | 11.3979 | 10.9611 | 10.5611 | 8.8432 | 7.3737 | 6.0126 | 15.7137 | 15.1558 | 14.5011 | 13.8811 | 13.2211 | 12.6495 | 12.1284 | 11.6916 | 11.2905 | 9.5663 | 8.0926 | 6.7284
|  | TWYFORD PRIMARY | HT |  |  |  |  | 18.1958 | 17.9116 | 17.3084 | 16.7368 | 16.0895 | 15.4884 | 14.9368 | 14.4326 | 13.9737 | 11.9 | 10.1263 | 8.4937 | 14.5074 | 13.7737 | 13.0453 | 12.3989 | 11.6611 | 10.98 | 10.3526 | 9.78 | 9.26 | 6.8726 | 4.8021 | 2.8663 | 15.2632 | 14.5063 | 13.7779 | 13.1316 | 12.3926 | 11.7126 | 11.0842 | 10.5105 | 9.9895 | 7.5979 | 5.5242 | 3.5853
|  | TWYFORD PRIMARY | HE |  |  |  |  | 18.5979 | 18.4389 | 18.2611 | 18.0705 | 17.7579 | 17.3684 | 17.0221 | 16.7442 | 16.4937 | 15.48 | 14.6842 | -9.9789 | 15.4074 | 15.0063 | 14.5326 | 14.0779 | 13.5495 | 13.1053 | 12.7116 | 12.4053 | 12.1253 | 10.9705 | 10.0347 | 9.1589 | 15.9568 | 15.7684 | 15.2863 | 14.8105 | 14.2811 | 13.8368 | 13.4442 | 13.1368 | 12.8568 | 11.6989 | 10.7611 | 9.8832
|  | TWYFORD PRIMARY | CF |  |  |  |  | 18.7495 | 18.6663 | 18.5789 | 18.4895 | 18.3958 | 18.3011 | 18.2084 | 18.1137 | 18.0221 | 16.8968 | 16.4158 | 16.0526 | 15.6674 | 15.5642 | 15.4368 | 15.2547 | 15.0137 | 14.7516 | 14.4863 | 14.1958 | 13.8968 | 12.5179 | 11.9621 | 11.5274 | 16.1284 | 16.0389 | 15.9432 | 15.8453 | 15.74 | 15.5105 | 15.2389 | 14.9274 | 14.6284 | 13.2495 | 12.6926 | 12.2568
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | UNION STREET PRIMARY | MINIMUM HEADROOM | SP 52865 05849 | NO | YES | 0 | 32.6842 | 32.4568 | 32.2147 | 31.9642 | 31.7032 | 31.2358 | 30.8442 | 30.5 | 30.1853 | 28.3884 | 27.0768 | 4.0989 | 28.4989 | 28.0916 | 27.6684 | 27.2474 | 26.8263 | 25.3347 | 24.8768 | 24.4768 | 24.1116 | 22.1221 | 20.6853 | 19.3442 | 29.3411 | 29.1168 | 28.8411 | 28.4189 | 27.9989 | 26.5063 | 26.0484 | 25.6484 | 25.2832 | 23.3 | 21.8642 | 20.5221
|  | UNION STREET PRIMARY | EE |  |  |  |  | 32.8168 | 32.6242 | 32.42 | 32.2053 | 31.9842 | 31.7232 | 31.4958 | 31.2063 | 30.9421 | 29.5253 | 28.5632 | 27.6821 | 28.8484 | 28.4674 | 28.1 | 27.7347 | 27.3821 | 26.38 | 25.7737 | 25.3263 | 25.0263 | 23.3663 | 22.3189 | 21.3421 | 29.4589 | 29.28 | 29.0789 | 28.8674 | 28.5547 | 27.5526 | 26.9453 | 26.4979 | 26.1979 | 24.5421 | 23.4979 | 22.52
|  | UNION STREET PRIMARY | HT |  |  |  |  | 32.6842 | 32.4568 | 32.2147 | 31.9642 | 31.7032 | 31.2358 | 30.8442 | 30.5 | 30.1853 | 28.3884 | 27.0768 | 25.8632 | 28.4989 | 28.0916 | 27.6684 | 27.2474 | 26.8263 | 25.3347 | 24.8768 | 24.4768 | 24.1116 | 22.1221 | 20.6853 | 19.3442 | 29.3411 | 29.1168 | 28.8411 | 28.4189 | 27.9989 | 26.5063 | 26.0484 | 25.6484 | 25.2832 | 23.3 | 21.8642 | 20.5221
|  | UNION STREET PRIMARY | HE |  |  |  |  | 32.9684 | 32.8168 | 32.6537 | 32.4789 | 32.2947 | 32.0705 | 31.8842 | 31.7221 | 31.5874 | 30.8495 | 30.3358 | 4.0989 | 29.08 | 28.9063 | 28.6421 | 28.3779 | 28.1126 | 27.1842 | 26.6632 | 26.3421 | 26.1284 | 24.9011 | 24.2916 | 23.8021 | 29.5958 | 29.4547 | 29.2989 | 29.1316 | 28.9526 | 28.3558 | 27.8347 | 27.5147 | 27.3 | 26.0684 | 25.4558 | 24.9653
|  | UNION STREET PRIMARY | CF |  |  |  |  | 33.0832 | 32.9958 | 32.9032 | 32.8084 | 32.7105 | 32.6095 | 32.5084 | 32.4032 | 32.2968 | 31.8095 | 31.5779 | 31.4253 | 29.1937 | 29.1063 | 29.0147 | 28.92 | 28.8232 | 28.7221 | 28.5253 | 28.2589 | 27.9832 | 26.5095 | 25.9884 | 25.5747 | 29.6968 | 29.6126 | 29.5253 | 29.4347 | 29.3411 | 29.2453 | 29.1516 | 29.0589 | 28.9568 | 27.6821 | 27.16 | 26.7463
COWLEY GSP | OXFORD (OSNEY) BSP | UNIVERSITY PARKS PRIMARY | MINIMUM HEADROOM | SP 51472 07052 | NO | YES | 0 | 50.3768 | 50.3432 | 50.3074 | 50.2695 | 50.2305 | 50.1905 | 50.1547 | 50.1232 | 50.0926 | 50.0063 | 49.9084 | 20.5684 | 44.4211 | 44.3853 | 44.3484 | 44.3084 | 44.2663 | 44.2221 | 44.1347 | 44.0442 | 43.9432 | 43.5663 | 43.1074 | 42.6695 | 45.6737 | 45.64 | 45.6042 | 45.5663 | 45.5274 | 45.4874 | 45.4516 | 45.4158 | 45.3811 | 45.2947 | 44.8484 | 44.4242
|  | UNIVERSITY PARKS PRIMARY | EE |  |  |  |  | 50.3958 | 50.3674 | 50.3368 | 50.3053 | 50.2716 | 50.2389 | 50.2074 | 50.1768 | 50.1484 | 50.0863 | 50.0126 | 49.9579 | 44.4495 | 44.4137 | 44.3789 | 44.3442 | 44.3074 | 44.2726 | 44.24 | 44.2042 | 44.1621 | 43.9389 | 43.5916 | 43.2663 | 45.6926 | 45.6642 | 45.6337 | 45.6021 | 45.5684 | 45.5358 | 45.5042 | 45.4737 | 45.4453 | 45.3926 | 45.3189 | 45.0032
|  | UNIVERSITY PARKS PRIMARY | HT |  |  |  |  | 50.3768 | 50.3432 | 50.3074 | 50.2695 | 50.2305 | 50.1905 | 50.1547 | 50.1232 | 50.0926 | 50.0063 | 49.9084 | 49.8274 | 44.4211 | 44.3853 | 44.3484 | 44.3084 | 44.2663 | 44.2221 | 44.1347 | 44.0442 | 43.9432 | 43.5663 | 43.1074 | 42.6695 | 45.6737 | 45.64 | 45.6042 | 45.5663 | 45.5274 | 45.4874 | 45.4516 | 45.4158 | 45.3811 | 45.2947 | 44.8484 | 44.4242
|  | UNIVERSITY PARKS PRIMARY | HE |  |  |  |  | 50.4168 | 50.3947 | 50.3695 | 50.3432 | 50.3137 | 50.2874 | 50.2611 | 50.2368 | 50.2168 | 50.1011 | 50.0568 | 20.5684 | 44.4716 | 44.4432 | 44.4137 | 44.3853 | 44.3537 | 44.3253 | 44.2979 | 44.2737 | 44.2526 | 44.0484 | 43.9684 | 43.8295 | 45.7137 | 45.6916 | 45.6663 | 45.64 | 45.6105 | 45.5842 | 45.5579 | 45.5337 | 45.5137 | 45.3663 | 45.32 | 45.2832
|  | UNIVERSITY PARKS PRIMARY | CF |  |  |  |  | 50.4316 | 50.4179 | 50.4032 | 50.3884 | 50.3726 | 50.3568 | 50.3421 | 50.3263 | 50.3116 | 50.2432 | 50.2084 | 50.1895 | 44.4905 | 44.4768 | 44.4611 | 44.4453 | 44.4295 | 44.4126 | 44.3968 | 44.3779 | 44.36 | 44.2779 | 44.2379 | 44.1853 | 45.7284 | 45.7147 | 45.7 | 45.6853 | 45.6695 | 45.6537 | 45.6389 | 45.6232 | 45.6084 | 45.54 | 45.5053 | 45.4863
EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD PRIMARY | MINIMUM HEADROOM | SP 51750 25667 | NO | YES | 0.77895 | 7.9505 | 7.8863 | 7.7695 | 7.1326 | 6.52 | 5.6632 | 4.8147 | 3.9726 | 3.1379 | 2.0095 | 5.0484 | -11.0516 | 6.5284 | 6.2495 | 5.7053 | 4.96 | 4.2505 | 3.2505 | 2.2621 | 1.2789 | 0.30316 | -0.99158 | 2.4937 | 2.1568 | 6.7768 | 6.5074 | 5.9811 | 5.2295 | 4.52 | 3.52 | 2.5305 | 1.5474 | 0.57158 | -0.72316 | 2.7621 | 2.4253
|  | UPPER HEYFORD PRIMARY | EE |  |  |  |  | 7.9895 | 7.9379 | 7.8832 | 7.2779 | 6.6853 | 5.8505 | 5.0189 | 4.1926 | 3.3716 | 2.3284 | 35.6232 | 35.0442 | 6.6095 | 6.3568 | 5.8347 | 5.1168 | 4.4284 | 3.4547 | 2.4832 | 1.5158 | 0.55579 | -0.64632 | 32.5989 | 31.9295 | 6.8568 | 6.6126 | 6.1105 | 5.3874 | 4.6989 | 3.7232 | 2.7516 | 1.7853 | 0.82421 | -0.37789 | 32.8663 | 32.1979
|  | UPPER HEYFORD PRIMARY | HT |  |  |  |  | 7.9505 | 7.8863 | 7.7695 | 7.1326 | 6.52 | 5.6632 | 4.8147 | 3.9726 | 3.1379 | 2.0095 | 35.1958 | 34.4895 | 6.5284 | 6.2495 | 5.7053 | 4.96 | 4.2505 | 3.2505 | 2.2621 | 1.2789 | 0.30316 | -0.99158 | 32.1337 | 31.3211 | 6.7768 | 6.5074 | 5.9811 | 5.2295 | 4.52 | 3.52 | 2.5305 | 1.5474 | 0.57158 | -0.72316 | 32.4011 | 31.5895
|  | UPPER HEYFORD PRIMARY | HE |  |  |  |  | 8.04 | 8.0053 | 7.9663 | 7.4674 | 6.9021 | 6.0926 | 5.2863 | 4.4842 | 3.6884 | 2.7579 | 36.1558 | -11.0516 | 6.7179 | 6.4989 | 6.0105 | 5.3242 | 4.6653 | 3.7179 | 2.7737 | 1.8337 | 0.9 | -0.17789 | 33.18 | 32.6179 | 6.9621 | 6.7505 | 6.2821 | 5.5937 | 4.9347 | 3.9874 | 3.0432 | 2.1021 | 1.1684 | 0.090526 | 33.4484 | 32.8853
|  | UPPER HEYFORD PRIMARY | CF |  |  |  |  | 8.0747 | 8.0579 | 8.0389 | 8.02 | 8 | 7.98 | 7.6253 | 7.0432 | 6.4168 | 5.2242 | 5.0484 | 4.7589 | 7.0158 | 6.9989 | 6.9095 | 6.7653 | 6.5537 | 6.1189 | 5.5042 | 4.8211 | 4.0842 | 2.6926 | 2.4937 | 2.1568 | 7.1242 | 7.1074 | 7.0842 | 7.0063 | 6.8032 | 6.3863 | 5.7737 | 5.0905 | 4.3537 | 2.9621 | 2.7621 | 2.4253
IVER 132KV GSP | UPTON BSP | UPTON PRIMARY | MINIMUM HEADROOM | TQ 00800 79434 | NO | NO | 0 | 26.0453 | 25.8842 | 25.5432 | 25.1874 | 24.6368 | 23.8011 | 23.1042 | 22.4337 | 21.7968 | 18.7979 | 16.2274 | -13.9158 | 20.5295 | 20.1874 | 19.1695 | 18.5189 | 17.2579 | 16.3379 | 15.5747 | 14.8358 | 14.1337 | 10.7968 | 7.9189 | 5.2674 | 21.68 | 21.5611 | 20.7105 | 20.0821 | 18.8547 | 17.9347 | 17.1726 | 16.4347 | 15.7337 | 12.4011 | 9.5263 | 6.8789
|  | UPTON PRIMARY | EE |  |  |  |  | 26.3989 | 26.1337 | 25.8537 | 25.5568 | 25.2495 | 24.7495 | 24.1716 | 23.5968 | 23.0611 | 20.6484 | 18.6632 | 16.8821 | 21.1621 | 20.7326 | 19.5474 | 19.2505 | 18.1632 | 17.3674 | 16.7358 | 16.1074 | 15.5189 | 12.8337 | 10.6011 | 8.5821 | 22.2716 | 21.9905 | 21.0832 | 20.7863 | 19.7579 | 18.9632 | 18.3326 | 17.7053 | 17.1168 | 14.4347 | 12.2063 | 10.1905
|  | UPTON PRIMARY | HT |  |  |  |  | 26.2063 | 25.8842 | 25.5432 | 25.1874 | 24.6368 | 23.8011 | 23.1042 | 22.4337 | 21.7968 | 18.7979 | 16.2274 | 13.8768 | 20.82 | 20.1874 | 19.1695 | 18.5189 | 17.2579 | 16.3379 | 15.5747 | 14.8358 | 14.1337 | 10.7968 | 7.9189 | 5.2674 | 22.0642 | 21.6779 | 20.7105 | 20.0821 | 18.8547 | 17.9347 | 17.1726 | 16.4347 | 15.7337 | 12.4011 | 9.5263 | 6.8789
|  | UPTON PRIMARY | HE |  |  |  |  | 26.6179 | 26.4189 | 26.1979 | 25.96 | 25.7095 | 25.4663 | 25.2368 | 24.9884 | 24.5821 | 22.8095 | 21.4389 | -13.9158 | 21.4758 | 21.2316 | 19.8916 | 19.6537 | 19.2789 | 18.6189 | 18.1232 | 17.6358 | 17.1895 | 15.2074 | 13.6558 | 12.2989 | 22.5105 | 22.3021 | 21.4274 | 21.1895 | 20.8242 | 20.1958 | 19.7189 | 19.2326 | 18.7863 | 16.8063 | 15.2568 | 13.9032
|  | UPTON PRIMARY | CF |  |  |  |  | 26.0453 | 25.9326 | 25.8147 | 25.6926 | 25.5674 | 25.4389 | 25.3105 | 25.1863 | 25.0611 | 24.4611 | 24.3484 | 23.5337 | 20.5295 | 20.3863 | 20.2232 | 20.0537 | 19.7063 | 19.2263 | 18.9179 | 18.6389 | 18.3663 | 16.8653 | 16.8916 | 15.9579 | 21.68 | 21.5611 | 21.4337 | 21.3021 | 21.1579 | 20.8758 | 20.5905 | 20.3232 | 20.06 | 18.6263 | 18.4895 | 17.5568
IVER 66KV GSP |  | UXBRIDGE PRIMARY | MINIMUM HEADROOM | TQ 04984 83484 | NO | NO | 0 | 67.5253 | 91.1705 | 90.7947 | 90.4042 | 90.0011 | 89.5968 | 89.24 | 88.9147 | 88.6147 | 85.8484 | 82.6358 | 24.7116 | 58.5726 | 81.96 | 81.1547 | 80.1463 | 79.0526 | 78.0147 | 77.0389 | 76.0905 | 75.1947 | 71.0621 | 67.4516 | 64.0958 | 60.1716 | 83.7905 | 83.3853 | 82.84 | 81.7463 | 80.7084 | 79.7326 | 78.7832 | 77.8874 | 73.7547 | 70.1432 | 66.7863
|  | UXBRIDGE PRIMARY | EE |  |  |  |  | 67.7442 | 91.4558 | 91.1505 | 90.8305 | 90.4979 | 90.1768 | 89.8716 | 89.5758 | 89.3137 | 88.3495 | 86.3916 | 84.2421 | 58.8505 | 82.4895 | 81.9705 | 81.3053 | 80.3495 | 79.5821 | 78.8316 | 78.0947 | 77.4484 | 74.3221 | 71.6484 | 69.2084 | 60.4063 | 84.1 | 83.7737 | 83.4284 | 83.0432 | 82.2758 | 81.5253 | 80.7874 | 80.1411 | 77.0147 | 74.34 | 71.9
|  | UXBRIDGE PRIMARY | HT |  |  |  |  | 67.5253 | 91.1705 | 90.7947 | 90.4042 | 90.0011 | 89.5968 | 89.24 | 88.9147 | 88.6147 | 85.8484 | 82.6358 | 79.6684 | 58.5726 | 81.96 | 81.1547 | 80.1463 | 79.0526 | 78.0147 | 77.0389 | 76.0905 | 75.1947 | 71.0621 | 67.4516 | 64.0958 | 60.1716 | 83.7905 | 83.3853 | 82.84 | 81.7463 | 80.7084 | 79.7326 | 78.7832 | 77.8874 | 73.7547 | 70.1432 | 66.7863
|  | UXBRIDGE PRIMARY | HE |  |  |  |  | 68 | 91.7905 | 91.5589 | 91.3095 | 91.0421 | 90.7884 | 90.5484 | 90.3253 | 90.1326 | 89.4768 | 89.0895 | 24.7116 | 59.1495 | 82.9126 | 82.6358 | 82.1558 | 81.4316 | 80.7979 | 80.1768 | 79.5737 | 79.2947 | 76.9179 | 74.9463 | 73.1811 | 60.6821 | 84.46 | 84.2116 | 83.9347 | 83.6337 | 83.3579 | 82.8705 | 82.2674 | 81.9884 | 79.6116 | 77.6389 | 75.8737
|  | UXBRIDGE PRIMARY | CF |  |  |  |  | 68.18 | 92.0642 | 91.9442 | 91.82 | 91.6916 | 91.5611 | 91.4326 | 91.3042 | 91.1779 | 90.6084 | 90.3242 | 90.1684 | 59.3316 | 83.2147 | 83.0747 | 82.9274 | 82.7653 | 82.5695 | 82.3074 | 82.0084 | 81.6958 | 79.9789 | 78.6411 | 77.4863 | 60.8653 | 84.7463 | 84.6179 | 84.4832 | 84.3432 | 84.2011 | 84.06 | 83.9179 | 83.7779 | 82.6726 | 81.3337 | 80.1789
NURSLING GSP | VELMORE BSP | VELMORE PRIMARY | MINIMUM HEADROOM | SU 42935 19205 | NO | YES | 0 | 36.6716 | 36.3568 | 36.0242 | 35.68 | 35.3221 | 34.1853 | 32.9063 | 31.6242 | 30.3558 | 25.9937 | 23.2326 | -13.7116 | 30.7495 | 30.0463 | 29.4368 | 28.5958 | 27.5179 | 26.0695 | 24.54 | 23.0011 | 21.4737 | 16.2779 | 13.1884 | 10.3295 | 32.52 | 31.8347 | 31.2158 | 30.3589 | 29.2568 | 27.78 | 26.2495 | 24.7074 | 23.1768 | 17.9642 | 14.8579 | 11.9905
|  | VELMORE PRIMARY | EE |  |  |  |  | 36.8642 | 36.6084 | 36.3368 | 36.0547 | 35.7558 | 35.4663 | 34.5653 | 33.3053 | 32.0158 | 27.7832 | 25.6453 | 23.6916 | 31.1579 | 30.5747 | 30.0863 | 29.4621 | 28.6726 | 27.6453 | 26.4905 | 24.9737 | 23.4116 | 18.3242 | 15.8684 | 13.6484 | 32.8832 | 32.3695 | 31.8758 | 31.2411 | 30.4347 | 29.3821 | 28.1989 | 26.6789 | 25.1126 | 20.0021 | 17.5221 | 15.2937
|  | VELMORE PRIMARY | HT |  |  |  |  | 36.6716 | 36.3568 | 36.0242 | 35.68 | 35.3221 | 34.1853 | 32.9063 | 31.6242 | 30.3558 | 25.9937 | 23.2326 | 20.7074 | 30.7495 | 30.0463 | 29.4368 | 28.5958 | 27.5179 | 26.0695 | 24.54 | 23.0011 | 21.4737 | 16.2779 | 13.1884 | 10.3295 | 32.52 | 31.8347 | 31.2158 | 30.3589 | 29.2568 | 27.78 | 26.2495 | 24.7074 | 23.1768 | 17.9642 | 14.8579 | 11.9905
|  | VELMORE PRIMARY | HE |  |  |  |  | 37.1105 | 36.9326 | 36.7337 | 36.5221 | 36.2905 | 36.0716 | 35.7747 | 34.6274 | 33.4853 | 29.9095 | 28.3926 | -13.7116 | 31.6863 | 31.2705 | 30.9358 | 30.4579 | 29.7968 | 28.8979 | 27.82 | 26.4453 | 25.0484 | 20.6968 | 18.8789 | 17.2147 | 33.3516 | 32.9863 | 32.6811 | 32.2537 | 31.5779 | 30.6579 | 29.5505 | 28.1537 | 26.7558 | 22.3947 | 20.5695 | 18.8979
|  | VELMORE PRIMARY | CF |  |  |  |  | 37.2789 | 37.1853 | 37.0884 | 36.9884 | 36.8832 | 36.7747 | 36.6695 | 36.5653 | 36.46 | 33.8653 | 32.8042 | 31.9284 | 32.1484 | 31.9147 | 31.7179 | 31.5147 | 31.2947 | 31.0432 | 30.7421 | 30.3968 | 29.98 | 25.3968 | 24.1253 | 23.0611 | 33.5737 | 33.48 | 33.3726 | 33.1905 | 32.9937 | 32.7726 | 32.5126 | 32.1884 | 31.7611 | 27.1053 | 25.8284 | 24.76
FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR PRIMARY | MINIMUM HEADROOM | SZ 56148 77857 | NO | YES | 0 | 26.6676 | 26.2434 | 25.8129 | 25.3624 | 24.8792 | 24.3739 | 23.8918 | 23.4308 | 22.9771 | 20.7792 | 18.8003 | 6.2518 | 23.395 | 22.9455 | 22.4897 | 22.0139 | 21.5013 | 20.9634 | 20.4476 | 19.9529 | 19.4645 | 17.075 | 14.9055 | 12.9476 | 23.9234 | 23.4824 | 23.0361 | 22.5697 | 22.0676 | 21.5413 | 21.0182 | 20.5139 | 20.0161 | 17.5771 | 15.3592 | 13.3539
|  | VENTNOR PRIMARY | EE |  |  |  |  | 26.955 | 26.6171 | 26.2571 | 25.8866 | 25.5097 | 25.1213 | 24.7392 | 24.3918 | 24.0455 | 22.3824 | 20.8361 | 19.4739 | 23.7024 | 23.3455 | 22.9645 | 22.5718 | 22.1739 | 21.7634 | 21.355 | 20.9876 | 20.6182 | 18.8139 | 17.1129 | 15.6066 | 24.2234 | 23.8739 | 23.5003 | 23.115 | 22.7255 | 22.3224 | 21.9234 | 21.5634 | 21.1929 | 19.3518 | 17.6108 | 16.0666
|  | VENTNOR PRIMARY | HT |  |  |  |  | 26.6676 | 26.2434 | 25.8129 | 25.3624 | 24.8792 | 24.3739 | 23.8918 | 23.4308 | 22.9771 | 20.7792 | 18.8003 | 17.0224 | 23.395 | 22.9455 | 22.4897 | 22.0139 | 21.5013 | 20.9634 | 20.4476 | 19.9529 | 19.4645 | 17.075 | 14.9055 | 12.9476 | 23.9234 | 23.4824 | 23.0361 | 22.5697 | 22.0676 | 21.5413 | 21.0182 | 20.5139 | 20.0161 | 17.5771 | 15.3592 | 13.3539
|  | VENTNOR PRIMARY | HE |  |  |  |  | 27.1487 | 27.0087 | 26.8539 | 26.6024 | 26.3182 | 26.0318 | 25.7466 | 25.4971 | 25.235 | 24.0234 | 22.8961 | 6.2518 | 24.1055 | 23.8729 | 23.615 | 23.3392 | 23.0403 | 22.7382 | 22.4361 | 22.1718 | 21.8908 | 20.5718 | 19.3234 | 18.2487 | 24.5761 | 24.3876 | 24.135 | 23.8645 | 23.5708 | 23.2739 | 22.9782 | 22.7192 | 22.4455 | 21.1403 | 19.8603 | 18.7561
|  | VENTNOR PRIMARY | CF |  |  |  |  | 27.2782 | 27.2045 | 27.1276 | 27.0487 | 26.9118 | 26.7213 | 26.5403 | 26.3687 | 26.1992 | 25.5424 | 24.8013 | 24.1697 | 24.3308 | 24.1897 | 24.0266 | 23.8476 | 23.6529 | 23.4476 | 23.2529 | 23.0687 | 22.8866 | 22.1897 | 21.3708 | 20.6655 | 24.7118 | 24.6339 | 24.5403 | 24.3666 | 24.1761 | 23.9761 | 23.7866 | 23.6076 | 23.4287 | 22.7466 | 21.9445 | 21.2203
MANNINGTON GSP | MANNINGTON BSP | VERWOOD PRIMARY | MINIMUM HEADROOM | SU 07716 10226 | NO | YES | 0 | 11.3905 | 10.7695 | 10.2516 | 9.7284 | 9.1989 | 8.6716 | 8.1916 | 7.7421 | 7.3189 | 3.6905 | 1.1453 | -10.4326 | 8.8095 | 8.1116 | 7.5453 | 6.9758 | 6.4042 | 5.8389 | 5.3221 | 4.8379 | 4.3811 | 0.15158 | -2.6537 | -3.6032 | 9.3042 | 8.6232 | 8.0674 | 7.5074 | 6.9442 | 6.3832 | 5.8589 | 5.3642 | 4.8958 | 0.59158 | -2.2547 | -3.2211
|  | VERWOOD PRIMARY | EE |  |  |  |  | 11.7389 | 11.2232 | 10.8116 | 10.3884 | 9.9537 | 9.5295 | 9.1211 | 8.7263 | 8.3579 | 6.8105 | 4.74 | 3.2284 | 9.1979 | 8.6168 | 8.1663 | 7.7074 | 7.2411 | 6.7874 | 6.3526 | 5.9316 | 5.5411 | 3.8937 | 1.5484 | -0.22632 | 9.6832 | 9.1158 | 8.6747 | 8.2232 | 7.7621 | 7.3105 | 6.8779 | 6.4579 | 6.0663 | 4.3579 | 1.9147 | 0.11789
|  | VERWOOD PRIMARY | HT |  |  |  |  | 11.3905 | 10.7695 | 10.2516 | 9.7284 | 9.1989 | 8.6716 | 8.1916 | 7.7421 | 7.3189 | 3.6905 | 1.1453 | 0.23263 | 8.8095 | 8.1116 | 7.5453 | 6.9758 | 6.4042 | 5.8389 | 5.3221 | 4.8379 | 4.3811 | 0.15158 | -2.6537 | -3.6032 | 9.3042 | 8.6232 | 8.0674 | 7.5074 | 6.9442 | 6.3832 | 5.8589 | 5.3642 | 4.8958 | 0.59158 | -2.2547 | -3.2211
|  | VERWOOD PRIMARY | HE |  |  |  |  | 12.1958 | 11.8232 | 11.5484 | 11.2558 | 10.9442 | 10.6453 | 10.3653 | 10.0979 | 9.8579 | 8.9463 | 7.5063 | -10.4326 | 9.7074 | 9.2842 | 8.9874 | 8.6726 | 8.3421 | 8.0253 | 7.7274 | 7.4453 | 7.1895 | 6.22 | 4.5305 | 3.2589 | 10.1811 | 9.7695 | 9.4779 | 9.1674 | 8.8389 | 8.5253 | 8.2284 | 7.9474 | 7.6937 | 6.7221 | 5.0126 | 3.6968
|  | VERWOOD PRIMARY | CF |  |  |  |  | 12.5716 | 12.4 | 12.2495 | 12.0916 | 11.9263 | 11.76 | 11.5958 | 11.4316 | 11.2695 | 10.5305 | 9.5779 | 8.9137 | 10.1705 | 9.9432 | 9.7758 | 9.6021 | 9.4221 | 9.2411 | 9.0611 | 8.8821 | 8.7063 | 7.9 | 6.7832 | 6.0011 | 10.6316 | 10.4095 | 10.2463 | 10.0768 | 9.8989 | 9.72 | 9.5432 | 9.3653 | 9.1916 | 8.3968 | 7.3095 | 6.5137
NORTH HYDE GSP |  | VICARAGE FARM ROAD PRIMARY | MINIMUM HEADROOM | TQ 12358 76435 | NO | NO | 0 | 45.8598 | 83.4453 | 82.8421 | 81.3705 | 79.2074 | 77.6568 | 76.1947 | 74.7832 | 73.4147 | 68.3505 | 63.4653 | 14.9684 | 37.1524 | 73.4316 | 71.3284 | 69.0263 | 66.5242 | 64.7632 | 63.0968 | 61.4811 | 59.9126 | 54.1895 | 48.64 | 43.1358 | 39.0419 | 75.4211 | 73.3947 | 71.0958 | 68.5979 | 66.8379 | 65.1737 | 63.5611 | 61.9947 | 56.2884 | 50.7474 | 45.2516
|  | VICARAGE FARM ROAD PRIMARY | EE |  |  |  |  | 46.1261 | 83.8411 | 83.4042 | 82.8884 | 82.2021 | 80.5663 | 79.1611 | 77.6547 | 76.2695 | 71.7421 | 68.3484 | 64.8495 | 38.0472 | 74.9726 | 73.6221 | 71.9642 | 70.0179 | 68.1316 | 66.5211 | 64.7853 | 63.1874 | 58 | 54.1421 | 50.1284 | 39.8914 | 76.8737 | 75.5937 | 74.0274 | 72.0853 | 70.2021 | 68.5937 | 66.8611 | 65.2653 | 60.0853 | 56.2421 | 52.2347
|  | VICARAGE FARM ROAD PRIMARY | HT |  |  |  |  | 45.8598 | 83.4453 | 82.8421 | 81.3705 | 79.2074 | 77.6568 | 76.1947 | 74.7832 | 73.4147 | 68.3505 | 63.4653 | 58.6305 | 37.1524 | 73.4316 | 71.3284 | 69.0263 | 66.5242 | 64.7632 | 63.0968 | 61.4811 | 59.9126 | 54.1895 | 48.64 | 43.1358 | 39.0419 | 75.4211 | 73.3947 | 71.0958 | 68.5979 | 66.8379 | 65.1737 | 63.5611 | 61.9947 | 56.2884 | 50.7474 | 45.2516
|  | VICARAGE FARM ROAD PRIMARY | HE |  |  |  |  | 46.4293 | 84.2316 | 83.9074 | 83.4937 | 83.0221 | 82.0884 | 80.8316 | 79.5337 | 78.3737 | 74.8347 | 72.2316 | 14.9684 | 38.7808 | 75.9105 | 74.7484 | 73.2884 | 71.4968 | 69.8232 | 68.3758 | 66.8737 | 65.5284 | 61.4463 | 58.42 | 55.4042 | 40.4051 | 77.7716 | 76.6705 | 75.2937 | 73.5632 | 71.8916 | 70.4463 | 68.9463 | 67.6032 | 63.5274 | 60.5053 | 57.4947
|  | VICARAGE FARM ROAD PRIMARY | CF |  |  |  |  | 46.6608 | 84.5884 | 84.4137 | 84.2326 | 84.0453 | 83.8537 | 83.6663 | 83.4789 | 83.2453 | 79.3211 | 77.6074 | 75.9589 | 39.5745 | 77.3516 | 76.9179 | 76.44 | 75.9221 | 75.3789 | 74.8642 | 74.1053 | 73.2379 | 66.5558 | 64.5737 | 62.6305 | 40.6724 | 78.5884 | 78.3979 | 78.2 | 77.7695 | 77.2526 | 76.7611 | 76.0432 | 75.2263 | 68.6305 | 66.6516 | 64.7116
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | WALLINGFORD PRIMARY | MINIMUM HEADROOM | SU 59847 89486 | NO | YES | 0.069474 | 22.8329 | 22.5635 | 21.6098 | 20.5435 | 19.3751 | 18.3182 | 17.1824 | 16.0772 | 15.3866 | 13.5656 | 11.9161 | -36.1807 | 19.3172 | 18.3582 | 17.2719 | 16.0635 | 14.7361 | 13.5666 | 12.2529 | 10.9708 | 10.1982 | 8.2172 | 6.5214 | 4.6445 | 19.9382 | 18.9677 | 17.8677 | 16.6424 | 15.2972 | 14.1508 | 12.8372 | 11.5551 | 10.7814 | 8.8003 | 6.9793 | 5.0803
|  | WALLINGFORD PRIMARY | EE |  |  |  |  | 22.9919 | 22.7698 | 22.114 | 21.1382 | 20.0561 | 18.974 | 17.9098 | 16.8572 | 16.2372 | 18.4035 | 17.2919 | 16.0719 | 19.6614 | 18.8066 | 17.8224 | 16.7108 | 15.4761 | 14.2298 | 12.9951 | 11.7729 | 11.0645 | 15.1214 | 13.9477 | 12.5761 | 20.2866 | 19.4203 | 18.4224 | 17.2972 | 16.0445 | 14.7898 | 13.5551 | 12.3319 | 11.6245 | 16.4098 | 15.2603 | 13.8877
|  | WALLINGFORD PRIMARY | HT |  |  |  |  | 22.8329 | 22.5635 | 21.6098 | 20.5435 | 19.3751 | 18.3182 | 17.1824 | 16.0772 | 15.3866 | 13.5656 | 11.9161 | 10.2193 | 19.3172 | 18.3582 | 17.2719 | 16.0635 | 14.7361 | 13.5666 | 12.2529 | 10.9708 | 10.1982 | 8.2172 | 6.5214 | 4.6445 | 19.9382 | 18.9677 | 17.8677 | 16.6424 | 15.2972 | 14.1508 | 12.8372 | 11.5551 | 10.7814 | 8.8003 | 6.9793 | 5.0803
|  | WALLINGFORD PRIMARY | HE |  |  |  |  | 23.2024 | 23.0466 | 22.7908 | 21.9287 | 20.9572 | 19.9814 | 19.0214 | 18.0782 | 17.5614 | 23.5856 | 22.6845 | -36.1807 | 20.1214 | 19.4098 | 18.5614 | 17.5751 | 16.4603 | 15.3393 | 14.2193 | 13.1161 | 12.5235 | 11.754 | 10.5972 | 9.7245 | 20.7508 | 20.0298 | 19.1687 | 18.1687 | 17.0372 | 15.9003 | 14.7803 | 13.6761 | 13.0835 | 17.914 | 16.8845 | 16.4687
|  | WALLINGFORD PRIMARY | CF |  |  |  |  | 23.3456 | 23.2624 | 23.1761 | 23.0877 | 22.9951 | 22.5919 | 22.0898 | 21.5572 | 21.2245 | 20.4266 | 19.8624 | 19.374 | 20.5908 | 20.2224 | 19.8119 | 19.3593 | 18.8635 | 18.3214 | 17.7435 | 17.1287 | 16.7519 | 15.8814 | 15.2508 | 14.6898 | 21.2256 | 20.8519 | 20.4361 | 19.9772 | 19.474 | 18.9235 | 18.3372 | 17.714 | 17.3319 | 16.454 | 15.8151 | 15.2498
COWLEY GSP | DRAYTON BSP | WANTAGE PRIMARY | MINIMUM HEADROOM | SU 41290 88304 | NO | YES | 0.10526 | 26.9811 | 26.5284 | 25.6947 | 24.9158 | 24.0768 | 23.2379 | 22.4347 | 21.6642 | 20.9126 | 17.7474 | 16.2811 | 0.44316 | 22.4979 | 21.4621 | 20.56 | 19.7179 | 18.8116 | 17.9042 | 17.0337 | 16.1958 | 15.3789 | 12.2937 | 10.6705 | 8.7116 | 24.1758 | 23.1611 | 22.2305 | 21.36 | 20.42 | 19.4789 | 18.5768 | 17.7074 | 16.8579 | 13.2758 | 11.6537 | 9.6979
|  | WANTAGE PRIMARY | EE |  |  |  |  | 27.1211 | 26.8863 | 26.1368 | 25.4368 | 24.6726 | 23.9179 | 23.1768 | 22.4516 | 21.7537 | 18.9053 | 17.9379 | 16.6768 | 22.7905 | 21.8421 | 21.0274 | 20.9547 | 20.0947 | 19.2432 | 18.4053 | 17.5863 | 16.7937 | 13.5484 | 12.4842 | 11.0526 | 24.4653 | 23.5347 | 22.7105 | 21.9242 | 21.0653 | 20.2147 | 19.3779 | 18.56 | 17.7695 | 14.5295 | 13.4653 | 12.0368
|  | WANTAGE PRIMARY | HT |  |  |  |  | 26.9811 | 26.5284 | 25.6947 | 24.9158 | 24.0768 | 23.2379 | 22.4347 | 21.6642 | 20.9126 | 17.7474 | 16.2811 | 14.5484 | 22.4979 | 21.4621 | 20.56 | 19.7179 | 18.8116 | 17.9042 | 17.0337 | 16.1958 | 15.3789 | 12.2937 | 10.6705 | 8.7116 | 24.1758 | 23.1611 | 22.2305 | 21.36 | 20.42 | 19.4789 | 18.5768 | 17.7074 | 16.8579 | 13.2758 | 11.6537 | 9.6979
|  | WANTAGE PRIMARY | HE |  |  |  |  | 27.3011 | 27.1684 | 26.7232 | 26.1253 | 25.4579 | 24.7947 | 24.1442 | 23.5116 | 22.9021 | 20.4832 | 19.9105 | 0.44316 | 23.1768 | 22.3484 | 21.6474 | 20.9979 | 20.2716 | 20.1968 | 19.4579 | 18.7379 | 18.0432 | 15.2684 | 14.6368 | 13.6189 | 24.8453 | 24.0347 | 23.3474 | 22.6737 | 21.9189 | 21.1684 | 20.4305 | 19.7126 | 19.0179 | 16.2474 | 15.6168 | 14.6
|  | WANTAGE PRIMARY | CF |  |  |  |  | 27.4242 | 27.3547 | 27.2821 | 27.2074 | 27.1295 | 26.9242 | 26.5779 | 26.2168 | 25.8368 | 24.1442 | 23.7284 | 23.1768 | 23.6137 | 23.2 | 22.8621 | 22.5558 | 22.2253 | 21.8684 | 21.4916 | 21.0968 | 20.6811 | 18.8295 | 18.3853 | 17.78 | 25.0558 | 24.8695 | 24.5389 | 24.2389 | 23.9147 | 23.5653 | 23.1863 | 22.7747 | 22.3421 | 20.4147 | 19.9558 | 19.3242
MANNINGTON GSP | WAREHAM BSP | WAREHAM TOWN PRIMARY | MINIMUM HEADROOM | SY 92036 87463 | NO | YES | 0 | 13.79 | 42.6832 | 42.3158 | 41.5484 | 41.0526 | 40.7042 | 40.0958 | 37.2611 | 36.9895 | 33.1611 | 30.9179 | 20.6642 | 10.9258 | 39.3358 | 38.98 | 38.1189 | 37.58 | 37.2147 | 36.5421 | 33.2653 | 33.0926 | 28.8684 | 26.2326 | 25.4905 | 11.5195 | 39.92 | 39.5326 | 38.6989 | 38.1726 | 37.8095 | 37.1547 | 33.8263 | 33.6484 | 29.2853 | 26.7611 | 26.0021
|  | WAREHAM TOWN PRIMARY | EE |  |  |  |  | 13.8995 | 42.9684 | 42.6653 | 41.9611 | 41.5232 | 41.2358 | 40.9579 | 40.6853 | 40.4326 | 36.9474 | 33.6347 | 32.2842 | 11.15 | 39.6284 | 39.3189 | 38.5653 | 38.0895 | 37.7916 | 37.5032 | 37.2232 | 36.9611 | 33.0495 | 29.4947 | 28.0179 | 11.7511 | 40.2221 | 39.9021 | 39.1358 | 38.6695 | 38.3705 | 38.0821 | 37.7979 | 37.5358 | 33.5674 | 29.8705 | 28.3411
|  | WAREHAM TOWN PRIMARY | HT |  |  |  |  | 13.79 | 42.6832 | 42.3158 | 41.5484 | 41.0526 | 40.7042 | 40.0958 | 37.2611 | 36.9895 | 33.1611 | 30.9179 | 30.2074 | 10.9258 | 39.3358 | 38.98 | 38.1189 | 37.58 | 37.2147 | 36.5421 | 33.2653 | 33.0926 | 28.8684 | 26.2326 | 25.4905 | 11.5195 | 39.92 | 39.5326 | 38.6989 | 38.1726 | 37.8095 | 37.1547 | 33.8263 | 33.6484 | 29.2853 | 26.7611 | 26.0021
|  | WAREHAM TOWN PRIMARY | HE |  |  |  |  | 14.0479 | 43.3568 | 43.1432 | 42.5211 | 42.1663 | 41.9632 | 41.7726 | 41.5916 | 41.4274 | 38.2737 | 35.7305 | 20.6642 | 11.4532 | 40.0253 | 39.8063 | 39.1695 | 38.7832 | 38.5726 | 38.3747 | 38.1874 | 38.0179 | 34.42 | 31.5063 | 30.3284 | 12.0647 | 40.6316 | 40.4074 | 39.7284 | 39.3495 | 39.1389 | 38.9421 | 38.7547 | 38.5853 | 35.1095 | 31.9842 | 30.7632
|  | WAREHAM TOWN PRIMARY | CF |  |  |  |  | 14.1511 | 42.8442 | 42.7853 | 44.6884 | 44.6189 | 44.5505 | 44.4811 | 44.4126 | 44.3474 | 44.0421 | 43.8684 | 43.7558 | 11.6447 | 40.2905 | 40.1705 | 39.8768 | 39.7011 | 39.5842 | 39.4684 | 39.3537 | 39.24 | 38.7274 | 38.2558 | 37.78 | 12.2321 | 40.8958 | 40.7811 | 41.3242 | 41.2126 | 41.1242 | 41.0358 | 40.9484 | 40.8653 | 40.4758 | 40.1821 | 39.9232
FLEET-BRAMLEY GSP | BRACKNELL BSP | WARFIELD PRIMARY | MINIMUM HEADROOM | SU 86960 71382 | NO | YES | 1.0516 | 35.5421 | 35.1673 | 34.7726 | 34.3652 | 32.7778 | 31.4905 | 29.8842 | 28.281 | 27.4505 | 24.6505 | 30.2484 | -12.2937 | 28.8157 | 27.5484 | 26.1147 | 24.6726 | 22.8736 | 21.4378 | 19.6199 | 17.7999 | 16.8821 | 13.8347 | 10.6515 | 7.6863 | 30.4252 | 29.1789 | 27.7273 | 26.2673 | 24.4663 | 23.0294 | 21.2094 | 19.3863 | 18.4663 | 15.4021 | 12.0189 | 9.0063
|  | WARFIELD PRIMARY | EE |  |  |  |  | 35.7694 | 35.4652 | 35.1421 | 34.8042 | 33.7442 | 32.5915 | 31.0852 | 29.5589 | 28.8094 | 32.6599 | 30.2484 | 28.1705 | 29.2978 | 28.1768 | 26.8852 | 25.5799 | 23.9199 | 22.6284 | 20.9178 | 19.1852 | 18.3568 | 25.4021 | 22.7231 | 20.3789 | 30.8936 | 29.8136 | 28.5042 | 27.1821 | 25.5126 | 24.2189 | 22.5063 | 20.7694 | 19.9368 | 28.1757 | 25.4736 | 23.1221
|  | WARFIELD PRIMARY | HT |  |  |  |  | 35.5421 | 35.1673 | 34.7726 | 34.3652 | 32.7778 | 31.4905 | 29.8842 | 28.281 | 27.4505 | 24.6505 | 33.2989 | 19.0221 | 28.8157 | 27.5484 | 26.1147 | 24.6726 | 22.8736 | 21.4378 | 19.6199 | 17.7999 | 16.8821 | 13.8347 | 10.6515 | 7.6863 | 30.4252 | 29.1789 | 27.7273 | 26.2673 | 24.4663 | 23.0294 | 21.2094 | 19.3863 | 18.4663 | 15.4021 | 12.0189 | 9.0063
|  | WARFIELD PRIMARY | HE |  |  |  |  | 36.0652 | 35.8536 | 35.6199 | 35.3684 | 34.8831 | 33.8852 | 32.5284 | 31.1631 | 30.5694 | 36.9747 | 36.4463 | -12.2937 | 30.0526 | 29.1357 | 27.9821 | 26.6273 | 25.1442 | 24.0178 | 22.4694 | 20.9094 | 20.2484 | 18.7842 | 16.8778 | 15.2147 | 31.6126 | 30.7452 | 29.6126 | 28.2389 | 26.7378 | 25.6105 | 24.061 | 22.4978 | 21.8357 | 27.0126 | 26.0852 | 25.3389
|  | WARFIELD PRIMARY | CF |  |  |  |  | 36.2631 | 36.1536 | 36.0389 | 35.9199 | 35.7957 | 35.6684 | 35.5421 | 35.4189 | 35.2957 | 34.3347 | 33.1831 | 32.2336 | 30.7157 | 30.2431 | 29.6894 | 29.0684 | 28.4105 | 27.8557 | 27.0578 | 26.1999 | 25.7747 | 24.5652 | 23.2684 | 22.1842 | 31.8378 | 31.7073 | 31.2778 | 30.6852 | 30.0442 | 29.4821 | 28.6705 | 27.801 | 27.3684 | 26.1557 | 24.8536 | 23.7663
MELKSHAM GSP | FROME BSP | WARMINSTER PRIMARY | MINIMUM HEADROOM | ST 84936 44551 | NO | YES | 0 | 17.6442 | 17.4968 | 17.0158 | 16.2137 | 15.2232 | 14.2358 | 13.3295 | 12.6716 | 12.0032 | 10.72 | 9.5789 | -2.7653 | 14.68 | 14.1284 | 13.5568 | 12.5832 | 11.4789 | 10.3789 | 9.3695 | 8.6411 | 7.9011 | 6.5326 | 5.3 | 4.1326 | 15.7116 | 15.0189 | 14.3926 | 13.3937 | 12.2579 | 11.1253 | 10.0874 | 9.3368 | 8.5737 | 7.1611 | 5.8979 | 4.72
|  | WARMINSTER PRIMARY | EE |  |  |  |  | 17.7168 | 17.6074 | 17.2368 | 16.6 | 15.7347 | 14.8642 | 13.8737 | 13.0768 | 12.4453 | 11.3821 | 10.44 | 9.6126 | 14.8221 | 14.3137 | 13.8168 | 13.0032 | 12.04 | 11.0695 | 9.9632 | 9.0768 | 8.38 | 7.2621 | 6.2737 | 5.3632 | 15.7895 | 15.2337 | 14.6568 | 13.8232 | 12.8295 | 11.8295 | 10.6905 | 9.7779 | 9.0568 | 7.8937 | 6.8547 | 5.9221
|  | WARMINSTER PRIMARY | HT |  |  |  |  | 17.6442 | 17.4968 | 17.0158 | 16.2137 | 15.2232 | 14.2358 | 13.3295 | 12.6716 | 12.0032 | 10.72 | 9.5789 | 8.5316 | 14.68 | 14.1284 | 13.5568 | 12.5832 | 11.4789 | 10.3789 | 9.3695 | 8.6411 | 7.9011 | 6.5326 | 5.3 | 4.1326 | 15.7116 | 15.0189 | 14.3926 | 13.3937 | 12.2579 | 11.1253 | 10.0874 | 9.3368 | 8.5737 | 7.1611 | 5.8979 | 4.72
|  | WARMINSTER PRIMARY | HE |  |  |  |  | 17.8168 | 17.7389 | 17.5389 | 16.9674 | 16.1663 | 15.3505 | 14.4011 | 13.7021 | 13.14 | 12.4063 | 11.8095 | -2.7653 | 15.0147 | 14.5674 | 14.1642 | 13.4168 | 12.5 | 11.5863 | 10.52 | 9.7389 | 9.1116 | 8.3295 | 7.6821 | 7.0326 | 15.8968 | 15.5284 | 15.0189 | 14.2442 | 13.2989 | 12.3589 | 11.2611 | 10.4558 | 9.8095 | 9 | 8.3305 | 7.6558
|  | WARMINSTER PRIMARY | CF |  |  |  |  | 17.8874 | 17.8453 | 17.8021 | 17.7568 | 17.7063 | 17.4926 | 17.2063 | 16.8526 | 16.4095 | 15.5032 | 15.1337 | 14.7484 | 15.2432 | 15.0189 | 14.8274 | 14.6158 | 14.3768 | 14.1084 | 13.7326 | 13.2684 | 12.7705 | 11.7737 | 11.3747 | 10.9516 | 15.98 | 15.9232 | 15.8558 | 15.5884 | 15.2842 | 14.9516 | 14.5653 | 14.0874 | 13.5758 | 12.5495 | 12.1368 | 11.6989
LOVEDEAN GSP | FORT WIDLEY BSP | WATERLOOVILLE PRIMARY | MINIMUM HEADROOM | SU 67988 09282 | NO | YES | 0 | 63.7453 | 63.2074 | 62.5168 | 60.8853 | 59.1032 | 57.4821 | 55.9958 | 54.5821 | 53.2337 | 47.5179 | 42.5832 | 10.0895 | 56.4716 | 54.8684 | 53.1695 | 51.3505 | 49.3568 | 47.5537 | 45.8968 | 44.3168 | 42.8084 | 36.3916 | 30.8168 | 25.6453 | 58.1505 | 56.5895 | 54.8905 | 53.0716 | 51.0779 | 49.2737 | 47.6158 | 46.0358 | 44.5253 | 38.1042 | 32.5242 | 27.3505
|  | WATERLOOVILLE PRIMARY | EE |  |  |  |  | 64.0737 | 63.6379 | 63.1747 | 62.1558 | 60.6032 | 59.2 | 57.8926 | 56.6947 | 55.5768 | 51.0337 | 47.1168 | 43.5695 | 57.2589 | 55.8516 | 54.3221 | 52.7347 | 50.9947 | 49.4253 | 47.9653 | 46.6326 | 45.3842 | 40.2853 | 35.8442 | 31.7853 | 58.9042 | 57.5684 | 56.0432 | 54.4558 | 52.7147 | 51.1453 | 49.6842 | 48.3505 | 47.1021 | 41.9979 | 37.5495 | 33.4884
|  | WATERLOOVILLE PRIMARY | HT |  |  |  |  | 63.7453 | 63.2074 | 62.5168 | 60.8853 | 59.1032 | 57.4821 | 55.9958 | 54.5821 | 53.2337 | 47.5179 | 42.5832 | 38.0368 | 56.4716 | 54.8684 | 53.1695 | 51.3505 | 49.3568 | 47.5537 | 45.8968 | 44.3168 | 42.8084 | 36.3916 | 30.8168 | 25.6453 | 58.1505 | 56.5895 | 54.8905 | 53.0716 | 51.0779 | 49.2737 | 47.6158 | 46.0358 | 44.5253 | 38.1042 | 32.5242 | 27.3505
|  | WATERLOOVILLE PRIMARY | HE |  |  |  |  | 64.4884 | 64.18 | 63.84 | 63.4726 | 62.4063 | 61.2158 | 60.1295 | 59.1453 | 58.22 | 54.6789 | 51.7084 | 10.0895 | 58.1716 | 57.0421 | 55.7874 | 54.4547 | 52.96 | 51.6232 | 50.4042 | 49.3042 | 48.2632 | 44.26 | 40.8568 | 37.7579 | 59.7179 | 58.7116 | 57.5095 | 56.1768 | 54.6811 | 53.3432 | 52.1253 | 51.0232 | 49.9821 | 45.9768 | 42.5716 | 39.4705
|  | WATERLOOVILLE PRIMARY | CF |  |  |  |  | 64.7758 | 64.6158 | 64.4484 | 64.2737 | 64.0958 | 63.9116 | 63.7326 | 63.5558 | 63.0316 | 60.4263 | 58.4832 | 56.7811 | 59.0421 | 58.5074 | 57.9011 | 57.2684 | 56.5842 | 55.8832 | 55.1611 | 54.4063 | 53.6463 | 50.7147 | 48.4947 | 46.5274 | 60.0389 | 59.8568 | 59.5274 | 58.9284 | 58.2811 | 57.6053 | 56.8832 | 56.1263 | 55.3663 | 52.4347 | 50.2137 | 48.2442
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON PRIMARY | MINIMUM HEADROOM | SU 69106 94287 | NO | YES | 0 | 9.9274 | 9.7021 | 9.4716 | 9.2379 | 8.8011 | 8.22 | 7.5221 | 7.3958 | 7.2758 | 5.9442 | 4.2305 | -27.3526 | 7.5316 | 7.2884 | 7.0432 | 6.7916 | 6.3074 | 5.6547 | 4.8611 | 4.7379 | 4.6232 | 3.1758 | 1.2663 | 0.73053 | 7.8168 | 7.5747 | 7.3284 | 7.0768 | 6.5916 | 5.9358 | 5.14 | 5.0126 | 4.8937 | 3.4189 | 1.4811 | 0.93263
|  | WATLINGTON PRIMARY | EE |  |  |  |  | 10.0779 | 9.8989 | 9.7126 | 9.5232 | 9.3179 | 9.1105 | 8.9116 | 8.7147 | 8.5326 | 7.7358 | 6.4937 | 5.4579 | 7.6958 | 7.5032 | 7.3042 | 7.1 | 6.8853 | 6.6695 | 6.4611 | 6.2579 | 6.0684 | 5.2516 | 3.9042 | 2.7368 | 7.9811 | 7.7884 | 7.5895 | 7.3863 | 7.1684 | 6.9474 | 6.7347 | 6.5263 | 6.3305 | 5.4758 | 4.0853 | 2.9053
|  | WATLINGTON PRIMARY | HT |  |  |  |  | 9.9274 | 9.7021 | 9.4716 | 9.2379 | 8.8011 | 8.22 | 7.5221 | 7.3958 | 7.2758 | 5.9442 | 4.2305 | 3.7211 | 7.5316 | 7.2884 | 7.0432 | 6.7916 | 6.3074 | 5.6547 | 4.8611 | 4.7379 | 4.6232 | 3.1758 | 1.2663 | 0.73053 | 7.8168 | 7.5747 | 7.3284 | 7.0768 | 6.5916 | 5.9358 | 5.14 | 5.0126 | 4.8937 | 3.4189 | 1.4811 | 0.93263
|  | WATLINGTON PRIMARY | HE |  |  |  |  | 10.2789 | 10.1642 | 10.04 | 9.9063 | 9.7568 | 9.6105 | 9.4684 | 9.3347 | 9.2137 | 8.7326 | 7.82 | -27.3526 | 7.9137 | 7.7905 | 7.6589 | 7.5158 | 7.3611 | 7.2074 | 7.0589 | 6.9189 | 6.7916 | 6.2916 | 5.26 | 4.3168 | 8.2 | 8.0768 | 7.9442 | 7.8021 | 7.6442 | 7.4884 | 7.3379 | 7.1958 | 7.0663 | 6.5516 | 5.5074 | 4.5537
|  | WATLINGTON PRIMARY | CF |  |  |  |  | 10.3937 | 10.3263 | 10.2568 | 10.1853 | 10.1063 | 10.0232 | 9.9421 | 9.86 | 9.7779 | 9.4053 | 9.0168 | 8.4053 | 8.0368 | 7.9632 | 7.8884 | 7.8105 | 7.7274 | 7.6389 | 7.5526 | 7.4642 | 7.3768 | 6.9789 | 6.5474 | 5.8516 | 8.3221 | 8.2484 | 8.1747 | 8.0968 | 8.0116 | 7.9221 | 7.8347 | 7.7463 | 7.6568 | 7.2547 | 6.8168 | 6.1137
AMERSHAM GSP | LOUDWATER BSP | WELL END PRIMARY | MINIMUM HEADROOM | SU 88511 87957 | NO | YES | 1.0516 | 22.9602 | 22.535 | 22.0929 | 21.6539 | 21.2329 | 20.8139 | 20.4308 | 20.0876 | 19.8045 | 18.5939 | 17.6192 | -4.6061 | 21.7287 | 20.835 | 19.9234 | 19.0508 | 18.2697 | 17.496 | 16.7581 | 16.1129 | 15.6381 | 13.4613 | 11.5423 | 9.8202 | 22.8718 | 22.0129 | 21.1381 | 20.2855 | 19.496 | 18.7139 | 17.9676 | 17.315 | 16.836 | 14.6371 | 12.695 | 10.9518
|  | WELL END PRIMARY | EE |  |  |  |  | 23.1245 | 22.8087 | 22.4318 | 22.0581 | 21.6992 | 21.3539 | 21.0202 | 20.715 | 20.4718 | 19.5202 | 18.8045 | 18.2245 | 21.8929 | 21.2823 | 20.475 | 19.7013 | 19.015 | 18.3487 | 17.6939 | 17.1223 | 16.7234 | 15.0045 | 13.5413 | 12.2402 | 23.036 | 22.4487 | 21.6739 | 20.9297 | 20.2476 | 19.5739 | 18.9118 | 18.3329 | 17.9308 | 16.1939 | 14.7129 | 13.396
|  | WELL END PRIMARY | HT |  |  |  |  | 22.9602 | 22.535 | 22.0929 | 21.6539 | 21.2329 | 20.8139 | 20.4308 | 20.0876 | 19.8045 | 18.5939 | 17.6192 | 16.7981 | 21.7287 | 20.835 | 19.9234 | 19.0508 | 18.2697 | 17.496 | 16.7581 | 16.1129 | 15.6381 | 13.4613 | 11.5423 | 9.8202 | 22.8718 | 22.0129 | 21.1381 | 20.2855 | 19.496 | 18.7139 | 17.9676 | 17.315 | 16.836 | 14.6371 | 12.695 | 10.9518
|  | WELL END PRIMARY | HE |  |  |  |  | 23.3318 | 23.1623 | 22.8666 | 22.5697 | 22.2823 | 22.0066 | 21.7392 | 21.5097 | 21.3371 | 20.6939 | 20.2455 | -4.6061 | 22.1002 | 21.8729 | 21.1981 | 20.5539 | 19.9834 | 19.4318 | 18.8876 | 18.4518 | 18.1792 | 17.0129 | 16.0318 | 15.1855 | 23.2434 | 23.0192 | 22.3739 | 21.7571 | 21.2076 | 20.6666 | 20.116 | 19.676 | 19.4002 | 18.2213 | 17.2287 | 16.3708
|  | WELL END PRIMARY | CF |  |  |  |  | 23.4718 | 23.3939 | 23.3129 | 23.2287 | 23.1002 | 22.936 | 22.7866 | 22.6602 | 22.5476 | 22.0318 | 21.7066 | 21.4739 | 22.2402 | 22.1623 | 22.0813 | 21.9971 | 21.7497 | 21.3645 | 21.0329 | 20.7887 | 20.6034 | 19.7066 | 18.9918 | 18.3855 | 23.3834 | 23.3055 | 23.2245 | 23.1402 | 22.9013 | 22.5329 | 22.215 | 21.9802 | 21.8002 | 20.9329 | 20.2234 | 19.6087
WILLESDEN GSP |  | WESLEY AVENUE PRIMARY | MINIMUM HEADROOM | TQ 20927 83082 | NO | NO | 0 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | WESLEY AVENUE PRIMARY | EE |  |  |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | WESLEY AVENUE PRIMARY | HT |  |  |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | WESLEY AVENUE PRIMARY | HE |  |  |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | WESLEY AVENUE PRIMARY | CF |  |  |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
LOVEDEAN GSP | FAREHAM (MAIN) BSP | WEST END PRIMARY | MINIMUM HEADROOM | SU 57216 06147 | NO | YES | 0 | 33.2832 | 32.9947 | 32.6863 | 32.3674 | 32.0379 | 31.7053 | 30.7095 | 29.6674 | 28.7558 | 25.3611 | 23.0179 | 3.6305 | 30.0968 | 29.5526 | 29.0011 | 28.4463 | 27.8958 | 26.4947 | 25.14 | 23.9884 | 22.9811 | 19.1737 | 16.5432 | 14.0916 | 31.0021 | 30.4695 | 29.9274 | 29.3832 | 28.8432 | 27.4768 | 26.1284 | 24.9674 | 23.9358 | 20.1105 | 17.4811 | 15.0316
|  | WEST END PRIMARY | EE |  |  |  |  | 33.4621 | 33.2263 | 32.9758 | 32.7137 | 32.44 | 32.1768 | 31.9242 | 30.9695 | 30.0389 | 26.9642 | 25.1463 | 23.5 | 30.4737 | 30.04 | 29.6 | 29.1547 | 28.7053 | 27.7568 | 26.7063 | 25.4011 | 24.3674 | 20.9295 | 18.8832 | 17.0095 | 31.3705 | 30.9453 | 30.5137 | 30.0758 | 29.6326 | 28.7147 | 27.6884 | 26.3884 | 25.3474 | 21.8621 | 19.8158 | 17.9442
|  | WEST END PRIMARY | HT |  |  |  |  | 33.2832 | 32.9947 | 32.6863 | 32.3674 | 32.0379 | 31.7053 | 30.7095 | 29.6674 | 28.7558 | 25.3611 | 23.0179 | 20.8516 | 30.0968 | 29.5526 | 29.0011 | 28.4463 | 27.8958 | 26.4947 | 25.14 | 23.9884 | 22.9811 | 19.1737 | 16.5432 | 14.0916 | 31.0021 | 30.4695 | 29.9274 | 29.3832 | 28.8432 | 27.4768 | 26.1284 | 24.9674 | 23.9358 | 20.1105 | 17.4811 | 15.0316
|  | WEST END PRIMARY | HE |  |  |  |  | 33.6758 | 33.5053 | 33.3158 | 33.1137 | 32.8958 | 32.6884 | 32.4926 | 32.1726 | 31.4063 | 28.9084 | 27.6158 | 3.6305 | 30.9495 | 30.6632 | 30.3611 | 30.0484 | 29.7221 | 28.88 | 27.8958 | 26.7126 | 25.8326 | 23.0516 | 21.5821 | 20.2558 | 31.8337 | 31.5526 | 31.2558 | 30.9484 | 30.6263 | 29.8116 | 28.8621 | 27.6979 | 26.82 | 23.9863 | 22.5168 | 21.1916
|  | WEST END PRIMARY | CF |  |  |  |  | 33.8221 | 33.7284 | 33.6316 | 33.5316 | 33.4274 | 33.3189 | 33.2147 | 33.1116 | 33.0084 | 31.8811 | 30.9663 | 30.1916 | 31.1253 | 31.0263 | 30.8484 | 30.6674 | 30.4811 | 30.2905 | 30.0547 | 29.74 | 29.3789 | 26.3179 | 25.3063 | 24.4379 | 32.0084 | 31.9105 | 31.7358 | 31.5579 | 31.3758 | 31.1884 | 30.9579 | 30.6526 | 30.3021 | 27.3063 | 26.2905 | 25.3979
MELKSHAM GSP | WEST GRAFTON BSP | WEST GRAFTON VILLAGE PRIMARY | MINIMUM HEADROOM | SU 24639 60279 | NO | YES | 0.15684 | 6.9131 | 6.7321 | 6.5489 | 6.3626 | 6.1552 | 5.9457 | 5.7584 | 5.5784 | 5.3426 | 4.2131 | 3.1268 | -1.0279 | 7.2826 | 7.0868 | 6.8857 | 6.6857 | 6.4657 | 6.2447 | 6.0489 | 5.8594 | 5.6015 | 4.3699 | 3.1847 | 2.1184 | 7.3394 | 7.1394 | 6.9363 | 6.7342 | 6.5068 | 6.2794 | 6.0752 | 5.8773 | 5.6089 | 4.3142 | 3.0594 | 1.9573
|  | WEST GRAFTON VILLAGE PRIMARY | EE |  |  |  |  | 7.0352 | 6.8899 | 6.7405 | 6.5899 | 6.4194 | 6.2468 | 6.0763 | 5.9026 | 5.6973 | 4.7089 | 3.7373 | 2.9721 | 7.4184 | 7.2605 | 7.0984 | 6.9363 | 6.7584 | 6.5805 | 6.4036 | 6.2247 | 6.0057 | 4.9594 | 3.9299 | 3.0605 | 7.4784 | 7.3163 | 7.1531 | 6.9878 | 6.8036 | 6.6163 | 6.4321 | 6.2436 | 6.0121 | 4.8931 | 3.7826 | 2.8721
|  | WEST GRAFTON VILLAGE PRIMARY | HT |  |  |  |  | 6.9131 | 6.7321 | 6.5489 | 6.3626 | 6.1552 | 5.9457 | 5.7584 | 5.5784 | 5.3426 | 4.2131 | 3.1268 | 2.1973 | 7.2826 | 7.0868 | 6.8857 | 6.6857 | 6.4657 | 6.2447 | 6.0489 | 5.8594 | 5.6015 | 4.3699 | 3.1847 | 2.1184 | 7.3394 | 7.1394 | 6.9363 | 6.7342 | 6.5068 | 6.2794 | 6.0752 | 5.8773 | 5.6089 | 4.3142 | 3.0594 | 1.9573
|  | WEST GRAFTON VILLAGE PRIMARY | HE |  |  |  |  | 7.1994 | 7.1057 | 7.0068 | 6.9047 | 6.7826 | 6.6657 | 6.5531 | 6.4468 | 6.3015 | 5.6615 | 5.0836 | -1.0279 | 7.6005 | 7.4984 | 7.3931 | 7.2836 | 7.1563 | 7.0352 | 6.9194 | 6.8099 | 6.651 | 5.951 | 5.3005 | 4.6194 | 7.6626 | 7.5594 | 7.4521 | 7.3415 | 7.2099 | 7.0847 | 6.9647 | 6.8499 | 6.6857 | 5.9489 | 5.2647 | 4.551
|  | WEST GRAFTON VILLAGE PRIMARY | CF |  |  |  |  | 7.2942 | 7.2415 | 7.1878 | 7.1321 | 7.0615 | 6.9868 | 6.9184 | 6.8563 | 6.7899 | 6.4163 | 6.0878 | 5.7152 | 7.7026 | 7.6457 | 7.5868 | 7.5257 | 7.4489 | 7.3689 | 7.2963 | 7.2289 | 7.1563 | 6.7468 | 6.3805 | 5.9542 | 7.7657 | 7.7078 | 7.6489 | 7.5868 | 7.5068 | 7.4247 | 7.3489 | 7.2794 | 7.2047 | 6.7805 | 6.3952 | 5.9468
AXMINSTER GSP | YEOVIL BSP | WEST HENDFORD PRIMARY | MINIMUM HEADROOM | ST 55000 15442 | NO | YES | 0 | 67.5526 | 67.0442 | 66.5253 | 65.8263 | 64.9947 | 64.1705 | 63.3653 | 62.5789 | 61.8105 | 60.3989 | 59.2411 | 31.4253 | 61.2074 | 60.6368 | 60.0589 | 59.2684 | 58.3242 | 57.3895 | 56.4726 | 55.5747 | 54.6968 | 53.2105 | 51.9263 | 50.5537 | 62.6558 | 62.0863 | 61.5074 | 60.7179 | 59.7726 | 58.8368 | 57.92 | 57.0221 | 56.1432 | 54.5842 | 53.2989 | 51.9284
|  | WEST HENDFORD PRIMARY | EE |  |  |  |  | 67.7453 | 67.2926 | 66.8316 | 66.1884 | 65.4084 | 64.6411 | 63.8821 | 63.1263 | 62.3937 | 61.2789 | 60.4084 | 59.4621 | 61.4158 | 60.9074 | 60.3905 | 59.6611 | 58.7726 | 57.8989 | 57.0305 | 56.1695 | 55.3316 | 54.1042 | 53.2105 | 52.1389 | 62.8653 | 62.3568 | 61.84 | 61.1105 | 60.2211 | 59.3463 | 58.4789 | 57.6158 | 56.7768 | 55.5474 | 54.58 | 53.5084
|  | WEST HENDFORD PRIMARY | HT |  |  |  |  | 67.5526 | 67.0442 | 66.5253 | 65.8263 | 64.9947 | 64.1705 | 63.3653 | 62.5789 | 61.8105 | 60.3989 | 59.2411 | 58.0232 | 61.2074 | 60.6368 | 60.0589 | 59.2684 | 58.3242 | 57.3895 | 56.4726 | 55.5747 | 54.6968 | 53.2105 | 51.9263 | 50.5537 | 62.6558 | 62.0863 | 61.5074 | 60.7179 | 59.7726 | 58.8368 | 57.92 | 57.0221 | 56.1432 | 54.5842 | 53.2989 | 51.9284
|  | WEST HENDFORD PRIMARY | HE |  |  |  |  | 67.9937 | 67.6168 | 67.2274 | 66.6537 | 65.9389 | 65.2379 | 64.5389 | 63.8495 | 63.1821 | 62.3863 | 61.8189 | 31.4253 | 61.6863 | 61.2611 | 60.8232 | 60.1695 | 59.3516 | 58.5484 | 57.7484 | 56.9579 | 56.1895 | 55.3095 | 54.6747 | 53.9884 | 63.1358 | 62.7105 | 62.2726 | 61.6179 | 60.8 | 59.9968 | 59.1958 | 58.4053 | 57.6368 | 56.7547 | 56.12 | 55.3611
|  | WEST HENDFORD PRIMARY | CF |  |  |  |  | 68.3421 | 68.1842 | 68.0389 | 67.8295 | 67.5274 | 67.14 | 66.6726 | 66.1842 | 65.6632 | 64.8305 | 64.4295 | 63.9895 | 62.0821 | 61.9053 | 61.7453 | 61.5084 | 61.1653 | 60.72 | 60.1821 | 59.6179 | 59.0168 | 58.0853 | 57.6379 | 57.1347 | 63.5316 | 63.3547 | 63.1947 | 62.9568 | 62.6137 | 62.1684 | 61.6305 | 61.0674 | 60.4653 | 59.5337 | 59.0853 | 58.5811
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR PRIMARY | MINIMUM HEADROOM | ST 77699 22040 | NO | YES | 0.17895 | 8.3689 | 8.1826 | 7.9953 | 7.4889 | 7.1121 | 6.9132 | 6.3384 | 6.2279 | 3.6837 | 2.4921 | 0.94789 | -0.90263 | 6.9226 | 6.7226 | 6.5216 | 5.9458 | 5.5268 | 5.3205 | 4.6668 | 4.5595 | 1.5795 | 0.28579 | -1.4342 | -1.9068 | 7.1205 | 6.9279 | 6.7321 | 6.19 | 5.7889 | 5.5837 | 4.9668 | 4.8542 | 1.8858 | 0.56158 | -1.1921 | -1.6784
|  | WEST STOUR PRIMARY | EE |  |  |  |  | 8.4974 | 8.3489 | 8.1974 | 7.73 | 7.3868 | 7.2226 | 7.0637 | 6.9089 | 6.7616 | 5.47 | 3.9216 | 2.9974 | 7.0626 | 6.9037 | 6.7426 | 6.2089 | 5.8268 | 5.6574 | 5.4932 | 5.3353 | 5.1858 | 3.7784 | 2.0647 | 1.0195 | 7.2553 | 7.1005 | 6.9437 | 6.4416 | 6.0774 | 5.9058 | 5.7405 | 5.5816 | 5.4289 | 4.0342 | 2.2711 | 1.2111
|  | WEST STOUR PRIMARY | HT |  |  |  |  | 8.3689 | 8.1826 | 7.9953 | 7.4889 | 7.1121 | 6.9132 | 6.3384 | 6.2279 | 3.6837 | 2.4921 | 0.94789 | 0.50053 | 6.9226 | 6.7226 | 6.5216 | 5.9458 | 5.5268 | 5.3205 | 4.6668 | 4.5595 | 1.5795 | 0.28579 | -1.4342 | -1.9068 | 7.1205 | 6.9279 | 6.7321 | 6.19 | 5.7889 | 5.5837 | 4.9668 | 4.8542 | 1.8858 | 0.56158 | -1.1921 | -1.6784
|  | WEST STOUR PRIMARY | HE |  |  |  |  | 8.6668 | 8.5732 | 8.4753 | 8.0553 | 7.7595 | 7.6468 | 7.5416 | 7.4395 | 7.3479 | 6.3616 | 5.2605 | -0.90263 | 7.2468 | 7.1468 | 7.0416 | 6.5595 | 6.2279 | 6.1121 | 6.0026 | 5.8984 | 5.8037 | 4.7005 | 3.4437 | 2.5953 | 7.4321 | 7.3353 | 7.2332 | 6.7805 | 6.4658 | 6.35 | 6.2395 | 6.1363 | 6.0416 | 4.9816 | 3.7247 | 2.8637
|  | WEST STOUR PRIMARY | CF |  |  |  |  | 8.8111 | 8.7584 | 8.7047 | 8.5195 | 8.3868 | 8.3247 | 8.2647 | 8.2037 | 8.1437 | 7.8721 | 7.6342 | 7.1258 | 7.4058 | 7.3489 | 7.2911 | 7.0784 | 6.9289 | 6.8647 | 6.8005 | 6.7363 | 6.6732 | 6.3858 | 6.1311 | 5.5532 | 7.5847 | 7.53 | 7.4732 | 7.2742 | 7.1321 | 7.0679 | 7.0047 | 6.9416 | 6.8795 | 6.5963 | 6.3447 | 5.7942
MANNINGTON GSP | BOURNEMOUTH BSP | WESTBOURNE PRIMARY | MINIMUM HEADROOM | SZ 07642 91485 | NO | YES | 0.015789 | 35.5029 | 35.2671 | 35.0176 | 34.7513 | 34.0766 | 33.3282 | 32.5829 | 32.065 | 31.5629 | 29.2197 | 26.9724 | 3.5713 | 30.5703 | 29.7492 | 29.0976 | 28.3945 | 27.6366 | 26.825 | 26.0113 | 25.4555 | 24.9124 | 22.3555 | 19.8503 | 17.4261 | 31.3934 | 30.5987 | 29.9376 | 29.2208 | 28.4471 | 27.6187 | 26.7871 | 26.2208 | 25.6692 | 23.0818 | 20.5755 | 18.1482
|  | WESTBOURNE PRIMARY | EE |  |  |  |  | 35.6629 | 35.4776 | 35.2808 | 35.0682 | 34.6703 | 34.025 | 33.3892 | 33.0155 | 32.6029 | 30.7755 | 29.0387 | 27.4039 | 30.9545 | 30.2934 | 29.6355 | 28.9566 | 28.2608 | 27.5587 | 26.865 | 26.4671 | 26.025 | 24.0492 | 22.1155 | 20.2703 | 31.6387 | 31.1282 | 30.4839 | 29.7903 | 29.0797 | 28.3608 | 27.6524 | 27.2503 | 26.7987 | 24.7818 | 22.8376 | 20.9924
|  | WESTBOURNE PRIMARY | HT |  |  |  |  | 35.5029 | 35.2671 | 35.0176 | 34.7513 | 34.0766 | 33.3282 | 32.5829 | 32.065 | 31.5629 | 29.2197 | 26.9724 | 24.8145 | 30.5703 | 29.7492 | 29.0976 | 28.3945 | 27.6366 | 26.825 | 26.0113 | 25.4555 | 24.9124 | 22.3555 | 19.8503 | 17.4261 | 31.3934 | 30.5987 | 29.9376 | 29.2208 | 28.4471 | 27.6187 | 26.7871 | 26.2208 | 25.6692 | 23.0818 | 20.5755 | 18.1482
|  | WESTBOURNE PRIMARY | HE |  |  |  |  | 35.7692 | 35.6092 | 35.4334 | 35.2429 | 35.0397 | 34.7092 | 34.165 | 33.8745 | 33.5587 | 32.2439 | 31.0355 | 3.5713 | 31.0724 | 30.685 | 30.1155 | 29.5271 | 28.9239 | 28.305 | 27.7113 | 27.4039 | 27.065 | 25.6418 | 24.3124 | 23.0713 | 31.7503 | 31.5082 | 30.9555 | 30.3724 | 29.7576 | 29.125 | 28.5176 | 28.2061 | 27.8608 | 26.4082 | 25.0471 | 23.7976
|  | WESTBOURNE PRIMARY | CF |  |  |  |  | 35.8503 | 35.7429 | 35.6313 | 35.5166 | 35.3976 | 35.2755 | 35.1555 | 35.0376 | 34.9197 | 34.1597 | 33.2703 | 32.5029 | 31.165 | 31.0482 | 30.9271 | 30.7187 | 30.3797 | 29.9987 | 29.5734 | 29.2692 | 28.9829 | 27.7429 | 26.7671 | 25.9155 | 31.8313 | 31.7239 | 31.6113 | 31.485 | 31.2071 | 30.8376 | 30.4239 | 30.1134 | 29.8218 | 28.5587 | 27.5618 | 26.6871
MELKSHAM GSP | FROME BSP | WESTBURY PRIMARY | MINIMUM HEADROOM | ST 87654 51530 | NO | YES | 0 | 33.0568 | 32.52 | 31.4253 | 30.3211 | 29.7789 | 28.6789 | 27.8895 | 27.3326 | 26.8326 | 23.7221 | 20.4821 | -1.5716 | 28.7621 | 27.9737 | 26.7484 | 25.5126 | 25.04 | 23.8211 | 22.9611 | 22.3716 | 21.7389 | 18.3674 | 14.8811 | 11.4789 | 29.1305 | 28.3421 | 27.1179 | 25.8853 | 25.2779 | 24.0537 | 23.1895 | 22.5937 | 21.9537 | 18.5379 | 15.0011 | 11.5811
|  | WESTBURY PRIMARY | EE |  |  |  |  | 33.4684 | 33.1042 | 32.34 | 31.4705 | 30.4621 | 29.4158 | 28.4179 | 27.6968 | 27.2263 | 29.3589 | 26.7821 | 24.4063 | 29.2168 | 28.6158 | 27.7695 | 26.8021 | 25.6779 | 24.5126 | 23.4011 | 22.6158 | 22.1242 | 26.5484 | 23.7537 | 21.0821 | 29.5853 | 28.9832 | 28.1379 | 27.1705 | 26.0432 | 24.8716 | 23.7537 | 22.96 | 22.4579 | 27.26 | 24.3958 | 21.7021
|  | WESTBURY PRIMARY | HT |  |  |  |  | 33.0568 | 32.52 | 31.4253 | 30.3211 | 29.7789 | 28.6789 | 27.8895 | 27.3326 | 26.8326 | 23.7221 | 20.4821 | 17.4674 | 28.7621 | 27.9737 | 26.7484 | 25.5126 | 25.04 | 23.8211 | 22.9611 | 22.3716 | 21.7389 | 18.3674 | 14.8811 | 11.4789 | 29.1305 | 28.3421 | 27.1179 | 25.8853 | 25.2779 | 24.0537 | 23.1895 | 22.5937 | 21.9537 | 18.5379 | 15.0011 | 11.5811
|  | WESTBURY PRIMARY | HE |  |  |  |  | 34.0211 | 33.6474 | 33.2274 | 32.5074 | 31.6337 | 30.74 | 29.8874 | 29.3821 | 29.0842 | 28.1347 | 26.2421 | -1.5716 | 29.8274 | 29.4179 | 28.7358 | 27.9295 | 26.9516 | 25.9453 | 24.9874 | 24.4358 | 24.1253 | 23.2495 | 21.1137 | 19.2779 | 30.1947 | 29.7863 | 29.1042 | 28.2989 | 27.3179 | 26.3105 | 25.3484 | 24.7947 | 24.4789 | 23.4474 | 21.2926 | 19.4389
|  | WESTBURY PRIMARY | CF |  |  |  |  | 34.4 | 34.2095 | 34.0147 | 34.0116 | 33.7768 | 33.5295 | 33.2295 | 32.8084 | 32.3632 | 30.4021 | 30.0368 | 28.8926 | 30.2453 | 30.0368 | 29.8253 | 29.6105 | 29.3568 | 29.0895 | 28.7611 | 28.2874 | 27.7853 | 25.5779 | 25.2989 | 23.9947 | 30.2884 | 30.4042 | 30.1926 | 29.9779 | 29.7232 | 29.4537 | 29.1232 | 28.6495 | 28.1463 | 25.9337 | 25.5126 | 24.1979
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WESTERN ESPLANADE PRIMARY | MINIMUM HEADROOM | SU 41618 12009 | NO | YES | 0.094737 | 69.7058 | 69.5195 | 68.6616 | 67.6374 | 65.4521 | 63.4826 | 61.8195 | 60.17 | 59.2163 | 57.2953 | 55.57 | 14.4311 | 60.7616 | 59.9532 | 58.7089 | 57.5553 | 55.0553 | 52.8079 | 50.9111 | 49.0037 | 47.9089 | 45.8079 | 43.8732 | 42.0521 | 63.1742 | 62.3774 | 61.1532 | 60.0174 | 57.5637 | 55.3553 | 53.4921 | 51.5774 | 50.4837 | 48.3942 | 46.4626 | 44.6437
|  | WESTERN ESPLANADE PRIMARY | EE |  |  |  |  | 69.8268 | 69.6763 | 69.0458 | 68.1068 | 67.0058 | 65.9016 | 63.7942 | 61.9111 | 61.0689 | 58.4879 | 57.1711 | 55.9584 | 60.8826 | 60.2753 | 59.1237 | 58.0616 | 56.8132 | 55.5605 | 53.1447 | 50.9868 | 50.0279 | 47.11 | 45.6395 | 44.2658 | 63.2953 | 62.6963 | 61.5637 | 60.5195 | 59.2921 | 58.0605 | 55.6889 | 53.5658 | 52.6005 | 49.6921 | 48.2268 | 46.8542
|  | WESTERN ESPLANADE PRIMARY | HT |  |  |  |  | 69.7058 | 69.5195 | 68.6616 | 67.6374 | 65.4521 | 63.4826 | 61.8195 | 60.17 | 59.2163 | 57.2953 | 55.57 | 53.9553 | 60.7616 | 59.9532 | 58.7089 | 57.5553 | 55.0553 | 52.8079 | 50.9111 | 49.0037 | 47.9089 | 45.8079 | 43.8732 | 42.0521 | 63.1742 | 62.3774 | 61.1532 | 60.0174 | 57.5637 | 55.3553 | 53.4921 | 51.5774 | 50.4837 | 48.3942 | 46.4626 | 44.6437
|  | WESTERN ESPLANADE PRIMARY | HE |  |  |  |  | 69.9205 | 69.7942 | 69.4216 | 68.5489 | 67.5089 | 66.4679 | 64.8121 | 63.1563 | 62.6574 | 60.0332 | 58.7995 | 14.4311 | 60.9763 | 60.6163 | 59.5374 | 58.5479 | 57.3689 | 56.1858 | 54.2879 | 52.3889 | 51.83 | 48.7963 | 47.3753 | 46.4616 | 63.3889 | 63.0321 | 61.9721 | 60.9995 | 59.8405 | 58.6774 | 56.8132 | 54.95 | 54.3984 | 51.3647 | 49.9437 | 49.0311
|  | WESTERN ESPLANADE PRIMARY | CF |  |  |  |  | 69.9995 | 69.9195 | 69.8363 | 69.7511 | 69.6626 | 69.5721 | 68.8795 | 67.7342 | 66.7447 | 64.9995 | 63.97 | 63.4153 | 61.0553 | 60.9753 | 60.8921 | 60.8068 | 60.7184 | 59.8658 | 58.9353 | 57.6205 | 56.4879 | 54.5268 | 53.3647 | 52.7395 | 63.4679 | 63.3879 | 63.3047 | 63.2195 | 63.1311 | 62.2921 | 61.3795 | 60.0879 | 58.9753 | 57.0458 | 55.9026 | 55.2868
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON PRIMARY | MINIMUM HEADROOM | SU 45207 09912 | NO | YES | 0.084211 | 22.3305 | 22.0168 | 21.4379 | 20.8074 | 20.2126 | 19.5895 | 19.0168 | 18.4547 | 17.86 | 14.6674 | 11.9705 | -4.6526 | 19.0979 | 18.5032 | 17.8358 | 17.1611 | 16.5316 | 15.8684 | 15.2589 | 14.6558 | 14.0137 | 10.4726 | 7.46 | 4.7021 | 19.4495 | 18.8695 | 18.1958 | 17.5158 | 16.88 | 16.2116 | 15.5958 | 14.9874 | 14.3358 | 10.7853 | 7.7695 | 5.0126
|  | WESTON PRIMARY | EE |  |  |  |  | 22.5147 | 22.2558 | 21.98 | 21.5432 | 20.9874 | 20.3916 | 19.9095 | 19.4295 | 18.9737 | 16.5737 | 14.4516 | 12.5779 | 19.5 | 19.0242 | 18.4926 | 17.9568 | 17.3621 | 16.7211 | 16.2095 | 15.6989 | 15.2126 | 12.5811 | 10.2063 | 8.0874 | 19.8389 | 19.3758 | 18.8589 | 18.3189 | 17.7179 | 17.0705 | 16.5537 | 16.0379 | 15.5442 | 12.8863 | 10.5074 | 8.3874
|  | WESTON PRIMARY | HT |  |  |  |  | 22.3305 | 22.0168 | 21.4379 | 20.8074 | 20.2126 | 19.5895 | 19.0168 | 18.4547 | 17.86 | 14.6674 | 11.9705 | 9.5211 | 19.0979 | 18.5032 | 17.8358 | 17.1611 | 16.5316 | 15.8684 | 15.2589 | 14.6558 | 14.0137 | 10.4726 | 7.46 | 4.7021 | 19.4495 | 18.8695 | 18.1958 | 17.5158 | 16.88 | 16.2116 | 15.5958 | 14.9874 | 14.3358 | 10.7853 | 7.7695 | 5.0126
|  | WESTON PRIMARY | HE |  |  |  |  | 22.7347 | 22.5421 | 22.3284 | 22.0989 | 21.8516 | 21.5274 | 21.1737 | 20.8232 | 20.4968 | 18.8958 | 17.4421 | -4.6526 | 20.0116 | 19.6937 | 19.3105 | 18.9189 | 18.4558 | 17.9505 | 17.5768 | 17.2053 | 16.8558 | 15.1084 | 13.4842 | 12.0063 | 20.3347 | 20.0242 | 19.6505 | 19.2684 | 18.8158 | 18.3126 | 17.9368 | 17.56 | 17.2084 | 15.4358 | 13.7947 | 12.3168
|  | WESTON PRIMARY | CF |  |  |  |  | 22.8979 | 22.7905 | 22.6779 | 22.5632 | 22.4432 | 22.32 | 22.2011 | 22.0811 | 21.9621 | 20.9642 | 19.9863 | 19.1126 | 20.2747 | 20.1179 | 19.9147 | 19.7084 | 19.4968 | 19.2653 | 19.0263 | 18.7874 | 18.5432 | 17.3316 | 16.2453 | 15.2621 | 20.6295 | 20.4379 | 20.24 | 20.0389 | 19.8326 | 19.6063 | 19.3737 | 19.1411 | 18.9042 | 17.6842 | 16.5832 | 15.5832
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH PRIMARY | MINIMUM HEADROOM | SY 67443 79096 | NO | YES | 0 | 37.4379 | 36.8926 | 36.3147 | 34.4747 | 32.4958 | 30.9789 | 29.7526 | 28.84 | 28.0295 | 24.3358 | 20.0705 | -22.4684 | 30.2726 | 28.1442 | 25.9179 | 23.5221 | 21.3 | 19.6263 | 18.28 | 17.2968 | 16.4274 | 12.4284 | 7.6789 | 2.6768 | 31.7295 | 29.6516 | 27.4242 | 25.0274 | 22.8042 | 21.1284 | 19.7811 | 18.7968 | 17.9253 | 13.92 | 9.1589 | 4.1505
|  | WEYMOUTH PRIMARY | EE |  |  |  |  | 37.7589 | 37.3116 | 36.8326 | 35.6947 | 33.8916 | 32.5737 | 31.4905 | 30.6989 | 30.0084 | 27.1074 | 23.9421 | 20.5968 | 30.9758 | 29.06 | 27.0421 | 24.8484 | 22.8179 | 21.3558 | 20.1674 | 19.3211 | 18.5832 | 15.4558 | 11.9368 | 8.1411 | 32.0716 | 30.5663 | 28.5484 | 26.3547 | 24.3221 | 22.8579 | 21.6684 | 20.8189 | 20.0811 | 16.9411 | 13.4063 | 9.6053
|  | WEYMOUTH PRIMARY | HT |  |  |  |  | 37.4379 | 36.8926 | 36.3147 | 34.4747 | 32.4958 | 30.9789 | 29.7526 | 28.84 | 28.0295 | 24.3358 | 20.0705 | 15.6463 | 30.2726 | 28.1442 | 25.9179 | 23.5221 | 21.3 | 19.6263 | 18.28 | 17.2968 | 16.4274 | 12.4284 | 7.6789 | 2.6768 | 31.7295 | 29.6516 | 27.4242 | 25.0274 | 22.8042 | 21.1284 | 19.7811 | 18.7968 | 17.9253 | 13.92 | 9.1589 | 4.1505
|  | WEYMOUTH PRIMARY | HE |  |  |  |  | 38.1379 | 37.8021 | 37.4316 | 37.0316 | 35.6316 | 34.5274 | 33.6589 | 33.0905 | 32.6232 | 30.8263 | 28.7337 | -22.4684 | 31.5295 | 30.2253 | 28.4674 | 26.5232 | 24.7263 | 23.4958 | 22.5421 | 21.9379 | 21.4421 | 19.52 | 17.1705 | 14.4874 | 32.4821 | 31.7326 | 29.9747 | 28.0295 | 26.2316 | 25.0011 | 24.0463 | 23.4411 | 22.9442 | 21.0168 | 18.6642 | 15.9768
|  | WEYMOUTH PRIMARY | CF |  |  |  |  | 38.4105 | 38.2211 | 38.0232 | 37.8189 | 37.6074 | 37.3905 | 37.1768 | 36.9663 | 36.7558 | 35.8158 | 34.5211 | 33.0095 | 31.8189 | 31.6 | 30.8042 | 29.8874 | 29.0495 | 28.3937 | 27.8326 | 27.4242 | 27.0442 | 25.2979 | 23.6463 | 21.9158 | 32.7768 | 32.5484 | 32.3042 | 31.3947 | 30.5558 | 29.9 | 29.3389 | 28.9295 | 28.5495 | 26.8011 | 25.1474 | 23.4137
COWLEY GSP | HEADINGTON BSP | WHEATLEY PRIMARY | MINIMUM HEADROOM | SP 60777 05379 | NO | YES | 0.37579 | 15.7325 | 40.5177 | 40.1619 | 38.8156 | 37.2535 | 35.3714 | 33.8209 | 32.4262 | 31.3746 | 29.6377 | 28.2525 | -10.4391 | 14.5335 | 39.3104 | 38.923 | 37.3714 | 35.5841 | 33.4188 | 31.6441 | 30.0504 | 28.8619 | 27.0735 | 25.6998 | 24.4967 | 14.7472 | 39.523 | 39.1356 | 37.5862 | 35.7904 | 33.6177 | 31.8335 | 30.2293 | 29.0262 | 27.143 | 25.6588 | 24.4125
|  | WHEATLEY PRIMARY | EE |  |  |  |  | 16.0788 | 40.943 | 40.4672 | 39.1756 | 37.6672 | 35.8262 | 34.303 | 32.9198 | 31.8883 | 30.2146 | 32.9914 | 32.1209 | 14.8683 | 39.7104 | 39.2567 | 37.7641 | 36.0335 | 33.9177 | 32.1767 | 30.6051 | 29.4441 | 27.7777 | 33.3388 | 32.4314 | 15.9388 | 40.7872 | 39.4683 | 37.9767 | 36.2377 | 34.1104 | 32.3567 | 30.7683 | 29.5883 | 27.7862 | 33.5862 | 32.6304
|  | WHEATLEY PRIMARY | HT |  |  |  |  | 15.7325 | 40.5177 | 40.1619 | 38.8156 | 37.2535 | 35.3714 | 33.8209 | 32.4262 | 31.3746 | 29.6377 | 28.2525 | 27.1219 | 14.5335 | 39.3104 | 38.923 | 37.3714 | 35.5841 | 33.4188 | 31.6441 | 30.0504 | 28.8619 | 27.0735 | 25.6998 | 24.4967 | 14.7472 | 39.523 | 39.1356 | 37.5862 | 35.7904 | 33.6177 | 31.8335 | 30.2293 | 29.0262 | 27.143 | 25.6588 | 24.4125
|  | WHEATLEY PRIMARY | HE |  |  |  |  | 16.2093 | 41.1167 | 41.0135 | 39.6746 | 38.2398 | 36.4956 | 35.0714 | 33.7925 | 32.8651 | 31.7956 | 31.1893 | -10.4391 | 15.0198 | 39.923 | 39.8072 | 38.3019 | 36.6493 | 34.6283 | 32.983 | 31.5093 | 30.4493 | 29.3346 | 28.7219 | 28.1209 | 16.0819 | 40.9872 | 40.8756 | 38.5177 | 36.8588 | 34.8346 | 33.1841 | 31.7051 | 30.6367 | 29.4662 | 28.8114 | 28.1704
|  | WHEATLEY PRIMARY | CF |  |  |  |  | 16.2977 | 41.2504 | 41.0219 | 40.8925 | 40.2956 | 39.4977 | 38.7841 | 38.0893 | 37.543 | 36.823 | 36.4051 | 36.0167 | 15.1083 | 40.0609 | 39.8356 | 39.6914 | 39.0051 | 38.0819 | 37.2588 | 36.4567 | 35.8283 | 35.0514 | 34.6209 | 34.2198 | 16.1704 | 41.123 | 40.0493 | 39.9051 | 39.2156 | 38.2914 | 37.4651 | 36.6598 | 36.0304 | 35.2356 | 34.7809 | 34.3535
MELKSHAM GSP | ANDOVER BSP | WHITCHURCH PRIMARY | MINIMUM HEADROOM | SU 45924 48466 | NO | YES | 0 | 4.6284 | 4.4663 | 4.3021 | 4.1358 | 3.9684 | 3.7926 | 3.6358 | 3.4874 | 3.3474 | 2.7337 | 2.1326 | -17.0474 | 5.1284 | 4.9537 | 4.7779 | 4.6 | 4.4221 | 4.2358 | 4.0684 | 3.9116 | 3.7611 | 3.1063 | 2.4558 | 1.7589 | 4.5011 | 4.3263 | 4.1505 | 3.9726 | 3.7947 | 3.6063 | 3.4389 | 3.28 | 3.1295 | 2.4663 | 1.8084 | 1.1074
|  | WHITCHURCH PRIMARY | EE |  |  |  |  | 4.7337 | 4.6053 | 4.4705 | 4.3358 | 4.1968 | 4.0621 | 3.9263 | 3.7958 | 3.6737 | 3.1653 | 2.7326 | 2.2505 | 5.2432 | 5.1053 | 4.9611 | 4.8179 | 4.6716 | 4.5295 | 4.3863 | 4.2474 | 4.12 | 3.5821 | 3.1221 | 2.5821 | 4.6158 | 4.4779 | 4.3337 | 4.1905 | 4.0421 | 3.9 | 3.7547 | 3.6158 | 3.4853 | 2.9379 | 2.4674 | 1.9242
|  | WHITCHURCH PRIMARY | HT |  |  |  |  | 4.6284 | 4.4663 | 4.3021 | 4.1358 | 3.9684 | 3.7926 | 3.6358 | 3.4874 | 3.3474 | 2.7337 | 2.1326 | 1.5074 | 5.1284 | 4.9537 | 4.7779 | 4.6 | 4.4221 | 4.2358 | 4.0684 | 3.9116 | 3.7611 | 3.1063 | 2.4558 | 1.7589 | 4.5011 | 4.3263 | 4.1505 | 3.9726 | 3.7947 | 3.6063 | 3.4389 | 3.28 | 3.1295 | 2.4663 | 1.8084 | 1.1074
|  | WHITCHURCH PRIMARY | HE |  |  |  |  | 4.8768 | 4.7916 | 4.7021 | 4.6074 | 4.5053 | 4.4105 | 4.3137 | 4.2221 | 4.1411 | 3.8284 | 3.6105 | -17.0474 | 5.3621 | 5.3063 | 5.2137 | 5.1137 | 5.0074 | 4.9074 | 4.8063 | 4.7095 | 4.6232 | 4.2905 | 4.0579 | 3.7547 | 4.7726 | 4.6811 | 4.5853 | 4.4863 | 4.3789 | 4.2789 | 4.1768 | 4.0789 | 3.9926 | 3.6568 | 3.4211 | 3.1137
|  | WHITCHURCH PRIMARY | CF |  |  |  |  | 4.9526 | 4.9032 | 4.8516 | 4.7979 | 4.7421 | 4.6811 | 4.6263 | 4.5705 | 4.5158 | 4.2495 | 4.0674 | 3.9137 | 5.4116 | 5.3811 | 5.3505 | 5.3126 | 5.2537 | 5.1895 | 5.1295 | 5.0705 | 5.0116 | 4.7253 | 4.5284 | 4.3568 | 4.8526 | 4.7989 | 4.7432 | 4.6853 | 4.6263 | 4.5611 | 4.5021 | 4.4421 | 4.3832 | 4.0958 | 3.8958 | 3.7232
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY PRIMARY | MINIMUM HEADROOM | SU 52936 08794 | NO | YES | 1.0516 | 34.4357 | 44.2694 | 43.3126 | 42.0589 | 40.8884 | 39.9957 | 39.3421 | 38.7799 | 38.2663 | 36.4736 | 35.0599 | 2.0726 | 27.4778 | 37.3115 | 36.2294 | 34.8052 | 33.4789 | 32.4726 | 31.7431 | 31.1168 | 30.5431 | 28.5599 | 26.9884 | 25.5399 | 28.5305 | 38.3642 | 37.2663 | 35.8189 | 34.4726 | 33.4526 | 32.7115 | 32.0757 | 31.4936 | 29.4821 | 27.8968 | 26.4484
|  | WHITELEY PRIMARY | EE |  |  |  |  | 34.5347 | 44.3989 | 43.6326 | 42.4378 | 41.3273 | 40.4915 | 39.8936 | 39.3684 | 38.901 | 37.4284 | 36.3147 | 35.321 | 27.5768 | 37.441 | 36.5747 | 35.2136 | 33.9526 | 33.0063 | 32.3389 | 31.7515 | 31.2294 | 29.601 | 28.3726 | 27.2484 | 28.6294 | 38.4936 | 37.6147 | 36.2326 | 34.9505 | 33.9905 | 33.3115 | 32.7168 | 32.1863 | 30.5315 | 29.2778 | 28.1505
|  | WHITELEY PRIMARY | HT |  |  |  |  | 34.4357 | 44.2694 | 43.3126 | 42.0589 | 40.8884 | 39.9957 | 39.3421 | 38.7799 | 38.2663 | 36.4736 | 35.0599 | 33.7768 | 27.4778 | 37.3115 | 36.2294 | 34.8052 | 33.4789 | 32.4726 | 31.7431 | 31.1168 | 30.5431 | 28.5599 | 26.9884 | 25.5399 | 28.5305 | 38.3642 | 37.2663 | 35.8189 | 34.4726 | 33.4526 | 32.7115 | 32.0757 | 31.4936 | 29.4821 | 27.8968 | 26.4484
|  | WHITELEY PRIMARY | HE |  |  |  |  | 34.6652 | 44.5694 | 44.0505 | 42.9315 | 41.8894 | 41.1231 | 40.5936 | 40.1336 | 39.7326 | 38.5694 | 37.7599 | 2.0726 | 27.7073 | 37.6115 | 37.0263 | 35.7473 | 34.5589 | 33.6884 | 33.0915 | 32.5757 | 32.1252 | 30.8273 | 29.9178 | 29.1021 | 28.7599 | 38.6642 | 38.0705 | 36.7715 | 35.5631 | 34.6789 | 34.0736 | 33.5505 | 33.0926 | 31.7747 | 30.8515 | 30.0199
|  | WHITELEY PRIMARY | CF |  |  |  |  | 35.4357 | 44.7021 | 44.6494 | 44.5936 | 44.5368 | 44.3452 | 44.0684 | 43.8084 | 43.5557 | 42.7968 | 42.2526 | 41.7621 | 29.8536 | 37.7442 | 37.6915 | 37.6357 | 37.5789 | 37.3652 | 37.0547 | 36.7631 | 36.4789 | 35.6389 | 35.0284 | 34.4726 | 30.9421 | 38.7968 | 38.7442 | 38.6884 | 38.6315 | 38.4147 | 38.0989 | 37.8031 | 37.5147 | 36.6642 | 36.0452 | 35.4778
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WHITLEY WOOD PRIMARY | MINIMUM HEADROOM | SU 72812 69667 | NO | YES | 1.0526 | 34.0179 | 33.6926 | 33.66 | 33.3642 | 32.5916 | 31.5779 | 30.7453 | 30.1463 | 29.5989 | 27.2379 | 25.0105 | -1.0842 | 29.1526 | 28.3579 | 27.3547 | 26.2453 | 25.0832 | 23.9558 | 23.0337 | 22.3811 | 21.7842 | 19.1989 | 16.7211 | 14.3589 | 30.3484 | 29.5705 | 28.8579 | 27.7474 | 26.4463 | 25.32 | 24.3979 | 23.7463 | 23.1495 | 20.5674 | 18.0926 | 15.7337
|  | WHITLEY WOOD PRIMARY | EE |  |  |  |  | 34.2116 | 33.9442 | 33.66 | 33.3642 | 33.0579 | 32.7653 | 31.9411 | 31.3053 | 30.8726 | 29.2105 | 27.6263 | 26.1547 | 29.3916 | 29.0295 | 28.3011 | 27.4389 | 26.3621 | 25.28 | 24.2537 | 23.5421 | 23.0705 | 21.2442 | 19.4779 | 17.8242 | 30.5853 | 30.2263 | 29.5147 | 28.6726 | 27.6242 | 26.5705 | 25.5716 | 24.8758 | 24.4126 | 22.6211 | 20.8989 | 19.2895
|  | WHITLEY WOOD PRIMARY | HT |  |  |  |  | 34.0179 | 33.6926 | 34.7526 | 33.7537 | 32.5916 | 31.5779 | 30.7453 | 30.1463 | 29.5989 | 27.2379 | 25.0105 | 22.9074 | 29.1526 | 28.3579 | 27.3547 | 26.2453 | 25.0832 | 23.9558 | 23.0337 | 22.3811 | 21.7842 | 19.1989 | 16.7211 | 14.3589 | 30.3484 | 29.5705 | 28.8579 | 27.7474 | 26.4463 | 25.32 | 24.3979 | 23.7463 | 23.1495 | 20.5674 | 18.0926 | 15.7337
|  | WHITLEY WOOD PRIMARY | HE |  |  |  |  | 34.4663 | 34.2779 | 34.0705 | 33.8463 | 34.9568 | 34.1179 | 33.3905 | 32.8547 | 32.5463 | 31.4495 | 30.4211 | -1.0842 | 29.6874 | 29.4916 | 29.1916 | 28.4884 | 27.5505 | 26.6042 | 25.7884 | 25.1947 | 24.8621 | 23.6758 | 22.5263 | 21.4495 | 30.88 | 30.6842 | 30.3884 | 29.7011 | 29.0526 | 28.1063 | 27.2905 | 26.6968 | 26.3632 | 25.1779 | 24.0274 | 22.9505
|  | WHITLEY WOOD PRIMARY | CF |  |  |  |  | 34.64 | 34.5421 | 34.44 | 34.3326 | 34.2232 | 34.1105 | 34 | 33.8916 | 33.7832 | 33.2958 | 33.0558 | 32.6305 | 29.8611 | 29.7632 | 29.6611 | 29.5421 | 29.4126 | 29.1979 | 28.8558 | 28.4453 | 28.0337 | 26.2653 | 25.5716 | 24.9947 | 31.0537 | 30.9558 | 30.8537 | 30.7358 | 30.6063 | 30.3958 | 30.0611 | 29.6621 | 29.2611 | 27.54 | 26.8632 | 26.3011
MINETY GSP | CIRENCESTER BSP | WHITEWAY PRIMARY | MINIMUM HEADROOM | SP 02076 03059 | NO | YES | 0 | 34.5642 | 34.1568 | 33.7074 | 33.2463 | 32.7632 | 32.2842 | 31.8274 | 31.3937 | 31.0305 | 28.8495 | 26.5558 | 10.9779 | 29.9716 | 29.5305 | 29.0411 | 28.5411 | 28.0158 | 27.4947 | 26.9979 | 26.5221 | 26.1253 | 23.6937 | 21.0979 | 18.7074 | 30.7947 | 30.3537 | 29.8642 | 29.3642 | 28.8389 | 28.3179 | 27.8189 | 27.3432 | 26.9474 | 24.5137 | 21.9158 | 19.5242
|  | WHITEWAY PRIMARY | EE |  |  |  |  | 34.8253 | 34.5105 | 34.1632 | 33.8074 | 33.4379 | 33.0737 | 32.7179 | 32.3674 | 32.0905 | 30.3842 | 28.5474 | 26.8821 | 30.2568 | 29.9179 | 29.5421 | 29.1579 | 28.7589 | 28.3674 | 27.9811 | 27.6 | 27.3032 | 25.4032 | 23.3189 | 21.4137 | 31.08 | 30.7411 | 30.3653 | 29.9811 | 29.5821 | 29.1884 | 28.8032 | 28.4232 | 28.1242 | 26.2232 | 24.1358 | 22.2295
|  | WHITEWAY PRIMARY | HT |  |  |  |  | 34.5642 | 34.1568 | 33.7074 | 33.2463 | 32.7632 | 32.2842 | 31.8274 | 31.3937 | 31.0305 | 28.8495 | 26.5558 | 24.4558 | 29.9716 | 29.5305 | 29.0411 | 28.5411 | 28.0158 | 27.4947 | 26.9979 | 26.5221 | 26.1253 | 23.6937 | 21.0979 | 18.7074 | 30.7947 | 30.3537 | 29.8642 | 29.3642 | 28.8389 | 28.3179 | 27.8189 | 27.3432 | 26.9474 | 24.5137 | 21.9158 | 19.5242
|  | WHITEWAY PRIMARY | HE |  |  |  |  | 35.1568 | 34.9442 | 34.6937 | 34.4316 | 34.1474 | 33.8684 | 33.5979 | 33.3337 | 33.1389 | 31.8432 | 30.3926 | 10.9779 | 30.6179 | 30.3895 | 30.12 | 29.8379 | 29.5337 | 29.2326 | 28.9389 | 28.6526 | 28.4453 | 26.9926 | 25.3295 | 23.8242 | 31.4411 | 31.2126 | 30.9432 | 30.6611 | 30.3558 | 30.0547 | 29.7611 | 29.4747 | 29.2674 | 27.8137 | 26.1495 | 24.6442
|  | WHITEWAY PRIMARY | CF |  |  |  |  | 34.8221 | 34.7011 | 34.5705 | 34.44 | 34.3042 | 34.1632 | 34.0158 | 33.8695 | 33.7411 | 32.84 | 32.4326 | 31.6242 | 30.1758 | 30.0453 | 29.9053 | 29.7642 | 29.6179 | 29.4653 | 29.3063 | 29.1463 | 29.0095 | 28.0105 | 27.5895 | 26.6579 | 31.0632 | 30.9326 | 30.7926 | 30.6516 | 30.5042 | 30.3526 | 30.1937 | 30.0337 | 29.8958 | 28.8968 | 28.4116 | 27.4789
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WILSON ROAD PRIMARY | MINIMUM HEADROOM | SU 69235 73304 | NO | YES | 0 | 34.8642 | 34.5958 | 34.3105 | 34.0116 | 33.7011 | 33.3495 | 32.8705 | 32.3947 | 31.9484 | 29.9147 | 27.6389 | 0.16105 | 30.4568 | 29.9547 | 29.4263 | 28.7358 | 27.4789 | 26.3358 | 25.8032 | 25.2979 | 24.8221 | 22.6253 | 20.0884 | 17.6 | 31.2758 | 30.9926 | 30.6937 | 30.1042 | 28.8347 | 27.6653 | 27.1253 | 26.6116 | 26.1284 | 23.9137 | 21.3768 | 18.8874
|  | WILSON ROAD PRIMARY | EE |  |  |  |  | 35.02 | 34.7989 | 34.5642 | 34.3137 | 34.0526 | 33.7958 | 33.5347 | 33.28 | 32.9368 | 31.3811 | 29.6411 | 27.9526 | 30.7958 | 30.3958 | 29.9705 | 29.3779 | 28.2726 | 27.2168 | 26.7568 | 26.2947 | 25.88 | 24.22 | 22.2842 | 20.3758 | 31.4421 | 31.2105 | 30.9642 | 30.6937 | 29.6421 | 28.5611 | 28.0947 | 27.6253 | 27.2032 | 25.5168 | 23.5726 | 21.6642
|  | WILSON ROAD PRIMARY | HT |  |  |  |  | 34.8642 | 34.5958 | 34.3105 | 34.0116 | 33.7011 | 33.3495 | 32.8705 | 32.3947 | 31.9484 | 29.9147 | 27.6389 | 25.4263 | 30.4568 | 29.9547 | 29.4263 | 28.7358 | 27.4789 | 26.3358 | 25.8032 | 25.2979 | 24.8221 | 22.6253 | 20.0884 | 17.6 | 31.2758 | 30.9926 | 30.6937 | 30.1042 | 28.8347 | 27.6653 | 27.1253 | 26.6116 | 26.1284 | 23.9137 | 21.3768 | 18.8874
|  | WILSON ROAD PRIMARY | HE |  |  |  |  | 35.1863 | 35.0116 | 34.8179 | 34.6105 | 34.3895 | 34.1779 | 33.9789 | 33.7926 | 33.6316 | 33.0474 | 31.9705 | 0.16105 | 31.0411 | 30.8495 | 30.6179 | 30.1442 | 29.1337 | 28.1926 | 27.8379 | 27.4947 | 27.1968 | 26.14 | 24.8305 | 23.5389 | 31.6232 | 31.4421 | 31.2421 | 31.0179 | 30.5021 | 29.5558 | 29.1968 | 28.8474 | 28.5453 | 27.4737 | 26.1326 | 24.8274
|  | WILSON ROAD PRIMARY | CF |  |  |  |  | 35.3084 | 35.2042 | 35.0947 | 34.9811 | 34.8642 | 34.7453 | 34.6284 | 34.5116 | 34.3958 | 33.8789 | 33.6168 | 33.4326 | 31.1747 | 31.06 | 30.9389 | 30.7747 | 30.3432 | 29.8842 | 29.6737 | 29.4463 | 29.2179 | 28.1611 | 27.2853 | 26.4137 | 31.7505 | 31.6421 | 31.5274 | 31.4042 | 31.2684 | 31.1295 | 31.0074 | 30.8063 | 30.5832 | 29.5326 | 28.6379 | 27.7421
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE PRIMARY | MINIMUM HEADROOM | SZ 02014 99989 | NO | YES | 0 | 19.4021 | 18.2958 | 42.1526 | 41.0179 | 40.1137 | 39.3 | 38.3474 | 37.3758 | 36.4442 | 32.0389 | 28.4958 | 0.48526 | 12.6021 | 11.3221 | 35.0611 | 33.8105 | 32.8411 | 31.9789 | 30.9421 | 29.8779 | 28.8558 | 23.9916 | 20.0863 | 16.6737 | 14.1747 | 12.8958 | 36.6358 | 35.3863 | 34.4147 | 33.5484 | 32.5084 | 31.44 | 30.4126 | 25.5189 | 21.5768 | 18.1516
|  | WIMBORNE PRIMARY | EE |  |  |  |  | 19.7368 | 18.9726 | 43.0053 | 42.0232 | 41.2642 | 40.6137 | 39.7874 | 38.9347 | 38.1021 | 34.3063 | 31.4916 | 29.2021 | 13.1716 | 12.0758 | 35.9874 | 34.9011 | 34.0874 | 33.4011 | 32.5063 | 31.5758 | 30.6674 | 26.4884 | 23.4095 | 20.8463 | 14.7526 | 13.6474 | 37.5611 | 36.4758 | 35.6589 | 34.9663 | 34.0663 | 33.1316 | 32.2158 | 27.9905 | 24.8568 | 22.2789
|  | WIMBORNE PRIMARY | HT |  |  |  |  | 19.4021 | 18.2958 | 42.1526 | 41.0179 | 40.1137 | 39.3 | 38.3474 | 37.3758 | 36.4442 | 32.0389 | 28.4958 | 25.4442 | 12.6021 | 11.3221 | 35.0611 | 33.8105 | 32.8411 | 31.9789 | 30.9421 | 29.8779 | 28.8558 | 23.9916 | 20.0863 | 16.6737 | 14.1747 | 12.8958 | 36.6358 | 35.3863 | 34.4147 | 33.5484 | 32.5084 | 31.44 | 30.4126 | 25.5189 | 21.5768 | 18.1516
|  | WIMBORNE PRIMARY | HE |  |  |  |  | 20.0811 | 19.8295 | 44.1116 | 43.3368 | 42.7621 | 42.2979 | 41.6621 | 40.9979 | 40.3537 | 37.4821 | 35.5758 | 0.48526 | 13.9147 | 13.0653 | 37.2032 | 36.3295 | 35.7158 | 35.2274 | 34.5347 | 33.8063 | 33.0958 | 29.8884 | 27.7516 | 25.9758 | 15.5042 | 14.64 | 38.7758 | 37.9042 | 37.2874 | 36.7968 | 36.1021 | 35.3716 | 34.6579 | 31.4347 | 29.2832 | 27.4947
|  | WIMBORNE PRIMARY | CF |  |  |  |  | 20.3179 | 20.1874 | 45.0516 | 44.9105 | 44.7611 | 44.6084 | 44.2621 | 43.8842 | 43.4937 | 41.4853 | 40.1884 | 39.1463 | 14.7389 | 14.2905 | 38.8642 | 38.4432 | 38.12 | 37.8326 | 37.4284 | 36.9874 | 36.5389 | 34.3011 | 32.8453 | 31.6663 | 16.3032 | 15.8695 | 40.4558 | 40.0274 | 39.6979 | 39.4053 | 38.9968 | 38.5547 | 38.1053 | 35.8632 | 34.4021 | 33.2137
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES PRIMARY | MINIMUM HEADROOM | SU 03028 12678 | YES | YES | 0 | 5.2179 | 5.1884 | 5.16 | 5.1305 | 5.1 | 5.0463 | 4.9768 | 4.9579 | 4.9421 | 4.7905 | 4.6074 | 3.3989 | 4.9968 | 4.9653 | 4.9347 | 4.9032 | 4.8716 | 4.8126 | 4.7337 | 4.7168 | 4.7011 | 4.5432 | 4.3453 | 4.28 | 5.0137 | 4.9821 | 4.9516 | 4.92 | 4.8884 | 4.8274 | 4.7484 | 4.7305 | 4.7147 | 4.5495 | 4.3463 | 4.2779
|  | WIMBORNE ST GILES PRIMARY | EE |  |  |  |  | 5.2347 | 5.2126 | 5.1895 | 5.1642 | 5.14 | 5.1126 | 5.0874 | 5.0632 | 5.0389 | 4.9274 | 4.7832 | 4.6747 | 5.0168 | 4.9926 | 4.9663 | 4.9411 | 4.9147 | 4.8884 | 4.8621 | 4.8368 | 4.8126 | 4.7032 | 4.5526 | 4.4347 | 5.0337 | 5.0095 | 4.9832 | 4.9579 | 4.9316 | 4.9032 | 4.8768 | 4.8505 | 4.8242 | 4.7074 | 4.5474 | 4.4263
|  | WIMBORNE ST GILES PRIMARY | HT |  |  |  |  | 5.2179 | 5.1884 | 5.16 | 5.1305 | 5.1 | 5.0463 | 4.9768 | 4.9579 | 4.9421 | 4.7905 | 4.6074 | 4.5432 | 4.9968 | 4.9653 | 4.9347 | 4.9032 | 4.8716 | 4.8126 | 4.7337 | 4.7168 | 4.7011 | 4.5432 | 4.3453 | 4.28 | 5.0137 | 4.9821 | 4.9516 | 4.92 | 4.8884 | 4.8274 | 4.7484 | 4.7305 | 4.7147 | 4.5495 | 4.3463 | 4.2779
|  | WIMBORNE ST GILES PRIMARY | HE |  |  |  |  | 5.2474 | 5.2379 | 5.2274 | 5.2147 | 5.1968 | 5.1789 | 5.1611 | 5.1463 | 5.1305 | 5.0695 | 4.9674 | 3.3989 | 5.0453 | 5.0295 | 5.0126 | 4.9958 | 4.9768 | 4.9589 | 4.9411 | 4.9253 | 4.9095 | 4.8495 | 4.7368 | 4.6432 | 5.0621 | 5.0463 | 5.0295 | 5.0126 | 4.9926 | 4.9747 | 4.9568 | 4.94 | 4.9242 | 4.86 | 4.7453 | 4.6495
|  | WIMBORNE ST GILES PRIMARY | CF |  |  |  |  | 5.2568 | 5.2516 | 5.2474 | 5.2421 | 5.2347 | 5.2284 | 5.2211 | 5.2116 | 5.2021 | 5.1579 | 5.1211 | 5.06 | 5.0611 | 5.0516 | 5.0432 | 5.0337 | 5.0221 | 5.0126 | 5.0032 | 4.9916 | 4.9832 | 4.9358 | 4.8979 | 4.8295 | 5.0779 | 5.0684 | 5.06 | 5.0505 | 5.0389 | 5.0284 | 5.0189 | 5.0084 | 4.9989 | 4.9505 | 4.9105 | 4.84
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON PRIMARY | MINIMUM HEADROOM | ST 71286 27802 | NO | YES | 0 | 13.7512 | 13.3522 | 12.9196 | 12.5922 | 12.3143 | 12.0375 | 11.787 | 11.1659 | 11.0375 | 6.7617 | 6.3775 | -2.1362 | 11.2396 | 10.7954 | 10.3133 | 9.9575 | 9.6607 | 9.3649 | 9.0964 | 8.387 | 8.2585 | 3.3354 | 2.9512 | 2.6491 | 11.4122 | 10.9733 | 10.4964 | 10.1438 | 9.8491 | 9.5554 | 9.288 | 8.5891 | 8.4607 | 3.7754 | 3.3912 | 3.0891
|  | WINCANTON PRIMARY | EE |  |  |  |  | 13.9364 | 13.5933 | 13.2154 | 12.9417 | 12.7133 | 12.4943 | 12.2849 | 12.0817 | 11.9017 | 9.4028 | 7.3028 | 7.1028 | 11.4417 | 11.0585 | 10.6364 | 10.3385 | 10.0943 | 9.8607 | 9.6364 | 9.4196 | 9.228 | 6.388 | 3.9512 | 3.7512 | 11.6122 | 11.2333 | 10.8164 | 10.5207 | 10.2785 | 10.0459 | 9.8238 | 9.608 | 9.4175 | 6.5922 | 4.1922 | 3.9922
|  | WINCANTON PRIMARY | HT |  |  |  |  | 13.7512 | 13.3522 | 12.9196 | 12.5922 | 12.3143 | 12.0375 | 11.787 | 11.1659 | 11.0375 | 6.7617 | 6.3775 | 6.0754 | 11.2396 | 10.7954 | 10.3133 | 9.9575 | 9.6607 | 9.3649 | 9.0964 | 8.387 | 8.2585 | 3.3354 | 2.9512 | 2.6491 | 11.4122 | 10.9733 | 10.4964 | 10.1438 | 9.8491 | 9.5554 | 9.288 | 8.5891 | 8.4607 | 3.7754 | 3.3912 | 3.0891
|  | WINCANTON PRIMARY | HE |  |  |  |  | 14.1796 | 13.9122 | 13.607 | 13.4017 | 13.2375 | 13.0796 | 12.9301 | 12.7901 | 12.668 | 9.9733 | 7.987 | -2.1362 | 11.708 | 11.408 | 11.0638 | 10.8407 | 10.667 | 10.4996 | 10.3417 | 10.1933 | 10.0638 | 6.947 | 4.6238 | 4.528 | 11.8764 | 11.5796 | 11.2396 | 11.0185 | 10.8459 | 10.6785 | 10.5228 | 10.3743 | 10.247 | 7.1628 | 4.8764 | 4.7807
|  | WINCANTON PRIMARY | CF |  |  |  |  | 14.487 | 14.3754 | 14.2575 | 14.0807 | 13.8849 | 13.7185 | 13.607 | 13.5185 | 13.4301 | 12.967 | 12.6007 | 12.1817 | 12.0554 | 11.9322 | 11.8007 | 11.6007 | 11.3785 | 11.1922 | 11.0691 | 10.9733 | 10.8775 | 10.3712 | 9.9575 | 9.4722 | 12.1449 | 12.0343 | 11.9154 | 11.7385 | 11.5428 | 11.3659 | 11.2438 | 11.1501 | 11.0543 | 10.5522 | 10.1438 | 9.6659
COWLEY GSP | WITNEY BSP | WINDRUSH PARK PRIMARY | MINIMUM HEADROOM | SP 33366 09758 | NO | YES | 0 | 33.8389 | 33.7126 | 33.5779 | 33.44 | 33.2979 | 33.1547 | 33.0305 | 32.8463 | 32.6516 | 31.7263 | 30.5189 | 13.58 | 30.4863 | 30.2463 | 29.9811 | 29.6084 | 29.2116 | 28.9558 | 28.7221 | 28.5021 | 28.2926 | 27.2789 | 25.9189 | 23.5821 | 31.1747 | 30.9347 | 30.6684 | 30.2958 | 29.8979 | 29.6421 | 29.4084 | 29.1895 | 28.9789 | 27.9663 | 26.6042 | 24.1611
|  | WINDRUSH PARK PRIMARY | EE |  |  |  |  | 33.9105 | 33.8063 | 33.6937 | 33.5779 | 33.4579 | 33.3421 | 33.2337 | 33.1263 | 33.0337 | 32.4253 | 32.0547 | 30.9895 | 30.6474 | 30.4558 | 30.2421 | 29.9695 | 29.6316 | 29.3884 | 29.1789 | 28.9737 | 28.7905 | 28.0474 | 27.8558 | 26.6316 | 31.3347 | 31.1432 | 30.9305 | 30.6579 | 30.3189 | 30.0758 | 29.8663 | 29.66 | 29.4779 | 28.7326 | 28.6453 | 27.4221
|  | WINDRUSH PARK PRIMARY | HT |  |  |  |  | 33.8389 | 33.7126 | 33.5779 | 33.44 | 33.2979 | 33.1547 | 33.0305 | 32.8463 | 32.6516 | 31.7263 | 30.5189 | 28.6642 | 30.4863 | 30.2463 | 29.9811 | 29.6084 | 29.2116 | 28.9558 | 28.7221 | 28.5021 | 28.2926 | 27.2789 | 25.9189 | 23.5821 | 31.1747 | 30.9347 | 30.6684 | 30.2958 | 29.8979 | 29.6421 | 29.4084 | 29.1895 | 28.9789 | 27.9663 | 26.6042 | 24.1611
|  | WINDRUSH PARK PRIMARY | HE |  |  |  |  | 34.0116 | 33.9379 | 33.8568 | 33.7695 | 33.6768 | 33.5874 | 33.5032 | 33.4253 | 33.3579 | 33.1305 | 32.0821 | 13.58 | 30.8684 | 30.7442 | 30.6021 | 30.3863 | 30.1 | 29.9137 | 29.7516 | 29.6095 | 29.48 | 28.9905 | 27.3926 | 26.3968 | 31.5568 | 31.4326 | 31.2905 | 31.0747 | 30.7884 | 30.6011 | 30.44 | 30.2968 | 30.1684 | 29.6779 | 27.9737 | 26.9768
|  | WINDRUSH PARK PRIMARY | CF |  |  |  |  | 34.0811 | 34.0432 | 34.0042 | 33.9632 | 33.9211 | 33.8779 | 33.8358 | 33.7937 | 33.7516 | 33.5653 | 33.4716 | 33.1821 | 31.0905 | 31.0179 | 30.9358 | 30.8442 | 30.7547 | 30.6579 | 30.5716 | 30.4695 | 30.3621 | 29.8484 | 29.4211 | 28.8084 | 31.7 | 31.66 | 31.6189 | 31.5326 | 31.4432 | 31.3463 | 31.26 | 31.1579 | 31.0495 | 30.5368 | 30.1084 | 29.4958
MANNINGTON GSP |  | WINFRITH HEATH PRIMARY | MINIMUM HEADROOM | SY 80748 86538 | NO | YES | 0 | 23.6529 | 23.2234 | 22.7013 | 21.9929 | 21.1003 | 19.8908 | 18.9392 | 18.1255 | 17.3192 | 14.3276 | 12.7739 | 1.1855 | 25.8529 | 25.3676 | 24.7718 | 23.9592 | 22.9413 | 21.5508 | 20.4634 | 19.535 | 18.6161 | 15.2613 | 13.6013 | 12.6371 | 23.4803 | 22.9961 | 22.4024 | 21.5908 | 20.5687 | 19.1739 | 18.0803 | 17.1466 | 16.2203 | 12.8108 | 11.0813 | 10.0887
|  | WINFRITH HEATH PRIMARY | EE |  |  |  |  | 23.7792 | 23.3887 | 22.8718 | 22.2297 | 21.3708 | 20.1908 | 19.2571 | 18.4539 | 17.6571 | 14.7118 | 13.2403 | 12.5466 | 25.9908 | 25.5476 | 24.9561 | 24.2171 | 23.2361 | 21.8803 | 20.8139 | 19.9034 | 19.0003 | 15.7297 | 14.2003 | 13.4603 | 23.6182 | 23.175 | 22.5845 | 21.8466 | 20.8613 | 19.4992 | 18.4245 | 17.5045 | 16.5908 | 13.2403 | 11.6118 | 10.8403
|  | WINFRITH HEATH PRIMARY | HT |  |  |  |  | 23.6529 | 23.2234 | 22.7013 | 21.9929 | 21.1003 | 19.8908 | 18.9392 | 18.1255 | 17.3192 | 14.3276 | 12.7739 | 11.8824 | 25.8529 | 25.3676 | 24.7718 | 23.9592 | 22.9413 | 21.5508 | 20.4634 | 19.535 | 18.6161 | 15.2613 | 13.6013 | 12.6371 | 23.4803 | 22.9961 | 22.4024 | 21.5908 | 20.5687 | 19.1739 | 18.0803 | 17.1466 | 16.2203 | 12.8108 | 11.0813 | 10.0887
|  | WINFRITH HEATH PRIMARY | HE |  |  |  |  | 23.9118 | 23.5771 | 23.0971 | 22.5118 | 21.7487 | 20.6329 | 19.7613 | 19.0255 | 18.3003 | 15.755 | 14.7497 | 1.1855 | 26.1318 | 25.7487 | 25.1939 | 24.5182 | 23.6424 | 22.3476 | 21.3434 | 20.4971 | 19.6613 | 16.7582 | 15.6413 | 15.1045 | 23.7592 | 23.3771 | 22.8245 | 22.1497 | 21.2697 | 19.975 | 18.9687 | 18.1182 | 17.2792 | 14.3476 | 13.2045 | 12.6424
|  | WINFRITH HEATH PRIMARY | CF |  |  |  |  | 24.0982 | 23.9308 | 23.7308 | 23.4592 | 23.1213 | 22.6118 | 22.1761 | 21.7761 | 21.3497 | 19.7276 | 19.0897 | 18.755 | 26.3413 | 26.1497 | 25.9192 | 25.6055 | 25.2171 | 24.6276 | 24.1245 | 23.6634 | 23.1718 | 21.3076 | 20.5961 | 20.2392 | 23.9676 | 23.7771 | 23.5476 | 23.2339 | 22.8445 | 22.2539 | 21.7497 | 21.2876 | 20.795 | 18.9245 | 18.1982 | 17.8245
COWLEY GSP | DRAYTON BSP | WINSMORE LANE PRIMARY | MINIMUM HEADROOM | SU 49513 96982 | NO | YES | 0.2 | 24.9995 | 24.7005 | 24.3826 | 24.0521 | 23.7121 | 23.3689 | 23.0668 | 22.79 | 22.5353 | 21.21 | 19.1005 | -10.1289 | 20.3016 | 19.7153 | 19.1195 | 18.5132 | 17.9089 | 17.3026 | 16.7437 | 16.2226 | 15.7353 | 13.5216 | 11.1784 | 8.1826 | 21.1279 | 20.8121 | 20.47 | 19.8647 | 19.2616 | 18.6553 | 18.0974 | 17.5763 | 17.09 | 14.8774 | 12.5384 | 9.5468
|  | WINSMORE LANE PRIMARY | EE |  |  |  |  | 25.1721 | 24.9247 | 24.6626 | 24.3858 | 24.0995 | 23.8216 | 23.5574 | 23.3026 | 23.0753 | 22.2395 | 21.3153 | 19.3942 | 20.6858 | 20.2153 | 19.7353 | 19.2384 | 18.7363 | 18.2426 | 17.77 | 17.3174 | 16.9037 | 15.1479 | 13.6153 | 11.4289 | 21.3132 | 21.0532 | 20.7784 | 20.4879 | 20.0879 | 19.5953 | 19.1226 | 18.67 | 18.2563 | 16.5026 | 14.9711 | 12.7889
|  | WINSMORE LANE PRIMARY | HT |  |  |  |  | 24.9995 | 24.7005 | 24.3826 | 24.0521 | 23.7121 | 23.3689 | 23.0668 | 22.79 | 22.5353 | 21.21 | 19.1005 | 16.4595 | 20.3016 | 19.7153 | 19.1195 | 18.5132 | 17.9089 | 17.3026 | 16.7437 | 16.2226 | 15.7353 | 13.5216 | 11.1784 | 8.1826 | 21.1279 | 20.8121 | 20.47 | 19.8647 | 19.2616 | 18.6553 | 18.0974 | 17.5763 | 17.09 | 14.8774 | 12.5384 | 9.5468
|  | WINSMORE LANE PRIMARY | HE |  |  |  |  | 25.39 | 25.2079 | 25.0068 | 24.7911 | 24.5605 | 24.3395 | 24.1321 | 23.9374 | 23.77 | 23.2016 | 22.8647 | -10.1289 | 20.9521 | 20.7532 | 20.5342 | 20.1805 | 19.81 | 19.4468 | 19.1026 | 18.7816 | 18.4974 | 17.3826 | 16.4626 | 14.8679 | 21.5479 | 21.3574 | 21.1489 | 20.9247 | 20.6858 | 20.4574 | 20.2416 | 20.0395 | 19.8489 | 18.7353 | 17.8163 | 16.2237
|  | WINSMORE LANE PRIMARY | CF |  |  |  |  | 25.5426 | 25.4416 | 25.3363 | 25.2268 | 25.1142 | 24.9995 | 24.8868 | 24.7753 | 24.6637 | 24.1658 | 23.9163 | 23.7784 | 21.1205 | 21.0068 | 20.89 | 20.7679 | 20.6416 | 20.4226 | 20.2037 | 19.9879 | 19.7742 | 18.7826 | 18.1079 | 17.13 | 21.7068 | 21.6005 | 21.49 | 21.3742 | 21.2563 | 21.1353 | 21.0163 | 20.8984 | 20.7816 | 20.1342 | 19.4605 | 18.4837
MANNINGTON GSP | LYTCHETT BSP | WINTERBORNE KINGSTON PRIMARY | MINIMUM HEADROOM | SY 84631 98138 | NO | YES | 0 | 8.3347 | 24.3705 | 22.5926 | 22.3832 | 21.5842 | 19.8484 | 17.6758 | 17.3632 | 17.0463 | 12.5895 | 6.4674 | 4.8674 | 7.1168 | 23.0989 | 21.7442 | 21.5211 | 19.9747 | 18.0274 | 15.5684 | 15.3032 | 15.0379 | 10.4379 | 3.9453 | 2.3716 | 7.3979 | 23.3789 | 21.5979 | 21.3737 | 20.2168 | 18.2326 | 15.7337 | 15.4211 | 15.1032 | 10.1705 | 3.2947 | 1.5663
|  | WINTERBORNE KINGSTON PRIMARY | EE |  |  |  |  | 8.5095 | 24.5905 | 22.5926 | 22.3832 | 21.9832 | 21.5811 | 21.1663 | 20.7358 | 20.2968 | 16.1232 | 10.2842 | 6.7105 | 7.2021 | 23.3411 | 21.7442 | 21.5211 | 21.1516 | 20.7832 | 20.4084 | 20.0232 | 19.6347 | 15.5316 | 9.56 | 5.66 | 7.5874 | 23.6189 | 21.5979 | 21.3737 | 20.9611 | 20.5453 | 20.1168 | 19.6747 | 19.2232 | 14.6937 | 8.2316 | 4.1779
|  | WINTERBORNE KINGSTON PRIMARY | HT |  |  |  |  | 8.3347 | 24.3705 | 24.1021 | 23.3579 | 21.5842 | 19.8484 | 17.6758 | 17.3632 | 17.0463 | 12.5895 | 6.4674 | 4.8674 | 7.1168 | 23.0989 | 22.8147 | 21.9705 | 19.9747 | 18.0274 | 15.5684 | 15.3032 | 15.0379 | 10.4379 | 3.9453 | 2.3716 | 7.3979 | 23.3789 | 23.0926 | 22.2474 | 20.2168 | 18.2326 | 15.7337 | 15.4211 | 15.1032 | 10.1705 | 3.2947 | 1.5663
|  | WINTERBORNE KINGSTON PRIMARY | HE |  |  |  |  | 8.74 | 24.9095 | 24.7684 | 24.6232 | 24.3621 | 24.12 | 23.8811 | 23.6432 | 23.4137 | 21.44 | 17.6432 | 13.4389 | 7.4516 | 23.6832 | 23.5347 | 23.3811 | 23.1411 | 22.9168 | 22.6989 | 22.4832 | 22.2768 | 20.3242 | 16.1358 | 12.8779 | 7.7937 | 23.9642 | 23.8147 | 23.6611 | 23.3916 | 23.1421 | 22.8968 | 22.6505 | 22.4147 | 20.2674 | 15.9316 | 12.54
|  | WINTERBORNE KINGSTON PRIMARY | CF |  |  |  |  | 8.8211 | 25.2611 | 25.1842 | 25.1042 | 24.9705 | 24.84 | 24.7074 | 24.58 | 24.4632 | 23.7463 | 21.4032 | 19.22 | 7.6537 | 23.9663 | 23.9926 | 23.9074 | 23.7811 | 23.6579 | 23.5337 | 23.4105 | 23.2989 | 22.5989 | 20 | 17.5958 | 7.9432 | 24.3189 | 24.2726 | 24.1874 | 24.0474 | 23.9105 | 23.7726 | 23.6379 | 23.5158 | 22.7505 | 20.0726 | 17.5779
MANNINGTON GSP | REDHILL BSP | WINTON PRIMARY | MINIMUM HEADROOM | SZ 09349 93822 | NO | YES | 0 | 26.0674 | 25.5853 | 37.8737 | 37.3442 | 36.7979 | 36.2474 | 35.7611 | 35.3189 | 34.5021 | 30.4526 | 26.7832 | -4.6747 | 20.2358 | 19.3284 | 31.2053 | 30.2874 | 29.3632 | 28.3484 | 27.3453 | 26.3126 | 25.3221 | 20.8495 | 16.7537 | 12.9789 | 21.7853 | 21.1358 | 33.0305 | 32.1305 | 31.22 | 30.1916 | 29.1842 | 28.1526 | 27.1589 | 22.6821 | 18.5779 | 14.8011
|  | WINTON PRIMARY | EE |  |  |  |  | 26.3432 | 25.9442 | 38.3189 | 37.8747 | 37.4126 | 36.9663 | 36.5421 | 36.1326 | 35.7684 | 33.3463 | 30.4958 | 27.9389 | 20.8432 | 20.1221 | 32.1821 | 31.4358 | 30.6884 | 29.8874 | 29.1126 | 28.3653 | 27.5526 | 24.0568 | 20.8674 | 17.9716 | 22.0811 | 21.6632 | 33.9842 | 33.2505 | 32.5158 | 31.7295 | 30.9684 | 30.2105 | 29.3905 | 25.8853 | 22.6863 | 19.7874
|  | WINTON PRIMARY | HT |  |  |  |  | 26.0674 | 25.5853 | 37.8737 | 37.3442 | 36.7979 | 36.2474 | 35.7611 | 35.3189 | 34.5021 | 30.4526 | 26.7832 | 23.4316 | 20.2358 | 19.3284 | 31.2053 | 30.2874 | 29.3632 | 28.3484 | 27.3453 | 26.3126 | 25.3221 | 20.8495 | 16.7537 | 12.9789 | 21.7853 | 21.1358 | 33.0305 | 32.1305 | 31.22 | 30.1916 | 29.1842 | 28.1526 | 27.1589 | 22.6821 | 18.5779 | 14.8011
|  | WINTON PRIMARY | HE |  |  |  |  | 26.7105 | 26.4232 | 38.9063 | 38.5653 | 38.2011 | 37.8505 | 37.5221 | 37.2126 | 36.9474 | 36.0453 | 34.7126 | -4.6747 | 21.4116 | 21.1137 | 33.4811 | 32.9621 | 32.4274 | 31.8347 | 31.2821 | 30.7295 | 30.1232 | 27.6832 | 25.4663 | 23.4842 | 22.4758 | 22.1768 | 34.6484 | 34.2968 | 33.9232 | 33.5579 | 33.0884 | 32.5453 | 31.9537 | 29.52 | 27.2989 | 25.3158
|  | WINTON PRIMARY | CF |  |  |  |  | 26.9737 | 26.8221 | 39.4642 | 39.3021 | 39.1326 | 38.96 | 38.7905 | 38.6221 | 38.4537 | 37.7042 | 37.3263 | 37.1147 | 21.6863 | 21.5274 | 34.1621 | 33.9926 | 33.7305 | 33.3579 | 32.9758 | 32.6232 | 32.2895 | 30.8589 | 29.3642 | 28.0368 | 22.7505 | 22.5905 | 35.2253 | 35.0558 | 34.8768 | 34.6916 | 34.5095 | 34.3305 | 34.0916 | 32.6895 | 31.2032 | 29.8737
COWLEY GSP | WITNEY BSP | WITNEY TOWN PRIMARY | MINIMUM HEADROOM | SP 35844 09625 | NO | YES | 0 | 40.1927 | 48.9832 | 48.1095 | 46.8547 | 44.8821 | 42.5811 | 40.4842 | 38.4326 | 36.4221 | 31.0232 | 27.3821 | -1.2263 | 30.7948 | 39.5305 | 38.5789 | 37.1832 | 34.9589 | 32.3484 | 29.9684 | 27.64 | 25.3526 | 19.3747 | 15.4221 | 11.38 | 31.9327 | 40.6674 | 39.7168 | 38.3221 | 36.0916 | 33.4758 | 31.0916 | 28.7558 | 26.46 | 20.4126 | 16.3758 | 12.3032
|  | WITNEY TOWN PRIMARY | EE |  |  |  |  | 40.6737 | 49.6084 | 48.9358 | 47.9368 | 46.3211 | 44.4832 | 42.7337 | 40.6211 | 38.4874 | 33.0053 | 30.0768 | 27.2274 | 31.319 | 40.2116 | 39.4863 | 38.3768 | 36.56 | 34.4832 | 32.5105 | 30.1095 | 27.6811 | 21.6053 | 18.4989 | 15.3063 | 32.4558 | 41.3484 | 40.6221 | 39.5147 | 37.6905 | 35.6053 | 33.6221 | 31.2095 | 28.7684 | 22.5937 | 19.3663 | 16.14
|  | WITNEY TOWN PRIMARY | HT |  |  |  |  | 40.1927 | 48.9832 | 48.1095 | 46.8547 | 44.8821 | 42.5811 | 40.4842 | 38.4326 | 36.4221 | 31.0232 | 27.3821 | 23.7716 | 30.7948 | 39.5305 | 38.5789 | 37.1832 | 34.9589 | 32.3484 | 29.9684 | 27.64 | 25.3526 | 19.3747 | 15.4221 | 11.38 | 31.9327 | 40.6674 | 39.7168 | 38.3221 | 36.0916 | 33.4758 | 31.0916 | 28.7558 | 26.46 | 20.4126 | 16.3758 | 12.3032
|  | WITNEY TOWN PRIMARY | HE |  |  |  |  | 41.3169 | 50.4526 | 49.9695 | 49.1495 | 47.6947 | 46.0284 | 44.4032 | 42.4674 | 40.5716 | 36.1968 | 34.3242 | -1.2263 | 32.0211 | 41.1316 | 40.6105 | 39.6958 | 38.0516 | 36.1516 | 34.2989 | 32.0768 | 29.8989 | 24.9579 | 22.8905 | 20.4874 | 33.1569 | 42.2684 | 41.7474 | 40.8337 | 39.1842 | 37.2821 | 35.4253 | 33.2011 | 31.0189 | 26.0411 | 23.9421 | 21.5105
|  | WITNEY TOWN PRIMARY | CF |  |  |  |  | 41.5558 | 50.9979 | 50.7505 | 50.3979 | 49.9242 | 49.3589 | 48.8358 | 48.2526 | 47.58 | 42.3421 | 41.1116 | 39.7432 | 32.3337 | 41.6021 | 41.3368 | 40.9463 | 40.5316 | 39.8979 | 39.3137 | 38.6579 | 37.8958 | 31.8705 | 30.5095 | 28.9674 | 33.5821 | 42.8505 | 42.5842 | 42.1937 | 41.6653 | 41.0295 | 40.4432 | 39.7853 | 39.0221 | 32.9916 | 31.6137 | 30.0526
FLEET-BRAMLEY GSP | WOKINGHAM BSP | WOKINGHAM PRIMARY | MINIMUM HEADROOM | SU 79589 67665 | NO | YES | 0 | 32.1916 | 31.9305 | 31.6368 | 31.3337 | 31.02 | 30.6168 | 30.1453 | 29.7189 | 29.3263 | 27.6337 | 26.1347 | 11.1768 | 29.2905 | 28.7737 | 28.2232 | 27.6737 | 27.0811 | 26.5242 | 26.0084 | 25.5411 | 25.1116 | 23.2484 | 21.5895 | 20.0789 | 30.0863 | 29.5705 | 29.02 | 28.4716 | 27.88 | 27.3221 | 26.8063 | 26.34 | 25.9105 | 24.0474 | 22.3884 | 20.8789
|  | WOKINGHAM PRIMARY | EE |  |  |  |  | 32.3568 | 32.1463 | 31.9232 | 31.6832 | 31.4253 | 31.18 | 30.9474 | 30.7274 | 30.42 | 29.1789 | 28.1189 | 27.18 | 29.6347 | 29.2484 | 28.8179 | 28.3832 | 27.9 | 27.4505 | 27.0305 | 26.66 | 26.3242 | 24.9674 | 23.7821 | 22.7189 | 30.4305 | 30.0453 | 29.6147 | 29.18 | 28.6979 | 28.2474 | 27.8284 | 27.4579 | 27.1211 | 25.7632 | 24.5768 | 23.5147
|  | WOKINGHAM PRIMARY | HT |  |  |  |  | 32.1916 | 31.9305 | 31.6368 | 31.3337 | 31.02 | 30.6168 | 30.1453 | 29.7189 | 29.3263 | 27.6337 | 26.1347 | 24.7768 | 29.2905 | 28.7737 | 28.2232 | 27.6737 | 27.0811 | 26.5242 | 26.0084 | 25.5411 | 25.1116 | 23.2484 | 21.5895 | 20.0789 | 30.0863 | 29.5705 | 29.02 | 28.4716 | 27.88 | 27.3221 | 26.8063 | 26.34 | 25.9105 | 24.0474 | 22.3884 | 20.8789
|  | WOKINGHAM PRIMARY | HE |  |  |  |  | 32.5663 | 32.4211 | 32.2621 | 32.0905 | 31.9063 | 31.7295 | 31.5547 | 31.3926 | 31.2537 | 30.7779 | 30.2958 | 11.1768 | 30.0853 | 29.8389 | 29.5432 | 29.2347 | 28.8695 | 28.5337 | 28.2253 | 27.9705 | 27.7379 | 26.8958 | 26.1821 | 25.5495 | 30.8379 | 30.6253 | 30.3389 | 30.0316 | 29.6653 | 29.3305 | 29.0211 | 28.7674 | 28.5337 | 27.6916 | 26.9789 | 26.3463
|  | WOKINGHAM PRIMARY | CF |  |  |  |  | 32.7042 | 32.6305 | 32.5526 | 32.4726 | 32.3905 | 32.3053 | 32.2221 | 32.14 | 32.0579 | 31.6705 | 31.4684 | 31.3505 | 30.3758 | 30.2211 | 30.0453 | 29.8611 | 29.6537 | 29.44 | 29.2463 | 29.08 | 28.9221 | 28.2221 | 27.7495 | 27.3821 | 30.9842 | 30.9063 | 30.8221 | 30.6484 | 30.4495 | 30.2368 | 30.0432 | 29.8768 | 29.7189 | 29.0189 | 28.5463 | 28.1789
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | WOODCOTE PRIMARY | MINIMUM HEADROOM | SU 64425 81624 | YES | YES | 0.82105 | 7.9695 | 7.9032 | 7.2337 | 7.1747 | 7.1137 | 7.0558 | 7 | 6.9474 | 6.9011 | 6.7011 | 6.3095 | 0.28316 | 6.7874 | 6.66 | 5.8137 | 5.7547 | 5.6937 | 5.6358 | 5.58 | 5.5274 | 5.4811 | 5.3084 | 4.8758 | 4.4316 | 7.0526 | 6.9305 | 6.1474 | 6.0884 | 6.0274 | 5.9695 | 5.9137 | 5.8611 | 5.8147 | 5.6284 | 5.2158 | 4.7968
|  | WOODCOTE PRIMARY | EE |  |  |  |  | 8.0126 | 7.9589 | 7.2337 | 7.1747 | 7.1137 | 7.0558 | 7 | 6.9474 | 6.9011 | 6.7326 | 6.6232 | 6.4968 | 6.8758 | 6.7768 | 5.8137 | 5.7547 | 5.6937 | 5.6358 | 5.58 | 5.5274 | 5.4811 | 5.3126 | 5.2032 | 5.0684 | 7.1211 | 7.0421 | 6.1474 | 6.0884 | 6.0274 | 5.9695 | 5.9137 | 5.8611 | 5.8147 | 5.6463 | 5.5368 | 5.4063
|  | WOODCOTE PRIMARY | HT |  |  |  |  | 7.9695 | 7.9032 | 7.8316 | 7.7084 | 7.5842 | 7.4611 | 7.3442 | 7.2337 | 7.1358 | 6.7011 | 6.3095 | 5.9137 | 6.7874 | 6.66 | 6.5316 | 6.3979 | 6.2642 | 6.1326 | 6.0063 | 5.8874 | 5.7821 | 5.3084 | 4.8758 | 4.4316 | 7.0526 | 6.9305 | 6.8063 | 6.6768 | 6.5484 | 6.4211 | 6.2989 | 6.1842 | 6.0821 | 5.6284 | 5.2158 | 4.7968
|  | WOODCOTE PRIMARY | HE |  |  |  |  | 8.0663 | 8.0305 | 7.3221 | 7.2789 | 7.2326 | 7.1874 | 7.1463 | 7.1074 | 7.0737 | 6.9611 | 6.8979 | 0.28316 | 6.9642 | 6.9253 | 5.9021 | 5.8589 | 5.8126 | 5.7674 | 5.7263 | 5.6874 | 5.6537 | 5.5411 | 5.4779 | 5.4389 | 7.1779 | 7.1411 | 6.2358 | 6.1926 | 6.1463 | 6.1011 | 6.06 | 6.0211 | 5.9874 | 5.8747 | 5.8116 | 5.7726
|  | WOODCOTE PRIMARY | CF |  |  |  |  | 8.1032 | 8.0842 | 8.0653 | 8.0453 | 8.0253 | 8.0042 | 7.9832 | 7.9632 | 7.9421 | 7.8211 | 7.6916 | 7.5853 | 7.0042 | 6.9832 | 6.9621 | 6.9389 | 6.8979 | 6.8537 | 6.8074 | 6.7611 | 6.7179 | 6.5137 | 6.3684 | 6.2474 | 7.2168 | 7.1968 | 7.1768 | 7.1558 | 7.1347 | 7.1116 | 7.0726 | 7.0284 | 6.9863 | 6.7916 | 6.6537 | 6.54
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WOODMILL LANE PRIMARY | MINIMUM HEADROOM | SU 43733 15470 | NO | YES | 0 | 25.0561 | 24.8656 | 24.6561 | 24.4392 | 24.2192 | 23.9971 | 23.7992 | 23.6182 | 23.3624 | 21.2392 | 19.4792 | 4.0698 | 22.9382 | 22.6056 | 22.1845 | 21.755 | 21.3835 | 21.0182 | 20.6845 | 20.3656 | 19.9835 | 17.6056 | 15.6266 | 13.7845 | 23.4498 | 23.2466 | 22.9624 | 22.5456 | 22.1835 | 21.8182 | 21.4824 | 21.1613 | 20.7792 | 18.4013 | 16.4224 | 14.5792
|  | WOODMILL LANE PRIMARY | EE |  |  |  |  | 25.1603 | 25.0108 | 24.8403 | 24.6603 | 24.4677 | 24.2792 | 24.1066 | 23.9382 | 23.7887 | 22.414 | 21.0224 | 19.7666 | 23.1266 | 22.8919 | 22.5729 | 22.2382 | 21.8256 | 21.3992 | 21.1066 | 20.8277 | 20.5813 | 18.9045 | 17.335 | 15.9098 | 23.5656 | 23.4035 | 23.2213 | 23.0129 | 22.614 | 22.2013 | 21.9077 | 21.6266 | 21.3771 | 19.7003 | 18.1308 | 16.7045
|  | WOODMILL LANE PRIMARY | HT |  |  |  |  | 25.0561 | 24.8656 | 24.6561 | 24.4392 | 24.2192 | 23.9971 | 23.7992 | 23.6182 | 23.3624 | 21.2392 | 19.4792 | 17.8498 | 22.9382 | 22.6056 | 22.1845 | 21.755 | 21.3835 | 21.0182 | 20.6845 | 20.3656 | 19.9835 | 17.6056 | 15.6266 | 13.7845 | 23.4498 | 23.2466 | 22.9624 | 22.5456 | 22.1835 | 21.8182 | 21.4824 | 21.1613 | 20.7792 | 18.4013 | 16.4224 | 14.5792
|  | WOODMILL LANE PRIMARY | HE |  |  |  |  | 25.2803 | 25.1645 | 25.0382 | 24.9003 | 24.7413 | 24.5866 | 24.4498 | 24.3224 | 24.2119 | 23.8003 | 22.8624 | 4.0698 | 23.254 | 23.135 | 23.0013 | 22.7613 | 22.4392 | 22.0877 | 21.8835 | 21.6919 | 21.5235 | 20.4782 | 19.375 | 18.3371 | 23.695 | 23.575 | 23.4413 | 23.2908 | 23.1192 | 22.8677 | 22.6677 | 22.4792 | 22.315 | 21.274 | 20.1708 | 19.1329
|  | WOODMILL LANE PRIMARY | CF |  |  |  |  | 25.3719 | 25.3066 | 25.2382 | 25.1677 | 25.094 | 25.0203 | 24.9466 | 24.8729 | 24.7961 | 24.4477 | 24.2466 | 23.935 | 23.3487 | 23.2813 | 23.2098 | 23.1371 | 23.0613 | 22.9813 | 22.8508 | 22.7213 | 22.5919 | 21.9024 | 21.2066 | 20.5371 | 23.7908 | 23.7224 | 23.6508 | 23.5771 | 23.5003 | 23.4235 | 23.3435 | 23.2624 | 23.1813 | 22.6845 | 22.0056 | 21.3329
COWLEY GSP | YARNTON BSP | WOODSTOCK PRIMARY | MINIMUM HEADROOM | SP 44795 17462 | NO | YES | 0.012632 | 17.8164 | 17.5048 | 17.1596 | 16.6943 | 16.1848 | 15.6775 | 15.2638 | 15.0627 | 14.8733 | 13.9827 | 12.9175 | 0.98905 | 14.7217 | 14.3764 | 13.9943 | 13.4691 | 12.8933 | 12.3196 | 11.8533 | 11.6354 | 11.4312 | 10.4575 | 9.2564 | 7.8333 | 15.2238 | 14.8785 | 14.4964 | 13.9722 | 13.3975 | 12.8248 | 12.3596 | 12.1427 | 11.9375 | 10.9648 | 9.7648 | 8.3438
|  | WOODSTOCK PRIMARY | EE |  |  |  |  | 17.9638 | 17.6985 | 17.4006 | 16.9775 | 16.5143 | 16.0564 | 15.6764 | 15.4985 | 15.3354 | 14.6575 | 13.8543 | 12.8775 | 14.8827 | 14.5869 | 14.2575 | 13.7785 | 13.2533 | 12.7333 | 12.3027 | 12.1133 | 11.9375 | 11.1996 | 10.2922 | 9.1691 | 15.3848 | 15.0901 | 14.7596 | 14.2817 | 13.7564 | 13.2375 | 12.808 | 12.6175 | 12.4417 | 11.7038 | 10.7975 | 9.6754
|  | WOODSTOCK PRIMARY | HT |  |  |  |  | 17.8164 | 17.5048 | 17.1596 | 16.6943 | 16.1848 | 15.6775 | 15.2638 | 15.0627 | 14.8733 | 13.9827 | 12.9175 | 11.6743 | 14.7217 | 14.3764 | 13.9943 | 13.4691 | 12.8933 | 12.3196 | 11.8533 | 11.6354 | 11.4312 | 10.4575 | 9.2564 | 7.8333 | 15.2238 | 14.8785 | 14.4964 | 13.9722 | 13.3975 | 12.8248 | 12.3596 | 12.1427 | 11.9375 | 10.9648 | 9.7648 | 8.3438
|  | WOODSTOCK PRIMARY | HE |  |  |  |  | 18.1659 | 17.9617 | 17.7259 | 17.3585 | 16.9459 | 16.5364 | 16.2059 | 16.0817 | 15.9691 | 15.5364 | 14.9543 | 0.98905 | 15.1027 | 14.8754 | 14.6112 | 14.1933 | 13.7227 | 13.2554 | 12.8806 | 12.7469 | 12.628 | 12.1575 | 11.4943 | 10.6059 | 15.6048 | 15.3785 | 15.1143 | 14.6964 | 14.228 | 13.7596 | 13.3859 | 13.2533 | 13.1333 | 12.6638 | 12.0006 | 11.1143
|  | WOODSTOCK PRIMARY | CF |  |  |  |  | 17.8448 | 17.7996 | 18.1554 | 17.9764 | 17.788 | 17.5817 | 17.4069 | 17.328 | 17.2491 | 16.8775 | 16.5238 | 16.0501 | 15.2901 | 15.1691 | 15.0933 | 14.8901 | 14.6754 | 14.4385 | 14.2406 | 14.1554 | 14.0701 | 13.6669 | 13.2669 | 12.7154 | 15.7785 | 15.6575 | 15.5964 | 15.3922 | 15.1775 | 14.9427 | 14.7438 | 14.6585 | 14.5733 | 14.1712 | 13.7712 | 13.2217
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON PRIMARY | MINIMUM HEADROOM | SU 44145 11242 | NO | YES | 0 | 32.3653 | 32.2568 | 32.1411 | 32.0011 | 31.7968 | 31.5937 | 31.4116 | 31.2368 | 31.0421 | 29.8937 | 28.9411 | 15.9642 | 30.1589 | 29.9516 | 29.7053 | 29.4568 | 29.2389 | 29.0221 | 28.8274 | 28.6389 | 28.4253 | 27.1411 | 26.0695 | 25.0811 | 31.4832 | 31.3684 | 31.2358 | 30.9947 | 30.7768 | 30.5589 | 30.3642 | 30.1758 | 29.9632 | 28.6789 | 27.6063 | 26.6179
|  | WOOLSTON PRIMARY | EE |  |  |  |  | 32.4274 | 32.3379 | 32.2421 | 32.1411 | 32.0358 | 31.8253 | 31.6663 | 31.5137 | 31.3768 | 30.5537 | 29.8084 | 29.1421 | 30.2989 | 30.1316 | 29.9368 | 29.7379 | 29.5042 | 29.2653 | 29.0947 | 28.9326 | 28.7863 | 27.8705 | 27.0305 | 26.2737 | 31.5495 | 31.4558 | 31.3537 | 31.2463 | 31.0421 | 30.8021 | 30.6326 | 30.4695 | 30.3232 | 29.4084 | 28.5674 | 27.8105
|  | WOOLSTON PRIMARY | HT |  |  |  |  | 32.3653 | 32.2568 | 32.1411 | 32.0011 | 31.7968 | 31.5937 | 31.4116 | 31.2368 | 31.0421 | 29.8937 | 28.9411 | 28.0663 | 30.1589 | 29.9516 | 29.7053 | 29.4568 | 29.2389 | 29.0221 | 28.8274 | 28.6389 | 28.4253 | 27.1411 | 26.0695 | 25.0811 | 31.4832 | 31.3684 | 31.2358 | 30.9947 | 30.7768 | 30.5589 | 30.3642 | 30.1758 | 29.9632 | 28.6789 | 27.6063 | 26.6179
|  | WOOLSTON PRIMARY | HE |  |  |  |  | 32.5032 | 32.4358 | 32.3611 | 32.28 | 32.1937 | 32.1116 | 32.0337 | 31.9621 | 31.8979 | 31.3853 | 30.8747 | 15.9642 | 30.4768 | 30.3653 | 30.2221 | 30.0726 | 29.8863 | 29.6937 | 29.5705 | 29.4558 | 29.3568 | 28.7905 | 28.2116 | 27.68 | 31.6326 | 31.5621 | 31.4832 | 31.3979 | 31.3053 | 31.2158 | 31.1084 | 30.9926 | 30.8947 | 30.3284 | 29.7495 | 29.2168
|  | WOOLSTON PRIMARY | CF |  |  |  |  | 32.5589 | 32.5211 | 32.4811 | 32.44 | 32.3979 | 32.3547 | 32.3116 | 32.2695 | 32.2274 | 32.04 | 31.7611 | 31.4484 | 30.5716 | 30.5011 | 30.4295 | 30.3558 | 30.2811 | 30.2063 | 30.1232 | 30.0453 | 29.9663 | 29.5705 | 29.1884 | 28.8274 | 31.6905 | 31.6505 | 31.6084 | 31.5653 | 31.5211 | 31.4758 | 31.4305 | 31.3863 | 31.3411 | 31.1084 | 30.7253 | 30.3653
MINETY GSP | SWINDON BSP | WOOTTON BASSETT PRIMARY | MINIMUM HEADROOM | SU 07587 81123 | NO | YES | 0.15789 | 23.5026 | 23.0447 | 22.5089 | 21.5742 | 21.2774 | 20.1058 | 18.8868 | 17.6111 | 22.0637 | 18.6616 | 15.9963 | 0.25421 | 22.5363 | 22.0079 | 21.39 | 20.3268 | 19.9732 | 18.6342 | 17.2384 | 15.7753 | 21.4205 | 17.6637 | 14.7616 | 12.0268 | 23.1879 | 22.6889 | 22.0711 | 21.0068 | 20.6437 | 19.2942 | 17.8847 | 16.4068 | 21.2416 | 17.3984 | 14.4089 | 11.6374
|  | WOOTTON BASSETT PRIMARY | EE |  |  |  |  | 23.8079 | 23.4426 | 23.0384 | 22.3995 | 21.2774 | 20.1058 | 18.8868 | 17.6111 | 23.2026 | 20.0721 | 19.9795 | 18.0468 | 22.8963 | 22.4774 | 22.01 | 21.2574 | 19.9732 | 18.6342 | 17.2384 | 15.7753 | 22.7237 | 19.3037 | 20.2879 | 18.1026 | 23.5037 | 23.1279 | 22.6911 | 21.9363 | 20.6437 | 19.2942 | 17.8847 | 16.4068 | 22.5184 | 18.9932 | 20.2942 | 18.0711
|  | WOOTTON BASSETT PRIMARY | HT |  |  |  |  | 23.5026 | 23.0447 | 22.5089 | 21.5742 | 26.8026 | 25.2142 | 23.9868 | 22.9542 | 22.0637 | 18.6616 | 15.9963 | 13.5805 | 22.5363 | 22.0079 | 21.39 | 20.3268 | 26.8458 | 25.0132 | 23.6079 | 22.4342 | 21.4321 | 17.6637 | 14.7616 | 12.0268 | 23.1879 | 22.6889 | 22.0711 | 21.0068 | 26.6963 | 24.8553 | 23.4405 | 22.2553 | 21.2416 | 17.3984 | 14.4089 | 11.6374
|  | WOOTTON BASSETT PRIMARY | HE |  |  |  |  | 24.2142 | 23.9784 | 23.6953 | 23.1942 | 22.1953 | 21.1395 | 20.0111 | 18.8963 | 24.6858 | 22.3584 | 20.9174 | 0.25421 | 23.3763 | 23.1089 | 22.7837 | 22.1574 | 20.9742 | 19.7521 | 18.4416 | 17.1447 | 24.3026 | 21.6816 | 20.0679 | 18.3847 | 23.8584 | 23.6616 | 23.39 | 22.8405 | 21.6489 | 20.4216 | 19.1037 | 17.8005 | 24.1311 | 21.4658 | 19.8184 | 18.1037
|  | WOOTTON BASSETT PRIMARY | CF |  |  |  |  | 24.4489 | 24.3132 | 24.1742 | 24.0311 | 23.8563 | 23.6742 | 23.4258 | 23.1058 | 22.5826 | 26.1426 | 25.23 | 24.2984 | 23.6437 | 23.4868 | 23.3247 | 23.1605 | 22.9605 | 22.7489 | 22.4468 | 22.0405 | 21.4205 | 25.9605 | 24.9363 | 23.8763 | 24.0511 | 23.9426 | 23.8311 | 23.7153 | 23.5532 | 23.3637 | 23.1058 | 22.7121 | 22.0879 | 25.7921 | 24.7489 | 23.6689
COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD PRIMARY | MINIMUM HEADROOM | SU 49244 98269 | NO | YES | 0 | 16.9253 | 16.22 | 15.5337 | 14.7126 | 13.4463 | 11.6358 | 9.6411 | 7.6916 | 5.7811 | -3.5989 | -10.9916 | -26.42 | 12.5632 | 11.4716 | 10.4484 | 9.1484 | 7.6389 | 5.5463 | 3.22 | 0.94421 | -1.2916 | -12.1895 | -20.6674 | -23.7463 | 13.6095 | 12.5189 | 11.4968 | 10.1979 | 8.6874 | 6.5937 | 4.2695 | 1.9916 | -0.24526 | -11.1547 | -19.6537 | -22.7411
|  | WOOTTON ROAD PRIMARY | EE |  |  |  |  | 17.2705 | 16.6684 | 16.0842 | 15.3663 | 14.3926 | 12.7126 | 10.8116 | 8.9305 | 7.0947 | -1.8074 | -8.4821 | -10.4989 | 13.0484 | 12.1011 | 11.2211 | 10.0589 | 8.6789 | 6.7274 | 4.5063 | 2.3084 | 0.15895 | -10.2211 | -17.8811 | -20.1442 | 14.0947 | 13.1484 | 12.2684 | 11.1084 | 9.7263 | 7.7726 | 5.5495 | 3.3505 | 1.1989 | -9.2063 | -16.9021 | -19.1758
|  | WOOTTON ROAD PRIMARY | HT |  |  |  |  | 16.9253 | 16.22 | 15.5337 | 14.7126 | 13.4463 | 11.6358 | 9.6411 | 7.6916 | 5.7811 | -3.5989 | -10.9916 | -13.7358 | 12.5632 | 11.4716 | 10.4484 | 9.1484 | 7.6389 | 5.5463 | 3.22 | 0.94421 | -1.2916 | -12.1895 | -20.6674 | -23.7463 | 13.6095 | 12.5189 | 11.4968 | 10.1979 | 8.6874 | 6.5937 | 4.2695 | 1.9916 | -0.24526 | -11.1547 | -19.6537 | -22.7411
|  | WOOTTON ROAD PRIMARY | HE |  |  |  |  | 17.7274 | 17.2674 | 16.8232 | 16.2326 | 15.5221 | 14.1358 | 12.3884 | 10.6674 | 8.9884 | 0.89368 | -5.0158 | -26.42 | 13.6947 | 12.9484 | 12.2611 | 11.28 | 10.0705 | 8.2895 | 6.2358 | 4.2084 | 2.2274 | -7.3284 | -14.1947 | -15.7884 | 14.74 | 13.9947 | 13.3084 | 12.3284 | 11.1189 | 9.3368 | 7.2832 | 5.2579 | 3.2779 | -6.2789 | -13.1453 | -14.7495
|  | WOOTTON ROAD PRIMARY | CF |  |  |  |  | 18.0653 | 17.8516 | 17.6253 | 17.3453 | 17.02 | 16.5568 | 15.9989 | 15.2053 | 14.1926 | 8.9011 | 5.1958 | 4.3379 | 14.2537 | 13.8579 | 13.5042 | 13.0368 | 12.4853 | 11.6368 | 10.5832 | 9.4579 | 8.2632 | 1.9968 | -2.4084 | -3.3979 | 15.2979 | 14.9032 | 14.5495 | 14.0832 | 13.5316 | 12.6821 | 11.6295 | 10.5063 | 9.3116 | 3.0505 | -1.3547 | -2.3516
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | WRECCLESHAM PRIMARY | MINIMUM HEADROOM | SU 82093 44312 | NO | YES | 0 | 33.2084 | 32.7874 | 32.3758 | 31.9526 | 31.4968 | 31.0474 | 30.6179 | 30.2053 | 29.78 | 26.6579 | 24.3158 | 6.1737 | 29.94 | 29.3147 | 28.7421 | 28.1537 | 27.5453 | 26.96 | 26.3632 | 25.7705 | 25.1968 | 21.8011 | 19.3 | 17.8011 | 29.1989 | 28.9 | 28.5832 | 28.2568 | 27.8958 | 27.5316 | 26.9558 | 26.3516 | 25.7663 | 22.3011 | 19.72 | 18.1884
|  | WRECCLESHAM PRIMARY | EE |  |  |  |  | 33.4695 | 33.14 | 32.8021 | 32.4537 | 32.0768 | 31.7063 | 31.3516 | 30.9842 | 30.6295 | 28.7716 | 26.7705 | 25.2411 | 30.3305 | 29.8516 | 29.3811 | 28.9021 | 28.4053 | 27.9326 | 27.4842 | 26.9905 | 26.4979 | 24.2211 | 22.1305 | 20.4505 | 29.3842 | 29.1421 | 28.8832 | 28.6147 | 28.3116 | 28.0074 | 27.7147 | 27.4295 | 27.0526 | 24.6789 | 22.4789 | 20.7632
|  | WRECCLESHAM PRIMARY | HT |  |  |  |  | 33.2084 | 32.7874 | 32.3758 | 31.9526 | 31.4968 | 31.0474 | 30.6179 | 30.2053 | 29.78 | 26.6579 | 24.3158 | 22.9168 | 29.94 | 29.3147 | 28.7421 | 28.1537 | 27.5453 | 26.96 | 26.3632 | 25.7705 | 25.1968 | 21.8011 | 19.3 | 17.8011 | 29.1989 | 28.9 | 28.5832 | 28.2568 | 27.8958 | 27.5316 | 26.9558 | 26.3516 | 25.7663 | 22.3011 | 19.72 | 18.1884
|  | WRECCLESHAM PRIMARY | HE |  |  |  |  | 33.8116 | 33.5905 | 33.3547 | 33.1084 | 32.8274 | 32.5684 | 32.3211 | 32.0632 | 31.8242 | 30.8358 | 29.9589 | 6.1737 | 30.7516 | 30.5095 | 30.2105 | 29.8779 | 29.5221 | 29.1989 | 28.8958 | 28.5432 | 28.2042 | 26.6947 | 25.3979 | 24.2389 | 29.6232 | 29.4579 | 29.2726 | 29.0758 | 28.8442 | 28.6242 | 28.4137 | 28.2147 | 28.0389 | 27.24 | 25.9126 | 24.7253
|  | WRECCLESHAM PRIMARY | CF |  |  |  |  | 34.0189 | 33.9042 | 33.7863 | 33.6663 | 33.5305 | 33.3947 | 33.2547 | 33.1179 | 32.9842 | 32.3316 | 31.8263 | 31.4158 | 30.9516 | 30.8421 | 30.7295 | 30.5989 | 30.4379 | 30.2537 | 30.06 | 29.8695 | 29.6821 | 28.7253 | 27.8337 | 27.0568 | 29.7842 | 29.6989 | 29.6116 | 29.5211 | 29.4158 | 29.3116 | 29.2063 | 29.1032 | 29.0021 | 28.5379 | 28.2684 | 27.6095
MINETY GSP | TOOTHILL BSP | WROUGHTON PRIMARY | MINIMUM HEADROOM | SU 14446 81504 | NO | YES | 0 | 26.1413 | 25.2192 | 24.2529 | 23.2624 | 22.3087 | 21.4192 | 20.8898 | 20.5098 | 20.1413 | 18.7477 | 17.3498 | 2.1687 | 22.1992 | 21.1413 | 20.035 | 18.8992 | 17.8087 | 16.7982 | 16.2045 | 15.7856 | 15.3782 | 13.855 | 12.3129 | 10.8877 | 22.9477 | 21.8887 | 20.7813 | 19.6445 | 18.554 | 17.5392 | 16.9435 | 16.5213 | 16.1108 | 14.5687 | 13.0045 | 11.5698
|  | WROUGHTON PRIMARY | EE |  |  |  |  | 26.3119 | 25.4403 | 24.5256 | 23.5813 | 22.674 | 21.834 | 21.3392 | 20.9813 | 20.6392 | 19.4624 | 18.314 | 17.2992 | 22.3845 | 21.3824 | 20.3308 | 19.2456 | 18.2066 | 17.2477 | 16.694 | 16.2971 | 15.9224 | 14.6498 | 13.3982 | 12.254 | 23.1329 | 22.1298 | 21.0771 | 19.9908 | 18.9498 | 17.9877 | 17.4308 | 17.0308 | 16.6519 | 15.3529 | 14.0698 | 12.915
|  | WROUGHTON PRIMARY | HT |  |  |  |  | 26.1413 | 25.2192 | 24.2529 | 23.2624 | 22.3087 | 21.4192 | 20.8898 | 20.5098 | 20.1413 | 18.7477 | 17.3498 | 16.0824 | 22.1992 | 21.1413 | 20.035 | 18.8992 | 17.8087 | 16.7982 | 16.2045 | 15.7856 | 15.3782 | 13.855 | 12.3129 | 10.8877 | 22.9477 | 21.8887 | 20.7813 | 19.6445 | 18.554 | 17.5392 | 16.9435 | 16.5213 | 16.1108 | 14.5687 | 13.0045 | 11.5698
|  | WROUGHTON PRIMARY | HE |  |  |  |  | 26.5382 | 25.7392 | 24.8929 | 24.014 | 23.1635 | 22.3877 | 21.9571 | 21.6624 | 21.3866 | 20.5371 | 19.7213 | 2.1687 | 22.6319 | 21.7066 | 20.7277 | 19.714 | 18.7361 | 17.8445 | 17.3582 | 17.0298 | 16.7213 | 15.7866 | 14.8687 | 13.9771 | 23.3792 | 22.454 | 21.4761 | 20.4603 | 19.4813 | 18.5877 | 18.0992 | 17.7698 | 17.4592 | 16.514 | 15.5856 | 14.6877
|  | WROUGHTON PRIMARY | CF |  |  |  |  | 26.8077 | 26.6287 | 26.2435 | 25.8624 | 25.5056 | 25.1424 | 24.9203 | 24.755 | 24.5845 | 24.0119 | 23.5445 | 23.0571 | 23.0235 | 22.7308 | 22.2866 | 21.8456 | 21.4361 | 21.0192 | 20.7677 | 20.5835 | 20.394 | 19.7624 | 19.2392 | 18.6856 | 23.7719 | 23.4792 | 23.034 | 22.594 | 22.1835 | 21.7656 | 21.5129 | 21.3277 | 21.1371 | 20.5024 | 19.974 | 19.414
AMERSHAM GSP | LOUDWATER BSP | WYCOMBE MARSH PRIMARY | MINIMUM HEADROOM | SU 88582 91845 | NO | YES | 0 | 26.8295 | 26.6158 | 26.3895 | 26.1537 | 25.9095 | 25.6642 | 25.4474 | 25.0853 | 24.7242 | 23.0453 | 21.5284 | 1.6526 | 25.7611 | 25.0147 | 24.5011 | 24.0905 | 23.6821 | 23.2653 | 22.8705 | 22.4653 | 22.0716 | 20.2284 | 18.5432 | 16.9905 | 26.4263 | 25.9295 | 25.4179 | 25.0074 | 24.6 | 24.1832 | 23.7884 | 23.3842 | 22.9916 | 21.1505 | 19.4684 | 17.9189
|  | WYCOMBE MARSH PRIMARY | EE |  |  |  |  | 26.9589 | 26.7842 | 26.5979 | 26.4032 | 26.2 | 26.0042 | 25.8179 | 25.6368 | 25.4747 | 24.2274 | 23.0642 | 22.0295 | 26.0337 | 25.3779 | 24.9463 | 24.6158 | 24.2832 | 23.9632 | 23.6442 | 23.2989 | 22.9705 | 21.5189 | 20.2242 | 19.0579 | 26.5642 | 26.2926 | 25.8621 | 25.5316 | 25.2 | 24.88 | 24.5611 | 24.2168 | 23.8884 | 22.44 | 21.1463 | 19.9832
|  | WYCOMBE MARSH PRIMARY | HT |  |  |  |  | 26.8295 | 26.6158 | 26.3895 | 26.1537 | 25.9095 | 25.6642 | 25.4474 | 25.0853 | 24.7242 | 23.0453 | 21.5284 | 20.1432 | 25.7611 | 25.0147 | 24.5011 | 24.0905 | 23.6821 | 23.2653 | 22.8705 | 22.4653 | 22.0716 | 20.2284 | 18.5432 | 16.9905 | 26.4263 | 25.9295 | 25.4179 | 25.0074 | 24.6 | 24.1832 | 23.7884 | 23.3842 | 22.9916 | 21.1505 | 19.4684 | 17.9189
|  | WYCOMBE MARSH PRIMARY | HE |  |  |  |  | 27.1116 | 26.9821 | 26.84 | 26.6863 | 26.5232 | 26.3663 | 26.2189 | 26.0811 | 25.9621 | 25.5579 | 24.9021 | 1.6526 | 26.1958 | 25.8389 | 25.5116 | 25.2789 | 25.04 | 24.8095 | 24.5811 | 24.3295 | 24.0937 | 23.0979 | 22.2379 | 21.4937 | 26.7284 | 26.5747 | 26.4232 | 26.1937 | 25.9547 | 25.7253 | 25.4968 | 25.2453 | 25.0105 | 24.0158 | 23.1568 | 22.4158
|  | WYCOMBE MARSH PRIMARY | CF |  |  |  |  | 27.2211 | 27.1505 | 27.0768 | 27 | 26.9211 | 26.8411 | 26.7611 | 26.6832 | 26.6042 | 26.2547 | 26.08 | 25.9821 | 26.3158 | 26.2347 | 26.1568 | 26.0768 | 25.9832 | 25.8453 | 25.7021 | 25.5421 | 25.3758 | 24.5726 | 23.9474 | 23.4137 | 26.8505 | 26.7674 | 26.6884 | 26.6084 | 26.5253 | 26.4421 | 26.3589 | 26.2768 | 26.1926 | 25.4874 | 24.8642 | 24.3316
LOVEDEAN GSP | WYMERING BSP | WYMERING PRIMARY | MINIMUM HEADROOM | SU 64974 05375 | NO | YES | 0.063158 | 77.5168 | 77.2884 | 77.0737 | 76.8547 | 76.6253 | 83.1358 | 82.0211 | 80.9453 | 80.2832 | 77.1379 | 73.8937 | 3.8042 | 74.0811 | 73.8232 | 73.5842 | 73.3411 | 73.0905 | 81.2095 | 79.9937 | 78.8168 | 78.1095 | 74.7926 | 71.2716 | 68.1989 | 76.3874 | 76.1389 | 75.9084 | 75.6737 | 75.4295 | 82.7621 | 81.5147 | 80.3095 | 79.5863 | 76.2105 | 72.5821 | 69.3516
|  | WYMERING PRIMARY | EE |  |  |  |  | 84.0326 | 83.7316 | 87.2284 | 86.6863 | 85.6295 | 84.5842 | 83.5568 | 82.5442 | 81.5684 | 79.0684 | 76.56 | 74.3558 | 86.7579 | 86.2168 | 85.6611 | 85.0895 | 83.9347 | 82.7947 | 81.6737 | 80.5674 | 79.5 | 76.8632 | 74.2053 | 71.78 | 83.1811 | 82.8811 | 82.5632 | 86.7316 | 85.5474 | 84.3789 | 83.2284 | 82.0926 | 80.9958 | 78.2842 | 75.5484 | 73.0526
|  | WYMERING PRIMARY | HT |  |  |  |  | 83.8326 | 87.2105 | 86.5611 | 85.4716 | 84.3011 | 83.1358 | 82.0211 | 80.9453 | 80.2832 | 77.1379 | 73.8937 | 71.0305 | 86.3074 | 85.6305 | 84.9442 | 83.7547 | 82.4789 | 81.2095 | 79.9937 | 78.8168 | 78.1095 | 74.7926 | 71.2716 | 68.1989 | 82.9811 | 82.6232 | 86.58 | 85.3663 | 84.0611 | 82.7621 | 81.5147 | 80.3095 | 79.5863 | 76.2105 | 72.5821 | 69.3516
|  | WYMERING PRIMARY | HE |  |  |  |  | 84.2832 | 84.06 | 83.8126 | 83.5453 | 86.9516 | 86.2211 | 85.5126 | 84.8263 | 84.1768 | 82.0568 | 80.3558 | 3.8042 | 87.34 | 86.9789 | 86.5926 | 86.1874 | 85.3695 | 84.5768 | 83.8053 | 83.0589 | 82.3505 | 80.0358 | 78.1295 | 76.4411 | 83.4316 | 83.2084 | 82.9611 | 82.6937 | 87.0137 | 86.2021 | 85.4126 | 84.6474 | 83.9211 | 81.5358 | 79.5484 | 77.8074
|  | WYMERING PRIMARY | CF |  |  |  |  | 77.5168 | 77.2884 | 77.0737 | 76.8547 | 76.6253 | 83.78 | 87.4263 | 87.0137 | 86.5853 | 84.8021 | 83.7989 | 82.7737 | 74.0811 | 73.8232 | 73.5842 | 73.3411 | 73.0905 | 86.2947 | 85.8579 | 85.4063 | 84.9389 | 82.9979 | 81.9053 | 80.7684 | 76.3874 | 76.1389 | 75.9084 | 75.6737 | 75.4295 | 82.9284 | 82.7832 | 87.0421 | 86.5621 | 84.5747 | 83.4526 | 82.2789
COWLEY GSP | YARNTON BSP | YARNTON PRIMARY | MINIMUM HEADROOM | SP 48277 12108 | NO | YES | 0 | 47.6282 | 46.9314 | 46.2093 | 45.4829 | 44.5882 | 43.8724 | 43.2187 | 42.6135 | 42.0429 | 39.5387 | 36.7566 | -21.2634 | 37.5408 | 36.7914 | 36.0156 | 35.2377 | 34.2651 | 33.4998 | 32.8019 | 32.1535 | 31.5408 | 28.8335 | 25.7398 | 21.264 | 38.8745 | 38.1261 | 37.3503 | 36.5724 | 35.6008 | 34.8366 | 34.1387 | 33.4893 | 32.8777 | 30.1682 | 27.0745 | 22.5745
|  | YARNTON PRIMARY | EE |  |  |  |  | 48.0977 | 47.5429 | 46.9608 | 46.3672 | 45.6029 | 45.0282 | 44.4766 | 43.9503 | 43.4682 | 41.7956 | 39.6619 | 36.9219 | 38.0524 | 37.4566 | 36.8335 | 36.1987 | 35.3661 | 34.7524 | 34.1651 | 33.6029 | 33.0882 | 31.4619 | 29.0851 | 25.9556 | 39.3851 | 38.7893 | 38.1672 | 37.5324 | 36.6998 | 36.0872 | 35.4987 | 34.9377 | 34.4219 | 32.8198 | 30.4419 | 27.3156
|  | YARNTON PRIMARY | HT |  |  |  |  | 47.6282 | 46.9314 | 46.2093 | 45.4829 | 44.5882 | 43.8724 | 43.2187 | 42.6135 | 42.0429 | 39.5387 | 36.7566 | 32.9608 | 37.5408 | 36.7914 | 36.0156 | 35.2377 | 34.2651 | 33.4998 | 32.8019 | 32.1535 | 31.5408 | 28.8335 | 25.7398 | 21.264 | 38.8745 | 38.1261 | 37.3503 | 36.5724 | 35.6008 | 34.8366 | 34.1387 | 33.4893 | 32.8777 | 30.1682 | 27.0745 | 22.5745
|  | YARNTON PRIMARY | HE |  |  |  |  | 48.7303 | 48.364 | 47.9703 | 47.5535 | 46.9535 | 46.5377 | 46.1429 | 45.7798 | 45.4514 | 43.9219 | 42.4735 | -21.2634 | 38.7419 | 38.3514 | 37.9314 | 37.4903 | 36.8335 | 36.3956 | 35.9766 | 35.5924 | 35.2451 | 33.424 | 31.7945 | 29.364 | 40.0735 | 39.684 | 39.264 | 38.8229 | 38.1672 | 37.7282 | 37.3103 | 36.9261 | 36.5777 | 34.7282 | 33.0966 | 30.6682
|  | YARNTON PRIMARY | CF |  |  |  |  | 48.424 | 48.304 | 48.1808 | 48.0535 | 47.9219 | 47.7872 | 47.6545 | 47.5229 | 47.3851 | 46.2187 | 45.2556 | 43.924 | 38.344 | 38.224 | 38.1008 | 37.9735 | 37.8419 | 37.7072 | 37.5756 | 37.444 | 37.304 | 36.0356 | 34.9545 | 33.4187 | 39.6766 | 39.5566 | 39.4335 | 39.3061 | 39.1745 | 39.0398 | 38.9072 | 38.7756 | 38.6366 | 37.3693 | 36.2882 | 34.7535
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | YATTENDON PRIMARY | MINIMUM HEADROOM | SU 53699 74307 | NO | YES | 0 | 17.9737 | 17.7821 | 17.5379 | 17.0758 | 16.5832 | 16.0905 | 15.8042 | 15.5832 | 15.3779 | 14.4705 | 13.4463 | -14.7842 | 14.9411 | 14.7389 | 14.4726 | 13.9253 | 13.3432 | 12.76 | 12.4358 | 12.1926 | 11.9653 | 10.9495 | 9.8053 | 8.6895 | 15.6874 | 15.4874 | 15.2253 | 14.6926 | 14.1126 | 13.5305 | 13.2063 | 12.9621 | 12.7347 | 11.7168 | 10.5695 | 9.4547
|  | YATTENDON PRIMARY | EE |  |  |  |  | 18.0926 | 17.9379 | 17.7737 | 17.4137 | 16.9716 | 16.5389 | 16.2905 | 16.0958 | 15.9242 | 15.2168 | 14.4642 | 13.7116 | 15.0674 | 14.9032 | 14.7305 | 14.3063 | 13.7811 | 13.2632 | 12.9832 | 12.7695 | 12.58 | 11.7947 | 10.9158 | 10.0653 | 15.8126 | 15.6505 | 15.4789 | 15.0663 | 14.5505 | 14.0337 | 13.7526 | 13.5389 | 13.3495 | 12.5589 | 11.6758 | 10.8253
|  | YATTENDON PRIMARY | HT |  |  |  |  | 17.9737 | 17.7821 | 17.5379 | 17.0758 | 16.5832 | 16.0905 | 15.8042 | 15.5832 | 15.3779 | 14.4705 | 13.4463 | 12.4516 | 14.9411 | 14.7389 | 14.4726 | 13.9253 | 13.3432 | 12.76 | 12.4358 | 12.1926 | 11.9653 | 10.9495 | 9.8053 | 8.6895 | 15.6874 | 15.4874 | 15.2253 | 14.6926 | 14.1126 | 13.5305 | 13.2063 | 12.9621 | 12.7347 | 11.7168 | 10.5695 | 9.4547
|  | YATTENDON PRIMARY | HE |  |  |  |  | 18.2379 | 18.1421 | 18.0263 | 17.8611 | 17.4821 | 17.1095 | 16.9211 | 16.7874 | 16.6726 | 16.24 | 15.7463 | -14.7842 | 15.2189 | 15.12 | 14.9979 | 14.8147 | 14.3589 | 13.9105 | 13.6968 | 13.5505 | 13.4263 | 12.9505 | 12.36 | 11.7705 | 15.9632 | 15.8653 | 15.7432 | 15.5642 | 15.1211 | 14.6789 | 14.4653 | 14.32 | 14.1958 | 13.7179 | 13.1274 | 12.5368
|  | YATTENDON PRIMARY | CF |  |  |  |  | 18.3337 | 18.2884 | 18.2421 | 18.1863 | 18.1263 | 17.9484 | 17.8442 | 17.7632 | 17.6811 | 17.3116 | 16.9895 | 16.6779 | 15.3168 | 15.2705 | 15.2232 | 15.1663 | 15.1032 | 14.8874 | 14.7695 | 14.68 | 14.5884 | 14.1737 | 13.7926 | 13.4084 | 16.0611 | 16.0147 | 15.9684 | 15.9105 | 15.8484 | 15.6389 | 15.5221 | 15.4347 | 15.3453 | 14.9379 | 14.56 | 14.1768
MELKSHAM GSP | CHIPPENHAM BSP | YATTON KEYNELL PRIMARY | MINIMUM HEADROOM | ST 87300 75782 | YES | YES | 0 | 6.5179 | 6.9305 | 6.7863 | 6.5463 | 5.9368 | 5.3358 | 4.6011 | 4.44 | 4.2758 | 2.0579 | -2.9411 | -28.4789 | 5.1389 | 5.1242 | 4.9726 | 4.7053 | 4.0316 | 3.3695 | 2.5505 | 2.4116 | 2.2716 | -0.10211 | -5.4958 | -6.8368 | 5.2611 | 5.1116 | 4.9579 | 4.6895 | 3.9979 | 3.3158 | 2.4768 | 2.3126 | 2.1463 | -0.50421 | -6.1695 | -7.5968
|  | YATTON KEYNELL PRIMARY | EE |  |  |  |  | 6.5653 | 7.0463 | 6.9295 | 6.8105 | 6.6295 | 6.4221 | 6.2116 | 5.9916 | 5.7653 | 2.0579 | -2.9411 | -4.2189 | 5.1884 | 5.2526 | 5.1305 | 5.0063 | 4.8347 | 4.6463 | 4.4558 | 4.2611 | 4.0632 | -0.10211 | -5.4958 | -6.8368 | 5.3484 | 5.2379 | 5.1147 | 4.9874 | 4.7979 | 4.5821 | 4.3621 | 4.1337 | 3.8989 | -0.50421 | -6.1695 | -7.5968
|  | YATTON KEYNELL PRIMARY | HT |  |  |  |  | 6.5179 | 6.9305 | 6.7863 | 6.5463 | 5.9368 | 5.3358 | 4.6011 | 4.44 | 4.2758 | 2.7284 | 0.44947 | -0.22842 | 5.1389 | 5.1242 | 4.9726 | 4.7053 | 4.0316 | 3.3695 | 2.5505 | 2.4116 | 2.2716 | 0.54737 | -1.7674 | -2.4063 | 5.2611 | 5.1116 | 4.9579 | 4.6895 | 3.9979 | 3.3158 | 2.4768 | 2.3126 | 2.1463 | 0.25053 | -2.2632 | -2.9821
|  | YATTON KEYNELL PRIMARY | HE |  |  |  |  | 6.6284 | 7.2189 | 7.1453 | 7.0695 | 6.9368 | 6.8137 | 6.6905 | 6.5695 | 6.4526 | 3.4011 | -0.48842 | -28.4789 | 5.2547 | 5.4379 | 5.3611 | 5.2811 | 5.1568 | 5.0432 | 4.9295 | 4.8189 | 4.7126 | 1.2905 | -3.1684 | -4.2768 | 5.4158 | 5.4253 | 5.3474 | 5.2674 | 5.1295 | 5.0011 | 4.8737 | 4.7484 | 4.6274 | 1.1095 | -3.4211 | -4.6
|  | YATTON KEYNELL PRIMARY | CF |  |  |  |  | 6.6705 | 7.3168 | 7.2737 | 7.2326 | 7.1589 | 7.0884 | 7.0168 | 6.9495 | 6.8884 | 6.5737 | 5.8042 | 5.0484 | 5.2979 | 5.5411 | 5.4947 | 5.4505 | 5.3821 | 5.3116 | 5.2442 | 5.18 | 5.1211 | 4.8211 | 3.9895 | 3.1789 | 5.46 | 5.5284 | 5.4821 | 5.4379 | 5.3611 | 5.2853 | 5.2105 | 5.1389 | 5.0747 | 4.7432 | 3.8695 | 3.0116
AXMINSTER GSP | YEOVIL BSP | YEOVIL PRIMARY | MINIMUM HEADROOM | ST 57690 16833 | NO | YES | 0 | 28.7453 | 28.1642 | 27.6347 | 27.0737 | 26.5305 | 26 | 25.5095 | 25.0526 | 24.62 | 22.2074 | 19.9874 | 5.2179 | 29.1495 | 28.6642 | 28.5989 | 28.0495 | 27.4716 | 26.9053 | 26.3821 | 25.8937 | 25.4295 | 22.7842 | 20.4242 | 17.7368 | 29.2221 | 28.6011 | 28.0105 | 27.4074 | 26.8284 | 26.2632 | 25.74 | 25.2495 | 24.7853 | 22.1347 | 19.6663 | 16.98
|  | YEOVIL PRIMARY | EE |  |  |  |  | 29.08 | 28.6 | 28.0958 | 27.6305 | 27.1811 | 26.8242 | 26.4074 | 26.0074 | 25.6347 | 23.7737 | 26.6821 | 24.84 | 29.3621 | 29.0463 | 28.5989 | 28.1632 | 27.7411 | 27.8021 | 27.3589 | 26.9337 | 26.5379 | 24.5053 | 29.7937 | 27.7084 | 29.4916 | 29.0684 | 28.5305 | 28.0379 | 27.5684 | 27.1589 | 26.7158 | 26.2895 | 25.8926 | 23.8547 | 30.0611 | 27.9726
|  | YEOVIL PRIMARY | HT |  |  |  |  | 28.7453 | 28.1642 | 27.6347 | 27.0737 | 26.5305 | 26 | 25.5095 | 25.0526 | 24.62 | 22.2074 | 19.9874 | 17.6063 | 29.1495 | 28.6642 | 28.6526 | 28.0495 | 27.4716 | 26.9053 | 26.3821 | 25.8937 | 25.4295 | 22.7842 | 20.4242 | 17.7368 | 29.2221 | 28.6011 | 28.0105 | 27.4074 | 26.8284 | 26.2632 | 25.74 | 25.2495 | 24.7853 | 22.1347 | 19.6663 | 16.98
|  | YEOVIL PRIMARY | HE |  |  |  |  | 29.4726 | 29.1811 | 28.8074 | 28.4674 | 28.1337 | 27.8179 | 27.5221 | 27.2389 | 26.9884 | 25.7263 | 27.3674 | 5.2179 | 29.6432 | 29.4126 | 29.1589 | 28.9063 | 28.6126 | 28.3126 | 28.0295 | 27.7621 | 27.5242 | 26.2926 | 25.8084 | 24.2674 | 29.8232 | 29.5579 | 29.26 | 28.9368 | 28.5884 | 28.2611 | 27.9526 | 27.6568 | 27.3947 | 26.0389 | 26.3684 | 25.7158
|  | YEOVIL PRIMARY | CF |  |  |  |  | 29.7042 | 29.5695 | 29.4274 | 29.2642 | 29.0284 | 28.8032 | 28.6021 | 28.4137 | 28.2253 | 27.2463 | 26.4768 | 25.6221 | 29.8547 | 29.7284 | 29.5958 | 29.4526 | 29.3021 | 29.1537 | 29.0147 | 28.88 | 28.7074 | 27.8042 | 27.0453 | 26.1042 | 30.0768 | 29.9316 | 29.78 | 29.6116 | 29.4347 | 29.2558 | 29.0779 | 28.8789 | 28.68 | 27.6337 | 26.7937 | 25.8253
AXMINSTER GSP | YEOVIL BSP | YETMINSTER PRIMARY | MINIMUM HEADROOM | ST 60294 10206 | NO | YES | 0.21053 | 8.8821 | 8.6 | 8.3168 | 7.6463 | 6.5021 | 5.1537 | 3.4853 | 3.2316 | 2.9779 | 0.17474 | -4.3811 | -5.6011 | 6.8747 | 6.5726 | 6.2705 | 5.5158 | 4.2537 | 2.7411 | 0.84947 | 0.62316 | 0.39789 | -2.4768 | -7.3779 | -8.6084 | 7.3726 | 7.0695 | 6.7663 | 6.0105 | 4.6968 | 3.1611 | 1.2453 | 0.99158 | 0.73789 | -2.3295 | -7.4537 | -8.7716
|  | YETMINSTER PRIMARY | EE |  |  |  |  | 9.0716 | 8.8432 | 8.6137 | 8.3768 | 8.06 | 7.7189 | 7.3747 | 7.0253 | 6.6758 | 3.8968 | -2.5084 | -5.1874 | 7.08 | 6.8379 | 6.5947 | 6.3453 | 6.0368 | 5.7105 | 5.3874 | 5.0611 | 4.74 | 2.0211 | -4.9242 | -7.8695 | 7.5779 | 7.3337 | 7.0895 | 6.8368 | 6.5074 | 6.1505 | 5.7947 | 5.4316 | 5.0684 | 2.0526 | -5.2032 | -8.2442
|  | YETMINSTER PRIMARY | HT |  |  |  |  | 8.8821 | 8.6 | 8.3168 | 7.6463 | 6.5021 | 5.1537 | 3.4853 | 3.2316 | 2.9779 | 0.17474 | -4.3811 | -5.6011 | 6.8747 | 6.5726 | 6.2705 | 5.5158 | 4.2537 | 2.7411 | 0.84947 | 0.62316 | 0.39789 | -2.4768 | -7.3779 | -8.6084 | 7.3726 | 7.0695 | 6.7663 | 6.0105 | 4.6968 | 3.1611 | 1.2453 | 0.99158 | 0.73789 | -2.3295 | -7.4537 | -8.7716
|  | YETMINSTER PRIMARY | HE |  |  |  |  | 9.3232 | 9.18 | 9.0326 | 8.8758 | 8.6474 | 8.4358 | 8.2253 | 8.0211 | 7.8284 | 6.18 | 1.7979 | -4.8316 | 7.3537 | 7.2011 | 7.0463 | 6.88 | 6.6589 | 6.4526 | 6.2516 | 6.0558 | 5.8737 | 4.1884 | -0.78105 | -3.2284 | 7.8516 | 7.6989 | 7.5432 | 7.3768 | 7.1389 | 6.9189 | 6.7011 | 6.4895 | 6.2905 | 4.4642 | -0.59368 | -3.12
|  | YETMINSTER PRIMARY | CF |  |  |  |  | 9.4684 | 9.3884 | 9.3063 | 9.2232 | 9.1042 | 8.9874 | 8.8716 | 8.7568 | 8.6516 | 7.5084 | 6.2979 | 4.9253 | 7.5084 | 7.4232 | 7.3347 | 7.2442 | 7.1274 | 7.0116 | 6.8968 | 6.7832 | 6.6768 | 5.4379 | 4.1274 | 2.6179 | 8.0063 | 7.9211 | 7.8326 | 7.7421 | 7.6168 | 7.4937 | 7.3716 | 7.2505 | 7.1389 | 5.8611 | 4.4758 | 2.9126
IVER 66KV GSP |  | YIEWSLEY PRIMARY | MINIMUM HEADROOM | TQ 05643 80961 | NO | NO | 0.36842 | 73.3416 | 72.8205 | 71.8016 | 70.5868 | 69.2616 | 67.9595 | 66.5847 | 65.2584 | 64.1984 | 58.2542 | 52.97 | 8.9163 | 60.9889 | 59.7763 | 58.39 | 56.8068 | 55.0626 | 53.3995 | 51.8353 | 50.3226 | 49.1668 | 42.5763 | 36.5984 | 30.9974 | 63.5395 | 62.3321 | 60.9184 | 59.3037 | 57.5237 | 55.8268 | 54.2311 | 52.6847 | 51.5405 | 44.9037 | 38.9237 | 33.3205
|  | YIEWSLEY PRIMARY | EE |  |  |  |  | 73.6363 | 73.2037 | 72.7437 | 71.8711 | 70.8511 | 69.8574 | 68.8921 | 67.9447 | 66.9395 | 62.7468 | 58.8321 | 55.2584 | 61.6795 | 60.7574 | 59.7068 | 58.5037 | 57.1879 | 55.9037 | 54.6532 | 53.4205 | 52.2742 | 47.6174 | 43.2163 | 39.1384 | 64.2132 | 63.3121 | 62.2637 | 61.0374 | 59.6953 | 58.3858 | 57.1111 | 55.8532 | 54.6837 | 49.9763 | 45.5426 | 41.4647
|  | YIEWSLEY PRIMARY | HT |  |  |  |  | 73.3416 | 72.8205 | 71.8016 | 70.5868 | 69.2616 | 67.9595 | 66.5847 | 65.2584 | 64.1984 | 58.2542 | 52.97 | 48.0489 | 60.9889 | 59.7763 | 58.39 | 56.8068 | 55.0626 | 53.3995 | 51.8353 | 50.3226 | 49.1668 | 42.5763 | 36.5984 | 30.9974 | 63.5395 | 62.3321 | 60.9184 | 59.3037 | 57.5237 | 55.8268 | 54.2311 | 52.6847 | 51.5405 | 44.9037 | 38.9237 | 33.3205
|  | YIEWSLEY PRIMARY | HE |  |  |  |  | 73.9984 | 73.6732 | 73.3132 | 72.9258 | 72.2721 | 71.45 | 70.6605 | 69.8963 | 69.2026 | 65.9511 | 62.8426 | 8.9163 | 62.5237 | 61.8574 | 61.0532 | 60.0858 | 58.9889 | 57.9216 | 56.8921 | 55.8889 | 54.9679 | 51.0353 | 47.39 | 44.3974 | 64.7879 | 64.3837 | 63.5995 | 62.6479 | 61.5289 | 60.4405 | 59.3911 | 58.3668 | 57.4258 | 53.4016 | 49.6121 | 46.6184
|  | YIEWSLEY PRIMARY | CF |  |  |  |  | 74.2647 | 74.0805 | 73.8889 | 73.6921 | 73.4879 | 73.2784 | 73.0742 | 72.7626 | 72.3153 | 70.1984 | 68.5879 | 67.0037 | 63.0721 | 62.6868 | 62.2553 | 61.7721 | 61.2458 | 60.6953 | 60.1363 | 59.5553 | 58.9679 | 56.1553 | 53.9868 | 52.1037 | 65.0542 | 64.87 | 64.6784 | 64.3037 | 63.7911 | 63.2553 | 62.6953 | 62.1026 | 61.5026 | 58.63 | 56.4068 | 54.4732
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ZETLAND ROAD PRIMARY | MINIMUM HEADROOM | SU 60592 00043 | NO | YES | 0 | 25.1253 | 24.7421 | 24.3358 | 23.9116 | 23.7674 | 23.3221 | 22.8579 | 22.2568 | 21.6853 | 18.8863 | 15.9589 | -17.4642 | 19.8947 | 19.1168 | 18.2305 | 17.2484 | 16.8168 | 15.9537 | 15.1084 | 14.4674 | 13.8537 | 10.8084 | 7.5579 | 4.4768 | 20.8705 | 20.1979 | 19.3474 | 18.4 | 17.9505 | 17.1032 | 16.2747 | 15.6421 | 15.04 | 12.0011 | 8.7495 | 5.6674
|  | ZETLAND ROAD PRIMARY | EE |  |  |  |  | 25.3411 | 25.0221 | 24.6832 | 24.3253 | 23.9516 | 23.5905 | 23.2442 | 22.9074 | 22.6074 | 20.8789 | 18.6242 | 16.5663 | 20.3895 | 19.7842 | 19.1189 | 18.3516 | 17.6179 | 16.8905 | 16.0505 | 15.3674 | 14.8432 | 12.9874 | 10.4779 | 8.1642 | 21.1032 | 20.7674 | 20.1979 | 19.4589 | 18.7505 | 18.0432 | 17.22 | 16.5505 | 16.0347 | 14.1789 | 11.6684 | 9.3526
|  | ZETLAND ROAD PRIMARY | HT |  |  |  |  | 25.1253 | 24.7421 | 24.3358 | 23.9116 | 23.7674 | 23.3221 | 22.8579 | 22.2568 | 21.6853 | 18.8863 | 15.9589 | 13.2074 | 19.8947 | 19.1168 | 18.2305 | 17.2484 | 16.8168 | 15.9537 | 15.1084 | 14.4674 | 13.8537 | 10.8084 | 7.5579 | 4.4768 | 20.8705 | 20.1979 | 19.3474 | 18.4 | 17.9505 | 17.1032 | 16.2747 | 15.6421 | 15.04 | 12.0011 | 8.7495 | 5.6674
|  | ZETLAND ROAD PRIMARY | HE |  |  |  |  | 25.6 | 25.3568 | 25.0895 | 24.8 | 24.4926 | 24.1968 | 23.92 | 23.6611 | 23.4379 | 22.9653 | 21.9863 | -17.4642 | 20.7695 | 20.5137 | 20.0926 | 19.5074 | 18.9505 | 18.3926 | 17.6884 | 17.1937 | 16.8453 | 15.8358 | 14.1611 | 12.6632 | 21.3832 | 21.1295 | 20.8484 | 20.5421 | 20.0284 | 19.4874 | 18.8137 | 18.3368 | 17.9937 | 16.9768 | 15.3442 | 13.8558
|  | ZETLAND ROAD PRIMARY | CF |  |  |  |  | 25.7874 | 25.6463 | 25.5 | 25.3484 | 25.1926 | 25.0326 | 24.8758 | 24.7189 | 24.5642 | 23.8716 | 23.8189 | 23.1621 | 20.9695 | 20.8221 | 20.6684 | 20.5095 | 20.3042 | 20.0337 | 19.7295 | 19.3537 | 18.9653 | 17.1695 | 16.4042 | 15.3453 | 21.5842 | 21.4358 | 21.2821 | 21.1232 | 20.9589 | 20.7916 | 20.6263 | 20.4232 | 20.0453 | 18.3232 | 17.5547 | 16.5284

## Primary Demand Headroom
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Demand (MVA) | Demand Headroom Winter (MVA) | [11 empty] | Demand Headroom Summer (MVA) | [11 empty] | Demand Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH BSP | ALDERNEY PRIMARY | MINIMUM HEADROOM | SZ 04270 95141 | NO | YES | 13.45 | -4.4434 | -4.8301 | -5.4158 | -6.0934 | -6.9281 | -7.9097 | -9.0893 | -10.226 | -11.1709 | -16.2842 | -18.9036 | -19.6005 | -1.7291 | -2.076 | -2.5281 | -2.926 | -3.4342 | -4.0158 | -4.7699 | -5.5995 | -6.2811 | -10.0362 | -11.8669 | -17.3189 | -4.897 | -5.3817 | -6.0204 | -6.5959 | -7.3143 | -8.1449 | -9.2398 | -10.3245 | -11.2225 | -16.1123 | -18.5786 | -19.2194
|  | ALDERNEY PRIMARY | EE |  |  |  |  | -4.4434 | -4.8301 | -5.4158 | -6.0934 | -6.9281 | -7.9097 | -9.0893 | -10.226 | -11.1709 | -14.5342 | -15.775 | -16.7414 | -1.7291 | -2.076 | -2.5281 | -2.926 | -3.4342 | -4.0158 | -4.7699 | -5.5995 | -6.2811 | -8.5801 | -10.0965 | -13.4679 | -4.897 | -5.3817 | -6.0204 | -6.5959 | -7.3143 | -8.1449 | -9.2398 | -10.3245 | -11.2225 | -14.3898 | -15.3704 | -15.8919
|  | ALDERNEY PRIMARY | HT |  |  |  |  | -4.0556 | -4.3097 | -4.7567 | -5.1005 | -5.5944 | -6.3424 | -7.1016 | -8.025 | -8.9822 | -13.3995 | -15.8618 | -16.9087 | -1.3362 | -1.5556 | -1.8903 | -2.1832 | -2.5362 | -2.9495 | -3.3516 | -3.875 | -4.4944 | -7.5403 | -8.8811 | -9.2822 | -4.3684 | -4.6888 | -5.1786 | -5.6051 | -6.1184 | -6.7327 | -7.3531 | -8.1827 | -9.0949 | -13.2796 | -15.2357 | -15.8939
|  | ALDERNEY PRIMARY | HE |  |  |  |  | -4.1709 | -4.4791 | -4.9281 | -5.4842 | -6.2699 | -7.1822 | -8.1679 | -9.3526 | -10.5852 | -16.2842 | -18.9036 | -19.6005 | -1.4679 | -1.7505 | -2.1322 | -2.5383 | -3.0158 | -3.5567 | -4.125 | -4.9475 | -5.8618 | -10.0362 | -11.8669 | -13.9516 | -4.5357 | -4.9347 | -5.4755 | -6.0541 | -6.7266 | -7.497 | -8.3531 | -9.4837 | -10.6643 | -16.1123 | -18.5786 | -19.2194
|  | ALDERNEY PRIMARY | CF |  |  |  |  | -3.8505 | -4.0138 | -4.2138 | -4.4434 | -4.7005 | -4.9883 | -5.4842 | -6.1556 | -6.7301 | -10.9699 | -14.7505 | -17.2281 | -1.2036 | -1.3434 | -1.5342 | -1.7546 | -1.9985 | -2.275 | -2.6495 | -3.075 | -3.425 | -6.3271 | -10.5944 | -17.3189 | -4.1225 | -4.3347 | -4.5939 | -4.8939 | -5.2215 | -5.5898 | -6.1021 | -6.6827 | -7.1755 | -11.0592 | -14.6592 | -16.9908
FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT PRIMARY | MINIMUM HEADROOM | SU 85976 48834 | NO | YES | 2.963 | 4.8164 | 4.199 | 3.849 | 3.1204 | 2.3204 | 1.2133 | -0.025469 | -1.2306 | -2.1234 | -7.8173 | -10.8428 | -11.4244 | 7.6939 | 7.1878 | 6.9082 | 6.3296 | 5.6929 | 4.899 | 3.9807 | 3.0756 | 2.399 | -1.3296 | -5.7255 | -15.8561 | 5.6745 | 5.0715 | 4.646 | 3.8164 | 2.9092 | 1.8378 | 0.56841 | -0.64384 | -1.6306 | -7.3398 | -10.1898 | -10.7255
|  | ALDERSHOT PRIMARY | EE |  |  |  |  | 4.8164 | 4.199 | 3.849 | 3.1204 | 2.3204 | 1.2133 | -0.025469 | -1.2306 | -2.1234 | -6.1561 | -8.5489 | -9.7357 | 7.6939 | 7.1878 | 6.9082 | 6.3296 | 5.6929 | 4.899 | 3.9807 | 3.0756 | 2.399 | -0.98159 | -4.2591 | -9.0469 | 5.6745 | 5.0715 | 4.646 | 3.8164 | 2.9092 | 1.8378 | 0.56841 | -0.64384 | -1.6306 | -5.0581 | -6.5285 | -7.55
|  | ALDERSHOT PRIMARY | HT |  |  |  |  | 5.3082 | 4.8602 | 4.3786 | 3.7531 | 3.0531 | 2.5286 | 1.5674 | 0.56535 | -0.47139 | -5.552 | -8.5663 | -9.7683 | 8.1929 | 7.8939 | 7.5786 | 7.1745 | 6.7153 | 6.4837 | 5.9072 | 5.2929 | 4.6511 | 1.7062 | 0.16637 | -0.38771 | 6.1756 | 5.7531 | 5.3194 | 4.7358 | 4.0776 | 3.6613 | 2.7664 | 1.8337 | 0.86739 | -3.8153 | -6.5214 | -7.5347
|  | ALDERSHOT PRIMARY | HE |  |  |  |  | 5.2204 | 4.7358 | 4.2286 | 3.5766 | 2.8245 | 2.2551 | 1.248 | 0.061265 | -1.3459 | -7.8173 | -10.8428 | -11.4244 | 8.0102 | 7.6123 | 7.2011 | 6.6837 | 6.0847 | 5.6939 | 4.9337 | 4.1245 | 3.2674 | -1.3296 | -5.1336 | -9.8183 | 6.0939 | 5.6388 | 5.1735 | 4.4286 | 3.5398 | 2.6745 | 1.4715 | 0.1878 | -1.1632 | -7.3398 | -10.1898 | -10.7255
|  | ALDERSHOT PRIMARY | CF |  |  |  |  | 5.6449 | 5.3674 | 5.1062 | 4.7817 | 4.4194 | 4.0123 | 3.8704 | 3.3511 | 2.8051 | -1.6 | -5.7989 | -8.452 | 8.247 | 7.9572 | 7.6725 | 7.3266 | 6.9113 | 6.4327 | 6.15 | 5.5613 | 4.9327 | 0.56535 | -5.7255 | -15.8561 | 6.4551 | 6.1796 | 5.9358 | 5.6133 | 5.2592 | 4.8623 | 4.4725 | 3.7817 | 3.05 | -1.4387 | -5.4285 | -7.9112
MELKSHAM GSP | CHIPPENHAM BSP | ALDERTON PRIMARY | MINIMUM HEADROOM | ST 84609 84059 | NO | YES | 0.26 | 0.81857 | 0.69714 | 0.59816 | 10.7913 | 10.6403 | 10.5087 | 10.2607 | 9.9934 | 9.8883 | 9.3852 | 9.1893 | 8.9923 | 1.5233 | 1.4365 | 1.3661 | 10.949 | 10.8398 | 10.7408 | 10.5673 | 10.3867 | 10.3133 | 9.9765 | 9.5949 | 8.6398 | 0.97204 | 0.85776 | 0.76898 | 10.7204 | 10.5837 | 10.4551 | 10.2286 | 9.9888 | 9.8888 | 9.4153 | 9.2439 | 9.0765
|  | ALDERTON PRIMARY | EE |  |  |  |  | 0.81857 | 0.69714 | 0.59816 | 10.7913 | 10.6403 | 10.5087 | 10.2607 | 9.9934 | 9.8883 | 9.3852 | 9.1893 | 9.0872 | 1.5233 | 1.4365 | 1.3661 | 10.949 | 10.8398 | 10.7408 | 10.5673 | 10.3867 | 10.3133 | 9.9765 | 9.6949 | 9.2429 | 0.97204 | 0.85776 | 0.76898 | 10.7204 | 10.5837 | 10.4551 | 10.2286 | 9.9888 | 9.8888 | 9.4153 | 9.2439 | 9.1582
|  | ALDERTON PRIMARY | HT |  |  |  |  | 0.89612 | 0.79714 | 0.71959 | 10.9628 | 10.8464 | 10.6842 | 10.4832 | 10.3168 | 10.2056 | 9.4862 | 9.2015 | 8.9923 | 1.6008 | 1.5345 | 1.4855 | 11.1184 | 11.0418 | 10.9561 | 10.8327 | 10.7235 | 10.648 | 10.1959 | 10.048 | 9.9469 | 1.0435 | 0.94959 | 0.87816 | 10.8724 | 10.7643 | 10.6194 | 10.4378 | 10.2857 | 10.1714 | 9.5102 | 9.2541 | 9.0765
|  | ALDERTON PRIMARY | HE |  |  |  |  | 0.8951 | 0.79816 | 0.72163 | 10.9668 | 10.8536 | 10.7556 | 10.5607 | 10.3342 | 10.224 | 9.4454 | 9.2566 | 9.1617 | 1.5896 | 1.5192 | 1.4702 | 11.0918 | 11.0122 | 10.9449 | 10.8214 | 10.6735 | 10.5918 | 10.0265 | 9.7388 | 9.2929 | 1.0414 | 0.94959 | 0.88122 | 10.8755 | 10.7704 | 10.6796 | 10.5061 | 10.302 | 10.1918 | 9.4776 | 9.3071 | 9.2276
|  | ALDERTON PRIMARY | CF |  |  |  |  | 0.91449 | 0.84918 | 0.78694 | 11.0372 | 10.9556 | 10.8577 | 10.7872 | 10.6679 | 10.5362 | 9.9056 | 9.525 | 9.2444 | 1.5998 | 1.5508 | 1.5069 | 11.1357 | 11.0745 | 10.9959 | 10.9378 | 10.8398 | 10.7347 | 10.1724 | 9.5949 | 8.6398 | 1.0649 | 0.99959 | 0.94347 | 10.949 | 10.8735 | 10.7857 | 10.7224 | 10.6163 | 10.499 | 9.9235 | 9.5673 | 9.3031
FLEET-BRAMLEY GSP | ALTON BSP | ALRESFORD PRIMARY | MINIMUM HEADROOM | SU 59684 32511 | NO | NO | 2.979 | 0.23469 | 17.6061 | 17.0214 | 16.8041 | 16.201 | 15.451 | 14.6816 | 13.9469 | 13.4357 | 10.7643 | 8.951 | 7.8 | 3.6092 | 15.6224 | 15.2031 | 15.1602 | 14.752 | 14.2633 | 13.7276 | 13.1949 | 12.8673 | 10.9827 | 8.7224 | 3.3204 | 0.44388 | 16.0398 | 15.4806 | 15.3867 | 14.8337 | 14.1429 | 13.4214 | 12.7265 | 12.2622 | 9.8867 | 8.3112 | 7.2796
|  | ALRESFORD PRIMARY | EE |  |  |  |  | 0.23469 | 17.6061 | 17.0214 | 16.8041 | 16.201 | 15.451 | 14.6816 | 13.9469 | 13.4357 | 10.7643 | 9.2133 | 8.1602 | 3.6092 | 15.6224 | 15.2031 | 15.1602 | 14.752 | 14.2633 | 13.7276 | 13.1949 | 12.8673 | 10.9827 | 9.0929 | 6.3255 | 0.44388 | 16.0398 | 15.4806 | 15.3867 | 14.8337 | 14.1429 | 13.4214 | 12.7265 | 12.2622 | 9.8867 | 8.5306 | 7.5939
|  | ALRESFORD PRIMARY | HT |  |  |  |  | 0.48776 | 17.95 | 17.5214 | 17.002 | 16.4306 | 16.0878 | 15.4347 | 14.7969 | 14.1214 | 10.8408 | 8.951 | 7.8 | 3.8898 | 16.0214 | 15.7765 | 15.4622 | 15.1173 | 15.0755 | 14.7071 | 14.3327 | 13.9337 | 12.1153 | 11.198 | 10.6765 | 0.72959 | 16.4296 | 16.051 | 15.5776 | 15.0541 | 14.7847 | 14.1867 | 13.5918 | 12.9663 | 9.9704 | 8.3112 | 7.2796
|  | ALRESFORD PRIMARY | HE |  |  |  |  | 0.49694 | 17.9735 | 17.5633 | 17.0612 | 16.5102 | 16.2357 | 15.6612 | 15.0969 | 14.5 | 11.3694 | 9.8265 | 9.0755 | 3.8429 | 15.95 | 15.6898 | 15.352 | 14.9806 | 14.8837 | 14.5071 | 14.1214 | 13.6969 | 11.3255 | 9.35 | 6.698 | 0.73673 | 16.449 | 16.0837 | 15.6286 | 15.1224 | 14.9204 | 14.3878 | 13.8602 | 13.3061 | 10.4153 | 8.8541 | 8.0755
|  | ALRESFORD PRIMARY | CF |  |  |  |  | 0.63673 | 18.2449 | 17.8969 | 17.5643 | 17.1602 | 16.7673 | 16.3714 | 16.4255 | 16.0949 | 13.9153 | 11.952 | 10.2571 | 3.8969 | 16.0847 | 15.8296 | 15.5929 | 15.2888 | 14.9571 | 14.5888 | 14.6122 | 14.2867 | 11.9857 | 8.7224 | 3.3204 | 0.85102 | 16.6867 | 16.3653 | 16.0694 | 15.6969 | 15.3296 | 14.9378 | 15.0796 | 14.7684 | 12.7347 | 10.9633 | 9.3643
FLEET-BRAMLEY GSP | ALTON BSP | ALTON LOCAL PRIMARY | MINIMUM HEADROOM | SU 72434 39606 | NO | NO | 6.559 | 19.2331 | 17.9463 | 16.5249 | 15.5657 | 14.5433 | 13.1188 | 11.4963 | 9.8902 | 8.6739 | 1.8555 | -3.1914 | -5.9741 | 28.6484 | 27.8198 | 26.7116 | 25.979 | 25.1902 | 24.1922 | 23.0127 | 21.8402 | 21.0076 | 16.482 | 11.8739 | -0.89857 | 20.7463 | 19.628 | 18.3055 | 17.4096 | 16.4443 | 15.1157 | 13.5933 | 12.0882 | 10.98 | 4.9627 | 0.50551 | -1.8373
|  | ALTON LOCAL PRIMARY | EE |  |  |  |  | 19.2331 | 17.9463 | 16.5249 | 15.5657 | 14.5433 | 13.1188 | 11.4963 | 9.8902 | 8.6739 | 2.2535 | -2.072 | -5.2741 | 28.6484 | 27.8198 | 26.7116 | 25.979 | 25.1902 | 24.1922 | 23.0127 | 21.8402 | 21.0076 | 16.482 | 11.9708 | 5.2024 | 20.7463 | 19.628 | 18.3055 | 17.4096 | 16.4443 | 15.1157 | 13.5933 | 12.0882 | 10.98 | 5.2514 | 1.4984 | -1.2394
|  | ALTON LOCAL PRIMARY | HT |  |  |  |  | 19.6729 | 18.1963 | 16.8361 | 16.3402 | 15.48 | 14.1973 | 12.7739 | 11.3014 | 9.7769 | 1.8555 | -3.1914 | -5.9741 | 29.1841 | 28.2535 | 27.2882 | 27.0912 | 26.5606 | 25.8535 | 25.0259 | 24.1698 | 23.2688 | 18.9473 | 16.5922 | 15.4116 | 21.1902 | 19.8841 | 18.629 | 18.1984 | 17.4055 | 16.231 | 14.9188 | 13.5637 | 12.1596 | 4.9627 | 0.50551 | -1.8373
|  | ALTON LOCAL PRIMARY | HE |  |  |  |  | 19.729 | 18.3035 | 17.0024 | 16.582 | 15.8035 | 14.7718 | 13.6024 | 12.3963 | 11.1351 | 4.4055 | 0.16673 | -1.8761 | 29.0953 | 28.1127 | 27.1035 | 26.8596 | 26.281 | 25.5688 | 24.7269 | 23.8453 | 22.8984 | 17.6902 | 13.08 | 6.7943 | 21.2412 | 19.98 | 18.7769 | 18.4167 | 17.6943 | 16.7443 | 15.6576 | 14.5371 | 13.3688 | 7.2514 | 3.5514 | 1.8698
|  | ALTON LOCAL PRIMARY | CF |  |  |  |  | 20.6933 | 19.7361 | 18.5739 | 17.8912 | 17.5331 | 16.9586 | 16.3933 | 15.8494 | 15.2739 | 10.8769 | 6.1361 | 1.83 | 29.5341 | 28.7565 | 27.8229 | 27.2759 | 27.0106 | 26.4351 | 25.7943 | 25.1433 | 24.4422 | 19.3494 | 11.8739 | -0.89857 | 22.0392 | 21.178 | 20.1371 | 19.531 | 19.2514 | 18.7341 | 18.1984 | 17.6769 | 17.1269 | 13.0259 | 8.7637 | 4.9637
MELKSHAM GSP | ANDOVER BSP | ANDOVER PRIMARY | MINIMUM HEADROOM | SU 35240 46643 | NO | NO | 2.339 | 21.446 | 21.195 | 20.8603 | 20.3552 | 20.0532 | 19.2583 | 18.4154 | 17.642 | 16.8603 | 13.5205 | 11.3634 | 10.0756 | 23.9124 | 23.695 | 23.4103 | 23.0399 | 22.9124 | 22.4522 | 21.9144 | 21.3185 | 20.842 | 18.6501 | 16.2511 | 10.3685 | 21.9266 | 21.6532 | 21.293 | 20.8052 | 20.6644 | 20.0093 | 19.2532 | 18.4215 | 17.7613 | 15.0175 | 13.1715 | 12.0573
|  | ANDOVER PRIMARY | EE |  |  |  |  | 21.446 | 21.195 | 20.8603 | 20.3552 | 20.1236 | 19.4011 | 18.5746 | 17.642 | 16.8603 | 13.6756 | 11.7328 | 10.2828 | 23.9124 | 23.695 | 23.4103 | 23.0399 | 22.9124 | 22.4522 | 21.9144 | 21.3185 | 20.842 | 18.6501 | 16.5991 | 13.5511 | 21.9266 | 21.6532 | 21.293 | 20.8052 | 20.6644 | 20.0103 | 19.2573 | 18.4215 | 17.7613 | 15.1062 | 13.492 | 12.2287
|  | ANDOVER PRIMARY | HT |  |  |  |  | 21.5971 | 21.3868 | 21.094 | 20.6236 | 20.0532 | 19.2583 | 18.4154 | 17.9001 | 17.0777 | 13.5205 | 11.3634 | 10.0756 | 24.1164 | 23.9817 | 23.794 | 23.5297 | 23.2062 | 22.7858 | 22.3215 | 22.145 | 21.7042 | 19.8511 | 18.846 | 18.2766 | 22.1287 | 21.9205 | 21.6317 | 21.2205 | 20.7062 | 20.0093 | 19.2532 | 18.9103 | 18.1848 | 15.0175 | 13.1715 | 12.0573
|  | ANDOVER PRIMARY | HE |  |  |  |  | 21.6124 | 21.4185 | 21.1613 | 20.7981 | 20.3297 | 19.7011 | 18.9715 | 18.4777 | 17.6787 | 14.392 | 12.493 | 11.6664 | 24.0644 | 23.9073 | 23.6991 | 23.444 | 23.1195 | 22.7154 | 22.2368 | 21.995 | 21.4817 | 19.0481 | 16.9797 | 14.1817 | 22.1358 | 21.9471 | 21.6889 | 21.3624 | 20.9317 | 20.3675 | 19.7022 | 19.3817 | 18.6838 | 15.8001 | 14.1787 | 13.4766
|  | ANDOVER PRIMARY | CF |  |  |  |  | 21.8052 | 21.6726 | 21.5471 | 21.3909 | 21.2522 | 21.0664 | 20.7991 | 20.4858 | 20.1124 | 17.0746 | 15.0552 | 12.9858 | 24.1603 | 24.0144 | 23.8807 | 23.7011 | 23.5185 | 23.2777 | 22.9746 | 22.6348 | 22.2583 | 19.6307 | 16.2511 | 10.3685 | 22.3052 | 22.1654 | 22.0471 | 21.8746 | 21.7317 | 21.5328 | 21.2552 | 20.942 | 20.5838 | 18.0695 | 16.3205 | 14.5715
MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST PRIMARY | MINIMUM HEADROOM | SU 37953 46433 | NO | NO | 6.363 | 6.6686 | 5.8084 | 4.7951 | 4.1278 | 3.2686 | 2.2982 | 1.2604 | 0.22473 | -0.58445 | -5.0089 | -8.8998 | -11.2151 | 8.5829 | 7.9002 | 7.1594 | 6.6553 | 6.0115 | 5.3941 | 4.686 | 3.9543 | 3.388 | 0.27678 | -3.0334 | -11.5069 | 6.388 | 5.6553 | 4.8258 | 4.1972 | 3.4707 | 2.6604 | 1.8013 | 0.86249 | 0.12065 | -3.9079 | -7.2896 | -9.2304
|  | ANDOVER EAST PRIMARY | EE |  |  |  |  | 6.7309 | 5.8084 | 4.7951 | 4.1278 | 3.2686 | 2.2982 | 1.2604 | 0.22473 | -0.58445 | -4.8824 | -8.3426 | -10.8926 | 8.5829 | 7.9002 | 7.1594 | 6.6553 | 6.0115 | 5.3941 | 4.686 | 3.9543 | 3.388 | 0.27678 | -3.0334 | -7.7151 | 6.4676 | 5.6809 | 4.8258 | 4.1972 | 3.4707 | 2.6604 | 1.8013 | 0.86249 | 0.12065 | -3.8589 | -6.8202 | -8.9926
|  | ANDOVER EAST PRIMARY | HT |  |  |  |  | 6.6686 | 5.8339 | 4.986 | 4.189 | 3.6145 | 2.7258 | 2.138 | 1.2635 | 0.37473 | -5.0089 | -8.8998 | -11.2151 | 8.6319 | 8.0737 | 7.5084 | 6.9819 | 6.6217 | 6.1431 | 5.9115 | 5.4247 | 4.9196 | 2.1237 | 0.32371 | -0.64567 | 6.388 | 5.6553 | 4.9115 | 4.2074 | 3.7125 | 2.9421 | 2.4145 | 1.6462 | 0.86861 | -3.9079 | -7.2896 | -9.2304
|  | ANDOVER EAST PRIMARY | HE |  |  |  |  | 6.9574 | 6.1451 | 5.3237 | 4.4819 | 3.7492 | 2.987 | 2.5176 | 1.7707 | 1.0094 | -3.3416 | -6.6844 | -8.2222 | 8.8023 | 8.2002 | 7.6002 | 6.9604 | 6.3911 | 5.8849 | 5.6207 | 5.089 | 4.5319 | 1.2329 | -2.0916 | -6.3487 | 6.6737 | 5.9553 | 5.2298 | 4.4758 | 3.8145 | 3.1502 | 2.7217 | 2.0604 | 1.387 | -2.4589 | -5.3212 | -6.5987
|  | ANDOVER EAST PRIMARY | CF |  |  |  |  | 7.286 | 6.9033 | 6.2237 | 5.5737 | 4.9288 | 4.4104 | 4.09 | 4.0502 | 3.7094 | 0.8982 | -2.2865 | -5.3151 | 8.9513 | 8.6564 | 8.0921 | 7.5411 | 6.9482 | 6.4023 | 6.0064 | 5.8329 | 5.4135 | 2.2227 | -2.9396 | -11.5069 | 6.9625 | 6.6564 | 6.0615 | 5.487 | 4.9074 | 4.4421 | 4.1707 | 4.1135 | 3.8472 | 1.5013 | -1.3498 | -4.0232
MELKSHAM GSP | ANDOVER BSP | ANDOVER TOWN PRIMARY | MINIMUM HEADROOM | SU 36207 45078 | NO | NO | 0.763 | 6.1133 | 5.8857 | 5.6092 | 5.3122 | 5.2837 | 4.7878 | 4.249 | 3.6867 | 3.2612 | 0.68367 | -1.4653 | -2.7592 | 7.4571 | 7.2276 | 6.9439 | 6.6255 | 6.6071 | 6.2224 | 5.7827 | 5.3296 | 5.0153 | 3.2449 | 0.58367 | -5.5643 | 5.9306 | 5.7041 | 5.4194 | 5.0633 | 5.0755 | 4.5786 | 4.0122 | 3.4459 | 3.0663 | 0.97347 | -0.8551 | -1.9143
|  | ANDOVER TOWN PRIMARY | EE |  |  |  |  | 6.1133 | 5.8857 | 5.6092 | 5.3122 | 5.2837 | 4.7878 | 4.249 | 3.6867 | 3.2612 | 0.89082 | -1.0582 | -2.552 | 7.4571 | 7.2276 | 6.9439 | 6.6255 | 6.6071 | 6.2224 | 5.7827 | 5.3296 | 5.0153 | 3.2449 | 1.1163 | -2.1704 | 5.9306 | 5.7041 | 5.4194 | 5.0633 | 5.0755 | 4.5786 | 4.0122 | 3.4459 | 3.0663 | 1.0918 | -0.49796 | -1.751
|  | ANDOVER TOWN PRIMARY | HT |  |  |  |  | 6.2367 | 6.052 | 5.8306 | 5.6265 | 5.3776 | 4.8735 | 4.3306 | 4.0796 | 3.5653 | 0.68367 | -1.4653 | -2.7592 | 7.6796 | 7.549 | 7.3755 | 7.2245 | 7.0224 | 6.7214 | 6.3776 | 6.3643 | 6.05 | 4.5163 | 3.5857 | 3.0663 | 6.0847 | 5.9041 | 5.6857 | 5.4898 | 5.2388 | 4.7755 | 4.2633 | 4.0796 | 3.598 | 0.97347 | -0.8551 | -1.9143
|  | ANDOVER TOWN PRIMARY | HE |  |  |  |  | 6.2643 | 6.0939 | 5.8898 | 5.7061 | 5.4806 | 5.0796 | 4.6337 | 4.4847 | 4.0745 | 1.7245 | -0.17755 | -1.1357 | 7.6327 | 7.4704 | 7.2694 | 7.0857 | 6.849 | 6.5316 | 6.1633 | 6.1204 | 5.7653 | 3.7398 | 1.5969 | -1.5 | 6.1041 | 5.9378 | 5.7357 | 5.5592 | 5.3347 | 4.9551 | 4.5214 | 4.4367 | 4.0429 | 1.9102 | 0.32653 | -0.4551
|  | ANDOVER TOWN PRIMARY | CF |  |  |  |  | 6.4316 | 6.3184 | 6.2133 | 6.0684 | 5.9429 | 5.7786 | 5.5969 | 5.4071 | 5.2051 | 4.0816 | 2.302 | 0.55612 | 7.7112 | 7.5551 | 7.4153 | 7.2255 | 7.0367 | 6.7816 | 6.4959 | 6.1837 | 5.85 | 4.0327 | 0.58367 | -5.5643 | 6.2592 | 6.1418 | 6.0378 | 5.8959 | 5.7786 | 5.6163 | 5.4255 | 5.1878 | 4.9357 | 3.8571 | 2.3429 | 0.93163
BRAMLEY (BASI) GSP | READING BSP | ARBORFIELD PRIMARY | MINIMUM HEADROOM | SU 75949 65766 | NO | NO | 9.793 | 4.5709 | 4.1311 | 3.6892 | 2.979 | 2.3229 | 1.8382 | 1.0025 | 0.03718 | -0.51282 | -6.0791 | -10.8363 | -14.3924 | 8.8688 | 8.58 | 8.2923 | 7.8545 | 7.4362 | 7.2606 | 6.777 | 6.1821 | 5.6739 | 2.7158 | -0.23629 | -5.2761 | 6.1045 | 5.7066 | 5.3015 | 4.6586 | 4.0606 | 3.5504 | 2.7821 | 1.8984 | 1.3525 | -3.3557 | -7.2853 | -10.1465
|  | ARBORFIELD PRIMARY | EE |  |  |  |  | 4.5709 | 4.1311 | 3.6892 | 2.979 | 2.3229 | 2.0504 | 1.3004 | 0.34738 | -0.46282 | -5.6077 | -10.3118 | -14.1465 | 8.8688 | 8.58 | 8.2923 | 7.8545 | 7.4362 | 7.2606 | 6.777 | 6.1821 | 5.6739 | 2.7158 | -0.23629 | -3.5077 | 6.1045 | 5.7066 | 5.3015 | 4.6586 | 4.0606 | 3.7117 | 3.0158 | 2.1372 | 1.3637 | -3.0138 | -6.8475 | -9.9434
|  | ARBORFIELD PRIMARY | HT |  |  |  |  | 4.6158 | 4.2933 | 3.9025 | 3.2117 | 2.6209 | 1.8382 | 1.0025 | 0.03718 | -0.51282 | -6.0791 | -10.8363 | -14.3924 | 8.9586 | 8.7739 | 8.5576 | 8.1739 | 7.8382 | 7.4004 | 6.929 | 6.3811 | 6.1096 | 3.3168 | 1.0484 | -0.63017 | 6.1341 | 5.8311 | 5.4637 | 4.8331 | 4.2739 | 3.5504 | 2.7821 | 1.8984 | 1.3525 | -3.3557 | -7.2853 | -10.1465
|  | ARBORFIELD PRIMARY | HE |  |  |  |  | 4.7586 | 4.3933 | 4.0351 | 3.428 | 2.926 | 2.326 | 1.63 | 0.71677 | 0.2984 | -5.072 | -9.7332 | -13.1628 | 8.9964 | 8.7668 | 8.5392 | 8.1749 | 7.8637 | 7.4841 | 7.0423 | 6.477 | 6.1862 | 3.0351 | 0.069833 | -3.0526 | 6.2576 | 5.9209 | 5.5862 | 5.0321 | 4.5555 | 4.0045 | 3.3688 | 2.5382 | 2.0504 | -2.4414 | -6.2587 | -9.0353
|  | ARBORFIELD PRIMARY | CF |  |  |  |  | 5.1341 | 4.9515 | 4.7902 | 4.4709 | 4.2331 | 4.076 | 3.7515 | 3.3494 | 2.9066 | -0.14343 | -5.9179 | -11.9945 | 9.2015 | 9.0606 | 8.9311 | 8.7055 | 8.5106 | 8.3464 | 8.0719 | 7.7494 | 7.3964 | 5.0025 | 0.58106 | -5.2761 | 6.5984 | 6.4331 | 6.2851 | 6.0025 | 5.7933 | 5.6504 | 5.3678 | 5.0137 | 4.627 | 1.7586 | -3.1271 | -8.0465
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ARGYLE ROAD PRIMARY | MINIMUM HEADROOM | SZ 93193 99152 | NO | YES | 0.852 | 12.2888 | 11.8878 | 11.4031 | 10.8684 | 10.648 | 9.7633 | 8.7612 | 7.752 | 6.9959 | 2.9204 | -1.0082 | -3.401 | 15.9735 | 15.5888 | 15.1255 | 14.5939 | 14.3398 | 13.6663 | 12.8918 | 12.1031 | 11.4776 | 7.8918 | 3.0857 | -8.8908 | 12.3816 | 11.9531 | 11.4133 | 10.8061 | 10.6684 | 9.8408 | 8.9 | 7.9633 | 7.2531 | 3.6796 | 0.25 | -1.6571
|  | ARGYLE ROAD PRIMARY | EE |  |  |  |  | 12.2888 | 11.8878 | 11.4031 | 10.8684 | 10.648 | 9.7633 | 8.7612 | 7.752 | 6.9959 | 3.0327 | -0.044898 | -2.9031 | 15.9735 | 15.5888 | 15.1255 | 14.5939 | 14.3398 | 13.6663 | 12.8918 | 12.1031 | 11.4776 | 7.8918 | 3.801 | -2.6582 | 12.3816 | 11.9531 | 11.4133 | 10.8061 | 10.6684 | 9.8408 | 8.9 | 7.9633 | 7.2531 | 3.6908 | 1.0704 | -1.2816
|  | ARGYLE ROAD PRIMARY | HT |  |  |  |  | 12.5643 | 12.2541 | 11.8867 | 11.5327 | 11.099 | 10.3214 | 9.7918 | 8.9704 | 8.1102 | 2.9204 | -1.0082 | -3.401 | 16.348 | 16.1306 | 15.8633 | 15.5959 | 15.2643 | 14.7959 | 14.5449 | 14.0316 | 13.4929 | 10.5939 | 8.599 | 7.5347 | 12.6837 | 12.3929 | 12.0408 | 11.6765 | 11.2265 | 10.4867 | 10.0133 | 9.2184 | 8.3867 | 3.6796 | 0.25 | -1.6571
|  | ARGYLE ROAD PRIMARY | HE |  |  |  |  | 12.5878 | 12.3071 | 11.9796 | 11.6704 | 11.2898 | 10.6439 | 10.248 | 9.5837 | 8.8908 | 4.9347 | 1.8184 | 0.16531 | 16.2469 | 15.9847 | 15.6704 | 15.3449 | 14.9531 | 14.4357 | 14.1224 | 13.548 | 12.9398 | 9.1694 | 5.0245 | -0.93776 | 12.702 | 12.4398 | 12.1286 | 11.8092 | 11.4194 | 10.799 | 10.4551 | 9.8051 | 9.1327 | 5.5173 | 2.9357 | 1.652
|  | ARGYLE ROAD PRIMARY | CF |  |  |  |  | 12.8571 | 12.7 | 12.5102 | 12.3051 | 12.1224 | 11.8806 | 11.5847 | 11.2602 | 11.2592 | 8.8908 | 6.1265 | 3.2143 | 16.3776 | 16.1633 | 15.9061 | 15.6051 | 15.2806 | 14.8673 | 14.3765 | 13.85 | 13.5755 | 9.6857 | 3.0857 | -8.8908 | 12.9459 | 12.8 | 12.6204 | 12.3847 | 12.1949 | 11.9224 | 11.5816 | 11.2112 | 11.3122 | 9.05 | 6.5653 | 4.0602
COWLEY GSP | HEADINGTON BSP | ARNCOTT PRIMARY | MINIMUM HEADROOM | SP 60730 18095 | NO | NO | 16.941 | -1.0873 | -1.4924 | -2.3944 | -3.5893 | -5.0709 | -7.9934 | -10.6342 | -13.1699 | -18.4771 | -22.6454 | -24.1301 | -24.6842 | -2.2501 | -2.4716 | -2.9144 | -3.4379 | -4.2522 | -6.6471 | -8.9562 | -11.1369 | -16.3818 | -18.8573 | -19.5297 | -21.3583 | -2.5658 | -2.9056 | -3.6291 | -4.4393 | -5.6852 | -8.2873 | -10.6822 | -12.9883 | -18.1036 | -21.5811 | -22.7791 | -23.2373
|  | ARNCOTT PRIMARY | EE |  |  |  |  | -1.0873 | -1.4924 | -2.3944 | -3.4128 | -4.8944 | -7.3954 | -9.6189 | -11.5036 | -15.1128 | -22.6454 | -24.0873 | -24.5332 | -2.2501 | -2.4716 | -2.9144 | -3.3858 | -4.1797 | -6.043 | -7.896 | -9.5542 | -12.9746 | -18.7256 | -19.345 | -20.3389 | -2.5658 | -2.9056 | -3.6291 | -4.4097 | -5.573 | -7.7669 | -9.7424 | -11.4005 | -14.8169 | -21.5811 | -22.7424 | -23.1005
|  | ARNCOTT PRIMARY | HT |  |  |  |  | -1.0107 | -1.3934 | -2.2618 | -3.5893 | -5.0709 | -7.9934 | -10.6342 | -13.1699 | -18.4771 | -22.5311 | -24.1301 | -24.6842 | -2.1389 | -2.3175 | -2.7195 | -3.4379 | -4.2522 | -6.6471 | -8.9562 | -11.1369 | -16.3818 | -18.6328 | -19.3011 | -19.5562 | -2.4546 | -2.7577 | -3.4362 | -4.4393 | -5.6852 | -8.2873 | -10.6822 | -12.9883 | -18.1036 | -21.4791 | -22.7791 | -23.2373
|  | ARNCOTT PRIMARY | HE |  |  |  |  | -1.0107 | -1.3852 | -2.2505 | -3.2291 | -4.6658 | -7.0822 | -9.1924 | -11.2811 | -14.9036 | -22.4301 | -23.8822 | -24.2271 | -2.1573 | -2.344 | -2.743 | -3.1777 | -3.9552 | -5.8124 | -7.5818 | -9.3358 | -12.7726 | -18.8573 | -19.5297 | -20.2522 | -2.4556 | -2.7526 | -3.425 | -4.1546 | -5.3087 | -7.4373 | -9.326 | -11.1924 | -14.6179 | -21.4097 | -22.5913 | -22.874
|  | ARNCOTT PRIMARY | CF |  |  |  |  | -0.65461 | -0.8138 | -1.1801 | -1.723 | -2.4271 | -4.2801 | -6.0536 | -7.724 | -10.1352 | -20.8464 | -22.573 | -23.6556 | -1.9716 | -2.0777 | -2.2909 | -2.5695 | -2.895 | -4.2777 | -5.592 | -6.8369 | -8.9267 | -18.0144 | -19.2879 | -21.3583 | -2.1403 | -2.2883 | -2.6118 | -3.0383 | -3.5658 | -5.0924 | -6.6301 | -8.073 | -10.2679 | -19.9975 | -21.4209 | -22.3597
FLEET-BRAMLEY GSP | BRACKNELL BSP | ASCOT PRIMARY | MINIMUM HEADROOM | SU 91615 68855 | NO | NO | 2.382 | 15.1703 | 14.8591 | 14.3724 | 13.7948 | 13.605 | 12.855 | 12.1418 | 11.4244 | 10.906 | 8.4244 | 6.504 | 5.7867 | 17.5162 | 17.2316 | 16.8397 | 16.3785 | 16.2754 | 15.7509 | 15.1989 | 14.6275 | 14.2326 | 12.0805 | 8.5642 | 0.75502 | 15.2581 | 14.9469 | 14.4744 | 13.9203 | 13.8101 | 13.1234 | 12.4367 | 11.7479 | 11.2816 | 9.1581 | 7.5122 | 6.9162
|  | ASCOT PRIMARY | EE |  |  |  |  | 15.1703 | 14.8591 | 14.3724 | 13.7948 | 13.605 | 12.855 | 12.1418 | 11.4244 | 10.906 | 8.4244 | 6.7662 | 6.255 | 17.5162 | 17.2316 | 16.8397 | 16.3785 | 16.2754 | 15.7509 | 15.1989 | 14.6275 | 14.2326 | 12.0805 | 9.6805 | 5.9754 | 15.2581 | 14.9469 | 14.4744 | 13.9203 | 13.8101 | 13.1234 | 12.4367 | 11.7479 | 11.2816 | 9.1581 | 7.7479 | 7.3173
|  | ASCOT PRIMARY | HT |  |  |  |  | 15.3887 | 15.1509 | 14.6662 | 14.2091 | 13.7193 | 13.153 | 12.8897 | 12.2989 | 11.6887 | 8.5142 | 6.504 | 5.7867 | 17.7979 | 17.6346 | 17.3346 | 17.0591 | 16.7428 | 16.3907 | 16.3295 | 15.9632 | 15.5918 | 13.7836 | 12.7836 | 12.4152 | 15.504 | 15.2754 | 14.8397 | 14.4336 | 13.9764 | 13.4428 | 13.2632 | 12.7101 | 12.1418 | 9.2642 | 7.5122 | 6.9162
|  | ASCOT PRIMARY | HE |  |  |  |  | 15.4081 | 15.1938 | 14.8224 | 14.5234 | 14.0724 | 13.4479 | 13.1183 | 12.5673 | 12.0091 | 9.3713 | 7.6969 | 7.1448 | 17.7254 | 17.5193 | 17.2275 | 16.9744 | 16.6111 | 16.1622 | 15.9938 | 15.5509 | 15.0928 | 12.5734 | 10.0611 | 6.352 | 15.5213 | 15.3071 | 14.9611 | 14.6826 | 14.2591 | 13.6846 | 13.4611 | 12.9448 | 12.4193 | 10.006 | 8.5734 | 8.1203
|  | ASCOT PRIMARY | CF |  |  |  |  | 15.6183 | 15.5009 | 15.3203 | 15.053 | 14.7224 | 14.3662 | 14.0652 | 14.0948 | 13.8326 | 11.9387 | 9.7958 | 7.806 | 17.8224 | 17.6601 | 17.4469 | 17.1979 | 16.8775 | 16.502 | 16.1193 | 16.0254 | 15.6489 | 12.9244 | 8.5642 | 0.75502 | 15.7142 | 15.5907 | 15.4081 | 15.1703 | 14.8662 | 14.5346 | 14.2316 | 14.304 | 14.0428 | 12.2193 | 10.3397 | 8.6632
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ASHLING ROAD PRIMARY | MINIMUM HEADROOM | SU 84085 06737 | NO | YES | 11.308 | -4.8812 | -5.8108 | -7.073 | 3.9749 | 2.3219 | 0.05249 | -2.4322 | -4.5924 | -6.2393 | -14.1424 | -19.8404 | -23.0812 | 2.9811 | 2.4076 | 1.5494 | 14.2678 | 13.1678 | 11.7596 | 10.1698 | 8.7086 | 7.626 | 2.2056 | -2.9536 | -15.9893 | -4.3587 | -5.1526 | -6.2873 | 5.7004 | 4.2147 | 2.1892 | -0.052612 | -2.0496 | -3.4944 | -10.4485 | -15.2047 | -17.8057
|  | ASHLING ROAD PRIMARY | EE |  |  |  |  | -4.8812 | -5.8108 | -7.073 | 3.9749 | 2.3219 | 0.05249 | -2.4322 | -4.5924 | -6.2393 | -14.1424 | -18.9781 | -22.5802 | 2.9811 | 2.4076 | 1.5494 | 14.2678 | 13.1678 | 11.7596 | 10.1698 | 8.7086 | 7.626 | 2.2056 | -2.5536 | -9.2853 | -4.3587 | -5.1526 | -6.2873 | 5.7004 | 4.2147 | 2.1892 | -0.052612 | -2.0496 | -3.4944 | -10.4485 | -14.47 | -17.4281
|  | ASHLING ROAD PRIMARY | HT |  |  |  |  | -4.2159 | -5.3424 | -6.4965 | 5.1056 | 3.6821 | 1.6515 | -0.51078 | -2.4424 | -4.3893 | -14.0179 | -19.8404 | -23.0812 | 3.6515 | 3.0035 | 2.3311 | 15.6004 | 14.8004 | 13.7372 | 12.5688 | 11.4821 | 10.3658 | 5.1331 | 2.3362 | 0.95147 | -3.6944 | -4.6822 | -5.7016 | 6.8474 | 5.5984 | 3.8219 | 1.9147 | 0.178 | -1.5791 | -10.221 | -15.2047 | -17.8057
|  | ASHLING ROAD PRIMARY | HE |  |  |  |  | -4.2536 | -5.3791 | -6.5159 | 5.0974 | 3.6821 | 1.8127 | -0.2271 | -2.022 | -3.8373 | -12.9393 | -18.2965 | -20.6149 | 3.48 | 2.7464 | 1.9872 | 15.1617 | 14.2484 | 13.1107 | 11.829 | 10.6127 | 9.3474 | 2.6627 | -2.6118 | -8.8608 | -3.7404 | -4.7291 | -5.7393 | 6.8107 | 5.5617 | 3.9188 | 2.1107 | 0.48412 | -1.1679 | -9.3914 | -13.9434 | -15.7944
|  | ASHLING ROAD PRIMARY | CF |  |  |  |  | -3.7128 | -4.4975 | -5.2781 | 6.2984 | 5.6596 | 4.5902 | 3.3556 | 2.3586 | 1.3494 | -5.0506 | -10.8598 | -15.9261 | 3.7556 | 3.2004 | 2.6188 | 15.6474 | 15.1933 | 14.3637 | 13.3974 | 12.5056 | 11.5729 | 5.326 | -2.9536 | -15.9893 | -3.2404 | -3.9118 | -4.5996 | 7.8923 | 7.3831 | 6.4658 | 5.3923 | 4.4953 | 3.58 | -2.2506 | -7.4791 | -11.9414
MELKSHAM GSP | NORRINGTON BSP | ASHTON PARK PRIMARY | MINIMUM HEADROOM | ST 87141 57741 | NO | YES | 19.333 | -5.3523 | -6.0921 | -7.3502 | -8.8166 | -10.5911 | -12.8564 | -15.6074 | -18.5513 | -20.8043 | -30.4574 | -37.2257 | -40.1584 | -1.1451 | -1.6298 | -2.5696 | -3.589 | -4.7094 | -6.0941 | -7.7839 | -9.5686 | -10.886 | -16.5819 | -22.0451 | -34.6176 | -6.0135 | -6.6217 | -7.8033 | -9.1533 | -10.7319 | -12.738 | -15.1696 | -17.7462 | -19.6298 | -27.4798 | -33.0982 | -35.587
|  | ASHTON PARK PRIMARY | EE |  |  |  |  | -5.3523 | -6.0921 | -7.3502 | -8.8166 | -10.5911 | -12.8564 | -15.6074 | -18.5513 | -20.8043 | -30.0043 | -36.2247 | -39.6196 | -1.1451 | -1.6298 | -2.5696 | -3.589 | -4.7094 | -6.0941 | -7.7839 | -9.5686 | -10.886 | -16.5819 | -21.7931 | -28.439 | -6.0135 | -6.6217 | -7.8033 | -9.1533 | -10.7319 | -12.738 | -15.1696 | -17.7462 | -19.6298 | -27.2053 | -32.236 | -35.1645
|  | ASHTON PARK PRIMARY | HT |  |  |  |  | -4.9502 | -5.9594 | -7.1706 | -8.2411 | -10.1033 | -12.4013 | -15.086 | -17.6564 | -20.0543 | -30.4574 | -37.2257 | -40.1584 | -0.61044 | -1.2196 | -2.0166 | -2.5135 | -3.5023 | -4.6911 | -6.1186 | -7.4951 | -8.7737 | -14.0564 | -17.1094 | -18.3553 | -5.4655 | -6.3757 | -7.4788 | -8.3176 | -9.8951 | -11.8564 | -14.1482 | -16.3696 | -18.4564 | -27.4798 | -33.0982 | -35.587
|  | ASHTON PARK PRIMARY | HE |  |  |  |  | -4.8645 | -5.8196 | -6.9951 | -7.987 | -9.5696 | -11.4645 | -13.8288 | -16.3737 | -18.69 | -28.3135 | -34.6849 | -36.9635 | -0.70126 | -1.3604 | -2.2145 | -2.8023 | -3.7502 | -4.8778 | -6.2911 | -7.8074 | -9.2441 | -15.7584 | -21.2257 | -27.4288 | -5.4043 | -6.2727 | -7.3421 | -8.1196 | -9.4768 | -11.1043 | -13.1308 | -15.3115 | -17.3206 | -25.6472 | -30.8778 | -32.8237
|  | ASHTON PARK PRIMARY | CF |  |  |  |  | -4.4186 | -5.0166 | -5.8553 | -6.6431 | -7.1125 | -7.8625 | -8.9747 | -10.3288 | -11.8278 | -21.1043 | -27.7962 | -32.6604 | -0.49616 | -0.97983 | -1.687 | -2.3451 | -2.7186 | -3.4013 | -4.3145 | -5.3666 | -6.5064 | -13.8288 | -22.0451 | -34.6176 | -5.0104 | -5.5594 | -6.3278 | -7.0574 | -7.3768 | -8.0513 | -9.0411 | -10.2227 | -11.5257 | -19.5155 | -25.1513 | -29.2206
FLEET-BRAMLEY GSP | BRACKNELL BSP | BAGSHOT PRIMARY | MINIMUM HEADROOM | SU 91122 63523 | NO | NO | 5.057 | 8.6589 | 8.3334 | 8.1681 | 7.8252 | 7.4303 | 6.6099 | 5.6834 | 4.7558 | 4.1446 | 0.62214 | -2.185 | -3.7401 | 12.2017 | 11.815 | 11.7242 | 11.3385 | 10.915 | 10.3426 | 9.6742 | 8.9966 | 8.5487 | 5.9926 | 2.1772 | -6.4309 | 8.7466 | 8.2997 | 8.2119 | 7.7762 | 7.3017 | 6.5374 | 5.6681 | 4.7987 | 4.2395 | 1.2007 | -1.2319 | -2.5187
|  | BAGSHOT PRIMARY | EE |  |  |  |  | 8.6589 | 8.3334 | 8.1681 | 7.8252 | 7.4303 | 6.6099 | 5.6834 | 4.7558 | 4.1446 | 0.91602 | -1.6217 | -3.4687 | 12.2017 | 11.815 | 11.7242 | 11.3385 | 10.915 | 10.3426 | 9.6742 | 8.9966 | 8.5487 | 5.9926 | 3.116 | -1.3381 | 8.7466 | 8.2997 | 8.2119 | 7.7762 | 7.3017 | 6.5374 | 5.6681 | 4.7987 | 4.2395 | 1.4262 | -0.71459 | -2.2738
|  | BAGSHOT PRIMARY | HT |  |  |  |  | 8.7915 | 8.5068 | 8.2272 | 7.8885 | 7.5242 | 6.9997 | 6.2497 | 5.5119 | 4.7528 | 0.62214 | -2.185 | -3.7401 | 12.5303 | 12.2966 | 12.0721 | 11.7885 | 11.4691 | 11.3803 | 10.9354 | 10.4762 | 9.9987 | 7.767 | 6.5497 | 5.9466 | 9.0354 | 8.6956 | 8.3711 | 7.964 | 7.5191 | 7.2283 | 6.4966 | 5.7558 | 4.9874 | 1.2007 | -1.2319 | -2.5187
|  | BAGSHOT PRIMARY | HE |  |  |  |  | 8.8323 | 8.5956 | 8.3181 | 8.013 | 7.6762 | 7.3058 | 6.6946 | 6.0711 | 5.4568 | 1.9089 | -0.90439 | -2.2064 | 12.4538 | 12.2007 | 11.9048 | 11.565 | 11.1854 | 11.0732 | 10.5793 | 10.0538 | 9.5099 | 6.4191 | 3.4293 | -0.77888 | 9.0589 | 8.7803 | 8.4405 | 8.066 | 7.6446 | 7.4823 | 6.8589 | 6.2109 | 5.5609 | 2.2844 | 0.093571 | -0.92173
|  | BAGSHOT PRIMARY | CF |  |  |  |  | 9.0844 | 8.9415 | 8.8323 | 8.6823 | 8.5191 | 8.316 | 8.2885 | 8.0538 | 7.8089 | 5.3477 | 2.7752 | 0.36398 | 12.5681 | 12.3385 | 12.1354 | 11.8711 | 11.5619 | 11.1895 | 11.114 | 10.7007 | 10.2599 | 7.0609 | 2.1772 | -6.4309 | 9.2946 | 9.0926 | 8.9293 | 8.7068 | 8.4477 | 8.1385 | 8.2762 | 7.9732 | 7.6528 | 5.3344 | 3.0028 | 0.94867
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BALL HILL PRIMARY | MINIMUM HEADROOM | SU 42417 63142 | NO | NO | 0.81 | 8.7673 | 8.6184 | 8.4204 | 8.2582 | 7.8633 | 7.5214 | 7.1898 | 6.3622 | 5.7163 | 4.1459 | 2.8602 | 1.4265 | 11.3449 | 11.2327 | 11.0714 | 10.9398 | 10.4582 | 10.1429 | 9.8367 | 8.9255 | 8.2367 | 6.6837 | 4.8 | 2.1439 | 9.1357 | 8.9888 | 8.7939 | 8.6337 | 8.1541 | 7.7929 | 7.4418 | 6.4796 | 5.7429 | 4.0888 | 2.5663 | 0.80816
|  | BALL HILL PRIMARY | EE |  |  |  |  | 8.7673 | 8.6184 | 8.4204 | 8.2582 | 7.9622 | 7.6061 | 7.2867 | 7.2327 | 6.999 | 5.6929 | 3.9224 | 3.2653 | 11.3449 | 11.2327 | 11.0786 | 10.9531 | 10.6786 | 10.3663 | 10.1122 | 10.0827 | 9.8745 | 8.6418 | 6.1653 | 4.5163 | 9.1357 | 8.9888 | 8.7939 | 8.6337 | 8.3173 | 7.9408 | 7.6184 | 7.6204 | 7.3837 | 6.0398 | 3.9143 | 3.1429
|  | BALL HILL PRIMARY | HT |  |  |  |  | 8.898 | 8.7347 | 8.5296 | 8.4112 | 8.0204 | 7.6796 | 7.3418 | 7.0612 | 6.6255 | 5.3439 | 3.548 | 2.2245 | 11.4776 | 11.3602 | 11.1939 | 11.1204 | 10.7296 | 10.4306 | 10.1337 | 9.9276 | 9.5327 | 8.4755 | 6.5265 | 5.0959 | 9.2755 | 9.1112 | 8.8959 | 8.7898 | 8.351 | 7.9867 | 7.6296 | 7.349 | 6.8765 | 5.5408 | 3.4286 | 1.8806
|  | BALL HILL PRIMARY | HE |  |  |  |  | 8.8929 | 8.7184 | 8.4704 | 8.3153 | 7.8633 | 7.5214 | 7.1898 | 6.3622 | 5.7163 | 4.1459 | 2.8602 | 1.4265 | 11.4469 | 11.302 | 11.0714 | 10.9398 | 10.4582 | 10.1429 | 9.8367 | 8.9255 | 8.2367 | 6.6837 | 4.8 | 2.1439 | 9.2724 | 9.0918 | 8.8235 | 8.6724 | 8.1541 | 7.7929 | 7.4418 | 6.4796 | 5.7429 | 4.0888 | 2.5663 | 0.80816
|  | BALL HILL PRIMARY | CF |  |  |  |  | 8.9194 | 8.8204 | 8.7092 | 8.551 | 8.4214 | 8.2276 | 8.0306 | 7.8694 | 7.6439 | 6.3071 | 5.5653 | 4.4837 | 11.4602 | 11.3888 | 11.301 | 11.1602 | 11.0347 | 10.8469 | 10.6571 | 10.4898 | 10.2643 | 8.7592 | 7.1704 | 4.3265 | 9.2888 | 9.1969 | 9.0878 | 8.9276 | 8.8 | 8.598 | 8.3929 | 8.2357 | 8.001 | 6.5786 | 5.8071 | 4.6133
MELKSHAM GSP | ANDOVER BSP | BARTON STACEY PRIMARY | MINIMUM HEADROOM | SU 42075 42720 | NO | NO | 0.57 | 7.5918 | 7.4633 | 7.3 | 7.1194 | 6.7612 | 6.4551 | 6.1122 | 5.3582 | 4.751 | 2.9571 | 1.6122 | 0.076531 | 8.7204 | 8.6276 | 8.4582 | 8.3102 | 7.8663 | 7.5694 | 7.2378 | 6.3847 | 5.7163 | 3.9367 | 2.0551 | -0.56327 | 7.7582 | 7.6408 | 7.4571 | 7.2847 | 6.8224 | 6.4949 | 6.1367 | 5.2378 | 4.5418 | 2.6408 | 1.0786 | -0.77857
|  | BARTON STACEY PRIMARY | EE |  |  |  |  | 7.5918 | 7.4633 | 7.3 | 7.1194 | 6.9041 | 6.5857 | 6.3173 | 5.9102 | 5.6969 | 4.5214 | 2.6847 | 1.9867 | 8.7204 | 8.6276 | 8.4929 | 8.352 | 8.1459 | 7.8602 | 7.65 | 7.2653 | 7.0745 | 5.9327 | 3.4449 | 1.8847 | 7.7582 | 7.6408 | 7.4939 | 7.3316 | 7.0969 | 6.7776 | 6.5194 | 6.0724 | 5.8541 | 4.6184 | 2.4418 | 1.6367
|  | BARTON STACEY PRIMARY | HT |  |  |  |  | 7.6837 | 7.5551 | 7.3806 | 7.2469 | 6.9184 | 6.6041 | 6.249 | 6.0592 | 5.6643 | 4.0857 | 2.2337 | 0.89592 | 8.8122 | 8.7173 | 8.5684 | 8.4694 | 8.1214 | 7.8347 | 7.5061 | 7.3765 | 6.998 | 5.5959 | 3.5969 | 2.151 | 7.8367 | 7.7061 | 7.5286 | 7.4031 | 7.0235 | 6.6898 | 6.3143 | 6.1214 | 5.6939 | 4.0133 | 1.8684 | 0.32245
|  | BARTON STACEY PRIMARY | HE |  |  |  |  | 7.6837 | 7.5449 | 7.3245 | 7.1531 | 6.7612 | 6.4551 | 6.1122 | 5.3582 | 4.751 | 2.9571 | 1.6122 | 0.076531 | 8.798 | 8.6796 | 8.4582 | 8.3102 | 7.8663 | 7.5694 | 7.2378 | 6.3847 | 5.7163 | 3.9367 | 2.0551 | -0.56327 | 7.8378 | 7.6939 | 7.4571 | 7.2847 | 6.8224 | 6.4949 | 6.1367 | 5.2378 | 4.5418 | 2.6408 | 1.0786 | -0.77857
|  | BARTON STACEY PRIMARY | CF |  |  |  |  | 7.7255 | 7.6449 | 7.5429 | 7.4112 | 7.2571 | 7.1204 | 6.9551 | 6.7776 | 6.6265 | 5.452 | 4.3592 | 3.3684 | 8.8276 | 8.7653 | 8.6847 | 8.5673 | 8.4173 | 8.2786 | 8.1071 | 7.9286 | 7.752 | 6.3827 | 4.5755 | 2.0367 | 7.8755 | 7.8 | 7.7051 | 7.5745 | 7.4224 | 7.2796 | 7.1163 | 6.9398 | 6.7745 | 5.5541 | 4.352 | 3.2878
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | BASINGSTOKE PRIMARY | MINIMUM HEADROOM | SU 65155 52705 | NO | NO | 2.036 | 18.3959 | 17.9163 | 17.4469 | 16.901 | 16.2235 | 15.5153 | 14.3643 | 13.1367 | 12.0388 | 8.3 | 6.4673 | 5.4684 | 17.4827 | 17.1908 | 16.9592 | 16.6582 | 16.2122 | 15.7867 | 15.0969 | 14.3173 | 13.602 | 11.3071 | 9.5776 | 4.3765 | 17.1949 | 16.7867 | 16.3918 | 15.9163 | 15.3133 | 14.7143 | 13.7469 | 12.6755 | 11.6857 | 8.3857 | 6.6143 | 5.6469
|  | BASINGSTOKE PRIMARY | EE |  |  |  |  | 18.3959 | 17.9163 | 17.4469 | 16.901 | 16.2235 | 15.5153 | 14.3643 | 13.1367 | 12.0388 | 8.4837 | 7.2643 | 6.5398 | 17.4827 | 17.1908 | 16.9592 | 16.6582 | 16.2122 | 15.7867 | 15.0969 | 14.3173 | 13.602 | 11.5459 | 9.7694 | 7.0959 | 17.1949 | 16.7867 | 16.3918 | 15.9163 | 15.3133 | 14.7143 | 13.7469 | 12.6755 | 11.6857 | 8.399 | 7.0867 | 6.2592
|  | BASINGSTOKE PRIMARY | HT |  |  |  |  | 18.6694 | 18.3571 | 17.9898 | 17.4806 | 16.8714 | 15.8878 | 14.749 | 13.7265 | 12.6541 | 8.6224 | 6.7571 | 5.7582 | 17.6286 | 17.4898 | 17.3153 | 17.0133 | 16.5724 | 16.0276 | 15.3633 | 14.7776 | 14.1806 | 11.8469 | 10.8051 | 10.2418 | 17.3949 | 17.1286 | 16.8153 | 16.3816 | 15.8592 | 14.9469 | 13.9061 | 12.9908 | 12.0245 | 8.4235 | 6.6286 | 5.6469
|  | BASINGSTOKE PRIMARY | HE |  |  |  |  | 18.7051 | 18.3337 | 17.95 | 17.5122 | 16.9531 | 16.201 | 15.15 | 14.1153 | 12.949 | 8.3 | 6.4673 | 5.4684 | 17.6357 | 17.4235 | 17.2306 | 17.0031 | 16.6867 | 16.2245 | 15.5939 | 14.9612 | 14.2041 | 11.3071 | 10.1327 | 7.5888 | 17.4408 | 17.1235 | 16.8061 | 16.4418 | 15.9694 | 15.3235 | 14.399 | 13.502 | 12.4786 | 8.3857 | 6.6143 | 5.6745
|  | BASINGSTOKE PRIMARY | CF |  |  |  |  | 19.0663 | 18.8908 | 18.652 | 18.4184 | 18.152 | 17.8316 | 17.3602 | 16.7918 | 16.1724 | 12.0418 | 9.1112 | 6.9704 | 17.7347 | 17.602 | 17.4265 | 17.2602 | 17.0643 | 16.8347 | 16.4959 | 16.099 | 15.6592 | 12.7837 | 9.5776 | 4.3765 | 17.6969 | 17.5704 | 17.3949 | 17.2031 | 16.9878 | 16.7122 | 16.2888 | 15.7796 | 15.2214 | 11.7357 | 9.1898 | 7.2153
NURSLING GSP | VELMORE BSP | BASSETT PRIMARY | MINIMUM HEADROOM | SU 42193 15958 | NO | YES | 4.695 | 10.3369 | 9.8359 | 9.4318 | 9.3298 | 8.8491 | 8.0195 | 7.1257 | 6.241 | 5.6053 | 2.092 | -0.88453 | -2.5988 | 13.7869 | 13.3002 | 12.9287 | 12.8114 | 12.3971 | 11.7746 | 11.0736 | 10.3655 | 9.8675 | 7.0593 | 2.5971 | -7.4529 | 11.3634 | 10.7828 | 10.3063 | 10.2308 | 9.7308 | 8.9359 | 8.0665 | 7.2083 | 6.6277 | 3.6716 | 1.1206 | -0.22127
|  | BASSETT PRIMARY | EE |  |  |  |  | 10.3369 | 9.8359 | 9.4318 | 9.3298 | 8.8491 | 8.0195 | 7.1257 | 6.241 | 5.6053 | 2.2757 | -0.28147 | -2.3845 | 13.7869 | 13.3002 | 12.9287 | 12.8114 | 12.3971 | 11.7746 | 11.0736 | 10.3655 | 9.8675 | 7.0593 | 3.6083 | -1.7345 | 11.3634 | 10.7828 | 10.3063 | 10.2308 | 9.7308 | 8.9359 | 8.0665 | 7.2083 | 6.6277 | 3.742 | 1.6144 | -0.081473
|  | BASSETT PRIMARY | HT |  |  |  |  | 10.3879 | 10.1022 | 9.8124 | 9.4583 | 9.0512 | 8.5971 | 7.8757 | 7.1379 | 6.3767 | 2.092 | -0.88453 | -2.5988 | 13.9246 | 13.7338 | 13.5471 | 13.2859 | 12.9706 | 12.8104 | 12.4114 | 11.993 | 11.5491 | 9.2379 | 7.8991 | 7.2349 | 11.4634 | 11.1665 | 10.8716 | 10.4849 | 10.0308 | 9.6685 | 8.9767 | 8.2634 | 7.5257 | 3.6716 | 1.1206 | -0.22127
|  | BASSETT PRIMARY | HE |  |  |  |  | 10.5624 | 10.1583 | 9.9012 | 9.6012 | 9.2502 | 8.9022 | 8.3175 | 7.7195 | 7.1053 | 3.6318 | 1.0124 | -0.21413 | 13.991 | 13.59 | 13.3563 | 13.0624 | 12.7042 | 12.4655 | 11.992 | 11.4951 | 10.9716 | 7.8032 | 4.2961 | -0.67739 | 11.6583 | 11.2073 | 10.944 | 10.6216 | 10.2318 | 9.9532 | 9.3716 | 8.7716 | 8.1542 | 5.0042 | 2.8624 | 1.9114
|  | BASSETT PRIMARY | CF |  |  |  |  | 10.7634 | 10.643 | 10.344 | 10.2083 | 10.0328 | 9.8185 | 9.5277 | 9.5338 | 9.2838 | 7.0746 | 4.6053 | 2.2216 | 14.0706 | 13.89 | 13.5114 | 13.2971 | 13.0053 | 12.6451 | 12.193 | 11.9951 | 11.5471 | 8.241 | 2.5971 | -7.4529 | 11.8471 | 11.7083 | 11.3563 | 11.2002 | 10.9961 | 10.7502 | 10.4002 | 10.4359 | 10.1512 | 8.0093 | 5.8563 | 3.7736
NORTH HYDE GSP | NORTH HYDE BSP | BATH ROAD EAST PRIMARY | MINIMUM HEADROOM | TQ 09097 76885 | NO | YES | 4.275 | 1.1112 | 0.78469 | 0.5551 | 25.5969 | 25.3612 | 25.0296 | 24.5827 | 24.15 | 23.9429 | 21.8878 | 21.101 | 20.752 | 2.499 | 2.2439 | 2.0408 | 25.2122 | 25.0041 | 24.7367 | 24.4316 | 24.1204 | 24.1378 | 22.6663 | 19.3867 | 13.4041 | 1.1184 | 0.77347 | 0.53776 | 24.6745 | 24.4459 | 24.1449 | 23.7847 | 23.4296 | 23.399 | 21.4531 | 20.7173 | 20.3867
|  | BATH ROAD EAST PRIMARY | EE |  |  |  |  | 1.1806 | 0.78469 | 0.5551 | 25.5969 | 25.3612 | 25.0296 | 24.5827 | 24.15 | 23.9429 | 22.7582 | 22.3847 | 22.4888 | 2.5857 | 2.2439 | 2.0408 | 25.2122 | 25.0041 | 24.7367 | 24.4316 | 24.1204 | 24.1378 | 22.799 | 21.0673 | 18.2714 | 1.149 | 0.77347 | 0.53776 | 24.6745 | 24.4459 | 24.1449 | 23.7847 | 23.4296 | 23.399 | 22.3163 | 21.9837 | 22.0714
|  | BATH ROAD EAST PRIMARY | HT |  |  |  |  | 1.1112 | 0.97959 | 0.82551 | 25.9827 | 25.8 | 25.5755 | 25.3531 | 25.0959 | 24.8143 | 23.3724 | 22.6531 | 22.4286 | 2.499 | 2.4429 | 2.3735 | 25.7031 | 25.5847 | 25.4449 | 25.3061 | 25.1398 | 24.9582 | 24.2255 | 23.7969 | 23.6071 | 1.1184 | 0.99082 | 0.84082 | 25.1102 | 24.9276 | 24.7071 | 24.4959 | 24.2367 | 23.9602 | 22.902 | 22.2388 | 22.0255
|  | BATH ROAD EAST PRIMARY | HE |  |  |  |  | 1.3082 | 0.97143 | 0.81939 | 25.952 | 25.7837 | 25.4286 | 24.9816 | 24.5255 | 24.0327 | 21.8878 | 21.101 | 21.0796 | 2.651 | 2.35 | 2.2357 | 25.4847 | 25.3286 | 25.1204 | 24.8837 | 24.6592 | 24.3888 | 22.8173 | 21.2918 | 18.452 | 1.3 | 0.98571 | 0.84082 | 25.0786 | 24.9357 | 24.7051 | 24.3388 | 23.9571 | 23.502 | 21.4531 | 20.7173 | 20.698
|  | BATH ROAD EAST PRIMARY | CF |  |  |  |  | 1.4418 | 1.3622 | 1.0551 | 26.2459 | 26.1255 | 26.0459 | 25.9265 | 25.7969 | 25.5061 | 23.7214 | 22.0255 | 20.752 | 2.7235 | 2.6612 | 2.3469 | 25.598 | 25.4224 | 25.2469 | 25.0184 | 24.7776 | 24.5153 | 22.6663 | 19.3867 | 13.4041 | 1.4204 | 1.3439 | 1.052 | 25.3459 | 25.2276 | 25.1551 | 25.0306 | 24.8908 | 24.7173 | 23.1827 | 21.5765 | 20.3867
IVER 132KV GSP | LONGFORD BSP | BATH ROAD WEST PRIMARY | MINIMUM HEADROOM | TQ 05814 76820 | NO | YES | 8.135 | 8.7249 | 8.231 | 7.6321 | 6.9566 | 6.18 | 5.3443 | 4.3382 | 3.3647 | 2.5402 | -0.51794 | -2.2486 | -3.0812 | 8.5198 | 8.3392 | 8.1168 | 7.681 | 7.1127 | 6.5188 | 5.7912 | 5.0933 | 4.5025 | 2.2433 | 0.98002 | 0.3739 | 8.929 | 8.4831 | 7.9453 | 7.3331 | 6.6321 | 5.8851 | 4.9759 | 4.1004 | 3.3617 | 0.50655 | -1.0822 | -1.7914
|  | BATH ROAD WEST PRIMARY | EE |  |  |  |  | 8.7249 | 8.231 | 7.6321 | 6.9566 | 6.18 | 5.3443 | 4.3382 | 3.3647 | 2.5402 | -0.032224 | -0.41692 | -0.39243 | 8.5198 | 8.3392 | 8.1168 | 7.681 | 7.1127 | 6.5188 | 5.7912 | 5.0933 | 4.5025 | 2.6963 | 2.4688 | 2.4147 | 8.929 | 8.4831 | 7.9453 | 7.3331 | 6.6321 | 5.8851 | 4.9759 | 4.1004 | 3.3617 | 1.0719 | 0.76676 | 0.75451
|  | BATH ROAD WEST PRIMARY | HT |  |  |  |  | 9.2249 | 8.9229 | 8.5688 | 8.1504 | 7.6637 | 7.1106 | 6.4076 | 5.6606 | 4.8759 | 1.3953 | 0.024918 | -0.51284 | 8.6708 | 8.5882 | 8.4882 | 8.3453 | 8.1739 | 7.8535 | 7.3627 | 6.8382 | 6.2872 | 3.8504 | 2.9035 | 2.5249 | 9.3851 | 9.1157 | 8.7994 | 8.427 | 7.9923 | 7.5014 | 6.88 | 6.2137 | 5.5188 | 2.4188 | 1.2055 | 0.72288
|  | BATH ROAD WEST PRIMARY | HE |  |  |  |  | 9.1198 | 8.7596 | 8.3402 | 7.8463 | 7.2719 | 6.5841 | 5.7361 | 4.8168 | 3.8423 | -0.51794 | -2.2486 | -3.0812 | 8.629 | 8.5198 | 8.3749 | 8.1902 | 7.9014 | 7.4137 | 6.8004 | 6.1382 | 5.428 | 2.2433 | 0.98002 | 0.3739 | 9.278 | 8.9535 | 8.5739 | 8.1259 | 7.6014 | 6.9831 | 6.2147 | 5.3841 | 4.4994 | 0.50655 | -1.0822 | -1.7914
|  | BATH ROAD WEST PRIMARY | CF |  |  |  |  | 9.5178 | 9.3259 | 9.0943 | 8.8321 | 8.5259 | 8.1821 | 7.7096 | 7.1892 | 6.6168 | 3.1566 | 0.15655 | -1.7353 | 8.7341 | 8.6678 | 8.5861 | 8.5014 | 8.3892 | 8.2535 | 8.0678 | 7.8117 | 7.3902 | 4.8525 | 2.679 | 1.28 | 9.6321 | 9.4586 | 9.2494 | 9.0076 | 8.7259 | 8.4157 | 7.9851 | 7.5096 | 6.9861 | 3.827 | 1.1076 | -0.60263
IVER 132KV GSP | DENHAM BSP | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | MINIMUM HEADROOM | SU 93668 91219 | NO | YES | 3.568 | 1.3286 | 0.90924 | 0.47659 | -0.10402 | 24.645 | 24.0429 | 23.7378 | 23.1205 | 22.6184 | 19.7786 | 18.1756 | 16.998 | 4.0439 | 3.8286 | 3.5623 | 6.0837 | 26.2735 | 25.8848 | 25.6633 | 25.2052 | 24.796 | 22.7082 | 21.7164 | 21.449 | 1.1909 | 0.8021 | 0.41128 | 2.7582 | 23.8205 | 23.246 | 23.0256 | 22.445 | 21.996 | 19.6623 | 18.0766 | 17.1123
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | EE |  |  |  |  | 1.3286 | 0.90924 | 0.47659 | -0.10402 | 24.645 | 24.0429 | 23.7378 | 23.1205 | 22.6184 | 20.1429 | 18.3725 | 17.0613 | 4.0439 | 3.8286 | 3.5623 | 6.0837 | 26.2735 | 25.8848 | 25.6633 | 25.2052 | 24.796 | 23.198 | 22.3868 | 21.9684 | 1.1909 | 0.8021 | 0.41128 | 2.7582 | 23.8205 | 23.246 | 23.0256 | 22.445 | 21.996 | 19.7899 | 18.247 | 17.1633
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | HT |  |  |  |  | 1.5256 | 1.1776 | 0.77863 | 0.32761 | 25.2041 | 24.6939 | 24.1164 | 23.5072 | 22.8664 | 20.1939 | 18.1756 | 16.998 | 4.1939 | 4.0643 | 3.8552 | 6.497 | 26.8062 | 26.5174 | 26.1654 | 25.7868 | 25.3827 | 23.5909 | 22.5225 | 21.9072 | 1.399 | 1.0868 | 0.72047 | 3.2154 | 24.4143 | 23.946 | 23.4072 | 22.8399 | 22.2399 | 19.8643 | 18.0766 | 17.1123
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | HE |  |  |  |  | 1.5215 | 1.1756 | 0.82047 | 0.36842 | 25.199 | 24.7419 | 24.2052 | 23.6378 | 23.1215 | 19.7786 | 18.2572 | 17.8103 | 4.1633 | 4.0154 | 3.8541 | 6.497 | 26.7603 | 26.4511 | 25.995 | 25.5021 | 25.097 | 22.7082 | 21.7164 | 21.449 | 1.3939 | 1.0807 | 0.77047 | 3.2643 | 24.4092 | 23.9858 | 23.4796 | 22.9399 | 22.7735 | 19.6623 | 18.2378 | 17.8266
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | CF |  |  |  |  | 1.7358 | 1.499 | 1.2286 | 0.9123 | 25.899 | 25.7011 | 25.4919 | 25.2164 | 24.9235 | 22.8603 | 20.5194 | 18.3674 | 4.2735 | 4.1766 | 4.0582 | 6.7664 | 27.1235 | 26.9756 | 26.8327 | 26.6276 | 26.4072 | 24.8266 | 23.1735 | 21.6939 | 1.5868 | 1.3735 | 1.1317 | 3.7399 | 25.0348 | 24.8368 | 24.6378 | 24.3633 | 24.0745 | 22.5786 | 20.3562 | 18.3184
IVER 132KV GSP | UPTON BSP | BEACONSFIELD (END BUSBARS) PRIMARY | MINIMUM HEADROOM | SU 93668 91219 | NO | YES | 0.669 | 1.8531 | 1.7347 | 1.5765 | 1.4449 | -5.1286 | -5.4214 | -5.752 | -5.6969 | -5.9959 | -6.9592 | -7.8184 | -8.3102 | 2.9571 | 2.8694 | 2.75 | 2.6633 | -3.5653 | -3.7459 | -3.9592 | -3.8408 | -3.9561 | -4.3388 | -4.699 | -4.8908 | 1.9735 | 1.8602 | 1.6939 | 4.4612 | -4.8235 | -5.1112 | -5.4439 | -5.3061 | -5.5816 | -6.4418 | -7.1908 | -7.6357
|  | BEACONSFIELD (END BUSBARS) PRIMARY | EE |  |  |  |  | 1.8531 | 1.7347 | 1.5765 | 1.4449 | -5.1286 | -5.4214 | -5.752 | -5.6939 | -5.8745 | -6.8214 | -7.6051 | -8.2296 | 2.9571 | 2.8694 | 2.75 | 2.6633 | -3.5653 | -3.7459 | -3.9592 | -3.8408 | -3.9276 | -4.301 | -4.601 | -4.8388 | 1.9735 | 1.8602 | 1.6939 | 4.4612 | -4.8235 | -5.1112 | -5.4439 | -5.3061 | -5.4684 | -6.3184 | -7.002 | -7.5684
|  | BEACONSFIELD (END BUSBARS) PRIMARY | HT |  |  |  |  | 1.9398 | 1.8469 | 1.7224 | 1.6306 | -4.9071 | -5.1704 | -5.4082 | -5.6969 | -5.9959 | -6.9592 | -7.8184 | -8.3102 | 3.0439 | 2.9867 | 2.9031 | 2.8449 | -3.349 | -3.4939 | -3.6153 | -3.7796 | -3.9561 | -4.3388 | -4.699 | -4.8908 | 2.0622 | 1.9745 | 1.8541 | 4.6684 | -4.5633 | -4.8082 | -5.0255 | -5.2949 | -5.5816 | -6.4418 | -7.1908 | -7.6357
|  | BEACONSFIELD (END BUSBARS) PRIMARY | HE |  |  |  |  | 1.9724 | 1.8714 | 1.7541 | 1.6724 | -4.8531 | -5.0612 | -5.2459 | -5.4796 | -5.7245 | -6.4939 | -7.2347 | -7.6429 | 3.0561 | 2.9816 | 2.898 | 2.8439 | -3.3429 | -3.4684 | -3.5673 | -3.7133 | -3.8694 | -4.1592 | -4.451 | -4.6041 | 2.0929 | 1.9949 | 1.8816 | 4.7051 | -4.5163 | -4.7184 | -4.8918 | -5.1235 | -5.3653 | -6.0133 | -6.6816 | -7.0347
|  | BEACONSFIELD (END BUSBARS) PRIMARY | CF |  |  |  |  | 2.0306 | 1.9765 | 1.9112 | 1.8306 | -4.6112 | -4.7031 | -4.8194 | -4.8959 | -5.0204 | -5.5041 | -6.2459 | -6.9306 | 3.0796 | 3.0316 | 2.9776 | 2.9163 | -3.2143 | -3.2857 | -3.3724 | -3.4235 | -3.5163 | -3.7663 | -4.1061 | -4.3653 | 2.1439 | 2.0918 | 2.0276 | 4.851 | -4.2939 | -4.3939 | -4.5173 | -4.5969 | -4.7296 | -5.1367 | -5.8 | -6.4092
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BEENHAM PRIMARY | MINIMUM HEADROOM | SU 58204 69025 | NO | NO | 0.73 | 5.8847 | 5.7143 | 5.5653 | 5.3612 | 5.1469 | 4.9265 | 4.6173 | 4.3102 | 4.1224 | 3.048 | 2.5092 | 2.3796 | 8.2224 | 8.0898 | 7.9847 | 7.8296 | 7.6612 | 7.5051 | 7.2663 | 7.0265 | 6.8949 | 6.2194 | 5.3541 | 3.5337 | 6.2745 | 6.1061 | 5.9633 | 5.7704 | 5.5612 | 5.352 | 5.0551 | 4.7592 | 4.5827 | 3.7714 | 3.2582 | 3.1347
|  | BEENHAM PRIMARY | EE |  |  |  |  | 5.8847 | 5.7143 | 5.5653 | 5.3612 | 5.1469 | 4.9265 | 4.6173 | 4.3102 | 4.1224 | 3.2908 | 3.0286 | 2.9173 | 8.2224 | 8.0898 | 7.9847 | 7.8296 | 7.6612 | 7.5051 | 7.2663 | 7.0265 | 6.8949 | 6.2449 | 5.7122 | 4.8878 | 6.2745 | 6.1061 | 5.9633 | 5.7704 | 5.5612 | 5.352 | 5.0551 | 4.7592 | 4.5827 | 3.8224 | 3.5969 | 3.498
|  | BEENHAM PRIMARY | HT |  |  |  |  | 5.9908 | 5.8786 | 5.749 | 5.6051 | 5.4816 | 5.2816 | 5.05 | 4.849 | 4.601 | 3.5031 | 3.0459 | 2.8235 | 8.3276 | 8.2582 | 8.1765 | 8.0755 | 7.9969 | 7.8694 | 7.7133 | 7.6 | 7.4316 | 6.7224 | 6.4571 | 6.35 | 6.3857 | 6.2806 | 6.1571 | 6.0163 | 5.898 | 5.7061 | 5.4827 | 5.2949 | 5.0571 | 4.0163 | 3.5949 | 3.4112
|  | BEENHAM PRIMARY | HE |  |  |  |  | 5.9776 | 5.8602 | 5.7286 | 5.5776 | 5.4367 | 5.2327 | 4.9908 | 4.7337 | 4.4439 | 3.048 | 2.5092 | 2.3796 | 8.302 | 8.2286 | 8.1296 | 8.0153 | 7.9163 | 7.7704 | 7.5929 | 7.4347 | 7.2378 | 6.2194 | 5.5755 | 4.7663 | 6.3724 | 6.2643 | 6.1347 | 5.9908 | 5.8694 | 5.6724 | 5.4429 | 5.2418 | 4.9929 | 3.7714 | 3.2582 | 3.1347
|  | BEENHAM PRIMARY | CF |  |  |  |  | 6.0388 | 5.9347 | 5.8449 | 5.7408 | 5.6214 | 5.5296 | 5.3847 | 5.2245 | 5.0582 | 4.15 | 3.2663 | 2.5929 | 8.3418 | 8.2571 | 8.198 | 8.1143 | 8.0143 | 7.9276 | 7.7929 | 7.649 | 7.4969 | 6.552 | 5.3541 | 3.5337 | 6.4347 | 6.3327 | 6.252 | 6.152 | 6.0378 | 5.952 | 5.8102 | 5.6541 | 5.4898 | 4.6245 | 3.9653 | 3.3357
MANNINGTON GSP | SALISBURY BSP | BEMERTON PRIMARY | MINIMUM HEADROOM | SU 11583 31233 | NO | NO | 2.196 | 16.7672 | 16.0998 | 15.3692 | 14.4631 | 14.1488 | 13.2498 | 12.3376 | 11.6365 | 11.1192 | 8.2906 | 6.0631 | 4.8804 | 19.7927 | 19.2314 | 18.6192 | 17.9855 | 17.9335 | 17.3896 | 16.8008 | 16.2927 | 15.9325 | 13.8774 | 11.6712 | 5.5835 | 17.4192 | 16.7804 | 16.0865 | 15.2651 | 15.0467 | 14.2437 | 13.4049 | 12.7274 | 12.2661 | 9.8172 | 7.86 | 6.8723
|  | BEMERTON PRIMARY | EE |  |  |  |  | 16.7672 | 16.0998 | 15.3692 | 14.4631 | 14.1488 | 13.2498 | 12.3376 | 11.6365 | 11.1192 | 8.3763 | 6.4835 | 5.261 | 19.7927 | 19.2314 | 18.6192 | 17.9855 | 17.9335 | 17.3896 | 16.8008 | 16.2927 | 15.9325 | 13.8774 | 11.7304 | 8.6253 | 17.4192 | 16.7804 | 16.0865 | 15.2651 | 15.0467 | 14.2437 | 13.4049 | 12.7274 | 12.2661 | 9.8682 | 8.2243 | 7.1896
|  | BEMERTON PRIMARY | HT |  |  |  |  | 17.0039 | 16.4018 | 15.7569 | 15.0855 | 14.4192 | 13.5345 | 13.009 | 12.3886 | 11.7488 | 8.2906 | 6.0631 | 4.8804 | 20.0559 | 19.5794 | 19.0906 | 18.6947 | 18.3161 | 17.8314 | 17.6263 | 17.2947 | 16.958 | 15.1202 | 14.0457 | 13.4957 | 17.658 | 17.1039 | 16.508 | 15.9294 | 15.3345 | 14.5508 | 14.1345 | 13.56 | 12.9672 | 9.8172 | 7.86 | 6.8723
|  | BEMERTON PRIMARY | HE |  |  |  |  | 17.0274 | 16.4467 | 15.8243 | 15.0947 | 14.5018 | 13.7192 | 13.2865 | 12.7651 | 12.2304 | 9.4039 | 7.6335 | 6.8172 | 20.0284 | 19.5151 | 19.009 | 18.4845 | 18.1212 | 17.659 | 17.4131 | 17.0651 | 16.6988 | 14.4855 | 12.3274 | 9.4202 | 17.6794 | 17.1396 | 16.5712 | 15.9447 | 15.4151 | 14.7223 | 14.3896 | 13.9049 | 13.4049 | 10.8243 | 9.2896 | 8.6304
|  | BEMERTON PRIMARY | CF |  |  |  |  | 17.2335 | 16.7488 | 16.2447 | 15.6253 | 15.2212 | 14.7498 | 14.3018 | 14.0192 | 14.0753 | 12.2559 | 10.2172 | 8.2406 | 20.1233 | 19.6467 | 19.1896 | 18.6988 | 18.4059 | 18.0457 | 17.6794 | 17.3886 | 17.309 | 15.1916 | 11.6712 | 5.5835 | 17.8682 | 17.4223 | 16.961 | 16.4284 | 16.0835 | 15.6712 | 15.261 | 14.9763 | 15.0784 | 13.3294 | 11.5386 | 9.8192
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | BERINSFIELD PRIMARY | MINIMUM HEADROOM | SU 58382 95467 | NO | NO | 5.4 | 9.0096 | 8.3566 | 6.68 | 5.0117 | 0.79124 | -2.7088 | -6.6118 | -9.0955 | -14.7312 | -32.2302 | -47.0639 | -55.7955 | 12.0953 | 11.529 | 10.1841 | 9.1831 | 5.5035 | 2.9372 | 0.098388 | -1.1149 | -6.1414 | -19.4986 | -32.871 | -43.5455 | 9.2198 | 8.53 | 6.8555 | 5.381 | 1.03 | -2.2486 | -5.8914 | -7.8373 | -13.6445 | -30.2251 | -45.7077 | -56.2537
|  | BERINSFIELD PRIMARY | EE |  |  |  |  | 9.0096 | 8.3974 | 7.378 | 5.8841 | 3.4351 | 0.14431 | -2.8945 | -6.8373 | -10.2118 | -25.7812 | -43.0924 | -48.3159 | 12.0953 | 11.7739 | 11.2974 | 10.5178 | 8.9014 | 6.6494 | 4.9402 | 2.0882 | -0.12202 | -10.9792 | -28.7026 | -36.172 | 9.2198 | 8.6545 | 7.8004 | 6.5627 | 4.3923 | 1.4086 | -1.1312 | -4.8016 | -7.8067 | -21.9588 | -40.8343 | -46.9792
|  | BERINSFIELD PRIMARY | HT |  |  |  |  | 9.0963 | 8.4178 | 7.0504 | 5.6484 | 1.88 | -1.7669 | -5.8832 | -8.7771 | -13.0608 | -30.219 | -47.0639 | -55.7955 | 12.2127 | 11.6974 | 10.7729 | 10.1637 | 7.1004 | 4.4637 | 1.478 | -0.121 | -3.3343 | -15.5047 | -31.6434 | -41.7996 | 9.3678 | 8.6208 | 7.3372 | 6.2025 | 2.4249 | -1.0108 | -4.8843 | -7.3098 | -11.4026 | -27.4557 | -45.7077 | -56.2537
|  | BERINSFIELD PRIMARY | HE |  |  |  |  | 9.0994 | 8.3566 | 6.68 | 5.0117 | 0.79124 | -2.7088 | -6.6118 | -9.0955 | -14.7312 | -32.2302 | -46.0128 | -53.5639 | 12.1851 | 11.529 | 10.1841 | 9.1831 | 5.5035 | 2.9372 | 0.098388 | -1.1149 | -6.1414 | -19.4986 | -32.871 | -43.5455 | 9.3851 | 8.53 | 6.8555 | 5.381 | 1.03 | -2.2486 | -5.8914 | -7.8373 | -13.6445 | -30.2251 | -44.7098 | -53.8894
|  | BERINSFIELD PRIMARY | CF |  |  |  |  | 9.1943 | 8.93 | 8.1657 | 6.7514 | 4.729 | 2.2453 | -0.4659 | -3.2047 | -5.7496 | -19.3149 | -30.0975 | -36.3822 | 12.2627 | 12.0096 | 11.63 | 10.7821 | 9.5382 | 7.881 | 6.1474 | 4.4086 | 2.7453 | -6.872 | -16.8475 | -26.3404 | 9.5586 | 9.1698 | 8.5463 | 7.331 | 5.6066 | 3.4566 | 1.1606 | -1.1588 | -3.3434 | -15.4873 | -26.0016 | -32.9434
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | BEVOIS VALLEY PRIMARY | MINIMUM HEADROOM | SU 42648 13187 | NO | YES | 3.088 | 7.0862 | 6.6485 | 6.1842 | 5.4444 | 4.7811 | 4.1852 | 3.4352 | 2.6913 | 2.1444 | -0.60253 | -2.9219 | -4.3382 | 11.724 | 11.4403 | 11.1373 | 10.6883 | 10.2342 | 9.672 | 8.9679 | 8.2505 | 7.6424 | 4.174 | -1.9138 | -15.1107 | 9.0791 | 8.6628 | 8.222 | 7.5332 | 6.8862 | 6.3087 | 5.5679 | 4.8271 | 4.2658 | 1.723 | -0.26069 | -1.4811
|  | BEVOIS VALLEY PRIMARY | EE |  |  |  |  | 7.0862 | 6.6485 | 6.1842 | 5.4444 | 4.7811 | 4.1852 | 3.4352 | 2.6913 | 2.1444 | -0.60253 | -2.474 | -4.178 | 11.724 | 11.4403 | 11.1373 | 10.6883 | 10.2342 | 9.672 | 8.9679 | 8.2505 | 7.6424 | 4.174 | 0.15767 | -6.7352 | 9.0791 | 8.6628 | 8.222 | 7.5332 | 6.8862 | 6.3087 | 5.5679 | 4.8271 | 4.2658 | 1.723 | 0.086245 | -1.4087
|  | BEVOIS VALLEY PRIMARY | HT |  |  |  |  | 7.3771 | 7.0862 | 6.7281 | 6.1016 | 5.6648 | 5.2107 | 4.6771 | 4.0995 | 3.5475 | -0.097429 | -2.9219 | -4.3382 | 11.975 | 11.8291 | 11.6597 | 11.3169 | 11.0801 | 10.8607 | 10.5995 | 10.3016 | 9.9097 | 7.6087 | 6.0087 | 5.3383 | 9.3873 | 9.1067 | 8.774 | 8.1924 | 7.775 | 7.3424 | 6.8128 | 6.2454 | 5.6975 | 2.3118 | -0.26069 | -1.4811
|  | BEVOIS VALLEY PRIMARY | HE |  |  |  |  | 7.3383 | 7.0587 | 6.7393 | 6.1913 | 5.7291 | 5.3393 | 4.8505 | 4.3332 | 3.825 | 0.91073 | -0.98008 | -1.7148 | 11.8516 | 11.626 | 11.3771 | 11.0046 | 10.6301 | 10.2893 | 9.8934 | 9.4648 | 8.9332 | 5.3097 | 1.1138 | -5.3372 | 9.3658 | 9.0944 | 8.775 | 8.2791 | 7.8281 | 7.4332 | 6.9413 | 6.4199 | 5.926 | 3.2434 | 1.5832 | 0.96584
|  | BEVOIS VALLEY PRIMARY | CF |  |  |  |  | 7.9393 | 7.7097 | 7.426 | 7.0689 | 6.6485 | 6.3403 | 6.0546 | 5.8209 | 5.5301 | 3.6913 | 1.7444 | -0.087224 | 12.1373 | 11.9067 | 11.6556 | 11.3434 | 10.9638 | 10.5832 | 10.1873 | 9.7924 | 9.2822 | 5.3056 | -1.9138 | -15.1107 | 9.9067 | 9.6556 | 9.3862 | 9.0618 | 8.6822 | 8.3913 | 8.1148 | 7.8822 | 7.6005 | 5.8475 | 3.9832 | 2.3322
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER PRIMARY | MINIMUM HEADROOM | SP 58381 21988 | NO | YES | 24.329 | 19.5994 | 18.6994 | 17.9035 | 16.6861 | 15.3198 | 13.2586 | 11.1504 | 9.2167 | 7.6626 | -0.0067429 | -5.5159 | -8.2088 | 22.2116 | 21.5841 | 21.1443 | 20.3953 | 19.5728 | 18.2575 | 16.9075 | 15.6402 | 14.6759 | 10.2749 | 6.3371 | -1.8527 | 17.8759 | 17.0239 | 16.4177 | 15.3392 | 14.1371 | 12.3392 | 10.4688 | 8.7402 | 7.4157 | 1.4463 | -3.119 | -5.3129
|  | BICESTER PRIMARY | EE |  |  |  |  | 19.5994 | 18.6994 | 17.9035 | 16.6861 | 15.3198 | 13.2586 | 11.1504 | 9.2167 | 7.6626 | 0.21673 | -4.9027 | -7.9108 | 22.2116 | 21.5841 | 21.1443 | 20.3953 | 19.5728 | 18.2575 | 16.9075 | 15.6402 | 14.6759 | 10.2749 | 6.3371 | 1.7351 | 17.8759 | 17.0239 | 16.4177 | 15.3392 | 14.1371 | 12.3392 | 10.4688 | 8.7402 | 7.4157 | 1.4994 | -2.6088 | -5.118
|  | BICESTER PRIMARY | HT |  |  |  |  | 19.8718 | 19.1035 | 18.0626 | 16.8892 | 15.9065 | 13.8249 | 11.7637 | 9.8902 | 8.2249 | -0.0067429 | -5.5159 | -8.2088 | 22.5739 | 22.1698 | 21.6035 | 20.9718 | 20.5565 | 19.2749 | 18.0228 | 16.9024 | 16.0096 | 11.9963 | 9.3882 | 8.0851 | 18.2463 | 17.5769 | 16.68 | 15.6677 | 14.9453 | 13.2106 | 11.4626 | 9.8484 | 8.3994 | 1.4463 | -3.119 | -5.3129
|  | BICESTER PRIMARY | HE |  |  |  |  | 19.9055 | 19.1718 | 18.1637 | 17.0259 | 16.078 | 14.2871 | 12.4963 | 10.8453 | 9.2463 | 1.6116 | -3.6078 | -5.6833 | 22.4728 | 22.0137 | 21.4014 | 20.728 | 20.2667 | 19.0871 | 17.9218 | 16.828 | 15.7861 | 10.9055 | 6.831 | 2.6831 | 18.2647 | 17.6228 | 16.7545 | 15.7708 | 15.081 | 13.582 | 12.0504 | 10.6167 | 9.2167 | 2.7769 | -1.468 | -3.1353
|  | BICESTER PRIMARY | CF |  |  |  |  | 20.3453 | 19.9453 | 19.5524 | 19.0106 | 18.2708 | 17.3484 | 16.0453 | 14.8228 | 13.7218 | 7.1494 | 1.3208 | -2.7741 | 22.6708 | 22.3463 | 22.0167 | 21.6106 | 21.079 | 20.4208 | 19.4606 | 18.5453 | 17.6943 | 12.5933 | 6.5545 | -1.8527 | 18.6484 | 18.2698 | 17.9086 | 17.4106 | 16.7555 | 16.0973 | 14.9963 | 13.9504 | 12.9922 | 7.3147 | 2.5708 | -0.66389
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH PRIMARY | MINIMUM HEADROOM | SP 59720 23735 | NO | YES | 35.918 | -14.3449 | -14.7756 | -15.246 | -15.0562 | -15.4674 | -16.0378 | -16.7102 | -17.3868 | -17.6204 | -19.547 | -21.7204 | -23.0551 | -12.0858 | -12.2184 | -12.3613 | -12.3582 | -12.5623 | -12.9704 | -13.4307 | -13.9 | -14.1613 | -15.3837 | -16.2541 | -17.0296 | -13.4204 | -13.6429 | -13.8817 | -13.9449 | -14.1786 | -14.6878 | -15.2878 | -15.9062 | -16.3837 | -19.3164 | -21.5 | -22.7347
|  | BICESTER NORTH PRIMARY | EE |  |  |  |  | -14.3449 | -14.7756 | -15.246 | -15.0562 | -15.4674 | -16.0378 | -16.7102 | -17.3868 | -17.6204 | -19.3796 | -21.4184 | -22.9735 | -12.0858 | -12.2184 | -12.3613 | -12.3582 | -12.5623 | -12.9704 | -13.4307 | -13.9 | -14.1613 | -15.3837 | -16.2541 | -17.0296 | -13.4204 | -13.6429 | -13.8817 | -13.9317 | -14.1694 | -14.6878 | -15.2878 | -15.9062 | -16.3837 | -19.096 | -21.1756 | -22.6725
|  | BICESTER NORTH PRIMARY | HT |  |  |  |  | -13.9735 | -14.2551 | -14.4939 | -14.8266 | -15.1898 | -15.1817 | -15.6613 | -16.1796 | -16.7102 | -19.547 | -21.7204 | -23.0551 | -12.0164 | -12.1184 | -12.2092 | -12.3398 | -12.4735 | -12.6062 | -12.8653 | -13.1511 | -13.5215 | -15.299 | -16.2378 | -16.697 | -13.3429 | -13.5378 | -13.7164 | -13.9449 | -14.1786 | -14.5378 | -15.0511 | -15.5715 | -16.0888 | -19.3164 | -21.5 | -22.7347
|  | BICESTER NORTH PRIMARY | HE |  |  |  |  | -13.9674 | -14.2439 | -14.4725 | -14.7837 | -15.1398 | -15.0327 | -15.4511 | -15.898 | -16.3684 | -18.5327 | -20.4684 | -21.3949 | -12.0072 | -12.1082 | -12.1929 | -12.3051 | -12.4388 | -12.5307 | -12.7409 | -12.9572 | -13.2837 | -14.8021 | -15.6562 | -16.1694 | -13.3143 | -13.4939 | -13.6551 | -13.849 | -14.0684 | -14.3153 | -14.7215 | -15.1337 | -15.547 | -18.1164 | -20.0837 | -20.9653
|  | BICESTER NORTH PRIMARY | CF |  |  |  |  | -13.8725 | -14.0327 | -14.2378 | -14.4 | -14.6337 | -14.9184 | -15.2674 | -14.9613 | -15.2368 | -17.0164 | -18.0582 | -19.35 | -11.9439 | -11.9909 | -12.0541 | -12.1011 | -12.1756 | -12.2786 | -12.3939 | -12.3592 | -12.4511 | -13.65 | -14.7511 | -15.8358 | -13.1572 | -13.2419 | -13.3409 | -13.4235 | -13.5327 | -13.6786 | -13.847 | -13.8235 | -13.9613 | -15.3939 | -17.2378 | -19.0378
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BILLINGSHURST PRIMARY | MINIMUM HEADROOM | TQ 08305 26315 | YES | YES | 1.787 | 5.7439 | 5.4255 | 5.1276 | 4.8051 | 4.4714 | 4.3041 | 3.7653 | 3.2306 | 2.8265 | 0.51224 | -1.1469 | -2.1551 | 6.9916 | 6.7406 | 6.512 | 6.2498 | 5.9692 | 5.8978 | 5.5161 | 5.1345 | 4.8467 | 3.2406 | 1.1784 | -3.4471 | 5.5845 | 5.2712 | 4.9957 | 4.6702 | 4.3304 | 4.2733 | 3.7773 | 3.2773 | 2.9273 | 1.0202 | -0.39612 | -1.2176
|  | BILLINGSHURST PRIMARY | EE |  |  |  |  | 5.7439 | 5.4255 | 5.1276 | 4.8051 | 4.4714 | 4.3041 | 3.7653 | 3.2306 | 2.8265 | 0.7398 | -0.7 | -1.7816 | 6.9916 | 6.7406 | 6.512 | 6.2498 | 5.9692 | 5.8978 | 5.5161 | 5.1345 | 4.8467 | 3.2406 | 1.5416 | -0.96245 | 5.5845 | 5.2712 | 4.9957 | 4.6702 | 4.3304 | 4.2733 | 3.7773 | 3.2773 | 2.9273 | 1.1804 | -0.028776 | -0.93184
|  | BILLINGSHURST PRIMARY | HT |  |  |  |  | 5.8673 | 5.5969 | 5.352 | 5.0745 | 4.8306 | 4.3684 | 3.8316 | 3.2786 | 3.0837 | 0.51224 | -1.1469 | -2.1551 | 7.1457 | 6.9661 | 6.8151 | 6.6386 | 6.4835 | 6.2253 | 5.911 | 5.5855 | 5.5467 | 4.1671 | 3.3518 | 2.8671 | 5.7427 | 5.4906 | 5.2692 | 5.0059 | 4.7896 | 4.3784 | 3.8896 | 3.3773 | 3.2845 | 1.0202 | -0.39612 | -1.2176
|  | BILLINGSHURST PRIMARY | HE |  |  |  |  | 5.8969 | 5.6735 | 5.4133 | 5.1714 | 4.9663 | 4.5847 | 4.1316 | 3.6612 | 3.5582 | 1.3612 | -0.061224 | -0.82143 | 7.112 | 6.9376 | 6.7427 | 6.5447 | 6.3733 | 6.108 | 5.7784 | 5.4345 | 5.3743 | 3.5886 | 1.8702 | -0.49408 | 5.7631 | 5.558 | 5.3182 | 5.0865 | 4.9008 | 4.5539 | 4.1365 | 3.6998 | 3.6804 | 1.7488 | 0.55286 | -0.057347
|  | BILLINGSHURST PRIMARY | CF |  |  |  |  | 6.0265 | 5.8429 | 5.6724 | 5.5061 | 5.3469 | 5.201 | 4.9561 | 4.699 | 4.4357 | 3.2265 | 1.7184 | 0.35204 | 7.1712 | 7.0039 | 6.8518 | 6.6916 | 6.5192 | 6.3376 | 6.0794 | 5.8008 | 5.51 | 3.9304 | 1.1784 | -3.4471 | 5.8733 | 5.6988 | 5.5447 | 5.3824 | 5.2202 | 5.0896 | 4.8508 | 4.5998 | 4.3386 | 3.3273 | 2.0478 | 0.9202
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BILSHAM PRIMARY | MINIMUM HEADROOM | SU 97366 01594 | NO | YES | 18.122 | 0.33245 | -0.92061 | -2.7614 | 24.9712 | 22.1978 | 19.7253 | 17.5937 | 15.7222 | 14.0386 | 4.3988 | 0.92939 | -1.1757 | -7.4216 | -8.3839 | -9.1716 | 19.8427 | 18.6518 | 17.5569 | 16.5774 | 15.6978 | 14.8978 | 10.1967 | 7.6386 | 1.2161 | -7.089 | -8.5665 | -10.0247 | 18.2018 | 16.0069 | 14.1059 | 12.4641 | 11.0202 | 9.6855 | 1.9365 | -0.92367 | -2.6431
|  | BILSHAM PRIMARY | EE |  |  |  |  | 0.3498 | -0.92061 | -2.7614 | 24.9712 | 22.1978 | 19.7253 | 17.5937 | 15.7222 | 14.0386 | 4.6539 | 1.609 | -0.68693 | -7.3961 | -8.3839 | -9.1716 | 19.8427 | 18.6518 | 17.5569 | 16.5774 | 15.6978 | 14.8978 | 10.1967 | 7.6386 | 4.0947 | -7.0573 | -8.5665 | -10.0247 | 18.2018 | 16.0069 | 14.1059 | 12.4641 | 11.0202 | 9.6855 | 2.1314 | -0.44 | -2.29
|  | BILSHAM PRIMARY | HT |  |  |  |  | 0.33245 | -0.71755 | -2.6165 | 25.1549 | 22.3243 | 20.0794 | 17.9457 | 16.1743 | 14.3896 | 4.3988 | 0.92939 | -1.1757 | -7.4216 | -8.1288 | -8.9604 | 20.1192 | 18.9539 | 18.0427 | 17.1365 | 16.3682 | 15.5916 | 11.3508 | 9.8855 | 8.9906 | -7.089 | -8.3706 | -9.9288 | 18.3192 | 16.0763 | 14.2855 | 12.6171 | 11.2161 | 9.808 | 1.9365 | -0.92367 | -2.6431
|  | BILSHAM PRIMARY | HE |  |  |  |  | 0.51613 | -0.69204 | -2.5216 | 25.2825 | 22.5722 | 20.5825 | 18.6763 | 17.011 | 15.3355 | 5.8947 | 2.9498 | 1.4161 | -7.2543 | -8.189 | -9.039 | 20.01 | 18.8488 | 17.9865 | 17.1049 | 16.309 | 15.4927 | 10.7049 | 8.1345 | 4.9692 | -6.8839 | -8.3226 | -9.8584 | 18.409 | 16.2508 | 14.6641 | 13.1682 | 11.8559 | 10.5294 | 2.9998 | 0.44572 | -0.86551
|  | BILSHAM PRIMARY | CF |  |  |  |  | 0.86102 | -0.092037 | -1.4604 | 26.7386 | 24.6947 | 23.0814 | 22.1355 | 21.16 | 20.1314 | 11.2192 | 7.6927 | 4.1957 | -7.0114 | -7.6859 | -8.6114 | 20.5947 | 19.6896 | 18.9233 | 18.4253 | 17.8896 | 17.3141 | 12.3927 | 8.3345 | 1.2161 | -6.4104 | -7.5155 | -8.9308 | 19.6886 | 18.0967 | 16.9008 | 16.1447 | 15.4039 | 14.6212 | 7.8008 | 4.7437 | 1.7284
FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD PRIMARY | MINIMUM HEADROOM | SZ 56409 91399 | NO | YES | 0.137 | 8.4857 | 8.1704 | 7.7827 | 7.3469 | 6.8776 | 6.6714 | 5.9959 | 5.3418 | 4.8245 | 1.4724 | -0.28776 | -0.56735 | 9.1561 | 8.9102 | 8.6031 | 8.252 | 7.8735 | 7.7643 | 7.2796 | 6.799 | 6.4602 | 4.0653 | 2.6357 | -1.5112 | 8.3469 | 8.0439 | 7.6704 | 7.25 | 6.7959 | 6.6224 | 5.9878 | 5.3673 | 4.9316 | 1.901 | 0.25 | 0.0040816
|  | BINSTEAD PRIMARY | EE |  |  |  |  | 8.4857 | 8.1704 | 7.7827 | 7.3469 | 6.8776 | 6.6714 | 5.9959 | 5.3418 | 4.8245 | 2.6041 | 1.1378 | 0.012245 | 9.1561 | 8.9102 | 8.6031 | 8.252 | 7.8735 | 7.7643 | 7.2796 | 6.799 | 6.4602 | 4.7878 | 3.2551 | 1.0633 | 8.3469 | 8.0439 | 7.6704 | 7.25 | 6.7959 | 6.6224 | 5.9878 | 5.3673 | 4.9316 | 2.9112 | 1.6541 | 0.72653
|  | BINSTEAD PRIMARY | HT |  |  |  |  | 8.7806 | 8.5653 | 8.2969 | 7.9959 | 7.7112 | 7.1704 | 6.5541 | 6.2898 | 5.6898 | 2.7765 | 0.95306 | 0.017347 | 9.4245 | 9.2837 | 9.1051 | 8.8969 | 8.7031 | 8.3776 | 7.999 | 7.9102 | 7.552 | 5.9051 | 5.0102 | 4.6224 | 8.6378 | 8.4337 | 8.1786 | 7.8918 | 7.6245 | 7.1204 | 6.548 | 6.3296 | 5.7776 | 3.1235 | 1.5296 | 0.76939
|  | BINSTEAD PRIMARY | HE |  |  |  |  | 8.7276 | 8.4888 | 8.1929 | 7.8592 | 7.5347 | 7.0122 | 6.3235 | 5.7224 | 4.9755 | 1.4724 | -0.28776 | -0.56735 | 9.3357 | 9.148 | 8.9194 | 8.65 | 8.3857 | 8.0133 | 7.5673 | 7.1449 | 6.5949 | 4.0653 | 2.6357 | 0.59592 | 8.5857 | 8.3582 | 8.0745 | 7.7531 | 7.4459 | 6.9622 | 6.3888 | 5.9541 | 5.2388 | 1.901 | 0.25 | 0.0040816
|  | BINSTEAD PRIMARY | CF |  |  |  |  | 8.9388 | 8.7786 | 8.6286 | 8.4214 | 8.1888 | 7.9806 | 7.6796 | 7.349 | 7.002 | 4.8061 | 2.5541 | 1.1347 | 9.4622 | 9.3153 | 9.1724 | 8.9837 | 8.7541 | 8.5388 | 8.2347 | 7.9031 | 7.55 | 5.7122 | 2.8214 | -1.5112 | 8.7867 | 8.6296 | 8.4867 | 8.2898 | 8.0694 | 7.8745 | 7.5837 | 7.2663 | 6.9327 | 5.0653 | 2.9316 | 1.6071
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BIRDHAM PRIMARY | MINIMUM HEADROOM | SZ 81965 99422 | NO | YES | 4.59 | -0.53162 | -0.90407 | -1.3888 | 14.1408 | 13.6184 | 12.8653 | 12.0296 | 11.2388 | 10.7 | 7.7755 | 5.5459 | 4.3367 | 1.2286 | 0.93777 | 0.56532 | 0.45511 | 14.5653 | 14.0674 | 13.499 | 12.9408 | 12.5592 | 10.4765 | 7.798 | 1.6418 | -0.059173 | -0.42652 | -0.89795 | -1.0377 | 13.6714 | 12.9806 | 12.2123 | 11.4816 | 10.9878 | 8.4388 | 6.5459 | 5.5735
|  | BIRDHAM PRIMARY | EE |  |  |  |  | -0.53162 | -0.90407 | -1.3888 | 14.1408 | 13.6184 | 12.8653 | 12.0296 | 11.2388 | 10.7 | 7.9755 | 6.0378 | 4.65 | 1.2286 | 0.93777 | 0.56532 | 0.45511 | 14.5653 | 14.0674 | 13.499 | 12.9408 | 12.5592 | 10.4765 | 8.3255 | 5.1867 | -0.059173 | -0.42652 | -0.89795 | -1.0377 | 13.6714 | 12.9806 | 12.2123 | 11.4816 | 10.9878 | 8.5602 | 6.9755 | 5.8327
|  | BIRDHAM PRIMARY | HT |  |  |  |  | -0.33877 | -0.65611 | -1.0326 | 14.2572 | 13.7623 | 13.0112 | 12.5735 | 11.8612 | 11.1776 | 7.7755 | 5.5459 | 4.3367 | 1.4725 | 1.2847 | 1.0561 | 0.79185 | 14.9867 | 14.5694 | 14.4204 | 14.0133 | 13.6112 | 11.7408 | 10.6878 | 10.1623 | 0.13572 | -0.13366 | -0.46938 | -0.85611 | 13.8806 | 13.2 | 12.85 | 12.1918 | 11.55 | 8.4388 | 6.5459 | 5.5735
|  | BIRDHAM PRIMARY | HE |  |  |  |  | -0.28877 | -0.61019 | -0.96223 | 14.3521 | 13.8847 | 13.251 | 12.9184 | 12.3194 | 11.748 | 8.6735 | 6.6133 | 5.65 | 1.449 | 1.2021 | 0.95409 | 0.66123 | 14.8123 | 14.3786 | 14.2031 | 13.7572 | 13.3102 | 10.8092 | 8.5265 | 5.5531 | 0.18266 | -0.094888 | -0.41428 | -0.77652 | 13.9837 | 13.3959 | 13.1357 | 12.5714 | 12.0214 | 9.2021 | 7.4837 | 6.7143
|  | BIRDHAM PRIMARY | CF |  |  |  |  | -0.11428 | -0.31734 | -0.57856 | 14.8939 | 14.5714 | 14.2418 | 13.8623 | 13.848 | 13.5796 | 11.5082 | 9.2612 | 7.2347 | 1.5214 | 1.351 | 1.1286 | 0.91838 | 15.1276 | 14.8061 | 14.4184 | 14.3286 | 13.9837 | 11.5123 | 7.798 | 1.6418 | 0.33777 | 0.17144 | -0.058153 | -0.27244 | 14.6306 | 14.3204 | 13.9551 | 13.9633 | 13.6898 | 11.7418 | 9.7225 | 7.9561
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM PRIMARY | MINIMUM HEADROOM | SU 56691 16683 | NO | NO | 2.202 | 5.3132 | 19.6744 | 19.3193 | 18.6295 | 17.9621 | 16.956 | 15.8254 | 14.6917 | 13.8601 | 9.5958 | 6.6652 | 5.0101 | 10.0997 | 23.8601 | 23.6315 | 23.1244 | 22.605 | 21.9183 | 21.1234 | 20.3183 | 19.7438 | 16.6938 | 13.2489 | 5.3989 | 5.9095 | 19.9989 | 19.7315 | 19.0744 | 18.4172 | 17.4713 | 16.3877 | 15.306 | 14.5652 | 10.9407 | 8.4999 | 7.0907
|  | BISHOPS WALTHAM PRIMARY | EE |  |  |  |  | 5.3132 | 19.6744 | 19.3193 | 18.6295 | 17.9621 | 16.956 | 15.8254 | 14.6917 | 13.8601 | 9.5958 | 7.0591 | 5.3121 | 10.0997 | 23.8601 | 23.6315 | 23.1244 | 22.605 | 21.9183 | 21.1234 | 20.3183 | 19.7438 | 16.6938 | 13.9009 | 9.9152 | 5.9095 | 19.9989 | 19.7315 | 19.0744 | 18.4172 | 17.4713 | 16.3877 | 15.306 | 14.5652 | 10.9407 | 8.8458 | 7.3397
|  | BISHOPS WALTHAM PRIMARY | HT |  |  |  |  | 5.7019 | 20.2479 | 19.6611 | 19.056 | 18.8366 | 17.9785 | 17.0295 | 16.0377 | 14.9979 | 9.8019 | 6.6652 | 5.0101 | 10.4997 | 24.4621 | 24.105 | 23.7244 | 23.6336 | 23.1601 | 22.6183 | 22.0366 | 21.4254 | 18.5509 | 17.0101 | 16.2713 | 6.3319 | 20.6234 | 20.0774 | 19.505 | 19.357 | 18.5764 | 17.704 | 16.7836 | 15.8244 | 11.1581 | 8.4999 | 7.0907
|  | BISHOPS WALTHAM PRIMARY | HE |  |  |  |  | 5.6785 | 20.2213 | 19.6305 | 19.0223 | 18.7917 | 18.0193 | 17.1499 | 16.2326 | 15.2642 | 10.1407 | 7.2591 | 6.1132 | 10.3926 | 24.2968 | 23.8764 | 23.4305 | 23.2662 | 22.7346 | 22.1234 | 21.4621 | 20.753 | 16.8509 | 13.7356 | 9.9999 | 6.3064 | 20.5958 | 20.0468 | 19.4662 | 19.3152 | 18.603 | 17.7907 | 16.9315 | 16.0264 | 11.4142 | 8.9785 | 8.007
|  | BISHOPS WALTHAM PRIMARY | CF |  |  |  |  | 5.9887 | 20.6499 | 20.2703 | 19.8611 | 19.4805 | 19.4264 | 19.006 | 18.5519 | 18.053 | 14.6254 | 11.253 | 8.3611 | 10.5517 | 24.505 | 24.206 | 23.8621 | 23.4928 | 23.3642 | 22.9274 | 22.453 | 21.9274 | 18.2877 | 13.2489 | 5.3989 | 6.5901 | 20.9795 | 20.6387 | 20.2468 | 19.8693 | 19.8785 | 19.4683 | 19.0244 | 18.5397 | 15.303 | 12.3305 | 9.8815
NURSLING GSP | VELMORE BSP | BISHOPSTOKE PRIMARY | MINIMUM HEADROOM | SU 46463 18472 | NO | YES | 3.005 | 6.5531 | 6.448 | 6.3214 | 6.1796 | 6.0194 | 5.8316 | 5.601 | 5.3786 | 5.1837 | 4.0449 | 3.551 | 3.4663 | 4.8612 | 4.7878 | 4.702 | 4.6031 | 4.4949 | 4.3653 | 4.1867 | 4.0163 | 3.8673 | 2.9949 | 2.6173 | 2.552 | 5.349 | 5.248 | 5.1276 | 4.9867 | 4.8337 | 4.6531 | 4.4296 | 4.2153 | 4.0276 | 2.9265 | 2.448 | 2.3684
|  | BISHOPSTOKE PRIMARY | EE |  |  |  |  | 6.5531 | 6.448 | 6.3214 | 6.1796 | 6.0194 | 5.8316 | 5.601 | 5.3786 | 5.1837 | 4.5204 | 4.4122 | 4.4041 | 4.8612 | 4.7878 | 4.702 | 4.6031 | 4.4949 | 4.3653 | 4.1867 | 4.0163 | 3.8673 | 3.3571 | 3.2776 | 3.2735 | 5.349 | 5.248 | 5.1276 | 4.9867 | 4.8337 | 4.6531 | 4.4296 | 4.2153 | 4.0276 | 3.3867 | 3.2827 | 3.2765
|  | BISHOPSTOKE PRIMARY | HT |  |  |  |  | 6.6571 | 6.5969 | 6.5173 | 6.4214 | 6.3061 | 6.1776 | 6.0102 | 5.8276 | 5.6388 | 4.7806 | 4.4143 | 4.3418 | 4.9276 | 4.8929 | 4.8398 | 4.7714 | 4.6939 | 4.6071 | 4.4939 | 4.3694 | 4.2245 | 3.5673 | 3.2898 | 3.2367 | 5.4143 | 5.3837 | 5.3153 | 5.2204 | 5.1102 | 4.9837 | 4.8224 | 4.648 | 4.4643 | 3.6357 | 3.2827 | 3.2133
|  | BISHOPSTOKE PRIMARY | HE |  |  |  |  | 6.6194 | 6.5418 | 6.4388 | 6.3122 | 6.1633 | 5.9888 | 5.7653 | 5.5204 | 5.2602 | 4.0449 | 3.551 | 3.4663 | 4.902 | 4.851 | 4.7827 | 4.6949 | 4.5929 | 4.4724 | 4.3153 | 4.1276 | 3.9265 | 2.9949 | 2.6173 | 2.552 | 5.3908 | 5.3378 | 5.2357 | 5.1153 | 4.9714 | 4.8031 | 4.5888 | 4.351 | 4.101 | 2.9265 | 2.448 | 2.3684
|  | BISHOPSTOKE PRIMARY | CF |  |  |  |  | 6.7122 | 6.6602 | 6.6194 | 6.5561 | 6.4786 | 6.3949 | 6.2776 | 6.1418 | 5.9929 | 5.0827 | 4.2418 | 3.6582 | 4.9643 | 4.9255 | 4.9051 | 4.8612 | 4.8082 | 4.749 | 4.6684 | 4.5755 | 4.4745 | 3.7908 | 3.1449 | 2.6969 | 5.4459 | 5.4112 | 5.3939 | 5.351 | 5.2765 | 5.1969 | 5.0827 | 4.952 | 4.8061 | 3.9286 | 3.1153 | 2.5531
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE PRIMARY | MINIMUM HEADROOM | SU 45116 13082 | NO | NO | 0.5 | 2.4071 | 1.9867 | 1.8816 | 1.4724 | 1.0276 | 0.24184 | -0.59898 | -1.4459 | -2.0276 | -5.6041 | -8.4296 | -10.1082 | 3.9592 | 3.5776 | 3.4306 | 3.0204 | 2.5612 | 1.9337 | 1.2398 | 0.51735 | -0.022449 | -3.6418 | -11.5235 | -26.9755 | 2.9704 | 2.6306 | 2.5582 | 2.2367 | 1.8408 | 1.099 | 0.28878 | -0.52857 | -1.048 | -4.1184 | -6.7653 | -8.2776
|  | BITTERNE PRIMARY | EE |  |  |  |  | 2.4071 | 1.9867 | 1.8816 | 1.4724 | 1.0276 | 0.24184 | -0.59898 | -1.4459 | -2.0276 | -5.3 | -7.8582 | -9.8888 | 3.9592 | 3.5776 | 3.4306 | 3.0204 | 2.5612 | 1.9337 | 1.2398 | 0.51735 | -0.022449 | -3.6418 | -8.5418 | -16.6418 | 2.9704 | 2.6306 | 2.5582 | 2.2367 | 1.8408 | 1.099 | 0.28878 | -0.52857 | -1.048 | -3.8816 | -6.2612 | -8.099
|  | BITTERNE PRIMARY | HT |  |  |  |  | 2.6714 | 2.3449 | 2.0316 | 1.6561 | 1.2571 | 0.89286 | 0.16122 | -0.60102 | -1.3939 | -5.6041 | -8.4296 | -10.1082 | 4.298 | 4.0969 | 3.9143 | 3.6724 | 3.3929 | 3.2898 | 2.8847 | 2.4622 | 2.0102 | -0.20102 | -1.5143 | -2.2592 | 3.1602 | 2.8847 | 2.6276 | 2.3204 | 1.9929 | 1.6429 | 0.99694 | 0.32959 | -0.36122 | -4.1184 | -6.7653 | -8.2776
|  | BITTERNE PRIMARY | HE |  |  |  |  | 2.7051 | 2.4082 | 2.1327 | 1.7949 | 1.4173 | 1.1796 | 0.6 | -0.0020408 | -0.62143 | -4.0051 | -6.4643 | -7.6908 | 4.1602 | 3.8745 | 3.6031 | 3.2622 | 2.8684 | 2.648 | 2.1347 | 1.5755 | 0.97347 | -2.9541 | -7.8745 | -15.6551 | 3.1918 | 2.9439 | 2.7173 | 2.4398 | 2.1347 | 1.9122 | 1.4102 | 0.89082 | 0.35918 | -2.701 | -5.0296 | -6.151
|  | BITTERNE PRIMARY | CF |  |  |  |  | 2.9327 | 2.7602 | 2.6143 | 2.4255 | 2.2184 | 1.9724 | 2.0255 | 1.7765 | 1.5173 | -0.58673 | -2.9796 | -5.2357 | 4.2316 | 3.9837 | 3.7408 | 3.4296 | 3.0469 | 2.5796 | 2.2959 | 1.7704 | 1.201 | -3.248 | -11.5235 | -26.9755 | 3.4 | 3.2612 | 3.1449 | 2.9939 | 2.8316 | 2.6347 | 2.6888 | 2.4949 | 2.2918 | 0.25816 | -1.8245 | -3.7918
MINETY GSP | STRATTON (RESERVE) BSP | BLACK BOURTON PRIMARY | MINIMUM HEADROOM | SP 28349 03818 | NO | NO | 0.978 | 7.1102 | 6.7929 | 6.4122 | 6.001 | 5.5337 | 4.9796 | 4.2469 | 3.5418 | 3.102 | 0.31837 | -1.0888 | -1.9082 | 8.4847 | 8.2561 | 7.9796 | 7.6755 | 7.3327 | 6.9398 | 6.4224 | 5.9031 | 5.5939 | 3.5908 | 2.6194 | 2.0102 | 7.2255 | 6.8969 | 6.5 | 6.0714 | 5.5878 | 5.0071 | 4.3082 | 3.6388 | 3.2276 | 0.5898 | -0.73163 | -1.502
|  | BLACK BOURTON PRIMARY | EE |  |  |  |  | 7.1102 | 6.7929 | 6.4122 | 6.001 | 5.5337 | 4.9796 | 4.2469 | 3.5418 | 3.102 | 1.0357 | 0.49082 | 0.19694 | 8.4847 | 8.2561 | 7.9796 | 7.6755 | 7.3327 | 6.9398 | 6.4224 | 5.9031 | 5.5939 | 4.2112 | 3.9367 | 3.7857 | 7.2255 | 6.8969 | 6.5 | 6.0714 | 5.5878 | 5.0071 | 4.3082 | 3.6388 | 3.2276 | 1.2908 | 0.8051 | 0.54592
|  | BLACK BOURTON PRIMARY | HT |  |  |  |  | 7.4245 | 7.201 | 6.9357 | 6.6337 | 6.2806 | 5.8541 | 5.3296 | 4.7102 | 4.0684 | 1.2939 | 0.035714 | -0.65816 | 8.6357 | 8.5561 | 8.3724 | 8.1592 | 7.9061 | 7.6082 | 7.2449 | 6.8449 | 6.3765 | 4.4235 | 3.6031 | 3.1571 | 7.3633 | 7.2449 | 7.0296 | 6.7204 | 6.352 | 5.8939 | 5.3561 | 4.7704 | 4.1592 | 1.5398 | 0.37143 | -0.27245
|  | BLACK BOURTON PRIMARY | HE |  |  |  |  | 7.3724 | 7.1255 | 6.8286 | 6.4929 | 6.0969 | 5.6143 | 5.0163 | 4.3204 | 3.5888 | 0.31837 | -1.0888 | -1.9082 | 8.6112 | 8.5051 | 8.2888 | 8.048 | 7.7633 | 7.4173 | 6.9908 | 6.5041 | 5.9571 | 3.5908 | 2.6194 | 2.0102 | 7.3622 | 7.2357 | 6.9245 | 6.5796 | 6.1684 | 5.6602 | 5.052 | 4.3898 | 3.6898 | 0.5898 | -0.73163 | -1.502
|  | BLACK BOURTON PRIMARY | CF |  |  |  |  | 7.5306 | 7.4459 | 7.3378 | 7.1439 | 6.9347 | 6.6908 | 6.3592 | 5.9816 | 5.598 | 2.9745 | 0.81429 | -0.72551 | 8.6735 | 8.5969 | 8.5061 | 8.3949 | 8.3051 | 8.1653 | 7.9378 | 7.6602 | 7.3694 | 5.4459 | 3.8806 | 2.5439 | 7.4541 | 7.3735 | 7.2776 | 7.1592 | 7.0367 | 6.7796 | 6.4337 | 6.0469 | 5.6469 | 3.0969 | 1.0541 | -0.39082
MANNINGTON GSP | LYTCHETT BSP | BLANDFORD PRIMARY | MINIMUM HEADROOM | ST 88810 05536 | NO | NO | 4.748 | 19.7312 | 19.0659 | 18.722 | 17.9812 | 17.171 | 15.8332 | 14.7587 | 13.6822 | 12.8638 | 8.6108 | 5.3863 | 3.574 | 22.0822 | 21.8189 | 21.6414 | 21.3353 | 21.0036 | 20.0904 | 19.3312 | 18.5638 | 18.0189 | 15.1373 | 12.0077 | 3.8465 | 19.8842 | 19.2547 | 18.9904 | 18.3087 | 17.5587 | 16.3455 | 15.3302 | 14.3138 | 13.5934 | 9.9128 | 7.0383 | 5.3944
|  | BLANDFORD PRIMARY | EE |  |  |  |  | 19.7312 | 19.0659 | 18.722 | 17.9812 | 17.171 | 15.8332 | 14.7587 | 13.6822 | 12.8638 | 8.6853 | 5.9669 | 3.9108 | 22.0822 | 21.8189 | 21.6414 | 21.3353 | 21.0036 | 20.0904 | 19.3312 | 18.5638 | 18.0189 | 15.1373 | 12.2169 | 7.871 | 19.8842 | 19.2547 | 18.9904 | 18.3087 | 17.5587 | 16.3455 | 15.3302 | 14.3138 | 13.5934 | 9.9567 | 7.5577 | 5.6842
|  | BLANDFORD PRIMARY | HT |  |  |  |  | 20.0261 | 19.471 | 18.9547 | 18.2761 | 17.522 | 16.6067 | 15.6822 | 14.721 | 13.7353 | 8.6108 | 5.3863 | 3.574 | 22.2618 | 22.0638 | 21.873 | 21.6251 | 21.3516 | 20.7659 | 20.3781 | 19.973 | 19.5383 | 16.8006 | 15.322 | 14.5689 | 20.2128 | 19.7077 | 19.2424 | 18.6261 | 17.9332 | 17.1985 | 16.3526 | 15.4761 | 14.573 | 9.9128 | 7.0383 | 5.3944
|  | BLANDFORD PRIMARY | HE |  |  |  |  | 20.0404 | 19.5087 | 19.0179 | 18.3659 | 17.6424 | 16.8526 | 16.0536 | 15.224 | 14.371 | 9.9271 | 7.1944 | 5.9455 | 22.2383 | 22.0281 | 21.8302 | 21.5669 | 21.273 | 20.6649 | 20.2506 | 19.8087 | 19.1965 | 15.8322 | 12.7628 | 8.7628 | 20.2271 | 19.7393 | 19.3006 | 18.7077 | 18.0455 | 17.42 | 16.6883 | 15.9281 | 15.1465 | 11.1087 | 8.6383 | 7.5057
|  | BLANDFORD PRIMARY | CF |  |  |  |  | 20.2893 | 19.9567 | 19.6251 | 19.172 | 18.6659 | 17.923 | 17.821 | 17.4067 | 16.9771 | 13.9842 | 11.0393 | 8.2955 | 22.3679 | 22.2353 | 22.1036 | 21.9312 | 21.7373 | 21.1904 | 21.0302 | 20.6067 | 20.1526 | 16.8536 | 12.0077 | 3.8465 | 20.4557 | 20.1516 | 19.8536 | 19.4465 | 18.9914 | 18.3179 | 18.2822 | 17.8893 | 17.4791 | 14.6802 | 12.0873 | 9.6608
COWLEY GSP | WITNEY BSP | BLEDINGTON PRIMARY | MINIMUM HEADROOM | SP 25641 22580 | YES | NO | 1.009 | 3.213 | 3.0681 | 2.9518 | 2.7895 | 2.611 | 2.4344 | 2.1763 | 1.9201 | 1.7742 | 1.0722 | 0.75688 | 0.48852 | 3.9668 | 3.8556 | 3.7709 | 3.6434 | 3.5015 | 3.3709 | 3.1832 | 2.9883 | 2.876 | 2.3005 | 1.473 | -0.34643 | 3.1541 | 3.0122 | 2.899 | 2.7326 | 2.5551 | 2.3867 | 2.1286 | 1.8724 | 1.7418 | 1.1551 | 0.87449 | 0.64489
|  | BLEDINGTON PRIMARY | EE |  |  |  |  | 3.213 | 3.0681 | 2.9518 | 2.7895 | 2.611 | 2.4344 | 2.1763 | 1.9201 | 1.7742 | 1.0722 | 0.77627 | 0.58954 | 3.9668 | 3.8556 | 3.7709 | 3.6434 | 3.5015 | 3.3709 | 3.1832 | 2.9883 | 2.876 | 2.3005 | 1.7464 | 0.86275 | 3.1541 | 3.0122 | 2.899 | 2.7326 | 2.5551 | 2.3867 | 2.1286 | 1.8724 | 1.7418 | 1.1551 | 0.89898 | 0.73571
|  | BLEDINGTON PRIMARY | HT |  |  |  |  | 3.2916 | 3.2008 | 3.0967 | 2.9732 | 2.8732 | 2.6977 | 2.4967 | 2.3344 | 2.1242 | 1.1855 | 0.75688 | 0.48852 | 4.0536 | 3.9974 | 3.926 | 3.8444 | 3.7832 | 3.6781 | 3.5495 | 3.4505 | 3.3168 | 2.7413 | 2.5138 | 2.3791 | 3.249 | 3.1592 | 3.0571 | 2.9367 | 2.8449 | 2.6786 | 2.4857 | 2.3357 | 2.1357 | 1.252 | 0.87449 | 0.64489
|  | BLEDINGTON PRIMARY | HE |  |  |  |  | 3.2906 | 3.2028 | 3.1048 | 2.9885 | 2.8946 | 2.7293 | 2.5406 | 2.3885 | 2.1895 | 1.2253 | 0.92321 | 0.77831 | 4.0403 | 3.9699 | 3.8934 | 3.8025 | 3.7301 | 3.6097 | 3.4719 | 3.3576 | 3.2036 | 2.4097 | 1.8372 | 0.97806 | 3.249 | 3.1612 | 3.0633 | 2.951 | 2.8653 | 2.7071 | 2.5255 | 2.3888 | 2.2 | 1.3041 | 1.0378 | 0.91428
|  | BLEDINGTON PRIMARY | CF |  |  |  |  | 3.3283 | 3.2477 | 3.1804 | 3.0977 | 3.0048 | 2.8957 | 2.8171 | 2.6936 | 2.565 | 1.8814 | 1.364 | 0.95076 | 4.0628 | 3.9923 | 3.9393 | 3.8597 | 3.774 | 3.6709 | 3.5842 | 3.4648 | 3.3352 | 2.5393 | 1.473 | -0.34643 | 3.2908 | 3.2061 | 3.1449 | 3.0622 | 2.9663 | 2.8602 | 2.7837 | 2.6592 | 2.5265 | 1.8633 | 1.3969 | 1.052
FLEET-BRAMLEY GSP | ALTON BSP | BORDON PRIMARY | MINIMUM HEADROOM | SU 82256 35269 | NO | NO | 7.347 | 2.414 | 1.4915 | -0.14213 | -1.4952 | -2.9115 | -4.7962 | -6.936 | -8.8666 | -10.2309 | -17.1962 | -22.4748 | -25.4156 | 7.2232 | 6.6334 | 5.314 | 4.3773 | 3.4436 | 2.264 | 0.8742 | -0.43091 | -1.3166 | -6.0687 | -11.0605 | -23.687 | 3.5242 | 2.6477 | 0.93134 | -0.30029 | -1.5768 | -3.2687 | -5.2003 | -6.9595 | -8.1829 | -14.2462 | -18.7462 | -21.2534
|  | BORDON PRIMARY | EE |  |  |  |  | 2.414 | 1.4915 | -0.14213 | -1.4952 | -2.9115 | -4.7962 | -6.936 | -8.8666 | -10.2309 | -16.9829 | -21.5432 | -24.9636 | 7.2232 | 6.6334 | 5.314 | 4.3773 | 3.4436 | 2.264 | 0.8742 | -0.43091 | -1.3166 | -6.0687 | -10.6513 | -17.3238 | 3.5242 | 2.6477 | 0.93134 | -0.30029 | -1.5768 | -3.2687 | -5.2003 | -6.9595 | -8.1829 | -14.1401 | -17.9483 | -20.8983
|  | BORDON PRIMARY | HT |  |  |  |  | 2.9303 | 1.8446 | 0.29562 | -0.57887 | -1.8044 | -3.5054 | -5.4034 | -7.1534 | -8.7891 | -17.1962 | -22.4748 | -25.4156 | 7.7987 | 7.1293 | 5.9446 | 5.4905 | 4.8354 | 3.9681 | 2.9354 | 1.9773 | 1.0466 | -3.4166 | -5.8452 | -7.0697 | 4.0426 | 3.0028 | 1.3762 | 0.62624 | -0.4554 | -1.9513 | -3.6319 | -5.1993 | -6.684 | -14.2462 | -18.7462 | -21.2534
|  | BORDON PRIMARY | HE |  |  |  |  | 2.9191 | 1.8405 | 0.30889 | -0.54825 | -1.7564 | -3.2778 | -5.0064 | -6.5891 | -8.0697 | -15.6258 | -20.535 | -22.6891 | 7.664 | 6.9201 | 5.6497 | 5.0997 | 4.3436 | 3.413 | 2.3171 | 1.2599 | 0.21501 | -5.4962 | -10.4972 | -16.6646 | 4.0262 | 2.9936 | 1.3793 | 0.64154 | -0.42989 | -1.7707 | -3.3105 | -4.7391 | -6.0901 | -12.9207 | -17.0983 | -18.9319
|  | BORDON PRIMARY | CF |  |  |  |  | 4.5252 | 3.9579 | 2.9915 | 2.2354 | 1.7793 | 0.79052 | -0.45846 | -1.5472 | -2.5248 | -8.486 | -13.5656 | -18.0809 | 8.4334 | 7.9222 | 6.9364 | 6.3171 | 5.9497 | 5.1834 | 4.2252 | 3.3354 | 2.4579 | -3.335 | -11.0605 | -23.687 | 5.3109 | 4.7191 | 3.6038 | 2.9242 | 2.566 | 1.7313 | 0.66195 | -0.28703 | -1.1554 | -6.5136 | -11.087 | -15.0738
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | BOSCOMBE DOWN PRIMARY | MINIMUM HEADROOM | SU 17186 41044 | NO | NO | 1.527 | 7.0375 | 6.9008 | 6.7814 | 6.6263 | 6.461 | 6.3916 | 6.1651 | 5.9396 | 5.7722 | 4.8967 | 4.2467 | 3.8824 | 6.5589 | 6.4253 | 6.314 | 6.1681 | 6.013 | 5.9569 | 5.7528 | 5.5447 | 5.3824 | 4.4487 | 3.4804 | 0.90589 | 6.1018 | 5.8702 | 5.6579 | 5.3732 | 5.0681 | 5.1528 | 4.7865 | 4.4181 | 4.211 | 3.1181 | 2.2549 | 1.8069
|  | BOSCOMBE DOWN PRIMARY | EE |  |  |  |  | 7.0375 | 6.9008 | 6.7814 | 6.6263 | 6.461 | 6.3916 | 6.1651 | 5.9396 | 5.7722 | 4.9232 | 4.3559 | 4.0681 | 6.5589 | 6.4253 | 6.314 | 6.1681 | 6.013 | 5.9569 | 5.7528 | 5.5447 | 5.3824 | 4.4487 | 3.4804 | 2.2406 | 6.1018 | 5.8702 | 5.6579 | 5.3732 | 5.0681 | 5.1528 | 4.7865 | 4.4181 | 4.211 | 3.1794 | 2.3722 | 1.9865
|  | BOSCOMBE DOWN PRIMARY | HT |  |  |  |  | 7.1079 | 6.9947 | 6.8916 | 6.7681 | 6.6559 | 6.46 | 6.2447 | 6.0181 | 5.9487 | 4.8967 | 4.2467 | 3.8824 | 6.6457 | 6.5559 | 6.4732 | 6.3722 | 6.2855 | 6.1334 | 5.962 | 5.7845 | 5.7589 | 4.964 | 4.4753 | 4.2202 | 6.1589 | 6.011 | 5.8763 | 5.7192 | 5.5447 | 5.2273 | 4.8702 | 4.4926 | 4.6049 | 3.1181 | 2.2549 | 1.8069
|  | BOSCOMBE DOWN PRIMARY | HE |  |  |  |  | 7.1161 | 7.0079 | 6.913 | 6.7936 | 6.6834 | 6.513 | 6.3151 | 6.1079 | 6.064 | 5.1569 | 4.6069 | 4.2722 | 6.6263 | 6.5212 | 6.4283 | 6.312 | 6.212 | 6.0549 | 5.8773 | 5.6865 | 5.6447 | 4.6396 | 3.664 | 2.414 | 6.1753 | 6.0396 | 5.9181 | 5.7681 | 5.6069 | 5.3345 | 5.012 | 4.6743 | 4.8385 | 3.5916 | 2.7181 | 2.2916
|  | BOSCOMBE DOWN PRIMARY | CF |  |  |  |  | 7.1987 | 7.1355 | 7.0794 | 7.0079 | 6.9253 | 6.862 | 6.7671 | 6.6661 | 6.5579 | 6.0528 | 5.3396 | 4.6753 | 6.6783 | 6.6049 | 6.5314 | 6.4457 | 6.3457 | 6.2579 | 6.1324 | 5.9998 | 5.8528 | 5.0406 | 3.5171 | 0.90589 | 6.2681 | 6.2089 | 6.1406 | 6.0518 | 5.913 | 5.812 | 5.6406 | 5.4569 | 5.261 | 4.6967 | 3.8161 | 3.0232
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST PRIMARY | MINIMUM HEADROOM | SZ 11636 92447 | NO | NO | 13.284 | 5.9949 | 5.4286 | 4.849 | 4.1969 | 3.9714 | 3.0714 | 2.0408 | 1.0112 | 0.23061 | -2.9541 | -5.0082 | -5.3459 | 7.5551 | 7.1327 | 6.6551 | 6.1031 | 5.8398 | 5.1561 | 4.3582 | 3.549 | 2.9031 | -0.3551 | -5.1786 | -16.3847 | 5.4276 | 4.9153 | 4.3755 | 3.7694 | 3.5255 | 2.6847 | 1.7204 | 0.75816 | 0.019388 | -2.9082 | -4.6755 | -4.9439
|  | BOSCOMBE EAST PRIMARY | EE |  |  |  |  | 5.9949 | 5.4286 | 4.849 | 4.1969 | 3.9714 | 3.0714 | 2.0408 | 1.0112 | 0.23061 | -2.9541 | -4.6622 | -4.6265 | 7.5551 | 7.1327 | 6.6551 | 6.1031 | 5.8398 | 5.1561 | 4.3582 | 3.549 | 2.9031 | -0.3551 | -3.7071 | -8.6898 | 5.4276 | 4.9153 | 4.3755 | 3.7694 | 3.5255 | 2.6847 | 1.7204 | 0.75816 | 0.019388 | -2.9082 | -4.3878 | -4.3551
|  | BOSCOMBE EAST PRIMARY | HT |  |  |  |  | 6.3449 | 5.9245 | 5.5378 | 5.1306 | 4.6286 | 3.8663 | 3.3908 | 2.55 | 1.6776 | -2.5388 | -5.0082 | -5.3459 | 7.9378 | 7.6786 | 7.4184 | 7.1653 | 6.8163 | 6.35 | 6.0888 | 5.5653 | 5.0122 | 2.4378 | 1.0296 | 0.76327 | 5.7429 | 5.4102 | 5.0286 | 4.648 | 4.1796 | 3.4755 | 3.0276 | 2.251 | 1.4398 | -2.449 | -4.6755 | -4.9439
|  | BOSCOMBE EAST PRIMARY | HE |  |  |  |  | 6.3592 | 5.9663 | 5.6112 | 5.2378 | 4.7714 | 4.0786 | 3.6622 | 2.9061 | 2.1082 | -1.2888 | -3.0245 | -3.3276 | 7.8214 | 7.4959 | 7.1776 | 6.8439 | 6.4388 | 5.8929 | 5.5408 | 4.9143 | 4.2398 | 0.61122 | -2.9031 | -8.0367 | 5.748 | 5.4418 | 5.0837 | 4.7296 | 4.2929 | 3.649 | 3.2582 | 2.548 | 1.802 | -1.3449 | -2.8878 | -3.1245
|  | BOSCOMBE EAST PRIMARY | CF |  |  |  |  | 6.6541 | 6.4061 | 6.2082 | 5.9592 | 5.7235 | 5.4041 | 5.0082 | 4.5806 | 4.5643 | 2.1184 | -0.58367 | -3.0939 | 7.9633 | 7.701 | 7.4439 | 7.149 | 6.8245 | 6.4051 | 5.9082 | 5.3561 | 5.0592 | 1.2122 | -5.1786 | -16.3847 | 5.999 | 5.8173 | 5.6439 | 5.4112 | 5.1908 | 4.9041 | 4.5378 | 4.1449 | 4.098 | 1.8092 | -0.71735 | -2.9561
EALING GSP |  | BOSTON MANOR PRIMARY | MINIMUM HEADROOM | TQ 17043 78092 | NO | NO | 12.454 | 1.6206 | 1.2104 | 39.2564 | 38.7299 | 38.1176 | 37.5258 | 36.8942 | 36.5003 | 36.1197 | 34.8503 | 34.185 | 33.7932 | 1.7747 | 1.4992 | 36.3778 | 36.0554 | 35.587 | 35.1003 | 34.5768 | 34.284 | 33.986 | 32.2942 | 27.537 | 18.2503 | 0.95838 | 0.47878 | 36.3074 | 35.5207 | 34.7748 | 34.3176 | 33.7993 | 33.5217 | 33.2758 | 32.3187 | 31.4901 | 31.0554
|  | BOSTON MANOR PRIMARY | EE |  |  |  |  | 1.6206 | 1.2104 | 39.2564 | 38.8523 | 38.1176 | 37.5258 | 36.8942 | 36.5003 | 36.1197 | 34.8503 | 34.3829 | 34.2401 | 1.7747 | 1.4992 | 36.3778 | 36.136 | 35.587 | 35.1003 | 34.5768 | 34.284 | 33.986 | 32.334 | 29.7207 | 25.1534 | 0.95838 | 0.50531 | 36.4054 | 35.9227 | 35.084 | 34.434 | 33.7993 | 33.5217 | 33.2758 | 32.3187 | 31.4901 | 31.2493
|  | BOSTON MANOR PRIMARY | HT |  |  |  |  | 1.7349 | 1.3135 | 39.3707 | 38.7299 | 38.1758 | 37.7646 | 37.4605 | 37.138 | 36.8248 | 35.3789 | 34.4819 | 34.0932 | 1.8778 | 1.6145 | 36.5299 | 36.0554 | 35.6972 | 35.4523 | 35.2778 | 35.0799 | 34.9023 | 34.2258 | 33.5993 | 33.3217 | 0.99919 | 0.47878 | 36.3074 | 35.5207 | 34.7748 | 34.3176 | 34.0952 | 33.8472 | 33.6146 | 32.5891 | 31.4932 | 31.0554
|  | BOSTON MANOR PRIMARY | HE |  |  |  |  | 1.7767 | 1.4125 | 39.5238 | 39.187 | 38.536 | 38.0227 | 37.4993 | 37.0605 | 36.6707 | 35.0095 | 34.185 | 33.7932 | 1.8645 | 1.6114 | 36.5289 | 36.3248 | 35.8309 | 35.3972 | 34.9585 | 34.5921 | 34.2748 | 32.6544 | 30.1054 | 25.5411 | 1.0706 | 0.64511 | 36.588 | 36.1472 | 35.3636 | 34.7932 | 34.2789 | 33.9278 | 33.6656 | 32.8411 | 32.0493 | 31.7544
|  | BOSTON MANOR PRIMARY | CF |  |  |  |  | 1.9523 | 1.7482 | 40.0401 | 39.9166 | 39.7952 | 39.5442 | 39.2003 | 38.7983 | 38.386 | 36.3993 | 35.2462 | 34.2534 | 1.9349 | 1.7563 | 36.7574 | 36.6442 | 36.5258 | 36.2574 | 35.9421 | 35.5636 | 35.0993 | 32.2942 | 27.537 | 18.2503 | 1.24 | 1.0186 | 37.2085 | 37.0921 | 36.988 | 36.785 | 36.4819 | 36.0921 | 35.6993 | 33.9513 | 33.2074 | 32.3095
MANNINGTON GSP | BOURNEMOUTH BSP | BOURNE VALLEY PRIMARY | MINIMUM HEADROOM | SZ 06207 92415 | NO | YES | 4.952 | 3.3214 | 2.8041 | 1.8867 | 0.88367 | -0.11122 | -1.7459 | -3.6041 | -5.4673 | -6.8459 | -13.9112 | -19.6337 | -22.4214 | 8.1469 | 7.7255 | 6.9398 | 6.0765 | 5.2163 | 4.0612 | 2.7102 | 1.3306 | 0.34184 | -4.9112 | -11.7133 | -28.4827 | 3.5408 | 3.0969 | 2.1929 | 1.2235 | 0.26429 | -1.2643 | -3.0133 | -4.7643 | -6.0265 | -12.0592 | -17.1296 | -19.451
|  | BOURNE VALLEY PRIMARY | EE |  |  |  |  | 3.3214 | 2.8041 | 1.8867 | 0.88367 | -0.11122 | -1.7459 | -3.6041 | -5.4673 | -6.8459 | -13.6071 | -18.402 | -21.5929 | 8.1469 | 7.7255 | 6.9398 | 6.0765 | 5.2163 | 4.0612 | 2.7102 | 1.3306 | 0.34184 | -4.9112 | -10.7551 | -19.3837 | 3.5408 | 3.0969 | 2.1929 | 1.2235 | 0.26429 | -1.2643 | -3.0133 | -4.7643 | -6.0265 | -11.9204 | -16.0847 | -18.801
|  | BOURNE VALLEY PRIMARY | HT |  |  |  |  | 3.902 | 3.149 | 2.3367 | 1.9469 | 1.1776 | -0.25612 | -1.852 | -3.548 | -5.2735 | -13.9112 | -19.6337 | -22.4214 | 8.7255 | 8.2337 | 7.7061 | 7.4939 | 6.9898 | 6.2143 | 5.3031 | 4.3143 | 3.2959 | -1.2949 | -3.9959 | -5.1745 | 4.2112 | 3.4776 | 2.6837 | 2.3704 | 1.6296 | 0.33571 | -1.1184 | -2.6704 | -4.2551 | -12.0592 | -17.1296 | -19.451
|  | BOURNE VALLEY PRIMARY | HE |  |  |  |  | 3.9684 | 3.2745 | 2.5276 | 2.1541 | 1.5 | 0.3449 | -0.95 | -2.3133 | -3.752 | -10.8418 | -15.5316 | -17.5837 | 8.5898 | 8.0194 | 7.4173 | 7.0459 | 6.5184 | 5.7378 | 4.8235 | 3.801 | 2.698 | -3.3286 | -9.2684 | -17.352 | 4.2643 | 3.5796 | 2.848 | 2.5449 | 1.9112 | 0.8551 | -0.34388 | -1.6153 | -2.9531 | -9.3429 | -13.4418 | -15.1071
|  | BOURNE VALLEY PRIMARY | CF |  |  |  |  | 4.4316 | 4.0122 | 3.5367 | 3.0367 | 2.9449 | 2.4847 | 1.9194 | 1.299 | 0.65102 | -3.9071 | -8.9735 | -13.948 | 8.7796 | 8.3276 | 7.8245 | 7.2867 | 6.9878 | 6.4061 | 5.7245 | 4.9592 | 4.1082 | -1.9092 | -11.7133 | -28.4827 | 4.652 | 4.2357 | 3.752 | 3.2286 | 3.2255 | 2.7827 | 2.2327 | 1.6388 | 1.0194 | -3.2796 | -7.8327 | -12.0939
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON PRIMARY | MINIMUM HEADROOM | ST 77363 30262 | NO | NO | 2.119 | 1.1563 | 0.47878 | -0.013061 | -0.11 | -0.57939 | -1.2743 | -2.058 | -2.8396 | -3.3712 | -6.0937 | -8.0345 | -9.2335 | 2.6573 | 2.1012 | 1.7094 | 1.7124 | 1.341 | 0.85837 | 0.3002 | -0.2702 | -0.62327 | -2.6202 | -5.2386 | -11.208 | 1.292 | 0.62878 | 0.14 | 0.12367 | -0.32224 | -0.97735 | -1.7161 | -2.458 | -2.9467 | -5.3906 | -7.0814 | -8.0518
|  | BOURTON PRIMARY | EE |  |  |  |  | 1.1563 | 0.47878 | -0.013061 | -0.11 | -0.57939 | -1.2743 | -2.058 | -2.8396 | -3.3712 | -6.0937 | -7.8049 | -9.0814 | 2.6573 | 2.1012 | 1.7094 | 1.7124 | 1.341 | 0.85837 | 0.3002 | -0.2702 | -0.62327 | -2.6202 | -4.6171 | -7.6763 | 1.292 | 0.62878 | 0.14 | 0.12367 | -0.32224 | -0.97735 | -1.7161 | -2.458 | -2.9467 | -5.3906 | -6.8835 | -7.9335
|  | BOURTON PRIMARY | HT |  |  |  |  | 1.4553 | 0.8849 | 0.57367 | 0.18592 | -0.23347 | -0.53143 | -1.1733 | -1.8406 | -2.5355 | -5.9559 | -8.0345 | -9.2335 | 2.9716 | 2.5431 | 2.3461 | 2.0849 | 1.7982 | 1.7869 | 1.4247 | 1.0359 | 0.62878 | -1.2386 | -2.2018 | -2.6865 | 1.6002 | 1.0614 | 0.76959 | 0.41653 | 0.0083673 | -0.24469 | -0.83755 | -1.4559 | -2.1008 | -5.2406 | -7.0814 | -8.0518
|  | BOURTON PRIMARY | HE |  |  |  |  | 1.442 | 0.87163 | 0.56041 | 0.17163 | -0.25286 | -0.8498 | -1.0845 | -1.7018 | -2.3437 | -5.7049 | -7.6447 | -8.4916 | 2.9094 | 2.4512 | 2.2216 | 1.9186 | 1.5818 | 1.1502 | 1.091 | 0.63286 | 0.14816 | -2.4916 | -4.7202 | -7.6059 | 1.5839 | 1.0441 | 0.7502 | 0.39102 | -0.0018367 | -0.56204 | -0.77633 | -1.3529 | -1.9559 | -5.0539 | -6.7753 | -7.4651
|  | BOURTON PRIMARY | CF |  |  |  |  | 1.6308 | 1.2114 | 0.97469 | 0.76449 | 0.49408 | 0.19918 | -0.1549 | -0.10796 | -0.43041 | -2.6651 | -4.8539 | -6.7988 | 2.991 | 2.6206 | 2.4104 | 2.2155 | 1.9492 | 1.6431 | 1.2727 | 1.2869 | 0.92265 | -1.6212 | -5.2386 | -11.208 | 1.7573 | 1.3553 | 1.1206 | 0.92469 | 0.65735 | 0.36551 | 0.012449 | 0.12265 | -0.17939 | -2.2865 | -4.2876 | -6.0049
MANNINGTON GSP | WAREHAM BSP | BOVINGTON PRIMARY | MINIMUM HEADROOM | SY 83933 87831 | NO | YES | 0.117 | 4.7408 | 4.6214 | 4.5173 | 4.2602 | 4.0224 | 3.7245 | 3.1051 | 2.8439 | 2.3786 | 0.62041 | -0.2398 | -0.74592 | 3.3939 | 3.3082 | 3.2245 | 2.9765 | 2.7959 | 2.6 | 2.2806 | 2.1531 | 1.9102 | 0.88469 | 0.1102 | -1.9602 | 3.7357 | 3.6 | 3.4888 | 3.1653 | 2.8561 | 2.5031 | 2.0347 | 1.7806 | 1.4153 | -0.07551 | -0.8051 | -1.2357
|  | BOVINGTON PRIMARY | EE |  |  |  |  | 4.7408 | 4.6214 | 4.5173 | 4.2602 | 4.0224 | 3.7245 | 3.1051 | 2.8439 | 2.3908 | 0.70918 | -0.083673 | -0.64184 | 3.3939 | 3.3082 | 3.2245 | 2.9765 | 2.7959 | 2.6 | 2.2806 | 2.1531 | 1.9102 | 0.88469 | 0.12041 | -0.97041 | 3.7357 | 3.6 | 3.4888 | 3.1653 | 2.8561 | 2.5031 | 2.0347 | 1.7806 | 1.4153 | -0.0020408 | -0.67755 | -1.1357
|  | BOVINGTON PRIMARY | HT |  |  |  |  | 4.8092 | 4.7122 | 4.6337 | 4.4878 | 4.2796 | 3.9878 | 3.4816 | 2.951 | 2.3786 | 0.62041 | -0.2398 | -0.74592 | 3.448 | 3.3816 | 3.3255 | 3.2276 | 3.0745 | 2.9082 | 2.6969 | 2.451 | 2.149 | 1.2776 | 0.89796 | 0.67245 | 3.7847 | 3.6582 | 3.5602 | 3.3714 | 3.0796 | 2.7408 | 2.3173 | 1.9051 | 1.4439 | -0.07551 | -0.8051 | -1.2357
|  | BOVINGTON PRIMARY | HE |  |  |  |  | 4.8071 | 4.7092 | 4.6286 | 4.3959 | 4.1837 | 3.9704 | 3.5143 | 3.0337 | 2.5418 | 1.0122 | 0.22449 | -0.15714 | 3.4408 | 3.3694 | 3.3051 | 3.0704 | 2.9082 | 2.7408 | 2.5337 | 2.2633 | 1.9857 | 1.0041 | 0.22551 | -0.78878 | 3.7929 | 3.6735 | 3.5827 | 3.2806 | 2.9929 | 2.6908 | 2.3 | 1.9214 | 1.5357 | 0.19184 | -0.52041 | -0.87551
|  | BOVINGTON PRIMARY | CF |  |  |  |  | 4.8673 | 4.7969 | 4.7582 | 4.5449 | 4.302 | 4.1622 | 3.9418 | 3.6796 | 3.3633 | 1.9959 | 1.402 | 0.57755 | 3.4765 | 3.4204 | 3.3755 | 3.1541 | 2.9694 | 2.848 | 2.6724 | 2.4724 | 2.2663 | 1.1714 | 0.1102 | -1.9602 | 3.8673 | 3.7857 | 3.7327 | 3.4694 | 3.199 | 3.0194 | 2.7347 | 2.4765 | 2.2388 | 1.1786 | 0.57245 | -0.14796
AMERSHAM GSP | LOUDWATER BSP | BOWERDEAN PRIMARY | MINIMUM HEADROOM | SU 87718 93880 | NO | YES | 5.388 | 2.1498 | 0.82943 | -0.40629 | -1.6951 | -2.9838 | -4.6787 | -6.4308 | -8.043 | -9.1757 | -16.2114 | -21.4206 | -24.2655 | 6.8764 | 6.0662 | 5.258 | 4.3917 | 3.5039 | 2.4019 | 1.1978 | 0.031469 | -0.71751 | -4.9828 | -10.5349 | -24.3593 | 1.4356 | 0.25188 | -0.87771 | -2.0726 | -3.291 | -4.8665 | -6.5481 | -8.1257 | -9.094 | -14.7614 | -19.2481 | -21.7165
|  | BOWERDEAN PRIMARY | EE |  |  |  |  | 2.1498 | 0.82943 | -0.40629 | -1.6951 | -2.9838 | -4.6787 | -6.4308 | -8.043 | -9.1757 | -15.3042 | -20.2379 | -23.8471 | 6.8764 | 6.0662 | 5.258 | 4.3917 | 3.5039 | 2.4019 | 1.1978 | 0.031469 | -0.71751 | -4.9828 | -9.9093 | -17.3298 | 1.4356 | 0.25188 | -0.87771 | -2.0726 | -3.291 | -4.8665 | -6.5481 | -8.1257 | -9.094 | -14.0685 | -18.194 | -21.3522
|  | BOWERDEAN PRIMARY | HT |  |  |  |  | 2.2162 | 0.90188 | 0.040653 | -1.09 | -2.2175 | -3.8206 | -5.4073 | -6.8859 | -8.3961 | -16.2114 | -21.4206 | -24.2655 | 7.1111 | 6.4141 | 6.0509 | 5.4702 | 4.8907 | 4.1039 | 3.259 | 2.4325 | 1.5743 | -2.4022 | -4.5298 | -5.64 | 1.5825 | 0.4131 | -0.16751 | -1.1593 | -2.1757 | -3.5696 | -4.9981 | -6.3726 | -7.791 | -14.7614 | -19.2481 | -21.7165
|  | BOWERDEAN PRIMARY | HE |  |  |  |  | 2.3182 | 1.0702 | 0.28249 | -0.77567 | -1.8277 | -3.0859 | -4.3277 | -5.4665 | -6.6665 | -13.094 | -17.9471 | -20.2634 | 7.007 | 6.2519 | 5.8304 | 5.1794 | 4.5182 | 3.7396 | 2.9029 | 2.0407 | 1.1304 | -3.9481 | -8.9175 | -15.8165 | 1.6529 | 0.53351 | 0.018204 | -0.91241 | -1.8614 | -2.991 | -4.1593 | -5.2706 | -6.4165 | -12.1502 | -16.1491 | -18.1614
|  | BOWERDEAN PRIMARY | CF |  |  |  |  | 2.8121 | 1.858 | 1.0437 | 0.57433 | -0.14506 | -0.7318 | -1.3247 | -1.8318 | -2.3685 | -6.6481 | -11.3838 | -15.8298 | 7.207 | 6.5611 | 5.9794 | 5.6631 | 5.0845 | 4.4907 | 3.8611 | 3.2162 | 2.508 | -2.69 | -10.5349 | -24.3593 | 2.0804 | 1.2172 | 0.45188 | 0.21412 | -0.44302 | -1.0175 | -1.6114 | -2.1481 | -2.7185 | -6.9002 | -10.9104 | -14.4747
FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL PRIMARY | MINIMUM HEADROOM | SU 86075 69397 | NO | NO | 15.464 | 32.5064 | 31.2533 | 30.3941 | 29.0809 | 27.2472 | 24.9013 | 21.9145 | 19.0574 | 16.6278 | 8.3962 | 2.3992 | -1.1038 | 34.5615 | 33.7115 | 33.1258 | 32.2105 | 30.89 | 29.0156 | 26.7247 | 24.5962 | 22.7023 | 15.7645 | 10.2064 | -2.0406 | 31.6145 | 30.5166 | 29.7696 | 28.587 | 26.938 | 24.6656 | 21.84 | 19.1962 | 16.9339 | 9.2686 | 3.5094 | 0.16351
|  | BRACKNELL PRIMARY | EE |  |  |  |  | 32.5064 | 31.2533 | 30.3941 | 29.0809 | 27.2472 | 24.9013 | 21.9145 | 19.0574 | 16.6278 | 8.7411 | 4.2839 | 0.3676 | 34.5615 | 33.7115 | 33.1258 | 32.2105 | 30.89 | 29.0156 | 26.7247 | 24.5962 | 22.7023 | 15.7645 | 10.2064 | 2.0166 | 31.6145 | 30.5166 | 29.7696 | 28.587 | 26.938 | 24.6656 | 21.84 | 19.1962 | 16.9339 | 9.6451 | 5.5237 | 1.8064
|  | BRACKNELL PRIMARY | HT |  |  |  |  | 32.9911 | 31.9543 | 30.9696 | 29.487 | 28.1656 | 26.1033 | 23.4462 | 20.8237 | 18.2972 | 8.3962 | 2.3992 | -1.1038 | 35.0747 | 34.487 | 33.9207 | 32.9339 | 32.1339 | 30.6492 | 28.7982 | 27.0523 | 25.3013 | 17.9166 | 14.1564 | 12.1176 | 32.1094 | 31.2227 | 30.3502 | 29.0227 | 27.886 | 25.8931 | 23.3931 | 20.9819 | 18.6207 | 9.2686 | 3.5094 | 0.16351
|  | BRACKNELL PRIMARY | HE |  |  |  |  | 32.9727 | 31.9502 | 30.9849 | 29.8319 | 28.4788 | 26.6288 | 24.1768 | 21.8533 | 19.4268 | 8.8839 | 3.7502 | 0.77678 | 34.9156 | 34.2421 | 33.589 | 32.8156 | 31.8594 | 30.4074 | 28.5727 | 26.939 | 25.3166 | 17.3156 | 11.7778 | 4.1033 | 32.087 | 31.2094 | 30.3523 | 29.3298 | 28.1564 | 26.4043 | 24.1329 | 22.0707 | 20.0268 | 9.7635 | 4.886 | 1.8737
|  | BRACKNELL PRIMARY | CF |  |  |  |  | 33.5002 | 32.7298 | 32.1023 | 31.3115 | 30.339 | 29.1839 | 27.7482 | 25.9288 | 24.2798 | 17.2043 | 10.9064 | 6.4237 | 35.1849 | 34.6247 | 34.1329 | 33.5329 | 32.7849 | 31.6594 | 30.3492 | 28.79 | 27.3278 | 20.3002 | 11.7574 | -2.0406 | 32.5737 | 31.9247 | 31.3819 | 30.6931 | 29.8513 | 28.7615 | 27.4656 | 25.8278 | 24.3554 | 17.8584 | 11.8329 | 7.5921
MELKSHAM GSP | NORRINGTON BSP | BRADFORD-ON-AVON PRIMARY | MINIMUM HEADROOM | ST 81260 60564 | NO | YES | 2.885 | 15.5034 | 15.0381 | 14.9218 | 14.4718 | 13.9942 | 13.2013 | 12.3146 | 11.4258 | 10.8187 | 7.3769 | 4.3952 | 2.6697 | 17.6279 | 17.2258 | 17.182 | 16.8024 | 16.3922 | 15.8381 | 15.1942 | 14.5371 | 14.133 | 11.7136 | 8.7809 | 1.3422 | 15.1564 | 14.7126 | 14.6105 | 14.1789 | 13.7156 | 12.9748 | 12.1391 | 11.2973 | 10.7381 | 7.7269 | 5.1687 | 3.6962
|  | BRADFORD-ON-AVON PRIMARY | EE |  |  |  |  | 15.5034 | 15.0381 | 14.9218 | 14.4718 | 13.9942 | 13.2013 | 12.3146 | 11.4258 | 10.8187 | 7.5238 | 4.9534 | 2.9922 | 17.6279 | 17.2258 | 17.182 | 16.8024 | 16.3922 | 15.8381 | 15.1942 | 14.5371 | 14.133 | 11.7136 | 9.0483 | 5.0064 | 15.1564 | 14.7126 | 14.6105 | 14.1789 | 13.7156 | 12.9748 | 12.1391 | 11.2973 | 10.7381 | 7.8177 | 5.6656 | 3.9677
|  | BRADFORD-ON-AVON PRIMARY | HT |  |  |  |  | 15.7973 | 15.4452 | 15.1258 | 14.7279 | 14.2922 | 13.9656 | 13.2228 | 12.4524 | 11.6422 | 7.3769 | 4.3952 | 2.6697 | 17.9707 | 17.7248 | 17.5064 | 17.2228 | 16.9013 | 16.8871 | 16.4605 | 16.0116 | 15.5371 | 13.2697 | 11.9238 | 11.1922 | 15.4544 | 15.1218 | 14.8177 | 14.4391 | 14.0228 | 13.7493 | 13.0575 | 12.3422 | 11.5901 | 7.7269 | 5.1687 | 3.6962
|  | BRADFORD-ON-AVON PRIMARY | HE |  |  |  |  | 15.8167 | 15.486 | 15.1901 | 14.8218 | 14.4177 | 14.2146 | 13.5983 | 12.9544 | 12.2922 | 8.7371 | 6.2411 | 5.0116 | 17.9105 | 17.6279 | 17.3871 | 17.0687 | 16.7167 | 16.6656 | 16.2218 | 15.7473 | 15.2473 | 12.3911 | 9.7044 | 5.984 | 15.4697 | 15.1564 | 14.8758 | 14.5238 | 14.1381 | 13.9769 | 13.4013 | 12.7993 | 12.1769 | 8.9248 | 6.835 | 5.8013
|  | BRADFORD-ON-AVON PRIMARY | CF |  |  |  |  | 16.0462 | 15.836 | 15.6616 | 15.4309 | 15.1697 | 14.8697 | 14.9462 | 14.6524 | 14.3452 | 12.0462 | 9.5881 | 7.2687 | 18.0177 | 17.7973 | 17.6003 | 17.3483 | 17.0524 | 16.7034 | 16.6809 | 16.3156 | 15.9218 | 13.0809 | 8.7809 | 1.3422 | 15.6871 | 15.484 | 15.3167 | 15.0973 | 14.8442 | 14.5534 | 14.636 | 14.3513 | 14.0564 | 11.884 | 9.6636 | 7.6554
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BRAMLEY GREEN PRIMARY | MINIMUM HEADROOM | SU 67431 58511 | NO | NO | 0.833 | 10.2316 | 9.9959 | 9.701 | 9.5214 | 9.2939 | 8.9786 | 8.6153 | 8.6306 | 8.3367 | 7.1786 | 6.248 | 5.6735 | 11.4837 | 11.3245 | 11.1153 | 10.9796 | 10.7959 | 10.5561 | 10.2714 | 10.4245 | 10.299 | 9.6153 | 8.8878 | 7.0439 | 10.4714 | 10.2592 | 9.9857 | 9.8122 | 9.5837 | 9.2643 | 8.8867 | 8.9898 | 8.7347 | 7.7429 | 6.9561 | 6.5031
|  | BRAMLEY GREEN PRIMARY | EE |  |  |  |  | 10.2316 | 9.9959 | 9.701 | 9.5214 | 9.2939 | 8.9786 | 8.6153 | 8.6306 | 8.4194 | 7.2704 | 6.4224 | 5.7673 | 11.4837 | 11.3245 | 11.1153 | 10.9796 | 10.7959 | 10.5561 | 10.2714 | 10.4245 | 10.299 | 9.6153 | 8.8878 | 7.8459 | 10.4714 | 10.2592 | 9.9857 | 9.8122 | 9.5837 | 9.2643 | 8.8867 | 8.9898 | 8.8041 | 7.8173 | 7.1184 | 6.5857
|  | BRAMLEY GREEN PRIMARY | HT |  |  |  |  | 10.3337 | 10.1061 | 9.8429 | 9.7041 | 9.5184 | 9.2735 | 8.9724 | 8.6582 | 8.3367 | 7.1786 | 6.248 | 5.6735 | 11.6194 | 11.4847 | 11.3296 | 11.249 | 11.1214 | 10.9939 | 10.8041 | 10.6031 | 10.3969 | 9.9796 | 9.5857 | 9.3551 | 10.5908 | 10.3918 | 10.1561 | 10.0255 | 9.8459 | 9.6255 | 9.3408 | 9.0408 | 8.7347 | 7.7429 | 6.9561 | 6.5031
|  | BRAMLEY GREEN PRIMARY | HE |  |  |  |  | 10.348 | 10.1265 | 9.8745 | 9.7469 | 9.5735 | 9.3816 | 9.1296 | 8.8694 | 8.598 | 7.6459 | 6.8184 | 6.399 | 11.602 | 11.4612 | 11.298 | 11.2102 | 11.0765 | 10.951 | 10.7612 | 10.5653 | 10.349 | 9.8041 | 9.0663 | 8.1194 | 10.6 | 10.4061 | 10.1816 | 10.0612 | 9.8929 | 9.7163 | 9.4724 | 9.2184 | 8.9531 | 8.1622 | 7.4663 | 7.1378
|  | BRAMLEY GREEN PRIMARY | CF |  |  |  |  | 10.4857 | 10.3847 | 10.2357 | 10.1051 | 9.9316 | 9.7806 | 9.6469 | 9.5541 | 9.4194 | 8.8112 | 7.9704 | 7.1949 | 11.6551 | 11.5735 | 11.4622 | 11.3694 | 11.2398 | 11.1082 | 10.9643 | 10.8622 | 10.7071 | 10.101 | 8.9418 | 7.0439 | 10.7133 | 10.6235 | 10.4888 | 10.3755 | 10.2173 | 10.0724 | 9.9367 | 9.8469 | 9.7031 | 9.1602 | 8.4245 | 7.7622
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD PRIMARY | MINIMUM HEADROOM | SZ 64712 98665 | NO | YES | 2.432 | 10.7624 | 9.992 | 9.1563 | 8.1736 | 7.1369 | 6.1175 | 4.5583 | 3.0114 | 1.7379 | -2.7457 | -5.8712 | -5.6957 | 14.1461 | 13.4645 | 12.7216 | 11.8379 | 10.8849 | 10.0043 | 8.7165 | 7.3941 | 6.2441 | 0.45018 | -8.9233 | -30.9202 | 10.6634 | 9.9277 | 9.1236 | 8.1726 | 7.1532 | 6.2032 | 4.7134 | 3.2328 | 2.0257 | -2.16 | -4.9559 | -4.7794
|  | BRANDON ROAD PRIMARY | EE |  |  |  |  | 10.7624 | 9.992 | 9.1563 | 8.1736 | 7.1369 | 6.1175 | 4.5583 | 3.0114 | 1.7379 | -2.7457 | -4.5835 | -4.1539 | 14.1461 | 13.4645 | 12.7216 | 11.8379 | 10.8849 | 10.0043 | 8.7165 | 7.3941 | 6.2441 | 0.45018 | -5.7508 | -15.711 | 10.6634 | 9.9277 | 9.1236 | 8.1726 | 7.1532 | 6.2032 | 4.7134 | 3.2328 | 2.0257 | -2.16 | -3.7733 | -3.4498
|  | BRANDON ROAD PRIMARY | HT |  |  |  |  | 11.3145 | 10.7634 | 10.1788 | 9.492 | 8.8002 | 7.7481 | 6.5369 | 5.2502 | 4.2788 | -2.157 | -5.8712 | -5.6957 | 14.7481 | 14.3971 | 13.9961 | 13.5104 | 13.0053 | 12.342 | 11.5553 | 10.7083 | 10.0828 | 5.9114 | 3.489 | 3.3461 | 11.2134 | 10.6971 | 10.1451 | 9.489 | 8.8216 | 7.8298 | 6.6808 | 5.4583 | 4.5563 | -1.5059 | -4.9559 | -4.7794
|  | BRANDON ROAD PRIMARY | HE |  |  |  |  | 11.3298 | 10.839 | 10.3308 | 9.741 | 9.1665 | 8.2869 | 7.2685 | 6.2053 | 5.5002 | 1.44 | -0.23656 | -0.28247 | 14.5328 | 14.0828 | 13.6053 | 13.0155 | 12.4073 | 11.6298 | 10.7277 | 9.7532 | 8.989 | 3.3104 | -2.96 | -12.9733 | 11.2247 | 10.7665 | 10.2879 | 9.7257 | 9.1716 | 8.3451 | 7.3808 | 6.3747 | 5.7216 | 1.8706 | 0.34916 | 0.33589
|  | BRANDON ROAD PRIMARY | CF |  |  |  |  | 11.7216 | 11.3941 | 11.0481 | 10.7196 | 10.3543 | 9.99 | 9.5594 | 9.0441 | 8.4961 | 5.5747 | 1.8788 | -1.5274 | 14.6879 | 14.2839 | 13.841 | 13.3634 | 12.7818 | 12.091 | 11.3012 | 10.4196 | 9.4665 | 2.991 | -8.9233 | -30.9202 | 11.5951 | 11.289 | 10.9553 | 10.6349 | 10.2706 | 9.9094 | 9.491 | 8.9777 | 8.4318 | 5.642 | 2.2206 | -0.859
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | BRAYWICK ROAD PRIMARY | MINIMUM HEADROOM | SU 88887 80726 | NO | NO | 6.338 | -7.6976 | -9.2129 | -11.1344 | -13.368 | -15.466 | -17.3946 | -19.0201 | -19.9344 | -20.6609 | -23.9639 | -26.3752 | -27.3497 | -1.6746 | -2.6582 | -3.5031 | -4.4817 | -5.6031 | -6.7337 | -7.7348 | -8.3807 | -8.9042 | -11.5868 | -14.8358 | -22.6521 | -8.0723 | -9.4274 | -11.0539 | -12.9335 | -14.6284 | -16.3039 | -17.7397 | -18.6274 | -19.2937 | -22.2162 | -24.256 | -25.0591
|  | BRAYWICK ROAD PRIMARY | EE |  |  |  |  | -7.6976 | -9.2129 | -11.1344 | -13.368 | -15.466 | -17.3946 | -19.0201 | -19.9344 | -20.6609 | -23.9639 | -25.9874 | -26.9425 | -1.6746 | -2.6582 | -3.5031 | -4.4817 | -5.6031 | -6.7337 | -7.7348 | -8.3807 | -8.9042 | -11.5868 | -14.1368 | -17.7327 | -8.0723 | -9.4274 | -11.0539 | -12.9335 | -14.6284 | -16.3039 | -17.7397 | -18.6274 | -19.2937 | -22.2162 | -23.9284 | -24.7417
|  | BRAYWICK ROAD PRIMARY | HT |  |  |  |  | -7.6548 | -9.1037 | -10.9354 | -13.0435 | -15.4078 | -16.9272 | -18.1435 | -18.9303 | -19.7364 | -23.8109 | -26.3752 | -27.3497 | -1.4715 | -2.3552 | -3.0786 | -3.9327 | -5.1276 | -5.9521 | -6.5613 | -6.9991 | -7.4684 | -9.8093 | -11.0858 | -11.5562 | -7.9182 | -9.1937 | -10.7121 | -12.4693 | -14.4601 | -15.7856 | -16.7978 | -17.5152 | -18.2652 | -21.9948 | -24.256 | -25.0591
|  | BRAYWICK ROAD PRIMARY | HE |  |  |  |  | -7.4486 | -8.7507 | -10.3762 | -12.3027 | -14.4537 | -16.0946 | -17.4466 | -18.3599 | -19.2986 | -23.3537 | -25.7139 | -26.5262 | -1.4827 | -2.3746 | -3.1011 | -3.8746 | -5.0409 | -6.0225 | -6.797 | -7.4164 | -8.0746 | -11.5286 | -14.2766 | -17.8001 | -7.7764 | -8.9448 | -10.3029 | -11.9172 | -13.7417 | -15.1601 | -16.2805 | -17.1019 | -17.9539 | -21.6611 | -23.7305 | -24.455
|  | BRAYWICK ROAD PRIMARY | CF |  |  |  |  | -6.8966 | -7.6527 | -8.5027 | -9.5833 | -11.2068 | -13.167 | -14.9782 | -15.368 | -15.9293 | -19.118 | -22.1854 | -24.967 | -1.2184 | -1.9235 | -2.4103 | -2.9205 | -3.5858 | -4.7613 | -5.8511 | -6.2093 | -6.7164 | -10.047 | -14.8358 | -22.6521 | -7.3356 | -8.0488 | -8.7835 | -9.6866 | -11.0244 | -12.6295 | -14.1346 | -14.4397 | -14.9478 | -17.9142 | -20.6642 | -23.0876
EALING GSP | EALING BSP | BRENTFORD PRIMARY | MINIMUM HEADROOM | TQ 17659 78277 | NO | NO | 13.703 | 6.0886 | 4.7692 | 3.3713 | 1.7396 | -0.492 | -2.3369 | -4.6032 | -6.8308 | -8.5563 | -13.8665 | -17.4889 | -18.5053 | 10.9815 | 10.0029 | 8.9651 | 7.7876 | 6.1447 | 4.4631 | 2.558 | 0.62738 | -0.97466 | -7.794 | -18.742 | -42.1185 | 7.1182 | 5.9355 | 4.6396 | 3.1621 | 1.1355 | -0.6818 | -2.8185 | -4.9196 | -6.5461 | -11.5083 | -14.7379 | -15.594
|  | BRENTFORD PRIMARY | EE |  |  |  |  | 6.0886 | 4.7692 | 3.3713 | 1.7631 | -0.31241 | -2.3369 | -4.6032 | -6.8308 | -8.5563 | -13.8665 | -16.5338 | -17.4338 | 10.9815 | 10.0029 | 8.9651 | 7.7876 | 6.1447 | 4.4631 | 2.558 | 0.62738 | -0.97466 | -7.794 | -14.6308 | -25.9614 | 7.1182 | 5.9355 | 4.6396 | 3.1621 | 1.2202 | -0.6818 | -2.8185 | -4.9196 | -6.5461 | -11.5083 | -13.8655 | -14.6869
|  | BRENTFORD PRIMARY | HT |  |  |  |  | 6.4233 | 5.2539 | 3.9294 | 1.7396 | -0.492 | -2.2451 | -3.9491 | -5.2624 | -6.7665 | -13.0451 | -17.4889 | -18.5053 | 11.5019 | 10.8509 | 10.0927 | 8.5458 | 7.0019 | 5.7651 | 4.4753 | 3.4968 | 2.3855 | -1.8961 | -4.492 | -5.0696 | 7.4998 | 6.4804 | 5.2947 | 3.2468 | 1.1355 | -0.49404 | -2.1022 | -3.3879 | -4.8022 | -10.6604 | -14.7379 | -15.594
|  | BRENTFORD PRIMARY | HE |  |  |  |  | 6.6621 | 5.56 | 4.4662 | 3.2733 | 1.1641 | -0.46037 | -2.2818 | -3.6165 | -5.2022 | -10.4828 | -13.0236 | -13.5583 | 11.4325 | 10.6335 | 9.8427 | 8.9958 | 7.3325 | 5.9437 | 4.3723 | 3.0784 | 1.5427 | -5.5206 | -12.6165 | -23.7236 | 7.7019 | 6.7202 | 5.7304 | 4.6631 | 2.6845 | 1.1611 | -0.54098 | -1.8328 | -3.3318 | -8.2767 | -10.5563 | -10.994
|  | BRENTFORD PRIMARY | CF |  |  |  |  | 7.308 | 6.7804 | 6.1111 | 5.5345 | 4.9651 | 4.2202 | 3.1692 | 1.9151 | 1.058 | -6.1175 | -9.7624 | -13.0471 | 11.7223 | 11.2121 | 10.5315 | 9.9172 | 9.2243 | 8.1458 | 6.808 | 5.3151 | 4.0896 | -5.9083 | -18.742 | -42.1185 | 8.2549 | 7.7866 | 7.1672 | 6.6315 | 6.106 | 5.3733 | 4.3621 | 3.1784 | 2.3937 | -4.194 | -7.5767 | -10.6185
EALING GSP |  | BRIDGE ROAD PRIMARY | MINIMUM HEADROOM | TQ 14778 75741 | NO | NO | 27.371 | 22.6253 | 21.1488 | 19.409 | 16.7426 | 89.9632 | 87.1295 | 83.6397 | 79.7683 | 76.5469 | 68.0908 | 63.7948 | 63.4234 | 33.8824 | 32.9324 | 31.5906 | 29.9661 | 103.9795 | 101.7193 | 99.0816 | 96.1775 | 93.7693 | 84.4999 | 71.3255 | 42.6224 | 24.609 | 23.4426 | 21.7539 | 19.6753 | 93.0591 | 90.1877 | 86.9336 | 83.3704 | 80.5193 | 73.0673 | 69.4387 | 69.154
|  | BRIDGE ROAD PRIMARY | EE |  |  |  |  | 22.6253 | 21.259 | 19.411 | 17.1141 | 90.2499 | 87.1295 | 83.6397 | 79.7683 | 76.5469 | 68.0908 | 64.7622 | 65.3561 | 33.8824 | 32.9324 | 31.5906 | 29.9661 | 103.9795 | 101.7193 | 99.0816 | 96.1775 | 93.7693 | 84.4999 | 76.0938 | 63.1204 | 24.609 | 23.4426 | 21.7539 | 19.6753 | 93.0591 | 90.1877 | 86.9336 | 83.3704 | 80.5193 | 73.0673 | 70.3071 | 70.6816
|  | BRIDGE ROAD PRIMARY | HT |  |  |  |  | 22.9518 | 21.1488 | 19.409 | 16.7426 | 89.9632 | 87.2857 | 84.352 | 81.2591 | 78.3255 | 69.0663 | 63.7948 | 63.4234 | 34.6416 | 33.6222 | 32.8028 | 31.2243 | 105.6408 | 103.9857 | 102.0591 | 99.9704 | 98.0081 | 91.6785 | 88.4806 | 87.9632 | 25.1345 | 23.5804 | 22.1692 | 19.7967 | 93.3489 | 90.951 | 88.2704 | 85.4387 | 82.7775 | 74.1428 | 69.4387 | 69.154
|  | BRIDGE ROAD PRIMARY | HE |  |  |  |  | 23.5518 | 22.1161 | 20.6008 | 19.111 | 92.7653 | 90.3683 | 87.651 | 84.5255 | 81.4571 | 73.1612 | 70.1112 | 69.5387 | 34.6957 | 33.6416 | 32.5753 | 31.7039 | 106.1204 | 104.3663 | 102.3255 | 99.951 | 97.5357 | 87.7336 | 79.2112 | 65.7428 | 25.6008 | 24.3233 | 22.9743 | 21.7845 | 95.7142 | 93.5775 | 91.1255 | 88.3153 | 85.5561 | 77.8816 | 75.253 | 74.8081
|  | BRIDGE ROAD PRIMARY | CF |  |  |  |  | 24.5171 | 24.0539 | 23.3733 | 22.7192 | 98.6336 | 97.7724 | 96.4918 | 94.9306 | 93.1693 | 79.0459 | 72.9755 | 68.0612 | 35.11 | 34.5355 | 33.7528 | 32.9539 | 108.605 | 107.451 | 105.9755 | 104.2581 | 102.3367 | 87.6163 | 71.3255 | 42.6224 | 26.4263 | 25.9733 | 25.3192 | 24.6906 | 100.6663 | 99.8326 | 98.6153 | 97.1489 | 95.5204 | 83.1734 | 77.7346 | 73.501
LOVEDEAN GSP | HAVANT BSP | BROCKHAMPTON PRIMARY | MINIMUM HEADROOM | SU 70868 05828 | NO | YES | 5.213 | 11.4601 | 10.9397 | 10.3285 | 9.6234 | 8.8581 | 8.0662 | 7.2887 | 6.6622 | 5.9152 | 3.3805 | 2.0795 | 1.3632 | 11.1377 | 10.6938 | 10.1724 | 9.5469 | 8.8754 | 8.1979 | 7.5642 | 6.9887 | 6.3754 | 4.3591 | 3.4397 | 2.3295 | 10.755 | 10.0958 | 9.3418 | 8.5795 | 7.7581 | 6.8907 | 6.0234 | 5.3162 | 4.5836 | 2.1152 | 0.88767 | 0.20298
|  | BROCKHAMPTON PRIMARY | EE |  |  |  |  | 11.6367 | 11.0428 | 10.3285 | 9.6234 | 8.8581 | 8.0662 | 7.2887 | 6.6622 | 5.9152 | 3.8305 | 3.2264 | 3.2336 | 11.3244 | 10.7969 | 10.1724 | 9.5469 | 8.8754 | 8.1979 | 7.5642 | 6.9887 | 6.3754 | 4.7979 | 4.4622 | 4.4152 | 10.7713 | 10.0958 | 9.3418 | 8.5795 | 7.7581 | 6.8907 | 6.0234 | 5.3162 | 4.5836 | 2.5724 | 2.0213 | 2.0275
|  | BROCKHAMPTON PRIMARY | HT |  |  |  |  | 11.4601 | 10.9397 | 10.3683 | 9.8173 | 9.1836 | 8.6203 | 7.9897 | 7.3101 | 6.7785 | 4.1101 | 2.8224 | 2.3071 | 11.1377 | 10.6938 | 10.1877 | 9.6387 | 9.0816 | 8.6213 | 8.103 | 7.5489 | 7.1499 | 5.053 | 4.1846 | 3.7969 | 10.755 | 10.1856 | 9.5397 | 8.8887 | 8.2111 | 7.5928 | 6.8867 | 6.1316 | 5.5091 | 2.8367 | 1.6316 | 1.1438
|  | BROCKHAMPTON PRIMARY | HE |  |  |  |  | 11.7724 | 11.2581 | 10.6907 | 10.0703 | 9.3754 | 8.654 | 7.9724 | 7.2387 | 6.456 | 3.3805 | 2.0795 | 1.3632 | 11.4397 | 10.9846 | 10.4673 | 9.8989 | 9.2816 | 8.6571 | 8.0938 | 7.4918 | 6.7948 | 4.3591 | 3.4397 | 2.8642 | 11.053 | 10.4458 | 9.7785 | 9.103 | 8.3581 | 7.5693 | 6.7999 | 5.9734 | 5.1132 | 2.1152 | 0.88767 | 0.20298
|  | BROCKHAMPTON PRIMARY | CF |  |  |  |  | 11.9183 | 11.7928 | 11.3224 | 10.903 | 10.4795 | 9.9367 | 9.354 | 8.8744 | 8.352 | 6.1152 | 3.9122 | 2.253 | 11.5336 | 11.4499 | 11.0213 | 10.602 | 10.1744 | 9.6877 | 9.1622 | 8.7438 | 8.2928 | 6.4336 | 4.6897 | 2.3295 | 11.206 | 11.0999 | 10.6428 | 10.1316 | 9.5969 | 9.0316 | 8.4101 | 7.8816 | 7.304 | 4.754 | 2.5887 | 1.052
LOVEDEAN GSP | FAREHAM (MAIN) BSP | BROCKHURST PRIMARY | MINIMUM HEADROOM | SU 59381 02061 | NO | YES | 4.112 | 9.0516 | 8.5067 | 8.1976 | 7.5129 | 6.6965 | 34.1639 | 32.8731 | 31.5424 | 30.4802 | 26.0537 | 22.669 | 20.5282 | 10.5465 | 10.0659 | 9.8363 | 9.2914 | 8.6812 | 34.6445 | 33.7424 | 32.7955 | 32.0537 | 28.2037 | 22.9557 | 11.5802 | 9.0231 | 8.4547 | 8.1935 | 7.5557 | 6.8118 | 33.469 | 32.2965 | 31.1006 | 30.1741 | 26.2802 | 23.3761 | 21.668
|  | BROCKHURST PRIMARY | EE |  |  |  |  | 9.0516 | 8.5067 | 8.2108 | 7.5129 | 6.6965 | 34.1639 | 32.8731 | 31.5424 | 30.4802 | 26.0537 | 23.1006 | 20.672 | 10.5465 | 10.0659 | 9.8363 | 9.2914 | 8.6812 | 34.6445 | 33.7424 | 32.7955 | 32.0537 | 28.2037 | 24.3333 | 18.3567 | 9.0231 | 8.4547 | 8.1935 | 7.5557 | 6.8118 | 33.469 | 32.2965 | 31.1006 | 30.1741 | 26.2802 | 23.7853 | 21.7935
|  | BROCKHURST PRIMARY | HT |  |  |  |  | 9.2486 | 8.7139 | 8.1976 | 7.5251 | 6.722 | 34.6333 | 33.5414 | 32.5659 | 31.4833 | 26.1241 | 22.669 | 20.5282 | 10.9067 | 10.5618 | 10.2384 | 9.82 | 9.3261 | 35.8098 | 35.1884 | 34.5986 | 33.9435 | 30.9047 | 29.2751 | 28.4302 | 9.318 | 8.8169 | 8.3353 | 7.7067 | 6.9578 | 34.0996 | 33.1129 | 32.1986 | 31.218 | 26.3884 | 23.3761 | 21.668
|  | BROCKHURST PRIMARY | HE |  |  |  |  | 9.3016 | 8.8527 | 8.418 | 7.8414 | 7.1363 | 35.1282 | 34.119 | 33.0771 | 31.9792 | 27.2486 | 24.1629 | 22.7649 | 10.819 | 10.4465 | 10.0945 | 9.6251 | 9.0771 | 35.47 | 34.7578 | 33.9873 | 33.1741 | 28.8567 | 24.8353 | 19.2741 | 9.3537 | 8.919 | 8.5037 | 7.9527 | 7.2863 | 34.4976 | 33.5802 | 32.6261 | 31.6496 | 27.3782 | 24.7924 | 23.6618
|  | BROCKHURST PRIMARY | CF |  |  |  |  | 9.6976 | 9.5149 | 9.3435 | 9.1363 | 8.8486 | 37.071 | 36.9792 | 36.521 | 35.8812 | 31.421 | 28.2884 | 25.7292 | 11.0037 | 10.7527 | 10.5118 | 10.2016 | 9.7884 | 36.0476 | 35.7904 | 35.2302 | 34.5547 | 29.6996 | 22.9557 | 11.5802 | 9.7047 | 9.4986 | 9.3129 | 9.0761 | 8.769 | 36.0741 | 36.0129 | 35.5976 | 35.0394 | 31.1557 | 28.3047 | 26.0231
MELKSHAM GSP | NORRINGTON BSP | BROMHAM PRIMARY | MINIMUM HEADROOM | ST 98670 65994 | YES | YES | 0.336 | 2.3454 | 2.2454 | 2.1668 | 2.0393 | 1.8985 | 1.7526 | 1.5046 | 1.273 | 1.1597 | 0.58214 | 0.15153 | -0.1148 | 2.7827 | 2.702 | 2.6378 | 2.5378 | 2.4357 | 2.3388 | 2.1714 | 2.0122 | 1.9347 | 1.5296 | 1.0765 | -0.013265 | 2.0776 | 1.9673 | 1.8837 | 1.7551 | 1.6194 | 1.4847 | 1.252 | 1.0296 | 0.92551 | 0.42041 | 0.068367 | -0.14796
|  | BROMHAM PRIMARY | EE |  |  |  |  | 2.3454 | 2.2454 | 2.1668 | 2.0393 | 1.8985 | 1.7526 | 1.5046 | 1.273 | 1.1597 | 0.58214 | 0.20867 | -0.043367 | 2.7827 | 2.702 | 2.6378 | 2.5378 | 2.4357 | 2.3388 | 2.1714 | 2.0122 | 1.9347 | 1.5296 | 1.1357 | 0.56735 | 2.0776 | 1.9673 | 1.8837 | 1.7551 | 1.6194 | 1.4847 | 1.252 | 1.0296 | 0.92551 | 0.42041 | 0.12245 | -0.087755
|  | BROMHAM PRIMARY | HT |  |  |  |  | 2.4056 | 2.3209 | 2.2536 | 2.1689 | 2.0699 | 1.8974 | 1.7321 | 1.5587 | 1.4168 | 0.59541 | 0.15153 | -0.1148 | 2.8541 | 2.7959 | 2.7541 | 2.6939 | 2.6235 | 2.5378 | 2.4367 | 2.3224 | 2.251 | 1.7724 | 1.5755 | 1.4653 | 2.1531 | 2.0653 | 2.001 | 1.9143 | 1.8112 | 1.6612 | 1.4969 | 1.3224 | 1.202 | 0.43061 | 0.068367 | -0.14796
|  | BROMHAM PRIMARY | HE |  |  |  |  | 2.4087 | 2.3301 | 2.2668 | 2.1883 | 2.0934 | 1.9944 | 1.8311 | 1.6454 | 1.526 | 0.74439 | 0.38214 | 0.20153 | 2.8439 | 2.7796 | 2.7347 | 2.6684 | 2.5949 | 2.5265 | 2.4102 | 2.2806 | 2.201 | 1.6173 | 1.2214 | 0.67959 | 2.1571 | 2.0714 | 2.0112 | 1.9296 | 1.8316 | 1.7388 | 1.5786 | 1.3939 | 1.2929 | 0.56735 | 0.27653 | 0.13265
|  | BROMHAM PRIMARY | CF |  |  |  |  | 2.4434 | 2.3954 | 2.3526 | 2.2913 | 2.2332 | 2.1597 | 2.1097 | 2.0168 | 1.9087 | 1.3281 | 0.88316 | 0.49133 | 2.8582 | 2.8163 | 2.7796 | 2.7224 | 2.6633 | 2.5929 | 2.5367 | 2.4459 | 2.35 | 1.7765 | 1.0765 | -0.013265 | 2.1867 | 2.1337 | 2.0929 | 2.0286 | 1.9663 | 1.8878 | 1.8357 | 1.7378 | 1.6357 | 1.0867 | 0.66837 | 0.34592
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | BROOK STREET PRIMARY | MINIMUM HEADROOM | SU 63480 52228 | NO | NO | 2.843 | 15.3038 | 15.1129 | 14.8936 | 14.6599 | 14.4017 | 14.066 | 13.5395 | 12.9732 | 12.3752 | 9.6129 | 8.3476 | 8.2232 | 16.2038 | 16.0885 | 15.9558 | 15.8201 | 15.6619 | 15.4476 | 15.0752 | 14.6629 | 14.3272 | 12.3915 | 8.2527 | 0.50989 | 15.1405 | 14.9609 | 14.7344 | 14.5078 | 14.2344 | 13.8629 | 13.4691 | 13.0446 | 12.5201 | 9.8783 | 8.6813 | 8.5691
|  | BROOK STREET PRIMARY | EE |  |  |  |  | 15.3038 | 15.1129 | 14.8936 | 14.6599 | 14.4017 | 14.0864 | 13.6874 | 13.2629 | 12.9425 | 11.6415 | 10.7517 | 9.9721 | 16.2038 | 16.0885 | 15.9558 | 15.8201 | 15.6619 | 15.4476 | 15.0752 | 14.6629 | 14.3272 | 12.3915 | 10.0793 | 6.1385 | 15.1405 | 14.9609 | 14.7344 | 14.5078 | 14.2344 | 13.8629 | 13.4691 | 13.0446 | 12.714 | 11.2987 | 10.5089 | 9.8089
|  | BROOK STREET PRIMARY | HT |  |  |  |  | 15.5262 | 15.4415 | 15.3487 | 15.2283 | 15.0803 | 14.9017 | 14.6783 | 14.3864 | 13.9885 | 11.9834 | 10.6293 | 10.015 | 16.3599 | 16.3089 | 16.2558 | 16.1936 | 16.115 | 16.0354 | 15.9262 | 15.8089 | 15.6834 | 14.5272 | 13.7527 | 13.4456 | 15.3048 | 15.2078 | 15.0813 | 14.9242 | 14.7415 | 14.4956 | 14.1823 | 13.8538 | 13.5109 | 11.6905 | 10.4466 | 9.914
|  | BROOK STREET PRIMARY | HE |  |  |  |  | 15.365 | 15.1752 | 14.964 | 14.7129 | 14.4232 | 14.066 | 13.5395 | 12.9732 | 12.3752 | 9.6129 | 8.3476 | 8.2232 | 16.2517 | 16.1436 | 16.0313 | 15.8956 | 15.7395 | 15.566 | 15.3415 | 14.9527 | 14.514 | 12.4905 | 10.0987 | 6.3905 | 15.2017 | 15.0844 | 14.9538 | 14.7956 | 14.5191 | 14.1334 | 13.6323 | 13.0905 | 12.5201 | 9.8783 | 8.6813 | 8.5691
|  | BROOK STREET PRIMARY | CF |  |  |  |  | 15.6048 | 15.5232 | 15.4191 | 15.2752 | 15.1089 | 14.9313 | 14.6844 | 14.4191 | 14.1262 | 11.965 | 9.9272 | 8.3987 | 16.366 | 16.2895 | 16.2027 | 16.1058 | 15.9885 | 15.8629 | 15.7007 | 15.4068 | 15.0568 | 12.5752 | 8.2527 | 0.50989 | 15.367 | 15.2997 | 15.217 | 15.1313 | 15.0262 | 14.9038 | 14.7395 | 14.5058 | 14.2068 | 12.1048 | 10.1558 | 8.7099
MELKSHAM GSP | FROME BSP | BRUTON PRIMARY | MINIMUM HEADROOM | ST 69094 35148 | NO | NO | 1.13 | 2.3041 | 2.1714 | 2.0622 | 1.9133 | 1.7541 | 1.5673 | 1.3102 | 1.048 | 0.89388 | 0.09898 | -0.43367 | -0.77755 | 2.7986 | 2.6802 | 2.5914 | 2.4578 | 2.3149 | 2.1822 | 1.9741 | 1.769 | 1.6649 | 1.1384 | 0.5598 | -1.0106 | 1.962 | 1.8182 | 1.709 | 1.5447 | 1.3682 | 1.1937 | 0.92939 | 0.66918 | 0.53041 | -0.10837 | -0.53796 | -0.82265
|  | BRUTON PRIMARY | EE |  |  |  |  | 2.3041 | 2.1714 | 2.0622 | 1.9133 | 1.7541 | 1.5673 | 1.3102 | 1.048 | 0.89388 | 0.09898 | -0.36939 | -0.69082 | 2.7986 | 2.6802 | 2.5914 | 2.4578 | 2.3149 | 2.1822 | 1.9741 | 1.769 | 1.6649 | 1.1384 | 0.64245 | -0.16776 | 1.962 | 1.8182 | 1.709 | 1.5447 | 1.3682 | 1.1937 | 0.92939 | 0.66918 | 0.53041 | -0.10837 | -0.47265 | -0.74714
|  | BRUTON PRIMARY | HT |  |  |  |  | 2.3806 | 2.2969 | 2.1959 | 2.0827 | 1.9939 | 1.8102 | 1.6041 | 1.4296 | 1.2153 | 0.15 | -0.43367 | -0.77755 | 2.8894 | 2.8302 | 2.7629 | 2.6751 | 2.6169 | 2.4976 | 2.3618 | 2.2547 | 2.1129 | 1.469 | 1.2067 | 1.0669 | 2.058 | 1.9773 | 1.8773 | 1.759 | 1.6733 | 1.4967 | 1.2947 | 1.1365 | 0.92327 | -0.063469 | -0.53796 | -0.82265
|  | BRUTON PRIMARY | HE |  |  |  |  | 2.3827 | 2.3031 | 2.2092 | 2.099 | 2.0184 | 1.8551 | 1.6694 | 1.5153 | 1.3224 | 0.33061 | -0.12959 | -0.3398 | 2.8771 | 2.8139 | 2.7384 | 2.6465 | 2.5802 | 2.4588 | 2.3139 | 2.2057 | 2.0516 | 1.2833 | 0.77918 | 0.014898 | 2.06 | 1.9835 | 1.8886 | 1.7773 | 1.6978 | 1.5376 | 1.3569 | 1.2151 | 1.0222 | 0.10796 | -0.25224 | -0.42878
|  | BRUTON PRIMARY | CF |  |  |  |  | 2.4388 | 2.3684 | 2.3163 | 2.248 | 2.1673 | 2.0765 | 2.0102 | 1.9031 | 1.7918 | 1.1214 | 0.53163 | 0.018367 | 2.9088 | 2.8384 | 2.7924 | 2.7271 | 2.6465 | 2.5496 | 2.4761 | 2.3608 | 2.2373 | 1.4904 | 0.5598 | -1.0106 | 2.1151 | 2.0324 | 1.9845 | 1.912 | 1.8284 | 1.7365 | 1.6671 | 1.5498 | 1.4304 | 0.7549 | 0.24061 | -0.15429
COWLEY GSP | WITNEY BSP | BURFORD PRIMARY | MINIMUM HEADROOM | SP 25671 12529 | NO | NO | 0.981 | 3.3793 | 3.3018 | 3.1997 | 3.0813 | 2.9946 | 2.8477 | 2.6722 | 2.4977 | 2.3987 | 2.0364 | 1.8752 | 1.7334 | 4.5554 | 4.5013 | 4.4207 | 4.3309 | 4.2564 | 4.1462 | 4.0136 | 3.8778 | 3.7952 | 3.4513 | 2.9064 | 1.6197 | 4.0773 | 4.0018 | 3.9028 | 3.7896 | 3.7069 | 3.561 | 3.3916 | 3.2222 | 3.1314 | 2.8008 | 2.6477 | 2.513
|  | BURFORD PRIMARY | EE |  |  |  |  | 3.3793 | 3.3018 | 3.1997 | 3.0813 | 2.9946 | 2.8477 | 2.6722 | 2.4977 | 2.3987 | 2.0364 | 1.8895 | 1.7936 | 4.5554 | 4.5013 | 4.4207 | 4.3309 | 4.2564 | 4.1462 | 4.0136 | 3.8778 | 3.7952 | 3.4513 | 3.0962 | 2.5105 | 4.0773 | 4.0018 | 3.9028 | 3.7896 | 3.7069 | 3.561 | 3.3916 | 3.2222 | 3.1314 | 2.8008 | 2.6589 | 2.5702
|  | BURFORD PRIMARY | HT |  |  |  |  | 3.4599 | 3.3926 | 3.3109 | 3.2497 | 3.1589 | 3.0528 | 2.9222 | 2.8273 | 2.6864 | 2.1303 | 1.8752 | 1.7334 | 4.6278 | 4.586 | 4.534 | 4.4901 | 4.4309 | 4.3625 | 4.2748 | 4.2136 | 4.1176 | 3.7646 | 3.6064 | 3.5299 | 4.1528 | 4.0926 | 4.014 | 3.9559 | 3.8681 | 3.7661 | 3.6416 | 3.5508 | 3.4161 | 2.8906 | 2.6477 | 2.513
|  | BURFORD PRIMARY | HE |  |  |  |  | 3.4579 | 3.3926 | 3.312 | 3.2548 | 3.1691 | 3.0671 | 2.9405 | 2.8507 | 2.715 | 2.1487 | 1.9854 | 1.9252 | 4.6156 | 4.5697 | 4.5084 | 4.4646 | 4.3942 | 4.3156 | 4.2207 | 4.1472 | 4.0411 | 3.5442 | 3.1666 | 2.6084 | 4.1487 | 4.0916 | 4.0161 | 3.962 | 3.8804 | 3.7814 | 3.661 | 3.5763 | 3.4487 | 2.912 | 2.7477 | 2.6936
|  | BURFORD PRIMARY | CF |  |  |  |  | 3.4864 | 3.4252 | 3.3722 | 3.3038 | 3.2579 | 3.1885 | 3.112 | 3.0211 | 2.9324 | 2.4752 | 2.2058 | 1.964 | 4.634 | 4.5891 | 4.5442 | 4.487 | 4.4442 | 4.3789 | 4.3033 | 4.2176 | 4.1258 | 3.584 | 2.9064 | 1.6197 | 4.1722 | 4.1222 | 4.0712 | 4.0079 | 3.9671 | 3.9018 | 3.8273 | 3.7436 | 3.6528 | 3.214 | 2.963 | 2.7232
MANNINGTON GSP | WAREHAM BSP | BUSHEY PRIMARY | MINIMUM HEADROOM | SY 97671 83532 | YES | YES | 0.074 | 3.8903 | 3.8464 | 3.7423 | 3.7005 | 3.6321 | 3.5546 | 3.4556 | 3.3985 | 3.3495 | 3.1005 | 2.9505 | 2.8454 | 3.6796 | 3.6469 | 3.5837 | 3.5541 | 3.5041 | 3.45 | 3.3796 | 3.3398 | 3.3082 | 3.1633 | 3.0469 | 2.801 | 3.401 | 3.3592 | 3.2653 | 3.2235 | 3.1571 | 3.0837 | 2.9888 | 2.9337 | 2.8888 | 2.6633 | 2.5276 | 2.4337
|  | BUSHEY PRIMARY | EE |  |  |  |  | 3.8903 | 3.8464 | 3.7423 | 3.7005 | 3.6321 | 3.5546 | 3.4556 | 3.3985 | 3.3495 | 3.1005 | 2.9628 | 2.8648 | 3.6796 | 3.6469 | 3.5837 | 3.5541 | 3.5041 | 3.45 | 3.3796 | 3.3398 | 3.3082 | 3.1633 | 3.0469 | 2.8796 | 3.401 | 3.3592 | 3.2653 | 3.2235 | 3.1571 | 3.0837 | 2.9888 | 2.9337 | 2.8888 | 2.6633 | 2.5408 | 2.452
|  | BUSHEY PRIMARY | HT |  |  |  |  | 3.9301 | 3.8862 | 3.8179 | 3.7781 | 3.7281 | 3.6597 | 3.6087 | 3.5332 | 3.4628 | 3.1362 | 2.9505 | 2.8454 | 3.7133 | 3.6816 | 3.6459 | 3.6204 | 3.5847 | 3.5429 | 3.5143 | 3.4643 | 3.4194 | 3.2286 | 3.1357 | 3.0939 | 3.4398 | 3.399 | 3.3388 | 3.3031 | 3.252 | 3.1888 | 3.1418 | 3.0673 | 3.0031 | 2.6949 | 2.5276 | 2.4337
|  | BUSHEY PRIMARY | HE |  |  |  |  | 3.9301 | 3.8872 | 3.8179 | 3.7832 | 3.7342 | 3.673 | 3.6281 | 3.5556 | 3.4944 | 3.1893 | 3.0577 | 3.0066 | 3.7112 | 3.6806 | 3.6439 | 3.6204 | 3.5857 | 3.5439 | 3.5163 | 3.4643 | 3.4224 | 3.2245 | 3.1041 | 2.9612 | 3.4408 | 3.4 | 3.3408 | 3.3071 | 3.2592 | 3.201 | 3.1582 | 3.0908 | 3.0327 | 2.748 | 2.6286 | 2.5837
|  | BUSHEY PRIMARY | CF |  |  |  |  | 3.9423 | 3.9168 | 3.8628 | 3.8281 | 3.7913 | 3.7668 | 3.724 | 3.676 | 3.6597 | 3.4046 | 3.2566 | 3.1117 | 3.7184 | 3.701 | 3.6704 | 3.6449 | 3.6173 | 3.6 | 3.5653 | 3.5276 | 3.5122 | 3.298 | 3.1082 | 2.801 | 3.4531 | 3.4286 | 3.3806 | 3.348 | 3.3122 | 3.2898 | 3.249 | 3.2041 | 3.1888 | 2.9408 | 2.8061 | 2.6755
FAWLEY GSP | LANGLEY BSP | BUTTS ASH PRIMARY | MINIMUM HEADROOM | SU 41923 05772 | NO | NO | 1.371 | 12.8331 | 12.5718 | 12.0473 | 11.4422 | 10.7953 | 9.6422 | 8.3637 | 7.08 | 6.1678 | 0.82898 | -3.321 | -5.6924 | 14.6382 | 14.4382 | 14.028 | 13.529 | 12.9933 | 12.2137 | 11.3249 | 10.4178 | 9.7933 | 6.229 | 1.7086 | -9.2016 | 11.5402 | 11.2892 | 10.7616 | 10.1841 | 9.5637 | 8.4973 | 7.2882 | 6.0657 | 5.2576 | 0.60959 | -2.8955 | -4.8771
|  | BUTTS ASH PRIMARY | EE |  |  |  |  | 12.8331 | 12.5718 | 12.0473 | 11.4422 | 10.7953 | 9.6422 | 8.3637 | 7.08 | 6.1678 | 1.3504 | -2.469 | -5.3771 | 14.6382 | 14.4382 | 14.028 | 13.529 | 12.9933 | 12.2137 | 11.3249 | 10.4178 | 9.7933 | 6.229 | 2.3545 | -3.4078 | 11.5402 | 11.2892 | 10.7616 | 10.1841 | 9.5637 | 8.4973 | 7.2882 | 6.0657 | 5.2576 | 0.97184 | -2.1629 | -4.619
|  | BUTTS ASH PRIMARY | HT |  |  |  |  | 13.1096 | 12.679 | 12.1943 | 11.9922 | 11.5035 | 10.4708 | 9.3698 | 8.231 | 7.0688 | 0.82898 | -3.321 | -5.6924 | 14.9484 | 14.7055 | 14.4269 | 14.3494 | 14.0698 | 13.5371 | 12.9392 | 12.3045 | 11.6484 | 8.4361 | 6.6167 | 5.6678 | 11.8882 | 11.4718 | 10.9943 | 10.8218 | 10.3422 | 9.4014 | 8.3841 | 7.3249 | 6.2382 | 0.60959 | -2.8955 | -4.8771
|  | BUTTS ASH PRIMARY | HE |  |  |  |  | 13.1882 | 12.7759 | 12.3239 | 12.1586 | 11.7076 | 10.8912 | 9.9902 | 9.0392 | 8.0514 | 2.7422 | -1.2322 | -3.0863 | 14.8902 | 14.5769 | 14.2402 | 14.0933 | 13.7341 | 13.18 | 12.53 | 11.831 | 11.0912 | 6.8494 | 2.7729 | -2.6088 | 11.9504 | 11.5433 | 11.0963 | 10.9535 | 10.5086 | 9.7463 | 8.8953 | 8.0024 | 7.081 | 2.2269 | -1.0924 | -2.622
|  | BUTTS ASH PRIMARY | CF |  |  |  |  | 13.5739 | 13.3667 | 13.0963 | 12.8249 | 12.8433 | 12.5647 | 12.2086 | 11.8096 | 11.3922 | 7.9535 | 4.128 | 0.5402 | 15.0596 | 14.8453 | 14.5698 | 14.278 | 14.1576 | 13.7922 | 13.3239 | 12.8096 | 12.2545 | 8.1024 | 1.7086 | -9.2016 | 12.2984 | 12.082 | 11.8045 | 11.5157 | 11.5443 | 11.2565 | 10.9055 | 10.5259 | 10.1198 | 6.8708 | 3.4494 | 0.30755
MELKSHAM GSP | CHIPPENHAM BSP | CALNE PRIMARY | MINIMUM HEADROOM | SU 00521 72497 | NO | YES | 4.034 | 6.0698 | 5.5045 | 5.2331 | 4.5341 | 3.6657 | 2.4484 | 1.1576 | -0.23224 | -1.4853 | -6.1812 | -10.0057 | -12.1843 | 6.9822 | 6.4598 | 6.3598 | 5.8098 | 5.171 | 4.3792 | 3.4802 | 2.5322 | 1.8465 | -1.0729 | -4.3443 | -12.8341 | 5.9 | 5.2673 | 5.049 | 4.3357 | 3.4888 | 2.348 | 1.098 | -0.22857 | -1.2898 | -5.1031 | -8.1612 | -9.9214
|  | CALNE PRIMARY | EE |  |  |  |  | 6.0698 | 5.5045 | 5.2331 | 4.5341 | 3.6657 | 2.4484 | 1.1576 | -0.23224 | -1.4853 | -6.1241 | -9.4129 | -11.8486 | 6.9822 | 6.4598 | 6.3598 | 5.8098 | 5.171 | 4.3792 | 3.4802 | 2.5322 | 1.8465 | -1.0729 | -4.1412 | -8.5606 | 5.9 | 5.2673 | 5.049 | 4.3357 | 3.4888 | 2.348 | 1.098 | -0.22857 | -1.2898 | -5.1031 | -7.6296 | -9.6643
|  | CALNE PRIMARY | HT |  |  |  |  | 6.3178 | 5.9014 | 5.4596 | 4.7229 | 4.1096 | 2.9198 | 1.8004 | 0.64224 | -0.54449 | -6.1812 | -10.0057 | -12.1843 | 7.4067 | 7.1241 | 6.7924 | 6.3159 | 6.169 | 5.5751 | 4.9629 | 4.3057 | 3.6251 | 0.67 | -1.0096 | -1.8994 | 6.2878 | 5.8663 | 5.402 | 4.6969 | 4.2541 | 3.2173 | 2.1918 | 1.1173 | 0.0081633 | -5.0571 | -8.1612 | -9.9214
|  | CALNE PRIMARY | HE |  |  |  |  | 6.3586 | 5.9453 | 5.4708 | 4.8361 | 4.3341 | 3.3586 | 2.3351 | 1.1841 | -0.081224 | -5.2169 | -8.7894 | -10.3547 | 7.3455 | 7.0231 | 6.6343 | 6.1547 | 5.9945 | 5.4057 | 4.7435 | 3.9986 | 3.1843 | -0.65857 | -4.0239 | -8.1218 | 6.3061 | 5.8959 | 5.4071 | 4.7816 | 4.4296 | 3.5531 | 2.602 | 1.5398 | 0.37551 | -4.2582 | -7.0786 | -8.3837
|  | CALNE PRIMARY | CF |  |  |  |  | 6.6943 | 6.4576 | 6.2004 | 5.8851 | 5.579 | 5.232 | 5.1127 | 4.6678 | 4.0167 | -0.12816 | -3.7782 | -7.1771 | 7.5149 | 7.2486 | 6.9955 | 6.668 | 6.2996 | 5.8782 | 5.8241 | 5.3394 | 4.7547 | 0.90673 | -4.3443 | -12.8341 | 6.6235 | 6.352 | 6.0898 | 5.75 | 5.4031 | 5.0163 | 4.9816 | 4.5163 | 3.8939 | 0.014286 | -3.1592 | -5.9133
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY PRIMARY | MINIMUM HEADROOM | SU 86584 59452 | NO | NO | 11.475 | 46.5128 | 45.9435 | 45.3965 | 44.67 | 43.8261 | 42.7904 | 41.5639 | 40.3781 | 39.373 | 34.3639 | 30.9986 | 29.2965 | 46.3741 | 45.9292 | 45.5322 | 44.9894 | 44.3557 | 43.6271 | 42.6802 | 41.7139 | 40.9608 | 36.8588 | 30.7853 | 17.5047 | 45.722 | 45.069 | 44.7894 | 44.1353 | 43.4016 | 42.3577 | 41.1628 | 39.9751 | 39.1159 | 35.0884 | 31.8741 | 30.2679
|  | CAMBERLEY PRIMARY | EE |  |  |  |  | 46.5128 | 45.9435 | 45.3965 | 44.67 | 43.8261 | 42.7904 | 41.5639 | 40.3781 | 39.373 | 35.0914 | 32.1435 | 29.5465 | 46.3741 | 45.9292 | 45.5322 | 44.9894 | 44.3557 | 43.6271 | 42.6802 | 41.7139 | 40.9608 | 36.8588 | 32.469 | 25.6312 | 45.722 | 45.069 | 44.7894 | 44.1353 | 43.4016 | 42.3577 | 41.1628 | 39.9751 | 39.1159 | 35.0884 | 32.4618 | 30.4628
|  | CAMBERLEY PRIMARY | HT |  |  |  |  | 46.9822 | 46.5955 | 46.1639 | 45.57 | 44.919 | 44.2302 | 43.269 | 42.2547 | 41.2067 | 35.4996 | 31.4588 | 29.2965 | 46.8016 | 46.4955 | 46.1649 | 45.7343 | 45.2649 | 44.8281 | 44.1741 | 43.4812 | 42.7598 | 39.4322 | 37.8537 | 37.0598 | 46.1496 | 45.6506 | 45.2006 | 44.622 | 43.9955 | 43.5108 | 42.5424 | 41.5292 | 40.4812 | 35.1853 | 31.8741 | 30.2679
|  | CAMBERLEY PRIMARY | HE |  |  |  |  | 46.8771 | 46.4373 | 45.9241 | 45.2914 | 44.521 | 43.7353 | 42.6312 | 41.4557 | 40.223 | 34.3639 | 30.9986 | 29.6649 | 46.6924 | 46.3363 | 45.9424 | 45.472 | 44.8935 | 44.3516 | 43.5567 | 42.7016 | 41.8047 | 37.3312 | 32.5547 | 26.1118 | 46.1384 | 45.6496 | 45.2057 | 44.6598 | 44.0332 | 43.6465 | 42.7608 | 41.8353 | 40.6577 | 35.0884 | 32.3037 | 31.0873
|  | CAMBERLEY PRIMARY | CF |  |  |  |  | 47.2904 | 47.0404 | 46.7935 | 46.4904 | 46.1475 | 45.723 | 45.2904 | 44.671 | 44.0067 | 39.7281 | 35.5965 | 32.371 | 46.9384 | 46.6445 | 46.3506 | 45.9863 | 45.5475 | 45.0292 | 44.7026 | 44.0975 | 43.4312 | 38.5792 | 30.7853 | 17.5047 | 46.4935 | 46.1873 | 45.9302 | 45.6067 | 45.2475 | 44.8526 | 44.8118 | 44.3628 | 43.8884 | 40.1384 | 36.2322 | 33.3567
WILLESDEN GSP |  | CANAL BANK 11KV PRIMARY | MINIMUM HEADROOM | TQ 20927 83082 | NO | YES | 22.81 | 17.9661 | 16.712 | 15.3039 | 13.2325 | 10.6753 | 7.1845 | 3.2529 | -0.71959 | -5.6604 | -22.1451 | -27.188 | -31.4645 | 14.661 | 13.9018 | 13.0202 | 11.3988 | 9.4192 | 5.5723 | 0.96205 | -3.3665 | -9.0665 | -30.1339 | -35.8298 | -40.2747 | 12.8345 | 11.7733 | 10.5488 | 8.51 | 5.9988 | 2.0814 | -2.4686 | -6.8441 | -12.4675 | -31.989 | -37.738 | -42.4665
|  | CANAL BANK 11KV PRIMARY | EE |  |  |  |  | 18.1365 | 17.1314 | 15.9049 | 14.4243 | 12.1927 | 9.0427 | 5.3753 | 1.7049 | -2.241 | -20.139 | -23.2584 | -27.4349 | 14.7212 | 14.0723 | 13.2865 | 12.3723 | 10.7263 | 7.2835 | 3.1774 | -0.46346 | -4.5757 | -27.6441 | -31.0349 | -35.3175 | 12.96 | 12.0702 | 10.9855 | 9.6896 | 7.5539 | 3.9967 | -0.18285 | -4.042 | -8.3094 | -29.4951 | -32.891 | -37.4808
|  | CANAL BANK 11KV PRIMARY | HT |  |  |  |  | 17.9661 | 16.712 | 15.3039 | 13.2325 | 10.6753 | 7.1845 | 3.2529 | -0.71959 | -5.6604 | -22.1451 | -27.188 | -31.4645 | 14.661 | 13.9018 | 13.0202 | 11.3988 | 9.4192 | 5.5723 | 0.96205 | -3.3665 | -9.0665 | -30.1339 | -35.8298 | -40.2747 | 12.8345 | 11.7733 | 10.5488 | 8.51 | 5.9988 | 2.0814 | -2.4686 | -6.8441 | -12.4675 | -31.989 | -37.738 | -42.4665
|  | CANAL BANK 11KV PRIMARY | HE |  |  |  |  | 18.161 | 17.1661 | 15.9416 | 14.4753 | 12.2651 | 9.7212 | 6.6039 | 3.8314 | 0.9345 | -16.2482 | -19.4543 | -23.5716 | 14.7416 | 14.0978 | 13.3274 | 12.4263 | 10.808 | 8.0978 | 4.6733 | 2.1467 | -0.69816 | -22.9931 | -26.5155 | -30.841 | 12.9835 | 12.1018 | 11.0212 | 9.7396 | 7.6253 | 4.8008 | 1.3131 | -1.4175 | -4.389 | -24.7461 | -28.2553 | -32.8257
|  | CANAL BANK 11KV PRIMARY | CF |  |  |  |  | 18.7049 | 18.2743 | 17.7539 | 17.1723 | 16.4284 | 14.8039 | 12.4253 | 10.1182 | 7.7682 | -6.4931 | -15.8941 | -15.8247 | 14.9998 | 14.5437 | 14.0743 | 13.5814 | 13.0263 | 11.2018 | 8.5498 | 6.2325 | 3.9845 | -8.0737 | -20.8257 | -21.0237 | 13.4396 | 12.9753 | 12.4855 | 11.9294 | 11.1559 | 9.2906 | 6.5518 | 4.0171 | 1.5906 | -11.9349 | -23.3288 | -23.0808
COWLEY GSP | WITNEY BSP | CARTERTON PRIMARY | MINIMUM HEADROOM | SP 28261 07823 | NO | NO | 2.163 | 12.402 | 11.5673 | 11.1459 | 10.4561 | 9.7776 | 9.1592 | 8.4694 | 7.7439 | 7.2378 | 4.148 | 1.4163 | -0.29592 | 17.8469 | 17.3439 | 17.1316 | 16.701 | 16.2622 | 15.8214 | 15.3194 | 14.799 | 14.4255 | 12.1571 | 8.9082 | 1.3969 | 13.851 | 13.1041 | 12.7541 | 12.1092 | 11.4653 | 10.848 | 10.1459 | 9.4449 | 8.9796 | 6.3255 | 4.0092 | 2.6367
|  | CARTERTON PRIMARY | EE |  |  |  |  | 12.402 | 11.5673 | 11.1459 | 10.4561 | 9.7776 | 9.1592 | 8.4694 | 7.7439 | 7.2378 | 4.4592 | 2.0031 | 0.005102 | 17.8469 | 17.3439 | 17.1316 | 16.701 | 16.2622 | 15.8214 | 15.3194 | 14.799 | 14.4255 | 12.1571 | 9.4173 | 5.3071 | 13.851 | 13.1041 | 12.7541 | 12.1092 | 11.4653 | 10.848 | 10.1459 | 9.4449 | 8.9796 | 6.5418 | 4.5316 | 2.8898
|  | CARTERTON PRIMARY | HT |  |  |  |  | 12.5918 | 11.8245 | 11.2194 | 10.5469 | 9.8827 | 9.5929 | 8.9878 | 8.3602 | 7.7102 | 4.148 | 1.4163 | -0.29592 | 18.0918 | 17.6959 | 17.3959 | 17.0449 | 16.6918 | 16.6184 | 16.2837 | 15.9357 | 15.5714 | 13.7204 | 12.4643 | 11.7092 | 14.0918 | 13.4316 | 12.9 | 12.2898 | 11.6776 | 11.4439 | 10.8643 | 10.2592 | 9.6286 | 6.3255 | 4.0092 | 2.6367
|  | CARTERTON PRIMARY | HE |  |  |  |  | 12.6316 | 11.8929 | 11.3224 | 10.6837 | 10.0571 | 9.9204 | 9.4633 | 8.9878 | 8.4949 | 5.6327 | 3.1684 | 1.8561 | 18.0327 | 17.6051 | 17.2714 | 16.8827 | 16.4847 | 16.399 | 16.0459 | 15.6643 | 15.2602 | 12.7602 | 9.9643 | 6.1449 | 14.1224 | 13.4888 | 12.9857 | 12.4092 | 11.8347 | 11.7316 | 11.2796 | 10.8051 | 10.3102 | 7.6398 | 5.598 | 4.549
|  | CARTERTON PRIMARY | CF |  |  |  |  | 12.9031 | 12.3612 | 11.9245 | 11.4949 | 11.0612 | 10.8571 | 10.9347 | 10.7398 | 10.5388 | 8.5939 | 6.3276 | 4.0388 | 18.1347 | 17.798 | 17.4939 | 17.198 | 16.8541 | 16.5663 | 16.4878 | 16.1796 | 15.85 | 13.2347 | 8.9082 | 1.3969 | 14.3592 | 13.9112 | 13.5235 | 13.1449 | 12.75 | 12.5337 | 12.6102 | 12.3929 | 12.1673 | 10.2388 | 8.198 | 6.2827
AXMINSTER GSP | YEOVIL BSP | CASTLE CARY PRIMARY | MINIMUM HEADROOM | ST 64534 31039 | NO | NO | 2.488 | 7.772 | 7.5648 | 7.2934 | 6.9842 | 6.7169 | 6.3944 | 6.0312 | 5.6638 | 5.8597 | 4.7485 | 3.971 | 3.4873 | 8.8914 | 8.7495 | 8.5587 | 8.3424 | 8.1577 | 7.923 | 7.6516 | 7.375 | 7.625 | 6.8546 | 5.9322 | 3.6638 | 7.9118 | 7.7199 | 7.4699 | 7.1761 | 6.925 | 6.6159 | 6.2659 | 5.9128 | 6.2036 | 5.324 | 4.6924 | 4.2995
|  | CASTLE CARY PRIMARY | EE |  |  |  |  | 7.772 | 7.5648 | 7.2934 | 6.9842 | 6.7169 | 6.3944 | 6.0312 | 5.6638 | 5.8597 | 4.7485 | 4.0699 | 3.5863 | 8.8914 | 8.7495 | 8.5587 | 8.3424 | 8.1577 | 7.923 | 7.6516 | 7.375 | 7.625 | 6.8546 | 6.0567 | 4.8863 | 7.9118 | 7.7199 | 7.4699 | 7.1761 | 6.925 | 6.6159 | 6.2659 | 5.9128 | 6.2057 | 5.324 | 4.7914 | 4.3873
|  | CASTLE CARY PRIMARY | HT |  |  |  |  | 7.8842 | 7.7026 | 7.473 | 7.2536 | 6.973 | 6.7087 | 6.4699 | 6.1842 | 5.8914 | 4.7842 | 3.971 | 3.4873 | 9.0077 | 8.9077 | 8.7699 | 8.6526 | 8.4893 | 8.3281 | 8.1873 | 8.0006 | 7.8016 | 7.3373 | 6.9587 | 6.7669 | 8.023 | 7.8669 | 7.6659 | 7.4761 | 7.2301 | 6.9791 | 6.7669 | 6.4904 | 6.2036 | 5.3546 | 4.6924 | 4.2995
|  | CASTLE CARY PRIMARY | HE |  |  |  |  | 7.8842 | 7.7067 | 7.4873 | 7.2679 | 6.9975 | 6.7648 | 6.5516 | 6.2934 | 6.0301 | 5.0332 | 4.3567 | 4.0699 | 8.9873 | 8.8781 | 8.7373 | 8.6036 | 8.4342 | 8.2679 | 8.1199 | 7.923 | 7.7128 | 7.0087 | 6.1904 | 5.1067 | 8.024 | 7.872 | 7.6771 | 7.4924 | 7.2567 | 7.0332 | 6.8444 | 6.5934 | 6.3342 | 5.5883 | 5.072 | 4.8271
|  | CASTLE CARY PRIMARY | CF |  |  |  |  | 7.971 | 7.8312 | 7.6659 | 7.473 | 7.2985 | 7.1771 | 7.0455 | 6.8995 | 6.7965 | 5.8067 | 5.3577 | 4.6373 | 9.0342 | 8.9404 | 8.8261 | 8.6955 | 8.575 | 8.4587 | 8.3169 | 8.1628 | 8.0465 | 6.9985 | 5.9322 | 3.6638 | 8.1016 | 7.9822 | 7.8363 | 7.6679 | 7.521 | 7.4016 | 7.2618 | 7.1108 | 7.0169 | 6.0546 | 5.825 | 5.2679
LALEHAM GSP | STAINES BSP | CAUSEWAY PRIMARY | MINIMUM HEADROOM | TQ 02763 71680 | NO | NO | 6.541 | 32.2124 | 31.8002 | 31.2879 | 30.8369 | 30.2308 | 29.3583 | 28.3359 | 27.2512 | 26.1042 | 22.9971 | 20.1971 | 18.6247 | 35.2267 | 35.0012 | 34.7185 | 34.5359 | 34.0593 | 33.342 | 32.544 | 31.643 | 30.7369 | 27.7012 | 23.2236 | 13.4614 | 32.9267 | 32.5379 | 32.0583 | 31.6491 | 31.0838 | 30.3614 | 29.5318 | 28.6185 | 27.4318 | 24.2257 | 21.7563 | 20.3991
|  | CAUSEWAY PRIMARY | EE |  |  |  |  | 32.2124 | 31.8002 | 31.2879 | 30.8369 | 30.2308 | 29.3583 | 28.3359 | 27.2512 | 26.1042 | 23.0073 | 20.7063 | 18.8716 | 35.2267 | 35.0012 | 34.7185 | 34.5359 | 34.0593 | 33.342 | 32.544 | 31.643 | 30.7369 | 27.7012 | 24.4002 | 19.3053 | 32.9267 | 32.5379 | 32.0583 | 31.6491 | 31.0838 | 30.3614 | 29.5318 | 28.6185 | 27.4318 | 24.3063 | 22.1818 | 20.591
|  | CAUSEWAY PRIMARY | HT |  |  |  |  | 32.4644 | 32.1328 | 31.7175 | 31.2624 | 30.7226 | 29.8849 | 29.0644 | 27.9359 | 26.7512 | 22.9971 | 20.1971 | 18.6247 | 35.3971 | 35.242 | 35.043 | 34.8379 | 34.5573 | 34.0553 | 33.6328 | 32.8144 | 32.0175 | 29.9491 | 28.6471 | 27.9655 | 33.1685 | 32.8614 | 32.4747 | 32.0461 | 31.5461 | 30.8379 | 30.0951 | 28.94 | 27.7114 | 24.2257 | 21.7563 | 20.3991
|  | CAUSEWAY PRIMARY | HE |  |  |  |  | 32.442 | 32.1012 | 31.6696 | 31.1951 | 30.6451 | 29.8675 | 29.0869 | 28.0685 | 26.8379 | 23.041 | 21.0042 | 20.0185 | 35.3491 | 35.1685 | 34.9389 | 34.6971 | 34.3298 | 33.6889 | 33.2502 | 32.4706 | 31.5369 | 28.2726 | 24.9144 | 20.094 | 33.1491 | 32.8338 | 32.4349 | 31.992 | 31.4787 | 30.8236 | 30.1971 | 29.3522 | 28.3359 | 25.093 | 23.0696 | 22.0716
|  | CAUSEWAY PRIMARY | CF |  |  |  |  | 32.7073 | 32.5491 | 32.3349 | 32.0614 | 31.6032 | 31.1491 | 30.6491 | 30.2022 | 29.4634 | 26.6389 | 23.9389 | 21.7073 | 35.4379 | 35.3287 | 35.1808 | 35.0032 | 34.6481 | 34.1481 | 33.5389 | 33.1124 | 32.292 | 28.7624 | 23.2236 | 13.4614 | 33.394 | 33.2461 | 33.0481 | 32.79 | 32.3634 | 31.943 | 31.4757 | 31.0614 | 30.3818 | 27.9614 | 25.8685 | 23.8532
FLEET-BRAMLEY GSP | READING TOWN BSP | CAVERSHAM PRIMARY | MINIMUM HEADROOM | SU 71512 75747 | NO | NO | 0.7 | 14.9071 | 14.301 | 14.2561 | 13.6959 | 13.0908 | 12.1061 | 10.9888 | 9.8694 | 9.1612 | 5.4755 | 2.5439 | 1.5153 | 18.1194 | 17.6398 | 17.5163 | 17.0408 | 16.5235 | 15.8082 | 14.9837 | 14.1429 | 13.5724 | 10.2735 | 5.2367 | -6.098 | 15.6143 | 15.0316 | 14.9867 | 14.4571 | 13.8663 | 12.9408 | 11.8806 | 10.8204 | 10.1643 | 6.7092 | 4.1653 | 3.3245
|  | CAVERSHAM PRIMARY | EE |  |  |  |  | 14.9071 | 14.301 | 14.2561 | 13.6959 | 13.0908 | 12.1061 | 10.9888 | 9.8694 | 9.1612 | 5.6112 | 3.0857 | 2.1459 | 18.1194 | 17.6398 | 17.5163 | 17.0408 | 16.5235 | 15.8082 | 14.9837 | 14.1429 | 13.5724 | 10.2735 | 6.702 | 1.3143 | 15.6143 | 15.0316 | 14.9867 | 14.4571 | 13.8663 | 12.9408 | 11.8806 | 10.8204 | 10.1643 | 6.8031 | 4.6724 | 3.8592
|  | CAVERSHAM PRIMARY | HT |  |  |  |  | 15.3092 | 14.9194 | 14.452 | 13.9378 | 13.9337 | 13.1235 | 12.2316 | 11.302 | 10.3276 | 5.4755 | 2.5439 | 1.5153 | 18.5378 | 18.2878 | 17.9806 | 17.6398 | 17.6245 | 17.1612 | 16.6337 | 16.0745 | 15.4929 | 12.6898 | 11.3194 | 10.8327 | 15.9857 | 15.6367 | 15.2041 | 14.7092 | 14.6806 | 13.9082 | 13.0571 | 12.1714 | 11.2551 | 6.7092 | 4.1653 | 3.3245
|  | CAVERSHAM PRIMARY | HE |  |  |  |  | 15.35 | 14.9949 | 14.5663 | 14.0959 | 14.1459 | 13.4704 | 12.7041 | 11.9051 | 11.0806 | 7.1092 | 4.7092 | 3.7378 | 18.4337 | 18.1286 | 17.7663 | 17.3673 | 17.2918 | 16.7796 | 16.1908 | 15.5571 | 14.8867 | 11.0561 | 7.4418 | 2.0806 | 16.0204 | 15.702 | 15.3051 | 14.852 | 14.8837 | 14.2398 | 13.5143 | 12.7551 | 11.9704 | 8.1806 | 6.1173 | 5.3286
|  | CAVERSHAM PRIMARY | CF |  |  |  |  | 15.6347 | 15.4173 | 15.148 | 14.8531 | 14.5265 | 14.6908 | 14.3408 | 13.9541 | 13.552 | 10.5837 | 7.7827 | 5.0939 | 18.5663 | 18.3184 | 18.0214 | 17.6918 | 17.3061 | 17.2 | 16.7286 | 16.2163 | 15.6684 | 11.5316 | 5.2367 | -6.098 | 16.2816 | 16.0888 | 15.8439 | 15.5561 | 15.2347 | 15.3969 | 15.0653 | 14.6929 | 14.3 | 11.4184 | 8.8041 | 6.3663
MANNINGTON GSP | BOURNEMOUTH BSP | CENTRAL PRIMARY | MINIMUM HEADROOM | SZ 10293 91931 | NO | YES | 1.592 | 4.6082 | 3.6245 | 2.6061 | 1.4408 | 0.73163 | -0.92347 | -2.8439 | -4.7418 | -6.3316 | -12.0388 | -15.6837 | -15.8367 | 10.7847 | 9.9398 | 9.0214 | 7.95 | 7.148 | 5.8031 | 4.2214 | 2.6224 | 1.2643 | -5.1337 | -13.9816 | -36.4796 | 4.7908 | 3.8357 | 2.8276 | 1.6745 | 0.87347 | -0.7051 | -2.552 | -4.3765 | -5.8582 | -11.0388 | -14.1133 | -14.2163
|  | CENTRAL PRIMARY | EE |  |  |  |  | 4.6082 | 3.6245 | 2.6061 | 1.4408 | 0.73163 | -0.92347 | -2.8439 | -4.7418 | -6.3316 | -12.0388 | -14.4684 | -14.2327 | 10.7847 | 9.9398 | 9.0214 | 7.95 | 7.148 | 5.8031 | 4.2214 | 2.6224 | 1.2643 | -5.1337 | -11.4051 | -21.4918 | 4.7908 | 3.8357 | 2.8276 | 1.6745 | 0.87347 | -0.7051 | -2.552 | -4.3765 | -5.8582 | -11.0388 | -13.0643 | -12.9888
|  | CENTRAL PRIMARY | HT |  |  |  |  | 5.35 | 4.6357 | 3.9541 | 3.2357 | 2.3561 | 1.0878 | -0.080612 | -1.6235 | -3.2388 | -11.1163 | -15.6837 | -15.8367 | 11.5694 | 11.0653 | 10.5541 | 10.0071 | 9.3316 | 8.4878 | 7.799 | 6.7714 | 5.6867 | 0.54286 | -2.3531 | -2.6663 | 5.5194 | 4.8357 | 4.1633 | 3.448 | 2.5765 | 1.3633 | 0.33163 | -1.1133 | -2.6316 | -9.9551 | -14.1133 | -14.2163
|  | CENTRAL PRIMARY | HE |  |  |  |  | 5.3592 | 4.7092 | 4.1071 | 3.4786 | 2.698 | 1.5724 | 0.26633 | -0.71429 | -2.098 | -7.7041 | -10.1194 | -10.2704 | 11.3561 | 10.7633 | 10.1633 | 9.502 | 8.7184 | 7.7622 | 6.6367 | 5.7908 | 4.55 | -2.1571 | -8.7122 | -18.7102 | 5.5122 | 4.8796 | 4.2714 | 3.6347 | 2.8653 | 1.8133 | 0.56939 | -0.27449 | -1.5704 | -6.7969 | -8.9051 | -8.9898
|  | CENTRAL PRIMARY | CF |  |  |  |  | 5.7857 | 5.2888 | 4.948 | 4.5204 | 4.0755 | 3.5612 | 2.9031 | 2.201 | 1.4602 | -2.149 | -6.8235 | -11.0571 | 11.6143 | 11.099 | 10.6418 | 10.0653 | 9.3939 | 8.599 | 7.6378 | 6.6092 | 5.502 | -1.5571 | -13.9816 | -36.4796 | 5.9735 | 5.5112 | 5.1776 | 4.7582 | 4.3173 | 3.8306 | 3.1949 | 2.5122 | 1.7898 | -1.849 | -6.101 | -9.7878
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CENTRAL BRIDGE PRIMARY | MINIMUM HEADROOM | SU 42591 11255 | NO | YES | 2.61 | 20.0007 | 19.569 | 18.6874 | 18.0292 | 15.3415 | 13.1058 | 11.1313 | 10.0537 | 7.9088 | 0.57718 | -7.3555 | -14.5116 | 22.9119 | 22.5088 | 21.5088 | 20.9037 | 18.2547 | 16.8496 | 15.0262 | 14.1751 | 10.5751 | 2.1098 | -8.2555 | -22.8289 | 20.1058 | 19.7149 | 18.666 | 17.9915 | 15.2904 | 13.1598 | 11.1364 | 10.1323 | 7.018 | -0.93506 | -9.9085 | -19.1881
|  | CENTRAL BRIDGE PRIMARY | EE |  |  |  |  | 20.0007 | 19.569 | 19.0578 | 18.4915 | 17.2007 | 16.0251 | 14.268 | 11.7904 | 10.167 | 5.0027 | -4.4473 | -8.2953 | 22.9119 | 22.6027 | 22.2333 | 21.8047 | 20.5272 | 19.3282 | 18.166 | 16.0711 | 14.7078 | 8.4792 | -5.1902 | -14.0534 | 20.1058 | 19.7149 | 19.2486 | 18.7292 | 17.3598 | 16.1017 | 14.5558 | 12.1017 | 10.5445 | 4.9894 | -6.4902 | -10.9953
|  | CENTRAL BRIDGE PRIMARY | HT |  |  |  |  | 20.2068 | 19.6966 | 18.9721 | 18.2966 | 15.3415 | 13.1058 | 11.1313 | 10.0537 | 8.1047 | 2.1711 | -7.3555 | -13.7769 | 23.1578 | 22.7823 | 22.1711 | 21.668 | 19.0568 | 17.3027 | 15.6078 | 14.87 | 13.0823 | 7.2394 | -3.682 | -11.3371 | 20.316 | 19.8149 | 19.0609 | 18.418 | 15.3476 | 13.1598 | 11.1364 | 10.1323 | 8.0609 | 1.4802 | -9.9085 | -17.7085
|  | CENTRAL BRIDGE PRIMARY | HE |  |  |  |  | 20.2058 | 19.6404 | 18.6874 | 18.0292 | 15.716 | 14.4425 | 12.466 | 11.2496 | 7.9088 | 0.57718 | -6.3932 | -14.5116 | 23.0445 | 22.5088 | 21.5088 | 20.9037 | 18.2547 | 16.8496 | 15.0262 | 14.1751 | 10.5751 | 2.1098 | -8.2555 | -22.8289 | 20.3068 | 19.7211 | 18.666 | 17.9915 | 15.2904 | 13.868 | 11.8302 | 10.7711 | 7.018 | -0.93506 | -9.1861 | -19.1881
|  | CENTRAL BRIDGE PRIMARY | CF |  |  |  |  | 20.769 | 20.5415 | 20.2915 | 19.8292 | 19.2374 | 18.516 | 17.8058 | 16.5088 | 15.0088 | 9.6741 | 4.6874 | 0.318 | 23.3221 | 23.1017 | 22.8578 | 22.3598 | 21.7272 | 20.8711 | 20.0384 | 18.8782 | 17.5343 | 10.8231 | 1.2507 | -12.6218 | 20.7588 | 20.5649 | 20.3466 | 19.869 | 19.266 | 18.5078 | 17.7884 | 16.5751 | 15.166 | 9.6996 | 4.1507 | -0.85853
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS PRIMARY | MINIMUM HEADROOM | ST 66140 01039 | YES | NO | 0.021 | 2.3918 | 2.3459 | 2.3112 | 2.2582 | 2.2327 | 2.1704 | 2.1051 | 2.0316 | 2.0102 | 1.8959 | 1.85 | 1.8133 | 3.1418 | 3.1092 | 3.0847 | 3.0449 | 3.0235 | 2.9816 | 2.9327 | 2.8816 | 2.851 | 2.7224 | 2.5184 | 2.102 | 2.65 | 2.6133 | 2.5837 | 2.5347 | 2.5092 | 2.45 | 2.3888 | 2.3184 | 2.2969 | 2.1816 | 2.1347 | 2.1031
|  | CERNE ABBAS PRIMARY | EE |  |  |  |  | 2.3918 | 2.3459 | 2.3112 | 2.2582 | 2.2327 | 2.1704 | 2.1051 | 2.0316 | 2.0102 | 1.8959 | 1.8561 | 1.8337 | 3.1418 | 3.1092 | 3.0847 | 3.0449 | 3.0235 | 2.9816 | 2.9327 | 2.8816 | 2.851 | 2.7224 | 2.599 | 2.3939 | 2.65 | 2.6133 | 2.5837 | 2.5347 | 2.5092 | 2.45 | 2.3888 | 2.3184 | 2.2969 | 2.1816 | 2.1439 | 2.1235
|  | CERNE ABBAS PRIMARY | HT |  |  |  |  | 2.4163 | 2.3939 | 2.3755 | 2.3378 | 2.3143 | 2.2684 | 2.2173 | 2.1898 | 2.1378 | 1.9255 | 1.85 | 1.8133 | 3.1622 | 3.1469 | 3.1347 | 3.1061 | 3.0898 | 3.0592 | 3.0224 | 3.0071 | 2.9704 | 2.8306 | 2.7837 | 2.7633 | 2.6643 | 2.6469 | 2.6265 | 2.5939 | 2.5714 | 2.5296 | 2.4827 | 2.4571 | 2.4061 | 2.2041 | 2.1347 | 2.1031
|  | CERNE ABBAS PRIMARY | HE |  |  |  |  | 2.4214 | 2.3918 | 2.3735 | 2.3378 | 2.3133 | 2.2684 | 2.2429 | 2.1918 | 2.1357 | 1.9327 | 1.8878 | 1.8755 | 3.1612 | 3.1378 | 3.1224 | 3.0959 | 3.0765 | 3.0439 | 3.0194 | 2.9837 | 2.9398 | 2.751 | 2.6235 | 2.4245 | 2.6663 | 2.6459 | 2.6276 | 2.5959 | 2.5735 | 2.5357 | 2.5082 | 2.4663 | 2.4173 | 2.2143 | 2.1765 | 2.1673
|  | CERNE ABBAS PRIMARY | CF |  |  |  |  | 2.4276 | 2.4112 | 2.3857 | 2.3745 | 2.349 | 2.3306 | 2.2959 | 2.2571 | 2.2449 | 2.048 | 1.9561 | 1.8847 | 3.1653 | 3.151 | 3.1265 | 3.1133 | 3.0898 | 3.0714 | 3.0398 | 3.0031 | 2.9857 | 2.7776 | 2.5184 | 2.102 | 2.6714 | 2.6592 | 2.6367 | 2.6235 | 2.599 | 2.5857 | 2.5531 | 2.5153 | 2.502 | 2.3235 | 2.2245 | 2.1694
LOVEDEAN GSP |  | CHALCRAFT LANE PRIMARY | MINIMUM HEADROOM | TBC | NO | YES | 0 |  |  |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | EE | [7 empty] | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | HT | [7 empty] | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | HE | [7 empty] | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | CF | [7 empty] | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
IVER 132KV GSP | CHALVEY BSP | CHALVEY PRIMARY | MINIMUM HEADROOM | SU 96669 79364 | NO | YES | 10.937 | 31.2913 | 29.3352 | 27.3801 | 25.1821 | 22.6229 | 19.4209 | 16.1689 | 13.1291 | 10.6331 | 1.1587 | -6.0893 | -8.2373 | 39.2189 | 37.9199 | 36.5801 | 35.0433 | 33.2903 | 30.827 | 28.1505 | 25.6576 | 23.5311 | 14.3423 | 5.9566 | -17.8893 | 31.6923 | 29.9627 | 28.1862 | 26.1852 | 23.8648 | 20.7842 | 17.5515 | 14.5627 | 12.1566 | 3.4372 | -3.423 | -5.5577
|  | CHALVEY PRIMARY | EE |  |  |  |  | 31.2913 | 29.3352 | 27.3801 | 25.1821 | 22.6229 | 19.4209 | 16.1689 | 13.1291 | 10.6331 | 1.1587 | -3.926 | -5.5148 | 39.2189 | 37.9199 | 36.5801 | 35.0433 | 33.2903 | 30.827 | 28.1505 | 25.6576 | 23.5311 | 14.3423 | 5.9566 | -6.1169 | 31.6923 | 29.9627 | 28.1862 | 26.1852 | 23.8648 | 20.7842 | 17.5515 | 14.5627 | 12.1566 | 3.4372 | -1.1567 | -2.8475
|  | CHALVEY PRIMARY | HT |  |  |  |  | 31.878 | 30.1025 | 28.7219 | 26.875 | 24.7015 | 21.9699 | 19.2678 | 16.6525 | 13.9025 | 1.2811 | -6.0893 | -8.2373 | 39.9301 | 38.9189 | 38.2015 | 37.1484 | 35.9199 | 34.0719 | 32.0984 | 30.2444 | 28.2484 | 19.5984 | 14.7015 | 12.8423 | 32.2974 | 30.7536 | 29.6199 | 28.0015 | 26.0944 | 23.5056 | 20.8576 | 18.3219 | 15.625 | 3.5423 | -3.423 | -5.5577
|  | CHALVEY PRIMARY | HE |  |  |  |  | 31.9148 | 30.2015 | 28.8893 | 27.1393 | 25.0536 | 22.676 | 20.328 | 18.1893 | 15.9556 | 6.1189 | 0.90967 | -1.1097 | 39.7056 | 38.5933 | 37.7658 | 36.5831 | 35.2025 | 33.4097 | 31.4587 | 29.7301 | 27.8648 | 17.9709 | 9.2178 | -2.823 | 32.324 | 30.8352 | 29.7648 | 28.2331 | 26.4148 | 24.2056 | 21.928 | 19.9087 | 17.7791 | 8.4301 | 3.6148 | 1.5984
|  | CHALVEY PRIMARY | CF |  |  |  |  | 33.9668 | 33.1301 | 32.2015 | 31.4036 | 29.8933 | 27.9923 | 25.4699 | 24.175 | 22.8423 | 15.9107 | 8.6291 | 2.2393 | 40.7168 | 40.0066 | 39.2138 | 38.5321 | 37.328 | 35.6821 | 33.5719 | 32.0097 | 30.4087 | 20.8984 | 6.4403 | -17.8893 | 33.978 | 33.2403 | 32.4066 | 31.7862 | 30.4995 | 28.8178 | 26.5515 | 25.2536 | 23.9382 | 17.2699 | 10.7576 | 5.2158
NURSLING GSP | VELMORE BSP | CHANDLERS FORD PRIMARY | MINIMUM HEADROOM | SU 43494 21552 | NO | YES | 4.641 | 10.4551 | 9.7939 | 8.699 | 7.5735 | 6.1898 | 4.2755 | 2.0133 | -0.10918 | -1.8602 | -12.2776 | -17.3724 | -18.2745 | 13.0582 | 12.5469 | 11.7224 | 10.8357 | 9.8571 | 8.6112 | 6.9806 | 5.4367 | 4.1847 | -3.4796 | -7.0867 | -18.7398 | 10.0878 | 9.5163 | 8.5 | 7.4306 | 6.2551 | 4.4867 | 2.3296 | 0.29796 | -1.3663 | -11.3204 | -16.1276 | -16.9347
|  | CHANDLERS FORD PRIMARY | EE |  |  |  |  | 10.4551 | 9.7939 | 8.699 | 7.5735 | 6.1898 | 4.2755 | 2.0133 | -0.10918 | -1.8602 | -7.6071 | -10.6194 | -13.3827 | 13.0582 | 12.5469 | 11.7224 | 10.8357 | 9.8571 | 8.6112 | 6.9806 | 5.4367 | 4.1847 | -0.12143 | -4.4214 | -10.7694 | 10.0878 | 9.5163 | 8.5 | 7.4306 | 6.2551 | 4.4867 | 2.3296 | 0.29796 | -1.3663 | -6.7602 | -9.048 | -11.4296
|  | CHANDLERS FORD PRIMARY | HT |  |  |  |  | 11.2827 | 10.5908 | 9.7163 | 9.1918 | 8.2714 | 6.7908 | 5.1459 | 3.5204 | 1.8071 | -6.0949 | -10.7265 | -12.9827 | 13.8531 | 13.4071 | 12.8439 | 12.5418 | 11.9357 | 11.0939 | 10.1153 | 9.1276 | 8.0878 | 3.0531 | 0.73163 | 0.15408 | 10.9204 | 10.2806 | 9.4714 | 9.05 | 8.202 | 6.8878 | 5.4102 | 3.9245 | 2.351 | -4.8786 | -9.0439 | -10.9633
|  | CHANDLERS FORD PRIMARY | HE |  |  |  |  | 11.0684 | 10.2827 | 9.2939 | 8.6276 | 7.4071 | 5.598 | 3.3908 | 1.0786 | -1.3561 | -12.2776 | -17.3724 | -18.2745 | 13.5378 | 12.9276 | 12.1816 | 11.6592 | 10.801 | 9.6296 | 8.0143 | 6.3071 | 4.5112 | -3.4796 | -7.0867 | -12.5929 | 10.7143 | 9.9857 | 9.0714 | 8.5153 | 7.4888 | 5.7643 | 3.6571 | 1.4449 | -0.8898 | -11.3204 | -16.1276 | -16.9347
|  | CHANDLERS FORD PRIMARY | CF |  |  |  |  | 11.7367 | 11.2755 | 10.6643 | 10.0602 | 9.7235 | 9.0122 | 8.1684 | 7.3265 | 6.1724 | -1.5898 | -8.2153 | -11.8704 | 13.9357 | 13.5082 | 12.9765 | 12.4173 | 12.0367 | 11.3357 | 10.4939 | 9.6153 | 8.6735 | 2.3378 | -6.0847 | -18.7398 | 11.3194 | 10.8878 | 10.3173 | 9.7388 | 9.4908 | 8.8388 | 8.0531 | 7.2541 | 6.3 | -1.1388 | -7.4347 | -10.8469
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CHAPEL PRIMARY | MINIMUM HEADROOM | SU 42849 11983 | NO | YES | 2.998 | 9.7959 | 9.6255 | 9.4163 | 9.1847 | 8.749 | 8.101 | 7.5796 | 6.8306 | 6.4092 | 3.9 | 2.5194 | 2.1806 | 11.9947 | 11.7855 | 11.5304 | 11.2284 | 10.8304 | 10.4151 | 9.7671 | 9.1814 | 8.7518 | 6.6692 | 2.8569 | -6.5533 | 10.3024 | 10.1412 | 9.9178 | 9.6249 | 9.2545 | 8.779 | 7.9688 | 7.2137 | 6.781 | 4.2147 | 2.9024 | 2.5871
|  | CHAPEL PRIMARY | EE |  |  |  |  | 9.7959 | 9.6255 | 9.4163 | 9.1847 | 8.8776 | 8.5031 | 7.5796 | 6.8306 | 6.4092 | 4.8939 | 4.1378 | 3.3796 | 11.9947 | 11.7855 | 11.5304 | 11.2284 | 10.8304 | 10.4151 | 9.7671 | 9.1814 | 8.7518 | 7.0141 | 4.662 | 0.31816 | 10.3024 | 10.1412 | 9.9178 | 9.6249 | 9.2545 | 8.8392 | 7.9688 | 7.2137 | 6.781 | 5.1882 | 4.7402 | 4.1249
|  | CHAPEL PRIMARY | HT |  |  |  |  | 9.9776 | 9.8663 | 9.7306 | 9.5184 | 8.749 | 8.101 | 7.7194 | 7.351 | 7.0939 | 5.4857 | 4.1439 | 3.4357 | 12.2396 | 12.112 | 11.9569 | 11.7222 | 11.3263 | 10.9314 | 10.5743 | 10.1927 | 9.8386 | 8.2182 | 7.4416 | 7.2049 | 10.4841 | 10.381 | 10.2484 | 10.0433 | 9.3759 | 8.779 | 8.3851 | 7.978 | 7.6535 | 5.9269 | 4.6759 | 4.1871
|  | CHAPEL PRIMARY | HE |  |  |  |  | 9.9092 | 9.7673 | 9.599 | 9.402 | 9.1327 | 8.798 | 8.0724 | 7.3612 | 6.8092 | 3.9 | 2.5194 | 2.1806 | 12.1324 | 11.9671 | 11.7569 | 11.5131 | 11.1549 | 10.7753 | 10.2059 | 9.6059 | 9.0345 | 6.6692 | 4.4365 | 0.50796 | 10.4147 | 10.28 | 10.1229 | 9.93 | 9.6708 | 9.3627 | 8.7249 | 7.9892 | 7.2463 | 4.2147 | 2.9024 | 2.5871
|  | CHAPEL PRIMARY | CF |  |  |  |  | 10.0347 | 9.95 | 9.8551 | 9.748 | 9.6214 | 9.4786 | 9.2969 | 8.8143 | 8.3031 | 6.7653 | 4.8398 | 3.5102 | 12.211 | 12.0784 | 11.9284 | 11.7518 | 11.5284 | 11.2569 | 10.9416 | 10.4386 | 9.9233 | 7.2273 | 2.8569 | -6.5533 | 10.5341 | 10.4535 | 10.3637 | 10.2616 | 10.1422 | 10.0055 | 9.8331 | 9.4086 | 8.9586 | 7.0147 | 5.0892 | 3.83
COWLEY GSP | YARNTON BSP | CHARLBURY PRIMARY | MINIMUM HEADROOM | SP 36034 18376 | NO | YES | 0.435 | 8.5755 | 8.3327 | 8.1224 | 7.851 | 7.4939 | 7.4429 | 7.0255 | 6.6071 | 6.3276 | 4.7898 | 3.4878 | 2.6847 | 9.7847 | 9.5827 | 9.4041 | 9.1704 | 8.8888 | 8.9449 | 8.6429 | 8.3337 | 8.15 | 7.0561 | 5.6296 | 2.1929 | 8.4633 | 8.2143 | 8.0031 | 7.7194 | 7.3684 | 7.4133 | 7.0153 | 6.6184 | 6.3776 | 5.049 | 3.9184 | 3.249
|  | CHARLBURY PRIMARY | EE |  |  |  |  | 8.5755 | 8.3327 | 8.1224 | 7.851 | 7.4939 | 7.4429 | 7.0255 | 6.6071 | 6.3276 | 4.8245 | 3.7153 | 2.85 | 9.7847 | 9.5827 | 9.4041 | 9.1704 | 8.8888 | 8.9449 | 8.6429 | 8.3337 | 8.15 | 7.0561 | 5.8541 | 4.0102 | 8.4633 | 8.2143 | 8.0031 | 7.7194 | 7.3684 | 7.4133 | 7.0153 | 6.6184 | 6.3776 | 5.0673 | 4.1224 | 3.3888
|  | CHARLBURY PRIMARY | HT |  |  |  |  | 8.7082 | 8.5296 | 8.3816 | 8.1837 | 7.9439 | 7.5755 | 7.1684 | 6.7398 | 6.6929 | 4.7898 | 3.4878 | 2.6847 | 9.9571 | 9.8255 | 9.7214 | 9.5765 | 9.4327 | 9.2122 | 8.9582 | 8.6816 | 8.8061 | 7.7939 | 7.2122 | 6.8724 | 8.6224 | 8.449 | 8.301 | 8.101 | 7.8847 | 7.5388 | 7.1531 | 6.7459 | 6.7724 | 5.049 | 3.9184 | 3.249
|  | CHARLBURY PRIMARY | HE |  |  |  |  | 8.7163 | 8.5469 | 8.4092 | 8.2214 | 7.998 | 7.6888 | 7.3378 | 6.9673 | 6.9969 | 5.3276 | 4.2378 | 3.6714 | 9.9245 | 9.7806 | 9.6633 | 9.5031 | 9.3429 | 9.1163 | 8.852 | 8.5622 | 8.6541 | 7.3265 | 6.1071 | 4.3908 | 8.6296 | 8.4602 | 8.3245 | 8.1357 | 7.9306 | 7.6357 | 7.2959 | 6.9337 | 7.0347 | 5.5204 | 4.5959 | 4.1255
|  | CHARLBURY PRIMARY | CF |  |  |  |  | 8.8184 | 8.7143 | 8.6265 | 8.4969 | 8.3061 | 8.1898 | 8.0122 | 7.8204 | 7.6204 | 6.8245 | 5.7194 | 4.6357 | 9.9714 | 9.8622 | 9.7704 | 9.6388 | 9.4643 | 9.3306 | 9.1286 | 8.9143 | 8.6816 | 7.6153 | 5.6296 | 2.1929 | 8.7163 | 8.6092 | 8.5194 | 8.3867 | 8.201 | 8.0867 | 7.901 | 7.701 | 7.4908 | 6.8184 | 5.8469 | 4.9398
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER PRIMARY | MINIMUM HEADROOM | SY 67309 93186 | NO | NO | 1.895 | 5.3949 | 4.8041 | 4.3602 | 3.8398 | 3.3663 | 3.2367 | 2.3347 | 1.1837 | 0.17551 | -4.6735 | -9.2602 | -13.0837 | 6.9561 | 6.5847 | 6.2959 | 5.9347 | 5.5796 | 5.5847 | 4.9867 | 4.3245 | 3.7704 | 0.92143 | -1.8949 | -7.3327 | 5.7163 | 5.1806 | 4.7806 | 4.2847 | 3.8224 | 3.7694 | 2.95 | 1.9561 | 1.1265 | -2.9092 | -6.6592 | -9.7071
|  | CHARMINSTER PRIMARY | EE |  |  |  |  | 5.3949 | 4.8041 | 4.3602 | 3.8398 | 3.3663 | 3.2367 | 2.3347 | 1.1837 | 0.17551 | -4.6735 | -9.0245 | -12.8827 | 6.9561 | 6.5847 | 6.2959 | 5.9347 | 5.5796 | 5.5847 | 4.9867 | 4.3245 | 3.7704 | 0.92143 | -1.8949 | -5.3918 | 5.7163 | 5.1806 | 4.7806 | 4.2847 | 3.8224 | 3.7694 | 2.95 | 1.9561 | 1.1265 | -2.9092 | -6.4276 | -9.5286
|  | CHARMINSTER PRIMARY | HT |  |  |  |  | 5.5806 | 5.0908 | 4.6867 | 4.2592 | 3.9327 | 3.4878 | 2.6092 | 1.4765 | 0.7102 | -4.6459 | -9.2602 | -13.0837 | 7.149 | 6.8918 | 6.6694 | 6.4286 | 6.2418 | 5.9704 | 5.448 | 4.8622 | 4.5745 | 1.8245 | -0.34388 | -2.0449 | 5.9163 | 5.501 | 5.1367 | 4.7449 | 4.4459 | 4.0265 | 3.2459 | 2.2714 | 1.7276 | -2.8633 | -6.6592 | -9.7071
|  | CHARMINSTER PRIMARY | HE |  |  |  |  | 5.5867 | 5.1082 | 4.7173 | 4.3041 | 3.998 | 3.6051 | 2.7867 | 1.7112 | 1.0092 | -4.0806 | -8.3745 | -11.7582 | 7.1112 | 6.8367 | 6.5959 | 6.3408 | 6.1357 | 5.8673 | 5.3337 | 4.7204 | 4.4041 | 1.351 | -1.5031 | -4.8194 | 5.9214 | 5.5173 | 5.1633 | 4.7898 | 4.5092 | 4.1378 | 3.4071 | 2.4806 | 2.002 | -2.3061 | -5.7939 | -8.4745
|  | CHARMINSTER PRIMARY | CF |  |  |  |  | 5.7367 | 5.3296 | 5.0643 | 4.7592 | 4.5194 | 4.3633 | 3.7837 | 2.9816 | 2.1582 | -1.6684 | -5.9857 | -10.4276 | 7.1816 | 6.9296 | 6.7561 | 6.5429 | 6.348 | 6.1806 | 5.7316 | 5.2214 | 4.6867 | 1.9531 | -1.8378 | -7.3327 | 6.0602 | 5.7102 | 5.4755 | 5.1929 | 4.9561 | 4.8122 | 4.2939 | 3.6051 | 2.902 | -0.18673 | -3.7816 | -7.3929
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | CHICHESTER PRIMARY | MINIMUM HEADROOM | SU 92198 07420 | NO | YES | 14.369 | -8.3007 | -9.4231 | 6.384 | 5.4228 | 4.3197 | 3.0115 | 1.5218 | 0.030935 | -0.99968 | -5.9415 | -9.4864 | -11.6211 | -11.7297 | -12.2246 | 5.1075 | 4.6401 | 4.1075 | 3.486 | 2.7411 | 1.9687 | 1.333 | -1.9109 | -5.2507 | -14.0078 | -11.9172 | -12.9499 | -13.3213 | 2.7248 | 1.7095 | 0.50236 | -0.88029 | -2.264 | -3.1946 | -7.5487 | -10.6956 | -12.5507
|  | CHICHESTER PRIMARY | EE |  |  |  |  | -8.3007 | -9.4231 | 6.384 | 5.4228 | 4.3197 | 3.0115 | 1.5218 | 0.030935 | -0.99968 | -5.7354 | -8.7619 | -11.116 | -11.7297 | -12.2246 | 5.1075 | 4.6401 | 4.1075 | 3.486 | 2.7411 | 1.9687 | 1.333 | -1.8813 | -5.0885 | -9.7354 | -11.9172 | -12.9499 | -13.3213 | 2.7248 | 1.7095 | 0.50236 | -0.88029 | -2.264 | -3.1946 | -7.414 | -10.065 | -12.1231
|  | CHICHESTER PRIMARY | HT |  |  |  |  | -7.8599 | -8.7538 | 6.6422 | 5.735 | 5.2371 | 4.0962 | 2.8279 | 1.5054 | 0.1993 | -5.9415 | -9.4864 | -11.6211 | -11.4695 | -11.8429 | 5.432 | 5.0534 | 4.7707 | 4.2769 | 3.6891 | 3.0452 | 2.4177 | -0.61396 | -2.4078 | -3.4385 | -11.4754 | -12.2744 | -13.057 | 3.0503 | 2.6381 | 1.6034 | 0.44522 | -0.76192 | -1.9568 | -7.5487 | -10.6956 | -12.5507
|  | CHICHESTER PRIMARY | HE |  |  |  |  | -7.8538 | -8.7293 | 6.6809 | 5.7932 | 5.3105 | 4.2993 | 3.1401 | 1.9391 | 0.7544 | -4.8007 | -7.9813 | -9.5711 | -11.5491 | -11.9644 | 5.2626 | 4.8228 | 4.4728 | 3.9432 | 3.3075 | 2.6054 | 1.8973 | -1.9109 | -5.2507 | -9.5997 | -11.4713 | -12.2601 | -13.0264 | 3.0932 | 2.6922 | 1.7728 | 0.70951 | -0.39458 | -1.4864 | -6.5691 | -9.6078 | -11.2129
|  | CHICHESTER PRIMARY | CF |  |  |  |  | -7.4721 | -8.2007 | 7.5105 | 6.9728 | 6.3279 | 6.2003 | 5.4942 | 4.7411 | 3.985 | -0.1456 | -3.6466 | -6.8823 | -11.3644 | -11.7072 | 5.6452 | 5.3595 | 5.0105 | 4.7881 | 4.3513 | 3.885 | 3.3962 | 0.21665 | -5.2027 | -14.0078 | -11.1213 | -11.7774 | -12.2652 | 4.1748 | 3.5809 | 3.5013 | 2.8513 | 2.1646 | 1.4697 | -2.364 | -5.5487 | -8.4191
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL PRIMARY | MINIMUM HEADROOM | SY 65479 80511 | NO | NO | 1.554 | 6.0039 | 5.7631 | 5.5253 | 5.2182 | 4.8253 | 4.4253 | 3.8467 | 3.309 | 2.7641 | 0.23653 | -1.1461 | -1.8482 | 6.321 | 6.1383 | 5.9618 | 5.7261 | 5.3751 | 5.1679 | 4.7414 | 4.3353 | 3.972 | 2.324 | 0.94955 | -2.6076 | 5.5007 | 5.2068 | 4.916 | 4.5211 | 4.0333 | 3.6313 | 3.0476 | 2.5058 | 1.9905 | -0.22992 | -1.4432 | -2.0452
|  | CHICKERELL PRIMARY | EE |  |  |  |  | 6.0039 | 5.7631 | 5.5253 | 5.2182 | 4.8253 | 4.4253 | 3.8467 | 3.309 | 2.7641 | 0.30592 | -0.92163 | -1.6645 | 6.321 | 6.1383 | 5.9618 | 5.7261 | 5.3751 | 5.1679 | 4.7414 | 4.3353 | 3.972 | 2.324 | 1.0271 | -0.73718 | 5.5007 | 5.2068 | 4.916 | 4.5211 | 4.0333 | 3.6313 | 3.0476 | 2.5058 | 1.9905 | -0.18094 | -1.2626 | -1.883
|  | CHICKERELL PRIMARY | HT |  |  |  |  | 6.1222 | 5.9202 | 5.7233 | 5.4661 | 5.061 | 4.5284 | 3.9682 | 3.4304 | 2.9631 | 0.23653 | -1.1461 | -1.8482 | 6.4169 | 6.272 | 6.1353 | 5.9465 | 5.7332 | 5.4353 | 5.0659 | 4.7077 | 4.5475 | 3.0781 | 2.421 | 2.0955 | 5.5864 | 5.3221 | 5.0558 | 4.6976 | 4.2701 | 3.7272 | 3.1589 | 2.615 | 2.215 | -0.22992 | -1.4432 | -2.0452
|  | CHICKERELL PRIMARY | HE |  |  |  |  | 6.111 | 5.9049 | 5.7029 | 5.4355 | 5.0845 | 4.5947 | 4.0671 | 3.562 | 3.1916 | 0.66306 | -0.65735 | -1.2573 | 6.3996 | 6.2404 | 6.0893 | 5.8822 | 5.6536 | 5.3118 | 4.922 | 4.5353 | 4.3444 | 2.5353 | 1.1791 | -0.52188 | 5.5997 | 5.3395 | 5.0803 | 4.7272 | 4.3048 | 3.8109 | 3.2844 | 2.7782 | 2.417 | 0.15171 | -1.0197 | -1.5442
|  | CHICKERELL PRIMARY | CF |  |  |  |  | 6.2233 | 6.0763 | 5.9365 | 5.7437 | 5.51 | 5.259 | 4.9488 | 4.6355 | 4.2784 | 2.7804 | 1.3151 | -0.10531 | 6.4689 | 6.3475 | 6.2342 | 6.073 | 5.8761 | 5.6271 | 5.3465 | 5.0485 | 4.7118 | 3.1424 | 0.94955 | -2.6076 | 5.7374 | 5.5568 | 5.3793 | 5.1282 | 4.8068 | 4.5099 | 4.2119 | 3.9089 | 3.5629 | 2.0731 | 0.73131 | -0.5391
AXMINSTER GSP | YEOVIL BSP | CHILTON CANTELO PRIMARY | MINIMUM HEADROOM | ST 57910 21616 | NO | NO | 4.61 | 1.3357 | 0.97143 | 0.32857 | -0.46735 | -1.4092 | -2.1949 | -2.9071 | -3.2459 | -3.7806 | -5.9286 | -7.1102 | -7.5378 | 3.098 | 2.7776 | 2.4082 | 1.9908 | 1.4959 | 1.0592 | 0.64388 | 0.41224 | 0.034694 | -1.7786 | -2.6265 | -4.2929 | 1.8051 | 1.349 | 0.78878 | 0.13061 | -0.64796 | -1.2765 | -1.848 | -2.2133 | -2.6745 | -4.9286 | -6.0408 | -6.4418
|  | CHILTON CANTELO PRIMARY | EE |  |  |  |  | 1.3357 | 0.97143 | 0.32857 | -0.46735 | -1.4092 | -2.1949 | -2.9071 | -3.2459 | -3.7806 | -5.1867 | -5.7143 | -6.0245 | 3.098 | 2.7776 | 2.4082 | 1.9908 | 1.4959 | 1.0592 | 0.64388 | 0.41224 | 0.034694 | -0.98061 | -1.6071 | -2.6582 | 1.8051 | 1.349 | 0.78878 | 0.13061 | -0.64796 | -1.2765 | -1.848 | -2.2133 | -2.6745 | -4.0571 | -4.4449 | -4.6908
|  | CHILTON CANTELO PRIMARY | HT |  |  |  |  | 1.5286 | 1.2173 | 0.63673 | -0.080612 | -0.96735 | -1.6714 | -2.2296 | -2.8388 | -3.452 | -4.8694 | -5.6878 | -6.1316 | 3.249 | 2.9745 | 2.6653 | 2.3061 | 1.8827 | 1.5245 | 1.2306 | 0.90612 | 0.57347 | -0.5551 | -1.1357 | -1.3429 | 1.9694 | 1.5388 | 1.0337 | 0.43163 | -0.29082 | -0.85408 | -1.3184 | -1.8173 | -2.3204 | -3.6653 | -4.4684 | -4.8776
|  | CHILTON CANTELO PRIMARY | HE |  |  |  |  | 1.4673 | 1.1286 | 0.56939 | -0.16939 | -1.0796 | -1.801 | -2.3908 | -3.0327 | -3.6847 | -5.9286 | -7.1102 | -7.5378 | 3.198 | 2.899 | 2.5622 | 2.1694 | 1.7051 | 1.3061 | 0.9602 | 0.57347 | 0.1602 | -1.7786 | -2.6265 | -3.1224 | 1.9327 | 1.4847 | 0.95918 | 0.33163 | -0.41837 | -1.0071 | -1.5092 | -2.049 | -2.598 | -4.9286 | -6.0408 | -6.4418
|  | CHILTON CANTELO PRIMARY | CF |  |  |  |  | 1.7439 | 1.5306 | 1.2878 | 0.77449 | 0.096939 | -0.53367 | -1.0827 | -1.6041 | -2.1673 | -3.5663 | -5.2255 | -6.5286 | 3.3857 | 3.1847 | 2.9561 | 2.6439 | 2.2755 | 1.9153 | 1.5878 | 1.2643 | 0.91531 | -0.33061 | -1.9418 | -4.2929 | 2.2112 | 1.9316 | 1.6 | 1.1469 | 0.58571 | 0.097959 | -0.33673 | -0.76224 | -1.2184 | -2.5194 | -4.2745 | -5.4918
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | CHINEHAM PRIMARY | MINIMUM HEADROOM | SU 65105 55805 | NO | NO | 6.975 | 12.6019 | 12.1896 | 11.6101 | 10.8172 | 10.255 | 8.7662 | 7.0988 | 5.6896 | 4.2937 | -0.11341 | -2.544 | -3.9297 | 16.4519 | 16.0907 | 15.655 | 15.1182 | 14.859 | 14.2366 | 13.3386 | 12.3233 | 11.5478 | 8.4692 | 6.3703 | 0.055976 | 13.6478 | 13.2448 | 12.6927 | 11.9682 | 11.5305 | 10.3315 | 8.8937 | 7.6917 | 6.4488 | 2.405 | 0.23863 | -0.95525
|  | CHINEHAM PRIMARY | EE |  |  |  |  | 12.6019 | 12.1896 | 11.6101 | 10.8172 | 10.255 | 9.2999 | 7.8274 | 6.1192 | 4.7662 | 0.036588 | -2.0991 | -3.7277 | 16.4519 | 16.0907 | 15.655 | 15.1182 | 14.859 | 14.2366 | 13.3386 | 12.3233 | 11.5478 | 8.4692 | 6.3703 | 3.1866 | 13.6478 | 13.2448 | 12.6927 | 11.9682 | 11.5305 | 10.6499 | 9.3427 | 7.8427 | 6.6774 | 2.5039 | 0.6223 | -0.78994
|  | CHINEHAM PRIMARY | HT |  |  |  |  | 12.8519 | 12.4111 | 11.8866 | 11.2029 | 10.3539 | 8.7662 | 7.0988 | 5.6896 | 4.2937 | -0.11341 | -2.544 | -3.9297 | 16.706 | 16.4499 | 16.1396 | 15.7723 | 15.2601 | 14.4519 | 13.5682 | 12.9641 | 12.1907 | 9.7733 | 8.658 | 8.1029 | 13.8009 | 13.4427 | 13.009 | 12.4386 | 11.6815 | 10.3315 | 8.8937 | 7.6917 | 6.4488 | 2.405 | 0.23863 | -0.95525
|  | CHINEHAM PRIMARY | HE |  |  |  |  | 12.8192 | 12.4386 | 11.9274 | 11.256 | 10.5121 | 9.6652 | 8.4958 | 7.5039 | 6.4958 | 1.755 | -1.3859 | -2.4808 | 16.6458 | 16.356 | 16.008 | 15.6101 | 15.1458 | 14.5978 | 13.8621 | 13.3866 | 12.7039 | 9.2937 | 6.6366 | 3.6601 | 13.808 | 13.4601 | 13.0376 | 12.4815 | 11.8437 | 11.0845 | 10.058 | 9.2131 | 8.2917 | 3.9274 | 1.2366 | 0.29781
|  | CHINEHAM PRIMARY | CF |  |  |  |  | 13.0927 | 12.9294 | 12.7448 | 12.4111 | 11.7907 | 11.1723 | 10.5611 | 9.905 | 9.4141 | 5.9825 | 2.357 | -0.46749 | 16.7733 | 16.5713 | 16.3835 | 16.106 | 15.7009 | 15.2478 | 14.7478 | 14.1958 | 13.6948 | 10.5499 | 6.3733 | 0.055976 | 14.0417 | 13.8815 | 13.7192 | 13.4468 | 12.956 | 12.4396 | 11.8835 | 11.2754 | 10.7754 | 7.5294 | 4.4937 | 2.056
COWLEY GSP | YARNTON BSP | CHIPPING NORTON PRIMARY | MINIMUM HEADROOM | SP 31382 26792 | NO | YES | 2.666 | 3.2275 | 2.9142 | 2.603 | 2.2652 | 1.6326 | 0.89482 | 0.099918 | -0.87763 | -1.844 | -4.5011 | -6.0817 | -7.0858 | 5.452 | 5.2091 | 4.9734 | 4.6969 | 4.2101 | 3.7101 | 3.4642 | 2.8397 | 2.3234 | 0.52645 | -1.0215 | -5.0552 | 3.1367 | 2.8244 | 2.5244 | 2.1601 | 1.5601 | 0.87135 | 0.46216 | -0.37049 | -1.1991 | -3.5266 | -4.894 | -5.7205
|  | CHIPPING NORTON PRIMARY | EE |  |  |  |  | 3.2275 | 2.9142 | 2.603 | 2.2652 | 1.6326 | 0.89482 | 0.31931 | -0.72967 | -1.6827 | -4.5011 | -5.8603 | -6.8889 | 5.452 | 5.2091 | 4.9734 | 4.6969 | 4.2101 | 3.7101 | 3.4642 | 2.8397 | 2.3234 | 0.52645 | -0.91437 | -3.0613 | 3.1367 | 2.8244 | 2.5244 | 2.1601 | 1.5601 | 0.87135 | 0.53563 | -0.36743 | -1.1531 | -3.5266 | -4.6817 | -5.5501
|  | CHIPPING NORTON PRIMARY | HT |  |  |  |  | 3.3407 | 3.0907 | 2.8367 | 2.3193 | 1.8132 | 1.0622 | 0.099918 | -0.87763 | -1.844 | -4.4572 | -6.0817 | -7.0858 | 5.6193 | 5.4611 | 5.3071 | 4.9469 | 4.6367 | 4.2367 | 3.7254 | 3.204 | 2.6816 | 1.4397 | 0.67951 | 0.26624 | 3.305 | 3.0713 | 2.8377 | 2.3734 | 1.9336 | 1.2846 | 0.46216 | -0.37049 | -1.1991 | -3.4766 | -4.894 | -5.7205
|  | CHIPPING NORTON PRIMARY | HE |  |  |  |  | 3.3469 | 3.102 | 2.856 | 2.5979 | 2.0499 | 1.4724 | 0.64788 | -0.35008 | -1.3409 | -3.9154 | -5.2378 | -5.8766 | 5.5897 | 5.4101 | 5.2397 | 5.0387 | 4.6397 | 4.2887 | 3.7907 | 3.2101 | 2.6203 | 0.92645 | -0.53376 | -2.5072 | 3.3122 | 3.0856 | 2.8632 | 2.6132 | 2.1316 | 1.6336 | 0.92441 | 0.080531 | -0.76437 | -2.9552 | -4.0807 | -4.6042
|  | CHIPPING NORTON PRIMARY | CF |  |  |  |  | 3.4734 | 3.2958 | 3.0969 | 2.9785 | 2.8244 | 2.5703 | 2.2877 | 1.9285 | 1.5173 | -1.8011 | -3.247 | -4.6674 | 5.654 | 5.506 | 5.3397 | 5.2213 | 5.052 | 4.7907 | 4.5183 | 4.1897 | 3.8234 | 1.3887 | -1.0215 | -5.0552 | 3.4275 | 3.2571 | 3.0632 | 2.9479 | 2.7877 | 2.5438 | 2.2846 | 1.9397 | 1.553 | -1.096 | -2.3878 | -3.6205
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE PRIMARY | MINIMUM HEADROOM | SU 80226 89155 | NO | NO | 0.863 | 3.1459 | 3.1102 | 3.0541 | 2.9796 | 2.9112 | 2.8133 | 2.6969 | 2.5898 | 2.499 | 2.0367 | 1.8296 | 1.6806 | 4.5969 | 4.5378 | 4.4673 | 4.3796 | 4.3214 | 4.2102 | 4.0816 | 3.999 | 3.9337 | 3.5704 | 3.1765 | 2.248 | 3.4816 | 3.4082 | 3.3153 | 3.2061 | 3.1306 | 2.9878 | 2.8224 | 2.702 | 2.6082 | 2.148 | 1.9653 | 1.8316
|  | CHISBRIDGE PRIMARY | EE |  |  |  |  | 3.1459 | 3.1102 | 3.0541 | 2.9796 | 2.9112 | 2.8133 | 2.6969 | 2.5898 | 2.499 | 2.0367 | 1.8367 | 1.7418 | 4.5969 | 4.5378 | 4.4673 | 4.3796 | 4.3214 | 4.2102 | 4.0816 | 3.999 | 3.9337 | 3.5704 | 3.2663 | 2.8245 | 3.4816 | 3.4082 | 3.3153 | 3.2061 | 3.1306 | 2.9878 | 2.8224 | 2.702 | 2.6082 | 2.148 | 1.9704 | 1.8847
|  | CHISBRIDGE PRIMARY | HT |  |  |  |  | 3.1755 | 3.1418 | 3.1041 | 3.0602 | 2.9949 | 2.9122 | 2.8224 | 2.7184 | 2.6102 | 2.102 | 1.8296 | 1.6806 | 4.6592 | 4.6163 | 4.5582 | 4.5235 | 4.4663 | 4.3867 | 4.3255 | 4.2347 | 4.1357 | 3.7867 | 3.652 | 3.5796 | 3.5439 | 3.4776 | 3.402 | 3.3408 | 3.2592 | 3.1439 | 3.0449 | 2.9102 | 2.7704 | 2.2082 | 1.9653 | 1.8316
|  | CHISBRIDGE PRIMARY | HE |  |  |  |  | 3.1755 | 3.1439 | 3.1071 | 3.0571 | 2.9929 | 2.9092 | 2.8204 | 2.7133 | 2.6041 | 2.0878 | 1.9276 | 1.8551 | 4.6541 | 4.6031 | 4.5449 | 4.5051 | 4.4449 | 4.3643 | 4.3031 | 4.2061 | 4.102 | 3.6337 | 3.3265 | 2.8969 | 3.5459 | 3.4806 | 3.4061 | 3.349 | 3.2735 | 3.1622 | 3.0745 | 2.9469 | 2.8163 | 2.2347 | 2.0653 | 1.999
|  | CHISBRIDGE PRIMARY | CF |  |  |  |  | 3.198 | 3.1765 | 3.152 | 3.1265 | 3.1031 | 3.0704 | 3.0122 | 2.949 | 2.8949 | 2.5092 | 2.1684 | 1.9133 | 4.6714 | 4.6347 | 4.5878 | 4.5337 | 4.5031 | 4.449 | 4.3765 | 4.299 | 4.251 | 3.7745 | 3.1765 | 2.248 | 3.5776 | 3.5296 | 3.4704 | 3.4102 | 3.3694 | 3.3102 | 3.2286 | 3.1449 | 3.0949 | 2.6592 | 2.3245 | 2.0735
MINETY GSP | TOOTHILL BSP | CHISLEDON PRIMARY | MINIMUM HEADROOM | SU 18894 79934 | NO | NO | 0.619 | 9.6265 | 8.7643 | 7.4112 | 5.5612 | 3.1102 | 0.3602 | -2.3051 | -4.7653 | -6.8296 | -12.0388 | -13.9592 | -15.2582 | 8.8184 | 8.3745 | 7.6918 | 6.7347 | 5.3337 | 3.449 | 1.5622 | -0.073469 | -1.4541 | -5.1061 | -6.8184 | -8.3122 | 9.0429 | 8.3592 | 7.2786 | 5.7633 | 3.6939 | 1.2173 | -1.2184 | -3.4163 | -5.2878 | -10.1908 | -12.2469 | -13.648
|  | CHISLEDON PRIMARY | EE |  |  |  |  | 9.6265 | 8.7643 | 7.4112 | 5.7673 | 3.549 | 0.95612 | -1.8031 | -4.3959 | -6.6143 | -11.4592 | -12.8398 | -14.149 | 8.8184 | 8.3745 | 7.6918 | 6.8806 | 5.6673 | 3.9143 | 1.9286 | 0.1551 | -1.4082 | -4.8653 | -6.3592 | -8.3122 | 9.0429 | 8.3592 | 7.2786 | 5.949 | 4.0969 | 1.7694 | -0.75918 | -3.0806 | -5.0949 | -9.5061 | -10.9184 | -12.3224
|  | CHISLEDON PRIMARY | HT |  |  |  |  | 9.7 | 8.8561 | 7.5337 | 5.5612 | 3.1102 | 0.3602 | -2.3051 | -4.7653 | -6.8296 | -12.0388 | -13.9592 | -15.2582 | 8.9061 | 8.4878 | 7.8398 | 6.7347 | 5.3337 | 3.449 | 1.5622 | -0.073469 | -1.4541 | -5.1061 | -6.8184 | -8.0408 | 9.1153 | 8.452 | 7.4031 | 5.7633 | 3.6939 | 1.2173 | -1.2184 | -3.4163 | -5.2878 | -10.1908 | -12.2469 | -13.648
|  | CHISLEDON PRIMARY | HE |  |  |  |  | 9.7163 | 8.8796 | 7.5633 | 5.9908 | 3.7827 | 1.401 | -1.1082 | -3.4031 | -5.4214 | -10.3031 | -11.7571 | -12.9602 | 8.901 | 8.4633 | 7.799 | 7.0378 | 5.8357 | 4.3 | 2.5551 | 1.099 | -0.20102 | -3.6612 | -5.2378 | -7.1786 | 9.1306 | 8.4724 | 7.4296 | 6.1673 | 4.3265 | 2.2408 | -0.0091837 | -1.9816 | -3.7367 | -8.1602 | -9.6459 | -10.9643
|  | CHISLEDON PRIMARY | CF |  |  |  |  | 9.8296 | 9.1 | 7.9633 | 6.5867 | 5.0245 | 3.1776 | 1.151 | -0.98265 | -2.7857 | -7.9153 | -8.9816 | -10.2102 | 8.951 | 8.5643 | 7.9714 | 7.2796 | 6.5122 | 5.3592 | 3.9724 | 2.5092 | 1.2918 | -2.3429 | -3.6265 | -5.7592 | 9.2327 | 8.6724 | 7.7867 | 6.698 | 5.4531 | 3.8857 | 2.1 | 0.23061 | -1.3327 | -5.8316 | -6.7827 | -7.8765
FLEET-BRAMLEY GSP | BRACKNELL BSP | CHOBHAM PRIMARY | MINIMUM HEADROOM | SU 97173 63223 | NO | NO | 4.905 | 9.279 | 8.6382 | 7.9514 | 7.1902 | 6.9239 | 6.4178 | 5.8167 | 5.2545 | 4.8933 | 2.8698 | 1.182 | 0.31673 | 11.6865 | 11.2835 | 10.8355 | 10.3498 | 10.2345 | 9.862 | 9.4182 | 8.9784 | 8.7008 | 7.1131 | 4.5865 | -0.88286 | 9.7331 | 9.1708 | 8.5494 | 7.8576 | 7.7524 | 7.278 | 6.7127 | 6.1749 | 5.8657 | 4.1269 | 2.5484 | 1.7382
|  | CHOBHAM PRIMARY | EE |  |  |  |  | 9.279 | 8.6382 | 7.9514 | 7.1902 | 6.9239 | 6.4178 | 5.8167 | 5.2545 | 4.8933 | 3.0484 | 1.5535 | 0.51776 | 11.6865 | 11.2835 | 10.8355 | 10.3498 | 10.2345 | 9.862 | 9.4182 | 8.9784 | 8.7008 | 7.1131 | 5.2529 | 2.4416 | 9.7331 | 9.1708 | 8.5494 | 7.8576 | 7.7524 | 7.278 | 6.7127 | 6.1749 | 5.8657 | 4.2882 | 2.8851 | 1.9208
|  | CHOBHAM PRIMARY | HT |  |  |  |  | 9.4729 | 8.8984 | 8.2749 | 7.6422 | 7.0096 | 6.4902 | 6.3086 | 5.8188 | 5.3127 | 2.8698 | 1.182 | 0.31673 | 11.909 | 11.5988 | 11.2539 | 10.9182 | 10.5631 | 10.2529 | 10.2273 | 9.9314 | 9.6202 | 8.2437 | 7.4876 | 7.1222 | 9.9565 | 9.4729 | 8.9331 | 8.3984 | 7.8402 | 7.3524 | 7.2198 | 6.7831 | 6.332 | 4.1269 | 2.5484 | 1.7382
|  | CHOBHAM PRIMARY | HE |  |  |  |  | 9.4922 | 8.932 | 8.3412 | 7.7443 | 7.132 | 6.7096 | 6.6127 | 6.2014 | 5.7769 | 3.6524 | 2.0831 | 1.3851 | 11.8539 | 11.5131 | 11.1427 | 10.7876 | 10.3947 | 10.0651 | 10.0049 | 9.6671 | 9.3151 | 7.3447 | 5.4059 | 2.7314 | 9.9718 | 9.4973 | 8.9841 | 8.4759 | 7.9371 | 7.5259 | 7.4963 | 7.1361 | 6.7647 | 4.8341 | 3.3627 | 2.7055
|  | CHOBHAM PRIMARY | CF |  |  |  |  | 9.6922 | 9.2392 | 8.7953 | 8.3596 | 7.9371 | 7.7565 | 7.5065 | 7.6147 | 7.3851 | 5.7616 | 4.1535 | 2.678 | 11.9457 | 11.6478 | 11.3416 | 11.0467 | 10.7284 | 10.4896 | 10.1886 | 10.1712 | 9.8753 | 7.7631 | 4.5865 | -0.88286 | 10.1463 | 9.7627 | 9.3739 | 9.0076 | 8.631 | 8.4351 | 8.1718 | 8.3535 | 8.1249 | 6.5933 | 5.228 | 3.9178
COWLEY GSP | DRAYTON BSP | CHOLSEY PRIMARY | MINIMUM HEADROOM | SU 58223 84685 | NO | YES | 0.653 | 7.6 | 7.3755 | 7.0163 | 6.7214 | 5.7327 | 5.1398 | 4.4571 | 2.552 | 1.1316 | -2.0541 | -5.7439 | -9.8673 | 9.2867 | 9.099 | 8.6847 | 8.401 | 7.2531 | 6.65 | 5.9459 | 3.7204 | 2.1204 | -1.2112 | -5.7286 | -11.8592 | 8.0408 | 7.8031 | 7.4 | 7.0776 | 5.8898 | 5.2398 | 4.4673 | 2.1786 | 0.5102 | -2.9673 | -7.2367 | -12.2194
|  | CHOLSEY PRIMARY | EE |  |  |  |  | 7.6 | 7.3755 | 7.1684 | 6.8878 | 6.3673 | 5.7265 | 5.7224 | 4.9837 | 4.5245 | 1.8296 | -3.1857 | -5.3286 | 9.2867 | 9.099 | 8.9316 | 8.7163 | 8.202 | 7.6245 | 7.6867 | 6.951 | 6.5418 | 3.9745 | -2.1633 | -5.599 | 8.0408 | 7.8031 | 7.5969 | 7.3255 | 6.7602 | 6.0888 | 6.1418 | 5.3255 | 4.85 | 2.0398 | -3.8745 | -6.2867
|  | CHOLSEY PRIMARY | HT |  |  |  |  | 7.7031 | 7.452 | 7.1388 | 6.9388 | 6.1102 | 5.4653 | 4.7071 | 4.2439 | 3.3663 | 0.25408 | -4.6102 | -8.0041 | 9.4296 | 9.2214 | 8.9316 | 8.7949 | 7.8776 | 7.2878 | 6.5612 | 6.2122 | 5.3582 | 2.7153 | -2.4633 | -6.1765 | 8.1735 | 7.9071 | 7.5694 | 7.3684 | 6.3867 | 5.6969 | 4.8561 | 4.3857 | 3.402 | 0.093878 | -5.5867 | -9.5816
|  | CHOLSEY PRIMARY | HE |  |  |  |  | 7.7122 | 7.4378 | 7.0163 | 6.7214 | 5.7327 | 5.1398 | 4.4571 | 2.552 | 1.1316 | -2.0541 | -5.7439 | -9.8673 | 9.4 | 9.1378 | 8.6847 | 8.401 | 7.2531 | 6.65 | 5.9459 | 3.7204 | 2.1204 | -1.2112 | -5.7286 | -11.8592 | 8.1776 | 7.8776 | 7.4 | 7.0776 | 5.8898 | 5.2398 | 4.4673 | 2.1786 | 0.5102 | -2.9673 | -7.2367 | -12.2194
|  | CHOLSEY PRIMARY | CF |  |  |  |  | 7.8245 | 7.7092 | 7.5857 | 7.4122 | 7.1714 | 6.8867 | 6.6714 | 6.3806 | 6.0347 | 4.2806 | 1.7398 | -0.71429 | 9.452 | 9.3459 | 9.2286 | 9.0357 | 8.7663 | 8.4367 | 8.1704 | 7.8429 | 7.449 | 5.2041 | 1.5286 | -3.4367 | 8.2806 | 8.1592 | 8.0296 | 7.8378 | 7.5643 | 7.2469 | 7.0051 | 6.6908 | 6.3112 | 4.3857 | 1.599 | -1.0847
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH PRIMARY | MINIMUM HEADROOM | SZ 15698 93141 | NO | NO | 5.496 | 3.8028 | 3.3998 | 2.6284 | 1.8039 | 0.92325 | -0.50022 | -2.089 | -3.6737 | -4.8461 | -11.1043 | -16.1278 | -18.8063 | 8.011 | 7.6906 | 7.0814 | 6.4273 | 5.712 | 4.7355 | 3.6151 | 2.4763 | 1.6559 | -2.8563 | -8.1268 | -21.1461 | 4.8232 | 4.4273 | 3.6845 | 2.8988 | 2.0579 | 0.73549 | -0.75328 | -2.237 | -3.3033 | -8.7829 | -13.1094 | -15.3298
|  | CHRISTCHURCH PRIMARY | EE |  |  |  |  | 3.8028 | 3.3998 | 2.6284 | 1.8039 | 0.92325 | -0.50022 | -2.089 | -3.6737 | -4.8461 | -10.8645 | -15.2523 | -18.3329 | 8.011 | 7.6906 | 7.0814 | 6.4273 | 5.712 | 4.7355 | 3.6151 | 2.4763 | 1.6559 | -2.8563 | -7.5563 | -14.3451 | 4.8232 | 4.4273 | 3.6845 | 2.8988 | 2.0579 | 0.73549 | -0.75328 | -2.237 | -3.3033 | -8.6604 | -12.3594 | -14.9584
|  | CHRISTCHURCH PRIMARY | HT |  |  |  |  | 4.2477 | 3.6151 | 2.9467 | 2.6232 | 1.961 | 0.71815 | -0.63287 | -2.0635 | -3.5349 | -11.1043 | -16.1278 | -18.8063 | 8.5722 | 8.1579 | 7.7028 | 7.563 | 7.1222 | 6.4518 | 5.6957 | 4.8845 | 4.0426 | 0.0038612 | -2.2982 | -3.4114 | 5.3498 | 4.7263 | 4.0641 | 3.7794 | 3.1314 | 1.9957 | 0.74774 | -0.56247 | -1.9104 | -8.7829 | -13.1094 | -15.3298
|  | CHRISTCHURCH PRIMARY | HE |  |  |  |  | 4.2865 | 3.6916 | 3.06 | 2.7743 | 2.1518 | 1.1324 | -0.010424 | -1.2094 | -2.4655 | -8.9839 | -13.4584 | -15.4308 | 8.4559 | 7.9743 | 7.4569 | 7.2345 | 6.7049 | 5.9896 | 5.1722 | 4.2937 | 3.3528 | -1.8961 | -6.7768 | -13.0961 | 5.3753 | 4.7845 | 4.1549 | 3.9049 | 3.2926 | 2.3437 | 1.2804 | 0.17121 | -0.9941 | -6.9329 | -10.7359 | -12.3676
|  | CHRISTCHURCH PRIMARY | CF |  |  |  |  | 4.7355 | 4.4039 | 4.0304 | 3.6447 | 3.5773 | 3.1763 | 2.6732 | 2.1447 | 1.5865 | -2.5604 | -7.1829 | -11.3859 | 8.6518 | 8.3059 | 7.9069 | 7.4824 | 7.2886 | 6.7712 | 6.1569 | 5.5028 | 4.7967 | -0.29104 | -8.1268 | -21.1461 | 5.7794 | 5.4396 | 5.0488 | 4.6539 | 4.6069 | 4.2181 | 3.7426 | 3.2396 | 2.709 | -1.1829 | -5.3421 | -9.0553
LALEHAM GSP | EAST BEDFONT BSP | CHURCH ROAD PRIMARY | MINIMUM HEADROOM | TQ 06820 71722 | NO | NO | 1.681 | 0.1199 | -0.525 | -0.73622 | -1.2893 | -1.8801 | -2.7954 | -4.0577 | -5.2148 | -5.9342 | -9.9128 | -13.2964 | -15.2923 | 2.876 | 2.3209 | 2.1658 | 1.6944 | 1.1862 | 0.50663 | -0.38418 | -1.2444 | -1.824 | -5.2597 | -10.9485 | -23.0556 | 0.31429 | -0.31837 | -0.44286 | -0.98163 | -1.5592 | -2.399 | -3.5388 | -4.599 | -5.2398 | -8.7082 | -11.6398 | -13.2347
|  | CHURCH ROAD PRIMARY | EE |  |  |  |  | 0.1199 | -0.525 | -0.73622 | -1.2893 | -1.8801 | -2.7954 | -4.0577 | -5.2148 | -5.9342 | -9.7505 | -12.6893 | -15.1087 | 2.876 | 2.3209 | 2.1658 | 1.6944 | 1.1862 | 0.50663 | -0.38418 | -1.2444 | -1.824 | -5.2597 | -9.2505 | -15.5046 | 0.31429 | -0.31837 | -0.44286 | -0.98163 | -1.5592 | -2.399 | -3.5388 | -4.599 | -5.2398 | -8.6327 | -11.1367 | -13.1092
|  | CHURCH ROAD PRIMARY | HT |  |  |  |  | 0.30459 | -0.068878 | -0.49337 | -0.98622 | -1.1628 | -1.9638 | -3.0709 | -4.1087 | -5.0311 | -9.9128 | -13.2964 | -15.2923 | 3.1954 | 2.9495 | 2.6617 | 2.3332 | 2.275 | 1.8423 | 1.2383 | 0.65765 | 0.11684 | -2.524 | -4.0954 | -4.9005 | 0.61735 | 0.2551 | -0.17449 | -0.64694 | -0.77245 | -1.5041 | -2.4878 | -3.4265 | -4.2786 | -8.7082 | -11.6398 | -13.2347
|  | CHURCH ROAD PRIMARY | HE |  |  |  |  | 0.42092 | -0.032143 | -0.43827 | -0.90765 | -1.0679 | -1.7281 | -2.7056 | -3.6148 | -4.4066 | -8.6801 | -11.7464 | -13.2179 | 3.1546 | 2.7617 | 2.4015 | 1.9934 | 1.8321 | 1.324 | 0.62704 | -0.068878 | -0.74031 | -4.7515 | -8.9148 | -14.8168 | 0.7 | 0.27449 | -0.13673 | -0.59082 | -0.7 | -1.3102 | -2.1816 | -3.0092 | -3.751 | -7.651 | -10.301 | -11.451
|  | CHURCH ROAD PRIMARY | CF |  |  |  |  | 1.0342 | 0.74949 | 0.38724 | 0.042347 | -0.33929 | -0.35765 | -0.89745 | -1.375 | -1.7362 | -4.5699 | -7.6434 | -10.5036 | 3.4393 | 3.1311 | 2.7566 | 2.3934 | 1.9638 | 1.7628 | 1.176 | 0.59337 | 0.034184 | -4.1495 | -10.9485 | -23.0556 | 1.1929 | 0.88265 | 0.54796 | 0.21122 | -0.15714 | -0.1 | -0.58469 | -1.0327 | -1.398 | -4.0418 | -6.7235 | -9.2561
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN PRIMARY | MINIMUM HEADROOM | SP 02761 00827 | NO | NO | 11.973 | 14.9846 | 14.6469 | 14.0244 | 13.4948 | 11.7836 | 10.6662 | 9.3877 | 6.2224 | 3.756 | -3.4501 | -10.1991 | -17.3542 | 17.9489 | 17.7234 | 16.9724 | 16.506 | 14.5775 | 13.4785 | 12.2367 | 8.5887 | 5.8785 | -0.68069 | -8.4633 | -19.2164 | 14.1928 | 13.9295 | 13.1458 | 12.6877 | 10.7479 | 9.5132 | 8.1183 | 4.3367 | 1.4611 | -5.9317 | -13.4113 | -21.9991
|  | CIRENCESTER TOWN PRIMARY | EE |  |  |  |  | 14.9846 | 14.6469 | 14.2469 | 13.7958 | 13.0816 | 12.104 | 11.3775 | 10.0693 | 9.1397 | 4.0203 | -4.8776 | -9.0756 | 17.9489 | 17.7367 | 17.4448 | 17.1101 | 16.3999 | 15.5152 | 15.002 | 13.7489 | 12.953 | 8.352 | -2.4552 | -8.7725 | 14.1928 | 13.9295 | 13.603 | 13.2397 | 12.4938 | 11.4581 | 10.7703 | 9.3469 | 8.402 | 3.0652 | -7.4205 | -11.9246
|  | CIRENCESTER TOWN PRIMARY | HT |  |  |  |  | 15.2622 | 14.8928 | 14.3448 | 14.0122 | 12.6152 | 11.5183 | 10.2428 | 9.605 | 8.1316 | 1.555 | -7.5317 | -13.7797 | 18.152 | 17.855 | 17.354 | 17.1316 | 15.5928 | 14.5275 | 13.2856 | 12.7918 | 11.353 | 5.6897 | -3.3419 | -9.746 | 14.3713 | 14.0071 | 13.4377 | 13.1856 | 11.6152 | 10.3407 | 8.8826 | 8.3713 | 6.753 | -0.21437 | -10.4644 | -17.5736
|  | CIRENCESTER TOWN PRIMARY | HE |  |  |  |  | 15.2264 | 14.7877 | 14.0244 | 13.4948 | 11.7836 | 10.6662 | 9.3877 | 6.2224 | 3.756 | -3.4501 | -10.1991 | -17.3542 | 18.1111 | 17.7234 | 16.9724 | 16.506 | 14.5775 | 13.4785 | 12.2367 | 8.5887 | 5.8785 | -0.68069 | -8.4633 | -19.2164 | 14.3764 | 13.9509 | 13.1458 | 12.6877 | 10.7479 | 9.5132 | 8.1183 | 4.3367 | 1.4611 | -5.9317 | -13.4113 | -21.9991
|  | CIRENCESTER TOWN PRIMARY | CF |  |  |  |  | 15.5173 | 15.3775 | 15.2183 | 14.8989 | 14.5234 | 14.0469 | 13.5622 | 13.0193 | 12.3775 | 8.206 | 2.9846 | -1.7787 | 18.2213 | 18.0969 | 17.9673 | 17.6438 | 17.2744 | 16.7683 | 16.3111 | 15.8122 | 15.2009 | 10.905 | 3.8979 | -5.4123 | 14.5836 | 14.455 | 14.3356 | 14.0193 | 13.6785 | 13.2009 | 12.7754 | 12.2775 | 11.5887 | 7.1234 | 1.6101 | -3.2991
IVER 132KV GSP | CIPPENHAM BSP | CLARENCE ROAD PRIMARY | MINIMUM HEADROOM | SU 95654 76652 | NO | YES | 12.271 | 17.9929 | 17.0613 | 15.7266 | 14.1827 | 12.696 | 10.799 | 8.6388 | 6.6103 | 5.0266 | -1.9152 | -6.7408 | -8.2408 | 23.3241 | 22.667 | 21.7792 | 20.7833 | 19.7599 | 18.5497 | 17.1384 | 15.769 | 14.6109 | 8.6537 | 2.0558 | -14.3952 | 16.6892 | 15.8739 | 14.7168 | 13.3954 | 12.078 | 10.3739 | 8.3535 | 6.429 | 4.9444 | -1.4169 | -5.6424 | -6.9189
|  | CLARENCE ROAD PRIMARY | EE |  |  |  |  | 17.9929 | 17.0613 | 15.7266 | 14.1827 | 12.696 | 10.799 | 8.6388 | 6.6103 | 5.0266 | -1.9152 | -5.8265 | -6.9091 | 23.3241 | 22.667 | 21.7792 | 20.7833 | 19.7599 | 18.5497 | 17.1384 | 15.769 | 14.6109 | 8.6537 | 3.1313 | -4.533 | 16.6892 | 15.8739 | 14.7168 | 13.3954 | 12.078 | 10.3739 | 8.3535 | 6.429 | 4.9444 | -1.4169 | -4.8516 | -5.7516
|  | CLARENCE ROAD PRIMARY | HT |  |  |  |  | 18.5286 | 17.4929 | 16.2348 | 15.1878 | 14.0021 | 12.5266 | 10.747 | 8.9909 | 7.1909 | -1.505 | -6.7408 | -8.2408 | 23.8782 | 23.2354 | 22.4986 | 21.9119 | 21.1986 | 20.366 | 19.3415 | 18.2986 | 17.2384 | 12.4925 | 9.7813 | 8.9323 | 17.2229 | 16.2913 | 15.1821 | 14.2801 | 13.2005 | 11.8546 | 10.2382 | 8.6321 | 6.9913 | -0.95463 | -5.6424 | -6.9189
|  | CLARENCE ROAD PRIMARY | HE |  |  |  |  | 18.548 | 17.5521 | 16.4358 | 15.6062 | 14.4939 | 13.0899 | 11.3674 | 9.8144 | 8.2205 | 0.99394 | -2.8928 | -4.101 | 23.716 | 22.9874 | 22.2088 | 21.6446 | 20.8241 | 19.8782 | 18.7119 | 17.5986 | 16.4139 | 10.116 | 4.5017 | -3.1289 | 17.2372 | 16.3362 | 15.3392 | 14.6423 | 13.626 | 12.3525 | 10.8005 | 9.3801 | 7.9168 | 1.2739 | -2.2822 | -3.3199
|  | CLARENCE ROAD PRIMARY | CF |  |  |  |  | 19.3001 | 18.696 | 18.0205 | 17.0756 | 16.4837 | 15.695 | 14.8439 | 14.149 | 13.3888 | 8.047 | 2.5674 | -2.405 | 24.0782 | 23.519 | 22.9282 | 22.2007 | 21.667 | 20.8946 | 20.0446 | 19.2486 | 18.3731 | 11.916 | 2.0558 | -14.3952 | 17.8933 | 17.3392 | 16.7362 | 15.928 | 15.4566 | 14.7668 | 14.0219 | 13.3974 | 12.7127 | 7.6597 | 2.6882 | -1.7301
MELKSHAM GSP | CHIPPENHAM BSP | COCKLEBURY PRIMARY | MINIMUM HEADROOM | ST 92447 73890 | NO | YES | 6.767 | 27.827 | 26.928 | 26.0413 | 25.4474 | 24.4719 | 23.2913 | 22.1393 | 21.0964 | 20.3148 | 16.8474 | 13.8495 | 11.9893 | 32.8882 | 32.224 | 31.6127 | 31.3168 | 30.6882 | 29.9454 | 29.1638 | 28.4168 | 27.8852 | 25.3352 | 22.3127 | 14.6933 | 27.2607 | 26.4301 | 25.6291 | 25.2658 | 24.3984 | 23.3525 | 22.3015 | 21.3372 | 20.6566 | 17.7964 | 15.2719 | 13.7464
|  | COCKLEBURY PRIMARY | EE |  |  |  |  | 27.827 | 26.928 | 26.0413 | 25.4474 | 24.4719 | 23.2913 | 22.1393 | 21.0964 | 20.3148 | 17.0495 | 14.4678 | 12.3209 | 32.8882 | 32.224 | 31.6127 | 31.3168 | 30.6882 | 29.9454 | 29.1638 | 28.4168 | 27.8852 | 25.3352 | 22.5872 | 18.5015 | 27.2607 | 26.4301 | 25.6291 | 25.2658 | 24.3984 | 23.3525 | 22.3015 | 21.3372 | 20.6566 | 17.8913 | 15.8015 | 13.9944
|  | COCKLEBURY PRIMARY | HT |  |  |  |  | 27.9556 | 27.1444 | 26.5066 | 25.6984 | 24.7546 | 23.8882 | 22.875 | 21.9546 | 21.0331 | 16.8474 | 13.8495 | 11.9893 | 33.1974 | 32.6678 | 32.3046 | 31.826 | 31.2882 | 30.978 | 30.4219 | 29.8811 | 29.3209 | 26.9617 | 25.5944 | 24.825 | 27.5127 | 26.7923 | 26.2505 | 25.5362 | 24.7066 | 24.1413 | 23.2454 | 22.3995 | 21.5403 | 17.7964 | 15.2719 | 13.7464
|  | COCKLEBURY PRIMARY | HE |  |  |  |  | 28.0566 | 27.3117 | 26.6638 | 25.7648 | 24.8831 | 24.1638 | 23.3005 | 22.5229 | 21.7546 | 18.2923 | 15.6382 | 14.2495 | 33.1699 | 32.6423 | 32.2189 | 31.626 | 31.0658 | 30.7301 | 30.1474 | 29.5791 | 28.9903 | 26.0352 | 23.2158 | 19.4393 | 27.5882 | 26.9209 | 26.378 | 25.6127 | 24.8382 | 24.3709 | 23.6015 | 22.878 | 22.1464 | 19.0362 | 16.8954 | 15.727
|  | COCKLEBURY PRIMARY | CF |  |  |  |  | 28.3117 | 27.7933 | 27.2862 | 26.6362 | 25.9199 | 25.2954 | 24.7148 | 24.5648 | 24.0811 | 21.5719 | 19.1229 | 16.8117 | 33.2719 | 32.8658 | 32.4842 | 32.0209 | 31.5199 | 31.0087 | 30.4801 | 30.2954 | 29.8087 | 26.7872 | 22.3127 | 14.6933 | 27.7893 | 27.3311 | 26.874 | 26.3525 | 25.7311 | 25.1658 | 24.6209 | 24.6505 | 24.2117 | 21.8668 | 19.725 | 17.7944
MELKSHAM GSP | FROME BSP | CODFORD PRIMARY | MINIMUM HEADROOM | ST 97372 39559 | YES | NO | 1.735 | 1.1679 | 1.1107 | 1.0281 | 0.94439 | 0.84745 | 0.77806 | 0.64439 | 0.50663 | 0.46786 | 0.21173 | 0.10255 | 0.039286 | 0.19694 | 0.17755 | 0.15306 | 0.12245 | 0.090816 | 0.065306 | 0.013265 | -0.087755 | -0.11531 | -0.26429 | -0.60306 | -1.3582 | 0.54592 | 0.49184 | 0.41327 | 0.33265 | 0.23776 | 0.16837 | 0.037755 | -0.097959 | -0.13673 | -0.37653 | -0.47551 | -0.53061
|  | CODFORD PRIMARY | EE |  |  |  |  | 1.1679 | 1.1107 | 1.0281 | 0.94439 | 0.84745 | 0.77806 | 0.64439 | 0.50663 | 0.46786 | 0.21173 | 0.10255 | 0.042347 | 0.19694 | 0.17755 | 0.15306 | 0.12245 | 0.090816 | 0.065306 | 0.013265 | -0.087755 | -0.11531 | -0.26429 | -0.48265 | -0.85204 | 0.54592 | 0.49184 | 0.41327 | 0.33265 | 0.23776 | 0.16837 | 0.037755 | -0.097959 | -0.13673 | -0.37653 | -0.47551 | -0.53061
|  | CODFORD PRIMARY | HT |  |  |  |  | 1.2158 | 1.1709 | 1.1138 | 1.0719 | 1.0117 | 0.93827 | 0.84847 | 0.78929 | 0.69541 | 0.26684 | 0.11173 | 0.039286 | 0.22143 | 0.2051 | 0.18878 | 0.17551 | 0.15714 | 0.13469 | 0.10204 | 0.084694 | 0.055102 | -0.16531 | -0.20408 | -0.20408 | 0.60408 | 0.55816 | 0.49796 | 0.46429 | 0.39694 | 0.32449 | 0.23163 | 0.17755 | 0.082653 | -0.32755 | -0.47041 | -0.5051
|  | CODFORD PRIMARY | HE |  |  |  |  | 1.2158 | 1.1709 | 1.1168 | 1.076 | 1.0179 | 0.94949 | 0.86071 | 0.80357 | 0.71684 | 0.2648 | 0.15255 | 0.09949 | 0.21633 | 0.19898 | 0.18061 | 0.16531 | 0.14184 | 0.11531 | 0.081633 | 0.058163 | 0.022449 | -0.22245 | -0.45408 | -0.82041 | 0.60408 | 0.55714 | 0.50102 | 0.46735 | 0.40408 | 0.33469 | 0.24592 | 0.19388 | 0.10408 | -0.32347 | -0.42143 | -0.46735
|  | CODFORD PRIMARY | CF |  |  |  |  | 1.226 | 1.1923 | 1.1566 | 1.1138 | 1.0638 | 1.0321 | 0.97398 | 0.92194 | 0.86276 | 0.54439 | 0.32398 | 0.16582 | 0.22041 | 0.20714 | 0.19184 | 0.17449 | 0.15408 | 0.1398 | 0.11224 | 0.084694 | 0.058163 | -0.15306 | -0.60306 | -1.3582 | 0.60918 | 0.57857 | 0.54286 | 0.49592 | 0.4449 | 0.42041 | 0.35816 | 0.30306 | 0.23878 | -0.067347 | -0.27245 | -0.41633
IVER 132KV GSP | DENHAM BSP | COKES LANE PRIMARY | MINIMUM HEADROOM | SU 99240 97483 | NO | YES | 0.653 | 4.2046 | 3.9689 | 3.7005 | 3.5281 | 3.3281 | 3.0393 | 2.7107 | 2.6617 | 2.3658 | 1.2301 | 0.30153 | -0.21684 | 5.576 | 5.4138 | 5.2189 | 5.0791 | 4.9026 | 4.6821 | 4.425 | 4.4832 | 4.3444 | 3.4944 | 1.9719 | -1.1638 | 5.3531 | 5.1286 | 4.8561 | 4.6816 | 4.4531 | 4.1541 | 3.8092 | 3.9398 | 3.6408 | 2.7918 | 2.0112 | 1.5776
|  | COKES LANE PRIMARY | EE |  |  |  |  | 4.2046 | 3.9689 | 3.7005 | 3.5281 | 3.3281 | 3.0393 | 2.7107 | 2.726 | 2.5321 | 1.4077 | 0.525 | -0.13622 | 5.576 | 5.4138 | 5.2189 | 5.0791 | 4.9026 | 4.6821 | 4.425 | 4.4832 | 4.3444 | 3.4944 | 2.424 | 0.76378 | 5.3531 | 5.1286 | 4.8561 | 4.6816 | 4.4531 | 4.1541 | 3.8092 | 3.9531 | 3.7878 | 2.9224 | 2.2082 | 1.649
|  | COKES LANE PRIMARY | HT |  |  |  |  | 4.274 | 4.0362 | 3.7862 | 3.6383 | 3.4617 | 3.1974 | 2.9485 | 2.6617 | 2.3658 | 1.2301 | 0.30153 | -0.21684 | 5.7087 | 5.577 | 5.4311 | 5.3485 | 5.2352 | 5.0801 | 4.9495 | 4.7689 | 4.5821 | 4.1403 | 3.7699 | 3.5699 | 5.4786 | 5.2633 | 5.0306 | 4.8929 | 4.7071 | 4.448 | 4.2286 | 3.9398 | 3.6408 | 2.7918 | 2.0112 | 1.5776
|  | COKES LANE PRIMARY | HE |  |  |  |  | 4.2903 | 4.0617 | 3.826 | 3.6883 | 3.523 | 3.3179 | 3.1291 | 2.9046 | 2.6689 | 1.7566 | 0.87704 | 0.44643 | 5.677 | 5.524 | 5.3628 | 5.2597 | 5.1219 | 4.9556 | 4.8097 | 4.6087 | 4.4015 | 3.6342 | 2.5556 | 0.97908 | 5.4867 | 5.2806 | 5.0561 | 4.9255 | 4.75 | 4.5337 | 4.3582 | 4.1112 | 3.8531 | 3.2214 | 2.5133 | 2.152
|  | COKES LANE PRIMARY | CF |  |  |  |  | 4.3699 | 4.2087 | 4.0362 | 3.9526 | 3.8434 | 3.7628 | 3.6679 | 3.5964 | 3.4801 | 2.9485 | 2.1291 | 1.2842 | 5.6964 | 5.575 | 5.4403 | 5.3577 | 5.2342 | 5.1015 | 4.9423 | 4.8148 | 4.6383 | 3.7362 | 1.9719 | -1.1638 | 5.5449 | 5.398 | 5.2357 | 5.1531 | 5.0327 | 4.9224 | 4.7878 | 4.7082 | 4.5643 | 4.1276 | 3.4429 | 2.8122
LOVEDEAN GSP | PORTSMOUTH BSP | COLLEGE PARK PRIMARY | MINIMUM HEADROOM | SU 65893 02686 | NO | YES | 0.626 | 4.4 | 4.0061 | 3.6 | 3.1051 | 2.5622 | 2.0908 | 1.2255 | 0.36531 | -0.32143 | -2.9173 | -4.7265 | -4.702 | 6.198 | 5.8224 | 5.4306 | 4.948 | 4.4173 | 4.0265 | 3.302 | 2.5612 | 1.9429 | -1.3969 | -7.7265 | -21.2245 | 4.5602 | 4.2102 | 3.849 | 3.3643 | 2.8378 | 2.4112 | 1.5918 | 0.77653 | 0.13571 | -2.2378 | -3.8245 | -3.7765
|  | COLLEGE PARK PRIMARY | EE |  |  |  |  | 4.4 | 4.0061 | 3.6 | 3.1051 | 2.5622 | 2.0908 | 1.2255 | 0.36531 | -0.32143 | -2.9173 | -4.1633 | -3.798 | 6.198 | 5.8224 | 5.4306 | 4.948 | 4.4173 | 4.0265 | 3.302 | 2.5612 | 1.9429 | -1.3969 | -5.2367 | -11.3163 | 4.5602 | 4.2102 | 3.849 | 3.3643 | 2.8378 | 2.4112 | 1.5918 | 0.77653 | 0.13571 | -2.2378 | -3.3214 | -3.0061
|  | COLLEGE PARK PRIMARY | HT |  |  |  |  | 4.648 | 4.3959 | 4.1173 | 3.7694 | 3.4143 | 2.7898 | 2.0796 | 1.3357 | 0.90102 | -2.6867 | -4.7265 | -4.702 | 6.5551 | 6.348 | 6.1449 | 5.8888 | 5.6276 | 5.2398 | 4.7908 | 4.3051 | 4.0806 | 1.8582 | 0.61735 | 0.48367 | 4.8112 | 4.5561 | 4.3082 | 4.002 | 3.6918 | 3.1092 | 2.4429 | 1.7378 | 1.351 | -1.9724 | -3.8245 | -3.7765
|  | COLLEGE PARK PRIMARY | HE |  |  |  |  | 4.6582 | 4.4296 | 4.1888 | 3.8796 | 3.5755 | 3.0163 | 2.3786 | 1.7184 | 1.3898 | -1.1204 | -2.2898 | -2.4531 | 6.4306 | 6.1612 | 5.8959 | 5.5622 | 5.2173 | 4.7347 | 4.1755 | 3.5745 | 3.2224 | -0.22347 | -4.1112 | -10.3194 | 4.8194 | 4.5867 | 4.3673 | 4.0929 | 3.8255 | 3.3204 | 2.7235 | 2.1 | 1.8102 | -0.54184 | -1.5837 | -1.701
|  | COLLEGE PARK PRIMARY | CF |  |  |  |  | 4.8847 | 4.7622 | 4.651 | 4.4765 | 4.2857 | 4.0939 | 3.8071 | 3.4969 | 3.1663 | 1.5388 | -0.78163 | -2.9408 | 6.5296 | 6.2969 | 6.0673 | 5.7735 | 5.4173 | 5.0163 | 4.5112 | 3.9663 | 3.3796 | -0.45102 | -7.7265 | -21.2245 | 5.0337 | 4.902 | 4.7898 | 4.6388 | 4.4724 | 4.3071 | 4.0418 | 3.7408 | 3.4204 | 1.8724 | -0.25204 | -2.1806
EALING GSP |  | COPLEY DENE PRIMARY | MINIMUM HEADROOM | TQ 17445 80798 | NO | NO | 13.892 | 1.0481 | 0.053249 | -0.78247 | 38.4925 | 37.0629 | 35.2742 | 33.2691 | 31.2803 | 29.7211 | 22.1231 | 15.5303 | 12.1772 | 7.3247 | 6.4339 | 5.8532 | 47.6089 | 46.4313 | 45.0946 | 43.5344 | 41.9629 | 40.7762 | 34.5476 | 26.3456 | 4.6191 | 0.80376 | -0.19318 | -0.91257 | 39.5313 | 38.1507 | 36.4691 | 34.5374 | 32.6231 | 31.1823 | 24.5089 | 18.7119 | 15.7956
|  | COPLEY DENE PRIMARY | EE |  |  |  |  | 1.0481 | 0.053249 | -0.78247 | 38.4925 | 37.0629 | 35.2742 | 33.2691 | 31.2803 | 29.7211 | 22.1231 | 16.6946 | 12.8507 | 7.3247 | 6.4339 | 5.8532 | 47.6089 | 46.4313 | 45.0946 | 43.5344 | 41.9629 | 40.7762 | 34.5476 | 27.2925 | 16.064 | 0.80376 | -0.19318 | -0.91257 | 39.5313 | 38.1507 | 36.4691 | 34.5374 | 32.6231 | 31.1823 | 24.5089 | 19.768 | 16.3436
|  | COPLEY DENE PRIMARY | HT |  |  |  |  | 1.7094 | 1.0186 | 0.098147 | 39.6385 | 38.9078 | 37.4976 | 35.9323 | 34.2987 | 32.6058 | 22.8578 | 15.5303 | 12.1772 | 8.1196 | 7.64 | 7.0094 | 49.1201 | 48.767 | 47.9456 | 46.9844 | 45.966 | 44.8874 | 39.4885 | 36.065 | 34.814 | 1.5334 | 0.88029 | 0.017024 | 40.7374 | 40.1099 | 38.8129 | 37.3466 | 35.8099 | 34.2068 | 25.3211 | 18.7119 | 15.7956
|  | COPLEY DENE PRIMARY | HE |  |  |  |  | 1.7288 | 1.1084 | 0.26856 | 39.9017 | 39.217 | 37.9568 | 36.5691 | 35.1466 | 33.6803 | 26.2834 | 21.3027 | 19.5211 | 7.9492 | 7.4012 | 6.7114 | 48.7558 | 48.3027 | 47.4007 | 46.3568 | 45.2517 | 44.0772 | 37.4405 | 30.1364 | 19.815 | 1.5476 | 0.95784 | 0.17213 | 40.9864 | 40.4201 | 39.268 | 37.9752 | 36.6415 | 35.265 | 28.5272 | 24.1119 | 22.5701
|  | COPLEY DENE PRIMARY | CF |  |  |  |  | 2.3073 | 1.9277 | 1.443 | 41.4436 | 40.8027 | 40.618 | 40.0078 | 39.3334 | 38.6262 | 34.0129 | 28.8701 | 23.6119 | 8.2155 | 7.7369 | 7.2186 | 49.4099 | 48.6629 | 48.2834 | 47.4242 | 46.4885 | 45.4864 | 38.4915 | 26.3456 | 4.6191 | 2.0487 | 1.6548 | 1.1976 | 42.3374 | 41.7129 | 41.5946 | 40.9844 | 40.3068 | 39.5946 | 35.1487 | 30.5242 | 26.015
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | CORDWALLIS PRIMARY | MINIMUM HEADROOM | SU 88285 81857 | NO | NO | 7.888 | 6.8944 | 6.2148 | 5.8005 | 5.0301 | 4.4127 | 3.5668 | 2.6097 | 1.6188 | 0.90762 | -2.1526 | -4.3995 | -4.7679 | 9.9433 | 9.4158 | 9.1617 | 8.5944 | 8.075 | 7.4311 | 6.6831 | 5.9015 | 5.3535 | 2.5239 | -1.775 | -12.0036 | 6.8984 | 6.279 | 5.9352 | 5.2403 | 4.6413 | 3.8331 | 2.9056 | 1.9535 | 1.3097 | -1.3505 | -3.2965 | -3.5883
|  | CORDWALLIS PRIMARY | EE |  |  |  |  | 6.8944 | 6.2148 | 5.8005 | 5.0301 | 4.4127 | 3.5668 | 2.6097 | 1.6188 | 0.90762 | -2.1526 | -4.0444 | -3.925 | 9.9433 | 9.4158 | 9.1617 | 8.5944 | 8.075 | 7.4311 | 6.6831 | 5.9015 | 5.3535 | 2.5239 | -0.55054 | -4.9261 | 6.8984 | 6.279 | 5.9352 | 5.2403 | 4.6413 | 3.8331 | 2.9056 | 1.9535 | 1.3097 | -1.3505 | -2.9883 | -2.873
|  | CORDWALLIS PRIMARY | HT |  |  |  |  | 7.2015 | 6.6382 | 6.0515 | 5.3454 | 4.7852 | 4.4444 | 3.7015 | 2.8893 | 2.0505 | -2.0067 | -4.3995 | -4.7679 | 10.328 | 9.979 | 9.6342 | 9.2076 | 8.827 | 8.7342 | 8.275 | 7.7699 | 7.2362 | 4.8209 | 3.575 | 3.2974 | 7.2076 | 6.7076 | 6.1944 | 5.5678 | 5.0444 | 4.7495 | 4.0617 | 3.3148 | 2.5403 | -1.1689 | -3.2965 | -3.5883
|  | CORDWALLIS PRIMARY | HE |  |  |  |  | 7.2923 | 6.8015 | 6.3015 | 5.7005 | 5.0352 | 4.6627 | 3.9893 | 3.2648 | 2.5158 | -0.61789 | -2.3465 | -2.7067 | 10.2597 | 9.876 | 9.5025 | 9.0454 | 8.5382 | 8.3393 | 7.8066 | 7.225 | 6.6046 | 3.3658 | 0.27905 | -4.2852 | 7.2739 | 6.8321 | 6.3903 | 5.8484 | 5.2464 | 4.9403 | 4.3117 | 3.6393 | 2.9444 | 0.064763 | -1.4444 | -1.7261
|  | CORDWALLIS PRIMARY | CF |  |  |  |  | 7.626 | 7.3066 | 6.9811 | 6.5842 | 6.1413 | 5.778 | 5.7933 | 5.4862 | 5.1474 | 2.7882 | 0.03109 | -2.5097 | 10.4137 | 10.1066 | 9.8035 | 9.4331 | 9.0025 | 8.5576 | 8.4107 | 7.9505 | 7.4505 | 3.8709 | -1.775 | -12.0036 | 7.578 | 7.2984 | 7.0117 | 6.6576 | 6.2627 | 5.9158 | 5.9576 | 5.6607 | 5.325 | 3.0321 | 0.60966 | -1.5934
MANNINGTON GSP | LYTCHETT BSP | CORFE MULLEN PRIMARY | MINIMUM HEADROOM | SY 98583 96071 | NO | NO | 2.919 | 15.8168 | 15.2536 | 14.974 | 14.4107 | 13.8005 | 12.6882 | 11.4984 | 10.5076 | 9.8821 | 5.1831 | 2.0403 | 0.326 | 15.8362 | 15.3984 | 15.3036 | 14.8689 | 14.3546 | 13.6546 | 12.874 | 12.1699 | 11.7393 | 8.8678 | 4.7219 | -4.5475 | 15.4168 | 14.8913 | 14.7301 | 14.2127 | 13.5913 | 12.5954 | 11.5138 | 10.5852 | 10.0372 | 6.1056 | 3.4331 | 2.0127
|  | CORFE MULLEN PRIMARY | EE |  |  |  |  | 15.8168 | 15.2536 | 15.0811 | 14.5148 | 13.8005 | 12.6882 | 11.4984 | 10.5076 | 9.8821 | 5.7587 | 2.7331 | 0.58008 | 15.8362 | 15.3984 | 15.3036 | 14.8689 | 14.3546 | 13.6546 | 12.874 | 12.1699 | 11.7393 | 8.8678 | 5.6025 | 0.65355 | 15.4168 | 14.8913 | 14.7668 | 14.2474 | 13.5913 | 12.5954 | 11.5138 | 10.5852 | 10.0372 | 6.5505 | 4.0301 | 2.225
|  | CORFE MULLEN PRIMARY | HT |  |  |  |  | 15.9525 | 15.4515 | 14.974 | 14.4107 | 14.0209 | 12.9464 | 11.9056 | 11.0791 | 10.2311 | 5.1831 | 2.0403 | 0.326 | 16.1372 | 15.8433 | 15.5454 | 15.1974 | 15.0974 | 14.577 | 14.0433 | 13.5872 | 13.1138 | 10.6393 | 9.3801 | 8.6913 | 15.6138 | 15.1729 | 14.7301 | 14.2127 | 13.9209 | 12.9923 | 12.077 | 11.3127 | 10.5311 | 6.1056 | 3.4331 | 2.0127
|  | CORFE MULLEN PRIMARY | HE |  |  |  |  | 16.0668 | 15.6709 | 15.2638 | 14.7607 | 14.4362 | 13.5617 | 12.6291 | 11.9046 | 11.2382 | 6.9862 | 4.0515 | 2.6382 | 16.0913 | 15.7923 | 15.4648 | 15.0719 | 14.926 | 14.3852 | 13.7872 | 13.2536 | 12.728 | 9.4087 | 6.1658 | 1.5015 | 15.6984 | 15.3413 | 14.9587 | 14.4964 | 14.2556 | 13.4974 | 12.676 | 12.0138 | 11.3995 | 7.6321 | 5.1852 | 4.0107
|  | CORFE MULLEN PRIMARY | CF |  |  |  |  | 16.3403 | 16.128 | 15.977 | 15.7158 | 15.3423 | 15.2291 | 14.8444 | 14.4525 | 14.0423 | 10.6117 | 7.7811 | 5.2117 | 16.2036 | 15.9597 | 15.7525 | 15.4658 | 15.0882 | 14.9525 | 14.5158 | 14.0678 | 13.5791 | 9.9056 | 4.7219 | -4.5475 | 15.9423 | 15.7301 | 15.5719 | 15.3291 | 14.9811 | 14.9352 | 14.5923 | 14.225 | 13.8362 | 10.7484 | 8.3117 | 6.124
MELKSHAM GSP | NORRINGTON BSP | CORSHAM PRIMARY | MINIMUM HEADROOM | ST 86766 69583 | NO | YES | 1.872 | 2.9126 | 2.5248 | 2.0473 | 1.5514 | 1.4401 | 0.57176 | -0.41701 | -1.3231 | -2.0619 | -5.6905 | -8.5099 | -10.266 | 3.4371 | 3.1697 | 2.8371 | 2.4595 | 2.3809 | 1.6473 | 0.79727 | 0.03911 | -0.60171 | -3.3578 | -5.7588 | -10.164 | 2.7738 | 2.4554 | 2.0626 | 1.6463 | 1.5534 | 0.66972 | -0.3466 | -1.2588 | -2.0129 | -5.5762 | -8.3762 | -10.0415
|  | CORSHAM PRIMARY | EE |  |  |  |  | 2.9126 | 2.5248 | 2.0473 | 1.5514 | 1.4401 | 0.57176 | -0.41701 | -1.3231 | -2.0619 | -5.3752 | -7.5915 | -9.518 | 3.4371 | 3.1697 | 2.8371 | 2.4595 | 2.3809 | 1.6473 | 0.79727 | 0.03911 | -0.60171 | -3.3578 | -5.7588 | -9.2333 | 2.7738 | 2.4554 | 2.0626 | 1.6463 | 1.5534 | 0.66972 | -0.3466 | -1.2588 | -2.0129 | -5.2007 | -7.3782 | -9.2007
|  | CORSHAM PRIMARY | HT |  |  |  |  | 3.1463 | 2.8412 | 2.4616 | 2.1248 | 1.7371 | 0.88809 | 0.29319 | -0.53538 | -1.4201 | -5.6905 | -8.5099 | -10.266 | 3.6656 | 3.4891 | 3.2636 | 3.0718 | 2.836 | 2.1932 | 1.7279 | 1.1105 | 0.43401 | -2.5099 | -4.315 | -5.4058 | 2.9565 | 2.6983 | 2.382 | 2.0932 | 1.7616 | 0.91462 | 0.26156 | -0.55171 | -1.4201 | -5.5762 | -8.3762 | -10.0415
|  | CORSHAM PRIMARY | HE |  |  |  |  | 3.1442 | 2.8463 | 2.4707 | 2.1381 | 1.7544 | 1.0728 | 0.61054 | -0.022114 | -0.69048 | -4.2956 | -6.6966 | -8.0854 | 3.6044 | 3.3901 | 3.1299 | 2.8942 | 2.6075 | 2.0565 | 1.6371 | 1.1483 | 0.60238 | -2.4762 | -5.0884 | -8.3517 | 2.9544 | 2.7024 | 2.386 | 2.0983 | 1.7677 | 1.1034 | 0.59829 | 0.0095184 | -0.61599 | -4.0844 | -6.4354 | -7.7803
|  | CORSHAM PRIMARY | CF |  |  |  |  | 3.3626 | 3.1677 | 2.9187 | 2.6809 | 2.4779 | 2.1371 | 1.6871 | 1.2534 | 1.1922 | -0.9466 | -3.1435 | -5.1109 | 3.7116 | 3.5493 | 3.3452 | 3.1381 | 2.9391 | 2.5565 | 2.0493 | 1.5656 | 1.3636 | -1.0997 | -4.5568 | -10.164 | 3.0922 | 2.982 | 2.7942 | 2.5952 | 2.4248 | 2.0952 | 1.6483 | 1.2289 | 1.1309 | -0.91905 | -2.9017 | -4.6905
EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD PRIMARY | MINIMUM HEADROOM | SP 59021 31128 | YES | YES | 0.606 | -1.1544 | -1.2544 | -1.3728 | -1.4595 | -1.5922 | -1.7646 | -1.9085 | -2.0973 | -2.2065 | -2.7493 | -2.985 | -3.2116 | -1.2814 | -1.3579 | -1.4467 | -1.512 | -1.6089 | -1.7354 | -1.8405 | -1.9803 | -2.0558 | -2.3905 | -2.6987 | -3.5875 | -1.2558 | -1.3446 | -1.4518 | -1.5303 | -1.6477 | -1.8007 | -1.9375 | -2.1069 | -2.216 | -2.7365 | -2.9548 | -3.1589
|  | COTTISFORD PRIMARY | EE |  |  |  |  | -1.1544 | -1.2544 | -1.3728 | -1.4595 | -1.5922 | -1.7646 | -1.9085 | -2.0973 | -2.2065 | -2.7493 | -2.985 | -3.1279 | -1.2814 | -1.3579 | -1.4467 | -1.512 | -1.6089 | -1.7354 | -1.8405 | -1.9803 | -2.0558 | -2.3905 | -2.6538 | -3.0314 | -1.2558 | -1.3446 | -1.4518 | -1.5303 | -1.6477 | -1.8007 | -1.9375 | -2.1069 | -2.216 | -2.7365 | -2.9548 | -3.0793
|  | COTTISFORD PRIMARY | HT |  |  |  |  | -1.1034 | -1.1789 | -1.2483 | -1.3401 | -1.432 | -1.5728 | -1.685 | -1.8391 | -2.0003 | -2.6626 | -2.982 | -3.2116 | -1.2303 | -1.2773 | -1.3201 | -1.3803 | -1.4426 | -1.5293 | -1.5997 | -1.7028 | -1.8109 | -2.212 | -2.3742 | -2.4875 | -1.2089 | -1.2763 | -1.3395 | -1.4222 | -1.5069 | -1.6354 | -1.7395 | -1.8824 | -2.0293 | -2.6497 | -2.9497 | -3.1589
|  | COTTISFORD PRIMARY | HE |  |  |  |  | -1.1024 | -1.1758 | -1.2442 | -1.332 | -1.4258 | -1.5565 | -1.6667 | -1.8146 | -1.9718 | -2.686 | -2.9167 | -3.0207 | -1.2375 | -1.2885 | -1.3324 | -1.3977 | -1.463 | -1.5558 | -1.6263 | -1.7354 | -1.8548 | -2.3467 | -2.612 | -2.9701 | -1.2079 | -1.2732 | -1.3375 | -1.4171 | -1.5018 | -1.6212 | -1.7222 | -1.8609 | -2.0058 | -2.6763 | -2.8885 | -2.9783
|  | COTTISFORD PRIMARY | CF |  |  |  |  | -1.0738 | -1.133 | -1.1983 | -1.2493 | -1.3207 | -1.3942 | -1.486 | -1.5503 | -1.6524 | -2.183 | -2.6116 | -3.0197 | -1.216 | -1.2599 | -1.3099 | -1.3436 | -1.4007 | -1.462 | -1.5436 | -1.5916 | -1.6834 | -2.1722 | -2.6987 | -3.5875 | -1.1783 | -1.2314 | -1.2926 | -1.3405 | -1.4038 | -1.4712 | -1.5569 | -1.613 | -1.7069 | -2.1967 | -2.6038 | -2.9916
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | COURAGES PRIMARY | MINIMUM HEADROOM | SU 70990 69570 | NO | NO | 12.547 | 8.0186 | 6.6757 | 5.44 | 4.0492 | 2.4798 | -1.1049 | -3.0223 | -4.81 | -6.1988 | -18.2335 | -22.1886 | -22.3396 | 10.8737 | 9.8083 | 8.8839 | 7.841 | 6.6604 | 3.19 | 1.741 | 0.38794 | -0.67737 | -10.7202 | -13.8825 | -14.0692 | 7.3359 | 6.0298 | 4.8522 | 3.5216 | 2.0196 | -1.3304 | -3.1672 | -4.8794 | -6.2172 | -17.9059 | -21.7314 | -21.8733
|  | COURAGES PRIMARY | EE |  |  |  |  | 8.0186 | 6.6757 | 5.44 | 4.0492 | 2.4798 | -1.1049 | -3.0223 | -4.81 | -6.1988 | -13.6896 | -14.7335 | -14.7784 | 10.8737 | 9.8083 | 8.8839 | 7.841 | 6.6604 | 3.19 | 1.741 | 0.38794 | -0.67737 | -7.1835 | -8.0845 | -8.2029 | 7.3359 | 6.0298 | 4.8522 | 3.5216 | 2.0196 | -1.3304 | -3.1672 | -4.8794 | -6.2172 | -13.4825 | -14.4743 | -14.5131
|  | COURAGES PRIMARY | HT |  |  |  |  | 8.641 | 7.9757 | 7.4032 | 6.6726 | 5.6155 | 2.5941 | 1.3318 | 0.0032449 | -1.611 | -10.1131 | -12.8019 | -12.9825 | 11.3706 | 10.8073 | 10.441 | 9.8583 | 9.0686 | 6.0369 | 5.0941 | 4.0981 | 2.7961 | -4.3835 | -6.5131 | -6.6488 | 8.541 | 7.6277 | 6.9145 | 6.0604 | 5.0543 | 2.2461 | 1.0441 | -0.22635 | -1.7845 | -10.0192 | -12.6039 | -12.7692
|  | COURAGES PRIMARY | HE |  |  |  |  | 8.3818 | 7.4288 | 6.3206 | 5.0267 | 3.4696 | -0.071245 | -1.9957 | -4.0335 | -6.0529 | -18.2335 | -22.1886 | -22.3396 | 11.1328 | 10.389 | 9.5594 | 8.593 | 7.4247 | 3.9808 | 2.5247 | 0.97569 | -0.57431 | -10.7202 | -13.8825 | -14.0692 | 7.9604 | 6.7604 | 5.7032 | 4.4655 | 2.9798 | -0.33451 | -2.1794 | -4.1376 | -6.0845 | -17.9059 | -21.7314 | -21.8733
|  | COURAGES PRIMARY | CF |  |  |  |  | 8.7941 | 8.192 | 7.7237 | 7.1706 | 6.1328 | 3.3553 | 2.2808 | 1.1083 | -0.020224 | -6.2519 | -14.9212 | -16.8172 | 11.4308 | 10.8747 | 10.5379 | 10.1461 | 9.3839 | 6.5216 | 5.7043 | 4.8155 | 3.9441 | -0.88451 | -8.3774 | -9.9366 | 8.7706 | 7.939 | 7.3349 | 6.6349 | 5.543 | 2.9634 | 1.9379 | 0.81651 | -0.26818 | -6.2896 | -14.708 | -16.5243
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | COVE PRIMARY | MINIMUM HEADROOM | SU 85415 55937 | NO | NO | 3.032 | 11.8796 | 10.8388 | 10.15 | 9.6867 | 8.8337 | 7.7378 | 6.5112 | 5.4184 | 4.5194 | 0.38469 | -2.5918 | -4.3245 | 12.6967 | 11.9518 | 11.458 | 11.2804 | 10.7161 | 9.8416 | 8.8437 | 7.9518 | 7.1804 | 3.7906 | 0.69878 | -6.9992 | 11.6351 | 10.6963 | 10.0576 | 9.7147 | 8.9555 | 7.8871 | 6.678 | 5.6065 | 4.7443 | 0.8902 | -1.9486 | -3.6088
|  | COVE PRIMARY | EE |  |  |  |  | 11.8796 | 10.8388 | 10.15 | 9.6867 | 8.8337 | 7.7378 | 6.5112 | 5.4184 | 4.5194 | 0.74898 | -1.6724 | -3.6939 | 12.6967 | 11.9518 | 11.458 | 11.2804 | 10.7161 | 9.8416 | 8.8437 | 7.9518 | 7.1804 | 3.7906 | 0.69878 | -3.8502 | 11.6351 | 10.6963 | 10.0576 | 9.7147 | 8.9555 | 7.8871 | 6.678 | 5.6065 | 4.7443 | 1.2627 | -0.97204 | -2.8822
|  | COVE PRIMARY | HT |  |  |  |  | 12.1582 | 11.1796 | 10.6337 | 9.9459 | 9.1398 | 8.0735 | 7.2776 | 6.2663 | 5.2184 | 0.38469 | -2.5918 | -4.3245 | 13.0273 | 12.4069 | 12.1141 | 11.7273 | 11.2824 | 10.5273 | 10.0222 | 9.3049 | 8.5488 | 5.2835 | 3.4386 | 2.3763 | 11.9157 | 11.0565 | 10.5861 | 9.9861 | 9.28 | 8.2463 | 7.4769 | 6.5137 | 5.5004 | 0.8902 | -1.9486 | -3.6088
|  | COVE PRIMARY | HE |  |  |  |  | 12.1673 | 11.1969 | 10.6622 | 9.9837 | 9.1837 | 8.2878 | 7.648 | 6.8449 | 6.0051 | 1.8673 | -0.75204 | -2.1663 | 12.9498 | 12.2916 | 11.9559 | 11.5151 | 10.9937 | 10.2824 | 9.758 | 9.1182 | 8.4243 | 4.6151 | 1.3171 | -3.0002 | 11.9188 | 11.0678 | 10.6065 | 10.0106 | 9.3096 | 8.4473 | 7.8514 | 7.1065 | 6.3147 | 2.4239 | -0.01898 | -1.3935
|  | COVE PRIMARY | CF |  |  |  |  | 12.4418 | 11.6398 | 11.2449 | 10.7949 | 10.2276 | 9.7306 | 9.0918 | 8.8592 | 8.3347 | 5.3347 | 2.9184 | 0.82143 | 13.0794 | 12.4896 | 12.1824 | 11.8702 | 11.4508 | 10.9294 | 10.2539 | 9.8998 | 9.2978 | 5.8029 | 1.0376 | -6.9992 | 12.1749 | 11.48 | 11.1259 | 10.7443 | 10.2514 | 9.7596 | 9.1198 | 8.9361 | 8.4239 | 5.6453 | 3.482 | 1.5922
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES PRIMARY | MINIMUM HEADROOM | SP 56113 03074 | NO | YES | 4.224 | 5.5949 | 4.9265 | 3.949 | 2.7663 | 1.451 | -0.21531 | -2.001 | -3.8255 | -5.2837 | -11.8347 | -17.4531 | -20.5378 | 10.3694 | 9.949 | 9.2929 | 8.5255 | 7.6755 | 6.648 | 5.4214 | 4.1643 | 3.2327 | -1.1592 | -5.202 | -14.748 | 5.552 | 4.9704 | 4.0245 | 2.9276 | 1.7051 | 0.17857 | -1.4949 | -3.1939 | -4.4847 | -10.2122 | -14.9469 | -17.4327
|  | COWES PRIMARY | EE |  |  |  |  | 5.5949 | 4.9265 | 3.949 | 2.7663 | 1.451 | -0.21531 | -2.001 | -3.8255 | -5.2837 | -11.8347 | -16.451 | -20.0888 | 10.3694 | 9.949 | 9.2929 | 8.5255 | 7.6755 | 6.648 | 5.4214 | 4.1643 | 3.2327 | -1.1592 | -5.202 | -10.8204 | 5.552 | 4.9704 | 4.0245 | 2.9276 | 1.7051 | 0.17857 | -1.4949 | -3.1939 | -4.4847 | -10.2122 | -14.0816 | -17.1
|  | COWES PRIMARY | HT |  |  |  |  | 5.9888 | 5.1592 | 4.2306 | 3.1714 | 2.4082 | 0.93878 | -0.56633 | -2.1286 | -3.7449 | -11.7755 | -17.4531 | -20.5378 | 10.8194 | 10.3551 | 9.8286 | 9.2224 | 8.8582 | 8.0867 | 7.2622 | 6.3939 | 5.4898 | 1.1102 | -1.6041 | -2.8551 | 6.0776 | 5.3245 | 4.4673 | 3.4857 | 2.8867 | 1.5867 | 0.2051 | -1.2388 | -2.7316 | -10.0296 | -14.9469 | -17.4327
|  | COWES PRIMARY | HE |  |  |  |  | 6.051 | 5.2939 | 4.4429 | 3.4449 | 2.6816 | 1.4153 | 0.082653 | -1.3398 | -2.8255 | -10.0286 | -15.0235 | -17.2245 | 10.7316 | 10.2418 | 9.6806 | 9.0204 | 8.5735 | 7.7806 | 6.9082 | 5.9643 | 4.9673 | -0.21633 | -4.6867 | -9.6857 | 6.1112 | 5.4163 | 4.6245 | 3.6949 | 3.1061 | 1.9602 | 0.72245 | -0.60204 | -1.9755 | -8.5316 | -12.7398 | -14.501
|  | COWES PRIMARY | CF |  |  |  |  | 6.749 | 6.3143 | 5.8959 | 5.3571 | 4.7622 | 4.5306 | 3.9418 | 3.25 | 2.4908 | -3.0959 | -8.151 | -12.5888 | 11.0867 | 10.7337 | 10.3878 | 9.9429 | 9.4286 | 9.1531 | 8.5684 | 7.9357 | 7.2357 | 2.2071 | -4.4878 | -14.748 | 6.7163 | 6.2867 | 5.8847 | 5.3612 | 4.7796 | 4.6388 | 4.0561 | 3.4071 | 2.6949 | -2.399 | -6.8367 | -10.748
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL PRIMARY | MINIMUM HEADROOM | SP 56113 03074 | NO | NO | 38.085 | 24.8347 | 23.3949 | 21.9255 | 20.4317 | 18.3051 | 15.5286 | 12.4766 | 9.3929 | 6.7 | -4.5449 | -8.5775 | -9.302 | 27.8521 | 26.7653 | 25.6102 | 24.5204 | 22.8368 | 20.747 | 18.3408 | 15.7949 | 13.5235 | 4.2398 | 0.6184 | -14.5285 | 24.198 | 23.1664 | 21.9796 | 20.698 | 18.8174 | 16.049 | 13.249 | 10.446 | 8.2541 | -2.0989 | -5.9357 | -6.6245
|  | COWLEY LOCAL PRIMARY | EE |  |  |  |  | 24.8347 | 23.3949 | 21.9255 | 20.4317 | 18.3051 | 15.5286 | 12.4766 | 9.3929 | 6.7 | -1.9102 | -3.5592 | -3.6367 | 27.8521 | 26.7653 | 25.6102 | 24.5204 | 22.8368 | 20.747 | 18.3408 | 15.7949 | 13.5235 | 6.4429 | 2.4817 | -4.25 | 24.198 | 23.1664 | 21.9796 | 20.698 | 18.8174 | 16.049 | 13.249 | 10.446 | 8.2541 | 0.54391 | -1.7724 | -1.8663
|  | COWLEY LOCAL PRIMARY | HT |  |  |  |  | 25.6123 | 24.547 | 23.5572 | 22.1317 | 20.4398 | 17.2613 | 14.7092 | 11.9266 | 9.4745 | 0.6082 | -3.4683 | -4.0949 | 28.5613 | 27.7398 | 26.9857 | 25.8327 | 24.3664 | 22.3521 | 20.1521 | 17.6133 | 15.4204 | 8.7164 | 6.397 | 5.9215 | 24.748 | 23.7704 | 22.8684 | 21.5429 | 20.1123 | 17.1868 | 14.8062 | 12.198 | 9.9194 | 2.0317 | -1.6622 | -2.2326
|  | COWLEY LOCAL PRIMARY | HE |  |  |  |  | 25.5806 | 24.2062 | 22.9062 | 21.5715 | 19.7072 | 17.1174 | 14.2388 | 11.1306 | 7.9613 | -4.5449 | -8.5775 | -9.302 | 28.3796 | 27.3419 | 26.3674 | 25.4031 | 23.9286 | 21.9766 | 19.6868 | 17.1133 | 14.4582 | 4.2398 | 1.2643 | -4.4745 | 24.8368 | 23.7041 | 22.699 | 21.6439 | 20.3347 | 17.9102 | 15.5408 | 12.8184 | 9.8 | -2.0989 | -5.9357 | -6.6245
|  | COWLEY LOCAL PRIMARY | CF |  |  |  |  | 26.5776 | 25.7143 | 24.9643 | 24.2419 | 23.2276 | 22.1949 | 20.6174 | 18.746 | 16.7286 | 4.5306 | -1.8479 | -5.5938 | 28.9051 | 28.1847 | 27.597 | 26.9837 | 26.1011 | 25.3347 | 24.0296 | 22.5011 | 20.85 | 9.7837 | 0.6184 | -14.5285 | 25.5664 | 24.8419 | 24.3 | 23.7102 | 22.8215 | 22.1449 | 20.8684 | 19.3357 | 17.7133 | 6.5623 | 0.48575 | -3.051
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | COXMOOR WOOD PRIMARY | MINIMUM HEADROOM | SU 78275 50779 | YES | NO | 1.109 | 4.4354 | 4.1242 | 3.8793 | 3.5762 | 3.2538 | 2.8048 | 2.6885 | 2.2579 | 1.8538 | 0.05174 | -1.4166 | -2.3034 | 6.4762 | 6.265 | 6.0875 | 5.864 | 5.6201 | 5.3109 | 5.264 | 4.963 | 4.7446 | 3.4966 | 2.0956 | -1.3636 | 4.7405 | 4.4446 | 4.2109 | 3.914 | 3.5926 | 3.1579 | 3.116 | 2.7089 | 2.3619 | 0.84562 | -0.39622 | -1.133
|  | COXMOOR WOOD PRIMARY | EE |  |  |  |  | 4.4354 | 4.1242 | 3.8793 | 3.5762 | 3.2538 | 2.8048 | 2.6885 | 2.2579 | 1.9395 | 0.22113 | -1.0932 | -2.1105 | 6.4762 | 6.265 | 6.0875 | 5.864 | 5.6201 | 5.3109 | 5.264 | 4.963 | 4.7446 | 3.4966 | 2.1691 | 0.29766 | 4.7405 | 4.4446 | 4.2109 | 3.914 | 3.5926 | 3.1579 | 3.116 | 2.7089 | 2.4272 | 0.97215 | -0.11561 | -0.97581
|  | COXMOOR WOOD PRIMARY | HT |  |  |  |  | 4.5436 | 4.2793 | 4.0762 | 3.8221 | 3.5528 | 3.1926 | 2.764 | 2.315 | 1.8538 | 0.05174 | -1.4166 | -2.3034 | 6.6068 | 6.4568 | 6.3436 | 6.1905 | 6.0232 | 5.8293 | 5.5813 | 5.316 | 5.0436 | 4.1783 | 3.4956 | 3.116 | 4.8681 | 4.6242 | 4.4385 | 4.2007 | 3.9395 | 3.6211 | 3.2191 | 2.7977 | 2.3619 | 0.84562 | -0.39622 | -1.133
|  | COXMOOR WOOD PRIMARY | HE |  |  |  |  | 4.5589 | 4.3079 | 4.1232 | 3.8895 | 3.6762 | 3.3568 | 3.0017 | 2.6283 | 2.2436 | 0.79256 | -0.49622 | -1.1809 | 6.5752 | 6.4089 | 6.2834 | 6.114 | 5.9579 | 5.7375 | 5.4824 | 5.2099 | 4.9232 | 3.7936 | 2.4609 | 0.71909 | 4.8772 | 4.6466 | 4.4783 | 4.2558 | 4.0579 | 3.7589 | 3.4191 | 3.0619 | 2.6905 | 1.4762 | 0.42419 | -0.14214
|  | COXMOOR WOOD PRIMARY | CF |  |  |  |  | 4.7007 | 4.5242 | 4.3834 | 4.2701 | 4.114 | 3.9681 | 3.8385 | 3.6558 | 3.466 | 2.5262 | 1.1824 | -0.042138 | 6.6426 | 6.5038 | 6.3813 | 6.2783 | 6.1334 | 5.9721 | 5.8109 | 5.6079 | 5.3905 | 4.2089 | 2.0956 | -1.3636 | 5.0058 | 4.8436 | 4.7048 | 4.5987 | 4.4487 | 4.3007 | 4.1752 | 3.9915 | 3.7966 | 2.9599 | 1.7977 | 0.77827
MANNINGTON GSP | LYTCHETT BSP | CREEKMOOR PRIMARY | MINIMUM HEADROOM | SZ 00552 94121 | NO | NO | 2.205 | 14.8199 | 14.276 | 13.9362 | 13.3331 | 12.6709 | 11.6913 | 10.6117 | 9.5515 | 8.724 | 4.1617 | 0.75457 | -1.0679 | 16.9973 | 16.5616 | 16.3401 | 15.8595 | 15.3299 | 14.6473 | 13.8269 | 12.9993 | 12.4126 | 9.234 | 4.6891 | -5.3323 | 16.2076 | 15.6944 | 15.4086 | 14.8505 | 14.2393 | 13.3464 | 12.326 | 11.3189 | 10.576 | 6.6801 | 3.6882 | 2.1219
|  | CREEKMOOR PRIMARY | EE |  |  |  |  | 14.8199 | 14.276 | 13.9362 | 13.3331 | 12.6709 | 11.6913 | 10.6117 | 9.5515 | 8.724 | 4.4872 | 1.3607 | -0.91992 | 16.9973 | 16.5616 | 16.3401 | 15.8595 | 15.3299 | 14.6473 | 13.8269 | 12.9993 | 12.4126 | 9.234 | 5.6912 | 0.45545 | 16.2076 | 15.6944 | 15.4086 | 14.8505 | 14.2393 | 13.3464 | 12.326 | 11.3189 | 10.576 | 6.877 | 4.1668 | 2.1954
|  | CREEKMOOR PRIMARY | HT |  |  |  |  | 15.0882 | 14.6566 | 14.0382 | 13.5066 | 13.1882 | 12.2882 | 11.3148 | 10.3291 | 9.325 | 4.1617 | 0.75457 | -1.0679 | 17.3636 | 17.1136 | 16.7463 | 16.4177 | 16.2922 | 15.8208 | 15.2912 | 14.7442 | 14.1789 | 11.4718 | 9.9616 | 9.1769 | 16.4831 | 16.0933 | 15.5484 | 15.0566 | 14.7913 | 13.9852 | 13.1076 | 12.2158 | 11.3107 | 6.6801 | 3.6882 | 2.1219
|  | CREEKMOOR PRIMARY | HE |  |  |  |  | 15.1127 | 14.7025 | 14.1627 | 13.6066 | 13.278 | 12.524 | 11.6056 | 10.627 | 9.6066 | 4.6617 | 1.7995 | 0.36069 | 17.2514 | 16.9381 | 16.5371 | 16.0973 | 15.8718 | 15.3361 | 14.7095 | 14.0554 | 13.3687 | 9.4514 | 5.6269 | 0.68504 | 16.4944 | 16.1189 | 15.6291 | 15.1199 | 14.8393 | 14.1546 | 13.3811 | 12.5954 | 11.7311 | 7.3658 | 4.5505 | 3.2729
|  | CREEKMOOR PRIMARY | CF |  |  |  |  | 15.4974 | 15.2535 | 15.0311 | 14.7586 | 14.375 | 14.3413 | 13.9291 | 13.4546 | 12.9515 | 9.5811 | 6.0648 | 3.3301 | 17.435 | 17.182 | 16.9371 | 16.6279 | 16.2095 | 16.0401 | 15.583 | 15.0871 | 14.5534 | 10.7095 | 4.6891 | -5.3323 | 16.8464 | 16.6178 | 16.4076 | 16.1484 | 15.7954 | 15.7801 | 15.4668 | 15.1148 | 14.6474 | 11.476 | 8.5433 | 6.1556
MINETY GSP | CIRENCESTER BSP | CRICKLADE PRIMARY | MINIMUM HEADROOM | SU 09400 93270 | NO | NO | 1.839 | 3.2643 | 2.999 | 2.7612 | 2.4582 | 2.1306 | 1.6704 | 1.598 | 1.1561 | 0.85204 | -0.77449 | -2.002 | -2.7041 | 6.3469 | 6.2173 | 6.0388 | 5.8112 | 5.5622 | 5.2449 | 5.1837 | 4.8663 | 4.6378 | 3.3418 | 1.7755 | -2.0418 | 3.6265 | 3.3633 | 3.1378 | 2.8357 | 2.5082 | 2.0602 | 2.0959 | 1.6827 | 1.4173 | 0.05 | -1.0265 | -1.6214
|  | CRICKLADE PRIMARY | EE |  |  |  |  | 3.2643 | 2.999 | 2.7612 | 2.4582 | 2.1306 | 1.6704 | 1.598 | 1.1561 | 0.85204 | -0.77449 | -1.7918 | -2.5214 | 6.3469 | 6.2173 | 6.0388 | 5.8112 | 5.5622 | 5.2449 | 5.1837 | 4.8663 | 4.6378 | 3.3418 | 2.048 | 0.097959 | 3.6265 | 3.3633 | 3.1378 | 2.8357 | 2.5082 | 2.0602 | 2.0959 | 1.6827 | 1.4173 | 0.05 | -0.83673 | -1.4663
|  | CRICKLADE PRIMARY | HT |  |  |  |  | 3.4071 | 3.2082 | 3.0265 | 2.8 | 2.548 | 2.2143 | 1.7969 | 1.3592 | 0.89898 | -0.75102 | -2.002 | -2.7041 | 6.4214 | 6.3602 | 6.3051 | 6.1776 | 6.0143 | 5.8286 | 5.5816 | 5.3204 | 5.048 | 4.1908 | 3.5745 | 3.2571 | 3.7878 | 3.5969 | 3.4265 | 3.2041 | 2.9571 | 2.6643 | 2.2694 | 1.8551 | 1.4184 | 0.084694 | -1.0265 | -1.6214
|  | CRICKLADE PRIMARY | HE |  |  |  |  | 3.4173 | 3.2286 | 3.0602 | 2.8469 | 2.6133 | 2.3347 | 1.9714 | 1.5857 | 1.1878 | -0.23265 | -1.2398 | -1.7449 | 6.4071 | 6.3408 | 6.2582 | 6.0959 | 5.9143 | 5.7184 | 5.4541 | 5.1724 | 4.8735 | 3.6663 | 2.348 | 0.47857 | 3.7949 | 3.6143 | 3.4531 | 3.2459 | 3.0184 | 2.7724 | 2.4235 | 2.0541 | 1.6704 | 0.55714 | -0.32551 | -0.73061
|  | CRICKLADE PRIMARY | CF |  |  |  |  | 3.5357 | 3.4041 | 3.2592 | 3.151 | 2.9908 | 2.8204 | 2.6673 | 2.4582 | 2.2398 | 1.3214 | 0.15408 | -0.92041 | 6.449 | 6.399 | 6.3429 | 6.2357 | 6.0806 | 5.9051 | 5.7255 | 5.5092 | 5.2694 | 4.0031 | 1.7755 | -2.0418 | 3.901 | 3.7694 | 3.6235 | 3.5204 | 3.3612 | 3.1888 | 3.048 | 2.8388 | 2.6173 | 1.8429 | 0.83469 | -0.04898
MELKSHAM GSP | FROME BSP | CROCKERTON PRIMARY | MINIMUM HEADROOM | ST 87736 43371 | NO | NO | 1.582 | 1.198 | 0.83265 | 0.33469 | 0.16531 | -0.28163 | -0.95918 | -1.7133 | -2.4714 | -3.0122 | -5.9776 | -8.3 | -9.6653 | 3.56 | 3.4029 | 3.0886 | 2.9784 | 2.6682 | 2.258 | 1.7671 | 1.261 | 0.88551 | -1.289 | -3.739 | -9.738 | 0.68816 | 0.32286 | -0.16898 | -0.31388 | -0.75163 | -1.3843 | -2.0945 | -2.8047 | -3.3047 | -5.9047 | -7.8843 | -8.9833
|  | CROCKERTON PRIMARY | EE |  |  |  |  | 1.198 | 0.83265 | 0.33469 | 0.16531 | -0.28163 | -0.95918 | -1.7133 | -2.4714 | -3.0122 | -5.9071 | -7.8776 | -9.3092 | 3.56 | 3.4029 | 3.0886 | 2.9784 | 2.6682 | 2.258 | 1.7671 | 1.261 | 0.88551 | -1.289 | -3.4533 | -6.5839 | 0.68816 | 0.32286 | -0.16898 | -0.31388 | -0.75163 | -1.3843 | -2.0945 | -2.8047 | -3.3047 | -5.8853 | -7.5037 | -8.6843
|  | CROCKERTON PRIMARY | HT |  |  |  |  | 1.4071 | 1.0704 | 0.66224 | 0.28469 | -0.10204 | -0.74082 | -1.0694 | -1.7194 | -2.3969 | -5.9776 | -8.3 | -9.6653 | 3.6927 | 3.5722 | 3.3937 | 3.2447 | 3.0263 | 2.6876 | 2.5457 | 2.1773 | 1.7906 | -0.072653 | -1.1227 | -1.7431 | 0.9249 | 0.61878 | 0.24429 | -0.12102 | -0.50367 | -1.1037 | -1.3731 | -1.9873 | -2.6312 | -5.9047 | -7.8843 | -8.9833
|  | CROCKERTON PRIMARY | HE |  |  |  |  | 1.4296 | 1.1357 | 0.78265 | 0.39898 | 0.014286 | -0.53469 | -0.77857 | -1.3398 | -1.9653 | -5.2041 | -7.1622 | -8.1337 | 3.6773 | 3.558 | 3.3773 | 3.1416 | 2.862 | 2.508 | 2.3549 | 1.9712 | 1.5692 | -0.88796 | -3.1431 | -6.0859 | 0.94224 | 0.67592 | 0.34224 | -0.02102 | -0.39449 | -0.91592 | -1.1118 | -1.6455 | -2.2006 | -5.1445 | -6.8261 | -7.6037
|  | CROCKERTON PRIMARY | CF |  |  |  |  | 1.6296 | 1.4684 | 1.2337 | 1.0704 | 0.85204 | 0.59796 | 0.29184 | 0.26837 | -0.032653 | -2.2255 | -4.5337 | -6.5051 | 3.7722 | 3.709 | 3.5784 | 3.4457 | 3.2304 | 2.9722 | 2.6671 | 2.56 | 2.2416 | -0.11245 | -3.739 | -9.738 | 1.1341 | 0.98102 | 0.75347 | 0.58612 | 0.36878 | 0.11673 | -0.19041 | -0.18939 | -0.48735 | -2.5312 | -4.5078 | -6.3027
FLEET-BRAMLEY GSP | PYESTOCK BSP | CROOKHAM PRIMARY | MINIMUM HEADROOM | SU 81702 53403 | NO | NO | 0.758 | 17.2684 | 16.8112 | 16.7214 | 16.2939 | 15.8214 | 14.9827 | 14.0551 | 13.1224 | 12.4939 | 8.5459 | 5.6449 | 3.951 | 18.5041 | 18.1143 | 18.0653 | 17.6939 | 17.299 | 16.7347 | 16.0776 | 15.4051 | 14.9653 | 12.4602 | 8.6867 | 0.23265 | 16.5469 | 16.0551 | 16.0643 | 15.6276 | 15.1602 | 14.3857 | 13.5071 | 12.6296 | 12.0959 | 8.7551 | 6.2316 | 4.7724
|  | CROOKHAM PRIMARY | EE |  |  |  |  | 17.2684 | 16.8112 | 16.7214 | 16.2939 | 15.8214 | 14.9827 | 14.0551 | 13.1224 | 12.4939 | 9.1122 | 6.4327 | 4.3163 | 18.5041 | 18.1143 | 18.0653 | 17.6939 | 17.299 | 16.7347 | 16.0776 | 15.4051 | 14.9653 | 12.4602 | 9.548 | 5.0755 | 16.5469 | 16.0551 | 16.0643 | 15.6276 | 15.1602 | 14.3857 | 13.5071 | 12.6296 | 12.0959 | 9.2184 | 6.9102 | 5.0653
|  | CROOKHAM PRIMARY | HT |  |  |  |  | 17.502 | 17.1786 | 16.7959 | 16.3745 | 16.2847 | 15.4949 | 14.6582 | 13.7918 | 12.9041 | 8.5459 | 5.6449 | 3.951 | 18.8337 | 18.6316 | 18.3704 | 18.0776 | 18.1122 | 17.7102 | 17.2592 | 16.7776 | 16.2745 | 14.0224 | 12.7582 | 12.0571 | 16.85 | 16.5378 | 16.1602 | 15.7286 | 15.7224 | 15.0184 | 14.2582 | 13.4653 | 12.651 | 8.7551 | 6.2316 | 4.7724
|  | CROOKHAM PRIMARY | HE |  |  |  |  | 17.55 | 17.2571 | 16.9133 | 16.5316 | 16.4857 | 15.8878 | 15.2337 | 14.5439 | 13.8398 | 10.1061 | 7.3347 | 5.9429 | 18.7561 | 18.5122 | 18.2133 | 17.8776 | 17.8684 | 17.4439 | 16.9653 | 16.4459 | 15.898 | 12.8337 | 9.8367 | 5.6337 | 16.8837 | 16.599 | 16.2449 | 15.8429 | 15.8867 | 15.3367 | 14.7255 | 14.0796 | 13.4153 | 10.0469 | 7.6939 | 6.5276
|  | CROOKHAM PRIMARY | CF |  |  |  |  | 17.802 | 17.602 | 17.4347 | 17.2071 | 16.9459 | 17.0255 | 16.749 | 16.4337 | 16.1031 | 13.5816 | 10.8357 | 8.1888 | 18.8633 | 18.6255 | 18.4173 | 18.152 | 17.8398 | 17.8204 | 17.448 | 17.0449 | 16.6133 | 13.4704 | 8.6867 | 0.23265 | 17.1143 | 16.8776 | 16.6959 | 16.4347 | 16.1541 | 16.3316 | 16.0388 | 15.7214 | 15.3857 | 12.998 | 10.6214 | 8.4204
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CROWTHORNE PRIMARY | MINIMUM HEADROOM | SU 84470 64352 | NO | NO | 2.351 | 4.7091 | 3.7479 | 2.3999 | 0.91827 | -0.7001 | -2.2705 | -3.8879 | -5.4123 | -6.5491 | -13.0021 | -17.4685 | -19.9154 | 9.5091 | 9.0132 | 8.1887 | 7.2968 | 6.2672 | 5.2274 | 4.0897 | 2.9632 | 2.1723 | -2.0093 | -6.7736 | -17.8726 | 5.1305 | 4.4172 | 3.2713 | 2.005 | 0.55908 | -0.89092 | -2.4246 | -3.9032 | -4.944 | -10.5215 | -14.5083 | -16.6113
|  | CROWTHORNE PRIMARY | EE |  |  |  |  | 4.7091 | 3.7479 | 2.3999 | 0.91827 | -0.7001 | -2.2705 | -3.8879 | -5.4123 | -6.5491 | -12.245 | -16.2552 | -19.2766 | 9.5091 | 9.0132 | 8.1887 | 7.2968 | 6.2672 | 5.2274 | 4.0897 | 2.9632 | 2.1723 | -2.0093 | -6.1042 | -11.9511 | 5.1305 | 4.4172 | 3.2713 | 2.005 | 0.55908 | -0.89092 | -2.4246 | -3.9032 | -4.944 | -9.9205 | -13.4664 | -16.0909
|  | CROWTHORNE PRIMARY | HT |  |  |  |  | 4.9774 | 3.8244 | 2.4856 | 1.3142 | -0.13071 | -1.596 | -3.0868 | -4.5654 | -6.0511 | -13.0021 | -17.4685 | -19.9154 | 9.9438 | 9.3448 | 8.6346 | 8.1285 | 7.3407 | 6.5479 | 5.6877 | 4.7897 | 3.8907 | 0.12949 | -1.8981 | -2.945 | 5.4917 | 4.5397 | 3.4162 | 2.5315 | 1.2509 | -0.060306 | -1.4338 | -2.8328 | -4.2368 | -10.5215 | -14.5083 | -16.6113
|  | CROWTHORNE PRIMARY | HE |  |  |  |  | 5.1774 | 3.9989 | 2.7264 | 1.7336 | 0.305 | -0.91847 | -2.1409 | -3.3205 | -4.545 | -10.7399 | -14.8501 | -16.8838 | 9.9213 | 9.2101 | 8.4458 | 7.9999 | 7.1254 | 6.3162 | 5.4499 | 4.5621 | 3.6172 | -1.3817 | -5.6542 | -11.1174 | 5.657 | 4.6652 | 3.5907 | 2.9009 | 1.6407 | 0.53357 | -0.60418 | -1.7409 | -2.9215 | -8.6542 | -12.2521 | -14.0062
|  | CROWTHORNE PRIMARY | CF |  |  |  |  | 5.8989 | 5.1132 | 4.2458 | 3.2887 | 2.7315 | 2.0785 | 1.405 | 0.71929 | 0.005 | -4.946 | -9.3705 | -13.4042 | 10.2193 | 9.6887 | 9.0897 | 8.4489 | 8.1366 | 7.5223 | 6.8417 | 6.1274 | 5.3652 | 0.051939 | -6.7736 | -17.8726 | 6.2152 | 5.5591 | 4.8132 | 3.9917 | 3.6581 | 3.0672 | 2.4295 | 1.7703 | 1.0785 | -3.6909 | -7.5623 | -10.9511
COWLEY GSP |  | CULHAM PRIMARY | MINIMUM HEADROOM | SU 50731 95053 | NO | NO | 19.2 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.6849 | 17.6849 | 17.6849 | 17.6849 | 17.6849 | 17.6849 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9614 | 15.9614 | 15.9614 | 15.9614 | 15.9614 | 15.9604 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0482 | 17.0482 | 17.0482 | 17.0482 | 17.0482 | 17.0482
|  | CULHAM PRIMARY | EE |  |  |  |  | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.6849 | 17.6849 | 17.6849 | 17.6849 | 17.6849 | 17.6849 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9614 | 15.9614 | 15.9614 | 15.9614 | 15.9614 | 15.9614 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0482 | 17.0482 | 17.0482 | 17.0482 | 17.0482 | 17.0482
|  | CULHAM PRIMARY | HT |  |  |  |  | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.6849 | 17.6849 | 17.6849 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9614 | 15.9614 | 15.9614 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0482 | 17.0482 | 17.0482
|  | CULHAM PRIMARY | HE |  |  |  |  | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.692 | 17.6849 | 17.6849 | 17.6849 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9614 | 15.9614 | 15.9614 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0553 | 17.0482 | 17.0482 | 17.0482
|  | CULHAM PRIMARY | CF |  |  |  |  | 17.6931 | 17.6931 | 17.6931 | 17.6931 | 17.6931 | 17.6931 | 17.6931 | 17.6931 | 17.6931 | 17.6859 | 17.6859 | 17.6859 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9686 | 15.9614 | 15.9614 | 15.9604 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0502 | 17.0502 | 17.0502
EALING GSP | EALING BSP | DEAN GARDENS PRIMARY | MINIMUM HEADROOM | TQ 16546 80368 | YES | NO | 3.783 | 4.8271 | 4.4588 | 4.2118 | 3.9496 | 3.6669 | 3.4547 | 3.1649 | 2.8771 | 2.67 | 2.0343 | 1.5353 | 1.5761 | 5.418 | 5.1363 | 4.8945 | 4.6067 | 4.2945 | 3.9965 | 3.622 | 3.2292 | 2.8761 | -0.18408 | -6.8922 | -19.98 | 4.7322 | 4.4139 | 4.1843 | 3.9404 | 3.6761 | 3.4761 | 3.2057 | 2.9322 | 2.7343 | 2.1322 | 1.6792 | 1.7149
|  | DEAN GARDENS PRIMARY | EE |  |  |  |  | 4.8271 | 4.4588 | 4.2118 | 3.9496 | 3.6669 | 3.4547 | 3.1649 | 2.8771 | 2.67 | 2.0343 | 1.7394 | 1.8241 | 5.418 | 5.1363 | 4.8945 | 4.6067 | 4.2945 | 3.9965 | 3.622 | 3.2292 | 2.8761 | 0.5802 | -2.9453 | -9.3667 | 4.7322 | 4.4139 | 4.1843 | 3.9404 | 3.6761 | 3.4761 | 3.2057 | 2.9322 | 2.7343 | 2.1322 | 1.869 | 1.9282
|  | DEAN GARDENS PRIMARY | HT |  |  |  |  | 4.9496 | 4.6057 | 4.4231 | 4.2159 | 4.0169 | 3.8486 | 3.6414 | 3.4231 | 3.2312 | 2.1751 | 1.5353 | 1.5761 | 5.522 | 5.4333 | 5.3384 | 5.2057 | 5.0771 | 4.9547 | 4.7945 | 4.6271 | 4.4802 | 3.6873 | 3.221 | 3.1384 | 4.8465 | 4.5547 | 4.3863 | 4.1924 | 4.0057 | 3.8506 | 3.6588 | 3.4537 | 3.2771 | 2.2792 | 1.6792 | 1.7149
|  | DEAN GARDENS PRIMARY | HE |  |  |  |  | 4.9486 | 4.6149 | 4.4435 | 4.2496 | 4.072 | 3.9343 | 3.7588 | 3.5751 | 3.4231 | 2.7567 | 2.4782 | 2.4935 | 5.4639 | 5.2639 | 5.0761 | 4.8455 | 4.6118 | 4.3659 | 4.0782 | 3.7598 | 3.4455 | 1.072 | -2.5402 | -8.9565 | 4.8445 | 4.5608 | 4.4037 | 4.2241 | 4.0547 | 3.9251 | 3.7618 | 3.5924 | 3.4516 | 2.8282 | 2.57 | 2.5863
|  | DEAN GARDENS PRIMARY | CF |  |  |  |  | 5.0435 | 4.7812 | 4.6649 | 4.5312 | 4.3935 | 4.3455 | 4.2547 | 4.1629 | 4.0588 | 3.4516 | 2.8057 | 2.2537 | 5.4792 | 5.2976 | 5.1027 | 4.8669 | 4.5771 | 4.2731 | 3.9078 | 3.522 | 3.0955 | -0.18408 | -6.8922 | -19.98 | 4.9333 | 4.7169 | 4.6067 | 4.4843 | 4.3557 | 4.3088 | 4.2251 | 4.1394 | 4.0404 | 3.4639 | 2.8598 | 2.3537
COWLEY GSP | YARNTON BSP | DEDDINGTON PRIMARY | MINIMUM HEADROOM | SP 46729 30325 | NO | YES | 0.7 | 1.8857 | 1.7459 | 1.6245 | 1.4582 | 1.2765 | 1.0929 | 0.81837 | 0.54796 | 0.39388 | -0.36429 | -0.84796 | -1.2235 | 3.2867 | 3.1837 | 3.0959 | 2.9673 | 2.8276 | 2.6959 | 2.4959 | 2.2847 | 2.1786 | 1.6143 | 0.89694 | -0.8 | 2.0663 | 1.9296 | 1.8153 | 1.6541 | 1.4786 | 1.3041 | 1.0418 | 0.78061 | 0.63878 | -0.019388 | -0.43571 | -0.75408
|  | DEDDINGTON PRIMARY | EE |  |  |  |  | 1.8857 | 1.7459 | 1.6245 | 1.4582 | 1.2765 | 1.0929 | 0.81837 | 0.54796 | 0.39388 | -0.36429 | -0.80204 | -1.1286 | 3.2867 | 3.1837 | 3.0959 | 2.9673 | 2.8276 | 2.6959 | 2.4959 | 2.2847 | 2.1786 | 1.6143 | 1.0429 | 0.17245 | 2.0663 | 1.9296 | 1.8153 | 1.6541 | 1.4786 | 1.3041 | 1.0418 | 0.78061 | 0.63878 | -0.019388 | -0.3898 | -0.66939
|  | DEDDINGTON PRIMARY | HT |  |  |  |  | 1.9724 | 1.8796 | 1.7684 | 1.649 | 1.55 | 1.3622 | 1.1459 | 0.92143 | 0.74184 | -0.28367 | -0.84796 | -1.2235 | 3.3796 | 3.3194 | 3.252 | 3.1673 | 3.1082 | 2.9918 | 2.8592 | 2.7133 | 2.6071 | 1.9929 | 1.7286 | 1.5469 | 2.1643 | 2.0776 | 1.9735 | 1.8551 | 1.7622 | 1.5867 | 1.3786 | 1.1643 | 1.002 | 0.05 | -0.43571 | -0.75408
|  | DEDDINGTON PRIMARY | HE |  |  |  |  | 1.9735 | 1.8837 | 1.7816 | 1.6633 | 1.5735 | 1.402 | 1.2061 | 1.002 | 0.84082 | -0.15918 | -0.58469 | -0.82143 | 3.3582 | 3.2949 | 3.2184 | 3.1245 | 3.0582 | 2.9357 | 2.799 | 2.6449 | 2.5306 | 1.7429 | 1.1653 | 0.33878 | 2.1633 | 2.0816 | 1.9837 | 1.8684 | 1.7827 | 1.6214 | 1.4337 | 1.2357 | 1.0908 | 0.17041 | -0.18673 | -0.38571
|  | DEDDINGTON PRIMARY | CF |  |  |  |  | 2.0184 | 1.9337 | 1.8704 | 1.7929 | 1.7041 | 1.6031 | 1.5224 | 1.399 | 1.2653 | 0.56429 | -0.005102 | -0.52347 | 3.3816 | 3.3133 | 3.2582 | 3.1929 | 3.1092 | 3.0112 | 2.9306 | 2.8163 | 2.6898 | 1.9245 | 0.89694 | -0.8 | 2.2071 | 2.1214 | 2.0653 | 1.9898 | 1.9031 | 1.801 | 1.7276 | 1.6061 | 1.4796 | 0.80714 | 0.28163 | -0.15306
IVER 132KV GSP | DENHAM BSP | DENHAM AVENUE PRIMARY | MINIMUM HEADROOM | TQ 03761 86587 | NO | YES | 3.058 | 1.9551 | 1.7214 | 1.502 | 1.2265 | 25.9337 | 25.4622 | 25.3041 | 24.8378 | 24.4929 | 22.6592 | 21.1449 | 20.3357 | 3.1582 | 3.002 | 2.8316 | 2.6296 | 25.8173 | 25.5378 | 25.3449 | 25.0541 | 24.8194 | 23.6082 | 21.9347 | 17.8643 | 1.9388 | 1.7153 | 1.5061 | 1.2449 | 25.3592 | 24.9184 | 24.7867 | 24.35 | 24.0378 | 22.4245 | 21.1612 | 20.5296
|  | DENHAM AVENUE PRIMARY | EE |  |  |  |  | 1.9551 | 1.7214 | 1.502 | 1.2265 | 25.9337 | 25.4622 | 25.3041 | 24.8378 | 24.4929 | 22.749 | 21.4398 | 20.5102 | 3.1582 | 3.002 | 2.8316 | 2.6296 | 25.8173 | 25.5378 | 25.3449 | 25.0541 | 24.8194 | 23.6082 | 22.2194 | 20.1031 | 1.9388 | 1.7153 | 1.5061 | 1.2449 | 25.3592 | 24.9184 | 24.7867 | 24.35 | 24.0378 | 22.4745 | 21.4276 | 20.6735
|  | DENHAM AVENUE PRIMARY | HT |  |  |  |  | 2.0704 | 1.9082 | 1.7541 | 1.549 | 26.3255 | 25.9663 | 25.5316 | 25.0755 | 24.602 | 22.6592 | 21.1449 | 20.3357 | 3.2929 | 3.2061 | 3.0949 | 2.9602 | 26.2071 | 26.0204 | 25.7847 | 25.5316 | 25.2663 | 24.2031 | 23.6684 | 23.3316 | 2.0755 | 1.9092 | 1.7633 | 1.5673 | 25.752 | 25.4255 | 25.0204 | 24.598 | 24.1571 | 22.4245 | 21.1612 | 20.5296
|  | DENHAM AVENUE PRIMARY | HE |  |  |  |  | 2.0816 | 1.9276 | 1.7837 | 1.5888 | 26.3786 | 26.0776 | 25.698 | 25.2939 | 24.8735 | 23.2337 | 21.8388 | 21.2357 | 3.2714 | 3.1653 | 3.0408 | 2.8878 | 26.1143 | 25.9051 | 25.6337 | 25.3449 | 25.0367 | 23.7582 | 22.3582 | 20.3673 | 2.0816 | 1.9265 | 1.7847 | 1.602 | 25.799 | 25.5255 | 25.1694 | 24.7898 | 24.399 | 22.8541 | 21.6786 | 21.1286
|  | DENHAM AVENUE PRIMARY | CF |  |  |  |  | 2.2255 | 2.1367 | 2.0296 | 1.9449 | 26.8214 | 26.6776 | 26.5378 | 26.348 | 26.148 | 25.1173 | 23.7469 | 22.4265 | 3.3357 | 3.2847 | 3.2316 | 3.1541 | 26.4347 | 26.2959 | 26.1184 | 25.8888 | 25.6398 | 24.3061 | 21.9347 | 17.8643 | 2.2133 | 2.1163 | 2.0102 | 1.9316 | 26.2112 | 26.0755 | 25.9408 | 25.7592 | 25.5673 | 24.6173 | 23.3133 | 22.1031
MELKSHAM GSP | NORRINGTON BSP | DEVIZES PRIMARY | MINIMUM HEADROOM | SU 00106 60986 | NO | YES | 4.301 | 14.3013 | 13.1666 | 12.2748 | 11.3176 | 10.3717 | 9.1687 | 7.8819 | 6.584 | 5.6911 | 0.886 | -2.8834 | -5.066 | 18.4105 | 17.5544 | 16.9401 | 16.2738 | 15.5891 | 14.7533 | 13.8105 | 12.8523 | 12.2125 | 8.6799 | 4.7942 | -5.4732 | 14.034 | 12.9972 | 12.3207 | 11.4533 | 10.5809 | 9.4911 | 8.2911 | 7.0829 | 6.3115 | 2.1452 | -1.1916 | -3.0579
|  | DEVIZES PRIMARY | EE |  |  |  |  | 14.3013 | 13.1666 | 12.2748 | 11.3176 | 10.3717 | 9.1687 | 7.8819 | 6.584 | 5.6911 | 0.9911 | -2.1518 | -4.5813 | 18.4105 | 17.5544 | 16.9401 | 16.2738 | 15.5891 | 14.7533 | 13.8105 | 12.8523 | 12.2125 | 8.6799 | 5.0564 | -0.27522 | 14.034 | 12.9972 | 12.3207 | 11.4533 | 10.5809 | 9.4911 | 8.2911 | 7.0829 | 6.3115 | 2.1921 | -0.54359 | -2.6477
|  | DEVIZES PRIMARY | HT |  |  |  |  | 14.685 | 13.7401 | 12.585 | 11.686 | 11.185 | 10.1227 | 9.0258 | 7.9523 | 6.8319 | 0.886 | -2.8834 | -5.066 | 18.8268 | 18.1911 | 17.4248 | 16.9033 | 16.6829 | 16.1003 | 15.4748 | 14.8421 | 14.1758 | 10.8748 | 9.037 | 8.0901 | 14.4789 | 13.6717 | 12.6605 | 11.8636 | 11.537 | 10.585 | 9.6044 | 8.6238 | 7.5829 | 2.1452 | -1.1916 | -3.0579
|  | DEVIZES PRIMARY | HE |  |  |  |  | 14.7176 | 13.8054 | 12.685 | 11.8513 | 11.4176 | 10.5258 | 9.587 | 8.6146 | 7.6738 | 2.6452 | -0.49563 | -2.0222 | 18.7472 | 18.0646 | 17.2584 | 16.7044 | 16.4421 | 15.8421 | 15.1778 | 14.4717 | 13.7564 | 9.6738 | 6.0033 | 0.96865 | 14.5033 | 13.7238 | 12.7493 | 12.0105 | 11.736 | 10.9401 | 10.1013 | 9.2278 | 8.3503 | 3.7482 | 0.97069 | -0.32216
|  | DEVIZES PRIMARY | CF |  |  |  |  | 15.0523 | 14.286 | 13.4207 | 12.8666 | 12.335 | 12.2289 | 11.8217 | 11.3554 | 10.8666 | 7.436 | 3.9911 | 0.84722 | 18.9054 | 18.2758 | 17.5799 | 17.1666 | 16.7156 | 16.5146 | 16.0289 | 15.4972 | 14.9278 | 10.8493 | 4.7942 | -5.4732 | 14.7952 | 14.1217 | 13.3829 | 12.8809 | 12.388 | 12.3819 | 11.986 | 11.5391 | 11.0676 | 7.9013 | 4.9207 | 2.1636
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH PRIMARY | MINIMUM HEADROOM | SU 19288 83540 | NO | NO | 6.688 | 10.5496 | 10.4455 | 10.3486 | 10.1588 | 9.8904 | 9.6149 | 9.2547 | 8.8792 | 8.6384 | 7.8129 | 7.3659 | 7.2547 | 10.1833 | 10.1108 | 10.0343 | 9.8598 | 9.6169 | 9.3996 | 9.1669 | 8.8894 | 8.671 | 7.8016 | 6.4945 | 3.4588 | 10.5537 | 10.4669 | 10.3812 | 10.1976 | 9.9322 | 9.6935 | 9.4149 | 9.0986 | 8.8567 | 8.1465 | 7.8271 | 7.6935
|  | DORCAN SOUTH PRIMARY | EE |  |  |  |  | 10.5496 | 10.4455 | 10.3486 | 10.1996 | 9.9149 | 9.6394 | 9.2547 | 8.8792 | 8.6384 | 7.8129 | 7.3955 | 7.4424 | 10.1833 | 10.1108 | 10.0343 | 9.9445 | 9.6873 | 9.4669 | 9.1833 | 8.8894 | 8.671 | 7.8016 | 6.8792 | 5.4986 | 10.5537 | 10.4669 | 10.3812 | 10.271 | 9.9996 | 9.7424 | 9.4149 | 9.0986 | 8.8567 | 8.1465 | 7.869 | 7.8445
|  | DORCAN SOUTH PRIMARY | HT |  |  |  |  | 10.5894 | 10.5149 | 10.421 | 10.1588 | 9.8904 | 9.6149 | 9.3098 | 9.0271 | 8.819 | 7.869 | 7.3659 | 7.2547 | 10.2322 | 10.1761 | 10.1118 | 9.8598 | 9.6169 | 9.3996 | 9.1669 | 8.9516 | 8.8149 | 8.2516 | 7.9812 | 7.8659 | 10.6057 | 10.5343 | 10.4557 | 10.1976 | 9.9322 | 9.6935 | 9.4282 | 9.171 | 8.9914 | 8.2088 | 7.8271 | 7.6935
|  | DORCAN SOUTH PRIMARY | HE |  |  |  |  | 10.6037 | 10.5333 | 10.4455 | 10.3476 | 10.1057 | 9.8659 | 9.5578 | 9.2506 | 8.9924 | 8.1302 | 7.7996 | 7.6751 | 10.2353 | 10.1822 | 10.118 | 10.0465 | 9.8139 | 9.6241 | 9.3741 | 9.1241 | 8.919 | 8.1027 | 7.2547 | 5.8312 | 10.6129 | 10.5486 | 10.4771 | 10.3924 | 10.1547 | 9.9394 | 9.6557 | 9.368 | 9.1292 | 8.3322 | 8.0649 | 7.921
|  | DORCAN SOUTH PRIMARY | CF |  |  |  |  | 10.6812 | 10.6424 | 10.6108 | 10.57 | 10.5159 | 10.3802 | 10.2241 | 10.0231 | 9.8384 | 8.9567 | 8.2833 | 7.7006 | 10.2863 | 10.2516 | 10.222 | 10.1822 | 10.1353 | 10.0078 | 9.8424 | 9.6129 | 9.3822 | 8.1363 | 6.4945 | 3.4588 | 10.67 | 10.6322 | 10.6016 | 10.5567 | 10.5027 | 10.3731 | 10.2139 | 10.0149 | 9.8271 | 8.9751 | 8.4231 | 8.0037
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER PRIMARY | MINIMUM HEADROOM | SY 69113 90401 | NO | NO | 3.209 | 9.0747 | 8.0288 | 7.2961 | 6.4104 | 5.2594 | 3.84 | 2.1063 | 0.4308 | -0.99062 | -8.9008 | -13.5029 | -15.0447 | 12.689 | 11.9686 | 11.4859 | 10.8257 | 10.1022 | 9.19 | 8.0002 | 6.8206 | 5.8482 | 0.32162 | -2.7121 | -12.4304 | 8.6553 | 7.7257 | 7.0798 | 6.243 | 5.343 | 4.09 | 2.6614 | 1.2553 | 0.11754 | -7.1294 | -10.9896 | -12.0518
|  | DORCHESTER PRIMARY | EE |  |  |  |  | 9.0747 | 8.0288 | 7.2961 | 6.4104 | 5.2594 | 3.84 | 2.1063 | 0.4308 | -0.99062 | -6.9621 | -10.5814 | -13.6284 | 12.689 | 11.9686 | 11.4859 | 10.8257 | 10.1022 | 9.19 | 8.0002 | 6.8206 | 5.8482 | 1.7584 | -2.0631 | -7.3998 | 8.6553 | 7.7257 | 7.0798 | 6.243 | 5.343 | 4.09 | 2.6614 | 1.2553 | 0.11754 | -5.6559 | -9.1814 | -11.8304
|  | DORCHESTER PRIMARY | HT |  |  |  |  | 9.6033 | 8.7665 | 7.9512 | 7.2318 | 6.7196 | 5.5971 | 4.3512 | 3.0512 | 1.7165 | -5.9753 | -11.0825 | -13.7845 | 13.2084 | 12.7226 | 12.2339 | 11.7788 | 11.4941 | 10.8665 | 10.1441 | 9.3798 | 8.4696 | 3.9277 | 1.8145 | 0.70631 | 9.1747 | 8.4584 | 7.7267 | 7.0522 | 6.589 | 5.5563 | 4.4022 | 3.1992 | 1.9604 | -5.061 | -9.6233 | -11.9478
|  | DORCHESTER PRIMARY | HE |  |  |  |  | 9.493 | 8.6175 | 7.7573 | 6.9808 | 6.3216 | 5.0043 | 3.4094 | 1.7155 | -0.056951 | -8.9008 | -13.5029 | -15.0447 | 13.0257 | 12.4451 | 11.8614 | 11.289 | 10.8675 | 10.1267 | 9.0104 | 7.7798 | 6.4726 | 0.32162 | -2.7121 | -7.5457 | 9.0686 | 8.3104 | 7.5359 | 6.8073 | 6.2767 | 5.2686 | 4.1084 | 2.7349 | 1.0288 | -7.1294 | -10.9896 | -12.0518
|  | DORCHESTER PRIMARY | CF |  |  |  |  | 10.0226 | 9.3941 | 8.8655 | 8.4124 | 7.9196 | 7.4451 | 7.1757 | 6.4114 | 5.4482 | -0.7294 | -6.3743 | -10.7416 | 13.3145 | 12.8553 | 12.4492 | 12.0471 | 11.5859 | 11.0818 | 10.7226 | 10.1033 | 9.4318 | 4.6012 | -2.1733 | -12.4304 | 9.5614 | 9.0298 | 8.5665 | 8.1379 | 7.6737 | 7.2216 | 6.9747 | 6.4175 | 5.8257 | 0.31754 | -5.0049 | -8.6478
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | DOWN GRANGE PRIMARY | MINIMUM HEADROOM | SU 61604 50238 | NO | NO | 0.99 | 9.6959 | 8.6765 | 7.5418 | 6.1469 | 4.6214 | 2.6 | 0.46633 | -1.7337 | -3.448 | -11.7592 | -18.0071 | -21.8092 | 11.499 | 10.7602 | 9.948 | 8.9673 | 7.899 | 6.5827 | 5.1235 | 3.6092 | 2.5245 | -2.8561 | -9.7337 | -26.7337 | 9.6133 | 8.6949 | 7.6571 | 6.3765 | 4.9745 | 3.1255 | 1.1337 | -0.90918 | -2.3918 | -9.5735 | -14.9133 | -17.9908
|  | DOWN GRANGE PRIMARY | EE |  |  |  |  | 9.6959 | 8.6765 | 7.5418 | 6.1469 | 4.6214 | 2.6 | 0.46633 | -1.7337 | -3.448 | -11.0378 | -16.7592 | -21.3745 | 11.499 | 10.7602 | 9.948 | 8.9673 | 7.899 | 6.5827 | 5.1235 | 3.6092 | 2.5245 | -2.8561 | -8.8857 | -18.0316 | 9.6133 | 8.6949 | 7.6571 | 6.3765 | 4.9745 | 3.1255 | 1.1337 | -0.90918 | -2.3918 | -8.9867 | -13.8071 | -17.6367
|  | DOWN GRANGE PRIMARY | HT |  |  |  |  | 9.8745 | 8.8898 | 8.1827 | 6.9694 | 5.601 | 3.5888 | 1.648 | -0.3398 | -2.1939 | -11.7592 | -18.0071 | -21.8092 | 11.8551 | 11.2724 | 10.9806 | 10.3184 | 9.55 | 8.5367 | 7.5061 | 6.4367 | 5.4061 | 0.59592 | -2.0031 | -3.4265 | 9.801 | 8.9255 | 8.3327 | 7.2765 | 6.0571 | 4.2847 | 2.549 | 0.76429 | -0.92041 | -9.5735 | -14.9133 | -17.9908
|  | DOWN GRANGE PRIMARY | HE |  |  |  |  | 9.9531 | 9.0255 | 8.3847 | 7.248 | 5.9908 | 4.4633 | 2.9306 | 1.3245 | -0.31224 | -8.2592 | -13.8316 | -16.552 | 11.7214 | 11.0684 | 10.7071 | 9.9571 | 9.1296 | 8.1571 | 7.1133 | 5.9959 | 4.8276 | -1.3969 | -7.4296 | -15.8061 | 9.8673 | 9.0429 | 8.5122 | 7.5224 | 6.4204 | 5.0602 | 3.6724 | 2.2204 | 0.73776 | -6.4276 | -11.1418 | -13.3398
|  | DOWN GRANGE PRIMARY | CF |  |  |  |  | 10.8327 | 10.4082 | 9.9122 | 9.6337 | 8.8071 | 7.3847 | 6.5378 | 5.8102 | 5.0571 | -0.62041 | -5.9776 | -11.0194 | 12.0939 | 11.6704 | 11.1724 | 10.9143 | 10.198 | 9.1459 | 8.2745 | 7.4173 | 6.5061 | -0.059184 | -9.7337 | -26.7337 | 10.6041 | 10.2173 | 9.7643 | 9.5571 | 8.848 | 7.6786 | 6.8939 | 6.1949 | 5.4663 | 0.19592 | -4.4878 | -8.8959
MINETY GSP | STRATTON (MAIN) BSP | DRAKES WAY PRIMARY | MINIMUM HEADROOM | SU 16899 85647 | NO | NO | 0.98 | 7.9673 | 7.852 | 7.7173 | 7.3316 | 6.8184 | 6.3776 | 5.9071 | 5.4347 | 5.0265 | 4.0051 | 3.6051 | 3.3939 | 8.3908 | 8.3173 | 8.2398 | 7.8 | 7.3286 | 6.9653 | 6.5898 | 6.2408 | 5.9755 | 5.2214 | 3.499 | -0.14286 | 7.7643 | 7.6827 | 7.5959 | 7.1949 | 6.7306 | 6.3398 | 5.9082 | 5.5235 | 5.1776 | 4.1612 | 3.7214 | 3.5071
|  | DRAKES WAY PRIMARY | EE |  |  |  |  | 7.9673 | 7.852 | 7.7173 | 7.552 | 6.9918 | 6.5265 | 5.9704 | 5.4347 | 5.0265 | 4.0378 | 3.7918 | 3.7908 | 8.3908 | 8.3173 | 8.2398 | 8.1418 | 7.6102 | 7.2296 | 6.7714 | 6.3133 | 5.9755 | 5.2214 | 4.2653 | 2.5673 | 7.7643 | 7.6827 | 7.5959 | 7.4724 | 6.9551 | 6.5327 | 6.0327 | 5.5429 | 5.1776 | 4.2061 | 3.9357 | 3.9837
|  | DRAKES WAY PRIMARY | HT |  |  |  |  | 8.0592 | 7.9776 | 7.8827 | 7.3316 | 6.8184 | 6.3776 | 5.9071 | 5.4827 | 5.1898 | 4.1286 | 3.6694 | 3.498 | 8.4551 | 8.4031 | 8.3459 | 7.8 | 7.3286 | 6.9653 | 6.5898 | 6.2408 | 6.0337 | 5.3929 | 5.1245 | 5.0061 | 7.8316 | 7.7694 | 7.702 | 7.1949 | 6.7306 | 6.3398 | 5.9082 | 5.5235 | 5.2755 | 4.2949 | 3.8071 | 3.6531
|  | DRAKES WAY PRIMARY | HE |  |  |  |  | 8.0541 | 7.9694 | 7.8694 | 7.7429 | 7.2204 | 6.8082 | 6.2847 | 5.7663 | 5.3173 | 4.0051 | 3.6051 | 3.3939 | 8.451 | 8.3929 | 8.3347 | 8.2571 | 7.7582 | 7.4143 | 6.9857 | 6.5439 | 6.1735 | 5.2367 | 4.4398 | 2.6857 | 7.8306 | 7.7673 | 7.7 | 7.6184 | 7.1541 | 6.7827 | 6.302 | 5.8286 | 5.4276 | 4.1612 | 3.7214 | 3.5071
|  | DRAKES WAY PRIMARY | CF |  |  |  |  | 8.1408 | 8.0959 | 8.0429 | 7.9878 | 7.9204 | 7.6571 | 7.3163 | 6.9337 | 6.5745 | 4.9939 | 4.1765 | 3.6051 | 8.502 | 8.4673 | 8.4276 | 8.3878 | 8.3347 | 8.0469 | 7.7112 | 7.3306 | 6.9857 | 5.4653 | 3.499 | -0.14286 | 7.8918 | 7.8592 | 7.8184 | 7.7786 | 7.7296 | 7.4898 | 7.1939 | 6.8551 | 6.5214 | 5.102 | 4.3694 | 3.7439
NURSLING GSP | WINCHESTER BSP | DUNBRIDGE PRIMARY | MINIMUM HEADROOM | SU 31520 26244 | NO | NO | 1.591 | 0.7763 | 0.26711 | -0.84717 | -1.4186 | -4.4094 | -5.891 | -7.5308 | -7.8706 | -8.8319 | -16.6768 | -23.5615 | -29.2951 | 2.9467 | 2.3906 | 1.0875 | 0.46507 | -3.1717 | -4.8819 | -6.7666 | -7.0268 | -7.7819 | -17.0217 | -25.7666 | -33.6441 | 2.4079 | 1.8365 | 0.49875 | -0.1635 | -3.8462 | -5.6002 | -7.5584 | -7.891 | -8.9574 | -18.3574 | -26.7615 | -33.6104
|  | DUNBRIDGE PRIMARY | EE |  |  |  |  | 0.7763 | 0.46609 | 0.25793 | -0.01962 | -1.0962 | -2.2655 | -2.2941 | -3.9462 | -4.8604 | -10.6319 | -21.8727 | -27.2288 | 2.9467 | 2.6896 | 2.5375 | 2.3202 | 1.1059 | -0.1584 | -0.11452 | -2.0013 | -3.0064 | -9.5349 | -23.7768 | -31.4441 | 2.4079 | 2.1038 | 1.9059 | 1.6334 | 0.36405 | -0.99615 | -0.95636 | -2.9186 | -3.9717 | -10.6706 | -24.4982 | -31.0798
|  | DUNBRIDGE PRIMARY | HT |  |  |  |  | 0.81813 | 0.38242 | -0.30431 | -0.50738 | -2.8921 | -4.3829 | -6.1206 | -6.7574 | -8.8319 | -15.8451 | -19.0502 | -29.2951 | 3.0161 | 2.5804 | 1.8222 | 1.6804 | -1.1727 | -2.8421 | -4.8145 | -5.4013 | -7.7819 | -15.7186 | -19.1859 | -31.6645 | 2.4804 | 1.9885 | 1.1824 | 0.98344 | -1.9359 | -3.6972 | -5.7706 | -6.4666 | -8.9574 | -17.2655 | -20.9727 | -33.5941
|  | DUNBRIDGE PRIMARY | HE |  |  |  |  | 0.90181 | 0.26711 | -0.84717 | -1.4186 | -4.4094 | -5.891 | -7.5308 | -7.8706 | -8.2237 | -16.6768 | -23.5615 | -29.1145 | 3.062 | 2.3906 | 1.0875 | 0.46507 | -3.1717 | -4.8819 | -6.7666 | -7.0268 | -7.3043 | -17.0217 | -25.7666 | -33.6441 | 2.5498 | 1.8365 | 0.49875 | -0.1635 | -3.8462 | -5.6002 | -7.5584 | -7.891 | -8.2339 | -18.3574 | -26.7615 | -33.6104
|  | DUNBRIDGE PRIMARY | CF |  |  |  |  | 0.97732 | 0.83854 | 0.60589 | 0.19058 | -0.34513 | -1.0166 | -1.5186 | -2.0972 | -2.8421 | -7.34 | -13.7217 | -19.9023 | 3.1038 | 2.9977 | 2.8049 | 2.3528 | 1.7498 | 0.96507 | 0.38752 | -0.27574 | -1.1472 | -6.7074 | -15.0441 | -24.3757 | 2.6171 | 2.4783 | 2.259 | 1.7875 | 1.1651 | 0.36507 | -0.20023 | -0.87064 | -1.7472 | -7.0482 | -14.7451 | -22.1584
EALING GSP |  | EALING PRIMARY | MINIMUM HEADROOM | SZ 06789 95116 | NO | NO | 17.45 | 59.7824 | 58.3783 | 57.2579 | 55.4405 | 53.4181 | 51.2691 | 49.1028 | 47.0028 | 45.4681 | 39.5426 | 34.3099 | 31.6742 | 65.2416 | 64.1099 | 63.4038 | 62.1722 | 60.5283 | 58.865 | 57.1497 | 55.4191 | 54.0936 | 47.911 | 37.8334 | 15.0497 | 58.6579 | 57.3844 | 56.4161 | 54.8895 | 52.9916 | 51.0079 | 48.9865 | 47.0089 | 45.5548 | 40.0212 | 35.4303 | 33.1426
|  | EALING PRIMARY | EE |  |  |  |  | 59.7824 | 58.3783 | 57.2579 | 55.5854 | 53.4181 | 51.2691 | 49.1028 | 47.0028 | 45.4681 | 39.5426 | 35.1742 | 32.4171 | 65.2416 | 64.1099 | 63.4038 | 62.1722 | 60.5283 | 58.865 | 57.1497 | 55.4191 | 54.0936 | 47.911 | 40.6793 | 28.9732 | 58.6579 | 57.3844 | 56.4161 | 54.9599 | 52.9916 | 51.0079 | 48.9865 | 47.0089 | 45.5548 | 40.0212 | 36.1946 | 33.7467
|  | EALING PRIMARY | HT |  |  |  |  | 60.0916 | 58.8283 | 57.3865 | 55.4405 | 53.814 | 52.0865 | 50.6303 | 49.062 | 47.6242 | 40.2661 | 34.3099 | 31.6742 | 65.8722 | 65.1181 | 64.2487 | 62.9814 | 62.0691 | 60.9497 | 59.913 | 58.7834 | 57.7354 | 53.2997 | 50.4273 | 49.3589 | 59.0079 | 57.914 | 56.6507 | 54.8895 | 53.4242 | 51.8538 | 50.4773 | 49.0089 | 47.6467 | 40.7926 | 35.4303 | 33.1426
|  | EALING PRIMARY | HE |  |  |  |  | 60.2763 | 59.1303 | 57.9222 | 56.5222 | 54.9722 | 53.2814 | 51.664 | 50.1007 | 48.6722 | 42.811 | 38.8936 | 37.4334 | 65.7824 | 64.9365 | 64.0528 | 63.0467 | 62.0405 | 60.7507 | 59.4671 | 58.1405 | 56.8181 | 50.1283 | 42.8293 | 31.7691 | 59.1518 | 58.1344 | 57.062 | 55.8242 | 54.4528 | 52.9191 | 51.4487 | 49.9997 | 48.6548 | 43.1538 | 39.664 | 38.4089
|  | EALING PRIMARY | CF |  |  |  |  | 60.9507 | 60.3691 | 59.7099 | 59.062 | 58.3824 | 57.9732 | 57.1487 | 56.111 | 54.9518 | 48.8293 | 44.6558 | 40.5701 | 66.0742 | 65.4467 | 64.765 | 64.0446 | 63.2181 | 62.5436 | 61.4405 | 60.2191 | 58.8967 | 50.314 | 37.8334 | 15.0497 | 59.7344 | 59.1936 | 58.5814 | 57.9783 | 57.3385 | 56.9558 | 56.1916 | 55.2783 | 54.2752 | 48.5722 | 44.7477 | 41.0967
LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT PRIMARY | MINIMUM HEADROOM | TQ 08394 73826 | NO | NO | 17.259 | 6.6949 | 5.9153 | 4.9082 | 3.8204 | 2.302 | 0.26224 | -2.1847 | -4.4541 | -6.5347 | -14.1684 | -18.651 | -20.2 | 11.4102 | 10.9194 | 10.3561 | 9.548 | 8.3622 | 6.6388 | 4.552 | 2.6653 | 0.88469 | -4.9643 | -9.001 | -19.6837 | 6.2622 | 5.5153 | 4.6704 | 3.649 | 2.1857 | 0.11327 | -2.3724 | -4.6459 | -6.7571 | -14.1224 | -18.55 | -20.2184
|  | EAST BEDFONT PRIMARY | EE |  |  |  |  | 6.6949 | 5.9153 | 4.9082 | 3.8204 | 2.302 | 0.26224 | -2.1847 | -4.4541 | -6.5347 | -13.2918 | -15.3694 | -17.3929 | 11.4102 | 10.9194 | 10.3561 | 9.548 | 8.3622 | 6.6388 | 4.552 | 2.6653 | 0.88469 | -4.5837 | -9.001 | -16.1602 | 6.2622 | 5.5153 | 4.6704 | 3.649 | 2.1857 | 0.11327 | -2.3724 | -4.6459 | -6.7571 | -13.4776 | -15.5439 | -17.8959
|  | EAST BEDFONT PRIMARY | HT |  |  |  |  | 7.4408 | 7.0337 | 6.5816 | 5.8286 | 4.8653 | 3.4082 | 1.5214 | -0.41531 | -2.4173 | -10.2622 | -14.8357 | -17.548 | 11.9408 | 11.6837 | 11.399 | 10.8745 | 10.2908 | 9.0827 | 7.4327 | 5.7837 | 4.0551 | -2.249 | -5.3949 | -6.8643 | 6.8939 | 6.4041 | 5.9082 | 5.1602 | 4.3265 | 3.0551 | 1.2031 | -0.74592 | -2.7898 | -10.7153 | -15.6265 | -18.2633
|  | EAST BEDFONT PRIMARY | HE |  |  |  |  | 7.1622 | 6.602 | 5.9031 | 4.9796 | 3.6847 | 2.0949 | -0.0020408 | -2.0367 | -4.2245 | -14.1684 | -18.651 | -20.2 | 11.7276 | 11.3439 | 10.9245 | 10.4245 | 9.4347 | 8.1122 | 6.3531 | 4.7398 | 2.9776 | -4.9643 | -8.5051 | -15.2459 | 6.7776 | 6.2316 | 5.6776 | 4.7694 | 3.5224 | 1.9214 | -0.1898 | -2.1796 | -4.3316 | -14.1224 | -18.55 | -20.2184
|  | EAST BEDFONT PRIMARY | CF |  |  |  |  | 7.6929 | 7.3898 | 7.0051 | 6.598 | 6.102 | 5.2571 | 4.1082 | 2.9602 | 1.6806 | -5.7102 | -10.8776 | -13.951 | 12.0306 | 11.8031 | 11.5122 | 11.1816 | 10.7214 | 9.8939 | 8.8122 | 7.9286 | 6.8714 | 0.24184 | -7.5245 | -19.6837 | 7.2153 | 6.9224 | 6.5429 | 6.1786 | 5.7316 | 4.9541 | 3.7878 | 2.6143 | 1.3276 | -5.8653 | -10.8122 | -13.699
MANNINGTON GSP | REDHILL BSP | EAST HOWE PRIMARY | MINIMUM HEADROOM | SZ 06789 95116 | NO | NO | 8.334 | -0.41111 | -1.2897 | -2.2621 | -3.3346 | -4.4683 | -6.1213 | -7.7958 | -9.4642 | -10.6856 | -17.958 | -23.2917 | -26.2142 | 1.7057 | 1.0791 | 0.3873 | -0.39331 | -1.2178 | -2.2974 | -3.4566 | -4.6352 | -5.4668 | -10.1913 | -15.6198 | -29.4219 | -0.5864 | -1.3823 | -2.2721 | -3.2548 | -4.318 | -5.8497 | -7.4466 | -9.0405 | -10.1119 | -16.3772 | -20.9425 | -23.4548
|  | EAST HOWE PRIMARY | EE |  |  |  |  | -0.41111 | -1.2897 | -2.2621 | -3.3346 | -4.4683 | -6.1213 | -7.7958 | -9.4642 | -10.6856 | -17.1172 | -22.0662 | -25.6958 | 1.7057 | 1.0791 | 0.3873 | -0.39331 | -1.2178 | -2.2974 | -3.4566 | -4.6352 | -5.4668 | -10.1913 | -15.2943 | -22.5739 | -0.5864 | -1.3823 | -2.2721 | -3.2548 | -4.318 | -5.8497 | -7.4466 | -9.0405 | -10.1119 | -15.717 | -19.9068 | -23.0497
|  | EAST HOWE PRIMARY | HT |  |  |  |  | -0.27233 | -1.1336 | -1.7142 | -2.6121 | -3.6029 | -5.1387 | -6.6468 | -8.2274 | -9.8305 | -17.958 | -23.2917 | -26.2142 | 1.9812 | 1.4689 | 1.1975 | 0.68322 | 0.11383 | -0.67903 | -1.4994 | -2.3719 | -3.2607 | -7.4678 | -9.8137 | -11.0382 | -0.43436 | -1.2068 | -1.6986 | -2.5007 | -3.3925 | -4.766 | -6.1384 | -7.5752 | -9.0374 | -16.3772 | -20.9425 | -23.4548
|  | EAST HOWE PRIMARY | HE |  |  |  |  | -0.15805 | -0.94682 | -1.454 | -2.2887 | -3.1836 | -4.3948 | -5.5723 | -6.804 | -8.0927 | -14.7989 | -19.607 | -21.9172 | 1.9036 | 1.3465 | 1.0271 | 0.4373 | -0.20046 | -0.99127 | -1.8229 | -2.7137 | -3.6627 | -9.0025 | -14.1005 | -20.8576 | -0.33538 | -1.0425 | -1.4701 | -2.218 | -3.0221 | -4.1119 | -5.1956 | -6.3313 | -7.517 | -13.5935 | -17.6844 | -19.6619
|  | EAST HOWE PRIMARY | CF |  |  |  |  | 0.29807 | -0.1907 | -0.76111 | -1.0387 | -1.6458 | -2.1907 | -2.6887 | -3.207 | -3.7489 | -7.9907 | -12.8978 | -17.5234 | 2.0975 | 1.6832 | 1.2016 | 0.9424 | 0.38016 | -0.20964 | -0.83617 | -1.4943 | -2.2056 | -7.426 | -15.6198 | -29.4219 | 0.07891 | -0.3568 | -0.86803 | -1.0844 | -1.618 | -2.1027 | -2.569 | -3.0578 | -3.5925 | -7.6517 | -11.9221 | -15.9905
MELKSHAM GSP | NORRINGTON BSP | EASTERTON PRIMARY | MINIMUM HEADROOM | SU 01568 54730 | NO | YES | 1.567 | 5.4165 | 5.1165 | 4.8665 | 4.5196 | 4.1431 | 4.2818 | 3.8686 | 3.438 | 3.2053 | 1.9808 | 1.5614 | 1.1706 | 7.689 | 7.4747 | 7.2931 | 7.039 | 6.7584 | 6.8318 | 6.5227 | 6.2043 | 6.038 | 5.1216 | 3.6237 | 0.35429 | 5.5604 | 5.2655 | 5.0206 | 4.6808 | 4.3135 | 4.4594 | 4.0614 | 3.6522 | 3.441 | 2.389 | 2.0339 | 1.7094
|  | EASTERTON PRIMARY | EE |  |  |  |  | 5.4165 | 5.1165 | 4.8665 | 4.5196 | 4.1431 | 4.2818 | 3.8686 | 3.438 | 3.2053 | 1.9808 | 1.5614 | 1.3747 | 7.689 | 7.4747 | 7.2931 | 7.039 | 6.7584 | 6.8318 | 6.5227 | 6.2043 | 6.038 | 5.1216 | 4.191 | 2.6624 | 5.5604 | 5.2655 | 5.0206 | 4.6808 | 4.3135 | 4.4594 | 4.0614 | 3.6522 | 3.441 | 2.389 | 2.0339 | 1.8808
|  | EASTERTON PRIMARY | HT |  |  |  |  | 5.5849 | 5.389 | 5.2155 | 4.9788 | 4.7288 | 4.3563 | 3.9829 | 3.639 | 3.641 | 2.2451 | 1.5961 | 1.1706 | 7.8645 | 7.7257 | 7.6176 | 7.4512 | 7.3033 | 7.0655 | 6.8104 | 6.5604 | 6.7124 | 5.8655 | 5.5349 | 5.3441 | 5.7349 | 5.542 | 5.3808 | 5.1543 | 4.9237 | 4.5696 | 4.2022 | 3.8594 | 3.9186 | 2.6155 | 2.0563 | 1.7094
|  | EASTERTON PRIMARY | HE |  |  |  |  | 5.5829 | 5.39 | 5.2186 | 4.9951 | 4.7737 | 4.4655 | 4.0951 | 3.6869 | 3.7033 | 2.1604 | 1.738 | 1.5696 | 7.8339 | 7.6788 | 7.5573 | 7.3778 | 7.2196 | 6.9859 | 6.7002 | 6.39 | 6.5176 | 5.2706 | 4.3145 | 2.7706 | 5.7318 | 5.5431 | 5.3859 | 5.1716 | 4.9624 | 4.6645 | 4.2992 | 3.9094 | 3.9798 | 2.5696 | 2.2033 | 2.0716
|  | EASTERTON PRIMARY | CF |  |  |  |  | 5.6369 | 5.4818 | 5.341 | 5.1747 | 4.9951 | 4.841 | 4.6288 | 4.388 | 4.1298 | 3.2288 | 2.4318 | 1.7747 | 7.8676 | 7.742 | 7.6339 | 7.491 | 7.3237 | 7.1778 | 6.9594 | 6.7196 | 6.4614 | 5.438 | 3.6237 | 0.35429 | 5.789 | 5.6441 | 5.5176 | 5.3573 | 5.1859 | 5.04 | 4.8318 | 4.5951 | 4.3339 | 3.5216 | 2.8002 | 2.2369
FLEET-BRAMLEY GSP | BRACKNELL BSP | EASTHAMPSTEAD PRIMARY | MINIMUM HEADROOM | SU 86148 67194 | NO | NO | 3.474 | 9.1676 | 8.4605 | 8.0493 | 7.2095 | 6.1554 | 4.3676 | 2.4227 | 0.70437 | -0.70073 | -8.1242 | -14.5334 | -18.3711 | 12.188 | 11.5901 | 11.2544 | 10.5656 | 9.7472 | 8.4238 | 6.9258 | 5.5666 | 4.4299 | -1.2864 | -7.0579 | -20.6589 | 8.6309 | 7.8574 | 7.587 | 6.7544 | 5.7431 | 4.0503 | 2.1646 | 0.46967 | -0.8742 | -7.563 | -13.4018 | -16.6722
|  | EASTHAMPSTEAD PRIMARY | EE |  |  |  |  | 9.1676 | 8.4605 | 8.0493 | 7.2095 | 6.1554 | 4.3676 | 2.4227 | 0.70437 | -0.70073 | -7.765 | -13.0864 | -17.4732 | 12.188 | 11.5901 | 11.2544 | 10.5656 | 9.7472 | 8.4238 | 6.9258 | 5.5666 | 4.4299 | -1.2864 | -7.0579 | -15.4793 | 8.6309 | 7.8574 | 7.587 | 6.7544 | 5.7431 | 4.0503 | 2.1646 | 0.46967 | -0.8742 | -7.2354 | -11.8946 | -15.7109
|  | EASTHAMPSTEAD PRIMARY | HT |  |  |  |  | 9.534 | 9.0238 | 8.4462 | 7.7717 | 7.2156 | 5.6544 | 4.0003 | 2.5054 | 0.93702 | -8.1242 | -14.5334 | -18.3711 | 12.6901 | 12.3533 | 11.9574 | 11.4942 | 11.1982 | 10.2074 | 9.1084 | 8.1156 | 7.0482 | 1.6972 | -1.8028 | -3.6916 | 9.1717 | 8.6615 | 8.0656 | 7.3646 | 6.9605 | 5.4891 | 3.9023 | 2.4564 | 0.92171 | -7.563 | -13.4018 | -16.6722
|  | EASTHAMPSTEAD PRIMARY | HE |  |  |  |  | 9.6095 | 9.085 | 8.5227 | 7.8911 | 7.3952 | 6.1095 | 4.7329 | 3.5625 | 2.3595 | -4.4997 | -9.812 | -12.415 | 12.5931 | 12.1748 | 11.7084 | 11.1687 | 10.8013 | 9.8625 | 8.7911 | 7.8778 | 6.9115 | 1.0411 | -4.8028 | -12.4334 | 9.2278 | 8.7197 | 8.1472 | 7.5013 | 7.1595 | 5.9595 | 4.6289 | 3.5176 | 2.3656 | -4.0018 | -8.5977 | -10.8518
|  | EASTHAMPSTEAD PRIMARY | CF |  |  |  |  | 10.0636 | 9.7268 | 9.438 | 9.0656 | 8.534 | 8.2064 | 7.5105 | 6.9391 | 6.3758 | 2.0319 | -2.7191 | -7.0232 | 12.7972 | 12.4401 | 12.1044 | 11.6687 | 11.1023 | 10.6176 | 9.7687 | 8.9789 | 8.1707 | 2.6482 | -5.9997 | -20.6589 | 9.6187 | 9.2503 | 8.9401 | 8.5299 | 7.987 | 7.7901 | 7.0727 | 6.4595 | 5.8564 | 1.7727 | -2.3783 | -6.0956
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH PRIMARY | MINIMUM HEADROOM | SU 45426 18958 | NO | YES | 5.402 | 7.4135 | 5.6441 | 3.6471 | 1.9951 | 0.1849 | -1.7447 | -3.8967 | -6.0161 | -7.6182 | -16.2314 | -23.5192 | -27.6794 | 14.7778 | 13.6961 | 12.4941 | 11.3992 | 10.2002 | 8.8982 | 7.4084 | 5.9033 | 4.789 | -1.2569 | -7.6631 | -24.411 | 8.9716 | 7.538 | 5.8982 | 4.4676 | 2.8329 | 1.0604 | -0.93449 | -2.8978 | -4.3437 | -11.7804 | -18.1365 | -21.7171
|  | EASTLEIGH NORTH PRIMARY | EE |  |  |  |  | 7.4135 | 5.6441 | 3.6471 | 1.9951 | 0.1849 | -1.7447 | -3.8967 | -6.0161 | -7.6182 | -15.9365 | -22.1947 | -26.9855 | 14.7778 | 13.6961 | 12.4941 | 11.3992 | 10.2002 | 8.8982 | 7.4084 | 5.9033 | 4.789 | -1.2569 | -7.3376 | -16.2896 | 8.9716 | 7.538 | 5.8982 | 4.4676 | 2.8329 | 1.0604 | -0.93449 | -2.8978 | -4.3437 | -11.6988 | -17.0651 | -21.2049
|  | EASTLEIGH NORTH PRIMARY | HT |  |  |  |  | 7.688 | 5.9869 | 4.4267 | 3.0278 | 1.4267 | -0.30388 | -2.0967 | -3.9376 | -5.8376 | -16.2314 | -23.5192 | -27.6794 | 15.1839 | 14.2696 | 13.5318 | 12.7961 | 11.9482 | 11.0502 | 10.0451 | 8.9747 | 7.8553 | 2.291 | -1.0641 | -2.76 | 9.2145 | 7.839 | 6.5727 | 5.3645 | 3.9869 | 2.4635 | 0.87673 | -0.75082 | -2.4416 | -11.7804 | -18.1365 | -21.7171
|  | EASTLEIGH NORTH PRIMARY | HE |  |  |  |  | 7.6982 | 6.0288 | 4.5022 | 3.1431 | 1.6308 | 0.19 | -1.3906 | -2.9988 | -4.6478 | -13.6824 | -20.158 | -23.0661 | 15.0063 | 14.0002 | 13.1778 | 12.3329 | 11.391 | 10.4441 | 9.3757 | 8.2165 | 6.9737 | -0.0089796 | -6.4937 | -14.6692 | 9.2186 | 7.8635 | 6.6227 | 5.441 | 4.1267 | 2.8482 | 1.4451 | 0.012449 | -1.4518 | -9.558 | -15.2763 | -17.7253
|  | EASTLEIGH NORTH PRIMARY | CF |  |  |  |  | 8.3176 | 7.0686 | 5.6553 | 4.9737 | 3.9961 | 3.4522 | 2.7829 | 2.0124 | 1.1706 | -4.8273 | -11.2161 | -17.1467 | 15.2849 | 14.4706 | 13.5635 | 13.0931 | 12.3339 | 11.6859 | 10.9104 | 10.0655 | 9.139 | 2.3982 | -7.6631 | -24.411 | 9.788 | 8.8145 | 7.6829 | 7.1135 | 6.2798 | 5.8124 | 5.2329 | 4.5982 | 3.8237 | -1.6763 | -7.3886 | -12.559
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY PRIMARY | MINIMUM HEADROOM | SZ 66357 99040 | NO | YES | 0.602 | 15.0869 | 14.79 | 14.4838 | 14.094 | 13.6634 | 13.1073 | 12.4104 | 11.7185 | 11.193 | 9.3063 | 7.8053 | 7.8022 | 16.6971 | 16.3981 | 16.0869 | 15.6971 | 15.2624 | 14.7593 | 14.142 | 13.5114 | 12.9644 | 9.9787 | 3.8512 | -8.8917 | 15.5461 | 15.2563 | 14.9512 | 14.5675 | 14.142 | 13.6134 | 12.942 | 12.2777 | 11.7685 | 9.9369 | 8.6063 | 8.6124
|  | EASTNEY PRIMARY | EE |  |  |  |  | 15.0869 | 14.79 | 14.4838 | 14.094 | 13.6634 | 13.1073 | 12.4104 | 11.7185 | 11.193 | 9.3063 | 8.4083 | 8.5308 | 16.6971 | 16.3981 | 16.0869 | 15.6971 | 15.2624 | 14.7593 | 14.142 | 13.5114 | 12.9644 | 9.9787 | 6.4277 | 0.54199 | 15.5461 | 15.2563 | 14.9512 | 14.5675 | 14.142 | 13.6134 | 12.942 | 12.2777 | 11.7685 | 9.9369 | 9.1634 | 9.242
|  | EASTNEY PRIMARY | HT |  |  |  |  | 15.3328 | 15.1226 | 14.9155 | 14.6624 | 14.3553 | 13.9502 | 13.4338 | 12.89 | 12.3532 | 9.4828 | 7.8053 | 7.8022 | 17.0012 | 16.8471 | 16.6879 | 16.4981 | 16.2726 | 16.0063 | 15.6634 | 15.2991 | 14.9359 | 13.0573 | 11.9869 | 11.8624 | 15.7879 | 15.5859 | 15.3797 | 15.1277 | 14.8318 | 14.441 | 13.9471 | 13.4175 | 12.892 | 10.14 | 8.6063 | 8.6124
|  | EASTNEY PRIMARY | HE |  |  |  |  | 15.3297 | 15.141 | 14.9624 | 14.742 | 14.4859 | 14.1359 | 13.693 | 13.2287 | 12.8053 | 10.9277 | 10.0695 | 9.9287 | 16.8746 | 16.6532 | 16.4348 | 16.1685 | 15.8624 | 15.5073 | 15.0695 | 14.6012 | 14.1216 | 11.0961 | 7.5063 | 1.5012 | 15.7859 | 15.6063 | 15.4297 | 15.2124 | 14.9604 | 14.6318 | 14.2002 | 13.7512 | 13.3328 | 11.4961 | 10.7318 | 10.6216
|  | EASTNEY PRIMARY | CF |  |  |  |  | 15.4838 | 15.3675 | 15.2665 | 15.1297 | 14.9879 | 14.8185 | 14.642 | 14.4083 | 14.1655 | 12.7012 | 11.0665 | 9.543 | 16.9338 | 16.7389 | 16.5328 | 16.2838 | 15.9787 | 15.6114 | 15.2042 | 14.743 | 14.244 | 10.6206 | 3.8512 | -8.8917 | 15.9338 | 15.8236 | 15.7226 | 15.5879 | 15.4461 | 15.2818 | 15.1083 | 14.8808 | 14.643 | 13.2195 | 11.6604 | 10.2481
LALEHAM GSP | STAINES BSP | EGHAM PRIMARY | MINIMUM HEADROOM | TQ 01030 71404 | NO | NO | 4.555 | 1.7255 | 0.37245 | -1.0592 | 25.9735 | 24.3592 | 22.5755 | 20.4755 | 18.4643 | 16.7704 | 7.0735 | 1.9796 | 0.64286 | 8.1204 | 7.1663 | 33.1112 | 32.2194 | 31.2449 | 29.9888 | 28.3469 | 26.7837 | 25.4939 | 17.8286 | 14.1776 | 7.6082 | 2.4867 | 1.2143 | 27.7949 | 26.6776 | 25.4663 | 23.8306 | 21.701 | 19.6663 | 17.9796 | 8.0265 | 3.1827 | 2.2694
|  | EGHAM PRIMARY | EE |  |  |  |  | 1.7255 | 0.37245 | -1.0592 | 25.9735 | 24.3592 | 22.5755 | 20.4755 | 18.4643 | 16.7704 | 10.5612 | 8.1602 | 6.5765 | 8.1204 | 7.1663 | 33.1112 | 32.2194 | 31.2449 | 29.9888 | 28.3469 | 26.7837 | 25.4939 | 21.4296 | 18.6041 | 13.4337 | 2.4867 | 1.2143 | 27.7949 | 26.6776 | 25.4663 | 23.8306 | 21.701 | 19.6663 | 17.9796 | 12.4214 | 10.9296 | 9.1316
|  | EGHAM PRIMARY | HT |  |  |  |  | 2.952 | 1.9439 | 0.72857 | 28.2092 | 27.0133 | 25.8306 | 24.2816 | 22.649 | 20.9633 | 12.9673 | 8.7245 | 7.0347 | 8.8469 | 8.1673 | 34.1622 | 33.55 | 32.8602 | 32.4245 | 31.5816 | 30.6806 | 29.4969 | 24.0194 | 21.552 | 20.9418 | 3.2571 | 2.248 | 28.7949 | 27.9265 | 26.9531 | 26.1306 | 24.9133 | 23.6439 | 22.3347 | 15.4418 | 11.4561 | 9.5051
|  | EGHAM PRIMARY | HE |  |  |  |  | 2.4602 | 1.2694 | -0.12347 | 27.0071 | 25.4469 | 23.9388 | 21.9388 | 19.8184 | 17.5765 | 7.0735 | 1.9796 | 0.64286 | 8.5918 | 7.7929 | 33.648 | 32.8694 | 31.9888 | 31.1071 | 29.5071 | 27.7939 | 25.9908 | 17.8286 | 14.1776 | 12.1857 | 3.0684 | 1.9908 | 28.4449 | 27.4163 | 26.2714 | 25.2337 | 23.1612 | 20.9531 | 18.6357 | 8.0265 | 3.1827 | 2.2694
|  | EGHAM PRIMARY | CF |  |  |  |  | 3.3969 | 2.6663 | 1.7612 | 29.5796 | 28.7245 | 27.9439 | 27.0306 | 25.8663 | 24.6286 | 17.1531 | 10.5857 | 6.2531 | 8.9663 | 8.3908 | 34.4316 | 33.9347 | 33.3337 | 32.7163 | 32.2755 | 31.501 | 30.6847 | 25.1592 | 17.9082 | 7.6082 | 3.6214 | 2.8837 | 29.6316 | 29.0806 | 28.4255 | 27.849 | 27.5449 | 26.8245 | 25.8306 | 18.1806 | 11.5378 | 7.6347
MANNINGTON GSP | BOURNEMOUTH BSP | ELECTRIC HOUSE PRIMARY | MINIMUM HEADROOM | SZ 08757 91379 | NO | YES | 4.559 | 8.6621 | 8.4417 | 7.8488 | 7.0488 | 6.1488 | 5.4611 | 4.9346 | 4.4366 | 4.004 | 2.6825 | 1.7356 | 1.6693 | 11.0009 | 10.8233 | 10.4999 | 10.0529 | 9.5499 | 9.104 | 8.6866 | 8.2693 | 7.8784 | 5.7029 | 0.91313 | -8.793 | 9.7754 | 9.5978 | 9.1244 | 8.4499 | 7.6825 | 7.0917 | 6.5886 | 6.1142 | 5.7019 | 4.4662 | 3.8295 | 3.808
|  | ELECTRIC HOUSE PRIMARY | EE |  |  |  |  | 8.6621 | 8.4417 | 7.8488 | 7.0488 | 6.1488 | 5.4611 | 4.9346 | 4.4366 | 4.004 | 2.6825 | 2.2131 | 2.1754 | 11.0009 | 10.8233 | 10.4999 | 10.0529 | 9.5499 | 9.104 | 8.6866 | 8.2693 | 7.8784 | 5.7029 | 3.0774 | -1.5491 | 9.7754 | 9.5978 | 9.1244 | 8.4499 | 7.6825 | 7.0917 | 6.5886 | 6.1142 | 5.7019 | 4.4662 | 4.0672 | 4.0254
|  | ELECTRIC HOUSE PRIMARY | HT |  |  |  |  | 8.8652 | 8.7162 | 8.2366 | 7.5764 | 6.7927 | 6.257 | 5.8978 | 5.5193 | 5.106 | 3.1325 | 1.8846 | 1.8478 | 11.2091 | 11.1274 | 10.9091 | 10.6152 | 10.2672 | 10.0213 | 9.8417 | 9.6478 | 9.4407 | 8.358 | 7.4652 | 7.3499 | 9.9519 | 9.8386 | 9.4886 | 8.956 | 8.2907 | 7.8488 | 7.5397 | 7.2152 | 6.8346 | 4.9968 | 3.8295 | 3.808
|  | ELECTRIC HOUSE PRIMARY | HE |  |  |  |  | 8.8376 | 8.6917 | 8.2172 | 7.5652 | 6.7988 | 6.3213 | 6.0264 | 5.7009 | 5.3437 | 2.8754 | 1.7356 | 1.7499 | 11.1019 | 10.9642 | 10.6846 | 10.3162 | 9.8672 | 9.5295 | 9.2458 | 8.9366 | 8.5682 | 6.3754 | 3.6356 | -0.76748 | 9.9142 | 9.7917 | 9.4356 | 8.9356 | 8.2866 | 7.8693 | 7.5907 | 7.3029 | 6.9846 | 5.5019 | 4.3978 | 4.4091
|  | ELECTRIC HOUSE PRIMARY | CF |  |  |  |  | 8.9856 | 8.8948 | 8.5182 | 7.9917 | 7.3795 | 7.0346 | 6.8754 | 6.706 | 6.4937 | 5.1937 | 3.1713 | 1.6693 | 11.1805 | 11.058 | 10.8152 | 10.4774 | 10.0611 | 9.7213 | 9.4305 | 9.0846 | 8.706 | 6.0284 | 0.91313 | -8.793 | 10.0407 | 9.9652 | 9.6876 | 9.2917 | 8.8274 | 8.5417 | 8.3795 | 8.208 | 8.0193 | 6.9101 | 5.7652 | 4.3397
FLEET-BRAMLEY GSP | WOKINGHAM BSP | ELMS ROAD PRIMARY | MINIMUM HEADROOM | SU 81057 68532 | NO | NO | 3.466 | 5.5237 | 4.6717 | 4.0359 | 3.1472 | 2.1961 | 0.94206 | -0.45794 | -1.9651 | -3.2008 | -9.0365 | -12.7702 | -14.7171 | 7.8598 | 7.2619 | 6.9282 | 6.319 | 5.6312 | 4.8078 | 3.8588 | 2.8568 | 2.1057 | -1.6728 | -5.8239 | -15.9851 | 5.6397 | 4.8509 | 4.353 | 3.5356 | 2.6418 | 1.4979 | 0.204 | -1.1725 | -2.2399 | -7.1164 | -10.4358 | -12.1093
|  | ELMS ROAD PRIMARY | EE |  |  |  |  | 5.5237 | 4.6717 | 4.0359 | 3.1472 | 2.1961 | 0.94206 | -0.45794 | -1.9651 | -3.2008 | -8.7049 | -11.7988 | -14.1743 | 7.8598 | 7.2619 | 6.9282 | 6.319 | 5.6312 | 4.8078 | 3.8588 | 2.8568 | 2.1057 | -1.6728 | -5.1892 | -10.4922 | 5.6397 | 4.8509 | 4.353 | 3.5356 | 2.6418 | 1.4979 | 0.204 | -1.1725 | -2.2399 | -6.9307 | -9.6327 | -11.7082
|  | ELMS ROAD PRIMARY | HT |  |  |  |  | 5.838 | 5.1319 | 4.2839 | 3.3961 | 2.8043 | 1.5921 | 0.2941 | -1.0834 | -2.4834 | -9.0365 | -12.7702 | -14.7171 | 8.271 | 7.8843 | 7.4088 | 6.8812 | 6.6568 | 6.0404 | 5.3455 | 4.6098 | 3.8496 | 0.40267 | -1.3606 | -2.2126 | 5.9979 | 5.3795 | 4.6367 | 3.8213 | 3.3642 | 2.3091 | 1.1611 | -0.052122 | -1.296 | -7.1164 | -10.4358 | -12.1093
|  | ELMS ROAD PRIMARY | HE |  |  |  |  | 5.8757 | 5.2033 | 4.387 | 3.5921 | 3.0666 | 2.088 | 0.98798 | -0.25692 | -1.5324 | -7.4202 | -10.6988 | -12.0508 | 8.1741 | 7.7414 | 7.2139 | 6.6812 | 6.4078 | 5.7843 | 5.0629 | 4.2578 | 3.4017 | -1.0116 | -4.7524 | -9.633 | 6.0213 | 5.4285 | 4.706 | 3.9867 | 3.5754 | 2.7071 | 1.7193 | 0.61012 | -0.52661 | -5.7491 | -8.646 | -9.8001
|  | ELMS ROAD PRIMARY | CF |  |  |  |  | 6.4849 | 5.9992 | 5.4666 | 4.9655 | 4.4839 | 4.0308 | 3.8574 | 3.3023 | 2.7033 | -2.5834 | -6.1263 | -9.3222 | 8.4435 | 8.0629 | 7.669 | 7.2619 | 6.8119 | 6.3129 | 6.1129 | 5.5435 | 4.9302 | 0.14655 | -5.8239 | -15.9851 | 6.5367 | 6.102 | 5.6428 | 5.1867 | 4.7387 | 4.2969 | 4.2101 | 3.6887 | 3.1275 | -1.5297 | -4.6501 | -7.4521
LOVEDEAN GSP | HAVANT BSP | EMSWORTH PRIMARY | MINIMUM HEADROOM | SU 74861 05807 | NO | YES | 7.765 | -2.9712 | -3.6498 | -4.2998 | 11.0635 | 10.24 | 9.0084 | 7.5482 | 5.9237 | 4.6053 | -2.8559 | -6.8886 | -7.7171 | -0.56304 | -1.1283 | -1.6692 | 12.589 | 11.9308 | 11.1033 | 10.1084 | 9.041 | 8.2247 | 2.7757 | -0.64161 | -9.5039 | -3.0937 | -3.7416 | -4.3641 | 10.5308 | 9.6574 | 8.5768 | 7.2696 | 5.8553 | 4.5257 | -2.7304 | -6.3834 | -6.8294
|  | EMSWORTH PRIMARY | EE |  |  |  |  | -2.9712 | -3.6498 | -4.2998 | 11.0635 | 10.24 | 9.0084 | 7.5482 | 5.9237 | 4.6053 | -1.3855 | -5.4141 | -7.3192 | -0.56304 | -1.1283 | -1.6692 | 12.589 | 11.9308 | 11.1033 | 10.1084 | 9.041 | 8.2247 | 4.1666 | 0.56451 | -3.9294 | -3.0937 | -3.7416 | -4.3641 | 10.5308 | 9.6574 | 8.5768 | 7.2696 | 5.8553 | 4.7043 | -0.43957 | -3.659 | -5.2192
|  | EMSWORTH PRIMARY | HT |  |  |  |  | -2.6151 | -2.9977 | -3.3947 | 11.737 | 11.0666 | 10.2635 | 8.9727 | 7.5186 | 6.0686 | -1.0141 | -5.661 | -7.3294 | -0.1661 | -0.44161 | -0.72222 | 13.3666 | 12.9053 | 12.5747 | 11.8563 | 11.0553 | 10.238 | 6.4278 | 4.2268 | 3.5053 | -2.7079 | -3.0855 | -3.4671 | 11.2023 | 10.5859 | 9.9033 | 8.7604 | 7.4829 | 6.2033 | 0.024714 | -3.8334 | -5.1732
|  | EMSWORTH PRIMARY | HE |  |  |  |  | -2.6283 | -3.1783 | -3.6334 | 11.49 | 10.6298 | 9.5788 | 8.139 | 6.5186 | 4.8502 | -2.8559 | -6.8886 | -7.7171 | -0.2559 | -0.71916 | -1.0977 | 12.9278 | 12.3135 | 11.6319 | 10.5931 | 9.44 | 8.2451 | 2.7757 | -0.61202 | -4.8141 | -2.7345 | -3.2641 | -3.7069 | 10.937 | 9.9778 | 8.989 | 7.6237 | 6.0982 | 4.5257 | -2.7304 | -6.3834 | -6.8294
|  | EMSWORTH PRIMARY | CF |  |  |  |  | -2.2467 | -2.46 | -2.863 | 12.5308 | 12.0859 | 11.5431 | 10.8788 | 10.5359 | 9.6737 | 4.0829 | -1.6171 | -4.6437 | -0.054878 | -0.29263 | -0.68753 | 13.5033 | 13.0737 | 12.5533 | 11.9278 | 11.6033 | 10.9482 | 6.2778 | -0.64161 | -9.5039 | -2.3865 | -2.5988 | -2.9834 | 11.9298 | 11.5227 | 11.0288 | 10.4217 | 9.9104 | 9.0808 | 3.8002 | -1.4896 | -4.1365
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | ENFORD PRIMARY | MINIMUM HEADROOM | SU 13728 51712 | NO | NO | 0.269 | 6.5431 | 6.4267 | 6.2931 | 6.1971 | 6.0471 | 5.8624 | 5.7053 | 5.4982 | 5.4329 | 5.0482 | 4.8737 | 4.7176 | 7.3304 | 7.2549 | 7.1641 | 7.1059 | 7.009 | 6.8845 | 6.7916 | 6.6529 | 6.5763 | 6.1835 | 5.6427 | 4.4416 | 6.3047 | 6.1894 | 6.0588 | 5.9649 | 5.82 | 5.6384 | 5.4853 | 5.2782 | 5.2169 | 5.0476 | 4.9496 | 4.8129
|  | ENFORD PRIMARY | EE |  |  |  |  | 6.5431 | 6.4267 | 6.2931 | 6.1971 | 6.0471 | 5.8624 | 5.7053 | 5.4982 | 5.4329 | 5.0482 | 4.8778 | 4.7931 | 7.3304 | 7.2549 | 7.1641 | 7.1059 | 7.009 | 6.8845 | 6.7916 | 6.6529 | 6.5763 | 6.1835 | 5.8182 | 5.2345 | 6.3047 | 6.1894 | 6.0588 | 5.9649 | 5.82 | 5.6384 | 5.4853 | 5.2782 | 5.2169 | 5.0476 | 4.9567 | 4.8822
|  | ENFORD PRIMARY | HT |  |  |  |  | 6.64 | 6.5522 | 6.4818 | 6.3941 | 6.2961 | 6.2012 | 6.0614 | 5.9135 | 5.7573 | 5.1349 | 4.8737 | 4.7176 | 7.4008 | 7.3437 | 7.308 | 7.2539 | 7.1876 | 7.1406 | 7.0518 | 6.9518 | 6.8467 | 6.4876 | 6.3447 | 6.261 | 6.4047 | 6.319 | 6.2598 | 6.1771 | 6.0771 | 5.9965 | 5.8578 | 5.7078 | 5.5527 | 5.0506 | 4.9496 | 4.8129
|  | ENFORD PRIMARY | HE |  |  |  |  | 6.639 | 6.5533 | 6.4839 | 6.4012 | 6.3063 | 6.2176 | 6.0808 | 5.939 | 5.7818 | 5.1451 | 4.9696 | 4.9012 | 7.3988 | 7.3427 | 7.3069 | 7.2539 | 7.1824 | 7.1192 | 7.0171 | 6.9069 | 6.7947 | 6.2569 | 5.8784 | 5.309 | 6.4037 | 6.3159 | 6.2598 | 6.1802 | 6.0812 | 6.0037 | 5.8669 | 5.721 | 5.5659 | 5.0751 | 5.0067 | 4.97
|  | ENFORD PRIMARY | CF |  |  |  |  | 6.6655 | 6.6053 | 6.538 | 6.4869 | 6.4216 | 6.342 | 6.2512 | 6.1941 | 6.1012 | 5.6104 | 5.2686 | 5.0206 | 7.4151 | 7.3722 | 7.3253 | 7.2865 | 7.2314 | 7.1692 | 7.0835 | 7.0273 | 6.9324 | 6.3702 | 5.6427 | 4.4416 | 6.4343 | 6.3843 | 6.321 | 6.2822 | 6.2251 | 6.1506 | 6.0578 | 6.0037 | 5.9067 | 5.3924 | 5.1527 | 5.0516
COWLEY GSP | YARNTON BSP | EYNSHAM PRIMARY | MINIMUM HEADROOM | SP 42236 10266 | NO | YES | 9.184 | 7.1721 | 6.817 | 6.3477 | 5.8528 | 5.1436 | 4.0793 | 2.5997 | 1.666 | 0.21806 | -6.5289 | -9.3768 | -10.4656 | 9.1354 | 8.9109 | 8.615 | 8.2599 | 7.8048 | 7.5783 | 6.8721 | 6.1477 | 5.3997 | 0.8752 | -1.4064 | -6.0074 | 7.5803 | 7.2885 | 6.8966 | 6.4783 | 5.866 | 4.9344 | 3.7028 | 2.966 | 1.7507 | -3.9697 | -6.3248 | -7.2187
|  | EYNSHAM PRIMARY | EE |  |  |  |  | 7.1721 | 6.817 | 6.3477 | 5.8528 | 5.1436 | 4.5762 | 3.3701 | 2.0242 | 0.58643 | -6.134 | -8.9952 | -10.2615 | 9.1354 | 8.9109 | 8.615 | 8.2599 | 7.8048 | 7.5783 | 6.9038 | 6.1477 | 5.3997 | 0.8752 | -1.384 | -3.8115 | 7.5803 | 7.2885 | 6.8966 | 6.4783 | 5.866 | 5.3558 | 4.3181 | 3.1619 | 1.9844 | -3.6626 | -5.9901 | -7.0462
|  | EYNSHAM PRIMARY | HT |  |  |  |  | 7.3354 | 7.0334 | 6.5997 | 6.1354 | 5.3619 | 4.0793 | 2.5997 | 1.666 | 0.21806 | -6.5289 | -9.3768 | -10.4656 | 9.2864 | 9.1191 | 8.8834 | 8.6385 | 8.2303 | 7.6017 | 6.8721 | 6.4997 | 5.6793 | 1.6803 | 0.37622 | -0.11357 | 7.7028 | 7.4426 | 7.0752 | 6.6762 | 6.0068 | 4.9344 | 3.7028 | 2.966 | 1.7507 | -3.9697 | -6.3248 | -7.2187
|  | EYNSHAM PRIMARY | HE |  |  |  |  | 7.3579 | 7.0732 | 6.6905 | 6.3344 | 5.7252 | 4.8426 | 3.6334 | 2.6415 | 1.2487 | -5.4626 | -8.2513 | -9.1126 | 9.2538 | 9.0681 | 8.8242 | 8.5997 | 8.2354 | 7.7293 | 7.0681 | 6.6038 | 5.8558 | 1.1905 | -1.0564 | -3.3289 | 7.7272 | 7.4854 | 7.1589 | 6.8517 | 6.3242 | 5.5589 | 4.5466 | 3.7721 | 2.6242 | -3.0442 | -5.3207 | -6.0289
|  | EYNSHAM PRIMARY | CF |  |  |  |  | 7.514 | 7.2742 | 7.0528 | 6.8823 | 6.7466 | 6.5681 | 6.2181 | 5.8028 | 5.1344 | 0.78337 | -5.7299 | -7.5697 | 9.3252 | 9.1497 | 8.9854 | 8.8364 | 8.6936 | 8.4997 | 8.2079 | 7.8752 | 7.4017 | 4.3466 | -1.4064 | -6.0074 | 7.8721 | 7.6793 | 7.4926 | 7.3507 | 7.2354 | 7.0874 | 6.8007 | 6.4589 | 5.9028 | 2.2701 | -3.2044 | -4.7585
MINETY GSP | CIRENCESTER BSP | FAIRFORD PRIMARY | MINIMUM HEADROOM | SP 14418 00559 | NO | NO | 2.349 | 5.5398 | 5.2796 | 5.0347 | 4.7327 | 4.3888 | 4.3 | 3.8551 | 3.4163 | 3.1082 | 1.3878 | 0.18165 | -0.58467 | 8.6317 | 8.4357 | 8.251 | 8.0163 | 7.7602 | 7.7214 | 7.4041 | 7.0847 | 6.8674 | 5.5796 | 3.9939 | 0.37757 | 5.7551 | 5.4878 | 5.251 | 4.947 | 4.6194 | 4.5766 | 4.149 | 3.7255 | 3.4521 | 1.9919 | 0.98063 | 0.3592
|  | FAIRFORD PRIMARY | EE |  |  |  |  | 5.5398 | 5.2796 | 5.0347 | 4.7327 | 4.3888 | 4.3 | 3.8551 | 3.4163 | 3.1082 | 1.3878 | 0.37757 | -0.30916 | 8.6317 | 8.4357 | 8.251 | 8.0163 | 7.7602 | 7.7214 | 7.4041 | 7.0847 | 6.8674 | 5.5796 | 4.3021 | 2.4276 | 5.7551 | 5.4878 | 5.251 | 4.947 | 4.6194 | 4.5766 | 4.149 | 3.7255 | 3.4521 | 1.9919 | 1.1429 | 0.58063
|  | FAIRFORD PRIMARY | HT |  |  |  |  | 5.6572 | 5.4531 | 5.2612 | 5.0296 | 4.8092 | 4.4174 | 3.9847 | 3.5317 | 3.4429 | 1.4214 | 0.18165 | -0.58467 | 8.7796 | 8.647 | 8.5327 | 8.3796 | 8.2419 | 8.0184 | 7.7582 | 7.4847 | 7.5031 | 6.3878 | 5.7725 | 5.4174 | 5.9051 | 5.7031 | 5.5214 | 5.2888 | 5.0817 | 4.7174 | 4.3051 | 3.8766 | 3.8623 | 2.0408 | 0.98063 | 0.3592
|  | FAIRFORD PRIMARY | HE |  |  |  |  | 5.6714 | 5.4786 | 5.301 | 5.0898 | 4.8908 | 4.5521 | 4.1684 | 3.7725 | 3.7378 | 1.8143 | 0.80716 | 0.30716 | 8.751 | 8.6031 | 8.4725 | 8.301 | 8.147 | 7.9133 | 7.6378 | 7.3459 | 7.3378 | 5.8347 | 4.5449 | 2.7572 | 5.9133 | 5.7225 | 5.5561 | 5.3388 | 5.1521 | 4.8327 | 4.4633 | 4.0796 | 4.1123 | 2.3888 | 1.5582 | 1.1582
|  | FAIRFORD PRIMARY | CF |  |  |  |  | 5.7663 | 5.6337 | 5.5133 | 5.3684 | 5.2072 | 5.0694 | 4.8612 | 4.6327 | 4.4082 | 3.398 | 2.1572 | 1.0735 | 8.799 | 8.6806 | 8.5766 | 8.4419 | 8.2837 | 8.1306 | 7.9194 | 7.6898 | 7.45 | 6.1786 | 3.9939 | 0.37757 | 6.001 | 5.8755 | 5.7643 | 5.6133 | 5.451 | 5.3184 | 5.1102 | 4.8837 | 4.6561 | 3.7572 | 2.6766 | 1.7725
MINETY GSP | STRATTON (RESERVE) BSP | FARINGDON PRIMARY | MINIMUM HEADROOM | SU 28819 94924 | NO | NO | 12.734 | 17.4615 | 16.9666 | 16.4104 | 15.8921 | 15.8176 | 15.236 | 14.5757 | 13.9166 | 13.4666 | 11.1278 | 9.1911 | 7.988 | 19.6941 | 19.3594 | 18.989 | 18.6033 | 18.5543 | 18.1543 | 17.6829 | 17.1992 | 16.8757 | 15.0625 | 13.0584 | 7.9584 | 17.0155 | 16.5482 | 16.0329 | 15.5421 | 15.486 | 14.9411 | 14.3176 | 13.6941 | 13.2788 | 11.1676 | 9.5237 | 8.5533
|  | FARINGDON PRIMARY | EE |  |  |  |  | 17.4615 | 16.9666 | 16.4104 | 15.8921 | 15.8176 | 15.236 | 14.5757 | 13.9166 | 13.4666 | 11.1278 | 9.4951 | 8.2666 | 19.6941 | 19.3594 | 18.989 | 18.6033 | 18.5543 | 18.1543 | 17.6829 | 17.1992 | 16.8757 | 15.0625 | 13.2553 | 10.5615 | 17.0155 | 16.5482 | 16.0329 | 15.5421 | 15.486 | 14.9411 | 14.3176 | 13.6941 | 13.2788 | 11.1676 | 9.8104 | 8.789
|  | FARINGDON PRIMARY | HT |  |  |  |  | 17.6982 | 17.2523 | 16.7778 | 16.4482 | 16.037 | 15.4737 | 15.2308 | 14.6747 | 14.0962 | 11.1308 | 9.1911 | 7.988 | 19.9115 | 19.6666 | 19.3911 | 19.19 | 18.94 | 18.6176 | 18.5257 | 18.1911 | 17.8462 | 16.1982 | 15.287 | 14.7635 | 17.239 | 16.8462 | 16.4115 | 16.0982 | 15.7104 | 15.186 | 14.9982 | 14.4666 | 13.9196 | 11.189 | 9.5237 | 8.5533
|  | FARINGDON PRIMARY | HE |  |  |  |  | 17.7145 | 17.287 | 16.8472 | 16.538 | 16.1319 | 15.6492 | 15.487 | 15.0104 | 14.5074 | 11.8911 | 10.3227 | 9.5227 | 19.8655 | 19.6002 | 19.3135 | 19.0931 | 18.7972 | 18.4615 | 18.3513 | 17.9972 | 17.6257 | 15.5257 | 13.7166 | 11.2084 | 17.2533 | 16.8778 | 16.4747 | 16.1819 | 15.8002 | 15.3482 | 15.2298 | 14.7696 | 14.2962 | 11.8992 | 10.5921 | 9.9513
|  | FARINGDON PRIMARY | CF |  |  |  |  | 17.889 | 17.5727 | 17.2523 | 16.9951 | 16.7829 | 16.5441 | 16.2574 | 15.9462 | 16.0441 | 14.2502 | 12.5482 | 10.9104 | 19.9564 | 19.736 | 19.5013 | 19.2829 | 19.0829 | 18.84 | 18.5482 | 18.2349 | 18.189 | 16.1104 | 13.0584 | 7.9584 | 17.4288 | 17.1451 | 16.8553 | 16.6053 | 16.4053 | 16.1798 | 15.9033 | 15.6053 | 15.7125 | 14.0196 | 12.4604 | 11.039
LOVEDEAN GSP | PORTSMOUTH BSP | FARLINGTON PRIMARY | MINIMUM HEADROOM | SU 67400 04843 | NO | YES | 8.935 | 11.1641 | 11.0039 | 10.7988 | 10.5824 | 10.3324 | 10.0171 | 9.6335 | 9.3814 | 9.0488 | 7.76 | 7.0845 | 6.759 | 11.76 | 11.6386 | 11.4845 | 11.3171 | 11.1273 | 10.9008 | 10.6253 | 10.4743 | 10.2692 | 9.4386 | 8.2682 | 3.7243 | 10.808 | 10.6763 | 10.5069 | 10.3182 | 10.0794 | 9.7794 | 9.4222 | 9.2161 | 8.9345 | 7.709 | 7.0763 | 6.7641
|  | FARLINGTON PRIMARY | EE |  |  |  |  | 11.1641 | 11.0039 | 10.7988 | 10.5824 | 10.3324 | 10.0171 | 9.6335 | 9.3814 | 9.0488 | 7.7998 | 7.3498 | 7.4018 | 11.76 | 11.6386 | 11.4845 | 11.3171 | 11.1273 | 10.9008 | 10.6253 | 10.4743 | 10.2692 | 9.5243 | 9.1702 | 7.0937 | 10.808 | 10.6763 | 10.5069 | 10.3182 | 10.0794 | 9.7794 | 9.4222 | 9.2161 | 8.9345 | 7.7722 | 7.3692 | 7.4141
|  | FARLINGTON PRIMARY | HT |  |  |  |  | 11.3151 | 11.1865 | 11.0396 | 10.8814 | 10.6896 | 10.4518 | 10.16 | 9.8427 | 9.4671 | 7.9345 | 7.1835 | 6.9324 | 11.8855 | 11.7967 | 11.6865 | 11.5753 | 11.4345 | 11.2712 | 11.0661 | 10.8467 | 10.6161 | 9.6916 | 9.2233 | 9.0284 | 10.9396 | 10.8355 | 10.7131 | 10.5845 | 10.4243 | 10.1998 | 9.9182 | 9.6212 | 9.31 | 7.8957 | 7.2039 | 6.9682
|  | FARLINGTON PRIMARY | HE |  |  |  |  | 11.3049 | 11.1702 | 11.0161 | 10.8508 | 10.6427 | 10.3906 | 10.0763 | 9.7243 | 9.3222 | 7.76 | 7.0845 | 6.759 | 11.8712 | 11.7712 | 11.6518 | 11.5284 | 11.3733 | 11.1927 | 10.96 | 10.7151 | 10.4529 | 9.4386 | 8.9896 | 7.2427 | 10.9314 | 10.8222 | 10.6957 | 10.56 | 10.3814 | 10.1396 | 9.8376 | 9.5171 | 9.1773 | 7.709 | 7.0763 | 6.7641
|  | FARLINGTON PRIMARY | CF |  |  |  |  | 11.4427 | 11.3722 | 11.2906 | 11.2049 | 11.0978 | 10.9722 | 10.8049 | 10.6253 | 10.4212 | 9.3243 | 8.0549 | 7.1069 | 11.9671 | 11.9131 | 11.8467 | 11.7763 | 11.6876 | 11.5896 | 11.46 | 11.3161 | 11.158 | 10.3131 | 8.2682 | 3.7243 | 11.0273 | 10.9784 | 10.909 | 10.8365 | 10.7457 | 10.6406 | 10.4998 | 10.3569 | 10.162 | 9.1141 | 7.9773 | 7.0978
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FARNBOROUGH PRIMARY | MINIMUM HEADROOM | SU 88404 53930 | NO | NO | 7.562 | 10.1526 | 9.1352 | 8.6434 | 7.8046 | 6.5526 | 4.9301 | 3.2546 | 1.5964 | 0.25971 | -6.325 | -10.3984 | -12.7117 | 12.9597 | 12.0954 | 11.7424 | 11.0709 | 10.1862 | 9.1097 | 7.9424 | 6.7597 | 5.8485 | 0.95053 | -4.4117 | -16.8525 | 10.0679 | 9.0995 | 8.6924 | 7.8975 | 6.7638 | 5.3067 | 3.772 | 2.2475 | 1.0801 | -4.6627 | -8.2393 | -10.1342
|  | FARNBOROUGH PRIMARY | EE |  |  |  |  | 10.1526 | 9.1352 | 8.6434 | 7.8046 | 6.5526 | 4.9301 | 3.2546 | 1.5964 | 0.25971 | -6.325 | -9.8076 | -12.5464 | 12.9597 | 12.0954 | 11.7424 | 11.0709 | 10.1862 | 9.1097 | 7.9424 | 6.7597 | 5.8485 | 0.95053 | -3.3444 | -9.7382 | 10.0679 | 9.0995 | 8.6924 | 7.8975 | 6.7638 | 5.3067 | 3.772 | 2.2475 | 1.0801 | -4.6627 | -7.7199 | -10.0107
|  | FARNBOROUGH PRIMARY | HT |  |  |  |  | 10.6281 | 9.823 | 9.172 | 8.4689 | 7.6822 | 6.2546 | 4.8271 | 3.3485 | 1.8342 | -6.0638 | -10.3984 | -12.7117 | 13.4934 | 12.8924 | 12.4648 | 11.9954 | 11.625 | 10.8618 | 10.0556 | 9.2067 | 8.323 | 4.0097 | 1.8352 | 0.87604 | 10.5699 | 9.8301 | 9.223 | 8.5607 | 7.9444 | 6.7036 | 5.4342 | 4.1138 | 2.7495 | -4.3464 | -8.2393 | -10.1342
|  | FARNBOROUGH PRIMARY | HE |  |  |  |  | 10.5913 | 9.7811 | 9.1301 | 8.4158 | 7.6199 | 6.2893 | 4.9454 | 3.5454 | 2.1087 | -5.2699 | -9.1699 | -10.7729 | 13.3322 | 12.6505 | 12.1362 | 11.5648 | 11.0913 | 10.2189 | 9.2862 | 8.2832 | 7.2342 | 1.4342 | -3.2556 | -9.1821 | 10.5291 | 9.7842 | 9.1791 | 8.5046 | 7.8852 | 6.722 | 5.523 | 4.2607 | 2.9505 | -4.0168 | -7.5648 | -8.8862
|  | FARNBOROUGH PRIMARY | CF |  |  |  |  | 11.0464 | 10.424 | 10.0546 | 9.6179 | 8.8444 | 8.0577 | 7.6638 | 6.9016 | 6.1036 | 0.86278 | -3.4668 | -7.2372 | 13.5669 | 12.9546 | 12.5934 | 12.1577 | 11.524 | 10.8179 | 10.4169 | 9.6556 | 8.8424 | 3.2505 | -4.4117 | -16.8525 | 10.9393 | 10.3577 | 10.0138 | 9.5985 | 8.9169 | 8.2148 | 7.9444 | 7.2505 | 6.5209 | 1.7995 | -2.2852 | -5.8607
FLEET-BRAMLEY GSP | PYESTOCK BSP | FARNBORO AIRFIELD PRIMARY | MINIMUM HEADROOM | SU 85838 54449 | NO | NO | 2.815 | 26.7986 | 26.7404 | 26.6822 | 26.62 | 26.5424 | 26.4802 | 26.4077 | 26.3353 | 26.2782 | 26.0649 | 25.7598 | 25.5516 | 25.221 | 25.1792 | 25.1333 | 25.07 | 25.0037 | 24.9537 | 24.8894 | 24.8271 | 24.7782 | 24.5567 | 24.3088 | 23.7322 | 26.073 | 26.023 | 25.9771 | 25.9251 | 25.869 | 25.8261 | 25.7741 | 25.722 | 25.6822 | 25.5741 | 25.3639 | 25.1894
|  | FARNBORO AIRFIELD PRIMARY | EE |  |  |  |  | 26.7986 | 26.7404 | 26.6822 | 26.62 | 26.5424 | 26.4802 | 26.4077 | 26.3353 | 26.2782 | 26.0649 | 25.7598 | 25.5516 | 25.221 | 25.1792 | 25.1333 | 25.07 | 25.0037 | 24.9537 | 24.8894 | 24.8271 | 24.7782 | 24.5567 | 24.3088 | 23.9833 | 26.073 | 26.023 | 25.9771 | 25.9251 | 25.869 | 25.8261 | 25.7741 | 25.722 | 25.6822 | 25.5741 | 25.3639 | 25.1894
|  | FARNBORO AIRFIELD PRIMARY | HT |  |  |  |  | 26.8149 | 26.7659 | 26.7128 | 26.6547 | 26.5894 | 26.5322 | 26.4782 | 26.4169 | 26.3618 | 26.0924 | 25.7802 | 25.5771 | 25.2363 | 25.2098 | 25.169 | 25.12 | 25.073 | 25.0302 | 24.9904 | 24.9435 | 24.9108 | 24.7333 | 24.6077 | 24.521 | 26.0873 | 26.0475 | 26.0037 | 25.9567 | 25.9118 | 25.872 | 25.8373 | 25.7945 | 25.7618 | 25.6251 | 25.3975 | 25.2271
|  | FARNBORO AIRFIELD PRIMARY | HE |  |  |  |  | 26.8169 | 26.771 | 26.72 | 26.6649 | 26.6026 | 26.5435 | 26.4863 | 26.4251 | 26.37 | 26.1435 | 25.921 | 25.7975 | 25.2343 | 25.2047 | 25.1608 | 25.1047 | 25.0547 | 25.0047 | 24.9588 | 24.9057 | 24.8639 | 24.6322 | 24.4088 | 24.1159 | 26.0884 | 26.0506 | 26.0077 | 25.9618 | 25.92 | 25.8792 | 25.8424 | 25.8006 | 25.7659 | 25.6333 | 25.5026 | 25.3965
|  | FARNBORO AIRFIELD PRIMARY | CF |  |  |  |  | 26.8445 | 26.8077 | 26.7669 | 26.7302 | 26.6894 | 26.6608 | 26.6292 | 26.5945 | 26.5547 | 26.3873 | 26.22 | 26.0853 | 25.2486 | 25.2271 | 25.1873 | 25.1526 | 25.1026 | 25.0761 | 25.0373 | 25.0006 | 24.9598 | 24.7486 | 24.3986 | 23.7322 | 26.1088 | 26.0792 | 26.0424 | 26.0098 | 25.9741 | 25.9526 | 25.9282 | 25.9026 | 25.873 | 25.7751 | 25.6853 | 25.6108
FLEET-BRAMLEY GSP | ALDERSHOT BSP | FARNHAM PRIMARY | MINIMUM HEADROOM | SU 84517 47217 | NO | YES | 7.81 | 5.2909 | 4.2705 | 3.0664 | 1.8144 | 0.31335 | -1.2622 | -3.0622 | -4.7764 | -6.1989 | -14.0867 | -17.7336 | -18.3591 | 10.2603 | 9.5062 | 8.6307 | 7.7368 | 6.6521 | 5.5144 | 4.1868 | 2.9236 | 1.8827 | -4.0183 | -6.706 | -10.8244 | 6.4542 | 5.646 | 4.6552 | 3.9093 | 2.4878 | 0.98988 | -0.73257 | -2.3724 | -3.7295 | -11.3132 | -14.7928 | -15.3795
|  | FARNHAM PRIMARY | EE |  |  |  |  | 5.2909 | 4.2705 | 3.0664 | 1.8144 | 0.31335 | -1.2622 | -3.0622 | -4.7764 | -6.1989 | -10.8693 | -11.9877 | -12.1775 | 10.2603 | 9.5062 | 8.6307 | 7.7368 | 6.6521 | 5.5144 | 4.1868 | 2.9236 | 1.8827 | -1.4152 | -2.103 | -5.452 | 6.4542 | 5.646 | 4.6552 | 3.9093 | 2.4878 | 0.98988 | -0.73257 | -2.3724 | -3.7295 | -8.153 | -9.1662 | -9.3326
|  | FARNHAM PRIMARY | HT |  |  |  |  | 6.2348 | 5.6215 | 4.8001 | 3.8215 | 2.7001 | 1.5715 | 0.4409 | -0.8938 | -2.2764 | -8.4489 | -11.2326 | -11.8183 | 11.0011 | 10.5715 | 10.0042 | 9.3256 | 8.546 | 7.7582 | 6.9593 | 5.995 | 4.995 | 0.58988 | -1.303 | -1.6846 | 7.096 | 6.4521 | 5.7256 | 4.8236 | 3.795 | 2.7858 | 2.2287 | 1.2287 | 0.063347 | -5.8203 | -8.4438 | -8.9816
|  | FARNHAM PRIMARY | HE |  |  |  |  | 5.9266 | 5.0409 | 4.0062 | 2.7644 | 1.3184 | -0.17441 | -1.7744 | -3.6071 | -5.5183 | -14.0867 | -17.7336 | -18.3591 | 10.7531 | 10.1031 | 9.3572 | 8.4644 | 7.4256 | 6.345 | 5.1664 | 3.8042 | 2.3746 | -4.0183 | -6.706 | -7.304 | 6.9613 | 6.2644 | 5.5021 | 4.5419 | 3.4327 | 2.0338 | 0.5062 | -1.2499 | -3.0887 | -11.3132 | -14.7928 | -15.3795
|  | FARNHAM PRIMARY | CF |  |  |  |  | 6.497 | 6.1052 | 5.595 | 4.8991 | 4.1093 | 3.4001 | 2.4909 | 1.6001 | 0.52457 | -5.8336 | -11.353 | -14.6285 | 11.1195 | 10.8266 | 10.448 | 9.9736 | 9.4093 | 8.897 | 8.2011 | 7.5276 | 6.7042 | 1.8868 | -2.6999 | -10.8244 | 7.3899 | 6.9603 | 6.4521 | 5.894 | 5.2307 | 4.7236 | 4.1287 | 3.7113 | 2.6766 | -3.4346 | -8.705 | -11.7979
IVER 132KV GSP | SLOUGH BSP | FARNHAM ROYAL PRIMARY | MINIMUM HEADROOM | SU 95597 82844 | NO | YES | 8.942 | 15.1079 | 14.2202 | 13.2987 | 12.2365 | 11.0896 | 9.2722 | 5.2079 | 1.761 | -1.3023 | -12.7176 | -21.4768 | -25.3176 | 21.3734 | 20.6377 | 19.8622 | 19.002 | 18.0591 | 16.7765 | 12.8173 | 9.604 | 6.4826 | -4.1419 | -13.3194 | -25.5623 | 15.5079 | 14.5936 | 13.6518 | 12.6202 | 11.4885 | 9.7916 | 5.3498 | 1.6804 | -1.6145 | -13.6717 | -22.9196 | -27.439
|  | FARNHAM ROYAL PRIMARY | EE |  |  |  |  | 15.1079 | 14.2202 | 13.2987 | 12.2365 | 11.0896 | 9.2722 | 5.2079 | 1.761 | -1.3023 | -11.3564 | -17.5543 | -20.2043 | 21.3734 | 20.6377 | 19.8622 | 19.002 | 18.0591 | 16.7765 | 12.8173 | 9.604 | 6.4826 | -4.1419 | -13.3194 | -25.5623 | 15.5079 | 14.5936 | 13.6518 | 12.6202 | 11.4885 | 9.7916 | 5.3498 | 1.6804 | -1.6145 | -11.9982 | -18.2115 | -21.7839
|  | FARNHAM ROYAL PRIMARY | HT |  |  |  |  | 15.3355 | 14.5059 | 14.0855 | 13.3661 | 12.5814 | 11.1783 | 7.6212 | 4.512 | 1.062 | -12.7176 | -21.4768 | -25.3176 | 21.8183 | 21.2734 | 21.0571 | 20.5673 | 20.0153 | 19.2142 | 15.7959 | 13.0061 | 9.852 | -1.6694 | -9.3021 | -13.7551 | 15.8396 | 15.0222 | 14.6824 | 13.9538 | 13.1477 | 11.8375 | 7.8579 | 4.4987 | 0.75384 | -13.6717 | -22.9196 | -27.439
|  | FARNHAM ROYAL PRIMARY | HE |  |  |  |  | 15.4273 | 14.66 | 14.3038 | 13.6569 | 12.961 | 11.7232 | 8.8916 | 6.9222 | 4.713 | -5.3962 | -11.2013 | -15.0676 | 21.6734 | 21.05 | 20.7459 | 20.1489 | 19.4836 | 18.5724 | 15.7204 | 13.9622 | 11.953 | 1.1602 | -8.0215 | -20.6194 | 15.91 | 15.1518 | 14.8691 | 14.211 | 13.4865 | 12.3283 | 9.1977 | 7.1742 | 4.9151 | -5.5482 | -11.5298 | -16.0156
|  | FARNHAM ROYAL PRIMARY | CF |  |  |  |  | 16.2038 | 15.8375 | 15.411 | 15.2977 | 14.8589 | 14.3732 | 12.6181 | 11.0028 | 9.5885 | 3.9161 | -1.7696 | -6.7717 | 22.0398 | 21.5857 | 21.0796 | 20.8173 | 20.2081 | 19.4938 | 17.2163 | 15.1551 | 13.3142 | 5.4908 | -6.0184 | -25.1909 | 16.5875 | 16.164 | 15.6671 | 15.661 | 15.1977 | 14.6844 | 12.6222 | 10.7793 | 9.1977 | 3.5875 | -1.5492 | -6.04
LALEHAM GSP | EAST BEDFONT BSP | FELTHAM PRIMARY | MINIMUM HEADROOM | TQ 10628 72811 | NO | NO | 2.213 | 11.1846 | 10.6743 | 10.0743 | 9.2427 | 8.4009 | 7.5478 | 6.7468 | 5.8805 | 5.2794 | 2.509 | 0.8019 | -0.20014 | 12.5203 | 12.2856 | 11.9978 | 11.4958 | 10.9958 | 10.5305 | 10.056 | 9.4366 | 8.9366 | 7.3509 | 6.4529 | 5.3539 | 10.7682 | 10.3386 | 9.807 | 9.0203 | 8.2427 | 7.4846 | 6.7835 | 6.0366 | 5.5631 | 3.2335 | 1.6846 | 0.72435
|  | FELTHAM PRIMARY | EE |  |  |  |  | 11.2488 | 10.8386 | 10.3468 | 9.6743 | 8.7733 | 8.2264 | 7.2652 | 6.156 | 5.2794 | 2.509 | 1.0437 | -0.20014 | 12.5203 | 12.2907 | 12.0152 | 11.6009 | 10.9958 | 10.7172 | 10.109 | 9.4366 | 8.9366 | 7.3509 | 6.4529 | 5.3539 | 10.7682 | 10.3723 | 9.9172 | 9.358 | 8.5437 | 8.0846 | 7.2488 | 6.306 | 5.5631 | 3.2335 | 1.8825 | 0.72435
|  | FELTHAM PRIMARY | HT |  |  |  |  | 11.1846 | 10.6743 | 10.0743 | 9.2427 | 8.4009 | 7.5478 | 6.7468 | 5.8805 | 5.457 | 2.5325 | 0.8019 | -0.18484 | 12.5305 | 12.2856 | 11.9978 | 11.4958 | 11.0243 | 10.5305 | 10.056 | 9.5417 | 9.3815 | 7.7682 | 6.9488 | 6.5601 | 10.7846 | 10.3386 | 9.807 | 9.0203 | 8.2427 | 7.4846 | 6.7835 | 6.0366 | 5.7141 | 3.2662 | 1.6846 | 0.75496
|  | FELTHAM PRIMARY | HE |  |  |  |  | 11.3682 | 10.9948 | 10.5846 | 10.0774 | 9.357 | 8.6478 | 7.7774 | 6.7692 | 6.2346 | 3.4784 | 2.0968 | 1.5009 | 12.606 | 12.3999 | 12.1876 | 11.9335 | 11.4948 | 11.0621 | 10.5264 | 9.9203 | 9.6733 | 7.9611 | 7.0723 | 6.2672 | 10.9356 | 10.5958 | 10.2243 | 9.7621 | 9.0856 | 8.4203 | 7.6672 | 6.8009 | 6.3784 | 4.0968 | 2.8294 | 2.2723
|  | FELTHAM PRIMARY | CF |  |  |  |  | 11.5866 | 11.4988 | 11.3948 | 11.2927 | 11.1876 | 11.0305 | 10.707 | 10.2682 | 9.7376 | 5.2784 | 3.8478 | 2.8356 | 12.707 | 12.6366 | 12.5488 | 12.4764 | 12.3927 | 12.2478 | 11.9999 | 11.6754 | 11.2948 | 8.6529 | 7.3182 | 5.705 | 11.1356 | 11.0325 | 10.9233 | 10.8029 | 10.6754 | 10.4927 | 10.1529 | 9.7356 | 9.2825 | 5.7029 | 4.4743 | 3.5448
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN PRIMARY | MINIMUM HEADROOM | SU 06593 00685 | NO | NO | 7.305 | 19.2654 | 18.6715 | 16.7613 | 15.5705 | 13.2032 | 10.6787 | 7.7705 | 6.1889 | 2.4052 | -14.5366 | -24.3642 | -34.0622 | 25.3889 | 24.7297 | 22.6991 | 21.5603 | 18.994 | 16.4634 | 13.5297 | 12.2858 | 8.3991 | -7.3479 | -19.8652 | -32.1836 | 20.6042 | 19.9338 | 17.8287 | 16.5725 | 13.8746 | 11.044 | 7.7725 | 6.094 | 1.6297 | -17.1877 | -27.5448 | -38.6632
|  | FERNDOWN PRIMARY | EE |  |  |  |  | 19.2654 | 18.6919 | 17.8695 | 16.893 | 14.4817 | 12.3021 | 10.8797 | 7.8919 | 5.9103 | -7.5917 | -13.9948 | -23.4979 | 25.3889 | 24.9674 | 24.344 | 23.5909 | 21.1378 | 19.1032 | 18.1164 | 15.1593 | 13.3521 | -0.23358 | -7.3999 | -21.9958 | 20.6042 | 20.1215 | 19.3766 | 18.447 | 15.8572 | 13.5072 | 12.1593 | 8.8501 | 6.7338 | -8.3866 | -14.9081 | -25.6336
|  | FERNDOWN PRIMARY | HT |  |  |  |  | 19.8042 | 18.9491 | 17.6256 | 17.1266 | 13.2032 | 10.6787 | 7.7705 | 6.1889 | 2.4052 | -14.5366 | -23.0928 | -34.0622 | 25.8327 | 25.0521 | 23.7419 | 23.4144 | 18.994 | 16.4634 | 13.5297 | 12.2858 | 8.3991 | -7.3479 | -13.4775 | -24.9417 | 21.0817 | 20.2481 | 18.8603 | 18.4113 | 13.8746 | 11.044 | 7.7725 | 6.094 | 1.6297 | -17.1877 | -25.9744 | -38.6632
|  | FERNDOWN PRIMARY | HE |  |  |  |  | 19.7307 | 18.6715 | 16.7613 | 15.5705 | 14.2501 | 11.6797 | 8.796 | 7.4695 | 6.0889 | -12.0356 | -24.3642 | -29.1734 | 25.7542 | 24.7297 | 22.6991 | 21.5603 | 20.4195 | 17.795 | 14.8807 | 13.9491 | 12.9705 | -5.1213 | -19.8652 | -29.9785 | 21.0185 | 19.9338 | 17.8287 | 16.5725 | 15.3123 | 12.4205 | 9.196 | 7.9419 | 6.6317 | -13.6724 | -27.5448 | -32.956
|  | FERNDOWN PRIMARY | CF |  |  |  |  | 20.2542 | 19.9113 | 19.5062 | 18.5562 | 16.8001 | 15.7052 | 14.6552 | 13.497 | 12.093 | 2.2409 | -11.2101 | -21.7673 | 26.044 | 25.8052 | 25.5123 | 24.5725 | 22.7338 | 21.6062 | 20.6052 | 19.5052 | 18.1144 | 6.8715 | -11.1856 | -32.1836 | 21.3552 | 21.1001 | 20.7664 | 19.7827 | 17.9593 | 16.7827 | 15.7246 | 14.5297 | 12.994 | 2.3154 | -12.5958 | -24.7795
FLEET-BRAMLEY GSP | FERNHURST BSP | FIVE OAKS PRIMARY | MINIMUM HEADROOM | TQ 10647 29057 | NO | NO | 3.821 | 4.5342 | 4.2362 | 3.9607 | 3.6005 | 3.1117 | 2.5587 | 2.4372 | 2.0168 | 1.624 | 0.18418 | -0.80867 | -1.4311 | 5.3362 | 5.1832 | 5.0219 | 4.8393 | 4.6515 | 4.4454 | 4.3974 | 4.227 | 4.0577 | 3.2352 | 2.627 | 1.4923 | 5.323 | 5.0444 | 4.7526 | 4.3709 | 3.923 | 3.424 | 3.3474 | 2.9679 | 2.6403 | 1.3954 | 0.55765 | 0.05051
|  | FIVE OAKS PRIMARY | EE |  |  |  |  | 4.5342 | 4.2362 | 3.9607 | 3.6005 | 3.1117 | 2.5587 | 2.4372 | 2.0168 | 1.7046 | 0.20459 | -0.60969 | -1.1679 | 5.3362 | 5.1832 | 5.0219 | 4.8393 | 4.6515 | 4.4454 | 4.3974 | 4.227 | 4.0577 | 3.2352 | 2.627 | 1.9077 | 5.323 | 5.0444 | 4.7526 | 4.3709 | 3.923 | 3.424 | 3.3474 | 2.9679 | 2.6913 | 1.3954 | 0.71276 | 0.25357
|  | FIVE OAKS PRIMARY | HT |  |  |  |  | 4.7189 | 4.4934 | 4.1923 | 3.8362 | 3.3821 | 2.926 | 2.5046 | 2.074 | 1.624 | 0.18418 | -0.80867 | -1.4311 | 5.3842 | 5.2495 | 5.0985 | 4.9556 | 4.7893 | 4.6342 | 4.476 | 4.3087 | 4.1036 | 3.4556 | 3.0372 | 2.7566 | 5.4209 | 5.175 | 4.9077 | 4.5985 | 4.2077 | 3.8117 | 3.4362 | 3.0485 | 2.6403 | 1.4015 | 0.55765 | 0.05051
|  | FIVE OAKS PRIMARY | HE |  |  |  |  | 4.7189 | 4.5097 | 4.2658 | 3.8974 | 3.4556 | 3.0372 | 2.6628 | 2.277 | 1.8821 | 0.52908 | -0.27398 | -0.69133 | 5.3801 | 5.2434 | 5.0954 | 4.9342 | 4.7648 | 4.6107 | 4.4515 | 4.2862 | 4.1066 | 3.3536 | 2.7372 | 2.0587 | 5.4321 | 5.2066 | 4.9658 | 4.6485 | 4.2648 | 3.9066 | 3.5689 | 3.2179 | 2.8597 | 1.6985 | 1.023 | 0.69031
|  | FIVE OAKS PRIMARY | CF |  |  |  |  | 4.7811 | 4.6158 | 4.4321 | 4.1985 | 3.8434 | 3.523 | 3.3036 | 3.0321 | 2.7577 | 1.7872 | 0.76276 | -0.125 | 5.4026 | 5.2842 | 5.1526 | 5.0209 | 4.8617 | 4.7189 | 4.6036 | 4.4648 | 4.323 | 3.7934 | 2.8546 | 1.4923 | 5.5066 | 5.3291 | 5.1301 | 4.9138 | 4.6066 | 4.3332 | 4.1383 | 3.8964 | 3.6485 | 2.8077 | 1.9158 | 1.1587
AMERSHAM GSP | LOUDWATER BSP | FLACKWELL HEATH PRIMARY | MINIMUM HEADROOM | SU 90667 89318 | NO | YES | 3.034 | 16.9292 | 16.5812 | 16.2037 | 16.118 | 15.7547 | 15.0629 | 14.3057 | 13.5414 | 12.9282 | 9.2282 | 6.52 | 5.0639 | 18.5333 | 18.1761 | 17.7812 | 17.7945 | 17.422 | 16.9108 | 16.318 | 15.7139 | 15.3292 | 13.2884 | 10.8996 | 4.4445 | 15.8843 | 15.47 | 15.0016 | 15.019 | 14.5986 | 13.9333 | 13.1557 | 12.37 | 11.8659 | 9.0037 | 6.7516 | 5.5476
|  | FLACKWELL HEATH PRIMARY | EE |  |  |  |  | 16.9292 | 16.5812 | 16.2037 | 16.118 | 15.7547 | 15.0629 | 14.3057 | 13.5414 | 12.9282 | 9.5496 | 7.0649 | 5.2976 | 18.5333 | 18.1761 | 17.7812 | 17.7945 | 17.422 | 16.9108 | 16.318 | 15.7139 | 15.3292 | 13.2884 | 11.1761 | 7.7935 | 15.8843 | 15.47 | 15.0016 | 15.019 | 14.5986 | 13.9333 | 13.1557 | 12.37 | 11.8659 | 9.2006 | 7.2292 | 5.7465
|  | FLACKWELL HEATH PRIMARY | HT |  |  |  |  | 17.0884 | 16.7976 | 16.52 | 16.1945 | 15.8384 | 15.4037 | 14.6945 | 13.9578 | 13.2067 | 9.2282 | 6.52 | 5.0639 | 18.8373 | 18.6108 | 18.4108 | 18.1465 | 17.8445 | 17.8169 | 17.418 | 16.9924 | 16.5465 | 14.5088 | 13.4629 | 12.9618 | 16.1496 | 15.8445 | 15.57 | 15.2088 | 14.8037 | 14.6078 | 13.9741 | 13.2945 | 12.5965 | 9.0037 | 6.7516 | 5.5476
|  | FLACKWELL HEATH PRIMARY | HE |  |  |  |  | 17.1292 | 16.8669 | 16.618 | 16.3231 | 15.9996 | 15.7159 | 15.1455 | 14.5424 | 13.9169 | 10.6088 | 8.1384 | 7.0108 | 18.7884 | 18.5343 | 18.3118 | 18.021 | 17.6924 | 17.6598 | 17.2496 | 16.8037 | 16.3302 | 13.822 | 11.6669 | 8.5373 | 16.1741 | 15.8904 | 15.6424 | 15.3108 | 14.9384 | 14.8465 | 14.3231 | 13.7598 | 13.172 | 10.1955 | 8.2169 | 7.2802
|  | FLACKWELL HEATH PRIMARY | CF |  |  |  |  | 17.3414 | 17.2159 | 17.0639 | 16.9292 | 16.7537 | 16.5455 | 16.2884 | 16.3088 | 16.0129 | 13.8629 | 11.5139 | 9.219 | 18.8669 | 18.6996 | 18.4853 | 18.2986 | 18.0333 | 17.7251 | 17.3435 | 17.3904 | 17.0343 | 14.4924 | 10.8996 | 4.4445 | 16.3414 | 16.1924 | 15.9996 | 15.8486 | 15.621 | 15.3567 | 15.0261 | 15.1965 | 14.9139 | 12.8802 | 10.8955 | 8.9771
NURSLING GSP | ROWNHAMS BSP | FLETCHWOOD PRIMARY | MINIMUM HEADROOM | SU 33800 12142 | NO | YES | 9.08 | 8.113 | 7.765 | 7.0589 | 6.364 | 5.5702 | 4.2548 | 2.8242 | 1.3181 | 0.18648 | -5.6247 | -9.6145 | -11.8992 | 12.9926 | 12.7793 | 12.3467 | 11.9028 | 11.3599 | 10.5304 | 9.5855 | 8.5906 | 7.911 | 4.2375 | 0.55995 | -8.6717 | 8.7885 | 8.4926 | 7.8518 | 7.211 | 6.4773 | 5.2916 | 3.9906 | 2.6314 | 1.6385 | -3.4278 | -6.8043 | -8.7166
|  | FLETCHWOOD PRIMARY | EE |  |  |  |  | 8.113 | 7.765 | 7.0589 | 6.364 | 5.5702 | 4.2548 | 2.8242 | 1.3181 | 0.18648 | -5.2258 | -8.8462 | -11.4839 | 12.9926 | 12.7793 | 12.3467 | 11.9028 | 11.3599 | 10.5304 | 9.5855 | 8.5906 | 7.911 | 4.2375 | 0.80893 | -4.0758 | 8.7885 | 8.4926 | 7.8518 | 7.211 | 6.4773 | 5.2916 | 3.9906 | 2.6314 | 1.6385 | -3.1207 | -6.1196 | -8.3645
|  | FLETCHWOOD PRIMARY | HT |  |  |  |  | 8.4487 | 7.9069 | 7.2375 | 6.9344 | 6.262 | 5.0457 | 3.7518 | 2.3528 | 0.87321 | -5.6247 | -9.6145 | -11.8992 | 13.2946 | 13.0079 | 12.6497 | 12.5253 | 12.1783 | 11.5844 | 10.9436 | 10.2477 | 9.4589 | 6.0559 | 4.3232 | 3.3253 | 9.1283 | 8.6426 | 8.0416 | 7.7936 | 7.1885 | 6.1089 | 4.9579 | 3.712 | 2.3875 | -3.4278 | -6.8043 | -8.7166
|  | FLETCHWOOD PRIMARY | HE |  |  |  |  | 8.5048 | 8.0038 | 7.3732 | 7.114 | 6.4834 | 5.4732 | 4.3824 | 3.1855 | 1.9844 | -3.7941 | -7.4513 | -9.2258 | 13.2283 | 12.9028 | 12.5048 | 12.3355 | 11.9253 | 11.3314 | 10.6793 | 9.9548 | 9.2089 | 4.9273 | 1.3375 | -3.2054 | 9.1763 | 8.7253 | 8.1599 | 7.9467 | 7.3824 | 6.4885 | 5.512 | 4.4446 | 3.3722 | -1.8247 | -4.8778 | -6.3696
|  | FLETCHWOOD PRIMARY | CF |  |  |  |  | 8.8324 | 8.4957 | 8.0589 | 7.6569 | 7.512 | 6.9844 | 6.3977 | 5.7089 | 5.0232 | 1.2834 | -2.6686 | -5.987 | 13.3722 | 13.1161 | 12.7926 | 12.4722 | 12.3079 | 11.8671 | 11.3681 | 10.8079 | 10.2273 | 6.3732 | 0.55995 | -8.6717 | 9.4773 | 9.1742 | 8.7906 | 8.4212 | 8.3232 | 7.863 | 7.3416 | 6.7395 | 6.1344 | 2.7171 | -0.82883 | -3.7288
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE PRIMARY | MINIMUM HEADROOM | SU 14069 15523 | NO | NO | 4.175 | 4.7772 | 4.3405 | 3.9211 | 3.3395 | 2.6354 | 1.8864 | 1.5895 | 0.97111 | 0.46805 | -1.7024 | -2.9626 | -3.6717 | 6.4966 | 6.1987 | 5.9415 | 5.5823 | 5.165 | 4.7048 | 4.6956 | 4.3068 | 4.0303 | 2.5905 | 1.3507 | -1.9146 | 5.3364 | 4.9323 | 4.5629 | 4.0425 | 3.4201 | 2.7456 | 2.6507 | 2.1007 | 1.665 | -0.21665 | -1.3054 | -1.9024
|  | FORDINGBRIDGE PRIMARY | EE |  |  |  |  | 4.7772 | 4.3405 | 3.9211 | 3.3395 | 2.6354 | 1.8864 | 1.5895 | 0.97111 | 0.46805 | -1.6503 | -2.735 | -3.5228 | 6.4966 | 6.1987 | 5.9415 | 5.5823 | 5.165 | 4.7048 | 4.6956 | 4.3068 | 4.0303 | 2.5905 | 1.3946 | -0.31359 | 5.3364 | 4.9323 | 4.5629 | 4.0425 | 3.4201 | 2.7456 | 2.6507 | 2.1007 | 1.665 | -0.18297 | -1.0973 | -1.7748
|  | FORDINGBRIDGE PRIMARY | HT |  |  |  |  | 4.8599 | 4.5038 | 4.1374 | 3.6201 | 3.0119 | 2.3242 | 1.715 | 1.0844 | 0.76601 | -1.7024 | -2.9626 | -3.6717 | 6.6262 | 6.4262 | 6.2395 | 5.967 | 5.668 | 5.3201 | 4.9915 | 4.6334 | 4.5527 | 3.2772 | 2.6813 | 2.365 | 5.467 | 5.1548 | 4.8476 | 4.4068 | 3.917 | 3.3262 | 2.7864 | 2.2262 | 1.9803 | -0.21665 | -1.3054 | -1.9024
|  | FORDINGBRIDGE PRIMARY | HE |  |  |  |  | 4.9119 | 4.5395 | 4.1885 | 3.6844 | 3.0976 | 2.4772 | 1.9293 | 1.365 | 1.1252 | -1.1044 | -2.1707 | -2.685 | 6.6313 | 6.3997 | 6.1946 | 5.9078 | 5.5885 | 5.2374 | 4.9068 | 4.5599 | 4.4507 | 2.8803 | 1.6783 | 0.083353 | 5.5048 | 5.1813 | 4.8895 | 4.4629 | 3.9895 | 3.4629 | 2.9731 | 2.4629 | 2.3058 | 0.32723 | -0.57379 | -1.0146
|  | FORDINGBRIDGE PRIMARY | CF |  |  |  |  | 5.0354 | 4.768 | 4.4323 | 4.067 | 3.5711 | 3.1364 | 2.8129 | 2.4334 | 2.0456 | 0.66703 | -0.61869 | -1.7585 | 6.6915 | 6.518 | 6.2966 | 6.0752 | 5.7711 | 5.4844 | 5.2497 | 4.9691 | 4.6752 | 3.3629 | 1.3507 | -1.9146 | 5.6109 | 5.3762 | 5.0854 | 4.7874 | 4.3752 | 3.9997 | 3.7231 | 3.3742 | 3.018 | 1.9129 | 0.75376 | -0.25236
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK PRIMARY | MINIMUM HEADROOM | SU 66139 00180 | NO | YES | 5.967 | -7.7102 | -8.6704 | -9.8347 | -11.1775 | -12.2275 | -14.0479 | -16.1438 | -18.2163 | -19.952 | -26.0459 | -30.1959 | -29.9826 | -1.3785 | -2.1867 | -3.1632 | -4.301 | -5.1673 | -6.5541 | -8.1857 | -9.8285 | -11.202 | -17.399 | -25.0214 | -44.9041 | -6.7173 | -7.6326 | -8.7418 | -10.0234 | -11.0153 | -12.7367 | -14.7275 | -16.6969 | -18.3306 | -23.9775 | -27.6357 | -27.3857
|  | FRATTON PARK PRIMARY | EE |  |  |  |  | -7.7102 | -8.6704 | -9.8347 | -11.1775 | -12.2275 | -14.0479 | -16.1438 | -18.2163 | -19.952 | -26.0459 | -28.6092 | -27.8306 | -1.3785 | -2.1867 | -3.1632 | -4.301 | -5.1673 | -6.5541 | -8.1857 | -9.8285 | -11.202 | -17.399 | -23.1847 | -31.7602 | -6.7173 | -7.6326 | -8.7418 | -10.0234 | -11.0153 | -12.7367 | -14.7275 | -16.6969 | -18.3306 | -23.9775 | -26.2 | -25.5459
|  | FRATTON PARK PRIMARY | HT |  |  |  |  | -7.0081 | -7.6724 | -8.502 | -9.4234 | -10.4765 | -11.8949 | -13.1796 | -14.8204 | -16.5806 | -25.2347 | -30.1959 | -29.9826 | -0.61018 | -1.0898 | -1.6765 | -2.3173 | -3.0734 | -3.9734 | -4.7275 | -5.8041 | -6.9704 | -12.5214 | -15.6275 | -15.7979 | -5.9938 | -6.6387 | -7.4163 | -8.2785 | -9.2745 | -10.603 | -11.799 | -13.3459 | -14.999 | -23.0755 | -27.6357 | -27.3857
|  | FRATTON PARK PRIMARY | HE |  |  |  |  | -7.0632 | -7.6959 | -8.4673 | -9.3265 | -10.301 | -11.5877 | -12.7408 | -14.2204 | -15.7581 | -21.9551 | -24.7643 | -25.0755 | -0.81324 | -1.3653 | -2.0275 | -2.7551 | -3.5979 | -4.5969 | -5.4612 | -6.651 | -7.9234 | -14.6224 | -20.8428 | -29.5081 | -6.0428 | -6.6551 | -7.3877 | -8.1898 | -9.1102 | -10.3143 | -11.3816 | -12.7765 | -14.2265 | -20.0857 | -22.6347 | -22.852
|  | FRATTON PARK PRIMARY | CF |  |  |  |  | -6.4449 | -6.8234 | -7.2622 | -7.8081 | -8.3449 | -8.8612 | -9.5336 | -10.2714 | -10.7132 | -15.4459 | -21.149 | -26.2724 | -0.49181 | -0.93569 | -1.4418 | -2.0479 | -2.7122 | -3.4592 | -4.3755 | -5.3694 | -6.1173 | -13.2806 | -25.0214 | -44.9041 | -5.4622 | -5.8306 | -6.2622 | -6.7755 | -7.2816 | -7.7796 | -8.4306 | -9.1479 | -9.5673 | -14.1092 | -19.3847 | -24.0061
COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD PRIMARY | MINIMUM HEADROOM | SP 50426 08256 | NO | YES | 6.111 | 6.2071 | 5.9602 | 5.6673 | 5.3908 | 5.0408 | 4.3581 | 3.7102 | 3.551 | 3.1908 | 1.7857 | 0.81527 | 0.78976 | 7.7622 | 7.5377 | 7.2663 | 7.0112 | 6.6949 | 6.2153 | 5.7194 | 5.6234 | 5.3214 | 3.7898 | 1.0643 | -5.1511 | 6.0551 | 5.8102 | 5.5102 | 5.2387 | 4.8938 | 4.2673 | 3.6643 | 3.5785 | 3.2561 | 2.0653 | 1.2183 | 1.1959
|  | FRENCHAY ROAD PRIMARY | EE |  |  |  |  | 6.2071 | 5.9602 | 5.6673 | 5.3908 | 5.0408 | 4.3581 | 3.7102 | 3.551 | 3.1908 | 1.7857 | 1.054 | 1.2051 | 7.7622 | 7.5377 | 7.2663 | 7.0112 | 6.6949 | 6.2153 | 5.7194 | 5.6234 | 5.3214 | 3.7898 | 2.0408 | -0.78881 | 6.0551 | 5.8102 | 5.5102 | 5.2387 | 4.8938 | 4.2673 | 3.6643 | 3.5785 | 3.2561 | 2.0653 | 1.4316 | 1.5489
|  | FRENCHAY ROAD PRIMARY | HT |  |  |  |  | 6.3285 | 6.1428 | 5.9673 | 5.7428 | 5.4938 | 4.8245 | 4.4194 | 3.9938 | 3.5571 | 1.9224 | 0.81527 | 0.78976 | 7.9673 | 7.8306 | 7.702 | 7.5306 | 7.3387 | 7.004 | 6.7296 | 6.4316 | 6.1285 | 5.1989 | 4.5673 | 4.4938 | 6.2183 | 6.0387 | 5.8653 | 5.6418 | 5.3908 | 4.8438 | 4.4571 | 4.051 | 3.6265 | 2.2265 | 1.2183 | 1.1959
|  | FRENCHAY ROAD PRIMARY | HE |  |  |  |  | 6.401 | 6.2051 | 6.0428 | 5.8377 | 5.6183 | 5.1214 | 4.6806 | 4.2836 | 3.9081 | 2.8643 | 2.2326 | 2.1622 | 7.9377 | 7.7551 | 7.5989 | 7.3979 | 7.1806 | 6.8653 | 6.5255 | 6.1806 | 5.8377 | 4.4775 | 2.7224 | -0.1786 | 6.2724 | 6.0826 | 5.9275 | 5.7234 | 5.502 | 5.0898 | 4.6867 | 4.3122 | 3.9438 | 3.0612 | 2.5316 | 2.4734
|  | FRENCHAY ROAD PRIMARY | CF |  |  |  |  | 6.5102 | 6.4704 | 6.3704 | 6.2867 | 6.1663 | 6.0153 | 5.7949 | 5.5826 | 5.3143 | 4.2734 | 3.0816 | 1.9938 | 7.9928 | 7.8755 | 7.7224 | 7.5836 | 7.3908 | 7.1643 | 6.8816 | 6.6081 | 6.2765 | 4.4683 | 1.0643 | -5.1511 | 6.3928 | 6.3143 | 6.1979 | 6.1071 | 5.9755 | 5.8224 | 5.6112 | 5.4132 | 5.1592 | 4.203 | 3.1775 | 2.301
FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER PRIMARY | MINIMUM HEADROOM | SZ 34325 86965 | NO | YES | 0.092 | 7.8255 | 7.5612 | 7.2357 | 6.8765 | 6.85 | 6.3306 | 5.752 | 5.1796 | 4.7653 | 2.2765 | 0.27347 | -0.83367 | 8.3867 | 8.2082 | 7.9551 | 7.6561 | 7.6653 | 7.3102 | 6.9031 | 6.4898 | 6.2184 | 4.7204 | 3.1204 | -0.78878 | 7.5276 | 7.2612 | 6.9316 | 6.5633 | 6.5806 | 6.0888 | 5.5367 | 4.9847 | 4.6133 | 2.5347 | 0.78163 | -0.16429
|  | FRESHWATER PRIMARY | EE |  |  |  |  | 7.8255 | 7.5612 | 7.2357 | 6.8765 | 6.85 | 6.3306 | 5.752 | 5.1796 | 4.7653 | 2.4816 | 0.75204 | -0.59286 | 8.3867 | 8.2082 | 7.9551 | 7.6561 | 7.6653 | 7.3102 | 6.9031 | 6.4898 | 6.2184 | 4.7204 | 3.1204 | 0.83061 | 7.5276 | 7.2612 | 6.9316 | 6.5633 | 6.5806 | 6.0888 | 5.5367 | 4.9847 | 4.6133 | 2.6765 | 1.1969 | 0.029592
|  | FRESHWATER PRIMARY | HT |  |  |  |  | 8 | 7.799 | 7.5541 | 7.3265 | 7.0357 | 6.5071 | 5.9296 | 5.7051 | 5.152 | 2.2765 | 0.27347 | -0.83367 | 8.5531 | 8.4388 | 8.2969 | 8.1684 | 7.9857 | 7.6857 | 7.3429 | 7.3235 | 7.0102 | 5.4918 | 4.5878 | 4.1133 | 7.7286 | 7.5306 | 7.2918 | 7.0735 | 6.7888 | 6.2969 | 5.7561 | 5.6214 | 5.1133 | 2.5347 | 0.78163 | -0.16429
|  | FRESHWATER PRIMARY | HE |  |  |  |  | 8.0224 | 7.8367 | 7.6092 | 7.401 | 7.1418 | 6.7276 | 6.2653 | 6.1571 | 5.7286 | 3.3806 | 1.6929 | 0.88776 | 8.5245 | 8.3959 | 8.2327 | 8.0888 | 7.899 | 7.6153 | 7.2837 | 7.2633 | 6.9571 | 5.2265 | 3.6143 | 1.5306 | 7.7459 | 7.5643 | 7.3408 | 7.1418 | 6.8837 | 6.4929 | 6.049 | 6.0133 | 5.6061 | 3.4949 | 2.0622 | 1.3765
|  | FRESHWATER PRIMARY | CF |  |  |  |  | 8.1878 | 8.0449 | 7.9286 | 7.7653 | 7.6245 | 7.4388 | 7.2224 | 6.9949 | 6.7561 | 5.6918 | 4.0224 | 2.452 | 8.601 | 8.4796 | 8.3714 | 8.2286 | 8.0867 | 7.8969 | 7.6765 | 7.4143 | 7.1398 | 5.8082 | 3.3398 | -0.78878 | 7.899 | 7.7541 | 7.6388 | 7.4776 | 7.3439 | 7.1571 | 6.9388 | 6.7041 | 6.4602 | 5.4796 | 4.0204 | 2.7082
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FRIMLEY PRIMARY | MINIMUM HEADROOM | SU 87745 57942 | NO | NO | 16.276 | -1.8058 | -2.7588 | -3.8966 | -5.1497 | -6.4231 | -7.7344 | -9.2007 | -10.6548 | -11.7272 | -17.2313 | -21.3772 | -23.5354 | 2.1503 | 1.6177 | 0.87381 | 0.044216 | -0.82109 | -1.7354 | -2.7935 | -3.8599 | -4.6088 | -8.5629 | -13.7742 | -25.9844 | -1.3109 | -2.0711 | -3.0854 | -4.2099 | -5.366 | -6.5864 | -7.968 | -9.3374 | -10.2874 | -14.9099 | -18.8017 | -20.8262
|  | FRIMLEY PRIMARY | EE |  |  |  |  | -1.8058 | -2.7588 | -3.8966 | -5.1497 | -6.4231 | -7.7344 | -9.2007 | -10.6548 | -11.7272 | -17.0242 | -20.665 | -23.3895 | 2.1503 | 1.6177 | 0.87381 | 0.044216 | -0.82109 | -1.7354 | -2.7935 | -3.8599 | -4.6088 | -8.5629 | -12.6711 | -18.9844 | -1.3109 | -2.0711 | -3.0854 | -4.2099 | -5.366 | -6.5864 | -7.968 | -9.3374 | -10.2874 | -14.7966 | -18.168 | -20.7129
|  | FRIMLEY PRIMARY | HT |  |  |  |  | -1.3844 | -2.4976 | -3.5456 | -4.3558 | -5.4558 | -6.6027 | -7.8568 | -9.1558 | -10.4813 | -17.2313 | -21.3772 | -23.5354 | 2.6697 | 2.0728 | 1.4881 | 1.1605 | 0.56258 | -0.057824 | -0.75884 | -1.5048 | -2.2762 | -5.8701 | -7.7711 | -8.665 | -0.84252 | -1.7884 | -2.7139 | -3.3395 | -4.3037 | -5.3354 | -6.4711 | -7.6527 | -8.866 | -14.9099 | -18.8017 | -20.8262
|  | FRIMLEY PRIMARY | HE |  |  |  |  | -1.3609 | -2.4558 | -3.5088 | -4.317 | -5.4231 | -6.4109 | -7.519 | -8.6752 | -9.8639 | -15.967 | -19.9864 | -21.6772 | 2.534 | 1.8595 | 1.183 | 0.75646 | 0.038094 | -0.65476 | -1.4599 | -2.3252 | -3.2374 | -8.2017 | -12.6762 | -18.5905 | -0.8364 | -1.769 | -2.6986 | -3.3242 | -4.2966 | -5.1966 | -6.219 | -7.2915 | -8.3956 | -13.8844 | -17.615 | -19.2354
|  | FRIMLEY PRIMARY | CF |  |  |  |  | -0.81293 | -1.5895 | -2.3037 | -3.0986 | -3.5507 | -3.9731 | -4.4782 | -5.017 | -5.5803 | -9.8354 | -14.1721 | -17.9517 | 2.7942 | 2.2616 | 1.731 | 1.1432 | 0.82789 | 0.32075 | -0.28129 | -0.92925 | -1.6242 | -6.5895 | -13.7742 | -25.9844 | -0.35272 | -1.0088 | -1.6395 | -2.3425 | -2.6629 | -3.0639 | -3.5527 | -4.0752 | -4.6252 | -8.6068 | -12.3997 | -15.617
MELKSHAM GSP | FROME BSP | FROME PRIMARY | MINIMUM HEADROOM | ST 78850 48051 | NO | NO | 9.952 | 14.9076 | 13.7586 | 12.4514 | 11.2025 | 9.7198 | 8.0137 | 5.8188 | 3.6627 | 2.0851 | -6.4802 | -13.5761 | -17.1945 | 20.829 | 20.1014 | 19.1902 | 18.2984 | 17.2953 | 16.1198 | 14.6259 | 13.1188 | 12.1157 | 6.2545 | 0.3045 | -13.7853 | 16.3157 | 15.4116 | 14.0994 | 12.8157 | 11.3902 | 9.7433 | 7.6463 | 5.5749 | 4.1045 | -3.219 | -9.1751 | -12.0128
|  | FROME PRIMARY | EE |  |  |  |  | 14.9076 | 13.7586 | 12.4514 | 11.2025 | 9.7198 | 8.0137 | 5.8188 | 3.6627 | 2.0851 | -6.4435 | -12.7394 | -16.6282 | 20.829 | 20.1014 | 19.1902 | 18.2984 | 17.2953 | 16.1198 | 14.6259 | 13.1188 | 12.1157 | 6.2545 | 0.48818 | -7.0445 | 16.3157 | 15.4116 | 14.0994 | 12.8157 | 11.3902 | 9.7433 | 7.6463 | 5.5749 | 4.1045 | -3.219 | -8.322 | -11.5128
|  | FROME PRIMARY | HT |  |  |  |  | 15.1821 | 13.9106 | 12.7086 | 11.7739 | 10.5382 | 9.0412 | 7.1392 | 5.2157 | 3.4463 | -6.4802 | -13.5761 | -17.1945 | 21.2576 | 20.4872 | 19.78 | 19.3412 | 18.6025 | 17.7749 | 16.6923 | 15.5545 | 14.5188 | 9.3106 | 6.0218 | 4.5106 | 16.9167 | 15.7086 | 14.5565 | 13.8443 | 12.6525 | 11.2514 | 9.4586 | 7.5984 | 5.8708 | -3.2006 | -9.1751 | -12.0128
|  | FROME PRIMARY | HE |  |  |  |  | 15.3045 | 14.0035 | 12.7759 | 11.9116 | 10.7025 | 9.4025 | 7.6923 | 5.9831 | 4.3586 | -4.622 | -10.9782 | -13.3955 | 21.2474 | 20.3545 | 19.528 | 19.0555 | 18.2351 | 17.3627 | 16.23 | 15.0433 | 13.8596 | 7.3147 | 1.4137 | -5.4965 | 17.0514 | 15.8157 | 14.6412 | 14.0147 | 12.881 | 11.6586 | 10.0494 | 8.4076 | 6.8045 | -1.2965 | -6.421 | -8.3057
|  | FROME PRIMARY | CF |  |  |  |  | 15.9331 | 15.1341 | 14.2494 | 13.3065 | 12.6106 | 11.9351 | 10.9882 | 10.0555 | 9.2025 | 3.0504 | -3.2322 | -8.2618 | 21.5433 | 20.9616 | 20.2555 | 19.5147 | 19.0433 | 18.3698 | 17.4912 | 16.5821 | 15.6667 | 9.3025 | 0.3045 | -13.7853 | 17.5606 | 16.8127 | 15.9392 | 15.0157 | 14.6137 | 13.9443 | 13.0127 | 12.0657 | 11.1657 | 5.1923 | -0.22203 | -4.5128
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE PRIMARY | MINIMUM HEADROOM | SU 84935 93873 | NO | NO | 1.326 | 11.1714 | 10.549 | 10.3306 | 9.7031 | 9.0265 | 7.9367 | 6.698 | 5.4541 | 4.5633 | -0.068367 | -4.0347 | -6.1061 | 14.7847 | 14.3102 | 14.1071 | 13.601 | 13.0459 | 12.2888 | 11.3847 | 10.4663 | 9.8133 | 6.2194 | 1.9449 | -8.5102 | 10.9694 | 10.3694 | 10.1714 | 9.5663 | 8.9122 | 7.8908 | 6.7204 | 5.5469 | 4.7235 | 0.65918 | -2.8112 | -4.6112
|  | FRYERS LANE PRIMARY | EE |  |  |  |  | 11.1714 | 10.549 | 10.3306 | 9.7031 | 9.0265 | 7.9367 | 6.698 | 5.4541 | 4.5633 | -0.0030612 | -3.3061 | -5.8224 | 14.7847 | 14.3102 | 14.1071 | 13.601 | 13.0459 | 12.2888 | 11.3847 | 10.4663 | 9.8133 | 6.2194 | 2.4827 | -3.0531 | 10.9694 | 10.3694 | 10.1714 | 9.5663 | 8.9122 | 7.8908 | 6.7204 | 5.5469 | 4.7235 | 0.65918 | -2.1571 | -4.3714
|  | FRYERS LANE PRIMARY | HT |  |  |  |  | 11.5888 | 11.1714 | 10.6847 | 10.1531 | 9.9776 | 9.0551 | 8.0347 | 6.9633 | 5.849 | -0.068367 | -4.0347 | -6.1061 | 15.201 | 14.9408 | 14.6276 | 14.2806 | 14.1765 | 13.6724 | 13.0867 | 12.4643 | 11.8133 | 8.5908 | 6.6888 | 5.8 | 11.3888 | 10.9929 | 10.5337 | 10.0224 | 9.8724 | 9.0245 | 8.0796 | 7.0847 | 6.0469 | 0.68163 | -2.8112 | -4.6112
|  | FRYERS LANE PRIMARY | HE |  |  |  |  | 11.6041 | 11.2143 | 10.7602 | 10.2622 | 10.1245 | 9.351 | 8.4796 | 7.5582 | 6.601 | 1.5469 | -1.8633 | -3.2755 | 15.101 | 14.7949 | 14.4388 | 14.0316 | 13.8582 | 13.3143 | 12.6827 | 11.9959 | 11.2684 | 7.0969 | 3.1755 | -1.8724 | 11.399 | 11.0296 | 10.599 | 10.1204 | 10.0031 | 9.2857 | 8.4755 | 7.6122 | 6.7173 | 2.1 | -0.83776 | -2.0602
|  | FRYERS LANE PRIMARY | CF |  |  |  |  | 11.9408 | 11.6714 | 11.4388 | 11.1388 | 10.8112 | 10.4327 | 10.4378 | 10.0133 | 9.5633 | 6.2398 | 2.7867 | -0.44286 | 15.2633 | 15.0041 | 14.749 | 14.4296 | 14.0541 | 13.6112 | 13.4031 | 12.8837 | 12.3235 | 8.2367 | 1.9449 | -8.5102 | 11.7092 | 11.451 | 11.2265 | 10.9367 | 10.6173 | 10.2561 | 10.2714 | 9.8653 | 9.4347 | 6.3041 | 3.1541 | 0.3551
COWLEY GSP | DRAYTON BSP | FULSCOT PRIMARY | MINIMUM HEADROOM | SU 54413 89511 | NO | YES | 7.803 | 7.7249 | 6.6055 | 6.03 | 5.0973 | 3.7524 | 3.1412 | 1.9851 | -0.17104 | -1.9751 | -8.0394 | -12.9598 | -17.1302 | 12.6371 | 11.9463 | 11.4749 | 10.8432 | 9.5657 | 9.0228 | 8.0943 | 5.8616 | 4.133 | -1.3047 | -7.0455 | -14.7312 | 10.2432 | 9.2779 | 8.7116 | 7.8606 | 6.4157 | 5.8065 | 4.6912 | 2.2494 | 0.32182 | -5.6812 | -10.6506 | -15.3996
|  | FULSCOT PRIMARY | EE |  |  |  |  | 7.7249 | 6.6055 | 6.1034 | 5.1871 | 4.2463 | 3.1412 | 2.0647 | 0.61263 | -0.39757 | -5.4955 | -11.4333 | -14.4374 | 12.6371 | 11.9463 | 11.6739 | 11.0973 | 10.3504 | 9.5024 | 8.7647 | 7.6106 | 6.8626 | 2.6371 | -4.4119 | -10.0608 | 10.2432 | 9.2779 | 8.8647 | 8.0534 | 7.1259 | 6.0514 | 5.0616 | 3.6351 | 2.6871 | -2.1598 | -8.4425 | -11.4649
|  | FULSCOT PRIMARY | HT |  |  |  |  | 8.0096 | 6.9412 | 6.083 | 5.2086 | 3.9769 | 3.2514 | 1.9851 | 0.88304 | -0.57002 | -6.967 | -12.9598 | -16.8068 | 12.9575 | 12.3351 | 11.7902 | 11.3075 | 10.2545 | 9.7555 | 8.8381 | 8.1912 | 7.1045 | 2.7402 | -2.4027 | -5.9057 | 10.533 | 9.6024 | 8.8096 | 8.0412 | 6.7473 | 6.03 | 4.7759 | 3.7626 | 2.3188 | -3.8935 | -10.171 | -14.3241
|  | FULSCOT PRIMARY | HE |  |  |  |  | 8.032 | 6.9606 | 6.03 | 5.0973 | 3.7524 | 3.1545 | 2.0351 | -0.17104 | -1.9751 | -8.0394 | -12.9537 | -17.1302 | 12.882 | 12.1881 | 11.4749 | 10.8432 | 9.5657 | 9.0228 | 8.0943 | 5.8616 | 4.133 | -1.3047 | -7.0455 | -14.7312 | 10.5494 | 9.6055 | 8.7116 | 7.8606 | 6.4157 | 5.8065 | 4.6912 | 2.2494 | 0.32182 | -5.6812 | -10.6506 | -15.3996
|  | FULSCOT PRIMARY | CF |  |  |  |  | 8.2973 | 7.4871 | 6.9453 | 6.2381 | 5.6657 | 5.1259 | 4.9259 | 4.2912 | 3.6014 | -0.65063 | -4.5129 | -8.0057 | 13.0055 | 12.4963 | 12.1279 | 11.6075 | 11.1137 | 10.5524 | 10.2637 | 9.6616 | 8.982 | 4.4443 | -1.8445 | -11.2904 | 10.7922 | 10.1198 | 9.6565 | 9.0177 | 8.4698 | 7.9341 | 7.7657 | 7.1688 | 6.5116 | 2.382 | -1.5241 | -4.9802
COWLEY GSP | WITNEY BSP | FYFIELD PRIMARY | MINIMUM HEADROOM | SU 42256 99551 | NO | NO | 7.492 | 0.65347 | 0.42592 | 0.073878 | -0.49653 | -1.1261 | -1.4435 | -2.1659 | -2.8863 | -3.1884 | -4.7649 | -5.8853 | -6.6353 | 2.6412 | 2.4627 | 2.2086 | 1.8341 | 1.431 | 1.3586 | 0.91571 | 0.46469 | 0.25755 | -0.93633 | -2.5761 | -6.2598 | 0.85245 | 0.63306 | 0.30551 | -0.2149 | -0.79347 | -0.98531 | -1.6292 | -2.27 | -2.5373 | -3.8782 | -4.8557 | -5.4659
|  | FYFIELD PRIMARY | EE |  |  |  |  | 0.65347 | 0.42592 | 0.073878 | -0.49653 | -1.1261 | -1.4435 | -2.1659 | -2.8863 | -3.1884 | -4.7649 | -5.7057 | -6.4312 | 2.6412 | 2.4627 | 2.2086 | 1.8341 | 1.431 | 1.3586 | 0.91571 | 0.46469 | 0.25755 | -0.93633 | -2.1792 | -4.0802 | 0.85245 | 0.63306 | 0.30551 | -0.2149 | -0.79347 | -0.98531 | -1.6292 | -2.27 | -2.5373 | -3.8782 | -4.6945 | -5.2955
|  | FYFIELD PRIMARY | HT |  |  |  |  | 0.78918 | 0.61878 | 0.34429 | -0.15061 | -0.66286 | -1.3424 | -2.0588 | -2.4516 | -2.8527 | -4.7618 | -5.8853 | -6.6353 | 2.8086 | 2.7045 | 2.5269 | 2.2443 | 1.9912 | 1.628 | 1.2269 | 1.1453 | 0.91367 | -0.12 | -0.65776 | -0.99551 | 1.0096 | 0.84327 | 0.5902 | 0.15857 | -0.27918 | -0.86796 | -1.5027 | -1.7588 | -2.1322 | -3.872 | -4.8557 | -5.4659
|  | FYFIELD PRIMARY | HE |  |  |  |  | 0.80143 | 0.64122 | 0.38102 | -0.10163 | -0.60265 | -1.2231 | -1.8863 | -2.218 | -2.5567 | -4.3506 | -5.2853 | -5.7986 | 2.7718 | 2.6494 | 2.4678 | 2.1749 | 1.8871 | 1.5198 | 1.1157 | 0.9749 | 0.72184 | -0.72306 | -1.9802 | -3.7894 | 1.0188 | 0.86163 | 0.62184 | 0.20245 | -0.2251 | -0.76592 | -1.3547 | -1.5578 | -1.8812 | -3.5118 | -4.3088 | -4.7231
|  | FYFIELD PRIMARY | CF |  |  |  |  | 0.90653 | 0.76673 | 0.60143 | 0.21265 | -0.2251 | -0.62 | -1.0894 | -1.5741 | -1.8118 | -2.7486 | -3.9302 | -5.068 | 2.8218 | 2.6953 | 2.5667 | 2.3137 | 2.028 | 1.7565 | 1.4157 | 1.0647 | 0.81367 | -0.41388 | -2.5761 | -6.2598 | 1.1188 | 0.97592 | 0.82694 | 0.49327 | 0.11776 | -0.20776 | -0.62102 | -1.0588 | -1.3159 | -2.1322 | -3.1802 | -4.1343
LOVEDEAN GSP | HAVANT BSP | GABLE HEAD PRIMARY | MINIMUM HEADROOM | SZ 72204 99904 | NO | YES | 2.065 | 15.6628 | 15.1302 | 14.9577 | 14.2873 | 13.5537 | 12.5241 | 11.3904 | 10.2741 | 9.4526 | 5.3445 | 2.3282 | 0.52509 | 17.7547 | 17.3261 | 17.1955 | 16.6914 | 16.1363 | 15.4384 | 14.6414 | 13.8445 | 13.271 | 10.3506 | 6.4037 | -3.0953 | 15.5179 | 14.9812 | 14.87 | 14.273 | 13.5955 | 12.6649 | 11.619 | 10.5863 | 9.8802 | 6.1588 | 3.4833 | 2.0312
|  | GABLE HEAD PRIMARY | EE |  |  |  |  | 15.6628 | 15.1302 | 14.9577 | 14.2873 | 13.5537 | 12.5241 | 11.3904 | 10.2741 | 9.4526 | 5.8465 | 3.2179 | 0.96182 | 17.7547 | 17.3261 | 17.1955 | 16.6914 | 16.1363 | 15.4384 | 14.6414 | 13.8445 | 13.271 | 10.3506 | 7.0812 | 2.0445 | 15.5179 | 14.9812 | 14.87 | 14.273 | 13.5955 | 12.6649 | 11.619 | 10.5863 | 9.8802 | 6.5516 | 4.2516 | 2.3894
|  | GABLE HEAD PRIMARY | HT |  |  |  |  | 15.9659 | 15.5435 | 15.1322 | 14.4955 | 13.7873 | 13.2322 | 12.2322 | 11.2057 | 10.1394 | 5.3445 | 2.3282 | 0.52509 | 18.0894 | 17.8302 | 17.57 | 17.1782 | 16.7343 | 16.5404 | 15.9863 | 15.4067 | 14.7996 | 12.2118 | 10.8241 | 10.0537 | 15.7873 | 15.4118 | 15.0373 | 14.4761 | 13.8435 | 13.3322 | 12.422 | 11.4863 | 10.5169 | 6.1588 | 3.4833 | 2.0312
|  | GABLE HEAD PRIMARY | HE |  |  |  |  | 16.021 | 15.6373 | 15.2792 | 14.7016 | 14.0618 | 13.6904 | 12.8812 | 12.0557 | 11.1975 | 7.3577 | 4.7445 | 3.2863 | 18.0261 | 17.7302 | 17.4465 | 17.0169 | 16.5353 | 16.3261 | 15.7588 | 15.1618 | 14.523 | 11.1955 | 7.8935 | 3.1975 | 15.8424 | 15.5016 | 15.173 | 14.6669 | 14.0761 | 13.7547 | 13.022 | 12.2751 | 11.4965 | 7.9659 | 5.672 | 4.4965
|  | GABLE HEAD PRIMARY | CF |  |  |  |  | 16.2986 | 16.0567 | 15.8343 | 15.4302 | 14.9863 | 14.5312 | 14.4679 | 14.023 | 13.5516 | 10.9506 | 8.2649 | 5.622 | 18.1486 | 17.9169 | 17.6935 | 17.3363 | 16.92 | 16.4577 | 16.27 | 15.7812 | 15.2588 | 11.8261 | 6.4037 | -3.0953 | 16.0955 | 15.8843 | 15.6833 | 15.3047 | 14.8853 | 14.4506 | 14.5006 | 14.0822 | 13.6394 | 11.1945 | 8.8169 | 6.4333
MINETY GSP |  | GALILEO PRIMARY | MINIMUM HEADROOM | SU 10596 83733 | NO | NO | 4.591 | 29.2147 | 29.0983 | 28.9851 | 28.7688 | 28.4473 | 28.0902 | 27.7392 | 27.2871 | 26.9075 | 25.5065 | 24.5881 | 24.3994 | 29.5769 | 29.482 | 29.3861 | 29.1677 | 28.8167 | 28.4096 | 28.1871 | 27.7657 | 27.432 | 25.8932 | 22.9902 | 17.2402 | 29.1371 | 28.9871 | 28.8341 | 28.6463 | 28.229 | 27.8218 | 27.48 | 27.0443 | 26.7055 | 25.5953 | 24.9606 | 24.681
|  | GALILEO PRIMARY | EE |  |  |  |  | 29.2147 | 29.0983 | 28.9851 | 28.8412 | 28.4616 | 28.0902 | 27.7453 | 27.2871 | 26.93 | 25.5065 | 24.6534 | 24.7698 | 29.5769 | 29.482 | 29.3861 | 29.231 | 28.8167 | 28.4096 | 28.1871 | 27.7657 | 27.432 | 25.8932 | 24.1136 | 21.4922 | 29.1371 | 28.9871 | 28.8341 | 28.6463 | 28.229 | 27.8218 | 27.48 | 27.0443 | 26.7055 | 25.681 | 25.082 | 25.2024
|  | GALILEO PRIMARY | HT |  |  |  |  | 29.3004 | 29.2126 | 29.131 | 28.7688 | 28.4473 | 28.1585 | 27.7392 | 27.2943 | 26.9075 | 25.583 | 24.5881 | 24.3994 | 29.6616 | 29.5943 | 29.529 | 29.1677 | 28.8606 | 28.6096 | 28.333 | 28.079 | 27.8912 | 27.2341 | 26.7392 | 26.582 | 29.2585 | 29.1453 | 29.032 | 28.6483 | 28.2953 | 27.9575 | 27.5749 | 27.2096 | 26.9024 | 25.7881 | 25.0259 | 24.8861
|  | GALILEO PRIMARY | HE |  |  |  |  | 29.2973 | 29.2106 | 29.1279 | 29.0188 | 28.6769 | 28.3963 | 28.0096 | 27.5585 | 27.1341 | 25.7636 | 25.0126 | 24.7361 | 29.6483 | 29.5769 | 29.5055 | 29.3902 | 29.0269 | 28.7269 | 28.3575 | 27.9575 | 27.5728 | 26.1463 | 24.3575 | 21.6177 | 29.2483 | 29.131 | 29.0157 | 28.8698 | 28.4912 | 28.1565 | 27.731 | 27.3014 | 26.8963 | 25.5953 | 24.9606 | 24.681
|  | GALILEO PRIMARY | CF |  |  |  |  | 29.382 | 29.3341 | 29.28 | 29.231 | 29.1626 | 28.9739 | 28.7626 | 28.5116 | 28.2769 | 27.032 | 25.9596 | 24.9626 | 29.7085 | 29.6636 | 29.6045 | 29.5075 | 29.383 | 29.1106 | 28.8034 | 28.4443 | 28.0841 | 26.1708 | 22.9902 | 17.2402 | 29.3688 | 29.3096 | 29.2371 | 29.1688 | 29.081 | 28.8718 | 28.629 | 28.3361 | 28.0606 | 26.7871 | 25.7759 | 24.981
LOVEDEAN GSP | PORTSMOUTH BSP | GAMBLE ROAD PRIMARY | MINIMUM HEADROOM | SU 64771 01769 | NO | YES | 9.36 | 2.4548 | 1.3497 | 0.088449 | -1.4024 | -3.4381 | -5.7513 | -7.8218 | -10.1401 | -12.1207 | -17.9871 | -21.0105 | -20.5013 | 5.5476 | 4.6936 | 3.7436 | 2.5997 | 1.1772 | -0.40645 | -1.8085 | -3.5105 | -5.0003 | -11.7585 | -20.3656 | -40.3258 | 3.1987 | 2.1854 | 1.0333 | -0.34522 | -2.1677 | -4.2309 | -6.0146 | -8.1064 | -9.8564 | -15.0911 | -17.7432 | -17.3126
|  | GAMBLE ROAD PRIMARY | EE |  |  |  |  | 2.4548 | 1.3497 | 0.088449 | -1.4024 | -3.4381 | -5.7513 | -7.8218 | -10.1401 | -12.1207 | -17.9871 | -19.5513 | -18.5911 | 5.5476 | 4.6936 | 3.7436 | 2.5997 | 1.1772 | -0.40645 | -1.8085 | -3.5105 | -5.0003 | -11.7585 | -17.4299 | -26.4646 | 3.1987 | 2.1854 | 1.0333 | -0.34522 | -2.1677 | -4.2309 | -6.0146 | -8.1064 | -9.8564 | -15.0911 | -16.4187 | -15.7554
|  | GAMBLE ROAD PRIMARY | HT |  |  |  |  | 2.7231 | 1.817 | 0.79457 | -0.75441 | -2.5422 | -4.382 | -6.3575 | -8.3422 | -10.1585 | -17.3626 | -21.0105 | -20.5013 | 6.0415 | 5.4782 | 4.8527 | 3.967 | 2.9466 | 1.9211 | 0.74151 | -0.484 | -1.7248 | -6.6299 | -9.0809 | -9.1044 | 3.565 | 2.765 | 1.8609 | 0.52314 | -1.032 | -2.6156 | -4.3636 | -6.134 | -7.8054 | -14.3595 | -17.7432 | -17.3126
|  | GAMBLE ROAD PRIMARY | HE |  |  |  |  | 3.0068 | 2.2282 | 1.3558 | 0.32416 | -1.0064 | -2.5013 | -4.134 | -5.7779 | -7.4126 | -13.636 | -15.7013 | -15.6646 | 6.0038 | 5.4027 | 4.7466 | 3.9507 | 2.9854 | 1.9374 | 0.73029 | -0.534 | -1.8493 | -8.8452 | -15.0044 | -24.083 | 3.7742 | 3.0833 | 2.315 | 1.3946 | 0.22416 | -1.0707 | -2.5218 | -3.9891 | -5.4626 | -10.9503 | -12.7605 | -12.7167
|  | GAMBLE ROAD PRIMARY | CF |  |  |  |  | 3.4527 | 3.2078 | 2.5956 | 1.9303 | 1.1476 | 0.25273 | -0.70543 | -1.733 | -2.7738 | -8.2789 | -13.7544 | -17.2687 | 6.2262 | 5.866 | 5.2976 | 4.6589 | 3.8701 | 2.9527 | 1.9272 | 0.81396 | -0.36563 | -7.9687 | -20.3656 | -40.3258 | 4.1915 | 3.9374 | 3.3997 | 2.818 | 2.1231 | 1.3517 | 0.51498 | -0.40237 | -1.333 | -6.2054 | -11.0799 | -14.1728
IVER 132KV GSP | DENHAM BSP | GERRARDS CROSS PRIMARY | MINIMUM HEADROOM | SU 99973 87964 | NO | YES | 1.763 | -1.175 | -1.4791 | -1.8087 | -2.173 | -2.1372 | -2.6617 | -3.2474 | -3.8403 | -4.2454 | -6.6995 | -8.6281 | -9.7648 | 1.5148 | 1.2577 | 0.98418 | 0.67806 | 0.71276 | 0.35561 | -0.054592 | -0.47602 | -0.74949 | -2.2617 | -4.3964 | -9.4189 | -1.0602 | -1.3663 | -1.7061 | -2.0847 | -1.9694 | -2.4622 | -3.0184 | -3.5837 | -3.9408 | -6.0429 | -7.7561 | -8.7786
|  | GERRARDS CROSS PRIMARY | EE |  |  |  |  | -1.175 | -1.4791 | -1.8087 | -2.173 | -2.1372 | -2.6617 | -3.2474 | -3.8403 | -4.2454 | -6.4607 | -8.1811 | -9.574 | 1.5148 | 1.2577 | 0.98418 | 0.67806 | 0.71276 | 0.35561 | -0.054592 | -0.47602 | -0.74949 | -2.2617 | -4.0311 | -6.6883 | -1.0602 | -1.3663 | -1.7061 | -2.0847 | -1.9694 | -2.4622 | -3.0184 | -3.5837 | -3.9408 | -5.8439 | -7.3561 | -8.6122
|  | GERRARDS CROSS PRIMARY | HT |  |  |  |  | -1.0495 | -1.2464 | -1.4872 | -1.7087 | -1.9954 | -2.5311 | -3.1209 | -3.3128 | -3.8679 | -6.6995 | -8.6281 | -9.7648 | 1.6893 | 1.5577 | 1.3852 | 1.2423 | 1.0413 | 0.74133 | 0.39847 | 0.4301 | 0.11786 | -1.3036 | -2.0903 | -2.5291 | -0.8949 | -1.0969 | -1.35 | -1.5633 | -1.851 | -2.3571 | -2.9235 | -2.9612 | -3.4724 | -6.0429 | -7.7561 | -8.7786
|  | GERRARDS CROSS PRIMARY | HE |  |  |  |  | -0.99337 | -1.2128 | -1.4362 | -1.6423 | -1.9097 | -2.3464 | -2.4587 | -2.8913 | -3.3352 | -5.7117 | -7.4179 | -8.2444 | 1.6832 | 1.4832 | 1.2883 | 1.1179 | 0.88827 | 0.5801 | 0.56071 | 0.24439 | -0.089286 | -1.923 | -3.7107 | -6.1342 | -0.83878 | -1.0724 | -1.3133 | -1.5082 | -1.7776 | -2.201 | -2.198 | -2.6071 | -3.0286 | -5.1633 | -6.6694 | -7.4184
|  | GERRARDS CROSS PRIMARY | CF |  |  |  |  | -0.83112 | -0.93724 | -1.1179 | -1.2791 | -1.4036 | -1.5954 | -1.8372 | -2.1056 | -1.9464 | -3.4964 | -5.1342 | -6.727 | 1.7536 | 1.624 | 1.423 | 1.2444 | 1.0913 | 0.86071 | 0.58214 | 0.27908 | 0.32908 | -1.5515 | -4.3964 | -9.4189 | -0.69592 | -0.81633 | -1.0194 | -1.1929 | -1.3102 | -1.5143 | -1.7694 | -2.051 | -1.8061 | -3.2857 | -4.7245 | -6.0694
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM PRIMARY | MINIMUM HEADROOM | ST 80185 25765 | NO | NO | 9.028 | 17.1583 | 16.1409 | 15.1062 | 14.4103 | 13.6195 | 12.8583 | 12.0348 | 11.3471 | 10.7705 | 7.0522 | 5.8491 | 5.4879 | 18.4246 | 17.6154 | 16.8103 | 16.4317 | 16.0195 | 15.5889 | 15.1205 | 14.7093 | 14.3654 | 11.0195 | 10.0103 | 7.7328 | 17.1093 | 16.2399 | 15.3715 | 14.7746 | 14.1022 | 13.443 | 12.7256 | 12.1144 | 11.6154 | 7.9011 | 6.5817 | 6.4624
|  | GILLINGHAM PRIMARY | EE |  |  |  |  | 17.1583 | 16.1409 | 15.1062 | 14.4103 | 13.6195 | 12.8583 | 12.0348 | 11.3471 | 10.7705 | 7.2705 | 6.4144 | 5.7858 | 18.4246 | 17.6154 | 16.8103 | 16.4317 | 16.0195 | 15.5889 | 15.1205 | 14.7093 | 14.3654 | 11.842 | 10.9185 | 9.5889 | 17.1093 | 16.2399 | 15.3715 | 14.7746 | 14.1022 | 13.443 | 12.7256 | 12.1144 | 11.6154 | 8.5613 | 7.8358 | 7.2971
|  | GILLINGHAM PRIMARY | HT |  |  |  |  | 17.3256 | 16.3777 | 15.3797 | 14.7511 | 14.0266 | 13.3368 | 12.6093 | 12.0266 | 11.3083 | 7.4664 | 6.3144 | 5.7613 | 18.5664 | 17.8175 | 17.0624 | 16.7552 | 16.4073 | 16.0593 | 15.6848 | 15.3777 | 14.944 | 12.5664 | 11.9889 | 11.742 | 17.2858 | 16.5001 | 15.6501 | 15.1205 | 14.5134 | 13.9277 | 13.3011 | 12.7971 | 12.1624 | 8.7746 | 7.7481 | 7.2838
|  | GILLINGHAM PRIMARY | HE |  |  |  |  | 17.2797 | 16.3103 | 15.2889 | 14.6317 | 13.8705 | 13.1736 | 12.4215 | 11.8103 | 11.1573 | 7.0522 | 5.8491 | 5.4879 | 18.495 | 17.7226 | 16.9297 | 16.5797 | 16.1828 | 15.7838 | 15.3491 | 14.9552 | 14.4287 | 11.0195 | 10.0103 | 9.1083 | 17.244 | 16.442 | 15.5634 | 15.0073 | 14.3675 | 13.7715 | 13.1195 | 12.5848 | 12.0062 | 7.9011 | 6.5817 | 6.4624
|  | GILLINGHAM PRIMARY | CF |  |  |  |  | 17.4644 | 16.5879 | 15.8858 | 15.2062 | 14.1807 | 13.7093 | 13.1756 | 12.7348 | 12.2777 | 9.6766 | 7.7522 | 6.394 | 18.6073 | 17.8705 | 17.3338 | 16.8715 | 16.1052 | 15.8113 | 15.4726 | 15.1695 | 14.8491 | 12.9124 | 10.542 | 7.7328 | 17.4093 | 16.6777 | 16.1022 | 15.5297 | 14.642 | 14.2532 | 13.8011 | 13.4175 | 13.0195 | 10.7511 | 8.4664 | 7.0828
FLEET-BRAMLEY GSP | ALDERSHOT BSP | GODALMING PRIMARY | MINIMUM HEADROOM | SU 96743 44375 | NO | YES | 3.967 | 8.3776 | 7.5122 | 6.9469 | 5.9745 | 4.8449 | 3.2388 | 1.3214 | -0.51939 | -2.0357 | -10.7378 | -15.0765 | -16.0898 | 13.1582 | 12.4612 | 12.0551 | 11.2755 | 10.4255 | 9.3704 | 8.1316 | 6.8867 | 5.851 | -0.48571 | -3.5173 | -13.7469 | 9.3102 | 8.4806 | 7.951 | 6.8684 | 5.549 | 4.0143 | 2.1796 | 0.41939 | -1.0224 | -9.3245 | -13.4092 | -14.3327
|  | GODALMING PRIMARY | EE |  |  |  |  | 8.3776 | 7.5122 | 6.9469 | 5.9745 | 4.8449 | 3.2388 | 1.3214 | -0.51939 | -2.0357 | -7.3143 | -10.5092 | -13.0786 | 13.1582 | 12.4612 | 12.0551 | 11.2755 | 10.4255 | 9.3704 | 8.1316 | 6.8867 | 5.851 | 1.6296 | -2.2316 | -7.8163 | 9.3102 | 8.4806 | 7.951 | 6.8684 | 5.549 | 4.0143 | 2.1796 | 0.41939 | -1.0224 | -5.9816 | -8.1031 | -10.3541
|  | GODALMING PRIMARY | HT |  |  |  |  | 9.1082 | 8.5449 | 7.8857 | 7.15 | 6.698 | 5.5143 | 4.1571 | 2.7378 | 1.2745 | -6.0653 | -10.7153 | -12.9092 | 13.8612 | 13.4847 | 13.0245 | 12.5082 | 12.2643 | 11.5694 | 10.748 | 9.8735 | 8.9551 | 4.399 | 2.2694 | 1.4286 | 10.0296 | 9.4959 | 8.8724 | 8.1704 | 7.7531 | 6.6541 | 5.3918 | 4.0673 | 2.702 | -4.0745 | -8.2582 | -10.1561
|  | GODALMING PRIMARY | HE |  |  |  |  | 8.9378 | 8.301 | 7.5571 | 6.7204 | 6.0204 | 4.5316 | 2.6969 | 0.73776 | -1.3163 | -10.7378 | -15.0765 | -16.0898 | 13.6214 | 13.1245 | 12.5347 | 11.8643 | 11.449 | 10.6092 | 9.3316 | 7.8878 | 6.3694 | -0.48571 | -3.5173 | -8.5122 | 9.8612 | 9.2582 | 8.55 | 7.752 | 6.6888 | 5.2694 | 3.5102 | 1.6306 | -0.33265 | -9.3245 | -13.4092 | -14.3327
|  | GODALMING PRIMARY | CF |  |  |  |  | 9.5163 | 9.1255 | 8.7357 | 8.2582 | 7.7316 | 7.5235 | 6.899 | 6.1918 | 5.098 | -1.5571 | -7.4153 | -10.8408 | 13.9541 | 13.5765 | 13.1959 | 12.7347 | 12.1949 | 11.9224 | 11.2551 | 10.5235 | 9.7449 | 4.448 | -2.8918 | -13.7469 | 10.4082 | 10.0316 | 9.6571 | 9.199 | 8.6898 | 8.5051 | 7.8265 | 6.8357 | 5.7796 | -0.60612 | -6.1724 | -9.3735
WILLESDEN GSP | ACTON LANE BSP | GOLDSMITHS PRIMARY | MINIMUM HEADROOM | TQ 21089 80758 | NO | YES | 2.015 | 1.1105 | 0.62786 | -0.1201 | -1.5232 | -3.3252 | -4.9272 | -6.6028 | -8.2558 | -9.5681 | -12.9191 | -15.1721 | -16.6987 | 3.5593 | 3.1807 | 2.7123 | 2.1144 | 0.96745 | -0.1152 | -1.4611 | -2.9805 | -4.203 | -8.9172 | -13.6774 | -23.7683 | 1.4124 | 0.96449 | 0.36551 | -1.0253 | -2.7784 | -4.2916 | -5.9488 | -7.6906 | -9.0855 | -12.3345 | -14.2814 | -15.6151
|  | GOLDSMITHS PRIMARY | EE |  |  |  |  | 1.1105 | 0.62786 | -0.028265 | -0.88337 | -2.3119 | -3.7181 | -5.466 | -7.0507 | -8.5303 | -12.9191 | -14.765 | -16.5926 | 3.5593 | 3.1807 | 2.7123 | 2.1481 | 1.097 | 0.032755 | -1.304 | -2.5468 | -3.8785 | -8.9172 | -12.1591 | -17.6346 | 1.4124 | 0.96449 | 0.36551 | -0.40184 | -1.7947 | -3.1682 | -4.8814 | -6.3702 | -7.8753 | -12.3345 | -13.9192 | -15.5355
|  | GOLDSMITHS PRIMARY | HT |  |  |  |  | 1.2003 | 0.685 | -0.1201 | -1.5232 | -3.3252 | -4.9272 | -6.6028 | -8.2558 | -9.5681 | -12.7609 | -15.1721 | -16.6987 | 3.7552 | 3.4695 | 3.0358 | 2.1144 | 0.96745 | -0.1152 | -1.4611 | -2.9805 | -4.203 | -6.4417 | -7.6091 | -8.2866 | 1.5247 | 1.0798 | 0.37878 | -1.0253 | -2.7784 | -4.2916 | -5.9488 | -7.6906 | -9.0855 | -12.1151 | -14.2814 | -15.6151
|  | GOLDSMITHS PRIMARY | HE |  |  |  |  | 1.337 | 0.94724 | 0.40439 | -0.32827 | -1.614 | -2.9058 | -4.5354 | -6.3823 | -7.816 | -11.8191 | -13.464 | -14.2354 | 3.7501 | 3.4542 | 3.0889 | 2.6307 | 1.696 | 0.77663 | -0.41214 | -1.9407 | -3.3417 | -8.2285 | -11.4193 | -16.353 | 1.6461 | 1.2941 | 0.81347 | 0.17878 | -1.1253 | -2.3651 | -3.8978 | -5.6722 | -7.1376 | -11.2263 | -12.6814 | -13.3457
|  | GOLDSMITHS PRIMARY | CF |  |  |  |  | 1.5564 | 1.4452 | 1.284 | 1.1279 | 0.99622 | 0.65643 | -0.033367 | -1.0099 | -2.066 | -9.9262 | -10.9823 | -12.1711 | 3.8521 | 3.6909 | 3.4756 | 3.2521 | 3.0154 | 2.5328 | 1.7858 | 0.83684 | -0.18051 | -8.4448 | -13.6774 | -23.7683 | 1.842 | 1.7339 | 1.5727 | 1.4176 | 1.288 | 0.91347 | 0.19816 | -0.78959 | -1.8508 | -9.5386 | -10.5447 | -11.5712
NURSLING GSP | WINCHESTER BSP | GORDON ROAD PRIMARY | MINIMUM HEADROOM | SU 48217 29991 | NO | NO | 4.242 | 5.8319 | 5.287 | 4.5798 | 3.7166 | 2.7421 | 1.7339 | 0.50124 | -0.65896 | -1.6763 | -6.7232 | -9.4681 | -10.4212 | 11.3604 | 11.0594 | 10.7053 | 10.2829 | 9.6227 | 8.938 | 8.0543 | 7.2176 | 6.4931 | 2.9614 | 0.60022 | -7.7049 | 6.0359 | 5.6502 | 5.1992 | 4.6563 | 4.04 | 3.1441 | 1.9737 | 0.86655 | -0.096714 | -4.8896 | -7.461 | -8.3416
|  | GORDON ROAD PRIMARY | EE |  |  |  |  | 5.8319 | 5.287 | 4.5798 | 3.7166 | 2.7421 | 1.7339 | 0.50124 | -0.65896 | -1.6763 | -5.5732 | -7.0202 | -9.4039 | 11.3604 | 11.0594 | 10.7053 | 10.2829 | 9.6227 | 8.938 | 8.0543 | 7.2176 | 6.4931 | 3.641 | 0.60022 | -3.7967 | 6.0359 | 5.6502 | 5.1992 | 4.6563 | 4.04 | 3.1441 | 1.9737 | 0.86655 | -0.096714 | -3.7437 | -5.5692 | -7.6396
|  | GORDON ROAD PRIMARY | HT |  |  |  |  | 6.3176 | 5.9237 | 5.4655 | 4.8635 | 4.1155 | 3.2166 | 2.2543 | 1.3839 | 0.36043 | -4.6386 | -7.4651 | -9.5988 | 11.6431 | 11.4461 | 11.2125 | 10.9247 | 10.5982 | 10.1451 | 9.4808 | 8.889 | 8.1717 | 4.8206 | 3.2227 | 2.6012 | 6.3574 | 6.0737 | 5.7472 | 5.3451 | 4.8819 | 4.3278 | 3.6614 | 2.84 | 1.8666 | -2.8539 | -5.9192 | -7.7569
|  | GORDON ROAD PRIMARY | HE |  |  |  |  | 6.1951 | 5.7472 | 5.2206 | 4.4931 | 3.6319 | 2.5982 | 1.4553 | 0.39614 | -0.84671 | -6.7232 | -9.4681 | -10.4212 | 11.5584 | 11.3166 | 11.0319 | 10.6819 | 10.288 | 9.6135 | 8.7982 | 8.038 | 7.137 | 2.9614 | 1.0625 | -2.8763 | 6.2798 | 5.9666 | 5.5992 | 5.1492 | 4.6298 | 3.9768 | 2.8921 | 1.8819 | 0.6992 | -4.8896 | -7.461 | -8.3416
|  | GORDON ROAD PRIMARY | CF |  |  |  |  | 6.5921 | 6.3553 | 6.0604 | 5.6798 | 5.2319 | 4.7686 | 4.1859 | 3.5543 | 2.8635 | -1.3202 | -5.3528 | -8.2967 | 11.7523 | 11.5859 | 11.4074 | 11.1778 | 10.9033 | 10.6268 | 10.3166 | 9.9849 | 9.6196 | 6.1523 | 0.7839 | -7.7049 | 6.5574 | 6.3614 | 6.1492 | 5.8666 | 5.5349 | 5.2063 | 4.8686 | 4.5104 | 4.1166 | 0.20635 | -3.6222 | -6.3834
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | GORING PRIMARY | MINIMUM HEADROOM | SU 60305 82895 | NO | NO | 0.207 | 9.0755 | 8.9633 | 8.8092 | 8.6367 | 8.5214 | 8.2541 | 7.9469 | 7.6388 | 7.4796 | 6.6133 | 5.9235 | 5.5827 | 10.3694 | 10.2816 | 10.1602 | 10.0296 | 9.9245 | 9.7418 | 9.5214 | 9.2857 | 9.1684 | 8.498 | 7.6959 | 5.3724 | 9.4092 | 9.3082 | 9.1622 | 9.0041 | 8.8898 | 8.6418 | 8.352 | 8.0571 | 7.9082 | 7.1327 | 6.5112 | 6.2133
|  | GORING PRIMARY | EE |  |  |  |  | 9.0755 | 8.9633 | 8.8092 | 8.6367 | 8.5214 | 8.2541 | 7.9469 | 7.6388 | 7.4796 | 6.6796 | 6.0643 | 5.5827 | 10.3694 | 10.2816 | 10.1602 | 10.0296 | 9.9245 | 9.7418 | 9.5214 | 9.2857 | 9.1684 | 8.498 | 7.6959 | 6.4653 | 9.4092 | 9.3082 | 9.1622 | 9.0041 | 8.8898 | 8.6418 | 8.352 | 8.0571 | 7.9082 | 7.1929 | 6.6408 | 6.2133
|  | GORING PRIMARY | HT |  |  |  |  | 9.1673 | 9.0776 | 8.9714 | 8.8827 | 8.7561 | 8.5265 | 8.3316 | 8.0776 | 7.8143 | 6.6133 | 5.9235 | 5.8673 | 10.4612 | 10.4102 | 10.3367 | 10.2827 | 10.201 | 10.0714 | 9.9622 | 9.8153 | 9.6571 | 8.9837 | 8.6684 | 8.8 | 9.4959 | 9.4122 | 9.3122 | 9.2347 | 9.1153 | 8.9031 | 8.7235 | 8.4898 | 8.2469 | 7.1327 | 6.5112 | 6.5571
|  | GORING PRIMARY | HE |  |  |  |  | 9.1684 | 9.0857 | 8.9867 | 8.9061 | 8.7857 | 8.5898 | 8.4306 | 8.2122 | 7.9867 | 6.9296 | 6.7745 | 6.4388 | 10.4357 | 10.3684 | 10.2857 | 10.2204 | 10.1163 | 9.9837 | 9.8622 | 9.6969 | 9.5265 | 8.6184 | 8.1306 | 6.9561 | 9.498 | 9.4204 | 9.3245 | 9.2551 | 9.1398 | 8.9602 | 8.8122 | 8.6092 | 8.399 | 7.4184 | 7.3173 | 7.052
|  | GORING PRIMARY | CF |  |  |  |  | 9.2378 | 9.1816 | 9.1143 | 9.0367 | 8.9898 | 8.8959 | 8.7786 | 8.651 | 8.5867 | 7.7735 | 7.5929 | 7.05 | 10.4653 | 10.4102 | 10.3398 | 10.2602 | 10.199 | 10.0929 | 9.9643 | 9.8255 | 9.7194 | 8.7541 | 7.7214 | 5.3724 | 9.5592 | 9.5082 | 9.4459 | 9.3714 | 9.3306 | 9.2439 | 9.1347 | 9.0173 | 8.952 | 8.1786 | 8.0459 | 7.5429
IVER 132KV GSP | DENHAM BSP | GRASSINGHAM ROAD PRIMARY | MINIMUM HEADROOM | TQ 00165 90988 | NO | YES | 1.126 | 1.2268 | 0.83903 | 0.41045 | 0.41556 | 0.026781 | -0.65179 | -1.413 | -2.1804 | -2.7008 | -5.8957 | -8.2804 | -9.6283 | 10.1298 | 9.8411 | 9.5217 | 9.587 | 9.3166 | 8.9268 | 8.4676 | 8.0013 | 7.7513 | 6.4656 | 5.4911 | 4.9768 | 1.9074 | 1.536 | 1.1227 | 1.14 | 0.76862 | 0.13494 | -0.58036 | -1.2997 | -1.7702 | -4.6202 | -6.7161 | -7.8916
|  | GRASSINGHAM ROAD PRIMARY | EE |  |  |  |  | 1.2268 | 0.83903 | 0.41045 | 0.41556 | 0.026781 | -0.65179 | -1.413 | -2.1804 | -2.7008 | -5.5069 | -7.7222 | -9.4069 | 10.1298 | 9.8411 | 9.5217 | 9.587 | 9.3166 | 8.9268 | 8.4676 | 8.0013 | 7.7513 | 6.5615 | 5.7421 | 5.1166 | 1.9074 | 1.536 | 1.1227 | 1.14 | 0.76862 | 0.13494 | -0.58036 | -1.2997 | -1.7702 | -4.2875 | -6.2181 | -7.6926
|  | GRASSINGHAM ROAD PRIMARY | HT |  |  |  |  | 1.4462 | 1.14 | 0.86148 | 0.51352 | 0.13903 | -0.15179 | -0.82832 | -1.5344 | -2.261 | -5.8957 | -8.2804 | -9.6283 | 10.3523 | 10.1523 | 9.9839 | 9.7543 | 9.5003 | 9.4717 | 9.1125 | 8.7309 | 8.3258 | 6.4656 | 5.4911 | 4.9768 | 2.1023 | 1.8237 | 1.5676 | 1.2503 | 0.89413 | 0.62066 | -0.0068921 | -0.65485 | -1.3222 | -4.6202 | -6.7161 | -7.8916
|  | GRASSINGHAM ROAD PRIMARY | HE |  |  |  |  | 1.4839 | 1.2003 | 0.94923 | 0.6329 | 0.29005 | 0.14923 | -0.38546 | -0.94363 | -1.5191 | -4.5191 | -6.66 | -7.764 | 10.339 | 10.1339 | 9.9635 | 9.7523 | 9.5156 | 9.5451 | 9.2421 | 8.9196 | 8.5829 | 7.0033 | 6.1768 | 5.7707 | 2.137 | 1.8819 | 1.6513 | 1.3554 | 1.0268 | 0.90229 | 0.40943 | -0.10281 | -0.6324 | -3.3977 | -5.2722 | -6.2314
|  | GRASSINGHAM ROAD PRIMARY | CF |  |  |  |  | 1.6666 | 1.5288 | 1.3492 | 1.2033 | 1.0064 | 0.76862 | 0.47372 | 0.61658 | 0.35943 | -1.6222 | -3.7293 | -5.7069 | 10.4196 | 10.3023 | 10.1462 | 10.0472 | 9.8972 | 9.7268 | 9.5074 | 9.6625 | 9.4798 | 8.2533 | 7.2564 | 6.4472 | 2.3084 | 2.187 | 2.0247 | 1.8849 | 1.69 | 1.4594 | 1.1747 | 1.3247 | 1.0809 | -0.78342 | -2.6855 | -4.4487
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | GREEN PARK PRIMARY | MINIMUM HEADROOM | SU 70508 70222 | NO | NO | 23.461 | 11.4571 | 11.4245 | 10.9918 | 10.9653 | 10.9398 | 10.952 | 10.9663 | 10.9776 | 10.9908 | 11.0214 | 11.0449 | 11.0622 | 9.1704 | 9.1245 | 8.6245 | 8.6031 | 8.5714 | 8.5908 | 8.6041 | 8.6143 | 8.6235 | 8.6459 | 8.6622 | 8.6765 | 9.1929 | 9.1378 | 8.6724 | 8.6245 | 8.548 | 8.599 | 8.6265 | 8.649 | 8.6745 | 8.7276 | 8.7724 | 8.8173
|  | GREEN PARK PRIMARY | EE |  |  |  |  | 11.4571 | 11.4245 | 10.9918 | 10.9663 | 10.9408 | 10.9531 | 10.9663 | 10.9776 | 10.9908 | 11.0541 | 11.0643 | 11.0622 | 9.1714 | 9.1245 | 8.6245 | 8.6031 | 8.5714 | 8.5908 | 8.6041 | 8.6143 | 8.6235 | 8.6735 | 8.6806 | 8.6765 | 9.1929 | 9.1378 | 8.6724 | 8.6255 | 8.549 | 8.599 | 8.6265 | 8.649 | 8.6745 | 8.7969 | 8.8194 | 8.8173
|  | GREEN PARK PRIMARY | HT |  |  |  |  | 11.4571 | 11.4245 | 10.9918 | 10.9653 | 10.9398 | 10.952 | 10.9663 | 10.9796 | 10.9918 | 11.0541 | 11.0653 | 11.0633 | 9.1704 | 9.1245 | 8.6255 | 8.6051 | 8.5735 | 8.5949 | 8.6071 | 8.6173 | 8.6265 | 8.6776 | 8.6857 | 8.6827 | 9.1929 | 9.1378 | 8.6724 | 8.6245 | 8.548 | 8.599 | 8.6276 | 8.651 | 8.6755 | 8.798 | 8.8204 | 8.8184
|  | GREEN PARK PRIMARY | HE |  |  |  |  | 11.4571 | 11.4245 | 10.9918 | 10.9663 | 10.9418 | 10.9531 | 10.9673 | 10.9806 | 10.9939 | 11.0592 | 11.0724 | 11.0724 | 9.1714 | 9.1245 | 8.6245 | 8.6031 | 8.5714 | 8.5918 | 8.6051 | 8.6153 | 8.6255 | 8.6776 | 8.6878 | 8.6847 | 9.1929 | 9.1378 | 8.6724 | 8.6255 | 8.549 | 8.599 | 8.6276 | 8.652 | 8.6776 | 8.802 | 8.8265 | 8.8276
|  | GREEN PARK PRIMARY | CF |  |  |  |  | 11.4694 | 11.4418 | 11.0184 | 10.999 | 10.9776 | 10.9837 | 10.9878 | 10.9929 | 10.9969 | 11.0214 | 11.0449 | 11.0684 | 9.1806 | 9.15 | 8.6439 | 8.6286 | 8.6133 | 8.6173 | 8.6204 | 8.6235 | 8.6276 | 8.6459 | 8.6622 | 8.6765 | 9.2143 | 9.1704 | 8.7173 | 8.6806 | 8.6439 | 8.6531 | 8.6622 | 8.6714 | 8.6816 | 8.7276 | 8.7724 | 8.8194
WILLESDEN GSP |  | GREENFORD PRIMARY | MINIMUM HEADROOM | TQ 14695 83785 | NO | YES | 31.16 | 20.2267 | 18.7492 | 16.7073 | 14.8737 | 12.8777 | 10.8961 | 8.8339 | 6.9328 | 5.7165 | 1.2145 | -1.5967 | -1.6488 | 24.3471 | 23.4502 | 22.2543 | 21.1328 | 19.9022 | 18.5277 | 16.9461 | 15.4124 | 14.338 | 8.938 | -0.58858 | -20.9641 | 18.2788 | 16.9696 | 15.1808 | 13.5247 | 11.7135 | 9.9073 | 8.0084 | 6.1982 | 5.0655 | 0.89816 | -1.562 | -1.51
|  | GREENFORD PRIMARY | EE |  |  |  |  | 20.2267 | 18.7492 | 16.7073 | 14.8737 | 12.8777 | 10.8961 | 8.8339 | 6.9328 | 5.7165 | 1.2145 | -1.5967 | -0.75287 | 24.3471 | 23.4502 | 22.2543 | 21.1328 | 19.9022 | 18.5277 | 16.9461 | 15.4124 | 14.338 | 8.938 | 2.7747 | -6.2569 | 18.2788 | 16.9696 | 15.1808 | 13.5247 | 11.7135 | 9.9073 | 8.0084 | 6.1982 | 5.0655 | 0.89816 | -1.562 | -0.82429
|  | GREENFORD PRIMARY | HT |  |  |  |  | 20.7247 | 19.4063 | 17.99 | 16.5206 | 14.8971 | 13.4043 | 11.9573 | 10.5839 | 9.1584 | 2.4726 | -1.4049 | -1.6488 | 24.8339 | 24.1604 | 23.4502 | 22.7084 | 21.8849 | 21.1237 | 20.3584 | 19.6226 | 18.7737 | 14.5706 | 12.4359 | 12.1043 | 18.7635 | 17.6165 | 16.438 | 15.1482 | 13.7135 | 12.3777 | 11.0451 | 9.7543 | 8.4104 | 2.1777 | -1.3161 | -1.51
|  | GREENFORD PRIMARY | HE |  |  |  |  | 20.6818 | 19.3706 | 17.941 | 16.4563 | 14.8165 | 13.3584 | 11.9145 | 10.54 | 9.1094 | 3.4308 | 0.4706 | 0.013461 | 24.592 | 23.7818 | 22.9165 | 21.9869 | 20.9512 | 19.9604 | 18.9247 | 17.8818 | 16.7512 | 10.0635 | 3.5482 | -5.8835 | 18.7124 | 17.5604 | 16.3706 | 15.0614 | 13.6104 | 12.2961 | 10.9553 | 9.6553 | 8.3002 | 2.9298 | 0.26652 | -0.11511
|  | GREENFORD PRIMARY | CF |  |  |  |  | 21.392 | 20.4604 | 19.1645 | 18.5716 | 17.5022 | 16.7339 | 15.9645 | 15.2206 | 14.5247 | 9.8196 | 4.9818 | 0.67162 | 24.9257 | 24.2726 | 23.4216 | 22.8818 | 22.0288 | 21.2237 | 20.3594 | 19.4726 | 18.5675 | 11.2798 | -0.58858 | -20.9641 | 19.3798 | 18.5828 | 17.4849 | 16.9706 | 16.0318 | 15.3573 | 14.6522 | 13.9543 | 13.3063 | 8.8522 | 4.3696 | 0.48081
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET PRIMARY | MINIMUM HEADROOM | SU 64445 00178 | NO | YES | 1.431 | 16.152 | 15.9102 | 15.2388 | 14.4439 | 13.2694 | 12.5806 | 11.8796 | 11.1776 | 10.5786 | 9.5 | 8.6857 | 8.6969 | 17.3653 | 17.1214 | 16.6592 | 16.1112 | 15.3847 | 14.849 | 14.2786 | 13.6847 | 13.1449 | 10.8163 | 5.9439 | -4.402 | 14.9031 | 14.6949 | 14.1449 | 13.4806 | 12.4949 | 11.9163 | 11.3163 | 10.6908 | 10.1684 | 9.1622 | 8.598 | 8.5867
|  | GREETHAM STREET PRIMARY | EE |  |  |  |  | 16.152 | 15.9102 | 15.2388 | 14.4439 | 13.2694 | 12.5806 | 11.8796 | 11.1776 | 10.5786 | 9.5 | 8.9582 | 9.0724 | 17.3653 | 17.1214 | 16.6592 | 16.1112 | 15.3847 | 14.849 | 14.2786 | 13.6847 | 13.1449 | 10.8163 | 7.8867 | 2.9092 | 14.9031 | 14.6949 | 14.1449 | 13.4806 | 12.4949 | 11.9163 | 11.3163 | 10.6908 | 10.1684 | 9.1622 | 8.7327 | 8.749
|  | GREETHAM STREET PRIMARY | HT |  |  |  |  | 16.2755 | 16.1633 | 15.5592 | 14.6153 | 13.5061 | 12.9878 | 12.4163 | 11.849 | 11.4929 | 9.851 | 8.6857 | 8.6969 | 17.6224 | 17.5041 | 17.1735 | 16.6888 | 16.1235 | 15.8357 | 15.4969 | 15.151 | 14.8918 | 13.7163 | 12.9031 | 12.7816 | 15.0796 | 14.9388 | 14.4551 | 13.6918 | 12.7755 | 12.3561 | 11.8929 | 11.4327 | 11.1398 | 9.6531 | 8.598 | 8.5867
|  | GREETHAM STREET PRIMARY | HE |  |  |  |  | 16.2735 | 16.1786 | 15.6265 | 14.9673 | 14.0235 | 13.6429 | 13.2163 | 12.799 | 12.3765 | 11.2061 | 10.8612 | 10.8643 | 17.5163 | 17.3459 | 16.9602 | 16.5194 | 15.9378 | 15.6051 | 15.2173 | 14.8071 | 14.3745 | 12.0398 | 9.2112 | 4.301 | 15.0776 | 14.951 | 14.4867 | 13.9398 | 13.151 | 12.8378 | 12.4816 | 12.1306 | 11.7796 | 10.8439 | 10.5745 | 10.5959
|  | GREETHAM STREET PRIMARY | CF |  |  |  |  | 16.3755 | 16.3102 | 15.9388 | 15.4 | 14.7867 | 14.5316 | 14.2449 | 13.9633 | 13.6643 | 12.2245 | 11.2378 | 10.3673 | 17.5816 | 17.4184 | 17.0653 | 16.649 | 16.1653 | 15.801 | 15.3908 | 14.9622 | 14.4939 | 11.3786 | 5.9439 | -4.402 | 15.2122 | 15.1255 | 14.7561 | 14.3163 | 13.8112 | 13.6092 | 13.3765 | 13.149 | 12.9071 | 11.6806 | 10.85 | 10.1531
COWLEY GSP | DRAYTON BSP | GROVE PRIMARY | MINIMUM HEADROOM | SU 39515 89611 | NO | YES | 8.891 | -8.94 | -9.8216 | -10.7033 | -11.4737 | -12.6359 | -13.8839 | -15.1012 | -16.241 | -17.0931 | -21.837 | -25.7696 | -28.89 | -5.8536 | -6.4679 | -7.022 | -7.4006 | -8.0383 | -8.7281 | -9.4322 | -10.1077 | -10.6077 | -13.4506 | -16.5496 | -23.2394 | -8.7295 | -9.5111 | -10.306 | -10.8601 | -11.8499 | -12.9254 | -14.004 | -15.0285 | -15.7325 | -19.7172 | -23.0264 | -25.5458
|  | GROVE PRIMARY | EE |  |  |  |  | -8.94 | -9.8216 | -10.7033 | -11.4737 | -12.6359 | -13.8839 | -15.1012 | -16.241 | -17.0931 | -21.6737 | -25.3543 | -28.6155 | -5.8536 | -6.4679 | -7.022 | -7.4006 | -8.0383 | -8.7281 | -9.4322 | -10.1077 | -10.6077 | -13.4506 | -16.3536 | -20.2751 | -8.7295 | -9.5111 | -10.306 | -10.8601 | -11.8499 | -12.9254 | -14.004 | -15.0285 | -15.7325 | -19.5836 | -22.6499 | -25.3101
|  | GROVE PRIMARY | HT |  |  |  |  | -8.7706 | -9.6043 | -10.4196 | -11.387 | -12.54 | -13.7992 | -14.6553 | -15.7461 | -16.7563 | -21.837 | -25.7696 | -28.89 | -5.6485 | -6.1812 | -6.6353 | -7.1251 | -7.6975 | -8.321 | -8.6567 | -9.2026 | -9.7465 | -12.2292 | -14.0271 | -15.4312 | -8.5325 | -9.257 | -9.9509 | -10.7632 | -11.7336 | -12.804 | -13.4928 | -14.4264 | -15.3203 | -19.7172 | -23.0264 | -25.5458
|  | GROVE PRIMARY | HE |  |  |  |  | -8.7472 | -9.5614 | -10.3196 | -11.2655 | -12.4278 | -13.5798 | -14.3319 | -15.3104 | -16.1737 | -20.8237 | -24.4829 | -27.2176 | -5.6996 | -6.2598 | -6.7139 | -7.2332 | -7.871 | -8.5077 | -8.8628 | -9.4332 | -9.9669 | -13.02 | -15.9526 | -19.6577 | -8.5101 | -9.2183 | -9.8621 | -10.654 | -11.6336 | -12.607 | -13.1999 | -14.0366 | -14.7846 | -18.806 | -21.8662 | -24.055
|  | GROVE PRIMARY | CF |  |  |  |  | -8.5308 | -9.2196 | -9.8584 | -10.6186 | -11.5176 | -12.3216 | -13.0941 | -13.4951 | -14.0645 | -17.6574 | -21.487 | -25.3992 | -5.6036 | -6.1169 | -6.5383 | -6.9904 | -7.519 | -8.0455 | -8.5781 | -8.8404 | -9.2883 | -12.3057 | -16.5496 | -23.2394 | -8.3142 | -8.9081 | -9.4438 | -10.0632 | -10.807 | -11.4683 | -12.1142 | -12.403 | -12.8866 | -16.0101 | -19.2315 | -22.5009
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL PRIMARY | MINIMUM HEADROOM | ST 98638 11417 | YES | NO | 0.045 | 4.2699 | 4.2301 | 4.1995 | 4.1546 | 4.1321 | 4.074 | 4.0148 | 3.9464 | 3.9301 | 3.8128 | 3.7638 | 3.726 | 3.8857 | 3.8571 | 3.8357 | 3.801 | 3.7898 | 3.7469 | 3.7092 | 3.6592 | 3.6398 | 3.5398 | 3.3796 | 3.0459 | 4.1816 | 4.1449 | 4.1133 | 4.0653 | 4.0439 | 3.9857 | 3.9276 | 3.8612 | 3.8449 | 3.7571 | 3.7112 | 3.6786
|  | GUSSAGE ST MICHAEL PRIMARY | EE |  |  |  |  | 4.2699 | 4.2301 | 4.1995 | 4.1546 | 4.1321 | 4.074 | 4.0148 | 3.9464 | 3.9301 | 3.8128 | 3.7638 | 3.7383 | 3.8857 | 3.8571 | 3.8357 | 3.801 | 3.7898 | 3.7469 | 3.7092 | 3.6592 | 3.6398 | 3.5398 | 3.4316 | 3.2684 | 4.1816 | 4.1449 | 4.1133 | 4.0653 | 4.0439 | 3.9857 | 3.9276 | 3.8612 | 3.8449 | 3.7571 | 3.7112 | 3.6898
|  | GUSSAGE ST MICHAEL PRIMARY | HT |  |  |  |  | 4.2903 | 4.2648 | 4.2464 | 4.2148 | 4.1923 | 4.1505 | 4.1026 | 4.0781 | 4.0301 | 3.8423 | 3.777 | 3.726 | 3.9031 | 3.8888 | 3.8765 | 3.8551 | 3.8408 | 3.8133 | 3.7796 | 3.7673 | 3.7357 | 3.6184 | 3.5827 | 3.5561 | 4.1969 | 4.1776 | 4.1612 | 4.1316 | 4.1102 | 4.0735 | 4.0286 | 4.0031 | 3.9582 | 3.7837 | 3.7204 | 3.6786
|  | GUSSAGE ST MICHAEL PRIMARY | HE |  |  |  |  | 4.2923 | 4.2668 | 4.2485 | 4.2189 | 4.1974 | 4.1556 | 4.1097 | 4.0883 | 4.0372 | 3.8342 | 3.7903 | 3.7658 | 3.902 | 3.8857 | 3.8745 | 3.852 | 3.8367 | 3.8051 | 3.7735 | 3.7561 | 3.7214 | 3.5571 | 3.45 | 3.2878 | 4.199 | 4.1796 | 4.1622 | 4.1347 | 4.1163 | 4.0765 | 4.0357 | 4.0102 | 3.9673 | 3.7776 | 3.7367 | 3.7163
|  | GUSSAGE ST MICHAEL PRIMARY | CF |  |  |  |  | 4.3036 | 4.2821 | 4.2577 | 4.2444 | 4.2209 | 4.1913 | 4.173 | 4.1372 | 4.1046 | 3.9587 | 3.8587 | 3.7893 | 3.9112 | 3.8959 | 3.8786 | 3.8694 | 3.849 | 3.8255 | 3.8071 | 3.7755 | 3.7469 | 3.5898 | 3.3796 | 3.0459 | 4.2102 | 4.1908 | 4.1724 | 4.1592 | 4.1388 | 4.1143 | 4.0959 | 4.0633 | 4.0327 | 3.8939 | 3.7969 | 3.7357
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE PRIMARY | MINIMUM HEADROOM | SU 47370 08794 | NO | NO | 0.97 | 13.2193 | 12.9499 | 12.5958 | 12.204 | 12.2101 | 11.6397 | 10.9825 | 10.3407 | 9.7989 | 7.2621 | 5.3101 | 4.0795 | 14.1325 | 13.8999 | 13.607 | 13.2764 | 13.3448 | 12.954 | 12.506 | 12.0438 | 11.7499 | 10.158 | 8.0264 | 2.5152 | 12.6611 | 12.4162 | 12.0948 | 11.7152 | 11.6968 | 11.1631 | 10.5478 | 9.9468 | 9.4438 | 7.0876 | 5.3356 | 4.2999
|  | HAMBLE PRIMARY | EE |  |  |  |  | 13.2193 | 12.9499 | 12.5958 | 12.204 | 12.2101 | 11.6397 | 10.9825 | 10.3407 | 9.7989 | 7.4142 | 5.7529 | 4.3529 | 14.1325 | 13.8999 | 13.607 | 13.2764 | 13.3448 | 12.954 | 12.506 | 12.0438 | 11.7499 | 10.158 | 8.5101 | 5.7315 | 12.6611 | 12.4162 | 12.0948 | 11.7152 | 11.6968 | 11.1631 | 10.5478 | 9.9468 | 9.4438 | 7.2693 | 5.7458 | 4.5325
|  | HAMBLE PRIMARY | HT |  |  |  |  | 13.3468 | 13.1601 | 12.9499 | 12.7489 | 12.458 | 11.9131 | 11.307 | 11.054 | 10.4917 | 7.4152 | 5.3101 | 4.0795 | 14.3723 | 14.2305 | 14.0458 | 13.8958 | 13.6733 | 13.3376 | 12.955 | 12.9968 | 12.6499 | 10.9509 | 9.9917 | 9.4499 | 12.8407 | 12.6468 | 12.4172 | 12.207 | 11.9376 | 11.4223 | 10.856 | 10.6274 | 10.0815 | 7.2019 | 5.3356 | 4.2999
|  | HAMBLE PRIMARY | HE |  |  |  |  | 13.358 | 13.1784 | 12.9795 | 12.7876 | 12.5315 | 12.0703 | 11.4754 | 11.0172 | 10.3887 | 7.2621 | 5.4938 | 4.6376 | 14.3376 | 14.1693 | 13.9662 | 13.7897 | 13.5478 | 13.2101 | 12.8182 | 12.8438 | 12.4754 | 10.505 | 8.5989 | 6.0519 | 12.8519 | 12.6672 | 12.4489 | 12.2529 | 12.0019 | 11.5733 | 11.0172 | 10.5968 | 10.0029 | 7.0876 | 5.4774 | 4.6968
|  | HAMBLE PRIMARY | CF |  |  |  |  | 13.5478 | 13.4427 | 13.3529 | 13.2213 | 13.0978 | 12.8846 | 12.6254 | 12.3387 | 12.0376 | 10.1407 | 7.8887 | 6.1009 | 14.4295 | 14.2774 | 14.1509 | 13.9805 | 13.8284 | 13.5938 | 13.3111 | 13.005 | 12.6774 | 11.1182 | 8.0264 | 2.5152 | 13.0325 | 12.905 | 12.806 | 12.6672 | 12.5611 | 12.3754 | 12.1233 | 11.8519 | 11.5621 | 9.7458 | 7.657 | 6.0244
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | HAMWORTHY PRIMARY | MINIMUM HEADROOM | SZ 00104 90800 | NO | NO | 4.051 | 22.4738 | 21.385 | 20.3003 | 18.9483 | 17.5115 | 15.8809 | 13.887 | 11.9676 | 10.3544 | 1.5064 | -2.6354 | -3.562 | 24.9901 | 24.2391 | 23.686 | 22.6921 | 21.6462 | 20.4962 | 19.0829 | 17.7258 | 16.6136 | 10.3197 | 6.3666 | -5.0028 | 22.7187 | 21.6983 | 20.9829 | 19.8136 | 18.4534 | 16.9074 | 15.0207 | 13.1901 | 11.6911 | 3.3136 | -0.58032 | -1.3466
|  | HAMWORTHY PRIMARY | EE |  |  |  |  | 22.4738 | 21.385 | 20.3003 | 18.9483 | 17.5115 | 15.8809 | 13.887 | 11.9676 | 10.3544 | 3.3401 | -0.6242 | -3.562 | 24.9901 | 24.2391 | 23.686 | 22.6921 | 21.6462 | 20.4962 | 19.0829 | 17.7258 | 16.6136 | 11.7483 | 7.5411 | 1.4268 | 22.7187 | 21.6983 | 20.9829 | 19.8136 | 18.4534 | 16.9074 | 15.0207 | 13.1901 | 11.6911 | 5.4115 | 2.2513 | -0.23032
|  | HAMWORTHY PRIMARY | HT |  |  |  |  | 23.0962 | 22.3095 | 21.286 | 20.1768 | 19.2615 | 17.7248 | 15.9166 | 14.185 | 12.4258 | 3.9636 | -0.80175 | -3.2385 | 25.5993 | 25.1146 | 24.4972 | 23.8411 | 23.3697 | 22.5534 | 21.5666 | 20.6034 | 19.6074 | 15.0309 | 12.7289 | 11.7085 | 23.4319 | 22.7044 | 21.7666 | 20.7462 | 19.986 | 18.6207 | 17.0054 | 15.4278 | 13.8156 | 6.2309 | 2.1625 | 0.14213
|  | HAMWORTHY PRIMARY | HE |  |  |  |  | 22.9534 | 22.1034 | 21.0768 | 19.8238 | 18.5523 | 17.0289 | 15.0993 | 13.0656 | 10.9452 | 1.5064 | -2.6354 | -3.5344 | 25.3615 | 24.7554 | 24.0574 | 23.2646 | 22.4605 | 21.3778 | 20.0064 | 18.5462 | 17.0258 | 10.3197 | 6.3666 | 0.72274 | 23.2758 | 22.488 | 21.5666 | 20.5176 | 19.4656 | 18.0207 | 16.1962 | 14.2656 | 12.2554 | 3.3136 | -0.58032 | -1.3466
|  | HAMWORTHY PRIMARY | CF |  |  |  |  | 23.5758 | 23.0115 | 22.5421 | 22.0176 | 21.4452 | 20.8983 | 19.9615 | 18.9289 | 17.8258 | 10.3595 | 4.9544 | 1.8809 | 25.7085 | 25.2421 | 24.8197 | 24.3319 | 23.8085 | 23.4707 | 22.7585 | 21.9727 | 21.1207 | 14.5136 | 6.7789 | -5.0028 | 23.8585 | 23.3217 | 22.8615 | 22.3309 | 21.785 | 21.5952 | 20.7809 | 19.7952 | 18.7391 | 11.7146 | 6.5901 | 3.7319
IVER 132KV GSP | DENHAM BSP | HAREFIELD PRIMARY | MINIMUM HEADROOM | TQ 04001 91227 | NO | YES | 0.651 | 6.6597 | 6.5128 | 6.3097 | 6.0821 | 5.8974 | 5.5495 | 5.1526 | 4.7556 | 4.5199 | 3.6036 | 2.5158 | 1.9128 | 7.1607 | 7.0444 | 6.8872 | 6.7056 | 6.5607 | 6.3148 | 6.0291 | 5.7403 | 5.5791 | 5.0617 | 4.2158 | 1.9821 | 6.8867 | 6.7439 | 6.549 | 6.3327 | 6.1592 | 5.8306 | 5.4541 | 5.0765 | 4.8571 | 4.1429 | 3.2184 | 2.7112
|  | HAREFIELD PRIMARY | EE |  |  |  |  | 6.6597 | 6.5128 | 6.3097 | 6.0821 | 5.8974 | 5.5495 | 5.1526 | 4.7556 | 4.5199 | 3.7117 | 2.7352 | 2.0158 | 7.1607 | 7.0444 | 6.8872 | 6.7056 | 6.5607 | 6.3148 | 6.0291 | 5.7403 | 5.5791 | 5.1056 | 4.2158 | 2.9352 | 6.8867 | 6.7439 | 6.549 | 6.3327 | 6.1592 | 5.8306 | 5.4541 | 5.0765 | 4.8571 | 4.2122 | 3.4153 | 2.7949
|  | HAREFIELD PRIMARY | HT |  |  |  |  | 6.7658 | 6.6434 | 6.4985 | 6.3689 | 6.1934 | 5.8964 | 5.6179 | 5.2883 | 4.9474 | 3.6036 | 2.5158 | 1.9128 | 7.2811 | 7.2015 | 7.1026 | 7.0199 | 6.8934 | 6.7189 | 6.5648 | 6.3607 | 6.1464 | 5.5607 | 5.0791 | 4.825 | 7 | 6.8867 | 6.748 | 6.6255 | 6.4561 | 6.1796 | 5.9327 | 5.6235 | 5.3 | 4.1429 | 3.2184 | 2.7112
|  | HAREFIELD PRIMARY | HE |  |  |  |  | 6.777 | 6.6668 | 6.5362 | 6.4209 | 6.2607 | 6.0158 | 5.7903 | 5.5138 | 5.2291 | 3.8179 | 3.2423 | 2.7985 | 7.2638 | 7.1801 | 7.077 | 6.9852 | 6.8556 | 6.6852 | 6.5291 | 6.3281 | 6.1168 | 5.0617 | 4.476 | 3.2985 | 7.0102 | 6.9061 | 6.7806 | 6.6724 | 6.5163 | 6.2847 | 6.0847 | 5.8204 | 5.549 | 4.2622 | 3.8735 | 3.4959
|  | HAREFIELD PRIMARY | CF |  |  |  |  | 6.874 | 6.8097 | 6.726 | 6.6291 | 6.5219 | 6.4423 | 6.3026 | 6.1526 | 6.0505 | 5.026 | 4.5434 | 3.724 | 7.3148 | 7.2485 | 7.1719 | 7.076 | 6.9719 | 6.8842 | 6.7403 | 6.5903 | 6.474 | 5.4117 | 4.324 | 1.9821 | 7.099 | 7.0357 | 6.9551 | 6.8612 | 6.7582 | 6.6847 | 6.55 | 6.4071 | 6.3133 | 5.3388 | 4.9959 | 4.2612
NURSLING GSP | WINCHESTER BSP | HARESTOCK PRIMARY | MINIMUM HEADROOM | SU 45908 31300 | NO | NO | 6.15 | 9.2678 | 8.6025 | 8.077 | 7.1249 | 5.7872 | 4.2657 | 2.6494 | -0.17304 | -2.2669 | -9.969 | -16.0679 | -21.0322 | 12.4463 | 11.9208 | 11.4647 | 10.7535 | 9.5259 | 8.3923 | 7.1188 | 4.3841 | 2.3392 | -4.4016 | -11.0179 | -19.1822 | 9.4045 | 8.78 | 8.2535 | 7.3555 | 5.9351 | 4.481 | 2.878 | -0.17917 | -2.4486 | -10.1312 | -16.4547 | -21.9792
|  | HARESTOCK PRIMARY | EE |  |  |  |  | 9.2678 | 8.6025 | 8.077 | 7.1372 | 5.8872 | 4.2657 | 2.6953 | 0.7943 | -0.39243 | -6.6761 | -14.0598 | -17.9251 | 12.4463 | 11.9208 | 11.6198 | 10.9739 | 9.9984 | 8.8433 | 7.8065 | 6.3463 | 5.4514 | 0.43512 | -7.6853 | -13.6914 | 9.4045 | 8.78 | 8.3372 | 7.4892 | 6.2902 | 4.7494 | 3.3147 | 1.4719 | 0.32287 | -5.7261 | -13.6077 | -17.3822
|  | HARESTOCK PRIMARY | HT |  |  |  |  | 9.6831 | 9.129 | 8.231 | 7.3678 | 6.1974 | 4.5953 | 2.827 | 1.2963 | -0.38427 | -8.0853 | -15.5149 | -20.369 | 12.8984 | 12.5076 | 11.8729 | 11.3484 | 10.3953 | 9.3157 | 8.0821 | 7.1729 | 5.8749 | 0.50961 | -5.8424 | -10.1363 | 9.8208 | 9.2902 | 8.4423 | 7.6729 | 6.4637 | 4.9208 | 3.2086 | 1.8076 | 0.10961 | -7.42 | -15.2557 | -20.3628
|  | HARESTOCK PRIMARY | HE |  |  |  |  | 9.6821 | 9.0984 | 8.0861 | 7.1249 | 5.7872 | 4.2943 | 2.6494 | -0.17304 | -2.2669 | -9.969 | -16.0679 | -21.0322 | 12.7963 | 12.3076 | 11.4647 | 10.7535 | 9.5259 | 8.3923 | 7.1188 | 4.3841 | 2.3392 | -4.4016 | -11.0179 | -19.1822 | 9.8137 | 9.2433 | 8.2535 | 7.3555 | 5.9351 | 4.481 | 2.878 | -0.17917 | -2.4486 | -10.1312 | -16.4547 | -21.9792
|  | HARESTOCK PRIMARY | CF |  |  |  |  | 10.0933 | 9.7719 | 9.2861 | 8.629 | 7.878 | 7.429 | 6.6361 | 5.7912 | 5.1127 | 0.20655 | -5.2935 | -10.3424 | 13.0157 | 12.7157 | 12.3474 | 11.8147 | 11.1882 | 10.7994 | 10.0984 | 9.3484 | 8.6157 | 3.4504 | -3.7394 | -13.8557 | 10.1974 | 9.8974 | 9.481 | 8.877 | 8.18 | 7.7729 | 7.0361 | 6.2463 | 5.5606 | 0.69226 | -4.7741 | -9.7771
EALING GSP | EALING BSP | HARVARD LANE PRIMARY | MINIMUM HEADROOM | TQ 20021 78030 | NO | NO | 3.383 | 0.95306 | 0.19694 | 50.4204 | 49.4418 | 48.2561 | 47.402 | 45.9918 | 44.5888 | 43.6153 | 38.4194 | 33.4163 | 30.2367 | 4.2255 | 3.601 | 53.9673 | 53.1847 | 52.2153 | 51.5684 | 50.4724 | 49.3694 | 48.5378 | 43.8337 | 37.6745 | 22.1878 | -0.47245 | -1.1908 | 49.0704 | 48.1429 | 46.998 | 46.1582 | 44.8163 | 43.4939 | 42.5704 | 37.998 | 33.7561 | 31.0041
|  | HARVARD LANE PRIMARY | EE |  |  |  |  | 0.95306 | 0.19694 | 50.4204 | 49.4418 | 48.2561 | 47.402 | 45.9918 | 44.5888 | 43.6153 | 38.4194 | 34.2214 | 30.4735 | 4.2255 | 3.601 | 53.9673 | 53.1847 | 52.2153 | 51.5684 | 50.4724 | 49.3694 | 48.5378 | 43.8337 | 38.5153 | 30.0296 | -0.47245 | -1.1908 | 49.0704 | 48.1429 | 46.998 | 46.1582 | 44.8163 | 43.4939 | 42.5704 | 37.998 | 34.4908 | 31.1867
|  | HARVARD LANE PRIMARY | HT |  |  |  |  | 1.3531 | 0.75918 | 51.0622 | 50.1561 | 49.3051 | 48.2541 | 47.1347 | 46.098 | 45.4265 | 39.001 | 33.4163 | 30.2367 | 4.698 | 4.3235 | 54.8776 | 54.2571 | 53.6888 | 53.048 | 52.3306 | 51.6265 | 51.2878 | 47.7133 | 44.9388 | 43.5959 | -0.080612 | -0.62755 | 49.7255 | 48.852 | 48.0408 | 47.0653 | 46.0153 | 45.0102 | 44.4388 | 38.6122 | 33.7561 | 31.0041
|  | HARVARD LANE PRIMARY | HE |  |  |  |  | 1.3745 | 0.84796 | 51.2622 | 50.5704 | 49.7082 | 48.6857 | 47.5653 | 46.7745 | 45.8561 | 40.8469 | 37.0143 | 35.4388 | 4.5776 | 4.1439 | 54.6684 | 54.1224 | 53.449 | 52.7102 | 51.8531 | 51.2276 | 50.4306 | 45.6173 | 40.3143 | 32.6684 | -0.069388 | -0.56327 | 49.8867 | 49.2378 | 48.4327 | 47.4939 | 46.4541 | 45.7918 | 44.9255 | 40.398 | 37.1418 | 35.7949
|  | HARVARD LANE PRIMARY | CF |  |  |  |  | 1.7429 | 1.4541 | 52.1388 | 51.7847 | 51.3918 | 51.0235 | 50.4786 | 49.8092 | 49.1255 | 45.9571 | 42.6684 | 39.2898 | 4.7449 | 4.4153 | 55.0418 | 54.6316 | 54.1459 | 53.6051 | 52.9051 | 52.1173 | 51.2735 | 46.1582 | 37.6745 | 22.1878 | 0.28163 | 0.0081633 | 50.7133 | 50.3796 | 50.0133 | 49.65 | 49.1214 | 48.4806 | 47.8306 | 44.8133 | 41.8316 | 38.9398
COWLEY GSP |  | HARWELL PRIMARY | MINIMUM HEADROOM | SU 47395 86969 | NO | NO | 6.678 | 26.3339 | 26.3237 | 26.3165 | 26.3043 | 26.2982 | 26.2788 | 26.2624 | 26.242 | 26.2267 | 26.1482 | 26.1033 | 26.0747 | 27.1665 | 27.1553 | 27.1482 | 27.1339 | 27.1247 | 27.1053 | 27.0808 | 27.0573 | 27.039 | 26.9165 | 26.8043 | 26.5451 | 26.4288 | 26.4114 | 26.3992 | 26.3788 | 26.3676 | 26.3308 | 26.292 | 26.2522 | 26.2186 | 26.0186 | 25.888 | 25.8084
|  | HARWELL PRIMARY | EE |  |  |  |  | 26.3339 | 26.3237 | 26.3165 | 26.3043 | 26.2982 | 26.2788 | 26.2624 | 26.242 | 26.2308 | 26.1533 | 26.1084 | 26.0767 | 27.1665 | 27.1553 | 27.1482 | 27.1339 | 27.1247 | 27.1053 | 27.0808 | 27.0573 | 27.039 | 26.9165 | 26.8043 | 26.6553 | 26.4288 | 26.4114 | 26.3992 | 26.3788 | 26.3676 | 26.3308 | 26.292 | 26.2522 | 26.2237 | 26.038 | 25.9053 | 25.8145
|  | HARWELL PRIMARY | HT |  |  |  |  | 26.34 | 26.3308 | 26.3257 | 26.3155 | 26.3084 | 26.2931 | 26.2839 | 26.2665 | 26.2267 | 26.1482 | 26.1033 | 26.0747 | 27.1767 | 27.1686 | 27.1645 | 27.1533 | 27.1471 | 27.1308 | 27.1196 | 27.1033 | 27.0584 | 26.9686 | 26.9165 | 26.8859 | 26.4349 | 26.4186 | 26.4084 | 26.39 | 26.3788 | 26.3431 | 26.3155 | 26.2788 | 26.2186 | 26.0186 | 25.888 | 25.8084
|  | HARWELL PRIMARY | HE |  |  |  |  | 26.341 | 26.3318 | 26.3257 | 26.3186 | 26.3124 | 26.3002 | 26.292 | 26.2778 | 26.2665 | 26.1808 | 26.1451 | 26.1237 | 27.1737 | 27.1645 | 27.1584 | 27.1492 | 27.139 | 27.1247 | 27.1124 | 27.0941 | 27.0757 | 26.9431 | 26.8359 | 26.6961 | 26.4369 | 26.4216 | 26.4124 | 26.3971 | 26.3849 | 26.3573 | 26.3369 | 26.3073 | 26.2788 | 26.0931 | 25.9686 | 25.9053
|  | HARWELL PRIMARY | CF |  |  |  |  | 26.3451 | 26.34 | 26.3349 | 26.3318 | 26.3247 | 26.3206 | 26.3124 | 26.3043 | 26.3012 | 26.2308 | 26.192 | 26.1594 | 27.1767 | 27.1727 | 27.1624 | 27.1594 | 27.1482 | 27.141 | 27.1267 | 27.1135 | 27.1053 | 26.9716 | 26.8124 | 26.5451 | 26.4451 | 26.439 | 26.4298 | 26.4257 | 26.4155 | 26.4094 | 26.3971 | 26.3829 | 26.3818 | 26.2543 | 26.141 | 26.0359
FLEET-BRAMLEY GSP | FERNHURST BSP | HASLEMERE PRIMARY | MINIMUM HEADROOM | SU 89300 31710 | NO | NO | 3.609 | 8.0765 | 7.5041 | 7.2571 | 6.6929 | 6.0724 | 5.1112 | 4.0806 | 3.052 | 2.2969 | -1.8786 | -5.2102 | -7.0765 | 12.1286 | 11.6959 | 11.5194 | 11.0796 | 10.5929 | 9.9296 | 9.1786 | 8.4112 | 7.8724 | 4.8347 | 1.1235 | -7.8643 | 8.6867 | 8.1235 | 7.9633 | 7.4214 | 6.8204 | 5.948 | 4.9857 | 4.0092 | 3.3378 | -0.31531 | -3.2541 | -4.852
|  | HASLEMERE PRIMARY | EE |  |  |  |  | 8.0765 | 7.5041 | 7.2571 | 6.6929 | 6.0724 | 5.1112 | 4.0806 | 3.052 | 2.2969 | -1.7398 | -4.55 | -6.648 | 12.1286 | 11.6959 | 11.5194 | 11.0796 | 10.5929 | 9.9296 | 9.1786 | 8.4112 | 7.8724 | 4.8347 | 1.5806 | -3.2245 | 8.6867 | 8.1235 | 7.9633 | 7.4214 | 6.8204 | 5.948 | 4.9857 | 4.0092 | 3.3378 | -0.22857 | -2.6663 | -4.4888
|  | HASLEMERE PRIMARY | HT |  |  |  |  | 8.3469 | 7.9378 | 7.4684 | 6.9592 | 6.7143 | 5.8133 | 4.9378 | 4.0133 | 3.0571 | -1.8786 | -5.2102 | -7.0765 | 12.4551 | 12.2143 | 11.9204 | 11.599 | 11.4969 | 11.0194 | 10.5286 | 10 | 9.45 | 6.7898 | 5.2041 | 4.3724 | 9.0102 | 8.6408 | 8.198 | 7.7163 | 7.5214 | 6.7092 | 5.902 | 5.0531 | 4.1735 | -0.31531 | -3.2541 | -4.852
|  | HASLEMERE PRIMARY | HE |  |  |  |  | 8.3969 | 7.9969 | 7.5541 | 7.0806 | 6.8878 | 6.1694 | 5.4224 | 4.6571 | 3.8633 | -0.37245 | -3.099 | -4.3663 | 12.3857 | 12.0918 | 11.7551 | 11.3878 | 11.2429 | 10.7582 | 10.2286 | 9.6643 | 9.0612 | 5.6143 | 2.3439 | -2.101 | 9.0469 | 8.6888 | 8.2735 | 7.8245 | 7.6786 | 7.0255 | 6.3378 | 5.6286 | 4.8959 | 1.0439 | -1.3347 | -2.4133
|  | HASLEMERE PRIMARY | CF |  |  |  |  | 8.701 | 8.4327 | 8.1888 | 7.8949 | 7.5755 | 7.2459 | 7.2296 | 6.8582 | 6.4592 | 3.6847 | 0.76122 | -1.951 | 12.5276 | 12.2714 | 12.0327 | 11.7408 | 11.4 | 11.0092 | 10.8571 | 10.4061 | 9.9255 | 6.4633 | 1.1235 | -7.8643 | 9.3092 | 9.0418 | 8.8153 | 8.5235 | 8.2061 | 7.8724 | 7.9388 | 7.5745 | 7.1867 | 4.6051 | 2.0378 | -0.34796
FLEET-BRAMLEY GSP | FERNHURST BSP | HASLINGBOURNE PRIMARY | MINIMUM HEADROOM | SU 98188 20276 | NO | NO | 0.965 | 6.2704 | 6.0857 | 5.8408 | 5.6306 | 5.3561 | 4.9847 | 4.552 | 4.5714 | 4.3184 | 2.9949 | 2.0714 | 1.4633 | 8.152 | 8.0143 | 7.8276 | 7.6673 | 7.4449 | 7.1755 | 6.851 | 6.9153 | 6.7306 | 5.7092 | 4.4653 | 1.4612 | 6.4714 | 6.2939 | 6.051 | 5.8459 | 5.5704 | 5.2082 | 4.7796 | 4.9102 | 4.6929 | 3.5408 | 2.752 | 2.2367
|  | HASLINGBOURNE PRIMARY | EE |  |  |  |  | 6.2704 | 6.0857 | 5.8408 | 5.6306 | 5.3561 | 4.9847 | 4.552 | 4.5714 | 4.3184 | 2.9949 | 2.202 | 1.6684 | 8.152 | 8.0143 | 7.8276 | 7.6673 | 7.4449 | 7.1755 | 6.851 | 6.9153 | 6.7306 | 5.7092 | 4.7061 | 3.1704 | 6.4714 | 6.2939 | 6.051 | 5.8459 | 5.5704 | 5.2082 | 4.7796 | 4.9102 | 4.6929 | 3.5408 | 2.8673 | 2.4112
|  | HASLINGBOURNE PRIMARY | HT |  |  |  |  | 6.4296 | 6.2684 | 6.0755 | 5.9224 | 5.7071 | 5.4459 | 5.1143 | 4.7592 | 4.3827 | 3.0898 | 2.0714 | 1.4633 | 8.3133 | 8.2122 | 8.0847 | 7.9898 | 7.8449 | 7.7051 | 7.5 | 7.2806 | 7.0418 | 6.3888 | 5.8888 | 5.6163 | 6.652 | 6.498 | 6.3173 | 6.1724 | 5.9684 | 5.7347 | 5.4204 | 5.0847 | 4.7286 | 3.6429 | 2.752 | 2.2367
|  | HASLINGBOURNE PRIMARY | HE |  |  |  |  | 6.4316 | 6.2745 | 6.0949 | 5.951 | 5.7531 | 5.5276 | 5.2235 | 4.902 | 4.5653 | 3.3541 | 2.5765 | 2.2194 | 8.2867 | 8.1735 | 8.0408 | 7.9316 | 7.7735 | 7.6235 | 7.4061 | 7.1684 | 6.9112 | 5.9469 | 4.9255 | 3.4704 | 6.652 | 6.5041 | 6.3327 | 6.199 | 6.0112 | 5.8092 | 5.5204 | 5.2143 | 4.8898 | 3.8837 | 3.2173 | 2.9235
|  | HASLINGBOURNE PRIMARY | CF |  |  |  |  | 6.499 | 6.398 | 6.2765 | 6.1398 | 6.0378 | 5.8918 | 5.7163 | 5.5786 | 5.3857 | 4.599 | 3.6459 | 2.7827 | 8.3173 | 8.2347 | 8.1337 | 8.0143 | 7.9112 | 7.7653 | 7.5867 | 7.4459 | 7.2459 | 6.2235 | 4.4653 | 1.4612 | 6.7041 | 6.6102 | 6.4949 | 6.3602 | 6.2653 | 6.1224 | 5.9449 | 5.8143 | 5.6235 | 4.9633 | 4.1561 | 3.401
MELKSHAM GSP | FROME BSP | HAWKERIDGE PRIMARY | MINIMUM HEADROOM | ST 86422 53026 | NO | NO | 0.1 | 3.2673 | 3.1847 | 3.0837 | 2.9653 | 2.8276 | 2.6633 | 2.4684 | 2.2745 | 2.098 | 1.3439 | 1.0704 | 0.95408 | 3.8153 | 3.7806 | 3.7347 | 3.6878 | 3.6276 | 3.552 | 3.4378 | 3.2878 | 3.1449 | 2.549 | 2.3378 | 2.2378 | 3.4918 | 3.4296 | 3.3551 | 3.2653 | 3.1622 | 3.0378 | 2.8898 | 2.7418 | 2.5571 | 1.7847 | 1.502 | 1.3867
|  | HAWKERIDGE PRIMARY | EE |  |  |  |  | 3.2673 | 3.1847 | 3.0837 | 2.9653 | 2.8276 | 2.6633 | 2.4684 | 2.2745 | 2.098 | 1.3439 | 1.1296 | 1.101 | 3.8153 | 3.7806 | 3.7347 | 3.6878 | 3.6276 | 3.552 | 3.4378 | 3.2878 | 3.1449 | 2.5684 | 2.4143 | 2.3888 | 3.4918 | 3.4296 | 3.3551 | 3.2653 | 3.1622 | 3.0378 | 2.8898 | 2.7418 | 2.5571 | 1.7878 | 1.5755 | 1.5429
|  | HAWKERIDGE PRIMARY | HT |  |  |  |  | 3.3235 | 3.2551 | 3.1714 | 3.0755 | 2.9561 | 2.8163 | 2.6418 | 2.4551 | 2.2653 | 1.4102 | 1.0704 | 0.95408 | 3.8388 | 3.8102 | 3.7724 | 3.7357 | 3.6857 | 3.6224 | 3.5398 | 3.4276 | 3.3102 | 2.6245 | 2.3571 | 2.2643 | 3.5316 | 3.4806 | 3.4153 | 3.3459 | 3.2531 | 3.1449 | 3.0133 | 2.8694 | 2.7255 | 1.8561 | 1.502 | 1.3867
|  | HAWKERIDGE PRIMARY | HE |  |  |  |  | 3.3306 | 3.2684 | 3.1878 | 3.0918 | 2.9735 | 2.8316 | 2.6561 | 2.4633 | 2.2612 | 1.3745 | 1.0918 | 0.96633 | 3.8429 | 3.8133 | 3.7776 | 3.7398 | 3.6898 | 3.6265 | 3.549 | 3.4327 | 3.2796 | 2.549 | 2.3378 | 2.2378 | 3.5398 | 3.4918 | 3.4306 | 3.3602 | 3.2724 | 3.1653 | 3.0327 | 2.8867 | 2.7286 | 1.7847 | 1.5173 | 1.398
|  | HAWKERIDGE PRIMARY | CF |  |  |  |  | 3.4031 | 3.3684 | 3.3286 | 3.2786 | 3.2224 | 3.1561 | 3.0663 | 2.9633 | 2.8439 | 2.1408 | 1.4745 | 0.97857 | 3.8694 | 3.851 | 3.8316 | 3.8092 | 3.7867 | 3.752 | 3.7112 | 3.6653 | 3.6133 | 3.1714 | 2.6316 | 2.252 | 3.5918 | 3.5663 | 3.5367 | 3.499 | 3.4592 | 3.4092 | 3.3408 | 3.2643 | 3.1745 | 2.5969 | 1.9 | 1.4041
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | HAWLEY PRIMARY | MINIMUM HEADROOM | SU 85973 57691 | NO | NO | 1.272 | 16.9469 | 16.5031 | 16.3469 | 15.9194 | 15.401 | 14.5041 | 13.5031 | 12.4918 | 11.7878 | 7.4204 | 4.0714 | 2.2378 | 18.2939 | 17.8735 | 17.7408 | 17.3122 | 16.848 | 16.2 | 15.4551 | 14.6898 | 14.149 | 10.8418 | 5.9929 | -5.3418 | 16.7582 | 16.2735 | 16.151 | 15.6857 | 15.1857 | 14.35 | 13.4082 | 12.4592 | 11.8153 | 8.1592 | 5.3102 | 3.75
|  | HAWLEY PRIMARY | EE |  |  |  |  | 16.9469 | 16.5031 | 16.3469 | 15.9194 | 15.401 | 14.5041 | 13.5031 | 12.4918 | 11.7878 | 7.7245 | 4.65 | 2.4163 | 18.2939 | 17.8735 | 17.7408 | 17.3122 | 16.848 | 16.2 | 15.4551 | 14.6898 | 14.149 | 10.8418 | 7.1643 | 1.2357 | 16.7582 | 16.2735 | 16.151 | 15.6857 | 15.1857 | 14.35 | 13.4082 | 12.4592 | 11.8153 | 8.348 | 5.8204 | 3.898
|  | HAWLEY PRIMARY | HT |  |  |  |  | 17.1796 | 16.8173 | 16.4786 | 16.0806 | 15.648 | 15.1602 | 14.3327 | 13.4714 | 12.5541 | 7.4204 | 4.0714 | 2.2378 | 18.6663 | 18.4092 | 18.1776 | 17.8827 | 17.551 | 17.4347 | 16.9673 | 16.4653 | 15.9163 | 13.2286 | 11.7908 | 11.0745 | 17.0776 | 16.7122 | 16.3724 | 15.9602 | 15.502 | 15.1684 | 14.401 | 13.6 | 12.7398 | 8.1592 | 5.3102 | 3.75
|  | HAWLEY PRIMARY | HE |  |  |  |  | 17.2102 | 16.8735 | 16.5602 | 16.1918 | 15.7918 | 15.449 | 14.7602 | 14.0439 | 13.3143 | 9.049 | 6 | 4.7092 | 18.5724 | 18.2673 | 17.9776 | 17.6184 | 17.2163 | 17.0429 | 16.5061 | 15.9276 | 15.3153 | 11.5633 | 7.8204 | 2.2449 | 17.099 | 16.7551 | 16.4408 | 16.0582 | 15.6347 | 15.4163 | 14.7643 | 14.0806 | 13.3776 | 9.5724 | 7.0582 | 5.9551
|  | HAWLEY PRIMARY | CF |  |  |  |  | 17.4837 | 17.3224 | 17.1602 | 16.9602 | 16.7388 | 16.4857 | 16.5031 | 16.2357 | 15.9327 | 13.2888 | 10.2837 | 7.5469 | 18.6735 | 18.4571 | 18.2316 | 17.9439 | 17.5929 | 17.1755 | 17.0173 | 16.5551 | 16.0582 | 12.2806 | 5.9929 | -5.3418 | 17.3316 | 17.1612 | 16.9857 | 16.7622 | 16.5143 | 16.2316 | 16.2939 | 16 | 15.6908 | 13.2112 | 10.5459 | 8.2816
NORTH HYDE GSP |  | HAYES PRIMARY | MINIMUM HEADROOM | TQ 09519 79541 | NO | YES | 22.787 | 25.334 | 24.3167 | 22.7932 | 21.281 | 19.6932 | 16.6044 | 13.0871 | 10.1238 | 7.3912 | -2.219 | -9.9292 | -13.0588 | 29.5842 | 28.8913 | 27.8281 | 26.7158 | 25.5546 | 22.676 | 19.376 | 16.726 | 14.0679 | 4.5148 | -3.4791 | -14.6638 | 23.7148 | 22.8474 | 21.3954 | 19.9107 | 18.3393 | 14.9362 | 11.0168 | 7.7832 | 4.8658 | -5.0699 | -12.9679 | -16.6128
|  | HAYES PRIMARY | EE |  |  |  |  | 25.334 | 24.3167 | 22.7932 | 21.281 | 19.6932 | 16.6044 | 13.0871 | 10.1238 | 7.3912 | -1.8425 | -7.0701 | -8.9721 | 29.5842 | 28.8913 | 27.8281 | 26.7158 | 25.5546 | 22.676 | 19.376 | 16.726 | 14.0679 | 4.5148 | -3.4791 | -14.2128 | 23.7148 | 22.8474 | 21.3954 | 19.9107 | 18.3393 | 14.9362 | 11.0168 | 7.7832 | 4.8658 | -4.374 | -9.3974 | -12.1505
|  | HAYES PRIMARY | HT |  |  |  |  | 25.8993 | 24.7095 | 23.3534 | 22.4442 | 21.2401 | 18.5289 | 15.5014 | 12.8616 | 9.9748 | -2.219 | -9.9292 | -13.0588 | 30.1015 | 29.3515 | 28.5219 | 27.9536 | 27.2464 | 24.7852 | 22.0077 | 19.7546 | 17.2097 | 7.1352 | 0.57908 | -3.0872 | 24.4566 | 23.3464 | 22.0944 | 21.3444 | 20.2026 | 17.2362 | 13.8872 | 11.0291 | 7.8566 | -5.0699 | -12.9679 | -16.6128
|  | HAYES PRIMARY | HE |  |  |  |  | 25.981 | 24.8922 | 23.5708 | 22.6544 | 21.3922 | 19.2136 | 16.634 | 14.7922 | 12.7779 | 3.6697 | -1.6599 | -4.817 | 29.9995 | 29.2628 | 28.3311 | 27.5842 | 26.626 | 24.576 | 22.1005 | 20.5505 | 18.7842 | 9.274 | 1.175 | -9.9638 | 24.4964 | 23.5097 | 22.2872 | 21.5311 | 20.3495 | 18.0209 | 15.2158 | 13.3423 | 11.2546 | 1.7474 | -3.4995 | -7.1128
|  | HAYES PRIMARY | CF |  |  |  |  | 26.6912 | 26.082 | 25.2044 | 24.3514 | 23.781 | 22.5187 | 20.8871 | 19.4034 | 18.1146 | 12.5993 | 7.0167 | 2.1881 | 30.3393 | 29.8719 | 29.1964 | 28.423 | 27.7536 | 26.1923 | 24.1944 | 22.3944 | 20.8138 | 13.6944 | 3.0628 | -14.6638 | 25.1383 | 24.5668 | 23.7719 | 22.9495 | 22.4923 | 21.0801 | 19.1883 | 17.4913 | 16.0403 | 10.2913 | 5.2821 | 1.2883
COWLEY GSP | HEADINGTON BSP | HEADINGTON PRIMARY | MINIMUM HEADROOM | SP 54440 08085 | NO | NO | 8.08 | 14.3852 | 13.5607 | 13.2566 | 12.5484 | 11.8178 | 9.8515 | 8.7841 | 7.7321 | 7.0454 | 4.1372 | 2.3056 | 2.077 | 14.3076 | 13.729 | 13.4729 | 12.9321 | 12.3668 | 11.1545 | 10.3515 | 9.5464 | 8.9821 | 6.0484 | 1.6566 | -8.8475 | 15.4045 | 14.6443 | 14.329 | 13.6586 | 12.9658 | 11.1719 | 10.1617 | 9.1668 | 8.4903 | 5.6872 | 4.0096 | 3.8035
|  | HEADINGTON PRIMARY | EE |  |  |  |  | 14.3852 | 13.5607 | 13.2566 | 12.5484 | 11.8178 | 9.8515 | 8.7841 | 7.7321 | 7.0454 | 4.1372 | 2.4831 | 2.676 | 14.3076 | 13.729 | 13.4729 | 12.9321 | 12.3668 | 11.1545 | 10.3515 | 9.5464 | 8.9821 | 6.0484 | 2.828 | -1.7526 | 15.4045 | 14.6443 | 14.329 | 13.6586 | 12.9658 | 11.1719 | 10.1617 | 9.1668 | 8.4903 | 5.6872 | 4.175 | 4.3433
|  | HEADINGTON PRIMARY | HT |  |  |  |  | 14.4892 | 13.9535 | 13.4413 | 12.8443 | 12.1913 | 10.8913 | 10.0984 | 9.277 | 8.427 | 4.4005 | 2.3056 | 2.077 | 14.5525 | 14.2301 | 13.9178 | 13.5464 | 13.1321 | 12.478 | 11.9913 | 11.4841 | 10.9474 | 8.5015 | 7.3127 | 7.1086 | 15.527 | 15.0198 | 14.5505 | 13.9903 | 13.379 | 12.1556 | 11.4066 | 10.6321 | 9.8219 | 6.0035 | 4.0096 | 3.8035
|  | HEADINGTON PRIMARY | HE |  |  |  |  | 14.8107 | 14.1647 | 13.6352 | 13.0433 | 12.427 | 11.2045 | 10.4903 | 9.7535 | 8.9923 | 5.8658 | 4.3474 | 4.0801 | 14.6137 | 14.1607 | 13.7739 | 13.326 | 12.8505 | 12.1127 | 11.5576 | 10.9688 | 10.3443 | 7.0117 | 3.7688 | -0.9628 | 15.7974 | 15.2066 | 14.7158 | 14.1647 | 13.5862 | 12.429 | 11.7382 | 11.0311 | 10.2974 | 7.2535 | 5.8341 | 5.5964
|  | HEADINGTON PRIMARY | CF |  |  |  |  | 15.2454 | 14.9923 | 14.6913 | 14.427 | 14.0872 | 12.8392 | 12.8586 | 12.4076 | 11.9301 | 9.0892 | 6.5923 | 4.3627 | 14.826 | 14.577 | 14.278 | 13.9943 | 13.6188 | 12.7352 | 12.5198 | 11.9974 | 11.4321 | 7.5994 | 1.6566 | -8.8475 | 16.1852 | 15.9494 | 15.6678 | 15.4331 | 15.1147 | 14.0178 | 14.0045 | 13.5831 | 13.1382 | 10.4566 | 7.9984 | 5.8372
NURSLING GSP | VELMORE BSP | HEDGE END PRIMARY | MINIMUM HEADROOM | SU 49035 15685 | NO | YES | 17.927 | 5.6069 | 4.962 | 4.2039 | 3.4957 | 2.6488 | 2.1376 | 1.8733 | 1.4539 | 1.361 | 0.19265 | -1.0798 | -1.9267 | 5.6365 | 5.2692 | 4.8814 | 4.4855 | 4.0253 | 3.6427 | 3.6314 | 3.3008 | 3.1345 | 2.1049 | 0.090612 | -4.0451 | 4.4794 | 3.9141 | 3.2896 | 2.6712 | 1.9406 | 1.4345 | 1.4294 | 1.0151 | 0.88347 | -0.054286 | -1.0727 | -1.7492
|  | HEDGE END PRIMARY | EE |  |  |  |  | 5.6069 | 4.962 | 4.2039 | 3.4957 | 2.6488 | 2.1376 | 1.9641 | 1.5243 | 1.361 | 0.46408 | -0.71857 | -1.7318 | 5.6365 | 5.2692 | 4.8814 | 4.4855 | 4.0253 | 3.6427 | 3.6314 | 3.3008 | 3.1345 | 2.1049 | 0.61306 | -1.6757 | 4.4794 | 3.9141 | 3.2896 | 2.6712 | 1.9406 | 1.4345 | 1.4427 | 1.0263 | 0.88347 | 0.13755 | -0.78388 | -1.6053
|  | HEDGE END PRIMARY | HT |  |  |  |  | 5.6906 | 5.0763 | 4.3396 | 3.6671 | 2.8794 | 2.3967 | 1.8733 | 1.4539 | 1.4682 | 0.19265 | -1.0798 | -1.9267 | 5.7763 | 5.4651 | 5.1212 | 4.7967 | 4.4447 | 4.1641 | 3.8427 | 3.5559 | 3.7029 | 2.9253 | 2.3529 | 1.9763 | 4.61 | 4.1018 | 3.5202 | 2.9631 | 2.3457 | 1.912 | 1.4294 | 1.0151 | 1.1416 | -0.054286 | -1.0727 | -1.7492
|  | HEDGE END PRIMARY | HE |  |  |  |  | 5.7202 | 5.1182 | 4.4018 | 3.7478 | 2.9937 | 2.6069 | 2.1916 | 1.8345 | 1.9457 | 1.0304 | -0.12163 | -0.83694 | 5.7631 | 5.4396 | 5.0794 | 4.7294 | 4.3467 | 4.0773 | 3.7804 | 3.4978 | 3.5284 | 2.3845 | 0.88653 | -1.2859 | 4.6335 | 4.1314 | 3.5641 | 3.0202 | 2.4324 | 2.0692 | 1.6682 | 1.2998 | 1.5161 | 0.63041 | -0.28184 | -0.83184
|  | HEDGE END PRIMARY | CF |  |  |  |  | 5.9018 | 5.4161 | 4.8365 | 4.3253 | 3.7243 | 3.4978 | 3.2702 | 3.0376 | 2.8763 | 2.1304 | 1.1284 | 0.23551 | 5.8263 | 5.5569 | 5.2386 | 4.9437 | 4.5896 | 4.3794 | 4.1406 | 3.8937 | 3.6722 | 2.4365 | 0.090612 | -4.0451 | 4.7733 | 4.3784 | 3.9192 | 3.4957 | 2.9998 | 2.8049 | 2.5651 | 2.3202 | 2.1324 | 1.5365 | 0.69571 | -0.021633
BRAMLEY (BASI) GSP | READING BSP | HENLEY PRIMARY | MINIMUM HEADROOM | SU 76070 82422 | NO | YES | 4.529 | 5.1514 | 4.7096 | 4.1075 | 3.8167 | 3.2993 | 2.4973 | 1.5953 | 0.6922 | 0.018735 | -3.5547 | -6.6047 | -8.3996 | 11.182 | 10.8147 | 10.3514 | 10.1647 | 9.7371 | 9.1636 | 8.4922 | 7.8085 | 7.3238 | 4.6259 | 1.4238 | -6.4384 | 6.4044 | 5.9575 | 5.3738 | 5.1636 | 4.6524 | 3.8932 | 3.0259 | 2.1616 | 1.5534 | -1.518 | -4.1772 | -5.6894
|  | HENLEY PRIMARY | EE |  |  |  |  | 5.1514 | 4.7096 | 4.1075 | 3.8167 | 3.2993 | 2.4973 | 1.5953 | 0.6922 | 0.018735 | -3.5547 | -6.0833 | -8.1058 | 11.182 | 10.8147 | 10.3514 | 10.1647 | 9.7371 | 9.1636 | 8.4922 | 7.8085 | 7.3238 | 4.6259 | 1.783 | -2.4333 | 6.4044 | 5.9575 | 5.3738 | 5.1636 | 4.6524 | 3.8932 | 3.0259 | 2.1616 | 1.5534 | -1.518 | -3.6721 | -5.4221
|  | HENLEY PRIMARY | HT |  |  |  |  | 5.431 | 5.0993 | 4.6575 | 4.1279 | 3.6636 | 3.2381 | 2.4728 | 1.6708 | 0.84833 | -3.5527 | -6.6047 | -8.3996 | 11.4902 | 11.2677 | 11.0014 | 10.6749 | 10.3636 | 10.1973 | 9.7555 | 9.2922 | 8.8055 | 6.3973 | 4.9483 | 4.2208 | 6.7157 | 6.382 | 5.982 | 5.4891 | 5.0351 | 4.7106 | 4.0024 | 3.2606 | 2.4902 | -1.4884 | -4.1772 | -5.6894
|  | HENLEY PRIMARY | HE |  |  |  |  | 5.4351 | 5.1177 | 4.6983 | 4.1902 | 3.7555 | 3.4453 | 2.7861 | 2.1055 | 1.4024 | -2.3639 | -4.8853 | -6.0558 | 11.4126 | 11.1422 | 10.8422 | 10.4657 | 10.1055 | 9.9198 | 9.4442 | 8.9381 | 8.4044 | 5.3279 | 2.4208 | -1.4394 | 6.7198 | 6.3983 | 6.0198 | 5.5473 | 5.1198 | 4.8993 | 4.2861 | 3.6483 | 2.9891 | -0.41698 | -2.5537 | -3.5741
|  | HENLEY PRIMARY | CF |  |  |  |  | 5.6534 | 5.4871 | 5.1667 | 4.8534 | 4.5861 | 4.2993 | 3.9422 | 3.9585 | 3.6269 | 1.2473 | -1.3109 | -3.6792 | 11.4993 | 11.3126 | 11.0361 | 10.7575 | 10.4606 | 10.1136 | 9.6963 | 9.5708 | 9.1504 | 6.1116 | 1.4238 | -6.4384 | 6.9116 | 6.7412 | 6.4412 | 6.1606 | 5.8922 | 5.6024 | 5.2412 | 5.3085 | 4.983 | 2.6902 | 0.42078 | -1.5904
AXMINSTER GSP | YEOVIL BSP | HENSTRIDGE PRIMARY | MINIMUM HEADROOM | ST 72676 19263 | NO | NO | 5.792 | 10.1373 | 9.7669 | 9.4016 | 8.8781 | 8.2495 | 8.0924 | 7.6424 | 7.2975 | 7.0434 | 5.7097 | 4.9322 | 4.4036 | 11.5126 | 11.2534 | 11.0289 | 10.6942 | 10.2973 | 10.3544 | 10.0452 | 9.7799 | 9.633 | 8.7534 | 7.5493 | 4.6401 | 11.2254 | 10.8642 | 10.5214 | 10.0367 | 9.4632 | 9.3887 | 8.9448 | 8.5846 | 8.355 | 7.2438 | 6.5785 | 6.1612
|  | HENSTRIDGE PRIMARY | EE |  |  |  |  | 10.1373 | 9.7669 | 9.4016 | 8.8781 | 8.2495 | 8.0924 | 7.6424 | 7.2975 | 7.0434 | 5.7097 | 4.9975 | 4.5556 | 11.5126 | 11.2534 | 11.0289 | 10.6942 | 10.2973 | 10.3544 | 10.0452 | 9.7799 | 9.633 | 8.7534 | 7.8146 | 6.384 | 11.2254 | 10.8642 | 10.5214 | 10.0367 | 9.4632 | 9.3887 | 8.9448 | 8.5846 | 8.355 | 7.2438 | 6.6571 | 6.2897
|  | HENSTRIDGE PRIMARY | HT |  |  |  |  | 10.2281 | 9.8995 | 9.5699 | 9.0985 | 8.5597 | 8.1607 | 7.724 | 7.3791 | 7.3158 | 5.8005 | 4.9322 | 4.4036 | 11.6565 | 11.4667 | 11.2983 | 11.0422 | 10.7728 | 10.5299 | 10.2493 | 10.0034 | 10.1503 | 9.2922 | 8.9095 | 8.6983 | 11.3683 | 11.0683 | 10.7826 | 10.3714 | 9.9152 | 9.5367 | 9.1122 | 8.752 | 8.7744 | 7.3285 | 6.5785 | 6.1612
|  | HENSTRIDGE PRIMARY | HE |  |  |  |  | 10.2618 | 9.9179 | 9.5985 | 9.1393 | 8.6087 | 8.2454 | 7.8495 | 7.5444 | 7.5179 | 6.0363 | 5.3301 | 5.0138 | 11.6585 | 11.4473 | 11.2748 | 11.0105 | 10.734 | 10.4932 | 10.2136 | 9.9565 | 10.1014 | 8.9758 | 8.0248 | 6.6565 | 11.3969 | 11.0867 | 10.8091 | 10.4081 | 9.9652 | 9.6183 | 9.2295 | 8.901 | 8.9561 | 7.5775 | 6.9999 | 6.7489
|  | HENSTRIDGE PRIMARY | CF |  |  |  |  | 10.3679 | 10.0893 | 9.8332 | 9.4669 | 9.0118 | 8.7689 | 8.5363 | 8.3546 | 8.1689 | 7.3924 | 6.424 | 5.5383 | 11.7105 | 11.5391 | 11.3973 | 11.1779 | 10.9054 | 10.7095 | 10.5432 | 10.3524 | 10.1554 | 9.2748 | 7.5493 | 4.6401 | 11.4999 | 11.253 | 11.0407 | 10.7265 | 10.3387 | 10.1061 | 9.8907 | 9.6877 | 9.4785 | 8.7295 | 7.8642 | 7.1316
FLEET-BRAMLEY GSP | ALTON BSP | HERRIARD PRIMARY | MINIMUM HEADROOM | SU 66770 44972 | YES | NO | 0.092 | 3.2559 | 3.2365 | 3.211 | 3.1895 | 3.163 | 3.1304 | 3.0875 | 3.0599 | 3.0344 | 2.9293 | 2.8936 | 2.8599 | 1.5638 | 1.5434 | 1.5189 | 1.4964 | 1.4699 | 1.4372 | 1.3923 | 1.3628 | 1.3372 | 1.1842 | 1.0393 | 0.69031 | 1.3918 | 1.3571 | 1.3092 | 1.2765 | 1.2214 | 1.1541 | 1.0653 | 1.0184 | 0.97449 | 0.78673 | 0.72143 | 0.65918
|  | HERRIARD PRIMARY | EE |  |  |  |  | 3.2559 | 3.2365 | 3.211 | 3.1895 | 3.163 | 3.1304 | 3.0875 | 3.0599 | 3.0344 | 2.9293 | 2.8997 | 2.8865 | 1.5638 | 1.5434 | 1.5189 | 1.4964 | 1.4699 | 1.4372 | 1.3923 | 1.3628 | 1.3372 | 1.1842 | 1.0709 | 0.91071 | 1.3918 | 1.3571 | 1.3092 | 1.2765 | 1.2214 | 1.1541 | 1.0653 | 1.0184 | 0.97449 | 0.78673 | 0.72653 | 0.69388
|  | HERRIARD PRIMARY | HT |  |  |  |  | 3.2712 | 3.2569 | 3.2365 | 3.2191 | 3.1977 | 3.1763 | 3.1436 | 3.1089 | 3.0753 | 2.9436 | 2.8936 | 2.8599 | 1.577 | 1.5628 | 1.5454 | 1.5291 | 1.5097 | 1.4893 | 1.4577 | 1.4281 | 1.3964 | 1.2679 | 1.2138 | 1.177 | 1.4245 | 1.4031 | 1.3694 | 1.3398 | 1.3 | 1.2622 | 1.2 | 1.1388 | 1.0694 | 0.81837 | 0.72143 | 0.65918
|  | HERRIARD PRIMARY | HE |  |  |  |  | 3.2702 | 3.2559 | 3.2385 | 3.2181 | 3.1987 | 3.1773 | 3.1436 | 3.111 | 3.0753 | 2.9324 | 2.8977 | 2.8742 | 1.576 | 1.5587 | 1.5403 | 1.5219 | 1.4985 | 1.4781 | 1.4423 | 1.4097 | 1.375 | 1.1934 | 1.0791 | 0.91684 | 1.4245 | 1.402 | 1.3704 | 1.3418 | 1.3041 | 1.2684 | 1.2102 | 1.152 | 1.0827 | 0.82143 | 0.7602 | 0.73163
|  | HERRIARD PRIMARY | CF |  |  |  |  | 3.2814 | 3.2681 | 3.2579 | 3.2446 | 3.2324 | 3.2151 | 3.1946 | 3.1824 | 3.1589 | 3.0477 | 2.961 | 2.8967 | 1.5842 | 1.5658 | 1.5536 | 1.5352 | 1.5179 | 1.4964 | 1.4709 | 1.4515 | 1.426 | 1.2617 | 1.0393 | 0.69031 | 1.4378 | 1.4112 | 1.3959 | 1.3663 | 1.3429 | 1.3112 | 1.2704 | 1.251 | 1.2051 | 0.99898 | 0.8551 | 0.75918
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE PRIMARY | MINIMUM HEADROOM | SU 84733 92200 | NO | NO | 7.471 | 3.1071 | 2.7051 | 2.2193 | 1.6744 | 1.2224 | 0.48669 | -0.398 | -1.2521 | -1.999 | -5.3358 | -7.5378 | -8.5807 | 6.5571 | 6.3673 | 6.1398 | 5.8775 | 5.5847 | 5.0887 | 4.454 | 3.8387 | 3.3122 | 1.0755 | -0.080653 | -5.3266 | 3.6459 | 3.2755 | 2.8132 | 2.2918 | 1.8622 | 1.1663 | 0.32751 | -0.48678 | -1.1898 | -4.2021 | -6.2072 | -7.1725
|  | HIGH WYCOMBE PRIMARY | EE |  |  |  |  | 3.1071 | 2.7051 | 2.2193 | 1.6744 | 1.2224 | 0.48669 | -0.398 | -1.2521 | -1.999 | -5.2123 | -6.7715 | -7.6807 | 6.5571 | 6.3673 | 6.1398 | 5.8775 | 5.5847 | 5.0887 | 4.454 | 3.8387 | 3.3122 | 1.3561 | 0.72343 | -2.1949 | 3.6459 | 3.2755 | 2.8132 | 2.2918 | 1.8622 | 1.1663 | 0.32751 | -0.48678 | -1.1898 | -3.997 | -5.3898 | -6.1909
|  | HIGH WYCOMBE PRIMARY | HT |  |  |  |  | 3.3877 | 3.1214 | 2.754 | 2.3438 | 1.8632 | 1.2408 | 0.61629 | -0.15106 | -0.94698 | -5.0909 | -7.3113 | -8.4215 | 6.7244 | 6.5949 | 6.4357 | 6.2724 | 6.0683 | 5.7214 | 5.3285 | 4.7979 | 4.2449 | 1.7285 | 0.51118 | -0.090857 | 3.8663 | 3.6673 | 3.3326 | 2.9428 | 2.4847 | 1.8949 | 1.3122 | 0.58363 | -0.17147 | -3.8745 | -5.9092 | -6.9184
|  | HIGH WYCOMBE PRIMARY | HE |  |  |  |  | 3.3775 | 3.103 | 2.7285 | 2.301 | 1.801 | 1.1612 | 0.36935 | -0.31943 | -1.1817 | -5.3358 | -7.5378 | -8.5807 | 6.7 | 6.5551 | 6.3857 | 6.2 | 5.9734 | 5.6 | 5.0326 | 4.5418 | 3.9163 | 1.0755 | -0.080653 | -1.7153 | 3.8663 | 3.651 | 3.3051 | 2.9 | 2.4193 | 1.8112 | 1.0581 | 0.40608 | -0.41127 | -4.2021 | -6.2072 | -7.1725
|  | HIGH WYCOMBE PRIMARY | CF |  |  |  |  | 3.6704 | 3.5255 | 3.3479 | 3.1438 | 2.9173 | 2.6244 | 2.2265 | 1.7724 | 1.402 | -1.6358 | -4.5133 | -6.9562 | 6.8285 | 6.7377 | 6.6285 | 6.502 | 6.3673 | 6.2081 | 6.001 | 5.7632 | 5.6132 | 3.4142 | 0.85404 | -5.3266 | 4.051 | 3.953 | 3.8347 | 3.6826 | 3.4785 | 3.1979 | 2.8153 | 2.3775 | 2.0275 | -0.87657 | -3.6021 | -5.7011
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN PRIMARY | MINIMUM HEADROOM | SU 86304 92972 | NO | NO | 4.343 | 36.1011 | 35.7908 | 35.4215 | 35.0082 | 34.5592 | 34.1715 | 33.4317 | 32.6939 | 32.0766 | 28.8327 | 26.0419 | 24.4715 | 37.3072 | 37.1204 | 36.85 | 36.5286 | 36.1286 | 35.8613 | 35.2929 | 34.6908 | 34.1817 | 31.3174 | 27.1582 | 17.849 | 34.7164 | 34.4235 | 34.0735 | 33.6806 | 33.2551 | 32.9143 | 32.2286 | 31.547 | 30.9868 | 28.097 | 25.7123 | 24.3551
|  | HIGH WYCOMBE TOWN PRIMARY | EE |  |  |  |  | 36.1011 | 35.7908 | 35.4215 | 35.0082 | 34.5592 | 34.1715 | 33.4317 | 32.6939 | 32.0766 | 28.8327 | 26.4857 | 24.6511 | 37.3072 | 37.1204 | 36.85 | 36.5286 | 36.1286 | 35.8613 | 35.2929 | 34.6908 | 34.1817 | 31.3174 | 28.1623 | 23.2715 | 34.7164 | 34.4235 | 34.0735 | 33.6806 | 33.2551 | 32.9143 | 32.2286 | 31.547 | 30.9868 | 28.097 | 26.0623 | 24.4664
|  | HIGH WYCOMBE TOWN PRIMARY | HT |  |  |  |  | 36.299 | 36.05 | 35.7592 | 35.4388 | 35.1215 | 34.5051 | 33.8194 | 33.3868 | 32.7021 | 28.8511 | 26.0419 | 24.4715 | 37.4888 | 37.3766 | 37.2378 | 37.0847 | 36.9082 | 36.6113 | 36.2551 | 36.0582 | 35.6786 | 33.5796 | 32.2113 | 31.5439 | 34.9194 | 34.6919 | 34.4245 | 34.1296 | 33.8357 | 33.2766 | 32.6521 | 32.2847 | 31.6643 | 28.2082 | 25.7123 | 24.3551
|  | HIGH WYCOMBE TOWN PRIMARY | HE |  |  |  |  | 36.2939 | 36.0592 | 35.7878 | 35.4878 | 35.1919 | 34.6592 | 34.0541 | 33.6286 | 32.8633 | 29.2602 | 27.4817 | 26.6296 | 37.4062 | 37.2572 | 37.0664 | 36.8204 | 36.5755 | 36.2204 | 35.7653 | 35.4908 | 34.998 | 32.0102 | 28.8082 | 24.3419 | 34.9072 | 34.6929 | 34.4378 | 34.1541 | 33.8786 | 33.3898 | 32.8337 | 32.5327 | 31.9796 | 29.0388 | 27.0357 | 26.2715
|  | HIGH WYCOMBE TOWN PRIMARY | CF |  |  |  |  | 36.5449 | 36.4041 | 36.2725 | 36.097 | 35.9041 | 35.7215 | 35.4582 | 35.1602 | 34.7653 | 32.3878 | 29.6704 | 27.498 | 37.5378 | 37.4245 | 37.2776 | 37.0796 | 36.8398 | 36.5908 | 36.2266 | 35.8123 | 35.3684 | 32.4704 | 27.1582 | 17.849 | 35.1368 | 35.0021 | 34.8796 | 34.7123 | 34.5286 | 34.3582 | 34.1123 | 33.8337 | 33.5419 | 31.9643 | 29.3949 | 27.3653
IVER 66KV GSP |  | HILLINGDON PRIMARY | MINIMUM HEADROOM | TQ 07470 82827 | NO | NO | 4.208 | 7.0611 | 5.754 | 4.3284 | 2.7142 | 0.95396 | -1.7532 | -4.8185 | -7.7062 | -9.9409 | -19.496 | -27.1971 | -31.1828 | 15.5131 | 14.4968 | 13.4101 | 12.1784 | 10.8101 | 8.6672 | 6.1907 | 3.858 | 2.0499 | -6.0838 | -13.7746 | -32.9491 | 8.3795 | 7.1305 | 5.7836 | 4.2774 | 2.6305 | -0.027673 | -3.0756 | -5.9134 | -8.0348 | -16.5756 | -23.5307 | -27.1256
|  | HILLINGDON PRIMARY | EE |  |  |  |  | 7.0611 | 5.754 | 4.3284 | 2.7142 | 0.95396 | -1.7532 | -4.8185 | -7.7062 | -9.9409 | -19.496 | -25.9777 | -29.9195 | 15.5131 | 14.4968 | 13.4101 | 12.1784 | 10.8101 | 8.6672 | 6.1907 | 3.858 | 2.0499 | -6.0838 | -13.7746 | -24.5726 | 8.3795 | 7.1305 | 5.7836 | 4.2774 | 2.6305 | -0.027673 | -3.0756 | -5.9134 | -8.0348 | -16.5756 | -22.2175 | -25.8185
|  | HILLINGDON PRIMARY | HT |  |  |  |  | 7.4846 | 6.6948 | 5.6182 | 4.4162 | 3.1468 | 0.88559 | -1.5991 | -4.0675 | -6.6573 | -19.1634 | -27.1971 | -31.1828 | 16.1193 | 15.705 | 15.0417 | 14.2805 | 13.4621 | 11.8774 | 10.0682 | 8.3642 | 6.5346 | -1.4971 | -6.194 | -8.6011 | 8.8938 | 8.2805 | 7.3101 | 6.2152 | 5.0284 | 2.8264 | 0.35498 | -2.0246 | -4.5501 | -16.2879 | -23.5307 | -27.1256
|  | HILLINGDON PRIMARY | HE |  |  |  |  | 7.508 | 6.6805 | 5.6223 | 4.454 | 3.1519 | 1.208 | -1.0226 | -3.146 | -5.3664 | -16.2195 | -23.2828 | -26.5287 | 15.9182 | 15.3274 | 14.5325 | 13.6284 | 12.5958 | 11.0295 | 9.1825 | 7.5203 | 5.7356 | -3.8889 | -12.2848 | -22.8073 | 8.8917 | 8.2489 | 7.2938 | 6.2305 | 5.008 | 3.1172 | 0.91212 | -1.095 | -3.2113 | -13.3511 | -19.6185 | -22.5909
|  | HILLINGDON PRIMARY | CF |  |  |  |  | 8.3611 | 7.7131 | 7.2805 | 6.5907 | 5.8448 | 4.9529 | 3.7927 | 2.607 | 1.4478 | -5.7756 | -13.1134 | -19.4981 | 16.3387 | 15.7346 | 15.3101 | 14.6244 | 13.8284 | 12.6958 | 11.308 | 9.8958 | 8.4927 | -0.22665 | -12.645 | -32.9491 | 9.605 | 8.958 | 8.655 | 7.9968 | 7.2795 | 6.3376 | 5.1356 | 3.9264 | 2.756 | -4.0409 | -10.5175 | -15.8991
LOVEDEAN GSP | PORTSMOUTH BSP | HILSEA PRIMARY | MINIMUM HEADROOM | SU 66394 03806 | NO | YES | 0.41 | 10.9277 | 10.8267 | 10.6512 | 10.4583 | 10.2369 | 9.9787 | 9.6644 | 9.3614 | 9.1053 | 8.0838 | 7.6624 | 7.4236 | 12.0726 | 12.0155 | 11.943 | 11.8665 | 11.7787 | 11.6757 | 11.5461 | 11.3206 | 11.1287 | 10.3522 | 10.0379 | 9.8451 | 9.8216 | 9.6808 | 9.5134 | 9.3267 | 9.1134 | 8.8685 | 8.5655 | 8.2767 | 8.0297 | 7.0379 | 6.6267 | 6.3951
|  | HILSEA PRIMARY | EE |  |  |  |  | 10.9277 | 10.8267 | 10.6512 | 10.4583 | 10.2369 | 9.9787 | 9.6644 | 9.3614 | 9.1053 | 8.142 | 7.9073 | 7.8838 | 12.0726 | 12.0155 | 11.943 | 11.8665 | 11.7787 | 11.6757 | 11.5461 | 11.3206 | 11.1287 | 10.4185 | 10.2634 | 10.2502 | 9.8216 | 9.6808 | 9.5134 | 9.3267 | 9.1134 | 8.8685 | 8.5655 | 8.2767 | 8.0297 | 7.1134 | 6.8951 | 6.8736
|  | HILSEA PRIMARY | HT |  |  |  |  | 11.0073 | 10.9267 | 10.8328 | 10.7104 | 10.5338 | 10.3297 | 10.0848 | 9.8206 | 9.5461 | 8.3114 | 7.8124 | 7.6053 | 12.1246 | 12.0828 | 12.0359 | 11.9818 | 11.9134 | 11.84 | 11.7502 | 11.6502 | 11.5236 | 10.6012 | 10.2328 | 10.0706 | 9.942 | 9.8338 | 9.7124 | 9.5675 | 9.3971 | 9.2032 | 8.9675 | 8.7124 | 8.4471 | 7.2614 | 6.7889 | 6.593
|  | HILSEA PRIMARY | HE |  |  |  |  | 11.0053 | 10.9216 | 10.8287 | 10.6787 | 10.4879 | 10.2706 | 10.0022 | 9.7114 | 9.4063 | 8.0838 | 7.6624 | 7.4236 | 12.1175 | 12.0706 | 12.0185 | 11.9553 | 11.8808 | 11.7971 | 11.6991 | 11.5879 | 11.3655 | 10.3522 | 10.0379 | 9.8451 | 9.9328 | 9.8195 | 9.691 | 9.5369 | 9.3583 | 9.1481 | 8.89 | 8.6083 | 8.3134 | 7.0379 | 6.6267 | 6.3951
|  | HILSEA PRIMARY | CF |  |  |  |  | 11.0951 | 11.0502 | 10.9981 | 10.9359 | 10.8634 | 10.7869 | 10.6389 | 10.4665 | 10.2848 | 9.1971 | 8.2644 | 7.6451 | 12.1655 | 12.1379 | 12.1073 | 12.0675 | 12.0246 | 11.9818 | 11.9226 | 11.8553 | 11.7838 | 11.2032 | 10.4981 | 10.0328 | 10.0338 | 9.994 | 9.9267 | 9.841 | 9.7461 | 9.643 | 9.5002 | 9.3328 | 9.1593 | 8.1083 | 7.2042 | 6.6104
MANNINGTON GSP | ARNEWOOD BSP | HINCHESLEA PRIMARY | MINIMUM HEADROOM | SU 27805 00447 | NO | NO | 0.495 | 7.7163 | 7.5459 | 7.3776 | 7.1541 | 6.9153 | 6.5367 | 6.5327 | 6.1847 | 5.8429 | 4.5296 | 3.3571 | 2.6745 | 8.55 | 8.3878 | 8.2551 | 8.0653 | 7.8653 | 7.5898 | 7.6898 | 7.4449 | 7.3031 | 6.5449 | 5.5061 | 2.8653 | 7.4102 | 7.2224 | 7.0633 | 6.8459 | 6.6112 | 6.2592 | 6.3041 | 5.9837 | 5.699 | 4.6418 | 3.6806 | 3.1316
|  | HINCHESLEA PRIMARY | EE |  |  |  |  | 7.7163 | 7.5459 | 7.3776 | 7.1541 | 6.9153 | 6.5367 | 6.5327 | 6.1847 | 5.9571 | 4.6551 | 3.5878 | 2.7888 | 8.55 | 8.3878 | 8.2551 | 8.0653 | 7.8653 | 7.5898 | 7.6898 | 7.4449 | 7.3031 | 6.5449 | 5.5184 | 4.0765 | 7.4102 | 7.2224 | 7.0633 | 6.8459 | 6.6112 | 6.2592 | 6.3041 | 5.9837 | 5.7898 | 4.7296 | 3.8827 | 3.2316
|  | HINCHESLEA PRIMARY | HT |  |  |  |  | 7.8061 | 7.6704 | 7.5541 | 7.4041 | 7.2398 | 6.9541 | 6.599 | 6.2296 | 5.8429 | 4.5296 | 3.3571 | 2.6745 | 8.6786 | 8.5755 | 8.4939 | 8.3735 | 8.2367 | 8.0918 | 7.8724 | 7.6378 | 7.4 | 6.9204 | 6.4684 | 6.2173 | 7.5327 | 7.3969 | 7.2837 | 7.1235 | 6.949 | 6.7092 | 6.3857 | 6.0469 | 5.699 | 4.6418 | 3.6806 | 3.1316
|  | HINCHESLEA PRIMARY | HE |  |  |  |  | 7.8204 | 7.699 | 7.5918 | 7.452 | 7.298 | 7.0816 | 6.7857 | 6.4806 | 6.1612 | 5.1071 | 4.0561 | 3.5245 | 8.6612 | 8.552 | 8.4643 | 8.3316 | 8.1878 | 8.052 | 7.8357 | 7.6031 | 7.3602 | 6.7459 | 5.7061 | 4.3622 | 7.5439 | 7.4153 | 7.3112 | 7.1622 | 6.9969 | 6.8112 | 6.5398 | 6.2531 | 5.9561 | 5.1133 | 4.2918 | 3.8653
|  | HINCHESLEA PRIMARY | CF |  |  |  |  | 7.9194 | 7.8439 | 7.7622 | 7.702 | 7.6112 | 7.4867 | 7.3806 | 7.2255 | 7.0622 | 6.4337 | 5.4643 | 4.5031 | 8.7133 | 8.6235 | 8.5255 | 8.4571 | 8.3439 | 8.2112 | 8.101 | 7.9337 | 7.7592 | 7.0786 | 5.5061 | 2.8653 | 7.6286 | 7.5398 | 7.4459 | 7.3827 | 7.2755 | 7.1541 | 7.0582 | 6.9041 | 6.7429 | 6.199 | 5.3806 | 4.6082
FLEET-BRAMLEY GSP | ALDERSHOT BSP | HINDHEAD PRIMARY | MINIMUM HEADROOM | SU 88631 36479 | NO | YES | 2.777 | 17.7326 | 17.406 | 16.9673 | 16.8662 | 16.3816 | 15.7367 | 14.9775 | 14.2683 | 13.7816 | 10.9795 | 8.7642 | 7.4795 | 21.2571 | 20.9795 | 20.6254 | 20.604 | 20.2407 | 19.7907 | 19.2448 | 18.7295 | 18.404 | 16.5744 | 14.203 | 8.2928 | 18.6601 | 18.3469 | 17.9193 | 17.8469 | 17.3826 | 16.7703 | 16.0571 | 15.3938 | 14.9448 | 12.5071 | 10.5438 | 9.4713
|  | HINDHEAD PRIMARY | EE |  |  |  |  | 17.7326 | 17.406 | 16.9673 | 16.8662 | 16.3816 | 15.7367 | 14.9775 | 14.2683 | 13.7816 | 11.1275 | 9.2122 | 7.7428 | 21.2571 | 20.9795 | 20.6254 | 20.604 | 20.2407 | 19.7907 | 19.2448 | 18.7295 | 18.404 | 16.5744 | 14.4805 | 11.3397 | 18.6601 | 18.3469 | 17.9193 | 17.8469 | 17.3826 | 16.7703 | 16.0571 | 15.3938 | 14.9448 | 12.6193 | 10.9458 | 9.703
|  | HINDHEAD PRIMARY | HT |  |  |  |  | 17.9622 | 17.7091 | 17.3387 | 16.9816 | 16.504 | 15.8958 | 15.5867 | 14.953 | 14.2989 | 10.9795 | 8.7642 | 7.4795 | 21.5183 | 21.352 | 21.105 | 20.8826 | 20.5703 | 20.2091 | 20.1785 | 19.8173 | 19.4367 | 17.7081 | 16.7846 | 16.2601 | 18.8918 | 18.654 | 18.3081 | 17.9693 | 17.5173 | 16.9448 | 16.6938 | 16.1132 | 15.5081 | 12.5071 | 10.5438 | 9.4713
|  | HINDHEAD PRIMARY | HE |  |  |  |  | 17.9918 | 17.7509 | 17.4326 | 17.1152 | 16.6795 | 16.1407 | 15.9326 | 15.4081 | 14.8724 | 12.003 | 10.1387 | 9.2448 | 21.4785 | 21.2816 | 21.0305 | 20.7877 | 20.4591 | 20.0683 | 20.0193 | 19.6407 | 19.2418 | 17.0367 | 14.9356 | 12.0367 | 18.9162 | 18.6897 | 18.3887 | 18.0918 | 17.6775 | 17.1642 | 16.9969 | 16.5091 | 16.0081 | 13.4183 | 11.7918 | 11.0499
|  | HINDHEAD PRIMARY | CF |  |  |  |  | 18.1877 | 18.0346 | 17.8469 | 17.6928 | 17.4856 | 17.253 | 16.9071 | 16.9775 | 16.6897 | 14.7285 | 12.7928 | 10.9173 | 21.5744 | 21.4213 | 21.2316 | 21.0611 | 20.8346 | 20.5611 | 20.1877 | 20.2091 | 19.8836 | 17.6377 | 14.203 | 8.2928 | 19.0969 | 18.953 | 18.7703 | 18.6244 | 18.4213 | 18.1969 | 17.852 | 17.9499 | 17.6754 | 15.8162 | 14.0652 | 12.4489
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL PRIMARY | MINIMUM HEADROOM | SU 00702 06030 | YES | NO | 0.4 | 5.0758 | 5.0217 | 4.9462 | 4.8727 | 4.7891 | 4.7248 | 4.6064 | 4.4891 | 4.4391 | 4.1993 | 4.1095 | 4.0278 | 5.3191 | 5.2824 | 5.2293 | 5.1742 | 5.113 | 5.0681 | 4.9803 | 4.8957 | 4.8559 | 4.6528 | 4.2957 | 3.5752 | 5.0147 | 4.9637 | 4.8902 | 4.8178 | 4.7372 | 4.6749 | 4.5627 | 4.4474 | 4.3994 | 4.1749 | 4.0923 | 4.0188
|  | HINTON MARTELL PRIMARY | EE |  |  |  |  | 5.0758 | 5.0217 | 4.9462 | 4.8727 | 4.7891 | 4.7248 | 4.6064 | 4.4891 | 4.4391 | 4.1993 | 4.1095 | 4.0635 | 5.3191 | 5.2824 | 5.2293 | 5.1742 | 5.113 | 5.0681 | 4.9803 | 4.8957 | 4.8559 | 4.6528 | 4.4467 | 4.1008 | 5.0147 | 4.9637 | 4.8902 | 4.8178 | 4.7372 | 4.6749 | 4.5627 | 4.4474 | 4.3994 | 4.1749 | 4.0923 | 4.0515
|  | HINTON MARTELL PRIMARY | HT |  |  |  |  | 5.1258 | 5.0697 | 5.0268 | 4.9635 | 4.9268 | 4.8574 | 4.7697 | 4.6768 | 4.6258 | 4.2523 | 4.1227 | 4.0278 | 5.3681 | 5.3334 | 5.3048 | 5.265 | 5.2446 | 5.2018 | 5.1436 | 5.0865 | 5.0559 | 4.8263 | 4.7579 | 4.7089 | 5.0637 | 5.0096 | 4.9698 | 4.9076 | 4.8749 | 4.8056 | 4.7239 | 4.6331 | 4.5821 | 4.226 | 4.1045 | 4.0188
|  | HINTON MARTELL PRIMARY | HE |  |  |  |  | 5.1248 | 5.0697 | 5.0268 | 4.9646 | 4.9299 | 4.8605 | 4.7727 | 4.6819 | 4.6319 | 4.2207 | 4.1319 | 4.087 | 5.3589 | 5.3181 | 5.2885 | 5.2426 | 5.2181 | 5.1681 | 5.1048 | 5.0375 | 4.9997 | 4.6701 | 4.461 | 4.1171 | 5.0627 | 5.0086 | 4.9688 | 4.9076 | 4.878 | 4.8096 | 4.726 | 4.6372 | 4.5902 | 4.1943 | 4.1178 | 4.077
|  | HINTON MARTELL PRIMARY | CF |  |  |  |  | 5.1299 | 5.0952 | 5.0584 | 5.0125 | 4.9625 | 4.936 | 4.8819 | 4.8186 | 4.7533 | 4.4523 | 4.2564 | 4.1258 | 5.361 | 5.3344 | 5.3059 | 5.2722 | 5.2314 | 5.2038 | 5.1528 | 5.0997 | 5.0395 | 4.714 | 4.2957 | 3.5752 | 5.0698 | 5.0351 | 5.0015 | 4.9576 | 4.9066 | 4.8821 | 4.83 | 4.7688 | 4.7056 | 4.4127 | 4.228 | 4.1045
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HITCHES LANE PRIMARY | MINIMUM HEADROOM | SU 79461 54769 | NO | NO | 9.465 | 8.289 | 7.4758 | 6.6982 | 5.7329 | 4.6594 | 3.2952 | 1.6411 | 0.037 | -1.4334 | -8.7334 | -12.4354 | -14.711 | 13.2799 | 12.6054 | 12.1921 | 11.4911 | 10.7197 | 9.7186 | 8.538 | 7.3564 | 6.4105 | 1.6288 | -2.8028 | -13.3681 | 8.8911 | 8.0707 | 7.5778 | 6.7656 | 5.8533 | 4.5564 | 3.0482 | 1.5054 | 0.32373 | -6.164 | -10.165 | -12.7212
|  | HITCHES LANE PRIMARY | EE |  |  |  |  | 8.289 | 7.4758 | 6.6982 | 5.7329 | 4.6594 | 3.2952 | 1.6411 | 0.037 | -1.4334 | -7.5977 | -11.4406 | -14.5865 | 13.2799 | 12.6054 | 12.1921 | 11.4911 | 10.7197 | 9.7186 | 8.538 | 7.3564 | 6.4105 | 1.6288 | -2.8028 | -8.5579 | 8.8911 | 8.0707 | 7.5778 | 6.7656 | 5.8533 | 4.5564 | 3.0482 | 1.5054 | 0.32373 | -5.6303 | -9.7844 | -12.6671
|  | HITCHES LANE PRIMARY | HT |  |  |  |  | 9.0074 | 8.4033 | 7.6992 | 6.935 | 6.2023 | 5.0758 | 3.7278 | 2.289 | 0.76557 | -6.8059 | -11.9283 | -14.711 | 13.835 | 13.4125 | 12.9074 | 12.387 | 12.1115 | 11.3839 | 10.5431 | 9.6411 | 8.6982 | 4.188 | 1.4901 | 0.10537 | 9.3707 | 8.7605 | 8.0472 | 7.3339 | 6.8992 | 5.7503 | 4.4676 | 3.1197 | 1.7186 | -5.4416 | -10.165 | -12.7212
|  | HITCHES LANE PRIMARY | HE |  |  |  |  | 8.8778 | 8.1952 | 7.4023 | 6.5401 | 5.6707 | 4.4197 | 2.8748 | 1.2176 | -0.45994 | -8.7334 | -12.4354 | -13.5283 | 13.6982 | 13.2033 | 12.6258 | 12.0278 | 11.6635 | 10.8758 | 9.9411 | 8.935 | 7.8931 | 2.2258 | -2.2283 | -7.2712 | 9.3584 | 8.7543 | 8.0472 | 7.3411 | 6.9054 | 5.8819 | 4.6982 | 3.3146 | 1.7115 | -6.164 | -9.6212 | -10.6161
|  | HITCHES LANE PRIMARY | CF |  |  |  |  | 9.5615 | 9.186 | 8.7676 | 8.3258 | 7.8207 | 7.3931 | 6.6615 | 5.8319 | 4.9411 | -0.85484 | -6.6069 | -11.4957 | 13.9941 | 13.6033 | 13.2156 | 12.7952 | 12.3084 | 12.0564 | 11.4421 | 10.7656 | 10.0421 | 4.9329 | -2.2803 | -13.3681 | 9.8605 | 9.4574 | 9.0717 | 8.6686 | 8.1962 | 8.1074 | 7.6013 | 7.0176 | 6.3839 | 1.2921 | -4.1589 | -8.7661
LOVEDEAN GSP | FAREHAM (MAIN) BSP | HOEFORD PRIMARY | MINIMUM HEADROOM | SU 57855 04433 | NO | YES | 8.021 | 0.25713 | -0.088792 | -0.31838 | -0.71532 | 27.3908 | 26.6888 | 25.9122 | 25.1449 | 24.3479 | 20.3092 | 17.6806 | 16.1439 | 2.3816 | 2.0816 | 1.799 | 1.403 | 27.6684 | 27.1245 | 26.4653 | 25.7643 | 25.2092 | 21.9694 | 17.049 | 6.45 | -0.26328 | -0.70104 | -1.099 | -1.6541 | 25.3724 | 24.6235 | 23.7316 | 22.8714 | 22.1592 | 18.6806 | 16.5122 | 15.5459
|  | HOEFORD PRIMARY | EE |  |  |  |  | 0.25713 | -0.088792 | -0.31838 | -0.71532 | 27.3908 | 26.6888 | 25.9122 | 25.1449 | 24.3479 | 20.6724 | 18.2316 | 16.2377 | 2.3816 | 2.0816 | 1.799 | 1.403 | 27.6684 | 27.1245 | 26.4653 | 25.7643 | 25.2092 | 21.9694 | 18.3571 | 12.8745 | -0.26328 | -0.70104 | -1.099 | -1.6541 | 25.3724 | 24.6235 | 23.7316 | 22.8714 | 22.1592 | 19.351 | 17.552 | 15.8337
|  | HOEFORD PRIMARY | HT |  |  |  |  | 0.47753 | 0.21223 | -0.081649 | -0.39798 | 27.7469 | 27.3 | 26.6286 | 25.9388 | 25.2245 | 20.8592 | 17.8551 | 16.1439 | 2.6898 | 2.5041 | 2.2684 | 2.0194 | 28.4163 | 28.1418 | 27.6663 | 27.1653 | 26.6286 | 23.9235 | 22.5847 | 21.9479 | 0.13876 | -0.1643 | -0.53063 | -0.92349 | 26.2204 | 25.7602 | 25.0735 | 24.3479 | 23.5857 | 19.7153 | 17.3071 | 15.8357
|  | HOEFORD PRIMARY | HE |  |  |  |  | 0.46019 | 0.18468 | -0.12042 | -0.47859 | 27.649 | 27.252 | 26.6214 | 25.9632 | 25.152 | 20.3092 | 17.6806 | 16.6245 | 2.6092 | 2.3765 | 2.0918 | 1.7459 | 28.0775 | 27.702 | 27.1204 | 26.4939 | 25.8367 | 22.3439 | 18.5571 | 13.352 | 0.051004 | -0.29389 | -0.71124 | -1.197 | 25.8745 | 25.3449 | 24.5571 | 23.7173 | 22.8388 | 18.6806 | 16.5122 | 15.5459
|  | HOEFORD PRIMARY | CF |  |  |  |  | 0.71631 | 0.5806 | 0.39182 | 0.20202 | 28.4724 | 28.2561 | 28.1592 | 27.8847 | 27.5939 | 24.8102 | 21.5408 | 18.8877 | 2.8194 | 2.6898 | 2.451 | 2.1653 | 28.5 | 28.1071 | 27.8928 | 27.4265 | 26.9306 | 23.2061 | 17.049 | 6.45 | 0.39794 | 0.22243 | -0.012261 | -0.28573 | 27.0081 | 26.7041 | 26.4204 | 25.9847 | 25.5163 | 22.4724 | 19.6143 | 17.5735
MANNINGTON GSP | LYTCHETT BSP | HOLES BAY PRIMARY | MINIMUM HEADROOM | SZ 00725 91955 | NO | NO | 2.278 | 4.892 | 4.7287 | 4.5287 | 4.3185 | 4.1277 | 3.74 | 3.2665 | 2.8073 | 2.4277 | 0.66751 | -0.38351 | -0.87127 | 5.0214 | 4.8836 | 4.7234 | 4.551 | 4.3979 | 4.1704 | 3.9061 | 3.5806 | 3.252 | 1.7785 | 1.052 | -1.7072 | 3.5434 | 3.3985 | 3.2169 | 3.022 | 2.8455 | 2.473 | 2.021 | 1.5832 | 1.2169 | -0.48208 | -1.6627 | -2.2372
|  | HOLES BAY PRIMARY | EE |  |  |  |  | 4.892 | 4.7287 | 4.5287 | 4.3185 | 4.1277 | 3.74 | 3.2665 | 2.8073 | 2.4277 | 1.0706 | 0.30935 | -0.30698 | 5.0214 | 4.8836 | 4.7234 | 4.551 | 4.3979 | 4.1704 | 3.9061 | 3.5806 | 3.252 | 2.1163 | 1.3938 | 0.041796 | 3.5434 | 3.3985 | 3.2169 | 3.022 | 2.8455 | 2.473 | 2.021 | 1.5832 | 1.2169 | -0.11473 | -0.73514 | -1.1137
|  | HOLES BAY PRIMARY | HT |  |  |  |  | 4.9859 | 4.8389 | 4.6716 | 4.5012 | 4.3389 | 4.0338 | 3.694 | 3.3655 | 3.0053 | 1.2134 | 0.10731 | -0.5029 | 5.1265 | 5.0316 | 4.9214 | 4.8132 | 4.7102 | 4.5489 | 4.3591 | 4.1806 | 3.9714 | 2.4489 | 1.8163 | 1.5428 | 3.6598 | 3.5465 | 3.42 | 3.2761 | 3.1271 | 2.8475 | 2.5332 | 2.2414 | 1.9098 | 0.065878 | -1.0229 | -1.5464
|  | HOLES BAY PRIMARY | HE |  |  |  |  | 4.994 | 4.8553 | 4.693 | 4.5185 | 4.3614 | 4.092 | 3.7604 | 3.3318 | 2.8604 | 0.66751 | -0.38351 | -0.87127 | 5.0959 | 4.9836 | 4.8551 | 4.7122 | 4.5847 | 4.402 | 4.1836 | 3.9704 | 3.6224 | 1.7785 | 1.052 | 0.054041 | 3.6649 | 3.5618 | 3.421 | 3.2649 | 3.1138 | 2.8924 | 2.4944 | 2.0822 | 1.6302 | -0.48208 | -1.6627 | -2.2372
|  | HOLES BAY PRIMARY | CF |  |  |  |  | 5.1257 | 5.0461 | 4.9532 | 4.8563 | 4.7604 | 4.6706 | 4.5328 | 4.3859 | 4.193 | 2.5328 | 1.0369 | -0.20494 | 5.1704 | 5.0836 | 4.9867 | 4.8867 | 4.7806 | 4.6744 | 4.5306 | 4.3734 | 4.2183 | 3.0469 | 1.3132 | -1.7072 | 3.7373 | 3.6659 | 3.5791 | 3.4934 | 3.4026 | 3.3342 | 3.2138 | 3.073 | 2.9016 | 1.3036 | -0.13004 | -1.377
MELKSHAM GSP | FROME BSP | HOLWELL PRIMARY | MINIMUM HEADROOM | ST 72191 44633 | NO | NO | 0.641 | 4.0184 | 3.9541 | 3.8684 | 3.7724 | 3.6571 | 3.5153 | 3.3643 | 3.251 | 3.1571 | 2.7071 | 2.5571 | 2.448 | 4.7255 | 4.6898 | 4.65 | 4.6031 | 4.5102 | 4.4337 | 4.3459 | 4.2796 | 4.2214 | 3.9878 | 3.7622 | 3.0245 | 3.2816 | 3.2245 | 3.1551 | 3.0796 | 2.9694 | 2.849 | 2.7235 | 2.6255 | 2.5449 | 2.1398 | 2.0133 | 1.9214
|  | HOLWELL PRIMARY | EE |  |  |  |  | 4.0184 | 3.9541 | 3.8684 | 3.7724 | 3.6571 | 3.5153 | 3.3643 | 3.251 | 3.1571 | 2.7071 | 2.5571 | 2.4969 | 4.7255 | 4.6898 | 4.65 | 4.6031 | 4.5102 | 4.4337 | 4.3459 | 4.2796 | 4.2214 | 4.0255 | 3.8408 | 3.4898 | 3.2816 | 3.2245 | 3.1551 | 3.0796 | 2.9694 | 2.849 | 2.7235 | 2.6255 | 2.5449 | 2.1398 | 2.0133 | 1.9684
|  | HOLWELL PRIMARY | HT |  |  |  |  | 4.0694 | 4.0102 | 3.9398 | 3.8265 | 3.7296 | 3.6184 | 3.499 | 3.4061 | 3.2898 | 2.8051 | 2.5847 | 2.448 | 4.7571 | 4.7306 | 4.7 | 4.6112 | 4.548 | 4.4908 | 4.4265 | 4.3724 | 4.3102 | 4.0643 | 3.9592 | 3.8929 | 3.3204 | 3.2704 | 3.2122 | 3.1071 | 3.0214 | 2.9265 | 2.8265 | 2.7408 | 2.6418 | 2.2306 | 2.0398 | 1.9214
|  | HOLWELL PRIMARY | HE |  |  |  |  | 4.0694 | 4.0122 | 3.9408 | 3.8878 | 3.7735 | 3.6571 | 3.5347 | 3.4388 | 3.3194 | 2.7684 | 2.6194 | 2.5612 | 4.7551 | 4.7245 | 4.6939 | 4.6622 | 4.5745 | 4.5051 | 4.4296 | 4.3663 | 4.2898 | 3.9878 | 3.8694 | 3.5224 | 3.3194 | 3.2714 | 3.2122 | 3.1653 | 3.0592 | 2.9612 | 2.8551 | 2.7673 | 2.6633 | 2.1796 | 2.05 | 2.0051
|  | HOLWELL PRIMARY | CF |  |  |  |  | 4.0918 | 4.0388 | 3.9908 | 3.9306 | 3.8888 | 3.8031 | 3.7204 | 3.6306 | 3.5663 | 3.1194 | 2.8673 | 2.6347 | 4.7786 | 4.7582 | 4.7398 | 4.7153 | 4.6939 | 4.6418 | 4.5898 | 4.5347 | 4.4878 | 4.198 | 3.7622 | 3.0245 | 3.3398 | 3.2929 | 3.252 | 3.202 | 3.1612 | 3.0867 | 3.0133 | 2.9347 | 2.8765 | 2.4939 | 2.2765 | 2.0704
MANNINGTON GSP | SALISBURY BSP | HOMINGTON PRIMARY | MINIMUM HEADROOM | SU 11742 26037 | NO | NO | 0.247 | 7.2071 | 7.0816 | 6.9663 | 6.8204 | 6.6684 | 6.5031 | 6.2582 | 6.0092 | 5.8745 | 5.1714 | 4.8673 | 4.6418 | 9.6888 | 9.5827 | 9.4959 | 9.3735 | 9.2378 | 9.1153 | 8.9286 | 8.7398 | 8.6439 | 8.1908 | 7.7653 | 6.5898 | 9.3041 | 9.1684 | 9.0582 | 8.9061 | 8.7429 | 8.5786 | 8.349 | 8.1092 | 7.9878 | 7.3653 | 7.1163 | 6.9296
|  | HOMINGTON PRIMARY | EE |  |  |  |  | 7.2071 | 7.0816 | 6.9663 | 6.8204 | 6.6684 | 6.5031 | 6.2582 | 6.0092 | 5.8745 | 5.1714 | 4.8673 | 4.7286 | 9.6888 | 9.5827 | 9.4959 | 9.3735 | 9.2378 | 9.1153 | 8.9286 | 8.7398 | 8.6439 | 8.1908 | 7.7888 | 7.2204 | 9.3041 | 9.1684 | 9.0582 | 8.9061 | 8.7429 | 8.5786 | 8.349 | 8.1092 | 7.9878 | 7.3653 | 7.1163 | 6.9959
|  | HOMINGTON PRIMARY | HT |  |  |  |  | 7.2653 | 7.1724 | 7.0602 | 6.9388 | 6.8357 | 6.6745 | 6.502 | 6.3173 | 6.1673 | 5.3143 | 4.9133 | 4.6418 | 9.7735 | 9.7112 | 9.6357 | 9.55 | 9.4837 | 9.3776 | 9.251 | 9.1163 | 9.0245 | 8.4592 | 8.2541 | 8.1306 | 9.3827 | 9.2878 | 9.1806 | 9.0602 | 8.9643 | 8.8082 | 8.6316 | 8.4449 | 8.3031 | 7.4837 | 7.1429 | 6.9296
|  | HOMINGTON PRIMARY | HE |  |  |  |  | 7.2724 | 7.1857 | 7.0827 | 6.9714 | 6.849 | 6.7245 | 6.5602 | 6.3857 | 6.249 | 5.3622 | 5.1153 | 4.9531 | 9.7643 | 9.7031 | 9.6286 | 9.5408 | 9.4408 | 9.3643 | 9.2337 | 9.0929 | 8.9949 | 8.3378 | 7.9592 | 7.402 | 9.3878 | 9.3 | 9.201 | 9.0898 | 8.9643 | 8.8541 | 8.6898 | 8.5122 | 8.3633 | 7.5041 | 7.2347 | 7.0786
|  | HOMINGTON PRIMARY | CF |  |  |  |  | 7.3204 | 7.2337 | 7.1633 | 7.0816 | 6.9867 | 6.8837 | 6.798 | 6.6837 | 6.5653 | 5.9694 | 5.4908 | 5.0878 | 9.798 | 9.7255 | 9.6776 | 9.6092 | 9.5347 | 9.4408 | 9.3724 | 9.2633 | 9.15 | 8.5133 | 7.7653 | 6.5898 | 9.4327 | 9.349 | 9.2847 | 9.2031 | 9.1122 | 9.0082 | 8.9337 | 8.8184 | 8.6959 | 8.0878 | 7.6265 | 7.2327
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HOOK PRIMARY | MINIMUM HEADROOM | SU 72602 53780 | NO | NO | 6.303 | 12.4187 | 12.0045 | 11.4953 | 11.2749 | 10.7422 | 9.8983 | 8.8483 | 7.7943 | 6.8892 | 2.2657 | -0.35881 | -1.3853 | 14.8657 | 14.6177 | 14.3116 | 14.1024 | 13.7545 | 13.3065 | 12.6198 | 11.9187 | 11.3963 | 8.1657 | 6.1381 | -0.23534 | 12.0953 | 11.6759 | 11.1626 | 10.9555 | 10.2647 | 9.3963 | 8.3565 | 7.3483 | 6.4871 | 2.0912 | -0.13534 | -0.89452
|  | HOOK PRIMARY | EE |  |  |  |  | 12.4187 | 12.0045 | 11.4953 | 11.2749 | 10.7422 | 9.8983 | 8.8483 | 7.7943 | 6.8892 | 3.1514 | 1.23 | -0.34044 | 14.8657 | 14.6177 | 14.3116 | 14.1024 | 13.7545 | 13.3065 | 12.6198 | 11.9187 | 11.3963 | 8.7647 | 6.4749 | 3.3055 | 12.0953 | 11.6759 | 11.1626 | 10.9555 | 10.2647 | 9.3963 | 8.3565 | 7.3483 | 6.4871 | 3.1932 | 1.8636 | 0.52997
|  | HOOK PRIMARY | HT |  |  |  |  | 12.7361 | 12.383 | 12.0289 | 11.6024 | 11.1269 | 10.3116 | 9.7871 | 8.9177 | 8.031 | 3.5626 | 0.78609 | -0.60677 | 15.1289 | 14.9514 | 14.7667 | 14.5361 | 14.2708 | 13.9147 | 13.6473 | 13.2279 | 12.7636 | 9.7708 | 8.3585 | 7.7412 | 12.4443 | 12.1004 | 11.7585 | 11.3432 | 10.8779 | 10.1198 | 9.6759 | 8.8647 | 8.0361 | 3.8504 | 1.4902 | 0.29833
|  | HOOK PRIMARY | HE |  |  |  |  | 12.731 | 12.3769 | 12.0259 | 11.5963 | 11.1157 | 10.3902 | 9.7738 | 8.7085 | 7.5851 | 2.2657 | -0.35881 | -1.3853 | 15.0596 | 14.8453 | 14.6198 | 14.3402 | 14.0167 | 13.6075 | 13.2698 | 12.7667 | 12.0187 | 8.1657 | 6.2871 | 3.3136 | 12.433 | 12.0892 | 11.7443 | 11.3249 | 10.8545 | 10.0738 | 9.2483 | 8.2289 | 7.1555 | 2.0912 | -0.13534 | -0.89452
|  | HOOK PRIMARY | CF |  |  |  |  | 13.0075 | 12.8208 | 12.5943 | 12.383 | 12.1136 | 11.7973 | 11.4096 | 11.3269 | 10.8983 | 6.9779 | 3.2494 | 0.52384 | 15.2177 | 15.0912 | 14.931 | 14.7728 | 14.5718 | 14.3361 | 14.0238 | 13.8453 | 13.4269 | 10.3718 | 6.1381 | -0.23534 | 12.681 | 12.4994 | 12.2708 | 12.0585 | 11.7871 | 11.4728 | 11.08 | 10.9055 | 10.3075 | 6.5524 | 3.0157 | 0.48405
LALEHAM GSP | EAST BEDFONT BSP | HOPE AND ANCHOR PRIMARY | MINIMUM HEADROOM | TQ 12710 72057 | YES | NO | 0.315 | 10.8368 | 10.7174 | 10.5705 | 10.444 | 10.2787 | 10.043 | 9.8195 | 9.5613 | 9.3827 | 8.5113 | 7.7542 | 7.3552 | 10.625 | 10.4872 | 10.3158 | 10.1474 | 9.9413 | 9.6913 | 9.4321 | 9.1311 | 8.8811 | 6.6495 | 1.8597 | -7.4332 | 10.5602 | 10.4531 | 10.3102 | 10.1898 | 10.0316 | 9.8071 | 9.5959 | 9.35 | 9.1867 | 8.399 | 7.7357 | 7.3888
|  | HOPE AND ANCHOR PRIMARY | EE |  |  |  |  | 10.8368 | 10.7174 | 10.5705 | 10.444 | 10.2787 | 10.043 | 9.8195 | 9.5613 | 9.3827 | 8.5113 | 7.8909 | 7.396 | 10.625 | 10.4872 | 10.3158 | 10.1474 | 9.9413 | 9.6913 | 9.4321 | 9.1311 | 8.8811 | 7.1077 | 4.3985 | -0.35969 | 10.5602 | 10.4531 | 10.3102 | 10.1898 | 10.0316 | 9.8071 | 9.5959 | 9.35 | 9.1867 | 8.399 | 7.8551 | 7.4204
|  | HOPE AND ANCHOR PRIMARY | HT |  |  |  |  | 10.9021 | 10.8123 | 10.7205 | 10.6062 | 10.4858 | 10.2991 | 10.1307 | 9.9205 | 9.6991 | 8.5185 | 7.7542 | 7.3552 | 10.7801 | 10.7138 | 10.6526 | 10.5668 | 10.4781 | 10.3597 | 10.2546 | 10.1158 | 9.9658 | 9.277 | 8.8526 | 8.6219 | 10.6306 | 10.55 | 10.4643 | 10.3551 | 10.2429 | 10.0694 | 9.9112 | 9.7122 | 9.5051 | 8.4173 | 7.7357 | 7.3888
|  | HOPE AND ANCHOR PRIMARY | HE |  |  |  |  | 10.9317 | 10.8348 | 10.7481 | 10.6389 | 10.5307 | 10.3674 | 10.2215 | 10.0338 | 9.8399 | 8.9276 | 8.3307 | 8.096 | 10.7026 | 10.5811 | 10.4617 | 10.3179 | 10.1556 | 9.9536 | 9.7515 | 9.5036 | 9.2362 | 7.374 | 4.6536 | 0.016837 | 10.652 | 10.5684 | 10.4867 | 10.3857 | 10.2847 | 10.1306 | 9.9959 | 9.8214 | 9.6378 | 8.798 | 8.2735 | 8.0735
|  | HOPE AND ANCHOR PRIMARY | CF |  |  |  |  | 11.0491 | 10.9878 | 10.9327 | 10.8634 | 10.8113 | 10.7348 | 10.6511 | 10.5491 | 10.4776 | 9.8093 | 9.1909 | 8.6236 | 10.7372 | 10.6199 | 10.4903 | 10.3352 | 10.1566 | 9.925 | 9.6607 | 9.3679 | 9.0709 | 6.6495 | 1.8597 | -7.4332 | 10.749 | 10.7 | 10.651 | 10.5857 | 10.5378 | 10.4684 | 10.3867 | 10.2898 | 10.2245 | 9.601 | 9.0378 | 8.5357
LOVEDEAN GSP | HAVANT BSP | HORNDEAN PRIMARY | MINIMUM HEADROOM | SU 70271 12802 | NO | YES | 13.016 | 0.058098 | -1.0858 | -2.4266 | -3.7062 | 23.4836 | 21.6571 | 19.6816 | 17.7101 | 16.3132 | 8.4316 | 2.6744 | -0.69802 | 3.403 | 2.5622 | 1.5867 | 0.66524 | 26.3979 | 25.1754 | 23.803 | 22.3979 | 21.4601 | 16.3132 | 8.6856 | -9.2909 | 0.18361 | -0.88884 | -2.1195 | -3.296 | 23.0877 | 21.4163 | 19.5744 | 17.7367 | 16.5234 | 9.9754 | 5.0785 | 2.2193
|  | HORNDEAN PRIMARY | EE |  |  |  |  | 0.058098 | -1.0858 | -2.4266 | -3.7062 | 23.4836 | 21.6571 | 19.6816 | 17.7101 | 16.3132 | 9.5163 | 4.1408 | 0.010139 | 3.403 | 2.5622 | 1.5867 | 0.66524 | 26.3979 | 25.1754 | 23.803 | 22.3979 | 21.4601 | 16.3132 | 10.3989 | 0.83769 | 0.18361 | -0.88884 | -2.1195 | -3.296 | 23.0877 | 21.4163 | 19.5744 | 17.7367 | 16.5234 | 10.7775 | 6.3326 | 2.7867
|  | HORNDEAN PRIMARY | HT |  |  |  |  | 0.14789 | -1.0041 | -1.9705 | -3.0878 | 24.2714 | 22.5561 | 20.7754 | 18.9428 | 17.153 | 8.4316 | 2.6744 | -0.69802 | 3.7418 | 3.055 | 2.5959 | 1.9734 | 28.0173 | 27.152 | 26.202 | 25.2081 | 24.2071 | 19.752 | 17.3367 | 15.9479 | 0.3632 | -0.6766 | -1.4429 | -2.4246 | 24.154 | 22.6469 | 21.0489 | 19.3948 | 17.7632 | 9.9754 | 5.0785 | 2.2193
|  | HORNDEAN PRIMARY | HE |  |  |  |  | 0.24381 | -0.84598 | -1.7358 | -2.7654 | 24.6856 | 23.3152 | 21.8703 | 20.3908 | 18.9459 | 11.7632 | 6.3805 | 3.6846 | 3.602 | 2.8275 | 2.2959 | 1.5836 | 27.5305 | 26.6173 | 25.6071 | 24.5224 | 23.4193 | 17.3693 | 11.3346 | 2.3469 | 0.43361 | -0.55619 | -1.2429 | -2.1552 | 24.4938 | 23.2703 | 21.9428 | 20.5703 | 19.2173 | 12.7897 | 8.3316 | 6.052
|  | HORNDEAN PRIMARY | CF |  |  |  |  | 0.91626 | 0.35198 | -0.35925 | -0.62864 | 27.253 | 26.505 | 25.5846 | 24.6316 | 23.5438 | 18.8816 | 13.7265 | 8.7132 | 3.8877 | 3.3418 | 2.6663 | 2.4091 | 28.4693 | 27.6846 | 26.7734 | 25.8081 | 24.7387 | 18.4673 | 8.6856 | -9.2909 | 1.005 | 0.44687 | -0.23272 | -0.39394 | 26.6326 | 25.9438 | 25.1142 | 24.2489 | 23.2744 | 18.8326 | 14.353 | 10.1897
NURSLING GSP | WINCHESTER BSP | HOUGHTON PRIMARY | MINIMUM HEADROOM | SU 33784 31741 | NO | NO | 1.058 | 7.9949 | 7.7724 | 7.2245 | 6.951 | 5.5847 | 4.851 | 4.0939 | 1.4184 | -0.47041 | -4.6867 | -9.2684 | -14.8112 | 10.9143 | 10.6816 | 10.0622 | 9.7765 | 8.1357 | 7.3163 | 6.4684 | 3.2306 | 0.97755 | -3.7714 | -9.7051 | -17.4153 | 9.0367 | 8.8051 | 8.1561 | 7.848 | 6.1776 | 5.3133 | 4.4204 | 1.1327 | -1.1663 | -6.0867 | -11.7031 | -18.7245
|  | HOUGHTON PRIMARY | EE |  |  |  |  | 7.9949 | 7.8276 | 7.652 | 7.4633 | 6.9592 | 6.3694 | 6.0837 | 5.2337 | 4.7724 | 1.9827 | -4.6367 | -6.6531 | 10.9143 | 10.7816 | 10.6429 | 10.4918 | 9.9398 | 9.3184 | 9.0918 | 8.1531 | 7.6684 | 4.6173 | -3.8459 | -7.1735 | 9.0367 | 8.8704 | 8.6918 | 8.4939 | 7.9061 | 7.2214 | 6.9204 | 5.9133 | 5.401 | 2.2776 | -5.8806 | -8.3888
|  | HOUGHTON PRIMARY | HT |  |  |  |  | 8.0469 | 7.8235 | 7.4643 | 7.35 | 6.249 | 5.5173 | 4.7163 | 4.3684 | 3.3816 | -0.22959 | -6.1847 | -10.7439 | 10.9816 | 10.7765 | 10.4051 | 10.3327 | 9.0429 | 8.2408 | 7.3612 | 7.0561 | 5.9592 | 2.0745 | -5.1449 | -10.6418 | 9.1133 | 8.8704 | 8.4571 | 8.348 | 7.0133 | 6.15 | 5.2051 | 4.8286 | 3.6602 | -0.55714 | -7.8673 | -13.4571
|  | HOUGHTON PRIMARY | HE |  |  |  |  | 8.0837 | 7.7724 | 7.2245 | 6.951 | 5.5847 | 4.851 | 4.0939 | 1.4184 | -0.47041 | -4.6867 | -9.2684 | -14.8112 | 10.9969 | 10.6816 | 10.0622 | 9.7765 | 8.1357 | 7.3163 | 6.4684 | 3.2306 | 0.97755 | -3.7714 | -9.7051 | -17.4153 | 9.1429 | 8.8051 | 8.1561 | 7.848 | 6.1776 | 5.3133 | 4.4204 | 1.1327 | -1.1663 | -6.0867 | -11.7031 | -18.7245
|  | HOUGHTON PRIMARY | CF |  |  |  |  | 8.1337 | 8.0459 | 7.9061 | 7.6694 | 7.3857 | 7.0806 | 6.7929 | 6.4867 | 6.1398 | 3.7031 | 0.77245 | -1.6357 | 11.0276 | 10.9612 | 10.852 | 10.6051 | 10.299 | 9.95 | 9.6316 | 9.2929 | 8.898 | 5.9765 | 1.9449 | -2.4265 | 9.1888 | 9.1102 | 8.9837 | 8.7133 | 8.3908 | 8.0388 | 7.7102 | 7.3582 | 6.9643 | 4.1041 | 0.65816 | -2.2245
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | HOUNDMILLS PRIMARY | MINIMUM HEADROOM | SU 62187 52886 | NO | NO | 27.767 | 1.3935 | 0.62 | -0.42796 | -1.5524 | -2.8943 | -4.1831 | -5.8096 | -7.4127 | -8.88 | -15.1637 | -17.5871 | -18.1147 | 1.9527 | 1.4088 | 0.69857 | -0.063673 | -1.0188 | -1.8586 | -2.93 | -3.9606 | -4.8565 | -9.428 | -11.1688 | -14.4627 | 1.4047 | 0.72306 | -0.29837 | -1.429 | -2.8331 | -3.9086 | -5.3086 | -6.6912 | -7.929 | -13.9167 | -16.2892 | -16.781
|  | HOUNDMILLS PRIMARY | EE |  |  |  |  | 1.3935 | 0.62 | -0.42796 | -1.5524 | -2.8943 | -4.1831 | -5.8096 | -7.4127 | -8.88 | -15.1157 | -16.8096 | -17.9708 | 1.9527 | 1.4088 | 0.69857 | -0.063673 | -1.0188 | -1.8586 | -2.93 | -3.9606 | -4.8565 | -7.9647 | -9.5371 | -11.8351 | 1.4047 | 0.72306 | -0.29837 | -1.429 | -2.8331 | -3.9086 | -5.3086 | -6.6912 | -7.929 | -13.1555 | -14.6392 | -15.6371
|  | HOUNDMILLS PRIMARY | HT |  |  |  |  | 1.9659 | 1.3782 | 0.55367 | -0.74837 | -2.1545 | -3.5616 | -5.0494 | -6.5647 | -7.7922 | -14.6086 | -16.8045 | -17.8596 | 2.4067 | 2.0169 | 1.4863 | 0.78531 | 0.084286 | -0.64429 | -1.4402 | -2.28 | -3.0392 | -6.7667 | -8.0708 | -8.4269 | 1.6914 | 1.12 | 0.21592 | -0.91673 | -2.1035 | -3.2861 | -4.5392 | -5.8218 | -6.8167 | -12.578 | -14.5524 | -15.4616
|  | HOUNDMILLS PRIMARY | HE |  |  |  |  | 1.7669 | 1.0853 | 0.14449 | -0.8851 | -2.3076 | -3.7402 | -5.2729 | -6.8473 | -8.1524 | -15.1637 | -17.5871 | -18.1147 | 2.2435 | 1.77 | 1.1435 | 0.45469 | -0.43714 | -1.3178 | -2.3535 | -3.4504 | -4.48 | -9.428 | -11.1688 | -12.2586 | 1.62 | 1.019 | 0.075102 | -0.96673 | -2.2637 | -3.481 | -4.7984 | -6.1473 | -7.231 | -13.9167 | -16.2892 | -16.781
|  | HOUNDMILLS PRIMARY | CF |  |  |  |  | 2.27 | 1.9618 | 1.5588 | 1.0455 | 0.37408 | -0.46469 | -1.6729 | -2.9616 | -4.279 | -10.8627 | -13.7402 | -16.2565 | 2.5118 | 2.3435 | 2.0914 | 1.7312 | 1.2771 | 0.63224 | -0.16571 | -0.98816 | -1.831 | -6.1831 | -9.5922 | -14.4627 | 1.9343 | 1.6986 | 1.369 | 0.90776 | 0.22204 | -0.62898 | -1.6698 | -2.7371 | -3.83 | -9.2994 | -12.5453 | -15.0239
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | HUNGERFORD PRIMARY | MINIMUM HEADROOM | SU 34066 68957 | NO | NO | 1.799 | 6.5949 | 6.4663 | 6.3082 | 6.1398 | 5.949 | 5.6327 | 5.5112 | 5.1704 | 4.8949 | 3.3806 | 2.2286 | 1.55 | 9.2449 | 9.1735 | 9.0602 | 8.9378 | 8.8 | 8.6286 | 8.5184 | 8.3357 | 8.1408 | 7.0612 | 5.7408 | 2.4908 | 7.0143 | 6.8724 | 6.6867 | 6.5214 | 6.3112 | 5.9816 | 5.8857 | 5.5694 | 5.3184 | 3.9561 | 2.9367 | 2.3449
|  | HUNGERFORD PRIMARY | EE |  |  |  |  | 6.5949 | 6.4663 | 6.3082 | 6.1398 | 5.949 | 5.6327 | 5.5112 | 5.1704 | 4.898 | 3.3806 | 2.3806 | 1.6796 | 9.2449 | 9.1735 | 9.0602 | 8.9378 | 8.8 | 8.6286 | 8.5184 | 8.3357 | 8.1408 | 7.0612 | 5.9367 | 4.2561 | 7.0143 | 6.8724 | 6.6867 | 6.5214 | 6.3112 | 5.9816 | 5.8857 | 5.5694 | 5.3184 | 3.9561 | 3.0786 | 2.4643
|  | HUNGERFORD PRIMARY | HT |  |  |  |  | 6.7 | 6.5939 | 6.4827 | 6.348 | 6.1959 | 5.9439 | 5.6051 | 5.2582 | 4.8949 | 3.3918 | 2.2286 | 1.55 | 9.3122 | 9.2643 | 9.2041 | 9.1122 | 9.0051 | 8.8765 | 8.7122 | 8.5398 | 8.3582 | 7.6602 | 7.2204 | 6.9449 | 7.1235 | 6.9929 | 6.8704 | 6.7214 | 6.552 | 6.2949 | 5.9847 | 5.6612 | 5.3245 | 3.9724 | 2.9367 | 2.3449
|  | HUNGERFORD PRIMARY | HE |  |  |  |  | 6.6959 | 6.5857 | 6.4735 | 6.3378 | 6.1816 | 5.9816 | 5.7296 | 5.4398 | 5.1255 | 3.7745 | 2.8112 | 2.3806 | 9.3041 | 9.252 | 9.1908 | 9.0969 | 8.9847 | 8.851 | 8.6765 | 8.4959 | 8.3 | 7.3306 | 6.1714 | 4.6082 | 7.1306 | 7.0071 | 6.8918 | 6.7531 | 6.5949 | 6.3796 | 6.1071 | 5.8276 | 5.5327 | 4.3327 | 3.4714 | 3.0969
|  | HUNGERFORD PRIMARY | CF |  |  |  |  | 6.798 | 6.7418 | 6.6755 | 6.6071 | 6.5245 | 6.4276 | 6.301 | 6.1704 | 6.0204 | 5.1612 | 4.1112 | 3.1204 | 9.3378 | 9.3031 | 9.2673 | 9.2286 | 9.1765 | 9.1173 | 9.0408 | 8.9194 | 8.7286 | 7.6582 | 5.7408 | 2.4908 | 7.2071 | 7.1367 | 7.052 | 6.9837 | 6.8867 | 6.7786 | 6.6439 | 6.5378 | 6.3918 | 5.6745 | 4.7092 | 3.7786
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | HUNSTON PRIMARY | MINIMUM HEADROOM | SU 86949 02632 | NO | YES | 12.714 | 8.9406 | 8.5671 | 8.1365 | 7.6273 | 7.1161 | 6.6355 | 5.9334 | 5.2488 | 4.6498 | 1.6477 | -0.089004 | -0.79104 | 11.8579 | 11.6528 | 11.4243 | 11.0314 | 10.6416 | 10.4834 | 9.9967 | 9.5028 | 9.1243 | 7.2059 | 5.4385 | 0.62936 | 9.1263 | 8.7732 | 8.3671 | 7.8885 | 7.4059 | 6.9528 | 6.2875 | 5.6406 | 5.0773 | 2.3528 | 0.95385 | 0.44467
|  | HUNSTON PRIMARY | EE |  |  |  |  | 8.9406 | 8.5671 | 8.1365 | 7.6273 | 7.1161 | 6.6355 | 5.9334 | 5.2488 | 4.6498 | 1.962 | 0.75998 | -0.15125 | 11.8579 | 11.6528 | 11.4243 | 11.0314 | 10.6416 | 10.4834 | 9.9967 | 9.5028 | 9.1243 | 7.2059 | 5.5416 | 3.059 | 9.1263 | 8.7732 | 8.3671 | 7.8885 | 7.4059 | 6.9528 | 6.2875 | 5.6406 | 5.0773 | 2.8488 | 2.0569 | 1.2702
|  | HUNSTON PRIMARY | HT |  |  |  |  | 9.2161 | 8.9294 | 8.6069 | 8.2059 | 7.812 | 7.3283 | 6.7528 | 6.1375 | 5.61 | 2.2569 | 0.53242 | -0.33696 | 12.0273 | 11.8783 | 11.7151 | 11.51 | 11.3151 | 11.0018 | 10.6202 | 10.2079 | 10.113 | 8.1875 | 7.1947 | 6.7273 | 9.3947 | 9.1243 | 8.8243 | 8.4518 | 8.0783 | 7.6232 | 7.0814 | 6.4967 | 6.0253 | 3.2334 | 1.9018 | 1.1651
|  | HUNSTON PRIMARY | HE |  |  |  |  | 9.163 | 8.8488 | 8.4947 | 8.0559 | 7.6181 | 7.0906 | 6.4406 | 5.7457 | 5.1447 | 1.6477 | -0.089004 | -0.79104 | 11.9865 | 11.8192 | 11.6314 | 11.4028 | 11.1702 | 10.8151 | 10.3977 | 9.9467 | 9.7334 | 7.3702 | 5.6732 | 3.3641 | 9.3385 | 9.0457 | 8.7141 | 8.3059 | 7.8926 | 7.3896 | 6.7732 | 6.112 | 5.5467 | 2.3528 | 0.95385 | 0.44467
|  | HUNSTON PRIMARY | CF |  |  |  |  | 9.4324 | 9.2467 | 9.0375 | 8.7743 | 8.5345 | 8.2773 | 7.9436 | 7.5661 | 7.1508 | 4.6916 | 2.3814 | 0.49977 | 12.1151 | 12.0069 | 11.8865 | 11.7304 | 11.5079 | 11.2559 | 10.9967 | 10.6732 | 10.3273 | 8.3794 | 5.4385 | 0.62936 | 9.5947 | 9.4232 | 9.2294 | 8.9845 | 8.759 | 8.511 | 8.1957 | 7.8355 | 7.4385 | 5.1079 | 2.9243 | 1.3253
MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT PRIMARY | MINIMUM HEADROOM | SU 39384 52476 | NO | NO | 1.804 | 1.6507 | 1.5211 | 1.4191 | 1.2701 | 1.113 | 0.97114 | 0.73645 | 0.49257 | 0.41502 | -0.12069 | -0.30437 | -0.47784 | 2.6191 | 2.5262 | 2.4507 | 2.3375 | 2.214 | 2.1079 | 1.9416 | 1.7681 | 1.6905 | 1.3242 | 0.87931 | -0.18906 | 1.5916 | 1.4599 | 1.3569 | 1.2007 | 1.0334 | 0.88747 | 0.64767 | 0.4089 | 0.33849 | -0.081918 | -0.24518 | -0.40845
|  | HURSTBOURNE TARRANT PRIMARY | EE |  |  |  |  | 1.6507 | 1.5211 | 1.4191 | 1.2701 | 1.113 | 0.97114 | 0.73645 | 0.49257 | 0.41502 | -0.12069 | -0.30437 | -0.39518 | 2.6191 | 2.5262 | 2.4507 | 2.3375 | 2.214 | 2.1079 | 1.9416 | 1.7681 | 1.6905 | 1.3242 | 1.0191 | 0.50278 | 1.5916 | 1.4599 | 1.3569 | 1.2007 | 1.0334 | 0.88747 | 0.64767 | 0.4089 | 0.33849 | -0.081918 | -0.24518 | -0.3309
|  | HURSTBOURNE TARRANT PRIMARY | HT |  |  |  |  | 1.7344 | 1.6497 | 1.5436 | 1.4395 | 1.3181 | 1.2089 | 1.0395 | 0.864 | 0.73849 | -0.01049 | -0.28702 | -0.47784 | 2.6997 | 2.6497 | 2.5844 | 2.515 | 2.4313 | 2.366 | 2.2558 | 2.1344 | 2.0579 | 1.5762 | 1.4232 | 1.3283 | 1.6834 | 1.6058 | 1.5058 | 1.4058 | 1.2885 | 1.1885 | 1.0262 | 0.85278 | 0.73849 | 0.020122 | -0.23906 | -0.40845
|  | HURSTBOURNE TARRANT PRIMARY | HE |  |  |  |  | 1.7324 | 1.6497 | 1.5436 | 1.4446 | 1.3262 | 1.2252 | 1.0609 | 0.88951 | 0.76808 | -0.047224 | -0.22682 | -0.30335 | 2.6895 | 2.6354 | 2.563 | 2.4916 | 2.3997 | 2.3313 | 2.216 | 2.0864 | 1.9997 | 1.3946 | 1.0762 | 0.57522 | 1.6803 | 1.6058 | 1.5069 | 1.4109 | 1.2967 | 1.2038 | 1.0467 | 0.87931 | 0.77216 | 0.00073469 | -0.16355 | -0.2309
|  | HURSTBOURNE TARRANT PRIMARY | CF |  |  |  |  | 1.7691 | 1.6834 | 1.6232 | 1.5385 | 1.4436 | 1.3426 | 1.2722 | 1.1609 | 1.0436 | 0.44869 | 0.051755 | -0.24008 | 2.713 | 2.6467 | 2.6038 | 2.5436 | 2.466 | 2.3813 | 2.3211 | 2.2201 | 2.1181 | 1.5293 | 0.87931 | -0.18906 | 1.713 | 1.6313 | 1.5762 | 1.4946 | 1.4028 | 1.3038 | 1.2385 | 1.1262 | 1.0079 | 0.43747 | 0.071143 | -0.17478
EALING GSP |  | IRONBRIDGE PRIMARY | MINIMUM HEADROOM | TQ 14226 80171 | NO | NO | 15.775 | 4.3445 | 3.3271 | 2.2261 | 0.77304 | -1.0372 | -2.9749 | -4.9351 | -6.9647 | -8.6361 | -15.4943 | -19.8953 | -21.8412 | 6.719 | 5.9373 | 5.2455 | 4.2241 | 2.9322 | 1.5986 | 0.13631 | -1.381 | -2.6014 | -8.3402 | -14.9912 | -32.6668 | 4.3261 | 3.4149 | 2.4363 | 1.1343 | -0.52798 | -2.3127 | -4.1453 | -6.0382 | -7.5647 | -13.7076 | -17.5902 | -19.2739
|  | IRONBRIDGE PRIMARY | EE |  |  |  |  | 4.3445 | 3.3271 | 2.2261 | 0.77304 | -1.0372 | -2.9749 | -4.9351 | -6.9647 | -8.6361 | -15.4943 | -19.2912 | -21.2392 | 6.719 | 5.9373 | 5.2455 | 4.2241 | 2.9322 | 1.5986 | 0.13631 | -1.381 | -2.6014 | -8.3402 | -13.8423 | -22.4545 | 4.3261 | 3.4149 | 2.4363 | 1.1343 | -0.52798 | -2.3127 | -4.1453 | -6.0382 | -7.5647 | -13.7076 | -17.0392 | -18.7729
|  | IRONBRIDGE PRIMARY | HT |  |  |  |  | 4.8496 | 3.9149 | 2.5679 | 1.0057 | -0.49329 | -1.8321 | -3.4157 | -5.031 | -6.6688 | -14.7157 | -19.8953 | -21.8412 | 7.3128 | 6.7465 | 6.0149 | 5.0567 | 4.1424 | 3.5332 | 2.5812 | 1.5863 | 0.58937 | -3.9902 | -6.6382 | -7.5117 | 4.8139 | 4.0037 | 2.8465 | 1.4332 | 0.06998 | -1.1076 | -2.5688 | -4.0617 | -5.5586 | -12.9147 | -17.5902 | -19.2739
|  | IRONBRIDGE PRIMARY | HE |  |  |  |  | 4.919 | 4.1598 | 3.0159 | 1.8159 | 0.27406 | -0.9688 | -2.4545 | -4.0617 | -5.6759 | -12.4392 | -15.9923 | -17.1096 | 7.1934 | 6.6241 | 5.8965 | 5.0853 | 4.0159 | 3.27 | 2.1873 | 1.0098 | -0.20247 | -6.2892 | -11.8861 | -20.1545 | 4.8588 | 4.1894 | 3.2016 | 2.1424 | 0.74243 | -0.33614 | -1.7025 | -3.179 | -4.6535 | -10.8106 | -13.98 | -14.9382
|  | IRONBRIDGE PRIMARY | CF |  |  |  |  | 5.5128 | 5.22 | 4.5486 | 4.0404 | 3.4343 | 2.7292 | 1.9526 | 1.5169 | 0.64039 | -6.028 | -10.4698 | -14.6361 | 7.4679 | 7.119 | 6.5588 | 6.0618 | 5.4281 | 4.6465 | 3.7496 | 3.1516 | 2.1353 | -5.2137 | -14.9912 | -32.6668 | 5.3904 | 5.123 | 4.5506 | 4.0986 | 3.5547 | 2.9118 | 2.1945 | 1.7577 | 0.94651 | -5.0219 | -9.0953 | -12.828
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | JAYS CLOSE PRIMARY | MINIMUM HEADROOM | SU 63055 50105 | NO | NO | 17.37 | 6.3081 | 5.8684 | 5.3765 | 5.2306 | 4.7184 | 3.8459 | 2.8612 | 1.8796 | 1.1755 | -2.7388 | -5.8623 | -7.6521 | 7.6173 | 7.2449 | 6.8184 | 6.6857 | 6.2541 | 5.6408 | 4.9296 | 4.2071 | 3.6969 | 0.92039 | -2.1806 | -10.2265 | 6.0459 | 5.6286 | 5.1684 | 5.0367 | 4.5581 | 3.7479 | 2.8337 | 1.9275 | 1.2602 | -2.1868 | -4.9714 | -6.5531
|  | JAYS CLOSE PRIMARY | EE |  |  |  |  | 6.3081 | 5.8684 | 5.3765 | 5.2306 | 4.7184 | 3.8459 | 2.8612 | 1.8796 | 1.1755 | -2.5602 | -5.2714 | -7.3663 | 7.6173 | 7.2449 | 6.8184 | 6.6857 | 6.2541 | 5.6408 | 4.9296 | 4.2071 | 3.6969 | 0.92039 | -1.9235 | -6.1449 | 6.0459 | 5.6286 | 5.1684 | 5.0367 | 4.5581 | 3.7479 | 2.8337 | 1.9275 | 1.2602 | -2.0663 | -4.45 | -6.3061
|  | JAYS CLOSE PRIMARY | HT |  |  |  |  | 6.5469 | 6.1898 | 5.849 | 5.4418 | 4.9796 | 4.4847 | 3.6684 | 2.8255 | 1.9663 | -2.7388 | -5.8623 | -7.6521 | 7.9265 | 7.6877 | 7.4571 | 7.1745 | 6.8418 | 6.652 | 6.1837 | 5.6898 | 5.1796 | 2.6673 | 1.2357 | 0.49386 | 6.2867 | 5.9561 | 5.6367 | 5.2581 | 4.8255 | 4.3969 | 3.653 | 2.8806 | 2.0908 | -2.1868 | -4.9714 | -6.5531
|  | JAYS CLOSE PRIMARY | HE |  |  |  |  | 6.5775 | 6.2479 | 5.9398 | 5.5663 | 5.1592 | 4.7908 | 4.103 | 3.3888 | 2.6541 | -1.299 | -4.0133 | -5.2623 | 7.8632 | 7.5969 | 7.3377 | 7.0143 | 6.6551 | 6.4408 | 5.9388 | 5.4 | 4.8326 | 1.6561 | -1.2684 | -5.1796 | 6.3112 | 6.0051 | 5.7184 | 5.3694 | 4.9837 | 4.6663 | 4.0347 | 3.3745 | 2.6949 | -0.91226 | -3.3572 | -4.4714
|  | JAYS CLOSE PRIMARY | CF |  |  |  |  | 6.8357 | 6.6755 | 6.4796 | 6.2979 | 6.0684 | 5.801 | 5.4592 | 5.4581 | 5.1449 | 2.5561 | -0.14185 | -2.7745 | 7.9786 | 7.8 | 7.5806 | 7.3581 | 7.0632 | 6.7163 | 6.2949 | 6.1479 | 5.7184 | 2.5724 | -2.1806 | -10.2265 | 6.551 | 6.3969 | 6.2071 | 6.0408 | 5.8194 | 5.5643 | 5.2469 | 5.252 | 4.9561 | 2.549 | 0.078555 | -2.2408
MINETY GSP | CIRENCESTER BSP | KEMBLE RAF PRIMARY | MINIMUM HEADROOM | ST 96064 96012 | YES | NO | 0.707 | 9.5194 | 9.502 | 9.4541 | 9.402 | 9.3429 | 9.2745 | 9.1898 | 9.1071 | 9.0316 | 8.7112 | 8.6041 | 8.552 | 8.9765 | 8.9663 | 8.9306 | 8.8898 | 8.8439 | 8.7918 | 8.7265 | 8.6612 | 8.6 | 8.3459 | 8.2602 | 8.2163 | 9.2112 | 9.1929 | 9.149 | 9.0959 | 9.0378 | 8.9704 | 8.8837 | 8.802 | 8.7235 | 8.4082 | 8.298 | 8.248
|  | KEMBLE RAF PRIMARY | EE |  |  |  |  | 9.5194 | 9.502 | 9.4541 | 9.402 | 9.3429 | 9.2745 | 9.1898 | 9.1071 | 9.0316 | 8.7173 | 8.6327 | 8.6265 | 8.9765 | 8.9663 | 8.9306 | 8.8898 | 8.8439 | 8.7918 | 8.7265 | 8.6612 | 8.6 | 8.3469 | 8.2816 | 8.2765 | 9.2112 | 9.1929 | 9.149 | 9.0959 | 9.0378 | 8.9704 | 8.8837 | 8.802 | 8.7235 | 8.4082 | 8.3255 | 8.3204
|  | KEMBLE RAF PRIMARY | HT |  |  |  |  | 9.552 | 9.5163 | 9.4959 | 9.4561 | 9.4061 | 9.3469 | 9.2745 | 9.1949 | 9.1173 | 8.75 | 8.6041 | 8.5602 | 9.0031 | 8.9735 | 8.9633 | 8.9316 | 8.8929 | 8.8469 | 8.7908 | 8.7286 | 8.6653 | 8.3724 | 8.2602 | 8.2265 | 9.2418 | 9.2051 | 9.1878 | 9.1469 | 9.0959 | 9.0367 | 8.9622 | 8.8837 | 8.8041 | 8.4378 | 8.298 | 8.2561
|  | KEMBLE RAF PRIMARY | HE |  |  |  |  | 9.5531 | 9.5184 | 9.498 | 9.4571 | 9.4071 | 9.3469 | 9.2704 | 9.1867 | 9.099 | 8.7112 | 8.6092 | 8.5643 | 9.0051 | 8.9765 | 8.9643 | 8.9327 | 8.8939 | 8.848 | 8.7878 | 8.7245 | 8.6541 | 8.3459 | 8.2653 | 8.2316 | 9.2449 | 9.2092 | 9.1908 | 9.15 | 9.099 | 9.0398 | 8.9622 | 8.8796 | 8.7918 | 8.4082 | 8.3092 | 8.2694
|  | KEMBLE RAF PRIMARY | CF |  |  |  |  | 9.5918 | 9.5714 | 9.5469 | 9.5255 | 9.5143 | 9.4888 | 9.448 | 9.4031 | 9.349 | 9.0418 | 8.7571 | 8.552 | 9.0357 | 9.0184 | 8.998 | 8.9816 | 8.9765 | 8.9561 | 8.9255 | 8.8888 | 8.849 | 8.6082 | 8.3796 | 8.2163 | 9.2816 | 9.2622 | 9.2378 | 9.2163 | 9.2061 | 9.1816 | 9.1398 | 9.0949 | 9.0429 | 8.7388 | 8.451 | 8.248
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | KENNINGTON PRIMARY | MINIMUM HEADROOM | SP 52881 01094 | YES | NO | 0.508 | 3.0579 | 2.8314 | 2.6283 | 2.3793 | 2.1181 | 1.761 | 1.7253 | 1.3722 | 1.0089 | -0.19515 | -1.2013 | -1.8054 | 4.3832 | 4.226 | 4.0811 | 3.9026 | 3.6995 | 3.4362 | 3.4821 | 3.2434 | 3.0934 | 2.1985 | 0.9301 | -1.9566 | 3.1612 | 2.95 | 2.7592 | 2.5143 | 2.2551 | 1.902 | 1.9388 | 1.6143 | 1.2724 | 0.21224 | -0.63265 | -1.1194
|  | KENNINGTON PRIMARY | EE |  |  |  |  | 3.0579 | 2.8314 | 2.6283 | 2.3793 | 2.1181 | 1.761 | 1.7334 | 1.4048 | 1.1783 | -0.034949 | -0.96352 | -1.6615 | 4.3832 | 4.226 | 4.0811 | 3.9026 | 3.6995 | 3.4362 | 3.4821 | 3.2434 | 3.0934 | 2.1985 | 1.1719 | -0.36173 | 3.1612 | 2.95 | 2.7592 | 2.5143 | 2.2551 | 1.902 | 1.9388 | 1.6224 | 1.4245 | 0.35408 | -0.42857 | -0.99694
|  | KENNINGTON PRIMARY | HT |  |  |  |  | 3.1344 | 2.9416 | 2.7732 | 2.5651 | 2.3446 | 2.0651 | 1.7253 | 1.3722 | 1.0089 | -0.19515 | -1.2013 | -1.8054 | 4.4842 | 4.376 | 4.2852 | 4.1679 | 4.0362 | 3.8944 | 3.7046 | 3.4903 | 3.2699 | 2.775 | 2.3495 | 2.0862 | 3.2398 | 3.0633 | 2.9092 | 2.7173 | 2.5122 | 2.2582 | 1.9449 | 1.6143 | 1.2724 | 0.21224 | -0.63265 | -1.1194
|  | KENNINGTON PRIMARY | HE |  |  |  |  | 3.1559 | 2.9763 | 2.8253 | 2.6304 | 2.4273 | 2.213 | 1.9334 | 1.6436 | 1.3436 | 0.37423 | -0.51964 | -1.0186 | 4.4617 | 4.3413 | 4.2372 | 4.1026 | 3.9566 | 3.8107 | 3.6087 | 3.3862 | 3.1495 | 2.3821 | 1.3556 | -0.10051 | 3.2582 | 3.0959 | 2.9541 | 2.7745 | 2.5847 | 2.3888 | 2.1296 | 1.8439 | 1.55 | 0.71939 | -0.045918 | -0.44592
|  | KENNINGTON PRIMARY | CF |  |  |  |  | 3.2691 | 3.1497 | 3.0202 | 2.9253 | 2.7916 | 2.6702 | 2.5732 | 2.4293 | 2.2804 | 1.6589 | 0.72526 | -0.20128 | 4.5117 | 4.4148 | 4.3046 | 4.2199 | 4.0964 | 3.9587 | 3.8342 | 3.6679 | 3.4842 | 2.6036 | 0.9301 | -1.9566 | 3.3622 | 3.251 | 3.1306 | 3.0429 | 2.9173 | 2.8041 | 2.7071 | 2.5561 | 2.399 | 1.8449 | 1.0245 | 0.21531
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | KENTWOOD HILL PRIMARY | MINIMUM HEADROOM | SU 67102 74048 | NO | NO | 0.914 | 7.848 | 7.1663 | 6.4265 | 5.6133 | 4.6163 | 2.9031 | 1.1582 | -0.58163 | -1.8071 | -9.2531 | -14.9837 | -18.2163 | 11.3353 | 10.7373 | 10.0792 | 9.3394 | 8.4782 | 7.2884 | 5.9833 | 4.6618 | 3.7802 | -1.4576 | -10.0484 | -28.9249 | 7.9896 | 7.3192 | 6.5814 | 5.7682 | 4.7947 | 3.2131 | 1.5437 | -0.12469 | -1.2033 | -7.3982 | -12.2655 | -15.1492
|  | KENTWOOD HILL PRIMARY | EE |  |  |  |  | 7.848 | 7.1663 | 6.4265 | 5.6133 | 4.6163 | 2.9031 | 1.1582 | -0.58163 | -1.8071 | -8.3755 | -13.752 | -17.8388 | 11.3353 | 10.7373 | 10.0792 | 9.3394 | 8.4782 | 7.2884 | 5.9833 | 4.6618 | 3.7802 | -1.4576 | -7.8831 | -17.9116 | 7.9896 | 7.3192 | 6.5814 | 5.7682 | 4.7947 | 3.2131 | 1.5437 | -0.12469 | -1.2033 | -6.7441 | -11.1859 | -14.84
|  | KENTWOOD HILL PRIMARY | HT |  |  |  |  | 7.9378 | 7.2929 | 6.9816 | 6.3449 | 5.5122 | 3.9235 | 2.3684 | 0.76939 | -0.87143 | -9.2531 | -14.9837 | -18.2163 | 11.6822 | 11.2333 | 11.122 | 10.7037 | 10.1833 | 9.3731 | 8.5231 | 7.6384 | 6.719 | 2.4435 | 0.075102 | -1.2106 | 8.1682 | 7.5263 | 7.2957 | 6.6773 | 5.9008 | 4.4886 | 3.0702 | 1.6029 | 0.089592 | -7.3982 | -12.2655 | -15.1492
|  | KENTWOOD HILL PRIMARY | HE |  |  |  |  | 8.052 | 7.4806 | 7.2459 | 6.6806 | 5.9316 | 4.6939 | 3.4827 | 2.2347 | 0.94694 | -5.9122 | -11.1735 | -13.8041 | 11.5363 | 11.0027 | 10.8047 | 10.2822 | 9.6424 | 8.7761 | 7.8486 | 6.8649 | 5.8139 | -0.27694 | -6.7127 | -16.1637 | 8.2447 | 7.6569 | 7.5049 | 6.958 | 6.2549 | 5.1355 | 4.0039 | 2.8273 | 1.612 | -4.592 | -8.8716 | -11.1767
|  | KENTWOOD HILL PRIMARY | CF |  |  |  |  | 8.55 | 8.2265 | 7.8561 | 7.8653 | 7.4071 | 6.8959 | 6.4235 | 5.9143 | 5.3837 | 0.90204 | -4.1622 | -8.951 | 11.7363 | 11.3006 | 10.8343 | 10.6904 | 10.1067 | 9.4129 | 8.6588 | 7.8527 | 6.9833 | 0.48122 | -10.0484 | -28.9249 | 8.659 | 8.2865 | 7.8947 | 7.9692 | 7.5324 | 7.0457 | 6.558 | 6.0304 | 5.4763 | 1.2253 | -3.1849 | -7.1665
COWLEY GSP | YARNTON BSP | KIDDINGTON PRIMARY | MINIMUM HEADROOM | SP 43362 24301 | NO | YES | 9.195 | 8.0875 | 8.0028 | 7.8845 | 7.7385 | 7.5875 | 7.3018 | 6.9712 | 6.6396 | 6.4681 | 5.913 | 5.3018 | 4.8487 | 8.8722 | 8.7702 | 8.6253 | 8.4691 | 8.3436 | 8.1304 | 7.8875 | 7.6324 | 7.5069 | 7.1936 | 6.4365 | 4.311 | 7.1151 | 6.9916 | 6.8253 | 6.6294 | 6.4773 | 6.2049 | 5.8885 | 5.5681 | 5.4079 | 5.0406 | 4.5436 | 4.1987
|  | KIDDINGTON PRIMARY | EE |  |  |  |  | 8.0875 | 8.0028 | 7.8845 | 7.7385 | 7.5875 | 7.3018 | 6.9712 | 6.6396 | 6.4681 | 5.913 | 5.3436 | 4.9732 | 8.8722 | 8.7702 | 8.6253 | 8.4691 | 8.3436 | 8.1304 | 7.8875 | 7.6324 | 7.5069 | 7.2691 | 6.6436 | 5.6089 | 7.1151 | 6.9916 | 6.8253 | 6.6294 | 6.4773 | 6.2049 | 5.8885 | 5.5681 | 5.4079 | 5.0406 | 4.6059 | 4.3049
|  | KIDDINGTON PRIMARY | HT |  |  |  |  | 8.1528 | 8.0845 | 7.9814 | 7.8855 | 7.76 | 7.5467 | 7.3508 | 7.1202 | 6.8855 | 5.9814 | 5.3018 | 4.8487 | 8.9804 | 8.9089 | 8.8222 | 8.7569 | 8.6498 | 8.5028 | 8.3794 | 8.2089 | 8.0334 | 7.6957 | 7.4089 | 7.2314 | 7.213 | 7.114 | 6.9865 | 6.8896 | 6.7487 | 6.5304 | 6.3345 | 6.0916 | 5.8375 | 5.0957 | 4.5436 | 4.1987
|  | KIDDINGTON PRIMARY | HE |  |  |  |  | 8.1487 | 8.0814 | 7.9957 | 7.9018 | 7.7824 | 7.5947 | 7.4222 | 7.2181 | 7.0079 | 6.0906 | 5.5273 | 5.2538 | 8.961 | 8.8906 | 8.7896 | 8.711 | 8.5947 | 8.4426 | 8.3089 | 8.1253 | 7.9334 | 7.3875 | 6.7538 | 5.7406 | 7.2151 | 7.1253 | 7.0008 | 6.9089 | 6.7712 | 6.5783 | 6.4028 | 6.1814 | 5.9498 | 5.2375 | 4.7865 | 4.5528
|  | KIDDINGTON PRIMARY | CF |  |  |  |  | 8.2089 | 8.1671 | 8.1079 | 8.0253 | 7.9569 | 7.862 | 7.7518 | 7.6355 | 7.5477 | 6.661 | 6.3467 | 5.6691 | 8.9967 | 8.9314 | 8.8579 | 8.7651 | 8.6926 | 8.5794 | 8.4406 | 8.2936 | 8.1845 | 7.1936 | 6.4365 | 4.311 | 7.2722 | 7.2028 | 7.1212 | 7.0242 | 6.961 | 6.8518 | 6.7242 | 6.5753 | 6.4814 | 5.6008 | 5.4059 | 4.8671
BRAMLEY (BASI) GSP | READING BSP | KIDMORE END PRIMARY | MINIMUM HEADROOM | SU 69953 78205 | NO | YES | 0.615 | 14.7378 | 14.4888 | 14.0653 | 13.7276 | 13.7327 | 13.2765 | 12.7755 | 12.2735 | 11.9245 | 9.8694 | 8.4327 | 7.6184 | 15.8222 | 15.6069 | 15.2784 | 14.9661 | 15.0539 | 14.7182 | 14.3345 | 13.9376 | 13.6988 | 12.1947 | 9.3406 | 3.3682 | 14.5208 | 14.2759 | 13.879 | 13.5331 | 13.5902 | 13.1606 | 12.681 | 12.1984 | 11.8933 | 10.1494 | 8.8576 | 8.0851
|  | KIDMORE END PRIMARY | EE |  |  |  |  | 14.7378 | 14.4888 | 14.0653 | 13.7276 | 13.7327 | 13.2765 | 12.7755 | 12.2735 | 11.9245 | 10.0398 | 8.7163 | 7.7847 | 15.8222 | 15.6069 | 15.2784 | 14.9661 | 15.0539 | 14.7182 | 14.3345 | 13.9376 | 13.6988 | 12.1947 | 10.261 | 7.1508 | 14.5208 | 14.2759 | 13.879 | 13.5331 | 13.5902 | 13.1606 | 12.681 | 12.1984 | 11.8933 | 10.2963 | 9.1178 | 8.229
|  | KIDMORE END PRIMARY | HT |  |  |  |  | 14.8714 | 14.6684 | 14.302 | 14.0724 | 13.7847 | 13.3071 | 12.7888 | 12.6459 | 12.1684 | 9.8694 | 8.4327 | 7.6184 | 16.0253 | 15.8988 | 15.6804 | 15.5345 | 15.3304 | 15.0447 | 14.7202 | 14.8335 | 14.559 | 13.3733 | 12.7916 | 12.4386 | 14.682 | 14.4871 | 14.1576 | 13.9402 | 13.6586 | 13.2157 | 12.7259 | 12.6729 | 12.231 | 10.1494 | 8.8576 | 8.0851
|  | KIDMORE END PRIMARY | HE |  |  |  |  | 14.8939 | 14.7082 | 14.3582 | 14.1459 | 13.8816 | 13.4939 | 13.399 | 13.0224 | 12.6398 | 10.6041 | 9.3122 | 8.6867 | 15.9722 | 15.8161 | 15.5682 | 15.3947 | 15.1529 | 14.8478 | 14.8651 | 14.5702 | 14.2569 | 12.4345 | 10.5151 | 7.5284 | 14.6963 | 14.5198 | 14.2014 | 14.0004 | 13.7392 | 13.3698 | 13.3392 | 12.9851 | 12.6208 | 10.781 | 9.6647 | 9.078
|  | KIDMORE END PRIMARY | CF |  |  |  |  | 15.0367 | 14.9184 | 14.6561 | 14.4867 | 14.349 | 14.1714 | 13.9561 | 13.7245 | 13.85 | 12.5153 | 11.1041 | 9.8092 | 16.0304 | 15.8957 | 15.6804 | 15.4967 | 15.3355 | 15.0906 | 14.7988 | 14.4835 | 14.5416 | 12.5835 | 9.3406 | 3.3682 | 14.828 | 14.7096 | 14.4739 | 14.3024 | 14.1739 | 13.9882 | 13.7678 | 13.5127 | 13.6994 | 12.4096 | 11.1739 | 10.0922
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | KINGS RIDE PRIMARY | MINIMUM HEADROOM | SU 87551 61530 | NO | NO | 1.728 | 10.2961 | 9.9685 | 9.4634 | 8.8614 | 8.6073 | 7.7634 | 6.7349 | 5.5839 | 4.8002 | 1.2145 | -1.0172 | -2.1498 | 12.6241 | 12.3639 | 11.9965 | 11.5649 | 11.3822 | 10.8404 | 10.173 | 9.4394 | 8.923 | 6.4271 | 3.6883 | -3.1953 | 10.1009 | 9.8458 | 9.4519 | 8.9193 | 8.6764 | 7.9315 | 7.0233 | 5.9938 | 5.306 | 2.1866 | 0.17436 | -0.84809
|  | KINGS RIDE PRIMARY | EE |  |  |  |  | 10.2961 | 9.9685 | 9.4634 | 8.8614 | 8.6073 | 7.7757 | 6.7349 | 5.5839 | 4.8002 | 1.4624 | -0.50186 | -1.9998 | 12.6241 | 12.3639 | 11.9965 | 11.5649 | 11.3822 | 10.8404 | 10.173 | 9.4394 | 8.923 | 6.4271 | 4.0894 | 0.50059 | 10.1009 | 9.8458 | 9.4519 | 8.9193 | 8.7182 | 7.9621 | 7.0233 | 5.9938 | 5.306 | 2.3948 | 0.62028 | -0.7236
|  | KINGS RIDE PRIMARY | HT |  |  |  |  | 10.5257 | 10.2706 | 9.7665 | 9.2441 | 8.6145 | 7.7634 | 6.839 | 6.3175 | 5.4053 | 1.2145 | -1.0172 | -2.1498 | 12.872 | 12.7169 | 12.4281 | 12.1343 | 11.773 | 11.3179 | 10.8088 | 10.5945 | 10.1006 | 7.9281 | 6.8863 | 6.4067 | 10.254 | 10.0448 | 9.6356 | 9.1999 | 8.6764 | 7.9315 | 7.1335 | 6.6346 | 5.8529 | 2.1866 | 0.17436 | -0.84809
|  | KINGS RIDE PRIMARY | HE |  |  |  |  | 10.5604 | 10.3359 | 9.9563 | 9.5492 | 9.0236 | 8.3359 | 7.4308 | 6.8869 | 6.1155 | 2.5971 | 0.61957 | -0.26819 | 12.8179 | 12.6332 | 12.3608 | 12.069 | 11.7057 | 11.2536 | 10.6781 | 10.3557 | 9.8261 | 7.1108 | 4.721 | 1.3465 | 10.2876 | 10.104 | 9.7978 | 9.456 | 9.0203 | 8.4284 | 7.6591 | 7.1356 | 6.4744 | 3.4009 | 1.6091 | 0.81416
|  | KINGS RIDE PRIMARY | CF |  |  |  |  | 10.7696 | 10.639 | 10.4798 | 10.3002 | 10.1532 | 9.939 | 9.6022 | 9.1094 | 8.9818 | 5.4267 | 3.443 | 1.5553 | 12.9169 | 12.769 | 12.5945 | 12.3955 | 12.1904 | 11.9179 | 11.5608 | 11.1159 | 10.9088 | 7.6322 | 3.6883 | -3.1953 | 10.4774 | 10.3784 | 10.256 | 10.1193 | 10.004 | 9.8427 | 9.5856 | 9.1601 | 9.0672 | 5.9774 | 4.1866 | 2.4917
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINGSCLERE PRIMARY | MINIMUM HEADROOM | SU 51982 59358 | NO | NO | 0.784 | 7.1704 | 7.0092 | 6.798 | 6.6133 | 6.3786 | 6.0398 | 5.6469 | 5.6633 | 5.4429 | 4.3173 | 3.6388 | 3.2204 | 8.4827 | 8.3602 | 8.201 | 8.0592 | 7.8755 | 7.6388 | 7.352 | 7.4051 | 7.249 | 6.4541 | 5.5163 | 3.3163 | 7.3092 | 7.152 | 6.9429 | 6.7653 | 6.5276 | 6.2051 | 5.8255 | 5.9071 | 5.701 | 4.7143 | 4.1102 | 3.7439
|  | KINGSCLERE PRIMARY | EE |  |  |  |  | 7.1704 | 7.0092 | 6.798 | 6.6133 | 6.3786 | 6.0398 | 5.6469 | 5.6633 | 5.4429 | 4.3173 | 3.7214 | 3.3153 | 8.4827 | 8.3602 | 8.201 | 8.0592 | 7.8755 | 7.6388 | 7.352 | 7.4051 | 7.249 | 6.4541 | 5.7276 | 4.6255 | 7.3092 | 7.152 | 6.9429 | 6.7653 | 6.5276 | 6.2051 | 5.8255 | 5.9071 | 5.701 | 4.7143 | 4.1908 | 3.8316
|  | KINGSCLERE PRIMARY | HT |  |  |  |  | 7.3 | 7.1786 | 7.0214 | 6.8939 | 6.7184 | 6.4469 | 6.1939 | 5.8857 | 5.5643 | 4.4347 | 3.6388 | 3.2204 | 8.6071 | 8.5357 | 8.4337 | 8.35 | 8.2306 | 8.0714 | 7.9286 | 7.7337 | 7.5296 | 6.9776 | 6.5939 | 6.4194 | 7.4459 | 7.3398 | 7.1857 | 7.0663 | 6.8969 | 6.6439 | 6.4153 | 6.1214 | 5.8163 | 4.8214 | 4.1102 | 3.7439
|  | KINGSCLERE PRIMARY | HE |  |  |  |  | 7.3133 | 7.1735 | 7.0184 | 6.8918 | 6.7173 | 6.4643 | 6.2276 | 5.9347 | 5.6265 | 4.4949 | 3.8071 | 3.5551 | 8.601 | 8.498 | 8.3857 | 8.2857 | 8.1541 | 7.9806 | 7.8194 | 7.6051 | 7.3776 | 6.5469 | 5.7224 | 4.6949 | 7.4643 | 7.3347 | 7.1857 | 7.0673 | 6.898 | 6.6653 | 6.449 | 6.1714 | 5.8776 | 4.8796 | 4.2592 | 4.0459
|  | KINGSCLERE PRIMARY | CF |  |  |  |  | 7.3745 | 7.2918 | 7.1908 | 7.0755 | 6.9888 | 6.8592 | 6.699 | 6.5724 | 6.4 | 5.2918 | 4.8184 | 4.0673 | 8.6296 | 8.5612 | 8.4765 | 8.3776 | 8.2949 | 8.1694 | 8.0173 | 7.8939 | 7.7265 | 6.5918 | 5.5163 | 3.3163 | 7.5153 | 7.4347 | 7.3367 | 7.2255 | 7.1429 | 7.0143 | 6.8561 | 6.7347 | 6.5643 | 5.4939 | 5.1459 | 4.4837
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINTBURY PRIMARY | MINIMUM HEADROOM | SU 37657 67143 | NO | NO | 0.219 | 7.7673 | 7.6133 | 7.4939 | 7.3296 | 7.2 | 6.9867 | 6.7327 | 6.4806 | 6.3602 | 5.8306 | 5.6418 | 5.4694 | 8.6755 | 8.551 | 8.4622 | 8.3214 | 8.2173 | 8.0449 | 7.8306 | 7.6173 | 7.5622 | 7.1724 | 6.4622 | 4.9959 | 7.9031 | 7.7622 | 7.652 | 7.499 | 7.3837 | 7.1888 | 6.9582 | 6.7265 | 6.6143 | 6.1367 | 5.9735 | 5.8214
|  | KINTBURY PRIMARY | EE |  |  |  |  | 7.7673 | 7.6133 | 7.4939 | 7.3296 | 7.2 | 6.9867 | 6.7327 | 6.4806 | 6.3602 | 5.8306 | 5.6418 | 5.551 | 8.6755 | 8.551 | 8.4622 | 8.3214 | 8.2173 | 8.0449 | 7.8306 | 7.6173 | 7.5622 | 7.1724 | 6.7316 | 6.0122 | 7.9031 | 7.7622 | 7.652 | 7.499 | 7.3837 | 7.1888 | 6.9582 | 6.7265 | 6.6143 | 6.1367 | 5.9735 | 5.8939
|  | KINTBURY PRIMARY | HT |  |  |  |  | 7.8622 | 7.7714 | 7.6643 | 7.5418 | 7.4531 | 7.2929 | 7.1082 | 6.9673 | 6.7714 | 5.95 | 5.6571 | 5.4694 | 8.7673 | 8.7143 | 8.6429 | 8.552 | 8.4908 | 8.3755 | 8.2378 | 8.1388 | 7.9918 | 7.452 | 7.3551 | 7.2612 | 7.9918 | 7.9082 | 7.8082 | 7.6969 | 7.6122 | 7.4653 | 7.2959 | 7.1704 | 6.9898 | 6.2408 | 5.9796 | 5.8214
|  | KINTBURY PRIMARY | HE |  |  |  |  | 7.8592 | 7.7714 | 7.6663 | 7.549 | 7.4612 | 7.3061 | 7.1255 | 6.9888 | 6.798 | 5.9194 | 5.7276 | 5.649 | 8.752 | 8.6847 | 8.6112 | 8.5194 | 8.4541 | 8.3408 | 8.2071 | 8.102 | 7.9551 | 7.2449 | 6.7878 | 6.0806 | 7.9888 | 7.9061 | 7.8092 | 7.702 | 7.6214 | 7.4786 | 7.3133 | 7.1908 | 7.0173 | 6.2276 | 6.0541 | 5.9878
|  | KINTBURY PRIMARY | CF |  |  |  |  | 7.898 | 7.8 | 7.7306 | 7.6439 | 7.5459 | 7.4796 | 7.3561 | 7.2296 | 7.0949 | 6.4357 | 6.0143 | 5.7276 | 8.7724 | 8.7 | 8.648 | 8.5776 | 8.5 | 8.4316 | 8.3245 | 8.2082 | 8.0837 | 7.3663 | 6.4622 | 4.9959 | 8.0245 | 7.9398 | 7.8755 | 7.7959 | 7.7061 | 7.6459 | 7.5378 | 7.4214 | 7.2969 | 6.7041 | 6.3204 | 6.0684
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | KNOWL HILL PRIMARY | MINIMUM HEADROOM | SU 82849 79105 | NO | NO | 0.306 | 4.4987 | 4.3967 | 4.2844 | 4.2058 | 4.0813 | 3.913 | 3.7793 | 3.5885 | 3.4895 | 2.9262 | 2.6038 | 2.4364 | 4.5564 | 4.4799 | 4.388 | 4.3207 | 4.2197 | 4.0942 | 3.987 | 3.8391 | 3.7625 | 3.3544 | 2.7758 | 1.4829 | 4.8712 | 4.7712 | 4.663 | 4.5834 | 4.462 | 4.2957 | 4.16 | 3.9742 | 3.8742 | 3.3467 | 3.0498 | 2.914
|  | KNOWL HILL PRIMARY | EE |  |  |  |  | 4.4987 | 4.3967 | 4.2844 | 4.2058 | 4.0813 | 3.913 | 3.7793 | 3.5885 | 3.4895 | 2.9681 | 2.6762 | 2.513 | 4.5564 | 4.4799 | 4.388 | 4.3207 | 4.2197 | 4.0942 | 3.987 | 3.8391 | 3.7625 | 3.3544 | 2.9523 | 2.3431 | 4.8712 | 4.7712 | 4.663 | 4.5834 | 4.462 | 4.2957 | 4.16 | 3.9742 | 3.8742 | 3.4191 | 3.1967 | 3.0589
|  | KNOWL HILL PRIMARY | HT |  |  |  |  | 4.5518 | 4.4742 | 4.414 | 4.3344 | 4.2385 | 4.1007 | 3.9977 | 3.8375 | 3.6732 | 3.0395 | 2.6813 | 2.4364 | 4.6125 | 4.5595 | 4.5207 | 4.4666 | 4.3993 | 4.3115 | 4.2431 | 4.137 | 4.0278 | 3.5901 | 3.3717 | 3.2329 | 4.9283 | 4.8538 | 4.7957 | 4.7202 | 4.6253 | 4.4957 | 4.3947 | 4.2385 | 4.0793 | 3.4732 | 3.1671 | 2.9559
|  | KNOWL HILL PRIMARY | HE |  |  |  |  | 4.5487 | 4.4762 | 4.4171 | 4.3385 | 4.2436 | 4.114 | 4.0171 | 3.8671 | 3.713 | 2.9262 | 2.6038 | 2.463 | 4.6003 | 4.5442 | 4.4972 | 4.434 | 4.3574 | 4.2636 | 4.1911 | 4.0717 | 3.9493 | 3.3942 | 2.9911 | 2.3972 | 4.9242 | 4.8559 | 4.7967 | 4.7222 | 4.6293 | 4.5049 | 4.4089 | 4.2661 | 4.114 | 3.3467 | 3.0498 | 2.914
|  | KNOWL HILL PRIMARY | CF |  |  |  |  | 4.5875 | 4.5324 | 4.462 | 4.4181 | 4.3599 | 4.2793 | 4.1854 | 4.1313 | 4.0324 | 3.5242 | 3.066 | 2.5997 | 4.6238 | 4.5758 | 4.5166 | 4.4789 | 4.4248 | 4.3482 | 4.2625 | 4.2074 | 4.1074 | 3.536 | 2.7758 | 1.4829 | 4.963 | 4.9079 | 4.8416 | 4.7987 | 4.7416 | 4.6661 | 4.5753 | 4.5212 | 4.4222 | 3.9212 | 3.4447 | 2.9896
FLEET-BRAMLEY GSP | ALDERSHOT BSP | LABURNUM ROAD PRIMARY | MINIMUM HEADROOM | SU 86017 50475 | NO | YES | 9.909 | 18.3764 | 16.8621 | 15.0376 | 13.6223 | 12.1641 | 10.9488 | 9.6988 | 8.4784 | 7.5396 | 3.4529 | -0.46446 | -2.6675 | 24.9427 | 24.0019 | 22.8651 | 22.0437 | 21.1039 | 20.2111 | 19.2376 | 18.2539 | 17.4682 | 13.4784 | 8.3835 | -3.9951 | 19.0029 | 17.7192 | 16.1325 | 14.9457 | 13.6406 | 12.5406 | 11.3794 | 10.2427 | 9.3855 | 5.6672 | 2.1968 | 0.2784
|  | LABURNUM ROAD PRIMARY | EE |  |  |  |  | 18.3764 | 16.8621 | 15.0376 | 13.6223 | 12.1641 | 10.9488 | 9.6988 | 8.4784 | 7.5396 | 3.4529 | 0.29779 | -2.3573 | 24.9427 | 24.0019 | 22.8651 | 22.0437 | 21.1039 | 20.2111 | 19.2376 | 18.2539 | 17.4682 | 13.4784 | 9.206 | 2.6019 | 19.0029 | 17.7192 | 16.1325 | 14.9457 | 13.6406 | 12.5406 | 11.3794 | 10.2427 | 9.3855 | 5.6672 | 2.8906 | 0.54983
|  | LABURNUM ROAD PRIMARY | HT |  |  |  |  | 18.7284 | 17.358 | 15.7294 | 14.1366 | 12.8019 | 11.7213 | 11.0325 | 9.9886 | 8.9264 | 3.6662 | -0.46446 | -2.6675 | 25.3743 | 24.6253 | 23.7427 | 22.8835 | 22.1508 | 21.4886 | 21.107 | 20.4355 | 19.7427 | 16.4988 | 14.357 | 13.3988 | 19.3845 | 18.2478 | 16.8743 | 15.5172 | 14.3366 | 13.3478 | 12.7376 | 11.7733 | 10.7968 | 5.9284 | 2.1968 | 0.2784
|  | LABURNUM ROAD PRIMARY | HE |  |  |  |  | 18.7376 | 17.3876 | 15.7937 | 14.2335 | 12.9437 | 11.9937 | 11.4253 | 10.5508 | 9.6396 | 5.4488 | 2.3427 | 0.9284 | 25.2611 | 24.4621 | 23.5223 | 22.5978 | 21.7998 | 21.0794 | 20.6253 | 19.8713 | 19.0835 | 14.8008 | 10.4325 | 4.4366 | 19.3927 | 18.2784 | 16.9386 | 15.6213 | 14.4927 | 13.6243 | 13.1284 | 12.2927 | 11.4508 | 7.5794 | 4.8253 | 3.6723
|  | LABURNUM ROAD PRIMARY | CF |  |  |  |  | 19.1182 | 18.0478 | 16.7304 | 15.5468 | 14.6131 | 14.0784 | 13.5662 | 13.3437 | 12.8182 | 9.7366 | 6.5753 | 3.6896 | 25.4345 | 24.7631 | 23.9294 | 23.1702 | 22.4988 | 21.9121 | 21.2743 | 20.8682 | 20.1927 | 15.6304 | 8.3835 | -3.9951 | 19.7396 | 18.8835 | 17.7917 | 16.8172 | 16.0162 | 15.5304 | 15.0406 | 14.858 | 14.3764 | 11.4917 | 8.5794 | 5.9713
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LAMBOURN PRIMARY | MINIMUM HEADROOM | SU 33280 78217 | NO | NO | 1.38 | -0.5949 | 10.9688 | 9.1382 | 7.0045 | 4.5504 | 1.731 | -1.7669 | -4.9741 | -8.2414 | -25.9802 | -32.2588 | -32.4914 | 1.098 | 12.1529 | 10.7559 | 9.1233 | 7.2457 | 5.1039 | 2.4345 | -0.0042857 | -2.4931 | -16.0124 | -20.7808 | -20.9859 | -0.24388 | 11.0729 | 9.3065 | 7.2443 | 4.8718 | 2.1494 | -1.2282 | -4.321 | -7.4771 | -24.5976 | -30.6496 | -30.8629
|  | LAMBOURN PRIMARY | EE |  |  |  |  | -0.5949 | 10.9688 | 9.1382 | 7.0045 | 4.5504 | 1.731 | -1.7669 | -4.9741 | -8.2414 | -21.0394 | -27.4302 | -29.2343 | 1.098 | 12.1529 | 10.7559 | 9.1233 | 7.2457 | 5.1039 | 2.4345 | -0.0042857 | -2.4931 | -12.191 | -17.0308 | -18.4135 | -0.24388 | 11.0729 | 9.3065 | 7.2443 | 4.8718 | 2.1494 | -1.2282 | -4.321 | -7.4771 | -19.8149 | -25.9741 | -27.7016
|  | LAMBOURN PRIMARY | HT |  |  |  |  | 1.1173 | 13.2535 | 11.9871 | 10.4606 | 8.6096 | 6.4484 | 3.7504 | 0.82796 | -2.2976 | -15.5731 | -22.7863 | -25.5037 | 2.4969 | 13.9192 | 12.9498 | 11.7896 | 10.3773 | 8.7396 | 6.6906 | 4.4712 | 2.0927 | -7.9665 | -13.4073 | -15.4329 | 1.5153 | 13.2922 | 12.0616 | 10.5892 | 8.8004 | 6.7147 | 4.1096 | 1.2902 | -1.7292 | -14.5312 | -21.4812 | -24.0914
|  | LAMBOURN PRIMARY | HE |  |  |  |  | 0.64592 | 12.4188 | 10.7514 | 8.7973 | 6.3749 | 3.5371 | -0.064898 | -3.9731 | -7.7904 | -25.9802 | -32.2588 | -32.4914 | 2.0908 | 13.2671 | 11.9957 | 10.5059 | 8.6518 | 6.4937 | 3.7416 | 0.75694 | -2.1563 | -16.0124 | -20.7808 | -20.9859 | 1.0071 | 12.4739 | 10.8667 | 8.982 | 6.6382 | 3.8973 | 0.41878 | -3.3557 | -7.0424 | -24.5976 | -30.6496 | -30.8629
|  | LAMBOURN PRIMARY | CF |  |  |  |  | 2.0837 | 14.5667 | 13.8412 | 12.98 | 11.8769 | 10.6259 | 8.9076 | 6.9616 | 4.879 | -7.4904 | -18.6231 | -25.471 | 3.2133 | 15.0182 | 14.408 | 13.6967 | 12.8498 | 11.8947 | 10.5784 | 9.0835 | 7.4896 | -1.9747 | -10.491 | -15.7645 | 2.148 | 14.5841 | 13.9208 | 13.0198 | 11.9535 | 10.7453 | 9.0861 | 7.2014 | 5.1912 | -6.7527 | -17.4955 | -24.0935
FAWLEY GSP | LANGLEY BSP | LANGLEY PRIMARY | MINIMUM HEADROOM | SU 45158 01418 | NO | NO | 7.736 | 0.94694 | 0.83163 | 0.54388 | 0.32143 | -0.49592 | -1.2929 | -2 | -3.4286 | -4.7939 | -9.3031 | -13.1408 | -16.7684 | -3.0378 | -3.1663 | -3.5255 | -3.7398 | -4.6133 | -5.1571 | -5.6337 | -7.3765 | -8.6551 | -12.5786 | -16.8286 | -22.3592 | -2.1837 | -2.3918 | -2.75 | -3.0184 | -3.9592 | -4.6633 | -5.3765 | -7.1653 | -8.6296 | -13.298 | -17.5184 | -21.7112
|  | LANGLEY PRIMARY | EE |  |  |  |  | 0.94694 | 0.83163 | 0.54388 | 0.51735 | 0.044898 | -0.67245 | -1.402 | -2.4663 | -3.2408 | -6.7684 | -11.552 | -13.9327 | -3.0378 | -3.1663 | -3.3235 | -3.3561 | -3.7163 | -4.1765 | -4.5092 | -5.2112 | -5.6959 | -8.7367 | -14.151 | -17.7173 | -2.1837 | -2.3918 | -2.6469 | -2.6888 | -3.1265 | -3.7929 | -4.3847 | -5.3633 | -6.0878 | -9.8459 | -15.2296 | -17.6837
|  | LANGLEY PRIMARY | HT |  |  |  |  | 1.0439 | 0.9 | 0.60714 | 0.41837 | -0.30306 | -1.2929 | -2 | -2.7827 | -3.7837 | -8.15 | -12.852 | -16.0031 | -2.9367 | -3.0929 | -3.3439 | -3.4408 | -4.1306 | -4.751 | -5.2867 | -5.6582 | -6.452 | -9.5551 | -13.8204 | -16.8204 | -2.0735 | -2.3255 | -2.6776 | -2.8643 | -3.6684 | -4.6082 | -5.3765 | -6.0592 | -7.0949 | -11.5143 | -16.6969 | -20.198
|  | LANGLEY PRIMARY | HE |  |  |  |  | 1.0449 | 0.88163 | 0.56633 | 0.32143 | -0.49592 | -1.2092 | -1.702 | -3.4286 | -4.7939 | -9.3031 | -13.1408 | -16.7684 | -2.9541 | -3.1541 | -3.5255 | -3.7398 | -4.6133 | -5.1571 | -5.6337 | -7.3765 | -8.6551 | -12.5786 | -16.8286 | -22.3592 | -2.0408 | -2.3061 | -2.75 | -3.0184 | -3.9592 | -4.6633 | -5.2367 | -7.1653 | -8.6296 | -13.298 | -17.5184 | -21.7112
|  | LANGLEY PRIMARY | CF |  |  |  |  | 1.1235 | 1.0735 | 1.0122 | 0.88673 | 0.75408 | 0.5551 | 0.27449 | -0.064286 | -0.07551 | -2.8837 | -6.1122 | -8.8929 | -2.8816 | -2.9551 | -3.0418 | -3.2163 | -3.4102 | -3.6755 | -3.9265 | -4.202 | -4.3765 | -6.8929 | -11.2408 | -17.3898 | -1.8847 | -1.9776 | -2.0898 | -2.2806 | -2.4694 | -2.7439 | -3.0031 | -3.2959 | -3.3816 | -5.9939 | -9.4469 | -12.4082
FLEET-BRAMLEY GSP | FERNHURST BSP | LANGLEY COURT PRIMARY | MINIMUM HEADROOM | SU 80847 29056 | NO | NO | 8.796 | 6.7642 | 6.4622 | 6.1856 | 5.8183 | 5.4275 | 5.353 | 4.8683 | 4.3764 | 4.0193 | 2.1346 | 0.71727 | -0.21029 | 9.1742 | 8.9436 | 8.7426 | 8.466 | 8.1762 | 8.1589 | 7.813 | 7.4538 | 7.2018 | 5.8007 | 4.1487 | 0.18135 | 7.3044 | 7.0146 | 6.7503 | 6.4085 | 6.0473 | 5.9799 | 5.5228 | 5.0595 | 4.733 | 3.0616 | 1.8524 | 1.0626
|  | LANGLEY COURT PRIMARY | EE |  |  |  |  | 6.7642 | 6.4622 | 6.1856 | 5.8183 | 5.4275 | 5.353 | 4.8683 | 4.3764 | 4.0193 | 2.1346 | 0.90808 | 0.030531 | 9.1742 | 8.9436 | 8.7426 | 8.466 | 8.1762 | 8.1589 | 7.813 | 7.4538 | 7.2018 | 5.8007 | 4.3844 | 2.362 | 7.3044 | 7.0146 | 6.7503 | 6.4085 | 6.0473 | 5.9799 | 5.5228 | 5.0595 | 4.733 | 3.0616 | 2.0085 | 1.2595
|  | LANGLEY COURT PRIMARY | HT |  |  |  |  | 6.9428 | 6.6979 | 6.4867 | 6.2009 | 5.9458 | 5.5234 | 5.055 | 4.553 | 4.4571 | 2.1764 | 0.71727 | -0.21029 | 9.3569 | 9.2069 | 9.0793 | 8.8967 | 8.7446 | 8.4977 | 8.215 | 7.9028 | 7.9181 | 6.6344 | 5.9201 | 5.4844 | 7.4799 | 7.2524 | 7.0544 | 6.7891 | 6.5534 | 6.1585 | 5.7218 | 5.2503 | 5.1891 | 3.1156 | 1.8524 | 1.0626
|  | LANGLEY COURT PRIMARY | HE |  |  |  |  | 6.9438 | 6.7469 | 6.5111 | 6.2387 | 6.002 | 5.6275 | 5.2081 | 4.756 | 4.7173 | 2.5499 | 1.3387 | 0.77135 | 9.3242 | 9.1803 | 9.0079 | 8.8079 | 8.6334 | 8.3701 | 8.065 | 7.7262 | 7.7171 | 6.0242 | 4.5946 | 2.7262 | 7.482 | 7.2983 | 7.0748 | 6.8218 | 6.6013 | 6.2513 | 5.8554 | 5.4269 | 5.4156 | 3.4411 | 2.3993 | 1.9299
|  | LANGLEY COURT PRIMARY | CF |  |  |  |  | 7.1203 | 6.952 | 6.8081 | 6.6183 | 6.4111 | 6.253 | 6.0234 | 5.7724 | 5.4999 | 4.3999 | 2.9734 | 1.5867 | 9.4038 | 9.2671 | 9.1497 | 8.9864 | 8.8089 | 8.6507 | 8.4181 | 8.1681 | 7.8956 | 6.5385 | 4.1487 | 0.18135 | 7.6371 | 7.482 | 7.3493 | 7.1718 | 6.9789 | 6.8299 | 6.6105 | 6.3758 | 6.1228 | 5.0962 | 3.8064 | 2.6034
AXMINSTER GSP | YEOVIL BSP | LARKHILL PRIMARY | MINIMUM HEADROOM | ST 53677 16914 | NO | NO | 8.866 | 12.1262 | 11.7109 | 11.5793 | 11.1793 | 10.7548 | 9.9721 | 9.1048 | 8.2466 | 7.5936 | 3.6344 | 0.7405 | -1.0105 | 14.0742 | 13.715 | 13.5966 | 13.2211 | 12.8129 | 12.2436 | 11.5905 | 10.9221 | 10.4446 | 7.6078 | 3.3854 | -6.3575 | 11.8099 | 11.3436 | 11.2527 | 10.8354 | 10.3854 | 9.6395 | 8.7874 | 7.9344 | 7.3711 | 4.1313 | 1.6936 | 0.2405
|  | LARKHILL PRIMARY | EE |  |  |  |  | 12.1262 | 11.7109 | 11.5793 | 11.1793 | 10.7548 | 9.9721 | 9.1048 | 8.2466 | 7.5936 | 4.0221 | 1.3527 | -0.7146 | 14.0742 | 13.715 | 13.5966 | 13.2211 | 12.8129 | 12.2436 | 11.5905 | 10.9221 | 10.4446 | 7.6078 | 4.3466 | -0.77277 | 11.8099 | 11.3436 | 11.2527 | 10.8354 | 10.3854 | 9.6395 | 8.7874 | 7.9344 | 7.3711 | 4.4048 | 2.216 | 0.48029
|  | LARKHILL PRIMARY | HT |  |  |  |  | 12.3385 | 11.9976 | 11.6823 | 11.3048 | 10.8936 | 10.4568 | 9.6793 | 8.8803 | 8.064 | 3.6344 | 0.7405 | -1.0105 | 14.3874 | 14.1609 | 13.9538 | 13.6925 | 13.4007 | 13.2711 | 12.8487 | 12.4027 | 11.9364 | 9.6272 | 8.3762 | 7.6538 | 12.0691 | 11.7395 | 11.4334 | 11.0629 | 10.6476 | 10.3078 | 9.5976 | 8.8578 | 8.0987 | 4.1313 | 1.6936 | 0.2405
|  | LARKHILL PRIMARY | HE |  |  |  |  | 12.3834 | 12.0742 | 11.7925 | 11.4466 | 11.0742 | 10.7905 | 10.1691 | 9.5293 | 8.8721 | 4.7323 | 2.3925 | 1.1293 | 14.314 | 14.0527 | 13.8038 | 13.4844 | 13.1334 | 12.9629 | 12.4895 | 11.9793 | 11.4425 | 8.2374 | 4.9313 | 0.011927 | 12.1048 | 11.8048 | 11.5272 | 11.1874 | 10.8068 | 10.4599 | 9.8691 | 9.1201 | 8.3252 | 4.4385 | 2.3119 | 1.1558
|  | LARKHILL PRIMARY | CF |  |  |  |  | 12.6395 | 12.4874 | 12.3048 | 12.1507 | 11.9466 | 11.7068 | 11.7283 | 11.4783 | 11.217 | 8.7099 | 5.6956 | 3.3089 | 14.415 | 14.2364 | 14.0119 | 13.7834 | 13.4813 | 13.1191 | 12.964 | 12.5558 | 12.1201 | 8.7885 | 3.3854 | -6.3575 | 12.3262 | 12.1793 | 11.9915 | 11.8242 | 11.5783 | 11.2976 | 11.3109 | 10.9823 | 10.6303 | 8.0966 | 5.3099 | 3.1395
COWLEY GSP | WITNEY BSP | LEAFIELD PRIMARY | MINIMUM HEADROOM | SP 30282 15270 | NO | NO | 1.385 | 1.3888 | 1.2663 | 1.102 | 0.91837 | 0.77653 | 0.49388 | 0.17143 | -0.15 | -0.33673 | -0.91735 | -1.7122 | -2.1969 | 2.1439 | 2.0388 | 1.9 | 1.7439 | 1.6245 | 1.4122 | 1.1633 | 0.90816 | 0.78163 | 0.46939 | -0.42245 | -2.5684 | 1.1786 | 1.0612 | 0.90102 | 0.72041 | 0.59184 | 0.31837 | -0.005102 | -0.32857 | -0.49388 | -0.91837 | -1.6071 | -2.0245
|  | LEAFIELD PRIMARY | EE |  |  |  |  | 1.3888 | 1.2663 | 1.102 | 0.91837 | 0.77653 | 0.49388 | 0.17143 | -0.15 | -0.33673 | -0.91735 | -1.5918 | -2.099 | 2.1439 | 2.0388 | 1.9 | 1.7439 | 1.6245 | 1.4122 | 1.1633 | 0.90816 | 0.78163 | 0.46939 | -0.27449 | -1.4041 | 1.1786 | 1.0612 | 0.90102 | 0.72041 | 0.59184 | 0.31837 | -0.005102 | -0.32857 | -0.49388 | -0.91837 | -1.499 | -1.9408
|  | LEAFIELD PRIMARY | HT |  |  |  |  | 1.4867 | 1.3888 | 1.2694 | 1.1673 | 1.0286 | 0.78878 | 0.57041 | 0.3 | 0.021429 | -0.91735 | -1.7122 | -2.1969 | 2.248 | 2.1857 | 2.101 | 2.0357 | 1.9337 | 1.7847 | 1.6602 | 1.4888 | 1.3082 | 0.93061 | 0.57653 | 0.37857 | 1.2786 | 1.1857 | 1.0735 | 0.97959 | 0.8449 | 0.61939 | 0.41837 | 0.16429 | -0.096939 | -0.91327 | -1.6071 | -2.0245
|  | LEAFIELD PRIMARY | HE |  |  |  |  | 1.4908 | 1.399 | 1.2867 | 1.1949 | 1.0612 | 0.85612 | 0.67143 | 0.43673 | 0.19388 | -0.62857 | -1.2878 | -1.6255 | 2.2337 | 2.1582 | 2.0663 | 1.9929 | 1.8796 | 1.7286 | 1.5969 | 1.4163 | 1.2224 | 0.61735 | -0.13571 | -1.1939 | 1.2816 | 1.1949 | 1.0878 | 1.0031 | 0.87347 | 0.68163 | 0.51122 | 0.28673 | 0.056122 | -0.65918 | -1.2245 | -1.5173
|  | LEAFIELD PRIMARY | CF |  |  |  |  | 1.5622 | 1.5041 | 1.4265 | 1.3367 | 1.2806 | 1.1806 | 1.0592 | 0.92959 | 0.84082 | -0.018367 | -0.36837 | -1.049 | 2.2714 | 2.2112 | 2.1388 | 2.051 | 1.9827 | 1.8735 | 1.7429 | 1.599 | 1.4929 | 0.51429 | -0.42245 | -2.5684 | 1.348 | 1.2918 | 1.2194 | 1.1327 | 1.0786 | 0.98163 | 0.86327 | 0.73469 | 0.65714 | -0.19592 | -0.44796 | -1.0173
WILLESDEN GSP | ACTON LANE BSP | LEAMINGTON PARK PRIMARY | MINIMUM HEADROOM | TQ 20539 81536 | NO | YES | 7.646 | 36.7548 | 34.7701 | 32.5058 | 30.515 | 28.1007 | 27.1364 | 26.116 | 25.1242 | 24.215 | 23.164 | 21.6487 | 20.213 | 38.0189 | 36.8546 | 35.5424 | 34.3413 | 32.9434 | 31.9036 | 30.7862 | 29.7271 | 28.7179 | 25.9638 | 23.3281 | 16.5577 | 39.2016 | 37.5577 | 35.6526 | 33.925 | 31.8158 | 30.7873 | 29.6893 | 28.6495 | 27.6628 | 26.0822 | 24.4893 | 23.2005
|  | LEAMINGTON PARK PRIMARY | EE |  |  |  |  | 36.9232 | 34.8416 | 32.5262 | 30.515 | 28.114 | 27.1364 | 26.116 | 25.1242 | 24.215 | 23.164 | 22.2181 | 20.6895 | 38.2118 | 36.9016 | 35.5424 | 34.3413 | 32.9434 | 31.9036 | 30.7862 | 29.7271 | 28.7179 | 25.9638 | 23.5342 | 19.3516 | 39.3822 | 37.6362 | 35.6995 | 33.9291 | 31.8281 | 30.7873 | 29.6893 | 28.6495 | 27.6628 | 26.0822 | 25.172 | 23.7811
|  | LEAMINGTON PARK PRIMARY | HT |  |  |  |  | 36.7548 | 34.7701 | 32.5058 | 30.5344 | 28.1007 | 27.1395 | 26.1426 | 25.2864 | 24.4997 | 23.1895 | 21.6487 | 20.213 | 38.0189 | 36.8546 | 35.5903 | 34.4689 | 33.1281 | 32.2016 | 31.1995 | 30.3362 | 29.5485 | 27.5352 | 26.2179 | 25.1954 | 39.2016 | 37.5577 | 35.6526 | 33.925 | 31.8158 | 30.8158 | 29.7536 | 28.8495 | 28.0342 | 26.1056 | 24.4893 | 23.2005
|  | LEAMINGTON PARK PRIMARY | HE |  |  |  |  | 37.0395 | 35.0058 | 32.7446 | 30.8058 | 28.4773 | 27.7028 | 26.815 | 26.0262 | 25.2609 | 24.2875 | 23.3773 | 22.3395 | 38.3067 | 37.0342 | 35.7199 | 34.5781 | 33.2413 | 32.3985 | 31.4189 | 30.575 | 29.7332 | 27.0169 | 24.5607 | 20.5852 | 39.5403 | 37.8516 | 35.9454 | 34.2577 | 32.2413 | 31.4332 | 30.4913 | 29.6944 | 28.926 | 27.4454 | 26.5301 | 25.5526
|  | LEAMINGTON PARK PRIMARY | CF |  |  |  |  | 37.4701 | 36.0967 | 34.2354 | 32.766 | 31.0946 | 30.3977 | 29.515 | 28.662 | 27.7732 | 24.7579 | 24.2477 | 24.0854 | 38.4985 | 37.7475 | 36.5454 | 35.5944 | 34.524 | 33.726 | 32.7679 | 31.8362 | 30.8842 | 27.2648 | 23.3281 | 16.5577 | 39.8648 | 38.822 | 37.273 | 35.9842 | 34.523 | 33.8005 | 32.8995 | 32.0403 | 31.1567 | 28.3852 | 27.5699 | 27.2924
MINETY GSP | STRATTON (RESERVE) BSP | LECHLADE PRIMARY | MINIMUM HEADROOM | SP 22074 00496 | NO | NO | 0.975 | 4.8563 | 4.7186 | 4.54 | 4.341 | 4.1808 | 3.8829 | 3.542 | 3.2012 | 2.992 | 1.9176 | 1.238 | 0.8798 | 6.3255 | 6.2184 | 6.0735 | 5.9153 | 5.7816 | 5.5612 | 5.299 | 5.0337 | 4.8857 | 4.1082 | 3.1133 | 0.70102 | 5.0694 | 4.9337 | 4.752 | 4.552 | 4.3939 | 4.1041 | 3.7663 | 3.4296 | 3.2459 | 2.3704 | 1.8031 | 1.5643
|  | LECHLADE PRIMARY | EE |  |  |  |  | 4.8563 | 4.7186 | 4.54 | 4.341 | 4.1808 | 3.8829 | 3.542 | 3.2012 | 2.992 | 1.9369 | 1.238 | 1.0359 | 6.3255 | 6.2184 | 6.0735 | 5.9153 | 5.7816 | 5.5612 | 5.299 | 5.0337 | 4.8857 | 4.1082 | 3.2704 | 2.3051 | 5.0694 | 4.9337 | 4.752 | 4.552 | 4.3939 | 4.1041 | 3.7663 | 3.4296 | 3.2459 | 2.3796 | 1.8031 | 1.6929
|  | LECHLADE PRIMARY | HT |  |  |  |  | 4.9482 | 4.838 | 4.7084 | 4.59 | 4.4329 | 4.1788 | 3.938 | 3.6522 | 3.3512 | 1.9176 | 1.3992 | 0.8798 | 6.4296 | 6.3602 | 6.2704 | 6.201 | 6.0929 | 5.9469 | 5.8092 | 5.6306 | 5.4378 | 4.5969 | 4.5153 | 4.2939 | 5.1786 | 5.0765 | 4.949 | 4.8378 | 4.6837 | 4.4469 | 4.2306 | 3.9622 | 3.6776 | 2.3704 | 1.9857 | 1.5643
|  | LECHLADE PRIMARY | HE |  |  |  |  | 4.9594 | 4.8573 | 4.7359 | 4.6329 | 4.492 | 4.2778 | 4.0329 | 3.8298 | 3.5767 | 2.2808 | 1.592 | 1.5533 | 6.4133 | 6.3337 | 6.2347 | 6.1551 | 6.0378 | 5.8857 | 5.7051 | 5.5561 | 5.3592 | 4.3122 | 3.4602 | 2.5735 | 5.1857 | 5.0898 | 4.9735 | 4.8735 | 4.7357 | 4.5327 | 4.298 | 4.1122 | 3.8673 | 2.6908 | 2.1265 | 2.1745
|  | LECHLADE PRIMARY | CF |  |  |  |  | 5.0349 | 4.9676 | 4.8869 | 4.7982 | 4.6961 | 4.6278 | 4.4992 | 4.3624 | 4.2676 | 3.338 | 2.5022 | 1.7849 | 6.448 | 6.3867 | 6.3133 | 6.2235 | 6.1194 | 6.0367 | 5.901 | 5.749 | 5.6296 | 4.5643 | 3.1133 | 0.70102 | 5.2571 | 5.1908 | 5.1051 | 5.0163 | 4.9153 | 4.848 | 4.7173 | 4.5755 | 4.4867 | 3.5735 | 2.849 | 2.2724
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LECKHAMPSTEAD PRIMARY | MINIMUM HEADROOM | SU 43962 77635 | NO | NO | 0.401 | 3.3701 | 3.2344 | 3.1252 | 2.9681 | 2.7977 | 2.6426 | 2.4069 | 2.1701 | 2.0548 | 1.5313 | 1.2507 | 1.1181 | 4.1217 | 4.0187 | 3.937 | 3.8156 | 3.6829 | 3.5697 | 3.388 | 3.2054 | 3.1197 | 2.6993 | 2.036 | 0.60029 | 3.4998 | 3.3691 | 3.264 | 3.112 | 2.9487 | 2.7998 | 2.5702 | 2.3447 | 2.2365 | 1.6742 | 1.3967 | 1.2487
|  | LECKHAMPSTEAD PRIMARY | EE |  |  |  |  | 3.3701 | 3.2344 | 3.1252 | 2.9681 | 2.7977 | 2.6426 | 2.4069 | 2.1701 | 2.0548 | 1.5313 | 1.3599 | 1.2987 | 4.1217 | 4.0187 | 3.937 | 3.8156 | 3.6829 | 3.5697 | 3.388 | 3.2054 | 3.1197 | 2.6993 | 2.2921 | 1.6329 | 3.4998 | 3.3691 | 3.264 | 3.112 | 2.9487 | 2.7998 | 2.5702 | 2.3447 | 2.2365 | 1.762 | 1.611 | 1.5538
|  | LECKHAMPSTEAD PRIMARY | HT |  |  |  |  | 3.4681 | 3.3813 | 3.2824 | 3.166 | 3.0803 | 2.9262 | 2.7518 | 2.564 | 2.4313 | 1.6528 | 1.3895 | 1.215 | 4.2105 | 4.1584 | 4.0931 | 4.0156 | 3.9595 | 3.8625 | 3.7452 | 3.6176 | 3.5319 | 3.0319 | 2.8799 | 2.7993 | 3.5947 | 3.5161 | 3.4202 | 3.3089 | 3.2283 | 3.0834 | 2.9151 | 2.7365 | 2.61 | 1.8732 | 1.6324 | 1.4773
|  | LECKHAMPSTEAD PRIMARY | HE |  |  |  |  | 3.464 | 3.3793 | 3.2813 | 3.1701 | 3.0844 | 2.9344 | 2.764 | 2.5783 | 2.4477 | 1.5364 | 1.2507 | 1.1181 | 4.1962 | 4.136 | 4.0625 | 3.9768 | 3.9115 | 3.8064 | 3.6768 | 3.5329 | 3.437 | 2.7554 | 2.3248 | 1.6687 | 3.5916 | 3.514 | 3.4191 | 3.314 | 3.2324 | 3.0896 | 2.9202 | 2.7426 | 2.5712 | 1.6742 | 1.3967 | 1.2487
|  | LECKHAMPSTEAD PRIMARY | CF |  |  |  |  | 3.5038 | 3.4109 | 3.3477 | 3.266 | 3.1701 | 3.0681 | 2.9905 | 2.8691 | 2.7405 | 2.1099 | 1.7099 | 1.3324 | 4.2207 | 4.1523 | 4.1044 | 4.036 | 3.9584 | 3.8646 | 3.7931 | 3.6809 | 3.5636 | 2.8891 | 2.036 | 0.60029 | 3.6293 | 3.5436 | 3.4855 | 3.4079 | 3.3151 | 3.2171 | 3.1457 | 3.0293 | 2.9059 | 2.2998 | 1.8212 | 1.4691
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | LEE-ON-SOLENT PRIMARY | MINIMUM HEADROOM | SU 56858 00293 | NO | YES | 13.83 | 2.1128 | 1.3098 | 0.92711 | 0.10772 | -0.65963 | -1.8994 | -3.0198 | -4.0892 | -4.7627 | -8.5321 | -11.53 | -13.3035 | 3.9545 | 3.2891 | 3.0126 | 2.3677 | 1.7494 | 0.85445 | -0.00064898 | -0.84657 | -1.4047 | -4.4425 | -9.9313 | -21.6629 | 2.0826 | 1.3194 | 1.0194 | 0.26425 | -0.45514 | -1.5806 | -2.6296 | -3.6388 | -4.2439 | -7.4837 | -10.099 | -11.5245
|  | LEE-ON-SOLENT PRIMARY | EE |  |  |  |  | 2.1128 | 1.3098 | 0.92711 | 0.10772 | -0.65963 | -1.8994 | -3.0198 | -4.0892 | -4.7627 | -8.0811 | -10.7862 | -13.0321 | 3.9545 | 3.2891 | 3.0126 | 2.3677 | 1.7494 | 0.85445 | -0.00064898 | -0.84657 | -1.4047 | -4.4425 | -8.2558 | -14.5017 | 2.0826 | 1.3194 | 1.0194 | 0.26425 | -0.45514 | -1.5806 | -2.6296 | -3.6388 | -4.2439 | -7.1153 | -9.446 | -11.2909
|  | LEE-ON-SOLENT PRIMARY | HT |  |  |  |  | 2.2455 | 1.6751 | 1.0475 | 0.25262 | -0.61167 | -1.4974 | -2.4841 | -3.4494 | -4.277 | -8.5321 | -11.53 | -13.3035 | 4.1596 | 3.8075 | 3.4187 | 2.9075 | 2.3116 | 1.8453 | 1.3045 | 0.74935 | 0.25139 | -2.0455 | -3.3935 | -4.1058 | 2.2714 | 1.752 | 1.1714 | 0.44792 | -0.35106 | -1.0745 | -1.9643 | -2.8429 | -3.6092 | -7.4837 | -10.099 | -11.5245
|  | LEE-ON-SOLENT PRIMARY | HE |  |  |  |  | 2.4077 | 1.7669 | 1.1802 | 0.43425 | 0.070984 | -0.91677 | -1.7453 | -2.5525 | -3.2494 | -6.6994 | -9.377 | -10.7851 | 4.1759 | 3.6555 | 3.2065 | 2.6381 | 2.3351 | 1.6177 | 1.0024 | 0.35956 | -0.27106 | -3.7302 | -7.5894 | -13.4925 | 2.4081 | 1.8265 | 1.2806 | 0.60098 | 0.32445 | -0.5531 | -1.3062 | -2.0409 | -2.7 | -5.8541 | -8.1684 | -9.2898
|  | LEE-ON-SOLENT PRIMARY | CF |  |  |  |  | 2.6832 | 2.2618 | 1.7506 | 1.1842 | 0.67813 | 0.063841 | -0.015751 | -0.45453 | -0.79636 | -3.3045 | -5.929 | -8.3729 | 4.2769 | 3.8912 | 3.3953 | 2.883 | 2.3922 | 1.7647 | 1.4932 | 0.94323 | 0.39833 | -3.5425 | -9.9313 | -21.6629 | 2.6591 | 2.2632 | 1.801 | 1.2847 | 0.81629 | 0.25507 | 0.2469 | -0.17249 | -0.51534 | -2.9398 | -5.2439 | -7.3123
LOVEDEAN GSP | HAVANT BSP | LEIGH PARK PRIMARY | MINIMUM HEADROOM | SU 72144 07875 | NO | YES | 3.857 | 12.738 | 12.1645 | 11.8951 | 11.3022 | 10.6278 | 9.5737 | 8.44 | 7.3441 | 6.4502 | 1.4696 | -1.6212 | -2.7069 | 15.0669 | 14.572 | 14.3588 | 13.8516 | 13.2486 | 12.4782 | 11.618 | 10.7608 | 10.0822 | 5.7894 | 0.5802 | -11.4371 | 13.3065 | 12.7371 | 12.5065 | 11.931 | 11.2739 | 10.278 | 9.1198 | 7.9831 | 7.179 | 2.9882 | 0.26163 | -0.60368
|  | LEIGH PARK PRIMARY | EE |  |  |  |  | 12.738 | 12.1645 | 11.8951 | 11.3022 | 10.6278 | 9.5737 | 8.44 | 7.3441 | 6.4502 | 1.5992 | -0.91102 | -1.711 | 15.0669 | 14.572 | 14.3588 | 13.8516 | 13.2486 | 12.4782 | 11.618 | 10.7608 | 10.0822 | 5.7894 | 1.9373 | -3.8147 | 13.3065 | 12.7371 | 12.5065 | 11.931 | 11.2739 | 10.278 | 9.1198 | 7.9831 | 7.179 | 2.9984 | 0.88102 | 0.20142
|  | LEIGH PARK PRIMARY | HT |  |  |  |  | 12.9492 | 12.5135 | 12.0451 | 11.4594 | 10.8155 | 10.1951 | 9.2665 | 8.3278 | 7.2288 | 1.4696 | -1.6212 | -2.7069 | 15.369 | 15.0833 | 14.7955 | 14.3863 | 13.918 | 13.6506 | 13.1037 | 12.5455 | 11.8475 | 8.4914 | 6.9455 | 6.3618 | 13.5494 | 13.1494 | 12.7218 | 12.1688 | 11.5555 | 11.0392 | 10.178 | 9.2953 | 8.2667 | 2.9882 | 0.26163 | -0.60368
|  | LEIGH PARK PRIMARY | HE |  |  |  |  | 13.0257 | 12.5757 | 12.1747 | 11.6655 | 11.0757 | 10.5155 | 9.6543 | 8.792 | 7.9155 | 3.0706 | 0.64612 | -0.1947 | 15.3282 | 14.9414 | 14.621 | 14.1945 | 13.672 | 13.3067 | 12.6516 | 11.972 | 11.2639 | 6.6547 | 2.7149 | -2.9769 | 13.6208 | 13.2004 | 12.832 | 12.3575 | 11.7953 | 11.3382 | 10.5361 | 9.7269 | 8.8994 | 4.4412 | 2.3514 | 1.68
|  | LEIGH PARK PRIMARY | CF |  |  |  |  | 13.3339 | 13.1992 | 12.9318 | 12.7298 | 12.4788 | 12.1502 | 11.7267 | 11.591 | 11.1778 | 8.3482 | 4.4686 | 1.2369 | 15.4618 | 15.2608 | 14.9404 | 14.6537 | 14.2833 | 13.8067 | 13.2302 | 12.9088 | 12.3078 | 8.07 | 0.5802 | -11.4371 | 13.9014 | 13.7688 | 13.5035 | 13.3147 | 13.0678 | 12.7484 | 12.331 | 12.2433 | 11.8412 | 9.0688 | 5.6167 | 2.8382
BRAMLEY (BASI) GSP | READING BSP | LITTLE HUNGERFORD PRIMARY | MINIMUM HEADROOM | SU 75372 72019 | NO | YES | 10.533 | 6.8676 | 6.089 | 5.2023 | 4.2472 | 3.1135 | 1.387 | -0.5008 | -2.3365 | -3.6192 | -10.3222 | -15.2845 | -17.4743 | 11.2502 | 10.6145 | 9.89 | 9.0951 | 8.1298 | 6.8982 | 5.5104 | 4.1298 | 3.2278 | -1.5028 | -8.0937 | -23.1865 | 6.241 | 5.5135 | 4.687 | 3.7635 | 2.6319 | 0.9941 | -0.81916 | -2.5937 | -3.7426 | -9.46 | -13.8426 | -15.6181
|  | LITTLE HUNGERFORD PRIMARY | EE |  |  |  |  | 6.8676 | 6.089 | 5.2023 | 4.2472 | 3.1135 | 1.387 | -0.5008 | -2.3365 | -3.6192 | -9.911 | -14.3722 | -16.3049 | 11.2502 | 10.6145 | 9.89 | 9.0951 | 8.1298 | 6.8982 | 5.5104 | 4.1298 | 3.2278 | -1.5028 | -6.6192 | -14.0375 | 6.241 | 5.5135 | 4.687 | 3.7635 | 2.6319 | 0.9941 | -0.81916 | -2.5937 | -3.7426 | -9.2059 | -13.0722 | -14.7008
|  | LITTLE HUNGERFORD PRIMARY | HT |  |  |  |  | 7.0104 | 6.2635 | 5.8217 | 4.9645 | 4.0023 | 2.5278 | 0.94002 | -0.68345 | -2.3151 | -10.3222 | -15.2845 | -17.4743 | 11.5972 | 11.0961 | 10.9104 | 10.3206 | 9.6533 | 8.8247 | 7.8992 | 6.941 | 5.9686 | 1.6257 | -0.63651 | -1.5998 | 6.4217 | 5.7257 | 5.3533 | 4.5359 | 3.6278 | 2.2849 | 0.82471 | -0.66712 | -2.1702 | -9.46 | -13.8426 | -15.6181
|  | LITTLE HUNGERFORD PRIMARY | HE |  |  |  |  | 7.1502 | 6.4635 | 6.0921 | 5.39 | 4.5084 | 3.2114 | 1.8023 | 0.38288 | -1.0651 | -7.8692 | -12.3243 | -14.0794 | 11.4788 | 10.9104 | 10.6543 | 10.0768 | 9.3268 | 8.4023 | 7.3666 | 6.2859 | 5.1594 | -0.63957 | -5.9212 | -13.2008 | 6.5196 | 5.8798 | 5.5676 | 4.9217 | 4.0849 | 2.8849 | 1.5747 | 0.24512 | -1.1161 | -7.3783 | -11.309 | -12.7661
|  | LITTLE HUNGERFORD PRIMARY | CF |  |  |  |  | 7.8431 | 7.4482 | 6.9798 | 6.887 | 6.3961 | 5.7829 | 5.0931 | 4.3808 | 3.6635 | -1.2294 | -6.3671 | -11.0212 | 11.7972 | 11.3523 | 10.8461 | 10.6839 | 10.1145 | 9.3992 | 8.5768 | 7.7196 | 6.8227 | 0.70227 | -8.0937 | -23.1865 | 7.1288 | 6.7584 | 6.3319 | 6.2808 | 5.8461 | 5.2676 | 4.5798 | 3.8645 | 3.1421 | -1.612 | -6.1447 | -10.1804
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW PRIMARY | MINIMUM HEADROOM | SU 86037 87794 | NO | NO | 4.852 | 1.6691 | 1.1579 | 0.95582 | 0.43949 | -0.12378 | -0.96765 | -1.9146 | -2.8656 | -3.5523 | -7.6207 | -10.7656 | -12.5289 | 8.3721 | 8.0211 | 7.8762 | 7.514 | 7.117 | 6.567 | 5.8895 | 5.1813 | 4.7007 | 1.8599 | -2.0279 | -11.0146 | 1.7099 | 1.2262 | 1.0558 | 0.56908 | 0.044592 | -0.74112 | -1.6279 | -2.5187 | -3.1411 | -6.7432 | -9.5319 | -11.0585
|  | LITTLE MARLOW PRIMARY | EE |  |  |  |  | 1.6691 | 1.1579 | 0.95582 | 0.43949 | -0.12378 | -0.96765 | -1.9146 | -2.8656 | -3.5523 | -7.2768 | -10.0952 | -12.2238 | 8.3721 | 8.0211 | 7.8762 | 7.514 | 7.117 | 6.567 | 5.8895 | 5.1813 | 4.7007 | 1.8599 | -1.433 | -6.2646 | 1.7099 | 1.2262 | 1.0558 | 0.56908 | 0.044592 | -0.74112 | -1.6279 | -2.5187 | -3.1411 | -6.4585 | -8.9238 | -10.7819
|  | LITTLE MARLOW PRIMARY | HT |  |  |  |  | 1.9395 | 1.5272 | 1.1313 | 0.6548 | 0.12418 | -0.30235 | -1.1289 | -1.9881 | -2.8758 | -7.6207 | -10.7656 | -12.5289 | 8.6426 | 8.4109 | 8.1956 | 7.9262 | 7.6293 | 7.4701 | 7.0517 | 6.6109 | 6.1538 | 3.7232 | 2.2548 | 1.4466 | 1.9834 | 1.6017 | 1.2385 | 0.79357 | 0.30276 | -0.058469 | -0.81969 | -1.6105 | -2.4289 | -6.7432 | -9.5319 | -11.0585
|  | LITTLE MARLOW PRIMARY | HE |  |  |  |  | 1.9701 | 1.6181 | 1.213 | 0.76704 | 0.2701 | -0.00030612 | -0.67173 | -1.3779 | -2.1064 | -6.0268 | -8.8105 | -10.1115 | 8.5599 | 8.3068 | 8.0181 | 7.6936 | 7.3374 | 7.1599 | 6.7068 | 6.2201 | 5.6956 | 2.4701 | -0.86765 | -5.3728 | 2.0079 | 1.6864 | 1.3109 | 0.89561 | 0.43745 | 0.21296 | -0.41153 | -1.0646 | -1.7401 | -5.3126 | -7.7656 | -8.8983
|  | LITTLE MARLOW PRIMARY | CF |  |  |  |  | 2.2466 | 1.9987 | 1.7772 | 1.4966 | 1.1874 | 0.9099 | 0.95582 | 0.65786 | 0.34153 | -2.2023 | -4.9789 | -7.5432 | 8.6793 | 8.4548 | 8.2415 | 7.9823 | 7.6772 | 7.3517 | 7.2181 | 6.8507 | 6.4283 | 3.217 | -2.0279 | -11.0146 | 2.2589 | 2.0323 | 1.8303 | 1.5691 | 1.2823 | 1.013 | 1.0691 | 0.78337 | 0.48439 | -1.8932 | -4.3952 | -6.6656
NURSLING GSP | ROWNHAMS BSP | LORDSHILL PRIMARY | MINIMUM HEADROOM | SU 38746 16055 | NO | YES | 7.682 | 12.8822 | 12.5822 | 12.1934 | 11.7628 | 11.8424 | 11.2832 | 10.6516 | 10.021 | 9.62 | 6.5608 | 4.4873 | 3.2843 | 10.3271 | 10.0853 | 9.7567 | 9.3802 | 9.3394 | 8.8792 | 8.3598 | 7.8179 | 7.4322 | 4.0985 | -0.76166 | -10.3494 | 10.7608 | 10.4792 | 10.12 | 9.723 | 9.7302 | 9.1934 | 8.5873 | 7.9832 | 7.5771 | 4.3373 | 2.6414 | 1.7108
|  | LORDSHILL PRIMARY | EE |  |  |  |  | 12.8822 | 12.5822 | 12.1934 | 11.7628 | 11.8424 | 11.2832 | 10.6516 | 10.021 | 9.62 | 6.7149 | 4.871 | 3.4996 | 10.3271 | 10.0853 | 9.7567 | 9.3802 | 9.3394 | 8.8792 | 8.3598 | 7.8179 | 7.4322 | 4.0985 | 0.96181 | -4.0402 | 10.7608 | 10.4792 | 10.12 | 9.723 | 9.7302 | 9.1934 | 8.5873 | 7.9832 | 7.5771 | 4.419 | 2.9843 | 1.8955
|  | LORDSHILL PRIMARY | HT |  |  |  |  | 13.1373 | 12.923 | 12.6394 | 12.3883 | 12.0649 | 11.5465 | 10.9639 | 10.9281 | 10.2883 | 6.5608 | 4.4873 | 3.2843 | 10.5792 | 10.4373 | 10.2424 | 10.0781 | 9.8496 | 9.5292 | 9.1577 | 9.2016 | 8.7445 | 6.2047 | 5.2445 | 4.723 | 10.9843 | 10.7812 | 10.5169 | 10.2761 | 9.972 | 9.4771 | 8.9271 | 8.8118 | 8.1567 | 4.3373 | 2.6414 | 1.7108
|  | LORDSHILL PRIMARY | HE |  |  |  |  | 13.1496 | 12.9475 | 12.6853 | 12.4577 | 12.1516 | 11.6924 | 11.1771 | 10.9465 | 10.4312 | 6.9179 | 5.4251 | 4.6975 | 10.5322 | 10.3639 | 10.1343 | 9.9016 | 9.6067 | 9.2179 | 8.7741 | 8.67 | 8.2332 | 4.5536 | 1.3792 | -3.4157 | 10.9955 | 10.8047 | 10.5588 | 10.3414 | 10.0536 | 9.619 | 9.1292 | 8.972 | 8.4894 | 5.17 | 3.7618 | 3.0934
|  | LORDSHILL PRIMARY | CF |  |  |  |  | 13.3149 | 13.1904 | 13.0261 | 12.8404 | 12.6934 | 12.4781 | 12.2098 | 11.922 | 12.1088 | 10.3108 | 7.4863 | 5.919 | 10.62 | 10.4679 | 10.2812 | 10.0557 | 9.8108 | 9.4843 | 9.0985 | 8.6863 | 8.5598 | 5.5669 | -0.76166 | -10.3494 | 11.1659 | 11.0536 | 10.9057 | 10.7383 | 10.6036 | 10.4077 | 10.1639 | 9.9026 | 10.02 | 8.3506 | 5.6281 | 4.2557
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LOVE LANE PRIMARY | MINIMUM HEADROOM | SU 47334 68495 | NO | NO | 12.567 | 8.3065 | 6.9433 | 5.3147 | 3.6484 | 1.5739 | -0.77816 | -3.421 | -7.1955 | -10.8924 | -25.8629 | -33.1435 | -37.2312 | 12.7851 | 11.7769 | 10.5831 | 9.3657 | 7.7208 | 5.8831 | 3.5657 | -0.2302 | -3.4598 | -15.471 | -21.9833 | -26.6771 | 9.7831 | 8.4861 | 6.9412 | 5.3565 | 3.3076 | 0.99735 | -1.5496 | -5.9353 | -9.7516 | -24.62 | -32.2567 | -37.0669
|  | LOVE LANE PRIMARY | EE |  |  |  |  | 8.3065 | 6.9433 | 5.3147 | 3.6484 | 1.5739 | -0.77816 | -3.421 | -6.2588 | -8.7924 | -19.1986 | -27.1363 | -29.9302 | 12.7851 | 11.7769 | 10.5831 | 9.3657 | 7.7208 | 5.8831 | 3.9086 | 1.6361 | -0.3302 | -8.4476 | -15.9578 | -18.6047 | 9.7831 | 8.4861 | 6.9412 | 5.3565 | 3.3076 | 0.99735 | -1.5424 | -4.3578 | -6.8373 | -17.0945 | -25.672 | -28.6598
|  | LOVE LANE PRIMARY | HT |  |  |  |  | 9.6361 | 8.578 | 7.2555 | 5.8933 | 3.9004 | 2.0188 | -0.39449 | -2.6792 | -5.4506 | -17.2608 | -25.9322 | -30.5639 | 13.8147 | 13.03 | 12.0157 | 11.0392 | 9.3045 | 7.7984 | 5.8514 | 4.132 | 1.8739 | -7.4435 | -15.3271 | -19.8231 | 10.7555 | 9.9198 | 8.7657 | 7.4759 | 5.4116 | 3.532 | 1.1188 | -1.0945 | -3.8741 | -15.5914 | -24.7996 | -29.8894
|  | LOVE LANE PRIMARY | HE |  |  |  |  | 9.3106 | 8.028 | 6.3647 | 4.6565 | 2.1698 | -0.10878 | -3.0394 | -7.1955 | -10.8924 | -25.8629 | -33.1435 | -37.2312 | 13.5627 | 12.5769 | 11.2453 | 9.9524 | 7.7576 | 5.9229 | 3.5657 | -0.2302 | -3.4598 | -15.471 | -21.9833 | -26.6771 | 10.6422 | 9.5137 | 7.8667 | 6.2157 | 3.628 | 1.3627 | -1.5496 | -5.9353 | -9.7516 | -24.62 | -32.2567 | -37.0669
|  | LOVE LANE PRIMARY | CF |  |  |  |  | 10.2229 | 9.6769 | 8.9565 | 8.1484 | 7.18 | 6.1188 | 4.7606 | 3.3616 | 1.7218 | -8.4343 | -18.0506 | -24.5312 | 14.08 | 13.6861 | 13.1933 | 12.6096 | 11.9259 | 11.0576 | 9.978 | 8.8729 | 7.5484 | -0.5751 | -8.4414 | -14.4792 | 11.2769 | 10.7922 | 10.1596 | 9.43 | 8.7055 | 7.6473 | 6.3137 | 4.9473 | 3.3239 | -6.6996 | -16.2873 | -22.8251
COWLEY GSP | YARNTON BSP | LOVELACE ROAD PRIMARY | MINIMUM HEADROOM | SP 50395 10376 | YES | YES | 13.402 | 1.5468 | 22.9484 | 22.6973 | 22.3708 | 21.9545 | 21.1004 | 20.6861 | 20.0004 | 19.4167 | 17.3698 | 16.431 | 16.2627 | 1.9096 | 23.128 | 22.9055 | 22.6229 | 22.2494 | 21.6718 | 21.4504 | 20.9024 | 20.4392 | 18.2708 | 15.4861 | 9.7555 | 1.282 | 22.3086 | 22.0545 | 21.731 | 21.3178 | 20.5504 | 20.2729 | 19.6371 | 19.132 | 17.2565 | 16.4147 | 16.2627
|  | LOVELACE ROAD PRIMARY | EE |  |  |  |  | 1.5468 | 22.9484 | 22.6973 | 22.3708 | 21.9545 | 21.1004 | 20.6861 | 20.0004 | 19.4678 | 17.3698 | 16.579 | 16.5555 | 1.9096 | 23.128 | 22.9055 | 22.6229 | 22.2494 | 21.6718 | 21.4504 | 20.9024 | 20.4392 | 18.2708 | 16.5912 | 14.0208 | 1.282 | 22.3086 | 22.0545 | 21.731 | 21.3178 | 20.5504 | 20.2729 | 19.6371 | 19.1545 | 17.2565 | 16.5565 | 16.5239
|  | LOVELACE ROAD PRIMARY | HT |  |  |  |  | 1.7142 | 23.1912 | 23.0065 | 22.6933 | 22.3106 | 21.3514 | 20.779 | 20.0922 | 19.4167 | 17.5422 | 16.431 | 16.2627 | 2.1178 | 23.432 | 23.3096 | 23.0749 | 22.7851 | 22.2871 | 21.8708 | 21.3565 | 20.8484 | 19.679 | 19.0647 | 18.9494 | 1.4729 | 22.582 | 22.4076 | 22.1106 | 21.7504 | 20.9484 | 20.4116 | 19.7678 | 19.132 | 17.43 | 16.4147 | 16.2627
|  | LOVELACE ROAD PRIMARY | HE |  |  |  |  | 1.7101 | 23.1892 | 23.0086 | 22.7831 | 22.4586 | 21.7453 | 21.1096 | 20.4963 | 19.8769 | 17.8167 | 16.879 | 16.728 | 2.0555 | 23.3361 | 23.1759 | 22.9769 | 22.6841 | 22.2504 | 21.7718 | 21.2647 | 20.7086 | 18.4637 | 16.6157 | 14.031 | 1.4688 | 22.58 | 22.4127 | 22.1902 | 21.88 | 21.2769 | 20.6984 | 20.1218 | 19.5371 | 17.6596 | 16.8024 | 16.6678
|  | LOVELACE ROAD PRIMARY | CF |  |  |  |  | 1.8734 | 23.4382 | 23.3116 | 23.2086 | 23.0565 | 22.8698 | 22.6259 | 22.2586 | 21.8627 | 19.5504 | 18.1973 | 16.9841 | 2.1331 | 23.4504 | 23.2953 | 23.1647 | 22.9739 | 22.7249 | 22.43 | 22.0382 | 21.6127 | 18.7453 | 15.4861 | 9.7555 | 1.6096 | 22.7943 | 22.6606 | 22.5576 | 22.4065 | 22.2208 | 21.9922 | 21.6473 | 21.282 | 19.2392 | 17.9912 | 16.8861
MANNINGTON GSP | ARNEWOOD BSP | LYMINGTON PRIMARY | MINIMUM HEADROOM | SZ 31720 96856 | NO | NO | 3.408 | 11.548 | 10.8194 | 10.5347 | 9.7796 | 8.9418 | 7.6204 | 6.3194 | 5.049 | 4.1612 | -0.9398 | -4.9582 | -7.1694 | 14.6143 | 14.0214 | 13.8592 | 13.2827 | 12.651 | 11.7898 | 10.8827 | 9.9694 | 9.351 | 5.9694 | 2.4245 | -7.1969 | 11.9735 | 11.2908 | 11.0388 | 10.3439 | 9.5724 | 8.3704 | 7.1704 | 5.9939 | 5.1551 | 0.61327 | -2.9551 | -4.9735
|  | LYMINGTON PRIMARY | EE |  |  |  |  | 11.548 | 10.8194 | 10.5347 | 9.7796 | 8.9418 | 7.6204 | 6.3194 | 5.049 | 4.1612 | -0.68878 | -4.1327 | -6.7378 | 14.6143 | 14.0214 | 13.8592 | 13.2827 | 12.651 | 11.7898 | 10.8827 | 9.9694 | 9.351 | 5.9694 | 2.5429 | -2.5765 | 11.9735 | 11.2908 | 11.0388 | 10.3439 | 9.5724 | 8.3704 | 7.1704 | 5.9939 | 5.1551 | 0.80306 | -2.2041 | -4.601
|  | LYMINGTON PRIMARY | HT |  |  |  |  | 11.7878 | 11.3214 | 10.7082 | 9.9745 | 9.5857 | 8.4265 | 7.351 | 6.2388 | 5.0929 | -0.9398 | -4.9582 | -7.1694 | 14.95 | 14.6602 | 14.2684 | 13.8082 | 13.6735 | 13.0643 | 12.4582 | 11.8173 | 11.149 | 7.9163 | 6.0867 | 5.1776 | 12.198 | 11.798 | 11.2408 | 10.5745 | 10.2531 | 9.2122 | 8.2235 | 7.1918 | 6.1296 | 0.61327 | -2.9551 | -4.9735
|  | LYMINGTON PRIMARY | HE |  |  |  |  | 11.9388 | 11.4214 | 10.902 | 10.2541 | 9.9112 | 8.8969 | 7.9633 | 7.0276 | 6.0786 | 0.95204 | -2.5153 | -4.1184 | 14.9663 | 14.5633 | 14.1643 | 13.6745 | 13.4929 | 12.8531 | 12.2082 | 11.5255 | 10.8184 | 6.8612 | 3.3255 | -1.3704 | 12.3469 | 11.8816 | 11.4031 | 10.8122 | 10.5337 | 9.6296 | 8.7663 | 7.898 | 7.0122 | 2.3194 | -0.78163 | -2.2786
|  | LYMINGTON PRIMARY | CF |  |  |  |  | 12.2857 | 12.0214 | 11.6827 | 11.35 | 10.9367 | 10.8378 | 10.4357 | 9.9663 | 9.4724 | 5.9337 | 2.3 | -1.1184 | 15.1306 | 14.8571 | 14.5296 | 14.1939 | 13.7745 | 13.6306 | 13.1612 | 12.6347 | 12.0694 | 8.1041 | 2.4245 | -7.1969 | 12.6643 | 12.4265 | 12.1112 | 11.798 | 11.4153 | 11.3531 | 10.9755 | 10.5378 | 10.0776 | 6.8051 | 3.498 | 0.46837
MELKSHAM GSP | CHIPPENHAM BSP | LYNEHAM PRIMARY | MINIMUM HEADROOM | ST 99348 80481 | NO | YES | 2.627 | 3.5467 | 3.1232 | 2.7457 | 2.262 | 1.8844 | 1.9375 | 1.5355 | 1.1344 | 0.89158 | -0.54719 | -1.4645 | -2.139 | 6.0941 | 5.837 | 5.5962 | 5.2972 | 5.0533 | 5.0462 | 4.7768 | 4.5003 | 4.3186 | 3.2941 | 2.0156 | -0.96505 | 4.8283 | 4.4406 | 4.0936 | 3.6436 | 3.2824 | 3.3559 | 2.9753 | 2.5936 | 2.3732 | 1.2018 | 0.45383 | -0.078824
|  | LYNEHAM PRIMARY | EE |  |  |  |  | 3.5467 | 3.1232 | 2.7457 | 2.262 | 1.8844 | 1.9375 | 1.5355 | 1.1344 | 0.89158 | -0.54719 | -1.3829 | -1.9125 | 6.0941 | 5.837 | 5.5962 | 5.2972 | 5.0533 | 5.0462 | 4.7768 | 4.5003 | 4.3186 | 3.2941 | 2.2911 | 0.80536 | 4.8283 | 4.4406 | 4.0936 | 3.6436 | 3.2824 | 3.3559 | 2.9753 | 2.5936 | 2.3732 | 1.2161 | 0.54362 | 0.10791
|  | LYNEHAM PRIMARY | HT |  |  |  |  | 3.6202 | 3.2457 | 2.912 | 2.6324 | 2.3987 | 2.0467 | 1.6569 | 1.2467 | 1.2742 | -0.46352 | -1.4645 | -2.139 | 6.1809 | 5.9768 | 5.8003 | 5.6462 | 5.5094 | 5.3145 | 5.0911 | 4.8554 | 4.8992 | 3.9564 | 3.4911 | 3.186 | 4.9161 | 4.5804 | 4.2773 | 4.014 | 3.7967 | 3.4691 | 3.0997 | 2.711 | 2.8242 | 1.2814 | 0.46199 | -0.078824
|  | LYNEHAM PRIMARY | HE |  |  |  |  | 3.7253 | 3.4181 | 3.16 | 2.8293 | 2.5283 | 2.1202 | 1.7579 | 1.3793 | 1.4446 | -0.29413 | -1.14 | -1.5717 | 6.2084 | 6.0196 | 5.8564 | 5.6492 | 5.4584 | 5.2013 | 4.9605 | 4.7033 | 4.7217 | 3.439 | 2.4064 | 0.93189 | 5.0079 | 4.7242 | 4.4875 | 4.1834 | 3.912 | 3.5365 | 3.1916 | 2.8314 | 2.9406 | 1.2018 | 0.45383 | 0.03342
|  | LYNEHAM PRIMARY | CF |  |  |  |  | 3.8151 | 3.6375 | 3.4375 | 3.1885 | 2.9069 | 2.6865 | 2.3885 | 2.1579 | 1.9161 | 1.1324 | 0.093624 | -0.87984 | 6.2543 | 6.1309 | 6.0003 | 5.8278 | 5.6298 | 5.4533 | 5.2258 | 5.0247 | 4.8105 | 3.7758 | 2.0156 | -0.96505 | 5.0885 | 4.9232 | 4.7436 | 4.5151 | 4.2579 | 4.06 | 3.7824 | 3.563 | 3.3314 | 2.611 | 1.5304 | 0.6722
FLEET-BRAMLEY GSP | BRACKNELL BSP | MVEE PRIMARY | MINIMUM HEADROOM | SU 98120 65945 | NO | NO | 4.024 | 21.6214 | 21.5612 | 21.4806 | 21.3878 | 21.3337 | 21.1847 | 21.0184 | 20.9031 | 20.8082 | 20.2929 | 19.8959 | 19.6745 | 20.3163 | 20.2643 | 20.1918 | 20.1041 | 20.05 | 19.9367 | 19.802 | 19.7184 | 19.6837 | 19.4673 | 18.849 | 17.5673 | 21.3867 | 21.3316 | 21.2612 | 21.1765 | 21.1276 | 20.9959 | 20.8449 | 20.7316 | 20.648 | 20.1714 | 19.8469 | 19.6724
|  | MVEE PRIMARY | EE |  |  |  |  | 21.6214 | 21.5612 | 21.4806 | 21.3878 | 21.3337 | 21.1847 | 21.0184 | 20.9031 | 20.8082 | 20.3684 | 20 | 19.7194 | 20.3163 | 20.2643 | 20.1918 | 20.1041 | 20.05 | 19.9367 | 19.802 | 19.7184 | 19.6837 | 19.4673 | 19.0449 | 18.3653 | 21.3867 | 21.3316 | 21.2612 | 21.1765 | 21.1276 | 20.9959 | 20.8449 | 20.7316 | 20.648 | 20.2367 | 19.9337 | 19.7082
|  | MVEE PRIMARY | HT |  |  |  |  | 21.6673 | 21.6173 | 21.5724 | 21.5 | 21.4347 | 21.299 | 21.1939 | 21.0429 | 20.8969 | 20.2929 | 19.8959 | 19.6745 | 20.3857 | 20.3459 | 20.3122 | 20.2571 | 20.2061 | 20.1276 | 20.0724 | 19.9776 | 19.8806 | 19.601 | 19.5367 | 19.4459 | 21.4357 | 21.3847 | 21.3408 | 21.2765 | 21.2163 | 21.0939 | 20.999 | 20.8633 | 20.7286 | 20.1714 | 19.8469 | 19.6724
|  | MVEE PRIMARY | HE |  |  |  |  | 21.6765 | 21.6306 | 21.5867 | 21.5214 | 21.4592 | 21.348 | 21.2663 | 21.1449 | 21.0163 | 20.4847 | 20.1265 | 19.9214 | 20.3827 | 20.3408 | 20.3071 | 20.252 | 20.1969 | 20.1173 | 20.0633 | 19.9673 | 19.8643 | 19.5102 | 19.0745 | 18.4265 | 21.4408 | 21.3949 | 21.3551 | 21.2949 | 21.2378 | 21.1398 | 21.0663 | 20.9541 | 20.8398 | 20.351 | 20.0367 | 19.8745
|  | MVEE PRIMARY | CF |  |  |  |  | 21.7153 | 21.6888 | 21.6429 | 21.6214 | 21.5827 | 21.5286 | 21.4602 | 21.4296 | 21.3612 | 20.95 | 20.5592 | 20.2378 | 20.399 | 20.3653 | 20.3214 | 20.298 | 20.2561 | 20.202 | 20.1327 | 20.0949 | 20.0184 | 19.5827 | 18.849 | 17.5673 | 21.4765 | 21.448 | 21.4082 | 21.3888 | 21.3531 | 21.3061 | 21.2459 | 21.2173 | 21.1592 | 20.7878 | 20.4286 | 20.1286
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON PRIMARY | MINIMUM HEADROOM | SY 59138 97747 | NO | NO | 0.852 | 6.751 | 6.602 | 6.4031 | 6.2429 | 6.0204 | 5.7388 | 5.3929 | 5.0439 | 5.5173 | 4.7633 | 4.5224 | 4.3194 | 8.1276 | 8.0204 | 7.8735 | 7.751 | 7.5755 | 7.3571 | 7.0929 | 6.8255 | 7.1816 | 6.5714 | 5.9469 | 4.3551 | 6.8745 | 6.7245 | 6.5245 | 6.3602 | 6.1347 | 5.8531 | 5.5133 | 5.1704 | 5.6847 | 5.0286 | 4.8224 | 4.6398
|  | MAIDEN NEWTON PRIMARY | EE |  |  |  |  | 6.751 | 6.602 | 6.4031 | 6.2429 | 6.0204 | 5.7388 | 5.3929 | 5.0439 | 5.5173 | 4.7633 | 4.5224 | 4.4194 | 8.1276 | 8.0204 | 7.8735 | 7.751 | 7.5755 | 7.3571 | 7.0929 | 6.8255 | 7.1816 | 6.6439 | 6.1663 | 5.4153 | 6.8745 | 6.7245 | 6.5245 | 6.3602 | 6.1347 | 5.8531 | 5.5133 | 5.1704 | 5.6847 | 5.0286 | 4.8224 | 4.7276
|  | MAIDEN NEWTON PRIMARY | HT |  |  |  |  | 6.8949 | 6.7908 | 6.6602 | 6.552 | 6.4071 | 6.2173 | 6.0418 | 5.8194 | 5.5796 | 4.9449 | 4.5541 | 4.3194 | 8.2357 | 8.1735 | 8.0796 | 8.0112 | 7.9031 | 7.7684 | 7.6531 | 7.4776 | 7.2908 | 7.0571 | 6.8541 | 6.7398 | 7.0276 | 6.9337 | 6.8041 | 6.702 | 6.551 | 6.3592 | 6.1959 | 5.9653 | 5.7214 | 5.1827 | 4.8378 | 4.6398
|  | MAIDEN NEWTON PRIMARY | HE |  |  |  |  | 6.8929 | 6.7908 | 6.6633 | 6.5622 | 6.4204 | 6.2388 | 6.0694 | 5.8531 | 5.6092 | 4.901 | 4.6551 | 4.5806 | 8.2214 | 8.152 | 8.05 | 7.9776 | 7.8602 | 7.7194 | 7.599 | 7.4265 | 7.2459 | 6.7571 | 6.2633 | 5.5388 | 7.0265 | 6.9347 | 6.8041 | 6.7071 | 6.5571 | 6.3714 | 6.2092 | 5.9765 | 5.7357 | 5.1724 | 4.9582 | 4.8949
|  | MAIDEN NEWTON PRIMARY | CF |  |  |  |  | 6.9398 | 6.852 | 6.7551 | 6.6469 | 6.5694 | 6.451 | 6.3122 | 6.1684 | 6.0602 | 5.1724 | 5.0582 | 4.6378 | 8.252 | 8.1847 | 8.1061 | 8.0163 | 7.952 | 7.8408 | 7.7112 | 7.5684 | 7.4663 | 6.5714 | 5.9469 | 4.3551 | 7.0816 | 6.999 | 6.9041 | 6.798 | 6.7255 | 6.6092 | 6.4714 | 6.3255 | 6.2265 | 5.299 | 5.3041 | 4.9378
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | MAIDENHEAD PRIMARY | MINIMUM HEADROOM | SU 86485 79800 | NO | NO | 12.207 | 12.1788 | 11.7839 | 10.9094 | 9.6727 | 8.5451 | 7.0186 | 5.3604 | 3.8553 | 2.8176 | -2.2529 | -5.9253 | -7.2182 | 13.4308 | 13.1778 | 12.5512 | 11.738 | 10.9043 | 9.8839 | 8.7492 | 7.6655 | 6.9471 | 3.4084 | -0.45693 | -10.8916 | 8.5543 | 8.2594 | 7.4594 | 6.3655 | 5.3257 | 3.9645 | 2.4614 | 1.0829 | 0.1849 | -4.0549 | -7.2488 | -8.3324
|  | MAIDENHEAD PRIMARY | EE |  |  |  |  | 12.1788 | 11.7839 | 10.9094 | 9.6727 | 8.5451 | 7.0186 | 5.3604 | 3.8553 | 2.8176 | -2.1396 | -5.3784 | -6.2926 | 13.4308 | 13.1778 | 12.5512 | 11.738 | 10.9043 | 9.8839 | 8.7492 | 7.6655 | 6.9471 | 3.4084 | -0.13959 | -4.9957 | 8.5543 | 8.2594 | 7.4594 | 6.3655 | 5.3257 | 3.9645 | 2.4614 | 1.0829 | 0.1849 | -4.011 | -6.7733 | -7.5406
|  | MAIDENHEAD PRIMARY | HT |  |  |  |  | 12.5441 | 11.9502 | 11.1145 | 10.1706 | 9.1604 | 7.8522 | 6.4757 | 5.2002 | 3.9298 | -2.2529 | -5.9253 | -7.2182 | 13.9063 | 13.5359 | 13.0278 | 12.5839 | 11.9522 | 11.2369 | 10.4584 | 9.7053 | 8.9512 | 5.5614 | 3.84 | 3.2125 | 9.0063 | 8.4655 | 7.7155 | 7.0369 | 6.1502 | 5.0431 | 3.8482 | 2.6829 | 1.5125 | -4.0549 | -7.2488 | -8.3324
|  | MAIDENHEAD PRIMARY | HE |  |  |  |  | 12.6247 | 12.0737 | 11.2951 | 10.5614 | 9.6441 | 8.4625 | 7.2053 | 6.09 | 4.9676 | -0.090608 | -3.1202 | -4.2396 | 13.8247 | 13.4084 | 12.8584 | 12.5002 | 11.8492 | 11.0788 | 10.2318 | 9.4196 | 8.5839 | 4.4492 | 0.90735 | -3.9263 | 9.0594 | 8.5574 | 7.8533 | 7.3553 | 6.5502 | 5.5369 | 4.44 | 3.4369 | 2.3951 | -2.2039 | -4.7549 | -5.6906
|  | MAIDENHEAD PRIMARY | CF |  |  |  |  | 13.1145 | 12.841 | 12.391 | 11.6971 | 11.4206 | 10.7227 | 9.9512 | 9.3155 | 8.7706 | 5.0237 | 1.1176 | -2.5937 | 14.0533 | 13.7604 | 13.3563 | 12.8227 | 12.6227 | 12.0125 | 11.3135 | 10.6512 | 10.0063 | 5.6431 | -0.45693 | -10.8916 | 9.4686 | 9.1971 | 8.7676 | 8.1482 | 8.0094 | 7.4002 | 6.7063 | 6.1084 | 5.5696 | 2.0971 | -1.2243 | -4.3212
MELKSHAM GSP | CHIPPENHAM BSP | MALMESBURY PRIMARY | MINIMUM HEADROOM | ST 92288 87493 | NO | YES | 1.603 | 1.3602 | 0.82959 | 0.39592 | -0.046939 | -0.51429 | -0.65918 | -1.1878 | -1.7092 | -2.0837 | -4.1408 | -5.6541 | -6.7092 | 4.1398 | 3.8888 | 3.6378 | 3.3694 | 3.0816 | 3.0092 | 2.6857 | 2.3602 | 2.1092 | 0.60102 | -1.0316 | -5.1245 | 2.3786 | 1.9153 | 1.4969 | 1.0541 | 0.58776 | 0.55 | 0.042857 | -0.45816 | -0.7949 | -2.5592 | -3.8643 | -4.6878
|  | MALMESBURY PRIMARY | EE |  |  |  |  | 1.3602 | 0.82959 | 0.39592 | -0.046939 | -0.51429 | -0.65918 | -1.1878 | -1.7092 | -2.0837 | -4.1408 | -5.4673 | -6.4531 | 4.1398 | 3.8888 | 3.6378 | 3.3694 | 3.0816 | 3.0092 | 2.6857 | 2.3602 | 2.1092 | 0.60102 | -0.90612 | -3.0663 | 2.3786 | 1.9153 | 1.4969 | 1.0541 | 0.58776 | 0.55 | 0.042857 | -0.45816 | -0.7949 | -2.5592 | -3.6704 | -4.4724
|  | MALMESBURY PRIMARY | HT |  |  |  |  | 1.5357 | 1.0663 | 0.70816 | 0.35102 | 0.017347 | -0.42959 | -0.92143 | -1.0918 | -1.5612 | -4.0551 | -5.6541 | -6.7092 | 4.2582 | 4.049 | 3.8908 | 3.7296 | 3.5755 | 3.3398 | 3.0837 | 3.0367 | 2.7898 | 1.5276 | 0.74898 | 0.27143 | 2.5827 | 2.1827 | 1.8561 | 1.5163 | 1.2102 | 0.79184 | 0.32551 | 0.23061 | -0.20918 | -2.4684 | -3.8643 | -4.6878
|  | MALMESBURY PRIMARY | HE |  |  |  |  | 1.5408 | 1.0806 | 0.73367 | 0.38469 | 0.066327 | -0.32959 | -0.77143 | -0.89286 | -1.3 | -3.5786 | -4.9378 | -5.5969 | 4.2265 | 4.0031 | 3.8245 | 3.6347 | 3.4357 | 3.1857 | 2.9041 | 2.8286 | 2.552 | 0.87143 | -0.65918 | -2.6969 | 2.5837 | 2.1939 | 1.8755 | 1.55 | 1.2592 | 0.88571 | 0.46122 | 0.4102 | 0.027551 | -2.0327 | -3.1316 | -3.6449
|  | MALMESBURY PRIMARY | CF |  |  |  |  | 1.701 | 1.3082 | 1.0878 | 0.84184 | 0.57755 | 0.40204 | 0.16939 | -0.084694 | -0.34694 | -1.5041 | -2.951 | -4.2949 | 4.2939 | 4.099 | 3.9724 | 3.8265 | 3.6316 | 3.4602 | 3.249 | 3.0143 | 2.7643 | 1.4051 | -1.0316 | -5.1245 | 2.7316 | 2.3959 | 2.199 | 1.9684 | 1.7235 | 1.5612 | 1.3204 | 1.0531 | 0.77653 | -0.23061 | -1.5031 | -2.65
MINETY GSP | SWINDON BSP | MANCHESTER ROAD PRIMARY | MINIMUM HEADROOM | SU 15254 85130 | NO | NO | 5.993 | 28.8673 | 28.1428 | 27.303 | 26.5765 | 24.6724 | 22.5214 | 20.0051 | 17.1214 | 14.9969 | 7.5235 | 3.6428 | 3.4602 | 29.7408 | 29.1459 | 28.4704 | 27.8949 | 26.5633 | 25.1316 | 23.4286 | 21.5286 | 20.0602 | 14.1357 | 6.752 | -8.7367 | 28.6571 | 28.0275 | 27.3 | 26.6663 | 25.0643 | 23.2255 | 21.0939 | 18.6235 | 16.8245 | 8.5806 | 4.8949 | 4.7388
|  | MANCHESTER ROAD PRIMARY | EE |  |  |  |  | 28.8673 | 28.1428 | 27.303 | 26.5765 | 24.6724 | 22.5214 | 20.0051 | 17.1214 | 14.9969 | 10.8082 | 9.1377 | 9.4959 | 29.7408 | 29.1459 | 28.4704 | 27.8949 | 26.5633 | 25.1316 | 23.4286 | 21.5286 | 20.0602 | 15.2775 | 10.699 | 3.6643 | 28.6571 | 28.0275 | 27.3 | 26.6663 | 25.0643 | 23.2255 | 21.0939 | 18.6235 | 16.8245 | 13.2969 | 11.9347 | 12.1949
|  | MANCHESTER ROAD PRIMARY | HT |  |  |  |  | 29.3959 | 28.7857 | 28.1163 | 27.051 | 24.9275 | 23.0041 | 20.8153 | 18.9153 | 17.0816 | 11.6653 | 8.7143 | 8.5449 | 30.3082 | 29.9224 | 29.5041 | 28.8071 | 27.603 | 26.5959 | 25.35 | 24.2224 | 23.1316 | 19.5265 | 17.6653 | 17.3724 | 29.1633 | 28.6592 | 28.1092 | 27.1888 | 25.4643 | 23.9122 | 22.0847 | 20.4826 | 18.9653 | 14.2 | 11.6061 | 11.5041
|  | MANCHESTER ROAD PRIMARY | HE |  |  |  |  | 29.2796 | 28.6949 | 28.0653 | 27.2163 | 25.403 | 23.4673 | 21.4673 | 18.85 | 16.6939 | 7.5235 | 3.6428 | 3.4602 | 30.0602 | 29.5826 | 29.0714 | 28.403 | 27.1826 | 25.903 | 24.6092 | 22.8816 | 21.2765 | 14.1357 | 10.3224 | 3.1959 | 29.0122 | 28.5041 | 27.9551 | 27.2163 | 25.6888 | 24.0602 | 22.2888 | 19.7826 | 17.399 | 8.5806 | 4.8949 | 4.7388
|  | MANCHESTER ROAD PRIMARY | CF |  |  |  |  | 29.8224 | 29.5959 | 29.3071 | 29.0153 | 28.6551 | 28.1755 | 27.2765 | 26.3102 | 24.8908 | 14.6041 | 7.9326 | 3.5684 | 30.3663 | 30.0694 | 29.7122 | 29.3082 | 28.802 | 28.1479 | 27.2061 | 26.2765 | 25.0337 | 16.2633 | 6.752 | -8.7367 | 29.5194 | 29.3082 | 29.0418 | 28.7704 | 28.4398 | 27.9898 | 27.2051 | 26.3826 | 24.8786 | 15.3173 | 8.9857 | 4.851
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON PRIMARY | MINIMUM HEADROOM | SU 07592 05256 | NO | NO | 2.182 | 5.7816 | 5.6296 | 5.4051 | 5.0663 | 4.8347 | 4.4306 | 4.3122 | 3.9041 | 3.7337 | 2.0469 | 0.96939 | 0.38673 | 4.4724 | 4.3061 | 4.1071 | 3.8031 | 3.5755 | 3.2673 | 3.3602 | 3.0878 | 2.9122 | 1.9316 | 0.68776 | -2.2633 | 4.1418 | 3.9469 | 3.7214 | 3.3908 | 3.1367 | 2.7398 | 2.7429 | 2.3592 | 2.1449 | 0.70102 | -0.27755 | -0.79796
|  | MANNINGTON PRIMARY | EE |  |  |  |  | 5.7816 | 5.6296 | 5.4051 | 5.0663 | 4.8347 | 4.4306 | 4.3796 | 4.001 | 3.7337 | 2.25 | 1.2163 | 0.51224 | 4.4724 | 4.3061 | 4.1071 | 3.8031 | 3.5755 | 3.2673 | 3.3602 | 3.0878 | 2.9122 | 1.9316 | 0.87143 | -0.64286 | 4.1418 | 3.9469 | 3.7214 | 3.3908 | 3.1367 | 2.7398 | 2.7439 | 2.3878 | 2.1449 | 0.87959 | -0.054082 | -0.68673
|  | MANNINGTON PRIMARY | HT |  |  |  |  | 5.8653 | 5.7367 | 5.5306 | 5.2286 | 5.0694 | 4.7051 | 4.3122 | 3.9041 | 3.8061 | 2.0469 | 0.96939 | 0.38673 | 4.5418 | 4.4612 | 4.3173 | 4.0888 | 4.0051 | 3.8133 | 3.5673 | 3.3071 | 3.3888 | 2.4786 | 2.0296 | 1.7755 | 4.2245 | 4.0765 | 3.8867 | 3.6041 | 3.448 | 3.1122 | 2.7429 | 2.3592 | 2.3092 | 0.70102 | -0.27755 | -0.79796
|  | MANNINGTON PRIMARY | HE |  |  |  |  | 5.8765 | 5.7673 | 5.5878 | 5.3133 | 5.1622 | 4.8929 | 4.5735 | 4.2429 | 4.2265 | 2.6816 | 1.6643 | 1.152 | 4.5327 | 4.4469 | 4.2959 | 4.0551 | 3.9531 | 3.7459 | 3.5041 | 3.2337 | 3.2939 | 2.101 | 1.051 | -0.39082 | 4.2582 | 4.1173 | 3.9439 | 3.6765 | 3.5347 | 3.2663 | 2.9612 | 2.6378 | 2.6551 | 1.252 | 0.35 | -0.10816
|  | MANNINGTON PRIMARY | CF |  |  |  |  | 5.9816 | 5.9194 | 5.7939 | 5.5867 | 5.498 | 5.4082 | 5.2633 | 5.1102 | 4.9459 | 4.1378 | 3.0653 | 1.9918 | 4.5827 | 4.5204 | 4.3918 | 4.1776 | 4.0755 | 3.9673 | 3.7878 | 3.5929 | 3.3776 | 2.4378 | 0.68776 | -2.2633 | 4.3561 | 4.2684 | 4.1469 | 3.9398 | 3.8306 | 3.7367 | 3.5878 | 3.4235 | 3.2388 | 2.55 | 1.549 | 0.65
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | MARKET PRIMARY | MINIMUM HEADROOM | SU 86479 04732 | NO | YES | 4.773 | 11.7733 | 11.2927 | 10.8151 | 10.3008 | 9.7488 | 9.3324 | 8.4345 | 7.5784 | 6.9253 | 3.3559 | 0.16204 | -1.7369 | 12.1851 | 11.8851 | 11.5627 | 11.2086 | 10.8218 | 10.4831 | 9.9351 | 9.2698 | 8.7127 | 5.5259 | 0.89837 | -9.9261 | 10.5261 | 10.2445 | 9.8282 | 9.3731 | 8.8873 | 8.5149 | 7.7271 | 6.8833 | 6.2761 | 3.2363 | 0.49959 | -1.1729
|  | MARKET PRIMARY | EE |  |  |  |  | 11.7733 | 11.2927 | 10.8151 | 10.3008 | 9.7488 | 9.3324 | 8.4345 | 7.5784 | 6.9253 | 3.3559 | 0.76102 | -1.4012 | 12.1851 | 11.8851 | 11.5627 | 11.2086 | 10.8218 | 10.4831 | 9.9351 | 9.2698 | 8.7127 | 5.5259 | 1.9688 | -3.7884 | 10.5261 | 10.2445 | 9.8282 | 9.3731 | 8.8873 | 8.5149 | 7.7271 | 6.8833 | 6.2761 | 3.2363 | 0.94347 | -0.95143
|  | MARKET PRIMARY | HT |  |  |  |  | 11.961 | 11.6784 | 11.2661 | 10.8743 | 10.4845 | 9.862 | 9.0651 | 8.2631 | 7.8437 | 3.4304 | 0.16204 | -1.7369 | 12.4524 | 12.2545 | 12.0178 | 11.7688 | 11.4953 | 11.1688 | 10.7433 | 10.2963 | 9.9535 | 7.8453 | 6.4678 | 5.6667 | 10.7169 | 10.5282 | 10.2455 | 9.9027 | 9.5629 | 9.0118 | 8.3169 | 7.6169 | 7.2516 | 3.3812 | 0.49959 | -1.1729
|  | MARKET PRIMARY | HE |  |  |  |  | 11.9427 | 11.6824 | 11.2957 | 10.9304 | 10.5763 | 10.0376 | 9.3243 | 8.6182 | 8.2967 | 4.7314 | 2.1508 | 0.94265 | 12.4076 | 12.1841 | 11.9259 | 11.6504 | 11.3484 | 10.9831 | 10.5004 | 9.9953 | 9.5892 | 6.5422 | 2.8657 | -2.5476 | 10.6976 | 10.5027 | 10.2516 | 9.9261 | 9.6088 | 9.1241 | 8.4955 | 7.872 | 7.5843 | 4.4302 | 2.1527 | 1.1078
|  | MARKET PRIMARY | CF |  |  |  |  | 12.1171 | 11.9773 | 11.8212 | 11.6018 | 11.3651 | 11.1916 | 10.8406 | 10.4967 | 10.1927 | 8.1651 | 5.7233 | 3.3978 | 12.6198 | 12.479 | 12.33 | 12.1718 | 11.9739 | 11.7678 | 11.332 | 10.8351 | 10.329 | 6.9453 | 0.89837 | -9.9261 | 10.8588 | 10.7261 | 10.6047 | 10.4812 | 10.319 | 10.1618 | 9.8618 | 9.5669 | 9.2976 | 7.5486 | 5.4088 | 3.3598
MELKSHAM GSP | WEST GRAFTON BSP | MARLBOROUGH SOUTH PRIMARY | MINIMUM HEADROOM | SU 19293 68264 | NO | NO | 1.533 | 1.9235 | 1.5847 | 1.1776 | 0.66735 | 0.53163 | -0.010204 | -0.60102 | -1.2122 | -1.6449 | -4.0459 | -5.9398 | -7.1102 | 4.7663 | 4.499 | 4.1643 | 3.7643 | 3.7347 | 3.3337 | 2.8765 | 2.4102 | 2.1102 | 0.39694 | -1.7214 | -6.8684 | 1.7827 | 1.4388 | 1.0122 | 0.49388 | 0.42347 | -0.11633 | -0.71939 | -1.3245 | -1.7153 | -3.7133 | -5.2867 | -6.2439
|  | MARLBOROUGH SOUTH PRIMARY | EE |  |  |  |  | 1.9235 | 1.5847 | 1.1776 | 0.66735 | 0.53163 | -0.010204 | -0.60102 | -1.2122 | -1.6449 | -4.0459 | -5.648 | -6.8255 | 4.7663 | 4.499 | 4.1643 | 3.7643 | 3.7347 | 3.3337 | 2.8765 | 2.4102 | 2.1102 | 0.39694 | -1.4316 | -4.1704 | 1.7827 | 1.4388 | 1.0122 | 0.49388 | 0.42347 | -0.11633 | -0.71939 | -1.3245 | -1.7153 | -3.7133 | -5.0112 | -6.0031
|  | MARLBOROUGH SOUTH PRIMARY | HT |  |  |  |  | 2.102 | 1.8102 | 1.4469 | 1.0388 | 0.70306 | 0.19184 | -0.061224 | -0.57755 | -1.1143 | -4.001 | -5.9398 | -7.1102 | 5.0122 | 4.8347 | 4.6031 | 4.3714 | 4.1327 | 3.8235 | 3.7939 | 3.4816 | 3.15 | 1.5714 | 0.65306 | 0.15 | 1.9888 | 1.7265 | 1.3908 | 1.0194 | 0.67551 | 0.18061 | 0.013265 | -0.48571 | -1.0061 | -3.649 | -5.2867 | -6.2439
|  | MARLBOROUGH SOUTH PRIMARY | HE |  |  |  |  | 2.1194 | 1.851 | 1.5276 | 1.1622 | 0.79694 | 0.34184 | -0.15918 | -0.30102 | -0.75714 | -3.3357 | -4.9153 | -5.6816 | 4.9714 | 4.7765 | 4.5367 | 4.2959 | 4.0143 | 3.6806 | 3.299 | 3.2776 | 2.9204 | 0.85408 | -1.0122 | -3.5735 | 2.002 | 1.7612 | 1.4602 | 1.1235 | 0.76531 | 0.32347 | -0.17857 | -0.23061 | -0.67755 | -3.0092 | -4.3184 | -4.9653
|  | MARLBOROUGH SOUTH PRIMARY | CF |  |  |  |  | 2.3071 | 2.1449 | 1.9755 | 1.7918 | 1.6327 | 1.4163 | 1.1439 | 0.82857 | 0.81939 | -0.95918 | -2.652 | -4.2541 | 5.0663 | 4.9194 | 4.75 | 4.5582 | 4.3806 | 4.1347 | 3.8276 | 3.4888 | 3.4745 | 1.349 | -1.7214 | -6.8684 | 2.1714 | 2.0224 | 1.8622 | 1.6776 | 1.5143 | 1.2878 | 1.0031 | 0.67551 | 0.73265 | -1.0153 | -2.502 | -3.798
NURSLING GSP | ROWNHAMS BSP | MAYBUSH PRIMARY | MINIMUM HEADROOM | SU 38426 14930 | NO | YES | 4.799 | 1.7666 | 1.1105 | 0.84722 | 0.16559 | -0.59768 | -1.7375 | -3.1436 | -4.5324 | -5.5467 | -10.1354 | -14.1834 | -16.2681 | 15.3789 | 14.8176 | 14.5605 | 13.9421 | 13.2411 | 12.3431 | 11.2615 | 10.1595 | 9.3054 | 4.7717 | -1.8742 | -17.966 | 2.2875 | 1.6753 | 1.3732 | 0.71814 | -0.025739 | -1.1247 | -2.4645 | -3.787 | -4.7737 | -9.0808 | -12.6502 | -14.5339
|  | MAYBUSH PRIMARY | EE |  |  |  |  | 1.7666 | 1.1105 | 0.84722 | 0.16559 | -0.59768 | -1.7375 | -3.1436 | -4.5324 | -5.5467 | -10.1354 | -13.465 | -16.0885 | 15.3789 | 14.8176 | 14.5605 | 13.9421 | 13.2411 | 12.3431 | 11.2615 | 10.1595 | 9.3054 | 4.7717 | -0.51604 | -8.9538 | 2.2875 | 1.6753 | 1.3732 | 0.71814 | -0.025739 | -1.1247 | -2.4645 | -3.787 | -4.7737 | -9.0808 | -11.9961 | -14.3931
|  | MAYBUSH PRIMARY | HT |  |  |  |  | 2.2033 | 1.7084 | 1.2115 | 0.60844 | -0.18441 | -0.79156 | -1.8967 | -2.9538 | -4.012 | -10.1314 | -14.1834 | -16.2681 | 15.8727 | 15.5268 | 15.1891 | 14.7452 | 14.2084 | 13.9125 | 13.235 | 12.5666 | 11.8931 | 8.387 | 6.3074 | 5.3758 | 2.6753 | 2.2222 | 1.7569 | 1.1692 | 0.42222 | -0.22064 | -1.2798 | -2.2982 | -3.3186 | -9.0104 | -12.6502 | -14.5339
|  | MAYBUSH PRIMARY | HE |  |  |  |  | 2.2493 | 1.8146 | 1.3962 | 0.89212 | 0.31457 | -0.022167 | -0.91809 | -1.8354 | -2.7752 | -7.3834 | -10.4599 | -11.7252 | 15.7697 | 15.387 | 15.0084 | 14.536 | 13.985 | 13.6289 | 12.8962 | 12.1146 | 11.2993 | 6.5595 | 1.334 | -6.5691 | 2.71 | 2.3151 | 1.9171 | 1.4406 | 0.88242 | 0.48447 | -0.38288 | -1.2676 | -2.1696 | -6.5104 | -9.2308 | -10.3584
|  | MAYBUSH PRIMARY | CF |  |  |  |  | 2.5564 | 2.3197 | 2.035 | 1.7758 | 1.4431 | 1.0748 | 0.60742 | 0.56355 | 0.065588 | -3.2181 | -6.2018 | -9.0109 | 15.9166 | 15.6391 | 15.3013 | 14.9421 | 14.4778 | 13.9197 | 13.2625 | 12.8625 | 12.1319 | 6.885 | -1.8742 | -17.966 | 2.9896 | 2.8253 | 2.562 | 2.3212 | 2.0171 | 1.6702 | 1.2375 | 1.1345 | 0.66712 | -2.4757 | -5.4074 | -7.988
MELKSHAM GSP | NORRINGTON BSP | MELKSHAM TOWN PRIMARY | MINIMUM HEADROOM | ST 90170 64096 | NO | YES | 8.264 | 13.3981 | 12.8522 | 11.8665 | 10.6073 | 9.1614 | 7.5522 | 5.8512 | 4.2777 | 3.242 | -1.7927 | -6.108 | -8.6611 | 15.8389 | 15.4736 | 14.8348 | 14.1134 | 13.1859 | 12.1491 | 11.0022 | 9.892 | 9.1604 | 5.4073 | 0.6777 | -10.6294 | 13.5379 | 13.1522 | 12.1614 | 11.0399 | 9.7614 | 8.3175 | 6.7593 | 5.2961 | 4.445 | 0.070555 | -3.7203 | -5.8917
|  | MELKSHAM TOWN PRIMARY | EE |  |  |  |  | 13.3981 | 12.8522 | 11.8665 | 10.6073 | 9.1614 | 7.5522 | 5.8512 | 4.2777 | 3.242 | -1.5417 | -5.2509 | -8.1254 | 15.8389 | 15.4736 | 14.8348 | 14.1134 | 13.1859 | 12.1491 | 11.0022 | 9.892 | 9.1604 | 5.4073 | 1.3563 | -4.5937 | 13.5379 | 13.1522 | 12.1614 | 11.0399 | 9.7614 | 8.3175 | 6.7593 | 5.2961 | 4.445 | 0.23586 | -2.9754 | -5.455
|  | MELKSHAM TOWN PRIMARY | HT |  |  |  |  | 13.8175 | 13.2399 | 12.0267 | 11.0746 | 9.6552 | 8.2195 | 6.9297 | 5.6787 | 4.4195 | -1.7927 | -6.108 | -8.6611 | 16.2022 | 15.7971 | 15.1879 | 14.7338 | 14.0318 | 13.3277 | 12.6818 | 11.9971 | 11.2461 | 7.7634 | 5.6961 | 4.5501 | 14.0767 | 13.3869 | 12.3257 | 11.7073 | 10.4899 | 9.2236 | 8.0542 | 6.9022 | 5.744 | 0.070555 | -3.7203 | -5.8917
|  | MELKSHAM TOWN PRIMARY | HE |  |  |  |  | 13.7563 | 13.1848 | 12.2614 | 11.4971 | 10.2389 | 8.9736 | 7.644 | 6.4308 | 5.2777 | -0.20291 | -4.1039 | -6.0396 | 16.1022 | 15.6399 | 15.042 | 14.5869 | 13.8634 | 13.1134 | 12.3063 | 11.4808 | 10.6063 | 6.0104 | 1.7257 | -3.8815 | 14.1022 | 13.4359 | 12.5216 | 12.0461 | 10.9552 | 9.8399 | 8.6532 | 7.5481 | 6.4899 | 1.444 | -1.9754 | -3.606
|  | MELKSHAM TOWN PRIMARY | CF |  |  |  |  | 14.1848 | 13.8134 | 13.345 | 12.7808 | 12.5624 | 12.0961 | 11.5318 | 10.8144 | 10.0052 | 5.1604 | 1.0838 | -2.6264 | 16.293 | 15.9226 | 15.5216 | 15.1134 | 14.8583 | 14.4124 | 13.8838 | 13.2665 | 12.5114 | 7.4604 | 0.6777 | -10.6294 | 14.4675 | 13.9869 | 13.4338 | 12.893 | 12.8604 | 12.4246 | 11.895 | 11.2389 | 10.5104 | 6.1583 | 2.591 | -0.66924
NURSLING GSP |  | MARCHWOOD PRIMARY | MINIMUM HEADROOM | SU 39234 11008 | NO | NO | 1.124 | 18.222 | 18.0394 | 17.8526 | 17.72 | 17.4771 | 17.1802 | 16.8384 | 16.521 | 16.2812 | 14.7996 | 13.9884 | 13.8006 | 17.6751 | 17.4812 | 17.2965 | 17.1822 | 17.0118 | 16.8282 | 16.5924 | 16.3577 | 16.1445 | 15.122 | 13.8884 | 10.8833 | 18.0363 | 17.873 | 17.6873 | 17.5353 | 17.3088 | 17.0496 | 16.7302 | 16.4128 | 16.1302 | 14.7292 | 13.9812 | 13.8159
|  | MARCHWOOD PRIMARY | EE |  |  |  |  | 18.3108 | 18.0445 | 17.8526 | 17.721 | 17.4771 | 17.1802 | 16.8384 | 16.521 | 16.3567 | 15.5006 | 14.7945 | 14.2261 | 17.7282 | 17.4812 | 17.2965 | 17.1904 | 17.0312 | 16.8424 | 16.5996 | 16.3618 | 16.2261 | 15.4241 | 14.4179 | 12.8363 | 18.1282 | 17.8843 | 17.6884 | 17.5465 | 17.3465 | 17.1047 | 16.822 | 16.5516 | 16.4016 | 15.6373 | 15.0241 | 14.5322
|  | MARCHWOOD PRIMARY | HT |  |  |  |  | 18.222 | 18.0394 | 17.9628 | 17.8659 | 17.6516 | 17.3843 | 17.0792 | 16.8016 | 16.6271 | 15.4782 | 14.6853 | 14.2098 | 17.6751 | 17.5292 | 17.4853 | 17.4302 | 17.3098 | 17.1751 | 17.0118 | 16.8577 | 16.7588 | 16.12 | 15.7516 | 15.5435 | 18.0363 | 17.873 | 17.8077 | 17.7292 | 17.5608 | 17.3373 | 17.0873 | 16.8435 | 16.6822 | 15.6404 | 14.9445 | 14.5353
|  | MARCHWOOD PRIMARY | HE |  |  |  |  | 18.3353 | 18.072 | 17.8577 | 17.72 | 17.5128 | 17.2547 | 16.9149 | 16.5782 | 16.2812 | 14.7996 | 13.9884 | 13.8006 | 17.7445 | 17.4904 | 17.2965 | 17.1822 | 17.0118 | 16.8282 | 16.5924 | 16.3577 | 16.1445 | 15.122 | 14.423 | 12.9414 | 18.17 | 17.9067 | 17.6873 | 17.5353 | 17.3088 | 17.0496 | 16.7302 | 16.4128 | 16.1302 | 14.7292 | 13.9812 | 13.8159
|  | MARCHWOOD PRIMARY | CF |  |  |  |  | 18.4394 | 18.3965 | 18.2037 | 18.0322 | 17.8955 | 17.7445 | 17.5802 | 17.3975 | 17.2404 | 16.1016 | 14.9771 | 14.0914 | 17.821 | 17.7608 | 17.5649 | 17.4037 | 17.27 | 17.1149 | 16.9649 | 16.7975 | 16.6537 | 15.6139 | 13.8884 | 10.8833 | 18.2506 | 18.2108 | 18.0271 | 17.8822 | 17.7394 | 17.5833 | 17.4077 | 17.2139 | 17.0455 | 15.9455 | 14.8863 | 14.0659
LOVEDEAN GSP | HAVANT BSP | MEYRICK ROAD PRIMARY | MINIMUM HEADROOM | SU 70849 06469 | NO | YES | 1.294 | 6.752 | 5.9429 | 5.1276 | 4.3612 | 3.501 | 2.1255 | 0.61735 | -0.86429 | -1.8878 | -6.5265 | -10.9857 | -12.0837 | 12.1153 | 11.6918 | 11.1378 | 10.551 | 9.9082 | 9.0867 | 8.0296 | 6.8857 | 6.1061 | 1.85 | -6.3276 | -22.8286 | 7.8827 | 7.2398 | 6.4418 | 5.6602 | 4.7888 | 3.5153 | 2.0918 | 0.68878 | -0.2102 | -4.049 | -7.7388 | -8.6092
|  | MEYRICK ROAD PRIMARY | EE |  |  |  |  | 6.752 | 5.9429 | 5.1276 | 4.3612 | 3.501 | 2.1255 | 0.61735 | -0.86429 | -1.8878 | -6.402 | -10.3939 | -10.9061 | 12.1153 | 11.6918 | 11.1378 | 10.551 | 9.9082 | 9.0867 | 8.0296 | 6.8857 | 6.1061 | 1.85 | -3.7112 | -11.448 | 7.8827 | 7.2398 | 6.4418 | 5.6602 | 4.7888 | 3.5153 | 2.0918 | 0.68878 | -0.2102 | -4.049 | -7.2551 | -7.6867
|  | MEYRICK ROAD PRIMARY | HT |  |  |  |  | 6.9531 | 6.0918 | 5.3031 | 4.9214 | 4.1776 | 3.0265 | 1.8051 | 0.54694 | -0.68061 | -6.5265 | -10.9857 | -12.0837 | 12.5082 | 12.048 | 11.5969 | 11.5224 | 11.0908 | 10.5469 | 9.9296 | 9.2745 | 8.599 | 5.3755 | 3.3133 | 2.6735 | 8.2378 | 7.4796 | 6.7378 | 6.4704 | 5.7694 | 4.7357 | 3.6112 | 2.4418 | 1.2806 | -4.0469 | -7.7388 | -8.6092
|  | MEYRICK ROAD PRIMARY | HE |  |  |  |  | 7.1714 | 6.2051 | 5.4714 | 5.1531 | 4.4776 | 3.4531 | 2.3541 | 1.2378 | 0.15102 | -4.5704 | -8.402 | -9.4571 | 12.5959 | 12.0031 | 11.5469 | 11.4653 | 11.0276 | 10.3337 | 9.5255 | 8.6643 | 7.7439 | 2.8102 | -2.8143 | -10.7194 | 8.4173 | 7.5673 | 6.8745 | 6.6571 | 6.0214 | 5.0929 | 4.0714 | 3.0173 | 1.9755 | -2.3969 | -5.4602 | -6.2867
|  | MEYRICK ROAD PRIMARY | CF |  |  |  |  | 7.6184 | 7.0418 | 6.4051 | 5.9888 | 5.8571 | 5.3847 | 4.8643 | 4.3204 | 3.8133 | 0.40714 | -4.4398 | -8.3173 | 12.7653 | 12.3755 | 11.899 | 11.5388 | 11.4959 | 10.9 | 10.2102 | 9.4847 | 8.7276 | 3.3357 | -6.3276 | -22.8286 | 8.7949 | 8.2857 | 7.6939 | 7.2694 | 7.2408 | 6.7888 | 6.2704 | 5.7224 | 5.1929 | 1.8888 | -2.2561 | -5.4296
MELKSHAM GSP | ANDOVER BSP | MIDDLE WALLOP PRIMARY | MINIMUM HEADROOM | SU 30984 40155 | YES | NO | 0.705 | 3.4171 | 3.3171 | 3.2253 | 3.1048 | 2.9763 | 2.8304 | 2.6222 | 2.4059 | 2.2814 | 1.5742 | 1.2191 | 1.0181 | 4.1811 | 4.1219 | 4.0709 | 3.9985 | 3.927 | 3.8444 | 3.7321 | 3.6199 | 3.5423 | 3.1066 | 2.7219 | 1.6964 | 3.2031 | 3.1204 | 3.0327 | 2.9245 | 2.8071 | 2.6684 | 2.4776 | 2.2878 | 2.1439 | 1.4418 | 1.1133 | 0.94082
|  | MIDDLE WALLOP PRIMARY | EE |  |  |  |  | 3.4171 | 3.3171 | 3.2253 | 3.1048 | 2.9763 | 2.8304 | 2.6222 | 2.4059 | 2.2814 | 1.6324 | 1.3069 | 1.1253 | 4.1811 | 4.1219 | 4.0709 | 3.9985 | 3.927 | 3.8444 | 3.7321 | 3.6199 | 3.5423 | 3.1066 | 2.7658 | 2.3097 | 3.2031 | 3.1204 | 3.0327 | 2.9245 | 2.8071 | 2.6684 | 2.4776 | 2.2878 | 2.1439 | 1.5184 | 1.3051 | 1.198
|  | MIDDLE WALLOP PRIMARY | HT |  |  |  |  | 3.4651 | 3.3753 | 3.3008 | 3.2079 | 3.1069 | 2.9804 | 2.811 | 2.6355 | 2.4936 | 1.6844 | 1.2773 | 1.0181 | 4.2199 | 4.175 | 4.1352 | 4.0893 | 4.0352 | 3.975 | 3.8893 | 3.7995 | 3.7301 | 3.323 | 3.1301 | 3.0066 | 3.2592 | 3.1857 | 3.1184 | 3.0398 | 2.9541 | 2.8398 | 2.6918 | 2.5296 | 2.3694 | 1.5847 | 1.2357 | 1.0184
|  | MIDDLE WALLOP PRIMARY | HE |  |  |  |  | 3.4702 | 3.3834 | 3.313 | 3.2242 | 3.1273 | 3.0151 | 2.8599 | 2.6987 | 2.5191 | 1.5742 | 1.2191 | 1.0304 | 4.2138 | 4.1658 | 4.1209 | 4.0658 | 4.0087 | 3.9393 | 3.8485 | 3.7526 | 3.673 | 3.1281 | 2.7648 | 2.3097 | 3.2622 | 3.1918 | 3.1235 | 3.0388 | 2.9408 | 2.8337 | 2.6714 | 2.4949 | 2.3265 | 1.4418 | 1.1133 | 0.94082
|  | MIDDLE WALLOP PRIMARY | CF |  |  |  |  | 3.5059 | 3.4477 | 3.3926 | 3.3171 | 3.2467 | 3.1671 | 3.1038 | 3.011 | 2.9099 | 2.3293 | 1.7059 | 1.2069 | 4.2342 | 4.1974 | 4.1628 | 4.1148 | 4.0658 | 4.0117 | 3.9566 | 3.8872 | 3.8158 | 3.3505 | 2.7219 | 1.6964 | 3.2949 | 3.2449 | 3.199 | 3.1367 | 3.0786 | 3.0102 | 2.95 | 2.8704 | 2.7837 | 2.1449 | 1.5622 | 1.102
FLEET-BRAMLEY GSP | FERNHURST BSP | MIDHURST PRIMARY | MINIMUM HEADROOM | SU 88127 19555 | NO | NO | 2.687 | 16.8051 | 16.4622 | 16.0276 | 15.5469 | 15.5286 | 14.9255 | 14.2347 | 13.5265 | 13.0143 | 10.298 | 8.2173 | 6.9714 | 18.4684 | 18.1888 | 17.8296 | 17.4306 | 17.4653 | 17.0286 | 16.5092 | 15.9847 | 15.6398 | 13.749 | 11.5061 | 5.8806 | 16.8765 | 16.5408 | 16.1112 | 15.6306 | 15.6245 | 15.0378 | 14.3673 | 13.6898 | 13.2184 | 10.8571 | 9.0643 | 7.9969
|  | MIDHURST PRIMARY | EE |  |  |  |  | 16.8051 | 16.4622 | 16.0276 | 15.5469 | 15.5286 | 14.9255 | 14.2347 | 13.5265 | 13.0143 | 10.298 | 8.5622 | 7.3133 | 18.4684 | 18.1888 | 17.8296 | 17.4306 | 17.4653 | 17.0286 | 16.5092 | 15.9847 | 15.6398 | 13.749 | 11.7306 | 8.7776 | 16.8765 | 16.5408 | 16.1112 | 15.6306 | 15.6245 | 15.0378 | 14.3673 | 13.6898 | 13.2184 | 10.8571 | 9.3694 | 8.2857
|  | MIDHURST PRIMARY | HT |  |  |  |  | 17.0735 | 16.8153 | 16.4857 | 16.1908 | 15.8102 | 15.2418 | 14.9704 | 14.3571 | 13.7143 | 10.3776 | 8.2173 | 6.9714 | 18.7459 | 18.5745 | 18.3449 | 18.1449 | 17.8735 | 17.5143 | 17.5082 | 17.1418 | 16.7531 | 14.9408 | 13.9429 | 13.3724 | 17.1327 | 16.8816 | 16.5663 | 16.2765 | 15.9071 | 15.3561 | 15.148 | 14.5776 | 13.9786 | 10.951 | 9.0643 | 7.9969
|  | MIDHURST PRIMARY | HE |  |  |  |  | 17.0786 | 16.8357 | 16.5276 | 16.2602 | 15.9153 | 15.4173 | 15.2194 | 14.6878 | 14.1327 | 11.1418 | 9.4449 | 8.6898 | 18.7031 | 18.5153 | 18.2673 | 18.048 | 17.7602 | 17.3939 | 17.3633 | 16.9816 | 16.5724 | 14.2776 | 12.2286 | 9.5041 | 17.1378 | 16.901 | 16.6061 | 16.3388 | 16.0031 | 15.5184 | 15.3735 | 14.8735 | 14.3531 | 11.6571 | 10.1908 | 9.5541
|  | MIDHURST PRIMARY | CF |  |  |  |  | 17.2469 | 17.0786 | 16.8684 | 16.6408 | 16.4551 | 16.2 | 15.8939 | 15.5612 | 15.6602 | 13.7561 | 11.8051 | 9.9949 | 18.7949 | 18.6449 | 18.45 | 18.2367 | 18.0367 | 17.7673 | 17.4388 | 17.0847 | 17.1306 | 14.8959 | 11.5061 | 5.8806 | 17.3061 | 17.1459 | 16.9469 | 16.7265 | 16.5469 | 16.2939 | 15.9827 | 15.65 | 15.7684 | 13.9347 | 12.202 | 10.6663
AXMINSTER GSP | YEOVIL BSP | MILBORNE PORT PRIMARY | MINIMUM HEADROOM | ST 67929 19741 | YES | NO | 0.353 | 2.5056 | 2.3699 | 2.2709 | 2.1189 | 2.0066 | 1.7811 | 1.5168 | 1.2597 | 1.1148 | 0.35459 | -0.2301 | -0.58929 | 0.82551 | 0.75408 | 0.69286 | 0.6102 | 0.54796 | 0.38673 | 0.19592 | 0.0040816 | -0.10204 | -0.66429 | -1.4337 | -3.2582 | 1.1265 | 1.0408 | 0.96939 | 0.87653 | 0.80816 | 0.64694 | 0.46837 | 0.29286 | 0.16837 | -0.56224 | -1.1255 | -1.4745
|  | MILBORNE PORT PRIMARY | EE |  |  |  |  | 2.5056 | 2.3699 | 2.2709 | 2.1189 | 2.0066 | 1.7811 | 1.5168 | 1.2597 | 1.1148 | 0.35459 | -0.14949 | -0.52194 | 0.82551 | 0.75408 | 0.69286 | 0.6102 | 0.54796 | 0.38673 | 0.19592 | 0.0040816 | -0.10204 | -0.66429 | -1.2816 | -2.2429 | 1.1265 | 1.0408 | 0.96939 | 0.87653 | 0.80816 | 0.64694 | 0.46837 | 0.29286 | 0.16837 | -0.5602 | -1.0663 | -1.4224
|  | MILBORNE PORT PRIMARY | HT |  |  |  |  | 2.5842 | 2.5036 | 2.4087 | 2.2954 | 2.2189 | 2.0291 | 1.8148 | 1.6434 | 1.4209 | 0.35867 | -0.2301 | -0.58929 | 0.88571 | 0.8449 | 0.80204 | 0.74694 | 0.70918 | 0.62041 | 0.52245 | 0.44592 | 0.32143 | -0.28265 | -0.55918 | -0.71939 | 1.1643 | 1.1031 | 1.0388 | 0.96429 | 0.90204 | 0.75204 | 0.58878 | 0.45714 | 0.29082 | -0.56224 | -1.1255 | -1.4745
|  | MILBORNE PORT PRIMARY | HE |  |  |  |  | 2.5883 | 2.5097 | 2.4199 | 2.3097 | 2.2383 | 2.075 | 1.8852 | 1.7383 | 1.5434 | 0.56071 | 0.067857 | -0.16684 | 0.86327 | 0.81633 | 0.76224 | 0.69592 | 0.64592 | 0.54898 | 0.44184 | 0.35 | 0.21837 | -0.55408 | -1.1898 | -2.0878 | 1.1653 | 1.1061 | 1.0439 | 0.96939 | 0.90816 | 0.78163 | 0.63878 | 0.52653 | 0.38163 | -0.4398 | -0.9398 | -1.1673
|  | MILBORNE PORT PRIMARY | CF |  |  |  |  | 2.6515 | 2.5791 | 2.5321 | 2.4679 | 2.3944 | 2.3413 | 2.2434 | 2.1393 | 2.0291 | 1.3689 | 0.77296 | 0.26173 | 0.89082 | 0.84286 | 0.8051 | 0.75408 | 0.69694 | 0.63776 | 0.55102 | 0.46327 | 0.37041 | -0.36633 | -1.4337 | -3.2582 | 1.2112 | 1.1684 | 1.1327 | 1.0898 | 1.0408 | 0.9949 | 0.93061 | 0.86429 | 0.79082 | 0.32857 | -0.19286 | -0.69592
FLEET-BRAMLEY GSP | ALDERSHOT BSP | MILFORD PRIMARY | MINIMUM HEADROOM | SU 94719 43018 | NO | YES | 4.416 | 9.9405 | 9.415 | 8.7374 | 8.4048 | 7.7915 | 7.0323 | 6.1844 | 5.4242 | 4.9119 | 1.813 | -0.60541 | -2.0207 | 13.466 | 13.0742 | 12.6038 | 12.5211 | 12.1007 | 11.6038 | 11.0313 | 10.4803 | 10.1487 | 8.0915 | 5.6242 | -0.48092 | 10.4293 | 9.9446 | 9.3313 | 9.0721 | 8.5099 | 7.8119 | 7.0262 | 6.314 | 5.8466 | 3.2211 | 1.216 | 0.025204
|  | MILFORD PRIMARY | EE |  |  |  |  | 9.9405 | 9.415 | 8.7374 | 8.4048 | 7.7915 | 7.0323 | 6.1844 | 5.4242 | 4.9119 | 2.016 | -0.14827 | -1.784 | 13.466 | 13.0742 | 12.6038 | 12.5211 | 12.1007 | 11.6038 | 11.0313 | 10.4803 | 10.1487 | 8.0915 | 5.8344 | 2.5854 | 10.4293 | 9.9446 | 9.3313 | 9.0721 | 8.5099 | 7.8119 | 7.0262 | 6.314 | 5.8466 | 3.3732 | 1.617 | 0.23541
|  | MILFORD PRIMARY | HT |  |  |  |  | 10.1732 | 9.7395 | 9.213 | 8.563 | 7.9721 | 7.5538 | 6.7895 | 6.1017 | 5.3987 | 1.813 | -0.60541 | -2.0207 | 13.7477 | 13.4783 | 13.1936 | 12.8242 | 12.4691 | 12.3936 | 11.9926 | 11.6109 | 11.2191 | 9.3538 | 8.2732 | 7.6874 | 10.664 | 10.2742 | 9.8099 | 9.2344 | 8.6987 | 8.3926 | 7.7109 | 7.0803 | 6.4313 | 3.2211 | 1.216 | 0.025204
|  | MILFORD PRIMARY | HE |  |  |  |  | 10.1966 | 9.7772 | 9.2752 | 8.6426 | 8.0783 | 7.7895 | 7.1599 | 6.6007 | 6.0303 | 2.9344 | 0.84561 | -0.16561 | 13.6977 | 13.4028 | 13.0905 | 12.6956 | 12.3089 | 12.1966 | 11.7885 | 11.3864 | 10.967 | 8.5477 | 6.2885 | 3.2905 | 10.6844 | 10.3048 | 9.866 | 9.3068 | 8.7936 | 8.5946 | 8.0221 | 7.4997 | 6.965 | 4.1783 | 2.4558 | 1.6497
|  | MILFORD PRIMARY | CF |  |  |  |  | 10.3732 | 10.0997 | 9.6905 | 9.2579 | 8.865 | 8.5242 | 8.1272 | 8.2497 | 7.9793 | 5.9915 | 3.864 | 1.7977 | 13.766 | 13.5538 | 13.2599 | 12.9711 | 12.6538 | 12.3272 | 11.9364 | 11.9456 | 11.6232 | 9.264 | 5.6242 | -0.48092 | 10.8466 | 10.6048 | 10.2446 | 9.8742 | 9.517 | 9.2017 | 8.8354 | 8.964 | 8.7048 | 6.8313 | 4.9242 | 3.1936
MANNINGTON GSP | ARNEWOOD BSP | MILFORD-ON-SEA PRIMARY | MINIMUM HEADROOM | SZ 28252 93347 | NO | NO | 2.134 | 27.859 | 27.3386 | 26.7223 | 26.4345 | 25.8172 | 24.9254 | 23.9376 | 22.9029 | 22.156 | 18.7111 | 16.0784 | 14.5764 | 28.2539 | 27.8611 | 27.4101 | 27.305 | 26.8631 | 26.2937 | 25.6458 | 24.9631 | 24.5111 | 22.3611 | 19.5111 | 12.456 | 27.0886 | 26.5641 | 25.9519 | 25.8448 | 25.2682 | 24.4672 | 23.557 | 22.608 | 21.957 | 18.9988 | 16.6978 | 15.4509
|  | MILFORD-ON-SEA PRIMARY | EE |  |  |  |  | 27.859 | 27.3386 | 26.7223 | 26.4345 | 25.8172 | 24.9254 | 23.9376 | 22.9029 | 22.156 | 19.0315 | 16.6886 | 14.8396 | 28.2539 | 27.8611 | 27.4101 | 27.305 | 26.8631 | 26.2937 | 25.6458 | 24.9631 | 24.5111 | 22.3611 | 19.855 | 16.1396 | 27.0886 | 26.5641 | 25.9519 | 25.8448 | 25.2682 | 24.4672 | 23.557 | 22.608 | 21.957 | 19.259 | 17.2386 | 15.6784
|  | MILFORD-ON-SEA PRIMARY | HT |  |  |  |  | 28.0733 | 27.6192 | 27.1386 | 26.5703 | 25.9631 | 25.3825 | 24.4662 | 23.5192 | 22.657 | 18.7111 | 16.0784 | 14.5764 | 28.5315 | 28.2539 | 27.9886 | 27.6529 | 27.2896 | 27.1509 | 26.6774 | 26.1835 | 25.7121 | 23.7019 | 22.5713 | 21.9754 | 27.3723 | 26.9519 | 26.5254 | 26.006 | 25.4376 | 25.0407 | 24.2233 | 23.3784 | 22.5948 | 18.9988 | 16.6978 | 15.4509
|  | MILFORD-ON-SEA PRIMARY | HE |  |  |  |  | 28.1141 | 27.6988 | 27.2468 | 26.707 | 26.1488 | 25.7499 | 24.9876 | 24.1641 | 23.4009 | 20.0937 | 17.7427 | 16.5815 | 28.4825 | 28.1866 | 27.8978 | 27.5305 | 27.1376 | 26.9988 | 26.5162 | 25.9845 | 25.4641 | 22.8886 | 20.3325 | 16.8978 | 27.4019 | 27.009 | 26.608 | 26.1111 | 25.5876 | 25.3509 | 24.6672 | 23.9305 | 23.2345 | 20.2325 | 18.1845 | 17.2366
|  | MILFORD-ON-SEA PRIMARY | CF |  |  |  |  | 28.3121 | 28.0621 | 27.7152 | 27.3754 | 27.0243 | 26.6866 | 26.6141 | 26.2366 | 25.8233 | 23.4213 | 20.9835 | 18.6703 | 28.559 | 28.3499 | 28.0723 | 27.8152 | 27.4968 | 27.1519 | 27.0682 | 26.6815 | 26.2662 | 23.5652 | 19.5111 | 12.456 | 27.5601 | 27.3223 | 26.9907 | 26.6907 | 26.3488 | 26.006 | 26.0682 | 25.708 | 25.3192 | 23.0662 | 20.9509 | 18.9692
MANNINGTON GSP | MANNINGTON BSP | MILL LANE PRIMARY | MINIMUM HEADROOM | SU 14691 05633 | NO | NO | 5.928 | 6.8972 | 5.938 | 14.5738 | 13.4391 | 12.1197 | 10.5309 | 8.6319 | 6.7676 | 5.2156 | -3.5191 | -7.4038 | -8.3507 | 10.9227 | 10.237 | 19.7227 | 18.8768 | 17.9054 | 16.784 | 15.4248 | 14.1003 | 13.0105 | 6.5401 | 3.8176 | -2.4885 | 7.337 | 6.5636 | 15.0401 | 13.9503 | 12.6942 | 11.1901 | 9.388 | 7.6238 | 6.1574 | -2.1232 | -5.7824 | -6.6466
|  | MILL LANE PRIMARY | EE |  |  |  |  | 6.8972 | 5.938 | 14.5738 | 13.4391 | 12.1197 | 10.5309 | 8.6319 | 6.7676 | 5.2156 | -0.69358 | -2.2671 | -4.2701 | 10.9227 | 10.237 | 19.7227 | 18.8768 | 17.9054 | 16.784 | 15.4248 | 14.1003 | 13.0105 | 8.8748 | 6.9574 | 2.5891 | 7.337 | 6.5636 | 15.0401 | 13.9503 | 12.6942 | 11.1901 | 9.388 | 7.6238 | 6.1574 | 0.64315 | -0.97726 | -2.8987
|  | MILL LANE PRIMARY | HT |  |  |  |  | 7.735 | 7.1738 | 15.9962 | 15.1911 | 14.3329 | 13.0789 | 11.6115 | 10.1013 | 8.4442 | 1.2329 | -2.2803 | -4.2589 | 11.4983 | 11.1391 | 20.7993 | 20.2687 | 19.6707 | 18.834 | 17.8319 | 16.786 | 15.5952 | 10.5125 | 8.5197 | 7.9452 | 7.8064 | 7.3401 | 15.9646 | 15.285 | 14.7523 | 13.4595 | 12.0472 | 10.6462 | 9.137 | 2.3238 | -1.1936 | -2.8507
|  | MILL LANE PRIMARY | HE |  |  |  |  | 7.5003 | 6.6972 | 15.3329 | 14.3105 | 13.1911 | 11.7207 | 9.9125 | 7.9625 | 5.9595 | -3.5191 | -7.4038 | -8.3507 | 11.3503 | 10.7799 | 20.3003 | 19.5503 | 18.738 | 17.6972 | 16.3962 | 14.9921 | 13.5411 | 6.5401 | 3.8176 | 1.8064 | 7.787 | 7.2105 | 15.7738 | 14.7921 | 13.7329 | 12.3411 | 10.6278 | 8.7748 | 6.8707 | -2.1232 | -5.7824 | -6.6466
|  | MILL LANE PRIMARY | CF |  |  |  |  | 8.2309 | 7.8401 | 16.8054 | 16.2799 | 15.6309 | 15.0809 | 14.1758 | 13.1534 | 12.0513 | 5.0391 | -1.0313 | -4.6691 | 11.7952 | 11.5432 | 21.2452 | 20.8778 | 20.4268 | 20.0534 | 19.3952 | 18.6289 | 17.8013 | 12.6758 | 6.4085 | -2.4885 | 8.2452 | 7.9258 | 16.7503 | 16.3656 | 15.8697 | 15.5197 | 14.6687 | 13.6921 | 12.6421 | 5.9983 | 0.23907 | -3.1752
COWLEY GSP | DRAYTON BSP | MILTON PRIMARY | MINIMUM HEADROOM | SU 49992 92060 | NO | YES | 22.092 | 15.4785 | 13.7132 | 11.3948 | 8.5989 | 5.6397 | 2.3897 | -1.0419 | -3.6766 | -6.0175 | -14.9083 | -21.4675 | -25.7726 | 20.6581 | 19.5754 | 18.2019 | 16.2264 | 14.2448 | 11.5458 | 8.605 | 6.3683 | 4.2785 | -3.2113 | -9.0032 | -18.4491 | 16.0091 | 14.5285 | 12.5448 | 10.0407 | 7.3968 | 4.2387 | 0.86009 | -1.7022 | -4.0042 | -12.4848 | -18.7766 | -22.8756
|  | MILTON PRIMARY | EE |  |  |  |  | 15.4785 | 13.7132 | 11.5213 | 8.5989 | 5.6397 | 2.3897 | -1.0419 | -3.6766 | -6.0175 | -14.1746 | -19.4052 | -24.0868 | 20.6581 | 19.5754 | 18.2019 | 16.2264 | 14.2448 | 11.5458 | 8.605 | 6.3683 | 4.2785 | -3.2113 | -9.0032 | -17.0634 | 16.0091 | 14.5285 | 12.6366 | 10.0407 | 7.3968 | 4.2387 | 0.86009 | -1.7022 | -4.0042 | -11.6981 | -16.497 | -20.9103
|  | MILTON PRIMARY | HT |  |  |  |  | 15.9295 | 14.0336 | 11.3948 | 8.9458 | 6.2121 | 3.1285 | -0.053171 | -2.5522 | -5.2399 | -14.9083 | -21.4675 | -25.7726 | 21.1723 | 20.0785 | 18.3805 | 16.8744 | 15.1478 | 12.6938 | 10.1172 | 8.1836 | 5.9999 | -1.5103 | -5.9195 | -8.7899 | 16.4662 | 14.8601 | 12.5448 | 10.4254 | 8.0121 | 5.0234 | 1.9213 | -0.49807 | -3.1317 | -12.4848 | -18.7766 | -22.8756
|  | MILTON PRIMARY | HE |  |  |  |  | 15.9611 | 14.1009 | 12.0203 | 9.956 | 7.104 | 4.3478 | 1.4591 | -0.61338 | -2.6675 | -11.796 | -17.5756 | -21.2981 | 21.0285 | 19.856 | 18.5591 | 17.3754 | 15.4754 | 13.2091 | 10.7305 | 9.0285 | 7.303 | -1.5073 | -7.4491 | -15.1532 | 16.4764 | 14.8907 | 13.0999 | 11.3672 | 8.8336 | 6.2111 | 3.4132 | 1.4703 | -0.45827 | -9.6195 | -14.5562 | -17.995
|  | MILTON PRIMARY | CF |  |  |  |  | 16.5805 | 15.0662 | 13.406 | 10.9876 | 8.9774 | 6.9703 | 4.7366 | 3.0407 | 1.4387 | -5.6399 | -10.6766 | -14.6124 | 21.3325 | 20.3101 | 19.203 | 17.4825 | 16.0417 | 14.1734 | 12.0295 | 10.3693 | 8.7907 | 1.7081 | -6.2297 | -18.4491 | 17.0397 | 15.7693 | 14.3581 | 12.2417 | 10.4958 | 8.605 | 6.4458 | 4.8121 | 3.2958 | -3.0838 | -7.5491 | -11.2613
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON PRIMARY | MINIMUM HEADROOM | ST 96164 14520 | YES | NO | 1.122 | 2.4615 | 2.3962 | 2.3238 | 2.236 | 2.1748 | 2.0615 | 1.9319 | 1.8431 | 1.7727 | 1.388 | 1.2605 | 1.1636 | 2.7661 | 2.7161 | 2.6477 | 2.5671 | 2.5192 | 2.4212 | 2.3039 | 2.2294 | 2.1763 | 1.9304 | 1.6008 | 0.82835 | 2.9732 | 2.9028 | 2.812 | 2.7018 | 2.6334 | 2.4998 | 2.3355 | 2.2324 | 2.1875 | 1.9355 | 1.8345 | 1.7457
|  | MINCHINGTON PRIMARY | EE |  |  |  |  | 2.4615 | 2.3962 | 2.3238 | 2.236 | 2.1748 | 2.0615 | 1.9319 | 1.8431 | 1.7727 | 1.388 | 1.2605 | 1.2197 | 2.7661 | 2.7161 | 2.6477 | 2.5671 | 2.5192 | 2.4212 | 2.3039 | 2.2294 | 2.1763 | 1.9304 | 1.709 | 1.3416 | 2.9732 | 2.9028 | 2.812 | 2.7018 | 2.6334 | 2.4998 | 2.3355 | 2.2324 | 2.1875 | 1.9355 | 1.8345 | 1.7916
|  | MINCHINGTON PRIMARY | HT |  |  |  |  | 2.5074 | 2.4533 | 2.3921 | 2.3421 | 2.2778 | 2.185 | 2.0829 | 2.0074 | 1.9044 | 1.4799 | 1.288 | 1.1636 | 2.8294 | 2.7926 | 2.7447 | 2.7161 | 2.6692 | 2.5988 | 2.5222 | 2.4783 | 2.3988 | 2.1161 | 2.0192 | 1.9641 | 3.0539 | 2.9977 | 2.9294 | 2.8834 | 2.8151 | 2.7181 | 2.6069 | 2.5375 | 2.4222 | 2.0049 | 1.8457 | 1.7457
|  | MINCHINGTON PRIMARY | HE |  |  |  |  | 2.5095 | 2.4544 | 2.3952 | 2.3472 | 2.284 | 2.1962 | 2.0952 | 2.0238 | 1.9227 | 1.4401 | 1.3187 | 1.2799 | 2.8243 | 2.7845 | 2.7304 | 2.6967 | 2.6467 | 2.5794 | 2.4937 | 2.4437 | 2.3528 | 1.9834 | 1.7569 | 1.3957 | 3.0539 | 2.9998 | 2.9314 | 2.8886 | 2.8232 | 2.7314 | 2.6222 | 2.5559 | 2.4457 | 1.9998 | 1.9018 | 1.8661
|  | MINCHINGTON PRIMARY | CF |  |  |  |  | 2.5289 | 2.4768 | 2.435 | 2.3809 | 2.3421 | 2.287 | 2.2248 | 2.1574 | 2.1125 | 1.7452 | 1.5319 | 1.3319 | 2.8386 | 2.7957 | 2.762 | 2.7171 | 2.6865 | 2.6334 | 2.5702 | 2.5059 | 2.4641 | 2.0304 | 1.6008 | 0.82835 | 3.0783 | 3.0222 | 2.9773 | 2.9222 | 2.8875 | 2.8273 | 2.762 | 2.6855 | 2.6488 | 2.2294 | 2.0549 | 1.9018
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE PRIMARY | MINIMUM HEADROOM | SU 01647 91932 | NO | NO | 0.248 | 9.499 | 9 | 8.398 | 7.598 | 6.6449 | 5.8969 | 5.1102 | 4.3704 | 3.6 | 1.452 | 1.1276 | 0.85306 | 12.0704 | 11.8041 | 11.5 | 11.0908 | 10.6276 | 10.2398 | 9.8061 | 9.3959 | 9.0051 | 7.7776 | 6.9551 | 4.9398 | 10.7163 | 10.3 | 9.8071 | 9.1469 | 8.3633 | 7.7469 | 7.0898 | 6.4694 | 5.8378 | 4.05 | 3.7673 | 3.5296
|  | MINETY VILLAGE PRIMARY | EE |  |  |  |  | 9.499 | 9 | 8.398 | 7.598 | 6.6449 | 5.8969 | 5.1102 | 4.3704 | 3.6 | 1.452 | 1.1276 | 0.97959 | 12.0704 | 11.8041 | 11.5 | 11.0908 | 10.6276 | 10.2398 | 9.8061 | 9.3959 | 9.0051 | 7.7776 | 7.1684 | 6.2265 | 10.7163 | 10.3 | 9.8071 | 9.1469 | 8.3633 | 7.7469 | 7.0898 | 6.4694 | 5.8378 | 4.05 | 3.7673 | 3.6418
|  | MINETY VILLAGE PRIMARY | HT |  |  |  |  | 9.5847 | 9.1265 | 8.5327 | 7.752 | 6.8612 | 6.1133 | 5.3704 | 4.6673 | 3.8857 | 1.6255 | 1.1418 | 0.85306 | 12.1663 | 11.9418 | 11.6531 | 11.2939 | 10.9 | 10.5378 | 10.1714 | 9.8173 | 9.4429 | 8.2745 | 8.0092 | 7.8745 | 10.8133 | 10.4408 | 9.949 | 9.3102 | 8.5765 | 7.9633 | 7.349 | 6.7633 | 6.1255 | 4.2082 | 3.7755 | 3.5296
|  | MINETY VILLAGE PRIMARY | HE |  |  |  |  | 9.5847 | 9.1316 | 8.5398 | 7.7663 | 6.8806 | 6.1439 | 5.4071 | 4.7143 | 3.9459 | 1.602 | 1.2684 | 1.1388 | 12.148 | 11.9153 | 11.6173 | 11.2429 | 10.8418 | 10.4673 | 10.0816 | 9.7133 | 9.3184 | 7.8847 | 7.2541 | 6.3235 | 10.8143 | 10.4449 | 9.9531 | 9.3214 | 8.5969 | 7.9908 | 7.3837 | 6.8071 | 6.1827 | 4.1969 | 3.902 | 3.7929
|  | MINETY VILLAGE PRIMARY | CF |  |  |  |  | 9.6531 | 9.2327 | 8.7296 | 8.0714 | 7.299 | 6.6663 | 6.0714 | 5.4796 | 4.7776 | 2.7765 | 2.0082 | 1.3408 | 12.1857 | 11.9571 | 11.7 | 11.3704 | 10.9908 | 10.65 | 10.3357 | 10.0041 | 9.6082 | 8.198 | 6.9551 | 4.9398 | 10.8755 | 10.5316 | 10.1296 | 9.598 | 8.9704 | 8.4643 | 7.9847 | 7.5041 | 6.9316 | 5.2469 | 4.55 | 3.9622
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | MORTIMER PRIMARY | MINIMUM HEADROOM | SU 62236 64103 | NO | NO | 2.647 | 4.953 | 4.5398 | 4.1183 | 3.7357 | 3.6847 | 3.2204 | 2.7071 | 2.1683 | 1.7898 | -0.37045 | -1.8796 | -2.749 | 5.0173 | 4.7418 | 4.4398 | 4.1408 | 4.1908 | 3.9051 | 3.5622 | 3.2163 | 3.0632 | 1.7724 | 0.21424 | -3.7511 | 4.7336 | 4.3581 | 3.9418 | 3.5316 | 3.6326 | 3.1898 | 2.6857 | 2.1775 | 1.8683 | 0.20404 | -1.0817 | -1.8082
|  | MORTIMER PRIMARY | EE |  |  |  |  | 4.953 | 4.5398 | 4.1183 | 3.7357 | 3.6847 | 3.2204 | 2.7071 | 2.1683 | 1.7898 | -0.27657 | -1.6266 | -2.5521 | 5.0173 | 4.7418 | 4.4398 | 4.1408 | 4.1908 | 3.9051 | 3.5622 | 3.2163 | 3.0632 | 1.7724 | 0.402 | -1.6643 | 4.7336 | 4.3581 | 3.9418 | 3.5316 | 3.6326 | 3.1898 | 2.6857 | 2.1775 | 1.8683 | 0.28159 | -0.84188 | -1.6296
|  | MORTIMER PRIMARY | HT |  |  |  |  | 5.0724 | 4.701 | 4.3367 | 4.054 | 3.7367 | 3.252 | 2.7296 | 2.5408 | 2.0591 | -0.37045 | -1.8796 | -2.749 | 5.1806 | 4.9632 | 4.7347 | 4.5765 | 4.3744 | 4.1183 | 3.8255 | 3.7847 | 3.5357 | 2.354 | 1.7489 | 1.3969 | 4.9244 | 4.6081 | 4.2704 | 4.0142 | 3.6969 | 3.2367 | 2.7255 | 2.7561 | 2.3112 | 0.20404 | -1.0817 | -1.8082
|  | MORTIMER PRIMARY | HE |  |  |  |  | 5.0959 | 4.7387 | 4.3918 | 4.1265 | 3.8398 | 3.4408 | 3.002 | 2.901 | 2.4979 | 0.30404 | -1.0398 | -1.6653 | 5.1683 | 4.9489 | 4.7163 | 4.5591 | 4.3612 | 4.1193 | 3.8357 | 3.8204 | 3.5581 | 2.0591 | 0.66424 | -1.2817 | 4.9377 | 4.6326 | 4.3081 | 4.0693 | 3.7775 | 3.3847 | 2.9377 | 3.0387 | 2.6591 | 0.78363 | -0.30922 | -0.83678
|  | MORTIMER PRIMARY | CF |  |  |  |  | 5.2459 | 4.9561 | 4.6908 | 4.4704 | 4.3142 | 4.1357 | 3.9153 | 3.6857 | 3.7632 | 2.35 | 0.87853 | -0.48576 | 5.2398 | 5.051 | 4.8642 | 4.703 | 4.5908 | 4.4398 | 4.2479 | 4.0367 | 4.1479 | 2.5336 | 0.21424 | -3.7511 | 5.0693 | 4.8275 | 4.5796 | 4.3581 | 4.2102 | 4.0081 | 3.7612 | 3.4949 | 3.7193 | 2.3459 | 1.1367 | 0.11731
MANNINGTON GSP | SALISBURY BSP | NETHERHAMPTON PRIMARY | MINIMUM HEADROOM | SU 12478 29102 | NO | NO | 5.298 | 2.1124 | 1.8237 | 1.5706 | 1.1114 | 0.4849 | -0.14469 | -0.86408 | -1.3498 | -1.7824 | -3.0508 | -3.8763 | -4.1988 | 5.8533 | 5.6767 | 5.4992 | 5.2339 | 4.8788 | 4.5073 | 4.0696 | 3.8941 | 3.6696 | 2.6869 | 1.3961 | -1.51 | 3.1247 | 2.8696 | 2.6186 | 2.2278 | 1.69 | 1.138 | 0.49918 | 0.21449 | -0.12224 | -1.1988 | -1.8957 | -2.16
|  | NETHERHAMPTON PRIMARY | EE |  |  |  |  | 2.1124 | 1.8237 | 1.5706 | 1.1114 | 0.4849 | -0.14469 | -0.86408 | -1.3314 | -1.7049 | -3.0478 | -3.7906 | -4.0682 | 5.8533 | 5.6767 | 5.4992 | 5.2339 | 4.8788 | 4.5073 | 4.0696 | 3.8941 | 3.6696 | 2.6869 | 1.7124 | 0.34408 | 3.1247 | 2.8696 | 2.6186 | 2.2278 | 1.69 | 1.138 | 0.49918 | 0.21449 | -0.095714 | -1.1988 | -1.8141 | -2.0498
|  | NETHERHAMPTON PRIMARY | HT |  |  |  |  | 2.1788 | 1.9165 | 1.7033 | 1.2461 | 0.60837 | -0.08449 | -0.73449 | -1.3498 | -1.7824 | -3.0508 | -3.8763 | -4.1988 | 5.9543 | 5.8206 | 5.7002 | 5.4747 | 5.1604 | 4.8145 | 4.4971 | 4.1767 | 3.9329 | 3.3206 | 2.9359 | 2.789 | 3.2308 | 2.9971 | 2.8012 | 2.4318 | 1.9104 | 1.3369 | 0.80224 | 0.27469 | -0.12224 | -1.1896 | -1.8957 | -2.16
|  | NETHERHAMPTON PRIMARY | HE |  |  |  |  | 2.2165 | 1.9431 | 1.7298 | 1.3012 | 0.71245 | 0.1451 | -0.44878 | -1.1335 | -1.5937 | -2.7478 | -3.4722 | -3.7304 | 5.939 | 5.7767 | 5.6359 | 5.4012 | 5.0839 | 4.7604 | 4.4308 | 4.038 | 3.7431 | 2.8033 | 1.8155 | 0.47061 | 3.2584 | 3.0196 | 2.8227 | 2.4798 | 1.9951 | 1.5196 | 1.0329 | 0.45531 | 0.042041 | -0.90796 | -1.5131 | -1.7212
|  | NETHERHAMPTON PRIMARY | CF |  |  |  |  | 2.4318 | 2.2696 | 2.1492 | 1.8614 | 1.5645 | 1.2767 | 0.91551 | 0.53082 | 0.25633 | -1.6416 | -2.361 | -3.3212 | 6.039 | 5.9247 | 5.8247 | 5.641 | 5.4492 | 5.241 | 4.9829 | 4.7206 | 4.49 | 2.8798 | 1.3961 | -1.51 | 3.4267 | 3.2849 | 3.1737 | 2.9267 | 2.692 | 2.442 | 2.1318 | 1.8155 | 1.5645 | -0.12531 | -0.60592 | -1.4069
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON PRIMARY | MINIMUM HEADROOM | SU 47615 12025 | NO | NO | 7.12 | 6.333 | 4.9993 | 3.4647 | 1.8983 | 0.51363 | -1.4731 | -3.6639 | -5.8629 | -7.4813 | -16.4833 | -23.5466 | -27.3119 | 12.8616 | 11.931 | 10.9483 | 9.9014 | 8.9157 | 7.5789 | 5.933 | 4.1973 | 2.9534 | -4.3017 | -15.5262 | -40.1721 | 3.481 | 2.2167 | 0.81465 | -0.64759 | -1.9935 | -3.867 | -5.969 | -8.0751 | -9.5272 | -17.0435 | -23.0731 | -26.2894
|  | NETLEY COMMON PRIMARY | EE |  |  |  |  | 6.333 | 4.9993 | 3.4647 | 1.8983 | 0.51363 | -1.4731 | -3.6639 | -5.8629 | -7.4813 | -15.8302 | -21.9027 | -26.5721 | 12.8616 | 11.931 | 10.9483 | 9.9014 | 8.9157 | 7.5789 | 5.933 | 4.1973 | 2.9534 | -4.3017 | -12.7496 | -25.7925 | 3.481 | 2.2167 | 0.81465 | -0.64759 | -1.9935 | -3.867 | -5.969 | -8.0751 | -9.5272 | -16.6394 | -21.6404 | -25.6986
|  | NETLEY COMMON PRIMARY | HT |  |  |  |  | 6.6167 | 5.3902 | 4.2891 | 3.0167 | 1.9463 | 0.23404 | -1.6231 | -3.5853 | -5.6251 | -16.4833 | -23.5466 | -27.3119 | 13.2157 | 12.5504 | 12.0085 | 11.334 | 10.7565 | 9.8942 | 8.931 | 7.9085 | 6.8422 | 0.9922 | -2.4486 | -4.1527 | 3.7575 | 2.6544 | 1.784 | 0.6422 | -0.36902 | -1.917 | -3.6292 | -5.4364 | -7.3221 | -17.0435 | -23.0731 | -26.2894
|  | NETLEY COMMON PRIMARY | HE |  |  |  |  | 6.7238 | 5.5361 | 4.5902 | 3.3657 | 2.334 | 0.93404 | -0.58841 | -2.1976 | -3.867 | -12.7721 | -19.0445 | -21.8915 | 13.0851 | 12.231 | 11.6136 | 10.7657 | 9.984 | 8.9983 | 7.9024 | 6.7126 | 5.4432 | -2.6925 | -11.4772 | -23.7343 | 3.8871 | 2.7718 | 2.03 | 0.93812 | -0.027184 | -1.3119 | -2.7364 | -4.2415 | -5.8129 | -13.8456 | -19.0904 | -21.5139
|  | NETLEY COMMON PRIMARY | CF |  |  |  |  | 7.3565 | 6.5667 | 5.6636 | 5.2636 | 4.7136 | 4.183 | 3.4973 | 2.7453 | 1.9432 | -4.1813 | -10.6343 | -16.4864 | 13.3504 | 12.7126 | 11.9381 | 11.4912 | 10.8208 | 10.0555 | 9.1453 | 8.1585 | 7.0871 | -1.3925 | -15.5262 | -40.1721 | 4.4626 | 3.7504 | 2.8942 | 2.6126 | 2.08 | 1.5575 | 0.88506 | 0.14118 | -0.64657 | -6.4364 | -12.1047 | -17.0302
MANNINGTON GSP | ARNEWOOD BSP | NEW MILTON PRIMARY | MINIMUM HEADROOM | SZ 23049 94942 | NO | NO | 1.574 | 11.0888 | 10.7194 | 10.0245 | 9.2531 | 8.3653 | 6.8755 | 5.2184 | 3.5786 | 2.3541 | -3.8633 | -8.6163 | -11.1888 | 14.2245 | 13.9296 | 13.3622 | 12.7133 | 11.9827 | 10.9602 | 9.7663 | 8.5633 | 7.7041 | 3.0541 | -2.7898 | -16.6633 | 10.6959 | 10.3776 | 9.6908 | 8.9255 | 8.0551 | 6.6694 | 5.1051 | 3.5571 | 2.4694 | -2.7796 | -6.8265 | -8.9724
|  | NEW MILTON PRIMARY | EE |  |  |  |  | 11.0888 | 10.7194 | 10.0245 | 9.2531 | 8.3653 | 6.8755 | 5.2184 | 3.5786 | 2.3541 | -3.5367 | -7.6255 | -10.8469 | 14.2245 | 13.9296 | 13.3622 | 12.7133 | 11.9827 | 10.9602 | 9.7663 | 8.5633 | 7.7041 | 3.0541 | -1.7582 | -8.9163 | 10.6959 | 10.3776 | 9.6908 | 8.9255 | 8.0551 | 6.6694 | 5.1051 | 3.5571 | 2.4694 | -2.5837 | -5.9633 | -8.6898
|  | NEW MILTON PRIMARY | HT |  |  |  |  | 11.549 | 11.0102 | 10.3969 | 10.0918 | 9.3898 | 8.0622 | 6.6265 | 5.1449 | 3.6133 | -3.8633 | -8.6163 | -11.1888 | 14.752 | 14.4122 | 14.0041 | 13.85 | 13.4031 | 12.6898 | 11.8867 | 11.0429 | 10.1531 | 6.0582 | 3.7663 | 2.6867 | 11.2092 | 10.6939 | 10.0949 | 9.8582 | 9.1969 | 8.0061 | 6.701 | 5.352 | 3.9469 | -2.7796 | -6.8265 | -8.9724
|  | NEW MILTON PRIMARY | HE |  |  |  |  | 11.5867 | 11.0847 | 10.5041 | 10.2306 | 9.5622 | 8.45 | 7.2163 | 5.9398 | 4.6388 | -1.9051 | -6.2857 | -8.2653 | 14.6224 | 14.2163 | 13.7398 | 13.4908 | 12.9347 | 12.1643 | 11.2796 | 10.3398 | 9.3449 | 3.8327 | -1.2908 | -7.9643 | 11.2357 | 10.752 | 10.1786 | 9.9755 | 9.3408 | 8.3337 | 7.198 | 6.0214 | 4.8082 | -1.1204 | -4.8122 | -6.4255
|  | NEW MILTON PRIMARY | CF |  |  |  |  | 12.0469 | 11.7704 | 11.4398 | 11.0704 | 10.9816 | 10.5102 | 9.949 | 9.349 | 8.7245 | 4.5388 | -0.16939 | -4.3959 | 14.848 | 14.5439 | 14.1847 | 13.7673 | 13.5408 | 12.9796 | 12.3184 | 11.6082 | 10.8439 | 5.5265 | -2.7898 | -16.6633 | 11.6531 | 11.3735 | 11.0367 | 10.6602 | 10.6286 | 10.1837 | 9.6439 | 9.0653 | 8.4592 | 4.452 | 0.29694 | -3.2776
FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT PRIMARY | MINIMUM HEADROOM | SZ 50076 89544 | NO | YES | 7.348 | 27.9817 | 27.2266 | 26.2705 | 25.1164 | 23.6786 | 22.0358 | 20.0858 | 18.0103 | 16.3705 | 8.7735 | 3.095 | 0.002102 | 29.8174 | 29.4235 | 28.8664 | 28.0092 | 26.8837 | 25.6011 | 24.2082 | 22.799 | 21.7092 | 16.348 | 11.3399 | -1.5959 | 26.5246 | 25.9817 | 25.2225 | 23.9939 | 22.4919 | 20.7256 | 18.8756 | 17.0246 | 15.5756 | 8.9031 | 4.1092 | 1.496
|  | NEWPORT PRIMARY | EE |  |  |  |  | 27.9817 | 27.2266 | 26.2705 | 25.1164 | 23.6786 | 22.0358 | 20.0858 | 18.0103 | 16.3705 | 8.7735 | 4.0154 | 0.55414 | 29.8174 | 29.4235 | 28.8664 | 28.0092 | 26.8837 | 25.6011 | 24.2082 | 22.799 | 21.7092 | 16.348 | 11.5725 | 4.8654 | 26.5246 | 25.9817 | 25.2225 | 23.9939 | 22.4919 | 20.7256 | 18.8756 | 17.0246 | 15.5756 | 8.9031 | 4.8194 | 1.8633
|  | NEWPORT PRIMARY | HT |  |  |  |  | 28.5592 | 27.8205 | 26.9858 | 25.8919 | 24.5409 | 22.7378 | 20.9654 | 19.199 | 17.4725 | 8.8123 | 3.095 | 0.002102 | 30.1919 | 29.7878 | 29.3358 | 28.6327 | 28.0031 | 27.0562 | 26.0705 | 25.0684 | 24.0643 | 19.299 | 16.4919 | 15.149 | 26.9113 | 26.3103 | 25.3623 | 24.1194 | 23.0052 | 21.4746 | 19.9205 | 18.3592 | 16.8246 | 9.1164 | 4.1092 | 1.496
|  | NEWPORT PRIMARY | HE |  |  |  |  | 28.4531 | 27.7286 | 26.8888 | 25.8807 | 24.7225 | 23.2501 | 21.5715 | 19.7939 | 18.0194 | 9.7562 | 5.0103 | 2.8439 | 30.1031 | 29.6888 | 29.2154 | 28.5276 | 27.8215 | 26.7705 | 25.6429 | 24.448 | 23.2205 | 17.0725 | 11.847 | 5.6939 | 26.8643 | 26.3052 | 25.645 | 24.5184 | 23.4694 | 22.0286 | 20.5266 | 18.945 | 17.4735 | 10.147 | 5.646 | 3.8388
|  | NEWPORT PRIMARY | CF |  |  |  |  | 29.0766 | 28.6878 | 28.2633 | 27.7388 | 27.1521 | 26.6501 | 25.8643 | 24.9654 | 23.9337 | 17.0154 | 11.2756 | 6.8664 | 30.4011 | 30.147 | 29.8705 | 29.5266 | 29.0541 | 28.6399 | 27.8633 | 27.0011 | 26.0848 | 19.5664 | 11.3399 | -1.5959 | 27.3072 | 27.0052 | 26.6786 | 26.2746 | 25.8225 | 25.496 | 24.8868 | 24.1011 | 23.2766 | 17.0776 | 11.7715 | 7.5725
FLEET-BRAMLEY GSP | ALDERSHOT BSP | NORMANDY PRIMARY | MINIMUM HEADROOM | SU 93221 52894 | YES | YES | 1.426 | 4.6299 | 4.5329 | 4.4074 | 4.2635 | 4.1503 | 3.9656 | 3.7584 | 3.5982 | 3.5064 | 3.0033 | 2.6033 | 2.3942 | 4.7967 | 4.7314 | 4.6497 | 4.5528 | 4.4824 | 4.363 | 4.2273 | 4.1252 | 4.064 | 3.7324 | 3.4028 | 2.561 | 4.5504 | 4.4617 | 4.3464 | 4.2107 | 4.1076 | 3.9321 | 3.7351 | 3.5902 | 3.5117 | 3.0739 | 2.7341 | 2.5596
|  | NORMANDY PRIMARY | EE |  |  |  |  | 4.6299 | 4.5329 | 4.4074 | 4.2635 | 4.1503 | 3.9656 | 3.7584 | 3.5982 | 3.5064 | 3.0411 | 2.6809 | 2.4299 | 4.7967 | 4.7314 | 4.6497 | 4.5528 | 4.4824 | 4.363 | 4.2273 | 4.1252 | 4.064 | 3.7324 | 3.4089 | 2.9691 | 4.5504 | 4.4617 | 4.3464 | 4.2107 | 4.1076 | 3.9321 | 3.7351 | 3.5902 | 3.5117 | 3.1076 | 2.8015 | 2.5913
|  | NORMANDY PRIMARY | HT |  |  |  |  | 4.686 | 4.5901 | 4.4778 | 4.3788 | 4.2554 | 4.0839 | 3.9391 | 3.7513 | 3.6054 | 3.0033 | 2.6033 | 2.3942 | 4.8528 | 4.7977 | 4.7324 | 4.6773 | 4.6079 | 4.511 | 4.4344 | 4.3293 | 4.2375 | 3.8977 | 3.7263 | 3.6375 | 4.6015 | 4.5188 | 4.4198 | 4.33 | 4.2219 | 4.0698 | 3.9392 | 3.7729 | 3.6392 | 3.0739 | 2.7341 | 2.5596
|  | NORMANDY PRIMARY | HE |  |  |  |  | 4.6931 | 4.6023 | 4.4942 | 4.4013 | 4.2809 | 4.135 | 4.0125 | 3.8462 | 3.7237 | 3.188 | 2.8584 | 2.6911 | 4.8457 | 4.7875 | 4.7171 | 4.662 | 4.5844 | 4.4926 | 4.4171 | 4.3089 | 4.2161 | 3.8069 | 3.4834 | 3.0752 | 4.6076 | 4.53 | 4.4351 | 4.3525 | 4.2453 | 4.1178 | 4.0096 | 3.8607 | 3.7392 | 3.2515 | 2.9576 | 2.8198
|  | NORMANDY PRIMARY | CF |  |  |  |  | 4.7339 | 4.6676 | 4.586 | 4.5186 | 4.4227 | 4.3431 | 4.2421 | 4.1309 | 4.1023 | 3.6972 | 3.2942 | 2.9584 | 4.8671 | 4.8201 | 4.761 | 4.7161 | 4.6508 | 4.5865 | 4.5059 | 4.4191 | 4.3793 | 3.9599 | 3.4028 | 2.561 | 4.6464 | 4.5902 | 4.5188 | 4.4617 | 4.378 | 4.3066 | 4.2096 | 4.1056 | 4.076 | 3.676 | 3.3239 | 3.0382
NURSLING GSP | ROWNHAMS BSP | NORTH BADDESLEY PRIMARY | MINIMUM HEADROOM | SU 38080 20568 | NO | YES | 15.286 | 1.3516 | 0.25768 | -0.65559 | -2.0954 | -5.1291 | -7.6699 | -10.8015 | -16.4311 | -21.0086 | -38.5801 | -48.6423 | -56.6423 | 3.276 | 2.5118 | 1.5465 | 0.42604 | -2.7556 | -4.9576 | -7.6546 | -13.4097 | -17.8821 | -33.6658 | -43.726 | -53.3474 | 1.2791 | 0.27707 | -0.74947 | -2.0689 | -5.624 | -8.2464 | -11.4607 | -17.7627 | -22.7668 | -40.7842 | -51.9444 | -61.6668
|  | NORTH BADDESLEY PRIMARY | EE |  |  |  |  | 1.3516 | 0.25768 | -0.55661 | -2.0954 | -4.274 | -6.7444 | -9.1627 | -12.1699 | -14.6954 | -27.4423 | -39.9372 | -44.4597 | 3.276 | 2.5118 | 1.8454 | 0.70972 | -1.1199 | -3.1444 | -4.9311 | -7.5189 | -9.5729 | -20.8607 | -33.9801 | -38.6862 | 1.2791 | 0.27707 | -0.53722 | -2.0086 | -4.2189 | -6.7086 | -9.0229 | -12.1168 | -14.6464 | -27.5729 | -41.7984 | -46.8842
|  | NORTH BADDESLEY PRIMARY | HT |  |  |  |  | 1.9883 | 0.92911 | -0.25253 | -1.3546 | -3.7413 | -5.4597 | -7.9005 | -10.0586 | -13.3954 | -27.4454 | -40.0056 | -47.6219 | 3.9016 | 3.1638 | 2.2475 | 1.5597 | -0.73824 | -2.6066 | -4.9342 | -6.5923 | -9.6495 | -22.1372 | -34.9484 | -43.174 | 1.9158 | 0.92707 | -0.23926 | -1.2342 | -3.825 | -5.6495 | -8.4086 | -10.5209 | -14.0005 | -28.4015 | -42.5199 | -51.3403
|  | NORTH BADDESLEY PRIMARY | HE |  |  |  |  | 1.8995 | 0.7536 | -0.65559 | -1.9556 | -5.1291 | -7.6699 | -10.8015 | -16.4311 | -21.0086 | -38.5801 | -48.6423 | -56.6423 | 3.7424 | 2.8362 | 1.5465 | 0.42604 | -2.7556 | -4.9576 | -7.6546 | -13.4097 | -17.8821 | -33.6658 | -43.726 | -53.3474 | 1.826 | 0.72094 | -0.74947 | -2.0689 | -5.624 | -8.2464 | -11.4607 | -17.7627 | -22.7668 | -40.7842 | -51.9444 | -61.6668
|  | NORTH BADDESLEY PRIMARY | CF |  |  |  |  | 2.5842 | 2.0179 | 1.5893 | 0.91686 | 0.12298 | -0.75049 | -1.4852 | -3.0076 | -4.7035 | -15.2362 | -27.428 | -35.1689 | 4.1689 | 3.7434 | 3.3781 | 2.7362 | 1.9679 | 1.0556 | 0.39849 | -0.62906 | -1.9893 | -10.9015 | -22.2474 | -33.6933 | 2.4709 | 1.9618 | 1.5679 | 0.88115 | 0.066861 | -0.84742 | -1.6668 | -3.1913 | -4.8984 | -15.5872 | -28.1393 | -36.3433
LOVEDEAN GSP | FAREHAM (MAIN) BSP | NORTH FAREHAM PRIMARY | MINIMUM HEADROOM | SU 56427 07430 | NO | YES | 14.81 | -9.5075 | -10.0534 | -10.1024 | -10.5983 | -11.1269 | -12.1238 | -13.2912 | -14.532 | -15.6891 | -21.3024 | -24.5391 | -26.3738 | -5.6159 | -6.0087 | -6.1291 | -6.5097 | -6.925 | -7.673 | -8.573 | -9.574 | -10.4271 | -14.6495 | -18.3863 | -27.3169 | -9.6204 | -10.1438 | -10.1734 | -10.6459 | -11.1479 | -12.1071 | -13.2377 | -14.4591 | -15.3867 | -20.405 | -23.2173 | -24.7408
|  | NORTH FAREHAM PRIMARY | EE |  |  |  |  | -9.5075 | -10.0534 | -10.1024 | -10.5983 | -11.1269 | -12.1238 | -13.2912 | -14.532 | -15.4789 | -20.9228 | -23.9136 | -26.1248 | -5.6159 | -6.0087 | -6.1291 | -6.5097 | -6.925 | -7.673 | -8.573 | -9.574 | -10.4271 | -14.6495 | -17.8618 | -22.6077 | -9.6204 | -10.1438 | -10.1734 | -10.6459 | -11.1479 | -12.1071 | -13.2377 | -14.4591 | -15.3867 | -20.1275 | -22.6959 | -24.553
|  | NORTH FAREHAM PRIMARY | HT |  |  |  |  | -9.2146 | -9.5493 | -9.9626 | -10.4238 | -10.7636 | -11.781 | -12.9789 | -14.3748 | -15.6891 | -21.3024 | -24.5391 | -26.3738 | -5.3179 | -5.5302 | -5.7842 | -6.0608 | -6.3587 | -6.9832 | -7.773 | -8.7424 | -9.6189 | -12.7904 | -14.2138 | -14.9567 | -9.303 | -9.6367 | -10.0377 | -10.4744 | -10.7224 | -11.6632 | -12.7887 | -14.1142 | -15.3357 | -20.405 | -23.2173 | -24.7408
|  | NORTH FAREHAM PRIMARY | HE |  |  |  |  | -9.1524 | -9.4759 | -9.8657 | -10.2953 | -10.2993 | -11.0779 | -11.9881 | -13.0197 | -14.1269 | -19.6922 | -22.6432 | -24.0585 | -5.3781 | -5.6404 | -5.9363 | -6.2628 | -6.3567 | -6.9434 | -7.6577 | -8.4924 | -9.4087 | -14.0189 | -17.271 | -21.7006 | -9.2642 | -9.5826 | -9.953 | -10.3642 | -10.3265 | -11.0316 | -11.8938 | -12.8867 | -13.952 | -18.9959 | -21.5346 | -22.702
|  | NORTH FAREHAM PRIMARY | CF |  |  |  |  | -8.8738 | -9.1218 | -9.335 | -9.6034 | -9.8922 | -10.2269 | -10.1606 | -10.635 | -11.1544 | -15.6014 | -18.5473 | -21.3524 | -5.2526 | -5.472 | -5.6893 | -5.9536 | -6.2587 | -6.623 | -6.8465 | -7.4179 | -8.0557 | -13.1955 | -18.3863 | -27.3169 | -9.0173 | -9.2602 | -9.455 | -9.7122 | -9.9918 | -10.3081 | -10.2377 | -10.7112 | -11.2397 | -15.501 | -18.0632 | -20.4377
LALEHAM GSP | EAST BEDFONT BSP | NORTH FELTHAM PRIMARY | MINIMUM HEADROOM | TQ 10987 74875 | NO | NO | 6.64 | -1.2677 | -1.7932 | -2.3299 | -2.9993 | -4.0799 | -4.884 | -6.2381 | -7.5922 | -8.7238 | -12.7238 | -14.9595 | -15.6014 | 0.59415 | 0.21047 | -0.16708 | -0.64463 | -1.4946 | -2.1661 | -3.0712 | -4.1181 | -4.9875 | -8.0712 | -14.4681 | -27.1926 | -0.95055 | -1.4199 | -1.8883 | -2.474 | -3.474 | -4.4179 | -5.7393 | -7.0169 | -8.0903 | -11.8924 | -14.0087 | -14.6046
|  | NORTH FELTHAM PRIMARY | EE |  |  |  |  | -1.2677 | -1.7932 | -2.3299 | -2.9993 | -4.0799 | -4.884 | -6.2381 | -7.5922 | -8.7238 | -12.3248 | -13.5514 | -14.7391 | 0.59415 | 0.21047 | -0.16708 | -0.64463 | -1.4946 | -2.1661 | -3.0712 | -4.1181 | -4.9875 | -8.0712 | -11.9599 | -18.2936 | -0.95055 | -1.4199 | -1.8883 | -2.474 | -3.474 | -4.4179 | -5.7393 | -7.0169 | -8.0903 | -11.4791 | -12.4342 | -12.8985
|  | NORTH FELTHAM PRIMARY | HT |  |  |  |  | -1.0503 | -1.4861 | -1.9361 | -2.7473 | -3.7238 | -4.6932 | -5.6901 | -6.6595 | -7.2075 | -11.0126 | -13.4942 | -14.6514 | 0.85945 | 0.62884 | 0.38904 | -0.2181 | -0.89463 | -1.4967 | -2.112 | -2.7048 | -3.2497 | -6.1405 | -7.4487 | -7.8722 | -0.73932 | -1.1056 | -1.4944 | -2.2608 | -3.1567 | -4.0199 | -4.9056 | -5.7659 | -6.2536 | -9.924 | -11.7914 | -12.7516
|  | NORTH FELTHAM PRIMARY | HE |  |  |  |  | -1.0299 | -1.4667 | -1.8993 | -2.435 | -3.3401 | -4.2544 | -5.2963 | -6.3901 | -7.532 | -12.7238 | -14.9595 | -15.6014 | 0.76149 | 0.44109 | 0.12476 | -0.26606 | -0.99157 | -1.714 | -2.5344 | -3.3926 | -4.0671 | -7.9854 | -11.8303 | -17.9497 | -0.73014 | -1.1148 | -1.4975 | -1.9659 | -2.8026 | -3.6373 | -4.5985 | -5.8414 | -6.9424 | -11.8924 | -14.0087 | -14.6046
|  | NORTH FELTHAM PRIMARY | CF |  |  |  |  | -0.67993 | -0.88402 | -1.1197 | -1.3687 | -1.6381 | -2.0218 | -2.5248 | -3.1554 | -3.782 | -8.3636 | -11.8626 | -14.332 | 0.92476 | 0.7217 | 0.46762 | 0.19721 | -0.12932 | -0.63851 | -1.2548 | -1.9671 | -2.6814 | -7.2681 | -14.4681 | -27.1926 | -0.42402 | -0.60361 | -0.81789 | -1.0393 | -1.2781 | -1.6414 | -2.1148 | -2.6975 | -3.3832 | -7.7444 | -11.0781 | -13.4199
COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY PRIMARY | MINIMUM HEADROOM | SP 48645 04403 | NO | YES | 2.844 | 1.6624 | 1.4471 | 1.1767 | 0.88179 | 0.56444 | 0.5073 | 0.03689 | -0.43352 | -0.74372 | -2.5805 | -3.9458 | -4.7274 | 0.9573 | 0.78179 | 0.56546 | 0.31954 | 0.060359 | 0.0624 | -0.26821 | -0.60495 | -0.82127 | -2.0345 | -3.6682 | -7.5866 | 0.61546 | 0.40118 | 0.12158 | -0.18556 | -0.51413 | -0.46821 | -0.91821 | -1.3692 | -1.6437 | -3.2039 | -4.409 | -5.0611
|  | NORTH HINKSEY PRIMARY | EE |  |  |  |  | 1.6624 | 1.4471 | 1.1767 | 0.88179 | 0.56444 | 0.5073 | 0.03689 | -0.43352 | -0.74372 | -2.3703 | -3.6141 | -4.5213 | 0.9573 | 0.78179 | 0.56546 | 0.31954 | 0.060359 | 0.0624 | -0.26821 | -0.60495 | -0.82127 | -2.0345 | -3.4111 | -5.4927 | 0.61546 | 0.40118 | 0.12158 | -0.18556 | -0.51413 | -0.46821 | -0.91821 | -1.3692 | -1.6437 | -3.0243 | -4.1141 | -4.8866
|  | NORTH HINKSEY PRIMARY | HT |  |  |  |  | 1.8032 | 1.6297 | 1.4195 | 1.1889 | 0.99403 | 0.56138 | 0.08689 | -0.01209 | -0.44372 | -2.5805 | -3.9458 | -4.7274 | 1.1216 | 1.0134 | 0.87669 | 0.71342 | 0.58995 | 0.33791 | 0.046073 | 0.096073 | -0.15189 | -1.2631 | -1.8652 | -2.21 | 0.78281 | 0.61036 | 0.40016 | 0.16648 | -0.01311 | -0.42331 | -0.88046 | -0.87433 | -1.2774 | -3.2039 | -4.409 | -5.0611
|  | NORTH HINKSEY PRIMARY | HE |  |  |  |  | 1.8308 | 1.6767 | 1.4879 | 1.2787 | 1.1053 | 0.75832 | 0.36648 | 0.3573 | 0.01342 | -1.7345 | -2.9447 | -3.5917 | 1.0889 | 0.96342 | 0.80832 | 0.63281 | 0.48689 | 0.23893 | -0.048824 | -0.031478 | -0.2927 | -1.7345 | -3.109 | -5.0886 | 0.80424 | 0.65118 | 0.45628 | 0.24403 | 0.081788 | -0.25699 | -0.64168 | -0.55699 | -0.88454 | -2.4621 | -3.5162 | -4.0672
|  | NORTH HINKSEY PRIMARY | CF |  |  |  |  | 1.9634 | 1.8389 | 1.7542 | 1.6236 | 1.4818 | 1.3695 | 1.1787 | 0.9726 | 0.7573 | -0.080457 | -1.3243 | -2.5468 | 1.1502 | 1.0206 | 0.92056 | 0.78485 | 0.62669 | 0.47669 | 0.2573 | 0.024645 | -0.22536 | -1.4274 | -3.6682 | -7.5866 | 0.92464 | 0.79301 | 0.7022 | 0.56342 | 0.4124 | 0.30832 | 0.10424 | -0.11413 | -0.34474 | -1.058 | -2.1529 | -3.1631
NORTH HYDE GSP |  | NORTH HYDE PRIMARY | MINIMUM HEADROOM | TQ 10367 79001 | NO | YES | 20.393 | 12.3203 | 10.3152 | 85.408 | 82.5601 | 79.7325 | 76.2917 | 72.3131 | 68.7703 | 65.405 | 51.9294 | 44.7141 | 41.5101 | 16.1203 | 14.8458 | 88.4203 | 86.5458 | 84.508 | 81.1437 | 77.2274 | 73.9029 | 70.4141 | 57.9121 | 47.1723 | 29.0631 | 11.7845 | 10.0958 | 83.1754 | 80.7162 | 78.0988 | 74.4315 | 70.1794 | 66.4856 | 62.9478 | 48.305 | 40.8968 | 37.1203
|  | NORTH HYDE PRIMARY | EE |  |  |  |  | 12.3203 | 10.3152 | 85.408 | 82.5601 | 79.7325 | 76.2917 | 72.3131 | 68.7703 | 65.405 | 51.9294 | 44.7141 | 41.5101 | 16.1203 | 14.8458 | 88.4203 | 86.5458 | 84.508 | 81.1437 | 77.2274 | 73.9029 | 70.4141 | 57.9121 | 47.1723 | 33.1784 | 11.7845 | 10.0958 | 83.1754 | 80.7162 | 78.0988 | 74.4315 | 70.1794 | 66.4856 | 62.9478 | 48.305 | 40.8968 | 37.1203
|  | NORTH HYDE PRIMARY | HT |  |  |  |  | 13.1672 | 11.2927 | 86.7029 | 84.2805 | 82.1703 | 79.2039 | 75.8396 | 72.8233 | 69.5743 | 55.7958 | 47.1886 | 43.2009 | 17.0672 | 16.0396 | 90.0335 | 88.7162 | 87.5203 | 84.7815 | 81.6141 | 78.8937 | 75.4835 | 61.4192 | 53.1345 | 48.5733 | 12.5713 | 11.0437 | 84.4356 | 82.3723 | 80.5478 | 77.4754 | 73.8764 | 70.6835 | 67.2019 | 52.5325 | 42.8396 | 37.9396
|  | NORTH HYDE PRIMARY | HE |  |  |  |  | 13.1723 | 11.1999 | 86.5723 | 84.3448 | 81.9192 | 79.3733 | 76.3335 | 73.9468 | 71.459 | 55.7927 | 49.1345 | 46.2386 | 16.8284 | 15.5662 | 89.3713 | 88.0345 | 86.3376 | 83.8631 | 80.8478 | 78.6294 | 75.9519 | 62.0856 | 52.8488 | 38.8458 | 12.5611 | 10.9233 | 84.2611 | 82.3805 | 80.2264 | 77.6682 | 74.5611 | 72.1825 | 69.2243 | 52.7131 | 45.7774 | 42.3223
|  | NORTH HYDE PRIMARY | CF |  |  |  |  | 14.2458 | 12.8805 | 88.8121 | 87.0172 | 85.5539 | 84.1488 | 82.2488 | 80.459 | 78.7968 | 71.1723 | 62.0152 | 55.8672 | 17.4111 | 16.4682 | 90.5141 | 89.258 | 88.0601 | 86.2886 | 83.9039 | 81.6458 | 79.5172 | 68.7876 | 53.6499 | 29.0631 | 13.5325 | 12.4478 | 86.2917 | 84.8315 | 83.5866 | 82.1294 | 80.1396 | 78.2948 | 76.5488 | 68.0886 | 59.2305 | 53.3519
MINETY GSP | CIRENCESTER BSP | NORTHLEACH PRIMARY | MINIMUM HEADROOM | SP 10557 14251 | NO | NO | 0.768 | 6.8255 | 6.6673 | 6.4592 | 6.2296 | 6.049 | 5.7571 | 5.4133 | 5.0704 | 4.8929 | 4.3704 | 3.9714 | 3.6133 | 8.2673 | 8.151 | 7.9959 | 7.8173 | 7.6776 | 7.4571 | 7.1959 | 6.9316 | 6.7929 | 6.4153 | 5.4235 | 3.252 | 7.0173 | 6.8663 | 6.6663 | 6.4449 | 6.2735 | 5.9929 | 5.6622 | 5.3327 | 5.1673 | 4.7684 | 4.4357 | 4.152
|  | NORTHLEACH PRIMARY | EE |  |  |  |  | 6.8255 | 6.6673 | 6.4592 | 6.2296 | 6.049 | 5.7571 | 5.4133 | 5.0704 | 4.8929 | 4.3704 | 3.9898 | 3.801 | 8.2673 | 8.151 | 7.9959 | 7.8173 | 7.6776 | 7.4571 | 7.1959 | 6.9316 | 6.7929 | 6.4153 | 5.7316 | 4.6827 | 7.0173 | 6.8663 | 6.6663 | 6.4449 | 6.2735 | 5.9929 | 5.6622 | 5.3327 | 5.1673 | 4.7684 | 4.4582 | 4.302
|  | NORTHLEACH PRIMARY | HT |  |  |  |  | 6.9408 | 6.8102 | 6.6531 | 6.5214 | 6.3398 | 6.1102 | 5.8969 | 5.6306 | 5.3612 | 4.5265 | 3.9714 | 3.6133 | 8.3796 | 8.3031 | 8.202 | 8.1204 | 8.001 | 7.8531 | 7.7235 | 7.5449 | 7.3612 | 6.9418 | 6.6367 | 6.4633 | 7.1316 | 7.0102 | 6.8663 | 6.7449 | 6.5735 | 6.3582 | 6.1612 | 5.9112 | 5.6571 | 4.9102 | 4.4357 | 4.152
|  | NORTHLEACH PRIMARY | HE |  |  |  |  | 6.9439 | 6.8184 | 6.6714 | 6.5459 | 6.3786 | 6.1622 | 5.9602 | 5.7082 | 5.449 | 4.5306 | 4.1571 | 3.9908 | 8.3633 | 8.2786 | 8.1724 | 8.0827 | 7.952 | 7.7959 | 7.6531 | 7.4622 | 7.2551 | 6.5469 | 5.8531 | 4.8276 | 7.1316 | 7.0184 | 6.8786 | 6.7673 | 6.6071 | 6.4041 | 6.2163 | 5.9806 | 5.7378 | 4.9357 | 4.6276 | 4.4969
|  | NORTHLEACH PRIMARY | CF |  |  |  |  | 6.9969 | 6.898 | 6.7878 | 6.6653 | 6.5704 | 6.4316 | 6.2694 | 6.0949 | 5.9714 | 4.9704 | 4.6878 | 4.1316 | 8.3959 | 8.3255 | 8.2418 | 8.1398 | 8.0571 | 7.9337 | 7.7867 | 7.6255 | 7.5 | 6.4337 | 5.4235 | 3.252 | 7.1847 | 7.0949 | 6.9898 | 6.8745 | 6.7867 | 6.6571 | 6.501 | 6.3347 | 6.2194 | 5.2622 | 5.0724 | 4.6031
IVER 66KV GSP |  | NORTHOLT PRIMARY | MINIMUM HEADROOM | TQ 11550 83230 | NO | NO | 14.554 | 36.5703 | 35.4836 | 34.254 | 32.8703 | 31.3693 | 29.0111 | 26.3254 | 23.6509 | 21.7356 | 14.4856 | 10.0274 | 10.1142 | 46.9397 | 46.0019 | 44.9407 | 43.706 | 42.355 | 40.6081 | 38.5458 | 36.4489 | 34.9183 | 27.3244 | 15.604 | -12.7073 | 40.8152 | 39.7683 | 38.5825 | 37.2489 | 35.7999 | 33.5795 | 31.0356 | 28.505 | 26.7305 | 20.1183 | 16.2846 | 16.3397
|  | NORTHOLT PRIMARY | EE |  |  |  |  | 36.5703 | 35.4836 | 34.254 | 32.8703 | 31.3693 | 29.0111 | 26.3254 | 23.6509 | 21.7356 | 14.4856 | 10.7417 | 12.0795 | 46.9397 | 46.0019 | 44.9407 | 43.706 | 42.355 | 40.6081 | 38.5458 | 36.4489 | 34.9183 | 27.3244 | 19.2846 | 7.1458 | 40.8152 | 39.7683 | 38.5825 | 37.2489 | 35.7999 | 33.5795 | 31.0356 | 28.505 | 26.7305 | 20.1183 | 16.9489 | 17.9519
|  | NORTHOLT PRIMARY | HT |  |  |  |  | 37.156 | 36.2683 | 35.7672 | 34.8223 | 33.7652 | 31.9917 | 30.0121 | 27.9356 | 25.7785 | 15.5203 | 10.0274 | 10.1142 | 47.6458 | 47.0162 | 46.7285 | 46.0642 | 45.3081 | 44.2754 | 43.0713 | 41.7774 | 40.4111 | 34.1642 | 31.0999 | 30.8244 | 41.3938 | 40.5458 | 40.0927 | 39.1978 | 38.1938 | 36.555 | 34.707 | 32.7621 | 30.7376 | 21.1805 | 16.2846 | 16.3397
|  | NORTHOLT PRIMARY | HE |  |  |  |  | 37.1978 | 36.3815 | 35.955 | 35.1009 | 34.1478 | 32.5468 | 30.7366 | 28.8407 | 26.8774 | 19.007 | 15.456 | 15.1907 | 47.4264 | 46.6968 | 46.3009 | 45.4764 | 44.5591 | 43.3315 | 41.904 | 40.3652 | 38.7285 | 30.0815 | 21.7989 | 9.2489 | 41.4285 | 40.6448 | 40.257 | 39.4468 | 38.5438 | 37.0611 | 35.3683 | 33.5948 | 31.7519 | 24.3774 | 21.2376 | 21.0009
|  | NORTHOLT PRIMARY | CF |  |  |  |  | 37.8774 | 37.403 | 36.8815 | 36.7856 | 36.2632 | 35.6438 | 34.8693 | 34.0254 | 33.1325 | 27.2417 | 20.7203 | 14.6223 | 47.7703 | 47.2019 | 46.5683 | 46.2203 | 45.4203 | 44.457 | 43.3152 | 42.0815 | 40.7499 | 31.2132 | 15.604 | -12.7073 | 42.0948 | 41.6478 | 41.154 | 41.0591 | 40.5591 | 39.9672 | 39.2213 | 38.4091 | 37.5509 | 31.8672 | 25.8683 | 20.4907
BRAMLEY (BASI) GSP | READING BSP | NORTHUMBERLAND AVENUE PRIMARY | MINIMUM HEADROOM | SU 72207 71092 | NO | YES | 4.447 | 4.0117 | 3.5117 | 2.929 | 2.5342 | 2.3627 | 1.676 | 0.64129 | -0.29646 | -0.95769 | -3.6444 | -4.9383 | -5.1056 | 5.6588 | 5.1456 | 4.5609 | 4.2252 | 4.0966 | 3.6537 | 3.015 | 2.4088 | 1.9517 | -0.49422 | -4.2299 | -11.6422 | 3.7542 | 3.2123 | 2.6358 | 2.2827 | 2.1521 | 1.5613 | 0.70007 | -0.079522 | -0.63156 | -2.8081 | -3.8601 | -3.9805
|  | NORTHUMBERLAND AVENUE PRIMARY | EE |  |  |  |  | 4.0117 | 3.5117 | 2.929 | 2.5342 | 2.3627 | 1.676 | 0.64129 | -0.29646 | -0.95769 | -3.6444 | -4.8934 | -4.6495 | 5.6588 | 5.1456 | 4.5609 | 4.2252 | 4.0966 | 3.6537 | 3.015 | 2.4088 | 1.9517 | -0.49422 | -2.9238 | -6.3422 | 3.7542 | 3.2123 | 2.6358 | 2.2827 | 2.1521 | 1.5613 | 0.70007 | -0.079522 | -0.63156 | -2.8081 | -3.851 | -3.5846
|  | NORTHUMBERLAND AVENUE PRIMARY | HT |  |  |  |  | 4.1495 | 3.6893 | 3.2158 | 3.0025 | 2.4627 | 1.7505 | 0.71782 | 0.31987 | -0.3883 | -3.5158 | -4.9383 | -5.1056 | 5.8548 | 5.4303 | 4.9446 | 4.816 | 4.517 | 4.1446 | 3.6048 | 3.4517 | 3.0639 | 1.3231 | 0.55987 | 0.39354 | 3.9052 | 3.4072 | 2.895 | 2.7052 | 2.2562 | 1.6521 | 0.79803 | 0.48476 | -0.10401 | -2.654 | -3.8601 | -3.9805
|  | NORTHUMBERLAND AVENUE PRIMARY | HE |  |  |  |  | 4.1505 | 3.6954 | 3.2372 | 3.0219 | 2.6331 | 2.0433 | 1.077 | 0.5964 | -0.060747 | -2.6169 | -3.6597 | -3.8597 | 5.8007 | 5.3384 | 4.8211 | 4.5844 | 4.2731 | 3.8844 | 3.2905 | 2.9925 | 2.5252 | 0.062927 | -2.2789 | -5.834 | 3.9337 | 3.4562 | 2.9674 | 2.7358 | 2.3817 | 1.8756 | 1.0776 | 0.69701 | 0.15007 | -1.8948 | -2.7601 | -2.9152
|  | NORTHUMBERLAND AVENUE PRIMARY | CF |  |  |  |  | 4.2933 | 3.8862 | 3.5076 | 3.3546 | 3.2607 | 3.1403 | 2.9403 | 2.6188 | 2.227 | -0.25258 | -2.6005 | -3.8036 | 5.8874 | 5.4415 | 4.9793 | 4.7568 | 4.5752 | 4.3282 | 3.9976 | 3.6099 | 3.1905 | 0.3568 | -4.2299 | -11.6422 | 4.1174 | 3.699 | 3.3266 | 3.1674 | 3.0776 | 2.9348 | 2.7052 | 2.4001 | 2.0756 | 0.13068 | -1.7938 | -2.8632
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD PRIMARY | MINIMUM HEADROOM | SU 68329 86784 | YES | NO | 1.228 | 3.2636 | 3.1269 | 2.781 | 2.5748 | 1.6748 | 1.2157 | 0.68199 | -1.0782 | -2.2854 | -5.0803 | -8.0588 | -11.8517 | 4.1144 | 3.9674 | 3.5726 | 3.3664 | 2.295 | 1.7797 | 1.194 | -0.92541 | -2.3601 | -5.4836 | -9.3438 | -14.5683 | 3.2649 | 3.1098 | 2.7016 | 2.4782 | 1.3833 | 0.84551 | 0.22714 | -1.9259 | -3.3912 | -6.6382 | -10.2963 | -15.0147
|  | NUFFIELD PRIMARY | EE |  |  |  |  | 3.2636 | 3.1463 | 3.0167 | 2.9167 | 2.5473 | 2.1371 | 1.9748 | 1.3993 | 1.0912 | -0.74352 | -5.0445 | -6.5721 | 4.1144 | 4.0287 | 3.9287 | 3.8501 | 3.4583 | 3.0419 | 2.9266 | 2.3062 | 1.9868 | -0.027449 | -5.5305 | -7.9142 | 3.2649 | 3.1537 | 3.0292 | 2.9353 | 2.5149 | 2.0578 | 1.9098 | 1.2506 | 0.90367 | -1.1984 | -6.5065 | -8.3882
|  | NUFFIELD PRIMARY | HT |  |  |  |  | 3.332 | 3.1626 | 2.934 | 2.8371 | 2.1044 | 1.6453 | 1.084 | 0.83301 | 0.16872 | -2.1915 | -6.269 | -9.2272 | 4.1828 | 4.0297 | 3.7991 | 3.7328 | 2.8838 | 2.3848 | 1.7807 | 1.5654 | 0.83786 | -1.6693 | -6.5723 | -10.1438 | 3.3353 | 3.1537 | 2.8976 | 2.8047 | 1.9251 | 1.3873 | 0.73531 | 0.47102 | -0.30653 | -3.0402 | -8.0453 | -11.6851
|  | NUFFIELD PRIMARY | HE |  |  |  |  | 3.333 | 3.1269 | 2.781 | 2.5748 | 1.6748 | 1.2157 | 0.68199 | -1.0782 | -2.2854 | -5.0803 | -8.0588 | -11.8517 | 4.1726 | 3.9674 | 3.5726 | 3.3664 | 2.295 | 1.7797 | 1.194 | -0.92541 | -2.3601 | -5.4836 | -9.3438 | -14.5683 | 3.3353 | 3.1098 | 2.7016 | 2.4782 | 1.3833 | 0.84551 | 0.22714 | -1.9259 | -3.3912 | -6.6382 | -10.2963 | -15.0147
|  | NUFFIELD PRIMARY | CF |  |  |  |  | 3.3585 | 3.2922 | 3.2371 | 3.0738 | 2.8953 | 2.6636 | 2.4983 | 2.2871 | 2.0208 | 0.40852 | -1.5282 | -3.3415 | 4.1868 | 4.1368 | 4.0919 | 3.9266 | 3.7328 | 3.4766 | 3.2909 | 3.0623 | 2.7685 | 0.86439 | -1.7897 | -4.8713 | 3.3578 | 3.2996 | 3.2486 | 3.072 | 2.8741 | 2.6098 | 2.4271 | 2.1945 | 1.8965 | 0.049592 | -2.2382 | -4.3953
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | OAKRIDGE PRIMARY | MINIMUM HEADROOM | SU 63496 53664 | NO | NO | 5.062 | 15.3332 | 14.6434 | 13.9383 | 13.5445 | 12.9383 | 12.0322 | 10.7934 | 9.4332 | 8.2649 | 4.0261 | 0.52711 | -1.628 | 16.1271 | 15.6087 | 15.0322 | 14.7557 | 14.2567 | 13.6322 | 12.8179 | 11.9434 | 11.2608 | 8.3036 | 5.2924 | -2.7974 | 14.9057 | 14.2679 | 13.5853 | 13.2598 | 12.6679 | 11.8128 | 10.6669 | 9.4332 | 8.4281 | 4.6485 | 1.5863 | -0.25147
|  | OAKRIDGE PRIMARY | EE |  |  |  |  | 15.3332 | 14.6434 | 13.9383 | 13.5445 | 12.9383 | 12.0322 | 10.7934 | 9.4332 | 8.2649 | 4.0261 | 1.0536 | -1.38 | 16.1271 | 15.6087 | 15.0322 | 14.7557 | 14.2567 | 13.6322 | 12.8179 | 11.9434 | 11.2608 | 8.3036 | 5.2924 | 0.82915 | 14.9057 | 14.2679 | 13.5853 | 13.2598 | 12.6679 | 11.8128 | 10.6669 | 9.4332 | 8.4281 | 4.6485 | 2.0832 | -0.041261
|  | OAKRIDGE PRIMARY | HT |  |  |  |  | 15.4771 | 14.8975 | 14.3587 | 13.8975 | 13.37 | 12.2179 | 11.3659 | 10.1853 | 9.271 | 4.0557 | 0.52711 | -1.628 | 16.3577 | 15.9802 | 15.6118 | 15.2934 | 14.9159 | 14.3047 | 14.0006 | 13.373 | 12.8434 | 10.1628 | 8.5138 | 7.6506 | 15.0679 | 14.5506 | 14.0536 | 13.6159 | 13.1077 | 12.0863 | 11.3628 | 10.3138 | 9.47 | 4.7067 | 1.5863 | -0.25147
|  | OAKRIDGE PRIMARY | HE |  |  |  |  | 15.621 | 15.0557 | 14.5006 | 13.9781 | 13.4832 | 12.7669 | 12.1853 | 11.2251 | 10.2465 | 5.6353 | 2.7016 | 1.4496 | 16.4077 | 15.9965 | 15.5638 | 15.1547 | 14.7547 | 14.2598 | 13.9975 | 13.3802 | 12.7312 | 9.3006 | 6.2587 | 2.2383 | 15.2016 | 14.6965 | 14.1842 | 13.6965 | 13.2322 | 12.5608 | 12.0618 | 11.1996 | 10.3189 | 6.1659 | 3.5812 | 2.4598
|  | OAKRIDGE PRIMARY | CF |  |  |  |  | 16.0342 | 15.8312 | 15.4496 | 15.0342 | 14.5485 | 14.1659 | 13.8098 | 13.4057 | 13.3598 | 9.7812 | 6.9608 | 4.3496 | 16.5996 | 16.3965 | 16.0383 | 15.6434 | 15.2149 | 14.8169 | 14.3914 | 13.9251 | 13.8026 | 10.2608 | 5.422 | -2.7974 | 15.5608 | 15.3761 | 15.02 | 14.6373 | 14.2026 | 13.8485 | 13.4812 | 13.0751 | 13.0873 | 9.8608 | 7.3138 | 4.9965
COWLEY GSP | HEADINGTON BSP | OLD ROAD PRIMARY | MINIMUM HEADROOM | SP 55274 06426 | NO | NO | 0.666 | 10.9939 | 10.4653 | 9.9459 | 9.4143 | 9.2337 | 8.2684 | 7.4469 | 6.7184 | 6.2602 | 4.4837 | 3.2714 | 3.1714 | 10.498 | 9.9643 | 9.6745 | 9.35 | 9.1469 | 8.4755 | 7.8551 | 7.2643 | 6.8459 | 4.6418 | 0.71633 | -7.9643 | 9.4378 | 8.8704 | 8.4122 | 7.9367 | 7.7408 | 6.8837 | 6.1408 | 5.4735 | 5.0449 | 3.4041 | 2.3541 | 2.2633
|  | OLD ROAD PRIMARY | EE |  |  |  |  | 11.1806 | 10.4653 | 9.9459 | 9.4143 | 9.2337 | 8.2684 | 7.4469 | 6.7184 | 6.2602 | 4.4837 | 3.4214 | 3.6337 | 10.498 | 9.9643 | 9.6745 | 9.35 | 9.1469 | 8.4755 | 7.8551 | 7.2643 | 6.8459 | 4.6418 | 2.0663 | -1.8959 | 9.5061 | 8.8704 | 8.4122 | 7.9367 | 7.7408 | 6.8837 | 6.1408 | 5.4735 | 5.0449 | 3.4041 | 2.4735 | 2.65
|  | OLD ROAD PRIMARY | HT |  |  |  |  | 10.9939 | 10.5122 | 10.202 | 9.8684 | 9.4469 | 8.3582 | 7.751 | 7.5449 | 7.0398 | 4.651 | 3.2714 | 3.1714 | 10.5122 | 10.1265 | 9.9622 | 9.7765 | 9.5327 | 8.9643 | 8.6265 | 8.4663 | 8.2173 | 6.7592 | 5.9796 | 5.8418 | 9.4378 | 9 | 8.6888 | 8.3561 | 7.9551 | 7.0092 | 6.4551 | 6.2643 | 5.7949 | 3.6031 | 2.3541 | 2.2633
|  | OLD ROAD PRIMARY | HE |  |  |  |  | 11.3898 | 10.7602 | 10.399 | 10.0837 | 9.6806 | 8.8561 | 8.1939 | 8.0194 | 7.5765 | 5.9 | 5.101 | 4.998 | 10.6092 | 10.1071 | 9.8714 | 9.6602 | 9.352 | 8.8296 | 8.3827 | 8.15 | 7.7643 | 5.5092 | 3.0316 | -1.0531 | 9.7306 | 9.1878 | 8.851 | 8.5531 | 8.1663 | 7.4398 | 6.8469 | 6.6847 | 6.2653 | 4.7276 | 4.0092 | 3.9204
|  | OLD ROAD PRIMARY | CF |  |  |  |  | 11.749 | 11.4459 | 11.3602 | 11.2082 | 10.9786 | 10.7724 | 10.4031 | 9.9378 | 9.4694 | 7.698 | 6.2408 | 4.9102 | 10.7582 | 10.3837 | 10.2541 | 10.0969 | 9.8184 | 9.5378 | 9.1714 | 8.748 | 8.2306 | 5.4061 | 0.71633 | -7.9643 | 10.0337 | 9.7429 | 9.6459 | 9.5051 | 9.2929 | 9.0959 | 8.7684 | 8.3622 | 7.9551 | 6.3959 | 5.0469 | 3.8306
COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD PRIMARY | MINIMUM HEADROOM | SP 50148 05901 | NO | YES | 19.76 | -5.6831 | -6.7617 | -7.976 | -9.3546 | -11.3311 | -13.5576 | -16.2525 | -19.1056 | -21.7648 | -34.2474 | -37.8056 | -38.0882 | -1.3627 | -1.9311 | -2.6301 | -3.674 | -5.2301 | -6.9464 | -9.0597 | -11.3209 | -13.4372 | -23.276 | -26.0076 | -26.3658 | -5.1985 | -6.1668 | -7.3342 | -8.6587 | -10.5607 | -12.6872 | -15.2801 | -18.0199 | -20.577 | -32.6454 | -36.075 | -36.3454
|  | OXFORD PRIMARY | EE |  |  |  |  | -5.6831 | -6.7617 | -7.976 | -9.3546 | -11.3311 | -13.5576 | -16.2525 | -19.1056 | -21.7648 | -30.2944 | -31.125 | -31.1342 | -1.3627 | -1.9311 | -2.6301 | -3.674 | -5.2301 | -6.9464 | -9.0597 | -11.3209 | -13.4372 | -20.1709 | -20.778 | -20.9648 | -5.1985 | -6.1668 | -7.3342 | -8.6587 | -10.5607 | -12.6872 | -15.2801 | -18.0199 | -20.577 | -28.778 | -29.5485 | -29.5617
|  | OXFORD PRIMARY | HT |  |  |  |  | -4.5729 | -5.1882 | -5.9138 | -7.3076 | -9.0699 | -11.0097 | -13.3678 | -16.2658 | -19.0076 | -26.9413 | -29.5127 | -29.7954 | -0.76784 | -1.076 | -1.4434 | -2.3505 | -3.5617 | -5.0403 | -6.9189 | -9.2434 | -11.4138 | -17.4576 | -19.325 | -19.5423 | -4.3934 | -4.8434 | -5.3699 | -6.6689 | -8.3638 | -10.2097 | -12.476 | -15.2689 | -17.9117 | -25.5423 | -27.9964 | -28.2566
|  | OXFORD PRIMARY | HE |  |  |  |  | -5.0036 | -5.9393 | -7.0097 | -8.2556 | -10.1627 | -12.3015 | -14.9546 | -17.975 | -21.2066 | -34.2474 | -37.8056 | -38.0882 | -1.0076 | -1.4954 | -2.0515 | -2.825 | -4.326 | -5.9791 | -8.0607 | -10.4587 | -13.024 | -23.276 | -26.0076 | -26.3658 | -4.6995 | -5.3923 | -6.3964 | -7.5944 | -9.427 | -11.475 | -14.027 | -16.9352 | -20.0566 | -32.6454 | -36.075 | -36.3454
|  | OXFORD PRIMARY | CF |  |  |  |  | -4.1117 | -4.5434 | -5.0791 | -5.7199 | -6.4566 | -7.4107 | -8.8423 | -10.577 | -12.4638 | -25.0882 | -30.5413 | -33.1036 | -0.54947 | -0.80049 | -1.0923 | -1.4393 | -1.8434 | -2.4393 | -3.4403 | -4.827 | -6.3372 | -16.4638 | -20.6648 | -23.3178 | -4.0209 | -4.3607 | -4.7627 | -5.2352 | -5.8852 | -6.8046 | -8.1831 | -9.8495 | -11.6648 | -23.8301 | -29.0801 | -31.5229
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | OXFORD SCIENCE PARK PRIMARY | MINIMUM HEADROOM | TBC | NO | NO | 27.185 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332
|  | OXFORD SCIENCE PARK PRIMARY | EE |  |  |  |  | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332
|  | OXFORD SCIENCE PARK PRIMARY | HT |  |  |  |  | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332
|  | OXFORD SCIENCE PARK PRIMARY | HE |  |  |  |  | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332
|  | OXFORD SCIENCE PARK PRIMARY | CF |  |  |  |  | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | OVERTON PRIMARY | MINIMUM HEADROOM | SU 52061 50913 | NO | NO | 1.96 | 23.1541 | 22.9674 | 22.7235 | 22.4848 | 22.1011 | 21.1082 | 19.8205 | 18.6582 | 17.3001 | 12.5582 | 10.8848 | 10.2796 | 24.1113 | 23.9756 | 23.799 | 23.6286 | 23.3654 | 23.0592 | 22.4399 | 21.8245 | 21.0113 | 17.5368 | 15.8664 | 13.1735 | 21.3194 | 21.1378 | 20.9011 | 20.6725 | 20.3154 | 19.5052 | 18.5021 | 17.5541 | 16.4439 | 12.6878 | 11.3929 | 10.899
|  | OVERTON PRIMARY | EE |  |  |  |  | 23.1541 | 22.9674 | 22.7235 | 22.4848 | 22.1011 | 21.6419 | 20.5929 | 19.8072 | 18.7399 | 13.1266 | 11.0552 | 10.3807 | 24.1113 | 23.9756 | 23.799 | 23.6286 | 23.3654 | 23.0592 | 22.4562 | 22.1745 | 21.6174 | 17.5368 | 15.8664 | 14.4399 | 21.3194 | 21.1378 | 20.9011 | 20.6725 | 20.3154 | 19.8807 | 18.9296 | 18.3837 | 17.5541 | 13.0858 | 11.549 | 10.9888
|  | OVERTON PRIMARY | HT |  |  |  |  | 23.3103 | 23.1337 | 22.946 | 22.7552 | 22.4296 | 21.1082 | 19.8205 | 18.6582 | 17.3001 | 12.5582 | 10.8848 | 10.2796 | 24.2592 | 24.1552 | 24.0378 | 23.9276 | 23.7419 | 23.0664 | 22.4399 | 21.8245 | 21.0113 | 17.8368 | 16.9378 | 16.6694 | 21.4786 | 21.3154 | 21.1358 | 20.9541 | 20.6541 | 19.5052 | 18.5021 | 17.5541 | 16.4439 | 12.6878 | 11.3929 | 10.899
|  | OVERTON PRIMARY | HE |  |  |  |  | 23.3164 | 23.148 | 22.9694 | 22.7888 | 22.4756 | 22.1174 | 21.3286 | 20.3511 | 19.4113 | 14.5725 | 12.0623 | 11.245 | 24.2358 | 24.1174 | 23.9919 | 23.8725 | 23.6725 | 23.449 | 23.0235 | 22.4848 | 21.9541 | 18.3041 | 16.3939 | 14.8654 | 21.4827 | 21.3266 | 21.1562 | 20.9858 | 20.698 | 20.3654 | 19.6674 | 18.8327 | 18.0501 | 14.2327 | 12.3684 | 11.7429
|  | OVERTON PRIMARY | CF |  |  |  |  | 23.4745 | 23.3623 | 23.2307 | 23.0664 | 22.8939 | 22.6521 | 22.3837 | 22.1745 | 21.8756 | 19.1358 | 13.3705 | 11.9062 | 24.3082 | 24.2215 | 24.1133 | 23.9919 | 23.8643 | 23.6766 | 23.4684 | 23.295 | 23.0562 | 21.146 | 16.2582 | 13.1735 | 21.6235 | 21.5174 | 21.396 | 21.2409 | 21.0807 | 20.8572 | 20.6052 | 20.4164 | 20.1348 | 17.9235 | 13.345 | 12.2592
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PADWORTH PRIMARY | MINIMUM HEADROOM | SU 62243 66052 | YES | NO | 0.121 | 5.1385 | 5.0906 | 5.0457 | 4.9804 | 4.9202 | 4.8253 | 4.7528 | 4.6518 | 4.5926 | 4.3099 | 4.1028 | 3.9865 | 5.1474 | 5.1066 | 5.075 | 5.0189 | 4.9648 | 4.8944 | 4.8372 | 4.7526 | 4.7036 | 4.4393 | 4.1454 | 3.4189 | 4.9837 | 4.9347 | 4.8939 | 4.8255 | 4.7602 | 4.6643 | 4.5949 | 4.4878 | 4.4367 | 4.1582 | 3.9653 | 3.8561
|  | PADWORTH PRIMARY | EE |  |  |  |  | 5.1385 | 5.0906 | 5.0457 | 4.9804 | 4.9202 | 4.8253 | 4.7528 | 4.6518 | 4.5926 | 4.3099 | 4.1671 | 4.0732 | 5.1474 | 5.1066 | 5.075 | 5.0189 | 4.9648 | 4.8944 | 4.8372 | 4.7526 | 4.7036 | 4.4791 | 4.2536 | 3.8903 | 4.9837 | 4.9347 | 4.8939 | 4.8255 | 4.7602 | 4.6643 | 4.5949 | 4.4878 | 4.4367 | 4.2092 | 4.0939 | 4.0102
|  | PADWORTH PRIMARY | HT |  |  |  |  | 5.1763 | 5.1436 | 5.1048 | 5.0548 | 5.0008 | 4.9457 | 4.8661 | 4.7804 | 4.6906 | 4.3273 | 4.1355 | 4.0253 | 5.1893 | 5.1658 | 5.1423 | 5.1056 | 5.0607 | 5.0311 | 4.9668 | 4.9015 | 4.8281 | 4.5352 | 4.4179 | 4.3505 | 5.0296 | 4.998 | 4.9622 | 4.9112 | 4.852 | 4.8061 | 4.7296 | 4.6439 | 4.5541 | 4.2214 | 4.0633 | 3.9704
|  | PADWORTH PRIMARY | HE |  |  |  |  | 5.1773 | 5.1436 | 5.1059 | 5.061 | 5.0099 | 4.9599 | 4.8895 | 4.8079 | 4.7263 | 4.3099 | 4.1028 | 3.9865 | 5.1832 | 5.1556 | 5.127 | 5.0883 | 5.0413 | 5.0056 | 4.9362 | 4.8607 | 4.7832 | 4.4393 | 4.2781 | 3.923 | 5.0306 | 4.998 | 4.9643 | 4.9163 | 4.8602 | 4.8194 | 4.751 | 4.6714 | 4.5888 | 4.1582 | 3.9653 | 3.8561
|  | PADWORTH PRIMARY | CF |  |  |  |  | 5.2028 | 5.1793 | 5.1477 | 5.1212 | 5.0844 | 5.0446 | 5.0161 | 4.9681 | 4.9253 | 4.663 | 4.3977 | 4.1702 | 5.1964 | 5.176 | 5.1444 | 5.1199 | 5.0852 | 5.0423 | 5.0056 | 4.9566 | 4.9097 | 4.5832 | 4.1454 | 3.4189 | 5.052 | 5.0316 | 4.9959 | 4.9714 | 4.9316 | 4.8898 | 4.8643 | 4.8122 | 4.7684 | 4.5041 | 4.2388 | 4.0265
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PANGBOURNE PRIMARY | MINIMUM HEADROOM | SU 62960 76144 | NO | NO | 1.276 | 14.6262 | 14.3844 | 14.1742 | 13.8977 | 13.5977 | 13.1732 | 13.2303 | 12.8446 | 12.516 | 11.1507 | 10.0936 | 9.417 | 16.9609 | 16.7874 | 16.6283 | 16.417 | 16.1905 | 15.8946 | 15.9048 | 15.6211 | 15.4364 | 14.3813 | 13.1599 | 10.264 | 14.416 | 14.1956 | 13.9997 | 13.7466 | 13.4691 | 13.0701 | 13.066 | 12.6987 | 12.4283 | 11.1966 | 10.3405 | 9.7834
|  | PANGBOURNE PRIMARY | EE |  |  |  |  | 14.6262 | 14.3844 | 14.1742 | 13.8977 | 13.5977 | 13.1732 | 13.2303 | 12.8446 | 12.6007 | 11.1507 | 10.214 | 9.5752 | 16.9609 | 16.7874 | 16.6283 | 16.417 | 16.1905 | 15.8946 | 15.9048 | 15.6211 | 15.4364 | 14.3813 | 13.3579 | 11.8762 | 14.416 | 14.1956 | 13.9997 | 13.7466 | 13.4691 | 13.0701 | 13.066 | 12.6987 | 12.4568 | 11.1966 | 10.4681 | 9.9252
|  | PANGBOURNE PRIMARY | HT |  |  |  |  | 14.7354 | 14.5813 | 14.4426 | 14.2385 | 14.0079 | 13.7262 | 13.3497 | 12.9507 | 12.516 | 11.1905 | 10.0936 | 9.417 | 17.0854 | 16.9762 | 16.8864 | 16.7528 | 16.6028 | 16.4364 | 16.2079 | 15.9538 | 15.6762 | 15.0201 | 14.5211 | 14.2344 | 14.5415 | 14.3793 | 14.2364 | 14.0446 | 13.8323 | 13.5599 | 13.2068 | 12.8334 | 12.4283 | 11.2374 | 10.3405 | 9.7834
|  | PANGBOURNE PRIMARY | HE |  |  |  |  | 14.7436 | 14.5977 | 14.464 | 14.267 | 14.0477 | 13.8058 | 13.463 | 13.1017 | 12.7272 | 11.5211 | 10.5966 | 10.1772 | 17.0538 | 16.9334 | 16.8283 | 16.6813 | 16.5119 | 16.3415 | 16.0966 | 15.8293 | 15.5517 | 14.5854 | 13.5568 | 12.1691 | 14.5466 | 14.3915 | 14.2568 | 14.0732 | 13.8711 | 13.6395 | 13.3191 | 12.9823 | 12.6334 | 11.5323 | 10.816 | 10.4732
|  | PANGBOURNE PRIMARY | CF |  |  |  |  | 14.8405 | 14.7374 | 14.6048 | 14.5058 | 14.3558 | 14.1864 | 14.0395 | 13.8283 | 13.6089 | 12.8681 | 11.8477 | 10.8691 | 17.1048 | 17.0017 | 16.8895 | 16.8007 | 16.6691 | 16.5089 | 16.3589 | 16.1568 | 15.9395 | 14.9211 | 13.1599 | 10.264 | 14.6374 | 14.5262 | 14.4017 | 14.3109 | 14.1732 | 14.0191 | 13.8834 | 13.6926 | 13.4895 | 12.7252 | 11.7854 | 10.9589
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE PRIMARY | MINIMUM HEADROOM | SU 51369 08259 | NO | NO | 3.285 | 16.5796 | 15.9418 | 15.7153 | 15.201 | 14.6551 | 13.7531 | 12.7663 | 11.7918 | 11.0847 | 7.0194 | 3.9765 | 2.2561 | 18.8235 | 18.3449 | 18.2092 | 17.7918 | 17.3408 | 16.6867 | 15.9571 | 15.2194 | 14.7112 | 11.9153 | 7.9378 | -1.3327 | 16.4796 | 15.85 | 15.7194 | 15.2204 | 14.6878 | 13.8418 | 12.9041 | 11.9735 | 11.348 | 7.8939 | 5.2837 | 3.799
|  | PARK GATE PRIMARY | EE |  |  |  |  | 16.5796 | 15.9418 | 15.7153 | 15.201 | 14.6551 | 13.7531 | 12.7663 | 11.7918 | 11.0847 | 7.4561 | 4.6908 | 2.5673 | 18.8235 | 18.3449 | 18.2092 | 17.7918 | 17.3408 | 16.6867 | 15.9571 | 15.2194 | 14.7112 | 11.9153 | 8.7102 | 3.7867 | 16.4796 | 15.85 | 15.7194 | 15.2204 | 14.6878 | 13.8418 | 12.9041 | 11.9735 | 11.348 | 8.2449 | 5.9041 | 4.0561
|  | PARK GATE PRIMARY | HT |  |  |  |  | 16.7439 | 16.2602 | 15.801 | 15.3194 | 14.6847 | 14.2112 | 13.3459 | 12.4602 | 11.5755 | 7.0194 | 3.9765 | 2.2561 | 19.0071 | 18.8306 | 18.5429 | 18.2316 | 17.7867 | 17.6531 | 17.1633 | 16.65 | 16.1357 | 13.7347 | 12.3847 | 11.648 | 16.7112 | 16.2724 | 15.8378 | 15.3735 | 14.7735 | 14.4276 | 13.6388 | 12.8245 | 12.0112 | 7.8939 | 5.2837 | 3.799
|  | PARK GATE PRIMARY | HE |  |  |  |  | 16.8653 | 16.3837 | 15.949 | 15.4969 | 15.3531 | 14.6929 | 13.9837 | 13.252 | 12.5163 | 8.7031 | 5.9663 | 4.5765 | 19.0224 | 18.7357 | 18.3959 | 18.0347 | 17.9439 | 17.4602 | 16.9235 | 16.3561 | 15.7694 | 12.5408 | 9.2837 | 4.652 | 16.8031 | 16.3714 | 15.9571 | 15.5235 | 15.4418 | 14.8388 | 14.1755 | 13.4918 | 12.802 | 9.3643 | 7.0439 | 5.8541
|  | PARK GATE PRIMARY | CF |  |  |  |  | 17.2694 | 16.9592 | 16.75 | 16.5031 | 16.2286 | 15.9469 | 15.9265 | 15.55 | 15.1592 | 12.4133 | 9.5827 | 6.9643 | 19.2102 | 18.9714 | 18.7418 | 18.4592 | 18.1276 | 17.7449 | 17.6143 | 17.1388 | 16.6418 | 13.1898 | 7.9378 | -1.3327 | 17.1418 | 16.8469 | 16.6357 | 16.3633 | 16.0684 | 15.75 | 15.8694 | 15.4969 | 15.1051 | 12.5245 | 10.0633 | 7.8551
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PARK HOUSE PRIMARY | MINIMUM HEADROOM | SU 23138 43780 | NO | NO | 0.035 | 3.2067 | 3.1476 | 3.0669 | 2.9771 | 2.92 | 2.8027 | 2.668 | 2.5302 | 2.4659 | 2.2302 | 2.1108 | 2.0139 | 3.5014 | 3.4576 | 3.3963 | 3.3269 | 3.2861 | 3.1984 | 3.0984 | 2.9922 | 2.9473 | 2.7708 | 2.4627 | 1.7861 | 3.2131 | 3.1549 | 3.0763 | 2.9886 | 2.9345 | 2.8212 | 2.6876 | 2.5549 | 2.4937 | 2.2804 | 2.1804 | 2.0947
|  | PARK HOUSE PRIMARY | EE |  |  |  |  | 3.2067 | 3.1476 | 3.0669 | 2.9771 | 2.92 | 2.8027 | 2.668 | 2.5302 | 2.4659 | 2.2302 | 2.1108 | 2.0588 | 3.5014 | 3.4576 | 3.3963 | 3.3269 | 3.2861 | 3.1984 | 3.0984 | 2.9922 | 2.9473 | 2.7708 | 2.5637 | 2.2331 | 3.2131 | 3.1549 | 3.0763 | 2.9886 | 2.9345 | 2.8212 | 2.6876 | 2.5549 | 2.4937 | 2.2804 | 2.1804 | 2.1324
|  | PARK HOUSE PRIMARY | HT |  |  |  |  | 3.269 | 3.2169 | 3.1486 | 3.1067 | 3.0353 | 2.9547 | 2.8537 | 2.7873 | 2.6812 | 2.2935 | 2.1251 | 2.0139 | 3.5555 | 3.5239 | 3.479 | 3.4504 | 3.4024 | 3.3514 | 3.2841 | 3.2473 | 3.1739 | 2.932 | 2.8473 | 2.7933 | 3.2722 | 3.2253 | 3.1569 | 3.1171 | 3.0478 | 2.9692 | 2.8722 | 2.808 | 2.7039 | 2.3406 | 2.1916 | 2.0947
|  | PARK HOUSE PRIMARY | HE |  |  |  |  | 3.27 | 3.219 | 3.1547 | 3.1129 | 3.0465 | 2.968 | 2.87 | 2.8078 | 2.7027 | 2.2843 | 2.1731 | 2.1302 | 3.5494 | 3.5157 | 3.4667 | 3.4351 | 3.3861 | 3.331 | 3.2596 | 3.2147 | 3.1382 | 2.8137 | 2.6045 | 2.2841 | 3.2743 | 3.2263 | 3.162 | 3.1233 | 3.0559 | 2.9824 | 2.8865 | 2.8284 | 2.7284 | 2.3355 | 2.2386 | 2.2008
|  | PARK HOUSE PRIMARY | CF |  |  |  |  | 3.2761 | 3.2333 | 3.1965 | 3.1384 | 3.1037 | 3.0465 | 2.9894 | 2.9169 | 2.8414 | 2.5006 | 2.3251 | 2.168 | 3.5494 | 3.5229 | 3.4922 | 3.4484 | 3.4198 | 3.3729 | 3.3198 | 3.2596 | 3.1933 | 2.8433 | 2.4627 | 1.7861 | 3.2804 | 3.2416 | 3.2029 | 3.1488 | 3.1182 | 3.062 | 3.0049 | 2.9345 | 2.861 | 2.5314 | 2.3702 | 2.2263
MINETY GSP | STRATTON (MAIN) BSP | PARK NORTH PRIMARY | MINIMUM HEADROOM | SU 18052 84542 | NO | NO | 4.55 | 7.5667 | 6.9086 | 6.0198 | 5.0535 | 4.0065 | 2.3759 | 0.50959 | -1.3996 | -2.8445 | -8.219 | -11.4139 | -11.9557 | 8.8749 | 8.3627 | 7.6096 | 6.7524 | 5.8422 | 4.6698 | 3.3045 | 1.8922 | 0.82898 | -3.9363 | -10.1843 | -23.6792 | 7.4229 | 6.8106 | 5.9086 | 4.9086 | 3.8637 | 2.3463 | 0.59735 | -1.1853 | -2.5088 | -7.9404 | -11.4231 | -11.9118
|  | PARK NORTH PRIMARY | EE |  |  |  |  | 7.5667 | 6.9086 | 6.0198 | 5.0535 | 4.0065 | 2.3759 | 0.50959 | -1.3996 | -2.8445 | -8.219 | -10.8394 | -10.8108 | 8.8749 | 8.3627 | 7.6096 | 6.7524 | 5.8422 | 4.6698 | 3.3045 | 1.8922 | 0.82898 | -3.8476 | -8.0486 | -13.8537 | 7.4229 | 6.8106 | 5.9086 | 4.9086 | 3.8637 | 2.3463 | 0.59735 | -1.1853 | -2.5088 | -7.268 | -9.4843 | -9.4027
|  | PARK NORTH PRIMARY | HT |  |  |  |  | 8.1504 | 7.4382 | 6.6994 | 6.1463 | 5.38 | 4.0269 | 2.5555 | 1.079 | -0.35776 | -7.1986 | -10.871 | -11.5231 | 9.5504 | 9.0616 | 8.5331 | 8.1718 | 7.5912 | 6.7749 | 5.8351 | 4.8708 | 3.93 | -0.2149 | -2.2659 | -2.7139 | 8.0984 | 7.4351 | 6.7137 | 6.2178 | 5.4341 | 4.182 | 2.7831 | 1.3667 | -0.02 | -6.2414 | -9.4751 | -9.9567
|  | PARK NORTH PRIMARY | HE |  |  |  |  | 8.0504 | 7.2953 | 6.5045 | 5.9127 | 5.0902 | 3.7912 | 2.2973 | 0.6851 | -0.93327 | -7.7986 | -11.4139 | -11.9557 | 9.3371 | 8.7351 | 8.0871 | 7.6096 | 6.8647 | 5.9106 | 4.779 | 3.5351 | 2.2535 | -3.9363 | -8.8986 | -14.9016 | 7.9922 | 7.2871 | 6.5137 | 5.9902 | 5.1545 | 3.9351 | 2.5065 | 0.96061 | -0.60163 | -7.9404 | -11.4231 | -11.9118
|  | PARK NORTH PRIMARY | CF |  |  |  |  | 8.6239 | 8.1484 | 7.6698 | 7.1484 | 6.731 | 6.5494 | 5.9596 | 5.3024 | 4.5851 | -0.99551 | -6.4118 | -10.3016 | 9.6524 | 9.2014 | 8.7167 | 8.1596 | 7.6167 | 7.2657 | 6.5137 | 5.682 | 4.7902 | -1.5027 | -10.1843 | -23.6792 | 8.529 | 8.081 | 7.6065 | 7.082 | 6.6239 | 6.4769 | 5.8504 | 5.1514 | 4.4035 | -0.76388 | -5.9771 | -9.2751
WILLESDEN GSP | ACTON LANE BSP | PARK ROYAL PRIMARY | MINIMUM HEADROOM | TQ 20137 82215 | NO | YES | 4.396 | -0.85594 | -1.2335 | 38.5517 | 37.9497 | 37.2497 | 36.616 | 35.917 | 35.3731 | 34.8507 | 33.0782 | 31.7731 | 31.214 | 0.49794 | 0.2061 | 38.4405 | 38.0854 | 37.6619 | 37.065 | 36.2415 | 35.567 | 34.9038 | 33.1691 | 32.1374 | 31.467 | -0.5142 | -0.86624 | 37.7487 | 37.3027 | 36.7109 | 36.065 | 35.2344 | 34.4507 | 33.6956 | 31.7956 | 30.4446 | 29.7803
|  | PARK ROYAL PRIMARY | EE |  |  |  |  | -0.85594 | -1.2335 | 38.5517 | 37.9497 | 37.2497 | 36.616 | 35.917 | 35.3731 | 34.8507 | 33.2007 | 32.6752 | 32.1752 | 0.49794 | 0.2061 | 38.4405 | 38.0854 | 37.6619 | 37.065 | 36.2415 | 35.567 | 34.9038 | 33.1691 | 32.5864 | 31.9782 | -0.5142 | -0.86624 | 37.7487 | 37.3027 | 36.7109 | 36.065 | 35.2344 | 34.4507 | 33.6956 | 31.7956 | 31.1925 | 30.5895
|  | PARK ROYAL PRIMARY | HT |  |  |  |  | -0.73553 | -1.0621 | 38.7456 | 38.1987 | 37.6323 | 37.0772 | 36.4905 | 35.9966 | 35.4874 | 34.0558 | 32.8109 | 32.2221 | 0.58365 | 0.33876 | 38.6242 | 38.2884 | 37.9997 | 37.5099 | 36.964 | 36.5231 | 35.9599 | 33.7425 | 32.5099 | 31.8619 | -0.37237 | -0.65094 | 38.067 | 37.5793 | 37.0823 | 36.5089 | 35.8884 | 35.3813 | 34.8466 | 32.5333 | 31.1609 | 30.4721
|  | PARK ROYAL PRIMARY | HE |  |  |  |  | -0.74676 | -1.0917 | 38.6936 | 38.1242 | 37.4599 | 36.9313 | 36.3558 | 35.9252 | 35.4915 | 33.0782 | 31.7731 | 31.214 | 0.59488 | 0.32957 | 38.5864 | 38.2344 | 37.8242 | 37.3762 | 36.8497 | 36.3272 | 35.7578 | 33.3231 | 32.1374 | 31.467 | -0.39278 | -0.71216 | 37.9548 | 37.5262 | 36.9191 | 36.3925 | 35.8027 | 35.3078 | 34.6221 | 31.8119 | 30.4446 | 29.7803
|  | PARK ROYAL PRIMARY | CF |  |  |  |  | -0.38757 | -0.50696 | 39.565 | 39.3293 | 39.0201 | 38.517 | 37.8731 | 37.2772 | 36.7252 | 35.3568 | 33.9813 | 33.1425 | 0.81835 | 0.73161 | 39.116 | 38.9119 | 38.6456 | 38.2221 | 37.717 | 37.2589 | 36.8425 | 35.3507 | 34.1487 | 32.6578 | -0.077469 | -0.18869 | 38.6364 | 38.414 | 38.1262 | 37.6701 | 37.1058 | 36.5772 | 36.0742 | 34.218 | 32.7803 | 31.9568
MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE NORTH PRIMARY | MINIMUM HEADROOM | SZ 03222 92233 | NO | YES | 3.079 | 5.4863 | 4.8587 | 3.7352 | 2.5832 | 1.3516 | -0.24231 | -2.0944 | -3.9311 | -5.2913 | -12.6352 | -18.9607 | -22.4403 | 13.0403 | 12.5832 | 11.7005 | 10.7536 | 9.7301 | 8.521 | 7.122 | 5.7056 | 4.7016 | -0.77088 | -7.8913 | -25.778 | 6.4832 | 5.9097 | 4.8434 | 3.723 | 2.5159 | 0.97504 | -0.75864 | -2.4801 | -3.7239 | -10.0046 | -15.4056 | -18.2372
|  | PARKSTONE NORTH PRIMARY | EE |  |  |  |  | 5.4863 | 4.8587 | 3.7352 | 2.5832 | 1.3516 | -0.24231 | -2.0944 | -3.9311 | -5.2913 | -12.2964 | -17.8015 | -22.0872 | 13.0403 | 12.5832 | 11.7005 | 10.7536 | 9.7301 | 8.521 | 7.122 | 5.7056 | 4.7016 | -0.77088 | -6.728 | -16.1627 | 6.4832 | 5.9097 | 4.8434 | 3.723 | 2.5159 | 0.97504 | -0.75864 | -2.4801 | -3.7239 | -9.9148 | -14.4352 | -17.9923
|  | PARKSTONE NORTH PRIMARY | HT |  |  |  |  | 6.0342 | 5.1414 | 4.3005 | 3.4271 | 2.421 | 0.99544 | -0.5566 | -2.1831 | -3.8454 | -12.6352 | -18.9607 | -22.4403 | 13.7883 | 13.2056 | 12.8056 | 12.2485 | 11.6046 | 10.8097 | 9.8965 | 8.9199 | 7.9056 | 3.1108 | 0.31075 | -1.0576 | 7.124 | 6.3036 | 5.6016 | 4.7822 | 3.8373 | 2.5281 | 1.0852 | -0.43721 | -2.0015 | -10.0046 | -15.4056 | -18.2372
|  | PARKSTONE NORTH PRIMARY | HE |  |  |  |  | 6.071 | 5.2465 | 4.5577 | 3.6414 | 2.6516 | 1.4934 | 0.21279 | -1.1199 | -2.5107 | -10.0046 | -15.5688 | -18.0505 | 13.623 | 12.971 | 12.5312 | 11.822 | 11.0475 | 10.1812 | 9.1771 | 8.1005 | 6.9465 | 0.50463 | -5.6739 | -14.4352 | 7.1434 | 6.3781 | 5.7965 | 4.9505 | 4.0271 | 2.9403 | 1.722 | 0.4434 | -0.89537 | -7.7495 | -12.3954 | -14.3984
|  | PARKSTONE NORTH PRIMARY | CF |  |  |  |  | 6.5893 | 6.1087 | 5.5791 | 5.3332 | 4.7444 | 4.3046 | 3.7444 | 3.1271 | 2.4924 | -2.3025 | -7.6454 | -12.7086 | 13.8556 | 13.375 | 12.8301 | 12.5465 | 11.8954 | 11.2342 | 10.4352 | 9.5699 | 8.6444 | 2.1138 | -7.8913 | -25.778 | 7.6179 | 7.1648 | 6.6556 | 6.4516 | 5.8975 | 5.4495 | 4.8812 | 4.2536 | 3.6005 | -0.95251 | -5.7668 | -10.1433
MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE SOUTH PRIMARY | MINIMUM HEADROOM | SZ 04762 89848 | NO | YES | 1.616 | 18.6245 | 18.1224 | 17.5388 | 16.8929 | 16.7602 | 15.8745 | 14.8663 | 13.8633 | 13.098 | 9.0531 | 5.5571 | 3.7112 | 19.6082 | 19.2071 | 18.7286 | 18.1867 | 18.0673 | 17.4347 | 16.6959 | 15.9459 | 15.3612 | 12.2765 | 8.7531 | -0.65102 | 18.5173 | 18.0439 | 17.4796 | 16.848 | 16.7561 | 15.9449 | 14.9959 | 14.0469 | 13.3378 | 9.7041 | 6.5694 | 4.9878
|  | PARKSTONE SOUTH PRIMARY | EE |  |  |  |  | 18.6245 | 18.1224 | 17.5388 | 16.8929 | 16.7602 | 15.8745 | 14.8663 | 13.8633 | 13.098 | 9.2847 | 6.4765 | 4.0663 | 19.6082 | 19.2071 | 18.7286 | 18.1867 | 18.0673 | 17.4347 | 16.6959 | 15.9459 | 15.3612 | 12.2765 | 9.0867 | 4.0418 | 18.5173 | 18.0439 | 17.4796 | 16.848 | 16.7561 | 15.9449 | 14.9959 | 14.0469 | 13.3378 | 9.8612 | 7.4 | 5.299
|  | PARKSTONE SOUTH PRIMARY | HT |  |  |  |  | 18.9694 | 18.5276 | 18.1143 | 17.7112 | 17.2163 | 16.3867 | 15.8714 | 14.9776 | 14.052 | 9.0531 | 5.5571 | 3.7112 | 19.9745 | 19.699 | 19.4112 | 19.1347 | 18.7827 | 18.2908 | 18.1327 | 17.5959 | 17.0347 | 14.2673 | 12.5908 | 11.849 | 18.8531 | 18.45 | 18.052 | 17.6827 | 17.2082 | 16.4388 | 16.0071 | 15.1765 | 14.3153 | 9.7041 | 6.5694 | 4.9878
|  | PARKSTONE SOUTH PRIMARY | HE |  |  |  |  | 18.9898 | 18.6357 | 18.2388 | 17.8694 | 17.4265 | 16.7367 | 16.3765 | 15.6531 | 14.8969 | 10.9255 | 8.1 | 6.8163 | 19.9041 | 19.6204 | 19.2969 | 18.9847 | 18.5969 | 18.0908 | 17.8694 | 17.3133 | 16.7143 | 13.3143 | 10.0051 | 5.4776 | 18.8714 | 18.5429 | 18.1622 | 17.8255 | 17.399 | 16.7551 | 16.4776 | 15.8031 | 15.098 | 11.4143 | 8.9163 | 7.8306
|  | PARKSTONE SOUTH PRIMARY | CF |  |  |  |  | 19.2398 | 19.0571 | 18.8276 | 18.6255 | 18.349 | 18.0378 | 17.6357 | 17.6735 | 17.302 | 14.7908 | 12.048 | 9.3469 | 20.0255 | 19.8255 | 19.5786 | 19.3367 | 19.0112 | 18.6327 | 18.1673 | 18.0041 | 17.5224 | 14.102 | 8.7531 | -0.65102 | 19.1102 | 18.9347 | 18.7122 | 18.5194 | 18.251 | 17.948 | 17.5582 | 17.6122 | 17.25 | 14.8888 | 12.4061 | 9.9673
FLEET-BRAMLEY GSP | WOKINGHAM BSP | PEACOCK FARM PRIMARY | MINIMUM HEADROOM | SU 84770 68709 | NO | NO | 6.854 | 5.9419 | 5.7287 | 5.5399 | 5.3358 | 5.1603 | 4.4562 | 3.647 | 2.993 | 2.3899 | -0.071327 | -2.1019 | -3.4591 | 6.9246 | 6.7685 | 6.6062 | 6.4256 | 6.2593 | 5.5072 | 4.6266 | 3.9317 | 3.2603 | 1.1338 | -1.104 | -4.4438 | 6.243 | 6.047 | 5.8419 | 5.6195 | 5.4491 | 4.6419 | 3.7032 | 2.9552 | 2.2848 | -0.18561 | -2.3468 | -3.8081
|  | PEACOCK FARM PRIMARY | EE |  |  |  |  | 5.9419 | 5.7287 | 5.5399 | 5.3358 | 5.1603 | 4.4562 | 3.647 | 2.993 | 2.3899 | 0.57357 | -0.93765 | -2.3866 | 6.9246 | 6.7685 | 6.6062 | 6.4256 | 6.2593 | 5.5072 | 4.6266 | 3.9317 | 3.2603 | 1.1338 | -1.104 | -4.4438 | 6.243 | 6.047 | 5.8419 | 5.6195 | 5.4491 | 4.6419 | 3.7032 | 2.9552 | 2.2848 | 0.545 | -0.99276 | -2.5285
|  | PEACOCK FARM PRIMARY | HT |  |  |  |  | 6.0103 | 5.8072 | 5.6521 | 5.5032 | 5.3236 | 4.6511 | 3.9328 | 3.2991 | 2.6093 | -0.071327 | -2.1019 | -3.4591 | 7.0399 | 6.9307 | 6.8379 | 6.7532 | 6.6409 | 5.9736 | 5.2328 | 4.6154 | 3.9236 | 1.5297 | -0.20908 | -1.4264 | 6.343 | 6.1654 | 6.0113 | 5.8797 | 5.6991 | 4.9297 | 4.1164 | 3.4001 | 2.6083 | -0.18561 | -2.3468 | -3.8081
|  | PEACOCK FARM PRIMARY | HE |  |  |  |  | 6.0236 | 5.8389 | 5.6899 | 5.5562 | 5.3858 | 4.9011 | 4.3746 | 4.0246 | 3.6368 | 1.8368 | 0.31133 | -0.88561 | 6.9909 | 6.8583 | 6.7317 | 6.6215 | 6.4726 | 5.9552 | 5.3593 | 4.997 | 4.5787 | 2.4246 | 0.13276 | -3.1234 | 6.3501 | 6.193 | 6.0409 | 5.9226 | 5.7511 | 5.193 | 4.595 | 4.2052 | 3.7705 | 1.9879 | 0.42459 | -0.8948
|  | PEACOCK FARM PRIMARY | CF |  |  |  |  | 6.1256 | 5.9899 | 5.8889 | 5.7828 | 5.6909 | 5.4134 | 5.0215 | 4.6858 | 4.4399 | 3.3001 | 2.7083 | 1.8623 | 7.0307 | 6.9042 | 6.7981 | 6.6746 | 6.5491 | 6.1583 | 5.6205 | 5.1481 | 4.7603 | 2.9399 | 0.57459 | -4.0519 | 6.4409 | 6.3185 | 6.2185 | 6.1042 | 6.0226 | 5.6807 | 5.2001 | 4.7797 | 4.494 | 3.2634 | 2.9174 | 2.2103
WILLESDEN GSP |  | PERIVALE PRIMARY | MINIMUM HEADROOM | TQ 17544 82947 | NO | YES | 16.031 | 47.3615 | 46.8901 | 46.3227 | 45.7391 | 43.6982 | 42.8584 | 41.4921 | 40.8748 | 38.0095 | 31.0401 | 22.8686 | 15.684 | 51.1584 | 50.8258 | 49.9931 | 49.3809 | 46.9595 | 45.8952 | 44.437 | 43.9135 | 40.5697 | 32.3237 | 21.9452 | 7.3452 | 47.9809 | 47.6493 | 46.7268 | 46.1809 | 43.8411 | 42.6584 | 41.1697 | 40.636 | 37.2768 | 29.4482 | 20.2809 | 10.8513
|  | PERIVALE PRIMARY | EE |  |  |  |  | 47.3615 | 46.8901 | 46.8462 | 46.4033 | 45.4686 | 44.2482 | 43.3891 | 41.7697 | 40.835 | 35.7309 | 25.588 | 22.2278 | 51.1584 | 50.8258 | 50.7554 | 50.3533 | 49.338 | 48.1748 | 47.4993 | 45.8635 | 44.8931 | 38.9472 | 25.1411 | 16.4788 | 47.9809 | 47.6758 | 47.5625 | 47.1931 | 46.1605 | 44.8686 | 44.0544 | 42.2942 | 41.2748 | 35.6707 | 23.6003 | 19.5268
|  | PERIVALE PRIMARY | HT |  |  |  |  | 47.7135 | 47.2309 | 46.6278 | 46.2503 | 44.5523 | 43.6768 | 42.2135 | 41.386 | 39.6891 | 32.7676 | 22.8686 | 16.4799 | 51.4462 | 51.0503 | 50.484 | 50.2431 | 48.3768 | 47.4952 | 46.0656 | 45.4431 | 43.7503 | 37.3962 | 26.5278 | 18.9595 | 48.1799 | 47.7646 | 47.1615 | 46.8972 | 44.9778 | 43.8217 | 42.2452 | 41.4115 | 39.5033 | 31.934 | 20.2809 | 12.5237
|  | PERIVALE PRIMARY | HE |  |  |  |  | 47.7084 | 47.1635 | 46.3227 | 45.7391 | 43.6982 | 42.8584 | 41.4921 | 40.8748 | 38.0095 | 31.0401 | 23.8115 | 15.684 | 51.4115 | 50.9074 | 49.9931 | 49.3809 | 46.9595 | 45.8952 | 44.437 | 43.9135 | 40.5697 | 32.3237 | 21.9452 | 7.3452 | 48.1595 | 47.6493 | 46.7268 | 46.1809 | 43.8411 | 42.6584 | 41.1697 | 40.636 | 37.2768 | 29.4482 | 20.8727 | 10.8513
|  | PERIVALE PRIMARY | CF |  |  |  |  | 47.9125 | 47.7513 | 47.535 | 47.2013 | 46.7452 | 46.1646 | 45.6074 | 45.5727 | 44.9595 | 40.7472 | 35.5931 | 30.5737 | 51.4962 | 51.3615 | 51.1676 | 50.7166 | 50.1176 | 49.3605 | 48.6391 | 48.2411 | 47.3768 | 41.2829 | 31.6074 | 17.2921 | 48.3737 | 48.2697 | 48.1288 | 47.8044 | 47.3768 | 46.8156 | 46.2391 | 46.0666 | 45.3901 | 40.7309 | 34.8717 | 29.288
FLEET-BRAMLEY GSP | FERNHURST BSP | PETERSFIELD PRIMARY | MINIMUM HEADROOM | SU 74173 23420 | NO | NO | 8.678 | 3.522 | 2.8455 | 2.5853 | 1.8761 | 1.1159 | -0.0014449 | -1.2616 | -2.5331 | -3.4535 | -8.0065 | -11.6014 | -13.6086 | 8.5935 | 8.0649 | 7.8618 | 7.3016 | 6.6904 | 5.8996 | 4.9853 | 4.0557 | 3.4016 | -0.00042449 | -3.6157 | -13.0014 | 3.4588 | 2.8159 | 2.6128 | 1.9475 | 1.2179 | 0.16692 | -1.0259 | -2.228 | -3.077 | -7.1657 | -10.1953 | -11.9229
|  | PETERSFIELD PRIMARY | EE |  |  |  |  | 3.522 | 2.8455 | 2.5853 | 1.8761 | 1.1159 | -0.0014449 | -1.2616 | -2.5331 | -3.4535 | -8.0065 | -10.9688 | -13.1606 | 8.5935 | 8.0649 | 7.8618 | 7.3016 | 6.6904 | 5.8996 | 4.9853 | 4.0557 | 3.4016 | -0.00042449 | -3.2045 | -8.0372 | 3.4588 | 2.8159 | 2.6128 | 1.9475 | 1.2179 | 0.16692 | -1.0259 | -2.228 | -3.077 | -7.1657 | -9.6423 | -11.5627
|  | PETERSFIELD PRIMARY | HT |  |  |  |  | 3.9822 | 3.5261 | 2.9904 | 2.3781 | 2.1353 | 1.1986 | 0.171 | -0.91981 | -2.0627 | -7.9004 | -11.6014 | -13.6086 | 9.0608 | 8.7659 | 8.4108 | 7.9955 | 7.8843 | 7.3455 | 6.7312 | 6.07 | 5.373 | 2.0353 | 0.24039 | -0.62389 | 3.9261 | 3.5128 | 3.0179 | 2.4486 | 2.2445 | 1.3812 | 0.42304 | -0.59124 | -1.6565 | -7.0137 | -10.1953 | -11.9229
|  | PETERSFIELD PRIMARY | HE |  |  |  |  | 3.9669 | 3.5179 | 2.9996 | 2.4037 | 2.1853 | 1.3588 | 0.43427 | -0.55349 | -1.5953 | -7.2902 | -10.3249 | -11.6014 | 8.9486 | 8.6057 | 8.1935 | 7.7251 | 7.5496 | 6.969 | 6.2955 | 5.5679 | 4.7914 | 0.5506 | -2.9576 | -7.5178 | 3.9088 | 3.5037 | 3.0241 | 2.471 | 2.0241 | 1.2781 | 0.38325 | -0.579 | -1.5994 | -6.4943 | -9.2668 | -10.4259
|  | PETERSFIELD PRIMARY | CF |  |  |  |  | 4.2945 | 3.97 | 3.6792 | 3.319 | 2.922 | 2.8914 | 2.4445 | 1.9567 | 1.4435 | -2.178 | -5.8331 | -8.9698 | 9.1261 | 8.8292 | 8.5465 | 8.1996 | 7.7955 | 7.6608 | 7.171 | 6.6384 | 6.0669 | 2.0373 | -3.6157 | -13.0014 | 4.1955 | 3.8863 | 3.62 | 3.2771 | 2.8945 | 2.9088 | 2.4894 | 2.019 | 1.473 | -2.08 | -5.4076 | -8.0351
IVER 132KV GSP | CHALVEY BSP | PETERSFIELD AVENUE PRIMARY | MINIMUM HEADROOM | SU 98108 80286 | NO | YES | 13.08 | 26.1803 | 24.564 | 22.6374 | 20.8395 | 18.8701 | 17.4221 | 16.1486 | 14.916 | 13.8762 | 10.7048 | 7.6986 | 6.7323 | 28.8499 | 27.9335 | 26.8448 | 25.9335 | 24.7917 | 23.458 | 22.1019 | 20.8601 | 19.6856 | 15.2876 | 10.9988 | -0.16748 | 25.8811 | 24.5086 | 22.8811 | 21.5229 | 19.8454 | 18.328 | 16.877 | 15.5648 | 14.4566 | 11.075 | 8.0229 | 6.8801
|  | PETERSFIELD AVENUE PRIMARY | EE |  |  |  |  | 26.1803 | 24.564 | 22.6374 | 20.8395 | 18.8701 | 17.4221 | 16.1486 | 14.916 | 13.8762 | 10.9211 | 9.0017 | 8.5548 | 28.8499 | 27.9335 | 26.8448 | 25.9335 | 24.7917 | 23.458 | 22.1019 | 20.8601 | 19.6856 | 15.2876 | 10.9988 | 4.706 | 25.8811 | 24.5086 | 22.8811 | 21.5229 | 19.8454 | 18.328 | 16.877 | 15.5648 | 14.4566 | 11.378 | 9.5178 | 8.778
|  | PETERSFIELD AVENUE PRIMARY | HT |  |  |  |  | 26.4935 | 24.9884 | 23.2323 | 21.1048 | 19.1568 | 18.117 | 17.0211 | 15.9354 | 14.7946 | 10.7048 | 7.6986 | 6.7323 | 29.1631 | 28.4284 | 27.5744 | 26.4754 | 25.4591 | 24.557 | 23.4713 | 22.4346 | 21.3101 | 17.5866 | 15.0999 | 13.8795 | 26.2688 | 25.0454 | 23.6352 | 21.8791 | 20.2035 | 19.1607 | 17.9688 | 16.8148 | 15.5433 | 11.075 | 8.0229 | 6.8801
|  | PETERSFIELD AVENUE PRIMARY | HE |  |  |  |  | 26.5242 | 25.0507 | 23.3354 | 21.3466 | 19.4813 | 18.6864 | 17.8548 | 17.1803 | 16.4191 | 13.5895 | 11.7446 | 10.6966 | 29.0662 | 28.2713 | 27.3601 | 26.2856 | 25.2244 | 24.4448 | 23.4784 | 22.7172 | 21.8315 | 17.4009 | 13.0437 | 6.5458 | 26.2933 | 25.1005 | 23.7291 | 22.1025 | 20.4984 | 19.7331 | 18.824 | 18.1413 | 17.3168 | 14.1688 | 12.328 | 11.0158
|  | PETERSFIELD AVENUE PRIMARY | CF |  |  |  |  | 28.0323 | 27.6344 | 26.8772 | 25.6456 | 23.4609 | 21.0282 | 20.0813 | 19.8435 | 19.3466 | 16.6191 | 14.3731 | 12.4517 | 29.805 | 29.5029 | 28.9815 | 28.2458 | 26.9886 | 25.354 | 24.3101 | 23.6999 | 22.8784 | 18.2142 | 11.5529 | -0.16748 | 27.4893 | 27.1301 | 26.4719 | 25.4913 | 23.775 | 21.7586 | 20.776 | 20.5107 | 19.925 | 17.1413 | 15.074 | 13.4066
MANNINGTON GSP | SALISBURY BSP | PETERSFINGER PRIMARY | MINIMUM HEADROOM | SU 15608 29334 | NO | NO | 8.215 | 5.0565 | 4.6248 | 4.1208 | 3.9034 | 3.3463 | 2.5636 | 1.6677 | 0.6973 | 0.12077 | -2.6078 | -4.366 | -5.1629 | 9.3861 | 9.0391 | 8.6463 | 8.5014 | 8.083 | 7.5473 | 6.931 | 6.2534 | 5.8453 | 3.6463 | 0.87383 | -5.6517 | 6.332 | 5.8657 | 5.3248 | 5.2595 | 4.7289 | 4.0004 | 3.1595 | 2.2585 | 1.7422 | -0.59454 | -2.07 | -2.7037
|  | PETERSFINGER PRIMARY | EE |  |  |  |  | 5.0565 | 4.6248 | 4.1208 | 3.9034 | 3.3463 | 2.5636 | 1.6677 | 0.6973 | 0.12077 | -2.6078 | -4.1568 | -4.5996 | 9.3861 | 9.0391 | 8.6463 | 8.5014 | 8.083 | 7.5473 | 6.931 | 6.2534 | 5.8453 | 3.6463 | 1.5106 | -1.5364 | 6.332 | 5.8657 | 5.3248 | 5.2595 | 4.7289 | 4.0004 | 3.1595 | 2.2585 | 1.7422 | -0.59454 | -1.8731 | -2.2517
|  | PETERSFINGER PRIMARY | HT |  |  |  |  | 5.2514 | 4.9187 | 4.5106 | 4.031 | 3.4993 | 3.0748 | 2.3514 | 1.6585 | 0.98607 | -2.3966 | -4.366 | -5.1629 | 9.6483 | 9.432 | 9.1861 | 8.8871 | 8.5504 | 8.3973 | 7.9769 | 7.5606 | 7.1453 | 5.1922 | 4.1748 | 3.7585 | 6.6238 | 6.2902 | 5.9167 | 5.4565 | 4.9463 | 4.6748 | 4.0106 | 3.3565 | 2.7085 | -0.38025 | -2.07 | -2.7037
|  | PETERSFINGER PRIMARY | HE |  |  |  |  | 5.2953 | 4.9606 | 4.6065 | 4.1748 | 3.6891 | 3.031 | 2.6534 | 1.8861 | 1.2697 | -1.7864 | -3.3721 | -3.9578 | 9.6004 | 9.3422 | 9.084 | 8.7565 | 8.3891 | 7.93 | 7.73 | 7.1963 | 6.7177 | 4.1065 | 1.8738 | -1.1813 | 6.6544 | 6.3197 | 5.9922 | 5.5708 | 5.1014 | 4.4861 | 4.2626 | 3.5585 | 2.9646 | 0.17281 | -1.1782 | -1.7956
|  | PETERSFINGER PRIMARY | CF |  |  |  |  | 5.5902 | 5.4157 | 5.2055 | 5.0259 | 4.782 | 4.4993 | 4.133 | 4.0177 | 3.5963 | 1.0606 | -1.1527 | -3.1925 | 9.7361 | 9.5677 | 9.3626 | 9.1616 | 8.8922 | 8.5769 | 8.1851 | 8.0351 | 7.6055 | 4.7993 | 0.87383 | -5.6517 | 6.8789 | 6.6973 | 6.4687 | 6.2748 | 6.0085 | 5.7034 | 5.3116 | 5.3718 | 4.9708 | 2.6259 | 0.67689 | -1.0354
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PEWSEY PRIMARY | MINIMUM HEADROOM | SU 14710 59252 | NO | NO | 0.608 | 4.6959 | 4.4265 | 4.2 | 3.8908 | 3.55 | 3.1153 | 3.3551 | 2.9847 | 2.8592 | 1.6888 | 1.2571 | 0.83673 | 7.8712 | 7.6682 | 7.5018 | 7.2631 | 7.01 | 6.6927 | 6.7947 | 6.511 | 6.3386 | 5.4018 | 4.0865 | 1.1498 | 5.282 | 5.0086 | 4.779 | 4.4637 | 4.1249 | 3.6994 | 3.9473 | 3.5851 | 3.4667 | 2.5882 | 2.2229 | 1.8841
|  | PEWSEY PRIMARY | EE |  |  |  |  | 4.6959 | 4.4265 | 4.2 | 3.8908 | 3.55 | 3.1153 | 3.3551 | 2.9847 | 2.8592 | 1.6888 | 1.2643 | 1.0316 | 7.8712 | 7.6682 | 7.5018 | 7.2631 | 7.01 | 6.6927 | 6.7947 | 6.511 | 6.3386 | 5.4018 | 4.5335 | 3.0988 | 5.282 | 5.0086 | 4.779 | 4.4637 | 4.1249 | 3.6994 | 3.9473 | 3.5851 | 3.4667 | 2.5882 | 2.228 | 2.0473
|  | PEWSEY PRIMARY | HT |  |  |  |  | 4.8929 | 4.7286 | 4.5847 | 4.3796 | 4.2071 | 3.9255 | 3.5929 | 3.2439 | 3.3061 | 1.9235 | 1.2571 | 0.83673 | 8.0427 | 7.9182 | 7.8141 | 7.6651 | 7.5447 | 7.3406 | 7.1029 | 6.8518 | 6.9845 | 6.1314 | 5.762 | 5.5529 | 5.4943 | 5.3188 | 5.1749 | 4.9718 | 4.7973 | 4.5167 | 4.1871 | 3.8433 | 4.0331 | 2.78 | 2.2229 | 1.8841
|  | PEWSEY PRIMARY | HE |  |  |  |  | 4.8908 | 4.7276 | 4.5857 | 4.3847 | 4.2173 | 3.9469 | 3.6163 | 3.2643 | 3.3929 | 1.9367 | 1.5061 | 1.3122 | 8.0335 | 7.8998 | 7.7886 | 7.6324 | 7.4937 | 7.2773 | 7.0171 | 6.7518 | 6.8029 | 5.6049 | 4.71 | 3.3069 | 5.4912 | 5.3188 | 5.178 | 4.9769 | 4.8106 | 4.5402 | 4.2116 | 3.8637 | 4.1045 | 2.8035 | 2.4331 | 2.2861
|  | PEWSEY PRIMARY | CF |  |  |  |  | 4.9745 | 4.8571 | 4.7204 | 4.6061 | 4.4602 | 4.2888 | 4.1408 | 3.9163 | 3.6796 | 2.9347 | 2.1633 | 1.5092 | 8.0722 | 7.96 | 7.8386 | 7.7324 | 7.5824 | 7.412 | 7.2498 | 7.0345 | 6.8039 | 5.7804 | 4.0865 | 1.1498 | 5.5729 | 5.4463 | 5.3096 | 5.2086 | 5.0514 | 4.8749 | 4.7249 | 4.4963 | 4.2596 | 3.6361 | 2.9698 | 2.4514
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE PRIMARY | MINIMUM HEADROOM | SY 70169 99809 | NO | NO | 0.592 | 5.2476 | 5.1812 | 5.0955 | 4.9945 | 4.9343 | 4.8037 | 4.6547 | 4.5669 | 4.4976 | 4.1557 | 4.0414 | 3.9353 | 5.0371 | 4.9841 | 4.9229 | 4.8463 | 4.7973 | 4.7014 | 4.5892 | 4.5188 | 4.4667 | 4.229 | 3.9371 | 3.1963 | 3.9508 | 3.8886 | 3.8069 | 3.7151 | 3.6559 | 3.5376 | 3.3967 | 3.3141 | 3.2478 | 2.9457 | 2.8488 | 2.7539
|  | PIDDLETRENTHIDE PRIMARY | EE |  |  |  |  | 5.2476 | 5.1812 | 5.0955 | 4.9945 | 4.9343 | 4.8037 | 4.6547 | 4.5669 | 4.4976 | 4.1557 | 4.0414 | 3.9924 | 5.0371 | 4.9841 | 4.9229 | 4.8463 | 4.7973 | 4.7014 | 4.5892 | 4.5188 | 4.4667 | 4.229 | 4.03 | 3.7065 | 3.9508 | 3.8886 | 3.8069 | 3.7151 | 3.6559 | 3.5376 | 3.3967 | 3.3141 | 3.2478 | 2.9457 | 2.8488 | 2.8039
|  | PIDDLETRENTHIDE PRIMARY | HT |  |  |  |  | 5.3027 | 5.2516 | 5.1802 | 5.1312 | 5.0608 | 4.9588 | 4.8435 | 4.7761 | 4.6588 | 4.2292 | 4.0547 | 3.9353 | 5.0933 | 5.0545 | 5.0065 | 4.979 | 4.932 | 4.8637 | 4.7871 | 4.7433 | 4.6647 | 4.3902 | 4.2973 | 4.2392 | 4.01 | 3.9559 | 3.8896 | 3.8437 | 3.7794 | 3.6865 | 3.5794 | 3.5141 | 3.4049 | 3.009 | 2.8539 | 2.7539
|  | PIDDLETRENTHIDE PRIMARY | HE |  |  |  |  | 5.3016 | 5.2506 | 5.1802 | 5.1353 | 5.0669 | 4.9669 | 4.8547 | 4.7873 | 4.6731 | 4.1945 | 4.0833 | 4.0384 | 5.0882 | 5.0433 | 4.9933 | 4.9616 | 4.9106 | 4.8392 | 4.7586 | 4.7086 | 4.6208 | 4.2627 | 4.0596 | 3.731 | 4.009 | 3.9569 | 3.8906 | 3.8467 | 3.7845 | 3.6957 | 3.5916 | 3.5263 | 3.4212 | 2.9906 | 2.8937 | 2.8539
|  | PIDDLETRENTHIDE PRIMARY | CF |  |  |  |  | 5.319 | 5.268 | 5.2282 | 5.1669 | 5.1322 | 5.0639 | 4.9976 | 4.9139 | 4.8761 | 4.4455 | 4.2496 | 4.068 | 5.0994 | 5.0586 | 5.0269 | 4.979 | 4.9504 | 4.8922 | 4.8371 | 4.7698 | 4.73 | 4.3127 | 3.9371 | 3.1963 | 4.0335 | 3.9763 | 3.9365 | 3.8824 | 3.8498 | 3.7896 | 3.7294 | 3.6539 | 3.6171 | 3.2253 | 3.0447 | 2.8845
FLEET-BRAMLEY GSP | FERNHURST BSP | PLAISTOW PRIMARY | MINIMUM HEADROOM | TQ 02071 29626 | NO | NO | 15.447 | -3.1786 | -3.3163 | -3.5051 | -3.7 | -3.8612 | -4.1163 | -4.4143 | -4.7276 | -4.8929 | -6.201 | -6.5449 | -6.5082 | -1.7837 | -1.8857 | -2.0245 | -2.1776 | -2.2929 | -2.4837 | -2.7092 | -2.9347 | -3.05 | -3.7571 | -4.2031 | -5.2969 | -2.949 | -3.0837 | -3.2673 | -3.4643 | -3.6102 | -3.8571 | -4.1469 | -4.449 | -4.6 | -5.6949 | -5.9888 | -5.8755
|  | PLAISTOW PRIMARY | EE |  |  |  |  | -3.1786 | -3.3163 | -3.5051 | -3.7 | -3.8612 | -4.1163 | -4.4143 | -4.7276 | -4.8929 | -6.201 | -6.5449 | -6.3663 | -1.7837 | -1.8857 | -2.0245 | -2.1776 | -2.2929 | -2.4837 | -2.7092 | -2.9347 | -3.05 | -3.7571 | -4.2031 | -4.5255 | -2.949 | -3.0837 | -3.2673 | -3.4643 | -3.6102 | -3.8571 | -4.1469 | -4.449 | -4.6 | -5.6949 | -5.9888 | -5.7571
|  | PLAISTOW PRIMARY | HT |  |  |  |  | -3.0857 | -3.199 | -3.3459 | -3.4643 | -3.6255 | -3.8316 | -4.0173 | -4.2571 | -4.5071 | -6.05 | -6.5408 | -6.5082 | -1.6837 | -1.7551 | -1.8439 | -1.9163 | -2.0245 | -2.1551 | -2.2653 | -2.4235 | -2.5908 | -3.4592 | -3.7082 | -3.5245 | -2.851 | -2.9571 | -3.0939 | -3.2 | -3.3551 | -3.551 | -3.7133 | -3.9408 | -4.1765 | -5.5622 | -5.9878 | -5.8755
|  | PLAISTOW PRIMARY | HE |  |  |  |  | -3.0867 | -3.198 | -3.3388 | -3.449 | -3.602 | -3.7969 | -3.9765 | -4.2071 | -4.4439 | -6.0776 | -6.0582 | -6.1918 | -1.701 | -1.7786 | -1.8714 | -1.9469 | -2.0571 | -2.1939 | -2.3153 | -2.4786 | -2.6551 | -3.6673 | -3.799 | -4.402 | -2.852 | -2.9561 | -3.0878 | -3.1888 | -3.3357 | -3.5235 | -3.6786 | -3.898 | -4.1255 | -5.5816 | -5.4837 | -5.5857
|  | PLAISTOW PRIMARY | CF |  |  |  |  | -3.0408 | -3.1347 | -3.2429 | -3.3633 | -3.452 | -3.5786 | -3.7276 | -3.8816 | -3.998 | -5.2969 | -5.5622 | -6.0939 | -1.6755 | -1.7408 | -1.8204 | -1.9092 | -1.9745 | -2.0776 | -2.201 | -2.3316 | -2.4296 | -3.4337 | -3.9898 | -5.2969 | -2.8112 | -2.8969 | -3.001 | -3.1194 | -3.1969 | -3.3214 | -3.4694 | -3.6235 | -3.7265 | -4.9224 | -5.0612 | -5.5184
MINETY GSP | STRATTON (MAIN) BSP | PLESSEY PRIMARY | MINIMUM HEADROOM | SU 16381 86720 | NO | NO | 2.58 | 6.0468 | 5.7448 | 5.3836 | 4.9234 | 4.0621 | 3.1866 | 2.2121 | 1.1611 | 0.31622 | -2.3001 | -3.6562 | -4.0654 | 8.5019 | 8.2315 | 7.905 | 7.5264 | 7.0458 | 6.2989 | 5.403 | 4.5183 | 3.8672 | 1.2683 | -2.346 | -10.5797 | 5.0968 | 4.8458 | 4.505 | 4.0785 | 3.3264 | 2.4642 | 1.7234 | 0.71724 | -0.048061 | -2.5358 | -3.9419 | -4.2756
|  | PLESSEY PRIMARY | EE |  |  |  |  | 6.0468 | 5.7448 | 5.3836 | 4.9764 | 4.1999 | 3.306 | 2.2121 | 1.1611 | 0.31622 | -2.3001 | -3.5256 | -3.4491 | 8.5019 | 8.2315 | 7.905 | 7.5264 | 7.0458 | 6.2989 | 5.403 | 4.5183 | 3.8672 | 1.2683 | -1.394 | -5.1287 | 5.0968 | 4.8458 | 4.505 | 4.1203 | 3.6377 | 2.7591 | 1.7234 | 0.71724 | -0.048061 | -2.5358 | -3.8583 | -3.8062
|  | PLESSEY PRIMARY | HT |  |  |  |  | 6.2703 | 6.0397 | 5.7662 | 4.9234 | 4.0621 | 3.1866 | 2.3764 | 1.5091 | 0.83255 | -2.0185 | -3.6562 | -4.0654 | 8.7581 | 8.604 | 8.4081 | 7.7785 | 7.1213 | 6.4581 | 5.9917 | 5.4091 | 4.954 | 3.0509 | 2.1142 | 1.7438 | 5.2479 | 5.055 | 4.8315 | 4.0785 | 3.3264 | 2.4642 | 1.804 | 1.0315 | 0.43459 | -2.3236 | -3.9419 | -4.2756
|  | PLESSEY PRIMARY | HE |  |  |  |  | 6.2693 | 6.0397 | 5.7611 | 5.4489 | 4.6132 | 3.806 | 2.7999 | 1.9295 | 1.0193 | -2.0817 | -3.2246 | -3.6879 | 8.703 | 8.5091 | 8.2744 | 8.0377 | 7.356 | 6.6958 | 5.8928 | 5.3836 | 4.6979 | 1.9223 | -0.67663 | -4.5307 | 5.2683 | 5.0907 | 4.8815 | 4.6764 | 3.9621 | 3.1989 | 2.2836 | 1.4917 | 0.61827 | -2.346 | -3.4134 | -3.8389
|  | PLESSEY PRIMARY | CF |  |  |  |  | 6.5326 | 6.404 | 6.2693 | 6.1009 | 5.9162 | 5.4723 | 4.8887 | 4.1979 | 3.5417 | 0.555 | -1.6766 | -3.4685 | 8.8203 | 8.653 | 8.4999 | 8.2877 | 8.0642 | 7.5805 | 6.9836 | 6.304 | 5.6479 | 2.3642 | -2.346 | -10.5797 | 5.4856 | 5.3866 | 5.3009 | 5.1866 | 5.0917 | 4.704 | 4.205 | 3.6305 | 3.0101 | 0.13255 | -1.9736 | -3.643
LOVEDEAN GSP | FAREHAM (MAIN) BSP | PLESSEY TITCHFIELD PRIMARY | MINIMUM HEADROOM | SU 53390 06922 | NO | YES | 5.524 | 16.9551 | 16.6398 | 16.2704 | 15.8571 | 15.5888 | 14.9183 | 14.1663 | 13.4388 | 12.8275 | 10.1163 | 8.1367 | 7.0673 | 18.2174 | 17.9919 | 17.7215 | 17.4235 | 17.3684 | 16.9082 | 16.4113 | 15.9092 | 15.5123 | 13.245 | 9.7919 | 2.4358 | 17.5011 | 17.2368 | 16.9205 | 16.5664 | 16.3256 | 15.7837 | 15.1613 | 14.5654 | 14.0735 | 11.8654 | 10.4154 | 9.4643
|  | PLESSEY TITCHFIELD PRIMARY | EE |  |  |  |  | 16.9551 | 16.6398 | 16.2704 | 15.8571 | 15.5888 | 14.9183 | 14.1663 | 13.4388 | 12.8275 | 10.2673 | 8.6255 | 7.4877 | 18.2174 | 17.9919 | 17.7215 | 17.4235 | 17.3684 | 16.9082 | 16.4113 | 15.9092 | 15.5123 | 13.245 | 10.699 | 6.8868 | 17.5011 | 17.2368 | 16.9205 | 16.5664 | 16.3256 | 15.7837 | 15.1613 | 14.5654 | 14.0735 | 12.2062 | 10.8613 | 9.8643
|  | PLESSEY TITCHFIELD PRIMARY | HT |  |  |  |  | 17.1857 | 16.9377 | 16.6479 | 16.3449 | 15.8836 | 15.2785 | 14.7602 | 14.0979 | 13.4357 | 10.1163 | 8.1367 | 7.0673 | 18.4174 | 18.2827 | 18.1123 | 17.9592 | 17.6664 | 17.3052 | 17.1541 | 16.8041 | 16.4613 | 14.8041 | 13.8062 | 13.2582 | 17.7235 | 17.5266 | 17.2878 | 17.0378 | 16.6358 | 16.1725 | 15.7705 | 15.2511 | 14.7317 | 12.1899 | 10.4154 | 9.4643
|  | PLESSEY TITCHFIELD PRIMARY | HE |  |  |  |  | 17.1775 | 16.9285 | 16.6367 | 16.3245 | 15.953 | 15.3602 | 14.8388 | 14.1694 | 13.4836 | 10.2132 | 8.399 | 7.501 | 18.3541 | 18.1766 | 17.9674 | 17.7654 | 17.5103 | 17.099 | 16.8919 | 16.4705 | 16.0348 | 13.5225 | 10.8725 | 7.2113 | 17.7052 | 17.499 | 17.2501 | 16.9858 | 16.6643 | 16.1745 | 15.7368 | 15.1756 | 14.595 | 11.8654 | 10.4735 | 9.6909
|  | PLESSEY TITCHFIELD PRIMARY | CF |  |  |  |  | 17.4551 | 17.3326 | 17.1775 | 17.0143 | 16.8214 | 16.5969 | 16.2551 | 16.0306 | 15.6724 | 13.2663 | 10.8449 | 8.899 | 18.447 | 18.3123 | 18.1429 | 17.9796 | 17.7603 | 17.497 | 17.1399 | 16.9909 | 16.6337 | 14.0511 | 9.7919 | 2.4358 | 17.9296 | 17.8225 | 17.6888 | 17.548 | 17.3776 | 17.1807 | 16.8745 | 16.6613 | 16.3327 | 14.2725 | 12.3552 | 10.9133
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | POOLE PRIMARY | MINIMUM HEADROOM | SZ 01091 90595 | NO | NO | 2.949 | 10.015 | 9.6263 | 9.2426 | 8.8844 | 8.0732 | 7.4956 | 6.9191 | 6.1936 | 6.013 | 4.8987 | 3.2793 | 2.2895 | 11.5242 | 11.3314 | 11.1303 | 10.7487 | 10.2018 | 9.7191 | 9.1507 | 8.563 | 8.2793 | 6.412 | 1.6048 | -8.0421 | 10.8201 | 10.4599 | 10.1079 | 9.6609 | 8.8946 | 8.4538 | 7.8936 | 7.1977 | 7.0181 | 6.1232 | 4.7058 | 3.762
|  | POOLE PRIMARY | EE |  |  |  |  | 10.0303 | 9.7038 | 9.3773 | 9.065 | 8.4222 | 7.7671 | 6.966 | 6.1936 | 6.013 | 4.8987 | 3.662 | 2.3742 | 11.5242 | 11.3334 | 11.1405 | 10.7487 | 10.2018 | 9.7191 | 9.1507 | 8.563 | 8.2793 | 6.412 | 3.3916 | -1.8033 | 10.8212 | 10.515 | 10.2058 | 9.866 | 9.1426 | 8.6181 | 7.8936 | 7.1977 | 7.0181 | 6.1232 | 4.9834 | 3.7926
|  | POOLE PRIMARY | HT |  |  |  |  | 10.015 | 9.6263 | 9.2426 | 8.8844 | 8.0732 | 7.4956 | 6.9191 | 6.6579 | 6.5303 | 5.0456 | 3.2793 | 2.2895 | 11.5436 | 11.3314 | 11.1303 | 10.9436 | 10.515 | 10.1967 | 9.8579 | 9.664 | 9.5375 | 8.6854 | 7.8426 | 7.3579 | 10.8201 | 10.4599 | 10.1079 | 9.6609 | 8.8946 | 8.4538 | 8.014 | 7.7732 | 7.614 | 6.266 | 4.7058 | 3.762
|  | POOLE PRIMARY | HE |  |  |  |  | 10.0732 | 9.765 | 9.4671 | 9.1722 | 8.7375 | 8.2079 | 7.4691 | 6.863 | 6.7589 | 6.1007 | 4.9324 | 4.3671 | 11.563 | 11.3865 | 11.2201 | 10.9722 | 10.4834 | 10.0946 | 9.5814 | 9.1048 | 8.8497 | 7.0456 | 4.2171 | -0.6013 | 10.8722 | 10.5875 | 10.313 | 10.0405 | 9.3997 | 8.9905 | 8.4273 | 7.9712 | 7.8589 | 7.1242 | 6.0773 | 5.5987
|  | POOLE PRIMARY | CF |  |  |  |  | 10.1752 | 10.0079 | 9.8579 | 9.762 | 9.6548 | 9.5814 | 9.4232 | 9.1997 | 8.9558 | 7.3283 | 6.4997 | 5.5507 | 11.6089 | 11.5038 | 11.4069 | 11.3354 | 11.162 | 10.8834 | 10.5058 | 10.0569 | 9.5518 | 6.5283 | 1.6048 | -8.0421 | 10.965 | 10.8079 | 10.666 | 10.5783 | 10.4773 | 10.4018 | 10.2497 | 10.0426 | 9.8089 | 8.2997 | 7.5232 | 6.716
LOVEDEAN GSP | PORTSMOUTH BSP | PORTCHESTER PRIMARY | MINIMUM HEADROOM | SU 62043 05575 | NO | YES | 3.637 | 11.6278 | 11.1533 | 10.3738 | 9.5503 | 8.6421 | 7.4095 | 6.0095 | 4.488 | 3.5044 | -1.0191 | -4.6171 | -6.5344 | 12.6635 | 12.4156 | 11.8431 | 11.2156 | 10.536 | 9.6727 | 8.6717 | 7.5952 | 6.938 | 3.1605 | -4.0293 | -18.9426 | 11.1768 | 10.8023 | 10.0921 | 9.3289 | 8.4921 | 7.3615 | 6.0727 | 4.686 | 3.8105 | -0.019106 | -3.0701 | -4.714
|  | PORTCHESTER PRIMARY | EE |  |  |  |  | 11.6278 | 11.1533 | 10.3738 | 9.5503 | 8.6421 | 7.4095 | 6.0095 | 4.488 | 3.5044 | -0.56196 | -3.9109 | -6.1426 | 12.6635 | 12.4156 | 11.8431 | 11.2156 | 10.536 | 9.6727 | 8.6717 | 7.5952 | 6.938 | 3.1605 | -1.6497 | -9.3385 | 11.1768 | 10.8023 | 10.0921 | 9.3289 | 8.4921 | 7.3615 | 6.0727 | 4.686 | 3.8105 | 0.27885 | -2.4538 | -4.3854
|  | PORTCHESTER PRIMARY | HT |  |  |  |  | 12.0186 | 11.3115 | 10.5176 | 10.0217 | 9.1819 | 8.0064 | 6.7717 | 5.5084 | 4.4738 | -1.0191 | -4.6171 | -6.5344 | 13.1778 | 12.7697 | 12.2962 | 12.1942 | 11.735 | 11.136 | 10.4697 | 9.7727 | 9.1533 | 6.2901 | 4.7554 | 3.9064 | 11.6003 | 10.9697 | 10.2554 | 9.8962 | 9.1452 | 8.1166 | 7.0115 | 5.8727 | 4.8891 | -0.019106 | -3.0701 | -4.714
|  | PORTCHESTER PRIMARY | HE |  |  |  |  | 12.0666 | 11.3901 | 10.6799 | 10.3248 | 9.5972 | 8.6778 | 7.635 | 6.4472 | 5.3809 | 0.78089 | -2.5885 | -4.1303 | 13.0646 | 12.5962 | 12.0758 | 11.8921 | 11.3554 | 10.7013 | 9.9493 | 9.0911 | 8.2656 | 3.7809 | -1.1456 | -8.5558 | 11.637 | 11.036 | 10.3952 | 10.1309 | 9.4686 | 8.6421 | 7.688 | 6.6135 | 5.6278 | 1.437 | -1.2936 | -2.612
|  | PORTCHESTER PRIMARY | CF |  |  |  |  | 12.4278 | 11.936 | 11.4972 | 11.1166 | 11.1197 | 10.8227 | 10.4013 | 9.9146 | 9.2799 | 5.2727 | 1.9248 | -1.2436 | 13.2156 | 12.8146 | 12.4064 | 11.9942 | 11.8809 | 11.4074 | 10.8186 | 10.1809 | 9.4309 | 4.1891 | -4.0293 | -18.9426 | 11.9676 | 11.536 | 11.1238 | 10.7391 | 10.7952 | 10.5074 | 10.1146 | 9.6615 | 9.0748 | 5.4248 | 2.4115 | -0.25482
CHICKERELL GSP | CHICKERELL BSP | PORTLAND PRIMARY | MINIMUM HEADROOM | SY 68307 73941 | NO | NO | 3.879 | 10.4627 | 9.978 | 9.4892 | 8.9556 | 8.6811 | 7.9199 | 7.0586 | 6.2015 | 5.5423 | 1.1484 | -2.3699 | -4.3679 | 13.5892 | 13.2352 | 12.9219 | 12.4995 | 12.2964 | 11.7515 | 11.1219 | 10.4811 | 9.9903 | 6.8086 | 3.5454 | -4.8975 | 11.0944 | 10.6127 | 10.125 | 9.5831 | 9.3464 | 8.6362 | 7.827 | 7.0188 | 6.4056 | 2.5474 | -0.40973 | -2.1291
|  | PORTLAND PRIMARY | EE |  |  |  |  | 10.4627 | 9.978 | 9.4892 | 8.9556 | 8.6811 | 7.9199 | 7.0586 | 6.2015 | 5.5423 | 1.1484 | -1.9118 | -4.1465 | 13.5892 | 13.2352 | 12.9219 | 12.4995 | 12.2964 | 11.7515 | 11.1219 | 10.4811 | 9.9903 | 6.8086 | 3.7117 | -0.89749 | 11.0944 | 10.6127 | 10.125 | 9.5831 | 9.3464 | 8.6362 | 7.827 | 7.0188 | 6.4056 | 2.5474 | 0.01578 | -1.9342
|  | PORTLAND PRIMARY | HT |  |  |  |  | 10.6933 | 10.2841 | 9.8944 | 9.5168 | 9.0158 | 8.3311 | 7.8831 | 7.1658 | 6.426 | 1.1995 | -2.3699 | -4.3679 | 13.8035 | 13.5382 | 13.3321 | 13.1301 | 12.8637 | 12.525 | 12.329 | 11.9005 | 11.4484 | 8.7015 | 7.0597 | 6.2525 | 11.2188 | 10.9556 | 10.5984 | 10.2341 | 9.7535 | 9.1076 | 8.7188 | 8.0352 | 7.3239 | 2.6454 | -0.40973 | -2.1291
|  | PORTLAND PRIMARY | HE |  |  |  |  | 10.6944 | 10.2944 | 9.9219 | 9.5637 | 9.0903 | 8.4933 | 7.827 | 7.5117 | 6.875 | 2.4882 | -0.38218 | -1.6516 | 13.7352 | 13.4311 | 13.1872 | 12.9403 | 12.6199 | 12.2403 | 11.7739 | 11.5597 | 11.0556 | 7.7178 | 4.5648 | 0.38925 | 11.2188 | 10.9658 | 10.627 | 10.2933 | 9.8454 | 9.2811 | 8.6464 | 8.3841 | 7.7729 | 3.8954 | 1.4331 | 0.37904
|  | PORTLAND PRIMARY | CF |  |  |  |  | 10.9556 | 10.6831 | 10.4535 | 10.2076 | 9.9392 | 9.7229 | 9.4474 | 9.1597 | 9.1699 | 6.278 | 3.5729 | 1.0668 | 13.8423 | 13.5882 | 13.3984 | 13.176 | 12.9209 | 12.6484 | 12.327 | 11.9535 | 11.7852 | 8.5005 | 3.5454 | -4.8975 | 11.3352 | 11.1535 | 11.0525 | 10.8862 | 10.6352 | 10.4107 | 10.126 | 9.8199 | 9.8382 | 7.2086 | 4.776 | 2.6311
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH PRIMARY | MINIMUM HEADROOM | SZ 63405 99685 | NO | YES | 3.73 | 23.2394 | 22.9323 | 22.5956 | 22.1996 | 21.7578 | 21.1894 | 20.4935 | 19.8109 | 19.2435 | 17.365 | 16.1945 | 16.2609 | 26.9129 | 26.6017 | 26.269 | 25.865 | 25.4129 | 24.9078 | 24.2905 | 23.6598 | 23.118 | 20.3017 | 14.7088 | 2.7588 | 23.7098 | 23.4109 | 23.0874 | 22.7047 | 22.2752 | 21.7384 | 21.0782 | 20.4282 | 19.8905 | 18.1496 | 17.167 | 17.2374
|  | PORTSMOUTH PRIMARY | EE |  |  |  |  | 23.2394 | 22.9323 | 22.5956 | 22.1996 | 21.7578 | 21.1894 | 20.4935 | 19.8109 | 19.2435 | 17.365 | 16.7047 | 16.8537 | 26.9129 | 26.6017 | 26.269 | 25.865 | 25.4129 | 24.9078 | 24.2905 | 23.6598 | 23.118 | 20.3017 | 17.0262 | 11.466 | 23.7098 | 23.4109 | 23.0874 | 22.7047 | 22.2752 | 21.7384 | 21.0782 | 20.4282 | 19.8905 | 18.1496 | 17.5833 | 17.7037
|  | PORTSMOUTH PRIMARY | HT |  |  |  |  | 23.4874 | 23.2854 | 23.0558 | 22.7823 | 22.4894 | 22.0466 | 21.5456 | 21.0078 | 20.465 | 17.7098 | 16.1945 | 16.2609 | 27.219 | 27.068 | 26.8935 | 26.6792 | 26.4537 | 26.168 | 25.8303 | 25.4598 | 25.0976 | 23.2486 | 22.2058 | 22.1037 | 23.9568 | 23.769 | 23.5558 | 23.2956 | 23.017 | 22.6078 | 22.1384 | 21.6343 | 21.1303 | 18.568 | 17.167 | 17.2374
|  | PORTSMOUTH PRIMARY | HE |  |  |  |  | 23.4864 | 23.3109 | 23.1088 | 22.8731 | 22.6241 | 22.2537 | 21.8252 | 21.3782 | 20.9445 | 19.1823 | 18.5598 | 18.4894 | 27.115 | 26.9129 | 26.6894 | 26.4201 | 26.1333 | 25.7762 | 25.369 | 24.9211 | 24.4721 | 21.5843 | 18.2527 | 12.5772 | 23.9537 | 23.7854 | 23.5935 | 23.3711 | 23.1313 | 22.7864 | 22.3843 | 21.966 | 21.5578 | 19.9088 | 19.2752 | 18.8445
|  | PORTSMOUTH PRIMARY | CF |  |  |  |  | 23.6323 | 23.5486 | 23.4201 | 23.2854 | 23.1221 | 22.9598 | 22.7619 | 22.5303 | 22.2915 | 20.8833 | 19.3741 | 18.0711 | 27.1945 | 27.0139 | 26.8058 | 26.5701 | 26.266 | 25.9231 | 25.5364 | 25.0996 | 24.6231 | 21.1384 | 14.7088 | 2.7588 | 24.118 | 24.0109 | 23.8843 | 23.7517 | 23.5945 | 23.4394 | 23.2547 | 23.0282 | 22.8017 | 21.469 | 20.0813 | 18.918
MELKSHAM GSP | ANDOVER BSP | PORTWAY PRIMARY | MINIMUM HEADROOM | SU 34402 46001 | NO | NO | 2.754 | 13.1957 | 12.3804 | 11.4273 | 10.3426 | 9.1518 | 7.9508 | 6.3804 | 4.8865 | 3.6457 | -3.5421 | -6.7543 | -7.3809 | 14.8875 | 14.3242 | 13.6814 | 12.9436 | 12.0855 | 11.2008 | 10.0232 | 8.9089 | 7.9906 | 2.663 | 0.3518 | -0.13698 | 12.9273 | 12.1416 | 11.2232 | 10.1783 | 9.0304 | 7.8834 | 6.3702 | 4.9385 | 3.7477 | -3.1768 | -6.2462 | -6.8309
|  | PORTWAY PRIMARY | EE |  |  |  |  | 13.1957 | 12.3804 | 11.4273 | 10.3426 | 9.1518 | 7.9508 | 6.3804 | 4.8865 | 3.6457 | -0.30942 | -1.188 | -1.5911 | 14.8875 | 14.3242 | 13.6814 | 12.9436 | 12.0855 | 11.2008 | 10.0232 | 8.9089 | 7.9906 | 5.1742 | 4.6559 | 4.4038 | 12.9273 | 12.1416 | 11.2232 | 10.1783 | 9.0304 | 7.8834 | 6.3702 | 4.9385 | 3.7477 | -0.020649 | -0.81963 | -1.1778
|  | PORTWAY PRIMARY | HT |  |  |  |  | 14.16 | 13.661 | 13.0865 | 12.4079 | 11.6253 | 10.7294 | 9.6304 | 8.464 | 7.3906 | 2.1508 | -0.17269 | -0.81963 | 15.5447 | 15.2059 | 14.8181 | 14.3579 | 13.8304 | 13.2253 | 12.4804 | 11.6855 | 10.9794 | 7.2294 | 5.6385 | 5.2559 | 13.8579 | 13.3783 | 12.8273 | 12.1753 | 11.4222 | 10.562 | 9.5069 | 8.3845 | 7.3569 | 2.3355 | 0.13956 | -0.45126
|  | PORTWAY PRIMARY | HE |  |  |  |  | 13.7651 | 13.0702 | 12.2579 | 11.2967 | 10.1753 | 8.9273 | 7.3722 | 5.713 | 4.11 | -3.5421 | -6.7543 | -7.3809 | 15.2855 | 14.814 | 14.2722 | 13.6242 | 12.8773 | 11.9528 | 10.7885 | 9.5406 | 8.3426 | 2.663 | 0.3518 | -0.13698 | 13.4783 | 12.8079 | 12.0263 | 11.0987 | 10.0222 | 8.8212 | 7.3242 | 5.7253 | 4.1845 | -3.1768 | -6.2462 | -6.8309
|  | PORTWAY PRIMARY | CF |  |  |  |  | 14.4661 | 14.0926 | 13.6528 | 13.1324 | 12.5324 | 11.9273 | 11.1294 | 10.2232 | 9.2651 | 3.8089 | -0.83289 | -3.2553 | 15.7487 | 15.4998 | 15.2038 | 14.8457 | 14.4385 | 14.0263 | 13.4896 | 12.8722 | 12.1457 | 8.0447 | 4.5804 | 2.7345 | 14.1528 | 13.7916 | 13.3702 | 12.8671 | 12.2936 | 11.7089 | 10.9385 | 10.0661 | 9.1365 | 3.8773 | -0.57881 | -2.8798
IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY | MINIMUM HEADROOM | TQ 03425 75555 | NO | YES | 7.932 | 4.4245 | 3.7724 | 2.8949 | 1.8388 | 0.68367 | -0.48061 | -2.0398 | -3.5255 | -4.9357 | -10.3786 | -13.0449 | -14.101 | 6.8592 | 6.3602 | 5.7622 | 4.9571 | 4.0704 | 3.2041 | 2.0337 | 0.91327 | -0.12449 | -4.1847 | -6.1429 | -7.8204 | 4.2255 | 3.5969 | 2.8 | 1.7878 | 0.67449 | -0.43776 | -1.9306 | -3.3582 | -4.6959 | -9.9194 | -12.4633 | -13.3837
|  | POYLE PRIMARY | EE |  |  |  |  | 4.4245 | 3.7724 | 2.8949 | 1.8388 | 0.68367 | -0.48061 | -2.0398 | -3.5255 | -4.9357 | -9.4969 | -10.6541 | -11.1418 | 6.8592 | 6.3602 | 5.7622 | 4.9571 | 4.0704 | 3.2041 | 2.0337 | 0.91327 | -0.12449 | -3.4531 | -4.1918 | -4.4724 | 4.2255 | 3.5969 | 2.8 | 1.7878 | 0.67449 | -0.43776 | -1.9306 | -3.3582 | -4.6959 | -9.0378 | -10.0694 | -10.4286
|  | POYLE PRIMARY | HT |  |  |  |  | 5.049 | 4.6194 | 4.1286 | 3.4633 | 2.6827 | 1.7459 | 0.58367 | -0.6551 | -1.9092 | -7.6878 | -10.3469 | -11.4153 | 7.3541 | 7.0378 | 6.6735 | 6.2153 | 5.6673 | 4.9908 | 4.1398 | 3.2235 | 2.3235 | -1.8633 | -3.5694 | -4.1561 | 4.8286 | 4.4163 | 3.9429 | 3.3541 | 2.602 | 1.7061 | 0.59286 | -0.5949 | -1.7816 | -7.2776 | -9.7092 | -10.699
|  | POYLE PRIMARY | HE |  |  |  |  | 4.9061 | 4.4071 | 3.8255 | 3.0041 | 2.0755 | 0.97449 | -0.4102 | -1.8918 | -3.4276 | -10.3786 | -13.0449 | -14.101 | 7.2337 | 6.8561 | 6.4112 | 5.8622 | 5.1571 | 4.3337 | 3.2949 | 2.1755 | 1.0367 | -4.1847 | -6.1429 | -6.9694 | 4.6918 | 4.2112 | 3.6531 | 2.9122 | 2.0194 | 0.96224 | -0.36429 | -1.7898 | -3.248 | -9.9194 | -12.4633 | -13.3837
|  | POYLE PRIMARY | CF |  |  |  |  | 5.4347 | 5.1684 | 4.8633 | 4.4857 | 4.049 | 3.5735 | 2.8612 | 2.0429 | 1.0367 | -4.1908 | -8.9327 | -12.0173 | 7.5622 | 7.4143 | 7.1837 | 6.8867 | 6.5459 | 6.1827 | 5.701 | 5.0663 | 4.3031 | 0.3051 | -3.3184 | -7.8204 | 5.1959 | 4.9418 | 4.648 | 4.2847 | 3.8653 | 3.4112 | 2.7684 | 1.9776 | 1.0194 | -4.0082 | -8.5531 | -11.4898
MINETY GSP | STRATTON (MAIN) BSP | PRESSED STEEL SWINDON PRIMARY | MINIMUM HEADROOM | SU 16963 86368 | NO | NO | 7.537 | 32.8615 | 65.5458 | 65.1345 | 64.6723 | 64.2253 | 63.257 | 61.9937 | 60.7356 | 59.7804 | 56.5141 | 55.0498 | 54.7886 | 31.0392 | 60.8662 | 60.4988 | 60.0825 | 59.7876 | 59.0672 | 58.1233 | 57.1519 | 56.3794 | 53.6427 | 49.9315 | 42.3488 | 30.3256 | 61.9539 | 61.5386 | 61.0733 | 60.6968 | 59.7845 | 58.6039 | 57.4172 | 56.5478 | 53.4784 | 52.0968 | 51.859
|  | PRESSED STEEL SWINDON PRIMARY | EE |  |  |  |  | 32.8615 | 65.5458 | 65.1345 | 64.6723 | 64.2253 | 63.257 | 61.9937 | 60.7356 | 59.7804 | 56.8764 | 55.61 | 55.6692 | 31.0392 | 60.8662 | 60.4988 | 60.0825 | 59.7876 | 59.0672 | 58.1233 | 57.1519 | 56.3794 | 53.6427 | 51.2815 | 47.9304 | 30.3256 | 61.9539 | 61.5386 | 61.0733 | 60.6968 | 59.7845 | 58.6039 | 57.4172 | 56.5478 | 53.9988 | 52.8958 | 52.9631
|  | PRESSED STEEL SWINDON PRIMARY | HT |  |  |  |  | 33.1237 | 65.8968 | 65.5968 | 65.0682 | 64.2549 | 63.2825 | 62.4356 | 61.3713 | 60.4947 | 57.2815 | 55.6804 | 55.3427 | 31.2862 | 61.2162 | 61.0315 | 60.5856 | 59.9539 | 59.2692 | 58.5386 | 57.7407 | 57.1519 | 54.9998 | 54.0927 | 53.8845 | 30.6082 | 62.3315 | 62.0366 | 61.4998 | 60.7162 | 59.8009 | 59.0794 | 58.0856 | 57.2876 | 54.3958 | 52.9651 | 52.6958
|  | PRESSED STEEL SWINDON PRIMARY | HE |  |  |  |  | 33.1247 | 65.8998 | 65.5978 | 65.3009 | 64.5958 | 63.71 | 62.8111 | 61.6172 | 60.4896 | 56.5141 | 55.0498 | 54.7886 | 31.2056 | 61.0886 | 60.8498 | 60.5998 | 59.9998 | 59.3151 | 58.6141 | 57.6447 | 56.7417 | 53.7039 | 51.1958 | 47.71 | 30.6051 | 62.3274 | 62.0304 | 61.7468 | 61.06 | 60.2284 | 59.4713 | 58.3356 | 57.2611 | 53.4784 | 52.0968 | 51.859
|  | PRESSED STEEL SWINDON PRIMARY | CF |  |  |  |  | 33.3717 | 66.2682 | 66.1039 | 65.9202 | 65.6427 | 65.1886 | 64.4907 | 63.6978 | 63.2835 | 59.7784 | 57.2927 | 55.4947 | 31.3341 | 61.2733 | 61.0978 | 60.8937 | 60.6162 | 60.159 | 59.509 | 58.7621 | 58.2447 | 54.4509 | 49.9315 | 42.3488 | 30.8327 | 62.6621 | 62.4947 | 62.3009 | 62.0529 | 61.6141 | 60.958 | 60.2111 | 59.8866 | 56.5804 | 54.2151 | 52.5315
FLEET-BRAMLEY GSP | ALTON BSP | PRESTON CANDOVER PRIMARY | MINIMUM HEADROOM | SU 60879 41131 | NO | NO | 9.135 | 2.5073 | 2.0644 | 1.7257 | 1.4777 | 1.2216 | 1.0573 | 0.80629 | 0.55629 | 0.41241 | -2.4682 | -2.706 | -2.9223 | 5.542 | 5.2747 | 5.1032 | 4.9481 | 4.7808 | 4.6532 | 4.4512 | 4.2542 | 4.1553 | 1.7767 | 1.1787 | -0.17535 | 4.0155 | 3.6206 | 3.3389 | 3.1053 | 2.8604 | 2.692 | 2.4532 | 2.2134 | 2.0808 | -0.44065 | -0.64984 | -0.83453
|  | PRESTON CANDOVER PRIMARY | EE |  |  |  |  | 2.5073 | 2.0644 | 1.7257 | 1.4777 | 1.2216 | 1.0573 | 0.80629 | 0.55629 | 0.41241 | -2.4682 | -2.706 | -2.8192 | 5.542 | 5.2747 | 5.1032 | 4.9481 | 4.7808 | 4.6532 | 4.4512 | 4.2542 | 4.1553 | 1.7767 | 1.3604 | 0.70935 | 4.0155 | 3.6206 | 3.3389 | 3.1053 | 2.8604 | 2.692 | 2.4532 | 2.2134 | 2.0808 | -0.44065 | -0.64984 | -0.74473
|  | PRESTON CANDOVER PRIMARY | HT |  |  |  |  | 2.5196 | 2.1706 | 1.8349 | 1.6206 | 1.4042 | 1.243 | 1.0593 | 0.90935 | 0.46241 | -2.3192 | -2.6794 | -2.9223 | 5.5451 | 5.3736 | 5.2114 | 5.1093 | 5.0012 | 4.9114 | 4.8032 | 4.7042 | 4.3532 | 2.1349 | 1.9481 | 1.8257 | 4.0379 | 3.7563 | 3.4777 | 3.2838 | 3.1012 | 2.94 | 2.7532 | 2.6063 | 2.192 | -0.31718 | -0.63453 | -0.83453
|  | PRESTON CANDOVER PRIMARY | HE |  |  |  |  | 2.5747 | 2.1696 | 1.842 | 1.6257 | 1.4298 | 1.2685 | 1.09 | 0.94302 | 0.75833 | -2.3845 | -2.6182 | -2.7172 | 5.6032 | 5.3502 | 5.1808 | 5.0644 | 4.9644 | 4.8634 | 4.7379 | 4.6389 | 4.492 | 1.8277 | 1.4022 | 0.75935 | 4.1053 | 3.7563 | 3.4828 | 3.29 | 3.1257 | 2.9685 | 2.7859 | 2.642 | 2.4573 | -0.37024 | -0.58147 | -0.66412
|  | PRESTON CANDOVER PRIMARY | CF |  |  |  |  | 2.9522 | 2.7583 | 2.4379 | 2.1318 | 1.8012 | 1.5981 | 1.4522 | 1.3247 | 1.1869 | 0.50016 | -2.1825 | -2.5927 | 5.7838 | 5.6726 | 5.4614 | 5.2961 | 5.1144 | 5.0002 | 4.8879 | 4.7828 | 4.6706 | 3.9614 | 1.1787 | -0.17535 | 4.3961 | 4.2318 | 3.9532 | 3.7053 | 3.4318 | 3.2716 | 3.1277 | 3.0012 | 2.8624 | 2.1777 | -0.18351 | -0.55086
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN PRIMARY | MINIMUM HEADROOM | SY 74226 95039 | NO | NO | 0.016 | 5.4681 | 5.3936 | 5.2936 | 5.2181 | 5.1007 | 4.9518 | 4.7691 | 4.6579 | 4.5844 | 4.1803 | 3.9252 | 3.7436 | 5.734 | 5.6727 | 5.5942 | 5.535 | 5.4411 | 5.3238 | 5.1789 | 5.0931 | 5.0554 | 4.7707 | 4.3268 | 3.3309 | 5.3834 | 5.3049 | 5.2059 | 5.1293 | 5.0079 | 4.8579 | 4.6732 | 4.56 | 4.5089 | 4.1661 | 3.9477 | 3.7926
|  | PUDDLETOWN PRIMARY | EE |  |  |  |  | 5.4681 | 5.3936 | 5.2936 | 5.2181 | 5.1007 | 4.9518 | 4.7691 | 4.6579 | 4.5844 | 4.1803 | 3.9497 | 3.8007 | 5.734 | 5.6727 | 5.5942 | 5.535 | 5.4411 | 5.3238 | 5.1789 | 5.0931 | 5.0554 | 4.7707 | 4.4401 | 3.9462 | 5.3834 | 5.3049 | 5.2059 | 5.1293 | 5.0079 | 4.8579 | 4.6732 | 4.56 | 4.5089 | 4.1661 | 3.9742 | 3.8426
|  | PUDDLETOWN PRIMARY | HT |  |  |  |  | 5.563 | 5.4977 | 5.4436 | 5.363 | 5.2813 | 5.1609 | 5.065 | 4.9273 | 4.7844 | 4.2252 | 3.9252 | 3.7436 | 5.8115 | 5.7666 | 5.7299 | 5.6707 | 5.6136 | 5.535 | 5.4789 | 5.384 | 5.2819 | 4.9799 | 4.8523 | 4.7646 | 5.4702 | 5.4059 | 5.3559 | 5.2793 | 5.2038 | 5.0865 | 4.9998 | 4.8671 | 4.7293 | 4.2028 | 3.9477 | 3.7926
|  | PUDDLETOWN PRIMARY | HE |  |  |  |  | 5.562 | 5.4997 | 5.4487 | 5.3701 | 5.2946 | 5.1834 | 5.0946 | 4.9691 | 4.8354 | 4.2854 | 4.0589 | 3.9487 | 5.8105 | 5.7656 | 5.7299 | 5.6707 | 5.6146 | 5.535 | 5.4778 | 5.3809 | 5.2799 | 4.838 | 4.4993 | 4.0227 | 5.4702 | 5.4079 | 5.36 | 5.2865 | 5.214 | 5.1069 | 5.0253 | 4.9028 | 4.7742 | 4.262 | 4.0742 | 3.9824
|  | PUDDLETOWN PRIMARY | CF |  |  |  |  | 5.5936 | 5.5456 | 5.4885 | 5.4497 | 5.3875 | 5.3293 | 5.2467 | 5.2007 | 5.1171 | 4.6752 | 4.3477 | 4.1058 | 5.8309 | 5.7962 | 5.7544 | 5.7268 | 5.6758 | 5.6187 | 5.5452 | 5.4962 | 5.4166 | 4.9431 | 4.3268 | 3.3309 | 5.5018 | 5.4538 | 5.3977 | 5.362 | 5.3028 | 5.2457 | 5.1661 | 5.1222 | 5.0406 | 4.5987 | 4.3151 | 4.0998
AXMINSTER GSP | YEOVIL BSP | PULHAM PRIMARY | MINIMUM HEADROOM | ST 71579 09451 | NO | NO | 0.472 | 5.9951 | 5.8522 | 5.7349 | 5.5808 | 5.4553 | 5.2512 | 5.0073 | 4.7594 | 4.6165 | 3.8798 | 3.6451 | 3.489 | 6.8222 | 6.708 | 6.6222 | 6.4947 | 6.3978 | 6.2376 | 6.0457 | 5.8549 | 5.759 | 5.3008 | 4.8304 | 3.6314 | 5.9424 | 5.7986 | 5.6884 | 5.522 | 5.3904 | 5.1761 | 4.9251 | 4.6761 | 4.5445 | 3.9108 | 3.7108 | 3.5731
|  | PULHAM PRIMARY | EE |  |  |  |  | 5.9951 | 5.8522 | 5.7349 | 5.5808 | 5.4553 | 5.2512 | 5.0073 | 4.7594 | 4.6165 | 3.8798 | 3.6451 | 3.5767 | 6.8222 | 6.708 | 6.6222 | 6.4947 | 6.3978 | 6.2376 | 6.0457 | 5.8549 | 5.759 | 5.3008 | 4.9498 | 4.411 | 5.9424 | 5.7986 | 5.6884 | 5.522 | 5.3904 | 5.1761 | 4.9251 | 4.6761 | 4.5445 | 3.9108 | 3.7108 | 3.6445
|  | PULHAM PRIMARY | HT |  |  |  |  | 6.0604 | 5.9635 | 5.8522 | 5.7298 | 5.6257 | 5.4584 | 5.2727 | 5.1176 | 4.9257 | 4.0543 | 3.7104 | 3.489 | 6.909 | 6.8498 | 6.7763 | 6.6906 | 6.6284 | 6.5161 | 6.3876 | 6.2937 | 6.158 | 5.6018 | 5.4284 | 5.3304 | 6.019 | 5.9261 | 5.82 | 5.6976 | 5.6027 | 5.4404 | 5.2567 | 5.1047 | 4.9057 | 4.0598 | 3.7567 | 3.5731
|  | PULHAM PRIMARY | HE |  |  |  |  | 6.0614 | 5.9665 | 5.8573 | 5.7369 | 5.638 | 5.4737 | 5.291 | 5.142 | 4.9512 | 3.9614 | 3.7482 | 3.6859 | 6.8967 | 6.8314 | 6.7539 | 6.6651 | 6.5947 | 6.4794 | 6.3386 | 6.2355 | 6.0876 | 5.3763 | 5.0294 | 4.4978 | 6.02 | 5.9282 | 5.8251 | 5.7078 | 5.6159 | 5.4588 | 5.2782 | 5.1312 | 4.9363 | 4.0016 | 3.82 | 3.7659
|  | PULHAM PRIMARY | CF |  |  |  |  | 6.0941 | 6.0155 | 5.9237 | 5.8308 | 5.7308 | 5.6502 | 5.5329 | 5.4053 | 5.2737 | 4.6237 | 4.1227 | 3.7329 | 6.9212 | 6.8682 | 6.7978 | 6.7294 | 6.6488 | 6.5855 | 6.4814 | 6.3651 | 6.2437 | 5.5743 | 4.8304 | 3.6314 | 6.0557 | 5.9812 | 5.8935 | 5.8047 | 5.7098 | 5.6394 | 5.5231 | 5.3976 | 5.2649 | 4.5863 | 4.1231 | 3.7894
LOVEDEAN GSP | FORT WIDLEY BSP | PURBROOK PRIMARY | MINIMUM HEADROOM | SU 67047 07819 | NO | YES | 2.146 | 5.7544 | 5.4728 | 5.1218 | 4.6718 | 4.3524 | 3.7922 | 3.383 | 2.7361 | 2.2534 | 0.10343 | -1.3649 | -2.1282 | 7.0126 | 6.7616 | 6.4483 | 6.08 | 6.0351 | 5.6259 | 5.1636 | 4.6657 | 4.3167 | 2.3932 | -1.3272 | -8.8578 | 5.7014 | 5.4157 | 5.0473 | 4.6116 | 4.53 | 4.0249 | 3.5269 | 2.9279 | 2.5187 | 0.76771 | -0.42514 | -1.017
|  | PURBROOK PRIMARY | EE |  |  |  |  | 5.7544 | 5.4728 | 5.1218 | 4.6718 | 4.5606 | 3.9963 | 3.383 | 2.7361 | 2.2534 | 0.25649 | -1.0762 | -1.7211 | 7.0126 | 6.7616 | 6.4483 | 6.08 | 6.0351 | 5.6259 | 5.1636 | 4.6657 | 4.3167 | 2.3932 | 0.046286 | -3.6578 | 5.7014 | 5.4157 | 5.0473 | 4.6116 | 4.6034 | 4.0983 | 3.5269 | 2.9279 | 2.5187 | 0.86771 | -0.18229 | -0.70371
|  | PURBROOK PRIMARY | HT |  |  |  |  | 5.8351 | 5.5381 | 5.18 | 4.8034 | 4.3524 | 3.7922 | 3.5289 | 3.0157 | 2.4902 | 0.10343 | -1.3649 | -2.1282 | 7.2085 | 7.0442 | 6.8238 | 6.6085 | 6.3289 | 6.0055 | 5.9647 | 5.6626 | 5.3493 | 4.0096 | 3.3483 | 2.9728 | 5.8606 | 5.5983 | 5.2657 | 4.9432 | 4.53 | 4.0249 | 3.8687 | 3.3973 | 2.9116 | 0.76771 | -0.42514 | -1.017
|  | PURBROOK PRIMARY | HE |  |  |  |  | 5.9187 | 5.6891 | 5.4085 | 5.1126 | 4.7371 | 4.2616 | 4.0555 | 3.5677 | 3.0687 | 0.98302 | -0.25473 | -0.87514 | 7.1687 | 6.983 | 6.7544 | 6.5147 | 6.2106 | 5.8483 | 5.7351 | 5.3534 | 4.9544 | 2.7606 | 0.42384 | -3.2568 | 5.9218 | 5.7096 | 5.4402 | 5.1769 | 4.8238 | 4.3891 | 4.284 | 3.8361 | 3.3738 | 1.5096 | 0.51771 | 0.03302
|  | PURBROOK PRIMARY | CF |  |  |  |  | 6.1851 | 6.1065 | 5.9942 | 5.8524 | 5.7402 | 5.5687 | 5.3279 | 5.0687 | 5.1249 | 2.7657 | 1.4065 | 0.024857 | 7.2871 | 7.1585 | 6.9902 | 6.7861 | 6.5851 | 6.3065 | 5.9677 | 5.6055 | 5.532 | 2.68 | -1.3272 | -8.8578 | 6.1402 | 6.0463 | 5.9116 | 5.7504 | 5.631 | 5.4412 | 5.1973 | 4.93 | 5.0667 | 3.0177 | 1.8493 | 0.71363
FLEET-BRAMLEY GSP | PYESTOCK BSP | PYESTOCK PRIMARY | MINIMUM HEADROOM | SU 82940 54553 | NO | NO | 11.45 | 11.0073 | 11.0073 | 11.0063 | 11.0063 | 11.0063 | 11.0063 | 11.0063 | 11.0053 | 11.0063 | 11.0063 | 11.0053 | 11.0053 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 10.1996 | 10.1996 | 10.1996 | 10.1986 | 10.1986 | 10.1986 | 10.1986 | 10.1986 | 10.1986 | 10.1986 | 10.1986 | 10.1986
|  | PYESTOCK PRIMARY | EE |  |  |  |  | 11.0073 | 11.0073 | 11.0073 | 11.0063 | 11.0063 | 11.0063 | 11.0063 | 11.0053 | 11.0063 | 11.0063 | 11.0053 | 11.0053 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0061 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 10.1996 | 10.1996 | 10.1996 | 10.1996 | 10.1986 | 10.1986 | 10.1986 | 10.1986 | 10.1986 | 10.1986 | 10.1986 | 10.1986
|  | PYESTOCK PRIMARY | HT |  |  |  |  | 11.0073 | 11.0073 | 11.0063 | 11.0063 | 11.0073 | 11.0063 | 11.0063 | 11.0063 | 11.0063 | 11.0063 | 11.0073 | 11.0073 | 9.0051 | 9.0051 | 9.0061 | 9.0061 | 9.0061 | 9.0051 | 9.0051 | 9.0061 | 9.0061 | 9.0082 | 9.0082 | 9.0082 | 10.1996 | 10.1996 | 10.1996 | 10.1986 | 10.1986 | 10.1996 | 10.1996 | 10.1986 | 10.1986 | 10.1996 | 10.1996 | 10.1996
|  | PYESTOCK PRIMARY | HE |  |  |  |  | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0063 | 11.0063 | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0084 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0061 | 9.0061 | 9.0061 | 9.0061 | 9.0071 | 9.0082 | 10.1996 | 10.1996 | 10.1996 | 10.1996 | 10.1996 | 10.1996 | 10.1986 | 10.1986 | 10.1996 | 10.1996 | 10.1996 | 10.1996
|  | PYESTOCK PRIMARY | CF |  |  |  |  | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0073 | 11.0084 | 9.0061 | 9.0061 | 9.0061 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0051 | 9.0071 | 9.0071 | 9.0082 | 10.2006 | 10.1996 | 10.1996 | 10.1996 | 10.1996 | 10.1996 | 10.1996 | 10.1996 | 10.1996 | 10.1996 | 10.2006 | 10.1996
MINETY GSP | TOOTHILL BSP | QUARRY ROAD PRIMARY | MINIMUM HEADROOM | SU 15334 83380 | NO | NO | 0.9 | 12.3245 | 11.8939 | 11.3306 | 10.6765 | 10.098 | 9 | 7.75 | 6.5204 | 5.6888 | 3.1908 | 1.4214 | 1.0571 | 14.5316 | 14.2092 | 13.8133 | 13.3643 | 12.8378 | 12.0663 | 11.1765 | 10.2745 | 9.598 | 6.8827 | 2.249 | -7.4071 | 12.3051 | 11.8918 | 11.3541 | 10.7276 | 10.2388 | 9.2235 | 8.052 | 6.8918 | 6.1214 | 3.8745 | 2.3929 | 2.1204
|  | QUARRY ROAD PRIMARY | EE |  |  |  |  | 12.3245 | 11.8939 | 11.3306 | 10.6765 | 10.098 | 9 | 7.75 | 6.5204 | 5.6888 | 3.1908 | 1.752 | 1.7469 | 14.5316 | 14.2092 | 13.8133 | 13.3643 | 12.8378 | 12.0663 | 11.1765 | 10.2745 | 9.598 | 6.8827 | 3.8929 | -0.48776 | 12.3051 | 11.8918 | 11.3541 | 10.7276 | 10.2388 | 9.2235 | 8.052 | 6.8918 | 6.1214 | 3.8745 | 2.699 | 2.6755
|  | QUARRY ROAD PRIMARY | HT |  |  |  |  | 12.6684 | 12.3398 | 11.8918 | 11.1816 | 10.2673 | 9.2255 | 8.5684 | 7.648 | 6.9204 | 3.5867 | 1.4214 | 1.0571 | 14.8571 | 14.6673 | 14.4122 | 13.8765 | 13.2571 | 12.6143 | 12.1888 | 11.6061 | 11.1776 | 9.3296 | 8.1367 | 7.8408 | 12.6806 | 12.3704 | 11.951 | 11.3092 | 10.4673 | 9.5184 | 8.9612 | 8.0918 | 7.3939 | 4.2755 | 2.3929 | 2.1204
|  | QUARRY ROAD PRIMARY | HE |  |  |  |  | 12.6571 | 12.3582 | 11.9745 | 11.5673 | 10.7459 | 9.8082 | 9.0816 | 8.0776 | 7.2418 | 4.3714 | 2.7633 | 2.3143 | 14.7357 | 14.4888 | 14.1888 | 13.8735 | 13.2112 | 12.5224 | 11.952 | 11.1724 | 10.4786 | 7.4173 | 4.2418 | -0.29388 | 12.6663 | 12.3847 | 12.0173 | 11.65 | 10.8929 | 10.0388 | 9.4398 | 8.5133 | 7.7133 | 4.9949 | 3.6255 | 3.2765
|  | QUARRY ROAD PRIMARY | CF |  |  |  |  | 12.9265 | 12.7847 | 12.601 | 12.3898 | 12.198 | 11.8235 | 11.2908 | 10.6347 | 10.352 | 7.2347 | 4.7378 | 2.5082 | 14.85 | 14.6694 | 14.4531 | 14.2122 | 13.9469 | 13.4857 | 12.9041 | 12.2286 | 11.7622 | 7.8071 | 2.249 | -7.4071 | 12.901 | 12.7469 | 12.5551 | 12.3367 | 12.15 | 11.7888 | 11.2765 | 10.6571 | 10.4663 | 7.5224 | 5.2949 | 3.401
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | QUEENSMEAD PRIMARY | MINIMUM HEADROOM | SU 87062 55683 | NO | NO | 4.555 | 2.9868 | 2.45 | 1.6582 | 0.95309 | 0.19187 | -0.70303 | -1.9112 | -3.2102 | -4.5836 | -10.7938 | -13.7622 | -14.0765 | 3.5031 | 3.146 | 2.5837 | 2.1153 | 1.6062 | 1.047 | 0.2633 | -0.70609 | -1.7581 | -6.453 | -8.6153 | -11.7194 | 2.1449 | 1.6306 | 0.90105 | 0.22452 | -0.50507 | -1.3561 | -2.5194 | -3.7673 | -5.0877 | -11.0275 | -13.7806 | -14.0571
|  | QUEENSMEAD PRIMARY | EE |  |  |  |  | 2.9868 | 2.45 | 1.6582 | 0.95309 | 0.19187 | -0.65405 | -1.5459 | -2.4898 | -3.2092 | -5.35 | -5.8867 | -6.451 | 3.5031 | 3.146 | 2.5837 | 2.1153 | 1.6062 | 1.047 | 0.46432 | -0.16323 | -0.65303 | -2.1398 | -3.2734 | -6.5275 | 2.1449 | 1.6306 | 0.90105 | 0.22452 | -0.50507 | -1.3173 | -2.1673 | -3.0724 | -3.7612 | -5.7734 | -6.251 | -6.6551
|  | QUEENSMEAD PRIMARY | HT |  |  |  |  | 3.3582 | 3.1062 | 2.6113 | 2.2949 | 1.9357 | 1.5153 | 1.0123 | 0.47248 | -0.096906 | -2.954 | -4.2949 | -5.1122 | 4.0817 | 3.9031 | 3.6092 | 3.3735 | 3.0888 | 2.7898 | 2.4021 | 1.9868 | 1.5572 | -0.19691 | -0.96731 | -1.0979 | 2.7011 | 2.4562 | 1.9868 | 1.6755 | 1.3245 | 0.94187 | 0.45207 | -0.10915 | -0.74997 | -3.4632 | -4.6571 | -4.9612
|  | QUEENSMEAD PRIMARY | HE |  |  |  |  | 3.1847 | 2.646 | 1.85 | 1.1123 | 0.25411 | -0.70303 | -1.9112 | -3.2102 | -4.5836 | -10.7938 | -13.7622 | -14.0765 | 3.6531 | 3.299 | 2.7337 | 2.25 | 1.6857 | 1.0633 | 0.2633 | -0.70609 | -1.7581 | -6.453 | -8.6153 | -8.8234 | 2.3388 | 1.8215 | 1.0898 | 0.38167 | -0.4418 | -1.3561 | -2.5194 | -3.7673 | -5.0877 | -11.0275 | -13.7806 | -14.0571
|  | QUEENSMEAD PRIMARY | CF |  |  |  |  | 3.5235 | 3.3378 | 2.8817 | 2.6664 | 2.1735 | 1.6735 | 1 | 0.23677 | -0.5816 | -5.4949 | -9.7989 | -12.7663 | 4.1388 | 3.9266 | 3.5204 | 3.2408 | 2.9092 | 2.5643 | 2.1082 | 1.5857 | 1.0286 | -2.5877 | -5.9418 | -11.7194 | 2.846 | 2.6664 | 2.2266 | 1.8735 | 1.4 | 0.91432 | 0.26432 | -0.47038 | -1.2561 | -5.9632 | -10.0826 | -12.851
MELKSHAM GSP | WEST GRAFTON BSP | RAMSBURY PRIMARY | MINIMUM HEADROOM | SU 27380 72108 | NO | NO | 1.451 | 3.6306 | 3.4765 | 3.351 | 3.1847 | 3.0132 | 2.8234 | 2.551 | 2.2785 | 2.1306 | 1.3234 | 0.64487 | 0.2316 | 4.5122 | 4.3959 | 4.3092 | 4.1806 | 4.0418 | 3.9183 | 3.7132 | 3.5061 | 3.3979 | 2.8571 | 2.1122 | 0.28569 | 3.8898 | 3.7449 | 3.6285 | 3.4714 | 3.3041 | 3.1255 | 2.8724 | 2.6214 | 2.4796 | 1.7551 | 1.1653 | 0.83058
|  | RAMSBURY PRIMARY | EE |  |  |  |  | 3.6306 | 3.4765 | 3.351 | 3.1847 | 3.0132 | 2.8234 | 2.551 | 2.2785 | 2.1306 | 1.3561 | 0.79385 | 0.34691 | 4.5122 | 4.3959 | 4.3092 | 4.1806 | 4.0418 | 3.9183 | 3.7132 | 3.5061 | 3.3979 | 2.8571 | 2.2234 | 1.2592 | 3.8898 | 3.7449 | 3.6285 | 3.4714 | 3.3041 | 3.1255 | 2.8724 | 2.6214 | 2.4796 | 1.7775 | 1.299 | 0.92956
|  | RAMSBURY PRIMARY | HT |  |  |  |  | 3.7 | 3.5816 | 3.4724 | 3.3551 | 3.2653 | 3.0704 | 2.85 | 2.6673 | 2.4326 | 1.3234 | 0.64487 | 0.2316 | 4.5918 | 4.5224 | 4.449 | 4.3663 | 4.3112 | 4.1918 | 4.053 | 3.9551 | 3.8081 | 3.1592 | 2.853 | 2.6775 | 3.9673 | 3.8602 | 3.7541 | 3.6428 | 3.5581 | 3.3755 | 3.1683 | 3 | 2.7806 | 1.7551 | 1.1653 | 0.83058
|  | RAMSBURY PRIMARY | HE |  |  |  |  | 3.7102 | 3.6132 | 3.503 | 3.3806 | 3.2979 | 3.1275 | 2.9428 | 2.7908 | 2.5918 | 1.602 | 1.0377 | 0.73364 | 4.5847 | 4.5173 | 4.4387 | 4.3449 | 4.2867 | 4.1673 | 4.0296 | 3.9255 | 3.7683 | 2.9867 | 2.3367 | 1.4306 | 3.9745 | 3.8836 | 3.7796 | 3.6653 | 3.5867 | 3.4285 | 3.252 | 3.1112 | 2.9245 | 2.0071 | 1.5122 | 1.2622
|  | RAMSBURY PRIMARY | CF |  |  |  |  | 3.7755 | 3.7132 | 3.6683 | 3.6051 | 3.5296 | 3.4775 | 3.3745 | 3.2602 | 3.1336 | 2.4122 | 1.7806 | 1.2204 | 4.6224 | 4.5602 | 4.5204 | 4.4592 | 4.3806 | 4.3153 | 4.2071 | 4.0918 | 3.9653 | 3.1908 | 2.1122 | 0.28569 | 4.0336 | 3.9704 | 3.9265 | 3.8653 | 3.7928 | 3.7459 | 3.6469 | 3.5377 | 3.4234 | 2.753 | 2.1622 | 1.6714
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | RATFYN PRIMARY | MINIMUM HEADROOM | SU 16215 42533 | NO | NO | 1.609 | 11.6759 | 11.2647 | 10.8035 | 10.7657 | 10.3576 | 9.7412 | 9.0443 | 8.3555 | 7.9076 | 5.6106 | 3.8024 | 2.8861 | 13.588 | 13.3329 | 13.0084 | 12.9645 | 12.6553 | 12.2431 | 11.7665 | 11.2839 | 10.9716 | 9.1869 | 6.9941 | 1.4676 | 11.5376 | 11.1478 | 10.708 | 10.6886 | 10.3018 | 9.7263 | 9.0692 | 8.4192 | 8.012 | 6.0141 | 4.5273 | 3.7733
|  | RATFYN PRIMARY | EE |  |  |  |  | 11.6759 | 11.2647 | 10.8035 | 10.7657 | 10.3576 | 9.7412 | 9.0443 | 8.3555 | 7.9076 | 5.6239 | 4.0647 | 3.2984 | 13.588 | 13.3329 | 13.0084 | 12.9645 | 12.6553 | 12.2431 | 11.7665 | 11.2839 | 10.9716 | 9.1869 | 7.2961 | 4.5778 | 11.5376 | 11.1478 | 10.708 | 10.6886 | 10.3018 | 9.7263 | 9.0692 | 8.4192 | 8.012 | 6.0141 | 4.7294 | 4.0988
|  | RATFYN PRIMARY | HT |  |  |  |  | 11.9035 | 11.58 | 11.2606 | 10.928 | 10.5555 | 10.3422 | 9.7922 | 9.2208 | 8.6198 | 5.6106 | 3.8024 | 2.8861 | 13.7869 | 13.6135 | 13.4431 | 13.2665 | 13.0533 | 12.9971 | 12.689 | 12.3635 | 12.0176 | 10.388 | 9.5063 | 9.0431 | 11.7865 | 11.4784 | 11.1835 | 10.8631 | 10.5131 | 10.36 | 9.8508 | 9.3192 | 8.7569 | 6.0457 | 4.5273 | 3.7733
|  | RATFYN PRIMARY | HE |  |  |  |  | 11.9331 | 11.6473 | 11.3678 | 11.0361 | 10.6831 | 10.5422 | 10.0627 | 9.5667 | 9.0504 | 6.4698 | 4.9769 | 4.279 | 13.7369 | 13.5451 | 13.3573 | 13.139 | 12.8941 | 12.8073 | 12.4829 | 12.1247 | 11.7492 | 9.6512 | 7.7665 | 5.0655 | 11.809 | 11.5324 | 11.2692 | 10.9559 | 10.6233 | 10.5294 | 10.0804 | 9.612 | 9.1253 | 6.7865 | 5.5549 | 4.9957
|  | RATFYN PRIMARY | CF |  |  |  |  | 12.0902 | 11.9473 | 11.7688 | 11.6127 | 11.3892 | 11.132 | 10.829 | 10.9178 | 10.6473 | 8.8239 | 7.0167 | 5.2871 | 13.8012 | 13.6757 | 13.5206 | 13.3788 | 13.1767 | 12.9298 | 12.6349 | 12.592 | 12.2961 | 10.1798 | 6.9941 | 1.4676 | 11.9508 | 11.808 | 11.6263 | 11.4814 | 11.2702 | 11.0263 | 10.7345 | 10.8386 | 10.5845 | 8.8824 | 7.2641 | 5.8171
BRAMLEY (BASI) GSP | READING BSP | READING PRIMARY | MINIMUM HEADROOM | SU 74591 73788 | NO | YES | 18.868 | 1.9361 | 1.4239 | 0.43305 | -0.53225 | -1.62 | -3.2476 | -5.0629 | -6.8516 | -8.169 | -14.1159 | -18.6231 | -20.0659 | 4.4416 | 4.1192 | 3.3049 | 2.4733 | 1.5335 | 0.33856 | -1.04 | -2.4267 | -3.3676 | -8.7349 | -17.2145 | -36.1216 | 0.47407 | 0.028155 | -0.93919 | -1.88 | -2.9331 | -4.4555 | -6.1729 | -7.8739 | -9.0504 | -14.1882 | -18.0372 | -19.2178
|  | READING PRIMARY | EE |  |  |  |  | 1.9361 | 1.4239 | 0.43305 | -0.53225 | -1.62 | -3.2476 | -5.0629 | -6.8516 | -8.169 | -14.1159 | -17.9139 | -18.7802 | 4.4416 | 4.1192 | 3.3049 | 2.4733 | 1.5335 | 0.33856 | -1.04 | -2.4267 | -3.3676 | -8.7349 | -14.7574 | -23.5012 | 0.47407 | 0.028155 | -0.93919 | -1.88 | -2.9331 | -4.4555 | -6.1729 | -7.8739 | -9.0504 | -14.1882 | -17.4382 | -18.2076
|  | READING PRIMARY | HT |  |  |  |  | 2.4218 | 1.6443 | 0.70754 | 0.23203 | -0.61287 | -1.9547 | -3.4078 | -4.9312 | -6.4996 | -14.072 | -18.6231 | -20.0659 | 5.1426 | 4.611 | 3.9835 | 3.8396 | 3.262 | 2.5059 | 1.6457 | 0.74469 | -0.21144 | -4.5033 | -6.792 | -7.5686 | 1.1026 | 0.35673 | -0.52695 | -0.89531 | -1.7127 | -2.932 | -4.282 | -5.6923 | -7.1423 | -14.0065 | -18.0372 | -19.2178
|  | READING PRIMARY | HE |  |  |  |  | 2.4912 | 1.7994 | 0.92897 | 0.55856 | -0.22613 | -1.3986 | -2.6874 | -4.0312 | -5.42 | -11.6374 | -15.321 | -16.5904 | 5.0171 | 4.4375 | 3.7355 | 3.509 | 2.8059 | 1.9396 | 0.94775 | -0.1298 | -1.2716 | -7.4125 | -13.5053 | -22.3461 | 1.1465 | 0.47305 | -0.35654 | -0.63205 | -1.3953 | -2.4739 | -3.6882 | -4.9525 | -6.2484 | -11.929 | -15.0933 | -16.1137
|  | READING PRIMARY | CF |  |  |  |  | 3.0218 | 2.6198 | 2.0392 | 1.8851 | 1.431 | 0.92285 | 0.32285 | -0.31389 | -0.97511 | -5.4435 | -10.4108 | -14.8935 | 5.2304 | 4.8018 | 4.2141 | 4.01 | 3.4069 | 2.7069 | 1.8937 | 1.0355 | 0.11203 | -6.489 | -17.2145 | -36.1216 | 1.6057 | 1.2026 | 0.64346 | 0.54346 | 0.08938 | -0.41674 | -1.0065 | -1.63 | -2.282 | -6.5647 | -10.9361 | -14.8025
FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN PRIMARY | MINIMUM HEADROOM | SU 71540 74122 | NO | NO | 14.43 | 52.8062 | 51.7572 | 50.5062 | 48.6664 | 46.4888 | 44.3388 | 42.0827 | 39.3756 | 37.0103 | 34.6317 | 33.0082 | 32.6021 | 59.6756 | 58.8235 | 58.0674 | 57.0001 | 55.7674 | 54.4552 | 52.8858 | 51.2276 | 49.7368 | 46.0307 | 40.6246 | 29.698 | 55.0786 | 54.4164 | 53.3715 | 51.8031 | 49.9154 | 48.0695 | 46.144 | 43.8593 | 41.9215 | 39.5991 | 38.1256 | 37.795
|  | READING TOWN PRIMARY | EE |  |  |  |  | 52.8062 | 51.7572 | 50.5062 | 48.6664 | 46.4888 | 44.3388 | 42.0827 | 39.3756 | 37.0103 | 34.6317 | 33.697 | 33.5082 | 59.6756 | 58.8235 | 58.0674 | 57.0001 | 55.7674 | 54.4552 | 52.8858 | 51.2276 | 49.7368 | 46.0307 | 42.8786 | 37.6695 | 55.0786 | 54.4164 | 53.3715 | 51.8031 | 49.9154 | 48.0695 | 46.144 | 43.8593 | 41.9215 | 39.5991 | 38.7899 | 38.5286
|  | READING TOWN PRIMARY | HT |  |  |  |  | 53.1582 | 52.3042 | 51.2184 | 49.5715 | 47.5052 | 45.3776 | 42.9878 | 40.6164 | 38.3103 | 35.1684 | 33.0082 | 32.6021 | 60.0786 | 59.4133 | 58.8644 | 58.0276 | 56.9929 | 55.8776 | 54.3552 | 53.0419 | 51.7297 | 49.0378 | 47.6766 | 47.3674 | 55.3766 | 54.8521 | 53.9756 | 52.644 | 50.9123 | 49.2235 | 47.2388 | 45.3235 | 43.4031 | 40.2378 | 38.1256 | 37.795
|  | READING TOWN PRIMARY | HE |  |  |  |  | 53.0837 | 52.2899 | 51.2225 | 49.5991 | 47.6399 | 45.8307 | 43.5501 | 41.0878 | 38.7695 | 36.4593 | 35.2735 | 34.9062 | 59.9358 | 59.195 | 58.5684 | 57.6521 | 56.5705 | 55.4797 | 53.8756 | 52.3644 | 50.8746 | 47.0276 | 43.5593 | 38.3429 | 55.3205 | 54.7705 | 53.9429 | 52.6164 | 50.9858 | 49.5399 | 47.6297 | 45.7072 | 43.8644 | 41.5399 | 40.1205 | 39.4348
|  | READING TOWN PRIMARY | CF |  |  |  |  | 53.6001 | 53.0786 | 52.3827 | 51.0817 | 49.6327 | 48.495 | 46.9307 | 45.1868 | 43.6807 | 37.8888 | 36.1052 | 34.6991 | 60.3072 | 59.6511 | 59.0786 | 58.295 | 57.394 | 56.5562 | 55.2368 | 54.0225 | 52.8868 | 46.9082 | 40.6246 | 29.698 | 55.7531 | 55.3021 | 54.898 | 53.9072 | 52.7419 | 51.8827 | 50.5654 | 49.2164 | 48.0378 | 43.0552 | 41.1919 | 39.8154
MANNINGTON GSP | REDHILL BSP | REDHILL PRIMARY | MINIMUM HEADROOM | SZ 08512 96149 | NO | NO | 5.64 | 14.8449 | 14.1664 | 13.2766 | 12.5756 | 11.8776 | 10.7327 | 9.4837 | 8.2358 | 7.2868 | 1.45 | -2.7816 | -5.0265 | 21.9378 | 21.4837 | 20.7929 | 20.2276 | 19.6388 | 18.8368 | 17.9164 | 16.9796 | 16.3317 | 12.6041 | 7.5715 | -4.3469 | 16.7031 | 16.1286 | 15.2725 | 14.5735 | 13.8623 | 12.7633 | 11.5358 | 10.3184 | 9.4756 | 4.647 | 1.1888 | -0.57751
|  | REDHILL PRIMARY | EE |  |  |  |  | 14.8449 | 14.1664 | 13.2766 | 12.5756 | 11.8776 | 10.7327 | 9.4837 | 8.2358 | 7.2868 | 2.1796 | -1.8244 | -4.5173 | 21.9378 | 21.4837 | 20.7929 | 20.2276 | 19.6388 | 18.8368 | 17.9164 | 16.9796 | 16.3317 | 12.6041 | 8.4051 | 2.247 | 16.7031 | 16.1286 | 15.2725 | 14.5735 | 13.8623 | 12.7633 | 11.5358 | 10.3184 | 9.4756 | 5.1674 | 1.9817 | -0.17445
|  | REDHILL PRIMARY | HT |  |  |  |  | 15.0837 | 14.1888 | 13.3 | 12.9551 | 12.3664 | 11.2776 | 10.1276 | 8.9266 | 7.7113 | 1.45 | -2.7816 | -5.0265 | 22.3745 | 21.8164 | 21.2337 | 21.1266 | 20.7551 | 20.1949 | 19.5582 | 18.8858 | 18.1888 | 14.9623 | 13.1715 | 12.2409 | 17.0704 | 16.2664 | 15.4388 | 15.1766 | 14.599 | 13.6102 | 12.5398 | 11.4225 | 10.2756 | 4.647 | 1.1888 | -0.57751
|  | REDHILL PRIMARY | HE |  |  |  |  | 15.1827 | 14.3398 | 13.5102 | 13.2235 | 12.696 | 11.8837 | 11.0062 | 10.0939 | 9.1266 | 3.95 | 0.0051429 | -1.8765 | 22.2909 | 21.6847 | 21.0602 | 20.8858 | 20.448 | 19.8715 | 19.2113 | 18.5021 | 17.7439 | 13.446 | 9.199 | 3.3388 | 17.1449 | 16.3868 | 15.6143 | 15.4011 | 14.8796 | 14.1153 | 13.2674 | 12.3807 | 11.4582 | 6.7562 | 3.5817 | 2.1051
|  | REDHILL PRIMARY | CF |  |  |  |  | 15.5837 | 14.9582 | 14.3623 | 13.9888 | 13.9347 | 13.6429 | 13.297 | 12.9245 | 12.5378 | 9.3613 | 5.3919 | 1.5623 | 22.4674 | 21.9449 | 21.4123 | 21.0204 | 20.8817 | 20.4419 | 19.9286 | 19.3786 | 18.7929 | 14.4582 | 7.5715 | -4.3469 | 17.5062 | 16.9439 | 16.3827 | 15.999 | 15.9878 | 15.6786 | 15.3062 | 14.9153 | 14.5051 | 11.3674 | 7.8939 | 4.698
CHICKERELL GSP | CHICKERELL BSP | REDLANDS PRIMARY | MINIMUM HEADROOM | SY 67131 82321 | NO | NO | 3.364 | 7.1386 | 6.3284 | 5.5999 | 4.8315 | 4.0856 | 3.156 | 2.1999 | 1.2917 | 0.62536 | -3.2634 | -5.9899 | -7.4532 | 8.9835 | 8.4305 | 7.9243 | 7.4315 | 6.9376 | 6.3427 | 5.7009 | 5.0692 | 4.6172 | 1.7713 | -1.4655 | -9.4563 | 7.105 | 6.3733 | 5.7784 | 5.0856 | 4.3999 | 3.5539 | 2.655 | 1.7937 | 1.2101 | -2.1318 | -4.4828 | -5.7083
|  | REDLANDS PRIMARY | EE |  |  |  |  | 7.1386 | 6.3284 | 5.5999 | 4.8315 | 4.0856 | 3.156 | 2.1999 | 1.2917 | 0.62536 | -3.0236 | -5.5287 | -7.1471 | 8.9835 | 8.4305 | 7.9243 | 7.4315 | 6.9376 | 6.3427 | 5.7009 | 5.0692 | 4.6172 | 1.7713 | -0.98688 | -5.1563 | 7.105 | 6.3733 | 5.7784 | 5.0856 | 4.3999 | 3.5539 | 2.655 | 1.7937 | 1.2101 | -1.9685 | -4.0736 | -5.4491
|  | REDLANDS PRIMARY | HT |  |  |  |  | 7.3631 | 6.6458 | 5.6948 | 4.9662 | 4.2499 | 3.6927 | 2.8631 | 2.0621 | 1.1335 | -3.2634 | -5.9899 | -7.4532 | 9.257 | 8.8294 | 8.2233 | 7.8254 | 7.4243 | 7.2468 | 6.807 | 6.3652 | 5.8172 | 3.4366 | 2.2458 | 1.6407 | 7.3754 | 6.7437 | 5.9172 | 5.2713 | 4.6162 | 4.1927 | 3.4396 | 2.7019 | 1.8468 | -2.1318 | -4.4828 | -5.7083
|  | REDLANDS PRIMARY | HE |  |  |  |  | 7.4029 | 6.7131 | 5.7978 | 5.0968 | 4.4213 | 3.9978 | 3.305 | 2.6448 | 1.9611 | -1.7604 | -4.1512 | -5.2604 | 9.1999 | 8.7366 | 8.1009 | 7.659 | 7.2162 | 7.0152 | 6.5437 | 6.0682 | 5.5652 | 2.4478 | -0.32362 | -4.2716 | 7.408 | 6.7978 | 6.0039 | 5.3845 | 4.7672 | 4.4611 | 3.8264 | 3.2101 | 2.5754 | -0.80015 | -2.8236 | -3.7471
|  | REDLANDS PRIMARY | CF |  |  |  |  | 7.657 | 7.1529 | 6.5223 | 5.8968 | 5.309 | 4.906 | 4.8396 | 4.5131 | 4.1754 | 1.9856 | -0.80219 | -3.1563 | 9.2886 | 8.9203 | 8.4468 | 7.9774 | 7.4958 | 7.109 | 6.9611 | 6.5805 | 6.1733 | 3.3499 | -1.4655 | -9.4563 | 7.6131 | 7.1845 | 6.6499 | 6.0978 | 5.5672 | 5.1876 | 5.1876 | 4.8733 | 4.5478 | 2.4468 | 0.01618 | -2.0001
MANNINGTON GSP | SALISBURY BSP | REDLYNCH PRIMARY | MINIMUM HEADROOM | SU 19073 20576 | NO | NO | 0.657 | 5.8531 | 5.6163 | 5.3235 | 4.9949 | 5.0439 | 4.6143 | 4.1337 | 3.648 | 3.3316 | 1.5429 | 0.10612 | -0.78061 | 7.2214 | 7.1357 | 7.0306 | 6.9143 | 6.9122 | 6.7276 | 6.4918 | 6.2071 | 5.9878 | 4.601 | 2.8337 | -1.3224 | 5.9316 | 5.8194 | 5.6061 | 5.3357 | 5.3633 | 4.9888 | 4.5714 | 4.1551 | 3.8551 | 2.1122 | 0.84388 | 0.079592
|  | REDLYNCH PRIMARY | EE |  |  |  |  | 5.8531 | 5.6163 | 5.3235 | 4.9949 | 5.0439 | 4.6143 | 4.1337 | 3.648 | 3.3316 | 1.6163 | 0.34592 | -0.57959 | 7.2214 | 7.1357 | 7.0306 | 6.9143 | 6.9122 | 6.7276 | 6.4918 | 6.2071 | 5.9878 | 4.601 | 3.1133 | 0.96224 | 5.9316 | 5.8194 | 5.6061 | 5.3357 | 5.3633 | 4.9888 | 4.5714 | 4.1551 | 3.8551 | 2.1796 | 1.051 | 0.2449
|  | REDLYNCH PRIMARY | HT |  |  |  |  | 6.0184 | 5.8337 | 5.6122 | 5.4102 | 5.1561 | 4.7194 | 4.2378 | 4.1612 | 3.7184 | 1.5429 | 0.10612 | -0.78061 | 7.3031 | 7.252 | 7.1857 | 7.1214 | 7.0388 | 6.9122 | 6.699 | 6.6398 | 6.4449 | 5.452 | 4.7755 | 4.3551 | 6.0092 | 5.9143 | 5.8051 | 5.6439 | 5.4265 | 5.0327 | 4.6041 | 4.5 | 4.1031 | 2.1122 | 0.84388 | 0.079592
|  | REDLYNCH PRIMARY | HE |  |  |  |  | 6.0367 | 5.8653 | 5.6531 | 5.4694 | 5.2306 | 4.8612 | 4.4459 | 4.4398 | 4.0714 | 2.1051 | 0.88061 | 0.23265 | 7.2857 | 7.2265 | 7.15 | 7.0755 | 6.9776 | 6.8204 | 6.6082 | 6.5408 | 6.3276 | 4.8316 | 3.3378 | 1.299 | 6.0173 | 5.9276 | 5.8224 | 5.699 | 5.4939 | 5.1684 | 4.8071 | 4.7714 | 4.4459 | 2.6398 | 1.5255 | 0.97041
|  | REDLYNCH PRIMARY | CF |  |  |  |  | 6.1592 | 6.0102 | 5.9051 | 5.75 | 5.6245 | 5.4388 | 5.2194 | 4.9867 | 4.7418 | 3.8153 | 2.5 | 1.2827 | 7.3214 | 7.2653 | 7.2163 | 7.15 | 7.0816 | 6.9898 | 6.8653 | 6.6827 | 6.452 | 5.2194 | 2.8337 | -1.3224 | 6.0816 | 6.0071 | 5.952 | 5.8735 | 5.8092 | 5.6939 | 5.5112 | 5.3204 | 5.1194 | 4.2918 | 3.0633 | 1.8969
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | REGENTS PARK PRIMARY | MINIMUM HEADROOM | SU 39267 13050 | NO | NO | 1.228 | 14.3653 | 13.8255 | 12.1612 | 11.1296 | 9.3582 | 7.1204 | 4.5276 | 3.3041 | 0.32653 | -10.6643 | -20.5255 | -24.5847 | 14.7367 | 14.1204 | 12.3704 | 11.4673 | 9.3827 | 7.0163 | 4.2163 | 3.1367 | -0.12857 | -11.7786 | -21.9112 | -27.5561 | 13.352 | 12.7112 | 10.798 | 9.7041 | 7.5561 | 5.0041 | 2.0561 | 0.82245 | -2.6051 | -15.0571 | -25.8224 | -31.5184
|  | REGENTS PARK PRIMARY | EE |  |  |  |  | 14.3653 | 13.8745 | 13.301 | 12.648 | 10.8704 | 8.9541 | 7.9592 | 5.2918 | 3.5776 | -5.0592 | -7.7408 | -14.5224 | 14.7367 | 14.4541 | 14.1316 | 13.7194 | 11.8796 | 9.9612 | 9.2102 | 6.402 | 4.7133 | -4.3714 | -7.4245 | -18.251 | 13.352 | 12.9071 | 12.3969 | 11.8061 | 9.8622 | 7.7888 | 6.8888 | 3.9184 | 2.0837 | -7.6265 | -10.6398 | -18.9469
|  | REGENTS PARK PRIMARY | HT |  |  |  |  | 14.7102 | 14.1276 | 13.1827 | 12.6765 | 9.3582 | 7.1204 | 4.5276 | 3.3041 | 0.32653 | -10.6643 | -15.5306 | -24.5847 | 15.0398 | 14.4776 | 13.4602 | 13.1378 | 9.3827 | 7.0163 | 4.2163 | 3.1367 | -0.12857 | -11.7786 | -16.7592 | -27.5561 | 13.8082 | 13.1265 | 11.9724 | 11.4898 | 7.5561 | 5.0041 | 2.0561 | 0.82245 | -2.6051 | -15.0571 | -20.5 | -31.5184
|  | REGENTS PARK PRIMARY | HE |  |  |  |  | 14.651 | 13.8255 | 12.1612 | 11.1296 | 10.3939 | 8.0092 | 5.2969 | 4.1694 | 3.0184 | -10.5918 | -20.5255 | -24.0663 | 14.9337 | 14.1204 | 12.3704 | 11.4673 | 10.9724 | 8.4173 | 5.5551 | 4.7 | 3.8286 | -10.6612 | -21.9112 | -27.0378 | 13.6612 | 12.7112 | 10.798 | 9.7041 | 9.0378 | 6.3561 | 3.3337 | 2.3092 | 1.2653 | -14.0969 | -25.8224 | -30.1602
|  | REGENTS PARK PRIMARY | CF |  |  |  |  | 14.9255 | 14.7663 | 14.5857 | 14.0194 | 13.2357 | 12.2306 | 11.2694 | 10.1796 | 8.8684 | 0.64388 | -9.1939 | -17.8276 | 15.152 | 15.0245 | 14.8724 | 14.2592 | 13.4929 | 12.4765 | 11.6143 | 10.6306 | 9.2898 | 0.78878 | -10.8071 | -24.8112 | 14.0102 | 13.851 | 13.6204 | 12.9204 | 12.052 | 10.9286 | 9.9153 | 8.7653 | 7.3469 | -1.6714 | -12.851 | -22.8908
COWLEY GSP | WITNEY BSP | RISSINGTON PRIMARY | MINIMUM HEADROOM | SP 19225 19563 | YES | NO | 4.446 | 3.0171 | 2.8151 | 2.6334 | 2.4008 | 2.1365 | 1.7385 | 1.6538 | 1.2732 | 0.95792 | -0.5829 | -1.8064 | -2.5533 | 5.1671 | 5.0161 | 4.8722 | 4.6875 | 4.4865 | 4.211 | 4.2018 | 3.9447 | 3.7732 | 2.7824 | 1.8375 | -0.49514 | 3.4865 | 3.261 | 3.0589 | 2.7783 | 2.4845 | 2.0987 | 2.3293 | 1.9998 | 1.7345 | 0.38751 | -0.63902 | -1.2349
|  | RISSINGTON PRIMARY | EE |  |  |  |  | 3.0171 | 2.8151 | 2.6334 | 2.4008 | 2.1365 | 1.7385 | 1.6538 | 1.2732 | 1.0059 | -0.52371 | -1.5829 | -2.3227 | 5.1671 | 5.0161 | 4.8722 | 4.6875 | 4.4865 | 4.211 | 4.2018 | 3.9447 | 3.7732 | 2.7824 | 1.8375 | 0.5467 | 3.4865 | 3.261 | 3.0589 | 2.7783 | 2.4845 | 2.0987 | 2.3293 | 1.9998 | 1.7569 | 0.41404 | -0.44616 | -1.0533
|  | RISSINGTON PRIMARY | HT |  |  |  |  | 3.1059 | 2.9406 | 2.7834 | 2.5977 | 2.3906 | 2.0926 | 1.7253 | 1.3467 | 0.95792 | -0.5829 | -1.8064 | -2.5533 | 5.2691 | 5.1702 | 5.0783 | 4.963 | 4.8253 | 4.662 | 4.4436 | 4.214 | 3.9793 | 3.2477 | 2.6793 | 2.3498 | 3.6671 | 3.5202 | 3.3967 | 3.2232 | 3.0232 | 2.8069 | 2.461 | 2.1028 | 1.7345 | 0.38751 | -0.63902 | -1.2349
|  | RISSINGTON PRIMARY | HE |  |  |  |  | 3.1202 | 2.9681 | 2.8263 | 2.6589 | 2.4732 | 2.2273 | 1.9161 | 1.5936 | 1.2579 | -0.09514 | -1.1258 | -1.6339 | 5.2498 | 5.1416 | 5.0447 | 4.9232 | 4.7814 | 4.6232 | 4.4069 | 4.1742 | 3.9365 | 3.0355 | 2.0834 | 0.87833 | 3.6691 | 3.5232 | 3.4079 | 3.2396 | 3.0457 | 2.862 | 2.5702 | 2.26 | 1.9324 | 0.82629 | -0.015548 | -0.41555
|  | RISSINGTON PRIMARY | CF |  |  |  |  | 3.2151 | 3.112 | 2.9998 | 2.911 | 2.7896 | 2.6538 | 2.5304 | 2.3691 | 2.2018 | 1.3426 | 0.22935 | -0.80024 | 5.2936 | 5.212 | 5.1171 | 5.0406 | 4.9273 | 4.8008 | 4.6753 | 4.5069 | 4.3324 | 3.4334 | 1.9273 | -0.49514 | 3.7355 | 3.6293 | 3.512 | 3.4304 | 3.3018 | 3.1457 | 3.012 | 2.813 | 2.5998 | 2.0855 | 1.1038 | 0.22731
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | RIVERSIDE PRIMARY | MINIMUM HEADROOM | SU 47846 67187 | NO | NO | 4.44 | 12.1269 | 11.8871 | 11.6351 | 11.333 | 10.9698 | 10.5514 | 10.0596 | 9.6412 | 9.28 | 7.7596 | 6.9085 | 6.5575 | 13.7468 | 13.6009 | 13.4488 | 13.2621 | 13.0631 | 12.857 | 12.6009 | 12.3754 | 12.1907 | 10.7846 | 8.8519 | 4.358 | 13.13 | 12.9055 | 12.6698 | 12.383 | 12.0555 | 11.6442 | 11.1555 | 10.7361 | 10.3851 | 8.8136 | 7.834 | 7.4014
|  | RIVERSIDE PRIMARY | EE |  |  |  |  | 12.1269 | 11.8871 | 11.6351 | 11.333 | 10.9698 | 10.5514 | 10.0596 | 9.6412 | 9.28 | 7.8412 | 7.2667 | 6.9391 | 13.7468 | 13.6009 | 13.4488 | 13.2621 | 13.0631 | 12.857 | 12.6009 | 12.3754 | 12.1907 | 10.7846 | 9.255 | 6.9213 | 13.13 | 12.9055 | 12.6698 | 12.383 | 12.0555 | 11.6442 | 11.1555 | 10.7361 | 10.3851 | 8.8963 | 8.1749 | 7.7106
|  | RIVERSIDE PRIMARY | HT |  |  |  |  | 12.2616 | 12.0708 | 11.8616 | 11.6126 | 11.3524 | 11.0034 | 10.6034 | 10.2442 | 9.8687 | 8.0391 | 7.1147 | 6.6891 | 13.8448 | 13.7458 | 13.6335 | 13.4988 | 13.3631 | 13.208 | 13.0243 | 12.8825 | 12.7213 | 11.8499 | 11.2233 | 10.8825 | 13.2483 | 13.083 | 12.8902 | 12.6585 | 12.4198 | 12.0789 | 11.6738 | 11.3218 | 10.9483 | 9.031 | 7.98 | 7.4249
|  | RIVERSIDE PRIMARY | HE |  |  |  |  | 12.2524 | 12.0596 | 11.8453 | 11.5932 | 11.3106 | 10.9422 | 10.5136 | 10.1218 | 9.7034 | 7.7596 | 6.9085 | 6.5575 | 13.8192 | 13.7019 | 13.5723 | 13.4182 | 13.2641 | 13.0784 | 12.8652 | 12.6835 | 12.4805 | 11.1019 | 9.5376 | 7.3692 | 13.2422 | 13.0728 | 12.8728 | 12.6361 | 12.3851 | 12.0177 | 11.5881 | 11.2044 | 10.7922 | 8.8136 | 7.834 | 7.4014
|  | RIVERSIDE PRIMARY | CF |  |  |  |  | 12.4024 | 12.2708 | 12.1391 | 11.98 | 11.8147 | 11.6493 | 11.4422 | 11.2565 | 11.0453 | 9.5606 | 8.133 | 7.0116 | 13.8825 | 13.7846 | 13.6886 | 13.5743 | 13.4448 | 13.3223 | 13.1641 | 13.0223 | 12.8672 | 11.4478 | 8.8519 | 4.358 | 13.3575 | 13.2463 | 13.1381 | 13.0024 | 12.8493 | 12.6942 | 12.4963 | 12.3177 | 12.1208 | 10.7004 | 9.2626 | 8.1096
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE PRIMARY | MINIMUM HEADROOM | SU 11617 17810 | YES | NO | 0.037 | 2.3078 | 2.2486 | 2.2047 | 2.1435 | 2.0649 | 1.969 | 1.9047 | 1.8016 | 1.7516 | 1.521 | 1.4384 | 1.3618 | 2.9104 | 2.8635 | 2.8298 | 2.7839 | 2.7247 | 2.6512 | 2.6053 | 2.5257 | 2.488 | 2.3022 | 2.0339 | 1.4084 | 2.3778 | 2.3135 | 2.2696 | 2.2114 | 2.1349 | 2.0431 | 1.9829 | 1.8808 | 1.838 | 1.6369 | 1.5635 | 1.4982
|  | ROCKBOURNE PRIMARY | EE |  |  |  |  | 2.3078 | 2.2486 | 2.2047 | 2.1435 | 2.0649 | 1.969 | 1.9047 | 1.8016 | 1.7516 | 1.521 | 1.4384 | 1.3976 | 2.9104 | 2.8635 | 2.8298 | 2.7839 | 2.7247 | 2.6512 | 2.6053 | 2.5257 | 2.488 | 2.3022 | 2.138 | 1.8369 | 2.3778 | 2.3135 | 2.2696 | 2.2114 | 2.1349 | 2.0431 | 1.9829 | 1.8808 | 1.838 | 1.6369 | 1.5635 | 1.5298
|  | ROCKBOURNE PRIMARY | HT |  |  |  |  | 2.3302 | 2.2955 | 2.2578 | 2.2108 | 2.172 | 2.1078 | 2.0394 | 1.9608 | 1.8751 | 1.5669 | 1.4435 | 1.3618 | 2.942 | 2.9216 | 2.8951 | 2.8604 | 2.839 | 2.7941 | 2.7451 | 2.691 | 2.6308 | 2.4431 | 2.3747 | 2.3298 | 2.4073 | 2.3757 | 2.3369 | 2.288 | 2.2543 | 2.188 | 2.1227 | 2.042 | 1.9614 | 1.6747 | 1.5655 | 1.4982
|  | ROCKBOURNE PRIMARY | HE |  |  |  |  | 2.3343 | 2.3006 | 2.2618 | 2.2159 | 2.1802 | 2.1159 | 2.0516 | 1.9771 | 1.8914 | 1.5639 | 1.4822 | 1.4506 | 2.938 | 2.9165 | 2.8859 | 2.8502 | 2.8257 | 2.7767 | 2.7278 | 2.6665 | 2.6012 | 2.3359 | 2.1665 | 1.8696 | 2.4094 | 2.3778 | 2.341 | 2.2931 | 2.2614 | 2.1992 | 2.1339 | 2.0573 | 1.9778 | 1.6788 | 1.6084 | 1.5798
|  | ROCKBOURNE PRIMARY | CF |  |  |  |  | 2.3516 | 2.3241 | 2.2873 | 2.2578 | 2.22 | 2.1771 | 2.1455 | 2.0965 | 2.0506 | 1.7873 | 1.6108 | 1.4884 | 2.9543 | 2.9308 | 2.9012 | 2.8788 | 2.8431 | 2.8022 | 2.7767 | 2.7227 | 2.6798 | 2.3971 | 2.0339 | 1.4084 | 2.4288 | 2.4022 | 2.3655 | 2.3359 | 2.2971 | 2.2522 | 2.2257 | 2.1747 | 2.1288 | 1.8808 | 1.7196 | 1.6124
NURSLING GSP | ROWNHAMS BSP | ROMSEY PRIMARY | MINIMUM HEADROOM | SU 36092 21110 | NO | YES | 5.063 | -2.7694 | 21.8786 | 21.4786 | 21.0929 | 20.5694 | 19.8429 | 19.0265 | 17.998 | 17.0051 | 11.8388 | 8.848 | 7.1133 | 1.9163 | 24.899 | 24.6163 | 24.3643 | 24.0051 | 23.5378 | 22.999 | 22.2969 | 21.7071 | 18.398 | 15.7398 | 9.0653 | -2.0663 | 21.749 | 21.2724 | 20.949 | 20.3214 | 19.3602 | 18.3214 | 17.2816 | 16.4173 | 11.9776 | 9.3857 | 7.9592
|  | ROMSEY PRIMARY | EE |  |  |  |  | -2.7663 | 21.8786 | 21.4786 | 21.0929 | 20.5694 | 19.8429 | 19.0265 | 17.998 | 17.0051 | 11.9592 | 9.3663 | 7.4418 | 1.9643 | 24.899 | 24.6163 | 24.3643 | 24.0051 | 23.5378 | 22.999 | 22.2969 | 21.7071 | 18.398 | 15.8827 | 12.3214 | -2.0663 | 21.749 | 21.2724 | 20.949 | 20.3214 | 19.3602 | 18.3214 | 17.2816 | 16.4173 | 12.0398 | 9.8714 | 8.25
|  | ROMSEY PRIMARY | HT |  |  |  |  | -2.7694 | 22.1622 | 21.8367 | 21.4449 | 20.9959 | 20.3408 | 19.7459 | 18.6602 | 17.45 | 11.8388 | 8.848 | 7.1133 | 1.9163 | 25.1378 | 24.9245 | 24.6622 | 24.3663 | 23.9633 | 23.6112 | 23.1429 | 22.5347 | 19.7214 | 18.402 | 17.6551 | -2.0653 | 22.002 | 21.6235 | 21.1276 | 20.5592 | 19.6265 | 18.9806 | 18.0204 | 16.9469 | 11.9776 | 9.3857 | 7.9592
|  | ROMSEY PRIMARY | HE |  |  |  |  | -2.5561 | 22.1571 | 21.8367 | 21.4041 | 20.9245 | 20.2612 | 19.65 | 18.8898 | 18.0551 | 12.8776 | 10.2714 | 9.048 | 2.1286 | 25.1173 | 24.901 | 24.6102 | 24.2867 | 23.8612 | 23.4765 | 22.9755 | 22.451 | 18.9306 | 16.3184 | 13.0449 | -1.8327 | 22.0643 | 21.7327 | 21.2184 | 20.6561 | 19.8092 | 19.249 | 18.3816 | 17.5031 | 12.9439 | 10.7327 | 9.7265
|  | ROMSEY PRIMARY | CF |  |  |  |  | -2.3143 | 22.7673 | 22.3796 | 22.1214 | 21.8173 | 21.4214 | 20.9571 | 20.5806 | 20.0653 | 16.9765 | 13.7939 | 11.1755 | 2.2908 | 25.601 | 25.252 | 25.0704 | 24.8602 | 24.5949 | 24.2745 | 23.9939 | 23.4633 | 20.2735 | 15.7398 | 9.0653 | -1.6163 | 22.6418 | 22.2378 | 21.9398 | 21.5643 | 21.0612 | 20.498 | 20.2102 | 19.6429 | 16.5724 | 13.7214 | 11.4735
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ROSE GREEN PRIMARY | MINIMUM HEADROOM | SZ 89974 99335 | NO | YES | 7.872 | 9.5268 | 9.1503 | 8.6034 | 8.0707 | 7.6238 | 7.0319 | 5.9493 | 4.8574 | 3.7534 | -2.1293 | -5.8732 | -7.5885 | 8.4156 | 7.937 | 7.5238 | 6.9074 | 6.3472 | 5.6003 | 4.8136 | 3.988 | 3.336 | -0.41093 | -4.5344 | -12.8375 | 7.6544 | 6.8982 | 6.0646 | 5.0227 | 4.3574 | 3.3278 | 2.1901 | 0.9258 | 0.037024 | -5.1711 | -8.4191 | -9.913
|  | ROSE GREEN PRIMARY | EE |  |  |  |  | 9.5666 | 9.2227 | 8.9207 | 8.485 | 7.9197 | 7.3595 | 6.7329 | 5.536 | 4.5023 | -1.2109 | -5.1711 | -7.2426 | 8.4156 | 7.937 | 7.6401 | 7.0646 | 6.3472 | 5.6003 | 4.8136 | 3.988 | 3.336 | -0.41093 | -4.0477 | -8.4936 | 7.6544 | 6.8982 | 6.5217 | 5.6421 | 4.5431 | 3.4003 | 2.1901 | 0.9258 | 0.037024 | -4.4977 | -7.7579 | -9.5885
|  | ROSE GREEN PRIMARY | HT |  |  |  |  | 9.5268 | 9.1503 | 8.6034 | 8.0707 | 7.6238 | 7.0319 | 5.9493 | 4.8574 | 3.7534 | -2.1293 | -5.8732 | -7.5885 | 8.5401 | 8.1227 | 7.5238 | 6.9074 | 6.4911 | 5.9003 | 5.3136 | 4.7074 | 4.0921 | 0.98907 | -0.80175 | -1.6232 | 7.7789 | 7.0768 | 6.0646 | 5.0227 | 4.3574 | 3.3278 | 2.3023 | 1.2503 | 0.17682 | -5.1711 | -8.4191 | -9.913
|  | ROSE GREEN PRIMARY | HE |  |  |  |  | 9.6738 | 9.3819 | 8.9952 | 8.5727 | 8.134 | 7.6289 | 7.1411 | 6.2207 | 5.2329 | -0.36196 | -4.4242 | -5.9895 | 8.5993 | 8.2197 | 7.7299 | 7.1738 | 6.7248 | 6.0829 | 5.4431 | 4.7513 | 4.0574 | 0.047229 | -3.6364 | -7.8313 | 7.986 | 7.4278 | 6.6738 | 5.8268 | 5.236 | 4.2952 | 3.3595 | 2.3605 | 1.3738 | -3.5895 | -6.816 | -8.0854
|  | ROSE GREEN PRIMARY | CF |  |  |  |  | 9.9595 | 9.7391 | 9.6564 | 9.5523 | 9.4401 | 9.3207 | 9.2044 | 8.9023 | 8.5748 | 5.7778 | -0.12624 | -3.0466 | 8.8574 | 8.538 | 8.3431 | 8.088 | 7.7993 | 7.4687 | 7.2931 | 6.787 | 6.2442 | 1.8921 | -4.5344 | -12.8375 | 8.4411 | 8.0136 | 7.787 | 7.4891 | 7.1727 | 6.8636 | 6.9136 | 6.3768 | 5.8064 | 1.1768 | -3.7742 | -5.9834
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | ROSE HILL PRIMARY | MINIMUM HEADROOM | SP 53637 03027 | NO | NO | 28.21 | -9.7984 | 15.1996 | 14.5751 | 14.3282 | 13.5598 | 11.4863 | 9.7639 | 8.1812 | 6.9731 | 2.5843 | 0.17307 | -0.96672 | -6.6647 | 17.27 | 16.8098 | 16.6088 | 15.9537 | 14.6823 | 13.4894 | 12.2955 | 11.3006 | 6.6874 | 0.87307 | -10.3473 | -9.3065 | 14.9384 | 14.3945 | 14.1914 | 13.4782 | 11.7098 | 10.1833 | 8.7527 | 7.6588 | 3.7761 | 1.8343 | 1.02
|  | ROSE HILL PRIMARY | EE |  |  |  |  | -9.7677 | 15.1996 | 14.5751 | 14.3282 | 13.5598 | 11.4863 | 9.7639 | 8.1812 | 6.9731 | 2.5843 | 0.31899 | -0.34019 | -6.6647 | 17.27 | 16.8098 | 16.6088 | 15.9537 | 14.6823 | 13.4894 | 12.2955 | 11.3006 | 6.6874 | 3.0078 | -2.4075 | -9.3065 | 14.9384 | 14.3945 | 14.1914 | 13.4782 | 11.7098 | 10.1833 | 8.7527 | 7.6588 | 3.7761 | 1.9465 | 1.5435
|  | ROSE HILL PRIMARY | HT |  |  |  |  | -9.7984 | 15.4374 | 15.0874 | 14.4486 | 13.7333 | 11.518 | 10.2445 | 8.8129 | 7.4567 | 2.9159 | 0.17307 | -0.96672 | -6.5024 | 17.6884 | 17.4833 | 16.9945 | 16.4302 | 15.2547 | 14.371 | 13.2976 | 12.2802 | 9.3588 | 7.8608 | 7.1496 | -9.2514 | 15.2108 | 14.8884 | 14.2833 | 13.6047 | 11.8078 | 10.6659 | 9.3598 | 8.1241 | 4.1272 | 1.8343 | 1.02
|  | ROSE HILL PRIMARY | HE |  |  |  |  | -9.4769 | 15.618 | 15.2088 | 14.7792 | 14.1353 | 12.1782 | 11.0088 | 9.6945 | 8.4557 | 3.8608 | 1.5904 | 0.36797 | -6.4514 | 17.5925 | 17.2741 | 16.9118 | 16.3292 | 15.1404 | 14.3221 | 13.2731 | 12.2027 | 7.2823 | 3.5139 | -2.031 | -9.0188 | 15.3455 | 14.9802 | 14.5802 | 13.9741 | 12.3292 | 11.3516 | 10.1823 | 9.0557 | 4.9292 | 3.0894 | 2.1955
|  | ROSE HILL PRIMARY | CF |  |  |  |  | -9.0708 | 16.4016 | 16.2353 | 16.0894 | 15.8884 | 15.2067 | 14.2904 | 13.5384 | 12.471 | 6.3476 | 3.1312 | 0.43226 | -6.2657 | 17.9547 | 17.7251 | 17.4833 | 17.169 | 16.5302 | 15.7139 | 15.0108 | 14.0394 | 7.368 | 0.87307 | -10.3473 | -8.6688 | 16.0057 | 15.8476 | 15.7037 | 15.5129 | 14.9323 | 14.1496 | 13.5292 | 12.6149 | 7.2006 | 4.4874 | 2.2547
MELKSHAM GSP | CHIPPENHAM BSP | ROWDEN PRIMARY | MINIMUM HEADROOM | ST 90805 72608 | NO | YES | 10.667 | -1.231 | -2.6412 | -3.4259 | -4.5493 | -6.2687 | -7.9096 | 0.15269 | -1.8269 | -3.4636 | -11.9269 | -17.3391 | -19.5565 | 2.7629 | 1.6711 | 1.1782 | 0.4231 | -0.86771 | -1.983 | 6.5711 | 5.2721 | 4.2802 | -0.5769 | -5.0555 | -14.5626 | -0.55751 | -1.8238 | -2.4993 | -3.4596 | -5.0198 | -6.5014 | 8.1823 | 6.416 | 5.0333 | -2.0606 | -6.7116 | -8.5953
|  | ROWDEN PRIMARY | EE |  |  |  |  | -1.231 | -2.6412 | -3.4259 | -4.5493 | -6.2687 | -7.9096 | 0.15269 | -1.8269 | -3.4636 | -11.5861 | -16.6208 | -19.1861 | 2.7629 | 1.6711 | 1.1782 | 0.4231 | -0.86771 | -1.983 | 6.5711 | 5.2721 | 4.2802 | -0.5769 | -4.7667 | -9.7779 | -0.55751 | -1.8238 | -2.4993 | -3.4596 | -5.0198 | -6.5014 | 8.1823 | 6.416 | 5.0333 | -1.7932 | -6.1055 | -8.3044
|  | ROWDEN PRIMARY | HT |  |  |  |  | -0.94016 | -2.2024 | -3.231 | -4.2555 | -5.6993 | -7.3636 | 0.67922 | -1.2453 | -2.9779 | -11.9269 | -17.3391 | -19.5565 | 3.1456 | 2.2517 | 1.62 | 1.0415 | 0.09351 | -0.8922 | 7.8231 | 6.7364 | 5.7925 | 1.3527 | -1.0749 | -2.0075 | -0.29424 | -1.434 | -2.3259 | -3.1993 | -4.5116 | -5.9912 | 8.7374 | 7.0711 | 5.5853 | -2.0606 | -6.7116 | -8.5953
|  | ROWDEN PRIMARY | HE |  |  |  |  | -0.91465 | -2.1575 | -3.1647 | -4.2157 | -5.5218 | -6.9116 | 1.4088 | -0.34935 | -2.0249 | -10.4432 | -15.6381 | -17.3136 | 3.0588 | 2.118 | 1.4404 | 0.75882 | -0.16057 | -1.0912 | 7.666 | 6.5384 | 5.4547 | -0.0085306 | -4.432 | -9.1014 | -0.27486 | -1.3983 | -2.2749 | -3.1769 | -4.3616 | -5.5973 | 9.3762 | 7.8558 | 6.4098 | -0.80139 | -5.2504 | -6.6626
|  | ROWDEN PRIMARY | CF |  |  |  |  | -0.54527 | -1.6259 | -2.3616 | -3.1504 | -5.4565 | -5.7534 | 3.4568 | 2.8772 | 2.2945 | -3.2269 | -10.4238 | -13.9657 | 3.2333 | 2.3558 | 1.8078 | 1.2425 | -0.66261 | -0.94322 | 8.2435 | 7.669 | 7.067 | 2.2435 | -5.0555 | -14.5626 | 0.062898 | -0.90751 | -1.5453 | -2.2055 | -4.3289 | -4.5677 | 11.2068 | 10.7088 | 10.2129 | 5.4976 | -0.55343 | -3.7106
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ROWNER PARK PRIMARY | MINIMUM HEADROOM | SU 58018 00782 | NO | YES | 0.296 | 17.9331 | 17.6045 | 17.1943 | 16.7361 | 16.6841 | 16.0586 | 15.3382 | 14.6259 | 14.1218 | 11.6892 | 9.7096 | 8.582 | 19.2169 | 18.9333 | 18.5894 | 18.1914 | 18.0986 | 17.62 | 17.0639 | 16.4996 | 16.0884 | 13.8476 | 10.1394 | 2.1037 | 18.0461 | 17.7298 | 17.341 | 16.9033 | 16.8451 | 16.2543 | 15.5716 | 14.8951 | 14.4267 | 12.2237 | 10.4482 | 9.5033
|  | ROWNER PARK PRIMARY | EE |  |  |  |  | 17.9331 | 17.6045 | 17.1943 | 16.7361 | 16.6841 | 16.0586 | 15.3382 | 14.6259 | 14.1218 | 11.6892 | 9.9994 | 8.6137 | 19.2169 | 18.9333 | 18.5894 | 18.1914 | 18.0986 | 17.62 | 17.0639 | 16.4996 | 16.0884 | 13.8476 | 11.2812 | 7.1822 | 18.0461 | 17.7298 | 17.341 | 16.9033 | 16.8451 | 16.2543 | 15.5716 | 14.8951 | 14.4267 | 12.2237 | 10.7053 | 9.5257
|  | ROWNER PARK PRIMARY | HT |  |  |  |  | 18.2229 | 17.9933 | 17.7106 | 17.4494 | 17.1106 | 16.5545 | 15.9269 | 15.7055 | 15.1014 | 11.7882 | 9.7096 | 8.582 | 19.5251 | 19.3659 | 19.172 | 18.9904 | 18.7496 | 18.4118 | 18.0169 | 17.9506 | 17.5741 | 15.6976 | 14.6771 | 14.2251 | 18.3339 | 18.1145 | 17.8471 | 17.5971 | 17.2716 | 16.7502 | 16.1584 | 15.9737 | 15.4033 | 12.3471 | 10.4482 | 9.5033
|  | ROWNER PARK PRIMARY | HE |  |  |  |  | 18.1953 | 17.9606 | 17.6749 | 17.4076 | 17.0627 | 16.5463 | 15.9463 | 15.7463 | 15.1708 | 12.2024 | 10.2494 | 9.4933 | 19.4251 | 19.22 | 18.971 | 18.72 | 18.4078 | 18.0037 | 17.5261 | 17.3557 | 16.8741 | 14.0741 | 11.2629 | 7.4047 | 18.3033 | 18.0808 | 17.8084 | 17.5502 | 17.2216 | 16.7349 | 16.1686 | 15.9992 | 15.4522 | 12.689 | 10.9124 | 10.2992
|  | ROWNER PARK PRIMARY | CF |  |  |  |  | 18.4157 | 18.2535 | 18.1198 | 17.931 | 17.7188 | 17.5514 | 17.2729 | 16.9698 | 16.6494 | 15.0402 | 13.0596 | 11.3718 | 19.5414 | 19.3618 | 19.1955 | 18.972 | 18.7057 | 18.4363 | 18.0731 | 17.6761 | 17.2506 | 14.7027 | 10.1394 | 2.1037 | 18.5104 | 18.3604 | 18.2339 | 18.0563 | 17.8563 | 17.6931 | 17.4267 | 17.1369 | 16.8318 | 15.29 | 13.4686 | 11.9196
FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE PRIMARY | MINIMUM HEADROOM | SZ 59554 91973 | NO | YES | 4.711 | 7.528 | 6.4494 | 5.7218 | 4.5769 | 3.4208 | 1.8627 | 0.10245 | -1.7006 | -3.1027 | -10.569 | -16.4782 | -19.8445 | 10.6249 | 9.9127 | 9.4484 | 8.63 | 7.7729 | 6.7147 | 5.482 | 4.2137 | 3.2382 | -2.0976 | -7.2098 | -21.2333 | 8.0984 | 7.1208 | 6.4943 | 5.4484 | 4.3739 | 2.9422 | 1.3198 | -0.34041 | -1.6027 | -8.0761 | -13.3088 | -16.0373
|  | RYDE PRIMARY | EE |  |  |  |  | 7.528 | 6.4494 | 5.7218 | 4.5769 | 3.4208 | 1.8627 | 0.10245 | -1.7006 | -3.1027 | -10.4333 | -15.1547 | -19.1608 | 10.6249 | 9.9127 | 9.4484 | 8.63 | 7.7729 | 6.7147 | 5.482 | 4.2137 | 3.2382 | -2.0976 | -7.1424 | -14.7414 | 8.0984 | 7.1208 | 6.4943 | 5.4484 | 4.3739 | 2.9422 | 1.3198 | -0.34041 | -1.6027 | -8.0608 | -12.1373 | -15.4761
|  | RYDE PRIMARY | HT |  |  |  |  | 7.9504 | 7.0851 | 6.1412 | 5.0922 | 4.4076 | 2.9596 | 1.3851 | -0.25265 | -1.8955 | -10.569 | -16.4782 | -19.8445 | 11.0698 | 10.5933 | 10.0565 | 9.4718 | 9.1473 | 8.3708 | 7.4892 | 6.5627 | 5.6147 | 0.88408 | -1.9894 | -3.368 | 8.5657 | 7.7973 | 6.9402 | 5.9973 | 5.4096 | 4.1178 | 2.6984 | 1.2229 | -0.26898 | -8.0761 | -13.3088 | -16.0373
|  | RYDE PRIMARY | HE |  |  |  |  | 8.0024 | 7.2035 | 6.3269 | 5.3718 | 4.8004 | 3.6402 | 2.3351 | 0.94531 | -0.45265 | -7.9557 | -12.7904 | -15.0924 | 10.9749 | 10.4524 | 9.8729 | 9.23 | 8.8463 | 8.0922 | 7.2024 | 6.2331 | 5.2218 | -0.58122 | -5.8384 | -12.7853 | 8.6035 | 7.8922 | 7.0973 | 6.2382 | 5.7473 | 4.7045 | 3.5218 | 2.2667 | 0.99633 | -5.719 | -9.8537 | -11.6996
|  | RYDE PRIMARY | CF |  |  |  |  | 8.5616 | 8.0157 | 7.482 | 6.8831 | 6.3086 | 6.128 | 5.5412 | 4.9249 | 4.3055 | -1.272 | -6.1404 | -10.619 | 11.2402 | 10.8127 | 10.3892 | 9.8871 | 9.3443 | 9.0208 | 8.379 | 7.6994 | 6.9555 | 1.0678 | -7.2098 | -21.2333 | 9.1065 | 8.6178 | 8.1392 | 7.6035 | 7.0831 | 6.9494 | 6.4167 | 5.8504 | 5.2759 | 0.28204 | -4.0976 | -8.0455
MANNINGTON GSP | SALISBURY BSP | SALISBURY CENTRAL PRIMARY | MINIMUM HEADROOM | SU 14215 30481 | NO | NO | 13.114 | 21.3412 | 20.8034 | 20.3401 | 19.2034 | 18.1544 | 16.6769 | 14.884 | 13.0075 | 11.4575 | 5.6799 | 1.8473 | 0.75647 | 24.2024 | 23.681 | 23.2861 | 22.2942 | 21.4554 | 20.4014 | 19.084 | 17.7259 | 16.6095 | 11.681 | 6.581 | -6.815 | 21.133 | 20.483 | 20.0197 | 18.835 | 17.8585 | 16.481 | 14.7738 | 13.0126 | 11.5748 | 6.235 | 2.9422 | 2.0554
|  | SALISBURY CENTRAL PRIMARY | EE |  |  |  |  | 21.3412 | 20.8034 | 20.3401 | 19.2034 | 18.1544 | 16.6769 | 14.884 | 13.0075 | 11.4575 | 5.6799 | 2.7401 | 1.8932 | 24.2024 | 23.681 | 23.2861 | 22.2942 | 21.4554 | 20.4014 | 19.084 | 17.7259 | 16.6095 | 11.681 | 7.3718 | 1.032 | 21.133 | 20.483 | 20.0197 | 18.835 | 17.8585 | 16.481 | 14.7738 | 13.0126 | 11.5748 | 6.235 | 3.6983 | 2.9912
|  | SALISBURY CENTRAL PRIMARY | HT |  |  |  |  | 21.5738 | 21.3248 | 20.6993 | 19.7177 | 19.1208 | 17.6473 | 16.0014 | 14.3514 | 12.8626 | 5.7228 | 1.8473 | 0.75647 | 24.6565 | 24.3728 | 23.8728 | 23.2044 | 22.8228 | 21.9748 | 20.9401 | 19.8983 | 18.9401 | 14.7361 | 12.6605 | 12.033 | 21.5361 | 21.134 | 20.4105 | 19.4585 | 18.9034 | 17.5616 | 15.984 | 14.4208 | 12.9901 | 6.3901 | 2.9422 | 2.0554
|  | SALISBURY CENTRAL PRIMARY | HE |  |  |  |  | 21.5963 | 21.3646 | 20.932 | 19.9687 | 19.4891 | 18.4197 | 17.1299 | 15.7524 | 14.3595 | 8.4616 | 5.7085 | 4.7075 | 24.5422 | 24.1993 | 23.6708 | 22.8105 | 22.4259 | 21.6748 | 20.7238 | 19.7187 | 18.6718 | 13.4014 | 8.9922 | 2.6503 | 21.5738 | 21.2248 | 20.6034 | 19.5891 | 19.181 | 18.1963 | 16.9697 | 15.682 | 14.3605 | 8.8605 | 6.4738 | 5.6656
|  | SALISBURY CENTRAL PRIMARY | CF |  |  |  |  | 21.831 | 21.685 | 21.4616 | 20.9748 | 20.5534 | 20.434 | 20.0708 | 19.5412 | 18.8932 | 13.5718 | 9.5646 | 5.8269 | 24.7299 | 24.4381 | 24.0626 | 23.3983 | 22.785 | 22.482 | 21.8146 | 21.1003 | 20.331 | 14.3891 | 6.581 | -6.815 | 21.9044 | 21.7503 | 21.4238 | 20.7973 | 20.2952 | 20.2014 | 19.6687 | 19.0779 | 18.4442 | 13.4442 | 9.8442 | 6.5738
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | SANDHURST PRIMARY | MINIMUM HEADROOM | SU 83597 60930 | NO | NO | 2.631 | 6.9806 | 6.6796 | 5.95 | 5.1296 | 4.2541 | 2.7571 | 1.0765 | -0.60408 | -1.7551 | -8.5153 | -13.7653 | -16.8082 | 10.4602 | 10.2204 | 9.6112 | 8.9296 | 8.1878 | 7.1388 | 5.9327 | 4.7061 | 3.8857 | -0.75408 | -7.5388 | -22.6173 | 7.05 | 6.7888 | 6.0827 | 5.3 | 4.4602 | 3.0622 | 1.4847 | -0.092857 | -1.1408 | -6.95 | -11.5163 | -14.1459
|  | SANDHURST PRIMARY | EE |  |  |  |  | 6.9806 | 6.6796 | 5.95 | 5.1296 | 4.2541 | 2.7571 | 1.0765 | -0.60408 | -1.7551 | -7.9378 | -12.6857 | -16.3327 | 10.4602 | 10.2204 | 9.6112 | 8.9296 | 8.1878 | 7.1388 | 5.9327 | 4.7061 | 3.8857 | -0.75408 | -6.048 | -13.9786 | 7.05 | 6.7888 | 6.0827 | 5.3 | 4.4602 | 3.0622 | 1.4847 | -0.092857 | -1.1408 | -6.498 | -10.5888 | -13.7643
|  | SANDHURST PRIMARY | HT |  |  |  |  | 7.5163 | 6.9122 | 6.599 | 5.9776 | 5.3061 | 3.9653 | 2.5184 | 1.0122 | -0.52449 | -8.5153 | -13.7653 | -16.8082 | 11.0949 | 10.6878 | 10.5622 | 10.1561 | 9.7061 | 8.9857 | 8.1776 | 7.3214 | 6.4316 | 2.2459 | -0.085714 | -1.3704 | 7.6347 | 7.0459 | 6.8071 | 6.2173 | 5.5755 | 4.3673 | 3.051 | 1.6714 | 0.25612 | -6.95 | -11.5163 | -14.1459
|  | SANDHURST PRIMARY | HE |  |  |  |  | 7.55 | 6.9684 | 6.6949 | 6.1051 | 5.4643 | 4.3612 | 3.1378 | 1.8531 | 0.53061 | -6.5 | -11.4704 | -13.8633 | 10.948 | 10.4561 | 10.2408 | 9.7459 | 9.1847 | 8.401 | 7.501 | 6.5327 | 5.5051 | -0.22857 | -5.8112 | -13.2673 | 7.6571 | 7.0847 | 6.8765 | 6.3153 | 5.698 | 4.6878 | 3.549 | 2.348 | 1.1061 | -5.2378 | -9.598 | -11.5765
|  | SANDHURST PRIMARY | CF |  |  |  |  | 7.9867 | 7.6837 | 7.3031 | 7.2929 | 6.9449 | 6.5112 | 5.9827 | 5.399 | 4.7867 | 0.047959 | -4.952 | -9.5867 | 11.1296 | 10.7796 | 10.3571 | 10.2367 | 9.7694 | 9.201 | 8.5286 | 7.7949 | 7.0102 | 1.2622 | -7.5388 | -22.6173 | 8.0398 | 7.7327 | 7.3582 | 7.3765 | 7.0286 | 6.6143 | 6.1082 | 5.5459 | 4.9561 | 0.5051 | -3.9786 | -7.9357
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN PRIMARY | MINIMUM HEADROOM | SZ 59877 85052 | NO | YES | 4.043 | 0.61784 | 0.082122 | -0.53624 | -0.69747 | -1.276 | -2.1301 | -3.1148 | -4.1046 | -4.8393 | -8.4179 | -11.4781 | -13.0587 | 0.80661 | 0.40457 | -0.051551 | -0.24441 | -0.71788 | -1.3413 | -2.0679 | -2.7934 | -3.3373 | -6.1771 | -9.3046 | -16.9352 | -0.28318 | -0.80053 | -1.3873 | -1.5669 | -2.1301 | -2.9679 | -3.9281 | -4.875 | -5.5536 | -8.8526 | -11.6179 | -13.022
|  | SANDOWN PRIMARY | EE |  |  |  |  | 0.61784 | 0.082122 | -0.53624 | -0.69747 | -1.276 | -2.1301 | -3.1148 | -4.1046 | -4.8393 | -8.4179 | -10.8628 | -12.824 | 0.80661 | 0.40457 | -0.051551 | -0.24441 | -0.71788 | -1.3413 | -2.0679 | -2.7934 | -3.3373 | -6.1771 | -8.9567 | -13.0077 | -0.28318 | -0.80053 | -1.3873 | -1.5669 | -2.1301 | -2.9679 | -3.9281 | -4.875 | -5.5536 | -8.8526 | -11.0964 | -12.8311
|  | SANDOWN PRIMARY | HT |  |  |  |  | 1.0056 | 0.60253 | 0.226 | -0.20461 | -0.69849 | -1.5148 | -1.9067 | -2.7913 | -3.7097 | -8.4036 | -11.4781 | -13.0587 | 1.1658 | 0.91478 | 0.66171 | 0.37498 | 0.039265 | -0.44339 | -0.67298 | -1.1924 | -1.7413 | -4.4097 | -5.9964 | -6.7148 | 0.10151 | -0.27706 | -0.65053 | -1.0669 | -1.5434 | -2.3209 | -2.7301 | -3.5526 | -4.4056 | -8.7709 | -11.6179 | -13.022
|  | SANDOWN PRIMARY | HE |  |  |  |  | 0.98314 | 0.58824 | 0.20151 | -0.23216 | -0.72196 | -1.426 | -1.8209 | -2.5944 | -3.4189 | -7.6516 | -10.4393 | -11.7679 | 1.0719 | 0.7709 | 0.4658 | 0.11069 | -0.29441 | -0.8189 | -1.1128 | -1.6995 | -2.3301 | -5.8413 | -8.9567 | -12.6628 | 0.070898 | -0.30767 | -0.68522 | -1.1077 | -1.5873 | -2.274 | -2.623 | -3.3628 | -4.1383 | -8.1516 | -10.7434 | -11.776
|  | SANDOWN PRIMARY | CF |  |  |  |  | 1.2342 | 1.0076 | 0.71376 | 0.476 | 0.15967 | -0.18114 | -0.60053 | -0.59135 | -0.97706 | -3.6444 | -6.5413 | -9.0618 | 1.2127 | 1.0107 | 0.75457 | 0.50661 | 0.18212 | -0.19135 | -0.63114 | -0.81686 | -1.2709 | -4.4781 | -9.3046 | -16.9352 | 0.32192 | 0.11273 | -0.16278 | -0.39237 | -0.69033 | -1.0169 | -1.4118 | -1.424 | -1.7964 | -4.372 | -7.073 | -9.424
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | SELSEY PRIMARY | MINIMUM HEADROOM | SZ 85667 94289 | NO | YES | 0.431 | 5.3755 | 5.0816 | 4.6918 | 4.7041 | 4.3571 | 3.7898 | 3.1459 | 2.498 | 2.0724 | -0.6449 | -2.948 | -4.2724 | 5.8 | 5.5612 | 5.252 | 5.2357 | 4.9459 | 4.5388 | 4.0663 | 3.5878 | 3.2684 | 1.4418 | -0.93061 | -6.7663 | 4.9602 | 4.6765 | 4.302 | 4.3255 | 3.9918 | 3.4582 | 2.851 | 2.2388 | 1.85 | -0.59592 | -2.4765 | -3.551
|  | SELSEY PRIMARY | EE |  |  |  |  | 5.3755 | 5.0816 | 4.6918 | 4.7041 | 4.3571 | 3.7898 | 3.1459 | 2.498 | 2.0724 | -0.21633 | -2.398 | -4.0112 | 5.8 | 5.5612 | 5.252 | 5.2357 | 4.9459 | 4.5388 | 4.0663 | 3.5878 | 3.2684 | 1.4418 | -0.63163 | -3.7224 | 4.9602 | 4.6765 | 4.302 | 4.3255 | 3.9918 | 3.4582 | 2.851 | 2.2388 | 1.85 | -0.29388 | -2.0102 | -3.3439
|  | SELSEY PRIMARY | HT |  |  |  |  | 5.6102 | 5.3827 | 5.1316 | 4.8276 | 4.4898 | 3.9061 | 3.7347 | 3.1531 | 2.5439 | -0.6449 | -2.948 | -4.2724 | 6.0378 | 5.8939 | 5.7296 | 5.5245 | 5.2969 | 4.949 | 4.9184 | 4.5765 | 4.2153 | 2.5429 | 1.5918 | 1.0724 | 5.1959 | 4.9827 | 4.748 | 4.4582 | 4.1378 | 3.5949 | 3.4622 | 2.9031 | 2.3194 | -0.59592 | -2.4765 | -3.551
|  | SELSEY PRIMARY | HE |  |  |  |  | 5.6429 | 5.4398 | 5.2235 | 4.951 | 4.6541 | 4.1908 | 4.1296 | 3.6694 | 3.1888 | 0.71122 | -1.4143 | -2.4898 | 6.001 | 5.8398 | 5.6592 | 5.4286 | 5.1765 | 4.8316 | 4.7847 | 4.4316 | 4.05 | 1.9153 | -0.17143 | -3.0571 | 5.2245 | 5.0347 | 4.8296 | 4.5704 | 4.2847 | 3.85 | 3.8143 | 3.3837 | 2.9337 | 0.56327 | -1.1235 | -1.9847
|  | SELSEY PRIMARY | CF |  |  |  |  | 5.8204 | 5.698 | 5.5327 | 5.4041 | 5.2184 | 5.0153 | 4.7592 | 4.901 | 4.6806 | 2.998 | 1.2153 | -0.53776 | 6.0908 | 5.9643 | 5.798 | 5.6449 | 5.4316 | 5.1786 | 4.8806 | 4.8724 | 4.5776 | 2.4092 | -0.93061 | -6.7663 | 5.3908 | 5.2724 | 5.1112 | 4.9898 | 4.8112 | 4.6122 | 4.3673 | 4.5133 | 4.298 | 2.7092 | 1.0663 | -0.48163
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY PRIMARY | MINIMUM HEADROOM | ST 85605 23325 | NO | NO | 2.366 | 10.4245 | 9.9276 | 9.4347 | 9.0582 | 8.4143 | 7.75 | 7.0694 | 6.3908 | 5.9041 | 3.2939 | 1.1745 | -0.11735 | 12.6651 | 12.359 | 12.0335 | 11.8386 | 11.4376 | 11.0222 | 10.5794 | 10.1284 | 9.7886 | 7.8304 | 5.6049 | 0.036531 | 9.9678 | 9.5229 | 9.0473 | 8.8076 | 8.2331 | 7.6198 | 6.9657 | 6.3127 | 5.8729 | 3.6239 | 1.7861 | 0.73918
|  | SHAFTESBURY PRIMARY | EE |  |  |  |  | 10.4245 | 9.9276 | 9.4347 | 9.0582 | 8.4143 | 7.75 | 7.0694 | 6.3908 | 5.9041 | 3.298 | 1.5041 | 0.13878 | 12.6651 | 12.359 | 12.0335 | 11.8386 | 11.4376 | 11.0222 | 10.5794 | 10.1284 | 9.7886 | 7.8304 | 5.7967 | 2.8498 | 9.9678 | 9.5229 | 9.0473 | 8.8076 | 8.2331 | 7.6198 | 6.9657 | 6.3127 | 5.8729 | 3.6239 | 2.0943 | 0.95959
|  | SHAFTESBURY PRIMARY | HT |  |  |  |  | 10.6245 | 10.2061 | 9.8112 | 9.2531 | 8.6469 | 7.9959 | 7.7143 | 7.1194 | 6.501 | 3.2939 | 1.1745 | -0.11735 | 12.8784 | 12.6508 | 12.4273 | 12.1335 | 11.8008 | 11.459 | 11.3712 | 11.0457 | 10.71 | 9.0406 | 8.0284 | 7.4427 | 10.2218 | 9.8576 | 9.4892 | 9.0218 | 8.4882 | 7.8912 | 7.6994 | 7.1443 | 6.5667 | 3.6361 | 1.7861 | 0.73918
|  | SHAFTESBURY PRIMARY | HE |  |  |  |  | 10.651 | 10.2551 | 9.8612 | 9.3265 | 8.7459 | 8.1898 | 7.9939 | 7.4898 | 6.9745 | 4.1735 | 2.3857 | 1.5092 | 12.8324 | 12.5865 | 12.3294 | 12.011 | 11.6478 | 11.2896 | 11.1784 | 10.8314 | 10.4651 | 8.2937 | 6.2427 | 3.5039 | 10.2371 | 9.8973 | 9.5361 | 9.0902 | 8.58 | 8.0678 | 7.9473 | 7.4739 | 6.9851 | 4.4412 | 2.9331 | 2.228
|  | SHAFTESBURY PRIMARY | CF |  |  |  |  | 10.8469 | 10.552 | 10.2735 | 9.8337 | 9.4459 | 9.1541 | 8.8755 | 8.5745 | 8.6408 | 6.7959 | 4.8541 | 3.0224 | 12.9263 | 12.7233 | 12.5141 | 12.2141 | 11.9365 | 11.66 | 11.3773 | 11.0661 | 11.0171 | 8.909 | 5.6049 | 0.036531 | 10.4116 | 10.1535 | 9.8943 | 9.5106 | 9.1892 | 8.9106 | 8.629 | 8.3208 | 8.4627 | 6.7147 | 5.0024 | 3.4249
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET PRIMARY | MINIMUM HEADROOM | SZ 40828 88643 | NO | YES | 0.866 | 8.1357 | 7.9531 | 7.7163 | 7.5122 | 7.249 | 6.8878 | 6.8745 | 6.5408 | 6.3153 | 5.1653 | 4.5378 | 4.1255 | 8.9796 | 8.8551 | 8.6827 | 8.5255 | 8.3235 | 8.0633 | 8.0765 | 7.8327 | 7.6714 | 6.8051 | 5.7724 | 3.3408 | 8.2684 | 8.1214 | 7.9071 | 7.7214 | 7.4663 | 7.1255 | 7.1276 | 6.8122 | 6.6041 | 5.5541 | 5.0133 | 4.6673
|  | SHALFLEET PRIMARY | EE |  |  |  |  | 8.1357 | 7.9531 | 7.7163 | 7.5122 | 7.249 | 6.8878 | 6.8745 | 6.5408 | 6.3153 | 5.1653 | 4.6163 | 4.298 | 8.9796 | 8.8551 | 8.6827 | 8.5255 | 8.3235 | 8.0633 | 8.0765 | 7.8327 | 7.6714 | 6.8051 | 6.0071 | 4.8031 | 8.2684 | 8.1214 | 7.9071 | 7.7214 | 7.4663 | 7.1255 | 7.1276 | 6.8122 | 6.6041 | 5.5541 | 5.0837 | 4.8082
|  | SHALFLEET PRIMARY | HT |  |  |  |  | 8.2786 | 8.1224 | 7.9867 | 7.8031 | 7.5969 | 7.3541 | 7.0367 | 6.698 | 6.352 | 5.2786 | 4.5378 | 4.1255 | 9.1112 | 9.0163 | 8.9367 | 8.8255 | 8.6929 | 8.5561 | 8.3571 | 8.1449 | 7.9204 | 7.3704 | 6.9949 | 6.8082 | 8.3724 | 8.2398 | 8.1214 | 7.9735 | 7.7939 | 7.5714 | 7.2837 | 6.9786 | 6.651 | 5.6694 | 5.0133 | 4.6673
|  | SHALFLEET PRIMARY | HE |  |  |  |  | 8.2847 | 8.1347 | 8.0031 | 7.8306 | 7.6408 | 7.4235 | 7.1357 | 6.8337 | 6.5194 | 5.4673 | 4.9245 | 4.701 | 9.0939 | 8.9847 | 8.8959 | 8.7704 | 8.6296 | 8.4867 | 8.2806 | 8.0561 | 7.8184 | 7.0092 | 6.1918 | 5.0398 | 8.3776 | 8.25 | 8.1378 | 7.9969 | 7.8347 | 7.6378 | 7.3755 | 7.101 | 6.8031 | 5.8439 | 5.3724 | 5.1847
|  | SHALFLEET PRIMARY | CF |  |  |  |  | 8.3337 | 8.2367 | 8.1102 | 8.001 | 7.8582 | 7.698 | 7.5122 | 7.3714 | 7.1735 | 6.4898 | 5.6918 | 5.0112 | 9.1184 | 9.0429 | 8.9418 | 8.8561 | 8.7327 | 8.5898 | 8.4265 | 8.2867 | 8.102 | 7.2418 | 5.7724 | 3.3408 | 8.4204 | 8.3337 | 8.2255 | 8.1337 | 8.0143 | 7.8857 | 7.7286 | 7.598 | 7.4204 | 6.7776 | 6.0469 | 5.449
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN PRIMARY | MINIMUM HEADROOM | SZ 57809 81912 | NO | YES | 3.733 | 15.4663 | 15.0796 | 14.6184 | 14.4959 | 14.0153 | 13.1857 | 12.2551 | 11.3296 | 10.6429 | 6.6327 | 3.3133 | 1.4439 | 16.3276 | 16.0133 | 15.65 | 15.548 | 15.1531 | 14.602 | 13.9653 | 13.3122 | 12.8551 | 10.3704 | 7.9061 | 2.0102 | 14.9918 | 14.5602 | 14.0755 | 13.9582 | 13.4786 | 12.7071 | 11.8357 | 10.9571 | 10.3388 | 6.8367 | 4.0071 | 2.5194
|  | SHANKLIN PRIMARY | EE |  |  |  |  | 15.4663 | 15.0796 | 14.6184 | 14.4959 | 14.0153 | 13.1857 | 12.2551 | 11.3296 | 10.6429 | 6.9714 | 4.1296 | 1.8378 | 16.3276 | 16.0133 | 15.65 | 15.548 | 15.1531 | 14.602 | 13.9653 | 13.3122 | 12.8551 | 10.3704 | 7.9061 | 4.4133 | 14.9918 | 14.5602 | 14.0755 | 13.9582 | 13.4786 | 12.7071 | 11.8357 | 10.9571 | 10.3388 | 7.0786 | 4.7245 | 2.8551
|  | SHANKLIN PRIMARY | HT |  |  |  |  | 15.6561 | 15.3378 | 15.0347 | 14.6735 | 14.2561 | 13.7602 | 12.9612 | 12.1204 | 11.252 | 6.6327 | 3.3133 | 1.4439 | 16.5765 | 16.3673 | 16.1776 | 15.9367 | 15.6561 | 15.4837 | 15.0337 | 14.551 | 14.0449 | 11.5582 | 10.0459 | 9.298 | 15.2224 | 14.9316 | 14.6214 | 14.2378 | 13.801 | 13.401 | 12.6459 | 11.8602 | 11.0439 | 6.8367 | 4.0071 | 2.5194
|  | SHANKLIN PRIMARY | HE |  |  |  |  | 15.6939 | 15.4041 | 15.1276 | 14.801 | 14.4388 | 14.1122 | 13.498 | 12.852 | 12.1796 | 8.3929 | 5.5265 | 4.1327 | 16.5347 | 16.3082 | 16.0939 | 15.8255 | 15.5296 | 15.3694 | 14.952 | 14.4847 | 13.9867 | 11.1918 | 8.6694 | 5.5031 | 15.2541 | 14.9888 | 14.7051 | 14.3571 | 13.9745 | 13.7245 | 13.1214 | 12.5031 | 11.8582 | 8.4153 | 6.0571 | 4.9602
|  | SHANKLIN PRIMARY | CF |  |  |  |  | 15.9184 | 15.7724 | 15.5765 | 15.398 | 15.1684 | 14.9051 | 14.5918 | 14.6265 | 14.3439 | 12.0827 | 9.3622 | 6.7847 | 16.6337 | 16.4806 | 16.2857 | 16.0949 | 15.8388 | 15.5429 | 15.2 | 15.1265 | 14.7786 | 12.2163 | 8.349 | 2.0102 | 15.4541 | 15.3235 | 15.1316 | 14.9398 | 14.6939 | 14.4194 | 14.0939 | 14.1439 | 13.849 | 11.6918 | 9.2684 | 7.0173
AXMINSTER GSP | YEOVIL BSP | SHERBORNE PRIMARY | MINIMUM HEADROOM | ST 63978 18163 | NO | NO | 1.363 | 4.8753 | 4.7304 | 4.5876 | 4.309 | 3.9274 | 3.5947 | 2.9202 | 2.0713 | 1.2856 | -1.7981 | -4.0175 | -5.2083 | 7.1345 | 6.8958 | 6.6866 | 6.36 | 6.0233 | 5.9672 | 5.5233 | 5.0049 | 4.556 | 2.56 | 0.74984 | -3.2461 | 5.5631 | 5.2753 | 5.0304 | 4.6172 | 4.2192 | 4.0723 | 3.4539 | 2.7029 | 2.0651 | -0.49098 | -2.4706 | -3.4767
|  | SHERBORNE PRIMARY | EE |  |  |  |  | 4.8753 | 4.7304 | 4.5876 | 4.309 | 3.9274 | 3.5947 | 2.9202 | 2.0713 | 1.2856 | -1.7706 | -3.7267 | -5.0481 | 7.1345 | 6.8958 | 6.6866 | 6.36 | 6.0233 | 5.9672 | 5.5233 | 5.0049 | 4.556 | 2.56 | 0.74984 | -1.5185 | 5.5631 | 5.2753 | 5.0304 | 4.6172 | 4.2192 | 4.0723 | 3.4539 | 2.7029 | 2.0651 | -0.47567 | -2.2053 | -3.3349
|  | SHERBORNE PRIMARY | HT |  |  |  |  | 4.9682 | 4.8539 | 4.7427 | 4.4998 | 4.3264 | 3.8019 | 3.1651 | 2.3315 | 1.7621 | -1.7981 | -4.0175 | -5.2083 | 7.2631 | 7.158 | 7.0641 | 6.8233 | 6.657 | 6.3294 | 5.96 | 5.4968 | 5.3356 | 3.4662 | 2.3529 | 1.8641 | 5.7641 | 5.5549 | 5.3804 | 5.0304 | 4.81 | 4.2784 | 3.6947 | 2.9519 | 2.6529 | -0.49098 | -2.4706 | -3.4767
|  | SHERBORNE PRIMARY | HE |  |  |  |  | 4.9662 | 4.8509 | 4.7386 | 4.5468 | 4.3498 | 3.9509 | 3.3845 | 2.6151 | 2.1049 | -1.0032 | -2.8716 | -3.6451 | 7.2253 | 7.1009 | 6.9896 | 6.7723 | 6.5825 | 6.2519 | 5.8774 | 5.4049 | 5.1825 | 3.0437 | 1.2468 | -0.78384 | 5.7702 | 5.5692 | 5.409 | 5.106 | 4.8927 | 4.4182 | 3.8917 | 3.207 | 2.9651 | 0.23657 | -1.4063 | -2.0461
|  | SHERBORNE PRIMARY | CF |  |  |  |  | 5.0784 | 5.0182 | 4.959 | 4.8376 | 4.757 | 4.5733 | 4.3927 | 3.9029 | 3.3243 | 1.3253 | -0.4971 | -2.0716 | 7.2856 | 7.1937 | 7.107 | 6.9529 | 6.8009 | 6.5509 | 6.2958 | 5.9243 | 5.5049 | 3.6243 | 0.90086 | -3.2461 | 5.8753 | 5.7825 | 5.6876 | 5.4764 | 5.3253 | 5.0447 | 4.7958 | 4.3509 | 3.8417 | 2.2172 | 0.67433 | -0.71649
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE PRIMARY | MINIMUM HEADROOM | SP 03884 19102 | NO | NO | 0.26 | 2.421 | 2.3476 | 2.2506 | 2.1394 | 2.0527 | 1.9169 | 1.7527 | 1.6057 | 1.4669 | 0.77 | 0.49143 | 0.33122 | 3.2443 | 3.1902 | 3.1218 | 3.0341 | 2.9759 | 2.8708 | 2.7494 | 2.6606 | 2.5933 | 2.1484 | 1.8167 | 0.89327 | 2.6069 | 2.5355 | 2.4467 | 2.3386 | 2.2651 | 2.1263 | 1.9559 | 1.8018 | 1.6702 | 1.0212 | 0.75592 | 0.60694
|  | SHIPTON OLIFFE PRIMARY | EE |  |  |  |  | 2.421 | 2.3476 | 2.2506 | 2.1394 | 2.0527 | 1.9169 | 1.7527 | 1.6057 | 1.4669 | 0.9149 | 0.77918 | 0.73327 | 3.2443 | 3.1902 | 3.1218 | 3.0341 | 2.9759 | 2.8708 | 2.7494 | 2.6606 | 2.5933 | 2.2545 | 1.9627 | 1.5188 | 2.6069 | 2.5355 | 2.4467 | 2.3386 | 2.2651 | 2.1263 | 1.9559 | 1.8018 | 1.6702 | 1.158 | 1.0345 | 0.99265
|  | SHIPTON OLIFFE PRIMARY | HT |  |  |  |  | 2.4894 | 2.4271 | 2.3435 | 2.2802 | 2.1996 | 2.0884 | 1.9802 | 1.8424 | 1.6976 | 1.0098 | 0.71694 | 0.53735 | 3.3076 | 3.2667 | 3.2147 | 3.1739 | 3.1208 | 3.0494 | 2.9902 | 2.9076 | 2.8004 | 2.3167 | 2.1208 | 2.0014 | 2.6682 | 2.61 | 2.5376 | 2.4763 | 2.4029 | 2.2978 | 2.1947 | 2.0518 | 1.9008 | 1.2427 | 0.97429 | 0.81
|  | SHIPTON OLIFFE PRIMARY | HE |  |  |  |  | 2.4884 | 2.4261 | 2.3455 | 2.2822 | 2.1833 | 2.0639 | 1.9302 | 1.7731 | 1.6108 | 0.77 | 0.49143 | 0.33122 | 3.2973 | 3.2535 | 3.1984 | 3.1514 | 3.0922 | 3.0127 | 2.9504 | 2.8514 | 2.7249 | 2.1484 | 1.9463 | 1.5433 | 2.6671 | 2.61 | 2.5386 | 2.4773 | 2.3967 | 2.2773 | 2.1416 | 1.9794 | 1.811 | 1.0212 | 0.75592 | 0.60694
|  | SHIPTON OLIFFE PRIMARY | CF |  |  |  |  | 2.519 | 2.469 | 2.4129 | 2.3506 | 2.3088 | 2.2465 | 2.1669 | 2.0782 | 2.0271 | 1.4333 | 0.89143 | 0.50265 | 3.3178 | 3.279 | 3.232 | 3.1861 | 3.1473 | 3.0912 | 3.0178 | 2.9382 | 2.8871 | 2.4116 | 1.8167 | 0.89327 | 2.6967 | 2.6498 | 2.5978 | 2.5427 | 2.4998 | 2.4447 | 2.3692 | 2.2855 | 2.2335 | 1.6427 | 1.1304 | 0.76918
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | SHIRLEY PRIMARY | MINIMUM HEADROOM | SU 39988 13808 | NO | NO | 9.286 | 7.2724 | 6.6612 | 6.2888 | 5.6 | 4.8327 | 3.6561 | 2.3612 | 1.0786 | 0.097959 | -5.0796 | -9.6092 | -12.1745 | 6.9541 | 6.3776 | 6.0663 | 5.4194 | 4.6959 | 3.7745 | 2.7245 | 1.6602 | 0.83776 | -3.8653 | -11.0398 | -27.5541 | 6.4327 | 5.8061 | 5.5163 | 4.8347 | 4.0735 | 2.9663 | 1.7204 | 0.48776 | -0.41429 | -4.9 | -8.6714 | -10.7643
|  | SHIRLEY PRIMARY | EE |  |  |  |  | 7.2724 | 6.6612 | 6.2888 | 5.6 | 4.8327 | 3.6561 | 2.3612 | 1.0786 | 0.097959 | -5.0796 | -8.7469 | -11.7602 | 6.9541 | 6.3776 | 6.0663 | 5.4194 | 4.6959 | 3.7745 | 2.7245 | 1.6602 | 0.83776 | -3.8653 | -9.2214 | -17.8112 | 6.4327 | 5.8061 | 5.5163 | 4.8347 | 4.0735 | 2.9663 | 1.7204 | 0.48776 | -0.41429 | -4.9 | -7.9194 | -10.4429
|  | SHIRLEY PRIMARY | HT |  |  |  |  | 7.7337 | 7.2939 | 6.8265 | 6.2755 | 5.6786 | 5.0347 | 3.9867 | 2.8878 | 1.7204 | -4.8173 | -9.6092 | -12.1745 | 7.4816 | 7.1806 | 6.8459 | 6.4306 | 5.9673 | 5.7255 | 5.0827 | 4.402 | 3.6704 | -0.057143 | -2.399 | -3.5051 | 6.9316 | 6.4949 | 6.0653 | 5.5276 | 4.9347 | 4.4173 | 3.4439 | 2.4173 | 1.3296 | -4.5582 | -8.6714 | -10.7643
|  | SHIRLEY PRIMARY | HE |  |  |  |  | 7.7092 | 7.2908 | 6.851 | 6.3398 | 5.7439 | 5.1857 | 4.2663 | 3.3051 | 2.3133 | -3.1224 | -6.8571 | -8.4765 | 7.3469 | 6.9429 | 6.5337 | 6.0347 | 5.4582 | 5.0633 | 4.3122 | 3.5041 | 2.6378 | -2.6133 | -8.1735 | -16.2684 | 6.9153 | 6.502 | 6.0939 | 5.5929 | 5.0133 | 4.5786 | 3.7194 | 2.8194 | 1.8867 | -3.101 | -6.1633 | -7.4888
|  | SHIRLEY PRIMARY | CF |  |  |  |  | 8.0204 | 7.802 | 7.5296 | 7.2694 | 6.9459 | 6.5765 | 6.4316 | 5.9857 | 5.5194 | 2.1735 | -1.6184 | -5.1653 | 7.4806 | 7.1786 | 6.8153 | 6.4398 | 5.9469 | 5.3643 | 4.9776 | 4.2908 | 3.548 | -1.8816 | -11.0398 | -27.5541 | 7.1673 | 6.9398 | 6.6531 | 6.4041 | 6.0684 | 5.6918 | 5.6592 | 5.2184 | 4.7551 | 1.552 | -1.8214 | -4.848
MINETY GSP | STRATTON (RESERVE) BSP | SHRIVENHAM PRIMARY | MINIMUM HEADROOM | SU 23782 87902 | NO | NO | 0.238 | 7.1204 | 6.9337 | 6.7224 | 6.448 | 6.2092 | 5.8867 | 5.5276 | 5.1653 | 5.2235 | 4.2816 | 3.5602 | 3.1122 | 10.3418 | 10.2255 | 10.0837 | 9.901 | 9.7449 | 9.5235 | 9.2704 | 9.0071 | 9.1255 | 8.4163 | 7.599 | 5.6357 | 7.7265 | 7.5531 | 7.3449 | 7.0898 | 6.8755 | 6.5714 | 6.2265 | 5.8806 | 5.9867 | 5.1306 | 4.4888 | 4.1082
|  | SHRIVENHAM PRIMARY | EE |  |  |  |  | 7.1204 | 6.9337 | 6.7224 | 6.448 | 6.2092 | 5.8867 | 5.5276 | 5.1653 | 5.2724 | 4.2949 | 3.6684 | 3.2092 | 10.3418 | 10.2255 | 10.0837 | 9.901 | 9.7449 | 9.5235 | 9.2704 | 9.0071 | 9.1255 | 8.4163 | 7.7194 | 6.6857 | 7.7265 | 7.5531 | 7.3449 | 7.0898 | 6.8755 | 6.5714 | 6.2265 | 5.8806 | 6.0633 | 5.1378 | 4.5867 | 4.1908
|  | SHRIVENHAM PRIMARY | HT |  |  |  |  | 7.2133 | 7.052 | 6.8327 | 6.6357 | 6.4 | 6.1173 | 5.849 | 5.5388 | 5.2235 | 4.2816 | 3.5602 | 3.1122 | 10.4316 | 10.352 | 10.2235 | 10.1122 | 9.9724 | 9.8082 | 9.6633 | 9.4786 | 9.2827 | 8.7816 | 8.4918 | 8.3082 | 7.8102 | 7.6643 | 7.4643 | 7.2796 | 7.0653 | 6.8041 | 6.5653 | 6.2827 | 5.9867 | 5.1306 | 4.4888 | 4.1082
|  | SHRIVENHAM PRIMARY | HE |  |  |  |  | 7.2184 | 7.0663 | 6.8939 | 6.748 | 6.5214 | 6.2745 | 6.0418 | 5.7653 | 5.4816 | 4.551 | 3.9071 | 3.5776 | 10.4112 | 10.3184 | 10.2082 | 10.1133 | 9.9663 | 9.801 | 9.6439 | 9.4469 | 9.25 | 8.5378 | 7.8133 | 6.8255 | 7.8143 | 7.6765 | 7.5204 | 7.3827 | 7.1755 | 6.95 | 6.7398 | 6.4908 | 6.2347 | 5.3714 | 4.799 | 4.5173
|  | SHRIVENHAM PRIMARY | CF |  |  |  |  | 7.3163 | 7.202 | 7.0857 | 6.9173 | 6.7735 | 6.6316 | 6.4622 | 6.2878 | 6.1541 | 5.2408 | 4.8357 | 4.1653 | 10.4561 | 10.3765 | 10.2908 | 10.1704 | 10.0592 | 9.9296 | 9.7796 | 9.6224 | 9.4908 | 8.5429 | 7.599 | 5.6357 | 7.9061 | 7.802 | 7.6969 | 7.5459 | 7.4112 | 7.2786 | 7.1276 | 6.9694 | 6.8531 | 5.9622 | 5.6388 | 5.0296
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON PRIMARY | MINIMUM HEADROOM | ST 85356 13659 | NO | NO | 1.734 | 8.1122 | 7.6388 | 7.0816 | 6.3429 | 6.0429 | 5.5092 | 4.9112 | 4.3112 | 3.9133 | 1.8245 | 0.15102 | -0.89796 | 9.9316 | 9.7235 | 9.4837 | 9.1612 | 8.9969 | 8.6908 | 8.3408 | 7.9857 | 7.7204 | 6.1224 | 4.3531 | -0.066327 | 8.2398 | 7.8388 | 7.3684 | 6.7235 | 6.451 | 5.9622 | 5.4143 | 4.8673 | 4.4929 | 2.5255 | 1.1092 | 0.24286
|  | SHROTON PRIMARY | EE |  |  |  |  | 8.1122 | 7.6388 | 7.0816 | 6.3429 | 6.0429 | 5.5092 | 4.9112 | 4.3112 | 3.9133 | 1.8245 | 0.33776 | -0.67653 | 9.9316 | 9.7235 | 9.4837 | 9.1612 | 8.9969 | 8.6908 | 8.3408 | 7.9857 | 7.7204 | 6.1224 | 4.5112 | 2.2051 | 8.2398 | 7.8388 | 7.3684 | 6.7235 | 6.451 | 5.9622 | 5.4143 | 4.8673 | 4.4929 | 2.5255 | 1.2857 | 0.43265
|  | SHROTON PRIMARY | HT |  |  |  |  | 8.3173 | 7.9153 | 7.4531 | 6.8684 | 6.2133 | 5.6918 | 5.4684 | 4.9735 | 4.4673 | 1.8602 | 0.15102 | -0.89796 | 10.0306 | 9.8633 | 9.6694 | 9.4265 | 9.151 | 8.9357 | 8.8449 | 8.6276 | 8.3939 | 7.0898 | 6.3112 | 5.8388 | 8.4 | 8.048 | 7.6408 | 7.1367 | 6.5612 | 6.0959 | 5.9112 | 5.4459 | 4.9714 | 2.5755 | 1.1092 | 0.24286
|  | SHROTON PRIMARY | HE |  |  |  |  | 8.3367 | 7.949 | 7.499 | 6.9316 | 6.298 | 5.85 | 5.7071 | 5.2918 | 4.8531 | 2.448 | 1.0235 | 0.34796 | 10.0122 | 9.8306 | 9.6235 | 9.3622 | 9.0714 | 8.848 | 8.7571 | 8.4939 | 8.199 | 6.4429 | 4.8398 | 2.6735 | 8.4163 | 8.0755 | 7.6837 | 7.1969 | 6.6408 | 6.2439 | 6.1265 | 5.7327 | 5.3327 | 3.1316 | 1.9255 | 1.3694
|  | SHROTON PRIMARY | CF |  |  |  |  | 8.5041 | 8.202 | 7.8592 | 7.3755 | 6.9214 | 6.6949 | 6.4133 | 6.1112 | 6.2306 | 4.5755 | 3.0204 | 1.549 | 10.0776 | 9.9286 | 9.7602 | 9.5286 | 9.302 | 9.1541 | 8.9296 | 8.6755 | 8.651 | 6.9704 | 4.3531 | -0.066327 | 8.5724 | 8.3112 | 8.0122 | 7.6 | 7.2173 | 7.0143 | 6.7776 | 6.5255 | 6.6051 | 5.1031 | 3.6633 | 2.3531
LALEHAM GSP | STAINES BSP | SIDNEY ROAD PRIMARY | MINIMUM HEADROOM | TQ 04100 71760 | NO | NO | 2.658 | 14.5649 | 14.0567 | 13.5628 | 13.4077 | 12.9792 | 12.3343 | 11.6118 | 10.8618 | 10.3159 | 7.1098 | 4.4445 | 2.921 | 16.6547 | 16.2986 | 15.9271 | 15.8037 | 15.4506 | 14.9904 | 14.4669 | 13.9302 | 13.5159 | 10.9577 | 7.2557 | -1.0749 | 14.3537 | 13.8833 | 13.3935 | 13.2567 | 12.819 | 12.1945 | 11.4863 | 10.7833 | 10.2822 | 7.5465 | 5.271 | 4.0333
|  | SIDNEY ROAD PRIMARY | EE |  |  |  |  | 14.5649 | 14.0567 | 13.5628 | 13.4077 | 12.9792 | 12.3343 | 11.6118 | 10.8618 | 10.3159 | 7.2884 | 4.9567 | 3.1373 | 16.6547 | 16.2986 | 15.9271 | 15.8037 | 15.4506 | 14.9904 | 14.4669 | 13.9302 | 13.5159 | 10.9577 | 8.022 | 3.5516 | 14.3537 | 13.8833 | 13.3935 | 13.2567 | 12.819 | 12.1945 | 11.4863 | 10.7833 | 10.2822 | 7.6424 | 5.7292 | 4.2159
|  | SIDNEY ROAD PRIMARY | HT |  |  |  |  | 14.773 | 14.3292 | 13.9567 | 13.5802 | 13.1792 | 12.5404 | 12.2037 | 11.5547 | 10.8884 | 7.1098 | 4.4445 | 2.921 | 16.9169 | 16.669 | 16.4608 | 16.2292 | 15.9751 | 15.6282 | 15.5149 | 15.1577 | 14.7812 | 12.822 | 11.5833 | 10.9108 | 14.5924 | 14.2077 | 13.8577 | 13.4935 | 13.0975 | 12.4996 | 12.223 | 11.6098 | 10.9761 | 7.5465 | 5.271 | 4.0333
|  | SIDNEY ROAD PRIMARY | HE |  |  |  |  | 14.7935 | 14.3669 | 14.02 | 13.671 | 13.2975 | 12.772 | 12.5496 | 12.021 | 11.473 | 8.3873 | 6.123 | 5.0618 | 16.8363 | 16.5475 | 16.2914 | 16.0128 | 15.7057 | 15.319 | 15.1618 | 14.7475 | 14.3067 | 11.569 | 8.6159 | 4.4598 | 14.6088 | 14.2414 | 13.9159 | 13.5761 | 13.2098 | 12.7108 | 12.5322 | 12.0251 | 11.4975 | 8.6996 | 6.8271 | 5.971
|  | SIDNEY ROAD PRIMARY | CF |  |  |  |  | 15.1067 | 14.8312 | 14.6108 | 14.3853 | 14.1006 | 13.8567 | 13.5965 | 13.6486 | 13.419 | 11.4833 | 9.321 | 7.2016 | 16.9771 | 16.7445 | 16.522 | 16.2965 | 15.9965 | 15.6761 | 15.3108 | 15.1884 | 14.8169 | 11.9945 | 7.2557 | -1.0749 | 14.8822 | 14.6445 | 14.4282 | 14.2159 | 13.9435 | 13.7006 | 13.4302 | 13.4904 | 13.2455 | 11.3822 | 9.4445 | 7.6557
NURSLING GSP | ROWNHAMS BSP | SILKSTEAD PRIMARY | MINIMUM HEADROOM | SU 44578 24565 | NO | YES | 2.32 | 2.9378 | 1.9653 | 0.82959 | -0.46224 | -1.8816 | -3.4408 | -5.1827 | -6.9418 | -8.3898 | -17.8204 | -22.0061 | -22.4214 | 4.9041 | 4.1633 | 3.299 | 2.3112 | 1.2286 | 0.055102 | -1.252 | -2.5776 | -3.6633 | -10.7816 | -13.8837 | -14.2092 | 2.8735 | 1.9367 | 0.8398 | -0.40612 | -1.7786 | -3.2806 | -4.9541 | -6.6469 | -8.0378 | -17.1143 | -21.1194 | -21.498
|  | SILKSTEAD PRIMARY | EE |  |  |  |  | 2.9378 | 1.9653 | 0.82959 | -0.46224 | -1.8816 | -3.4408 | -5.1827 | -6.9418 | -8.3898 | -12.8194 | -13.6337 | -14.0163 | 4.9041 | 4.1633 | 3.299 | 2.3112 | 1.2286 | 0.055102 | -1.252 | -2.5776 | -3.6633 | -6.8786 | -7.3653 | -7.6082 | 2.8735 | 1.9367 | 0.8398 | -0.40612 | -1.7786 | -3.2806 | -4.9541 | -6.6469 | -8.0378 | -12.2673 | -13.0061 | -13.3398
|  | SILKSTEAD PRIMARY | HT |  |  |  |  | 3.9561 | 3.5806 | 2.9918 | 2.2327 | 1.3531 | 0.34796 | -0.89082 | -2.2133 | -3.5888 | -9.4082 | -12.0541 | -12.5031 | 5.8704 | 5.4551 | 4.9724 | 4.4 | 3.7327 | 2.9918 | 2.0745 | 1.0918 | 0.068367 | -4.1939 | -6.0551 | -6.2949 | 4 | 3.552 | 2.9337 | 2.2031 | 1.3531 | 0.3898 | -0.8 | -2.0704 | -3.3898 | -8.9612 | -11.4714 | -11.8735
|  | SILKSTEAD PRIMARY | HE |  |  |  |  | 3.5908 | 2.7439 | 1.748 | 0.56531 | -0.81837 | -2.3337 | -4.2306 | -6.2633 | -8.2714 | -17.8204 | -22.0061 | -22.4214 | 5.4082 | 4.7643 | 4.0092 | 3.1041 | 2.05 | 0.90714 | -0.52959 | -2.0694 | -3.5888 | -10.7816 | -13.8837 | -14.2092 | 3.5071 | 2.6918 | 1.7306 | 0.5898 | -0.74694 | -2.2082 | -4.0357 | -5.9939 | -7.9276 | -17.1143 | -21.1194 | -21.498
|  | SILKSTEAD PRIMARY | CF |  |  |  |  | 4.1561 | 3.8755 | 3.4367 | 2.8194 | 2.1 | 1.3724 | 0.39694 | -0.7 | -1.8694 | -8.55 | -14.1694 | -16.95 | 5.9388 | 5.6949 | 5.2806 | 4.8051 | 4.2541 | 3.6969 | 2.9469 | 2.1041 | 1.2031 | -3.8918 | -8.1469 | -10.2796 | 4.1888 | 3.8143 | 3.3561 | 2.7612 | 2.0653 | 1.3612 | 0.42143 | -0.6398 | -1.7704 | -8.2051 | -13.599 | -16.2459
BRAMLEY (BASI) GSP | READING BSP | SILVER STREET PRIMARY | MINIMUM HEADROOM | SU 71957 72821 | NO | YES | 3.306 | 17.7051 | 17.0878 | 16.2 | 15.2347 | 14.2827 | 13.001 | 11.4449 | 10.549 | 9.5918 | 6.9439 | 5.0092 | 5.0327 | 21.1282 | 20.6037 | 19.9078 | 19.1506 | 18.3496 | 17.3557 | 16.1598 | 15.3465 | 14.471 | 10.6598 | 4.9016 | -9.0504 | 17.0229 | 16.4361 | 15.6127 | 14.6851 | 13.7657 | 12.5412 | 11.0576 | 10.1178 | 9.1698 | 6.479 | 4.6759 | 4.7167
|  | SILVER STREET PRIMARY | EE |  |  |  |  | 17.7051 | 17.0878 | 16.2 | 15.2347 | 14.2827 | 13.001 | 11.4449 | 10.549 | 9.5918 | 6.9439 | 5.798 | 5.9571 | 21.1282 | 20.6037 | 19.9078 | 19.1506 | 18.3496 | 17.3557 | 16.1598 | 15.3465 | 14.471 | 10.6598 | 6.769 | 0.32612 | 17.0229 | 16.4361 | 15.6127 | 14.6851 | 13.7657 | 12.5412 | 11.0576 | 10.1178 | 9.1698 | 6.479 | 5.4004 | 5.5259
|  | SILVER STREET PRIMARY | HT |  |  |  |  | 18.1235 | 17.6173 | 16.9092 | 16.1265 | 15.3 | 14.1031 | 12.902 | 11.9459 | 10.9571 | 7.4092 | 5.0092 | 5.0327 | 21.5088 | 21.2547 | 20.7945 | 20.2996 | 19.7506 | 19.0149 | 18.2373 | 17.5557 | 16.8465 | 14.1639 | 12.472 | 12.3047 | 17.4218 | 16.9514 | 16.2963 | 15.5637 | 14.78 | 13.6678 | 12.5229 | 11.6055 | 10.6555 | 7.0127 | 4.6759 | 4.7167
|  | SILVER STREET PRIMARY | HE |  |  |  |  | 18.1163 | 17.6888 | 17.0388 | 16.3276 | 15.6622 | 14.7541 | 13.6796 | 12.7051 | 11.8602 | 9.7949 | 8.7806 | 8.6255 | 21.4547 | 21.0914 | 20.5863 | 20.0271 | 19.4537 | 18.7424 | 17.9047 | 17.0741 | 16.271 | 12.6955 | 8.7067 | 2.3027 | 17.4147 | 17.0065 | 16.4055 | 15.7361 | 15.0963 | 14.2382 | 13.2127 | 12.2831 | 11.4678 | 9.229 | 8.2127 | 8.0994
|  | SILVER STREET PRIMARY | CF |  |  |  |  | 18.4102 | 18.1031 | 17.6347 | 17.0745 | 16.7827 | 16.5153 | 16.0837 | 15.5439 | 15.0296 | 11.6908 | 9.8357 | 7.8173 | 21.5822 | 21.3047 | 20.8812 | 20.3812 | 19.9639 | 19.4863 | 18.8782 | 18.1812 | 17.4639 | 12.3618 | 4.9016 | -9.0504 | 17.7157 | 17.4351 | 17.0106 | 16.5024 | 16.2147 | 15.9596 | 15.5576 | 15.0514 | 14.5504 | 11.332 | 9.3473 | 7.3249
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD PRIMARY | MINIMUM HEADROOM | SZ 18262 93590 | NO | NO | 1.447 | 6.0153 | 5.3143 | 4.1735 | 2.8969 | 1.9408 | 0.62755 | -0.89184 | -2.4245 | -3.5408 | -10.2459 | -15.4582 | -18.3235 | 10.851 | 10.4133 | 9.6653 | 8.8133 | 8.0898 | 7.1755 | 6.099 | 4.951 | 4.1265 | -0.59388 | -7.2102 | -22.5704 | 6.2929 | 5.7071 | 4.7041 | 3.5765 | 2.6612 | 1.3867 | -0.057143 | -1.4959 | -2.5112 | -8.2633 | -12.8622 | -15.3337
|  | SOMERFORD PRIMARY | EE |  |  |  |  | 6.0153 | 5.3143 | 4.1735 | 2.8969 | 1.9408 | 0.62755 | -0.89184 | -2.4245 | -3.5408 | -9.4173 | -14.1867 | -17.8388 | 10.851 | 10.4133 | 9.6653 | 8.8133 | 8.0898 | 7.1755 | 6.099 | 4.951 | 4.1265 | -0.59388 | -6.1173 | -14.3337 | 6.2929 | 5.7071 | 4.7041 | 3.5765 | 2.6612 | 1.3867 | -0.057143 | -1.4959 | -2.5112 | -7.6745 | -11.7653 | -14.9429
|  | SOMERFORD PRIMARY | HT |  |  |  |  | 6.402 | 5.4357 | 4.3184 | 3.4673 | 2.6408 | 1.4153 | 0.085714 | -1.2949 | -2.7133 | -10.2459 | -15.4582 | -18.3235 | 11.348 | 10.8122 | 10.201 | 9.8347 | 9.3704 | 8.7367 | 8.0214 | 7.2663 | 6.4816 | 2.5255 | 0.16633 | -1.0602 | 6.6867 | 5.8469 | 4.8714 | 4.1735 | 3.4173 | 2.3061 | 1.0959 | -0.16429 | -1.4571 | -8.2633 | -12.8622 | -15.3337
|  | SOMERFORD PRIMARY | HE |  |  |  |  | 6.4898 | 5.5857 | 4.5316 | 3.7429 | 2.9929 | 2.0653 | 1.0429 | -0.023469 | -1.1388 | -7.249 | -12.0418 | -14.2929 | 11.2327 | 10.6245 | 9.9459 | 9.4888 | 8.9255 | 8.2551 | 7.4878 | 6.6602 | 5.7796 | 0.48469 | -5.1469 | -12.7918 | 6.7622 | 5.9735 | 5.0582 | 4.4143 | 3.7224 | 2.8724 | 1.9265 | 0.94184 | -0.084694 | -5.6622 | -9.8245 | -11.7592
|  | SOMERFORD PRIMARY | CF |  |  |  |  | 6.9602 | 6.3653 | 5.6245 | 5.1061 | 4.65 | 4.3245 | 3.9255 | 3.5082 | 3.0612 | -0.88776 | -5.4622 | -9.8704 | 11.4153 | 10.9531 | 10.3949 | 10.0051 | 9.5143 | 9 | 8.3847 | 7.7388 | 7.0367 | 1.7071 | -7.2102 | -22.5704 | 7.1888 | 6.6827 | 6.05 | 5.6459 | 5.2245 | 4.9224 | 4.5449 | 4.1439 | 3.7051 | -0.07449 | -4.1908 | -7.9602
LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | SOUTH BERSTED PRIMARY | MINIMUM HEADROOM | SU 94025 00705 | NO | YES | 13.488 | 11.4076 | 11.1392 | 10.6096 | 10.029 | 9.4086 | 8.2412 | 6.9249 | 5.6127 | 4.6484 | -1.2118 | -6.1302 | -9.1251 | 15.2076 | 14.9984 | 14.5422 | 13.9912 | 13.3871 | 12.5545 | 11.5922 | 10.6127 | 9.932 | 6.0249 | 0.96367 | -11.7465 | 10.7984 | 10.5565 | 9.9902 | 9.3637 | 8.6841 | 7.5759 | 6.3249 | 5.0769 | 4.2208 | -0.47102 | -4.4812 | -6.8904
|  | SOUTH BERSTED PRIMARY | EE |  |  |  |  | 11.4076 | 11.1392 | 10.6096 | 10.029 | 9.4086 | 8.2412 | 6.9249 | 5.6127 | 4.6484 | -0.70163 | -5.0771 | -8.5567 | 15.2076 | 14.9984 | 14.5422 | 13.9912 | 13.3871 | 12.5545 | 11.5922 | 10.6127 | 9.932 | 6.0249 | 1.4718 | -5.4455 | 10.7984 | 10.5565 | 9.9902 | 9.3637 | 8.6841 | 7.5759 | 6.3249 | 5.0769 | 4.2208 | -0.23531 | -3.6516 | -6.5108
|  | SOUTH BERSTED PRIMARY | HT |  |  |  |  | 11.7076 | 11.2698 | 10.7739 | 10.2351 | 10.0351 | 8.9912 | 7.8708 | 6.7106 | 5.5229 | -1.2118 | -6.1302 | -9.1251 | 15.5922 | 15.3351 | 15.0269 | 14.6596 | 14.6157 | 14.0596 | 13.431 | 12.7667 | 12.0718 | 8.5678 | 6.4024 | 5.1239 | 11.2137 | 10.7831 | 10.278 | 9.7259 | 9.6014 | 8.6627 | 7.6361 | 6.5606 | 5.4484 | -0.47102 | -4.4812 | -6.8904
|  | SOUTH BERSTED PRIMARY | HE |  |  |  |  | 11.7606 | 11.3647 | 10.9096 | 10.4147 | 10.2647 | 9.4331 | 8.5208 | 7.5749 | 6.6096 | 1.079 | -3.2588 | -5.5261 | 15.4912 | 15.179 | 14.8127 | 14.3912 | 14.2392 | 13.6698 | 13.0014 | 12.2708 | 11.4922 | 7.0086 | 2.3627 | -4.0516 | 11.2484 | 10.8524 | 10.3831 | 9.8688 | 9.7851 | 9.0188 | 8.1565 | 7.2545 | 6.3249 | 1.4167 | -1.969 | -3.7537
|  | SOUTH BERSTED PRIMARY | CF |  |  |  |  | 12.1473 | 11.929 | 11.6759 | 11.3994 | 11.1035 | 11.1188 | 10.782 | 10.4127 | 10.029 | 6.6076 | 2.6351 | -1.5078 | 15.6606 | 15.4147 | 15.128 | 14.7963 | 14.3973 | 14.2198 | 13.728 | 13.1963 | 12.5902 | 8.1218 | 0.96367 | -11.7465 | 11.5984 | 11.3576 | 11.0769 | 10.7667 | 10.43 | 10.5065 | 10.1361 | 9.729 | 9.3035 | 6.0463 | 2.6198 | -0.70776
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE PRIMARY | MINIMUM HEADROOM | SZ 13563 92074 | NO | NO | 5.346 | 3.9102 | 3.2969 | 3.0765 | 2.451 | 1.7704 | 0.67755 | -0.56122 | -1.7949 | -2.6857 | -6.4959 | -9.3388 | -9.998 | 7.4439 | 6.9 | 6.6694 | 6.0888 | 5.4571 | 4.6153 | 3.6388 | 2.6469 | 1.9133 | -2.0378 | -8.6459 | -23.7816 | 5.0286 | 4.399 | 4.2714 | 3.649 | 2.9776 | 1.9571 | 0.78367 | -0.38673 | -1.1714 | -4.6051 | -7.0735 | -7.6102
|  | SOUTHBOURNE PRIMARY | EE |  |  |  |  | 3.9102 | 3.2969 | 3.0765 | 2.451 | 1.7704 | 0.67755 | -0.56122 | -1.7949 | -2.6857 | -6.4959 | -8.8235 | -9.0918 | 7.4439 | 6.9 | 6.6694 | 6.0888 | 5.4571 | 4.6153 | 3.6388 | 2.6469 | 1.9133 | -2.0378 | -6.5612 | -13.5776 | 5.0286 | 4.399 | 4.2714 | 3.649 | 2.9776 | 1.9571 | 0.78367 | -0.38673 | -1.1714 | -4.6051 | -6.6 | -6.8714
|  | SOUTHBOURNE PRIMARY | HT |  |  |  |  | 4.3357 | 3.9306 | 3.45 | 2.9204 | 2.7449 | 1.8827 | 0.91429 | -0.10612 | -1.1694 | -6.2786 | -9.3388 | -9.998 | 7.9408 | 7.6622 | 7.3214 | 6.9459 | 6.852 | 6.3469 | 5.7561 | 5.1276 | 4.4653 | 1.4347 | -0.2051 | -0.61327 | 5.4969 | 5.1173 | 4.6469 | 4.1224 | 4.0031 | 3.2061 | 2.3051 | 1.3561 | 0.36735 | -4.3531 | -7.0735 | -7.6102
|  | SOUTHBOURNE PRIMARY | HE |  |  |  |  | 4.3918 | 4.0378 | 3.6245 | 3.1673 | 3.0653 | 2.3378 | 1.5173 | 0.66531 | -0.23571 | -4.0663 | -6.1163 | -6.6408 | 7.8224 | 7.4827 | 7.0878 | 6.6388 | 6.4673 | 5.8816 | 5.2122 | 4.4898 | 3.7143 | -0.57551 | -5.0878 | -12.1061 | 5.5418 | 5.2082 | 4.7969 | 4.3388 | 4.2949 | 3.6204 | 2.8551 | 2.0571 | 1.2184 | -2.3327 | -4.1469 | -4.5867
|  | SOUTHBOURNE PRIMARY | CF |  |  |  |  | 4.7163 | 4.4714 | 4.2653 | 3.9959 | 3.6786 | 3.2735 | 3.3031 | 2.9041 | 2.4888 | -0.24898 | -3.3286 | -6.1908 | 7.9633 | 7.65 | 7.3531 | 6.9735 | 6.5092 | 5.95 | 5.6704 | 5.0469 | 4.3755 | -0.42653 | -8.6459 | -23.7816 | 5.8214 | 5.5714 | 5.3541 | 5.0633 | 4.7306 | 4.3388 | 4.4367 | 4.0378 | 3.6194 | 0.96837 | -1.7102 | -4.2531
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | SOUTHCOTE PRIMARY | MINIMUM HEADROOM | SU 68199 71325 | NO | NO | 5.592 | 7.1602 | 6.8694 | 6.498 | 6.0041 | 5.9286 | 5.2276 | 4.5061 | 3.8112 | 3.35 | 0.65714 | -1.4816 | -2.7092 | 8.0816 | 7.8082 | 7.4745 | 7.0551 | 6.9898 | 6.4806 | 5.9357 | 5.3816 | 5.001 | 2.7 | -1.5653 | -10.5847 | 6.8602 | 6.5561 | 6.1633 | 5.6684 | 5.7102 | 5.0622 | 4.3816 | 3.7204 | 3.3133 | 1.0327 | -0.85816 | -1.8571
|  | SOUTHCOTE PRIMARY | EE |  |  |  |  | 7.1602 | 6.8694 | 6.498 | 6.0041 | 5.9286 | 5.2276 | 4.5061 | 3.8112 | 3.35 | 0.88571 | -1.0214 | -2.5541 | 8.0816 | 7.8082 | 7.4745 | 7.0551 | 6.9898 | 6.4806 | 5.9357 | 5.3816 | 5.001 | 2.7 | -0.19286 | -4.8765 | 6.8602 | 6.5561 | 6.1633 | 5.6684 | 5.7102 | 5.0622 | 4.3816 | 3.7204 | 3.3133 | 1.201 | -0.44592 | -1.7224
|  | SOUTHCOTE PRIMARY | HT |  |  |  |  | 7.3561 | 7.1276 | 6.8541 | 6.4816 | 6.0286 | 5.3561 | 5.0786 | 4.4918 | 3.8918 | 0.65714 | -1.4816 | -2.7092 | 8.3633 | 8.2102 | 8.0173 | 7.7888 | 7.5041 | 7.1194 | 7.0673 | 6.7235 | 6.3724 | 4.649 | 3.6745 | 3.1786 | 7.1163 | 6.8888 | 6.601 | 6.2673 | 5.8327 | 5.2112 | 5.0643 | 4.5173 | 3.9592 | 1.0327 | -0.85816 | -1.8571
|  | SOUTHCOTE PRIMARY | HE |  |  |  |  | 7.3796 | 7.1776 | 6.9286 | 6.6296 | 6.2418 | 5.6643 | 5.4469 | 4.9551 | 4.4694 | 1.8653 | -0.067347 | -0.97551 | 8.2837 | 8.0888 | 7.851 | 7.5898 | 7.2582 | 6.8255 | 6.6969 | 6.2796 | 5.8531 | 3.2337 | 0.28061 | -4.1408 | 7.1378 | 6.9296 | 6.6663 | 6.3969 | 6.0153 | 5.4735 | 5.3765 | 4.9204 | 4.4582 | 2.0867 | 0.43163 | -0.30714
|  | SOUTHCOTE PRIMARY | CF |  |  |  |  | 7.5796 | 7.4704 | 7.3245 | 7.1622 | 7.0357 | 6.8439 | 6.5724 | 6.2582 | 6.3439 | 4.4265 | 2.551 | 0.77755 | 8.3704 | 8.2061 | 8.0071 | 7.7765 | 7.55 | 7.2296 | 6.8418 | 6.4173 | 6.3041 | 3.349 | -1.5653 | -10.5847 | 7.3194 | 7.1939 | 7.0286 | 6.8439 | 6.7184 | 6.5051 | 6.2245 | 5.9051 | 6.0888 | 4.2929 | 2.6439 | 1.148
EALING GSP |  | SOUTHFIELD ROAD PRIMARY | MINIMUM HEADROOM | TQ 20533 79746 | NO | NO | 22.497 | 17.8143 | 15.8132 | 13.3979 | 11.1949 | 8.3888 | 6.1081 | 3.6388 | 1.9071 | 0.54794 | -6.8419 | -14.9674 | -20.2143 | 26.0775 | 24.749 | 23.1612 | 21.8418 | 20.0357 | 18.3806 | 16.5102 | 14.9122 | 13.603 | 5.6183 | -7.3766 | -37.5235 | 18.9928 | 17.2479 | 15.1173 | 13.1888 | 10.6796 | 8.6102 | 6.3469 | 4.6765 | 3.3816 | -3.3306 | -10.1949 | -14.6041
|  | SOUTHFIELD ROAD PRIMARY | EE |  |  |  |  | 17.8143 | 15.8132 | 13.3979 | 11.1949 | 8.3888 | 6.1081 | 3.6388 | 1.9071 | 0.54794 | -6.8419 | -13.6245 | -19.8235 | 26.0775 | 24.749 | 23.1612 | 21.8418 | 20.0357 | 18.3806 | 16.5102 | 14.9122 | 13.603 | 5.6183 | -4.4623 | -20.848 | 18.9928 | 17.2479 | 15.1173 | 13.1888 | 10.6796 | 8.6102 | 6.3469 | 4.6765 | 3.3816 | -3.3306 | -8.9398 | -14.3051
|  | SOUTHFIELD ROAD PRIMARY | HT |  |  |  |  | 18.5367 | 16.8112 | 14.7837 | 12.5734 | 10.0775 | 8.1092 | 6.4388 | 5.101 | 3.6765 | -5.7225 | -14.9674 | -20.2143 | 26.9449 | 26.0092 | 24.9306 | 23.7388 | 22.3969 | 21.2571 | 20.4275 | 19.4765 | 18.4673 | 12.9469 | 8.5663 | 6.4643 | 19.7132 | 18.2439 | 16.5 | 14.5643 | 12.3643 | 10.6112 | 9.1714 | 7.8734 | 6.5051 | -2.1653 | -10.1949 | -14.6041
|  | SOUTHFIELD ROAD PRIMARY | HE |  |  |  |  | 18.45 | 16.7551 | 14.7724 | 12.6316 | 10.2255 | 8.351 | 6.7673 | 5.5847 | 4.3622 | -2.6143 | -8.6255 | -11.0735 | 26.6418 | 25.5734 | 24.3653 | 23.0408 | 21.5643 | 20.2622 | 19.2653 | 18.1326 | 16.9204 | 8.8224 | -1.1674 | -15.8572 | 19.6326 | 18.1959 | 16.4979 | 14.6316 | 12.5265 | 10.8775 | 9.5714 | 8.4428 | 7.2714 | 0.88671 | -4.1847 | -6.1806
|  | SOUTHFIELD ROAD PRIMARY | CF |  |  |  |  | 19.0255 | 17.6459 | 16.0071 | 14.3459 | 12.449 | 11.3194 | 10.0898 | 9.8581 | 9.2612 | 5.1541 | 0.37651 | -4.4602 | 26.8816 | 25.9132 | 24.7847 | 23.6347 | 22.2622 | 21.0888 | 19.7571 | 19.0204 | 17.8122 | 8.8632 | -7.3766 | -37.5235 | 20.1632 | 19.0153 | 17.6265 | 16.2041 | 14.5663 | 13.5877 | 12.499 | 12.2755 | 11.6908 | 7.752 | 3.3347 | -0.96941
AXMINSTER GSP | YEOVIL BSP | SPARKFORD PRIMARY | MINIMUM HEADROOM | ST 60767 25496 | NO | NO | 0.755 | 2.5071 | 2.4 | 2.2765 | 2.1867 | 2.0531 | 1.8827 | 1.7388 | 1.552 | 1.45 | 0.96122 | 0.78469 | 0.61837 | 3.5663 | 3.4878 | 3.3939 | 3.3306 | 3.2276 | 3.1041 | 2.9949 | 2.8541 | 2.7816 | 2.4112 | 1.9439 | 0.94388 | 2.8939 | 2.7837 | 2.6551 | 2.5653 | 2.4245 | 2.25 | 2.1143 | 1.9163 | 1.8592 | 1.4418 | 1.2857 | 1.1378
|  | SPARKFORD PRIMARY | EE |  |  |  |  | 2.5071 | 2.4 | 2.2765 | 2.1867 | 2.0531 | 1.8827 | 1.7388 | 1.552 | 1.45 | 0.96122 | 0.78469 | 0.69694 | 3.5663 | 3.4878 | 3.3939 | 3.3306 | 3.2276 | 3.1041 | 2.9949 | 2.8541 | 2.7816 | 2.4112 | 2.098 | 1.6286 | 2.8939 | 2.7837 | 2.6551 | 2.5653 | 2.4245 | 2.25 | 2.1143 | 1.9163 | 1.8592 | 1.4418 | 1.2857 | 1.2092
|  | SPARKFORD PRIMARY | HT |  |  |  |  | 2.5806 | 2.4929 | 2.4214 | 2.3306 | 2.2296 | 2.1347 | 1.9918 | 1.8388 | 1.7255 | 1.0582 | 0.80612 | 0.61837 | 3.6316 | 3.5735 | 3.5337 | 3.4745 | 3.4061 | 3.3541 | 3.2561 | 3.1551 | 3.0847 | 2.6602 | 2.5143 | 2.4102 | 2.9643 | 2.8796 | 2.8143 | 2.7316 | 2.6316 | 2.5459 | 2.4082 | 2.2643 | 2.1561 | 1.5306 | 1.302 | 1.1378
|  | SPARKFORD PRIMARY | HE |  |  |  |  | 2.5806 | 2.4918 | 2.4224 | 2.3347 | 2.2347 | 2.1418 | 2.001 | 1.849 | 1.7357 | 1.001 | 0.83061 | 0.7602 | 3.6235 | 3.5602 | 3.5112 | 3.449 | 3.3724 | 3.3102 | 3.2051 | 3.0918 | 3.0112 | 2.4459 | 2.1265 | 1.6714 | 2.9633 | 2.8796 | 2.8163 | 2.7347 | 2.6367 | 2.552 | 2.4153 | 2.2735 | 2.1684 | 1.4816 | 1.3286 | 1.2694
|  | SPARKFORD PRIMARY | CF |  |  |  |  | 2.601 | 2.5418 | 2.4878 | 2.4143 | 2.3449 | 2.2582 | 2.1939 | 2.0949 | 1.9898 | 1.4582 | 1.0786 | 0.75204 | 3.6347 | 3.5898 | 3.55 | 3.4949 | 3.4378 | 3.3622 | 3.3061 | 3.2173 | 3.1245 | 2.5847 | 1.9439 | 0.94388 | 2.9847 | 2.9286 | 2.8776 | 2.8082 | 2.7429 | 2.6602 | 2.602 | 2.5071 | 2.4082 | 1.9 | 1.548 | 1.2531
MELKSHAM GSP | NORRINGTON BSP | SPRING QUARRY WEST PRIMARY | MINIMUM HEADROOM | ST 84368 68717 | NO | YES | 0.617 | 20.0878 | 19.8918 | 19.7133 | 19.4255 | 19.0745 | 18.1622 | 17.5153 | 16.7694 | 16.048 | 13.0857 | 10.8092 | 9.2224 | 20.3898 | 20.2337 | 20.0908 | 19.8684 | 19.6143 | 18.7602 | 18.148 | 17.449 | 16.7786 | 14.4612 | 12.6367 | 10.2684 | 19.6255 | 19.4286 | 19.2531 | 18.9704 | 18.6367 | 17.649 | 16.9571 | 16.1541 | 15.351 | 12.202 | 9.8418 | 8.1796
|  | SPRING QUARRY WEST PRIMARY | EE |  |  |  |  | 20.0878 | 19.8918 | 19.7133 | 19.4255 | 19.0745 | 18.1622 | 17.5153 | 16.7694 | 16.1122 | 13.6408 | 11.9684 | 10.3643 | 20.3898 | 20.2337 | 20.0908 | 19.8684 | 19.6143 | 18.7602 | 18.148 | 17.449 | 16.7786 | 14.552 | 12.7367 | 10.2684 | 19.6255 | 19.4286 | 19.2531 | 18.9704 | 18.6367 | 17.649 | 16.9571 | 16.1541 | 15.4214 | 12.8643 | 11.2092 | 9.5388
|  | SPRING QUARRY WEST PRIMARY | HT |  |  |  |  | 20.2051 | 20.0592 | 19.9327 | 19.7031 | 19.4122 | 18.5908 | 17.6388 | 16.8612 | 16.048 | 13.0857 | 10.8092 | 9.2224 | 20.4837 | 20.4102 | 20.3429 | 20.2133 | 20.0316 | 19.3051 | 18.4255 | 17.7286 | 16.9531 | 14.4612 | 12.6367 | 11.2898 | 19.7429 | 19.6051 | 19.4878 | 19.2806 | 19.0112 | 18.1357 | 17.0929 | 16.2551 | 15.351 | 12.202 | 9.8418 | 8.1796
|  | SPRING QUARRY WEST PRIMARY | HE |  |  |  |  | 20.2102 | 20.0704 | 19.949 | 19.7296 | 19.4459 | 18.8245 | 18.0582 | 17.5653 | 17.0796 | 14.9459 | 13.2378 | 11.8929 | 20.4602 | 20.3673 | 20.2827 | 20.1429 | 19.95 | 19.4041 | 18.6888 | 18.2755 | 17.8255 | 15.8755 | 13.9755 | 11.5857 | 19.7469 | 19.6143 | 19.502 | 19.3031 | 19.0449 | 18.3939 | 17.5673 | 17.0653 | 16.5469 | 14.3602 | 12.65 | 11.201
|  | SPRING QUARRY WEST PRIMARY | CF |  |  |  |  | 20.3133 | 20.2245 | 20.1245 | 20 | 19.7939 | 19.3816 | 18.8755 | 18.4367 | 18.0939 | 17.0898 | 15.95 | 14.9296 | 20.5071 | 20.4327 | 20.352 | 20.2582 | 20.1112 | 19.6939 | 19.1531 | 18.6571 | 18.2459 | 17.0439 | 15.3061 | 12.4235 | 19.8418 | 19.7582 | 19.6612 | 19.5551 | 19.3694 | 18.9306 | 18.3745 | 17.8837 | 17.4888 | 16.4888 | 15.4602 | 14.5582
NORTH HYDE GSP | NORTH HYDE BSP | SPRINGFIELD ROAD PRIMARY | MINIMUM HEADROOM | TQ 11409 80620 | NO | YES | 1.869 | 7.6459 | 7.2 | 6.6888 | 30.3806 | 29.8612 | 28.4041 | 26.748 | 25.3255 | 24.0531 | 19.3684 | 15.8204 | 14.5724 | 11.0241 | 10.5894 | 10.121 | 35.0908 | 34.5592 | 33.0724 | 31.3633 | 29.9194 | 28.4898 | 22.5694 | 16.348 | -1.5071 | 7.6182 | 7.1865 | 6.6743 | 31.151 | 30.651 | 29.0939 | 27.3051 | 25.8122 | 24.4643 | 19.499 | 15.7786 | 14.2755
|  | SPRINGFIELD ROAD PRIMARY | EE |  |  |  |  | 7.6459 | 7.2 | 6.6888 | 30.3806 | 29.8612 | 28.4041 | 26.748 | 25.3255 | 24.0531 | 19.9204 | 17.6194 | 16.898 | 11.0241 | 10.5894 | 10.121 | 35.0908 | 34.5592 | 33.0724 | 31.3633 | 29.9194 | 28.4898 | 22.5694 | 16.4133 | 6.7378 | 7.6182 | 7.1865 | 6.6743 | 31.151 | 30.651 | 29.0939 | 27.3051 | 25.8122 | 24.4643 | 20.1908 | 17.8622 | 16.7918
|  | SPRINGFIELD ROAD PRIMARY | HT |  |  |  |  | 7.8939 | 7.6276 | 7.2827 | 30.7796 | 30.3367 | 28.9786 | 27.8857 | 26.6194 | 25.2245 | 19.3684 | 15.8204 | 14.5724 | 11.3914 | 11.1965 | 10.9486 | 35.9347 | 35.6276 | 34.3929 | 33.2857 | 32.1694 | 30.9031 | 25.9071 | 22.7878 | 21.0939 | 7.8947 | 7.6651 | 7.3151 | 31.5296 | 31.101 | 29.6276 | 28.4571 | 27.1214 | 25.6306 | 19.499 | 15.7786 | 14.2755
|  | SPRINGFIELD ROAD PRIMARY | HE |  |  |  |  | 7.9622 | 7.6765 | 7.3735 | 30.9143 | 30.5265 | 29.4786 | 28.6561 | 27.8357 | 26.9347 | 22.9796 | 20.8704 | 19.4847 | 11.2751 | 10.9516 | 10.6159 | 35.4867 | 35.0561 | 33.9643 | 32.9449 | 32.0939 | 31.1194 | 25.3276 | 19.1724 | 9.1918 | 7.9549 | 7.711 | 7.3978 | 31.6541 | 31.2755 | 30.1612 | 29.2949 | 28.4857 | 27.5796 | 23.499 | 21.3041 | 19.6837
|  | SPRINGFIELD ROAD PRIMARY | CF |  |  |  |  | 8.2143 | 8.0918 | 7.8816 | 31.5143 | 31.3296 | 30.7653 | 29.9969 | 29.2847 | 29.0551 | 26.6867 | 24.3541 | 22.2224 | 11.372 | 11.1241 | 10.7792 | 35.649 | 35.2367 | 34.3357 | 33.1663 | 32.0602 | 31.2969 | 25.851 | 16.348 | -1.5071 | 8.16 | 8.0784 | 7.8651 | 32.1888 | 32.0173 | 31.3837 | 30.5092 | 29.7071 | 29.5031 | 27.1449 | 25.0327 | 23.1418
NURSLING GSP | WINCHESTER BSP | ST CROSS PRIMARY | MINIMUM HEADROOM | SU 47287 28156 | NO | NO | 2.461 | 10.9217 | 10.038 | 9.5503 | 8.9054 | 8.2891 | 7.2993 | 6.1646 | 4.988 | 4.0503 | -0.92216 | -4.8487 | -7.1313 | 10.3289 | 9.5707 | 9.0238 | 8.6462 | 8.3472 | 7.8656 | 7.2931 | 6.6615 | 6.0656 | 3.3503 | 1.3809 | -0.72624 | 10.1176 | 9.284 | 8.837 | 8.2238 | 7.6329 | 6.7105 | 5.6462 | 4.5442 | 3.687 | -0.57522 | -4.014 | -5.9528
|  | ST CROSS PRIMARY | EE |  |  |  |  | 10.9217 | 10.038 | 9.5503 | 8.9054 | 8.2891 | 7.2993 | 6.1646 | 4.988 | 4.0503 | -0.70176 | -4.1109 | -6.7762 | 10.3289 | 9.5707 | 9.0238 | 8.6462 | 8.3472 | 7.8656 | 7.2931 | 6.6615 | 6.0656 | 3.3503 | 1.3809 | -0.72624 | 10.1176 | 9.284 | 8.837 | 8.2238 | 7.6329 | 6.7105 | 5.6462 | 4.5442 | 3.687 | -0.44257 | -3.3824 | -5.6803
|  | ST CROSS PRIMARY | HT |  |  |  |  | 11.238 | 10.4748 | 9.7901 | 9.2656 | 8.6676 | 8.134 | 7.1156 | 5.9799 | 4.8084 | -0.92216 | -4.8487 | -7.1313 | 10.4748 | 9.7748 | 9.1758 | 8.9258 | 8.6166 | 8.288 | 7.7268 | 7.0482 | 6.3758 | 3.8462 | 2.2299 | 1.2401 | 10.4401 | 9.7258 | 9.087 | 8.5942 | 8.0289 | 7.5687 | 6.6391 | 5.6054 | 4.5411 | -0.57522 | -4.014 | -5.9528
|  | ST CROSS PRIMARY | HE |  |  |  |  | 11.2676 | 10.536 | 9.8911 | 9.3513 | 8.8431 | 8.4819 | 7.6768 | 6.8023 | 5.8493 | 1.0595 | -2.1405 | -3.6875 | 10.4503 | 9.738 | 9.1309 | 8.7799 | 8.5187 | 8.2595 | 7.7993 | 7.2687 | 6.6758 | 3.9513 | 2.0268 | 0.28396 | 10.4605 | 9.7778 | 9.1748 | 8.6656 | 8.184 | 7.8768 | 7.1299 | 6.3207 | 5.4442 | 1.1962 | -1.5701 | -2.8701
|  | ST CROSS PRIMARY | CF |  |  |  |  | 11.535 | 10.9911 | 10.4564 | 10.1289 | 9.7411 | 9.4084 | 9.3809 | 8.9931 | 8.5513 | 5.2748 | 2.2554 | -0.70278 | 10.535 | 9.8768 | 9.2942 | 9.0105 | 8.6972 | 8.5136 | 8.4115 | 8.1462 | 7.8421 | 5.537 | 3.2238 | -0.087469 | 10.7064 | 10.1931 | 9.688 | 9.3799 | 9.0105 | 8.6911 | 8.684 | 8.3136 | 7.8972 | 4.8758 | 2.1962 | -0.28645
COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES PRIMARY | MINIMUM HEADROOM | SP 51259 05741 | NO | YES | 4.731 | 7.4872 | 7.378 | 7.178 | 6.8902 | 6.3311 | 5.2494 | 4.576 | 3.8341 | 3.2607 | 1.4913 | 0.57392 | 0.3729 | 11.5107 | 11.3566 | 11.1709 | 10.9984 | 10.5678 | 9.9056 | 9.2892 | 8.6219 | 8.0362 | 5.7688 | 2.9198 | -3.5108 | 6.9413 | 6.8494 | 6.6647 | 6.4198 | 6.0178 | 5.3362 | 4.7086 | 4.0168 | 3.476 | 1.8372 | 1.0668 | 0.89535
|  | ST EBBES PRIMARY | EE |  |  |  |  | 7.6811 | 7.3994 | 7.178 | 6.8902 | 6.3311 | 5.3351 | 4.576 | 3.8341 | 3.2607 | 1.4913 | 0.81984 | 0.67086 | 11.5627 | 11.3566 | 11.1709 | 10.9984 | 10.5821 | 9.9056 | 9.2892 | 8.6219 | 8.0362 | 5.7688 | 3.8678 | 0.71473 | 7.0964 | 6.8566 | 6.6647 | 6.4964 | 6.129 | 5.4015 | 4.7086 | 4.0168 | 3.476 | 1.8372 | 1.2596 | 1.0984
|  | ST EBBES PRIMARY | HT |  |  |  |  | 7.4872 | 7.378 | 7.2658 | 6.9219 | 6.4331 | 5.2494 | 4.7117 | 4.0535 | 3.5382 | 1.6943 | 0.57392 | 0.3729 | 11.5107 | 11.4321 | 11.3576 | 11.0015 | 10.5678 | 9.9719 | 9.4943 | 8.8739 | 8.4525 | 7.48 | 6.8535 | 6.7045 | 6.9413 | 6.8494 | 6.7545 | 6.4198 | 6.0178 | 5.3362 | 4.8147 | 4.176 | 3.7035 | 2.1158 | 1.0668 | 0.89535
|  | ST EBBES PRIMARY | HE |  |  |  |  | 7.7576 | 7.5004 | 7.327 | 7.1678 | 6.7872 | 5.9586 | 5.3372 | 4.7851 | 4.2698 | 2.6392 | 2.0994 | 1.9872 | 11.6239 | 11.4372 | 11.2953 | 11.1525 | 10.779 | 10.2943 | 9.8168 | 9.28 | 8.7198 | 6.5045 | 4.7004 | 1.6627 | 7.1658 | 6.9494 | 6.8015 | 6.6668 | 6.3433 | 5.8617 | 5.4045 | 4.876 | 4.3668 | 2.8882 | 2.4504 | 2.3566
|  | ST EBBES PRIMARY | CF |  |  |  |  | 7.979 | 7.9331 | 7.877 | 7.826 | 7.7637 | 7.6056 | 7.3035 | 6.9086 | 6.48 | 3.7984 | 2.8688 | 2.0504 | 11.7198 | 11.6545 | 11.5811 | 11.5056 | 11.4004 | 11.1719 | 10.8086 | 10.3576 | 9.8647 | 6.328 | 2.9198 | -3.5108 | 7.3504 | 7.3086 | 7.2607 | 7.2147 | 7.1627 | 7.0096 | 6.726 | 6.3566 | 5.9556 | 3.7107 | 3.127 | 2.4351
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | ST JOHNS PRIMARY | MINIMUM HEADROOM | SU 47113 66363 | NO | NO | 8.28 | -11.8453 | -12.9463 | -13.7953 | -15.0106 | -16.327 | -17.8035 | -19.4014 | -20.9463 | -22.0821 | -26.4821 | -30.0974 | -32.1025 | -5.5504 | -6.2912 | -6.7239 | -7.5004 | -8.3331 | -9.2719 | -10.3168 | -11.3463 | -12.0698 | -15.279 | -19.3208 | -29.9065 | -11.1239 | -12.129 | -12.7494 | -13.8208 | -14.9882 | -16.327 | -17.7933 | -19.1984 | -20.177 | -23.8892 | -27.0045 | -28.6402
|  | ST JOHNS PRIMARY | EE |  |  |  |  | -11.8453 | -12.9463 | -13.7953 | -15.0106 | -16.327 | -17.8035 | -19.4014 | -20.9463 | -22.0821 | -26.3239 | -29.4831 | -31.8974 | -5.5504 | -6.2912 | -6.7239 | -7.5004 | -8.3331 | -9.2719 | -10.3168 | -11.3463 | -12.0698 | -15.279 | -18.778 | -24.4229 | -11.1239 | -12.129 | -12.7494 | -13.8208 | -14.9882 | -16.327 | -17.7933 | -19.1984 | -20.177 | -23.8402 | -26.4402 | -28.4647
|  | ST JOHNS PRIMARY | HT |  |  |  |  | -11.5872 | -12.5535 | -13.6433 | -14.8178 | -15.7637 | -17.1565 | -18.6065 | -20.0076 | -21.3157 | -26.4821 | -30.0974 | -32.1025 | -5.1474 | -5.6708 | -6.2606 | -6.8943 | -7.2514 | -7.9484 | -8.7096 | -9.4647 | -10.1984 | -12.9953 | -14.6035 | -15.38 | -10.7463 | -11.5525 | -12.479 | -13.4912 | -14.2443 | -15.4412 | -16.7076 | -17.9494 | -19.1321 | -23.8892 | -27.0045 | -28.6402
|  | ST JOHNS PRIMARY | HE |  |  |  |  | -11.5555 | -12.4872 | -13.5402 | -14.6759 | -15.5708 | -16.7882 | -18.0627 | -19.278 | -20.3953 | -24.6219 | -27.6178 | -28.9861 | -5.2402 | -5.8086 | -6.4433 | -7.13 | -7.531 | -8.2535 | -9.0453 | -9.8433 | -10.6249 | -14.2229 | -17.7055 | -22.9208 | -10.727 | -11.5035 | -12.3912 | -13.3637 | -14.0657 | -15.1096 | -16.2239 | -17.3025 | -18.3116 | -22.1872 | -24.678 | -25.7851
|  | ST JOHNS PRIMARY | CF |  |  |  |  | -11.2484 | -12.029 | -12.8249 | -13.7025 | -14.6525 | -15.1535 | -15.9657 | -16.73 | -17.4025 | -20.1596 | -23.1933 | -26.13 | -5.1055 | -5.6321 | -6.1453 | -6.727 | -7.378 | -7.7157 | -8.3882 | -9.0596 | -9.7229 | -13.5106 | -19.3208 | -29.9065 | -10.4606 | -11.131 | -11.7861 | -12.528 | -13.33 | -13.6423 | -14.3423 | -15.0219 | -15.6494 | -18.3994 | -21.0698 | -23.5321
COWLEY GSP | WITNEY BSP | STANDLAKE PRIMARY | MINIMUM HEADROOM | SP 38923 02349 | NO | NO | 1.357 | -0.63265 | -0.76939 | -0.88469 | -1.0347 | -1.1673 | -1.3929 | -1.6612 | -1.9347 | -2.0939 | -2.8408 | -3.2469 | -3.5561 | 1.1735 | 1.052 | 0.9602 | 0.82449 | 0.71122 | 0.54184 | 0.33163 | 0.12653 | 0.005102 | -0.60204 | -1.3806 | -3.0918 | 0.081633 | -0.056122 | -0.17959 | -0.34592 | -0.48469 | -0.70816 | -0.96531 | -1.2286 | -1.3765 | -2.052 | -2.3929 | -2.6337
|  | STANDLAKE PRIMARY | EE |  |  |  |  | -0.63265 | -0.76939 | -0.88469 | -1.0347 | -1.1673 | -1.3929 | -1.6612 | -1.9347 | -2.0939 | -2.8408 | -3.2265 | -3.451 | 1.1735 | 1.052 | 0.9602 | 0.82449 | 0.71122 | 0.54184 | 0.33163 | 0.12653 | 0.005102 | -0.60204 | -1.1684 | -2.0163 | 0.081633 | -0.056122 | -0.17959 | -0.34592 | -0.48469 | -0.70816 | -0.96531 | -1.2286 | -1.3765 | -2.052 | -2.3602 | -2.55
|  | STANDLAKE PRIMARY | HT |  |  |  |  | -0.57347 | -0.67245 | -0.78776 | -0.9102 | -1.0173 | -1.199 | -1.398 | -1.5735 | -1.7827 | -2.7694 | -3.2469 | -3.5561 | 1.2612 | 1.1939 | 1.1173 | 1.0255 | 0.96122 | 0.84082 | 0.69694 | 0.58878 | 0.44082 | -0.1898 | -0.44184 | -0.58571 | 0.14184 | 0.054082 | -0.04898 | -0.16122 | -0.26531 | -0.4449 | -0.65204 | -0.82041 | -1.0357 | -1.9806 | -2.3929 | -2.6337
|  | STANDLAKE PRIMARY | HE |  |  |  |  | -0.56939 | -0.66429 | -0.77347 | -0.89286 | -0.9949 | -1.1561 | -1.3418 | -1.502 | -1.6969 | -2.6898 | -3.0745 | -3.2643 | 1.2439 | 1.1684 | 1.0847 | 0.98673 | 0.90816 | 0.77959 | 0.62449 | 0.49898 | 0.33265 | -0.50102 | -1.0673 | -1.8929 | 0.14184 | 0.054082 | -0.04898 | -0.16327 | -0.27041 | -0.42551 | -0.60714 | -0.77857 | -0.97653 | -1.95 | -2.3051 | -2.4806
|  | STANDLAKE PRIMARY | CF |  |  |  |  | -0.51429 | -0.60102 | -0.67041 | -0.7551 | -0.84898 | -0.91837 | -1.0235 | -1.1357 | -1.2531 | -1.9612 | -2.551 | -3.0327 | 1.2755 | 1.202 | 1.1439 | 1.0663 | 0.97551 | 0.90306 | 0.78265 | 0.65612 | 0.52041 | -0.3051 | -1.3806 | -3.0918 | 0.20918 | 0.14184 | 0.081633 | -0.0030612 | -0.1 | -0.16327 | -0.28061 | -0.4051 | -0.53673 | -1.2378 | -1.7959 | -2.2908
MINETY GSP | STRATTON (RESERVE) BSP | STANTON FITZWARREN PRIMARY | MINIMUM HEADROOM | SU 17585 90987 | NO | YES | 8.078 | 9.2558 | 8.5762 | 7.8884 | 7.3619 | 6.2088 | 5.0027 | 3.8588 | 2.318 | 1.0813 | -4.0616 | -7.0208 | -8.482 | 8.8372 | 8.2035 | 7.7443 | 7.4474 | 6.6729 | 5.8382 | 4.88 | 3.7505 | 2.8402 | -1.4557 | -3.5455 | -9.4598 | 6.997 | 6.249 | 5.5929 | 5.2602 | 4.2051 | 3.098 | 2.0082 | 0.5827 | -0.65404 | -6.2949 | -8.9142 | -9.3836
|  | STANTON FITZWARREN PRIMARY | EE |  |  |  |  | 9.2558 | 8.5762 | 7.8884 | 7.418 | 6.4282 | 5.3486 | 3.8588 | 2.318 | 1.0813 | -3.7677 | -6.6249 | -8.2198 | 8.8372 | 8.2035 | 7.7443 | 7.4474 | 6.728 | 5.9596 | 4.88 | 3.7505 | 2.8443 | -0.69036 | -3.3914 | -6.4424 | 6.997 | 6.249 | 5.5929 | 5.2837 | 4.3756 | 3.3796 | 2.0082 | 0.5827 | -0.51424 | -4.8642 | -7.2938 | -8.6234
|  | STANTON FITZWARREN PRIMARY | HT |  |  |  |  | 9.4741 | 8.868 | 8.3037 | 7.3619 | 6.2088 | 5.0027 | 3.8721 | 2.4323 | 1.2394 | -3.9198 | -7.0208 | -8.482 | 9.0454 | 8.4994 | 8.1658 | 7.5117 | 6.6729 | 5.8382 | 5.0535 | 4.076 | 3.3576 | 0.57494 | -1.0802 | -1.7669 | 7.2807 | 6.6123 | 6.1174 | 5.2602 | 4.2051 | 3.098 | 2.0633 | 0.72453 | -0.34996 | -4.9173 | -7.603 | -8.804
|  | STANTON FITZWARREN PRIMARY | HE |  |  |  |  | 9.4833 | 8.8884 | 8.3435 | 7.6496 | 6.7078 | 5.7537 | 4.7772 | 3.4139 | 1.9282 | -4.0616 | -6.8687 | -7.4044 | 8.9678 | 8.3841 | 8.0066 | 7.5484 | 6.8505 | 6.1372 | 5.2913 | 4.03 | 2.8402 | -1.4557 | -3.3322 | -5.9689 | 7.2847 | 6.6215 | 6.1398 | 5.5266 | 4.5919 | 3.5531 | 2.2858 | 0.78678 | -0.65404 | -6.2949 | -8.9142 | -9.3836
|  | STANTON FITZWARREN PRIMARY | CF |  |  |  |  | 9.766 | 9.3017 | 8.866 | 8.3843 | 7.8292 | 7.3619 | 6.5568 | 5.9558 | 5.069 | 0.037392 | -3.9759 | -6.8646 | 9.1249 | 8.5984 | 8.2596 | 7.9025 | 7.48 | 7.0454 | 6.3607 | 5.7698 | 4.976 | 0.56066 | -3.5455 | -9.4598 | 7.5164 | 6.9776 | 6.5827 | 6.1684 | 5.6756 | 5.2296 | 4.4858 | 3.9327 | 2.947 | -2.4908 | -6.2744 | -8.9479
LALEHAM GSP | STAINES BSP | STANWELL PRIMARY | MINIMUM HEADROOM | TQ 06003 72766 | NO | NO | 10.58 | 11.8076 | 11.5719 | 11.3535 | 11.077 | 10.777 | 9.6545 | 8.7362 | 7.7453 | 6.7678 | 2.226 | -1.0516 | -3.1393 | 12.0994 | 11.9168 | 11.7413 | 11.5188 | 11.2647 | 10.1035 | 9.0596 | 8.0372 | 6.9821 | 2.9372 | -0.62404 | -5.8628 | 11.1556 | 10.8984 | 10.6627 | 10.3586 | 10.028 | 8.7484 | 7.7331 | 6.6209 | 5.5433 | 0.88412 | -2.4649 | -4.7332
|  | STANWELL PRIMARY | EE |  |  |  |  | 11.8076 | 11.5719 | 11.3535 | 11.077 | 10.777 | 9.6545 | 8.7362 | 7.7453 | 6.7678 | 3.0331 | 0.61167 | -1.6159 | 12.0994 | 11.9168 | 11.7413 | 11.5188 | 11.2647 | 10.1035 | 9.0596 | 8.0372 | 6.9821 | 2.9372 | -0.62404 | -5.8628 | 11.1556 | 10.8984 | 10.6627 | 10.3586 | 10.028 | 8.7484 | 7.7331 | 6.6209 | 5.5433 | 1.7953 | -0.50669 | -2.8914
|  | STANWELL PRIMARY | HT |  |  |  |  | 11.9362 | 11.7494 | 11.576 | 11.3627 | 11.126 | 10.1137 | 8.9178 | 7.9015 | 6.7953 | 2.226 | -1.0516 | -3.1393 | 12.2545 | 12.1515 | 12.0566 | 11.9311 | 11.7933 | 10.8219 | 9.6729 | 8.7586 | 7.7045 | 3.7821 | 1.0209 | -0.83731 | 11.3168 | 11.13 | 10.9617 | 10.7423 | 10.4964 | 9.3627 | 8.0056 | 6.876 | 5.6331 | 0.88412 | -2.4649 | -4.7332
|  | STANWELL PRIMARY | HE |  |  |  |  | 11.9504 | 11.779 | 11.6198 | 11.4198 | 11.2045 | 10.4739 | 9.5453 | 8.9341 | 8.2678 | 5.0423 | 2.5964 | 0.828 | 12.1882 | 12.0484 | 11.9096 | 11.7362 | 11.5413 | 10.7933 | 9.8423 | 9.2698 | 8.6035 | 4.9627 | 1.3331 | -3.7312 | 11.329 | 11.1535 | 10.9994 | 10.7953 | 10.5709 | 9.7627 | 8.7147 | 8.0678 | 7.3494 | 4.1096 | 1.7188 | -0.25261
|  | STANWELL PRIMARY | CF |  |  |  |  | 12.1086 | 12.0127 | 11.9117 | 11.8249 | 11.7066 | 11.2851 | 10.727 | 10.2056 | 9.7566 | 8.1984 | 6.5239 | 4.9872 | 12.2525 | 12.1351 | 12.0066 | 11.8729 | 11.6923 | 11.1188 | 10.3556 | 9.6566 | 9.0066 | 6.3321 | 2.0321 | -5.4944 | 11.4729 | 11.3678 | 11.2535 | 11.1668 | 11.0351 | 10.53 | 9.8596 | 9.2331 | 8.7015 | 7.1392 | 5.6484 | 4.3831
MANNINGTON GSP | SALISBURY BSP | STAPLEFORD PRIMARY | MINIMUM HEADROOM | SU 06871 37078 | NO | NO | 1.583 | 8.3499 | 8.204 | 8.0132 | 7.853 | 7.6346 | 7.354 | 7.0193 | 7.2019 | 7.0274 | 6.0642 | 5.6142 | 5.3887 | 8.4693 | 8.3652 | 8.2295 | 8.1111 | 7.957 | 7.756 | 7.5162 | 7.6111 | 7.4978 | 6.8111 | 5.9448 | 3.9693 | 8.0672 | 7.9254 | 7.7417 | 7.5876 | 7.3632 | 7.0815 | 6.7407 | 6.9815 | 6.8203 | 5.9999 | 5.5938 | 5.3713
|  | STAPLEFORD PRIMARY | EE |  |  |  |  | 8.3499 | 8.204 | 8.0132 | 7.853 | 7.6346 | 7.354 | 7.0193 | 7.2019 | 7.054 | 6.1438 | 5.7815 | 5.5458 | 8.4693 | 8.3652 | 8.2295 | 8.1111 | 7.957 | 7.756 | 7.5162 | 7.6111 | 7.4978 | 6.8519 | 6.2274 | 5.254 | 8.0672 | 7.9254 | 7.7417 | 7.5876 | 7.3632 | 7.0815 | 6.7407 | 6.9815 | 6.8448 | 6.0846 | 5.7836 | 5.5907
|  | STAPLEFORD PRIMARY | HT |  |  |  |  | 8.4642 | 8.3601 | 8.2162 | 8.1019 | 7.9417 | 7.7223 | 7.5387 | 7.2897 | 7.0274 | 6.2948 | 5.7744 | 5.3927 | 8.5734 | 8.5091 | 8.4162 | 8.353 | 8.2509 | 8.1142 | 8.005 | 7.8427 | 7.6713 | 7.3111 | 7.0438 | 6.8611 | 8.1815 | 8.0815 | 7.9458 | 7.8397 | 7.6876 | 7.4785 | 7.3081 | 7.0693 | 6.8203 | 6.2203 | 5.7621 | 5.4458
|  | STAPLEFORD PRIMARY | HE |  |  |  |  | 8.4652 | 8.3632 | 8.2223 | 8.1152 | 7.9591 | 7.7519 | 7.5785 | 7.3417 | 7.0927 | 6.0642 | 5.6142 | 5.3887 | 8.553 | 8.4764 | 8.3785 | 8.2999 | 8.1866 | 8.0387 | 7.9091 | 7.7346 | 7.5509 | 6.9274 | 6.2856 | 5.3295 | 8.1815 | 8.0836 | 7.9519 | 7.8499 | 7.7009 | 7.506 | 7.3438 | 7.1172 | 6.8815 | 5.9999 | 5.5938 | 5.3713
|  | STAPLEFORD PRIMARY | CF |  |  |  |  | 8.5193 | 8.4305 | 8.3285 | 8.2111 | 8.1244 | 7.9907 | 7.8397 | 7.6774 | 7.5754 | 6.654 | 6.3132 | 5.6856 | 8.5846 | 8.5183 | 8.4407 | 8.3478 | 8.2734 | 8.1581 | 8.0244 | 7.8815 | 7.7703 | 6.8111 | 5.9448 | 3.9693 | 8.2315 | 8.1509 | 8.056 | 7.9427 | 7.8621 | 7.7356 | 7.5907 | 7.4346 | 7.3417 | 6.4591 | 6.1805 | 5.6203
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH PRIMARY | MINIMUM HEADROOM | SU 77124 94355 | NO | NO | 5.149 | -1.9837 | -2.2674 | -2.5204 | -2.848 | -3.1949 | -3.2725 | -3.749 | -4.2327 | -4.5653 | -6.3133 | -7.5021 | -8.2245 | 0.35303 | 0.11936 | -0.083706 | -0.35513 | -0.64697 | -0.59799 | -0.94595 | -1.3011 | -1.5204 | -2.8408 | -4.4735 | -8.3245 | -1.7021 | -1.9929 | -2.2398 | -2.5725 | -2.9276 | -2.8919 | -3.3449 | -3.8021 | -4.0847 | -5.6439 | -6.697 | -7.3215
|  | STOKENCHURCH PRIMARY | EE |  |  |  |  | -1.9837 | -2.2674 | -2.5204 | -2.848 | -3.1949 | -3.2725 | -3.749 | -4.2327 | -4.5653 | -6.3133 | -7.3715 | -8.0674 | 0.35303 | 0.11936 | -0.083706 | -0.35513 | -0.64697 | -0.59799 | -0.94595 | -1.3011 | -1.5204 | -2.8408 | -4.1776 | -6.1643 | -1.7021 | -1.9929 | -2.2398 | -2.5725 | -2.9276 | -2.8919 | -3.3449 | -3.8021 | -4.0847 | -5.6439 | -6.5735 | -7.1817
|  | STOKENCHURCH PRIMARY | HT |  |  |  |  | -1.8153 | -2 | -2.2204 | -2.4664 | -2.6817 | -3.0878 | -3.5388 | -4.0204 | -4.0725 | -6.2317 | -7.5021 | -8.2245 | 0.53568 | 0.42752 | 0.2714 | 0.10201 | -0.037788 | -0.28473 | -0.57146 | -0.88167 | -0.7633 | -1.9429 | -2.55 | -2.8704 | -1.5102 | -1.6847 | -1.9011 | -2.1429 | -2.3408 | -2.7184 | -3.1521 | -3.6123 | -3.5653 | -5.5623 | -6.697 | -7.3215
|  | STOKENCHURCH PRIMARY | HE |  |  |  |  | -1.8092 | -1.9847 | -2.197 | -2.4286 | -2.6266 | -2.9868 | -3.3929 | -3.8245 | -3.8266 | -5.8021 | -6.8255 | -7.2796 | 0.50099 | 0.37344 | 0.21017 | 0.027518 | -0.13064 | -0.38881 | -0.69289 | -1.0225 | -0.96024 | -2.5368 | -3.8837 | -5.7511 | -1.5041 | -1.6715 | -1.8796 | -2.1072 | -2.2898 | -2.6276 | -3.0194 | -3.4378 | -3.3368 | -5.1653 | -6.0684 | -6.4562
|  | STOKENCHURCH PRIMARY | CF |  |  |  |  | -1.6939 | -1.8388 | -1.9551 | -2.1133 | -2.2796 | -2.4204 | -2.6388 | -2.8766 | -3.1245 | -4.1439 | -5.3592 | -6.4368 | 0.55507 | 0.43364 | 0.3316 | 0.1867 | 0.015273 | -0.13881 | -0.3684 | -0.6184 | -0.88779 | -2.1735 | -4.4735 | -8.3245 | -1.4051 | -1.55 | -1.6602 | -1.8174 | -1.9878 | -2.1225 | -2.3429 | -2.5837 | -2.8378 | -3.6919 | -4.7582 | -5.7378
MINETY GSP | STRATTON (RESERVE) BSP | STRATTON PRIMARY | MINIMUM HEADROOM | SU 16998 88837 | NO | YES | 19.329 | -0.11336 | -0.86948 | -1.7389 | -2.6266 | -4.3634 | -5.9225 | -7.6746 | -9.5246 | -11.043 | -15.4358 | -18.0827 | -19.2756 | 3.7591 | 3.256 | 2.6897 | 2.3081 | 1.206 | 0.051947 | -1.3185 | -2.644 | -3.7001 | -7.0654 | -10.3409 | -18.3634 | 1.7091 | 0.99276 | 0.17338 | -0.34805 | -1.846 | -3.2154 | -4.9644 | -6.6368 | -7.9348 | -11.743 | -14.0532 | -14.994
|  | STRATTON PRIMARY | EE |  |  |  |  | -0.11336 | -0.86948 | -1.7389 | -2.4134 | -3.9868 | -5.7287 | -7.6736 | -9.5246 | -11.043 | -15.4358 | -17.8389 | -18.8052 | 3.7591 | 3.256 | 2.6897 | 2.3081 | 1.2142 | 0.051947 | -1.3185 | -2.644 | -3.7001 | -7.0654 | -9.8889 | -13.6766 | 1.7091 | 0.99276 | 0.17338 | -0.31234 | -1.6817 | -3.2154 | -4.9644 | -6.6368 | -7.9348 | -11.6266 | -13.5348 | -14.3297
|  | STRATTON PRIMARY | HT |  |  |  |  | 0.13154 | -0.54193 | -1.2817 | -2.6266 | -4.3634 | -5.9225 | -7.6746 | -9.2817 | -10.6093 | -15.2807 | -18.0827 | -19.2756 | 4.0489 | 3.6703 | 3.2703 | 2.3601 | 1.206 | 0.26215 | -0.85724 | -1.8685 | -2.6307 | -5.1409 | -6.5593 | -7.2154 | 2.0387 | 1.4428 | 0.81113 | -0.34805 | -1.846 | -3.097 | -4.6205 | -6.0276 | -7.1981 | -11.3746 | -13.7225 | -14.6542
|  | STRATTON PRIMARY | HE |  |  |  |  | 0.14787 | -0.51132 | -1.2378 | -2.096 | -3.6083 | -4.9399 | -6.6848 | -8.3695 | -9.9236 | -14.5144 | -16.994 | -17.9654 | 3.9652 | 3.5366 | 3.0856 | 2.5509 | 1.507 | 0.64787 | -0.58989 | -1.8103 | -2.9246 | -6.6644 | -9.6256 | -13.4062 | 2.0458 | 1.4591 | 0.83766 | 0.088682 | -1.2052 | -2.2603 | -3.7766 | -5.2593 | -6.6317 | -11.743 | -14.0532 | -14.994
|  | STRATTON PRIMARY | CF |  |  |  |  | 0.46929 | 0.017253 | -0.52458 | -1.1113 | -1.9103 | -2.8654 | -3.9685 | -4.8715 | -5.9807 | -10.2654 | -13.445 | -16.397 | 4.1162 | 3.7928 | 3.4091 | 3.005 | 2.4581 | 1.7111 | 0.80093 | 0.014192 | -0.94295 | -5.397 | -10.3409 | -18.3634 | 2.307 | 1.9152 | 1.4346 | 0.93766 | 0.25603 | -0.56846 | -1.543 | -2.2123 | -3.195 | -7.2021 | -10.694 | -13.4685
LALEHAM GSP | STAINES BSP | SUNBURY CROSS PRIMARY | MINIMUM HEADROOM | TQ 10053 69996 | NO | NO | 11.081 | 14.2607 | 13.3117 | 12.2464 | 10.9913 | 9.4474 | 7.1597 | 4.5678 | 2.1035 | 0.30049 | -8.6954 | -16.4495 | -20.6791 | 21.7413 | 20.9046 | 19.9587 | 18.8668 | 17.624 | 16.025 | 14.1719 | 12.3495 | 10.9995 | 3.7525 | -5.5107 | -27.025 | 14.3913 | 13.3831 | 12.2433 | 10.9464 | 9.4689 | 7.3556 | 4.9342 | 2.6127 | 0.99743 | -6.7128 | -12.8679 | -16.5097
|  | SUNBURY CROSS PRIMARY | EE |  |  |  |  | 14.2607 | 13.3117 | 12.2464 | 10.9913 | 9.4474 | 7.1597 | 4.5678 | 2.1035 | 0.30049 | -8.6954 | -15.3199 | -20.3373 | 21.7413 | 20.9046 | 19.9587 | 18.8668 | 17.624 | 16.025 | 14.1719 | 12.3495 | 10.9995 | 3.7525 | -3.6158 | -14.6424 | 14.3913 | 13.3831 | 12.2433 | 10.9464 | 9.4689 | 7.3556 | 4.9342 | 2.6127 | 0.99743 | -6.7128 | -11.9016 | -16.2618
|  | SUNBURY CROSS PRIMARY | HT |  |  |  |  | 14.6199 | 13.7087 | 13.0076 | 11.9199 | 10.7291 | 8.7576 | 6.8199 | 4.8291 | 2.8005 | -8.6638 | -16.4495 | -20.6791 | 22.3444 | 21.728 | 21.3423 | 20.6178 | 19.8148 | 18.7199 | 17.5627 | 16.3444 | 15.0903 | 8.7944 | 5.174 | 3.4893 | 14.8689 | 13.9617 | 13.3872 | 12.3433 | 11.1882 | 9.428 | 7.6178 | 5.7342 | 3.7923 | -6.4373 | -12.8679 | -16.5097
|  | SUNBURY CROSS PRIMARY | HE |  |  |  |  | 14.5995 | 13.7495 | 13.126 | 12.1546 | 10.9913 | 9.2484 | 7.2842 | 5.3872 | 3.5087 | -6.7811 | -14.0016 | -16.9516 | 22.0954 | 21.377 | 20.8872 | 20.0597 | 19.0821 | 17.8433 | 16.3995 | 14.9209 | 13.3872 | 4.7291 | -3.2465 | -13.5424 | 14.8362 | 13.977 | 13.4648 | 12.5158 | 11.3933 | 9.8117 | 7.9882 | 6.1852 | 4.3678 | -4.8454 | -10.7893 | -13.3209
|  | SUNBURY CROSS PRIMARY | CF |  |  |  |  | 15.3454 | 14.925 | 14.4607 | 14.2648 | 13.7801 | 13.2015 | 12.4321 | 11.5097 | 10.4587 | 3.0964 | -3.9689 | -10.3342 | 22.4678 | 21.9515 | 21.378 | 21.0331 | 20.325 | 19.4842 | 18.4484 | 17.2903 | 16.0515 | 7.3117 | -5.5107 | -27.025 | 15.5015 | 15.0178 | 14.4923 | 14.3566 | 13.8199 | 13.2015 | 12.3852 | 11.4382 | 10.4372 | 3.6219 | -2.6056 | -7.9383
FLEET-BRAMLEY GSP | BRACKNELL BSP | SUNNINGHILL PRIMARY | MINIMUM HEADROOM | SU 93757 67606 | NO | NO | 1.551 | 12.0633 | 11.7847 | 11.5286 | 11.2 | 10.8082 | 10.2755 | 10.1449 | 9.6163 | 9.2449 | 7.6173 | 6.4276 | 6.1306 | 13.9559 | 13.7243 | 13.5171 | 13.2457 | 12.9069 | 12.51 | 12.4569 | 12.0631 | 11.7947 | 10.4539 | 8.7161 | 4.3386 | 12.3147 | 12.0443 | 11.8035 | 11.4871 | 11.0933 | 10.5871 | 10.5167 | 10.029 | 9.6861 | 8.1963 | 7.1524 | 6.9055
|  | SUNNINGHILL PRIMARY | EE |  |  |  |  | 12.0633 | 11.7847 | 11.5286 | 11.2 | 10.8082 | 10.2755 | 10.1449 | 9.6163 | 9.2449 | 7.6173 | 6.6031 | 6.5163 | 13.9559 | 13.7243 | 13.5171 | 13.2457 | 12.9069 | 12.51 | 12.4569 | 12.0631 | 11.7947 | 10.4539 | 9.0916 | 7.1549 | 12.3147 | 12.0443 | 11.8035 | 11.4871 | 11.0933 | 10.5871 | 10.5167 | 10.029 | 9.6861 | 8.1963 | 7.3127 | 7.2412
|  | SUNNINGHILL PRIMARY | HT |  |  |  |  | 12.2296 | 12.0102 | 11.8204 | 11.5224 | 11.2786 | 10.8684 | 10.4122 | 9.9184 | 9.8173 | 7.7061 | 6.4276 | 6.1306 | 14.1437 | 13.9978 | 13.8753 | 13.6498 | 13.4824 | 13.2314 | 12.9467 | 12.6284 | 12.6518 | 11.4457 | 10.8182 | 10.6518 | 12.4912 | 12.2851 | 12.1086 | 11.8127 | 11.58 | 11.2076 | 10.7861 | 10.331 | 10.2453 | 8.2953 | 7.1524 | 6.9055
|  | SUNNINGHILL PRIMARY | HE |  |  |  |  | 12.2878 | 12.0429 | 11.8724 | 11.6459 | 11.4061 | 11.0306 | 10.6143 | 10.1694 | 10.1286 | 8.4633 | 7.5388 | 7.2735 | 14.1243 | 13.9355 | 13.7906 | 13.6008 | 13.3916 | 13.1161 | 12.7957 | 12.4539 | 12.4498 | 10.9222 | 9.5396 | 7.5896 | 12.5341 | 12.3086 | 12.1494 | 11.9341 | 11.7035 | 11.3565 | 10.9667 | 10.5535 | 10.53 | 8.9922 | 8.1637 | 7.9402
|  | SUNNINGHILL PRIMARY | CF |  |  |  |  | 12.4306 | 12.2745 | 12.1806 | 12.0429 | 11.8908 | 11.749 | 11.5347 | 11.3051 | 11.0612 | 10.1041 | 8.7714 | 7.5714 | 14.1886 | 14.0416 | 13.9294 | 13.7784 | 13.6029 | 13.4182 | 13.1641 | 12.8916 | 12.6039 | 11.1876 | 8.7161 | 4.3386 | 12.6596 | 12.5127 | 12.4188 | 12.2831 | 12.1341 | 11.9953 | 11.781 | 11.5514 | 11.3096 | 10.4494 | 9.2708 | 8.1851
MELKSHAM GSP | CHIPPENHAM BSP | SUTTON BENGER PRIMARY | MINIMUM HEADROOM | ST 93394 80051 | NO | YES | 9.422 | 2.2377 | 2.104 | 1.9469 | 1.804 | 1.6428 | 1.4795 | 1.3398 | 1.1642 | 1.0653 | 0.53771 | 0.29485 | 0.058118 | 2.8244 | 2.7377 | 2.6336 | 2.5428 | 2.4316 | 2.3051 | 2.202 | 2.0642 | 1.9949 | 1.6091 | 1.0244 | -0.17964 | 2.3255 | 2.203 | 2.0591 | 1.9357 | 1.7877 | 1.6285 | 1.4908 | 1.3051 | 1.2183 | 0.78261 | 0.57853 | 0.38261
|  | SUTTON BENGER PRIMARY | EE |  |  |  |  | 2.2377 | 2.104 | 1.9469 | 1.804 | 1.6428 | 1.4795 | 1.3398 | 1.1642 | 1.0653 | 0.53771 | 0.29996 | 0.16118 | 2.8244 | 2.7377 | 2.6336 | 2.5428 | 2.4316 | 2.3051 | 2.202 | 2.0642 | 1.9949 | 1.6091 | 1.2346 | 0.64587 | 2.3255 | 2.203 | 2.0591 | 1.9357 | 1.7877 | 1.6285 | 1.4908 | 1.3051 | 1.2183 | 0.78261 | 0.57853 | 0.46526
|  | SUTTON BENGER PRIMARY | HT |  |  |  |  | 2.2959 | 2.1489 | 2.0091 | 1.8846 | 1.7724 | 1.6765 | 1.5387 | 1.3949 | 1.2418 | 0.61118 | 0.29485 | 0.058118 | 2.8898 | 2.804 | 2.7316 | 2.6663 | 2.5949 | 2.5469 | 2.4581 | 2.3642 | 2.2591 | 1.8887 | 1.7214 | 1.601 | 2.3826 | 2.253 | 2.1357 | 2.0244 | 1.9193 | 1.8326 | 1.701 | 1.5673 | 1.4224 | 0.85098 | 0.57955 | 0.38261
|  | SUTTON BENGER PRIMARY | HE |  |  |  |  | 2.2949 | 2.1744 | 2.0622 | 1.9224 | 1.7857 | 1.6898 | 1.553 | 1.4122 | 1.2663 | 0.57955 | 0.34383 | 0.2224 | 2.8734 | 2.7959 | 2.7285 | 2.6408 | 2.5551 | 2.4908 | 2.3928 | 2.2877 | 2.1693 | 1.6346 | 1.252 | 0.67547 | 2.3816 | 2.2744 | 2.1765 | 2.052 | 1.9316 | 1.8449 | 1.7153 | 1.5836 | 1.4459 | 0.82036 | 0.61934 | 0.52342
|  | SUTTON BENGER PRIMARY | CF |  |  |  |  | 2.3183 | 2.2551 | 2.2 | 2.1275 | 2.053 | 1.9724 | 1.902 | 1.7846 | 1.6622 | 1.0704 | 0.66934 | 0.31016 | 2.8816 | 2.8346 | 2.7938 | 2.7357 | 2.6765 | 2.603 | 2.5387 | 2.4428 | 2.3387 | 1.7438 | 1.0244 | -0.17964 | 2.403 | 2.3428 | 2.2908 | 2.2255 | 2.1571 | 2.0826 | 2.0183 | 1.9132 | 1.801 | 1.2459 | 0.89689 | 0.58465
IVER 132KV GSP | UPTON BSP | SUTTON LANE PRIMARY | MINIMUM HEADROOM | TQ 02185 78595 | NO | YES | 1.666 | 13.9221 | 13.6232 | 13.264 | 12.8038 | 12.3099 | 12.1813 | 11.5803 | 10.9752 | 10.5364 | 8.7966 | 7.7211 | 7.4732 | 16.3752 | 16.0966 | 15.7915 | 15.4109 | 15.0007 | 14.8477 | 14.3558 | 13.8497 | 13.4609 | 11.3844 | 7.2803 | -0.97684 | 14.7099 | 14.4109 | 14.0711 | 13.6344 | 13.163 | 13.0252 | 12.4568 | 11.8874 | 11.4783 | 9.5885 | 8.4487 | 8.1385
|  | SUTTON LANE PRIMARY | EE |  |  |  |  | 13.9221 | 13.6232 | 13.264 | 12.8038 | 12.3099 | 12.1813 | 11.5803 | 10.9752 | 10.5364 | 8.7966 | 7.915 | 8.1181 | 16.3752 | 16.0966 | 15.7915 | 15.4109 | 15.0007 | 14.8477 | 14.3558 | 13.8497 | 13.4609 | 11.3844 | 9.0415 | 5.3579 | 14.7099 | 14.4109 | 14.0711 | 13.6344 | 13.163 | 13.0252 | 12.4568 | 11.8874 | 11.4783 | 9.9303 | 9.1619 | 9.3415
|  | SUTTON LANE PRIMARY | HT |  |  |  |  | 14.1068 | 13.915 | 13.6609 | 13.3446 | 13.0364 | 12.6211 | 12.1099 | 11.567 | 11.4119 | 9.0181 | 7.7211 | 7.6313 | 16.6466 | 16.4834 | 16.3119 | 16.0793 | 15.865 | 15.5895 | 15.2517 | 14.8915 | 14.8436 | 13.3538 | 12.6211 | 12.4405 | 14.9497 | 14.7364 | 14.4936 | 14.1752 | 13.8762 | 13.464 | 12.9844 | 12.4721 | 12.3497 | 10.1579 | 8.9905 | 8.9252
|  | SUTTON LANE PRIMARY | HE |  |  |  |  | 14.1038 | 13.9191 | 13.6721 | 13.3579 | 13.0548 | 12.6568 | 12.1823 | 11.6558 | 11.4711 | 9.014 | 7.7997 | 7.4732 | 16.5619 | 16.3609 | 16.1364 | 15.8507 | 15.5772 | 15.2252 | 14.8028 | 14.3446 | 14.1609 | 11.7109 | 9.1946 | 5.3507 | 14.9456 | 14.7415 | 14.5048 | 14.1946 | 13.9048 | 13.514 | 13.0466 | 12.5477 | 12.1487 | 9.5885 | 8.4487 | 8.1385
|  | SUTTON LANE PRIMARY | CF |  |  |  |  | 14.2834 | 14.1885 | 14.063 | 13.9374 | 13.6762 | 13.4293 | 13.2334 | 12.964 | 12.6834 | 11.3895 | 9.4579 | 7.8599 | 16.6446 | 16.4854 | 16.2956 | 16.1119 | 15.8221 | 15.5007 | 15.1844 | 14.8089 | 14.4028 | 11.9038 | 7.2803 | -0.97684 | 15.1079 | 14.9926 | 14.8446 | 14.717 | 14.4823 | 14.2456 | 14.0579 | 13.7946 | 13.5211 | 12.015 | 10.0558 | 8.5119
MANNINGTON GSP | WAREHAM BSP | SWANAGE PRIMARY | MINIMUM HEADROOM | SZ 02010 79296 | NO | YES | 1.205 | 2.8214 | 27.6398 | 27.1796 | 26.5949 | 26.298 | 25.4204 | 24.5541 | 23.7133 | 23.0745 | 19.6684 | 16.752 | 15.2082 | 4.7949 | 27.899 | 27.5357 | 27.0816 | 26.8837 | 26.299 | 25.6806 | 25.0633 | 24.599 | 22.0296 | 19.3153 | 11.9918 | 2.8959 | 26.9153 | 26.448 | 25.8684 | 25.6551 | 24.8439 | 24.0143 | 23.202 | 22.6173 | 19.7041 | 17.0949 | 15.7643
|  | SWANAGE PRIMARY | EE |  |  |  |  | 2.8214 | 27.6398 | 27.1796 | 26.5949 | 26.298 | 25.4204 | 24.5541 | 23.7133 | 23.0745 | 19.7398 | 17.3724 | 15.4622 | 4.7949 | 27.899 | 27.5357 | 27.0816 | 26.8837 | 26.299 | 25.6806 | 25.0633 | 24.599 | 22.0296 | 19.3735 | 15.3755 | 2.8959 | 26.9153 | 26.448 | 25.8684 | 25.6551 | 24.8439 | 24.0143 | 23.202 | 22.6173 | 19.7235 | 17.6694 | 15.9898
|  | SWANAGE PRIMARY | HT |  |  |  |  | 3.0694 | 27.9745 | 27.6245 | 27.2133 | 26.6429 | 25.8031 | 25.3459 | 24.5969 | 23.8255 | 19.6684 | 16.752 | 15.2082 | 5.0663 | 28.2867 | 28.0571 | 27.8051 | 27.4551 | 26.9929 | 26.8061 | 26.3724 | 25.9235 | 23.6663 | 22.2551 | 21.598 | 3.1765 | 27.2908 | 26.9469 | 26.5633 | 26.0316 | 25.2663 | 24.9122 | 24.2122 | 23.4857 | 19.7041 | 17.0949 | 15.7643
|  | SWANAGE PRIMARY | HE |  |  |  |  | 3.0908 | 28.0245 | 27.7051 | 27.3306 | 26.8092 | 26.0949 | 25.7694 | 25.1643 | 24.5388 | 21.1786 | 18.8827 | 17.852 | 5.0133 | 28.2071 | 27.9592 | 27.6745 | 27.2959 | 26.8204 | 26.6173 | 26.1684 | 25.6939 | 22.9337 | 20.252 | 16.6714 | 3.1939 | 27.3357 | 27.0204 | 26.6755 | 26.1867 | 25.5347 | 25.2959 | 24.7255 | 24.1337 | 21.0806 | 19.0816 | 18.2143
|  | SWANAGE PRIMARY | CF |  |  |  |  | 3.3296 | 28.3714 | 28.1806 | 27.9031 | 27.5816 | 27.2296 | 26.9071 | 26.5878 | 26.6337 | 24.548 | 22.2061 | 19.952 | 5.1306 | 28.3673 | 28.1745 | 27.9184 | 27.6184 | 27.2653 | 26.8898 | 26.501 | 26.3857 | 23.6439 | 19.3153 | 11.9918 | 3.4163 | 27.6561 | 27.4622 | 27.1959 | 26.9092 | 26.5776 | 26.2541 | 25.9245 | 26.0153 | 23.9949 | 21.9071 | 19.9949
MINETY GSP | SWINDON BSP | SWINDON PRIMARY | MINIMUM HEADROOM | SU 12449 86967 | NO | NO | 4.686 | 23.0192 | 22.0212 | 20.9151 | 19.7845 | 18.2437 | 15.9437 | 13.3508 | 10.7784 | 8.9294 | -0.23389 | -7.5921 | -11.2063 | 26.4171 | 25.6202 | 24.7396 | 23.7886 | 22.4386 | 20.7886 | 18.8804 | 16.962 | 15.5977 | 8.5661 | -0.97777 | -23.0921 | 20.3171 | 19.3457 | 18.262 | 17.1335 | 15.5886 | 13.4161 | 10.9386 | 8.4835 | 6.8314 | -0.90532 | -7.3227 | -10.3339
|  | SWINDON PRIMARY | EE |  |  |  |  | 23.0192 | 22.0212 | 20.9151 | 19.7845 | 18.2437 | 15.9437 | 13.3508 | 10.7784 | 8.9294 | 0.17427 | -6.3441 | -10.1308 | 26.4171 | 25.6202 | 24.7396 | 23.7886 | 22.4386 | 20.7886 | 18.8804 | 16.962 | 15.5977 | 8.5661 | 0.76713 | -10.437 | 20.3171 | 19.3457 | 18.262 | 17.1335 | 15.5886 | 13.4161 | 10.9386 | 8.4835 | 6.8314 | -0.63185 | -6.2318 | -9.4472
|  | SWINDON PRIMARY | HT |  |  |  |  | 23.2233 | 22.6161 | 21.7988 | 20.5426 | 19.2488 | 17.1967 | 15.0141 | 12.809 | 10.6753 | -0.23389 | -7.5921 | -11.2063 | 26.8641 | 26.5457 | 26.0406 | 25.1212 | 24.1926 | 23.0008 | 21.711 | 20.4049 | 19.1651 | 13.3641 | 9.8345 | 8.1233 | 20.5784 | 20.063 | 19.2896 | 18.0733 | 16.8314 | 14.9692 | 12.963 | 10.9253 | 8.9406 | -0.90532 | -7.3227 | -10.3339
|  | SWINDON PRIMARY | HE |  |  |  |  | 23.3957 | 22.9049 | 22.1324 | 21.2835 | 20.0957 | 18.3886 | 16.4692 | 14.5028 | 12.5569 | 3.412 | -3.0339 | -5.9033 | 26.7161 | 26.313 | 25.6886 | 24.9814 | 23.9141 | 22.659 | 21.211 | 19.6998 | 18.1773 | 10.2386 | 2.2988 | -8.4441 | 20.711 | 20.2947 | 19.5671 | 18.761 | 17.5988 | 16.0243 | 14.2345 | 12.3947 | 10.5641 | 2.261 | -3.2584 | -5.64
|  | SWINDON PRIMARY | CF |  |  |  |  | 24.0712 | 23.6233 | 23.4722 | 22.9977 | 22.4682 | 21.7498 | 20.8865 | 19.9222 | 18.9641 | 12.4161 | 5.3794 | -1.3604 | 27.012 | 26.5018 | 26.2202 | 25.6488 | 24.9641 | 24.0243 | 22.909 | 21.6957 | 20.4365 | 11.9039 | -0.97777 | -23.0921 | 21.3222 | 20.8528 | 20.7559 | 20.2886 | 19.7671 | 19.0539 | 18.1896 | 17.2324 | 16.2784 | 9.9845 | 3.8498 | -1.7798
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | TADLEY PRIMARY | MINIMUM HEADROOM | SU 57753 62717 | NO | NO | 2.203 | 14.4246 | 14.1614 | 13.84 | 13.4889 | 13.4767 | 12.9134 | 12.2757 | 11.6338 | 11.1726 | 8.4655 | 6.5134 | 5.4093 | 16.8838 | 16.6532 | 16.3593 | 16.0267 | 16.0542 | 15.6553 | 15.191 | 14.7226 | 14.4073 | 12.6593 | 10.3787 | 4.894 | 15.0185 | 14.7348 | 14.3859 | 13.9971 | 14.0359 | 13.4991 | 12.8889 | 12.2787 | 11.8685 | 9.6685 | 7.9797 | 6.9889
|  | TADLEY PRIMARY | EE |  |  |  |  | 14.4246 | 14.1614 | 13.84 | 13.4889 | 13.4767 | 12.9134 | 12.2757 | 11.6338 | 11.1726 | 8.6889 | 6.9389 | 5.6461 | 16.8838 | 16.6532 | 16.3593 | 16.0267 | 16.0542 | 15.6553 | 15.191 | 14.7226 | 14.4073 | 12.6593 | 10.8287 | 8.0104 | 15.0185 | 14.7348 | 14.3859 | 13.9971 | 14.0359 | 13.4991 | 12.8889 | 12.2787 | 11.8685 | 9.8216 | 8.3614 | 7.2022
|  | TADLEY PRIMARY | HT |  |  |  |  | 14.5787 | 14.3573 | 14.094 | 13.8614 | 13.5644 | 12.993 | 12.6961 | 12.1246 | 11.5389 | 8.4655 | 6.5134 | 5.4093 | 17.1155 | 16.9746 | 16.7838 | 16.6308 | 16.4104 | 16.0859 | 16.0338 | 15.7002 | 15.3604 | 13.7502 | 12.9165 | 12.4757 | 15.2246 | 15.0083 | 14.74 | 14.5063 | 14.1991 | 13.6665 | 13.4808 | 12.9512 | 12.4022 | 9.6685 | 7.9797 | 6.9889
|  | TADLEY PRIMARY | HE |  |  |  |  | 14.6042 | 14.4012 | 14.1583 | 13.9461 | 13.6685 | 13.2063 | 13.0114 | 12.541 | 12.0553 | 9.39 | 7.5767 | 6.7389 | 17.0736 | 16.9063 | 16.6981 | 16.5083 | 16.2563 | 15.9134 | 15.841 | 15.4848 | 15.1063 | 12.9848 | 11.0746 | 8.4144 | 15.241 | 15.041 | 14.792 | 14.5757 | 14.2889 | 13.842 | 13.7369 | 13.2879 | 12.8206 | 10.4348 | 8.9093 | 8.1512
|  | TADLEY PRIMARY | CF |  |  |  |  | 14.7879 | 14.6726 | 14.5297 | 14.3787 | 14.2512 | 14.0644 | 13.8369 | 13.5889 | 13.6767 | 11.9379 | 10.094 | 8.3104 | 17.1563 | 17.0257 | 16.8624 | 16.6787 | 16.5134 | 16.2655 | 15.9634 | 15.642 | 15.6512 | 13.5134 | 10.3787 | 4.894 | 15.4083 | 15.2889 | 15.1318 | 14.9624 | 14.8257 | 14.6236 | 14.3706 | 14.0951 | 14.24 | 12.5624 | 10.943 | 9.5134
IVER 132KV GSP | SLOUGH BSP | TAPLOW PRIMARY | MINIMUM HEADROOM | SU 91721 81234 | NO | YES | 0.881 | 14.1122 | 13.6633 | 13.1673 | 13.0663 | 12.5827 | 11.802 | 10.9051 | 10.002 | 9.3653 | 6.5347 | 4.5 | 3.9663 | 16.9898 | 16.5878 | 16.1418 | 16.0102 | 15.55 | 14.9357 | 14.2173 | 13.4816 | 12.9388 | 9.8755 | 3.9439 | -8.4112 | 14.499 | 14.0398 | 13.5347 | 13.5224 | 13.0459 | 12.3204 | 11.4765 | 10.6276 | 10.0429 | 7.4908 | 5.6847 | 5.2204
|  | TAPLOW PRIMARY | EE |  |  |  |  | 14.1122 | 13.6633 | 13.1673 | 13.0663 | 12.5827 | 11.802 | 10.9051 | 10.002 | 9.3653 | 6.5347 | 4.8796 | 4.5214 | 16.9898 | 16.5878 | 16.1418 | 16.0102 | 15.55 | 14.9357 | 14.2173 | 13.4816 | 12.9388 | 9.8755 | 6.201 | 0.36735 | 14.499 | 14.0398 | 13.5347 | 13.5224 | 13.0459 | 12.3204 | 11.4765 | 10.6276 | 10.0429 | 7.4908 | 6.0388 | 5.7102
|  | TAPLOW PRIMARY | HT |  |  |  |  | 14.4173 | 14.0827 | 13.7663 | 13.3796 | 12.9561 | 12.6418 | 11.9306 | 11.1837 | 10.4112 | 6.6429 | 4.5 | 3.9663 | 17.3612 | 17.1286 | 16.9173 | 16.6398 | 16.3337 | 16.2296 | 15.8031 | 15.349 | 14.8663 | 12.6541 | 11.5082 | 11.1837 | 14.8378 | 14.5071 | 14.2071 | 13.8245 | 13.4031 | 13.1735 | 12.5163 | 11.8194 | 11.099 | 7.6184 | 5.6847 | 5.2204
|  | TAPLOW PRIMARY | HE |  |  |  |  | 14.4398 | 14.1296 | 13.8439 | 13.4898 | 13.099 | 12.8663 | 12.2367 | 11.5755 | 10.8888 | 7.8143 | 6.1694 | 5.7051 | 17.2531 | 16.9643 | 16.6888 | 16.3388 | 15.95 | 15.7541 | 15.2286 | 14.6633 | 14.0592 | 10.599 | 6.848 | 0.95102 | 14.8531 | 14.5439 | 14.2735 | 13.9204 | 13.5316 | 13.3786 | 12.7929 | 12.1704 | 11.5316 | 8.6816 | 7.2153 | 6.8143
|  | TAPLOW PRIMARY | CF |  |  |  |  | 14.6561 | 14.5071 | 14.3102 | 14.1418 | 13.9133 | 13.6347 | 13.2918 | 13.3551 | 13.0316 | 10.8173 | 8.4622 | 6.3429 | 17.3378 | 17.1224 | 16.8582 | 16.5959 | 16.2418 | 15.8153 | 15.3031 | 15.1061 | 14.5724 | 10.6929 | 3.9439 | -8.4112 | 15.0327 | 14.8755 | 14.6673 | 14.4949 | 14.252 | 13.9694 | 13.6133 | 13.7663 | 13.4469 | 11.352 | 9.2459 | 7.349
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON PRIMARY | MINIMUM HEADROOM | ST 94510 07307 | NO | NO | 0.653 | 4.0701 | 3.9385 | 3.8007 | 3.6303 | 3.4334 | 3.2416 | 2.9803 | 2.715 | 2.5099 | 1.9518 | 1.6273 | 1.415 | 4.9319 | 4.8452 | 4.7533 | 4.6472 | 4.5238 | 4.4136 | 4.2829 | 4.1493 | 4.037 | 3.685 | 3.3982 | 2.5911 | 3.5926 | 3.4324 | 3.2844 | 3.0967 | 2.8773 | 2.6967 | 2.462 | 2.2273 | 2.0559 | 1.5712 | 1.2906 | 1.1151
|  | TARRANT RUSHTON PRIMARY | EE |  |  |  |  | 4.0701 | 3.9385 | 3.8007 | 3.6303 | 3.4334 | 3.2416 | 2.9803 | 2.715 | 2.5099 | 1.9518 | 1.666 | 1.4732 | 4.9319 | 4.8452 | 4.7533 | 4.6472 | 4.5238 | 4.4136 | 4.2829 | 4.1493 | 4.037 | 3.685 | 3.4054 | 3.0156 | 3.5926 | 3.4324 | 3.2844 | 3.0967 | 2.8773 | 2.6967 | 2.462 | 2.2273 | 2.0559 | 1.5712 | 1.3314 | 1.1681
|  | TARRANT RUSHTON PRIMARY | HT |  |  |  |  | 4.1262 | 4.013 | 3.8864 | 3.7313 | 3.566 | 3.3752 | 3.1405 | 2.8946 | 2.6752 | 1.9671 | 1.6273 | 1.415 | 4.9676 | 4.8901 | 4.8115 | 4.7136 | 4.6197 | 4.5166 | 4.4054 | 4.2942 | 4.1891 | 3.8544 | 3.7033 | 3.6084 | 3.6477 | 3.511 | 3.3681 | 3.1906 | 3.01 | 2.8222 | 2.6181 | 2.4038 | 2.2253 | 1.5885 | 1.2906 | 1.1151
|  | TARRANT RUSHTON PRIMARY | HE |  |  |  |  | 4.1191 | 4.0028 | 3.8742 | 3.716 | 3.5456 | 3.3711 | 3.1722 | 2.9416 | 2.7334 | 2.0589 | 1.766 | 1.6201 | 4.9574 | 4.8799 | 4.7942 | 4.6921 | 4.5911 | 4.486 | 4.3727 | 4.2544 | 4.1421 | 3.7187 | 3.4197 | 3.0391 | 3.6467 | 3.5151 | 3.3732 | 3.1998 | 3.0222 | 2.8447 | 2.6498 | 2.4487 | 2.2793 | 1.6793 | 1.4293 | 1.3089
|  | TARRANT RUSHTON PRIMARY | CF |  |  |  |  | 4.1671 | 4.0864 | 3.9854 | 3.8681 | 3.7364 | 3.613 | 3.4456 | 3.2752 | 3.0967 | 2.5926 | 2.2262 | 1.8844 | 4.9707 | 4.9074 | 4.835 | 4.7523 | 4.6564 | 4.5748 | 4.4809 | 4.387 | 4.287 | 3.8901 | 3.3982 | 2.5911 | 3.6742 | 3.5753 | 3.4579 | 3.3191 | 3.16 | 3.0416 | 2.9008 | 2.7569 | 2.6038 | 2.1498 | 1.8151 | 1.5283
MANNINGTON GSP | SALISBURY BSP | TEFFONT PRIMARY | MINIMUM HEADROOM | ST 99837 30994 | NO | NO | 0.476 | 2.8745 | 2.7694 | 2.649 | 2.5602 | 2.4286 | 2.2622 | 2.1204 | 1.9184 | 1.8378 | 1.35 | 1.1724 | 1.0082 | 4.199 | 4.1122 | 4.0092 | 3.9378 | 3.8224 | 3.6827 | 3.5673 | 3.4061 | 3.3643 | 3.2082 | 2.7694 | 1.6816 | 2.9531 | 2.898 | 2.801 | 2.7224 | 2.602 | 2.4367 | 2.2888 | 2.0827 | 2.0235 | 1.602 | 1.449 | 1.3082
|  | TEFFONT PRIMARY | EE |  |  |  |  | 2.8745 | 2.7694 | 2.649 | 2.5602 | 2.4286 | 2.2622 | 2.1204 | 1.9184 | 1.8378 | 1.35 | 1.1724 | 1.0908 | 4.199 | 4.1122 | 4.0092 | 3.9378 | 3.8224 | 3.6827 | 3.5673 | 3.4061 | 3.3643 | 3.2082 | 2.9316 | 2.4112 | 2.9531 | 2.898 | 2.801 | 2.7224 | 2.602 | 2.4367 | 2.2888 | 2.0827 | 2.0235 | 1.602 | 1.449 | 1.3776
|  | TEFFONT PRIMARY | HT |  |  |  |  | 2.9276 | 2.8459 | 2.7786 | 2.698 | 2.5959 | 2.501 | 2.3622 | 2.2122 | 2.0582 | 1.4449 | 1.1857 | 1.0082 | 4.2827 | 4.2194 | 4.1765 | 4.1153 | 4.0398 | 3.9837 | 3.8786 | 3.7663 | 3.649 | 3.2847 | 3.2245 | 3.1776 | 2.9837 | 2.9429 | 2.8918 | 2.8255 | 2.7418 | 2.6561 | 2.5347 | 2.4071 | 2.2612 | 1.6888 | 1.4592 | 1.3082
|  | TEFFONT PRIMARY | HE |  |  |  |  | 2.9276 | 2.849 | 2.7857 | 2.7071 | 2.6082 | 2.5194 | 2.3827 | 2.2378 | 2.0857 | 1.4296 | 1.2582 | 1.1816 | 4.2816 | 4.2184 | 4.1765 | 4.1163 | 4.0398 | 3.9847 | 3.8816 | 3.7684 | 3.648 | 3.2694 | 2.9724 | 2.4531 | 2.9847 | 2.9449 | 2.8959 | 2.8286 | 2.752 | 2.6673 | 2.55 | 2.4265 | 2.2878 | 1.6786 | 1.5306 | 1.4673
|  | TEFFONT PRIMARY | CF |  |  |  |  | 2.9459 | 2.8888 | 2.8194 | 2.7714 | 2.7041 | 2.6245 | 2.5337 | 2.4745 | 2.3776 | 1.8806 | 1.5255 | 1.251 | 4.299 | 4.2582 | 4.2061 | 4.1776 | 4.1306 | 4.0694 | 3.9908 | 3.948 | 3.8684 | 3.4031 | 2.7694 | 1.6816 | 2.9908 | 2.9602 | 2.9204 | 2.8776 | 2.8224 | 2.7561 | 2.6827 | 2.6265 | 2.5408 | 2.0929 | 1.7663 | 1.5255
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | TEMPLE FARM PRIMARY | MINIMUM HEADROOM | SU 84178 83872 | YES | NO | 0.727 | 1.4986 | 1.4578 | 1.4057 | 1.369 | 1.3139 | 1.2486 | 1.1659 | 1.1118 | 1.0547 | 0.75878 | 0.63633 | 0.57 | 2.1012 | 2.0767 | 2.042 | 2.0196 | 1.9808 | 1.9359 | 1.8818 | 1.838 | 1.8002 | 1.6114 | 1.438 | 0.99102 | 1.3604 | 1.3206 | 1.2716 | 1.2288 | 1.1737 | 1.1114 | 1.0339 | 0.97571 | 0.91959 | 0.6451 | 0.53184 | 0.47163
|  | TEMPLE FARM PRIMARY | EE |  |  |  |  | 1.4986 | 1.4578 | 1.4057 | 1.369 | 1.3139 | 1.2486 | 1.1659 | 1.1118 | 1.0547 | 0.82408 | 0.77408 | 0.75776 | 2.1012 | 2.0767 | 2.042 | 2.0196 | 1.9808 | 1.9359 | 1.8818 | 1.838 | 1.8002 | 1.6573 | 1.5216 | 1.3084 | 1.3604 | 1.3206 | 1.2716 | 1.2288 | 1.1737 | 1.1114 | 1.0339 | 0.97571 | 0.91959 | 0.71143 | 0.66449 | 0.64918
|  | TEMPLE FARM PRIMARY | HT |  |  |  |  | 1.5292 | 1.5006 | 1.4618 | 1.4292 | 1.3873 | 1.3271 | 1.2873 | 1.221 | 1.1618 | 0.87204 | 0.75776 | 0.68429 | 2.1308 | 2.1104 | 2.089 | 2.0696 | 2.0451 | 2.0124 | 1.9767 | 1.9308 | 1.8859 | 1.6941 | 1.6237 | 1.5829 | 1.3941 | 1.3655 | 1.3308 | 1.2941 | 1.2533 | 1.2002 | 1.1492 | 1.0869 | 1.0237 | 0.75429 | 0.64612 | 0.58082
|  | TEMPLE FARM PRIMARY | HE |  |  |  |  | 1.5282 | 1.4986 | 1.4608 | 1.4271 | 1.3843 | 1.3261 | 1.2629 | 1.1894 | 1.1139 | 0.75878 | 0.63633 | 0.57 | 2.1237 | 2.1043 | 2.0778 | 2.0563 | 2.0247 | 1.9859 | 1.9502 | 1.9012 | 1.8471 | 1.6114 | 1.5145 | 1.3012 | 1.389 | 1.3584 | 1.3206 | 1.2798 | 1.2349 | 1.1778 | 1.1186 | 1.0512 | 0.97673 | 0.6451 | 0.53184 | 0.47163
|  | TEMPLE FARM PRIMARY | CF |  |  |  |  | 1.5384 | 1.5098 | 1.4904 | 1.4588 | 1.4322 | 1.3955 | 1.3547 | 1.3312 | 1.2873 | 1.0292 | 0.82408 | 0.67816 | 2.1298 | 2.1084 | 2.0951 | 2.0686 | 2.0502 | 2.0196 | 1.9869 | 1.9604 | 1.9257 | 1.6982 | 1.438 | 0.99102 | 1.4053 | 1.3778 | 1.3584 | 1.3288 | 1.3053 | 1.2706 | 1.2318 | 1.2073 | 1.1594 | 0.89612 | 0.70429 | 0.56857
MELKSHAM GSP | CHIPPENHAM BSP | TETBURY PRIMARY | MINIMUM HEADROOM | ST 89708 93444 | NO | YES | 2.363 | 3.8268 | 3.6064 | 3.4003 | 3.1258 | 2.8227 | 2.3819 | 2.2737 | 1.8584 | 1.536 | -0.15892 | -1.511 | -2.3242 | 3.1717 | 2.989 | 2.8258 | 2.5992 | 2.3513 | 2.038 | 2.0268 | 1.7237 | 1.5248 | 0.38802 | -0.82933 | -3.9446 | 3.4462 | 3.2033 | 2.9952 | 2.7084 | 2.3952 | 1.9584 | 1.9982 | 1.6033 | 1.3064 | -0.085453 | -1.2569 | -1.9171
|  | TETBURY PRIMARY | EE |  |  |  |  | 3.8268 | 3.6064 | 3.4003 | 3.1258 | 2.8227 | 2.3819 | 2.2737 | 1.8584 | 1.5676 | -0.083412 | -1.2334 | -2.1038 | 3.1717 | 2.989 | 2.8258 | 2.5992 | 2.3513 | 2.038 | 2.0268 | 1.7237 | 1.5248 | 0.38802 | -0.77321 | -2.4273 | 3.4462 | 3.2033 | 2.9952 | 2.7084 | 2.3952 | 1.9584 | 1.9982 | 1.6033 | 1.3564 | -0.041576 | -1.0201 | -1.7375
|  | TETBURY PRIMARY | HT |  |  |  |  | 3.938 | 3.7666 | 3.6043 | 3.3788 | 3.1186 | 2.785 | 2.3819 | 1.9625 | 1.536 | -0.15892 | -1.511 | -2.3242 | 3.3156 | 3.1982 | 3.0931 | 2.9431 | 2.7686 | 2.5901 | 2.3441 | 2.086 | 1.8166 | 1.0288 | 0.4074 | 0.067608 | 3.6013 | 3.4299 | 3.2778 | 3.0533 | 2.7992 | 2.5084 | 2.1278 | 1.7227 | 1.3064 | -0.085453 | -1.2569 | -1.9171
|  | TETBURY PRIMARY | HE |  |  |  |  | 3.9533 | 3.7931 | 3.6482 | 3.4492 | 3.2186 | 2.937 | 2.5921 | 2.2319 | 1.8717 | 0.43904 | -0.69158 | -1.262 | 3.287 | 3.1574 | 3.0452 | 2.886 | 2.7033 | 2.5207 | 2.2676 | 1.9982 | 1.7166 | 0.68496 | -0.48851 | -2.0201 | 3.6105 | 3.4513 | 3.3125 | 3.1145 | 2.8819 | 2.6339 | 2.2992 | 1.9462 | 1.585 | 0.43393 | -0.51607 | -0.97525
|  | TETBURY PRIMARY | CF |  |  |  |  | 4.0666 | 3.9615 | 3.8472 | 3.7635 | 3.6401 | 3.4962 | 3.3625 | 3.1758 | 2.988 | 2.0533 | 0.84006 | -0.24872 | 3.3452 | 3.2431 | 3.1278 | 3.038 | 2.9033 | 2.7421 | 2.589 | 2.386 | 2.1707 | 1.0656 | -0.82933 | -3.9446 | 3.7115 | 3.5982 | 3.4788 | 3.3911 | 3.2564 | 3.1033 | 2.9686 | 2.7615 | 2.5482 | 1.7992 | 0.76659 | -0.14362
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM PRIMARY | MINIMUM HEADROOM | SU 52758 66466 | NO | NO | 6.19 | 0.98367 | 0.60816 | -0.09898 | -0.92245 | -1.7276 | -3.1429 | -4.9276 | -6.9214 | -8.348 | -16.2939 | -20.9327 | -23.348 | 10.9663 | 10.6867 | 10.0959 | 9.4286 | 8.7745 | 7.8469 | 6.6837 | 5.4153 | 4.5684 | -0.018367 | -4.6541 | -15.6051 | 1.5959 | 1.2714 | 0.64184 | -0.078571 | -0.77143 | -2.0296 | -3.6357 | -5.4071 | -6.651 | -13.698 | -17.8245 | -19.9082
|  | THATCHAM PRIMARY | EE |  |  |  |  | 0.98367 | 0.60816 | -0.09898 | -0.92245 | -1.7276 | -3.1429 | -4.9276 | -6.9214 | -8.348 | -15.7551 | -20.0714 | -22.9388 | 10.9663 | 10.6867 | 10.0959 | 9.4286 | 8.7745 | 7.8469 | 6.6837 | 5.4153 | 4.5684 | -0.018367 | -4.2561 | -10.0918 | 1.5959 | 1.2714 | 0.64184 | -0.078571 | -0.77143 | -2.0296 | -3.6357 | -5.4071 | -6.651 | -13.1959 | -17.048 | -19.549
|  | THATCHAM PRIMARY | HT |  |  |  |  | 1.3592 | 0.7602 | 0.086735 | -0.3398 | -1.0439 | -2.4378 | -4.198 | -5.9357 | -7.6388 | -16.2939 | -20.9327 | -23.348 | 11.4429 | 11.0388 | 10.5612 | 10.3816 | 9.948 | 9.2337 | 8.3245 | 7.4071 | 6.4878 | 2.1449 | 0.13776 | -0.86633 | 1.9082 | 1.3673 | 0.75714 | 0.39286 | -0.22449 | -1.4633 | -3.002 | -4.5245 | -6.0194 | -13.698 | -17.8245 | -19.9082
|  | THATCHAM PRIMARY | HE |  |  |  |  | 1.4286 | 0.87653 | 0.25714 | -0.067347 | -0.67653 | -1.7388 | -3.152 | -4.7796 | -6.251 | -13.949 | -18.2173 | -20.1082 | 11.3612 | 10.9102 | 10.3908 | 10.1796 | 9.701 | 9.0224 | 8.1398 | 7.1306 | 6.1612 | 0.9051 | -3.3724 | -8.8143 | 1.9735 | 1.4745 | 0.91224 | 0.63571 | 0.10204 | -0.83776 | -2.0673 | -3.4735 | -4.7531 | -11.5561 | -15.3786 | -17.0133
|  | THATCHAM PRIMARY | CF |  |  |  |  | 1.8082 | 1.4449 | 1.0327 | 0.60918 | 0.62551 | 0.28878 | -0.18469 | -0.77143 | -1.4184 | -7.1786 | -12.9163 | -16.6102 | 11.5388 | 11.1724 | 10.7459 | 10.301 | 10.2255 | 9.7949 | 9.248 | 8.6276 | 7.95 | 2.6602 | -4.6541 | -15.6051 | 2.3184 | 1.9959 | 1.6214 | 1.2418 | 1.2714 | 0.97653 | 0.57143 | 0.071429 | -0.47449 | -5.449 | -10.4765 | -13.901
NORTH HYDE GSP | NORTH HYDE BSP | THE GREEN PRIMARY | MINIMUM HEADROOM | TQ 12414 79503 | NO | YES | 4.195 | -1.5784 | -3.8641 | -7.4519 | -11.1988 | -14.2906 | -15.7182 | -16.4162 | -16.1019 | -15.7121 | -13.4253 | -13.4764 | -13.4335 | 1.8012 | 0.55426 | -1.3131 | -3.4437 | -4.9794 | -5.907 | -6.4845 | -6.5733 | -6.61 | -7.5345 | -11.311 | -18.7886 | -0.37993 | -2.2391 | -5.1126 | -8.2922 | -10.8544 | -12.0167 | -12.6044 | -12.3809 | -12.0534 | -10.2697 | -10.3503 | -10.3309
|  | THE GREEN PRIMARY | EE |  |  |  |  | -1.5784 | -3.8641 | -7.4519 | -11.1988 | -14.2906 | -15.7182 | -16.4162 | -16.1019 | -15.7121 | -13.4253 | -13.3172 | -13.0957 | 1.8012 | 0.55426 | -1.3131 | -3.4437 | -4.9794 | -5.907 | -6.4845 | -6.5733 | -6.61 | -7.0682 | -9.0988 | -12.8182 | -0.37993 | -2.2391 | -5.1126 | -8.2922 | -10.8544 | -12.0167 | -12.6044 | -12.3809 | -12.0534 | -10.2697 | -10.2197 | -10.1034
|  | THE GREEN PRIMARY | HT |  |  |  |  | -1.46 | -3.6876 | -7.2406 | -10.9213 | -13.9264 | -15.2968 | -15.8988 | -15.4682 | -15.0243 | -13.1947 | -13.4764 | -13.4335 | 1.9971 | 0.82262 | -0.96411 | -2.9815 | -4.3692 | -5.1723 | -5.5815 | -5.5049 | -5.408 | -4.9845 | -5.3345 | -5.3947 | -0.24625 | -2.0371 | -4.8687 | -7.9748 | -10.4381 | -11.5442 | -12.0269 | -11.7146 | -11.3697 | -10.0116 | -10.3503 | -10.3309
|  | THE GREEN PRIMARY | HE |  |  |  |  | -1.4508 | -3.6662 | -7.209 | -10.8733 | -13.8815 | -15.1988 | -15.761 | -15.2957 | -14.7978 | -12.3733 | -12.1682 | -12.1804 | 1.9287 | 0.70528 | -1.1264 | -3.1937 | -4.6631 | -5.5141 | -5.9968 | -6.0019 | -6.0039 | -6.4213 | -8.4233 | -12.2019 | -0.23707 | -2.0218 | -4.8412 | -7.9269 | -10.3942 | -11.4452 | -11.8901 | -11.5391 | -11.1524 | -9.2636 | -9.1575 | -9.1748
|  | THE GREEN PRIMARY | CF |  |  |  |  | -1.1815 | -3.1376 | -6.2315 | -9.3947 | -11.8876 | -13.308 | -14.0559 | -13.8917 | -13.7325 | -13.2192 | -12.9396 | -12.6468 | 2.0267 | 0.89711 | -0.77533 | -2.6672 | -3.9753 | -4.9233 | -5.5192 | -5.6886 | -5.8835 | -7.5345 | -11.311 | -18.7886 | -0.0013551 | -1.5667 | -4.0003 | -6.6626 | -8.6912 | -9.8187 | -10.4034 | -10.2901 | -10.184 | -9.8024 | -9.6881 | -9.536
FLEET-BRAMLEY GSP | READING TOWN BSP | THE MALL PRIMARY | MINIMUM HEADROOM | SU 71319 73293 | NO | NO | 4.516 | 12.7899 | 12.6083 | 12.1072 | 10.3042 | 9.3236 | 8.7572 | 8.0787 | 7.2981 | 6.644 | 5.6868 | 4.9032 | 4.8991 | 15.6644 | 15.5532 | 15.2807 | 13.5348 | 12.9113 | 12.4675 | 11.9287 | 11.3215 | 10.7756 | 8.6409 | 3.7124 | -5.8795 | 13.6491 | 13.5297 | 13.1613 | 11.5042 | 10.6164 | 10.0583 | 9.3511 | 8.5715 | 7.9603 | 6.9328 | 6.2348 | 6.2236
|  | THE MALL PRIMARY | EE |  |  |  |  | 12.7899 | 12.6083 | 12.1072 | 10.3042 | 9.3236 | 8.7572 | 8.0787 | 7.2981 | 6.644 | 5.6868 | 5.1726 | 5.2991 | 15.6644 | 15.5532 | 15.2807 | 13.5348 | 12.9113 | 12.4675 | 11.9287 | 11.3215 | 10.7756 | 8.6409 | 5.9338 | 1.3236 | 13.6491 | 13.5297 | 13.1613 | 11.5042 | 10.6164 | 10.0583 | 9.3511 | 8.5715 | 7.9603 | 6.9328 | 6.5011 | 6.5287
|  | THE MALL PRIMARY | HT |  |  |  |  | 12.9297 | 12.8134 | 12.3685 | 10.6634 | 9.6634 | 9.0532 | 8.4419 | 7.8695 | 7.2858 | 5.9399 | 4.9032 | 4.8991 | 15.7899 | 15.743 | 15.6011 | 13.9266 | 13.5746 | 13.2634 | 12.9317 | 12.5909 | 12.2154 | 11.1787 | 10.4756 | 10.3756 | 13.7501 | 13.6766 | 13.4358 | 11.8695 | 11.0317 | 10.5246 | 10.0062 | 9.4787 | 8.8858 | 7.2481 | 6.2348 | 6.2236
|  | THE MALL PRIMARY | HE |  |  |  |  | 12.9307 | 12.8256 | 12.396 | 10.7144 | 9.8593 | 9.4011 | 8.8675 | 8.2613 | 7.6583 | 6.8175 | 6.3256 | 6.2746 | 15.7389 | 15.6644 | 15.494 | 13.7848 | 13.2807 | 12.9358 | 12.5328 | 12.0593 | 11.5532 | 9.4195 | 6.6603 | 2.0521 | 13.7399 | 13.6664 | 13.4277 | 11.9134 | 11.1868 | 10.8032 | 10.3491 | 9.847 | 9.3001 | 8.1603 | 7.6909 | 7.6511
|  | THE MALL PRIMARY | CF |  |  |  |  | 13.0062 | 12.9552 | 12.6389 | 11.0705 | 10.5879 | 10.5042 | 10.3419 | 10.1072 | 9.8134 | 7.8654 | 6.8624 | 5.9644 | 15.7736 | 15.7011 | 15.544 | 13.8634 | 13.4868 | 13.2348 | 12.9246 | 12.5624 | 12.145 | 8.9215 | 3.7124 | -5.8795 | 13.8246 | 13.7787 | 13.5889 | 12.1695 | 11.8307 | 11.7389 | 11.594 | 11.3868 | 11.1348 | 9.246 | 8.1511 | 7.3389
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | THEALE PRIMARY | MINIMUM HEADROOM | SU 64755 71015 | NO | NO | 5.164 | 12.4117 | 12.0281 | 11.5852 | 11.0985 | 10.5056 | 9.9709 | 9.3332 | 8.7199 | 8.1964 | 5.7474 | 4.625 | 4.1852 | 14.7036 | 14.4444 | 14.124 | 13.774 | 13.3199 | 12.9015 | 12.4066 | 11.9291 | 11.526 | 9.6403 | 8.7913 | 8.4168 | 12.8872 | 12.5209 | 12.1036 | 11.6464 | 11.0954 | 10.5862 | 9.977 | 9.3862 | 8.8893 | 6.525 | 5.4454 | 5.023
|  | THEALE PRIMARY | EE |  |  |  |  | 12.4117 | 12.0281 | 11.5852 | 11.0985 | 10.5056 | 9.9709 | 9.3332 | 8.7199 | 8.1964 | 6.5117 | 6.174 | 6.1577 | 14.7036 | 14.4444 | 14.124 | 13.774 | 13.3199 | 12.9015 | 12.4066 | 11.9291 | 11.526 | 10.2464 | 10.0128 | 9.9587 | 12.8872 | 12.5209 | 12.1036 | 11.6464 | 11.0954 | 10.5862 | 9.977 | 9.3862 | 8.8893 | 7.275 | 6.9638 | 6.9485
|  | THEALE PRIMARY | HT |  |  |  |  | 12.6709 | 12.4087 | 12.0944 | 11.6219 | 11.176 | 10.8005 | 10.3219 | 9.8097 | 9.2852 | 6.9617 | 5.9923 | 5.6658 | 14.8872 | 14.7311 | 14.5321 | 14.1781 | 13.8495 | 13.5628 | 13.1964 | 12.8107 | 12.4117 | 10.6658 | 9.9566 | 9.7107 | 13.1781 | 12.8985 | 12.5944 | 12.1648 | 11.7515 | 11.3913 | 10.9321 | 10.4464 | 9.9403 | 7.7026 | 6.7781 | 6.4709
|  | THEALE PRIMARY | HE |  |  |  |  | 12.6148 | 12.3179 | 11.9526 | 11.5209 | 10.9862 | 10.5209 | 9.9332 | 9.3036 | 8.6444 | 5.7474 | 4.625 | 4.1852 | 14.8546 | 14.6526 | 14.4117 | 14.1056 | 13.6954 | 13.3321 | 12.873 | 12.3852 | 11.8709 | 9.6403 | 8.7913 | 8.4168 | 13.1138 | 12.8005 | 12.4597 | 12.0556 | 11.5607 | 11.1168 | 10.5515 | 9.9505 | 9.3189 | 6.525 | 5.4454 | 5.023
|  | THEALE PRIMARY | CF |  |  |  |  | 12.8342 | 12.6454 | 12.4413 | 12.2107 | 11.9536 | 11.6913 | 11.3526 | 10.9862 | 10.5862 | 8.2291 | 6.1913 | 4.8495 | 14.9536 | 14.8505 | 14.7434 | 14.5893 | 14.4219 | 14.2107 | 13.9383 | 13.6454 | 13.3301 | 11.4913 | 9.9281 | 8.8607 | 13.3658 | 13.1689 | 12.9556 | 12.7158 | 12.4709 | 12.224 | 11.9036 | 11.5546 | 11.1709 | 8.9036 | 6.9474 | 5.6607
MELKSHAM GSP | ANDOVER BSP | THRUXTON PRIMARY | MINIMUM HEADROOM | SU 29134 45674 | NO | NO | 0.915 | 3.3252 | 3.1691 | 3.0252 | 2.6222 | 2.014 | 1.3344 | 0.64053 | 0.10788 | -0.586 | -2.4789 | -2.7462 | -2.9187 | 4.334 | 4.2156 | 4.1166 | 3.8819 | 3.637 | 3.3401 | 2.986 | 2.6105 | 2.3033 | 1.0442 | 0.31967 | -1.2222 | 3.7661 | 3.611 | 3.4742 | 3.114 | 2.6763 | 2.1253 | 1.5559 | 1.1212 | 0.53955 | -1.1604 | -1.3594 | -1.5339
|  | THRUXTON PRIMARY | EE |  |  |  |  | 3.3252 | 3.1691 | 3.0252 | 2.6222 | 2.1405 | 1.614 | 1.0018 | 0.33441 | -0.30131 | -2.4697 | -2.7166 | -2.8115 | 4.334 | 4.2156 | 4.1166 | 3.8819 | 3.637 | 3.3401 | 2.986 | 2.6105 | 2.3033 | 1.0636 | 0.60539 | -0.11502 | 3.7661 | 3.611 | 3.4742 | 3.114 | 2.714 | 2.2508 | 1.7069 | 1.1212 | 0.60282 | -1.1604 | -1.3594 | -1.4462
|  | THRUXTON PRIMARY | HT |  |  |  |  | 3.4099 | 3.3109 | 3.1477 | 2.6293 | 2.014 | 1.3344 | 0.64053 | 0.10788 | -0.586 | -2.3033 | -2.6615 | -2.9187 | 4.4197 | 4.3636 | 4.2656 | 4.0064 | 3.7248 | 3.4023 | 3.0656 | 2.8166 | 2.4472 | 1.4319 | 1.2584 | 1.135 | 3.8569 | 3.7681 | 3.6191 | 3.1834 | 2.6763 | 2.1253 | 1.5559 | 1.1334 | 0.53955 | -1.0309 | -1.3288 | -1.5339
|  | THRUXTON PRIMARY | HE |  |  |  |  | 3.4079 | 3.3058 | 3.1681 | 2.7956 | 2.3385 | 1.8456 | 1.2375 | 0.62522 | -0.093143 | -2.4789 | -2.7462 | -2.8319 | 4.4064 | 4.3401 | 4.2472 | 4.0452 | 3.8227 | 3.5636 | 3.2452 | 2.9605 | 2.5962 | 1.0442 | 0.56049 | -0.13237 | 3.8538 | 3.7651 | 3.6365 | 3.3181 | 2.9375 | 2.5151 | 2.011 | 1.5324 | 0.94363 | -1.136 | -1.3502 | -1.4247
|  | THRUXTON PRIMARY | CF |  |  |  |  | 3.4487 | 3.3722 | 3.2701 | 3.1722 | 3.0599 | 2.9793 | 2.763 | 2.5354 | 2.2558 | -1.2636 | -2.2207 | -2.7258 | 4.4319 | 4.3778 | 4.3064 | 4.2289 | 4.1442 | 4.0768 | 3.9268 | 3.7676 | 3.5789 | 1.6044 | 0.31967 | -1.2222 | 3.8926 | 3.8212 | 3.7263 | 3.6314 | 3.5212 | 3.4477 | 3.2467 | 3.0416 | 2.7885 | -0.071673 | -0.9482 | -1.3502
MELKSHAM GSP | WEST GRAFTON BSP | TIDWORTH PRIMARY | MINIMUM HEADROOM | SU 24088 49593 | NO | NO | 3.203 | 1.2545 | 0.54123 | -0.25877 | -1.0884 | -1.5353 | -2.5577 | -3.5771 | -5.1812 | -6.3547 | -12.9649 | -15.5384 | -16.8659 | 3.5943 | 3.1555 | 2.6504 | 2.1096 | 1.9045 | 1.3137 | 0.62287 | -0.30571 | -0.96081 | -4.7047 | -7.3588 | -13.77 | 1.1698 | 0.5494 | -0.16591 | -0.91999 | -1.2373 | -2.0782 | -3.0577 | -4.4322 | -5.4047 | -10.7241 | -12.9445 | -14.0608
|  | TIDWORTH PRIMARY | EE |  |  |  |  | 1.2545 | 0.54123 | -0.25877 | -1.0884 | -1.5353 | -2.4812 | -3.5771 | -5.1812 | -6.3547 | -12.8312 | -15.0924 | -16.5465 | 3.5943 | 3.1555 | 2.6504 | 2.1096 | 1.9045 | 1.3137 | 0.62287 | -0.30571 | -0.96081 | -4.7047 | -7.1098 | -10.4924 | 1.1698 | 0.5494 | -0.16591 | -0.91999 | -1.2373 | -2.0782 | -3.0577 | -4.4322 | -5.4047 | -10.6404 | -12.5577 | -13.7965
|  | TIDWORTH PRIMARY | HT |  |  |  |  | 1.4055 | 0.8147 | 0.17899 | -0.55775 | -1.4761 | -2.5577 | -3.369 | -4.669 | -5.9282 | -12.9649 | -15.5384 | -16.8659 | 3.8218 | 3.5045 | 3.1555 | 2.782 | 2.2974 | 1.731 | 1.4229 | 0.7545 | 0.10042 | -3.371 | -4.5975 | -5.1863 | 1.3759 | 0.86878 | 0.31164 | -0.31387 | -1.1067 | -2.0384 | -2.6435 | -3.7445 | -4.8169 | -10.7241 | -12.9445 | -14.0608
|  | TIDWORTH PRIMARY | HE |  |  |  |  | 1.5208 | 0.9494 | 0.26368 | -0.40775 | -1.1659 | -1.9904 | -2.6435 | -4.0741 | -5.2475 | -11.9037 | -14.1945 | -15.1465 | 3.8218 | 3.479 | 3.0708 | 2.68 | 2.2239 | 1.7167 | 1.4055 | 0.61062 | -0.085298 | -4.1455 | -6.619 | -9.7782 | 1.4667 | 0.97899 | 0.38103 | -0.18632 | -0.8506 | -1.5741 | -2.0465 | -3.2312 | -4.2251 | -9.7751 | -11.7026 | -12.4771
|  | TIDWORTH PRIMARY | CF |  |  |  |  | 1.8076 | 1.4137 | 0.87287 | 0.32593 | 0.032049 | -0.20469 | -0.57611 | -1.1118 | -1.3506 | -7.8088 | -11.2516 | -13.3802 | 3.9637 | 3.7045 | 3.3555 | 2.9984 | 2.7514 | 2.4749 | 2.1147 | 1.6596 | 1.4616 | -3.0149 | -7.3588 | -13.77 | 1.7045 | 1.3678 | 0.90654 | 0.44123 | 0.18307 | -0.058767 | -0.41591 | -0.90162 | -0.98938 | -6.3006 | -9.1567 | -11.0108
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY PRIMARY | MINIMUM HEADROOM | ST 93438 29127 | NO | NO | 6.223 | 0.73142 | 0.5855 | 0.3855 | 0.15795 | -0.017563 | -0.29818 | -0.63185 | -0.9645 | -1.0584 | -1.54 | -1.5441 | -1.7482 | 2.2433 | 2.1371 | 1.9882 | 1.8126 | 1.6739 | 1.4637 | 1.2188 | 0.98305 | 0.8708 | 0.47591 | -0.026135 | -1.8608 | 0.95223 | 0.81652 | 0.6206 | 0.39815 | 0.22978 | -0.045727 | -0.37328 | -0.69879 | -0.79062 | -1.1978 | -1.1518 | -1.3294
|  | TISBURY PRIMARY | EE |  |  |  |  | 0.73142 | 0.5855 | 0.3855 | 0.15795 | -0.017563 | -0.29818 | -0.63185 | -0.9645 | -1.0584 | -1.3135 | -1.5441 | -1.6655 | 2.2433 | 2.1371 | 1.9882 | 1.8126 | 1.6739 | 1.4637 | 1.2188 | 0.98305 | 0.8708 | 0.73407 | 0.24733 | -0.62409 | 0.95223 | 0.81652 | 0.6206 | 0.39815 | 0.22978 | -0.045727 | -0.37328 | -0.69879 | -0.79062 | -0.94981 | -1.1518 | -1.258
|  | TISBURY PRIMARY | HT |  |  |  |  | 0.88244 | 0.75897 | 0.60999 | 0.46101 | 0.26101 | 0.025294 | -0.13695 | -0.34818 | -0.5696 | -1.1543 | -1.5247 | -1.7482 | 2.3524 | 2.2769 | 2.1851 | 2.0984 | 1.9749 | 1.831 | 1.7249 | 1.579 | 1.4198 | 1.1616 | 0.96672 | 0.86264 | 1.0655 | 0.95223 | 0.81448 | 0.68387 | 0.49917 | 0.27774 | 0.13591 | -0.069196 | -0.28552 | -0.80389 | -1.1376 | -1.3294
|  | TISBURY PRIMARY | HE |  |  |  |  | 0.8804 | 0.76815 | 0.63142 | 0.49366 | 0.30693 | 0.086518 | -0.099196 | -0.31144 | -0.52267 | -1.54 | -1.3931 | -1.4849 | 2.3351 | 2.2596 | 2.1596 | 2.0698 | 1.9392 | 1.7871 | 1.6575 | 1.4933 | 1.3188 | 0.47591 | 0.35958 | -0.49858 | 1.0624 | 0.96244 | 0.83387 | 0.71142 | 0.53795 | 0.33387 | 0.17264 | -0.033482 | -0.2396 | -1.1978 | -1.0029 | -1.0804
|  | TISBURY PRIMARY | CF |  |  |  |  | 0.92836 | 0.84876 | 0.75999 | 0.65489 | 0.54366 | 0.46407 | 0.31815 | 0.14468 | 0.01509 | -0.90328 | -1.0002 | -1.3614 | 2.3626 | 2.3024 | 2.2279 | 2.1392 | 2.0402 | 1.9626 | 1.829 | 1.6759 | 1.5596 | 0.61774 | -0.026135 | -1.8608 | 1.1084 | 1.0328 | 0.94407 | 0.84101 | 0.7308 | 0.65836 | 0.51448 | 0.35019 | 0.23999 | -0.63654 | -0.65695 | -0.98144
LOVEDEAN GSP | FAREHAM (MAIN) BSP | TITCHFIELD PRIMARY | MINIMUM HEADROOM | SU 54104 05695 | NO | YES | 1.414 | 9.1296 | 8.0745 | 6.8276 | 5.4265 | 3.7224 | 21.3378 | 20.0622 | 18.4765 | 16.8714 | 11.0745 | 8.5898 | 7.2082 | 10 | 9.4112 | 8.7041 | 8.199 | 7.3673 | 24.8122 | 23.8765 | 22.8776 | 22.0276 | 18.5827 | 15.8224 | 8.9878 | 9.2245 | 8.3418 | 7.2694 | 6.3224 | 4.8837 | 22.152 | 21.1041 | 19.6296 | 18.3418 | 13.4418 | 11.2531 | 10.0684
|  | TITCHFIELD PRIMARY | EE |  |  |  |  | 9.1296 | 8.0745 | 6.8276 | 5.7194 | 4.1561 | 21.8439 | 20.2224 | 18.4898 | 16.9163 | 11.3112 | 9.0908 | 7.4704 | 10 | 9.4112 | 8.7041 | 8.199 | 7.3673 | 24.8122 | 23.8765 | 22.8776 | 22.0276 | 18.5827 | 16.1327 | 12.5939 | 9.2245 | 8.3418 | 7.2694 | 6.5 | 5.1806 | 22.4939 | 21.1041 | 19.6296 | 18.3418 | 13.6276 | 11.698 | 10.2918
|  | TITCHFIELD PRIMARY | HT |  |  |  |  | 9.2173 | 8.1378 | 6.9061 | 5.4265 | 3.7224 | 21.3378 | 20.0622 | 18.4765 | 16.8714 | 11.0745 | 8.5898 | 7.2082 | 10.1704 | 9.6255 | 9.0306 | 8.3265 | 7.4857 | 25 | 24.4235 | 23.6286 | 22.8276 | 19.9592 | 18.7867 | 18.1561 | 9.399 | 8.5173 | 7.5265 | 6.3224 | 4.8837 | 22.152 | 21.1235 | 19.7867 | 18.4367 | 13.4418 | 11.2531 | 10.0684
|  | TITCHFIELD PRIMARY | HE |  |  |  |  | 9.3592 | 8.3847 | 7.2847 | 5.9378 | 4.3816 | 22.1612 | 20.9959 | 19.4163 | 17.8204 | 12.151 | 9.8939 | 8.851 | 10.2082 | 9.6776 | 9.0827 | 8.3673 | 7.5622 | 25.0663 | 24.4633 | 23.5765 | 22.6745 | 18.9786 | 16.452 | 13.1459 | 9.5051 | 8.7092 | 7.8204 | 6.7224 | 5.4184 | 22.8245 | 21.8908 | 20.5714 | 19.2367 | 14.3929 | 12.4153 | 11.5224
|  | TITCHFIELD PRIMARY | CF |  |  |  |  | 9.7776 | 9.1051 | 8.3204 | 7.4592 | 6.4755 | 24.8571 | 23.8918 | 23.2265 | 22.2143 | 16.0367 | 13.3367 | 10.8255 | 10.4041 | 10.0031 | 9.5388 | 9.0429 | 8.4531 | 26.199 | 25.5378 | 25.1133 | 24.4184 | 19.9704 | 15.8224 | 8.9878 | 9.851 | 9.2939 | 8.6357 | 7.9469 | 7.1296 | 25.0327 | 24.2051 | 23.8235 | 22.9878 | 17.8541 | 15.4398 | 13.2235
FLEET-BRAMLEY GSP | ALDERSHOT BSP | TONGHAM PRIMARY | MINIMUM HEADROOM | SU 88310 49487 | NO | YES | 2.838 | 14.4031 | 13.4541 | 12.8439 | 11.8949 | 10.898 | 9.5592 | 8.1898 | 6.8327 | 5.7316 | -0.16327 | -4.1602 | -6.2561 | 19.0867 | 18.3582 | 17.9898 | 17.3194 | 16.5959 | 15.6776 | 14.7051 | 13.7122 | 12.9592 | 8.8051 | 3.8071 | -7.8949 | 16.2082 | 15.3184 | 14.8163 | 13.9694 | 13.0714 | 11.8571 | 10.6122 | 9.3673 | 8.3796 | 3.199 | -0.35918 | -2.1867
|  | TONGHAM PRIMARY | EE |  |  |  |  | 14.4031 | 13.4541 | 12.8439 | 11.8949 | 10.898 | 9.5592 | 8.1898 | 6.8327 | 5.7316 | 0.088776 | -3.4847 | -6.0051 | 19.0867 | 18.3582 | 17.9898 | 17.3194 | 16.5959 | 15.6776 | 14.7051 | 13.7122 | 12.9592 | 8.8051 | 4.7102 | -1.3041 | 16.2082 | 15.3184 | 14.8163 | 13.9694 | 13.0714 | 11.8571 | 10.6122 | 9.3673 | 8.3796 | 3.3776 | 0.23776 | -1.9714
|  | TONGHAM PRIMARY | HT |  |  |  |  | 14.699 | 13.901 | 13.05 | 12.1439 | 11.5357 | 10.2959 | 9.0653 | 7.8 | 6.5173 | -0.16327 | -4.1602 | -6.2561 | 19.4969 | 18.9837 | 18.499 | 17.9765 | 17.7163 | 17.0459 | 16.3643 | 15.651 | 14.9173 | 11.3959 | 9.5653 | 8.6969 | 16.5102 | 15.7724 | 15.0316 | 14.2316 | 13.7235 | 12.6173 | 11.5133 | 10.3694 | 9.2092 | 3.199 | -0.35918 | -2.1867
|  | TONGHAM PRIMARY | HE |  |  |  |  | 14.7327 | 13.9592 | 13.1327 | 12.252 | 11.6663 | 10.5878 | 9.5133 | 8.399 | 7.2622 | 1.3908 | -2.2235 | -3.7082 | 19.3929 | 18.8184 | 18.2724 | 17.6735 | 17.3194 | 16.5908 | 15.8378 | 15.0276 | 14.1796 | 9.4561 | 5.2408 | -0.36735 | 16.5367 | 15.8173 | 15.099 | 14.3224 | 13.8316 | 12.8673 | 11.9 | 10.8888 | 9.8571 | 4.5602 | 1.3622 | 0.072449
|  | TONGHAM PRIMARY | CF |  |  |  |  | 15.2071 | 14.6031 | 14.0418 | 13.399 | 12.7796 | 12.5041 | 11.999 | 11.4541 | 10.8939 | 7.0061 | 3.1439 | -0.47347 | 19.6173 | 19.1071 | 18.6806 | 18.1827 | 17.6439 | 17.3133 | 16.7347 | 16.1153 | 15.448 | 10.7663 | 3.8071 | -7.8949 | 16.9592 | 16.3959 | 15.9255 | 15.3704 | 14.8286 | 14.6133 | 14.1602 | 13.6663 | 13.1571 | 9.6184 | 6.1204 | 2.8929
MINETY GSP | TOOTHILL BSP | TOOTHILL PRIMARY | MINIMUM HEADROOM | SU 13215 83986 | NO | NO | 2.34 | 15.2618 | 14.8547 | 14.3537 | 13.7945 | 13.2741 | 12.1935 | 10.8251 | 9.469 | 8.3629 | 3.521 | 1.2037 | 0.82918 | 14.9894 | 14.6139 | 14.1547 | 13.6241 | 13.218 | 12.3822 | 11.3588 | 10.3047 | 9.4904 | 6.421 | 2.6129 | -5.9382 | 14.368 | 13.9761 | 13.4955 | 12.9547 | 12.4588 | 11.4445 | 10.2292 | 8.9843 | 8.021 | 3.6802 | 1.4822 | 1.1384
|  | TOOTHILL PRIMARY | EE |  |  |  |  | 15.2618 | 14.8547 | 14.3537 | 13.7945 | 13.2741 | 12.1935 | 10.8251 | 9.469 | 8.3629 | 5.2996 | 4.1639 | 4.2486 | 14.9894 | 14.6139 | 14.1547 | 13.6241 | 13.218 | 12.3822 | 11.3588 | 10.3047 | 9.4904 | 6.6047 | 4.0639 | 0.41898 | 14.368 | 13.9761 | 13.4955 | 12.9547 | 12.4588 | 11.4445 | 10.2292 | 8.9843 | 8.021 | 5.2761 | 4.069 | 4.2139
|  | TOOTHILL PRIMARY | HT |  |  |  |  | 15.6435 | 15.3578 | 15.0139 | 14.4557 | 13.6129 | 12.5659 | 11.7455 | 10.6986 | 9.7935 | 6.1955 | 4.0873 | 3.7853 | 15.4047 | 15.1884 | 14.9231 | 14.4669 | 13.8322 | 13.119 | 12.5894 | 11.8547 | 11.2455 | 8.9027 | 7.6618 | 7.4169 | 14.7455 | 14.4761 | 14.1486 | 13.5904 | 12.7894 | 11.8129 | 11.0557 | 10.072 | 9.2343 | 5.9078 | 4.0251 | 3.8149
|  | TOOTHILL PRIMARY | HE |  |  |  |  | 15.5782 | 15.2649 | 14.8935 | 14.5149 | 13.769 | 12.8047 | 11.6006 | 10.1935 | 8.8149 | 3.521 | 1.2037 | 0.82918 | 15.2761 | 14.9955 | 14.6588 | 14.3078 | 13.668 | 12.9139 | 12.2516 | 11.2965 | 10.3751 | 6.421 | 3.5904 | -0.16265 | 14.6782 | 14.3822 | 14.0251 | 13.6659 | 12.9435 | 12.0394 | 11.1088 | 9.8567 | 8.6363 | 3.6802 | 1.4822 | 1.1384
|  | TOOTHILL PRIMARY | CF |  |  |  |  | 15.9098 | 15.7506 | 15.5506 | 15.3292 | 15.1169 | 14.7343 | 14.1792 | 13.519 | 12.8516 | 8.2649 | 4.7363 | 2.2608 | 15.4618 | 15.2659 | 15.0241 | 14.7414 | 14.4465 | 13.9802 | 13.3659 | 12.6486 | 12.1833 | 7.8792 | 2.6129 | -5.9382 | 14.9873 | 14.8322 | 14.6414 | 14.4241 | 14.219 | 13.8414 | 13.3037 | 12.6588 | 12.1149 | 8.0118 | 4.8424 | 2.5149
NURSLING GSP | ROWNHAMS BSP | TOTTON PRIMARY | MINIMUM HEADROOM | SU 35835 13428 | NO | YES | 8.846 | 5.4001 | 4.8521 | 4.5766 | 4.1603 | 3.7041 | 3.0348 | 2.2501 | 1.4531 | 0.747 | -3.8999 | -7.201 | -8.9856 | 9.0337 | 8.649 | 8.5062 | 8.2307 | 7.9286 | 7.4939 | 6.7837 | 6.0256 | 5.4399 | 2.2613 | -1.3877 | -9.9224 | 6.3082 | 5.7756 | 5.6184 | 5.2552 | 4.8644 | 4.0664 | 3.1776 | 2.249 | 1.4674 | -2.6938 | -5.6346 | -7.2173
|  | TOTTON PRIMARY | EE |  |  |  |  | 5.4001 | 4.8521 | 4.5766 | 4.1603 | 3.7041 | 3.0348 | 2.2501 | 1.4531 | 0.747 | -3.6183 | -6.6356 | -8.7438 | 9.095 | 8.649 | 8.5062 | 8.2307 | 7.9286 | 7.4939 | 6.7837 | 6.0256 | 5.4399 | 2.2613 | -0.97136 | -5.5132 | 6.3419 | 5.7756 | 5.6184 | 5.2552 | 4.8644 | 4.0664 | 3.1776 | 2.249 | 1.4674 | -2.4663 | -5.153 | -7.0275
|  | TOTTON PRIMARY | HT |  |  |  |  | 5.4582 | 5.1827 | 4.8817 | 4.5348 | 4.1399 | 3.6633 | 2.9888 | 2.2623 | 1.3419 | -3.8999 | -7.201 | -8.9856 | 9.0337 | 8.8837 | 8.7246 | 8.5327 | 8.2939 | 8.0644 | 7.6909 | 7.2837 | 6.8113 | 4.0705 | 2.5582 | 1.7858 | 6.3082 | 6.0113 | 5.7235 | 5.3858 | 5.0123 | 4.4735 | 3.6766 | 2.8164 | 1.9103 | -2.6938 | -5.6346 | -7.2173
|  | TOTTON PRIMARY | HE |  |  |  |  | 5.649 | 5.1807 | 4.8797 | 4.5235 | 4.1205 | 3.6797 | 3.0144 | 2.2786 | 1.4929 | -2.355 | -5.3214 | -6.6377 | 9.2541 | 8.8633 | 8.699 | 8.4929 | 8.2358 | 8.0011 | 7.6041 | 7.0399 | 6.4144 | 2.9062 | -0.353 | -4.5805 | 6.5511 | 6.0695 | 5.8082 | 5.4929 | 5.149 | 4.7674 | 4.1123 | 3.3888 | 2.6164 | -1.3397 | -3.9877 | -5.1459
|  | TOTTON PRIMARY | CF |  |  |  |  | 5.9246 | 5.7929 | 5.4348 | 5.2541 | 5.047 | 4.8021 | 4.6062 | 4.2613 | 3.8766 | 1.0827 | -1.7101 | -4.0989 | 9.3848 | 9.297 | 8.9562 | 8.847 | 8.7092 | 8.4225 | 8.2705 | 7.8766 | 7.4439 | 3.9858 | -1.3877 | -9.9224 | 6.795 | 6.6633 | 6.297 | 6.1592 | 5.9746 | 5.7603 | 5.7246 | 5.4674 | 5.1817 | 2.5297 | -0.48667 | -2.8428
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK PRIMARY | MINIMUM HEADROOM | SU 45156 14783 | NO | NO | 1.009 | 10.2592 | 9.948 | 9.1306 | 8.2224 | 7.2245 | 5.7122 | 4.0235 | 2.3347 | 1.2255 | -5.5102 | -11.0235 | -14.0663 | 13.95 | 13.6327 | 12.9908 | 12.2153 | 11.3571 | 10.2133 | 8.9153 | 7.5939 | 6.6571 | 1.2684 | -7.1347 | -26.2429 | 9.8276 | 9.551 | 8.7633 | 7.8908 | 6.9286 | 5.502 | 3.898 | 2.2929 | 1.2724 | -4.4418 | -9.3184 | -11.8663
|  | TOWNHILL PARK PRIMARY | EE |  |  |  |  | 10.2592 | 9.948 | 9.1306 | 8.2224 | 7.2245 | 5.7122 | 4.0235 | 2.3347 | 1.2255 | -5.0245 | -9.7429 | -13.5276 | 13.95 | 13.6327 | 12.9908 | 12.2153 | 11.3571 | 10.2133 | 8.9153 | 7.5939 | 6.6571 | 1.2684 | -5.0541 | -15.199 | 9.8276 | 9.551 | 8.7633 | 7.8908 | 6.9286 | 5.502 | 3.898 | 2.2929 | 1.2724 | -4.1561 | -8.2102 | -11.4347
|  | TOWNHILL PARK PRIMARY | HT |  |  |  |  | 10.948 | 10.2633 | 9.5204 | 9.2969 | 8.5724 | 7.2551 | 5.8224 | 4.3276 | 2.7653 | -5.5102 | -11.0235 | -14.0663 | 14.5316 | 14.1469 | 13.6878 | 13.5561 | 13.1163 | 12.3898 | 11.5704 | 10.6888 | 9.7633 | 5.2571 | 2.6888 | 1.4235 | 10.5235 | 9.8776 | 9.1735 | 8.9959 | 8.3071 | 7.1255 | 5.8071 | 4.4235 | 2.9755 | -4.4418 | -9.3184 | -11.8663
|  | TOWNHILL PARK PRIMARY | HE |  |  |  |  | 11 | 10.3673 | 9.6939 | 9.5633 | 8.8898 | 7.8214 | 6.6673 | 5.4633 | 4.2082 | -2.5173 | -7.2765 | -9.5571 | 14.3663 | 13.8878 | 13.3724 | 13.1092 | 12.5296 | 11.752 | 10.8633 | 9.8786 | 8.8265 | 2.6837 | -3.8673 | -13.3541 | 10.5663 | 9.9653 | 9.3214 | 9.2224 | 8.5806 | 7.6173 | 6.5378 | 5.402 | 4.2184 | -1.8653 | -5.9592 | -7.8398
|  | TOWNHILL PARK PRIMARY | CF |  |  |  |  | 11.4949 | 11.1184 | 10.6735 | 10.1867 | 10.2357 | 9.7837 | 9.2378 | 8.6633 | 8.0582 | 3.6643 | -0.85408 | -5.4204 | 14.5969 | 14.2224 | 13.7939 | 13.298 | 13.0071 | 12.3816 | 11.6459 | 10.8714 | 10.0235 | 3.5776 | -7.1347 | -26.2429 | 11.0122 | 10.651 | 10.2276 | 9.7561 | 9.8224 | 9.3929 | 8.8663 | 8.3112 | 7.7276 | 3.5663 | -0.52041 | -4.3684
MINETY GSP | SWINDON BSP | TRADING ESTATE PRIMARY | MINIMUM HEADROOM | SU 13490 85868 | NO | NO | 5.44 | 6.4853 | 5.7088 | 4.7945 | 3.6812 | 1.9904 | 0.15675 | -2.1871 | -4.4667 | -6.3157 | -14.7973 | -18.1279 | -18.5188 | 7.9772 | 7.3221 | 6.5547 | 5.6649 | 4.2537 | 2.7639 | 0.84144 | -1.0688 | -2.6096 | -9.229 | -11.7841 | -12.183 | 6.6506 | 6.0363 | 5.068 | 3.9476 | 2.319 | 0.55063 | -1.7035 | -3.9055 | -5.6902 | -13.8963 | -17.1055 | -17.4779
|  | TRADING ESTATE PRIMARY | EE |  |  |  |  | 6.4853 | 5.7088 | 4.7945 | 3.6812 | 1.9904 | 0.15675 | -2.1871 | -4.4667 | -6.3157 | -11.4024 | -12.281 | -12.3055 | 7.9772 | 7.3221 | 6.5547 | 5.6649 | 4.2537 | 2.7639 | 0.84144 | -1.0688 | -2.6096 | -6.6004 | -7.2637 | -7.4126 | 6.6506 | 6.0363 | 5.068 | 3.9476 | 2.319 | 0.55063 | -1.7035 | -3.9055 | -5.6902 | -10.5861 | -11.4096 | -11.4351
|  | TRADING ESTATE PRIMARY | HT |  |  |  |  | 7.3955 | 6.921 | 6.3496 | 5.2272 | 3.8649 | 2.3363 | 0.45981 | -1.329 | -2.8086 | -8.7984 | -11.3453 | -11.732 | 8.7496 | 8.3547 | 7.8812 | 6.8384 | 5.57 | 4.2629 | 2.6751 | 1.167 | 0.0077694 | -4.4749 | -6.3657 | -6.6718 | 7.37 | 6.9986 | 6.5496 | 5.5547 | 4.1557 | 2.6527 | 0.84552 | -0.88509 | -2.3137 | -8.08 | -10.5188 | -10.879
|  | TRADING ESTATE PRIMARY | HE |  |  |  |  | 7.0282 | 6.371 | 5.5792 | 4.6353 | 3.0598 | 1.3016 | -0.99835 | -3.4361 | -5.7779 | -14.7973 | -18.1279 | -18.5188 | 8.4363 | 7.8843 | 7.221 | 6.4282 | 5.0843 | 3.6537 | 1.7639 | -0.26774 | -2.1922 | -9.229 | -11.7841 | -12.183 | 7.0792 | 6.5598 | 5.8986 | 4.9006 | 3.3516 | 1.6588 | -0.5555 | -2.9116 | -5.179 | -13.8963 | -17.1055 | -17.4779
|  | TRADING ESTATE PRIMARY | CF |  |  |  |  | 7.7088 | 7.3537 | 6.9353 | 6.4414 | 5.871 | 5.0863 | 3.97 | 2.5404 | 1.0312 | -6.7239 | -12.1994 | -15.3422 | 9.0037 | 8.7047 | 8.3516 | 7.9323 | 7.4496 | 6.7445 | 5.7333 | 4.4914 | 3.2088 | -3.1657 | -7.3739 | -9.8973 | 7.6119 | 7.3282 | 6.9986 | 6.6098 | 6.1598 | 5.4067 | 4.2496 | 2.8435 | 1.3853 | -6.1157 | -11.3902 | -14.4096
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | TRASH GREEN PRIMARY | MINIMUM HEADROOM | SU 66254 68745 | NO | NO | 3.331 | 1.5412 | 0.91573 | -0.1659 | -1.4781 | -2.9669 | -4.5679 | -6.6659 | -8.6771 | -10.6179 | -20.9588 | -24.821 | -25.1639 | 3.43 | 2.7137 | 1.8719 | 0.87696 | -0.25366 | -1.4496 | -3.0322 | -4.5465 | -6.0047 | -13.8149 | -16.6751 | -16.9496 | 0.46573 | -0.44753 | -1.523 | -2.7894 | -4.2281 | -5.7649 | -7.7873 | -9.723 | -11.5914 | -21.5547 | -25.2506 | -25.5608
|  | TRASH GREEN PRIMARY | EE |  |  |  |  | 1.5412 | 0.91573 | -0.1659 | -1.4781 | -2.9669 | -4.5679 | -6.6659 | -8.6771 | -10.6179 | -18.2465 | -22.0843 | -23.2649 | 3.43 | 2.7137 | 1.8719 | 0.87696 | -0.25366 | -1.4496 | -3.0322 | -4.5465 | -6.0047 | -11.6659 | -14.4945 | -15.3649 | 0.46573 | -0.44753 | -1.523 | -2.7894 | -4.2281 | -5.7649 | -7.7873 | -9.723 | -11.5914 | -18.9159 | -22.5884 | -23.7016
|  | TRASH GREEN PRIMARY | HT |  |  |  |  | 2.0923 | 1.6423 | 1.1555 | 0.55144 | -0.52713 | -1.87 | -3.5312 | -5.3169 | -7.0853 | -15.2037 | -19.572 | -21.2445 | 4.2647 | 3.777 | 3.1974 | 2.4861 | 1.6423 | 0.64838 | -0.59039 | -1.9241 | -3.2394 | -9.27 | -12.469 | -13.6639 | 1.5096 | 0.87593 | 0.129 | -0.78325 | -1.8628 | -3.1526 | -4.7516 | -6.469 | -8.1649 | -15.97 | -20.1526 | -21.7424
|  | TRASH GREEN PRIMARY | HE |  |  |  |  | 1.9841 | 1.4616 | 0.8443 | -0.34549 | -1.7894 | -3.4945 | -5.6516 | -7.9802 | -10.1241 | -20.9588 | -24.821 | -25.1639 | 4.0331 | 3.4035 | 2.6484 | 1.7484 | 0.65451 | -0.63121 | -2.2628 | -4.0302 | -5.6424 | -13.8149 | -16.6751 | -16.9496 | 1.2239 | 0.41573 | -0.54651 | -1.6924 | -3.0843 | -4.7292 | -6.8088 | -9.0557 | -11.1149 | -21.5547 | -25.2506 | -25.5608
|  | TRASH GREEN PRIMARY | CF |  |  |  |  | 2.4994 | 2.2198 | 1.9259 | 1.5576 | 1.1341 | 0.71777 | -0.29243 | -1.4608 | -2.7006 | -9.9975 | -16.6261 | -20.6384 | 4.731 | 4.4412 | 4.0739 | 3.6412 | 3.1249 | 2.5535 | 1.7647 | 0.86981 | -0.079167 | -5.6292 | -10.6496 | -13.72 | 2.0912 | 1.7474 | 1.279 | 0.72696 | 0.071853 | -0.64958 | -1.6445 | -2.772 | -3.971 | -11.0037 | -17.3781 | -21.2159
MELKSHAM GSP | NORRINGTON BSP | TROWBRIDGE TOWN PRIMARY | MINIMUM HEADROOM | ST 84668 58036 | NO | YES | 5.759 | 11.234 | 10.6361 | 10.3401 | 9.7646 | 9.1167 | 8.1452 | 7.0646 | 5.9401 | 5.0993 | 0.77585 | -2.8966 | -5.0374 | 16.5412 | 16.1248 | 15.9146 | 15.4901 | 15.0156 | 14.385 | 13.6656 | 12.9167 | 12.332 | 9.1136 | 5.2524 | -4.1986 | 12.7554 | 12.2401 | 11.9065 | 11.3003 | 10.6279 | 9.7361 | 8.6973 | 7.6667 | 6.8156 | 3.0126 | 0.12789 | -1.7578
|  | TROWBRIDGE TOWN PRIMARY | EE |  |  |  |  | 11.234 | 10.6361 | 10.3401 | 9.7646 | 9.1167 | 8.1452 | 7.0646 | 5.9401 | 5.0993 | 0.88912 | -2.2007 | -4.5997 | 16.5412 | 16.1248 | 15.9146 | 15.4901 | 15.0156 | 14.385 | 13.6656 | 12.9167 | 12.332 | 9.1136 | 5.6697 | 0.59218 | 12.7554 | 12.2401 | 11.9065 | 11.3003 | 10.6279 | 9.7361 | 8.6973 | 7.6667 | 6.8156 | 3.2646 | 0.72789 | -1.3864
|  | TROWBRIDGE TOWN PRIMARY | HT |  |  |  |  | 11.4565 | 10.9718 | 10.534 | 10.0391 | 9.434 | 8.8269 | 7.8748 | 6.8871 | 5.9687 | 0.77585 | -2.8966 | -5.0374 | 16.8075 | 16.5299 | 16.2687 | 15.9748 | 15.6146 | 15.3565 | 14.8483 | 14.3136 | 13.8034 | 11.0912 | 9.3391 | 8.3544 | 12.9667 | 12.5493 | 12.1605 | 11.7208 | 11.1891 | 10.6473 | 9.7993 | 8.8891 | 7.9881 | 3.3901 | 0.12789 | -1.7578
|  | TROWBRIDGE TOWN PRIMARY | HE |  |  |  |  | 11.5361 | 11.081 | 10.6432 | 10.1503 | 9.5901 | 9.1238 | 8.2952 | 7.3973 | 6.5565 | 2.1656 | -0.94762 | -2.4711 | 16.7616 | 16.4432 | 16.1299 | 15.7677 | 15.3514 | 15.0575 | 14.4963 | 13.883 | 13.2779 | 9.7452 | 6.2126 | 1.5442 | 13.0228 | 12.631 | 12.2442 | 11.7993 | 11.1932 | 10.5605 | 9.6514 | 8.682 | 7.7044 | 3.0126 | 0.47891 | -0.81904
|  | TROWBRIDGE TOWN PRIMARY | CF |  |  |  |  | 11.8667 | 11.6912 | 11.4544 | 11.2381 | 10.9759 | 10.6738 | 10.5871 | 10.183 | 9.7156 | 6.582 | 3.4483 | 0.53606 | 16.9136 | 16.734 | 16.5014 | 16.2605 | 15.9595 | 15.5932 | 15.3728 | 14.9197 | 14.4167 | 10.8401 | 5.2524 | -4.1986 | 13.3126 | 13.1585 | 12.9493 | 12.7575 | 12.5248 | 12.2585 | 12.0228 | 11.5299 | 10.9799 | 7.4289 | 4.1116 | 1.4871
BRAMLEY (BASI) GSP | READING BSP | TWYFORD PRIMARY | MINIMUM HEADROOM | SU 78430 76339 | NO | YES | 0.91 | 0.20714 | -0.31735 | -0.87959 | -0.98061 | -1.4827 | -2.1908 | -2.9816 | -3.7561 | -4.2724 | -7.7673 | -10.4286 | -11.999 | 4.9643 | 4.5714 | 4.1418 | 4.1347 | 3.7561 | 3.2622 | 2.6969 | 2.1327 | 1.7827 | -0.27857 | -3.1827 | -9.9755 | 1.649 | 1.1571 | 0.62959 | 0.52347 | 0.046939 | -0.63367 | -1.3969 | -2.149 | -2.65 | -5.5898 | -7.9694 | -9.3327
|  | TWYFORD PRIMARY | EE |  |  |  |  | 0.20714 | -0.31735 | -0.87959 | -0.98061 | -1.4827 | -2.1908 | -2.9816 | -3.7561 | -4.2724 | -7.301 | -9.7398 | -11.599 | 4.9643 | 4.5714 | 4.1418 | 4.1347 | 3.7561 | 3.2622 | 2.6969 | 2.1327 | 1.7827 | -0.27857 | -2.6602 | -6.2612 | 1.649 | 1.1571 | 0.62959 | 0.52347 | 0.046939 | -0.63367 | -1.3969 | -2.149 | -2.65 | -5.2612 | -7.3878 | -9.0122
|  | TWYFORD PRIMARY | HT |  |  |  |  | 0.37857 | -0.07551 | -0.45918 | -0.87449 | -1.3439 | -1.6531 | -2.3704 | -3.1041 | -3.8561 | -7.7673 | -10.4286 | -11.999 | 5.2031 | 4.9153 | 4.6755 | 4.3969 | 4.0796 | 4.049 | 3.649 | 3.2306 | 2.801 | 0.80612 | -0.26429 | -0.84286 | 1.7408 | 1.3561 | 1.0173 | 0.64286 | 0.19898 | -0.096939 | -0.73673 | -1.4173 | -2.1153 | -5.5898 | -7.9694 | -9.3327
|  | TWYFORD PRIMARY | HE |  |  |  |  | 0.47449 | 0.060204 | -0.30918 | -0.73469 | -1.1867 | -1.3429 | -1.902 | -2.4755 | -3.0704 | -6.3908 | -8.8296 | -9.9643 | 5.1929 | 4.8908 | 4.6265 | 4.3031 | 3.9561 | 3.9306 | 3.5327 | 3.1143 | 2.6735 | 0.1398 | -2.2847 | -5.5673 | 1.8255 | 1.4745 | 1.149 | 0.76735 | 0.3398 | 0.17245 | -0.35612 | -0.91122 | -1.4827 | -4.4592 | -6.5908 | -7.5663
|  | TWYFORD PRIMARY | CF |  |  |  |  | 0.80816 | 0.63673 | 0.39898 | 0.2051 | -0.072449 | -0.37653 | -0.3449 | -0.68878 | -1.049 | -3.45 | -5.5949 | -8.0133 | 5.3439 | 5.1765 | 4.948 | 4.7602 | 4.4847 | 4.1714 | 4.1724 | 3.8327 | 3.4684 | 0.73776 | -3.1827 | -9.9755 | 2.1357 | 2.0082 | 1.8337 | 1.649 | 1.3918 | 1.1092 | 1.1408 | 0.81735 | 0.47755 | -1.8265 | -3.9082 | -5.8724
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | UNION STREET PRIMARY | MINIMUM HEADROOM | SP 52865 05849 | NO | NO | 4.137 | 8.5357 | 8.0929 | 7.5714 | 6.9847 | 6.349 | 5.7276 | 4.7459 | 3.8245 | 3.1622 | 0.50306 | -1.2245 | -1.1949 | 11.7884 | 11.4108 | 10.9578 | 10.4486 | 9.8884 | 9.4843 | 8.7271 | 7.9863 | 7.422 | 4.62 | 0.62408 | -9.6892 | 7.7498 | 7.3233 | 6.8202 | 6.258 | 5.6457 | 5.06 | 4.1243 | 3.2355 | 2.5967 | 0.17633 | -1.3145 | -1.3022
|  | UNION STREET PRIMARY | EE |  |  |  |  | 8.5357 | 8.0929 | 7.5714 | 6.9847 | 6.349 | 5.7276 | 4.7459 | 3.8245 | 3.1622 | 0.50306 | -0.78776 | -0.41531 | 11.7884 | 11.4108 | 10.9578 | 10.4486 | 9.8884 | 9.4843 | 8.7271 | 7.9863 | 7.422 | 4.62 | 1.668 | -2.7953 | 7.7498 | 7.3233 | 6.8202 | 6.258 | 5.6457 | 5.06 | 4.1243 | 3.2355 | 2.5967 | 0.17633 | -0.91347 | -0.66959
|  | UNION STREET PRIMARY | HT |  |  |  |  | 8.8153 | 8.5 | 8.1235 | 7.7071 | 7.3 | 6.2837 | 5.5531 | 5.1857 | 4.4582 | 0.79388 | -1.2245 | -1.1949 | 12.1261 | 11.9108 | 11.6445 | 11.3424 | 11.0527 | 10.4659 | 9.9822 | 9.7955 | 9.32 | 7.0302 | 5.8588 | 5.7516 | 8.0233 | 7.7263 | 7.3692 | 6.9733 | 6.5773 | 5.6416 | 4.9427 | 4.5988 | 3.908 | 0.51102 | -1.3145 | -1.3022
|  | UNION STREET PRIMARY | HE |  |  |  |  | 8.8878 | 8.5888 | 8.2571 | 7.8929 | 7.55 | 6.7643 | 6.0469 | 5.3643 | 5.1173 | 2.6214 | 1.5408 | 1.4306 | 12.0649 | 11.8037 | 11.5006 | 11.1659 | 10.8404 | 10.2843 | 9.72 | 9.1476 | 8.9394 | 6.0322 | 3.1098 | -1.4239 | 8.0845 | 7.8029 | 7.4824 | 7.1355 | 6.7978 | 6.0661 | 5.3835 | 4.7253 | 4.5233 | 2.1916 | 1.2467 | 1.1478
|  | UNION STREET PRIMARY | CF |  |  |  |  | 9.1694 | 8.9969 | 8.8367 | 8.6286 | 8.3969 | 8.199 | 7.8663 | 7.4724 | 7.0622 | 5.1378 | 3.052 | 1.05 | 12.2078 | 11.9884 | 11.7731 | 11.5067 | 11.1863 | 10.8639 | 10.4159 | 9.922 | 9.3935 | 6.219 | 0.62408 | -9.6892 | 8.3529 | 8.1886 | 8.0396 | 7.8396 | 7.6202 | 7.4294 | 7.1131 | 6.7437 | 6.362 | 4.5427 | 2.5478 | 0.80286
COWLEY GSP | OXFORD (OSNEY) BSP | UNIVERSITY PARKS PRIMARY | MINIMUM HEADROOM | SP 51472 07052 | NO | YES | 0.982 | 29.7173 | 29.6265 | 29.5245 | 29.4184 | 29.3071 | 29.1633 | 29.0194 | 28.8684 | 28.7418 | 28.2357 | 27.9347 | 27.8306 | 30.2612 | 30.1724 | 30.0928 | 30.0071 | 29.9194 | 29.8061 | 29.698 | 29.5755 | 29.4735 | 28.9816 | 28.348 | 26.1275 | 29.2206 | 29.139 | 29.0451 | 28.9492 | 28.8512 | 28.7226 | 28.5961 | 28.4635 | 28.3522 | 27.9165 | 27.6665 | 27.5777
|  | UNIVERSITY PARKS PRIMARY | EE |  |  |  |  | 29.7571 | 29.6326 | 29.5245 | 29.4184 | 29.3071 | 29.1633 | 29.0194 | 28.8684 | 28.7418 | 28.2357 | 27.9347 | 27.8306 | 30.2612 | 30.1724 | 30.0928 | 30.0071 | 29.9194 | 29.8061 | 29.698 | 29.5755 | 29.4735 | 28.9816 | 28.3663 | 27.2949 | 29.2471 | 29.139 | 29.0451 | 28.9492 | 28.8512 | 28.7226 | 28.5961 | 28.4635 | 28.3522 | 27.9165 | 27.6665 | 27.5777
|  | UNIVERSITY PARKS PRIMARY | HT |  |  |  |  | 29.7173 | 29.6265 | 29.5296 | 29.4296 | 29.3286 | 29.2245 | 29.1143 | 28.999 | 28.8837 | 28.3398 | 28.0061 | 27.8684 | 30.2622 | 30.2051 | 30.1449 | 30.0765 | 30.0163 | 29.949 | 29.8765 | 29.801 | 29.7235 | 29.3745 | 29.1469 | 29.05 | 29.2206 | 29.142 | 29.0614 | 28.9737 | 28.8869 | 28.7971 | 28.7022 | 28.6022 | 28.5012 | 28.0328 | 27.7441 | 27.6247
|  | UNIVERSITY PARKS PRIMARY | HE |  |  |  |  | 29.798 | 29.6969 | 29.6082 | 29.5204 | 29.4388 | 29.3582 | 29.2735 | 29.1826 | 29.0928 | 28.8122 | 28.7224 | 28.5949 | 30.2918 | 30.2204 | 30.1551 | 30.0867 | 30.0224 | 29.9571 | 29.8877 | 29.8082 | 29.7245 | 29.3877 | 28.9949 | 27.9296 | 29.2859 | 29.1982 | 29.1226 | 29.0471 | 28.9737 | 28.9033 | 28.8277 | 28.7471 | 28.6655 | 28.4196 | 28.3451 | 28.2737
|  | UNIVERSITY PARKS PRIMARY | CF |  |  |  |  | 29.901 | 29.8582 | 29.8133 | 29.7653 | 29.7133 | 29.6592 | 29.6 | 29.5194 | 29.4408 | 29.0796 | 28.8071 | 28.5816 | 30.35 | 30.3102 | 30.2653 | 30.2184 | 30.1633 | 30.1041 | 30.0408 | 29.9592 | 29.8765 | 29.4112 | 28.348 | 26.1275 | 29.3737 | 29.3369 | 29.2951 | 29.2533 | 29.2063 | 29.1594 | 29.1063 | 29.0369 | 28.9686 | 28.6533 | 28.4196 | 28.2298
EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD PRIMARY | MINIMUM HEADROOM | SP 51750 25667 | NO | YES | 5.45 | -1.97 | -2.2292 | -2.6333 | -3.0914 | -4.1159 | -5.7169 | -7.3098 | -8.6873 | -9.4853 | -10.7771 | -11.0822 | -11.3833 | -0.90673 | -1.0578 | -1.2863 | -1.518 | -2.4731 | -3.5935 | -4.9843 | -6.1659 | -6.6751 | -7.5149 | -8.0516 | -9.4486 | -2.1129 | -2.3363 | -2.6771 | -3.0557 | -4.1751 | -5.7414 | -7.2404 | -8.5486 | -9.2394 | -10.3424 | -10.6108 | -10.8567
|  | UPPER HEYFORD PRIMARY | EE |  |  |  |  | -1.97 | -2.2292 | -2.6333 | -3.0914 | -4.1159 | -5.568 | -6.9037 | -8.1557 | -9.1578 | -10.7771 | -11.0822 | -11.27 | -0.90673 | -1.0578 | -1.2863 | -1.518 | -2.3547 | -3.4914 | -4.5465 | -5.5435 | -6.3006 | -7.5149 | -7.9516 | -8.5884 | -2.1129 | -2.3363 | -2.6771 | -3.0557 | -4.1751 | -5.5782 | -6.819 | -7.9731 | -8.8802 | -10.3424 | -10.6108 | -10.7567
|  | UPPER HEYFORD PRIMARY | HT |  |  |  |  | -1.8976 | -2.1363 | -2.4873 | -2.9455 | -3.9914 | -5.7169 | -7.3098 | -8.6873 | -9.4853 | -10.6404 | -11.0516 | -11.3833 | -0.82918 | -0.95878 | -1.1292 | -1.3547 | -2.2149 | -3.5935 | -4.9843 | -6.1659 | -6.6751 | -7.2363 | -7.4414 | -7.6067 | -2.0404 | -2.2414 | -2.5271 | -2.9027 | -4.068 | -5.7414 | -7.2404 | -8.5486 | -9.2394 | -10.2241 | -10.5833 | -10.8567
|  | UPPER HEYFORD PRIMARY | HE |  |  |  |  | -1.8986 | -2.1373 | -2.4843 | -2.9384 | -3.9139 | -5.3516 | -6.6822 | -7.9108 | -8.9231 | -10.7373 | -11.0322 | -11.1863 | -0.84857 | -0.98122 | -1.1649 | -1.3965 | -2.1904 | -3.2812 | -4.3649 | -5.3516 | -6.1394 | -7.4904 | -7.9322 | -8.5465 | -2.0404 | -2.2404 | -2.5231 | -2.8965 | -3.969 | -5.3629 | -6.5986 | -7.7312 | -8.6486 | -10.3057 | -10.5639 | -10.6802
|  | UPPER HEYFORD PRIMARY | CF |  |  |  |  | -1.6414 | -1.7588 | -1.9016 | -2.1139 | -3.6027 | -4.5608 | -5.5649 | -6.5302 | -7.421 | -9.8271 | -10.4639 | -11.118 | -0.72102 | -0.79959 | -0.88633 | -1.0108 | -2.4731 | -3.2547 | -3.9741 | -4.6618 | -5.2669 | -7.1833 | -8.0516 | -9.4486 | -1.8343 | -1.9363 | -2.0537 | -2.2322 | -4.0486 | -4.9098 | -5.771 | -6.5976 | -7.3506 | -9.4802 | -10.0588 | -10.6343
IVER 132KV GSP | UPTON BSP | UPTON PRIMARY | MINIMUM HEADROOM | TQ 00800 79434 | NO | YES | 4.681 | 3.6249 | 3.0371 | 2.5514 | 1.8994 | 0.93 | -0.47918 | -1.9822 | -3.3996 | -4.5496 | -8.8741 | -12.0639 | -12.672 | 9.2627 | 9.0116 | 8.7239 | 8.1433 | 7.3922 | 6.2545 | 4.9647 | 3.7616 | 2.778 | -1.5751 | -6.2159 | -19.2414 | 3.6596 | 3.0494 | 2.7127 | 2.0678 | 1.1596 | -0.22612 | -1.7424 | -3.1527 | -4.27 | -8.268 | -11.2833 | -11.9669
|  | UPTON PRIMARY | EE |  |  |  |  | 3.6249 | 3.0371 | 2.5514 | 1.8994 | 0.93 | -0.47918 | -1.9822 | -3.3996 | -4.5496 | -8.8741 | -11.1037 | -11.1271 | 9.2627 | 9.0116 | 8.7239 | 8.1433 | 7.3922 | 6.2545 | 4.9647 | 3.7616 | 2.778 | -1.5751 | -5.8312 | -12.07 | 3.6596 | 3.0494 | 2.7127 | 2.0678 | 1.1596 | -0.22612 | -1.7424 | -3.1527 | -4.27 | -8.268 | -10.2598 | -10.5037
|  | UPTON PRIMARY | HT |  |  |  |  | 4.03 | 3.5963 | 2.9718 | 2.431 | 1.5657 | 0.71571 | -0.50265 | -1.6945 | -2.9588 | -8.77 | -12.0639 | -12.672 | 9.479 | 9.3157 | 9.0922 | 8.8851 | 8.4035 | 7.8953 | 6.9759 | 6.1096 | 5.1657 | 1.1178 | -1.118 | -1.8853 | 4.1188 | 3.6882 | 3.1402 | 2.6157 | 1.8229 | 1.0678 | -0.14755 | -1.32 | -2.57 | -8.1741 | -11.2833 | -11.9669
|  | UPTON PRIMARY | HE |  |  |  |  | 4.0688 | 3.6718 | 3.0973 | 2.6106 | 1.8086 | 1.1167 | 0.067755 | -0.89959 | -1.919 | -6.269 | -8.3996 | -9.0976 | 9.4422 | 9.2545 | 9.0096 | 8.7157 | 8.0994 | 7.5739 | 6.6831 | 5.8953 | 5.0412 | 0.3249 | -4.1118 | -10.5751 | 4.1524 | 3.7524 | 3.2524 | 2.7759 | 2.0453 | 1.4535 | 0.41878 | -0.50673 | -1.4884 | -5.67 | -7.6231 | -8.5833
|  | UPTON PRIMARY | CF |  |  |  |  | 4.3933 | 4.2086 | 3.9535 | 3.6433 | 3.1484 | 2.4892 | 2.2178 | 1.6708 | 1.1402 | -1.9782 | -5.3251 | -8.3343 | 9.5759 | 9.4586 | 9.3188 | 9.1463 | 8.6678 | 7.9627 | 7.4565 | 6.7208 | 5.9871 | 1.3361 | -6.2159 | -19.2414 | 4.4198 | 4.2137 | 3.978 | 3.6586 | 3.1943 | 2.5535 | 2.379 | 1.8045 | 1.2576 | -1.7802 | -4.771 | -7.3527
IVER 66KV GSP |  | UXBRIDGE PRIMARY | MINIMUM HEADROOM | TQ 04984 83484 | NO | NO | 32.331 | 14.4058 | 44.0442 | 42.7942 | 41.3748 | 39.8585 | 38.2013 | 36.2299 | 34.2381 | 32.5207 | 27.9993 | 26.1513 | 24.8891 | 16.7968 | 46.6462 | 45.4268 | 44.2687 | 43.1095 | 41.885 | 40.4207 | 38.9605 | 37.5044 | 34.3524 | 30.3197 | 19.2656 | 11.2066 | 38.3697 | 37.1922 | 36.0115 | 34.8136 | 33.485 | 31.5452 | 29.6442 | 28.0126 | 23.8197 | 21.1411 | 20.0779
|  | UXBRIDGE PRIMARY | EE |  |  |  |  | 14.662 | 44.1013 | 42.8962 | 41.3748 | 39.8585 | 38.2013 | 36.2299 | 34.2381 | 32.5207 | 27.9993 | 26.4024 | 25.5534 | 17.3499 | 47.0381 | 45.9728 | 44.583 | 43.2575 | 41.885 | 40.4207 | 38.9605 | 37.5044 | 34.3524 | 30.4728 | 25.1687 | 11.6505 | 38.6687 | 37.6554 | 36.3248 | 34.9901 | 33.485 | 31.5452 | 29.6442 | 28.0126 | 23.8197 | 21.4656 | 20.5901
|  | UXBRIDGE PRIMARY | HT |  |  |  |  | 14.4058 | 44.0442 | 42.7942 | 41.5452 | 40.2493 | 38.9503 | 37.4024 | 35.8442 | 34.5677 | 29.0656 | 26.1513 | 24.8891 | 16.7968 | 46.6462 | 45.4268 | 44.2687 | 43.1095 | 42.0503 | 40.7983 | 39.582 | 38.9503 | 35.4779 | 33.885 | 33.1166 | 11.2066 | 38.3697 | 37.1922 | 36.0115 | 34.8136 | 33.633 | 32.1799 | 30.6013 | 29.4656 | 24.3217 | 21.1411 | 20.0779
|  | UXBRIDGE PRIMARY | HE |  |  |  |  | 15.0568 | 44.6717 | 43.5473 | 42.3289 | 40.9993 | 39.7034 | 38.1411 | 36.4268 | 34.6575 | 28.9973 | 26.7728 | 25.5585 | 17.5846 | 47.3615 | 46.285 | 45.1503 | 43.9156 | 42.8166 | 41.5197 | 40.186 | 38.8799 | 34.9177 | 32.0391 | 26.8187 | 11.9352 | 39.0656 | 38.0503 | 36.9799 | 35.7646 | 34.6268 | 33.2881 | 31.7268 | 30.0381 | 24.6646 | 22.5901 | 21.4513
|  | UXBRIDGE PRIMARY | CF |  |  |  |  | 15.4344 | 45.9258 | 45.0166 | 43.9228 | 42.784 | 41.7024 | 40.6585 | 39.4524 | 38.2075 | 33.7003 | 29.8248 | 27.0064 | 17.7683 | 48.4615 | 47.4217 | 46.2166 | 44.9768 | 43.8177 | 42.7697 | 41.5738 | 40.3493 | 36.7952 | 30.3197 | 19.2656 | 12.223 | 40.2024 | 39.2748 | 38.2289 | 37.1075 | 36.0483 | 35.0768 | 33.9666 | 32.834 | 29.0738 | 25.4268 | 22.8136
NURSLING GSP | VELMORE BSP | VELMORE PRIMARY | MINIMUM HEADROOM | SU 42935 19205 | NO | YES | 3.97 | 4.7253 | 3.9977 | 3.3283 | 2.4324 | 1.4171 | 0.15384 | -1.3696 | -2.9655 | -4.4196 | -10.6594 | -14.1758 | -15.8217 | 8.2477 | 7.7865 | 7.4987 | 6.9936 | 6.3467 | 5.4498 | 4.3589 | 3.2651 | 2.3242 | -2.09 | -6.4268 | -17.7798 | 5.4079 | 4.7171 | 4.0824 | 3.2304 | 2.264 | 1.0722 | -0.36453 | -1.9278 | -3.2829 | -9.1727 | -12.4329 | -13.9523
|  | VELMORE PRIMARY | EE |  |  |  |  | 4.7253 | 3.9977 | 3.3283 | 2.4324 | 1.4171 | 0.15384 | -1.3696 | -2.9655 | -4.4196 | -9.8023 | -11.9339 | -13.2951 | 8.2477 | 7.7865 | 7.4987 | 6.9936 | 6.3467 | 5.4498 | 4.3589 | 3.2651 | 2.3242 | -1.1829 | -5.0104 | -10.7421 | 5.4079 | 4.7171 | 4.0824 | 3.2304 | 2.264 | 1.0722 | -0.36453 | -1.9278 | -3.2829 | -8.2727 | -10.1747 | -11.3666
|  | VELMORE PRIMARY | HT |  |  |  |  | 5.3242 | 4.7814 | 4.2089 | 3.4875 | 2.6253 | 1.6702 | 0.39262 | -1.09 | -2.6411 | -9.3962 | -12.7043 | -14.4023 | 8.5936 | 8.2814 | 8.0049 | 7.6202 | 7.1477 | 6.711 | 5.8824 | 4.96 | 3.9569 | -0.288 | -2.24 | -3.1931 | 5.9875 | 5.4783 | 4.9345 | 4.2508 | 3.4406 | 2.5569 | 1.3008 | -0.084935 | -1.538 | -7.8655 | -10.9033 | -12.438
|  | VELMORE PRIMARY | HE |  |  |  |  | 5.2222 | 4.6334 | 3.9998 | 3.2263 | 2.3038 | 1.314 | -0.066567 | -1.5798 | -3.188 | -10.6594 | -14.1758 | -15.8217 | 8.4732 | 8.0885 | 7.7273 | 7.2702 | 6.7283 | 6.2589 | 5.3528 | 4.261 | 3.113 | -2.09 | -5.1125 | -10.6104 | 5.8906 | 5.3334 | 4.7314 | 3.9947 | 3.1161 | 2.1926 | 0.88649 | -0.54208 | -2.1186 | -9.1727 | -12.4329 | -13.9523
|  | VELMORE PRIMARY | CF |  |  |  |  | 5.7926 | 5.4528 | 5.1059 | 4.7008 | 4.2375 | 3.7375 | 3.1865 | 2.4212 | 1.5742 | -4.3839 | -9.4033 | -13.1002 | 8.6722 | 8.3753 | 8.1049 | 7.7804 | 7.3957 | 6.961 | 6.6304 | 6.0722 | 5.4569 | 0.42017 | -6.4268 | -17.7798 | 6.4304 | 6.112 | 5.7814 | 5.3936 | 4.9528 | 4.4712 | 3.9477 | 3.2181 | 2.411 | -3.1921 | -8.0125 | -11.4543
FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR PRIMARY | MINIMUM HEADROOM | SZ 56148 77857 | NO | YES | 0.44 | 14.4466 | 14.1344 | 13.7354 | 13.2905 | 13.2395 | 12.6456 | 11.965 | 11.2905 | 10.8099 | 8.2752 | 6.2007 | 5.0497 | 16.5987 | 16.3446 | 16.0252 | 15.6589 | 15.5987 | 15.167 | 14.6568 | 14.1436 | 13.7793 | 11.7721 | 9.3752 | 3.364 | 14.7701 | 14.466 | 14.0803 | 13.6507 | 13.6058 | 13.0477 | 12.4038 | 11.764 | 11.3181 | 9.0936 | 7.3262 | 6.3436
|  | VENTNOR PRIMARY | EE |  |  |  |  | 14.4466 | 14.1344 | 13.7354 | 13.2905 | 13.2395 | 12.6456 | 11.965 | 11.2905 | 10.8099 | 8.2752 | 6.6364 | 5.3915 | 16.5987 | 16.3446 | 16.0252 | 15.6589 | 15.5987 | 15.167 | 14.6568 | 14.1436 | 13.7793 | 11.7721 | 9.7589 | 6.6558 | 14.7701 | 14.466 | 14.0803 | 13.6507 | 13.6058 | 13.0477 | 12.4038 | 11.764 | 11.3181 | 9.0936 | 7.7119 | 6.6272
|  | VENTNOR PRIMARY | HT |  |  |  |  | 14.6732 | 14.4436 | 14.1701 | 13.9048 | 13.566 | 13.0119 | 12.3752 | 12.1262 | 11.5201 | 8.3436 | 6.2007 | 5.0497 | 16.8517 | 16.6977 | 16.5048 | 16.3252 | 16.0813 | 15.7426 | 15.3487 | 15.2926 | 14.916 | 13.0997 | 12.0568 | 11.5732 | 15.0313 | 14.8058 | 14.5313 | 14.2752 | 13.9385 | 13.416 | 12.8232 | 12.6477 | 12.0793 | 9.1844 | 7.3262 | 6.3436
|  | VENTNOR PRIMARY | HE |  |  |  |  | 14.6783 | 14.4599 | 14.1987 | 13.9538 | 13.6456 | 13.1701 | 12.617 | 12.4548 | 11.9415 | 9.1477 | 7.4977 | 6.7895 | 16.8028 | 16.6303 | 16.415 | 16.2028 | 15.9313 | 15.5762 | 15.1599 | 15.0803 | 14.6711 | 12.3487 | 10.264 | 7.3997 | 15.0344 | 14.8201 | 14.563 | 14.3252 | 14.0201 | 13.567 | 13.0466 | 12.9487 | 12.463 | 9.9303 | 8.5181 | 7.9221
|  | VENTNOR PRIMARY | CF |  |  |  |  | 14.8395 | 14.667 | 14.513 | 14.3058 | 14.1201 | 13.8772 | 13.5885 | 13.2752 | 12.9456 | 11.5946 | 9.7762 | 8.117 | 16.8905 | 16.7242 | 16.5772 | 16.3619 | 16.1558 | 15.8762 | 15.5497 | 15.1987 | 14.8242 | 12.8538 | 9.3752 | 3.364 | 15.1823 | 15.0068 | 14.8599 | 14.6528 | 14.4844 | 14.2487 | 13.966 | 13.663 | 13.3436 | 12.0834 | 10.4487 | 9.0344
MANNINGTON GSP | MANNINGTON BSP | VERWOOD PRIMARY | MINIMUM HEADROOM | SU 07716 10226 | NO | NO | 0.558 | 2.6714 | 2.1265 | 2.0265 | 1.5939 | 1.1367 | 0.42857 | -0.36122 | -1.15 | -1.6633 | -4.7582 | -7.4051 | -8.8194 | 5.1133 | 4.7276 | 4.6755 | 4.3459 | 3.9918 | 3.5133 | 2.9622 | 2.4031 | 2.0571 | 0.095918 | -2.7245 | -9.15 | 2.8969 | 2.3612 | 2.3296 | 1.9163 | 1.4786 | 0.81531 | 0.062245 | -0.68776 | -1.1245 | -3.7959 | -5.999 | -7.1806
|  | VERWOOD PRIMARY | EE |  |  |  |  | 2.6714 | 2.1265 | 2.0265 | 1.5939 | 1.1367 | 0.42857 | -0.36122 | -1.15 | -1.6633 | -4.3622 | -6.8469 | -8.5806 | 5.1133 | 4.7276 | 4.6755 | 4.3459 | 3.9918 | 3.5133 | 2.9622 | 2.4031 | 2.0571 | 0.095918 | -2.2786 | -5.7224 | 2.8969 | 2.3612 | 2.3296 | 1.9163 | 1.4786 | 0.81531 | 0.062245 | -0.68776 | -1.1245 | -3.4837 | -5.5092 | -6.9786
|  | VERWOOD PRIMARY | HT |  |  |  |  | 2.9122 | 2.4561 | 2.1082 | 1.6908 | 1.2418 | 0.9602 | 0.26531 | -0.45 | -1.1827 | -4.7582 | -7.4051 | -8.8194 | 5.3898 | 5.1235 | 4.9194 | 4.6602 | 4.3755 | 4.3367 | 3.9653 | 3.5735 | 3.1643 | 1.3347 | 0.25408 | -0.30204 | 3.1582 | 2.7418 | 2.4204 | 2.0255 | 1.5908 | 1.3857 | 0.75 | 0.092857 | -0.58367 | -3.7959 | -5.999 | -7.1806
|  | VERWOOD PRIMARY | HE |  |  |  |  | 2.9612 | 2.5347 | 2.2184 | 1.8347 | 1.4265 | 1.3061 | 0.76429 | 0.19796 | -0.37959 | -3.3755 | -5.8133 | -7.0071 | 5.3439 | 5.052 | 4.8224 | 4.5316 | 4.2153 | 4.1745 | 3.7908 | 3.3786 | 2.9449 | 0.5449 | -1.8469 | -5.0878 | 3.201 | 2.8122 | 2.5194 | 2.15 | 1.7429 | 1.6837 | 1.1796 | 0.65204 | 0.11224 | -2.6306 | -4.6071 | -5.5959
|  | VERWOOD PRIMARY | CF |  |  |  |  | 3.1847 | 2.8827 | 2.6857 | 2.4367 | 2.1755 | 1.9071 | 2.0184 | 1.7612 | 1.4888 | -0.56531 | -2.9429 | -4.9939 | 5.4408 | 5.2 | 5.0214 | 4.7878 | 4.5224 | 4.2153 | 4.2051 | 3.8878 | 3.5469 | 1.0704 | -2.7245 | -9.15 | 3.4041 | 3.1286 | 2.9378 | 2.6827 | 2.4143 | 2.1316 | 2.3204 | 2.0612 | 1.7816 | -0.18367 | -2.2408 | -3.9827
NORTH HYDE GSP |  | VICARAGE FARM ROAD PRIMARY | MINIMUM HEADROOM | TQ 12358 76435 | NO | YES | 41.166 | -20.4104 | 16.3019 | 14.5254 | 12.4336 | 9.8295 | 7.1029 | 4.0999 | 1.0968 | -1.3399 | -9.5481 | -14.1042 | -14.9624 | -9.9522 | 27.1703 | 25.908 | 24.4182 | 22.5336 | 20.5244 | 18.2336 | 15.9019 | 13.9815 | 5.907 | -1.1369 | -20.2256 | -17.5145 | 19.3754 | 17.7703 | 15.8774 | 13.4642 | 10.9029 | 8.0621 | 5.2274 | 2.8938 | -5.1379 | -9.9879 | -10.8379
|  | VICARAGE FARM ROAD PRIMARY | EE |  |  |  |  | -20.4104 | 16.3019 | 14.5254 | 12.4336 | 9.8295 | 7.1029 | 4.0999 | 1.0968 | -1.3399 | -9.5481 | -14.1042 | -14.9624 | -9.9522 | 27.1703 | 25.908 | 24.4182 | 22.5336 | 20.5244 | 18.2336 | 15.9019 | 13.9815 | 5.907 | -1.1369 | -9.8971 | -17.5145 | 19.3754 | 17.7703 | 15.8774 | 13.4642 | 10.9029 | 8.0621 | 5.2274 | 2.8938 | -5.1379 | -9.9879 | -10.8379
|  | VICARAGE FARM ROAD PRIMARY | HT |  |  |  |  | -19.6094 | 17.1091 | 15.4948 | 13.8815 | 11.7448 | 9.806 | 7.5917 | 5.2172 | 2.8468 | -6.5358 | -12.0971 | -13.194 | -9.1288 | 28.1652 | 27.2121 | 26.2856 | 24.9591 | 23.7121 | 22.1917 | 20.5315 | 18.8723 | 12.4825 | 8.9438 | 7.5642 | -16.6869 | 20.2131 | 18.8019 | 17.4274 | 15.4387 | 13.6193 | 11.5193 | 9.2652 | 7.0193 | -1.8879 | -7.0848 | -8.0164
|  | VICARAGE FARM ROAD PRIMARY | HE |  |  |  |  | -19.342 | 17.3836 | 15.958 | 14.7029 | 12.6223 | 10.4917 | 8.1438 | 5.6499 | 3.2019 | -7.9328 | -12.5603 | -13.1113 | -9.1206 | 27.9887 | 27.0019 | 26.1917 | 24.7285 | 23.1489 | 21.3356 | 19.3458 | 17.3274 | 8.1223 | 1.3305 | -7.2603 | -16.4675 | 20.4152 | 19.1519 | 18.105 | 16.1417 | 14.1346 | 11.904 | 9.5315 | 7.1999 | -4.2124 | -8.6154 | -9.1185
|  | VICARAGE FARM ROAD PRIMARY | CF |  |  |  |  | -18.3563 | 19.1876 | 18.3366 | 17.5866 | 16.7489 | 16.2795 | 15.1244 | 13.7407 | 12.2744 | 2.6458 | -3.9001 | -9.1899 | -8.5655 | 29.0223 | 28.2499 | 27.5346 | 26.6917 | 26.0642 | 24.8652 | 23.505 | 22.0142 | 11.7142 | -0.73481 | -20.2256 | -15.6012 | 21.9907 | 21.2019 | 20.507 | 19.7264 | 19.3336 | 18.2601 | 16.9907 | 15.6499 | 6.9009 | 0.080494 | -5.196
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | WALLINGFORD PRIMARY | MINIMUM HEADROOM | SU 59847 89486 | NO | NO | 4.111 | 10.4995 | 9.7709 | 8.3158 | 7.2087 | 4.0556 | 2.5189 | 0.65356 | -0.12195 | -3.7913 | -12.1699 | -23.2066 | -32.822 | 14.066 | 13.4619 | 12.0966 | 11.2507 | 7.9068 | 6.3578 | 4.516 | 4.0048 | -0.27583 | -9.7789 | -22.1503 | -34.1422 | 10.184 | 9.5207 | 8.0054 | 6.9513 | 3.3687 | 1.7738 | -0.28134 | -0.98542 | -5.4048 | -15.0436 | -27.2528 | -38.4517
|  | WALLINGFORD PRIMARY | EE |  |  |  |  | 10.4995 | 9.7709 | 8.9413 | 8.3709 | 6.7934 | 5.177 | 4.1413 | 2.0883 | 0.96682 | -5.1638 | -19.1862 | -25.1709 | 14.066 | 13.6242 | 13.1344 | 12.8323 | 11.4854 | 10.0905 | 9.4425 | 7.464 | 6.3711 | -0.24828 | -17.3217 | -25.9697 | 10.184 | 9.5207 | 8.7666 | 8.3942 | 6.7809 | 5.1248 | 4.1799 | 1.9483 | 0.76152 | -5.9313 | -22.3936 | -28.9895
|  | WALLINGFORD PRIMARY | HT |  |  |  |  | 10.6913 | 9.828 | 8.6944 | 7.8719 | 5.1934 | 3.5423 | 1.4852 | 0.34948 | -1.7597 | -9.7842 | -23.2066 | -32.822 | 14.2783 | 13.6742 | 12.7721 | 12.3487 | 9.668 | 8.1436 | 6.2303 | 5.4589 | 3.3211 | -4.4391 | -19.1911 | -29.8636 | 10.4544 | 9.6309 | 8.5136 | 7.8197 | 4.836 | 3.1452 | 0.9054 | -0.19154 | -2.6109 | -11.5854 | -27.2528 | -38.4517
|  | WALLINGFORD PRIMARY | HE |  |  |  |  | 10.7189 | 9.7729 | 8.3158 | 7.2087 | 4.0556 | 2.5189 | 0.65356 | -0.12195 | -3.7913 | -12.1699 | -22.372 | -30.5607 | 14.2252 | 13.4619 | 12.0966 | 11.2507 | 7.9068 | 6.3578 | 4.516 | 4.0048 | -0.27583 | -9.7789 | -22.1503 | -34.1422 | 10.4707 | 9.5391 | 8.0054 | 6.9513 | 3.3687 | 1.7738 | -0.28134 | -0.98542 | -5.4048 | -15.0436 | -26.7548 | -36.4854
|  | WALLINGFORD PRIMARY | CF |  |  |  |  | 10.9689 | 10.5097 | 9.9699 | 9.1719 | 8.2127 | 7.2903 | 6.4566 | 5.9454 | 5.1872 | 0.29846 | -6.1015 | -12.2699 | 14.3323 | 14.0364 | 13.6905 | 13.0436 | 12.2415 | 11.3323 | 10.5374 | 9.9466 | 9.0538 | 2.9385 | -6.2615 | -17.9207 | 10.6656 | 10.2758 | 9.8136 | 9.0636 | 8.137 | 7.1646 | 6.2962 | 5.8513 | 4.9819 | -0.58032 | -7.815 | -14.7303
COWLEY GSP | DRAYTON BSP | WANTAGE PRIMARY | MINIMUM HEADROOM | SU 41290 88304 | NO | YES | 3.658 | 9.1666 | 8.4472 | 7.735 | 6.9758 | 6.6421 | 5.8381 | 4.9564 | 4.0809 | 3.4075 | -0.19867 | -2.3619 | -3.6364 | 10.9736 | 10.543 | 10.0807 | 9.5746 | 9.444 | 8.946 | 8.3879 | 7.8236 | 7.394 | 5.1389 | 3.2542 | -1.7948 | 9.0558 | 8.4303 | 7.7905 | 7.0977 | 6.8334 | 6.1068 | 5.3028 | 4.5048 | 3.9058 | 0.91807 | -0.90234 | -1.9003
|  | WANTAGE PRIMARY | EE |  |  |  |  | 9.1666 | 8.4472 | 7.735 | 6.9758 | 6.6421 | 5.8381 | 4.9564 | 4.0809 | 3.4075 | -0.022139 | -1.915 | -3.3742 | 10.9736 | 10.543 | 10.0807 | 9.5746 | 9.444 | 8.946 | 8.3879 | 7.8236 | 7.394 | 5.1389 | 3.3124 | 0.62256 | 9.0558 | 8.4303 | 7.7905 | 7.0977 | 6.8334 | 6.1068 | 5.3028 | 4.5048 | 3.9058 | 1.0242 | -0.485 | -1.6728
|  | WANTAGE PRIMARY | HT |  |  |  |  | 9.386 | 8.733 | 8.0748 | 7.5075 | 6.835 | 6.0401 | 5.5085 | 4.7064 | 3.8575 | -0.19867 | -2.3619 | -3.6364 | 11.2032 | 10.8603 | 10.4838 | 10.1828 | 9.8175 | 9.3889 | 9.1981 | 8.7624 | 8.2726 | 6.1889 | 5.2185 | 4.6981 | 9.2732 | 8.7201 | 8.1354 | 7.6334 | 7.0334 | 6.3211 | 5.9477 | 5.2293 | 4.4456 | 0.91807 | -0.90234 | -1.9003
|  | WANTAGE PRIMARY | HE |  |  |  |  | 9.4054 | 8.7748 | 8.1758 | 7.634 | 6.9513 | 6.2564 | 5.8462 | 5.1615 | 4.4483 | 0.83092 | -1.0752 | -2.014 | 11.1583 | 10.793 | 10.4317 | 10.1062 | 9.6787 | 9.2501 | 9.0481 | 8.6021 | 8.1348 | 5.6124 | 3.7328 | 1.2572 | 9.2926 | 8.7568 | 8.2283 | 7.7507 | 7.1385 | 6.516 | 6.2354 | 5.6099 | 4.9691 | 1.8099 | 0.29868 | -0.44724
|  | WANTAGE PRIMARY | CF |  |  |  |  | 9.6136 | 9.1085 | 8.6503 | 8.1717 | 7.7391 | 7.3258 | 6.8585 | 6.3707 | 6.2932 | 3.6197 | 1.6585 | -0.26398 | 11.2552 | 10.9419 | 10.644 | 10.3113 | 10.0164 | 9.6909 | 9.3124 | 8.9154 | 8.793 | 6.3164 | 3.2542 | -1.7948 | 9.4854 | 9.0609 | 8.665 | 8.2375 | 7.863 | 7.4956 | 7.0762 | 6.6354 | 6.6058 | 4.1885 | 2.4568 | 0.86909
MANNINGTON GSP | WAREHAM BSP | WAREHAM TOWN PRIMARY | MINIMUM HEADROOM | SY 92036 87463 | NO | YES | 1.517 | -0.57168 | 26.2092 | 25.8745 | 25.3776 | 25.2612 | 24.9122 | 24.4867 | 24.0592 | 23.699 | 20.9378 | 19.2082 | 18.1786 | 1.289 | 26.4143 | 26.1408 | 25.7888 | 25.7531 | 25.6327 | 25.4898 | 25.3102 | 25.1847 | 23.7827 | 22.8459 | 21.7796 | -0.1449 | 25.7592 | 25.3337 | 24.6704 | 24.5786 | 24.1418 | 23.6622 | 23.1776 | 22.8224 | 20.3704 | 18.7816 | 17.8969
|  | WAREHAM TOWN PRIMARY | EE |  |  |  |  | -0.57168 | 26.2092 | 25.8745 | 25.3776 | 25.2612 | 24.9122 | 24.4867 | 24.0592 | 23.699 | 21.1469 | 19.4959 | 18.3224 | 1.289 | 26.4143 | 26.1408 | 25.7888 | 25.7531 | 25.6327 | 25.4898 | 25.3102 | 25.1847 | 23.7827 | 22.8459 | 21.8306 | -0.1449 | 25.7592 | 25.3337 | 24.6704 | 24.5786 | 24.1418 | 23.6622 | 23.1776 | 22.8224 | 20.5143 | 19.0857 | 18.0388
|  | WAREHAM TOWN PRIMARY | HT |  |  |  |  | -0.48393 | 26.3296 | 26.0286 | 25.7633 | 25.4867 | 25.0561 | 24.6051 | 24.3316 | 23.7643 | 20.9378 | 19.2082 | 18.1786 | 1.3513 | 26.5 | 26.2531 | 26.1306 | 26.0347 | 25.9276 | 25.7939 | 25.7724 | 25.4367 | 23.9949 | 23.2622 | 22.8337 | -0.07449 | 25.9163 | 25.5541 | 25.1541 | 24.8153 | 24.3673 | 23.8827 | 23.7122 | 23.1408 | 20.3704 | 18.7816 | 17.8969
|  | WAREHAM TOWN PRIMARY | HE |  |  |  |  | -0.47985 | 26.3378 | 26.0408 | 25.5918 | 25.3888 | 25.0694 | 24.7133 | 24.5306 | 24.1888 | 21.7214 | 20.0786 | 19.2561 | 1.3482 | 26.4959 | 26.2439 | 25.9327 | 25.8347 | 25.7347 | 25.5969 | 25.5827 | 25.4398 | 24.0602 | 23.1102 | 22.2357 | -0.069388 | 25.9255 | 25.6163 | 25.0724 | 24.7582 | 24.4 | 24.0031 | 23.9204 | 23.5592 | 21.2235 | 19.8367 | 19.1796
|  | WAREHAM TOWN PRIMARY | CF |  |  |  |  | -0.36658 | 26.4939 | 26.3224 | 25.8847 | 25.6061 | 25.5122 | 25.3898 | 25.2582 | 25.1194 | 24.2561 | 22.5112 | 20.9888 | 1.3901 | 26.5469 | 26.3949 | 26.0327 | 25.7929 | 25.7367 | 25.6633 | 25.5847 | 25.4786 | 24.9735 | 23.6653 | 21.7796 | -0.0010204 | 26.0153 | 25.8643 | 25.4531 | 25.1429 | 24.9929 | 24.8143 | 24.6214 | 24.4224 | 23.4582 | 21.8153 | 20.4633
FLEET-BRAMLEY GSP | BRACKNELL BSP | WARFIELD PRIMARY | MINIMUM HEADROOM | SU 86960 71382 | NO | NO | 3.959 | 7.7184 | 6.6847 | 5.9092 | 4.7786 | 3.4204 | 2 | 0.25612 | -1.4878 | -2.5429 | -7.2316 | -11.1765 | -13.2092 | 11.3245 | 10.6327 | 10.2337 | 9.5112 | 8.6571 | 7.7541 | 6.649 | 5.5347 | 4.8531 | 1.6184 | -2.2031 | -11.4765 | 6.2561 | 5.3204 | 4.7173 | 3.7061 | 2.5061 | 1.2316 | -0.33163 | -1.8929 | -2.8153 | -6.9337 | -10.3704 | -12.1112
|  | WARFIELD PRIMARY | EE |  |  |  |  | 7.7184 | 6.6847 | 5.9092 | 4.7786 | 3.4204 | 2 | 0.25612 | -1.4878 | -2.5429 | -7.1347 | -10.5071 | -12.951 | 11.3245 | 10.6327 | 10.2337 | 9.5112 | 8.6571 | 7.7541 | 6.649 | 5.5347 | 4.8531 | 1.6184 | -1.649 | -6.4398 | 6.2561 | 5.3204 | 4.7173 | 3.7061 | 2.5061 | 1.2316 | -0.33163 | -1.8929 | -2.8153 | -6.9082 | -9.7857 | -11.9031
|  | WARFIELD PRIMARY | HT |  |  |  |  | 8.1122 | 7.2571 | 6.2612 | 5.1745 | 4.2735 | 3 | 1.448 | -0.15816 | -1.4235 | -7.2316 | -11.1765 | -13.2092 | 11.7745 | 11.3092 | 10.7653 | 10.1582 | 9.802 | 9.1398 | 8.3255 | 7.4673 | 6.749 | 3.6214 | 1.849 | 1.0357 | 6.6837 | 5.949 | 5.0816 | 4.1306 | 3.4133 | 2.2857 | 0.92653 | -0.48571 | -1.6327 | -6.9337 | -10.3704 | -12.1112
|  | WARFIELD PRIMARY | HE |  |  |  |  | 8.2041 | 7.3755 | 6.3755 | 5.2337 | 4.3214 | 3.1755 | 1.7398 | 0.24592 | -0.90816 | -6.1949 | -9.9418 | -11.5306 | 11.7051 | 11.1867 | 10.5724 | 9.8755 | 9.4316 | 8.7214 | 7.8347 | 6.8929 | 6.0745 | 1.9663 | -1.6806 | -6.1184 | 6.7439 | 6.0316 | 5.1612 | 4.1673 | 3.4388 | 2.4235 | 1.1612 | -0.15408 | -1.2122 | -6.0755 | -9.3418 | -10.6969
|  | WARFIELD PRIMARY | CF |  |  |  |  | 8.6133 | 7.9724 | 7.2684 | 6.4327 | 5.5235 | 5.1796 | 4.2939 | 3.3673 | 2.7531 | -0.8898 | -4.8837 | -8.4347 | 11.9041 | 11.451 | 10.9816 | 10.4245 | 9.799 | 9.5439 | 8.851 | 8.1204 | 7.502 | 3.5071 | -2.2031 | -11.4765 | 7.1122 | 6.5531 | 5.9582 | 5.2367 | 4.448 | 4.2286 | 3.4612 | 2.6541 | 2.0786 | -1.352 | -4.8908 | -8.0439
MELKSHAM GSP | FROME BSP | WARMINSTER PRIMARY | MINIMUM HEADROOM | ST 84936 44551 | NO | NO | 6.159 | 1.4372 | 0.92287 | 0.4045 | -0.41387 | -1.1516 | -1.9516 | -2.5047 | -3.2547 | -3.8812 | -5.672 | -7.0557 | -7.8496 | 2.3514 | 2.0331 | 1.7076 | 1.1708 | 0.73205 | 0.22695 | 0.010624 | -0.46795 | -0.8006 | -2.1026 | -3.6465 | -7.4149 | 1.3055 | 0.84838 | 0.39124 | -0.33019 | -0.97917 | -1.6955 | -2.071 | -2.7394 | -3.2139 | -4.7986 | -6.023 | -6.7088
|  | WARMINSTER PRIMARY | EE |  |  |  |  | 1.4372 | 0.92287 | 0.4045 | -0.41387 | -1.1516 | -1.9516 | -2.5047 | -3.2547 | -3.82 | -5.5843 | -6.7986 | -7.7057 | 2.3514 | 2.0331 | 1.7076 | 1.1708 | 0.73205 | 0.22695 | 0.010624 | -0.46795 | -0.8006 | -2.1026 | -3.4537 | -5.4465 | 1.3055 | 0.84838 | 0.39124 | -0.33019 | -0.97917 | -1.6955 | -2.071 | -2.7394 | -3.2067 | -4.7343 | -5.7894 | -6.5853
|  | WARMINSTER PRIMARY | HT |  |  |  |  | 1.5443 | 1.0708 | 0.59124 | -0.13631 | -0.91897 | -1.6975 | -2.5026 | -3.2108 | -3.8812 | -5.672 | -7.0557 | -7.8496 | 2.4841 | 2.2382 | 1.9739 | 1.5688 | 1.1484 | 0.73818 | 0.29736 | -0.10264 | -0.47101 | -1.3037 | -1.9475 | -2.2924 | 1.4229 | 1.0443 | 0.63818 | 0.016747 | -0.65264 | -1.3118 | -2.0057 | -2.6302 | -3.2139 | -4.7986 | -6.023 | -6.7088
|  | WARMINSTER PRIMARY | HE |  |  |  |  | 1.5535 | 1.0943 | 0.62083 | -0.13427 | -0.81284 | -1.4618 | -2.2496 | -2.9322 | -3.5486 | -5.0822 | -6.2996 | -6.872 | 2.4535 | 2.1923 | 1.9106 | 1.4198 | 1.0423 | 0.66267 | 0.1994 | -0.22713 | -0.62611 | -1.8394 | -3.2292 | -5.0812 | 1.4321 | 1.0627 | 0.66573 | 0.0075633 | -0.56999 | -1.1179 | -1.7884 | -2.3782 | -2.9169 | -4.271 | -5.3496 | -5.8516
|  | WARMINSTER PRIMARY | CF |  |  |  |  | 1.6923 | 1.3239 | 0.92287 | 0.38409 | -0.067947 | -0.43631 | -0.82917 | -1.3169 | -1.8108 | -3.1996 | -4.5077 | -5.7659 | 2.5157 | 2.2902 | 2.0218 | 1.6412 | 1.3402 | 1.0586 | 0.76267 | 0.40654 | 0.037155 | -1.419 | -3.6465 | -7.4149 | 1.5606 | 1.2698 | 0.93205 | 0.46879 | 0.083073 | -0.22917 | -0.5557 | -0.97407 | -1.4057 | -2.6169 | -3.771 | -4.8771
LOVEDEAN GSP | FORT WIDLEY BSP | WATERLOOVILLE PRIMARY | MINIMUM HEADROOM | SU 67988 09282 | NO | YES | 14.326 | 22.2935 | 21.3853 | 20.1088 | 18.8986 | 17.5884 | 15.872 | 14.0108 | 12.1833 | 10.7588 | 3.3577 | -1.9412 | -4.1974 | 25.7747 | 25.189 | 24.3441 | 23.5124 | 22.5563 | 21.3869 | 20.0716 | 18.7471 | 17.7757 | 12.4063 | 5.1931 | -10.8967 | 21.982 | 21.232 | 20.1137 | 19.0371 | 17.8657 | 16.3239 | 14.6382 | 12.9739 | 11.7086 | 5.3035 | 0.7004 | -1.1425
|  | WATERLOOVILLE PRIMARY | EE |  |  |  |  | 22.2935 | 21.3853 | 20.1088 | 18.8986 | 17.5884 | 15.872 | 14.0108 | 12.1833 | 10.7588 | 3.7567 | -0.97389 | -3.2147 | 25.7747 | 25.189 | 24.3441 | 23.5124 | 22.5563 | 21.3869 | 20.0716 | 18.7471 | 17.7757 | 12.4063 | 6.8165 | -1.1539 | 21.982 | 21.232 | 20.1137 | 19.0371 | 17.8657 | 16.3239 | 14.6382 | 12.9739 | 11.7086 | 5.5433 | 1.5137 | -0.36287
|  | WATERLOOVILLE PRIMARY | HT |  |  |  |  | 22.6373 | 21.4996 | 20.2965 | 19.5261 | 18.3731 | 16.8149 | 15.168 | 13.4802 | 11.7343 | 3.3577 | -1.9412 | -4.1974 | 26.2349 | 25.5737 | 24.8828 | 24.542 | 23.9216 | 23.142 | 22.2992 | 21.388 | 20.3716 | 15.8053 | 13.3339 | 12.29 | 22.3851 | 21.3902 | 20.332 | 19.7116 | 18.6953 | 17.3239 | 15.8575 | 14.3524 | 12.7861 | 5.3035 | 0.7004 | -1.1425
|  | WATERLOOVILLE PRIMARY | HE |  |  |  |  | 22.769 | 21.6761 | 20.5016 | 19.7833 | 18.6945 | 17.3537 | 15.9169 | 14.4588 | 12.9996 | 5.8067 | 0.99244 | -0.90348 | 26.1308 | 25.388 | 24.6063 | 24.1614 | 23.4328 | 22.5767 | 21.6288 | 20.6073 | 19.541 | 13.4349 | 7.6124 | -0.17225 | 22.4841 | 21.5269 | 20.4994 | 19.9239 | 18.9586 | 17.7728 | 16.4912 | 15.179 | 13.8606 | 7.4004 | 3.2749 | 1.732
|  | WATERLOOVILLE PRIMARY | CF |  |  |  |  | 23.3659 | 22.6608 | 21.8486 | 21.4302 | 20.7057 | 20.0455 | 19.2935 | 18.4914 | 17.7006 | 12.7924 | 7.0302 | 2.1026 | 26.389 | 25.8186 | 25.1788 | 24.8175 | 24.19 | 23.5298 | 22.7543 | 21.9114 | 21.0277 | 14.9696 | 5.1931 | -10.8967 | 22.9994 | 22.3943 | 21.6963 | 21.3708 | 20.7473 | 20.178 | 19.5218 | 18.8106 | 18.1075 | 13.6698 | 8.5484 | 4.2392
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON PRIMARY | MINIMUM HEADROOM | SU 69106 94287 | NO | NO | 1.614 | -10.9255 | -11.0928 | -11.3235 | -11.5704 | -12.3622 | -12.8286 | -13.3969 | -14.9286 | -16.0663 | -18.5877 | -21.3418 | -24.5061 | -11.8837 | -12.0041 | -12.3357 | -12.5643 | -13.4684 | -13.95 | -14.5112 | -16.2857 | -17.5684 | -20.2969 | -23.8745 | -28.7449 | -12.2663 | -12.4153 | -12.7408 | -12.9939 | -13.9255 | -14.4551 | -15.0714 | -16.8837 | -18.202 | -21.0612 | -24.2908 | -28.1347
|  | WATLINGTON PRIMARY | EE |  |  |  |  | -10.9255 | -11.0928 | -11.3153 | -11.4959 | -11.9153 | -12.4275 | -12.4173 | -13.0235 | -13.3765 | -15.4418 | -19.2326 | -20.748 | -11.8837 | -12.0041 | -12.1724 | -12.3255 | -12.751 | -13.2275 | -13.1653 | -13.752 | -14.0837 | -16.1806 | -21.0306 | -23.7428 | -12.2663 | -12.4153 | -12.6153 | -12.7877 | -13.2286 | -13.7786 | -13.7775 | -14.4275 | -14.8031 | -17.0459 | -21.5633 | -23.3082
|  | WATLINGTON PRIMARY | HT |  |  |  |  | -10.7663 | -10.9704 | -11.2153 | -11.3837 | -12.0459 | -12.5388 | -13.1551 | -13.5377 | -14.2459 | -16.5357 | -20.2449 | -22.8704 | -11.748 | -11.9092 | -12.1306 | -12.2337 | -12.95 | -13.4204 | -14.0071 | -14.298 | -14.9888 | -17.0571 | -21.1214 | -24.0408 | -12.1316 | -12.3337 | -12.599 | -12.7551 | -13.5224 | -14.0765 | -14.7428 | -15.1112 | -15.8826 | -18.4469 | -22.8173 | -25.9184
|  | WATLINGTON PRIMARY | HE |  |  |  |  | -10.7643 | -10.9928 | -11.3235 | -11.5704 | -12.3622 | -12.8286 | -13.3969 | -14.9286 | -16.0663 | -18.5877 | -21.3418 | -24.5061 | -11.7745 | -11.9826 | -12.3357 | -12.5643 | -13.4684 | -13.95 | -14.5112 | -16.2857 | -17.5684 | -20.2969 | -23.8745 | -28.7449 | -12.1306 | -12.3633 | -12.7408 | -12.9939 | -13.9255 | -14.4551 | -15.0714 | -16.8837 | -18.202 | -21.0612 | -24.2908 | -28.1347
|  | WATLINGTON PRIMARY | CF |  |  |  |  | -10.7184 | -10.8071 | -10.9255 | -11.0765 | -11.2837 | -11.5357 | -11.7796 | -11.9816 | -12.2775 | -13.7173 | -15.6541 | -17.4714 | -11.751 | -11.8275 | -11.9245 | -12.0826 | -12.299 | -12.5714 | -12.8286 | -13.0633 | -13.3898 | -15.2775 | -18.2704 | -22.2755 | -12.0806 | -12.1602 | -12.2673 | -12.4286 | -12.6428 | -12.9071 | -13.1561 | -13.3735 | -13.6826 | -15.298 | -17.4755 | -19.5286
AMERSHAM GSP | LOUDWATER BSP | WELL END PRIMARY | MINIMUM HEADROOM | SU 88511 87957 | NO | YES | 2.646 | 7.1623 | 6.5031 | 5.7898 | 5.4133 | 4.7592 | 3.9562 | 3.0592 | 2.2143 | 1.6439 | -1.2142 | -3.4448 | -4.4275 | 11.9817 | 11.5511 | 11.0633 | 10.8919 | 10.4358 | 9.897 | 9.2796 | 8.6654 | 8.2684 | 6.1439 | 3.4041 | -3.0204 | 8.7184 | 8.1327 | 7.4756 | 7.2092 | 6.6052 | 5.8654 | 5.0286 | 4.2358 | 3.7266 | 1.2827 | -0.76219 | -1.6602
|  | WELL END PRIMARY | EE |  |  |  |  | 7.1623 | 6.5031 | 5.7898 | 5.4133 | 4.7592 | 3.9562 | 3.0592 | 2.2143 | 1.6439 | -1.2142 | -3.0826 | -4.0653 | 11.9817 | 11.5511 | 11.0633 | 10.8919 | 10.4358 | 9.897 | 9.2796 | 8.6654 | 8.2684 | 6.1439 | 3.9552 | 0.81128 | 8.7184 | 8.1327 | 7.4756 | 7.2092 | 6.6052 | 5.8654 | 5.0286 | 4.2358 | 3.7266 | 1.2827 | -0.44791 | -1.3336
|  | WELL END PRIMARY | HT |  |  |  |  | 7.4358 | 6.8245 | 6.2521 | 5.6388 | 5.0266 | 4.2531 | 3.8092 | 3.0623 | 2.3572 | -1.1928 | -3.4448 | -4.4275 | 12.298 | 11.9541 | 11.6419 | 11.2919 | 10.9286 | 10.4827 | 10.3603 | 9.9276 | 9.5031 | 7.5327 | 6.4725 | 6.0398 | 8.996 | 8.4786 | 7.9868 | 7.445 | 6.8847 | 6.1766 | 5.8307 | 5.1664 | 4.5327 | 1.3143 | -0.76219 | -1.6602
|  | WELL END PRIMARY | HE |  |  |  |  | 7.445 | 6.848 | 6.2888 | 5.6939 | 5.0939 | 4.395 | 4.0286 | 3.3603 | 2.7286 | -0.4428 | -2.4061 | -3.1418 | 12.2307 | 11.8501 | 11.499 | 11.1123 | 10.698 | 10.2266 | 10.0654 | 9.5817 | 9.098 | 6.4919 | 4.1613 | 1.1327 | 9.0041 | 8.498 | 8.0184 | 7.4898 | 6.9368 | 6.296 | 6.0245 | 5.4286 | 4.8398 | 1.9633 | 0.13577 | -0.53566
|  | WELL END PRIMARY | CF |  |  |  |  | 7.8062 | 7.4378 | 7.0592 | 6.6164 | 6.0929 | 5.646 | 5.2001 | 5.1674 | 4.8633 | 2.698 | 0.32556 | -1.8397 | 12.3888 | 12.1215 | 11.8337 | 11.5235 | 11.1398 | 10.748 | 10.3245 | 10.2501 | 9.8817 | 7.2694 | 3.4041 | -3.0204 | 9.3174 | 9.0103 | 8.6684 | 8.2909 | 7.8307 | 7.4256 | 7.0031 | 7.0358 | 6.7368 | 4.6694 | 2.5817 | 0.7072
WILLESDEN GSP |  | WESLEY AVENUE PRIMARY | MINIMUM HEADROOM | TQ 20927 83082 | NO | YES | 18.765 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388
|  | WESLEY AVENUE PRIMARY | EE |  |  |  |  | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388
|  | WESLEY AVENUE PRIMARY | HT |  |  |  |  | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388
|  | WESLEY AVENUE PRIMARY | HE |  |  |  |  | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388
|  | WESLEY AVENUE PRIMARY | CF |  |  |  |  | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 61.788 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 58.188 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388 | 59.388
LOVEDEAN GSP | FAREHAM (MAIN) BSP | WEST END PRIMARY | MINIMUM HEADROOM | SU 57216 06147 | NO | YES | 7.399 | 12.2693 | 11.8387 | 11.3642 | 11.2377 | 10.7724 | 9.7163 | 8.5122 | 7.2163 | 6.301 | 2.0612 | -1.1531 | -3.0082 | 12.3347 | 11.9255 | 11.4693 | 11.3704 | 10.9112 | 10.1908 | 9.3398 | 8.4285 | 7.8091 | 4.753 | 0.72343 | -8.9307 | 11.5877 | 11.0959 | 10.5459 | 10.5469 | 10.0347 | 9.0765 | 7.9581 | 6.7724 | 6.0336 | 2.6969 | -0.041878 | -1.6102
|  | WEST END PRIMARY | EE |  |  |  |  | 12.2693 | 11.8387 | 11.3642 | 11.2377 | 10.7724 | 9.7163 | 8.5122 | 7.2163 | 6.301 | 2.2938 | -0.53371 | -2.7409 | 12.3347 | 11.9255 | 11.4693 | 11.3704 | 10.9112 | 10.1908 | 9.3398 | 8.4285 | 7.8091 | 4.753 | 1.5296 | -3.5041 | 11.5877 | 11.0959 | 10.5459 | 10.5469 | 10.0347 | 9.0765 | 7.9581 | 6.7724 | 6.0336 | 2.7928 | 0.48159 | -1.4113
|  | WEST END PRIMARY | HT |  |  |  |  | 12.5112 | 12.1632 | 11.8377 | 11.4459 | 11.0142 | 10.151 | 8.9602 | 7.8796 | 6.8673 | 2.0612 | -1.1531 | -3.0082 | 12.6877 | 12.4255 | 12.2 | 11.8969 | 11.5571 | 11.3 | 10.6591 | 10.0551 | 9.4632 | 6.8591 | 5.4204 | 4.6765 | 11.9428 | 11.5826 | 11.253 | 10.8377 | 10.3744 | 9.8714 | 8.8571 | 7.9102 | 6.9989 | 2.6969 | -0.041878 | -1.6102
|  | WEST END PRIMARY | HE |  |  |  |  | 12.5377 | 12.2102 | 11.9102 | 11.5469 | 11.1489 | 10.5765 | 9.5938 | 8.5244 | 7.6183 | 3.5632 | 0.73873 | -0.61024 | 12.6153 | 12.3163 | 12.0387 | 11.6898 | 11.2979 | 11.0296 | 10.3724 | 9.6428 | 8.9653 | 5.4928 | 2.1979 | -2.5256 | 11.9571 | 11.6153 | 11.3091 | 10.9214 | 10.4877 | 10.204 | 9.3602 | 8.4398 | 7.6265 | 4.0234 | 1.6816 | 0.502
|  | WEST END PRIMARY | CF |  |  |  |  | 12.7908 | 12.6306 | 12.4683 | 12.2632 | 12.0377 | 11.7796 | 11.7367 | 11.3632 | 10.9489 | 7.3377 | 4.6326 | 2.0867 | 12.7153 | 12.5061 | 12.2857 | 12.004 | 11.6714 | 11.2816 | 11.1204 | 10.6428 | 10.1153 | 6.1061 | 0.72343 | -8.9307 | 12.152 | 11.9683 | 11.7836 | 11.5367 | 11.2653 | 10.9612 | 11.0489 | 10.6693 | 10.252 | 7.0081 | 4.8387 | 2.7336
MELKSHAM GSP | WEST GRAFTON BSP | WEST GRAFTON VILLAGE PRIMARY | MINIMUM HEADROOM | SU 24639 60279 | NO | NO | 1.493 | 3.458 | 3.3039 | 3.0988 | 2.9284 | 2.7008 | 2.4131 | 2.0671 | 1.7192 | 2.1416 | 1.2651 | 0.96204 | 0.65898 | 5.0059 | 4.8937 | 4.7488 | 4.6314 | 4.4631 | 4.259 | 4.009 | 3.758 | 4.0039 | 3.2671 | 2.3784 | 0.29367 | 3.8794 | 3.7294 | 3.5284 | 3.3631 | 3.1365 | 2.8559 | 2.5161 | 2.1743 | 2.6927 | 1.9345 | 1.6773 | 1.4335
|  | WEST GRAFTON VILLAGE PRIMARY | EE |  |  |  |  | 3.458 | 3.3039 | 3.0988 | 2.9284 | 2.7008 | 2.4131 | 2.0671 | 1.7192 | 2.1416 | 1.2651 | 0.96204 | 0.79571 | 5.0059 | 4.8937 | 4.7488 | 4.6314 | 4.4631 | 4.259 | 4.009 | 3.758 | 4.0039 | 3.3386 | 2.7212 | 1.7355 | 3.8794 | 3.7294 | 3.5284 | 3.3631 | 3.1365 | 2.8559 | 2.5161 | 2.1743 | 2.6927 | 1.9345 | 1.6773 | 1.5478
|  | WEST GRAFTON VILLAGE PRIMARY | HT |  |  |  |  | 3.5804 | 3.4702 | 3.3324 | 3.2212 | 3.0733 | 2.8733 | 2.6886 | 2.4641 | 2.1886 | 1.4396 | 0.97837 | 0.65898 | 5.1161 | 5.0498 | 4.9529 | 4.8845 | 4.7753 | 4.6386 | 4.5335 | 4.3722 | 4.1947 | 3.8529 | 3.6039 | 3.4467 | 4.0365 | 3.9406 | 3.809 | 3.709 | 3.5549 | 3.361 | 3.2029 | 2.9702 | 2.7202 | 2.0957 | 1.6957 | 1.4335
|  | WEST GRAFTON VILLAGE PRIMARY | HE |  |  |  |  | 3.5794 | 3.4712 | 3.3365 | 3.2304 | 3.0886 | 2.8957 | 2.7182 | 2.5029 | 2.2406 | 1.3937 | 1.0835 | 0.93755 | 5.0988 | 5.0202 | 4.9192 | 4.8416 | 4.7243 | 4.5835 | 4.4529 | 4.2784 | 4.0855 | 3.4467 | 2.81 | 1.8457 | 4.0355 | 3.9416 | 3.809 | 3.7141 | 3.5631 | 3.3763 | 3.2151 | 2.9855 | 2.7386 | 2.062 | 1.7988 | 1.6865
|  | WEST GRAFTON VILLAGE PRIMARY | CF |  |  |  |  | 3.6222 | 3.5324 | 3.4294 | 3.3141 | 3.2233 | 3.0937 | 2.9467 | 2.7804 | 2.6682 | 1.7039 | 1.5549 | 1.0692 | 5.1294 | 5.0569 | 4.9763 | 4.8794 | 4.7998 | 4.6784 | 4.5416 | 4.3916 | 4.2743 | 3.2671 | 2.3784 | 0.29367 | 4.0937 | 4.0131 | 3.9171 | 3.808 | 3.7263 | 3.608 | 3.4733 | 3.3161 | 3.2049 | 2.2804 | 2.2039 | 1.7865
AXMINSTER GSP | YEOVIL BSP | WEST HENDFORD PRIMARY | MINIMUM HEADROOM | ST 55000 15442 | NO | NO | 12.9 | 30.2098 | 29.7823 | 29.319 | 28.7547 | 28.118 | 27.5272 | 26.7159 | 25.9292 | 25.2445 | 22.4425 | 20.8782 | 20.0996 | 29.6241 | 29.3567 | 29.0772 | 28.7333 | 28.3486 | 27.9731 | 27.4078 | 26.8312 | 26.3282 | 24.2761 | 22.1578 | 16.2802 | 27.6914 | 27.3394 | 26.9669 | 26.5078 | 25.9914 | 25.4935 | 24.7343 | 23.9965 | 23.3598 | 20.7016 | 19.2731 | 18.7016
|  | WEST HENDFORD PRIMARY | EE |  |  |  |  | 30.2098 | 29.7823 | 29.319 | 28.7547 | 28.118 | 27.5272 | 26.7159 | 25.9292 | 25.2445 | 23.0404 | 21.5782 | 20.4537 | 29.6241 | 29.3567 | 29.0772 | 28.7333 | 28.3486 | 27.9731 | 27.4078 | 26.8312 | 26.3282 | 24.722 | 22.7761 | 19.7802 | 27.6914 | 27.3394 | 26.9669 | 26.5078 | 25.9914 | 25.4935 | 24.7343 | 23.9965 | 23.3598 | 21.4282 | 20.5006 | 19.5251
|  | WEST HENDFORD PRIMARY | HT |  |  |  |  | 30.5159 | 30.1833 | 29.8353 | 29.3955 | 28.8874 | 28.2874 | 27.4731 | 26.6312 | 26.0976 | 23.1669 | 21.2884 | 20.2782 | 29.8455 | 29.6506 | 29.4516 | 29.1996 | 28.92 | 28.5955 | 28.1527 | 27.6312 | 27.2159 | 25.1731 | 24.219 | 23.7486 | 27.9567 | 27.6843 | 27.4067 | 27.0567 | 26.6598 | 26.2006 | 25.62 | 24.9608 | 24.4149 | 21.8057 | 20.2598 | 19.3904
|  | WEST HENDFORD PRIMARY | HE |  |  |  |  | 30.4486 | 30.0833 | 29.6996 | 29.2149 | 28.6516 | 28.0118 | 27.2476 | 26.4465 | 25.7363 | 22.4425 | 20.8782 | 20.0996 | 29.7904 | 29.571 | 29.3435 | 29.0516 | 28.7272 | 28.3455 | 27.82 | 27.2374 | 26.7323 | 24.2761 | 22.8241 | 20.0027 | 27.8986 | 27.6016 | 27.2935 | 26.9006 | 26.4588 | 25.9465 | 25.2425 | 24.4904 | 23.8323 | 20.7016 | 19.2731 | 18.7016
|  | WEST HENDFORD PRIMARY | CF |  |  |  |  | 30.8272 | 30.6333 | 30.4374 | 30.1669 | 29.822 | 29.4312 | 28.9394 | 28.4067 | 27.8435 | 25.3761 | 23.0802 | 21.3455 | 30.0118 | 29.8863 | 29.7578 | 29.5863 | 29.3731 | 29.1374 | 28.8078 | 28.3374 | 27.8374 | 25.6731 | 22.1578 | 16.2802 | 28.2037 | 28.0404 | 27.8782 | 27.6537 | 27.37 | 27.0557 | 26.6486 | 26.2118 | 25.7486 | 23.4618 | 21.2833 | 19.6598
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR PRIMARY | MINIMUM HEADROOM | ST 77699 22040 | NO | NO | 0.574 | 4.4786 | 4.3296 | 4.1347 | 3.8214 | 3.5204 | 3.2541 | 2.9439 | 3.0337 | 2.8765 | 2.0316 | 1.6643 | 1.3602 | 5.9041 | 5.8 | 5.6582 | 5.4663 | 5.2673 | 5.0653 | 4.8235 | 4.948 | 4.8429 | 4.2418 | 3.5939 | 1.9663 | 4.5918 | 4.4449 | 4.249 | 3.9592 | 3.6704 | 3.401 | 3.0837 | 3.2541 | 3.0939 | 2.3969 | 2.0816 | 1.8224
|  | WEST STOUR PRIMARY | EE |  |  |  |  | 4.4786 | 4.3296 | 4.1347 | 3.8214 | 3.5204 | 3.2541 | 2.9439 | 3.0337 | 2.8765 | 2.0316 | 1.6643 | 1.4673 | 5.9041 | 5.8 | 5.6582 | 5.4663 | 5.2673 | 5.0653 | 4.8235 | 4.948 | 4.8429 | 4.2816 | 3.7765 | 3.0051 | 4.5918 | 4.4449 | 4.249 | 3.9592 | 3.6704 | 3.401 | 3.0837 | 3.2541 | 3.1153 | 2.3969 | 2.0816 | 1.9143
|  | WEST STOUR PRIMARY | HT |  |  |  |  | 4.6071 | 4.4714 | 4.3235 | 4.0388 | 3.7724 | 3.5622 | 3.3684 | 3.1255 | 2.8776 | 2.1612 | 1.6806 | 1.3602 | 6.0204 | 5.9337 | 5.8408 | 5.6918 | 5.5449 | 5.4143 | 5.301 | 5.1449 | 4.9786 | 4.6673 | 4.4398 | 4.2939 | 4.7316 | 4.6 | 4.4531 | 4.2092 | 3.9704 | 3.7643 | 3.5847 | 3.3459 | 3.0939 | 2.5061 | 2.0929 | 1.8224
|  | WEST STOUR PRIMARY | HE |  |  |  |  | 4.6082 | 4.4765 | 4.3296 | 4.051 | 3.7939 | 3.5959 | 3.4153 | 3.1878 | 2.9551 | 2.1571 | 1.7765 | 1.6194 | 6.0041 | 5.9133 | 5.8082 | 5.6541 | 5.4969 | 5.3582 | 5.2337 | 5.0653 | 4.8857 | 4.3582 | 3.8418 | 3.0939 | 4.7316 | 4.6051 | 4.4602 | 4.2224 | 3.9908 | 3.7949 | 3.6276 | 3.399 | 3.1602 | 2.5143 | 2.202 | 2.0735
|  | WEST STOUR PRIMARY | CF |  |  |  |  | 4.6418 | 4.552 | 4.4418 | 4.1806 | 3.9969 | 3.8796 | 3.7378 | 3.6255 | 3.4765 | 2.6051 | 2.3653 | 1.8367 | 6.0194 | 5.9561 | 5.8724 | 5.7092 | 5.599 | 5.4959 | 5.3633 | 5.2653 | 5.1286 | 4.2418 | 3.5939 | 1.9663 | 4.7602 | 4.6724 | 4.5684 | 4.3327 | 4.1796 | 4.0582 | 3.9092 | 3.8031 | 3.6459 | 2.75 | 2.6837 | 2.2347
MANNINGTON GSP | BOURNEMOUTH BSP | WESTBOURNE PRIMARY | MINIMUM HEADROOM | SZ 07642 91485 | NO | YES | 1.942 | 12.9296 | 12.2061 | 11.451 | 10.5694 | 9.6 | 8.5082 | 7.2204 | 6.0561 | 5.1071 | 1.6469 | -1.1031 | -1.6235 | 16.648 | 16.0541 | 15.4224 | 14.6765 | 13.848 | 12.9653 | 11.902 | 10.8704 | 9.9918 | 5.6929 | -0.85714 | -16.4888 | 13.2418 | 12.5643 | 11.8418 | 10.9969 | 10.0735 | 9.049 | 7.8276 | 6.7071 | 5.802 | 2.5694 | 0.12347 | -0.2949
|  | WESTBOURNE PRIMARY | EE |  |  |  |  | 12.9296 | 12.2061 | 11.451 | 10.5694 | 9.6 | 8.5082 | 7.2204 | 6.0561 | 5.1071 | 1.6469 | -0.015306 | -0.70102 | 16.648 | 16.0541 | 15.4224 | 14.6765 | 13.848 | 12.9653 | 11.902 | 10.8704 | 9.9918 | 5.6929 | 1.1602 | -6.5102 | 13.2418 | 12.5643 | 11.8418 | 10.9969 | 10.0735 | 9.049 | 7.8276 | 6.7071 | 5.802 | 2.5694 | 1.1337 | 0.46633
|  | WESTBOURNE PRIMARY | HT |  |  |  |  | 13.2816 | 12.6867 | 12.1337 | 11.498 | 10.7704 | 9.9316 | 8.9459 | 8.0173 | 7.0857 | 2.0704 | -1.1031 | -1.6235 | 17.0969 | 16.7224 | 16.349 | 15.9153 | 15.4153 | 14.8878 | 14.2316 | 13.5806 | 12.9296 | 9.5827 | 7.5724 | 7.2408 | 13.6061 | 13.0806 | 12.5633 | 11.9622 | 11.2755 | 10.5061 | 9.5796 | 8.6857 | 7.7939 | 3.052 | 0.12347 | -0.2949
|  | WESTBOURNE PRIMARY | HE |  |  |  |  | 13.3592 | 12.8388 | 12.2939 | 11.7092 | 11.0673 | 10.3602 | 9.5388 | 8.8071 | 8.0786 | 4.8194 | 3.1847 | 2.8949 | 16.9888 | 16.5663 | 16.1122 | 15.6102 | 15.0418 | 14.448 | 13.7347 | 13.0194 | 12.2939 | 7.9541 | 3.2449 | -4.0439 | 13.6694 | 13.2061 | 12.7071 | 12.1673 | 11.5653 | 10.9224 | 10.1551 | 9.45 | 8.7561 | 5.65 | 4.2051 | 3.9786
|  | WESTBOURNE PRIMARY | CF |  |  |  |  | 13.7031 | 13.4204 | 13.1061 | 12.7316 | 12.3061 | 11.901 | 11.4327 | 10.9806 | 10.5224 | 7.9429 | 5.3061 | 2.9071 | 17.1663 | 16.8398 | 16.4837 | 16.0531 | 15.5327 | 14.9561 | 14.301 | 13.6184 | 12.8878 | 7.8602 | -0.85714 | -16.4888 | 13.9663 | 13.7092 | 13.4265 | 13.0796 | 12.6939 | 12.3224 | 11.8898 | 11.4622 | 11.0245 | 8.5194 | 6.0347 | 3.8541
MELKSHAM GSP | FROME BSP | WESTBURY PRIMARY | MINIMUM HEADROOM | ST 87654 51530 | NO | NO | 3.045 | 12.2184 | 11.4173 | 10.7847 | 9.998 | 9.0643 | 7.8163 | 6.4602 | 5.2388 | 4.4806 | 0.40714 | -2.948 | -4.9061 | 15.3592 | 14.7327 | 14.2602 | 13.7041 | 13.05 | 12.2235 | 11.3102 | 10.4439 | 9.9 | 7.0163 | 3.6592 | -4.8082 | 11.8816 | 11.1245 | 10.5571 | 9.8337 | 8.9786 | 7.8357 | 6.5888 | 5.45 | 4.7459 | 1.2776 | -1.6143 | -3.2735
|  | WESTBURY PRIMARY | EE |  |  |  |  | 12.2184 | 11.4173 | 10.7847 | 9.998 | 9.0643 | 7.8163 | 6.4602 | 5.2388 | 4.4806 | 0.46633 | -2.3735 | -4.5153 | 15.3592 | 14.7327 | 14.2602 | 13.7041 | 13.05 | 12.2235 | 11.3102 | 10.4439 | 9.9 | 7.0163 | 4.0704 | -0.30204 | 11.8816 | 11.1245 | 10.5571 | 9.8337 | 8.9786 | 7.8357 | 6.5888 | 5.45 | 4.7459 | 1.2806 | -1.1143 | -2.9551
|  | WESTBURY PRIMARY | HT |  |  |  |  | 12.599 | 11.9602 | 10.9112 | 10.1184 | 9.549 | 8.4439 | 7.4153 | 6.4571 | 5.4735 | 0.40714 | -2.948 | -4.9061 | 15.751 | 15.3133 | 14.6031 | 14.1357 | 13.9092 | 13.3112 | 12.7122 | 12.1296 | 11.5398 | 8.7714 | 7.252 | 6.4571 | 12.2633 | 11.6745 | 10.7194 | 10.0051 | 9.5796 | 8.6071 | 7.6612 | 6.7571 | 5.8439 | 1.2776 | -1.6143 | -3.2735
|  | WESTBURY PRIMARY | HE |  |  |  |  | 12.6092 | 12.0173 | 11.1041 | 10.398 | 9.9235 | 8.9255 | 7.8724 | 6.9459 | 6.0857 | 1.5071 | -1.4888 | -2.9051 | 15.6724 | 15.2153 | 14.5153 | 14.0296 | 13.7776 | 13.1388 | 12.4398 | 11.7694 | 11.1173 | 7.5469 | 4.4143 | 0.30612 | 12.2694 | 11.7204 | 10.8724 | 10.2337 | 9.8745 | 8.9908 | 8.0378 | 7.1796 | 6.3673 | 2.2245 | -0.33878 | -1.5327
|  | WESTBURY PRIMARY | CF |  |  |  |  | 12.9071 | 12.4602 | 11.9133 | 11.5959 | 11.15 | 11.1398 | 10.6714 | 10.0888 | 9.4837 | 5.751 | 2.6061 | -0.31224 | 15.8224 | 15.4184 | 14.9122 | 14.6082 | 14.1684 | 14.0541 | 13.5857 | 13.0429 | 12.4694 | 8.6806 | 3.6592 | -4.8082 | 12.5469 | 12.1235 | 11.602 | 11.299 | 10.8724 | 10.8837 | 10.451 | 9.9204 | 9.3653 | 5.9357 | 3.1265 | 0.67347
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WESTERN ESPLANADE PRIMARY | MINIMUM HEADROOM | SU 41618 12009 | NO | NO | 6.304 | 27.3228 | 25.9953 | 24.7422 | 23.4637 | 21.1116 | 19.4667 | 17.8759 | 16.1218 | 14.8555 | 11.231 | 8.6167 | 6.879 | 30.1841 | 29.4514 | 28.7504 | 28.0188 | 26.4484 | 25.2882 | 23.8647 | 22.2882 | 21.0351 | 16.4728 | 11.8065 | 1.0177 | 26.9177 | 25.8086 | 24.7198 | 23.582 | 21.5106 | 20.0473 | 18.5749 | 16.779 | 15.582 | 12.2167 | 10.0228 | 8.6137
|  | WESTERN ESPLANADE PRIMARY | EE |  |  |  |  | 27.3228 | 25.9953 | 24.7422 | 23.4637 | 21.5586 | 20.1545 | 18.0912 | 16.1565 | 14.9055 | 11.231 | 9.2086 | 7.1014 | 30.1841 | 29.4514 | 28.7504 | 28.0188 | 26.6004 | 25.429 | 23.8647 | 22.2882 | 21.0351 | 16.4728 | 13.082 | 7.2851 | 26.9177 | 25.8086 | 24.7198 | 23.582 | 21.83 | 20.48 | 18.5749 | 16.779 | 15.582 | 12.2167 | 10.533 | 8.73
|  | WESTERN ESPLANADE PRIMARY | HT |  |  |  |  | 27.6239 | 26.4055 | 25.2892 | 23.5769 | 21.1116 | 19.4667 | 17.8759 | 16.1218 | 14.8555 | 11.6126 | 8.6167 | 6.879 | 30.4922 | 29.9035 | 29.3657 | 28.1106 | 26.4484 | 25.2882 | 24.0759 | 22.6535 | 21.5657 | 19.2422 | 17.7555 | 16.9514 | 27.2239 | 26.2259 | 25.282 | 23.7157 | 21.5106 | 20.0473 | 18.6259 | 17.0504 | 15.8963 | 12.7606 | 10.0228 | 8.6137
|  | WESTERN ESPLANADE PRIMARY | HE |  |  |  |  | 27.6147 | 26.4157 | 25.329 | 24.2677 | 22.5402 | 21.3759 | 19.7759 | 18.1861 | 17.0892 | 12.8024 | 10.9933 | 10.0239 | 30.3739 | 29.7198 | 29.1249 | 28.5239 | 27.2167 | 26.1922 | 24.881 | 23.5035 | 22.3259 | 17.3177 | 14.0433 | 8.929 | 27.2106 | 26.2259 | 25.3045 | 24.3882 | 22.8147 | 21.7473 | 20.3035 | 18.88 | 17.8371 | 13.9228 | 12.3994 | 11.58
|  | WESTERN ESPLANADE PRIMARY | CF |  |  |  |  | 29.1728 | 28.4963 | 27.6922 | 26.7453 | 25.5698 | 24.4555 | 23.2871 | 21.8157 | 20.5637 | 15.5075 | 13.4596 | 11.7779 | 31.1228 | 30.681 | 30.1739 | 29.5871 | 28.8565 | 27.9157 | 26.8177 | 25.5177 | 24.3004 | 17.5412 | 11.8065 | 1.0177 | 28.1371 | 27.782 | 27.2279 | 26.4433 | 25.4667 | 24.5147 | 23.4688 | 22.1749 | 21.0657 | 16.3586 | 14.4555 | 12.9239
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON PRIMARY | MINIMUM HEADROOM | SU 45207 09912 | NO | NO | 1.395 | 14.301 | 13.7388 | 13.5133 | 12.9276 | 12.2694 | 11.2622 | 10.1449 | 9.0296 | 8.2276 | 3.752 | -0.041837 | -2.0714 | 15.9571 | 15.5622 | 15.352 | 14.9133 | 14.3622 | 13.5765 | 12.6857 | 11.7765 | 11.0929 | 6.9929 | -0.18367 | -15.8276 | 13.7194 | 13.1551 | 13.0173 | 12.449 | 11.8112 | 10.8806 | 9.8316 | 8.7786 | 8.0561 | 4.1561 | 0.78776 | -0.94898
|  | WESTON PRIMARY | EE |  |  |  |  | 14.301 | 13.7388 | 13.5133 | 12.9276 | 12.2694 | 11.2622 | 10.1449 | 9.0296 | 8.2276 | 3.9541 | 0.77041 | -1.749 | 15.9571 | 15.5622 | 15.352 | 14.9133 | 14.3622 | 13.5765 | 12.6857 | 11.7765 | 11.0929 | 6.9929 | 1.9714 | -6.3173 | 13.7194 | 13.1551 | 13.0173 | 12.449 | 11.8112 | 10.8806 | 9.8316 | 8.7786 | 8.0561 | 4.2847 | 1.5112 | -0.67449
|  | WESTON PRIMARY | HT |  |  |  |  | 14.6286 | 14.2245 | 13.8112 | 13.302 | 12.751 | 12.2398 | 11.3265 | 10.3724 | 9.3735 | 3.752 | -0.041837 | -2.0714 | 16.3041 | 16.0745 | 15.848 | 15.5582 | 15.251 | 15.0367 | 14.5735 | 14.0653 | 13.4582 | 10.3806 | 8.5765 | 7.7122 | 14.1143 | 13.7061 | 13.3194 | 12.8153 | 12.2745 | 11.9031 | 11.0592 | 10.1776 | 9.2531 | 4.1561 | 0.78776 | -0.94898
|  | WESTON PRIMARY | HE |  |  |  |  | 14.6541 | 14.2796 | 13.9112 | 13.4724 | 12.9541 | 12.5745 | 11.8265 | 11.0418 | 10.2398 | 5.8418 | 2.7286 | 1.3296 | 16.1684 | 15.8694 | 15.5663 | 15.1898 | 14.7643 | 14.4408 | 13.8724 | 13.2643 | 12.6092 | 8.1531 | 2.9969 | -4.7755 | 14.1347 | 13.7582 | 13.4112 | 12.9704 | 12.4673 | 12.2184 | 11.5214 | 10.7969 | 10.0429 | 6.048 | 3.3173 | 2.1612
|  | WESTON PRIMARY | CF |  |  |  |  | 14.9337 | 14.7449 | 14.5102 | 14.301 | 14.0163 | 13.6969 | 13.6837 | 13.3408 | 12.9755 | 10.15 | 7.1439 | 4.248 | 16.2602 | 16.0276 | 15.7469 | 15.4561 | 15.0653 | 14.5857 | 14.25 | 13.7061 | 13.1184 | 8.3918 | -0.18367 | -15.8276 | 14.3755 | 14.1745 | 13.9173 | 13.7071 | 13.4153 | 13.0878 | 13.1531 | 12.8133 | 12.4531 | 9.8122 | 7.1357 | 4.6276
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH PRIMARY | MINIMUM HEADROOM | SY 67443 79096 | NO | NO | 4.754 | 11.3026 | 9.9934 | 8.2761 | 6.3638 | 4.4077 | 2.2006 | -0.20964 | -2.4627 | -4.18 | -11.1137 | -15.4423 | -16.576 | 15.7751 | 14.9424 | 13.7495 | 12.3955 | 10.97 | 9.42 | 7.6557 | 5.9444 | 4.671 | -1.2066 | -7.9494 | -25.5688 | 11.3291 | 10.1893 | 8.6087 | 6.8322 | 4.9812 | 2.924 | 0.66485 | -1.4658 | -3.0709 | -9.4311 | -13.2382 | -14.1627
|  | WEYMOUTH PRIMARY | EE |  |  |  |  | 11.3026 | 9.9934 | 8.2761 | 6.3638 | 4.4077 | 2.2006 | -0.20964 | -2.4627 | -4.18 | -11.1137 | -14.7249 | -15.4984 | 15.7751 | 14.9424 | 13.7495 | 12.3955 | 10.97 | 9.42 | 7.6557 | 5.9444 | 4.671 | -1.2066 | -6.6535 | -14.4566 | 11.3291 | 10.1893 | 8.6087 | 6.8322 | 4.9812 | 2.924 | 0.66485 | -1.4658 | -3.0709 | -9.4311 | -12.5933 | -13.2647
|  | WEYMOUTH PRIMARY | HT |  |  |  |  | 12.0598 | 10.6995 | 9.1924 | 7.8689 | 6.2434 | 4.4791 | 2.6506 | 0.88016 | -0.92188 | -10.0658 | -15.4423 | -16.576 | 16.5955 | 15.821 | 14.9353 | 14.2863 | 13.3251 | 12.3016 | 11.1628 | 10.0108 | 8.8118 | 3.2159 | 0.26996 | -0.3627 | 12.172 | 10.9853 | 9.6465 | 8.5261 | 7.0475 | 5.4271 | 3.6965 | 1.9842 | 0.22404 | -8.3596 | -13.2382 | -14.1627
|  | WEYMOUTH PRIMARY | HE |  |  |  |  | 11.9904 | 10.6271 | 9.1128 | 7.7751 | 6.1302 | 4.4495 | 2.6781 | 0.96689 | -0.778 | -8.7556 | -13.0811 | -14.13 | 16.3649 | 15.4802 | 14.4955 | 13.6649 | 12.5638 | 11.42 | 10.1414 | 8.7975 | 7.3863 | 0.064853 | -6.1117 | -13.9576 | 12.0934 | 10.9046 | 9.5618 | 8.4302 | 6.9393 | 5.3924 | 3.7108 | 2.0536 | 0.35261 | -7.2341 | -11.0923 | -11.9229
|  | WEYMOUTH PRIMARY | CF |  |  |  |  | 12.6934 | 11.7169 | 10.6465 | 9.4587 | 8.6271 | 7.8342 | 6.9934 | 6.2087 | 5.4098 | -0.30249 | -6.626 | -12.0913 | 16.7414 | 16.0383 | 15.271 | 14.4006 | 13.7363 | 12.92 | 11.9965 | 11.0587 | 10.0495 | 2.8261 | -7.9494 | -25.5688 | 12.7618 | 11.9271 | 10.9955 | 9.9577 | 9.2679 | 8.5291 | 7.7036 | 6.9016 | 6.0751 | 0.52812 | -5.2954 | -10.1923
COWLEY GSP | HEADINGTON BSP | WHEATLEY PRIMARY | MINIMUM HEADROOM | SP 60777 05379 | NO | NO | 19.594 | -9.3521 | 13.9367 | 13.0265 | 12.0112 | 9.5928 | 7.6856 | 5.6693 | 1.3622 | -1.6756 | -10.398 | -17.798 | -25.2858 | -8.2572 | 13.6438 | 12.6203 | 11.755 | 9.2163 | 7.5683 | 5.8499 | 1.2163 | -1.9725 | -10.3919 | -19.3184 | -32.1001 | -9.7837 | 12.7724 | 11.703 | 10.6918 | 7.9571 | 5.9652 | 3.9387 | -1.0082 | -4.6327 | -14.1001 | -22.7235 | -31.9552
|  | WHEATLEY PRIMARY | EE |  |  |  |  | -9.3521 | 13.9367 | 13.2887 | 12.403 | 11.0112 | 9.5224 | 8.154 | 6.1714 | 4.8805 | -0.10313 | -9.1664 | -12.8062 | -8.2572 | 13.6438 | 13.1775 | 12.4856 | 11.1856 | 10.0775 | 9.2142 | 7.501 | 6.4305 | 1.0397 | -11.149 | -18.6409 | -9.7837 | 12.7724 | 12.1571 | 11.3326 | 9.8387 | 8.3785 | 7.1663 | 5.154 | 3.804 | -1.749 | -12.2572 | -16.4786
|  | WHEATLEY PRIMARY | HT |  |  |  |  | -8.8225 | 14.4999 | 13.7652 | 13.054 | 10.8448 | 8.855 | 6.8448 | 5.4775 | 3.8356 | -2.449 | -11.3909 | -17.6848 | -7.9011 | 13.9765 | 13.3112 | 12.8061 | 10.804 | 9.2897 | 7.6601 | 6.7959 | 5.3673 | -0.86435 | -10.9266 | -18.1511 | -9.3205 | 13.2367 | 12.4234 | 11.6397 | 9.2999 | 7.3489 | 5.3234 | 4.0816 | 2.3459 | -4.4776 | -15.0603 | -22.5705
|  | WHEATLEY PRIMARY | HE |  |  |  |  | -9.0327 | 14.1316 | 13.0265 | 12.0112 | 9.5928 | 7.6856 | 5.6693 | 1.3622 | -1.6756 | -10.398 | -17.798 | -25.2858 | -8.048 | 13.6938 | 12.6203 | 11.755 | 9.2163 | 7.5683 | 5.8499 | 1.2163 | -1.9725 | -10.3919 | -19.3184 | -32.1001 | -9.4756 | 12.904 | 11.703 | 10.6918 | 7.9571 | 5.9652 | 3.9387 | -1.0082 | -4.6327 | -14.1001 | -22.7235 | -31.9552
|  | WHEATLEY PRIMARY | CF |  |  |  |  | -8.6541 | 14.8816 | 14.5173 | 13.8132 | 12.803 | 11.5877 | 10.4856 | 9.3877 | 8.3336 | 3.7254 | -2.2052 | -6.8103 | -7.9031 | 14.1377 | 13.8224 | 13.1285 | 12.3061 | 11.3377 | 10.4305 | 9.4918 | 8.4795 | 3.0479 | -5.4123 | -17.1725 | -9.1654 | 13.654 | 13.304 | 12.4765 | 11.504 | 10.3938 | 9.3877 | 8.3703 | 7.3408 | 2.1703 | -4.3409 | -9.5521
MELKSHAM GSP | ANDOVER BSP | WHITCHURCH PRIMARY | MINIMUM HEADROOM | SU 45924 48466 | NO | NO | 0.825 | 0.53245 | 0.42633 | 0.081429 | -0.10531 | -0.96143 | -1.4757 | -2.0288 | -3.7869 | -5.0859 | -8.3339 | -11.4655 | -15.3624 | 1.8161 | 1.7008 | 1.2804 | 1.0743 | 0.022245 | -0.57061 | -1.1727 | -3.2624 | -4.7461 | -8.1747 | -11.9318 | -17.489 | 1.0467 | 0.91306 | 0.49061 | 0.28143 | -0.76857 | -1.4002 | -2.0512 | -4.1716 | -5.688 | -9.288 | -13.0665 | -17.8053
|  | WHITCHURCH PRIMARY | EE |  |  |  |  | 0.53245 | 0.44571 | 0.33755 | 0.21306 | -0.15531 | -0.6951 | -1.0676 | -1.7859 | -2.1982 | -4.5216 | -8.9155 | -10.9063 | 1.8161 | 1.711 | 1.5671 | 1.408 | 1.0161 | 0.51612 | 0.24163 | -0.47469 | -0.85939 | -3.1614 | -8.4563 | -11.4216 | 1.0467 | 0.94571 | 0.81102 | 0.66102 | 0.27122 | -0.27265 | -0.5849 | -1.3278 | -1.7727 | -4.3961 | -9.7461 | -12.0104
|  | WHITCHURCH PRIMARY | HT |  |  |  |  | 0.5998 | 0.46 | 0.23551 | 0.14673 | -0.5849 | -1.1237 | -1.7584 | -2.1349 | -2.9053 | -5.6992 | -10.2573 | -13.4441 | 1.9243 | 1.7722 | 1.5069 | 1.4386 | 0.57224 | -0.0053061 | -0.62673 | -0.90939 | -1.6767 | -4.1839 | -9.0624 | -12.5614 | 1.1141 | 0.94163 | 0.66102 | 0.56816 | -0.31857 | -0.97878 | -1.688 | -2.0543 | -2.8982 | -5.988 | -11.3553 | -15.1431
|  | WHITCHURCH PRIMARY | HE |  |  |  |  | 0.59776 | 0.42633 | 0.081429 | -0.10531 | -0.96143 | -1.4757 | -2.0288 | -3.7869 | -5.0859 | -8.3339 | -11.4655 | -15.3624 | 1.9059 | 1.7008 | 1.2804 | 1.0743 | 0.022245 | -0.57061 | -1.1727 | -3.2624 | -4.7461 | -8.1747 | -11.9318 | -17.489 | 1.1202 | 0.91306 | 0.49061 | 0.28143 | -0.76857 | -1.4002 | -2.0512 | -4.1716 | -5.688 | -9.288 | -13.0665 | -17.8053
|  | WHITCHURCH PRIMARY | CF |  |  |  |  | 0.67429 | 0.63653 | 0.59061 | 0.46204 | 0.31714 | 0.11408 | -0.084898 | -0.29918 | -0.55837 | -2.4716 | -4.4431 | -6.6257 | 1.9498 | 1.8906 | 1.8131 | 1.6314 | 1.4406 | 1.16 | 0.89776 | 0.61102 | 0.31306 | -2.0073 | -4.8359 | -9.0114 | 1.1855 | 1.1549 | 1.0967 | 0.93857 | 0.77122 | 0.52429 | 0.29878 | 0.057959 | -0.20837 | -2.2696 | -4.6145 | -7.1339
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY PRIMARY | MINIMUM HEADROOM | SU 52936 08794 | NO | NO | 17.021 | -0.061273 | 8.4244 | 7.4724 | 6.4265 | 5.3408 | 4.3448 | 3.0469 | 1.8357 | 0.82444 | -3.649 | -6.1909 | -7.4756 | 2.9622 | 11.1214 | 10.5132 | 9.8428 | 9.1642 | 8.6867 | 7.9663 | 7.1714 | 6.4071 | 3.1306 | 1.4622 | -2.6552 | 0.15505 | 7.2234 | 6.3448 | 5.3765 | 4.3693 | 3.4397 | 2.1214 | 0.85709 | -0.20005 | -4.7133 | -7.0868 | -8.2868
|  | WHITELEY PRIMARY | EE |  |  |  |  | -0.061273 | 8.4244 | 7.4724 | 6.4265 | 5.3408 | 4.3448 | 3.0469 | 1.8357 | 0.82444 | -2.5674 | -3.7664 | -4.5021 | 2.9622 | 11.1214 | 10.5132 | 9.8428 | 9.1642 | 8.6867 | 7.9663 | 7.1714 | 6.4071 | 4.1142 | 2.7969 | 0.2622 | 0.15505 | 7.2234 | 6.3448 | 5.3765 | 4.3693 | 3.4397 | 2.1214 | 0.85709 | -0.20005 | -3.6368 | -4.7052 | -5.3531
|  | WHITELEY PRIMARY | HT |  |  |  |  | 0.26016 | 9.0744 | 8.3051 | 7.202 | 5.9122 | 4.8867 | 3.9387 | 3.0295 | 2.4204 | -2.1439 | -4.3868 | -5.5358 | 3.004 | 11.4306 | 10.9163 | 10.3479 | 9.6469 | 9.0326 | 8.452 | 7.8928 | 7.6132 | 4.5561 | 3.1653 | 2.4785 | 0.47546 | 7.7693 | 6.9153 | 5.9683 | 4.8591 | 3.9693 | 3.1265 | 2.2744 | 1.3561 | -3.2194 | -5.2949 | -6.346
|  | WHITELEY PRIMARY | HE |  |  |  |  | 0.33056 | 8.9346 | 8.0959 | 7.1693 | 6.0612 | 5.1561 | 3.9561 | 2.7163 | 1.6132 | -3.649 | -6.1909 | -7.4756 | 3.1112 | 11.3336 | 10.7612 | 10.152 | 9.5561 | 8.9663 | 8.3 | 7.6479 | 7.001 | 3.1306 | 1.4622 | -0.0010694 | 0.53567 | 7.7163 | 6.8897 | 5.9285 | 4.9673 | 4.1785 | 3.0683 | 1.7857 | 0.66322 | -4.7133 | -7.0868 | -8.2868
|  | WHITELEY PRIMARY | CF |  |  |  |  | 0.78975 | 9.7734 | 9.0255 | 8.2153 | 7.3346 | 6.852 | 6.3214 | 5.7469 | 4.9826 | 0.83464 | -2.6327 | -5.2745 | 3.2724 | 11.753 | 11.1132 | 10.6244 | 10.1255 | 9.7775 | 9.3326 | 8.8285 | 8.3336 | 5.8173 | 2.4673 | -2.6552 | 0.95097 | 8.4142 | 7.5887 | 6.8714 | 6.1489 | 5.7479 | 5.2755 | 4.7591 | 4.0469 | -0.005151 | -3.6949 | -6.2368
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WHITLEY WOOD PRIMARY | MINIMUM HEADROOM | SU 72812 69667 | NO | NO | 4.877 | 9.7871 | 9.1943 | 9.081 | 8.1065 | 7.3239 | 6.0596 | 4.6208 | 3.0678 | 1.6106 | -2.9078 | -5.3557 | -6.1567 | 10.7708 | 10.3157 | 10.1637 | 9.6882 | 8.8147 | 7.8014 | 6.5769 | 5.2473 | 4.13 | -0.47816 | -5.0537 | -15.069 | 8.8443 | 8.381 | 8.1994 | 7.1912 | 6.2678 | 5.0035 | 3.5249 | 1.8004 | 0.22184 | -4.1873 | -6.3078 | -6.9761
|  | WHITLEY WOOD PRIMARY | EE |  |  |  |  | 9.7871 | 9.1943 | 9.081 | 8.4637 | 7.429 | 6.132 | 4.6208 | 3.0841 | 1.9137 | -2.7363 | -4.9588 | -5.3649 | 10.7708 | 10.3157 | 10.1637 | 9.6882 | 8.8147 | 7.8014 | 6.5769 | 5.2473 | 4.13 | -0.47816 | -3.7047 | -8.3608 | 8.8443 | 8.381 | 8.2116 | 7.7035 | 6.6984 | 5.4331 | 3.9494 | 2.3127 | 0.9698 | -4.0863 | -5.9618 | -6.3282
|  | WHITLEY WOOD PRIMARY | HT |  |  |  |  | 10.1045 | 9.6688 | 9.1065 | 8.1065 | 7.3239 | 6.0596 | 4.6484 | 3.0678 | 1.6106 | -2.9078 | -5.3557 | -6.1567 | 11.1229 | 10.8473 | 10.4984 | 9.729 | 9.0973 | 8.2076 | 7.1116 | 5.7984 | 4.5963 | 1.6106 | 0.49837 | 0.05551 | 9.0514 | 8.6718 | 8.1994 | 7.1912 | 6.2678 | 5.0035 | 3.5249 | 1.8004 | 0.22184 | -4.1873 | -6.3078 | -6.9761
|  | WHITLEY WOOD PRIMARY | HE |  |  |  |  | 10.1667 | 9.8045 | 9.3371 | 8.7933 | 8.3178 | 7.2647 | 6.0504 | 4.7657 | 3.4973 | -1.4333 | -3.4884 | -4.1833 | 11.0463 | 10.7412 | 10.3718 | 9.9596 | 9.4698 | 8.6259 | 7.6137 | 6.4555 | 5.2504 | 0.13714 | -3.0761 | -7.7659 | 9.1178 | 8.7994 | 8.4127 | 7.9627 | 7.3351 | 6.2688 | 5.0371 | 3.6708 | 2.2871 | -2.8914 | -4.6435 | -5.2241
|  | WHITLEY WOOD PRIMARY | CF |  |  |  |  | 10.4351 | 10.1749 | 9.9647 | 9.6861 | 9.3657 | 8.8494 | 8.6871 | 7.8984 | 7.0729 | 1.4678 | -0.78122 | -3.1792 | 11.1708 | 10.9004 | 10.6514 | 10.3535 | 9.9963 | 9.4137 | 8.9933 | 8.128 | 7.2014 | 0.50245 | -5.0537 | -15.069 | 9.381 | 9.178 | 9.0218 | 8.8178 | 8.5831 | 8.1137 | 7.7841 | 6.981 | 6.129 | -0.07 | -2.272 | -4.4302
MINETY GSP | CIRENCESTER BSP | WHITEWAY PRIMARY | MINIMUM HEADROOM | SP 02076 03059 | NO | NO | 0.939 | 18.25 | 17.9867 | 17.6714 | 17.3235 | 17.25 | 16.6776 | 16.0153 | 15.3551 | 14.8735 | 12.0367 | 9.6602 | 8.2551 | 20.0663 | 19.8265 | 19.5327 | 19.2041 | 19.1347 | 18.7286 | 18.2531 | 17.7796 | 17.4357 | 15.4806 | 13.3714 | 7.9429 | 18.1949 | 17.9092 | 17.5571 | 17.1684 | 17.1092 | 16.5612 | 15.9388 | 15.3224 | 14.8816 | 12.4398 | 10.449 | 9.3592
|  | WHITEWAY PRIMARY | EE |  |  |  |  | 18.25 | 17.9867 | 17.6714 | 17.3235 | 17.25 | 16.6776 | 16.0153 | 15.3551 | 14.8735 | 12.2459 | 10.1786 | 8.6194 | 20.0663 | 19.8265 | 19.5327 | 19.2041 | 19.1347 | 18.7286 | 18.2531 | 17.7796 | 17.4357 | 15.4806 | 13.4449 | 10.498 | 18.1949 | 17.9092 | 17.5571 | 17.1684 | 17.1092 | 16.5612 | 15.9388 | 15.3224 | 14.8816 | 12.551 | 10.9204 | 9.6551
|  | WHITEWAY PRIMARY | HT |  |  |  |  | 18.3959 | 18.1765 | 17.9122 | 17.6622 | 17.3602 | 16.802 | 16.1969 | 15.8888 | 15.3133 | 12.0367 | 9.6602 | 8.2551 | 20.2806 | 20.1347 | 19.9418 | 19.7643 | 19.5378 | 19.2122 | 18.8327 | 18.7459 | 18.3949 | 16.5949 | 15.4878 | 14.901 | 18.3949 | 18.1745 | 17.9061 | 17.651 | 17.3337 | 16.8051 | 16.2184 | 15.9908 | 15.4337 | 12.4398 | 10.449 | 9.3592
|  | WHITEWAY PRIMARY | HE |  |  |  |  | 18.4173 | 18.2184 | 17.9827 | 17.7592 | 17.4898 | 17.0316 | 16.5255 | 16.3224 | 15.8551 | 13.102 | 11.0684 | 10.0602 | 20.2408 | 20.0735 | 19.8663 | 19.6673 | 19.4194 | 19.0867 | 18.698 | 18.5969 | 18.2276 | 16.0439 | 13.9694 | 11.2551 | 18.4133 | 18.2122 | 17.9694 | 17.7418 | 17.4582 | 17.0184 | 16.5194 | 16.3837 | 15.9265 | 13.4378 | 11.8112 | 11.0296
|  | WHITEWAY PRIMARY | CF |  |  |  |  | 18.599 | 18.4622 | 18.348 | 18.2 | 18.0724 | 17.8929 | 17.6786 | 17.4429 | 17.2112 | 15.7776 | 13.8265 | 11.9847 | 20.3337 | 20.1806 | 20.0459 | 19.8673 | 19.6898 | 19.449 | 19.1622 | 18.852 | 18.5276 | 16.6469 | 13.3714 | 7.9429 | 18.5837 | 18.4327 | 18.3163 | 18.1551 | 18.0153 | 17.8214 | 17.5837 | 17.3245 | 17.0612 | 15.7418 | 14.0092 | 12.4735
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WILSON ROAD PRIMARY | MINIMUM HEADROOM | SU 69235 73304 | NO | NO | 2.791 | 13.2497 | 12.6742 | 11.9283 | 11.1334 | 10.4803 | 9.1813 | 8.0068 | 6.8436 | 5.9456 | 1.5079 | -2.2462 | -4.3819 | 15.8619 | 15.3528 | 14.6834 | 14.0007 | 13.5303 | 12.5783 | 11.6446 | 10.6936 | 9.9344 | 5.8823 | 0.59459 | -12.9626 | 12.3436 | 11.7772 | 11.0221 | 10.2538 | 9.717 | 8.4987 | 7.3803 | 6.2742 | 5.4334 | 1.4691 | -1.6921 | -3.535
|  | WILSON ROAD PRIMARY | EE |  |  |  |  | 13.2497 | 12.6742 | 11.9283 | 11.1334 | 10.4803 | 9.1813 | 8.0068 | 6.8436 | 5.9456 | 1.5079 | -1.6503 | -4.1289 | 15.8619 | 15.3528 | 14.6834 | 14.0007 | 13.5303 | 12.5783 | 11.6446 | 10.6936 | 9.9344 | 5.8823 | 1.5915 | -5.3738 | 12.3436 | 11.7772 | 11.0221 | 10.2538 | 9.717 | 8.4987 | 7.3803 | 6.2742 | 5.4334 | 1.4691 | -1.1503 | -3.337
|  | WILSON ROAD PRIMARY | HT |  |  |  |  | 13.6752 | 13.264 | 12.715 | 12.1874 | 11.3252 | 10.2068 | 9.2426 | 8.6415 | 7.666 | 2.0344 | -2.2462 | -4.3819 | 16.3395 | 16.0283 | 15.5966 | 15.2395 | 14.6977 | 14.0303 | 13.4089 | 13.0997 | 12.4619 | 9.1772 | 7.013 | 6.1293 | 12.8007 | 12.3987 | 11.8446 | 11.3538 | 10.5721 | 9.5293 | 8.6201 | 8.1017 | 7.1813 | 2.0364 | -1.6921 | -3.535
|  | WILSON ROAD PRIMARY | HE |  |  |  |  | 13.6446 | 13.2487 | 12.7303 | 12.2395 | 11.4364 | 10.3813 | 9.4987 | 8.9568 | 8.0834 | 3.5028 | 0.35684 | -0.86051 | 16.2109 | 15.8415 | 15.3589 | 14.9405 | 14.3262 | 13.5589 | 12.8415 | 12.4232 | 11.6762 | 7.315 | 2.866 | -3.6677 | 12.7803 | 12.3936 | 11.8568 | 11.4007 | 10.6742 | 9.7007 | 8.866 | 8.4242 | 7.6079 | 3.4426 | 0.75786 | -0.27888
|  | WILSON ROAD PRIMARY | CF |  |  |  |  | 13.9813 | 13.7058 | 13.3895 | 13.0456 | 12.5589 | 11.9895 | 11.5752 | 11.116 | 10.6334 | 8.0211 | 4.8191 | 1.8293 | 16.3691 | 16.0415 | 15.6538 | 15.2732 | 14.7987 | 14.1752 | 13.5946 | 12.9609 | 12.2864 | 8.0334 | 0.59459 | -12.9626 | 13.063 | 12.767 | 12.4293 | 12.1028 | 11.6701 | 11.1354 | 10.7262 | 10.2721 | 9.8007 | 7.414 | 4.5007 | 1.9242
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE PRIMARY | MINIMUM HEADROOM | SZ 02014 99989 | NO | NO | 3.581 | 0.083624 | -0.64903 | 17.1193 | 16.0285 | 15.004 | 13.7428 | 12.2204 | 10.6816 | 9.5295 | 3.5714 | -0.84801 | -3.196 | 5.2265 | 4.8193 | 21.4316 | 20.6877 | 19.9469 | 19.0632 | 17.9897 | 16.8969 | 16.1367 | 12.1612 | 7.6244 | -3.2868 | 0.43464 | -0.15821 | 15.903 | 14.8959 | 13.9295 | 12.7408 | 11.3071 | 9.8622 | 8.85 | 3.8734 | -0.0071918 | -2.0643
|  | WIMBORNE PRIMARY | EE |  |  |  |  | 0.083624 | -0.64903 | 17.1193 | 16.0285 | 15.004 | 13.7428 | 12.2204 | 10.6816 | 9.5295 | 3.7112 | -0.05209 | -2.8909 | 5.2265 | 4.8193 | 21.4316 | 20.6877 | 19.9469 | 19.0632 | 17.9897 | 16.8969 | 16.1367 | 12.1612 | 8.3806 | 2.754 | 0.43464 | -0.15821 | 15.903 | 14.8959 | 13.9295 | 12.7408 | 11.3071 | 9.8622 | 8.85 | 3.9367 | 0.68567 | -1.8205
|  | WIMBORNE PRIMARY | HT |  |  |  |  | 0.54995 | -0.34699 | 17.502 | 16.8642 | 16.0214 | 14.9153 | 13.6061 | 12.2204 | 10.7969 | 3.5714 | -0.84801 | -3.196 | 5.7591 | 5.2663 | 22.0193 | 21.7785 | 21.2887 | 20.6857 | 19.952 | 19.1612 | 18.3397 | 14.4938 | 12.4826 | 11.5469 | 0.94281 | 0.15811 | 16.3 | 15.8112 | 15.0428 | 14.0397 | 12.853 | 11.5948 | 10.2969 | 3.8734 | -0.0071918 | -2.0643
|  | WIMBORNE PRIMARY | HE |  |  |  |  | 0.54791 | -0.33474 | 17.5204 | 16.8887 | 16.0469 | 15.1061 | 13.9438 | 12.704 | 11.4183 | 4.704 | 0.53158 | -1.2827 | 5.6295 | 5.0714 | 21.7561 | 21.4316 | 20.851 | 20.1877 | 19.3795 | 18.4969 | 17.5632 | 12.5132 | 8.3132 | 3.0918 | 0.93464 | 0.15913 | 16.3091 | 15.8214 | 15.054 | 14.1857 | 13.1204 | 11.9795 | 10.7938 | 4.7959 | 1.1295 | -0.44801
|  | WIMBORNE PRIMARY | CF |  |  |  |  | 1.0357 | 0.40403 | 18.554 | 17.8734 | 17.6275 | 17.2397 | 16.6714 | 16.0418 | 15.3816 | 10.7336 | 6.2061 | 2.2775 | 5.8673 | 5.4204 | 22.2418 | 21.7244 | 21.5306 | 21.0714 | 20.4765 | 19.8214 | 19.1234 | 14.2581 | 7.6244 | -3.2868 | 1.3755 | 0.82138 | 17.2387 | 16.6224 | 16.4663 | 16.0877 | 15.5489 | 14.952 | 14.3224 | 10.0091 | 6.0397 | 2.6795
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES PRIMARY | MINIMUM HEADROOM | SU 03028 12678 | YES | NO | 0.027 | 4.5352 | 4.4954 | 4.4638 | 4.4158 | 4.3913 | 4.3332 | 4.275 | 4.2087 | 4.176 | 4.0219 | 3.9699 | 3.926 | 4.2888 | 4.2592 | 4.2347 | 4.2 | 4.1806 | 4.1357 | 4.0929 | 4.0388 | 4.0153 | 3.901 | 3.7245 | 3.3235 | 4.3745 | 4.3367 | 4.3061 | 4.2622 | 4.2367 | 4.1806 | 4.1245 | 4.0582 | 4.0286 | 3.8918 | 3.8449 | 3.8061
|  | WIMBORNE ST GILES PRIMARY | EE |  |  |  |  | 4.5352 | 4.4954 | 4.4638 | 4.4158 | 4.3913 | 4.3332 | 4.275 | 4.2087 | 4.176 | 4.0219 | 3.9699 | 3.9464 | 4.2888 | 4.2592 | 4.2347 | 4.2 | 4.1806 | 4.1357 | 4.0929 | 4.0388 | 4.0153 | 3.901 | 3.7827 | 3.5918 | 4.3745 | 4.3367 | 4.3061 | 4.2622 | 4.2367 | 4.1806 | 4.1245 | 4.0582 | 4.0286 | 3.8918 | 3.8449 | 3.8245
|  | WIMBORNE ST GILES PRIMARY | HT |  |  |  |  | 4.5546 | 4.5321 | 4.5107 | 4.4801 | 4.4515 | 4.4077 | 4.3577 | 4.326 | 4.274 | 4.0566 | 3.977 | 3.926 | 4.3102 | 4.2949 | 4.2816 | 4.2622 | 4.2449 | 4.2173 | 4.1837 | 4.1684 | 4.1306 | 3.9888 | 3.949 | 3.9255 | 4.3939 | 4.3724 | 4.3541 | 4.3235 | 4.298 | 4.2561 | 4.2082 | 4.1786 | 4.1286 | 3.9224 | 3.85 | 3.8061
|  | WIMBORNE ST GILES PRIMARY | HE |  |  |  |  | 4.5566 | 4.5321 | 4.5117 | 4.4832 | 4.4566 | 4.4128 | 4.3617 | 4.3321 | 4.2821 | 4.0495 | 3.9923 | 3.973 | 4.3061 | 4.2867 | 4.2735 | 4.2531 | 4.2337 | 4.2031 | 4.1663 | 4.149 | 4.1082 | 3.9245 | 3.798 | 3.6082 | 4.3969 | 4.3735 | 4.3551 | 4.3255 | 4.302 | 4.2612 | 4.2133 | 4.1857 | 4.1388 | 3.9204 | 3.8684 | 3.85
|  | WIMBORNE ST GILES PRIMARY | CF |  |  |  |  | 4.5699 | 4.5464 | 4.526 | 4.5036 | 4.4872 | 4.4617 | 4.4372 | 4.4066 | 4.373 | 4.2148 | 4.0995 | 4.0158 | 4.3153 | 4.2969 | 4.2827 | 4.2622 | 4.251 | 4.2255 | 4.2031 | 4.1755 | 4.1449 | 3.9663 | 3.7245 | 3.3235 | 4.4092 | 4.3867 | 4.3704 | 4.3459 | 4.3316 | 4.3071 | 4.2857 | 4.2541 | 4.2235 | 4.0714 | 3.9673 | 3.8908
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON PRIMARY | MINIMUM HEADROOM | ST 71286 27802 | NO | NO | 4.042 | 1.2389 | 0.8818 | 0.52976 | 0.17874 | -0.17228 | -0.28861 | -0.72433 | -1.1631 | -1.4743 | -3.1458 | -4.3468 | -5.0917 | 0.58486 | 0.4369 | 0.26649 | 0.028736 | -0.21412 | -0.26412 | -0.55392 | -0.85392 | -1.0743 | -2.3682 | -3.9264 | -7.6386 | 0.15016 | -0.097795 | -0.3478 | -0.60494 | -0.93657 | -1.0284 | -1.4407 | -1.8519 | -2.1376 | -3.6304 | -4.6876 | -5.2856
|  | WINCANTON PRIMARY | EE |  |  |  |  | 1.2389 | 0.8818 | 0.52976 | 0.17874 | -0.17228 | -0.28861 | -0.72433 | -1.1631 | -1.4743 | -3.1458 | -4.1407 | -4.9039 | 0.58486 | 0.4369 | 0.26649 | 0.028736 | -0.21412 | -0.26412 | -0.55392 | -0.85392 | -1.0743 | -2.3682 | -3.66 | -5.5835 | 0.15016 | -0.097795 | -0.3478 | -0.60494 | -0.93657 | -1.0284 | -1.4407 | -1.8519 | -2.1376 | -3.6304 | -4.5009 | -5.1243
|  | WINCANTON PRIMARY | HT |  |  |  |  | 1.3706 | 1.0716 | 0.77465 | 0.49098 | 0.24608 | -0.12739 | -0.54575 | -0.98555 | -1.0927 | -3.1335 | -4.3468 | -5.0917 | 0.66343 | 0.55425 | 0.42669 | 0.30323 | 0.19608 | 0.019552 | -0.21412 | -0.46412 | -0.46922 | -1.5509 | -2.1498 | -2.4866 | 0.21853 | -0.004938 | -0.23045 | -0.44575 | -0.63249 | -0.92841 | -1.2539 | -1.6651 | -1.7447 | -3.61 | -4.6876 | -5.2856
|  | WINCANTON PRIMARY | HE |  |  |  |  | 1.3828 | 1.094 | 0.81241 | 0.542 | 0.31139 | -0.0059584 | -0.37433 | -0.75494 | -0.80596 | -2.6509 | -3.6947 | -4.2162 | 0.65016 | 0.52669 | 0.39302 | 0.24914 | 0.12363 | -0.095754 | -0.34677 | -0.61922 | -0.64984 | -2.109 | -3.4315 | -5.257 | 0.22874 | 0.011389 | -0.20698 | -0.41514 | -0.5978 | -0.84882 | -1.1315 | -1.457 | -1.5447 | -3.1692 | -4.1039 | -4.5672
|  | WINCANTON PRIMARY | CF |  |  |  |  | 1.6206 | 1.4838 | 1.3002 | 1.0787 | 0.79812 | 0.56343 | 0.39812 | 0.19506 | -0.018203 | -1.0009 | -2.2162 | -3.3345 | 0.73588 | 0.66343 | 0.58078 | 0.46955 | 0.31445 | 0.11649 | -0.051877 | -0.26106 | -0.48555 | -1.7274 | -3.9264 | -7.6386 | 0.42057 | 0.30527 | 0.17159 | 0.0073069 | -0.20086 | -0.37024 | -0.49167 | -0.63555 | -0.78453 | -1.6876 | -2.7886 | -3.7713
COWLEY GSP | WITNEY BSP | WINDRUSH PARK PRIMARY | MINIMUM HEADROOM | SP 33366 09758 | NO | NO | 11.939 | 11.2419 | 11.0358 | 10.8337 | 10.5674 | 10.2551 | 9.8541 | 9.7062 | 9.3164 | 8.9184 | 7.2643 | 5.9041 | 5.0786 | 12.8388 | 12.7225 | 12.596 | 12.4317 | 12.1766 | 11.8694 | 11.8164 | 11.5215 | 11.3041 | 10.0449 | 8.1817 | 3.8521 | 11.7633 | 11.5592 | 11.3694 | 11.1102 | 10.8143 | 10.4337 | 10.3521 | 9.999 | 9.65 | 8.2276 | 7.0735 | 6.4041
|  | WINDRUSH PARK PRIMARY | EE |  |  |  |  | 11.2419 | 11.0358 | 10.8337 | 10.5674 | 10.2551 | 9.8541 | 9.7245 | 9.3511 | 9.0592 | 7.4715 | 6.1919 | 5.2194 | 12.8388 | 12.7225 | 12.596 | 12.4317 | 12.1766 | 11.8694 | 11.8164 | 11.5215 | 11.3041 | 10.0449 | 8.5602 | 6.2888 | 11.7633 | 11.5592 | 11.3694 | 11.1102 | 10.8143 | 10.4337 | 10.3521 | 9.999 | 9.7398 | 8.3674 | 7.3021 | 6.499
|  | WINDRUSH PARK PRIMARY | HT |  |  |  |  | 11.3092 | 11.1307 | 10.9511 | 10.6919 | 10.4041 | 10.0817 | 9.7062 | 9.3164 | 8.9184 | 7.2643 | 5.9041 | 5.0786 | 12.9266 | 12.8439 | 12.7531 | 12.6266 | 12.4847 | 12.3409 | 12.1582 | 11.9551 | 11.7133 | 10.9674 | 10.3633 | 9.996 | 11.848 | 11.6796 | 11.5184 | 11.2807 | 11.0174 | 10.7337 | 10.3858 | 10.0225 | 9.65 | 8.2276 | 7.0735 | 6.4041
|  | WINDRUSH PARK PRIMARY | HE |  |  |  |  | 11.3398 | 11.1796 | 11.0225 | 10.8051 | 10.547 | 10.2878 | 9.9837 | 9.6704 | 9.3531 | 8.0623 | 6.8072 | 6.1307 | 12.9204 | 12.8358 | 12.7429 | 12.6184 | 12.4735 | 12.2878 | 12.0429 | 11.7807 | 11.5041 | 10.3643 | 8.8868 | 6.7164 | 11.8745 | 11.7204 | 11.5766 | 11.3745 | 11.1368 | 10.9072 | 10.6215 | 10.3225 | 10.0184 | 8.8929 | 7.8766 | 7.3276
|  | WINDRUSH PARK PRIMARY | CF |  |  |  |  | 11.4858 | 11.3909 | 11.2858 | 11.197 | 11.0837 | 10.9766 | 10.8766 | 10.7347 | 10.5827 | 9.6735 | 8.4307 | 7.2653 | 13.0041 | 12.9541 | 12.8939 | 12.8327 | 12.6898 | 12.5204 | 12.3541 | 12.1449 | 11.9194 | 10.5939 | 8.1817 | 3.8521 | 12.0031 | 11.9102 | 11.8092 | 11.7256 | 11.6143 | 11.5082 | 11.4133 | 11.2715 | 11.1225 | 10.3521 | 9.2102 | 8.2582
MANNINGTON GSP |  | WINFRITH HEATH PRIMARY | MINIMUM HEADROOM | SY 80748 86538 | NO | NO | 5.044 | 9.6621 | 8.6397 | 7.4958 | 6.2836 | 5.704 | 4.9009 | 4.1928 | 3.555 | 3.2826 | 0.41827 | -0.72255 | -1.2368 | 16.9326 | 15.957 | 14.9121 | 13.8723 | 13.554 | 13.3519 | 13.0366 | 12.6999 | 12.5999 | 10.7407 | 9.7785 | 7.6101 | 17.0132 | 16.0468 | 14.9723 | 13.8264 | 13.3652 | 12.7213 | 12.1509 | 11.6305 | 11.4172 | 8.9489 | 7.9928 | 7.5621
|  | WINFRITH HEATH PRIMARY | EE |  |  |  |  | 9.6621 | 8.6397 | 7.4958 | 6.2836 | 5.704 | 4.9009 | 4.1928 | 3.555 | 3.2826 | 0.44786 | -0.5899 | -1.1164 | 16.9326 | 15.957 | 14.9121 | 13.8723 | 13.6907 | 13.3601 | 13.0366 | 12.6999 | 12.5999 | 10.7407 | 9.8407 | 8.7448 | 17.0132 | 16.0468 | 14.9723 | 13.8264 | 13.3652 | 12.7213 | 12.1509 | 11.6305 | 11.4172 | 8.9734 | 8.105 | 7.6632
|  | WINFRITH HEATH PRIMARY | HT |  |  |  |  | 9.7254 | 8.7152 | 7.603 | 7.1479 | 6.5662 | 5.7877 | 5.1448 | 4.5377 | 3.6295 | 0.41827 | -0.72255 | -1.2368 | 16.9795 | 16.0213 | 15.003 | 14.8672 | 14.6877 | 14.3642 | 14.0989 | 13.8193 | 13.2091 | 11.1785 | 10.6683 | 10.4397 | 17.0591 | 16.1081 | 15.057 | 14.703 | 14.2356 | 13.6132 | 13.0989 | 12.606 | 11.7979 | 8.9489 | 7.9928 | 7.5621
|  | WINFRITH HEATH PRIMARY | HE |  |  |  |  | 9.7315 | 8.7305 | 7.6203 | 6.4713 | 5.8989 | 5.155 | 4.5499 | 3.9805 | 3.404 | 0.69786 | -0.34602 | -0.68173 | 16.9621 | 15.9989 | 14.9683 | 13.954 | 13.7652 | 13.4795 | 13.205 | 12.9336 | 12.6479 | 10.8183 | 9.8928 | 8.8774 | 17.056 | 16.1091 | 15.0652 | 13.9672 | 13.5183 | 12.9346 | 12.453 | 11.9877 | 11.5183 | 9.1642 | 8.2795 | 7.9999
|  | WINFRITH HEATH PRIMARY | CF |  |  |  |  | 9.8203 | 8.8754 | 8.1213 | 6.755 | 6.053 | 5.4846 | 5.004 | 4.5734 | 4.1652 | 2.1754 | 0.90704 | -0.056224 | 16.9968 | 16.053 | 15.3836 | 14.0448 | 13.554 | 13.3519 | 13.1509 | 12.9274 | 12.7172 | 11.3315 | 9.7785 | 7.6101 | 17.1234 | 16.2183 | 15.5295 | 14.2142 | 13.5938 | 13.1713 | 12.803 | 12.4632 | 12.1448 | 10.5213 | 9.3928 | 8.5509
COWLEY GSP | DRAYTON BSP | WINSMORE LANE PRIMARY | MINIMUM HEADROOM | SU 49513 96982 | NO | YES | 2.779 | 9.149 | 8.6704 | 8.4694 | 7.9306 | 7.3765 | 6.4439 | 5.3949 | 4.351 | 3.5704 | -0.68163 | -4.2367 | -6.3388 | 12.7184 | 12.2878 | 12.102 | 11.5918 | 11.1112 | 10.4571 | 9.7 | 8.9306 | 8.3571 | 5.1276 | 1.4265 | -8.2449 | 8.9724 | 8.4755 | 8.2745 | 7.7 | 7.1653 | 6.2949 | 5.3133 | 4.3357 | 3.6143 | -0.14286 | -3.2051 | -4.902
|  | WINSMORE LANE PRIMARY | EE |  |  |  |  | 9.149 | 8.6704 | 8.4694 | 7.9306 | 7.3765 | 6.4439 | 5.3949 | 4.351 | 3.5704 | -0.52959 | -3.5449 | -5.9929 | 12.7184 | 12.2878 | 12.102 | 11.5918 | 11.1112 | 10.4571 | 9.7 | 8.9306 | 8.3571 | 5.1276 | 1.7796 | -3.3663 | 8.9724 | 8.4755 | 8.2745 | 7.7 | 7.1653 | 6.2949 | 5.3133 | 4.3357 | 3.6143 | -0.069388 | -2.5878 | -4.6184
|  | WINSMORE LANE PRIMARY | HT |  |  |  |  | 9.401 | 9.0133 | 8.5939 | 8.1724 | 7.7031 | 7.1857 | 6.3235 | 5.4286 | 4.4827 | -0.68163 | -4.2367 | -6.3388 | 13.0653 | 12.7918 | 12.4765 | 12.1755 | 11.8306 | 11.6337 | 11.1378 | 10.6082 | 10.0255 | 7.2531 | 5.6031 | 4.7163 | 9.2724 | 8.8888 | 8.4571 | 8.0347 | 7.5602 | 7.1286 | 6.3184 | 5.4755 | 4.5776 | -0.14286 | -3.2051 | -4.902
|  | WINSMORE LANE PRIMARY | HE |  |  |  |  | 9.4276 | 9.0694 | 8.749 | 8.3622 | 7.8714 | 7.4949 | 6.7724 | 6.0286 | 5.2643 | 1.0459 | -1.9347 | -3.4224 | 12.9816 | 12.6643 | 12.3827 | 12.0316 | 11.5663 | 11.3398 | 10.8031 | 10.2276 | 9.6224 | 6.0959 | 2.7041 | -2.0878 | 9.2939 | 8.9378 | 8.6173 | 8.2316 | 7.7184 | 7.4102 | 6.7276 | 6.0194 | 5.2878 | 1.4449 | -1.0378 | -2.2327
|  | WINSMORE LANE PRIMARY | CF |  |  |  |  | 9.7041 | 9.5204 | 9.3122 | 9.0612 | 8.8214 | 8.55 | 8.5286 | 8.2276 | 7.9143 | 5.1745 | 2.2898 | -0.52041 | 13.0959 | 12.8755 | 12.6224 | 12.3 | 11.9735 | 11.5867 | 11.4041 | 10.9663 | 10.4888 | 6.9367 | 1.4265 | -8.2449 | 9.5418 | 9.3561 | 9.1378 | 8.8633 | 8.6133 | 8.3316 | 8.3214 | 8.0112 | 7.6816 | 5.1235 | 2.5061 | 0.056122
MANNINGTON GSP | LYTCHETT BSP | WINTERBORNE KINGSTON PRIMARY | MINIMUM HEADROOM | SY 84631 98138 | NO | NO | 1.81 | 16.4684 | 16.0877 | 15.851 | 15.5582 | 15.2408 | 14.8255 | 14.8071 | 14.4173 | 14.1571 | 12.7541 | 11.8898 | 11.2949 | 16.6794 | 16.4263 | 16.2539 | 16.0273 | 15.7804 | 15.4733 | 15.5692 | 15.2886 | 15.1192 | 14.1661 | 13.1926 | 10.5682 | 16.0106 | 15.6555 | 15.429 | 15.1351 | 14.8177 | 14.4075 | 14.483 | 14.1137 | 13.8728 | 12.6382 | 11.8728 | 11.3657
|  | WINTERBORNE KINGSTON PRIMARY | EE |  |  |  |  | 16.4684 | 16.0877 | 15.851 | 15.5582 | 15.2408 | 14.8255 | 14.8071 | 14.4173 | 14.1571 | 12.7541 | 11.9602 | 11.4469 | 16.6794 | 16.4263 | 16.2539 | 16.0273 | 15.7804 | 15.4733 | 15.5692 | 15.2886 | 15.1192 | 14.1661 | 13.2896 | 11.9998 | 16.0106 | 15.6555 | 15.429 | 15.1351 | 14.8177 | 14.4075 | 14.483 | 14.1137 | 13.8728 | 12.6382 | 11.9433 | 11.4984
|  | WINTERBORNE KINGSTON PRIMARY | HT |  |  |  |  | 16.6041 | 16.2796 | 16.0979 | 15.8684 | 15.6184 | 15.3296 | 14.9582 | 14.5673 | 14.1612 | 12.8582 | 11.8898 | 11.2949 | 16.8222 | 16.6375 | 16.5324 | 16.3835 | 16.2171 | 16.062 | 15.8273 | 15.5763 | 15.31 | 14.7375 | 14.2794 | 14.0161 | 16.1545 | 15.8688 | 15.7035 | 15.482 | 15.2433 | 14.9861 | 14.6392 | 14.2688 | 13.881 | 12.7341 | 11.8728 | 11.3657
|  | WINTERBORNE KINGSTON PRIMARY | HE |  |  |  |  | 16.6133 | 16.2949 | 16.1224 | 15.9041 | 15.6704 | 15.4184 | 15.0837 | 14.7296 | 14.3643 | 13.1041 | 12.3367 | 11.9928 | 16.8049 | 16.6151 | 16.4988 | 16.3416 | 16.1661 | 16.0028 | 15.761 | 15.4988 | 15.2222 | 14.3733 | 13.4916 | 12.2937 | 16.1616 | 15.882 | 15.7249 | 15.5157 | 15.2892 | 15.0677 | 14.7504 | 14.4096 | 14.0545 | 12.9657 | 12.2912 | 12.0126
|  | WINTERBORNE KINGSTON PRIMARY | CF |  |  |  |  | 16.7082 | 16.452 | 16.2969 | 16.1724 | 16.0102 | 15.8439 | 15.6949 | 15.4959 | 15.2837 | 14.4592 | 13.45 | 12.4653 | 16.8559 | 16.6957 | 16.5743 | 16.4794 | 16.3406 | 16.1855 | 16.0447 | 15.8518 | 15.6467 | 14.7386 | 13.1926 | 10.5682 | 16.2504 | 16.0239 | 15.8718 | 15.7586 | 15.5994 | 15.4341 | 15.2973 | 15.0973 | 14.883 | 14.1647 | 13.2504 | 12.3892
MANNINGTON GSP | REDHILL BSP | WINTON PRIMARY | MINIMUM HEADROOM | SZ 09349 93822 | NO | NO | 1.448 | 3.8163 | 3.5122 | 10.052 | 9.3235 | 8.5429 | 7.1929 | 5.6786 | 4.1694 | 3.0776 | -1.9316 | -5.4582 | -6.3959 | 8.3867 | 8.1347 | 15.951 | 15.2867 | 14.5714 | 13.5786 | 12.4296 | 11.2653 | 10.4612 | 6.2551 | -0.0020408 | -14.9888 | 2.9082 | 2.6459 | 9.9878 | 9.252 | 8.4612 | 7.1796 | 5.7245 | 4.2704 | 3.2969 | -0.97755 | -3.9082 | -4.6776
|  | WINTON PRIMARY | EE |  |  |  |  | 3.8163 | 3.5122 | 10.052 | 9.3235 | 8.5429 | 7.1929 | 5.6786 | 4.1694 | 3.0776 | -1.9316 | -5.1276 | -5.348 | 8.3867 | 8.1347 | 15.951 | 15.2867 | 14.5714 | 13.5786 | 12.4296 | 11.2653 | 10.4612 | 6.2551 | 1.6827 | -5.1 | 2.9082 | 2.6459 | 9.9878 | 9.252 | 8.4612 | 7.1796 | 5.7245 | 4.2704 | 3.2969 | -0.97755 | -3.6122 | -3.8347
|  | WINTON PRIMARY | HT |  |  |  |  | 4.302 | 3.8 | 10.4153 | 10.1827 | 9.5878 | 8.5031 | 7.3041 | 6.0418 | 4.7337 | -1.652 | -5.4582 | -6.3959 | 8.9296 | 8.6306 | 16.6173 | 16.5357 | 16.1184 | 15.498 | 14.7888 | 14.0235 | 13.2235 | 9.5837 | 7.7194 | 7.1857 | 3.4551 | 2.9673 | 10.3918 | 10.2235 | 9.6439 | 8.6541 | 7.5429 | 6.3714 | 5.152 | -0.65612 | -3.9082 | -4.6776
|  | WINTON PRIMARY | HE |  |  |  |  | 4.3745 | 3.9286 | 10.6082 | 10.4327 | 9.9092 | 8.9449 | 7.8704 | 6.7439 | 5.5633 | 0.34592 | -2.7082 | -3.5276 | 8.8102 | 8.448 | 16.3918 | 16.2255 | 15.7265 | 15.0235 | 14.2112 | 13.3357 | 12.3969 | 7.4439 | 2.7184 | -4.2755 | 3.5102 | 3.0724 | 10.552 | 10.4378 | 9.9214 | 9.0347 | 8.0327 | 6.9755 | 5.8684 | 1.0755 | -1.5 | -2.1806
|  | WINTON PRIMARY | CF |  |  |  |  | 4.8204 | 4.5908 | 11.5112 | 11.1959 | 11.2102 | 10.8235 | 10.3561 | 9.8673 | 9.3561 | 5.8102 | 1.5429 | -2.4837 | 9.0112 | 8.7357 | 16.8051 | 16.3867 | 16.2265 | 15.6837 | 15.0398 | 14.3531 | 13.6204 | 8.4041 | -0.0020408 | -14.9888 | 3.9194 | 3.6786 | 11.3816 | 11.049 | 11.1051 | 10.7276 | 10.2673 | 9.7745 | 9.2633 | 5.7969 | 2.0449 | -1.3398
COWLEY GSP | WITNEY BSP | WITNEY TOWN PRIMARY | MINIMUM HEADROOM | SP 35844 09625 | NO | NO | 3.563 | 16.8305 | 16.5182 | 15.9009 | 15.0438 | 13.8305 | 12.1142 | 10.3509 | 8.4744 | 6.9305 | 1.3356 | -2.8838 | -5.3573 | 21.1989 | 20.9744 | 20.5346 | 19.8917 | 19.0499 | 17.9642 | 16.7825 | 15.5254 | 14.5468 | 10.5213 | 6.2264 | -4.5756 | 17.1989 | 16.9142 | 16.3152 | 15.4876 | 14.3733 | 12.8295 | 11.204 | 9.4948 | 8.1774 | 3.5305 | -0.10216 | -2.1603
|  | WITNEY TOWN PRIMARY | EE |  |  |  |  | 16.8305 | 16.5182 | 15.9009 | 15.0438 | 13.8305 | 12.1142 | 10.3509 | 8.4744 | 6.9305 | 1.5376 | -2.0338 | -4.9328 | 21.1989 | 20.9744 | 20.5346 | 19.8917 | 19.0499 | 17.9642 | 16.7825 | 15.5254 | 14.5468 | 10.5213 | 6.7468 | 1.0152 | 17.1989 | 16.9142 | 16.3152 | 15.4876 | 14.3733 | 12.8295 | 11.204 | 9.4948 | 8.1774 | 3.5764 | 0.63457 | -1.8307
|  | WITNEY TOWN PRIMARY | HT |  |  |  |  | 17.1682 | 16.7111 | 16.1101 | 15.2458 | 14.3366 | 12.5907 | 10.8938 | 9.2172 | 7.5733 | 1.3356 | -2.8838 | -5.3573 | 21.5611 | 21.3019 | 20.957 | 20.4754 | 20.0509 | 19.1856 | 18.3142 | 17.3876 | 16.4438 | 12.8693 | 10.8427 | 9.7917 | 17.5407 | 17.1182 | 16.5713 | 15.8091 | 15.0733 | 13.5846 | 12.1182 | 10.6642 | 9.206 | 3.5305 | -0.10216 | -2.1603
|  | WITNEY TOWN PRIMARY | HE |  |  |  |  | 17.206 | 16.7856 | 16.254 | 15.4948 | 14.7468 | 13.3315 | 11.8825 | 10.3009 | 8.7611 | 3.1427 | -0.57461 | -2.4083 | 21.4642 | 21.154 | 20.7744 | 20.2642 | 19.8254 | 18.9907 | 18.107 | 17.1009 | 16.0489 | 11.4305 | 7.4509 | 2.1182 | 17.5693 | 17.1754 | 16.6866 | 16.0101 | 15.407 | 14.1866 | 12.9325 | 11.555 | 10.1907 | 5.1152 | 1.9938 | 0.44988
|  | WITNEY TOWN PRIMARY | CF |  |  |  |  | 17.5978 | 17.3203 | 17.0723 | 16.6417 | 16.0611 | 15.7458 | 15.1284 | 14.4591 | 13.7264 | 7.8631 | 4.1836 | 0.66824 | 21.6438 | 21.3887 | 21.1376 | 20.7652 | 20.2795 | 19.9591 | 19.3887 | 18.7682 | 18.0427 | 12.5917 | 6.2264 | -4.5756 | 17.9274 | 17.6652 | 17.4325 | 17.0448 | 16.5336 | 16.307 | 15.7591 | 15.1356 | 14.4601 | 9.2795 | 5.954 | 2.9417
FLEET-BRAMLEY GSP | WOKINGHAM BSP | WOKINGHAM PRIMARY | MINIMUM HEADROOM | SU 79589 67665 | NO | NO | 1.804 | 19.1306 | 18.7908 | 18.3704 | 18.2643 | 17.8469 | 17.1684 | 16.4102 | 15.6643 | 15.1122 | 11.8347 | 9.6092 | 8.4133 | 21.549 | 21.3633 | 21.0102 | 20.9704 | 20.6276 | 20.1714 | 19.6398 | 19.1061 | 18.7469 | 16.6439 | 13.9592 | 7.5061 | 18.7663 | 18.4439 | 18.0245 | 17.9612 | 17.5694 | 16.9408 | 16.2378 | 15.5296 | 15.0408 | 12.151 | 10.1857 | 9.1
|  | WOKINGHAM PRIMARY | EE |  |  |  |  | 19.1306 | 18.7908 | 18.3704 | 18.2643 | 17.8469 | 17.1684 | 16.4102 | 15.6643 | 15.1122 | 12.2673 | 10.2214 | 8.6918 | 21.549 | 21.3633 | 21.0102 | 20.9704 | 20.6276 | 20.1714 | 19.6398 | 19.1061 | 18.7469 | 16.6439 | 14.3551 | 10.9806 | 18.7663 | 18.4439 | 18.0245 | 17.9612 | 17.5694 | 16.9408 | 16.2378 | 15.5296 | 15.0408 | 12.4908 | 10.7031 | 9.3194
|  | WOKINGHAM PRIMARY | HT |  |  |  |  | 19.3 | 19.0071 | 18.6878 | 18.3235 | 17.9112 | 17.2082 | 16.8388 | 16.1276 | 15.4051 | 11.8347 | 9.6092 | 8.4133 | 21.6969 | 21.5561 | 21.3929 | 21.201 | 20.9776 | 20.6041 | 20.4673 | 20.1337 | 19.7622 | 17.8949 | 16.8847 | 16.3786 | 18.9429 | 18.6714 | 18.3816 | 18.0429 | 17.6602 | 17.0184 | 16.7071 | 16.0561 | 15.3959 | 12.151 | 10.1857 | 9.1
|  | WOKINGHAM PRIMARY | HE |  |  |  |  | 19.3847 | 19.1 | 18.8255 | 18.499 | 18.1276 | 17.5704 | 17.352 | 16.7939 | 16.2224 | 13.2714 | 11.2704 | 10.2531 | 21.7 | 21.551 | 21.3908 | 21.151 | 20.8429 | 20.4459 | 20.3878 | 19.9796 | 19.5531 | 17.1439 | 14.849 | 11.6653 | 19.0173 | 18.75 | 18.4949 | 18.1898 | 17.8429 | 17.3265 | 17.151 | 16.6337 | 16.1041 | 13.4102 | 11.65 | 10.7296
|  | WOKINGHAM PRIMARY | CF |  |  |  |  | 19.5827 | 19.4327 | 19.2357 | 19.0622 | 18.8316 | 18.5816 | 18.2898 | 18.3561 | 18.102 | 16.1235 | 13.9551 | 11.9837 | 21.8327 | 21.752 | 21.5663 | 21.3857 | 21.1286 | 20.8327 | 20.4806 | 20.4776 | 20.1459 | 17.7235 | 13.9592 | 7.5061 | 19.1939 | 19.0551 | 18.8704 | 18.7122 | 18.4918 | 18.2214 | 17.9 | 18.0633 | 17.8163 | 15.9327 | 14.0092 | 12.2541
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | WOODCOTE PRIMARY | MINIMUM HEADROOM | SU 64425 81624 | YES | NO | 1.329 | 3.4702 | 3.3997 | 3.3212 | 3.2008 | 3.0753 | 2.9222 | 2.7038 | 2.4865 | 2.361 | 1.6681 | 1.1855 | 0.91097 | 3.826 | 3.7464 | 3.6832 | 3.5883 | 3.4852 | 3.3821 | 3.2219 | 3.0648 | 2.977 | 2.5128 | 1.8679 | 0.48112 | 3.3837 | 3.2949 | 3.2245 | 3.1163 | 3.0051 | 2.8612 | 2.6653 | 2.4663 | 2.351 | 1.7031 | 1.2561 | 1.0041
|  | WOODCOTE PRIMARY | EE |  |  |  |  | 3.4702 | 3.3997 | 3.3212 | 3.2008 | 3.0753 | 2.9222 | 2.7038 | 2.4865 | 2.361 | 1.7406 | 1.2977 | 0.97628 | 3.826 | 3.7464 | 3.6832 | 3.5883 | 3.4852 | 3.3821 | 3.2219 | 3.0648 | 2.977 | 2.5128 | 2.0097 | 1.2699 | 3.3837 | 3.2949 | 3.2245 | 3.1163 | 3.0051 | 2.8612 | 2.6653 | 2.4663 | 2.351 | 1.7694 | 1.3582 | 1.0633
|  | WOODCOTE PRIMARY | HT |  |  |  |  | 3.511 | 3.4691 | 3.4069 | 3.3202 | 3.2181 | 3.0824 | 2.8936 | 2.6997 | 2.5467 | 1.6681 | 1.1855 | 0.91097 | 3.8923 | 3.8485 | 3.7913 | 3.7342 | 3.6628 | 3.5964 | 3.4821 | 3.3648 | 3.2821 | 2.7913 | 2.5719 | 2.4474 | 3.4378 | 3.3776 | 3.2969 | 3.2204 | 3.1286 | 3.0031 | 2.8337 | 2.6571 | 2.5102 | 1.7031 | 1.2561 | 1.0041
|  | WOODCOTE PRIMARY | HE |  |  |  |  | 3.512 | 3.4712 | 3.4191 | 3.3436 | 3.2497 | 3.1446 | 2.9885 | 2.8232 | 2.7008 | 1.9151 | 1.4691 | 1.2477 | 3.8791 | 3.8311 | 3.7668 | 3.7015 | 3.623 | 3.5515 | 3.4352 | 3.3117 | 3.2189 | 2.5883 | 2.076 | 1.374 | 3.4459 | 3.3888 | 3.3163 | 3.2429 | 3.1592 | 3.0633 | 2.9214 | 2.7704 | 2.6561 | 1.9398 | 1.5276 | 1.3235
|  | WOODCOTE PRIMARY | CF |  |  |  |  | 3.5538 | 3.5253 | 3.5018 | 3.4691 | 3.4151 | 3.3416 | 3.2987 | 3.211 | 3.1202 | 2.5691 | 2.0518 | 1.6242 | 3.9066 | 3.8505 | 3.8148 | 3.7628 | 3.6974 | 3.6199 | 3.5607 | 3.4668 | 3.3658 | 2.7352 | 1.8679 | 0.48112 | 3.4929 | 3.4439 | 3.4133 | 3.3663 | 3.3102 | 3.2459 | 3.2061 | 3.1306 | 3.048 | 2.5367 | 2.0714 | 1.6684
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WOODMILL LANE PRIMARY | MINIMUM HEADROOM | SU 43733 15470 | NO | NO | 3.086 | 11.4655 | 11.1134 | 10.6726 | 10.1808 | 9.6165 | 9.4104 | 8.6706 | 7.9277 | 7.3777 | 4.3991 | 1.7767 | 0.23893 | 14.2277 | 13.9165 | 13.5389 | 13.1093 | 12.6073 | 12.3624 | 11.7553 | 11.1379 | 10.6532 | 7.79 | 3.3573 | -7.3386 | 11.8348 | 11.5002 | 11.0767 | 10.6042 | 10.0593 | 9.8889 | 9.1879 | 8.4879 | 7.9828 | 5.4002 | 3.1991 | 1.8746
|  | WOODMILL LANE PRIMARY | EE |  |  |  |  | 11.4655 | 11.1134 | 10.6726 | 10.1808 | 9.6165 | 9.4104 | 8.6706 | 7.9277 | 7.3777 | 4.3991 | 2.1889 | 0.40322 | 14.2277 | 13.9165 | 13.5389 | 13.1093 | 12.6073 | 12.3624 | 11.7553 | 11.1379 | 10.6532 | 7.79 | 4.4522 | -1.0845 | 11.8348 | 11.5002 | 11.0767 | 10.6042 | 10.0593 | 9.8889 | 9.1879 | 8.4879 | 7.9828 | 5.4002 | 3.5318 | 1.9736
|  | WOODMILL LANE PRIMARY | HT |  |  |  |  | 11.7481 | 11.4971 | 11.1695 | 10.792 | 10.4593 | 9.8787 | 9.2236 | 8.9042 | 8.2461 | 4.4951 | 1.7767 | 0.23893 | 14.5338 | 14.3624 | 14.1389 | 13.8655 | 13.6257 | 13.2695 | 12.8583 | 12.7308 | 12.3318 | 10.2512 | 8.9522 | 8.2961 | 12.1216 | 11.8889 | 11.5818 | 11.2277 | 10.9144 | 10.3787 | 9.7685 | 9.5114 | 8.9042 | 5.5685 | 3.1991 | 1.8746
|  | WOODMILL LANE PRIMARY | HE |  |  |  |  | 11.7532 | 11.5206 | 11.2236 | 10.9032 | 10.5787 | 10.0481 | 9.4736 | 8.8726 | 8.6665 | 5.6951 | 3.6144 | 2.6451 | 14.44 | 14.2175 | 13.9471 | 13.644 | 13.3185 | 12.8767 | 12.393 | 11.8685 | 11.6777 | 8.6563 | 5.3267 | 0.090971 | 12.1236 | 11.9053 | 11.6246 | 11.3246 | 11.0195 | 10.5308 | 9.992 | 9.4257 | 9.2889 | 6.6451 | 4.8736 | 4.0675
|  | WOODMILL LANE PRIMARY | CF |  |  |  |  | 11.9481 | 11.7828 | 11.64 | 11.4502 | 11.244 | 11.0083 | 10.7716 | 10.4726 | 10.1644 | 8.7644 | 6.7879 | 4.8451 | 14.5369 | 14.3359 | 14.142 | 13.8879 | 13.5879 | 13.2226 | 12.8379 | 12.39 | 11.9155 | 8.9246 | 3.3573 | -7.3386 | 12.3053 | 12.1451 | 12.0093 | 11.8277 | 11.6287 | 11.4042 | 11.1818 | 10.8971 | 10.6002 | 9.3063 | 7.5542 | 5.9216
COWLEY GSP | YARNTON BSP | WOODSTOCK PRIMARY | MINIMUM HEADROOM | SP 44795 17462 | NO | YES | 1.705 | 5.937 | 5.6564 | 5.3074 | 4.9217 | 4.4513 | 3.9105 | 3.735 | 3.3544 | 3.0768 | 1.5268 | 0.1462 | -0.74665 | 7.6758 | 7.4901 | 7.2513 | 7.0115 | 6.7013 | 6.3472 | 6.2829 | 5.9982 | 5.7972 | 4.687 | 3.3166 | -0.25686 | 5.6809 | 5.4289 | 5.1013 | 4.7605 | 4.3248 | 3.8187 | 3.7717 | 3.4054 | 3.1493 | 1.7829 | 0.61049 | -0.1038
|  | WOODSTOCK PRIMARY | EE |  |  |  |  | 5.937 | 5.6564 | 5.3074 | 4.9217 | 4.4513 | 3.9105 | 3.735 | 3.3544 | 3.0768 | 1.5768 | 0.39416 | -0.58645 | 7.6758 | 7.4901 | 7.2513 | 7.0115 | 6.7013 | 6.3472 | 6.2829 | 5.9982 | 5.7972 | 4.687 | 3.4809 | 1.5472 | 5.6809 | 5.4289 | 5.1013 | 4.7605 | 4.3248 | 3.8187 | 3.7717 | 3.4054 | 3.1615 | 1.8176 | 0.84008 | 0.033959
|  | WOODSTOCK PRIMARY | HT |  |  |  |  | 6.0952 | 5.8319 | 5.5738 | 5.2074 | 4.7982 | 4.3564 | 3.885 | 3.4993 | 3.1003 | 1.5268 | 0.1462 | -0.74665 | 7.8493 | 7.6982 | 7.5656 | 7.3646 | 7.137 | 6.9125 | 6.6401 | 6.4003 | 6.1493 | 5.4146 | 4.8064 | 4.4472 | 5.8513 | 5.6187 | 5.3982 | 5.0799 | 4.7125 | 4.3421 | 3.9095 | 3.537 | 3.1493 | 1.7829 | 0.61049 | -0.1038
|  | WOODSTOCK PRIMARY | HE |  |  |  |  | 6.0982 | 5.8493 | 5.5993 | 5.2431 | 4.8482 | 4.4615 | 4.0482 | 3.7187 | 3.3799 | 2.0993 | 0.91253 | 0.26559 | 7.8156 | 7.6523 | 7.5013 | 7.2809 | 7.0289 | 6.7982 | 6.5156 | 6.2615 | 5.9891 | 4.9778 | 3.7462 | 1.9329 | 5.8533 | 5.6299 | 5.4187 | 5.1105 | 4.7584 | 4.434 | 4.0493 | 3.7227 | 3.385 | 2.3013 | 1.338 | 0.80743
|  | WOODSTOCK PRIMARY | CF |  |  |  |  | 6.2268 | 6.0421 | 5.8431 | 5.6023 | 5.3064 | 5.0493 | 4.837 | 4.6697 | 4.4891 | 3.6768 | 2.5299 | 1.4074 | 7.8748 | 7.736 | 7.5901 | 7.4319 | 7.2278 | 7.0105 | 6.8187 | 6.6176 | 6.4074 | 5.3003 | 3.3166 | -0.25686 | 5.9615 | 5.7972 | 5.6187 | 5.4187 | 5.1646 | 4.9309 | 4.7472 | 4.5687 | 4.385 | 3.7013 | 2.688 | 1.7136
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON PRIMARY | MINIMUM HEADROOM | SU 44145 11242 | NO | NO | 3.571 | 19.1378 | 18.9582 | 18.7133 | 18.4939 | 18.1173 | 17.6173 | 17.0837 | 16.9776 | 16.652 | 15.0357 | 13.6184 | 12.8602 | 20.4265 | 20.2469 | 20.0102 | 19.7878 | 19.4214 | 18.9929 | 18.5276 | 18.4143 | 18.0949 | 16.2143 | 12.352 | 4.6684 | 19.7316 | 19.5673 | 19.3449 | 19.1296 | 18.7541 | 18.2776 | 17.7571 | 17.7092 | 17.3959 | 15.9245 | 14.6918 | 14.0398
|  | WOOLSTON PRIMARY | EE |  |  |  |  | 19.1378 | 18.9582 | 18.7133 | 18.4939 | 18.1173 | 17.6173 | 17.0837 | 16.9776 | 16.652 | 15.0357 | 13.9 | 12.9918 | 20.4265 | 20.2469 | 20.0102 | 19.7878 | 19.4214 | 18.9929 | 18.5276 | 18.4143 | 18.0949 | 16.2143 | 13.8724 | 9.8827 | 19.7316 | 19.5673 | 19.3449 | 19.1296 | 18.7541 | 18.2776 | 17.7571 | 17.7092 | 17.3959 | 15.9245 | 14.9388 | 14.1459
|  | WOOLSTON PRIMARY | HT |  |  |  |  | 19.3173 | 19.1704 | 18.9908 | 18.7378 | 18.4214 | 18.0378 | 17.6735 | 17.251 | 16.8286 | 15.0469 | 13.6184 | 12.8602 | 20.6459 | 20.5388 | 20.4071 | 20.2 | 19.949 | 19.6949 | 19.4622 | 19.1837 | 18.9031 | 17.9898 | 17.2857 | 16.9296 | 19.8929 | 19.7571 | 19.598 | 19.3561 | 19.0622 | 18.7031 | 18.3592 | 17.9704 | 17.5816 | 15.9612 | 14.6918 | 14.0398
|  | WOOLSTON PRIMARY | HE |  |  |  |  | 19.3173 | 19.1765 | 19.0092 | 18.8684 | 18.5847 | 18.2092 | 17.8735 | 17.4816 | 17.0969 | 15.6449 | 14.4908 | 13.9939 | 20.5786 | 20.4337 | 20.2622 | 20.1041 | 19.8143 | 19.4765 | 19.1633 | 18.7929 | 18.4173 | 16.5847 | 14.1571 | 10.3531 | 19.8918 | 19.7612 | 19.6122 | 19.4857 | 19.2214 | 18.8735 | 18.552 | 18.1878 | 17.8276 | 16.4949 | 15.4816 | 15.0622
|  | WOOLSTON PRIMARY | CF |  |  |  |  | 19.4102 | 19.3337 | 19.2408 | 19.1357 | 19.0531 | 18.8867 | 18.6612 | 18.4878 | 18.2724 | 16.9031 | 16.1276 | 15.0184 | 20.6102 | 20.4918 | 20.351 | 20.1837 | 20.0133 | 19.7388 | 19.398 | 19.0806 | 18.7255 | 16.2316 | 12.352 | 4.6684 | 19.9806 | 19.9133 | 19.8306 | 19.7337 | 19.6592 | 19.5041 | 19.2898 | 19.1143 | 18.898 | 17.5724 | 16.9133 | 15.9316
MINETY GSP | SWINDON BSP | WOOTTON BASSETT PRIMARY | MINIMUM HEADROOM | SU 07587 81123 | NO | NO | 2.167 | 12.169 | 11.7455 | 11.269 | 11.0812 | 10.2128 | 9.222 | 8.0322 | 6.8088 | 5.8741 | 2.2833 | -0.021849 | -1.4841 | 15.271 | 14.921 | 14.5282 | 14.4975 | 13.9965 | 13.3516 | 12.6139 | 11.8465 | 11.2955 | 8.9741 | 6.5251 | 0.26489 | 11.523 | 11.1088 | 10.6251 | 10.521 | 9.7986 | 8.8618 | 7.7924 | 6.6965 | 5.8812 | 2.7302 | 0.58733 | -0.63307
|  | WOOTTON BASSETT PRIMARY | EE |  |  |  |  | 12.169 | 11.7455 | 11.269 | 11.0812 | 10.2955 | 9.222 | 8.0322 | 6.8088 | 5.8741 | 2.5098 | 0.51284 | -1.1341 | 15.271 | 14.921 | 14.5282 | 14.4975 | 13.9965 | 13.3516 | 12.6139 | 11.8465 | 11.2955 | 8.9741 | 6.7404 | 3.4475 | 11.523 | 11.1088 | 10.6251 | 10.521 | 9.819 | 8.8618 | 7.7924 | 6.6965 | 5.8812 | 2.92 | 1.0669 | -0.34226
|  | WOOTTON BASSETT PRIMARY | HT |  |  |  |  | 12.4169 | 12.0884 | 11.7475 | 11.1424 | 10.2128 | 9.3863 | 8.3394 | 7.3547 | 6.4149 | 2.2833 | -0.021849 | -1.4841 | 15.569 | 15.3475 | 15.1353 | 14.7782 | 14.271 | 13.9833 | 13.4353 | 12.8975 | 12.3782 | 10.1679 | 9.0475 | 8.421 | 11.7782 | 11.4679 | 11.1537 | 10.6128 | 9.7986 | 9.1241 | 8.1996 | 7.3179 | 6.473 | 2.7302 | 0.58733 | -0.63307
|  | WOOTTON BASSETT PRIMARY | HE |  |  |  |  | 12.4486 | 12.1424 | 11.8455 | 11.3557 | 10.6179 | 10.0639 | 9.0853 | 8.0843 | 7.1118 | 3.3955 | 1.3312 | 0.22713 | 15.522 | 15.2782 | 15.0557 | 14.7088 | 14.2424 | 14.0057 | 13.42 | 12.8047 | 12.1853 | 9.4343 | 7.1118 | 4.0016 | 11.8026 | 11.5139 | 11.2394 | 10.7935 | 10.1394 | 9.6945 | 8.8333 | 7.9496 | 7.0863 | 3.7343 | 1.8241 | 0.86999
|  | WOOTTON BASSETT PRIMARY | CF |  |  |  |  | 12.6261 | 12.4628 | 12.2588 | 12.0873 | 11.8455 | 11.5669 | 11.1404 | 11.0741 | 10.4904 | 6.4965 | 4.1404 | 1.9986 | 15.5945 | 15.4322 | 15.2251 | 15.0435 | 14.7884 | 14.4863 | 14.0802 | 14.0302 | 13.5526 | 10.2435 | 6.5251 | 0.26489 | 11.9659 | 11.8118 | 11.6139 | 11.4465 | 11.2016 | 10.9179 | 10.5026 | 10.5373 | 10.0241 | 6.5118 | 4.3853 | 2.4822
COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD PRIMARY | MINIMUM HEADROOM | SU 49244 98269 | NO | YES | 3.827 | -2.4759 | -3.3453 | -3.7881 | -4.731 | -5.8116 | -7.4524 | -9.3463 | -11.2341 | -12.7932 | -20.9728 | -27.182 | -29.229 | 1.43 | 0.82084 | 0.58819 | -0.046502 | -0.76181 | -1.7465 | -2.9016 | -4.0659 | -4.9465 | -9.6516 | -14.5455 | -23.9322 | -1.5673 | -2.3785 | -2.7092 | -3.5643 | -4.5418 | -5.9847 | -7.6581 | -9.3275 | -10.6285 | -17.4959 | -22.7398 | -24.5112
|  | WOOTTON ROAD PRIMARY | EE |  |  |  |  | -2.4759 | -3.3453 | -3.7881 | -4.731 | -5.8116 | -7.4524 | -9.3463 | -11.2341 | -12.7932 | -20.683 | -26.4657 | -28.9575 | 1.43 | 0.82084 | 0.58819 | -0.046502 | -0.76181 | -1.7465 | -2.9016 | -4.0659 | -4.9465 | -9.6516 | -14.172 | -19.0751 | -1.5673 | -2.3785 | -2.7092 | -3.5643 | -4.5418 | -5.9847 | -7.6581 | -9.3275 | -10.6285 | -17.2336 | -22.1183 | -24.303
|  | WOOTTON ROAD PRIMARY | HT |  |  |  |  | -2.131 | -2.8392 | -3.5616 | -4.4504 | -5.0881 | -6.6085 | -8.3392 | -10.1065 | -11.9157 | -20.9728 | -27.182 | -29.229 | 1.8484 | 1.4525 | 1.0229 | 0.50656 | 0.28411 | -0.46997 | -1.3516 | -2.2649 | -3.2118 | -7.7302 | -10.4914 | -11.3975 | -1.1826 | -1.802 | -2.4592 | -3.2581 | -3.7234 | -5.0183 | -6.4959 | -8.0163 | -9.5867 | -17.4959 | -22.7398 | -24.5112
|  | WOOTTON ROAD PRIMARY | HE |  |  |  |  | -2.1055 | -2.7861 | -3.4841 | -4.3524 | -4.9667 | -6.3279 | -7.9075 | -9.5279 | -11.1769 | -19.633 | -25.6187 | -27.2341 | 1.7525 | 1.3127 | 0.83105 | 0.25758 | -0.032216 | -0.82201 | -1.7547 | -2.7353 | -3.7567 | -9.2475 | -14.0138 | -18.57 | -1.1653 | -1.7663 | -2.4051 | -3.1816 | -3.6296 | -4.7938 | -6.151 | -7.549 | -8.9796 | -16.299 | -21.4112 | -22.7969
|  | WOOTTON ROAD PRIMARY | CF |  |  |  |  | -1.7187 | -2.233 | -2.6677 | -3.279 | -3.9912 | -4.5126 | -5.532 | -6.5922 | -7.679 | -14.3994 | -20.4994 | -24.0381 | 1.9402 | 1.5494 | 1.2086 | 0.75554 | 0.21778 | -0.10058 | -0.83732 | -1.6128 | -2.4281 | -7.7475 | -14.5455 | -23.9322 | -0.82038 | -1.2806 | -1.6683 | -2.2112 | -2.8469 | -3.1887 | -4.0551 | -4.9592 | -5.8918 | -11.6612 | -16.751 | -20.0051
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | WRECCLESHAM PRIMARY | MINIMUM HEADROOM | SU 82093 44312 | NO | NO | 2.799 | 15.9747 | 15.5451 | 15.0859 | 15.0614 | 14.5971 | 13.8941 | 13.1094 | 12.3094 | 11.7676 | 8.4829 | 5.8165 | 4.24 | 19.9022 | 19.5829 | 19.238 | 19.1798 | 18.8063 | 18.3369 | 17.8002 | 17.2451 | 16.8604 | 14.592 | 11.741 | 5.0278 | 15.8706 | 15.4308 | 14.9553 | 15.0237 | 14.5665 | 13.9084 | 13.1676 | 12.4094 | 11.9502 | 9.1369 | 6.8471 | 5.4563
|  | WRECCLESHAM PRIMARY | EE |  |  |  |  | 15.9747 | 15.5451 | 15.0859 | 15.0614 | 14.5971 | 13.8941 | 13.1094 | 12.3094 | 11.7676 | 8.7767 | 6.3665 | 4.5298 | 19.9022 | 19.5829 | 19.238 | 19.1798 | 18.8063 | 18.3369 | 17.8002 | 17.2451 | 16.8604 | 14.592 | 12.0941 | 8.4818 | 15.8706 | 15.4308 | 14.9553 | 15.0237 | 14.5665 | 13.9084 | 13.1676 | 12.4094 | 11.9502 | 9.3778 | 7.3308 | 5.6982
|  | WRECCLESHAM PRIMARY | HT |  |  |  |  | 16.2247 | 15.8706 | 15.5808 | 15.2063 | 14.7645 | 14.4778 | 13.7778 | 13.0441 | 12.289 | 8.4829 | 5.8165 | 4.24 | 20.1655 | 19.9502 | 19.7706 | 19.5278 | 19.2329 | 19.1359 | 18.7584 | 18.3522 | 17.9339 | 15.9563 | 14.789 | 14.1257 | 16.1594 | 15.8145 | 15.5369 | 15.1635 | 14.7247 | 14.5676 | 13.9247 | 13.2512 | 12.5584 | 9.1369 | 6.8471 | 5.4563
|  | WRECCLESHAM PRIMARY | HE |  |  |  |  | 16.2482 | 15.9278 | 15.6563 | 15.3012 | 14.8859 | 14.7349 | 14.1829 | 13.5931 | 12.9818 | 9.7492 | 7.4237 | 6.2431 | 20.0971 | 19.8563 | 19.641 | 19.3553 | 19.0206 | 18.9196 | 18.5298 | 18.1022 | 17.6512 | 15.0522 | 12.5502 | 9.1941 | 16.1757 | 15.8584 | 15.5961 | 15.239 | 14.8237 | 14.7982 | 14.2829 | 13.7329 | 13.1635 | 10.2278 | 8.2706 | 7.242
|  | WRECCLESHAM PRIMARY | CF |  |  |  |  | 16.4482 | 16.2573 | 16.1094 | 15.89 | 15.6278 | 15.3614 | 15.4624 | 15.1971 | 14.9206 | 12.8227 | 10.5808 | 8.442 | 20.19 | 20.0094 | 19.8369 | 19.6145 | 19.3257 | 19.0278 | 18.9655 | 18.638 | 18.2941 | 15.7318 | 11.741 | 5.0278 | 16.3584 | 16.1604 | 16.0012 | 15.7737 | 15.5002 | 15.2247 | 15.3931 | 15.1267 | 14.8451 | 12.8492 | 10.9298 | 9.092
MINETY GSP | TOOTHILL BSP | WROUGHTON PRIMARY | MINIMUM HEADROOM | SU 14446 81504 | NO | NO | 4.447 | 11.4522 | 10.5767 | 9.8124 | 8.9797 | 8.0257 | 7.0042 | 5.9777 | 5.1226 | 4.6348 | 1.6257 | -0.26515 | -1.4141 | 14.3991 | 13.8542 | 13.4512 | 13.0022 | 12.4348 | 11.8634 | 11.0216 | 10.3053 | 9.6491 | 7.4267 | 5.691 | 3.2369 | 12.0614 | 11.293 | 10.6573 | 9.9542 | 9.1155 | 8.1471 | 7.1002 | 6.2216 | 5.7308 | 2.7665 | 0.9226 | -0.20801
|  | WROUGHTON PRIMARY | EE |  |  |  |  | 11.4522 | 10.5767 | 9.8124 | 8.9797 | 8.0257 | 7.2644 | 6.292 | 5.4369 | 4.6869 | 2.0665 | 0.48587 | -0.76311 | 14.3991 | 13.8542 | 13.4512 | 13.0022 | 12.4348 | 11.8889 | 11.0512 | 10.3053 | 9.6491 | 7.4267 | 5.691 | 3.3318 | 12.0614 | 11.293 | 10.6573 | 9.9542 | 9.1155 | 8.4134 | 7.4155 | 6.5328 | 5.7716 | 3.2328 | 1.7512 | 0.53791
|  | WROUGHTON PRIMARY | HT |  |  |  |  | 11.5522 | 10.7093 | 9.9757 | 9.0563 | 8.1022 | 7.0042 | 5.9777 | 5.1226 | 4.6348 | 1.6257 | -0.26515 | -1.4141 | 14.5348 | 14.0471 | 13.7063 | 13.2042 | 12.6746 | 11.8634 | 11.0216 | 10.3328 | 9.94 | 7.8032 | 6.4971 | 5.642 | 12.1787 | 11.4512 | 10.8644 | 10.0634 | 9.2155 | 8.1471 | 7.1002 | 6.2216 | 5.7308 | 2.7665 | 0.9226 | -0.20801
|  | WROUGHTON PRIMARY | HE |  |  |  |  | 11.5777 | 10.7471 | 10.0287 | 9.2553 | 8.4032 | 7.5236 | 6.6777 | 5.99 | 5.6246 | 3.0277 | 1.4328 | 0.4022 | 14.5093 | 14.0042 | 13.6502 | 13.2563 | 12.7787 | 12.14 | 11.4257 | 10.8502 | 10.5073 | 8.2093 | 6.44 | 4.1593 | 12.1971 | 11.4797 | 10.9053 | 10.2675 | 9.5226 | 8.69 | 7.841 | 7.1532 | 6.793 | 4.2553 | 2.7512 | 1.7277
|  | WROUGHTON PRIMARY | CF |  |  |  |  | 11.7369 | 11.0318 | 10.4471 | 9.8277 | 9.2216 | 8.6726 | 8.1308 | 7.6165 | 7.1216 | 5.2604 | 3.8369 | 2.5277 | 14.5746 | 14.1226 | 13.8155 | 13.4787 | 13.142 | 12.7012 | 12.1675 | 11.641 | 11.1308 | 9.0838 | 6.8593 | 3.2369 | 12.3379 | 11.7277 | 11.2695 | 10.7685 | 10.2726 | 9.7695 | 9.2114 | 8.6746 | 8.1604 | 6.3512 | 5.0818 | 3.9379
AMERSHAM GSP | LOUDWATER BSP | WYCOMBE MARSH PRIMARY | MINIMUM HEADROOM | SU 88582 91845 | NO | YES | 4.443 | 9.3956 | 8.8262 | 8.3058 | 7.7843 | 7.6098 | 6.9425 | 6.1864 | 5.4262 | 4.8547 | 1.869 | -0.52078 | -1.7493 | 14.3507 | 13.9588 | 13.5649 | 13.1445 | 13.0435 | 12.5649 | 12.0017 | 11.4241 | 11.0098 | 8.7935 | 6.2302 | -0.37078 | 11.6027 | 11.0802 | 10.5711 | 10.0384 | 9.9598 | 9.3262 | 8.6027 | 7.8711 | 7.3547 | 4.8353 | 2.7782 | 1.6833
|  | WYCOMBE MARSH PRIMARY | EE |  |  |  |  | 9.3956 | 8.8262 | 8.3058 | 7.7843 | 7.6098 | 6.9425 | 6.1864 | 5.4262 | 4.8547 | 1.9578 | -0.014653 | -1.5647 | 14.3507 | 13.9588 | 13.5649 | 13.1445 | 13.0435 | 12.5649 | 12.0017 | 11.4241 | 11.0098 | 8.7935 | 6.4772 | 3.0129 | 11.6027 | 11.0802 | 10.5711 | 10.0384 | 9.9598 | 9.3262 | 8.6027 | 7.8711 | 7.3547 | 4.8558 | 3.2262 | 1.8404
|  | WYCOMBE MARSH PRIMARY | HT |  |  |  |  | 9.6068 | 9.1313 | 8.7241 | 8.3639 | 7.9384 | 7.3109 | 6.6129 | 6.27 | 5.5813 | 1.869 | -0.52078 | -1.7493 | 14.617 | 14.3445 | 14.0966 | 13.8751 | 13.5935 | 13.2221 | 12.7935 | 12.6996 | 12.2864 | 10.2507 | 9.1017 | 8.5823 | 11.8762 | 11.4496 | 11.0588 | 10.7251 | 10.3129 | 9.7282 | 9.068 | 8.8231 | 8.1853 | 4.8353 | 2.7782 | 1.6833
|  | WYCOMBE MARSH PRIMARY | HE |  |  |  |  | 9.6241 | 9.1649 | 8.7853 | 8.4527 | 8.0568 | 7.5333 | 6.9394 | 6.6956 | 6.117 | 3.0466 | 0.99249 | 0.10473 | 14.5598 | 14.2558 | 13.9813 | 13.7282 | 13.4221 | 13.0374 | 12.5813 | 12.4415 | 11.9976 | 9.4445 | 7.0262 | 3.8741 | 11.8884 | 11.4813 | 11.1149 | 10.8047 | 10.4231 | 9.9302 | 9.3578 | 9.2027 | 8.6619 | 5.8823 | 4.1364 | 3.3935
|  | WYCOMBE MARSH PRIMARY | CF |  |  |  |  | 9.8568 | 9.5017 | 9.2843 | 9.0547 | 8.8456 | 8.6343 | 8.3649 | 8.0639 | 7.7292 | 6.0813 | 3.9323 | 1.9517 | 14.6731 | 14.4007 | 14.2078 | 13.9853 | 13.7629 | 13.4925 | 13.1547 | 12.7874 | 12.3904 | 10.1486 | 6.2302 | -0.37078 | 12.1058 | 11.7731 | 11.566 | 11.3333 | 11.1374 | 10.9129 | 10.6272 | 10.3098 | 9.9731 | 8.5139 | 6.6078 | 4.9221
LOVEDEAN GSP | WYMERING BSP | WYMERING PRIMARY | MINIMUM HEADROOM | SU 64974 05375 | NO | YES | 14.319 | 24.6149 | 23.6088 | 22.1139 | 20.4282 | 18.52 | 16.3251 | 13.7302 | 11.2465 | 9.1782 | -2.2657 | -7.0831 | -7.8606 | 23.8904 | 23.2302 | 22.1026 | 20.8108 | 19.3945 | 17.821 | 15.9414 | 14.1424 | 12.6669 | 3.7526 | 0.10264 | -6.9504 | 23.9853 | 23.0404 | 21.6057 | 19.9863 | 18.1649 | 16.0792 | 13.6077 | 11.2455 | 9.2812 | -1.7178 | -6.3178 | -7.0474
|  | WYMERING PRIMARY | EE |  |  |  |  | 24.6149 | 23.6088 | 22.1139 | 20.4282 | 18.52 | 16.3251 | 13.7302 | 11.2465 | 9.1782 | 1.7077 | -0.057563 | -0.17491 | 23.8904 | 23.2302 | 22.1026 | 20.8108 | 19.3945 | 17.821 | 15.9414 | 14.1424 | 12.6669 | 6.9914 | 5.769 | 1.0863 | 23.9853 | 23.0404 | 21.6057 | 19.9863 | 18.1649 | 16.0792 | 13.6077 | 11.2455 | 9.2812 | 2.2241 | 0.62509 | 0.5057
|  | WYMERING PRIMARY | HT |  |  |  |  | 25.5404 | 24.8506 | 24.0506 | 22.9914 | 22.0322 | 20.5047 | 18.6812 | 16.7516 | 14.6486 | 5.3465 | 1.4486 | 0.70672 | 24.6282 | 24.1955 | 23.6945 | 23.0843 | 22.2251 | 21.1782 | 19.8986 | 18.5404 | 16.9506 | 10.0384 | 7.3016 | 6.6598 | 24.8608 | 24.2649 | 23.5792 | 22.7077 | 21.5802 | 20.1343 | 18.4037 | 16.5741 | 14.5659 | 5.721 | 2.0639 | 1.3822
|  | WYMERING PRIMARY | HE |  |  |  |  | 25.3863 | 24.569 | 23.2557 | 21.7343 | 20.0924 | 18.1077 | 15.6782 | 13.0965 | 10.4067 | -2.2657 | -7.0831 | -7.8606 | 24.3506 | 23.7496 | 22.9802 | 21.8118 | 20.5986 | 19.1669 | 17.3904 | 15.4986 | 13.52 | 3.7526 | 0.10264 | -0.79226 | 24.5455 | 23.8394 | 22.7098 | 21.2486 | 19.6822 | 17.7904 | 15.469 | 12.9986 | 10.422 | -1.7178 | -6.3178 | -7.0474
|  | WYMERING PRIMARY | CF |  |  |  |  | 26.0343 | 25.5271 | 25.0761 | 24.4863 | 23.6373 | 22.7853 | 21.521 | 20.119 | 18.6271 | 10.0955 | 1.6486 | -2.5882 | 24.7822 | 24.3679 | 23.9679 | 23.4373 | 22.8526 | 22.3782 | 21.5526 | 20.4904 | 19.3639 | 12.9455 | 5.2904 | -6.9504 | 25.1975 | 24.7547 | 24.3098 | 23.7363 | 23.069 | 22.2618 | 21.0496 | 19.7037 | 18.2761 | 10.0812 | 2.0333 | -1.9494
COWLEY GSP | YARNTON BSP | YARNTON PRIMARY | MINIMUM HEADROOM | SP 48277 12108 | NO | YES | 43.367 | -15.0915 | -16.3741 | -17.6986 | -19.3333 | -21.1649 | -23.17 | -25.5721 | -27.8466 | -29.7068 | -40.5139 | -45.6364 | -46.8384 | -8.6639 | -9.618 | -10.5996 | -11.8241 | -13.1955 | -14.6629 | -16.4333 | -18.1119 | -19.4649 | -27.4598 | -31.0996 | -32.0343 | -14.7731 | -16.0068 | -17.2741 | -18.8476 | -20.6017 | -22.519 | -24.8221 | -27.0037 | -28.7802 | -39.1333 | -43.9772 | -45.069
|  | YARNTON PRIMARY | EE |  |  |  |  | -15.0915 | -16.3741 | -17.6986 | -19.3333 | -21.1649 | -23.17 | -25.5721 | -27.8466 | -29.7068 | -35.8098 | -37.4915 | -38.6088 | -8.6639 | -9.618 | -10.5996 | -11.8241 | -13.1955 | -14.6629 | -16.4333 | -18.1119 | -19.4649 | -23.6619 | -24.5996 | -26.6874 | -14.7731 | -16.0068 | -17.2741 | -18.8476 | -20.6017 | -22.519 | -24.8221 | -27.0037 | -28.7802 | -34.5435 | -36.0517 | -36.9517
|  | YARNTON PRIMARY | HT |  |  |  |  | -13.6221 | -14.4098 | -15.3323 | -16.3884 | -17.5088 | -18.9006 | -20.5843 | -22.3557 | -24.1884 | -32.3272 | -36.2068 | -37.9302 | -7.5129 | -8.0772 | -8.7476 | -9.52 | -10.3241 | -11.3037 | -12.5047 | -13.7772 | -15.0904 | -20.8057 | -23.2455 | -23.9506 | -13.6251 | -14.266 | -15.0108 | -15.9966 | -17.0568 | -18.3802 | -19.9833 | -21.6762 | -23.4231 | -31.1588 | -34.6588 | -36.0374
|  | YARNTON PRIMARY | HE |  |  |  |  | -14.2231 | -15.3088 | -16.5904 | -18.0782 | -19.7108 | -21.5894 | -23.9108 | -26.3782 | -28.9486 | -40.5139 | -45.6364 | -46.8384 | -7.9915 | -8.7925 | -9.7445 | -10.8557 | -12.0649 | -13.4496 | -15.1741 | -17.0108 | -18.9302 | -27.4598 | -31.0996 | -32.0343 | -13.9557 | -14.9741 | -16.2027 | -17.6364 | -19.1915 | -20.9915 | -23.22 | -25.5864 | -28.0557 | -39.1333 | -43.9772 | -45.069
|  | YARNTON PRIMARY | CF |  |  |  |  | -13.1639 | -13.769 | -14.4537 | -15.2557 | -16.2068 | -16.9762 | -18.1598 | -19.4894 | -20.8915 | -29.2108 | -36.2211 | -39.9762 | -7.216 | -7.669 | -8.1813 | -8.7884 | -9.5006 | -10.0874 | -10.9966 | -12.0149 | -13.0925 | -19.3853 | -24.5966 | -31.9925 | -13.2211 | -13.7078 | -14.1711 | -14.9272 | -15.8343 | -16.5731 | -17.7149 | -18.9955 | -20.3435 | -28.3374 | -35.016 | -38.5262
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | YATTENDON PRIMARY | MINIMUM HEADROOM | SU 53699 74307 | NO | NO | 1.469 | 4.1916 | 3.9335 | 3.5661 | 3.1253 | 1.9682 | 1.1712 | 0.40796 | -1.6431 | -2.7737 | -6.5492 | -10.0859 | -14.2624 | 7.76 | 7.612 | 7.1631 | 6.8182 | 5.5743 | 4.8437 | 4.0896 | 1.7222 | 0.35388 | -3.5053 | -8.0012 | -14.0298 | 4.1865 | 3.9416 | 3.4855 | 3.0498 | 1.7212 | 0.87531 | 0.030408 | -2.4227 | -3.7931 | -7.9471 | -12.1247 | -17.238
|  | YATTENDON PRIMARY | EE |  |  |  |  | 4.1916 | 3.9335 | 3.7059 | 3.3008 | 2.6263 | 2.2467 | 1.8416 | 1.0692 | 0.62327 | -2.0073 | -6.8788 | -8.6839 | 7.76 | 7.6202 | 7.4529 | 7.1876 | 6.5957 | 6.2661 | 5.9876 | 5.2233 | 4.8059 | 2.2437 | -3.9349 | -6.9767 | 4.1865 | 3.9416 | 3.7243 | 3.3559 | 2.6569 | 2.262 | 1.8773 | 1.0304 | 0.5549 | -2.241 | -8.1053 | -10.2471
|  | YATTENDON PRIMARY | HT |  |  |  |  | 4.3141 | 4.0569 | 3.7335 | 3.4008 | 2.4314 | 1.6233 | 0.82224 | 0.36102 | -0.16245 | -3.4145 | -8.1665 | -11.5757 | 7.8416 | 7.6824 | 7.4202 | 7.2447 | 6.2549 | 5.5437 | 4.7824 | 4.4376 | 3.8743 | 0.8049 | -4.5778 | -8.4716 | 4.3365 | 4.0518 | 3.6957 | 3.3967 | 2.2998 | 1.4437 | 0.56 | 0.099796 | -0.50224 | -4.089 | -9.738 | -13.7971
|  | YATTENDON PRIMARY | HE |  |  |  |  | 4.3131 | 4.0161 | 3.5661 | 3.1253 | 1.9682 | 1.1712 | 0.40796 | -1.6431 | -2.7737 | -6.5492 | -10.0859 | -14.2624 | 7.8273 | 7.612 | 7.1631 | 6.8182 | 5.5743 | 4.8437 | 4.0896 | 1.7222 | 0.35388 | -3.5053 | -8.0012 | -14.0298 | 4.3345 | 4.0029 | 3.4855 | 3.0498 | 1.7212 | 0.87531 | 0.030408 | -2.4227 | -3.7931 | -7.9471 | -12.1247 | -17.238
|  | YATTENDON PRIMARY | CF |  |  |  |  | 4.3773 | 4.2345 | 4.111 | 3.7651 | 3.3733 | 2.96 | 2.6304 | 2.2967 | 1.8937 | -0.06551 | -2.6084 | -5.0012 | 7.8804 | 7.8345 | 7.7559 | 7.4753 | 7.1406 | 6.7753 | 6.4508 | 6.109 | 5.6937 | 3.3845 | -0.10837 | -4.4329 | 4.4039 | 4.261 | 4.1437 | 3.8039 | 3.4069 | 2.9967 | 2.6467 | 2.2886 | 1.8569 | -0.30224 | -3.1471 | -5.8094
MELKSHAM GSP | CHIPPENHAM BSP | YATTON KEYNELL PRIMARY | MINIMUM HEADROOM | ST 87300 75782 | YES | YES | 2.114 | -2.0066 | -2.8964 | -3.9464 | -5.1913 | -6.6158 | -8.2434 | -10.2668 | -12.1985 | -14.0832 | -24.224 | -27.7811 | -27.9291 | -0.60918 | -1.2857 | -2.0857 | -3.0378 | -4.1255 | -5.3622 | -6.9 | -8.3704 | -9.8061 | -17.5163 | -20.2133 | -20.3367 | -2.0592 | -2.9173 | -3.9316 | -5.1347 | -6.5112 | -8.0837 | -10.0347 | -11.901 | -13.7214 | -23.5061 | -26.9327 | -27.0684
|  | YATTON KEYNELL PRIMARY | EE |  |  |  |  | -2.0066 | -2.8964 | -3.9464 | -5.1913 | -6.6158 | -8.2434 | -10.2668 | -12.1985 | -14.0832 | -21.4832 | -25.1148 | -26.1015 | -0.60918 | -1.2857 | -2.0857 | -3.0378 | -4.1255 | -5.3622 | -6.9 | -8.3704 | -9.8061 | -15.3949 | -18.1398 | -18.8939 | -2.0592 | -2.9173 | -3.9316 | -5.1347 | -6.5112 | -8.0837 | -10.0347 | -11.901 | -13.7214 | -20.852 | -24.349 | -25.2939
|  | YATTON KEYNELL PRIMARY | HT |  |  |  |  | -0.97908 | -1.577 | -2.3189 | -3.2179 | -4.2872 | -5.5434 | -7.1168 | -8.8026 | -10.6128 | -18.3679 | -22.4821 | -23.9781 | 0.13265 | -0.29184 | -0.83061 | -1.5143 | -2.3286 | -3.2796 | -4.4694 | -5.748 | -7.1235 | -12.9908 | -16.0898 | -17.1959 | -1.152 | -1.6847 | -2.3561 | -3.2245 | -4.2551 | -5.4704 | -6.9867 | -8.6153 | -10.3633 | -17.8378 | -21.802 | -23.2367
|  | YATTON KEYNELL PRIMARY | HE |  |  |  |  | -1.2648 | -2.0546 | -3.0128 | -4.1546 | -5.5464 | -7.1842 | -9.2668 | -11.5087 | -13.7077 | -24.224 | -27.7811 | -27.9291 | -0.080612 | -0.63673 | -1.3684 | -2.2378 | -3.3 | -4.5459 | -6.1337 | -7.8418 | -9.5184 | -17.5163 | -20.2133 | -20.3367 | -1.4082 | -2.1031 | -3.0306 | -4.1306 | -5.4765 | -7.0551 | -9.0673 | -11.2347 | -13.3551 | -23.5061 | -26.9327 | -27.0684
|  | YATTON KEYNELL PRIMARY | CF |  |  |  |  | -0.6648 | -0.89439 | -1.1923 | -1.7352 | -2.3842 | -3.1015 | -4.0934 | -5.225 | -6.425 | -13.6005 | -19.9689 | -23.7464 | 0.56939 | 0.2949 | -0.029592 | -0.4102 | -0.89082 | -1.4367 | -2.1949 | -3.0592 | -3.9786 | -9.4633 | -14.3235 | -17.2214 | -0.68673 | -0.94592 | -1.351 | -1.8255 | -2.4235 | -3.1153 | -4.0724 | -5.1653 | -6.3265 | -13.2551 | -19.4 | -23.0337
AXMINSTER GSP | YEOVIL BSP | YEOVIL PRIMARY | MINIMUM HEADROOM | ST 57690 16833 | NO | NO | 7.19 | 12.4944 | 11.8985 | 11.7648 | 11.2169 | 10.6342 | 9.7373 | 8.7189 | 7.6964 | 7.026 | 3.1709 | -0.47702 | -2.7076 | 12.0771 | 11.6536 | 11.5883 | 11.1781 | 10.7281 | 10.1158 | 9.4067 | 8.6801 | 8.1842 | 5.1577 | 0.62094 | -10.0311 | 11.8689 | 11.3975 | 11.2158 | 10.7618 | 10.2862 | 9.4883 | 8.6056 | 7.7087 | 7.0373 | 3.1975 | -0.030082 | -1.8801
|  | YEOVIL PRIMARY | EE |  |  |  |  | 12.4944 | 11.8985 | 11.7648 | 11.2169 | 10.6342 | 9.7373 | 8.7189 | 7.6964 | 7.026 | 3.325 | 0.088286 | -2.4617 | 12.0771 | 11.6536 | 11.5883 | 11.1781 | 10.7281 | 10.1158 | 9.4067 | 8.6801 | 8.1842 | 5.1577 | 1.3046 | -4.4689 | 11.8689 | 11.3975 | 11.2158 | 10.7618 | 10.2862 | 9.4883 | 8.6056 | 7.7087 | 7.0373 | 3.2995 | 0.48318 | -1.676
|  | YEOVIL PRIMARY | HT |  |  |  |  | 12.8842 | 12.4403 | 12.0291 | 11.5464 | 11.0271 | 10.7567 | 9.9567 | 9.1179 | 8.2444 | 3.1709 | -0.47702 | -2.7076 | 12.4169 | 12.1352 | 11.8791 | 11.5658 | 11.225 | 11.1811 | 10.7291 | 10.2495 | 9.7403 | 7.0924 | 5.5985 | 4.7924 | 12.1291 | 11.7536 | 11.4005 | 10.9964 | 10.5658 | 10.1689 | 9.4271 | 8.6536 | 7.8567 | 3.1975 | -0.030082 | -1.8801
|  | YEOVIL PRIMARY | HE |  |  |  |  | 12.9016 | 12.4822 | 12.0975 | 11.6526 | 11.176 | 11.0118 | 10.3301 | 9.6148 | 8.875 | 4.8199 | 1.6699 | 0.20053 | 12.3781 | 12.0832 | 11.8169 | 11.4873 | 11.1077 | 10.9403 | 10.4648 | 9.9546 | 9.4148 | 5.9403 | 2.1067 | -3.2209 | 12.1403 | 11.7873 | 11.4577 | 11.0801 | 10.6842 | 10.3964 | 9.7699 | 9.1199 | 8.4516 | 4.6862 | 1.9873 | 0.774
|  | YEOVIL PRIMARY | CF |  |  |  |  | 13.1985 | 12.9924 | 12.7281 | 12.474 | 12.1454 | 11.8016 | 11.9016 | 11.5832 | 11.2505 | 8.6138 | 6.0424 | 3.3954 | 12.5138 | 12.324 | 12.0954 | 11.8373 | 11.5097 | 11.1311 | 10.9383 | 10.5281 | 10.0944 | 6.6301 | 0.62094 | -10.0311 | 12.4362 | 12.2699 | 12.0679 | 11.8597 | 11.5985 | 11.3322 | 11.3454 | 11.0934 | 10.8301 | 8.5322 | 5.9424 | 3.4485
AXMINSTER GSP | YEOVIL BSP | YETMINSTER PRIMARY | MINIMUM HEADROOM | ST 60294 10206 | NO | NO | 0.717 | 2.4276 | 2.1602 | 1.9398 | 1.6408 | 1.3255 | 1.3918 | 1.0418 | 0.69286 | 0.47449 | -1.1122 | -2.1969 | -2.5122 | 4.4276 | 4.2327 | 4.0684 | 3.8459 | 3.6061 | 3.7031 | 3.4469 | 3.1888 | 3.049 | 2.1378 | 0.90102 | -1.3143 | 2.7724 | 2.5357 | 2.3337 | 2.0633 | 1.7745 | 1.8265 | 1.501 | 1.1745 | 0.98673 | -0.29898 | -1.1643 | -1.4316
|  | YETMINSTER PRIMARY | EE |  |  |  |  | 2.4276 | 2.1602 | 1.9398 | 1.6408 | 1.3255 | 1.3918 | 1.0418 | 0.69286 | 0.47449 | -1.1122 | -2.1969 | -2.3582 | 4.4276 | 4.2327 | 4.0684 | 3.8459 | 3.6061 | 3.7031 | 3.4469 | 3.1888 | 3.049 | 2.1378 | 1.1827 | 0.12755 | 2.7724 | 2.5357 | 2.3337 | 2.0633 | 1.7745 | 1.8265 | 1.501 | 1.1745 | 0.98673 | -0.29898 | -1.1643 | -1.3031
|  | YETMINSTER PRIMARY | HT |  |  |  |  | 2.5316 | 2.3837 | 2.2255 | 2.0061 | 1.8296 | 1.5337 | 1.2 | 0.84796 | 0.91633 | -0.85102 | -2.1286 | -2.5122 | 4.5531 | 4.45 | 4.352 | 4.2071 | 4.0939 | 3.9092 | 3.6918 | 3.4561 | 3.6122 | 2.6551 | 2.0541 | 1.8765 | 2.849 | 2.7265 | 2.598 | 2.4 | 2.2398 | 1.9714 | 1.6724 | 1.351 | 1.4449 | -0.084694 | -1.1255 | -1.4316
|  | YETMINSTER PRIMARY | HE |  |  |  |  | 2.5296 | 2.3786 | 2.2327 | 2.0194 | 1.848 | 1.5633 | 1.2367 | 0.89184 | 0.97449 | -0.94796 | -2.0204 | -2.1602 | 4.552 | 4.4204 | 4.3122 | 4.1622 | 4.0367 | 3.8357 | 3.6031 | 3.351 | 3.4888 | 2.2684 | 1.302 | 0.25816 | 2.8439 | 2.7204 | 2.5929 | 2.4143 | 2.2602 | 2.0031 | 1.7071 | 1.3969 | 1.501 | -0.12959 | -0.98878 | -1.1041
|  | YETMINSTER PRIMARY | CF |  |  |  |  | 2.5786 | 2.452 | 2.3367 | 2.1796 | 2 | 1.801 | 1.6378 | 1.4051 | 1.1622 | 0.055102 | -1.3684 | -2.0041 | 4.5816 | 4.4776 | 4.3888 | 4.2592 | 4.1204 | 3.9612 | 3.8173 | 3.6214 | 3.4102 | 2.4898 | 0.90102 | -1.3143 | 2.9051 | 2.7918 | 2.6888 | 2.5663 | 2.4102 | 2.2357 | 2.0898 | 1.8837 | 1.6663 | 0.7 | -0.47245 | -0.97959
IVER 66KV GSP |  | YIEWSLEY PRIMARY | MINIMUM HEADROOM | TQ 05643 80961 | NO | NO | 18.752 | 35.8292 | 35.3751 | 34.369 | 33.2261 | 31.9792 | 29.917 | 27.5506 | 25.2884 | 23.5914 | 16.5506 | 11.3914 | 10.321 | 38.2343 | 37.867 | 37.0619 | 36.1323 | 35.1088 | 33.4853 | 31.5802 | 29.7792 | 28.3945 | 22.3782 | 16.9006 | 2.6904 | 33.9006 | 33.4853 | 32.5231 | 31.4302 | 30.2323 | 28.1894 | 25.8292 | 23.5955 | 21.8537 | 15.3149 | 10.6119 | 9.5343
|  | YIEWSLEY PRIMARY | EE |  |  |  |  | 35.8292 | 35.3751 | 34.369 | 33.2261 | 31.9792 | 29.917 | 27.5506 | 25.2884 | 23.5914 | 16.5506 | 12.6935 | 12.4802 | 38.2343 | 37.867 | 37.0619 | 36.1323 | 35.1088 | 33.4853 | 31.5802 | 29.7792 | 28.3945 | 22.3782 | 16.9006 | 9.6098 | 33.9006 | 33.4853 | 32.5231 | 31.4302 | 30.2323 | 28.1894 | 25.8292 | 23.5955 | 21.8537 | 15.3149 | 11.9547 | 11.5098
|  | YIEWSLEY PRIMARY | HT |  |  |  |  | 36.6302 | 35.8608 | 34.9914 | 34.6006 | 33.6619 | 31.9986 | 30.1261 | 28.2037 | 26.1772 | 16.7506 | 11.3914 | 10.321 | 39.02 | 38.4914 | 37.8925 | 37.6863 | 37.0343 | 35.8547 | 34.4843 | 33.1537 | 31.7343 | 25.5741 | 22.3414 | 21.2425 | 34.7047 | 33.9843 | 33.167 | 32.7486 | 31.8547 | 30.1833 | 28.2935 | 26.4272 | 24.467 | 15.5292 | 10.6119 | 9.5343
|  | YIEWSLEY PRIMARY | HE |  |  |  |  | 36.6527 | 36.0149 | 35.2466 | 34.9537 | 34.1384 | 32.7466 | 31.1547 | 29.618 | 27.9619 | 20.9884 | 17.5119 | 16.3884 | 38.8843 | 38.3629 | 37.7394 | 37.4884 | 36.8068 | 35.7119 | 34.4221 | 33.2414 | 31.9578 | 25.4761 | 20.0139 | 12.5955 | 34.7159 | 34.1159 | 33.3884 | 33.069 | 32.2874 | 30.8966 | 29.2955 | 27.8098 | 26.2404 | 19.6333 | 16.5292 | 15.4159
|  | YIEWSLEY PRIMARY | CF |  |  |  |  | 37.1884 | 36.8047 | 36.3394 | 35.8027 | 35.7414 | 35.0812 | 34.2466 | 33.3874 | 32.52 | 27.571 | 22.4955 | 17.6129 | 39.171 | 38.7761 | 38.3068 | 37.7649 | 37.5608 | 36.7823 | 35.8108 | 34.8159 | 33.8017 | 27.5976 | 18.2272 | 2.6904 | 35.219 | 34.8506 | 34.4047 | 33.8914 | 33.8557 | 33.1986 | 32.3527 | 31.4894 | 30.6282 | 25.8853 | 21.0966 | 16.8741
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ZETLAND ROAD PRIMARY | MINIMUM HEADROOM | SU 60592 00043 | NO | YES | 4.366 | 6.0232 | 5.2262 | 4.7548 | 3.8773 | 2.916 | 1.5018 | -0.14723 | -1.7258 | -2.9003 | -8.9482 | -13.9646 | -17.0074 | 9.6987 | 9.0711 | 8.6824 | 7.9885 | 7.2456 | 6.2538 | 5.0191 | 3.7844 | 2.8324 | -2.4972 | -9.9238 | -27.0819 | 6.3824 | 5.5446 | 5.1109 | 4.2058 | 3.262 | 1.9324 | 0.36706 | -1.1431 | -2.2146 | -7.5248 | -11.8901 | -14.3717
|  | ZETLAND ROAD PRIMARY | EE |  |  |  |  | 6.0232 | 5.2262 | 4.7548 | 3.8773 | 2.916 | 1.5018 | -0.14723 | -1.7258 | -2.9003 | -8.9482 | -13.3156 | -16.7891 | 9.6987 | 9.0711 | 8.6824 | 7.9885 | 7.2456 | 6.2538 | 5.0191 | 3.7844 | 2.8324 | -2.4972 | -8.3513 | -17.4666 | 6.3824 | 5.5446 | 5.1109 | 4.2058 | 3.262 | 1.9324 | 0.36706 | -1.1431 | -2.2146 | -7.5248 | -11.286 | -14.2074
|  | ZETLAND ROAD PRIMARY | HT |  |  |  |  | 6.4915 | 5.8997 | 5.2334 | 4.5038 | 4.0854 | 2.9671 | 1.7232 | 0.47726 | -0.85539 | -8.4921 | -13.9646 | -17.0074 | 10.1966 | 9.813 | 9.3966 | 8.963 | 8.7385 | 8.1507 | 7.4742 | 6.7681 | 5.9915 | 1.6926 | -1.0227 | -2.2574 | 6.9558 | 6.3773 | 5.715 | 4.9844 | 4.6293 | 3.5895 | 2.4109 | 1.2171 | -0.030902 | -6.9972 | -11.8901 | -14.3717
|  | ZETLAND ROAD PRIMARY | HE |  |  |  |  | 6.4507 | 5.8732 | 5.2487 | 4.5283 | 4.1303 | 3.1007 | 1.8885 | 0.71604 | -0.45335 | -6.9003 | -11.4197 | -13.2431 | 10.0109 | 9.5354 | 9.0354 | 8.4456 | 8.0834 | 7.3538 | 6.4864 | 5.5915 | 4.6293 | -1.2227 | -7.3564 | -15.7462 | 6.913 | 6.3558 | 5.7334 | 5.0201 | 4.6905 | 3.7405 | 2.6069 | 1.4824 | 0.35073 | -5.5544 | -9.3942 | -10.9003
|  | ZETLAND ROAD PRIMARY | CF |  |  |  |  | 7.013 | 6.6405 | 6.3507 | 5.9752 | 5.6018 | 5.5007 | 5.0232 | 4.465 | 3.8773 | -0.49111 | -4.9421 | -8.8738 | 10.2701 | 9.8711 | 9.5222 | 9.064 | 8.563 | 8.2018 | 7.5446 | 6.8181 | 5.9997 | -0.015596 | -9.9238 | -27.0819 | 7.412 | 7.0415 | 6.7344 | 6.3334 | 5.9252 | 5.8711 | 5.3732 | 4.7997 | 4.2018 | 0.095629 | -3.8544 | -7.3023

## LEP Reference
Local Authority | Grid Supply Point | Bulk Supply Point | Primary Substation
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ARGYLE ROAD PRIMARY
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BILSHAM PRIMARY
Arun | LOVEDEAN GSP |  | CHALCRAFT LANE PRIMARY
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | CHICHESTER PRIMARY
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ROSE GREEN PRIMARY
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | SOUTH BERSTED PRIMARY
Basingstoke and Deane | MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST PRIMARY
Basingstoke and Deane | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BALL HILL PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | BASINGSTOKE PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BRAMLEY GREEN PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | BROOK STREET PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | CHINEHAM PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | DOWN GRANGE PRIMARY
Basingstoke and Deane | FLEET-BRAMLEY GSP | ALTON BSP | HERRIARD PRIMARY
Basingstoke and Deane | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HOOK PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | HOUNDMILLS PRIMARY
Basingstoke and Deane | MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | JAYS CLOSE PRIMARY
Basingstoke and Deane | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINGSCLERE PRIMARY
Basingstoke and Deane | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | MORTIMER PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | OAKRIDGE PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | OVERTON PRIMARY
Basingstoke and Deane | FLEET-BRAMLEY GSP | ALTON BSP | PRESTON CANDOVER PRIMARY
Basingstoke and Deane | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | ST JOHNS PRIMARY
Basingstoke and Deane | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | TADLEY PRIMARY
Basingstoke and Deane | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM PRIMARY
Basingstoke and Deane | MELKSHAM GSP | ANDOVER BSP | WHITCHURCH PRIMARY
Bath and North East Somerset | MELKSHAM GSP | NORRINGTON BSP | BRADFORD-ON-AVON PRIMARY
Bath and North East Somerset | MELKSHAM GSP | NORRINGTON BSP | SPRING QUARRY WEST PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | ALDERNEY PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | BOURNE VALLEY PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | CENTRAL PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | LYTCHETT BSP | CORFE MULLEN PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | LYTCHETT BSP | CREEKMOOR PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | REDHILL BSP | EAST HOWE PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | ELECTRIC HOUSE PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | POOLE (HAMWORTHY) BSP | HAMWORTHY PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | LYTCHETT BSP | HOLES BAY PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE NORTH PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE SOUTH PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | REDHILL BSP | REDHILL PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | WESTBOURNE PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | REDHILL BSP | WINTON PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | ASCOT PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | BAGSHOT PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CROWTHORNE PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | EASTHAMPSTEAD PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | KINGS RIDE PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | KNOWL HILL PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | WOKINGHAM BSP | PEACOCK FARM PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | SANDHURST PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | SUNNINGHILL PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | WARFIELD PRIMARY
Buckinghamshire | IVER 132KV GSP | UPTON BSP | BEACONSFIELD (END BUSBARS) PRIMARY
Buckinghamshire | IVER 132KV GSP | DENHAM BSP | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY
Buckinghamshire | AMERSHAM GSP | LOUDWATER BSP | BOWERDEAN PRIMARY
Buckinghamshire | IVER 132KV GSP | CHALVEY BSP | CHALVEY PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE PRIMARY
Buckinghamshire | IVER 132KV GSP | DENHAM BSP | COKES LANE PRIMARY
Buckinghamshire | IVER 132KV GSP | DENHAM BSP | DENHAM AVENUE PRIMARY
Buckinghamshire | IVER 132KV GSP | SLOUGH BSP | FARNHAM ROYAL PRIMARY
Buckinghamshire | AMERSHAM GSP | LOUDWATER BSP | FLACKWELL HEATH PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE PRIMARY
Buckinghamshire | IVER 132KV GSP | DENHAM BSP | GERRARDS CROSS PRIMARY
Buckinghamshire | IVER 132KV GSP | DENHAM BSP | GRASSINGHAM ROAD PRIMARY
Buckinghamshire | BRAMLEY (BASI) GSP | READING BSP | HENLEY PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW PRIMARY
Buckinghamshire | IVER 132KV GSP | CHALVEY BSP | PETERSFIELD AVENUE PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH PRIMARY
Buckinghamshire | IVER 132KV GSP | UPTON BSP | SUTTON LANE PRIMARY
Buckinghamshire | IVER 132KV GSP | SLOUGH BSP | TAPLOW PRIMARY
Buckinghamshire | IVER 132KV GSP | UPTON BSP | UPTON PRIMARY
Buckinghamshire | IVER 66KV GSP |  | UXBRIDGE PRIMARY
Buckinghamshire | AMERSHAM GSP | LOUDWATER BSP | WELL END PRIMARY
Buckinghamshire | AMERSHAM GSP | LOUDWATER BSP | WYCOMBE MARSH PRIMARY
Buckinghamshire | IVER 66KV GSP |  | YIEWSLEY PRIMARY
Cherwell | COWLEY GSP | HEADINGTON BSP | ARNCOTT PRIMARY
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH PRIMARY
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER PRIMARY
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD PRIMARY
Cherwell | COWLEY GSP | YARNTON BSP | DEDDINGTON PRIMARY
Cherwell | COWLEY GSP | HEADINGTON BSP | HEADINGTON PRIMARY
Cherwell | COWLEY GSP | YARNTON BSP | KIDDINGTON PRIMARY
Cherwell | COWLEY GSP | YARNTON BSP | LOVELACE ROAD PRIMARY
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD PRIMARY
Cherwell | COWLEY GSP | YARNTON BSP | WOODSTOCK PRIMARY
Cherwell | COWLEY GSP | YARNTON BSP | YARNTON PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ASHLING ROAD PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BILLINGSHURST PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BIRDHAM PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | CHICHESTER PRIMARY
Chichester | LOVEDEAN GSP | HAVANT BSP | EMSWORTH PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | FIVE OAKS PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | HASLEMERE PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | HASLINGBOURNE PRIMARY
Chichester | LOVEDEAN GSP | HAVANT BSP | HORNDEAN PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | HUNSTON PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | LANGLEY COURT PRIMARY
Chichester | LOVEDEAN GSP | HAVANT BSP | LEIGH PARK PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | MARKET PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | MIDHURST PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | PETERSFIELD PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | PLAISTOW PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ROSE GREEN PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | SELSEY PRIMARY
Cotswold | MELKSHAM GSP | CHIPPENHAM BSP | ALDERTON PRIMARY
Cotswold | COWLEY GSP | WITNEY BSP | BLEDINGTON PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | CRICKLADE PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | FAIRFORD PRIMARY
Cotswold | MINETY GSP | STRATTON (RESERVE) BSP | LECHLADE PRIMARY
Cotswold | MELKSHAM GSP | CHIPPENHAM BSP | MALMESBURY PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | NORTHLEACH PRIMARY
Cotswold | COWLEY GSP | WITNEY BSP | RISSINGTON PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE PRIMARY
Cotswold | MINETY GSP | STRATTON (RESERVE) BSP | STANTON FITZWARREN PRIMARY
Cotswold | MELKSHAM GSP | CHIPPENHAM BSP | TETBURY PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | WHITEWAY PRIMARY
Cotswold | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WHITLEY WOOD PRIMARY
Dorset | MANNINGTON GSP | LYTCHETT BSP | BLANDFORD PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | CHICKERELL PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | CHILTON CANTELO PRIMARY
Dorset | MANNINGTON GSP | LYTCHETT BSP | CORFE MULLEN PRIMARY
Dorset | MANNINGTON GSP | LYTCHETT BSP | CREEKMOOR PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | DORCHESTER PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL PRIMARY
Dorset | MANNINGTON GSP | POOLE (HAMWORTHY) BSP | HAMWORTHY PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | HENSTRIDGE PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | MANNINGTON PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | Mill Lane PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON PRIMARY
Dorset | MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE SOUTH PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | PORTLAND PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | PULHAM PRIMARY
Dorset | MANNINGTON GSP | REDHILL BSP | REDHILL PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | REDLANDS PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | SHERBORNE PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON PRIMARY
Dorset | MANNINGTON GSP | WAREHAM BSP | SWANAGE PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | VERWOOD PRIMARY
Dorset | MANNINGTON GSP | WAREHAM BSP | WAREHAM TOWN PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | WEST HENDFORD PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES PRIMARY
Dorset | MANNINGTON GSP |  | WINFRITH HEATH PRIMARY
Dorset | MANNINGTON GSP | LYTCHETT BSP | WINTERBORNE KINGSTON PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | YEOVIL PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | YETMINSTER PRIMARY
Ealing | EALING GSP |  | BOSTON MANOR PRIMARY
Ealing | EALING GSP | EALING BSP | BRENTFORD PRIMARY
Ealing | WILLESDEN GSP |  | CANAL BANK 11kV PRIMARY
Ealing | EALING GSP |  | COPLEY DENE PRIMARY
Ealing | EALING GSP | EALING BSP | DEAN GARDENS PRIMARY
Ealing | EALING GSP |  | EALING PRIMARY
Ealing | WILLESDEN GSP | ACTON LANE BSP | GOLDSMITHS PRIMARY
Ealing | WILLESDEN GSP |  | GREENFORD PRIMARY
Ealing | EALING GSP |  | IRONBRIDGE PRIMARY
Ealing | WILLESDEN GSP | ACTON LANE BSP | LEAMINGTON PARK PRIMARY
Ealing | NORTH HYDE GSP |  | NORTH HYDE PRIMARY
Ealing | IVER 66KV GSP |  | NORTHOLT PRIMARY
Ealing | WILLESDEN GSP | ACTON LANE BSP | PARK ROYAL PRIMARY
Ealing | WILLESDEN GSP |  | PERIVALE PRIMARY
Ealing | EALING GSP |  | SOUTHFIELD ROAD PRIMARY
Ealing | NORTH HYDE GSP | NORTH HYDE BSP | SPRINGFIELD ROAD PRIMARY
Ealing | NORTH HYDE GSP | NORTH HYDE BSP | THE GREEN PRIMARY
Ealing | WILLESDEN GSP |  | WESLEY AVENUE PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALTON BSP | ALRESFORD PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALTON BSP | ALTON LOCAL PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALTON BSP | BORDON PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALTON BSP | HERRIARD PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALDERSHOT BSP | HINDHEAD PRIMARY
East Hampshire | LOVEDEAN GSP | HAVANT BSP | HORNDEAN PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | FERNHURST BSP | LANGLEY COURT PRIMARY
East Hampshire | LOVEDEAN GSP | HAVANT BSP | LEIGH PARK PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | FERNHURST BSP | PETERSFIELD PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALTON BSP | PRESTON CANDOVER PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | WRECCLESHAM PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | BASSETT PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | BISHOPSTOKE PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | CHANDLERS FORD PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | HEDGE END PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | VELMORE PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | BROCKHURST PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | HOEFORD PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (RESERVE) BSP | LEE-ON-SOLENT PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | NORTH FAREHAM PRIMARY
Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | PLESSEY TITCHFIELD PRIMARY
Fareham | LOVEDEAN GSP | PORTSMOUTH BSP | PORTCHESTER PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | TITCHFIELD PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | WEST END PRIMARY
Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY PRIMARY
Fareham | LOVEDEAN GSP | WYMERING BSP | WYMERING PRIMARY
Gosport | LOVEDEAN GSP | FAREHAM (MAIN) BSP | BROCKHURST PRIMARY
Gosport | LOVEDEAN GSP | FAREHAM (MAIN) BSP | HOEFORD PRIMARY
Gosport | LOVEDEAN GSP | FAREHAM (RESERVE) BSP | LEE-ON-SOLENT PRIMARY
Gosport | LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ROWNER PARK PRIMARY
Gosport | LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ZETLAND ROAD PRIMARY
Guildford | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FARNBOROUGH PRIMARY
Guildford | FLEET-BRAMLEY GSP | ALDERSHOT BSP | GODALMING PRIMARY
Guildford | FLEET-BRAMLEY GSP | ALDERSHOT BSP | MILFORD PRIMARY
Guildford | FLEET-BRAMLEY GSP | ALDERSHOT BSP | NORMANDY PRIMARY
Guildford | FLEET-BRAMLEY GSP | ALDERSHOT BSP | TONGHAM PRIMARY
Hammersmith and Fulham | WILLESDEN GSP |  | CANAL BANK 11kV PRIMARY
Hart | FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT PRIMARY
Hart | BRAMLEY (BASI) GSP | READING BSP | ARBORFIELD PRIMARY
Hart | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BRAMLEY GREEN PRIMARY
Hart | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | COVE PRIMARY
Hart | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | COXMOOR WOOD PRIMARY
Hart | FLEET-BRAMLEY GSP | PYESTOCK BSP | Crookham PRIMARY
Hart | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | HAWLEY PRIMARY
Hart | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HITCHES LANE PRIMARY
Hart | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HOOK PRIMARY
Hart | FLEET-BRAMLEY GSP | PYESTOCK BSP | PYESTOCK PRIMARY
Hart | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | SANDHURST PRIMARY
Havant | LOVEDEAN GSP | HAVANT BSP | BROCKHAMPTON PRIMARY
Havant | LOVEDEAN GSP | HAVANT BSP | EMSWORTH PRIMARY
Havant | LOVEDEAN GSP | PORTSMOUTH BSP | FARLINGTON PRIMARY
Havant | LOVEDEAN GSP | HAVANT BSP | GABLE HEAD PRIMARY
Havant | LOVEDEAN GSP | HAVANT BSP | LEIGH PARK PRIMARY
Havant | LOVEDEAN GSP | HAVANT BSP | MEYRICK ROAD PRIMARY
Havant | LOVEDEAN GSP | FORT WIDLEY BSP | PURBROOK PRIMARY
Havant | LOVEDEAN GSP | FORT WIDLEY BSP | WATERLOOVILLE PRIMARY
Hillingdon | NORTH HYDE GSP | NORTH HYDE BSP | BATH ROAD EAST PRIMARY
Hillingdon | IVER 132KV GSP | LONGFORD BSP | BATH ROAD WEST PRIMARY
Hillingdon | IVER 132KV GSP | DENHAM BSP | DENHAM AVENUE PRIMARY
Hillingdon | LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT PRIMARY
Hillingdon | IVER 132KV GSP | DENHAM BSP | HAREFIELD PRIMARY
Hillingdon | NORTH HYDE GSP |  | HAYES PRIMARY
Hillingdon | IVER 66KV GSP |  | HILLINGDON PRIMARY
Hillingdon | LALEHAM GSP | EAST BEDFONT BSP | NORTH FELTHAM PRIMARY
Hillingdon | NORTH HYDE GSP |  | NORTH HYDE PRIMARY
Hillingdon | IVER 66KV GSP |  | NORTHOLT PRIMARY
Hillingdon | IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY
Hillingdon | NORTH HYDE GSP | NORTH HYDE BSP | SPRINGFIELD ROAD PRIMARY
Hillingdon | IVER 66KV GSP |  | UXBRIDGE PRIMARY
Hillingdon | IVER 66KV GSP |  | YIEWSLEY PRIMARY
Horsham | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BILLINGSHURST PRIMARY
Horsham | FLEET-BRAMLEY GSP | FERNHURST BSP | FIVE OAKS PRIMARY
Horsham | FLEET-BRAMLEY GSP | FERNHURST BSP | PLAISTOW PRIMARY
Hounslow | NORTH HYDE GSP | NORTH HYDE BSP | BATH ROAD EAST PRIMARY
Hounslow | EALING GSP |  | BOSTON MANOR PRIMARY
Hounslow | EALING GSP | EALING BSP | BRENTFORD PRIMARY
Hounslow | EALING GSP |  | BRIDGE ROAD PRIMARY
Hounslow | LALEHAM GSP | EAST BEDFONT BSP | CHURCH ROAD PRIMARY
Hounslow | EALING GSP |  | EALING PRIMARY
Hounslow | LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT PRIMARY
Hounslow | LALEHAM GSP | EAST BEDFONT BSP | FELTHAM PRIMARY
Hounslow | EALING GSP | EALING BSP | HARVARD LANE PRIMARY
Hounslow | LALEHAM GSP | EAST BEDFONT BSP | HOPE AND ANCHOR PRIMARY
Hounslow | EALING GSP |  | IRONBRIDGE PRIMARY
Hounslow | LALEHAM GSP | EAST BEDFONT BSP | NORTH FELTHAM PRIMARY
Hounslow | NORTH HYDE GSP |  | NORTH HYDE PRIMARY
Hounslow | EALING GSP |  | SOUTHFIELD ROAD PRIMARY
Hounslow | LALEHAM GSP | STAINES BSP | STANWELL PRIMARY
Hounslow | LALEHAM GSP | STAINES BSP | SUNBURY CROSS PRIMARY
Hounslow | NORTH HYDE GSP |  | VICARAGE FARM ROAD PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR PRIMARY
Mendip | MELKSHAM GSP | NORRINGTON BSP | BRADFORD-ON-AVON PRIMARY
Mendip | MELKSHAM GSP | FROME BSP | BRUTON PRIMARY
Mendip | MELKSHAM GSP | FROME BSP | FROME PRIMARY
Mendip | MELKSHAM GSP | FROME BSP | HOLWELL PRIMARY
Mendip | MELKSHAM GSP | NORRINGTON BSP | TROWBRIDGE TOWN PRIMARY
New Forest | FAWLEY GSP | LANGLEY BSP | BUTTS ASH PRIMARY
New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH PRIMARY
New Forest | NURSLING GSP | ROWNHAMS BSP | FLETCHWOOD PRIMARY
New Forest | MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE PRIMARY
New Forest | MANNINGTON GSP | ARNEWOOD BSP | HINCHESLEA PRIMARY
New Forest | MANNINGTON GSP | SALISBURY BSP | HOMINGTON PRIMARY
New Forest | FAWLEY GSP | LANGLEY BSP | LANGLEY PRIMARY
New Forest | MANNINGTON GSP | ARNEWOOD BSP | LYMINGTON PRIMARY
New Forest | NURSLING GSP |  | MARCHWOOD PRIMARY
New Forest | MANNINGTON GSP | ARNEWOOD BSP | MILFORD-ON-SEA PRIMARY
New Forest | MANNINGTON GSP | MANNINGTON BSP | Mill Lane PRIMARY
New Forest | MANNINGTON GSP | ARNEWOOD BSP | NEW MILTON PRIMARY
New Forest | MANNINGTON GSP | SALISBURY BSP | REDLYNCH PRIMARY
New Forest | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE PRIMARY
New Forest | NURSLING GSP | ROWNHAMS BSP | ROMSEY PRIMARY
New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD PRIMARY
New Forest | NURSLING GSP | ROWNHAMS BSP | TOTTON PRIMARY
New Forest | MANNINGTON GSP | MANNINGTON BSP | VERWOOD PRIMARY
Oxford | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL PRIMARY
Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD PRIMARY
Oxford | COWLEY GSP | HEADINGTON BSP | HEADINGTON PRIMARY
Oxford | COWLEY GSP | YARNTON BSP | LOVELACE ROAD PRIMARY
Oxford | COWLEY GSP | HEADINGTON BSP | OLD ROAD PRIMARY
Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD PRIMARY
Oxford | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | OXFORD SCIENCE PARK PRIMARY
Oxford | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | ROSE HILL PRIMARY
Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES PRIMARY
Oxford | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | UNION STREET PRIMARY
Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | UNIVERSITY PARKS PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | COLLEGE PARK PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | FARLINGTON PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | GAMBLE ROAD PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | HILSEA PRIMARY
Portsmouth | LOVEDEAN GSP | HAVANT BSP | MEYRICK ROAD PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | PORTCHESTER PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH PRIMARY
Portsmouth | LOVEDEAN GSP | WYMERING BSP | WYMERING PRIMARY
Purbeck | MANNINGTON GSP | WAREHAM BSP | BOVINGTON PRIMARY
Purbeck | MANNINGTON GSP | WAREHAM BSP | BUSHEY PRIMARY
Reading | FLEET-BRAMLEY GSP | READING TOWN BSP | CAVERSHAM PRIMARY
Reading | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | COURAGES PRIMARY
Reading | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | GREEN PARK PRIMARY
Reading | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | KENTWOOD HILL PRIMARY
Reading | BRAMLEY (BASI) GSP | READING BSP | NORTHUMBERLAND AVENUE PRIMARY
Reading | BRAMLEY (BASI) GSP | READING BSP | READING PRIMARY
Reading | FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN PRIMARY
Reading | BRAMLEY (BASI) GSP | READING BSP | SILVER STREET PRIMARY
Reading | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | SOUTHCOTE PRIMARY
Reading | FLEET-BRAMLEY GSP | READING TOWN BSP | THE MALL PRIMARY
Reading | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WILSON ROAD PRIMARY
Richmond upon Thames | EALING GSP |  | BRIDGE ROAD PRIMARY
Richmond upon Thames | LALEHAM GSP | EAST BEDFONT BSP | HOPE AND ANCHOR PRIMARY
Runnymede | LALEHAM GSP | STAINES BSP | CAUSEWAY PRIMARY
Runnymede | LALEHAM GSP | STAINES BSP | EGHAM PRIMARY
Runnymede | FLEET-BRAMLEY GSP | BRACKNELL BSP | MVEE PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | COVE PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | PYESTOCK BSP | Crookham PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | PYESTOCK BSP | FARNBORO AIRFIELD PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FARNBOROUGH PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | HAWLEY PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | ALDERSHOT BSP | LABURNUM ROAD PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | QUEENSMEAD PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | ALDERSHOT BSP | TONGHAM PRIMARY
Slough | IVER 132KV GSP | CHALVEY BSP | CHALVEY PRIMARY
Slough | IVER 132KV GSP | SLOUGH BSP | FARNHAM ROYAL PRIMARY
Slough | IVER 132KV GSP | CHALVEY BSP | PETERSFIELD AVENUE PRIMARY
Slough | IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY
Slough | IVER 132KV GSP | UPTON BSP | SUTTON LANE PRIMARY
Slough | IVER 132KV GSP | UPTON BSP | UPTON PRIMARY
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | BERINSFIELD PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | READING TOWN BSP | CAVERSHAM PRIMARY
South Oxfordshire | COWLEY GSP | DRAYTON BSP | CHOLSEY PRIMARY
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL PRIMARY
South Oxfordshire | COWLEY GSP |  | CULHAM PRIMARY
South Oxfordshire | COWLEY GSP | DRAYTON BSP | FULSCOT PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | GORING PRIMARY
South Oxfordshire | COWLEY GSP | HEADINGTON BSP | HEADINGTON PRIMARY
South Oxfordshire | BRAMLEY (BASI) GSP | READING BSP | HENLEY PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | KENTWOOD HILL PRIMARY
South Oxfordshire | BRAMLEY (BASI) GSP | READING BSP | KIDMORE END PRIMARY
South Oxfordshire | COWLEY GSP | DRAYTON BSP | MILTON PRIMARY
South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD PRIMARY
South Oxfordshire | COWLEY GSP | HEADINGTON BSP | OLD ROAD PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PANGBOURNE PRIMARY
South Oxfordshire | BRAMLEY (BASI) GSP | READING BSP | READING PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN PRIMARY
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | ROSE HILL PRIMARY
South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH PRIMARY
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | WALLINGFORD PRIMARY
South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON PRIMARY
South Oxfordshire | COWLEY GSP | HEADINGTON BSP | WHEATLEY PRIMARY
South Oxfordshire | COWLEY GSP | DRAYTON BSP | WINSMORE LANE PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | WOODCOTE PRIMARY
South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON PRIMARY
South Somerset | MELKSHAM GSP | FROME BSP | BRUTON PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | CASTLE CARY PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | CHILTON CANTELO PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | HENSTRIDGE PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | LARKHILL PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | MILBORNE PORT PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | SHERBORNE PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | SPARKFORD PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | WEST HENDFORD PRIMARY
South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR PRIMARY
South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | YEOVIL PRIMARY
Southampton | NURSLING GSP | VELMORE BSP | BASSETT PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | BEVOIS VALLEY PRIMARY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CENTRAL BRIDGE PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CHAPEL PRIMARY
Southampton | NURSLING GSP | ROWNHAMS BSP | LORDSHILL PRIMARY
Southampton | NURSLING GSP | ROWNHAMS BSP | MAYBUSH PRIMARY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (MAIN) BSP | REGENTS PARK PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (MAIN) BSP | SHIRLEY PRIMARY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WESTERN ESPLANADE PRIMARY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WOODMILL LANE PRIMARY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON PRIMARY
Spelthorne | LALEHAM GSP | STAINES BSP | CAUSEWAY PRIMARY
Spelthorne | LALEHAM GSP | EAST BEDFONT BSP | CHURCH ROAD PRIMARY
Spelthorne | LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT PRIMARY
Spelthorne | IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY
Spelthorne | LALEHAM GSP | STAINES BSP | SIDNEY ROAD PRIMARY
Spelthorne | LALEHAM GSP | STAINES BSP | STANWELL PRIMARY
Spelthorne | LALEHAM GSP | STAINES BSP | SUNBURY CROSS PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | BRACKNELL BSP | BAGSHOT PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | BRACKNELL BSP | CHOBHAM PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FARNBOROUGH PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FRIMLEY PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | KINGS RIDE PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | BRACKNELL BSP | MVEE PRIMARY
Swindon | MINETY GSP | TOOTHILL BSP | CHISLEDON PRIMARY
Swindon | MINETY GSP | TOOTHILL BSP | DORCAN SOUTH PRIMARY
Swindon | MINETY GSP | STRATTON (MAIN) BSP | DRAKES WAY PRIMARY
Swindon | MINETY GSP |  | GALILEO PRIMARY
Swindon | MINETY GSP | SWINDON BSP | MANCHESTER ROAD PRIMARY
Swindon | MINETY GSP | STRATTON (MAIN) BSP | PARK NORTH PRIMARY
Swindon | MINETY GSP | STRATTON (MAIN) BSP | PLESSEY PRIMARY
Swindon | MINETY GSP | STRATTON (MAIN) BSP | PRESSED STEEL SWINDON PRIMARY
Swindon | MINETY GSP | TOOTHILL BSP | QUARRY ROAD PRIMARY
Swindon | MINETY GSP | STRATTON (RESERVE) BSP | SHRIVENHAM PRIMARY
Swindon | MINETY GSP | STRATTON (RESERVE) BSP | STANTON FITZWARREN PRIMARY
Swindon | MINETY GSP | STRATTON (RESERVE) BSP | STRATTON PRIMARY
Swindon | MINETY GSP | SWINDON BSP | SWINDON PRIMARY
Swindon | MINETY GSP | TOOTHILL BSP | TOOTHILL PRIMARY
Swindon | MINETY GSP | SWINDON BSP | TRADING ESTATE PRIMARY
Swindon | MINETY GSP | SWINDON BSP | WOOTTON BASSETT PRIMARY
Swindon | MINETY GSP | TOOTHILL BSP | WROUGHTON PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | ANDOVER PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | ANDOVER TOWN PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | BARTON STACEY PRIMARY
Test Valley | NURSLING GSP | VELMORE BSP | BASSETT PRIMARY
Test Valley | NURSLING GSP | VELMORE BSP | CHANDLERS FORD PRIMARY
Test Valley | NURSLING GSP | WINCHESTER BSP | DUNBRIDGE PRIMARY
Test Valley | NURSLING GSP | WINCHESTER BSP | HOUGHTON PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT PRIMARY
Test Valley | NURSLING GSP | ROWNHAMS BSP | LORDSHILL PRIMARY
Test Valley | NURSLING GSP | ROWNHAMS BSP | MAYBUSH PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | MIDDLE WALLOP PRIMARY
Test Valley | NURSLING GSP | ROWNHAMS BSP | NORTH BADDESLEY PRIMARY
Test Valley | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PARK HOUSE PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | PORTWAY PRIMARY
Test Valley | NURSLING GSP | ROWNHAMS BSP | ROMSEY PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | THRUXTON PRIMARY
Test Valley | MELKSHAM GSP | WEST GRAFTON BSP | TIDWORTH PRIMARY
Test Valley | NURSLING GSP | VELMORE BSP | VELMORE PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | WHITCHURCH PRIMARY
Three Rivers | IVER 132KV GSP | DENHAM BSP | COKES LANE PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | CHOLSEY PRIMARY
Vale of White Horse | COWLEY GSP | YARNTON BSP | EYNSHAM PRIMARY
Vale of White Horse | MINETY GSP | STRATTON (RESERVE) BSP | FARINGDON PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | FULSCOT PRIMARY
Vale of White Horse | COWLEY GSP | WITNEY BSP | FYFIELD PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | GROVE PRIMARY
Vale of White Horse | COWLEY GSP |  | HARWELL PRIMARY
Vale of White Horse | COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | KENNINGTON PRIMARY
Vale of White Horse | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LAMBOURN PRIMARY
Vale of White Horse | MINETY GSP | STRATTON (RESERVE) BSP | LECHLADE PRIMARY
Vale of White Horse | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LECKHAMPSTEAD PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | MILTON PRIMARY
Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY PRIMARY
Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD PRIMARY
Vale of White Horse | MINETY GSP | STRATTON (RESERVE) BSP | SHRIVENHAM PRIMARY
Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES PRIMARY
Vale of White Horse | COWLEY GSP | WITNEY BSP | STANDLAKE PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | WANTAGE PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | WINSMORE LANE PRIMARY
Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD PRIMARY
Vale of White Horse | COWLEY GSP | YARNTON BSP | YARNTON PRIMARY
Waverley | FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT PRIMARY
Waverley | FLEET-BRAMLEY GSP | ALDERSHOT BSP | FARNHAM PRIMARY
Waverley | FLEET-BRAMLEY GSP | ALDERSHOT BSP | GODALMING PRIMARY
Waverley | FLEET-BRAMLEY GSP | FERNHURST BSP | HASLEMERE PRIMARY
Waverley | FLEET-BRAMLEY GSP | ALDERSHOT BSP | HINDHEAD PRIMARY
Waverley | FLEET-BRAMLEY GSP | ALDERSHOT BSP | MILFORD PRIMARY
Waverley | FLEET-BRAMLEY GSP | FERNHURST BSP | PLAISTOW PRIMARY
Waverley | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | WRECCLESHAM PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BALL HILL PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BEENHAM PRIMARY
West Berkshire | COWLEY GSP | DRAYTON BSP | CHOLSEY PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | GORING PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | HUNGERFORD PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | KENTWOOD HILL PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINTBURY PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LAMBOURN PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LECKHAMPSTEAD PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LOVE LANE PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | MORTIMER PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PADWORTH PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PANGBOURNE PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | RIVERSIDE PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | ST JOHNS PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | TADLEY PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | THEALE PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | TRASH GREEN PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WHITLEY WOOD PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | YATTENDON PRIMARY
West Dorset | MANNINGTON GSP | WAREHAM BSP | BOVINGTON PRIMARY
West Dorset | AXMINSTER GSP | YEOVIL BSP | MILBORNE PORT PRIMARY
West Oxfordshire | MINETY GSP | STRATTON (RESERVE) BSP | BLACK BOURTON PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | BLEDINGTON PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | BURFORD PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | CARTERTON PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | CHARLBURY PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | CHIPPING NORTON PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | DEDDINGTON PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | EYNSHAM PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | KIDDINGTON PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | LEAFIELD PRIMARY
West Oxfordshire | MINETY GSP | STRATTON (RESERVE) BSP | LECHLADE PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | RISSINGTON PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | STANDLAKE PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | WINDRUSH PARK PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | WITNEY TOWN PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | WOODSTOCK PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | YARNTON PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | POOLE (HAMWORTHY) BSP | POOLE PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | ALDERTON PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | ASHTON PARK PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | BEMERTON PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | BOSCOMBE DOWN PRIMARY
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | BRADFORD-ON-AVON PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | BROMHAM PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | CALNE PRIMARY
Wiltshire | MINETY GSP | TOOTHILL BSP | CHISLEDON PRIMARY
Wiltshire | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | COCKLEBURY PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | CODFORD PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | CORSHAM PRIMARY
Wiltshire | MINETY GSP | CIRENCESTER BSP | CRICKLADE PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | CROCKERTON PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | DEVIZES PRIMARY
Wiltshire | NURSLING GSP | WINCHESTER BSP | DUNBRIDGE PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | EASTERTON PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | ENFORD PRIMARY
Wiltshire | MINETY GSP | CIRENCESTER BSP | FAIRFORD PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | FROME PRIMARY
Wiltshire | MINETY GSP |  | GALILEO PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | HAWKERIDGE PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | HOMINGTON PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | HUNGERFORD PRIMARY
Wiltshire | MINETY GSP | CIRENCESTER BSP | KEMBLE RAF PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINTBURY PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LAMBOURN PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | LYNEHAM PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | MALMESBURY PRIMARY
Wiltshire | MELKSHAM GSP | WEST GRAFTON BSP | MARLBOROUGH SOUTH PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | MELKSHAM TOWN PRIMARY
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON PRIMARY
Wiltshire | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | NETHERHAMPTON PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PARK HOUSE PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | PETERSFINGER PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PEWSEY PRIMARY
Wiltshire | MELKSHAM GSP | WEST GRAFTON BSP | RAMSBURY PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | RATFYN PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | REDLYNCH PRIMARY
Wiltshire | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | ROWDEN PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | SALISBURY CENTRAL PRIMARY
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY PRIMARY
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | SPRING QUARRY WEST PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | STAPLEFORD PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | SUTTON BENGER PRIMARY
Wiltshire | MINETY GSP | SWINDON BSP | SWINDON PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | TEFFONT PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | TETBURY PRIMARY
Wiltshire | MELKSHAM GSP | ANDOVER BSP | THRUXTON PRIMARY
Wiltshire | MELKSHAM GSP | WEST GRAFTON BSP | TIDWORTH PRIMARY
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | TISBURY PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | TROWBRIDGE TOWN PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | WARMINSTER PRIMARY
Wiltshire | MELKSHAM GSP | WEST GRAFTON BSP | WEST GRAFTON VILLAGE PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | WESTBURY PRIMARY
Wiltshire | MINETY GSP | SWINDON BSP | WOOTTON BASSETT PRIMARY
Wiltshire | MINETY GSP | TOOTHILL BSP | WROUGHTON PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | YATTON KEYNELL PRIMARY
Winchester | FLEET-BRAMLEY GSP | ALTON BSP | ALRESFORD PRIMARY
Winchester | MELKSHAM GSP | ANDOVER BSP | BARTON STACEY PRIMARY
Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM PRIMARY
Winchester | NURSLING GSP | VELMORE BSP | CHANDLERS FORD PRIMARY
Winchester | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH PRIMARY
Winchester | NURSLING GSP | WINCHESTER BSP | GORDON ROAD PRIMARY
Winchester | NURSLING GSP | WINCHESTER BSP | HARESTOCK PRIMARY
Winchester | NURSLING GSP | VELMORE BSP | HEDGE END PRIMARY
Winchester | LOVEDEAN GSP | HAVANT BSP | HORNDEAN PRIMARY
Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON PRIMARY
Winchester | NURSLING GSP | ROWNHAMS BSP | NORTH BADDESLEY PRIMARY
Winchester | LOVEDEAN GSP | FAREHAM (MAIN) BSP | NORTH FAREHAM PRIMARY
Winchester | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | OVERTON PRIMARY
Winchester | LOVEDEAN GSP | PORTSMOUTH BSP | PORTCHESTER PRIMARY
Winchester | FLEET-BRAMLEY GSP | ALTON BSP | PRESTON CANDOVER PRIMARY
Winchester | LOVEDEAN GSP | FORT WIDLEY BSP | PURBROOK PRIMARY
Winchester | NURSLING GSP | ROWNHAMS BSP | SILKSTEAD PRIMARY
Winchester | NURSLING GSP | WINCHESTER BSP | ST CROSS PRIMARY
Winchester | LOVEDEAN GSP | FAREHAM (MAIN) BSP | TITCHFIELD PRIMARY
Winchester | LOVEDEAN GSP | FORT WIDLEY BSP | WATERLOOVILLE PRIMARY
Winchester | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY PRIMARY
Winchester | LOVEDEAN GSP | WYMERING BSP | WYMERING PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | BRACKNELL BSP | ASCOT PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | BRACKNELL BSP | BAGSHOT PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | BRAYWICK ROAD PRIMARY
Windsor and Maidenhead | LALEHAM GSP | STAINES BSP | CAUSEWAY PRIMARY
Windsor and Maidenhead | IVER 132KV GSP | CHALVEY BSP | CHALVEY PRIMARY
Windsor and Maidenhead | IVER 132KV GSP | CIPPENHAM BSP | CLARENCE ROAD PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | CORDWALLIS PRIMARY
Windsor and Maidenhead | LALEHAM GSP | STAINES BSP | EGHAM PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | KNOWL HILL PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | MAIDENHEAD PRIMARY
Windsor and Maidenhead | IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | BRACKNELL BSP | SUNNINGHILL PRIMARY
Windsor and Maidenhead | IVER 132KV GSP | UPTON BSP | SUTTON LANE PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | TEMPLE FARM PRIMARY
Windsor and Maidenhead | IVER 132KV GSP | UPTON BSP | UPTON PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | BRACKNELL BSP | WARFIELD PRIMARY
Windsor and Maidenhead | AMERSHAM GSP | LOUDWATER BSP | WELL END PRIMARY
Wokingham | BRAMLEY (BASI) GSP | READING BSP | ARBORFIELD PRIMARY
Wokingham | FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL PRIMARY
Wokingham | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | COURAGES PRIMARY
Wokingham | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CROWTHORNE PRIMARY
Wokingham | FLEET-BRAMLEY GSP | WOKINGHAM BSP | ELMS ROAD PRIMARY
Wokingham | BRAMLEY (BASI) GSP | READING BSP | HENLEY PRIMARY
Wokingham | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | KNOWL HILL PRIMARY
Wokingham | BRAMLEY (BASI) GSP | READING BSP | LITTLE HUNGERFORD PRIMARY
Wokingham | BRAMLEY (BASI) GSP | READING BSP | READING PRIMARY
Wokingham | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | TEMPLE FARM PRIMARY
Wokingham | BRAMLEY (BASI) GSP | READING BSP | TWYFORD PRIMARY
Wokingham | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WHITLEY WOOD PRIMARY
Wokingham | FLEET-BRAMLEY GSP | WOKINGHAM BSP | WOKINGHAM PRIMARY

## EISD
| GSPs in November 2022 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Acton Lane | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the Strategic Development Plan
| Amersham Main | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Axminster | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Botley Wood | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Bramley | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Chickerell | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Cowley | 2029 | Under active review | 2029 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Ealing | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| East Claydon | 2034 | Under active review | 2034 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Fawley | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Fleet | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Iver | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Laleham | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Lovedean | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Mannington | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Melksham | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Minety | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| North Hyde | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Nursling | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Tynemouth | 2032 | Under active review | 2032 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Willesden | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
2023-01-31 | Transmission Owner's freeze date
Southern Electric Power Distribution | DNO Licence area
NGET | Transmision Owner providing
2023-03-01 | Last update (version, date)
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 The above EISD's are likely to be subject to change on completion of NESO's Connections Reform Project TMO4+, further information can be found at:
https://www.neso.energy/industry-information/connections-reform
3 For storage, both the demand and generation EISDs may be relevant.
4 Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
5 Where the tranmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
6 The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
7 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
8 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.