## Contents
SHEPD Network Scenario Headroom Report 2026 Consultation Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations and Bulk Supply Points (BSP) up to 2050. In consultation version, SSEN have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN's best view of the future demand and generation needs on our network is aligned to the Holistic Transition scenario, moving from Consumer Transformation which was our best view in the 2024 NSHR. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Local Authority Reference | This tab provides information on the local authorities and the Primaries that support those areas
EISD | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
Mar 2026 Version 1.1

## Key Information
SHEPD Network Scenario Headroom Report 2026 Consultation Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our other documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation or BSP as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. In order to identify future overloaded network assets, forecasts are created which combine our long term DFES projections with the estimated contribution from our connections pipeline after appropriate diversity factors have been applied. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SEPD. Please note that our DFES scenario naming convention has been updated since 2024 to more closely align with the updated NESO Future Energy Scenario (FES) pathways framework. Published annually, the FES framework outlines different scenarios for the future of the whole energy system. SSEN's DFES builds on the FES scenarios by engaging a diverse and expert range of stakeholders, undertaking detailed investigations into the pipeline of projects seeking to connect, and reflecting extensive industry and local area insight to forecast future load on SSEN’s network.
New DFES Scenario | Previous DFES Scenario | FES Pathway Description
Electric Engagement (EE) | Consumer Transformation (CT) | Net zero met through mainly electrified demand. Consumers are highly engaged in the energy transition through smart technologies that reduce energy demands, utilising technologies such as electric heat pumps and electric vehicles.
Holistic Transition (HT) | Leading the Way (LW) | Net zero met through a mix of electrification and hydrogen, with hydrogen mainly around industrial clusters. Consumer engagement in the transition is very strong with demand shifting, with smart homes and electric vehicles providing flexibility to the grid.
Hydrogen Evolution (HE) | System Transformation (ST) | Net zero met through fast progress for hydrogen in industry and heat. Many consumers will have hydrogen boilers, though energy efficiency will be key to reducing cost. There are low levels of consumer engagement. Hydrogen will be prevalent for heavy goods vehicles but electric car uptake is strong.
Counterfactual (CF) | Falling Short (FS) | Net zero missed, though some progress is made for decarbonisation compared to today. While home insulation improves, there is still a heavy reliance on gas across all sectors, particularly power and space heating. Electric vehicle uptake is slower than the net zero pathways, but still displaces petrol and diesel.
`
Mar 2026
Version 1.1

## Primary Headroom Dem
#VALUE! | Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Demand (MVA) | Demand Headroom Winter (MVA) | [11 empty] | Demand Headroom Summer (MVA) | [11 empty] | Demand Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
| FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | 0.13 | 0.11718 | 0.11412 | 0.1131 | 0.10392 | 0.10188 | 0.092694 | 0.092694 | 0.090653 | 0.088612 | 0.089633 | 0.084531 | 0.079429 | 0.061429 | 0.11551 | 0.11449 | 0.11347 | 0.10429 | 0.10327 | 0.095102 | 0.099184 | 0.094082 | 0.09102 | 0.095102 | 0.097143 | 0.10206 | 0.095939 | 0.11839 | 0.11533 | 0.11431 | 0.10512 | 0.1041 | 0.094918 | 0.093898 | 0.092878 | 0.090837 | 0.091857
|  | ABERCHALDER | EE |  |  |  |  | 0.11718 | 0.11412 | 0.1131 | 0.10392 | 0.10188 | 0.092694 | 0.092694 | 0.095755 | 0.091673 | 0.089633 | 0.084531 | 0.080449 | 0.062449 | 0.11551 | 0.11449 | 0.11347 | 0.10429 | 0.10327 | 0.095102 | 0.099184 | 0.10327 | 0.099184 | 0.097143 | 0.097143 | 0.10206 | 0.099 | 0.11839 | 0.11533 | 0.11431 | 0.10512 | 0.1041 | 0.094918 | 0.093898 | 0.09798 | 0.093898 | 0.091857
|  | ABERCHALDER | HT |  |  |  |  | 0.12433 | 0.12331 | 0.1131 | 0.11208 | 0.11208 | 0.1029 | 0.10086 | 0.090653 | 0.090653 | 0.089633 | 0.085551 | 0.079429 | 0.061429 | 0.12265 | 0.12265 | 0.11449 | 0.11245 | 0.11245 | 0.10429 | 0.10327 | 0.095102 | 0.098163 | 0.098163 | 0.097143 | 0.10206 | 0.10206 | 0.12553 | 0.12451 | 0.11533 | 0.11329 | 0.11329 | 0.1041 | 0.10308 | 0.092878 | 0.092878 | 0.091857
|  | ABERCHALDER | HE |  |  |  |  | 0.12433 | 0.12433 | 0.11412 | 0.1131 | 0.11208 | 0.10188 | 0.10086 | 0.091673 | 0.088612 | 0.091673 | 0.087592 | 0.084531 | 0.063469 | 0.12265 | 0.12265 | 0.11449 | 0.11347 | 0.11245 | 0.10327 | 0.10224 | 0.094082 | 0.09102 | 0.098163 | 0.097143 | 0.1041 | 0.10104 | 0.12553 | 0.12553 | 0.11533 | 0.11431 | 0.11329 | 0.1041 | 0.10206 | 0.093898 | 0.090837 | 0.093898
|  | ABERCHALDER | CF |  |  |  |  | 0.12433 | 0.12433 | 0.11616 | 0.11412 | 0.11412 | 0.1131 | 0.10494 | 0.10188 | 0.094735 | 0.092694 | 0.096776 | 0.089633 | 0.06551 | 0.12265 | 0.12265 | 0.11551 | 0.11449 | 0.11449 | 0.11245 | 0.10429 | 0.10327 | 0.096122 | 0.095102 | 0.10327 | 0.10512 | 0.095939 | 0.12553 | 0.12553 | 0.11737 | 0.11533 | 0.11533 | 0.11329 | 0.10512 | 0.1041 | 0.096959 | 0.093898
| TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 0.326 | 3.7212 | 3.5396 | 3.361 | 3.1447 | 2.8773 | 2.5906 | 2.2447 | 1.9059 | 1.6253 | 1.2845 | 0.25592 | -0.15633 | -0.6349 | 4.6773 | 4.5549 | 4.4396 | 4.2927 | 4.1161 | 3.9478 | 3.7131 | 3.4845 | 3.3182 | 3.1171 | 2.5355 | 2.4773 | 2.1712 | 4.3212 | 4.159 | 3.9978 | 3.8018 | 3.562 | 3.3039 | 2.9763 | 2.6631 | 2.4131 | 2.109
|  | ABERFELDY | EE |  |  |  |  | 3.7212 | 3.5396 | 3.3671 | 3.1478 | 2.8865 | 2.6284 | 2.2447 | 1.9059 | 1.6253 | 1.2845 | 0.25592 | -0.13796 | -0.62878 | 4.6773 | 4.5549 | 4.4396 | 4.2927 | 4.1161 | 3.9478 | 3.7131 | 3.4845 | 3.3182 | 3.1171 | 2.5355 | 2.4773 | 2.2243 | 4.3212 | 4.159 | 4.0029 | 3.8018 | 3.5651 | 3.3182 | 2.9763 | 2.6631 | 2.4131 | 2.109
|  | ABERFELDY | HT |  |  |  |  | 3.7376 | 3.5671 | 3.361 | 3.1447 | 2.8773 | 2.5906 | 2.2947 | 1.9916 | 1.6702 | 1.3131 | 0.33653 | -0.15633 | -0.6349 | 4.6947 | 4.5906 | 4.4671 | 4.3355 | 4.1682 | 3.9978 | 3.8192 | 3.6508 | 3.4671 | 3.2733 | 2.712 | 2.6712 | 2.6355 | 4.3335 | 4.1784 | 3.9978 | 3.8029 | 3.562 | 3.3039 | 3.0386 | 2.7682 | 2.4804 | 2.1682
|  | ABERFELDY | HE |  |  |  |  | 3.758 | 3.6365 | 3.4988 | 3.3437 | 3.1335 | 2.8814 | 2.5641 | 2.3018 | 2.0161 | 1.6784 | 0.81204 | 0.37531 | -0.18388 | 4.7069 | 4.6192 | 4.5263 | 4.4212 | 4.2784 | 4.1202 | 3.9243 | 3.7682 | 3.5896 | 3.3916 | 2.8141 | 2.7151 | 2.4559 | 4.3539 | 4.2406 | 4.1171 | 3.9743 | 3.7835 | 3.56 | 3.2804 | 3.0478 | 2.7957 | 2.5018
|  | ABERFELDY | CF |  |  |  |  | 3.8202 | 3.7559 | 3.6743 | 3.5784 | 3.4784 | 3.3457 | 3.1988 | 3.0131 | 2.8896 | 2.7059 | 1.7324 | 1.0508 | 0.19265 | 4.7549 | 4.7039 | 4.6427 | 4.5733 | 4.4967 | 4.3957 | 4.2886 | 4.1529 | 4.0631 | 3.9335 | 3.2447 | 2.7937 | 2.1712 | 4.4141 | 4.3539 | 4.2784 | 4.1886 | 4.1018 | 3.9773 | 3.8457 | 3.6784 | 3.5641 | 3.4018
| STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 0.383 | 3.4776 | 3.4367 | 3.3867 | 3.3194 | 3.2745 | 3.2071 | 3.1224 | 3.0235 | 2.949 | 2.8398 | 2.5296 | 2.3612 | 1.8286 | 4.149 | 4.1082 | 4.0633 | 4.0071 | 3.9612 | 3.9 | 3.8235 | 3.7327 | 3.6827 | 3.6133 | 3.3918 | 3.5056 | 3.2393 | 3.9628 | 3.9046 | 3.8393 | 3.7556 | 3.6903 | 3.6087 | 3.4985 | 3.3709 | 3.2954 | 3.1964
|  | ABERFOYLE | EE |  |  |  |  | 3.4776 | 3.4367 | 3.3867 | 3.3194 | 3.2745 | 3.2071 | 3.1224 | 3.0235 | 2.949 | 2.8398 | 2.5296 | 2.4306 | 1.9071 | 4.149 | 4.1082 | 4.0633 | 4.0071 | 3.9612 | 3.9 | 3.8235 | 3.7327 | 3.6827 | 3.6133 | 3.3918 | 3.5056 | 3.3495 | 3.9628 | 3.9046 | 3.8393 | 3.7556 | 3.6903 | 3.6087 | 3.4985 | 3.3709 | 3.2954 | 3.1964
|  | ABERFOYLE | HT |  |  |  |  | 3.5112 | 3.4776 | 3.4408 | 3.3918 | 3.35 | 3.2939 | 3.2531 | 3.1816 | 3.0939 | 2.9908 | 2.5816 | 2.3612 | 1.8286 | 4.1765 | 4.1439 | 4.1102 | 4.0653 | 4.0214 | 3.9714 | 3.9296 | 3.8643 | 3.8071 | 3.7429 | 3.4827 | 3.573 | 3.527 | 3.9913 | 3.9403 | 3.8862 | 3.8168 | 3.7587 | 3.6832 | 3.6158 | 3.523 | 3.4434 | 3.3485
|  | ABERFOYLE | HE |  |  |  |  | 3.5112 | 3.4827 | 3.452 | 3.4112 | 3.3765 | 3.3296 | 3.2918 | 3.2276 | 3.1684 | 3.1041 | 2.6745 | 2.5224 | 2.0071 | 4.1724 | 4.1459 | 4.1173 | 4.0786 | 4.0449 | 3.998 | 3.9602 | 3.9 | 3.8459 | 3.7878 | 3.4918 | 3.574 | 3.427 | 3.9913 | 3.9515 | 3.9107 | 3.8597 | 3.8128 | 3.7505 | 3.6954 | 3.6158 | 3.5454 | 3.4638
|  | ABERFOYLE | CF |  |  |  |  | 3.5204 | 3.5 | 3.4684 | 3.448 | 3.4122 | 3.3867 | 3.349 | 3.301 | 3.2816 | 3.2398 | 2.9531 | 2.6949 | 2.0653 | 4.1806 | 4.1592 | 4.1296 | 4.1041 | 4.0694 | 4.0418 | 4.001 | 3.952 | 3.9276 | 3.8816 | 3.6153 | 3.5658 | 3.2393 | 4.0026 | 3.9679 | 3.9281 | 3.8923 | 3.8485 | 3.8107 | 3.7597 | 3.6964 | 3.6638 | 3.6077
| KEITH 2 | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 2.923 | 0.46122 | 0.36837 | 0.28776 | 0.2102 | 0.086735 | -0.011224 | -0.10816 | -0.26633 | -0.48878 | -0.68571 | -1.25 | -1.4806 | -1.5602 | 1.2959 | 1.2245 | 1.1622 | 1.1071 | 1.0112 | 0.93265 | 0.86122 | 0.76122 | 0.58673 | 0.44184 | 0.055102 | -0.076531 | -0.15 | 0.88776 | 0.81837 | 0.76429 | 0.71429 | 0.6 | 0.48469 | 0.37449 | 0.22857 | 0.014286 | -0.17245
|  | ABERLOUR | EE |  |  |  |  | 0.46122 | 0.36837 | 0.28776 | 0.2102 | 0.086735 | -0.011224 | -0.10816 | -0.26633 | -0.48878 | -0.68571 | -1.25 | -1.4265 | -1.4551 | 1.2959 | 1.2245 | 1.1622 | 1.1071 | 1.0112 | 0.93265 | 0.86122 | 0.76122 | 0.58673 | 0.44184 | 0.061224 | -0.011224 | -0.026531 | 0.88776 | 0.81837 | 0.76429 | 0.71429 | 0.6 | 0.48469 | 0.37449 | 0.22857 | 0.014286 | -0.17245
|  | ABERLOUR | HT |  |  |  |  | 0.48673 | 0.40102 | 0.33673 | 0.27347 | 0.16327 | 0.084694 | -0.013265 | -0.14286 | -0.40612 | -0.60204 | -1.2163 | -1.4806 | -1.5602 | 1.3184 | 1.2571 | 1.2092 | 1.1602 | 1.0755 | 1.0204 | 0.95102 | 0.86633 | 0.64286 | 0.48878 | 0.086735 | -0.05102 | -0.10714 | 0.90612 | 0.84388 | 0.8 | 0.75816 | 0.67959 | 0.58776 | 0.48571 | 0.3602 | 0.10306 | -0.084694
|  | ABERLOUR | HE |  |  |  |  | 0.48469 | 0.40714 | 0.35102 | 0.29082 | 0.18673 | 0.11429 | 0.030612 | -0.073469 | -0.25816 | -0.42551 | -1.1724 | -1.4041 | -1.5173 | 1.3153 | 1.2592 | 1.2143 | 1.1663 | 1.0888 | 1.0327 | 0.96531 | 0.87857 | 0.71939 | 0.58469 | 0.055102 | -0.076531 | -0.15 | 0.9051 | 0.84694 | 0.8102 | 0.77245 | 0.69898 | 0.63776 | 0.54184 | 0.42347 | 0.23163 | 0.068367
|  | ABERLOUR | CF |  |  |  |  | 0.50102 | 0.44388 | 0.40612 | 0.36939 | 0.29388 | 0.24286 | 0.20102 | 0.14286 | 0.055102 | -0.032653 | -0.54592 | -1.0449 | -1.3551 | 1.3296 | 1.2837 | 1.2571 | 1.2255 | 1.1673 | 1.1265 | 1.0939 | 1.0439 | 0.96837 | 0.89082 | 0.47041 | 0.11837 | -0.064286 | 0.91327 | 0.86837 | 0.8449 | 0.82143 | 0.76429 | 0.72959 | 0.7051 | 0.66429 | 0.57041 | 0.47449
| ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 0.119 | 1.6602 | 1.6133 | 1.5592 | 1.4908 | 1.4388 | 1.3408 | 1.2204 | 1.1082 | 1.0357 | 0.9051 | 0.62857 | 0.57041 | 0.55408 | 2.3133 | 2.2949 | 2.2684 | 2.2316 | 2.201 | 2.1398 | 2.0704 | 2.002 | 1.9612 | 1.8898 | 1.7224 | 1.6459 | 1.4173 | 2.1398 | 2.101 | 2.052 | 1.9918 | 1.9408 | 1.8531 | 1.7439 | 1.6408 | 1.5755 | 1.4633
|  | ABERNETHY | EE |  |  |  |  | 1.6602 | 1.6133 | 1.5592 | 1.4908 | 1.4388 | 1.3408 | 1.2204 | 1.1082 | 1.0357 | 0.9051 | 0.62857 | 0.59592 | 0.58367 | 2.3133 | 2.2949 | 2.2684 | 2.2316 | 2.201 | 2.1398 | 2.0704 | 2.002 | 1.9612 | 1.8898 | 1.7224 | 1.6612 | 1.5653 | 2.1398 | 2.101 | 2.052 | 1.9918 | 1.9408 | 1.8531 | 1.7439 | 1.6408 | 1.5755 | 1.4633
|  | ABERNETHY | HT |  |  |  |  | 1.6867 | 1.6429 | 1.602 | 1.549 | 1.4929 | 1.4 | 1.3265 | 1.2255 | 1.1143 | 0.92857 | 0.68673 | 0.57041 | 0.55408 | 2.3347 | 2.3184 | 2.2969 | 2.2694 | 2.2429 | 2.1929 | 2.1602 | 2.1071 | 2.048 | 1.9551 | 1.7959 | 1.7337 | 1.7224 | 2.1592 | 2.1204 | 2.0816 | 2.0347 | 1.9847 | 1.9071 | 1.8459 | 1.7571 | 1.6633 | 1.5102
|  | ABERNETHY | HE |  |  |  |  | 1.6878 | 1.6531 | 1.6214 | 1.5724 | 1.5316 | 1.4449 | 1.3571 | 1.2582 | 1.1561 | 1.0296 | 0.70204 | 0.62245 | 0.61429 | 2.3357 | 2.3184 | 2.301 | 2.2745 | 2.2531 | 2.2061 | 2.1582 | 2.1051 | 2.0469 | 1.9765 | 1.7673 | 1.6776 | 1.5867 | 2.1592 | 2.1316 | 2.102 | 2.0643 | 2.0265 | 1.948 | 1.8765 | 1.7878 | 1.701 | 1.5918
|  | ABERNETHY | CF |  |  |  |  | 1.6918 | 1.6622 | 1.6204 | 1.5969 | 1.5653 | 1.5143 | 1.4551 | 1.4051 | 1.3439 | 1.251 | 0.94082 | 0.73061 | 0.62245 | 2.3388 | 2.3245 | 2.3 | 2.2888 | 2.2684 | 2.2429 | 2.2092 | 2.1776 | 2.1347 | 2.0816 | 1.8663 | 1.6459 | 1.4173 | 2.1643 | 2.1388 | 2.1051 | 2.0837 | 2.0531 | 2.0143 | 1.9622 | 1.9194 | 1.8622 | 1.7796
| TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | NO | 1.645 | 7.7135 | 7.5523 | 7.2809 | 6.9604 | 6.6309 | 6.2482 | 5.8196 | 5.3604 | 5.1441 | 4.7962 | 3.888 | 3.6002 | 2.7288 | 9.3472 | 9.2227 | 9.0819 | 8.9155 | 8.7441 | 8.5431 | 8.3125 | 8.0564 | 7.9288 | 7.7257 | 7.1451 | 7.2895 | 6.4222 | 8.9742 | 8.7579 | 8.511 | 8.2191 | 7.9263 | 7.5834 | 7.1967 | 6.7793 | 6.6048 | 6.2844
|  | ABOYNE | EE |  |  |  |  | 7.7135 | 7.5523 | 7.2809 | 6.9604 | 6.6309 | 6.2482 | 5.8196 | 5.3604 | 5.1441 | 4.7962 | 3.888 | 3.7206 | 2.9135 | 9.3472 | 9.2227 | 9.0819 | 8.9155 | 8.7441 | 8.5431 | 8.3125 | 8.0564 | 7.9288 | 7.7257 | 7.1737 | 7.3671 | 6.9814 | 8.9742 | 8.7579 | 8.511 | 8.2191 | 7.9263 | 7.5834 | 7.1967 | 6.7793 | 6.6048 | 6.2844
|  | ABOYNE | HT |  |  |  |  | 7.7502 | 7.5921 | 7.3421 | 7.04 | 6.7594 | 6.4064 | 6.0431 | 5.6839 | 5.2992 | 4.9502 | 4.1217 | 3.6002 | 2.7288 | 9.388 | 9.2717 | 9.1523 | 9.0013 | 8.8635 | 8.6747 | 8.4798 | 8.2655 | 8.039 | 7.8166 | 7.2666 | 7.3732 | 7.2579 | 9.0191 | 8.8089 | 8.5854 | 8.312 | 8.0589 | 7.7365 | 7.412 | 7.0916 | 6.7405 | 6.4201
|  | ABOYNE | HE |  |  |  |  | 7.7564 | 7.6523 | 7.4798 | 7.2451 | 7.0115 | 6.7074 | 6.3594 | 6.0441 | 5.7002 | 5.4053 | 4.187 | 3.839 | 2.9645 | 9.389 | 9.2941 | 9.1829 | 9.0513 | 8.9186 | 8.7431 | 8.5431 | 8.3329 | 8.1135 | 7.9023 | 7.1451 | 7.2895 | 7.0518 | 9.0212 | 8.8722 | 8.6987 | 8.4905 | 8.2803 | 8.0048 | 7.6956 | 7.413 | 7.1028 | 6.8263
|  | ABOYNE | CF |  |  |  |  | 7.7594 | 7.6604 | 7.5513 | 7.3584 | 7.1462 | 6.9217 | 6.6778 | 6.4064 | 6.1911 | 5.9921 | 5.0217 | 4.4757 | 3.1227 | 9.4115 | 9.3421 | 9.2706 | 9.1747 | 9.0717 | 8.9635 | 8.8349 | 8.6839 | 8.5553 | 8.4237 | 7.6951 | 7.4201 | 6.4222 | 9.0395 | 8.9089 | 8.7701 | 8.5977 | 8.4059 | 8.2079 | 7.9916 | 7.7507 | 7.564 | 7.3814
| GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | NO | 0.304 | -0.022437 | -0.035702 | -0.060192 | -0.07958 | -0.10611 | -0.12244 | -0.15407 | -0.19182 | -0.21631 | -0.24591 | -0.3204 | -0.34693 | -0.35203 | 0.13471 | 0.12756 | 0.11328 | 0.10205 | 0.083686 | 0.072461 | 0.054094 | 0.029604 | 0.014298 | -0.003049 | -0.052029 | -0.068355 | -0.10509 | -0.14489 | -0.15713 | -0.17856 | -0.19693 | -0.22142 | -0.23774 | -0.26836 | -0.30509 | -0.32856 | -0.35509
|  | ACHILTIBUIE | EE |  |  |  |  | -0.022437 | -0.035702 | -0.060192 | -0.07958 | -0.10611 | -0.12244 | -0.15407 | -0.19182 | -0.21631 | -0.24591 | -0.3204 | -0.32958 | -0.33672 | 0.13471 | 0.12756 | 0.11328 | 0.10205 | 0.083686 | 0.072461 | 0.054094 | 0.029604 | 0.014298 | -0.003049 | -0.052029 | -0.068355 | -0.092845 | -0.14489 | -0.15713 | -0.17856 | -0.19693 | -0.22142 | -0.23774 | -0.26836 | -0.30509 | -0.32856 | -0.35509
|  | ACHILTIBUIE | HT |  |  |  |  | -0.017335 | -0.027539 | -0.042845 | -0.061212 | -0.0806 | -0.094886 | -0.12244 | -0.14999 | -0.16427 | -0.19489 | -0.29795 | -0.34693 | -0.35203 | 0.13879 | 0.13369 | 0.1245 | 0.11532 | 0.10409 | 0.09491 | 0.078584 | 0.062257 | 0.053073 | 0.035727 | -0.03162 | -0.062233 | -0.064273 | -0.13978 | -0.14897 | -0.16325 | -0.17856 | -0.19693 | -0.21121 | -0.23672 | -0.26325 | -0.27856 | -0.30509
|  | ACHILTIBUIE | HE |  |  |  |  | -0.017335 | -0.025498 | -0.036722 | -0.047947 | -0.067335 | -0.078559 | -0.099988 | -0.12652 | -0.1357 | -0.15713 | -0.27244 | -0.30101 | -0.30713 | 0.13879 | 0.13471 | 0.12756 | 0.12144 | 0.10613 | 0.098992 | 0.085727 | 0.07042 | 0.064298 | 0.051033 | -0.019376 | -0.049988 | -0.070396 | -0.13978 | -0.14693 | -0.15611 | -0.16733 | -0.18264 | -0.19489 | -0.21733 | -0.2408 | -0.25101 | -0.27346
|  | ACHILTIBUIE | CF |  |  |  |  | -0.016314 | -0.019376 | -0.027539 | -0.038763 | -0.051008 | -0.065294 | -0.075498 | -0.092845 | -0.10611 | -0.11223 | -0.18978 | -0.26529 | -0.30305 | 0.13879 | 0.13981 | 0.13267 | 0.12348 | 0.11634 | 0.10818 | 0.10307 | 0.091849 | 0.078584 | 0.075522 | 0.02042 | -0.046927 | -0.10509 | -0.13774 | -0.13978 | -0.14795 | -0.15917 | -0.17142 | -0.18162 | -0.19182 | -0.20917 | -0.22346 | -0.22856
| BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | NO | 0.023 | 0.45122 | 0.44918 | 0.44714 | 0.44 | 0.43592 | 0.42673 | 0.41653 | 0.40224 | 0.4002 | 0.38898 | 0.36959 | 0.36653 | 0.32051 | 0.44806 | 0.44806 | 0.45316 | 0.44806 | 0.445 | 0.43888 | 0.43378 | 0.42357 | 0.42153 | 0.41439 | 0.39806 | 0.41444 | 0.39097 | 0.45423 | 0.45321 | 0.45321 | 0.44811 | 0.44301 | 0.43383 | 0.42566 | 0.4124 | 0.4073 | 0.39709
|  | AIGAS | EE |  |  |  |  | 0.45122 | 0.45531 | 0.44714 | 0.44 | 0.43592 | 0.42673 | 0.41653 | 0.40224 | 0.4002 | 0.38898 | 0.36959 | 0.36959 | 0.32051 | 0.44806 | 0.45827 | 0.45316 | 0.44806 | 0.445 | 0.43888 | 0.43378 | 0.42357 | 0.42153 | 0.41439 | 0.39806 | 0.41648 | 0.40628 | 0.45423 | 0.46036 | 0.45321 | 0.44811 | 0.44301 | 0.43383 | 0.42566 | 0.4124 | 0.4073 | 0.39709
|  | AIGAS | HT |  |  |  |  | 0.46755 | 0.44918 | 0.44714 | 0.4451 | 0.44204 | 0.43898 | 0.42776 | 0.42469 | 0.41755 | 0.41041 | 0.37878 | 0.36653 | 0.32051 | 0.46235 | 0.44806 | 0.45316 | 0.45214 | 0.4501 | 0.4501 | 0.44194 | 0.43888 | 0.43582 | 0.42969 | 0.40929 | 0.42362 | 0.4226 | 0.47056 | 0.45321 | 0.45321 | 0.45219 | 0.44913 | 0.44607 | 0.43587 | 0.43179 | 0.42566 | 0.41852
|  | AIGAS | HE |  |  |  |  | 0.46755 | 0.44918 | 0.4502 | 0.44918 | 0.4451 | 0.44204 | 0.4349 | 0.43082 | 0.42265 | 0.41551 | 0.38184 | 0.37265 | 0.32561 | 0.46235 | 0.44806 | 0.4552 | 0.45418 | 0.45214 | 0.4501 | 0.44398 | 0.44296 | 0.43786 | 0.43173 | 0.40724 | 0.41954 | 0.40934 | 0.47056 | 0.45321 | 0.45628 | 0.45526 | 0.45219 | 0.45015 | 0.44097 | 0.43791 | 0.43179 | 0.4226
|  | AIGAS | CF |  |  |  |  | 0.46755 | 0.46041 | 0.45122 | 0.45327 | 0.44918 | 0.44408 | 0.44102 | 0.43388 | 0.43082 | 0.42367 | 0.40224 | 0.37469 | 0.32459 | 0.46235 | 0.4552 | 0.4552 | 0.45724 | 0.4552 | 0.45316 | 0.45112 | 0.445 | 0.44092 | 0.43582 | 0.41847 | 0.41444 | 0.39097 | 0.47056 | 0.46342 | 0.4573 | 0.46036 | 0.45628 | 0.45219 | 0.44913 | 0.43995 | 0.43893 | 0.43179
| ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 0.693 | 4.6092 | 4.5582 | 4.501 | 4.4469 | 4.3551 | 4.2184 | 4.1153 | 4.0347 | 3.9265 | 3.8357 | 3.6153 | 3.5408 | 3.2804 | 5.5753 | 5.5437 | 5.5018 | 5.462 | 5.3733 | 5.2651 | 5.2049 | 5.1396 | 5.0773 | 5.0212 | 4.812 | 4.9049 | 4.7131 | 5.1559 | 5.1141 | 5.0529 | 4.9988 | 4.9069 | 4.7488 | 4.6467 | 4.5671 | 4.461 | 4.3722
|  | AIRD | EE |  |  |  |  | 4.6092 | 4.5582 | 4.501 | 4.4469 | 4.3735 | 4.2184 | 4.1153 | 4.0347 | 3.9265 | 3.8357 | 3.6153 | 3.5847 | 3.3243 | 5.5753 | 5.5437 | 5.5018 | 5.462 | 5.412 | 5.2651 | 5.2049 | 5.1396 | 5.0773 | 5.0212 | 4.858 | 5.0059 | 4.8896 | 5.1559 | 5.1141 | 5.0529 | 4.9988 | 4.9161 | 4.7488 | 4.6467 | 4.5671 | 4.461 | 4.3722
|  | AIRD | HT |  |  |  |  | 4.6367 | 4.5857 | 4.5429 | 4.4959 | 4.3551 | 4.2939 | 4.2418 | 4.1694 | 4.0949 | 4.0133 | 3.6847 | 3.5408 | 3.2824 | 5.6008 | 5.5712 | 5.5437 | 5.508 | 5.3733 | 5.3304 | 5.2937 | 5.2365 | 5.1824 | 5.1263 | 4.8927 | 4.9978 | 4.962 | 5.1763 | 5.1345 | 5.0967 | 5.0569 | 4.9069 | 4.8488 | 4.8029 | 4.7222 | 4.6416 | 4.5569
|  | AIRD | HE |  |  |  |  | 4.6357 | 4.5949 | 4.5643 | 4.5265 | 4.4806 | 4.351 | 4.3061 | 4.2408 | 4.1745 | 4.098 | 3.7316 | 3.5816 | 3.2804 | 5.5988 | 5.5702 | 5.5416 | 5.5069 | 5.4712 | 5.3314 | 5.2876 | 5.2263 | 5.1702 | 5.1059 | 4.812 | 4.9049 | 4.858 | 5.1743 | 5.1416 | 5.1151 | 5.0824 | 5.0416 | 4.8896 | 4.8529 | 4.7814 | 4.708 | 4.6324
|  | AIRD | CF |  |  |  |  | 4.6408 | 4.6112 | 4.5735 | 4.5469 | 4.5163 | 4.4786 | 4.3551 | 4.3194 | 4.2786 | 4.2367 | 3.9929 | 3.748 | 3.3273 | 5.6029 | 5.5876 | 5.56 | 5.5406 | 5.5222 | 5.4916 | 5.3682 | 5.3376 | 5.2978 | 5.262 | 5.0365 | 5.0049 | 4.7131 | 5.1784 | 5.1539 | 5.1243 | 5.0998 | 5.0753 | 5.0416 | 4.8998 | 4.8692 | 4.8192 | 4.7753
| PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0 | 0.31966 | 0.31864 | 0.3166 | 0.30843 | 0.29925 | 0.29721 | 0.29517 | 0.29619 | 0.29415 | 0.29109 | 0.28599 | 0.28497 | 0.25457 | 0.3107 | 0.30968 | 0.30866 | 0.30151 | 0.29437 | 0.29233 | 0.29437 | 0.29131 | 0.29335 | 0.29233 | 0.28927 | 0.3014 | 0.29732 | 0.31773 | 0.31671 | 0.31569 | 0.30752 | 0.29834 | 0.2963 | 0.29528 | 0.29528 | 0.29426 | 0.29222
|  | AIRIGH-NA-BRODAIG | EE |  |  |  |  | 0.31966 | 0.31864 | 0.3166 | 0.30843 | 0.29925 | 0.29721 | 0.29517 | 0.30027 | 0.29415 | 0.29211 | 0.28599 | 0.28599 | 0.25662 | 0.3107 | 0.30968 | 0.30866 | 0.30151 | 0.29437 | 0.29233 | 0.29437 | 0.29845 | 0.29539 | 0.29335 | 0.28927 | 0.3014 | 0.30038 | 0.31773 | 0.31671 | 0.31569 | 0.30752 | 0.29834 | 0.2963 | 0.29528 | 0.30038 | 0.29426 | 0.29222
|  | AIRIGH-NA-BRODAIG | HT |  |  |  |  | 0.3268 | 0.32374 | 0.3166 | 0.31558 | 0.31354 | 0.30639 | 0.30435 | 0.29619 | 0.29415 | 0.29109 | 0.29007 | 0.28497 | 0.25457 | 0.31784 | 0.3158 | 0.30866 | 0.30866 | 0.30866 | 0.30151 | 0.29947 | 0.29131 | 0.29335 | 0.29233 | 0.29131 | 0.30242 | 0.30242 | 0.32487 | 0.32283 | 0.31569 | 0.31467 | 0.31365 | 0.30548 | 0.30344 | 0.29528 | 0.29426 | 0.29222
|  | AIRIGH-NA-BRODAIG | HE |  |  |  |  | 0.3268 | 0.32374 | 0.31864 | 0.3166 | 0.3166 | 0.30843 | 0.30639 | 0.29823 | 0.29517 | 0.29619 | 0.29211 | 0.28701 | 0.25866 | 0.31784 | 0.3158 | 0.30968 | 0.30866 | 0.30866 | 0.30151 | 0.30151 | 0.29233 | 0.29335 | 0.29437 | 0.29233 | 0.30242 | 0.30242 | 0.32487 | 0.32283 | 0.31671 | 0.31569 | 0.31569 | 0.3065 | 0.30548 | 0.29732 | 0.2963 | 0.29528
|  | AIRIGH-NA-BRODAIG | CF |  |  |  |  | 0.3268 | 0.32476 | 0.3166 | 0.3166 | 0.3166 | 0.30843 | 0.30843 | 0.30741 | 0.29823 | 0.29823 | 0.29415 | 0.29007 | 0.25866 | 0.31784 | 0.31682 | 0.30866 | 0.30866 | 0.30866 | 0.30151 | 0.30151 | 0.30151 | 0.29335 | 0.29335 | 0.29539 | 0.30344 | 0.29732 | 0.32487 | 0.32385 | 0.31569 | 0.31569 | 0.31569 | 0.30752 | 0.30752 | 0.3065 | 0.29834 | 0.29834
| COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | NO | 1.219 | 2.5078 | 2.2394 | 1.9394 | 1.62 | 1.2088 | 0.77408 | 0.3149 | 0.016939 | -0.30959 | -0.63408 | -1.7922 | -2.4024 | -2.5127 | 3.5802 | 3.4373 | 3.27 | 3.0843 | 2.9006 | 2.6608 | 2.4159 | 2.2496 | 2.0578 | 1.8751 | 1.2792 | 0.95163 | 0.67204 | 3.0108 | 2.7894 | 2.5353 | 2.2384 | 1.9169 | 1.5149 | 1.1139 | 0.84653 | 0.54653 | 0.25878
|  | ALYTH | EE |  |  |  |  | 2.5312 | 2.2578 | 1.9598 | 1.62 | 1.2424 | 0.77408 | 0.3149 | 0.016939 | -0.30959 | -0.63408 | -1.7922 | -2.3606 | -2.479 | 3.5863 | 3.4373 | 3.27 | 3.0843 | 2.9006 | 2.6608 | 2.4159 | 2.2496 | 2.0578 | 1.8751 | 1.2792 | 0.95163 | 0.67204 | 3.0231 | 2.7904 | 2.5353 | 2.2384 | 1.9169 | 1.5149 | 1.1139 | 0.84653 | 0.54653 | 0.25878
|  | ALYTH | HT |  |  |  |  | 2.5078 | 2.2394 | 1.9394 | 1.62 | 1.2088 | 0.77714 | 0.45265 | 0.13327 | -0.21469 | -0.54224 | -1.7484 | -2.4024 | -2.5127 | 3.5802 | 3.4496 | 3.3006 | 3.1537 | 2.9598 | 2.7506 | 2.6078 | 2.4404 | 2.2608 | 2.1078 | 1.4486 | 1.1578 | 1.1108 | 3.0108 | 2.7894 | 2.5353 | 2.27 | 1.9261 | 1.5588 | 1.2822 | 0.99653 | 0.68735 | 0.41184
|  | ALYTH | HE |  |  |  |  | 2.5741 | 2.3486 | 2.1078 | 1.8404 | 1.4914 | 1.071 | 0.73633 | 0.48429 | 0.22306 | -0.0044898 | -1.0667 | -1.6861 | -1.9249 | 3.6312 | 3.5057 | 3.3659 | 3.2302 | 3.0557 | 2.8496 | 2.6873 | 2.5384 | 2.3894 | 2.2608 | 1.6098 | 1.2363 | 0.92918 | 3.07 | 2.8822 | 2.6761 | 2.4567 | 2.1618 | 1.8098 | 1.5282 | 1.2996 | 1.069 | 0.87612
|  | ALYTH | CF |  |  |  |  | 2.7965 | 2.618 | 2.422 | 2.2322 | 1.9914 | 1.722 | 1.5129 | 1.3476 | 1.1761 | 0.95265 | 0.088367 | -0.68612 | -1.3188 | 3.8027 | 3.6873 | 3.572 | 3.4659 | 3.3343 | 3.1843 | 3.0547 | 2.9527 | 2.8373 | 2.6976 | 2.0863 | 1.4088 | 0.68939 | 3.2751 | 3.1231 | 2.9557 | 2.7976 | 2.5945 | 2.3659 | 2.1853 | 2.0424 | 1.8914 | 1.6976
| FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | NO | 0.224 | 3.8092 | 3.7265 | 3.6439 | 3.5429 | 3.4306 | 3.3449 | 3.202 | 3.0347 | 2.8765 | 2.7918 | 2.4592 | 2.3388 | 2.3051 | 4.7806 | 4.7347 | 4.6918 | 4.6367 | 4.5776 | 4.5316 | 4.4459 | 4.3398 | 4.2367 | 4.1908 | 3.9867 | 3.8816 | 3.4684 | 4.4388 | 4.3571 | 4.2786 | 4.1806 | 4.0745 | 3.9918 | 3.8592 | 3.701 | 3.5531 | 3.4694
|  | ANNAT | EE |  |  |  |  | 3.8092 | 3.7265 | 3.6439 | 3.5429 | 3.4306 | 3.3449 | 3.202 | 3.0347 | 2.8765 | 2.7918 | 2.4592 | 2.3898 | 2.3582 | 4.7806 | 4.7347 | 4.6918 | 4.6367 | 4.5776 | 4.5316 | 4.4459 | 4.3398 | 4.2367 | 4.1908 | 3.9867 | 3.8816 | 3.702 | 4.4388 | 4.3571 | 4.2786 | 4.1806 | 4.0745 | 3.9918 | 3.8592 | 3.701 | 3.5531 | 3.4694
|  | ANNAT | HT |  |  |  |  | 3.8469 | 3.7796 | 3.7082 | 3.6224 | 3.5541 | 3.4582 | 3.351 | 3.2214 | 3.1357 | 3.0153 | 2.548 | 2.3388 | 2.3051 | 4.8 | 4.7653 | 4.7296 | 4.6847 | 4.649 | 4.601 | 4.5439 | 4.4765 | 4.4367 | 4.3653 | 4.0745 | 3.9612 | 3.9439 | 4.4745 | 4.4092 | 4.3388 | 4.2561 | 4.1867 | 4.0949 | 3.9949 | 3.8714 | 3.7959 | 3.6806
|  | ANNAT | HE |  |  |  |  | 3.8469 | 3.7949 | 3.7408 | 3.6694 | 3.6153 | 3.5388 | 3.448 | 3.3357 | 3.2663 | 3.1592 | 2.6286 | 2.4949 | 2.4755 | 4.801 | 4.7704 | 4.7408 | 4.701 | 4.6704 | 4.6265 | 4.5724 | 4.5112 | 4.4694 | 4.4112 | 4.0847 | 3.9337 | 3.7602 | 4.4745 | 4.4255 | 4.3704 | 4.301 | 4.249 | 4.1745 | 4.0898 | 3.9796 | 3.9163 | 3.8133
|  | ANNAT | CF |  |  |  |  | 3.8582 | 3.8153 | 3.7582 | 3.7092 | 3.6439 | 3.6071 | 3.5388 | 3.4673 | 3.3878 | 3.3102 | 2.952 | 2.6612 | 2.4969 | 4.8082 | 4.7816 | 4.75 | 4.7224 | 4.6878 | 4.6612 | 4.6214 | 4.5745 | 4.5255 | 4.4776 | 4.2224 | 3.8939 | 3.4684 | 4.4857 | 4.4449 | 4.3929 | 4.3459 | 4.2867 | 4.2469 | 4.1827 | 4.1163 | 4.0449 | 3.9735
| KILLIN | ARDCHYLE | MINIMUM HEADROOM | NN 52734 29223 | YES | YES | 0 | 0.10678 | 0.10576 | 0.10576 | 0.098612 | 0.098612 | 0.098612 | 0.098612 | 0.091469 | 0.090449 | 0.090449 | 0.083306 | 0.081265 | 0.072265 | 0.10288 | 0.10288 | 0.10288 | 0.095735 | 0.095735 | 0.095735 | 0.095735 | 0.088592 | 0.087571 | 0.087571 | 0.080429 | 0.083908 | 0.083908 | 0.021663 | 0.021663 | 0.021663 | 0.01452 | 0.01452 | 0.01452 | 0.01452 | 0.0073776 | 0.0063571 | 0.0063571
|  | ARDCHYLE | EE |  |  |  |  | 0.10678 | 0.10576 | 0.10576 | 0.098612 | 0.098612 | 0.098612 | 0.098612 | 0.091469 | 0.090449 | 0.090449 | 0.083306 | 0.081265 | 0.072265 | 0.10288 | 0.10288 | 0.10288 | 0.095735 | 0.095735 | 0.095735 | 0.095735 | 0.088592 | 0.087571 | 0.087571 | 0.080429 | 0.083908 | 0.083908 | 0.021663 | 0.021663 | 0.021663 | 0.01452 | 0.01452 | 0.01452 | 0.01452 | 0.0073776 | 0.0063571 | 0.0063571
|  | ARDCHYLE | HT |  |  |  |  | 0.10678 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.098612 | 0.098612 | 0.098612 | 0.097592 | 0.097592 | 0.083306 | 0.081265 | 0.072265 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.095735 | 0.095735 | 0.095735 | 0.094714 | 0.094714 | 0.080429 | 0.083908 | 0.083908 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.01452 | 0.01452 | 0.01452 | 0.0135 | 0.0135
|  | ARDCHYLE | HE |  |  |  |  | 0.10678 | 0.10678 | 0.10576 | 0.10576 | 0.10576 | 0.098612 | 0.098612 | 0.098612 | 0.098612 | 0.098612 | 0.090449 | 0.083306 | 0.072265 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.095735 | 0.095735 | 0.095735 | 0.095735 | 0.095735 | 0.087571 | 0.084929 | 0.083908 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.01452 | 0.01452 | 0.01452 | 0.01452 | 0.01452
|  | ARDCHYLE | CF |  |  |  |  | 0.10678 | 0.10678 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.098612 | 0.098612 | 0.098612 | 0.098612 | 0.090449 | 0.083306 | 0.072265 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.095735 | 0.095735 | 0.095735 | 0.095735 | 0.087571 | 0.084929 | 0.083908 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.01452 | 0.01452 | 0.01452 | 0.01452
| NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 0.315 | 4.2735 | 4.2031 | 4.1102 | 4.0429 | 3.9571 | 3.699 | 3.3245 | 2.9398 | 2.5796 | 2.199 | 1.7755 | 1.6878 | 1.652 | 5.2551 | 5.2214 | 5.1673 | 5.1296 | 5.0776 | 4.9714 | 4.7908 | 4.598 | 4.4276 | 4.2388 | 3.9184 | 3.8265 | 3.4714 | 4.9112 | 4.8439 | 4.7653 | 4.6969 | 4.6194 | 4.4276 | 4.1204 | 3.8031 | 3.5122 | 3.199
|  | ARDERSIER | EE |  |  |  |  | 4.2735 | 4.2031 | 4.1102 | 4.0429 | 3.9571 | 3.8531 | 3.7684 | 3.3765 | 2.9694 | 2.5796 | 1.7755 | 1.7296 | 1.7102 | 5.2551 | 5.2214 | 5.1673 | 5.1296 | 5.0776 | 5.0163 | 4.9663 | 4.752 | 4.5388 | 4.3418 | 3.9184 | 3.8265 | 3.6786 | 4.9112 | 4.8439 | 4.7653 | 4.6969 | 4.6194 | 4.5286 | 4.4418 | 4.1041 | 3.7633 | 3.4418
|  | ARDERSIER | HT |  |  |  |  | 4.301 | 4.2439 | 4.1806 | 4.1173 | 4.051 | 3.699 | 3.3245 | 2.9398 | 2.5796 | 2.199 | 1.8143 | 1.6878 | 1.652 | 5.2704 | 5.252 | 5.2153 | 5.1816 | 5.148 | 4.9714 | 4.7908 | 4.598 | 4.4276 | 4.2388 | 3.9959 | 3.9327 | 3.9143 | 4.9388 | 4.8847 | 4.8245 | 4.7663 | 4.7061 | 4.4276 | 4.1204 | 3.8031 | 3.5122 | 3.199
|  | ARDERSIER | HE |  |  |  |  | 4.299 | 4.2459 | 4.1898 | 4.1316 | 4.0673 | 4.002 | 3.9173 | 3.7612 | 3.6112 | 3.4765 | 2.599 | 2.0827 | 1.748 | 5.2684 | 5.251 | 5.2194 | 5.1918 | 5.151 | 5.1255 | 5.0786 | 4.9816 | 4.8806 | 4.8061 | 4.2969 | 3.9898 | 3.701 | 4.9367 | 4.8867 | 4.8337 | 4.7796 | 4.7184 | 4.6571 | 4.5755 | 4.4337 | 4.2959 | 4.1714
|  | ARDERSIER | CF |  |  |  |  | 4.3061 | 4.2694 | 4.2306 | 4.1929 | 4.1388 | 4.1082 | 4.05 | 3.9888 | 3.8561 | 3.7194 | 3.0398 | 2.3714 | 1.8031 | 5.2714 | 5.2571 | 5.2367 | 5.2112 | 5.1796 | 5.1561 | 5.1194 | 5.0786 | 5 | 4.9204 | 4.4918 | 4.0071 | 3.4714 | 4.9398 | 4.9051 | 4.8724 | 4.8388 | 4.7949 | 4.7622 | 4.7122 | 4.651 | 4.5398 | 4.4184
| FORT AUGUSTUS | ARDOCHY | MINIMUM HEADROOM | NH 47714 12561 | YES | YES | 0 | 0.118 | 0.11086 | 0.10882 | 0.10882 | 0.10167 | 0.10167 | 0.09351 | 0.09351 | 0.091469 | 0.091469 | 0.091469 | 0.094531 | 0.085531 | 0.109 | 0.10186 | 0.10084 | 0.10084 | 0.093694 | 0.093694 | 0.085531 | 0.085531 | 0.086551 | 0.085531 | 0.086551 | 0.095133 | 0.094112 | 0.1135 | 0.10636 | 0.10534 | 0.10534 | 0.098194 | 0.098194 | 0.08901 | 0.08901 | 0.086969 | 0.086969
|  | ARDOCHY | EE |  |  |  |  | 0.118 | 0.11086 | 0.10984 | 0.10984 | 0.10167 | 0.10167 | 0.09351 | 0.09351 | 0.091469 | 0.091469 | 0.095551 | 0.095551 | 0.085531 | 0.109 | 0.10186 | 0.10186 | 0.10186 | 0.093694 | 0.093694 | 0.085531 | 0.085531 | 0.086551 | 0.086551 | 0.091653 | 0.096153 | 0.095133 | 0.1135 | 0.10636 | 0.10534 | 0.10534 | 0.098194 | 0.098194 | 0.08901 | 0.08901 | 0.086969 | 0.086969
|  | ARDOCHY | HT |  |  |  |  | 0.118 | 0.118 | 0.10882 | 0.10984 | 0.10984 | 0.10984 | 0.10167 | 0.10065 | 0.10065 | 0.09351 | 0.095551 | 0.094531 | 0.085531 | 0.109 | 0.109 | 0.10084 | 0.10186 | 0.10186 | 0.10186 | 0.093694 | 0.092673 | 0.092673 | 0.085531 | 0.091653 | 0.095133 | 0.095133 | 0.1135 | 0.1135 | 0.10534 | 0.10534 | 0.10534 | 0.10534 | 0.098194 | 0.096153 | 0.096153 | 0.08901
|  | ARDOCHY | HE |  |  |  |  | 0.118 | 0.118 | 0.11086 | 0.10882 | 0.10984 | 0.10984 | 0.10269 | 0.10167 | 0.10167 | 0.09351 | 0.095551 | 0.095551 | 0.086551 | 0.109 | 0.109 | 0.10186 | 0.10084 | 0.10186 | 0.10186 | 0.094714 | 0.093694 | 0.093694 | 0.085531 | 0.091653 | 0.096153 | 0.096153 | 0.1135 | 0.1135 | 0.10636 | 0.10534 | 0.10534 | 0.10534 | 0.098194 | 0.098194 | 0.098194 | 0.08901
|  | ARDOCHY | CF |  |  |  |  | 0.118 | 0.118 | 0.118 | 0.11086 | 0.11086 | 0.10882 | 0.10882 | 0.10882 | 0.10167 | 0.10065 | 0.091469 | 0.095551 | 0.086551 | 0.109 | 0.109 | 0.109 | 0.10186 | 0.10186 | 0.10084 | 0.10084 | 0.10084 | 0.093694 | 0.092673 | 0.086551 | 0.096153 | 0.094112 | 0.1135 | 0.1135 | 0.1135 | 0.10636 | 0.10636 | 0.10534 | 0.10534 | 0.10534 | 0.098194 | 0.097173
| FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | NO | 0.128 | 2.3224 | 2.2949 | 2.2684 | 2.25 | 2.2133 | 2.1898 | 2.1439 | 2.0929 | 2.0755 | 2.0367 | 1.9541 | 1.9255 | 1.6934 | 2.1801 | 2.1597 | 2.1413 | 2.1301 | 2.1046 | 2.0862 | 2.0587 | 2.0189 | 2.0077 | 1.9791 | 1.9158 | 2.0028 | 1.8885 | 2.261 | 2.2355 | 2.212 | 2.1906 | 2.1579 | 2.1344 | 2.0926 | 2.0426 | 2.0242 | 1.9885
|  | ARISAIG | EE |  |  |  |  | 2.3224 | 2.2949 | 2.2684 | 2.25 | 2.2133 | 2.1898 | 2.1439 | 2.0929 | 2.0755 | 2.0367 | 1.9541 | 1.9418 | 1.7077 | 2.1801 | 2.1597 | 2.1413 | 2.1301 | 2.1046 | 2.0862 | 2.0587 | 2.0189 | 2.0077 | 1.9791 | 1.9158 | 2.0028 | 1.9559 | 2.261 | 2.2355 | 2.212 | 2.1906 | 2.1579 | 2.1344 | 2.0926 | 2.0426 | 2.0242 | 1.9885
|  | ARISAIG | HT |  |  |  |  | 2.3367 | 2.3163 | 2.2969 | 2.2745 | 2.248 | 2.2327 | 2.202 | 2.1622 | 2.1408 | 2.1031 | 1.9806 | 1.9255 | 1.6934 | 2.1923 | 2.176 | 2.1648 | 2.1526 | 2.1332 | 2.124 | 2.1046 | 2.0781 | 2.0617 | 2.0362 | 1.9495 | 2.0273 | 2.0242 | 2.2753 | 2.2569 | 2.2395 | 2.2181 | 2.1936 | 2.1793 | 2.1487 | 2.111 | 2.0895 | 2.0548
|  | ARISAIG | HE |  |  |  |  | 2.3327 | 2.3214 | 2.302 | 2.2857 | 2.2602 | 2.252 | 2.2245 | 2.1878 | 2.1684 | 2.1347 | 2 | 1.9653 | 1.7332 | 2.1903 | 2.1811 | 2.1679 | 2.1556 | 2.1372 | 2.1311 | 2.1117 | 2.0842 | 2.0709 | 2.0474 | 1.9505 | 2.0191 | 1.9773 | 2.2732 | 2.263 | 2.2426 | 2.2283 | 2.2048 | 2.1946 | 2.1671 | 2.1344 | 2.1151 | 2.0834
|  | ARISAIG | CF |  |  |  |  | 2.3378 | 2.3235 | 2.3102 | 2.2929 | 2.2796 | 2.2582 | 2.251 | 2.2265 | 2.2041 | 2.1929 | 2.0969 | 1.998 | 1.7352 | 2.1923 | 2.1821 | 2.173 | 2.1587 | 2.1505 | 2.1332 | 2.1291 | 2.1107 | 2.0923 | 2.0832 | 2.0015 | 2.0069 | 1.8885 | 2.2773 | 2.263 | 2.2508 | 2.2344 | 2.2202 | 2.2018 | 2.1936 | 2.1691 | 2.1477 | 2.1385
| ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 4.628 | 0.50332 | 25.6737 | 24.4176 | 23.3288 | 22.4329 | 21.3666 | 20.2411 | 18.9329 | 17.6492 | 16.5952 | 12.6503 | 11.1054 | -16.4293 | 28.0543 | 27.2094 | 26.2727 | 25.5788 | 25.0533 | 24.4115 | 23.7329 | 22.8043 | 21.9115 | 21.1819 | 18.6319 | -7.8814 | 17.6707 | 27.9064 | 26.8574 | 25.7003 | 24.7186 | 23.935 | 23.0156 | 22.0472 | 20.8758 | 19.7401 | 18.8043
|  | ASHGROVE | EE |  |  |  |  | 0.50332 | 25.6778 | 24.4401 | 23.4094 | 22.5227 | 21.4982 | 20.9166 | 19.938 | 18.9645 | 17.9401 | 13.1105 | 11.3645 | -16.3783 | 28.0543 | 27.2135 | 26.2931 | 25.5952 | 25.0839 | 24.4666 | 24.1543 | 23.4952 | 22.8237 | 22.0952 | 18.6319 | -7.8814 | 17.738 | 27.9064 | 26.8574 | 25.7105 | 24.7829 | 24.0319 | 23.1523 | 22.6543 | 21.787 | 20.9248 | 20.0145
|  | ASHGROVE | HT |  |  |  |  | 0.52475 | 25.6737 | 24.4176 | 23.3288 | 22.4329 | 21.3666 | 20.2411 | 18.9329 | 17.6492 | 16.5952 | 12.6503 | 11.1054 | -16.4293 | 28.0594 | 27.2094 | 26.2727 | 25.5788 | 25.0533 | 24.4115 | 23.7329 | 22.8043 | 21.9115 | 21.1819 | 18.737 | -7.4201 | 18.8727 | 27.9299 | 26.8625 | 25.7003 | 24.7186 | 23.935 | 23.0156 | 22.0472 | 20.8758 | 19.7401 | 18.8043
|  | ASHGROVE | HE |  |  |  |  | 0.55944 | 25.8554 | 24.7523 | 23.8574 | 23.1452 | 22.3043 | 21.6533 | 20.788 | 19.9064 | 19.2431 | 14.7064 | 12.9329 | -15.0559 | 28.0819 | 27.2594 | 26.386 | 25.7635 | 25.3799 | 24.8584 | 24.4492 | 23.8299 | 23.187 | 22.6696 | 19.2625 | -7.2814 | 18.2605 | 27.9625 | 27.0258 | 25.9982 | 25.1911 | 24.5686 | 23.8523 | 23.3033 | 22.5462 | 21.7737 | 21.1839
|  | ASHGROVE | CF |  |  |  |  | 0.66455 | 26.0911 | 25.1411 | 24.4268 | 23.9278 | 23.3329 | 22.9513 | 22.585 | 22.1768 | 21.6992 | 17.9574 | 14.6492 | -13.7069 | 28.1339 | 27.3748 | 26.5829 | 26.0839 | 25.8533 | 25.4962 | 25.2309 | 24.937 | 24.6166 | 24.236 | 21.3411 | -7.062 | 17.6707 | 28.0605 | 27.2421 | 26.3533 | 25.7156 | 25.2901 | 24.7799 | 24.4707 | 24.1584 | 23.8094 | 23.4023
| MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | NO | 1.063 | 3.6971 | 3.3113 | 18.994 | 18.5399 | 18.1062 | 17.6603 | 17.4205 | 16.8185 | 16.2328 | 15.6726 | 13.7042 | 13.1471 | -3.0611 | 6.9522 | 21.3389 | 21.0909 | 20.8164 | 20.5399 | 20.246 | 20.2022 | 19.842 | 19.494 | 19.1746 | 18.0481 | 2.9777 | 1.145 | 20.3848 | 20.043 | 19.6562 | 19.2215 | 18.7909 | 18.3409 | 18.2154 | 17.643 | 17.0868 | 16.5766
|  | ASHLUDIE | EE |  |  |  |  | 3.6971 | 3.3113 | 18.994 | 18.5399 | 18.1062 | 17.6603 | 17.4205 | 16.8185 | 16.2328 | 15.6726 | 13.7042 | 13.5113 | -2.6264 | 6.9522 | 21.3389 | 21.0909 | 20.8164 | 20.5399 | 20.246 | 20.2022 | 19.842 | 19.494 | 19.1746 | 18.0481 | 2.9777 | 2.2266 | 20.3848 | 20.043 | 19.6562 | 19.2215 | 18.7909 | 18.3409 | 18.2154 | 17.643 | 17.0868 | 16.5766
|  | ASHLUDIE | HT |  |  |  |  | 3.7828 | 3.4236 | 19.1389 | 18.7246 | 18.3868 | 17.9981 | 17.4705 | 16.892 | 16.6603 | 16.093 | 13.9195 | 13.1471 | -3.0611 | 7.043 | 21.4664 | 21.2736 | 21.0562 | 20.8807 | 20.6624 | 20.3746 | 20.0511 | 20.0317 | 19.7348 | 18.5389 | 3.5215 | 3.4542 | 20.5052 | 20.194 | 19.8593 | 19.4868 | 19.1756 | 18.8052 | 18.3154 | 17.7695 | 17.6532 | 17.1511
|  | ASHLUDIE | HE |  |  |  |  | 3.8124 | 3.5593 | 19.395 | 19.1093 | 18.8899 | 18.6266 | 18.2287 | 17.7664 | 17.6562 | 17.2338 | 15.1562 | 14.0715 | -2.2376 | 7.0552 | 21.495 | 21.3338 | 21.1511 | 21.0042 | 20.8185 | 20.5705 | 20.2695 | 20.2807 | 20.0175 | 18.6501 | 3.194 | 2.4073 | 20.5338 | 20.294 | 20.0552 | 19.7787 | 19.5654 | 19.294 | 18.9093 | 18.4511 | 18.4409 | 18.044
|  | ASHLUDIE | CF |  |  |  |  | 3.8695 | 3.7052 | 19.6175 | 19.4154 | 19.246 | 19.1103 | 18.9266 | 18.7113 | 18.493 | 18.5858 | 17.2766 | 15.6379 | -1.8825 | 7.0715 | 21.5583 | 21.4358 | 21.292 | 21.1552 | 21.0389 | 20.8756 | 20.6777 | 20.4858 | 20.5603 | 19.4277 | 3.1838 | 1.145 | 20.5787 | 20.4236 | 20.2501 | 20.0532 | 19.8705 | 19.7297 | 19.5317 | 19.2909 | 19.0562 | 19.2083
| GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | NO | 0.212 | -0.50816 | -0.55714 | -0.61837 | -0.6949 | -0.74694 | -0.82755 | -0.91735 | -1.0296 | -1.0959 | -1.1857 | -1.3908 | -1.4673 | -1.4888 | 0.022449 | -0.0071429 | -0.044898 | -0.094898 | -0.13265 | -0.18571 | -0.24592 | -0.32143 | -0.36327 | -0.41939 | -0.57857 | -0.65204 | -0.88061 | -0.36837 | -0.41327 | -0.47245 | -0.54388 | -0.59388 | -0.67143 | -0.75612 | -0.86633 | -0.92857 | -1.0112
|  | AULTBEA | EE |  |  |  |  | -0.50816 | -0.55714 | -0.61837 | -0.6949 | -0.74694 | -0.82755 | -0.91735 | -1.0296 | -1.0959 | -1.1857 | -1.3908 | -1.4296 | -1.4551 | 0.022449 | -0.0071429 | -0.044898 | -0.094898 | -0.13265 | -0.18571 | -0.24592 | -0.32143 | -0.36327 | -0.41939 | -0.57857 | -0.65204 | -0.76531 | -0.36837 | -0.41327 | -0.47245 | -0.54388 | -0.59388 | -0.67143 | -0.75612 | -0.86633 | -0.92857 | -1.0112
|  | AULTBEA | HT |  |  |  |  | -0.47551 | -0.52041 | -0.56224 | -0.61837 | -0.66837 | -0.73469 | -0.8102 | -0.86633 | -0.93673 | -1.0173 | -1.3214 | -1.4673 | -1.4888 | 0.046939 | 0.022449 | -0.0030612 | -0.036735 | -0.072449 | -0.11122 | -0.15918 | -0.19592 | -0.2398 | -0.29184 | -0.49082 | -0.58061 | -0.59388 | -0.33673 | -0.37755 | -0.41735 | -0.47041 | -0.51735 | -0.58163 | -0.65306 | -0.70408 | -0.77143 | -0.85
|  | AULTBEA | HE |  |  |  |  | -0.47449 | -0.50918 | -0.55612 | -0.58878 | -0.62857 | -0.67959 | -0.74694 | -0.79184 | -0.85306 | -0.92347 | -1.2551 | -1.3439 | -1.3561 | 0.046939 | 0.02551 | -0.005102 | -0.028571 | -0.055102 | -0.088776 | -0.13469 | -0.16735 | -0.2102 | -0.2602 | -0.48571 | -0.59184 | -0.69184 | -0.33571 | -0.36735 | -0.41429 | -0.44388 | -0.48061 | -0.53265 | -0.59592 | -0.63673 | -0.69388 | -0.76224
|  | AULTBEA | CF |  |  |  |  | -0.46735 | -0.50306 | -0.53673 | -0.56327 | -0.6051 | -0.63776 | -0.68367 | -0.73776 | -0.7602 | -0.80918 | -1.0684 | -1.2459 | -1.3541 | 0.052041 | 0.030612 | 0.0071429 | -0.0081633 | -0.035714 | -0.059184 | -0.091837 | -0.13367 | -0.15102 | -0.18673 | -0.40102 | -0.61735 | -0.88061 | -0.32653 | -0.36327 | -0.3949 | -0.41837 | -0.4602 | -0.48878 | -0.53367 | -0.58571 | -0.60612 | -0.65306
| BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 5.98 | 2.57 | 2.221 | 1.8282 | 1.4282 | 0.94043 | 0.41594 | -0.071814 | -0.69732 | -1.2769 | -1.7106 | -3.8075 | -4.88 | -4.9392 | 6.3088 | 6.0884 | 5.8068 | 5.5068 | 5.1659 | 4.8027 | 4.4241 | 3.9598 | 3.5486 | 3.2159 | 1.4476 | 0.64655 | 0.58941 | 4.2394 | 3.9017 | 3.5057 | 3.0945 | 2.6272 | 2.1261 | 1.618 | 0.99553 | 0.44043 | -0.008549
|  | AVIEMORE | EE |  |  |  |  | 2.57 | 2.221 | 1.8282 | 1.4282 | 0.94043 | 0.41594 | -0.071814 | -0.69732 | -1.2769 | -1.7106 | -2.8126 | -3.0392 | -3.1626 | 6.3088 | 6.0884 | 5.8068 | 5.5068 | 5.1659 | 4.8027 | 4.4241 | 3.9598 | 3.5486 | 3.2159 | 2.2812 | 2.1425 | 1.8374 | 4.2394 | 3.9017 | 3.5057 | 3.0945 | 2.6272 | 2.1261 | 1.618 | 0.99553 | 0.44043 | -0.008549
|  | AVIEMORE | HT |  |  |  |  | 2.7231 | 2.4282 | 2.1251 | 1.7884 | 1.3976 | 0.95676 | 0.50676 | 0.022063 | -0.40447 | -0.71569 | -2.28 | -3.0116 | -3.0708 | 6.4221 | 6.2466 | 6.0721 | 5.8761 | 5.6455 | 5.3945 | 5.1221 | 4.7986 | 4.4976 | 4.217 | 2.9608 | 2.4047 | 2.3721 | 4.3915 | 4.1384 | 3.8721 | 3.5741 | 3.221 | 2.8312 | 2.4251 | 1.9843 | 1.5935 | 1.2547
|  | AVIEMORE | HE |  |  |  |  | 2.6986 | 2.4047 | 2.1078 | 1.7649 | 1.3619 | 0.94757 | 0.51492 | 0.0016551 | -0.5361 | -1.1208 | -3.8075 | -4.88 | -4.9392 | 6.4017 | 6.2149 | 6.0037 | 5.7394 | 5.4323 | 5.0966 | 4.7241 | 4.2659 | 3.8323 | 3.4068 | 1.4476 | 0.64655 | 0.58941 | 4.37 | 4.0884 | 3.7721 | 3.419 | 3.0047 | 2.5455 | 2.0496 | 1.4415 | 0.86594 | 0.30472
|  | AVIEMORE | CF |  |  |  |  | 2.8037 | 2.6149 | 2.3649 | 2.117 | 1.821 | 1.4904 | 1.1863 | 0.87206 | 0.52512 | 0.25778 | -1.1953 | -2.9514 | -4.0483 | 6.4659 | 6.3455 | 6.1894 | 6.0363 | 5.8527 | 5.6435 | 5.4343 | 5.2159 | 4.9751 | 4.7282 | 3.2731 | 1.9915 | 1.0333 | 4.4506 | 4.2904 | 4.0721 | 3.8598 | 3.5976 | 3.3047 | 3.0353 | 2.7547 | 2.4312 | 2.1139
| ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | NO | 0.122 | -1.7592 | -1.9 | -2.0531 | -2.2224 | -2.4 | -2.5612 | -2.7837 | -3.1102 | -3.3857 | -3.6776 | -4.4449 | -4.9122 | -4.949 | -0.59184 | -0.68163 | -0.77857 | -0.89286 | -1.0224 | -1.1255 | -1.2816 | -1.501 | -1.6653 | -1.8449 | -2.3439 | -2.6837 | -3.248 | -1.1327 | -1.2684 | -1.4122 | -1.5745 | -1.752 | -1.902 | -2.1194 | -2.4286 | -2.6776 | -2.9439
|  | BALALDIE | EE |  |  |  |  | -1.7592 | -1.9 | -2.0531 | -2.2224 | -2.4 | -2.5612 | -2.7837 | -3.1102 | -3.3857 | -3.6776 | -4.4031 | -4.5122 | -4.5653 | -0.59184 | -0.68163 | -0.77857 | -0.89286 | -1.0224 | -1.1255 | -1.2816 | -1.501 | -1.6653 | -1.8449 | -2.3439 | -2.5204 | -2.7643 | -1.1327 | -1.2684 | -1.4122 | -1.5745 | -1.752 | -1.902 | -2.1194 | -2.4286 | -2.6776 | -2.9439
|  | BALALDIE | HT |  |  |  |  | -1.7041 | -1.8224 | -1.9469 | -2.0867 | -2.2112 | -2.4255 | -2.6643 | -2.9071 | -3.1418 | -3.3847 | -4.1714 | -4.5755 | -4.6255 | -0.53571 | -0.60306 | -0.67653 | -0.76327 | -0.8398 | -0.96224 | -1.1031 | -1.2388 | -1.3847 | -1.5398 | -2.0918 | -2.3459 | -2.3714 | -1.0755 | -1.1837 | -1.299 | -1.4306 | -1.549 | -1.7429 | -1.9582 | -2.1704 | -2.3867 | -2.6163
|  | BALALDIE | HE |  |  |  |  | -1.7102 | -1.8102 | -1.9204 | -2.0459 | -2.152 | -2.2878 | -2.452 | -2.6867 | -2.9357 | -3.1959 | -4.4449 | -4.9122 | -4.949 | -0.54286 | -0.60816 | -0.68061 | -0.76735 | -0.84082 | -0.93673 | -1.0561 | -1.2 | -1.3612 | -1.5316 | -2.3367 | -2.6837 | -2.8561 | -1.0827 | -1.1745 | -1.2765 | -1.399 | -1.502 | -1.6337 | -1.7949 | -2.0041 | -2.2357 | -2.4745
|  | BALALDIE | CF |  |  |  |  | -1.6867 | -1.7622 | -1.8622 | -1.951 | -2.0469 | -2.1286 | -2.2276 | -2.352 | -2.5265 | -2.6837 | -3.5704 | -4.2449 | -4.8898 | -0.52551 | -0.57143 | -0.63673 | -0.6949 | -0.76735 | -0.82347 | -0.89796 | -1 | -1.1153 | -1.2133 | -1.8898 | -2.5347 | -3.248 | -1.0592 | -1.1286 | -1.2184 | -1.302 | -1.3918 | -1.4714 | -1.5673 | -1.6908 | -1.849 | -1.9796
| ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 0.745 | 4.7768 | 4.6432 | 4.4605 | 4.1626 | 3.9768 | 3.5023 | 3.2626 | 2.9993 | 2.6881 | 2.336 | 0.35337 | -1.2232 | -3.1992 | 5.2029 | 5.1273 | 4.9835 | 4.7222 | 4.6161 | 4.1376 | 3.9539 | 3.7161 | 3.4712 | 3.0937 | 1.2345 | -0.15556 | -1.8331 | 5.0924 | 4.9761 | 4.7608 | 4.4587 | 4.3077 | 3.7669 | 3.5557 | 3.323 | 3.0812 | 2.6271
|  | BALBEGGIE | EE |  |  |  |  | 4.7768 | 4.6432 | 4.4789 | 4.3268 | 4.0401 | 3.6452 | 3.3452 | 3.0666 | 2.6881 | 2.336 | 0.98194 | -0.43847 | -1.6349 | 5.2029 | 5.1273 | 5.0263 | 4.9386 | 4.712 | 4.36 | 4.1559 | 3.9773 | 3.6784 | 3.4141 | 2.3651 | 1.1373 | 0.34852 | 5.0924 | 4.9761 | 4.8455 | 4.7097 | 4.4465 | 4.0587 | 3.7597 | 3.5026 | 3.1189 | 2.771
|  | BALBEGGIE | HT |  |  |  |  | 4.8381 | 4.7044 | 4.4605 | 4.1626 | 3.9768 | 3.5023 | 3.2626 | 2.9993 | 2.7442 | 2.385 | 0.81969 | -0.88541 | -2.7502 | 5.2508 | 5.1814 | 4.9835 | 4.7222 | 4.6161 | 4.1376 | 3.9855 | 3.811 | 3.66 | 3.4222 | 2.1722 | 0.71995 | -0.69332 | 5.1251 | 5.0097 | 4.7608 | 4.4587 | 4.3077 | 3.7669 | 3.5557 | 3.323 | 3.1138 | 2.772
|  | BALBEGGIE | HE |  |  |  |  | 4.8421 | 4.7493 | 4.5656 | 4.3217 | 4.1238 | 3.6748 | 3.3942 | 3.1044 | 2.8034 | 2.385 | 0.35337 | -1.2232 | -3.1992 | 5.2498 | 5.1947 | 5.0294 | 4.7998 | 4.6457 | 4.1712 | 3.9539 | 3.7161 | 3.4712 | 3.0937 | 1.2345 | -0.15556 | -1.8331 | 5.1261 | 5.0475 | 4.8608 | 4.6077 | 4.4302 | 3.9118 | 3.6455 | 3.3699 | 3.0812 | 2.6271
|  | BALBEGGIE | CF |  |  |  |  | 4.8636 | 4.8044 | 4.7156 | 4.6523 | 4.5064 | 4.2952 | 4.1503 | 3.9687 | 3.7993 | 3.5707 | 2.5758 | 1.636 | 0.37939 | 5.2641 | 5.2253 | 5.1661 | 5.1243 | 4.9988 | 4.7978 | 4.6753 | 4.5324 | 4.3937 | 4.2069 | 3.3671 | 2.8067 | 2.0434 | 5.1485 | 5.0995 | 5.0383 | 4.9863 | 4.8506 | 4.6444 | 4.4985 | 4.3444 | 4.1965 | 3.9699
| MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | NO | 0.947 | 10.6014 | 10.0331 | 9.3382 | 8.5739 | 7.5678 | 6.4657 | 5.2851 | 3.9463 | 2.7137 | 1.682 | -1.6812 | -2.6567 | -2.821 | 13.1627 | 12.7116 | 12.1341 | 11.4892 | 10.5882 | 9.578 | 8.6443 | 7.5739 | 6.5943 | 5.7667 | 3.1392 | 2.4014 | 0.67184 | 12.3167 | 11.8116 | 11.1882 | 10.4922 | 9.5565 | 8.5096 | 7.4749 | 6.2688 | 5.1147 | 4.1106
|  | BALDOVIE | EE |  |  |  |  | 10.6555 | 10.0902 | 9.4555 | 8.7576 | 7.8698 | 6.8688 | 5.7963 | 4.5627 | 3.4106 | 2.2473 | -1.6812 | -2.3424 | -2.4659 | 13.2188 | 12.7586 | 12.2382 | 11.6463 | 10.8545 | 9.9484 | 9.0616 | 8.0739 | 7.1514 | 6.2076 | 3.1392 | 2.4014 | 1.478 | 12.379 | 11.879 | 11.2953 | 10.6331 | 9.7871 | 8.8412 | 7.9463 | 6.8208 | 5.7535 | 4.682
|  | BALDOVIE | HT |  |  |  |  | 10.6014 | 10.0331 | 9.3382 | 8.5739 | 7.5678 | 6.4657 | 5.2851 | 3.9463 | 2.7137 | 1.682 | -1.6271 | -2.6567 | -2.821 | 13.1627 | 12.7116 | 12.1341 | 11.4892 | 10.5882 | 9.578 | 8.6443 | 7.5739 | 6.5943 | 5.7667 | 3.6729 | 3.1729 | 3.081 | 12.3167 | 11.8116 | 11.1882 | 10.4922 | 9.5565 | 8.5096 | 7.4749 | 6.2688 | 5.1147 | 4.1106
|  | BALDOVIE | HE |  |  |  |  | 10.7208 | 10.2882 | 9.8065 | 9.2504 | 8.5157 | 7.7024 | 6.6014 | 5.5341 | 4.5371 | 3.7382 | 0.074898 | -1.1996 | -1.5047 | 13.2729 | 12.8739 | 12.428 | 11.9045 | 11.1912 | 10.3892 | 9.4198 | 8.5065 | 7.6524 | 6.9014 | 3.9147 | 2.9443 | 1.9718 | 12.4331 | 12.0096 | 11.5422 | 10.9973 | 10.2759 | 9.4596 | 8.4331 | 7.4371 | 6.5127 | 5.6943
|  | BALDOVIE | CF |  |  |  |  | 11.0831 | 10.8371 | 10.5453 | 10.2698 | 9.881 | 9.4127 | 8.9269 | 8.3259 | 7.7871 | 7.1933 | 4.0218 | 0.87898 | -0.60265 | 13.6065 | 13.3555 | 13.0627 | 12.781 | 12.382 | 11.8922 | 11.3892 | 10.782 | 10.2331 | 9.6249 | 6.3953 | 3.0729 | 0.67184 | 12.7871 | 12.5443 | 12.2586 | 11.9841 | 11.6024 | 11.1392 | 10.6484 | 10.0565 | 9.5239 | 8.9382
| TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | NO | 0.941 | 5.3561 | 5.2092 | 5.048 | 4.8673 | 4.6959 | 4.4898 | 4.2327 | 4.0194 | 3.7867 | 3.5469 | 2.7327 | 2.5786 | 2.5459 | 8.802 | 8.7378 | 8.6663 | 8.5704 | 8.449 | 8.2908 | 8.1 | 7.9347 | 7.748 | 7.5704 | 7.0194 | 6.8582 | 6.3163 | 7.4235 | 7.2694 | 7.0918 | 6.8827 | 6.699 | 6.4633 | 6.1704 | 5.9214 | 5.6408 | 5.3714
|  | BALLATER | EE |  |  |  |  | 5.3561 | 5.2092 | 5.048 | 4.8673 | 4.6959 | 4.4898 | 4.2327 | 4.0194 | 3.7867 | 3.5469 | 2.7327 | 2.6571 | 2.6357 | 8.802 | 8.7378 | 8.6663 | 8.5704 | 8.449 | 8.2908 | 8.1 | 7.9347 | 7.748 | 7.5704 | 7.0194 | 6.8582 | 6.6041 | 7.4235 | 7.2694 | 7.0918 | 6.8827 | 6.699 | 6.4633 | 6.1704 | 5.9214 | 5.6408 | 5.3714
|  | BALLATER | HT |  |  |  |  | 5.3959 | 5.2459 | 5.0786 | 4.9092 | 4.7153 | 4.5255 | 4.3541 | 4.149 | 3.9214 | 3.6857 | 2.9306 | 2.6133 | 2.5469 | 8.8459 | 8.7908 | 8.7255 | 8.6633 | 8.5663 | 8.4398 | 8.3378 | 8.1806 | 8.0224 | 7.8786 | 7.2469 | 7.0184 | 6.9898 | 7.4888 | 7.3367 | 7.1622 | 6.9939 | 6.7939 | 6.5918 | 6.4143 | 6.1827 | 5.9347 | 5.6908
|  | BALLATER | HE |  |  |  |  | 5.3867 | 5.2796 | 5.1541 | 5.0235 | 4.8704 | 4.699 | 4.5071 | 4.3031 | 4.0878 | 3.8439 | 2.8204 | 2.5786 | 2.5459 | 8.8235 | 8.7612 | 8.6959 | 8.6214 | 8.5398 | 8.4459 | 8.3459 | 8.2224 | 8.0837 | 7.9102 | 7.2041 | 6.9439 | 6.7122 | 7.4847 | 7.3714 | 7.2347 | 7.1041 | 6.9469 | 6.7653 | 6.5827 | 6.3622 | 6.1378 | 5.8847
|  | BALLATER | CF |  |  |  |  | 5.3939 | 5.3224 | 5.2357 | 5.149 | 5.0449 | 4.9439 | 4.8245 | 4.7061 | 4.5827 | 4.4347 | 3.5061 | 3.0214 | 2.6469 | 8.8459 | 8.8143 | 8.7714 | 8.7276 | 8.6755 | 8.6214 | 8.5571 | 8.4816 | 8.3827 | 8.2684 | 7.5551 | 6.9327 | 6.3163 | 7.4939 | 7.4204 | 7.3316 | 7.2449 | 7.1367 | 7.0296 | 6.901 | 6.7837 | 6.6469 | 6.4908
| CARRADALE 1 | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0 | 0.48673 | 0.46837 | 0.45306 | 0.42551 | 0.40918 | 0.38571 | 0.34796 | 0.32551 | 0.29184 | 0.26122 | 0.20102 | 0.18265 | 0.17653 | 0.65918 | 0.64796 | 0.63776 | 0.61939 | 0.6102 | 0.59388 | 0.56837 | 0.55102 | 0.52755 | 0.50918 | 0.46735 | 0.45816 | 0.44898 | 0.56429 | 0.54796 | 0.53571 | 0.51122 | 0.49796 | 0.47449 | 0.44286 | 0.42143 | 0.3898 | 0.36429
|  | BALLIEKINE | EE |  |  |  |  | 0.48673 | 0.46837 | 0.45306 | 0.42551 | 0.40918 | 0.38571 | 0.34796 | 0.32551 | 0.29184 | 0.26122 | 0.20102 | 0.19082 | 0.18367 | 0.65918 | 0.64796 | 0.63776 | 0.61939 | 0.6102 | 0.59388 | 0.56837 | 0.55102 | 0.52755 | 0.50918 | 0.46735 | 0.45918 | 0.44898 | 0.56429 | 0.54796 | 0.53571 | 0.51122 | 0.49796 | 0.47449 | 0.44286 | 0.42143 | 0.3898 | 0.36429
|  | BALLIEKINE | HT |  |  |  |  | 0.49592 | 0.47857 | 0.46837 | 0.45 | 0.43469 | 0.41327 | 0.38673 | 0.37245 | 0.34388 | 0.31837 | 0.22041 | 0.18265 | 0.17653 | 0.66735 | 0.65612 | 0.65 | 0.63878 | 0.62959 | 0.61531 | 0.59898 | 0.59082 | 0.57245 | 0.55306 | 0.48265 | 0.45816 | 0.45408 | 0.57449 | 0.55918 | 0.55102 | 0.53469 | 0.52143 | 0.50102 | 0.47857 | 0.46735 | 0.44184 | 0.41735
|  | BALLIEKINE | HE |  |  |  |  | 0.49694 | 0.48163 | 0.47449 | 0.46224 | 0.44898 | 0.42755 | 0.40612 | 0.39592 | 0.37245 | 0.34694 | 0.24184 | 0.21633 | 0.21224 | 0.66735 | 0.65612 | 0.65408 | 0.6449 | 0.63776 | 0.62143 | 0.60612 | 0.60204 | 0.58571 | 0.56837 | 0.49898 | 0.47959 | 0.47347 | 0.57551 | 0.56122 | 0.55612 | 0.54286 | 0.53265 | 0.51429 | 0.49286 | 0.48571 | 0.46327 | 0.44184
|  | BALLIEKINE | CF |  |  |  |  | 0.49082 | 0.48776 | 0.47857 | 0.46837 | 0.45714 | 0.44898 | 0.43265 | 0.41327 | 0.4102 | 0.39286 | 0.32041 | 0.24184 | 0.21122 | 0.66224 | 0.66224 | 0.65306 | 0.64694 | 0.6398 | 0.63367 | 0.62143 | 0.60918 | 0.60816 | 0.5949 | 0.53878 | 0.48367 | 0.45816 | 0.56939 | 0.56633 | 0.55714 | 0.54796 | 0.53776 | 0.52857 | 0.51531 | 0.49898 | 0.49592 | 0.48061
| BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | YES | 1.465 | 7.4462 | 7.3728 | 7.2799 | 7.2044 | 7.1095 | 7.0126 | 6.883 | 6.7728 | 6.6401 | 6.5197 | 6.1983 | 6.0993 | 5.4202 | 7.7284 | 7.6835 | 7.6273 | 7.5845 | 7.5263 | 7.4539 | 7.3753 | 7.311 | 7.2253 | 7.1488 | 6.9386 | 7.1603 | 6.8807 | 7.3827 | 7.3154 | 7.2235 | 7.1541 | 7.0643 | 6.9643 | 6.8388 | 6.7409 | 6.6123 | 6.496
|  | BALLINDALLOCH | EE |  |  |  |  | 7.4462 | 7.3728 | 7.2799 | 7.2044 | 7.1095 | 7.0126 | 6.883 | 6.7728 | 6.6401 | 6.5197 | 6.1983 | 6.1401 | 5.4978 | 7.7284 | 7.6835 | 7.6273 | 7.5845 | 7.5263 | 7.4539 | 7.3753 | 7.311 | 7.2253 | 7.1488 | 6.9386 | 7.1603 | 7.0398 | 7.3827 | 7.3154 | 7.2235 | 7.1541 | 7.0643 | 6.9643 | 6.8388 | 6.7409 | 6.6123 | 6.496
|  | BALLINDALLOCH | HT |  |  |  |  | 7.4666 | 7.3983 | 7.3319 | 7.2585 | 7.1768 | 7.1064 | 7.0146 | 6.9085 | 6.8023 | 6.7228 | 6.2972 | 6.0993 | 5.4396 | 7.7467 | 7.711 | 7.6743 | 7.6355 | 7.5876 | 7.5498 | 7.4927 | 7.4314 | 7.3641 | 7.3233 | 7.0437 | 7.249 | 7.2092 | 7.4103 | 7.3501 | 7.2868 | 7.2215 | 7.148 | 7.0837 | 6.998 | 6.9021 | 6.8001 | 6.7347
|  | BALLINDALLOCH | HE |  |  |  |  | 7.4656 | 7.4177 | 7.3666 | 7.3136 | 7.2503 | 7.1993 | 7.1126 | 7.0105 | 6.9115 | 6.8238 | 6.2656 | 6.1074 | 5.4202 | 7.7478 | 7.7131 | 7.6845 | 7.6518 | 7.61 | 7.5722 | 7.5192 | 7.4631 | 7.3978 | 7.3518 | 6.9957 | 7.2021 | 7.0807 | 7.4103 | 7.3633 | 7.3184 | 7.2664 | 7.2031 | 7.1511 | 7.0623 | 6.9613 | 6.8633 | 6.7756
|  | BALLINDALLOCH | CF |  |  |  |  | 7.4748 | 7.434 | 7.3921 | 7.3421 | 7.3003 | 7.2442 | 7.2034 | 7.1411 | 7.0819 | 7.0217 | 6.6983 | 6.3636 | 5.4988 | 7.7529 | 7.7284 | 7.7018 | 7.6692 | 7.6386 | 7.6029 | 7.5773 | 7.5284 | 7.4886 | 7.4406 | 7.1998 | 7.2001 | 6.8807 | 7.4184 | 7.3817 | 7.3419 | 7.2929 | 7.2511 | 7.1949 | 7.1603 | 7.0949 | 7.0398 | 6.9776
| CARRADALE 1 | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 0.155 | 1.8959 | 1.8663 | 1.8388 | 1.8 | 1.7673 | 1.7224 | 1.6857 | 1.6235 | 1.5724 | 1.5224 | 1.398 | 1.3531 | 1.1158 | 1.9995 | 1.9791 | 1.9617 | 1.9352 | 1.9138 | 1.8852 | 1.8668 | 1.823 | 1.7903 | 1.7597 | 1.674 | 1.7559 | 1.6987 | 1.7773 | 1.7559 | 1.7334 | 1.6967 | 1.6681 | 1.6222 | 1.5916 | 1.5304 | 1.4824 | 1.4344
|  | BALLURE | EE |  |  |  |  | 1.8959 | 1.8663 | 1.8388 | 1.8 | 1.7673 | 1.7224 | 1.6857 | 1.6235 | 1.5724 | 1.5224 | 1.398 | 1.3724 | 1.1342 | 1.9995 | 1.9791 | 1.9617 | 1.9352 | 1.9138 | 1.8852 | 1.8668 | 1.823 | 1.7903 | 1.7597 | 1.674 | 1.7559 | 1.7171 | 1.7773 | 1.7559 | 1.7334 | 1.6967 | 1.6681 | 1.6222 | 1.5916 | 1.5304 | 1.4824 | 1.4344
|  | BALLURE | HT |  |  |  |  | 1.9112 | 1.8847 | 1.8592 | 1.8296 | 1.8041 | 1.7684 | 1.7367 | 1.6949 | 1.6469 | 1.6214 | 1.4337 | 1.3531 | 1.1158 | 2.0148 | 1.9985 | 1.9852 | 1.9638 | 1.9526 | 1.9291 | 1.9107 | 1.8821 | 1.8526 | 1.8352 | 1.7107 | 1.7742 | 1.7651 | 1.7987 | 1.7814 | 1.764 | 1.7385 | 1.7191 | 1.6814 | 1.6497 | 1.6048 | 1.5579 | 1.5395
|  | BALLURE | HE |  |  |  |  | 1.9112 | 1.8888 | 1.8714 | 1.8469 | 1.8276 | 1.8031 | 1.7776 | 1.7367 | 1.6969 | 1.6745 | 1.4684 | 1.4133 | 1.1811 | 2.0148 | 1.9995 | 1.9893 | 1.9679 | 1.9607 | 1.9403 | 1.926 | 1.8954 | 1.8699 | 1.8587 | 1.7209 | 1.7875 | 1.7538 | 1.7997 | 1.7824 | 1.7661 | 1.7416 | 1.7314 | 1.7069 | 1.6844 | 1.6395 | 1.5987 | 1.5855
|  | BALLURE | CF |  |  |  |  | 1.9102 | 1.898 | 1.8796 | 1.8622 | 1.8388 | 1.8255 | 1.802 | 1.7765 | 1.7622 | 1.7378 | 1.6082 | 1.4816 | 1.1883 | 2.0158 | 2.0077 | 1.9934 | 1.9842 | 1.9679 | 1.9607 | 1.9464 | 1.925 | 1.9148 | 1.8923 | 1.7954 | 1.7926 | 1.6987 | 1.8018 | 1.7906 | 1.7753 | 1.763 | 1.7395 | 1.7355 | 1.7099 | 1.6814 | 1.6661 | 1.6375
| DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | NO | YES | 1.02 | 0.43227 | 0.079208 | -0.57181 | -1.5004 | -2.6218 | -3.9177 | -4.8269 | -5.8198 | -6.7208 | -7.6647 | -9.2402 | -9.5779 | -9.7014 | 1.3139 | 1.0568 | 0.71594 | 0.20676 | -0.45855 | -1.2759 | -1.9024 | -2.6147 | -3.3055 | -4.0892 | -5.1443 | -5.3136 | -5.579 | 1.0415 | 0.6588 | 0.087371 | -0.69222 | -1.6371 | -2.7381 | -3.531 | -4.4055 | -5.2198 | -6.0912
|  | BALMEDIE | EE |  |  |  |  | 0.43227 | 0.18431 | -0.27896 | -1.0341 | -2.0279 | -3.3034 | -4.6769 | -5.5341 | -6.3239 | -7.1157 | -9.182 | -9.5136 | -9.6453 | 1.3159 | 1.1261 | 0.83941 | 0.46084 | -0.12793 | -0.89834 | -1.7555 | -2.3667 | -2.9688 | -3.6116 | -5.1443 | -5.3136 | -5.579 | 1.0415 | 0.78839 | 0.30676 | -0.32691 | -1.1688 | -2.2555 | -3.4188 | -4.1871 | -4.9045 | -5.6218
|  | BALMEDIE | HT |  |  |  |  | 0.44145 | 0.079208 | -0.57181 | -1.5004 | -2.6218 | -3.9177 | -4.8269 | -5.8198 | -6.7208 | -7.6647 | -9.2402 | -9.5779 | -9.7014 | 1.3139 | 1.0568 | 0.71594 | 0.20676 | -0.45855 | -1.2759 | -1.9024 | -2.6147 | -3.3055 | -4.0892 | -5.0392 | -5.133 | -5.1943 | 1.0557 | 0.6588 | 0.087371 | -0.69222 | -1.6371 | -2.7381 | -3.531 | -4.4055 | -5.2198 | -6.0912
|  | BALMEDIE | HE |  |  |  |  | 0.46696 | 0.25574 | -0.028955 | -0.48814 | -1.2228 | -2.1361 | -3.1759 | -3.983 | -4.6698 | -5.3963 | -7.7075 | -8.3341 | -8.8443 | 1.3374 | 1.1568 | 0.93125 | 0.62309 | 0.24145 | -0.35344 | -1.0626 | -1.6555 | -2.2034 | -2.8218 | -4.5228 | -4.831 | -5.2555 | 1.0812 | 0.87411 | 0.59247 | 0.13125 | -0.4963 | -1.279 | -2.1769 | -2.8963 | -3.5034 | -4.1647
|  | BALMEDIE | CF |  |  |  |  | 0.54043 | 0.42002 | 0.27615 | 0.065943 | -0.26977 | -0.76569 | -1.4208 | -2.1463 | -2.6463 | -3.1351 | -5.5422 | -7.23 | -8.2147 | 1.3945 | 1.2915 | 1.1659 | 1.0057 | 0.78941 | 0.52104 | 0.12411 | -0.36161 | -0.73712 | -1.1361 | -3.1034 | -4.5585 | -5.4147 | 1.1496 | 1.0312 | 0.89247 | 0.66288 | 0.32002 | -0.10038 | -0.64834 | -1.2667 | -1.7055 | -2.1371
| CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | NO | 0.003 | 10.1027 | 9.9894 | 9.8506 | 9.7159 | 9.5618 | 9.3863 | 9.122 | 8.8343 | 8.5414 | 8.2751 | 7.019 | 6.0578 | 4.8779 | 8.8932 | 8.8187 | 8.7228 | 8.6309 | 8.5228 | 8.3952 | 8.2319 | 8.0554 | 7.8738 | 7.7146 | 6.9717 | 6.9607 | 6.4749 | 9.6443 | 9.5433 | 9.4168 | 9.2943 | 9.1474 | 8.976 | 8.7158 | 8.4423 | 8.1709 | 7.9229
|  | BALNAGASK | EE |  |  |  |  | 10.1027 | 9.9894 | 9.8506 | 9.7159 | 9.5618 | 9.3863 | 9.122 | 8.8343 | 8.5414 | 8.2751 | 7.019 | 6.1669 | 4.9003 | 8.8932 | 8.8187 | 8.7228 | 8.6309 | 8.5228 | 8.3952 | 8.2319 | 8.0554 | 7.8738 | 7.7146 | 6.9717 | 6.9607 | 6.4749 | 9.6443 | 9.5433 | 9.4168 | 9.2943 | 9.1474 | 8.976 | 8.7158 | 8.4423 | 8.1709 | 7.9229
|  | BALNAGASK | HT |  |  |  |  | 10.1445 | 10.0506 | 9.9445 | 9.8333 | 9.7027 | 9.571 | 9.32 | 9.0476 | 8.77 | 8.4884 | 7.0282 | 6.0578 | 4.8779 | 8.9156 | 8.8687 | 8.8085 | 8.7381 | 8.6534 | 8.5707 | 8.4309 | 8.2819 | 8.133 | 7.9768 | 7.2054 | 7.2505 | 7.1872 | 9.6678 | 9.5984 | 9.4964 | 9.3892 | 9.2668 | 9.1443 | 8.9076 | 8.6576 | 8.4025 | 8.1433
|  | BALNAGASK | HE |  |  |  |  | 10.1414 | 10.0782 | 10.0037 | 9.9282 | 9.8363 | 9.7486 | 9.5802 | 9.4006 | 9.2067 | 9.0078 | 7.9445 | 7.2271 | 5.9901 | 8.9105 | 8.8738 | 8.8279 | 8.7697 | 8.7003 | 8.6319 | 8.5248 | 8.4054 | 8.2819 | 8.1564 | 7.4799 | 7.4994 | 7.0668 | 9.6678 | 9.6239 | 9.5586 | 9.4882 | 9.4045 | 9.327 | 9.1576 | 8.976 | 8.7984 | 8.6127
|  | BALNAGASK | CF |  |  |  |  | 10.17 | 10.1333 | 10.0904 | 10.0424 | 9.9904 | 9.9271 | 9.8761 | 9.7945 | 9.719 | 9.6496 | 9.1404 | 8.5384 | 6.8523 | 8.9258 | 8.8993 | 8.8738 | 8.8309 | 8.787 | 8.7309 | 8.6768 | 8.6013 | 8.5279 | 8.4585 | 7.9554 | 7.7147 | 6.6423 | 9.679 | 9.6637 | 9.6382 | 9.5964 | 9.5535 | 9.4994 | 9.4545 | 9.379 | 9.3086 | 9.2403
| KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 4.121 | 2.3609 | 1.6619 | 25.3268 | 24.3635 | 23.6492 | 22.4931 | 21.5911 | 20.6584 | 20.0727 | 19.1339 | 15.7554 | 12.8554 | -13.8636 | 5.3598 | 28.8533 | 28.3339 | 27.7625 | 27.4278 | 26.5666 | 26.0809 | 25.5247 | 25.1258 | 24.5084 | 21.6278 | -4.2136 | -6.6708 | 28.1707 | 27.5829 | 26.8288 | 25.938 | 25.3125 | 24.1594 | 23.3421 | 22.4798 | 21.9931 | 21.1339
|  | BANCHORY | EE |  |  |  |  | 2.3609 | 1.6905 | 25.4921 | 24.69 | 23.8043 | 22.7849 | 22.0717 | 21.2074 | 20.2472 | 19.3411 | 16.09 | 13.4758 | -12.5575 | 5.3884 | 28.8829 | 28.4839 | 28.0737 | 27.5666 | 26.8972 | 26.4217 | 25.9145 | 25.287 | 24.7145 | 22.6329 | -3.3371 | -4.7657 | 28.1707 | 27.5829 | 26.9584 | 26.2502 | 25.4278 | 24.4472 | 23.8472 | 23.0492 | 22.1319 | 21.29
|  | BANCHORY | HT |  |  |  |  | 2.3792 | 1.6619 | 25.3268 | 24.3635 | 23.6492 | 22.4931 | 21.5911 | 20.6584 | 20.0727 | 19.1339 | 15.7554 | 12.8554 | -13.8636 | 5.3598 | 28.8533 | 28.3339 | 27.7625 | 27.4278 | 26.5666 | 26.0809 | 25.5247 | 25.1258 | 24.5258 | 22.4951 | -3.4095 | -5.0993 | 28.2125 | 27.5982 | 26.8288 | 25.938 | 25.3125 | 24.1594 | 23.3421 | 22.4798 | 21.9931 | 21.1339
|  | BANCHORY | HE |  |  |  |  | 2.4731 | 1.9415 | 25.8298 | 25.0717 | 24.44 | 23.4023 | 22.5666 | 21.7931 | 21.387 | 20.5482 | 16.7033 | 13.8676 | -13.2422 | 5.4568 | 28.99 | 28.5543 | 28.038 | 27.6502 | 26.8247 | 26.2594 | 25.6829 | 25.239 | 24.5084 | 21.6278 | -4.2136 | -6.6708 | 28.2951 | 27.8278 | 27.2543 | 26.5441 | 25.9778 | 24.9411 | 24.1615 | 23.4135 | 23.0533 | 22.2115
|  | BANCHORY | CF |  |  |  |  | 2.6864 | 2.3374 | 26.4768 | 26.0431 | 25.5584 | 25.0319 | 24.5319 | 24.0329 | 23.6043 | 23.4431 | 21.086 | 18.6186 | -8.482 | 5.6711 | 29.3543 | 29.1268 | 28.8921 | 28.588 | 28.2013 | 27.8584 | 27.4788 | 27.1298 | 26.9043 | 25.0635 | -0.78404 | -3.1728 | 28.4819 | 28.1798 | 27.8554 | 27.4778 | 27.0278 | 26.5247 | 26.0533 | 25.5809 | 25.1584 | 25.0319
| TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | 2.006 | -3.9082 | -3.9847 | -4.0888 | -4.2041 | -4.352 | -4.5133 | -4.6541 | -4.8347 | -4.999 | -5.149 | -5.4806 | -5.5714 | -5.599 | -3.6714 | -3.7163 | -3.7796 | -3.8429 | -3.9276 | -4.0184 | -4.099 | -4.2184 | -4.3306 | -4.4296 | -4.6663 | -4.7653 | -5.1102 | -3.6296 | -3.7051 | -3.8051 | -3.9082 | -4.0429 | -4.1908 | -4.3163 | -4.4867 | -4.6449 | -4.7857
|  | BARCALDINE | EE |  |  |  |  | -3.9082 | -3.9847 | -4.0888 | -4.2041 | -4.352 | -4.5133 | -4.6541 | -4.8347 | -4.999 | -5.149 | -5.4806 | -5.5327 | -5.5561 | -3.6714 | -3.7163 | -3.7796 | -3.8429 | -3.9276 | -4.0184 | -4.099 | -4.2184 | -4.3306 | -4.4296 | -4.6663 | -4.7653 | -4.9122 | -3.6296 | -3.7051 | -3.8051 | -3.9082 | -4.0429 | -4.1908 | -4.3163 | -4.4867 | -4.6449 | -4.7857
|  | BARCALDINE | HT |  |  |  |  | -3.8786 | -3.9449 | -4.0235 | -4.1347 | -4.2724 | -4.399 | -4.5398 | -4.6959 | -4.8367 | -4.9357 | -5.3837 | -5.5714 | -5.599 | -3.6541 | -3.6939 | -3.7347 | -3.7939 | -3.8684 | -3.9327 | -4.0184 | -4.1122 | -4.1949 | -4.252 | -4.5459 | -4.6582 | -4.6776 | -3.601 | -3.6673 | -3.7398 | -3.8398 | -3.9643 | -4.0735 | -4.2092 | -4.3551 | -4.4878 | -4.5776
|  | BARCALDINE | HE |  |  |  |  | -3.8796 | -3.9316 | -3.9969 | -4.0827 | -4.2092 | -4.3255 | -4.4602 | -4.5969 | -4.7265 | -4.8071 | -5.3265 | -5.449 | -5.4673 | -3.6541 | -3.6878 | -3.7276 | -3.7776 | -3.848 | -3.9112 | -3.9878 | -4.0755 | -4.1561 | -4.2133 | -4.5643 | -4.7051 | -4.849 | -3.602 | -3.6541 | -3.7153 | -3.7939 | -3.9051 | -4.0071 | -4.1296 | -4.2582 | -4.3827 | -4.4582
|  | BARCALDINE | CF |  |  |  |  | -3.8653 | -3.9133 | -3.9612 | -4.0327 | -4.1265 | -4.2122 | -4.2765 | -4.3827 | -4.4663 | -4.5643 | -4.9531 | -5.2847 | -5.4633 | -3.6459 | -3.6755 | -3.7041 | -3.75 | -3.8041 | -3.8531 | -3.8939 | -3.9633 | -4.0184 | -4.0806 | -4.3827 | -4.7367 | -5.1102 | -3.5878 | -3.6347 | -3.6796 | -3.7449 | -3.8296 | -3.9071 | -3.9633 | -4.0612 | -4.1388 | -4.2296
| STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 0.148 | 0.7449 | 5.5584 | 5.3747 | 5.2563 | 5.1104 | 4.9594 | 4.7982 | 4.5829 | 4.3614 | 4.1665 | 3.7176 | 3.6165 | -1.3622 | 6.5788 | 6.4971 | 6.4227 | 6.3757 | 6.3135 | 6.2124 | 6.1145 | 5.9624 | 5.8186 | 5.6971 | 5.3798 | 0.29184 | 4.6757 | 6.2043 | 6.088 | 5.9135 | 5.8063 | 5.6716 | 5.5308 | 5.3839 | 5.1961 | 5.0145 | 4.8502
|  | BARVAS | EE |  |  |  |  | 0.7449 | 5.5676 | 5.3747 | 5.2563 | 5.1104 | 4.9594 | 4.7982 | 4.5829 | 4.3614 | 4.1665 | 3.7176 | 3.6543 | -1.3143 | 6.5788 | 6.5471 | 6.4227 | 6.3757 | 6.3135 | 6.2124 | 6.1145 | 5.9624 | 5.8186 | 5.6971 | 5.3798 | 0.29184 | 4.9961 | 6.2043 | 6.1033 | 5.9135 | 5.8063 | 5.6716 | 5.5308 | 5.3839 | 5.1961 | 5.0145 | 4.8502
|  | BARVAS | HT |  |  |  |  | 0.78367 | 5.5584 | 5.4369 | 5.3308 | 5.2094 | 5.0808 | 4.9614 | 4.8063 | 4.6522 | 4.5267 | 3.8941 | 3.6165 | -1.3622 | 6.6022 | 6.4971 | 6.4614 | 6.4237 | 6.3737 | 6.3196 | 6.2727 | 6.2002 | 6.0971 | 6.0257 | 5.59 | 0.49286 | 5.4104 | 6.2349 | 6.088 | 5.9757 | 5.8798 | 5.7686 | 5.6482 | 5.5431 | 5.3992 | 5.2573 | 5.141
|  | BARVAS | HE |  |  |  |  | 0.78265 | 5.6471 | 5.4951 | 5.4206 | 5.3359 | 5.2339 | 5.1329 | 4.9971 | 4.8635 | 4.7563 | 3.9512 | 3.7614 | -1.2031 | 6.5992 | 6.5757 | 6.4696 | 6.439 | 6.3971 | 6.3471 | 6.3022 | 6.2329 | 6.1492 | 6.0808 | 5.5298 | 0.36837 | 5.0798 | 6.2318 | 6.1757 | 6.0278 | 5.9614 | 5.8808 | 5.788 | 5.6951 | 5.5696 | 5.4451 | 5.3502
|  | BARVAS | CF |  |  |  |  | 0.78367 | 5.6604 | 5.589 | 5.4635 | 5.3839 | 5.3063 | 5.2186 | 5.1471 | 5.0563 | 4.9645 | 4.5043 | 4.0206 | -1.1704 | 6.6033 | 6.589 | 6.5686 | 6.4737 | 6.4431 | 6.4104 | 6.3706 | 6.3369 | 6.2686 | 6.19 | 5.7727 | 0.29388 | 4.6757 | 6.24 | 6.191 | 6.1247 | 6.0002 | 5.9257 | 5.8522 | 5.7727 | 5.7063 | 5.6237 | 5.5369
| STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 5.152 | 12.4076 | 12.0342 | 11.3117 | 10.3933 | 9.5831 | 8.4617 | 7.5219 | 6.1893 | 4.776 | 2.7719 | -5.1903 | -9.2536 | -13.3505 | 14.7076 | 14.374 | 13.6729 | 12.8964 | 12.3148 | 10.9658 | 10.1556 | 9.1515 | 7.9046 | 6.0474 | -0.95869 | -4.3944 | -7.5311 | 14.6025 | 14.1699 | 13.3729 | 12.4444 | 11.6372 | 10.2842 | 9.2168 | 7.8893 | 6.4903 | 4.4597
|  | BATTERY POINT | EE |  |  |  |  | 12.4076 | 12.0413 | 11.3638 | 10.5433 | 9.5831 | 8.6097 | 7.5352 | 6.3546 | 4.8321 | 3.2709 | -1.7903 | -4.4332 | -6.9271 | 14.7076 | 14.4076 | 13.7627 | 13.1546 | 12.3658 | 11.4556 | 10.678 | 9.8138 | 8.4821 | 7.1148 | 2.7638 | 0.46478 | -0.75971 | 14.6025 | 14.1699 | 13.4495 | 12.6648 | 11.6372 | 10.5138 | 9.4454 | 8.3127 | 6.7893 | 5.2495
|  | BATTERY POINT | HT |  |  |  |  | 12.5811 | 12.0342 | 11.3117 | 10.3933 | 9.7821 | 8.4617 | 7.526 | 6.4484 | 5.328 | 3.5954 | -1.1169 | -5.0332 | -8.973 | 14.8913 | 14.374 | 13.6729 | 12.8964 | 12.4811 | 11.2076 | 10.5556 | 9.7627 | 8.7362 | 7.2464 | 3.0311 | -0.34339 | -3.2628 | 14.8005 | 14.1984 | 13.3729 | 12.4444 | 11.928 | 10.4995 | 9.5831 | 8.4923 | 7.2607 | 5.5566
|  | BATTERY POINT | HE |  |  |  |  | 12.5546 | 12.2474 | 11.5005 | 10.6842 | 10.0138 | 8.5872 | 7.5219 | 6.1893 | 4.776 | 2.7719 | -5.1903 | -9.2536 | -13.3505 | 14.8515 | 14.5893 | 13.8076 | 12.9505 | 12.3148 | 10.9658 | 10.1556 | 9.1515 | 7.9046 | 6.0474 | -0.95869 | -4.3944 | -7.5311 | 14.7668 | 14.4372 | 13.6423 | 12.678 | 11.8515 | 10.2842 | 9.2168 | 7.8893 | 6.4903 | 4.4597
|  | BATTERY POINT | CF |  |  |  |  | 12.6617 | 12.4903 | 12.2842 | 11.8046 | 11.1811 | 10.5087 | 9.9087 | 9.2801 | 8.576 | 7.6515 | 2.6995 | -1.6413 | -5.2618 | 14.9433 | 14.7984 | 14.624 | 14.1311 | 13.5556 | 12.8995 | 12.3638 | 11.7903 | 11.1505 | 10.3331 | 6.3393 | 3.4617 | 1.7576 | 14.8811 | 14.6597 | 14.3801 | 13.8882 | 13.2627 | 12.6036 | 11.9689 | 11.2393 | 10.4546 | 9.4984
| DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | NO | 0.132 | 0.21122 | 0.17347 | 0.14082 | 0.092857 | 0.052041 | 0.005102 | -0.058163 | -0.1051 | -0.16735 | -0.21531 | -0.34694 | -0.38673 | -0.39898 | 0.48163 | 0.45918 | 0.43878 | 0.40714 | 0.38367 | 0.34796 | 0.30714 | 0.28061 | 0.2398 | 0.2102 | 0.12245 | 0.087755 | -0.035714 | 0.31327 | 0.27959 | 0.24796 | 0.20204 | 0.16429 | 0.11735 | 0.055102 | 0.014286 | -0.043878 | -0.090816
|  | BETTYHILL | EE |  |  |  |  | 0.21122 | 0.17347 | 0.14082 | 0.092857 | 0.052041 | 0.005102 | -0.058163 | -0.1051 | -0.16735 | -0.21531 | -0.34694 | -0.36633 | -0.37857 | 0.48163 | 0.45918 | 0.43878 | 0.40714 | 0.38367 | 0.34796 | 0.30714 | 0.28061 | 0.2398 | 0.2102 | 0.12245 | 0.087755 | 0.033673 | 0.31327 | 0.27959 | 0.24796 | 0.20204 | 0.16429 | 0.11735 | 0.055102 | 0.014286 | -0.043878 | -0.090816
|  | BETTYHILL | HT |  |  |  |  | 0.22449 | 0.19592 | 0.16531 | 0.12755 | 0.09898 | 0.059184 | 0.020408 | -0.030612 | -0.079592 | -0.13061 | -0.30204 | -0.38673 | -0.39898 | 0.49388 | 0.47959 | 0.46122 | 0.43878 | 0.42449 | 0.40102 | 0.37857 | 0.34592 | 0.31224 | 0.27857 | 0.17347 | 0.12143 | 0.11531 | 0.32857 | 0.30306 | 0.27551 | 0.23878 | 0.21429 | 0.17551 | 0.14184 | 0.092857 | 0.044898 | -0.0071429
|  | BETTYHILL | HE |  |  |  |  | 0.22653 | 0.20408 | 0.17959 | 0.14898 | 0.13061 | 0.097959 | 0.063265 | 0.020408 | -0.02449 | -0.069388 | -0.27857 | -0.33571 | -0.34388 | 0.49694 | 0.48265 | 0.46531 | 0.4449 | 0.43469 | 0.40816 | 0.39286 | 0.35816 | 0.33061 | 0.29796 | 0.16939 | 0.11122 | 0.059184 | 0.33061 | 0.30918 | 0.28673 | 0.2551 | 0.2398 | 0.20612 | 0.17755 | 0.13367 | 0.091837 | 0.047959
|  | BETTYHILL | CF |  |  |  |  | 0.22857 | 0.2102 | 0.18673 | 0.16735 | 0.1398 | 0.12551 | 0.095918 | 0.064286 | 0.042857 | 0.015306 | -0.12755 | -0.25816 | -0.33571 | 0.49796 | 0.48673 | 0.46939 | 0.45714 | 0.43776 | 0.42959 | 0.40714 | 0.38367 | 0.36939 | 0.34388 | 0.23469 | 0.09898 | -0.035714 | 0.33265 | 0.31633 | 0.29184 | 0.27449 | 0.24592 | 0.23367 | 0.20408 | 0.17143 | 0.15204 | 0.12245
| GRUDIE BRIDGE | BIDEN CLAN RAONAILD | MINIMUM HEADROOM | NH 06927 58342 | YES | NO | 0 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201
|  | BIDEN CLAN RAONAILD | EE |  |  |  |  | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201
|  | BIDEN CLAN RAONAILD | HT |  |  |  |  | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201
|  | BIDEN CLAN RAONAILD | HE |  |  |  |  | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201
|  | BIDEN CLAN RAONAILD | CF |  |  |  |  | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201
| ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 5.055 | 7.5216 | 16.4518 | 16.3334 | 16.1916 | 16.0701 | 15.9181 | 15.7191 | 15.515 | 15.2763 | 14.9946 | 14.0803 | 13.6844 | 3.4109 | 16.8283 | 16.7538 | 16.6936 | 16.6171 | 16.5548 | 16.4691 | 16.363 | 16.2518 | 16.1222 | 15.9916 | 15.4895 | 6.7867 | 15.5446 | 16.5895 | 16.4324 | 16.3232 | 16.1946 | 16.0875 | 15.9518 | 15.7742 | 15.5875 | 15.3803 | 15.1487
|  | BILBOHALL | EE |  |  |  |  | 7.5216 | 16.4518 | 16.3334 | 16.1916 | 16.0701 | 15.9181 | 15.7191 | 15.515 | 15.2763 | 15.0242 | 14.0803 | 13.7303 | 3.4548 | 16.8283 | 16.7538 | 16.6936 | 16.6171 | 16.5548 | 16.4691 | 16.363 | 16.2518 | 16.1222 | 15.9916 | 15.4895 | 6.7867 | 15.6252 | 16.5895 | 16.4324 | 16.3232 | 16.1946 | 16.0875 | 15.9518 | 15.7742 | 15.5875 | 15.3803 | 15.1569
|  | BILBOHALL | HT |  |  |  |  | 7.5481 | 16.4956 | 16.3814 | 16.265 | 16.1395 | 16.0007 | 15.7773 | 15.565 | 15.2834 | 14.9946 | 14.1007 | 13.6844 | 3.4109 | 16.8436 | 16.7946 | 16.7334 | 16.6793 | 16.6181 | 16.5456 | 16.4375 | 16.3395 | 16.1987 | 16.0548 | 15.6058 | 6.952 | 15.9773 | 16.613 | 16.4712 | 16.365 | 16.2599 | 16.1467 | 16.0212 | 15.8232 | 15.6395 | 15.3987 | 15.1487
|  | BILBOHALL | HE |  |  |  |  | 7.5501 | 16.5354 | 16.4538 | 16.3783 | 16.2834 | 16.1885 | 16.0609 | 15.9038 | 15.7099 | 15.4854 | 14.5365 | 14.1222 | 3.7681 | 16.8416 | 16.8007 | 16.7589 | 16.7181 | 16.664 | 16.6079 | 16.5334 | 16.4507 | 16.3446 | 16.2232 | 15.6854 | 6.9428 | 15.7487 | 16.614 | 16.5058 | 16.4314 | 16.364 | 16.2783 | 16.1926 | 16.0763 | 15.9436 | 15.7742 | 15.5824
|  | BILBOHALL | CF |  |  |  |  | 7.5736 | 16.5854 | 16.5283 | 16.4579 | 16.4099 | 16.3405 | 16.2803 | 16.2079 | 16.1487 | 16.0538 | 15.2803 | 14.7477 | 4.1405 | 16.8487 | 16.815 | 16.7936 | 16.7518 | 16.7222 | 16.6783 | 16.6344 | 16.5803 | 16.5436 | 16.4763 | 15.9885 | 7.052 | 15.5446 | 16.6375 | 16.5518 | 16.4987 | 16.4365 | 16.3936 | 16.3293 | 16.2763 | 16.213 | 16.164 | 16.0793
| RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0 | 0.015122 | 0.0079796 | 0.0079796 | 0.0079796 | 0.00083673 | -0.00018367 | -0.0073265 | -0.0073265 | -0.0083469 | -0.011408 | -0.0093673 | -0.0093673 | -0.016929 | 0.015724 | 0.0075612 | 0.0075612 | 0.0075612 | 0.00041837 | -0.00060204 | -0.0077449 | -0.0077449 | -0.0046837 | -0.0087653 | -0.0087653 | -0.0024337 | -0.0065153 | 0.014913 | 0.0077704 | 0.0077704 | 0.0077704 | 0.00062755 | -0.00039286 | -0.0075357 | -0.0075357 | -0.010597 | -0.012638
|  | BLACKMOUNT | EE |  |  |  |  | 0.015122 | 0.0079796 | 0.0079796 | 0.0079796 | 0.00083673 | -0.00018367 | -0.0073265 | -0.0073265 | -0.0083469 | -0.011408 | -0.0063061 | -0.0063061 | -0.010806 | 0.015724 | 0.0075612 | 0.0075612 | 0.0075612 | 0.00041837 | -0.00060204 | -0.0077449 | -0.0077449 | -0.0046837 | -0.0057041 | -0.0016224 | 0.00062755 | 0.00062755 | 0.014913 | 0.0077704 | 0.0077704 | 0.0077704 | 0.00062755 | -0.00039286 | -0.0075357 | -0.0075357 | -0.010597 | -0.012638
|  | BLACKMOUNT | HT |  |  |  |  | 0.015122 | 0.015122 | 0.015122 | 0.0079796 | 0.0079796 | 0.0079796 | 0.0069592 | -0.00018367 | -0.00018367 | -0.0073265 | -0.0042653 | -0.0052857 | -0.0097857 | 0.015724 | 0.015724 | 0.015724 | 0.0075612 | 0.0075612 | 0.0075612 | 0.0075612 | -0.00060204 | -0.00060204 | -0.0077449 | -0.00060204 | 0.00062755 | 0.00062755 | 0.014913 | 0.014913 | 0.014913 | 0.0077704 | 0.0077704 | 0.0077704 | 0.00675 | -0.00039286 | -0.00039286 | -0.0075357
|  | BLACKMOUNT | HE |  |  |  |  | 0.015122 | 0.015122 | 0.015122 | 0.0079796 | 0.0079796 | 0.0079796 | 0.0069592 | -0.00018367 | -0.00018367 | -0.0083469 | -0.0093673 | -0.0063061 | -0.010806 | 0.015724 | 0.015724 | 0.014704 | 0.0075612 | 0.0075612 | 0.0075612 | 0.0075612 | 0.00041837 | -0.00060204 | -0.0087653 | -0.0046837 | 0.00062755 | 0.00062755 | 0.014913 | 0.014913 | 0.014913 | 0.0077704 | 0.0077704 | 0.0077704 | 0.0077704 | 0.00062755 | -0.00039286 | -0.0075357
|  | BLACKMOUNT | CF |  |  |  |  | 0.015122 | 0.015122 | 0.015122 | 0.015122 | 0.0079796 | 0.0079796 | 0.0079796 | 0.0079796 | 0.0079796 | -0.00018367 | -0.0083469 | -0.0093673 | -0.016929 | 0.015724 | 0.015724 | 0.015724 | 0.015724 | 0.0075612 | 0.0075612 | 0.0075612 | 0.0075612 | 0.0075612 | -0.00060204 | -0.0087653 | -0.0024337 | -0.0065153 | 0.014913 | 0.014913 | 0.014913 | 0.014913 | 0.0077704 | 0.0077704 | 0.0077704 | 0.0077704 | 0.0077704 | -0.00039286
| BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | NO | 0.15 | 4.2422 | 4.1076 | 3.98 | 3.8229 | 3.681 | 3.5096 | 3.3096 | 3.1269 | 2.9371 | 2.7647 | 2.3524 | 2.2167 | 1.6318 | 4.9155 | 4.8298 | 4.7594 | 4.6584 | 4.5767 | 4.4665 | 4.34 | 4.2267 | 4.1053 | 3.9951 | 3.7114 | 3.8457 | 3.3549 | 4.7641 | 4.6386 | 4.5222 | 4.3702 | 4.2427 | 4.0763 | 3.8773 | 3.7069 | 3.5212 | 3.3569
|  | BLACKSTAND | EE |  |  |  |  | 4.2422 | 4.1076 | 3.98 | 3.8229 | 3.681 | 3.5096 | 3.3096 | 3.1269 | 2.9371 | 2.7647 | 2.3524 | 2.2882 | 1.7176 | 4.9155 | 4.8298 | 4.7594 | 4.6584 | 4.5767 | 4.4665 | 4.34 | 4.2267 | 4.1053 | 3.9951 | 3.7114 | 3.8457 | 3.6376 | 4.7641 | 4.6386 | 4.5222 | 4.3702 | 4.2427 | 4.0763 | 3.8773 | 3.7069 | 3.5212 | 3.3569
|  | BLACKSTAND | HT |  |  |  |  | 4.2657 | 4.1545 | 4.03 | 3.9086 | 3.7708 | 3.6147 | 3.481 | 3.3116 | 3.1708 | 3.0259 | 2.479 | 2.2167 | 1.6318 | 4.941 | 4.8829 | 4.8206 | 4.7584 | 4.6829 | 4.5931 | 4.5227 | 4.4176 | 4.3257 | 4.2329 | 3.8737 | 3.9978 | 3.9712 | 4.7906 | 4.6916 | 4.5804 | 4.4733 | 4.3478 | 4.208 | 4.0876 | 3.9284 | 3.7886 | 3.6406
|  | BLACKSTAND | HE |  |  |  |  | 4.2647 | 4.18 | 4.082 | 3.9902 | 3.8759 | 3.7504 | 3.632 | 3.478 | 3.3555 | 3.229 | 2.5463 | 2.3769 | 1.8165 | 4.94 | 4.89 | 4.8318 | 4.7788 | 4.7063 | 4.6247 | 4.5594 | 4.4584 | 4.3727 | 4.2778 | 3.8288 | 3.9029 | 3.7049 | 4.7906 | 4.7141 | 4.6253 | 4.5416 | 4.4406 | 4.3192 | 4.2131 | 4.0661 | 3.9396 | 3.8069
|  | BLACKSTAND | CF |  |  |  |  | 4.2831 | 4.2147 | 4.1259 | 4.0269 | 3.9402 | 3.8341 | 3.728 | 3.6178 | 3.5576 | 3.4698 | 3.0484 | 2.6167 | 1.8512 | 4.9492 | 4.9084 | 4.8594 | 4.7992 | 4.7482 | 4.6818 | 4.6063 | 4.5206 | 4.4849 | 4.4135 | 4.0471 | 3.8488 | 3.3549 | 4.8059 | 4.7437 | 4.6671 | 4.5773 | 4.5018 | 4.4069 | 4.3069 | 4.1906 | 4.1376 | 4.0447
| COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | NO | 2.031 | 12.9293 | 12.566 | 12.1334 | 11.7058 | 11.1926 | 10.5824 | 9.8466 | 8.7762 | 7.6283 | 6.8854 | 3.8375 | 2.1375 | 0.69052 | 15.2834 | 15.0773 | 14.8089 | 14.5538 | 14.2313 | 13.8528 | 13.5568 | 12.9497 | 12.3232 | 11.7599 | 10.0517 | 9.6737 | 8.8574 | 14.4553 | 14.1257 | 13.7278 | 13.3349 | 12.8645 | 12.3023 | 11.737 | 10.7686 | 9.7339 | 9.1063
|  | BLAIRGOWRIE | EE |  |  |  |  | 12.9293 | 12.566 | 12.1334 | 11.7058 | 11.1926 | 10.5824 | 9.912 | 8.9354 | 7.9283 | 6.9864 | 3.9201 | 2.2436 | 0.72216 | 15.2834 | 15.0773 | 14.8089 | 14.5538 | 14.2313 | 13.8528 | 13.5568 | 12.9497 | 12.3232 | 11.7599 | 10.0517 | 9.6737 | 8.8574 | 14.4553 | 14.1257 | 13.7278 | 13.3349 | 12.8645 | 12.3023 | 11.7533 | 10.8655 | 9.9523 | 9.1063
|  | BLAIRGOWRIE | HT |  |  |  |  | 13.0048 | 12.6426 | 12.2313 | 11.8283 | 11.3273 | 10.7844 | 9.8466 | 8.7762 | 7.6283 | 6.8854 | 3.8375 | 2.1375 | 0.69052 | 15.3762 | 15.1915 | 14.9722 | 14.7711 | 14.5017 | 14.2232 | 13.6936 | 13.0466 | 12.3487 | 12.0364 | 10.4436 | 10.2533 | 10.1257 | 14.5421 | 14.2247 | 13.8574 | 13.4961 | 13.0492 | 12.5727 | 11.737 | 10.7686 | 9.7339 | 9.1339
|  | BLAIRGOWRIE | HE |  |  |  |  | 13.013 | 12.7946 | 12.5242 | 12.2722 | 11.9262 | 11.5262 | 10.8334 | 10.0589 | 9.2354 | 8.7517 | 5.9711 | 4.2395 | 2.3813 | 15.3711 | 15.2324 | 15.0548 | 14.8977 | 14.6762 | 14.4395 | 14.013 | 13.4977 | 12.9497 | 12.7242 | 10.9528 | 10.5023 | 9.6165 | 14.5472 | 14.3512 | 14.1053 | 13.8727 | 13.5584 | 13.2074 | 12.587 | 11.8788 | 11.1278 | 10.7523
|  | BLAIRGOWRIE | CF |  |  |  |  | 13.0864 | 12.9395 | 12.7579 | 12.5895 | 12.3711 | 12.0864 | 11.8028 | 11.4171 | 11.0222 | 10.5793 | 8.9395 | 6.8456 | 4.0375 | 15.4089 | 15.3038 | 15.1711 | 15.0568 | 14.8956 | 14.6987 | 14.4905 | 14.1864 | 13.8732 | 13.5344 | 12.2089 | 10.8921 | 8.8767 | 14.6114 | 14.487 | 14.3196 | 14.1635 | 13.9614 | 13.7043 | 13.4563 | 13.0972 | 12.7329 | 12.3308
| STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | 0.069 | 0.48571 | 0.46429 | 0.44286 | 0.41939 | 0.39592 | 0.37041 | 0.33878 | 0.30204 | 0.27551 | 0.25 | 0.17653 | 0.13163 | 0.11327 | 0.58776 | 0.57653 | 0.56224 | 0.54796 | 0.53061 | 0.51122 | 0.49184 | 0.46327 | 0.44286 | 0.42653 | 0.36939 | 0.33673 | 0.32143 | 0.54592 | 0.52653 | 0.5051 | 0.48469 | 0.46122 | 0.43673 | 0.40816 | 0.37347 | 0.34694 | 0.32245
|  | BLAIRLINNANS | EE |  |  |  |  | 0.48571 | 0.46429 | 0.44286 | 0.41939 | 0.39592 | 0.37041 | 0.33878 | 0.30204 | 0.27551 | 0.25 | 0.19184 | 0.18469 | 0.18367 | 0.58776 | 0.57653 | 0.56224 | 0.54796 | 0.53061 | 0.51122 | 0.49184 | 0.46327 | 0.44286 | 0.42653 | 0.38367 | 0.38061 | 0.38061 | 0.54592 | 0.52653 | 0.5051 | 0.48469 | 0.46122 | 0.43673 | 0.40816 | 0.37347 | 0.34694 | 0.32245
|  | BLAIRLINNANS | HT |  |  |  |  | 0.4898 | 0.48265 | 0.46939 | 0.45408 | 0.43673 | 0.41837 | 0.39694 | 0.36735 | 0.34592 | 0.32143 | 0.22041 | 0.18469 | 0.17143 | 0.58878 | 0.58265 | 0.58061 | 0.57551 | 0.56122 | 0.55 | 0.53367 | 0.51531 | 0.49694 | 0.47959 | 0.40408 | 0.37959 | 0.37143 | 0.54898 | 0.54592 | 0.53265 | 0.51735 | 0.50102 | 0.48367 | 0.46327 | 0.43571 | 0.41224 | 0.39082
|  | BLAIRLINNANS | HE |  |  |  |  | 0.48878 | 0.48061 | 0.46837 | 0.45102 | 0.43367 | 0.41429 | 0.39082 | 0.35918 | 0.33469 | 0.30408 | 0.17653 | 0.13163 | 0.11327 | 0.58878 | 0.58367 | 0.58163 | 0.57143 | 0.5602 | 0.5449 | 0.52551 | 0.50306 | 0.48571 | 0.46429 | 0.36939 | 0.33673 | 0.32143 | 0.54898 | 0.54286 | 0.53265 | 0.51429 | 0.49796 | 0.48061 | 0.45612 | 0.42653 | 0.40306 | 0.37347
|  | BLAIRLINNANS | CF |  |  |  |  | 0.49388 | 0.4898 | 0.48061 | 0.46939 | 0.45816 | 0.44388 | 0.43163 | 0.41122 | 0.39286 | 0.37857 | 0.27449 | 0.18571 | 0.13776 | 0.59184 | 0.58367 | 0.58367 | 0.58061 | 0.57551 | 0.56633 | 0.55714 | 0.54286 | 0.52857 | 0.51735 | 0.4398 | 0.37551 | 0.34082 | 0.55306 | 0.55 | 0.54388 | 0.53367 | 0.52143 | 0.50714 | 0.4949 | 0.47551 | 0.45714 | 0.44388
| BOAT OF GARTEN | BOAT OF GARTEN | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 0.436 | 7.6398 | 7.5633 | 7.4878 | 7.3847 | 7.2857 | 7.1694 | 7.0724 | 6.8816 | 6.698 | 6.5357 | 6.2918 | 6.1776 | 6.149 | 8.9255 | 8.8796 | 8.8296 | 8.7602 | 8.6898 | 8.6102 | 8.5469 | 8.4235 | 8.302 | 8.198 | 8.0112 | 7.9 | 7.4776 | 8.3306 | 8.2561 | 8.1847 | 8.0878 | 7.9898 | 7.8786 | 7.7867 | 7.6071 | 7.4347 | 7.2806
|  | BOAT OF GARTEN | EE |  |  |  |  | 7.6398 | 7.5633 | 7.4878 | 7.3847 | 7.2857 | 7.1694 | 7.0724 | 6.8816 | 6.698 | 6.5357 | 6.2918 | 6.2398 | 6.2031 | 8.9255 | 8.8796 | 8.8296 | 8.7602 | 8.6898 | 8.6102 | 8.5469 | 8.4235 | 8.302 | 8.198 | 8.0112 | 7.9 | 7.7133 | 8.3306 | 8.2561 | 8.1847 | 8.0878 | 7.9898 | 7.8786 | 7.7867 | 7.6071 | 7.4347 | 7.2806
|  | BOAT OF GARTEN | HT |  |  |  |  | 7.6847 | 7.6245 | 7.5582 | 7.4786 | 7.4194 | 7.2949 | 7.1684 | 7.0112 | 6.9367 | 6.8235 | 6.3776 | 6.1776 | 6.149 | 8.9571 | 8.9224 | 8.8827 | 8.8337 | 8.798 | 8.7214 | 8.6469 | 8.55 | 8.5071 | 8.4316 | 8.1378 | 8.0153 | 8 | 8.3561 | 8.3082 | 8.2561 | 8.1796 | 8.1224 | 8.0071 | 7.8918 | 7.7429 | 7.6755 | 7.5663
|  | BOAT OF GARTEN | HE |  |  |  |  | 7.6837 | 7.6327 | 7.5816 | 7.5153 | 7.4684 | 7.3949 | 7.3122 | 7.1735 | 7.0847 | 6.9449 | 6.4704 | 6.348 | 6.3276 | 8.9531 | 8.9235 | 8.8878 | 8.8449 | 8.8102 | 8.7602 | 8.7031 | 8.6122 | 8.5571 | 8.4653 | 8.1316 | 7.9745 | 7.8 | 8.3551 | 8.3143 | 8.2755 | 8.2112 | 8.1673 | 8.0949 | 8.0194 | 7.8878 | 7.8051 | 7.6755
|  | BOAT OF GARTEN | CF |  |  |  |  | 7.6837 | 7.6378 | 7.5959 | 7.55 | 7.4888 | 7.451 | 7.3888 | 7.3204 | 7.2204 | 7.1194 | 6.7439 | 6.4714 | 6.3367 | 8.9561 | 8.9255 | 8.901 | 8.8694 | 8.8296 | 8.801 | 8.7531 | 8.699 | 8.6316 | 8.5612 | 8.249 | 7.9061 | 7.4776 | 8.3643 | 8.3286 | 8.2908 | 8.2469 | 8.1878 | 8.1541 | 8.0908 | 8.0276 | 7.9347 | 7.8378
| PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 1.41 | -0.93596 | -1.0288 | -1.1441 | -1.2696 | -1.4054 | -1.8594 | -2.4176 | -3.1278 | -3.9186 | -4.8625 | -5.9666 | -6.1819 | -6.2972 | 0.12016 | 0.042608 | -0.050249 | -0.15739 | -0.26964 | -0.72576 | -1.2686 | -1.9656 | -2.7431 | -3.6829 | -4.6462 | -4.7972 | -4.8829 | 0.19975 | 0.12016 | 0.026282 | -0.084943 | -0.20025 | -0.64719 | -1.1839 | -1.8666 | -2.6298 | -3.5451
|  | BODDAM | EE |  |  |  |  | -0.93596 | -1.0288 | -1.1441 | -1.2696 | -1.4054 | -1.7758 | -2.3217 | -2.9135 | -3.5349 | -4.2717 | -5.9666 | -6.136 | -6.1625 | 0.12016 | 0.042608 | -0.050249 | -0.15739 | -0.26964 | -0.62372 | -1.1492 | -1.7176 | -2.3207 | -3.0451 | -4.6462 | -4.7605 | -4.7768 | 0.19975 | 0.12016 | 0.026282 | -0.084943 | -0.20025 | -0.54923 | -1.0676 | -1.6268 | -2.2207 | -2.938
|  | BODDAM | HT |  |  |  |  | -0.91249 | -0.99923 | -1.1002 | -1.2186 | -1.3431 | -1.8594 | -2.4176 | -3.1278 | -3.9186 | -4.8625 | -5.9105 | -6.1819 | -6.2737 | 0.14057 | 0.066078 | -0.013514 | -0.11351 | -0.2227 | -0.72576 | -1.2686 | -1.9656 | -2.7431 | -3.6829 | -4.587 | -4.7839 | -4.8554 | 0.21812 | 0.14465 | 0.058935 | -0.043106 | -0.15535 | -0.64719 | -1.1839 | -1.8666 | -2.6298 | -3.5451
|  | BODDAM | HE |  |  |  |  | -0.90841 | -0.98902 | -1.0758 | -1.1778 | -1.2962 | -1.6492 | -2.1656 | -2.7349 | -3.3533 | -4.0962 | -5.9319 | -6.1758 | -6.2972 | 0.14567 | 0.074241 | 0.0038327 | -0.086984 | -0.188 | -0.52678 | -1.0309 | -1.5819 | -2.1849 | -2.9196 | -4.6268 | -4.7972 | -4.8829 | 0.22322 | 0.15077 | 0.078322 | -0.011473 | -0.11351 | -0.44923 | -0.94311 | -1.4849 | -2.0798 | -2.7951
|  | BODDAM | CF |  |  |  |  | -0.8778 | -0.92372 | -0.97474 | -1.0309 | -1.1002 | -1.2533 | -1.4707 | -1.7656 | -2.0717 | -2.4554 | -4.3441 | -5.7758 | -6.1105 | 0.17016 | 0.13138 | 0.084445 | 0.036486 | -0.022698 | -0.16964 | -0.37984 | -0.66453 | -0.96453 | -1.3431 | -3.1737 | -4.5288 | -4.7727 | 0.24873 | 0.20996 | 0.16506 | 0.11608 | 0.055873 | -0.085963 | -0.29311 | -0.57372 | -0.86658 | -1.237
| TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | 0.304 | -2.7908 | -2.848 | -2.9408 | -3.0582 | -3.1745 | -3.3367 | -3.5255 | -3.6867 | -3.8153 | -3.9745 | -4.6704 | -5.0061 | -5.1194 | -1.6429 | -1.6796 | -1.7245 | -1.7786 | -1.8337 | -1.9031 | -2.0082 | -2.1173 | -2.199 | -2.3265 | -2.9214 | -3.1694 | -3.2612 | -2.1531 | -2.2235 | -2.3061 | -2.4071 | -2.5153 | -2.6449 | -2.7888 | -2.9388 | -3.0622 | -3.2102
|  | BONSKEID | EE |  |  |  |  | -2.7908 | -2.848 | -2.9408 | -3.0582 | -3.1745 | -3.3367 | -3.5255 | -3.6867 | -3.8153 | -3.9745 | -4.5133 | -4.7031 | -4.748 | -1.6429 | -1.6796 | -1.7245 | -1.7786 | -1.8337 | -1.9031 | -2.0082 | -2.1173 | -2.199 | -2.2929 | -2.5918 | -2.7163 | -2.8357 | -2.1531 | -2.2235 | -2.3061 | -2.4071 | -2.5153 | -2.6449 | -2.7888 | -2.9388 | -3.0622 | -3.1888
|  | BONSKEID | HT |  |  |  |  | -2.7571 | -2.8224 | -2.9224 | -3.0459 | -3.1714 | -3.298 | -3.4122 | -3.549 | -3.6969 | -3.8714 | -4.4184 | -4.7061 | -4.7541 | -1.6163 | -1.649 | -1.6847 | -1.7265 | -1.7694 | -1.8255 | -1.8827 | -1.9663 | -2.048 | -2.1469 | -2.4724 | -2.6255 | -2.6469 | -2.1143 | -2.1633 | -2.2286 | -2.3051 | -2.4061 | -2.5194 | -2.6214 | -2.75 | -2.8816 | -3.0388
|  | BONSKEID | HE |  |  |  |  | -2.7714 | -2.8255 | -2.8786 | -2.9653 | -3.0724 | -3.2082 | -3.3531 | -3.5194 | -3.6857 | -3.8663 | -4.6704 | -5.0061 | -5.0296 | -1.6296 | -1.6663 | -1.7041 | -1.75 | -1.8031 | -1.8684 | -1.9561 | -2.0786 | -2.1969 | -2.3265 | -2.9214 | -3.1694 | -3.1867 | -2.1306 | -2.2 | -2.2714 | -2.3622 | -2.4633 | -2.5888 | -2.7245 | -2.8847 | -3.0388 | -3.2102
|  | BONSKEID | CF |  |  |  |  | -2.752 | -2.7776 | -2.8112 | -2.848 | -2.899 | -2.9653 | -3.0571 | -3.1592 | -3.2592 | -3.3867 | -4.0388 | -4.6398 | -5.1194 | -1.6153 | -1.6316 | -1.6602 | -1.6847 | -1.7133 | -1.75 | -1.7969 | -1.849 | -1.9041 | -1.9939 | -2.4724 | -2.9133 | -3.2612 | -2.1112 | -2.1378 | -2.1847 | -2.2347 | -2.2929 | -2.3643 | -2.4469 | -2.549 | -2.6429 | -2.7612
| PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | NO | YES | 0.841 | 4.6282 | 4.5312 | 4.3098 | 3.9761 | 3.8343 | 3.1986 | 2.7373 | 2.322 | 2.0618 | 1.6322 | -0.44837 | -2.4463 | -4.6922 | 5.2965 | 5.2373 | 5.0231 | 4.6873 | 4.5955 | 3.9016 | 3.4955 | 3.119 | 2.8067 | 2.2588 | 0.047551 | -2.2422 | -4.6953 | 5.0455 | 4.9588 | 4.7108 | 4.3302 | 4.1976 | 3.4435 | 2.9302 | 2.5016 | 2.2292 | 1.6476
|  | BOWMORE | EE |  |  |  |  | 4.6282 | 4.5312 | 4.4006 | 4.2792 | 3.9843 | 3.5445 | 3.271 | 2.8965 | 2.4282 | 2.0812 | 0.97408 | -0.78306 | -1.931 | 5.2965 | 5.2373 | 5.1547 | 5.0822 | 4.818 | 4.3812 | 4.1527 | 3.8394 | 3.3751 | 3.0588 | 1.9516 | -0.094286 | -1.1729 | 5.0455 | 4.9588 | 4.8363 | 4.7261 | 4.4088 | 3.9149 | 3.6251 | 3.2241 | 2.6976 | 2.32
|  | BOWMORE | HT |  |  |  |  | 4.6516 | 4.568 | 4.3098 | 3.9761 | 3.8343 | 3.1986 | 2.7373 | 2.322 | 2.0618 | 1.8476 | 0.69245 | -1.5035 | -3.6688 | 5.321 | 5.2751 | 5.0231 | 4.6873 | 4.6057 | 3.9016 | 3.4955 | 3.119 | 2.9118 | 2.722 | 1.5965 | -0.80449 | -2.9861 | 5.07 | 4.9996 | 4.7108 | 4.3302 | 4.1976 | 3.4435 | 2.9302 | 2.5016 | 2.2455 | 2.02
|  | BOWMORE | HE |  |  |  |  | 4.6659 | 4.5976 | 4.3894 | 4.0904 | 3.8884 | 3.2761 | 2.9904 | 2.5394 | 2.1404 | 1.6322 | -0.44837 | -2.4463 | -4.6922 | 5.3302 | 5.2843 | 5.0782 | 4.77 | 4.5955 | 3.9088 | 3.6516 | 3.2129 | 2.8067 | 2.2588 | 0.047551 | -2.2422 | -4.6953 | 5.0833 | 5.0241 | 4.7884 | 4.4496 | 4.2373 | 3.5078 | 3.1996 | 2.6863 | 2.2292 | 1.6476
|  | BOWMORE | CF |  |  |  |  | 4.6873 | 4.6404 | 4.5873 | 4.5129 | 4.3394 | 4.071 | 3.8853 | 3.7129 | 3.5271 | 3.2914 | 2.3159 | 1.4455 | 0.57714 | 5.3414 | 5.3098 | 5.2741 | 5.2261 | 5.068 | 4.7976 | 4.6343 | 4.4853 | 4.2976 | 4.0547 | 3.0976 | 2.3302 | 1.5567 | 5.1016 | 5.0557 | 5.0057 | 4.9343 | 4.7445 | 4.4435 | 4.2476 | 4.0639 | 3.8598 | 3.5965
| SHETLAND | BRAE | MINIMUM HEADROOM | HU3604068816 | YES | YES | 0.995 | -1.5646 | -1.6085 | -1.6544 | -1.6993 | -1.8717 | -2.1717 | -2.4473 | -2.7748 | -3.136 | -3.382 | -3.8513 | -3.9248 | -3.9371 | -0.46358 | -0.50338 | -0.53909 | -0.57481 | -0.71971 | -1.032 | -1.3177 | -1.6585 | -2.035 | -2.2738 | -2.5432 | -2.5932 | -2.7942 | -1.0054 | -1.0524 | -1.0952 | -1.136 | -1.3075 | -1.6095 | -1.8891 | -2.2228 | -2.5891 | -2.8289
|  | BRAE | EE |  |  |  |  | -1.5646 | -1.6085 | -1.6544 | -1.6993 | -1.8666 | -2.1105 | -2.4197 | -2.7054 | -3.032 | -3.2973 | -3.8513 | -3.8789 | -3.9064 | -0.46358 | -0.50338 | -0.53909 | -0.57481 | -0.71358 | -0.92277 | -1.2146 | -1.4932 | -1.7983 | -2.0411 | -2.5432 | -2.5534 | -2.6595 | -1.0054 | -1.0524 | -1.0952 | -1.136 | -1.2922 | -1.5217 | -1.8146 | -2.0922 | -2.3962 | -2.6462
|  | BRAE | HT |  |  |  |  | -1.5513 | -1.5871 | -1.6258 | -1.6666 | -1.8717 | -2.1717 | -2.4473 | -2.7748 | -3.136 | -3.382 | -3.782 | -3.9248 | -3.9371 | -0.44726 | -0.47175 | -0.49522 | -0.52175 | -0.71971 | -1.032 | -1.3177 | -1.6585 | -2.035 | -2.2738 | -2.5187 | -2.5717 | -2.5881 | -0.99318 | -1.0299 | -1.0677 | -1.1054 | -1.3075 | -1.6095 | -1.8891 | -2.2228 | -2.5891 | -2.8289
|  | BRAE | HE |  |  |  |  | -1.5534 | -1.582 | -1.6115 | -1.6442 | -1.782 | -1.9993 | -2.2636 | -2.534 | -2.8187 | -3.0717 | -3.7166 | -3.7952 | -3.8217 | -0.44828 | -0.47175 | -0.49216 | -0.51664 | -0.64726 | -0.87277 | -1.1473 | -1.4248 | -1.7248 | -1.9697 | -2.5422 | -2.5932 | -2.6166 | -0.99624 | -1.0268 | -1.0544 | -1.085 | -1.2238 | -1.4422 | -1.7095 | -1.9881 | -2.282 | -2.5299
|  | BRAE | CF |  |  |  |  | -1.5452 | -1.5666 | -1.5881 | -1.6126 | -1.6687 | -1.7687 | -1.8881 | -2.0289 | -2.186 | -2.3381 | -3.0962 | -3.6758 | -3.7728 | -0.43909 | -0.46052 | -0.47889 | -0.50236 | -0.55848 | -0.65032 | -0.76971 | -0.90644 | -1.0656 | -1.2207 | -1.9677 | -2.5422 | -2.7942 | -0.98399 | -1.0044 | -1.0228 | -1.0503 | -1.1105 | -1.2146 | -1.336 | -1.4738 | -1.6309 | -1.7768
| BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | NO | 2.524 | 3.7155 | 3.338 | 2.8176 | 2.0737 | 1.7257 | 0.33286 | -0.45388 | -1.308 | -2.1192 | -3.0957 | -7.2018 | -11.6478 | -15.7483 | 5.6487 | 5.4395 | 4.9915 | 4.3385 | 4.1599 | 2.7609 | 2.2579 | 1.7038 | 1.1711 | 0.13541 | -4.2901 | -8.6296 | -13.1123 | 4.8367 | 4.504 | 3.8938 | 3.0857 | 2.7489 | 1.1826 | 0.44893 | -0.34903 | -1.0878 | -1.9929
|  | BRECHIN | EE |  |  |  |  | 3.7155 | 3.338 | 2.9522 | 2.5288 | 1.9359 | 0.96551 | 0.12163 | -0.64163 | -1.2008 | -2.0967 | -6.1988 | -10.4345 | -12.5299 | 5.6487 | 5.4395 | 5.2293 | 5.0028 | 4.5232 | 3.6497 | 3.0456 | 2.5681 | 2.0283 | 1.4007 | -1.6758 | -5.7296 | -7.896 | 4.8367 | 4.504 | 4.1602 | 3.7622 | 3.1255 | 2.0642 | 1.2051 | 0.46219 | -0.14393 | -0.98474
|  | BRECHIN | HT |  |  |  |  | 3.8053 | 3.4645 | 2.8176 | 2.0737 | 1.7257 | 0.33286 | -0.45388 | -1.308 | -2.1192 | -3.0957 | -6.9416 | -11.6478 | -15.3217 | 5.7007 | 5.5191 | 4.9915 | 4.3385 | 4.1599 | 2.7609 | 2.2579 | 1.7038 | 1.213 | 0.57827 | -2.1717 | -6.5419 | -10.1521 | 4.8938 | 4.5755 | 3.8938 | 3.0857 | 2.7489 | 1.1826 | 0.44893 | -0.34903 | -1.0878 | -1.9929
|  | BRECHIN | HE |  |  |  |  | 3.8288 | 3.588 | 3.0951 | 2.488 | 2.1135 | 0.90327 | 0.2798 | -0.47224 | -1.2457 | -2.3641 | -7.2018 | -11.6396 | -15.7483 | 5.7089 | 5.5732 | 5.1466 | 4.5864 | 4.2854 | 3.0007 | 2.467 | 1.8334 | 1.1711 | 0.13541 | -4.2901 | -8.6296 | -13.1123 | 4.9112 | 4.703 | 4.1928 | 3.5428 | 3.1581 | 1.7744 | 1.104 | 0.32138 | -0.49597 | -1.7011
|  | BRECHIN | CF |  |  |  |  | 3.892 | 3.7318 | 3.5482 | 3.3808 | 3.1084 | 2.638 | 2.2961 | 1.9492 | 1.6553 | 1.2247 | -0.86306 | -3.3314 | -5.6789 | 5.7415 | 5.6466 | 5.5395 | 5.4354 | 5.1803 | 4.7058 | 4.3885 | 4.0926 | 3.8038 | 3.4058 | 1.415 | -0.75719 | -3.0419 | 4.9734 | 4.8428 | 4.6887 | 4.5469 | 4.2591 | 3.7489 | 3.3979 | 3.0397 | 2.7255 | 2.2724
| PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | NO | 6.325 | -2.832 | -3.6105 | -5.6412 | -8.1126 | -9.3585 | -13.382 | -14.7758 | -16.2616 | -17.2728 | -19.131 | -30.0952 | -40.3218 | -51.2728 | 0.6966 | 0.080273 | -1.7646 | -4.1207 | -4.8707 | -9.0595 | -9.9861 | -11.5095 | -12.9197 | -15.5412 | -26.632 | -36.0886 | -45.5733 | -1.0672 | -1.807 | -4.0039 | -6.6937 | -7.8008 | -12.3917 | -13.6702 | -15.0264 | -16.1621 | -18.9784
|  | BRIDGE OF DON | EE |  |  |  |  | -2.832 | -3.6105 | -4.5544 | -5.7493 | -7.7442 | -10.4116 | -11.9452 | -13.1116 | -15.1575 | -16.731 | -24.2779 | -36.4289 | -41.6769 | 0.6966 | 0.080273 | -0.58299 | -1.2748 | -2.9595 | -5.4656 | -6.6636 | -7.2503 | -8.9881 | -10.1544 | -16.0636 | -29.3253 | -35.4121 | -1.0672 | -1.807 | -2.7376 | -3.8151 | -5.8457 | -8.7284 | -10.2815 | -11.2998 | -13.4294 | -14.9886
|  | BRIDGE OF DON | HT |  |  |  |  | -2.7463 | -3.585 | -5.6412 | -8.1126 | -9.3585 | -13.382 | -14.7758 | -16.2616 | -17.2728 | -18.9054 | -26.8054 | -40.3218 | -51.2728 | 0.74456 | 0.084355 | -1.7646 | -4.1207 | -4.8707 | -9.0595 | -9.8565 | -10.7065 | -11.1585 | -12.0901 | -18.435 | -33.1345 | -45.5733 | -0.98554 | -1.7764 | -4.0039 | -6.6937 | -7.8008 | -12.3917 | -13.6702 | -15.0264 | -15.907 | -17.3937
|  | BRIDGE OF DON | HE |  |  |  |  | -2.7299 | -3.4452 | -4.8483 | -6.832 | -8.1912 | -11.9473 | -13.6054 | -15.2789 | -16.6381 | -19.131 | -30.0952 | -39.6116 | -41.734 | 0.76599 | 0.18946 | -1.3044 | -3.3126 | -4.4687 | -8.5432 | -9.9861 | -11.5095 | -12.9197 | -15.5412 | -26.632 | -36.0886 | -37.6498 | -0.96718 | -1.6508 | -3.21 | -5.4417 | -6.8396 | -11.1927 | -12.9151 | -14.6621 | -16.1621 | -18.9784
|  | BRIDGE OF DON | CF |  |  |  |  | -2.6228 | -3.0758 | -3.483 | -3.9003 | -4.9156 | -6.3942 | -7.3534 | -8.2381 | -9.0769 | -9.8003 | -13.9218 | -18.5575 | -23.5065 | 0.83946 | 0.49456 | 0.16293 | -0.16871 | -1.1218 | -2.6167 | -3.5452 | -4.3187 | -5.1126 | -5.9401 | -9.683 | -13.8325 | -18.657 | -0.86616 | -1.2896 | -1.6804 | -2.0753 | -3.1937 | -4.8468 | -5.859 | -6.7447 | -7.6019 | -8.4243
| BRIDGE OF DUN | BRIDGE OF DUN | MINIMUM HEADROOM | NO 66018 58883 | YES | NO | 0.051 | 0.12347 | 0.087755 | 0.057143 | 0.022449 | -0.019388 | -0.065306 | -0.10612 | -0.16939 | -0.22653 | -0.28061 | -0.44184 | -0.52245 | -0.54286 | 0.37347 | 0.35204 | 0.33469 | 0.30918 | 0.27755 | 0.24592 | 0.22245 | 0.17959 | 0.14388 | 0.10612 | 0.016327 | -0.02449 | -0.11327 | 0.23061 | 0.19694 | 0.16735 | 0.13469 | 0.090816 | 0.042857 | 0.0071429 | -0.056122 | -0.1102 | -0.16224
|  | BRIDGE OF DUN | EE |  |  |  |  | 0.12347 | 0.087755 | 0.057143 | 0.022449 | -0.019388 | -0.065306 | -0.10612 | -0.16939 | -0.22653 | -0.28061 | -0.44184 | -0.50816 | -0.52245 | 0.37347 | 0.35204 | 0.33469 | 0.30918 | 0.27755 | 0.24592 | 0.22245 | 0.17959 | 0.14388 | 0.10612 | 0.016327 | -0.02449 | -0.07449 | 0.23061 | 0.19694 | 0.16735 | 0.13469 | 0.090816 | 0.042857 | 0.0071429 | -0.056122 | -0.1102 | -0.16224
|  | BRIDGE OF DUN | HT |  |  |  |  | 0.13878 | 0.10714 | 0.077551 | 0.039796 | 0.011224 | -0.02449 | -0.068367 | -0.12041 | -0.15612 | -0.20612 | -0.41837 | -0.52245 | -0.54286 | 0.3898 | 0.37449 | 0.35816 | 0.33061 | 0.31939 | 0.29286 | 0.27143 | 0.23673 | 0.22245 | 0.19082 | 0.055102 | 0.0091837 | -0.011224 | 0.24898 | 0.22143 | 0.19286 | 0.15714 | 0.13367 | 0.095918 | 0.059184 | 0.0081633 | -0.02449 | -0.072449
|  | BRIDGE OF DUN | HE |  |  |  |  | 0.13878 | 0.11939 | 0.09898 | 0.069388 | 0.054082 | 0.02551 | -0.0061224 | -0.05 | -0.092857 | -0.11837 | -0.35918 | -0.45612 | -0.50714 | 0.3898 | 0.37755 | 0.36429 | 0.33776 | 0.32959 | 0.3051 | 0.28469 | 0.2551 | 0.22449 | 0.19898 | 0.042857 | -0.013265 | -0.058163 | 0.24898 | 0.22959 | 0.20918 | 0.18061 | 0.16122 | 0.13163 | 0.093878 | 0.046939 | 0.0020408 | -0.034694
|  | BRIDGE OF DUN | CF |  |  |  |  | 0.14592 | 0.12959 | 0.11327 | 0.092857 | 0.081633 | 0.059184 | 0.032653 | 0.013265 | -0.012245 | -0.039796 | -0.16429 | -0.32653 | -0.43469 | 0.3949 | 0.38265 | 0.37245 | 0.35306 | 0.34694 | 0.32857 | 0.30714 | 0.29184 | 0.27041 | 0.24592 | 0.14694 | 0.0040816 | -0.11327 | 0.2551 | 0.23776 | 0.22245 | 0.2 | 0.19286 | 0.16837 | 0.14286 | 0.12449 | 0.096939 | 0.068367
| ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 0.747 | 10.3163 | 9.8643 | 9.3316 | 8.6918 | 8.0102 | 7.2776 | 6.6908 | 6.0296 | 5.349 | 4.6265 | 2.3673 | 1.8122 | 0.97959 | 11.599 | 11.299 | 10.9469 | 10.5224 | 10.0592 | 9.5653 | 9.1827 | 8.7388 | 8.2643 | 7.7347 | 6.1684 | 6.2087 | 5.7423 | 11.4087 | 11.0117 | 10.5454 | 9.9832 | 9.377 | 8.725 | 8.2046 | 7.6138 | 7.0036 | 6.3658
|  | BRIDGE OF EARN | EE |  |  |  |  | 10.3378 | 9.8959 | 9.3898 | 8.8173 | 8.1847 | 7.501 | 6.8398 | 6.1847 | 5.5276 | 4.8418 | 2.3673 | 1.8582 | 1.0163 | 11.6153 | 11.3214 | 10.9867 | 10.6041 | 10.1735 | 9.7082 | 9.2622 | 8.8143 | 8.3704 | 7.8959 | 6.1684 | 6.2087 | 5.9128 | 11.4138 | 11.0393 | 10.5923 | 10.0852 | 9.5148 | 8.8974 | 8.3148 | 7.7199 | 7.1301 | 6.5138
|  | BRIDGE OF EARN | HT |  |  |  |  | 10.3163 | 9.8643 | 9.3316 | 8.6918 | 8.0102 | 7.2776 | 6.6908 | 6.0296 | 5.349 | 4.6265 | 2.3939 | 1.8122 | 0.97959 | 11.599 | 11.299 | 10.9469 | 10.5224 | 10.0592 | 9.5653 | 9.1827 | 8.7388 | 8.2643 | 7.7347 | 6.3071 | 6.4434 | 6.4026 | 11.4087 | 11.0117 | 10.5454 | 9.9832 | 9.377 | 8.725 | 8.2046 | 7.6138 | 7.0036 | 6.3658
|  | BRIDGE OF EARN | HE |  |  |  |  | 10.3816 | 9.9898 | 9.5551 | 9.0194 | 8.4531 | 7.8276 | 7.2561 | 6.6898 | 6.1184 | 5.5265 | 2.9306 | 2.3337 | 1.3898 | 11.652 | 11.3776 | 11.0857 | 10.7173 | 10.3296 | 9.899 | 9.4929 | 9.0867 | 8.6694 | 8.2163 | 6.3378 | 6.3985 | 6.0709 | 11.4679 | 11.127 | 10.7474 | 10.273 | 9.773 | 9.2138 | 8.7056 | 8.1964 | 7.6852 | 7.1628
|  | BRIDGE OF EARN | CF |  |  |  |  | 10.5653 | 10.2806 | 9.9388 | 9.5867 | 9.202 | 8.7684 | 8.3806 | 7.9908 | 7.5959 | 7.1602 | 4.8531 | 3.1398 | 1.8408 | 11.8041 | 11.6163 | 11.3857 | 11.1592 | 10.901 | 10.6041 | 10.3204 | 10.0357 | 9.7469 | 9.4245 | 7.6224 | 6.4913 | 5.7423 | 11.623 | 11.3903 | 11.1005 | 10.8036 | 10.4668 | 10.0791 | 9.7342 | 9.3883 | 9.0393 | 8.6505
| RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 0.069 | 0.61735 | 0.61633 | 0.61327 | 0.60714 | 0.59694 | 0.58571 | 0.57755 | 0.55918 | 0.54184 | 0.52857 | 0.51122 | 0.50714 | 0.50408 | 0.66224 | 0.6551 | 0.65918 | 0.65204 | 0.64286 | 0.63571 | 0.62959 | 0.61633 | 0.6051 | 0.59592 | 0.58571 | 0.57959 | 0.56122 | 0.63061 | 0.62755 | 0.62245 | 0.61224 | 0.59796 | 0.58673 | 0.57959 | 0.56122 | 0.54592 | 0.53163
|  | BRIDGE OF GAUR | EE |  |  |  |  | 0.61735 | 0.61939 | 0.61327 | 0.60714 | 0.59694 | 0.58571 | 0.57755 | 0.55918 | 0.54184 | 0.52857 | 0.51122 | 0.50714 | 0.50408 | 0.66224 | 0.66429 | 0.65918 | 0.65204 | 0.64286 | 0.63571 | 0.62959 | 0.61633 | 0.6051 | 0.59592 | 0.58571 | 0.57959 | 0.57041 | 0.63061 | 0.62755 | 0.62245 | 0.61224 | 0.59796 | 0.58673 | 0.57959 | 0.56122 | 0.54592 | 0.53163
|  | BRIDGE OF GAUR | HT |  |  |  |  | 0.62551 | 0.61633 | 0.61939 | 0.61224 | 0.61122 | 0.60204 | 0.59694 | 0.58469 | 0.57449 | 0.56531 | 0.51224 | 0.50714 | 0.50408 | 0.66429 | 0.6551 | 0.66429 | 0.65816 | 0.6551 | 0.64592 | 0.6449 | 0.63673 | 0.62755 | 0.62245 | 0.58571 | 0.58673 | 0.58571 | 0.64082 | 0.62959 | 0.62857 | 0.61939 | 0.61531 | 0.6051 | 0.59796 | 0.58776 | 0.57653 | 0.56837
|  | BRIDGE OF GAUR | HE |  |  |  |  | 0.62551 | 0.61735 | 0.62143 | 0.61735 | 0.61327 | 0.60612 | 0.60102 | 0.59388 | 0.58367 | 0.57755 | 0.51837 | 0.52041 | 0.51735 | 0.66429 | 0.65612 | 0.66633 | 0.6602 | 0.65918 | 0.65204 | 0.64694 | 0.6398 | 0.63265 | 0.63061 | 0.58673 | 0.58776 | 0.57857 | 0.64082 | 0.63163 | 0.63061 | 0.62347 | 0.62041 | 0.61327 | 0.60612 | 0.59592 | 0.58469 | 0.57857
|  | BRIDGE OF GAUR | CF |  |  |  |  | 0.62653 | 0.61735 | 0.61735 | 0.61837 | 0.61633 | 0.61327 | 0.60816 | 0.60408 | 0.59592 | 0.5898 | 0.55204 | 0.52959 | 0.51429 | 0.66429 | 0.65612 | 0.66122 | 0.66429 | 0.6602 | 0.65612 | 0.65204 | 0.64592 | 0.6398 | 0.63571 | 0.60714 | 0.58776 | 0.56122 | 0.64082 | 0.63061 | 0.62653 | 0.62653 | 0.62143 | 0.61837 | 0.6102 | 0.60714 | 0.59694 | 0.59082
| BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 2.036 | 2.994 | 2.946 | 2.8909 | 2.8195 | 2.7675 | 2.6899 | 2.6052 | 2.4634 | 2.3665 | 2.243 | 2.042 | 1.9695 | 1.4971 | 2.9369 | 2.9073 | 2.8695 | 2.8256 | 2.7899 | 2.7348 | 2.6787 | 2.5869 | 2.5277 | 2.4552 | 2.3011 | 2.4506 | 2.2129 | 2.8935 | 2.8486 | 2.7955 | 2.7272 | 2.6761 | 2.6037 | 2.52 | 2.3894 | 2.3027 | 2.1904
|  | BROADFORD | EE |  |  |  |  | 2.994 | 2.946 | 2.8909 | 2.8195 | 2.7675 | 2.6899 | 2.6052 | 2.4634 | 2.3665 | 2.243 | 2.042 | 2.0093 | 1.5379 | 2.9369 | 2.9073 | 2.8695 | 2.8256 | 2.7899 | 2.7348 | 2.6787 | 2.5869 | 2.5277 | 2.4552 | 2.3011 | 2.4506 | 2.3343 | 2.8935 | 2.8486 | 2.7955 | 2.7272 | 2.6761 | 2.6037 | 2.52 | 2.3894 | 2.3027 | 2.1904
|  | BROADFORD | HT |  |  |  |  | 3.0267 | 2.9848 | 2.943 | 2.8879 | 2.8409 | 2.7389 | 2.6552 | 2.542 | 2.4726 | 2.394 | 2.1022 | 1.9695 | 1.4971 | 2.9614 | 2.9338 | 2.9093 | 2.8767 | 2.8491 | 2.795 | 2.7481 | 2.6818 | 2.6369 | 2.5858 | 2.3889 | 2.5282 | 2.517 | 2.9251 | 2.8843 | 2.8445 | 2.7935 | 2.7476 | 2.6588 | 2.5833 | 2.4802 | 2.4129 | 2.3404
|  | BROADFORD | HE |  |  |  |  | 3.0267 | 2.995 | 2.9614 | 2.9185 | 2.8818 | 2.8297 | 2.7869 | 2.6909 | 2.6022 | 2.5083 | 2.1756 | 2.092 | 1.6318 | 2.9573 | 2.9369 | 2.9154 | 2.8879 | 2.8634 | 2.8267 | 2.8011 | 2.742 | 2.6828 | 2.6236 | 2.393 | 2.5098 | 2.4037 | 2.9261 | 2.8935 | 2.8608 | 2.82 | 2.7843 | 2.7364 | 2.6976 | 2.6068 | 2.5282 | 2.4404
|  | BROADFORD | CF |  |  |  |  | 3.0348 | 3.0073 | 2.9695 | 2.944 | 2.9042 | 2.8756 | 2.8338 | 2.7818 | 2.7348 | 2.6654 | 2.3705 | 2.1981 | 1.6491 | 2.9624 | 2.946 | 2.9226 | 2.9032 | 2.8777 | 2.8593 | 2.8277 | 2.7909 | 2.7593 | 2.7124 | 2.4756 | 2.4802 | 2.2129 | 2.9323 | 2.9068 | 2.8721 | 2.8496 | 2.8098 | 2.7823 | 2.7404 | 2.6904 | 2.6517 | 2.5884
| CARRADALE 1 | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 0.333 | 2.9345 | 2.8131 | 2.6569 | 2.4835 | 2.3314 | 2.1365 | 1.9049 | 1.6824 | 1.4386 | 1.2182 | 0.64061 | 0.44265 | 0.004898 | 4.1967 | 4.1171 | 4.0202 | 3.909 | 3.8131 | 3.6794 | 3.5284 | 3.3784 | 3.2171 | 3.0702 | 2.6222 | 2.6253 | 2.058 | 3.5845 | 3.4692 | 3.3294 | 3.1651 | 3.0222 | 2.8345 | 2.611 | 2.4008 | 2.1661 | 1.9569
|  | BRODICK | EE |  |  |  |  | 2.9345 | 2.8131 | 2.6569 | 2.4835 | 2.3314 | 2.1365 | 1.9049 | 1.6824 | 1.4386 | 1.2182 | 0.64061 | 0.53857 | 0.074286 | 4.1967 | 4.1171 | 4.0202 | 3.909 | 3.8131 | 3.6794 | 3.5284 | 3.3784 | 3.2171 | 3.0702 | 2.6222 | 2.6253 | 2.3314 | 3.5845 | 3.4692 | 3.3294 | 3.1651 | 3.0222 | 2.8345 | 2.611 | 2.4008 | 2.1661 | 1.9569
|  | BRODICK | HT |  |  |  |  | 2.9835 | 2.8845 | 2.7631 | 2.6488 | 2.509 | 2.3488 | 2.2059 | 2.008 | 1.8151 | 1.611 | 0.80286 | 0.44265 | 0.004898 | 4.2324 | 4.1743 | 4.1039 | 4.0355 | 3.9549 | 3.8539 | 3.7692 | 3.6396 | 3.5141 | 3.3855 | 2.8447 | 2.811 | 2.7855 | 3.6284 | 3.5335 | 3.4253 | 3.3202 | 3.1947 | 3.0447 | 2.912 | 2.7212 | 2.5355 | 2.3416
|  | BRODICK | HE |  |  |  |  | 2.9824 | 2.9049 | 2.808 | 2.7171 | 2.6049 | 2.4702 | 2.3498 | 2.1773 | 2.0049 | 1.8304 | 1.0018 | 0.79469 | 0.37429 | 4.2335 | 4.1794 | 4.1182 | 4.058 | 3.9855 | 3.8916 | 3.8151 | 3.6957 | 3.5784 | 3.46 | 2.8692 | 2.812 | 2.5569 | 3.6202 | 3.5518 | 3.4671 | 3.3814 | 3.2824 | 3.1559 | 3.0437 | 2.8773 | 2.7141 | 2.5447
|  | BRODICK | CF |  |  |  |  | 2.9896 | 2.9345 | 2.8712 | 2.7835 | 2.7141 | 2.6202 | 2.5202 | 2.3947 | 2.3233 | 2.2069 | 1.609 | 1.059 | 0.35694 | 4.2478 | 4.2018 | 4.158 | 4.0988 | 4.0508 | 3.9824 | 3.908 | 3.8161 | 3.7569 | 3.6712 | 3.1671 | 2.7457 | 2.058 | 3.6488 | 3.5896 | 3.5233 | 3.4416 | 3.3773 | 3.2896 | 3.2008 | 3.0855 | 3.0182 | 2.9069
| BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | NO | 0.872 | 3.7833 | 3.7027 | 3.6241 | 3.52 | 3.4169 | 3.3016 | 3.2006 | 3.0282 | 2.8578 | 2.7067 | 2.469 | 2.37 | 2.3414 | 4.6516 | 4.6118 | 4.5669 | 4.5118 | 4.4557 | 4.3904 | 4.3394 | 4.2424 | 4.1384 | 4.0496 | 3.8822 | 3.7996 | 3.5588 | 4.3251 | 4.2567 | 4.1843 | 4.0843 | 3.9863 | 3.8771 | 3.7843 | 3.619 | 3.4598 | 3.32
|  | BRORA | EE |  |  |  |  | 3.7833 | 3.7027 | 3.6241 | 3.52 | 3.4169 | 3.3016 | 3.2006 | 3.0282 | 2.8578 | 2.7067 | 2.469 | 2.421 | 2.3924 | 4.6516 | 4.6118 | 4.5669 | 4.5118 | 4.4557 | 4.3904 | 4.3394 | 4.2424 | 4.1384 | 4.0496 | 3.8822 | 3.7996 | 3.6741 | 4.3251 | 4.2567 | 4.1843 | 4.0843 | 3.9863 | 3.8771 | 3.7843 | 3.619 | 3.4598 | 3.32
|  | BRORA | HT |  |  |  |  | 3.822 | 3.7598 | 3.6761 | 3.6037 | 3.5384 | 3.4312 | 3.3169 | 3.1771 | 3.1027 | 2.9904 | 2.5629 | 2.37 | 2.3414 | 4.6771 | 4.6445 | 4.6027 | 4.5639 | 4.5302 | 4.471 | 4.4108 | 4.3373 | 4.2986 | 4.2394 | 3.9904 | 3.8782 | 3.8639 | 4.3476 | 4.2935 | 4.2333 | 4.1669 | 4.1078 | 4.0067 | 3.9027 | 3.771 | 3.7016 | 3.5965
|  | BRORA | HE |  |  |  |  | 3.822 | 3.7761 | 3.7078 | 3.6527 | 3.5822 | 3.5343 | 3.4516 | 3.3322 | 3.2139 | 3.1302 | 2.5843 | 2.522 | 2.5078 | 4.6741 | 4.6486 | 4.6098 | 4.5812 | 4.5424 | 4.5139 | 4.47 | 4.4047 | 4.3353 | 4.2894 | 3.9598 | 3.871 | 3.7567 | 4.3465 | 4.3098 | 4.2639 | 4.2118 | 4.1445 | 4.0996 | 4.022 | 3.9098 | 3.7986 | 3.7231
|  | BRORA | CF |  |  |  |  | 3.8271 | 3.7792 | 3.7353 | 3.6894 | 3.6302 | 3.5659 | 3.5282 | 3.4649 | 3.3822 | 3.2965 | 2.9455 | 2.6873 | 2.5384 | 4.6751 | 4.6537 | 4.6271 | 4.6016 | 4.572 | 4.5322 | 4.5098 | 4.471 | 4.422 | 4.37 | 4.1333 | 3.8639 | 3.5588 | 4.3516 | 4.3169 | 4.2822 | 4.2496 | 4.1914 | 4.1302 | 4.0976 | 4.0373 | 3.9578 | 3.8782
| MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | NO | 1.811 | 5.081 | 4.7973 | 4.5167 | 4.1738 | 3.8636 | 3.485 | 2.9228 | 2.6871 | 2.1493 | 1.6646 | -0.22007 | -1.119 | -1.2517 | 7.5095 | 7.4371 | 7.331 | 7.0942 | 6.8769 | 6.6014 | 6.2401 | 6.1391 | 5.7963 | 5.485 | 4.1473 | 3.1442 | -0.2966 | 6.3952 | 6.1534 | 5.9167 | 5.6167 | 5.3269 | 4.981 | 4.4626 | 4.2208 | 3.7228 | 3.2728
|  | BROUGHTY FERRY | EE |  |  |  |  | 5.081 | 4.7973 | 4.5167 | 4.1738 | 3.8636 | 3.485 | 2.9228 | 2.6871 | 2.1493 | 1.6646 | -0.22007 | -0.83537 | -1.0129 | 7.5095 | 7.4371 | 7.331 | 7.0942 | 6.8769 | 6.6014 | 6.2401 | 6.1391 | 5.7963 | 5.485 | 4.1473 | 3.1442 | 1.6687 | 6.3952 | 6.1534 | 5.9167 | 5.6167 | 5.3269 | 4.981 | 4.4626 | 4.2208 | 3.7228 | 3.2728
|  | BROUGHTY FERRY | HT |  |  |  |  | 5.1942 | 4.9697 | 4.7146 | 4.4799 | 4.1963 | 3.8861 | 3.4616 | 2.9493 | 2.4514 | 1.932 | -0.041494 | -1.119 | -1.2517 | 7.5636 | 7.5146 | 7.4585 | 7.4146 | 7.2412 | 7.0514 | 6.8238 | 6.534 | 6.2452 | 5.9493 | 4.9534 | 4.3881 | 4.3126 | 6.4759 | 6.2728 | 6.0524 | 5.8452 | 5.6065 | 5.3463 | 4.9503 | 4.482 | 4.0187 | 3.5401
|  | BROUGHTY FERRY | HE |  |  |  |  | 5.1932 | 5.0565 | 4.8871 | 4.7391 | 4.5401 | 4.3269 | 4.0116 | 3.6054 | 3.2116 | 2.8014 | 1.2881 | 0.15442 | -0.12721 | 7.5432 | 7.4881 | 7.4279 | 7.3667 | 7.2789 | 7.1014 | 6.8963 | 6.6095 | 6.334 | 6.0422 | 4.8463 | 3.5861 | 2.1065 | 6.4718 | 6.3575 | 6.2218 | 6.0993 | 5.9432 | 5.7544 | 5.4595 | 5.085 | 4.7218 | 4.3442
|  | BROUGHTY FERRY | CF |  |  |  |  | 5.2595 | 5.184 | 5.0799 | 4.9636 | 4.8738 | 4.7463 | 4.583 | 4.435 | 4.2575 | 4.0738 | 3.2677 | 1.8238 | 0.60034 | 7.5687 | 7.533 | 7.4881 | 7.4391 | 7.3942 | 7.285 | 7.1044 | 6.9299 | 6.732 | 6.5248 | 5.4452 | 3.1799 | -0.2966 | 6.531 | 6.4759 | 6.3963 | 6.3105 | 6.2422 | 6.1401 | 5.9963 | 5.8544 | 5.6932 | 5.5259
| DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 0.501 | 11.8296 | 11.752 | 11.651 | 11.5551 | 11.4245 | 11.2918 | 11.1306 | 10.9786 | 10.8082 | 10.6622 | 10.2602 | 10.0827 | 9.3133 | 12.3908 | 12.348 | 12.298 | 12.248 | 12.1622 | 12.0704 | 11.9653 | 11.8571 | 11.7357 | 11.6327 | 11.3296 | 11.6015 | 11.4321 | 12.1148 | 12.0352 | 11.9393 | 11.8454 | 11.7199 | 11.5923 | 11.4362 | 11.2913 | 11.125 | 10.9852
|  | BRUCHAG | EE |  |  |  |  | 11.8296 | 11.752 | 11.651 | 11.5551 | 11.4245 | 11.2918 | 11.1306 | 10.9786 | 10.8082 | 10.6622 | 10.2602 | 10.1827 | 9.3633 | 12.3908 | 12.348 | 12.298 | 12.248 | 12.1622 | 12.0704 | 11.9653 | 11.8571 | 11.7357 | 11.6327 | 11.3296 | 11.6015 | 11.4321 | 12.1148 | 12.0352 | 11.9393 | 11.8454 | 11.7199 | 11.5923 | 11.4362 | 11.2913 | 11.125 | 10.9852
|  | BRUCHAG | HT |  |  |  |  | 11.8867 | 11.8143 | 11.7439 | 11.6633 | 11.5653 | 11.4571 | 11.3602 | 11.2255 | 11.0939 | 10.952 | 10.3765 | 10.0827 | 9.3133 | 12.4194 | 12.3867 | 12.352 | 12.3133 | 12.2684 | 12.2061 | 12.1439 | 12.0582 | 11.9684 | 11.8765 | 11.4684 | 11.6403 | 11.6301 | 12.1689 | 12.0995 | 12.0311 | 11.9536 | 11.8617 | 11.7556 | 11.6658 | 11.5362 | 11.4077 | 11.2699
|  | BRUCHAG | HE |  |  |  |  | 11.8878 | 11.8306 | 11.7745 | 11.7143 | 11.6388 | 11.552 | 11.4714 | 11.3663 | 11.2592 | 11.1459 | 10.6316 | 10.4755 | 9.7041 | 12.4204 | 12.3888 | 12.3622 | 12.3276 | 12.2867 | 12.2418 | 12.1939 | 12.1194 | 12.0469 | 11.9704 | 11.6102 | 11.823 | 11.6934 | 12.1709 | 12.1158 | 12.0617 | 12.0026 | 11.9281 | 11.8434 | 11.7689 | 11.6668 | 11.5628 | 11.4515
|  | BRUCHAG | CF |  |  |  |  | 11.8939 | 11.852 | 11.8122 | 11.7571 | 11.7031 | 11.6418 | 11.5745 | 11.5194 | 11.449 | 11.3847 | 11.0102 | 10.649 | 9.7051 | 12.4255 | 12.4 | 12.3796 | 12.35 | 12.3153 | 12.2816 | 12.2408 | 12.2051 | 12.1612 | 12.1092 | 11.7959 | 11.8015 | 11.4393 | 12.1791 | 12.1403 | 12.1015 | 12.0515 | 11.9985 | 11.9413 | 11.876 | 11.823 | 11.7546 | 11.6893
| KEITH 1 | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 3.567 | 11.4203 | 10.7662 | 9.9009 | 8.7611 | 7.9448 | 6.2019 | 4.8703 | 3.7754 | 2.4907 | 1.1743 | -4.1318 | -9.4736 | -13.5252 | 12.9237 | 12.5135 | 11.8727 | 10.9717 | 10.5125 | 8.9697 | 8.1299 | 7.4452 | 6.7309 | 5.637 | 0.65231 | -3.7467 | -8.4701 | 12.5962 | 12.0115 | 11.1911 | 10.0513 | 9.3411 | 7.4982 | 6.2921 | 5.3523 | 4.2288 | 3.0472
|  | BUCKIE | EE |  |  |  |  | 11.4203 | 10.7662 | 10.0417 | 9.2305 | 8.1478 | 7.0601 | 5.7366 | 4.5988 | 3.208 | 1.9356 | -3.3501 | -8.2787 | -10.6528 | 12.9237 | 12.5135 | 12.0748 | 11.585 | 10.7952 | 9.8972 | 9.0554 | 8.3829 | 7.4135 | 6.5941 | 3.136 | -0.99667 | -3.3416 | 12.5962 | 12.0115 | 11.3656 | 10.6319 | 9.5768 | 8.5115 | 7.287 | 6.2584 | 4.9237 | 3.7513
|  | BUCKIE | HT |  |  |  |  | 11.5141 | 10.8611 | 9.9009 | 8.7611 | 7.9448 | 6.2019 | 4.8703 | 3.7754 | 2.4907 | 1.1743 | -4.1318 | -9.4736 | -13.4712 | 12.9941 | 12.6023 | 11.8727 | 10.9717 | 10.5125 | 8.9697 | 8.1299 | 7.4452 | 6.7309 | 5.9513 | 2.6758 | -1.6661 | -5.3467 | 12.7125 | 12.1329 | 11.1911 | 10.0513 | 9.3411 | 7.4982 | 6.2921 | 5.3523 | 4.2288 | 3.0472
|  | BUCKIE | HE |  |  |  |  | 11.5254 | 11.0284 | 10.2784 | 9.3356 | 8.5652 | 6.9723 | 5.8203 | 4.6488 | 3.7427 | 2.3458 | -3.8063 | -8.9308 | -13.5252 | 13.0003 | 12.6574 | 12.036 | 11.2339 | 10.6686 | 9.1758 | 8.3564 | 7.4829 | 6.8105 | 5.637 | 0.65231 | -3.7467 | -8.4701 | 12.7207 | 12.2717 | 11.5278 | 10.5727 | 9.8452 | 8.139 | 7.0462 | 5.9125 | 5.0972 | 3.6819
|  | BUCKIE | CF |  |  |  |  | 11.6274 | 11.2407 | 10.7886 | 10.3315 | 9.6876 | 8.9039 | 8.2366 | 7.6192 | 7.0662 | 6.6662 | 3.2948 | 0.1621 | -3.0599 | 13.0605 | 12.7737 | 12.4472 | 12.1248 | 11.5992 | 10.9166 | 10.3635 | 9.8921 | 9.4697 | 9.1156 | 6.5482 | 4.3268 | 1.3972 | 12.8094 | 12.4635 | 12.0584 | 11.6533 | 11.0258 | 10.2401 | 9.5962 | 9.0064 | 8.4758 | 8.1299
| FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 0 | 2.1457 | 2.1304 | 2.112 | 2.0865 | 2.0722 | 2.0447 | 2.0141 | 1.9886 | 1.9559 | 1.9284 | 1.8855 | 1.8682 | 1.6831 | 2.0208 | 2.0106 | 1.9963 | 1.98 | 1.9688 | 1.9504 | 1.9269 | 1.9127 | 1.8871 | 1.8667 | 1.8249 | 1.8384 | 1.671 | 2.0863 | 2.072 | 2.0537 | 2.0282 | 2.0159 | 1.9873 | 1.9557 | 1.9322 | 1.8996 | 1.87
|  | BUNOICH | EE |  |  |  |  | 2.1457 | 2.1304 | 2.112 | 2.0865 | 2.0722 | 2.0447 | 2.0141 | 1.9886 | 1.9559 | 1.9284 | 1.8855 | 1.8773 | 1.6933 | 2.0208 | 2.0106 | 1.9963 | 1.98 | 1.9688 | 1.9504 | 1.9269 | 1.9127 | 1.8871 | 1.8667 | 1.8249 | 1.868 | 1.7945 | 2.0863 | 2.072 | 2.0537 | 2.0282 | 2.0159 | 1.9873 | 1.9557 | 1.9322 | 1.8996 | 1.87
|  | BUNOICH | HT |  |  |  |  | 2.1569 | 2.1406 | 2.1243 | 2.1069 | 2.0927 | 2.0702 | 2.0447 | 2.0314 | 2.008 | 1.9896 | 1.8855 | 1.8682 | 1.6831 | 2.0269 | 2.0188 | 2.0096 | 1.9984 | 1.9902 | 1.9769 | 1.9606 | 1.9545 | 1.9382 | 1.928 | 1.8484 | 1.9353 | 1.9333 | 2.0986 | 2.0822 | 2.07 | 2.0506 | 2.0363 | 2.0149 | 1.9894 | 1.9792 | 1.9547 | 1.9394
|  | BUNOICH | HE |  |  |  |  | 2.1569 | 2.1437 | 2.1335 | 2.1192 | 2.108 | 2.0906 | 2.0671 | 2.0549 | 2.0345 | 2.01 | 1.9008 | 1.8947 | 1.7116 | 2.0269 | 2.0188 | 2.0116 | 2.0004 | 1.9922 | 1.981 | 1.9627 | 1.9555 | 1.9371 | 1.9198 | 1.8331 | 1.8833 | 1.8098 | 2.0986 | 2.0853 | 2.0761 | 2.0598 | 2.0506 | 2.0322 | 2.0078 | 1.9996 | 1.9761 | 1.9537
|  | BUNOICH | CF |  |  |  |  | 2.1518 | 2.1478 | 2.1376 | 2.1263 | 2.1141 | 2.1059 | 2.0906 | 2.0733 | 2.0682 | 2.0518 | 1.9794 | 1.9284 | 1.7178 | 2.0229 | 2.0188 | 2.0127 | 2.0035 | 1.9943 | 1.9892 | 1.9759 | 1.9576 | 1.9535 | 1.9412 | 1.8586 | 1.8384 | 1.671 | 2.0924 | 2.0884 | 2.0802 | 2.068 | 2.0547 | 2.0476 | 2.0322 | 2.0139 | 2.0098 | 1.9945
| THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | NO | 0 | -0.72551 | -0.76122 | -0.80918 | -0.84796 | -0.90306 | -0.95714 | -1.0276 | -1.0878 | -1.1571 | -1.2235 | -1.3918 | -1.4469 | -1.4724 | 0.44796 | 0.41735 | 0.37959 | 0.34898 | 0.29694 | 0.24694 | 0.18265 | 0.14082 | 0.07449 | 0.015306 | -0.11327 | -0.15918 | -0.27755 | -0.31429 | -0.3551 | -0.40408 | -0.44898 | -0.51327 | -0.57245 | -0.6551 | -0.71327 | -0.7949 | -0.86837
|  | BURGARHILL | EE |  |  |  |  | -0.72551 | -0.76122 | -0.80918 | -0.84796 | -0.90306 | -0.95714 | -1.0276 | -1.0878 | -1.1571 | -1.2235 | -1.3918 | -1.4235 | -1.4357 | 0.44796 | 0.41735 | 0.37959 | 0.34898 | 0.29694 | 0.24694 | 0.18265 | 0.14082 | 0.07449 | 0.015306 | -0.11327 | -0.15918 | -0.22041 | -0.31429 | -0.3551 | -0.40408 | -0.44898 | -0.51327 | -0.57245 | -0.6551 | -0.71327 | -0.7949 | -0.86837
|  | BURGARHILL | HT |  |  |  |  | -0.70612 | -0.74082 | -0.77551 | -0.81531 | -0.86224 | -0.89796 | -0.95102 | -1.0061 | -1.0653 | -1.1214 | -1.3388 | -1.4469 | -1.4724 | 0.47653 | 0.44694 | 0.42551 | 0.39796 | 0.35816 | 0.33571 | 0.29082 | 0.24592 | 0.19286 | 0.13878 | -0.052041 | -0.12551 | -0.14184 | -0.29796 | -0.33061 | -0.3602 | -0.40102 | -0.45306 | -0.4898 | -0.55 | -0.61224 | -0.67653 | -0.74592
|  | BURGARHILL | HE |  |  |  |  | -0.70714 | -0.73265 | -0.75918 | -0.78673 | -0.82245 | -0.85306 | -0.9 | -0.94694 | -1 | -1.0541 | -1.3214 | -1.3969 | -1.4173 | 0.47551 | 0.45102 | 0.42959 | 0.4051 | 0.36939 | 0.34898 | 0.30612 | 0.2602 | 0.21224 | 0.15918 | -0.053061 | -0.13061 | -0.1898 | -0.29898 | -0.32551 | -0.35306 | -0.38061 | -0.41939 | -0.45102 | -0.50306 | -0.55816 | -0.61837 | -0.68061
|  | BURGARHILL | CF |  |  |  |  | -0.7 | -0.72347 | -0.74694 | -0.77551 | -0.8 | -0.83163 | -0.85408 | -0.89286 | -0.92245 | -0.95918 | -1.1286 | -1.2908 | -1.3878 | 0.48163 | 0.46122 | 0.44286 | 0.41633 | 0.39388 | 0.36429 | 0.35 | 0.30918 | 0.28163 | 0.2449 | 0.069388 | -0.13367 | -0.27755 | -0.29184 | -0.30816 | -0.32857 | -0.3602 | -0.38571 | -0.42347 | -0.44286 | -0.48878 | -0.52143 | -0.56429
| ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 2.258 | 6.1469 | 5.9642 | 5.7244 | 5.5081 | 5.2346 | 4.9907 | 4.652 | 4.2877 | 3.9469 | 3.6458 | 2.9611 | 2.7132 | 1.8367 | 6.9275 | 6.8285 | 6.6775 | 6.5509 | 6.3754 | 6.2346 | 6.0203 | 5.7785 | 5.552 | 5.354 | 4.8877 | 4.9606 | 4.3831 | 6.4872 | 6.3239 | 6.1045 | 5.9106 | 5.6627 | 5.4382 | 5.129 | 4.7963 | 4.4861 | 4.2086
|  | BURGHEAD | EE |  |  |  |  | 6.1469 | 5.9642 | 5.7244 | 5.5081 | 5.2346 | 4.9907 | 4.652 | 4.2877 | 3.9469 | 3.6458 | 3.1489 | 2.9948 | 2.1989 | 6.9275 | 6.8285 | 6.6775 | 6.5509 | 6.3754 | 6.2346 | 6.0203 | 5.7785 | 5.552 | 5.354 | 5.0173 | 5.2923 | 4.978 | 6.4872 | 6.3239 | 6.1045 | 5.9106 | 5.6627 | 5.4382 | 5.129 | 4.7963 | 4.4861 | 4.2086
|  | BURGHEAD | HT |  |  |  |  | 6.2285 | 6.053 | 5.8662 | 5.6499 | 5.4122 | 5.203 | 4.9438 | 4.6509 | 4.4213 | 4.1346 | 2.9611 | 2.8846 | 2.006 | 6.9999 | 6.9091 | 6.8111 | 6.6938 | 6.5591 | 6.4458 | 6.2948 | 6.1132 | 5.9591 | 5.7805 | 5.0111 | 5.2014 | 5.1055 | 6.5606 | 6.4045 | 6.2331 | 6.0412 | 5.8239 | 5.6341 | 5.3984 | 5.13 | 4.9178 | 4.6555
|  | BURGHEAD | HE |  |  |  |  | 6.2244 | 6.0836 | 5.9356 | 5.7632 | 5.5611 | 5.3887 | 5.1397 | 4.8622 | 4.654 | 4.3958 | 3.1295 | 2.7132 | 1.8367 | 6.9958 | 6.9101 | 6.8183 | 6.7091 | 6.5836 | 6.454 | 6.2897 | 6.0918 | 5.9203 | 5.7305 | 4.8877 | 4.9606 | 4.8474 | 6.5566 | 6.43 | 6.2943 | 6.1423 | 5.9596 | 5.8025 | 5.577 | 5.3249 | 5.1321 | 4.8933
|  | BURGHEAD | CF |  |  |  |  | 6.2479 | 6.1336 | 6.0193 | 5.8805 | 5.7336 | 5.5673 | 5.4397 | 5.2479 | 5.0795 | 4.9479 | 3.904 | 3.3499 | 1.9591 | 7.0122 | 6.9397 | 6.8713 | 6.7867 | 6.6877 | 6.5764 | 6.4969 | 6.3601 | 6.2346 | 6.1448 | 5.3632 | 5.2892 | 4.3831 | 6.58 | 6.4759 | 6.3729 | 6.2484 | 6.1127 | 5.9627 | 5.8494 | 5.68 | 5.5219 | 5.3984
| BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 13.56 | -7.9913 | -8.9331 | -10.6239 | -12.9209 | -15.4658 | -18.3137 | -21.6484 | -25.6076 | -29.1311 | -32.7709 | -47.2382 | -54.5209 | -57.2316 | -5.504 | -6.5836 | -7.9397 | -9.5418 | -11.4653 | -13.605 | -16.1142 | -19.1326 | -21.804 | -24.5714 | -35.4387 | -40.6068 | -42.115 | -6.4528 | -7.7946 | -9.6834 | -11.8956 | -14.3456 | -17.0813 | -20.2854 | -24.0977 | -27.4915 | -30.9783
|  | BURGHMUIR | EE |  |  |  |  | -7.9913 | -8.9331 | -10.6239 | -12.9209 | -15.4658 | -18.3137 | -21.6484 | -25.6076 | -29.1311 | -32.7709 | -47.2382 | -54.5209 | -57.2316 | -5.504 | -6.5836 | -7.9397 | -9.5418 | -11.4653 | -13.605 | -16.1142 | -19.1326 | -21.804 | -24.5714 | -35.4387 | -40.6068 | -42.115 | -6.4528 | -7.7946 | -9.6834 | -11.8956 | -14.3456 | -17.0813 | -20.2854 | -24.0977 | -27.4915 | -30.9783
|  | BURGHMUIR | HT |  |  |  |  | -7.5974 | -8.376 | -9.2535 | -10.2831 | -12.026 | -14.079 | -16.6831 | -19.6872 | -22.676 | -25.9974 | -39.1392 | -46.478 | -49.7336 | -5.0255 | -5.7408 | -6.6489 | -7.6612 | -8.8459 | -10.3224 | -12.2979 | -14.5908 | -16.8418 | -19.3663 | -29.154 | -34.3099 | -36.2119 | -6.0528 | -6.7966 | -7.9211 | -9.3374 | -11.0079 | -12.9813 | -15.4813 | -18.3691 | -21.2385 | -24.4007
|  | BURGHMUIR | HE |  |  |  |  | -7.6433 | -8.4005 | -9.3545 | -11.1035 | -13.1556 | -15.6852 | -18.827 | -22.5464 | -26.2505 | -29.8474 | -46.3239 | -51.5994 | -52.7867 | -5.0704 | -6.0571 | -7.0795 | -8.305 | -9.7612 | -11.6714 | -14.0499 | -16.8928 | -19.7102 | -22.455 | -34.9193 | -38.4446 | -38.7895 | -6.0987 | -7.0619 | -8.463 | -10.1466 | -12.1252 | -14.5548 | -17.5762 | -21.1558 | -24.7191 | -28.166
|  | BURGHMUIR | CF |  |  |  |  | -7.2698 | -7.6382 | -8.0658 | -8.5668 | -9.3352 | -10.5698 | -12.0147 | -13.9158 | -15.728 | -17.5341 | -28.928 | -39.2994 | -45.7285 | -4.804 | -5.102 | -5.6581 | -6.3224 | -7.0846 | -7.955 | -8.9857 | -10.3979 | -11.7948 | -13.1857 | -21.8806 | -29.315 | -33.4732 | -5.7477 | -6.1028 | -6.516 | -7.415 | -8.4487 | -9.6415 | -11.0344 | -12.8701 | -14.617 | -16.3487
| CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0 | 0.11086 | 0.10984 | 0.10984 | 0.10882 | 0.10678 | 0.10678 | 0.10576 | 0.097592 | 0.096571 | 0.096571 | 0.090449 | 0.089429 | 0.080429 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10288 | 0.10186 | 0.093694 | 0.092673 | 0.092673 | 0.088592 | 0.092071 | 0.091051 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10534 | 0.10534 | 0.10432 | 0.095133 | 0.095133 | 0.094112
|  | BUTTERBRIDGE | EE |  |  |  |  | 0.11086 | 0.10984 | 0.10984 | 0.10882 | 0.10678 | 0.10678 | 0.10576 | 0.097592 | 0.096571 | 0.096571 | 0.090449 | 0.089429 | 0.080429 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10288 | 0.10186 | 0.093694 | 0.092673 | 0.092673 | 0.088592 | 0.092071 | 0.092071 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10534 | 0.10534 | 0.10432 | 0.095133 | 0.095133 | 0.094112
|  | BUTTERBRIDGE | HT |  |  |  |  | 0.11086 | 0.11086 | 0.10984 | 0.10984 | 0.10882 | 0.10882 | 0.10576 | 0.10576 | 0.10473 | 0.096571 | 0.09249 | 0.089429 | 0.080429 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10186 | 0.10186 | 0.10084 | 0.092673 | 0.089612 | 0.092071 | 0.092071 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10636 | 0.10432 | 0.10432 | 0.1033 | 0.094112
|  | BUTTERBRIDGE | HE |  |  |  |  | 0.11086 | 0.11086 | 0.10984 | 0.10984 | 0.10882 | 0.10678 | 0.10678 | 0.10576 | 0.10473 | 0.096571 | 0.091469 | 0.089429 | 0.080429 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10288 | 0.10186 | 0.10084 | 0.092673 | 0.088592 | 0.092071 | 0.092071 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10534 | 0.10534 | 0.10432 | 0.10228 | 0.095133
|  | BUTTERBRIDGE | CF |  |  |  |  | 0.11086 | 0.11086 | 0.11086 | 0.10984 | 0.10984 | 0.10984 | 0.10882 | 0.10882 | 0.10678 | 0.10678 | 0.095551 | 0.091469 | 0.080429 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10288 | 0.10288 | 0.091653 | 0.094112 | 0.091051 | 0.1084 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10738 | 0.10636 | 0.10636 | 0.10534 | 0.10534
| BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 0.581 | 2.2365 | 2.1008 | 1.9447 | 1.762 | 1.561 | 1.3437 | 1.0376 | 0.65898 | 0.27837 | -0.073673 | -1.4533 | -2.4114 | -3.14 | 3.3845 | 3.3212 | 3.2467 | 3.1376 | 2.9957 | 2.8355 | 2.6376 | 2.3876 | 2.1447 | 1.9263 | 1.0835 | 0.75286 | 0.3049 | 2.9059 | 2.7855 | 2.6406 | 2.461 | 2.2651 | 2.061 | 1.7712 | 1.4141 | 1.0763 | 0.75388
|  | CALLANDER | EE |  |  |  |  | 2.2365 | 2.1008 | 1.9447 | 1.762 | 1.561 | 1.3437 | 1.0376 | 0.65898 | 0.27837 | -0.073673 | -1.3982 | -2.2369 | -2.9522 | 3.3845 | 3.3212 | 3.2467 | 3.1376 | 2.9957 | 2.8355 | 2.6376 | 2.3876 | 2.1447 | 1.9263 | 1.0835 | 0.75286 | 0.3049 | 2.9059 | 2.7855 | 2.6406 | 2.461 | 2.2651 | 2.061 | 1.7712 | 1.4141 | 1.0763 | 0.75388
|  | CALLANDER | HT |  |  |  |  | 2.2559 | 2.1202 | 1.9824 | 1.7855 | 1.5814 | 1.3641 | 1.0794 | 0.74878 | 0.4202 | 0.11408 | -1.4533 | -2.4114 | -3.14 | 3.3957 | 3.3437 | 3.2835 | 3.1763 | 3.0569 | 2.9273 | 2.7733 | 2.5743 | 2.3824 | 2.1978 | 1.2396 | 0.93551 | 0.7549 | 2.9273 | 2.8243 | 2.6998 | 2.4998 | 2.31 | 2.1131 | 1.86 | 1.5488 | 1.2324 | 0.94061
|  | CALLANDER | HE |  |  |  |  | 2.2661 | 2.1763 | 2.0886 | 1.9539 | 1.8161 | 1.6794 | 1.4896 | 1.2539 | 1.012 | 0.79163 | -0.62878 | -1.5012 | -2.3206 | 3.4059 | 3.3539 | 3.3029 | 3.2141 | 3.1253 | 3.0171 | 2.8712 | 2.6845 | 2.5018 | 2.3304 | 1.4284 | 1.1141 | 0.64469 | 2.9355 | 2.8488 | 2.7508 | 2.608 | 2.4529 | 2.2865 | 2.0947 | 1.8539 | 1.6161 | 1.3804
|  | CALLANDER | CF |  |  |  |  | 2.309 | 2.2508 | 2.1865 | 2.11 | 2.0222 | 1.9294 | 1.8304 | 1.7273 | 1.6161 | 1.4998 | 0.59469 | -0.46653 | -1.6451 | 3.4437 | 3.411 | 3.3722 | 3.3222 | 3.2661 | 3.2018 | 3.1365 | 3.059 | 2.9631 | 2.8396 | 2.112 | 1.3539 | 0.32837 | 2.9763 | 2.9324 | 2.8763 | 2.7978 | 2.7049 | 2.608 | 2.4998 | 2.3743 | 2.2488 | 2.1059
| STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 0.295 | -0.35102 | -0.46939 | -0.58265 | -0.65102 | -0.73571 | -0.82551 | -0.91327 | -1.0347 | -1.15 | -1.2551 | -1.4724 | -1.5347 | -1.5582 | 0.57653 | 0.49388 | 0.41429 | 0.37041 | 0.3102 | 0.24694 | 0.19592 | 0.10714 | 0.022449 | -0.045918 | -0.19082 | -0.29592 | -0.60204 | -0.11939 | -0.22959 | -0.33571 | -0.39898 | -0.47857 | -0.56531 | -0.64286 | -0.75714 | -0.86633 | -0.96327
|  | CALLANISH | EE |  |  |  |  | -0.35102 | -0.42143 | -0.58265 | -0.65102 | -0.73571 | -0.82551 | -0.91327 | -1.0347 | -1.15 | -1.2551 | -1.4724 | -1.5112 | -1.5224 | 0.57653 | 0.53367 | 0.41429 | 0.37041 | 0.3102 | 0.24694 | 0.19592 | 0.10714 | 0.022449 | -0.045918 | -0.19082 | -0.27143 | -0.40204 | -0.11939 | -0.18469 | -0.33571 | -0.39898 | -0.47857 | -0.56531 | -0.64286 | -0.75714 | -0.86633 | -0.96327
|  | CALLANISH | HT |  |  |  |  | -0.32857 | -0.46939 | -0.52857 | -0.59184 | -0.66531 | -0.72245 | -0.80408 | -0.89796 | -0.98878 | -1.0551 | -1.4133 | -1.5347 | -1.5582 | 0.5949 | 0.49388 | 0.46224 | 0.43163 | 0.38878 | 0.3551 | 0.30714 | 0.24286 | 0.18265 | 0.15 | -0.10816 | -0.16122 | -0.17449 | -0.097959 | -0.22959 | -0.28367 | -0.34184 | -0.40714 | -0.46327 | -0.53776 | -0.62551 | -0.70918 | -0.76939
|  | CALLANISH | HE |  |  |  |  | -0.32857 | -0.37755 | -0.49694 | -0.54388 | -0.6 | -0.64286 | -0.71224 | -0.79388 | -0.87551 | -0.92857 | -1.3837 | -1.4918 | -1.5092 | 0.5949 | 0.56429 | 0.47347 | 0.44388 | 0.40612 | 0.37959 | 0.33265 | 0.27143 | 0.21224 | 0.18265 | -0.13571 | -0.2602 | -0.38776 | -0.097959 | -0.14286 | -0.25408 | -0.29898 | -0.35102 | -0.3898 | -0.45612 | -0.53367 | -0.60612 | -0.65816
|  | CALLANISH | CF |  |  |  |  | -0.32245 | -0.36327 | -0.40102 | -0.51429 | -0.56224 | -0.61429 | -0.64796 | -0.70612 | -0.75408 | -0.81122 | -1.0735 | -1.3276 | -1.4776 | 0.60102 | 0.57755 | 0.55204 | 0.46224 | 0.43163 | 0.39592 | 0.37347 | 0.32551 | 0.28673 | 0.24184 | 0.012245 | -0.29592 | -0.60204 | -0.091837 | -0.12857 | -0.16429 | -0.27041 | -0.31429 | -0.36224 | -0.39388 | -0.44898 | -0.49388 | -0.54796
| TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | 0.587 | -0.5051 | -0.52449 | -0.54592 | -0.57041 | -0.5949 | -0.61939 | -0.65204 | -0.68469 | -0.71837 | -0.74898 | -0.83469 | -0.86122 | -0.88367 | -0.47041 | -0.47653 | -0.48673 | -0.4949 | -0.50714 | -0.51429 | -0.52857 | -0.54082 | -0.5551 | -0.56735 | -0.6102 | -0.63469 | -0.65306 | -0.46327 | -0.47959 | -0.50102 | -0.52143 | -0.5449 | -0.56633 | -0.5949 | -0.62755 | -0.66531 | -0.69694
|  | CALVINE | EE |  |  |  |  | -0.5051 | -0.52449 | -0.54592 | -0.57041 | -0.5949 | -0.61939 | -0.65204 | -0.68469 | -0.71837 | -0.74898 | -0.83469 | -0.8449 | -0.84694 | -0.47041 | -0.47653 | -0.48673 | -0.4949 | -0.50714 | -0.51429 | -0.52857 | -0.54082 | -0.5551 | -0.56735 | -0.6102 | -0.61939 | -0.63061 | -0.46327 | -0.47959 | -0.50102 | -0.52143 | -0.5449 | -0.56633 | -0.5949 | -0.62755 | -0.66531 | -0.69694
|  | CALVINE | HT |  |  |  |  | -0.49796 | -0.51224 | -0.52755 | -0.54592 | -0.56531 | -0.58367 | -0.60816 | -0.63163 | -0.65714 | -0.68469 | -0.7949 | -0.83776 | -0.85816 | -0.46531 | -0.47143 | -0.47653 | -0.48265 | -0.48878 | -0.49694 | -0.50714 | -0.51531 | -0.52755 | -0.53571 | -0.58469 | -0.61327 | -0.62857 | -0.4551 | -0.47041 | -0.48571 | -0.50204 | -0.51939 | -0.53469 | -0.55816 | -0.57857 | -0.60102 | -0.62755
|  | CALVINE | HE |  |  |  |  | -0.49796 | -0.51327 | -0.52653 | -0.54184 | -0.5602 | -0.57959 | -0.6051 | -0.62959 | -0.65612 | -0.68776 | -0.82143 | -0.86122 | -0.88367 | -0.46531 | -0.47143 | -0.47755 | -0.48163 | -0.49082 | -0.49796 | -0.50612 | -0.51837 | -0.52755 | -0.5398 | -0.60306 | -0.63469 | -0.65306 | -0.4551 | -0.47041 | -0.48061 | -0.49592 | -0.51327 | -0.53061 | -0.55306 | -0.57653 | -0.59898 | -0.62857
|  | CALVINE | CF |  |  |  |  | -0.49592 | -0.50204 | -0.5102 | -0.52245 | -0.53265 | -0.54694 | -0.55816 | -0.57653 | -0.59184 | -0.60714 | -0.70714 | -0.79592 | -0.85204 | -0.46633 | -0.46837 | -0.47245 | -0.47653 | -0.48163 | -0.48673 | -0.49388 | -0.5 | -0.50918 | -0.51429 | -0.55816 | -0.60714 | -0.64898 | -0.45714 | -0.46122 | -0.47347 | -0.48367 | -0.49388 | -0.50714 | -0.51531 | -0.53061 | -0.54592 | -0.55408
| CARRADALE 1 | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 0.486 | 8.398 | 8.2082 | 7.201 | 5.6745 | 5.4031 | 2.1316 | 1.2143 | 0.071429 | -1.1286 | -3.2235 | -11.898 | -19.7122 | -22.4469 | 9.2398 | 9.0888 | 7.9469 | 6.199 | 5.9337 | 2.1357 | 0.98469 | -0.21429 | -1.4969 | -3.9061 | -13.799 | -22.724 | -23.7658 | 9.2679 | 9.0403 | 7.8189 | 5.9893 | 5.7423 | 1.7679 | 0.62908 | -0.6801 | -2.0658 | -4.576
|  | CAMPBELTOWN | EE |  |  |  |  | 8.398 | 8.2082 | 7.9643 | 7.6704 | 6.5622 | 4.7194 | 3.6143 | 3.0449 | 1.5673 | 1.0316 | -3.3031 | -14.1643 | -19.2143 | 9.2398 | 9.0888 | 8.9398 | 8.7449 | 7.5643 | 5.4837 | 4.449 | 4.0816 | 2.5663 | 2.0939 | -2.2592 | -14.9689 | -20.5811 | 9.2679 | 9.0403 | 8.8107 | 8.5352 | 7.2587 | 5.0689 | 3.8648 | 3.3321 | 1.6587 | 1.0321
|  | CAMPBELTOWN | HT |  |  |  |  | 8.4867 | 8.3214 | 7.201 | 5.6745 | 5.4031 | 2.1316 | 1.4663 | 0.77653 | 0.25204 | -0.49796 | -5.5245 | -11.4969 | -22.4469 | 9.3153 | 9.2041 | 7.9469 | 6.199 | 6.0541 | 2.1918 | 1.6724 | 1.1265 | 0.79796 | 0.16531 | -4.8765 | -11.1526 | -23.7658 | 9.3403 | 9.1587 | 7.8189 | 5.9893 | 5.7423 | 1.7679 | 1.0852 | 0.37296 | -0.12092 | -0.91276
|  | CAMPBELTOWN | HE |  |  |  |  | 8.4867 | 8.3837 | 7.4847 | 6.1582 | 5.5122 | 2.3378 | 1.2143 | 0.071429 | -1.1286 | -3.2235 | -11.898 | -19.7122 | -20.899 | 9.3153 | 9.2204 | 8.1816 | 6.6204 | 5.9337 | 2.1357 | 0.98469 | -0.21429 | -1.4969 | -3.9061 | -13.799 | -22.724 | -23.427 | 9.3423 | 9.2158 | 8.1301 | 6.525 | 5.7801 | 1.9046 | 0.62908 | -0.6801 | -2.0658 | -4.576
|  | CAMPBELTOWN | CF |  |  |  |  | 8.5235 | 8.4561 | 8.3857 | 8.2786 | 7.65 | 6.5857 | 5.9255 | 5.3592 | 4.7939 | 4.1153 | 1.4857 | -0.8102 | -3.8551 | 9.3408 | 9.2724 | 9.2 | 9.1194 | 8.4082 | 7.151 | 6.4194 | 5.8388 | 5.2388 | 4.4796 | 1.7143 | -0.52092 | -3.5964 | 9.3811 | 9.2995 | 9.2128 | 9.1087 | 8.3668 | 7.0801 | 6.3158 | 5.6862 | 5.0495 | 4.2556
| COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | NO | 0.868 | 5.4612 | 5.3133 | 5.1296 | 4.9551 | 4.6939 | 4.4459 | 4.0878 | 3.6704 | 3.2265 | 2.8286 | 2.1031 | 1.7041 | 1.6122 | 7.8541 | 7.7806 | 7.6816 | 7.5867 | 7.4571 | 7.3092 | 7.0847 | 6.8092 | 6.5163 | 6.2602 | 5.9133 | 5.75 | 5.1959 | 6.7582 | 6.601 | 6.3969 | 6.2194 | 5.9837 | 5.7561 | 5.4276 | 5.049 | 4.6408 | 4.2765
|  | CAPUTH | EE |  |  |  |  | 5.4612 | 5.3133 | 5.1296 | 4.9551 | 4.6939 | 4.4459 | 4.0878 | 3.6704 | 3.2265 | 2.8286 | 2.1031 | 1.7765 | 1.6888 | 7.8541 | 7.7806 | 7.6816 | 7.5867 | 7.4571 | 7.3092 | 7.0847 | 6.8092 | 6.5163 | 6.2602 | 5.9133 | 5.75 | 5.4255 | 6.7582 | 6.601 | 6.3969 | 6.2194 | 5.9837 | 5.7561 | 5.4276 | 5.049 | 4.6408 | 4.2765
|  | CAPUTH | HT |  |  |  |  | 5.5173 | 5.3776 | 5.2398 | 5.0867 | 4.9061 | 4.7 | 4.3898 | 4.101 | 3.699 | 3.3235 | 2.2918 | 1.7041 | 1.6122 | 7.8918 | 7.8276 | 7.7602 | 7.6847 | 7.5918 | 7.4837 | 7.3265 | 7.1673 | 6.8918 | 6.6663 | 6.0827 | 5.8194 | 5.7367 | 6.8337 | 6.6827 | 6.5337 | 6.3653 | 6.1724 | 5.9878 | 5.7051 | 5.4367 | 5.0643 | 4.7224
|  | CAPUTH | HE |  |  |  |  | 5.5133 | 5.4 | 5.2939 | 5.1714 | 5.0276 | 4.8755 | 4.6592 | 4.3939 | 4.1153 | 3.8031 | 2.6418 | 2.2265 | 2.0531 | 7.8898 | 7.8296 | 7.7684 | 7.699 | 7.6153 | 7.5235 | 7.3918 | 7.2235 | 7.0092 | 6.7939 | 6.051 | 5.8194 | 5.6459 | 6.8327 | 6.7214 | 6.6173 | 6.4929 | 6.3408 | 6.202 | 5.9776 | 5.7153 | 5.4582 | 5.1694
|  | CAPUTH | CF |  |  |  |  | 5.5459 | 5.4776 | 5.4051 | 5.3224 | 5.2265 | 5.1245 | 4.9714 | 4.7898 | 4.599 | 4.4449 | 3.4194 | 2.9031 | 2.3286 | 7.9102 | 7.8755 | 7.8327 | 7.7898 | 7.7357 | 7.6796 | 7.6092 | 7.4765 | 7.3367 | 7.2296 | 6.4306 | 6.002 | 5.1959 | 6.8582 | 6.7755 | 6.6939 | 6.5969 | 6.4816 | 6.3786 | 6.2408 | 6.0786 | 5.9061 | 5.7633
| ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 1.399 | 5.701 | 5.0755 | 4.4173 | 3.7582 | 3.0439 | 2.4755 | 1.7602 | 1.0398 | 0.52551 | -0.13061 | -3.0827 | -4.8714 | -5.9235 | 7.5796 | 7.199 | 6.798 | 6.3429 | 5.8388 | 5.6286 | 5.2745 | 4.8857 | 4.4776 | 4.1133 | 2.7694 | 2.074 | 1.1821 | 6.6199 | 6.0587 | 5.4536 | 4.8485 | 4.2117 | 3.6821 | 3.0383 | 2.3811 | 1.925 | 1.327
|  | CARNOUSTIE | EE |  |  |  |  | 5.701 | 5.0796 | 4.4255 | 3.7582 | 3.0439 | 2.7173 | 1.9765 | 1.2316 | 0.52551 | -0.13061 | -2.8684 | -4.7439 | -5.8867 | 7.5796 | 7.199 | 6.798 | 6.3429 | 5.8388 | 5.7337 | 5.3122 | 4.8857 | 4.4776 | 4.1133 | 2.7694 | 2.074 | 1.1821 | 6.6199 | 6.0607 | 5.4821 | 4.8689 | 4.2117 | 3.9158 | 3.2362 | 2.5638 | 1.925 | 1.327
|  | CARNOUSTIE | HT |  |  |  |  | 5.7112 | 5.0755 | 4.4173 | 3.7612 | 3.0745 | 2.4755 | 1.7602 | 1.0398 | 0.64286 | -0.0091837 | -3.0827 | -4.8714 | -5.9235 | 7.6255 | 7.252 | 6.849 | 6.4255 | 5.9898 | 5.6286 | 5.2745 | 4.902 | 4.8357 | 4.5276 | 3.1122 | 2.7413 | 2.6179 | 6.625 | 6.0587 | 5.4536 | 4.8485 | 4.2301 | 3.6821 | 3.0383 | 2.3811 | 2.0587 | 1.4689
|  | CARNOUSTIE | HE |  |  |  |  | 5.8265 | 5.3398 | 4.8541 | 4.3816 | 3.9092 | 3.4663 | 2.9459 | 2.4276 | 2.3071 | 1.8765 | -0.61735 | -2.5102 | -4.0786 | 7.7031 | 7.3827 | 7.0541 | 6.7112 | 6.3694 | 6.0531 | 5.7143 | 5.3551 | 5.3888 | 5.1388 | 3.702 | 2.9403 | 1.924 | 6.726 | 6.2995 | 5.8658 | 5.426 | 4.9903 | 4.5811 | 4.1056 | 3.6352 | 3.5301 | 3.1423
|  | CARNOUSTIE | CF |  |  |  |  | 6.0449 | 5.7816 | 5.452 | 5.1939 | 4.8714 | 4.5908 | 4.3031 | 3.9929 | 3.7306 | 3.4571 | 2.1786 | 0.18163 | -2.1214 | 7.852 | 7.6643 | 7.4184 | 7.2255 | 6.9663 | 6.7551 | 6.5061 | 6.2296 | 5.9908 | 5.7367 | 4.8316 | 3.3883 | 1.2219 | 6.9281 | 6.7005 | 6.4087 | 6.1719 | 5.8791 | 5.626 | 5.3668 | 5.0862 | 4.8413 | 4.5811
| KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 0.02 | 0.62449 | 0.62347 | 0.62245 | 0.61735 | 0.61224 | 0.61122 | 0.60204 | 0.59592 | 0.58571 | 0.58469 | 0.54898 | 0.52755 | 0.52041 | 0.75 | 0.75306 | 0.74286 | 0.74796 | 0.7449 | 0.74184 | 0.73367 | 0.72653 | 0.71633 | 0.71122 | 0.67041 | 0.65714 | 0.65102 | 0.66429 | 0.66531 | 0.65816 | 0.65306 | 0.65 | 0.64592 | 0.63673 | 0.62755 | 0.61633 | 0.60918
|  | CASHLIE | EE |  |  |  |  | 0.62449 | 0.62347 | 0.62347 | 0.61735 | 0.61224 | 0.61122 | 0.60204 | 0.59592 | 0.58571 | 0.58469 | 0.57041 | 0.56735 | 0.56633 | 0.75 | 0.75306 | 0.75306 | 0.74796 | 0.7449 | 0.74184 | 0.73367 | 0.72653 | 0.71633 | 0.71429 | 0.69388 | 0.6898 | 0.67959 | 0.66429 | 0.66531 | 0.65918 | 0.65306 | 0.65 | 0.64592 | 0.63673 | 0.62755 | 0.61633 | 0.60918
|  | CASHLIE | HT |  |  |  |  | 0.6398 | 0.63061 | 0.62245 | 0.62653 | 0.62245 | 0.61735 | 0.61735 | 0.60918 | 0.6051 | 0.59898 | 0.57959 | 0.57143 | 0.56837 | 0.76531 | 0.75714 | 0.74796 | 0.75714 | 0.75102 | 0.74796 | 0.74694 | 0.73673 | 0.73469 | 0.72857 | 0.70612 | 0.69796 | 0.69592 | 0.68061 | 0.66837 | 0.6602 | 0.66429 | 0.65816 | 0.6551 | 0.65306 | 0.64388 | 0.63878 | 0.63265
|  | CASHLIE | HE |  |  |  |  | 0.6398 | 0.63163 | 0.62347 | 0.62653 | 0.62245 | 0.61939 | 0.61735 | 0.60918 | 0.60816 | 0.60102 | 0.54898 | 0.52755 | 0.52449 | 0.76429 | 0.75306 | 0.74286 | 0.75612 | 0.75 | 0.74388 | 0.73776 | 0.72755 | 0.71939 | 0.71122 | 0.67041 | 0.65714 | 0.65612 | 0.67959 | 0.66837 | 0.65816 | 0.66633 | 0.65918 | 0.65306 | 0.6449 | 0.63163 | 0.62041 | 0.6102
|  | CASHLIE | CF |  |  |  |  | 0.6398 | 0.63163 | 0.62347 | 0.62347 | 0.62857 | 0.62347 | 0.62143 | 0.62041 | 0.61633 | 0.61122 | 0.5898 | 0.54796 | 0.52041 | 0.76531 | 0.75714 | 0.74592 | 0.75306 | 0.75714 | 0.75306 | 0.75 | 0.7449 | 0.73878 | 0.73265 | 0.7 | 0.67143 | 0.65102 | 0.67959 | 0.67041 | 0.6602 | 0.66531 | 0.66633 | 0.66122 | 0.65714 | 0.65306 | 0.64592 | 0.63878
| KILLIN | CHAORACH | MINIMUM HEADROOM | NN 45400 27553 | YES | YES | 0.023 | 0.5602 | 0.55918 | 0.55102 | 0.54388 | 0.54082 | 0.5398 | 0.53776 | 0.53265 | 0.53265 | 0.52755 | 0.52041 | 0.5102 | 0.5051 | 0.76735 | 0.76633 | 0.75918 | 0.75102 | 0.75 | 0.75612 | 0.74796 | 0.75 | 0.75 | 0.75 | 0.74592 | 0.73878 | 0.73061 | 0.65816 | 0.65612 | 0.64796 | 0.6398 | 0.63878 | 0.63776 | 0.63571 | 0.63163 | 0.63163 | 0.62653
|  | CHAORACH | EE |  |  |  |  | 0.5602 | 0.55918 | 0.55102 | 0.54388 | 0.54082 | 0.5398 | 0.54286 | 0.53878 | 0.53265 | 0.52755 | 0.52041 | 0.51429 | 0.50714 | 0.76735 | 0.76633 | 0.75918 | 0.75102 | 0.75 | 0.75714 | 0.75918 | 0.7551 | 0.75204 | 0.75 | 0.74694 | 0.73878 | 0.73061 | 0.65816 | 0.65612 | 0.64796 | 0.6398 | 0.63878 | 0.63776 | 0.6398 | 0.63776 | 0.63163 | 0.62653
|  | CHAORACH | HT |  |  |  |  | 0.56735 | 0.55918 | 0.55918 | 0.55816 | 0.54898 | 0.54796 | 0.53776 | 0.53265 | 0.53776 | 0.53061 | 0.52041 | 0.5102 | 0.5051 | 0.77449 | 0.76735 | 0.76633 | 0.76633 | 0.75714 | 0.75612 | 0.74796 | 0.7551 | 0.75714 | 0.75306 | 0.74592 | 0.73878 | 0.73571 | 0.66531 | 0.65714 | 0.65612 | 0.6551 | 0.64592 | 0.6449 | 0.63571 | 0.63163 | 0.63571 | 0.63061
|  | CHAORACH | HE |  |  |  |  | 0.56735 | 0.55918 | 0.55918 | 0.55918 | 0.55 | 0.54796 | 0.53776 | 0.53571 | 0.54082 | 0.53878 | 0.52041 | 0.51633 | 0.51122 | 0.77449 | 0.76735 | 0.76633 | 0.76633 | 0.75816 | 0.75714 | 0.74898 | 0.7551 | 0.75816 | 0.75714 | 0.74592 | 0.7398 | 0.73367 | 0.66531 | 0.65714 | 0.65612 | 0.65612 | 0.64694 | 0.64592 | 0.63673 | 0.63571 | 0.63878 | 0.63673
|  | CHAORACH | CF |  |  |  |  | 0.56735 | 0.56735 | 0.5602 | 0.55918 | 0.55918 | 0.55204 | 0.55102 | 0.54286 | 0.54082 | 0.53776 | 0.53265 | 0.51837 | 0.51531 | 0.77449 | 0.77449 | 0.76735 | 0.76633 | 0.76633 | 0.75918 | 0.75816 | 0.75 | 0.75 | 0.75612 | 0.75204 | 0.74184 | 0.73163 | 0.66531 | 0.66531 | 0.65816 | 0.65612 | 0.65612 | 0.64898 | 0.64796 | 0.64082 | 0.63776 | 0.63673
| ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 1.139 | 3.9433 | 3.6198 | 3.2392 | 2.8759 | 2.4596 | 2.0127 | 1.3525 | 0.37696 | -0.46794 | -1.0863 | -4.2537 | -6.171 | -6.4792 | 6.129 | 6.0157 | 5.8708 | 5.6586 | 5.4065 | 5.1361 | 4.8188 | 4.1933 | 3.6861 | 3.1953 | 1.3688 | 0.19124 | -1.3424 | 4.9484 | 4.6606 | 4.3198 | 3.9923 | 3.6178 | 3.2208 | 2.5647 | 1.6535 | 0.87185 | 0.33614
|  | CHARLES AVENUE | EE |  |  |  |  | 3.9433 | 3.6198 | 3.2392 | 2.8759 | 2.4596 | 2.0127 | 1.5341 | 0.56471 | -0.3006 | -1.0863 | -4.1547 | -5.97 | -6.3894 | 6.129 | 6.0157 | 5.8708 | 5.6586 | 5.4065 | 5.1361 | 4.878 | 4.2351 | 3.6861 | 3.1953 | 1.3688 | 0.19124 | -0.86386 | 4.9484 | 4.6606 | 4.3198 | 3.9923 | 3.6178 | 3.2208 | 2.7586 | 1.8596 | 1.0606 | 0.33614
|  | CHARLES AVENUE | HT |  |  |  |  | 4.0463 | 3.7382 | 3.3994 | 3.077 | 2.7065 | 2.3514 | 1.3525 | 0.37696 | -0.46794 | -0.94039 | -4.2537 | -6.171 | -6.4792 | 6.1902 | 6.0984 | 5.9974 | 5.8637 | 5.6698 | 5.4851 | 4.8188 | 4.1933 | 3.6923 | 3.481 | 1.829 | 0.94226 | 0.80349 | 5.0392 | 4.7606 | 4.4576 | 4.1678 | 3.8361 | 3.5137 | 2.5647 | 1.6535 | 0.87185 | 0.429
|  | CHARLES AVENUE | HE |  |  |  |  | 4.0443 | 3.8637 | 3.6586 | 3.4616 | 3.2249 | 3.0035 | 2.4841 | 1.73 | 1.0688 | 0.74634 | -2.2608 | -4.2128 | -4.9261 | 6.1821 | 6.1035 | 6.0188 | 5.931 | 5.8137 | 5.6616 | 5.3147 | 4.7637 | 4.2974 | 4.08 | 2.1361 | 0.79634 | -0.34345 | 5.0382 | 4.8739 | 4.6902 | 4.5178 | 4.3035 | 4.1014 | 3.6076 | 2.9014 | 2.2851 | 1.9729
|  | CHARLES AVENUE | CF |  |  |  |  | 4.1331 | 4.0392 | 3.9208 | 3.8157 | 3.6749 | 3.5259 | 3.3688 | 3.1188 | 2.8372 | 2.5474 | 0.8892 | -1.321 | -3.1026 | 6.2045 | 6.1586 | 6.0974 | 6.0402 | 5.9637 | 5.8759 | 5.7484 | 5.5229 | 5.2657 | 5.0004 | 3.5331 | 1.3219 | -1.3424 | 5.1178 | 5.031 | 4.927 | 4.8361 | 4.7096 | 4.578 | 4.4239 | 4.1933 | 3.93 | 3.6586
| CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | YES | 1.962 | 7.9929 | 7.8418 | 7.6684 | 7.4704 | 7.2531 | 7.0041 | 6.6918 | 6.3694 | 6.0367 | 5.7133 | 4.152 | 3.4133 | 2.5531 | 3.5592 | 3.4776 | 3.3827 | 3.2786 | 3.1306 | 2.9643 | 2.751 | 2.5551 | 2.3122 | 2.0714 | 0.85612 | 0.675 | 0.23214 | 3.2699 | 3.1944 | 3.0985 | 3.0087 | 2.8913 | 2.7607 | 2.5964 | 2.4719 | 2.324 | 2.1832
|  | CHARLESTON | EE |  |  |  |  | 7.9929 | 7.8418 | 7.6684 | 7.4704 | 7.2531 | 7.0041 | 6.6918 | 6.3694 | 6.0367 | 5.7133 | 4.6602 | 4.5612 | 3.7643 | 3.5592 | 3.4776 | 3.3827 | 3.2786 | 3.1306 | 2.9643 | 2.751 | 2.5551 | 2.3122 | 2.0714 | 1.2837 | 1.5505 | 1.275 | 3.2699 | 3.1944 | 3.0985 | 3.0087 | 2.8913 | 2.7607 | 2.5964 | 2.4719 | 2.324 | 2.1832
|  | CHARLESTON | HT |  |  |  |  | 8.0663 | 7.9459 | 7.8173 | 7.6592 | 7.4459 | 7.2398 | 7.0214 | 6.7776 | 6.5551 | 6.2888 | 5.0204 | 4.4704 | 3.6541 | 3.601 | 3.5367 | 3.4714 | 3.3765 | 3.248 | 3.1337 | 3.002 | 2.848 | 2.7102 | 2.5388 | 1.6061 | 1.5526 | 1.4985 | 3.3077 | 3.2413 | 3.173 | 3.0913 | 2.9893 | 2.9087 | 2.8036 | 2.6832 | 2.5668 | 2.4556
|  | CHARLESTON | HE |  |  |  |  | 8.0531 | 7.9235 | 7.7888 | 7.6204 | 7.4153 | 7.1878 | 6.8918 | 6.5653 | 6.2551 | 5.8755 | 4.152 | 3.4133 | 2.6163 | 3.5929 | 3.5245 | 3.4551 | 3.3653 | 3.2541 | 3.1276 | 2.9408 | 2.7092 | 2.4561 | 2.1633 | 0.85612 | 0.675 | 0.61378 | 3.3087 | 3.2556 | 3.1995 | 3.1291 | 3.0423 | 2.9628 | 2.8423 | 2.727 | 2.623 | 2.4985
|  | CHARLESTON | CF |  |  |  |  | 8.1041 | 8.0439 | 7.9673 | 7.8765 | 7.7755 | 7.6561 | 7.5061 | 7.2837 | 7.101 | 6.8918 | 5.6755 | 4.3704 | 2.5531 | 3.6163 | 3.5827 | 3.5408 | 3.4898 | 3.4316 | 3.3622 | 3.2755 | 3.1327 | 3.0133 | 2.8816 | 1.9551 | 1.3444 | 0.23214 | 3.3301 | 3.3015 | 3.2719 | 3.226 | 3.1852 | 3.1311 | 3.0648 | 2.9862 | 2.9138 | 2.8362
| ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | NO | YES | 0.996 | 4.8959 | 4.803 | 4.6744 | 4.552 | 4.4469 | 4.2959 | 4.2112 | 4.0734 | 3.9449 | 3.8316 | 3.5796 | 3.5612 | 3.5418 | 5.9581 | 5.8867 | 5.804 | 5.7091 | 5.6326 | 5.5132 | 5.4653 | 5.3714 | 5.2877 | 5.2153 | 5.05 | 5.0459 | 4.8449 | 5.4581 | 5.3969 | 5.2724 | 5.1714 | 5.0806 | 4.9428 | 4.8714 | 4.7428 | 4.6193 | 4.5132
|  | CLACHAN | EE |  |  |  |  | 4.8959 | 4.8275 | 4.6744 | 4.552 | 4.4469 | 4.2959 | 4.2112 | 4.0734 | 3.9449 | 3.8316 | 3.5796 | 3.6 | 3.5785 | 5.9581 | 5.9255 | 5.804 | 5.7091 | 5.6326 | 5.5132 | 5.4653 | 5.3714 | 5.2877 | 5.2153 | 5.05 | 5.0489 | 4.9632 | 5.4581 | 5.401 | 5.2724 | 5.1714 | 5.0806 | 4.9428 | 4.8714 | 4.7428 | 4.6193 | 4.5132
|  | CLACHAN | HT |  |  |  |  | 4.9275 | 4.803 | 4.6918 | 4.6132 | 4.4877 | 4.4326 | 4.351 | 4.2489 | 4.1479 | 4.0877 | 3.6632 | 3.5612 | 3.5418 | 5.9714 | 5.8867 | 5.8091 | 5.7571 | 5.654 | 5.6234 | 5.5744 | 5.5061 | 5.4408 | 5.4112 | 5.1244 | 5.0775 | 5.0663 | 5.4949 | 5.3969 | 5.3102 | 5.252 | 5.1255 | 5.0775 | 5 | 4.9081 | 4.8173 | 4.7632
|  | CLACHAN | HE |  |  |  |  | 4.9265 | 4.8744 | 4.7693 | 4.6642 | 4.5826 | 4.4928 | 4.4204 | 4.3296 | 4.2387 | 4.1877 | 3.7132 | 3.6 | 3.5867 | 5.9683 | 5.9469 | 5.8663 | 5.7663 | 5.7122 | 5.6163 | 5.5704 | 5.5183 | 5.4642 | 5.4224 | 5.1377 | 5.0459 | 4.9693 | 5.4938 | 5.452 | 5.3663 | 5.2785 | 5.2081 | 5.1285 | 5.0602 | 4.9775 | 4.8928 | 4.8469
|  | CLACHAN | CF |  |  |  |  | 4.9367 | 4.8959 | 4.8591 | 4.7551 | 4.6479 | 4.5755 | 4.4949 | 4.4275 | 4.3765 | 4.3122 | 4.0193 | 3.7316 | 3.6081 | 5.9734 | 5.9581 | 5.9398 | 5.8602 | 5.7755 | 5.7204 | 5.6428 | 5.602 | 5.5673 | 5.5204 | 5.3091 | 5.05 | 4.8449 | 5.5061 | 5.4724 | 5.4469 | 5.3663 | 5.2775 | 5.2183 | 5.1347 | 5.0744 | 5.0255 | 4.9663
| CARRADALE 1 | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0 | 0.25435 | 0.25231 | 0.24823 | 0.24211 | 0.24109 | 0.23497 | 0.22578 | 0.21762 | 0.20639 | 0.20435 | 0.18394 | 0.17986 | 0.15151 | 0.25866 | 0.2607 | 0.25662 | 0.25355 | 0.25457 | 0.25151 | 0.24437 | 0.23825 | 0.23111 | 0.22906 | 0.2158 | 0.22793 | 0.22691 | 0.26161 | 0.25957 | 0.25855 | 0.25242 | 0.24936 | 0.24426 | 0.23508 | 0.22691 | 0.21467 | 0.21467
|  | CLAONAIG | EE |  |  |  |  | 0.25435 | 0.25231 | 0.24925 | 0.24211 | 0.24109 | 0.23497 | 0.22578 | 0.21762 | 0.20639 | 0.20435 | 0.18394 | 0.18292 | 0.15253 | 0.25866 | 0.2607 | 0.26172 | 0.25355 | 0.25457 | 0.25151 | 0.24437 | 0.23825 | 0.23111 | 0.22906 | 0.2158 | 0.22895 | 0.22691 | 0.26161 | 0.25957 | 0.25855 | 0.25242 | 0.24936 | 0.24426 | 0.23508 | 0.22691 | 0.21467 | 0.21467
|  | CLAONAIG | HT |  |  |  |  | 0.26864 | 0.25843 | 0.24823 | 0.25129 | 0.24721 | 0.24211 | 0.23905 | 0.22782 | 0.22578 | 0.21762 | 0.19109 | 0.17986 | 0.15151 | 0.27294 | 0.2658 | 0.25662 | 0.26376 | 0.25968 | 0.25559 | 0.25457 | 0.24539 | 0.24641 | 0.24029 | 0.22192 | 0.22793 | 0.22793 | 0.27793 | 0.26773 | 0.25855 | 0.25957 | 0.2565 | 0.2514 | 0.24732 | 0.23712 | 0.23508 | 0.22691
|  | CLAONAIG | HE |  |  |  |  | 0.26864 | 0.25843 | 0.24925 | 0.25537 | 0.24925 | 0.24619 | 0.24415 | 0.23599 | 0.23088 | 0.22476 | 0.19721 | 0.19007 | 0.1607 | 0.27294 | 0.2658 | 0.25662 | 0.26478 | 0.2607 | 0.25764 | 0.25662 | 0.25049 | 0.24947 | 0.24437 | 0.22498 | 0.23508 | 0.23406 | 0.27793 | 0.26671 | 0.25855 | 0.26365 | 0.25855 | 0.25548 | 0.25344 | 0.24528 | 0.2412 | 0.23406
|  | CLAONAIG | CF |  |  |  |  | 0.26966 | 0.26048 | 0.25231 | 0.25129 | 0.25537 | 0.24823 | 0.24517 | 0.24007 | 0.24007 | 0.23394 | 0.21252 | 0.19619 | 0.16172 | 0.27294 | 0.2658 | 0.25866 | 0.26172 | 0.26478 | 0.26172 | 0.25764 | 0.25355 | 0.25355 | 0.24845 | 0.23519 | 0.23814 | 0.23201 | 0.27793 | 0.26977 | 0.26059 | 0.26059 | 0.26365 | 0.25753 | 0.25344 | 0.25038 | 0.24936 | 0.24324
| CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | NO | 8.274 | 1.318 | 0.86796 | 0.36286 | -0.15653 | -0.75143 | -1.4239 | -2.5014 | -3.7555 | -4.9647 | -6.0973 | -11.1749 | -14.7637 | -15.1178 | 5.5731 | 5.3578 | 5.1057 | 4.8414 | 4.4394 | 3.9608 | 3.3241 | 2.5598 | 1.8312 | 1.1506 | -2.0555 | -4.578 | -8.8422 | 4.0843 | 3.6435 | 3.1424 | 2.6261 | 2.0373 | 1.4016 | 0.4098 | -0.78612 | -1.9361 | -2.9973
|  | CLAYHILLS | EE |  |  |  |  | 1.318 | 0.86796 | 0.36286 | -0.15653 | -0.75143 | -1.4239 | -2.5014 | -3.7555 | -4.9647 | -6.0973 | -11.1749 | -14.4545 | -15.0341 | 5.5731 | 5.3578 | 5.1057 | 4.8414 | 4.4394 | 3.9608 | 3.3241 | 2.5598 | 1.8312 | 1.1506 | -2.0555 | -4.578 | -7.0269 | 4.0843 | 3.6435 | 3.1424 | 2.6261 | 2.0373 | 1.4016 | 0.4098 | -0.78612 | -1.9361 | -2.9973
|  | CLAYHILLS | HT |  |  |  |  | 1.4884 | 1.118 | 0.73122 | 0.31286 | -0.14122 | -0.6198 | -1.6086 | -2.6953 | -3.7412 | -4.8688 | -10.7229 | -14.7637 | -15.1178 | 5.7149 | 5.5629 | 5.3965 | 5.2088 | 4.9945 | 4.7527 | 4.2639 | 3.6771 | 3.1271 | 2.52 | -0.51265 | -2.4565 | -2.529 | 4.269 | 3.9098 | 3.5373 | 3.1241 | 2.67 | 2.1965 | 1.2904 | 0.30061 | -0.64939 | -1.6718
|  | CLAYHILLS | HE |  |  |  |  | 1.4527 | 1.1914 | 0.92102 | 0.61694 | 0.27714 | -0.084082 | -0.7902 | -1.6198 | -2.4086 | -3.2616 | -7.9922 | -10.9861 | -12.0484 | 5.6843 | 5.5088 | 5.3292 | 5.1149 | 4.869 | 4.5894 | 4.2271 | 3.7445 | 3.2312 | 2.6547 | -0.65143 | -3.1382 | -5.7912 | 4.2394 | 3.9761 | 3.7078 | 3.3986 | 3.0516 | 2.6884 | 2.0118 | 1.2302 | 0.50673 | -0.28204
|  | CLAYHILLS | CF |  |  |  |  | 1.5669 | 1.4282 | 1.2751 | 1.0945 | 0.89959 | 0.68327 | 0.45061 | 0.13735 | -0.16061 | -0.48306 | -2.9269 | -5.5341 | -8.4851 | 5.7476 | 5.6527 | 5.5394 | 5.4067 | 5.2588 | 5.0884 | 4.8853 | 4.5302 | 4.1894 | 3.818 | 1.2445 | -2.6422 | -8.8422 | 4.3506 | 4.2078 | 4.0527 | 3.8659 | 3.6649 | 3.4363 | 3.2078 | 2.8843 | 2.5812 | 2.2547
| DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | NO | 0.606 | -0.069249 | -0.10496 | -0.13762 | -0.16721 | -0.20904 | -0.24272 | -0.29374 | -0.35496 | -0.38353 | -0.43047 | -0.57639 | -0.65394 | -0.66517 | 0.16442 | 0.14096 | 0.12361 | 0.10524 | 0.07769 | 0.057282 | 0.024629 | -0.018229 | -0.031494 | -0.063127 | -0.17945 | -0.23251 | -0.28353 | -0.010065 | -0.043739 | -0.076392 | -0.1019 | -0.14068 | -0.17231 | -0.21925 | -0.27843 | -0.30496 | -0.34782
|  | COLDBACKIE | EE |  |  |  |  | -0.069249 | -0.10496 | -0.13762 | -0.16721 | -0.20904 | -0.24272 | -0.29374 | -0.35496 | -0.38353 | -0.43047 | -0.54272 | -0.56211 | -0.56823 | 0.16442 | 0.14096 | 0.12361 | 0.10524 | 0.07769 | 0.057282 | 0.024629 | -0.018229 | -0.031494 | -0.063127 | -0.13558 | -0.16517 | -0.21007 | -0.010065 | -0.043739 | -0.076392 | -0.1019 | -0.14068 | -0.17231 | -0.21925 | -0.27843 | -0.30496 | -0.34782
|  | COLDBACKIE | HT |  |  |  |  | -0.055984 | -0.083535 | -0.11109 | -0.13558 | -0.17027 | -0.19374 | -0.23353 | -0.27639 | -0.307 | -0.35292 | -0.50088 | -0.57231 | -0.58353 | 0.17463 | 0.15932 | 0.14606 | 0.13177 | 0.1083 | 0.098098 | 0.073608 | 0.046057 | 0.029731 | 0.0011592 | -0.093739 | -0.13251 | -0.13558 | 0.0021796 | -0.023331 | -0.04782 | -0.070269 | -0.10394 | -0.12333 | -0.16211 | -0.20496 | -0.23251 | -0.27333
|  | COLDBACKIE | HE |  |  |  |  | -0.057004 | -0.079453 | -0.10088 | -0.12027 | -0.15088 | -0.16619 | -0.20904 | -0.257 | -0.2968 | -0.34782 | -0.57639 | -0.65394 | -0.66007 | 0.17463 | 0.16034 | 0.14606 | 0.12973 | 0.1083 | 0.087894 | 0.060343 | 0.02769 | 0.00013878 | -0.032514 | -0.17945 | -0.23251 | -0.23456 | 0.0021796 | -0.020269 | -0.040678 | -0.057004 | -0.085576 | -0.10496 | -0.14374 | -0.18966 | -0.22639 | -0.27231
|  | COLDBACKIE | CF |  |  |  |  | -0.054963 | -0.07231 | -0.089657 | -0.11211 | -0.12741 | -0.15496 | -0.18047 | -0.19374 | -0.22027 | -0.23864 | -0.41313 | -0.56007 | -0.66517 | 0.17463 | 0.16647 | 0.15524 | 0.14198 | 0.12973 | 0.1134 | 0.091976 | 0.082792 | 0.062384 | 0.045037 | -0.079453 | -0.17741 | -0.28353 | 0.0032 | -0.011086 | -0.029453 | -0.049861 | -0.064147 | -0.088637 | -0.11415 | -0.12843 | -0.15292 | -0.17027
| DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0 | 0.47163 | 0.46143 | 0.45429 | 0.44408 | 0.4349 | 0.4298 | 0.41041 | 0.39408 | 0.39204 | 0.37878 | 0.35429 | 0.34612 | 0.29908 | 0.46847 | 0.46643 | 0.46031 | 0.4552 | 0.44704 | 0.44602 | 0.43276 | 0.42051 | 0.41847 | 0.41133 | 0.39704 | 0.41444 | 0.41036 | 0.47056 | 0.46138 | 0.45423 | 0.44505 | 0.43689 | 0.42974 | 0.41342 | 0.39709 | 0.39505 | 0.38281
|  | COLINTRAIVE | EE |  |  |  |  | 0.47163 | 0.46143 | 0.45429 | 0.44408 | 0.4349 | 0.4298 | 0.41041 | 0.39408 | 0.39204 | 0.37878 | 0.35429 | 0.35122 | 0.30214 | 0.47255 | 0.46745 | 0.46031 | 0.4552 | 0.44704 | 0.44602 | 0.43276 | 0.42051 | 0.41847 | 0.41133 | 0.39704 | 0.41546 | 0.4124 | 0.47056 | 0.4624 | 0.45423 | 0.44505 | 0.43689 | 0.42974 | 0.41342 | 0.39709 | 0.39505 | 0.38281
|  | COLINTRAIVE | HT |  |  |  |  | 0.47265 | 0.46143 | 0.46245 | 0.45327 | 0.44816 | 0.44204 | 0.43184 | 0.41653 | 0.41041 | 0.39714 | 0.36245 | 0.34612 | 0.29908 | 0.46847 | 0.46643 | 0.46745 | 0.46133 | 0.45929 | 0.45622 | 0.44806 | 0.43888 | 0.4348 | 0.42663 | 0.40214 | 0.41444 | 0.41342 | 0.47056 | 0.46138 | 0.4624 | 0.45423 | 0.44913 | 0.44301 | 0.43383 | 0.41954 | 0.41342 | 0.40219
|  | COLINTRAIVE | HE |  |  |  |  | 0.47265 | 0.46245 | 0.46551 | 0.45735 | 0.45224 | 0.44612 | 0.43796 | 0.42571 | 0.41959 | 0.40939 | 0.36551 | 0.35429 | 0.30724 | 0.46847 | 0.46643 | 0.46949 | 0.46235 | 0.46031 | 0.45827 | 0.45112 | 0.44194 | 0.43786 | 0.43071 | 0.40418 | 0.41852 | 0.4175 | 0.47056 | 0.4624 | 0.46444 | 0.4573 | 0.45219 | 0.44709 | 0.43995 | 0.42668 | 0.4226 | 0.41138
|  | COLINTRAIVE | CF |  |  |  |  | 0.47367 | 0.46245 | 0.46347 | 0.46041 | 0.45939 | 0.44816 | 0.4451 | 0.43694 | 0.42776 | 0.42776 | 0.38388 | 0.36347 | 0.30622 | 0.46847 | 0.46745 | 0.46847 | 0.46745 | 0.46643 | 0.45724 | 0.45724 | 0.45112 | 0.445 | 0.44398 | 0.41235 | 0.42158 | 0.41036 | 0.4726 | 0.4624 | 0.46444 | 0.46138 | 0.46036 | 0.44913 | 0.44607 | 0.43893 | 0.42872 | 0.42872
| STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 0.108 | 0.44592 | 5.5839 | 5.4931 | 5.3849 | 5.291 | 5.1727 | 5.0186 | 4.8512 | 4.7308 | 4.591 | 4.2451 | 4.142 | -1.3546 | 6.9135 | 6.8522 | 6.7941 | 6.7155 | 6.6553 | 6.5655 | 6.4533 | 6.3176 | 6.241 | 6.138 | 5.891 | 0.42628 | 5.3727 | 6.4604 | 6.3522 | 6.2594 | 6.1461 | 6.0573 | 5.9288 | 5.7676 | 5.5849 | 5.4706 | 5.3257
|  | COLL | EE |  |  |  |  | 0.44592 | 5.5839 | 5.4931 | 5.3849 | 5.291 | 5.1727 | 5.0186 | 4.8512 | 4.7308 | 4.591 | 4.2451 | 4.1951 | -1.2872 | 6.9135 | 6.8522 | 6.7941 | 6.7155 | 6.6553 | 6.5655 | 6.4533 | 6.3176 | 6.241 | 6.138 | 5.891 | 0.42934 | 5.6094 | 6.4604 | 6.3522 | 6.2594 | 6.1461 | 6.0573 | 5.9288 | 5.7676 | 5.5849 | 5.4706 | 5.3257
|  | COLL | HT |  |  |  |  | 0.47449 | 5.6308 | 5.5492 | 5.4686 | 5.3706 | 5.2757 | 5.1594 | 5.0594 | 4.938 | 4.8135 | 4.3563 | 4.142 | -1.3546 | 6.9369 | 6.8951 | 6.8533 | 6.8135 | 6.7594 | 6.6982 | 6.6186 | 6.5604 | 6.4747 | 6.3808 | 6.038 | 0.55995 | 5.8951 | 6.4971 | 6.4216 | 6.338 | 6.2624 | 6.1614 | 6.0655 | 5.9461 | 5.8522 | 5.7278 | 5.5941
|  | COLL | HE |  |  |  |  | 0.47347 | 5.6533 | 5.5931 | 5.5339 | 5.4604 | 5.3869 | 5.2869 | 5.2002 | 5.0941 | 4.9839 | 4.392 | 4.2451 | -1.2393 | 6.9369 | 6.9012 | 6.8635 | 6.8288 | 6.7788 | 6.7227 | 6.6482 | 6.592 | 6.5084 | 6.4196 | 5.9992 | 0.4773 | 5.6635 | 6.4971 | 6.438 | 6.3716 | 6.3155 | 6.2339 | 6.1573 | 6.0492 | 5.9686 | 5.8563 | 5.7369
|  | COLL | CF |  |  |  |  | 0.48469 | 5.6727 | 5.6186 | 5.5573 | 5.5094 | 5.4461 | 5.3818 | 5.3033 | 5.2533 | 5.1808 | 4.8216 | 4.4747 | -1.2026 | 6.942 | 6.9145 | 6.8829 | 6.842 | 6.8124 | 6.7665 | 6.7165 | 6.6461 | 6.6124 | 6.5461 | 6.2084 | 0.42628 | 5.3727 | 6.5114 | 6.4645 | 6.4114 | 6.3451 | 6.3002 | 6.2318 | 6.1676 | 6.0818 | 6.039 | 5.9614
| CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | NO | 4.474 | 7.2368 | 7.1092 | 6.949 | 6.797 | 6.6174 | 6.4133 | 6.1776 | 5.8878 | 5.4745 | 5.047 | 3.347 | 2.7368 | 1.3051 | 9.1541 | 9.0531 | 8.9307 | 8.8225 | 8.6847 | 8.5276 | 8.348 | 8.1266 | 7.9245 | 7.7347 | 6.6939 | 6.821 | 6.1587 | 8.7322 | 8.6006 | 8.4169 | 8.2291 | 8.0057 | 7.7516 | 7.4516 | 7.0363 | 6.6261 | 6.2179
|  | COMMERCE STREET | EE |  |  |  |  | 7.2368 | 7.1092 | 6.949 | 6.797 | 6.6174 | 6.4133 | 6.1776 | 5.8878 | 5.4745 | 5.047 | 3.347 | 2.846 | 1.6276 | 9.1541 | 9.0531 | 8.9307 | 8.8225 | 8.6847 | 8.5276 | 8.348 | 8.1266 | 7.9245 | 7.7347 | 6.6949 | 6.9159 | 6.8393 | 8.7322 | 8.6006 | 8.4169 | 8.2291 | 8.0057 | 7.7516 | 7.4516 | 7.0363 | 6.6261 | 6.2179
|  | COMMERCE STREET | HT |  |  |  |  | 7.2684 | 7.1653 | 7.0398 | 6.9092 | 6.747 | 6.5868 | 6.3847 | 6.1368 | 5.8909 | 5.5307 | 3.5725 | 2.7368 | 1.3051 | 9.1817 | 9.1041 | 9.0153 | 8.9225 | 8.8041 | 8.6878 | 8.5409 | 8.3572 | 8.1776 | 7.9919 | 6.9245 | 6.8965 | 6.6842 | 8.7618 | 8.6577 | 8.5342 | 8.373 | 8.1791 | 7.975 | 7.7261 | 7.4148 | 7.0669 | 6.6812
|  | COMMERCE STREET | HE |  |  |  |  | 7.2694 | 7.1704 | 7.0572 | 6.9347 | 6.7827 | 6.6256 | 6.4256 | 6.1684 | 5.9174 | 5.4623 | 3.3807 | 2.7602 | 1.3419 | 9.1807 | 9.1011 | 9.0133 | 8.9184 | 8.8011 | 8.6837 | 8.5296 | 8.3307 | 8.1388 | 7.9368 | 6.6939 | 6.821 | 6.5893 | 8.7638 | 8.6597 | 8.5485 | 8.3924 | 8.2026 | 8.0036 | 7.7485 | 7.4016 | 7.0332 | 6.6108
|  | COMMERCE STREET | CF |  |  |  |  | 7.3092 | 7.2551 | 7.2021 | 7.1347 | 7.0592 | 6.9704 | 6.8909 | 6.7602 | 6.6368 | 6.4919 | 5.3409 | 3.8204 | 1.5296 | 9.2184 | 9.1704 | 9.1245 | 9.0643 | 8.999 | 8.9174 | 8.8541 | 8.746 | 8.6409 | 8.5215 | 7.8062 | 7.4985 | 6.1587 | 8.8148 | 8.7597 | 8.7057 | 8.6332 | 8.5475 | 8.4291 | 8.3189 | 8.1495 | 7.9883 | 7.8006
| ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | YES | 0 | 0.042673 | 0.032469 | 0.032469 | 0.025327 | 0.022265 | 0.015122 | 0.014102 | 0.012061 | 0.012061 | 0.012061 | 0.011041 | 0.01002 | 0.0045 | 0.044296 | 0.036133 | 0.035112 | 0.027969 | 0.025929 | 0.018786 | 0.017765 | 0.020827 | 0.017765 | 0.017765 | 0.020827 | 0.024097 | 0.021036 | 0.043485 | 0.035321 | 0.034301 | 0.027158 | 0.024097 | 0.016954 | 0.015934 | 0.013893 | 0.014913 | 0.014913
|  | COMRIE | EE |  |  |  |  | 0.042673 | 0.032469 | 0.032469 | 0.025327 | 0.022265 | 0.015122 | 0.014102 | 0.012061 | 0.018184 | 0.017163 | 0.011041 | 0.01002 | 0.0055204 | 0.044296 | 0.036133 | 0.035112 | 0.027969 | 0.025929 | 0.018786 | 0.017765 | 0.020827 | 0.025929 | 0.024908 | 0.022867 | 0.024097 | 0.024097 | 0.043485 | 0.035321 | 0.034301 | 0.027158 | 0.024097 | 0.016954 | 0.015934 | 0.013893 | 0.020015 | 0.018995
|  | COMRIE | HT |  |  |  |  | 0.042673 | 0.040633 | 0.03349 | 0.032469 | 0.031449 | 0.030429 | 0.022265 | 0.020224 | 0.012061 | 0.012061 | 0.011041 | 0.01002 | 0.0045 | 0.044296 | 0.043276 | 0.036133 | 0.035112 | 0.034092 | 0.034092 | 0.026949 | 0.025929 | 0.017765 | 0.017765 | 0.022867 | 0.024097 | 0.024097 | 0.044505 | 0.043485 | 0.036342 | 0.034301 | 0.033281 | 0.03226 | 0.024097 | 0.023077 | 0.014913 | 0.014913
|  | COMRIE | HE |  |  |  |  | 0.042673 | 0.040633 | 0.03349 | 0.032469 | 0.032469 | 0.032469 | 0.024306 | 0.021245 | 0.014102 | 0.014102 | 0.011041 | 0.011041 | 0.0055204 | 0.044296 | 0.043276 | 0.036133 | 0.035112 | 0.035112 | 0.035112 | 0.026949 | 0.024908 | 0.017765 | 0.017765 | 0.022867 | 0.024097 | 0.024097 | 0.044505 | 0.043485 | 0.036342 | 0.034301 | 0.034301 | 0.034301 | 0.026138 | 0.023077 | 0.015934 | 0.015934
|  | COMRIE | CF |  |  |  |  | 0.042673 | 0.040633 | 0.03349 | 0.03349 | 0.032469 | 0.032469 | 0.032469 | 0.024306 | 0.024306 | 0.023286 | 0.013082 | 0.013082 | 0.0065408 | 0.044296 | 0.043276 | 0.036133 | 0.036133 | 0.035112 | 0.035112 | 0.035112 | 0.026949 | 0.026949 | 0.025929 | 0.020827 | 0.025117 | 0.021036 | 0.044505 | 0.043485 | 0.036342 | 0.036342 | 0.034301 | 0.034301 | 0.034301 | 0.026138 | 0.026138 | 0.025117
| TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | 0.891 | -0.81269 | -0.85759 | -0.90759 | -0.97392 | -1.0188 | -1.0831 | -1.1698 | -1.3178 | -1.4035 | -1.5076 | -1.7433 | -1.8096 | -1.8331 | -0.2382 | -0.26678 | -0.30249 | -0.34943 | -0.38004 | -0.42494 | -0.48412 | -0.60453 | -0.66882 | -0.74943 | -0.93616 | -1.0004 | -1.2729 | -0.50657 | -0.55045 | -0.60045 | -0.66473 | -0.71065 | -0.77086 | -0.85351 | -0.99637 | -1.0739 | -1.1719
|  | CONNEL | EE |  |  |  |  | -0.81269 | -0.85759 | -0.90759 | -0.97392 | -1.0188 | -1.0831 | -1.1698 | -1.3178 | -1.4035 | -1.5076 | -1.7433 | -1.779 | -1.8015 | -0.2382 | -0.26678 | -0.30249 | -0.34943 | -0.38004 | -0.42494 | -0.48412 | -0.60453 | -0.66882 | -0.74943 | -0.93616 | -0.99331 | -1.1045 | -0.50657 | -0.55045 | -0.60045 | -0.66473 | -0.71065 | -0.77086 | -0.85351 | -0.99637 | -1.0739 | -1.1719
|  | CONNEL | HT |  |  |  |  | -0.78412 | -0.82698 | -0.86576 | -0.91576 | -0.95759 | -1.0188 | -1.1382 | -1.2525 | -1.3392 | -1.4249 | -1.6892 | -1.8096 | -1.8331 | -0.21269 | -0.2382 | -0.26269 | -0.29535 | -0.32188 | -0.36167 | -0.45657 | -0.54841 | -0.60657 | -0.67188 | -0.86167 | -0.9382 | -0.95045 | -0.47596 | -0.5178 | -0.55657 | -0.60453 | -0.64535 | -0.70555 | -0.81269 | -0.9229 | -1.0035 | -1.0862
|  | CONNEL | HE |  |  |  |  | -0.78514 | -0.81678 | -0.84739 | -0.89229 | -0.92596 | -0.97494 | -1.0117 | -1.128 | -1.2188 | -1.3107 | -1.6617 | -1.7372 | -1.7474 | -0.21371 | -0.23412 | -0.25657 | -0.28718 | -0.31269 | -0.35147 | -0.37188 | -0.46678 | -0.53922 | -0.61371 | -0.878 | -0.96576 | -1.0637 | -0.47698 | -0.50963 | -0.54024 | -0.58616 | -0.61678 | -0.66678 | -0.69943 | -0.81167 | -0.89229 | -0.97902
|  | CONNEL | CF |  |  |  |  | -0.77902 | -0.80453 | -0.84127 | -0.86576 | -0.89024 | -0.928 | -0.96984 | -0.99739 | -1.0566 | -1.1107 | -1.3902 | -1.6525 | -1.7627 | -0.21065 | -0.22596 | -0.25453 | -0.2729 | -0.29229 | -0.31984 | -0.35453 | -0.37494 | -0.42392 | -0.46984 | -0.71576 | -1.0004 | -1.2729 | -0.47086 | -0.49637 | -0.53208 | -0.55555 | -0.58004 | -0.61678 | -0.65657 | -0.68106 | -0.73922 | -0.7882
| BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | NO | 1.356 | 1.6001 | 1.3899 | 1.1837 | 9.4365 | 9.2192 | 8.9621 | 8.5202 | 8.0845 | 7.5835 | 7.3029 | 6.2059 | 5.5733 | -3.3502 | 2.807 | 2.6876 | 10.6253 | 10.4814 | 10.3529 | 10.1937 | 9.9825 | 9.6886 | 9.4039 | 9.4437 | 8.7947 | 0.52647 | -0.10006 | 2.3724 | 10.4411 | 10.2524 | 10.0228 | 9.8146 | 9.5636 | 9.2177 | 8.7401 | 8.2769 | 8.2013
|  | CONON BRIDGE | EE |  |  |  |  | 1.6001 | 1.3899 | 1.1837 | 9.4365 | 9.2192 | 8.9651 | 8.6049 | 8.0845 | 7.5835 | 7.4437 | 6.2059 | 5.6774 | -3.2471 | 2.807 | 2.6876 | 10.6253 | 10.4814 | 10.3529 | 10.1937 | 9.9825 | 9.6886 | 9.4039 | 9.4437 | 8.7947 | 0.52647 | 0.13565 | 2.3724 | 10.4411 | 10.2524 | 10.0228 | 9.8146 | 9.5636 | 9.2177 | 8.7401 | 8.2769 | 8.2779
|  | CONON BRIDGE | HT |  |  |  |  | 1.6429 | 1.447 | 1.2562 | 9.5253 | 9.3263 | 8.9621 | 8.5202 | 8.0927 | 7.7039 | 7.3029 | 6.2325 | 5.5733 | -3.3502 | 2.8498 | 2.7539 | 10.7161 | 10.5968 | 10.5008 | 10.3161 | 10.0957 | 9.8906 | 9.6855 | 9.4763 | 8.9988 | 0.80504 | 0.74994 | 2.4306 | 10.5238 | 10.3564 | 10.1513 | 9.9789 | 9.6626 | 9.2779 | 8.9136 | 8.5636 | 8.2013
|  | CONON BRIDGE | HE |  |  |  |  | 1.6552 | 1.5225 | 1.4052 | 9.7478 | 9.6182 | 9.46 | 9.2263 | 8.9243 | 8.5906 | 8.2539 | 6.9457 | 6.3039 | -2.742 | 2.8519 | 2.7743 | 10.7559 | 10.66 | 10.5855 | 10.4784 | 10.3376 | 10.1702 | 9.9814 | 9.7804 | 9.1141 | 0.77851 | 0.3581 | 2.4438 | 10.582 | 10.4697 | 10.3248 | 10.2095 | 10.0462 | 9.8218 | 9.5544 | 9.2513 | 8.9401
|  | CONON BRIDGE | CF |  |  |  |  | 1.6807 | 1.5888 | 1.499 | 9.8814 | 9.7661 | 9.6733 | 9.5457 | 9.3998 | 9.2223 | 9.0039 | 7.808 | 7.2774 | -2.2084 | 2.8631 | 2.808 | 10.8008 | 10.7274 | 10.6457 | 10.5835 | 10.4865 | 10.3733 | 10.26 | 10.1141 | 9.2774 | 0.853 | -0.10006 | 2.4652 | 10.6442 | 10.5554 | 10.4524 | 10.333 | 10.2493 | 10.1197 | 9.9656 | 9.8105 | 9.6095
| BEAULY | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | NO | 0.264 | 0.26119 | 0.24895 | 0.24078 | 0.23058 | 0.22038 | 0.20813 | 0.19282 | 0.1714 | 0.16936 | 0.15405 | 0.12446 | 0.11425 | 0.064151 | 0.31925 | 0.31211 | 0.30599 | 0.30089 | 0.29374 | 0.28762 | 0.2764 | 0.26109 | 0.26211 | 0.24884 | 0.23048 | 0.24686 | 0.22645 | 0.32032 | 0.31522 | 0.30808 | 0.2989 | 0.28869 | 0.27951 | 0.26522 | 0.24686 | 0.24277 | 0.22849
|  | CONON FALLS | EE |  |  |  |  | 0.26119 | 0.24895 | 0.24078 | 0.23058 | 0.22038 | 0.20813 | 0.19282 | 0.1714 | 0.16936 | 0.15405 | 0.12446 | 0.11833 | 0.070273 | 0.31925 | 0.31313 | 0.30599 | 0.30089 | 0.29374 | 0.28762 | 0.2764 | 0.26109 | 0.26211 | 0.24884 | 0.23048 | 0.24686 | 0.23461 | 0.32441 | 0.31522 | 0.30808 | 0.2989 | 0.28869 | 0.27951 | 0.26522 | 0.24686 | 0.24277 | 0.22849
|  | CONON FALLS | HT |  |  |  |  | 0.26221 | 0.24997 | 0.24997 | 0.24078 | 0.23058 | 0.22344 | 0.21119 | 0.20303 | 0.1918 | 0.17446 | 0.13364 | 0.11425 | 0.064151 | 0.32027 | 0.31211 | 0.31415 | 0.30905 | 0.30191 | 0.29884 | 0.2917 | 0.28558 | 0.27844 | 0.26517 | 0.23966 | 0.24992 | 0.24788 | 0.32032 | 0.31624 | 0.31624 | 0.3091 | 0.30094 | 0.29379 | 0.28461 | 0.27543 | 0.26318 | 0.24992
|  | CONON FALLS | HE |  |  |  |  | 0.26221 | 0.25201 | 0.25303 | 0.24691 | 0.23772 | 0.2316 | 0.22242 | 0.21323 | 0.19793 | 0.18772 | 0.13466 | 0.12242 | 0.073335 | 0.32027 | 0.31313 | 0.31415 | 0.31109 | 0.30395 | 0.30089 | 0.29578 | 0.29068 | 0.2815 | 0.27027 | 0.23762 | 0.24788 | 0.23869 | 0.32032 | 0.31828 | 0.31726 | 0.31318 | 0.30604 | 0.29992 | 0.29175 | 0.28257 | 0.27237 | 0.2591
|  | CONON FALLS | CF |  |  |  |  | 0.26221 | 0.25201 | 0.25201 | 0.24793 | 0.24384 | 0.23466 | 0.2316 | 0.22344 | 0.21323 | 0.21017 | 0.17548 | 0.13874 | 0.075376 | 0.32027 | 0.31415 | 0.31619 | 0.31313 | 0.31007 | 0.30395 | 0.30191 | 0.29476 | 0.28762 | 0.28558 | 0.26007 | 0.25196 | 0.22645 | 0.32032 | 0.31828 | 0.3193 | 0.31726 | 0.31216 | 0.30502 | 0.30196 | 0.29379 | 0.28461 | 0.28155
| DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | NO | 4.362 | 12.6564 | 12.3247 | 11.9094 | 11.4288 | 10.9635 | 10.4839 | 9.7982 | 8.8931 | 8.0513 | 7.3319 | 5.089 | 4.4982 | 3.0135 | 14.7411 | 14.4798 | 14.1615 | 13.789 | 13.3962 | 12.987 | 12.5104 | 11.9053 | 11.3319 | 10.8166 | 8.7717 | 8.3533 | 3.3686 | 13.5594 | 13.2023 | 12.7798 | 12.2747 | 11.7482 | 11.2176 | 10.5727 | 9.7217 | 8.9339 | 8.2686
|  | CONSTABLE STREET | EE |  |  |  |  | 12.6564 | 12.3247 | 11.9094 | 11.4288 | 10.9635 | 10.4839 | 9.7982 | 8.8931 | 8.0513 | 7.3319 | 5.089 | 5.4237 | 3.7656 | 14.7411 | 14.4798 | 14.1615 | 13.789 | 13.3962 | 12.987 | 12.5104 | 11.9053 | 11.3319 | 10.8166 | 8.7717 | 8.5268 | 6.4431 | 13.5594 | 13.2023 | 12.7798 | 12.2747 | 11.7482 | 11.2176 | 10.5727 | 9.7217 | 8.9339 | 8.2686
|  | CONSTABLE STREET | HT |  |  |  |  | 12.7482 | 12.5196 | 12.1992 | 11.8166 | 11.4717 | 11.0156 | 10.436 | 9.8156 | 9.1104 | 8.3594 | 5.4319 | 4.4982 | 3.0135 | 14.8829 | 14.7033 | 14.49 | 14.2319 | 13.9849 | 13.6635 | 13.287 | 12.8686 | 12.4431 | 12.0053 | 10.0911 | 10.0217 | 9.9839 | 13.7278 | 13.4696 | 13.1553 | 12.7727 | 12.4176 | 11.9482 | 11.3635 | 10.6972 | 10.0268 | 9.336
|  | CONSTABLE STREET | HE |  |  |  |  | 12.739 | 12.6043 | 12.3747 | 12.086 | 11.8411 | 11.5574 | 11.1523 | 10.6319 | 10.1533 | 9.5676 | 7.2319 | 6.4115 | 5.0666 | 14.8604 | 14.6951 | 14.4962 | 14.2513 | 14.0207 | 13.7421 | 13.4115 | 12.988 | 12.6013 | 12.1656 | 10.0645 | 9.2604 | 7.3625 | 13.7166 | 13.5349 | 13.2911 | 12.987 | 12.7186 | 12.3972 | 11.987 | 11.4584 | 10.9584 | 10.389
|  | CONSTABLE STREET | CF |  |  |  |  | 12.7666 | 12.6921 | 12.5819 | 12.3972 | 12.237 | 12.0676 | 11.9125 | 11.7125 | 11.487 | 11.2451 | 9.589 | 7.7023 | 4.5727 | 14.9104 | 14.7931 | 14.6309 | 14.4482 | 14.2615 | 14.0513 | 13.8156 | 13.5298 | 13.236 | 12.9207 | 10.8615 | 8.3533 | 3.3686 | 13.7798 | 13.6809 | 13.4962 | 13.287 | 13.0911 | 12.8941 | 12.6951 | 12.437 | 12.1686 | 11.8839
| ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | NO | 0 | 0.090449 | 0.089429 | 0.080245 | 0.079224 | 0.071061 | 0.071061 | 0.06902 | 0.070041 | 0.06902 | 0.068 | 0.063918 | 0.061878 | 0.052878 | 0.088592 | 0.088592 | 0.080429 | 0.079408 | 0.071245 | 0.074306 | 0.071245 | 0.072265 | 0.071245 | 0.073286 | 0.070224 | 0.072684 | 0.068602 | 0.091051 | 0.091051 | 0.081867 | 0.080847 | 0.072684 | 0.071663 | 0.070643 | 0.070643 | 0.069622 | 0.068602
|  | CONTULLICH | EE |  |  |  |  | 0.090449 | 0.089429 | 0.080245 | 0.079224 | 0.071061 | 0.071061 | 0.075143 | 0.073102 | 0.072082 | 0.068 | 0.063918 | 0.061878 | 0.052878 | 0.088592 | 0.088592 | 0.080429 | 0.079408 | 0.071245 | 0.074306 | 0.079408 | 0.077367 | 0.075327 | 0.073286 | 0.070224 | 0.072684 | 0.071663 | 0.091051 | 0.091051 | 0.081867 | 0.080847 | 0.072684 | 0.071663 | 0.075745 | 0.072684 | 0.071663 | 0.068602
|  | CONTULLICH | HT |  |  |  |  | 0.098612 | 0.090449 | 0.089429 | 0.087388 | 0.079224 | 0.078204 | 0.06902 | 0.070041 | 0.070041 | 0.075143 | 0.063918 | 0.061878 | 0.052878 | 0.096755 | 0.088592 | 0.088592 | 0.087571 | 0.079408 | 0.078388 | 0.071245 | 0.074306 | 0.074306 | 0.078388 | 0.070224 | 0.074724 | 0.074724 | 0.099214 | 0.091051 | 0.091051 | 0.08901 | 0.080847 | 0.079827 | 0.070643 | 0.070643 | 0.069622 | 0.075745
|  | CONTULLICH | HE |  |  |  |  | 0.097592 | 0.090449 | 0.089429 | 0.087388 | 0.079224 | 0.079224 | 0.070041 | 0.071061 | 0.06902 | 0.075143 | 0.064939 | 0.063918 | 0.052878 | 0.095735 | 0.088592 | 0.088592 | 0.087571 | 0.079408 | 0.079408 | 0.071245 | 0.074306 | 0.073286 | 0.078388 | 0.070224 | 0.072684 | 0.071663 | 0.098194 | 0.091051 | 0.091051 | 0.08901 | 0.080847 | 0.080847 | 0.071663 | 0.070643 | 0.069622 | 0.075745
|  | CONTULLICH | CF |  |  |  |  | 0.098612 | 0.097592 | 0.090449 | 0.089429 | 0.087388 | 0.080245 | 0.080245 | 0.072082 | 0.070041 | 0.072082 | 0.073102 | 0.064939 | 0.054918 | 0.096755 | 0.095735 | 0.088592 | 0.087571 | 0.087571 | 0.080429 | 0.080429 | 0.072265 | 0.071245 | 0.074306 | 0.076347 | 0.072684 | 0.068602 | 0.099214 | 0.098194 | 0.091051 | 0.090031 | 0.08799 | 0.080847 | 0.080847 | 0.072684 | 0.070643 | 0.071663
| FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | NO | 0.746 | -0.63237 | -0.67012 | -0.70788 | -0.76094 | -0.80278 | -0.864 | -0.91298 | -0.99155 | -1.062 | -1.1293 | -1.3273 | -1.4058 | -1.463 | -0.42931 | -0.4538 | -0.47931 | -0.51502 | -0.54155 | -0.58747 | -0.61298 | -0.6691 | -0.71196 | -0.75788 | -0.88849 | -0.94971 | -1.0987 | -0.55176 | -0.58951 | -0.62216 | -0.67216 | -0.714 | -0.77216 | -0.81808 | -0.89359 | -0.95992 | -1.0252
|  | CORRAN | EE |  |  |  |  | -0.63237 | -0.67012 | -0.70788 | -0.76094 | -0.80278 | -0.864 | -0.91298 | -0.99155 | -1.062 | -1.1293 | -1.3273 | -1.3813 | -1.4018 | -0.42931 | -0.4538 | -0.47931 | -0.51502 | -0.54155 | -0.58747 | -0.61298 | -0.6691 | -0.71196 | -0.75788 | -0.88849 | -0.94971 | -1.0109 | -0.55176 | -0.58951 | -0.62216 | -0.67216 | -0.714 | -0.77216 | -0.81808 | -0.89359 | -0.95992 | -1.0252
|  | CORRAN | HT |  |  |  |  | -0.61196 | -0.64461 | -0.68135 | -0.72216 | -0.75482 | -0.80584 | -0.84869 | -0.91502 | -0.97829 | -1.0211 | -1.2854 | -1.4058 | -1.4528 | -0.414 | -0.43135 | -0.45278 | -0.48339 | -0.49869 | -0.53339 | -0.55686 | -0.60073 | -0.64257 | -0.664 | -0.84155 | -0.91196 | -0.95176 | -0.53033 | -0.56196 | -0.59563 | -0.63645 | -0.66706 | -0.71706 | -0.75788 | -0.8191 | -0.88033 | -0.91808
|  | CORRAN | HE |  |  |  |  | -0.61196 | -0.63849 | -0.664 | -0.70278 | -0.72522 | -0.77012 | -0.80584 | -0.86502 | -0.92318 | -0.96604 | -1.2875 | -1.3824 | -1.4089 | -0.414 | -0.43033 | -0.45073 | -0.47522 | -0.49053 | -0.5242 | -0.54665 | -0.58849 | -0.62931 | -0.64767 | -0.84563 | -0.91604 | -0.97012 | -0.53033 | -0.55584 | -0.58237 | -0.61808 | -0.63849 | -0.68135 | -0.71808 | -0.77522 | -0.83645 | -0.88951
|  | CORRAN | CF |  |  |  |  | -0.60788 | -0.63135 | -0.64767 | -0.67829 | -0.69563 | -0.72624 | -0.75992 | -0.78543 | -0.8242 | -0.86298 | -1.0467 | -1.2589 | -1.463 | -0.40992 | -0.42522 | -0.43849 | -0.45992 | -0.47216 | -0.49053 | -0.5191 | -0.53951 | -0.56808 | -0.59767 | -0.73951 | -0.92216 | -1.0987 | -0.52727 | -0.54971 | -0.56706 | -0.59461 | -0.61196 | -0.64257 | -0.67318 | -0.70278 | -0.73645 | -0.7742
| KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 1.425 | -0.060816 | -0.11082 | -0.17612 | -0.24143 | -0.32612 | -0.38735 | -0.48531 | -0.58429 | -0.68531 | -0.77816 | -0.98122 | -1.0455 | -1.0629 | 0.90857 | 0.88 | 0.83408 | 0.79735 | 0.74531 | 0.70755 | 0.64735 | 0.58306 | 0.52184 | 0.46163 | 0.33102 | 0.2698 | 0.068776 | 0.6249 | 0.58 | 0.51571 | 0.45551 | 0.37796 | 0.32184 | 0.23 | 0.13714 | 0.042245 | -0.04551
|  | COSHIEVILLE | EE |  |  |  |  | -0.060816 | -0.11082 | -0.17612 | -0.24143 | -0.32612 | -0.38735 | -0.48531 | -0.58429 | -0.68531 | -0.77816 | -0.98122 | -1.0159 | -1.0343 | 0.90857 | 0.88 | 0.83408 | 0.79735 | 0.74531 | 0.70755 | 0.64735 | 0.58306 | 0.52184 | 0.46163 | 0.33102 | 0.2698 | 0.17184 | 0.6249 | 0.58 | 0.51571 | 0.45551 | 0.37796 | 0.32184 | 0.23 | 0.13714 | 0.042245 | -0.04551
|  | COSHIEVILLE | HT |  |  |  |  | -0.032245 | -0.080204 | -0.13224 | -0.18735 | -0.25673 | -0.31694 | -0.39041 | -0.45776 | -0.54347 | -0.63224 | -0.91184 | -1.0455 | -1.0629 | 0.92898 | 0.90347 | 0.87388 | 0.84735 | 0.80449 | 0.77286 | 0.72694 | 0.69122 | 0.6402 | 0.5902 | 0.41061 | 0.33204 | 0.32286 | 0.65347 | 0.61061 | 0.56163 | 0.51469 | 0.44939 | 0.39531 | 0.32592 | 0.26776 | 0.1902 | 0.10857
|  | COSHIEVILLE | HE |  |  |  |  | -0.032245 | -0.07 | -0.11184 | -0.15265 | -0.20878 | -0.25776 | -0.3302 | -0.38735 | -0.4598 | -0.53224 | -0.86082 | -0.94653 | -0.95673 | 0.92898 | 0.90755 | 0.88 | 0.85551 | 0.82184 | 0.7902 | 0.74531 | 0.71061 | 0.66673 | 0.62082 | 0.40959 | 0.3198 | 0.22898 | 0.65347 | 0.61878 | 0.57898 | 0.54224 | 0.48918 | 0.44429 | 0.37796 | 0.32592 | 0.25959 | 0.19327
|  | COSHIEVILLE | CF |  |  |  |  | -0.028163 | -0.059796 | -0.092449 | -0.12102 | -0.1598 | -0.19041 | -0.23531 | -0.29245 | -0.32306 | -0.38633 | -0.65163 | -0.8302 | -0.95061 | 0.93102 | 0.91469 | 0.89224 | 0.8749 | 0.84939 | 0.82796 | 0.79735 | 0.75551 | 0.73714 | 0.69633 | 0.4902 | 0.29735 | 0.068776 | 0.65857 | 0.62796 | 0.59735 | 0.5698 | 0.53306 | 0.50245 | 0.45857 | 0.40347 | 0.37694 | 0.31878
| COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | NO | 7.396 | -4.1814 | -4.412 | -4.6569 | -4.9029 | -5.2467 | -5.6447 | -6.1324 | -6.5876 | -7.2018 | -8.1447 | -10.3457 | -11.5069 | -12.0824 | -2.2518 | -2.3967 | -2.559 | -2.7273 | -2.9539 | -3.2151 | -3.5039 | -3.7916 | -4.1916 | -4.8253 | -6.2345 | -6.8478 | -7.4916 | -3.8131 | -4.0212 | -4.2447 | -4.4712 | -4.7763 | -5.1253 | -5.562 | -5.9702 | -6.5335 | -7.3947
|  | COUPAR ANGUS | EE |  |  |  |  | -4.1814 | -4.412 | -4.6569 | -4.9029 | -5.2467 | -5.6447 | -6.1324 | -6.5876 | -7.1661 | -7.8916 | -10.2365 | -11.3018 | -11.9069 | -2.2518 | -2.3967 | -2.559 | -2.7273 | -2.9539 | -3.2151 | -3.5039 | -3.7916 | -4.1916 | -4.708 | -6.2345 | -6.8478 | -7.4284 | -3.8131 | -4.0212 | -4.2447 | -4.4712 | -4.7743 | -5.1253 | -5.562 | -5.9702 | -6.4988 | -7.162
|  | COUPAR ANGUS | HT |  |  |  |  | -4.158 | -4.3835 | -4.6131 | -4.8702 | -5.2396 | -5.608 | -6.0263 | -6.4865 | -7.2018 | -8.1447 | -10.3457 | -11.5069 | -12.0824 | -2.2324 | -2.3702 | -2.5161 | -2.6876 | -2.9202 | -3.1508 | -3.3988 | -3.6702 | -4.159 | -4.8253 | -6.1018 | -6.6467 | -6.9212 | -3.7947 | -4.0018 | -4.21 | -4.4488 | -4.7763 | -5.1039 | -5.4773 | -5.8865 | -6.5335 | -7.3947
|  | COUPAR ANGUS | HE |  |  |  |  | -4.1243 | -4.2937 | -4.458 | -4.6498 | -4.9284 | -5.2406 | -5.6702 | -6.0529 | -6.5886 | -7.2498 | -9.6671 | -10.7284 | -11.3661 | -2.212 | -2.3273 | -2.4437 | -2.5845 | -2.7763 | -2.9814 | -3.2467 | -3.4947 | -3.8641 | -4.3406 | -5.9712 | -6.5988 | -7.1722 | -3.7682 | -3.9192 | -4.0692 | -4.2447 | -4.4927 | -4.7641 | -5.1406 | -5.4784 | -5.959 | -6.558
|  | COUPAR ANGUS | CF |  |  |  |  | -4.0365 | -4.1243 | -4.2447 | -4.3549 | -4.5018 | -4.6824 | -4.8845 | -5.0876 | -5.3314 | -5.6631 | -7.6273 | -9.4937 | -10.6978 | -2.1447 | -2.208 | -2.2998 | -2.3804 | -2.4896 | -2.6233 | -2.7722 | -2.9243 | -3.1141 | -3.3702 | -4.8508 | -6.3324 | -7.4916 | -3.6876 | -3.7692 | -3.8743 | -3.9743 | -4.1069 | -4.2661 | -4.4416 | -4.6212 | -4.8386 | -5.1376
| CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | NO | 4.166 | 14.5056 | 14.1934 | 13.8465 | 13.5536 | 13.224 | 12.8801 | 12.3648 | 11.9128 | 11.3801 | 11.125 | 8.9883 | 7.7628 | 6.7367 | 15.5316 | 15.355 | 15.1265 | 14.951 | 14.7173 | 14.4714 | 14.1479 | 14.2142 | 13.9183 | 13.6928 | 12.8285 | 12.852 | 12.4601 | 14.3061 | 14.0387 | 13.7091 | 13.4459 | 13.1152 | 12.7703 | 12.2908 | 12.0469 | 11.5652 | 11.3591
|  | CRAIGIEBUCKLER | EE |  |  |  |  | 14.5056 | 14.1934 | 13.8465 | 13.5536 | 13.224 | 12.8801 | 12.3648 | 12.124 | 11.6352 | 11.1648 | 9.1975 | 7.871 | 6.7703 | 15.5316 | 15.355 | 15.1265 | 14.951 | 14.7173 | 14.4714 | 14.1479 | 14.2183 | 13.9408 | 13.6928 | 12.8285 | 12.852 | 12.4601 | 14.3061 | 14.0387 | 13.7091 | 13.4459 | 13.1152 | 12.7703 | 12.2908 | 12.2224 | 11.7805 | 11.3591
|  | CRAIGIEBUCKLER | HT |  |  |  |  | 14.5516 | 14.223 | 13.8761 | 13.5852 | 13.2608 | 12.9526 | 12.4485 | 11.9128 | 11.3801 | 11.125 | 8.9883 | 7.7628 | 6.7367 | 15.6152 | 15.452 | 15.2693 | 15.1203 | 14.9316 | 14.7785 | 14.5122 | 14.2142 | 13.9183 | 14.0142 | 12.9714 | 13.0734 | 12.9897 | 14.3938 | 14.1224 | 13.8152 | 13.554 | 13.2601 | 12.9826 | 12.5305 | 12.0469 | 11.5652 | 11.3642
|  | CRAIGIEBUCKLER | HE |  |  |  |  | 14.5659 | 14.3781 | 14.1669 | 14.0118 | 13.8261 | 13.6577 | 13.3516 | 13.0077 | 12.6699 | 12.6189 | 10.8281 | 9.3638 | 7.8938 | 15.6101 | 15.4918 | 15.3346 | 15.2275 | 15.0744 | 14.9591 | 14.751 | 14.504 | 14.2632 | 14.4234 | 13.3877 | 13.2908 | 12.8061 | 14.3979 | 14.2305 | 14.0183 | 13.8683 | 13.6663 | 13.501 | 13.2061 | 12.8612 | 12.5265 | 12.6173
|  | CRAIGIEBUCKLER | CF |  |  |  |  | 14.624 | 14.4985 | 14.3597 | 14.2679 | 14.1505 | 14.0271 | 13.9444 | 13.8067 | 13.6301 | 13.4444 | 12.6791 | 11.2659 | 9.1744 | 15.6336 | 15.5336 | 15.4142 | 15.3326 | 15.2122 | 15.0826 | 14.9999 | 14.8387 | 14.6826 | 14.5214 | 14.0642 | 13.6356 | 12.5693 | 14.4469 | 14.3193 | 14.1652 | 14.0652 | 13.9224 | 13.7673 | 13.6714 | 13.4856 | 13.3091 | 13.1254
| REDMOSS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | NO | 1.904 | 8.882 | 8.6473 | 8.3789 | 8.0902 | 7.7167 | 7.2891 | 6.6728 | 5.9442 | 5.2912 | 4.6718 | 2.2228 | 0.8422 | 0.29731 | 11.2912 | 11.0922 | 10.8626 | 10.6167 | 10.3371 | 10.0473 | 9.6769 | 9.2249 | 8.8198 | 8.4453 | 6.8585 | 6.0524 | 5.7412 | 9.8402 | 9.6861 | 9.5106 | 9.3228 | 9.0514 | 8.6667 | 8.1606 | 7.5483 | 6.9442 | 6.3667
|  | CRAIGINCHES | EE |  |  |  |  | 8.882 | 8.6473 | 8.3789 | 8.0902 | 7.7167 | 7.2891 | 6.6728 | 5.9442 | 5.2912 | 4.6718 | 2.2228 | 1.1218 | 0.90649 | 11.2912 | 11.0922 | 10.8626 | 10.6167 | 10.3371 | 10.0473 | 9.6769 | 9.2249 | 8.8198 | 8.4453 | 7.0912 | 6.6983 | 6.582 | 9.8402 | 9.6861 | 9.5106 | 9.3228 | 9.0514 | 8.6667 | 8.1606 | 7.5483 | 6.9442 | 6.3667
|  | CRAIGINCHES | HT |  |  |  |  | 8.9504 | 8.8034 | 8.6044 | 8.384 | 8.1381 | 7.7738 | 7.2147 | 6.581 | 5.9606 | 5.334 | 2.3677 | 0.8422 | 0.42792 | 11.3861 | 11.2381 | 11.0728 | 10.8902 | 10.6851 | 10.4442 | 10.1412 | 9.7738 | 9.4177 | 9.0534 | 7.3596 | 6.5749 | 6.3432 | 9.9055 | 9.7861 | 9.6575 | 9.5075 | 9.3504 | 9.1391 | 8.7014 | 8.1769 | 7.5973 | 7.0116
|  | CRAIGINCHES | HE |  |  |  |  | 8.9422 | 8.783 | 8.5922 | 8.3698 | 8.1198 | 7.7912 | 7.334 | 6.7238 | 6.1208 | 5.4902 | 2.383 | 0.85139 | 0.29731 | 11.3728 | 11.2096 | 11.0432 | 10.8493 | 10.6259 | 10.3718 | 10.0463 | 9.6432 | 9.2493 | 8.83 | 6.8585 | 6.0524 | 5.7412 | 9.8973 | 9.78 | 9.6575 | 9.5187 | 9.3626 | 9.1208 | 8.681 | 8.1483 | 7.6249 | 7.0749
|  | CRAIGINCHES | CF |  |  |  |  | 8.9932 | 8.9259 | 8.8259 | 8.6973 | 8.5473 | 8.3861 | 8.1942 | 7.9371 | 7.6575 | 7.3463 | 5.3483 | 3.28 | 1.5391 | 11.432 | 11.3453 | 11.2412 | 11.1259 | 10.9932 | 10.8453 | 10.6769 | 10.4463 | 10.234 | 9.9953 | 8.5177 | 7.0993 | 5.9738 | 9.9422 | 9.881 | 9.8055 | 9.7249 | 9.6289 | 9.5289 | 9.4106 | 9.2524 | 8.983 | 8.683
| CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | NO | NO | 1.177 | 4.3731 | 1.9986 | 0.92518 | -0.68707 | -2.1544 | -3.585 | -4.4473 | -5.3126 | -6.0718 | -6.7952 | -8.3514 | -9.0309 | -9.1973 | 6.1293 | 4.3813 | 3.3313 | 2.1476 | 1.2323 | 0.50477 | 0.0088531 | -0.47584 | -0.92992 | -1.3503 | -2.1626 | -2.4656 | -2.632 | 1.8701 | -0.29625 | -1.3136 | -2.6973 | -4.0085 | -5.2391 | -5.9554 | -6.6289 | -7.2758 | -7.8728
|  | CRAIGTON | EE |  |  |  |  | 4.4578 | 2.0884 | 1.0925 | -0.46462 | -1.9003 | -3.3718 | -4.3758 | -5.3126 | -5.8299 | -6.5616 | -8.286 | -8.9289 | -9.1401 | 6.2609 | 4.5282 | 3.614 | 2.5313 | 1.6252 | 0.81702 | 0.15069 | -0.42686 | -0.784 | -1.2391 | -2.1626 | -2.4656 | -2.632 | 1.9752 | -0.18502 | -1.0932 | -2.3585 | -3.6442 | -4.9483 | -5.8218 | -6.6105 | -7.0626 | -7.6718
|  | CRAIGTON | HT |  |  |  |  | 4.3731 | 1.9986 | 0.92518 | -0.68707 | -2.1544 | -3.585 | -4.4473 | -5.2769 | -6.0718 | -6.7952 | -8.3514 | -9.0309 | -9.1973 | 6.1293 | 4.3813 | 3.3313 | 2.1476 | 1.2323 | 0.50477 | 0.0088531 | -0.47584 | -0.92992 | -1.3503 | -2.1126 | -2.436 | -2.5136 | 1.8701 | -0.29625 | -1.3136 | -2.6973 | -4.0085 | -5.2391 | -5.9554 | -6.6289 | -7.2758 | -7.8728
|  | CRAIGTON | HE |  |  |  |  | 4.5058 | 2.1731 | 1.267 | -0.059514 | -1.4075 | -2.7707 | -3.5728 | -4.3207 | -5.0034 | -5.6452 | -7.136 | -7.9391 | -8.4126 | 6.2925 | 4.5884 | 3.6976 | 2.6578 | 1.7691 | 0.99559 | 0.43947 | -0.042167 | -0.47482 | -0.89319 | -1.8871 | -2.2493 | -2.4156 | 2.0099 | -0.1136 | -0.99727 | -2.0422 | -3.2565 | -4.4514 | -5.1462 | -5.7646 | -6.3218 | -6.8401
|  | CRAIGTON | CF |  |  |  |  | 4.8915 | 2.7507 | 2.0313 | 1.1027 | 0.048649 | -1.0952 | -1.8524 | -2.5616 | -3.2462 | -3.9299 | -6.3524 | -7.2565 | -7.6279 | 6.7558 | 5.2609 | 4.5691 | 3.8578 | 3.1793 | 2.4935 | 1.9456 | 1.4242 | 0.94661 | 0.46804 | -1.085 | -1.9187 | -2.2697 | 2.4038 | 0.466 | -0.23502 | -0.95441 | -1.7065 | -2.7187 | -3.3748 | -3.9881 | -4.5718 | -5.1483
| BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 2.375 | 14.7447 | 14.3223 | 13.8396 | 13.3478 | 12.806 | 12.2243 | 11.5335 | 11.1672 | 10.5233 | 9.9233 | 7.6886 | 6.3876 | 4.9447 | 16.7356 | 16.4907 | 16.206 | 15.9203 | 15.5958 | 15.2407 | 14.8345 | 14.6662 | 14.2896 | 13.9386 | 12.5703 | 12.3345 | 11.4601 | 16.3254 | 15.9488 | 15.5172 | 15.0825 | 14.5937 | 14.0733 | 13.4509 | 13.1315 | 12.555 | 12.0141
|  | CRIEFF | EE |  |  |  |  | 14.7447 | 14.3223 | 13.8396 | 13.3478 | 12.806 | 12.2243 | 11.5335 | 11.1672 | 10.5233 | 9.9233 | 7.6886 | 6.5152 | 5.007 | 16.7356 | 16.4907 | 16.206 | 15.9203 | 15.5958 | 15.2407 | 14.8345 | 14.6662 | 14.2896 | 13.9386 | 12.5703 | 12.3345 | 11.5692 | 16.3254 | 15.9488 | 15.5172 | 15.0825 | 14.5937 | 14.0733 | 13.4509 | 13.1315 | 12.555 | 12.0141
|  | CRIEFF | HT |  |  |  |  | 14.8356 | 14.4284 | 13.9886 | 13.5417 | 13.0478 | 12.556 | 11.9672 | 11.3305 | 10.706 | 10.058 | 7.7958 | 6.3876 | 4.9447 | 16.806 | 16.5784 | 16.3366 | 16.0866 | 15.8101 | 15.5366 | 15.2152 | 14.857 | 14.5039 | 14.1335 | 12.9835 | 12.8937 | 12.7652 | 16.4019 | 16.0447 | 15.6458 | 15.2407 | 14.7958 | 14.355 | 13.8213 | 13.2478 | 12.6845 | 12.0968
|  | CRIEFF | HE |  |  |  |  | 14.8519 | 14.5478 | 14.2213 | 13.8845 | 13.505 | 13.0968 | 12.6856 | 12.1998 | 11.7284 | 11.2468 | 9.2947 | 8.0345 | 6.3478 | 16.8101 | 16.6254 | 16.4223 | 16.2152 | 15.9784 | 15.7192 | 15.4682 | 15.1611 | 14.8621 | 14.5509 | 13.3366 | 13.0335 | 12.2141 | 16.4203 | 16.155 | 15.8641 | 15.5621 | 15.2223 | 14.855 | 14.4886 | 14.056 | 13.6345 | 13.2039
|  | CRIEFF | CF |  |  |  |  | 14.956 | 14.7345 | 14.4947 | 14.2274 | 13.9937 | 13.705 | 13.4529 | 13.206 | 12.9417 | 12.6662 | 11.3447 | 9.7998 | 7.456 | 16.8784 | 16.7396 | 16.5845 | 16.4152 | 16.259 | 16.0652 | 15.8774 | 15.6917 | 15.4866 | 15.2723 | 14.2192 | 13.2815 | 11.4601 | 16.5141 | 16.3233 | 16.1172 | 15.8825 | 15.6743 | 15.4152 | 15.1937 | 14.9815 | 14.7478 | 14.5039
| PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 0.079 | 0.21122 | 0.18367 | 0.14592 | 0.12245 | 0.093878 | 0.054082 | 0.0081633 | -0.040816 | -0.096939 | -0.1449 | -0.24898 | -0.27449 | -0.28367 | 0.18673 | 0.17143 | 0.15 | 0.13776 | 0.12041 | 0.093878 | 0.060204 | 0.033673 | -0.010204 | -0.043878 | -0.091837 | -0.09898 | -0.12857 | 0.12959 | 0.10816 | 0.078571 | 0.061224 | 0.038776 | 0.0061224 | -0.032653 | -0.067347 | -0.11531 | -0.15204
|  | CRINAN | EE |  |  |  |  | 0.21122 | 0.18367 | 0.14592 | 0.12245 | 0.093878 | 0.054082 | 0.0081633 | -0.040816 | -0.096939 | -0.1449 | -0.24898 | -0.26429 | -0.27245 | 0.18673 | 0.17143 | 0.15 | 0.13776 | 0.12041 | 0.093878 | 0.060204 | 0.033673 | -0.010204 | -0.043878 | -0.091837 | -0.09898 | -0.1051 | 0.12959 | 0.10816 | 0.078571 | 0.061224 | 0.038776 | 0.0061224 | -0.032653 | -0.067347 | -0.11531 | -0.15204
|  | CRINAN | HT |  |  |  |  | 0.22245 | 0.20408 | 0.17755 | 0.15306 | 0.12143 | 0.10408 | 0.047959 | 0.0061224 | -0.040816 | -0.084694 | -0.21531 | -0.27449 | -0.28367 | 0.19592 | 0.18673 | 0.17347 | 0.16224 | 0.14286 | 0.13571 | 0.09898 | 0.073469 | 0.042857 | 0.011224 | -0.070408 | -0.092857 | -0.097959 | 0.14082 | 0.12959 | 0.10918 | 0.091837 | 0.068367 | 0.056122 | 0.011224 | -0.021429 | -0.055102 | -0.090816
|  | CRINAN | HE |  |  |  |  | 0.22245 | 0.20816 | 0.18571 | 0.16735 | 0.14184 | 0.12653 | 0.094898 | 0.055102 | 0.012245 | -0.029592 | -0.19286 | -0.23265 | -0.2398 | 0.19592 | 0.1898 | 0.17449 | 0.16429 | 0.14796 | 0.14184 | 0.12245 | 0.095918 | 0.062245 | 0.029592 | -0.069388 | -0.091837 | -0.095918 | 0.14082 | 0.13163 | 0.11224 | 0.096939 | 0.077551 | 0.068367 | 0.040816 | 0.0061224 | -0.027551 | -0.064286
|  | CRINAN | CF |  |  |  |  | 0.22653 | 0.21429 | 0.19694 | 0.18367 | 0.1602 | 0.15 | 0.12959 | 0.10408 | 0.086735 | 0.056122 | -0.072449 | -0.18878 | -0.23776 | 0.19796 | 0.1949 | 0.18367 | 0.17653 | 0.16122 | 0.15918 | 0.1449 | 0.12653 | 0.11531 | 0.094898 | -0.0010204 | -0.084694 | -0.12857 | 0.1449 | 0.13673 | 0.12449 | 0.11429 | 0.096939 | 0.089796 | 0.073469 | 0.053061 | 0.036735 | 0.015306
| PORT ANN | CROMALT | MINIMUM HEADROOM | NN 08395 07755 | YES | YES | 0 | 2.1755 | 2.1571 | 2.1327 | 2.1531 | 2.1276 | 2.0959 | 2.0612 | 2 | 1.9429 | 1.8888 | 1.6541 | 1.5857 | 1.2842 | 2.2189 | 2.2077 | 2.4684 | 2.4469 | 2.4347 | 2.4061 | 2.3878 | 2.3418 | 2.3 | 2.2653 | 2.0929 | 1.8814 | 1.8559 | 2.2089 | 2.3541 | 2.3347 | 2.3041 | 2.2867 | 2.2551 | 2.2265 | 2.1694 | 2.1143 | 2.0633
|  | CROMALT | EE |  |  |  |  | 2.1755 | 2.1571 | 2.1327 | 2.1531 | 2.1276 | 2.0959 | 2.0612 | 2 | 1.9469 | 1.9031 | 1.7837 | 1.7551 | 1.477 | 2.2189 | 2.2077 | 2.4684 | 2.4469 | 2.4347 | 2.4061 | 2.3878 | 2.3418 | 2.3 | 2.2653 | 2.1898 | 1.9916 | 1.9497 | 2.2089 | 2.3541 | 2.3347 | 2.3041 | 2.2867 | 2.2551 | 2.2265 | 2.1694 | 2.1194 | 2.0745
|  | CROMALT | HT |  |  |  |  | 2.1898 | 2.1735 | 2.1551 | 2.1847 | 2.1643 | 2.1388 | 2.0908 | 2.0398 | 2.001 | 1.9653 | 1.8316 | 1.7755 | 1.4821 | 2.2291 | 2.2189 | 2.4837 | 2.4684 | 2.4561 | 2.4388 | 2.402 | 2.3684 | 2.3347 | 2.3163 | 2.2276 | 2.0283 | 2.0202 | 2.2222 | 2.3714 | 2.3541 | 2.3347 | 2.3153 | 2.2898 | 2.25 | 2.2041 | 2.1643 | 2.1378
|  | CROMALT | HE |  |  |  |  | 2.1827 | 2.1602 | 2.1378 | 2.1643 | 2.1378 | 2.102 | 2.0684 | 2.002 | 1.9429 | 1.8888 | 1.6541 | 1.5857 | 1.3087 | 2.2291 | 2.2179 | 2.4837 | 2.4704 | 2.4602 | 2.4388 | 2.4133 | 2.3571 | 2.3082 | 2.2694 | 2.0929 | 1.8814 | 1.8814 | 2.2212 | 2.3714 | 2.352 | 2.3276 | 2.302 | 2.2704 | 2.2367 | 2.1714 | 2.1143 | 2.0633
|  | CROMALT | CF |  |  |  |  | 2.1908 | 2.1776 | 2.1663 | 2.199 | 2.1786 | 2.1602 | 2.1378 | 2.1082 | 2.0796 | 2.0429 | 1.8418 | 1.6724 | 1.2842 | 2.2311 | 2.223 | 2.4918 | 2.4837 | 2.4694 | 2.4622 | 2.4459 | 2.4286 | 2.4153 | 2.3867 | 2.2296 | 1.9375 | 1.8559 | 2.2242 | 2.3745 | 2.3684 | 2.3541 | 2.3357 | 2.3255 | 2.3041 | 2.2735 | 2.248 | 2.2133
| ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | NO | 4.128 | 4.8906 | 4.5416 | 4.1926 | 3.8467 | 3.4906 | 2.8273 | 2.1324 | 1.3967 | 0.71913 | 0.089539 | -1.5839 | -2.6023 | -3.5431 | 5.7242 | 5.4314 | 5.2048 | 4.9712 | 4.7304 | 4.4824 | 4.1967 | 3.8712 | 3.5936 | 3.313 | 2.3691 | 2.1217 | 1.5105 | 5.6717 | 5.3074 | 5.0156 | 4.6768 | 4.3268 | 3.7911 | 3.187 | 2.5339 | 1.9309 | 1.3615
|  | CROSSHILLS | EE |  |  |  |  | 4.8906 | 4.5416 | 4.2375 | 3.8804 | 3.5099 | 3.114 | 2.6395 | 1.8497 | 1.3406 | 0.63342 | -1.4656 | -2.4747 | -3.4482 | 5.7355 | 5.4477 | 5.2161 | 4.9712 | 4.7304 | 4.4916 | 4.2426 | 3.8712 | 3.662 | 3.361 | 2.3691 | 2.1217 | 1.5737 | 5.6717 | 5.3074 | 5.0227 | 4.6768 | 4.3268 | 3.9431 | 3.4839 | 2.7605 | 2.4074 | 1.787
|  | CROSSHILLS | HT |  |  |  |  | 4.9008 | 4.5446 | 4.1926 | 3.8467 | 3.4906 | 2.8273 | 2.1324 | 1.3967 | 0.71913 | 0.089539 | -1.5839 | -2.6023 | -3.5431 | 5.7242 | 5.4314 | 5.2048 | 4.9824 | 4.7834 | 4.4824 | 4.1967 | 3.8793 | 3.5936 | 3.313 | 2.5416 | 2.486 | 2.3931 | 5.6839 | 5.3145 | 5.0156 | 4.687 | 4.3686 | 3.7911 | 3.187 | 2.5339 | 1.9309 | 1.3615
|  | CROSSHILLS | HE |  |  |  |  | 4.9467 | 4.6395 | 4.414 | 4.2079 | 3.9936 | 3.712 | 3.4314 | 2.9304 | 2.4385 | 1.9467 | -0.079849 | -1.3666 | -2.5635 | 5.7702 | 5.512 | 5.3171 | 5.1385 | 4.9426 | 4.7416 | 4.5559 | 4.2814 | 4.0191 | 3.7518 | 2.7477 | 2.587 | 1.9798 | 5.7278 | 5.4125 | 5.1768 | 4.9543 | 4.736 | 4.4809 | 4.2125 | 3.8105 | 3.3747 | 2.9278
|  | CROSSHILLS | CF |  |  |  |  | 5.1028 | 4.9314 | 4.7834 | 4.6508 | 4.4987 | 4.3334 | 4.1875 | 4.0171 | 3.7283 | 3.3987 | 1.815 | 0.32219 | -1.487 | 5.911 | 5.7599 | 5.6375 | 5.5365 | 5.411 | 5.2753 | 5.1497 | 4.9987 | 4.8191 | 4.6242 | 3.6681 | 2.8676 | 1.5105 | 5.8921 | 5.7145 | 5.5605 | 5.4237 | 5.2696 | 5.0962 | 4.9564 | 4.788 | 4.5472 | 4.2482
| KEITH 1 | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 0.277 | 6.0571 | 5.9194 | 5.7459 | 5.5449 | 5.3653 | 5.1612 | 4.8663 | 4.5918 | 4.3102 | 4.0469 | 3.0592 | 2.4531 | 1.6709 | 6.273 | 6.1934 | 6.0954 | 5.9699 | 5.8709 | 5.7393 | 5.5719 | 5.4087 | 5.2311 | 5.075 | 4.5372 | 4.5411 | 4.1962 | 6.237 | 6.1084 | 5.9543 | 5.7584 | 5.5982 | 5.3952 | 5.1176 | 4.8666 | 4.5952 | 4.3462
|  | CULLEN | EE |  |  |  |  | 6.0571 | 5.9194 | 5.7541 | 5.5449 | 5.3653 | 5.1612 | 4.8663 | 4.5918 | 4.3102 | 4.0469 | 3.0592 | 2.5051 | 1.7128 | 6.273 | 6.1934 | 6.0954 | 5.9699 | 5.8709 | 5.7393 | 5.5719 | 5.4087 | 5.2311 | 5.075 | 4.5372 | 4.5411 | 4.2421 | 6.237 | 6.1084 | 5.9543 | 5.7584 | 5.5982 | 5.3952 | 5.1176 | 4.8666 | 4.5952 | 4.3462
|  | CULLEN | HT |  |  |  |  | 6.0684 | 5.9316 | 5.7459 | 5.5653 | 5.3806 | 5.1969 | 4.9429 | 4.6776 | 4.4265 | 4.1745 | 3.0745 | 2.4531 | 1.6709 | 6.2995 | 6.2342 | 6.1332 | 6.0444 | 5.9485 | 5.8464 | 5.7168 | 5.5679 | 5.427 | 5.2862 | 4.6985 | 4.7543 | 4.7094 | 6.2574 | 6.136 | 5.9758 | 5.8176 | 5.6523 | 5.4839 | 5.2543 | 5.0115 | 4.7798 | 4.5472
|  | CULLEN | HE |  |  |  |  | 6.0898 | 6.0082 | 5.8918 | 5.75 | 5.6163 | 5.4673 | 5.3 | 5.1071 | 4.9255 | 4.7449 | 3.7724 | 3.1684 | 2.2444 | 6.3056 | 6.2587 | 6.1811 | 6.1036 | 6.024 | 5.9281 | 5.8393 | 5.7077 | 5.5852 | 5.4648 | 4.8546 | 4.8166 | 4.486 | 6.2727 | 6.2003 | 6.0931 | 5.9696 | 5.8472 | 5.7064 | 5.5615 | 5.3737 | 5.1992 | 5.0166
|  | CULLEN | CF |  |  |  |  | 6.1255 | 6.0806 | 6.0224 | 5.9571 | 5.8684 | 5.7878 | 5.6786 | 5.5714 | 5.4714 | 5.3622 | 4.7755 | 4.0541 | 2.8015 | 6.327 | 6.2954 | 6.2526 | 6.2087 | 6.1423 | 6.0821 | 5.9995 | 5.9281 | 5.8485 | 5.7566 | 5.2628 | 4.9309 | 4.1962 | 6.3054 | 6.2615 | 6.2064 | 6.1462 | 6.0605 | 5.9819 | 5.8809 | 5.7829 | 5.6778 | 5.5676
| INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | NO | 3.889 | 7.6349 | 16.4727 | 15.638 | 14.738 | 13.842 | 13.1553 | 12.191 | 11.2972 | 10.3135 | 9.6318 | 6.8043 | 5.1492 | -4.7528 | 19.2635 | 18.8614 | 18.4318 | 17.9625 | 17.4839 | 17.2696 | 16.7686 | 16.2135 | 15.6737 | 15.2859 | 13.8451 | 4.7267 | 12.1767 | 18.4757 | 17.8186 | 17.1002 | 16.3074 | 15.5033 | 15.0829 | 14.2482 | 13.342 | 12.4635 | 11.84
|  | CULLODEN | EE |  |  |  |  | 7.6349 | 16.4727 | 15.638 | 14.738 | 13.842 | 13.2451 | 12.2961 | 11.2972 | 10.3135 | 9.6318 | 7.0002 | 5.388 | -4.5937 | 19.2635 | 18.8614 | 18.4318 | 17.9625 | 17.4839 | 17.2696 | 16.7686 | 16.2135 | 15.6737 | 15.2859 | 13.8451 | 4.7267 | 12.5778 | 18.4757 | 17.8186 | 17.1002 | 16.3074 | 15.5033 | 15.0829 | 14.2482 | 13.342 | 12.4635 | 11.84
|  | CULLODEN | HT |  |  |  |  | 7.7267 | 16.5778 | 15.7553 | 14.8829 | 14.0757 | 13.1553 | 12.191 | 11.5084 | 10.5747 | 9.89 | 6.8043 | 5.1492 | -4.7528 | 19.3533 | 18.9869 | 18.5992 | 18.1778 | 17.8074 | 17.3604 | 16.8931 | 16.6543 | 16.2063 | 15.8747 | 14.2706 | 5.4012 | 14.1165 | 18.6012 | 17.9778 | 17.3043 | 16.5655 | 15.889 | 15.0961 | 14.2584 | 13.7839 | 12.9788 | 12.3563
|  | CULLODEN | HE |  |  |  |  | 7.7431 | 16.7594 | 16.1125 | 15.4094 | 14.7747 | 14.041 | 13.3165 | 12.8839 | 12.1859 | 11.7441 | 9.1114 | 7.3227 | -3.0386 | 19.3492 | 19.0359 | 18.6982 | 18.3318 | 18.0104 | 17.6247 | 17.2288 | 17.0665 | 16.69 | 16.4114 | 14.7563 | 5.491 | 13.2461 | 18.6114 | 18.1176 | 17.5798 | 16.9778 | 16.4359 | 15.79 | 15.1441 | 14.8563 | 14.2431 | 13.8104
|  | CULLODEN | CF |  |  |  |  | 7.9584 | 17.1869 | 16.64 | 16.0206 | 15.5257 | 14.9523 | 14.4869 | 13.9706 | 13.7869 | 13.5451 | 11.8533 | 9.7747 | -1.4957 | 19.4543 | 19.241 | 18.94 | 18.6043 | 18.339 | 18.0165 | 17.7206 | 17.3869 | 17.3165 | 17.1216 | 15.792 | 5.7359 | 12.1767 | 18.7859 | 18.4655 | 18.0196 | 17.4982 | 17.0788 | 16.5829 | 16.1635 | 15.6839 | 15.6206 | 15.3727
| CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | NO | 1.088 | 4.5969 | 4.1663 | 3.7653 | 3.3204 | 2.8776 | 2.4061 | 1.9286 | 1.3857 | 1.2347 | 0.71837 | -0.93571 | -2.0612 | -2.2602 | 6.8969 | 6.6633 | 6.4439 | 6.2 | 5.9735 | 5.7102 | 5.4449 | 5.1347 | 5.1194 | 4.8827 | 3.9214 | 3.2469 | 2.4367 | 5.6153 | 5.2459 | 4.8939 | 4.4929 | 4.102 | 3.6704 | 3.2286 | 2.7245 | 2.6194 | 2.1663
|  | CULTER | EE |  |  |  |  | 4.5969 | 4.1663 | 3.7653 | 3.3204 | 2.8776 | 2.4061 | 1.9286 | 1.3857 | 1.2469 | 0.81224 | -0.89082 | -1.9235 | -2.1867 | 6.8969 | 6.6633 | 6.4439 | 6.2 | 5.9735 | 5.7102 | 5.4449 | 5.1347 | 5.1194 | 4.8827 | 3.9214 | 3.2469 | 2.651 | 5.6153 | 5.2459 | 4.8939 | 4.4929 | 4.102 | 3.6704 | 3.2286 | 2.7245 | 2.6194 | 2.2204
|  | CULTER | HT |  |  |  |  | 4.6745 | 4.2755 | 3.8745 | 3.4908 | 3.052 | 2.6163 | 2.2041 | 1.7204 | 1.2347 | 0.71837 | -0.93571 | -2.0612 | -2.2602 | 6.9571 | 6.7612 | 6.5612 | 6.3755 | 6.1551 | 5.9347 | 5.7337 | 5.4816 | 5.2316 | 4.9602 | 4.1857 | 3.648 | 3.5551 | 5.6949 | 5.3571 | 5.0051 | 4.6724 | 4.2827 | 3.8908 | 3.5204 | 3.0765 | 2.6337 | 2.1663
|  | CULTER | HE |  |  |  |  | 4.6776 | 4.3796 | 4.0816 | 3.7888 | 3.448 | 3.1092 | 2.8582 | 2.5143 | 2.1684 | 1.8051 | 0.34388 | -0.85102 | -1.3112 | 6.9531 | 6.7867 | 6.6173 | 6.4561 | 6.2694 | 6.0765 | 5.9327 | 5.7255 | 5.5112 | 5.2878 | 4.4235 | 3.6245 | 2.9643 | 5.6959 | 5.4449 | 5.1867 | 4.9306 | 4.6286 | 4.3235 | 4.0898 | 3.7704 | 3.448 | 3.1143
|  | CULTER | CF |  |  |  |  | 4.7388 | 4.5041 | 4.2847 | 4.0337 | 3.8143 | 3.5684 | 3.4337 | 3.3102 | 3.15 | 2.9816 | 2.0449 | 0.78571 | -0.30204 | 6.9806 | 6.8469 | 6.7143 | 6.5643 | 6.4357 | 6.2857 | 6.1765 | 6.0765 | 5.9449 | 5.8102 | 5.1071 | 3.9327 | 2.4367 | 5.7541 | 5.5582 | 5.3704 | 5.151 | 4.9592 | 4.7388 | 4.6092 | 4.4929 | 4.3378 | 4.1755
| ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 4.356 | 5.8641 | 5.7212 | 5.5651 | 5.3386 | 4.8916 | 4.6886 | 4.1549 | 3.8457 | 3.8396 | 3.5723 | 2.1508 | 0.85491 | -0.53285 | 9.1274 | 9.0539 | 8.96 | 8.8335 | 8.3906 | 8.2845 | 7.8263 | 7.6192 | 7.5518 | 7.3365 | 6.3702 | 6.1687 | 5.483 | 6.8503 | 6.7391 | 6.5983 | 6.4105 | 5.9024 | 5.7411 | 5.2034 | 4.9789 | 4.8636 | 4.4707
|  | CUMMING STREET | EE |  |  |  |  | 5.8641 | 5.7212 | 5.5651 | 5.3386 | 4.8916 | 4.6886 | 4.1549 | 3.8457 | 3.8682 | 3.6365 | 2.2345 | 0.94674 | -0.47571 | 9.1274 | 9.0539 | 8.96 | 8.8335 | 8.3906 | 8.2845 | 7.8263 | 7.6192 | 7.5518 | 7.3365 | 6.3702 | 6.1687 | 5.5248 | 6.8503 | 6.7391 | 6.5983 | 6.4105 | 5.9024 | 5.7411 | 5.2034 | 4.9789 | 4.8636 | 4.4707
|  | CUMMING STREET | HT |  |  |  |  | 5.909 | 5.7845 | 5.6284 | 5.412 | 4.9916 | 4.8212 | 4.3192 | 4.0937 | 3.8396 | 3.5723 | 2.1508 | 0.85491 | -0.53285 | 9.1661 | 9.1059 | 9.0233 | 8.911 | 8.4927 | 8.4151 | 7.9896 | 7.861 | 7.6723 | 7.4763 | 6.6427 | 6.6238 | 6.5187 | 6.8932 | 6.8024 | 6.6687 | 6.4932 | 6.0166 | 5.8952 | 5.4013 | 5.236 | 5.0115 | 4.5809
|  | CUMMING STREET | HE |  |  |  |  | 5.9161 | 5.8314 | 5.7314 | 5.5692 | 5.1896 | 5.0651 | 4.6498 | 4.509 | 4.3386 | 4.161 | 3.4447 | 2.1743 | 0.45287 | 9.162 | 9.108 | 9.0345 | 8.9314 | 8.5151 | 8.4365 | 8.011 | 7.9131 | 7.8069 | 7.6916 | 6.9488 | 6.6819 | 5.9575 | 6.8911 | 6.8156 | 6.7095 | 6.5595 | 6.0901 | 5.9768 | 5.4983 | 5.3493 | 5.1922 | 5.0238
|  | CUMMING STREET | CF |  |  |  |  | 5.9355 | 5.8865 | 5.8233 | 5.7202 | 5.3692 | 5.3131 | 4.9814 | 4.8896 | 4.8437 | 4.7631 | 4.1661 | 3.7488 | 1.8539 | 9.1794 | 9.1427 | 9.0947 | 9.0243 | 8.6325 | 8.5876 | 8.2008 | 8.1263 | 8.0723 | 8.0039 | 7.4712 | 7.0717 | 5.483 | 6.9146 | 6.8707 | 6.8044 | 6.7075 | 6.2819 | 6.2228 | 5.8075 | 5.7115 | 5.6401 | 5.5503
| ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | YES | 0.652 | 5.0629 | 4.9547 | 4.8424 | 4.7078 | 4.5567 | 4.4271 | 4.2394 | 4.0506 | 3.871 | 3.7435 | 3.1598 | 2.8098 | 2.2086 | 5.2463 | 5.1851 | 5.1239 | 5.0422 | 4.9473 | 4.878 | 4.7678 | 4.6463 | 4.5341 | 4.4739 | 4.1545 | 4.2204 | 4.001 | 5.1827 | 5.0837 | 4.9837 | 4.8571 | 4.7163 | 4.602 | 4.4296 | 4.2449 | 4.0755 | 3.9633
|  | DALCHONZIE | EE |  |  |  |  | 5.0629 | 4.9547 | 4.8424 | 4.7078 | 4.5567 | 4.4271 | 4.2394 | 4.0506 | 3.871 | 3.7435 | 3.1598 | 2.8322 | 2.2178 | 5.2463 | 5.1851 | 5.1239 | 5.0422 | 4.9473 | 4.878 | 4.7678 | 4.6463 | 4.5341 | 4.4739 | 4.1545 | 4.2204 | 4.0347 | 5.1827 | 5.0837 | 4.9837 | 4.8571 | 4.7163 | 4.602 | 4.4296 | 4.2449 | 4.0755 | 3.9633
|  | DALCHONZIE | HT |  |  |  |  | 5.0945 | 4.9853 | 4.8659 | 4.7261 | 4.5976 | 4.4822 | 4.3292 | 4.1649 | 4.0373 | 3.8761 | 3.1792 | 2.8098 | 2.2086 | 5.281 | 5.2269 | 5.1657 | 5.0922 | 5.031 | 4.9678 | 4.8841 | 4.7902 | 4.732 | 4.6402 | 4.2606 | 4.3592 | 4.3296 | 5.2143 | 5.1204 | 5.0143 | 4.8929 | 4.7816 | 4.6745 | 4.5347 | 4.3816 | 4.2684 | 4.1173
|  | DALCHONZIE | HE |  |  |  |  | 5.0976 | 5.0271 | 4.9465 | 4.8435 | 4.7516 | 4.6496 | 4.5322 | 4.4108 | 4.3302 | 4.2139 | 3.5976 | 3.2414 | 2.5586 | 5.279 | 5.2382 | 5.1882 | 5.1259 | 5.0759 | 5.0127 | 4.9402 | 4.8565 | 4.8127 | 4.73 | 4.3494 | 4.3898 | 4.1888 | 5.2163 | 5.1561 | 5.0837 | 4.9908 | 4.9102 | 4.8153 | 4.7041 | 4.5867 | 4.5133 | 4.401
|  | DALCHONZIE | CF |  |  |  |  | 5.1149 | 5.0771 | 5.021 | 4.97 | 4.9016 | 4.8547 | 4.7843 | 4.7016 | 4.6363 | 4.5965 | 4.1761 | 3.7424 | 2.8586 | 5.2871 | 5.2606 | 5.2198 | 5.1851 | 5.1382 | 5.1065 | 5.0565 | 4.9912 | 4.9361 | 4.9055 | 4.5616 | 4.452 | 4.001 | 5.2337 | 5.199 | 5.1459 | 5.099 | 5.0316 | 4.9929 | 4.9265 | 4.8469 | 4.7816 | 4.7469
| NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 3.269 | 7.9818 | 7.6808 | 7.3227 | 6.9012 | 6.3982 | 5.7788 | 5.2573 | 4.7084 | 4.19 | 3.9982 | 3.4594 | 3.3104 | 2.5114 | 8.3614 | 8.2124 | 8.038 | 7.8369 | 7.6094 | 7.3543 | 7.1227 | 6.8339 | 6.5788 | 6.4471 | 6.088 | 6.3374 | 6.0977 | 8.3007 | 8.0589 | 7.767 | 7.4181 | 7.0079 | 6.5181 | 6.0987 | 5.6528 | 5.2293 | 5.0436
|  | DALCROSS | EE |  |  |  |  | 7.9818 | 7.6808 | 7.3227 | 6.9012 | 6.3982 | 5.8206 | 5.3665 | 4.791 | 4.2522 | 4.0227 | 3.4594 | 3.3471 | 2.5716 | 8.3614 | 8.2124 | 8.038 | 7.8369 | 7.6094 | 7.3543 | 7.1227 | 6.8339 | 6.5788 | 6.4471 | 6.088 | 6.3374 | 6.2252 | 8.3007 | 8.0589 | 7.767 | 7.4181 | 7.0079 | 6.5323 | 6.1589 | 5.6823 | 5.2466 | 5.0436
|  | DALCROSS | HT |  |  |  |  | 8.0053 | 7.7063 | 7.3584 | 6.9522 | 6.4543 | 5.7788 | 5.2573 | 4.7084 | 4.19 | 3.9982 | 3.5369 | 3.3104 | 2.5114 | 8.3849 | 8.2359 | 8.0747 | 7.89 | 7.6686 | 7.3706 | 7.1288 | 6.8594 | 6.6022 | 6.492 | 6.1818 | 6.415 | 6.3854 | 8.3252 | 8.0844 | 7.8038 | 7.4711 | 7.067 | 6.5181 | 6.0987 | 5.6528 | 5.2293 | 5.0609
|  | DALCROSS | HE |  |  |  |  | 8.0063 | 7.7196 | 7.389 | 7.0053 | 6.5124 | 5.9563 | 5.5502 | 5.0553 | 4.5522 | 4.3829 | 3.5798 | 3.442 | 2.6645 | 8.3818 | 8.242 | 8.0839 | 7.9094 | 7.6869 | 7.44 | 7.2461 | 7.0022 | 6.7482 | 6.6441 | 6.1635 | 6.4048 | 6.2936 | 8.3262 | 8.0966 | 7.8313 | 7.5211 | 7.1211 | 6.664 | 6.3354 | 5.9323 | 5.5211 | 5.3691
|  | DALCROSS | CF |  |  |  |  | 8.1002 | 7.9145 | 7.6247 | 7.2849 | 6.8706 | 6.3941 | 6.0114 | 5.6278 | 5.1727 | 4.9951 | 4.3043 | 3.7971 | 2.691 | 8.4308 | 8.34 | 8.1992 | 8.0329 | 7.8492 | 7.6308 | 7.4451 | 7.2563 | 7.0359 | 6.938 | 6.5104 | 6.4854 | 6.0977 | 8.3977 | 8.2497 | 8.0221 | 7.7507 | 7.4191 | 7.0354 | 6.7313 | 6.4252 | 6.0599 | 5.9089
| TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0.011 | 0.82143 | 0.81224 | 0.80408 | 0.79592 | 0.78469 | 0.77245 | 0.76429 | 0.74694 | 0.72857 | 0.73061 | 0.7051 | 0.7 | 0.69592 | 0.88163 | 0.87347 | 0.87347 | 0.87041 | 0.86224 | 0.85408 | 0.84694 | 0.83367 | 0.82347 | 0.82449 | 0.8051 | 0.78878 | 0.75102 | 0.86224 | 0.85306 | 0.8449 | 0.83776 | 0.82857 | 0.81429 | 0.80714 | 0.79082 | 0.77551 | 0.77653
|  | DALMALLY | EE |  |  |  |  | 0.82143 | 0.81224 | 0.80408 | 0.79592 | 0.78469 | 0.77245 | 0.76429 | 0.74694 | 0.72857 | 0.73061 | 0.7051 | 0.7 | 0.69694 | 0.88367 | 0.88061 | 0.87347 | 0.87041 | 0.86224 | 0.85408 | 0.84694 | 0.83367 | 0.82347 | 0.82449 | 0.8051 | 0.79592 | 0.77653 | 0.86224 | 0.85408 | 0.8449 | 0.83776 | 0.82857 | 0.81429 | 0.80714 | 0.79082 | 0.77551 | 0.77653
|  | DALMALLY | HT |  |  |  |  | 0.82347 | 0.81224 | 0.8102 | 0.80306 | 0.79592 | 0.79184 | 0.78367 | 0.77041 | 0.76429 | 0.75 | 0.71429 | 0.7 | 0.69592 | 0.88163 | 0.87959 | 0.87857 | 0.87449 | 0.87143 | 0.86837 | 0.86224 | 0.8551 | 0.85204 | 0.84184 | 0.81837 | 0.8102 | 0.80816 | 0.86429 | 0.85306 | 0.85306 | 0.8449 | 0.83878 | 0.83367 | 0.82653 | 0.81327 | 0.8102 | 0.79592
|  | DALMALLY | HE |  |  |  |  | 0.82347 | 0.81429 | 0.81224 | 0.80612 | 0.80306 | 0.79796 | 0.78878 | 0.77755 | 0.77449 | 0.76224 | 0.71735 | 0.70714 | 0.70612 | 0.88163 | 0.87959 | 0.88061 | 0.87449 | 0.87347 | 0.87245 | 0.86327 | 0.8551 | 0.85306 | 0.84694 | 0.81429 | 0.79898 | 0.78265 | 0.86429 | 0.85408 | 0.8551 | 0.84694 | 0.84388 | 0.8398 | 0.83163 | 0.82041 | 0.81633 | 0.8051
|  | DALMALLY | CF |  |  |  |  | 0.82347 | 0.81224 | 0.81735 | 0.81122 | 0.80816 | 0.8 | 0.79694 | 0.78878 | 0.78061 | 0.77041 | 0.73776 | 0.71531 | 0.70612 | 0.88163 | 0.87347 | 0.88265 | 0.88061 | 0.87857 | 0.86939 | 0.86735 | 0.86327 | 0.8551 | 0.84796 | 0.81633 | 0.78878 | 0.75102 | 0.86429 | 0.85408 | 0.85816 | 0.85408 | 0.85102 | 0.84184 | 0.83878 | 0.83061 | 0.82347 | 0.81429
| TAYNUILT | DALMALLY SCHOOL | MINIMUM HEADROOM | NN 17249 27128 | YES | YES | 0 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.037228 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.15226 | 0.15226 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137
|  | DALMALLY SCHOOL | EE |  |  |  |  | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.037228 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.15811 | 0.15811 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137
|  | DALMALLY SCHOOL | HT |  |  |  |  | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.037228 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.15226 | 0.15226 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218
|  | DALMALLY SCHOOL | HE |  |  |  |  | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.037228 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.15226 | 0.15226 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218
|  | DALMALLY SCHOOL | CF |  |  |  |  | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.037228 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.13809 | 0.15226 | 0.15226 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218 | 0.12218
| INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | NO | 2.494 | 4.9728 | 4.5493 | 4.1228 | 3.636 | 3.1218 | 2.8452 | 2.0809 | 1.2544 | 0.44216 | -0.34661 | -3.6527 | -5.2884 | -6.6225 | 5.503 | 5.3213 | 5.102 | 4.853 | 4.5846 | 4.4611 | 4.0938 | 3.6826 | 3.1887 | 2.7152 | 0.86931 | 0.31849 | -1.8693 | 1.8879 | 1.4562 | 1.0154 | 0.49706 | -0.084571 | -0.25396 | -1.0091 | -1.8529 | -2.6611 | -3.4029
|  | DALNEIGH | EE |  |  |  |  | 4.9728 | 4.5493 | 4.1228 | 3.636 | 3.1218 | 2.8452 | 2.0809 | 1.2544 | 0.44216 | -0.34661 | -3.4823 | -4.7619 | -6.1491 | 5.503 | 5.3213 | 5.102 | 4.853 | 4.5846 | 4.4611 | 4.0938 | 3.6826 | 3.1887 | 2.7152 | 0.86931 | 0.31849 | -0.95906 | 1.8879 | 1.4562 | 1.0154 | 0.49706 | -0.084571 | -0.25396 | -1.0091 | -1.8529 | -2.6611 | -3.4029
|  | DALNEIGH | HT |  |  |  |  | 5.0493 | 4.6299 | 4.232 | 3.8075 | 3.3738 | 2.8809 | 2.1064 | 1.5207 | 0.75135 | -0.032327 | -3.6527 | -5.2884 | -6.6225 | 5.5724 | 5.4081 | 5.2305 | 5.0254 | 4.8264 | 4.5907 | 4.2469 | 4.0152 | 3.6703 | 3.3173 | 1.4887 | 1.1644 | 1.0318 | 2.0277 | 1.6124 | 1.2175 | 0.77971 | 0.36033 | -0.12947 | -0.8662 | -1.3478 | -2.0713 | -2.8152
|  | DALNEIGH | HE |  |  |  |  | 5.0636 | 4.8248 | 4.6167 | 4.3769 | 4.1391 | 3.8452 | 3.3248 | 2.983 | 2.4656 | 1.934 | -0.91906 | -2.8405 | -4.5133 | 5.5693 | 5.4479 | 5.3438 | 5.1979 | 5.055 | 4.8816 | 4.6081 | 4.4469 | 4.1662 | 3.8816 | 2.0509 | 1.196 | -0.13559 | 2.0379 | 1.7818 | 1.5501 | 1.2777 | 1.0226 | 0.68788 | 0.15624 | -0.072327 | -0.59069 | -1.1244
|  | DALNEIGH | CF |  |  |  |  | 5.1422 | 5.032 | 4.9187 | 4.7922 | 4.6503 | 4.5228 | 4.3473 | 4.1258 | 3.9187 | 3.9422 | 2.335 | -0.039469 | -3.2093 | 5.6071 | 5.5326 | 5.4571 | 5.3703 | 5.2744 | 5.1754 | 5.0377 | 4.8673 | 4.705 | 4.6805 | 3.3142 | 1.3858 | -1.8693 | 2.1369 | 1.9991 | 1.8542 | 1.694 | 1.4807 | 1.3052 | 1.0644 | 0.7542 | 0.46645 | 0.66747
| COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | NO | NO | 0.069 | 1.0673 | 1.0173 | 0.95918 | 0.88469 | 0.83265 | 0.75612 | 0.66633 | 0.5602 | 0.45612 | 0.41327 | 0.20816 | 0.14184 | 0.11837 | 2.1224 | 2.0918 | 2.0531 | 2.0082 | 1.9704 | 1.9204 | 1.8643 | 1.7959 | 1.7255 | 1.699 | 1.5551 | 1.4878 | 1.2908 | 1.6908 | 1.6429 | 1.5867 | 1.5173 | 1.4673 | 1.3918 | 1.3082 | 1.2041 | 1.1051 | 1.0643
|  | DALRULZION | EE |  |  |  |  | 1.0673 | 1.0173 | 0.95918 | 0.88469 | 0.83265 | 0.75612 | 0.66633 | 0.5602 | 0.45612 | 0.41327 | 0.20816 | 0.16633 | 0.14796 | 2.1224 | 2.0918 | 2.0531 | 2.0082 | 1.9704 | 1.9204 | 1.8643 | 1.7959 | 1.7255 | 1.699 | 1.5551 | 1.4878 | 1.3929 | 1.6908 | 1.6429 | 1.5867 | 1.5173 | 1.4673 | 1.3918 | 1.3082 | 1.2041 | 1.1051 | 1.0643
|  | DALRULZION | HT |  |  |  |  | 1.0969 | 1.051 | 0.99388 | 0.95204 | 0.9051 | 0.84388 | 0.76939 | 0.71429 | 0.63878 | 0.56735 | 0.27653 | 0.14184 | 0.11837 | 2.1439 | 2.1173 | 2.0827 | 2.0582 | 2.0316 | 1.9929 | 1.948 | 1.9133 | 1.8653 | 1.8214 | 1.6388 | 1.5561 | 1.5429 | 1.7194 | 1.6776 | 1.6204 | 1.5827 | 1.5367 | 1.4765 | 1.4061 | 1.3541 | 1.2806 | 1.2143
|  | DALRULZION | HE |  |  |  |  | 1.0969 | 1.0602 | 1.0163 | 0.98265 | 0.94592 | 0.89592 | 0.82959 | 0.77449 | 0.70816 | 0.64286 | 0.28673 | 0.17245 | 0.12143 | 2.1439 | 2.1224 | 2.0898 | 2.0694 | 2.0429 | 2.0102 | 1.9673 | 1.9388 | 1.8918 | 1.8469 | 1.6296 | 1.5327 | 1.4378 | 1.7184 | 1.6837 | 1.6418 | 1.6112 | 1.5765 | 1.5255 | 1.4633 | 1.4214 | 1.3571 | 1.299
|  | DALRULZION | CF |  |  |  |  | 1.1051 | 1.0694 | 1.0378 | 1.0112 | 0.97143 | 0.94286 | 0.89796 | 0.84694 | 0.82449 | 0.77551 | 0.52959 | 0.35 | 0.1949 | 2.149 | 2.1296 | 2.1061 | 2.0908 | 2.0633 | 2.0449 | 2.0102 | 1.9735 | 1.9551 | 1.9204 | 1.7214 | 1.5235 | 1.2908 | 1.7276 | 1.6908 | 1.6622 | 1.6378 | 1.6 | 1.5714 | 1.5296 | 1.4786 | 1.4592 | 1.4122
| BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 0.061 | 0.30918 | 0.2898 | 0.27041 | 0.2449 | 0.21122 | 0.20204 | 0.16633 | 0.13571 | 0.10204 | 0.070408 | -0.0030612 | -0.02449 | -0.035714 | 0.5051 | 0.49184 | 0.48061 | 0.45918 | 0.43878 | 0.43367 | 0.40918 | 0.39082 | 0.36633 | 0.34796 | 0.29592 | 0.27755 | 0.22347 | 0.4051 | 0.38571 | 0.36837 | 0.34592 | 0.31531 | 0.30408 | 0.26837 | 0.24388 | 0.2102 | 0.17959
|  | DALWHINNIE | EE |  |  |  |  | 0.30918 | 0.2898 | 0.27041 | 0.2449 | 0.21122 | 0.20204 | 0.16633 | 0.13571 | 0.10204 | 0.070408 | -0.0030612 | -0.015306 | -0.020408 | 0.5051 | 0.49184 | 0.48061 | 0.45918 | 0.43878 | 0.43367 | 0.40918 | 0.39082 | 0.36633 | 0.34796 | 0.29592 | 0.27755 | 0.25408 | 0.4051 | 0.38571 | 0.36837 | 0.34592 | 0.31531 | 0.30408 | 0.26837 | 0.24388 | 0.2102 | 0.17959
|  | DALWHINNIE | HT |  |  |  |  | 0.32041 | 0.30306 | 0.29184 | 0.26939 | 0.25306 | 0.23061 | 0.20408 | 0.1898 | 0.15918 | 0.13163 | 0.023469 | -0.02449 | -0.032653 | 0.51224 | 0.50204 | 0.49592 | 0.48265 | 0.47347 | 0.45816 | 0.44184 | 0.43265 | 0.41429 | 0.39592 | 0.32551 | 0.29388 | 0.2898 | 0.41429 | 0.39898 | 0.38776 | 0.36837 | 0.35306 | 0.33061 | 0.30612 | 0.29388 | 0.26531 | 0.2398
|  | DALWHINNIE | HE |  |  |  |  | 0.31837 | 0.30612 | 0.29694 | 0.28061 | 0.26735 | 0.24898 | 0.22347 | 0.20714 | 0.18367 | 0.15612 | 0.026531 | -0.014286 | -0.035714 | 0.51224 | 0.50306 | 0.49796 | 0.48367 | 0.47653 | 0.46224 | 0.44694 | 0.43878 | 0.42245 | 0.40204 | 0.32041 | 0.28673 | 0.26327 | 0.41327 | 0.40102 | 0.39286 | 0.37755 | 0.36531 | 0.34898 | 0.32551 | 0.30816 | 0.28571 | 0.26122
|  | DALWHINNIE | CF |  |  |  |  | 0.31429 | 0.3102 | 0.3 | 0.28776 | 0.27653 | 0.26633 | 0.25 | 0.22959 | 0.22551 | 0.20612 | 0.12551 | 0.042857 | -0.0081633 | 0.50918 | 0.50612 | 0.49694 | 0.49082 | 0.48265 | 0.47653 | 0.46224 | 0.45 | 0.44388 | 0.43163 | 0.36633 | 0.28673 | 0.22347 | 0.40918 | 0.4051 | 0.39592 | 0.38571 | 0.37347 | 0.36429 | 0.35102 | 0.33265 | 0.32653 | 0.31122
| WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | NO | 0.775 | 6.9616 | 6.7983 | 6.6157 | 6.4218 | 6.2075 | 5.9687 | 5.5402 | 4.9738 | 4.4208 | 3.8596 | 1.0381 | -1.0915 | -2.5282 | 8.9687 | 8.8524 | 8.7177 | 8.5759 | 8.4167 | 8.2351 | 8.0249 | 7.7677 | 7.5371 | 7.3218 | 5.5912 | 4.0825 | -1.393 | 8.7325 | 8.5805 | 8.409 | 8.2264 | 8.0254 | 7.7978 | 7.5192 | 7.0529 | 6.5356 | 6.059
|  | DENBURN | EE |  |  |  |  | 6.9616 | 6.7983 | 6.6157 | 6.4218 | 6.2075 | 5.9687 | 5.5402 | 4.9738 | 4.4208 | 3.8596 | 1.0381 | -0.85269 | -2.3956 | 8.9687 | 8.8524 | 8.7177 | 8.5759 | 8.4167 | 8.2351 | 8.0249 | 7.7677 | 7.5371 | 7.3218 | 5.5912 | 4.0825 | 1.3907 | 8.7325 | 8.5805 | 8.409 | 8.2264 | 8.0254 | 7.7978 | 7.5192 | 7.0529 | 6.5356 | 6.059
|  | DENBURN | HT |  |  |  |  | 7.0371 | 6.9044 | 6.7647 | 6.6065 | 6.4371 | 6.2432 | 5.883 | 5.3708 | 4.8626 | 4.3565 | 1.1769 | -1.0915 | -2.5282 | 9.0351 | 8.9453 | 8.8544 | 8.7463 | 8.6289 | 8.4922 | 8.3269 | 8.1259 | 7.934 | 7.7422 | 6.8075 | 6.3988 | 6.206 | 8.8039 | 8.6825 | 8.5519 | 8.406 | 8.2468 | 8.0631 | 7.8223 | 7.4917 | 7.0315 | 6.5743
|  | DENBURN | HE |  |  |  |  | 7.031 | 6.9126 | 6.7902 | 6.6524 | 6.5004 | 6.3238 | 6.0902 | 5.8085 | 5.4759 | 5.0891 | 2.6851 | 1.2647 | -0.368 | 9.0238 | 8.933 | 8.8381 | 8.732 | 8.6106 | 8.4687 | 8.2983 | 8.0871 | 7.884 | 7.6779 | 6.634 | 5.1988 | 2.557 | 8.7988 | 8.6876 | 8.5723 | 8.4427 | 8.2999 | 8.1315 | 7.9121 | 7.6488 | 7.256 | 6.7784
|  | DENBURN | CF |  |  |  |  | 7.0779 | 7.0198 | 6.9473 | 6.8708 | 6.784 | 6.6902 | 6.584 | 6.4432 | 6.3157 | 6.1728 | 5.0932 | 3.4861 | 1.1647 | 9.0565 | 9.0024 | 8.9391 | 8.8708 | 8.7942 | 8.7034 | 8.6034 | 8.4738 | 8.3514 | 8.2167 | 7.3565 | 4.4203 | -1.393 | 8.8427 | 8.7886 | 8.7213 | 8.6499 | 8.5662 | 8.4764 | 8.3743 | 8.2437 | 8.1203 | 7.9866
| TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42441 51227 | YES | YES | 0.547 | 1.4251 | 1.3822 | 1.321 | 1.2384 | 1.171 | 1.0731 | 0.97612 | 0.80571 | 0.65878 | 0.56694 | 0.27816 | 0.19857 | -0.17878 | 1.8141 | 1.7927 | 1.7702 | 1.7294 | 1.6998 | 1.6559 | 1.5722 | 1.4947 | 1.412 | 1.3498 | 1.1427 | 1.2604 | 1.0604 | 1.4492 | 1.4022 | 1.342 | 1.2604 | 1.1992 | 1.1033 | 1.0084 | 0.84714 | 0.70531 | 0.62367
|  | DERVAIG | EE |  |  |  |  | 1.4251 | 1.3822 | 1.321 | 1.2384 | 1.171 | 1.0731 | 0.97612 | 0.80571 | 0.65878 | 0.56694 | 0.27816 | 0.24551 | -0.14306 | 1.8141 | 1.7927 | 1.7702 | 1.7294 | 1.6998 | 1.6559 | 1.612 | 1.5029 | 1.412 | 1.3498 | 1.1427 | 1.2604 | 1.1553 | 1.4492 | 1.4022 | 1.342 | 1.2604 | 1.1992 | 1.1033 | 1.0084 | 0.84714 | 0.70531 | 0.62367
|  | DERVAIG | HT |  |  |  |  | 1.4506 | 1.4108 | 1.3598 | 1.2914 | 1.2322 | 1.1496 | 0.98327 | 0.86694 | 0.75571 | 0.66286 | 0.35163 | 0.19857 | -0.17878 | 1.8284 | 1.811 | 1.7865 | 1.76 | 1.7355 | 1.6978 | 1.5722 | 1.4947 | 1.4294 | 1.3794 | 1.2294 | 1.3094 | 1.3022 | 1.4747 | 1.439 | 1.3829 | 1.3237 | 1.2676 | 1.189 | 1.0339 | 0.92878 | 0.82061 | 0.73184
|  | DERVAIG | HE |  |  |  |  | 1.4506 | 1.419 | 1.3802 | 1.3302 | 1.2853 | 1.2078 | 1.1333 | 1.0169 | 0.90673 | 0.81184 | 0.42102 | 0.32612 | -0.048163 | 1.8263 | 1.812 | 1.7937 | 1.7682 | 1.7457 | 1.712 | 1.6773 | 1.5886 | 1.5131 | 1.4518 | 1.2131 | 1.3053 | 1.2176 | 1.4747 | 1.4461 | 1.4022 | 1.3563 | 1.3124 | 1.24 | 1.1696 | 1.0655 | 0.95939 | 0.86755
|  | DERVAIG | CF |  |  |  |  | 1.4598 | 1.4282 | 1.3986 | 1.369 | 1.3312 | 1.2935 | 1.2506 | 1.1904 | 1.1343 | 1.0557 | 0.69347 | 0.43939 | -0.055306 | 1.8294 | 1.8171 | 1.7998 | 1.7855 | 1.7631 | 1.7447 | 1.7202 | 1.6886 | 1.6478 | 1.5978 | 1.3488 | 1.288 | 1.0604 | 1.4839 | 1.4584 | 1.4278 | 1.3982 | 1.3594 | 1.3216 | 1.2788 | 1.2216 | 1.1727 | 1.1012
| BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | NO | 2.115 | 5.2404 | 5.0516 | 4.8271 | 4.5384 | 4.0914 | 3.5924 | 2.9771 | 2.5445 | 1.9914 | 1.4067 | -0.58715 | -1.8045 | -2.8239 | 7.6169 | 7.5108 | 7.3904 | 7.268 | 7.0588 | 6.7812 | 6.4659 | 6.2975 | 5.9782 | 5.6782 | 4.5486 | 4.1848 | 3.2174 | 6.2266 | 5.9623 | 5.6664 | 5.3583 | 4.9746 | 4.5113 | 3.945 | 3.645 | 3.0787 | 2.5481
|  | DINGWALL | EE |  |  |  |  | 5.2404 | 5.0516 | 4.8271 | 4.5384 | 4.0914 | 3.5924 | 2.9771 | 2.621 | 1.9955 | 1.4067 | -0.58715 | -1.6269 | -2.6402 | 7.6169 | 7.5108 | 7.3904 | 7.268 | 7.0588 | 6.7812 | 6.4659 | 6.2975 | 5.9782 | 5.6782 | 4.5486 | 4.1848 | 3.4991 | 6.2266 | 5.9623 | 5.6664 | 5.3583 | 4.9746 | 4.5113 | 3.945 | 3.645 | 3.0787 | 2.5481
|  | DINGWALL | HT |  |  |  |  | 5.3139 | 5.1577 | 4.9659 | 4.6608 | 4.2455 | 3.7026 | 3.1322 | 2.5445 | 1.9914 | 1.4261 | -0.55348 | -1.8045 | -2.8239 | 7.6618 | 7.5822 | 7.4802 | 7.3802 | 7.2404 | 6.9608 | 6.6894 | 6.3873 | 6.1037 | 5.8118 | 4.8618 | 4.6419 | 4.4634 | 6.3001 | 6.0623 | 5.7909 | 5.5164 | 5.1674 | 4.7266 | 4.246 | 3.6858 | 3.1562 | 2.6113
|  | DINGWALL | HE |  |  |  |  | 5.3098 | 5.1731 | 5.0108 | 4.8445 | 4.5782 | 4.2751 | 3.9557 | 3.5333 | 3.12 | 2.67 | 0.58428 | -0.5545 | -1.7882 | 7.6577 | 7.5894 | 7.5016 | 7.4149 | 7.2884 | 7.1424 | 6.9639 | 6.7149 | 6.47 | 6.1914 | 4.9292 | 4.6685 | 3.9246 | 6.297 | 6.1236 | 5.9256 | 5.7205 | 5.4389 | 5.1185 | 4.7715 | 4.3521 | 3.946 | 3.5297
|  | DINGWALL | CF |  |  |  |  | 5.3628 | 5.2884 | 5.1782 | 5.0608 | 4.9149 | 4.6822 | 4.4863 | 4.3394 | 4.118 | 3.8894 | 2.6669 | 1.2057 | -0.88103 | 7.6782 | 7.6312 | 7.5588 | 7.4833 | 7.3914 | 7.2782 | 7.1782 | 7.0843 | 6.9231 | 6.7537 | 5.872 | 4.9409 | 3.2174 | 6.3613 | 6.2634 | 6.1338 | 5.9878 | 5.8123 | 5.5981 | 5.4154 | 5.2358 | 5.0236 | 4.7991
| CARRADALE 1 | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 0.023 | 0.52449 | 0.50102 | 0.46735 | 0.44388 | 0.40714 | 0.37551 | 0.32653 | 0.27449 | 0.24694 | 0.20714 | 0.093878 | 0.061224 | 0.052041 | 0.72755 | 0.71429 | 0.6949 | 0.67959 | 0.65612 | 0.63776 | 0.6051 | 0.57041 | 0.55612 | 0.52959 | 0.4551 | 0.41735 | 0.28265 | 0.64796 | 0.62653 | 0.59388 | 0.57143 | 0.53571 | 0.50816 | 0.46224 | 0.41122 | 0.38776 | 0.35102
|  | DIPPEN | EE |  |  |  |  | 0.52449 | 0.50102 | 0.46735 | 0.44388 | 0.40714 | 0.37551 | 0.32653 | 0.27449 | 0.24694 | 0.20714 | 0.093878 | 0.07449 | 0.067347 | 0.72755 | 0.71429 | 0.6949 | 0.67959 | 0.65612 | 0.63776 | 0.6051 | 0.57041 | 0.55612 | 0.52959 | 0.4551 | 0.41735 | 0.35918 | 0.64796 | 0.62653 | 0.59388 | 0.57143 | 0.53571 | 0.50816 | 0.46224 | 0.41122 | 0.38776 | 0.35102
|  | DIPPEN | HT |  |  |  |  | 0.53571 | 0.51837 | 0.4898 | 0.46224 | 0.43061 | 0.40714 | 0.37347 | 0.34388 | 0.30306 | 0.26224 | 0.11327 | 0.061224 | 0.052041 | 0.73265 | 0.72245 | 0.71122 | 0.69592 | 0.67755 | 0.66735 | 0.64796 | 0.63163 | 0.60714 | 0.58061 | 0.48367 | 0.45408 | 0.45 | 0.65714 | 0.64184 | 0.61633 | 0.59184 | 0.56122 | 0.54082 | 0.50816 | 0.48061 | 0.4449 | 0.4051
|  | DIPPEN | HE |  |  |  |  | 0.53673 | 0.52347 | 0.5 | 0.47857 | 0.45204 | 0.43469 | 0.40102 | 0.36429 | 0.33776 | 0.30102 | 0.13571 | 0.09898 | 0.095918 | 0.73265 | 0.72653 | 0.71327 | 0.7 | 0.68469 | 0.67653 | 0.65408 | 0.63367 | 0.61531 | 0.59388 | 0.48673 | 0.43571 | 0.37959 | 0.65816 | 0.64796 | 0.62449 | 0.60612 | 0.58061 | 0.56531 | 0.53367 | 0.50102 | 0.47449 | 0.44082
|  | DIPPEN | CF |  |  |  |  | 0.54286 | 0.52755 | 0.51224 | 0.49592 | 0.48061 | 0.46122 | 0.45 | 0.42347 | 0.4051 | 0.38878 | 0.27755 | 0.15612 | 0.10306 | 0.73571 | 0.72857 | 0.71837 | 0.70918 | 0.70102 | 0.68776 | 0.67755 | 0.66122 | 0.64796 | 0.63571 | 0.54694 | 0.41939 | 0.28265 | 0.66327 | 0.64898 | 0.63673 | 0.62041 | 0.60714 | 0.58878 | 0.57857 | 0.55306 | 0.53469 | 0.52143
| BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | NO | 1.416 | 0.22062 | 0.1145 | -0.007951 | -0.14367 | -0.25897 | -0.40795 | -0.60183 | -0.8253 | -1.0773 | -1.261 | -1.7182 | -1.8926 | -2.3037 | 1.4167 | 1.3535 | 1.2749 | 1.1851 | 1.1167 | 1.0208 | 0.8994 | 0.7698 | 0.61776 | 0.50246 | 0.19021 | 0.23348 | -0.17367 | 0.72531 | 0.6447 | 0.5447 | 0.41001 | 0.30184 | 0.15287 | -0.033869 | -0.23897 | -0.47571 | -0.64918
|  | DORNOCH | EE |  |  |  |  | 0.22062 | 0.1145 | -0.007951 | -0.14367 | -0.25897 | -0.40795 | -0.60183 | -0.8253 | -1.0773 | -1.261 | -1.7182 | -1.8131 | -2.2159 | 1.4167 | 1.3535 | 1.2749 | 1.1851 | 1.1167 | 1.0208 | 0.8994 | 0.7698 | 0.61776 | 0.50246 | 0.19021 | 0.23348 | 0.030416 | 0.72531 | 0.6447 | 0.5447 | 0.41001 | 0.30184 | 0.15287 | -0.033869 | -0.23897 | -0.47571 | -0.64918
|  | DORNOCH | HT |  |  |  |  | 0.24103 | 0.16042 | 0.056335 | -0.038563 | -0.14979 | -0.3202 | -0.52224 | -0.65081 | -0.80081 | -0.95999 | -1.5926 | -1.8926 | -2.3037 | 1.4484 | 1.3984 | 1.3412 | 1.2892 | 1.2259 | 1.128 | 1.0167 | 0.94531 | 0.85042 | 0.75246 | 0.35246 | 0.36205 | 0.3345 | 0.74776 | 0.67225 | 0.59062 | 0.51511 | 0.42123 | 0.26613 | 0.082457 | -0.03489 | -0.18081 | -0.33897
|  | DORNOCH | HE |  |  |  |  | 0.24001 | 0.18491 | 0.11246 | 0.04511 | -0.036522 | -0.1304 | -0.24979 | -0.37938 | -0.52938 | -0.68856 | -1.4447 | -1.6477 | -2.0506 | 1.4463 | 1.4035 | 1.3555 | 1.3127 | 1.2576 | 1.1933 | 1.1116 | 1.0392 | 0.94225 | 0.84123 | 0.36266 | 0.33858 | 0.14062 | 0.74674 | 0.6947 | 0.63858 | 0.5845 | 0.51919 | 0.42531 | 0.30695 | 0.19266 | 0.046743 | -0.1053
|  | DORNOCH | CF |  |  |  |  | 0.24715 | 0.20531 | 0.14919 | 0.077763 | 0.021641 | -0.049788 | -0.12938 | -0.21918 | -0.30081 | -0.40183 | -0.91407 | -1.3773 | -1.9761 | 1.4586 | 1.4239 | 1.3841 | 1.3341 | 1.2994 | 1.2504 | 1.1902 | 1.1198 | 1.0718 | 0.99531 | 0.60348 | 0.31919 | -0.17367 | 0.75491 | 0.71103 | 0.66103 | 0.60797 | 0.56001 | 0.50491 | 0.43552 | 0.34368 | 0.27736 | 0.18042
| CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 0.196 | 0.025053 | 0.026073 | 0.012808 | 0.0015837 | -0.019845 | -0.042294 | -0.079029 | -0.12597 | -0.15454 | -0.19127 | -0.28209 | -0.31576 | -0.32189 | 0.30669 | 0.31383 | 0.29852 | 0.28322 | 0.25975 | 0.24648 | 0.22097 | 0.19036 | 0.17097 | 0.14852 | 0.078114 | 0.046482 | -0.041273 | 0.2373 | 0.21893 | 0.1924 | 0.16791 | 0.13628 | 0.11791 | 0.080155 | 0.037298 | 0.0087265 | -0.024947
|  | DOUGLAS PIER | EE |  |  |  |  | 0.033216 | 0.026073 | 0.012808 | 0.0015837 | -0.019845 | -0.042294 | -0.079029 | -0.12597 | -0.15454 | -0.19127 | -0.28209 | -0.29842 | -0.31066 | 0.31995 | 0.31383 | 0.29852 | 0.28322 | 0.25975 | 0.24648 | 0.22097 | 0.19036 | 0.17097 | 0.14852 | 0.078114 | 0.046482 | -0.0035184 | 0.2373 | 0.21893 | 0.1924 | 0.16791 | 0.13628 | 0.11791 | 0.080155 | 0.037298 | 0.0087265 | -0.024947
|  | DOUGLAS PIER | HT |  |  |  |  | 0.037298 | 0.031176 | 0.021992 | 0.013829 | 0.0026041 | -0.0086204 | -0.038212 | -0.072906 | -0.091273 | -0.12393 | -0.25352 | -0.31576 | -0.32189 | 0.32097 | 0.31893 | 0.31179 | 0.3026 | 0.2873 | 0.27505 | 0.25464 | 0.2322 | 0.22199 | 0.19954 | 0.11485 | 0.077094 | 0.074033 | 0.2424 | 0.23118 | 0.21077 | 0.1924 | 0.16893 | 0.14954 | 0.11995 | 0.084237 | 0.069951 | 0.036278
|  | DOUGLAS PIER | HE |  |  |  |  | 0.037298 | 0.032196 | 0.024033 | 0.01689 | 0.0077061 | 0.00056327 | -0.013722 | -0.039233 | -0.053518 | -0.080049 | -0.21474 | -0.25658 | -0.2627 | 0.32097 | 0.31893 | 0.31383 | 0.30669 | 0.29444 | 0.28322 | 0.26689 | 0.24546 | 0.23628 | 0.21791 | 0.12301 | 0.075053 | 0.033216 | 0.24342 | 0.23526 | 0.21995 | 0.20567 | 0.1873 | 0.17403 | 0.1475 | 0.11791 | 0.10567 | 0.080155
|  | DOUGLAS PIER | CF |  |  |  |  | 0.025053 | 0.036278 | 0.032196 | 0.027094 | 0.021992 | 0.014849 | 0.0087265 | -0.00045714 | -0.018824 | -0.039233 | -0.11678 | -0.20352 | -0.25352 | 0.30669 | 0.32199 | 0.31791 | 0.31485 | 0.30567 | 0.29444 | 0.28628 | 0.26791 | 0.25669 | 0.24036 | 0.16893 | 0.069951 | -0.041273 | 0.24546 | 0.24036 | 0.22913 | 0.21995 | 0.20464 | 0.19036 | 0.17811 | 0.15873 | 0.14138 | 0.11995
| ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 0.058 | 1.152 | 1.1194 | 1.0847 | 1.05 | 1.001 | 0.95306 | 0.91531 | 0.85102 | 0.79796 | 0.7449 | 0.62959 | 0.6051 | 0.5949 | 1.8051 | 1.7847 | 1.7653 | 1.7398 | 1.7082 | 1.6724 | 1.652 | 1.6082 | 1.5745 | 1.5398 | 1.4724 | 1.4633 | 1.4561 | 1.3602 | 1.3408 | 1.3204 | 1.3 | 1.2724 | 1.2459 | 1.2224 | 1.1857 | 1.1582 | 1.1286
|  | DRIMORE | EE |  |  |  |  | 1.152 | 1.1194 | 1.0847 | 1.05 | 1.001 | 0.95306 | 0.91531 | 0.85102 | 0.79796 | 0.7449 | 0.62959 | 0.61224 | 0.60204 | 1.8051 | 1.7847 | 1.7653 | 1.7398 | 1.7082 | 1.6724 | 1.652 | 1.6082 | 1.5745 | 1.5398 | 1.4724 | 1.4633 | 1.4561 | 1.3602 | 1.3408 | 1.3204 | 1.3 | 1.2724 | 1.2459 | 1.2224 | 1.1857 | 1.1582 | 1.1286
|  | DRIMORE | HT |  |  |  |  | 1.1724 | 1.1449 | 1.1153 | 1.0806 | 1.0531 | 1.0163 | 0.98265 | 0.93163 | 0.88571 | 0.85918 | 0.68061 | 0.6051 | 0.5949 | 1.8214 | 1.8082 | 1.7898 | 1.7684 | 1.7541 | 1.7286 | 1.7082 | 1.6745 | 1.6439 | 1.6347 | 1.5071 | 1.4633 | 1.4571 | 1.3714 | 1.3551 | 1.3378 | 1.3194 | 1.3031 | 1.2796 | 1.2592 | 1.2306 | 1.2061 | 1.1847
|  | DRIMORE | HE |  |  |  |  | 1.1745 | 1.152 | 1.1286 | 1.101 | 1.0816 | 1.052 | 1.0245 | 0.98265 | 0.93878 | 0.91633 | 0.70612 | 0.65306 | 0.64898 | 1.8235 | 1.8112 | 1.7969 | 1.7786 | 1.7673 | 1.7459 | 1.7296 | 1.698 | 1.6694 | 1.6602 | 1.5286 | 1.498 | 1.4939 | 1.3704 | 1.3571 | 1.3418 | 1.3245 | 1.3112 | 1.2908 | 1.2724 | 1.2408 | 1.2133 | 1.1929
|  | DRIMORE | CF |  |  |  |  | 1.1755 | 1.1582 | 1.1388 | 1.1184 | 1.0908 | 1.0776 | 1.05 | 1.0296 | 1 | 0.97347 | 0.8398 | 0.71735 | 0.65306 | 1.8245 | 1.8143 | 1.802 | 1.7888 | 1.7704 | 1.7643 | 1.7449 | 1.7327 | 1.7122 | 1.6908 | 1.6031 | 1.5204 | 1.4918 | 1.3745 | 1.3633 | 1.3531 | 1.3439 | 1.3286 | 1.3184 | 1.3031 | 1.2878 | 1.2724 | 1.2551
| CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | NO | 1.457 | 2.635 | 2.5829 | 2.5125 | 2.4472 | 2.3727 | 2.2544 | 2.1482 | 1.987 | 1.837 | 1.7023 | 1.4503 | 1.3442 | 1.3125 | 3.7431 | 3.7207 | 3.6788 | 3.6299 | 3.5595 | 3.4829 | 3.4186 | 3.3135 | 3.2156 | 3.1299 | 2.9544 | 2.8574 | 2.5523 | 3.4207 | 3.3431 | 3.2431 | 3.1666 | 3.0646 | 2.9493 | 2.8544 | 2.7013 | 2.5574 | 2.4309
|  | DRUMNADROCHIT | EE |  |  |  |  | 2.635 | 2.5829 | 2.5125 | 2.4472 | 2.3727 | 2.2544 | 2.1482 | 1.987 | 1.837 | 1.7023 | 1.4503 | 1.3982 | 1.3666 | 3.7431 | 3.7207 | 3.6788 | 3.6299 | 3.5595 | 3.4829 | 3.4186 | 3.3135 | 3.2156 | 3.1299 | 2.9544 | 2.8574 | 2.7105 | 3.4207 | 3.3431 | 3.2431 | 3.1666 | 3.0646 | 2.9493 | 2.8544 | 2.7013 | 2.5574 | 2.4309
|  | DRUMNADROCHIT | HT |  |  |  |  | 2.6544 | 2.6125 | 2.5574 | 2.5003 | 2.4411 | 2.3727 | 2.2942 | 2.1829 | 2.1044 | 1.9901 | 1.4891 | 1.3442 | 1.3125 | 3.7544 | 3.7391 | 3.7186 | 3.6972 | 3.6666 | 3.6095 | 3.5472 | 3.4707 | 3.4268 | 3.3544 | 3.0329 | 2.9533 | 2.935 | 3.4615 | 3.4013 | 3.3227 | 3.2533 | 3.1901 | 3.1023 | 3.0105 | 2.8921 | 2.8186 | 2.7115
|  | DRUMNADROCHIT | HE |  |  |  |  | 2.6523 | 2.6156 | 2.5758 | 2.5299 | 2.4819 | 2.4258 | 2.3533 | 2.2697 | 2.187 | 2.1248 | 1.5697 | 1.5013 | 1.4788 | 3.7533 | 3.7391 | 3.7207 | 3.7023 | 3.6819 | 3.6309 | 3.5748 | 3.5033 | 3.435 | 3.3942 | 3.0288 | 2.9288 | 2.7952 | 3.4605 | 3.4135 | 3.3462 | 3.2911 | 3.2452 | 3.1737 | 3.0931 | 2.9891 | 2.8901 | 2.8329
|  | DRUMNADROCHIT | CF |  |  |  |  | 2.6656 | 2.6391 | 2.6125 | 2.5819 | 2.5401 | 2.5074 | 2.4615 | 2.4054 | 2.336 | 2.2635 | 1.9176 | 1.6452 | 1.4901 | 3.7574 | 3.7472 | 3.736 | 3.7237 | 3.6952 | 3.6737 | 3.6278 | 3.5758 | 3.5237 | 3.4686 | 3.1921 | 2.8891 | 2.5523 | 3.4625 | 3.4156 | 3.3748 | 3.3309 | 3.2697 | 3.2329 | 3.1707 | 3.1044 | 3.035 | 2.9635
| GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | NO | 0 | 0.11967 | 0.11457 | 0.10743 | 0.10029 | 0.093143 | 0.079878 | 0.062531 | 0.053347 | 0.036 | 0.022735 | -0.01298 | -0.023184 | -0.043224 | 0.13637 | 0.13331 | 0.13331 | 0.12718 | 0.1231 | 0.11596 | 0.10473 | 0.099633 | 0.087388 | 0.079224 | 0.055755 | 0.061694 | 0.050469 | 0.12292 | 0.11782 | 0.11169 | 0.10047 | 0.094347 | 0.083122 | 0.067816 | 0.058633 | 0.042306 | 0.029041
|  | DRUMRUNIE | EE |  |  |  |  | 0.11967 | 0.11559 | 0.10743 | 0.10029 | 0.093143 | 0.079878 | 0.062531 | 0.053347 | 0.036 | 0.022735 | -0.01298 | -0.016041 | -0.038122 | 0.13637 | 0.13841 | 0.13331 | 0.12718 | 0.1231 | 0.11596 | 0.10473 | 0.099633 | 0.087388 | 0.079224 | 0.055755 | 0.061694 | 0.050469 | 0.12292 | 0.11782 | 0.11169 | 0.10047 | 0.094347 | 0.083122 | 0.067816 | 0.058633 | 0.042306 | 0.029041
|  | DRUMRUNIE | HT |  |  |  |  | 0.12784 | 0.11457 | 0.11049 | 0.10845 | 0.10131 | 0.094163 | 0.08702 | 0.072735 | 0.06049 | 0.048245 | -0.00073469 | -0.023184 | -0.043224 | 0.14453 | 0.13331 | 0.13433 | 0.13535 | 0.13024 | 0.12616 | 0.12208 | 0.11392 | 0.10678 | 0.097592 | 0.064939 | 0.061694 | 0.059653 | 0.13108 | 0.11884 | 0.11271 | 0.10965 | 0.10353 | 0.097408 | 0.091286 | 0.077 | 0.065776 | 0.055571
|  | DRUMRUNIE | HE |  |  |  |  | 0.12784 | 0.11763 | 0.11355 | 0.11151 | 0.10539 | 0.10437 | 0.091102 | 0.08498 | 0.074776 | 0.06151 | 0.01049 | -0.0048163 | -0.026898 | 0.14453 | 0.13535 | 0.13535 | 0.13637 | 0.13229 | 0.13127 | 0.1231 | 0.11698 | 0.11392 | 0.10473 | 0.072082 | 0.068837 | 0.059653 | 0.13108 | 0.12088 | 0.11578 | 0.11373 | 0.10965 | 0.10659 | 0.092306 | 0.087204 | 0.081082 | 0.065776
|  | DRUMRUNIE | CF |  |  |  |  | 0.13702 | 0.12478 | 0.11661 | 0.12069 | 0.11049 | 0.10641 | 0.10437 | 0.095184 | 0.092122 | 0.081918 | 0.050286 | 0.014571 | -0.020776 | 0.15269 | 0.14351 | 0.13535 | 0.14147 | 0.13637 | 0.13331 | 0.13229 | 0.12514 | 0.12514 | 0.11596 | 0.09249 | 0.073939 | 0.053531 | 0.14027 | 0.12904 | 0.11986 | 0.1219 | 0.11271 | 0.11067 | 0.10761 | 0.098429 | 0.097408 | 0.087204
| STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | 0.525 | -1.649 | -1.7347 | -1.8449 | -1.9388 | -2.0531 | -2.1786 | -2.3061 | -2.4867 | -2.6622 | -2.8133 | -3.2714 | -3.5929 | -3.7102 | -0.65816 | -0.70918 | -0.77755 | -0.83367 | -0.90714 | -0.98571 | -1.0582 | -1.1704 | -1.2755 | -1.3633 | -1.6296 | -1.8143 | -2.1082 | -1.1214 | -1.202 | -1.3051 | -1.3918 | -1.498 | -1.6194 | -1.7327 | -1.901 | -2.0663 | -2.2071
|  | DRYMEN | EE |  |  |  |  | -1.649 | -1.7347 | -1.8449 | -1.9388 | -2.0531 | -2.1786 | -2.3061 | -2.4867 | -2.6622 | -2.8133 | -3.2714 | -3.5296 | -3.6418 | -0.65816 | -0.70918 | -0.77755 | -0.83367 | -0.90714 | -0.98571 | -1.0582 | -1.1704 | -1.2755 | -1.3633 | -1.6296 | -1.8143 | -2.0082 | -1.1214 | -1.202 | -1.3051 | -1.3918 | -1.498 | -1.6194 | -1.7327 | -1.901 | -2.0663 | -2.2071
|  | DRYMEN | HT |  |  |  |  | -1.6112 | -1.6888 | -1.7755 | -1.8735 | -1.9602 | -2.0653 | -2.202 | -2.3551 | -2.4735 | -2.6214 | -3.251 | -3.5929 | -3.7102 | -0.62551 | -0.66531 | -0.71224 | -0.76531 | -0.81633 | -0.87959 | -0.95204 | -1.0408 | -1.102 | -1.1857 | -1.5367 | -1.7122 | -1.7735 | -1.0816 | -1.151 | -1.2276 | -1.3184 | -1.3939 | -1.4918 | -1.6122 | -1.7571 | -1.8582 | -1.9959
|  | DRYMEN | HE |  |  |  |  | -1.6122 | -1.6633 | -1.7224 | -1.7929 | -1.8541 | -1.9347 | -2.0388 | -2.1622 | -2.2469 | -2.3673 | -2.9816 | -3.3184 | -3.4745 | -0.62857 | -0.66327 | -0.69898 | -0.74592 | -0.78469 | -0.83673 | -0.90204 | -0.98163 | -1.0316 | -1.1051 | -1.4969 | -1.7316 | -1.9388 | -1.0827 | -1.1306 | -1.1847 | -1.2531 | -1.3082 | -1.3827 | -1.4806 | -1.5959 | -1.6714 | -1.7816
|  | DRYMEN | CF |  |  |  |  | -1.6 | -1.6439 | -1.6867 | -1.7337 | -1.7918 | -1.8367 | -1.9041 | -1.9694 | -2.0429 | -2.1214 | -2.5286 | -2.9347 | -3.249 | -0.62245 | -0.65204 | -0.68265 | -0.71429 | -0.75306 | -0.78776 | -0.83469 | -0.88673 | -0.9398 | -0.99694 | -1.3031 | -1.6796 | -2.1082 | -1.0704 | -1.1153 | -1.152 | -1.1959 | -1.2531 | -1.2908 | -1.3541 | -1.4184 | -1.4888 | -1.5592
| DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | NO | 1.745 | 0.532 | 0.46976 | 0.39527 | 0.30445 | 0.2422 | 0.15547 | 0.041184 | -0.09351 | -0.17208 | -0.28024 | -0.55269 | -0.64453 | -0.90116 | 0.72945 | 0.69986 | 0.65496 | 0.59476 | 0.55394 | 0.4968 | 0.42129 | 0.32741 | 0.27945 | 0.21006 | 0.018224 | 0.057255 | -0.21213 | 0.63583 | 0.57766 | 0.50828 | 0.42256 | 0.3644 | 0.28072 | 0.17154 | 0.04399 | -0.0305 | -0.1305
|  | DRYNOCH | EE |  |  |  |  | 0.532 | 0.46976 | 0.39527 | 0.30445 | 0.2422 | 0.15547 | 0.041184 | -0.09351 | -0.17208 | -0.28024 | -0.55269 | -0.61086 | -0.86035 | 0.72945 | 0.69986 | 0.65496 | 0.59476 | 0.55394 | 0.4968 | 0.42129 | 0.32741 | 0.27945 | 0.21006 | 0.018224 | 0.057255 | -0.068255 | 0.63583 | 0.57766 | 0.50828 | 0.42256 | 0.3644 | 0.28072 | 0.17154 | 0.04399 | -0.0305 | -0.1305
|  | DRYNOCH | HT |  |  |  |  | 0.56771 | 0.50853 | 0.45343 | 0.38302 | 0.32282 | 0.24322 | 0.1769 | 0.078939 | -0.0067755 | -0.10576 | -0.4731 | -0.64453 | -0.90116 | 0.74271 | 0.71618 | 0.68863 | 0.657 | 0.62231 | 0.56924 | 0.53455 | 0.46924 | 0.41414 | 0.34884 | 0.10496 | 0.11542 | 0.09399 | 0.66134 | 0.61134 | 0.56032 | 0.50011 | 0.44501 | 0.36644 | 0.3093 | 0.2144 | 0.1297 | 0.037867
|  | DRYNOCH | HE |  |  |  |  | 0.56669 | 0.51976 | 0.47996 | 0.42282 | 0.37282 | 0.30751 | 0.25343 | 0.16567 | 0.089143 | 0.0024082 | -0.41494 | -0.52514 | -0.79504 | 0.74271 | 0.71618 | 0.69169 | 0.66108 | 0.63047 | 0.59067 | 0.54884 | 0.49169 | 0.43761 | 0.38047 | 0.11108 | 0.11848 | 0.0072551 | 0.66032 | 0.6195 | 0.58174 | 0.53379 | 0.48685 | 0.42256 | 0.37358 | 0.28787 | 0.21032 | 0.12256
|  | DRYNOCH | CF |  |  |  |  | 0.57384 | 0.53608 | 0.48914 | 0.45547 | 0.41567 | 0.36465 | 0.30853 | 0.27282 | 0.21261 | 0.15955 | -0.118 | -0.39555 | -0.77055 | 0.75088 | 0.73455 | 0.7172 | 0.6968 | 0.66924 | 0.63455 | 0.59271 | 0.56618 | 0.52333 | 0.48455 | 0.26516 | 0.099092 | -0.21213 | 0.67154 | 0.64195 | 0.59603 | 0.56542 | 0.5297 | 0.48174 | 0.42664 | 0.39399 | 0.33685 | 0.28685
| KEITH 2 | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 1.483 | 1.2873 | 1.1659 | 1.0486 | 8.9455 | 8.8078 | 8.621 | 8.3547 | 8.1027 | 7.9241 | 7.7159 | 7.0027 | 6.5741 | -1.5718 | 2.3996 | 2.3445 | 9.5904 | 9.52 | 9.4547 | 9.3578 | 9.218 | 9.0833 | 8.9833 | 8.871 | 8.4578 | 0.88939 | 0.61184 | 1.7108 | 9.2899 | 9.1787 | 9.044 | 8.9164 | 8.746 | 8.4981 | 8.2532 | 8.095 | 7.897
|  | DUFFTOWN | EE |  |  |  |  | 1.2873 | 1.1659 | 1.0486 | 8.9455 | 8.8078 | 8.621 | 8.3547 | 8.1027 | 7.9241 | 7.7159 | 7.0027 | 6.619 | -1.529 | 2.3996 | 2.3445 | 9.5904 | 9.52 | 9.4547 | 9.3578 | 9.218 | 9.0833 | 8.9833 | 8.871 | 8.4578 | 0.88939 | 0.66184 | 1.7108 | 9.2899 | 9.1787 | 9.044 | 8.9164 | 8.746 | 8.4981 | 8.2532 | 8.095 | 7.897
|  | DUFFTOWN | HT |  |  |  |  | 1.3302 | 1.2435 | 1.1108 | 9.0292 | 8.8639 | 8.7047 | 8.4914 | 8.3129 | 8.1108 | 7.9067 | 7.0414 | 6.5741 | -1.5718 | 2.4149 | 2.3741 | 9.6139 | 9.5527 | 9.4792 | 9.4088 | 9.3037 | 9.219 | 9.118 | 9.0149 | 8.5771 | 1.0496 | 0.99755 | 1.7312 | 9.3287 | 9.2277 | 9.1042 | 8.9562 | 8.8113 | 8.6195 | 8.4583 | 8.2736 | 8.0879
|  | DUFFTOWN | HE |  |  |  |  | 1.3292 | 1.2731 | 1.1802 | 9.1404 | 9.018 | 8.8884 | 8.6986 | 8.57 | 8.42 | 8.271 | 7.4945 | 7.0567 | -1.1473 | 2.4129 | 2.3853 | 9.6404 | 9.5924 | 9.5302 | 9.4639 | 9.371 | 9.2914 | 9.2078 | 9.1231 | 8.6771 | 1.0782 | 0.82714 | 1.7302 | 9.3542 | 9.2868 | 9.2093 | 9.1093 | 8.9899 | 8.8195 | 8.6981 | 8.5603 | 8.4215
|  | DUFFTOWN | CF |  |  |  |  | 1.3527 | 1.3108 | 1.2588 | 9.2404 | 9.1904 | 9.1139 | 9.0241 | 8.8833 | 8.821 | 8.718 | 8.1986 | 7.6394 | -0.80959 | 2.42 | 2.4047 | 9.6822 | 9.6506 | 9.621 | 9.5853 | 9.5394 | 9.4649 | 9.422 | 9.3588 | 8.9986 | 1.2057 | 0.61184 | 1.7516 | 9.394 | 9.3583 | 9.3144 | 9.2695 | 9.2011 | 9.1205 | 8.996 | 8.9389 | 8.846
| BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 2.67 | 1.464 | 1.1242 | 0.70885 | 0.28028 | -0.20543 | -0.71462 | -1.182 | -1.9279 | -2.6636 | -3.2299 | -6.3901 | -8.4462 | -9.8345 | 4.0879 | 3.8981 | 3.6359 | 3.3757 | 3.0716 | 2.7492 | 2.6104 | 2.19 | 1.7869 | 1.4022 | -0.15594 | -0.97508 | -1.9496 | 2.729 | 2.4249 | 2.031 | 1.6484 | 1.1974 | 0.72084 | 0.43921 | -0.2261 | -0.87814 | -1.4394
|  | DUNBLANE | EE |  |  |  |  | 1.464 | 1.1242 | 0.70885 | 0.28028 | -0.20543 | -0.71462 | -1.1003 | -1.835 | -2.5473 | -3.2299 | -6.1167 | -8.0605 | -9.4253 | 4.0879 | 3.8981 | 3.6359 | 3.3757 | 3.0716 | 2.7492 | 2.6104 | 2.19 | 1.7869 | 1.4022 | -0.15594 | -0.97508 | -1.9475 | 2.729 | 2.4249 | 2.031 | 1.6484 | 1.1974 | 0.72084 | 0.45758 | -0.20161 | -0.83834 | -1.4394
|  | DUNBLANE | HT |  |  |  |  | 1.5405 | 1.1976 | 0.83028 | 0.39355 | -0.061555 | -0.49421 | -1.182 | -1.9279 | -2.6636 | -3.0748 | -6.3901 | -8.4462 | -9.8345 | 4.1726 | 4.0022 | 3.8134 | 3.5716 | 3.3155 | 3.0716 | 2.7175 | 2.3134 | 1.9185 | 1.8073 | 0.079771 | -0.59752 | -1.0077 | 2.8321 | 2.5413 | 2.2178 | 1.8331 | 1.4239 | 1.0413 | 0.43921 | -0.2261 | -0.87814 | -1.1475
|  | DUNBLANE | HE |  |  |  |  | 1.5517 | 1.3507 | 1.1282 | 0.84967 | 0.53844 | 0.24559 | -0.24319 | -0.79319 | -0.99625 | -1.5003 | -4.3411 | -6.3565 | -8.0631 | 4.1696 | 4.04 | 3.892 | 3.6981 | 3.4859 | 3.2951 | 3.0032 | 2.6614 | 2.5971 | 2.289 | 0.57977 | -0.31793 | -1.3832 | 2.8402 | 2.6525 | 2.4494 | 2.1831 | 1.8913 | 1.63 | 1.1882 | 0.68207 | 0.57901 | 0.13207
|  | DUNBLANE | CF |  |  |  |  | 1.6272 | 1.4946 | 1.3293 | 1.1578 | 0.93844 | 0.74559 | 0.49763 | 0.20375 | -0.079922 | -0.37686 | -1.8279 | -3.9565 | -6.4253 | 4.2073 | 4.1053 | 3.9736 | 3.8451 | 3.691 | 3.5481 | 3.3563 | 3.1308 | 2.9104 | 2.6828 | 1.6134 | 0.14023 | -1.9496 | 2.9066 | 2.777 | 2.6117 | 2.4596 | 2.2535 | 2.08 | 1.8494 | 1.5678 | 1.3025 | 1.0198
| DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 0.41 | 11.6337 | 11.348 | 11.0561 | 10.7163 | 10.3806 | 9.9857 | 9.3735 | 8.6929 | 8.0204 | 7.3908 | 4.8276 | 2.9908 | 2.6582 | 13.552 | 13.4173 | 13.2714 | 13.1051 | 12.9408 | 12.7449 | 12.4276 | 11.9735 | 11.601 | 11.2735 | 9.7378 | 8.6276 | 7.5235 | 13.1898 | 12.9163 | 12.6418 | 12.3 | 11.9745 | 11.5786 | 11.0031 | 10.5347 | 9.9194 | 9.3316
|  | DUNOON | EE |  |  |  |  | 11.6337 | 11.348 | 11.0561 | 10.7163 | 10.3806 | 9.9857 | 9.3735 | 8.85 | 8.1296 | 7.4765 | 4.8388 | 3.1276 | 2.7296 | 13.552 | 13.4173 | 13.2714 | 13.1051 | 12.9408 | 12.7449 | 12.4276 | 12.1112 | 11.6694 | 11.2806 | 9.7378 | 8.6276 | 7.6408 | 13.1898 | 12.9163 | 12.6418 | 12.3 | 11.9745 | 11.5786 | 11.0031 | 10.599 | 9.9286 | 9.3316
|  | DUNOON | HT |  |  |  |  | 11.7235 | 11.4837 | 11.2143 | 10.949 | 10.6316 | 10.2888 | 9.5214 | 8.6929 | 8.0204 | 7.3908 | 4.8276 | 2.9908 | 2.6582 | 13.6082 | 13.501 | 13.3827 | 13.2592 | 13.1153 | 12.9582 | 12.4755 | 11.9735 | 11.601 | 11.2735 | 10.1367 | 9.3622 | 9.2031 | 13.2929 | 13.0735 | 12.8276 | 12.5878 | 12.2939 | 11.9684 | 11.2888 | 10.5347 | 9.9194 | 9.3357
|  | DUNOON | HE |  |  |  |  | 11.7173 | 11.5653 | 11.3888 | 11.1949 | 10.998 | 10.7551 | 10.401 | 9.8194 | 9.2714 | 8.7531 | 6.6469 | 5.0908 | 4.4827 | 13.598 | 13.5173 | 13.4265 | 13.3245 | 13.2122 | 13.0786 | 12.9061 | 12.5224 | 12.15 | 11.8102 | 10.4847 | 9.451 | 8.4133 | 13.2888 | 13.1439 | 12.9765 | 12.7806 | 12.5949 | 12.352 | 12.0337 | 11.4949 | 10.9888 | 10.501
|  | DUNOON | CF |  |  |  |  | 11.7704 | 11.6745 | 11.5745 | 11.452 | 11.3306 | 11.1735 | 11.0102 | 10.8102 | 10.651 | 10.4184 | 9.252 | 7.6214 | 6.2735 | 13.6224 | 13.5653 | 13.5031 | 13.4327 | 13.352 | 13.248 | 13.1367 | 13.001 | 12.8561 | 12.6592 | 11.5776 | 9.8184 | 7.5235 | 13.3388 | 13.2429 | 13.1439 | 13.0214 | 12.9061 | 12.7439 | 12.5776 | 12.3684 | 12.2071 | 11.9704
| DUNVEGAN | DUNVEGAN | MINIMUM HEADROOM | NG 27646 47150 | YES | NO | 0.83 | 1.1819 | 1.0992 | 1.0186 | 0.94006 | 0.84108 | 0.74516 | 0.61455 | 0.5074 | 0.37169 | 0.25536 | -0.040555 | -0.15076 | -0.18341 | 1.6788 | 1.6288 | 1.5788 | 1.5339 | 1.4717 | 1.4094 | 1.3299 | 1.2635 | 1.1778 | 1.1074 | 0.88904 | 0.78598 | 0.44618 | 1.3145 | 1.236 | 1.1625 | 1.089 | 0.99516 | 0.90128 | 0.77985 | 0.67883 | 0.55026 | 0.44006
|  | DUNVEGAN | EE |  |  |  |  | 1.1819 | 1.0992 | 1.0186 | 0.94006 | 0.84108 | 0.74516 | 0.61455 | 0.5074 | 0.37169 | 0.25536 | -0.040555 | -0.091576 | -0.12627 | 1.6788 | 1.6288 | 1.5788 | 1.5339 | 1.4717 | 1.4094 | 1.3299 | 1.2635 | 1.1778 | 1.1074 | 0.88904 | 0.78598 | 0.62577 | 1.3145 | 1.236 | 1.1625 | 1.089 | 0.99516 | 0.90128 | 0.77985 | 0.67883 | 0.55026 | 0.44006
|  | DUNVEGAN | HT |  |  |  |  | 1.2074 | 1.1401 | 1.0778 | 1.0125 | 0.93393 | 0.86455 | 0.76761 | 0.66761 | 0.56149 | 0.45332 | 0.045159 | -0.15076 | -0.18341 | 1.6992 | 1.6635 | 1.6309 | 1.5921 | 1.5472 | 1.5094 | 1.4503 | 1.389 | 1.3258 | 1.2605 | 1.0074 | 0.887 | 0.87067 | 1.3431 | 1.2809 | 1.2258 | 1.1625 | 1.085 | 1.0227 | 0.93291 | 0.83598 | 0.73598 | 0.63496
|  | DUNVEGAN | HE |  |  |  |  | 1.2064 | 1.1554 | 1.1084 | 1.0605 | 0.99618 | 0.94618 | 0.86557 | 0.77577 | 0.68393 | 0.59006 | 0.13598 | 0.015567 | -0.0017796 | 1.6982 | 1.6666 | 1.636 | 1.6064 | 1.5645 | 1.5319 | 1.4819 | 1.4278 | 1.3645 | 1.3054 | 1.0023 | 0.8574 | 0.71353 | 1.3421 | 1.2962 | 1.2492 | 1.2013 | 1.1411 | 1.0952 | 1.0176 | 0.93393 | 0.84822 | 0.75638
|  | DUNVEGAN | CF |  |  |  |  | 1.2145 | 1.1758 | 1.137 | 1.086 | 1.0441 | 0.9921 | 0.95332 | 0.89006 | 0.837 | 0.77475 | 0.47271 | 0.17577 | 0.013527 | 1.7023 | 1.6799 | 1.6554 | 1.6217 | 1.5941 | 1.5554 | 1.5288 | 1.4839 | 1.4421 | 1.3972 | 1.1503 | 0.82271 | 0.44618 | 1.3523 | 1.3125 | 1.2778 | 1.2258 | 1.187 | 1.1329 | 1.1013 | 1.038 | 0.98802 | 0.92577
| DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 0.728 | 2.8255 | 2.1041 | 0.81837 | -0.73878 | -1.3878 | -4.2551 | -5.4153 | -6.8071 | -8.1327 | -10.1694 | -18.8276 | -28.3122 | -37.0143 | 5.0714 | 4.5071 | 3.2418 | 1.6878 | 1.3561 | -1.8735 | -3.1204 | -4.4551 | -5.7633 | -7.9408 | -17.0755 | -28.0031 | -38.4 | 3.6122 | 2.9296 | 1.5082 | -0.26735 | -0.87143 | -4.2388 | -5.5531 | -7.0469 | -8.499 | -10.8255
|  | DYCE NORTH | EE |  |  |  |  | 2.9939 | 2.1612 | 1.4337 | 0.67653 | -0.71531 | -2.6388 | -3.9265 | -4.8561 | -6.3204 | -7.2255 | -11.6173 | -19.8388 | -23.002 | 5.3867 | 4.75 | 4.2847 | 3.7408 | 2.4112 | 0.42551 | -0.71939 | -1.3888 | -2.8112 | -3.6276 | -7.7776 | -17.4612 | -21.3122 | 3.7704 | 2.9816 | 2.2939 | 1.5684 | 0.084694 | -2.0673 | -3.4071 | -4.2857 | -5.8857 | -6.8418
|  | DYCE NORTH | HT |  |  |  |  | 2.8255 | 2.1041 | 0.81837 | -0.73878 | -1.3878 | -4.2551 | -5.1204 | -6.0582 | -6.7735 | -7.6939 | -13.1408 | -23.0571 | -31.0704 | 5.0714 | 4.5071 | 3.2418 | 1.6878 | 1.3561 | -1.848 | -2.5194 | -3.2622 | -3.7735 | -4.5316 | -9.699 | -21.2531 | -30.9806 | 3.6122 | 2.9296 | 1.5082 | -0.26735 | -0.87143 | -4.2388 | -5.1 | -6.0327 | -6.7184 | -7.6541
|  | DYCE NORTH | HE |  |  |  |  | 3.1418 | 2.3816 | 1.2214 | -0.26633 | -1.2296 | -4.1122 | -5.4153 | -6.8071 | -8.1327 | -10.1694 | -18.8276 | -28.3122 | -37.0143 | 5.4408 | 4.8367 | 3.7194 | 2.248 | 1.3704 | -1.8735 | -3.1204 | -4.4551 | -5.7633 | -7.9408 | -17.0755 | -28.0031 | -38.4 | 3.9153 | 3.1908 | 1.9214 | 0.25612 | -0.77041 | -4.151 | -5.5531 | -7.0469 | -8.499 | -10.8255
|  | DYCE NORTH | CF |  |  |  |  | 4.1071 | 3.6031 | 3.1245 | 2.6561 | 1.7929 | 0.5898 | -0.26633 | -1.0847 | -1.799 | -2.6622 | -6.7194 | -10.3551 | -13.0439 | 6.4704 | 6.0143 | 5.6378 | 5.3082 | 4.5153 | 3.3245 | 2.4704 | 1.6939 | 0.99286 | 0.11735 | -3.5857 | -6.8867 | -9.302 | 4.8582 | 4.3571 | 3.9041 | 3.4653 | 2.5408 | 1.1959 | 0.28571 | -0.56939 | -1.3327 | -2.2776
| THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | NO | 0.556 | 0.42186 | 0.41369 | 0.40349 | 0.39635 | 0.38206 | 0.37594 | 0.35757 | 0.33716 | 0.3341 | 0.31982 | 0.28818 | 0.27492 | 0.26573 | 0.51369 | 0.50961 | 0.50349 | 0.49839 | 0.4892 | 0.4841 | 0.47288 | 0.45553 | 0.45247 | 0.44431 | 0.41778 | 0.40655 | 0.38002 | 0.47186 | 0.46063 | 0.45247 | 0.44431 | 0.43308 | 0.4239 | 0.40757 | 0.38716 | 0.38512 | 0.36982
|  | EDAY | EE |  |  |  |  | 0.4239 | 0.41369 | 0.40349 | 0.39635 | 0.38206 | 0.37594 | 0.35757 | 0.33716 | 0.3341 | 0.31982 | 0.28818 | 0.28104 | 0.279 | 0.51676 | 0.50961 | 0.50349 | 0.49839 | 0.4892 | 0.4841 | 0.47288 | 0.45553 | 0.45247 | 0.44431 | 0.41778 | 0.40655 | 0.39431 | 0.47186 | 0.46063 | 0.45247 | 0.44431 | 0.43308 | 0.4239 | 0.40757 | 0.38716 | 0.38512 | 0.36982
|  | EDAY | HT |  |  |  |  | 0.42186 | 0.42288 | 0.41573 | 0.40859 | 0.40247 | 0.39227 | 0.379 | 0.37084 | 0.35757 | 0.34227 | 0.29839 | 0.27798 | 0.27186 | 0.51369 | 0.5188 | 0.51369 | 0.50757 | 0.50451 | 0.49737 | 0.48818 | 0.48206 | 0.47288 | 0.46267 | 0.43002 | 0.41676 | 0.41267 | 0.479 | 0.47084 | 0.46573 | 0.45859 | 0.45247 | 0.44124 | 0.43104 | 0.42186 | 0.40961 | 0.39431
|  | EDAY | HE |  |  |  |  | 0.42186 | 0.41778 | 0.41676 | 0.41267 | 0.40349 | 0.39635 | 0.38716 | 0.37798 | 0.36573 | 0.35145 | 0.29227 | 0.27492 | 0.26573 | 0.51471 | 0.51369 | 0.51471 | 0.51165 | 0.50247 | 0.49839 | 0.49329 | 0.48716 | 0.47492 | 0.46676 | 0.42696 | 0.41471 | 0.40349 | 0.479 | 0.46471 | 0.46573 | 0.46369 | 0.45145 | 0.44635 | 0.43716 | 0.43002 | 0.41676 | 0.40553
|  | EDAY | CF |  |  |  |  | 0.42288 | 0.4188 | 0.41778 | 0.41369 | 0.40859 | 0.40553 | 0.39839 | 0.3892 | 0.379 | 0.37594 | 0.34124 | 0.29839 | 0.27186 | 0.51471 | 0.51471 | 0.51573 | 0.51267 | 0.50961 | 0.50655 | 0.49839 | 0.49329 | 0.48512 | 0.48308 | 0.45247 | 0.41267 | 0.38002 | 0.479 | 0.46778 | 0.46778 | 0.46267 | 0.45757 | 0.45451 | 0.44737 | 0.4392 | 0.429 | 0.42492
| THURSO | EDAY TIDAL | MINIMUM HEADROOM | HY 54226 31320 | YES | NO | 0 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694
|  | EDAY TIDAL | EE |  |  |  |  | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694
|  | EDAY TIDAL | HT |  |  |  |  | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694
|  | EDAY TIDAL | HE |  |  |  |  | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694
|  | EDAY TIDAL | CF |  |  |  |  | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694
| FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | NO | 1.648 | 1.0235 | 0.91122 | 0.78367 | 0.62958 | 0.45509 | 0.16122 | -0.18572 | -0.63164 | -1.1714 | -1.8163 | -2.9041 | -3.2255 | -3.6498 | 1.8206 | 1.7482 | 1.6767 | 1.591 | 1.4931 | 1.2675 | 0.98285 | 0.6604 | 0.33795 | -0.027355 | -0.60082 | -0.62899 | -1.0076 | 1.4363 | 1.3057 | 1.1914 | 1.0496 | 0.88734 | 0.63122 | 0.29652 | -0.10858 | -0.56878 | -1.1218
|  | EDZELL | EE |  |  |  |  | 1.0235 | 0.91122 | 0.78367 | 0.62958 | 0.45509 | 0.16122 | -0.18572 | -0.61225 | -1.05 | -1.5061 | -2.9041 | -3.1837 | -3.5886 | 1.8206 | 1.7482 | 1.6767 | 1.591 | 1.4931 | 1.2675 | 0.98285 | 0.6604 | 0.33795 | 0.024686 | -0.60082 | -0.62899 | -0.82899 | 1.4363 | 1.3057 | 1.1914 | 1.0496 | 0.88734 | 0.63122 | 0.29652 | -0.10858 | -0.51266 | -0.91368
|  | EDZELL | HT |  |  |  |  | 1.052 | 0.93264 | 0.81224 | 0.67754 | 0.56224 | 0.24591 | -0.1847 | -0.63164 | -1.1714 | -1.8163 | -2.8357 | -3.2255 | -3.6498 | 1.8441 | 1.7818 | 1.7237 | 1.6461 | 1.592 | 1.3482 | 1.0359 | 0.71856 | 0.3655 | -0.027355 | -0.46715 | -0.4698 | -0.50246 | 1.4822 | 1.3537 | 1.2424 | 1.1149 | 1.0098 | 0.70877 | 0.30877 | -0.092253 | -0.56878 | -1.1218
|  | EDZELL | HE |  |  |  |  | 1.05 | 0.9755 | 0.88877 | 0.78367 | 0.67754 | 0.39489 | 0.092849 | -0.25307 | -0.63062 | -1.0296 | -2.1561 | -2.7255 | -3.4182 | 1.84 | 1.791 | 1.7451 | 1.6798 | 1.6216 | 1.3706 | 1.0941 | 0.80224 | 0.49407 | 0.17979 | -0.33348 | -0.42899 | -0.75246 | 1.4792 | 1.3894 | 1.3026 | 1.1955 | 1.1067 | 0.84346 | 0.55264 | 0.23734 | -0.11776 | -0.49123
|  | EDZELL | CF |  |  |  |  | 1.0653 | 1.0071 | 0.94795 | 0.86836 | 0.79183 | 0.50611 | 0.25611 | -0.007151 | -0.28062 | -0.55919 | -1.4459 | -2.1959 | -3.1906 | 1.8533 | 1.8135 | 1.7808 | 1.7267 | 1.6818 | 1.4522 | 1.2043 | 0.95224 | 0.69407 | 0.44101 | 0.0022367 | -0.36776 | -1.0076 | 1.4955 | 1.42 | 1.3577 | 1.2741 | 1.2077 | 0.94856 | 0.70877 | 0.45469 | 0.1853 | -0.076947
| MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | NO | 0.009 | 9.1051 | 8.9837 | 8.8296 | 8.6939 | 8.5306 | 8.3429 | 8.099 | 7.7847 | 7.4837 | 7.2071 | 6.3806 | 6.3194 | 5.3796 | 9.0204 | 8.9306 | 8.7898 | 8.6816 | 8.5265 | 8.3602 | 8.1949 | 7.952 | 7.7204 | 7.5092 | 6.9908 | 5.7439 | 2.1602 | 9.0735 | 8.9561 | 8.7969 | 8.6643 | 8.4949 | 8.3163 | 8.0929 | 7.801 | 7.5245 | 7.2724
|  | EDZELL STREET | EE |  |  |  |  | 9.1051 | 8.9837 | 8.8296 | 8.6939 | 8.5306 | 8.3429 | 8.099 | 7.7847 | 7.4837 | 7.2071 | 6.6204 | 6.501 | 5.5847 | 9.0204 | 8.9306 | 8.7898 | 8.6816 | 8.5265 | 8.3602 | 8.1949 | 7.952 | 7.7204 | 7.5092 | 6.9908 | 6.5388 | 4.9429 | 9.0735 | 8.9561 | 8.7969 | 8.6643 | 8.4949 | 8.3163 | 8.0929 | 7.801 | 7.5245 | 7.2724
|  | EDZELL STREET | HT |  |  |  |  | 9.1398 | 9.0163 | 8.8898 | 8.7561 | 8.6082 | 8.4816 | 8.2439 | 7.9898 | 7.7735 | 7.5235 | 6.3806 | 6.3194 | 5.3796 | 9.0796 | 9.0153 | 8.9459 | 8.8592 | 8.7571 | 8.6837 | 8.5429 | 8.3816 | 8.2714 | 8.1153 | 7.3939 | 8.0214 | 7.9867 | 9.1286 | 9.0082 | 8.8908 | 8.7622 | 8.6173 | 8.4969 | 8.2786 | 8.0357 | 7.8378 | 7.601
|  | EDZELL STREET | HE |  |  |  |  | 9.149 | 9.0878 | 9.0286 | 8.9531 | 8.8673 | 8.8071 | 8.6327 | 8.4306 | 8.2755 | 8.0796 | 7.0918 | 6.902 | 5.8898 | 9.0714 | 9.0092 | 8.9398 | 8.8531 | 8.75 | 8.6724 | 8.5255 | 8.35 | 8.2286 | 8.051 | 7 | 6.7153 | 5.0949 | 9.1357 | 9.0673 | 9 | 8.9184 | 8.8245 | 8.7592 | 8.5898 | 8.399 | 8.2571 | 8.0724
|  | EDZELL STREET | CF |  |  |  |  | 9.1837 | 9.1571 | 9.1296 | 9.0878 | 9.049 | 8.999 | 8.9571 | 8.8653 | 8.7776 | 8.7255 | 8.0898 | 7.65 | 6.1224 | 9.0816 | 9.0296 | 8.9786 | 8.898 | 8.8163 | 8.7082 | 8.6092 | 8.4602 | 8.3133 | 8.199 | 7.148 | 5.7439 | 2.1602 | 9.1684 | 9.1296 | 9.0918 | 9.0388 | 8.9888 | 8.9255 | 8.8827 | 8.7949 | 8.7133 | 8.6633
| ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 1.439 | 6.9872 | 6.3443 | 5.68 | 5.0413 | 4.4004 | 3.68 | 2.7709 | 1.7709 | 0.51576 | -0.91384 | -7.274 | -10.4536 | -11.1271 | 8.7862 | 8.3535 | 7.9025 | 7.478 | 7.0596 | 6.6178 | 6.0964 | 5.6127 | 4.9423 | 4.1535 | -0.025061 | -1.4128 | -2.4006 | 7.8484 | 7.2841 | 6.68 | 6.0953 | 5.5086 | 4.8729 | 4.078 | 3.1923 | 2.1086 | 0.89739
|  | ELGIN | EE |  |  |  |  | 6.9872 | 6.3443 | 5.68 | 5.0413 | 4.4004 | 3.68 | 2.7709 | 2.0045 | 0.95453 | -0.10771 | -6.7434 | -9.9567 | -11.1271 | 8.7862 | 8.3535 | 7.9025 | 7.478 | 7.0596 | 6.6178 | 6.0964 | 5.6127 | 4.9729 | 4.3647 | 0.25249 | -1.4128 | -2.4006 | 7.8484 | 7.2841 | 6.68 | 6.0953 | 5.5086 | 4.8729 | 4.078 | 3.3678 | 2.4392 | 1.5076
|  | ELGIN | HT |  |  |  |  | 7.0851 | 6.478 | 5.7902 | 5.1964 | 4.626 | 3.9851 | 2.9504 | 1.7709 | 0.51576 | -0.91384 | -7.274 | -10.4536 | -11.0679 | 8.8586 | 8.4535 | 7.979 | 7.5994 | 7.2545 | 6.8923 | 6.329 | 5.6504 | 4.9423 | 4.1535 | 0.35759 | -1.1659 | -1.4557 | 7.9515 | 7.3964 | 6.7504 | 6.1994 | 5.677 | 5.1096 | 4.2209 | 3.1923 | 2.1086 | 0.89739
|  | ELGIN | HE |  |  |  |  | 7.0974 | 6.5923 | 6.0453 | 5.5382 | 5.0331 | 4.4341 | 3.7413 | 2.8004 | 1.83 | 0.79535 | -5.0373 | -7.9026 | -9.4353 | 8.8668 | 8.5035 | 8.1035 | 7.7504 | 7.3984 | 7.0147 | 6.5382 | 5.8719 | 5.1913 | 4.4647 | -0.025061 | -1.3761 | -1.9598 | 7.9668 | 7.5076 | 7.0004 | 6.53 | 6.0627 | 5.5311 | 4.9209 | 4.0994 | 3.2484 | 2.3423
|  | ELGIN | CF |  |  |  |  | 7.2413 | 6.9096 | 6.5402 | 6.1882 | 5.8627 | 5.4474 | 5.0096 | 4.5576 | 4.0443 | 3.4647 | -0.50567 | -4.8557 | -7.7649 | 8.978 | 8.7474 | 8.476 | 8.2321 | 8.0035 | 7.7249 | 7.4311 | 7.1198 | 6.7719 | 6.38 | 3.2974 | 0.23718 | -2.0659 | 8.0984 | 7.8147 | 7.4923 | 7.179 | 6.879 | 6.5137 | 6.1402 | 5.7453 | 5.2953 | 4.7811
| ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | 2.98 | -6.8971 | -7.2961 | -7.6675 | -8.0053 | -8.2441 | -8.4461 | -8.6369 | -8.8512 | -9.0614 | -9.2247 | -10.0839 | -10.5563 | -10.6482 | -6.1849 | -6.4655 | -6.689 | -6.8818 | -7.0114 | -7.1175 | -7.241 | -7.388 | -7.5196 | -7.6267 | -8.0808 | -8.339 | -8.6369 | -6.6073 | -6.9196 | -7.1982 | -7.4308 | -7.59 | -7.7512 | -7.9216 | -8.1053 | -8.3135 | -8.4655
|  | ELLIOT DEPOT | EE |  |  |  |  | -6.8492 | -7.242 | -7.5941 | -7.941 | -8.2043 | -8.4206 | -8.6349 | -8.8512 | -9.0614 | -9.2247 | -10.0369 | -10.5288 | -10.6196 | -6.1278 | -6.4022 | -6.6094 | -6.8155 | -6.9726 | -7.1012 | -7.241 | -7.388 | -7.5196 | -7.6267 | -8.0808 | -8.339 | -8.5931 | -6.5573 | -6.8635 | -7.1257 | -7.3737 | -7.5594 | -7.7155 | -7.9104 | -8.1053 | -8.3135 | -8.4655
|  | ELLIOT DEPOT | HT |  |  |  |  | -6.8971 | -7.2961 | -7.6675 | -8.0053 | -8.2441 | -8.4461 | -8.6369 | -8.8359 | -9.0155 | -9.2124 | -10.0839 | -10.5563 | -10.6482 | -6.1849 | -6.4655 | -6.689 | -6.8818 | -7.0114 | -7.1175 | -7.2084 | -7.3288 | -7.4329 | -7.5461 | -8.0543 | -8.2808 | -8.3471 | -6.6073 | -6.9196 | -7.1982 | -7.4308 | -7.59 | -7.7512 | -7.9216 | -8.1022 | -8.2594 | -8.4349
|  | ELLIOT DEPOT | HE |  |  |  |  | -6.8288 | -7.1798 | -7.4982 | -7.8022 | -8.0124 | -8.191 | -8.3441 | -8.4931 | -8.6237 | -8.7665 | -9.5278 | -10.0226 | -10.2196 | -6.1114 | -6.3778 | -6.5696 | -6.7502 | -6.8829 | -6.9982 | -7.1124 | -7.2369 | -7.342 | -7.4584 | -7.9716 | -8.1706 | -8.3798 | -6.5369 | -6.8288 | -7.0645 | -7.2869 | -7.442 | -7.5737 | -7.69 | -7.8226 | -7.9584 | -8.1063
|  | ELLIOT DEPOT | CF |  |  |  |  | -6.6329 | -6.8798 | -7.1329 | -7.3635 | -7.5369 | -7.6706 | -7.7604 | -7.8512 | -7.939 | -8.0288 | -8.6033 | -9.241 | -9.7512 | -5.9135 | -6.0869 | -6.241 | -6.3624 | -6.4798 | -6.5778 | -6.6604 | -6.7451 | -6.8196 | -6.9063 | -7.4114 | -7.9665 | -8.6369 | -6.341 | -6.5369 | -6.7278 | -6.8931 | -7.0237 | -7.1267 | -7.2124 | -7.2992 | -7.3778 | -7.4747
| DYCE | ELLON | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 2.433 | 25.9788 | 25.3084 | 24.4431 | 23.338 | 22.3808 | 20.2676 | 18.7818 | 16.8155 | 14.74 | 12.3063 | 6.6757 | 2.0216 | -1.9222 | 28.2022 | 27.7798 | 27.2655 | 26.4869 | 25.9502 | 24.1665 | 23.2002 | 21.7982 | 20.3155 | 18.3818 | 12.3318 | 9.4716 | 5.8522 | 27.5441 | 26.9216 | 26.1461 | 25.0839 | 24.24 | 22.1165 | 20.7655 | 18.9451 | 16.9971 | 14.6859
|  | ELLON | EE |  |  |  |  | 25.9788 | 25.3084 | 24.5767 | 23.7298 | 22.9278 | 21.3676 | 19.4227 | 17.6829 | 15.7002 | 13.6655 | 7.2584 | 2.9339 | 0.38082 | 28.2022 | 27.7798 | 27.3359 | 26.8084 | 26.3002 | 25.0635 | 23.6951 | 22.4645 | 20.9441 | 19.4073 | 14.7594 | 11.8859 | 9.8788 | 27.5441 | 26.9216 | 26.2604 | 25.488 | 24.7624 | 23.2431 | 21.4584 | 19.8584 | 17.9727 | 16.0604
|  | ELLON | HT |  |  |  |  | 26.0665 | 25.4033 | 24.4431 | 23.338 | 22.3808 | 20.2676 | 18.7818 | 16.8155 | 14.74 | 12.3063 | 6.6757 | 2.0216 | -1.6243 | 28.3033 | 27.9298 | 27.2655 | 26.4869 | 25.9502 | 24.1665 | 23.2002 | 21.7982 | 20.3155 | 18.3818 | 14.6522 | 11.6839 | 9.04 | 27.6553 | 27.0645 | 26.1461 | 25.0839 | 24.24 | 22.1165 | 20.7655 | 18.9451 | 16.9971 | 14.6859
|  | ELLON | HE |  |  |  |  | 26.1073 | 25.6829 | 25.0165 | 24.2104 | 23.3961 | 21.6757 | 20.2267 | 18.6104 | 16.8849 | 14.7451 | 7.2012 | 2.3808 | -1.9222 | 28.3216 | 28.0247 | 27.4839 | 26.8257 | 26.2451 | 24.7053 | 23.6431 | 22.3482 | 20.9573 | 18.9318 | 12.3318 | 9.4716 | 5.8522 | 27.692 | 27.2941 | 26.6298 | 25.8278 | 25.0635 | 23.3063 | 22.0022 | 20.4594 | 18.8155 | 16.6931
|  | ELLON | CF |  |  |  |  | 26.2971 | 26.0359 | 25.7482 | 25.4145 | 24.9318 | 24.1992 | 23.4002 | 22.7696 | 21.9573 | 20.9543 | 15.2359 | 9.8992 | 6.0696 | 28.4482 | 28.2431 | 28.0288 | 27.7747 | 27.388 | 26.7369 | 26.0594 | 25.5298 | 24.8135 | 23.9308 | 19.2431 | 15.6165 | 12.4778 | 27.8665 | 27.6124 | 27.342 | 27.0247 | 26.5584 | 25.8227 | 25.0563 | 24.492 | 23.7135 | 22.7543
| TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0 | 0.14314 | 0.13192 | 0.1309 | 0.12988 | 0.12478 | 0.12273 | 0.11865 | 0.11049 | 0.10539 | 0.095184 | 0.083959 | 0.086 | 0.068 | 0.15269 | 0.14453 | 0.14453 | 0.14453 | 0.14453 | 0.14453 | 0.14147 | 0.13433 | 0.13127 | 0.12616 | 0.11596 | 0.127 | 0.1168 | 0.15353 | 0.14333 | 0.14129 | 0.14027 | 0.13516 | 0.13312 | 0.12904 | 0.1219 | 0.11782 | 0.10761
|  | EREDINE | EE |  |  |  |  | 0.14314 | 0.13192 | 0.136 | 0.1309 | 0.12478 | 0.12273 | 0.11865 | 0.11049 | 0.10539 | 0.095184 | 0.083959 | 0.088041 | 0.070041 | 0.15269 | 0.14453 | 0.15371 | 0.15065 | 0.14453 | 0.14453 | 0.14147 | 0.13433 | 0.13127 | 0.12616 | 0.11596 | 0.12802 | 0.1219 | 0.15353 | 0.14333 | 0.14741 | 0.14231 | 0.13516 | 0.13312 | 0.12904 | 0.1219 | 0.11782 | 0.10761
|  | EREDINE | HT |  |  |  |  | 0.15029 | 0.14008 | 0.1309 | 0.12988 | 0.13294 | 0.12886 | 0.12478 | 0.12273 | 0.11253 | 0.11151 | 0.088041 | 0.086 | 0.068 | 0.16086 | 0.15167 | 0.14453 | 0.14759 | 0.15167 | 0.14861 | 0.14555 | 0.14453 | 0.13739 | 0.13637 | 0.12106 | 0.13006 | 0.12904 | 0.16067 | 0.15047 | 0.14129 | 0.14027 | 0.14435 | 0.13924 | 0.13516 | 0.13414 | 0.12394 | 0.12394
|  | EREDINE | HE |  |  |  |  | 0.15029 | 0.14008 | 0.13192 | 0.1309 | 0.13498 | 0.1309 | 0.12784 | 0.12682 | 0.11967 | 0.11661 | 0.090082 | 0.089061 | 0.071061 | 0.16086 | 0.15269 | 0.14453 | 0.14861 | 0.15269 | 0.14963 | 0.14657 | 0.14657 | 0.14147 | 0.14045 | 0.11902 | 0.12904 | 0.12394 | 0.16067 | 0.15149 | 0.14333 | 0.14129 | 0.14639 | 0.14231 | 0.13822 | 0.1372 | 0.13006 | 0.12802
|  | EREDINE | CF |  |  |  |  | 0.15029 | 0.14927 | 0.1411 | 0.13192 | 0.1309 | 0.136 | 0.12988 | 0.12682 | 0.12376 | 0.12273 | 0.10845 | 0.097224 | 0.073102 | 0.16086 | 0.15984 | 0.15167 | 0.14453 | 0.14861 | 0.15371 | 0.14963 | 0.14759 | 0.14453 | 0.14453 | 0.13229 | 0.127 | 0.1168 | 0.16067 | 0.15965 | 0.15251 | 0.14231 | 0.14129 | 0.14741 | 0.14231 | 0.13924 | 0.13516 | 0.13414
| INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | NO | 0.051 | 0.86837 | 0.8602 | 0.8602 | 0.85306 | 0.84286 | 0.83469 | 0.82857 | 0.81327 | 0.79898 | 0.78878 | 0.77959 | 0.77551 | 0.77245 | 0.9051 | 0.89796 | 0.9051 | 0.9 | 0.89286 | 0.88673 | 0.88265 | 0.87041 | 0.86122 | 0.85 | 0.84898 | 0.84082 | 0.82143 | 0.88469 | 0.87653 | 0.87857 | 0.87041 | 0.86224 | 0.85408 | 0.84898 | 0.83367 | 0.82041 | 0.8102
|  | ERROGIE | EE |  |  |  |  | 0.86837 | 0.86735 | 0.8602 | 0.85306 | 0.84286 | 0.83469 | 0.82857 | 0.81327 | 0.79898 | 0.78878 | 0.77959 | 0.77551 | 0.77347 | 0.90714 | 0.90918 | 0.9051 | 0.9 | 0.89286 | 0.88673 | 0.88265 | 0.87041 | 0.86122 | 0.85 | 0.84898 | 0.84286 | 0.83571 | 0.88469 | 0.88367 | 0.87857 | 0.87041 | 0.86224 | 0.85408 | 0.84898 | 0.83367 | 0.82041 | 0.8102
|  | ERROGIE | HT |  |  |  |  | 0.86837 | 0.86531 | 0.86327 | 0.85918 | 0.85408 | 0.84592 | 0.83776 | 0.83061 | 0.82245 | 0.81633 | 0.78673 | 0.77551 | 0.77245 | 0.9051 | 0.90612 | 0.90612 | 0.90408 | 0.90204 | 0.89592 | 0.89286 | 0.88776 | 0.87857 | 0.87551 | 0.85612 | 0.85 | 0.84796 | 0.88571 | 0.88163 | 0.88061 | 0.87653 | 0.87245 | 0.86429 | 0.85714 | 0.85 | 0.84286 | 0.83776
|  | ERROGIE | HE |  |  |  |  | 0.86939 | 0.86429 | 0.86531 | 0.86224 | 0.85918 | 0.85102 | 0.8449 | 0.83878 | 0.82857 | 0.82551 | 0.78878 | 0.78061 | 0.77857 | 0.90612 | 0.90612 | 0.90816 | 0.90612 | 0.90408 | 0.89694 | 0.89388 | 0.8898 | 0.88163 | 0.87653 | 0.85408 | 0.84592 | 0.83878 | 0.88673 | 0.88061 | 0.88265 | 0.88061 | 0.87653 | 0.86837 | 0.86327 | 0.85714 | 0.84796 | 0.84694
|  | ERROGIE | CF |  |  |  |  | 0.86939 | 0.8602 | 0.86837 | 0.86429 | 0.85918 | 0.85816 | 0.85408 | 0.84592 | 0.84184 | 0.83571 | 0.80408 | 0.78673 | 0.77653 | 0.90612 | 0.89796 | 0.90918 | 0.90816 | 0.90408 | 0.90306 | 0.90102 | 0.89286 | 0.89082 | 0.88469 | 0.8602 | 0.84082 | 0.82143 | 0.88673 | 0.87653 | 0.88469 | 0.88163 | 0.87755 | 0.87551 | 0.87143 | 0.86531 | 0.8602 | 0.8551
| ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 0.708 | 3.7429 | 3.5837 | 3.3306 | 2.8898 | 2.6306 | 1.8949 | 1.5551 | 1.1918 | 0.87041 | 0.4602 | -2.102 | -4.099 | -6.0867 | 4.7541 | 4.6612 | 4.4388 | 4.0439 | 3.902 | 3.1622 | 2.9224 | 2.599 | 2.3102 | 1.7908 | -0.55102 | -2.8306 | -5.2592 | 4.3653 | 4.2133 | 3.9276 | 3.4551 | 3.2235 | 2.3888 | 2.0694 | 1.7235 | 1.4459 | 0.85102
|  | ERROL | EE |  |  |  |  | 3.7429 | 3.5837 | 3.3622 | 3.148 | 2.7316 | 2.1684 | 1.7592 | 1.3918 | 0.87041 | 0.4602 | -0.7051 | -2.8541 | -3.6449 | 4.7541 | 4.6612 | 4.5255 | 4.402 | 4.0735 | 3.5735 | 3.2847 | 3.0653 | 2.6531 | 2.3622 | 1.5133 | -0.85408 | -1.8755 | 4.3653 | 4.2133 | 4.0031 | 3.8041 | 3.3827 | 2.7827 | 2.3816 | 2.0367 | 1.5051 | 1.101
|  | ERROL | HT |  |  |  |  | 3.8133 | 3.6592 | 3.3306 | 2.8898 | 2.6306 | 1.8949 | 1.5551 | 1.1918 | 0.92245 | 0.5602 | -1.399 | -3.5551 | -5.3541 | 4.7959 | 4.7286 | 4.4388 | 4.0439 | 3.902 | 3.1622 | 2.9551 | 2.7255 | 2.5806 | 2.3459 | 0.8398 | -1.5776 | -3.7459 | 4.4347 | 4.2878 | 3.9276 | 3.4551 | 3.2235 | 2.3888 | 2.0694 | 1.7235 | 1.4745 | 1.1286
|  | ERROL | HE |  |  |  |  | 3.8122 | 3.7082 | 3.449 | 3.0867 | 2.8112 | 2.1337 | 1.7602 | 1.3724 | 1.0296 | 0.48673 | -2.102 | -4.099 | -6.0867 | 4.7949 | 4.7418 | 4.502 | 4.1551 | 3.9357 | 3.2214 | 2.9224 | 2.599 | 2.3102 | 1.7908 | -0.55102 | -2.8306 | -5.2592 | 4.4327 | 4.3347 | 4.051 | 3.651 | 3.3704 | 2.5918 | 2.2102 | 1.8061 | 1.4459 | 0.85102
|  | ERROL | CF |  |  |  |  | 3.8398 | 3.7633 | 3.6602 | 3.5245 | 3.298 | 2.9796 | 2.7918 | 2.5816 | 2.3745 | 2.1306 | 1.0163 | 0.28776 | -0.51327 | 4.8061 | 4.7776 | 4.7102 | 4.6245 | 4.4327 | 4.1357 | 3.9714 | 3.7969 | 3.6214 | 3.4071 | 2.5316 | 1.899 | 1.1265 | 4.4633 | 4.3878 | 4.2929 | 4.1694 | 3.9347 | 3.5867 | 3.3878 | 3.1735 | 2.9592 | 2.7
| FASNAKYLE | FASNAKYLE | MINIMUM HEADROOM | NH 31948 29998 | YES | YES | 0.086 | 0.58776 | 0.57245 | 0.55 | 0.52449 | 0.51224 | 0.48265 | 0.45714 | 0.42347 | 0.38673 | 0.35714 | 0.32245 | 0.30714 | 0.30204 | 0.65714 | 0.64592 | 0.63163 | 0.6102 | 0.60102 | 0.58163 | 0.56735 | 0.54286 | 0.51633 | 0.49694 | 0.47347 | 0.45102 | 0.38163 | 0.6551 | 0.6398 | 0.61939 | 0.59388 | 0.58163 | 0.5551 | 0.53061 | 0.49796 | 0.46429 | 0.43673
|  | FASNAKYLE | EE |  |  |  |  | 0.58776 | 0.57245 | 0.55 | 0.52449 | 0.51224 | 0.48265 | 0.45714 | 0.42347 | 0.38673 | 0.35714 | 0.32245 | 0.31122 | 0.30714 | 0.65714 | 0.64592 | 0.63163 | 0.6102 | 0.60102 | 0.58163 | 0.56735 | 0.54286 | 0.51633 | 0.49694 | 0.47347 | 0.45204 | 0.42653 | 0.6551 | 0.6398 | 0.61939 | 0.59388 | 0.58163 | 0.5551 | 0.53061 | 0.49796 | 0.46429 | 0.43673
|  | FASNAKYLE | HT |  |  |  |  | 0.6 | 0.58571 | 0.56939 | 0.55 | 0.53469 | 0.5102 | 0.50204 | 0.47143 | 0.44286 | 0.42653 | 0.34388 | 0.30714 | 0.30204 | 0.66429 | 0.65714 | 0.64592 | 0.63265 | 0.62449 | 0.60918 | 0.60408 | 0.58367 | 0.56735 | 0.5551 | 0.50102 | 0.47959 | 0.47449 | 0.66633 | 0.65204 | 0.63673 | 0.61939 | 0.60306 | 0.58265 | 0.57143 | 0.54388 | 0.51837 | 0.50306
|  | FASNAKYLE | HE |  |  |  |  | 0.6 | 0.5898 | 0.57857 | 0.55816 | 0.54796 | 0.52551 | 0.51837 | 0.49082 | 0.46531 | 0.45306 | 0.35306 | 0.32551 | 0.32143 | 0.66429 | 0.65816 | 0.65 | 0.63469 | 0.62755 | 0.61327 | 0.60714 | 0.5898 | 0.56837 | 0.56224 | 0.49388 | 0.46224 | 0.43776 | 0.66633 | 0.65612 | 0.64388 | 0.62551 | 0.61531 | 0.59592 | 0.58776 | 0.56429 | 0.53776 | 0.52551
|  | FASNAKYLE | CF |  |  |  |  | 0.60204 | 0.5898 | 0.58163 | 0.56837 | 0.55918 | 0.54184 | 0.52449 | 0.51837 | 0.50204 | 0.48367 | 0.4 | 0.34898 | 0.31837 | 0.66633 | 0.65816 | 0.65 | 0.64184 | 0.63469 | 0.62449 | 0.6102 | 0.6051 | 0.59082 | 0.57653 | 0.50918 | 0.45102 | 0.38163 | 0.66837 | 0.65816 | 0.65 | 0.63878 | 0.62857 | 0.61327 | 0.59694 | 0.5898 | 0.57551 | 0.55612
| TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0 | 0.068 | 0.059837 | 0.049633 | 0.047592 | 0.046571 | 0.046571 | 0.041469 | 0.039429 | 0.033306 | 0.031265 | 0.021061 | 0.01902 | 0.009 | 0.072265 | 0.064102 | 0.056959 | 0.06002 | 0.055939 | 0.056959 | 0.054918 | 0.055939 | 0.050837 | 0.050837 | 0.044714 | 0.045133 | 0.041051 | 0.072684 | 0.065541 | 0.054316 | 0.054316 | 0.053296 | 0.053296 | 0.049214 | 0.048194 | 0.041051 | 0.03901
|  | FINCASTLE | EE |  |  |  |  | 0.068 | 0.059837 | 0.049633 | 0.047592 | 0.052694 | 0.047592 | 0.041469 | 0.039429 | 0.033306 | 0.031265 | 0.021061 | 0.021061 | 0.011041 | 0.072265 | 0.064102 | 0.056959 | 0.06002 | 0.064102 | 0.061041 | 0.055939 | 0.055939 | 0.050837 | 0.050837 | 0.044714 | 0.045133 | 0.043092 | 0.072684 | 0.065541 | 0.054316 | 0.054316 | 0.059418 | 0.054316 | 0.049214 | 0.048194 | 0.041051 | 0.03901
|  | FINCASTLE | HT |  |  |  |  | 0.068 | 0.068 | 0.057796 | 0.054735 | 0.046571 | 0.046571 | 0.049633 | 0.044531 | 0.04249 | 0.038408 | 0.025143 | 0.01902 | 0.009 | 0.072265 | 0.072265 | 0.064102 | 0.063082 | 0.055939 | 0.059 | 0.062061 | 0.05798 | 0.05798 | 0.054918 | 0.046755 | 0.048194 | 0.048194 | 0.072684 | 0.072684 | 0.06248 | 0.061459 | 0.053296 | 0.053296 | 0.056357 | 0.052276 | 0.050235 | 0.047173
|  | FINCASTLE | HE |  |  |  |  | 0.06902 | 0.068 | 0.065959 | 0.056776 | 0.049633 | 0.047592 | 0.046571 | 0.048612 | 0.047592 | 0.04351 | 0.030245 | 0.024122 | 0.014102 | 0.072265 | 0.072265 | 0.071245 | 0.064102 | 0.055939 | 0.06002 | 0.059 | 0.06002 | 0.06002 | 0.05798 | 0.050837 | 0.049214 | 0.046153 | 0.072684 | 0.072684 | 0.070643 | 0.06248 | 0.054316 | 0.053296 | 0.052276 | 0.055337 | 0.054316 | 0.051255
|  | FINCASTLE | CF |  |  |  |  | 0.077184 | 0.068 | 0.068 | 0.058816 | 0.057796 | 0.050653 | 0.048612 | 0.047592 | 0.053714 | 0.047592 | 0.038408 | 0.031265 | 0.015122 | 0.080429 | 0.072265 | 0.072265 | 0.064102 | 0.064102 | 0.056959 | 0.054918 | 0.059 | 0.064102 | 0.06002 | 0.054918 | 0.049214 | 0.041051 | 0.079827 | 0.072684 | 0.072684 | 0.0635 | 0.06248 | 0.055337 | 0.054316 | 0.054316 | 0.059418 | 0.054316
| SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 0.15 | -1.9316 | -2.7939 | -3.6694 | -4.548 | -5.449 | -6.3531 | -7.2663 | -8.1796 | -9.0827 | -9.1337 | -9.2857 | -9.3469 | -9.3765 | -1.6286 | -2.5755 | -3.5316 | -4.4888 | -5.4571 | -6.4286 | -7.4082 | -8.3888 | -9.3582 | -9.3796 | -9.4296 | -9.4602 | -9.4959 | -1.7541 | -2.6133 | -3.4827 | -4.3531 | -5.2378 | -6.1306 | -7.0296 | -7.9255 | -8.8133 | -8.8449
|  | FIRTH | EE |  |  |  |  | -1.9316 | -2.7939 | -3.6694 | -4.548 | -5.449 | -6.3531 | -7.2663 | -8.1796 | -9.0827 | -9.1337 | -9.2561 | -9.2643 | -9.2653 | -1.6286 | -2.5755 | -3.5316 | -4.4888 | -5.4571 | -6.4286 | -7.4082 | -8.3888 | -9.3582 | -9.3796 | -9.4296 | -9.4429 | -9.4704 | -1.7541 | -2.6133 | -3.4827 | -4.3531 | -5.2378 | -6.1306 | -7.0296 | -7.9255 | -8.8133 | -8.8449
|  | FIRTH | HT |  |  |  |  | -1.9235 | -2.7786 | -3.6449 | -4.5194 | -5.4163 | -6.3143 | -7.2143 | -8.1184 | -9.0276 | -9.0827 | -9.2378 | -9.2898 | -9.3143 | -1.6194 | -2.5673 | -3.5143 | -4.4704 | -5.4378 | -6.4041 | -7.3755 | -8.3469 | -9.3235 | -9.3449 | -9.4061 | -9.4306 | -9.4378 | -1.7469 | -2.6031 | -3.4684 | -4.3357 | -5.2214 | -6.1092 | -6.9959 | -7.8878 | -8.7816 | -8.8194
|  | FIRTH | HE |  |  |  |  | -1.9235 | -2.7776 | -3.6429 | -4.5163 | -5.4082 | -6.3061 | -7.2163 | -8.1255 | -9.0367 | -9.0898 | -9.2857 | -9.3469 | -9.3765 | -1.6204 | -2.5694 | -3.5194 | -4.4745 | -5.4429 | -6.4102 | -7.3867 | -8.3612 | -9.3327 | -9.3561 | -9.4276 | -9.4602 | -9.4959 | -1.748 | -2.602 | -3.4643 | -4.3316 | -5.2143 | -6.1 | -6.9949 | -7.8888 | -8.7827 | -8.8143
|  | FIRTH | CF |  |  |  |  | -1.9153 | -2.7582 | -3.6082 | -4.4663 | -5.3286 | -6.2 | -7.0755 | -7.951 | -8.8286 | -8.8602 | -9.0449 | -9.1847 | -9.2714 | -1.6204 | -2.5633 | -3.5112 | -4.4653 | -5.4204 | -6.3837 | -7.3469 | -8.3112 | -9.2745 | -9.2949 | -9.3704 | -9.4316 | -9.4939 | -1.7408 | -2.5847 | -3.4367 | -4.2939 | -5.1551 | -6.0235 | -6.8959 | -7.7684 | -8.6429 | -8.6653
| FORT WILLIAM | FISHNISH | MINIMUM HEADROOM | NM 66623 42191 | YES | NO | 0 | 0.23192 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.22886 | 0.22886 | 0.22784 | 0.22784 | 0.22784 | 0.22478 | 0.22376 | 0.20576 | 0.21494 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.2129 | 0.2129 | 0.21188 | 0.21188 | 0.21188 | 0.20984 | 0.21782 | 0.21782 | 0.22394 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22088 | 0.22088 | 0.21986 | 0.21986 | 0.21986
|  | FISHNISH | EE |  |  |  |  | 0.23192 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.22886 | 0.22886 | 0.22784 | 0.22784 | 0.22784 | 0.22682 | 0.22682 | 0.20882 | 0.21494 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.2129 | 0.2129 | 0.21188 | 0.21188 | 0.21188 | 0.21086 | 0.21986 | 0.21986 | 0.22394 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22088 | 0.22088 | 0.21986 | 0.21986 | 0.21986
|  | FISHNISH | HT |  |  |  |  | 0.23192 | 0.23192 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.22886 | 0.22886 | 0.22886 | 0.22784 | 0.22682 | 0.22478 | 0.20678 | 0.21494 | 0.21494 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.2129 | 0.2129 | 0.2129 | 0.21188 | 0.21086 | 0.21884 | 0.21884 | 0.22394 | 0.22394 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22088 | 0.22088 | 0.22088 | 0.21986
|  | FISHNISH | HE |  |  |  |  | 0.23192 | 0.23192 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.22886 | 0.22886 | 0.22784 | 0.22784 | 0.22478 | 0.22376 | 0.20576 | 0.21494 | 0.21494 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.2129 | 0.2129 | 0.21188 | 0.21188 | 0.20984 | 0.21782 | 0.21782 | 0.22394 | 0.22394 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22088 | 0.22088 | 0.21986 | 0.21986
|  | FISHNISH | CF |  |  |  |  | 0.23192 | 0.23192 | 0.23192 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.22886 | 0.22886 | 0.22784 | 0.22478 | 0.20678 | 0.21494 | 0.21494 | 0.21494 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.2129 | 0.2129 | 0.21188 | 0.21884 | 0.21884 | 0.22394 | 0.22394 | 0.22394 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22088 | 0.22088
| THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | NO | 0 | 0.67245 | 0.66531 | 0.66531 | 0.66122 | 0.65612 | 0.64592 | 0.63571 | 0.63061 | 0.61735 | 0.60714 | 0.58571 | 0.57959 | 0.57551 | 0.13367 | 0.12653 | 0.13163 | 0.12755 | 0.12347 | 0.11735 | 0.11122 | 0.10612 | 0.096939 | 0.089796 | 0.072449 | 0.071429 | 0.066327 | 0.81735 | 0.8102 | 0.8051 | 0.80204 | 0.7949 | 0.78776 | 0.77857 | 0.77245 | 0.75918 | 0.75
|  | FLOTTA | EE |  |  |  |  | 0.67245 | 0.67245 | 0.66531 | 0.66122 | 0.65612 | 0.64592 | 0.63571 | 0.63061 | 0.61735 | 0.60714 | 0.58571 | 0.58265 | 0.57959 | 0.13367 | 0.13673 | 0.13163 | 0.12755 | 0.12347 | 0.11735 | 0.11122 | 0.10612 | 0.096939 | 0.089796 | 0.072449 | 0.071429 | 0.066327 | 0.81735 | 0.81224 | 0.8051 | 0.80204 | 0.7949 | 0.78776 | 0.77857 | 0.77245 | 0.75918 | 0.75
|  | FLOTTA | HT |  |  |  |  | 0.67755 | 0.66531 | 0.67347 | 0.66837 | 0.66122 | 0.6602 | 0.6551 | 0.64388 | 0.63776 | 0.62959 | 0.59286 | 0.57959 | 0.57755 | 0.13367 | 0.12653 | 0.13878 | 0.13571 | 0.12755 | 0.12755 | 0.12551 | 0.11837 | 0.11224 | 0.10612 | 0.078571 | 0.071429 | 0.070408 | 0.82041 | 0.8102 | 0.81531 | 0.81122 | 0.80306 | 0.80204 | 0.79796 | 0.78878 | 0.77959 | 0.77143
|  | FLOTTA | HE |  |  |  |  | 0.67755 | 0.66735 | 0.67449 | 0.66939 | 0.66735 | 0.66327 | 0.65714 | 0.64796 | 0.64082 | 0.62959 | 0.59184 | 0.58061 | 0.57551 | 0.13367 | 0.12653 | 0.13878 | 0.13571 | 0.13163 | 0.12959 | 0.12653 | 0.12143 | 0.11429 | 0.10918 | 0.081633 | 0.07551 | 0.069388 | 0.82041 | 0.81327 | 0.81633 | 0.81122 | 0.80816 | 0.80408 | 0.8 | 0.79082 | 0.78265 | 0.77653
|  | FLOTTA | CF |  |  |  |  | 0.68571 | 0.67653 | 0.67245 | 0.67653 | 0.67041 | 0.66633 | 0.66531 | 0.65918 | 0.65714 | 0.64898 | 0.62653 | 0.59898 | 0.58061 | 0.14286 | 0.13367 | 0.13367 | 0.13878 | 0.13571 | 0.13265 | 0.13163 | 0.12551 | 0.12347 | 0.12041 | 0.10204 | 0.078571 | 0.069388 | 0.82857 | 0.81939 | 0.81735 | 0.81633 | 0.81224 | 0.80918 | 0.80816 | 0.80306 | 0.80102 | 0.79388
| ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 3.349 | 5.6194 | 5.3327 | 5.002 | 4.6459 | 4.2469 | 3.5153 | 2.4429 | 1.4337 | 0.49388 | -0.59082 | -4.9745 | -6.2133 | -7.2388 | 6.4184 | 6.2265 | 6.0061 | 5.7622 | 5.4918 | 4.8694 | 3.9439 | 3.05 | 2.1918 | 1.2837 | -2.35 | -2.8332 | -3.0087 | 6.2087 | 5.9434 | 5.6311 | 5.2903 | 4.9117 | 4.1872 | 3.1648 | 2.1862 | 1.2872 | 0.32602
|  | FOCHABERS | EE |  |  |  |  | 5.6194 | 5.3327 | 5.002 | 4.6459 | 4.2469 | 3.5153 | 2.4429 | 1.4337 | 0.49388 | -0.30306 | -4.5469 | -5.0112 | -5.8612 | 6.4184 | 6.2265 | 6.0061 | 5.7622 | 5.4918 | 4.8694 | 3.9439 | 3.1082 | 2.3388 | 1.6857 | -1.8337 | -1.6893 | -1.7505 | 6.2087 | 5.9434 | 5.6311 | 5.2903 | 4.9117 | 4.1872 | 3.1648 | 2.1862 | 1.2872 | 0.5199
|  | FOCHABERS | HT |  |  |  |  | 5.7714 | 5.548 | 5.2969 | 5.0235 | 4.7173 | 3.8551 | 2.6408 | 1.551 | 0.51939 | -0.59082 | -3.9622 | -4.8969 | -5.7949 | 6.5357 | 6.3939 | 6.2398 | 6.0643 | 5.8684 | 5.0837 | 3.9918 | 3.05 | 2.1918 | 1.2837 | -1.3806 | -1.5862 | -1.6781 | 6.3699 | 6.1648 | 5.9372 | 5.6821 | 5.4189 | 4.5872 | 3.4189 | 2.3689 | 1.3832 | 0.32602
|  | FOCHABERS | HE |  |  |  |  | 5.7316 | 5.4959 | 5.248 | 4.9622 | 4.6327 | 3.9316 | 2.9082 | 1.9245 | 0.98673 | -0.02449 | -4.9745 | -6.2133 | -7.2388 | 6.5051 | 6.3398 | 6.1673 | 5.9663 | 5.7357 | 5.1214 | 4.2276 | 3.4194 | 2.6306 | 1.7816 | -2.35 | -2.8332 | -3.0087 | 6.327 | 6.0995 | 5.8536 | 5.5709 | 5.2403 | 4.5352 | 3.5444 | 2.6046 | 1.7046 | 0.73622
|  | FOCHABERS | CF |  |  |  |  | 5.8122 | 5.6745 | 5.5143 | 5.3418 | 5.1449 | 4.8245 | 4.3816 | 3.8959 | 3.4398 | 2.9071 | -0.8898 | -4.3449 | -6.3949 | 6.5592 | 6.4633 | 6.3541 | 6.2357 | 6.0929 | 5.8265 | 5.4398 | 5.0265 | 4.6398 | 4.2071 | 1.0031 | -1.5505 | -2.4587 | 6.4026 | 6.277 | 6.125 | 5.9587 | 5.7628 | 5.4413 | 5.0036 | 4.5128 | 4.0546 | 3.5383
| NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 2.073 | 2.6471 | 1.8084 | 0.93489 | 23.4022 | 22.2084 | 21.242 | 19.738 | 18.1726 | 16.6471 | 15.189 | 8.5012 | 5.6012 | -19.1814 | 6.341 | 5.9614 | 28.3767 | 27.591 | 26.6716 | 25.7788 | 24.6849 | 23.4359 | 22.2522 | 21.1767 | 15.7186 | -8.8768 | -9.1748 | 4.6844 | 27.542 | 26.6757 | 25.6716 | 24.5502 | 23.4665 | 22.1084 | 20.5624 | 19.1084 | 17.7747
|  | FORRES | EE |  |  |  |  | 2.6471 | 1.8084 | 0.93489 | 23.4022 | 22.2084 | 21.242 | 19.738 | 18.1726 | 16.6471 | 15.189 | 8.6196 | 6.4482 | -18.2835 | 6.341 | 5.9614 | 28.3767 | 27.591 | 26.6716 | 25.7788 | 24.6849 | 23.4359 | 22.2522 | 21.1767 | 17.1359 | -6.0789 | -6.7309 | 4.6844 | 27.542 | 26.6757 | 25.6716 | 24.5502 | 23.4665 | 22.1084 | 20.5624 | 19.1084 | 17.7747
|  | FORRES | HT |  |  |  |  | 2.8349 | 2.0696 | 1.2594 | 23.7971 | 22.6828 | 21.4543 | 19.9482 | 18.6135 | 16.9737 | 15.2533 | 9.1186 | 6.5063 | -18.1284 | 6.5216 | 6.1859 | 28.6624 | 28.0084 | 27.2931 | 26.4808 | 25.4961 | 24.4482 | 23.288 | 22.1563 | 18.3053 | -5.7381 | -5.8768 | 4.9915 | 27.938 | 27.2002 | 26.2859 | 25.2828 | 24.1696 | 22.8073 | 21.6277 | 20.1482 | 18.6237
|  | FORRES | HE |  |  |  |  | 2.8502 | 2.1992 | 1.5431 | 24.2298 | 23.2798 | 22.1084 | 20.7196 | 19.2471 | 17.69 | 16.0818 | 8.5012 | 5.6012 | -19.1814 | 6.5502 | 6.2135 | 28.7471 | 28.039 | 27.1849 | 26.2135 | 25.1298 | 23.9757 | 22.7431 | 21.4777 | 15.7186 | -8.8768 | -9.1748 | 4.9446 | 27.8808 | 27.1767 | 26.2951 | 25.2839 | 24.1216 | 22.8043 | 21.4033 | 19.9206 | 18.3808
|  | FORRES | CF |  |  |  |  | 3.1431 | 2.7308 | 2.2982 | 25.3063 | 24.7206 | 24.0645 | 23.4145 | 22.6982 | 21.9502 | 21.1808 | 15.2941 | 9.8451 | -17.4131 | 6.6788 | 6.4828 | 29.2655 | 28.9043 | 28.4788 | 28.0063 | 27.4573 | 26.7441 | 26.0635 | 25.4349 | 20.7777 | -6.0615 | -8.1289 | 5.2834 | 28.5053 | 28.0645 | 27.5492 | 26.9624 | 26.291 | 25.5982 | 24.7543 | 23.9584 | 23.2247
| DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | NO | 0.795 | -0.82041 | -0.88776 | -0.9602 | -1.0378 | -1.1153 | -1.2 | -1.2918 | -1.3908 | -1.4918 | -1.5827 | -1.9551 | -2.1194 | -2.2112 | -0.60714 | -0.66224 | -0.72041 | -0.77755 | -0.83367 | -0.89592 | -0.96224 | -1.0316 | -1.0969 | -1.152 | -1.4153 | -1.5378 | -1.6112 | -1.0949 | -1.1316 | -1.1908 | -1.2602 | -1.3337 | -1.4122 | -1.5041 | -1.6082 | -1.7071 | -1.7939
|  | FORSS | EE |  |  |  |  | -0.82041 | -0.88776 | -0.9602 | -1.0378 | -1.1153 | -1.2 | -1.2918 | -1.3908 | -1.4918 | -1.5827 | -1.8582 | -1.8918 | -1.898 | -0.60714 | -0.66224 | -0.72041 | -0.77755 | -0.83367 | -0.89592 | -0.96224 | -1.0316 | -1.0969 | -1.152 | -1.3316 | -1.3561 | -1.3633 | -1.0949 | -1.1316 | -1.1908 | -1.2602 | -1.3337 | -1.4122 | -1.5041 | -1.6082 | -1.7071 | -1.7939
|  | FORSS | HT |  |  |  |  | -0.80306 | -0.86531 | -0.92143 | -0.98571 | -1.0459 | -1.1122 | -1.1816 | -1.2673 | -1.3449 | -1.4214 | -1.8041 | -1.9612 | -2.0408 | -0.5898 | -0.63776 | -0.69082 | -0.74082 | -0.78367 | -0.83163 | -0.87857 | -0.93776 | -0.99388 | -1.0439 | -1.2969 | -1.4102 | -1.4684 | -1.0765 | -1.1102 | -1.1561 | -1.2092 | -1.2663 | -1.3286 | -1.3959 | -1.4735 | -1.552 | -1.6286
|  | FORSS | HE |  |  |  |  | -0.80306 | -0.85408 | -0.91224 | -0.97347 | -1.0327 | -1.1031 | -1.1786 | -1.2714 | -1.3622 | -1.4612 | -1.9551 | -2.1194 | -2.2112 | -0.5898 | -0.63776 | -0.68571 | -0.73571 | -0.77959 | -0.83265 | -0.88571 | -0.9551 | -1.0173 | -1.0765 | -1.4153 | -1.5378 | -1.6112 | -1.0776 | -1.1061 | -1.1459 | -1.2041 | -1.2612 | -1.3276 | -1.398 | -1.4929 | -1.5867 | -1.6796
|  | FORSS | CF |  |  |  |  | -0.80102 | -0.83061 | -0.86224 | -0.89388 | -0.93776 | -0.97959 | -1.0306 | -1.0888 | -1.1459 | -1.2041 | -1.5663 | -1.898 | -2.1041 | -0.59082 | -0.60816 | -0.63265 | -0.66429 | -0.69796 | -0.72857 | -0.76735 | -0.80918 | -0.85 | -0.89388 | -1.1408 | -1.3816 | -1.5296 | -1.0776 | -1.0918 | -1.1122 | -1.1347 | -1.1643 | -1.2031 | -1.252 | -1.3051 | -1.3592 | -1.4163
| BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 0.231 | 4.9371 | 4.6095 | 4.384 | 4.2085 | 4.0564 | 3.9371 | 3.7626 | 3.6207 | 3.4616 | 3.3207 | 2.8238 | 2.5575 | 1.9374 | 5.0548 | 4.7894 | 4.6007 | 4.4639 | 4.3517 | 4.2527 | 4.1343 | 4.0343 | 3.9384 | 3.8507 | 3.569 | 3.7648 | 3.5546 | 5.1107 | 4.8138 | 4.6056 | 4.4464 | 4.3056 | 4.1617 | 4.0056 | 3.8648 | 3.726 | 3.5995
|  | FORTEVIOT | EE |  |  |  |  | 5.0228 | 4.7034 | 4.4718 | 4.2789 | 4.0993 | 3.9371 | 3.7626 | 3.6207 | 3.4616 | 3.3207 | 2.8238 | 2.5779 | 1.9588 | 5.1221 | 4.868 | 4.6752 | 4.518 | 4.3792 | 4.2527 | 4.1343 | 4.0343 | 3.9384 | 3.8507 | 3.569 | 3.7648 | 3.6138 | 5.1852 | 4.8903 | 4.675 | 4.4903 | 4.3209 | 4.1617 | 4.0056 | 3.8648 | 3.726 | 3.5995
|  | FORTEVIOT | HT |  |  |  |  | 4.9371 | 4.6095 | 4.384 | 4.2085 | 4.0564 | 3.9401 | 3.8126 | 3.683 | 3.5513 | 3.4493 | 2.8687 | 2.5575 | 1.9374 | 5.0548 | 4.7894 | 4.6007 | 4.4639 | 4.3517 | 4.2711 | 4.1986 | 4.118 | 4.0456 | 3.9792 | 3.6517 | 3.7954 | 3.7505 | 5.1107 | 4.8138 | 4.6056 | 4.4464 | 4.3056 | 4.1985 | 4.0832 | 3.9597 | 3.8383 | 3.7423
|  | FORTEVIOT | HE |  |  |  |  | 5.0381 | 4.7422 | 4.5483 | 4.386 | 4.2401 | 4.1289 | 4.0085 | 3.8983 | 3.7891 | 3.7075 | 3.1452 | 2.8595 | 2.1762 | 5.1354 | 4.8915 | 4.7221 | 4.5782 | 4.4548 | 4.3578 | 4.2619 | 4.1711 | 4.0884 | 4.016 | 3.6476 | 3.7944 | 3.7117 | 5.2015 | 4.926 | 4.7413 | 4.5811 | 4.4383 | 4.3219 | 4.1995 | 4.0791 | 3.9668 | 3.8689
|  | FORTEVIOT | CF |  |  |  |  | 5.2667 | 5.1064 | 4.9718 | 4.8493 | 4.7218 | 4.6013 | 4.5064 | 4.3962 | 4.3116 | 4.2197 | 3.7493 | 3.2677 | 2.4201 | 5.3282 | 5.1946 | 5.0823 | 4.9884 | 4.8915 | 4.7935 | 4.7119 | 4.618 | 4.5435 | 4.4639 | 4.0517 | 3.9444 | 3.5546 | 5.4117 | 5.2617 | 5.1342 | 5.025 | 4.9087 | 4.7944 | 4.6995 | 4.5923 | 4.5046 | 4.4107
| INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | NO | 0.237 | 0.53624 | 0.52808 | 0.52196 | 0.50971 | 0.48931 | 0.48216 | 0.46073 | 0.43727 | 0.43522 | 0.41584 | 0.37706 | 0.36278 | 0.35767 | 0.60053 | 0.59849 | 0.59543 | 0.58727 | 0.574 | 0.56992 | 0.55767 | 0.53522 | 0.53624 | 0.52604 | 0.49747 | 0.48829 | 0.45257 | 0.56073 | 0.55563 | 0.54849 | 0.53522 | 0.51686 | 0.51176 | 0.49339 | 0.4689 | 0.46482 | 0.44849
|  | FOYERS | EE |  |  |  |  | 0.53829 | 0.52808 | 0.52196 | 0.50971 | 0.48931 | 0.48216 | 0.46073 | 0.43727 | 0.43522 | 0.41584 | 0.37706 | 0.36686 | 0.36482 | 0.60461 | 0.59849 | 0.59543 | 0.58727 | 0.574 | 0.56992 | 0.55767 | 0.53522 | 0.53624 | 0.52604 | 0.49747 | 0.48829 | 0.474 | 0.5638 | 0.55563 | 0.54849 | 0.53522 | 0.51686 | 0.51176 | 0.49339 | 0.4689 | 0.46482 | 0.44849
|  | FOYERS | HT |  |  |  |  | 0.53624 | 0.53727 | 0.52706 | 0.51788 | 0.51176 | 0.49645 | 0.48216 | 0.47298 | 0.45563 | 0.43829 | 0.38727 | 0.36278 | 0.35767 | 0.60053 | 0.60563 | 0.59951 | 0.59441 | 0.59135 | 0.58216 | 0.574 | 0.56686 | 0.55563 | 0.54645 | 0.51278 | 0.49951 | 0.49645 | 0.56176 | 0.56278 | 0.55359 | 0.54441 | 0.53931 | 0.52706 | 0.5138 | 0.50359 | 0.48624 | 0.47196
|  | FOYERS | HE |  |  |  |  | 0.53624 | 0.53931 | 0.52808 | 0.52502 | 0.52094 | 0.50767 | 0.49543 | 0.48727 | 0.47094 | 0.45563 | 0.39543 | 0.37502 | 0.36992 | 0.60053 | 0.60563 | 0.59951 | 0.59645 | 0.59441 | 0.58522 | 0.57706 | 0.56992 | 0.55971 | 0.54951 | 0.50767 | 0.49339 | 0.47808 | 0.56073 | 0.56584 | 0.55665 | 0.55257 | 0.54645 | 0.53318 | 0.52298 | 0.51686 | 0.50053 | 0.48727
|  | FOYERS | CF |  |  |  |  | 0.54543 | 0.5342 | 0.53522 | 0.52604 | 0.51992 | 0.51788 | 0.50767 | 0.49747 | 0.49339 | 0.4842 | 0.44339 | 0.39543 | 0.374 | 0.60869 | 0.60257 | 0.60461 | 0.59849 | 0.59339 | 0.58931 | 0.58522 | 0.57604 | 0.574 | 0.56482 | 0.53216 | 0.48931 | 0.45257 | 0.57094 | 0.56073 | 0.56176 | 0.55359 | 0.54849 | 0.54543 | 0.53624 | 0.52502 | 0.52298 | 0.51482
| FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | YES | 4.602 | 17.1528 | 16.0742 | 14.9467 | 13.711 | 12.3222 | 10.7875 | 9.2957 | 7.4395 | 5.4038 | 3.1589 | -2.6798 | -5.5594 | -7.3574 | 21.3538 | 20.5967 | 19.7844 | 18.8773 | 17.8426 | 16.6518 | 15.664 | 14.3702 | 12.9212 | 11.2548 | 7.6559 | 7.0446 | 5.46 | 19.3742 | 18.3997 | 17.363 | 16.2069 | 14.9018 | 13.4416 | 12.0712 | 10.3457 | 8.464 | 6.3763
|  | FRASERBURGH | EE |  |  |  |  | 17.161 | 16.114 | 15.0977 | 13.8885 | 12.7987 | 11.4008 | 9.6814 | 7.9232 | 6.1089 | 4.164 | -2.6503 | -5.29 | -7.1217 | 21.36 | 20.614 | 19.8814 | 18.9916 | 18.1957 | 17.1232 | 15.8763 | 14.6263 | 13.3538 | 11.9426 | 7.6559 | 7.0446 | 5.8181 | 19.3742 | 18.4079 | 17.4487 | 16.314 | 15.3497 | 14.0304 | 12.412 | 10.7681 | 9.1018 | 7.3069
|  | FRASERBURGH | HT |  |  |  |  | 17.1528 | 16.0742 | 14.9467 | 13.711 | 12.3222 | 10.7875 | 9.2957 | 7.4395 | 5.4038 | 3.1589 | -2.6798 | -5.5594 | -7.3574 | 21.3538 | 20.5967 | 19.7844 | 18.8773 | 17.8426 | 16.6518 | 15.664 | 14.3702 | 12.9212 | 11.2548 | 8.0875 | 7.8814 | 7.5589 | 19.3875 | 18.3997 | 17.363 | 16.2069 | 14.9018 | 13.4416 | 12.0712 | 10.3457 | 8.464 | 6.3763
|  | FRASERBURGH | HE |  |  |  |  | 17.2742 | 16.4487 | 15.6702 | 14.6957 | 13.6048 | 12.4151 | 11.01 | 9.8151 | 8.3365 | 6.6906 | 0.21199 | -2.8543 | -5.1288 | 21.4518 | 20.813 | 20.1957 | 19.4375 | 18.5732 | 17.5926 | 16.462 | 15.3763 | 14.1426 | 12.7446 | 8.3222 | 7.9406 | 6.5538 | 19.4967 | 18.7385 | 18.0151 | 17.1089 | 16.0814 | 14.9467 | 13.6079 | 12.4997 | 11.1089 | 9.562
|  | FRASERBURGH | CF |  |  |  |  | 17.563 | 17.0661 | 16.5875 | 16.0355 | 15.4059 | 14.6671 | 13.9355 | 13.0957 | 12.5385 | 11.6436 | 6.0671 | 1.1048 | -2.8962 | 21.6844 | 21.3028 | 20.912 | 20.4814 | 19.9753 | 19.361 | 18.7232 | 17.9834 | 17.4773 | 16.6895 | 12.1467 | 8.7742 | 5.46 | 19.7671 | 19.313 | 18.8702 | 18.361 | 17.7763 | 17.0865 | 16.3936 | 15.5967 | 15.0763 | 14.2304
| LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | YES | 0.22 | 2.6857 | 2.5724 | 2.4378 | 2.2796 | 2.1418 | 1.9776 | 1.75 | 1.552 | 1.3265 | 1.1214 | 0.48469 | 0.11327 | 0.032653 | 4.0357 | 3.9694 | 3.8847 | 3.7816 | 3.701 | 3.5908 | 3.4469 | 3.3347 | 3.1918 | 3.0673 | 2.7102 | 2.5255 | 2.1816 | 3.299 | 3.1969 | 3.0694 | 2.9214 | 2.7959 | 2.6408 | 2.4224 | 2.2449 | 2.0276 | 1.8357
|  | FRIOCKHEIM | EE |  |  |  |  | 2.6857 | 2.5724 | 2.4378 | 2.2796 | 2.1418 | 1.9776 | 1.75 | 1.552 | 1.3265 | 1.1214 | 0.48469 | 0.17041 | 0.10102 | 4.0357 | 3.9694 | 3.8847 | 3.7816 | 3.701 | 3.5908 | 3.4469 | 3.3347 | 3.1918 | 3.0673 | 2.7102 | 2.5255 | 2.3224 | 3.299 | 3.1969 | 3.0694 | 2.9214 | 2.7959 | 2.6408 | 2.4224 | 2.2449 | 2.0276 | 1.8357
|  | FRIOCKHEIM | HT |  |  |  |  | 2.7245 | 2.6163 | 2.5061 | 2.3776 | 2.2327 | 2.0949 | 1.9357 | 1.7439 | 1.55 | 1.351 | 0.53878 | 0.11327 | 0.032653 | 4.0745 | 4.0184 | 3.9551 | 3.8888 | 3.8102 | 3.7224 | 3.649 | 3.5347 | 3.4194 | 3.3 | 2.8306 | 2.6347 | 2.599 | 3.3388 | 3.2418 | 3.1388 | 3.0276 | 2.8959 | 2.7643 | 2.6286 | 2.448 | 2.2673 | 2.0806
|  | FRIOCKHEIM | HE |  |  |  |  | 2.7255 | 2.6663 | 2.5827 | 2.499 | 2.3898 | 2.2827 | 2.1755 | 2.0235 | 1.8724 | 1.7163 | 0.91531 | 0.50612 | 0.31837 | 4.0714 | 4.0357 | 3.9765 | 3.9255 | 3.8561 | 3.7806 | 3.7102 | 3.6051 | 3.5061 | 3.4031 | 2.9122 | 2.6653 | 2.4327 | 3.3388 | 3.2714 | 3.1969 | 3.1143 | 3.0163 | 2.9153 | 2.798 | 2.6469 | 2.5061 | 2.3571
|  | FRIOCKHEIM | CF |  |  |  |  | 2.7459 | 2.699 | 2.6418 | 2.5704 | 2.5163 | 2.4439 | 2.3582 | 2.2939 | 2.2082 | 2.1214 | 1.6184 | 1.0469 | 0.67041 | 4.0837 | 4.049 | 4.0102 | 3.9561 | 3.9194 | 3.8653 | 3.8 | 3.752 | 3.6857 | 3.6143 | 3.2316 | 2.7327 | 2.1816 | 3.3582 | 3.3153 | 3.2602 | 3.1939 | 3.1429 | 3.0745 | 2.9939 | 2.9296 | 2.8449 | 2.7561
| KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 0.484 | 3.3335 | 3.2345 | 3.1029 | 2.9518 | 2.8233 | 2.6631 | 2.4794 | 2.3273 | 2.1529 | 2.0008 | 1.5529 | 1.4304 | 1.3733 | 4.7131 | 4.6294 | 4.5243 | 4.3916 | 4.2804 | 4.1437 | 3.9937 | 3.8804 | 3.7467 | 3.6294 | 3.3518 | 3.2498 | 2.9539 | 4.1243 | 3.9927 | 3.8416 | 3.6682 | 3.509 | 3.3273 | 3.0998 | 2.9243 | 2.7202 | 2.5437
|  | FYVIE | EE |  |  |  |  | 3.3335 | 3.2345 | 3.1029 | 2.9518 | 2.8233 | 2.6631 | 2.4794 | 2.3273 | 2.1529 | 2.0008 | 1.5529 | 1.4794 | 1.4467 | 4.7131 | 4.6294 | 4.5243 | 4.3916 | 4.2804 | 4.1437 | 3.9937 | 3.8804 | 3.7467 | 3.6294 | 3.3518 | 3.2498 | 3.1069 | 4.1243 | 3.9927 | 3.8416 | 3.6682 | 3.509 | 3.3273 | 3.0998 | 2.9243 | 2.7202 | 2.5437
|  | FYVIE | HT |  |  |  |  | 3.3794 | 3.3029 | 3.1855 | 3.0804 | 2.9457 | 2.8182 | 2.7304 | 2.5824 | 2.4243 | 2.262 | 1.6947 | 1.4304 | 1.3733 | 4.7467 | 4.6733 | 4.5671 | 4.4671 | 4.3447 | 4.2355 | 4.1641 | 4.059 | 3.96 | 3.86 | 3.4916 | 3.3518 | 3.3253 | 4.1437 | 4.0253 | 3.8733 | 3.7171 | 3.5355 | 3.3814 | 3.2559 | 3.109 | 2.9661 | 2.8222
|  | FYVIE | HE |  |  |  |  | 3.3824 | 3.3161 | 3.2192 | 3.1324 | 3.0171 | 2.8988 | 2.8039 | 2.6733 | 2.5498 | 2.4182 | 1.7406 | 1.5508 | 1.512 | 4.7498 | 4.6876 | 4.6029 | 4.5212 | 4.4171 | 4.3141 | 4.2294 | 4.1263 | 4.0324 | 3.9294 | 3.462 | 3.2927 | 3.1529 | 4.1498 | 4.061 | 3.9467 | 3.8324 | 3.6998 | 3.5631 | 3.4304 | 3.2957 | 3.1671 | 3.0314
|  | FYVIE | CF |  |  |  |  | 3.4039 | 3.3508 | 3.2865 | 3.2294 | 3.1508 | 3.0692 | 2.9773 | 2.908 | 2.8182 | 2.7243 | 2.2641 | 1.811 | 1.5855 | 4.7671 | 4.7171 | 4.661 | 4.6049 | 4.5314 | 4.4569 | 4.3733 | 4.312 | 4.2355 | 4.1569 | 3.7529 | 3.3059 | 2.9539 | 4.1712 | 4.0978 | 4.0171 | 3.9386 | 3.8416 | 3.7467 | 3.6376 | 3.5508 | 3.4569 | 3.358
| GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | NO | 0 | 0.11698 | 0.11596 | 0.11596 | 0.11596 | 0.11392 | 0.11392 | 0.11392 | 0.1129 | 0.1129 | 0.11188 | 0.10984 | 0.10882 | 0.098796 | 0.10798 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10636 | 0.10534 | 0.11248 | 0.11146 | 0.11146 | 0.11146 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10738
|  | GARBAT FOREST | EE |  |  |  |  | 0.11698 | 0.11596 | 0.11596 | 0.11596 | 0.11392 | 0.11392 | 0.11392 | 0.1129 | 0.1129 | 0.11188 | 0.10984 | 0.10984 | 0.10084 | 0.10798 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10738 | 0.10738 | 0.11248 | 0.11146 | 0.11146 | 0.11146 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10738
|  | GARBAT FOREST | HT |  |  |  |  | 0.11698 | 0.11698 | 0.11596 | 0.11596 | 0.11596 | 0.11596 | 0.11392 | 0.11392 | 0.11392 | 0.1129 | 0.10984 | 0.10984 | 0.10084 | 0.10798 | 0.10798 | 0.10696 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10288 | 0.10738 | 0.10738 | 0.11248 | 0.11248 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.10942 | 0.10942 | 0.10942 | 0.1084
|  | GARBAT FOREST | HE |  |  |  |  | 0.11698 | 0.11698 | 0.11596 | 0.11596 | 0.11596 | 0.11392 | 0.11392 | 0.11392 | 0.1129 | 0.1129 | 0.10984 | 0.10882 | 0.098796 | 0.10798 | 0.10798 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10288 | 0.10636 | 0.10534 | 0.11248 | 0.11248 | 0.11146 | 0.11146 | 0.11146 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084
|  | GARBAT FOREST | CF |  |  |  |  | 0.11698 | 0.11698 | 0.11698 | 0.11596 | 0.11596 | 0.11596 | 0.11596 | 0.11596 | 0.11392 | 0.11392 | 0.11188 | 0.10984 | 0.099816 | 0.10798 | 0.10798 | 0.10798 | 0.10696 | 0.10696 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.1039 | 0.10738 | 0.10636 | 0.11248 | 0.11248 | 0.11248 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.10942 | 0.10942
| STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | 0.097 | -0.73265 | -0.75102 | -0.79184 | 1.4388 | 1.4071 | 1.3827 | 1.3418 | 1.3163 | 1.2765 | 1.2408 | 1.0806 | 1.0235 | -1.2449 | -0.3449 | -0.36224 | 1.851 | 1.8357 | 1.8082 | 1.7898 | 1.7551 | 1.7347 | 1.7031 | 1.6724 | 1.5796 | -0.70816 | -0.74286 | -0.65918 | 1.5653 | 1.5286 | 1.5031 | 1.4755 | 1.4459 | 1.4031 | 1.3673 | 1.3214 | 1.2755
|  | GISLA | EE |  |  |  |  | -0.73265 | -0.75102 | -0.79184 | 1.4388 | 1.4071 | 1.3827 | 1.3418 | 1.3163 | 1.2765 | 1.2408 | 1.0806 | 1.0276 | -1.2286 | -0.3449 | -0.36224 | 1.851 | 1.8357 | 1.8082 | 1.7898 | 1.7551 | 1.7347 | 1.7031 | 1.6724 | 1.5796 | -0.7051 | -0.71122 | -0.65918 | 1.5735 | 1.5286 | 1.5031 | 1.4755 | 1.4459 | 1.4031 | 1.3673 | 1.3214 | 1.2755
|  | GISLA | HT |  |  |  |  | -0.71837 | -0.74184 | -0.76122 | 1.4714 | 1.4449 | 1.4316 | 1.402 | 1.3786 | 1.3429 | 1.2969 | 1.1071 | 1.0235 | -1.2449 | -0.33367 | -0.35306 | 1.8796 | 1.8663 | 1.8449 | 1.8367 | 1.8102 | 1.7837 | 1.752 | 1.7224 | 1.598 | -0.70816 | -0.72041 | -0.64898 | 1.5653 | 1.5429 | 1.5184 | 1.4918 | 1.4684 | 1.4337 | 1.401 | 1.3643 | 1.3276
|  | GISLA | HE |  |  |  |  | -0.71837 | -0.72959 | -0.75918 | 1.4765 | 1.4531 | 1.4429 | 1.4163 | 1.3929 | 1.3633 | 1.3173 | 1.1092 | 1.0643 | -1.1959 | -0.33367 | -0.34184 | 1.8816 | 1.8684 | 1.849 | 1.8418 | 1.8184 | 1.7918 | 1.7633 | 1.7296 | 1.5959 | -0.68776 | -0.69694 | -0.64898 | 1.5908 | 1.5541 | 1.5347 | 1.5133 | 1.4959 | 1.4663 | 1.4357 | 1.401 | 1.3663
|  | GISLA | CF |  |  |  |  | -0.71327 | -0.72653 | -0.73571 | 1.4949 | 1.4776 | 1.4592 | 1.452 | 1.4306 | 1.4082 | 1.398 | 1.3 | 1.148 | -1.2184 | -0.32959 | -0.34082 | 1.901 | 1.8837 | 1.8673 | 1.85 | 1.8449 | 1.8255 | 1.8071 | 1.8 | 1.7153 | -0.63673 | -0.74286 | -0.64388 | 1.5939 | 1.5816 | 1.551 | 1.5327 | 1.5163 | 1.5031 | 1.4827 | 1.4582 | 1.4429
| ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | NO | 0.165 | -0.67653 | -0.75 | -0.84082 | -0.91122 | -1.001 | -1.1082 | -1.1949 | -1.3347 | -1.4694 | -1.5878 | -1.8541 | -1.9469 | -1.9194 | 0.64796 | 0.60102 | 0.54286 | 0.5 | 0.44082 | 0.37143 | 0.32143 | 0.22755 | 0.13776 | 0.063265 | -0.11633 | -0.18061 | -0.39694 | -0.31327 | -0.37959 | -0.46531 | -0.53367 | -0.61633 | -0.71531 | -0.79694 | -0.92959 | -1.0551 | -1.1643
|  | GLASTULLICH | EE |  |  |  |  | -0.67653 | -0.75 | -0.84082 | -0.91122 | -1.001 | -1.1082 | -1.1949 | -1.3347 | -1.4694 | -1.5878 | -1.8541 | -1.899 | -1.8663 | 0.64796 | 0.60102 | 0.54286 | 0.5 | 0.44082 | 0.37143 | 0.32143 | 0.22755 | 0.13776 | 0.063265 | -0.11633 | -0.18061 | -0.25306 | -0.31327 | -0.37959 | -0.46531 | -0.53367 | -0.61633 | -0.71531 | -0.79694 | -0.92959 | -1.0551 | -1.1643
|  | GLASTULLICH | HT |  |  |  |  | -0.64796 | -0.71122 | -0.77347 | -0.83878 | -0.91531 | -0.98061 | -1.0684 | -1.1704 | -1.2724 | -1.3347 | -1.7714 | -1.9469 | -1.9194 | 0.67245 | 0.63469 | 0.60102 | 0.56122 | 0.51122 | 0.47653 | 0.42551 | 0.35714 | 0.28878 | 0.25816 | -0.036735 | -0.13776 | -0.10408 | -0.28469 | -0.34388 | -0.40204 | -0.46327 | -0.53571 | -0.59592 | -0.67653 | -0.77347 | -0.86939 | -0.92755
|  | GLASTULLICH | HE |  |  |  |  | -0.64796 | -0.7 | -0.74694 | -0.7949 | -0.85714 | -0.90306 | -0.97653 | -1.0684 | -1.1612 | -1.2122 | -1.699 | -1.8102 | -1.8265 | 0.67041 | 0.63878 | 0.60816 | 0.57857 | 0.53163 | 0.50612 | 0.45918 | 0.3949 | 0.33367 | 0.3051 | -0.011224 | -0.11837 | -0.21837 | -0.28469 | -0.33265 | -0.37755 | -0.42449 | -0.48163 | -0.52551 | -0.5949 | -0.68367 | -0.76735 | -0.81633
|  | GLASTULLICH | CF |  |  |  |  | -0.63776 | -0.68163 | -0.71939 | -0.75918 | -0.81531 | -0.87041 | -0.90408 | -0.97143 | -1.0265 | -1.0888 | -1.3857 | -1.6796 | -1.8082 | 0.67857 | 0.65 | 0.62857 | 0.59898 | 0.56633 | 0.52449 | 0.50714 | 0.45612 | 0.41735 | 0.37245 | 0.15102 | -0.12857 | -0.39694 | -0.27551 | -0.31429 | -0.35102 | -0.38878 | -0.43878 | -0.49286 | -0.52143 | -0.58469 | -0.63776 | -0.69796
| SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | NO | 0.377 | 1.396 | 1.3491 | 1.2991 | 1.2327 | 1.1899 | 1.0756 | 0.97661 | 0.87967 | 0.79089 | 0.75212 | 0.57967 | 0.51436 | 0.271 | 1.7577 | 1.7332 | 1.7006 | 1.6598 | 1.6322 | 1.5659 | 1.5057 | 1.4455 | 1.3863 | 1.3649 | 1.2414 | 1.2957 | 1.109 | 1.5835 | 1.5386 | 1.4906 | 1.4304 | 1.3876 | 1.2825 | 1.1927 | 1.1049 | 1.0213 | 0.98452
|  | GLEDFIELD | EE |  |  |  |  | 1.396 | 1.3491 | 1.2991 | 1.2327 | 1.1899 | 1.0756 | 0.97661 | 0.87967 | 0.79089 | 0.75212 | 0.57967 | 0.54702 | 0.30161 | 1.7577 | 1.7332 | 1.7006 | 1.6598 | 1.6322 | 1.5659 | 1.5057 | 1.4455 | 1.3863 | 1.3649 | 1.2414 | 1.2957 | 1.2039 | 1.5835 | 1.5386 | 1.4906 | 1.4304 | 1.3876 | 1.2825 | 1.1927 | 1.1049 | 1.0213 | 0.98452
|  | GLEDFIELD | HT |  |  |  |  | 1.4215 | 1.3838 | 1.3286 | 1.2909 | 1.2491 | 1.144 | 1.0562 | 1.0052 | 0.93885 | 0.87763 | 0.63069 | 0.51436 | 0.271 | 1.771 | 1.7516 | 1.7261 | 1.7036 | 1.6792 | 1.623 | 1.572 | 1.5455 | 1.5057 | 1.4649 | 1.3128 | 1.3549 | 1.3437 | 1.6049 | 1.5682 | 1.5182 | 1.4825 | 1.4427 | 1.3488 | 1.2692 | 1.2233 | 1.16 | 1.0998
|  | GLEDFIELD | HE |  |  |  |  | 1.4215 | 1.3919 | 1.345 | 1.3195 | 1.2858 | 1.197 | 1.1144 | 1.0766 | 1.0195 | 0.96742 | 0.67457 | 0.6062 | 0.36896 | 1.771 | 1.7567 | 1.7312 | 1.7139 | 1.6945 | 1.6414 | 1.5894 | 1.569 | 1.5281 | 1.4924 | 1.3036 | 1.3315 | 1.2498 | 1.6049 | 1.5753 | 1.5376 | 1.51 | 1.4794 | 1.3957 | 1.3243 | 1.2855 | 1.2304 | 1.1825
|  | GLEDFIELD | CF |  |  |  |  | 1.4225 | 1.398 | 1.3664 | 1.3429 | 1.3062 | 1.2409 | 1.1827 | 1.1327 | 1.1144 | 1.0725 | 0.8511 | 0.7011 | 0.3863 | 1.771 | 1.7598 | 1.7414 | 1.7302 | 1.7057 | 1.669 | 1.6332 | 1.5965 | 1.5843 | 1.5526 | 1.3781 | 1.3161 | 1.109 | 1.607 | 1.5845 | 1.5559 | 1.5345 | 1.5019 | 1.4417 | 1.3896 | 1.3468 | 1.3264 | 1.2896
| FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0 | 0.1129 | 0.1129 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10984 | 0.10984 | 0.10882 | 0.1078 | 0.1078 | 0.096755 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10738 | 0.10636 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10738 | 0.10738 | 0.10738 | 0.10636
|  | GLEN LAOGH | EE |  |  |  |  | 0.1129 | 0.1129 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10984 | 0.10984 | 0.10882 | 0.10882 | 0.10882 | 0.099816 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.1084 | 0.1084 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10738 | 0.10738 | 0.10738 | 0.10636
|  | GLEN LAOGH | HT |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10984 | 0.10984 | 0.10882 | 0.1078 | 0.098796 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.1039 | 0.10738 | 0.10738 | 0.11044 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10738 | 0.10738 | 0.10738
|  | GLEN LAOGH | HE |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10984 | 0.10984 | 0.1078 | 0.1078 | 0.096755 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.10288 | 0.10738 | 0.10636 | 0.11044 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10738 | 0.10738 | 0.10738
|  | GLEN LAOGH | CF |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10882 | 0.1078 | 0.098796 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.1039 | 0.10738 | 0.10738 | 0.11044 | 0.11044 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942
| KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 0.104 | 1.0867 | 1.0337 | 0.97245 | 0.89388 | 0.81224 | 0.75204 | 0.6602 | 0.54796 | 0.44184 | 0.38367 | 0.12245 | 0.023469 | -0.012245 | 1.7418 | 1.7092 | 1.6745 | 1.6255 | 1.5724 | 1.5398 | 1.4857 | 1.4122 | 1.3429 | 1.3184 | 1.1418 | 1.051 | 0.81531 | 1.4786 | 1.4265 | 1.3694 | 1.299 | 1.2235 | 1.1653 | 1.0806 | 0.97551 | 0.87449 | 0.82041
|  | GLENCOE | EE |  |  |  |  | 1.0867 | 1.0337 | 0.97245 | 0.89388 | 0.81224 | 0.75204 | 0.6602 | 0.54796 | 0.44184 | 0.38367 | 0.12245 | 0.057143 | 0.029592 | 1.7418 | 1.7092 | 1.6745 | 1.6255 | 1.5724 | 1.5398 | 1.4857 | 1.4122 | 1.3429 | 1.3184 | 1.1418 | 1.051 | 0.94082 | 1.4786 | 1.4265 | 1.3694 | 1.299 | 1.2235 | 1.1653 | 1.0806 | 0.97551 | 0.87449 | 0.82041
|  | GLENCOE | HT |  |  |  |  | 1.1133 | 1.0612 | 0.99898 | 0.94592 | 0.8898 | 0.81837 | 0.74082 | 0.67347 | 0.5898 | 0.51122 | 0.18367 | 0.023469 | -0.012245 | 1.7633 | 1.7357 | 1.698 | 1.6735 | 1.6429 | 1.6031 | 1.552 | 1.5204 | 1.4694 | 1.4235 | 1.2184 | 1.1224 | 1.099 | 1.501 | 1.451 | 1.3949 | 1.3469 | 1.2929 | 1.2276 | 1.1531 | 1.0929 | 1.0143 | 0.94082
|  | GLENCOE | HE |  |  |  |  | 1.1133 | 1.0745 | 1.0224 | 0.98265 | 0.9398 | 0.87959 | 0.81122 | 0.75306 | 0.68163 | 0.61122 | 0.24082 | 0.14592 | 0.13163 | 1.7633 | 1.7378 | 1.7041 | 1.6857 | 1.6592 | 1.6204 | 1.5765 | 1.548 | 1.5 | 1.4571 | 1.2133 | 1.1092 | 1.0133 | 1.501 | 1.4633 | 1.4153 | 1.3796 | 1.3398 | 1.2847 | 1.2214 | 1.1653 | 1.0969 | 1.0327
|  | GLENCOE | CF |  |  |  |  | 1.1347 | 1.0888 | 1.048 | 1.0204 | 0.97653 | 0.94184 | 0.9 | 0.84694 | 0.81837 | 0.76633 | 0.49694 | 0.28061 | 0.11531 | 1.7765 | 1.7469 | 1.7224 | 1.7061 | 1.6776 | 1.6571 | 1.6255 | 1.5857 | 1.5724 | 1.5367 | 1.3316 | 1.102 | 0.81531 | 1.5184 | 1.4765 | 1.4408 | 1.4143 | 1.3735 | 1.3418 | 1.3031 | 1.2531 | 1.2255 | 1.1796
| DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0.023 | 0.21966 | 0.20843 | 0.19517 | 0.18905 | 0.1768 | 0.1666 | 0.14721 | 0.12986 | 0.12476 | 0.1115 | 0.079863 | 0.07068 | 0.040289 | 0.24641 | 0.24539 | 0.23621 | 0.23111 | 0.22192 | 0.21784 | 0.20355 | 0.18927 | 0.18519 | 0.17498 | 0.15253 | 0.15855 | 0.13099 | 0.23406 | 0.22385 | 0.21059 | 0.20548 | 0.19324 | 0.18508 | 0.16569 | 0.14834 | 0.14528 | 0.13201
|  | GLENDARUEL | EE |  |  |  |  | 0.21966 | 0.20843 | 0.19517 | 0.18905 | 0.1768 | 0.1666 | 0.14721 | 0.12986 | 0.12476 | 0.1115 | 0.079863 | 0.073741 | 0.04335 | 0.25049 | 0.24539 | 0.23621 | 0.23111 | 0.22192 | 0.21784 | 0.20355 | 0.18927 | 0.18519 | 0.17498 | 0.15253 | 0.15855 | 0.1463 | 0.23406 | 0.22385 | 0.21059 | 0.20548 | 0.19324 | 0.18508 | 0.16569 | 0.14834 | 0.14528 | 0.13201
|  | GLENDARUEL | HT |  |  |  |  | 0.22068 | 0.21048 | 0.20639 | 0.19619 | 0.18803 | 0.18292 | 0.17272 | 0.15639 | 0.14823 | 0.13292 | 0.091088 | 0.07068 | 0.040289 | 0.24641 | 0.24539 | 0.24335 | 0.23825 | 0.23213 | 0.22906 | 0.22192 | 0.20968 | 0.20662 | 0.19539 | 0.16682 | 0.16773 | 0.16569 | 0.23508 | 0.22385 | 0.22181 | 0.21263 | 0.2065 | 0.19936 | 0.1912 | 0.17181 | 0.16773 | 0.15446
|  | GLENDARUEL | HE |  |  |  |  | 0.22068 | 0.21048 | 0.20946 | 0.20027 | 0.19619 | 0.19007 | 0.17884 | 0.16558 | 0.15946 | 0.14721 | 0.09619 | 0.083945 | 0.052534 | 0.24641 | 0.24539 | 0.24539 | 0.23927 | 0.23621 | 0.23213 | 0.22498 | 0.2158 | 0.20764 | 0.19947 | 0.16478 | 0.16569 | 0.15344 | 0.23508 | 0.22487 | 0.22385 | 0.21569 | 0.21059 | 0.2065 | 0.1963 | 0.18304 | 0.17793 | 0.16365
|  | GLENDARUEL | CF |  |  |  |  | 0.22068 | 0.21048 | 0.2115 | 0.20537 | 0.20231 | 0.19211 | 0.18905 | 0.18088 | 0.17068 | 0.16864 | 0.11864 | 0.09721 | 0.050493 | 0.24641 | 0.24641 | 0.24743 | 0.24437 | 0.24233 | 0.23519 | 0.22906 | 0.22498 | 0.21682 | 0.2158 | 0.17396 | 0.16263 | 0.13099 | 0.23508 | 0.22589 | 0.22691 | 0.22181 | 0.21875 | 0.20855 | 0.20548 | 0.19732 | 0.18814 | 0.1861
| ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 1.18 | 3.0217 | 2.9564 | 2.8788 | 2.7982 | 2.69 | 2.5696 | 2.4462 | 2.3768 | 2.24 | 2.0921 | 1.6717 | 1.6207 | 1.2402 | 3.1045 | 3.0688 | 3.0239 | 2.98 | 2.9209 | 2.8535 | 2.778 | 2.7402 | 2.6464 | 2.5402 | 2.226 | 2.3651 | 2.2294 | 3.0692 | 3.0111 | 2.9396 | 2.8702 | 2.7723 | 2.6662 | 2.5509 | 2.4856 | 2.3621 | 2.2202
|  | GLENDEVON | EE |  |  |  |  | 3.0217 | 2.9564 | 2.8788 | 2.7982 | 2.69 | 2.5696 | 2.4462 | 2.3768 | 2.24 | 2.0921 | 1.6717 | 1.6411 | 1.2739 | 3.1045 | 3.0688 | 3.0239 | 2.98 | 2.9209 | 2.8535 | 2.778 | 2.7402 | 2.6464 | 2.5402 | 2.226 | 2.3651 | 2.31 | 3.0692 | 3.0111 | 2.9396 | 2.8702 | 2.7723 | 2.6662 | 2.5509 | 2.4856 | 2.3621 | 2.2202
|  | GLENDEVON | HT |  |  |  |  | 3.0462 | 2.9696 | 2.8931 | 2.8043 | 2.7002 | 2.6258 | 2.5554 | 2.4839 | 2.3431 | 2.1431 | 1.74 | 1.6207 | 1.2402 | 3.1239 | 3.0841 | 3.0433 | 3.0015 | 2.9464 | 2.9127 | 2.8698 | 2.828 | 2.726 | 2.5688 | 2.2872 | 2.4049 | 2.3927 | 3.0968 | 3.0284 | 2.959 | 2.8845 | 2.7917 | 2.7305 | 2.6611 | 2.5907 | 2.459 | 2.2825
|  | GLENDEVON | HE |  |  |  |  | 3.0472 | 2.9911 | 2.937 | 2.8656 | 2.7727 | 2.69 | 2.6156 | 2.5502 | 2.4431 | 2.3043 | 1.7482 | 1.6625 | 1.2872 | 3.1239 | 3.0913 | 3.0596 | 3.0198 | 2.9709 | 2.928 | 2.8862 | 2.8474 | 2.7668 | 2.6627 | 2.2607 | 2.3713 | 2.3131 | 3.0968 | 3.0437 | 2.9958 | 2.9345 | 2.8509 | 2.7835 | 2.7141 | 2.6498 | 2.5529 | 2.4213
|  | GLENDEVON | CF |  |  |  |  | 3.0584 | 3.0237 | 2.988 | 2.937 | 2.8921 | 2.8298 | 2.7696 | 2.688 | 2.6258 | 2.537 | 2.1288 | 1.7931 | 1.3147 | 3.13 | 3.1096 | 3.0862 | 3.0556 | 3.0341 | 2.9943 | 2.9627 | 2.9158 | 2.8698 | 2.8127 | 2.4933 | 2.3856 | 2.2294 | 3.106 | 3.0733 | 3.0407 | 2.9927 | 2.9539 | 2.8958 | 2.8458 | 2.7723 | 2.7131 | 2.6325
| FORT AUGUSTUS | GLENDOE | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 0.493 | 7.4349 | 7.4155 | 7.391 | 7.3676 | 7.3369 | 7.1757 | 7.142 | 7.1002 | 7.0706 | 7.039 | 6.9522 | 6.9247 | 6.2436 | 7.2456 | 7.2344 | 7.217 | 7.2038 | 7.1854 | 7.1068 | 7.0813 | 7.0558 | 7.0405 | 7.0181 | 6.9609 | 7.2709 | 7.1954 | 7.379 | 7.3627 | 7.3403 | 7.3178 | 7.2903 | 7.1586 | 7.1239 | 7.0852 | 7.0586 | 7.029
|  | GLENDOE | EE |  |  |  |  | 7.4349 | 7.4155 | 7.391 | 7.3676 | 7.3369 | 7.1757 | 7.142 | 7.1002 | 7.0706 | 7.039 | 6.9522 | 6.938 | 6.2538 | 7.2456 | 7.2344 | 7.217 | 7.2038 | 7.1854 | 7.1068 | 7.0813 | 7.0558 | 7.0405 | 7.0181 | 6.9609 | 7.2709 | 7.227 | 7.379 | 7.3627 | 7.3403 | 7.3178 | 7.2903 | 7.1586 | 7.1239 | 7.0852 | 7.0586 | 7.029
|  | GLENDOE | HT |  |  |  |  | 7.442 | 7.4257 | 7.4094 | 7.392 | 7.3696 | 7.2043 | 7.1767 | 7.1451 | 7.1257 | 7.0982 | 6.9829 | 6.9247 | 6.2436 | 7.2497 | 7.2436 | 7.2334 | 7.2242 | 7.2109 | 7.1323 | 7.115 | 7.0966 | 7.0864 | 7.0691 | 6.9926 | 7.2964 | 7.2954 | 7.3862 | 7.3719 | 7.3566 | 7.3423 | 7.3198 | 7.1882 | 7.1607 | 7.1321 | 7.1137 | 7.0862
|  | GLENDOE | HE |  |  |  |  | 7.442 | 7.4308 | 7.4176 | 7.4053 | 7.3859 | 7.2278 | 7.2043 | 7.1818 | 7.1655 | 7.14 | 7.0124 | 6.9747 | 6.2926 | 7.2497 | 7.2456 | 7.2344 | 7.2262 | 7.215 | 7.1395 | 7.1211 | 7.1058 | 7.0977 | 7.0783 | 6.9977 | 7.2943 | 7.2545 | 7.3862 | 7.376 | 7.3637 | 7.3525 | 7.3362 | 7.2086 | 7.1862 | 7.1627 | 7.1474 | 7.1249
|  | GLENDOE | CF |  |  |  |  | 7.4441 | 7.4359 | 7.4278 | 7.4155 | 7.4002 | 7.2573 | 7.2461 | 7.2257 | 7.2104 | 7.1931 | 7.1155 | 7.0288 | 6.3028 | 7.2507 | 7.2456 | 7.2395 | 7.2323 | 7.2242 | 7.1528 | 7.1446 | 7.1303 | 7.1181 | 7.1038 | 7.0436 | 7.2923 | 7.1954 | 7.3882 | 7.3811 | 7.3729 | 7.3627 | 7.3484 | 7.2372 | 7.2249 | 7.2066 | 7.1892 | 7.1729
| BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | 1.076 | 2.848 | 2.501 | 2.1449 | 1.5714 | 1.1582 | 0.18163 | -0.33265 | -0.92551 | -1.5235 | -2.2592 | -5.198 | -8.2551 | -11.3827 | 5.6112 | 5.399 | 5.1265 | 4.6592 | 4.4378 | 3.5112 | 3.1929 | 2.7286 | 2.2398 | 1.5122 | -1.2398 | -4.0536 | -7.123 | 4.6964 | 4.3832 | 3.9628 | 3.3679 | 3.0015 | 1.9291 | 1.4668 | 0.91071 | 0.37296 | -0.32092
|  | GLENEAGLES | EE |  |  |  |  | 2.848 | 2.501 | 2.1449 | 1.7408 | 1.2133 | 0.45816 | -0.26633 | -0.51327 | -1.2337 | -1.9194 | -4.5694 | -7.4 | -9.149 | 5.6112 | 5.399 | 5.1857 | 4.9347 | 4.5224 | 3.8765 | 3.3704 | 3.3102 | 2.7724 | 2.3337 | 0.48776 | -2.0883 | -3.6372 | 4.6964 | 4.3832 | 4.0536 | 3.6913 | 3.1566 | 2.3791 | 1.6801 | 1.4546 | 0.75153 | 0.11173
|  | GLENEAGLES | HT |  |  |  |  | 2.9582 | 2.6704 | 2.1449 | 1.5714 | 1.1582 | 0.18163 | -0.33265 | -0.92551 | -1.5235 | -2.2592 | -4.9061 | -8.1561 | -11.0184 | 5.6969 | 5.5367 | 5.1265 | 4.6592 | 4.4378 | 3.5112 | 3.2286 | 2.8612 | 2.5265 | 2.0888 | 0.30612 | -2.5209 | -4.9781 | 4.7719 | 4.5005 | 3.9628 | 3.3679 | 3.0015 | 1.9291 | 1.4668 | 0.91071 | 0.37296 | -0.29541
|  | GLENEAGLES | HE |  |  |  |  | 2.9602 | 2.7398 | 2.3286 | 1.8786 | 1.4857 | 0.59082 | 0.052041 | -0.54694 | -1.1806 | -2.0408 | -5.198 | -8.2551 | -11.3827 | 5.6929 | 5.5541 | 5.2112 | 4.7959 | 4.4969 | 3.6 | 3.1929 | 2.7286 | 2.2398 | 1.5122 | -1.2398 | -4.0536 | -7.123 | 4.776 | 4.5791 | 4.1607 | 3.675 | 3.2893 | 2.2964 | 1.7526 | 1.1679 | 0.55051 | -0.32092
|  | GLENEAGLES | CF |  |  |  |  | 3.0061 | 2.8316 | 2.6173 | 2.3969 | 2.1296 | 1.7408 | 1.4306 | 1.1429 | 0.83163 | 0.44286 | -1.1378 | -2.802 | -4.95 | 5.7214 | 5.6092 | 5.4735 | 5.3316 | 5.1061 | 4.7408 | 4.4704 | 4.2306 | 3.9684 | 3.6398 | 2.3367 | 1.0423 | -0.80051 | 4.823 | 4.674 | 4.4913 | 4.3056 | 4.0291 | 3.626 | 3.3281 | 3.0577 | 2.7587 | 2.3679
| RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0 | 0.29584 | 0.29584 | 0.2938 | 0.2938 | 0.2938 | 0.2938 | 0.29176 | 0.28971 | 0.28869 | 0.28665 | 0.28053 | 0.27645 | 0.24843 | 0.29741 | 0.29741 | 0.29741 | 0.29639 | 0.29537 | 0.29537 | 0.29537 | 0.29435 | 0.29231 | 0.29129 | 0.28618 | 0.29764 | 0.29662 | 0.29356 | 0.29356 | 0.29254 | 0.29254 | 0.2905 | 0.2905 | 0.28948 | 0.28744 | 0.2854 | 0.28438
|  | GLENETIVE | EE |  |  |  |  | 0.29584 | 0.29584 | 0.2938 | 0.2938 | 0.2938 | 0.2938 | 0.29176 | 0.28971 | 0.28869 | 0.28665 | 0.28155 | 0.28155 | 0.25455 | 0.29741 | 0.29741 | 0.29741 | 0.29639 | 0.29537 | 0.29537 | 0.29537 | 0.29435 | 0.29231 | 0.29129 | 0.2872 | 0.3007 | 0.3007 | 0.29356 | 0.29356 | 0.29254 | 0.29254 | 0.2905 | 0.2905 | 0.28948 | 0.28744 | 0.2854 | 0.28438
|  | GLENETIVE | HT |  |  |  |  | 0.29584 | 0.29584 | 0.29584 | 0.29482 | 0.2938 | 0.2938 | 0.2938 | 0.29278 | 0.29073 | 0.28971 | 0.28359 | 0.28053 | 0.25149 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29639 | 0.29639 | 0.29639 | 0.29537 | 0.29537 | 0.29333 | 0.28924 | 0.3007 | 0.29968 | 0.29356 | 0.29356 | 0.29356 | 0.29356 | 0.29254 | 0.29254 | 0.29152 | 0.28948 | 0.28846 | 0.28642
|  | GLENETIVE | HE |  |  |  |  | 0.29584 | 0.29584 | 0.29482 | 0.29482 | 0.2938 | 0.2938 | 0.2938 | 0.29073 | 0.28971 | 0.28767 | 0.28053 | 0.27645 | 0.24843 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29639 | 0.29639 | 0.29537 | 0.29537 | 0.29333 | 0.29231 | 0.28618 | 0.29764 | 0.29662 | 0.29356 | 0.29356 | 0.29356 | 0.29356 | 0.29254 | 0.29152 | 0.2905 | 0.28846 | 0.28642 | 0.2854
|  | GLENETIVE | CF |  |  |  |  | 0.29584 | 0.29584 | 0.29584 | 0.29584 | 0.29482 | 0.2938 | 0.2938 | 0.2938 | 0.2938 | 0.29278 | 0.28665 | 0.28155 | 0.25047 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29639 | 0.29639 | 0.29537 | 0.29537 | 0.29027 | 0.29968 | 0.29764 | 0.29356 | 0.29356 | 0.29356 | 0.29356 | 0.29356 | 0.29254 | 0.29254 | 0.29254 | 0.2905 | 0.28948
| FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | NO | 0 | 0.048612 | 0.039429 | 0.037388 | 0.029224 | 0.027184 | 0.026163 | 0.026163 | 0.025143 | 0.024122 | 0.01902 | 0.0098367 | 0.0098367 | 0.00083673 | 0.055939 | 0.047776 | 0.046755 | 0.038592 | 0.044714 | 0.037571 | 0.038592 | 0.043694 | 0.042673 | 0.038592 | 0.03349 | 0.034929 | 0.027786 | 0.056357 | 0.048194 | 0.045133 | 0.036969 | 0.036969 | 0.034929 | 0.035949 | 0.034929 | 0.032888 | 0.027786
|  | GLENUIG | EE |  |  |  |  | 0.048612 | 0.039429 | 0.037388 | 0.029224 | 0.027184 | 0.032286 | 0.029224 | 0.025143 | 0.024122 | 0.01902 | 0.0098367 | 0.010857 | 0.00083673 | 0.055939 | 0.047776 | 0.046755 | 0.038592 | 0.044714 | 0.047776 | 0.045735 | 0.043694 | 0.042673 | 0.038592 | 0.03349 | 0.034929 | 0.032888 | 0.056357 | 0.048194 | 0.045133 | 0.036969 | 0.036969 | 0.042071 | 0.03799 | 0.034929 | 0.032888 | 0.027786
|  | GLENUIG | HT |  |  |  |  | 0.055755 | 0.047592 | 0.045551 | 0.037388 | 0.036367 | 0.027184 | 0.026163 | 0.032286 | 0.026163 | 0.026163 | 0.012898 | 0.0098367 | 0.00083673 | 0.063082 | 0.055939 | 0.053898 | 0.046755 | 0.046755 | 0.037571 | 0.043694 | 0.048796 | 0.043694 | 0.043694 | 0.035531 | 0.036969 | 0.035949 | 0.0635 | 0.056357 | 0.052276 | 0.044112 | 0.043092 | 0.034929 | 0.035949 | 0.042071 | 0.035949 | 0.034929
|  | GLENUIG | HE |  |  |  |  | 0.055755 | 0.047592 | 0.046571 | 0.037388 | 0.036367 | 0.026163 | 0.027184 | 0.032286 | 0.028204 | 0.029224 | 0.013918 | 0.0098367 | 0.0028776 | 0.063082 | 0.054918 | 0.054918 | 0.046755 | 0.045735 | 0.037571 | 0.043694 | 0.047776 | 0.045735 | 0.045735 | 0.035531 | 0.034929 | 0.033908 | 0.0635 | 0.055337 | 0.055337 | 0.045133 | 0.044112 | 0.035949 | 0.036969 | 0.042071 | 0.03901 | 0.03799
|  | GLENUIG | CF |  |  |  |  | 0.055755 | 0.047592 | 0.047592 | 0.045551 | 0.037388 | 0.037388 | 0.029224 | 0.027184 | 0.027184 | 0.032286 | 0.022082 | 0.014939 | 0.0018571 | 0.063082 | 0.054918 | 0.054918 | 0.054918 | 0.046755 | 0.046755 | 0.038592 | 0.044714 | 0.044714 | 0.047776 | 0.039612 | 0.035949 | 0.027786 | 0.0635 | 0.055337 | 0.055337 | 0.054316 | 0.045133 | 0.044112 | 0.036969 | 0.036969 | 0.036969 | 0.042071
| BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | NO | 0.251 | 0.99082 | 0.92245 | 0.84082 | 0.77347 | 0.7051 | 0.63265 | 0.52449 | 0.41224 | 0.26735 | 0.13367 | -0.10612 | -0.1898 | -0.21633 | 1.6531 | 1.5959 | 1.5204 | 1.4724 | 1.4112 | 1.3418 | 1.2612 | 1.1918 | 1.098 | 1.0153 | 0.84898 | 0.77857 | 0.5449 | 1.4398 | 1.3633 | 1.2796 | 1.2082 | 1.1265 | 1.0388 | 0.93367 | 0.82653 | 0.69082 | 0.56735
|  | GOLSPIE | EE |  |  |  |  | 0.99082 | 0.92551 | 0.84082 | 0.77347 | 0.7051 | 0.63265 | 0.52449 | 0.41224 | 0.26735 | 0.13367 | -0.10612 | -0.14694 | -0.16735 | 1.6531 | 1.5959 | 1.5204 | 1.4724 | 1.4112 | 1.3418 | 1.2612 | 1.1918 | 1.098 | 1.0153 | 0.84898 | 0.77857 | 0.66837 | 1.4398 | 1.3694 | 1.2796 | 1.2082 | 1.1265 | 1.0388 | 0.93367 | 0.82653 | 0.69082 | 0.56735
|  | GOLSPIE | HT |  |  |  |  | 1.0092 | 0.92245 | 0.85612 | 0.79286 | 0.73163 | 0.65612 | 0.57041 | 0.48163 | 0.4051 | 0.34694 | -0.035714 | -0.1898 | -0.21633 | 1.6673 | 1.598 | 1.551 | 1.5102 | 1.4663 | 1.4224 | 1.3612 | 1.2918 | 1.2337 | 1.202 | 0.93163 | 0.8398 | 0.82653 | 1.4418 | 1.3633 | 1.3031 | 1.2459 | 1.1847 | 1.1071 | 1.0061 | 0.90408 | 0.82245 | 0.76735
|  | GOLSPIE | HE |  |  |  |  | 1.0153 | 0.95306 | 0.89286 | 0.8449 | 0.7949 | 0.75 | 0.69286 | 0.62041 | 0.54796 | 0.46939 | 0.032653 | -0.066327 | -0.081633 | 1.6745 | 1.6235 | 1.5745 | 1.5357 | 1.4949 | 1.4653 | 1.4184 | 1.3561 | 1.2918 | 1.2265 | 0.94286 | 0.83776 | 0.73571 | 1.451 | 1.3918 | 1.3367 | 1.2898 | 1.2408 | 1.2031 | 1.1337 | 1.051 | 0.96531 | 0.87755
|  | GOLSPIE | CF |  |  |  |  | 1.0316 | 0.98878 | 0.94898 | 0.90102 | 0.86122 | 0.81837 | 0.77347 | 0.73571 | 0.68367 | 0.63265 | 0.33469 | 0.066327 | -0.052041 | 1.6908 | 1.6592 | 1.6265 | 1.5827 | 1.5531 | 1.5143 | 1.4684 | 1.4418 | 1.3918 | 1.35 | 1.102 | 0.82041 | 0.5449 | 1.4673 | 1.4276 | 1.3908 | 1.3408 | 1.3071 | 1.2653 | 1.2143 | 1.1786 | 1.1133 | 1.0602
| BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 1.654 | 1.2253 | 0.92024 | 0.19269 | -0.89915 | -1.293 | -3.393 | -4.2298 | -5.2236 | -6.0328 | -7.3777 | -13.5583 | -20.6481 | -27.4354 | 4.4738 | 4.3565 | 3.6391 | 2.5565 | 2.3299 | -0.00067755 | -0.88537 | -1.9548 | -2.9966 | -4.4446 | -11.4711 | -20.1147 | -29.1229 | 3.4363 | 3.2557 | 2.4761 | 1.3149 | 1.0577 | -1.4076 | -2.2361 | -3.3504 | -4.427 | -6.03
|  | GOODLYBURN | EE |  |  |  |  | 1.2253 | 0.92024 | 0.5631 | 0.19473 | -0.68588 | -2.0379 | -3.1502 | -3.6991 | -4.9512 | -5.8736 | -9.5645 | -15.0502 | -17.9844 | 4.4738 | 4.3565 | 4.1901 | 3.9748 | 3.0963 | 1.6463 | 0.68198 | 0.35953 | -0.83027 | -1.6344 | -5.3017 | -12.9749 | -17.2637 | 3.4363 | 3.2557 | 3.0057 | 2.7333 | 1.8618 | 0.31692 | -0.84634 | -1.327 | -2.6872 | -3.6514
|  | GOODLYBURN | HT |  |  |  |  | 1.3019 | 1.0284 | 0.19269 | -0.89915 | -1.293 | -3.393 | -4.2298 | -5.2236 | -5.9757 | -6.5747 | -10.8389 | -17.9226 | -24.4303 | 4.5228 | 4.4299 | 3.6391 | 2.5565 | 2.3861 | -0.00067755 | -0.60986 | -1.367 | -1.8772 | -2.266 | -6.2037 | -14.731 | -22.1361 | 3.4863 | 3.3445 | 2.4761 | 1.3149 | 1.0577 | -1.4076 | -2.2361 | -3.2239 | -3.9494 | -4.5239
|  | GOODLYBURN | HE |  |  |  |  | 1.309 | 1.159 | 0.54983 | -0.32874 | -0.84711 | -2.8042 | -3.8451 | -4.9665 | -6.0328 | -7.3777 | -13.5583 | -20.6481 | -27.4354 | 4.5218 | 4.4361 | 3.7861 | 2.8156 | 2.3299 | 0.039118 | -0.88537 | -1.9548 | -2.9966 | -4.4446 | -11.4711 | -20.1147 | -29.1229 | 3.4884 | 3.3843 | 2.6833 | 1.6618 | 1.1179 | -1.2433 | -2.2351 | -3.3504 | -4.427 | -6.03
|  | GOODLYBURN | CF |  |  |  |  | 1.3947 | 1.3304 | 1.2478 | 1.1631 | 0.76208 | 0.088608 | -0.37772 | -0.87466 | -1.3247 | -1.8747 | -3.9165 | -6.6808 | -9.7558 | 4.5575 | 4.5085 | 4.4524 | 4.3912 | 3.9575 | 3.185 | 2.6626 | 2.1136 | 1.5891 | 0.93708 | -1.5517 | -4.8616 | -9.2902 | 3.5333 | 3.4873 | 3.4312 | 3.3679 | 2.9057 | 2.1047 | 1.5792 | 1.072 | 0.58835 | -0.028994
| CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | YES | 3.691 | 1.8718 | 1.3554 | 0.88502 | 0.43502 | -0.067016 | -0.56293 | -1.0272 | -1.3925 | -1.818 | -2.1293 | -3.0599 | -3.4946 | -4.2054 | 2.3884 | 1.9476 | 1.5517 | 1.1752 | 0.88027 | 0.49353 | 0.14558 | -0.082996 | -0.2881 | -0.46463 | -1.0646 | -1.075 | -1.5281 | 2.2127 | 1.724 | 1.276 | 0.84642 | 0.40357 | -0.072965 | -0.51174 | -0.85358 | -1.2199 | -1.4954
|  | GOURDIE | EE |  |  |  |  | 1.9248 | 1.434 | 1.0238 | 0.60441 | 0.17992 | -0.30987 | -0.89967 | -1.3078 | -1.6629 | -2.0099 | -3.0599 | -3.4731 | -4.1514 | 2.4568 | 2.0415 | 1.6976 | 1.3558 | 1.0609 | 0.70068 | 0.28945 | 0.0098612 | -0.20442 | -0.41259 | -1.0646 | -1.075 | -1.3311 | 2.273 | 1.8087 | 1.4179 | 1.0219 | 0.6301 | 0.16989 | -0.37705 | -0.75358 | -1.075 | -1.3862
|  | GOURDIE | HT |  |  |  |  | 1.8718 | 1.3554 | 0.88502 | 0.43502 | -0.067016 | -0.56293 | -1.0272 | -1.3925 | -1.818 | -2.1293 | -3.017 | -3.4946 | -4.2054 | 2.3884 | 1.9476 | 1.5517 | 1.1752 | 0.88027 | 0.49353 | 0.14558 | -0.082996 | -0.2881 | -0.46463 | -0.92483 | -0.88419 | -0.99541 | 2.2127 | 1.724 | 1.276 | 0.84642 | 0.40357 | -0.072965 | -0.51174 | -0.85358 | -1.2199 | -1.4954
|  | GOURDIE | HE |  |  |  |  | 1.9534 | 1.5167 | 1.1452 | 0.77686 | 0.35033 | -0.10783 | -0.60885 | -0.97722 | -1.3517 | -1.6129 | -2.5935 | -3.0752 | -3.8116 | 2.4762 | 2.0752 | 1.7466 | 1.4211 | 1.1221 | 0.77619 | 0.38741 | 0.11394 | -0.11973 | -0.30851 | -0.95442 | -0.92705 | -1.1852 | 2.2934 | 1.8801 | 1.5281 | 1.174 | 0.78826 | 0.36173 | -0.11174 | -0.45256 | -0.78623 | -1.0281
|  | GOURDIE | CF |  |  |  |  | 2.1381 | 1.8952 | 1.634 | 1.4218 | 1.1932 | 0.934 | 0.65135 | 0.34523 | 0.096249 | -0.19763 | -1.4048 | -2.4109 | -3.6116 | 2.669 | 2.4609 | 2.2435 | 2.0568 | 1.8701 | 1.6476 | 1.4129 | 1.1741 | 0.98435 | 0.78027 | -0.17585 | -0.8148 | -1.5281 | 2.4944 | 2.2546 | 2.0107 | 1.8097 | 1.5923 | 1.3434 | 1.077 | 0.79438 | 0.56989 | 0.30867
| BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 0.777 | 5.1461 | 4.9829 | 4.7951 | 4.6267 | 4.4094 | 4.1727 | 3.9522 | 3.6359 | 3.338 | 3.0757 | 2.4441 | 2.2033 | 2.1359 | 7.6247 | 7.5288 | 7.4176 | 7.3196 | 7.1859 | 7.0431 | 6.9012 | 6.69 | 6.4829 | 6.3012 | 5.8237 | 5.5992 | 4.7329 | 6.5043 | 6.3522 | 6.1665 | 6.0022 | 5.7869 | 5.5584 | 5.34 | 5.041 | 4.7563 | 4.5073
|  | GRANTOWN | EE |  |  |  |  | 5.1461 | 4.9829 | 4.7951 | 4.6267 | 4.4094 | 4.1727 | 3.9522 | 3.6359 | 3.338 | 3.0757 | 2.4441 | 2.3247 | 2.2451 | 7.6247 | 7.5288 | 7.4176 | 7.3196 | 7.1859 | 7.0431 | 6.9012 | 6.69 | 6.4829 | 6.3012 | 5.8237 | 5.5992 | 5.2043 | 6.5043 | 6.3522 | 6.1665 | 6.0022 | 5.7869 | 5.5584 | 5.34 | 5.041 | 4.7563 | 4.5073
|  | GRANTOWN | HT |  |  |  |  | 5.2349 | 5.09 | 4.9563 | 4.8022 | 4.6308 | 4.4747 | 4.2767 | 4.039 | 3.8696 | 3.639 | 2.6349 | 2.2033 | 2.1359 | 7.6757 | 7.5951 | 7.5206 | 7.4369 | 7.3369 | 7.2522 | 7.14 | 7.0053 | 6.9063 | 6.7624 | 6.089 | 5.8216 | 5.7829 | 6.592 | 6.4482 | 6.3135 | 6.1584 | 5.989 | 5.84 | 5.6451 | 5.4165 | 5.2461 | 5.0237
|  | GRANTOWN | HE |  |  |  |  | 5.2339 | 5.1135 | 5.0104 | 4.8869 | 4.7431 | 4.6308 | 4.4553 | 4.2461 | 4.1043 | 3.9063 | 2.8186 | 2.5553 | 2.5114 | 7.6727 | 7.6022 | 7.5359 | 7.4624 | 7.3757 | 7.3002 | 7.19 | 7.0635 | 6.9727 | 6.841 | 6.0829 | 5.7543 | 5.392 | 6.591 | 6.4757 | 6.3716 | 6.2471 | 6.1094 | 5.9961 | 5.8237 | 5.6247 | 5.4788 | 5.2869
|  | GRANTOWN | CF |  |  |  |  | 5.2635 | 5.1543 | 5.0329 | 4.9451 | 4.8329 | 4.7084 | 4.6227 | 4.4757 | 4.3369 | 4.1931 | 3.4961 | 2.842 | 2.5206 | 7.692 | 7.6267 | 7.5553 | 7.5022 | 7.4308 | 7.3533 | 7.288 | 7.1859 | 7.09 | 6.9931 | 6.4124 | 5.6369 | 4.7329 | 6.6165 | 6.5186 | 6.4022 | 6.3176 | 6.2145 | 6.0951 | 6.0135 | 5.8716 | 5.741 | 5.6022
| SHETLAND | GREMISTA | MINIMUM HEADROOM | HU4646842756 | NO | YES | 0 | 22.9455 | 21.8394 | 20.67 | 19.4731 | 18.32 | 17.1057 | 15.7894 | 14.6016 | 13.3159 | 12.6496 | 10.2751 | 9.4312 | 7.2741 | 25.9578 | 24.9231 | 23.8363 | 22.7271 | 21.7006 | 20.6282 | 19.4914 | 18.4506 | 17.3333 | 16.871 | 15.2945 | 15.6302 | 15.0629 | 23.9455 | 22.872 | 21.7353 | 20.5751 | 19.4639 | 18.2955 | 17.0302 | 15.8884 | 14.6547 | 14.0282
|  | GREMISTA | EE |  |  |  |  | 22.9455 | 21.8394 | 20.67 | 19.4731 | 18.32 | 17.1057 | 15.7894 | 14.6016 | 13.3159 | 12.6496 | 10.2751 | 9.6476 | 7.7118 | 25.9578 | 24.9231 | 23.8363 | 22.7271 | 21.7006 | 20.6282 | 19.4914 | 18.4506 | 17.3333 | 16.871 | 15.2945 | 15.8394 | 15.7435 | 23.9455 | 22.872 | 21.7353 | 20.5751 | 19.4639 | 18.2955 | 17.0302 | 15.8884 | 14.6547 | 14.0282
|  | GREMISTA | HT |  |  |  |  | 23.0251 | 21.9527 | 20.8363 | 19.6843 | 18.5404 | 17.3659 | 16.17 | 14.8731 | 13.5639 | 12.8282 | 10.4384 | 9.4312 | 7.2741 | 26.0169 | 25.0118 | 23.9659 | 22.8935 | 21.8802 | 20.8353 | 19.7904 | 18.6608 | 17.5241 | 17.02 | 15.4414 | 15.6935 | 15.4373 | 24.0241 | 22.9812 | 21.8965 | 20.7822 | 19.6843 | 18.5516 | 17.4016 | 16.1557 | 14.8965 | 14.2108
|  | GREMISTA | HE |  |  |  |  | 23.0384 | 22.0129 | 20.97 | 19.8853 | 18.8322 | 17.7047 | 16.4914 | 15.2169 | 13.9333 | 13.2057 | 10.4904 | 9.5853 | 7.4016 | 26.0333 | 25.0404 | 24.0292 | 22.9863 | 22.0231 | 21.0006 | 19.9282 | 18.8016 | 17.6771 | 17.1567 | 15.3027 | 15.6302 | 15.3618 | 24.0363 | 23.0363 | 22.019 | 20.9618 | 19.9435 | 18.8588 | 17.6904 | 16.4578 | 15.2251 | 14.5424
|  | GREMISTA | CF |  |  |  |  | 23.2057 | 22.3353 | 21.4312 | 20.5078 | 19.7078 | 18.8537 | 17.972 | 17.021 | 16.0863 | 15.6731 | 13.2271 | 11.1312 | 7.8496 | 26.1527 | 25.2659 | 24.3455 | 23.4149 | 22.6271 | 21.7965 | 20.9465 | 20.0404 | 19.1476 | 18.8292 | 17.0669 | 16.4894 | 15.0629 | 24.1945 | 23.3404 | 22.4537 | 21.5455 | 20.7659 | 19.9302 | 19.0731 | 18.1486 | 17.2384 | 16.8445
| WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | NO | 4.685 | 10.7799 | 10.2952 | 9.7442 | 9.1248 | 8.4309 | 7.6687 | 6.7666 | 5.8983 | 5.086 | 4.3228 | 0.91461 | -1.7068 | -2.9442 | 13.215 | 12.9069 | 12.5385 | 12.1334 | 11.6701 | 11.1569 | 10.5844 | 9.9732 | 9.3956 | 8.8518 | 6.0181 | 3.8405 | -4.7574 | 12.3936 | 11.9569 | 11.4518 | 10.8905 | 10.2538 | 9.5497 | 8.714 | 7.8915 | 7.1232 | 6.4007
|  | GREYFRIARS | EE |  |  |  |  | 10.7799 | 10.2952 | 9.7442 | 9.1248 | 8.4309 | 7.6687 | 6.7666 | 5.8983 | 5.086 | 4.3228 | 0.91461 | -1.3007 | -2.836 | 13.215 | 12.9069 | 12.5385 | 12.1334 | 11.6701 | 11.1569 | 10.5844 | 9.9732 | 9.3956 | 8.8518 | 6.0181 | 3.8405 | -0.13702 | 12.3936 | 11.9569 | 11.4518 | 10.8905 | 10.2538 | 9.5497 | 8.714 | 7.8915 | 7.1232 | 6.4007
|  | GREYFRIARS | HT |  |  |  |  | 10.9126 | 10.3718 | 9.8922 | 9.3503 | 8.7636 | 8.0952 | 7.4115 | 6.6401 | 5.8983 | 5.086 | 1.0922 | -1.7068 | -2.9442 | 13.3538 | 13.0783 | 12.8181 | 12.5222 | 12.2069 | 11.8375 | 11.4711 | 11.0344 | 10.6283 | 10.1742 | 7.9834 | 7.1507 | 6.9456 | 12.5201 | 12.0538 | 11.6211 | 11.1303 | 10.5987 | 9.9875 | 9.3446 | 8.6171 | 7.9201 | 7.1609
|  | GREYFRIARS | HE |  |  |  |  | 10.8993 | 10.5718 | 10.2993 | 9.9942 | 9.6697 | 9.2952 | 8.7758 | 8.1687 | 7.5769 | 6.9911 | 3.8003 | 1.6554 | 0.20991 | 13.316 | 13.0926 | 12.8783 | 12.6405 | 12.3793 | 12.0803 | 11.7171 | 11.2773 | 10.8466 | 10.4058 | 7.5977 | 5.3079 | 1.4762 | 12.5079 | 12.2171 | 11.963 | 11.6813 | 11.3773 | 11.0283 | 10.5375 | 9.9722 | 9.4191 | 8.8711
|  | GREYFRIARS | CF |  |  |  |  | 10.9922 | 10.7595 | 10.6136 | 10.4228 | 10.1962 | 9.9677 | 9.7483 | 9.482 | 9.2258 | 8.9473 | 7.0575 | 5.136 | 2.3415 | 13.3548 | 13.1701 | 13.0109 | 12.8171 | 12.5885 | 12.3232 | 12.0171 | 11.665 | 11.3099 | 10.9334 | 8.2324 | 3.8732 | -4.7574 | 12.5915 | 12.3956 | 12.2569 | 12.0793 | 11.8701 | 11.6558 | 11.4507 | 11.2028 | 10.964 | 10.7058
| SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 0.427 | 0.084731 | 0.069424 | 0.047996 | 0.031669 | 0.0071796 | -0.0071061 | -0.032616 | -0.06629 | -0.086698 | -0.11119 | -0.16833 | -0.18874 | -0.19384 | 0.26228 | 0.2531 | 0.24085 | 0.22963 | 0.21228 | 0.2031 | 0.18881 | 0.16432 | 0.15208 | 0.13575 | 0.092894 | 0.080649 | 0.03269 | 0.14596 | 0.13677 | 0.11942 | 0.1031 | 0.079629 | 0.066363 | 0.041873 | 0.0071796 | -0.0091469 | -0.033637
|  | GUTCHER | EE |  |  |  |  | 0.084731 | 0.069424 | 0.047996 | 0.031669 | 0.0071796 | -0.0071061 | -0.032616 | -0.06629 | -0.086698 | -0.11119 | -0.16833 | -0.17649 | -0.18262 | 0.26228 | 0.2531 | 0.24085 | 0.22963 | 0.21228 | 0.2031 | 0.18881 | 0.16432 | 0.15208 | 0.13575 | 0.092894 | 0.080649 | 0.054118 | 0.14596 | 0.13677 | 0.11942 | 0.1031 | 0.079629 | 0.066363 | 0.041873 | 0.0071796 | -0.0091469 | -0.033637
|  | GUTCHER | HT |  |  |  |  | 0.088812 | 0.078608 | 0.065343 | 0.050037 | 0.035751 | 0.019424 | -0.0020041 | -0.028535 | -0.038739 | -0.060167 | -0.14894 | -0.18874 | -0.19384 | 0.2633 | 0.25718 | 0.25208 | 0.24289 | 0.23575 | 0.22759 | 0.2133 | 0.19596 | 0.18983 | 0.17453 | 0.11534 | 0.090853 | 0.088812 | 0.14902 | 0.14187 | 0.13371 | 0.12044 | 0.10922 | 0.099016 | 0.075547 | 0.050037 | 0.042894 | 0.020445
|  | GUTCHER | HE |  |  |  |  | 0.088812 | 0.079629 | 0.071465 | 0.060241 | 0.043914 | 0.031669 | 0.013302 | -0.0091469 | -0.018331 | -0.039759 | -0.13262 | -0.15711 | -0.16119 | 0.2633 | 0.2582 | 0.25412 | 0.24902 | 0.23779 | 0.22963 | 0.2184 | 0.2031 | 0.19698 | 0.18269 | 0.11738 | 0.094935 | 0.070445 | 0.148 | 0.14187 | 0.13575 | 0.12963 | 0.11738 | 0.10616 | 0.088812 | 0.065343 | 0.0582 | 0.036771
|  | GUTCHER | CF |  |  |  |  | 0.089833 | 0.085751 | 0.078608 | 0.070445 | 0.0582 | 0.045955 | 0.038812 | 0.022486 | 0.0071796 | -0.0081265 | -0.064249 | -0.12956 | -0.15711 | 0.2633 | 0.26126 | 0.25922 | 0.25106 | 0.24391 | 0.23779 | 0.23371 | 0.21942 | 0.20922 | 0.20004 | 0.15616 | 0.089833 | 0.03269 | 0.14902 | 0.14391 | 0.14085 | 0.13269 | 0.12351 | 0.11534 | 0.1082 | 0.091873 | 0.075547 | 0.062282
| THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | NO | 0.273 | 5.3524 | 5.2667 | 5.94 | 5.841 | 5.7441 | 5.6339 | 5.5257 | 5.3543 | 5.1808 | 5.0216 | 4.6982 | 4.5829 | 3.215 | 5.4639 | 6.7359 | 6.6849 | 6.6135 | 6.5471 | 6.4665 | 6.4063 | 6.288 | 6.1757 | 6.0767 | 5.9043 | 4.7801 | 4.4474 | 6.5431 | 6.4635 | 6.3839 | 6.2849 | 6.189 | 6.0788 | 5.9788 | 5.8135 | 5.6553 | 5.5084
|  | HALKIRK | EE |  |  |  |  | 5.3524 | 5.2667 | 5.94 | 5.841 | 5.7441 | 5.6339 | 5.5257 | 5.3543 | 5.1808 | 5.0216 | 4.6982 | 4.6257 | 3.2803 | 5.4639 | 6.7359 | 6.6849 | 6.6135 | 6.5471 | 6.4665 | 6.4063 | 6.288 | 6.1757 | 6.0767 | 5.9043 | 4.7801 | 4.6525 | 6.5431 | 6.4635 | 6.3839 | 6.2849 | 6.189 | 6.0788 | 5.9788 | 5.8135 | 5.6553 | 5.5084
|  | HALKIRK | HT |  |  |  |  | 5.3748 | 5.3024 | 5.9788 | 5.891 | 5.8176 | 5.6982 | 5.5727 | 5.4257 | 5.3369 | 5.2247 | 4.7941 | 4.5829 | 3.215 | 5.4946 | 6.7808 | 6.7349 | 6.6818 | 6.6451 | 6.5737 | 6.5053 | 6.4135 | 6.3676 | 6.292 | 6.0094 | 4.8556 | 4.8342 | 6.5727 | 6.5063 | 6.4318 | 6.3502 | 6.2808 | 6.1706 | 6.0573 | 5.9206 | 5.8369 | 5.7278
|  | HALKIRK | HE |  |  |  |  | 5.3769 | 5.3197 | 6.0186 | 5.9543 | 5.8992 | 5.8257 | 5.7339 | 5.6114 | 5.5155 | 5.3961 | 4.8176 | 4.6839 | 3.3374 | 5.4935 | 6.7849 | 6.7482 | 6.6971 | 6.6655 | 6.6124 | 6.5543 | 6.4696 | 6.4186 | 6.3369 | 5.989 | 4.827 | 4.6974 | 6.5737 | 6.5216 | 6.4665 | 6.4002 | 6.3492 | 6.2757 | 6.188 | 6.0676 | 5.9859 | 5.8686
|  | HALKIRK | CF |  |  |  |  | 5.3799 | 5.333 | 6.041 | 5.991 | 5.9349 | 5.89 | 5.8267 | 5.7635 | 5.6767 | 5.5869 | 5.2155 | 4.9176 | 3.366 | 5.4966 | 6.7869 | 6.7604 | 6.7267 | 6.6849 | 6.6584 | 6.6084 | 6.5584 | 6.4982 | 6.4298 | 6.1441 | 4.824 | 4.4474 | 6.5778 | 6.5318 | 6.4869 | 6.441 | 6.3859 | 6.3461 | 6.2829 | 6.2176 | 6.1359 | 6.0522
| ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 2.03 | 17.9216 | 17.442 | 16.4094 | 15.2451 | 14.7094 | 12.8349 | 12.2339 | 11.5808 | 10.8859 | 9.5951 | 4.2941 | -1.658 | -6.9386 | 20.2951 | 19.992 | 19.091 | 18.0196 | 17.7155 | 15.7124 | 14.9951 | 14.188 | 13.3798 | 12.0155 | 6.4227 | -0.39265 | -6.8396 | 19.2818 | 18.8461 | 17.7941 | 16.542 | 16.0757 | 13.9084 | 13.3369 | 12.5757 | 11.6124 | 10.0829
|  | HARBOUR | EE |  |  |  |  | 17.9216 | 17.442 | 16.8696 | 16.2859 | 15.3482 | 14.0737 | 13.142 | 12.5196 | 11.8063 | 11.0359 | 7.8624 | 2.8533 | 0.86959 | 20.2951 | 19.992 | 19.6267 | 19.2349 | 18.4063 | 17.1512 | 16.4359 | 16.0329 | 15.2431 | 14.64 | 11.8869 | 5.7869 | 2.8022 | 19.2818 | 18.8461 | 18.3441 | 17.8196 | 16.8573 | 15.4624 | 14.5318 | 13.9441 | 13.1124 | 12.3196
|  | HARBOUR | HT |  |  |  |  | 17.9624 | 17.4829 | 16.4094 | 15.2451 | 14.7094 | 12.8349 | 12.2339 | 11.5808 | 11.0318 | 10.3206 | 6.9339 | 0.82265 | -4.0029 | 20.3186 | 20.0196 | 19.091 | 18.0196 | 17.7155 | 15.7124 | 15.3267 | 14.8859 | 14.5727 | 14.0961 | 10.9227 | 3.6522 | -2.4335 | 19.3216 | 18.8982 | 17.7941 | 16.542 | 16.0757 | 13.9084 | 13.3369 | 12.7073 | 12.2073 | 11.5227
|  | HARBOUR | HE |  |  |  |  | 18.0043 | 17.6512 | 16.8267 | 15.8318 | 15.1757 | 13.3818 | 12.5584 | 11.7196 | 10.8859 | 9.5951 | 4.2941 | -1.658 | -6.9386 | 20.3482 | 20.0727 | 19.3094 | 18.3329 | 17.7543 | 15.7441 | 14.9951 | 14.188 | 13.3798 | 12.0155 | 6.4227 | -0.39265 | -6.8396 | 19.3614 | 19.0431 | 18.1859 | 17.1084 | 16.4563 | 14.3645 | 13.5084 | 12.5757 | 11.6124 | 10.0829
|  | HARBOUR | CF |  |  |  |  | 18.1094 | 17.9278 | 17.6584 | 17.3941 | 16.8788 | 16.1614 | 15.6635 | 15.2227 | 14.8655 | 14.3686 | 12.1441 | 9.7573 | 7.7227 | 20.438 | 20.291 | 20.0982 | 19.9308 | 19.4676 | 18.7471 | 18.2624 | 17.8369 | 17.4339 | 16.9114 | 14.8543 | 12.7727 | 10.1206 | 19.4676 | 19.2931 | 19.0594 | 18.8288 | 18.2931 | 17.4971 | 16.9737 | 16.5227 | 16.092 | 15.5124
| ARDMORE | HARRIS GRID | MINIMUM HEADROOM | NG 13500 94249 | YES | YES | 0 | 35.3704 | 35.2092 | 35.1908 | 35.1745 | 35.1582 | 35.1429 | 35.1224 | 35.1 | 35.0786 | 35.0571 | 34.9796 | 34.952 | 32.2316 | 32.6724 | 32.5092 | 32.498 | 32.4888 | 32.4755 | 32.4653 | 32.45 | 32.4357 | 32.4204 | 32.4061 | 32.349 | 33.6786 | 33.6612 | 34.0204 | 33.8582 | 33.8429 | 33.8306 | 33.8133 | 33.799 | 33.7796 | 33.7571 | 33.7367 | 33.7173
|  | HARRIS GRID | EE |  |  |  |  | 35.3724 | 35.3633 | 35.1908 | 35.1745 | 35.1582 | 35.1429 | 35.1224 | 35.1 | 35.0786 | 35.0571 | 34.9796 | 34.9561 | 32.25 | 32.6776 | 32.6714 | 32.498 | 32.4888 | 32.4755 | 32.4653 | 32.45 | 32.4357 | 32.4204 | 32.4061 | 32.349 | 33.6816 | 33.6776 | 34.0224 | 34.0133 | 33.8429 | 33.8306 | 33.8133 | 33.799 | 33.7796 | 33.7571 | 33.7367 | 33.7173
|  | HARRIS GRID | HT |  |  |  |  | 35.3704 | 35.2092 | 35.199 | 35.1867 | 35.1755 | 35.1612 | 35.1439 | 35.1235 | 35.1031 | 35.0827 | 34.9949 | 34.952 | 32.2367 | 32.6724 | 32.5092 | 32.5031 | 32.498 | 32.4898 | 32.4786 | 32.4673 | 32.4541 | 32.4367 | 32.4245 | 32.3602 | 33.6796 | 33.6673 | 34.0204 | 33.8582 | 33.85 | 33.8418 | 33.8306 | 33.8163 | 33.8 | 33.7806 | 33.7612 | 33.7408
|  | HARRIS GRID | HE |  |  |  |  | 35.3714 | 35.3735 | 35.199 | 35.1878 | 35.1786 | 35.1633 | 35.1469 | 35.1265 | 35.1061 | 35.0827 | 34.9816 | 34.9541 | 32.2429 | 32.6735 | 32.6796 | 32.5051 | 32.498 | 32.4898 | 32.4786 | 32.4673 | 32.451 | 32.4378 | 32.4204 | 32.349 | 33.6786 | 33.6704 | 34.0214 | 34.0235 | 33.851 | 33.8408 | 33.8316 | 33.8184 | 33.802 | 33.7827 | 33.7633 | 33.7398
|  | HARRIS GRID | CF |  |  |  |  | 35.3806 | 35.3694 | 35.3673 | 35.2031 | 35.1959 | 35.1878 | 35.1786 | 35.1663 | 35.1551 | 35.1439 | 35.0684 | 34.9939 | 32.2316 | 32.6827 | 32.6776 | 32.6765 | 32.5041 | 32.502 | 32.4969 | 32.4898 | 32.4806 | 32.4724 | 32.4643 | 32.4092 | 33.7061 | 33.6612 | 34.0306 | 34.0204 | 34.0184 | 33.8531 | 33.849 | 33.8398 | 33.8316 | 33.8204 | 33.8092 | 33.799
| DYCE | HARVEST AVENUE | MINIMUM HEADROOM | NJ 86978 11769 | NO | YES | 0.158 | 19.7841 | 19.778 | 19.7698 | 19.7647 | 19.7576 | 19.7514 | 19.7422 | 19.732 | 19.7259 | 19.7137 | 19.6769 | 19.6678 | 18.4657 | 20.2147 | 20.2096 | 20.2024 | 20.1963 | 20.1851 | 20.182 | 20.1708 | 20.1606 | 20.1535 | 20.1433 | 20.1208 | 20.7137 | 20.7127 | 20.4361 | 20.43 | 20.4249 | 20.4208 | 20.4137 | 20.4086 | 20.4024 | 20.3933 | 20.3882 | 20.379
|  | HARVEST AVENUE | EE |  |  |  |  | 19.7841 | 19.778 | 19.7698 | 19.7647 | 19.7576 | 19.7514 | 19.7422 | 19.732 | 19.7259 | 19.7137 | 19.6769 | 19.6678 | 18.4657 | 20.2147 | 20.2096 | 20.2024 | 20.1963 | 20.1851 | 20.182 | 20.1708 | 20.1606 | 20.1535 | 20.1433 | 20.1208 | 20.7137 | 20.7127 | 20.4361 | 20.43 | 20.4249 | 20.4208 | 20.4137 | 20.4086 | 20.4024 | 20.3933 | 20.3882 | 20.379
|  | HARVEST AVENUE | HT |  |  |  |  | 19.7861 | 19.781 | 19.7739 | 19.7698 | 19.7637 | 19.7576 | 19.7494 | 19.7453 | 19.7371 | 19.729 | 19.6922 | 19.6718 | 18.4678 | 20.2178 | 20.2127 | 20.2076 | 20.2035 | 20.1963 | 20.1912 | 20.182 | 20.179 | 20.1718 | 20.1637 | 20.1382 | 20.7249 | 20.7218 | 20.4371 | 20.432 | 20.429 | 20.4259 | 20.4198 | 20.4157 | 20.4096 | 20.4055 | 20.3984 | 20.3912
|  | HARVEST AVENUE | HE |  |  |  |  | 19.7861 | 19.782 | 19.778 | 19.7739 | 19.7678 | 19.7647 | 19.7576 | 19.7545 | 19.7463 | 19.7392 | 19.6994 | 19.6831 | 18.4769 | 20.2178 | 20.2137 | 20.2096 | 20.2055 | 20.2004 | 20.1963 | 20.1882 | 20.1861 | 20.179 | 20.1718 | 20.1392 | 20.731 | 20.7259 | 20.4371 | 20.4331 | 20.43 | 20.4269 | 20.4218 | 20.4198 | 20.4137 | 20.4106 | 20.4055 | 20.3994
|  | HARVEST AVENUE | CF |  |  |  |  | 19.7851 | 19.7831 | 19.78 | 19.778 | 19.7729 | 19.7688 | 19.7657 | 19.7606 | 19.7586 | 19.7555 | 19.7361 | 19.7086 | 18.4851 | 20.2167 | 20.2147 | 20.2116 | 20.2065 | 20.2024 | 20.2014 | 20.1953 | 20.1892 | 20.1882 | 20.1851 | 20.1657 | 20.7422 | 20.729 | 20.4361 | 20.4341 | 20.432 | 20.429 | 20.4239 | 20.4229 | 20.4208 | 20.4167 | 20.4157 | 20.4116
| THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | NO | 0.452 | 0.15882 | 0.041469 | -0.092204 | -0.24016 | -0.35955 | -0.51363 | -0.71363 | -0.8922 | -1.0963 | -1.28 | -1.7391 | -1.8881 | -1.9422 | 1.0374 | 0.97412 | 0.89657 | 0.80371 | 0.73637 | 0.63739 | 0.51494 | 0.41392 | 0.28943 | 0.17922 | -0.097306 | -0.20139 | -0.482 | 0.52616 | 0.4231 | 0.30473 | 0.17616 | 0.072082 | -0.062612 | -0.23506 | -0.38914 | -0.56976 | -0.74016
|  | HASTIGROW | EE |  |  |  |  | 0.15882 | 0.041469 | -0.092204 | -0.24016 | -0.35955 | -0.51363 | -0.71363 | -0.8922 | -1.0963 | -1.28 | -1.7391 | -1.8208 | -1.8493 | 1.0374 | 0.97412 | 0.89657 | 0.80371 | 0.73637 | 0.63739 | 0.51494 | 0.41392 | 0.28943 | 0.17922 | -0.097306 | -0.20139 | -0.34118 | 0.52616 | 0.4231 | 0.30473 | 0.17616 | 0.072082 | -0.062612 | -0.23506 | -0.38914 | -0.56976 | -0.74016
|  | HASTIGROW | HT |  |  |  |  | 0.18535 | 0.079224 | -0.03098 | -0.1371 | -0.25853 | -0.39527 | -0.51669 | -0.67792 | -0.83608 | -0.99935 | -1.5963 | -1.8881 | -1.9422 | 1.0456 | 1.0149 | 0.95576 | 0.90371 | 0.83535 | 0.75882 | 0.69861 | 0.60269 | 0.50882 | 0.4078 | 0.039429 | -0.10955 | -0.13608 | 0.55167 | 0.45167 | 0.35065 | 0.25371 | 0.14453 | 0.024122 | -0.082 | -0.2218 | -0.36159 | -0.50139
|  | HASTIGROW | HE |  |  |  |  | 0.18535 | 0.1129 | 0.029224 | -0.046286 | -0.13506 | -0.2371 | -0.33812 | -0.47894 | -0.61771 | -0.75955 | -1.5259 | -1.7085 | -1.733 | 1.0445 | 1.0241 | 0.97412 | 0.93127 | 0.8731 | 0.80473 | 0.75269 | 0.6629 | 0.57718 | 0.48331 | 0.034327 | -0.12996 | -0.26261 | 0.54963 | 0.48229 | 0.4078 | 0.34147 | 0.26392 | 0.17616 | 0.086367 | -0.035061 | -0.15139 | -0.27588
|  | HASTIGROW | CF |  |  |  |  | 0.19555 | 0.13127 | 0.063918 | -0.00036735 | -0.08302 | -0.16159 | -0.25343 | -0.32078 | -0.41465 | -0.50853 | -0.97384 | -1.4208 | -1.6769 | 1.0476 | 1.0384 | 0.99657 | 0.95882 | 0.90678 | 0.85678 | 0.79759 | 0.75473 | 0.68943 | 0.62106 | 0.28024 | -0.12588 | -0.482 | 0.56188 | 0.50065 | 0.43433 | 0.37718 | 0.30473 | 0.23433 | 0.15576 | 0.095551 | 0.015959 | -0.065673
| STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | YES | 0.237 | 4.5798 | 4.3359 | 4.0512 | 3.7798 | 3.4543 | 3.1594 | 2.7778 | 2.3482 | 1.9971 | 1.6288 | 0.49408 | -0.074286 | -0.11714 | 6.0624 | 5.9155 | 5.7359 | 5.5767 | 5.3635 | 5.1553 | 4.9563 | 4.7002 | 4.4757 | 4.2645 | 3.6788 | 3.3767 | 3.0696 | 5.2441 | 5.0318 | 4.7757 | 4.5441 | 4.2492 | 3.9614 | 3.6441 | 3.2543 | 2.9114 | 2.5808
|  | HATTON | EE |  |  |  |  | 4.5798 | 4.3359 | 4.0512 | 3.79 | 3.4727 | 3.1594 | 2.791 | 2.3686 | 1.9982 | 1.6288 | 0.50735 | -0.0069388 | -0.11714 | 6.0624 | 5.9155 | 5.7359 | 5.5767 | 5.3635 | 5.1553 | 4.9563 | 4.7002 | 4.4757 | 4.2645 | 3.6788 | 3.3767 | 3.0696 | 5.2441 | 5.0318 | 4.7757 | 4.5441 | 4.2492 | 3.9614 | 3.6441 | 3.2543 | 2.9114 | 2.5808
|  | HATTON | HT |  |  |  |  | 4.6135 | 4.3563 | 4.0716 | 3.7798 | 3.4543 | 3.1798 | 2.7778 | 2.3482 | 1.9971 | 1.6461 | 0.49408 | -0.074286 | 0.085918 | 6.1073 | 5.9604 | 5.791 | 5.6094 | 5.4022 | 5.2471 | 5.039 | 4.8186 | 4.6512 | 4.4655 | 3.841 | 3.5869 | 3.7839 | 5.3002 | 5.0859 | 4.8349 | 4.5747 | 4.2798 | 4.0349 | 3.6849 | 3.3145 | 3.0124 | 2.6982
|  | HATTON | HE |  |  |  |  | 4.6247 | 4.4431 | 4.24 | 4.0318 | 3.789 | 3.5778 | 3.2829 | 2.9635 | 2.7288 | 2.4522 | 1.1645 | 0.81755 | 0.56551 | 6.1145 | 5.992 | 5.8624 | 5.7176 | 5.5502 | 5.4104 | 5.2329 | 5.0471 | 4.9124 | 4.7441 | 3.9431 | 3.8176 | 3.4645 | 5.3104 | 5.1451 | 4.9716 | 4.7839 | 4.5604 | 4.3829 | 4.1196 | 3.8298 | 3.6267 | 3.3716
|  | HATTON | CF |  |  |  |  | 4.6747 | 4.542 | 4.3869 | 4.2584 | 4.1033 | 3.9288 | 3.7676 | 3.5798 | 3.4369 | 3.2767 | 2.29 | 1.7267 | 1.1053 | 6.141 | 6.0584 | 5.9461 | 5.8604 | 5.7512 | 5.6257 | 5.5237 | 5.3849 | 5.2716 | 5.1451 | 4.4329 | 3.9522 | 3.1676 | 5.3512 | 5.2349 | 5.089 | 4.9757 | 4.8308 | 4.6696 | 4.5359 | 4.3584 | 4.2165 | 4.0594
| PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | NO | 3.379 | 10.0852 | 9.6618 | 9.2128 | 8.7159 | 8.1648 | 7.6159 | 6.7495 | 5.7873 | 4.873 | 4.375 | 0.84136 | -1.7617 | -3.1648 | 11.6148 | 11.3546 | 11.071 | 10.7454 | 10.3771 | 10.0159 | 9.5026 | 8.9108 | 8.3505 | 8.1281 | 6.121 | 5.1842 | 3.8301 | 11.0067 | 10.6077 | 10.1842 | 9.7016 | 9.173 | 8.6608 | 7.8648 | 6.9689 | 6.1189 | 5.6842
|  | HAUDAGAIN | EE |  |  |  |  | 10.0852 | 9.6618 | 9.2128 | 8.7159 | 8.1648 | 7.6159 | 6.7495 | 5.7873 | 4.873 | 4.375 | 0.8781 | -1.5444 | -3.1648 | 11.6148 | 11.3546 | 11.071 | 10.7454 | 10.3771 | 10.0159 | 9.5026 | 8.9108 | 8.3505 | 8.1281 | 6.121 | 5.1842 | 3.8628 | 11.0067 | 10.6077 | 10.1842 | 9.7016 | 9.173 | 8.6608 | 7.8648 | 6.9689 | 6.1189 | 5.6842
|  | HAUDAGAIN | HT |  |  |  |  | 10.2046 | 9.8261 | 9.4352 | 9.0159 | 8.5903 | 8.1128 | 7.3087 | 6.4832 | 5.6393 | 4.771 | 0.84136 | -1.7617 | -3.1382 | 11.7271 | 11.5291 | 11.3261 | 11.0893 | 10.8536 | 10.5638 | 10.1505 | 9.7189 | 9.2659 | 8.7975 | 6.825 | 6.0791 | 5.923 | 11.1505 | 10.8067 | 10.4495 | 10.0597 | 9.6679 | 9.2108 | 8.4852 | 7.7301 | 6.9577 | 6.1608
|  | HAUDAGAIN | HE |  |  |  |  | 10.1893 | 9.9352 | 9.675 | 9.3832 | 9.0903 | 8.7475 | 8.1801 | 7.5852 | 6.9781 | 6.3485 | 3.1812 | 0.80157 | -0.85251 | 11.7077 | 11.5454 | 11.371 | 11.1659 | 10.9587 | 10.6985 | 10.3536 | 9.9771 | 9.5883 | 9.1822 | 7.2056 | 6.1271 | 4.8914 | 11.1383 | 10.8944 | 10.6434 | 10.3597 | 10.0791 | 9.7352 | 9.2138 | 8.6556 | 8.0903 | 7.5046
|  | HAUDAGAIN | CF |  |  |  |  | 10.3026 | 10.1638 | 10.0169 | 9.8465 | 9.6577 | 9.4822 | 9.2771 | 9.0097 | 8.7638 | 8.5454 | 6.6761 | 4.8383 | 1.721 | 11.7628 | 11.6597 | 11.5475 | 11.4046 | 11.2403 | 11.0812 | 10.8812 | 10.6403 | 10.4097 | 10.1944 | 8.521 | 6.9505 | 3.8301 | 11.2383 | 11.0985 | 10.9505 | 10.7771 | 10.5812 | 10.4036 | 10.1954 | 9.9301 | 9.6852 | 9.4761
| WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | NO | 0.26 | 17.8233 | 17.3284 | 16.7559 | 16.1263 | 15.4804 | 14.7478 | 13.7569 | 12.6427 | 11.5794 | 10.612 | 5.511 | 2.9692 | 1.6212 | 18.2906 | 17.96 | 17.5539 | 17.1069 | 16.5835 | 15.9069 | 15.1641 | 14.2692 | 13.4824 | 12.8059 | 8.8753 | 7.684 | 7.3401 | 17.4411 | 17.0391 | 16.4962 | 15.8534 | 15.1666 | 14.4074 | 13.4728 | 12.3911 | 11.4064 | 10.536
|  | HAYTON | EE |  |  |  |  | 17.8233 | 17.3284 | 16.7559 | 16.1263 | 15.4804 | 14.7478 | 13.7569 | 12.6427 | 11.5794 | 10.612 | 6.8376 | 4.9365 | 3.2702 | 18.2906 | 17.96 | 17.5539 | 17.1069 | 16.5835 | 15.9069 | 15.1641 | 14.2692 | 13.4824 | 12.8059 | 10.6222 | 10.0472 | 8.534 | 17.4411 | 17.0391 | 16.4962 | 15.8534 | 15.1666 | 14.4074 | 13.4728 | 12.3911 | 11.4064 | 10.536
|  | HAYTON | HT |  |  |  |  | 18.1059 | 17.7212 | 17.2978 | 16.86 | 16.3692 | 15.8141 | 14.9753 | 14.0029 | 13.0304 | 12.0569 | 7.662 | 5.2182 | 3.7865 | 18.509 | 18.2855 | 18.0345 | 17.759 | 17.4386 | 17.0722 | 16.6018 | 16.0243 | 15.4569 | 14.8967 | 12.2396 | 11.5656 | 11.436 | 17.6819 | 17.3789 | 17.0472 | 16.7034 | 16.3085 | 15.7697 | 15.0452 | 14.1921 | 13.3687 | 12.5309
|  | HAYTON | HE |  |  |  |  | 18.0314 | 17.6671 | 17.2733 | 16.8427 | 16.3447 | 15.6304 | 14.7304 | 13.5855 | 12.3998 | 11.16 | 5.511 | 2.9692 | 1.6212 | 18.4386 | 18.1855 | 17.8998 | 17.5773 | 17.0671 | 16.3988 | 15.6743 | 14.7549 | 13.8835 | 12.9773 | 8.8753 | 7.684 | 7.534 | 17.6023 | 17.2881 | 16.9391 | 16.4146 | 15.8044 | 15.0799 | 14.2074 | 13.1136 | 12.0779 | 10.9921
|  | HAYTON | CF |  |  |  |  | 18.1722 | 17.9773 | 17.7549 | 17.509 | 17.2151 | 16.8937 | 16.5518 | 16.0824 | 15.5284 | 14.9314 | 11.2733 | 7.9692 | 5.01 | 18.5233 | 18.3733 | 18.1988 | 17.9967 | 17.7457 | 17.46 | 17.1529 | 16.7488 | 16.2916 | 15.7998 | 12.9202 | 11.0074 | 7.3401 | 17.7319 | 17.5656 | 17.3768 | 17.1646 | 16.8636 | 16.4748 | 16.0697 | 15.5299 | 15.0044 | 14.4432
| BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | NO | 0.022 | 0.36735 | 0.30408 | 0.2551 | 0.19898 | 0.13265 | 0.090816 | 0.0091837 | -0.082653 | -0.18265 | -0.27245 | -0.40714 | -0.4602 | -0.47347 | 0.71939 | 0.67755 | 0.64694 | 0.61531 | 0.57143 | 0.54388 | 0.49388 | 0.43673 | 0.37959 | 0.32347 | 0.23469 | 0.17959 | 0.0071429 | 0.56429 | 0.5051 | 0.4602 | 0.40714 | 0.34592 | 0.3051 | 0.22857 | 0.14286 | 0.05 | -0.034694
|  | HELMSDALE | EE |  |  |  |  | 0.36735 | 0.30408 | 0.2551 | 0.19898 | 0.13265 | 0.090816 | 0.0091837 | -0.082653 | -0.18265 | -0.27245 | -0.40714 | -0.43163 | -0.4449 | 0.71939 | 0.67755 | 0.64694 | 0.61531 | 0.57143 | 0.54388 | 0.49388 | 0.43673 | 0.37959 | 0.32347 | 0.23469 | 0.17959 | 0.094898 | 0.56429 | 0.5051 | 0.4602 | 0.40714 | 0.34592 | 0.3051 | 0.22857 | 0.14286 | 0.05 | -0.034694
|  | HELMSDALE | HT |  |  |  |  | 0.38061 | 0.33061 | 0.28367 | 0.24592 | 0.19592 | 0.13878 | 0.066327 | -0.021429 | -0.064286 | -0.12857 | -0.3949 | -0.4602 | -0.47347 | 0.73469 | 0.70102 | 0.67143 | 0.6449 | 0.61327 | 0.57959 | 0.53878 | 0.4898 | 0.46837 | 0.43367 | 0.26429 | 0.23673 | 0.22857 | 0.58367 | 0.53673 | 0.49082 | 0.45612 | 0.40612 | 0.35714 | 0.28673 | 0.20204 | 0.17143 | 0.10918
|  | HELMSDALE | HE |  |  |  |  | 0.37959 | 0.34184 | 0.31122 | 0.27959 | 0.23673 | 0.20408 | 0.14796 | 0.07449 | 0.028571 | -0.044898 | -0.34796 | -0.37653 | -0.38469 | 0.73061 | 0.70306 | 0.68061 | 0.66122 | 0.63163 | 0.6102 | 0.57347 | 0.52857 | 0.50408 | 0.4602 | 0.27041 | 0.21735 | 0.13878 | 0.58367 | 0.5449 | 0.51327 | 0.48367 | 0.44286 | 0.41224 | 0.3602 | 0.29184 | 0.25 | 0.18265
|  | HELMSDALE | CF |  |  |  |  | 0.38367 | 0.35612 | 0.33163 | 0.29694 | 0.27551 | 0.23673 | 0.21122 | 0.16633 | 0.11224 | 0.057143 | -0.13673 | -0.32245 | -0.36735 | 0.73367 | 0.71633 | 0.7 | 0.67347 | 0.65918 | 0.63571 | 0.61735 | 0.58571 | 0.55306 | 0.51837 | 0.36735 | 0.18061 | 0.0071429 | 0.5898 | 0.56429 | 0.53265 | 0.49796 | 0.47959 | 0.44286 | 0.41939 | 0.37857 | 0.32857 | 0.27755
| INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | NO | 6.821 | 5.8577 | 5.3149 | 4.6945 | 4.0047 | 3.6945 | 3.0261 | 1.9781 | 0.84853 | -0.24738 | -1.2627 | -5.5168 | -7.9933 | -9.2419 | 9.5928 | 9.2979 | 8.952 | 8.5734 | 8.4306 | 8.0071 | 7.4204 | 6.7653 | 6.1285 | 5.5551 | 3.2663 | 2.2132 | -0.398 | 7.003 | 6.5163 | 5.9734 | 5.3989 | 5.0571 | 4.4653 | 3.5367 | 2.4928 | 1.4857 | 0.55711
|  | HILTON | EE |  |  |  |  | 5.8577 | 5.3149 | 4.6945 | 4.0047 | 3.6965 | 3.0302 | 1.9781 | 0.84853 | -0.24738 | -1.2627 | -5.2392 | -7.5688 | -8.9439 | 9.5928 | 9.2979 | 8.952 | 8.5734 | 8.4306 | 8.0071 | 7.4204 | 6.7653 | 6.1285 | 5.5551 | 3.2663 | 2.2132 | 0.45098 | 7.003 | 6.5163 | 5.9734 | 5.3989 | 5.1173 | 4.502 | 3.5367 | 2.4928 | 1.4857 | 0.55711
|  | HILTON | HT |  |  |  |  | 5.9424 | 5.4291 | 4.8669 | 4.3149 | 3.6945 | 3.0261 | 2.3118 | 1.2853 | 0.26894 | -0.76269 | -5.5168 | -7.9933 | -9.2419 | 9.6775 | 9.4306 | 9.1551 | 8.8877 | 8.5765 | 8.2347 | 7.9816 | 7.501 | 6.9979 | 6.4714 | 4.0275 | 3.4653 | 3.2734 | 7.0847 | 6.6153 | 6.1071 | 5.6081 | 5.0571 | 4.4653 | 3.8245 | 2.8989 | 1.9857 | 1.0591
|  | HILTON | HE |  |  |  |  | 5.9955 | 5.7291 | 5.4108 | 5.1149 | 4.72 | 4.2802 | 3.9873 | 3.3169 | 2.6608 | 1.9934 | -1.7719 | -4.3943 | -6.296 | 9.6969 | 9.5234 | 9.3194 | 9.1326 | 8.8969 | 8.6296 | 8.503 | 8.0959 | 7.6938 | 7.2724 | 4.8418 | 3.551 | 1.6836 | 7.1326 | 6.8867 | 6.604 | 6.3418 | 6.0224 | 5.6612 | 5.3765 | 4.7724 | 4.1683 | 3.5489
|  | HILTON | CF |  |  |  |  | 6.2077 | 6.0465 | 5.8751 | 5.7067 | 5.4434 | 5.1587 | 4.8424 | 4.8985 | 4.623 | 4.3404 | 2.0587 | -0.8433 | -4.0562 | 9.8489 | 9.703 | 9.5663 | 9.4275 | 9.2428 | 9.0377 | 8.7765 | 8.7469 | 8.4898 | 8.2194 | 6.2296 | 3.7142 | -0.398 | 7.3367 | 7.1745 | 7.0245 | 6.8765 | 6.6755 | 6.4622 | 6.1857 | 6.2183 | 5.9683 | 5.7112
| ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 0.454 | 14.3061 | 13.9173 | 13.5459 | 13.1357 | 12.7408 | 12.298 | 11.6327 | 11.1531 | 10.5082 | 9.9071 | 7.1255 | 5.1704 | 3.9933 | 16.4943 | 16.2831 | 16.0739 | 15.8392 | 15.6055 | 15.3167 | 14.9076 | 14.6994 | 14.3065 | 13.9514 | 12.1902 | 11.7443 | 10.579 | 15.7933 | 15.4249 | 15.0698 | 14.6708 | 14.279 | 13.8402 | 13.1718 | 12.7861 | 12.1729 | 11.5912
|  | HUME STREET | EE |  |  |  |  | 14.3061 | 13.9173 | 13.5459 | 13.1357 | 12.7408 | 12.298 | 11.6327 | 11.1531 | 10.5082 | 9.9071 | 7.1255 | 5.2602 | 3.9933 | 16.4943 | 16.2831 | 16.0739 | 15.8392 | 15.6055 | 15.3167 | 14.9076 | 14.6994 | 14.3065 | 13.9514 | 12.431 | 11.9045 | 10.8933 | 15.7933 | 15.4249 | 15.0698 | 14.6708 | 14.279 | 13.8402 | 13.1718 | 12.7861 | 12.1729 | 11.5912
|  | HUME STREET | HT |  |  |  |  | 14.4224 | 14.0827 | 13.752 | 13.4327 | 13.0724 | 12.699 | 12.1286 | 11.4939 | 10.8633 | 10.2204 | 7.2092 | 5.1704 | 4.0127 | 16.5953 | 16.431 | 16.2667 | 16.1106 | 15.928 | 15.729 | 15.4606 | 15.132 | 14.7841 | 14.4249 | 12.9861 | 12.6484 | 12.5045 | 15.9157 | 15.6024 | 15.2871 | 14.9831 | 14.6371 | 14.2739 | 13.7371 | 13.132 | 12.5361 | 11.9229
|  | HUME STREET | HE |  |  |  |  | 14.3827 | 14.1235 | 13.8724 | 13.6031 | 13.3398 | 13.0357 | 12.6184 | 12.1276 | 11.65 | 11.1541 | 8.0714 | 6.2418 | 5.1014 | 16.5627 | 16.4096 | 16.2606 | 16.0973 | 15.931 | 15.7331 | 15.4922 | 15.1912 | 14.7514 | 14.282 | 12.1902 | 11.7443 | 11.4576 | 15.8841 | 15.6422 | 15.4004 | 15.1392 | 14.8933 | 14.5984 | 14.2014 | 13.732 | 13.2759 | 12.6759
|  | HUME STREET | CF |  |  |  |  | 14.4776 | 14.3061 | 14.152 | 13.9837 | 13.7969 | 13.6235 | 13.4469 | 13.2357 | 13.0724 | 12.8694 | 11.2551 | 8.8602 | 6.0402 | 16.6116 | 16.5035 | 16.4014 | 16.2902 | 16.1555 | 16.0269 | 15.8769 | 15.6943 | 15.5443 | 15.3657 | 14.0147 | 13.03 | 10.579 | 15.9729 | 15.8137 | 15.6667 | 15.5024 | 15.3208 | 15.1596 | 14.9882 | 14.7759 | 14.6127 | 14.4116
| KEITH 2 | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 1.002 | 8.403 | 7.901 | 7.3551 | 6.7449 | 6.0918 | 5.6061 | 5.1418 | 4.6173 | 4.1081 | 3.849 | 2.2438 | 1.2132 | 0.24691 | 9.7643 | 9.349 | 8.9 | 8.4061 | 7.8704 | 7.5347 | 7.2694 | 6.9194 | 6.6204 | 6.4816 | 5.6581 | 5.5066 | 4.9882 | 9.1342 | 8.6617 | 8.1525 | 7.5882 | 6.977 | 6.527 | 6.1086 | 5.6291 | 5.2086 | 4.9791
|  | HUNTLY | EE |  |  |  |  | 8.4224 | 7.9561 | 7.4734 | 6.9102 | 6.2877 | 5.7796 | 5.1704 | 4.6173 | 4.1081 | 3.9336 | 2.2602 | 1.3296 | 0.35916 | 9.8224 | 9.4214 | 9.0428 | 8.5938 | 8.0877 | 7.6653 | 7.2694 | 6.9194 | 6.6204 | 6.4816 | 5.6581 | 5.5066 | 5.0362 | 9.1586 | 8.6842 | 8.2178 | 7.6852 | 7.1005 | 6.6148 | 6.1086 | 5.6291 | 5.2086 | 4.9791
|  | HUNTLY | HT |  |  |  |  | 8.403 | 7.901 | 7.3551 | 6.7449 | 6.0918 | 5.6061 | 5.1418 | 4.7102 | 4.2796 | 3.849 | 2.2438 | 1.2132 | 0.24691 | 9.7643 | 9.349 | 8.9 | 8.4061 | 7.8704 | 7.5347 | 7.2694 | 7.0224 | 6.7918 | 6.5653 | 5.7173 | 5.6525 | 5.4791 | 9.1342 | 8.6617 | 8.1525 | 7.5882 | 6.977 | 6.527 | 6.1515 | 5.7862 | 5.4362 | 5.0617
|  | HUNTLY | HE |  |  |  |  | 8.4836 | 8.0683 | 7.6734 | 7.2061 | 6.6949 | 6.2602 | 5.8581 | 5.5122 | 5.1459 | 4.7775 | 3.1714 | 2.3153 | 1.1918 | 9.8592 | 9.4755 | 9.1194 | 8.6979 | 8.2418 | 7.8857 | 7.552 | 7.2643 | 7.0041 | 6.7469 | 5.75 | 5.6964 | 5.3484 | 9.2199 | 8.8046 | 8.4097 | 7.9433 | 7.4382 | 7.0015 | 6.578 | 6.2076 | 5.8627 | 5.5158
|  | HUNTLY | CF |  |  |  |  | 8.6887 | 8.4592 | 8.2102 | 7.9643 | 7.6653 | 7.3867 | 7.1214 | 6.8357 | 6.5959 | 6.3663 | 4.8745 | 3.5775 | 1.8714 | 10.0551 | 9.8428 | 9.6132 | 9.3918 | 9.1234 | 8.8765 | 8.6551 | 8.4357 | 8.2367 | 8.0428 | 6.8255 | 6.2056 | 4.9882 | 9.4086 | 9.1903 | 8.9433 | 8.6954 | 8.3995 | 8.1209 | 7.8495 | 7.5597 | 7.3137 | 7.077
| BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | NO | 0.492 | 1.7029 | 1.6733 | 1.6314 | 1.5947 | 1.5508 | 1.5039 | 1.4467 | 1.3855 | 1.3222 | 1.2661 | 1.0355 | 0.91816 | 0.59214 | 1.8799 | 1.8615 | 1.835 | 1.8115 | 1.786 | 1.7544 | 1.7156 | 1.6717 | 1.6279 | 1.5911 | 1.4156 | 1.4475 | 1.3659 | 1.7812 | 1.7557 | 1.721 | 1.6873 | 1.6495 | 1.6087 | 1.5536 | 1.4955 | 1.4363 | 1.3832
|  | INCHBARE | EE |  |  |  |  | 1.7029 | 1.6733 | 1.6314 | 1.5947 | 1.5508 | 1.5039 | 1.4467 | 1.3855 | 1.3222 | 1.2661 | 1.0712 | 0.99979 | 0.7401 | 1.8799 | 1.8615 | 1.835 | 1.8115 | 1.786 | 1.7544 | 1.7156 | 1.6717 | 1.6279 | 1.5911 | 1.4554 | 1.5189 | 1.4934 | 1.7812 | 1.7557 | 1.721 | 1.6873 | 1.6495 | 1.6087 | 1.5536 | 1.4955 | 1.4363 | 1.3832
|  | INCHBARE | HT |  |  |  |  | 1.7161 | 1.6927 | 1.6671 | 1.6365 | 1.5988 | 1.5641 | 1.5212 | 1.4641 | 1.411 | 1.3539 | 1.1039 | 0.9702 | 0.65949 | 1.8911 | 1.8779 | 1.8625 | 1.8432 | 1.8207 | 1.8003 | 1.7717 | 1.736 | 1.6972 | 1.6554 | 1.4779 | 1.4995 | 1.4353 | 1.7944 | 1.7761 | 1.7495 | 1.721 | 1.6883 | 1.6577 | 1.6199 | 1.572 | 1.521 | 1.4659
|  | INCHBARE | HE |  |  |  |  | 1.7161 | 1.6947 | 1.6692 | 1.6396 | 1.6039 | 1.5702 | 1.5243 | 1.4671 | 1.41 | 1.3447 | 1.0355 | 0.91816 | 0.63908 | 1.8911 | 1.8758 | 1.8595 | 1.8401 | 1.8156 | 1.7932 | 1.7625 | 1.7238 | 1.6799 | 1.636 | 1.4156 | 1.4475 | 1.4097 | 1.7944 | 1.7761 | 1.7546 | 1.7291 | 1.6965 | 1.6689 | 1.625 | 1.572 | 1.5148 | 1.4567
|  | INCHBARE | CF |  |  |  |  | 1.7192 | 1.7059 | 1.6927 | 1.6753 | 1.6529 | 1.6284 | 1.6039 | 1.5671 | 1.5314 | 1.4978 | 1.2702 | 1.0406 | 0.59214 | 1.8932 | 1.8809 | 1.8738 | 1.8646 | 1.8493 | 1.835 | 1.8177 | 1.7921 | 1.7687 | 1.7442 | 1.5799 | 1.525 | 1.3659 | 1.7985 | 1.7853 | 1.774 | 1.7587 | 1.7373 | 1.7179 | 1.6975 | 1.6648 | 1.6342 | 1.5995
| DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 0.012 | 1.8561 | 1.802 | 1.7418 | 1.6837 | 1.599 | 1.5184 | 1.3673 | 1.2602 | 1.1245 | 0.99796 | 0.56633 | 0.28673 | 0.016837 | 2.0617 | 2.027 | 1.9862 | 1.9464 | 1.8852 | 1.8311 | 1.7403 | 1.677 | 1.5893 | 1.5128 | 1.2811 | 1.261 | 1.1212 | 1.9538 | 1.9028 | 1.8406 | 1.7875 | 1.7038 | 1.6242 | 1.4865 | 1.3885 | 1.261 | 1.1446
|  | INNELLAN | EE |  |  |  |  | 1.8561 | 1.802 | 1.7418 | 1.6837 | 1.599 | 1.5184 | 1.3673 | 1.2602 | 1.1245 | 0.99796 | 0.56633 | 0.30918 | 0.02398 | 2.0617 | 2.027 | 1.9862 | 1.9464 | 1.8852 | 1.8311 | 1.7403 | 1.677 | 1.5893 | 1.5128 | 1.2811 | 1.261 | 1.1242 | 1.9538 | 1.9028 | 1.8406 | 1.7875 | 1.7038 | 1.6242 | 1.4865 | 1.3885 | 1.261 | 1.1446
|  | INNELLAN | HT |  |  |  |  | 1.8867 | 1.8347 | 1.7827 | 1.7276 | 1.651 | 1.5898 | 1.4694 | 1.3418 | 1.2082 | 1.0878 | 0.58367 | 0.28673 | 0.016837 | 2.0934 | 2.0617 | 2.0321 | 1.9995 | 1.9505 | 1.9209 | 1.8515 | 1.7811 | 1.7036 | 1.6301 | 1.3536 | 1.3314 | 1.313 | 1.9926 | 1.9457 | 1.8957 | 1.8477 | 1.7742 | 1.7232 | 1.6099 | 1.4967 | 1.3773 | 1.262
|  | INNELLAN | HE |  |  |  |  | 1.8867 | 1.8531 | 1.8173 | 1.7837 | 1.7286 | 1.6827 | 1.5735 | 1.4755 | 1.3867 | 1.299 | 0.89082 | 0.62959 | 0.30153 | 2.0934 | 2.0658 | 2.0423 | 2.0158 | 1.973 | 1.9485 | 1.8842 | 1.8219 | 1.7587 | 1.6985 | 1.4342 | 1.3936 | 1.2497 | 1.9926 | 1.9589 | 1.9222 | 1.8895 | 1.8324 | 1.7926 | 1.6936 | 1.6038 | 1.5191 | 1.4324
|  | INNELLAN | CF |  |  |  |  | 1.898 | 1.8765 | 1.8551 | 1.8276 | 1.8031 | 1.7704 | 1.7408 | 1.6806 | 1.6347 | 1.5724 | 1.3071 | 0.99694 | 0.56173 | 2.1005 | 2.0791 | 2.0628 | 2.0372 | 2.0158 | 1.9832 | 1.9607 | 1.9128 | 1.877 | 1.8301 | 1.6168 | 1.4375 | 1.1212 | 2.0028 | 1.9783 | 1.9569 | 1.9212 | 1.8946 | 1.8569 | 1.8314 | 1.7712 | 1.7253 | 1.6661
| KEITH 2 | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 0.562 | 0.73926 | 7.5275 | 6.9275 | 6.2571 | 5.5306 | 4.9898 | 4.5275 | 4.0081 | 3.8796 | 3.4928 | 2.4755 | 2.1836 | -5.5888 | 9.3796 | 9.0469 | 8.6888 | 8.1949 | 7.6398 | 7.2612 | 6.9581 | 6.5898 | 6.5836 | 6.351 | 5.6796 | -1.3084 | 4.8393 | 8.7178 | 8.2678 | 7.7352 | 7.125 | 6.4535 | 5.9505 | 5.5138 | 5.0301 | 4.9321 | 4.577
|  | INSCH | EE |  |  |  |  | 0.73926 | 7.5275 | 6.9959 | 6.35 | 5.6796 | 5.0969 | 4.5275 | 4.0081 | 3.8796 | 3.4928 | 2.4755 | 2.303 | -5.4031 | 9.3796 | 9.0469 | 8.6918 | 8.2326 | 7.7683 | 7.3408 | 6.9581 | 6.5898 | 6.5836 | 6.351 | 5.6796 | -1.3084 | 5.3974 | 8.7178 | 8.2678 | 7.7862 | 7.1944 | 6.5791 | 6.0393 | 5.5138 | 5.0301 | 4.9321 | 4.577
|  | INSCH | HT |  |  |  |  | 0.75763 | 7.5357 | 6.9275 | 6.2571 | 5.5306 | 4.9898 | 4.6408 | 4.2724 | 3.9224 | 3.5704 | 2.7275 | 2.1836 | -5.5888 | 9.4224 | 9.103 | 8.6888 | 8.1949 | 7.6398 | 7.2612 | 7.05 | 6.8183 | 6.6081 | 6.402 | 5.9755 | -1.0135 | 5.9893 | 8.7393 | 8.2893 | 7.7352 | 7.125 | 6.4535 | 5.9505 | 5.6321 | 5.2893 | 4.9658 | 4.6433
|  | INSCH | HE |  |  |  |  | 0.79947 | 7.6816 | 7.2245 | 6.7061 | 6.1132 | 5.5959 | 5.1836 | 4.7979 | 4.4469 | 4.103 | 2.7755 | 2.4143 | -5.3092 | 9.451 | 9.1775 | 8.852 | 8.4714 | 8.0061 | 7.6183 | 7.3296 | 7.0643 | 6.8245 | 6.5949 | 5.8326 | -1.2452 | 5.4597 | 8.776 | 8.4158 | 7.9984 | 7.525 | 6.975 | 6.5015 | 6.1229 | 5.7648 | 5.4372 | 5.1178
|  | INSCH | CF |  |  |  |  | 0.90151 | 7.902 | 7.6081 | 7.2673 | 6.9173 | 6.5469 | 6.1918 | 5.8918 | 5.603 | 5.3102 | 4.1704 | 3.0653 | -5.1684 | 9.5296 | 9.3347 | 9.1367 | 8.8969 | 8.6561 | 8.3857 | 8.1296 | 7.9071 | 7.6877 | 7.4673 | 6.5541 | -1.2595 | 4.8393 | 8.8719 | 8.6209 | 8.3535 | 8.0433 | 7.7209 | 7.3821 | 7.0576 | 6.7831 | 6.5148 | 6.2413
| BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | YES | 14.469 | 5.0112 | 4.5633 | 3.9133 | 3.198 | 2.5122 | 1.8428 | 1.3102 | 0.73877 | 0.25713 | -0.16225 | -1.6276 | -2.5786 | -4.3551 | 5.051 | 4.6357 | 4.0031 | 3.3275 | 2.8469 | 2.5296 | 2.2826 | 1.8133 | 1.4204 | 1.0745 | -0.15919 | -0.27552 | -0.70205 | 5.4541 | 5.0326 | 4.4041 | 3.7347 | 3.1622 | 2.5469 | 2.0439 | 1.5092 | 1.0561 | 0.65816
|  | INVERALMOND | EE |  |  |  |  | 5.0469 | 4.5877 | 3.9571 | 3.198 | 2.5122 | 1.8428 | 1.3102 | 0.73877 | 0.25713 | -0.16225 | -1.4806 | -1.9939 | -3.5602 | 5.1224 | 4.7082 | 4.1673 | 3.5541 | 3.0612 | 2.6408 | 2.2826 | 1.8133 | 1.4204 | 1.0745 | -0.046947 | 0.18264 | -0.061233 | 5.5031 | 5.0775 | 4.5061 | 3.798 | 3.1622 | 2.5469 | 2.0439 | 1.5092 | 1.0561 | 0.65816
|  | INVERALMOND | HT |  |  |  |  | 5.0112 | 4.5633 | 3.9133 | 3.2112 | 2.5898 | 2.0775 | 1.6735 | 1.2602 | 0.89591 | 0.53775 | -0.9245 | -1.8072 | -3.5408 | 5.051 | 4.6357 | 4.0031 | 3.3275 | 2.8469 | 2.5296 | 2.2847 | 2.0633 | 1.8786 | 1.599 | 0.39489 | 0.32958 | -0.058171 | 5.4541 | 5.0326 | 4.4041 | 3.7347 | 3.2265 | 2.7643 | 2.3847 | 1.9969 | 1.6541 | 1.3163
|  | INVERALMOND | HE |  |  |  |  | 5.0898 | 4.6418 | 4.0918 | 3.4184 | 2.7816 | 2.1918 | 1.7041 | 1.1796 | 0.71836 | 0.25611 | -1.6276 | -2.5786 | -4.3551 | 5.15 | 4.7428 | 4.2286 | 3.6357 | 3.151 | 2.7704 | 2.4592 | 2.1561 | 1.7786 | 1.402 | -0.15919 | -0.27552 | -0.70205 | 5.5367 | 5.1194 | 4.5949 | 3.9969 | 3.4112 | 2.8714 | 2.4112 | 1.9214 | 1.4826 | 1.0439
|  | INVERALMOND | CF |  |  |  |  | 5.35 | 5.0428 | 4.6582 | 4.2724 | 3.8816 | 3.4561 | 3.0735 | 2.6551 | 2.2714 | 1.8765 | -0.24184 | -2.0286 | -4.2153 | 5.45 | 5.1806 | 4.8398 | 4.5061 | 4.1755 | 3.8724 | 3.6 | 3.3265 | 3.0806 | 2.8306 | 1.1092 | 0.23367 | -0.54491 | 5.7969 | 5.5133 | 5.1531 | 4.7959 | 4.4347 | 4.0571 | 3.699 | 3.3082 | 2.9531 | 2.5837
| CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 0.003 | 1.902 | 1.8643 | 1.8388 | 1.8469 | 1.798 | 1.7582 | 1.5622 | 1.4367 | 1.3439 | 1.2571 | 1.1459 | 1.1265 | 0.84235 | 2.1372 | 2.1179 | 2.3949 | 2.3796 | 2.3582 | 2.3378 | 2.101 | 1.9541 | 1.8653 | 1.799 | 1.7214 | 1.5395 | 1.4804 | 2.063 | 2.202 | 2.199 | 2.1786 | 2.1541 | 2.1337 | 1.9061 | 1.7673 | 1.6684 | 1.5908
|  | INVERARAY | EE |  |  |  |  | 1.9092 | 1.8898 | 1.8643 | 1.8837 | 1.849 | 1.8041 | 1.7531 | 1.6143 | 1.5051 | 1.4051 | 1.1459 | 1.1357 | 0.85051 | 2.1495 | 2.1413 | 2.4051 | 2.3918 | 2.3724 | 2.3469 | 2.3194 | 2.1745 | 2.051 | 1.952 | 1.7214 | 1.5395 | 1.5161 | 2.0773 | 2.2276 | 2.2143 | 2.198 | 2.1816 | 2.1592 | 2.1327 | 1.9786 | 1.8531 | 1.7449
|  | INVERARAY | HT |  |  |  |  | 1.902 | 1.8643 | 1.8388 | 1.8469 | 1.798 | 1.7582 | 1.5622 | 1.4367 | 1.3439 | 1.2571 | 1.1541 | 1.1265 | 0.84235 | 2.1372 | 2.1179 | 2.3949 | 2.3796 | 2.3582 | 2.3378 | 2.101 | 1.9541 | 1.8653 | 1.799 | 1.7357 | 1.5599 | 1.5518 | 2.063 | 2.202 | 2.199 | 2.1786 | 2.1541 | 2.1337 | 1.9061 | 1.7673 | 1.6684 | 1.5908
|  | INVERARAY | HE |  |  |  |  | 1.9184 | 1.8888 | 1.8735 | 1.8959 | 1.8561 | 1.8184 | 1.7786 | 1.6367 | 1.5255 | 1.4173 | 1.1694 | 1.1582 | 0.88112 | 2.1444 | 2.1281 | 2.4092 | 2.3959 | 2.3786 | 2.3633 | 2.3418 | 2.1867 | 2.0622 | 1.9602 | 1.7316 | 1.5518 | 1.5304 | 2.0722 | 2.2153 | 2.2163 | 2.202 | 2.1816 | 2.1633 | 2.1429 | 1.9898 | 1.8714 | 1.7612
|  | INVERARAY | CF |  |  |  |  | 1.9357 | 1.9204 | 1.9051 | 1.948 | 1.9296 | 1.9133 | 1.8969 | 1.8694 | 1.8092 | 1.7378 | 1.3571 | 1.1806 | 0.85867 | 2.1556 | 2.1454 | 2.4235 | 2.4184 | 2.4092 | 2.4031 | 2.3929 | 2.3806 | 2.3204 | 2.2551 | 1.9224 | 1.5446 | 1.4804 | 2.0844 | 2.2367 | 2.2388 | 2.2327 | 2.2224 | 2.2143 | 2.2051 | 2.1878 | 2.1306 | 2.0673
| LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | YES | 0 | 0.18061 | 0.15204 | 0.12143 | 0.084694 | 0.028571 | -0.030612 | -0.1051 | -0.1949 | -0.26429 | -0.3398 | -0.60612 | -0.71327 | -0.76327 | 0.53061 | 0.50204 | 0.47143 | 0.43673 | 0.39592 | 0.35306 | 0.3 | 0.23673 | 0.18673 | 0.13367 | -0.067347 | -0.1449 | -0.17959 | 0.34796 | 0.31327 | 0.27041 | 0.22755 | 0.17959 | 0.12449 | 0.057143 | -0.020408 | -0.087755 | -0.15306
|  | INVERARITY | EE |  |  |  |  | 0.18061 | 0.15204 | 0.12143 | 0.084694 | 0.028571 | -0.030612 | -0.1051 | -0.1949 | -0.26429 | -0.3398 | -0.60102 | -0.66429 | -0.67143 | 0.53061 | 0.50204 | 0.47143 | 0.43673 | 0.39592 | 0.35306 | 0.3 | 0.23673 | 0.18673 | 0.13367 | -0.054082 | -0.097959 | -0.10306 | 0.34796 | 0.31327 | 0.27041 | 0.22755 | 0.17959 | 0.12449 | 0.057143 | -0.020408 | -0.087755 | -0.15306
|  | INVERARITY | HT |  |  |  |  | 0.18673 | 0.16224 | 0.1398 | 0.11122 | 0.078571 | 0.032653 | -0.026531 | -0.10306 | -0.17041 | -0.24388 | -0.56122 | -0.69286 | -0.73878 | 0.5398 | 0.51837 | 0.49694 | 0.46837 | 0.43571 | 0.40102 | 0.35816 | 0.30612 | 0.25714 | 0.2051 | -0.02551 | -0.11939 | -0.15204 | 0.35816 | 0.33163 | 0.30204 | 0.26531 | 0.22347 | 0.17959 | 0.12653 | 0.056122 | -0.0081633 | -0.072449
|  | INVERARITY | HE |  |  |  |  | 0.18776 | 0.16837 | 0.14898 | 0.12653 | 0.089796 | 0.039796 | -0.021429 | -0.097959 | -0.16939 | -0.24694 | -0.60612 | -0.71327 | -0.76327 | 0.5398 | 0.51735 | 0.4949 | 0.46837 | 0.43673 | 0.4 | 0.35714 | 0.29898 | 0.24694 | 0.18878 | -0.067347 | -0.1449 | -0.17959 | 0.35816 | 0.33163 | 0.30408 | 0.26735 | 0.22755 | 0.18367 | 0.12653 | 0.055102 | -0.011224 | -0.082653
|  | INVERARITY | CF |  |  |  |  | 0.19184 | 0.17857 | 0.16531 | 0.14898 | 0.13571 | 0.11735 | 0.090816 | 0.05102 | 0.0091837 | -0.038776 | -0.30816 | -0.55204 | -0.72755 | 0.54082 | 0.53367 | 0.52347 | 0.5051 | 0.48776 | 0.46633 | 0.44082 | 0.41122 | 0.37959 | 0.34388 | 0.1449 | -0.033673 | -0.15714 | 0.35918 | 0.35102 | 0.33673 | 0.31633 | 0.29286 | 0.26531 | 0.23469 | 0.19796 | 0.1602 | 0.11633
| INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | NO | 0.749 | 1.1805 | 1.0988 | 0.99782 | 0.88251 | 0.75496 | 0.60394 | 0.43251 | 0.21925 | 0.02231 | -0.18891 | -1.1389 | -1.5114 | -1.6012 | 1.3703 | 1.308 | 1.2315 | 1.1407 | 1.0458 | 0.93149 | 0.79986 | 0.6366 | 0.48456 | 0.32537 | -0.39402 | -0.67973 | -0.75524 | 1.2723 | 1.1937 | 1.0988 | 0.98558 | 0.86415 | 0.72027 | 0.557 | 0.3519 | 0.16415 | -0.037894
|  | INVERARNIE | EE |  |  |  |  | 1.1805 | 1.1029 | 1.0121 | 0.91925 | 0.81211 | 0.70394 | 0.57639 | 0.43456 | 0.31007 | 0.21211 | -0.00013878 | -0.015445 | -0.018506 | 1.3703 | 1.3131 | 1.2448 | 1.1774 | 1.0999 | 1.0162 | 0.92435 | 0.81823 | 0.72741 | 0.65802 | 0.50904 | 0.49986 | 0.4968 | 1.2723 | 1.1988 | 1.1111 | 1.0213 | 0.92231 | 0.81721 | 0.6968 | 0.56109 | 0.44272 | 0.35088
|  | INVERARNIE | HT |  |  |  |  | 1.2437 | 1.2213 | 1.1723 | 1.156 | 1.0988 | 1.0356 | 0.96313 | 0.88047 | 0.80292 | 0.72333 | 0.42435 | 0.33149 | 0.32537 | 1.4386 | 1.408 | 1.3713 | 1.3652 | 1.3244 | 1.2764 | 1.2274 | 1.1652 | 1.1111 | 1.0539 | 0.83558 | 0.77537 | 0.77231 | 1.357 | 1.3141 | 1.2652 | 1.2519 | 1.1978 | 1.1366 | 1.0672 | 0.98966 | 0.91619 | 0.8417
|  | INVERARNIE | HE |  |  |  |  | 1.1968 | 1.0988 | 0.99782 | 0.88251 | 0.75496 | 0.60394 | 0.43251 | 0.21925 | 0.02231 | -0.18891 | -1.1389 | -1.5114 | -1.5154 | 1.3835 | 1.308 | 1.2315 | 1.1407 | 1.0458 | 0.93149 | 0.79986 | 0.6366 | 0.48456 | 0.32537 | -0.39402 | -0.67973 | -0.68279 | 1.2886 | 1.1937 | 1.0988 | 0.98558 | 0.86415 | 0.72027 | 0.557 | 0.3519 | 0.16415 | -0.037894
|  | INVERARNIE | CF |  |  |  |  | 1.2478 | 1.1897 | 1.1152 | 1.0346 | 0.94476 | 0.84884 | 0.7417 | 0.59578 | 0.47333 | 0.3366 | -0.45728 | -1.1461 | -1.6012 | 1.4244 | 1.3774 | 1.3223 | 1.2611 | 1.1917 | 1.1203 | 1.0376 | 0.92741 | 0.83149 | 0.72843 | 0.11721 | -0.41034 | -0.75524 | 1.3397 | 1.2805 | 1.2111 | 1.1346 | 1.0468 | 0.95598 | 0.85292 | 0.71517 | 0.59578 | 0.46517
| FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | NO | 0.446 | 3.7907 | 3.4611 | 3.1662 | 2.8489 | 2.5081 | 2.254 | 1.9346 | 1.5866 | 1.2305 | 0.81316 | -0.50317 | -1.0062 | -1.5083 | 4.6438 | 4.404 | 4.1754 | 3.9305 | 3.6693 | 3.5091 | 3.3509 | 3.1162 | 2.8866 | 2.6713 | 1.9703 | 1.855 | 1.2999 | 4.2285 | 3.9509 | 3.6713 | 3.3744 | 3.055 | 2.8295 | 2.5489 | 2.2152 | 1.8846 | 1.554
|  | INVERBERVIE | EE |  |  |  |  | 3.7917 | 3.4754 | 3.1815 | 2.8876 | 2.5519 | 2.254 | 1.9581 | 1.5928 | 1.2376 | 0.87132 | -0.50317 | -0.92664 | -1.4348 | 4.6438 | 4.4325 | 4.2203 | 4.0132 | 3.7662 | 3.5438 | 3.3601 | 3.1162 | 2.8866 | 2.6713 | 1.9703 | 1.855 | 1.5132 | 4.2285 | 3.9601 | 3.6907 | 3.4264 | 3.1152 | 2.8336 | 2.557 | 2.2152 | 1.8846 | 1.554
|  | INVERBERVIE | HT |  |  |  |  | 3.7907 | 3.4611 | 3.1662 | 2.8489 | 2.5081 | 2.2621 | 1.9346 | 1.5866 | 1.2305 | 0.81316 | -0.46643 | -1.0062 | -1.5083 | 4.6479 | 4.404 | 4.1754 | 3.9305 | 3.6693 | 3.5091 | 3.3509 | 3.1968 | 3.0325 | 2.8356 | 2.1305 | 2.0652 | 2.0203 | 4.255 | 3.9509 | 3.6713 | 3.3744 | 3.055 | 2.8295 | 2.5489 | 2.2509 | 1.957 | 1.6091
|  | INVERBERVIE | HE |  |  |  |  | 3.8387 | 3.5744 | 3.3591 | 3.1162 | 2.8509 | 2.654 | 2.4172 | 2.1448 | 1.906 | 1.6203 | 0.22847 | -0.44092 | -1.0205 | 4.6979 | 4.4856 | 4.306 | 4.104 | 3.8846 | 3.7305 | 3.5764 | 3.4315 | 3.2979 | 3.1397 | 2.303 | 2.0662 | 1.704 | 4.2979 | 4.0611 | 3.856 | 3.6295 | 3.3785 | 3.1917 | 2.9805 | 2.7479 | 2.5376 | 2.2795
|  | INVERBERVIE | CF |  |  |  |  | 3.955 | 3.7744 | 3.6132 | 3.4744 | 3.307 | 3.1366 | 3.0101 | 2.854 | 2.6979 | 2.5244 | 1.4499 | 0.32132 | -0.60623 | 4.7846 | 4.6581 | 4.5295 | 4.4254 | 4.2897 | 4.155 | 4.0489 | 3.9183 | 3.7887 | 3.6509 | 2.8703 | 2.1203 | 1.2999 | 4.3938 | 4.2376 | 4.0825 | 3.9591 | 3.8081 | 3.6438 | 3.5315 | 3.3723 | 3.2172 | 3.0458
| GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | NO | 0.012 | 0.14722 | 0.14314 | 0.14008 | 0.13294 | 0.12273 | 0.11253 | 0.10539 | 0.088041 | 0.072735 | 0.073755 | 0.050286 | 0.041102 | 0.020041 | 0.15576 | 0.15371 | 0.15269 | 0.14759 | 0.14147 | 0.13433 | 0.1282 | 0.11698 | 0.10678 | 0.10473 | 0.089429 | 0.089245 | 0.067816 | 0.14435 | 0.14129 | 0.13924 | 0.1321 | 0.1219 | 0.11271 | 0.10353 | 0.088224 | 0.071898 | 0.073939
|  | INVERBROOM | EE |  |  |  |  | 0.14722 | 0.1462 | 0.14008 | 0.13294 | 0.12273 | 0.11253 | 0.10539 | 0.088041 | 0.072735 | 0.073755 | 0.050286 | 0.045184 | 0.026163 | 0.15576 | 0.15678 | 0.15269 | 0.14759 | 0.14147 | 0.13433 | 0.1282 | 0.11698 | 0.10678 | 0.10473 | 0.089429 | 0.091286 | 0.082102 | 0.14435 | 0.14435 | 0.13924 | 0.1321 | 0.1219 | 0.11271 | 0.10353 | 0.088224 | 0.071898 | 0.073939
|  | INVERBROOM | HT |  |  |  |  | 0.15641 | 0.14314 | 0.14416 | 0.13804 | 0.13294 | 0.12886 | 0.11763 | 0.10641 | 0.10335 | 0.091102 | 0.055388 | 0.041102 | 0.020041 | 0.16086 | 0.15371 | 0.15576 | 0.15167 | 0.14963 | 0.14657 | 0.13841 | 0.13127 | 0.13024 | 0.12106 | 0.096571 | 0.097408 | 0.096388 | 0.15455 | 0.14129 | 0.14231 | 0.1372 | 0.1321 | 0.12802 | 0.11578 | 0.10659 | 0.10149 | 0.090265
|  | INVERBROOM | HE |  |  |  |  | 0.15641 | 0.14416 | 0.14518 | 0.14212 | 0.13498 | 0.13294 | 0.12273 | 0.11355 | 0.11151 | 0.098245 | 0.06049 | 0.050286 | 0.030245 | 0.16086 | 0.15473 | 0.15678 | 0.15371 | 0.14963 | 0.14759 | 0.14147 | 0.13433 | 0.13433 | 0.1231 | 0.096571 | 0.095367 | 0.085163 | 0.15455 | 0.14231 | 0.14333 | 0.14027 | 0.13312 | 0.1321 | 0.1219 | 0.11271 | 0.11067 | 0.097408
|  | INVERBROOM | CF |  |  |  |  | 0.15641 | 0.14722 | 0.14927 | 0.14518 | 0.13906 | 0.13498 | 0.13396 | 0.12273 | 0.11763 | 0.11151 | 0.076816 | 0.058449 | 0.031265 | 0.16086 | 0.15371 | 0.15984 | 0.15678 | 0.15269 | 0.14861 | 0.14963 | 0.14045 | 0.13739 | 0.13127 | 0.10167 | 0.089245 | 0.067816 | 0.15455 | 0.14639 | 0.14741 | 0.14333 | 0.1372 | 0.13312 | 0.1321 | 0.12088 | 0.1168 | 0.10965
| FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 0.036 | 0.6949 | 0.69184 | 0.68163 | 0.67143 | 0.65306 | 0.63061 | 0.62551 | 0.60204 | 0.57653 | 0.57143 | 0.53469 | 0.52143 | 0.51735 | 0.82755 | 0.82449 | 0.81939 | 0.81224 | 0.80204 | 0.78776 | 0.78163 | 0.76633 | 0.75 | 0.74694 | 0.71735 | 0.7051 | 0.6602 | 0.78061 | 0.76837 | 0.7602 | 0.75 | 0.73265 | 0.71122 | 0.70714 | 0.68367 | 0.65816 | 0.6551
|  | INVERGARRY | EE |  |  |  |  | 0.7051 | 0.69184 | 0.68163 | 0.67143 | 0.65306 | 0.63061 | 0.62551 | 0.60204 | 0.57653 | 0.57143 | 0.53469 | 0.52755 | 0.52551 | 0.83367 | 0.82449 | 0.81939 | 0.81224 | 0.80204 | 0.78776 | 0.78163 | 0.76633 | 0.75 | 0.74694 | 0.71735 | 0.7051 | 0.68673 | 0.78265 | 0.76837 | 0.7602 | 0.75 | 0.73265 | 0.71122 | 0.70714 | 0.68367 | 0.65816 | 0.6551
|  | INVERGARRY | HT |  |  |  |  | 0.70408 | 0.70204 | 0.69286 | 0.68469 | 0.67449 | 0.65816 | 0.65 | 0.62653 | 0.62245 | 0.60816 | 0.54694 | 0.52143 | 0.51735 | 0.83265 | 0.83469 | 0.82551 | 0.82347 | 0.81735 | 0.8051 | 0.79898 | 0.78673 | 0.78469 | 0.77347 | 0.73367 | 0.71837 | 0.71633 | 0.78265 | 0.78163 | 0.77041 | 0.76327 | 0.75306 | 0.73878 | 0.72959 | 0.70816 | 0.7051 | 0.6898
|  | INVERGARRY | HE |  |  |  |  | 0.70408 | 0.70204 | 0.69592 | 0.69082 | 0.68061 | 0.66633 | 0.65918 | 0.63878 | 0.63776 | 0.62041 | 0.55306 | 0.53571 | 0.53163 | 0.83265 | 0.83469 | 0.82857 | 0.82449 | 0.81939 | 0.8102 | 0.80102 | 0.78878 | 0.78878 | 0.77653 | 0.72959 | 0.7102 | 0.6898 | 0.78265 | 0.78265 | 0.77347 | 0.76837 | 0.75816 | 0.7449 | 0.73776 | 0.71939 | 0.71837 | 0.70102
|  | INVERGARRY | CF |  |  |  |  | 0.6949 | 0.70204 | 0.69592 | 0.69388 | 0.68571 | 0.67653 | 0.66735 | 0.66122 | 0.65 | 0.63469 | 0.58776 | 0.55306 | 0.53571 | 0.82755 | 0.83469 | 0.83061 | 0.82755 | 0.82245 | 0.81429 | 0.80816 | 0.80306 | 0.79184 | 0.78469 | 0.7449 | 0.7051 | 0.6602 | 0.78061 | 0.78265 | 0.77653 | 0.77143 | 0.76531 | 0.75612 | 0.74694 | 0.74082 | 0.72959 | 0.71633
| ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | NO | 3.173 | 5.994 | 5.6787 | 5.2746 | 4.7675 | 4.2848 | 3.4858 | 2.6644 | 1.7593 | 0.78993 | -0.13456 | -2.4029 | -3.1795 | -4.0856 | 5.9614 | 5.6889 | 5.3256 | 4.8746 | 4.4491 | 4.0685 | 3.6818 | 3.1736 | 2.6328 | 2.0838 | 0.013396 | -0.36569 | -0.49324 | 6.0057 | 5.721 | 5.3262 | 4.8527 | 4.3751 | 3.718 | 3.0068 | 2.1976 | 1.3415 | 0.52819
|  | INVERGORDON | EE |  |  |  |  | 5.994 | 5.6787 | 5.2746 | 4.7807 | 4.2848 | 3.8175 | 3.3777 | 2.4634 | 1.4777 | 0.56238 | -2.4029 | -3.1407 | -4.058 | 5.9614 | 5.6889 | 5.3256 | 4.8746 | 4.4491 | 4.0685 | 3.7114 | 3.1756 | 2.6328 | 2.1114 | 0.21136 | 0.34452 | 0.24962 | 6.0057 | 5.721 | 5.3262 | 4.8527 | 4.3751 | 3.9282 | 3.5078 | 2.6843 | 1.8037 | 0.98533
|  | INVERGORDON | HT |  |  |  |  | 6.0665 | 5.744 | 5.3093 | 4.7675 | 4.2869 | 3.4858 | 2.6644 | 1.7593 | 0.78993 | -0.13456 | -2.2386 | -3.1795 | -4.0856 | 6.046 | 5.7838 | 5.4001 | 4.9103 | 4.5246 | 4.1052 | 3.6818 | 3.1736 | 2.642 | 2.0838 | 0.51952 | 0.36187 | 0.26493 | 6.0557 | 5.8006 | 5.3874 | 4.871 | 4.4221 | 3.718 | 3.0068 | 2.1976 | 1.3415 | 0.52819
|  | INVERGORDON | HE |  |  |  |  | 6.0552 | 5.7909 | 5.4379 | 4.9777 | 4.5358 | 4.1185 | 3.7369 | 3.1736 | 2.5716 | 1.9654 | -1.3305 | -2.7907 | -3.8356 | 6.0267 | 5.7726 | 5.4491 | 5.0267 | 4.6358 | 4.2736 | 3.944 | 3.4828 | 2.993 | 2.4838 | 0.013396 | -0.36569 | -0.49324 | 6.0537 | 5.8455 | 5.5037 | 5.0425 | 4.6047 | 4.1955 | 3.8241 | 3.2598 | 2.6374 | 2.0027
|  | INVERGORDON | CF |  |  |  |  | 6.1052 | 5.9614 | 5.7756 | 5.5634 | 5.3012 | 5.0287 | 4.7899 | 4.5246 | 4.144 | 3.7399 | 1.1552 | -1.2274 | -3.0662 | 6.0705 | 5.942 | 5.7624 | 5.5583 | 5.3287 | 5.092 | 4.8797 | 4.645 | 4.3409 | 4.0226 | 1.9624 | 0.50574 | -0.29834 | 6.0578 | 5.9772 | 5.819 | 5.6251 | 5.3659 | 5.1006 | 4.8659 | 4.6027 | 4.2445 | 3.871
| FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | NO | 6.429 | 0.62732 | 14.9528 | 14.7283 | 14.4712 | 14.1967 | 13.8202 | 13.2028 | 12.5743 | 12.0263 | 11.4569 | 10.2232 | 9.7936 | -5.7094 | 16.6283 | 16.4987 | 16.3712 | 16.2151 | 16.0426 | 15.8814 | 15.6141 | 15.2559 | 14.8518 | 14.6763 | 13.759 | -0.071151 | 12.8753 | 16.712 | 16.5416 | 16.3538 | 16.1477 | 15.91 | 15.6436 | 15.1671 | 14.6049 | 13.9508 | 13.6141
|  | INVERLOCHY | EE |  |  |  |  | 0.62732 | 14.9528 | 14.7283 | 14.4712 | 14.1967 | 13.9345 | 13.5641 | 12.8049 | 12.0712 | 11.7273 | 10.2232 | 9.9426 | -5.5023 | 16.6283 | 16.4987 | 16.3712 | 16.2151 | 16.0426 | 15.8814 | 15.6681 | 15.2559 | 14.8518 | 14.7049 | 13.759 | -0.071151 | 13.5824 | 16.712 | 16.5416 | 16.3538 | 16.1477 | 15.91 | 15.6436 | 15.2804 | 14.6049 | 13.9508 | 13.7436
|  | INVERLOCHY | HT |  |  |  |  | 0.68242 | 15.0365 | 14.8396 | 14.6232 | 14.4171 | 13.8202 | 13.2028 | 12.5743 | 12.0263 | 11.4569 | 10.4477 | 9.7936 | -5.7094 | 16.6773 | 16.5753 | 16.4732 | 16.3508 | 16.2416 | 15.9345 | 15.6141 | 15.2865 | 14.9855 | 14.6763 | 14.0885 | 0.27783 | 14.3141 | 16.76 | 16.6192 | 16.4681 | 16.2967 | 16.1202 | 15.7028 | 15.1671 | 14.6304 | 14.1345 | 13.6141
|  | INVERLOCHY | HE |  |  |  |  | 0.6814 | 15.0783 | 14.9283 | 14.7579 | 14.5977 | 14.3977 | 14.16 | 13.7232 | 13.263 | 12.7773 | 10.862 | 10.2345 | -5.1339 | 16.6732 | 16.5834 | 16.4947 | 16.3916 | 16.2916 | 16.162 | 16.009 | 15.76 | 15.4896 | 15.2079 | 14.0947 | 0.10232 | 13.8192 | 16.7569 | 16.6304 | 16.4967 | 16.3457 | 16.1824 | 15.9916 | 15.76 | 15.3702 | 14.9743 | 14.5549
|  | INVERLOCHY | CF |  |  |  |  | 0.72936 | 15.1467 | 15.0141 | 14.8732 | 14.7192 | 14.5885 | 14.4324 | 14.2518 | 13.8977 | 13.5722 | 11.7926 | 10.8396 | -5.2451 | 16.7028 | 16.6243 | 16.5467 | 16.463 | 16.3641 | 16.2794 | 16.1651 | 16.0314 | 15.8192 | 15.6202 | 14.4192 | 0.040073 | 12.8753 | 16.8079 | 16.7365 | 16.6518 | 16.5579 | 16.4518 | 16.3487 | 16.2151 | 16.0314 | 15.7243 | 15.4487
| PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 0.064 | 2.3408 | 2.3204 | 2.2888 | 2.2653 | 2.2255 | 2.1827 | 2.1143 | 2.051 | 2.0122 | 1.9622 | 1.8551 | 1.8214 | 1.8235 | 2.5867 | 2.5735 | 2.551 | 2.5378 | 2.5143 | 2.4878 | 2.4469 | 2.4041 | 2.3796 | 2.3459 | 2.2643 | 2.2255 | 2.1041 | 2.4898 | 2.4714 | 2.4398 | 2.4224 | 2.3908 | 2.3643 | 2.3153 | 2.2541 | 2.2173 | 2.1704
|  | INVERNEIL | EE |  |  |  |  | 2.3408 | 2.3204 | 2.2888 | 2.2653 | 2.2255 | 2.1827 | 2.1143 | 2.051 | 2.0122 | 1.9622 | 1.8551 | 1.8408 | 1.8276 | 2.5867 | 2.5735 | 2.551 | 2.5378 | 2.5143 | 2.4878 | 2.4469 | 2.4041 | 2.3796 | 2.3459 | 2.2643 | 2.2255 | 2.1643 | 2.4898 | 2.4714 | 2.4398 | 2.4224 | 2.3908 | 2.3643 | 2.3153 | 2.2541 | 2.2173 | 2.1704
|  | INVERNEIL | HT |  |  |  |  | 2.3541 | 2.3398 | 2.3184 | 2.3 | 2.2663 | 2.2316 | 2.1867 | 2.1439 | 2.0765 | 2.0235 | 1.8847 | 1.8214 | 1.8235 | 2.598 | 2.5898 | 2.5765 | 2.5633 | 2.5459 | 2.5306 | 2.5031 | 2.4755 | 2.4378 | 2.4061 | 2.3071 | 2.2633 | 2.2653 | 2.5031 | 2.4908 | 2.4694 | 2.451 | 2.4265 | 2.4082 | 2.3786 | 2.3418 | 2.2837 | 2.2337
|  | INVERNEIL | HE |  |  |  |  | 2.3541 | 2.3429 | 2.3245 | 2.3102 | 2.2878 | 2.2551 | 2.2031 | 2.1612 | 2.1071 | 2.0673 | 1.9204 | 1.8806 | 1.8765 | 2.599 | 2.5908 | 2.5796 | 2.5684 | 2.5531 | 2.5337 | 2.5041 | 2.4765 | 2.4459 | 2.4173 | 2.3143 | 2.2592 | 2.2071 | 2.5031 | 2.4929 | 2.4755 | 2.4612 | 2.4378 | 2.4224 | 2.3929 | 2.3612 | 2.3122 | 2.2745
|  | INVERNEIL | CF |  |  |  |  | 2.3602 | 2.349 | 2.3388 | 2.3265 | 2.3143 | 2.2847 | 2.2694 | 2.2316 | 2.198 | 2.1704 | 2.0418 | 1.9255 | 1.8735 | 2.602 | 2.5939 | 2.5867 | 2.5765 | 2.5673 | 2.551 | 2.5378 | 2.5122 | 2.4888 | 2.4694 | 2.3622 | 2.2378 | 2.1041 | 2.5092 | 2.5 | 2.4888 | 2.4765 | 2.4684 | 2.451 | 2.4439 | 2.4204 | 2.3918 | 2.3663
| INVERNESS | INVERNESS | MINIMUM HEADROOM | NH 65302 42625 | NO | NO | 4.547 | 3.4042 | 2.7614 | 1.9981 | 1.1879 | 0.2828 | -0.70087 | -1.3896 | -2.2488 | -3.0723 | -3.6264 | -5.7121 | -6.7488 | -7.6703 | 5.641 | 5.3124 | 4.9093 | 4.4981 | 4.0318 | 3.5206 | 3.2777 | 2.8012 | 2.341 | 2.0195 | 0.87362 | 0.62005 | -0.59322 | 4.5517 | 4.0221 | 3.3711 | 2.6843 | 1.9068 | 1.0537 | 0.55168 | -0.21158 | -0.9575 | -1.4779
|  | INVERNESS | EE |  |  |  |  | 3.4042 | 2.7614 | 1.9981 | 1.1879 | 0.2828 | -0.70087 | -1.3488 | -2.2111 | -3.057 | -3.6264 | -5.6539 | -6.4029 | -7.3396 | 5.641 | 5.3124 | 4.9093 | 4.4981 | 4.0318 | 3.5206 | 3.2777 | 2.8012 | 2.341 | 2.0195 | 0.87362 | 0.62005 | -0.10138 | 4.5517 | 4.0221 | 3.3711 | 2.6843 | 1.9068 | 1.0537 | 0.55168 | -0.21158 | -0.9575 | -1.4779
|  | INVERNESS | HT |  |  |  |  | 3.4848 | 2.8491 | 2.1144 | 1.3277 | 0.46036 | -0.47638 | -1.3896 | -2.2488 | -3.0723 | -3.3274 | -5.7121 | -6.7488 | -7.6703 | 5.7257 | 5.4236 | 5.0655 | 4.7073 | 4.2961 | 3.8644 | 3.4185 | 2.9746 | 2.5512 | 2.5134 | 1.2246 | 1.0598 | 0.97107 | 4.6496 | 4.1303 | 3.517 | 2.8752 | 2.1456 | 1.3649 | 0.58025 | -0.17179 | -0.89322 | -1.1004
|  | INVERNESS | HE |  |  |  |  | 3.4981 | 3.0022 | 2.4053 | 1.7553 | 1.0287 | 0.25933 | -0.46413 | -1.156 | -1.8376 | -1.9468 | -3.9743 | -5.2203 | -6.3845 | 5.7236 | 5.4624 | 5.1481 | 4.8287 | 4.4614 | 4.0869 | 3.6991 | 3.3032 | 2.9195 | 2.9206 | 1.6114 | 1.1262 | 0.36189 | 4.6588 | 4.2558 | 3.7568 | 3.2282 | 2.618 | 1.9741 | 1.3537 | 0.74556 | 0.14454 | 0.085355
|  | INVERNESS | CF |  |  |  |  | 3.6818 | 3.3838 | 2.8961 | 2.3685 | 1.7757 | 1.1134 | 0.61648 | 0.1675 | -0.29475 | -0.55597 | -1.6264 | -3.3417 | -5.6376 | 5.8226 | 5.644 | 5.3767 | 5.1053 | 4.793 | 4.442 | 4.1614 | 3.8675 | 3.5746 | 3.3695 | 2.5083 | 1.3252 | -0.59322 | 4.8149 | 4.5568 | 4.1649 | 3.7425 | 3.2537 | 2.7088 | 2.2976 | 1.9027 | 1.5027 | 1.2496
| KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 3.209 | 11.9984 | 10.7086 | 9.1494 | 7.3841 | 5.6351 | 3.178 | 0.97594 | -1.3343 | -3.7526 | -5.9414 | -15.6006 | -20.7639 | -23.7383 | 16.4321 | 15.4433 | 14.2923 | 13.0484 | 11.6433 | 9.8117 | 7.9892 | 5.9463 | 3.8106 | 1.2943 | -7.4649 | -11.722 | -14.57 | 13.979 | 12.8178 | 11.4392 | 9.878 | 8.278 | 5.8249 | 3.9617 | 1.8617 | -0.40263 | -2.5149
|  | INVERURIE | EE |  |  |  |  | 11.9984 | 10.7086 | 9.1494 | 7.3841 | 5.6351 | 3.3321 | 0.97594 | -1.3343 | -3.7526 | -5.9414 | -12.3261 | -16.6445 | -18.4179 | 16.4321 | 15.4433 | 14.2923 | 13.0484 | 11.6433 | 9.8504 | 7.9892 | 6.0566 | 3.9668 | 1.9923 | -3.3986 | -6.0077 | -7.169 | 13.979 | 12.8178 | 11.4392 | 9.878 | 8.278 | 6.1239 | 3.9617 | 1.8617 | -0.40263 | -2.4577
|  | INVERURIE | HT |  |  |  |  | 12.2953 | 11.0953 | 9.4331 | 7.5861 | 5.7933 | 3.178 | 1.3331 | -1.0486 | -3.4628 | -5.923 | -12.0547 | -17.1292 | -19.8914 | 16.6668 | 15.9014 | 14.7749 | 13.5147 | 12.4463 | 10.4086 | 8.9402 | 7.0372 | 5.0994 | 2.9055 | -2.2169 | -6.1394 | -8.7332 | 14.2504 | 13.181 | 11.6647 | 9.9494 | 8.3739 | 5.8249 | 4.1351 | 1.9555 | -0.23222 | -2.5149
|  | INVERURIE | HE |  |  |  |  | 12.2586 | 11.2566 | 9.83 | 8.1872 | 6.4596 | 4.1096 | 2.3484 | -0.0056939 | -2.5241 | -5.3475 | -15.6006 | -20.7639 | -23.7383 | 16.6229 | 15.8249 | 14.6382 | 13.2545 | 11.9045 | 9.8117 | 8.0474 | 5.9463 | 3.8106 | 1.2943 | -7.4649 | -11.722 | -14.57 | 14.2157 | 13.3168 | 12.0137 | 10.4892 | 8.9331 | 6.6433 | 5.0004 | 2.7821 | 0.34022 | -2.4537
|  | INVERURIE | CF |  |  |  |  | 12.4994 | 11.7208 | 10.7923 | 9.6892 | 8.4178 | 7.1117 | 5.9719 | 4.9688 | 3.8382 | 2.731 | -4.77 | -11.0373 | -14.3679 | 16.7729 | 16.1892 | 15.5249 | 14.731 | 13.728 | 12.7321 | 11.7586 | 10.6617 | 9.5392 | 8.2821 | 1.8933 | -2.8649 | -5.0618 | 14.4382 | 13.7504 | 12.9412 | 11.9841 | 10.8392 | 9.6392 | 8.6127 | 7.7096 | 6.681 | 5.4249
| BROADFORD | KALNAKIL | MINIMUM HEADROOM | NG 69146 53941 | YES | YES | 0.009 | 2.5184 | 2.501 | 2.4847 | 2.4643 | 2.4459 | 2.4194 | 2.3898 | 2.3735 | 2.3439 | 2.3184 | 2.2694 | 2.249 | 2.0209 | 2.4015 | 2.3974 | 2.3852 | 2.373 | 2.3587 | 2.3413 | 2.3209 | 2.3117 | 2.2923 | 2.275 | 2.2403 | 2.3406 | 2.2926 | 2.4763 | 2.462 | 2.4446 | 2.4253 | 2.4089 | 2.3844 | 2.3548 | 2.3385 | 2.3099 | 2.2855
|  | KALNAKIL | EE |  |  |  |  | 2.5184 | 2.501 | 2.4847 | 2.4643 | 2.4459 | 2.4194 | 2.3898 | 2.3735 | 2.3439 | 2.3184 | 2.2694 | 2.2602 | 2.0291 | 2.4077 | 2.3974 | 2.3852 | 2.373 | 2.3587 | 2.3413 | 2.3209 | 2.3117 | 2.2923 | 2.275 | 2.2403 | 2.3406 | 2.3161 | 2.4773 | 2.462 | 2.4446 | 2.4253 | 2.4089 | 2.3844 | 2.3548 | 2.3385 | 2.3099 | 2.2855
|  | KALNAKIL | HT |  |  |  |  | 2.5194 | 2.5092 | 2.4949 | 2.4796 | 2.4673 | 2.449 | 2.4327 | 2.4102 | 2.3847 | 2.3765 | 2.2878 | 2.249 | 2.0209 | 2.4026 | 2.4036 | 2.3934 | 2.3862 | 2.3791 | 2.3679 | 2.3566 | 2.3403 | 2.325 | 2.3209 | 2.2628 | 2.3497 | 2.3477 | 2.4763 | 2.4702 | 2.4559 | 2.4426 | 2.4304 | 2.414 | 2.3967 | 2.3732 | 2.3518 | 2.3426
|  | KALNAKIL | HE |  |  |  |  | 2.5204 | 2.5112 | 2.501 | 2.4898 | 2.4796 | 2.4643 | 2.4531 | 2.4286 | 2.4082 | 2.4031 | 2.3082 | 2.2806 | 2.0526 | 2.4015 | 2.4036 | 2.3964 | 2.3903 | 2.3821 | 2.3709 | 2.3638 | 2.3485 | 2.3352 | 2.3321 | 2.2679 | 2.3569 | 2.3365 | 2.4763 | 2.4722 | 2.461 | 2.4508 | 2.4406 | 2.4273 | 2.4161 | 2.3926 | 2.3732 | 2.3681
|  | KALNAKIL | CF |  |  |  |  | 2.5194 | 2.5184 | 2.5041 | 2.4969 | 2.4908 | 2.4755 | 2.4643 | 2.4561 | 2.4398 | 2.4255 | 2.3622 | 2.3071 | 2.0495 | 2.4036 | 2.4097 | 2.4015 | 2.3954 | 2.3893 | 2.3801 | 2.3719 | 2.3648 | 2.3546 | 2.3444 | 2.2954 | 2.3508 | 2.2926 | 2.4763 | 2.4783 | 2.4661 | 2.4579 | 2.4508 | 2.4365 | 2.4273 | 2.4171 | 2.4028 | 2.3875
| DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 0.22 | 2.3663 | 2.3276 | 2.2898 | 2.2367 | 2.1908 | 2.1143 | 2.0194 | 1.9582 | 1.8796 | 1.8184 | 1.651 | 1.5959 | 1.3597 | 2.4291 | 2.4026 | 2.376 | 2.3393 | 2.3097 | 2.2607 | 2.1995 | 2.1628 | 2.1087 | 2.0668 | 1.9454 | 2.0171 | 1.9212 | 2.4099 | 2.3732 | 2.3375 | 2.2844 | 2.2395 | 2.1691 | 2.0793 | 2.0191 | 1.9446 | 1.8865
|  | KAMES | EE |  |  |  |  | 2.3663 | 2.3276 | 2.2898 | 2.2367 | 2.1908 | 2.1143 | 2.0194 | 1.9582 | 1.8796 | 1.8184 | 1.651 | 1.6255 | 1.3801 | 2.4291 | 2.4026 | 2.376 | 2.3393 | 2.3097 | 2.2607 | 2.1995 | 2.1628 | 2.1087 | 2.0668 | 1.9454 | 2.0171 | 1.9487 | 2.4099 | 2.3732 | 2.3375 | 2.2844 | 2.2395 | 2.1691 | 2.0793 | 2.0191 | 1.9446 | 1.8865
|  | KAMES | HT |  |  |  |  | 2.3867 | 2.3551 | 2.3235 | 2.2765 | 2.2418 | 2.1796 | 2.1204 | 2.0459 | 1.9806 | 1.9357 | 1.699 | 1.5959 | 1.3597 | 2.4464 | 2.426 | 2.4077 | 2.376 | 2.3566 | 2.3199 | 2.2862 | 2.2372 | 2.1954 | 2.1709 | 2.0056 | 2.0467 | 2.0426 | 2.4293 | 2.3987 | 2.3691 | 2.3253 | 2.2916 | 2.2314 | 2.1804 | 2.1089 | 2.0446 | 2.0028
|  | KAMES | HE |  |  |  |  | 2.3867 | 2.3602 | 2.3378 | 2.302 | 2.2745 | 2.2184 | 2.1531 | 2.0929 | 2.0418 | 1.9857 | 1.7704 | 1.7082 | 1.4801 | 2.4464 | 2.4291 | 2.4117 | 2.3862 | 2.3689 | 2.3342 | 2.2985 | 2.2587 | 2.223 | 2.1821 | 2.0332 | 2.0814 | 2.0253 | 2.4293 | 2.4048 | 2.3814 | 2.3477 | 2.3212 | 2.2691 | 2.2099 | 2.1528 | 2.1028 | 2.0497
|  | KAMES | CF |  |  |  |  | 2.3908 | 2.3714 | 2.3459 | 2.3286 | 2.302 | 2.2786 | 2.2408 | 2.1857 | 2.1541 | 2.1112 | 1.9367 | 1.7878 | 1.4801 | 2.4485 | 2.4362 | 2.4189 | 2.4066 | 2.3862 | 2.3719 | 2.3464 | 2.3087 | 2.2893 | 2.2577 | 2.1189 | 2.0742 | 1.9212 | 2.4344 | 2.4181 | 2.3957 | 2.3783 | 2.3508 | 2.3273 | 2.2926 | 2.2416 | 2.213 | 2.1712
| KEITH 2 | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 1.132 | 7.2731 | 7.0037 | 6.72 | 6.371 | 6.0139 | 5.6486 | 5.1139 | 4.5598 | 4.2945 | 3.8241 | 2.0506 | 0.95367 | 0.0097959 | 6.8292 | 6.6639 | 6.5006 | 6.272 | 6.0537 | 5.8384 | 5.5567 | 5.2445 | 5.1516 | 4.9159 | 3.9578 | 3.7144 | 3.247 | 7.4746 | 7.244 | 7.0062 | 6.7032 | 6.396 | 6.094 | 5.6746 | 5.2021 | 4.945 | 4.5736
|  | KEITH | EE |  |  |  |  | 7.2731 | 7.0037 | 6.72 | 6.371 | 6.0139 | 5.6486 | 5.1139 | 4.5598 | 4.3629 | 3.919 | 2.1006 | 1.0455 | 0.084286 | 6.8292 | 6.6639 | 6.5006 | 6.272 | 6.0537 | 5.8384 | 5.5567 | 5.2445 | 5.1516 | 4.9159 | 3.9578 | 3.7144 | 3.247 | 7.4746 | 7.244 | 7.0062 | 6.7032 | 6.396 | 6.094 | 5.6746 | 5.2021 | 4.945 | 4.5736
|  | KEITH | HT |  |  |  |  | 7.3282 | 7.0649 | 6.7955 | 6.4404 | 6.0812 | 5.7496 | 5.2261 | 4.7649 | 4.2945 | 3.8241 | 2.0506 | 0.95367 | 0.0097959 | 6.868 | 6.7057 | 6.5547 | 6.322 | 6.1098 | 5.9271 | 5.6394 | 5.4027 | 5.1669 | 4.9353 | 4.1496 | 4.0552 | 3.9634 | 7.5205 | 7.2919 | 7.0654 | 6.7501 | 6.4521 | 6.1715 | 5.7379 | 5.3409 | 4.9562 | 4.5766
|  | KEITH | HE |  |  |  |  | 7.3373 | 7.1588 | 6.9771 | 6.7394 | 6.4792 | 6.22 | 5.8322 | 5.5006 | 5.1455 | 4.7904 | 3.2557 | 2.1659 | 0.98429 | 6.87 | 6.7435 | 6.6282 | 6.4516 | 6.2792 | 6.1108 | 5.8976 | 5.6751 | 5.4476 | 5.221 | 4.3455 | 4.1328 | 3.5797 | 7.5226 | 7.3552 | 7.196 | 6.9715 | 6.7409 | 6.5083 | 6.1858 | 5.8603 | 5.5419 | 5.2226
|  | KEITH | CF |  |  |  |  | 7.3812 | 7.2822 | 7.1567 | 7.0282 | 6.8516 | 6.7241 | 6.5578 | 6.3537 | 6.2129 | 6.0241 | 4.7414 | 3.768 | 2.0496 | 6.8904 | 6.82 | 6.7373 | 6.6455 | 6.52 | 6.422 | 6.3016 | 6.1618 | 6.0496 | 5.9118 | 4.9976 | 4.4756 | 3.2634 | 7.5664 | 7.4797 | 7.3766 | 7.2623 | 7.1134 | 6.995 | 6.8501 | 6.6787 | 6.5338 | 6.3603
| KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 0.22 | 10.7459 | 10.5878 | 10.3908 | 10.1898 | 9.9918 | 9.7051 | 9.2816 | 8.799 | 8.3173 | 7.7541 | 6.3776 | 5.75 | 4.8776 | 11.4929 | 11.4071 | 11.2908 | 11.1827 | 11.0551 | 10.8531 | 10.5959 | 10.2857 | 9.9582 | 9.6143 | 8.6847 | 8.6801 | 8.274 | 11.1587 | 11.0117 | 10.8291 | 10.6464 | 10.4464 | 10.174 | 9.8077 | 9.3801 | 8.9434 | 8.427
|  | KEMNAY | EE |  |  |  |  | 10.7459 | 10.5878 | 10.3969 | 10.1969 | 9.9918 | 9.7071 | 9.3122 | 8.8653 | 8.402 | 7.9184 | 6.4459 | 5.8204 | 4.9388 | 11.4929 | 11.4071 | 11.2908 | 11.1827 | 11.0551 | 10.8531 | 10.5959 | 10.2857 | 9.9582 | 9.6143 | 8.6847 | 8.6801 | 8.3383 | 11.1587 | 11.0117 | 10.8291 | 10.6464 | 10.4464 | 10.174 | 9.8077 | 9.3801 | 8.9434 | 8.4893
|  | KEMNAY | HT |  |  |  |  | 10.7806 | 10.6071 | 10.3908 | 10.1898 | 10.0092 | 9.7051 | 9.2816 | 8.799 | 8.3173 | 7.7541 | 6.3776 | 5.75 | 4.8776 | 11.5357 | 11.451 | 11.3439 | 11.2418 | 11.1459 | 10.9398 | 10.6684 | 10.3439 | 10.0194 | 9.6153 | 8.8337 | 8.9209 | 8.8638 | 11.2026 | 11.0474 | 10.8607 | 10.676 | 10.5056 | 10.226 | 9.8362 | 9.3862 | 8.9515 | 8.427
|  | KEMNAY | HE |  |  |  |  | 10.7857 | 10.6888 | 10.5663 | 10.4214 | 10.2939 | 10.1082 | 9.7959 | 9.4592 | 9.1357 | 8.7367 | 7.2051 | 6.4888 | 5.4429 | 11.5337 | 11.4735 | 11.4 | 11.3133 | 11.2276 | 11.0918 | 10.8653 | 10.6163 | 10.3735 | 10.0673 | 9.0112 | 8.9403 | 8.5495 | 11.2066 | 11.1158 | 11.0036 | 10.8689 | 10.7454 | 10.575 | 10.2811 | 9.9597 | 9.6607 | 9.2862
|  | KEMNAY | CF |  |  |  |  | 10.8184 | 10.7704 | 10.7051 | 10.6347 | 10.552 | 10.4367 | 10.3102 | 10.1357 | 9.9724 | 9.7776 | 8.6704 | 7.5418 | 6.1418 | 11.55 | 11.5143 | 11.4612 | 11.4143 | 11.3541 | 11.2602 | 11.1622 | 11.0102 | 10.8643 | 10.6898 | 9.7571 | 9.1107 | 8.274 | 11.2383 | 11.1913 | 11.1209 | 11.0566 | 10.977 | 10.8628 | 10.7464 | 10.577 | 10.4158 | 10.227
| TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0 | 0.79694 | 0.79082 | 0.79286 | 0.78061 | 0.77551 | 0.76429 | 0.75918 | 0.7449 | 0.73163 | 0.72041 | 0.69796 | 0.68776 | 0.68061 | 0.86735 | 0.86122 | 0.86531 | 0.85816 | 0.85408 | 0.84796 | 0.84388 | 0.83571 | 0.82551 | 0.81327 | 0.80408 | 0.80204 | 0.77857 | 0.84184 | 0.83878 | 0.83776 | 0.82551 | 0.82143 | 0.81327 | 0.80612 | 0.79082 | 0.77857 | 0.76735
|  | KENMORE | EE |  |  |  |  | 0.79694 | 0.79694 | 0.79286 | 0.78061 | 0.77551 | 0.76429 | 0.75918 | 0.7449 | 0.73163 | 0.72041 | 0.70612 | 0.70408 | 0.70408 | 0.86735 | 0.86939 | 0.86531 | 0.85816 | 0.85408 | 0.84796 | 0.84388 | 0.83571 | 0.82551 | 0.81327 | 0.80714 | 0.80306 | 0.7898 | 0.84184 | 0.84184 | 0.83776 | 0.82551 | 0.82143 | 0.81327 | 0.80612 | 0.79082 | 0.77857 | 0.76735
|  | KENMORE | HT |  |  |  |  | 0.80408 | 0.79184 | 0.79796 | 0.79184 | 0.78878 | 0.77653 | 0.77347 | 0.76429 | 0.75408 | 0.74694 | 0.71122 | 0.69694 | 0.69184 | 0.87041 | 0.86122 | 0.86939 | 0.86735 | 0.86327 | 0.85714 | 0.8551 | 0.84898 | 0.84184 | 0.83776 | 0.81531 | 0.80714 | 0.80612 | 0.85 | 0.83878 | 0.84388 | 0.83776 | 0.83469 | 0.82347 | 0.82041 | 0.81224 | 0.80102 | 0.79388
|  | KENMORE | HE |  |  |  |  | 0.80306 | 0.79082 | 0.80102 | 0.7949 | 0.7898 | 0.78367 | 0.77755 | 0.76735 | 0.75612 | 0.74898 | 0.69796 | 0.68776 | 0.68061 | 0.86939 | 0.86122 | 0.87041 | 0.86837 | 0.86327 | 0.8602 | 0.85612 | 0.85204 | 0.84388 | 0.84082 | 0.80408 | 0.80612 | 0.79082 | 0.84898 | 0.83878 | 0.8449 | 0.84082 | 0.83469 | 0.82857 | 0.82449 | 0.81531 | 0.8051 | 0.79694
|  | KENMORE | CF |  |  |  |  | 0.80408 | 0.7949 | 0.79286 | 0.79592 | 0.79286 | 0.79082 | 0.78265 | 0.78061 | 0.77449 | 0.76837 | 0.73776 | 0.70918 | 0.6898 | 0.87041 | 0.86122 | 0.86633 | 0.86837 | 0.86633 | 0.86633 | 0.8602 | 0.8551 | 0.85204 | 0.84796 | 0.82653 | 0.80204 | 0.77857 | 0.84898 | 0.8398 | 0.83776 | 0.84184 | 0.83878 | 0.83776 | 0.82857 | 0.82653 | 0.82041 | 0.81531
| STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 1.179 | 1.8887 | 1.7693 | 1.6234 | 9.699 | 9.5582 | 9.3745 | 9.1337 | 8.9051 | 8.648 | 8.4173 | 7.5867 | 7 | -1.8016 | 2.8861 | 2.8167 | 10.5418 | 10.4327 | 10.3469 | 10.2235 | 10.0714 | 9.9418 | 9.7776 | 9.6367 | 9.1888 | 1.2476 | 0.8823 | 2.2649 | 10.1984 | 10.0708 | 9.928 | 9.8024 | 9.6494 | 9.4392 | 9.2392 | 9.0167 | 8.8167
|  | KEPCULLOCH | EE |  |  |  |  | 1.8887 | 1.7693 | 1.6234 | 9.699 | 9.5582 | 9.3745 | 9.1337 | 8.9051 | 8.648 | 8.4173 | 7.6204 | 7.149 | -1.6424 | 2.8861 | 2.8167 | 10.5418 | 10.4327 | 10.3469 | 10.2235 | 10.0714 | 9.9418 | 9.7776 | 9.6367 | 9.1888 | 1.2476 | 0.95679 | 2.2649 | 10.1984 | 10.0708 | 9.928 | 9.8024 | 9.6494 | 9.4392 | 9.2392 | 9.0167 | 8.8167
|  | KEPCULLOCH | HT |  |  |  |  | 1.9254 | 1.807 | 1.6774 | 9.7898 | 9.6398 | 9.4786 | 9.2929 | 9.0582 | 8.8316 | 8.5959 | 7.5867 | 7 | -1.8016 | 2.9239 | 2.8616 | 10.6092 | 10.5398 | 10.4561 | 10.3531 | 10.2602 | 10.1245 | 9.9918 | 9.8531 | 9.2776 | 1.3303 | 1.2119 | 2.2966 | 10.229 | 10.1167 | 10.0035 | 9.8729 | 9.7351 | 9.5678 | 9.3627 | 9.1657 | 8.9565
|  | KEPCULLOCH | HE |  |  |  |  | 1.9264 | 1.8458 | 1.7601 | 9.9133 | 9.8061 | 9.6827 | 9.5531 | 9.3704 | 9.1908 | 9.0051 | 8.0622 | 7.5153 | -1.3414 | 2.9198 | 2.8718 | 10.6306 | 10.5755 | 10.5031 | 10.4173 | 10.3418 | 10.2245 | 10.1051 | 9.9816 | 9.3939 | 1.3864 | 1.0843 | 2.2976 | 10.2667 | 10.1902 | 10.1147 | 10.0259 | 9.9259 | 9.8055 | 9.6514 | 9.4984 | 9.3422
|  | KEPCULLOCH | CF |  |  |  |  | 1.9479 | 1.8928 | 1.8274 | 9.9857 | 9.9204 | 9.8357 | 9.7367 | 9.6163 | 9.551 | 9.4378 | 8.8194 | 8.1296 | -0.93327 | 2.9341 | 2.8984 | 10.6694 | 10.6061 | 10.5633 | 10.498 | 10.4255 | 10.3347 | 10.2857 | 10.2 | 9.7235 | 1.4629 | 0.8823 | 2.317 | 10.3076 | 10.2524 | 10.181 | 10.1269 | 10.0606 | 9.98 | 9.8861 | 9.8269 | 9.7392
| TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0 | 0.27543 | 0.2642 | 0.2591 | 0.24788 | 0.25502 | 0.2438 | 0.24482 | 0.23563 | 0.22951 | 0.22237 | 0.19788 | 0.18563 | 0.15149 | 0.27496 | 0.2668 | 0.26373 | 0.25353 | 0.26067 | 0.25047 | 0.25353 | 0.25047 | 0.24537 | 0.24129 | 0.2219 | 0.22723 | 0.22213 | 0.27826 | 0.26703 | 0.26295 | 0.25172 | 0.25887 | 0.24866 | 0.24968 | 0.2405 | 0.23438 | 0.22826
|  | KERRERA | EE |  |  |  |  | 0.27543 | 0.2642 | 0.2591 | 0.24788 | 0.25604 | 0.25196 | 0.24482 | 0.23563 | 0.22951 | 0.22237 | 0.20298 | 0.20196 | 0.17394 | 0.27496 | 0.2668 | 0.26373 | 0.25353 | 0.26169 | 0.26373 | 0.25863 | 0.25047 | 0.24537 | 0.24129 | 0.227 | 0.2405 | 0.2405 | 0.27826 | 0.26703 | 0.26295 | 0.25172 | 0.25887 | 0.25785 | 0.24968 | 0.2405 | 0.23438 | 0.22826
|  | KERRERA | HT |  |  |  |  | 0.28461 | 0.27441 | 0.27033 | 0.26012 | 0.25502 | 0.2438 | 0.25196 | 0.24788 | 0.24176 | 0.23461 | 0.2091 | 0.19482 | 0.16271 | 0.28312 | 0.27394 | 0.27496 | 0.26578 | 0.26169 | 0.25251 | 0.25965 | 0.26169 | 0.25557 | 0.25047 | 0.23006 | 0.23642 | 0.23234 | 0.28744 | 0.27723 | 0.27519 | 0.26499 | 0.26091 | 0.24968 | 0.25581 | 0.25274 | 0.24662 | 0.2405
|  | KERRERA | HE |  |  |  |  | 0.28461 | 0.27339 | 0.27033 | 0.26012 | 0.25502 | 0.2438 | 0.25094 | 0.24686 | 0.23869 | 0.23155 | 0.19788 | 0.18563 | 0.15149 | 0.28312 | 0.27496 | 0.27394 | 0.26476 | 0.26067 | 0.25047 | 0.26169 | 0.25965 | 0.25251 | 0.24741 | 0.2219 | 0.22723 | 0.22213 | 0.28744 | 0.27723 | 0.27315 | 0.26397 | 0.25887 | 0.24866 | 0.25683 | 0.25274 | 0.2456 | 0.23642
|  | KERRERA | CF |  |  |  |  | 0.28461 | 0.27645 | 0.27441 | 0.27135 | 0.26114 | 0.2591 | 0.24788 | 0.25706 | 0.254 | 0.25094 | 0.22237 | 0.19992 | 0.16067 | 0.28414 | 0.27496 | 0.27394 | 0.27394 | 0.2668 | 0.26373 | 0.25353 | 0.26271 | 0.26169 | 0.26271 | 0.24129 | 0.23744 | 0.22826 | 0.28744 | 0.27928 | 0.27723 | 0.27417 | 0.26499 | 0.26193 | 0.2507 | 0.25989 | 0.25887 | 0.25581
| GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | NO | 0.561 | 1.8082 | 1.7663 | 1.7153 | 1.6602 | 1.6143 | 1.5592 | 1.4837 | 1.3837 | 1.3041 | 1.2143 | 1.0296 | 0.96837 | 0.93878 | 1.8786 | 1.8643 | 1.8449 | 1.8153 | 1.8031 | 1.7786 | 1.7255 | 1.6398 | 1.5898 | 1.5184 | 1.3612 | 1.2867 | 1.0357 | 1.7449 | 1.7122 | 1.6704 | 1.6245 | 1.5908 | 1.549 | 1.4878 | 1.4071 | 1.3531 | 1.2827
|  | KERRY FALLS | EE |  |  |  |  | 1.8082 | 1.7663 | 1.7153 | 1.6602 | 1.6143 | 1.5592 | 1.4837 | 1.3837 | 1.3041 | 1.2143 | 1.0296 | 0.9949 | 0.98163 | 1.8786 | 1.8643 | 1.8449 | 1.8153 | 1.8031 | 1.7786 | 1.7255 | 1.6398 | 1.5898 | 1.5184 | 1.3612 | 1.2867 | 1.1643 | 1.7449 | 1.7122 | 1.6704 | 1.6245 | 1.5908 | 1.549 | 1.4878 | 1.4071 | 1.3531 | 1.2827
|  | KERRY FALLS | HT |  |  |  |  | 1.8224 | 1.7806 | 1.7388 | 1.6929 | 1.648 | 1.5786 | 1.5092 | 1.4214 | 1.3653 | 1.3071 | 1.0837 | 0.96837 | 0.93878 | 1.8939 | 1.8806 | 1.8684 | 1.848 | 1.8347 | 1.8071 | 1.7888 | 1.7449 | 1.7 | 1.6469 | 1.448 | 1.3622 | 1.349 | 1.7602 | 1.7276 | 1.6949 | 1.6582 | 1.6235 | 1.5694 | 1.5194 | 1.4541 | 1.4102 | 1.3612
|  | KERRY FALLS | HE |  |  |  |  | 1.8224 | 1.7908 | 1.7633 | 1.7296 | 1.6959 | 1.6582 | 1.6184 | 1.5459 | 1.4806 | 1.4082 | 1.099 | 1.0163 | 1.002 | 1.8949 | 1.8827 | 1.8714 | 1.8531 | 1.8418 | 1.8214 | 1.8122 | 1.7816 | 1.7418 | 1.6827 | 1.4439 | 1.3357 | 1.2245 | 1.7612 | 1.7347 | 1.7112 | 1.6827 | 1.6571 | 1.6245 | 1.5969 | 1.5429 | 1.4939 | 1.4398
|  | KERRY FALLS | CF |  |  |  |  | 1.8265 | 1.802 | 1.7704 | 1.7439 | 1.7122 | 1.6867 | 1.652 | 1.6265 | 1.5765 | 1.5265 | 1.3296 | 1.1653 | 1.0439 | 1.8969 | 1.8857 | 1.8704 | 1.8602 | 1.8439 | 1.8347 | 1.8184 | 1.8092 | 1.7878 | 1.7663 | 1.5653 | 1.3082 | 1.0357 | 1.7612 | 1.7418 | 1.7143 | 1.6929 | 1.6653 | 1.6449 | 1.6143 | 1.5939 | 1.5531 | 1.5143
| TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0.046 | 0.19082 | 0.17449 | 0.15408 | 0.12959 | 0.10306 | 0.085714 | 0.057143 | 0.028571 | -0.0030612 | -0.033673 | -0.09898 | -0.12347 | -0.12857 | 0.44388 | 0.43367 | 0.41837 | 0.40306 | 0.38776 | 0.37959 | 0.35816 | 0.3398 | 0.32041 | 0.30306 | 0.25102 | 0.23061 | 0.16224 | 0.33367 | 0.31633 | 0.29796 | 0.27551 | 0.24796 | 0.23469 | 0.2051 | 0.17959 | 0.14796 | 0.11837
|  | KILCHRENAN | EE |  |  |  |  | 0.19082 | 0.17449 | 0.15408 | 0.12959 | 0.10306 | 0.085714 | 0.057143 | 0.028571 | -0.0030612 | -0.033673 | -0.09898 | -0.1102 | -0.11531 | 0.44388 | 0.43367 | 0.41837 | 0.40306 | 0.38776 | 0.37959 | 0.35816 | 0.3398 | 0.32041 | 0.30306 | 0.25102 | 0.23061 | 0.1949 | 0.33367 | 0.31633 | 0.29796 | 0.27551 | 0.24796 | 0.23469 | 0.2051 | 0.17959 | 0.14796 | 0.11837
|  | KILCHRENAN | HT |  |  |  |  | 0.2 | 0.18469 | 0.17041 | 0.14898 | 0.13469 | 0.11224 | 0.088776 | 0.072449 | 0.046939 | 0.020408 | -0.080612 | -0.12347 | -0.12857 | 0.45102 | 0.44082 | 0.43367 | 0.42347 | 0.41429 | 0.4 | 0.38469 | 0.37653 | 0.36122 | 0.34388 | 0.27755 | 0.25306 | 0.25 | 0.33776 | 0.32653 | 0.31429 | 0.29592 | 0.27959 | 0.26122 | 0.23776 | 0.22143 | 0.19898 | 0.17245
|  | KILCHRENAN | HE |  |  |  |  | 0.2 | 0.18571 | 0.17653 | 0.1602 | 0.14898 | 0.12959 | 0.10816 | 0.094898 | 0.071429 | 0.047959 | -0.065306 | -0.092857 | -0.094898 | 0.45102 | 0.44184 | 0.43367 | 0.42449 | 0.41531 | 0.40408 | 0.39082 | 0.38061 | 0.36633 | 0.35 | 0.27449 | 0.24388 | 0.20918 | 0.33776 | 0.32755 | 0.31837 | 0.30612 | 0.29388 | 0.27551 | 0.25306 | 0.2449 | 0.22041 | 0.19796
|  | KILCHRENAN | CF |  |  |  |  | 0.20102 | 0.19082 | 0.17857 | 0.16837 | 0.1551 | 0.14694 | 0.13061 | 0.11122 | 0.10714 | 0.091837 | 0.014286 | -0.061224 | -0.073469 | 0.45306 | 0.44388 | 0.43571 | 0.42959 | 0.42347 | 0.41429 | 0.40306 | 0.38571 | 0.38469 | 0.37347 | 0.31327 | 0.23061 | 0.16224 | 0.33878 | 0.33265 | 0.32143 | 0.31224 | 0.30204 | 0.29184 | 0.27755 | 0.25918 | 0.25408 | 0.2398
| STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | 0.456 | -1.1214 | -1.2255 | -1.3327 | -1.4653 | -1.6173 | -1.7765 | -1.9592 | -2.1673 | -2.3653 | -2.549 | -3.2592 | -3.7643 | -4.0184 | -0.26224 | -0.32449 | -0.38776 | -0.47245 | -0.56429 | -0.6602 | -0.75612 | -0.88776 | -1.0041 | -1.1133 | -1.4531 | -1.7194 | -1.9724 | -0.63265 | -0.72143 | -0.81429 | -0.93061 | -1.0673 | -1.2102 | -1.3653 | -1.552 | -1.7286 | -1.8908
|  | KILLEARN | EE |  |  |  |  | -1.1214 | -1.2255 | -1.3327 | -1.4653 | -1.6173 | -1.7765 | -1.9592 | -2.1673 | -2.3653 | -2.549 | -3.1806 | -3.6316 | -3.8622 | -0.26224 | -0.32449 | -0.38776 | -0.47245 | -0.56429 | -0.6602 | -0.75612 | -0.88776 | -1.0041 | -1.1133 | -1.4531 | -1.7194 | -1.9602 | -0.63265 | -0.72143 | -0.81429 | -0.93061 | -1.0673 | -1.2102 | -1.3653 | -1.552 | -1.7286 | -1.8908
|  | KILLEARN | HT |  |  |  |  | -1.101 | -1.199 | -1.3153 | -1.4582 | -1.5867 | -1.7357 | -1.9102 | -2.1061 | -2.2602 | -2.4459 | -3.2592 | -3.7643 | -4.0184 | -0.23878 | -0.28878 | -0.35306 | -0.43163 | -0.49898 | -0.58163 | -0.67449 | -0.78673 | -0.86122 | -0.96429 | -1.4122 | -1.6684 | -1.8031 | -0.60612 | -0.69184 | -0.79286 | -0.91327 | -1.0214 | -1.148 | -1.299 | -1.4694 | -1.598 | -1.7602
|  | KILLEARN | HE |  |  |  |  | -1.0898 | -1.1561 | -1.2367 | -1.3429 | -1.4327 | -1.552 | -1.7051 | -1.8541 | -1.9602 | -2.1 | -2.8255 | -3.3245 | -3.6296 | -0.23673 | -0.27857 | -0.32755 | -0.39898 | -0.45408 | -0.52347 | -0.61224 | -0.70918 | -0.76837 | -0.85612 | -1.3031 | -1.6061 | -1.8714 | -0.59796 | -0.65612 | -0.72551 | -0.81735 | -0.89592 | -1 | -1.1327 | -1.2673 | -1.3571 | -1.4816
|  | KILLEARN | CF |  |  |  |  | -1.0694 | -1.1102 | -1.1724 | -1.2367 | -1.3173 | -1.3735 | -1.4643 | -1.5735 | -1.6704 | -1.7755 | -2.2969 | -2.8388 | -3.2806 | -0.22551 | -0.25408 | -0.3 | -0.3449 | -0.39694 | -0.43776 | -0.49898 | -0.57245 | -0.6398 | -0.71122 | -1.0827 | -1.5133 | -1.9724 | -0.57959 | -0.61633 | -0.67347 | -0.72857 | -0.80204 | -0.84898 | -0.92959 | -1.0276 | -1.1143 | -1.2082
| KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 0.131 | 1.9939 | 1.9622 | 1.9286 | 1.8755 | 1.8255 | 1.7643 | 1.7122 | 1.6327 | 1.5653 | 1.498 | 1.3102 | 1.2112 | 0.9352 | 2.0526 | 2.026 | 2.0026 | 1.9617 | 1.9342 | 1.8923 | 1.8607 | 1.8046 | 1.7617 | 1.7168 | 1.5791 | 1.6191 | 1.4365 | 2.012 | 1.9763 | 1.9416 | 1.8926 | 1.8497 | 1.7957 | 1.7457 | 1.6753 | 1.614 | 1.5559
|  | KILLIN TOWN | EE |  |  |  |  | 1.9939 | 1.9622 | 1.9286 | 1.8755 | 1.8255 | 1.7643 | 1.7122 | 1.6327 | 1.5653 | 1.498 | 1.3102 | 1.2459 | 0.97194 | 2.0526 | 2.026 | 2.0026 | 1.9617 | 1.9342 | 1.8923 | 1.8607 | 1.8046 | 1.7617 | 1.7168 | 1.5791 | 1.6191 | 1.5242 | 2.012 | 1.9763 | 1.9416 | 1.8926 | 1.8497 | 1.7957 | 1.7457 | 1.6753 | 1.614 | 1.5559
|  | KILLIN TOWN | HT |  |  |  |  | 2.0173 | 1.9939 | 1.9551 | 1.9112 | 1.8755 | 1.8235 | 1.7765 | 1.7112 | 1.648 | 1.6061 | 1.3449 | 1.2112 | 0.9352 | 2.0709 | 2.0536 | 2.025 | 1.9964 | 1.977 | 1.9454 | 1.9168 | 1.875 | 1.8332 | 1.8097 | 1.6383 | 1.6691 | 1.6365 | 2.0314 | 1.9997 | 1.9671 | 1.9263 | 1.8946 | 1.8487 | 1.8089 | 1.7487 | 1.6946 | 1.6548
|  | KILLIN TOWN | HE |  |  |  |  | 2.0173 | 1.9949 | 1.9663 | 1.9296 | 1.898 | 1.8571 | 1.8122 | 1.751 | 1.6939 | 1.6439 | 1.3622 | 1.2561 | 1.0117 | 2.0668 | 2.0505 | 2.0321 | 2.0026 | 1.9821 | 1.9505 | 1.9168 | 1.8709 | 1.827 | 1.7934 | 1.5893 | 1.6263 | 1.5548 | 2.0304 | 2.0038 | 1.9783 | 1.9446 | 1.9181 | 1.8793 | 1.8416 | 1.7885 | 1.7385 | 1.6957
|  | KILLIN TOWN | CF |  |  |  |  | 2.0214 | 2.0112 | 1.9827 | 1.9582 | 1.9255 | 1.9041 | 1.8673 | 1.8367 | 1.798 | 1.7561 | 1.5643 | 1.3786 | 1.0056 | 2.0689 | 2.0587 | 2.0403 | 2.0199 | 2.0005 | 1.9862 | 1.9597 | 1.9332 | 1.9056 | 1.876 | 1.7199 | 1.6385 | 1.4365 | 2.0314 | 2.0161 | 1.9885 | 1.9681 | 1.9406 | 1.9181 | 1.8885 | 1.8599 | 1.8242 | 1.7906
| TAYNUILT | KILMELFORD | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | 0.323 | -1.4968 | -1.5142 | -1.5315 | -1.5519 | -1.5795 | 2.4716 | 2.4389 | 2.3716 | 2.3114 | 2.2552 | 2.1287 | 2.0991 | -2.008 | -1.1152 | -1.1376 | -1.1631 | -1.1897 | 2.8705 | 2.8267 | 2.7991 | 2.745 | 2.7032 | 2.6593 | 2.545 | -1.5927 | -1.7642 | -1.9284 | -1.954 | -1.9805 | 2.0858 | 2.044 | 1.996 | 1.9644 | 1.9073 | 1.8552 | 1.8083
|  | KILMELFORD | EE |  |  |  |  | -1.4968 | -1.5142 | -1.5315 | -1.5519 | -1.5795 | 2.4716 | 2.4389 | 2.3716 | 2.3114 | 2.2552 | 2.1287 | 2.1144 | -1.9968 | -1.1152 | -1.1376 | -1.1631 | -1.1897 | 2.8705 | 2.8267 | 2.7991 | 2.745 | 2.7032 | 2.6593 | 2.545 | -1.5927 | -1.6693 | -1.9284 | -1.954 | -1.9805 | 2.0858 | 2.044 | 1.996 | 1.9644 | 1.9073 | 1.8552 | 1.8083
|  | KILMELFORD | HT |  |  |  |  | -1.4866 | -1.5019 | -1.5162 | -1.5315 | -1.5519 | 2.5267 | 2.5032 | 2.4532 | 2.4195 | 2.3675 | 2.1562 | 2.0991 | -2.008 | -1.0958 | -1.1111 | -1.1346 | -1.1519 | 2.9175 | 2.893 | 2.8583 | 2.8154 | 2.7981 | 2.7593 | 2.595 | -1.556 | -1.5662 | -1.906 | -1.9264 | -1.9499 | 2.1297 | 2.0981 | 2.0705 | 2.0318 | 1.9879 | 1.9654 | 1.9205
|  | KILMELFORD | HE |  |  |  |  | -1.4866 | -1.5009 | -1.5142 | -1.5295 | -1.5509 | 2.5307 | 2.5073 | 2.4787 | 2.4511 | 2.4052 | 2.1787 | 2.1185 | -2.0029 | -1.0978 | -1.1131 | -1.1335 | -1.1489 | 2.9226 | 2.9022 | 2.8675 | 2.8256 | 2.8124 | 2.7746 | 2.595 | -1.5652 | -1.6397 | -1.906 | -1.9254 | -1.9458 | 2.1358 | 2.1073 | 2.0838 | 2.0471 | 2.0042 | 1.9838 | 1.944
|  | KILMELFORD | CF |  |  |  |  | -1.4856 | -1.4948 | -1.505 | -1.5213 | -1.5335 | 2.5501 | 2.5318 | 2.5154 | 2.495 | 2.4756 | 2.3409 | 2.196 | -1.9713 | -1.0927 | -1.107 | -1.1203 | -1.1448 | 2.9409 | 2.9175 | 2.8889 | 2.8685 | 2.8358 | 2.8052 | 2.6716 | -1.5927 | -1.7642 | -1.8989 | -1.9152 | -1.9295 | 2.1481 | 2.1358 | 2.1124 | 2.0858 | 2.0644 | 2.0358 | 2.0062
| TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | 0.305 | -0.63061 | -0.68878 | -0.73571 | -0.7898 | -0.85714 | -0.92857 | -0.98878 | -1.0755 | -1.1622 | -1.2418 | -1.4337 | -1.501 | -1.4806 | 0.1 | 0.065306 | 0.032653 | 0 | -0.043878 | -0.093878 | -0.13265 | -0.18776 | -0.24898 | -0.29898 | -0.43776 | -0.49592 | -0.6602 | -0.11327 | -0.16633 | -0.21122 | -0.26224 | -0.32449 | -0.39286 | -0.45204 | -0.53367 | -0.61531 | -0.6898
|  | KILNINVER | EE |  |  |  |  | -0.63061 | -0.68878 | -0.73571 | -0.7898 | -0.85714 | -0.92857 | -0.98878 | -1.0755 | -1.1622 | -1.2418 | -1.4337 | -1.4612 | -1.4806 | 0.1 | 0.065306 | 0.032653 | 0 | -0.043878 | -0.093878 | -0.13265 | -0.18776 | -0.24898 | -0.29898 | -0.43776 | -0.49592 | -0.58265 | -0.11327 | -0.16633 | -0.21122 | -0.26224 | -0.32449 | -0.39286 | -0.45204 | -0.53367 | -0.61531 | -0.6898
|  | KILNINVER | HT |  |  |  |  | -0.61224 | -0.65612 | -0.6949 | -0.73673 | -0.79082 | -0.83776 | -0.9 | -0.97245 | -1.0194 | -1.0908 | -1.3735 | -1.501 | -1.4806 | 0.11531 | 0.090816 | 0.066327 | 0.043878 | 0.011224 | -0.017347 | -0.057143 | -0.10204 | -0.13061 | -0.17653 | -0.36837 | -0.45 | -0.42857 | -0.094898 | -0.13163 | -0.17041 | -0.2102 | -0.25918 | -0.30408 | -0.36327 | -0.43163 | -0.47449 | -0.54388
|  | KILNINVER | HE |  |  |  |  | -0.61429 | -0.6449 | -0.67959 | -0.70816 | -0.74796 | -0.78469 | -0.84082 | -0.90408 | -0.94082 | -1.002 | -1.3122 | -1.3867 | -1.398 | 0.11327 | 0.094898 | 0.071429 | 0.054082 | 0.027551 | 0.0020408 | -0.035714 | -0.077551 | -0.10204 | -0.1449 | -0.3551 | -0.43878 | -0.51633 | -0.096939 | -0.12347 | -0.15612 | -0.18265 | -0.22245 | -0.25612 | -0.30816 | -0.36837 | -0.4051 | -0.46327
|  | KILNINVER | CF |  |  |  |  | -0.60714 | -0.63265 | -0.65918 | -0.69184 | -0.71531 | -0.75102 | -0.77959 | -0.82143 | -0.86327 | -0.90408 | -1.0949 | -1.2888 | -1.3939 | 0.11837 | 0.10612 | 0.085714 | 0.063265 | 0.04898 | 0.022449 | 0.0020408 | -0.028571 | -0.063265 | -0.092857 | -0.24796 | -0.45408 | -0.6602 | -0.088776 | -0.11122 | -0.13469 | -0.16837 | -0.19082 | -0.22347 | -0.25 | -0.29184 | -0.33061 | -0.36939
| BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | NO | 0.566 | 4.251 | 4.199 | 4.1378 | 4.0633 | 4.0112 | 3.9418 | 3.8439 | 3.752 | 3.6316 | 3.5194 | 3.3224 | 3.251 | 3.2296 | 4.9327 | 4.902 | 4.8612 | 4.8112 | 4.7776 | 4.7327 | 4.6673 | 4.6133 | 4.5347 | 4.4653 | 4.3276 | 4.2704 | 4.0347 | 4.6684 | 4.6204 | 4.5622 | 4.4898 | 4.4388 | 4.3724 | 4.2796 | 4.1918 | 4.0765 | 3.9704
|  | KILTARLITY | EE |  |  |  |  | 4.251 | 4.199 | 4.1378 | 4.0633 | 4.0112 | 3.9418 | 3.8439 | 3.752 | 3.6316 | 3.5194 | 3.3224 | 3.2878 | 3.2694 | 4.9327 | 4.902 | 4.8612 | 4.8112 | 4.7776 | 4.7327 | 4.6673 | 4.6133 | 4.5347 | 4.4653 | 4.3276 | 4.2704 | 4.1724 | 4.6684 | 4.6204 | 4.5622 | 4.4898 | 4.4388 | 4.3724 | 4.2796 | 4.1918 | 4.0765 | 3.9704
|  | KILTARLITY | HT |  |  |  |  | 4.2755 | 4.2276 | 4.1816 | 4.1306 | 4.0714 | 3.9867 | 3.9143 | 3.8143 | 3.7418 | 3.6663 | 3.3796 | 3.251 | 3.2296 | 4.9612 | 4.9327 | 4.9071 | 4.8765 | 4.8388 | 4.7847 | 4.748 | 4.6898 | 4.6388 | 4.5857 | 4.3959 | 4.3224 | 4.3102 | 4.702 | 4.6561 | 4.6133 | 4.5653 | 4.5071 | 4.4255 | 4.3633 | 4.2694 | 4.1949 | 4.1173
|  | KILTARLITY | HE |  |  |  |  | 4.2745 | 4.2398 | 4.2051 | 4.1673 | 4.1204 | 4.0643 | 4.0235 | 3.9429 | 3.8571 | 3.7673 | 3.4163 | 3.3296 | 3.3163 | 4.9582 | 4.9357 | 4.9112 | 4.8857 | 4.851 | 4.8133 | 4.7867 | 4.7357 | 4.6796 | 4.6194 | 4.3867 | 4.2969 | 4.2061 | 4.701 | 4.6653 | 4.6296 | 4.5939 | 4.5449 | 4.4908 | 4.452 | 4.3755 | 4.2969 | 4.2122
|  | KILTARLITY | CF |  |  |  |  | 4.2806 | 4.249 | 4.2194 | 4.1837 | 4.1531 | 4.1082 | 4.0602 | 4.0337 | 3.9663 | 3.9112 | 3.6561 | 3.4316 | 3.3286 | 4.9633 | 4.9418 | 4.9245 | 4.8939 | 4.8745 | 4.8439 | 4.8061 | 4.7847 | 4.7408 | 4.7041 | 4.5082 | 4.2704 | 4.0347 | 4.7071 | 4.6776 | 4.648 | 4.6102 | 4.5786 | 4.5337 | 4.4867 | 4.4612 | 4.399 | 4.348
| REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | NO | 6.72 | 1.5797 | 1.0593 | 0.24807 | -0.51928 | -1.2397 | -1.953 | -2.507 | -3.0846 | -3.5672 | -4.0713 | -6.0111 | -7.3785 | -8.2422 | 1.7557 | 1.4537 | 0.9598 | 0.37307 | -0.1953 | -0.76061 | -1.0759 | -1.431 | -1.6218 | -1.8667 | -2.9565 | -3.4971 | -4.2022 | 1.7009 | 1.2866 | 0.58352 | -0.11443 | -0.76954 | -1.4348 | -1.9348 | -2.5093 | -2.8981 | -3.3553
|  | KINCORTH | EE |  |  |  |  | 1.6032 | 1.1226 | 0.48888 | -0.3101 | -1.0223 | -1.7397 | -2.4479 | -3.0846 | -3.3325 | -3.8264 | -5.8581 | -7.2958 | -8.231 | 1.7557 | 1.4537 | 1.0516 | 0.49858 | -0.019792 | -0.56367 | -1.0422 | -1.431 | -1.5667 | -1.8514 | -2.9565 | -3.4971 | -4.2022 | 1.7192 | 1.3141 | 0.75801 | 0.039647 | -0.60729 | -1.2685 | -1.9185 | -2.5093 | -2.7093 | -3.1604
|  | KINCORTH | HT |  |  |  |  | 1.5797 | 1.0593 | 0.24807 | -0.51928 | -1.2397 | -1.953 | -2.507 | -3.054 | -3.5672 | -4.0713 | -6.0111 | -7.3785 | -8.2422 | 1.7731 | 1.4608 | 0.9598 | 0.37307 | -0.1953 | -0.76061 | -1.0759 | -1.3657 | -1.6218 | -1.8667 | -2.6759 | -2.9297 | -3.0348 | 1.7009 | 1.2866 | 0.58352 | -0.11443 | -0.76954 | -1.4348 | -1.9348 | -2.4318 | -2.8981 | -3.3553
|  | KINCORTH | HE |  |  |  |  | 1.645 | 1.3042 | 0.70113 | 0.046024 | -0.51724 | -1.0795 | -1.5672 | -1.9479 | -2.3162 | -2.6815 | -4.2387 | -5.6172 | -6.7626 | 1.8047 | 1.5669 | 1.1792 | 0.68633 | 0.21796 | -0.25244 | -0.63 | -0.89326 | -1.1351 | -1.3718 | -2.2831 | -2.8134 | -3.5767 | 1.7437 | 1.4866 | 0.97128 | 0.38148 | -0.13484 | -0.65525 | -1.1073 | -1.4583 | -1.7971 | -2.1348
|  | KINCORTH | CF |  |  |  |  | 1.7083 | 1.6113 | 1.4164 | 1.0909 | 0.73684 | 0.36337 | 0.022555 | -0.31316 | -0.51214 | -0.76112 | -1.9632 | -3.4499 | -5.231 | 1.8537 | 1.7506 | 1.5843 | 1.3384 | 1.0649 | 0.75368 | 0.47613 | 0.19756 | 0.012861 | -0.20244 | -1.2739 | -2.4379 | -4.1879 | 1.7876 | 1.7009 | 1.5458 | 1.2774 | 0.96312 | 0.62332 | 0.3172 | 0.017198 | -0.16341 | -0.39301
| FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | NO | 0.046 | 0.01591 | 0.011829 | 0.0077469 | -0.0024571 | -0.0075592 | -0.019804 | -0.011641 | -0.017763 | -0.030008 | -0.036131 | -0.046335 | -0.056539 | -0.071661 | 0.026298 | 0.024257 | 0.021196 | 0.012012 | 0.008951 | -0.0012531 | 0.0048694 | 0.00078776 | -0.0094163 | -0.014518 | -0.01758 | -0.020222 | -0.024304 | 0.024676 | 0.021614 | 0.018553 | 0.0093694 | 0.0042673 | -0.0069571 | 0.00018571 | -0.0059367 | -0.017161 | -0.022263
|  | KINGAIRLOCH | EE |  |  |  |  | 0.01591 | 0.011829 | 0.0077469 | -0.0024571 | -0.0075592 | -0.019804 | -0.011641 | -0.015722 | -0.020824 | -0.025927 | -0.040212 | -0.042253 | -0.051253 | 0.026298 | 0.024257 | 0.021196 | 0.012012 | 0.008951 | -0.0012531 | 0.0099714 | 0.0058898 | 0.0028286 | -0.0012531 | -0.011457 | -0.008998 | -0.008998 | 0.024676 | 0.021614 | 0.018553 | 0.0093694 | 0.0042673 | -0.0069571 | 0.0022265 | -0.0018551 | -0.0059367 | -0.011039
|  | KINGAIRLOCH | HT |  |  |  |  | 0.024073 | 0.021012 | 0.011829 | 0.0097878 | 0.0067265 | -0.0055184 | -0.0096 | -0.015722 | -0.025927 | -0.031029 | -0.037151 | -0.045314 | -0.059416 | 0.034461 | 0.03242 | 0.024257 | 0.022216 | 0.020176 | 0.0099714 | 0.0079306 | 0.0028286 | -0.0073755 | -0.010437 | -0.0094163 | -0.011039 | -0.01512 | 0.032839 | 0.029778 | 0.021614 | 0.019573 | 0.017533 | 0.0052878 | 0.0032469 | -0.0018551 | -0.012059 | -0.017161
|  | KINGAIRLOCH | HE |  |  |  |  | 0.024073 | 0.022033 | 0.010808 | 0.0077469 | 0.0046857 | 0.00060408 | -0.011641 | -0.017763 | -0.030008 | -0.036131 | -0.046335 | -0.056539 | -0.071661 | 0.034461 | 0.03242 | 0.023237 | 0.021196 | 0.019155 | 0.016094 | 0.0048694 | 0.00078776 | -0.0094163 | -0.014518 | -0.01758 | -0.020222 | -0.024304 | 0.032839 | 0.029778 | 0.020594 | 0.018553 | 0.016512 | 0.012431 | 0.00018571 | -0.0059367 | -0.017161 | -0.022263
|  | KINGAIRLOCH | CF |  |  |  |  | 0.024073 | 0.023053 | 0.01489 | 0.011829 | 0.0097878 | 0.0077469 | 0.0046857 | -0.0065388 | -0.0085796 | -0.012661 | -0.026947 | -0.043273 | -0.063498 | 0.034461 | 0.033441 | 0.025278 | 0.024257 | 0.022216 | 0.021196 | 0.019155 | 0.008951 | 0.0069102 | 0.0048694 | -0.0032939 | -0.011039 | -0.019202 | 0.032839 | 0.031818 | 0.022635 | 0.021614 | 0.019573 | 0.018553 | 0.016512 | 0.0052878 | 0.0032469 | -0.00083469
| DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 1.8 | 9.7227 | 9.4758 | 9.1472 | 8.7819 | 8.3635 | 7.837 | 7.2574 | 6.6268 | 5.9809 | 5.2186 | 4.087 | 3.9125 | 3.0523 | 10.6472 | 10.5156 | 10.3319 | 10.1533 | 9.9176 | 9.6115 | 9.2135 | 8.7839 | 8.2809 | 7.6482 | 6.9207 | 7.0232 | 6.5171 | 10.2253 | 10.0222 | 9.7304 | 9.4446 | 9.0691 | 8.6283 | 8.1069 | 7.5263 | 6.9365 | 6.2304
|  | KINGSEAT | EE |  |  |  |  | 9.7227 | 9.4758 | 9.1472 | 8.8023 | 8.3635 | 7.8482 | 7.2574 | 6.6574 | 6.0452 | 5.4054 | 4.4043 | 4.0003 | 3.1411 | 10.6472 | 10.5156 | 10.3319 | 10.1533 | 9.9176 | 9.6115 | 9.2135 | 8.7839 | 8.3452 | 7.8584 | 6.9625 | 7.0232 | 6.7089 | 10.2253 | 10.0222 | 9.7304 | 9.4446 | 9.0691 | 8.6375 | 8.1069 | 7.562 | 7.0059 | 6.4161
|  | KINGSEAT | HT |  |  |  |  | 9.7788 | 9.5043 | 9.1645 | 8.7819 | 8.3901 | 7.837 | 7.2737 | 6.6268 | 5.9809 | 5.2186 | 4.087 | 3.9125 | 3.0523 | 10.7043 | 10.5645 | 10.4033 | 10.2125 | 10.0186 | 9.6727 | 9.2717 | 8.786 | 8.2809 | 7.6482 | 6.9207 | 7.2528 | 7.1793 | 10.3008 | 10.0753 | 9.7946 | 9.4691 | 9.1344 | 8.6283 | 8.1181 | 7.5263 | 6.9365 | 6.2304
|  | KINGSEAT | HE |  |  |  |  | 9.7809 | 9.5839 | 9.337 | 9.0248 | 8.6615 | 8.239 | 7.7686 | 7.2839 | 6.8156 | 6.2574 | 5.0207 | 4.5196 | 3.5472 | 10.7003 | 10.586 | 10.4564 | 10.287 | 10.0962 | 9.839 | 9.5043 | 9.1278 | 8.7492 | 8.2737 | 7.1513 | 7.2191 | 6.8579 | 10.3018 | 10.1324 | 9.9283 | 9.6681 | 9.363 | 8.9998 | 8.5793 | 8.1344 | 7.7049 | 7.1855
|  | KINGSEAT | CF |  |  |  |  | 9.8115 | 9.6778 | 9.5094 | 9.3023 | 9.039 | 8.7564 | 8.4574 | 8.1186 | 7.8043 | 7.489 | 6.0594 | 5.1962 | 3.9717 | 10.7176 | 10.637 | 10.538 | 10.4196 | 10.2758 | 10.1135 | 9.9064 | 9.6564 | 9.4207 | 9.1829 | 7.9125 | 7.2946 | 6.5171 | 10.3273 | 10.2089 | 10.063 | 9.8875 | 9.662 | 9.4314 | 9.1712 | 8.8661 | 8.5804 | 8.3161
| BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 1.594 | 1.69 | 1.5084 | 1.2778 | 1.0196 | 0.77163 | 0.47265 | 0.1451 | -0.16 | -0.48041 | -0.74469 | -1.4835 | -1.7498 | -2.1835 | 3.189 | 3.0747 | 2.9318 | 2.7778 | 2.6318 | 2.4502 | 2.2441 | 2.0471 | 1.842 | 1.6686 | 1.139 | 1.0048 | 0.26194 | 2.5109 | 2.3446 | 2.1426 | 1.9119 | 1.7017 | 1.4344 | 1.1405 | 0.87418 | 0.57827 | 0.33847
|  | KINGUSSIE | EE |  |  |  |  | 1.69 | 1.5084 | 1.2778 | 1.0196 | 0.77163 | 0.47265 | 0.1451 | -0.16 | -0.48041 | -0.74469 | -1.4835 | -1.6263 | -2.0529 | 3.189 | 3.0747 | 2.9318 | 2.7778 | 2.6318 | 2.4502 | 2.2441 | 2.0471 | 1.842 | 1.6686 | 1.139 | 1.0987 | 0.78643 | 2.5109 | 2.3446 | 2.1426 | 1.9119 | 1.7017 | 1.4344 | 1.1405 | 0.87418 | 0.57827 | 0.33847
|  | KINGUSSIE | HT |  |  |  |  | 1.7604 | 1.6073 | 1.4084 | 1.2104 | 0.98286 | 0.72265 | 0.4951 | 0.2349 | -0.022245 | -0.26 | -1.2355 | -1.7263 | -2.1386 | 3.241 | 3.1533 | 3.042 | 2.938 | 2.8114 | 2.6645 | 2.5369 | 2.3767 | 2.2206 | 2.0665 | 1.4227 | 1.2936 | 1.2599 | 2.5803 | 2.4477 | 2.2772 | 2.116 | 1.9262 | 1.7007 | 1.515 | 1.2772 | 1.0477 | 0.82622
|  | KINGUSSIE | HE |  |  |  |  | 1.7533 | 1.6227 | 1.4461 | 1.2716 | 1.0665 | 0.8298 | 0.61143 | 0.35429 | 0.10837 | -0.12735 | -1.3222 | -1.7498 | -2.1835 | 3.2359 | 3.1512 | 3.04 | 2.941 | 2.8135 | 2.6706 | 2.54 | 2.3665 | 2.2053 | 2.039 | 1.2186 | 1.0048 | 0.72827 | 2.5701 | 2.4538 | 2.3038 | 2.1609 | 1.9864 | 1.7793 | 1.5926 | 1.3446 | 1.1017 | 0.86092
|  | KINGUSSIE | CF |  |  |  |  | 1.7941 | 1.688 | 1.5553 | 1.4155 | 1.239 | 1.0594 | 0.88592 | 0.73796 | 0.56959 | 0.42061 | -0.38449 | -1.16 | -2.0365 | 3.2584 | 3.1941 | 3.1124 | 3.0288 | 2.9237 | 2.8135 | 2.6971 | 2.5941 | 2.4788 | 2.3645 | 1.7114 | 1.0987 | 0.26194 | 2.6099 | 2.515 | 2.3926 | 2.2721 | 2.1201 | 1.965 | 1.8099 | 1.6823 | 1.5283 | 1.3895
| TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | 0.993 | -0.85448 | -0.89427 | -0.93203 | -0.98203 | -1.0279 | -1.0861 | -1.1524 | -1.2065 | -1.2739 | -1.329 | -1.4779 | -1.53 | -1.5402 | -0.55754 | -0.58101 | -0.60346 | -0.64121 | -0.66876 | -0.70754 | -0.75142 | -0.78713 | -0.83305 | -0.86978 | -0.97182 | -1.0086 | -1.0973 | -1.0137 | -1.03 | -1.0443 | -1.0667 | -1.0861 | -1.1371 | -1.2014 | -1.2514 | -1.3157 | -1.3688
|  | KINLOCH | EE |  |  |  |  | -0.85448 | -0.89427 | -0.93203 | -0.98203 | -1.0279 | -1.0861 | -1.1524 | -1.2065 | -1.2739 | -1.329 | -1.4779 | -1.5024 | -1.5198 | -0.55754 | -0.58101 | -0.60346 | -0.64121 | -0.66876 | -0.70754 | -0.75142 | -0.78713 | -0.83305 | -0.86978 | -0.97182 | -1.0086 | -1.0616 | -1.0137 | -1.03 | -1.0443 | -1.0667 | -1.0861 | -1.1371 | -1.2014 | -1.2514 | -1.3157 | -1.3688
|  | KINLOCH | HT |  |  |  |  | -0.83611 | -0.86876 | -0.9004 | -0.94223 | -0.97284 | -1.0167 | -1.0565 | -1.1157 | -1.1688 | -1.2055 | -1.4269 | -1.53 | -1.5402 | -0.54121 | -0.55958 | -0.57897 | -0.60448 | -0.62284 | -0.65142 | -0.67591 | -0.71468 | -0.74836 | -0.76978 | -0.92182 | -0.98509 | -0.99325 | -1.0045 | -1.0208 | -1.032 | -1.0484 | -1.0637 | -1.081 | -1.1065 | -1.1606 | -1.2126 | -1.2484
|  | KINLOCH | HE |  |  |  |  | -0.83611 | -0.86264 | -0.88713 | -0.91978 | -0.94223 | -0.97693 | -1.0147 | -1.0637 | -1.1126 | -1.1616 | -1.383 | -1.4443 | -1.4514 | -0.54121 | -0.55856 | -0.57387 | -0.59836 | -0.61162 | -0.63713 | -0.65856 | -0.69529 | -0.72693 | -0.76366 | -0.90652 | -0.96774 | -1.0096 | -1.0065 | -1.0198 | -1.031 | -1.0463 | -1.0575 | -1.0759 | -1.0953 | -1.1218 | -1.1606 | -1.2096
|  | KINLOCH | CF |  |  |  |  | -0.83305 | -0.85244 | -0.87693 | -0.89836 | -0.92693 | -0.94427 | -0.97284 | -1.0096 | -1.03 | -1.0637 | -1.2228 | -1.3708 | -1.4524 | -0.53917 | -0.5504 | -0.5657 | -0.58305 | -0.60142 | -0.6157 | -0.63407 | -0.66264 | -0.67795 | -0.70244 | -0.82693 | -0.96978 | -1.0973 | -1.0024 | -1.0096 | -1.0188 | -1.0279 | -1.0402 | -1.0473 | -1.0606 | -1.0769 | -1.0882 | -1.1167
| TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | 0.09 | -0.0091837 | -0.02449 | -0.039796 | -0.054082 | -0.07449 | -0.083673 | -0.11327 | -0.13673 | -0.17143 | -0.19796 | -0.26939 | -0.29286 | -0.29796 | 0.46122 | 0.44898 | 0.43776 | 0.42245 | 0.40306 | 0.39592 | 0.37551 | 0.35918 | 0.33571 | 0.31735 | 0.26531 | 0.24286 | 0.17041 | 0.18571 | 0.16939 | 0.1551 | 0.14082 | 0.11429 | 0.10306 | 0.07449 | 0.05 | 0.016327 | -0.0081633
|  | KINLOCH RANNOCH | EE |  |  |  |  | -0.0091837 | -0.02449 | -0.039796 | -0.054082 | -0.07449 | -0.083673 | -0.11327 | -0.13673 | -0.17143 | -0.19796 | -0.26939 | -0.28469 | -0.29184 | 0.46122 | 0.44898 | 0.43776 | 0.42245 | 0.40306 | 0.39592 | 0.37551 | 0.35918 | 0.33571 | 0.31735 | 0.26531 | 0.24286 | 0.21224 | 0.18571 | 0.16939 | 0.1551 | 0.14082 | 0.11429 | 0.10306 | 0.07449 | 0.05 | 0.016327 | -0.0081633
|  | KINLOCH RANNOCH | HT |  |  |  |  | -0.0040816 | -0.013265 | -0.023469 | -0.031633 | -0.04898 | -0.059184 | -0.082653 | -0.09898 | -0.12143 | -0.14796 | -0.24694 | -0.29286 | -0.29796 | 0.46735 | 0.45816 | 0.45 | 0.44082 | 0.42959 | 0.42041 | 0.40408 | 0.39694 | 0.37959 | 0.36327 | 0.29286 | 0.26429 | 0.25918 | 0.19184 | 0.18265 | 0.17041 | 0.1602 | 0.14082 | 0.12857 | 0.10408 | 0.089796 | 0.067347 | 0.039796
|  | KINLOCH RANNOCH | HE |  |  |  |  | -0.0040816 | -0.012245 | -0.021429 | -0.028571 | -0.042857 | -0.05102 | -0.066327 | -0.07551 | -0.09898 | -0.12041 | -0.23163 | -0.26735 | -0.27347 | 0.46735 | 0.45714 | 0.45102 | 0.44286 | 0.43163 | 0.42245 | 0.4102 | 0.40204 | 0.38469 | 0.36837 | 0.28878 | 0.25204 | 0.22653 | 0.19184 | 0.18265 | 0.17347 | 0.16735 | 0.15306 | 0.14082 | 0.12245 | 0.1102 | 0.086735 | 0.066327
|  | KINLOCH RANNOCH | CF |  |  |  |  | -0.0091837 | -0.0071429 | -0.013265 | -0.020408 | -0.027551 | -0.038776 | -0.042857 | -0.058163 | -0.072449 | -0.076531 | -0.15306 | -0.23163 | -0.27857 | 0.46327 | 0.46429 | 0.45714 | 0.44796 | 0.44082 | 0.43265 | 0.42551 | 0.41224 | 0.39796 | 0.39694 | 0.33265 | 0.24898 | 0.17041 | 0.19286 | 0.18878 | 0.18163 | 0.17449 | 0.16531 | 0.15408 | 0.14694 | 0.12959 | 0.11429 | 0.11122
| GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | NO | 0.18 | 0.71531 | 0.69592 | 0.67653 | 0.64388 | 0.62653 | 0.59796 | 0.57041 | 0.52755 | 0.4898 | 0.4551 | 0.40816 | 0.3898 | 0.38265 | 0.80612 | 0.7949 | 0.78061 | 0.75918 | 0.74694 | 0.72347 | 0.70714 | 0.67755 | 0.64694 | 0.62449 | 0.58776 | 0.56327 | 0.48061 | 0.7398 | 0.72347 | 0.70408 | 0.67347 | 0.65918 | 0.62857 | 0.60612 | 0.56429 | 0.52449 | 0.49388
|  | KINLOCHEWE | EE |  |  |  |  | 0.71531 | 0.69592 | 0.67653 | 0.64388 | 0.62653 | 0.59796 | 0.57041 | 0.52755 | 0.4898 | 0.4551 | 0.40816 | 0.39694 | 0.3898 | 0.80612 | 0.7949 | 0.78061 | 0.75918 | 0.74694 | 0.72347 | 0.70714 | 0.67755 | 0.64694 | 0.62449 | 0.58776 | 0.56327 | 0.52755 | 0.7398 | 0.72347 | 0.70408 | 0.67347 | 0.65918 | 0.62857 | 0.60612 | 0.56429 | 0.52449 | 0.49388
|  | KINLOCHEWE | HT |  |  |  |  | 0.72653 | 0.71224 | 0.69592 | 0.67551 | 0.65918 | 0.63469 | 0.62041 | 0.58878 | 0.55714 | 0.53878 | 0.43571 | 0.3898 | 0.38265 | 0.81939 | 0.8102 | 0.79898 | 0.78367 | 0.77245 | 0.75612 | 0.74796 | 0.72653 | 0.70408 | 0.69286 | 0.62143 | 0.59184 | 0.58776 | 0.75306 | 0.74082 | 0.72347 | 0.7051 | 0.68776 | 0.66429 | 0.65204 | 0.62245 | 0.5898 | 0.57653
|  | KINLOCHEWE | HE |  |  |  |  | 0.72653 | 0.71633 | 0.70204 | 0.68673 | 0.67143 | 0.64796 | 0.63878 | 0.61122 | 0.57959 | 0.56837 | 0.45408 | 0.42245 | 0.41735 | 0.81735 | 0.80816 | 0.79898 | 0.78878 | 0.77755 | 0.7602 | 0.75306 | 0.73571 | 0.71122 | 0.70204 | 0.61837 | 0.58163 | 0.54796 | 0.75306 | 0.74388 | 0.72959 | 0.71327 | 0.69898 | 0.67857 | 0.66837 | 0.64184 | 0.61429 | 0.60102
|  | KINLOCHEWE | CF |  |  |  |  | 0.73061 | 0.71837 | 0.7102 | 0.69796 | 0.67857 | 0.67041 | 0.65 | 0.64286 | 0.62245 | 0.60306 | 0.51429 | 0.45204 | 0.41837 | 0.82041 | 0.81122 | 0.8051 | 0.79796 | 0.78265 | 0.77755 | 0.75918 | 0.75408 | 0.7398 | 0.72551 | 0.64694 | 0.57143 | 0.48061 | 0.75816 | 0.74694 | 0.73776 | 0.72653 | 0.70714 | 0.69898 | 0.67653 | 0.67143 | 0.6551 | 0.63673
| KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 0.07 | 2.0837 | 2.0398 | 1.9847 | 1.9388 | 1.8806 | 1.8398 | 1.7735 | 1.6806 | 1.5847 | 1.4969 | 1.3918 | 1.3418 | 1.3265 | 2.5347 | 2.5051 | 2.4684 | 2.4347 | 2.3918 | 2.3653 | 2.3184 | 2.2592 | 2.1949 | 2.1367 | 2.0592 | 2.0041 | 1.8337 | 2.3643 | 2.3235 | 2.2714 | 2.2265 | 2.1714 | 2.1337 | 2.0684 | 1.9816 | 1.8939 | 1.8112
|  | KINLOCHLEVEN | EE |  |  |  |  | 2.0837 | 2.0398 | 1.9847 | 1.9388 | 1.8806 | 1.8398 | 1.7735 | 1.6806 | 1.5847 | 1.4969 | 1.3918 | 1.3694 | 1.3571 | 2.5347 | 2.5051 | 2.4684 | 2.4347 | 2.3918 | 2.3653 | 2.3184 | 2.2592 | 2.1949 | 2.1367 | 2.0592 | 2.0041 | 1.9194 | 2.3643 | 2.3235 | 2.2714 | 2.2265 | 2.1714 | 2.1337 | 2.0684 | 1.9816 | 1.8939 | 1.8112
|  | KINLOCHLEVEN | HT |  |  |  |  | 2.1071 | 2.0582 | 2.0153 | 1.9837 | 1.9388 | 1.8776 | 1.8031 | 1.7408 | 1.6867 | 1.6388 | 1.4316 | 1.3418 | 1.3265 | 2.5531 | 2.5224 | 2.4939 | 2.4714 | 2.4418 | 2.4061 | 2.3643 | 2.3286 | 2.2929 | 2.2612 | 2.1194 | 2.0602 | 2.051 | 2.3878 | 2.3418 | 2.302 | 2.2704 | 2.2296 | 2.1745 | 2.1051 | 2.051 | 2.001 | 1.9541
|  | KINLOCHLEVEN | HE |  |  |  |  | 2.1071 | 2.0694 | 2.0327 | 2.0061 | 1.9704 | 1.9418 | 1.8969 | 1.849 | 1.7878 | 1.7245 | 1.4847 | 1.4316 | 1.4245 | 2.5531 | 2.5255 | 2.501 | 2.4827 | 2.4531 | 2.4337 | 2.4 | 2.3724 | 2.3337 | 2.2898 | 2.1214 | 2.049 | 1.9704 | 2.3878 | 2.35 | 2.3173 | 2.2939 | 2.2571 | 2.2306 | 2.1857 | 2.1439 | 2.0878 | 2.0296
|  | KINLOCHLEVEN | CF |  |  |  |  | 2.1092 | 2.0867 | 2.0592 | 2.0296 | 2.0143 | 1.9816 | 1.9582 | 1.9224 | 1.8765 | 1.85 | 1.6296 | 1.5092 | 1.4408 | 2.5561 | 2.5398 | 2.5204 | 2.498 | 2.4857 | 2.4633 | 2.4449 | 2.4163 | 2.3806 | 2.3643 | 2.1867 | 2.0255 | 1.8337 | 2.3888 | 2.3684 | 2.3439 | 2.3133 | 2.299 | 2.2684 | 2.2459 | 2.2092 | 2.1653 | 2.1449
| FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | NO | 0 | 0.93776 | 0.93571 | 0.92857 | 0.92755 | 0.91939 | 0.91735 | 0.91735 | 0.91735 | 0.91531 | 0.91327 | 0.9102 | 0.90918 | 0.90918 | 0.95204 | 0.95102 | 0.9449 | 0.94286 | 0.93571 | 0.94082 | 0.93571 | 0.93571 | 0.93571 | 0.94082 | 0.93673 | 0.93571 | 0.93469 | 0.94796 | 0.94694 | 0.9398 | 0.93776 | 0.93061 | 0.92959 | 0.92959 | 0.92959 | 0.92857 | 0.92755
|  | KINLOCHMOIDART | EE |  |  |  |  | 0.93776 | 0.93673 | 0.92857 | 0.92755 | 0.91939 | 0.91735 | 0.92347 | 0.91735 | 0.91531 | 0.91327 | 0.9102 | 0.90918 | 0.91122 | 0.95204 | 0.95204 | 0.9449 | 0.94286 | 0.93571 | 0.94082 | 0.94592 | 0.94184 | 0.94286 | 0.94082 | 0.93673 | 0.93673 | 0.93571 | 0.94796 | 0.94796 | 0.9398 | 0.93776 | 0.93061 | 0.92959 | 0.93571 | 0.93061 | 0.92959 | 0.92755
|  | KINLOCHMOIDART | HT |  |  |  |  | 0.9449 | 0.93571 | 0.93673 | 0.93571 | 0.92755 | 0.92653 | 0.91735 | 0.91735 | 0.91633 | 0.92143 | 0.9102 | 0.90918 | 0.90918 | 0.95918 | 0.95102 | 0.95204 | 0.95102 | 0.94286 | 0.94286 | 0.93571 | 0.94082 | 0.9398 | 0.9449 | 0.93673 | 0.93571 | 0.93571 | 0.9551 | 0.94694 | 0.94796 | 0.94694 | 0.93776 | 0.93776 | 0.92959 | 0.92959 | 0.92857 | 0.93469
|  | KINLOCHMOIDART | HE |  |  |  |  | 0.9449 | 0.93571 | 0.93673 | 0.93673 | 0.92959 | 0.92755 | 0.91939 | 0.91837 | 0.91735 | 0.92245 | 0.91122 | 0.91327 | 0.91224 | 0.95918 | 0.95102 | 0.95204 | 0.95204 | 0.9449 | 0.94286 | 0.93571 | 0.94082 | 0.94082 | 0.94592 | 0.93776 | 0.9398 | 0.93673 | 0.9551 | 0.94694 | 0.94796 | 0.94796 | 0.94082 | 0.93776 | 0.93061 | 0.93061 | 0.92959 | 0.93469
|  | KINLOCHMOIDART | CF |  |  |  |  | 0.9449 | 0.93776 | 0.93571 | 0.93571 | 0.93571 | 0.92857 | 0.92653 | 0.91837 | 0.91837 | 0.91837 | 0.91939 | 0.91327 | 0.91327 | 0.95918 | 0.95204 | 0.95102 | 0.95102 | 0.95102 | 0.94388 | 0.94286 | 0.93571 | 0.93571 | 0.94082 | 0.94286 | 0.93673 | 0.93469 | 0.9551 | 0.94796 | 0.94694 | 0.94694 | 0.94694 | 0.9398 | 0.93776 | 0.93061 | 0.93061 | 0.93061
| ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 0.09 | 11.1724 | 11.0122 | 10.7898 | 10.5439 | 10.2704 | 9.9806 | 9.6316 | 9.2092 | 8.8429 | 8.5122 | 6.7153 | 5.8704 | 4.9898 | 12.4724 | 12.3367 | 12.1827 | 12.0102 | 11.8214 | 11.6143 | 11.3602 | 11.048 | 10.7786 | 10.5408 | 9.1673 | 8.927 | 8.8301 | 12.3617 | 12.1964 | 11.9852 | 11.7474 | 11.4862 | 11.2097 | 10.875 | 10.4699 | 10.1199 | 9.8046
|  | KINLOSS | EE |  |  |  |  | 11.1724 | 11.0122 | 10.7898 | 10.5439 | 10.2704 | 9.9806 | 9.6316 | 9.2092 | 8.8429 | 8.5122 | 7.401 | 7.1704 | 6.3582 | 12.4724 | 12.3367 | 12.1827 | 12.0102 | 11.8214 | 11.6143 | 11.3602 | 11.048 | 10.7786 | 10.5408 | 9.7408 | 9.9689 | 9.9179 | 12.3617 | 12.1964 | 11.9852 | 11.7474 | 11.4862 | 11.2097 | 10.875 | 10.4699 | 10.1199 | 9.8046
|  | KINLOSS | HT |  |  |  |  | 11.25 | 11.1429 | 11.0235 | 10.8571 | 10.6714 | 10.448 | 10.1806 | 9.8796 | 9.5786 | 9.2684 | 7.8827 | 7.2337 | 6.3735 | 12.5602 | 12.4633 | 12.3571 | 12.2347 | 12.1071 | 11.952 | 11.7714 | 11.5622 | 11.3551 | 11.1398 | 10.1194 | 10.0291 | 9.9566 | 12.4719 | 12.3566 | 12.224 | 12.0546 | 11.877 | 11.6689 | 11.4158 | 11.1301 | 10.8454 | 10.5495
|  | KINLOSS | HE |  |  |  |  | 11.2367 | 11.1306 | 10.952 | 10.7469 | 10.5122 | 10.2347 | 9.9031 | 9.5031 | 9.1102 | 8.6939 | 6.7153 | 5.8704 | 4.9898 | 12.5357 | 12.4204 | 12.2969 | 12.1531 | 11.9929 | 11.7878 | 11.5418 | 11.2439 | 10.9469 | 10.6378 | 9.1673 | 8.927 | 8.8301 | 12.4403 | 12.2985 | 12.1403 | 11.9413 | 11.7168 | 11.4495 | 11.1321 | 10.7474 | 10.3709 | 9.9719
|  | KINLOSS | CF |  |  |  |  | 11.2714 | 11.2082 | 11.1357 | 11.0367 | 10.8949 | 10.7378 | 10.5633 | 10.3306 | 10.1163 | 9.8969 | 8.4602 | 7.1163 | 5.4306 | 12.5796 | 12.5133 | 12.4367 | 12.349 | 12.2531 | 12.1439 | 12.0224 | 11.8541 | 11.6898 | 11.5265 | 10.4398 | 9.8138 | 9.1199 | 12.4934 | 12.4158 | 12.3219 | 12.2128 | 12.0872 | 11.9332 | 11.7658 | 11.5423 | 11.3362 | 11.126
| BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 0.422 | 3.3192 | 3.1886 | 3.0273 | 2.8794 | 2.6927 | 2.4937 | 2.3018 | 2.0365 | 1.7855 | 1.56 | 0.94265 | 0.55184 | -0.074694 | 4.6294 | 4.5845 | 4.5273 | 4.4763 | 4.409 | 4.3365 | 4.2743 | 4.109 | 3.9365 | 3.7937 | 3.4008 | 3.3753 | 2.8386 | 4.3182 | 4.2018 | 4.0569 | 3.9284 | 3.758 | 3.5773 | 3.411 | 3.1702 | 2.9386 | 2.7396
|  | KIPPEN | EE |  |  |  |  | 3.3192 | 3.1886 | 3.0273 | 2.8794 | 2.6927 | 2.4937 | 2.3018 | 2.0365 | 1.7855 | 1.56 | 0.94265 | 0.70898 | 0.12633 | 4.6294 | 4.5845 | 4.5273 | 4.4763 | 4.409 | 4.3365 | 4.2743 | 4.109 | 3.9365 | 3.7937 | 3.4008 | 3.3967 | 3.1161 | 4.3182 | 4.2018 | 4.0569 | 3.9284 | 3.758 | 3.5773 | 3.411 | 3.1702 | 2.9386 | 2.7396
|  | KIPPEN | HT |  |  |  |  | 3.3753 | 3.2559 | 3.1314 | 2.9784 | 2.8233 | 2.6478 | 2.4967 | 2.2845 | 2.0804 | 1.912 | 1.0192 | 0.55184 | -0.074694 | 4.6539 | 4.6182 | 4.5763 | 4.5263 | 4.4763 | 4.4161 | 4.3651 | 4.2906 | 4.2039 | 4.111 | 3.5273 | 3.4539 | 3.3192 | 4.3712 | 4.2661 | 4.1539 | 4.0202 | 3.8865 | 3.7335 | 3.6039 | 3.4182 | 3.2345 | 3.0927
|  | KIPPEN | HE |  |  |  |  | 3.3753 | 3.2794 | 3.1794 | 3.0529 | 2.9233 | 2.7794 | 2.6498 | 2.4569 | 2.2692 | 2.1233 | 1.1069 | 0.73959 | 0.16204 | 4.6498 | 4.611 | 4.5702 | 4.5222 | 4.4722 | 4.411 | 4.3569 | 4.2794 | 4.1998 | 4.0794 | 3.4406 | 3.3753 | 3.1345 | 4.3682 | 4.2835 | 4.1957 | 4.0855 | 3.9753 | 3.8478 | 3.7335 | 3.558 | 3.3865 | 3.2314
|  | KIPPEN | CF |  |  |  |  | 3.3814 | 3.3029 | 3.212 | 3.1243 | 3.0161 | 2.8998 | 2.7753 | 2.6733 | 2.5427 | 2.4069 | 1.7253 | 1.0702 | 0.28245 | 4.6539 | 4.6202 | 4.5845 | 4.5478 | 4.5039 | 4.4549 | 4.4059 | 4.3539 | 4.2967 | 4.2365 | 3.8008 | 3.4018 | 2.8386 | 4.3753 | 4.3029 | 4.2263 | 4.1498 | 4.0559 | 3.9539 | 3.8406 | 3.7478 | 3.6284 | 3.5049
| THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | NO | 2.953 | 4.8205 | 4.045 | 2.7521 | 1.2174 | -0.1142 | -2.4836 | -3.4173 | -4.4775 | -5.4264 | -7.0826 | -14.8969 | -20.555 | -26.9877 | 9.2756 | 8.5766 | 7.2654 | 5.646 | 4.3531 | 1.7154 | 0.91131 | 0.0092653 | -1.0275 | -2.853 | -10.755 | -16.8918 | -23.3142 | 7.3603 | 6.5899 | 5.2174 | 3.5654 | 2.2633 | -0.41727 | -1.3295 | -2.3632 | -3.404 | -5.3703
|  | KIRKWALL | EE |  |  |  |  | 4.9695 | 4.1827 | 3.3531 | 2.4419 | 0.88682 | -0.85196 | -1.8173 | -2.706 | -4.053 | -5.2275 | -10.552 | -15.504 | -18.8122 | 9.5154 | 8.7868 | 8.0419 | 7.2154 | 5.646 | 3.8184 | 2.8746 | 2.1521 | 0.87049 | -0.17135 | -4.9887 | -10.4479 | -13.5142 | 7.5358 | 6.7317 | 5.9287 | 5.047 | 3.4358 | 1.5552 | 0.5562 | -0.29176 | -1.703 | -2.8816
|  | KIRKWALL | HT |  |  |  |  | 4.8205 | 4.045 | 2.7521 | 1.2174 | -0.1142 | -2.4836 | -3.4173 | -4.4775 | -5.4264 | -6.7611 | -11.3122 | -17.5071 | -23.5867 | 9.2756 | 8.5766 | 7.2654 | 5.646 | 4.3531 | 1.7154 | 0.91131 | 0.0092653 | -0.75706 | -1.8081 | -6.1795 | -12.7969 | -18.8969 | 7.3603 | 6.5899 | 5.2174 | 3.5654 | 2.2633 | -0.41727 | -1.3295 | -2.3632 | -3.254 | -4.4642
|  | KIRKWALL | HE |  |  |  |  | 5.0991 | 4.3511 | 3.2725 | 1.9042 | 0.60008 | -1.705 | -2.8428 | -4.0989 | -5.2683 | -7.0826 | -14.8969 | -20.555 | -26.9877 | 9.5756 | 8.8827 | 7.7817 | 6.3276 | 5.0052 | 2.4154 | 1.2776 | 0.093959 | -1.0275 | -2.853 | -10.755 | -16.8918 | -23.3142 | 7.6348 | 6.8899 | 5.7429 | 4.2644 | 2.9338 | 0.31845 | -0.88155 | -2.1856 | -3.404 | -5.3703
|  | KIRKWALL | CF |  |  |  |  | 5.8317 | 5.3358 | 4.8072 | 4.3266 | 3.4654 | 2.4276 | 1.6501 | 0.93273 | 0.18273 | -0.71727 | -5.6775 | -9.554 | -12.5111 | 10.3684 | 9.9031 | 9.4205 | 8.9838 | 8.0899 | 6.9593 | 6.1695 | 5.4664 | 4.7562 | 3.9031 | -0.58053 | -3.955 | -6.9571 | 8.3419 | 7.8664 | 7.3674 | 6.9103 | 6.0154 | 4.895 | 4.095 | 3.3491 | 2.594 | 1.6848
| BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 0.689 | -0.16216 | -0.16727 | -0.17543 | -0.18767 | -0.20196 | -0.21216 | -0.23155 | -0.24073 | -0.25808 | -0.27135 | -0.30604 | -0.31727 | -0.31829 | -0.28767 | -0.27441 | -0.27747 | -0.28155 | -0.28665 | -0.28869 | -0.29482 | -0.29992 | -0.30502 | -0.31012 | -0.32135 | -0.32951 | -0.33563 | -0.11318 | -0.11931 | -0.12441 | -0.13869 | -0.154 | -0.16216 | -0.18155 | -0.18869 | -0.20604 | -0.22135
|  | KISHORNHILL | EE |  |  |  |  | -0.1591 | -0.16727 | -0.17543 | -0.18767 | -0.20196 | -0.21216 | -0.23155 | -0.24073 | -0.25808 | -0.27135 | -0.30604 | -0.31114 | -0.3142 | -0.27135 | -0.27441 | -0.27747 | -0.28155 | -0.28665 | -0.28869 | -0.29482 | -0.29992 | -0.30502 | -0.31012 | -0.32033 | -0.32339 | -0.32747 | -0.11012 | -0.11931 | -0.12441 | -0.13869 | -0.154 | -0.16216 | -0.18155 | -0.18869 | -0.20604 | -0.22135
|  | KISHORNHILL | HT |  |  |  |  | -0.16216 | -0.16012 | -0.16931 | -0.17645 | -0.18461 | -0.19584 | -0.21012 | -0.21829 | -0.23359 | -0.24788 | -0.2938 | -0.31727 | -0.31829 | -0.28767 | -0.27135 | -0.27339 | -0.27645 | -0.28053 | -0.28359 | -0.28665 | -0.29073 | -0.29584 | -0.2989 | -0.31727 | -0.32237 | -0.32543 | -0.11318 | -0.11114 | -0.11931 | -0.12645 | -0.13461 | -0.14584 | -0.15808 | -0.16727 | -0.18155 | -0.19788
|  | KISHORNHILL | HE |  |  |  |  | -0.16216 | -0.1591 | -0.16624 | -0.17339 | -0.18155 | -0.18767 | -0.1989 | -0.2091 | -0.22237 | -0.23665 | -0.28971 | -0.30502 | -0.3091 | -0.28767 | -0.27135 | -0.27339 | -0.27747 | -0.27951 | -0.28359 | -0.28665 | -0.29176 | -0.29686 | -0.30094 | -0.32135 | -0.32951 | -0.33563 | -0.11318 | -0.11012 | -0.11727 | -0.12339 | -0.13053 | -0.13767 | -0.14992 | -0.1591 | -0.17237 | -0.18665
|  | KISHORNHILL | CF |  |  |  |  | -0.154 | -0.16318 | -0.1642 | -0.16931 | -0.17543 | -0.17951 | -0.18767 | -0.19686 | -0.20196 | -0.2091 | -0.24788 | -0.28767 | -0.30502 | -0.28053 | -0.27237 | -0.27237 | -0.27441 | -0.27543 | -0.27951 | -0.28155 | -0.28461 | -0.28665 | -0.28869 | -0.30604 | -0.32441 | -0.33461 | -0.10502 | -0.1142 | -0.11522 | -0.12135 | -0.12441 | -0.12951 | -0.13869 | -0.14788 | -0.14992 | -0.1591
| BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 0.088 | 6.3971 | 6.3512 | 6.2941 | 6.2257 | 6.1747 | 6.0951 | 6.0114 | 5.8798 | 5.7553 | 5.6829 | 5.4757 | 5.3971 | 5.3696 | 6.589 | 6.5563 | 6.5176 | 6.4676 | 6.4359 | 6.3798 | 6.3227 | 6.2349 | 6.1522 | 6.1104 | 5.9431 | 5.8594 | 5.5727 | 6.2604 | 6.2165 | 6.1645 | 6.0982 | 6.0522 | 5.9798 | 5.9002 | 5.7788 | 5.6665 | 5.6053
|  | KYLE | EE |  |  |  |  | 6.3971 | 6.3512 | 6.2941 | 6.2257 | 6.1747 | 6.0951 | 6.0114 | 5.8798 | 5.7553 | 5.6829 | 5.4757 | 5.4369 | 5.4043 | 6.589 | 6.5563 | 6.5176 | 6.4676 | 6.4359 | 6.3798 | 6.3227 | 6.2349 | 6.1522 | 6.1104 | 5.9431 | 5.8594 | 5.7216 | 6.2604 | 6.2165 | 6.1645 | 6.0982 | 6.0522 | 5.9798 | 5.9002 | 5.7788 | 5.6665 | 5.6053
|  | KYLE | HT |  |  |  |  | 6.4278 | 6.388 | 6.3349 | 6.291 | 6.242 | 6.1563 | 6.0614 | 5.9778 | 5.9033 | 5.8318 | 5.538 | 5.3971 | 5.3696 | 6.6114 | 6.5859 | 6.5522 | 6.5298 | 6.4971 | 6.4441 | 6.389 | 6.341 | 6.292 | 6.2431 | 6.04 | 5.9482 | 5.9298 | 6.289 | 6.2492 | 6.2022 | 6.1604 | 6.1176 | 6.041 | 5.9563 | 5.8829 | 5.8155 | 5.7492
|  | KYLE | HE |  |  |  |  | 6.4257 | 6.3971 | 6.3502 | 6.3206 | 6.2829 | 6.2329 | 6.1706 | 6.1053 | 6.0247 | 5.9492 | 5.6033 | 5.5186 | 5.489 | 6.6094 | 6.5869 | 6.5563 | 6.5359 | 6.5094 | 6.4737 | 6.4278 | 6.3869 | 6.3339 | 6.2808 | 6.0329 | 5.9186 | 5.7982 | 6.2869 | 6.2573 | 6.2155 | 6.188 | 6.1533 | 6.1063 | 6.0482 | 5.992 | 5.9196 | 5.8512
|  | KYLE | CF |  |  |  |  | 6.4349 | 6.4012 | 6.3727 | 6.3471 | 6.3084 | 6.2778 | 6.2359 | 6.1859 | 6.1522 | 6.0931 | 5.8084 | 5.6257 | 5.5022 | 6.6165 | 6.5941 | 6.5757 | 6.5584 | 6.5298 | 6.5053 | 6.4737 | 6.4339 | 6.4033 | 6.3635 | 6.1206 | 5.8778 | 5.5727 | 6.2951 | 6.2665 | 6.24 | 6.2155 | 6.1798 | 6.1522 | 6.1124 | 6.0665 | 6.0349 | 5.9808
| LAIRG | LAIRG | MINIMUM HEADROOM | NC 58798 07111 | YES | NO | 0.141 | -0.31122 | -0.37245 | 1.8092 | 1.7224 | 1.6622 | 1.5806 | 1.4684 | 1.3061 | 1.1929 | 1.051 | 0.77755 | 0.67857 | -1.6082 | 0.20204 | 2.4153 | 2.3714 | 2.3153 | 2.2776 | 2.2224 | 2.151 | 2.049 | 1.9857 | 1.9041 | 1.7204 | -0.6 | -0.77857 | 2.2347 | 2.1755 | 2.1112 | 2.0327 | 1.9704 | 1.8929 | 1.7888 | 1.6357 | 1.5306 | 1.3969
|  | LAIRG | EE |  |  |  |  | -0.31122 | -0.37245 | 1.8092 | 1.7224 | 1.6622 | 1.5806 | 1.4684 | 1.3061 | 1.1929 | 1.051 | 0.77755 | 0.71633 | -1.55 | 0.20204 | 2.4153 | 2.3714 | 2.3153 | 2.2776 | 2.2224 | 2.151 | 2.049 | 1.9857 | 1.9041 | 1.7204 | -0.6 | -0.68571 | 2.2347 | 2.1755 | 2.1112 | 2.0327 | 1.9704 | 1.8929 | 1.7888 | 1.6357 | 1.5306 | 1.3969
|  | LAIRG | HT |  |  |  |  | -0.29898 | -0.34796 | 1.8429 | 1.7765 | 1.7163 | 1.6 | 1.4918 | 1.3551 | 1.2714 | 1.1827 | 0.84898 | 0.67857 | -1.6082 | 0.22449 | 2.4439 | 2.4122 | 2.3714 | 2.3367 | 2.2735 | 2.2245 | 2.1408 | 2.0898 | 2.0286 | 1.798 | -0.54694 | -0.56837 | 2.249 | 2.1959 | 2.1429 | 2.0827 | 2.0255 | 1.9214 | 1.8276 | 1.7041 | 1.6224 | 1.5357
|  | LAIRG | HE |  |  |  |  | -0.29184 | -0.32959 | 1.8776 | 1.8255 | 1.7806 | 1.7194 | 1.6663 | 1.5561 | 1.4561 | 1.3449 | 0.88163 | 0.77653 | -1.4857 | 0.23061 | 2.449 | 2.4235 | 2.3847 | 2.3551 | 2.3092 | 2.2827 | 2.2112 | 2.151 | 2.0816 | 1.799 | -0.54694 | -0.62551 | 2.2561 | 2.2153 | 2.1735 | 2.1235 | 2.0806 | 2.0214 | 1.9694 | 1.8663 | 1.7724 | 1.6714
|  | LAIRG | CF |  |  |  |  | -0.2551 | -0.29082 | 1.9122 | 1.8776 | 1.8276 | 1.7878 | 1.7337 | 1.698 | 1.6204 | 1.5398 | 1.2143 | 0.94796 | -1.4724 | 0.25306 | 2.4776 | 2.4449 | 2.4235 | 2.3878 | 2.3622 | 2.3235 | 2.2969 | 2.248 | 2.1929 | 1.9643 | -0.5449 | -0.77857 | 2.2847 | 2.25 | 2.2071 | 2.1735 | 2.1306 | 2.0929 | 2.0459 | 2.0082 | 1.9378 | 1.8633
| MYBSTER 1 | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | NO | 0.068 | 1.0827 | 0.9898 | 0.89898 | 0.79592 | 0.69082 | 0.57755 | 0.46327 | 0.29184 | 0.13469 | -0.023469 | -0.3398 | -0.44898 | -0.4898 | 1.75 | 1.698 | 1.648 | 1.5755 | 1.5051 | 1.4235 | 1.3602 | 1.2408 | 1.1337 | 1.0367 | 0.87347 | 0.79082 | 0.47857 | 1.4 | 1.3133 | 1.2286 | 1.1224 | 1.0153 | 0.8949 | 0.7898 | 0.61633 | 0.45306 | 0.30306
|  | LATHERON | EE |  |  |  |  | 1.0827 | 0.9898 | 0.89898 | 0.79592 | 0.69082 | 0.57755 | 0.46327 | 0.29184 | 0.13469 | -0.023469 | -0.3398 | -0.4 | -0.41837 | 1.75 | 1.698 | 1.648 | 1.5755 | 1.5051 | 1.4235 | 1.3602 | 1.2408 | 1.1337 | 1.0367 | 0.87347 | 0.79082 | 0.64592 | 1.4 | 1.3133 | 1.2286 | 1.1224 | 1.0153 | 0.8949 | 0.7898 | 0.61633 | 0.45306 | 0.30306
|  | LATHERON | HT |  |  |  |  | 1.1092 | 1.0255 | 0.93469 | 0.85102 | 0.76837 | 0.65306 | 0.53265 | 0.3949 | 0.30102 | 0.18673 | -0.23469 | -0.44898 | -0.4898 | 1.7776 | 1.7367 | 1.6908 | 1.651 | 1.6112 | 1.5449 | 1.4765 | 1.3867 | 1.3418 | 1.2673 | 0.98469 | 0.87143 | 0.85306 | 1.4439 | 1.3704 | 1.2847 | 1.2082 | 1.1398 | 1.0306 | 0.91939 | 0.78265 | 0.70408 | 0.58878
|  | LATHERON | HE |  |  |  |  | 1.1092 | 1.051 | 0.98367 | 0.92143 | 0.86531 | 0.79388 | 0.70306 | 0.58061 | 0.46327 | 0.36837 | -0.23163 | -0.3398 | -0.35918 | 1.7776 | 1.7449 | 1.7061 | 1.6673 | 1.6357 | 1.5847 | 1.5296 | 1.448 | 1.3684 | 1.3204 | 0.93265 | 0.84898 | 0.70918 | 1.4439 | 1.3908 | 1.3194 | 1.2602 | 1.2102 | 1.1347 | 1.049 | 0.92653 | 0.80918 | 0.73163
|  | LATHERON | CF |  |  |  |  | 1.1133 | 1.0592 | 1.0102 | 0.95714 | 0.89796 | 0.84898 | 0.78469 | 0.71837 | 0.63673 | 0.55102 | 0.20816 | -0.076531 | -0.29592 | 1.7816 | 1.75 | 1.7214 | 1.6949 | 1.6531 | 1.6286 | 1.5827 | 1.5316 | 1.4755 | 1.4112 | 1.1367 | 0.83776 | 0.47857 | 1.4469 | 1.3929 | 1.349 | 1.301 | 1.2367 | 1.1959 | 1.1306 | 1.0643 | 0.98061 | 0.89592
| FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | NO | 2.738 | 7.5917 | 7.355 | 7.0376 | 6.655 | 6.2305 | 5.608 | 4.855 | 4.0172 | 3.058 | 1.905 | 0.058037 | -0.59196 | -1.4828 | 8.8764 | 8.7376 | 8.5397 | 8.2948 | 8.0203 | 7.5958 | 7.0662 | 6.4591 | 5.758 | 4.9091 | 3.7223 | 3.7034 | 3.1228 | 8.1892 | 7.9565 | 7.6647 | 7.3045 | 6.9024 | 6.4126 | 5.7392 | 4.9861 | 4.1218 | 3.0943
|  | LAURENCEKIRK | EE |  |  |  |  | 7.5917 | 7.355 | 7.0376 | 6.655 | 6.2305 | 5.7111 | 4.956 | 4.1774 | 3.3601 | 2.754 | 0.058037 | -0.50013 | -1.3746 | 8.8764 | 8.7376 | 8.5397 | 8.2948 | 8.0203 | 7.657 | 7.1295 | 6.5733 | 5.9805 | 5.5111 | 3.7223 | 3.7034 | 3.3361 | 8.1892 | 7.9565 | 7.6647 | 7.3045 | 6.9024 | 6.4126 | 5.7473 | 5.0443 | 4.3188 | 3.8371
|  | LAURENCEKIRK | HT |  |  |  |  | 7.6417 | 7.3907 | 7.0856 | 6.7131 | 6.3019 | 5.608 | 4.855 | 4.0172 | 3.058 | 1.905 | 0.10293 | -0.59196 | -1.4828 | 8.8927 | 8.756 | 8.5591 | 8.3305 | 8.0927 | 7.5958 | 7.0662 | 6.4591 | 5.758 | 4.9091 | 3.904 | 3.9779 | 3.8922 | 8.2361 | 7.9973 | 7.7085 | 7.3657 | 7.0239 | 6.4147 | 5.7392 | 4.9861 | 4.1218 | 3.0943
|  | LAURENCEKIRK | HE |  |  |  |  | 7.6509 | 7.4856 | 7.257 | 6.9642 | 6.6784 | 6.2009 | 5.5713 | 4.9244 | 4.2499 | 3.4784 | 1.2121 | 0.3213 | -0.90523 | 8.9009 | 8.7886 | 8.6499 | 8.4611 | 8.2621 | 7.8968 | 7.4193 | 6.9091 | 6.3621 | 5.7213 | 4.0938 | 4.03 | 3.5116 | 8.2463 | 8.0841 | 7.8708 | 7.5963 | 7.332 | 6.8912 | 6.3432 | 5.7861 | 5.1708 | 4.4667
|  | LAURENCEKIRK | CF |  |  |  |  | 7.6958 | 7.5795 | 7.4223 | 7.2091 | 6.9601 | 6.6927 | 6.3733 | 5.9917 | 5.6274 | 5.2029 | 3.0397 | 1.4407 | -0.34196 | 8.9438 | 8.8764 | 8.7713 | 8.6397 | 8.4784 | 8.2754 | 8.0254 | 7.7142 | 7.4264 | 7.0754 | 5.2897 | 4.23 | 3.1228 | 8.2922 | 8.18 | 8.0341 | 7.8381 | 7.6106 | 7.3596 | 7.0585 | 6.6963 | 6.3841 | 6.0034
| STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | 0.071 | 6.4829 | 6.4043 | 6.3124 | 6.2318 | 6.138 | 6.0278 | 5.9278 | 5.7798 | 5.64 | 5.5124 | 5.2216 | 5.1196 | 5.0839 | 7.191 | 7.1451 | 7.091 | 7.041 | 6.9788 | 6.9084 | 6.8512 | 6.7543 | 6.6604 | 6.5767 | 6.3818 | 6.2798 | 5.9461 | 6.8859 | 6.8094 | 6.7145 | 6.639 | 6.5431 | 6.4349 | 6.342 | 6.1961 | 6.0594 | 5.939
|  | LAXAY | EE |  |  |  |  | 6.4829 | 6.4043 | 6.3124 | 6.2318 | 6.138 | 6.0278 | 5.9278 | 5.7798 | 5.64 | 5.5124 | 5.2216 | 5.1614 | 5.138 | 7.191 | 7.1451 | 7.091 | 7.041 | 6.9788 | 6.9084 | 6.8512 | 6.7543 | 6.6604 | 6.5767 | 6.3818 | 6.2798 | 6.1349 | 6.8859 | 6.8094 | 6.7145 | 6.639 | 6.5431 | 6.4349 | 6.342 | 6.1961 | 6.0594 | 5.939
|  | LAXAY | HT |  |  |  |  | 6.5094 | 6.441 | 6.3624 | 6.29 | 6.2063 | 6.1329 | 6.039 | 5.9288 | 5.8186 | 5.7369 | 5.2798 | 5.1196 | 5.0839 | 7.2124 | 7.1767 | 7.1339 | 7.0961 | 7.0482 | 7.0094 | 6.9553 | 6.8778 | 6.8104 | 6.7696 | 6.4635 | 6.3839 | 6.3645 | 6.9145 | 6.8533 | 6.7778 | 6.7114 | 6.6278 | 6.5614 | 6.4706 | 6.3563 | 6.2492 | 6.1788
|  | LAXAY | HE |  |  |  |  | 6.5084 | 6.4584 | 6.3982 | 6.3451 | 6.2767 | 6.2257 | 6.1441 | 6.0461 | 5.9441 | 5.8778 | 5.3267 | 5.2369 | 5.2216 | 7.2114 | 7.1818 | 7.1461 | 7.1114 | 7.0665 | 7.0339 | 6.9839 | 6.9145 | 6.8492 | 6.8073 | 6.441 | 6.3329 | 6.1951 | 6.9135 | 6.8676 | 6.8114 | 6.7573 | 6.6869 | 6.638 | 6.5584 | 6.4584 | 6.3584 | 6.2992
|  | LAXAY | CF |  |  |  |  | 6.5145 | 6.4696 | 6.4267 | 6.3818 | 6.3288 | 6.2727 | 6.2318 | 6.1706 | 6.1073 | 6.042 | 5.7176 | 5.4298 | 5.2329 | 7.2155 | 7.1869 | 7.1614 | 7.1349 | 7.1012 | 7.0635 | 7.0369 | 6.9941 | 6.9441 | 6.8951 | 6.6308 | 6.3165 | 5.9461 | 6.9206 | 6.8788 | 6.839 | 6.7971 | 6.7451 | 6.688 | 6.6492 | 6.59 | 6.5247 | 6.4584
| COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | NO | 0.516 | -2.2378 | -2.348 | -2.4898 | -2.6092 | -2.7684 | -2.9347 | -3.1327 | -3.3959 | -3.648 | -3.8786 | -4.6224 | -5.0276 | -5.1235 | -1.0367 | -1.102 | -1.1898 | -1.2582 | -1.3653 | -1.4816 | -1.5898 | -1.7602 | -1.9224 | -2.0633 | -2.4755 | -2.7122 | -3.1765 | -1.6898 | -1.8 | -1.9378 | -2.0551 | -2.2122 | -2.3765 | -2.5541 | -2.8092 | -3.051 | -3.2694
|  | LEOCH | EE |  |  |  |  | -2.2378 | -2.348 | -2.4898 | -2.6092 | -2.7684 | -2.9347 | -3.1327 | -3.3959 | -3.648 | -3.8786 | -4.6224 | -4.9612 | -5.049 | -1.0367 | -1.102 | -1.1898 | -1.2582 | -1.3653 | -1.4816 | -1.5898 | -1.7602 | -1.9224 | -2.0633 | -2.4755 | -2.7122 | -2.9796 | -1.6898 | -1.8 | -1.9378 | -2.0551 | -2.2122 | -2.3765 | -2.5541 | -2.8092 | -3.051 | -3.2694
|  | LEOCH | HT |  |  |  |  | -2.1816 | -2.2878 | -2.4214 | -2.5327 | -2.6633 | -2.8153 | -2.9786 | -3.199 | -3.4163 | -3.5939 | -4.5776 | -5.0276 | -5.1235 | -0.9949 | -1.0531 | -1.1286 | -1.1857 | -1.2571 | -1.3408 | -1.4204 | -1.551 | -1.6806 | -1.7643 | -2.3469 | -2.5643 | -2.6092 | -1.6276 | -1.7337 | -1.8622 | -1.9622 | -2.0857 | -2.2306 | -2.3776 | -2.5888 | -2.7939 | -2.9459
|  | LEOCH | HE |  |  |  |  | -2.1796 | -2.25 | -2.3184 | -2.4071 | -2.4949 | -2.601 | -2.7163 | -2.8898 | -3.0561 | -3.1816 | -4.1122 | -4.5663 | -4.7153 | -0.99796 | -1.0418 | -1.0878 | -1.1469 | -1.2041 | -1.2745 | -1.3418 | -1.4582 | -1.5714 | -1.6378 | -2.2469 | -2.5541 | -2.8296 | -1.6265 | -1.6959 | -1.7653 | -1.8582 | -1.9449 | -2.0531 | -2.1582 | -2.3286 | -2.4898 | -2.5969
|  | LEOCH | CF |  |  |  |  | -2.1704 | -2.2184 | -2.2694 | -2.3133 | -2.3765 | -2.448 | -2.5316 | -2.5888 | -2.6786 | -2.7684 | -3.3 | -3.9735 | -4.449 | -0.99286 | -1.0276 | -1.0633 | -1.098 | -1.1388 | -1.1949 | -1.2571 | -1.3041 | -1.3796 | -1.4571 | -1.899 | -2.5122 | -3.1765 | -1.6204 | -1.6673 | -1.7235 | -1.7663 | -1.8286 | -1.9031 | -1.9898 | -2.0469 | -2.1398 | -2.2337
| NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 0.255 | 2.9853 | 2.9261 | 2.8547 | 2.7894 | 2.718 | 2.6414 | 2.5435 | 2.4465 | 2.3435 | 2.2424 | 1.9231 | 1.771 | 1.3406 | 3.2865 | 3.2498 | 3.2018 | 3.1569 | 3.1039 | 3.0447 | 2.9733 | 2.8998 | 2.8273 | 2.762 | 2.5386 | 2.6176 | 2.5176 | 3.239 | 3.1818 | 3.1155 | 3.0543 | 2.9798 | 2.9063 | 2.8063 | 2.7247 | 2.6165 | 2.5186
|  | LETHEN | EE |  |  |  |  | 2.9853 | 2.9261 | 2.8547 | 2.7894 | 2.718 | 2.6414 | 2.5435 | 2.4465 | 2.3435 | 2.2424 | 1.9333 | 1.8741 | 1.5049 | 3.2865 | 3.2498 | 3.2018 | 3.1569 | 3.1039 | 3.0447 | 2.9733 | 2.8998 | 2.8273 | 2.762 | 2.562 | 2.7033 | 2.6288 | 3.239 | 3.1818 | 3.1155 | 3.0543 | 2.9798 | 2.9063 | 2.8063 | 2.7247 | 2.6165 | 2.5186
|  | LETHEN | HT |  |  |  |  | 3.0057 | 2.9496 | 2.8924 | 2.8312 | 2.7669 | 2.6955 | 2.6261 | 2.5455 | 2.4649 | 2.3751 | 1.9996 | 1.82 | 1.3957 | 3.3049 | 3.2753 | 3.2447 | 3.2049 | 3.16 | 3.111 | 3.062 | 2.9967 | 2.9355 | 2.8692 | 2.6008 | 2.6706 | 2.6257 | 3.2624 | 3.2094 | 3.1584 | 3.1012 | 3.038 | 2.9676 | 2.9073 | 2.8257 | 2.7441 | 2.6573
|  | LETHEN | HE |  |  |  |  | 3.0057 | 2.9639 | 2.9231 | 2.8792 | 2.8302 | 2.7751 | 2.7149 | 2.622 | 2.5261 | 2.4251 | 1.9231 | 1.771 | 1.3406 | 3.3049 | 3.2753 | 3.2457 | 3.209 | 3.1641 | 3.1151 | 3.0641 | 2.9957 | 2.9314 | 2.86 | 2.5386 | 2.6176 | 2.5655 | 3.2635 | 3.2216 | 3.1849 | 3.1431 | 3.092 | 3.039 | 2.9778 | 2.8941 | 2.8124 | 2.7227
|  | LETHEN | CF |  |  |  |  | 3.0118 | 2.9792 | 2.9476 | 2.9057 | 2.869 | 2.8282 | 2.7833 | 2.7414 | 2.6935 | 2.6506 | 2.32 | 2.0006 | 1.4202 | 3.31 | 3.2896 | 3.2712 | 3.2437 | 3.2222 | 3.1896 | 3.1539 | 3.1182 | 3.0784 | 3.0365 | 2.7957 | 2.7543 | 2.5176 | 3.2696 | 3.238 | 3.2073 | 3.1676 | 3.1318 | 3.091 | 3.0451 | 3.0094 | 2.9604 | 2.9176
| GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | NO | 0 | 0.11494 | 0.11392 | 0.11392 | 0.11392 | 0.11188 | 0.11188 | 0.11086 | 0.11086 | 0.10984 | 0.10984 | 0.10678 | 0.10576 | 0.096755 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10288 | 0.10288 | 0.10084 | 0.10432 | 0.10432 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10636
|  | LETTEREWE | EE |  |  |  |  | 0.11494 | 0.11392 | 0.11392 | 0.11392 | 0.11188 | 0.11188 | 0.11086 | 0.11086 | 0.10984 | 0.10984 | 0.1078 | 0.1078 | 0.098796 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10288 | 0.10288 | 0.10186 | 0.10636 | 0.10636 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10636
|  | LETTEREWE | HT |  |  |  |  | 0.11494 | 0.11494 | 0.11392 | 0.11392 | 0.11392 | 0.11188 | 0.11188 | 0.11188 | 0.11086 | 0.11086 | 0.1078 | 0.10678 | 0.097776 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10186 | 0.10534 | 0.10534 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.1084 | 0.10738 | 0.10738
|  | LETTEREWE | HE |  |  |  |  | 0.11494 | 0.11392 | 0.11392 | 0.11392 | 0.11392 | 0.11188 | 0.11188 | 0.11086 | 0.11086 | 0.10984 | 0.10678 | 0.10576 | 0.096755 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10288 | 0.10084 | 0.10432 | 0.10432 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10636
|  | LETTEREWE | CF |  |  |  |  | 0.11494 | 0.11494 | 0.11494 | 0.11392 | 0.11392 | 0.11392 | 0.11392 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10678 | 0.096755 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.10288 | 0.10534 | 0.10432 | 0.11044 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.1084
| ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 0.364 | 4.8847 | 4.7092 | 4.5214 | 4.3541 | 4.1929 | 4.0684 | 3.8888 | 3.7 | 3.5531 | 3.3837 | 2.748 | 2.3714 | 2.3051 | 5.1459 | 5.0724 | 5.0031 | 4.9173 | 4.8255 | 4.7663 | 4.6561 | 4.5214 | 4.448 | 4.352 | 4.1551 | 3.9918 | 3.7286 | 5.1704 | 5.0265 | 4.8684 | 4.7224 | 4.5806 | 4.4684 | 4.3041 | 4.1316 | 3.998 | 3.8469
|  | LHANBRYDE | EE |  |  |  |  | 4.8847 | 4.7092 | 4.5214 | 4.3541 | 4.1929 | 4.0684 | 3.8888 | 3.7 | 3.5531 | 3.3837 | 2.7622 | 2.4112 | 2.3357 | 5.1459 | 5.0724 | 5.0031 | 4.9173 | 4.8255 | 4.7663 | 4.6561 | 4.5214 | 4.448 | 4.352 | 4.1551 | 3.9918 | 3.7949 | 5.1704 | 5.0265 | 4.8684 | 4.7224 | 4.5806 | 4.4684 | 4.3041 | 4.1316 | 3.998 | 3.8469
|  | LHANBRYDE | HT |  |  |  |  | 4.9082 | 4.7306 | 4.5286 | 4.3694 | 4.2357 | 4.1041 | 3.9408 | 3.7949 | 3.6306 | 3.4612 | 2.748 | 2.3714 | 2.3051 | 5.1918 | 5.1388 | 5.049 | 4.9837 | 4.9214 | 4.8571 | 4.7786 | 4.7214 | 4.6378 | 4.551 | 4.2051 | 4.0694 | 4.049 | 5.1949 | 5.05 | 4.8847 | 4.748 | 4.6296 | 4.5071 | 4.3602 | 4.2296 | 4.0816 | 3.9276
|  | LHANBRYDE | HE |  |  |  |  | 4.9092 | 4.7765 | 4.6184 | 4.4878 | 4.3929 | 4.2929 | 4.1837 | 4.0898 | 3.9786 | 3.8622 | 3.2041 | 2.8041 | 2.6551 | 5.1908 | 5.1418 | 5.0714 | 4.998 | 4.9571 | 4.9031 | 4.8378 | 4.7898 | 4.7173 | 4.6327 | 4.2704 | 4.1378 | 3.9245 | 5.1949 | 5.0888 | 4.9612 | 4.848 | 4.7663 | 4.6765 | 4.5755 | 4.4908 | 4.3878 | 4.2806
|  | LHANBRYDE | CF |  |  |  |  | 4.9306 | 4.8296 | 4.7153 | 4.6204 | 4.5561 | 4.4816 | 4.4276 | 4.3582 | 4.299 | 4.2633 | 3.8408 | 3.4031 | 3.0306 | 5.2031 | 5.1643 | 5.1153 | 5.0592 | 5.0296 | 4.9827 | 4.9439 | 4.8857 | 4.8286 | 4.8061 | 4.4745 | 4.2061 | 3.7286 | 5.2153 | 5.1357 | 5.0429 | 4.9622 | 4.9071 | 4.8429 | 4.7908 | 4.7276 | 4.6735 | 4.6418
| FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | NO | 0 | 0.10167 | 0.10167 | 0.099633 | 0.099633 | 0.091469 | 0.090449 | 0.087388 | 0.087388 | 0.086367 | 0.085347 | 0.075143 | 0.071061 | 0.06002 | 0.096755 | 0.096755 | 0.095735 | 0.095735 | 0.087571 | 0.086551 | 0.085531 | 0.085531 | 0.08451 | 0.08349 | 0.074306 | 0.075745 | 0.074724 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.090031 | 0.08901 | 0.08799 | 0.08799 | 0.085949 | 0.084929
|  | LIDDESDALE | EE |  |  |  |  | 0.10167 | 0.10167 | 0.099633 | 0.099633 | 0.091469 | 0.090449 | 0.087388 | 0.087388 | 0.086367 | 0.085347 | 0.075143 | 0.075143 | 0.066143 | 0.096755 | 0.096755 | 0.095735 | 0.095735 | 0.087571 | 0.086551 | 0.085531 | 0.085531 | 0.08451 | 0.08349 | 0.074306 | 0.078806 | 0.078806 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.090031 | 0.08901 | 0.08799 | 0.08799 | 0.085949 | 0.084929
|  | LIDDESDALE | HT |  |  |  |  | 0.10269 | 0.10167 | 0.10167 | 0.099633 | 0.099633 | 0.098612 | 0.098612 | 0.089429 | 0.087388 | 0.086367 | 0.082286 | 0.073102 | 0.063082 | 0.097776 | 0.096755 | 0.096755 | 0.095735 | 0.095735 | 0.094714 | 0.094714 | 0.086551 | 0.085531 | 0.08451 | 0.081449 | 0.077786 | 0.076765 | 0.10126 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.097173 | 0.097173 | 0.08901 | 0.08799 | 0.085949
|  | LIDDESDALE | HE |  |  |  |  | 0.10269 | 0.10167 | 0.10167 | 0.099633 | 0.099633 | 0.098612 | 0.097592 | 0.088408 | 0.087388 | 0.086367 | 0.080245 | 0.071061 | 0.06002 | 0.097776 | 0.096755 | 0.096755 | 0.095735 | 0.095735 | 0.094714 | 0.093694 | 0.085531 | 0.08451 | 0.08451 | 0.080429 | 0.075745 | 0.074724 | 0.10126 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.097173 | 0.096153 | 0.08799 | 0.086969 | 0.085949
|  | LIDDESDALE | CF |  |  |  |  | 0.10269 | 0.10167 | 0.10167 | 0.10167 | 0.099633 | 0.099633 | 0.099633 | 0.098612 | 0.091469 | 0.090449 | 0.085347 | 0.073102 | 0.062061 | 0.097776 | 0.096755 | 0.096755 | 0.096755 | 0.095735 | 0.095735 | 0.095735 | 0.094714 | 0.087571 | 0.086551 | 0.08349 | 0.077786 | 0.075745 | 0.10126 | 0.10023 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.099214 | 0.097173 | 0.090031 | 0.08901
| KEITH 1 | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 0.101 | -0.24796 | -0.2949 | -0.33878 | -0.39082 | -0.48265 | -0.57041 | -0.69388 | -0.78469 | -0.89694 | -1.002 | -1.2653 | -1.3429 | -1.3745 | 0.50918 | 0.46939 | 0.42857 | 0.38776 | 0.33061 | 0.28061 | 0.20102 | 0.15204 | 0.080612 | 0.017347 | -0.14388 | -0.21122 | -0.46327 | 0.1051 | 0.030612 | -0.036735 | -0.09898 | -0.1898 | -0.27449 | -0.39592 | -0.47551 | -0.5898 | -0.6898
|  | LIMEHILLOCKS | EE |  |  |  |  | -0.24796 | -0.2949 | -0.33878 | -0.39082 | -0.48265 | -0.57041 | -0.69388 | -0.78469 | -0.89694 | -1.002 | -1.2653 | -1.3133 | -1.3235 | 0.50918 | 0.46939 | 0.42857 | 0.38776 | 0.33061 | 0.28061 | 0.20102 | 0.15204 | 0.080612 | 0.017347 | -0.14388 | -0.20816 | -0.3102 | 0.1051 | 0.030612 | -0.036735 | -0.09898 | -0.1898 | -0.27449 | -0.39592 | -0.47551 | -0.5898 | -0.6898
|  | LIMEHILLOCKS | HT |  |  |  |  | -0.23571 | -0.27449 | -0.3102 | -0.35306 | -0.43367 | -0.50204 | -0.59388 | -0.68265 | -0.77143 | -0.86939 | -1.1867 | -1.3429 | -1.3745 | 0.52347 | 0.49184 | 0.4602 | 0.42347 | 0.37959 | 0.34082 | 0.28878 | 0.23469 | 0.18367 | 0.12653 | -0.083673 | -0.17347 | -0.20714 | 0.12857 | 0.073469 | 0.021429 | -0.039796 | -0.11939 | -0.17653 | -0.26122 | -0.3449 | -0.43367 | -0.52959
|  | LIMEHILLOCKS | HE |  |  |  |  | -0.23571 | -0.26735 | -0.2949 | -0.33163 | -0.37347 | -0.42041 | -0.50408 | -0.58571 | -0.66735 | -0.74796 | -1.1714 | -1.2888 | -1.351 | 0.52347 | 0.49388 | 0.46531 | 0.43265 | 0.39388 | 0.35408 | 0.30408 | 0.24796 | 0.19184 | 0.13571 | -0.12959 | -0.21122 | -0.29286 | 0.12857 | 0.083673 | 0.045918 | -0.005102 | -0.070408 | -0.11429 | -0.19286 | -0.27143 | -0.35306 | -0.43367
|  | LIMEHILLOCKS | CF |  |  |  |  | -0.23061 | -0.25714 | -0.27755 | -0.30918 | -0.33469 | -0.36735 | -0.40612 | -0.47041 | -0.52143 | -0.58265 | -0.85 | -1.1071 | -1.2837 | 0.52857 | 0.50918 | 0.48878 | 0.46327 | 0.44082 | 0.41224 | 0.38469 | 0.3449 | 0.30918 | 0.27041 | 0.062245 | -0.19592 | -0.46327 | 0.13673 | 0.097959 | 0.066327 | 0.018367 | -0.017347 | -0.070408 | -0.10408 | -0.16939 | -0.22041 | -0.28061
| ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 0.034 | 9.787 | 9.7707 | 9.7523 | 9.736 | 9.7104 | 9.6982 | 9.6686 | 9.6441 | 9.6125 | 9.587 | 9.5084 | 9.488 | 8.9629 | 9.3466 | 9.3384 | 9.3262 | 9.316 | 9.3007 | 9.2904 | 9.2721 | 9.2517 | 9.2313 | 9.2119 | 9.1323 | 9.3658 | 9.3586 | 9.4066 | 9.3943 | 9.38 | 9.3658 | 9.3474 | 9.3321 | 9.3096 | 9.2841 | 9.2576 | 9.2351
|  | LOCH CARNAN | EE |  |  |  |  | 9.787 | 9.7707 | 9.7523 | 9.736 | 9.7104 | 9.6982 | 9.6686 | 9.6441 | 9.6125 | 9.587 | 9.5084 | 9.488 | 8.9649 | 9.3466 | 9.3384 | 9.3262 | 9.316 | 9.3007 | 9.2904 | 9.2721 | 9.2517 | 9.2313 | 9.2119 | 9.1323 | 9.3658 | 9.3617 | 9.4076 | 9.3943 | 9.38 | 9.3658 | 9.3474 | 9.3321 | 9.3096 | 9.2841 | 9.2576 | 9.2351
|  | LOCH CARNAN | HT |  |  |  |  | 9.787 | 9.7788 | 9.7656 | 9.7533 | 9.7349 | 9.7207 | 9.6982 | 9.6696 | 9.6564 | 9.6309 | 9.5298 | 9.489 | 8.9629 | 9.3466 | 9.3404 | 9.3333 | 9.3241 | 9.3119 | 9.3007 | 9.2843 | 9.266 | 9.2476 | 9.2282 | 9.1435 | 9.3668 | 9.3586 | 9.4066 | 9.3974 | 9.3872 | 9.377 | 9.3607 | 9.3453 | 9.3249 | 9.3015 | 9.28 | 9.2556
|  | LOCH CARNAN | HE |  |  |  |  | 9.787 | 9.7819 | 9.7717 | 9.7604 | 9.7462 | 9.7339 | 9.7156 | 9.687 | 9.6758 | 9.6513 | 9.5431 | 9.5176 | 8.9945 | 9.3466 | 9.3415 | 9.3364 | 9.3272 | 9.317 | 9.3047 | 9.2894 | 9.268 | 9.2527 | 9.2343 | 9.1456 | 9.3862 | 9.3811 | 9.4076 | 9.4004 | 9.3913 | 9.38 | 9.3668 | 9.3525 | 9.3341 | 9.3086 | 9.2892 | 9.2637
|  | LOCH CARNAN | CF |  |  |  |  | 9.7911 | 9.788 | 9.7809 | 9.7717 | 9.7625 | 9.7523 | 9.74 | 9.7258 | 9.7115 | 9.6941 | 9.6298 | 9.5513 | 8.9915 | 9.3486 | 9.3466 | 9.3425 | 9.3384 | 9.3323 | 9.3272 | 9.319 | 9.3078 | 9.2976 | 9.2853 | 9.2241 | 9.4168 | 9.3668 | 9.4107 | 9.4076 | 9.4004 | 9.3943 | 9.3872 | 9.379 | 9.3688 | 9.3566 | 9.3443 | 9.329
| GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | NO | 0.023 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.54398 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.5675 | 0.5675 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648
|  | LOCH GLASCARNOCH | EE |  |  |  |  | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.54398 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.5675 | 0.5675 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648
|  | LOCH GLASCARNOCH | HT |  |  |  |  | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.54398 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.5675 | 0.5675 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648
|  | LOCH GLASCARNOCH | HE |  |  |  |  | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.54398 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.5675 | 0.5675 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648
|  | LOCH GLASCARNOCH | CF |  |  |  |  | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.58898 | 0.54398 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.545 | 0.5675 | 0.5675 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648
| FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | NO | 0.74 | -0.58539 | -0.60171 | -0.62416 | -0.64151 | -0.66906 | -0.68131 | -0.71294 | -0.73845 | -0.76702 | -0.79559 | -0.85682 | -0.87518 | -0.87927 | -0.30988 | -0.316 | -0.32518 | -0.33539 | -0.34355 | -0.35069 | -0.36294 | -0.37212 | -0.38335 | -0.39457 | -0.4211 | -0.43029 | -0.44355 | -0.2609 | -0.27518 | -0.29355 | -0.30886 | -0.33029 | -0.34253 | -0.37008 | -0.39559 | -0.42416 | -0.45171
|  | LOCHALINE | EE |  |  |  |  | -0.58539 | -0.60171 | -0.62416 | -0.64151 | -0.66906 | -0.68131 | -0.71294 | -0.73845 | -0.76702 | -0.79559 | -0.85682 | -0.86702 | -0.87212 | -0.30988 | -0.316 | -0.32518 | -0.33539 | -0.34355 | -0.35069 | -0.36294 | -0.37212 | -0.38335 | -0.39457 | -0.4211 | -0.4262 | -0.43845 | -0.2609 | -0.27518 | -0.29355 | -0.30886 | -0.33029 | -0.34253 | -0.37008 | -0.39559 | -0.42416 | -0.45171
|  | LOCHALINE | HT |  |  |  |  | -0.57722 | -0.59253 | -0.60376 | -0.61906 | -0.63335 | -0.65478 | -0.68029 | -0.69355 | -0.71702 | -0.74355 | -0.83641 | -0.87518 | -0.87927 | -0.3058 | -0.31396 | -0.31702 | -0.32416 | -0.33131 | -0.34151 | -0.34967 | -0.3558 | -0.36498 | -0.37722 | -0.41396 | -0.43029 | -0.43437 | -0.25478 | -0.26906 | -0.27824 | -0.29355 | -0.30682 | -0.32416 | -0.34457 | -0.35886 | -0.37824 | -0.40171
|  | LOCHALINE | HE |  |  |  |  | -0.57722 | -0.59151 | -0.59763 | -0.60988 | -0.62314 | -0.64049 | -0.65988 | -0.67212 | -0.69355 | -0.716 | -0.8211 | -0.84661 | -0.84865 | -0.3058 | -0.31396 | -0.316 | -0.32008 | -0.32722 | -0.33539 | -0.34457 | -0.35171 | -0.35988 | -0.37008 | -0.41702 | -0.43029 | -0.43437 | -0.25478 | -0.266 | -0.27008 | -0.28233 | -0.29457 | -0.30784 | -0.32518 | -0.33743 | -0.35273 | -0.37518
|  | LOCHALINE | CF |  |  |  |  | -0.58131 | -0.58335 | -0.59355 | -0.60478 | -0.61396 | -0.62314 | -0.63845 | -0.6558 | -0.67212 | -0.67518 | -0.74763 | -0.816 | -0.84457 | -0.30784 | -0.30988 | -0.31498 | -0.31804 | -0.32212 | -0.32518 | -0.33131 | -0.33947 | -0.34661 | -0.34967 | -0.38233 | -0.41294 | -0.44355 | -0.2558 | -0.2609 | -0.26906 | -0.27824 | -0.28845 | -0.29661 | -0.30784 | -0.32212 | -0.33539 | -0.33947
| GRUDIE BRIDGE | LOCHCARRON | MINIMUM HEADROOM | NG 91944 41839 | YES | NO | 0.037 | 1.9571 | 1.902 | 1.8602 | 1.8122 | 1.7551 | 1.7163 | 1.6429 | 1.5327 | 1.4194 | 1.3112 | 1.1541 | 1.1082 | 0.90357 | 2.1219 | 2.0862 | 2.0597 | 2.0321 | 1.9862 | 1.9648 | 1.9148 | 1.8485 | 1.7821 | 1.7189 | 1.6066 | 1.6936 | 1.5089 | 2.0467 | 1.9946 | 1.9548 | 1.9099 | 1.8548 | 1.8202 | 1.7508 | 1.6518 | 1.5477 | 1.4497
|  | LOCHCARRON | EE |  |  |  |  | 1.9571 | 1.902 | 1.8602 | 1.8122 | 1.7551 | 1.7163 | 1.6439 | 1.5327 | 1.4194 | 1.3112 | 1.1541 | 1.1643 | 0.925 | 2.1219 | 2.0862 | 2.0597 | 2.0321 | 1.9862 | 1.9648 | 1.9148 | 1.8485 | 1.7821 | 1.7189 | 1.6066 | 1.7028 | 1.6263 | 2.0467 | 1.9946 | 1.9548 | 1.9099 | 1.8548 | 1.8202 | 1.7508 | 1.6518 | 1.5477 | 1.4497
|  | LOCHCARRON | HT |  |  |  |  | 1.9704 | 1.9327 | 1.8908 | 1.8602 | 1.8143 | 1.7337 | 1.6429 | 1.5398 | 1.502 | 1.4469 | 1.2102 | 1.1082 | 0.90357 | 2.1393 | 2.1168 | 2.0903 | 2.073 | 2.0444 | 2.0026 | 1.9515 | 1.8934 | 1.874 | 1.8352 | 1.674 | 1.7242 | 1.7497 | 2.062 | 2.0283 | 1.9895 | 1.961 | 1.9171 | 1.8497 | 1.7681 | 1.6753 | 1.6426 | 1.5875
|  | LOCHCARRON | HE |  |  |  |  | 1.9724 | 1.9408 | 1.9122 | 1.8837 | 1.849 | 1.8184 | 1.7714 | 1.6857 | 1.6286 | 1.5418 | 1.2459 | 1.1827 | 0.94643 | 2.1383 | 2.1179 | 2.0974 | 2.0811 | 2.0536 | 2.0342 | 2.0005 | 1.9454 | 1.9199 | 1.8689 | 1.6719 | 1.713 | 1.6426 | 2.064 | 2.0355 | 2.0059 | 1.9834 | 1.9477 | 1.9191 | 1.8732 | 1.7946 | 1.7477 | 1.6722
|  | LOCHCARRON | CF |  |  |  |  | 1.9827 | 1.9582 | 1.9337 | 1.901 | 1.8837 | 1.8531 | 1.8276 | 1.7908 | 1.7296 | 1.6643 | 1.4388 | 1.2694 | 0.95153 | 2.1464 | 2.1301 | 2.1128 | 2.0893 | 2.077 | 2.0536 | 2.0372 | 2.0066 | 1.9628 | 1.925 | 1.7648 | 1.6936 | 1.5089 | 2.0742 | 2.0518 | 2.0242 | 1.9946 | 1.9753 | 1.9457 | 1.9232 | 1.8865 | 1.8293 | 1.7712
| TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0.058 | 0.15306 | 0.13367 | 0.11327 | 0.064286 | 0.022449 | -0.020408 | -0.19184 | -0.30612 | -0.40408 | -0.49796 | -0.64082 | -0.69184 | -0.69694 | 0.40408 | 0.3898 | 0.37551 | 0.34898 | 0.32245 | 0.3 | 0.17245 | 0.094898 | 0.026531 | -0.032653 | -0.21939 | -0.2551 | -0.26327 | 0.21531 | 0.19694 | 0.17653 | 0.13571 | 0.095918 | 0.058163 | -0.088776 | -0.18367 | -0.26939 | -0.34898
|  | LOCHDONHEAD | EE |  |  |  |  | 0.15306 | 0.13367 | 0.11327 | 0.064286 | 0.022449 | -0.020408 | -0.085714 | -0.20714 | -0.31429 | -0.41531 | -0.63265 | -0.65 | -0.65918 | 0.40408 | 0.3898 | 0.37551 | 0.34898 | 0.32245 | 0.3 | 0.26122 | 0.16327 | 0.080612 | 0.011224 | -0.14184 | -0.1602 | -0.18673 | 0.21531 | 0.19694 | 0.17653 | 0.13571 | 0.095918 | 0.058163 | 0.0010204 | -0.11122 | -0.21122 | -0.30102
|  | LOCHDONHEAD | HT |  |  |  |  | 0.16327 | 0.14796 | 0.13571 | 0.069388 | 0.023469 | -0.014286 | -0.19184 | -0.30612 | -0.40408 | -0.49796 | -0.60816 | -0.65612 | -0.66224 | 0.40918 | 0.4 | 0.39388 | 0.3602 | 0.33367 | 0.31531 | 0.17245 | 0.094898 | 0.026531 | -0.032653 | -0.11531 | -0.1449 | -0.14796 | 0.22347 | 0.2102 | 0.19898 | 0.14388 | 0.10408 | 0.068367 | -0.088776 | -0.18367 | -0.26939 | -0.34898
|  | LOCHDONHEAD | HE |  |  |  |  | 0.16327 | 0.1449 | 0.13571 | 0.085714 | 0.05 | 0.0071429 | -0.05102 | -0.18061 | -0.29694 | -0.39592 | -0.64082 | -0.69184 | -0.6949 | 0.40918 | 0.39694 | 0.39388 | 0.36735 | 0.34184 | 0.31837 | 0.28878 | 0.18163 | 0.080612 | -0.005102 | -0.21939 | -0.2551 | -0.25714 | 0.22245 | 0.20612 | 0.19286 | 0.15612 | 0.12551 | 0.086735 | 0.035714 | -0.086735 | -0.19898 | -0.29286
|  | LOCHDONHEAD | CF |  |  |  |  | 0.1602 | 0.15714 | 0.14286 | 0.12857 | 0.11122 | 0.089796 | 0.065306 | 0.02449 | -0.032653 | -0.10816 | -0.40918 | -0.61939 | -0.69694 | 0.40612 | 0.40714 | 0.39694 | 0.38776 | 0.37347 | 0.36122 | 0.34898 | 0.32245 | 0.27755 | 0.23265 | -0.027551 | -0.21327 | -0.26327 | 0.22143 | 0.21837 | 0.20612 | 0.19184 | 0.17551 | 0.15714 | 0.13673 | 0.10102 | 0.045918 | -0.018367
| KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | 0.073 | -0.20102 | -0.25306 | -0.29082 | -0.34286 | -0.40306 | -0.4449 | -0.52245 | -0.59898 | -0.67959 | -0.75306 | -0.92857 | -0.97041 | -1 | 0.10306 | 0.065306 | 0.041837 | 0.0071429 | -0.031633 | -0.058163 | -0.10612 | -0.15612 | -0.20612 | -0.25204 | -0.37347 | -0.43878 | -0.58265 | -0.095918 | -0.14694 | -0.18367 | -0.23061 | -0.2898 | -0.32959 | -0.40102 | -0.47551 | -0.55102 | -0.62041
|  | LOCHEARNHEAD | EE |  |  |  |  | -0.20102 | -0.25306 | -0.29082 | -0.34286 | -0.40306 | -0.4449 | -0.52245 | -0.59898 | -0.67959 | -0.75306 | -0.92857 | -0.97041 | -0.9602 | 0.10306 | 0.065306 | 0.041837 | 0.0071429 | -0.031633 | -0.058163 | -0.10612 | -0.15612 | -0.20612 | -0.25204 | -0.37347 | -0.43878 | -0.49184 | -0.095918 | -0.14694 | -0.18367 | -0.23061 | -0.2898 | -0.32959 | -0.40102 | -0.47551 | -0.55102 | -0.62041
|  | LOCHEARNHEAD | HT |  |  |  |  | -0.18265 | -0.22143 | -0.26224 | -0.3 | -0.34592 | -0.38673 | -0.4449 | -0.51531 | -0.55204 | -0.61735 | -0.88061 | -0.96429 | -1 | 0.11735 | 0.092857 | 0.068367 | 0.047959 | 0.019388 | -0.0061224 | -0.041837 | -0.089796 | -0.10918 | -0.15102 | -0.31531 | -0.35612 | -0.37857 | -0.076531 | -0.11224 | -0.15102 | -0.18469 | -0.23163 | -0.27041 | -0.32653 | -0.39184 | -0.42653 | -0.48776
|  | LOCHEARNHEAD | HE |  |  |  |  | -0.18265 | -0.21327 | -0.24694 | -0.27347 | -0.31429 | -0.34388 | -0.39796 | -0.45918 | -0.49082 | -0.54796 | -0.85 | -0.89898 | -0.92755 | 0.11735 | 0.092857 | 0.072449 | 0.052041 | 0.02551 | 0.005102 | -0.028571 | -0.070408 | -0.088776 | -0.12857 | -0.32551 | -0.38776 | -0.46939 | -0.076531 | -0.10816 | -0.13878 | -0.16531 | -0.20204 | -0.23265 | -0.28367 | -0.34082 | -0.37041 | -0.42653
|  | LOCHEARNHEAD | CF |  |  |  |  | -0.18163 | -0.20408 | -0.23061 | -0.26633 | -0.28776 | -0.32143 | -0.34796 | -0.3949 | -0.43469 | -0.45102 | -0.65714 | -0.80714 | -0.90408 | 0.11735 | 0.1 | 0.084694 | 0.059184 | 0.044898 | 0.019388 | 0.0040816 | -0.030612 | -0.059184 | -0.070408 | -0.23265 | -0.39286 | -0.58265 | -0.076531 | -0.097959 | -0.12449 | -0.15816 | -0.17755 | -0.21122 | -0.23469 | -0.27755 | -0.31633 | -0.33265
| LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | YES | 0.909 | 16.0971 | 15.7727 | 15.5298 | 15.2829 | 14.991 | 14.689 | 14.3512 | 13.9084 | 13.4818 | 13.1002 | 11.9155 | 11.6104 | 10.6208 | 16.3126 | 16.1075 | 15.9259 | 15.7555 | 15.534 | 15.2932 | 15.0657 | 14.7544 | 14.4596 | 14.1993 | 13.3085 | 13.5141 | 10.557 | 16.4856 | 16.2692 | 16.0284 | 15.8029 | 15.5294 | 15.2468 | 14.9356 | 14.5213 | 14.1111 | 13.7437
|  | LOCHEE | EE |  |  |  |  | 16.0971 | 15.7727 | 15.5298 | 15.2829 | 14.991 | 14.689 | 14.3512 | 13.9084 | 13.4818 | 13.1002 | 11.9155 | 12.1196 | 11.0769 | 16.3126 | 16.1075 | 15.9259 | 15.7555 | 15.534 | 15.2932 | 15.0657 | 14.7544 | 14.4596 | 14.1993 | 13.3085 | 13.5141 | 12.5897 | 16.4856 | 16.2692 | 16.0284 | 15.8029 | 15.5294 | 15.2468 | 14.9356 | 14.5213 | 14.1111 | 13.7437
|  | LOCHEE | HT |  |  |  |  | 16.1257 | 15.8339 | 15.6216 | 15.4216 | 15.1788 | 14.9206 | 14.6186 | 14.2686 | 13.9237 | 13.5982 | 11.9951 | 11.6104 | 10.6208 | 16.3871 | 16.2198 | 16.081 | 15.9616 | 15.8055 | 15.6289 | 15.4657 | 15.2361 | 15.0126 | 14.831 | 13.7963 | 14.0478 | 14.0335 | 16.5039 | 16.3315 | 16.1376 | 15.9437 | 15.7182 | 15.4764 | 15.2039 | 14.8794 | 14.5631 | 14.2631
|  | LOCHEE | HE |  |  |  |  | 16.1614 | 15.9329 | 15.7992 | 15.6788 | 15.5339 | 15.3716 | 15.1543 | 14.89 | 14.6329 | 14.4012 | 13.2594 | 12.8012 | 11.8667 | 16.3983 | 16.2432 | 16.1238 | 16.0259 | 15.8963 | 15.7483 | 15.6055 | 15.4055 | 15.2055 | 15.0453 | 14.0422 | 13.9733 | 13.1692 | 16.5213 | 16.3866 | 16.2999 | 16.1774 | 16.0335 | 15.8805 | 15.6835 | 15.4356 | 15.1988 | 14.9846
|  | LOCHEE | CF |  |  |  |  | 16.2135 | 16.0563 | 15.9869 | 15.9124 | 15.8247 | 15.7359 | 15.6522 | 15.5604 | 15.4655 | 15.3614 | 14.6227 | 13.5767 | 11.6851 | 16.4238 | 16.3075 | 16.2279 | 16.1544 | 16.0483 | 15.9391 | 15.8126 | 15.6973 | 15.5636 | 15.4187 | 14.5269 | 13.6652 | 10.557 | 16.559 | 16.4774 | 16.4376 | 16.3978 | 16.308 | 16.2152 | 16.1264 | 16.0427 | 15.9509 | 15.8509
| PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 1.28 | 16.2714 | 16.1173 | 15.8959 | 15.6694 | 15.3938 | 15.1194 | 14.7387 | 14.2622 | 13.7785 | 13.35 | 12.7683 | 12.4969 | 11.1969 | 18.1581 | 18.0612 | 17.9122 | 17.7734 | 17.5877 | 17.4214 | 17.1806 | 16.8316 | 16.4826 | 16.1775 | 15.7857 | 16.0898 | 14.9979 | 17.4071 | 17.2592 | 17.053 | 16.8418 | 16.5806 | 16.3285 | 15.9775 | 15.5041 | 15.0316 | 14.6183
|  | LOCHGILPHEAD | EE |  |  |  |  | 16.2714 | 16.1173 | 15.8959 | 15.6694 | 15.3938 | 15.1194 | 14.7387 | 14.2622 | 13.7785 | 13.35 | 12.7683 | 12.6306 | 11.3306 | 18.1581 | 18.0612 | 17.9122 | 17.7734 | 17.5877 | 17.4214 | 17.1806 | 16.8316 | 16.4826 | 16.1775 | 15.7959 | 16.0898 | 15.6092 | 17.4071 | 17.2592 | 17.053 | 16.8418 | 16.5806 | 16.3285 | 15.9775 | 15.5041 | 15.0316 | 14.6183
|  | LOCHGILPHEAD | HT |  |  |  |  | 16.3653 | 16.2234 | 16.0602 | 15.8275 | 15.5796 | 15.353 | 14.9357 | 14.4632 | 14.0887 | 13.7296 | 12.9469 | 12.4969 | 11.2204 | 18.2357 | 18.151 | 18.0541 | 17.9163 | 17.7663 | 17.6398 | 17.3296 | 16.9857 | 16.7377 | 16.4938 | 16.0734 | 16.4183 | 16.3694 | 17.501 | 17.3663 | 17.2163 | 17.0041 | 16.7765 | 16.5734 | 16.149 | 15.6877 | 15.3296 | 14.9887
|  | LOCHGILPHEAD | HE |  |  |  |  | 16.3663 | 16.253 | 16.1296 | 15.9479 | 15.7438 | 15.5387 | 15.249 | 14.852 | 14.5194 | 14.1806 | 12.7704 | 12.552 | 11.1969 | 18.2347 | 18.1602 | 18.0785 | 17.9653 | 17.8347 | 17.7143 | 17.5357 | 17.249 | 17.0163 | 16.7643 | 15.7857 | 16.2622 | 15.8183 | 17.501 | 17.3949 | 17.2775 | 17.1112 | 16.9245 | 16.7398 | 16.4765 | 16.0887 | 15.7622 | 15.4285
|  | LOCHGILPHEAD | CF |  |  |  |  | 16.3938 | 16.3092 | 16.2204 | 16.102 | 15.9765 | 15.8306 | 15.703 | 15.4734 | 15.252 | 14.9887 | 13.8214 | 13.1204 | 11.2898 | 18.2438 | 18.2 | 18.1449 | 18.0632 | 17.9816 | 17.8826 | 17.8051 | 17.65 | 17.4898 | 17.302 | 16.3418 | 16.1071 | 14.9979 | 17.5194 | 17.4469 | 17.3632 | 17.251 | 17.1347 | 16.9979 | 16.8847 | 16.6724 | 16.4612 | 16.2132
| CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | 0.069 | -0.18776 | -0.19796 | -0.20816 | -0.21837 | -0.22959 | -0.23673 | -0.2602 | -0.2898 | -0.30408 | -0.32449 | -0.36837 | -0.38265 | -0.38776 | 0.76837 | 0.7602 | 0.74796 | 0.73673 | 0.71939 | 0.71735 | 0.7 | 0.67755 | 0.66429 | 0.65102 | 0.61224 | 0.59796 | 0.54694 | 0.57041 | 0.55612 | 0.54184 | 0.52755 | 0.50612 | 0.50102 | 0.47755 | 0.44592 | 0.43367 | 0.41429
|  | LOCHGOILHEAD | EE |  |  |  |  | -0.18673 | -0.19796 | -0.20816 | -0.21837 | -0.22959 | -0.23673 | -0.2602 | -0.2898 | -0.30408 | -0.32449 | -0.36837 | -0.37551 | -0.38061 | 0.76939 | 0.7602 | 0.74796 | 0.73673 | 0.71939 | 0.71735 | 0.7 | 0.67755 | 0.66429 | 0.65102 | 0.61224 | 0.59796 | 0.57245 | 0.57041 | 0.55612 | 0.54184 | 0.52755 | 0.50612 | 0.50102 | 0.47755 | 0.44592 | 0.43367 | 0.41429
|  | LOCHGOILHEAD | HT |  |  |  |  | -0.18776 | -0.1898 | -0.2 | -0.2102 | -0.21939 | -0.22857 | -0.23878 | -0.24796 | -0.26122 | -0.28163 | -0.35612 | -0.38265 | -0.38776 | 0.76837 | 0.76735 | 0.75816 | 0.75306 | 0.7449 | 0.73673 | 0.72347 | 0.71735 | 0.7051 | 0.6898 | 0.63265 | 0.61531 | 0.6102 | 0.57449 | 0.56735 | 0.55714 | 0.54898 | 0.53776 | 0.52755 | 0.51122 | 0.50204 | 0.48571 | 0.46429
|  | LOCHGOILHEAD | HE |  |  |  |  | -0.18776 | -0.1898 | -0.19592 | -0.20408 | -0.2102 | -0.21735 | -0.22857 | -0.2398 | -0.24388 | -0.26122 | -0.33878 | -0.35816 | -0.3602 | 0.76837 | 0.76735 | 0.76122 | 0.75306 | 0.74592 | 0.74082 | 0.72653 | 0.71327 | 0.70918 | 0.69592 | 0.63469 | 0.61327 | 0.58776 | 0.57449 | 0.56939 | 0.56122 | 0.55306 | 0.54184 | 0.53469 | 0.51633 | 0.49694 | 0.49388 | 0.47449
|  | LOCHGOILHEAD | CF |  |  |  |  | -0.18469 | -0.18878 | -0.19184 | -0.19898 | -0.20408 | -0.20918 | -0.21633 | -0.22653 | -0.23367 | -0.24184 | -0.28367 | -0.33571 | -0.35408 | 0.76939 | 0.77041 | 0.76735 | 0.7602 | 0.75204 | 0.7449 | 0.73878 | 0.72755 | 0.71837 | 0.70714 | 0.66531 | 0.60408 | 0.54694 | 0.57653 | 0.57347 | 0.56939 | 0.56224 | 0.55204 | 0.54286 | 0.5398 | 0.52449 | 0.51122 | 0.49898
| GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | NO | 0.236 | -0.57347 | -0.6102 | -0.65816 | -0.70612 | -0.77959 | -0.82551 | -0.9102 | -0.99796 | -1.0898 | -1.1673 | -1.3173 | -1.3816 | -1.3949 | -0.24898 | -0.26939 | -0.28878 | -0.31735 | -0.36224 | -0.39796 | -0.4551 | -0.51837 | -0.58367 | -0.63673 | -0.75102 | -0.81224 | -0.98061 | -0.41327 | -0.43776 | -0.49898 | -0.55408 | -0.62347 | -0.66735 | -0.75102 | -0.83673 | -0.92347 | -0.99694
|  | LOCHINVER | EE |  |  |  |  | -0.56224 | -0.6051 | -0.65816 | -0.70612 | -0.77959 | -0.82551 | -0.9102 | -0.99796 | -1.0898 | -1.1673 | -1.3173 | -1.349 | -1.3724 | -0.22857 | -0.25816 | -0.28878 | -0.31735 | -0.36224 | -0.39796 | -0.4551 | -0.51837 | -0.58367 | -0.63673 | -0.75102 | -0.81224 | -0.90408 | -0.39286 | -0.43776 | -0.49898 | -0.55408 | -0.62347 | -0.66735 | -0.75102 | -0.83673 | -0.92347 | -0.99694
|  | LOCHINVER | HT |  |  |  |  | -0.57347 | -0.6102 | -0.64592 | -0.67755 | -0.72041 | -0.75816 | -0.81122 | -0.85918 | -0.92653 | -0.99796 | -1.2959 | -1.3816 | -1.3949 | -0.24898 | -0.26939 | -0.28673 | -0.3051 | -0.32857 | -0.35102 | -0.37857 | -0.40714 | -0.45204 | -0.5 | -0.7102 | -0.75918 | -0.77041 | -0.41327 | -0.43469 | -0.47041 | -0.5051 | -0.55408 | -0.59796 | -0.65714 | -0.70612 | -0.77245 | -0.83776
|  | LOCHINVER | HE |  |  |  |  | -0.54592 | -0.58265 | -0.61327 | -0.6449 | -0.67959 | -0.71122 | -0.75816 | -0.82449 | -0.8602 | -0.92041 | -1.2224 | -1.2571 | -1.2653 | -0.22041 | -0.24592 | -0.26633 | -0.28776 | -0.31122 | -0.33469 | -0.36531 | -0.39898 | -0.42449 | -0.46735 | -0.68469 | -0.74082 | -0.82143 | -0.38571 | -0.41224 | -0.4398 | -0.47143 | -0.51429 | -0.55 | -0.60408 | -0.66735 | -0.70306 | -0.75816
|  | LOCHINVER | CF |  |  |  |  | -0.45 | -0.49286 | -0.52857 | -0.56531 | -0.59388 | -0.63367 | -0.66531 | -0.71327 | -0.76224 | -0.78367 | -1.0204 | -1.1888 | -1.2816 | -0.11633 | -0.14694 | -0.17245 | -0.19592 | -0.21531 | -0.24286 | -0.26837 | -0.30918 | -0.34796 | -0.36633 | -0.56939 | -0.76327 | -0.98061 | -0.28571 | -0.32449 | -0.3602 | -0.40306 | -0.43163 | -0.47551 | -0.50816 | -0.55714 | -0.60306 | -0.62449
| LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | YES | 2.425 | 5.7775 | 4.6949 | 3.7265 | 2.6326 | 2.0255 | 0.3571 | -0.62351 | -1.5378 | -2.2653 | -3.1694 | -8.3317 | -13.9398 | -19.1241 | 8.8147 | 7.9361 | 7.1606 | 6.2402 | 5.98 | 4.2147 | 3.4483 | 2.631 | 1.7034 | 0.33098 | -5.0884 | -10.6374 | -16.6241 | 7.9391 | 7.0208 | 6.1493 | 5.0238 | 4.5126 | 2.6024 | 1.6759 | 0.82078 | 0.14322 | -1.2915
|  | LOCHSIDE | EE |  |  |  |  | 5.7887 | 4.8612 | 4.1704 | 3.5989 | 2.5714 | 1.3244 | 0.3622 | -0.2531 | -1.4276 | -2.3378 | -5.9143 | -10.4541 | -12.8792 | 8.8422 | 8.1085 | 7.6534 | 7.3606 | 6.633 | 5.5136 | 4.8432 | 4.3198 | 3.3259 | 2.63 | -0.20167 | -5.3231 | -8.1894 | 7.9687 | 7.184 | 6.6269 | 6.2055 | 5.2249 | 3.88 | 2.9055 | 2.3647 | 1.1402 | 0.232
|  | LOCHSIDE | HT |  |  |  |  | 5.7775 | 4.6949 | 3.7265 | 2.6326 | 2.0255 | 0.3571 | -0.62351 | -1.5378 | -2.2653 | -3.0674 | -6.7735 | -12.4858 | -17.3527 | 8.8147 | 7.9361 | 7.1606 | 6.2402 | 5.98 | 4.2147 | 3.4483 | 2.7902 | 2.3391 | 1.7993 | -1.2507 | -7.119 | -12.4343 | 7.9391 | 7.0208 | 6.1493 | 5.0238 | 4.5126 | 2.6024 | 1.6759 | 0.82078 | 0.14322 | -0.64045
|  | LOCHSIDE | HE |  |  |  |  | 5.8908 | 5.102 | 4.2428 | 3.3367 | 2.5744 | 0.97037 | 0.22853 | -0.83473 | -1.8296 | -3.1694 | -8.3317 | -13.9398 | -19.1241 | 8.8993 | 8.1922 | 7.3932 | 6.5412 | 6.0249 | 4.2983 | 3.633 | 2.631 | 1.7034 | 0.33098 | -5.0884 | -10.6374 | -16.6241 | 8.031 | 7.3055 | 6.4504 | 5.5106 | 4.8738 | 3.0442 | 2.2871 | 1.1963 | 0.17486 | -1.2915
|  | LOCHSIDE | CF |  |  |  |  | 6.1806 | 5.6408 | 5.4081 | 5.0459 | 4.5479 | 3.8663 | 3.3377 | 2.8836 | 2.3938 | 1.8142 | -0.51637 | -3.3174 | -6.1762 | 9.1585 | 8.6034 | 8.4249 | 8.1249 | 7.6902 | 7.0289 | 6.5871 | 6.2136 | 5.7575 | 5.2106 | 2.9167 | 0.832 | -2.1639 | 8.2983 | 7.7493 | 7.5636 | 7.2534 | 6.78 | 6.0667 | 5.5636 | 5.1034 | 4.5881 | 3.9728
| BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | NO | 1.073 | 3.5549 | 3.5355 | 3.5059 | 3.4885 | 3.4661 | 3.4345 | 3.3987 | 3.3763 | 3.3355 | 3.3038 | 3.1865 | 3.1161 | 2.6355 | 3.612 | 3.5977 | 3.5702 | 3.5579 | 3.5406 | 3.513 | 3.4814 | 3.4528 | 3.4181 | 3.3896 | 3.2845 | 3.4605 | 3.4319 | 3.5054 | 3.4788 | 3.4401 | 3.4176 | 3.3911 | 3.3513 | 3.3044 | 3.2758 | 3.2278 | 3.185
|  | LOGIE PERT | EE |  |  |  |  | 3.5549 | 3.5355 | 3.5059 | 3.4885 | 3.4661 | 3.4345 | 3.3987 | 3.3763 | 3.3355 | 3.3038 | 3.1916 | 3.1732 | 2.7212 | 3.612 | 3.5977 | 3.5702 | 3.5579 | 3.5406 | 3.513 | 3.4814 | 3.4528 | 3.4181 | 3.3896 | 3.3069 | 3.5227 | 3.5115 | 3.5054 | 3.4788 | 3.4401 | 3.4176 | 3.3911 | 3.3513 | 3.3044 | 3.2758 | 3.2278 | 3.185
|  | LOGIE PERT | HT |  |  |  |  | 3.564 | 3.5538 | 3.5355 | 3.5192 | 3.4957 | 3.4834 | 3.4579 | 3.4365 | 3.4069 | 3.3753 | 3.2232 | 3.1508 | 2.6743 | 3.6202 | 3.611 | 3.5947 | 3.5814 | 3.56 | 3.5498 | 3.5273 | 3.5028 | 3.4743 | 3.4447 | 3.3253 | 3.5054 | 3.4839 | 3.5156 | 3.4972 | 3.4717 | 3.4493 | 3.4176 | 3.3982 | 3.3635 | 3.3309 | 3.2931 | 3.2544
|  | LOGIE PERT | HE |  |  |  |  | 3.5651 | 3.5569 | 3.5375 | 3.5263 | 3.5028 | 3.4936 | 3.4661 | 3.4477 | 3.4192 | 3.3896 | 3.1865 | 3.1161 | 2.6355 | 3.6202 | 3.613 | 3.5967 | 3.5865 | 3.5661 | 3.5518 | 3.5253 | 3.4967 | 3.4661 | 3.4314 | 3.2845 | 3.4605 | 3.4319 | 3.5146 | 3.5023 | 3.4788 | 3.4615 | 3.4339 | 3.4197 | 3.385 | 3.3462 | 3.3013 | 3.2544
|  | LOGIE PERT | CF |  |  |  |  | 3.5702 | 3.5579 | 3.5487 | 3.5385 | 3.5212 | 3.5028 | 3.4967 | 3.4763 | 3.4651 | 3.4457 | 3.3559 | 3.2222 | 2.6814 | 3.6253 | 3.6151 | 3.6059 | 3.5967 | 3.5814 | 3.5651 | 3.5589 | 3.5396 | 3.5324 | 3.514 | 3.3998 | 3.5248 | 3.4513 | 3.5207 | 3.5054 | 3.4911 | 3.4737 | 3.4533 | 3.4319 | 3.4227 | 3.3952 | 3.3819 | 3.3574
| MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | NO | 5.323 | 10.3686 | 9.441 | 8.4635 | 7.3196 | 6.1543 | 4.9676 | 4.0278 | 3.142 | 2.4339 | 1.6033 | -1.462 | -2.7029 | -2.8488 | 12.689 | 12.0165 | 11.3053 | 10.4196 | 9.5135 | 8.588 | 8.0155 | 7.5022 | 7.0757 | 6.5951 | 4.8839 | 4.39 | 3.9716 | 11.9502 | 11.0808 | 10.1686 | 9.0849 | 7.9778 | 6.8502 | 6.0033 | 5.2104 | 4.6165 | 3.8798
|  | LONGHAUGH | EE |  |  |  |  | 10.3686 | 9.4614 | 8.5849 | 7.4849 | 6.3329 | 5.4727 | 4.3512 | 3.3522 | 2.4339 | 1.6033 | -1.4355 | -2.1998 | -2.3692 | 12.6971 | 12.0543 | 11.4145 | 10.5778 | 9.6941 | 9.0114 | 8.2563 | 7.6216 | 7.0757 | 6.5951 | 4.8839 | 4.39 | 3.9716 | 11.9645 | 11.1441 | 10.3318 | 9.3053 | 8.2247 | 7.3563 | 6.3267 | 5.4196 | 4.6165 | 3.8798
|  | LONGHAUGH | HT |  |  |  |  | 10.3859 | 9.441 | 8.4635 | 7.3196 | 6.1543 | 4.9676 | 4.0278 | 3.142 | 2.6329 | 1.8818 | -1.462 | -2.7029 | -2.8488 | 12.689 | 12.0165 | 11.3053 | 10.4196 | 9.5135 | 8.588 | 8.0155 | 7.5022 | 7.3012 | 6.9084 | 5.1227 | 4.4798 | 4.4033 | 11.9502 | 11.0808 | 10.1686 | 9.0849 | 7.9778 | 6.8502 | 6.0033 | 5.2104 | 4.7441 | 4.0788
|  | LONGHAUGH | HE |  |  |  |  | 10.5196 | 9.7849 | 9.0859 | 8.1982 | 7.2686 | 6.3624 | 5.442 | 4.6471 | 4.2135 | 3.5645 | 0.46755 | -1.1631 | -1.4855 | 12.8043 | 12.2288 | 11.6788 | 10.9553 | 10.19 | 9.4349 | 8.7696 | 8.2278 | 7.9941 | 7.5808 | 5.6941 | 4.7869 | 4.342 | 12.0808 | 11.3982 | 10.738 | 9.8961 | 9.0063 | 8.139 | 7.2839 | 6.5522 | 6.142 | 5.5573
|  | LONGHAUGH | CF |  |  |  |  | 10.9206 | 10.5298 | 10.1176 | 9.6798 | 9.1441 | 8.5624 | 8.0696 | 7.5216 | 7.0747 | 6.6135 | 4.2584 | 1.4594 | -0.43347 | 13.1369 | 12.8227 | 12.4829 | 12.1186 | 11.6665 | 11.1665 | 10.7563 | 10.3155 | 9.9573 | 9.59 | 7.7584 | 5.6767 | 4.1543 | 12.4798 | 12.1216 | 11.7318 | 11.3135 | 10.8073 | 10.2502 | 9.7859 | 9.2951 | 8.891 | 8.4778
| INVERNESS | LONGMAN DRIVE | MINIMUM HEADROOM | NH 67139 46770 | NO | NO | 3.852 | 9.4679 | 8.6146 | 7.5912 | 6.5353 | 5.3323 | 3.9538 | 2.5512 | 0.8478 | -0.6537 | -1.9786 | -9.6712 | -13.0519 | -15.1711 | 9.6302 | 9.0365 | 8.3094 | 7.5743 | 6.6582 | 5.5757 | 4.5017 | 3.2221 | 2.0715 | 0.86057 | -5.1982 | -7.45 | -8.4442 | 7.5483 | 6.7944 | 5.8873 | 4.9561 | 3.8769 | 2.6209 | 1.2692 | -0.36416 | -1.8165 | -3.1989
|  | LONGMAN DRIVE | EE |  |  |  |  | 9.4679 | 8.6146 | 7.5912 | 6.5353 | 5.3323 | 3.9538 | 2.5512 | 0.8478 | -0.6537 | -1.9783 | -6.1496 | -7.3117 | -8.8624 | 9.6302 | 9.0365 | 8.3094 | 7.5743 | 6.6582 | 5.5757 | 4.5017 | 3.2221 | 2.0715 | 1.07 | -2.162 | -2.7334 | -3.1219 | 7.5483 | 6.7944 | 5.8873 | 4.9561 | 3.8769 | 2.6209 | 1.2692 | -0.36416 | -1.8165 | -3.0921
|  | LONGMAN DRIVE | HT |  |  |  |  | 9.8727 | 9.2392 | 8.5467 | 7.7725 | 6.9886 | 5.8192 | 4.7596 | 3.4952 | 2.3589 | 1.1842 | -3.902 | -6.623 | -8.6788 | 9.9343 | 9.4863 | 8.982 | 8.4136 | 7.8837 | 6.9778 | 6.1956 | 5.2512 | 4.4005 | 3.5111 | -0.43955 | -2.2352 | -3.1666 | 7.9108 | 7.3539 | 6.729 | 6.0268 | 5.3451 | 4.2043 | 3.2362 | 2.1055 | 1.0787 | -0.054272
|  | LONGMAN DRIVE | HE |  |  |  |  | 9.7613 | 8.9851 | 8.1028 | 7.1139 | 6.0205 | 4.5903 | 3.1926 | 1.445 | -0.20663 | -1.9786 | -9.6712 | -13.0519 | -15.1711 | 9.8396 | 9.294 | 8.6315 | 7.8972 | 7.1157 | 5.9546 | 4.8752 | 3.5287 | 2.2529 | 0.86057 | -5.1982 | -7.45 | -8.4442 | 7.8076 | 7.1236 | 6.3226 | 5.422 | 4.4476 | 3.1117 | 1.8331 | 0.13641 | -1.4668 | -3.1989
|  | LONGMAN DRIVE | CF |  |  |  |  | 9.9849 | 9.5663 | 9.0785 | 8.4933 | 7.8511 | 7.0737 | 6.3234 | 5.3724 | 4.4658 | 3.4867 | -1.9907 | -6.6651 | -10.4216 | 10.006 | 9.7062 | 9.3576 | 8.9246 | 8.4546 | 7.8769 | 7.3402 | 6.6317 | 5.9297 | 5.167 | 0.95431 | -2.0315 | -3.9811 | 8.0035 | 7.6302 | 7.1955 | 6.6699 | 6.0873 | 5.3668 | 4.7006 | 3.8645 | 3.0558 | 2.1657
| ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 0.788 | 7.0561 | 6.7949 | 6.5235 | 6.2082 | 5.9153 | 5.5633 | 5.051 | 4.4796 | 4.2612 | 3.7898 | 1.802 | 0.58673 | 0.3949 | 6.4643 | 6.3867 | 6.302 | 6.1949 | 6.0224 | 5.8194 | 5.5367 | 5.2204 | 5.1408 | 4.8918 | 3.7816 | 3.0092 | 1.8714 | 5.4969 | 5.2673 | 5.0296 | 4.7561 | 4.4898 | 4.1827 | 3.7235 | 3.2173 | 3.0092 | 2.5898
|  | LOSSIEMOUTH | EE |  |  |  |  | 7.0561 | 6.7949 | 6.5235 | 6.2082 | 5.9153 | 5.5633 | 5.051 | 4.4796 | 4.2612 | 3.7898 | 1.802 | 0.66224 | 0.40408 | 6.4643 | 6.3867 | 6.302 | 6.1949 | 6.0224 | 5.8194 | 5.5367 | 5.2204 | 5.1408 | 4.8918 | 3.7816 | 3.0092 | 2.3184 | 5.4969 | 5.2673 | 5.0296 | 4.7561 | 4.4898 | 4.1827 | 3.7235 | 3.2173 | 3.0092 | 2.5898
|  | LOSSIEMOUTH | HT |  |  |  |  | 7.1306 | 6.8908 | 6.652 | 6.3776 | 6.1102 | 5.802 | 5.3327 | 4.8714 | 4.3816 | 3.8786 | 1.8316 | 0.58673 | 0.3949 | 6.5112 | 6.4531 | 6.3949 | 6.3204 | 6.2153 | 6.052 | 5.8235 | 5.5959 | 5.35 | 5.0949 | 4.1429 | 3.5643 | 3.4735 | 5.5653 | 5.352 | 5.1398 | 4.8969 | 4.6643 | 4.3898 | 3.9704 | 3.5531 | 3.1112 | 2.6602
|  | LOSSIEMOUTH | HE |  |  |  |  | 7.1214 | 6.9653 | 6.8041 | 6.6092 | 6.4194 | 6.1888 | 5.8439 | 5.5071 | 5.1367 | 4.7582 | 2.9571 | 1.6418 | 1.1847 | 6.5 | 6.4388 | 6.3796 | 6.3041 | 6.2245 | 6.1286 | 5.9398 | 5.7408 | 5.5184 | 5.2888 | 4.2122 | 3.3041 | 2.551 | 5.5571 | 5.4204 | 5.2765 | 5.1082 | 4.9418 | 4.7378 | 4.4327 | 4.1276 | 3.7969 | 3.4561
|  | LOSSIEMOUTH | CF |  |  |  |  | 7.1857 | 7.0857 | 6.9857 | 6.8612 | 6.7102 | 6.5939 | 6.4286 | 6.2306 | 6.101 | 5.9082 | 4.5571 | 3.5469 | 2.3541 | 6.5214 | 6.4806 | 6.4378 | 6.3867 | 6.3286 | 6.2735 | 6.202 | 6.0765 | 5.9643 | 5.8214 | 4.7939 | 3.6704 | 1.8714 | 5.5888 | 5.5296 | 5.4418 | 5.3347 | 5.2163 | 5.1133 | 4.9816 | 4.8214 | 4.6969 | 4.5418
| BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 1.072 | -0.46259 | -0.48708 | -0.52687 | -0.5534 | -0.5932 | -0.62483 | -0.67789 | -0.73606 | -0.76565 | -0.80953 | -0.90953 | -0.94524 | -0.95442 | -0.31055 | -0.32585 | -0.35136 | -0.36973 | -0.39728 | -0.41667 | -0.45238 | -0.49218 | -0.50953 | -0.5381 | -0.60953 | -0.63606 | -0.7534 | -0.40953 | -0.433 | -0.47177 | -0.49524 | -0.53504 | -0.56361 | -0.61463 | -0.67177 | -0.6983 | -0.73912
|  | LOWER OLLACH | EE |  |  |  |  | -0.46259 | -0.48708 | -0.52687 | -0.5534 | -0.5932 | -0.62483 | -0.67789 | -0.73606 | -0.76565 | -0.80953 | -0.90953 | -0.92177 | -0.93198 | -0.31055 | -0.32585 | -0.35136 | -0.36973 | -0.39728 | -0.41667 | -0.45238 | -0.49218 | -0.50953 | -0.5381 | -0.60953 | -0.63606 | -0.68708 | -0.40953 | -0.433 | -0.47177 | -0.49524 | -0.53504 | -0.56361 | -0.61463 | -0.67177 | -0.6983 | -0.73912
|  | LOWER OLLACH | HT |  |  |  |  | -0.4483 | -0.46667 | -0.49728 | -0.52279 | -0.55953 | -0.57993 | -0.61769 | -0.65238 | -0.69218 | -0.73402 | -0.88402 | -0.94524 | -0.95442 | -0.29932 | -0.30851 | -0.32789 | -0.3432 | -0.36565 | -0.37687 | -0.4034 | -0.42381 | -0.44932 | -0.47687 | -0.57687 | -0.61361 | -0.61871 | -0.39524 | -0.41463 | -0.44218 | -0.46565 | -0.50136 | -0.52075 | -0.55647 | -0.58606 | -0.62585 | -0.66667
|  | LOWER OLLACH | HE |  |  |  |  | -0.4483 | -0.46565 | -0.4881 | -0.50749 | -0.53708 | -0.5483 | -0.58708 | -0.61565 | -0.64932 | -0.68912 | -0.85851 | -0.89422 | -0.89932 | -0.29932 | -0.30851 | -0.32585 | -0.33912 | -0.35851 | -0.36667 | -0.39218 | -0.41157 | -0.43606 | -0.46259 | -0.57687 | -0.61565 | -0.66055 | -0.39626 | -0.41361 | -0.43402 | -0.45238 | -0.48198 | -0.49116 | -0.52891 | -0.55442 | -0.5881 | -0.62585
|  | LOWER OLLACH | CF |  |  |  |  | -0.4432 | -0.46055 | -0.47789 | -0.49422 | -0.51871 | -0.5432 | -0.55238 | -0.583 | -0.60953 | -0.62483 | -0.74116 | -0.84626 | -0.89932 | -0.29422 | -0.30647 | -0.31871 | -0.32993 | -0.34524 | -0.36361 | -0.37075 | -0.3932 | -0.41055 | -0.42177 | -0.51565 | -0.63198 | -0.7534 | -0.39116 | -0.40749 | -0.42381 | -0.44014 | -0.46157 | -0.48606 | -0.49524 | -0.52381 | -0.55034 | -0.56361
| KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0 | 0.20029 | 0.20029 | 0.19212 | 0.1911 | 0.19008 | 0.18192 | 0.17988 | 0.17069 | 0.17069 | 0.16967 | 0.16967 | 0.17069 | 0.15269 | 0.19249 | 0.19249 | 0.18433 | 0.18433 | 0.18331 | 0.17514 | 0.17412 | 0.16494 | 0.16494 | 0.16392 | 0.16392 | 0.177 | 0.17496 | 0.19231 | 0.19231 | 0.18312 | 0.1821 | 0.18108 | 0.17292 | 0.1719 | 0.16169 | 0.16169 | 0.16067
|  | LUBNAIG | EE |  |  |  |  | 0.20029 | 0.20029 | 0.19212 | 0.1911 | 0.19008 | 0.18192 | 0.17988 | 0.17069 | 0.17069 | 0.16967 | 0.17171 | 0.17069 | 0.15269 | 0.19249 | 0.19249 | 0.18433 | 0.18433 | 0.18331 | 0.17514 | 0.17412 | 0.16494 | 0.16494 | 0.16392 | 0.16902 | 0.177 | 0.177 | 0.19231 | 0.19231 | 0.18312 | 0.1821 | 0.18108 | 0.17292 | 0.1719 | 0.16169 | 0.16169 | 0.16067
|  | LUBNAIG | HT |  |  |  |  | 0.20029 | 0.20029 | 0.20029 | 0.1911 | 0.1911 | 0.19008 | 0.19008 | 0.1809 | 0.17886 | 0.17784 | 0.17171 | 0.17069 | 0.15269 | 0.19351 | 0.19249 | 0.19249 | 0.18433 | 0.18433 | 0.18331 | 0.18331 | 0.17412 | 0.1731 | 0.17208 | 0.16902 | 0.177 | 0.177 | 0.19231 | 0.19231 | 0.19231 | 0.1821 | 0.1821 | 0.18108 | 0.18108 | 0.1719 | 0.17088 | 0.16884
|  | LUBNAIG | HE |  |  |  |  | 0.20029 | 0.20029 | 0.20029 | 0.19212 | 0.1911 | 0.19008 | 0.18906 | 0.17988 | 0.17886 | 0.17784 | 0.17273 | 0.17273 | 0.15371 | 0.19249 | 0.19249 | 0.19249 | 0.18433 | 0.18433 | 0.18331 | 0.18229 | 0.17412 | 0.1731 | 0.17208 | 0.17004 | 0.17904 | 0.17802 | 0.19231 | 0.19231 | 0.19231 | 0.18312 | 0.1821 | 0.18108 | 0.18006 | 0.1719 | 0.16986 | 0.16884
|  | LUBNAIG | CF |  |  |  |  | 0.20029 | 0.20029 | 0.20029 | 0.19314 | 0.19212 | 0.19212 | 0.1911 | 0.19008 | 0.19008 | 0.18192 | 0.16967 | 0.17171 | 0.15269 | 0.19351 | 0.19249 | 0.19249 | 0.18535 | 0.18433 | 0.18433 | 0.18433 | 0.18331 | 0.18331 | 0.17514 | 0.16392 | 0.17904 | 0.17496 | 0.19231 | 0.19231 | 0.19231 | 0.18516 | 0.18312 | 0.18312 | 0.1821 | 0.18108 | 0.18108 | 0.17292
| LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | YES | 0.934 | 7.5755 | 7.3969 | 7.0673 | 6.5969 | 6.4296 | 5.4847 | 5.0071 | 4.4571 | 3.952 | 3.3337 | -0.23673 | -3.7939 | -7.5622 | 9.1602 | 9.0122 | 8.6765 | 8.149 | 7.9898 | 6.8959 | 6.4857 | 5.9755 | 5.4592 | 4.65 | 1.252 | -2.1944 | -5.724 | 8.5056 | 8.2577 | 7.8423 | 7.223 | 6.975 | 5.7913 | 5.3709 | 4.8046 | 4.177 | 3.2485
|  | LUNANHEAD | EE |  |  |  |  | 7.5755 | 7.3969 | 7.2286 | 7.0347 | 6.6653 | 6.0194 | 5.3888 | 4.8449 | 4.4051 | 3.8194 | 1.3143 | -2.0827 | -4.0418 | 9.1602 | 9.0122 | 8.8582 | 8.6776 | 8.2459 | 7.5633 | 7.1153 | 6.7959 | 6.35 | 5.948 | 4.1878 | 1.1617 | -0.55969 | 8.5056 | 8.2577 | 7.9985 | 7.7209 | 7.2015 | 6.423 | 5.8311 | 5.3566 | 4.7913 | 4.2485
|  | LUNANHEAD | HT |  |  |  |  | 7.5857 | 7.4449 | 7.0673 | 6.5969 | 6.4296 | 5.4847 | 5.0071 | 4.4571 | 3.952 | 3.3337 | 0.75918 | -3.1684 | -6.6224 | 9.1837 | 9.0745 | 8.6765 | 8.149 | 7.9898 | 6.8959 | 6.6112 | 6.2653 | 5.9898 | 5.6133 | 3.55 | -0.13929 | -3.4342 | 8.5464 | 8.3454 | 7.8423 | 7.223 | 6.975 | 5.7913 | 5.3709 | 4.874 | 4.4128 | 3.8372
|  | LUNANHEAD | HE |  |  |  |  | 7.6235 | 7.5122 | 7.2092 | 6.7959 | 6.5643 | 5.701 | 5.3276 | 4.8827 | 4.2827 | 3.4367 | -0.23673 | -3.7939 | -7.5622 | 9.2153 | 9.102 | 8.752 | 8.2622 | 7.9898 | 6.9224 | 6.4857 | 5.9755 | 5.4592 | 4.65 | 1.252 | -2.1944 | -5.724 | 8.5781 | 8.4056 | 7.9903 | 7.4342 | 7.0974 | 5.9628 | 5.426 | 4.8046 | 4.177 | 3.2485
|  | LUNANHEAD | CF |  |  |  |  | 7.7857 | 7.6918 | 7.6041 | 7.5133 | 7.3092 | 6.9745 | 6.7449 | 6.5316 | 6.3398 | 6.0786 | 4.6224 | 2.902 | 0.75816 | 9.3796 | 9.2939 | 9.2071 | 9.1194 | 8.8776 | 8.4827 | 8.2194 | 7.9704 | 7.7296 | 7.4112 | 6.101 | 5.1423 | 3.475 | 8.7638 | 8.6403 | 8.5199 | 8.3893 | 8.1097 | 7.6668 | 7.3526 | 7.0454 | 6.7556 | 6.3903
| PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0 | 0.089429 | 0.089429 | 0.080245 | 0.073102 | 0.070041 | 0.06902 | 0.071061 | 0.06698 | 0.06698 | 0.063918 | 0.064939 | 0.063918 | 0.054918 | 0.089612 | 0.089612 | 0.081449 | 0.074306 | 0.075327 | 0.073286 | 0.073286 | 0.074306 | 0.074306 | 0.072265 | 0.073286 | 0.076765 | 0.076765 | 0.091051 | 0.091051 | 0.082888 | 0.075745 | 0.071663 | 0.070643 | 0.072684 | 0.069622 | 0.070643 | 0.066561
|  | LUSSAGIVEN | EE |  |  |  |  | 0.089429 | 0.089429 | 0.080245 | 0.073102 | 0.070041 | 0.06902 | 0.071061 | 0.070041 | 0.06698 | 0.063918 | 0.064939 | 0.063918 | 0.054918 | 0.089612 | 0.089612 | 0.081449 | 0.074306 | 0.075327 | 0.074306 | 0.077367 | 0.077367 | 0.075327 | 0.072265 | 0.073286 | 0.076765 | 0.076765 | 0.091051 | 0.091051 | 0.082888 | 0.075745 | 0.071663 | 0.070643 | 0.072684 | 0.072684 | 0.070643 | 0.066561
|  | LUSSAGIVEN | HT |  |  |  |  | 0.096571 | 0.089429 | 0.087388 | 0.087388 | 0.080245 | 0.071061 | 0.071061 | 0.06698 | 0.073102 | 0.068 | 0.06698 | 0.063918 | 0.054918 | 0.096755 | 0.089612 | 0.088592 | 0.088592 | 0.081449 | 0.073286 | 0.073286 | 0.074306 | 0.079408 | 0.076347 | 0.075327 | 0.076765 | 0.076765 | 0.098194 | 0.091051 | 0.090031 | 0.090031 | 0.082888 | 0.072684 | 0.072684 | 0.069622 | 0.075745 | 0.070643
|  | LUSSAGIVEN | HE |  |  |  |  | 0.096571 | 0.089429 | 0.089429 | 0.087388 | 0.080245 | 0.080245 | 0.072082 | 0.06902 | 0.075143 | 0.06902 | 0.064939 | 0.063918 | 0.054918 | 0.096755 | 0.089612 | 0.089612 | 0.088592 | 0.081449 | 0.081449 | 0.073286 | 0.074306 | 0.079408 | 0.077367 | 0.074306 | 0.076765 | 0.076765 | 0.098194 | 0.091051 | 0.091051 | 0.090031 | 0.082888 | 0.082888 | 0.074724 | 0.070643 | 0.076765 | 0.071663
|  | LUSSAGIVEN | CF |  |  |  |  | 0.096571 | 0.089429 | 0.089429 | 0.089429 | 0.082286 | 0.080245 | 0.080245 | 0.073102 | 0.073102 | 0.070041 | 0.070041 | 0.06698 | 0.055939 | 0.096755 | 0.089612 | 0.089612 | 0.089612 | 0.082469 | 0.081449 | 0.081449 | 0.074306 | 0.074306 | 0.075327 | 0.077367 | 0.078806 | 0.077786 | 0.098194 | 0.091051 | 0.091051 | 0.091051 | 0.083908 | 0.082888 | 0.082888 | 0.075745 | 0.075745 | 0.071663
| LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | YES | 2.897 | 7.9053 | 7.79 | 7.6951 | 7.5931 | 7.4808 | 7.3696 | 7.1757 | 6.9471 | 6.7614 | 6.5573 | 5.8206 | 5.69 | 4.9329 | 8.4737 | 8.3492 | 8.2502 | 8.139 | 8.0176 | 7.9145 | 7.7849 | 7.6431 | 7.5339 | 7.4165 | 6.9033 | 6.9874 | 5.5946 | 8.2252 | 8.1119 | 8.0201 | 7.9232 | 7.813 | 7.7221 | 7.5374 | 7.3334 | 7.164 | 6.9874
|  | LYNDHURST | EE |  |  |  |  | 7.938 | 7.8043 | 7.6982 | 7.5931 | 7.4808 | 7.3696 | 7.1757 | 6.9471 | 6.7614 | 6.5573 | 5.8206 | 5.9318 | 5.2043 | 8.5114 | 8.3624 | 8.2502 | 8.139 | 8.0176 | 7.9145 | 7.7849 | 7.6431 | 7.5339 | 7.4165 | 6.9033 | 7.0619 | 6.516 | 8.2558 | 8.1262 | 8.0242 | 7.9232 | 7.813 | 7.7221 | 7.5374 | 7.3334 | 7.164 | 6.9874
|  | LYNDHURST | HT |  |  |  |  | 7.9053 | 7.79 | 7.6951 | 7.6084 | 7.5196 | 7.438 | 7.2767 | 7.0931 | 6.9012 | 6.7053 | 5.84 | 5.69 | 4.9329 | 8.4737 | 8.3492 | 8.2502 | 8.1604 | 8.0757 | 7.9941 | 7.8971 | 7.8084 | 7.7124 | 7.6124 | 7.1492 | 7.4252 | 7.4068 | 8.2252 | 8.1119 | 8.0201 | 7.9374 | 7.8548 | 7.7762 | 7.6293 | 7.465 | 7.2946 | 7.1211
|  | LYNDHURST | HE |  |  |  |  | 7.9624 | 7.8502 | 7.7635 | 7.6839 | 7.6022 | 7.5237 | 7.4227 | 7.2767 | 7.1308 | 6.9818 | 6.2073 | 5.9329 | 5.1298 | 8.5339 | 8.4104 | 8.3216 | 8.24 | 8.1584 | 8.0778 | 7.9767 | 7.8829 | 7.7829 | 7.6798 | 7.1512 | 7.1599 | 6.6415 | 8.2803 | 8.1701 | 8.0874 | 8.0079 | 7.9313 | 7.8538 | 7.767 | 7.6834 | 7.5936 | 7.4507
|  | LYNDHURST | CF |  |  |  |  | 8.1247 | 8.0502 | 7.9808 | 7.9257 | 7.8594 | 7.8063 | 7.7461 | 7.6798 | 7.6206 | 7.5573 | 7.0104 | 6.4124 | 5.1727 | 8.7033 | 8.6165 | 8.54 | 8.4788 | 8.4043 | 8.3369 | 8.2645 | 8.1788 | 8.1043 | 8.0237 | 7.4982 | 6.9874 | 5.5946 | 8.4405 | 8.366 | 8.2997 | 8.2426 | 8.1803 | 8.1262 | 8.067 | 8.0028 | 7.9456 | 7.8813
| THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | NO | 0.005 | 0.21837 | 0.20408 | 0.19082 | 0.17551 | 0.16327 | 0.13878 | 0.11735 | 0.076531 | 0.040816 | 0.038776 | -0.046939 | -0.084694 | -0.09898 | 0.55918 | 0.5449 | 0.52959 | 0.50612 | 0.49796 | 0.47551 | 0.45816 | 0.42653 | 0.39898 | 0.39898 | 0.34286 | 0.31429 | 0.24082 | 0.13265 | 0.11735 | 0.10306 | 0.084694 | 0.070408 | 0.04898 | 0.028571 | -0.0020408 | -0.030612 | -0.047959
|  | LYNESS | EE |  |  |  |  | 0.21837 | 0.20408 | 0.19082 | 0.17551 | 0.16327 | 0.13878 | 0.11735 | 0.076531 | 0.040816 | 0.038776 | -0.046939 | -0.067347 | -0.067347 | 0.55918 | 0.5449 | 0.52959 | 0.50612 | 0.49796 | 0.47551 | 0.45816 | 0.42653 | 0.39898 | 0.39898 | 0.34286 | 0.31429 | 0.27959 | 0.13265 | 0.11735 | 0.10306 | 0.084694 | 0.070408 | 0.04898 | 0.028571 | -0.0020408 | -0.030612 | -0.047959
|  | LYNESS | HT |  |  |  |  | 0.22245 | 0.21224 | 0.20204 | 0.18878 | 0.17755 | 0.16224 | 0.1449 | 0.11735 | 0.10102 | 0.077551 | -0.029592 | -0.078571 | -0.092857 | 0.56633 | 0.56122 | 0.54898 | 0.53673 | 0.52551 | 0.50918 | 0.50102 | 0.48061 | 0.47143 | 0.44796 | 0.37245 | 0.3398 | 0.33571 | 0.13469 | 0.12449 | 0.11122 | 0.09898 | 0.084694 | 0.068367 | 0.053061 | 0.027551 | 0.010204 | -0.014286
|  | LYNESS | HE |  |  |  |  | 0.22245 | 0.21327 | 0.2051 | 0.19388 | 0.18367 | 0.17041 | 0.15918 | 0.13776 | 0.11939 | 0.097959 | -0.044898 | -0.084694 | -0.09898 | 0.56633 | 0.56122 | 0.55 | 0.53673 | 0.52857 | 0.51327 | 0.50816 | 0.48571 | 0.46531 | 0.45714 | 0.36939 | 0.33265 | 0.3 | 0.13469 | 0.12449 | 0.11531 | 0.10714 | 0.094898 | 0.081633 | 0.069388 | 0.05 | 0.02551 | 0.011224
|  | LYNESS | CF |  |  |  |  | 0.22449 | 0.21735 | 0.21122 | 0.20204 | 0.1949 | 0.18776 | 0.17653 | 0.16735 | 0.15714 | 0.1449 | 0.067347 | -0.022449 | -0.085714 | 0.57143 | 0.56224 | 0.55918 | 0.54898 | 0.53776 | 0.52857 | 0.51633 | 0.51327 | 0.5 | 0.48878 | 0.41122 | 0.32959 | 0.24082 | 0.13673 | 0.12959 | 0.12347 | 0.11224 | 0.10306 | 0.094898 | 0.084694 | 0.07449 | 0.063265 | 0.05
| STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0.012 | 0.16049 | 0.15131 | 0.1411 | 0.14008 | 0.13906 | 0.13702 | 0.13192 | 0.12988 | 0.11967 | 0.11967 | 0.10743 | 0.10335 | 0.084327 | 0.16596 | 0.1578 | 0.14861 | 0.15473 | 0.14657 | 0.14759 | 0.15269 | 0.15371 | 0.14759 | 0.14759 | 0.14045 | 0.14435 | 0.13516 | 0.16884 | 0.15965 | 0.14945 | 0.14843 | 0.14741 | 0.14537 | 0.14027 | 0.13822 | 0.12904 | 0.13108
|  | MAARUIG | EE |  |  |  |  | 0.16049 | 0.15131 | 0.1411 | 0.14008 | 0.1411 | 0.14008 | 0.13192 | 0.12988 | 0.11967 | 0.11967 | 0.10743 | 0.10335 | 0.086367 | 0.16596 | 0.1578 | 0.14861 | 0.15984 | 0.16086 | 0.15984 | 0.15269 | 0.15371 | 0.14759 | 0.14759 | 0.14045 | 0.14435 | 0.13822 | 0.16884 | 0.15965 | 0.14945 | 0.14843 | 0.14945 | 0.14741 | 0.14027 | 0.13822 | 0.12904 | 0.13108
|  | MAARUIG | HT |  |  |  |  | 0.16151 | 0.15845 | 0.15029 | 0.14722 | 0.13906 | 0.13702 | 0.14212 | 0.13804 | 0.12988 | 0.12988 | 0.11049 | 0.10437 | 0.084327 | 0.16596 | 0.16494 | 0.15678 | 0.15576 | 0.14759 | 0.1578 | 0.16188 | 0.15984 | 0.15576 | 0.15269 | 0.14147 | 0.14639 | 0.14537 | 0.16884 | 0.1668 | 0.15965 | 0.15659 | 0.14741 | 0.14537 | 0.14945 | 0.14537 | 0.14129 | 0.14129
|  | MAARUIG | HE |  |  |  |  | 0.16151 | 0.15845 | 0.15029 | 0.14824 | 0.14008 | 0.14008 | 0.14518 | 0.13906 | 0.136 | 0.1309 | 0.11457 | 0.10641 | 0.088408 | 0.16596 | 0.16494 | 0.15678 | 0.15473 | 0.14657 | 0.15984 | 0.16188 | 0.15984 | 0.15576 | 0.15371 | 0.14045 | 0.14537 | 0.14027 | 0.16884 | 0.1668 | 0.15761 | 0.15659 | 0.14741 | 0.14843 | 0.15353 | 0.14741 | 0.14435 | 0.13822
|  | MAARUIG | CF |  |  |  |  | 0.16151 | 0.16049 | 0.15845 | 0.15131 | 0.14212 | 0.1411 | 0.1411 | 0.14518 | 0.14212 | 0.14008 | 0.12682 | 0.11559 | 0.091469 | 0.16596 | 0.16596 | 0.16494 | 0.1578 | 0.14861 | 0.14759 | 0.16086 | 0.1629 | 0.16086 | 0.16086 | 0.14861 | 0.14537 | 0.13516 | 0.16884 | 0.16884 | 0.1668 | 0.15965 | 0.15047 | 0.14945 | 0.14945 | 0.15353 | 0.15047 | 0.14843
| LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | YES | 1.201 | 13.0786 | 12.8051 | 12.498 | 12.1929 | 11.8439 | 11.4235 | 11.1612 | 10.5878 | 10.0224 | 9.4918 | 7.7 | 7.3133 | 7.2837 | 14.7888 | 14.6806 | 14.5449 | 14.3929 | 14.2061 | 13.9429 | 13.8429 | 13.5051 | 13.1561 | 12.8337 | 11.6092 | 11.048 | 8.2878 | 14.0204 | 13.7908 | 13.4765 | 13.1908 | 12.85 | 12.4622 | 12.249 | 11.7204 | 11.1969 | 10.7153
|  | MACALPINE ROAD | EE |  |  |  |  | 13.0786 | 12.8051 | 12.498 | 12.1929 | 11.8439 | 11.4235 | 11.1704 | 10.5878 | 10.0224 | 9.4918 | 7.7 | 7.799 | 7.8092 | 14.7888 | 14.6806 | 14.5449 | 14.3929 | 14.2061 | 13.9429 | 13.8429 | 13.5051 | 13.1561 | 12.8337 | 11.6092 | 11.048 | 9.9735 | 14.0204 | 13.7908 | 13.4765 | 13.1908 | 12.85 | 12.4622 | 12.249 | 11.7204 | 11.1969 | 10.7153
|  | MACALPINE ROAD | HT |  |  |  |  | 13.1286 | 12.8714 | 12.5867 | 12.3214 | 12.0214 | 11.6806 | 11.1612 | 10.6092 | 10.0633 | 9.7918 | 7.7643 | 7.3133 | 7.2837 | 14.8204 | 14.7265 | 14.6245 | 14.5194 | 14.3704 | 14.1959 | 13.9592 | 13.7041 | 13.4071 | 13.3571 | 12.2286 | 11.8969 | 11.8571 | 14.0531 | 13.8612 | 13.6112 | 13.3592 | 13.0704 | 12.7551 | 12.2786 | 11.7684 | 11.2653 | 11.0765
|  | MACALPINE ROAD | HE |  |  |  |  | 13.151 | 13.0153 | 12.8622 | 12.7214 | 12.5541 | 12.3633 | 11.9724 | 11.5347 | 11.0888 | 10.9531 | 9.2306 | 8.3602 | 8.2918 | 14.8286 | 14.7459 | 14.6653 | 14.5867 | 14.4908 | 14.3602 | 14.1837 | 13.9449 | 13.6643 | 13.6347 | 12.349 | 11.3857 | 10.2765 | 14.0622 | 13.9837 | 13.85 | 13.7061 | 13.5224 | 13.3418 | 12.9745 | 12.5633 | 12.1571 | 12.0724
|  | MACALPINE ROAD | CF |  |  |  |  | 13.2398 | 13.1837 | 13.1112 | 13.048 | 12.9735 | 12.8745 | 12.7694 | 12.5949 | 12.4061 | 12.2092 | 11.2908 | 9.7184 | 8.4255 | 14.8735 | 14.8286 | 14.7776 | 14.7316 | 14.6755 | 14.599 | 14.5071 | 14.3673 | 14.2204 | 14.0327 | 13.0673 | 11.1082 | 8.2878 | 14.1082 | 14.0653 | 14.0173 | 13.9745 | 13.9204 | 13.8031 | 13.6949 | 13.5235 | 13.3602 | 13.1765
| MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | NO | 1.226 | 13.4331 | 12.7556 | 12.0842 | 11.3872 | 10.6607 | 9.8413 | 8.7342 | 7.525 | 6.5117 | 5.0158 | 1.228 | -0.54849 | -2.0607 | 15.5872 | 15.1495 | 14.725 | 14.2862 | 13.7811 | 13.176 | 12.5036 | 11.7525 | 11.1433 | 10.2036 | 8.0321 | 7.6127 | 6.7107 | 14.6505 | 14.0025 | 13.3566 | 12.6862 | 12.0168 | 11.2536 | 10.2678 | 9.1933 | 8.2791 | 6.9597
|  | MACDUFF | EE |  |  |  |  | 13.4801 | 12.828 | 12.2138 | 11.5025 | 10.7525 | 9.9484 | 9.2025 | 8.1209 | 7.0199 | 5.8454 | 1.3209 | -0.37502 | -1.9658 | 15.674 | 15.2556 | 14.8882 | 14.378 | 13.8393 | 13.2444 | 12.7791 | 12.0821 | 11.3811 | 10.6138 | 8.0321 | 7.6127 | 6.7107 | 14.6689 | 14.0464 | 13.4556 | 12.7984 | 12.1036 | 11.3536 | 10.6923 | 9.7087 | 8.7138 | 7.6587
|  | MACDUFF | HT |  |  |  |  | 13.4331 | 12.7556 | 12.0842 | 11.3872 | 10.6607 | 9.8413 | 8.7342 | 7.525 | 6.5117 | 5.0158 | 1.228 | -0.54849 | -2.0607 | 15.5872 | 15.1495 | 14.725 | 14.2862 | 13.7811 | 13.176 | 12.5036 | 11.7525 | 11.1433 | 10.2036 | 8.3862 | 8.2495 | 8.1158 | 14.6505 | 14.0025 | 13.3566 | 12.6862 | 12.0168 | 11.2536 | 10.2678 | 9.1933 | 8.2791 | 6.9597
|  | MACDUFF | HE |  |  |  |  | 13.5393 | 13.0444 | 12.5933 | 12.0933 | 11.578 | 10.9852 | 10.1974 | 9.3556 | 8.7821 | 7.8801 | 4.027 | 1.8668 | -0.23727 | 15.7025 | 15.3127 | 14.9811 | 14.6117 | 14.2352 | 13.7801 | 13.1964 | 12.6025 | 12.1903 | 11.5372 | 9.1811 | 8.525 | 7.4576 | 14.7525 | 14.2719 | 13.8301 | 13.3403 | 12.8505 | 12.2944 | 11.5658 | 10.8005 | 10.2638 | 9.4454
|  | MACDUFF | CF |  |  |  |  | 13.7964 | 13.5046 | 13.2148 | 12.9454 | 12.6229 | 12.2576 | 11.8974 | 11.4617 | 11.0311 | 10.5454 | 7.8546 | 4.7066 | 1.6015 | 15.928 | 15.7046 | 15.4852 | 15.2893 | 15.0525 | 14.7576 | 14.4423 | 14.0597 | 13.6882 | 13.2699 | 11.0729 | 9.0342 | 6.7648 | 15.0025 | 14.7199 | 14.427 | 14.1689 | 13.8474 | 13.4913 | 13.1546 | 12.7464 | 12.3484 | 11.8954
| CARRADALE 1 | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 0.035 | 1.3459 | 1.601 | 1.5673 | 1.5235 | 1.4663 | 1.4214 | 1.3541 | 1.2827 | 1.2082 | 1.1449 | 1.0316 | 0.99082 | 0.45765 | 2.2276 | 2.198 | 2.1714 | 2.1439 | 2.1041 | 2.0735 | 2.0296 | 1.9786 | 1.9296 | 1.8837 | 1.8041 | 1.3518 | 1.6469 | 1.9806 | 1.9367 | 1.9071 | 1.8633 | 1.8082 | 1.7704 | 1.7061 | 1.6367 | 1.5622 | 1.501
|  | MACHRIE | EE |  |  |  |  | 1.3459 | 1.601 | 1.5673 | 1.5235 | 1.4663 | 1.4214 | 1.3541 | 1.2827 | 1.2082 | 1.1449 | 1.0316 | 1.0143 | 0.47398 | 2.2276 | 2.198 | 2.1714 | 2.1439 | 2.1041 | 2.0735 | 2.0296 | 1.9786 | 1.9296 | 1.8837 | 1.8041 | 1.3518 | 1.702 | 1.9806 | 1.9367 | 1.9071 | 1.8633 | 1.8082 | 1.7704 | 1.7061 | 1.6367 | 1.5622 | 1.501
|  | MACHRIE | HT |  |  |  |  | 1.3643 | 1.6357 | 1.6041 | 1.5724 | 1.5276 | 1.4878 | 1.4347 | 1.3735 | 1.3388 | 1.2776 | 1.0429 | 0.99082 | 0.45765 | 2.2418 | 2.2235 | 2.2041 | 2.1847 | 2.1571 | 2.1306 | 2.0959 | 2.0551 | 2.0367 | 1.9969 | 1.8306 | 1.3885 | 1.7959 | 2.002 | 1.9745 | 1.9429 | 1.9184 | 1.8745 | 1.8408 | 1.7867 | 1.7276 | 1.699 | 1.6429
|  | MACHRIE | HE |  |  |  |  | 1.3653 | 1.6398 | 1.6153 | 1.5918 | 1.5531 | 1.5184 | 1.4735 | 1.4194 | 1.3878 | 1.3378 | 1.0908 | 1.0724 | 0.54031 | 2.2408 | 2.2265 | 2.2061 | 2.1918 | 2.1653 | 2.1408 | 2.1102 | 2.0704 | 2.0561 | 2.0184 | 1.8429 | 1.3957 | 1.7531 | 2.0031 | 1.9776 | 1.952 | 1.9316 | 1.8949 | 1.8663 | 1.8194 | 1.7663 | 1.7418 | 1.6939
|  | MACHRIE | CF |  |  |  |  | 1.3704 | 1.652 | 1.6306 | 1.6 | 1.5806 | 1.549 | 1.5235 | 1.4847 | 1.449 | 1.4296 | 1.249 | 1.1327 | 0.54439 | 2.2459 | 2.2347 | 2.2184 | 2.1969 | 2.1837 | 2.1622 | 2.1429 | 2.1143 | 2.0867 | 2.0724 | 1.9245 | 1.3793 | 1.6469 | 2.0082 | 1.9898 | 1.9673 | 1.9347 | 1.9204 | 1.8867 | 1.8643 | 1.8255 | 1.7867 | 1.7745
| FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | NO | 0.131 | 0.61643 | 0.57051 | 0.53786 | 0.49704 | 0.44194 | 0.38276 | 0.33684 | 0.22867 | 0.12051 | 0.021531 | -0.13561 | -0.25398 | -0.30704 | 1.0205 | 0.99194 | 0.96847 | 0.93888 | 0.90112 | 0.85827 | 0.83071 | 0.76337 | 0.695 | 0.63786 | 0.51745 | 0.4399 | 0.22255 | 0.72051 | 0.67867 | 0.64194 | 0.60214 | 0.54908 | 0.49602 | 0.4501 | 0.35316 | 0.25316 | 0.16235
|  | MALLAIG | EE |  |  |  |  | 0.61643 | 0.57051 | 0.53786 | 0.49704 | 0.44194 | 0.38276 | 0.33684 | 0.22867 | 0.12051 | 0.021531 | -0.13561 | -0.16622 | -0.18867 | 1.0205 | 0.99194 | 0.96847 | 0.93888 | 0.90112 | 0.85827 | 0.83071 | 0.76337 | 0.695 | 0.63786 | 0.51745 | 0.46235 | 0.37765 | 0.72051 | 0.67867 | 0.64194 | 0.60214 | 0.54908 | 0.49602 | 0.4501 | 0.35316 | 0.25316 | 0.16235
|  | MALLAIG | HT |  |  |  |  | 0.6348 | 0.60827 | 0.57153 | 0.545 | 0.50214 | 0.42969 | 0.34194 | 0.24296 | 0.20724 | 0.1501 | -0.095816 | -0.20296 | -0.21929 | 1.0368 | 1.0215 | 0.99602 | 0.98173 | 0.95418 | 0.91643 | 0.86541 | 0.80827 | 0.78786 | 0.75112 | 0.58071 | 0.51133 | 0.49908 | 0.73582 | 0.70929 | 0.67459 | 0.64806 | 0.60929 | 0.54398 | 0.46745 | 0.37867 | 0.34704 | 0.29194
|  | MALLAIG | HE |  |  |  |  | 0.63276 | 0.61031 | 0.58173 | 0.55622 | 0.51847 | 0.47969 | 0.42663 | 0.34602 | 0.27765 | 0.19908 | -0.13561 | -0.25398 | -0.2601 | 1.0348 | 1.0195 | 1.0001 | 0.98378 | 0.95827 | 0.93582 | 0.90418 | 0.84908 | 0.81439 | 0.76439 | 0.54704 | 0.45418 | 0.37867 | 0.73378 | 0.71235 | 0.6848 | 0.66133 | 0.62867 | 0.6001 | 0.55214 | 0.47561 | 0.42153 | 0.345
|  | MALLAIG | CF |  |  |  |  | 0.64092 | 0.62051 | 0.59908 | 0.56847 | 0.55214 | 0.52051 | 0.48684 | 0.45827 | 0.39908 | 0.33378 | 0.10724 | -0.12745 | -0.30704 | 1.0409 | 1.0277 | 1.0134 | 0.98888 | 0.97561 | 0.95622 | 0.92561 | 0.9052 | 0.86439 | 0.82051 | 0.64704 | 0.4399 | 0.22255 | 0.74194 | 0.72459 | 0.70418 | 0.67663 | 0.65827 | 0.62969 | 0.59806 | 0.56949 | 0.51439 | 0.45622
| KEITH 1 | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 0.787 | 2.6408 | 2.5031 | 2.3408 | 2.1561 | 1.9776 | 1.7776 | 1.5367 | 1.3163 | 1.0786 | 0.84898 | 0.22245 | 0.065306 | 0.0030612 | 4.048 | 3.9643 | 3.8571 | 3.7286 | 3.6163 | 3.4776 | 3.3163 | 3.1847 | 3.0224 | 2.8765 | 2.5031 | 2.3684 | 1.9367 | 2.8918 | 2.7878 | 2.6531 | 2.4908 | 2.3602 | 2.1776 | 1.9531 | 1.7592 | 1.5357 | 1.3286
|  | MARNOCH | EE |  |  |  |  | 2.6408 | 2.5031 | 2.3408 | 2.1561 | 1.9776 | 1.7776 | 1.5367 | 1.3163 | 1.0786 | 0.84898 | 0.22245 | 0.13163 | 0.091837 | 4.048 | 3.9643 | 3.8571 | 3.7286 | 3.6163 | 3.4776 | 3.3163 | 3.1847 | 3.0224 | 2.8765 | 2.5031 | 2.3684 | 2.1612 | 2.8918 | 2.7878 | 2.6531 | 2.4908 | 2.3602 | 2.1776 | 1.9531 | 1.7592 | 1.5357 | 1.3286
|  | MARNOCH | HT |  |  |  |  | 2.6673 | 2.5316 | 2.3837 | 2.2143 | 2.0255 | 1.851 | 1.6816 | 1.4684 | 1.251 | 0.99082 | 0.37041 | 0.065306 | 0.0030612 | 4.0867 | 4.0092 | 3.9184 | 3.8255 | 3.7112 | 3.6 | 3.5153 | 3.3867 | 3.2571 | 3.1061 | 2.6755 | 2.5082 | 2.4816 | 2.949 | 2.8582 | 2.7306 | 2.5837 | 2.4214 | 2.2714 | 2.1235 | 1.9469 | 1.7704 | 1.5439
|  | MARNOCH | HE |  |  |  |  | 2.6745 | 2.5694 | 2.4592 | 2.3378 | 2.1949 | 2.0459 | 1.899 | 1.7 | 1.5122 | 1.3194 | 0.43367 | 0.22653 | 0.18469 | 4.0878 | 4.0224 | 3.9459 | 3.8714 | 3.7724 | 3.6684 | 3.5827 | 3.4571 | 3.3378 | 3.2071 | 2.652 | 2.4449 | 2.249 | 2.951 | 2.8724 | 2.7816 | 2.6939 | 2.5673 | 2.4398 | 2.3071 | 2.1439 | 1.9714 | 1.7949
|  | MARNOCH | CF |  |  |  |  | 2.6929 | 2.6173 | 2.5276 | 2.4316 | 2.3408 | 2.2408 | 2.1296 | 2.0061 | 1.9051 | 1.7684 | 1.0714 | 0.57347 | 0.26837 | 4.1051 | 4.0561 | 3.999 | 3.9276 | 3.8704 | 3.8031 | 3.7194 | 3.6194 | 3.5622 | 3.4622 | 2.95 | 2.4173 | 1.9367 | 2.9755 | 2.9214 | 2.8561 | 2.7765 | 2.6959 | 2.6082 | 2.5143 | 2.402 | 2.3214 | 2.1929
| BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | NO | 1.01 | 2.9241 | 2.8853 | 2.8384 | 2.7782 | 2.7394 | 2.6782 | 2.6078 | 2.4914 | 2.4169 | 2.2965 | 2.12 | 2.0578 | 1.6641 | 3.1824 | 3.16 | 3.1324 | 3.1008 | 3.0794 | 3.0437 | 3.0039 | 2.9222 | 2.8753 | 2.8049 | 2.6835 | 2.8073 | 2.588 | 3.0971 | 3.0563 | 3.0094 | 2.9482 | 2.9084 | 2.8441 | 2.7716 | 2.6461 | 2.5665 | 2.4594
|  | MARYBANK | EE |  |  |  |  | 2.9241 | 2.8853 | 2.8384 | 2.7782 | 2.7394 | 2.6782 | 2.6078 | 2.4914 | 2.4169 | 2.2965 | 2.12 | 2.0812 | 1.6978 | 3.1824 | 3.16 | 3.1324 | 3.1008 | 3.0794 | 3.0437 | 3.0039 | 2.9222 | 2.8753 | 2.8049 | 2.6835 | 2.8073 | 2.7073 | 3.0971 | 3.0563 | 3.0094 | 2.9482 | 2.9084 | 2.8441 | 2.7716 | 2.6461 | 2.5665 | 2.4594
|  | MARYBANK | HT |  |  |  |  | 2.9527 | 2.9169 | 2.8822 | 2.8353 | 2.7986 | 2.7139 | 2.6476 | 2.5384 | 2.4853 | 2.422 | 2.1771 | 2.0578 | 1.6641 | 3.1947 | 3.1794 | 3.159 | 3.1345 | 3.1161 | 3.0671 | 3.0243 | 2.9651 | 2.9365 | 2.9008 | 2.7437 | 2.8512 | 2.8318 | 3.1278 | 3.092 | 3.0573 | 3.0104 | 2.9716 | 2.8849 | 2.8165 | 2.7104 | 2.6573 | 2.591
|  | MARYBANK | HE |  |  |  |  | 2.9506 | 2.9231 | 2.8955 | 2.8588 | 2.8302 | 2.7863 | 2.7333 | 2.6792 | 2.6108 | 2.5353 | 2.2108 | 2.1322 | 1.758 | 3.1937 | 3.1814 | 3.1631 | 3.1437 | 3.1253 | 3.1008 | 3.0702 | 3.0376 | 2.9927 | 2.9457 | 2.7406 | 2.84 | 2.7543 | 3.1257 | 3.1002 | 3.0716 | 3.0318 | 3.0033 | 2.9573 | 2.9022 | 2.8451 | 2.7747 | 2.6961
|  | MARYBANK | CF |  |  |  |  | 2.9608 | 2.9373 | 2.9047 | 2.8894 | 2.8567 | 2.8322 | 2.7976 | 2.7547 | 2.722 | 2.6649 | 2.3843 | 2.218 | 1.7447 | 3.1988 | 3.1876 | 3.1661 | 3.1549 | 3.1355 | 3.1192 | 3.0978 | 3.0661 | 3.0437 | 3.0059 | 2.8161 | 2.8186 | 2.588 | 3.1349 | 3.1073 | 3.0747 | 3.0543 | 3.0186 | 2.9951 | 2.9563 | 2.9084 | 2.8757 | 2.8135
| LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | YES | 1.117 | 7.3398 | 7.0143 | 6.4418 | 5.5602 | 5.0133 | 3.551 | 2.9765 | 2.3459 | 1.8 | 1.1796 | -2.9214 | -7.802 | -12.6051 | 9.2551 | 9.0847 | 8.6092 | 7.7714 | 7.3459 | 5.7888 | 5.4367 | 4.8827 | 4.2776 | 3.2867 | -0.7602 | -5.673 | -10.8046 | 8.5179 | 8.223 | 7.6423 | 6.6699 | 6.1046 | 4.3964 | 3.8495 | 3.2372 | 2.7179 | 1.6781
|  | MARYTON | EE |  |  |  |  | 7.3398 | 7.0143 | 6.6439 | 6.2 | 5.4245 | 4.4122 | 3.5878 | 3.2857 | 2.4214 | 1.7653 | -1.1418 | -5.7071 | -8.0918 | 9.2551 | 9.0847 | 8.8612 | 8.5684 | 7.8551 | 6.8663 | 6.2255 | 6.1133 | 5.3847 | 4.8929 | 2.6449 | -1.8954 | -4.2434 | 8.5179 | 8.223 | 7.874 | 7.4393 | 6.5781 | 5.4362 | 4.5913 | 4.3393 | 3.4209 | 2.7536
|  | MARYTON | HT |  |  |  |  | 7.4112 | 7.0867 | 6.4418 | 5.5602 | 5.0133 | 3.551 | 2.9765 | 2.3459 | 1.8 | 1.1796 | -1.9224 | -7.1143 | -11.4786 | 9.3184 | 9.1653 | 8.6092 | 7.7714 | 7.3459 | 5.7888 | 5.4367 | 5.0439 | 4.7429 | 4.35 | 1.998 | -3.0495 | -7.3679 | 8.6097 | 8.3281 | 7.6423 | 6.6699 | 6.1046 | 4.3964 | 3.8495 | 3.2372 | 2.7179 | 2.1056
|  | MARYTON | HE |  |  |  |  | 7.4133 | 7.2031 | 6.7204 | 6.0306 | 5.5071 | 4.1816 | 3.5551 | 2.8827 | 2.2102 | 1.2408 | -2.9214 | -7.802 | -12.6051 | 9.3133 | 9.198 | 8.7459 | 8.0398 | 7.5327 | 6.0418 | 5.4816 | 4.8827 | 4.2776 | 3.2867 | -0.7602 | -5.673 | -10.8046 | 8.6128 | 8.4219 | 7.8903 | 7.1066 | 6.5189 | 4.9362 | 4.2587 | 3.5189 | 2.7832 | 1.6781
|  | MARYTON | CF |  |  |  |  | 7.4745 | 7.3245 | 7.1612 | 6.95 | 6.5939 | 6.0592 | 5.699 | 5.398 | 5.0786 | 4.6929 | 3.2429 | 1.2898 | -1.1378 | 9.3439 | 9.2541 | 9.1531 | 9.0031 | 8.6459 | 8.0714 | 7.699 | 7.3939 | 7.0653 | 6.6714 | 5.2245 | 3.573 | 1.3923 | 8.6699 | 8.5342 | 8.3811 | 8.1709 | 7.774 | 7.1505 | 6.7362 | 6.3995 | 6.0403 | 5.6199
| STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | YES | 0.319 | 4.8447 | 4.7192 | 4.5508 | 4.3692 | 4.1998 | 3.9998 | 3.7661 | 3.5131 | 3.2233 | 2.8794 | 2.0294 | 1.8712 | 1.4059 | 5.9478 | 5.8784 | 5.7804 | 5.6651 | 5.5733 | 5.4376 | 5.2804 | 5.1324 | 4.9508 | 4.7682 | 4.3018 | 4.36 | 3.8437 | 5.4488 | 5.3335 | 5.1794 | 5.01 | 4.8631 | 4.6722 | 4.4498 | 4.2182 | 3.958 | 3.6753
|  | MAUD | EE |  |  |  |  | 4.8447 | 4.7192 | 4.5508 | 4.3692 | 4.1998 | 3.9998 | 3.7661 | 3.5131 | 3.2233 | 2.911 | 2.0294 | 1.9355 | 1.5018 | 5.9478 | 5.8784 | 5.7804 | 5.6651 | 5.5733 | 5.4376 | 5.2804 | 5.1324 | 4.9508 | 4.7682 | 4.3018 | 4.362 | 4.1498 | 5.4488 | 5.3335 | 5.1794 | 5.01 | 4.8631 | 4.6722 | 4.4498 | 4.2182 | 3.958 | 3.6753
|  | MAUD | HT |  |  |  |  | 4.8784 | 4.7498 | 4.5927 | 4.4447 | 4.2998 | 4.1151 | 3.8733 | 3.5927 | 3.2386 | 2.8794 | 2.1631 | 1.8712 | 1.4059 | 5.9814 | 5.9243 | 5.8396 | 5.7712 | 5.6927 | 5.5804 | 5.46 | 5.2947 | 5.1059 | 4.909 | 4.4671 | 4.51 | 4.4824 | 5.4845 | 5.3763 | 5.2335 | 5.1059 | 4.9743 | 4.8049 | 4.6029 | 4.3549 | 4.0539 | 3.7457
|  | MAUD | HE |  |  |  |  | 4.8763 | 4.7988 | 4.6784 | 4.5733 | 4.4447 | 4.2722 | 4.1284 | 3.8865 | 3.6253 | 3.3345 | 2.208 | 1.9886 | 1.5406 | 5.9794 | 5.9376 | 5.8631 | 5.8059 | 5.7263 | 5.6161 | 5.5284 | 5.3692 | 5.211 | 5.0386 | 4.4039 | 4.3865 | 4.1753 | 5.4835 | 5.4131 | 5.3018 | 5.2069 | 5.0927 | 4.9355 | 4.809 | 4.5947 | 4.362 | 4.1059
|  | MAUD | CF |  |  |  |  | 4.8896 | 4.8151 | 4.7314 | 4.6427 | 4.5314 | 4.3978 | 4.2518 | 4.1529 | 4.011 | 3.8457 | 2.8478 | 2.3539 | 1.6294 | 5.9886 | 5.9427 | 5.8927 | 5.8478 | 5.7763 | 5.6906 | 5.5906 | 5.5171 | 5.4141 | 5.2978 | 4.6794 | 4.36 | 3.8437 | 5.4967 | 5.4273 | 5.3539 | 5.2763 | 5.1743 | 5.0569 | 4.9212 | 4.8345 | 4.7069 | 4.558
| DOUNREAY | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | NO | 0.87 | -0.20823 | -0.24191 | -0.2715 | -0.31844 | -0.35517 | -0.40415 | -0.46231 | -0.50415 | -0.56436 | -0.60925 | -0.73272 | -0.78884 | -0.79497 | 0.081563 | 0.064216 | 0.049931 | 0.021359 | 0.0019714 | -0.029661 | -0.069457 | -0.093947 | -0.13578 | -0.16027 | -0.27354 | -0.32864 | -0.41129 | -0.067416 | -0.099049 | -0.12864 | -0.16946 | -0.20517 | -0.25313 | -0.30925 | -0.34599 | -0.40517 | -0.44599
|  | MELVICH | EE |  |  |  |  | -0.20823 | -0.24191 | -0.2715 | -0.31844 | -0.35517 | -0.40415 | -0.46231 | -0.50415 | -0.56436 | -0.60925 | -0.73272 | -0.75007 | -0.76027 | 0.081563 | 0.064216 | 0.049931 | 0.021359 | 0.0019714 | -0.029661 | -0.069457 | -0.093947 | -0.13578 | -0.16027 | -0.24293 | -0.27558 | -0.32864 | -0.067416 | -0.099049 | -0.12864 | -0.16946 | -0.20517 | -0.25313 | -0.30925 | -0.34599 | -0.40517 | -0.44599
|  | MELVICH | HT |  |  |  |  | -0.19293 | -0.21742 | -0.25007 | -0.28374 | -0.30721 | -0.34599 | -0.39191 | -0.42966 | -0.47762 | -0.52966 | -0.69191 | -0.7715 | -0.78068 | 0.091767 | 0.078502 | 0.064216 | 0.04789 | 0.034624 | 0.012176 | -0.012314 | -0.034763 | -0.066396 | -0.098029 | -0.20109 | -0.24701 | -0.25415 | -0.053131 | -0.07558 | -0.10721 | -0.1368 | -0.15925 | -0.19599 | -0.23987 | -0.27456 | -0.32048 | -0.36742
|  | MELVICH | HE |  |  |  |  | -0.19395 | -0.21231 | -0.23987 | -0.26436 | -0.28374 | -0.31946 | -0.35721 | -0.38782 | -0.43476 | -0.47864 | -0.71333 | -0.78884 | -0.79395 | 0.086665 | 0.07238 | 0.055033 | 0.038706 | 0.021359 | -6.9388e-05 | -0.02558 | -0.059253 | -0.090886 | -0.12252 | -0.27354 | -0.32864 | -0.3317 | -0.054151 | -0.072518 | -0.097008 | -0.1215 | -0.13884 | -0.17048 | -0.20721 | -0.24803 | -0.29599 | -0.33987
|  | MELVICH | CF |  |  |  |  | -0.18884 | -0.20517 | -0.2266 | -0.24701 | -0.27456 | -0.28987 | -0.3164 | -0.35007 | -0.36844 | -0.40007 | -0.5368 | -0.6868 | -0.79497 | 0.093808 | 0.082584 | 0.070339 | 0.057073 | 0.041767 | 0.029522 | 0.014216 | -0.0082327 | -0.022518 | -0.043947 | -0.16538 | -0.27456 | -0.41129 | -0.049049 | -0.063335 | -0.084763 | -0.10211 | -0.12966 | -0.14293 | -0.16844 | -0.20211 | -0.21844 | -0.24803
| CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | YES | 2.08 | 10.0232 | 9.563 | 9.0252 | 8.4008 | 7.8018 | 7.2038 | 6.5079 | 5.7426 | 5.2038 | 4.5742 | 2.5028 | 2.0181 | 0.58647 | 9.5018 | 9.1946 | 8.8303 | 8.3967 | 8.0069 | 7.6079 | 7.1242 | 6.5681 | 6.2079 | 5.7814 | 4.4048 | 4.2023 | 1.7727 | 11.6074 | 11.1706 | 10.6962 | 10.1288 | 9.6094 | 9.0584 | 8.4145 | 7.6951 | 7.4206 | 6.8625
|  | MENZIESHILL | EE |  |  |  |  | 10.0232 | 9.563 | 9.0252 | 8.4008 | 7.8018 | 7.2038 | 6.5079 | 5.7426 | 5.2038 | 4.5742 | 2.5028 | 2.6946 | 1.7293 | 9.5018 | 9.1946 | 8.8303 | 8.3967 | 8.0069 | 7.6079 | 7.1242 | 6.5681 | 6.2079 | 5.7814 | 4.4548 | 4.6594 | 3.489 | 11.6074 | 11.1706 | 10.6962 | 10.1288 | 9.6094 | 9.0584 | 8.4145 | 7.6951 | 7.4206 | 6.8625
|  | MENZIESHILL | HT |  |  |  |  | 10.1405 | 9.7048 | 9.1987 | 8.6252 | 8.1048 | 7.5936 | 7.0222 | 6.3814 | 5.7508 | 5.1008 | 2.665 | 2.0181 | 0.70993 | 9.5854 | 9.312 | 8.9589 | 8.5671 | 8.2548 | 7.9426 | 7.615 | 7.1752 | 6.7548 | 6.3089 | 4.6293 | 4.5788 | 4.3053 | 11.7339 | 11.3298 | 10.8686 | 10.3513 | 9.9155 | 9.4676 | 8.9849 | 8.4206 | 7.8564 | 7.2737
|  | MENZIESHILL | HE |  |  |  |  | 10.163 | 9.8559 | 9.4446 | 8.9742 | 8.5375 | 8.0916 | 7.5365 | 6.9059 | 6.3028 | 5.6712 | 3.165 | 2.061 | 0.58647 | 9.5875 | 9.365 | 9.0803 | 8.7528 | 8.4008 | 8.0426 | 7.6691 | 7.2181 | 6.764 | 6.2803 | 4.4048 | 4.2023 | 3.8309 | 11.7502 | 11.4727 | 11.1349 | 10.7492 | 10.4268 | 10.0809 | 9.6727 | 9.1727 | 8.5635 | 7.9186
|  | MENZIESHILL | CF |  |  |  |  | 10.2375 | 10.1038 | 9.9497 | 9.7181 | 9.4712 | 9.2048 | 8.9191 | 8.5865 | 8.2875 | 7.9661 | 6.0252 | 3.7814 | 1.1089 | 9.6293 | 9.511 | 9.3518 | 9.1548 | 8.9732 | 8.7559 | 8.5273 | 8.2885 | 8.0518 | 7.8018 | 6.2436 | 4.7635 | 1.7727 | 11.8155 | 11.6798 | 11.5155 | 11.2951 | 11.0982 | 10.8655 | 10.6227 | 10.386 | 10.1431 | 9.8829
| KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 0.241 | 4.8941 | 4.8349 | 4.7737 | 4.6971 | 4.6063 | 4.5124 | 4.44 | 4.3114 | 4.189 | 4.1033 | 3.7482 | 3.6135 | 3.5267 | 6.4084 | 6.3584 | 6.3094 | 6.2492 | 6.1747 | 6.0971 | 6.042 | 5.9359 | 5.8359 | 5.7951 | 5.5941 | 5.5247 | 5.2522 | 5.0716 | 4.9941 | 4.9186 | 4.8278 | 4.7196 | 4.6094 | 4.5155 | 4.3594 | 4.2114 | 4.1298
|  | METHLICK | EE |  |  |  |  | 4.8941 | 4.8349 | 4.7737 | 4.6971 | 4.6063 | 4.5124 | 4.44 | 4.3114 | 4.189 | 4.1033 | 3.7482 | 3.6757 | 3.6655 | 6.4084 | 6.3584 | 6.3094 | 6.2492 | 6.1747 | 6.0971 | 6.042 | 5.9359 | 5.8359 | 5.7951 | 5.5941 | 5.5247 | 5.439 | 5.0716 | 4.9941 | 4.9186 | 4.8278 | 4.7196 | 4.6094 | 4.5155 | 4.3594 | 4.2114 | 4.1298
|  | METHLICK | HT |  |  |  |  | 4.9349 | 4.891 | 4.84 | 4.7767 | 4.7318 | 4.6614 | 4.5839 | 4.4778 | 4.3655 | 4.2461 | 3.8278 | 3.6227 | 3.5655 | 6.439 | 6.4012 | 6.3594 | 6.3063 | 6.2686 | 6.2104 | 6.1461 | 6.0614 | 6.0145 | 5.9369 | 5.6747 | 5.5706 | 5.5471 | 5.1084 | 5.0461 | 4.9778 | 4.8951 | 4.8318 | 4.7431 | 4.6441 | 4.5206 | 4.4329 | 4.3124
|  | METHLICK | HE |  |  |  |  | 4.9339 | 4.8961 | 4.8522 | 4.7951 | 4.7563 | 4.6931 | 4.6196 | 4.5257 | 4.4676 | 4.3431 | 3.789 | 3.6135 | 3.5267 | 6.438 | 6.4073 | 6.3676 | 6.3206 | 6.289 | 6.238 | 6.1818 | 6.1012 | 6.0614 | 5.9788 | 5.6614 | 5.542 | 5.4492 | 5.1084 | 5.0604 | 5.0053 | 4.938 | 4.89 | 4.8176 | 4.7318 | 4.6176 | 4.54 | 4.4227
|  | METHLICK | CF |  |  |  |  | 4.9431 | 4.9135 | 4.8686 | 4.8349 | 4.7859 | 4.7584 | 4.7084 | 4.6441 | 4.5808 | 4.5553 | 4.2124 | 3.8737 | 3.6359 | 6.4461 | 6.4196 | 6.3788 | 6.3471 | 6.3043 | 6.2808 | 6.241 | 6.1839 | 6.1288 | 6.1073 | 5.7982 | 5.5522 | 5.2522 | 5.1186 | 5.0798 | 5.0216 | 4.9757 | 4.9145 | 4.8808 | 4.8237 | 4.7492 | 4.6767 | 4.64
| SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | 0.007 | 0.039796 | 0.0061224 | -0.02449 | -0.066327 | -0.1 | -0.14592 | -0.20306 | -0.24184 | -0.29898 | -0.34286 | -0.45816 | -0.49592 | -0.50714 | 0.35408 | 0.33367 | 0.31633 | 0.29388 | 0.27551 | 0.25102 | 0.22041 | 0.1949 | 0.16429 | 0.14082 | 0.067347 | 0.041837 | -0.021429 | 0.20204 | 0.17755 | 0.15612 | 0.12449 | 0.09898 | 0.066327 | 0.022449 | -0.013265 | -0.066327 | -0.10408
|  | MID YELL | EE |  |  |  |  | 0.039796 | 0.0061224 | -0.02449 | -0.066327 | -0.1 | -0.14592 | -0.20306 | -0.24184 | -0.29898 | -0.34286 | -0.45816 | -0.47653 | -0.48571 | 0.35408 | 0.33367 | 0.31633 | 0.29388 | 0.27551 | 0.25102 | 0.22041 | 0.1949 | 0.16429 | 0.14082 | 0.067347 | 0.041837 | 0.0061224 | 0.20204 | 0.17755 | 0.15612 | 0.12449 | 0.09898 | 0.066327 | 0.022449 | -0.013265 | -0.066327 | -0.10408
|  | MID YELL | HT |  |  |  |  | 0.04898 | 0.02551 | 0.0010204 | -0.034694 | -0.056122 | -0.093878 | -0.12755 | -0.17347 | -0.21837 | -0.26633 | -0.42245 | -0.49592 | -0.50714 | 0.36122 | 0.35 | 0.33673 | 0.31735 | 0.30714 | 0.28571 | 0.26939 | 0.24388 | 0.21939 | 0.19184 | 0.10204 | 0.063265 | 0.056122 | 0.20918 | 0.18776 | 0.16837 | 0.14388 | 0.12551 | 0.096939 | 0.070408 | 0.035714 | 0.0020408 | -0.036735
|  | MID YELL | HE |  |  |  |  | 0.05 | 0.033673 | 0.014286 | -0.014286 | -0.033673 | -0.061224 | -0.10102 | -0.12959 | -0.17143 | -0.21327 | -0.39286 | -0.44082 | -0.44796 | 0.36224 | 0.35 | 0.34082 | 0.32449 | 0.31327 | 0.29694 | 0.27551 | 0.25714 | 0.23367 | 0.21224 | 0.1051 | 0.064286 | 0.029592 | 0.2102 | 0.19388 | 0.17857 | 0.15816 | 0.14184 | 0.12245 | 0.095918 | 0.071429 | 0.041837 | 0.011224
|  | MID YELL | CF |  |  |  |  | 0.053061 | 0.037755 | 0.021429 | 0.0030612 | -0.019388 | -0.032653 | -0.058163 | -0.088776 | -0.10714 | -0.13367 | -0.25714 | -0.37449 | -0.43673 | 0.36531 | 0.35408 | 0.34184 | 0.33367 | 0.32143 | 0.3102 | 0.2949 | 0.27653 | 0.26633 | 0.24796 | 0.16735 | 0.068367 | -0.021429 | 0.21122 | 0.19796 | 0.18265 | 0.16837 | 0.15204 | 0.1398 | 0.12041 | 0.097959 | 0.084694 | 0.064286
| KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 0.445 | 3.1306 | 2.9857 | 2.8398 | 4.1222 | 3.9243 | 3.7692 | 3.559 | 3.3518 | 3.1937 | 3.0202 | 2.5498 | 2.3988 | 0.43061 | 3.6765 | 3.6092 | 5.4498 | 5.358 | 5.2518 | 5.159 | 5.0478 | 4.9253 | 4.8253 | 4.7294 | 4.4069 | 2.577 | 2.2454 | 3.3832 | 4.9427 | 4.8151 | 4.66 | 4.4784 | 4.3498 | 4.1549 | 3.9559 | 3.8222 | 3.66
|  | MIDMAR | EE |  |  |  |  | 3.1306 | 2.9857 | 2.8398 | 4.1222 | 3.9243 | 3.7692 | 3.559 | 3.3518 | 3.1937 | 3.0202 | 2.5498 | 2.4651 | 0.52551 | 3.6765 | 3.6092 | 5.4498 | 5.358 | 5.2518 | 5.159 | 5.0478 | 4.9253 | 4.8253 | 4.7294 | 4.4478 | 2.6464 | 2.4801 | 3.3832 | 4.9427 | 4.8151 | 4.66 | 4.4784 | 4.3498 | 4.1549 | 3.9559 | 3.8222 | 3.66
|  | MIDMAR | HT |  |  |  |  | 3.1653 | 3.0173 | 2.8602 | 4.159 | 3.9927 | 3.8365 | 3.6886 | 3.5508 | 3.3988 | 3.2406 | 2.6692 | 2.3988 | 0.43061 | 3.7133 | 3.651 | 5.4896 | 5.411 | 5.3212 | 5.2386 | 5.1529 | 5.0661 | 4.9763 | 4.8794 | 4.5008 | 2.6628 | 2.6005 | 3.4291 | 4.9906 | 4.859 | 4.7273 | 4.5835 | 4.4488 | 4.308 | 4.1957 | 4.0529 | 3.9039
|  | MIDMAR | HE |  |  |  |  | 3.1643 | 3.0592 | 2.9449 | 4.2814 | 4.1273 | 3.9896 | 3.8396 | 3.7243 | 3.5865 | 3.4447 | 2.708 | 2.5151 | 0.51327 | 3.7112 | 3.6602 | 5.5049 | 5.4345 | 5.3457 | 5.259 | 5.1641 | 5.0733 | 4.9753 | 4.8753 | 4.4069 | 2.577 | 2.5015 | 3.427 | 5.0202 | 4.9192 | 4.8192 | 4.6824 | 4.561 | 4.4202 | 4.3253 | 4.1978 | 4.0631
|  | MIDMAR | CF |  |  |  |  | 3.1796 | 3.0939 | 3.0163 | 4.3712 | 4.2763 | 4.1498 | 4.0447 | 3.9314 | 3.8549 | 3.7518 | 3.2692 | 2.8284 | 0.62959 | 3.7184 | 3.6806 | 5.5508 | 5.4967 | 5.4539 | 5.3927 | 5.3365 | 5.261 | 5.209 | 5.1396 | 4.7733 | 2.6628 | 2.2454 | 3.4444 | 5.0539 | 4.9845 | 4.8886 | 4.811 | 4.6988 | 4.6049 | 4.4947 | 4.4355 | 4.3396
| BRIDGE OF DUN | MILL RD | MINIMUM HEADROOM | NO 71317 57683 | NO | NO | 0 | 5.1888 | 5.0143 | 4.1347 | 2.8714 | 2.6582 | -0.02551 | -0.86327 | -1.8612 | -2.8837 | -4.6837 | -12.7204 | -22.9592 | -32.7255 | 7.3439 | 7.2296 | 6.2082 | 4.7347 | 4.4765 | 1.298 | 0.32653 | -0.7449 | -1.8571 | -3.9327 | -12.8622 | -24.5946 | -36.3273 | 6.587 | 6.3686 | 5.3043 | 3.7258 | 3.4717 | 0.14515 | -0.74362 | -1.9334 | -3.1304 | -5.3171
|  | MILL RD | EE |  |  |  |  | 5.1888 | 5.0143 | 4.8092 | 4.5939 | 3.7184 | 2.2 | 1.3061 | 0.74694 | -0.57755 | -1.4857 | -6.102 | -15.5949 | -19.8245 | 7.3439 | 7.2296 | 7.0878 | 6.9378 | 5.9765 | 4.1806 | 3.2969 | 2.9184 | 1.5776 | 0.74388 | -3.5306 | -14.2712 | -19.2212 | 6.587 | 6.3686 | 6.1054 | 5.8472 | 4.7513 | 2.8523 | 1.8094 | 1.2676 | -0.22832 | -1.213
|  | MILL RD | HT |  |  |  |  | 5.2286 | 5.0704 | 4.1347 | 2.8714 | 2.6582 | -0.02551 | -0.52041 | -1.2204 | -1.7316 | -2.4816 | -7.951 | -18.8735 | -28.0327 | 7.3755 | 7.2735 | 6.2082 | 4.7347 | 4.5898 | 1.3571 | 0.92959 | 0.42857 | 0.13469 | -0.45918 | -5.55 | -17.7946 | -28.4089 | 6.6656 | 6.4676 | 5.3043 | 3.7258 | 3.4717 | 0.14515 | -0.50281 | -1.2293 | -1.713 | -2.4946
|  | MILL RD | HE |  |  |  |  | 5.2296 | 5.099 | 4.3378 | 3.2184 | 2.6582 | 0.039796 | -0.86327 | -1.8612 | -2.8837 | -4.6837 | -12.7204 | -22.9592 | -32.7255 | 7.3765 | 7.2857 | 6.4041 | 5.0827 | 4.4765 | 1.298 | 0.32653 | -0.7449 | -1.8571 | -3.9327 | -12.8622 | -24.5946 | -36.3273 | 6.6645 | 6.5268 | 5.5972 | 4.2258 | 3.5656 | 0.3523 | -0.74362 | -1.9334 | -3.1304 | -5.3171
|  | MILL RD | CF |  |  |  |  | 5.2837 | 5.2214 | 5.1469 | 5.0694 | 4.5714 | 3.6867 | 3.1765 | 2.749 | 2.3 | 1.7041 | -0.6 | -3.1153 | -5.9816 | 7.4133 | 7.3684 | 7.3153 | 7.2561 | 6.6776 | 5.6255 | 5.0398 | 4.5796 | 4.0898 | 3.4051 | 0.87449 | -1.8967 | -5.1212 | 6.7196 | 6.6401 | 6.5401 | 6.4503 | 5.838 | 4.7411 | 4.1329 | 3.6278 | 3.1023 | 2.4043
| ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 6.312 | -1.166 | 21.3105 | 20.0044 | 18.6044 | 16.8268 | 14.6023 | 12.5279 | 10.3044 | 7.833 | 5.536 | -5.815 | -12.616 | -41.013 | 25.4044 | 24.7911 | 23.7421 | 22.6187 | 21.0687 | 18.9758 | 17.3421 | 15.5136 | 13.685 | 11.3972 | 1.1391 | -28.3676 | -9.6507 | 24.4095 | 23.4003 | 22.1074 | 20.6707 | 18.7881 | 16.4993 | 14.4513 | 12.3177 | 9.8523 | 7.5972
|  | MILNATHORT | EE |  |  |  |  | -1.166 | 21.3105 | 20.0044 | 18.6044 | 16.8268 | 14.6023 | 12.5279 | 10.3044 | 7.833 | 5.536 | -3.8477 | -11.5854 | -38.3966 | 25.4044 | 24.7911 | 23.7421 | 22.6187 | 21.0687 | 19.1268 | 17.4707 | 15.7921 | 13.7707 | 11.9666 | 4.5156 | -25.5941 | -4.5926 | 24.4095 | 23.4003 | 22.1074 | 20.6707 | 18.7881 | 16.4993 | 14.4513 | 12.3177 | 9.8523 | 7.5972
|  | MILNATHORT | HT |  |  |  |  | -0.62724 | 22.0728 | 20.7462 | 19.3003 | 18.2626 | 15.9442 | 14.2646 | 12.4268 | 10.635 | 8.6881 | -0.21602 | -8.6028 | -38.0068 | 25.6983 | 25.1615 | 24.137 | 22.8983 | 22.0809 | 19.7513 | 18.3615 | 16.9279 | 15.5881 | 14.0972 | 6.9483 | -23.8982 | -5.866 | 24.7677 | 23.9962 | 22.7177 | 21.2554 | 20.2228 | 17.6207 | 15.8972 | 14.1003 | 12.3779 | 10.483
|  | MILNATHORT | HE |  |  |  |  | -0.73439 | 21.8758 | 20.5819 | 19.0503 | 17.6809 | 15.1911 | 13.2217 | 11.0074 | 8.8013 | 6.185 | -5.815 | -12.616 | -41.013 | 25.6503 | 25.1197 | 24.0687 | 22.6442 | 21.4483 | 18.9758 | 17.3421 | 15.5136 | 13.685 | 11.3972 | 1.1391 | -28.3676 | -9.6507 | 24.7187 | 23.9432 | 22.6289 | 20.9789 | 19.5217 | 16.7472 | 14.7779 | 12.5717 | 10.3626 | 7.6707
|  | MILNATHORT | CF |  |  |  |  | -0.44357 | 22.6411 | 22.0177 | 21.3503 | 20.4421 | 19.3023 | 18.284 | 17.1013 | 15.9656 | 14.8013 | 7.9758 | 1.5146 | -27.1936 | 25.8115 | 25.5013 | 25.1258 | 24.7238 | 24.0105 | 22.9207 | 22.0054 | 20.9758 | 20.0054 | 19.0197 | 13.5421 | -14.2339 | 5.8921 | 24.934 | 24.5268 | 24.0452 | 23.4421 | 22.5238 | 21.2656 | 20.1779 | 18.9299 | 17.7574 | 16.5901
| MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | NO | 6.755 | 8.6409 | 8.3103 | 7.898 | 7.5021 | 6.9797 | 6.4368 | 5.7909 | 5.1664 | 4.6011 | 4.0042 | 2.2307 | 2.0807 | 0.87252 | 13.6297 | 13.4011 | 13.1184 | 12.8531 | 12.495 | 12.1082 | 11.6501 | 11.2031 | 10.8062 | 10.3674 | 9.1164 | 8.9797 | 6.496 | 9.349 | 9.0582 | 8.6888 | 8.3378 | 7.8684 | 7.397 | 6.8174 | 6.2409 | 5.7205 | 5.1817
|  | MILTON OF CRAIGIE | EE |  |  |  |  | 8.6409 | 8.3103 | 7.898 | 7.5021 | 6.9797 | 6.4368 | 5.7909 | 5.1664 | 4.6011 | 4.0042 | 2.4521 | 2.5807 | 1.3593 | 13.6297 | 13.4011 | 13.1184 | 12.8531 | 12.495 | 12.1082 | 11.6501 | 11.2031 | 10.8062 | 10.3674 | 9.1164 | 9.2246 | 8.2827 | 9.349 | 9.0582 | 8.6888 | 8.3378 | 7.8684 | 7.397 | 6.8174 | 6.2409 | 5.7205 | 5.1817
|  | MILTON OF CRAIGIE | HT |  |  |  |  | 8.7256 | 8.4133 | 8.0276 | 7.6388 | 7.1552 | 6.6613 | 6.1215 | 5.5868 | 5.1439 | 4.4827 | 2.2307 | 2.0807 | 0.87252 | 13.7021 | 13.5001 | 13.2531 | 13.0154 | 12.7072 | 12.3582 | 12.0011 | 11.6593 | 11.3878 | 10.9266 | 9.4286 | 9.9042 | 9.8725 | 9.448 | 9.1786 | 8.8531 | 8.5195 | 8.1042 | 7.6715 | 7.197 | 6.7225 | 6.345 | 5.7572
|  | MILTON OF CRAIGIE | HE |  |  |  |  | 8.749 | 8.5205 | 8.2552 | 7.9633 | 7.5715 | 7.1919 | 6.7082 | 6.2388 | 5.8521 | 5.3307 | 3.2419 | 2.898 | 1.7358 | 13.7154 | 13.5368 | 13.3419 | 13.1327 | 12.8542 | 12.5613 | 12.2001 | 11.8582 | 11.5776 | 11.1817 | 9.4256 | 9.4276 | 8.547 | 9.4695 | 9.2623 | 9.0317 | 8.7705 | 8.4276 | 8.0929 | 7.6644 | 7.2388 | 6.9093 | 6.4439
|  | MILTON OF CRAIGIE | CF |  |  |  |  | 8.8582 | 8.7378 | 8.5827 | 8.4429 | 8.245 | 8.0093 | 7.7878 | 7.5144 | 7.2899 | 7.0215 | 5.4215 | 3.6644 | 1.2837 | 13.7878 | 13.6776 | 13.5439 | 13.4246 | 13.2613 | 13.0542 | 12.849 | 12.599 | 12.3817 | 12.1205 | 10.5113 | 8.9797 | 6.496 | 9.5623 | 9.446 | 9.3001 | 9.1725 | 8.9878 | 8.7705 | 8.5746 | 8.3154 | 8.1031 | 7.848
| STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | YES | 2.232 | 7.4886 | 6.9998 | 6.4845 | 5.8763 | 5.2304 | 4.6753 | 4.1804 | 3.662 | 3.1835 | 2.6835 | 0.85693 | -0.22164 | -1.1033 | 8.5753 | 8.259 | 7.9049 | 7.4906 | 7.0355 | 6.6947 | 6.4345 | 6.1171 | 5.9447 | 5.6998 | 4.6773 | 4.436 | 3.6983 | 8.0625 | 7.6493 | 7.2034 | 6.6625 | 6.0799 | 5.588 | 5.1574 | 4.6472 | 4.2972 | 3.8615
|  | MINTLAW | EE |  |  |  |  | 7.4886 | 6.9998 | 6.5324 | 5.963 | 5.359 | 4.7814 | 4.2171 | 3.662 | 3.4151 | 2.9069 | 0.85693 | -0.12777 | -0.99818 | 8.5753 | 8.259 | 7.9457 | 7.5579 | 7.1426 | 6.7743 | 6.4355 | 6.1171 | 6.013 | 5.7488 | 4.6773 | 4.436 | 4.0278 | 8.0625 | 7.6493 | 7.2309 | 6.7187 | 6.185 | 5.6676 | 5.1574 | 4.6472 | 4.484 | 4.0442
|  | MINTLAW | HT |  |  |  |  | 7.5039 | 7.0069 | 6.4845 | 5.8763 | 5.2304 | 4.6753 | 4.1804 | 3.7192 | 3.1835 | 2.6835 | 0.87121 | -0.22164 | -1.1033 | 8.5845 | 8.263 | 7.9049 | 7.4906 | 7.0355 | 6.6947 | 6.4345 | 6.2059 | 5.9447 | 5.6998 | 4.8733 | 4.7503 | 4.6789 | 8.1023 | 7.6738 | 7.2034 | 6.6625 | 6.0799 | 5.588 | 5.1585 | 4.7585 | 4.2972 | 3.8615
|  | MINTLAW | HE |  |  |  |  | 7.5396 | 7.1396 | 6.7406 | 6.2569 | 5.7416 | 5.2539 | 4.8079 | 4.3957 | 3.9671 | 3.5141 | 1.5202 | 0.41509 | -0.5645 | 8.613 | 8.3386 | 8.0539 | 7.7069 | 7.3324 | 7.0049 | 6.7212 | 6.4845 | 6.2365 | 5.9845 | 4.9426 | 4.6432 | 4.2054 | 8.135 | 7.7891 | 7.436 | 7.0034 | 6.5483 | 6.1146 | 5.7166 | 5.3564 | 4.9758 | 4.5748
|  | MINTLAW | CF |  |  |  |  | 7.6222 | 7.3263 | 7.0477 | 6.7324 | 6.3957 | 6.0375 | 5.7294 | 5.4079 | 5.1365 | 4.8212 | 3.0151 | 1.46 | -0.082869 | 8.6814 | 8.4886 | 8.2967 | 8.0886 | 7.8528 | 7.6079 | 7.3886 | 7.1641 | 6.9835 | 6.7712 | 5.6192 | 4.7768 | 3.6983 | 8.2064 | 7.9564 | 7.7187 | 7.4442 | 7.1442 | 6.8268 | 6.5534 | 6.2625 | 6.0309 | 5.7483
| BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | NO | 0.764 | 4.9875 | 3.4466 | 2.3711 | 25.1364 | 24.5364 | 24.0599 | 23.4691 | 22.8334 | 22.1609 | 21.3609 | 19.0844 | 17.762 | -6.7636 | 5.7079 | 4.1273 | 26.1538 | 25.512 | 25.0783 | 24.8079 | 24.6222 | 24.4313 | 24.2446 | 24.0262 | 23.062 | -0.37223 | -1.0406 | 5.8512 | 27.9875 | 26.9609 | 26.2201 | 25.664 | 25.2395 | 24.7518 | 24.2303 | 23.6834 | 23.0446
|  | MONTROSE NORTH | EE |  |  |  |  | 5.3232 | 3.9262 | 2.8569 | 25.5528 | 24.8824 | 24.2885 | 23.6181 | 23.213 | 22.613 | 22.013 | 19.1966 | 17.8293 | -6.7636 | 6.1487 | 4.764 | 26.764 | 26.0609 | 25.5354 | 25.1262 | 24.7844 | 24.6405 | 24.4181 | 24.214 | 23.062 | -0.37223 | -1.0406 | 6.1716 | 28.5181 | 27.4773 | 26.6844 | 26.0681 | 25.5344 | 24.9466 | 24.565 | 24.0589 | 23.5548
|  | MONTROSE NORTH | HT |  |  |  |  | 4.9875 | 3.4466 | 2.3711 | 25.1364 | 24.5364 | 24.0599 | 23.4691 | 22.8334 | 22.1609 | 21.3609 | 19.0844 | 17.762 | -6.7605 | 5.7079 | 4.1273 | 26.1538 | 25.512 | 25.0783 | 24.8079 | 24.6222 | 24.4313 | 24.2446 | 24.0262 | 23.2722 | 0.13798 | 0.0492 | 5.8512 | 27.9875 | 26.9609 | 26.2201 | 25.664 | 25.2395 | 24.7518 | 24.2303 | 23.6834 | 23.0446
|  | MONTROSE NORTH | HE |  |  |  |  | 5.3793 | 4.1099 | 3.1415 | 25.9885 | 25.4232 | 24.962 | 24.5262 | 24.0691 | 23.6364 | 23.1875 | 21.2609 | 19.6793 | -5.3921 | 6.1762 | 4.8273 | 26.8487 | 26.1895 | 25.6834 | 25.3089 | 25.0405 | 24.816 | 24.6313 | 24.4487 | 23.8456 | 0.38798 | -0.46713 | 6.238 | 28.6589 | 27.714 | 27.0375 | 26.5007 | 26.0742 | 25.6864 | 25.2997 | 24.9344 | 24.5671
|  | MONTROSE NORTH | CF |  |  |  |  | 6.463 | 5.665 | 5.0089 | 27.9466 | 27.4966 | 27.0497 | 26.6895 | 26.3681 | 26.066 | 25.7518 | 23.9089 | 21.8293 | -3.9585 | 7.4283 | 6.5844 | 28.9211 | 28.2956 | 27.8354 | 27.4007 | 27.0446 | 26.7303 | 26.462 | 26.1936 | 24.8691 | 0.74308 | -0.99672 | 7.2268 | 30.1273 | 29.5313 | 28.9711 | 28.5528 | 28.1283 | 27.7824 | 27.4854 | 27.2007 | 26.9018
| TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | NO | 2.09 | 0.37406 | 0.22814 | 0.026102 | 4.333 | 4.1126 | 3.9177 | 3.7045 | 3.5208 | 3.3432 | 3.2228 | 2.8249 | 2.7045 | -1.8576 | 0.98324 | 0.88937 | 4.8851 | 4.7565 | 4.6116 | 4.4953 | 4.3698 | 4.2371 | 4.1167 | 4.0626 | 3.8014 | -0.41471 | -0.80451 | 0.69753 | 4.8718 | 4.7024 | 4.5249 | 4.3157 | 4.1504 | 3.9514 | 3.7718 | 3.6014 | 3.4983
|  | MOSSAT | EE |  |  |  |  | 0.37406 | 0.22814 | 0.035286 | 4.3443 | 4.1126 | 3.9177 | 3.7045 | 3.5208 | 3.3432 | 3.2228 | 2.8249 | 2.7575 | -1.777 | 0.98324 | 0.88937 | 4.8851 | 4.7565 | 4.6116 | 4.4953 | 4.3698 | 4.2371 | 4.1167 | 4.0626 | 3.8014 | -0.41471 | -0.56778 | 0.69753 | 4.8718 | 4.7024 | 4.5249 | 4.3157 | 4.1504 | 3.9514 | 3.7718 | 3.6014 | 3.4983
|  | MOSSAT | HT |  |  |  |  | 0.40569 | 0.22814 | 0.026102 | 4.333 | 4.1218 | 3.931 | 3.7963 | 3.682 | 3.5483 | 3.4157 | 2.9381 | 2.7045 | -1.8576 | 1.0016 | 0.89651 | 4.8861 | 4.7586 | 4.6351 | 4.5269 | 4.4483 | 4.3851 | 4.3096 | 4.2341 | 3.931 | -0.30553 | -0.33104 | 0.72814 | 4.8892 | 4.7188 | 4.5392 | 4.3534 | 4.1841 | 4.0677 | 3.9626 | 3.8402 | 3.7116
|  | MOSSAT | HE |  |  |  |  | 0.41794 | 0.30978 | 0.1608 | 4.4892 | 4.3086 | 4.1351 | 3.9616 | 3.8239 | 3.7269 | 3.6014 | 2.9616 | 2.8024 | -1.7402 | 1.0098 | 0.93529 | 4.9524 | 4.8351 | 4.7228 | 4.6167 | 4.5116 | 4.4239 | 4.3626 | 4.2851 | 3.883 | -0.3892 | -0.54329 | 0.73937 | 4.9514 | 4.8208 | 4.6626 | 4.5116 | 4.3575 | 4.1994 | 4.0637 | 3.9841 | 3.8637
|  | MOSSAT | CF |  |  |  |  | 0.44345 | 0.36692 | 0.26794 | 4.6483 | 4.5004 | 4.3718 | 4.2453 | 4.1024 | 4.0096 | 3.9443 | 3.4524 | 3.0677 | -1.68 | 1.0312 | 0.97916 | 5.0218 | 4.9473 | 4.8555 | 4.7769 | 4.6953 | 4.6045 | 4.5371 | 4.4902 | 4.1004 | -0.39839 | -0.80451 | 0.76794 | 5.0034 | 4.9116 | 4.8034 | 4.6728 | 4.5657 | 4.4534 | 4.3218 | 4.23 | 4.18
| THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | NO | 1.436 | 9.0429 | 8.3827 | 7.5806 | 6.9867 | 6.552 | 6.1061 | 5.6418 | 5.202 | 4.749 | 4.4582 | 3.1633 | 2.3653 | 1.4786 | 9.8347 | 9.3194 | 8.6531 | 8.1878 | 7.8673 | 7.5929 | 7.3571 | 7.1337 | 6.8378 | 6.7908 | 6.099 | 6.0913 | 5.8097 | 9.6638 | 9.0495 | 8.2944 | 7.7515 | 7.3617 | 7.0128 | 6.6362 | 6.224 | 5.7413 | 5.5689
|  | MOUNT PLEASANT | EE |  |  |  |  | 9.1612 | 8.5173 | 7.8418 | 7.248 | 6.7357 | 6.3306 | 5.8388 | 5.2765 | 4.749 | 4.5408 | 3.1633 | 2.4571 | 1.5408 | 9.9408 | 9.4378 | 8.9 | 8.4316 | 8.0449 | 7.7541 | 7.4551 | 7.1337 | 6.8378 | 6.799 | 6.099 | 6.0913 | 5.8097 | 9.7974 | 9.2046 | 8.5801 | 8.0495 | 7.5842 | 7.2066 | 6.7423 | 6.224 | 5.7413 | 5.6128
|  | MOUNT PLEASANT | HT |  |  |  |  | 9.0429 | 8.3827 | 7.5806 | 6.9867 | 6.552 | 6.1061 | 5.6418 | 5.202 | 4.8112 | 4.4582 | 3.1857 | 2.3653 | 1.4786 | 9.8347 | 9.3194 | 8.6531 | 8.1878 | 7.8673 | 7.5929 | 7.3571 | 7.149 | 6.9633 | 6.7908 | 6.2367 | 6.2454 | 6.1842 | 9.6638 | 9.0495 | 8.2944 | 7.7515 | 7.3617 | 7.0128 | 6.6362 | 6.2546 | 5.8974 | 5.5689
|  | MOUNT PLEASANT | HE |  |  |  |  | 9.2051 | 8.6459 | 8.0541 | 7.5541 | 7.1684 | 6.8357 | 6.4827 | 6.1245 | 5.7714 | 5.4153 | 4.0776 | 3.2949 | 2.2663 | 9.9786 | 9.5153 | 9.0122 | 8.5918 | 8.2673 | 8.0041 | 7.7724 | 7.5653 | 7.3653 | 7.1704 | 6.5041 | 6.4526 | 6.1444 | 9.824 | 9.2903 | 8.723 | 8.2536 | 7.8903 | 7.5923 | 7.2923 | 7.0087 | 6.7158 | 6.3883
|  | MOUNT PLEASANT | CF |  |  |  |  | 9.6704 | 9.3214 | 8.9306 | 8.6214 | 8.3061 | 8.0357 | 7.7745 | 7.5112 | 7.2276 | 6.9735 | 5.4878 | 4.5102 | 3.0082 | 10.3827 | 10.0908 | 9.7612 | 9.5092 | 9.252 | 9.0276 | 8.8133 | 8.601 | 8.3959 | 8.2122 | 7.1327 | 6.7536 | 6.027 | 10.2842 | 9.9566 | 9.5893 | 9.3046 | 9.0209 | 8.7679 | 8.5393 | 8.3077 | 8.0444 | 7.8179
| BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | NO | 5.8 | 1.2132 | 0.9163 | 0.57242 | 0.24487 | -0.13472 | -0.71533 | -1.5674 | -2.449 | -3.2082 | -3.699 | -5.4796 | -6.148 | -6.3225 | 4.2673 | 4.1081 | 3.903 | 3.701 | 3.4377 | 3.1561 | 2.8122 | 2.4714 | 2.0816 | 1.7561 | 0.62038 | 0.14283 | -0.86737 | 2.9449 | 2.6734 | 2.352 | 2.049 | 1.6908 | 1.2694 | 0.54998 | -0.21023 | -0.86839 | -1.2276
|  | MUIR OF ORD | EE |  |  |  |  | 1.2132 | 0.9163 | 0.57242 | 0.24487 | -0.13472 | -0.53064 | -1.0388 | -1.6878 | -2.5725 | -3.4419 | -5.4796 | -5.9694 | -6.099 | 4.2673 | 4.1081 | 3.903 | 3.701 | 3.4377 | 3.1561 | 2.8122 | 2.6734 | 2.2 | 1.7561 | 0.62038 | 0.14283 | -0.45717 | 2.9449 | 2.6734 | 2.352 | 2.049 | 1.6908 | 1.3132 | 0.83467 | 0.34283 | -0.41839 | -1.1572
|  | MUIR OF ORD | HT |  |  |  |  | 1.2816 | 0.99487 | 0.68365 | 0.38773 | 0.049976 | -0.71533 | -1.5674 | -2.449 | -3.2082 | -3.699 | -5.3082 | -6.148 | -6.3225 | 4.3336 | 4.1979 | 4.0377 | 3.8888 | 3.7071 | 3.3439 | 2.9194 | 2.4714 | 2.0816 | 1.9316 | 0.99385 | 0.56222 | 0.47344 | 3.0245 | 2.7704 | 2.4847 | 2.2163 | 1.9041 | 1.2694 | 0.54998 | -0.21023 | -0.86839 | -1.2276
|  | MUIR OF ORD | HE |  |  |  |  | 1.2836 | 1.0877 | 0.86936 | 0.66528 | 0.41936 | 0.18263 | -0.15309 | -0.66533 | -1.1602 | -1.6755 | -3.7521 | -4.7878 | -5.2204 | 4.3316 | 4.2214 | 4.0888 | 3.9663 | 3.8122 | 3.6724 | 3.4571 | 3.1439 | 2.8336 | 2.5122 | 1.45 | 0.71018 | 0.0020163 | 3.0255 | 2.849 | 2.6449 | 2.453 | 2.2204 | 2.0071 | 1.6928 | 1.2326 | 0.78671 | 0.32242
|  | MUIR OF ORD | CF |  |  |  |  | 1.3275 | 1.1785 | 0.99589 | 0.82957 | 0.62753 | 0.41732 | 0.23059 | 0.018343 | -0.3286 | -0.67758 | -2.1031 | -3.6041 | -4.7582 | 4.3571 | 4.2734 | 4.1602 | 4.0602 | 3.9336 | 3.7877 | 3.6683 | 3.4826 | 3.252 | 3.0112 | 2.099 | 0.72753 | -0.86737 | 3.0673 | 2.9316 | 2.7653 | 2.6122 | 2.4265 | 2.2285 | 2.0622 | 1.8551 | 1.549 | 1.2357
| BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | NO | 0.11 | 0.22629 | 0.1222 | 0.0099592 | -0.095143 | -0.21351 | -0.30331 | -0.44208 | -0.62473 | -0.80127 | -0.9278 | -1.2462 | -1.3574 | -1.3911 | 1.4589 | 1.3977 | 1.3334 | 1.264 | 1.1875 | 1.1324 | 1.0396 | 0.92322 | 0.8069 | 0.74057 | 0.5171 | 0.4069 | 0.01098 | 0.92833 | 0.83037 | 0.73037 | 0.63037 | 0.512 | 0.42731 | 0.28649 | 0.10588 | -0.066571 | -0.16453
|  | MUIREND | EE |  |  |  |  | 0.22629 | 0.1222 | 0.0099592 | -0.095143 | -0.21351 | -0.30331 | -0.44208 | -0.62473 | -0.80127 | -0.9278 | -1.2462 | -1.3013 | -1.3278 | 1.4589 | 1.3977 | 1.3334 | 1.264 | 1.1875 | 1.1324 | 1.0396 | 0.92322 | 0.8069 | 0.74057 | 0.5171 | 0.4069 | 0.24261 | 0.92833 | 0.83037 | 0.73037 | 0.63037 | 0.512 | 0.42731 | 0.28649 | 0.10588 | -0.066571 | -0.16453
|  | MUIREND | HT |  |  |  |  | 0.262 | 0.16812 | 0.067102 | -0.027796 | -0.10739 | -0.22984 | -0.36351 | -0.51759 | -0.59718 | -0.71351 | -1.1543 | -1.3574 | -1.3911 | 1.4906 | 1.4426 | 1.3885 | 1.3334 | 1.2906 | 1.2222 | 1.1447 | 1.0518 | 1.0038 | 0.92833 | 0.64363 | 0.52833 | 0.50792 | 0.9722 | 0.89057 | 0.79976 | 0.70996 | 0.63955 | 0.52833 | 0.40486 | 0.25588 | 0.18241 | 0.065061
|  | MUIREND | HE |  |  |  |  | 0.25996 | 0.18547 | 0.10486 | 0.028327 | -0.033918 | -0.10841 | -0.20331 | -0.33188 | -0.41759 | -0.538 | -1.0972 | -1.2298 | -1.2502 | 1.4896 | 1.4467 | 1.3967 | 1.3457 | 1.3079 | 1.2579 | 1.1916 | 1.1089 | 1.0579 | 0.97424 | 0.60996 | 0.45384 | 0.29567 | 0.97016 | 0.90486 | 0.82833 | 0.75282 | 0.69567 | 0.62424 | 0.52833 | 0.4018 | 0.32527 | 0.2069
|  | MUIREND | CF |  |  |  |  | 0.27935 | 0.21914 | 0.13343 | 0.072204 | 0.0048571 | -0.042082 | -0.10433 | -0.17984 | -0.26861 | -0.32678 | -0.74412 | -1.0411 | -1.2247 | 1.5028 | 1.4671 | 1.414 | 1.3732 | 1.3273 | 1.2967 | 1.2528 | 1.1926 | 1.1273 | 1.0926 | 0.74873 | 0.4069 | 0.01098 | 0.98751 | 0.93241 | 0.85078 | 0.79261 | 0.72424 | 0.68241 | 0.6222 | 0.54057 | 0.4518 | 0.4018
| NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 3.163 | 2.8445 | 2.3966 | 1.9129 | 1.3802 | 0.78635 | 0.1792 | -0.77488 | -1.7688 | -2.4443 | -3.3626 | -6.5402 | -8.3749 | -9.4963 | 5.1414 | 5.0078 | 4.8221 | 4.5517 | 4.2527 | 4.1057 | 3.6741 | 3.2159 | 2.8108 | 2.3751 | 0.81594 | 0.078694 | -0.82437 | 3.7909 | 3.5052 | 3.192 | 2.7583 | 2.2532 | 1.7562 | 0.95318 | 0.11951 | -0.44886 | -1.2254
|  | NAIRN CENTRAL | EE |  |  |  |  | 2.8445 | 2.3966 | 1.9129 | 1.3802 | 0.78635 | 0.43941 | -0.32182 | -1.3055 | -2.2688 | -3.1739 | -6.3208 | -8.1902 | -9.3769 | 5.1414 | 5.0078 | 4.8221 | 4.5517 | 4.2527 | 4.12 | 3.7557 | 3.2761 | 2.8108 | 2.3751 | 0.81594 | 0.078694 | -0.82437 | 3.7909 | 3.5052 | 3.192 | 2.7583 | 2.2532 | 1.9542 | 1.2981 | 0.46951 | -0.34273 | -1.105
|  | NAIRN CENTRAL | HT |  |  |  |  | 2.9261 | 2.471 | 2.0027 | 1.4884 | 0.95165 | 0.1792 | -0.77488 | -1.7688 | -2.4443 | -3.3626 | -6.5402 | -8.3749 | -9.4963 | 5.1935 | 5.0761 | 4.9221 | 4.6976 | 4.4598 | 4.1057 | 3.6741 | 3.2159 | 2.9731 | 2.5588 | 1.1221 | 0.70931 | 0.52563 | 3.8562 | 3.5777 | 3.2858 | 2.8491 | 2.395 | 1.7562 | 0.95318 | 0.11951 | -0.44886 | -1.2254
|  | NAIRN CENTRAL | HE |  |  |  |  | 2.9537 | 2.6517 | 2.3547 | 2.0159 | 1.6547 | 1.2343 | 0.70676 | 0.088388 | -0.21467 | -0.75855 | -3.5565 | -5.732 | -7.5463 | 5.1966 | 5.0894 | 4.9904 | 4.8608 | 4.6802 | 4.4568 | 4.1874 | 3.8608 | 3.7496 | 3.4659 | 1.9455 | 1.042 | -0.095796 | 3.8664 | 3.6664 | 3.4695 | 3.244 | 3.0001 | 2.6542 | 2.2052 | 1.6807 | 1.4205 | 0.95829
|  | NAIRN CENTRAL | CF |  |  |  |  | 3.1639 | 2.9261 | 2.6568 | 2.4445 | 2.1659 | 1.9037 | 1.6414 | 1.3476 | 1.0159 | 0.70573 | -0.64222 | -2.8392 | -5.7157 | 5.2731 | 5.1843 | 5.0904 | 5.0159 | 4.8823 | 4.7292 | 4.5578 | 4.3568 | 4.1404 | 3.9292 | 2.9823 | 1.5777 | -0.80294 | 3.9899 | 3.8501 | 3.6899 | 3.5573 | 3.3818 | 3.2134 | 3.0124 | 2.7685 | 2.4981 | 2.243
| STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | YES | 0.091 | 6.1502 | 6.0808 | 5.9971 | 5.9278 | 5.8431 | 5.7492 | 5.6308 | 5.5176 | 5.3839 | 5.2492 | 4.7665 | 4.6706 | 4.6329 | 6.7931 | 6.7512 | 6.69 | 6.6502 | 6.59 | 6.5196 | 6.4359 | 6.3696 | 6.2767 | 6.1931 | 5.9278 | 5.8573 | 5.5931 | 6.442 | 6.3757 | 6.291 | 6.2216 | 6.139 | 6.0431 | 5.9206 | 5.8165 | 5.6818 | 5.5543
|  | NEW PITSLIGO | EE |  |  |  |  | 6.1502 | 6.0808 | 5.9971 | 5.9278 | 5.8431 | 5.7492 | 5.6308 | 5.5176 | 5.3839 | 5.2492 | 4.7665 | 4.7084 | 4.688 | 6.7931 | 6.7512 | 6.69 | 6.6502 | 6.59 | 6.5196 | 6.4359 | 6.3696 | 6.2767 | 6.1931 | 5.9278 | 5.8573 | 5.7482 | 6.442 | 6.3757 | 6.291 | 6.2216 | 6.139 | 6.0431 | 5.9206 | 5.8165 | 5.6818 | 5.5543
|  | NEW PITSLIGO | HT |  |  |  |  | 6.1665 | 6.1033 | 6.041 | 5.9727 | 5.8951 | 5.8288 | 5.7176 | 5.5971 | 5.4594 | 5.3227 | 4.8492 | 4.6706 | 4.6329 | 6.8155 | 6.7788 | 6.7431 | 6.7053 | 6.6563 | 6.6247 | 6.5563 | 6.4859 | 6.4022 | 6.342 | 6.0206 | 5.9216 | 5.9022 | 6.4635 | 6.4043 | 6.3441 | 6.2808 | 6.2063 | 6.1431 | 6.04 | 5.9257 | 5.7992 | 5.6869
|  | NEW PITSLIGO | HE |  |  |  |  | 6.1676 | 6.1196 | 6.0747 | 6.0237 | 5.9645 | 5.9165 | 5.839 | 5.7247 | 5.5982 | 5.4553 | 4.8818 | 4.7594 | 4.7267 | 6.8155 | 6.7829 | 6.7553 | 6.7227 | 6.6778 | 6.6492 | 6.5961 | 6.5247 | 6.4461 | 6.3604 | 6.0165 | 5.9053 | 5.792 | 6.4655 | 6.4165 | 6.3727 | 6.3227 | 6.2635 | 6.2176 | 6.14 | 6.0359 | 5.9206 | 5.7869
|  | NEW PITSLIGO | CF |  |  |  |  | 6.1788 | 6.138 | 6.1002 | 6.0512 | 6.0114 | 5.9614 | 5.9227 | 5.8655 | 5.8043 | 5.7278 | 5.2563 | 4.9747 | 4.789 | 6.8227 | 6.7971 | 6.7737 | 6.739 | 6.7124 | 6.6767 | 6.6543 | 6.6063 | 6.5655 | 6.5114 | 6.1971 | 5.9104 | 5.5931 | 6.4747 | 6.4369 | 6.4002 | 6.3543 | 6.3165 | 6.2645 | 6.2308 | 6.1706 | 6.1145 | 6.0431
| DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0.084 | 0.17197 | 0.16891 | 0.16176 | 0.1536 | 0.14646 | 0.13727 | 0.12401 | 0.11278 | 0.098498 | 0.085233 | 0.05462 | 0.043396 | 0.015376 | 0.18884 | 0.18782 | 0.18987 | 0.18476 | 0.17966 | 0.17354 | 0.16333 | 0.15721 | 0.14497 | 0.13782 | 0.11538 | 0.11867 | 0.09112 | 0.18092 | 0.17786 | 0.17275 | 0.16561 | 0.15949 | 0.14928 | 0.135 | 0.12581 | 0.11153 | 0.10132
|  | NEWTON | EE |  |  |  |  | 0.17197 | 0.16891 | 0.16176 | 0.1536 | 0.14646 | 0.13727 | 0.12401 | 0.11278 | 0.098498 | 0.085233 | 0.05462 | 0.05258 | 0.022518 | 0.18884 | 0.19497 | 0.18987 | 0.18476 | 0.17966 | 0.17354 | 0.16333 | 0.15721 | 0.14497 | 0.13782 | 0.11538 | 0.11867 | 0.10643 | 0.18092 | 0.1799 | 0.17275 | 0.16561 | 0.15949 | 0.14928 | 0.135 | 0.12581 | 0.11153 | 0.10132
|  | NEWTON | HT |  |  |  |  | 0.17911 | 0.16891 | 0.16891 | 0.16278 | 0.1536 | 0.14952 | 0.14238 | 0.12911 | 0.12095 | 0.10768 | 0.064824 | 0.043396 | 0.015376 | 0.19599 | 0.18782 | 0.19599 | 0.19191 | 0.18578 | 0.18476 | 0.17864 | 0.16946 | 0.16436 | 0.15619 | 0.1266 | 0.12581 | 0.12581 | 0.18806 | 0.17786 | 0.1799 | 0.17479 | 0.16561 | 0.16153 | 0.15439 | 0.14214 | 0.13398 | 0.12479
|  | NEWTON | HE |  |  |  |  | 0.17911 | 0.16891 | 0.17299 | 0.16482 | 0.1587 | 0.1536 | 0.14952 | 0.13829 | 0.13217 | 0.11789 | 0.072988 | 0.059722 | 0.028641 | 0.19599 | 0.18782 | 0.19701 | 0.19293 | 0.1868 | 0.18476 | 0.18272 | 0.17558 | 0.1664 | 0.15925 | 0.12864 | 0.12479 | 0.11153 | 0.18806 | 0.17786 | 0.18296 | 0.17479 | 0.16969 | 0.16561 | 0.16255 | 0.1503 | 0.14418 | 0.13092
|  | NEWTON | CF |  |  |  |  | 0.18625 | 0.17809 | 0.16789 | 0.17095 | 0.16584 | 0.15768 | 0.1536 | 0.15054 | 0.14238 | 0.13829 | 0.10564 | 0.074008 | 0.030682 | 0.20211 | 0.19599 | 0.19395 | 0.19701 | 0.19395 | 0.1868 | 0.1817 | 0.18068 | 0.17558 | 0.17252 | 0.14599 | 0.12479 | 0.09112 | 0.1952 | 0.18704 | 0.17888 | 0.18194 | 0.17683 | 0.16765 | 0.16561 | 0.16255 | 0.15439 | 0.1503
| REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | NO | 6.813 | -1.0896 | -2.1886 | 11.0839 | 9.6328 | 8.0002 | 6.5481 | 5.2012 | 3.7706 | 2.6339 | 1.1441 | -6.1253 | -10.1151 | -25.6896 | 0.8706 | 13.8726 | 12.9288 | 11.8522 | 10.5349 | 9.4604 | 8.5971 | 7.6532 | 6.8175 | 5.7584 | 2.3277 | -13.135 | -13.9238 | 13.8686 | 12.9288 | 11.7247 | 10.3451 | 8.7951 | 7.4522 | 6.2308 | 4.941 | 3.893 | 2.5359
|  | NEWTONHILL | EE |  |  |  |  | -1.0896 | -2.1406 | 11.2237 | 9.9135 | 8.3635 | 6.9767 | 5.8318 | 4.4594 | 3.1471 | 1.792 | -5.958 | -9.9906 | -25.5916 | 0.8706 | 13.891 | 13.0084 | 12.0339 | 10.8941 | 9.9155 | 9.0267 | 8.1002 | 7.2155 | 6.2777 | 2.3277 | -13.135 | -13.8258 | 13.8951 | 13.0022 | 11.9022 | 10.6645 | 9.2216 | 7.9594 | 6.8584 | 5.6175 | 4.4196 | 3.1818
|  | NEWTONHILL | HT |  |  |  |  | -1.0886 | -2.1886 | 11.0839 | 9.6328 | 8.0002 | 6.5481 | 5.2012 | 3.7706 | 2.6339 | 1.1441 | -6.1253 | -10.1151 | -25.6896 | 0.87876 | 13.8726 | 12.9288 | 11.8522 | 10.5349 | 9.4604 | 8.5971 | 7.6532 | 6.8175 | 5.7584 | 2.5716 | -12.6401 | -12.7758 | 13.8686 | 12.9288 | 11.7247 | 10.3451 | 8.7951 | 7.4522 | 6.2308 | 4.941 | 3.893 | 2.5359
|  | NEWTONHILL | HE |  |  |  |  | -1.0059 | -1.9121 | 11.64 | 10.4584 | 9.1155 | 7.9073 | 6.6584 | 5.4686 | 4.6553 | 3.491 | -4.1988 | -8.4233 | -24.4376 | 0.9359 | 14.0247 | 13.242 | 12.3196 | 11.2094 | 10.2675 | 9.3165 | 8.4359 | 7.7073 | 6.79 | 2.9828 | -12.5789 | -13.4054 | 13.9461 | 13.1206 | 12.2277 | 11.139 | 9.8706 | 8.7594 | 7.6114 | 6.5369 | 5.7441 | 4.6737
|  | NEWTONHILL | CF |  |  |  |  | -0.80287 | -1.4631 | 12.3145 | 11.5339 | 10.5584 | 9.7686 | 8.9981 | 8.1716 | 7.4165 | 6.6043 | -0.26818 | -5.8957 | -22.9549 | 1.089 | 14.3624 | 13.7512 | 13.1451 | 12.4012 | 11.8441 | 11.2777 | 10.6624 | 10.0971 | 9.4798 | 5.2359 | -12.0432 | -13.9238 | 14.1257 | 13.5318 | 12.8481 | 12.1604 | 11.3012 | 10.593 | 9.9073 | 9.1706 | 8.5022 | 7.7686
| ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | NO | 8.5 | -7.4082 | -7.4082 | -7.4102 | -7.4102 | -7.4112 | -7.4112 | -7.4122 | -7.4143 | -7.4143 | -7.4153 | -7.4194 | -7.4214 | -7.4224 | -6.9806 | -6.9806 | -6.9816 | -6.9816 | -6.9816 | -6.9816 | -6.9827 | -6.9837 | -6.9837 | -6.9847 | -6.9867 | -6.9878 | -6.9878 | -7.1561 | -7.1561 | -7.1582 | -7.1582 | -7.1592 | -7.1592 | -7.1602 | -7.1612 | -7.1612 | -7.1633
|  | NIGG | EE |  |  |  |  | -7.4082 | -7.4082 | -7.4102 | -7.4102 | -7.4112 | -7.4112 | -7.4122 | -7.4143 | -7.4143 | -7.4153 | -7.4184 | -7.4184 | -7.4184 | -6.9806 | -6.9806 | -6.9816 | -6.9816 | -6.9816 | -6.9816 | -6.9827 | -6.9837 | -6.9837 | -6.9847 | -6.9857 | -6.9857 | -6.9857 | -7.1561 | -7.1561 | -7.1582 | -7.1582 | -7.1592 | -7.1592 | -7.1602 | -7.1612 | -7.1612 | -7.1633
|  | NIGG | HT |  |  |  |  | -7.4071 | -7.4082 | -7.4082 | -7.4082 | -7.4102 | -7.4102 | -7.4112 | -7.4122 | -7.4122 | -7.4143 | -7.4184 | -7.4194 | -7.4194 | -6.9796 | -6.9806 | -6.9806 | -6.9806 | -6.9816 | -6.9816 | -6.9816 | -6.9827 | -6.9827 | -6.9837 | -6.9857 | -6.9867 | -6.9867 | -7.1551 | -7.1561 | -7.1561 | -7.1561 | -7.1582 | -7.1582 | -7.1592 | -7.1602 | -7.1602 | -7.1612
|  | NIGG | HE |  |  |  |  | -7.4071 | -7.4082 | -7.4082 | -7.4102 | -7.4102 | -7.4112 | -7.4112 | -7.4122 | -7.4143 | -7.4153 | -7.4194 | -7.4214 | -7.4224 | -6.9796 | -6.9806 | -6.9806 | -6.9816 | -6.9816 | -6.9816 | -6.9816 | -6.9827 | -6.9837 | -6.9847 | -6.9867 | -6.9878 | -6.9878 | -7.1551 | -7.1561 | -7.1561 | -7.1582 | -7.1582 | -7.1592 | -7.1592 | -7.1602 | -7.1612 | -7.1633
|  | NIGG | CF |  |  |  |  | -7.4071 | -7.4082 | -7.4082 | -7.4082 | -7.4082 | -7.4102 | -7.4102 | -7.4112 | -7.4112 | -7.4112 | -7.4153 | -7.4194 | -7.4214 | -6.9796 | -6.9806 | -6.9806 | -6.9806 | -6.9806 | -6.9816 | -6.9816 | -6.9816 | -6.9816 | -6.9816 | -6.9847 | -6.9867 | -6.9878 | -7.1551 | -7.1561 | -7.1561 | -7.1561 | -7.1561 | -7.1582 | -7.1582 | -7.1592 | -7.1592 | -7.1592
| CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | YES | 3.266 | 7.667 | 7.4425 | 7.1395 | 6.7935 | 6.5803 | 6.3344 | 6.0905 | 5.817 | 5.5354 | 5.2874 | 4.5558 | 4.2088 | 3.2456 | 7.8548 | 7.7456 | 7.5782 | 7.4058 | 7.2292 | 7.0344 | 6.8303 | 6.5588 | 6.318 | 6.1099 | 5.4792 | 5.4359 | 3.5583 | 7.6461 | 7.4726 | 7.2338 | 6.9818 | 6.7696 | 6.5002 | 6.2257 | 5.8757 | 5.5604 | 5.2808
|  | NINEWELLS | EE |  |  |  |  | 7.667 | 7.4425 | 7.1395 | 6.7935 | 6.5803 | 6.3344 | 6.0905 | 5.817 | 5.5354 | 5.2874 | 4.5558 | 4.5762 | 3.8446 | 7.8548 | 7.7456 | 7.5782 | 7.4058 | 7.2292 | 7.0344 | 6.8303 | 6.5588 | 6.318 | 6.1099 | 5.5139 | 5.7338 | 4.942 | 7.6461 | 7.4726 | 7.2338 | 6.9818 | 6.7696 | 6.5002 | 6.2257 | 5.8757 | 5.5604 | 5.2808
|  | NINEWELLS | HT |  |  |  |  | 7.718 | 7.5037 | 7.2048 | 6.8986 | 6.6925 | 6.4752 | 6.3058 | 6.0119 | 5.7619 | 5.5619 | 4.6395 | 4.3384 | 3.4282 | 7.9037 | 7.8119 | 7.6558 | 7.5119 | 7.3976 | 7.2364 | 7.0905 | 6.8282 | 6.6109 | 6.416 | 5.617 | 5.7318 | 5.6042 | 7.7114 | 7.5614 | 7.342 | 7.0787 | 6.891 | 6.691 | 6.5359 | 6.2104 | 5.9257 | 5.6634
|  | NINEWELLS | HE |  |  |  |  | 7.7231 | 7.5548 | 7.316 | 7.066 | 6.9058 | 6.7405 | 6.6078 | 6.3844 | 6.1813 | 5.9609 | 4.719 | 4.2088 | 3.2456 | 7.8986 | 7.8037 | 7.6629 | 7.5231 | 7.4109 | 7.2558 | 7.0966 | 6.8415 | 6.6201 | 6.4058 | 5.4792 | 5.5155 | 5.0032 | 7.7063 | 7.5634 | 7.3706 | 7.1706 | 7.0083 | 6.8267 | 6.6277 | 6.3124 | 6.0298 | 5.7604
|  | NINEWELLS | CF |  |  |  |  | 7.7537 | 7.6292 | 7.4639 | 7.2792 | 7.1803 | 7.0721 | 6.9986 | 6.918 | 6.8252 | 6.718 | 5.8803 | 4.9303 | 3.517 | 7.919 | 7.8558 | 7.7629 | 7.668 | 7.5966 | 7.519 | 7.4395 | 7.3292 | 7.2109 | 7.0741 | 6.2925 | 5.4359 | 3.5583 | 7.744 | 7.6512 | 7.5247 | 7.392 | 7.291 | 7.1798 | 7.0747 | 6.9308 | 6.7971 | 6.6522
| THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | NO | 0 | 0.16865 | 0.15743 | 0.14824 | 0.1462 | 0.14416 | 0.14824 | 0.14212 | 0.13804 | 0.136 | 0.1309 | 0.11559 | 0.10845 | 0.085347 | 0.17514 | 0.16494 | 0.15678 | 0.15678 | 0.15473 | 0.15678 | 0.16086 | 0.15678 | 0.15473 | 0.15167 | 0.13943 | 0.14333 | 0.13822 | 0.17496 | 0.16373 | 0.15557 | 0.15557 | 0.15251 | 0.15557 | 0.15047 | 0.14639 | 0.14435 | 0.14027
|  | NORTH HOY | EE |  |  |  |  | 0.16865 | 0.15743 | 0.14824 | 0.15641 | 0.15131 | 0.14927 | 0.14212 | 0.13804 | 0.136 | 0.1309 | 0.11763 | 0.11661 | 0.098612 | 0.17514 | 0.16494 | 0.15678 | 0.16902 | 0.16596 | 0.16494 | 0.16086 | 0.15678 | 0.15473 | 0.15167 | 0.14147 | 0.14945 | 0.14639 | 0.17496 | 0.16373 | 0.15557 | 0.16476 | 0.15863 | 0.15761 | 0.15047 | 0.14639 | 0.14435 | 0.14027
|  | NORTH HOY | HT |  |  |  |  | 0.16967 | 0.16661 | 0.15845 | 0.1462 | 0.14416 | 0.14824 | 0.15335 | 0.14824 | 0.14212 | 0.14008 | 0.12069 | 0.11355 | 0.09249 | 0.17616 | 0.17412 | 0.16596 | 0.15678 | 0.15576 | 0.1629 | 0.16698 | 0.16392 | 0.15984 | 0.1578 | 0.14249 | 0.14741 | 0.14537 | 0.17598 | 0.17394 | 0.16476 | 0.15557 | 0.15251 | 0.15557 | 0.16169 | 0.15659 | 0.15047 | 0.14741
|  | NORTH HOY | HE |  |  |  |  | 0.16967 | 0.16661 | 0.15743 | 0.15539 | 0.14416 | 0.15029 | 0.15335 | 0.14824 | 0.14314 | 0.136 | 0.11559 | 0.10845 | 0.085347 | 0.17616 | 0.1731 | 0.16494 | 0.16392 | 0.15473 | 0.16392 | 0.16698 | 0.16188 | 0.15882 | 0.15473 | 0.13943 | 0.14333 | 0.13924 | 0.17598 | 0.1719 | 0.16373 | 0.16271 | 0.15251 | 0.15863 | 0.16271 | 0.15659 | 0.15149 | 0.14537
|  | NORTH HOY | CF |  |  |  |  | 0.16865 | 0.16661 | 0.16559 | 0.15845 | 0.15029 | 0.14824 | 0.15029 | 0.15539 | 0.15029 | 0.15131 | 0.13498 | 0.11865 | 0.090449 | 0.17616 | 0.17514 | 0.17412 | 0.16596 | 0.1578 | 0.15678 | 0.16392 | 0.168 | 0.16596 | 0.16596 | 0.15167 | 0.14843 | 0.13822 | 0.17598 | 0.17394 | 0.17292 | 0.16476 | 0.15659 | 0.15557 | 0.15863 | 0.16373 | 0.15863 | 0.15965
| BEAULY | NORTH KESSOCK | MINIMUM HEADROOM | NH 65004 48461 | YES | NO | 1.5 | 2.0292 | 1.9588 | 1.8669 | 1.7935 | 1.7047 | 1.6037 | 1.518 | 1.3822 | 1.2516 | 1.1353 | 0.86898 | 0.78531 | 0.44265 | 2.2498 | 2.208 | 2.1447 | 2.1018 | 2.0437 | 1.9784 | 1.9263 | 1.8345 | 1.7457 | 1.6753 | 1.4978 | 1.6053 | 1.3716 | 2.2206 | 2.1563 | 2.0655 | 2.0022 | 1.9155 | 1.8196 | 1.738 | 1.6053 | 1.4778 | 1.3696
|  | NORTH KESSOCK | EE |  |  |  |  | 2.0292 | 1.9588 | 1.8669 | 1.7935 | 1.7047 | 1.6037 | 1.518 | 1.3822 | 1.2516 | 1.1353 | 0.86898 | 0.8251 | 0.49367 | 2.2498 | 2.208 | 2.1447 | 2.1018 | 2.0437 | 1.9784 | 1.9263 | 1.8345 | 1.7457 | 1.6753 | 1.4978 | 1.6053 | 1.5492 | 2.2206 | 2.1563 | 2.0655 | 2.0022 | 1.9155 | 1.8196 | 1.738 | 1.6053 | 1.4778 | 1.3696
|  | NORTH KESSOCK | HT |  |  |  |  | 2.0578 | 1.9955 | 1.921 | 1.8527 | 1.7751 | 1.7118 | 1.6251 | 1.522 | 1.42 | 1.3567 | 0.95163 | 0.78531 | 0.44265 | 2.2784 | 2.2467 | 2.1998 | 2.162 | 2.111 | 2.0814 | 2.0294 | 1.961 | 1.8978 | 1.8641 | 1.5896 | 1.6788 | 1.7084 | 2.2553 | 2.2002 | 2.1329 | 2.0686 | 1.9941 | 1.938 | 1.8584 | 1.7573 | 1.6584 | 1.6022
|  | NORTH KESSOCK | HE |  |  |  |  | 2.0557 | 2.0118 | 1.9516 | 1.9037 | 1.8373 | 1.7914 | 1.7169 | 1.622 | 1.5312 | 1.4792 | 0.98327 | 0.92102 | 0.54673 | 2.2743 | 2.2498 | 2.2059 | 2.1753 | 2.1273 | 2.1029 | 2.0549 | 1.9865 | 1.9253 | 1.8947 | 1.5671 | 1.6808 | 1.5839 | 2.2533 | 2.2124 | 2.1553 | 2.1084 | 2.0431 | 2.0022 | 1.9329 | 1.84 | 1.7512 | 1.7022
|  | NORTH KESSOCK | CF |  |  |  |  | 2.0629 | 2.0159 | 1.9761 | 1.9353 | 1.8812 | 1.8465 | 1.7894 | 1.7302 | 1.669 | 1.6037 | 1.3027 | 1.0659 | 0.5702 | 2.2784 | 2.2488 | 2.2243 | 2.1967 | 2.158 | 2.1355 | 2.0947 | 2.0498 | 2.0039 | 1.9508 | 1.7222 | 1.6573 | 1.3716 | 2.2594 | 2.2165 | 2.1778 | 2.138 | 2.0849 | 2.0543 | 1.9961 | 1.939 | 1.8778 | 1.8124
| BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | 0.521 | -1.0898 | -1.1633 | -1.2602 | -1.3337 | -1.4276 | -1.5357 | -1.6663 | -1.7776 | -1.9122 | -2.0327 | -2.3316 | -2.4367 | -2.4714 | -0.4449 | -0.48776 | -0.55 | -0.59898 | -0.66327 | -0.73367 | -0.82143 | -0.89184 | -0.98061 | -1.0602 | -1.2776 | -1.3837 | -1.7214 | -0.74286 | -0.79898 | -0.87653 | -0.94694 | -1.0398 | -1.1408 | -1.2653 | -1.3704 | -1.499 | -1.6122
|  | NOSTIE BRIDGE | EE |  |  |  |  | -1.0898 | -1.1633 | -1.2602 | -1.3337 | -1.4276 | -1.5357 | -1.6663 | -1.7776 | -1.9122 | -2.0327 | -2.3316 | -2.3867 | -2.4255 | -0.4449 | -0.48776 | -0.55 | -0.59898 | -0.66327 | -0.73367 | -0.82143 | -0.89184 | -0.98061 | -1.0602 | -1.2776 | -1.3837 | -1.5459 | -0.74286 | -0.79898 | -0.87653 | -0.94694 | -1.0398 | -1.1408 | -1.2653 | -1.3704 | -1.499 | -1.6122
|  | NOSTIE BRIDGE | HT |  |  |  |  | -1.0582 | -1.1235 | -1.1857 | -1.2541 | -1.3357 | -1.4031 | -1.5 | -1.6051 | -1.7122 | -1.8224 | -2.2327 | -2.4367 | -2.4714 | -0.41735 | -0.4551 | -0.49388 | -0.53265 | -0.58163 | -0.62143 | -0.68061 | -0.74694 | -0.81429 | -0.88469 | -1.1551 | -1.2765 | -1.298 | -0.72245 | -0.77041 | -0.81939 | -0.87143 | -0.94796 | -1.0102 | -1.101 | -1.2 | -1.3 | -1.4061
|  | NOSTIE BRIDGE | HE |  |  |  |  | -1.0592 | -1.1122 | -1.1582 | -1.2082 | -1.2745 | -1.3214 | -1.4041 | -1.4939 | -1.5878 | -1.6837 | -2.1449 | -2.2724 | -2.2939 | -0.42245 | -0.45204 | -0.48469 | -0.51735 | -0.56224 | -0.59592 | -0.65102 | -0.71122 | -0.77449 | -0.84286 | -1.1561 | -1.3041 | -1.449 | -0.72551 | -0.76735 | -0.80204 | -0.84184 | -0.89082 | -0.93571 | -1.0163 | -1.1 | -1.1888 | -1.2796
|  | NOSTIE BRIDGE | CF |  |  |  |  | -1.049 | -1.0939 | -1.1327 | -1.1867 | -1.2296 | -1.2857 | -1.3204 | -1.3898 | -1.4449 | -1.5102 | -1.8194 | -2.1235 | -2.2949 | -0.41327 | -0.44082 | -0.46429 | -0.5 | -0.53061 | -0.57041 | -0.59592 | -0.64796 | -0.6898 | -0.7398 | -1.0051 | -1.35 | -1.7214 | -0.71531 | -0.74286 | -0.76939 | -0.8051 | -0.84286 | -0.8949 | -0.92959 | -0.99388 | -1.0469 | -1.1082
| TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 5.535 | 6.2033 | 5.841 | 4.9655 | 3.5869 | 3.0431 | 0.29918 | -0.84367 | -1.9998 | -3.3682 | -5.3294 | -12.9059 | -21.7273 | -30.9937 | 10.2563 | 10.0614 | 9.1329 | 7.7196 | 7.4155 | 4.4145 | 3.3931 | 1.9778 | 0.61857 | -1.5212 | -9.958 | -20.1937 | -30.9182 | 8.6798 | 8.3482 | 7.34 | 5.7665 | 5.2798 | 2.041 | 0.8798 | -0.51408 | -2.0284 | -4.311
|  | OBAN | EE |  |  |  |  | 6.2033 | 5.841 | 5.4747 | 4.988 | 3.9012 | 2.1298 | 0.85531 | 0.19714 | -1.3835 | -2.5243 | -6.8937 | -15.0896 | -19.6447 | 10.2563 | 10.0614 | 9.8584 | 9.5931 | 8.5982 | 6.8216 | 5.8022 | 5.2767 | 3.7604 | 2.7461 | -1.5967 | -11.1314 | -15.9233 | 8.6798 | 8.3482 | 8.0033 | 7.5512 | 6.3665 | 4.3706 | 3.0696 | 2.4329 | 0.69918 | -0.51306
|  | OBAN | HT |  |  |  |  | 6.342 | 6.0165 | 4.9655 | 3.5869 | 3.0431 | 0.29918 | -0.84367 | -1.9998 | -2.8784 | -3.8039 | -8.3692 | -18.1641 | -27.0651 | 10.341 | 10.1778 | 9.1329 | 7.7196 | 7.4369 | 4.4145 | 3.4196 | 2.4808 | 1.8716 | 1.1482 | -3.1794 | -14.0018 | -23.4886 | 8.8196 | 8.5298 | 7.34 | 5.7665 | 5.2798 | 2.041 | 0.8798 | -0.28857 | -1.1386 | -2.0967
|  | OBAN | HE |  |  |  |  | 6.3431 | 6.1073 | 5.2686 | 4.092 | 3.3104 | 0.62878 | -0.53041 | -1.9998 | -3.3682 | -5.3294 | -12.9059 | -21.7273 | -30.9937 | 10.3359 | 10.2022 | 9.342 | 8.088 | 7.4155 | 4.4216 | 3.3931 | 1.9778 | 0.61857 | -1.5212 | -9.958 | -20.1937 | -30.9182 | 8.8206 | 8.6053 | 7.6502 | 6.2869 | 5.4676 | 2.3002 | 1.0727 | -0.51408 | -2.0284 | -4.311
|  | OBAN | CF |  |  |  |  | 6.389 | 6.2563 | 6.1104 | 5.9043 | 5.3247 | 4.3604 | 3.6676 | 3.0206 | 2.2818 | 1.3665 | -1.7243 | -4.6692 | -8.0988 | 10.3543 | 10.2727 | 10.1808 | 10.0522 | 9.4655 | 8.4186 | 7.7584 | 7.1931 | 6.5012 | 5.6206 | 2.488 | -0.45796 | -4.1386 | 8.8655 | 8.739 | 8.5992 | 8.4094 | 7.7604 | 6.642 | 5.8941 | 5.2308 | 4.4563 | 3.4808
| MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | NO | 1.31 | 6.2154 | 5.799 | 5.4225 | 5.049 | 4.7184 | 4.346 | 3.9113 | 3.3715 | 3.2756 | 2.8786 | 1.596 | 1.3184 | 1.3113 | 7.9572 | 7.7205 | 7.499 | 7.2684 | 7.0654 | 6.8031 | 6.4899 | 6.1133 | 6.1235 | 5.8613 | 4.896 | 4.3092 | 1.9378 | 7.3684 | 6.996 | 6.6592 | 6.3041 | 5.9939 | 5.6225 | 5.1919 | 4.6899 | 4.6766 | 4.3113
|  | OLD CRAIGIE ROAD | EE |  |  |  |  | 6.2154 | 5.799 | 5.4225 | 5.049 | 4.7184 | 4.346 | 3.9113 | 3.3715 | 3.2756 | 2.8786 | 1.596 | 1.7184 | 1.7103 | 7.9572 | 7.7205 | 7.499 | 7.2684 | 7.0654 | 6.8031 | 6.4899 | 6.1133 | 6.1235 | 5.8613 | 4.896 | 4.4501 | 3.5643 | 7.3684 | 6.996 | 6.6592 | 6.3041 | 5.9939 | 5.6225 | 5.1919 | 4.6899 | 4.6766 | 4.3113
|  | OLD CRAIGIE ROAD | HT |  |  |  |  | 6.2766 | 5.9041 | 5.5511 | 5.2531 | 4.947 | 4.6225 | 4.296 | 3.9052 | 3.5225 | 3.1266 | 1.7756 | 1.3184 | 1.3113 | 8.0297 | 7.8429 | 7.6623 | 7.5113 | 7.3429 | 7.1613 | 6.9848 | 6.7511 | 6.5143 | 6.2511 | 5.4766 | 5.1378 | 5.1123 | 7.4715 | 7.1643 | 6.8623 | 6.6133 | 6.3327 | 6.0307 | 5.7439 | 5.3633 | 4.9899 | 4.596
|  | OLD CRAIGIE ROAD | HE |  |  |  |  | 6.299 | 6.0103 | 5.7378 | 5.499 | 5.3011 | 5.0623 | 4.8011 | 4.4776 | 4.1531 | 3.8103 | 2.6154 | 1.8388 | 1.8225 | 8.0276 | 7.8613 | 7.6929 | 7.5378 | 7.4052 | 7.2348 | 7.0633 | 6.8256 | 6.5827 | 6.3143 | 5.3368 | 4.4633 | 3.6052 | 7.4848 | 7.2348 | 6.9878 | 6.7592 | 6.5735 | 6.3297 | 6.0929 | 5.7633 | 5.4399 | 5.099
|  | OLD CRAIGIE ROAD | CF |  |  |  |  | 6.3725 | 6.1786 | 6.0052 | 5.8552 | 5.7378 | 5.5919 | 5.4715 | 5.2766 | 5.1603 | 4.9817 | 4.2899 | 2.9582 | 1.8225 | 8.0654 | 7.9358 | 7.8194 | 7.7062 | 7.6103 | 7.4797 | 7.348 | 7.1776 | 7.0572 | 6.8797 | 6.0052 | 4.3092 | 1.9378 | 7.5419 | 7.3643 | 7.2052 | 7.0521 | 6.9327 | 6.7786 | 6.6286 | 6.445 | 6.3358 | 6.1664
| KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 1.1 | 1.9279 | 1.4034 | 22.1005 | 21.3046 | 20.6658 | 19.7515 | 19.2158 | 18.6515 | 18.0658 | 17.4587 | 15.5668 | 13.4781 | -9.9038 | 3.2034 | 23.0668 | 22.5505 | 21.9383 | 21.5271 | 20.7168 | 20.3801 | 20.0158 | 19.6495 | 19.0954 | 16.9862 | -5.2119 | -7.2609 | 23.2148 | 22.7454 | 22.125 | 21.3638 | 20.7924 | 19.8393 | 19.3526 | 18.8373 | 18.3128 | 17.7464
|  | OLDMELDRUM | EE |  |  |  |  | 1.9432 | 1.4258 | 22.2893 | 21.722 | 21.0138 | 20.2903 | 19.5485 | 18.9944 | 18.323 | 18.0138 | 16.0924 | 14.1924 | -8.2068 | 3.2442 | 23.1026 | 22.7628 | 22.3801 | 21.8556 | 21.2913 | 20.8077 | 20.4668 | 19.974 | 19.7005 | 18.2924 | -3.7385 | -4.7038 | 23.2148 | 22.7699 | 22.3393 | 21.8322 | 21.1648 | 20.4546 | 19.7791 | 19.2832 | 18.6393 | 18.3128
|  | OLDMELDRUM | HT |  |  |  |  | 1.9279 | 1.4034 | 22.1005 | 21.3046 | 20.6658 | 19.7515 | 19.2158 | 18.6515 | 18.0658 | 17.4587 | 15.7944 | 13.622 | -9.565 | 3.2034 | 23.0668 | 22.5505 | 21.9383 | 21.5271 | 20.7168 | 20.3801 | 20.0158 | 19.6495 | 19.225 | 18.0454 | -4.164 | -5.864 | 23.222 | 22.7454 | 22.125 | 21.3638 | 20.7924 | 19.8393 | 19.3526 | 18.8373 | 18.3128 | 17.7464
|  | OLDMELDRUM | HE |  |  |  |  | 1.985 | 1.5503 | 22.3893 | 21.7383 | 21.1556 | 20.2964 | 19.6607 | 19.1373 | 18.5832 | 17.9424 | 15.5668 | 13.4781 | -9.9038 | 3.2656 | 23.1607 | 22.7322 | 22.1913 | 21.7577 | 20.9822 | 20.522 | 20.1168 | 19.6822 | 19.0954 | 16.9862 | -5.2119 | -7.2609 | 23.2699 | 22.8842 | 22.3934 | 21.7607 | 21.2179 | 20.3209 | 19.726 | 19.224 | 18.6903 | 18.022
|  | OLDMELDRUM | CF |  |  |  |  | 2.1248 | 1.7901 | 22.8403 | 22.523 | 22.1046 | 21.7311 | 21.373 | 20.9434 | 20.6434 | 20.2546 | 18.5291 | 17.3362 | -5.4242 | 3.3952 | 23.3801 | 23.1444 | 22.9036 | 22.5638 | 22.2311 | 21.9566 | 21.6546 | 21.4158 | 21.1015 | 19.725 | -1.4834 | -2.6956 | 23.3913 | 23.1056 | 22.8495 | 22.5597 | 22.1587 | 21.7781 | 21.4424 | 21.0617 | 20.7771 | 20.4107
| THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | NO | NO | 0.813 | 9.6398 | 9.4337 | 9.1878 | 8.8918 | 8.5133 | 8.0969 | 7.6184 | 6.9469 | 6.3398 | 5.7816 | 3.3724 | 2.2684 | 1.3806 | 11.0255 | 10.8969 | 10.7082 | 10.4684 | 10.1898 | 9.8857 | 9.5408 | 9.0673 | 8.6378 | 8.249 | 6.4327 | 6.0138 | 5.9026 | 10.4536 | 10.2556 | 9.9883 | 9.6862 | 9.3444 | 8.974 | 8.5332 | 7.9005 | 7.324 | 6.7985
|  | ORMLIE | EE |  |  |  |  | 9.6398 | 9.4337 | 9.1878 | 8.8918 | 8.5133 | 8.0969 | 7.6184 | 6.9469 | 6.3398 | 5.7816 | 4.0194 | 3.6163 | 2.7735 | 11.0255 | 10.8969 | 10.7082 | 10.4684 | 10.1898 | 9.8857 | 9.5408 | 9.0673 | 8.6378 | 8.249 | 6.9969 | 7.0985 | 7.0199 | 10.4536 | 10.2556 | 9.9883 | 9.6862 | 9.3444 | 8.974 | 8.5332 | 7.9005 | 7.324 | 6.7985
|  | ORMLIE | HT |  |  |  |  | 9.7398 | 9.5602 | 9.3765 | 9.1704 | 8.9459 | 8.548 | 8.0673 | 7.5316 | 7.0724 | 6.65 | 4.6388 | 3.7296 | 2.8296 | 11.1041 | 11.001 | 10.8969 | 10.7755 | 10.5888 | 10.3204 | 10.0143 | 9.6429 | 9.3051 | 8.9602 | 7.4867 | 7.2066 | 7.1005 | 10.5628 | 10.3944 | 10.2209 | 10.025 | 9.7638 | 9.3964 | 8.9679 | 8.4648 | 8.0107 | 7.5617
|  | ORMLIE | HE |  |  |  |  | 9.7235 | 9.5694 | 9.4163 | 9.1745 | 8.8439 | 8.4755 | 8.0214 | 7.4092 | 6.8194 | 6.2061 | 3.3724 | 2.2684 | 1.3806 | 11.0867 | 10.9857 | 10.8714 | 10.6663 | 10.4214 | 10.1459 | 9.8153 | 9.3684 | 8.9408 | 8.4949 | 6.4327 | 6.0138 | 5.9026 | 10.5464 | 10.3985 | 10.2077 | 9.9607 | 9.6699 | 9.3413 | 8.9158 | 8.3321 | 7.7719 | 7.1862
|  | ORMLIE | CF |  |  |  |  | 9.7673 | 9.6704 | 9.5622 | 9.4531 | 9.3184 | 9.1714 | 8.9633 | 8.6684 | 8.3367 | 7.9786 | 5.8837 | 3.95 | 1.9133 | 11.1153 | 11.049 | 10.9745 | 10.8949 | 10.8041 | 10.6653 | 10.4918 | 10.2673 | 10.0245 | 9.7633 | 8.2286 | 7.1883 | 6.2423 | 10.5862 | 10.4954 | 10.3893 | 10.2832 | 10.1485 | 9.9566 | 9.7495 | 9.4913 | 9.1964 | 8.877
| DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | 0.282 | -0.31224 | -0.32653 | -0.33776 | -0.35306 | -0.37143 | -0.39184 | -0.40918 | -0.44694 | -0.48265 | -0.50204 | -0.58061 | -0.60408 | -0.6102 | 0.19388 | 0.19082 | 0.18061 | 0.16837 | 0.15408 | 0.13265 | 0.12143 | 0.093878 | 0.069388 | 0.061224 | 0.010204 | -0.011224 | -0.037755 | -0.23367 | -0.2449 | -0.25918 | -0.28265 | -0.30714 | -0.33673 | -0.35612 | -0.39286 | -0.42755 | -0.44592
|  | OTTER FERRY | EE |  |  |  |  | -0.31224 | -0.32653 | -0.33776 | -0.35306 | -0.37143 | -0.39184 | -0.40918 | -0.44694 | -0.48265 | -0.50204 | -0.58061 | -0.59184 | -0.60102 | 0.2 | 0.19082 | 0.18061 | 0.16837 | 0.15408 | 0.13265 | 0.12143 | 0.093878 | 0.069388 | 0.061224 | 0.010204 | -0.011224 | -0.033673 | -0.22755 | -0.2449 | -0.25918 | -0.28265 | -0.30714 | -0.33673 | -0.35612 | -0.39286 | -0.42755 | -0.44592
|  | OTTER FERRY | HT |  |  |  |  | -0.31122 | -0.31531 | -0.32245 | -0.33367 | -0.3449 | -0.36327 | -0.37449 | -0.39796 | -0.42857 | -0.4449 | -0.55 | -0.60408 | -0.6102 | 0.19388 | 0.19796 | 0.19082 | 0.18367 | 0.17245 | 0.15918 | 0.14898 | 0.13265 | 0.11531 | 0.1051 | 0.033673 | 0.0010204 | -0.0020408 | -0.23367 | -0.23163 | -0.24286 | -0.25816 | -0.27857 | -0.29898 | -0.31837 | -0.34592 | -0.37449 | -0.38878
|  | OTTER FERRY | HE |  |  |  |  | -0.31122 | -0.31327 | -0.31837 | -0.32755 | -0.3398 | -0.35204 | -0.36122 | -0.37959 | -0.39796 | -0.40714 | -0.51837 | -0.55204 | -0.55714 | 0.19388 | 0.19898 | 0.1949 | 0.18673 | 0.17959 | 0.16531 | 0.15714 | 0.14184 | 0.12857 | 0.12143 | 0.05 | 0.019388 | -0.0020408 | -0.23367 | -0.22857 | -0.23776 | -0.24694 | -0.26429 | -0.27959 | -0.2949 | -0.32041 | -0.34388 | -0.3551
|  | OTTER FERRY | CF |  |  |  |  | -0.3102 | -0.30714 | -0.31531 | -0.31837 | -0.32653 | -0.33367 | -0.3449 | -0.35102 | -0.36224 | -0.37449 | -0.44796 | -0.51429 | -0.55612 | 0.1949 | 0.20408 | 0.19694 | 0.19184 | 0.18469 | 0.17551 | 0.16633 | 0.1602 | 0.14796 | 0.1398 | 0.082653 | 0.020408 | -0.037755 | -0.23265 | -0.22143 | -0.23367 | -0.24184 | -0.25204 | -0.26224 | -0.27653 | -0.28878 | -0.30306 | -0.32041
| DUDHOPE | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | NO | 3.986 | 20.0382 | 19.877 | 19.5964 | 19.229 | 18.9148 | 18.5576 | 18.1801 | 17.8892 | 17.6382 | 17.4209 | 16.8913 | 16.7637 | 14.8362 | 21.4903 | 21.3443 | 21.1739 | 20.9903 | 20.829 | 20.6648 | 20.4852 | 20.3056 | 20.1505 | 20.0086 | 19.5209 | 19.9556 | 18.1219 | 21.7464 | 21.5994 | 21.3984 | 21.1454 | 20.9066 | 20.6515 | 20.3943 | 20.1882 | 20.0137 | 19.8617
|  | OVERGATE | EE |  |  |  |  | 20.0382 | 19.877 | 19.5964 | 19.229 | 18.9148 | 18.5576 | 18.1801 | 17.8892 | 17.6382 | 17.4209 | 16.8913 | 17.0178 | 15.0862 | 21.4903 | 21.3443 | 21.1739 | 20.9903 | 20.829 | 20.6648 | 20.4852 | 20.3056 | 20.1505 | 20.0086 | 19.5209 | 20.1566 | 19.377 | 21.7464 | 21.5994 | 21.3984 | 21.1454 | 20.9066 | 20.6515 | 20.3943 | 20.1882 | 20.0137 | 19.8617
|  | OVERGATE | HT |  |  |  |  | 20.0515 | 19.9076 | 19.6046 | 19.2494 | 18.9515 | 18.6668 | 18.4423 | 18.1137 | 17.8566 | 17.6607 | 17.0158 | 16.7637 | 14.8362 | 21.4984 | 21.3627 | 21.1943 | 21.0331 | 20.9005 | 20.775 | 20.6617 | 20.5076 | 20.3729 | 20.2494 | 19.7382 | 20.4423 | 20.379 | 21.7586 | 21.6219 | 21.4117 | 21.1709 | 20.9515 | 20.7423 | 20.5862 | 20.3699 | 20.1974 | 20.0648
|  | OVERGATE | HE |  |  |  |  | 20.075 | 19.9535 | 19.7107 | 19.3841 | 19.1005 | 18.7933 | 18.5035 | 18.2321 | 18.0454 | 17.9086 | 17.4586 | 17.2433 | 15.375 | 21.5199 | 21.3831 | 21.2301 | 21.0617 | 20.9127 | 20.7617 | 20.6025 | 20.428 | 20.2821 | 20.1433 | 19.5321 | 20.228 | 19.6505 | 21.779 | 21.6464 | 21.4678 | 21.2484 | 21.0362 | 20.8005 | 20.5831 | 20.3821 | 20.2403 | 20.129
|  | OVERGATE | CF |  |  |  |  | 20.1903 | 20.1178 | 19.9546 | 19.7586 | 19.5974 | 19.4382 | 19.2709 | 18.9933 | 18.8597 | 18.6974 | 18.0658 | 17.529 | 15.1443 | 21.6372 | 21.5535 | 21.4474 | 21.3362 | 21.2362 | 21.1372 | 21.0301 | 20.877 | 20.7729 | 20.6484 | 20.0494 | 19.9556 | 18.1219 | 21.9005 | 21.8219 | 21.6974 | 21.5586 | 21.425 | 21.2974 | 21.1627 | 20.9505 | 20.8382 | 20.7056
| CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | NO | 0 | 0.16067 | 0.15353 | 0.15251 | 0.15149 | 0.15149 | 0.14027 | 0.14027 | 0.13312 | 0.1321 | 0.13108 | 0.12802 | 0.127 | 0.11146 | 0.15126 | 0.14309 | 0.14309 | 0.14207 | 0.14207 | 0.13391 | 0.13391 | 0.12574 | 0.12472 | 0.12472 | 0.12472 | 0.13249 | 0.13045 | 0.15392 | 0.14576 | 0.14576 | 0.14474 | 0.14474 | 0.13352 | 0.13352 | 0.12637 | 0.12637 | 0.12535
|  | OVERSCAIG | EE |  |  |  |  | 0.16067 | 0.15353 | 0.15251 | 0.15149 | 0.15149 | 0.14027 | 0.14027 | 0.13312 | 0.1321 | 0.13108 | 0.12802 | 0.127 | 0.1135 | 0.15126 | 0.14309 | 0.14309 | 0.14207 | 0.14207 | 0.13391 | 0.13391 | 0.12574 | 0.12472 | 0.12472 | 0.12677 | 0.13249 | 0.13249 | 0.15392 | 0.14576 | 0.14576 | 0.14474 | 0.14474 | 0.13352 | 0.13352 | 0.12637 | 0.12637 | 0.12535
|  | OVERSCAIG | HT |  |  |  |  | 0.16067 | 0.16067 | 0.16067 | 0.15149 | 0.15149 | 0.14843 | 0.14843 | 0.14231 | 0.14027 | 0.14027 | 0.12904 | 0.127 | 0.11146 | 0.15126 | 0.15126 | 0.15023 | 0.14207 | 0.14207 | 0.14207 | 0.14207 | 0.13391 | 0.13289 | 0.13289 | 0.12779 | 0.13249 | 0.13147 | 0.15392 | 0.15392 | 0.1529 | 0.14474 | 0.14474 | 0.14168 | 0.14168 | 0.13454 | 0.13352 | 0.13352
|  | OVERSCAIG | HE |  |  |  |  | 0.16067 | 0.16067 | 0.16067 | 0.15251 | 0.15149 | 0.15149 | 0.15047 | 0.14027 | 0.14027 | 0.14129 | 0.12904 | 0.12802 | 0.11452 | 0.15126 | 0.15126 | 0.15023 | 0.14309 | 0.14207 | 0.14207 | 0.14105 | 0.13391 | 0.13391 | 0.13289 | 0.12677 | 0.13352 | 0.13249 | 0.15392 | 0.15392 | 0.1529 | 0.14576 | 0.14474 | 0.14474 | 0.1427 | 0.13352 | 0.13352 | 0.13454
|  | OVERSCAIG | CF |  |  |  |  | 0.16067 | 0.16067 | 0.16067 | 0.15353 | 0.15353 | 0.15251 | 0.15149 | 0.15149 | 0.14435 | 0.14333 | 0.13312 | 0.13006 | 0.11452 | 0.15126 | 0.15126 | 0.15126 | 0.14309 | 0.14309 | 0.14309 | 0.14207 | 0.14207 | 0.13493 | 0.13391 | 0.12472 | 0.13454 | 0.13045 | 0.15392 | 0.15392 | 0.15392 | 0.14576 | 0.14576 | 0.14576 | 0.14474 | 0.14474 | 0.1376 | 0.13556
| KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | YES | 0.197 | -1.2235 | -1.3071 | -1.3959 | -1.5082 | -1.6224 | -1.7541 | -1.901 | -2.0643 | -2.2265 | -2.3735 | -2.8214 | -3.0694 | -3.1296 | -0.24694 | -0.3 | -0.35204 | -0.42551 | -0.49898 | -0.58571 | -0.6602 | -0.76939 | -0.87347 | -0.96633 | -1.2184 | -1.3602 | -1.6408 | -0.68163 | -0.76224 | -0.8449 | -0.95408 | -1.0612 | -1.1918 | -1.3153 | -1.4786 | -1.6327 | -1.7714
|  | PARK | EE |  |  |  |  | -1.2235 | -1.3071 | -1.3959 | -1.5082 | -1.6224 | -1.7541 | -1.901 | -2.0643 | -2.2265 | -2.3735 | -2.8214 | -3.0245 | -3.0694 | -0.24694 | -0.3 | -0.35204 | -0.42551 | -0.49898 | -0.58571 | -0.6602 | -0.76939 | -0.87347 | -0.96633 | -1.2184 | -1.3408 | -1.4806 | -0.68163 | -0.76224 | -0.8449 | -0.95408 | -1.0612 | -1.1918 | -1.3153 | -1.4786 | -1.6327 | -1.7714
|  | PARK | HT |  |  |  |  | -1.202 | -1.2837 | -1.3765 | -1.4929 | -1.5969 | -1.7122 | -1.85 | -1.9969 | -2.1133 | -2.2561 | -2.801 | -3.0694 | -3.1296 | -0.22143 | -0.26429 | -0.31327 | -0.37755 | -0.42857 | -0.4949 | -0.56939 | -0.66224 | -0.73469 | -0.82143 | -1.1827 | -1.3327 | -1.3908 | -0.65306 | -0.72551 | -0.80816 | -0.9102 | -1.001 | -1.1051 | -1.2286 | -1.3704 | -1.4684 | -1.598
|  | PARK | HE |  |  |  |  | -1.2 | -1.252 | -1.3112 | -1.3918 | -1.4592 | -1.548 | -1.6673 | -1.7827 | -1.8684 | -1.9939 | -2.6378 | -2.9143 | -3.0378 | -0.22245 | -0.25816 | -0.30204 | -0.35714 | -0.40918 | -0.47347 | -0.55408 | -0.64388 | -0.71531 | -0.80612 | -1.2153 | -1.3602 | -1.4429 | -0.65204 | -0.7 | -0.75816 | -0.83878 | -0.89796 | -0.98776 | -1.1031 | -1.2296 | -1.3327 | -1.4561
|  | PARK | CF |  |  |  |  | -1.1867 | -1.2214 | -1.2643 | -1.3173 | -1.3571 | -1.4194 | -1.4857 | -1.5633 | -1.6265 | -1.6714 | -2.0806 | -2.5112 | -2.852 | -0.21735 | -0.24082 | -0.27041 | -0.31224 | -0.3398 | -0.38776 | -0.4398 | -0.50306 | -0.55816 | -0.58571 | -0.91531 | -1.2663 | -1.6408 | -0.63776 | -0.67245 | -0.71531 | -0.77041 | -0.80918 | -0.87143 | -0.93673 | -1.0163 | -1.0857 | -1.1245
| ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | NO | NO | 0.027 | 1.6286 | 1.5847 | 1.5255 | 1.4663 | 1.3959 | 1.3418 | 1.2531 | 1.1612 | 1.0653 | 0.98367 | 0.81837 | 0.74592 | 0.72347 | 2.2878 | 2.2561 | 2.2112 | 2.1735 | 2.1235 | 2.0918 | 2.0306 | 1.9684 | 1.9041 | 1.8469 | 1.7469 | 1.6959 | 1.55 | 1.9612 | 1.9133 | 1.85 | 1.7949 | 1.7224 | 1.6765 | 1.5867 | 1.498 | 1.401 | 1.3245
|  | PEDDIESTON | EE |  |  |  |  | 1.6286 | 1.5847 | 1.5255 | 1.4663 | 1.3959 | 1.3418 | 1.2531 | 1.1612 | 1.0653 | 0.98367 | 0.81837 | 0.78265 | 0.76122 | 2.2878 | 2.2561 | 2.2112 | 2.1735 | 2.1235 | 2.0918 | 2.0306 | 1.9684 | 1.9041 | 1.8469 | 1.7469 | 1.6959 | 1.6122 | 1.9612 | 1.9133 | 1.85 | 1.7949 | 1.7224 | 1.6765 | 1.5867 | 1.498 | 1.401 | 1.3245
|  | PEDDIESTON | HT |  |  |  |  | 1.6408 | 1.601 | 1.5531 | 1.5163 | 1.4612 | 1.4071 | 1.3398 | 1.2796 | 1.2071 | 1.1418 | 0.87959 | 0.74592 | 0.72347 | 2.3112 | 2.2847 | 2.25 | 2.2276 | 2.1908 | 2.1602 | 2.1143 | 2.0847 | 2.0367 | 1.9929 | 1.8112 | 1.7347 | 1.7224 | 1.9837 | 1.9418 | 1.8908 | 1.852 | 1.798 | 1.749 | 1.6816 | 1.6286 | 1.5602 | 1.4969
|  | PEDDIESTON | HE |  |  |  |  | 1.6398 | 1.6122 | 1.5755 | 1.55 | 1.5071 | 1.4673 | 1.4092 | 1.3592 | 1.2959 | 1.2398 | 0.93469 | 0.85612 | 0.84388 | 2.3082 | 2.2857 | 2.2551 | 2.2347 | 2.201 | 2.1745 | 2.1327 | 2.1041 | 2.0643 | 2.0255 | 1.8255 | 1.7469 | 1.6745 | 1.9816 | 1.952 | 1.9082 | 1.8806 | 1.8347 | 1.7969 | 1.7388 | 1.6969 | 1.6357 | 1.5796
|  | PEDDIESTON | CF |  |  |  |  | 1.6439 | 1.6194 | 1.5908 | 1.5663 | 1.5337 | 1.502 | 1.4704 | 1.4224 | 1.3765 | 1.352 | 1.1306 | 0.96633 | 0.86122 | 2.3102 | 2.2888 | 2.2694 | 2.2541 | 2.2255 | 2.1969 | 2.1735 | 2.1347 | 2.1 | 2.0898 | 1.9061 | 1.7378 | 1.55 | 1.9847 | 1.9612 | 1.9306 | 1.9082 | 1.8684 | 1.8276 | 1.799 | 1.749 | 1.702 | 1.6837
| PETERHEAD GRANGE | PETERHEAD GRANGE | MINIMUM HEADROOM | NK 11738 46516 | NO | YES | 6.003 | 6.6753 | 5.9508 | 4.858 | 3.6682 | 2.8182 | 0.84673 | -0.47469 | -2.1584 | -3.9033 | -5.8982 | -12.9543 | -19.6696 | -24.5947 | 9.7696 | 9.3349 | 8.6073 | 7.7339 | 7.2869 | 5.5298 | 4.7522 | 3.6706 | 2.5665 | 1.2247 | -4.5324 | -9.6733 | -15.0855 | 8.138 | 7.4706 | 6.4369 | 5.2461 | 4.4727 | 2.39 | 1.2216 | -0.33755 | -1.9171 | -3.7508
|  | PETERHEAD GRANGE | EE |  |  |  |  | 6.6753 | 5.9508 | 5.1467 | 4.3029 | 3.5478 | 2.1559 | 0.4702 | -1.0492 | -2.8543 | -4.6084 | -11.6594 | -18.2859 | -21.8029 | 9.7696 | 9.3349 | 8.8655 | 8.3767 | 7.8594 | 6.7104 | 5.5931 | 4.6502 | 3.3543 | 2.1359 | -2.4131 | -7.312 | -10.3447 | 8.138 | 7.4706 | 6.7298 | 5.9451 | 5.2461 | 3.8227 | 2.2441 | 0.85939 | -0.87327 | -2.509
|  | PETERHEAD GRANGE | HT |  |  |  |  | 6.7049 | 5.9559 | 4.858 | 3.6682 | 2.8182 | 0.84673 | -0.47469 | -2.1584 | -3.9033 | -5.8982 | -12.9543 | -19.6696 | -24.5947 | 9.8022 | 9.3788 | 8.6073 | 7.7339 | 7.2869 | 5.5298 | 4.7522 | 3.6706 | 2.5665 | 1.2247 | -2.9233 | -7.7835 | -11.8324 | 8.1829 | 7.5094 | 6.4369 | 5.2461 | 4.4727 | 2.39 | 1.2216 | -0.33755 | -1.9171 | -3.7508
|  | PETERHEAD GRANGE | HE |  |  |  |  | 6.7824 | 6.2998 | 5.5457 | 4.6855 | 3.9957 | 2.4222 | 1.2998 | -0.029796 | -1.4502 | -3.2696 | -11.238 | -17.9767 | -23.7427 | 9.8584 | 9.5267 | 8.9206 | 8.1941 | 7.6818 | 6.1369 | 5.2971 | 4.2563 | 3.142 | 1.5961 | -4.5324 | -9.6733 | -15.0855 | 8.2543 | 7.8155 | 7.0573 | 6.1686 | 5.492 | 3.7727 | 2.7329 | 1.4318 | 0.055306 | -1.7569
|  | PETERHEAD GRANGE | CF |  |  |  |  | 7.012 | 6.708 | 6.3896 | 6.0437 | 5.6192 | 4.9671 | 4.3804 | 4.0059 | 3.4386 | 2.7437 | -1.8655 | -7.2931 | -12.4355 | 10.0206 | 9.7931 | 9.5706 | 9.3318 | 8.9604 | 8.3257 | 7.7798 | 7.4043 | 6.8665 | 6.191 | 2.5033 | -1.2518 | -5.4069 | 8.4686 | 8.1859 | 7.9002 | 7.5839 | 7.142 | 6.4461 | 5.8471 | 5.5135 | 4.9451 | 4.2441
| PETERHEAD GRANGE | PETERHEAD NORTH STREET | MINIMUM HEADROOM | NK 13470 46450 | NO | YES | 4.148 | 5.2289 | 5.1462 | 5.0462 | 4.9289 | 4.8146 | 4.6779 | 4.4932 | 4.2738 | 4.082 | 3.8391 | 2.4656 | 1.6962 | 0.59562 | 10.2742 | 10.1773 | 10.0599 | 9.9242 | 9.7905 | 9.6334 | 9.4283 | 9.1803 | 8.964 | 8.7507 | 7.8405 | 7.6007 | 5.662 | 10.0875 | 9.9701 | 9.8385 | 9.6854 | 9.5354 | 9.366 | 9.0926 | 8.7834 | 8.5068 | 8.2262
|  | PETERHEAD NORTH STREET | EE |  |  |  |  | 5.2289 | 5.1462 | 5.0462 | 4.9289 | 4.8146 | 4.6779 | 4.4932 | 4.2738 | 4.082 | 3.8391 | 2.4656 | 1.7401 | 0.6344 | 10.2742 | 10.1773 | 10.0599 | 9.9242 | 9.7905 | 9.6334 | 9.4283 | 9.1803 | 8.964 | 8.7507 | 7.8405 | 7.6007 | 6.6283 | 10.0875 | 9.9701 | 9.8385 | 9.6854 | 9.5354 | 9.366 | 9.0926 | 8.7834 | 8.5068 | 8.2262
|  | PETERHEAD NORTH STREET | HT |  |  |  |  | 5.2524 | 5.1799 | 5.1013 | 5.0136 | 4.9126 | 4.7911 | 4.6371 | 4.4432 | 4.2534 | 4.0585 | 2.5901 | 1.6962 | 0.59562 | 10.3068 | 10.2232 | 10.1344 | 10.0324 | 9.916 | 9.7803 | 9.6079 | 9.3905 | 9.1813 | 8.966 | 7.9466 | 8.0528 | 7.9181 | 10.1181 | 10.013 | 9.9017 | 9.7762 | 9.6446 | 9.4936 | 9.2477 | 8.966 | 8.6885 | 8.4048
|  | PETERHEAD NORTH STREET | HE |  |  |  |  | 5.2534 | 5.1891 | 5.1248 | 5.0442 | 4.9554 | 4.8452 | 4.6983 | 4.5217 | 4.3442 | 4.1554 | 2.7085 | 2.1605 | 1.0742 | 10.3048 | 10.2262 | 10.1456 | 10.0487 | 9.9405 | 9.8068 | 9.6313 | 9.4262 | 9.2171 | 8.9987 | 7.9701 | 8.065 | 7.1109 | 10.1181 | 10.0415 | 9.9671 | 9.8742 | 9.7793 | 9.663 | 9.4732 | 9.263 | 9.0262 | 8.7262
|  | PETERHEAD NORTH STREET | CF |  |  |  |  | 5.2768 | 5.2452 | 5.2075 | 5.1656 | 5.1126 | 5.0575 | 4.9901 | 4.9003 | 4.8115 | 4.7197 | 4.1105 | 3.0503 | 1.2048 | 10.3364 | 10.2936 | 10.2487 | 10.1946 | 10.1344 | 10.064 | 9.9813 | 9.8722 | 9.766 | 9.6528 | 8.7885 | 7.9334 | 5.662 | 10.1487 | 10.112 | 10.0701 | 10.0252 | 9.9691 | 9.912 | 9.8436 | 9.7538 | 9.664 | 9.5579
| FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | NO | 0.539 | 6.0071 | 5.7704 | 5.5663 | 5.3347 | 5.0694 | 4.8286 | 4.5622 | 4.2551 | 4.0163 | 3.8133 | 3.2898 | 3.0847 | 2.4367 | 7.298 | 7.1612 | 7.0439 | 6.9041 | 6.7398 | 6.6 | 6.4245 | 6.2184 | 6.0643 | 5.9235 | 5.5051 | 5.6153 | 5.0286 | 6.5429 | 6.3337 | 6.151 | 5.9378 | 5.6949 | 5.4755 | 5.2255 | 4.9398 | 4.7173 | 4.5265
|  | PINEGROVE | EE |  |  |  |  | 6.0071 | 5.7704 | 5.5663 | 5.3347 | 5.0694 | 4.8286 | 4.5622 | 4.2551 | 4.0163 | 3.8133 | 3.2898 | 3.2041 | 2.5235 | 7.298 | 7.1612 | 7.0439 | 6.9041 | 6.7398 | 6.6 | 6.4245 | 6.2184 | 6.0643 | 5.9235 | 5.5051 | 5.6153 | 5.2888 | 6.5429 | 6.3337 | 6.151 | 5.9378 | 5.6949 | 5.4755 | 5.2255 | 4.9398 | 4.7173 | 4.5265
|  | PINEGROVE | HT |  |  |  |  | 6.0714 | 5.8571 | 5.6765 | 5.4724 | 5.2745 | 5.0388 | 4.8224 | 4.6184 | 4.3949 | 4.2061 | 3.4439 | 3.0847 | 2.4367 | 7.3531 | 7.2388 | 7.1408 | 7.0276 | 6.9194 | 6.7878 | 6.6561 | 6.5367 | 6.3969 | 6.2704 | 5.7408 | 5.8031 | 5.7724 | 6.5949 | 6.4194 | 6.2602 | 6.0755 | 5.898 | 5.6837 | 5.4857 | 5.3 | 5.0918 | 4.9102
|  | PINEGROVE | HE |  |  |  |  | 6.0714 | 5.8806 | 5.7245 | 5.5439 | 5.3745 | 5.1714 | 4.9796 | 4.802 | 4.602 | 4.4429 | 3.6745 | 3.4776 | 2.8561 | 7.351 | 7.2429 | 7.1551 | 7.05 | 6.951 | 6.8347 | 6.7112 | 6.598 | 6.4643 | 6.351 | 5.7878 | 5.8224 | 5.5439 | 6.5959 | 6.4408 | 6.302 | 6.1408 | 5.9878 | 5.8061 | 5.6286 | 5.4684 | 5.2816 | 5.1306
|  | PINEGROVE | CF |  |  |  |  | 6.1276 | 5.9816 | 5.8265 | 5.6786 | 5.5367 | 5.3673 | 5.2296 | 5.0653 | 4.9092 | 4.8286 | 4.2204 | 3.749 | 2.8694 | 7.3806 | 7.3 | 7.2112 | 7.1214 | 7.0449 | 6.9408 | 6.8469 | 6.7327 | 6.6214 | 6.5602 | 6.0265 | 5.7357 | 5.0286 | 6.6337 | 6.5163 | 6.3867 | 6.2592 | 6.1367 | 5.9867 | 5.8622 | 5.7133 | 5.5673 | 5.4959
| TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 2.06 | 1.0799 | 0.94417 | 0.77581 | 0.58805 | 0.42377 | 0.21152 | -0.055827 | -0.30685 | -0.5844 | -0.81705 | -1.5538 | -1.9364 | -2.3316 | 1.9817 | 1.9225 | 1.8551 | 1.7664 | 1.6786 | 1.5725 | 1.4409 | 1.3123 | 1.1551 | 1.0225 | 0.55514 | 0.41649 | -0.066158 | 1.5328 | 1.4073 | 1.2512 | 1.0777 | 0.92772 | 0.73282 | 0.48384 | 0.25017 | -0.0079949 | -0.22432
|  | PITLOCHRY | EE |  |  |  |  | 1.0799 | 0.94417 | 0.77581 | 0.58805 | 0.42377 | 0.21152 | -0.055827 | -0.30685 | -0.5844 | -0.81705 | -1.5538 | -1.8854 | -2.302 | 1.9817 | 1.9225 | 1.8551 | 1.7664 | 1.6786 | 1.5725 | 1.4409 | 1.3123 | 1.1551 | 1.0225 | 0.55514 | 0.41649 | 0.10731 | 1.5328 | 1.4073 | 1.2512 | 1.0777 | 0.92772 | 0.73282 | 0.48384 | 0.25017 | -0.0079949 | -0.22432
|  | PITLOCHRY | HT |  |  |  |  | 1.1289 | 0.99826 | 0.85642 | 0.71662 | 0.55234 | 0.36662 | 0.17785 | -0.066031 | -0.30583 | -0.5293 | -1.4619 | -1.9364 | -2.3316 | 2.0011 | 1.949 | 1.8909 | 1.8317 | 1.7602 | 1.6735 | 1.5827 | 1.4664 | 1.3531 | 1.2439 | 0.74698 | 0.65221 | 0.60527 | 1.5798 | 1.4624 | 1.3318 | 1.2063 | 1.0583 | 0.88588 | 0.71649 | 0.49098 | 0.26956 | 0.063434
|  | PITLOCHRY | HE |  |  |  |  | 1.1299 | 1.037 | 0.93601 | 0.83397 | 0.71254 | 0.56662 | 0.42683 | 0.22989 | 0.042133 | -0.13236 | -1.013 | -1.4252 | -1.8775 | 1.999 | 1.9592 | 1.9174 | 1.8745 | 1.8133 | 1.7398 | 1.6643 | 1.5602 | 1.4643 | 1.3704 | 0.83065 | 0.65119 | 0.3369 | 1.5808 | 1.4971 | 1.4022 | 1.3104 | 1.1991 | 1.0655 | 0.93792 | 0.75425 | 0.57874 | 0.41854
|  | PITLOCHRY | CF |  |  |  |  | 1.1523 | 1.086 | 1.0085 | 0.9105 | 0.83499 | 0.73703 | 0.62989 | 0.50336 | 0.42274 | 0.32581 | -0.23338 | -0.87726 | -1.6418 | 2.0082 | 1.9786 | 1.9439 | 1.9011 | 1.8643 | 1.8102 | 1.746 | 1.6715 | 1.6143 | 1.5531 | 1.1572 | 0.68894 | -0.066158 | 1.6042 | 1.543 | 1.4706 | 1.3828 | 1.3124 | 1.2236 | 1.1236 | 1.0053 | 0.93282 | 0.84201
| ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 1.19 | 1.0849 | 0.97371 | 0.82269 | 0.69514 | 0.588 | 0.44412 | 0.26963 | 0.021673 | -0.19567 | -0.4171 | -0.91506 | -1.0151 | -1.0436 | 2.64 | 2.5717 | 2.4656 | 2.387 | 2.3186 | 2.2217 | 2.1084 | 1.9278 | 1.7717 | 1.6104 | 1.2329 | 1.1186 | 0.82167 | 1.9931 | 1.8819 | 1.7298 | 1.6094 | 1.5104 | 1.3696 | 1.2002 | 0.95637 | 0.75331 | 0.54412
|  | POLLACHAR | EE |  |  |  |  | 1.0849 | 0.97371 | 0.82269 | 0.69514 | 0.588 | 0.44412 | 0.26963 | 0.021673 | -0.19567 | -0.4171 | -0.91506 | -0.96914 | -1.0059 | 2.64 | 2.5778 | 2.4656 | 2.387 | 2.3186 | 2.2217 | 2.1084 | 1.9278 | 1.7717 | 1.6104 | 1.2329 | 1.1186 | 0.93596 | 1.9931 | 1.8819 | 1.7298 | 1.6094 | 1.5104 | 1.3696 | 1.2002 | 0.95637 | 0.75331 | 0.54412
|  | POLLACHAR | HT |  |  |  |  | 1.1268 | 1.0013 | 0.91351 | 0.82984 | 0.71963 | 0.61045 | 0.47984 | 0.29514 | 0.03698 | -0.17731 | -0.77016 | -1.0151 | -1.0436 | 2.6666 | 2.5717 | 2.5258 | 2.4839 | 2.4278 | 2.3666 | 2.286 | 2.1543 | 1.9543 | 1.7992 | 1.4002 | 1.2472 | 1.2319 | 2.0431 | 1.9145 | 1.8319 | 1.7594 | 1.6564 | 1.5564 | 1.4319 | 1.2635 | 1.0145 | 0.80841
|  | POLLACHAR | HE |  |  |  |  | 1.1278 | 1.0707 | 0.95943 | 0.87269 | 0.81045 | 0.72678 | 0.61453 | 0.47984 | 0.28392 | 0.10331 | -0.63343 | -0.78343 | -0.79771 | 2.6676 | 2.6329 | 2.54 | 2.4911 | 2.4574 | 2.4074 | 2.336 | 2.237 | 2.088 | 1.9472 | 1.4319 | 1.2604 | 1.0992 | 2.0441 | 1.986 | 1.8676 | 1.7839 | 1.7288 | 1.6492 | 1.5431 | 1.4156 | 1.2288 | 1.0523
|  | POLLACHAR | CF |  |  |  |  | 1.14 | 1.089 | 1.037 | 0.92882 | 0.87882 | 0.81045 | 0.74208 | 0.63494 | 0.52576 | 0.45024 | -0.13343 | -0.562 | -0.75792 | 2.6717 | 2.6472 | 2.6135 | 2.5217 | 2.49 | 2.4492 | 2.4033 | 2.3268 | 2.2411 | 2.1809 | 1.6931 | 1.2349 | 0.82167 | 2.0564 | 2.0074 | 1.9533 | 1.8329 | 1.786 | 1.7166 | 1.6513 | 1.5482 | 1.438 | 1.3676
| FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | NO | 0 | 0.10269 | 0.10065 | 0.09351 | 0.09351 | 0.09249 | 0.09249 | 0.085347 | 0.084327 | 0.084327 | 0.076163 | 0.074122 | 0.074122 | 0.064102 | 0.097776 | 0.096755 | 0.089612 | 0.089612 | 0.088592 | 0.088592 | 0.081449 | 0.081449 | 0.081449 | 0.074306 | 0.072265 | 0.076765 | 0.074724 | 0.10126 | 0.10023 | 0.093092 | 0.092071 | 0.092071 | 0.092071 | 0.083908 | 0.083908 | 0.083908 | 0.075745
|  | POOR HOUSE | EE |  |  |  |  | 0.10269 | 0.10065 | 0.09351 | 0.09351 | 0.09249 | 0.09249 | 0.085347 | 0.084327 | 0.084327 | 0.076163 | 0.074122 | 0.074122 | 0.065122 | 0.097776 | 0.096755 | 0.089612 | 0.089612 | 0.088592 | 0.088592 | 0.081449 | 0.081449 | 0.081449 | 0.074306 | 0.072265 | 0.076765 | 0.076765 | 0.10126 | 0.10023 | 0.093092 | 0.092071 | 0.092071 | 0.092071 | 0.083908 | 0.083908 | 0.083908 | 0.075745
|  | POOR HOUSE | HT |  |  |  |  | 0.10269 | 0.10065 | 0.10065 | 0.10065 | 0.09351 | 0.09351 | 0.09249 | 0.09249 | 0.09249 | 0.084327 | 0.076163 | 0.075143 | 0.065122 | 0.097776 | 0.096755 | 0.096755 | 0.096755 | 0.089612 | 0.089612 | 0.088592 | 0.088592 | 0.088592 | 0.081449 | 0.073286 | 0.076765 | 0.076765 | 0.10126 | 0.10023 | 0.10023 | 0.10023 | 0.092071 | 0.092071 | 0.091051 | 0.091051 | 0.091051 | 0.083908
|  | POOR HOUSE | HE |  |  |  |  | 0.10269 | 0.10065 | 0.10065 | 0.10065 | 0.09351 | 0.09351 | 0.09351 | 0.09249 | 0.091469 | 0.084327 | 0.074122 | 0.074122 | 0.064102 | 0.097776 | 0.096755 | 0.096755 | 0.096755 | 0.089612 | 0.089612 | 0.089612 | 0.088592 | 0.088592 | 0.081449 | 0.072265 | 0.076765 | 0.075745 | 0.10126 | 0.10023 | 0.10023 | 0.099214 | 0.092071 | 0.092071 | 0.092071 | 0.092071 | 0.091051 | 0.083908
|  | POOR HOUSE | CF |  |  |  |  | 0.10269 | 0.10269 | 0.10065 | 0.10065 | 0.10065 | 0.09351 | 0.09351 | 0.09351 | 0.09351 | 0.09351 | 0.083306 | 0.074122 | 0.065122 | 0.097776 | 0.097776 | 0.096755 | 0.096755 | 0.096755 | 0.089612 | 0.089612 | 0.089612 | 0.089612 | 0.089612 | 0.081449 | 0.076765 | 0.074724 | 0.10126 | 0.10126 | 0.10023 | 0.10023 | 0.10023 | 0.092071 | 0.092071 | 0.092071 | 0.092071 | 0.092071
| PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | NO | YES | 1.161 | -0.82176 | -0.84829 | -0.88706 | -0.91461 | -0.95849 | -0.99216 | -1.0442 | -1.1177 | -1.1544 | -1.2095 | -1.332 | -1.3779 | -1.3881 | -0.56971 | -0.58298 | -0.59931 | -0.61359 | -0.63808 | -0.66461 | -0.69931 | -0.75339 | -0.7789 | -0.81767 | -0.91155 | -0.93808 | -1.0524 | -0.66155 | -0.68604 | -0.72278 | -0.75135 | -0.79318 | -0.82686 | -0.87686 | -0.94931 | -0.99012 | -1.0442
|  | PORT ASKAIG | EE |  |  |  |  | -0.82176 | -0.84829 | -0.88706 | -0.91461 | -0.95849 | -0.99216 | -1.0442 | -1.1177 | -1.1544 | -1.2095 | -1.332 | -1.3534 | -1.3677 | -0.56971 | -0.58298 | -0.59931 | -0.61359 | -0.63808 | -0.66461 | -0.69931 | -0.75339 | -0.7789 | -0.81767 | -0.91155 | -0.93808 | -0.98502 | -0.66155 | -0.68604 | -0.72278 | -0.75135 | -0.79318 | -0.82686 | -0.87686 | -0.94931 | -0.99012 | -1.0442
|  | PORT ASKAIG | HT |  |  |  |  | -0.80339 | -0.8238 | -0.85135 | -0.87686 | -0.91053 | -0.9289 | -0.98502 | -1.0289 | -1.0758 | -1.1258 | -1.2932 | -1.3779 | -1.3881 | -0.56053 | -0.57176 | -0.58604 | -0.59829 | -0.61155 | -0.6238 | -0.66155 | -0.6891 | -0.72278 | -0.75747 | -0.86971 | -0.92176 | -0.92686 | -0.64216 | -0.66461 | -0.69114 | -0.71563 | -0.74829 | -0.77073 | -0.82992 | -0.8738 | -0.91869 | -0.96869
|  | PORT ASKAIG | HE |  |  |  |  | -0.80339 | -0.8238 | -0.84114 | -0.86155 | -0.89012 | -0.90645 | -0.93808 | -0.98808 | -1.0238 | -1.0687 | -1.2697 | -1.3299 | -1.3381 | -0.56359 | -0.57176 | -0.58196 | -0.59216 | -0.60441 | -0.61665 | -0.63298 | -0.66665 | -0.69216 | -0.7289 | -0.86971 | -0.92482 | -0.96257 | -0.64216 | -0.66461 | -0.68094 | -0.69931 | -0.72992 | -0.74522 | -0.77686 | -0.8289 | -0.86665 | -0.91053
|  | PORT ASKAIG | CF |  |  |  |  | -0.80237 | -0.81665 | -0.83604 | -0.85135 | -0.86971 | -0.89318 | -0.90543 | -0.9391 | -0.96869 | -0.98604 | -1.1299 | -1.2728 | -1.3636 | -0.56053 | -0.56869 | -0.57788 | -0.58604 | -0.59522 | -0.60747 | -0.61461 | -0.63094 | -0.65033 | -0.66461 | -0.78604 | -0.92788 | -1.0524 | -0.64114 | -0.65543 | -0.67278 | -0.69012 | -0.70645 | -0.72992 | -0.74012 | -0.77073 | -0.80033 | -0.82073
| PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 3.186 | -0.65478 | -0.74866 | -0.86193 | -0.9405 | -1.0374 | -1.1089 | -1.214 | -1.366 | -1.5119 | -1.5987 | -1.8823 | -1.9517 | -2.3291 | -0.23213 | -0.28621 | -0.34744 | -0.39131 | -0.44131 | -0.48213 | -0.58417 | -0.67601 | -0.77397 | -0.84438 | -1.0709 | -0.95417 | -1.1603 | -0.43989 | -0.52866 | -0.62968 | -0.69703 | -0.78478 | -0.84601 | -0.94397 | -1.0909 | -1.2256 | -1.3052
|  | PORT ELLEN | EE |  |  |  |  | -0.65478 | -0.74866 | -0.86193 | -0.9405 | -1.0374 | -1.1089 | -1.1915 | -1.366 | -1.5119 | -1.5987 | -1.8823 | -1.916 | -2.2985 | -0.23213 | -0.28621 | -0.34744 | -0.39131 | -0.44131 | -0.48213 | -0.53213 | -0.6658 | -0.77397 | -0.84438 | -1.0709 | -0.95417 | -1.0542 | -0.43989 | -0.52866 | -0.62968 | -0.69703 | -0.78478 | -0.84601 | -0.92458 | -1.0909 | -1.2256 | -1.3052
|  | PORT ELLEN | HT |  |  |  |  | -0.64458 | -0.71703 | -0.81907 | -0.88233 | -0.96091 | -1.0293 | -1.214 | -1.3303 | -1.4385 | -1.5262 | -1.8201 | -1.9517 | -2.3291 | -0.21478 | -0.26682 | -0.31887 | -0.35152 | -0.39336 | -0.42805 | -0.58417 | -0.67601 | -0.75152 | -0.81172 | -0.99233 | -0.89295 | -0.90315 | -0.4154 | -0.49499 | -0.58478 | -0.63784 | -0.70825 | -0.7654 | -0.94397 | -1.0603 | -1.1583 | -1.2368
|  | PORT ELLEN | HE |  |  |  |  | -0.6456 | -0.70478 | -0.79866 | -0.85274 | -0.92213 | -0.97825 | -1.0385 | -1.1599 | -1.2742 | -1.3732 | -1.7538 | -1.8323 | -2.1985 | -0.21478 | -0.25968 | -0.30866 | -0.34233 | -0.37805 | -0.40968 | -0.44744 | -0.54846 | -0.63927 | -0.71989 | -0.99438 | -0.90723 | -0.99193 | -0.4154 | -0.48682 | -0.56744 | -0.6154 | -0.67662 | -0.72458 | -0.7807 | -0.89091 | -0.99805 | -1.0909
|  | PORT ELLEN | CF |  |  |  |  | -0.63948 | -0.68948 | -0.76295 | -0.80784 | -0.86193 | -0.91295 | -0.94356 | -0.99254 | -1.064 | -1.1119 | -1.466 | -1.7221 | -2.1974 | -0.21376 | -0.25254 | -0.29336 | -0.31784 | -0.34948 | -0.38009 | -0.39744 | -0.43111 | -0.48825 | -0.52907 | -0.82499 | -0.91948 | -1.1603 | -0.41438 | -0.47356 | -0.53682 | -0.5756 | -0.62458 | -0.66948 | -0.69601 | -0.74397 | -0.81233 | -0.85519
| DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | NO | 1.345 | 2.3959 | 2.2541 | 2.0816 | 1.8837 | 1.7092 | 1.2469 | 0.98776 | 0.64082 | 0.24898 | -0.11429 | -0.84694 | -1.1092 | -1.4176 | 3.511 | 3.4386 | 3.3273 | 3.2059 | 3.1059 | 2.8539 | 2.6967 | 2.4957 | 2.2651 | 2.058 | 1.612 | 1.6569 | 1.0927 | 3.0896 | 2.9559 | 2.8018 | 2.6365 | 2.4865 | 2.0896 | 1.8794 | 1.5651 | 1.2284 | 0.91408
|  | PORTREE | EE |  |  |  |  | 2.3959 | 2.2541 | 2.0816 | 1.8837 | 1.7092 | 1.2469 | 1.0071 | 0.64082 | 0.24898 | -0.11429 | -0.84694 | -0.99694 | -1.3196 | 3.511 | 3.4386 | 3.3273 | 3.2059 | 3.1059 | 2.8539 | 2.6967 | 2.4957 | 2.2651 | 2.058 | 1.612 | 1.6569 | 1.3845 | 3.0896 | 2.9559 | 2.8018 | 2.6365 | 2.4865 | 2.0896 | 1.8794 | 1.5651 | 1.2284 | 0.91408
|  | PORTREE | HT |  |  |  |  | 2.4235 | 2.3041 | 2.1561 | 2.0173 | 1.8622 | 1.2806 | 0.98776 | 0.65612 | 0.40714 | 0.13673 | -0.70612 | -1.1092 | -1.4176 | 3.5335 | 3.4947 | 3.4192 | 3.3478 | 3.2559 | 2.9743 | 2.8314 | 2.6365 | 2.4835 | 2.3202 | 1.7773 | 1.7416 | 1.709 | 3.1294 | 3.0059 | 2.8733 | 2.7447 | 2.6029 | 2.1284 | 1.8814 | 1.5865 | 1.359 | 1.1212
|  | PORTREE | HE |  |  |  |  | 2.4224 | 2.3337 | 2.2255 | 2.1184 | 1.9949 | 1.5969 | 1.4827 | 1.2276 | 0.96633 | 0.7 | -0.44286 | -0.70204 | -0.9951 | 3.5324 | 3.4978 | 3.4376 | 3.3784 | 3.2988 | 3.0916 | 3.0253 | 2.8641 | 2.711 | 2.5508 | 1.8753 | 1.8488 | 1.5763 | 3.1284 | 3.0324 | 2.9324 | 2.8335 | 2.7212 | 2.3916 | 2.2865 | 2.0661 | 1.8416 | 1.612
|  | PORTREE | CF |  |  |  |  | 2.4837 | 2.4041 | 2.2867 | 2.1857 | 2.099 | 1.7673 | 1.6735 | 1.5663 | 1.4051 | 1.2173 | 0.29286 | -0.30816 | -0.91959 | 3.5682 | 3.5314 | 3.4814 | 3.4131 | 3.3661 | 3.1957 | 3.1212 | 3.0294 | 2.9437 | 2.8233 | 2.2182 | 1.8416 | 1.0927 | 3.1978 | 3.0937 | 2.9916 | 2.8998 | 2.8192 | 2.5508 | 2.4631 | 2.3651 | 2.2294 | 2.0682
| MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | NO | 0.082 | -0.57935 | -0.62629 | -0.67424 | -0.73445 | -0.81914 | -0.91506 | -1.0416 | -1.1977 | -1.3518 | -1.4987 | -2.0242 | -2.3691 | -2.4375 | 0.014531 | -0.0079184 | -0.030367 | -0.057918 | -0.11608 | -0.19363 | -0.25996 | -0.37016 | -0.47833 | -0.5671 | -0.79261 | -0.94976 | -1.111 | -0.23853 | -0.30486 | -0.37118 | -0.4518 | -0.52935 | -0.61812 | -0.73139 | -0.87016 | -1.0079 | -1.1324
|  | PORTSOY | EE |  |  |  |  | -0.57935 | -0.62629 | -0.67424 | -0.73445 | -0.81914 | -0.91506 | -1.0416 | -1.1977 | -1.3518 | -1.4987 | -2.012 | -2.3314 | -2.4018 | 0.014531 | -0.0079184 | -0.030367 | -0.057918 | -0.11608 | -0.19363 | -0.25996 | -0.37016 | -0.47833 | -0.5671 | -0.79261 | -0.94976 | -1.0947 | -0.23853 | -0.30486 | -0.37118 | -0.4518 | -0.52935 | -0.61812 | -0.73139 | -0.87016 | -1.0079 | -1.1324
|  | PORTSOY | HT |  |  |  |  | -0.562 | -0.60384 | -0.64873 | -0.7069 | -0.77833 | -0.86608 | -0.99261 | -1.1334 | -1.2549 | -1.3936 | -2.0242 | -2.3691 | -2.4375 | 0.028816 | 0.011469 | -0.006898 | -0.027306 | -0.046694 | -0.078327 | -0.14976 | -0.23547 | -0.28955 | -0.37118 | -0.7171 | -0.86608 | -0.89567 | -0.2171 | -0.28037 | -0.34669 | -0.42016 | -0.48547 | -0.56404 | -0.67935 | -0.8069 | -0.91608 | -1.0416
|  | PORTSOY | HE |  |  |  |  | -0.56098 | -0.58649 | -0.62016 | -0.64873 | -0.67731 | -0.71302 | -0.78649 | -0.88445 | -0.96302 | -1.0579 | -1.6151 | -1.9661 | -2.111 | 0.027796 | 0.01351 | -0.0048571 | -0.023224 | -0.038531 | -0.06098 | -0.088531 | -0.16302 | -0.20384 | -0.27424 | -0.61302 | -0.80078 | -0.96914 | -0.21506 | -0.2518 | -0.29873 | -0.33445 | -0.37118 | -0.42016 | -0.49873 | -0.58853 | -0.65894 | -0.74771
|  | PORTSOY | CF |  |  |  |  | -0.55384 | -0.57424 | -0.58955 | -0.60894 | -0.63445 | -0.65894 | -0.67935 | -0.71098 | -0.73955 | -0.77016 | -1.0773 | -1.4396 | -1.7661 | 0.029837 | 0.020653 | 0.010449 | -0.0017959 | -0.018122 | -0.033429 | -0.045673 | -0.067102 | -0.10078 | -0.14669 | -0.40894 | -0.71404 | -1.111 | -0.20384 | -0.22833 | -0.25282 | -0.27731 | -0.30894 | -0.34261 | -0.36914 | -0.4069 | -0.44465 | -0.48445
| WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 0.894 | 1.4963 | 0.98606 | 0.40647 | 16.7662 | 16.0998 | 15.3733 | 14.4356 | 13.4447 | 12.4631 | 11.5856 | 7.1743 | 4.5111 | -13.6134 | 5.108 | 4.8141 | 20.5784 | 20.1662 | 19.6856 | 19.158 | 18.51 | 17.8253 | 17.1427 | 16.5447 | 13.2376 | -4.3499 | -7.3091 | 3.4889 | 19.56 | 19.0488 | 18.4968 | 17.9151 | 17.2182 | 16.3039 | 15.3927 | 14.46 | 13.6304
|  | QUEENS LANE NORTH | EE |  |  |  |  | 1.4963 | 0.98606 | 0.40647 | 16.7662 | 16.0998 | 15.3733 | 14.4356 | 13.4447 | 12.4631 | 11.5856 | 7.5835 | 4.9856 | -13.2818 | 5.108 | 4.8141 | 20.5784 | 20.1662 | 19.6856 | 19.158 | 18.51 | 17.8253 | 17.1427 | 16.5447 | 14.1223 | -3.503 | -5.4438 | 3.4889 | 19.56 | 19.0488 | 18.4968 | 17.9151 | 17.2182 | 16.3039 | 15.3927 | 14.46 | 13.6304
|  | QUEENS LANE NORTH | HT |  |  |  |  | 1.8177 | 1.4616 | 1.0524 | 17.6192 | 17.158 | 16.6498 | 15.8417 | 14.9019 | 13.9896 | 13.0437 | 8.2774 | 4.8662 | -13.2349 | 5.3162 | 5.1243 | 21.006 | 20.7835 | 20.5009 | 20.1407 | 19.6835 | 19.1182 | 18.5815 | 18.0121 | 15.4264 | -1.955 | -2.1744 | 3.7195 | 19.908 | 19.5182 | 19.1396 | 18.7019 | 18.2233 | 17.4825 | 16.6121 | 15.7702 | 14.8927
|  | QUEENS LANE NORTH | HE |  |  |  |  | 1.7238 | 1.3116 | 0.87382 | 17.3702 | 16.8121 | 16.1672 | 15.3376 | 14.3019 | 13.3111 | 12.258 | 7.1743 | 4.5111 | -13.6134 | 5.258 | 5.01 | 20.8458 | 20.556 | 20.1611 | 19.6764 | 19.0845 | 18.3345 | 17.6162 | 16.8519 | 13.2376 | -4.3499 | -5.2754 | 3.6664 | 19.906 | 19.5713 | 19.1233 | 18.5886 | 17.9662 | 17.1784 | 16.1896 | 15.2396 | 14.2315
|  | QUEENS LANE NORTH | CF |  |  |  |  | 1.883 | 1.6544 | 1.3891 | 18.0723 | 17.759 | 17.3927 | 16.9784 | 16.4315 | 15.9223 | 15.3672 | 11.9509 | 8.4376 | -11.9471 | 5.3437 | 5.1988 | 21.1315 | 20.9447 | 20.7458 | 20.4947 | 20.1815 | 19.8141 | 19.4213 | 18.9978 | 16.4264 | -2.5448 | -7.3091 | 3.7787 | 20.1396 | 19.9264 | 19.7019 | 19.4866 | 19.1386 | 18.7376 | 18.2111 | 17.7182 | 17.1835
| THURSO | RACKWICK | MINIMUM HEADROOM | ND 20206 99857 | YES | NO | 0 | 0.076163 | 0.076163 | 0.06698 | 0.06698 | 0.059837 | 0.059837 | 0.058816 | 0.055755 | 0.056776 | 0.053714 | 0.048612 | 0.047592 | 0.038592 | 0.080429 | 0.079408 | 0.071245 | 0.071245 | 0.064102 | 0.064102 | 0.063082 | 0.063082 | 0.064102 | 0.064102 | 0.059 | 0.061459 | 0.058398 | 0.076765 | 0.076765 | 0.068602 | 0.067582 | 0.060439 | 0.057378 | 0.060439 | 0.057378 | 0.056357 | 0.053296
|  | RACKWICK | EE |  |  |  |  | 0.076163 | 0.076163 | 0.06698 | 0.06698 | 0.059837 | 0.059837 | 0.062898 | 0.057796 | 0.057796 | 0.053714 | 0.048612 | 0.048612 | 0.038592 | 0.080429 | 0.079408 | 0.071245 | 0.071245 | 0.064102 | 0.064102 | 0.069204 | 0.067163 | 0.066143 | 0.064102 | 0.059 | 0.061459 | 0.060439 | 0.076765 | 0.076765 | 0.068602 | 0.067582 | 0.060439 | 0.057378 | 0.061459 | 0.057378 | 0.058398 | 0.053296
|  | RACKWICK | HT |  |  |  |  | 0.083306 | 0.076163 | 0.074122 | 0.075143 | 0.068 | 0.06698 | 0.059837 | 0.055755 | 0.056776 | 0.061878 | 0.053714 | 0.047592 | 0.038592 | 0.087571 | 0.079408 | 0.078388 | 0.079408 | 0.072265 | 0.071245 | 0.064102 | 0.063082 | 0.064102 | 0.069204 | 0.061041 | 0.06248 | 0.06248 | 0.083908 | 0.076765 | 0.075745 | 0.075745 | 0.068602 | 0.067582 | 0.060439 | 0.058398 | 0.056357 | 0.06248
|  | RACKWICK | HE |  |  |  |  | 0.083306 | 0.077184 | 0.076163 | 0.074122 | 0.06902 | 0.06698 | 0.058816 | 0.058816 | 0.058816 | 0.062898 | 0.053714 | 0.049633 | 0.040633 | 0.087571 | 0.080429 | 0.079408 | 0.078388 | 0.072265 | 0.071245 | 0.063082 | 0.063082 | 0.064102 | 0.069204 | 0.062061 | 0.06248 | 0.06248 | 0.083908 | 0.077786 | 0.076765 | 0.075745 | 0.068602 | 0.067582 | 0.060439 | 0.060439 | 0.057378 | 0.06248
|  | RACKWICK | CF |  |  |  |  | 0.084327 | 0.084327 | 0.076163 | 0.075143 | 0.075143 | 0.068 | 0.068 | 0.065959 | 0.058816 | 0.058816 | 0.059837 | 0.055755 | 0.041653 | 0.087571 | 0.087571 | 0.080429 | 0.079408 | 0.079408 | 0.072265 | 0.072265 | 0.071245 | 0.064102 | 0.064102 | 0.067163 | 0.06452 | 0.058398 | 0.084929 | 0.084929 | 0.076765 | 0.075745 | 0.075745 | 0.068602 | 0.068602 | 0.067582 | 0.060439 | 0.060439
| FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | NO | 0 | 0.97449 | 0.97347 | 0.96531 | 0.96429 | 0.96122 | 0.9602 | 0.95714 | 0.94898 | 0.94592 | 0.9449 | 0.92857 | 0.92551 | 0.92245 | 0.98163 | 0.98061 | 0.97245 | 0.97143 | 0.97041 | 0.96939 | 0.96735 | 0.95918 | 0.95714 | 0.95612 | 0.94184 | 0.9398 | 0.93776 | 0.97959 | 0.97857 | 0.97041 | 0.96837 | 0.96735 | 0.96531 | 0.96327 | 0.95408 | 0.95204 | 0.95
|  | RAHOY | EE |  |  |  |  | 0.97449 | 0.97347 | 0.96531 | 0.96429 | 0.96122 | 0.9602 | 0.95714 | 0.94898 | 0.94592 | 0.9449 | 0.93265 | 0.93061 | 0.93061 | 0.98163 | 0.98061 | 0.97245 | 0.97143 | 0.97041 | 0.96939 | 0.96735 | 0.95918 | 0.95714 | 0.95612 | 0.9449 | 0.94388 | 0.94388 | 0.97959 | 0.97857 | 0.97041 | 0.96837 | 0.96735 | 0.96531 | 0.96327 | 0.95408 | 0.95204 | 0.95
|  | RAHOY | HT |  |  |  |  | 0.97449 | 0.97449 | 0.97347 | 0.97245 | 0.96429 | 0.96327 | 0.9602 | 0.95918 | 0.95714 | 0.94898 | 0.93265 | 0.92959 | 0.92857 | 0.98163 | 0.98163 | 0.98061 | 0.97959 | 0.97143 | 0.97143 | 0.96939 | 0.96837 | 0.96735 | 0.95918 | 0.9449 | 0.94286 | 0.94184 | 0.97959 | 0.97959 | 0.97857 | 0.97755 | 0.96837 | 0.96837 | 0.96531 | 0.96429 | 0.96327 | 0.95408
|  | RAHOY | HE |  |  |  |  | 0.97449 | 0.97347 | 0.97347 | 0.97245 | 0.96429 | 0.96224 | 0.9602 | 0.95714 | 0.95612 | 0.94592 | 0.92857 | 0.92551 | 0.92245 | 0.98163 | 0.98061 | 0.98061 | 0.97959 | 0.97143 | 0.97041 | 0.96939 | 0.96735 | 0.96633 | 0.95714 | 0.94184 | 0.9398 | 0.93776 | 0.97959 | 0.97857 | 0.97857 | 0.97755 | 0.96837 | 0.96735 | 0.96531 | 0.96327 | 0.96122 | 0.95204
|  | RAHOY | CF |  |  |  |  | 0.97449 | 0.97449 | 0.97449 | 0.97347 | 0.97245 | 0.96531 | 0.96429 | 0.96122 | 0.9602 | 0.95918 | 0.9449 | 0.92959 | 0.92653 | 0.98163 | 0.98163 | 0.98163 | 0.98061 | 0.97959 | 0.97245 | 0.97143 | 0.97041 | 0.96939 | 0.96837 | 0.95612 | 0.94286 | 0.94082 | 0.97959 | 0.97959 | 0.97959 | 0.97857 | 0.97755 | 0.97041 | 0.96837 | 0.96735 | 0.96531 | 0.96429
| INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | NO | 4.986 | 10.168 | 8.6841 | 6.9779 | 5.1391 | 3.0404 | 0.67566 | -1.7301 | -4.5137 | -6.9347 | -9.719 | -23.0016 | -29.1441 | -31.5827 | 10.6279 | 9.4893 | 8.1756 | 6.7619 | 5.1085 | 3.2127 | 1.3537 | -0.76788 | -2.7533 | -5.175 | -15.7427 | -20.4356 | -22.2994 | 7.4764 | 6.0502 | 4.4045 | 2.6288 | 0.57809 | -1.7533 | -4.0896 | -6.7746 | -9.1379 | -12.0334
|  | RAIGMORE | EE |  |  |  |  | 10.168 | 8.6841 | 6.9779 | 5.1391 | 3.0404 | 0.67566 | -1.7301 | -4.5137 | -6.9347 | -9.0313 | -15.7288 | -17.8081 | -19.3082 | 10.6279 | 9.4893 | 8.1756 | 6.7619 | 5.1085 | 3.2127 | 1.3537 | -0.76788 | -2.6602 | -4.2761 | -9.503 | -11.0746 | -11.8478 | 7.4764 | 6.0502 | 4.4045 | 2.6288 | 0.57809 | -1.7533 | -4.0896 | -6.7746 | -9.1379 | -11.1727
|  | RAIGMORE | HT |  |  |  |  | 10.9245 | 9.9311 | 8.7327 | 7.4003 | 6.0978 | 4.2561 | 2.6361 | 0.67705 | -1.125 | -3.0125 | -11.362 | -16.1401 | -18.4711 | 11.2385 | 10.4785 | 9.4997 | 8.4014 | 7.408 | 5.8338 | 4.6063 | 3.1099 | 1.7455 | 0.30195 | -6.2171 | -9.9256 | -11.6658 | 8.2079 | 7.2562 | 6.0717 | 4.7421 | 3.4861 | 1.6111 | 0.045953 | -1.8478 | -3.5866 | -5.415
|  | RAIGMORE | HE |  |  |  |  | 10.7029 | 9.335 | 7.8261 | 6.0484 | 4.1123 | 1.5718 | -0.8742 | -3.8649 | -6.6798 | -9.719 | -23.0016 | -29.1441 | -31.5827 | 11.0398 | 9.9832 | 8.7682 | 7.3253 | 5.8081 | 3.6872 | 1.781 | -0.55114 | -2.7533 | -5.175 | -15.7427 | -20.4356 | -22.2994 | 7.9926 | 6.6775 | 5.1936 | 3.4361 | 1.5534 | -0.99887 | -3.3817 | -6.2973 | -9.0434 | -12.0334
|  | RAIGMORE | CF |  |  |  |  | 11.0877 | 10.3423 | 9.4767 | 8.5188 | 7.3711 | 6.0248 | 4.6986 | 3.0293 | 1.5065 | -0.13296 | -9.2994 | -16.9779 | -21.5402 | 11.3649 | 10.7842 | 10.1096 | 9.3656 | 8.4472 | 7.351 | 6.3041 | 4.9967 | 3.7997 | 2.5069 | -4.6137 | -9.9631 | -12.8724 | 8.3642 | 7.6487 | 6.8137 | 5.8883 | 4.7629 | 3.4312 | 2.137 | 0.51348 | -0.97177 | -2.5744
| ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | 0.231 | -1.7704 | -1.8602 | -1.95 | -2.0541 | -2.1714 | -2.2561 | -2.4153 | -2.5959 | -2.7663 | -2.8714 | -3.3194 | -3.5776 | -3.6357 | -0.72959 | -0.78673 | -0.84184 | -0.90918 | -0.98878 | -1.0388 | -1.1408 | -1.2612 | -1.3735 | -1.4173 | -1.6653 | -1.7969 | -2.0673 | -1.3888 | -1.4724 | -1.5582 | -1.6541 | -1.7653 | -1.8449 | -1.9929 | -2.1622 | -2.3235 | -2.4173
|  | REDFORD | EE |  |  |  |  | -1.7704 | -1.8602 | -1.95 | -2.0541 | -2.1714 | -2.2561 | -2.4153 | -2.5959 | -2.7663 | -2.8714 | -3.3194 | -3.5347 | -3.5765 | -0.72959 | -0.78673 | -0.84184 | -0.90918 | -0.98878 | -1.0388 | -1.1408 | -1.2612 | -1.3735 | -1.4173 | -1.6653 | -1.7969 | -1.9367 | -1.3888 | -1.4724 | -1.5582 | -1.6541 | -1.7653 | -1.8449 | -1.9929 | -2.1622 | -2.3235 | -2.4173
|  | REDFORD | HT |  |  |  |  | -1.75 | -1.8296 | -1.9143 | -2.0102 | -2.0878 | -2.1837 | -2.3173 | -2.4327 | -2.5704 | -2.7112 | -3.2776 | -3.5776 | -3.6357 | -0.70102 | -0.7398 | -0.78776 | -0.84592 | -0.88571 | -0.9398 | -1.0184 | -1.0796 | -1.1612 | -1.249 | -1.5755 | -1.7092 | -1.7357 | -1.3541 | -1.4255 | -1.5041 | -1.5918 | -1.6622 | -1.752 | -1.8765 | -1.9765 | -2.1061 | -2.2378
|  | REDFORD | HE |  |  |  |  | -1.7449 | -1.7969 | -1.8541 | -1.9184 | -1.9673 | -2.0337 | -2.1429 | -2.2265 | -2.3388 | -2.4531 | -3.0418 | -3.3204 | -3.4276 | -0.69796 | -0.73265 | -0.77347 | -0.82245 | -0.85408 | -0.9 | -0.97347 | -1.0235 | -1.098 | -1.1755 | -1.5469 | -1.7276 | -1.8816 | -1.352 | -1.402 | -1.4582 | -1.5265 | -1.5745 | -1.6449 | -1.7469 | -1.848 | -1.9551 | -2.0663
|  | REDFORD | CF |  |  |  |  | -1.7235 | -1.7612 | -1.8031 | -1.8531 | -1.8929 | -1.9459 | -2.002 | -2.0765 | -2.1449 | -2.1765 | -2.5837 | -2.952 | -3.2071 | -0.68469 | -0.71327 | -0.74286 | -0.78469 | -0.8102 | -0.8551 | -0.89796 | -0.95408 | -1.0102 | -1.0347 | -1.3663 | -1.7071 | -2.0673 | -1.3327 | -1.3684 | -1.4112 | -1.4663 | -1.5 | -1.5551 | -1.6092 | -1.6786 | -1.7449 | -1.7755
| BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 4.254 | 5.4044 | 4.7921 | 4.1197 | 3.3309 | 2.4982 | 1.5084 | 0.60946 | -0.24973 | -0.88238 | -1.7967 | -5.1569 | -6.1058 | -6.9487 | 7.4074 | 7.035 | 6.639 | 6.1768 | 5.6982 | 5.1248 | 4.5799 | 4.0554 | 3.7533 | 3.1901 | 1.0707 | 0.85487 | -0.0012571 | 6.6253 | 6.0896 | 5.5212 | 4.8426 | 4.1232 | 3.261 | 2.4692 | 1.7059 | 1.1875 | 0.38344
|  | REDGORTON | EE |  |  |  |  | 5.4156 | 4.7921 | 4.1197 | 3.3309 | 2.4982 | 1.5084 | 0.60946 | -0.24973 | -0.78646 | -1.611 | -5.1569 | -5.9885 | -6.813 | 7.4197 | 7.035 | 6.639 | 6.1768 | 5.6982 | 5.1248 | 4.5799 | 4.0554 | 3.7829 | 3.2788 | 1.0707 | 0.85487 | 0.4018 | 6.6253 | 6.0896 | 5.5212 | 4.8426 | 4.1232 | 3.261 | 2.4692 | 1.7059 | 1.2681 | 0.54568
|  | REDGORTON | HT |  |  |  |  | 5.4044 | 4.8156 | 4.1288 | 3.3574 | 2.5319 | 1.535 | 0.78599 | -0.005849 | -0.88238 | -1.7967 | -4.9946 | -6.1058 | -6.9487 | 7.4074 | 7.0584 | 6.6564 | 6.2115 | 5.7493 | 5.1819 | 4.7595 | 4.2921 | 3.7533 | 3.1901 | 1.3839 | 1.21 | 1.1589 | 6.6324 | 6.1345 | 5.5477 | 4.8794 | 4.1692 | 3.3038 | 2.662 | 1.962 | 1.1875 | 0.38344
|  | REDGORTON | HE |  |  |  |  | 5.4839 | 4.9595 | 4.3666 | 3.6839 | 2.9493 | 2.0605 | 1.3217 | 0.60129 | -0.16401 | -0.96095 | -4.3905 | -5.4763 | -6.3834 | 7.4758 | 7.1431 | 6.787 | 6.3829 | 5.9605 | 5.4452 | 5.0013 | 4.5605 | 4.0819 | 3.5778 | 1.4605 | 1.1283 | 0.66507 | 6.7049 | 6.263 | 5.763 | 5.1732 | 4.5467 | 3.7753 | 3.1385 | 2.5069 | 1.8375 | 1.1406
|  | REDGORTON | CF |  |  |  |  | 5.7258 | 5.2921 | 4.8135 | 4.2839 | 3.7125 | 3.0452 | 2.5023 | 1.986 | 1.4442 | 0.86864 | -2.1793 | -4.4058 | -6.0467 | 7.6727 | 7.4064 | 7.1176 | 6.8084 | 6.4839 | 6.1003 | 5.7533 | 5.4248 | 5.0748 | 4.7033 | 2.6707 | 1.214 | -0.0012571 | 6.9212 | 6.562 | 6.1681 | 5.7294 | 5.2508 | 4.6804 | 4.2181 | 3.7753 | 3.3089 | 2.813
| REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | NO | 14.699 | 7.7226 | 6.794 | 4.94 | 2.5614 | 1.0644 | -3.3305 | -4.857 | -6.6152 | -8.3743 | -11.0376 | -20.8396 | -31.4743 | -42.5621 | 12.0063 | 11.2991 | 9.5195 | 7.1175 | 5.9195 | 1.2685 | -0.20903 | -2.1356 | -3.8835 | -6.6968 | -17.3937 | -28.6498 | -40.3335 | 10.9542 | 10.1287 | 8.1951 | 5.6389 | 4.2359 | -0.67433 | -2.1621 | -4.2284 | -6.1049 | -9.0723
|  | REDMOSS | EE |  |  |  |  | 8.7277 | 7.84 | 5.6542 | 4.4451 | 2.3787 | -0.76923 | -2.7968 | -4.2509 | -6.3243 | -7.9019 | -13.3325 | -22.8274 | -27.7703 | 13.3583 | 12.7195 | 10.4951 | 9.5144 | 7.5777 | 4.491 | 2.6706 | 1.5277 | -0.45699 | -1.8805 | -7.2325 | -17.3192 | -21.7213 | 12.2736 | 11.4961 | 9.0951 | 7.9726 | 5.8389 | 2.4828 | 0.43791 | -0.93964 | -3.1345 | -4.7468
|  | REDMOSS | HT |  |  |  |  | 8.8124 | 6.794 | 4.94 | 2.5614 | 1.0644 | -3.3305 | -4.857 | -6.3723 | -7.46 | -8.8662 | -15.1335 | -26.3407 | -36.6621 | 13.3736 | 11.2991 | 9.5195 | 7.1175 | 5.9195 | 1.2685 | 0.010359 | -1.2386 | -2.0682 | -3.2478 | -9.4549 | -21.506 | -32.4682 | 12.3267 | 10.1287 | 8.1951 | 5.6389 | 4.2359 | -0.67433 | -2.1621 | -3.6478 | -4.6733 | -6.0641
|  | REDMOSS | HE |  |  |  |  | 7.7226 | 6.9226 | 5.3838 | 3.291 | 1.6267 | -2.4794 | -4.6233 | -6.6152 | -8.3743 | -11.0376 | -20.8396 | -31.4743 | -42.5621 | 12.0063 | 11.4042 | 9.9359 | 7.8032 | 6.2726 | 1.8236 | -0.20903 | -2.1356 | -3.8835 | -6.6968 | -17.3937 | -28.6498 | -40.3335 | 10.9542 | 10.243 | 8.6481 | 6.39 | 4.7195 | 0.084849 | -2.1345 | -4.2284 | -6.1049 | -9.0723
|  | REDMOSS | CF |  |  |  |  | 9.1032 | 8.6063 | 6.8767 | 6.2379 | 5.0553 | 3.2257 | 1.8338 | 0.51444 | -0.6978 | -2.0876 | -6.9488 | -11.4009 | -15.6386 | 13.6165 | 13.2461 | 11.3808 | 10.9185 | 9.8185 | 7.9502 | 6.6032 | 5.3706 | 4.1838 | 2.8012 | -1.7978 | -4.9294 | -7.5876 | 12.592 | 12.1461 | 10.193 | 9.6308 | 8.4359 | 6.4808 | 5.0563 | 3.7369 | 2.5073 | 1.0389
| CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | NO | 0.213 | -0.48878 | -0.53878 | -0.59694 | -0.66735 | -0.71939 | -0.79796 | -0.88061 | -0.98776 | -1.0908 | -1.1337 | -1.3347 | -1.4061 | -1.4255 | -0.25408 | -0.28571 | -0.32551 | -0.37041 | -0.4051 | -0.4551 | -0.51224 | -0.58061 | -0.64796 | -0.67653 | -0.82449 | -0.88061 | -1.05 | -0.44796 | -0.4949 | -0.55 | -0.61837 | -0.66531 | -0.74184 | -0.82143 | -0.92347 | -1.0224 | -1.0653
|  | RHICONICH | EE |  |  |  |  | -0.48878 | -0.53878 | -0.59694 | -0.66735 | -0.71939 | -0.79796 | -0.88061 | -0.98776 | -1.0908 | -1.1337 | -1.3347 | -1.3673 | -1.3847 | -0.25408 | -0.28571 | -0.32551 | -0.37041 | -0.4051 | -0.4551 | -0.51224 | -0.58061 | -0.64796 | -0.67653 | -0.82449 | -0.88061 | -0.97041 | -0.44796 | -0.4949 | -0.55 | -0.61837 | -0.66531 | -0.74184 | -0.82143 | -0.92347 | -1.0224 | -1.0653
|  | RHICONICH | HT |  |  |  |  | -0.45918 | -0.5051 | -0.5602 | -0.6 | -0.65204 | -0.71122 | -0.78571 | -0.84184 | -0.91531 | -0.98469 | -1.2694 | -1.4061 | -1.4255 | -0.23265 | -0.2602 | -0.29286 | -0.31633 | -0.34694 | -0.38571 | -0.43061 | -0.46429 | -0.51224 | -0.55612 | -0.7449 | -0.82959 | -0.83878 | -0.41939 | -0.46122 | -0.51327 | -0.55 | -0.59898 | -0.65714 | -0.72653 | -0.78265 | -0.85306 | -0.91837
|  | RHICONICH | HE |  |  |  |  | -0.45918 | -0.49388 | -0.54184 | -0.57143 | -0.60816 | -0.66122 | -0.72143 | -0.76531 | -0.83061 | -0.89082 | -1.2153 | -1.301 | -1.3388 | -0.23367 | -0.25306 | -0.28469 | -0.30612 | -0.33163 | -0.36531 | -0.40714 | -0.43673 | -0.48265 | -0.52551 | -0.74184 | -0.83163 | -0.91531 | -0.41939 | -0.44898 | -0.49592 | -0.52551 | -0.55918 | -0.60918 | -0.66837 | -0.71122 | -0.77449 | -0.83367
|  | RHICONICH | CF |  |  |  |  | -0.45612 | -0.48673 | -0.51837 | -0.54592 | -0.58571 | -0.61327 | -0.65612 | -0.70918 | -0.72857 | -0.77653 | -1.0214 | -1.1918 | -1.3041 | -0.23061 | -0.24796 | -0.26939 | -0.28571 | -0.31327 | -0.33265 | -0.36429 | -0.40306 | -0.41735 | -0.45102 | -0.64694 | -0.83878 | -1.05 | -0.41531 | -0.44388 | -0.47449 | -0.49898 | -0.53878 | -0.56327 | -0.60612 | -0.65612 | -0.67857 | -0.72143
| DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | NO | 1.879 | 10.3377 | 9.8561 | 9.1418 | 7.9745 | 7.4806 | 5.4388 | 4.501 | 3.4918 | 2.2622 | 1.1122 | -4.3776 | -10.6388 | -16.8123 | 12.5214 | 12.2306 | 11.5735 | 10.4704 | 10.1857 | 8.001 | 7.2796 | 6.2857 | 5.3306 | 3.7306 | -3.0561 | -11.027 | -19.9199 | 11.0087 | 10.5423 | 9.7617 | 8.4556 | 7.9678 | 5.577 | 4.677 | 3.7005 | 2.6872 | 1.2587
|  | ROSEBANK STREET | EE |  |  |  |  | 10.3377 | 9.8561 | 9.2847 | 8.6204 | 7.5194 | 6.0337 | 4.8133 | 3.7439 | 2.2622 | 1.1122 | -2.7204 | -7.0786 | -10.3786 | 12.5214 | 12.2306 | 11.8388 | 11.4184 | 10.4214 | 8.9571 | 7.9622 | 7.2041 | 5.9 | 4.9673 | 1.1663 | -5.6822 | -10.7577 | 11.0087 | 10.5423 | 9.9709 | 9.3291 | 8.1566 | 6.5127 | 5.2678 | 4.2413 | 2.6872 | 1.5281
|  | ROSEBANK STREET | HT |  |  |  |  | 10.4806 | 10.0173 | 9.1418 | 7.9745 | 7.4806 | 5.4388 | 4.501 | 3.4918 | 2.5816 | 1.5112 | -3.7939 | -10.4449 | -16.601 | 12.652 | 12.3745 | 11.5735 | 10.4704 | 10.1857 | 8.001 | 7.3928 | 6.7265 | 6.1663 | 5.4194 | 1.0561 | -6.5117 | -12.9015 | 11.1719 | 10.7342 | 9.7617 | 8.4556 | 7.9678 | 5.577 | 4.677 | 3.7005 | 2.8434 | 1.7944
|  | ROSEBANK STREET | HE |  |  |  |  | 10.4888 | 10.2724 | 9.6041 | 8.7163 | 8.1653 | 6.3428 | 5.3531 | 4.251 | 3.198 | 1.6245 | -4.3776 | -10.6388 | -16.8123 | 12.6367 | 12.4765 | 11.7541 | 10.8 | 10.2673 | 8.1602 | 7.2796 | 6.2857 | 5.3306 | 3.7306 | -3.0561 | -11.027 | -19.9199 | 11.1811 | 10.9607 | 10.1954 | 9.1576 | 8.5189 | 6.3372 | 5.2923 | 4.1291 | 3.0138 | 1.2587
|  | ROSEBANK STREET | CF |  |  |  |  | 10.5898 | 10.4765 | 10.3357 | 10.1275 | 9.7061 | 9.0306 | 8.5775 | 8.1082 | 7.6541 | 7.1082 | 4.5704 | 1.8602 | -2.15 | 12.6867 | 12.5714 | 12.4306 | 12.2194 | 11.7286 | 10.9173 | 10.3826 | 9.8245 | 9.2694 | 8.598 | 5.3908 | 1.3903 | -5.3832 | 11.2791 | 11.1566 | 11.0076 | 10.7954 | 10.2923 | 9.4607 | 8.9464 | 8.4332 | 7.9321 | 7.3189
| KEITH 2 | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 1.653 | 0.43037 | 0.30486 | 0.17424 | 0.026286 | -0.12882 | -0.27167 | -0.45943 | -0.66453 | -0.85841 | -1.0207 | -1.6013 | -1.8564 | -1.9604 | 2.0263 | 1.9222 | 1.8222 | 1.7181 | 1.61 | 1.513 | 1.3885 | 1.2498 | 1.1222 | 1.0151 | 0.64669 | 0.46404 | 0.3722 | 1.3998 | 1.2804 | 1.1498 | 1.0059 | 0.85996 | 0.73037 | 0.55078 | 0.35894 | 0.17527 | 0.025265
|  | ROTHES | EE |  |  |  |  | 0.43037 | 0.30486 | 0.17424 | 0.026286 | -0.12882 | -0.27167 | -0.45943 | -0.66453 | -0.85841 | -1.0207 | -1.6013 | -1.7849 | -1.8156 | 2.0263 | 1.9222 | 1.8222 | 1.7181 | 1.61 | 1.513 | 1.3885 | 1.2498 | 1.1222 | 1.0151 | 0.64669 | 0.55282 | 0.53547 | 1.3998 | 1.2804 | 1.1498 | 1.0059 | 0.85996 | 0.73037 | 0.55078 | 0.35894 | 0.17527 | 0.025265
|  | ROTHES | HT |  |  |  |  | 0.44567 | 0.33241 | 0.21914 | 0.082408 | -0.030857 | -0.15739 | -0.31147 | -0.48698 | -0.66147 | -0.83188 | -1.5309 | -1.8564 | -1.9604 | 2.0365 | 1.9457 | 1.8538 | 1.76 | 1.6865 | 1.6028 | 1.5028 | 1.3875 | 1.2783 | 1.164 | 0.69976 | 0.50384 | 0.43037 | 1.4151 | 1.31 | 1.1906 | 1.063 | 0.9569 | 0.83751 | 0.69363 | 0.52833 | 0.37118 | 0.20792
|  | ROTHES | HE |  |  |  |  | 0.46098 | 0.35486 | 0.2569 | 0.14363 | 0.030367 | -0.08698 | -0.24412 | -0.41555 | -0.58188 | -0.74718 | -1.5186 | -1.8186 | -1.9574 | 2.0518 | 1.963 | 1.8814 | 1.7916 | 1.711 | 1.6253 | 1.5181 | 1.3947 | 1.2824 | 1.1661 | 0.64669 | 0.46404 | 0.3722 | 1.4304 | 1.3324 | 1.2344 | 1.1171 | 1.012 | 0.89976 | 0.7518 | 0.58853 | 0.43649 | 0.27833
|  | ROTHES | CF |  |  |  |  | 0.51404 | 0.45588 | 0.39159 | 0.32833 | 0.25486 | 0.18139 | 0.091592 | -0.020653 | -0.12371 | -0.22269 | -0.83698 | -1.3809 | -1.7604 | 2.1038 | 2.0508 | 1.9957 | 1.9416 | 1.8834 | 1.8304 | 1.764 | 1.6824 | 1.6049 | 1.5344 | 1.0916 | 0.71608 | 0.47731 | 1.4824 | 1.4253 | 1.363 | 1.2998 | 1.2253 | 1.1549 | 1.0671 | 0.96302 | 0.86506 | 0.77322
| DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 0.835 | 9.9847 | 9.7663 | 9.4959 | 9.2255 | 8.9082 | 8.5786 | 8.0847 | 7.5184 | 6.9735 | 6.4724 | 4.2918 | 2.5541 | 1.5214 | 10.6602 | 10.5388 | 10.3867 | 10.2306 | 10.0418 | 9.8439 | 9.5786 | 9.2429 | 8.9235 | 8.6388 | 7.4418 | 6.9668 | 6.2668 | 10.4444 | 10.2403 | 9.9944 | 9.7444 | 9.4505 | 9.1332 | 8.6842 | 8.1536 | 7.6485 | 7.1862
|  | ROTHESAY | EE |  |  |  |  | 9.9847 | 9.7663 | 9.4959 | 9.2255 | 8.9082 | 8.5786 | 8.0847 | 7.5184 | 6.9735 | 6.4724 | 4.2918 | 2.7102 | 1.5745 | 10.6602 | 10.5388 | 10.3867 | 10.2306 | 10.0418 | 9.8439 | 9.5786 | 9.2429 | 8.9235 | 8.6388 | 7.4418 | 6.9668 | 6.2668 | 10.4444 | 10.2403 | 9.9944 | 9.7444 | 9.4505 | 9.1332 | 8.6842 | 8.1536 | 7.6485 | 7.1862
|  | ROTHESAY | HT |  |  |  |  | 10.0837 | 9.8918 | 9.6694 | 9.4163 | 9.1745 | 8.9418 | 8.4867 | 7.9857 | 7.4867 | 7.0255 | 4.3214 | 2.5541 | 1.5214 | 10.7255 | 10.6265 | 10.5112 | 10.3786 | 10.2439 | 10.1173 | 9.8888 | 9.6245 | 9.3724 | 9.148 | 7.7786 | 7.3556 | 7.2434 | 10.5342 | 10.3546 | 10.1546 | 9.9199 | 9.6974 | 9.4801 | 9.0566 | 8.5923 | 8.1372 | 7.7148
|  | ROTHESAY | HE |  |  |  |  | 10.0755 | 9.952 | 9.8061 | 9.6276 | 9.4561 | 9.2653 | 8.9571 | 8.5949 | 8.248 | 7.9449 | 5.9816 | 4.5827 | 3.3582 | 10.7194 | 10.6449 | 10.5602 | 10.4531 | 10.3429 | 10.2255 | 10.0561 | 9.8469 | 9.6469 | 9.4765 | 8.2949 | 7.8199 | 7.125 | 10.527 | 10.4117 | 10.2791 | 10.1179 | 9.9607 | 9.7852 | 9.5026 | 9.1648 | 8.8423 | 8.5587
|  | ROTHESAY | CF |  |  |  |  | 10.1133 | 10.0459 | 9.9622 | 9.8765 | 9.7673 | 9.649 | 9.5061 | 9.3735 | 9.2265 | 9.0704 | 8.101 | 6.8959 | 5.0735 | 10.7408 | 10.6898 | 10.6337 | 10.5765 | 10.4969 | 10.4071 | 10.301 | 10.1959 | 10.0827 | 9.9592 | 9.1582 | 8.323 | 6.7597 | 10.5658 | 10.4995 | 10.4219 | 10.3434 | 10.2444 | 10.1372 | 10.0036 | 9.8781 | 9.7372 | 9.5883
| THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | NO | 0.023 | 0.37959 | 0.36531 | 0.34898 | 0.33673 | 0.31633 | 0.30918 | 0.28776 | 0.26735 | 0.24184 | 0.21939 | 0.16122 | 0.14796 | 0.14082 | 0.67143 | 0.66122 | 0.64796 | 0.63878 | 0.62041 | 0.61531 | 0.59694 | 0.57959 | 0.56224 | 0.54796 | 0.50918 | 0.49796 | 0.47551 | 0.45204 | 0.43673 | 0.41837 | 0.40714 | 0.38265 | 0.37143 | 0.34388 | 0.32245 | 0.29694 | 0.27551
|  | ROUSAY | EE |  |  |  |  | 0.37959 | 0.36531 | 0.34898 | 0.33673 | 0.31633 | 0.30918 | 0.28776 | 0.26735 | 0.24184 | 0.21939 | 0.16122 | 0.15306 | 0.14694 | 0.67143 | 0.66122 | 0.64796 | 0.63878 | 0.62041 | 0.61531 | 0.59694 | 0.57959 | 0.56224 | 0.54796 | 0.50918 | 0.49796 | 0.48163 | 0.45204 | 0.43673 | 0.41837 | 0.40714 | 0.38265 | 0.37143 | 0.34388 | 0.32245 | 0.29694 | 0.27551
|  | ROUSAY | HT |  |  |  |  | 0.38469 | 0.37653 | 0.36633 | 0.35816 | 0.34184 | 0.33265 | 0.31633 | 0.30816 | 0.29082 | 0.26735 | 0.18163 | 0.14796 | 0.14082 | 0.67755 | 0.67143 | 0.66122 | 0.65408 | 0.64286 | 0.63367 | 0.61837 | 0.61327 | 0.59796 | 0.58163 | 0.52449 | 0.50306 | 0.50102 | 0.45918 | 0.44694 | 0.43469 | 0.42551 | 0.40918 | 0.39388 | 0.37449 | 0.36122 | 0.34082 | 0.31735
|  | ROUSAY | HE |  |  |  |  | 0.38469 | 0.37857 | 0.36735 | 0.3602 | 0.34592 | 0.33878 | 0.32245 | 0.31633 | 0.29796 | 0.27959 | 0.19388 | 0.17143 | 0.16837 | 0.67755 | 0.67143 | 0.66224 | 0.65714 | 0.64592 | 0.63878 | 0.62653 | 0.62041 | 0.60612 | 0.59082 | 0.53061 | 0.51327 | 0.49796 | 0.45918 | 0.44898 | 0.43878 | 0.42959 | 0.41633 | 0.40408 | 0.38571 | 0.37551 | 0.35714 | 0.33571
|  | ROUSAY | CF |  |  |  |  | 0.38061 | 0.38265 | 0.37755 | 0.36837 | 0.36224 | 0.34898 | 0.34388 | 0.33163 | 0.31939 | 0.31837 | 0.25612 | 0.18776 | 0.16531 | 0.67449 | 0.67347 | 0.66939 | 0.66224 | 0.6551 | 0.6449 | 0.64082 | 0.62959 | 0.61837 | 0.61837 | 0.56837 | 0.50816 | 0.47551 | 0.4551 | 0.45408 | 0.4449 | 0.43571 | 0.42959 | 0.41327 | 0.40816 | 0.39184 | 0.37857 | 0.37653
| CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | NO | 1.617 | 14.117 | 13.7639 | 13.3415 | 12.9384 | 12.468 | 11.9741 | 11.519 | 10.718 | 9.9405 | 9.2139 | 6.017 | 3.7721 | 2.1976 | 15.7517 | 15.5517 | 15.3007 | 15.0639 | 14.7762 | 14.4649 | 14.2813 | 13.818 | 13.37 | 12.9598 | 11.168 | 10.2711 | 8.1802 | 14.9098 | 14.5843 | 14.1915 | 13.816 | 13.3762 | 12.9078 | 12.516 | 11.7762 | 11.0619 | 10.3996
|  | RUTHRIESTON | EE |  |  |  |  | 14.117 | 13.7639 | 13.3415 | 12.9384 | 12.468 | 11.9741 | 11.519 | 10.718 | 9.9405 | 9.2139 | 6.0894 | 3.9711 | 2.2435 | 15.7517 | 15.5517 | 15.3007 | 15.0639 | 14.7762 | 14.4649 | 14.2813 | 13.818 | 13.37 | 12.9598 | 11.168 | 10.2711 | 8.7649 | 14.9098 | 14.5843 | 14.1915 | 13.816 | 13.3762 | 12.9078 | 12.516 | 11.7762 | 11.0619 | 10.3996
|  | RUTHRIESTON | HT |  |  |  |  | 14.2323 | 13.9037 | 13.5313 | 13.1864 | 12.7874 | 12.3976 | 11.667 | 10.8813 | 10.1058 | 9.6833 | 6.017 | 3.7721 | 2.1976 | 15.8486 | 15.6874 | 15.4945 | 15.317 | 15.1047 | 14.9037 | 14.5466 | 14.1527 | 13.7649 | 13.6435 | 11.8476 | 11.417 | 11.2558 | 14.9619 | 14.7272 | 14.3874 | 14.068 | 13.6986 | 13.3415 | 12.6751 | 11.9568 | 11.2456 | 10.8894
|  | RUTHRIESTON | HE |  |  |  |  | 14.2333 | 14.0445 | 13.82 | 13.6211 | 13.369 | 13.1415 | 12.6588 | 12.12 | 11.6017 | 11.4313 | 8.57 | 6.4802 | 4.5129 | 15.8343 | 15.716 | 15.5629 | 15.4262 | 15.2547 | 15.0996 | 14.82 | 14.5007 | 14.1874 | 14.1302 | 12.3027 | 11.3507 | 9.7802 | 14.9609 | 14.8537 | 14.6394 | 14.4537 | 14.216 | 13.9996 | 13.5547 | 13.0558 | 12.5741 | 12.4394
|  | RUTHRIESTON | CF |  |  |  |  | 14.32 | 14.2139 | 14.0843 | 13.9721 | 13.8221 | 13.6588 | 13.5109 | 13.2864 | 13.0792 | 12.8568 | 11.67 | 9.7251 | 6.669 | 15.8762 | 15.7864 | 15.6782 | 15.5751 | 15.4466 | 15.2996 | 15.1578 | 14.9486 | 14.7547 | 14.5445 | 13.3476 | 11.6139 | 8.1802 | 15.0007 | 14.9517 | 14.8792 | 14.7741 | 14.6282 | 14.4711 | 14.3292 | 14.1119 | 13.9119 | 13.7017
| TAYNUILT | SALEN | MINIMUM HEADROOM | NM 57252 42849 | NO | YES | 1.09 | 5.6716 | 5.6226 | 5.5532 | 5.4573 | 5.3338 | 5.2083 | 5.0858 | 4.9807 | 4.8818 | 4.8297 | 4.6114 | 4.5338 | 4.5185 | 6.2583 | 6.2297 | 6.1838 | 6.1297 | 6.0583 | 5.9899 | 5.9175 | 5.8461 | 5.7828 | 5.7512 | 5.5828 | 5.5134 | 5.292 | 5.9318 | 5.8889 | 5.8236 | 5.741 | 5.6328 | 5.5277 | 5.4144 | 5.3154 | 5.2205 | 5.1726
|  | SALEN | EE |  |  |  |  | 5.6716 | 5.6226 | 5.5532 | 5.4573 | 5.3338 | 5.2083 | 5.0858 | 4.9807 | 4.8818 | 4.8297 | 4.6114 | 4.5756 | 4.5512 | 6.2583 | 6.2297 | 6.1838 | 6.1297 | 6.0583 | 5.9899 | 5.9175 | 5.8461 | 5.7828 | 5.7512 | 5.5828 | 5.5134 | 5.4114 | 5.9318 | 5.8889 | 5.8236 | 5.741 | 5.6328 | 5.5277 | 5.4144 | 5.3154 | 5.2205 | 5.1726
|  | SALEN | HT |  |  |  |  | 5.6991 | 5.6532 | 5.594 | 5.5154 | 5.4195 | 5.2858 | 5.1767 | 5.1165 | 5.0338 | 4.9614 | 4.6705 | 4.5338 | 4.5185 | 6.2777 | 6.2522 | 6.2175 | 6.1746 | 6.1246 | 6.0522 | 5.9899 | 5.9532 | 5.9022 | 5.8563 | 5.6624 | 5.5716 | 5.5634 | 5.9603 | 5.9226 | 5.8695 | 5.8063 | 5.7246 | 5.6042 | 5.5052 | 5.4491 | 5.3716 | 5.3042
|  | SALEN | HE |  |  |  |  | 5.7001 | 5.6614 | 5.6114 | 5.542 | 5.4573 | 5.3297 | 5.2246 | 5.1726 | 5.1012 | 5.0379 | 4.7328 | 4.6501 | 4.6379 | 6.2787 | 6.2552 | 6.2216 | 6.1848 | 6.1369 | 6.0675 | 6.0052 | 5.9695 | 5.9277 | 5.8818 | 5.6654 | 5.5685 | 5.4756 | 5.9614 | 5.9287 | 5.8807 | 5.8236 | 5.7532 | 5.644 | 5.5512 | 5.5022 | 5.4338 | 5.3726
|  | SALEN | CF |  |  |  |  | 5.7022 | 5.6716 | 5.642 | 5.5828 | 5.5052 | 5.4236 | 5.3501 | 5.293 | 5.2634 | 5.2103 | 4.9389 | 4.7471 | 4.6226 | 6.2807 | 6.2644 | 6.241 | 6.2103 | 6.1644 | 6.1195 | 6.0756 | 6.0338 | 6.0124 | 5.9716 | 5.7593 | 5.545 | 5.292 | 5.9624 | 5.9358 | 5.9032 | 5.8542 | 5.7889 | 5.7185 | 5.6522 | 5.5991 | 5.5736 | 5.5226
| FORT WILLIAM | SALEN 2 | MINIMUM HEADROOM | NM 69002 65519 | YES | NO | 0.33 | 1.1173 | 1.0724 | 1.0122 | 0.9602 | 0.89388 | 0.8449 | 0.76224 | 0.67449 | 0.58673 | 0.50816 | 0.35204 | 0.27449 | 0.25714 | 1.9082 | 1.8796 | 1.8429 | 1.8082 | 1.7602 | 1.7327 | 1.6765 | 1.6204 | 1.5602 | 1.5092 | 1.4051 | 1.3531 | 1.1959 | 1.551 | 1.5102 | 1.4561 | 1.4071 | 1.3469 | 1.301 | 1.2245 | 1.1398 | 1.0582 | 0.98469
|  | SALEN 2 | EE |  |  |  |  | 1.1173 | 1.0724 | 1.0122 | 0.9602 | 0.89388 | 0.8449 | 0.76224 | 0.67449 | 0.58673 | 0.50816 | 0.35204 | 0.31429 | 0.29286 | 1.9082 | 1.8796 | 1.8429 | 1.8082 | 1.7602 | 1.7327 | 1.6765 | 1.6204 | 1.5602 | 1.5092 | 1.4051 | 1.3531 | 1.2735 | 1.551 | 1.5102 | 1.4561 | 1.4071 | 1.3469 | 1.301 | 1.2245 | 1.1398 | 1.0582 | 0.98469
|  | SALEN 2 | HT |  |  |  |  | 1.1408 | 1.0969 | 1.0541 | 1.0143 | 0.96224 | 0.91633 | 0.85306 | 0.79796 | 0.73163 | 0.66122 | 0.36633 | 0.27449 | 0.25714 | 1.9245 | 1.899 | 1.8755 | 1.8551 | 1.8204 | 1.7939 | 1.752 | 1.7194 | 1.6776 | 1.6327 | 1.4388 | 1.3908 | 1.3837 | 1.5735 | 1.5327 | 1.4929 | 1.4561 | 1.4092 | 1.3653 | 1.3092 | 1.2582 | 1.1949 | 1.1306
|  | SALEN 2 | HE |  |  |  |  | 1.1357 | 1.1051 | 1.0704 | 1.0408 | 0.99898 | 0.96531 | 0.90612 | 0.86327 | 0.80408 | 0.74286 | 0.42551 | 0.37551 | 0.36224 | 1.9245 | 1.9 | 1.8786 | 1.8612 | 1.8296 | 1.8082 | 1.7684 | 1.7429 | 1.702 | 1.6571 | 1.4449 | 1.3908 | 1.3214 | 1.5724 | 1.5408 | 1.5102 | 1.4816 | 1.4418 | 1.4092 | 1.3592 | 1.3163 | 1.2633 | 1.2051
|  | SALEN 2 | CF |  |  |  |  | 1.1439 | 1.1194 | 1.0929 | 1.0561 | 1.0357 | 0.99796 | 0.97041 | 0.92653 | 0.88367 | 0.86429 | 0.64694 | 0.48571 | 0.37143 | 1.9245 | 1.9092 | 1.8929 | 1.8673 | 1.8561 | 1.8296 | 1.8092 | 1.7765 | 1.7449 | 1.7296 | 1.5541 | 1.3857 | 1.1959 | 1.5755 | 1.552 | 1.5286 | 1.4949 | 1.4745 | 1.4398 | 1.4163 | 1.3755 | 1.3367 | 1.3163
| THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | NO | 0.064 | 0.29796 | 0.27347 | 0.23673 | 0.21327 | 0.17449 | 0.14694 | 0.096939 | 0.067347 | 0.019388 | -0.022449 | -0.11122 | -0.14184 | -0.14796 | 0.47959 | 0.46633 | 0.44286 | 0.42959 | 0.40204 | 0.38469 | 0.35 | 0.33163 | 0.29694 | 0.26735 | 0.20714 | 0.17857 | 0.095918 | 0.40714 | 0.38265 | 0.3449 | 0.32449 | 0.28469 | 0.25816 | 0.21122 | 0.18265 | 0.13571 | 0.094898
|  | SANDAY | EE |  |  |  |  | 0.29796 | 0.27347 | 0.23673 | 0.21327 | 0.17449 | 0.14694 | 0.096939 | 0.067347 | 0.019388 | -0.022449 | -0.11122 | -0.12653 | -0.13571 | 0.47959 | 0.46633 | 0.44286 | 0.42959 | 0.40204 | 0.38469 | 0.35 | 0.33163 | 0.29694 | 0.26735 | 0.20714 | 0.17857 | 0.13469 | 0.40714 | 0.38265 | 0.3449 | 0.32449 | 0.28469 | 0.25816 | 0.21122 | 0.18265 | 0.13571 | 0.094898
|  | SANDAY | HT |  |  |  |  | 0.30918 | 0.2898 | 0.26327 | 0.24082 | 0.2102 | 0.19082 | 0.15612 | 0.12551 | 0.090816 | 0.04898 | -0.078571 | -0.14184 | -0.14796 | 0.48878 | 0.47755 | 0.46224 | 0.45 | 0.43265 | 0.42143 | 0.40204 | 0.38571 | 0.3602 | 0.33163 | 0.24592 | 0.20816 | 0.2051 | 0.41939 | 0.40102 | 0.37347 | 0.35306 | 0.32245 | 0.30306 | 0.26939 | 0.24286 | 0.20612 | 0.16735
|  | SANDAY | HE |  |  |  |  | 0.30918 | 0.2949 | 0.27245 | 0.25612 | 0.23163 | 0.21837 | 0.18776 | 0.16224 | 0.12959 | 0.096939 | -0.056122 | -0.088776 | -0.092857 | 0.48878 | 0.48061 | 0.46735 | 0.45816 | 0.43878 | 0.43163 | 0.41327 | 0.3949 | 0.37245 | 0.34592 | 0.2449 | 0.20816 | 0.16837 | 0.41939 | 0.4051 | 0.38367 | 0.36633 | 0.34184 | 0.32959 | 0.29796 | 0.27347 | 0.24286 | 0.20918
|  | SANDAY | CF |  |  |  |  | 0.31429 | 0.29694 | 0.28469 | 0.26837 | 0.24796 | 0.22755 | 0.21939 | 0.1949 | 0.17143 | 0.15918 | 0.059184 | -0.035714 | -0.084694 | 0.49082 | 0.48163 | 0.47347 | 0.46327 | 0.45 | 0.43776 | 0.42959 | 0.41122 | 0.39388 | 0.38469 | 0.29898 | 0.19694 | 0.095918 | 0.42347 | 0.40918 | 0.39592 | 0.38265 | 0.36122 | 0.3398 | 0.33265 | 0.30918 | 0.28469 | 0.27347
| DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 0.441 | 4.4355 | 4.3376 | 4.2365 | 4.108 | 3.9569 | 3.8263 | 3.6059 | 3.3814 | 3.209 | 3.0018 | 2.409 | 2.1263 | 1.6692 | 5.2814 | 5.2131 | 5.1498 | 5.0702 | 4.9712 | 4.8947 | 4.7631 | 4.6182 | 4.5202 | 4.3988 | 4.0518 | 4.058 | 3.6243 | 4.8733 | 4.7753 | 4.6763 | 4.56 | 4.4192 | 4.2998 | 4.0957 | 3.8835 | 3.7243 | 3.5314
|  | SANDBANK | EE |  |  |  |  | 4.4355 | 4.3376 | 4.2365 | 4.108 | 3.9569 | 3.8263 | 3.6059 | 3.3814 | 3.209 | 3.0018 | 2.409 | 2.1906 | 1.7171 | 5.2814 | 5.2131 | 5.1498 | 5.0702 | 4.9712 | 4.8947 | 4.7631 | 4.6182 | 4.5202 | 4.3988 | 4.0518 | 4.058 | 3.8008 | 4.8733 | 4.7753 | 4.6763 | 4.56 | 4.4192 | 4.2998 | 4.0957 | 3.8835 | 3.7243 | 3.5314
|  | SANDBANK | HT |  |  |  |  | 4.4876 | 4.4069 | 4.3069 | 4.1916 | 4.0845 | 3.9518 | 3.7794 | 3.6253 | 3.4273 | 3.2171 | 2.4937 | 2.1263 | 1.6692 | 5.3151 | 5.2712 | 5.2161 | 5.1467 | 5.0896 | 5.0131 | 4.9131 | 4.8304 | 4.7192 | 4.5957 | 4.1784 | 4.1927 | 4.1661 | 4.9161 | 4.8335 | 4.7416 | 4.6365 | 4.5386 | 4.4192 | 4.2631 | 4.1212 | 3.9437 | 3.7518
|  | SANDBANK | HE |  |  |  |  | 4.4876 | 4.4304 | 4.3631 | 4.2814 | 4.2059 | 4.0978 | 3.9427 | 3.8182 | 3.6549 | 3.4978 | 2.7978 | 2.5069 | 2.0222 | 5.312 | 5.2784 | 5.2365 | 5.1784 | 5.1324 | 5.0661 | 4.9733 | 4.9008 | 4.8018 | 4.7008 | 4.2671 | 4.2233 | 3.9794 | 4.9161 | 4.859 | 4.7967 | 4.7212 | 4.6518 | 4.5559 | 4.4161 | 4.2998 | 4.1498 | 4.0039
|  | SANDBANK | CF |  |  |  |  | 4.5029 | 4.46 | 4.41 | 4.3488 | 4.3018 | 4.2324 | 4.159 | 4.059 | 3.9692 | 3.8947 | 3.3518 | 2.912 | 2.1906 | 5.3212 | 5.2978 | 5.2702 | 5.2243 | 5.1947 | 5.1457 | 5.0937 | 5.0212 | 4.9569 | 4.909 | 4.4784 | 4.212 | 3.6243 | 4.9294 | 4.8906 | 4.8427 | 4.7876 | 4.7437 | 4.6794 | 4.612 | 4.5212 | 4.4355 | 4.3682
| SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 0.148 | 0.43265 | 0.36531 | 5.0529 | 4.9631 | 4.8722 | 4.7651 | 4.6784 | 4.5386 | 4.41 | 4.2957 | 4.0651 | 3.9682 | -0.81122 | 1.7184 | 6.0284 | 5.9804 | 5.912 | 5.8427 | 5.761 | 5.7008 | 5.5916 | 5.4906 | 5.4049 | 5.211 | 0.74184 | 0.32551 | 5.5651 | 5.4998 | 5.4324 | 5.3457 | 5.258 | 5.1569 | 5.0743 | 4.9406 | 4.8161 | 4.7069
|  | SANDWICK | EE |  |  |  |  | 0.43265 | 0.36531 | 5.0529 | 4.9631 | 4.8722 | 4.7651 | 4.6784 | 4.5386 | 4.41 | 4.2957 | 4.0651 | 4.0284 | -0.76224 | 1.7184 | 6.0284 | 5.9804 | 5.912 | 5.8427 | 5.761 | 5.7008 | 5.5916 | 5.4906 | 5.4049 | 5.211 | 0.74184 | 0.55102 | 5.5651 | 5.4998 | 5.4324 | 5.3457 | 5.258 | 5.1569 | 5.0743 | 4.9406 | 4.8161 | 4.7069
|  | SANDWICK | HT |  |  |  |  | 0.46735 | 0.41224 | 5.1141 | 5.0406 | 4.9824 | 4.8998 | 4.8171 | 4.712 | 4.6437 | 4.5437 | 4.1457 | 3.9682 | -0.81122 | 1.7459 | 6.0733 | 6.0355 | 5.9865 | 5.9508 | 5.8937 | 5.8365 | 5.758 | 5.7171 | 5.6386 | 5.3488 | 0.87041 | 0.85714 | 5.5988 | 5.5478 | 5.4927 | 5.4233 | 5.3682 | 5.2906 | 5.211 | 5.11 | 5.0447 | 4.9498
|  | SANDWICK | HE |  |  |  |  | 0.46633 | 0.42449 | 5.1365 | 5.0784 | 5.0324 | 4.9661 | 4.8927 | 4.7978 | 4.7457 | 4.6569 | 4.2355 | 4.1284 | -0.64796 | 1.7449 | 6.0743 | 6.0406 | 5.9947 | 5.9631 | 5.911 | 5.8549 | 5.7804 | 5.7406 | 5.6712 | 5.3376 | 0.82041 | 0.64592 | 5.5978 | 5.558 | 5.512 | 5.4569 | 5.4141 | 5.3498 | 5.2784 | 5.1896 | 5.1396 | 5.0559
|  | SANDWICK | CF |  |  |  |  | 0.47347 | 0.43673 | 5.1549 | 5.1161 | 5.0651 | 5.0314 | 4.9784 | 4.9192 | 4.859 | 4.7967 | 4.5008 | 4.2569 | -0.63469 | 1.749 | 6.0824 | 6.0539 | 6.0253 | 5.9845 | 5.9569 | 5.91 | 5.859 | 5.8059 | 5.7498 | 5.4569 | 0.7449 | 0.32551 | 5.6049 | 5.5692 | 5.5324 | 5.4937 | 5.4467 | 5.4131 | 5.3631 | 5.3059 | 5.2488 | 5.1896
| SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | 0.051 | -2.6357 | -2.7306 | 3.9049 | 3.7559 | 3.6069 | 3.4712 | 3.3202 | 3.1437 | 3.0222 | 2.8733 | 2.5049 | 2.3743 | -4.4102 | -1.0643 | 5.2294 | 5.1549 | 5.0631 | 4.9753 | 4.8814 | 4.7784 | 4.6559 | 4.5763 | 4.4804 | 4.1957 | -2.3051 | -2.8408 | 4.5304 | 4.4529 | 4.3661 | 4.2365 | 4.1059 | 3.9763 | 3.8233 | 3.6396 | 3.51 | 3.3631
|  | SCALLOWAY | EE |  |  |  |  | -2.6357 | -2.7306 | 3.9049 | 3.7559 | 3.6069 | 3.4712 | 3.3202 | 3.1437 | 3.0222 | 2.8733 | 2.5049 | 2.4529 | -4.35 | -1.0643 | 5.2294 | 5.1549 | 5.0631 | 4.9753 | 4.8814 | 4.7784 | 4.6559 | 4.5763 | 4.4804 | 4.1957 | -2.3051 | -2.549 | 4.5304 | 4.4529 | 4.3661 | 4.2365 | 4.1059 | 3.9763 | 3.8233 | 3.6396 | 3.51 | 3.3631
|  | SCALLOWAY | HT |  |  |  |  | -2.6071 | -2.7031 | 3.9416 | 3.8233 | 3.7182 | 3.61 | 3.4927 | 3.3896 | 3.2682 | 3.1406 | 2.6202 | 2.3743 | -4.4102 | -1.0367 | 5.2651 | 5.2029 | 5.1365 | 5.0763 | 5.01 | 4.9345 | 4.8712 | 4.7906 | 4.7069 | 4.3661 | -2.1531 | -2.1694 | 4.5508 | 4.4773 | 4.3947 | 4.31 | 4.2141 | 4.111 | 4.0029 | 3.9059 | 3.7855 | 3.6529
|  | SCALLOWAY | HE |  |  |  |  | -2.6061 | -2.6582 | 4.0212 | 3.9376 | 3.8294 | 3.7141 | 3.5988 | 3.511 | 3.4069 | 3.2967 | 2.7488 | 2.5988 | -4.1806 | -1.0378 | 5.2824 | 5.2324 | 5.1814 | 5.11 | 5.0406 | 4.96 | 4.9029 | 4.8263 | 4.7488 | 4.3529 | -2.2092 | -2.4347 | 4.5498 | 4.4988 | 4.4365 | 4.3733 | 4.2967 | 4.2049 | 4.0978 | 4.0141 | 3.9161 | 3.8029
|  | SCALLOWAY | CF |  |  |  |  | -2.598 | -2.6429 | 4.0682 | 3.9855 | 3.9141 | 3.8171 | 3.7263 | 3.6304 | 3.5804 | 3.5059 | 3.1314 | 2.7753 | -4.1684 | -1.0327 | 5.2957 | 5.262 | 5.211 | 5.161 | 5.0967 | 5.0345 | 4.9641 | 4.9222 | 4.8631 | 4.5202 | -2.301 | -2.8408 | 4.5682 | 4.5386 | 4.5039 | 4.4529 | 4.3876 | 4.2998 | 4.2182 | 4.1284 | 4.0814 | 4.011
| TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0 | 0.04249 | 0.032286 | 0.029224 | 0.030245 | 0.028204 | 0.023102 | 0.022082 | 0.020041 | 0.010857 | 0.0088163 | -0.0034286 | -0.0064898 | -0.017531 | 0.054918 | 0.045735 | 0.049816 | 0.045735 | 0.045735 | 0.047776 | 0.045735 | 0.044714 | 0.038592 | 0.037571 | 0.028388 | 0.027786 | 0.022684 | 0.053296 | 0.044112 | 0.040031 | 0.041051 | 0.03901 | 0.035949 | 0.032888 | 0.030847 | 0.021663 | 0.019622
|  | SCAMMADALE | EE |  |  |  |  | 0.04249 | 0.032286 | 0.029224 | 0.031265 | 0.030245 | 0.023102 | 0.022082 | 0.020041 | 0.010857 | 0.0088163 | -0.0034286 | -0.0064898 | -0.01549 | 0.054918 | 0.045735 | 0.049816 | 0.051857 | 0.051857 | 0.047776 | 0.045735 | 0.044714 | 0.038592 | 0.037571 | 0.028388 | 0.027786 | 0.025745 | 0.053296 | 0.044112 | 0.040031 | 0.043092 | 0.042071 | 0.035949 | 0.032888 | 0.030847 | 0.021663 | 0.019622
|  | SCAMMADALE | HT |  |  |  |  | 0.049633 | 0.047592 | 0.037388 | 0.030245 | 0.028204 | 0.032286 | 0.028204 | 0.025143 | 0.023102 | 0.01902 | 0.00065306 | -0.0064898 | -0.017531 | 0.062061 | 0.061041 | 0.052878 | 0.045735 | 0.048796 | 0.053898 | 0.051857 | 0.048796 | 0.047776 | 0.042673 | 0.031449 | 0.030847 | 0.030847 | 0.060439 | 0.059418 | 0.048194 | 0.041051 | 0.03901 | 0.044112 | 0.040031 | 0.036969 | 0.034929 | 0.029827
|  | SCAMMADALE | HE |  |  |  |  | 0.049633 | 0.047592 | 0.038408 | 0.030245 | 0.029224 | 0.035347 | 0.030245 | 0.026163 | 0.026163 | 0.01902 | 0.0016735 | -0.0024082 | -0.011408 | 0.062061 | 0.061041 | 0.052878 | 0.045735 | 0.049816 | 0.054918 | 0.051857 | 0.049816 | 0.049816 | 0.044714 | 0.03349 | 0.031867 | 0.029827 | 0.060439 | 0.058398 | 0.049214 | 0.041051 | 0.040031 | 0.046153 | 0.042071 | 0.03901 | 0.03799 | 0.030847
|  | SCAMMADALE | CF |  |  |  |  | 0.049633 | 0.047592 | 0.040449 | 0.039429 | 0.031265 | 0.030245 | 0.035347 | 0.031265 | 0.031265 | 0.026163 | 0.01698 | 0.0037143 | -0.0083469 | 0.062061 | 0.061041 | 0.053898 | 0.053898 | 0.045735 | 0.049816 | 0.054918 | 0.051857 | 0.051857 | 0.049816 | 0.039612 | 0.033908 | 0.022684 | 0.060439 | 0.059418 | 0.052276 | 0.050235 | 0.042071 | 0.041051 | 0.046153 | 0.043092 | 0.042071 | 0.03901
| ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 3.485 | 7.5212 | 7.21 | 6.8722 | 6.4671 | 6.0773 | 5.6151 | 5.0294 | 4.7875 | 4.2406 | 3.6814 | 1.5253 | 0.46916 | -0.43696 | 8.8967 | 8.7467 | 8.5692 | 8.3426 | 8.1212 | 7.8549 | 7.5263 | 7.4355 | 7.1263 | 6.8457 | 5.7059 | 5.435 | 4.5819 | 8.5625 | 8.285 | 7.988 | 7.6278 | 7.2768 | 6.8625 | 6.335 | 6.1003 | 5.6074 | 5.1431
|  | SCONE | EE |  |  |  |  | 7.5212 | 7.21 | 6.8722 | 6.4671 | 6.0773 | 5.6151 | 5.0294 | 4.7875 | 4.2406 | 3.7314 | 1.5732 | 0.60794 | -0.33288 | 8.8967 | 8.7467 | 8.5692 | 8.3426 | 8.1212 | 7.8549 | 7.5263 | 7.4355 | 7.1263 | 6.8457 | 5.7059 | 5.435 | 4.8309 | 8.5625 | 8.285 | 7.988 | 7.6278 | 7.2768 | 6.8625 | 6.335 | 6.1003 | 5.6074 | 5.1431
|  | SCONE | HT |  |  |  |  | 7.609 | 7.3324 | 6.9988 | 6.6702 | 6.2834 | 5.8559 | 5.36 | 4.8018 | 4.2457 | 3.6814 | 1.5253 | 0.46916 | -0.43696 | 8.9273 | 8.8222 | 8.659 | 8.4977 | 8.3028 | 8.0947 | 7.863 | 7.5753 | 7.2875 | 6.9947 | 6.0079 | 5.886 | 5.8146 | 8.6401 | 8.3921 | 8.0993 | 7.8044 | 7.4584 | 7.0819 | 6.6482 | 6.1482 | 5.6533 | 5.1493
|  | SCONE | HE |  |  |  |  | 7.6181 | 7.4345 | 7.1906 | 6.959 | 6.6661 | 6.3447 | 5.9947 | 5.5712 | 5.1518 | 4.7212 | 2.9743 | 1.8028 | 0.65488 | 8.9253 | 8.8579 | 8.7263 | 8.5977 | 8.4406 | 8.2641 | 8.0692 | 7.8212 | 7.5753 | 7.3222 | 6.3273 | 5.9503 | 5.3013 | 8.6482 | 8.487 | 8.2778 | 8.0758 | 7.8176 | 7.5329 | 7.2207 | 6.8411 | 6.4656 | 6.0809
|  | SCONE | CF |  |  |  |  | 7.6732 | 7.5263 | 7.3702 | 7.1692 | 6.9875 | 6.7549 | 6.5314 | 6.3192 | 6.0794 | 5.8324 | 4.6732 | 3.3396 | 1.4977 | 8.9467 | 8.8937 | 8.8049 | 8.6916 | 8.5845 | 8.4457 | 8.3008 | 8.1518 | 7.9845 | 7.813 | 6.9794 | 6.1095 | 4.5819 | 8.6982 | 8.5748 | 8.4411 | 8.2687 | 8.1105 | 7.9125 | 7.7176 | 7.5329 | 7.3227 | 7.0962
| THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | NO | 0 | 0.73163 | 0.71735 | 0.69796 | 0.68673 | 0.66327 | 0.65408 | 0.62755 | 0.59796 | 0.58163 | 0.5602 | 0.50714 | 0.49286 | 0.48571 | 0.85612 | 0.84592 | 0.83163 | 0.82449 | 0.80714 | 0.80204 | 0.78061 | 0.75918 | 0.74898 | 0.73469 | 0.6949 | 0.68367 | 0.65 | 0.79898 | 0.78367 | 0.76735 | 0.7551 | 0.73265 | 0.72449 | 0.69898 | 0.67041 | 0.65714 | 0.63571
|  | SHAPINSAY | EE |  |  |  |  | 0.73163 | 0.71735 | 0.69796 | 0.68673 | 0.66327 | 0.65408 | 0.62755 | 0.59796 | 0.58163 | 0.5602 | 0.50714 | 0.5 | 0.4949 | 0.85612 | 0.84592 | 0.83163 | 0.82449 | 0.80714 | 0.80204 | 0.78061 | 0.75918 | 0.74898 | 0.73469 | 0.6949 | 0.68367 | 0.66633 | 0.79898 | 0.78367 | 0.76735 | 0.7551 | 0.73265 | 0.72449 | 0.69898 | 0.67041 | 0.65714 | 0.63571
|  | SHAPINSAY | HT |  |  |  |  | 0.73163 | 0.72653 | 0.71633 | 0.7051 | 0.68878 | 0.67653 | 0.65612 | 0.64694 | 0.62653 | 0.60408 | 0.52245 | 0.49286 | 0.48571 | 0.85612 | 0.85306 | 0.8449 | 0.83878 | 0.82653 | 0.82041 | 0.80612 | 0.79898 | 0.78673 | 0.76939 | 0.71224 | 0.69388 | 0.69082 | 0.80306 | 0.7949 | 0.78469 | 0.77653 | 0.7602 | 0.75 | 0.72959 | 0.71837 | 0.70102 | 0.67959
|  | SHAPINSAY | HE |  |  |  |  | 0.73673 | 0.73061 | 0.71735 | 0.70918 | 0.69796 | 0.68776 | 0.66837 | 0.65816 | 0.63878 | 0.62041 | 0.53367 | 0.51122 | 0.50408 | 0.86122 | 0.85408 | 0.8449 | 0.84082 | 0.83061 | 0.82551 | 0.80816 | 0.80408 | 0.78878 | 0.77551 | 0.71122 | 0.69286 | 0.67551 | 0.80612 | 0.79694 | 0.78571 | 0.77857 | 0.76531 | 0.75612 | 0.73673 | 0.73163 | 0.71122 | 0.69184
|  | SHAPINSAY | CF |  |  |  |  | 0.73367 | 0.73061 | 0.72347 | 0.71633 | 0.70612 | 0.69286 | 0.68878 | 0.66939 | 0.6551 | 0.65306 | 0.59184 | 0.52755 | 0.50918 | 0.85612 | 0.85816 | 0.85102 | 0.84592 | 0.83776 | 0.82653 | 0.82347 | 0.81122 | 0.79898 | 0.79796 | 0.74898 | 0.68776 | 0.65 | 0.80408 | 0.80306 | 0.7949 | 0.78776 | 0.77857 | 0.76531 | 0.76122 | 0.74184 | 0.72755 | 0.72857
| BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 0.028 | 0.65918 | 0.6602 | 0.65204 | 0.63673 | 0.62143 | 0.6102 | 0.59286 | 0.58265 | 0.56633 | 0.55 | 0.51429 | 0.50408 | 0.50102 | 0.75816 | 0.7602 | 0.75204 | 0.74286 | 0.73163 | 0.72347 | 0.7102 | 0.70408 | 0.6898 | 0.67959 | 0.65408 | 0.64694 | 0.61837 | 0.68673 | 0.68571 | 0.67959 | 0.66531 | 0.65204 | 0.64082 | 0.62347 | 0.61327 | 0.59898 | 0.58367
|  | SHIELDAIG | EE |  |  |  |  | 0.66531 | 0.6602 | 0.65204 | 0.63673 | 0.62143 | 0.6102 | 0.59286 | 0.58265 | 0.56633 | 0.55 | 0.51429 | 0.5102 | 0.50612 | 0.76327 | 0.7602 | 0.75204 | 0.74286 | 0.73163 | 0.72347 | 0.7102 | 0.70408 | 0.6898 | 0.67959 | 0.65408 | 0.64694 | 0.62959 | 0.69286 | 0.68571 | 0.67959 | 0.66531 | 0.65204 | 0.64082 | 0.62347 | 0.61327 | 0.59898 | 0.58367
|  | SHIELDAIG | HT |  |  |  |  | 0.65918 | 0.66429 | 0.65816 | 0.64796 | 0.6398 | 0.62959 | 0.61429 | 0.60612 | 0.59082 | 0.57449 | 0.52755 | 0.50408 | 0.50102 | 0.75816 | 0.76531 | 0.75918 | 0.75306 | 0.74898 | 0.74082 | 0.73061 | 0.72449 | 0.71429 | 0.70306 | 0.66837 | 0.65204 | 0.65102 | 0.68673 | 0.69184 | 0.68469 | 0.67857 | 0.66735 | 0.6602 | 0.64388 | 0.63776 | 0.62347 | 0.60816
|  | SHIELDAIG | HE |  |  |  |  | 0.65918 | 0.66633 | 0.65918 | 0.65204 | 0.64694 | 0.63776 | 0.62449 | 0.61531 | 0.60204 | 0.58878 | 0.53367 | 0.51735 | 0.51735 | 0.75816 | 0.76633 | 0.75918 | 0.75408 | 0.75102 | 0.7449 | 0.73571 | 0.72857 | 0.71735 | 0.70612 | 0.66837 | 0.65306 | 0.63878 | 0.68673 | 0.69286 | 0.68571 | 0.68163 | 0.67449 | 0.66633 | 0.65306 | 0.64592 | 0.63265 | 0.62041
|  | SHIELDAIG | CF |  |  |  |  | 0.66735 | 0.66531 | 0.66224 | 0.65612 | 0.65102 | 0.64694 | 0.63878 | 0.62755 | 0.62347 | 0.61429 | 0.57755 | 0.53571 | 0.51939 | 0.76735 | 0.76224 | 0.76224 | 0.75714 | 0.75204 | 0.75 | 0.74184 | 0.73469 | 0.73265 | 0.72551 | 0.69184 | 0.65 | 0.61837 | 0.6949 | 0.69286 | 0.6898 | 0.68367 | 0.67857 | 0.67551 | 0.66633 | 0.65816 | 0.65306 | 0.6449
| SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | NO | 0.019 | 2.5357 | 2.5184 | 2.4929 | 2.4735 | 2.4439 | 2.4327 | 2.3969 | 2.3704 | 2.3357 | 2.3061 | 2.2378 | 2.2173 | 1.9852 | 2.4821 | 2.4699 | 2.4546 | 2.4383 | 2.4219 | 2.4138 | 2.3913 | 2.375 | 2.3495 | 2.3311 | 2.2832 | 2.3783 | 2.3089 | 2.5038 | 2.4875 | 2.4661 | 2.4477 | 2.4222 | 2.411 | 2.3773 | 2.3528 | 2.3191 | 2.2895
|  | SHIN | EE |  |  |  |  | 2.5357 | 2.5184 | 2.4929 | 2.4735 | 2.4439 | 2.4327 | 2.3969 | 2.3704 | 2.3357 | 2.3061 | 2.2378 | 2.2276 | 1.9964 | 2.4821 | 2.4699 | 2.4546 | 2.4383 | 2.4219 | 2.4138 | 2.3913 | 2.375 | 2.3495 | 2.3311 | 2.2832 | 2.3783 | 2.3477 | 2.5038 | 2.4875 | 2.4661 | 2.4477 | 2.4222 | 2.411 | 2.3773 | 2.3528 | 2.3191 | 2.2895
|  | SHIN | HT |  |  |  |  | 2.5469 | 2.5286 | 2.5173 | 2.4969 | 2.4827 | 2.4582 | 2.4316 | 2.4163 | 2.3888 | 2.3622 | 2.2592 | 2.2173 | 1.9852 | 2.4872 | 2.4781 | 2.4719 | 2.4617 | 2.4526 | 2.4362 | 2.4189 | 2.4128 | 2.3934 | 2.375 | 2.3066 | 2.3916 | 2.3885 | 2.511 | 2.4957 | 2.4834 | 2.4651 | 2.4508 | 2.4304 | 2.4089 | 2.3957 | 2.3702 | 2.3467
|  | SHIN | HE |  |  |  |  | 2.5469 | 2.5327 | 2.5255 | 2.5071 | 2.4949 | 2.4745 | 2.451 | 2.4388 | 2.4163 | 2.3888 | 2.2704 | 2.2408 | 2.0107 | 2.4872 | 2.4791 | 2.474 | 2.4628 | 2.4546 | 2.4413 | 2.425 | 2.4179 | 2.4015 | 2.3832 | 2.3046 | 2.3865 | 2.3579 | 2.511 | 2.4987 | 2.4906 | 2.4773 | 2.4651 | 2.4477 | 2.4273 | 2.4161 | 2.3957 | 2.3702
|  | SHIN | CF |  |  |  |  | 2.5418 | 2.5337 | 2.5245 | 2.5143 | 2.501 | 2.4908 | 2.4745 | 2.4531 | 2.451 | 2.4327 | 2.352 | 2.2735 | 2.0148 | 2.4842 | 2.4801 | 2.473 | 2.4679 | 2.4597 | 2.4536 | 2.4403 | 2.426 | 2.4219 | 2.4117 | 2.3444 | 2.3804 | 2.3089 | 2.5079 | 2.5018 | 2.4926 | 2.4834 | 2.4722 | 2.463 | 2.4487 | 2.4314 | 2.4263 | 2.411
| FORT WILLIAM | SHONA BEG | MINIMUM HEADROOM | NM 67173 74363 | YES | NO | 0 | 0.095551 | 0.095551 | 0.095551 | 0.087388 | 0.087388 | 0.087388 | 0.085347 | 0.077184 | 0.077184 | 0.075143 | 0.072082 | 0.062898 | 0.053898 | 0.092673 | 0.092673 | 0.091653 | 0.08451 | 0.08451 | 0.08451 | 0.08349 | 0.075327 | 0.075327 | 0.075327 | 0.073286 | 0.069622 | 0.067582 | 0.096153 | 0.096153 | 0.095133 | 0.08799 | 0.08799 | 0.086969 | 0.084929 | 0.076765 | 0.076765 | 0.074724
|  | SHONA BEG | EE |  |  |  |  | 0.095551 | 0.095551 | 0.095551 | 0.087388 | 0.087388 | 0.087388 | 0.085347 | 0.077184 | 0.077184 | 0.075143 | 0.072082 | 0.064939 | 0.055939 | 0.092673 | 0.092673 | 0.091653 | 0.08451 | 0.08451 | 0.08451 | 0.08349 | 0.075327 | 0.075327 | 0.075327 | 0.073286 | 0.070643 | 0.067582 | 0.096153 | 0.096153 | 0.095133 | 0.08799 | 0.08799 | 0.086969 | 0.084929 | 0.076765 | 0.076765 | 0.074724
|  | SHONA BEG | HT |  |  |  |  | 0.095551 | 0.095551 | 0.096571 | 0.095551 | 0.094531 | 0.087388 | 0.085347 | 0.085347 | 0.085347 | 0.082286 | 0.073102 | 0.062898 | 0.053898 | 0.092673 | 0.092673 | 0.092673 | 0.091653 | 0.091653 | 0.08451 | 0.08349 | 0.08349 | 0.08349 | 0.082469 | 0.074306 | 0.069622 | 0.069622 | 0.096153 | 0.096153 | 0.096153 | 0.095133 | 0.095133 | 0.08799 | 0.084929 | 0.084929 | 0.084929 | 0.082888
|  | SHONA BEG | HE |  |  |  |  | 0.095551 | 0.095551 | 0.095551 | 0.095551 | 0.094531 | 0.087388 | 0.087388 | 0.087388 | 0.084327 | 0.084327 | 0.073102 | 0.065959 | 0.056959 | 0.092673 | 0.092673 | 0.092673 | 0.091653 | 0.091653 | 0.08451 | 0.08451 | 0.08451 | 0.08451 | 0.08349 | 0.074306 | 0.071663 | 0.067582 | 0.096153 | 0.096153 | 0.096153 | 0.095133 | 0.095133 | 0.08799 | 0.08799 | 0.08799 | 0.085949 | 0.084929
|  | SHONA BEG | CF |  |  |  |  | 0.095551 | 0.095551 | 0.095551 | 0.095551 | 0.094531 | 0.09351 | 0.086367 | 0.086367 | 0.086367 | 0.086367 | 0.078204 | 0.076163 | 0.063082 | 0.092673 | 0.092673 | 0.092673 | 0.092673 | 0.091653 | 0.090633 | 0.08349 | 0.08349 | 0.08349 | 0.08349 | 0.076347 | 0.075745 | 0.071663 | 0.096153 | 0.096153 | 0.096153 | 0.096153 | 0.095133 | 0.094112 | 0.086969 | 0.086969 | 0.086969 | 0.086969
| KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 2.223 | 23.2964 | 22.9873 | 22.5964 | 22.1791 | 21.7016 | 21.2801 | 20.5475 | 19.6964 | 18.9107 | 18.1689 | 15.2883 | 13.7434 | 13.2464 | 26.4607 | 26.2373 | 25.9781 | 25.7005 | 25.3964 | 25.175 | 24.8026 | 24.3454 | 23.9373 | 23.5648 | 22.0771 | 21.1556 | 20.7281 | 25.5699 | 25.2403 | 24.8709 | 24.4577 | 23.9454 | 23.5597 | 22.8811 | 22.0862 | 21.3597 | 20.674
|  | SKENE | EE |  |  |  |  | 23.2964 | 22.9873 | 22.5964 | 22.1791 | 21.7016 | 21.2801 | 20.5475 | 19.6964 | 18.9107 | 18.1689 | 15.2883 | 14.0873 | 13.8128 | 26.4607 | 26.2373 | 25.9781 | 25.7005 | 25.3964 | 25.175 | 24.8026 | 24.3454 | 23.9373 | 23.5648 | 22.2526 | 21.9301 | 21.8179 | 25.5699 | 25.2403 | 24.8709 | 24.4577 | 23.9454 | 23.5597 | 22.8811 | 22.0862 | 21.3597 | 20.674
|  | SKENE | HT |  |  |  |  | 23.4322 | 23.1842 | 22.8709 | 22.523 | 22.1158 | 21.6046 | 20.8903 | 20.2373 | 19.4699 | 18.6413 | 15.2913 | 13.7434 | 13.3016 | 26.5832 | 26.3985 | 26.2128 | 25.9995 | 25.7699 | 25.5046 | 25.1679 | 24.8689 | 24.4954 | 24.0893 | 22.4005 | 21.7087 | 21.4485 | 25.7199 | 25.4322 | 25.1403 | 24.7842 | 24.3628 | 23.8832 | 23.2291 | 22.6332 | 21.9271 | 21.1699
|  | SKENE | HE |  |  |  |  | 23.4199 | 23.2056 | 22.9495 | 22.6434 | 22.3189 | 21.9393 | 21.4454 | 20.9036 | 20.2526 | 19.5618 | 16.0709 | 14.1128 | 13.2464 | 26.5669 | 26.3862 | 26.2087 | 25.9954 | 25.7628 | 25.4954 | 25.1587 | 24.8444 | 24.4658 | 24.0546 | 22.0771 | 21.1556 | 20.7281 | 25.7046 | 25.4526 | 25.2046 | 24.9128 | 24.6056 | 24.2424 | 23.7005 | 23.1893 | 22.5811 | 21.9301
|  | SKENE | CF |  |  |  |  | 23.4934 | 23.3709 | 23.2362 | 23.0709 | 22.875 | 22.6464 | 22.3934 | 22.0587 | 21.873 | 21.5567 | 19.224 | 16.5352 | 14.476 | 26.6291 | 26.525 | 26.4077 | 26.274 | 26.1301 | 25.9628 | 25.775 | 25.525 | 25.3985 | 25.1658 | 23.6454 | 22.1434 | 21.076 | 25.7954 | 25.6536 | 25.4975 | 25.3158 | 25.1291 | 24.9107 | 24.6689 | 24.3454 | 24.172 | 23.873
| BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | 5.142 | 2.0004 | 1.9157 | 1.8055 | 1.7086 | 1.5851 | 1.4423 | 1.28 | 1.1004 | 0.90145 | 0.73411 | 0.33513 | 0.22186 | 0.19227 | 2.6555 | 2.6015 | 2.5341 | 2.4759 | 2.3974 | 2.3086 | 2.2066 | 2.1015 | 1.9821 | 1.879 | 1.6086 | 1.5106 | 1.1872 | 2.2841 | 2.2045 | 2.1025 | 2.0147 | 1.8974 | 1.7688 | 1.6178 | 1.4555 | 1.2749 | 1.1229
|  | SKULAMUS | EE |  |  |  |  | 2.0004 | 1.9157 | 1.8055 | 1.7086 | 1.5851 | 1.4423 | 1.28 | 1.1004 | 0.90145 | 0.73411 | 0.33513 | 0.28104 | 0.24839 | 2.6555 | 2.6015 | 2.5341 | 2.4759 | 2.3974 | 2.3086 | 2.2066 | 2.1015 | 1.9821 | 1.879 | 1.6086 | 1.5106 | 1.3484 | 2.2841 | 2.2045 | 2.1025 | 2.0147 | 1.8974 | 1.7688 | 1.6178 | 1.4555 | 1.2749 | 1.1229
|  | SKULAMUS | HT |  |  |  |  | 2.0341 | 1.9535 | 1.877 | 1.7912 | 1.68 | 1.5372 | 1.3688 | 1.1943 | 1.0239 | 0.89737 | 0.42594 | 0.22186 | 0.19227 | 2.68 | 2.6361 | 2.5943 | 2.5464 | 2.48 | 2.4086 | 2.3137 | 2.2147 | 2.1178 | 2.0515 | 1.7351 | 1.6086 | 1.5923 | 2.3168 | 2.2433 | 2.1739 | 2.0974 | 1.9943 | 1.8678 | 1.7157 | 1.5637 | 1.4106 | 1.2994
|  | SKULAMUS | HE |  |  |  |  | 2.0321 | 1.9668 | 1.9076 | 1.8382 | 1.7423 | 1.6617 | 1.5494 | 1.3943 | 1.2392 | 1.1382 | 0.52798 | 0.40145 | 0.37798 | 2.679 | 2.6382 | 2.6025 | 2.5617 | 2.4994 | 2.4525 | 2.3821 | 2.2902 | 2.1964 | 2.1392 | 1.7402 | 1.5933 | 1.4433 | 2.3147 | 2.2576 | 2.2015 | 2.1372 | 2.0484 | 1.978 | 1.8749 | 1.7351 | 1.5964 | 1.5076
|  | SKULAMUS | CF |  |  |  |  | 2.0464 | 1.9974 | 1.9474 | 1.8831 | 1.8147 | 1.729 | 1.6719 | 1.579 | 1.4606 | 1.3555 | 0.89533 | 0.57594 | 0.40247 | 2.6892 | 2.6576 | 2.627 | 2.5831 | 2.5433 | 2.4872 | 2.4515 | 2.3872 | 2.3137 | 2.2464 | 1.9106 | 1.5555 | 1.1872 | 2.328 | 2.2841 | 2.2372 | 2.1749 | 2.1168 | 2.0351 | 1.9831 | 1.8953 | 1.7943 | 1.6964
| WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 5.874 | 18.9459 | 18.2235 | 17.4143 | 16.8153 | 15.9816 | 15.1796 | 13.7531 | 12.1837 | 10.5551 | 8.749 | 0.7602 | -4.3653 | -6.7204 | 22.1041 | 21.7255 | 21.2806 | 21.0337 | 20.5816 | 20.051 | 19.3071 | 18.4418 | 17.6041 | 16.8153 | 13.2735 | 11.4786 | 9.4735 | 20.2694 | 19.6245 | 18.8918 | 18.3888 | 17.6388 | 16.8898 | 15.6122 | 14.2031 | 12.8184 | 11.3112
|  | SPRINGHILL | EE |  |  |  |  | 18.9459 | 18.2235 | 17.4143 | 16.852 | 16.0367 | 15.1796 | 13.7531 | 12.1837 | 10.6286 | 9.102 | 1.6286 | -3.801 | -6.5827 | 22.1041 | 21.7255 | 21.2806 | 21.0337 | 20.5816 | 20.051 | 19.3071 | 18.4418 | 17.6041 | 16.8153 | 13.2735 | 11.4786 | 9.4735 | 20.2694 | 19.6245 | 18.8918 | 18.4031 | 17.6663 | 16.8898 | 15.6122 | 14.2031 | 12.8184 | 11.4653
|  | SPRINGHILL | HT |  |  |  |  | 19.0724 | 18.3571 | 17.5816 | 16.8153 | 15.9816 | 15.3704 | 13.8316 | 12.2214 | 10.5551 | 8.749 | 0.7602 | -4.3653 | -6.7204 | 22.2357 | 21.9031 | 21.5276 | 21.1602 | 20.7449 | 20.5173 | 19.8265 | 19.0878 | 18.3235 | 17.4878 | 13.7755 | 12.552 | 12.0786 | 20.4 | 19.7653 | 19.0745 | 18.3888 | 17.6388 | 17.1184 | 15.7643 | 14.3429 | 12.8837 | 11.3112
|  | SPRINGHILL | HE |  |  |  |  | 19.0837 | 18.6827 | 18.2306 | 17.7806 | 17.2684 | 16.9837 | 16.1092 | 15.0286 | 13.9173 | 12.7265 | 5.9337 | 0.68163 | -2.8735 | 22.2235 | 21.9898 | 21.7214 | 21.4531 | 21.1378 | 21.0102 | 20.5612 | 19.9847 | 19.3867 | 18.7306 | 15.0714 | 13.2582 | 11.0153 | 20.4082 | 20.052 | 19.6429 | 19.2388 | 18.7694 | 18.5347 | 17.751 | 16.8 | 15.8245 | 14.7857
|  | SPRINGHILL | CF |  |  |  |  | 19.2582 | 19.0378 | 18.7704 | 18.5061 | 18.1949 | 17.8582 | 17.502 | 17.4245 | 17.0429 | 16.6071 | 12.4388 | 7.3449 | 1.3582 | 22.3031 | 22.148 | 21.9551 | 21.7684 | 21.5469 | 21.2867 | 20.9888 | 20.9296 | 20.6082 | 20.2449 | 17.401 | 14.5388 | 9.8765 | 20.5653 | 20.3673 | 20.1276 | 19.8888 | 19.6092 | 19.298 | 18.9745 | 18.9235 | 18.5847 | 18.1959
| BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | NO | 0.676 | 4.1531 | 4.0694 | 3.9521 | 3.798 | 3.6296 | 3.4541 | 3.3103 | 3.1245 | 2.9613 | 2.8378 | 2.5705 | 2.4715 | 2.4296 | 6.2521 | 6.1837 | 6.1011 | 5.996 | 5.8817 | 5.7684 | 5.6837 | 5.5623 | 5.4531 | 5.3674 | 5.1868 | 5.0664 | 4.6684 | 4.8256 | 4.7205 | 4.6113 | 4.4715 | 4.3184 | 4.1572 | 4.0317 | 3.8572 | 3.698 | 3.5766
|  | ST CYRUS | EE |  |  |  |  | 4.1531 | 4.0694 | 3.9521 | 3.798 | 3.6296 | 3.4541 | 3.3103 | 3.1245 | 2.9613 | 2.8378 | 2.5705 | 2.5154 | 2.4837 | 6.2521 | 6.1837 | 6.1011 | 5.996 | 5.8817 | 5.7684 | 5.6837 | 5.5623 | 5.4531 | 5.3674 | 5.1868 | 5.0756 | 4.9072 | 4.8256 | 4.7205 | 4.6113 | 4.4715 | 4.3184 | 4.1572 | 4.0317 | 3.8572 | 3.698 | 3.5766
|  | ST CYRUS | HT |  |  |  |  | 4.1878 | 4.1041 | 3.9766 | 3.8276 | 3.6756 | 3.5225 | 3.395 | 3.2511 | 3.1511 | 3.046 | 2.6531 | 2.4715 | 2.4296 | 6.2796 | 6.2113 | 6.1327 | 6.0337 | 5.9337 | 5.8398 | 5.7664 | 5.6786 | 5.6266 | 5.5582 | 5.3062 | 5.2011 | 5.1735 | 4.8582 | 4.7664 | 4.6582 | 4.5266 | 4.4041 | 4.2664 | 4.1541 | 4.0184 | 3.9337 | 3.8286
|  | ST CYRUS | HE |  |  |  |  | 4.1888 | 4.1296 | 4.0286 | 3.9021 | 3.7817 | 3.6429 | 3.5123 | 3.3756 | 3.2837 | 3.1858 | 2.698 | 2.5735 | 2.5531 | 6.2817 | 6.2235 | 6.1521 | 6.0664 | 5.9847 | 5.8929 | 5.8103 | 5.7174 | 5.6654 | 5.5939 | 5.2643 | 5.1113 | 4.9541 | 4.8613 | 4.7837 | 4.695 | 4.5827 | 4.4807 | 4.3562 | 4.2398 | 4.1103 | 4.0337 | 3.9337
|  | ST CYRUS | CF |  |  |  |  | 4.2031 | 4.1552 | 4.0837 | 3.999 | 3.896 | 3.8021 | 3.7041 | 3.599 | 3.5021 | 3.4276 | 3.0643 | 2.749 | 2.5684 | 6.2909 | 6.245 | 6.196 | 6.1398 | 6.0725 | 6.0092 | 5.9419 | 5.8664 | 5.8001 | 5.7368 | 5.4256 | 5.0664 | 4.6684 | 4.8705 | 4.8041 | 4.7358 | 4.6643 | 4.5694 | 4.4929 | 4.399 | 4.3031 | 4.2123 | 4.1307
| ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 0916 5377 | NO | NO | 0 | 23.2806 | 23.2184 | 23.148 | 23.0786 | 23.0041 | 22.9204 | 22.8235 | 22.6969 | 22.5755 | 22.4663 | 22.0418 | 21.8378 | 21.7888 | 29.949 | 29.9071 | 29.8531 | 29.8082 | 29.752 | 29.6908 | 29.6316 | 29.5408 | 29.4561 | 29.3806 | 29.1245 | 28.9765 | 28.8214 | 38.898 | 38.8255 | 38.7337 | 38.6612 | 38.5714 | 38.4653 | 38.3684 | 38.2163 | 38.0684 | 37.9429
|  | ST FERGUS GAS TERM | EE |  |  |  |  | 23.2806 | 23.2184 | 23.148 | 23.0786 | 23.0041 | 22.9204 | 22.8235 | 22.6969 | 22.5755 | 22.4663 | 22.0602 | 21.8622 | 21.8204 | 29.949 | 29.9071 | 29.8531 | 29.8082 | 29.752 | 29.6908 | 29.6316 | 29.5408 | 29.4561 | 29.3806 | 29.1245 | 28.9765 | 28.848 | 38.898 | 38.8255 | 38.7337 | 38.6612 | 38.5714 | 38.4653 | 38.3684 | 38.2163 | 38.0684 | 37.9429
|  | ST FERGUS GAS TERM | HT |  |  |  |  | 23.2918 | 23.2255 | 23.1633 | 23.0908 | 23.0194 | 22.948 | 22.8337 | 22.7092 | 22.5806 | 22.4714 | 22.0418 | 21.8378 | 21.7888 | 29.9663 | 29.9245 | 29.8847 | 29.8418 | 29.7898 | 29.75 | 29.6827 | 29.6041 | 29.5224 | 29.4633 | 29.1827 | 29.0663 | 29.0429 | 38.9214 | 38.849 | 38.7837 | 38.7071 | 38.6194 | 38.5541 | 38.4337 | 38.2959 | 38.152 | 38.048
|  | ST FERGUS GAS TERM | HE |  |  |  |  | 23.2918 | 23.25 | 23.2112 | 23.1653 | 23.1102 | 23.0622 | 22.9867 | 22.8929 | 22.8031 | 22.7316 | 22.2806 | 22.0245 | 21.9 | 29.9643 | 29.9316 | 29.9041 | 29.8694 | 29.8265 | 29.798 | 29.7429 | 29.6796 | 29.6143 | 29.5704 | 29.2541 | 29.0714 | 28.9163 | 38.9214 | 38.8724 | 38.8265 | 38.7735 | 38.7061 | 38.6429 | 38.551 | 38.4378 | 38.3296 | 38.2347
|  | ST FERGUS GAS TERM | CF |  |  |  |  | 23.3071 | 23.2796 | 23.251 | 23.2163 | 23.1857 | 23.148 | 23.1184 | 23.0755 | 23.0337 | 22.9959 | 22.7041 | 22.4031 | 22.1663 | 29.9735 | 29.951 | 29.9255 | 29.8969 | 29.8724 | 29.8408 | 29.8173 | 29.7776 | 29.7388 | 29.7051 | 29.4602 | 29.152 | 28.8214 | 38.9398 | 38.9031 | 38.8694 | 38.8224 | 38.7867 | 38.7367 | 38.7092 | 38.649 | 38.601 | 38.548
| PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | NO | 0.184 | 14.4867 | 14.0337 | 13.5102 | 12.9367 | 12.302 | 11.6571 | 10.6286 | 9.4663 | 8.3643 | 7.3888 | 2.9673 | -0.14082 | -1.4792 | 15.4218 | 15.1708 | 14.8759 | 14.5576 | 14.1433 | 13.7035 | 13.0973 | 12.3831 | 11.7188 | 11.1606 | 8.7076 | 7.7963 | 6.578 | 14.6718 | 14.2524 | 13.7596 | 13.2218 | 12.6178 | 12.0035 | 11.0473 | 9.9596 | 8.9341 | 8.0382
|  | ST MACHAR | EE |  |  |  |  | 14.4867 | 14.0337 | 13.5102 | 12.9367 | 12.302 | 11.6571 | 10.6286 | 9.4663 | 8.3643 | 7.3888 | 2.9673 | 0.11327 | -1.4792 | 15.4218 | 15.1708 | 14.8759 | 14.5576 | 14.1433 | 13.7035 | 13.0973 | 12.3831 | 11.7188 | 11.1606 | 8.7076 | 7.7963 | 6.578 | 14.6718 | 14.2524 | 13.7596 | 13.2218 | 12.6178 | 12.0035 | 11.0473 | 9.9596 | 8.9341 | 8.0382
|  | ST MACHAR | HT |  |  |  |  | 14.6847 | 14.2969 | 13.8888 | 13.4408 | 12.9694 | 12.4367 | 11.4888 | 10.449 | 9.448 | 8.3694 | 3.1755 | -0.14082 | -1.422 | 15.5463 | 15.4096 | 15.2157 | 15.0004 | 14.7494 | 14.4167 | 13.9188 | 13.3535 | 12.832 | 12.2453 | 9.4861 | 8.4412 | 8.2586 | 14.8106 | 14.5269 | 14.1453 | 13.7208 | 13.2769 | 12.7749 | 11.9086 | 10.9524 | 10.0494 | 9.0637
|  | ST MACHAR | HE |  |  |  |  | 14.648 | 14.3663 | 14.0673 | 13.7173 | 13.3469 | 12.9184 | 12.2133 | 11.3806 | 10.6122 | 9.7786 | 5.402 | 2.5408 | 1.0086 | 15.5137 | 15.3382 | 15.1178 | 14.8596 | 14.5688 | 14.2269 | 13.8004 | 13.2688 | 12.7688 | 12.232 | 9.6382 | 8.6943 | 7.632 | 14.7729 | 14.58 | 14.2912 | 13.9555 | 13.6045 | 13.1943 | 12.5351 | 11.7616 | 11.0524 | 10.279
|  | ST MACHAR | CF |  |  |  |  | 14.7714 | 14.6255 | 14.4429 | 14.251 | 14.0235 | 13.7929 | 13.5204 | 13.1776 | 12.8541 | 12.5041 | 10.0673 | 7.55 | 4.1841 | 15.5657 | 15.4861 | 15.379 | 15.23 | 15.0535 | 14.8616 | 14.6473 | 14.3637 | 14.1004 | 13.8137 | 11.9392 | 10.1769 | 7.1912 | 14.8545 | 14.7555 | 14.6331 | 14.4586 | 14.2371 | 14.0106 | 13.7473 | 13.4188 | 13.1055 | 12.7708
| THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | NO | 0 | -2.1949 | -2.2867 | -2.3684 | -2.4694 | -2.5847 | -2.6714 | -2.8143 | -3.0133 | -3.2122 | -3.4908 | -4.0408 | -4.1643 | -4.2122 | -1.1408 | -1.199 | -1.2459 | -1.3133 | -1.4122 | -1.4694 | -1.5857 | -1.7286 | -1.8173 | -1.9347 | -2.1459 | -2.2704 | -2.7194 | -1.9082 | -1.9969 | -2.0765 | -2.1776 | -2.302 | -2.3786 | -2.5245 | -2.7071 | -2.8214 | -2.9724
|  | ST MARYS | EE |  |  |  |  | -2.1949 | -2.2867 | -2.3684 | -2.4694 | -2.5847 | -2.6714 | -2.8143 | -3.0133 | -3.1867 | -3.4286 | -4.0408 | -4.1082 | -4.1418 | -1.1408 | -1.199 | -1.2459 | -1.3133 | -1.4122 | -1.4694 | -1.5857 | -1.7286 | -1.8173 | -1.9347 | -2.1459 | -2.2653 | -2.4541 | -1.9082 | -1.9969 | -2.0765 | -2.1776 | -2.302 | -2.3786 | -2.5245 | -2.7071 | -2.8214 | -2.9724
|  | ST MARYS | HT |  |  |  |  | -2.1673 | -2.2367 | -2.3082 | -2.3827 | -2.4704 | -2.5602 | -2.7429 | -2.9378 | -3.2122 | -3.4908 | -3.9439 | -4.1643 | -4.2122 | -1.1071 | -1.1418 | -1.1806 | -1.2163 | -1.2694 | -1.3224 | -1.4102 | -1.4867 | -1.6061 | -1.7459 | -2.0796 | -2.1724 | -2.1888 | -1.8592 | -1.9133 | -1.9765 | -2.0327 | -2.1163 | -2.198 | -2.3214 | -2.4378 | -2.6224 | -2.8112
|  | ST MARYS | HE |  |  |  |  | -2.1673 | -2.2214 | -2.2786 | -2.3316 | -2.402 | -2.4765 | -2.5755 | -2.7255 | -2.9194 | -3.1469 | -3.9 | -4.0561 | -4.0929 | -1.1092 | -1.1398 | -1.1765 | -1.2082 | -1.2531 | -1.3041 | -1.3806 | -1.449 | -1.549 | -1.6592 | -2.0684 | -2.2367 | -2.4204 | -1.8602 | -1.9082 | -1.9684 | -2.0153 | -2.0908 | -2.1653 | -2.2684 | -2.3551 | -2.4837 | -2.6286
|  | ST MARYS | CF |  |  |  |  | -2.1582 | -2.201 | -2.249 | -2.3031 | -2.3459 | -2.4092 | -2.4724 | -2.549 | -2.6163 | -2.7306 | -3.4857 | -3.8469 | -4.0684 | -1.098 | -1.1235 | -1.15 | -1.1898 | -1.2092 | -1.252 | -1.2918 | -1.3582 | -1.3908 | -1.4592 | -1.8918 | -2.2704 | -2.7194 | -1.8439 | -1.8816 | -1.9245 | -1.9837 | -2.0184 | -2.0806 | -2.1408 | -2.2265 | -2.2653 | -2.352
| WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | NO | 0.579 | 9.8618 | 9.5648 | 9.1699 | 8.6689 | 8.0995 | 7.4791 | 6.8557 | 6.424 | 6.0026 | 5.6261 | 3.9495 | 2.521 | 2.3046 | 12.424 | 12.3006 | 12.1036 | 11.8169 | 11.4567 | 11.0801 | 10.6904 | 10.3689 | 10.0526 | 9.7628 | 8.2842 | 6.8475 | 2.8924 | 11.4087 | 11.1373 | 10.7679 | 10.3189 | 9.8026 | 9.2557 | 8.7046 | 8.2975 | 7.9006 | 7.5485
|  | ST NICHOLAS | EE |  |  |  |  | 9.8618 | 9.6842 | 9.2179 | 8.6985 | 8.0995 | 7.4791 | 6.8557 | 6.424 | 6.0026 | 5.6261 | 3.9495 | 2.7546 | 2.3577 | 12.424 | 12.3169 | 12.1036 | 11.8169 | 11.4567 | 11.0801 | 10.6904 | 10.3689 | 10.0526 | 9.7628 | 8.2842 | 6.8475 | 4.8587 | 11.4087 | 11.1801 | 10.7679 | 10.3189 | 9.8026 | 9.2557 | 8.7046 | 8.2975 | 7.9006 | 7.5485
|  | ST NICHOLAS | HT |  |  |  |  | 9.8924 | 9.5648 | 9.1699 | 8.6689 | 8.1567 | 7.5781 | 7.2404 | 6.8659 | 6.4904 | 6.1077 | 4.0495 | 2.521 | 2.3046 | 12.4557 | 12.3006 | 12.1271 | 11.9067 | 11.6679 | 11.3873 | 11.1914 | 10.9628 | 10.7383 | 10.5057 | 9.3128 | 8.5036 | 8.3934 | 11.4689 | 11.1373 | 10.771 | 10.3475 | 9.9067 | 9.4057 | 9.0904 | 8.7444 | 8.3965 | 8.0363
|  | ST NICHOLAS | HE |  |  |  |  | 9.8852 | 9.7699 | 9.6036 | 9.4057 | 9.1373 | 8.8832 | 8.5791 | 8.2546 | 7.9393 | 7.6169 | 5.9444 | 4.7465 | 4.3138 | 12.4414 | 12.3679 | 12.2669 | 12.1638 | 12.0036 | 11.8434 | 11.6291 | 11.3904 | 11.1506 | 10.8985 | 9.4067 | 7.9067 | 5.9618 | 11.4648 | 11.3261 | 11.1363 | 10.9332 | 10.6944 | 10.4659 | 10.1914 | 9.8893 | 9.6006 | 9.3046
|  | ST NICHOLAS | CF |  |  |  |  | 9.921 | 9.8414 | 9.7771 | 9.6567 | 9.5199 | 9.3128 | 9.173 | 9.0046 | 8.8628 | 8.7046 | 7.7271 | 6.6332 | 5.5179 | 12.4577 | 12.3955 | 12.3393 | 12.2526 | 12.1383 | 11.9771 | 11.8271 | 11.6332 | 11.4434 | 11.2383 | 9.8016 | 7.2271 | 2.8924 | 11.5128 | 11.4179 | 11.3342 | 11.1975 | 11.0352 | 10.8506 | 10.725 | 10.5699 | 10.4404 | 10.2944
| ARDMORE / HARRIS GRID | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | 0.227 | 0.18961 | 0.16818 | 0.14471 | 0.10696 | 0.077363 | 0.032465 | 0.00083265 | -0.059371 | -0.10529 | -0.15121 | -0.25427 | -0.2808 | -0.28998 | 0.39981 | 0.38349 | 0.36614 | 0.33757 | 0.3192 | 0.28553 | 0.26818 | 0.22736 | 0.19981 | 0.16716 | 0.10185 | 0.086547 | 0.034506 | 0.24879 | 0.22226 | 0.19675 | 0.15798 | 0.1294 | 0.087567 | 0.058996 | 0.00083265 | -0.045086 | -0.089984
|  | STOCKINISH | EE |  |  |  |  | 0.18961 | 0.16818 | 0.14471 | 0.10696 | 0.077363 | 0.032465 | 0.00083265 | -0.059371 | -0.10529 | -0.15121 | -0.25427 | -0.26856 | -0.27774 | 0.39981 | 0.38349 | 0.36614 | 0.33757 | 0.3192 | 0.28553 | 0.26818 | 0.22736 | 0.19981 | 0.16716 | 0.10185 | 0.086547 | 0.054914 | 0.24879 | 0.22226 | 0.19675 | 0.15798 | 0.1294 | 0.087567 | 0.058996 | 0.00083265 | -0.045086 | -0.089984
|  | STOCKINISH | HT |  |  |  |  | 0.21002 | 0.19267 | 0.17736 | 0.14165 | 0.12328 | 0.087567 | 0.056955 | 0.012057 | -0.0308 | -0.051208 | -0.21651 | -0.2808 | -0.28998 | 0.41818 | 0.40287 | 0.38859 | 0.36512 | 0.35696 | 0.33144 | 0.3141 | 0.28451 | 0.25696 | 0.24573 | 0.13451 | 0.096751 | 0.091649 | 0.27226 | 0.25083 | 0.22838 | 0.19573 | 0.17838 | 0.14369 | 0.11512 | 0.072261 | 0.029404 | 0.013078
|  | STOCKINISH | HE |  |  |  |  | 0.21002 | 0.19471 | 0.1794 | 0.15798 | 0.14471 | 0.11512 | 0.091649 | 0.050833 | 0.011037 | -0.003249 | -0.19304 | -0.23896 | -0.24713 | 0.41716 | 0.40389 | 0.39267 | 0.37328 | 0.36308 | 0.34471 | 0.32736 | 0.30083 | 0.27226 | 0.26614 | 0.14471 | 0.11002 | 0.082465 | 0.27226 | 0.25491 | 0.23655 | 0.21002 | 0.19777 | 0.16818 | 0.14471 | 0.10593 | 0.067159 | 0.056955
|  | STOCKINISH | CF |  |  |  |  | 0.209 | 0.20185 | 0.18655 | 0.17532 | 0.15593 | 0.14471 | 0.12022 | 0.10083 | 0.075322 | 0.047771 | -0.072637 | -0.18386 | -0.23794 | 0.41614 | 0.409 | 0.39471 | 0.38553 | 0.37022 | 0.36206 | 0.34573 | 0.33451 | 0.31512 | 0.29471 | 0.20798 | 0.11308 | 0.034506 | 0.27124 | 0.26308 | 0.24267 | 0.22736 | 0.20287 | 0.19471 | 0.1692 | 0.15083 | 0.12532 | 0.098792
| PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | 0 | 0.33905 | 0.32986 | 0.32986 | 0.3217 | 0.3217 | 0.31354 | 0.17884 | 0.0217 | -0.070137 | -0.12014 | -0.1334 | -0.13646 | -0.16481 | 0.32498 | 0.3158 | 0.3158 | 0.30866 | 0.30866 | 0.30049 | 0.15049 | -0.016854 | -0.11481 | -0.16787 | -0.18216 | -0.16901 | -0.17003 | 0.33406 | 0.32589 | 0.32589 | 0.31671 | 0.31671 | 0.30752 | 0.17385 | 0.018749 | -0.072067 | -0.12309
|  | STONEFIELD | EE |  |  |  |  | 0.33905 | 0.32986 | 0.32986 | 0.3217 | 0.3217 | 0.31354 | 0.31354 | 0.23292 | 0.12578 | 0.038027 | -0.1334 | -0.1334 | -0.16175 | 0.32498 | 0.3158 | 0.3158 | 0.30866 | 0.30866 | 0.30049 | 0.30049 | 0.21274 | 0.095391 | 0.00049286 | -0.18216 | -0.16799 | -0.16799 | 0.33406 | 0.32589 | 0.32589 | 0.31671 | 0.31671 | 0.30752 | 0.30855 | 0.22997 | 0.12181 | 0.036096
|  | STONEFIELD | HT |  |  |  |  | 0.34007 | 0.33803 | 0.33088 | 0.32986 | 0.32884 | 0.32782 | 0.17884 | 0.0217 | -0.070137 | -0.12014 | -0.13238 | -0.1334 | -0.16277 | 0.32498 | 0.32396 | 0.31682 | 0.3158 | 0.3158 | 0.3158 | 0.15049 | -0.016854 | -0.11481 | -0.16787 | -0.18216 | -0.16799 | -0.16901 | 0.33508 | 0.33304 | 0.32589 | 0.32589 | 0.32385 | 0.32283 | 0.17385 | 0.018749 | -0.072067 | -0.12309
|  | STONEFIELD | HE |  |  |  |  | 0.34007 | 0.33803 | 0.33088 | 0.32986 | 0.32884 | 0.32884 | 0.32068 | 0.22578 | 0.11048 | 0.02272 | -0.1334 | -0.13646 | -0.16481 | 0.32498 | 0.32396 | 0.31682 | 0.3158 | 0.3158 | 0.3158 | 0.30764 | 0.20559 | 0.080085 | -0.014813 | -0.18216 | -0.16901 | -0.16901 | 0.33508 | 0.33304 | 0.32589 | 0.32589 | 0.32385 | 0.32385 | 0.31569 | 0.22385 | 0.10548 | 0.01977
|  | STONEFIELD | CF |  |  |  |  | 0.34007 | 0.34007 | 0.33088 | 0.33088 | 0.32986 | 0.32986 | 0.32884 | 0.3217 | 0.29211 | 0.24211 | 0.024761 | -0.12932 | -0.15971 | 0.32498 | 0.32498 | 0.31682 | 0.31682 | 0.3158 | 0.3158 | 0.3158 | 0.30866 | 0.276 | 0.22498 | -0.014813 | -0.16696 | -0.17003 | 0.33508 | 0.33508 | 0.32589 | 0.32589 | 0.32589 | 0.32589 | 0.32385 | 0.31671 | 0.28712 | 0.23916
| FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | NO | 6.046 | 4.006 | 3.1448 | 2.003 | 0.6795 | -0.63887 | -1.9338 | -2.8695 | -3.7889 | -4.297 | -5.1276 | -8.946 | -12.1378 | -13.6072 | 6.6785 | 6.1091 | 5.2336 | 4.0744 | 2.9611 | 1.8428 | 1.3162 | 0.8295 | 0.56726 | 0.14481 | -2.2552 | -4.8134 | -7.2623 | 5.3285 | 4.5571 | 3.4703 | 2.2203 | 0.97338 | -0.30315 | -1.147 | -1.9929 | -2.4654 | -3.2287
|  | STONEHAVEN | EE |  |  |  |  | 4.0111 | 3.2081 | 2.2866 | 1.1673 | -0.18376 | -1.3929 | -2.2032 | -3.1746 | -4.1664 | -5.0511 | -8.5409 | -11.545 | -12.4317 | 6.6785 | 6.1091 | 5.455 | 4.6683 | 3.5805 | 2.5938 | 1.9815 | 1.4193 | 0.79991 | 0.28154 | -1.7634 | -4.2542 | -5.7368 | 5.3285 | 4.5571 | 3.6611 | 2.654 | 1.4122 | 0.24889 | -0.45009 | -1.344 | -2.2889 | -3.1093
|  | STONEHAVEN | HT |  |  |  |  | 4.006 | 3.1448 | 2.003 | 0.6795 | -0.63887 | -1.9338 | -2.8695 | -3.7889 | -4.297 | -5.1276 | -8.946 | -12.1378 | -13.6072 | 6.7458 | 6.1662 | 5.2336 | 4.0744 | 2.9611 | 1.8428 | 1.3162 | 0.8295 | 0.56726 | 0.14481 | -1.8317 | -4.1776 | -5.7083 | 5.3826 | 4.5703 | 3.4703 | 2.2203 | 0.97338 | -0.30315 | -1.147 | -1.9929 | -2.4654 | -3.2287
|  | STONEHAVEN | HE |  |  |  |  | 4.0907 | 3.4458 | 2.6295 | 1.6611 | 0.64073 | -0.54907 | -1.4613 | -2.2746 | -2.6817 | -3.4685 | -7.3776 | -10.5144 | -12.4695 | 6.8203 | 6.3142 | 5.6224 | 4.7081 | 3.7662 | 2.6775 | 1.9968 | 1.4213 | 1.0366 | 0.43256 | -2.2552 | -4.8134 | -7.2623 | 5.4734 | 4.8438 | 4.0377 | 3.0795 | 2.1336 | 0.95603 | 0.09991 | -0.68274 | -1.0664 | -1.8348
|  | STONEHAVEN | CF |  |  |  |  | 4.2866 | 3.9448 | 3.4815 | 3.0438 | 2.404 | 1.7346 | 1.202 | 0.6795 | 0.23767 | 0.078482 | -2.4715 | -5.2725 | -7.3307 | 6.9499 | 6.6468 | 6.2479 | 5.9071 | 5.3917 | 4.8326 | 4.3673 | 3.9091 | 3.5091 | 3.2724 | 1.1795 | -1.3766 | -3.9205 | 5.653 | 5.2826 | 4.7958 | 4.3734 | 3.7632 | 3.1295 | 2.6193 | 2.1122 | 1.6754 | 1.5428
| STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 6773 4109 | YES | YES | 0 | -2.449 | -2.45 | -2.45 | -2.451 | -2.451 | -2.451 | -2.451 | -2.452 | -2.452 | -2.4531 | -2.4551 | -2.4551 | -2.4561 | -2.3878 | -2.3888 | -2.3888 | -2.3898 | -2.3898 | -2.3898 | -2.3908 | -2.3918 | -2.3918 | -2.3929 | -2.3949 | -2.3949 | -2.3959 | -2.3214 | -2.3224 | -2.3224 | -2.3235 | -2.3235 | -2.3235 | -2.3255 | -2.3265 | -2.3265 | -2.3276
|  | STONEYHILL | EE |  |  |  |  | -2.449 | -2.45 | -2.45 | -2.451 | -2.451 | -2.451 | -2.451 | -2.452 | -2.452 | -2.4531 | -2.4541 | -2.4541 | -2.4541 | -2.3878 | -2.3888 | -2.3888 | -2.3898 | -2.3898 | -2.3898 | -2.3908 | -2.3918 | -2.3918 | -2.3929 | -2.3939 | -2.3939 | -2.3939 | -2.3214 | -2.3224 | -2.3224 | -2.3235 | -2.3235 | -2.3235 | -2.3255 | -2.3265 | -2.3265 | -2.3276
|  | STONEYHILL | HT |  |  |  |  | -2.449 | -2.45 | -2.45 | -2.45 | -2.45 | -2.451 | -2.451 | -2.451 | -2.451 | -2.452 | -2.4541 | -2.4551 | -2.4551 | -2.3878 | -2.3888 | -2.3888 | -2.3888 | -2.3888 | -2.3898 | -2.3898 | -2.3908 | -2.3908 | -2.3918 | -2.3939 | -2.3949 | -2.3949 | -2.3214 | -2.3224 | -2.3224 | -2.3224 | -2.3224 | -2.3235 | -2.3235 | -2.3255 | -2.3255 | -2.3265
|  | STONEYHILL | HE |  |  |  |  | -2.449 | -2.45 | -2.45 | -2.45 | -2.451 | -2.451 | -2.451 | -2.451 | -2.452 | -2.452 | -2.4551 | -2.4551 | -2.4561 | -2.3878 | -2.3888 | -2.3888 | -2.3888 | -2.3898 | -2.3898 | -2.3898 | -2.3908 | -2.3918 | -2.3918 | -2.3949 | -2.3949 | -2.3959 | -2.3214 | -2.3224 | -2.3224 | -2.3224 | -2.3235 | -2.3235 | -2.3235 | -2.3255 | -2.3265 | -2.3265
|  | STONEYHILL | CF |  |  |  |  | -2.449 | -2.449 | -2.45 | -2.45 | -2.45 | -2.45 | -2.451 | -2.451 | -2.451 | -2.451 | -2.4531 | -2.4551 | -2.4551 | -2.3878 | -2.3878 | -2.3888 | -2.3888 | -2.3888 | -2.3888 | -2.3898 | -2.3898 | -2.3898 | -2.3908 | -2.3929 | -2.3949 | -2.3949 | -2.3214 | -2.3214 | -2.3224 | -2.3224 | -2.3224 | -2.3224 | -2.3235 | -2.3235 | -2.3235 | -2.3255
| PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | NO | 0.458 | 14.7643 | 14.198 | 13.5204 | 12.7582 | 11.9898 | 11.1837 | 10.4286 | 9.5561 | 8.9133 | 8.1051 | 5.0418 | 2.9327 | 1.5729 | 16.0657 | 15.732 | 15.3596 | 14.9494 | 14.5382 | 14.128 | 13.679 | 13.0984 | 12.6545 | 12.2586 | 10.3055 | 9.8014 | 9.2912 | 15.7586 | 15.3239 | 14.828 | 14.279 | 13.6576 | 12.9708 | 12.2739 | 11.4555 | 10.8331 | 10.2596
|  | STONEYWOOD T1&T2 | EE |  |  |  |  | 14.7643 | 14.198 | 13.5204 | 12.7582 | 11.9898 | 11.1837 | 10.4286 | 9.5561 | 8.9561 | 8.3847 | 5.4173 | 3.3184 | 1.6637 | 16.0657 | 15.732 | 15.3596 | 14.9494 | 14.5382 | 14.128 | 13.679 | 13.0984 | 12.6545 | 12.2586 | 10.7167 | 10.6402 | 10.4035 | 15.7586 | 15.3239 | 14.828 | 14.279 | 13.6576 | 12.9708 | 12.2739 | 11.4555 | 10.8331 | 10.2647
|  | STONEYWOOD T1&T2 | HT |  |  |  |  | 14.8296 | 14.2694 | 13.6286 | 12.8561 | 12.1112 | 11.3347 | 10.4847 | 9.5857 | 8.9133 | 8.1051 | 5.0418 | 2.9327 | 1.5729 | 16.1667 | 15.8667 | 15.5596 | 15.18 | 14.8259 | 14.4576 | 14.0024 | 13.5137 | 13.1269 | 12.6535 | 10.7933 | 10.3667 | 10.08 | 15.882 | 15.4892 | 15.0739 | 14.5229 | 13.8473 | 13.1545 | 12.3882 | 11.5739 | 10.9698 | 10.2596
|  | STONEYWOOD T1&T2 | HE |  |  |  |  | 14.8245 | 14.3276 | 13.7449 | 13.0561 | 12.3724 | 11.6449 | 11.0122 | 10.2224 | 9.6959 | 9.1418 | 6.101 | 3.9918 | 2.0208 | 16.1473 | 15.8412 | 15.528 | 15.1535 | 14.7851 | 14.4024 | 13.9953 | 13.4841 | 13.0494 | 12.5841 | 10.3055 | 9.8014 | 9.2912 | 15.8586 | 15.4647 | 15.0504 | 14.5524 | 14.0586 | 13.4351 | 12.8239 | 12.0586 | 11.4657 | 10.831
|  | STONEYWOOD T1&T2 | CF |  |  |  |  | 14.8949 | 14.5112 | 14.051 | 13.5306 | 13.0173 | 12.449 | 12.0378 | 11.5786 | 11.3184 | 11.0888 | 9.002 | 6.4245 | 3.0708 | 16.2035 | 15.9871 | 15.7494 | 15.4871 | 15.229 | 14.9514 | 14.6902 | 14.3657 | 14.1259 | 13.8882 | 12.179 | 11.0545 | 9.6718 | 15.932 | 15.6535 | 15.3382 | 14.9841 | 14.6371 | 14.1576 | 13.7943 | 13.378 | 13.131 | 12.8096
| DYCE | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | NO | YES | 0 | 19.4184 | 19.3735 | 19.3265 | 19.2724 | 19.2214 | 19.1592 | 19.0837 | 18.9959 | 18.9133 | 18.8449 | 18.5776 | 18.4061 | 17.4188 | 18.8627 | 18.8433 | 18.8178 | 18.7922 | 18.7637 | 18.7331 | 18.6902 | 18.6259 | 18.5678 | 18.5208 | 18.3402 | 18.8402 | 18.7851 | 19.432 | 19.4096 | 19.3769 | 19.3422 | 19.2953 | 19.2351 | 19.1616 | 19.0759 | 18.9963 | 18.931
|  | STONEYWOOD T3 | EE |  |  |  |  | 19.4184 | 19.3735 | 19.3265 | 19.2724 | 19.2214 | 19.1592 | 19.0837 | 18.9959 | 18.9133 | 18.8449 | 18.5776 | 18.4439 | 17.4963 | 18.8627 | 18.8433 | 18.8178 | 18.7922 | 18.7637 | 18.7331 | 18.6902 | 18.6259 | 18.5678 | 18.5208 | 18.3463 | 18.8984 | 18.8912 | 19.432 | 19.4096 | 19.3769 | 19.3422 | 19.2953 | 19.2351 | 19.1616 | 19.0759 | 18.9963 | 18.931
|  | STONEYWOOD T3 | HT |  |  |  |  | 19.4327 | 19.399 | 19.3592 | 19.3173 | 19.2735 | 19.2204 | 19.1571 | 19.0796 | 19.0082 | 18.9316 | 18.5959 | 18.4061 | 17.4188 | 18.8729 | 18.8586 | 18.8382 | 18.8178 | 18.7963 | 18.7698 | 18.7433 | 18.7035 | 18.6535 | 18.6014 | 18.3739 | 18.8759 | 18.8371 | 19.4402 | 19.4218 | 19.4014 | 19.3739 | 19.3443 | 19.2963 | 19.2382 | 19.1606 | 19.0922 | 19.0178
|  | STONEYWOOD T3 | HE |  |  |  |  | 19.4316 | 19.399 | 19.3653 | 19.3286 | 19.2867 | 19.2378 | 19.1776 | 19.1041 | 19.0337 | 18.9602 | 18.6122 | 18.4602 | 17.4453 | 18.8718 | 18.8555 | 18.8392 | 18.8208 | 18.7973 | 18.7718 | 18.7422 | 18.6953 | 18.6443 | 18.5902 | 18.3402 | 18.8402 | 18.7851 | 19.4402 | 19.4229 | 19.4065 | 19.382 | 19.3535 | 19.3116 | 19.2535 | 19.178 | 19.1116 | 19.0392
|  | STONEYWOOD T3 | CF |  |  |  |  | 19.4449 | 19.4265 | 19.4071 | 19.3867 | 19.3612 | 19.3327 | 19.3 | 19.2622 | 19.2224 | 19.1827 | 18.9296 | 18.6888 | 17.5902 | 18.879 | 18.8688 | 18.8586 | 18.8473 | 18.8351 | 18.8178 | 18.8014 | 18.782 | 18.7596 | 18.7382 | 18.5565 | 18.9851 | 18.8678 | 19.4463 | 19.4371 | 19.4249 | 19.4167 | 19.4024 | 19.3841 | 19.3596 | 19.3351 | 19.2953 | 19.2565
| CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 0.126 | 0.28776 | 0.26735 | 0.23469 | 0.21224 | 0.17449 | 0.13367 | 0.070408 | 0.018367 | -0.0061224 | -0.044898 | -0.15102 | -0.18061 | -0.1898 | 0.66224 | 0.65 | 0.62551 | 0.61224 | 0.58265 | 0.5602 | 0.52041 | 0.48265 | 0.47041 | 0.4449 | 0.37755 | 0.35204 | 0.2449 | 0.46633 | 0.45 | 0.41837 | 0.39796 | 0.36327 | 0.32551 | 0.26735 | 0.22041 | 0.19592 | 0.15918
|  | STRACHUR | EE |  |  |  |  | 0.28776 | 0.26735 | 0.23469 | 0.21224 | 0.17449 | 0.13367 | 0.070408 | 0.018367 | -0.0061224 | -0.044898 | -0.15102 | -0.16735 | -0.17755 | 0.66224 | 0.65 | 0.62551 | 0.61224 | 0.58265 | 0.5602 | 0.52041 | 0.48265 | 0.47041 | 0.4449 | 0.37755 | 0.35204 | 0.3 | 0.46633 | 0.45 | 0.41837 | 0.39796 | 0.36327 | 0.32551 | 0.26735 | 0.22041 | 0.19592 | 0.15918
|  | STRACHUR | HT |  |  |  |  | 0.30204 | 0.28265 | 0.25714 | 0.23163 | 0.19694 | 0.16735 | 0.12245 | 0.090816 | 0.046939 | -0.0061224 | -0.13469 | -0.18061 | -0.1898 | 0.67347 | 0.66327 | 0.64898 | 0.63163 | 0.60816 | 0.59388 | 0.56633 | 0.55 | 0.51939 | 0.48571 | 0.4 | 0.37449 | 0.36735 | 0.47755 | 0.46735 | 0.44184 | 0.41837 | 0.38878 | 0.35918 | 0.31939 | 0.29082 | 0.25 | 0.20102
|  | STRACHUR | HE |  |  |  |  | 0.30204 | 0.28673 | 0.26531 | 0.25 | 0.22245 | 0.18878 | 0.13673 | 0.11224 | 0.076531 | 0.039796 | -0.10306 | -0.13469 | -0.13878 | 0.67347 | 0.66429 | 0.65102 | 0.64082 | 0.61633 | 0.60204 | 0.57245 | 0.55408 | 0.53061 | 0.5051 | 0.40714 | 0.37653 | 0.33061 | 0.47755 | 0.46837 | 0.45102 | 0.43367 | 0.4102 | 0.37959 | 0.33469 | 0.31122 | 0.27857 | 0.24286
|  | STRACHUR | CF |  |  |  |  | 0.3051 | 0.29286 | 0.27959 | 0.2602 | 0.24796 | 0.22653 | 0.21122 | 0.18469 | 0.16224 | 0.14694 | 0.005102 | -0.088776 | -0.13469 | 0.67551 | 0.66735 | 0.65918 | 0.64286 | 0.63469 | 0.61837 | 0.61122 | 0.59184 | 0.57245 | 0.56327 | 0.46531 | 0.35714 | 0.2449 | 0.48163 | 0.47245 | 0.46327 | 0.4449 | 0.43265 | 0.41224 | 0.4 | 0.37449 | 0.35204 | 0.33878
| TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | NO | 0.169 | 0.069008 | 0.035335 | 0.0047224 | -0.041196 | -0.07691 | -0.12181 | -0.18201 | -0.21977 | -0.28099 | -0.32181 | -0.4412 | -0.47283 | -0.48711 | 0.43023 | 0.41084 | 0.39044 | 0.36493 | 0.3435 | 0.31289 | 0.27717 | 0.25574 | 0.21901 | 0.19146 | 0.11595 | 0.095539 | 0.02411 | 0.36493 | 0.33329 | 0.30472 | 0.26289 | 0.22819 | 0.18431 | 0.12615 | 0.091457 | 0.032273 | -0.0044612
|  | STRATHDON | EE |  |  |  |  | 0.069008 | 0.035335 | 0.0047224 | -0.041196 | -0.07691 | -0.12181 | -0.18201 | -0.21977 | -0.28099 | -0.32181 | -0.4412 | -0.45956 | -0.46671 | 0.43023 | 0.41084 | 0.39044 | 0.36493 | 0.3435 | 0.31289 | 0.27717 | 0.25574 | 0.21901 | 0.19146 | 0.11595 | 0.095539 | 0.061865 | 0.36493 | 0.33329 | 0.30472 | 0.26289 | 0.22819 | 0.18431 | 0.12615 | 0.091457 | 0.032273 | -0.0044612
|  | STRATHDON | HT |  |  |  |  | 0.083294 | 0.055743 | 0.025131 | -0.0044612 | -0.028951 | -0.065686 | -0.11058 | -0.1463 | -0.19426 | -0.24222 | -0.39528 | -0.47283 | -0.48711 | 0.43942 | 0.42411 | 0.40676 | 0.39146 | 0.37819 | 0.35574 | 0.32921 | 0.30778 | 0.28023 | 0.25166 | 0.15676 | 0.11901 | 0.10982 | 0.37819 | 0.3537 | 0.32615 | 0.29758 | 0.27513 | 0.23942 | 0.1986 | 0.16289 | 0.11901 | 0.07411
|  | STRATHDON | HE |  |  |  |  | 0.083294 | 0.062886 | 0.036355 | 0.015947 | -0.0034408 | -0.035073 | -0.071808 | -0.10344 | -0.14426 | -0.19018 | -0.38099 | -0.43711 | -0.45038 | 0.43942 | 0.42819 | 0.41289 | 0.39962 | 0.3884 | 0.36697 | 0.3435 | 0.32309 | 0.29758 | 0.26901 | 0.15268 | 0.10676 | 0.071049 | 0.37819 | 0.35982 | 0.33636 | 0.31391 | 0.29758 | 0.26901 | 0.23431 | 0.20166 | 0.16187 | 0.12003
|  | STRATHDON | CF |  |  |  |  | 0.088396 | 0.07309 | 0.0486 | 0.031253 | 0.003702 | -0.0054816 | -0.032012 | -0.064665 | -0.084053 | -0.11364 | -0.24324 | -0.36773 | -0.43405 | 0.4435 | 0.43431 | 0.42105 | 0.40982 | 0.39248 | 0.38636 | 0.37003 | 0.34758 | 0.33636 | 0.31595 | 0.22513 | 0.11697 | 0.02411 | 0.38329 | 0.37003 | 0.34656 | 0.33329 | 0.30574 | 0.29554 | 0.27003 | 0.2384 | 0.22003 | 0.19452
| STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | YES | 0.494 | 4.4073 | 3.9808 | 3.542 | 3.1043 | 2.6686 | 2.5818 | 2.4808 | 2.3594 | 2.2369 | 2.1053 | 1.7441 | 1.6104 | 1.54 | 6.7002 | 6.2645 | 5.8124 | 5.3553 | 4.9053 | 4.8216 | 4.7247 | 4.6216 | 4.5073 | 4.3869 | 4.0441 | 3.9227 | 3.592 | 4.0329 | 3.5818 | 3.1104 | 2.639 | 2.1747 | 2.0624 | 1.9186 | 1.7676 | 1.5992 | 1.4196
|  | STRICHEN | EE |  |  |  |  | 4.4073 | 3.9808 | 3.542 | 3.1043 | 2.6686 | 2.5818 | 2.4808 | 2.3594 | 2.2369 | 2.1053 | 1.7441 | 1.6686 | 1.6461 | 6.7002 | 6.2645 | 5.8124 | 5.3553 | 4.9053 | 4.8216 | 4.7247 | 4.6216 | 4.5073 | 4.3869 | 4.0441 | 3.9227 | 3.7818 | 4.0329 | 3.5818 | 3.1104 | 2.639 | 2.1747 | 2.0624 | 1.9186 | 1.7676 | 1.5992 | 1.4196
|  | STRICHEN | HT |  |  |  |  | 4.4318 | 4.0145 | 3.589 | 3.1696 | 2.738 | 2.6655 | 2.5747 | 2.4594 | 2.3176 | 2.1931 | 1.8186 | 1.6104 | 1.54 | 6.7206 | 6.2951 | 5.8512 | 5.4145 | 4.9696 | 4.9022 | 4.8227 | 4.7196 | 4.5961 | 4.4869 | 4.1655 | 4.0196 | 3.9808 | 4.0563 | 3.6124 | 3.1573 | 2.7084 | 2.2441 | 2.1451 | 2.0206 | 1.8645 | 1.6737 | 1.5084
|  | STRICHEN | HE |  |  |  |  | 4.4298 | 4.0206 | 3.6043 | 3.191 | 2.7686 | 2.7033 | 2.6318 | 2.5206 | 2.4033 | 2.2696 | 1.7818 | 1.6461 | 1.5808 | 6.7196 | 6.292 | 5.8553 | 5.4206 | 4.9798 | 4.9349 | 4.8869 | 4.79 | 4.692 | 4.5767 | 4.1114 | 3.9247 | 3.7563 | 4.0543 | 3.6318 | 3.1961 | 2.7686 | 2.3278 | 2.2482 | 2.1573 | 2.0206 | 1.8757 | 1.7073
|  | STRICHEN | CF |  |  |  |  | 4.4441 | 4.0522 | 3.6533 | 3.2553 | 2.8573 | 2.8135 | 2.7676 | 2.7114 | 2.6584 | 2.59 | 2.1624 | 1.8655 | 1.6676 | 6.7278 | 6.3104 | 5.8829 | 5.4553 | 5.0308 | 4.9992 | 4.9624 | 4.9073 | 4.8553 | 4.788 | 4.3951 | 4.0114 | 3.592 | 4.0686 | 3.6543 | 3.2339 | 2.8104 | 2.392 | 2.3339 | 2.2686 | 2.1941 | 2.1308 | 2.042
| THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | NO | 0.285 | 2.3714 | 1.9908 | 1.3847 | 0.71939 | 0.41327 | -0.47653 | -0.82959 | -1.2214 | -1.6459 | -2.3122 | -4.9735 | -7.4143 | -9.8184 | 4.4878 | 4.1459 | 3.5357 | 2.8459 | 2.5929 | 1.5918 | 1.2653 | 0.82551 | 0.41837 | -0.26735 | -3.0031 | -5.9714 | -8.9214 | 3.3337 | 2.9949 | 2.3633 | 1.65 | 1.3704 | 0.34286 | 0.010204 | -0.45102 | -0.89796 | -1.6245
|  | STROMNESS | EE |  |  |  |  | 2.3796 | 2.001 | 1.601 | 1.2408 | 0.74694 | 0.12857 | -0.37551 | -0.74592 | -1.2949 | -1.7235 | -2.7459 | -5.0112 | -5.9602 | 4.5051 | 4.1714 | 3.8265 | 3.5163 | 3.0398 | 2.3949 | 1.9551 | 1.7061 | 1.2429 | 0.91224 | -0.23776 | -3.0071 | -4.4031 | 3.3459 | 3.0224 | 2.6418 | 2.3051 | 1.802 | 1.1204 | 0.64898 | 0.29796 | -0.29184 | -0.72755
|  | STROMNESS | HT |  |  |  |  | 2.3714 | 1.9908 | 1.3847 | 0.71939 | 0.41327 | -0.47653 | -0.82959 | -1.1673 | -1.4235 | -1.7694 | -3.4163 | -5.9255 | -8.1673 | 4.4878 | 4.1459 | 3.5357 | 2.8459 | 2.5929 | 1.5918 | 1.2939 | 1.0163 | 0.84082 | 0.57347 | -0.90204 | -4.0888 | -6.8765 | 3.3337 | 2.9949 | 2.3633 | 1.65 | 1.3704 | 0.34286 | 0.010204 | -0.31735 | -0.5449 | -0.8602
|  | STROMNESS | HE |  |  |  |  | 2.4296 | 2.0735 | 1.5714 | 0.99184 | 0.60102 | -0.28265 | -0.7602 | -1.2214 | -1.6459 | -2.3122 | -4.9735 | -7.4143 | -9.8184 | 4.5469 | 4.2265 | 3.7143 | 3.1041 | 2.7316 | 1.7327 | 1.2653 | 0.82551 | 0.41837 | -0.26735 | -3.0031 | -5.9714 | -8.9214 | 3.3929 | 3.0806 | 2.552 | 1.9286 | 1.5327 | 0.51429 | 0.021429 | -0.45102 | -0.89796 | -1.6245
|  | STROMNESS | CF |  |  |  |  | 2.6102 | 2.3541 | 2.098 | 1.9102 | 1.6 | 1.199 | 0.91735 | 0.63878 | 0.37143 | 0.055102 | -1.3612 | -2.3847 | -3.1112 | 4.7235 | 4.498 | 4.2663 | 4.1092 | 3.8102 | 3.3908 | 3.102 | 2.8337 | 2.5857 | 2.2878 | 1.0173 | 0.005102 | -1.2398 | 3.5622 | 3.3378 | 3.1143 | 2.9602 | 2.65 | 2.2051 | 1.9143 | 1.6245 | 1.3439 | 1.0071
| THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | NO | 0.036 | 0.67449 | 0.66224 | 0.65 | 0.62755 | 0.61837 | 0.59694 | 0.57959 | 0.5449 | 0.51122 | 0.48367 | 0.4449 | 0.43571 | 0.43163 | 0.81327 | 0.80408 | 0.79184 | 0.77245 | 0.76633 | 0.74592 | 0.73163 | 0.70612 | 0.68367 | 0.66327 | 0.64592 | 0.63673 | 0.59082 | 0.75816 | 0.74388 | 0.72857 | 0.70612 | 0.69592 | 0.67347 | 0.65408 | 0.62449 | 0.5949 | 0.57041
|  | STRONSAY | EE |  |  |  |  | 0.67449 | 0.66224 | 0.65 | 0.62755 | 0.61837 | 0.59694 | 0.57959 | 0.5449 | 0.51122 | 0.48367 | 0.45102 | 0.44082 | 0.43776 | 0.81327 | 0.80408 | 0.79184 | 0.77245 | 0.76633 | 0.74592 | 0.73163 | 0.70612 | 0.68367 | 0.66327 | 0.65102 | 0.63673 | 0.61531 | 0.75816 | 0.74388 | 0.72857 | 0.70612 | 0.69592 | 0.67347 | 0.65408 | 0.62449 | 0.5949 | 0.57041
|  | STRONSAY | HT |  |  |  |  | 0.68571 | 0.67551 | 0.66531 | 0.65306 | 0.64388 | 0.62449 | 0.60204 | 0.59184 | 0.56735 | 0.55306 | 0.4449 | 0.43571 | 0.43163 | 0.82347 | 0.81735 | 0.80714 | 0.79694 | 0.7898 | 0.77551 | 0.75714 | 0.74898 | 0.73265 | 0.72551 | 0.64592 | 0.65102 | 0.64898 | 0.76735 | 0.75714 | 0.74286 | 0.72755 | 0.71735 | 0.69796 | 0.67653 | 0.66837 | 0.64694 | 0.63367
|  | STRONSAY | HE |  |  |  |  | 0.68571 | 0.67653 | 0.66837 | 0.65612 | 0.64796 | 0.63163 | 0.61327 | 0.60408 | 0.58571 | 0.57551 | 0.45306 | 0.45408 | 0.45102 | 0.82347 | 0.81735 | 0.8102 | 0.79796 | 0.79082 | 0.77857 | 0.76122 | 0.7551 | 0.73673 | 0.72959 | 0.64898 | 0.64592 | 0.62551 | 0.76735 | 0.75918 | 0.74796 | 0.73571 | 0.72551 | 0.71122 | 0.68776 | 0.68061 | 0.65918 | 0.65102
|  | STRONSAY | CF |  |  |  |  | 0.68061 | 0.67959 | 0.66939 | 0.66531 | 0.6551 | 0.65102 | 0.63673 | 0.62245 | 0.62041 | 0.60612 | 0.53061 | 0.48367 | 0.4551 | 0.82143 | 0.81735 | 0.81122 | 0.8051 | 0.79796 | 0.79082 | 0.78061 | 0.76531 | 0.76633 | 0.75408 | 0.69592 | 0.64592 | 0.59082 | 0.76224 | 0.76122 | 0.75306 | 0.7449 | 0.73469 | 0.72755 | 0.71224 | 0.69694 | 0.6949 | 0.68367
| FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | NO | 0.058 | 0.15 | 0.13571 | 0.11429 | 0.083673 | 0.066327 | 0.035714 | 0.011224 | -0.028571 | -0.066327 | -0.080612 | -0.14898 | -0.17143 | -0.17449 | 0.51633 | 0.49898 | 0.48469 | 0.46327 | 0.45408 | 0.43265 | 0.41429 | 0.38878 | 0.36122 | 0.3551 | 0.3051 | 0.28367 | 0.20408 | 0.36837 | 0.34796 | 0.32857 | 0.29796 | 0.28367 | 0.25408 | 0.23163 | 0.19286 | 0.15612 | 0.14694
|  | STRONTIAN | EE |  |  |  |  | 0.15 | 0.13571 | 0.11429 | 0.083673 | 0.066327 | 0.035714 | 0.011224 | -0.028571 | -0.066327 | -0.080612 | -0.14898 | -0.15918 | -0.16633 | 0.51633 | 0.49898 | 0.48469 | 0.46327 | 0.45408 | 0.43265 | 0.41429 | 0.38878 | 0.36122 | 0.3551 | 0.3051 | 0.28367 | 0.2449 | 0.36837 | 0.34796 | 0.32857 | 0.29796 | 0.28367 | 0.25408 | 0.23163 | 0.19286 | 0.15612 | 0.14694
|  | STRONTIAN | HT |  |  |  |  | 0.15612 | 0.14286 | 0.12857 | 0.11224 | 0.094898 | 0.068367 | 0.053061 | 0.02449 | -0.0061224 | -0.02449 | -0.12653 | -0.17143 | -0.17449 | 0.52347 | 0.51531 | 0.50204 | 0.4898 | 0.48061 | 0.46327 | 0.4551 | 0.43265 | 0.41224 | 0.40102 | 0.33367 | 0.3051 | 0.30306 | 0.37857 | 0.36327 | 0.34592 | 0.32857 | 0.31327 | 0.28878 | 0.27449 | 0.2449 | 0.21633 | 0.2
|  | STRONTIAN | HE |  |  |  |  | 0.15612 | 0.14388 | 0.13265 | 0.12143 | 0.1102 | 0.088776 | 0.07551 | 0.046939 | 0.022449 | 0.0071429 | -0.10816 | -0.13878 | -0.14184 | 0.52347 | 0.51122 | 0.50204 | 0.49082 | 0.48367 | 0.46939 | 0.45918 | 0.4398 | 0.42347 | 0.40918 | 0.33367 | 0.3 | 0.26531 | 0.37857 | 0.36531 | 0.35204 | 0.33571 | 0.32347 | 0.30408 | 0.29184 | 0.26735 | 0.24082 | 0.22653
|  | STRONTIAN | CF |  |  |  |  | 0.15714 | 0.14898 | 0.14082 | 0.12959 | 0.12347 | 0.10714 | 0.087755 | 0.079592 | 0.061224 | 0.042857 | -0.044898 | -0.1051 | -0.14286 | 0.52653 | 0.51735 | 0.50918 | 0.49796 | 0.49184 | 0.47959 | 0.46735 | 0.45816 | 0.4449 | 0.42959 | 0.35612 | 0.28469 | 0.20408 | 0.38163 | 0.37143 | 0.35918 | 0.34592 | 0.33878 | 0.32143 | 0.30306 | 0.29592 | 0.27857 | 0.2602
| SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | 0.109 | -0.62857 | -0.66939 | -0.70204 | -0.74082 | -0.79184 | -0.82245 | -0.88673 | -0.95204 | -1.0204 | -1.0786 | -1.1724 | -1.2214 | -1.2286 | 0.04898 | 0.028571 | 0.012245 | -0.011224 | -0.034694 | -0.053061 | -0.085714 | -0.11939 | -0.15612 | -0.19184 | -0.26633 | -0.30918 | -0.44184 | -0.23776 | -0.27347 | -0.30306 | -0.33571 | -0.37653 | -0.40408 | -0.45612 | -0.51224 | -0.56837 | -0.62347
|  | SUMBURGH | EE |  |  |  |  | -0.62857 | -0.66939 | -0.70204 | -0.74082 | -0.79184 | -0.82245 | -0.88673 | -0.95204 | -1.0204 | -1.0786 | -1.1724 | -1.1918 | -1.2092 | 0.04898 | 0.028571 | 0.012245 | -0.011224 | -0.034694 | -0.053061 | -0.085714 | -0.11939 | -0.15612 | -0.19184 | -0.26633 | -0.30918 | -0.38163 | -0.23776 | -0.27347 | -0.30306 | -0.33571 | -0.37653 | -0.40408 | -0.45612 | -0.51224 | -0.56837 | -0.62347
|  | SUMBURGH | HT |  |  |  |  | -0.61224 | -0.6398 | -0.66633 | -0.69184 | -0.73265 | -0.76429 | -0.81224 | -0.86735 | -0.8949 | -0.94694 | -1.1704 | -1.2214 | -1.2286 | 0.060204 | 0.046939 | 0.033673 | 0.017347 | -0.0020408 | -0.019388 | -0.043878 | -0.071429 | -0.084694 | -0.1102 | -0.24388 | -0.26939 | -0.27755 | -0.22755 | -0.25204 | -0.27653 | -0.3 | -0.33265 | -0.36122 | -0.40102 | -0.44694 | -0.47245 | -0.51837
|  | SUMBURGH | HE |  |  |  |  | -0.61224 | -0.63469 | -0.65816 | -0.67653 | -0.70918 | -0.73571 | -0.77551 | -0.82551 | -0.84694 | -0.8898 | -1.1163 | -1.1327 | -1.1388 | 0.057143 | 0.045918 | 0.033673 | 0.021429 | 0.005102 | -0.0071429 | -0.030612 | -0.056122 | -0.068367 | -0.092857 | -0.22857 | -0.26531 | -0.32857 | -0.22755 | -0.24694 | -0.26633 | -0.28469 | -0.31122 | -0.33163 | -0.36429 | -0.40408 | -0.42551 | -0.46122
|  | SUMBURGH | CF |  |  |  |  | -0.60612 | -0.62551 | -0.6449 | -0.67143 | -0.68776 | -0.71429 | -0.73469 | -0.76939 | -0.80102 | -0.83469 | -0.97449 | -1.0806 | -1.1327 | 0.061224 | 0.05102 | 0.040816 | 0.02449 | 0.015306 | -0.0010204 | -0.013265 | -0.032653 | -0.052041 | -0.071429 | -0.17143 | -0.28878 | -0.44184 | -0.22347 | -0.23776 | -0.25612 | -0.27755 | -0.29286 | -0.31531 | -0.33265 | -0.35816 | -0.38571 | -0.41429
| ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | NO | 4.146 | 6.3242 | 6.1814 | 6.012 | 14.5869 | 14.3603 | 14.094 | 13.5991 | 13.0705 | 12.6216 | 12.0746 | 10.8389 | 10.4828 | 0.94462 | 7.9793 | 7.8844 | 16.044 | 15.9328 | 15.7665 | 15.5828 | 15.4175 | 15.0573 | 14.7124 | 14.395 | 13.5899 | 5.2533 | 4.2594 | 7.3655 | 15.7216 | 15.5297 | 15.3593 | 15.0991 | 14.8256 | 14.5154 | 14.0114 | 13.4797 | 12.9797
|  | TAIN | EE |  |  |  |  | 6.3242 | 6.1814 | 6.012 | 14.5869 | 14.3603 | 14.094 | 13.8358 | 13.2256 | 12.6358 | 12.0746 | 10.8389 | 10.694 | 1.1467 | 7.9793 | 7.8844 | 16.044 | 15.9328 | 15.7665 | 15.5828 | 15.4175 | 15.0573 | 14.7124 | 14.395 | 13.5899 | 5.4247 | 5.0349 | 7.3655 | 15.7216 | 15.5297 | 15.3593 | 15.0991 | 14.8256 | 14.5675 | 14.0114 | 13.4797 | 12.9797
|  | TAIN | HT |  |  |  |  | 6.3844 | 6.2609 | 6.1334 | 14.7226 | 14.5338 | 14.094 | 13.5991 | 13.0705 | 12.6216 | 12.1828 | 11.1216 | 10.594 | 1.0467 | 8.0426 | 7.965 | 16.1665 | 16.0777 | 15.9542 | 15.7063 | 15.446 | 15.1583 | 14.9236 | 14.6767 | 13.9409 | 5.6992 | 5.6604 | 7.4676 | 15.843 | 15.7154 | 15.5624 | 15.3583 | 14.943 | 14.5154 | 14.0512 | 13.6634 | 13.2654
|  | TAIN | HE |  |  |  |  | 6.3752 | 6.2722 | 6.166 | 14.7777 | 14.6052 | 14.4348 | 14.243 | 13.8685 | 13.4746 | 13.0981 | 11.1644 | 10.4828 | 0.94462 | 8.0324 | 7.9599 | 16.1634 | 16.0777 | 15.9481 | 15.8307 | 15.694 | 15.4501 | 15.2032 | 14.9828 | 13.7399 | 5.2533 | 4.891 | 7.4604 | 15.843 | 15.7154 | 15.5705 | 15.3848 | 15.1899 | 14.9542 | 14.5981 | 14.2481 | 13.8899
|  | TAIN | CF |  |  |  |  | 6.3865 | 6.3069 | 6.214 | 14.8522 | 14.7114 | 14.5634 | 14.445 | 14.3236 | 14.0675 | 13.7767 | 12.3338 | 11.193 | 1.0048 | 8.0416 | 7.9916 | 16.2032 | 16.143 | 16.043 | 15.9389 | 15.8369 | 15.7399 | 15.5593 | 15.3695 | 14.3573 | 5.3696 | 4.2594 | 7.4686 | 15.9001 | 15.795 | 15.7052 | 15.5614 | 15.4063 | 15.2695 | 15.1501 | 14.896 | 14.6318
| ARDMORE / HARRIS GRID | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | 0.216 | 0.073469 | 0.017347 | -0.088776 | -0.17041 | -0.23163 | -0.33571 | -0.43878 | -0.52143 | -0.63061 | -0.72551 | -0.95102 | -1.0204 | -1.0388 | 0.35918 | 0.32857 | 0.2551 | 0.20102 | 0.16735 | 0.088776 | 0.017347 | -0.037755 | -0.1102 | -0.17347 | -0.34796 | -0.42653 | -0.69796 | 0.23571 | 0.18061 | 0.077551 | -0.0020408 | -0.057143 | -0.15714 | -0.25816 | -0.33571 | -0.44184 | -0.53163
|  | TARBERT | EE |  |  |  |  | 0.073469 | 0.017347 | -0.088776 | -0.17041 | -0.23163 | -0.33571 | -0.43878 | -0.52143 | -0.63061 | -0.72551 | -0.95102 | -0.98367 | -1.0082 | 0.35918 | 0.32857 | 0.2551 | 0.20102 | 0.16735 | 0.088776 | 0.017347 | -0.037755 | -0.1102 | -0.17347 | -0.34796 | -0.42653 | -0.55714 | 0.23571 | 0.18367 | 0.077551 | -0.0020408 | -0.057143 | -0.15714 | -0.25816 | -0.33571 | -0.44184 | -0.53163
|  | TARBERT | HT |  |  |  |  | 0.10918 | 0.017347 | -0.031633 | -0.094898 | -0.17245 | -0.24388 | -0.3 | -0.38163 | -0.46327 | -0.55306 | -0.87347 | -1.0204 | -1.0388 | 0.39388 | 0.33469 | 0.3102 | 0.27041 | 0.21429 | 0.16939 | 0.13776 | 0.083673 | 0.029592 | -0.027551 | -0.24082 | -0.33469 | -0.34592 | 0.27245 | 0.18061 | 0.13469 | 0.073469 | 0.0020408 | -0.065306 | -0.11633 | -0.19388 | -0.27347 | -0.35714
|  | TARBERT | HE |  |  |  |  | 0.10918 | 0.069388 | -0.010204 | -0.059184 | -0.10306 | -0.18061 | -0.22959 | -0.30714 | -0.37551 | -0.45 | -0.80918 | -0.90408 | -0.91837 | 0.39388 | 0.37041 | 0.31327 | 0.27959 | 0.25408 | 0.18878 | 0.15714 | 0.10408 | 0.057143 | 0.005102 | -0.24694 | -0.36531 | -0.48571 | 0.27245 | 0.23571 | 0.1551 | 0.10612 | 0.065306 | -0.013265 | -0.055102 | -0.12959 | -0.19184 | -0.26531
|  | TARBERT | CF |  |  |  |  | 0.11633 | 0.086735 | 0.042857 | -0.026531 | -0.061224 | -0.10612 | -0.17245 | -0.20714 | -0.2551 | -0.30102 | -0.54694 | -0.78367 | -0.90714 | 0.39898 | 0.38265 | 0.35306 | 0.30306 | 0.27959 | 0.24694 | 0.18878 | 0.16224 | 0.12347 | 0.088776 | -0.12653 | -0.4 | -0.69796 | 0.28061 | 0.2551 | 0.21224 | 0.1398 | 0.10612 | 0.061224 | -0.0091837 | -0.040816 | -0.090816 | -0.13265
| PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0.092 | 0.16447 | 0.15631 | 0.15529 | 0.15529 | 0.15427 | 0.14611 | 0.14509 | 0.1359 | 0.13488 | 0.13692 | 0.13386 | 0.13386 | 0.11586 | 0.15362 | 0.14647 | 0.14545 | 0.14545 | 0.14443 | 0.13627 | 0.13525 | 0.12709 | 0.12607 | 0.13117 | 0.12504 | 0.13915 | 0.13711 | 0.16058 | 0.15241 | 0.15037 | 0.15037 | 0.14935 | 0.14119 | 0.14017 | 0.132 | 0.12996 | 0.13302
|  | TARBERT JURA | EE |  |  |  |  | 0.16447 | 0.15631 | 0.15529 | 0.15529 | 0.15427 | 0.14611 | 0.14509 | 0.1359 | 0.13488 | 0.13692 | 0.13488 | 0.13488 | 0.11586 | 0.15362 | 0.14647 | 0.14545 | 0.14545 | 0.14443 | 0.13627 | 0.13525 | 0.12709 | 0.12607 | 0.13117 | 0.13117 | 0.14017 | 0.13915 | 0.16058 | 0.15241 | 0.15037 | 0.15037 | 0.14935 | 0.14119 | 0.14017 | 0.132 | 0.12996 | 0.13302
|  | TARBERT JURA | HT |  |  |  |  | 0.16549 | 0.16345 | 0.16345 | 0.15529 | 0.15529 | 0.15427 | 0.15325 | 0.14509 | 0.14304 | 0.14304 | 0.13488 | 0.13386 | 0.11586 | 0.15464 | 0.15362 | 0.15362 | 0.14545 | 0.14545 | 0.14443 | 0.14341 | 0.13525 | 0.13423 | 0.13423 | 0.13117 | 0.13915 | 0.13915 | 0.16058 | 0.15956 | 0.15956 | 0.15037 | 0.15037 | 0.14935 | 0.14833 | 0.14017 | 0.13915 | 0.13915
|  | TARBERT JURA | HE |  |  |  |  | 0.16549 | 0.16345 | 0.16345 | 0.15529 | 0.15529 | 0.15427 | 0.15325 | 0.14611 | 0.14407 | 0.14202 | 0.13488 | 0.13488 | 0.11688 | 0.15464 | 0.15362 | 0.15362 | 0.14545 | 0.14545 | 0.14443 | 0.14341 | 0.13627 | 0.13525 | 0.13321 | 0.13117 | 0.14017 | 0.14017 | 0.16058 | 0.15956 | 0.15956 | 0.15037 | 0.15037 | 0.14935 | 0.14833 | 0.14119 | 0.14017 | 0.13711
|  | TARBERT JURA | CF |  |  |  |  | 0.16549 | 0.16345 | 0.16345 | 0.16345 | 0.15631 | 0.15529 | 0.15529 | 0.15427 | 0.15427 | 0.14611 | 0.13386 | 0.13488 | 0.11586 | 0.15464 | 0.15362 | 0.15362 | 0.15362 | 0.14647 | 0.14545 | 0.14545 | 0.14443 | 0.14443 | 0.13627 | 0.12504 | 0.14017 | 0.13711 | 0.16058 | 0.15956 | 0.15956 | 0.15956 | 0.15241 | 0.15037 | 0.15037 | 0.14935 | 0.14935 | 0.14119
| PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 1.694 | 0.92675 | 0.8492 | 0.76654 | 0.67164 | 0.57471 | 0.46246 | 0.32267 | 0.18695 | 0.099196 | -0.0079469 | -0.27631 | -0.37529 | -0.59264 | 1.6441 | 1.5961 | 1.5431 | 1.4798 | 1.4237 | 1.3492 | 1.2563 | 1.1614 | 1.1023 | 1.0318 | 0.81756 | 0.82369 | 0.55838 | 1.2921 | 1.2237 | 1.1431 | 1.0543 | 0.96654 | 0.86144 | 0.73083 | 0.60124 | 0.51858 | 0.41654
|  | TARBERT LOCH FYNE | EE |  |  |  |  | 0.92675 | 0.8492 | 0.76654 | 0.67164 | 0.57471 | 0.46246 | 0.32267 | 0.18695 | 0.099196 | -0.0079469 | -0.27631 | -0.32121 | -0.55795 | 1.6441 | 1.5961 | 1.5431 | 1.4798 | 1.4237 | 1.3492 | 1.2563 | 1.1614 | 1.1023 | 1.0318 | 0.81756 | 0.82369 | 0.67675 | 1.2921 | 1.2237 | 1.1431 | 1.0543 | 0.96654 | 0.86144 | 0.73083 | 0.60124 | 0.51858 | 0.41654
|  | TARBERT LOCH FYNE | HT |  |  |  |  | 0.96144 | 0.88389 | 0.80124 | 0.73083 | 0.64001 | 0.55532 | 0.47777 | 0.37675 | 0.28593 | 0.18287 | -0.19264 | -0.37529 | -0.59264 | 1.6737 | 1.6278 | 1.5808 | 1.5359 | 1.4859 | 1.4298 | 1.39 | 1.3227 | 1.2655 | 1.1931 | 0.93083 | 0.91144 | 0.89716 | 1.3267 | 1.2584 | 1.1829 | 1.1165 | 1.0359 | 0.95532 | 0.88389 | 0.78899 | 0.70226 | 0.60532
|  | TARBERT LOCH FYNE | HE |  |  |  |  | 0.96144 | 0.90226 | 0.84205 | 0.78287 | 0.70124 | 0.62777 | 0.53899 | 0.45532 | 0.38287 | 0.29818 | -0.088559 | -0.18856 | -0.39672 | 1.6727 | 1.6359 | 1.6002 | 1.5584 | 1.5125 | 1.4604 | 1.4084 | 1.3502 | 1.2972 | 1.238 | 0.95532 | 0.92573 | 0.8043 | 1.3267 | 1.2757 | 1.2196 | 1.1625 | 1.091 | 1.0206 | 0.94205 | 0.86246 | 0.79001 | 0.71144
|  | TARBERT LOCH FYNE | CF |  |  |  |  | 0.97164 | 0.94001 | 0.89511 | 0.85634 | 0.7992 | 0.75532 | 0.67981 | 0.60022 | 0.55838 | 0.49307 | 0.16858 | -0.059988 | -0.40591 | 1.6808 | 1.6604 | 1.6278 | 1.6063 | 1.5645 | 1.5359 | 1.4839 | 1.4267 | 1.3972 | 1.3472 | 1.0716 | 0.89307 | 0.55838 | 1.337 | 1.3063 | 1.2645 | 1.2288 | 1.1767 | 1.1349 | 1.0676 | 0.99307 | 0.95634 | 0.89511
| TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | NO | YES | 0.257 | 2.4133 | 2.3735 | 2.3469 | 2.3133 | 2.2653 | 2.2184 | 2.1827 | 2.1235 | 2.0612 | 2.0071 | 1.8827 | 1.8367 | 1.8204 | 2.8102 | 2.7837 | 2.7633 | 2.7408 | 2.7031 | 2.6673 | 2.6439 | 2.598 | 2.551 | 2.5143 | 2.4092 | 2.3531 | 2.1439 | 2.6735 | 2.6347 | 2.6082 | 2.5765 | 2.5276 | 2.4786 | 2.45 | 2.3929 | 2.3316 | 2.2806
|  | TAYNUILT | EE |  |  |  |  | 2.4133 | 2.3735 | 2.3469 | 2.3133 | 2.2653 | 2.2184 | 2.1827 | 2.1235 | 2.0612 | 2.0071 | 1.8827 | 1.8571 | 1.8398 | 2.8102 | 2.7837 | 2.7633 | 2.7408 | 2.7031 | 2.6673 | 2.6439 | 2.598 | 2.551 | 2.5143 | 2.4092 | 2.3561 | 2.2684 | 2.6735 | 2.6347 | 2.6082 | 2.5765 | 2.5276 | 2.4786 | 2.45 | 2.3929 | 2.3316 | 2.2806
|  | TAYNUILT | HT |  |  |  |  | 2.4255 | 2.4 | 2.3724 | 2.349 | 2.3163 | 2.2878 | 2.248 | 2.198 | 2.1704 | 2.1214 | 1.9184 | 1.8367 | 1.8204 | 2.8224 | 2.8082 | 2.7898 | 2.7745 | 2.75 | 2.7327 | 2.7031 | 2.6663 | 2.652 | 2.6194 | 2.4673 | 2.4143 | 2.4041 | 2.6929 | 2.6714 | 2.6469 | 2.6214 | 2.5878 | 2.5612 | 2.5173 | 2.4704 | 2.4439 | 2.3969
|  | TAYNUILT | HE |  |  |  |  | 2.4235 | 2.4031 | 2.3847 | 2.3663 | 2.3388 | 2.3173 | 2.2796 | 2.2347 | 2.2122 | 2.1704 | 1.9551 | 1.899 | 1.8959 | 2.8204 | 2.8082 | 2.7929 | 2.7806 | 2.7561 | 2.7418 | 2.7122 | 2.6755 | 2.6622 | 2.6316 | 2.4622 | 2.3867 | 2.3102 | 2.6908 | 2.6724 | 2.652 | 2.6347 | 2.6041 | 2.5837 | 2.5449 | 2.498 | 2.4806 | 2.4357
|  | TAYNUILT | CF |  |  |  |  | 2.4265 | 2.4122 | 2.3949 | 2.3745 | 2.3602 | 2.3367 | 2.3112 | 2.2898 | 2.2622 | 2.2296 | 2.098 | 1.9561 | 1.8857 | 2.8265 | 2.8133 | 2.802 | 2.7847 | 2.7745 | 2.7541 | 2.7296 | 2.7102 | 2.6857 | 2.6582 | 2.5347 | 2.3531 | 2.1439 | 2.698 | 2.6847 | 2.6673 | 2.6449 | 2.6327 | 2.6082 | 2.5827 | 2.5633 | 2.5337 | 2.501
| BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 1.327 | 7.5439 | 7.3857 | 7.2071 | 6.9837 | 6.602 | 6.2031 | 5.7051 | 5.0867 | 4.5 | 3.9612 | 2.3929 | 2.1571 | 2.1724 | 12.9306 | 12.8327 | 12.7184 | 12.6041 | 12.3765 | 12.0939 | 11.7531 | 11.3347 | 10.9286 | 10.5173 | 9.1796 | 8.1908 | 4.2306 | 10.998 | 10.851 | 10.5194 | 10.1724 | 9.7796 | 9.3582 | 8.8663 | 8.1765 | 7.5286 | 6.951
|  | THIMBLEROW | EE |  |  |  |  | 7.5439 | 7.3857 | 7.2071 | 6.9837 | 6.602 | 6.2031 | 5.7051 | 5.0867 | 4.5 | 3.9612 | 2.5163 | 2.9316 | 2.8296 | 12.9306 | 12.8327 | 12.7184 | 12.6041 | 12.3765 | 12.0939 | 11.7531 | 11.3347 | 10.9286 | 10.5173 | 9.1796 | 8.4041 | 6.7306 | 10.998 | 10.851 | 10.5194 | 10.1724 | 9.7796 | 9.3582 | 8.8663 | 8.1765 | 7.5286 | 6.951
|  | THIMBLEROW | HT |  |  |  |  | 7.5857 | 7.4347 | 7.2806 | 7.1439 | 6.9214 | 6.6235 | 6.1745 | 5.6796 | 5.2041 | 4.6684 | 2.3929 | 2.1571 | 2.1724 | 12.9745 | 12.8949 | 12.8122 | 12.7327 | 12.6408 | 12.5439 | 12.3031 | 12.0204 | 11.748 | 11.4398 | 9.9286 | 9.602 | 9.5714 | 11.0388 | 10.902 | 10.7122 | 10.4429 | 10.1378 | 9.8388 | 9.3929 | 8.8969 | 8.4439 | 7.949
|  | THIMBLEROW | HE |  |  |  |  | 7.5959 | 7.4898 | 7.3827 | 7.2663 | 7.15 | 7.0408 | 6.8673 | 6.501 | 6.1776 | 5.8235 | 4.3143 | 3.7357 | 4.1561 | 12.9745 | 12.9051 | 12.8316 | 12.752 | 12.6633 | 12.5827 | 12.4408 | 12.1898 | 11.9643 | 11.6867 | 10.2347 | 9.0449 | 7.7531 | 11.048 | 10.95 | 10.8531 | 10.7469 | 10.5561 | 10.3704 | 10.0408 | 9.6714 | 9.3439 | 8.9837
|  | THIMBLEROW | CF |  |  |  |  | 7.6459 | 7.6051 | 7.548 | 7.4898 | 7.4214 | 7.349 | 7.2816 | 7.1857 | 7.1061 | 7.0184 | 6.1306 | 4.7684 | 3.449 | 12.999 | 12.9592 | 12.9061 | 12.8531 | 12.7878 | 12.7153 | 12.6439 | 12.4837 | 12.3061 | 12.1122 | 10.7643 | 8.1908 | 4.2306 | 11.0908 | 11.0541 | 10.998 | 10.9459 | 10.8827 | 10.7796 | 10.6571 | 10.4786 | 10.3245 | 10.1643
| TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0 | 0.19416 | 0.18498 | 0.18294 | 0.17376 | 0.17273 | 0.17069 | 0.16049 | 0.15743 | 0.15947 | 0.15845 | 0.15131 | 0.14722 | 0.12922 | 0.19045 | 0.18229 | 0.18229 | 0.17412 | 0.1731 | 0.1731 | 0.1629 | 0.16596 | 0.1629 | 0.16188 | 0.1629 | 0.17088 | 0.16884 | 0.19537 | 0.1872 | 0.18414 | 0.17598 | 0.17496 | 0.17292 | 0.16271 | 0.16067 | 0.16169 | 0.16067
|  | TIRORAN BRIDGE | EE |  |  |  |  | 0.19416 | 0.18498 | 0.18294 | 0.17376 | 0.17273 | 0.17069 | 0.16049 | 0.15743 | 0.16355 | 0.16151 | 0.15131 | 0.15029 | 0.13229 | 0.19045 | 0.18229 | 0.18229 | 0.17412 | 0.1731 | 0.1731 | 0.1629 | 0.16596 | 0.17004 | 0.16902 | 0.1629 | 0.1719 | 0.16884 | 0.19537 | 0.1872 | 0.18414 | 0.17598 | 0.17496 | 0.17292 | 0.16271 | 0.16067 | 0.16578 | 0.16373
|  | TIRORAN BRIDGE | HT |  |  |  |  | 0.19518 | 0.19212 | 0.18294 | 0.18294 | 0.1809 | 0.17886 | 0.16865 | 0.16865 | 0.15947 | 0.15845 | 0.15335 | 0.14722 | 0.12922 | 0.19147 | 0.18943 | 0.18229 | 0.18229 | 0.18127 | 0.18024 | 0.17106 | 0.17106 | 0.1629 | 0.16188 | 0.16494 | 0.17088 | 0.17088 | 0.19639 | 0.19435 | 0.18414 | 0.18414 | 0.18312 | 0.18108 | 0.1719 | 0.17088 | 0.16169 | 0.16067
|  | TIRORAN BRIDGE | HE |  |  |  |  | 0.19518 | 0.19212 | 0.18498 | 0.18294 | 0.18294 | 0.18294 | 0.17273 | 0.17171 | 0.16253 | 0.15947 | 0.15641 | 0.15335 | 0.13433 | 0.19147 | 0.18943 | 0.18229 | 0.18229 | 0.18229 | 0.18229 | 0.1731 | 0.1731 | 0.16494 | 0.1629 | 0.16698 | 0.17394 | 0.17088 | 0.19639 | 0.19435 | 0.1872 | 0.18414 | 0.18414 | 0.18414 | 0.17496 | 0.17394 | 0.16476 | 0.16271
|  | TIRORAN BRIDGE | CF |  |  |  |  | 0.19518 | 0.19314 | 0.19212 | 0.18396 | 0.18396 | 0.18396 | 0.18192 | 0.17478 | 0.17273 | 0.17273 | 0.15845 | 0.15641 | 0.13433 | 0.19147 | 0.19045 | 0.18943 | 0.18229 | 0.18229 | 0.18229 | 0.18127 | 0.17412 | 0.1731 | 0.1731 | 0.16698 | 0.17292 | 0.16884 | 0.19639 | 0.19537 | 0.19435 | 0.18516 | 0.18516 | 0.18516 | 0.18414 | 0.177 | 0.17496 | 0.17496
| BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 1.423 | -0.77829 | -0.79768 | -0.82421 | -0.84666 | -0.87523 | -0.98033 | -1.1232 | -1.2762 | -1.363 | -1.3946 | -1.5344 | -1.5589 | -1.564 | -0.41094 | -0.42217 | -0.44156 | -0.45584 | -0.48033 | -0.51196 | -0.58747 | -0.66604 | -0.71094 | -0.75074 | -0.82727 | -0.85074 | -0.94156 | -0.52217 | -0.54156 | -0.57523 | -0.5936 | -0.62931 | -0.70482 | -0.83135 | -0.96196 | -1.0344 | -1.0885
|  | TOMATIN | EE |  |  |  |  | -0.77829 | -0.79768 | -0.82421 | -0.84666 | -0.87523 | -0.89666 | -0.93135 | -1.0814 | -1.2232 | -1.3946 | -1.5344 | -1.5487 | -1.5487 | -0.41094 | -0.42217 | -0.44156 | -0.45584 | -0.48033 | -0.49462 | -0.52115 | -0.60686 | -0.66809 | -0.75074 | -0.82727 | -0.85074 | -0.88747 | -0.52217 | -0.54156 | -0.57523 | -0.5936 | -0.62931 | -0.6487 | -0.69258 | -0.83747 | -0.9487 | -1.0885
|  | TOMATIN | HT |  |  |  |  | -0.77115 | -0.78849 | -0.80686 | -0.82727 | -0.85176 | -0.98033 | -1.1232 | -1.2762 | -1.363 | -1.3936 | -1.5018 | -1.5589 | -1.564 | -0.40176 | -0.40992 | -0.42319 | -0.43441 | -0.45278 | -0.51196 | -0.58747 | -0.66604 | -0.71094 | -0.72931 | -0.80278 | -0.83135 | -0.82931 | -0.50992 | -0.52523 | -0.54768 | -0.56707 | -0.59462 | -0.70482 | -0.83135 | -0.96196 | -1.0344 | -1.065
|  | TOMATIN | HE |  |  |  |  | -0.77115 | -0.78441 | -0.80074 | -0.81604 | -0.83339 | -0.85176 | -0.87523 | -0.97115 | -1.0834 | -1.2018 | -1.4956 | -1.5354 | -1.5405 | -0.40176 | -0.4089 | -0.42217 | -0.43033 | -0.44972 | -0.45482 | -0.47421 | -0.52625 | -0.58645 | -0.64768 | -0.80584 | -0.84564 | -0.88441 | -0.50992 | -0.52115 | -0.54258 | -0.55584 | -0.57931 | -0.59053 | -0.61707 | -0.71298 | -0.81502 | -0.92115
|  | TOMATIN | CF |  |  |  |  | -0.76707 | -0.78033 | -0.79258 | -0.80686 | -0.82013 | -0.83441 | -0.84666 | -0.86502 | -0.94972 | -1.0416 | -1.364 | -1.462 | -1.5242 | -0.39768 | -0.40788 | -0.41502 | -0.42931 | -0.43747 | -0.44972 | -0.45686 | -0.47217 | -0.52625 | -0.57217 | -0.75074 | -0.84258 | -0.94156 | -0.50686 | -0.52013 | -0.53441 | -0.55176 | -0.564 | -0.58441 | -0.59156 | -0.61298 | -0.70176 | -0.77931
| LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | NO | 0 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10269 | 0.10269 | 0.10269 | 0.10269 | 0.10269 | 0.096571 | 0.094531 | 0.094531 | 0.085531 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.097776 | 0.097776 | 0.097776 | 0.097776 | 0.097776 | 0.090633 | 0.089612 | 0.094112 | 0.094112 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10126 | 0.10126 | 0.10126 | 0.10126 | 0.10126 | 0.094112
|  | TORBOLL | EE |  |  |  |  | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10269 | 0.10269 | 0.10269 | 0.10371 | 0.10371 | 0.096571 | 0.094531 | 0.094531 | 0.085531 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.097776 | 0.097776 | 0.097776 | 0.098796 | 0.097776 | 0.090633 | 0.089612 | 0.094112 | 0.094112 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10126 | 0.10126 | 0.10126 | 0.10228 | 0.10126 | 0.094112
|  | TORBOLL | HT |  |  |  |  | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10984 | 0.10269 | 0.10371 | 0.10371 | 0.10371 | 0.094531 | 0.094531 | 0.085531 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.097776 | 0.098796 | 0.098796 | 0.098796 | 0.089612 | 0.094112 | 0.094112 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10126 | 0.10228 | 0.10228 | 0.10228
|  | TORBOLL | HE |  |  |  |  | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10269 | 0.10269 | 0.10269 | 0.10371 | 0.094531 | 0.094531 | 0.085531 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.097776 | 0.097776 | 0.097776 | 0.098796 | 0.089612 | 0.094112 | 0.094112 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.10126 | 0.10126 | 0.10126 | 0.10228
|  | TORBOLL | CF |  |  |  |  | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10473 | 0.10473 | 0.10473 | 0.10269 | 0.094531 | 0.085531 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.098796 | 0.098796 | 0.098796 | 0.097776 | 0.094112 | 0.094112 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10228 | 0.10228 | 0.10228
| KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 2.421 | 11.4471 | 10.8858 | 10.0032 | 8.8369 | 7.796 | 5.8828 | 4.8328 | 3.696 | 2.5899 | 1.6379 | -3.6325 | -8.2233 | -13.2489 | 12.9481 | 12.4736 | 11.5736 | 10.494 | 9.796 | 8.0277 | 7.3654 | 6.5511 | 5.6195 | 4.4083 | -0.61008 | -4.6795 | -9.0223 | 12.2767 | 11.7848 | 10.8981 | 9.7256 | 8.8981 | 6.9705 | 6.1277 | 5.142 | 4.1583 | 3.0144
|  | TORRYBURN | EE |  |  |  |  | 11.4481 | 10.8981 | 10.3052 | 9.6471 | 8.4022 | 6.9267 | 5.6583 | 4.895 | 3.5807 | 2.3858 | -2.0366 | -6.256 | -8.9519 | 12.9716 | 12.4899 | 11.9552 | 11.3736 | 10.3899 | 9.1807 | 8.294 | 7.7593 | 6.7685 | 5.9277 | 2.9338 | -0.70294 | -2.3529 | 12.292 | 11.8144 | 11.2654 | 10.5899 | 9.4746 | 8.0991 | 7.0226 | 6.3216 | 5.1409 | 4.1226
|  | TORRYBURN | HT |  |  |  |  | 11.4471 | 10.8858 | 10.0032 | 8.8369 | 7.796 | 5.8828 | 4.8328 | 3.696 | 2.5899 | 1.6379 | -2.8193 | -7.5305 | -12.0764 | 12.9481 | 12.4736 | 11.5736 | 10.494 | 9.796 | 8.0277 | 7.3654 | 6.6175 | 5.9226 | 5.192 | 2.1328 | -2.2468 | -6.307 | 12.2767 | 11.7848 | 10.8981 | 9.7256 | 8.8981 | 6.9705 | 6.1277 | 5.142 | 4.1583 | 3.2654
|  | TORRYBURN | HE |  |  |  |  | 11.5124 | 11.0195 | 10.2705 | 9.3379 | 8.4787 | 6.7756 | 5.6828 | 4.5726 | 3.4287 | 2.2552 | -3.6325 | -8.2233 | -13.2489 | 13.0134 | 12.5858 | 11.8175 | 10.8471 | 10.0379 | 8.3552 | 7.4664 | 6.5511 | 5.6195 | 4.4083 | -0.61008 | -4.6795 | -9.0223 | 12.3409 | 11.9022 | 11.1552 | 10.194 | 9.2971 | 7.4889 | 6.4705 | 5.4134 | 4.3358 | 3.0144
|  | TORRYBURN | CF |  |  |  |  | 11.6858 | 11.3603 | 10.9909 | 10.5971 | 9.9256 | 9.0726 | 8.4001 | 7.7103 | 7.0256 | 6.245 | 2.9909 | 0.32257 | -2.7621 | 13.1664 | 12.8736 | 12.5511 | 12.193 | 11.546 | 10.7981 | 10.2511 | 9.7001 | 9.1664 | 8.5287 | 5.8899 | 4.3052 | 3.046 | 12.495 | 12.2011 | 11.8624 | 11.5134 | 10.8644 | 10.0777 | 9.4634 | 8.8348 | 8.2256 | 7.5093
| LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | NO | 0.003 | 0.26653 | 0.2502 | 0.22776 | 0.2002 | 0.18592 | 0.15735 | 0.11959 | 0.094082 | 0.056327 | 0.024694 | -0.044694 | -0.065102 | -0.11316 | 0.36847 | 0.35929 | 0.34704 | 0.32663 | 0.31949 | 0.3001 | 0.27765 | 0.26133 | 0.23582 | 0.21643 | 0.17459 | 0.18689 | 0.18587 | 0.3277 | 0.31036 | 0.29199 | 0.26444 | 0.25117 | 0.22362 | 0.19097 | 0.16342 | 0.1277 | 0.099133
|  | TRESSADY | EE |  |  |  |  | 0.26653 | 0.2502 | 0.22776 | 0.2002 | 0.18592 | 0.15735 | 0.11959 | 0.094082 | 0.056327 | 0.024694 | -0.044694 | -0.029388 | -0.07949 | 0.36847 | 0.35929 | 0.34704 | 0.32663 | 0.31949 | 0.3001 | 0.27765 | 0.26133 | 0.23582 | 0.21643 | 0.17459 | 0.20832 | 0.20015 | 0.3277 | 0.31036 | 0.29199 | 0.26444 | 0.25117 | 0.22362 | 0.19097 | 0.16342 | 0.1277 | 0.099133
|  | TRESSADY | HT |  |  |  |  | 0.27776 | 0.26245 | 0.24714 | 0.22571 | 0.21143 | 0.18592 | 0.15837 | 0.14408 | 0.11551 | 0.086939 | -0.018163 | -0.065102 | -0.11316 | 0.37765 | 0.36949 | 0.35929 | 0.34806 | 0.33888 | 0.32357 | 0.30418 | 0.29806 | 0.27867 | 0.26031 | 0.19194 | 0.18689 | 0.18587 | 0.33893 | 0.3226 | 0.31036 | 0.28995 | 0.27668 | 0.25321 | 0.22668 | 0.21138 | 0.18485 | 0.1573
|  | TRESSADY | HE |  |  |  |  | 0.27878 | 0.26449 | 0.25429 | 0.23694 | 0.22469 | 0.20327 | 0.18082 | 0.16653 | 0.14204 | 0.11755 | -0.004898 | -0.03449 | -0.085612 | 0.37867 | 0.37153 | 0.36337 | 0.35214 | 0.345 | 0.33071 | 0.31439 | 0.30827 | 0.29194 | 0.27459 | 0.19908 | 0.20321 | 0.19607 | 0.33995 | 0.32668 | 0.31546 | 0.29913 | 0.28995 | 0.26954 | 0.24505 | 0.23383 | 0.21138 | 0.18485
|  | TRESSADY | CF |  |  |  |  | 0.27878 | 0.26755 | 0.25429 | 0.24306 | 0.22878 | 0.21959 | 0.20224 | 0.1798 | 0.17673 | 0.16041 | 0.075714 | 0.019592 | -0.058061 | 0.37867 | 0.37153 | 0.36235 | 0.35724 | 0.34908 | 0.34194 | 0.32969 | 0.31541 | 0.31439 | 0.30418 | 0.24602 | 0.23077 | 0.2073 | 0.33995 | 0.32974 | 0.3175 | 0.30628 | 0.29199 | 0.28281 | 0.2675 | 0.24505 | 0.24199 | 0.22668
| SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 0.036 | 5.1218 | 5.0606 | 4.9943 | 4.932 | 4.8586 | 4.778 | 4.6627 | 4.5667 | 4.4473 | 4.3433 | 4.0984 | 4.0229 | 3.4635 | 5.4318 | 5.3829 | 5.3349 | 5.2951 | 5.2298 | 5.1727 | 5.092 | 5.0359 | 4.9522 | 4.8869 | 4.7706 | 4.9784 | 4.7529 | 5.2049 | 5.1478 | 5.0876 | 5.0294 | 4.96 | 4.8916 | 4.808 | 4.7284 | 4.6324 | 4.5324
|  | TUMBLIN | EE |  |  |  |  | 5.1218 | 5.0606 | 4.9943 | 4.932 | 4.8586 | 4.778 | 4.6627 | 4.5667 | 4.4473 | 4.3433 | 4.0984 | 4.0657 | 3.4961 | 5.4318 | 5.3829 | 5.3349 | 5.2951 | 5.2298 | 5.1727 | 5.092 | 5.0359 | 4.9522 | 4.8869 | 4.7706 | 4.9784 | 4.8631 | 5.2049 | 5.1478 | 5.0876 | 5.0294 | 4.96 | 4.8916 | 4.808 | 4.7284 | 4.6324 | 4.5324
|  | TUMBLIN | HT |  |  |  |  | 5.1422 | 5.0902 | 5.0402 | 4.9841 | 4.9218 | 4.8647 | 4.7963 | 4.7208 | 4.6443 | 4.5545 | 4.1882 | 4.0229 | 3.4635 | 5.4553 | 5.4267 | 5.3992 | 5.3676 | 5.3206 | 5.2941 | 5.239 | 5.1818 | 5.1216 | 5.0553 | 4.8216 | 5.0294 | 5.0212 | 5.2253 | 5.1773 | 5.1314 | 5.0794 | 5.0222 | 4.9692 | 4.9049 | 4.8335 | 4.7631 | 4.6906
|  | TUMBLIN | HE |  |  |  |  | 5.1412 | 5.0973 | 5.0535 | 5.0055 | 4.9524 | 4.9024 | 4.8341 | 4.7555 | 4.679 | 4.5973 | 4.2229 | 4.1106 | 3.5237 | 5.4553 | 5.4308 | 5.4022 | 5.3737 | 5.3318 | 5.3073 | 5.2553 | 5.2033 | 5.1441 | 5.0818 | 4.841 | 5.0416 | 4.9335 | 5.2243 | 5.1835 | 5.1427 | 5.0978 | 5.0478 | 5.0018 | 4.9365 | 4.8631 | 4.7916 | 4.7151
|  | TUMBLIN | CF |  |  |  |  | 5.1555 | 5.1249 | 5.0943 | 5.0504 | 5.0178 | 4.9749 | 4.929 | 4.8933 | 4.8453 | 4.8004 | 4.5371 | 4.279 | 3.592 | 5.4604 | 5.4369 | 5.4196 | 5.391 | 5.3676 | 5.342 | 5.3053 | 5.2829 | 5.242 | 5.2094 | 5.0124 | 5.0253 | 4.7529 | 5.2376 | 5.212 | 5.1865 | 5.1549 | 5.1243 | 5.0886 | 5.0488 | 5.011 | 4.9682 | 4.9233
| TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 0.15 | 0.27959 | 0.2551 | 0.23265 | 0.2 | 0.17347 | 0.13878 | 0.1 | 0.053061 | 0.0091837 | -0.030612 | -0.14898 | -0.17653 | -0.19898 | 0.40102 | 0.39286 | 0.38163 | 0.36939 | 0.35816 | 0.34184 | 0.31531 | 0.28061 | 0.25204 | 0.22449 | 0.14286 | 0.11939 | 0.087755 | 0.22857 | 0.20408 | 0.17959 | 0.15 | 0.12143 | 0.089796 | 0.052041 | 0.0071429 | -0.033673 | -0.071429
|  | TUMMEL BRIDGE | EE |  |  |  |  | 0.27959 | 0.2551 | 0.23265 | 0.2 | 0.17347 | 0.13878 | 0.1 | 0.053061 | 0.0091837 | -0.030612 | -0.14898 | -0.17551 | -0.17653 | 0.40102 | 0.39286 | 0.38163 | 0.36939 | 0.35816 | 0.34184 | 0.31531 | 0.28061 | 0.25204 | 0.22449 | 0.14286 | 0.12551 | 0.12041 | 0.22857 | 0.20408 | 0.17959 | 0.15 | 0.12143 | 0.089796 | 0.052041 | 0.0071429 | -0.033673 | -0.071429
|  | TUMMEL BRIDGE | HT |  |  |  |  | 0.28571 | 0.27041 | 0.25204 | 0.23061 | 0.20918 | 0.17857 | 0.15306 | 0.11429 | 0.080612 | 0.046939 | -0.09898 | -0.1602 | -0.18163 | 0.4051 | 0.39796 | 0.3898 | 0.38265 | 0.37347 | 0.36224 | 0.35306 | 0.32959 | 0.30408 | 0.28163 | 0.17959 | 0.13673 | 0.12143 | 0.23469 | 0.21735 | 0.19796 | 0.17755 | 0.15612 | 0.12755 | 0.10306 | 0.068367 | 0.034694 | 0.0030612
|  | TUMMEL BRIDGE | HE |  |  |  |  | 0.28571 | 0.27347 | 0.2551 | 0.23571 | 0.21224 | 0.18673 | 0.15918 | 0.12041 | 0.086735 | 0.05 | -0.12245 | -0.17653 | -0.19898 | 0.4051 | 0.39796 | 0.39184 | 0.38265 | 0.37449 | 0.36224 | 0.35306 | 0.32653 | 0.30102 | 0.27755 | 0.15612 | 0.11939 | 0.10306 | 0.23469 | 0.21735 | 0.20102 | 0.18265 | 0.15918 | 0.13571 | 0.10816 | 0.071429 | 0.038776 | 0.0040816
|  | TUMMEL BRIDGE | CF |  |  |  |  | 0.28469 | 0.27959 | 0.26735 | 0.25306 | 0.2398 | 0.22347 | 0.2051 | 0.19286 | 0.17143 | 0.14592 | 0.015306 | -0.097959 | -0.18163 | 0.40612 | 0.40408 | 0.39898 | 0.39286 | 0.38878 | 0.38163 | 0.37347 | 0.36633 | 0.35612 | 0.33878 | 0.25102 | 0.17245 | 0.087755 | 0.2398 | 0.22959 | 0.21837 | 0.2051 | 0.19388 | 0.17653 | 0.15918 | 0.1398 | 0.12041 | 0.095918
| MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | NO | 0.933 | 2.4786 | 2.2051 | 1.7949 | 1.3153 | 0.71735 | -0.15 | -1.0939 | -2.1806 | -3.349 | -4.399 | -6.8633 | -8.1622 | -9.3959 | 6.2816 | 6.0184 | 5.6959 | 5.3612 | 4.9357 | 4.3418 | 3.5888 | 2.7286 | 1.7429 | 0.79184 | -0.97959 | -1.273 | -1.8281 | 1.0566 | 0.80051 | 0.46786 | 0.13112 | -0.29337 | -0.86888 | -1.6158 | -2.6719 | -3.8087 | -4.8434
|  | TURRIFF | EE |  |  |  |  | 2.4786 | 2.2051 | 1.7949 | 1.3327 | 0.76429 | -0.016327 | -1.0337 | -1.8378 | -2.851 | -3.8908 | -6.8633 | -8.0367 | -9.2092 | 6.2816 | 6.0184 | 5.6959 | 5.3612 | 4.9357 | 4.3418 | 3.5888 | 3.0561 | 2.2235 | 1.3255 | -0.97959 | -1.273 | -1.7944 | 1.0566 | 0.80051 | 0.46786 | 0.13112 | -0.29337 | -0.86888 | -1.6158 | -2.4179 | -3.4219 | -4.4505
|  | TURRIFF | HT |  |  |  |  | 2.5582 | 2.2449 | 1.801 | 1.3153 | 0.71735 | -0.15 | -1.0939 | -2.1806 | -3.349 | -4.399 | -6.8082 | -8.1622 | -9.3959 | 6.3112 | 6.101 | 5.798 | 5.4806 | 5.0755 | 4.3898 | 3.6327 | 2.7286 | 1.7429 | 0.79184 | -0.7602 | -0.99847 | -1.2311 | 1.1689 | 0.94235 | 0.65051 | 0.35663 | -0.016837 | -0.67398 | -1.6026 | -2.6719 | -3.8087 | -4.8434
|  | TURRIFF | HE |  |  |  |  | 2.5765 | 2.351 | 2.0418 | 1.6684 | 1.198 | 0.53163 | -0.33673 | -1.2082 | -2.1122 | -2.8837 | -6.0061 | -7.1786 | -8.6041 | 6.3327 | 6.1439 | 5.9071 | 5.6439 | 5.301 | 4.8194 | 4.1214 | 3.3857 | 2.6082 | 1.8439 | -0.57653 | -0.96173 | -1.5852 | 1.1791 | 0.9852 | 0.74337 | 0.49745 | 0.17296 | -0.25255 | -0.86276 | -1.7311 | -2.624 | -3.3934
|  | TURRIFF | CF |  |  |  |  | 2.6439 | 2.4949 | 2.3061 | 2.0704 | 1.7673 | 1.3633 | 0.93673 | 0.38878 | -0.13163 | -0.67449 | -3.2327 | -5.5806 | -7.5867 | 6.3969 | 6.2714 | 6.1 | 5.9296 | 5.6959 | 5.3827 | 5.0592 | 4.6153 | 4.1949 | 3.7408 | 1.3908 | -0.46276 | -1.8281 | 1.2403 | 1.1005 | 0.92602 | 0.76786 | 0.54745 | 0.26276 | -0.02398 | -0.4352 | -0.825 | -1.2474
| RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 0.476 | 0.17408 | 0.16082 | 0.13939 | 0.1251 | 0.10163 | 0.076122 | 0.059796 | 0.029184 | 0.010816 | -0.015714 | -0.11163 | -0.22082 | -0.26265 | 0.46184 | 0.45061 | 0.43633 | 0.42714 | 0.40469 | 0.38429 | 0.3649 | 0.33224 | 0.30367 | 0.27 | 0.10878 | 0.033265 | -0.0014286 | 0.43633 | 0.41388 | 0.38837 | 0.35673 | 0.32408 | 0.28633 | 0.24041 | 0.18122 | 0.13122 | 0.072041
|  | TYNDRUM | EE |  |  |  |  | 0.17408 | 0.16082 | 0.13939 | 0.1251 | 0.10163 | 0.076122 | 0.059796 | 0.029184 | 0.010816 | -0.015714 | -0.069796 | -0.088163 | -0.10143 | 0.46184 | 0.45061 | 0.43633 | 0.42714 | 0.40469 | 0.38429 | 0.37306 | 0.34755 | 0.3302 | 0.31184 | 0.27102 | 0.24449 | 0.21184 | 0.43633 | 0.41388 | 0.38837 | 0.3598 | 0.33122 | 0.29551 | 0.2649 | 0.22306 | 0.18939 | 0.15878
|  | TYNDRUM | HT |  |  |  |  | 0.17612 | 0.1751 | 0.15878 | 0.14347 | 0.12714 | 0.11184 | 0.093469 | 0.066939 | 0.057755 | 0.032245 | -0.049388 | -0.089184 | -0.10449 | 0.4649 | 0.46184 | 0.45469 | 0.44551 | 0.43327 | 0.42408 | 0.41082 | 0.39041 | 0.38224 | 0.36592 | 0.29857 | 0.26796 | 0.25673 | 0.45367 | 0.44551 | 0.4302 | 0.42102 | 0.40367 | 0.38429 | 0.3649 | 0.33633 | 0.31388 | 0.29245
|  | TYNDRUM | HE |  |  |  |  | 0.1751 | 0.17306 | 0.15776 | 0.14653 | 0.13122 | 0.12 | 0.097551 | 0.072041 | 0.059796 | 0.034286 | -0.11163 | -0.22082 | -0.22592 | 0.46388 | 0.46082 | 0.44347 | 0.42918 | 0.4098 | 0.38939 | 0.3649 | 0.33224 | 0.30367 | 0.27 | 0.10878 | 0.033265 | 0.027143 | 0.44143 | 0.41694 | 0.38837 | 0.35673 | 0.32408 | 0.28633 | 0.24041 | 0.18122 | 0.13122 | 0.072041
|  | TYNDRUM | CF |  |  |  |  | 0.18122 | 0.17714 | 0.16694 | 0.15673 | 0.14857 | 0.13939 | 0.12612 | 0.1149 | 0.099592 | 0.082245 | 0.0036735 | -0.11163 | -0.26265 | 0.46184 | 0.46082 | 0.45469 | 0.44551 | 0.43429 | 0.42102 | 0.40469 | 0.38531 | 0.3649 | 0.34449 | 0.21898 | 0.096531 | -0.0014286 | 0.43939 | 0.43939 | 0.42306 | 0.39959 | 0.37612 | 0.35163 | 0.3251 | 0.28837 | 0.25571 | 0.21898
| DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | NO | 1.131 | 1.2523 | 1.2013 | 1.14 | 1.0645 | 1.0115 | 0.93084 | 0.84207 | 0.72982 | 0.62574 | 0.57574 | 0.36146 | 0.28391 | 0.036457 | 1.3007 | 1.2681 | 1.2324 | 1.1803 | 1.1497 | 1.0946 | 1.0385 | 0.96401 | 0.89258 | 0.86809 | 0.71299 | 0.74998 | 0.49283 | 1.2183 | 1.1755 | 1.1173 | 1.0469 | 0.99488 | 0.91732 | 0.83263 | 0.72753 | 0.62855 | 0.58263
|  | UIG | EE |  |  |  |  | 1.2523 | 1.2013 | 1.14 | 1.0645 | 1.0115 | 0.93084 | 0.84207 | 0.72982 | 0.62574 | 0.57574 | 0.36146 | 0.32268 | 0.071151 | 1.3007 | 1.2681 | 1.2324 | 1.1803 | 1.1497 | 1.0946 | 1.0385 | 0.96401 | 0.89258 | 0.86809 | 0.71299 | 0.74998 | 0.63365 | 1.2183 | 1.1755 | 1.1173 | 1.0469 | 0.99488 | 0.91732 | 0.83263 | 0.72753 | 0.62855 | 0.58263
|  | UIG | HT |  |  |  |  | 1.2839 | 1.2359 | 1.1757 | 1.1319 | 1.0788 | 1.0125 | 0.93595 | 0.87574 | 0.79513 | 0.71962 | 0.42676 | 0.28391 | 0.036457 | 1.3222 | 1.2956 | 1.2599 | 1.2354 | 1.2069 | 1.163 | 1.115 | 1.0803 | 1.0314 | 0.98442 | 0.79666 | 0.82651 | 0.81222 | 1.2469 | 1.2071 | 1.152 | 1.1081 | 1.0581 | 0.99386 | 0.92447 | 0.86834 | 0.79283 | 0.71937
|  | UIG | HE |  |  |  |  | 1.2808 | 1.2431 | 1.1962 | 1.1615 | 1.1206 | 1.0686 | 0.99819 | 0.95125 | 0.88187 | 0.81452 | 0.47268 | 0.38084 | 0.14564 | 1.3201 | 1.2956 | 1.2671 | 1.2426 | 1.2201 | 1.1814 | 1.1354 | 1.1038 | 1.0569 | 1.013 | 0.7834 | 0.78773 | 0.68467 | 1.2449 | 1.2153 | 1.1704 | 1.1367 | 1.0969 | 1.0469 | 0.98263 | 0.93467 | 0.86732 | 0.80712
|  | UIG | CF |  |  |  |  | 1.29 | 1.2492 | 1.2166 | 1.188 | 1.1462 | 1.1094 | 1.0645 | 1.0094 | 0.98289 | 0.93391 | 0.67472 | 0.48901 | 0.15278 | 1.3232 | 1.3007 | 1.2793 | 1.263 | 1.2344 | 1.213 | 1.1783 | 1.1375 | 1.1212 | 1.0834 | 0.86809 | 0.76018 | 0.49283 | 1.2541 | 1.2214 | 1.1918 | 1.1643 | 1.1265 | 1.0928 | 1.0479 | 0.99488 | 0.97141 | 0.92345
| GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | NO | NO | 0.139 | -0.25816 | -0.30408 | -0.35102 | 3.7959 | 3.7449 | 3.6888 | 3.6143 | 3.548 | 3.4704 | 3.399 | 3.2071 | 3.1327 | -1.0929 | 0.34796 | 0.31429 | 4.4796 | 4.4367 | 4.4051 | 4.3602 | 4.3031 | 4.2551 | 4.1969 | 4.1439 | 4.0163 | -0.23061 | -0.24592 | -0.47143 | 3.6786 | 3.6184 | 3.5449 | 3.4908 | 3.4184 | 3.3204 | 3.2429 | 3.1429 | 3.0541
|  | ULLAPOOL | EE |  |  |  |  | -0.25816 | -0.30408 | -0.35102 | 3.7959 | 3.7449 | 3.6888 | 3.6143 | 3.548 | 3.4704 | 3.399 | 3.2071 | 3.1663 | -1.0571 | 0.34796 | 0.31429 | 4.4796 | 4.4367 | 4.4051 | 4.3602 | 4.3031 | 4.2551 | 4.1969 | 4.1439 | 4.0163 | -0.2102 | -0.23367 | -0.47143 | 3.6786 | 3.6184 | 3.5449 | 3.4908 | 3.4184 | 3.3204 | 3.2429 | 3.1429 | 3.0541
|  | ULLAPOOL | HT |  |  |  |  | -0.2398 | -0.28367 | -0.32245 | 3.8306 | 3.7867 | 3.7337 | 3.6847 | 3.6245 | 3.5643 | 3.501 | 3.2633 | 3.1327 | -1.0929 | 0.37041 | 0.34286 | 4.5204 | 4.4837 | 4.4571 | 4.4153 | 4.3878 | 4.3418 | 4.2949 | 4.2469 | 4.0571 | -0.23061 | -0.24592 | -0.43469 | 3.7194 | 3.6796 | 3.6194 | 3.5724 | 3.5051 | 3.4561 | 3.3806 | 3.3041 | 3.2204
|  | ULLAPOOL | HE |  |  |  |  | -0.24184 | -0.27245 | -0.30612 | 3.8592 | 3.8265 | 3.7847 | 3.7418 | 3.6847 | 3.6306 | 3.5735 | 3.2571 | 3.1531 | -1.0582 | 0.36837 | 0.34388 | 4.5245 | 4.4939 | 4.4714 | 4.4388 | 4.4122 | 4.3663 | 4.3296 | 4.2847 | 4.0816 | -0.17959 | -0.18776 | -0.43571 | 3.7276 | 3.6929 | 3.6459 | 3.6071 | 3.5541 | 3.5122 | 3.4388 | 3.3776 | 3.3031
|  | ULLAPOOL | CF |  |  |  |  | -0.23776 | -0.26429 | -0.29592 | 3.8786 | 3.851 | 3.8153 | 3.7806 | 3.749 | 3.7112 | 3.6765 | 3.4888 | 3.3102 | -1.0551 | 0.37449 | 0.35204 | 4.5316 | 4.5143 | 4.4969 | 4.4714 | 4.4439 | 4.4255 | 4.3969 | 4.3694 | 4.2224 | -0.12449 | -0.20612 | -0.42959 | 3.7418 | 3.7031 | 3.6776 | 3.6459 | 3.6051 | 3.5592 | 3.5276 | 3.4827 | 3.4378
| SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | 0.639 | -0.61367 | -0.63612 | -0.66469 | -0.69531 | -0.73204 | -0.76776 | -0.80143 | -0.84429 | -0.89633 | -0.94531 | -1.0688 | -1.1106 | -1.1178 | 0.038367 | 0.013878 | -0.010612 | -0.034082 | -0.070816 | -0.11163 | -0.1351 | -0.1851 | -0.22388 | -0.26265 | -0.36163 | -0.40041 | -0.50857 | -0.3902 | -0.41673 | -0.44327 | -0.47286 | -0.50653 | -0.54122 | -0.57592 | -0.64224 | -0.69531 | -0.74531
|  | UNST | EE |  |  |  |  | -0.61367 | -0.63612 | -0.66469 | -0.69531 | -0.73204 | -0.76776 | -0.80143 | -0.84429 | -0.89633 | -0.94531 | -1.0688 | -1.0861 | -1.1004 | 0.038367 | 0.013878 | -0.010612 | -0.034082 | -0.070816 | -0.11163 | -0.1351 | -0.1851 | -0.22388 | -0.26265 | -0.36163 | -0.40041 | -0.46673 | -0.3902 | -0.41673 | -0.44327 | -0.47286 | -0.50653 | -0.54122 | -0.57592 | -0.64224 | -0.69531 | -0.74531
|  | UNST | HT |  |  |  |  | -0.60245 | -0.62184 | -0.64633 | -0.6749 | -0.70041 | -0.73408 | -0.76265 | -0.80143 | -0.8351 | -0.86061 | -1.0229 | -1.1106 | -1.1178 | 0.056735 | 0.042449 | 0.022041 | -0.0034694 | -0.018776 | -0.047347 | -0.070816 | -0.10449 | -0.1402 | -0.15959 | -0.30653 | -0.36776 | -0.37082 | -0.38 | -0.40347 | -0.42592 | -0.45347 | -0.47592 | -0.50653 | -0.53204 | -0.56673 | -0.60143 | -0.6249
|  | UNST | HE |  |  |  |  | -0.60245 | -0.61878 | -0.63612 | -0.66163 | -0.68204 | -0.70959 | -0.73918 | -0.77592 | -0.81061 | -0.8402 | -1.0106 | -1.0555 | -1.0749 | 0.056735 | 0.042449 | 0.027143 | 0.0016327 | -0.0085714 | -0.035102 | -0.05551 | -0.089184 | -0.1249 | -0.1351 | -0.28612 | -0.34735 | -0.40347 | -0.38 | -0.39837 | -0.41673 | -0.44224 | -0.45959 | -0.48612 | -0.51367 | -0.54735 | -0.58102 | -0.60755
|  | UNST | CF |  |  |  |  | -0.60347 | -0.61469 | -0.63 | -0.64633 | -0.66673 | -0.67694 | -0.69735 | -0.71367 | -0.73612 | -0.75551 | -0.85449 | -0.97388 | -1.0463 | 0.059796 | 0.049592 | 0.032245 | 0.01898 | 0.00061224 | -0.010612 | -0.033061 | -0.051429 | -0.074898 | -0.098367 | -0.21469 | -0.36469 | -0.50857 | -0.37592 | -0.3902 | -0.40245 | -0.41571 | -0.43306 | -0.44122 | -0.45959 | -0.4749 | -0.49327 | -0.51265
| SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 0.196 | 6.3196 | 6.24 | 6.1584 | 6.0665 | 5.9461 | 5.8471 | 5.6982 | 5.5339 | 5.3808 | 5.2798 | 4.9308 | 4.8288 | 4.0822 | 6.8261 | 6.772 | 6.721 | 6.6557 | 6.5741 | 6.5088 | 6.4129 | 6.3037 | 6.1996 | 6.1373 | 5.8782 | 6.1147 | 5.6708 | 6.3596 | 6.2882 | 6.2137 | 6.131 | 6.0371 | 5.9596 | 5.8473 | 5.7229 | 5.6106 | 5.5218
|  | VOE | EE |  |  |  |  | 6.3196 | 6.24 | 6.1584 | 6.0665 | 5.9461 | 5.8471 | 5.6982 | 5.5339 | 5.3808 | 5.2798 | 4.9308 | 4.8869 | 4.1353 | 6.8261 | 6.772 | 6.721 | 6.6557 | 6.5741 | 6.5088 | 6.4129 | 6.3037 | 6.1996 | 6.1373 | 5.8782 | 6.1147 | 5.9127 | 6.3596 | 6.2882 | 6.2137 | 6.131 | 6.0371 | 5.9596 | 5.8473 | 5.7229 | 5.6106 | 5.5218
|  | VOE | HT |  |  |  |  | 6.3492 | 6.2829 | 6.2135 | 6.1349 | 6.0584 | 5.9696 | 5.8553 | 5.7298 | 5.6339 | 5.4982 | 5.041 | 4.8288 | 4.0822 | 6.8608 | 6.821 | 6.7782 | 6.7282 | 6.6812 | 6.6231 | 6.5547 | 6.4731 | 6.418 | 6.3343 | 6.0251 | 6.2504 | 6.2371 | 6.3841 | 6.3239 | 6.2596 | 6.1892 | 6.1137 | 6.0351 | 5.9473 | 5.8463 | 5.7678 | 5.6637
|  | VOE | HE |  |  |  |  | 6.3471 | 6.291 | 6.2318 | 6.1676 | 6.1012 | 6.0216 | 5.9237 | 5.8145 | 5.7237 | 5.6155 | 5.1155 | 4.9737 | 4.1924 | 6.8578 | 6.8231 | 6.7904 | 6.7424 | 6.7027 | 6.6476 | 6.5812 | 6.5078 | 6.4527 | 6.3761 | 6.019 | 6.2004 | 6.0086 | 6.3841 | 6.3351 | 6.282 | 6.2239 | 6.1616 | 6.0912 | 6.0035 | 5.9065 | 5.8239 | 5.729
|  | VOE | CF |  |  |  |  | 6.3676 | 6.3237 | 6.2706 | 6.2267 | 6.1645 | 6.1216 | 6.0584 | 5.9869 | 5.9124 | 5.8329 | 5.4614 | 5.1788 | 4.2822 | 6.8669 | 6.8373 | 6.7996 | 6.77 | 6.7271 | 6.6914 | 6.6445 | 6.5873 | 6.5322 | 6.469 | 6.1496 | 6.1382 | 5.6708 | 6.3953 | 6.3586 | 6.3178 | 6.282 | 6.232 | 6.1922 | 6.1402 | 6.0841 | 6.0269 | 5.9637
| DUDHOPE | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | NO | 0.673 | 17.2982 | 16.9084 | 16.0217 | 14.8768 | 14.5523 | 12.3666 | 11.7972 | 11.0482 | 10.1288 | 8.6104 | 2.4533 | -4.8732 | -12.6926 | 18.1472 | 17.9156 | 16.9615 | 15.7431 | 15.5533 | 13.0237 | 12.1829 | 11.2564 | 10.3023 | 8.6043 | 1.1798 | -8.0671 | -18.3038 | 17.7104 | 17.3819 | 16.3676 | 15.0482 | 14.7502 | 12.1125 | 11.5288 | 10.5268 | 9.5013 | 7.7339
|  | WALTON | EE |  |  |  |  | 17.336 | 16.9084 | 16.4962 | 16.0921 | 15.1809 | 13.7982 | 12.9196 | 12.3717 | 11.2309 | 10.4196 | 7.038 | 0.84718 | -3.0467 | 18.2492 | 17.9502 | 17.6676 | 17.3635 | 16.439 | 14.9258 | 14.0921 | 13.6829 | 12.5288 | 11.7676 | 7.9349 | -0.44873 | -5.6498 | 17.7798 | 17.3819 | 16.9962 | 16.6156 | 15.6053 | 14.0033 | 13.0615 | 12.5462 | 11.289 | 10.4349
|  | WALTON | HT |  |  |  |  | 17.2982 | 16.9553 | 16.0217 | 14.8768 | 14.5523 | 12.3666 | 11.7972 | 11.1533 | 10.6176 | 9.936 | 5.7176 | -2.2273 | -9.8202 | 18.1472 | 17.9156 | 16.9615 | 15.7431 | 15.5707 | 13.0431 | 12.6278 | 12.1472 | 11.8023 | 11.2615 | 7.1921 | -1.9181 | -9.9589 | 17.7104 | 17.4217 | 16.3676 | 15.0482 | 14.7502 | 12.1125 | 11.54 | 10.8931 | 10.39 | 9.6951
|  | WALTON | HE |  |  |  |  | 17.4196 | 17.136 | 16.3931 | 15.4064 | 14.8584 | 12.7543 | 11.9482 | 11.0482 | 10.1288 | 8.6104 | 2.4533 | -4.8732 | -12.6926 | 18.2717 | 18.0258 | 17.2196 | 16.1043 | 15.5533 | 13.0237 | 12.1829 | 11.2564 | 10.3023 | 8.6043 | 1.1798 | -8.0671 | -18.3038 | 17.8329 | 17.5829 | 16.7462 | 15.5941 | 14.989 | 12.4329 | 11.5288 | 10.5268 | 9.5013 | 7.7339
|  | WALTON | CF |  |  |  |  | 17.7737 | 17.5951 | 17.4023 | 17.2329 | 16.7472 | 15.9584 | 15.4686 | 15.0574 | 14.636 | 14.1002 | 11.8982 | 9.539 | 6.2707 | 18.6227 | 18.44 | 18.2564 | 18.1033 | 17.5533 | 16.5931 | 15.9849 | 15.4768 | 14.9564 | 14.2931 | 11.3972 | 7.8319 | 2.0951 | 18.1921 | 18.0258 | 17.8421 | 17.6839 | 17.1309 | 16.1992 | 15.6411 | 15.187 | 14.7166 | 14.1104
| INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | NO | 4.971 | 30.1949 | 30.0545 | 29.8554 | 29.6828 | 29.4876 | 29.2472 | 29.0025 | 28.6476 | 28.3212 | 28.0168 | 26.9984 | 26.5522 | 25.1094 | 29.3893 | 29.3235 | 29.2369 | 29.1725 | 29.047 | 28.8744 | 28.6941 | 28.4402 | 28.2056 | 27.9882 | 27.1934 | 27.8636 | 27.7564 | 29.5615 | 29.4802 | 29.3648 | 29.2768 | 29.172 | 29.0268 | 28.7984 | 28.4647 | 28.158 | 27.8714
|  | WATERLOO PLACE | EE |  |  |  |  | 30.1949 | 30.0545 | 29.8554 | 29.6828 | 29.4876 | 29.2472 | 29.0025 | 28.6476 | 28.3212 | 28.0168 | 27.098 | 26.9311 | 25.6027 | 29.3893 | 29.336 | 29.2369 | 29.1725 | 29.047 | 28.8744 | 28.6941 | 28.4402 | 28.2056 | 27.9882 | 27.292 | 28.1555 | 28.1324 | 29.5615 | 29.4855 | 29.3648 | 29.2768 | 29.172 | 29.0268 | 28.7984 | 28.4647 | 28.158 | 27.8714
|  | WATERLOO PLACE | HT |  |  |  |  | 30.2396 | 30.0901 | 29.9737 | 29.8405 | 29.6862 | 29.4136 | 29.1462 | 28.838 | 28.5784 | 28.3202 | 27.2763 | 26.8479 | 25.4167 | 29.4052 | 29.3235 | 29.2831 | 29.2355 | 29.1783 | 29.0287 | 28.8446 | 28.6282 | 28.4402 | 28.2508 | 27.454 | 28.1194 | 28.0165 | 29.5788 | 29.4802 | 29.4182 | 29.348 | 29.2653 | 29.0321 | 28.8234 | 28.607 | 28.4186 | 28.1729
|  | WATERLOO PLACE | HE |  |  |  |  | 30.2329 | 30.1127 | 29.9569 | 29.8184 | 29.653 | 29.44 | 29.2164 | 28.9087 | 28.613 | 28.3038 | 26.9984 | 26.5522 | 25.1094 | 29.4038 | 29.359 | 29.2763 | 29.2249 | 29.1624 | 29.0138 | 28.8484 | 28.6229 | 28.4061 | 28.1772 | 27.1934 | 27.8636 | 27.7564 | 29.5769 | 29.5168 | 29.423 | 29.3547 | 29.273 | 29.1489 | 29.0052 | 28.7114 | 28.4301 | 28.1358
|  | WATERLOO PLACE | CF |  |  |  |  | 30.2713 | 30.2098 | 30.1367 | 30.0155 | 29.9227 | 29.7924 | 29.678 | 29.528 | 29.3563 | 29.1688 | 28.1178 | 27.1605 | 25.146 | 29.4163 | 29.3917 | 29.3629 | 29.2879 | 29.2528 | 29.196 | 29.1552 | 29.0701 | 28.9446 | 28.8051 | 28.0262 | 28.3165 | 27.7948 | 29.5961 | 29.5624 | 29.524 | 29.4422 | 29.3932 | 29.3076 | 29.2547 | 29.1879 | 29.0879 | 28.9643
| LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | YES | 2.858 | 11.1294 | 10.7386 | 10.2672 | 9.7957 | 9.3018 | 8.7906 | 8.5651 | 8.0641 | 7.5825 | 7.1376 | 5.5825 | 5.259 | 4.0916 | 12.5825 | 12.3804 | 12.1263 | 11.8845 | 11.6141 | 11.3376 | 11.2733 | 11.0039 | 10.7427 | 10.4967 | 9.5182 | 9.6493 | 7.3391 | 12.3085 | 11.9677 | 11.5442 | 11.1207 | 10.6636 | 10.1881 | 10.0228 | 9.5432 | 9.084 | 8.6687
|  | WEST KIRKTON | EE |  |  |  |  | 11.1294 | 10.7386 | 10.2672 | 9.7957 | 9.3018 | 8.7906 | 8.5651 | 8.0641 | 7.5825 | 7.1376 | 5.5825 | 5.7202 | 4.6131 | 12.5825 | 12.3804 | 12.1263 | 11.8845 | 11.6141 | 11.3376 | 11.2733 | 11.0039 | 10.7427 | 10.4967 | 9.5182 | 9.6493 | 8.7605 | 12.3085 | 11.9677 | 11.5442 | 11.1207 | 10.6636 | 10.1881 | 10.0228 | 9.5432 | 9.084 | 8.6687
|  | WEST KIRKTON | HT |  |  |  |  | 11.207 | 10.8182 | 10.3835 | 9.9253 | 9.4723 | 9.0865 | 8.6274 | 8.1427 | 7.6702 | 7.5457 | 5.6702 | 5.259 | 4.0916 | 12.6478 | 12.46 | 12.257 | 12.0355 | 11.8192 | 11.6335 | 11.4161 | 11.1702 | 10.9335 | 10.9498 | 10.0294 | 10.3666 | 10.3432 | 12.3728 | 12.0575 | 11.6993 | 11.3115 | 10.9075 | 10.5585 | 10.1381 | 9.6809 | 9.2371 | 9.1697
|  | WEST KIRKTON | HE |  |  |  |  | 11.2202 | 10.9621 | 10.6294 | 10.2978 | 9.9621 | 9.6651 | 9.3029 | 8.9294 | 8.56 | 8.5274 | 7.0284 | 6.1814 | 4.9518 | 12.6437 | 12.5008 | 12.3161 | 12.1437 | 11.957 | 11.7906 | 11.5906 | 11.3753 | 11.159 | 11.1794 | 10.16 | 9.8891 | 8.9636 | 12.384 | 12.184 | 11.8993 | 11.6166 | 11.3156 | 11.0411 | 10.7034 | 10.3442 | 9.9932 | 9.9983
|  | WEST KIRKTON | CF |  |  |  |  | 11.3018 | 11.158 | 10.9682 | 10.7651 | 10.5478 | 10.3559 | 10.2049 | 9.9988 | 9.8345 | 9.659 | 8.9855 | 7.5508 | 5.1263 | 12.6794 | 12.5865 | 12.4631 | 12.3437 | 12.207 | 12.0733 | 11.9488 | 11.7835 | 11.6406 | 11.4855 | 10.7794 | 9.7258 | 7.3391 | 12.4564 | 12.3462 | 12.186 | 12.0136 | 11.8177 | 11.632 | 11.4881 | 11.283 | 11.1146 | 10.935
| KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | 0 | 0.087388 | 0.087388 | 0.086367 | 0.078204 | 0.078204 | 0.070041 | 0.068 | 0.068 | 0.06698 | 0.065959 | 0.065959 | 0.061878 | 0.052878 | 0.090633 | 0.090633 | 0.089612 | 0.081449 | 0.081449 | 0.074306 | 0.076347 | 0.073286 | 0.073286 | 0.074306 | 0.077367 | 0.076765 | 0.075745 | 0.090031 | 0.090031 | 0.08901 | 0.080847 | 0.080847 | 0.072684 | 0.070643 | 0.071663 | 0.070643 | 0.068602
|  | WESTER DRUMMOND | EE |  |  |  |  | 0.087388 | 0.087388 | 0.086367 | 0.078204 | 0.078204 | 0.070041 | 0.068 | 0.073102 | 0.068 | 0.06698 | 0.065959 | 0.065959 | 0.053898 | 0.090633 | 0.090633 | 0.089612 | 0.081449 | 0.081449 | 0.074306 | 0.076347 | 0.080429 | 0.077367 | 0.077367 | 0.077367 | 0.081867 | 0.077786 | 0.090031 | 0.090031 | 0.08901 | 0.080847 | 0.080847 | 0.072684 | 0.070643 | 0.075745 | 0.070643 | 0.069622
|  | WESTER DRUMMOND | HT |  |  |  |  | 0.094531 | 0.094531 | 0.087388 | 0.085347 | 0.085347 | 0.077184 | 0.077184 | 0.068 | 0.06698 | 0.065959 | 0.068 | 0.061878 | 0.052878 | 0.097776 | 0.097776 | 0.090633 | 0.088592 | 0.088592 | 0.081449 | 0.081449 | 0.073286 | 0.073286 | 0.075327 | 0.077367 | 0.077786 | 0.077786 | 0.097173 | 0.097173 | 0.090031 | 0.08799 | 0.08799 | 0.079827 | 0.079827 | 0.071663 | 0.070643 | 0.068602
|  | WESTER DRUMMOND | HE |  |  |  |  | 0.094531 | 0.094531 | 0.087388 | 0.087388 | 0.085347 | 0.079224 | 0.078204 | 0.06902 | 0.06902 | 0.06698 | 0.06902 | 0.063918 | 0.054918 | 0.097776 | 0.097776 | 0.090633 | 0.089612 | 0.088592 | 0.081449 | 0.081449 | 0.074306 | 0.074306 | 0.075327 | 0.077367 | 0.079827 | 0.077786 | 0.097173 | 0.097173 | 0.090031 | 0.090031 | 0.08799 | 0.081867 | 0.080847 | 0.071663 | 0.071663 | 0.069622
|  | WESTER DRUMMOND | CF |  |  |  |  | 0.096571 | 0.094531 | 0.087388 | 0.087388 | 0.087388 | 0.086367 | 0.078204 | 0.078204 | 0.071061 | 0.071061 | 0.06902 | 0.064939 | 0.055939 | 0.097776 | 0.097776 | 0.090633 | 0.090633 | 0.090633 | 0.089612 | 0.081449 | 0.081449 | 0.074306 | 0.074306 | 0.078388 | 0.076765 | 0.075745 | 0.098194 | 0.097173 | 0.090031 | 0.090031 | 0.090031 | 0.08901 | 0.080847 | 0.080847 | 0.073704 | 0.073704
| THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | NO | 0.079 | -0.89388 | -0.92143 | -0.94388 | -0.98061 | -1.0071 | -1.0449 | -1.0694 | -1.1184 | -1.1612 | -1.2 | -1.2837 | -1.3112 | -1.3235 | -0.44184 | -0.46122 | -0.47551 | -0.5051 | -0.52347 | -0.55408 | -0.56531 | -0.6051 | -0.63469 | -0.66429 | -0.72959 | -0.75102 | -0.82347 | -0.61633 | -0.64388 | -0.66429 | -0.70408 | -0.72959 | -0.77041 | -0.79286 | -0.84592 | -0.88878 | -0.92857
|  | WESTRAY | EE |  |  |  |  | -0.89388 | -0.92143 | -0.94388 | -0.98061 | -1.0071 | -1.0449 | -1.0694 | -1.1184 | -1.1612 | -1.2 | -1.2837 | -1.299 | -1.3112 | -0.44184 | -0.46122 | -0.47551 | -0.5051 | -0.52347 | -0.55408 | -0.56531 | -0.6051 | -0.63469 | -0.66429 | -0.72959 | -0.75102 | -0.78469 | -0.61633 | -0.64388 | -0.66429 | -0.70408 | -0.72959 | -0.77041 | -0.79286 | -0.84592 | -0.88878 | -0.92857
|  | WESTRAY | HT |  |  |  |  | -0.87755 | -0.89796 | -0.91837 | -0.95 | -0.96531 | -0.9949 | -1.0194 | -1.0561 | -1.0949 | -1.1092 | -1.2571 | -1.3112 | -1.3235 | -0.42755 | -0.4398 | -0.4551 | -0.47755 | -0.48469 | -0.50714 | -0.52245 | -0.55102 | -0.58163 | -0.58469 | -0.6949 | -0.72959 | -0.74082 | -0.59796 | -0.61837 | -0.63776 | -0.67143 | -0.68367 | -0.71531 | -0.7398 | -0.78061 | -0.81837 | -0.83163
|  | WESTRAY | HE |  |  |  |  | -0.87755 | -0.8949 | -0.91122 | -0.93571 | -0.94796 | -0.97347 | -0.99592 | -1.0296 | -1.0622 | -1.0745 | -1.2337 | -1.2724 | -1.2816 | -0.42653 | -0.43776 | -0.45 | -0.47245 | -0.47857 | -0.49898 | -0.51327 | -0.54184 | -0.56633 | -0.57245 | -0.69286 | -0.73163 | -0.76327 | -0.59694 | -0.61429 | -0.63163 | -0.65714 | -0.66939 | -0.69592 | -0.71837 | -0.7551 | -0.78878 | -0.8
|  | WESTRAY | CF |  |  |  |  | -0.87857 | -0.89082 | -0.90612 | -0.92143 | -0.94388 | -0.95306 | -0.97551 | -0.98878 | -1.0122 | -1.0367 | -1.1306 | -1.2316 | -1.2724 | -0.42653 | -0.43673 | -0.44898 | -0.4602 | -0.47755 | -0.48163 | -0.49898 | -0.51122 | -0.53163 | -0.55102 | -0.62959 | -0.73571 | -0.82347 | -0.59694 | -0.60918 | -0.62755 | -0.64184 | -0.66735 | -0.67347 | -0.69694 | -0.71327 | -0.73776 | -0.76224
| TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | NO | 1.11 | 3.2973 | 3.0391 | 2.7626 | 2.4575 | 2.1187 | 1.834 | 1.4769 | 1.0942 | 0.73505 | 0.74219 | -0.055767 | -0.3272 | -0.82209 | 4.8167 | 4.6463 | 4.4738 | 4.2667 | 4.031 | 3.8493 | 3.6095 | 3.3534 | 3.1116 | 3.2146 | 2.6789 | 2.6238 | 1.7667 | 4.1259 | 3.8861 | 3.6432 | 3.3585 | 3.0422 | 2.7963 | 2.4595 | 2.085 | 1.735 | 1.7963
|  | WHITEHOUSE | EE |  |  |  |  | 3.2973 | 3.0391 | 2.7626 | 2.4575 | 2.1187 | 1.834 | 1.4769 | 1.0942 | 0.73505 | 0.74219 | -0.055767 | -0.22107 | -0.68128 | 4.8167 | 4.6463 | 4.4738 | 4.2667 | 4.031 | 3.8493 | 3.6095 | 3.3534 | 3.1116 | 3.2146 | 2.6789 | 2.6238 | 2.2534 | 4.1259 | 3.8861 | 3.6432 | 3.3585 | 3.0422 | 2.7963 | 2.4595 | 2.085 | 1.735 | 1.7963
|  | WHITEHOUSE | HT |  |  |  |  | 3.3534 | 3.1024 | 2.831 | 2.5483 | 2.2646 | 1.9871 | 1.7167 | 1.4697 | 1.1922 | 0.9126 | 0.15036 | -0.3272 | -0.82209 | 4.8585 | 4.7095 | 4.5412 | 4.3585 | 4.1728 | 4.0065 | 3.8463 | 3.6973 | 3.5289 | 3.3514 | 2.9473 | 2.8902 | 2.8381 | 4.184 | 3.9708 | 3.7289 | 3.4657 | 3.2044 | 2.9504 | 2.7024 | 2.4708 | 2.2136 | 1.9483
|  | WHITEHOUSE | HE |  |  |  |  | 3.3585 | 3.1595 | 2.9534 | 2.732 | 2.5146 | 2.2799 | 2.0218 | 1.7932 | 1.5432 | 1.2881 | 0.26872 | -0.034339 | -0.49148 | 4.8626 | 4.731 | 4.5963 | 4.4391 | 4.2891 | 4.1248 | 3.9463 | 3.7983 | 3.6279 | 3.4524 | 2.8697 | 2.7402 | 2.383 | 4.1902 | 4.0116 | 3.834 | 3.6299 | 3.433 | 3.2126 | 2.9738 | 2.7636 | 2.5269 | 2.2871
|  | WHITEHOUSE | CF |  |  |  |  | 3.3953 | 3.2473 | 3.0861 | 2.9289 | 2.7463 | 2.5973 | 2.4238 | 2.232 | 2.0504 | 1.9085 | 0.93913 | 0.47995 | -0.40373 | 4.8902 | 4.7942 | 4.6912 | 4.5861 | 4.4585 | 4.3555 | 4.2248 | 4.0759 | 3.9381 | 3.835 | 3.0279 | 2.6861 | 1.7667 | 4.2228 | 4.0871 | 3.9453 | 3.7973 | 3.6248 | 3.4932 | 3.3248 | 3.134 | 2.9565 | 2.8402
| PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | NO | 6.667 | 2.2558 | 1.7354 | 1.1201 | 0.49051 | -0.23806 | -1.0207 | -1.736 | -2.6289 | -3.2717 | -4.085 | -7.8707 | -10.5483 | -12.8503 | 3.9507 | 3.6834 | 3.3538 | 3.0334 | 2.6528 | 2.2415 | 2.066 | 1.6221 | 1.1926 | 0.78235 | -1.0044 | -2.1549 | -3.8641 | 3.1349 | 2.6982 | 2.1625 | 1.6196 | 0.9849 | 0.29511 | -0.20081 | -0.9753 | -1.609 | -2.309
|  | WHITESTRIPES | EE |  |  |  |  | 2.2558 | 1.7354 | 1.1201 | 0.49051 | -0.23806 | -1.0207 | -1.5615 | -2.4238 | -3.2717 | -4.085 | -7.6462 | -10.4299 | -12.8013 | 3.9507 | 3.6834 | 3.3538 | 3.0334 | 2.6528 | 2.2415 | 2.066 | 1.6221 | 1.1926 | 0.78235 | -1.0044 | -2.1549 | -3.5886 | 3.1349 | 2.6982 | 2.1625 | 1.6196 | 0.9849 | 0.29511 | -0.11 | -0.86918 | -1.609 | -2.309
|  | WHITESTRIPES | HT |  |  |  |  | 2.3221 | 1.7966 | 1.213 | 0.55786 | -0.11663 | -0.87785 | -1.736 | -2.6289 | -3.183 | -4.0197 | -7.8707 | -10.5483 | -12.8503 | 4.0221 | 3.7732 | 3.4987 | 3.1834 | 2.8752 | 2.5119 | 2.1089 | 1.6711 | 1.5048 | 1.1191 | -0.68806 | -1.4998 | -2.2304 | 3.2216 | 2.7818 | 2.3012 | 1.7461 | 1.1798 | 0.53082 | -0.20081 | -0.9753 | -1.4039 | -2.1304
|  | WHITESTRIPES | HE |  |  |  |  | 2.3415 | 1.9721 | 1.5497 | 1.0538 | 0.53847 | -0.061527 | -0.69418 | -1.3615 | -1.6932 | -2.3044 | -5.7176 | -8.6421 | -11.4299 | 4.017 | 3.8201 | 3.5946 | 3.3283 | 3.0681 | 2.7558 | 2.4191 | 2.0568 | 1.9579 | 1.6293 | -0.21867 | -1.4702 | -3.0539 | 3.2329 | 2.9257 | 2.5737 | 2.1502 | 1.7176 | 1.2022 | 0.65531 | 0.065514 | -0.15591 | -0.68449
|  | WHITESTRIPES | CF |  |  |  |  | 2.4252 | 2.1477 | 1.8017 | 1.4466 | 1.0252 | 0.5997 | 0.21602 | -0.20234 | -0.61153 | -1.033 | -3.236 | -6.2789 | -9.9248 | 4.0528 | 3.8936 | 3.6915 | 3.4966 | 3.2579 | 3.0272 | 2.7824 | 2.514 | 2.2487 | 1.9752 | 0.65072 | -1.161 | -3.8641 | 3.3074 | 3.0788 | 2.7839 | 2.4951 | 2.1369 | 1.7798 | 1.4492 | 1.0818 | 0.72062 | 0.35021
| CARRADALE 1 | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 0.44 | 5.0602 | 4.9816 | 4.9031 | 4.8306 | 4.7357 | 4.6418 | 4.5214 | 4.4194 | 4.2959 | 4.1847 | 3.9153 | 3.8235 | 3.802 | 5.7765 | 5.7224 | 5.6765 | 5.6327 | 5.5684 | 5.5041 | 5.4265 | 5.3622 | 5.2786 | 5.2041 | 5.0163 | 4.949 | 4.7694 | 5.3745 | 5.299 | 5.2255 | 5.1582 | 5.0684 | 4.9796 | 4.8612 | 4.7684 | 4.6469 | 4.5418
|  | WHITING BAY | EE |  |  |  |  | 5.0602 | 4.9816 | 4.9031 | 4.8306 | 4.7357 | 4.6418 | 4.5214 | 4.4194 | 4.2959 | 4.1847 | 3.9153 | 3.8786 | 3.849 | 5.7765 | 5.7224 | 5.6765 | 5.6327 | 5.5684 | 5.5041 | 5.4265 | 5.3622 | 5.2786 | 5.2041 | 5.0163 | 4.949 | 4.8398 | 5.3745 | 5.299 | 5.2255 | 5.1582 | 5.0684 | 4.9796 | 4.8612 | 4.7684 | 4.6469 | 4.5418
|  | WHITING BAY | HT |  |  |  |  | 5.0857 | 5.0245 | 4.9663 | 4.9031 | 4.8265 | 4.7643 | 4.6776 | 4.5806 | 4.4837 | 4.3786 | 4.001 | 3.8235 | 3.802 | 5.798 | 5.7622 | 5.7296 | 5.6918 | 5.6459 | 5.6102 | 5.5541 | 5.4939 | 5.4306 | 5.3612 | 5.1092 | 5.001 | 4.9908 | 5.402 | 5.3429 | 5.2888 | 5.2286 | 5.1561 | 5.1 | 5.0163 | 4.9255 | 4.8316 | 4.7347
|  | WHITING BAY | HE |  |  |  |  | 5.0857 | 5.0357 | 4.9949 | 4.9459 | 4.8847 | 4.8408 | 4.7633 | 4.6796 | 4.5949 | 4.5071 | 4.0888 | 3.9816 | 3.9663 | 5.798 | 5.7643 | 5.7367 | 5.7061 | 5.6653 | 5.6367 | 5.5867 | 5.5306 | 5.4704 | 5.4133 | 5.1378 | 5.0245 | 4.9306 | 5.402 | 5.352 | 5.3133 | 5.2684 | 5.2082 | 5.1673 | 5.0939 | 5.0163 | 4.9347 | 4.85
|  | WHITING BAY | CF |  |  |  |  | 5.0949 | 5.0561 | 5.0204 | 4.9745 | 4.9357 | 4.8857 | 4.85 | 4.7888 | 4.7398 | 4.6806 | 4.398 | 4.1235 | 3.9857 | 5.8041 | 5.7786 | 5.7571 | 5.7235 | 5.698 | 5.6622 | 5.6398 | 5.5918 | 5.5571 | 5.5143 | 5.2918 | 5.0194 | 4.7694 | 5.4092 | 5.3735 | 5.3388 | 5.2949 | 5.2571 | 5.2092 | 5.1776 | 5.1163 | 5.0684 | 5.0102
| MYBSTER 1 | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | NO | 2.666 | 5.4181 | 5.0466 | 4.6109 | 4.1334 | 3.6548 | 3.1915 | 2.5742 | 2.1568 | 1.6446 | 1.0936 | -0.81458 | -1.9932 | -2.2085 | 7.8936 | 7.6507 | 7.3426 | 6.9844 | 6.662 | 6.3609 | 6.0181 | 5.8834 | 5.5834 | 5.3038 | 4.3099 | 3.6252 | 2.7885 | 6.5844 | 6.2324 | 5.8089 | 5.365 | 4.9048 | 4.463 | 3.8844 | 3.6038 | 3.0895 | 2.5813
|  | WICK | EE |  |  |  |  | 5.4181 | 5.0466 | 4.6109 | 4.1375 | 3.6548 | 3.1915 | 2.5742 | 2.2364 | 1.6528 | 1.0936 | -0.81458 | -1.8156 | -2.0523 | 7.8936 | 7.6507 | 7.3426 | 6.9936 | 6.662 | 6.3609 | 6.0181 | 5.8834 | 5.5834 | 5.3038 | 4.3099 | 3.6252 | 2.963 | 6.5844 | 6.2324 | 5.8089 | 5.365 | 4.9048 | 4.463 | 3.8844 | 3.6262 | 3.0895 | 2.5813
|  | WICK | HT |  |  |  |  | 5.4364 | 5.0681 | 4.6232 | 4.1334 | 3.6915 | 3.2701 | 2.7273 | 2.1568 | 1.6446 | 1.415 | -0.73907 | -1.9932 | -2.2085 | 7.9089 | 7.6732 | 7.3548 | 6.9844 | 6.6752 | 6.4364 | 6.1752 | 5.9017 | 5.664 | 5.616 | 4.6415 | 4.1079 | 4.016 | 6.6262 | 6.2895 | 5.8711 | 5.4191 | 4.9997 | 4.6222 | 4.1293 | 3.6038 | 3.1293 | 2.9681
|  | WICK | HE |  |  |  |  | 5.4752 | 5.216 | 4.9181 | 4.5824 | 4.2568 | 3.9834 | 3.5844 | 3.1487 | 2.7293 | 2.5722 | 0.46705 | -0.61866 | -0.96968 | 7.9405 | 7.7497 | 7.5099 | 7.2222 | 6.9609 | 6.7558 | 6.5181 | 6.2732 | 6.0415 | 5.9885 | 4.8681 | 4.1364 | 3.4487 | 6.664 | 6.4181 | 6.1303 | 5.812 | 5.4946 | 5.2354 | 4.864 | 4.4558 | 4.0671 | 3.9691
|  | WICK | CF |  |  |  |  | 5.6538 | 5.466 | 5.2507 | 5.0252 | 4.815 | 4.5834 | 4.365 | 4.1609 | 3.9099 | 3.6548 | 2.5681 | 1.2089 | 0.10583 | 8.0926 | 7.9528 | 7.7813 | 7.6017 | 7.4303 | 7.2395 | 7.0589 | 6.8956 | 6.714 | 6.5252 | 5.6742 | 4.3773 | 2.7885 | 6.8364 | 6.6609 | 6.4497 | 6.2303 | 6.0324 | 5.8038 | 5.5844 | 5.3875 | 5.1497 | 4.9068
| WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 5.811 | 3.6397 | 3.1478 | 2.5856 | 1.9499 | 1.2213 | 0.82131 | -0.37461 | -1.6613 | -2.9011 | -4.0736 | -9.5358 | -13.1338 | -14.9603 | 5.2407 | 5.0519 | 4.7989 | 4.4213 | 3.956 | 3.6784 | 3.0733 | 2.3182 | 1.6325 | 0.98661 | -1.7399 | -3.1797 | -5.0338 | 5.1478 | 4.707 | 4.1325 | 3.4917 | 2.7989 | 2.2325 | 1.2142 | 0.065184 | -0.99094 | -1.9716
|  | WOODHILL | EE |  |  |  |  | 3.6397 | 3.1478 | 2.5856 | 1.9499 | 1.2213 | 0.82131 | -0.37461 | -1.6613 | -2.9011 | -4.0736 | -9.246 | -12.7552 | -14.7716 | 5.2407 | 5.0519 | 4.7989 | 4.4213 | 3.956 | 3.6784 | 3.0733 | 2.3182 | 1.6325 | 0.98661 | -1.7399 | -3.1797 | -5.0338 | 5.1478 | 4.707 | 4.1325 | 3.4917 | 2.7989 | 2.2325 | 1.2142 | 0.065184 | -0.99094 | -1.9716
|  | WOODHILL | HT |  |  |  |  | 3.804 | 3.2866 | 2.7621 | 2.206 | 1.6601 | 1.056 | -0.15522 | -1.1491 | -2.3226 | -3.5511 | -9.5358 | -13.1338 | -14.9603 | 5.3336 | 5.1887 | 5.0193 | 4.7356 | 4.4611 | 4.1417 | 3.5836 | 3.0968 | 2.4815 | 1.8417 | -1.1052 | -1.9583 | -2.3767 | 5.3284 | 4.9376 | 4.454 | 3.9305 | 3.4172 | 2.8193 | 1.758 | 0.85702 | -0.22155 | -1.3267
|  | WOODHILL | HE |  |  |  |  | 3.7846 | 3.4887 | 3.1805 | 2.8407 | 2.5121 | 2.0764 | 1.3591 | 0.74784 | -0.144 | -1.0991 | -6.0818 | -9.0889 | -11.6154 | 5.3233 | 5.1856 | 5.0499 | 4.8376 | 4.5295 | 4.1744 | 3.7284 | 3.2591 | 2.6713 | 2.0601 | -0.96237 | -1.8409 | -3.5726 | 5.305 | 4.9805 | 4.6621 | 4.2417 | 3.7662 | 3.2223 | 2.4223 | 1.6417 | 0.78559 | -0.10624
|  | WOODHILL | CF |  |  |  |  | 3.8846 | 3.7366 | 3.5703 | 3.3754 | 3.156 | 2.9346 | 2.6703 | 2.3203 | 1.9478 | 1.6846 | -1.0409 | -4.3328 | -8.2828 | 5.3662 | 5.2897 | 5.2019 | 5.0958 | 4.9784 | 4.8233 | 4.5846 | 4.2713 | 3.9876 | 3.7907 | 1.7927 | -0.68992 | -4.9971 | 5.4254 | 5.256 | 5.0682 | 4.8478 | 4.6029 | 4.3407 | 4.0152 | 3.5601 | 3.1468 | 2.8611

## Primary Headroom Gen
#VALUE! | Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Generation (MVA) | Generation Headroom Winter (MVA) | [11 empty] | Generation Headroom Summer (MVA) | [11 empty] | Generation Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
| FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | 0 | 0.19684 | 0.19684 | 0.19579 | 0.19474 | 0.19368 | 0.19053 | 0.18947 | 0.18842 | 0.18421 | 0.15474 | 0.11579 | 0.088421 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19474 | 0.19263 | 0.19053 | 0.18842 | 0.18316 | 0.14947 | 0.10526 | 0.071579 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19263 | 0.19158 | 0.18947 | 0.18316 | 0.14947 | 0.10526 | 0.071579
|  | ABERCHALDER | EE |  |  |  |  | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19474 | 0.19263 | 0.19158 | 0.18947 | 0.18737 | 0.16211 | 0.12842 | 0.095789 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19263 | 0.19158 | 0.18947 | 0.15789 | 0.12316 | 0.085263 | 0.20105 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19474 | 0.19368 | 0.19158 | 0.18947 | 0.15789 | 0.12105 | 0.082105
|  | ABERCHALDER | HT |  |  |  |  | 0.19684 | 0.19684 | 0.19579 | 0.19474 | 0.19368 | 0.19053 | 0.18947 | 0.18842 | 0.18421 | 0.15474 | 0.11579 | 0.088421 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19474 | 0.19263 | 0.19053 | 0.18842 | 0.18316 | 0.14947 | 0.10526 | 0.071579 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19263 | 0.19158 | 0.18947 | 0.18316 | 0.14947 | 0.10526 | 0.071579
|  | ABERCHALDER | HE |  |  |  |  | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19263 | 0.19053 | 0.18526 | 0.16632 | 0.13895 | 0.10842 | 0.20105 | 0.20105 | 0.2 | 0.19895 | 0.19789 | 0.19579 | 0.19263 | 0.18947 | 0.18421 | 0.16211 | 0.13158 | 0.097895 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19263 | 0.19158 | 0.18947 | 0.18316 | 0.14947 | 0.10526 | 0.071579
|  | ABERCHALDER | CF |  |  |  |  | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19579 | 0.19368 | 0.19263 | 0.18316 | 0.16526 | 0.14316 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19684 | 0.19579 | 0.19263 | 0.17895 | 0.15895 | 0.13474 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.19789 | 0.19579 | 0.19263 | 0.18 | 0.16 | 0.13474
| TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 0 | 6.6674 | 6.5884 | 6.4558 | 6.2295 | 5.7347 | 5.1926 | 4.6295 | 4.1084 | 3.4811 | 0.87368 | -3.1632 | -6.1074 | 6.8463 | 6.6484 | 6.4326 | 6.1737 | 5.7074 | 5.2737 | 4.8032 | 4.2621 | 3.6084 | 1.4095 | -2.4558 | -5.5695 | 6.1684 | 6.0589 | 5.8568 | 5.6126 | 5.0811 | 4.4979 | 3.8979 | 3.3389 | 2.6547 | -0.12947 | -4.5147 | -7.8021
|  | ABERFELDY | EE |  |  |  |  | 6.6979 | 6.6221 | 6.5432 | 6.4074 | 5.8537 | 5.1926 | 4.6295 | 4.1084 | 3.4811 | 0.87368 | -3.1632 | -6.1074 | 6.9368 | 6.7989 | 6.6337 | 6.4179 | 5.9116 | 5.2937 | 4.8032 | 4.3358 | 3.7347 | 1.4095 | -2.4558 | -5.5695 | 6.1958 | 6.1158 | 6.0137 | 5.8032 | 5.2147 | 4.4979 | 3.8979 | 3.3389 | 2.6547 | -0.12947 | -4.5147 | -7.8021
|  | ABERFELDY | HT |  |  |  |  | 6.6674 | 6.5884 | 6.4558 | 6.2295 | 5.7347 | 5.2716 | 4.7937 | 4.2116 | 3.5516 | 1.3137 | -2.2379 | -4.6305 | 6.8463 | 6.6484 | 6.4326 | 6.1737 | 5.7074 | 5.2737 | 4.82 | 4.2621 | 3.6084 | 1.4653 | -2.3611 | -5.0211 | 6.1684 | 6.0589 | 5.8568 | 5.6126 | 5.0811 | 4.5821 | 4.0674 | 3.4358 | 2.7147 | 0.25789 | -3.6989 | -6.4347
|  | ABERFELDY | HE |  |  |  |  | 6.7505 | 6.7116 | 6.6695 | 6.6242 | 6.0695 | 5.5232 | 5.0463 | 4.5274 | 3.9158 | 2.1411 | -0.86737 | -4.1705 | 7.0358 | 6.9368 | 6.8063 | 6.6179 | 6.1021 | 5.5663 | 5.1189 | 4.6147 | 3.9937 | 2.4484 | -0.59263 | -3.8979 | 6.1684 | 6.0589 | 5.8568 | 5.6126 | 5.0811 | 4.5821 | 4.0674 | 3.4358 | 2.7147 | 0.25789 | -3.6989 | -6.4347
|  | ABERFELDY | CF |  |  |  |  | 6.7821 | 6.76 | 6.74 | 6.7168 | 6.5789 | 6.4589 | 6.3379 | 6.1947 | 6.0021 | 4.7516 | 2.9274 | 0.89368 | 7.1221 | 7.0811 | 7.0379 | 6.98 | 6.8263 | 6.6537 | 6.4589 | 6.2874 | 6.0842 | 4.7863 | 2.8579 | 0.67158 | 6.2853 | 6.2632 | 6.2421 | 6.2179 | 6.0863 | 5.9695 | 5.7642 | 5.5768 | 5.3716 | 3.9937 | 1.9232 | -0.3579
| STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 0 | 4.2832 | 4.2453 | 4.2021 | 4.1421 | 4.0189 | 3.8958 | 3.7621 | 3.6326 | 3.5053 | 2.8621 | 2.2811 | 1.8295 | 4.3653 | 4.2853 | 4.1874 | 4.0821 | 3.9558 | 3.8316 | 3.6958 | 3.5674 | 3.4316 | 2.8053 | 2.2558 | 1.7579 | 4.4116 | 4.3274 | 4.2274 | 4.12 | 3.9863 | 3.8495 | 3.7042 | 3.5632 | 3.4232 | 2.7168 | 2.0705 | 1.5568
|  | ABERFOYLE | EE |  |  |  |  | 4.2884 | 4.2453 | 4.2021 | 4.1526 | 4.0253 | 3.8958 | 3.7621 | 3.6326 | 3.5053 | 2.8621 | 2.2811 | 1.8295 | 4.3926 | 4.3147 | 4.2253 | 4.1242 | 4.0021 | 3.88 | 3.7537 | 3.6305 | 3.5105 | 2.8947 | 2.3347 | 1.8853 | 4.4326 | 4.3453 | 4.2453 | 4.1316 | 3.9916 | 3.8495 | 3.7042 | 3.5632 | 3.4232 | 2.7168 | 2.0705 | 1.5568
|  | ABERFOYLE | HT |  |  |  |  | 4.2832 | 4.2484 | 4.2116 | 4.1421 | 4.0189 | 3.8989 | 3.7695 | 3.6432 | 3.5126 | 2.9168 | 2.4042 | 1.9495 | 4.3653 | 4.2853 | 4.1874 | 4.0821 | 3.9558 | 3.8316 | 3.6958 | 3.5674 | 3.4316 | 2.8053 | 2.2558 | 1.7579 | 4.4116 | 4.3274 | 4.2274 | 4.12 | 3.9863 | 3.8558 | 3.7137 | 3.5747 | 3.4326 | 2.7674 | 2.1853 | 1.6632
|  | ABERFOYLE | HE |  |  |  |  | 4.3232 | 4.3011 | 4.2768 | 4.2526 | 4.2032 | 4.12 | 4.0211 | 3.9242 | 3.8295 | 3.3653 | 2.9474 | 2.5526 | 4.4537 | 4.4063 | 4.3421 | 4.2716 | 4.1705 | 4.0768 | 3.9779 | 3.8789 | 3.7811 | 3.3063 | 2.8758 | 2.4747 | 4.4116 | 4.3274 | 4.2274 | 4.12 | 3.9863 | 3.8558 | 3.7137 | 3.5747 | 3.4326 | 2.7674 | 2.1853 | 1.6632
|  | ABERFOYLE | CF |  |  |  |  | 4.3432 | 4.3326 | 4.32 | 4.3095 | 4.2905 | 4.2716 | 4.2537 | 4.2358 | 4.2189 | 3.9695 | 3.7295 | 3.5253 | 4.4937 | 4.4684 | 4.4368 | 4.4042 | 4.3642 | 4.3221 | 4.2747 | 4.2253 | 4.1758 | 3.8989 | 3.6474 | 3.4263 | 4.5432 | 4.5158 | 4.4853 | 4.4516 | 4.4063 | 4.3611 | 4.3116 | 4.26 | 4.2084 | 3.9232 | 3.6568 | 3.4284
| KEITH 2 | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 0 | 5.8842 | 5.8358 | 5.7758 | 5.5758 | 5.2989 | 5.2326 | 4.9126 | 4.5947 | 4.2674 | 2.14 | -0.52211 | -2.2042 | 5.4926 | 5.4126 | 5.3347 | 5.1126 | 4.8779 | 4.8074 | 4.5716 | 4.3021 | 4.0305 | 2.1684 | -0.30842 | -2.0726 | 6.0674 | 5.9958 | 5.9242 | 5.7547 | 5.4768 | 5.4158 | 5.0768 | 4.7547 | 4.4263 | 2.2526 | -0.58842 | -2.4695
|  | ABERLOUR | EE |  |  |  |  | 5.9074 | 5.86 | 5.8116 | 5.64 | 5.3274 | 5.2779 | 4.9126 | 4.5947 | 4.2674 | 2.14 | -0.52211 | -2.2042 | 5.5421 | 5.4716 | 5.4021 | 5.1874 | 4.9295 | 4.8779 | 4.5779 | 4.3168 | 4.0516 | 2.1684 | -0.30842 | -2.0726 | 6.1084 | 6.0421 | 5.9747 | 5.8095 | 5.4937 | 5.4484 | 5.0768 | 4.7547 | 4.4263 | 2.2526 | -0.58842 | -2.4695
|  | ABERLOUR | HT |  |  |  |  | 5.8842 | 5.8358 | 5.7758 | 5.5758 | 5.2989 | 5.2326 | 4.9568 | 4.6347 | 4.3105 | 2.4958 | 0.43789 | -0.88 | 5.4926 | 5.4126 | 5.3347 | 5.1126 | 4.8779 | 4.8074 | 4.5716 | 4.3021 | 4.0305 | 2.3179 | 0.16421 | -1.2726 | 6.0674 | 5.9958 | 5.9242 | 5.7547 | 5.4768 | 5.4158 | 5.1368 | 4.8095 | 4.4789 | 2.5621 | 0.26632 | -1.2347
|  | ABERLOUR | HE |  |  |  |  | 5.9379 | 5.9147 | 5.8884 | 5.8 | 5.4853 | 5.4516 | 5.1905 | 4.9263 | 4.6442 | 2.9432 | 1.0147 | -1.0653 | 5.6074 | 5.5705 | 5.5316 | 5.3474 | 5.0916 | 5.0568 | 4.8432 | 4.6305 | 4.3937 | 2.8274 | 0.96316 | -1.0526 | 6.0674 | 5.9958 | 5.9242 | 5.7547 | 5.4768 | 5.4158 | 5.1368 | 4.8095 | 4.4789 | 2.5621 | 0.26632 | -1.2347
|  | ABERLOUR | CF |  |  |  |  | 5.9579 | 5.9453 | 5.9305 | 5.9168 | 5.8137 | 5.8021 | 5.7105 | 5.6326 | 5.5305 | 4.7 | 3.4947 | 2.28 | 5.7 | 5.6779 | 5.6547 | 5.5705 | 5.4674 | 5.4463 | 5.3547 | 5.2737 | 5.16 | 4.3589 | 3.1863 | 1.9337 | 6.1884 | 6.1758 | 6.1621 | 6.1295 | 6.0042 | 5.9863 | 5.8747 | 5.78 | 5.6705 | 4.8695 | 3.5726 | 2.2211
| ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 0 | 2.3026 | 2.2532 | 2.2037 | 2.1353 | 1.9679 | 1.8184 | 1.6584 | 1.45 | 1.1184 | 0.57211 | -2.5868 | -3.5647 | 2.1247 | 2.07 | 2.0184 | 1.9416 | 1.77 | 1.6163 | 1.4532 | 1.2342 | 0.87211 | 0.42053 | -2.2289 | -3.2247 | 2.0847 | 2.0374 | 1.9858 | 1.9079 | 1.7216 | 1.5542 | 1.3753 | 1.1395 | 0.75737 | 0.21947 | -1.0332 | -1.9521
|  | ABERNETHY | EE |  |  |  |  | 2.3342 | 2.2942 | 2.2563 | 2.2058 | 2.0384 | 1.8342 | 1.6816 | 1.5353 | 1.3279 | 0.57211 | -0.43 | -1.3437 | 2.1595 | 2.1163 | 2.0763 | 2.0216 | 1.8532 | 1.6437 | 1.5016 | 1.3605 | 1.1447 | 0.45211 | -0.56474 | -1.5837 | 2.1142 | 2.0763 | 2.0395 | 1.9879 | 1.8016 | 1.5711 | 1.4068 | 1.2479 | 1.0121 | 0.21947 | -0.89105 | -1.9521
|  | ABERNETHY | HT |  |  |  |  | 2.3026 | 2.2532 | 2.2037 | 2.1353 | 1.9679 | 1.8184 | 1.6584 | 1.45 | 1.1184 | 0.61737 | -0.47842 | -1.2721 | 2.1247 | 2.07 | 2.0184 | 1.9416 | 1.77 | 1.6163 | 1.4532 | 1.2342 | 0.87211 | 0.42053 | -0.80684 | -1.6932 | 2.0847 | 2.0374 | 1.9858 | 1.9079 | 1.7216 | 1.5542 | 1.3753 | 1.1395 | 0.75737 | 0.23842 | -1.0332 | -1.9447
|  | ABERNETHY | HE |  |  |  |  | 2.3595 | 2.3447 | 2.3279 | 2.2889 | 2.1132 | 1.9289 | 1.7805 | 1.61 | 1.4089 | 0.96684 | -2.5868 | -3.5647 | 2.2026 | 2.1784 | 2.1553 | 2.1089 | 1.9332 | 1.7353 | 1.5858 | 1.4068 | 1.1921 | 0.81 | -2.2289 | -3.2247 | 2.0847 | 2.0374 | 1.9858 | 1.9079 | 1.7216 | 1.5542 | 1.3753 | 1.1395 | 0.75737 | 0.23842 | -1.0332 | -1.9447
|  | ABERNETHY | CF |  |  |  |  | 2.3732 | 2.3647 | 2.3553 | 2.3479 | 2.2995 | 2.2458 | 2.1816 | 2.1258 | 2.0279 | 1.6911 | -0.46474 | -1.1047 | 2.2258 | 2.21 | 2.1963 | 2.1784 | 2.1311 | 2.0763 | 2.01 | 1.9542 | 1.8405 | 1.4837 | -0.36263 | -1.0489 | 2.1658 | 2.1563 | 2.1426 | 2.1289 | 2.0784 | 2.0247 | 1.9605 | 1.8995 | 1.7805 | 1.3953 | -0.83526 | -1.5637
| TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | YES | 0 | 15.6289 | 15.3184 | 14.9668 | 14.6384 | 14.0805 | 13.5321 | 12.9879 | 12.4026 | 11.9268 | 10.0174 | 7.8637 | 5.7616 | 13.6853 | 13.3326 | 12.9274 | 12.5526 | 11.9832 | 11.4253 | 10.8716 | 10.2853 | 9.8411 | 8.2695 | 6.3274 | 4.0811 | 14.3403 | 14.0003 | 13.6118 | 13.2508 | 12.6466 | 12.0539 | 11.4634 | 10.8297 | 10.3255 | 8.3182 | 6.0213 | 3.7045
|  | ABOYNE | EE |  |  |  |  | 15.8026 | 15.5353 | 15.2184 | 14.8774 | 14.3142 | 13.7079 | 13.1068 | 12.5542 | 12.1111 | 10.0174 | 7.8637 | 5.7616 | 13.8832 | 13.5811 | 13.2179 | 12.8253 | 12.2642 | 11.6726 | 11.0884 | 10.5453 | 10.1389 | 8.2811 | 6.3432 | 4.0811 | 14.5297 | 14.2361 | 13.8866 | 13.5066 | 12.8971 | 12.2434 | 11.595 | 10.9971 | 10.5255 | 8.3182 | 6.0213 | 3.7045
|  | ABOYNE | HT |  |  |  |  | 15.6289 | 15.3184 | 14.9668 | 14.6384 | 14.0805 | 13.5321 | 12.9879 | 12.4026 | 11.9268 | 10.2342 | 8.4005 | 6.6195 | 13.6853 | 13.3326 | 12.9274 | 12.5526 | 11.9832 | 11.4253 | 10.8716 | 10.2853 | 9.8411 | 8.2695 | 6.3274 | 4.3705 | 14.3403 | 14.0003 | 13.6118 | 13.2508 | 12.6466 | 12.0539 | 11.4634 | 10.8297 | 10.3255 | 8.5287 | 6.455 | 4.4371
|  | ABOYNE | HE |  |  |  |  | 16.0026 | 15.8258 | 15.6005 | 15.3489 | 14.7858 | 14.2711 | 13.8026 | 13.3405 | 12.9921 | 11.6079 | 9.8363 | 7.4711 | 14.1084 | 13.9042 | 13.6421 | 13.3474 | 12.7884 | 12.2674 | 11.8032 | 11.3474 | 11.0316 | 9.8242 | 8.0747 | 5.6726 | 14.3403 | 14.0003 | 13.6118 | 13.2508 | 12.6466 | 12.0539 | 11.4634 | 10.8297 | 10.3255 | 8.5287 | 6.455 | 4.4371
|  | ABOYNE | CF |  |  |  |  | 16.1374 | 16.0489 | 15.9353 | 15.8142 | 15.5805 | 15.3521 | 15.1142 | 14.8995 | 14.7637 | 14.0542 | 12.8416 | 11.4311 | 14.26 | 14.16 | 14.0284 | 13.8863 | 13.6495 | 13.4137 | 13.1653 | 12.94 | 12.8042 | 12.1505 | 10.9189 | 9.3547 | 14.8918 | 14.795 | 14.6697 | 14.5339 | 14.2792 | 14.0287 | 13.7676 | 13.5318 | 13.3866 | 12.6339 | 11.3003 | 9.6918
| GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | NO | 0 | 0.37263 | 0.36 | 0.34737 | 0.33368 | 0.32105 | 0.30737 | 0.29579 | 0.28211 | 0.27053 | 0.21158 | -0.30211 | -0.36316 | 0.45158 | 0.42947 | 0.40737 | 0.38632 | 0.36526 | 0.34526 | 0.32632 | 0.30632 | 0.28632 | 0.19895 | -0.21895 | -0.28421 | 0.39474 | 0.37895 | 0.36421 | 0.34842 | 0.33368 | 0.31684 | 0.30211 | 0.28737 | 0.27368 | 0.19684 | -0.32737 | -0.39684
|  | ACHILTIBUIE | EE |  |  |  |  | 0.38 | 0.36947 | 0.35789 | 0.34632 | 0.33368 | 0.32421 | 0.31263 | 0.30316 | 0.29263 | 0.25368 | -0.23474 | -0.2821 | 0.46526 | 0.44842 | 0.43053 | 0.41368 | 0.39579 | 0.38105 | 0.36421 | 0.34947 | 0.33474 | 0.26526 | -0.13895 | -0.18737 | 0.40421 | 0.39053 | 0.37684 | 0.36211 | 0.34842 | 0.33579 | 0.32316 | 0.31158 | 0.29895 | 0.24842 | -0.25474 | -0.30737
|  | ACHILTIBUIE | HT |  |  |  |  | 0.37263 | 0.36 | 0.34737 | 0.33368 | 0.32105 | 0.30737 | 0.29579 | 0.28211 | 0.27053 | 0.21158 | -0.30211 | -0.36316 | 0.45158 | 0.42947 | 0.40737 | 0.38632 | 0.36526 | 0.34526 | 0.32632 | 0.30632 | 0.28632 | 0.19895 | -0.21895 | -0.28421 | 0.39474 | 0.37895 | 0.36421 | 0.34842 | 0.33368 | 0.31684 | 0.30211 | 0.28737 | 0.27368 | 0.19684 | -0.32737 | -0.39684
|  | ACHILTIBUIE | HE |  |  |  |  | 0.39053 | 0.38421 | 0.37684 | 0.36842 | 0.36105 | 0.35263 | 0.34632 | 0.33895 | 0.33368 | 0.31158 | 0.10105 | 0.093684 | 0.48632 | 0.47684 | 0.46421 | 0.45368 | 0.44211 | 0.43158 | 0.42105 | 0.41158 | 0.40316 | 0.36947 | 0.17053 | 0.14421 | 0.39474 | 0.37895 | 0.36421 | 0.34842 | 0.33368 | 0.31684 | 0.30211 | 0.28737 | 0.27368 | 0.19684 | -0.32737 | -0.39684
|  | ACHILTIBUIE | CF |  |  |  |  | 0.39684 | 0.39368 | 0.39053 | 0.38632 | 0.38211 | 0.37895 | 0.37579 | 0.37158 | 0.36842 | 0.35263 | 0.34526 | 0.33895 | 0.49684 | 0.49053 | 0.48421 | 0.47895 | 0.47263 | 0.46632 | 0.46 | 0.45263 | 0.44737 | 0.41789 | 0.4 | 0.38421 | 0.42526 | 0.42105 | 0.41684 | 0.41158 | 0.40737 | 0.40316 | 0.39895 | 0.39474 | 0.39053 | 0.37053 | 0.36 | 0.35158
| BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | YES | 0 | 0.53158 | 0.52316 | 0.51368 | 0.50632 | 0.43263 | 0.34105 | 0.24632 | 0.15684 | 0.018947 | -0.76211 | -1.7095 | -2.4611 | 0.52 | 0.51158 | 0.50316 | 0.49579 | 0.43474 | 0.35158 | 0.26211 | 0.18 | 0.042105 | -0.71263 | -1.7105 | -2.46 | 0.52211 | 0.51263 | 0.50316 | 0.49474 | 0.42632 | 0.34211 | 0.25684 | 0.18105 | 0.027368 | -0.86105 | -1.9 | -2.7579
|  | AIGAS | EE |  |  |  |  | 0.53474 | 0.52526 | 0.51684 | 0.50632 | 0.43684 | 0.35263 | 0.26632 | 0.19158 | 0.078947 | -0.76211 | -1.7095 | -2.4611 | 0.52421 | 0.51474 | 0.50632 | 0.49895 | 0.44526 | 0.37789 | 0.30737 | 0.24737 | 0.14105 | -0.69053 | -1.6379 | -2.46 | 0.52526 | 0.51579 | 0.50632 | 0.49684 | 0.42632 | 0.34211 | 0.25684 | 0.18105 | 0.062105 | -0.86105 | -1.9 | -2.7579
|  | AIGAS | HT |  |  |  |  | 0.53158 | 0.52316 | 0.51368 | 0.50632 | 0.44737 | 0.38842 | 0.31789 | 0.22526 | 0.062105 | -0.71368 | -1.6179 | -2.24 | 0.52 | 0.51158 | 0.50316 | 0.49579 | 0.45158 | 0.40316 | 0.34211 | 0.25684 | 0.093684 | -0.71263 | -1.7105 | -2.4158 | 0.52211 | 0.51263 | 0.50316 | 0.49474 | 0.43684 | 0.37789 | 0.30526 | 0.20632 | 0.027368 | -0.83579 | -1.8705 | -2.5905
|  | AIGAS | HE |  |  |  |  | 0.53684 | 0.53368 | 0.53158 | 0.52842 | 0.43263 | 0.34105 | 0.24632 | 0.15684 | 0.018947 | -0.56316 | -1.3095 | -2.12 | 0.52632 | 0.52421 | 0.52211 | 0.51895 | 0.43474 | 0.35158 | 0.26211 | 0.18 | 0.042105 | -0.53263 | -1.3042 | -2.1453 | 0.52211 | 0.51263 | 0.50316 | 0.49474 | 0.43684 | 0.37789 | 0.30526 | 0.20632 | 0.027368 | -0.83579 | -1.8705 | -2.5905
|  | AIGAS | CF |  |  |  |  | 0.53789 | 0.53684 | 0.53474 | 0.53368 | 0.50632 | 0.48 | 0.42526 | 0.36632 | 0.29684 | -0.008421 | -0.4779 | -1.0084 | 0.52737 | 0.52737 | 0.52526 | 0.52421 | 0.50316 | 0.48421 | 0.42421 | 0.36105 | 0.28526 | -0.027368 | -0.51684 | -1.0979 | 0.53263 | 0.53158 | 0.52842 | 0.52526 | 0.49684 | 0.47158 | 0.40947 | 0.34421 | 0.26632 | -0.071579 | -0.59579 | -1.2011
| ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 0 | 7.5095 | 7.4758 | 7.4421 | 7.4084 | 7.3716 | 7.3358 | 7.3011 | 7.2684 | 7.2368 | 7.1326 | 7.0621 | 6.2032 | 7.1705 | 7.1063 | 7.0432 | 6.9832 | 6.92 | 6.86 | 6.8011 | 6.7463 | 6.6926 | 6.4779 | 6.3 | 5.5284 | 7.4337 | 7.3695 | 7.3063 | 7.2453 | 7.1832 | 7.1232 | 7.0642 | 7.0095 | 6.9558 | 6.74 | 6.5632 | 5.6116
|  | AIRD | EE |  |  |  |  | 7.5263 | 7.4989 | 7.4705 | 7.4411 | 7.4105 | 7.3811 | 7.3537 | 7.3274 | 7.3021 | 7.2032 | 7.1495 | 6.3947 | 7.2116 | 7.1611 | 7.1105 | 7.06 | 7.0095 | 6.9621 | 6.9147 | 6.8716 | 6.8295 | 6.6474 | 6.5137 | 5.78 | 7.4747 | 7.4242 | 7.3737 | 7.3232 | 7.2726 | 7.2253 | 7.1779 | 7.1347 | 7.0916 | 6.9105 | 6.7768 | 5.8684
|  | AIRD | HT |  |  |  |  | 7.5095 | 7.4758 | 7.4421 | 7.4084 | 7.3716 | 7.3358 | 7.3011 | 7.2684 | 7.2368 | 7.1326 | 7.0621 | 6.2032 | 7.1705 | 7.1063 | 7.0432 | 6.9832 | 6.92 | 6.86 | 6.8011 | 6.7463 | 6.6926 | 6.4779 | 6.3 | 5.5284 | 7.4337 | 7.3695 | 7.3063 | 7.2453 | 7.1832 | 7.1232 | 7.0642 | 7.0095 | 6.9558 | 6.74 | 6.5632 | 5.6116
|  | AIRD | HE |  |  |  |  | 7.5537 | 7.5347 | 7.5137 | 7.4916 | 7.4684 | 7.4474 | 7.4263 | 7.4063 | 7.3884 | 7.3284 | 7.2979 | 6.9253 | 7.2716 | 7.24 | 7.2063 | 7.1726 | 7.1379 | 7.1063 | 7.0747 | 7.0453 | 7.0179 | 6.9168 | 6.8463 | 6.4863 | 7.4337 | 7.3695 | 7.3063 | 7.2453 | 7.1832 | 7.1232 | 7.0642 | 7.0095 | 6.9558 | 6.74 | 6.5632 | 5.6116
|  | AIRD | CF |  |  |  |  | 7.5716 | 7.5611 | 7.5505 | 7.54 | 7.5295 | 7.5179 | 7.5063 | 7.4958 | 7.4842 | 7.4379 | 7.4137 | 7.4032 | 7.3042 | 7.2842 | 7.2653 | 7.2453 | 7.2253 | 7.2053 | 7.1853 | 7.1653 | 7.1453 | 7.0579 | 6.9958 | 6.9505 | 7.5305 | 7.5189 | 7.5084 | 7.4968 | 7.4863 | 7.4684 | 7.4484 | 7.4284 | 7.4084 | 7.3211 | 7.2589 | 7.2137
| PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0 | 0.32658 | 0.32342 | 0.32026 | 0.31395 | 0.26237 | 0.20237 | 0.14237 | 0.084474 | -0.005 | -0.50184 | -3.7882 | -4.2408 | 0.32132 | 0.31816 | 0.31605 | 0.31079 | 0.26447 | 0.20974 | 0.15395 | 0.10132 | 0.011842 | -0.46184 | -3.1987 | -3.7018 | 0.32237 | 0.31921 | 0.31605 | 0.31079 | 0.26974 | 0.215 | 0.16132 | 0.11395 | 0.011842 | -0.5629 | -3.9018 | -4.4418
|  | AIRIGH-NA-BRODAIG | EE |  |  |  |  | 0.32763 | 0.32342 | 0.32026 | 0.31395 | 0.27184 | 0.21816 | 0.16342 | 0.11711 | 0.038158 | -0.50184 | -3.7882 | -4.2408 | 0.32237 | 0.31816 | 0.31605 | 0.31079 | 0.27816 | 0.235 | 0.19184 | 0.15395 | 0.081316 | -0.45342 | -3.1987 | -3.7018 | 0.32342 | 0.31921 | 0.31605 | 0.31079 | 0.26974 | 0.215 | 0.16132 | 0.11395 | 0.029737 | -0.5629 | -3.9018 | -4.4418
|  | AIRIGH-NA-BRODAIG | HT |  |  |  |  | 0.32658 | 0.32342 | 0.32026 | 0.31816 | 0.28237 | 0.24658 | 0.195 | 0.135 | 0.031842 | -0.46395 | -3.1566 | -3.5461 | 0.32132 | 0.31921 | 0.31605 | 0.31395 | 0.28553 | 0.25711 | 0.21079 | 0.15711 | 0.052895 | -0.46184 | -2.7734 | -3.1976 | 0.32237 | 0.32026 | 0.31711 | 0.31395 | 0.27921 | 0.24237 | 0.18868 | 0.12553 | 0.011842 | -0.54184 | -3.3239 | -3.7745
|  | AIRIGH-NA-BRODAIG | HE |  |  |  |  | 0.32763 | 0.32658 | 0.32553 | 0.32447 | 0.26237 | 0.20237 | 0.14237 | 0.084474 | -0.005 | -0.37763 | -2.1797 | -2.6976 | 0.32342 | 0.32237 | 0.32132 | 0.32026 | 0.26447 | 0.20974 | 0.15395 | 0.10132 | 0.011842 | -0.35658 | -1.9018 | -2.4282 | 0.32237 | 0.32026 | 0.31711 | 0.31395 | 0.27921 | 0.24237 | 0.18868 | 0.12553 | 0.011842 | -0.54184 | -3.3239 | -3.7745
|  | AIRIGH-NA-BRODAIG | CF |  |  |  |  | 0.32763 | 0.32658 | 0.32658 | 0.32553 | 0.30974 | 0.29395 | 0.25395 | 0.21605 | 0.17184 | -0.022895 | -1.6503 | -1.985 | 0.32342 | 0.32237 | 0.32237 | 0.32237 | 0.30763 | 0.295 | 0.25395 | 0.215 | 0.16763 | -0.032368 | -1.4018 | -1.7576 | 0.32447 | 0.32342 | 0.32342 | 0.32237 | 0.30658 | 0.28974 | 0.24658 | 0.20342 | 0.15289 | -0.062895 | -1.7282 | -2.1113
| COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | YES | 0.196 | 4.6556 | 4.3745 | 4.0493 | 3.6082 | 2.884 | 2.5914 | 2.0829 | 1.8145 | 1.1851 | -1.3665 | -5.6876 | -9.1413 | 4.6124 | 4.2577 | 3.8419 | 3.264 | 2.4661 | 2.0861 | 1.5819 | 1.2335 | 0.604 | -1.4276 | -5.0592 | -8.5065 | 4.724 | 4.3724 | 3.9619 | 3.3935 | 2.5314 | 2.1608 | 1.5851 | 1.2451 | 0.52611 | -2.1181 | -5.0992 | -8.4581
|  | ALYTH | EE |  |  |  |  | 4.7535 | 4.5166 | 4.2366 | 3.8598 | 3.0672 | 2.6766 | 2.0914 | 1.9251 | 1.3629 | -1.3665 | -4.176 | -7.1928 | 4.7335 | 4.4366 | 4.0808 | 3.5903 | 2.7282 | 2.204 | 1.6766 | 1.4629 | 0.93558 | -1.4276 | -4.0013 | -7.2086 | 4.8419 | 4.5461 | 4.1924 | 3.7072 | 2.7619 | 2.2514 | 1.6093 | 1.4019 | 0.77453 | -2.1181 | -5.0992 | -8.4581
|  | ALYTH | HT |  |  |  |  | 4.6556 | 4.3745 | 4.0493 | 3.6082 | 2.884 | 2.5914 | 2.0829 | 1.8145 | 1.1851 | -0.68758 | -3.5781 | -6.0402 | 4.6124 | 4.2577 | 3.8419 | 3.264 | 2.4661 | 2.0861 | 1.5819 | 1.2335 | 0.604 | -0.98232 | -4.0718 | -6.8128 | 4.724 | 4.3724 | 3.9619 | 3.3935 | 2.5314 | 2.1608 | 1.5851 | 1.2451 | 0.52611 | -1.4255 | -4.6276 | -7.4423
|  | ALYTH | HE |  |  |  |  | 4.8451 | 4.6503 | 4.4061 | 4.0451 | 3.2303 | 2.8619 | 2.3672 | 2.1745 | 1.6861 | -0.011789 | -5.6876 | -9.1413 | 4.8408 | 4.5851 | 4.2608 | 3.7766 | 2.8903 | 2.3903 | 1.9114 | 1.6566 | 1.1829 | -0.2139 | -5.0592 | -8.5065 | 4.724 | 4.3724 | 3.9619 | 3.3935 | 2.5314 | 2.1608 | 1.5851 | 1.2451 | 0.52611 | -1.4255 | -4.6276 | -7.4423
|  | ALYTH | CF |  |  |  |  | 4.9903 | 4.8987 | 4.8008 | 4.6766 | 4.3998 | 4.2745 | 4.0366 | 3.9324 | 3.6903 | 2.6966 | -2.0286 | -4.1455 | 5.0229 | 4.9103 | 4.7861 | 4.6251 | 4.3335 | 4.1661 | 3.9198 | 3.7808 | 3.4956 | 2.5061 | -1.6602 | -3.8971 | 5.1335 | 5.0177 | 4.8924 | 4.7335 | 4.4093 | 4.2461 | 3.9703 | 3.8345 | 3.5366 | 2.3998 | -2.7002 | -5.0792
| FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | NO | 0 | 7.0189 | 6.9726 | 6.9274 | 6.8811 | 6.8063 | 6.7042 | 6.6011 | 6.4979 | 6.4021 | 5.9747 | 5.6537 | 5.4189 | 6.6274 | 6.5463 | 6.4674 | 6.3884 | 6.2895 | 6.1916 | 6.0958 | 6.0011 | 5.9126 | 5.5137 | 5.2095 | 4.9737 | 6.8105 | 6.7453 | 6.6789 | 6.6126 | 6.5158 | 6.4232 | 6.3305 | 6.2368 | 6.1411 | 5.6895 | 5.3516 | 5.1011
|  | ANNAT | EE |  |  |  |  | 7.0421 | 7.0021 | 6.9589 | 6.9179 | 6.8495 | 6.7758 | 6.7021 | 6.6084 | 6.5168 | 6.0779 | 5.6853 | 5.46 | 6.6768 | 6.6105 | 6.5432 | 6.4768 | 6.3926 | 6.3053 | 6.2147 | 6.1305 | 6.0495 | 5.6632 | 5.3253 | 5.1137 | 6.8347 | 6.7916 | 6.7337 | 6.6737 | 6.5863 | 6.4947 | 6.3989 | 6.3126 | 6.2263 | 5.7968 | 5.38 | 5.14
|  | ANNAT | HT |  |  |  |  | 7.0189 | 6.9726 | 6.9274 | 6.8811 | 6.8063 | 6.7042 | 6.6011 | 6.4979 | 6.4021 | 5.9747 | 5.6537 | 5.4189 | 6.6274 | 6.5463 | 6.4674 | 6.3884 | 6.2895 | 6.1916 | 6.0958 | 6.0011 | 5.9126 | 5.5137 | 5.2095 | 4.9737 | 6.8105 | 6.7453 | 6.6789 | 6.6126 | 6.5158 | 6.4232 | 6.3305 | 6.2368 | 6.1411 | 5.6895 | 5.3516 | 5.1011
|  | ANNAT | HE |  |  |  |  | 7.0779 | 7.0526 | 7.0253 | 6.9947 | 6.9358 | 6.8821 | 6.8305 | 6.78 | 6.7305 | 6.5347 | 6.3379 | 6.0547 | 6.7516 | 6.7116 | 6.6695 | 6.6263 | 6.56 | 6.5011 | 6.4389 | 6.3768 | 6.3253 | 6.1116 | 5.9389 | 5.6789 | 6.8105 | 6.7453 | 6.6789 | 6.6126 | 6.5158 | 6.4232 | 6.3305 | 6.2368 | 6.1411 | 5.6895 | 5.3516 | 5.1011
|  | ANNAT | CF |  |  |  |  | 7.1011 | 7.0874 | 7.0716 | 7.0579 | 7.0326 | 7.0095 | 6.9853 | 6.96 | 6.94 | 6.8326 | 6.7379 | 6.6305 | 6.7926 | 6.7674 | 6.7411 | 6.7158 | 6.68 | 6.6484 | 6.6158 | 6.58 | 6.5505 | 6.4053 | 6.2821 | 6.1747 | 6.8968 | 6.8821 | 6.8674 | 6.8526 | 6.8274 | 6.8032 | 6.78 | 6.7495 | 6.7221 | 6.5779 | 6.4474 | 6.3432
| KILLIN | ARDCHYLE | MINIMUM HEADROOM | NN 52734 29223 | YES | YES | 0 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.088421 | 0.081053 | 0.075789 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.093684 | 0.088421 | 0.08 | 0.073684 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.093684 | 0.087368 | 0.078947 | 0.072632
|  | ARDCHYLE | EE |  |  |  |  | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.089474 | 0.083158 | 0.076842 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.095789 | 0.089474 | 0.083158 | 0.075789 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.088421 | 0.082105 | 0.074737
|  | ARDCHYLE | HT |  |  |  |  | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.088421 | 0.081053 | 0.075789 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.093684 | 0.088421 | 0.08 | 0.073684 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.093684 | 0.087368 | 0.078947 | 0.072632
|  | ARDCHYLE | HE |  |  |  |  | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.095789 | 0.095789 | 0.095789 | 0.095789 | 0.090526 | 0.086316 | 0.08 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.090526 | 0.08421 | 0.078947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.093684 | 0.087368 | 0.078947 | 0.072632
|  | ARDCHYLE | CF |  |  |  |  | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.093684 | 0.090526 | 0.086316 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.093684 | 0.090526 | 0.086316 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.093684 | 0.089474 | 0.085263
| NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 0 | 5.6084 | 5.5389 | 5.4684 | 5.4 | 4.6411 | 3.8832 | 3.1263 | 2.3389 | 1.5547 | 0.24421 | -1.0305 | -1.9295 | 5.2853 | 5.2137 | 5.14 | 5.0684 | 4.2358 | 3.4042 | 2.5737 | 1.7221 | 0.87368 | -0.16 | -1.2074 | -2.1137 | 5.3326 | 5.2905 | 5.2263 | 5.1547 | 4.3337 | 3.4811 | 2.6158 | 1.7211 | 0.82947 | -0.50421 | -1.7958 | -2.7842
|  | ARDERSIER | EE |  |  |  |  | 5.6484 | 5.5874 | 5.5242 | 5.4611 | 5.2411 | 4.9842 | 4.1674 | 3.3821 | 2.5947 | 0.24421 | -1.0305 | -1.9295 | 5.3253 | 5.2674 | 5.2042 | 5.1411 | 4.9516 | 4.7358 | 3.8642 | 3.0189 | 2.1695 | -0.16 | -1.2074 | -2.1137 | 5.3526 | 5.3116 | 5.2705 | 5.2179 | 4.9863 | 4.7168 | 3.8326 | 2.9705 | 2.0758 | -0.50421 | -1.7958 | -2.7842
|  | ARDERSIER | HT |  |  |  |  | 5.6084 | 5.5389 | 5.4684 | 5.4 | 4.6411 | 3.8832 | 3.1263 | 2.3389 | 1.5547 | 0.62526 | -0.004211 | -1.2484 | 5.2853 | 5.2137 | 5.14 | 5.0684 | 4.2358 | 3.4042 | 2.5737 | 1.7221 | 0.87368 | 0.066316 | -0.48421 | -1.8695 | 5.3326 | 5.2905 | 5.2263 | 5.1547 | 4.3337 | 3.4811 | 2.6158 | 1.7211 | 0.82947 | -0.14211 | -0.79474 | -2.2179
|  | ARDERSIER | HE |  |  |  |  | 5.6768 | 5.6547 | 5.6305 | 5.6021 | 5.38 | 5.1453 | 4.8347 | 4.4779 | 4.1295 | 2.4589 | 0.87053 | -0.92421 | 5.3537 | 5.3326 | 5.3105 | 5.2842 | 5.0989 | 4.8853 | 4.5821 | 4.2263 | 3.8789 | 2.2126 | 0.62316 | -1.1821 | 5.3326 | 5.2905 | 5.2263 | 5.1547 | 4.3337 | 3.4811 | 2.6158 | 1.7211 | 0.82947 | -0.14211 | -0.79474 | -2.2179
|  | ARDERSIER | CF |  |  |  |  | 5.6947 | 5.6821 | 5.6684 | 5.6558 | 5.5811 | 5.5042 | 5.4063 | 5.2526 | 5.0853 | 4.2084 | 3.1905 | 1.9579 | 5.3716 | 5.36 | 5.3474 | 5.3347 | 5.2821 | 5.2126 | 5.1221 | 4.9653 | 4.7842 | 3.8747 | 2.8389 | 1.5021 | 5.3989 | 5.3863 | 5.3737 | 5.36 | 5.2916 | 5.2284 | 5.1579 | 4.9937 | 4.8116 | 3.8674 | 2.7537 | 1.3463
| FORT AUGUSTUS | ARDOCHY | MINIMUM HEADROOM | NH 47714 12561 | YES | YES | 0 | 0.097895 | 0.095789 | 0.094737 | 0.092632 | 0.066316 | 0.037895 | 0.010526 | -0.017895 | -0.058947 | -0.29474 | -0.57684 | -0.79368 | 0.097895 | 0.096842 | 0.094737 | 0.093684 | 0.069474 | 0.04421 | 0.018947 | -0.006316 | -0.046316 | -0.26526 | -0.54632 | -0.77895 | 0.097895 | 0.095789 | 0.093684 | 0.092632 | 0.070526 | 0.043158 | 0.01579 | -0.007368 | -0.051579 | -0.32 | -0.62947 | -0.87579
|  | ARDOCHY | EE |  |  |  |  | 0.097895 | 0.095789 | 0.094737 | 0.092632 | 0.071579 | 0.04421 | 0.016842 | -0.006316 | -0.042105 | -0.29474 | -0.57684 | -0.79368 | 0.097895 | 0.096842 | 0.094737 | 0.093684 | 0.076842 | 0.053684 | 0.031579 | 0.013684 | -0.02 | -0.26526 | -0.54421 | -0.77895 | 0.097895 | 0.095789 | 0.093684 | 0.092632 | 0.070526 | 0.043158 | 0.01579 | -0.007368 | -0.045263 | -0.32 | -0.62947 | -0.87579
|  | ARDOCHY | HT |  |  |  |  | 0.097895 | 0.096842 | 0.095789 | 0.093684 | 0.076842 | 0.058947 | 0.034737 | 0.0063158 | -0.043158 | -0.26947 | -0.53053 | -0.70737 | 0.097895 | 0.096842 | 0.096842 | 0.093684 | 0.08 | 0.065263 | 0.04421 | 0.018947 | -0.030526 | -0.26105 | -0.54632 | -0.74421 | 0.097895 | 0.096842 | 0.095789 | 0.093684 | 0.075789 | 0.057895 | 0.032632 | 0.0031579 | -0.051579 | -0.30211 | -0.6 | -0.80421
|  | ARDOCHY | HE |  |  |  |  | 0.1 | 0.1 | 0.096842 | 0.096842 | 0.066316 | 0.037895 | 0.010526 | -0.017895 | -0.058947 | -0.23368 | -0.45263 | -0.69263 | 0.1 | 0.1 | 0.096842 | 0.096842 | 0.069474 | 0.04421 | 0.018947 | -0.006316 | -0.046316 | -0.21684 | -0.44 | -0.68526 | 0.097895 | 0.096842 | 0.095789 | 0.093684 | 0.075789 | 0.057895 | 0.032632 | 0.0031579 | -0.051579 | -0.30211 | -0.6 | -0.80421
|  | ARDOCHY | CF |  |  |  |  | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.088421 | 0.08 | 0.063158 | 0.045263 | 0.025263 | -0.063158 | -0.20105 | -0.35579 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.090526 | 0.08421 | 0.066316 | 0.048421 | 0.026316 | -0.063158 | -0.20526 | -0.37263 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.088421 | 0.08 | 0.061053 | 0.041053 | 0.018947 | -0.08 | -0.23263 | -0.40842
| FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | NO | 0 | 2.5747 | 2.5474 | 2.5211 | 2.4968 | 2.4705 | 2.4453 | 2.4211 | 2.3979 | 2.3768 | 2.2916 | 2.2232 | 2.1674 | 2.5358 | 2.5074 | 2.4789 | 2.4526 | 2.4242 | 2.3968 | 2.3716 | 2.3474 | 2.3242 | 2.2316 | 2.1568 | 2.0958 | 2.5053 | 2.4768 | 2.4495 | 2.4242 | 2.3958 | 2.3695 | 2.3453 | 2.3211 | 2.2989 | 2.2095 | 2.1368 | 2.0779
|  | ARISAIG | EE |  |  |  |  | 2.5926 | 2.5716 | 2.5505 | 2.5305 | 2.5116 | 2.4916 | 2.4726 | 2.4558 | 2.4379 | 2.3684 | 2.3179 | 2.2789 | 2.5558 | 2.5337 | 2.5105 | 2.4895 | 2.4684 | 2.4474 | 2.4274 | 2.4095 | 2.3905 | 2.3158 | 2.26 | 2.2168 | 2.5242 | 2.5021 | 2.48 | 2.4589 | 2.4389 | 2.4189 | 2.3989 | 2.3811 | 2.3632 | 2.2905 | 2.2368 | 2.1947
|  | ARISAIG | HT |  |  |  |  | 2.5747 | 2.5474 | 2.5211 | 2.4968 | 2.4705 | 2.4453 | 2.4211 | 2.3979 | 2.3768 | 2.2916 | 2.2232 | 2.1674 | 2.5358 | 2.5074 | 2.4789 | 2.4526 | 2.4242 | 2.3968 | 2.3716 | 2.3474 | 2.3242 | 2.2316 | 2.1568 | 2.0958 | 2.5053 | 2.4768 | 2.4495 | 2.4242 | 2.3958 | 2.3695 | 2.3453 | 2.3211 | 2.2989 | 2.2095 | 2.1368 | 2.0779
|  | ARISAIG | HE |  |  |  |  | 2.6179 | 2.6042 | 2.5916 | 2.5779 | 2.5642 | 2.5516 | 2.5389 | 2.5263 | 2.5158 | 2.4768 | 2.4505 | 2.4326 | 2.5832 | 2.5695 | 2.5558 | 2.5411 | 2.5263 | 2.5126 | 2.5 | 2.4863 | 2.4758 | 2.4337 | 2.4042 | 2.3853 | 2.5053 | 2.4768 | 2.4495 | 2.4242 | 2.3958 | 2.3695 | 2.3453 | 2.3211 | 2.2989 | 2.2095 | 2.1368 | 2.0779
|  | ARISAIG | CF |  |  |  |  | 2.6316 | 2.6242 | 2.6158 | 2.6074 | 2.6 | 2.5926 | 2.5853 | 2.5768 | 2.5695 | 2.5368 | 2.5137 | 2.4979 | 2.5979 | 2.5895 | 2.5811 | 2.5726 | 2.5642 | 2.5558 | 2.5484 | 2.5389 | 2.5316 | 2.4958 | 2.4695 | 2.4516 | 2.5653 | 2.5568 | 2.5484 | 2.54 | 2.5326 | 2.5242 | 2.5168 | 2.5084 | 2.5 | 2.4653 | 2.4411 | 2.4242
| ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 0 | 9.5947 | 37.5411 | 37.3863 | 37.2295 | 36.9737 | 35.94 | 35.0463 | 34.0242 | 32.7863 | 27.0011 | 24.0589 | 22.7884 | 10.6116 | 36.7242 | 36.0042 | 35.1463 | 34.1179 | 32.9221 | 31.9326 | 30.7979 | 29.4074 | 22.8716 | 19.5863 | 18.1789 | 10.8947 | 38.0189 | 37.2916 | 36.4242 | 35.3726 | 34.1537 | 33.1421 | 31.98 | 30.5611 | 23.9147 | 20.5642 | 19.1305
|  | ASHGROVE | EE |  |  |  |  | 9.6768 | 37.6484 | 37.5158 | 37.3768 | 37.1326 | 36.5379 | 35.7926 | 35.0463 | 34.2358 | 28.1168 | 24.6842 | 22.9411 | 10.7937 | 36.9726 | 36.3042 | 35.4947 | 34.5074 | 33.6179 | 32.8158 | 32.0032 | 31.1168 | 24.2758 | 20.5853 | 18.6611 | 11.0684 | 38.2684 | 37.5916 | 36.7726 | 35.7537 | 34.8316 | 33.9968 | 33.1547 | 32.2368 | 25.2305 | 21.3684 | 19.3884
|  | ASHGROVE | HT |  |  |  |  | 9.5947 | 37.5411 | 37.3863 | 37.2295 | 36.9737 | 35.94 | 35.0463 | 34.0242 | 32.7863 | 27.0011 | 24.0589 | 22.7884 | 10.6116 | 36.7242 | 36.0042 | 35.1463 | 34.1179 | 32.9221 | 31.9326 | 30.7979 | 29.4074 | 22.8716 | 19.5863 | 18.1789 | 10.8947 | 38.0189 | 37.2916 | 36.4242 | 35.3726 | 34.1537 | 33.1421 | 31.98 | 30.5611 | 23.9147 | 20.5642 | 19.1305
|  | ASHGROVE | HE |  |  |  |  | 9.7937 | 37.8063 | 37.7147 | 37.6147 | 37.3937 | 37.1558 | 36.3895 | 35.5463 | 34.6147 | 29.2516 | 26.3663 | 24.9242 | 11.0442 | 37.3126 | 36.7253 | 35.9947 | 35.0684 | 34.2758 | 33.4305 | 32.4916 | 31.4474 | 25.3758 | 22.1958 | 20.7126 | 10.8947 | 38.0189 | 37.2916 | 36.4242 | 35.3726 | 34.1537 | 33.1421 | 31.98 | 30.5611 | 23.9147 | 20.5642 | 19.1305
|  | ASHGROVE | CF |  |  |  |  | 9.8684 | 37.92 | 37.8716 | 37.8211 | 37.7263 | 37.6379 | 37.5495 | 37.4663 | 37.3926 | 35.1442 | 32.9705 | 31.6905 | 11.3063 | 37.8758 | 37.6105 | 37.2916 | 36.8968 | 36.5263 | 36.2442 | 35.8926 | 35.4905 | 31.9737 | 29.5305 | 28.1116 | 11.5042 | 39.1389 | 38.8905 | 38.5905 | 38.1811 | 37.7979 | 37.5053 | 37.1432 | 36.7316 | 33.1632 | 30.6558 | 29.1905
| MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | YES | 0 | 12.26 | 11.8337 | 30.52 | 30.1663 | 29.5979 | 28.9979 | 28.3968 | 27.7337 | 27.0137 | 24.9547 | 22.4453 | 19.7653 | 10.8811 | 10.3726 | 27.4895 | 27.1147 | 26.5768 | 26.0011 | 25.4242 | 24.7947 | 24.0968 | 22.1242 | 19.8895 | 17.5611 | 11.0768 | 10.5716 | 28.4426 | 28.0626 | 27.4732 | 26.8437 | 26.2142 | 25.5184 | 24.7542 | 22.6016 | 20.0384 | 17.3068
|  | ASHLUDIE | EE |  |  |  |  | 12.4895 | 12.1242 | 30.8747 | 30.5947 | 30.0537 | 29.46 | 28.8347 | 28.2695 | 27.6884 | 25.1537 | 22.4453 | 20.0084 | 11.1505 | 10.7179 | 27.9074 | 27.5958 | 27.1021 | 26.5737 | 26.0084 | 25.4895 | 24.9526 | 22.5916 | 20.1611 | 17.5611 | 11.3421 | 10.9095 | 28.85 | 28.5363 | 27.9742 | 27.3626 | 26.7153 | 26.1279 | 25.5226 | 22.8668 | 20.0384 | 17.3068
|  | ASHLUDIE | HT |  |  |  |  | 12.26 | 11.8337 | 30.52 | 30.1663 | 29.5979 | 28.9979 | 28.3968 | 27.7337 | 27.0137 | 24.9768 | 22.78 | 20.6705 | 10.8811 | 10.3726 | 27.4895 | 27.1147 | 26.5768 | 26.0011 | 25.4242 | 24.7947 | 24.0968 | 22.1242 | 19.8895 | 17.5684 | 11.0768 | 10.5716 | 28.4426 | 28.0626 | 27.4732 | 26.8437 | 26.2142 | 25.5184 | 24.7542 | 22.6016 | 20.21 | 17.8279
|  | ASHLUDIE | HE |  |  |  |  | 12.7832 | 12.5305 | 31.3853 | 31.2042 | 30.7337 | 30.3274 | 29.8811 | 29.4189 | 28.9526 | 24.9547 | 22.4968 | 19.7653 | 11.4937 | 11.1895 | 28.4958 | 28.2937 | 27.8705 | 27.4947 | 27.0779 | 26.6537 | 26.2221 | 22.86 | 20.4368 | 17.7137 | 11.0768 | 10.5716 | 28.4426 | 28.0626 | 27.4732 | 26.8437 | 26.2142 | 25.5184 | 24.7542 | 22.6016 | 20.21 | 17.8279
|  | ASHLUDIE | CF |  |  |  |  | 12.9916 | 12.8516 | 31.8179 | 31.7158 | 31.5084 | 31.3126 | 31.1221 | 30.9326 | 30.7663 | 29.7095 | 28.2126 | 26.5211 | 11.7389 | 11.5726 | 29.0147 | 28.8989 | 28.6979 | 28.5074 | 28.32 | 28.1295 | 27.9579 | 26.9063 | 25.4305 | 23.6347 | 11.8832 | 11.7368 | 29.95 | 29.8374 | 29.6111 | 29.3974 | 29.1879 | 28.9795 | 28.7942 | 27.6374 | 26.0121 | 24.1163
| GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | NO | 0 | 1.2758 | 1.2242 | 1.1705 | 1.1189 | 1.0621 | 1.0063 | 0.95684 | 0.90947 | 0.86526 | 0.67579 | 0.5 | 0.34211 | 1.0505 | 0.99053 | 0.92526 | 0.86316 | 0.79474 | 0.72632 | 0.66632 | 0.61053 | 0.55789 | 0.31368 | 0.11053 | -0.067368 | 1.0726 | 1.0095 | 0.94526 | 0.88316 | 0.81474 | 0.74842 | 0.68947 | 0.63263 | 0.58105 | 0.34 | 0.14211 | -0.031579
|  | AULTBEA | EE |  |  |  |  | 1.2979 | 1.2684 | 1.2263 | 1.1821 | 1.1389 | 1.0989 | 1.0589 | 1.0211 | 0.98632 | 0.82526 | 0.70632 | 0.59053 | 1.0716 | 1.0432 | 0.99895 | 0.94632 | 0.89579 | 0.84842 | 0.80211 | 0.75789 | 0.71684 | 0.51684 | 0.35684 | 0.22 | 1.1168 | 1.0663 | 1.0147 | 0.96211 | 0.91158 | 0.86421 | 0.81789 | 0.77263 | 0.73158 | 0.53158 | 0.37263 | 0.23579
|  | AULTBEA | HT |  |  |  |  | 1.2758 | 1.2242 | 1.1705 | 1.1189 | 1.0621 | 1.0063 | 0.95684 | 0.90947 | 0.86526 | 0.67579 | 0.5 | 0.34211 | 1.0505 | 0.99053 | 0.92526 | 0.86316 | 0.79474 | 0.72632 | 0.66632 | 0.61053 | 0.55789 | 0.31368 | 0.11053 | -0.067368 | 1.0726 | 1.0095 | 0.94526 | 0.88316 | 0.81474 | 0.74842 | 0.68947 | 0.63263 | 0.58105 | 0.34 | 0.14211 | -0.031579
|  | AULTBEA | HE |  |  |  |  | 1.3274 | 1.3074 | 1.2874 | 1.2663 | 1.2421 | 1.2189 | 1.1926 | 1.1674 | 1.1442 | 1.06 | 1.0074 | 0.97158 | 1.1021 | 1.0832 | 1.0621 | 1.04 | 1.0158 | 0.99474 | 0.96737 | 0.93895 | 0.91263 | 0.81368 | 0.74526 | 0.69579 | 1.0726 | 1.0095 | 0.94526 | 0.88316 | 0.81474 | 0.74842 | 0.68947 | 0.63263 | 0.58105 | 0.34 | 0.14211 | -0.031579
|  | AULTBEA | CF |  |  |  |  | 1.3453 | 1.3358 | 1.3263 | 1.3158 | 1.3063 | 1.2958 | 1.2853 | 1.2747 | 1.2632 | 1.1968 | 1.1526 | 1.1232 | 1.1211 | 1.1116 | 1.1011 | 1.0905 | 1.08 | 1.0695 | 1.0589 | 1.0474 | 1.0368 | 0.96105 | 0.90211 | 0.86 | 1.1811 | 1.1716 | 1.1611 | 1.1505 | 1.1368 | 1.1179 | 1.0989 | 1.08 | 1.0621 | 0.98 | 0.92105 | 0.88
| BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 0 | 18.2021 | 18.0947 | 17.9842 | 17.6779 | 17.18 | 16.6884 | 16.2442 | 15.9 | 15.7326 | 15 | 14.4147 | 13.9158 | 17.0116 | 16.6853 | 16.3295 | 15.9168 | 15.3526 | 14.7958 | 14.2937 | 13.9084 | 13.7305 | 12.9295 | 12.2842 | 11.7274 | 17.2179 | 16.9947 | 16.6568 | 16.2663 | 15.7347 | 15.2021 | 14.6989 | 14.3137 | 14.1358 | 13.3347 | 12.6884 | 12.1305
|  | AVIEMORE | EE |  |  |  |  | 18.2621 | 18.1747 | 18.0832 | 17.9147 | 17.5516 | 17.1979 | 16.7895 | 16.3884 | 16.1684 | 15.5705 | 15.1189 | 14.7474 | 17.1484 | 16.8663 | 16.5516 | 16.1747 | 15.7653 | 15.3663 | 14.9021 | 14.4463 | 14.2021 | 13.5568 | 13.0568 | 12.64 | 17.2779 | 17.1684 | 16.8705 | 16.5137 | 16.1263 | 15.7505 | 15.3084 | 14.8526 | 14.6074 | 13.9611 | 13.4611 | 13.0442
|  | AVIEMORE | HT |  |  |  |  | 18.2021 | 18.0947 | 17.9842 | 17.6779 | 17.18 | 16.6884 | 16.2442 | 15.9 | 15.7326 | 15 | 14.4147 | 13.9158 | 17.0116 | 16.6853 | 16.3295 | 15.9168 | 15.3526 | 14.7958 | 14.2937 | 13.9084 | 13.7305 | 12.9295 | 12.2842 | 11.7274 | 17.2179 | 16.9947 | 16.6568 | 16.2663 | 15.7347 | 15.2021 | 14.6989 | 14.3137 | 14.1358 | 13.3347 | 12.6884 | 12.1305
|  | AVIEMORE | HE |  |  |  |  | 18.3484 | 18.2874 | 18.2211 | 18.1495 | 17.9253 | 17.62 | 17.2905 | 16.9653 | 16.82 | 16.4168 | 16.2126 | 16.0547 | 17.26 | 17.1168 | 16.8579 | 16.5337 | 16.1716 | 15.8253 | 15.4505 | 15.08 | 14.9189 | 14.4789 | 14.2579 | 14.0811 | 17.2179 | 16.9947 | 16.6568 | 16.2663 | 15.7347 | 15.2021 | 14.6989 | 14.3137 | 14.1358 | 13.3347 | 12.6884 | 12.1305
|  | AVIEMORE | CF |  |  |  |  | 18.4042 | 18.3705 | 18.3358 | 18.3 | 18.2642 | 18.2284 | 18.1916 | 18.0947 | 17.9968 | 17.6263 | 17.4442 | 17.3105 | 17.3232 | 17.2853 | 17.2463 | 17.1337 | 16.9621 | 16.7779 | 16.5842 | 16.3568 | 16.2484 | 15.84 | 15.64 | 15.4895 | 17.42 | 17.3863 | 17.3516 | 17.3158 | 17.2642 | 17.0905 | 16.9084 | 16.6947 | 16.5916 | 16.2021 | 16.0105 | 15.8684
| ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | YES | 0 | 1.3779 | 1.2695 | 1.1663 | 1.0758 | 0.86526 | 0.65263 | 0.41158 | 0.21895 | 0.02421 | -0.46947 | -0.79263 | -1.0768 | 0.99895 | 0.87474 | 0.75579 | 0.65368 | 0.39053 | 0.12632 | -0.14737 | -0.36421 | -0.58316 | -1.0958 | -1.4537 | -1.7716 | 0.9 | 0.78316 | 0.67053 | 0.57263 | 0.31895 | 0.053684 | -0.22 | -0.43579 | -0.65579 | -1.1884 | -1.5474 | -1.8653
|  | BALALDIE | EE |  |  |  |  | 1.4368 | 1.3495 | 1.2632 | 1.1874 | 1.1084 | 1.0379 | 0.85263 | 0.66947 | 0.45368 | -0.16947 | -0.40737 | -0.60105 | 1.0684 | 0.96632 | 0.86842 | 0.78421 | 0.69579 | 0.61789 | 0.38316 | 0.14632 | -0.098947 | -0.76526 | -1.0295 | -1.2463 | 0.96632 | 0.86947 | 0.77684 | 0.69579 | 0.61158 | 0.53579 | 0.31053 | 0.073684 | -0.17158 | -0.85895 | -1.1221 | -1.34
|  | BALALDIE | HT |  |  |  |  | 1.3779 | 1.2695 | 1.1663 | 1.0758 | 0.86526 | 0.65263 | 0.41158 | 0.21895 | 0.02421 | -0.46947 | -0.79263 | -1.0768 | 0.99895 | 0.87474 | 0.75579 | 0.65368 | 0.39053 | 0.12632 | -0.14737 | -0.36421 | -0.58316 | -1.0958 | -1.4537 | -1.7716 | 0.9 | 0.78316 | 0.67053 | 0.57263 | 0.31895 | 0.053684 | -0.22 | -0.43579 | -0.65579 | -1.1884 | -1.5474 | -1.8653
|  | BALALDIE | HE |  |  |  |  | 1.5221 | 1.46 | 1.3979 | 1.3474 | 1.2895 | 1.2421 | 1.0895 | 0.94105 | 0.79474 | 0.33474 | 0.22842 | 0.14105 | 1.1663 | 1.0947 | 1.0242 | 0.96842 | 0.90526 | 0.85263 | 0.66211 | 0.47158 | 0.28 | -0.22842 | -0.34421 | -0.44211 | 0.9 | 0.78316 | 0.67053 | 0.57263 | 0.31895 | 0.053684 | -0.22 | -0.43579 | -0.65579 | -1.1884 | -1.5474 | -1.8653
|  | BALALDIE | CF |  |  |  |  | 1.58 | 1.5411 | 1.5042 | 1.4737 | 1.4432 | 1.4137 | 1.3832 | 1.2979 | 1.2074 | 0.87474 | 0.78421 | 0.71474 | 1.2337 | 1.1884 | 1.1453 | 1.1105 | 1.0758 | 1.0421 | 1.0084 | 0.90105 | 0.78737 | 0.36105 | 0.25684 | 0.17895 | 1.1221 | 1.0789 | 1.0389 | 1.0053 | 0.97263 | 0.94105 | 0.90842 | 0.80947 | 0.70632 | 0.28947 | 0.18526 | 0.10632
| ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 0.145 | 7.1855 | 7.0161 | 6.8339 | 6.6234 | 5.9918 | 5.2329 | 4.4382 | 3.7234 | 2.9803 | -2.7145 | -9.5218 | -14.4313 | 6.0761 | 5.8697 | 5.6708 | 5.4382 | 4.8876 | 4.2876 | 3.6318 | 3.0487 | 2.4234 | -2.9713 | -9.5755 | -14.8713 | 6.3297 | 6.1213 | 5.9182 | 5.6834 | 5.015 | 4.215 | 3.3971 | 2.6761 | 1.9224 | -4.2282 | -11.605 | -17.0966
|  | BALBEGGIE | EE |  |  |  |  | 7.2339 | 7.1424 | 6.9929 | 6.8139 | 6.075 | 5.2329 | 4.4382 | 3.7234 | 2.9803 | -2.7145 | -9.5218 | -14.4313 | 6.1855 | 6.0276 | 5.8624 | 5.6697 | 5.0276 | 4.2876 | 3.6318 | 3.0487 | 2.4234 | -2.9713 | -9.5755 | -14.8713 | 6.4371 | 6.2718 | 6.0992 | 5.8992 | 5.1118 | 4.215 | 3.3971 | 2.6761 | 1.9224 | -4.2282 | -11.605 | -17.0966
|  | BALBEGGIE | HT |  |  |  |  | 7.1855 | 7.0161 | 6.8339 | 6.6234 | 5.9918 | 5.3961 | 4.7939 | 4.0634 | 3.2687 | -2.1039 | -8.0955 | -12.1071 | 6.0761 | 5.8697 | 5.6708 | 5.4382 | 4.8876 | 4.3676 | 3.8339 | 3.2003 | 2.5087 | -2.9282 | -9.3597 | -13.8397 | 6.3297 | 6.1213 | 5.9182 | 5.6834 | 5.015 | 4.3855 | 3.7466 | 2.9824 | 2.1582 | -3.7418 | -10.4597 | -15.0629
|  | BALBEGGIE | HE |  |  |  |  | 7.2939 | 7.2476 | 7.195 | 7.0718 | 6.3276 | 5.6897 | 5.0992 | 4.395 | 3.4118 | -0.85553 | -6.0197 | -11.6313 | 6.3034 | 6.1971 | 6.0803 | 5.9245 | 5.2876 | 4.7234 | 4.215 | 3.5897 | 2.6108 | -1.4839 | -6.6713 | -12.3166 | 6.3297 | 6.1213 | 5.9182 | 5.6834 | 5.015 | 4.3855 | 3.7466 | 2.9824 | 2.1582 | -3.7418 | -10.4597 | -15.0629
|  | BALBEGGIE | CF |  |  |  |  | 7.3339 | 7.3076 | 7.2803 | 7.2518 | 7.0318 | 6.7992 | 6.5361 | 6.1434 | 5.6982 | 3.5561 | 0.30658 | -3.1997 | 6.3845 | 6.3434 | 6.2918 | 6.2318 | 5.9982 | 5.7687 | 5.5308 | 5.1182 | 4.6203 | 2.4445 | -0.83974 | -4.5703 | 6.6297 | 6.5887 | 6.5371 | 6.4771 | 6.1855 | 5.9066 | 5.6234 | 5.1761 | 4.6571 | 2.2834 | -1.2745 | -5.2018
| MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | YES | 0.029 | 20.231 | 19.9552 | 19.5257 | 18.9036 | 18.0763 | 16.7299 | 16.291 | 15.8836 | 15.4647 | 14.8552 | 14.5436 | 14.2763 | 20.5531 | 20.2468 | 19.7468 | 19.0057 | 18.0342 | 17.1657 | 16.6668 | 16.1878 | 15.7257 | 15.0689 | 14.4521 | 13.9552 | 20.0236 | 19.7173 | 19.2163 | 18.4752 | 17.4984 | 16.9089 | 16.2521 | 15.6426 | 15.3952 | 14.4973 | 13.8668 | 13.3668
|  | BALDOVIE | EE |  |  |  |  | 20.4152 | 20.2015 | 19.8247 | 19.3194 | 18.6626 | 18.1615 | 17.6731 | 17.2163 | 16.7415 | 15.8405 | 15.2952 | 14.9352 | 20.7615 | 20.5257 | 20.0836 | 19.4836 | 18.7026 | 18.1205 | 17.5699 | 17.0605 | 16.5321 | 15.611 | 15.0742 | 14.6994 | 20.2321 | 19.9952 | 19.5531 | 18.9531 | 18.1657 | 17.5836 | 17.0268 | 16.511 | 15.9773 | 15.0247 | 14.4531 | 14.0678
|  | BALDOVIE | HT |  |  |  |  | 20.231 | 19.9552 | 19.5257 | 18.9036 | 18.0763 | 17.5584 | 16.9763 | 16.4299 | 16.1931 | 15.3405 | 14.7447 | 14.2763 | 20.5531 | 20.2468 | 19.7468 | 19.0057 | 18.0342 | 17.4447 | 16.7921 | 16.1878 | 15.9468 | 15.0689 | 14.4521 | 13.9552 | 20.0236 | 19.7173 | 19.2163 | 18.4752 | 17.4984 | 16.9089 | 16.2521 | 15.6426 | 15.3952 | 14.4973 | 13.8668 | 13.3668
|  | BALDOVIE | HE |  |  |  |  | 20.6321 | 20.4015 | 20.0805 | 19.6226 | 19.0057 | 16.7299 | 16.291 | 15.8836 | 15.4647 | 14.8552 | 14.5436 | 14.2952 | 21.0036 | 20.7363 | 20.3573 | 19.8068 | 19.0678 | 17.1657 | 16.6668 | 16.2047 | 15.7257 | 15.0952 | 14.7889 | 14.5478 | 20.0236 | 19.7173 | 19.2163 | 18.4752 | 17.4984 | 16.9089 | 16.2521 | 15.6426 | 15.3952 | 14.4973 | 13.8668 | 13.3668
|  | BALDOVIE | CF |  |  |  |  | 20.7489 | 20.6878 | 20.5973 | 20.5068 | 20.4068 | 20.2531 | 20.0647 | 19.8689 | 19.6478 | 18.7152 | 18.1089 | 17.9531 | 21.1647 | 21.0678 | 20.9678 | 20.8678 | 20.7605 | 20.5847 | 20.3657 | 20.1363 | 19.8742 | 18.7784 | 18.0889 | 17.9289 | 20.6226 | 20.5289 | 20.4321 | 20.3352 | 20.2289 | 20.051 | 19.831 | 19.5994 | 19.3352 | 18.2299 | 17.5289 | 17.3605
| TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | YES | 0 | 11.9063 | 11.8189 | 11.6568 | 11.4189 | 11.2032 | 10.9758 | 10.7495 | 10.4789 | 10.1537 | 5.88 | 5.46 | 5.0737 | 11.98 | 11.7337 | 11.4695 | 11.1884 | 10.9411 | 10.6821 | 10.4179 | 10.0979 | 9.7116 | 6.1358 | 5.6726 | 5.24 | 11.6884 | 11.46 | 11.2084 | 10.9389 | 10.6968 | 10.4368 | 10.1716 | 9.8537 | 9.4663 | 5.0705 | 4.6105 | 4.1811
|  | BALLATER | EE |  |  |  |  | 11.9568 | 11.8863 | 11.8126 | 11.7126 | 11.5211 | 11.2895 | 11.1253 | 10.9526 | 10.7484 | 6.2042 | 5.8853 | 5.6158 | 12.1137 | 11.9474 | 11.7558 | 11.5484 | 11.3168 | 11.0442 | 10.8568 | 10.6589 | 10.42 | 6.4926 | 6.1463 | 5.8453 | 11.8105 | 11.6568 | 11.4768 | 11.2779 | 11.0568 | 10.7926 | 10.6084 | 10.4074 | 10.1674 | 5.4168 | 5.0663 | 4.7653
|  | BALLATER | HT |  |  |  |  | 11.9063 | 11.8189 | 11.6568 | 11.4189 | 11.2032 | 10.9758 | 10.7495 | 10.4789 | 10.1537 | 5.88 | 5.46 | 5.0737 | 11.98 | 11.7337 | 11.4695 | 11.1884 | 10.9411 | 10.6821 | 10.4179 | 10.0979 | 9.7116 | 6.1358 | 5.6726 | 5.24 | 11.6884 | 11.46 | 11.2084 | 10.9389 | 10.6968 | 10.4368 | 10.1716 | 9.8537 | 9.4663 | 5.0705 | 4.6105 | 4.1811
|  | BALLATER | HE |  |  |  |  | 12.0274 | 11.9789 | 11.9274 | 11.8737 | 11.74 | 11.5284 | 11.3505 | 11.1442 | 10.8937 | 8.6221 | 8.4642 | 8.3284 | 12.2653 | 12.1284 | 11.9632 | 11.7695 | 11.5537 | 11.2979 | 11.0853 | 10.8368 | 10.5358 | 8.5474 | 8.3758 | 8.2242 | 11.6884 | 11.46 | 11.2084 | 10.9389 | 10.6968 | 10.4368 | 10.1716 | 9.8537 | 9.4663 | 5.0705 | 4.6105 | 4.1811
|  | BALLATER | CF |  |  |  |  | 12.0726 | 12.0474 | 12.0211 | 11.9947 | 11.9674 | 11.94 | 11.9126 | 11.8842 | 11.8568 | 11.1253 | 10.9895 | 10.8947 | 12.3863 | 12.3295 | 12.2695 | 12.2042 | 12.1379 | 12.0558 | 11.9579 | 11.8674 | 11.7379 | 10.7905 | 10.6389 | 10.5274 | 12.0053 | 11.98 | 11.9526 | 11.8926 | 11.8326 | 11.7579 | 11.6705 | 11.5863 | 11.4653 | 10.5484 | 10.3937 | 10.2811
| CARRADALE 1 | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0 | 0.94526 | 0.92316 | 0.90105 | 0.87684 | 0.82842 | 0.77579 | 0.72316 | 0.67474 | 0.62737 | 0.38421 | 0.14947 | 0.038947 | 0.94842 | 0.92526 | 0.90316 | 0.88 | 0.84421 | 0.80632 | 0.76211 | 0.72 | 0.67895 | 0.46947 | 0.27579 | 0.17789 | 0.94 | 0.91474 | 0.89263 | 0.86737 | 0.81895 | 0.76526 | 0.71158 | 0.66421 | 0.61474 | 0.35895 | 0.11579 | -0.003158
|  | BALLIEKINE | EE |  |  |  |  | 0.95053 | 0.92737 | 0.90105 | 0.87684 | 0.82842 | 0.77579 | 0.72316 | 0.67474 | 0.62737 | 0.38421 | 0.14947 | 0.038947 | 0.95895 | 0.93684 | 0.91263 | 0.89053 | 0.85053 | 0.80737 | 0.76211 | 0.72 | 0.67895 | 0.46947 | 0.27579 | 0.17789 | 0.94737 | 0.92105 | 0.89368 | 0.86737 | 0.81895 | 0.76526 | 0.71158 | 0.66421 | 0.61474 | 0.35895 | 0.11579 | -0.003158
|  | BALLIEKINE | HT |  |  |  |  | 0.94526 | 0.92316 | 0.90211 | 0.88 | 0.84 | 0.79895 | 0.76 | 0.71368 | 0.66842 | 0.49053 | 0.36421 | 0.28632 | 0.94842 | 0.92526 | 0.90316 | 0.88 | 0.84421 | 0.80632 | 0.77053 | 0.72947 | 0.69158 | 0.53895 | 0.42947 | 0.35895 | 0.94 | 0.91474 | 0.89263 | 0.86842 | 0.82842 | 0.78526 | 0.74526 | 0.69895 | 0.65474 | 0.46947 | 0.33579 | 0.25263
|  | BALLIEKINE | HE |  |  |  |  | 0.97474 | 0.96211 | 0.94947 | 0.93895 | 0.89684 | 0.86316 | 0.82737 | 0.79368 | 0.76211 | 0.61158 | 0.47895 | 0.34 | 0.98211 | 0.97053 | 0.95684 | 0.94632 | 0.91263 | 0.88316 | 0.85474 | 0.82632 | 0.79789 | 0.67053 | 0.56105 | 0.44842 | 0.94 | 0.91474 | 0.89263 | 0.86842 | 0.82842 | 0.78526 | 0.74526 | 0.69895 | 0.65474 | 0.46947 | 0.33579 | 0.25263
|  | BALLIEKINE | CF |  |  |  |  | 0.98526 | 0.98 | 0.97263 | 0.96737 | 0.95053 | 0.93474 | 0.92105 | 0.90842 | 0.89684 | 0.82842 | 0.75053 | 0.69263 | 0.99368 | 0.98737 | 0.98 | 0.97368 | 0.96105 | 0.94526 | 0.93263 | 0.92 | 0.91158 | 0.84947 | 0.78211 | 0.73579 | 0.98421 | 0.97895 | 0.97053 | 0.96526 | 0.94947 | 0.93158 | 0.91789 | 0.90421 | 0.89263 | 0.82421 | 0.74421 | 0.68421
| BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | YES | 0.1 | 14.1924 | 14.0976 | 14.0071 | 13.9176 | 13.5724 | 13.1292 | 12.6482 | 12.2303 | 11.725 | 7.8124 | 3.3534 | -0.005526 | 11.9821 | 11.8874 | 11.7926 | 11.7011 | 11.42 | 11.0705 | 10.6674 | 10.3168 | 9.7368 | 6.1284 | 1.7789 | -1.8063 | 13.5125 | 13.4136 | 13.3178 | 13.2241 | 12.8599 | 12.4072 | 11.9178 | 11.4904 | 11.0146 | 6.7862 | 1.9262 | -1.8296
|  | BALLINDALLOCH | EE |  |  |  |  | 14.245 | 14.1587 | 14.0745 | 13.9892 | 13.5987 | 13.1292 | 12.6482 | 12.2303 | 11.805 | 7.8124 | 3.3534 | -0.005526 | 12.0389 | 11.9558 | 11.8737 | 11.7895 | 11.4674 | 11.0705 | 10.6674 | 10.3168 | 9.9579 | 6.1284 | 1.7863 | -1.8063 | 13.5683 | 13.4788 | 13.3904 | 13.2988 | 12.8883 | 12.4072 | 11.9178 | 11.4904 | 11.0557 | 6.7862 | 1.9262 | -1.8296
|  | BALLINDALLOCH | HT |  |  |  |  | 14.1924 | 14.0976 | 14.0071 | 13.9176 | 13.5724 | 13.2271 | 12.8745 | 12.4597 | 11.7955 | 8.1682 | 4.0997 | 1.3418 | 11.9821 | 11.8874 | 11.7926 | 11.7011 | 11.42 | 11.1158 | 10.8126 | 10.4611 | 9.8284 | 6.1789 | 1.7789 | -1.3263 | 13.5125 | 13.4136 | 13.3178 | 13.2241 | 12.8599 | 12.4999 | 12.1388 | 11.7167 | 11.0146 | 7.0525 | 2.4725 | -0.70224
|  | BALLINDALLOCH | HE |  |  |  |  | 14.2892 | 14.2639 | 14.2292 | 14.1839 | 13.7808 | 13.3145 | 12.8366 | 12.3797 | 11.725 | 8.9387 | 5.5018 | 1.7618 | 12.0853 | 12.0611 | 12.0263 | 11.9811 | 11.6516 | 11.2253 | 10.7884 | 10.3747 | 9.7368 | 7.0663 | 3.6011 | -0.17579 | 13.5125 | 13.4136 | 13.3178 | 13.2241 | 12.8599 | 12.4999 | 12.1388 | 11.7167 | 11.0146 | 7.0525 | 2.4725 | -0.70224
|  | BALLINDALLOCH | CF |  |  |  |  | 14.3082 | 14.2934 | 14.2808 | 14.265 | 14.1155 | 13.9776 | 13.7682 | 13.4882 | 13.1734 | 11.7376 | 9.5703 | 7.185 | 12.1042 | 12.0905 | 12.0789 | 12.0642 | 11.9495 | 11.8337 | 11.6347 | 11.3526 | 11.0253 | 9.5937 | 7.3968 | 4.8274 | 13.6325 | 13.6178 | 13.6041 | 13.5883 | 13.4304 | 13.2841 | 13.062 | 12.7599 | 12.4199 | 10.8725 | 8.4914 | 5.8146
| CARRADALE 1 | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 0 | 2.2168 | 2.1895 | 2.1621 | 1.5989 | 1.5705 | 1.5368 | 1.5053 | 1.3095 | 1.04 | -0.58105 | -2.4411 | -3.3095 | 2.1253 | 2.0853 | 2.0453 | 1.5095 | 1.4716 | 1.4326 | 1.3968 | 1.2316 | 1.0095 | -0.35684 | -1.96 | -2.7989 | 2.0453 | 2.0011 | 1.9579 | 1.3179 | 1.2768 | 1.2347 | 1.1958 | 1 | 0.73684 | -0.89053 | -2.8 | -3.7505
|  | BALLURE | EE |  |  |  |  | 2.2263 | 2.1979 | 2.1674 | 1.6021 | 1.5716 | 1.5421 | 1.5095 | 1.3789 | 1.1074 | -0.58105 | -2.4411 | -3.3095 | 2.1453 | 2.1074 | 2.0684 | 1.5337 | 1.4958 | 1.46 | 1.4242 | 1.3105 | 1.0821 | -0.35684 | -1.96 | -2.7989 | 2.0674 | 2.0242 | 1.9821 | 1.3421 | 1.3 | 1.26 | 1.2211 | 1.0863 | 0.81579 | -0.89053 | -2.8 | -3.7505
|  | BALLURE | HT |  |  |  |  | 2.2168 | 2.1895 | 2.1621 | 1.5989 | 1.5705 | 1.5368 | 1.5053 | 1.3095 | 1.04 | -0.23684 | -1.3021 | -1.9021 | 2.1253 | 2.0853 | 2.0453 | 1.5095 | 1.4716 | 1.4326 | 1.3968 | 1.2316 | 1.0095 | -0.11895 | -1.1463 | -1.7568 | 2.0453 | 2.0011 | 1.9579 | 1.3179 | 1.2768 | 1.2347 | 1.1958 | 1 | 0.73684 | -0.59053 | -1.7653 | -2.4432
|  | BALLURE | HE |  |  |  |  | 2.2411 | 2.2295 | 2.2158 | 1.9326 | 1.9189 | 1.7695 | 1.5726 | 1.56 | 1.3063 | 0.092632 | -1.1484 | -2.4842 | 2.1747 | 2.1579 | 2.1379 | 1.8705 | 1.8516 | 1.7063 | 1.5032 | 1.4705 | 1.2379 | 0.19684 | -0.89789 | -2.0947 | 2.0453 | 2.0011 | 1.9579 | 1.3179 | 1.2768 | 1.2347 | 1.1958 | 1 | 0.73684 | -0.59053 | -1.7653 | -2.4432
|  | BALLURE | CF |  |  |  |  | 2.2505 | 2.2432 | 2.2347 | 2.2274 | 2.1389 | 2.0621 | 1.9842 | 1.9179 | 1.8684 | 1.38 | 0.62 | -0.042105 | 2.1916 | 2.18 | 2.1684 | 2.1568 | 2.0705 | 1.9947 | 1.9179 | 1.8347 | 1.7516 | 1.2779 | 0.60316 | -0.022105 | 2.1158 | 2.1032 | 2.0905 | 2.0779 | 1.9758 | 1.8853 | 1.7947 | 1.6979 | 1.6011 | 1.0432 | 0.24632 | -0.47579
| DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | NO | YES | 0 | 5.2032 | 4.6042 | 3.6705 | 2.4916 | 1.0874 | -0.26526 | -1.0611 | -1.64 | -4.5063 | -6.0979 | -7.1895 | -7.8568 | 4.3084 | 3.7211 | 2.6684 | 1.2947 | -0.24421 | -1.6726 | -2.44 | -2.9737 | -5.1211 | -6.5042 | -7.4863 | -8.1474 | 4.9347 | 4.2274 | 3.1232 | 1.7232 | 0.097895 | -1.4495 | -2.3158 | -2.9326 | -5.74 | -7.36 | -8.4905 | -9.2105
|  | BALMEDIE | EE |  |  |  |  | 5.3663 | 5.0284 | 4.2747 | 3.2032 | 1.5811 | -0.26526 | -1.0611 | -1.64 | -1.8021 | -4.0074 | -6.0937 | -6.9379 | 4.4853 | 4.1716 | 3.3611 | 2.1295 | 0.35895 | -1.6726 | -2.44 | -2.9737 | -3.1526 | -4.9421 | -6.6568 | -7.4126 | 5.0347 | 4.7358 | 3.8358 | 2.5642 | 0.68632 | -1.4495 | -2.3158 | -2.9326 | -3.1126 | -5.3568 | -7.4495 | -8.3263
|  | BALMEDIE | HT |  |  |  |  | 5.2032 | 4.6042 | 3.6705 | 2.4916 | 1.0874 | 0.23053 | -0.61684 | -1.3042 | -4.5063 | -6.0979 | -7.1895 | -7.8568 | 4.3084 | 3.7211 | 2.6684 | 1.2947 | -0.24421 | -1.1432 | -2.0274 | -2.6926 | -5.1211 | -6.5042 | -7.4863 | -8.1474 | 4.9347 | 4.2274 | 3.1232 | 1.7232 | 0.097895 | -0.86526 | -1.8168 | -2.5611 | -5.74 | -7.36 | -8.4905 | -9.2105
|  | BALMEDIE | HE |  |  |  |  | 5.4358 | 5.3884 | 4.9474 | 4.2 | 2.9821 | 1.7505 | 0.96526 | 0.40211 | -1.7063 | -3.5326 | -5.1937 | -6.9084 | 4.5789 | 4.4526 | 4.0821 | 3.2526 | 1.9768 | 0.64947 | -0.15158 | -0.69368 | -2.2811 | -3.9368 | -5.4421 | -6.9821 | 4.9347 | 4.2274 | 3.1232 | 1.7232 | 0.097895 | -0.86526 | -1.8168 | -2.5611 | -5.74 | -7.36 | -8.4905 | -9.2105
|  | BALMEDIE | CF |  |  |  |  | 5.4779 | 5.4516 | 5.4253 | 5.3168 | 4.9516 | 4.4516 | 3.9032 | 3.5768 | 1.5968 | 0.40105 | -0.64421 | -1.4653 | 4.6337 | 4.5968 | 4.5337 | 4.4147 | 4.1379 | 3.6316 | 3.0495 | 2.7105 | 1.2253 | 0.038947 | -0.92105 | -1.6958 | 5.1463 | 5.12 | 5.0937 | 5.0516 | 4.6463 | 4.0653 | 3.4295 | 3.06 | 1.0695 | -0.24421 | -1.3474 | -2.2263
| CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | YES | 0.947 | 10.3298 | 10.273 | 10.2151 | 10.1551 | 10.0898 | 10.0235 | 9.9604 | 9.8951 | 9.833 | 9.5856 | 9.3825 | 9.213 | 10.3709 | 10.3077 | 10.2446 | 10.1804 | 10.1098 | 10.0404 | 9.973 | 9.9035 | 9.8372 | 9.5719 | 9.3477 | 9.1562 | 10.2319 | 10.1719 | 10.1098 | 10.0467 | 9.9772 | 9.9077 | 9.8414 | 9.773 | 9.7077 | 9.4446 | 9.2256 | 9.0414
|  | BALNAGASK | EE |  |  |  |  | 10.3741 | 10.3319 | 10.2877 | 10.2435 | 10.193 | 10.1414 | 10.0898 | 10.0425 | 9.9951 | 9.773 | 9.6046 | 9.4783 | 10.4193 | 10.373 | 10.3246 | 10.2751 | 10.2225 | 10.1688 | 10.1151 | 10.0656 | 10.0141 | 9.7835 | 9.6035 | 9.4604 | 10.2793 | 10.2341 | 10.1877 | 10.1404 | 10.0867 | 10.033 | 9.9793 | 9.9298 | 9.8783 | 9.6467 | 9.4646 | 9.3256
|  | BALNAGASK | HT |  |  |  |  | 10.3298 | 10.273 | 10.2151 | 10.1551 | 10.0898 | 10.0235 | 9.9604 | 9.8951 | 9.833 | 9.5856 | 9.3825 | 9.213 | 10.3709 | 10.3077 | 10.2446 | 10.1804 | 10.1098 | 10.0404 | 9.973 | 9.9035 | 9.8372 | 9.5719 | 9.3477 | 9.1562 | 10.2319 | 10.1719 | 10.1098 | 10.0467 | 9.9772 | 9.9077 | 9.8414 | 9.773 | 9.7077 | 9.4446 | 9.2256 | 9.0414
|  | BALNAGASK | HE |  |  |  |  | 10.393 | 10.3688 | 10.3383 | 10.3014 | 10.2583 | 10.2183 | 10.1804 | 10.1425 | 10.1077 | 9.9698 | 9.8709 | 9.793 | 10.4404 | 10.4162 | 10.3846 | 10.3446 | 10.3004 | 10.2604 | 10.2204 | 10.1814 | 10.1456 | 10.0025 | 9.8983 | 9.8151 | 10.2319 | 10.1719 | 10.1098 | 10.0467 | 9.9772 | 9.9077 | 9.8414 | 9.773 | 9.7077 | 9.4446 | 9.2256 | 9.0414
|  | BALNAGASK | CF |  |  |  |  | 10.4035 | 10.3867 | 10.3688 | 10.3498 | 10.3277 | 10.3014 | 10.2741 | 10.2477 | 10.2225 | 10.1046 | 10.0256 | 9.9698 | 10.4509 | 10.4341 | 10.4162 | 10.3972 | 10.3741 | 10.3456 | 10.3183 | 10.2909 | 10.2635 | 10.1404 | 10.0541 | 9.993 | 10.3109 | 10.2941 | 10.2762 | 10.2572 | 10.233 | 10.2056 | 10.1783 | 10.1498 | 10.1235 | 10.0004 | 9.9151 | 9.8551
| KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 2.004 | 13.5549 | 12.8802 | 36.6192 | 35.9497 | 34.9981 | 34.1318 | 33.3581 | 32.5318 | 31.7244 | 28.5002 | 22.9455 | 21.3686 | 10.8097 | 10.0213 | 33.0181 | 32.2465 | 31.276 | 30.4086 | 29.6592 | 28.8813 | 28.1286 | 25.5465 | 21.0718 | 19.5476 | 11.7597 | 11.0018 | 34.6865 | 33.9507 | 32.9286 | 32.0055 | 31.1844 | 30.3139 | 29.4665 | 26.2318 | 20.6139 | 18.9255
|  | BANCHORY | EE |  |  |  |  | 13.8402 | 13.276 | 37.1402 | 36.4876 | 35.4992 | 34.4549 | 33.6202 | 32.8802 | 32.1181 | 28.5002 | 22.9455 | 21.3686 | 11.1349 | 10.4813 | 33.6318 | 32.8686 | 31.8792 | 30.8644 | 30.1128 | 29.4434 | 28.7486 | 25.5792 | 21.0718 | 19.5476 | 12.0734 | 11.4397 | 35.2686 | 34.5328 | 33.4728 | 32.3749 | 31.5118 | 30.7465 | 29.9549 | 26.2318 | 20.6139 | 18.9255
|  | BANCHORY | HT |  |  |  |  | 13.5549 | 12.8802 | 36.6192 | 35.9497 | 34.9981 | 34.1318 | 33.3581 | 32.5318 | 31.7244 | 28.8971 | 24.7002 | 23.1413 | 10.8097 | 10.0213 | 33.0181 | 32.2465 | 31.276 | 30.4086 | 29.6592 | 28.8813 | 28.1286 | 25.5465 | 21.9792 | 20.2834 | 11.7597 | 11.0018 | 34.6865 | 33.9507 | 32.9286 | 32.0055 | 31.1844 | 30.3139 | 29.4665 | 26.5181 | 22.2213 | 20.4528
|  | BANCHORY | HE |  |  |  |  | 14.1707 | 13.7318 | 37.7097 | 37.1665 | 36.1349 | 35.256 | 34.6213 | 34.0244 | 33.4539 | 31.1034 | 28.0044 | 25.0876 | 11.5076 | 10.9844 | 34.2518 | 33.6023 | 32.5623 | 31.6634 | 31.0813 | 30.5455 | 30.0413 | 28.0413 | 25.5434 | 22.7549 | 11.7597 | 11.0018 | 34.6865 | 33.9507 | 32.9286 | 32.0055 | 31.1844 | 30.3139 | 29.4665 | 26.5181 | 22.2213 | 20.4528
|  | BANCHORY | CF |  |  |  |  | 14.4402 | 14.2392 | 38.5265 | 38.3065 | 37.9234 | 37.5371 | 37.1749 | 36.8844 | 36.6128 | 35.2676 | 33.9686 | 32.2402 | 11.8202 | 11.5844 | 35.2286 | 34.9686 | 34.5865 | 34.1886 | 33.8202 | 33.5339 | 33.2507 | 31.9707 | 30.8539 | 29.0339 | 12.7323 | 12.506 | 36.8118 | 36.5634 | 36.1528 | 35.7339 | 35.3423 | 35.0339 | 34.7402 | 33.3244 | 31.9907 | 30.0792
| TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | 0.52 | -1.06 | -1.1084 | -1.2516 | -1.4242 | -1.5968 | -1.7442 | -1.8916 | -2.0221 | -2.1358 | -2.9495 | -3.7084 | -3.8947 | -0.60211 | -0.7021 | -0.86105 | -1.0442 | -1.2326 | -1.3958 | -1.5611 | -1.7053 | -1.8305 | -2.4968 | -3.1042 | -3.3053 | -0.82737 | -0.94 | -1.1095 | -1.3053 | -1.5011 | -1.6663 | -1.8326 | -1.9789 | -2.1063 | -2.9211 | -3.6768 | -3.8853
|  | BARCALDINE | EE |  |  |  |  | -1.0358 | -1.08 | -1.1716 | -1.3284 | -1.4916 | -1.6505 | -1.7663 | -1.8737 | -1.9874 | -1.0074 | -1.7411 | -1.9021 | -0.57474 | -0.63263 | -0.77368 | -0.94 | -1.1116 | -1.28 | -1.4011 | -1.5168 | -1.6411 | 0.038947 | -0.58105 | -0.73053 | -0.77368 | -0.86947 | -1.0211 | -1.1989 | -1.3853 | -1.5684 | -1.6979 | -1.8168 | -1.9474 | -0.7221 | -1.4526 | -1.6326
|  | BARCALDINE | HT |  |  |  |  | -1.06 | -1.1084 | -1.2516 | -1.4242 | -1.5968 | -1.7442 | -1.8916 | -2.0221 | -2.1358 | -2.9495 | -3.7084 | -3.8947 | -0.60211 | -0.7021 | -0.86105 | -1.0442 | -1.2326 | -1.3958 | -1.5611 | -1.7053 | -1.8305 | -2.4968 | -3.1042 | -3.3053 | -0.82737 | -0.94 | -1.1095 | -1.3053 | -1.5011 | -1.6663 | -1.8326 | -1.9789 | -2.1063 | -2.9211 | -3.6768 | -3.8853
|  | BARCALDINE | HE |  |  |  |  | -0.99158 | -1.0189 | -1.0484 | -1.1684 | -1.3232 | -1.4768 | -1.5726 | -1.6589 | -1.7232 | -2.1295 | -2.4937 | -2.5653 | -0.53368 | -0.56 | -0.63053 | -0.77684 | -0.9421 | -1.1116 | -1.2168 | -1.3137 | -1.3842 | -1.7116 | -1.9958 | -2.0684 | -0.82737 | -0.94 | -1.1095 | -1.3053 | -1.5011 | -1.6663 | -1.8326 | -1.9789 | -2.1063 | -2.9211 | -3.6768 | -3.8853
|  | BARCALDINE | CF |  |  |  |  | -0.96632 | -0.97895 | -0.99263 | -1.0063 | -1.0211 | -1.0411 | -1.1053 | -1.1547 | -1.2137 | -1.3768 | -1.4463 | -1.4979 | -0.50947 | -0.52211 | -0.53474 | -0.54842 | -0.59263 | -0.64316 | -0.71158 | -0.76526 | -0.82842 | -0.99895 | -1.0716 | -1.1295 | -0.63263 | -0.66316 | -0.71579 | -0.78 | -0.82842 | -0.88211 | -0.95474 | -1.0126 | -1.08 | -1.2621 | -1.3389 | -1.3989
| STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 0 | 2.6389 | 6.3779 | 6.3147 | 6.2516 | 6.1821 | 6.1158 | 6.0526 | 5.9916 | 5.9 | 5.5337 | 5.2389 | 4.9884 | 2.3958 | 6.1347 | 6.06 | 5.9453 | 5.8295 | 5.7168 | 5.6105 | 5.5063 | 5.4074 | 5.0032 | 4.6747 | 4.3926 | 2.5347 | 6.2737 | 6.1884 | 6.0747 | 5.9589 | 5.8463 | 5.74 | 5.6358 | 5.5368 | 5.1337 | 4.8063 | 4.5242
|  | BARVAS | EE |  |  |  |  | 2.6716 | 6.4211 | 6.3674 | 6.3126 | 6.2568 | 6.2032 | 6.1516 | 6.1032 | 6.0568 | 5.8242 | 5.6032 | 5.4221 | 2.4284 | 6.1779 | 6.1242 | 6.0695 | 5.9968 | 5.9084 | 5.8232 | 5.7421 | 5.6632 | 5.3274 | 5.0811 | 4.8758 | 2.5674 | 6.3168 | 6.2632 | 6.2084 | 6.1263 | 6.0379 | 5.9526 | 5.8716 | 5.7937 | 5.4568 | 5.2116 | 5.0074
|  | BARVAS | HT |  |  |  |  | 2.6389 | 6.3779 | 6.3147 | 6.2516 | 6.1821 | 6.1158 | 6.0526 | 5.9916 | 5.9 | 5.5337 | 5.2389 | 4.9884 | 2.3958 | 6.1347 | 6.06 | 5.9453 | 5.8295 | 5.7168 | 5.6105 | 5.5063 | 5.4074 | 5.0032 | 4.6747 | 4.3926 | 2.5347 | 6.2737 | 6.1884 | 6.0747 | 5.9589 | 5.8463 | 5.74 | 5.6358 | 5.5368 | 5.1337 | 4.8063 | 4.5242
|  | BARVAS | HE |  |  |  |  | 2.7221 | 6.4863 | 6.4484 | 6.4074 | 6.3653 | 6.3253 | 6.2863 | 6.2495 | 6.2168 | 6.1063 | 6.0516 | 6.0242 | 2.4789 | 6.2432 | 6.2053 | 6.1642 | 6.1221 | 6.0821 | 6.0432 | 6.0063 | 5.9737 | 5.8253 | 5.6989 | 5.6053 | 2.5347 | 6.2737 | 6.1884 | 6.0747 | 5.9589 | 5.8463 | 5.74 | 5.6358 | 5.5368 | 5.1337 | 4.8063 | 4.5242
|  | BARVAS | CF |  |  |  |  | 2.7537 | 6.5347 | 6.5147 | 6.4947 | 6.4747 | 6.4537 | 6.4326 | 6.4126 | 6.3916 | 6.3032 | 6.26 | 6.2389 | 2.5105 | 6.2916 | 6.2716 | 6.2516 | 6.2316 | 6.2105 | 6.1895 | 6.1695 | 6.1484 | 6.06 | 5.9589 | 5.8737 | 2.6495 | 6.4305 | 6.4105 | 6.3905 | 6.3705 | 6.3495 | 6.3284 | 6.3084 | 6.2874 | 6.1989 | 6.0884 | 6.0042
| STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 0 | 29.7537 | 29.32 | 28.9253 | 28.5684 | 28.14 | 27.6063 | 27.0674 | 26.4526 | 25.7189 | 23.7032 | 22.5263 | 21.6168 | 27.9295 | 27.4411 | 27.0021 | 26.6095 | 26.1705 | 25.5947 | 25.0116 | 24.3389 | 23.5126 | 21.3305 | 20.08 | 19.0611 | 28.0089 | 27.5142 | 27.0689 | 26.6732 | 26.2132 | 25.6142 | 25.0058 | 24.3026 | 23.4437 | 21.1479 | 19.8289 | 18.7774
|  | BATTERY POINT | EE |  |  |  |  | 30.0137 | 29.6495 | 29.28 | 28.9558 | 28.5705 | 28.1884 | 27.7516 | 27.3284 | 26.8674 | 39.2737 | 38.02 | 37.2579 | 28.2295 | 27.82 | 27.4053 | 27.0495 | 26.6611 | 26.2842 | 25.8379 | 25.3979 | 24.9116 | 41.8295 | 40.6147 | 39.7926 | 28.3121 | 27.8963 | 27.4753 | 27.1153 | 26.7026 | 26.2953 | 25.8174 | 25.3489 | 24.8311 | 38.7447 | 37.3984 | 36.5363
|  | BATTERY POINT | HT |  |  |  |  | 29.7537 | 29.32 | 28.9253 | 28.5684 | 28.14 | 27.6063 | 27.0674 | 26.4526 | 25.7189 | 23.7032 | 22.5263 | 21.6168 | 27.9295 | 27.4411 | 27.0021 | 26.6095 | 26.1705 | 25.5947 | 25.0116 | 24.3389 | 23.5126 | 21.3305 | 20.08 | 19.0611 | 28.0089 | 27.5142 | 27.0689 | 26.6732 | 26.2132 | 25.6142 | 25.0058 | 24.3026 | 23.4437 | 21.1479 | 19.8289 | 18.7774
|  | BATTERY POINT | HE |  |  |  |  | 30.3453 | 30.0747 | 29.8179 | 29.6063 | 29.3084 | 29.0442 | 28.6916 | 28.3116 | 27.9063 | 26.2611 | 25.3989 | 24.7842 | 28.6021 | 28.2926 | 28.0053 | 27.7747 | 27.4895 | 27.2347 | 26.8663 | 26.4632 | 26.0253 | 24.2463 | 23.3947 | 22.8421 | 28.0089 | 27.5142 | 27.0689 | 26.6732 | 26.2132 | 25.6142 | 25.0058 | 24.3026 | 23.4437 | 21.1479 | 19.8289 | 18.7774
|  | BATTERY POINT | CF |  |  |  |  | 30.5579 | 30.4632 | 30.3284 | 30.1947 | 30.0337 | 29.8695 | 29.7063 | 29.5411 | 29.3632 | 28.18 | 27.4347 | 27.0537 | 28.9 | 28.7505 | 28.5874 | 28.4368 | 28.2716 | 28.1 | 27.9284 | 27.7516 | 27.5579 | 26.2232 | 25.4316 | 25.0484 | 28.9889 | 28.8395 | 28.6732 | 28.5205 | 28.3447 | 28.1637 | 27.9826 | 27.7974 | 27.5974 | 26.2068 | 25.3532 | 24.9279
| DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | YES | 0 | 1.0484 | 1.0179 | 0.98526 | 0.95263 | 0.79474 | 0.57474 | 0.35158 | 0.15789 | -0.12842 | -4.2779 | -6.4368 | -8.9811 | 1.0295 | 0.98947 | 0.94842 | 0.90842 | 0.78105 | 0.63053 | 0.45053 | 0.25368 | -0.06 | -3.6074 | -5.7168 | -8.1874 | 1.0547 | 1.0147 | 0.97158 | 0.93053 | 0.77579 | 0.56947 | 0.34737 | 0.15263 | -0.14316 | -4.4716 | -6.8389 | -9.6147
|  | BETTYHILL | EE |  |  |  |  | 1.0653 | 1.0337 | 1 | 0.96947 | 0.79579 | 0.57474 | 0.35158 | 0.15789 | -0.057895 | -4.2779 | -6.4368 | -8.9811 | 1.0526 | 1.0168 | 0.97895 | 0.94316 | 0.79895 | 0.63053 | 0.45474 | 0.29579 | 0.11368 | -3.6074 | -5.7168 | -8.1874 | 1.0789 | 1.0389 | 0.99789 | 0.95895 | 0.78211 | 0.56947 | 0.34737 | 0.15263 | -0.066316 | -4.4716 | -6.8389 | -9.6147
|  | BETTYHILL | HT |  |  |  |  | 1.0484 | 1.0179 | 0.98526 | 0.95263 | 0.79474 | 0.63684 | 0.47474 | 0.28421 | -0.092632 | -3.6632 | -5.6589 | -7.9211 | 1.0295 | 0.98947 | 0.94842 | 0.90842 | 0.78105 | 0.65263 | 0.52526 | 0.37474 | -0.006316 | -3.2295 | -5.4021 | -7.6337 | 1.0547 | 1.0147 | 0.97158 | 0.93053 | 0.77579 | 0.62 | 0.46316 | 0.27368 | -0.14316 | -3.9126 | -6.1842 | -8.6568
|  | BETTYHILL | HE |  |  |  |  | 1.0874 | 1.0737 | 1.0579 | 1.0411 | 0.85895 | 0.63579 | 0.40632 | 0.18842 | -0.12842 | -2.4663 | -4.1326 | -6.4084 | 1.0863 | 1.0695 | 1.0495 | 1.0295 | 0.85895 | 0.65789 | 0.45053 | 0.25368 | -0.06 | -2.1379 | -3.8463 | -6.0705 | 1.0547 | 1.0147 | 0.97158 | 0.93053 | 0.77579 | 0.62 | 0.46316 | 0.27368 | -0.14316 | -3.9126 | -6.1842 | -8.6568
|  | BETTYHILL | CF |  |  |  |  | 1.1011 | 1.0926 | 1.0842 | 1.0747 | 1.0116 | 0.95474 | 0.85474 | 0.71684 | 0.56105 | -1.2589 | -2.3095 | -3.4853 | 1.1042 | 1.0947 | 1.0821 | 1.0716 | 1.0147 | 0.96211 | 0.84737 | 0.70526 | 0.53579 | -1.0274 | -2.1126 | -3.3832 | 1.1305 | 1.12 | 1.1084 | 1.0958 | 1.0253 | 0.96105 | 0.83579 | 0.68526 | 0.51158 | -1.3768 | -2.5442 | -3.8811
| GRUDIE BRIDGE | BIDEN CLAN RAONAILD | MINIMUM HEADROOM | NH 06927 58342 | YES | NO | 0 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154
|  | BIDEN CLAN RAONAILD | EE |  |  |  |  | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154
|  | BIDEN CLAN RAONAILD | HT |  |  |  |  | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154
|  | BIDEN CLAN RAONAILD | HE |  |  |  |  | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154
|  | BIDEN CLAN RAONAILD | CF |  |  |  |  | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154
| ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 0.07 | 12.1174 | 23.3332 | 23.2679 | 23.17 | 23.0605 | 22.6995 | 22.2774 | 21.7121 | 21.1374 | 18.6511 | 14.7795 | 11.8089 | 11.4711 | 21.4374 | 21.3258 | 21.2132 | 21.0995 | 20.7584 | 20.3668 | 19.8289 | 19.2837 | 16.7889 | 12.8437 | 9.9932 | 11.7921 | 22.3595 | 22.2479 | 22.1321 | 22.0174 | 21.6342 | 21.1868 | 20.5816 | 19.9679 | 17.2679 | 13.1311 | 9.7584
|  | BILBOHALL | EE |  |  |  |  | 12.1479 | 23.3679 | 23.3037 | 23.2384 | 23.1668 | 22.8321 | 22.3584 | 21.9237 | 21.4237 | 18.6921 | 14.7795 | 11.8089 | 11.5395 | 21.5226 | 21.4237 | 21.3226 | 21.2247 | 20.9447 | 20.5416 | 20.1616 | 19.7079 | 17.0879 | 13.2416 | 9.9932 | 11.8584 | 22.4384 | 22.3363 | 22.2332 | 22.1321 | 21.7858 | 21.2932 | 20.8374 | 20.3089 | 17.3784 | 13.1311 | 9.7584
|  | BILBOHALL | HT |  |  |  |  | 12.1174 | 23.3332 | 23.2679 | 23.17 | 23.0605 | 22.6995 | 22.2774 | 21.7121 | 21.1374 | 18.6511 | 15.0374 | 12.5753 | 11.4711 | 21.4374 | 21.3258 | 21.2132 | 21.0995 | 20.7584 | 20.3668 | 19.8289 | 19.2837 | 16.7889 | 12.8437 | 10.0763 | 11.7921 | 22.3595 | 22.2479 | 22.1321 | 22.0174 | 21.6342 | 21.1868 | 20.5816 | 19.9679 | 17.2679 | 13.1605 | 10.3289
|  | BILBOHALL | HE |  |  |  |  | 12.1911 | 23.4384 | 23.4016 | 23.3637 | 23.3237 | 23.0774 | 22.7311 | 22.31 | 21.7837 | 19.5595 | 16.5342 | 13.27 | 11.6353 | 21.6584 | 21.5995 | 21.5384 | 21.4753 | 21.2374 | 20.8837 | 20.4984 | 19.9879 | 17.7858 | 14.6879 | 11.3468 | 11.7921 | 22.3595 | 22.2479 | 22.1321 | 22.0174 | 21.6342 | 21.1868 | 20.5816 | 19.9679 | 17.2679 | 13.1605 | 10.3289
|  | BILBOHALL | CF |  |  |  |  | 12.2184 | 23.4795 | 23.4605 | 23.4405 | 23.4205 | 23.3247 | 23.2195 | 23.1268 | 22.8742 | 21.7353 | 19.8311 | 17.7353 | 11.7563 | 21.8016 | 21.7668 | 21.7311 | 21.6942 | 21.5932 | 21.4837 | 21.2753 | 20.9679 | 19.7774 | 17.8195 | 15.5574 | 11.9616 | 22.6226 | 22.6037 | 22.5837 | 22.5647 | 22.4732 | 22.3458 | 22.1247 | 21.8132 | 20.5595 | 18.45 | 16.0742
| RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.03421 | 0.03421 | 0.03421 | 0.033158 | 0.031053 | 0.028947 | 0.026842 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.03421 | 0.033158 | 0.033158 | 0.033158 | 0.032105 | 0.028947 | 0.026842 | 0.023684 | 0.043684 | 0.043684 | 0.042632 | 0.042632 | 0.041579 | 0.040526 | 0.040526 | 0.040526 | 0.039474 | 0.036316 | 0.03421 | 0.031053
|  | BLACKMOUNT | EE |  |  |  |  | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.03421 | 0.03421 | 0.033158 | 0.031053 | 0.028947 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.03421 | 0.033158 | 0.033158 | 0.032105 | 0.028947 | 0.026842 | 0.044737 | 0.043684 | 0.043684 | 0.043684 | 0.042632 | 0.042632 | 0.041579 | 0.040526 | 0.040526 | 0.039474 | 0.036316 | 0.03421
|  | BLACKMOUNT | HT |  |  |  |  | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.03421 | 0.03421 | 0.03421 | 0.033158 | 0.031053 | 0.028947 | 0.026842 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.03421 | 0.033158 | 0.033158 | 0.033158 | 0.032105 | 0.028947 | 0.026842 | 0.023684 | 0.043684 | 0.043684 | 0.042632 | 0.042632 | 0.041579 | 0.040526 | 0.040526 | 0.040526 | 0.039474 | 0.036316 | 0.03421 | 0.031053
|  | BLACKMOUNT | HE |  |  |  |  | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.03421 | 0.03421 | 0.03421 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.033158 | 0.033158 | 0.033158 | 0.043684 | 0.043684 | 0.042632 | 0.042632 | 0.041579 | 0.040526 | 0.040526 | 0.040526 | 0.039474 | 0.036316 | 0.03421 | 0.031053
|  | BLACKMOUNT | CF |  |  |  |  | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.03421 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.043684 | 0.043684 | 0.043684 | 0.042632 | 0.042632 | 0.041579
| BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | YES | 0 | 6.2832 | 6.1484 | 6.0063 | 5.86 | 5.6947 | 5.5368 | 5.3842 | 5.2842 | 5.1895 | 4.7695 | 4.4284 | 4.1421 | 6.0411 | 5.8937 | 5.7368 | 5.5758 | 5.3926 | 5.2189 | 5.0505 | 4.9432 | 4.8421 | 4.3789 | 4.0021 | 3.6811 | 6.1979 | 6.0516 | 5.8958 | 5.7358 | 5.5547 | 5.3821 | 5.2147 | 5.1074 | 5.0074 | 4.5484 | 4.1737 | 3.8537
|  | BLACKSTAND | EE |  |  |  |  | 6.3568 | 6.2463 | 6.1253 | 6 | 5.8611 | 5.7316 | 5.6 | 5.5232 | 5.4484 | 5.1021 | 4.8526 | 4.66 | 6.1211 | 5.9989 | 5.8663 | 5.7274 | 5.5737 | 5.4295 | 5.2853 | 5.2021 | 5.1211 | 4.7453 | 4.4684 | 4.2516 | 6.2779 | 6.1558 | 6.0242 | 5.8863 | 5.7337 | 5.5916 | 5.4474 | 5.3653 | 5.2853 | 4.9116 | 4.6358 | 4.4221
|  | BLACKSTAND | HT |  |  |  |  | 6.2832 | 6.1484 | 6.0063 | 5.86 | 5.6947 | 5.5368 | 5.3842 | 5.2842 | 5.1895 | 4.7695 | 4.4284 | 4.1421 | 6.0411 | 5.8937 | 5.7368 | 5.5758 | 5.3926 | 5.2189 | 5.0505 | 4.9432 | 4.8421 | 4.3789 | 4.0021 | 3.6811 | 6.1979 | 6.0516 | 5.8958 | 5.7358 | 5.5547 | 5.3821 | 5.2147 | 5.1074 | 5.0074 | 4.5484 | 4.1737 | 3.8537
|  | BLACKSTAND | HE |  |  |  |  | 6.4579 | 6.3768 | 6.2863 | 6.1884 | 6.0758 | 5.9726 | 5.8663 | 5.8126 | 5.7621 | 5.5905 | 5.4811 | 5.3937 | 6.2316 | 6.1421 | 6.0411 | 5.9326 | 5.8074 | 5.6926 | 5.5737 | 5.5168 | 5.4642 | 5.2789 | 5.1611 | 5.0632 | 6.1979 | 6.0516 | 5.8958 | 5.7358 | 5.5547 | 5.3821 | 5.2147 | 5.1074 | 5.0074 | 4.5484 | 4.1737 | 3.8537
|  | BLACKSTAND | CF |  |  |  |  | 6.5358 | 6.4874 | 6.4368 | 6.3842 | 6.3242 | 6.2653 | 6.2116 | 6.1758 | 6.1411 | 5.9916 | 5.8937 | 5.8253 | 6.3168 | 6.2642 | 6.2074 | 6.1484 | 6.0821 | 6.0158 | 5.9547 | 5.9168 | 5.8789 | 5.7168 | 5.6095 | 5.5316 | 6.4705 | 6.4189 | 6.3621 | 6.3042 | 6.2379 | 6.1726 | 6.1126 | 6.0747 | 6.0379 | 5.8768 | 5.7695 | 5.6926
| COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | YES | 0.628 | 23.0641 | 22.7852 | 22.4988 | 22.0936 | 21.2167 | 20.4315 | 19.6157 | 18.6831 | 17.7062 | 15.2536 | 8.6999 | 5.7767 | 20.5425 | 20.2383 | 19.9278 | 19.4552 | 18.4973 | 17.6562 | 16.8109 | 15.8783 | 14.8973 | 12.6657 | 6.6878 | 3.3994 | 21.4586 | 21.1649 | 20.8638 | 20.4217 | 19.4544 | 18.5554 | 17.6523 | 16.6459 | 15.5912 | 13.0407 | 6.1175 | 2.7944
|  | BLAIRGOWRIE | EE |  |  |  |  | 23.2315 | 23.0146 | 22.7925 | 22.5567 | 21.7115 | 20.8262 | 19.9946 | 19.1936 | 18.3399 | 15.2841 | 12.3704 | 8.9578 | 20.7309 | 20.4994 | 20.2625 | 20.0067 | 19.1067 | 18.1888 | 17.3531 | 16.5625 | 15.7278 | 13.0415 | 10.3373 | 6.5909 | 21.6365 | 21.4091 | 21.1744 | 20.9249 | 20.0017 | 19.0196 | 18.0881 | 17.2154 | 16.2965 | 13.1365 | 10.0502 | 6.1881
|  | BLAIRGOWRIE | HT |  |  |  |  | 23.0641 | 22.7852 | 22.4988 | 22.0936 | 21.2167 | 20.4315 | 19.6157 | 18.6831 | 17.7062 | 15.2536 | 8.6999 | 5.7767 | 20.5425 | 20.2383 | 19.9278 | 19.4552 | 18.4973 | 17.6562 | 16.8109 | 15.8783 | 14.8973 | 12.6657 | 6.6878 | 3.3994 | 21.4586 | 21.1649 | 20.8638 | 20.4217 | 19.4544 | 18.5554 | 17.6523 | 16.6459 | 15.5912 | 13.0407 | 6.1175 | 2.7944
|  | BLAIRGOWRIE | HE |  |  |  |  | 23.3894 | 23.2873 | 23.162 | 23.0136 | 22.2715 | 21.5494 | 20.8725 | 20.1788 | 19.4588 | 17.5157 | 12.6178 | 8.9062 | 20.8983 | 20.7952 | 20.6657 | 20.5078 | 19.752 | 18.9794 | 18.2667 | 17.5278 | 16.8078 | 15.1604 | 10.7794 | 6.9646 | 21.4586 | 21.1649 | 20.8638 | 20.4217 | 19.4544 | 18.5554 | 17.6523 | 16.6459 | 15.5912 | 13.0407 | 6.1175 | 2.7944
|  | BLAIRGOWRIE | CF |  |  |  |  | 23.4767 | 23.4167 | 23.3536 | 23.2936 | 23.0852 | 22.882 | 22.6736 | 22.3988 | 22.0757 | 20.9631 | 17.0452 | 14.6788 | 20.9846 | 20.9246 | 20.8646 | 20.8057 | 20.6278 | 20.4436 | 20.2541 | 19.9552 | 19.5678 | 18.4741 | 14.9352 | 12.3657 | 21.8881 | 21.8281 | 21.7649 | 21.7049 | 21.4923 | 21.2817 | 21.0659 | 20.7638 | 20.3986 | 19.2144 | 15.0259 | 12.3544
| STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | 0.931 | -0.56574 | -0.571 | -0.57732 | -0.58258 | -0.591 | -0.59732 | -0.60468 | -0.60995 | -0.61732 | -0.64363 | -0.72995 | -0.74574 | -0.74363 | -0.74889 | -0.75521 | -0.76153 | -0.76889 | -0.77626 | -0.78363 | -0.7889 | -0.79626 | -0.82258 | -0.89416 | -0.911 | -0.731 | -0.73732 | -0.74363 | -0.74889 | -0.75837 | -0.76468 | -0.77205 | -0.77837 | -0.78574 | -0.81416 | -0.90258 | -0.92047
|  | BLAIRLINNANS | EE |  |  |  |  | -0.56153 | -0.56574 | -0.56995 | -0.57521 | -0.58153 | -0.58784 | -0.5931 | -0.60047 | -0.60468 | -0.631 | -0.70995 | -0.72047 | -0.73942 | -0.74363 | -0.74784 | -0.75311 | -0.75942 | -0.76679 | -0.771 | -0.77732 | -0.78258 | -0.80784 | -0.871 | -0.88363 | -0.72784 | -0.731 | -0.73626 | -0.74153 | -0.74784 | -0.75416 | -0.76047 | -0.76784 | -0.77205 | -0.80047 | -0.88047 | -0.89311
|  | BLAIRLINNANS | HT |  |  |  |  | -0.56574 | -0.571 | -0.57732 | -0.58258 | -0.591 | -0.59732 | -0.60468 | -0.60995 | -0.61732 | -0.64363 | -0.72995 | -0.74574 | -0.74363 | -0.74889 | -0.75521 | -0.76153 | -0.76889 | -0.77626 | -0.78363 | -0.7889 | -0.79626 | -0.82258 | -0.89416 | -0.911 | -0.731 | -0.73732 | -0.74363 | -0.74889 | -0.75837 | -0.76468 | -0.77205 | -0.77837 | -0.78574 | -0.81416 | -0.90258 | -0.92047
|  | BLAIRLINNANS | HE |  |  |  |  | -0.55837 | -0.56047 | -0.56258 | -0.56574 | -0.571 | -0.57521 | -0.57837 | -0.58363 | -0.58679 | -0.60363 | -0.63732 | -0.64363 | -0.73521 | -0.73732 | -0.74047 | -0.74363 | -0.74784 | -0.75311 | -0.75521 | -0.75942 | -0.76258 | -0.77942 | -0.8089 | -0.81521 | -0.731 | -0.73732 | -0.74363 | -0.74889 | -0.75837 | -0.76468 | -0.77205 | -0.77837 | -0.78574 | -0.81416 | -0.90258 | -0.92047
|  | BLAIRLINNANS | CF |  |  |  |  | -0.55626 | -0.55732 | -0.55837 | -0.55942 | -0.56153 | -0.56258 | -0.56574 | -0.56784 | -0.56995 | -0.58047 | -0.58784 | -0.59521 | -0.73311 | -0.73416 | -0.73521 | -0.73626 | -0.73837 | -0.74047 | -0.74258 | -0.74574 | -0.74784 | -0.75732 | -0.76574 | -0.77205 | -0.72153 | -0.72258 | -0.72363 | -0.72468 | -0.72679 | -0.72889 | -0.731 | -0.73416 | -0.73626 | -0.74679 | -0.75521 | -0.76258
| BOAT OF GARTEN | BOAT OF GARTEN | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 0 | 8.5505 | 8.4747 | 8.3842 | 8.2958 | 8.1274 | 7.9611 | 7.7895 | 7.6968 | 7.6116 | 7.2453 | 6.9611 | 6.7347 | 8.1611 | 8.06 | 7.96 | 7.8621 | 7.6684 | 7.4758 | 7.2758 | 7.1779 | 7.0874 | 6.6821 | 6.3621 | 6.1 | 8.22 | 8.1253 | 8.0263 | 7.9284 | 7.7305 | 7.5358 | 7.3337 | 7.2326 | 7.14 | 6.7263 | 6.3989 | 6.1337
|  | BOAT OF GARTEN | EE |  |  |  |  | 8.6011 | 8.54 | 8.4789 | 8.4105 | 8.3326 | 8.2568 | 8.1084 | 7.9653 | 7.8179 | 7.4968 | 7.2474 | 7.0705 | 8.2316 | 8.1516 | 8.0726 | 7.9937 | 7.9116 | 7.8295 | 7.66 | 7.4937 | 7.32 | 6.9789 | 6.7095 | 6.5084 | 8.2853 | 8.2105 | 8.1358 | 8.0589 | 7.9758 | 7.8916 | 7.7179 | 7.5495 | 7.3716 | 7.0189 | 6.7379 | 6.5305
|  | BOAT OF GARTEN | HT |  |  |  |  | 8.5505 | 8.4747 | 8.3842 | 8.2958 | 8.1274 | 7.9611 | 7.7895 | 7.6968 | 7.6116 | 7.2453 | 6.9611 | 6.7347 | 8.1611 | 8.06 | 7.96 | 7.8621 | 7.6684 | 7.4758 | 7.2758 | 7.1779 | 7.0874 | 6.6821 | 6.3621 | 6.1 | 8.22 | 8.1253 | 8.0263 | 7.9284 | 7.7305 | 7.5358 | 7.3337 | 7.2326 | 7.14 | 6.7263 | 6.3989 | 6.1337
|  | BOAT OF GARTEN | HE |  |  |  |  | 8.6695 | 8.6305 | 8.5895 | 8.5474 | 8.4947 | 8.4474 | 8.3432 | 8.2263 | 8.0937 | 7.9211 | 7.8011 | 7.6989 | 8.3263 | 8.2768 | 8.2263 | 8.1747 | 8.1147 | 8.06 | 7.9221 | 7.7853 | 7.6284 | 7.4505 | 7.3263 | 7.22 | 8.22 | 8.1253 | 8.0263 | 7.9284 | 7.7305 | 7.5358 | 7.3337 | 7.2326 | 7.14 | 6.7263 | 6.3989 | 6.1337
|  | BOAT OF GARTEN | CF |  |  |  |  | 8.7063 | 8.6853 | 8.6632 | 8.64 | 8.6126 | 8.5874 | 8.5611 | 8.5147 | 8.4547 | 8.2674 | 8.1684 | 8.0989 | 8.3758 | 8.3463 | 8.3168 | 8.2874 | 8.2526 | 8.22 | 8.1874 | 8.1105 | 8.0337 | 7.8211 | 7.7158 | 7.6379 | 8.42 | 8.3926 | 8.3653 | 8.3368 | 8.3042 | 8.2737 | 8.2411 | 8.1726 | 8.0968 | 7.8811 | 7.7705 | 7.6895
| PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 0.05 | 6.4132 | 6.3532 | 6.29 | 6.2216 | 5.9816 | 5.7426 | 5.4711 | 5.1616 | 4.9889 | 4.1605 | 3.4521 | 3.1595 | 5.9079 | 5.8205 | 5.7279 | 5.6247 | 5.27 | 4.9184 | 4.4995 | 4.0195 | 3.8163 | 2.9984 | 2.3458 | 2.0447 | 6.3784 | 6.3279 | 6.2753 | 6.2163 | 6.0195 | 5.8226 | 5.6026 | 5.3532 | 5.1879 | 4.3784 | 3.5584 | 3.2068
|  | BODDAM | EE |  |  |  |  | 6.4416 | 6.39 | 6.3353 | 6.2763 | 6.0668 | 5.8111 | 5.5468 | 5.2858 | 4.9889 | 4.1605 | 3.4521 | 3.1595 | 5.95 | 5.8784 | 5.7995 | 5.7132 | 5.4395 | 5.0953 | 4.7342 | 4.3521 | 3.9068 | 2.9984 | 2.3458 | 2.0447 | 6.4037 | 6.3584 | 6.3121 | 6.2616 | 6.0826 | 5.8668 | 5.6447 | 5.43 | 5.1879 | 4.3784 | 3.5584 | 3.2068
|  | BODDAM | HT |  |  |  |  | 6.4132 | 6.3532 | 6.29 | 6.2216 | 5.9816 | 5.7426 | 5.4711 | 5.1616 | 4.9889 | 4.3458 | 3.9721 | 3.6184 | 5.9079 | 5.8205 | 5.7279 | 5.6247 | 5.27 | 4.9184 | 4.4995 | 4.0195 | 3.8163 | 3.0584 | 2.6542 | 2.1963 | 6.3784 | 6.3279 | 6.2753 | 6.2163 | 6.0195 | 5.8226 | 5.6026 | 5.3532 | 5.2005 | 4.5205 | 4.0574 | 3.5763
|  | BODDAM | HE |  |  |  |  | 6.4689 | 6.4437 | 6.4121 | 6.37 | 6.1637 | 5.9468 | 5.7279 | 5.4921 | 5.2258 | 4.6237 | 4.1953 | 3.7237 | 5.9826 | 5.95 | 5.9026 | 5.8384 | 5.5742 | 5.2689 | 4.9511 | 4.5995 | 4.1837 | 3.5016 | 3.1079 | 2.6511 | 6.3784 | 6.3279 | 6.2753 | 6.2163 | 6.0195 | 5.8226 | 5.6026 | 5.3532 | 5.2005 | 4.5205 | 4.0574 | 3.5763
|  | BODDAM | CF |  |  |  |  | 6.49 | 6.4795 | 6.4679 | 6.4553 | 6.3963 | 6.3332 | 6.2595 | 6.1826 | 6.1026 | 5.6784 | 5.2826 | 5.0889 | 6.0111 | 5.9984 | 5.9847 | 5.9711 | 5.9111 | 5.8342 | 5.7384 | 5.63 | 5.5037 | 4.8911 | 4.3858 | 4.1984 | 6.4468 | 6.4374 | 6.4268 | 6.4153 | 6.3616 | 6.3058 | 6.2437 | 6.1784 | 6.1153 | 5.7658 | 5.4258 | 5.2479
| TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | 0 | 1.5684 | 1.5316 | 1.4926 | 1.4526 | 1.3863 | 1.3263 | 1.2663 | 1.2053 | 1.0842 | 0.71474 | 0.46316 | 0.31789 | 1.0032 | 0.87895 | 0.73895 | 0.58211 | 0.43053 | 0.30842 | 0.18632 | 0.032632 | -0.16526 | -0.54316 | -0.76842 | -0.93474 | 1.3316 | 1.2021 | 1.0547 | 0.89158 | 0.73053 | 0.60105 | 0.47158 | 0.30737 | 0.10105 | -0.30105 | -0.5579 | -0.71474
|  | BONSKEID | EE |  |  |  |  | 1.5895 | 1.5621 | 1.5337 | 1.5053 | 1.4484 | 1.3874 | 1.3284 | 1.2747 | 1.2211 | 0.76316 | 0.46316 | 0.31789 | 1.0589 | 0.98842 | 0.89474 | 0.77789 | 0.58105 | 0.38737 | 0.28947 | 0.18421 | 0.064211 | -0.47053 | -0.74632 | -0.89158 | 1.3895 | 1.3137 | 1.2179 | 1.0947 | 0.88526 | 0.67895 | 0.57053 | 0.45789 | 0.32842 | -0.24526 | -0.5579 | -0.71474
|  | BONSKEID | HT |  |  |  |  | 1.5684 | 1.5316 | 1.4926 | 1.4526 | 1.3863 | 1.3263 | 1.2663 | 1.2053 | 1.0842 | 0.71474 | 0.49158 | 0.33684 | 1.0032 | 0.87895 | 0.73895 | 0.58211 | 0.43053 | 0.30842 | 0.18632 | 0.032632 | -0.16526 | -0.54316 | -0.76842 | -0.93474 | 1.3316 | 1.2021 | 1.0547 | 0.89158 | 0.73053 | 0.60105 | 0.47158 | 0.30737 | 0.10105 | -0.30105 | -0.54 | -0.71263
|  | BONSKEID | HE |  |  |  |  | 1.6147 | 1.5979 | 1.5779 | 1.5579 | 1.5063 | 1.4621 | 1.4179 | 1.3747 | 1.3337 | 1.0853 | 0.91158 | 0.74526 | 1.1126 | 1.0484 | 0.96 | 0.85474 | 0.66 | 0.51158 | 0.41158 | 0.29789 | 0.16316 | -0.13895 | -0.29684 | -0.44737 | 1.3316 | 1.2021 | 1.0547 | 0.89158 | 0.73053 | 0.60105 | 0.47158 | 0.30737 | 0.10105 | -0.30105 | -0.54 | -0.71263
|  | BONSKEID | CF |  |  |  |  | 1.6316 | 1.6221 | 1.6116 | 1.6021 | 1.5811 | 1.5611 | 1.5411 | 1.5232 | 1.5063 | 1.4179 | 1.3326 | 1.2758 | 1.16 | 1.1389 | 1.1137 | 1.0832 | 1.0337 | 0.96737 | 0.89263 | 0.83895 | 0.72105 | 0.42316 | 0.31053 | 0.22842 | 1.4947 | 1.4716 | 1.4453 | 1.4137 | 1.36 | 1.2895 | 1.2095 | 1.1537 | 1.0274 | 0.70947 | 0.58526 | 0.49263
| PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | NO | YES | 0 | 8.8053 | 8.6863 | 8.5537 | 8.3979 | 8.2368 | 8.0337 | 7.8832 | 7.7905 | 7.7095 | 7.1084 | 6.8537 | 6.5568 | 7.8716 | 7.7642 | 7.6453 | 7.4695 | 7.2789 | 7.0337 | 6.8568 | 6.7526 | 6.6632 | 6.1021 | 5.8074 | 5.4505 | 8.2726 | 8.1389 | 7.9874 | 7.8063 | 7.6179 | 7.3737 | 7.1968 | 7.0916 | 7.0021 | 6.3726 | 6.0779 | 5.7211
|  | BOWMORE | EE |  |  |  |  | 8.8705 | 8.7779 | 8.6621 | 8.5105 | 8.3589 | 8.1547 | 8.0211 | 7.9505 | 7.8821 | 11.4274 | 11.2768 | 11.1274 | 7.9305 | 7.8463 | 7.7432 | 7.5989 | 7.4168 | 7.1684 | 7.0095 | 6.9305 | 6.8526 | 11.4726 | 11.2653 | 11.0905 | 8.3453 | 8.2432 | 8.1116 | 7.9347 | 7.7547 | 7.5074 | 7.3495 | 7.2695 | 7.1926 | 11.2126 | 11.0074 | 10.8337
|  | BOWMORE | HT |  |  |  |  | 8.8053 | 8.6863 | 8.5537 | 8.3979 | 8.2368 | 8.0337 | 7.8832 | 7.7905 | 7.7095 | 7.1084 | 6.8537 | 6.5568 | 7.8716 | 7.7642 | 7.6453 | 7.4695 | 7.2789 | 7.0337 | 6.8568 | 6.7526 | 6.6632 | 6.1021 | 5.8074 | 5.4505 | 8.2726 | 8.1389 | 7.9874 | 7.8063 | 7.6179 | 7.3737 | 7.1968 | 7.0916 | 7.0021 | 6.3726 | 6.0779 | 5.7211
|  | BOWMORE | HE |  |  |  |  | 8.9516 | 8.8779 | 8.78 | 8.6526 | 8.5221 | 8.3432 | 8.2158 | 8.1653 | 8.1211 | 7.8242 | 7.7305 | 7.6621 | 8.0042 | 7.9389 | 7.8516 | 7.74 | 7.6021 | 7.3821 | 7.2284 | 7.1716 | 7.1232 | 6.8526 | 6.7453 | 6.6642 | 8.2726 | 8.1389 | 7.9874 | 7.8063 | 7.6179 | 7.3737 | 7.1968 | 7.0916 | 7.0021 | 6.3726 | 6.0779 | 5.7211
|  | BOWMORE | CF |  |  |  |  | 9.0116 | 8.9758 | 8.9368 | 8.8737 | 8.8105 | 8.7221 | 8.6463 | 8.6105 | 8.5716 | 8.4253 | 8.3411 | 8.28 | 8.0589 | 8.0263 | 7.9905 | 7.9358 | 7.88 | 7.8042 | 7.7379 | 7.7053 | 7.66 | 7.4947 | 7.3968 | 7.3232 | 8.4758 | 8.4526 | 8.4137 | 8.3453 | 8.2737 | 8.1684 | 8.0789 | 8.04 | 7.9958 | 7.8316 | 7.7337 | 7.6611
| SHETLAND | BRAE | MINIMUM HEADROOM | HU3604068816 | YES | YES | 0 | 1.4032 | 1.3379 | -0.89263 | -0.94737 | -1.0179 | -1.1484 | -1.2958 | -1.4537 | -1.5832 | -1.8284 | -1.9926 | -2.0811 | 1.1358 | 1.0558 | -0.72526 | -0.78632 | -0.85789 | -1.0116 | -1.1737 | -1.3495 | -1.4979 | -1.7411 | -1.8937 | -1.9811 | 1.26 | 1.2179 | -1.0958 | -1.1537 | -1.2284 | -1.3768 | -1.5484 | -1.7305 | -1.8811 | -2.14 | -2.3116 | -2.4042
|  | BRAE | EE |  |  |  |  | 1.4432 | 1.3895 | -0.89263 | -0.94737 | -1.0179 | -1.1484 | -1.2958 | -1.4537 | -1.5832 | -1.8284 | -1.9926 | -2.0811 | 1.1874 | 1.1232 | -0.72526 | -0.78632 | -0.85789 | -1.0116 | -1.1737 | -1.3495 | -1.4979 | -1.7411 | -1.8937 | -1.9811 | 1.2811 | 1.2453 | -1.0958 | -1.1537 | -1.2284 | -1.3768 | -1.5484 | -1.7305 | -1.8811 | -2.14 | -2.3116 | -2.4042
|  | BRAE | HT |  |  |  |  | 1.4032 | 1.3379 | 1.2737 | 1.2095 | 1.1295 | 0.98947 | 0.81895 | 0.62526 | 0.57053 | -0.48947 | -1.3937 | -1.4863 | 1.1358 | 1.0558 | 0.97789 | 0.90105 | 0.80632 | 0.61895 | 0.40842 | 0.18105 | 0.12842 | -0.73158 | -1.4642 | -1.5632 | 1.26 | 1.2179 | 1.1526 | 1.0758 | 0.98105 | 0.79684 | 0.59053 | 0.36737 | 0.31158 | -0.75263 | -1.6916 | -1.7895
|  | BRAE | HE |  |  |  |  | 1.5011 | 1.4674 | 1.4316 | 1.3937 | 1.3137 | 1.1979 | 1.0821 | 0.94632 | 0.82842 | 0.28842 | -0.15368 | -0.18632 | 1.2611 | 1.2211 | 1.1789 | 1.1368 | 1.0337 | 0.86947 | 0.71263 | 0.54316 | 0.40526 | -0.049474 | -0.40632 | -0.44 | 1.26 | 1.2179 | 1.1526 | 1.0758 | 0.98105 | 0.79684 | 0.59053 | 0.36737 | 0.31158 | -0.75263 | -1.6916 | -1.7895
|  | BRAE | CF |  |  |  |  | 1.5337 | 1.5126 | 1.4916 | 1.4695 | 1.4453 | 1.42 | 1.3937 | 1.3705 | 1.3305 | 1.1389 | 1.0032 | 0.96 | 1.2958 | 1.2747 | 1.2495 | 1.2232 | 1.1937 | 1.1663 | 1.1368 | 1.1084 | 1.0547 | 0.79789 | 0.62842 | 0.58632 | 1.3358 | 1.3232 | 1.3095 | 1.2947 | 1.2779 | 1.26 | 1.2421 | 1.2253 | 1.2084 | 0.96947 | 0.79895 | 0.75368
| BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | YES | 0.405 | 12.6221 | 12.4737 | 12.2168 | 11.8642 | 11.2705 | 10.6937 | 10.1032 | 9.4105 | 8.6105 | 5.6032 | 0.42105 | -3.5453 | 10.8529 | 10.395 | 9.9824 | 9.6013 | 9.0392 | 8.4961 | 7.9392 | 7.2845 | 6.5066 | 3.655 | -1.6787 | -5.5734 | 11.5464 | 11.0949 | 10.6822 | 10.3001 | 9.6696 | 9.058 | 8.4296 | 7.6907 | 6.8286 | 3.6464 | -2.0441 | -6.5083
|  | BRECHIN | EE |  |  |  |  | 12.7021 | 12.5705 | 12.4326 | 12.2611 | 11.6263 | 10.8705 | 10.2032 | 9.5874 | 8.8737 | 5.6032 | 0.42105 | -3.5453 | 11.0318 | 10.7003 | 10.3624 | 10.0497 | 9.4592 | 8.755 | 8.1571 | 7.5961 | 6.9224 | 3.9518 | -1.2292 | -5.5734 | 11.7264 | 11.3959 | 11.0528 | 10.737 | 10.0612 | 9.2538 | 8.5486 | 7.8938 | 7.1286 | 3.6464 | -2.0441 | -6.5083
|  | BRECHIN | HT |  |  |  |  | 12.6221 | 12.4737 | 12.2168 | 11.8642 | 11.2705 | 10.6937 | 10.1032 | 9.4105 | 8.6105 | 5.6642 | 0.77789 | -2.5726 | 10.8529 | 10.395 | 9.9824 | 9.6013 | 9.0392 | 8.4961 | 7.9392 | 7.2845 | 6.5066 | 3.655 | -1.6787 | -5.4271 | 11.5464 | 11.0949 | 10.6822 | 10.3001 | 9.6696 | 9.058 | 8.4296 | 7.6907 | 6.8286 | 3.6496 | -1.8325 | -5.6209
|  | BRECHIN | HE |  |  |  |  | 12.7947 | 12.7116 | 12.6221 | 12.5274 | 12.0211 | 11.42 | 10.8842 | 10.3147 | 9.6632 | 7.0884 | 3.1095 | -1.1674 | 11.1297 | 10.9834 | 10.7118 | 10.4571 | 9.875 | 9.3055 | 8.8118 | 8.2792 | 7.6466 | 5.2318 | 1.1203 | -3.3103 | 11.5464 | 11.0949 | 10.6822 | 10.3001 | 9.6696 | 9.058 | 8.4296 | 7.6907 | 6.8286 | 3.6496 | -1.8325 | -5.6209
|  | BRECHIN | CF |  |  |  |  | 12.8579 | 12.8084 | 12.7568 | 12.7063 | 12.5253 | 12.3611 | 12.1968 | 12.0516 | 11.9326 | 10.4221 | 7.8926 | 5.1274 | 11.2003 | 11.1487 | 11.0961 | 11.0445 | 10.9255 | 10.7055 | 10.4634 | 10.2497 | 10.0108 | 8.3245 | 5.695 | 2.6971 | 11.8822 | 11.8328 | 11.7822 | 11.7307 | 11.5549 | 11.3149 | 11.0528 | 10.8212 | 10.5696 | 8.7507 | 5.9433 | 2.8338
| PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | NO | 0.255 | 17.6118 | 16.995 | 16.2718 | 15.4803 | 14.6392 | 13.7624 | 12.8097 | 11.735 | 10.4497 | 7.8929 | 6.635 | 5.5866 | 14.7934 | 14.0208 | 13.165 | 12.2324 | 11.2766 | 10.2724 | 9.2197 | 8.0534 | 6.6471 | 3.9618 | 2.6597 | 1.5366 | 15.94 | 15.1495 | 14.2705 | 13.3158 | 12.3253 | 11.2853 | 10.1947 | 8.9811 | 7.5232 | 4.7326 | 3.3684 | 2.2063
|  | BRIDGE OF DON | EE |  |  |  |  | 17.9024 | 17.3561 | 16.7213 | 16.0297 | 15.2539 | 14.4066 | 13.7118 | 13.0013 | 12.2182 | 8.5013 | 7.2729 | 6.4339 | 15.1461 | 14.4566 | 13.6755 | 12.8608 | 11.9797 | 11.0166 | 10.2429 | 9.4671 | 8.6261 | 4.6418 | 3.4913 | 2.6218 | 16.3 | 15.5916 | 14.7905 | 13.9537 | 13.0368 | 12.0316 | 11.2221 | 10.4084 | 9.5305 | 5.3547 | 4.1021 | 3.1832
|  | BRIDGE OF DON | HT |  |  |  |  | 17.6118 | 16.995 | 16.2718 | 15.4803 | 14.6392 | 13.7624 | 12.8097 | 11.735 | 10.4497 | 7.8929 | 6.635 | 5.5866 | 14.7934 | 14.0208 | 13.165 | 12.2324 | 11.2766 | 10.2724 | 9.2197 | 8.0534 | 6.6471 | 3.9618 | 2.6597 | 1.5366 | 15.94 | 15.1495 | 14.2705 | 13.3158 | 12.3253 | 11.2853 | 10.1947 | 8.9811 | 7.5232 | 4.7326 | 3.3684 | 2.2063
|  | BRIDGE OF DON | HE |  |  |  |  | 18.1382 | 17.7792 | 17.3003 | 16.7603 | 16.1034 | 15.4182 | 14.8034 | 14.2171 | 13.6666 | 11.9918 | 10.8055 | 9.7361 | 15.4913 | 14.9608 | 14.3492 | 13.6903 | 12.9513 | 12.1682 | 11.4703 | 10.8061 | 10.1839 | 8.4366 | 7.2061 | 6.1187 | 15.94 | 15.1495 | 14.2705 | 13.3158 | 12.3253 | 11.2853 | 10.1947 | 8.9811 | 7.5232 | 4.7326 | 3.3684 | 2.2063
|  | BRIDGE OF DON | CF |  |  |  |  | 18.2676 | 18.1866 | 18.1013 | 17.935 | 17.6897 | 17.4234 | 17.1097 | 16.8097 | 16.4887 | 15.3129 | 14.4518 | 13.7371 | 16.0145 | 15.7639 | 15.4597 | 15.1745 | 14.8829 | 14.5587 | 14.1713 | 13.8113 | 13.4376 | 12.1155 | 11.1745 | 10.3703 | 16.6568 | 16.5789 | 16.4968 | 16.3263 | 16.0221 | 15.6853 | 15.2821 | 14.9095 | 14.5232 | 13.1442 | 12.1442 | 11.2947
| BRIDGE OF DUN | BRIDGE OF DUN | MINIMUM HEADROOM | NO 66018 58883 | YES | YES | 0.66 | 0.28 | 0.24947 | 0.22 | 0.18947 | 0.0021053 | -0.22947 | -0.46842 | -0.6821 | -1.0368 | -3.0926 | -5.5095 | -7.3811 | 0.28947 | 0.25684 | 0.22421 | 0.19263 | 0.061053 | -0.13789 | -0.36842 | -0.58526 | -0.93053 | -2.8642 | -5.3358 | -7.2674 | 0.32737 | 0.29474 | 0.26211 | 0.22842 | 0.042105 | -0.19158 | -0.43053 | -0.63895 | -0.97158 | -3.2642 | -5.9074 | -8.0453
|  | BRIDGE OF DUN | EE |  |  |  |  | 0.29263 | 0.26211 | 0.22947 | 0.19579 | 0.0021053 | -0.22947 | -0.46842 | -0.67368 | -0.92421 | -3.0926 | -5.5095 | -7.3811 | 0.30632 | 0.27684 | 0.24421 | 0.21263 | 0.061053 | -0.12842 | -0.3221 | -0.49158 | -0.72526 | -2.8379 | -5.2284 | -7.2674 | 0.34421 | 0.31053 | 0.27474 | 0.23895 | 0.042105 | -0.19158 | -0.43053 | -0.63895 | -0.90947 | -3.2642 | -5.9074 | -8.0453
|  | BRIDGE OF DUN | HT |  |  |  |  | 0.28 | 0.24947 | 0.22 | 0.18947 | 0.025263 | -0.14 | -0.30526 | -0.53368 | -0.95579 | -2.9305 | -5.1874 | -6.7305 | 0.28947 | 0.25684 | 0.22421 | 0.19263 | 0.062105 | -0.073684 | -0.21158 | -0.42211 | -0.84105 | -2.8642 | -5.3358 | -7.0821 | 0.32737 | 0.29474 | 0.26211 | 0.22842 | 0.061053 | -0.10632 | -0.27368 | -0.51789 | -0.97158 | -3.1642 | -5.7358 | -7.5168
|  | BRIDGE OF DUN | HE |  |  |  |  | 0.31368 | 0.3 | 0.28632 | 0.27053 | 0.037895 | -0.19789 | -0.44632 | -0.6821 | -1.0368 | -2.5326 | -4.4084 | -6.4547 | 0.33263 | 0.31684 | 0.30211 | 0.28632 | 0.08421 | -0.13789 | -0.36842 | -0.58526 | -0.93053 | -2.3916 | -4.3158 | -6.4179 | 0.32737 | 0.29474 | 0.26211 | 0.22842 | 0.061053 | -0.10632 | -0.27368 | -0.51789 | -0.97158 | -3.1642 | -5.7358 | -7.5168
|  | BRIDGE OF DUN | CF |  |  |  |  | 0.32526 | 0.31684 | 0.30842 | 0.3 | 0.22211 | 0.15263 | 0.031579 | -0.12211 | -0.29684 | -1.0726 | -2.2558 | -3.5768 | 0.34632 | 0.33684 | 0.32842 | 0.31895 | 0.25895 | 0.20526 | 0.065263 | -0.093684 | -0.28421 | -1.0747 | -2.2979 | -3.7337 | 0.38 | 0.37053 | 0.36211 | 0.35263 | 0.27263 | 0.20316 | 0.061053 | -0.10316 | -0.30105 | -1.1611 | -2.4789 | -3.98
| ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 0.066 | 14.9008 | 14.5693 | 14.1756 | 13.8019 | 13.2282 | 12.6735 | 12.1198 | 11.5377 | 10.944 | 7.524 | 6.4629 | 4.7335 | 13.5393 | 13.1593 | 12.7045 | 12.2772 | 11.6793 | 11.0993 | 10.5224 | 9.9256 | 9.3172 | 6.5224 | 5.5866 | 3.8866 | 13.9774 | 13.6174 | 13.1869 | 12.7816 | 12.1606 | 11.5501 | 10.9416 | 10.3048 | 9.6553 | 7.4785 | 5.7669 | 4.2048
|  | BRIDGE OF EARN | EE |  |  |  |  | 14.9914 | 14.6872 | 14.324 | 13.9829 | 13.4135 | 12.8145 | 12.2135 | 11.6482 | 11.0745 | 8.9282 | 7.2766 | 5.8787 | 13.6372 | 13.2898 | 12.8698 | 12.4772 | 11.8961 | 11.2929 | 10.6908 | 10.1161 | 9.5329 | 7.4129 | 6.0066 | 4.5119 | 14.0722 | 13.7416 | 13.3448 | 12.9722 | 12.3606 | 11.7079 | 11.0522 | 10.4353 | 9.8058 | 7.4785 | 5.7669 | 4.2048
|  | BRIDGE OF EARN | HT |  |  |  |  | 14.9008 | 14.5693 | 14.1756 | 13.8019 | 13.2282 | 12.6735 | 12.1198 | 11.5377 | 10.944 | 9.0893 | 8.1029 | 6.1903 | 13.5393 | 13.1593 | 12.7045 | 12.2772 | 11.6793 | 11.0993 | 10.5224 | 9.9256 | 9.3172 | 7.3845 | 6.4424 | 4.254 | 13.9774 | 13.6174 | 13.1869 | 12.7816 | 12.1606 | 11.5501 | 10.9416 | 10.3048 | 9.6553 | 7.6143 | 6.5637 | 4.3785
|  | BRIDGE OF EARN | HE |  |  |  |  | 15.1019 | 14.8493 | 14.5293 | 14.2293 | 13.6787 | 13.1682 | 12.6608 | 12.1587 | 11.6503 | 7.524 | 6.4629 | 4.7335 | 13.7635 | 13.4645 | 13.0877 | 12.7382 | 12.1814 | 11.6551 | 11.1329 | 10.6151 | 10.0898 | 6.5224 | 5.5866 | 3.8866 | 13.9774 | 13.6174 | 13.1869 | 12.7816 | 12.1606 | 11.5501 | 10.9416 | 10.3048 | 9.6553 | 7.6143 | 6.5637 | 4.3785
|  | BRIDGE OF EARN | CF |  |  |  |  | 15.2187 | 15.1366 | 14.9935 | 14.8566 | 14.6314 | 14.4029 | 14.164 | 13.9229 | 13.6819 | 10.3998 | 9.7229 | 8.2882 | 13.9024 | 13.8056 | 13.6308 | 13.474 | 13.2414 | 13.0024 | 12.7498 | 12.4919 | 12.2245 | 9.4224 | 8.8161 | 7.2687 | 14.3248 | 14.2322 | 14.069 | 13.9206 | 13.6774 | 13.4332 | 13.1753 | 12.9153 | 12.6532 | 9.2595 | 8.5511 | 6.9258
| RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 0 | 0.88316 | 0.86947 | 0.85474 | 0.83789 | 0.76421 | 0.68526 | 0.60105 | 0.52947 | 0.44316 | -0.20211 | -0.90316 | -1.3821 | 0.87789 | 0.86526 | 0.85053 | 0.83579 | 0.77579 | 0.70947 | 0.64 | 0.58 | 0.50737 | -0.054737 | -0.7221 | -1.2453 | 0.94632 | 0.93053 | 0.91263 | 0.89684 | 0.82105 | 0.73684 | 0.64842 | 0.57263 | 0.48 | -0.22947 | -1.0011 | -1.5632
|  | BRIDGE OF GAUR | EE |  |  |  |  | 0.88316 | 0.86947 | 0.85474 | 0.83789 | 0.76421 | 0.68526 | 0.60105 | 0.52947 | 0.44316 | -0.20211 | -0.90316 | -1.3821 | 0.87895 | 0.86526 | 0.85053 | 0.83579 | 0.77579 | 0.70947 | 0.64 | 0.58 | 0.50737 | -0.054737 | -0.7221 | -1.2453 | 0.94632 | 0.93053 | 0.91263 | 0.89684 | 0.82105 | 0.73684 | 0.64842 | 0.57263 | 0.48 | -0.22947 | -1.0011 | -1.5632
|  | BRIDGE OF GAUR | HT |  |  |  |  | 0.88526 | 0.87684 | 0.86526 | 0.85684 | 0.79789 | 0.74526 | 0.68842 | 0.61579 | 0.50211 | -0.033684 | -0.60211 | -0.99263 | 0.87789 | 0.86842 | 0.85684 | 0.85053 | 0.80421 | 0.75895 | 0.71263 | 0.64947 | 0.54105 | 0.014737 | -0.60737 | -1.0379 | 0.94737 | 0.93579 | 0.92421 | 0.91474 | 0.85368 | 0.79579 | 0.73789 | 0.66 | 0.52842 | -0.073684 | -0.73263 | -1.1821
|  | BRIDGE OF GAUR | HE |  |  |  |  | 0.89053 | 0.88632 | 0.88105 | 0.87684 | 0.80105 | 0.73053 | 0.65579 | 0.58421 | 0.48526 | 0.049474 | -0.46 | -1.0137 | 0.88947 | 0.88316 | 0.87789 | 0.87263 | 0.81053 | 0.74526 | 0.68 | 0.61579 | 0.52526 | 0.12737 | -0.38947 | -0.95053 | 0.94737 | 0.93579 | 0.92421 | 0.91474 | 0.85368 | 0.79579 | 0.73789 | 0.66 | 0.52842 | -0.073684 | -0.73263 | -1.1821
|  | BRIDGE OF GAUR | CF |  |  |  |  | 0.89368 | 0.89053 | 0.88947 | 0.88737 | 0.86526 | 0.84211 | 0.80526 | 0.76737 | 0.72737 | 0.52211 | 0.20842 | -0.12842 | 0.89158 | 0.88842 | 0.88632 | 0.88421 | 0.86421 | 0.84526 | 0.80947 | 0.76842 | 0.72211 | 0.51474 | 0.19895 | -0.16105 | 0.96105 | 0.95895 | 0.95579 | 0.95263 | 0.92632 | 0.90105 | 0.85895 | 0.81263 | 0.76211 | 0.52737 | 0.17263 | -0.21368
| BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 0.008 | 5.5741 | 5.5288 | 5.4667 | 5.4036 | 5.2152 | 5.0341 | 4.8488 | 4.7331 | 4.6194 | 4.0036 | 2.9352 | 2.1573 | 5.1594 | 5.0941 | 5.0288 | 4.9636 | 4.7783 | 4.6015 | 4.4215 | 4.3215 | 4.2257 | 3.6425 | 2.4615 | 1.6173 | 5.3373 | 5.2888 | 5.2215 | 5.1541 | 4.9467 | 4.7499 | 4.5478 | 4.4278 | 4.312 | 3.6478 | 2.4309 | 1.5731
|  | BROADFORD | EE |  |  |  |  | 5.6004 | 5.5625 | 5.5236 | 5.4783 | 5.3709 | 5.2509 | 5.0583 | 4.8783 | 4.6931 | 4.0709 | 3.0194 | 2.1573 | 5.2046 | 5.152 | 5.0973 | 5.0446 | 4.9531 | 4.8552 | 4.6762 | 4.5057 | 4.3288 | 3.7878 | 2.7194 | 1.7615 | 5.3594 | 5.3267 | 5.2909 | 5.2352 | 5.1246 | 5.0025 | 4.7931 | 4.5983 | 4.3962 | 3.7457 | 2.5867 | 1.6004
|  | BROADFORD | HT |  |  |  |  | 5.5741 | 5.5288 | 5.4667 | 5.4036 | 5.2152 | 5.0341 | 4.8488 | 4.7331 | 4.6194 | 4.0036 | 2.9352 | 2.1878 | 5.1594 | 5.0941 | 5.0288 | 4.9636 | 4.7783 | 4.6015 | 4.4215 | 4.3215 | 4.2257 | 3.6425 | 2.4615 | 1.6173 | 5.3373 | 5.2888 | 5.2215 | 5.1541 | 4.9467 | 4.7499 | 4.5478 | 4.4278 | 4.312 | 3.6478 | 2.4309 | 1.5731
|  | BROADFORD | HE |  |  |  |  | 5.6341 | 5.6141 | 5.5899 | 5.5636 | 5.4731 | 5.3962 | 5.2699 | 5.1278 | 4.9888 | 4.3741 | 3.5478 | 2.6594 | 5.2646 | 5.232 | 5.2004 | 5.1657 | 5.0867 | 5.0183 | 4.8825 | 4.7499 | 4.6204 | 4.0488 | 3.1815 | 2.2446 | 5.3373 | 5.2888 | 5.2215 | 5.1541 | 4.9467 | 4.7499 | 4.5478 | 4.4278 | 4.312 | 3.6478 | 2.4309 | 1.5731
|  | BROADFORD | CF |  |  |  |  | 5.6531 | 5.6415 | 5.632 | 5.6194 | 5.5836 | 5.5499 | 5.5152 | 5.4762 | 5.4067 | 5.0383 | 4.512 | 3.9173 | 5.2973 | 5.2773 | 5.2594 | 5.2394 | 5.2046 | 5.1709 | 5.1362 | 5.0699 | 4.9962 | 4.6331 | 4.1067 | 3.4583 | 5.4088 | 5.3973 | 5.3878 | 5.3752 | 5.3457 | 5.3173 | 5.2878 | 5.2394 | 5.1573 | 4.7509 | 4.1594 | 3.4815
| CARRADALE 1 | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 0 | 8.7053 | 8.6158 | 8.5147 | 8.4295 | 8.3295 | 8.2126 | 8.0621 | 7.9168 | 7.7768 | 7.2274 | 4.0021 | 3.7305 | 7.6158 | 7.5274 | 7.3716 | 7.1979 | 7.0221 | 6.8505 | 6.6842 | 6.5263 | 6.3726 | 5.7789 | 3.4011 | 3.0011 | 8.1232 | 8.0263 | 7.8758 | 7.7021 | 7.5253 | 7.3537 | 7.1884 | 7.0284 | 6.8758 | 6.2789 | 3.0537 | 2.7411
|  | BRODICK | EE |  |  |  |  | 8.7537 | 8.6758 | 8.5147 | 8.4316 | 8.3463 | 8.2653 | 8.1863 | 8.0895 | 7.9758 | 7.4853 | 4.0021 | 3.7305 | 7.6663 | 7.5916 | 7.48 | 7.3516 | 7.2063 | 7.0663 | 6.9305 | 6.8021 | 6.6789 | 6.1632 | 3.4137 | 3.1158 | 8.1726 | 8.0884 | 7.8937 | 7.7768 | 7.6274 | 7.4853 | 7.3453 | 7.2126 | 7.0863 | 6.5516 | 3.0537 | 2.7411
|  | BRODICK | HT |  |  |  |  | 8.7053 | 8.6158 | 8.5232 | 8.4295 | 8.3295 | 8.2126 | 8.0621 | 7.9168 | 7.7768 | 7.2274 | 4.3011 | 3.9505 | 7.6158 | 7.5274 | 7.3716 | 7.1979 | 7.0221 | 6.8505 | 6.6842 | 6.5263 | 6.3726 | 5.7789 | 3.4011 | 3.0011 | 8.1232 | 8.0263 | 7.8758 | 7.7021 | 7.5253 | 7.3537 | 7.1884 | 7.0284 | 6.8758 | 6.2789 | 3.3126 | 2.9084
|  | BRODICK | HE |  |  |  |  | 8.8284 | 8.7779 | 8.7221 | 8.6632 | 8.6021 | 8.5442 | 8.4874 | 8.4347 | 8.3863 | 8.2232 | 6.5326 | 6.4116 | 7.7389 | 7.6895 | 7.6347 | 7.5768 | 7.5158 | 7.46 | 7.4042 | 7.3274 | 7.2453 | 6.9474 | 5.5695 | 5.4347 | 8.1232 | 8.0263 | 7.8758 | 7.7021 | 7.5253 | 7.3537 | 7.1884 | 7.0284 | 6.8758 | 6.2789 | 3.3126 | 2.9084
|  | BRODICK | CF |  |  |  |  | 8.8779 | 8.8505 | 8.8232 | 8.7947 | 8.7663 | 8.7368 | 8.7084 | 8.68 | 8.6516 | 8.5284 | 6.9832 | 6.8832 | 7.7874 | 7.7611 | 7.7326 | 7.7053 | 7.6768 | 7.6484 | 7.62 | 7.5916 | 7.5632 | 7.3874 | 6.0337 | 5.9158 | 8.3053 | 8.2779 | 8.2474 | 8.2189 | 8.1874 | 8.1579 | 8.1263 | 8.0958 | 8.0653 | 7.8916 | 6.1726 | 6.0547
| BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | YES | 0 | 5.3663 | 5.2853 | 5.2053 | 5.1263 | 4.8695 | 4.6116 | 4.3516 | 4.0674 | 3.7221 | 0.95474 | -2.3463 | -5.1442 | 5.1726 | 5.0853 | 4.9979 | 4.9116 | 4.6642 | 4.4179 | 4.1684 | 3.9442 | 3.5389 | 0.72842 | -3.0568 | -5.7705 | 5.2105 | 5.1211 | 5.0337 | 4.9453 | 4.6642 | 4.38 | 4.0926 | 3.8095 | 3.4232 | 0.39579 | -3.4442 | -6.5011
|  | BRORA | EE |  |  |  |  | 5.4126 | 5.34 | 5.2663 | 5.1937 | 4.9505 | 4.6726 | 4.3516 | 4.0674 | 3.7726 | 0.95474 | -2.3463 | -5.1442 | 5.2253 | 5.1526 | 5.0779 | 5.0021 | 4.7958 | 4.5611 | 4.2621 | 3.9926 | 3.7158 | 0.87368 | -2.5179 | -5.6284 | 5.2589 | 5.1842 | 5.1042 | 5.0242 | 4.7663 | 4.4705 | 4.1211 | 3.8095 | 3.4884 | 0.39579 | -3.2884 | -6.5011
|  | BRORA | HT |  |  |  |  | 5.3663 | 5.2853 | 5.2053 | 5.1263 | 4.8695 | 4.6116 | 4.3516 | 4.0968 | 3.7347 | 1.1242 | -2.2663 | -4.6442 | 5.1726 | 5.0853 | 4.9979 | 4.9116 | 4.6642 | 4.4179 | 4.1684 | 3.9442 | 3.5863 | 0.72842 | -3.0568 | -5.7705 | 5.2105 | 5.1211 | 5.0337 | 4.9453 | 4.6642 | 4.38 | 4.0926 | 3.82 | 3.4232 | 0.44211 | -3.4442 | -6.1958
|  | BRORA | HE |  |  |  |  | 5.4779 | 5.44 | 5.3989 | 5.3568 | 5.1053 | 4.8042 | 4.4968 | 4.2063 | 3.7221 | 1.6842 | -0.95579 | -3.8411 | 5.2832 | 5.2568 | 5.2147 | 5.1705 | 4.9632 | 4.6579 | 4.3432 | 4.0484 | 3.5389 | 1.4674 | -1.3326 | -4.3926 | 5.2105 | 5.1211 | 5.0337 | 4.9453 | 4.6642 | 4.38 | 4.0926 | 3.82 | 3.4232 | 0.44211 | -3.4442 | -6.1958
|  | BRORA | CF |  |  |  |  | 5.5147 | 5.4926 | 5.4684 | 5.4432 | 5.3484 | 5.26 | 5.1137 | 4.9147 | 4.6863 | 3.6 | 1.9274 | -0.021053 | 5.3063 | 5.2926 | 5.2789 | 5.2642 | 5.1895 | 5.1147 | 4.9558 | 4.7168 | 4.4253 | 3.2526 | 1.46 | -0.6979 | 5.3189 | 5.3042 | 5.2884 | 5.2726 | 5.1937 | 5.1042 | 4.9347 | 4.6937 | 4.4042 | 3.1558 | 1.2589 | -0.97053
| MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | YES | 0 | 11.5126 | 11.3695 | 11.2253 | 11.0747 | 10.8979 | 10.7263 | 10.5589 | 10.3958 | 10.24 | 9.4947 | 8.6274 | 7.9432 | 11.0074 | 10.86 | 10.7095 | 10.5558 | 10.3863 | 10.2221 | 10.0632 | 9.9084 | 9.6884 | 8.3895 | 7.44 | 6.6853 | 11.0705 | 10.9221 | 10.7716 | 10.6168 | 10.4432 | 10.2726 | 10.1084 | 9.9484 | 9.7947 | 8.5832 | 7.6347 | 6.8842
|  | BROUGHTY FERRY | EE |  |  |  |  | 11.6032 | 11.4916 | 11.3747 | 11.2526 | 11.1168 | 10.9811 | 10.8453 | 10.7179 | 10.5947 | 10.0695 | 9.5884 | 9.0705 | 11.1032 | 10.9884 | 10.8653 | 10.74 | 10.6063 | 10.4758 | 10.3505 | 10.2316 | 10.1158 | 9.2811 | 8.5147 | 7.9442 | 11.1611 | 11.0495 | 10.9295 | 10.8021 | 10.6632 | 10.5253 | 10.3926 | 10.2684 | 10.1463 | 9.4558 | 8.6768 | 8.1074
|  | BROUGHTY FERRY | HT |  |  |  |  | 11.5126 | 11.3695 | 11.2253 | 11.0747 | 10.8979 | 10.7263 | 10.5589 | 10.3958 | 10.24 | 9.4947 | 8.6274 | 7.9432 | 11.0074 | 10.86 | 10.7095 | 10.5558 | 10.3863 | 10.2221 | 10.0632 | 9.9084 | 9.6884 | 8.3895 | 7.44 | 6.6853 | 11.0705 | 10.9221 | 10.7716 | 10.6168 | 10.4432 | 10.2726 | 10.1084 | 9.9484 | 9.7947 | 8.5832 | 7.6347 | 6.8842
|  | BROUGHTY FERRY | HE |  |  |  |  | 11.7042 | 11.6242 | 11.5368 | 11.4411 | 11.3316 | 11.2316 | 11.1316 | 11.0368 | 10.9516 | 10.6263 | 10.4337 | 10.3042 | 11.2105 | 11.1284 | 11.0379 | 10.9411 | 10.8347 | 10.7379 | 10.6389 | 10.5484 | 10.4653 | 10.1663 | 9.8947 | 9.5674 | 11.0705 | 10.9221 | 10.7716 | 10.6168 | 10.4432 | 10.2726 | 10.1084 | 9.9484 | 9.7947 | 8.5832 | 7.6347 | 6.8842
|  | BROUGHTY FERRY | CF |  |  |  |  | 11.7705 | 11.7232 | 11.6747 | 11.6242 | 11.5705 | 11.5147 | 11.4611 | 11.4074 | 11.3547 | 11.1189 | 10.9726 | 10.8895 | 11.2789 | 11.2305 | 11.18 | 11.1284 | 11.0737 | 11.0189 | 10.9653 | 10.9105 | 10.8568 | 10.62 | 10.4905 | 10.4211 | 11.3284 | 11.2811 | 11.2326 | 11.1821 | 11.1284 | 11.0737 | 11.02 | 10.9663 | 10.9137 | 10.6674 | 10.5232 | 10.4442
| DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 3.5 | 11.5342 | 11.4553 | 11.3753 | 11.2974 | 11.1795 | 11.0616 | 10.9416 | 10.8153 | 10.6911 | 10.2005 | 9.7816 | 9.5226 | 10.4253 | 10.3726 | 10.3189 | 10.2274 | 10.1021 | 9.9811 | 9.86 | 9.7347 | 9.6095 | 9.1095 | 8.7158 | 8.4084 | 10.935 | 10.8803 | 10.7961 | 10.7055 | 10.5761 | 10.4508 | 10.3255 | 10.1939 | 10.0634 | 9.5361 | 9.1076 | 8.7803
|  | BRUCHAG | EE |  |  |  |  | 11.5858 | 11.5226 | 11.4563 | 11.39 | 11.2816 | 11.1647 | 11.0447 | 10.9353 | 10.8226 | 10.2763 | 9.7816 | 9.5226 | 10.4568 | 10.4147 | 10.3695 | 10.3221 | 10.2295 | 10.1116 | 9.9916 | 9.8832 | 9.7747 | 9.2442 | 8.7663 | 8.4937 | 10.9666 | 10.9224 | 10.875 | 10.8192 | 10.7003 | 10.5761 | 10.4487 | 10.3339 | 10.2203 | 9.6518 | 9.1108 | 8.8108
|  | BRUCHAG | HT |  |  |  |  | 11.5342 | 11.4553 | 11.3753 | 11.2974 | 11.1795 | 11.0616 | 10.9416 | 10.8153 | 10.6911 | 10.2005 | 9.8226 | 9.5258 | 10.4253 | 10.3726 | 10.3189 | 10.2274 | 10.1021 | 9.9811 | 9.86 | 9.7347 | 9.6095 | 9.1095 | 8.7158 | 8.4084 | 10.935 | 10.8803 | 10.7961 | 10.7055 | 10.5761 | 10.4508 | 10.3255 | 10.1939 | 10.0634 | 9.5361 | 9.1076 | 8.7803
|  | BRUCHAG | HE |  |  |  |  | 11.6437 | 11.6005 | 11.5553 | 11.5089 | 11.4111 | 11.3237 | 11.2395 | 11.1553 | 11.0753 | 10.7332 | 10.4447 | 10.1311 | 10.4895 | 10.4579 | 10.4221 | 10.3863 | 10.3274 | 10.2737 | 10.22 | 10.1368 | 10.0579 | 9.7253 | 9.4516 | 9.1463 | 10.935 | 10.8803 | 10.7961 | 10.7055 | 10.5761 | 10.4508 | 10.3255 | 10.1939 | 10.0634 | 9.5361 | 9.1076 | 8.7803
|  | BRUCHAG | CF |  |  |  |  | 11.6721 | 11.6426 | 11.6142 | 11.5826 | 11.5353 | 11.4889 | 11.4426 | 11.3974 | 11.3563 | 11.1447 | 10.9437 | 10.7942 | 10.5105 | 10.4905 | 10.4695 | 10.4463 | 10.4179 | 10.3895 | 10.3621 | 10.3326 | 10.3063 | 10.1053 | 9.9011 | 9.7495 | 11.0192 | 10.9992 | 10.9782 | 10.9561 | 10.9182 | 10.8824 | 10.8466 | 10.8118 | 10.7824 | 10.5634 | 10.3466 | 10.1876
| KEITH 1 | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 2.37 | 22.6805 | 22.4668 | 22.23 | 21.6753 | 20.6216 | 19.6268 | 18.6353 | 17.3342 | 16.0868 | 12.1847 | 9.2437 | 7.9679 | 21.1426 | 20.5889 | 19.8963 | 19.1247 | 18.0647 | 17.0426 | 16.0111 | 14.6405 | 13.3426 | 9.5279 | 7.1784 | 5.9711 | 21.8721 | 21.2784 | 20.5647 | 19.7742 | 18.6216 | 17.5363 | 16.4532 | 15.0226 | 13.6626 | 9.4963 | 6.4879 | 5.1363
|  | BUCKIE | EE |  |  |  |  | 22.7953 | 22.6142 | 22.4237 | 22.1521 | 21.0984 | 19.9289 | 18.9574 | 17.9447 | 16.9058 | 12.1847 | 9.2437 | 7.9679 | 21.2574 | 20.9289 | 20.3195 | 19.6511 | 18.5953 | 17.4268 | 16.4826 | 15.4584 | 14.3974 | 9.7247 | 7.1784 | 5.9711 | 21.9868 | 21.6268 | 20.9921 | 20.3005 | 19.15 | 17.8742 | 16.8311 | 15.7268 | 14.5921 | 9.4963 | 6.4879 | 5.1363
|  | BUCKIE | HT |  |  |  |  | 22.6805 | 22.4668 | 22.23 | 21.6753 | 20.6216 | 19.6268 | 18.6353 | 17.3342 | 16.0868 | 12.2753 | 10.3163 | 9.1132 | 21.1426 | 20.5889 | 19.8963 | 19.1247 | 18.0647 | 17.0426 | 16.0111 | 14.6405 | 13.3426 | 9.5279 | 7.6174 | 6.3816 | 21.8721 | 21.2784 | 20.5647 | 19.7742 | 18.6216 | 17.5363 | 16.4532 | 15.0226 | 13.6626 | 9.6047 | 7.5174 | 6.2205
|  | BUCKIE | HE |  |  |  |  | 22.9542 | 22.8384 | 22.7121 | 22.5637 | 21.7405 | 20.7132 | 19.8363 | 18.7911 | 17.8711 | 14.5226 | 12.6237 | 10.9763 | 21.4163 | 21.3026 | 20.8795 | 20.3005 | 19.2658 | 18.2184 | 17.3416 | 16.2468 | 15.2921 | 11.9637 | 10.2521 | 8.87 | 21.8721 | 21.2784 | 20.5647 | 19.7742 | 18.6216 | 17.5363 | 16.4532 | 15.0226 | 13.6626 | 9.6047 | 7.5174 | 6.2205
|  | BUCKIE | CF |  |  |  |  | 23.0574 | 22.9921 | 22.9268 | 22.8584 | 22.6795 | 22.5142 | 22.3405 | 22.1416 | 21.6711 | 19.4837 | 18.1742 | 17.3753 | 21.5195 | 21.4563 | 21.3921 | 21.3258 | 20.9995 | 20.6068 | 20.1647 | 19.7279 | 19.2289 | 16.9689 | 15.7532 | 15.0416 | 22.2489 | 22.1837 | 22.1195 | 22.0511 | 21.6742 | 21.2479 | 20.77 | 20.3005 | 19.7721 | 17.3437 | 15.9584 | 15.1247
| FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 0 | 2.0116 | 1.9968 | 1.9821 | 1.9674 | 1.9516 | 1.9347 | 1.9179 | 1.9021 | 1.8853 | 1.82 | 1.7621 | 1.7105 | 1.9884 | 1.9726 | 1.9568 | 1.9411 | 1.9253 | 1.9063 | 1.8884 | 1.8705 | 1.8537 | 1.7821 | 1.7179 | 1.66 | 2.0126 | 1.9968 | 1.9821 | 1.9663 | 1.9505 | 1.9326 | 1.9147 | 1.8979 | 1.8811 | 1.8095 | 1.7474 | 1.6895
|  | BUNOICH | EE |  |  |  |  | 2.0211 | 2.0105 | 1.9979 | 1.9863 | 1.9747 | 1.9653 | 1.9516 | 1.94 | 1.9274 | 1.8716 | 1.8295 | 1.7905 | 1.9989 | 1.9874 | 1.9747 | 1.9621 | 1.9495 | 1.9389 | 1.9253 | 1.9116 | 1.8989 | 1.8389 | 1.7916 | 1.7484 | 2.0221 | 2.0105 | 1.9989 | 1.9863 | 1.9747 | 1.9642 | 1.9505 | 1.9379 | 1.9253 | 1.8653 | 1.82 | 1.7768
|  | BUNOICH | HT |  |  |  |  | 2.0116 | 1.9968 | 1.9821 | 1.9674 | 1.9516 | 1.9347 | 1.9179 | 1.9021 | 1.8853 | 1.82 | 1.7621 | 1.7105 | 1.9884 | 1.9726 | 1.9568 | 1.9411 | 1.9253 | 1.9063 | 1.8884 | 1.8705 | 1.8537 | 1.7821 | 1.7179 | 1.66 | 2.0126 | 1.9968 | 1.9821 | 1.9663 | 1.9505 | 1.9326 | 1.9147 | 1.8979 | 1.8811 | 1.8095 | 1.7474 | 1.6895
|  | BUNOICH | HE |  |  |  |  | 2.0347 | 2.0274 | 2.0211 | 2.0137 | 2.0042 | 1.9968 | 1.9905 | 1.9832 | 1.9768 | 1.9484 | 1.9242 | 1.9042 | 2.0147 | 2.0053 | 1.9989 | 1.9905 | 1.9821 | 1.9737 | 1.9663 | 1.96 | 1.9526 | 1.9221 | 1.8947 | 1.8726 | 2.0126 | 1.9968 | 1.9821 | 1.9663 | 1.9505 | 1.9326 | 1.9147 | 1.8979 | 1.8811 | 1.8095 | 1.7474 | 1.6895
|  | BUNOICH | CF |  |  |  |  | 2.04 | 2.0379 | 2.0337 | 2.0295 | 2.0242 | 2.02 | 2.0158 | 2.0116 | 2.0063 | 1.9874 | 1.9705 | 1.9558 | 2.02 | 2.0168 | 2.0126 | 2.0074 | 2.0032 | 1.9979 | 1.9926 | 1.9895 | 1.9832 | 1.9632 | 1.9453 | 1.9274 | 2.0347 | 2.0316 | 2.0284 | 2.0263 | 2.0232 | 2.0211 | 2.0168 | 2.0126 | 2.0074 | 1.9874 | 1.9695 | 1.9537
| THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | YES | 0 | -1.5379 | -1.5684 | -1.6011 | -1.6337 | -1.6821 | -1.7295 | -3.7221 | -3.7632 | -3.8032 | -3.9621 | -4.0989 | -4.9389 | -1.8189 | -1.8726 | -1.9326 | -1.9895 | -2.0621 | -2.1253 | -3.6947 | -3.74 | -3.7842 | -3.9526 | -4.1095 | -4.7979 | -3.5695 | -3.6242 | -3.6874 | -3.7442 | -3.8221 | -3.8895 | -4.7116 | -4.7347 | -4.7558 | -4.8758 | -4.9853 | -6.1811
|  | BURGARHILL | EE |  |  |  |  | -1.52 | -1.5463 | -1.5737 | -1.6032 | -1.6495 | -1.6989 | -1.7232 | -1.7663 | -1.8105 | -2.0189 | -2.4042 | -3.8095 | -1.7832 | -1.8263 | -1.8779 | -1.9263 | -1.9905 | -2.0632 | -2.1011 | -2.1547 | -2.2147 | -2.4968 | -2.8453 | -3.9979 | -3.5337 | -3.5779 | -3.6295 | -3.6811 | -3.7505 | -3.8295 | -3.8674 | -3.9263 | -3.9926 | -4.3042 | -4.7053 | -6.1126
|  | BURGARHILL | HT |  |  |  |  | -1.5379 | -1.5684 | -1.6011 | -1.6337 | -1.6821 | -1.7295 | -1.7611 | -1.8095 | -1.8589 | -2.0768 | -2.5463 | -3.8463 | -1.8189 | -1.8726 | -1.9326 | -1.9895 | -2.0621 | -2.1253 | -2.1789 | -2.2495 | -2.3168 | -2.5789 | -3.0053 | -4.0926 | -3.5695 | -3.6242 | -3.6874 | -3.7442 | -3.8221 | -3.8895 | -3.9442 | -4.02 | -4.0926 | -4.3758 | -4.8674 | -6.1811
|  | BURGARHILL | HE |  |  |  |  | -1.4937 | -1.5116 | -1.5316 | -1.5505 | -1.5716 | -1.6063 | -3.7221 | -3.7632 | -3.8032 | -3.9621 | -4.0989 | -4.9389 | -1.7326 | -1.7611 | -1.7884 | -1.8168 | -1.8516 | -1.9021 | -3.6947 | -3.74 | -3.7842 | -3.9526 | -4.1095 | -4.7979 | -3.5695 | -3.6242 | -3.6874 | -3.7442 | -3.8221 | -3.8895 | -3.9442 | -4.02 | -4.0926 | -4.3758 | -4.8674 | -6.1811
|  | BURGARHILL | CF |  |  |  |  | -1.4789 | -1.4884 | -1.4989 | -1.5084 | -1.5189 | -1.5347 | -2.5811 | -2.5989 | -2.6158 | -2.7063 | -2.7905 | -2.8537 | -1.7063 | -1.7221 | -1.7389 | -1.7568 | -1.7758 | -1.8032 | -2.7379 | -2.76 | -2.78 | -2.8895 | -2.9874 | -3.0705 | -3.4547 | -3.4705 | -3.4884 | -3.5063 | -3.5253 | -3.5547 | -4.7116 | -4.7347 | -4.7558 | -4.8758 | -4.9853 | -5.0758
| ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 0 | 17.3279 | 17.21 | 17.0532 | 16.8132 | 16.3963 | 15.9921 | 15.5921 | 15.1595 | 14.7258 | 12.7711 | 10.8837 | 9.2826 | 15.7716 | 15.5284 | 15.2758 | 15.0116 | 14.6147 | 14.2326 | 13.8547 | 13.4579 | 13.0589 | 11.4147 | 9.7642 | 8.1189 | 16.8055 | 16.5803 | 16.3455 | 16.1003 | 15.675 | 15.2603 | 14.8382 | 14.3876 | 13.935 | 11.9329 | 9.9855 | 8.1982
|  | BURGHEAD | EE |  |  |  |  | 17.39 | 17.29 | 17.1847 | 17.0426 | 16.6163 | 16.1405 | 15.6879 | 15.3005 | 14.9216 | 12.7711 | 10.8837 | 9.2826 | 15.8958 | 15.7011 | 15.4947 | 15.2747 | 14.8821 | 14.4516 | 14.0495 | 13.7074 | 13.3716 | 11.4147 | 9.7642 | 8.1189 | 16.8929 | 16.735 | 16.5424 | 16.335 | 15.8992 | 15.4161 | 14.9539 | 14.5592 | 14.1739 | 11.9329 | 9.9855 | 8.1982
|  | BURGHEAD | HT |  |  |  |  | 17.3279 | 17.21 | 17.0532 | 16.8132 | 16.3963 | 15.9921 | 15.5921 | 15.1595 | 14.7258 | 13.0616 | 11.61 | 10.3037 | 15.7716 | 15.5284 | 15.2758 | 15.0116 | 14.6147 | 14.2326 | 13.8547 | 13.4579 | 13.0589 | 11.5221 | 10.06 | 8.6126 | 16.8055 | 16.5803 | 16.3455 | 16.1003 | 15.675 | 15.2603 | 14.8382 | 14.3876 | 13.935 | 12.1897 | 10.6013 | 9.1045
|  | BURGHEAD | HE |  |  |  |  | 17.4742 | 17.4142 | 17.3468 | 17.2753 | 16.95 | 16.5795 | 16.2268 | 15.8995 | 15.5837 | 14.13 | 12.59 | 10.6732 | 16.0642 | 15.9284 | 15.7747 | 15.6042 | 15.2379 | 14.8968 | 14.5779 | 14.2874 | 14.0053 | 12.6905 | 11.2495 | 9.4 | 16.8055 | 16.5803 | 16.3455 | 16.1003 | 15.675 | 15.2603 | 14.8382 | 14.3876 | 13.935 | 12.1897 | 10.6013 | 9.1045
|  | BURGHEAD | CF |  |  |  |  | 17.5279 | 17.4953 | 17.4605 | 17.4258 | 17.3047 | 17.1942 | 17.0837 | 16.9879 | 16.9089 | 16.0942 | 15.1489 | 14.0163 | 16.1674 | 16.0968 | 16.0211 | 15.9432 | 15.7937 | 15.6453 | 15.4905 | 15.3642 | 15.2516 | 14.4484 | 13.5653 | 12.3789 | 17.0834 | 17.0361 | 16.9845 | 16.9329 | 16.7918 | 16.635 | 16.4687 | 16.3318 | 16.2129 | 15.3634 | 14.3855 | 13.1139
| BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 1.388 | 12.3591 | 11.9707 | 11.4602 | 10.8675 | 9.9802 | 9.1791 | 8.3728 | 7.4433 | 6.3717 | 1.7717 | -2.4367 | -6.0977 | 10.1699 | 9.6741 | 9.0636 | 8.4067 | 7.5099 | 6.7078 | 5.8973 | 4.9646 | 3.8625 | -0.96695 | -5.168 | -8.8817 | 11.1477 | 10.6856 | 10.1213 | 9.5171 | 8.6108 | 7.7971 | 6.9308 | 5.9308 | 4.7634 | -0.31129 | -4.8281 | -8.9871
|  | BURGHMUIR | EE |  |  |  |  | 12.5738 | 12.2928 | 11.9644 | 11.5833 | 10.7528 | 9.7654 | 9.0128 | 8.3138 | 7.5738 | 2.7202 | -2.4367 | -6.0977 | 10.4394 | 10.0899 | 9.6667 | 9.2067 | 8.3867 | 7.4015 | 6.7004 | 6.0373 | 5.3267 | 0.44253 | -4.8027 | -8.8648 | 11.3992 | 11.0687 | 10.674 | 10.2456 | 9.3982 | 8.3877 | 7.6213 | 6.9066 | 6.1192 | 0.83608 | -4.8281 | -8.9871
|  | BURGHMUIR | HT |  |  |  |  | 12.3591 | 11.9707 | 11.4602 | 10.8675 | 9.9802 | 9.1791 | 8.3728 | 7.4433 | 6.3717 | 1.7717 | -2.0956 | -5.3451 | 10.1699 | 9.6741 | 9.0636 | 8.4067 | 7.5099 | 6.7078 | 5.8973 | 4.9646 | 3.8625 | -0.96695 | -5.168 | -8.8817 | 11.1477 | 10.6856 | 10.1213 | 9.5171 | 8.6108 | 7.7971 | 6.9308 | 5.9308 | 4.7634 | -0.31129 | -4.645 | -8.4102
|  | BURGHMUIR | HE |  |  |  |  | 12.8296 | 12.6338 | 12.3759 | 12.0854 | 11.2707 | 10.3959 | 9.6875 | 8.917 | 8.0612 | 4.0844 | 0.40016 | -3.2704 | 10.7688 | 10.5152 | 10.1646 | 9.7657 | 8.9288 | 8.0299 | 7.3278 | 6.5499 | 5.6678 | 1.5509 | -2.2891 | -6.0891 | 11.1477 | 10.6856 | 10.1213 | 9.5171 | 8.6108 | 7.7971 | 6.9308 | 5.9308 | 4.7634 | -0.31129 | -4.645 | -8.4102
|  | BURGHMUIR | CF |  |  |  |  | 12.9412 | 12.8707 | 12.7633 | 12.6475 | 12.3981 | 12.1454 | 11.8781 | 11.6454 | 11.4065 | 9.2054 | 6.4307 | 3.9486 | 10.892 | 10.8152 | 10.6794 | 10.5309 | 10.2752 | 10.0004 | 9.6973 | 9.4394 | 9.1478 | 6.7973 | 3.8257 | 1.1046 | 11.6592 | 11.5961 | 11.5287 | 11.4592 | 11.2077 | 10.9224 | 10.6119 | 10.3466 | 10.0624 | 7.7761 | 4.6656 | 1.8529
| CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.093684 | 0.090526 | 0.085263 | 0.082105 | 0.075789 | 0.041053 | -0.004211 | -0.043158 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.092632 | 0.090526 | 0.085263 | 0.082105 | 0.075789 | 0.038947 | -0.012632 | -0.049474 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.092632 | 0.090526 | 0.086316 | 0.083158 | 0.075789 | 0.034737 | -0.017895 | -0.058947
|  | BUTTERBRIDGE | EE |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.093684 | 0.091579 | 0.086316 | 0.08421 | 0.08 | 0.041053 | -0.004211 | -0.043158 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.092632 | 0.090526 | 0.087368 | 0.085263 | 0.082105 | 0.043158 | -0.003158 | -0.046316 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.093684 | 0.090526 | 0.086316 | 0.083158 | 0.08 | 0.036842 | -0.013684 | -0.058947
|  | BUTTERBRIDGE | HT |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.093684 | 0.092632 | 0.088421 | 0.085263 | 0.077895 | 0.041053 | -0.004211 | -0.036842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.092632 | 0.091579 | 0.088421 | 0.086316 | 0.077895 | 0.038947 | -0.012632 | -0.049474 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.092632 | 0.091579 | 0.088421 | 0.085263 | 0.075789 | 0.034737 | -0.017895 | -0.055789
|  | BUTTERBRIDGE | HE |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.094737 | 0.090526 | 0.085263 | 0.082105 | 0.075789 | 0.048421 | 0.011579 | -0.027368 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.093684 | 0.090526 | 0.085263 | 0.082105 | 0.075789 | 0.048421 | 0.0094737 | -0.032632 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.092632 | 0.091579 | 0.088421 | 0.085263 | 0.075789 | 0.034737 | -0.017895 | -0.055789
|  | BUTTERBRIDGE | CF |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.093684 | 0.091579 | 0.087368 | 0.071579 | 0.049474 | 0.023158 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.092632 | 0.089474 | 0.086316 | 0.070526 | 0.046316 | 0.017895 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.090526 | 0.086316 | 0.069474 | 0.04421 | 0.013684
| BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 0 | 8.3495 | 8.1653 | 7.9358 | 7.6842 | 7.4021 | 7.12 | 6.8253 | 6.5368 | 6.2474 | 4.8274 | 3.5684 | 2.3968 | 6.8695 | 6.6632 | 6.4053 | 6.1179 | 5.7989 | 5.4789 | 5.1421 | 4.8158 | 4.4863 | 2.8726 | 1.4221 | 0.064211 | 8.0874 | 7.88 | 7.6211 | 7.3316 | 7.0126 | 6.6916 | 6.3537 | 6.0232 | 5.6926 | 4.0621 | 2.6063 | 1.2463
|  | CALLANDER | EE |  |  |  |  | 8.4389 | 8.2842 | 8.0905 | 7.8726 | 7.6326 | 7.4011 | 7.1432 | 6.9021 | 6.6589 | 5.4242 | 4.3453 | 3.3589 | 6.9705 | 6.8021 | 6.5863 | 6.3432 | 6.0747 | 5.8168 | 5.5274 | 5.2547 | 4.9811 | 3.5926 | 2.3663 | 1.24 | 8.18 | 8.0116 | 7.7926 | 7.5453 | 7.2705 | 7.0074 | 6.7116 | 6.4337 | 6.1547 | 4.7358 | 3.4895 | 2.3453
|  | CALLANDER | HT |  |  |  |  | 8.3495 | 8.1653 | 7.9358 | 7.6842 | 7.4021 | 7.12 | 6.8253 | 6.5368 | 6.2474 | 4.8274 | 3.5684 | 2.3968 | 6.8695 | 6.6632 | 6.4053 | 6.1179 | 5.7989 | 5.4789 | 5.1421 | 4.8158 | 4.4863 | 2.8726 | 1.4221 | 0.064211 | 8.0874 | 7.88 | 7.6211 | 7.3316 | 7.0126 | 6.6916 | 6.3537 | 6.0232 | 5.6926 | 4.0621 | 2.6063 | 1.2463
|  | CALLANDER | HE |  |  |  |  | 8.5505 | 8.4526 | 8.3021 | 8.1232 | 7.9179 | 7.7274 | 7.5063 | 7.2979 | 7.0863 | 6.0726 | 5.1432 | 4.2863 | 7.1084 | 6.9821 | 6.8116 | 6.6074 | 6.3758 | 6.1589 | 5.9053 | 5.6642 | 5.4232 | 4.2474 | 3.1768 | 2.1884 | 8.0874 | 7.88 | 7.6211 | 7.3316 | 7.0126 | 6.6916 | 6.3537 | 6.0232 | 5.6926 | 4.0621 | 2.6063 | 1.2463
|  | CALLANDER | CF |  |  |  |  | 8.6211 | 8.5716 | 8.5116 | 8.4347 | 8.3432 | 8.2526 | 8.1484 | 8.0411 | 7.9284 | 7.3105 | 6.7579 | 6.2579 | 7.2 | 7.1316 | 7.0495 | 6.9568 | 6.8547 | 6.7505 | 6.6326 | 6.5095 | 6.3779 | 5.6611 | 5.0126 | 4.4211 | 8.38 | 8.3232 | 8.2547 | 8.1747 | 8.0716 | 7.9663 | 7.8484 | 7.7253 | 7.5926 | 6.8726 | 6.2221 | 5.6295
| STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 0 | 2.02 | 1.9874 | 1.9537 | 1.9189 | 1.8821 | 1.8463 | 1.8126 | 1.7789 | 1.7337 | 1.5368 | 0.59579 | 0.45789 | 2.0474 | 2.0147 | 1.9684 | 1.9074 | 1.8442 | 1.7842 | 1.7263 | 1.6705 | 1.6168 | 1.4032 | 0.61263 | 0.46211 | 2 | 1.9379 | 1.8758 | 1.8147 | 1.7537 | 1.6937 | 1.6368 | 1.5811 | 1.5284 | 1.3168 | 0.32526 | 0.17368
|  | CALLANISH | EE |  |  |  |  | 2.0368 | 2.0095 | 1.9811 | 1.9516 | 1.9211 | 1.8926 | 1.8642 | 1.8379 | 1.8126 | 1.6905 | 0.78737 | 0.68842 | 2.0642 | 2.0368 | 2.0084 | 1.9789 | 1.9337 | 1.8863 | 1.8389 | 1.7958 | 1.7537 | 1.5716 | 0.81789 | 0.71263 | 2.0358 | 1.9905 | 1.9411 | 1.8905 | 1.8411 | 1.7937 | 1.7474 | 1.7042 | 1.6621 | 1.4832 | 0.53474 | 0.42632
|  | CALLANISH | HT |  |  |  |  | 2.02 | 1.9874 | 1.9537 | 1.9189 | 1.8821 | 1.8463 | 1.8126 | 1.7789 | 1.7337 | 1.5368 | 0.59579 | 0.45789 | 2.0474 | 2.0147 | 1.9684 | 1.9074 | 1.8442 | 1.7842 | 1.7263 | 1.6705 | 1.6168 | 1.4032 | 0.61263 | 0.46211 | 2 | 1.9379 | 1.8758 | 1.8147 | 1.7537 | 1.6937 | 1.6368 | 1.5811 | 1.5284 | 1.3168 | 0.32526 | 0.17368
|  | CALLANISH | HE |  |  |  |  | 2.0642 | 2.0453 | 2.0242 | 2.0021 | 1.9789 | 1.9579 | 1.9368 | 1.9168 | 1.8989 | 1.8389 | 1.4526 | 1.4368 | 2.0916 | 2.0726 | 2.0516 | 2.0295 | 2.0063 | 1.9853 | 1.9642 | 1.9442 | 1.9263 | 1.8411 | 1.4674 | 1.4158 | 2 | 1.9379 | 1.8758 | 1.8147 | 1.7537 | 1.6937 | 1.6368 | 1.5811 | 1.5284 | 1.3168 | 0.32526 | 0.17368
|  | CALLANISH | CF |  |  |  |  | 2.0821 | 2.0716 | 2.0611 | 2.0505 | 2.0389 | 2.0284 | 2.0168 | 2.0063 | 1.9947 | 1.9474 | 1.9242 | 1.9126 | 2.1095 | 2.0989 | 2.0884 | 2.0779 | 2.0663 | 2.0558 | 2.0442 | 2.0337 | 2.0221 | 1.9747 | 1.9189 | 1.8737 | 2.0968 | 2.0863 | 2.0747 | 2.06 | 2.0432 | 2.0284 | 2.0126 | 1.9958 | 1.9747 | 1.8874 | 1.8274 | 1.7821
| TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | 0 | 0.85684 | 0.83579 | 0.81579 | 0.79368 | 0.74105 | 0.68947 | 0.62632 | 0.56842 | 0.51053 | 0.046316 | -0.59789 | -1.1221 | 1.1116 | 1.1011 | 1.0895 | 1.0789 | 1.0505 | 1.0274 | 1.0011 | 0.95895 | 0.91474 | 0.52 | -0.17263 | -0.66526 | 0.85474 | 0.83368 | 0.81368 | 0.79158 | 0.74 | 0.69053 | 0.63053 | 0.57579 | 0.52105 | 0.054737 | -0.62632 | -1.1853
|  | CALVINE | EE |  |  |  |  | 0.86737 | 0.85158 | 0.83263 | 0.81368 | 0.75579 | 0.69368 | 0.62632 | 0.56842 | 0.51053 | 0.046316 | -0.59789 | -1.1221 | 1.1158 | 1.1084 | 1.1 | 1.0895 | 1.0621 | 1.0326 | 1.0011 | 0.95895 | 0.91474 | 0.56105 | -0.082105 | -0.65474 | 0.86526 | 0.84947 | 0.82947 | 0.80947 | 0.75368 | 0.69474 | 0.63053 | 0.57579 | 0.52105 | 0.057895 | -0.60632 | -1.1853
|  | CALVINE | HT |  |  |  |  | 0.85684 | 0.83579 | 0.81579 | 0.79368 | 0.74105 | 0.68947 | 0.63684 | 0.57895 | 0.51789 | 0.056842 | -0.5779 | -1.0158 | 1.1116 | 1.1011 | 1.0895 | 1.0789 | 1.0505 | 1.0274 | 1.0011 | 0.96947 | 0.92211 | 0.52 | -0.17263 | -0.66526 | 0.85474 | 0.83368 | 0.81368 | 0.79158 | 0.74 | 0.69053 | 0.64 | 0.58421 | 0.52737 | 0.054737 | -0.62632 | -1.1147
|  | CALVINE | HE |  |  |  |  | 0.87895 | 0.87263 | 0.86632 | 0.85474 | 0.80211 | 0.75579 | 0.70947 | 0.66526 | 0.61263 | 0.21053 | -0.29474 | -0.84526 | 1.1242 | 1.1189 | 1.1137 | 1.1063 | 1.0811 | 1.0589 | 1.0368 | 1.0168 | 0.99474 | 0.69579 | 0.17053 | -0.4021 | 0.85474 | 0.83368 | 0.81368 | 0.79158 | 0.74 | 0.69053 | 0.64 | 0.58421 | 0.52737 | 0.054737 | -0.62632 | -1.1147
|  | CALVINE | CF |  |  |  |  | 0.88421 | 0.88211 | 0.87789 | 0.87474 | 0.85474 | 0.83579 | 0.81579 | 0.79895 | 0.78316 | 0.60105 | 0.28 | -0.081053 | 1.1284 | 1.1263 | 1.1242 | 1.1211 | 1.1095 | 1.1011 | 1.0916 | 1.0842 | 1.0768 | 1.0105 | 0.71579 | 0.32421 | 0.88211 | 0.88 | 0.87579 | 0.87263 | 0.85263 | 0.83474 | 0.81579 | 0.79895 | 0.78526 | 0.60737 | 0.27368 | -0.10632
| CARRADALE 1 | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 0 | 14.4574 | 14.2479 | 14.0216 | 13.6953 | 13.3226 | 12.9542 | 10.6068 | 10.2805 | 9.9847 | 8.8837 | 8.0132 | 7.4268 | 13.4274 | 13.1853 | 12.9463 | 12.5947 | 12.2032 | 11.8179 | 10.1526 | 9.8011 | 9.4905 | 8.5147 | 7.7305 | 7.1547 | 13.2455 | 12.9961 | 12.7529 | 12.3939 | 11.9887 | 11.5866 | 9.2266 | 8.8718 | 8.5529 | 7.3813 | 6.4561 | 5.815
|  | CAMPBELTOWN | EE |  |  |  |  | 14.5142 | 14.3837 | 14.1679 | 13.8942 | 13.5174 | 13.1016 | 10.6068 | 10.2805 | 9.9847 | 8.8837 | 8.0132 | 7.4268 | 13.56 | 13.3526 | 13.1389 | 12.8579 | 12.4768 | 12.0505 | 10.1526 | 9.8274 | 9.5379 | 8.5147 | 7.7305 | 7.1726 | 13.3666 | 13.1424 | 12.9108 | 12.6118 | 12.1982 | 11.7424 | 9.2266 | 8.8718 | 8.5529 | 7.3813 | 6.4561 | 5.815
|  | CAMPBELTOWN | HT |  |  |  |  | 14.4574 | 14.2479 | 14.0216 | 13.6953 | 13.3226 | 12.9542 | 10.8595 | 10.4963 | 10.1921 | 9.2489 | 8.49 | 7.8721 | 13.4274 | 13.1853 | 12.9463 | 12.5947 | 12.2032 | 11.8179 | 10.1779 | 9.8011 | 9.4905 | 8.5611 | 7.7958 | 7.1547 | 13.2455 | 12.9961 | 12.7529 | 12.3939 | 11.9887 | 11.5866 | 9.4634 | 9.0697 | 8.7413 | 7.7382 | 6.9182 | 6.2413
|  | CAMPBELTOWN | HE |  |  |  |  | 14.6142 | 14.5374 | 14.4542 | 14.31 | 13.9784 | 13.6237 | 12.2711 | 12.0311 | 11.8511 | 11.2668 | 10.8058 | 10.4258 | 13.7642 | 13.6274 | 13.4884 | 13.2611 | 12.9147 | 12.5379 | 11.4716 | 11.2295 | 11.0526 | 10.5179 | 10.1032 | 9.7653 | 13.2455 | 12.9961 | 12.7529 | 12.3939 | 11.9887 | 11.5866 | 9.4634 | 9.0697 | 8.7413 | 7.7382 | 6.9182 | 6.2413
|  | CAMPBELTOWN | CF |  |  |  |  | 14.6732 | 14.6311 | 14.5879 | 14.5458 | 14.4816 | 14.4047 | 13.1637 | 13.0184 | 12.8753 | 12.3963 | 12.0721 | 11.8511 | 13.8737 | 13.7958 | 13.72 | 13.6274 | 13.5 | 13.3611 | 12.4032 | 12.2505 | 12.0968 | 11.6042 | 11.2937 | 11.0737 | 13.6961 | 13.6161 | 13.5403 | 13.4445 | 13.3108 | 13.1645 | 11.9108 | 11.7518 | 11.595 | 11.0782 | 10.735 | 10.495
| COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | YES | 0 | 11.9242 | 11.6884 | 11.4526 | 11.1916 | 10.0463 | 8.5884 | 7.0411 | 5.6726 | 3.9811 | -8.4474 | -22.6695 | -33.2411 | 11.0242 | 10.7853 | 10.5442 | 10.2789 | 9.2874 | 8.1537 | 6.8789 | 5.7263 | 3.7242 | -7.6695 | -21.5653 | -33.001 | 11.1768 | 10.9305 | 10.6789 | 10.4032 | 9.1968 | 7.6526 | 6.0526 | 4.6547 | 3.0274 | -10.5126 | -25.9442 | -37.761
|  | CAPUTH | EE |  |  |  |  | 12 | 11.8326 | 11.6147 | 11.3768 | 10.0747 | 8.5884 | 7.0411 | 5.6726 | 4.2832 | -8.4474 | -22.6695 | -33.2411 | 11.1579 | 10.9495 | 10.7389 | 10.5042 | 9.4011 | 8.1537 | 6.8789 | 5.7263 | 4.5558 | -7.6695 | -21.5653 | -33.001 | 11.3042 | 11.08 | 10.8526 | 10.6 | 9.2242 | 7.6526 | 6.0526 | 4.6547 | 3.2337 | -10.5126 | -25.9442 | -37.761
|  | CAPUTH | HT |  |  |  |  | 11.9242 | 11.6884 | 11.4526 | 11.1916 | 10.0463 | 8.9442 | 7.8295 | 6.5042 | 4.2179 | -7.3053 | -20.1 | -28.7495 | 11.0242 | 10.7853 | 10.5442 | 10.2789 | 9.2874 | 8.3347 | 7.3747 | 6.2674 | 4.0526 | -7.6516 | -21.4747 | -31.1442 | 11.1768 | 10.9305 | 10.6789 | 10.4032 | 9.1968 | 8.0347 | 6.8621 | 5.4905 | 3.0274 | -9.5895 | -23.9758 | -33.9263
|  | CAPUTH | HE |  |  |  |  | 12.0821 | 12.0158 | 11.9411 | 11.86 | 10.4789 | 9.02 | 7.5168 | 6.0695 | 3.9811 | -4.8947 | -15.7842 | -27.6305 | 11.3032 | 11.2295 | 11.1168 | 10.9758 | 9.7958 | 8.4537 | 7.0737 | 5.7716 | 3.7242 | -4.8284 | -15.8568 | -27.8789 | 11.1768 | 10.9305 | 10.6789 | 10.4032 | 9.1968 | 8.0347 | 6.8621 | 5.4905 | 3.0274 | -9.5895 | -23.9758 | -33.9263
|  | CAPUTH | CF |  |  |  |  | 12.1337 | 12.0937 | 12.0537 | 12.0126 | 11.5758 | 11.1168 | 10.4137 | 9.5274 | 8.5432 | 4.0116 | -2.8421 | -10.3495 | 11.3558 | 11.3211 | 11.2853 | 11.2126 | 10.7758 | 10.3821 | 9.7021 | 8.7905 | 7.7284 | 3.1516 | -3.8358 | -11.8547 | 11.4589 | 11.42 | 11.38 | 11.3389 | 10.8053 | 10.3189 | 9.5653 | 8.5853 | 7.4811 | 2.5137 | -5.0095 | -13.4242
| ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 0.175 | 15.8508 | 15.6582 | 15.3834 | 15.0529 | 14.6308 | 14.2182 | 13.8171 | 13.4013 | 12.9939 | 11.3866 | 10.1687 | 9.2466 | 14.265 | 13.7324 | 13.3776 | 13.025 | 12.6018 | 12.1913 | 11.7913 | 11.3808 | 10.9797 | 9.3755 | 8.1271 | 7.1376 | 14.98 | 14.4674 | 14.1105 | 13.7568 | 13.3105 | 12.8768 | 12.4526 | 12.0147 | 11.5842 | 9.8726 | 8.5526 | 7.5337
|  | CARNOUSTIE | EE |  |  |  |  | 15.9613 | 15.8034 | 15.6371 | 15.4108 | 15.0213 | 14.6213 | 14.2361 | 13.8845 | 13.5392 | 11.8539 | 10.3813 | 9.5518 | 14.5566 | 14.085 | 13.7355 | 13.4113 | 13.0292 | 12.6418 | 12.2724 | 11.9324 | 11.5987 | 10.0029 | 8.6366 | 7.7892 | 15.2611 | 14.8053 | 14.4663 | 14.1421 | 13.7316 | 13.3105 | 12.9063 | 12.5368 | 12.1737 | 10.4189 | 8.8789 | 7.9747
|  | CARNOUSTIE | HT |  |  |  |  | 15.8508 | 15.6582 | 15.3834 | 15.0529 | 14.6308 | 14.2182 | 13.8171 | 13.4013 | 12.9939 | 11.3866 | 10.1687 | 9.2466 | 14.265 | 13.7324 | 13.3776 | 13.025 | 12.6018 | 12.1913 | 11.7913 | 11.3808 | 10.9797 | 9.3755 | 8.1271 | 7.1376 | 14.98 | 14.4674 | 14.1105 | 13.7568 | 13.3105 | 12.8768 | 12.4526 | 12.0147 | 11.5842 | 9.8726 | 8.5526 | 7.5337
|  | CARNOUSTIE | HE |  |  |  |  | 16.1097 | 16.0034 | 15.8887 | 15.7666 | 15.5203 | 15.3034 | 15.0897 | 14.8634 | 14.6182 | 13.5634 | 12.7361 | 11.9708 | 14.8797 | 14.4913 | 14.2503 | 14.0397 | 13.7429 | 13.4808 | 13.2261 | 12.9808 | 12.7461 | 11.7513 | 10.9997 | 10.3229 | 14.98 | 14.4674 | 14.1105 | 13.7568 | 13.3105 | 12.8768 | 12.4526 | 12.0147 | 11.5842 | 9.8726 | 8.5526 | 7.5337
|  | CARNOUSTIE | CF |  |  |  |  | 16.2034 | 16.1445 | 16.0855 | 16.0234 | 15.9192 | 15.8182 | 15.7192 | 15.6245 | 15.5403 | 15.0939 | 14.5624 | 14.1371 | 15.185 | 15.0692 | 14.9292 | 14.7829 | 14.6071 | 14.4261 | 14.2461 | 14.0903 | 13.9408 | 13.2545 | 12.6934 | 12.2797 | 15.6537 | 15.5958 | 15.5358 | 15.4747 | 15.2926 | 15.1053 | 14.92 | 14.76 | 14.6084 | 13.8874 | 13.2684 | 12.8147
| KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 0 | 1.0221 | 1.02 | 1.0158 | 1.0126 | 1 | 0.98842 | 0.97474 | 0.96105 | 0.94737 | 0.88632 | 0.81895 | 0.78737 | 1.0147 | 1.0116 | 1.0032 | 0.99579 | 0.98316 | 0.97158 | 0.95895 | 0.94737 | 0.93368 | 0.88 | 0.82632 | 0.79579 | 1.0137 | 1.0074 | 0.99789 | 0.99053 | 0.97579 | 0.96316 | 0.94947 | 0.93474 | 0.92 | 0.85895 | 0.78947 | 0.75579
|  | CASHLIE | EE |  |  |  |  | 1.0232 | 1.02 | 1.0189 | 1.0158 | 1.0074 | 0.99579 | 0.98105 | 0.96842 | 0.95474 | 0.88632 | 0.81895 | 0.78737 | 1.0158 | 1.0137 | 1.0126 | 1.0074 | 0.99474 | 0.98211 | 0.96842 | 0.95789 | 0.94632 | 0.88526 | 0.82632 | 0.79579 | 1.0168 | 1.0116 | 1.0074 | 1.0011 | 0.98737 | 0.97158 | 0.95684 | 0.94421 | 0.92947 | 0.85895 | 0.78947 | 0.75579
|  | CASHLIE | HT |  |  |  |  | 1.0221 | 1.02 | 1.0158 | 1.0126 | 1 | 0.98842 | 0.97474 | 0.96105 | 0.94737 | 0.88947 | 0.84632 | 0.81789 | 1.0147 | 1.0116 | 1.0032 | 0.99579 | 0.98316 | 0.97158 | 0.95895 | 0.94737 | 0.93368 | 0.88 | 0.83789 | 0.80842 | 1.0137 | 1.0074 | 0.99789 | 0.99053 | 0.97579 | 0.96316 | 0.94947 | 0.93474 | 0.92 | 0.85895 | 0.81263 | 0.78105
|  | CASHLIE | HE |  |  |  |  | 1.0253 | 1.0242 | 1.0232 | 1.0211 | 1.0116 | 1.0032 | 0.99579 | 0.98842 | 0.98105 | 0.93789 | 0.89789 | 0.85579 | 1.0179 | 1.0168 | 1.0158 | 1.0137 | 1.0084 | 1.0021 | 0.99263 | 0.98526 | 0.97579 | 0.93579 | 0.90211 | 0.86421 | 1.0137 | 1.0074 | 0.99789 | 0.99053 | 0.97579 | 0.96316 | 0.94947 | 0.93474 | 0.92 | 0.85895 | 0.81263 | 0.78105
|  | CASHLIE | CF |  |  |  |  | 1.0263 | 1.0263 | 1.0253 | 1.0242 | 1.0211 | 1.0179 | 1.0137 | 1.0116 | 1.0084 | 0.99368 | 0.97263 | 0.95158 | 1.0189 | 1.0189 | 1.0179 | 1.0168 | 1.0158 | 1.0126 | 1.0105 | 1.0095 | 1.0063 | 0.98632 | 0.96421 | 0.94526 | 1.0221 | 1.0211 | 1.02 | 1.0189 | 1.0147 | 1.0105 | 1.0063 | 1.0021 | 0.99789 | 0.97474 | 0.94842 | 0.92632
| KILLIN | CHAORACH | MINIMUM HEADROOM | NN 45400 27553 | YES | YES | 0 | -2.0537 | -2.0558 | -2.0589 | -2.0611 | -2.0642 | -2.0663 | -2.0684 | -2.0716 | -2.0737 | -2.0853 | -2.0937 | -2.1021 | -1.6547 | -1.6558 | -1.6568 | -1.6579 | -1.66 | -1.6611 | -1.6621 | -1.6632 | -1.6642 | -1.6695 | -1.6726 | -1.6758 | -1.9632 | -1.9653 | -1.9695 | -1.9768 | -1.9842 | -1.9916 | -1.9989 | -2.0063 | -2.0126 | -2.0516 | -2.0874 | -2.1242
|  | CHAORACH | EE |  |  |  |  | -2.0537 | -2.0558 | -2.0589 | -2.0611 | -2.0642 | -2.0663 | -2.0684 | -2.0716 | -2.0737 | -2.0853 | -2.0937 | -2.1021 | -1.6547 | -1.6558 | -1.6568 | -1.6579 | -1.66 | -1.6611 | -1.6621 | -1.6632 | -1.6642 | -1.6695 | -1.6726 | -1.6758 | -1.9632 | -1.9653 | -1.9684 | -1.9758 | -1.9842 | -1.9884 | -1.9947 | -2.0032 | -2.0116 | -2.0516 | -2.0874 | -2.1242
|  | CHAORACH | HT |  |  |  |  | -2.0537 | -2.0558 | -2.0568 | -2.0579 | -2.06 | -2.0621 | -2.0632 | -2.0663 | -2.0663 | -2.0747 | -2.0811 | -2.0863 | -1.6547 | -1.6558 | -1.6558 | -1.6579 | -1.6589 | -1.66 | -1.6611 | -1.6621 | -1.6621 | -1.6663 | -1.6695 | -1.6716 | -1.9632 | -1.9642 | -1.9695 | -1.9768 | -1.9842 | -1.9916 | -1.9989 | -2.0063 | -2.0126 | -2.0484 | -2.0821 | -2.1147
|  | CHAORACH | HE |  |  |  |  | -2.0526 | -2.0537 | -2.0537 | -2.0547 | -2.0579 | -2.0579 | -2.06 | -2.0611 | -2.0611 | -2.0674 | -2.0737 | -2.0779 | -1.6537 | -1.6537 | -1.6537 | -1.6558 | -1.6568 | -1.6568 | -1.6579 | -1.6579 | -1.6579 | -1.6611 | -1.6632 | -1.6642 | -1.9632 | -1.9642 | -1.9695 | -1.9768 | -1.9842 | -1.9916 | -1.9989 | -2.0063 | -2.0126 | -2.0484 | -2.0821 | -2.1147
|  | CHAORACH | CF |  |  |  |  | -2.0516 | -2.0516 | -2.0526 | -2.0526 | -2.0526 | -2.0526 | -2.0537 | -2.0547 | -2.0558 | -2.0579 | -2.0611 | -2.0632 | -1.6526 | -1.6526 | -1.6537 | -1.6537 | -1.6537 | -1.6537 | -1.6547 | -1.6547 | -1.6547 | -1.6558 | -1.6579 | -1.6579 | -1.9579 | -1.9589 | -1.9611 | -1.9611 | -1.9611 | -1.9621 | -1.9653 | -1.9684 | -1.9716 | -1.9905 | -2.0105 | -2.0284
| ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 0 | 12.4926 | 12.3368 | 12.1758 | 12.0368 | 11.8337 | 11.6326 | 11.3568 | 11.0832 | 10.8126 | 9.6811 | 8.7537 | 7.9579 | 11.8137 | 11.6505 | 11.4832 | 11.2505 | 10.9347 | 10.6263 | 10.3263 | 10.0305 | 9.7368 | 8.5168 | 7.5242 | 6.6537 | 12.0316 | 11.8684 | 11.6989 | 11.56 | 11.2432 | 10.9305 | 10.6242 | 10.3211 | 10.02 | 8.7726 | 7.7516 | 6.8674
|  | CHARLES AVENUE | EE |  |  |  |  | 12.5853 | 12.4589 | 12.3253 | 12.1874 | 12.0137 | 11.8632 | 11.6905 | 11.5316 | 11.3663 | 10.3274 | 9.4695 | 8.8495 | 11.9126 | 11.7821 | 11.6442 | 11.5011 | 11.3137 | 11.1137 | 10.86 | 10.6221 | 10.3916 | 9.2947 | 8.4084 | 7.7263 | 12.1305 | 11.9979 | 11.8589 | 11.7147 | 11.5389 | 11.3979 | 11.1389 | 10.8958 | 10.6579 | 9.5137 | 8.5737 | 7.8811
|  | CHARLES AVENUE | HT |  |  |  |  | 12.4926 | 12.3368 | 12.1758 | 12.0368 | 11.8337 | 11.6326 | 11.3568 | 11.0832 | 10.8126 | 9.6811 | 8.7537 | 7.9579 | 11.8137 | 11.6505 | 11.4832 | 11.2505 | 10.9347 | 10.6263 | 10.3263 | 10.0305 | 9.7368 | 8.5168 | 7.5242 | 6.6537 | 12.0316 | 11.8684 | 11.6989 | 11.56 | 11.2432 | 10.9305 | 10.6242 | 10.3211 | 10.02 | 8.7726 | 7.7516 | 6.8674
|  | CHARLES AVENUE | HE |  |  |  |  | 12.6958 | 12.6032 | 12.5042 | 12.3979 | 12.2495 | 12.1158 | 11.9853 | 11.8379 | 11.7211 | 11.2895 | 10.9642 | 10.5979 | 12.0316 | 11.9368 | 11.8347 | 11.7232 | 11.5937 | 11.4737 | 11.3568 | 11.2147 | 11.1116 | 10.4968 | 10.0295 | 9.6432 | 12.0316 | 11.8684 | 11.6989 | 11.56 | 11.2432 | 10.9305 | 10.6242 | 10.3211 | 10.02 | 8.7726 | 7.7516 | 6.8674
|  | CHARLES AVENUE | CF |  |  |  |  | 12.7684 | 12.7137 | 12.6589 | 12.6021 | 12.5316 | 12.4621 | 12.3926 | 12.3242 | 12.26 | 11.9579 | 11.7568 | 11.6168 | 12.1063 | 12.0516 | 11.9947 | 11.9337 | 11.8695 | 11.8042 | 11.7379 | 11.6726 | 11.6095 | 11.3211 | 10.9358 | 10.6463 | 12.3221 | 12.2674 | 12.2116 | 12.1516 | 12.08 | 12.0084 | 11.9379 | 11.8684 | 11.8021 | 11.4926 | 11.1884 | 10.8916
| CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | YES | 0 | 16.3405 | 16.2889 | 16.2311 | 16.0563 | 15.89 | 15.7321 | 15.5668 | 15.4321 | 15.3279 | 14.9489 | 14.6458 | 14.3984 | 15.2221 | 15.1695 | 15.1116 | 14.9316 | 14.7232 | 14.5221 | 14.3126 | 14.1463 | 14.0211 | 13.5863 | 13.2558 | 12.9811 | 15.7382 | 15.6424 | 15.4255 | 15.1834 | 14.9834 | 14.7939 | 14.5939 | 14.4339 | 14.3139 | 13.8897 | 13.555 | 13.2792
|  | CHARLESTON | EE |  |  |  |  | 16.37 | 16.33 | 16.2868 | 16.2374 | 16.0984 | 15.8447 | 15.7079 | 15.5889 | 15.4774 | 15.0858 | 14.8321 | 14.6363 | 15.2526 | 15.2116 | 15.1674 | 15.1168 | 14.9916 | 14.6547 | 14.4832 | 14.3326 | 14.1947 | 13.7368 | 13.4674 | 13.2526 | 15.7634 | 15.7276 | 15.6361 | 15.4571 | 15.2371 | 14.9203 | 14.7561 | 14.6118 | 14.4792 | 14.0318 | 13.7571 | 13.5403
|  | CHARLESTON | HT |  |  |  |  | 16.3405 | 16.2889 | 16.2311 | 16.0563 | 15.89 | 15.7321 | 15.5668 | 15.4321 | 15.3279 | 14.9489 | 14.6458 | 14.3984 | 15.2221 | 15.1695 | 15.1116 | 14.9316 | 14.7232 | 14.5221 | 14.3126 | 14.1463 | 14.0211 | 13.5863 | 13.2558 | 12.9811 | 15.7382 | 15.6424 | 15.4255 | 15.1834 | 14.9834 | 14.7939 | 14.5939 | 14.4339 | 14.3139 | 13.8897 | 13.555 | 13.2792
|  | CHARLESTON | HE |  |  |  |  | 16.3995 | 16.3668 | 16.3289 | 16.2858 | 16.1395 | 15.8942 | 15.7511 | 15.6595 | 15.6026 | 15.3995 | 15.2595 | 15.1416 | 15.2821 | 15.2484 | 15.2095 | 15.1653 | 15.0263 | 14.6989 | 14.5126 | 14.3979 | 14.3316 | 14.0979 | 13.9347 | 13.8032 | 15.7382 | 15.6424 | 15.4255 | 15.1834 | 14.9834 | 14.7939 | 14.5939 | 14.4339 | 14.3139 | 13.8897 | 13.555 | 13.2792
|  | CHARLESTON | CF |  |  |  |  | 16.4216 | 16.4047 | 16.3847 | 16.3658 | 16.3426 | 16.3184 | 16.2858 | 16.2605 | 16.1963 | 15.9363 | 15.8279 | 15.7458 | 15.3042 | 15.2874 | 15.2674 | 15.2474 | 15.2253 | 15.2011 | 15.1684 | 15.1432 | 15.1074 | 14.7811 | 14.6537 | 14.5516 | 15.8076 | 15.7918 | 15.7739 | 15.7571 | 15.7371 | 15.7097 | 15.5603 | 15.4624 | 15.3466 | 15.0361 | 14.9097 | 14.8118
| ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | NO | YES | 0 | 6.1021 | 6.0347 | 5.9695 | 5.9042 | 5.8379 | 5.7747 | 5.7137 | 5.6547 | 5.5979 | 5.3747 | 3.6305 | 3.4758 | 6.0842 | 6.0116 | 5.9421 | 5.8726 | 5.8011 | 5.7337 | 5.6684 | 5.6053 | 5.5442 | 5.3021 | 3.8937 | 3.7274 | 6.1042 | 6.0368 | 5.9716 | 5.9063 | 5.8389 | 5.7758 | 5.7147 | 5.6558 | 5.5989 | 5.3695 | 3.5779 | 3.4042
|  | CLACHAN | EE |  |  |  |  | 6.1442 | 6.0916 | 6.0379 | 5.9842 | 5.9316 | 5.88 | 5.8326 | 5.7853 | 5.7421 | 5.5505 | 3.8432 | 3.7389 | 6.1305 | 6.0747 | 6.0168 | 5.9589 | 5.9032 | 5.8495 | 5.7989 | 5.7484 | 5.7011 | 5.4958 | 4.1274 | 4.0084 | 6.1463 | 6.0937 | 6.0389 | 5.9853 | 5.9337 | 5.8821 | 5.8347 | 5.7874 | 5.7432 | 5.5526 | 3.8211 | 3.6958
|  | CLACHAN | HT |  |  |  |  | 6.1021 | 6.0347 | 5.9695 | 5.9042 | 5.8379 | 5.7747 | 5.7137 | 5.6547 | 5.5979 | 5.3747 | 3.6305 | 3.4758 | 6.0842 | 6.0116 | 5.9421 | 5.8726 | 5.8011 | 5.7337 | 5.6684 | 5.6053 | 5.5442 | 5.3021 | 3.8937 | 3.7274 | 6.1042 | 6.0368 | 5.9716 | 5.9063 | 5.8389 | 5.7758 | 5.7147 | 5.6558 | 5.5989 | 5.3695 | 3.5779 | 3.4042
|  | CLACHAN | HE |  |  |  |  | 6.2074 | 6.1726 | 6.1368 | 6.1011 | 6.0484 | 6.0189 | 5.9884 | 5.9653 | 5.9368 | 5.8295 | 4.9758 | 4.9305 | 6.2 | 6.1632 | 6.1253 | 6.0874 | 6.0295 | 5.9989 | 5.9684 | 5.9442 | 5.9137 | 5.7989 | 5.1347 | 5.0789 | 6.1042 | 6.0368 | 5.9716 | 5.9063 | 5.8389 | 5.7758 | 5.7147 | 5.6558 | 5.5989 | 5.3695 | 3.5779 | 3.4042
|  | CLACHAN | CF |  |  |  |  | 6.2411 | 6.2211 | 6.2011 | 6.1789 | 6.1589 | 6.1379 | 6.1168 | 6.0958 | 6.0768 | 5.9832 | 5.9221 | 5.8768 | 6.2368 | 6.2147 | 6.1926 | 6.1695 | 6.1484 | 6.1253 | 6.1021 | 6.08 | 6.0589 | 5.9589 | 5.8905 | 5.84 | 6.2432 | 6.2232 | 6.2032 | 6.1811 | 6.1611 | 6.14 | 6.1189 | 6.0979 | 6.0779 | 5.9853 | 5.9232 | 5.8779
| CARRADALE 1 | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0 | 0.33921 | 0.33184 | 0.32447 | 0.31605 | 0.22026 | 0.10026 | -0.022895 | -0.12816 | -0.23868 | -0.93763 | -1.6913 | -2.0461 | 0.32447 | 0.31816 | 0.31079 | 0.30132 | 0.22658 | 0.12974 | 0.029737 | -0.054474 | -0.14395 | -0.74816 | -1.405 | -1.7534 | 0.32553 | 0.31711 | 0.30658 | 0.29605 | 0.19605 | 0.075 | -0.049211 | -0.15447 | -0.265 | -0.98289 | -1.7629 | -2.1534
|  | CLAONAIG | EE |  |  |  |  | 0.34026 | 0.33184 | 0.32447 | 0.31605 | 0.22026 | 0.10026 | -0.022895 | -0.12816 | -0.23868 | -0.93763 | -1.6913 | -2.0461 | 0.32553 | 0.32026 | 0.31079 | 0.30132 | 0.22658 | 0.12974 | 0.029737 | -0.054474 | -0.14395 | -0.74816 | -1.405 | -1.7534 | 0.32763 | 0.31711 | 0.30763 | 0.29605 | 0.19605 | 0.075 | -0.049211 | -0.15447 | -0.265 | -0.98289 | -1.7629 | -2.1534
|  | CLAONAIG | HT |  |  |  |  | 0.33921 | 0.33289 | 0.32658 | 0.31921 | 0.23816 | 0.15711 | 0.073947 | -0.029211 | -0.14921 | -0.67026 | -1.1092 | -1.3566 | 0.32447 | 0.31816 | 0.31079 | 0.30237 | 0.23921 | 0.17184 | 0.10447 | 0.022368 | -0.082895 | -0.55342 | -0.97553 | -1.225 | 0.32553 | 0.31711 | 0.30658 | 0.29921 | 0.215 | 0.13079 | 0.047632 | -0.054474 | -0.17974 | -0.725 | -1.2039 | -1.4776
|  | CLAONAIG | HE |  |  |  |  | 0.34237 | 0.34026 | 0.33711 | 0.335 | 0.23395 | 0.13816 | 0.042368 | -0.054474 | -0.16184 | -0.65132 | -1.1566 | -1.7018 | 0.32763 | 0.32658 | 0.32342 | 0.32237 | 0.23816 | 0.15816 | 0.078158 | -0.003947 | -0.096579 | -0.51868 | -0.97342 | -1.4639 | 0.32553 | 0.31711 | 0.30658 | 0.29921 | 0.215 | 0.13079 | 0.047632 | -0.054474 | -0.17974 | -0.725 | -1.2039 | -1.4776
|  | CLAONAIG | CF |  |  |  |  | 0.34342 | 0.34132 | 0.34132 | 0.33921 | 0.30447 | 0.27395 | 0.23395 | 0.19289 | 0.15605 | -0.057632 | -0.36605 | -0.64395 | 0.32868 | 0.32763 | 0.32658 | 0.32553 | 0.29921 | 0.27289 | 0.23816 | 0.20132 | 0.16658 | -0.025 | -0.3029 | -0.565 | 0.33079 | 0.32868 | 0.32868 | 0.32658 | 0.28658 | 0.25184 | 0.21079 | 0.16763 | 0.12868 | -0.095526 | -0.42079 | -0.71974
| CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | YES | 0 | 24.8611 | 24.6832 | 24.5042 | 24.3158 | 24.1021 | 23.8937 | 23.6884 | 23.4863 | 23.2695 | 22.4916 | 21.4432 | 20.3832 | 23.8453 | 23.6611 | 23.4758 | 23.2789 | 23.0611 | 22.8463 | 22.6326 | 22.4084 | 22.0337 | 20.6337 | 19.3821 | 18.1758 | 23.9337 | 23.7558 | 23.5768 | 23.3884 | 23.1663 | 22.9474 | 22.7305 | 22.5168 | 22.2684 | 20.86 | 19.6032 | 18.3979
|  | CLAYHILLS | EE |  |  |  |  | 24.9874 | 24.8537 | 24.7126 | 24.5642 | 24.4 | 24.2379 | 24.0768 | 23.9232 | 23.7737 | 23.1 | 22.5926 | 21.9074 | 23.9768 | 23.8389 | 23.6926 | 23.5379 | 23.3737 | 23.2126 | 23.0495 | 22.8947 | 22.7411 | 21.7105 | 20.7526 | 19.9084 | 24.06 | 23.9263 | 23.7863 | 23.6368 | 23.4726 | 23.3116 | 23.1442 | 22.9832 | 22.8242 | 21.9263 | 20.9526 | 20.1053
|  | CLAYHILLS | HT |  |  |  |  | 24.8611 | 24.6832 | 24.5042 | 24.3158 | 24.1021 | 23.8937 | 23.6884 | 23.4863 | 23.2695 | 22.4916 | 21.4432 | 20.3832 | 23.8453 | 23.6611 | 23.4758 | 23.2789 | 23.0611 | 22.8463 | 22.6326 | 22.4084 | 22.0337 | 20.6337 | 19.3821 | 18.1758 | 23.9337 | 23.7558 | 23.5768 | 23.3884 | 23.1663 | 22.9474 | 22.7305 | 22.5168 | 22.2684 | 20.86 | 19.6032 | 18.3979
|  | CLAYHILLS | HE |  |  |  |  | 25.0705 | 24.9589 | 24.8368 | 24.7063 | 24.56 | 24.4263 | 24.2947 | 24.1684 | 24.0547 | 23.6453 | 23.4074 | 23.2411 | 24.0674 | 23.9526 | 23.8274 | 23.6947 | 23.5505 | 23.4179 | 23.2853 | 23.1589 | 23.0432 | 22.6295 | 22.38 | 22.0611 | 23.9337 | 23.7558 | 23.5768 | 23.3884 | 23.1663 | 22.9474 | 22.7305 | 22.5168 | 22.2684 | 20.86 | 19.6032 | 18.3979
|  | CLAYHILLS | CF |  |  |  |  | 25.1232 | 25.0453 | 24.9653 | 24.8832 | 24.7947 | 24.7074 | 24.6189 | 24.5316 | 24.4463 | 24.0716 | 23.8674 | 23.7589 | 24.1211 | 24.0411 | 23.9579 | 23.8737 | 23.7842 | 23.6958 | 23.6074 | 23.5189 | 23.4295 | 23.0379 | 22.8295 | 22.6926 | 24.1958 | 24.1179 | 24.0379 | 23.9558 | 23.8674 | 23.7811 | 23.6926 | 23.6053 | 23.52 | 23.1326 | 22.9126 | 22.7926
| DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | YES | 0 | 1.2116 | 1.1263 | 1.0326 | 0.93579 | 0.79053 | 0.64421 | 0.49474 | 0.35368 | -1.9842 | -2.8116 | -3.7074 | -4.4305 | 1.1011 | 1.0158 | 0.92105 | 0.82316 | 0.68737 | 0.55368 | 0.41789 | 0.28632 | -1.56 | -2.2916 | -3.0284 | -3.6516 | 1.0821 | 0.99579 | 0.89684 | 0.79263 | 0.64105 | 0.48737 | 0.33263 | 0.18421 | -2.2221 | -3.1158 | -4.1063 | -4.9284
|  | COLDBACKIE | EE |  |  |  |  | 1.2116 | 1.1263 | 1.0326 | 0.93579 | 0.79053 | 0.64421 | 0.49474 | 0.35368 | -1.9842 | -2.8116 | -3.7074 | -4.4305 | 1.1011 | 1.0158 | 0.92105 | 0.82316 | 0.68737 | 0.55368 | 0.41789 | 0.28632 | -1.56 | -2.2916 | -3.0284 | -3.6516 | 1.0821 | 0.99579 | 0.89684 | 0.79263 | 0.64105 | 0.48737 | 0.33263 | 0.18421 | -2.2221 | -3.1158 | -4.1063 | -4.9284
|  | COLDBACKIE | HT |  |  |  |  | 1.2347 | 1.1895 | 1.1432 | 1.0989 | 1.0137 | 0.92947 | 0.84737 | 0.75474 | -1.6242 | -2.2505 | -2.9284 | -3.4284 | 1.1032 | 1.0642 | 1.0263 | 0.98632 | 0.91684 | 0.84842 | 0.77895 | 0.69684 | -1.1874 | -1.7905 | -2.4853 | -2.9779 | 1.1063 | 1.0558 | 1.0084 | 0.95895 | 0.87053 | 0.78211 | 0.69368 | 0.59579 | -1.7968 | -2.4874 | -3.2758 | -3.8505
|  | COLDBACKIE | HE |  |  |  |  | 1.2726 | 1.2442 | 1.2137 | 1.1821 | 1.0968 | 1.0168 | 0.92526 | 0.83263 | -0.42211 | -0.93895 | -1.5337 | -2.1884 | 1.1495 | 1.1274 | 1.1032 | 1.0747 | 0.99789 | 0.92737 | 0.84947 | 0.77263 | -0.22526 | -0.69158 | -1.2568 | -1.8674 | 1.1063 | 1.0558 | 1.0084 | 0.95895 | 0.87053 | 0.78211 | 0.69368 | 0.59579 | -1.7968 | -2.4874 | -3.2758 | -3.8505
|  | COLDBACKIE | CF |  |  |  |  | 1.2958 | 1.2842 | 1.2737 | 1.2632 | 1.2305 | 1.2021 | 1.1716 | 1.1295 | 1.0758 | 0.83158 | 0.48632 | 0.11474 | 1.1663 | 1.1589 | 1.1495 | 1.14 | 1.1116 | 1.0874 | 1.0632 | 1.0179 | 0.96211 | 0.72211 | 0.37684 | -0.014737 | 1.1632 | 1.1537 | 1.1453 | 1.1368 | 1.1063 | 1.0747 | 1.0432 | 0.99263 | 0.93474 | 0.66526 | 0.28 | -0.14316
| DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0 | 0.52421 | 0.51789 | 0.51053 | 0.50316 | 0.49158 | 0.48211 | 0.47263 | 0.46211 | 0.45368 | 0.41053 | 0.37684 | 0.34316 | 0.50737 | 0.50421 | 0.49579 | 0.48526 | 0.47474 | 0.46526 | 0.45474 | 0.44526 | 0.43474 | 0.39158 | 0.35579 | 0.32211 | 0.51579 | 0.50737 | 0.49684 | 0.48632 | 0.47368 | 0.46316 | 0.45368 | 0.44211 | 0.43158 | 0.38632 | 0.34947 | 0.31474
|  | COLINTRAIVE | EE |  |  |  |  | 0.52526 | 0.51789 | 0.51053 | 0.50316 | 0.49158 | 0.48211 | 0.47263 | 0.46211 | 0.45368 | 0.41053 | 0.37684 | 0.34316 | 0.51053 | 0.50526 | 0.49579 | 0.48526 | 0.47474 | 0.46526 | 0.45474 | 0.44526 | 0.43474 | 0.39158 | 0.35579 | 0.32211 | 0.51579 | 0.50737 | 0.49684 | 0.48632 | 0.47368 | 0.46316 | 0.45368 | 0.44211 | 0.43158 | 0.38632 | 0.34947 | 0.31474
|  | COLINTRAIVE | HT |  |  |  |  | 0.52421 | 0.52 | 0.51474 | 0.50947 | 0.50105 | 0.49368 | 0.48737 | 0.47895 | 0.47263 | 0.44316 | 0.41789 | 0.39474 | 0.50737 | 0.50421 | 0.49895 | 0.49053 | 0.48316 | 0.47684 | 0.46947 | 0.46211 | 0.45579 | 0.42737 | 0.40316 | 0.37895 | 0.51579 | 0.51158 | 0.50211 | 0.49263 | 0.48421 | 0.47579 | 0.46947 | 0.46 | 0.45368 | 0.42211 | 0.39474 | 0.36842
|  | COLINTRAIVE | HE |  |  |  |  | 0.53053 | 0.52737 | 0.52421 | 0.52 | 0.51684 | 0.51368 | 0.51053 | 0.50737 | 0.50316 | 0.48842 | 0.47474 | 0.46105 | 0.51474 | 0.51263 | 0.50947 | 0.50632 | 0.50211 | 0.5 | 0.49684 | 0.49263 | 0.48842 | 0.47053 | 0.45684 | 0.44526 | 0.51579 | 0.51158 | 0.50211 | 0.49263 | 0.48421 | 0.47579 | 0.46947 | 0.46 | 0.45368 | 0.42211 | 0.39474 | 0.36842
|  | COLINTRAIVE | CF |  |  |  |  | 0.53263 | 0.53263 | 0.53053 | 0.52842 | 0.52737 | 0.52526 | 0.52421 | 0.52316 | 0.52211 | 0.51684 | 0.51368 | 0.51053 | 0.51684 | 0.51684 | 0.51579 | 0.51263 | 0.51158 | 0.51053 | 0.50947 | 0.50737 | 0.50632 | 0.50105 | 0.49684 | 0.49263 | 0.52421 | 0.52421 | 0.52316 | 0.52 | 0.51895 | 0.51789 | 0.51579 | 0.51474 | 0.51368 | 0.50632 | 0.49789 | 0.49263
| STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 0 | 2.2474 | 5.9579 | 5.8695 | 5.7832 | 5.6874 | 5.5968 | 5.5074 | 5.42 | 5.3368 | 4.2684 | 4.0242 | 3.8168 | 2.22 | 5.9232 | 5.8284 | 5.7358 | 5.6358 | 5.5411 | 5.4474 | 5.3579 | 5.2705 | 4.3526 | 4.0884 | 3.86 | 2.2179 | 5.9221 | 5.8263 | 5.7337 | 5.6326 | 5.5368 | 5.4421 | 5.3495 | 5.2621 | 4.1674 | 3.9 | 3.6695
|  | COLL | EE |  |  |  |  | 2.3053 | 6.0337 | 5.9621 | 5.8884 | 5.8116 | 5.7337 | 5.6568 | 5.5884 | 5.5189 | 4.5063 | 4.3221 | 4.1705 | 2.2832 | 6.0063 | 5.9295 | 5.8526 | 5.7716 | 5.6916 | 5.6137 | 5.5432 | 5.4726 | 4.6084 | 4.4126 | 4.2463 | 2.2821 | 6.0053 | 5.9284 | 5.8495 | 5.7684 | 5.6853 | 5.6053 | 5.5326 | 5.46 | 4.4263 | 4.2274 | 4.0568
|  | COLL | HT |  |  |  |  | 2.2474 | 5.9579 | 5.8695 | 5.7832 | 5.6874 | 5.5968 | 5.5074 | 5.42 | 5.3368 | 4.2684 | 4.0242 | 3.8168 | 2.22 | 5.9232 | 5.8284 | 5.7358 | 5.6358 | 5.5411 | 5.4474 | 5.3579 | 5.2705 | 4.3526 | 4.0884 | 3.86 | 2.2179 | 5.9221 | 5.8263 | 5.7337 | 5.6326 | 5.5368 | 5.4421 | 5.3495 | 5.2621 | 4.1674 | 3.9 | 3.6695
|  | COLL | HE |  |  |  |  | 2.3874 | 6.1432 | 6.0958 | 6.0474 | 5.9905 | 5.9358 | 5.8832 | 5.8358 | 5.7895 | 5.2842 | 5.1895 | 5.1189 | 2.3737 | 6.1263 | 6.0758 | 6.0242 | 5.9674 | 5.9116 | 5.8589 | 5.8095 | 5.7632 | 5.3316 | 5.2295 | 5.1537 | 2.2179 | 5.9221 | 5.8263 | 5.7337 | 5.6326 | 5.5368 | 5.4421 | 5.3495 | 5.2621 | 4.1674 | 3.9 | 3.6695
|  | COLL | CF |  |  |  |  | 2.4295 | 6.2032 | 6.1768 | 6.1495 | 6.1211 | 6.0895 | 6.0589 | 6.0274 | 5.9989 | 5.8611 | 5.7568 | 5.6821 | 2.4211 | 6.1916 | 6.1621 | 6.1316 | 6.1011 | 6.0684 | 6.0358 | 6.0032 | 5.9726 | 5.8284 | 5.7211 | 5.6421 | 2.4189 | 6.1895 | 6.16 | 6.1295 | 6.0989 | 6.0653 | 6.0326 | 5.9989 | 5.9684 | 5.8221 | 5.7095 | 5.6274
| CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | YES | 0 | 26.1184 | 26.0816 | 26.0437 | 26.0026 | 25.9563 | 25.91 | 25.8647 | 25.8205 | 25.7774 | 25.6247 | 25.5163 | 25.4384 | 24.1568 | 24.0084 | 23.86 | 23.7126 | 23.5642 | 23.4168 | 23.2705 | 23.1295 | 22.9884 | 22.3484 | 21.7589 | 21.2021 | 25.3518 | 25.315 | 25.2771 | 25.2361 | 25.1908 | 25.1445 | 25.0992 | 25.055 | 25.0118 | 24.8613 | 24.7529 | 24.6761
|  | COMMERCE STREET | EE |  |  |  |  | 26.1447 | 26.1153 | 26.0847 | 26.0521 | 26.0153 | 25.9774 | 25.9416 | 25.9058 | 25.8721 | 25.7226 | 25.6237 | 25.5658 | 24.2674 | 24.1516 | 24.0368 | 23.9232 | 23.8074 | 23.6916 | 23.5789 | 23.4684 | 23.3611 | 22.8421 | 22.38 | 21.9611 | 25.3782 | 25.3487 | 25.3182 | 25.2855 | 25.2487 | 25.2118 | 25.1761 | 25.1413 | 25.1066 | 24.9603 | 24.8634 | 24.8055
|  | COMMERCE STREET | HT |  |  |  |  | 26.1184 | 26.0816 | 26.0437 | 26.0026 | 25.9563 | 25.91 | 25.8647 | 25.8205 | 25.7774 | 25.6247 | 25.5163 | 25.4384 | 24.1568 | 24.0084 | 23.86 | 23.7126 | 23.5642 | 23.4168 | 23.2705 | 23.1295 | 22.9884 | 22.3484 | 21.7589 | 21.2021 | 25.3518 | 25.315 | 25.2771 | 25.2361 | 25.1908 | 25.1445 | 25.0992 | 25.055 | 25.0118 | 24.8613 | 24.7529 | 24.6761
|  | COMMERCE STREET | HE |  |  |  |  | 26.1626 | 26.1395 | 26.1132 | 26.0858 | 26.0521 | 26.0216 | 25.9932 | 25.9637 | 25.9374 | 25.8416 | 25.7837 | 25.7426 | 24.3211 | 24.2979 | 24.2484 | 24.1737 | 24.0926 | 24.0158 | 23.9442 | 23.8716 | 23.8042 | 23.5011 | 23.24 | 23.0021 | 25.3518 | 25.315 | 25.2771 | 25.2361 | 25.1908 | 25.1445 | 25.0992 | 25.055 | 25.0118 | 24.8613 | 24.7529 | 24.6761
|  | COMMERCE STREET | CF |  |  |  |  | 26.1763 | 26.1605 | 26.1447 | 26.1279 | 26.1089 | 26.0911 | 26.0721 | 26.0532 | 26.0353 | 25.9563 | 25.9089 | 25.8837 | 24.3347 | 24.3189 | 24.3032 | 24.2863 | 24.2526 | 24.2 | 24.1463 | 24.0916 | 24.0389 | 23.7916 | 23.5842 | 23.4042 | 25.4097 | 25.3939 | 25.3782 | 25.3613 | 25.3434 | 25.3245 | 25.3066 | 25.2866 | 25.2697 | 25.1908 | 25.1445 | 25.1203
| ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | YES | 0 | 0.054211 | 0.052105 | 0.051053 | 0.051053 | 0.039474 | 0.026842 | 0.012105 | -0.000526 | -0.021579 | -0.13632 | -0.28158 | -0.40263 | 0.053158 | 0.051053 | 0.051053 | 0.05 | 0.040526 | 0.027895 | 0.013158 | 0.0015789 | -0.020526 | -0.13737 | -0.29842 | -0.4121 | 0.053158 | 0.051053 | 0.05 | 0.048947 | 0.040526 | 0.027895 | 0.016316 | 0.0057895 | -0.020526 | -0.15421 | -0.32053 | -0.45105
|  | COMRIE | EE |  |  |  |  | 0.054211 | 0.053158 | 0.051053 | 0.051053 | 0.042632 | 0.03 | 0.018421 | 0.0078947 | -0.008947 | -0.13632 | -0.28158 | -0.40263 | 0.053158 | 0.052105 | 0.051053 | 0.051053 | 0.043684 | 0.033158 | 0.023684 | 0.015263 | -0.000526 | -0.12895 | -0.27737 | -0.41 | 0.053158 | 0.052105 | 0.05 | 0.05 | 0.041579 | 0.027895 | 0.016316 | 0.0057895 | -0.012105 | -0.1521 | -0.31316 | -0.45105
|  | COMRIE | HT |  |  |  |  | 0.054211 | 0.052105 | 0.052105 | 0.051053 | 0.042632 | 0.035263 | 0.023684 | 0.011053 | -0.014211 | -0.13421 | -0.27737 | -0.37842 | 0.053158 | 0.051053 | 0.051053 | 0.05 | 0.042632 | 0.037368 | 0.027895 | 0.015263 | -0.012105 | -0.13737 | -0.29842 | -0.4121 | 0.053158 | 0.051053 | 0.051053 | 0.048947 | 0.040526 | 0.033158 | 0.021579 | 0.0078947 | -0.020526 | -0.15421 | -0.32053 | -0.43632
|  | COMRIE | HE |  |  |  |  | 0.055263 | 0.055263 | 0.055263 | 0.054211 | 0.039474 | 0.026842 | 0.012105 | -0.000526 | -0.021579 | -0.11 | -0.22474 | -0.35211 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.040526 | 0.027895 | 0.013158 | 0.0015789 | -0.020526 | -0.1079 | -0.22895 | -0.36263 | 0.053158 | 0.051053 | 0.051053 | 0.048947 | 0.040526 | 0.033158 | 0.021579 | 0.0078947 | -0.020526 | -0.15421 | -0.32053 | -0.43632
|  | COMRIE | CF |  |  |  |  | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.051053 | 0.046842 | 0.038421 | 0.03 | 0.018421 | -0.028947 | -0.10158 | -0.18579 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.051053 | 0.047895 | 0.038421 | 0.028947 | 0.016316 | -0.033158 | -0.11105 | -0.20368 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.051053 | 0.045789 | 0.036316 | 0.026842 | 0.01421 | -0.039474 | -0.12158 | -0.21737
| TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | 0 | 1.1295 | 1.0768 | 1.0253 | 0.97368 | 0.92105 | 0.87053 | 0.82316 | 0.77684 | 0.73263 | 0.55895 | 0.41895 | 0.3 | 0.92632 | 0.87053 | 0.81474 | 0.76211 | 0.70632 | 0.65474 | 0.60526 | 0.55579 | 0.50947 | 0.32632 | 0.17684 | 0.045263 | 0.95474 | 0.89895 | 0.84316 | 0.78842 | 0.73263 | 0.68 | 0.62947 | 0.58 | 0.53368 | 0.34632 | 0.19474 | 0.064211
|  | CONNEL | EE |  |  |  |  | 1.1653 | 1.1221 | 1.08 | 1.0368 | 0.99474 | 0.95579 | 0.91579 | 0.87895 | 0.84421 | 0.69263 | 0.58526 | 0.49684 | 0.96421 | 0.92105 | 0.87579 | 0.83263 | 0.78842 | 0.74842 | 0.70737 | 0.66947 | 0.63368 | 0.47789 | 0.36526 | 0.27053 | 0.99263 | 0.94842 | 0.90211 | 0.85684 | 0.81158 | 0.76947 | 0.72947 | 0.68947 | 0.65263 | 0.49158 | 0.37368 | 0.27579
|  | CONNEL | HT |  |  |  |  | 1.1295 | 1.0768 | 1.0253 | 0.97368 | 0.92105 | 0.87053 | 0.82316 | 0.77684 | 0.73263 | 0.55895 | 0.41895 | 0.3 | 0.92632 | 0.87053 | 0.81474 | 0.76211 | 0.70632 | 0.65474 | 0.60526 | 0.55579 | 0.50947 | 0.32632 | 0.17684 | 0.045263 | 0.95474 | 0.89895 | 0.84316 | 0.78842 | 0.73263 | 0.68 | 0.62947 | 0.58 | 0.53368 | 0.34632 | 0.19474 | 0.064211
|  | CONNEL | HE |  |  |  |  | 1.2147 | 1.1884 | 1.1621 | 1.1337 | 1.1053 | 1.0737 | 1.0474 | 1.0242 | 1 | 0.91684 | 0.86316 | 0.82316 | 1.0168 | 0.98842 | 0.96105 | 0.93263 | 0.90316 | 0.87053 | 0.84316 | 0.81789 | 0.79474 | 0.70842 | 0.65158 | 0.60947 | 0.95474 | 0.89895 | 0.84316 | 0.78842 | 0.73263 | 0.68 | 0.62947 | 0.58 | 0.53368 | 0.34632 | 0.19474 | 0.064211
|  | CONNEL | CF |  |  |  |  | 1.2411 | 1.2253 | 1.2095 | 1.1926 | 1.1768 | 1.1611 | 1.1453 | 1.1295 | 1.1126 | 1.0442 | 0.99579 | 0.96105 | 1.0442 | 1.0284 | 1.0116 | 0.99474 | 0.97789 | 0.96105 | 0.94421 | 0.92737 | 0.90842 | 0.83579 | 0.78421 | 0.74737 | 1.0747 | 1.0579 | 1.04 | 1.0232 | 1.0063 | 0.98947 | 0.97263 | 0.95579 | 0.93789 | 0.86421 | 0.81158 | 0.77368
| BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | YES | 0 | 6.2888 | 6.0867 | 5.8814 | 14.1637 | 13.5647 | 12.9289 | 12.2847 | 11.7437 | 11.1953 | 9.2668 | 7.2984 | 5.2647 | 5.4689 | 5.2374 | 5.0047 | 12.82 | 12.1579 | 11.5032 | 10.84 | 10.3147 | 9.7811 | 8.1389 | 6.4737 | 4.3316 | 5.722 | 5.4936 | 5.2641 | 13.3013 | 12.6171 | 11.9403 | 11.255 | 10.6855 | 10.1087 | 8.1297 | 6.1013 | 3.8224
|  | CONON BRIDGE | EE |  |  |  |  | 6.4109 | 6.2372 | 6.0614 | 14.3679 | 13.9721 | 13.5332 | 12.8826 | 12.2363 | 11.59 | 9.2668 | 7.2984 | 5.2647 | 5.6153 | 5.4216 | 5.2247 | 13.0726 | 12.7084 | 12.3116 | 11.6284 | 10.9821 | 10.3326 | 8.2189 | 6.5326 | 4.3316 | 5.862 | 5.6662 | 5.4684 | 13.535 | 13.1192 | 12.6561 | 11.9224 | 11.2371 | 10.5476 | 8.1297 | 6.1013 | 3.8224
|  | CONON BRIDGE | HT |  |  |  |  | 6.2888 | 6.0867 | 5.8814 | 14.1637 | 13.5647 | 12.9289 | 12.2847 | 11.7437 | 11.1953 | 9.4363 | 7.8026 | 6.1079 | 5.4689 | 5.2374 | 5.0047 | 12.82 | 12.1579 | 11.5032 | 10.84 | 10.3147 | 9.7811 | 8.1389 | 6.4737 | 4.5821 | 5.722 | 5.4936 | 5.2641 | 13.3013 | 12.6171 | 11.9403 | 11.255 | 10.6855 | 10.1087 | 8.2676 | 6.4782 | 4.5192
|  | CONON BRIDGE | HE |  |  |  |  | 6.5667 | 6.4741 | 6.3625 | 14.7342 | 14.3616 | 14.0395 | 13.5753 | 13.1174 | 12.6532 | 10.8321 | 9.1626 | 6.87 | 5.8016 | 5.6911 | 5.5647 | 13.48 | 13.1516 | 12.8621 | 12.3726 | 11.8905 | 11.4221 | 9.7021 | 8.1147 | 5.8063 | 5.722 | 5.4936 | 5.2641 | 13.3013 | 12.6171 | 11.9403 | 11.255 | 10.6855 | 10.1087 | 8.2676 | 6.4782 | 4.5192
|  | CONON BRIDGE | CF |  |  |  |  | 6.6257 | 6.5909 | 6.552 | 14.9795 | 14.8226 | 14.6784 | 14.5332 | 14.3216 | 14.1279 | 13.0847 | 12.0532 | 10.6384 | 5.8605 | 5.8279 | 5.7858 | 13.76 | 13.6147 | 13.4779 | 13.34 | 13.1021 | 12.8747 | 11.7632 | 10.7758 | 9.2621 | 6.1031 | 6.0684 | 6.0263 | 14.2213 | 14.0561 | 13.9013 | 13.7445 | 13.5003 | 13.2697 | 12.1055 | 11.0161 | 9.4645
| BEAULY | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | YES | 0.25 | 0.24263 | 0.23737 | 0.23211 | 0.044737 | 0.018421 | -0.013158 | -0.045789 | -0.075263 | -0.10263 | -0.29526 | -0.56474 | -0.75211 | 0.25 | 0.23947 | 0.23105 | 0.047895 | 0.025789 | -0.000526 | -0.026842 | -0.052105 | -0.076316 | -0.23842 | -0.44684 | -0.64368 | 0.24579 | 0.23632 | 0.22684 | 0.035263 | 0.0078947 | -0.024737 | -0.057368 | -0.087895 | -0.11737 | -0.35632 | -0.64684 | -0.85737
|  | CONON FALLS | EE |  |  |  |  | 0.24368 | 0.23737 | 0.23211 | 0.044737 | 0.018421 | -0.013158 | -0.045789 | -0.075263 | -0.10263 | -0.29526 | -0.56474 | -0.75211 | 0.25316 | 0.24579 | 0.23737 | 0.047895 | 0.025789 | -0.000526 | -0.026842 | -0.052105 | -0.076316 | -0.23842 | -0.44684 | -0.64368 | 0.24895 | 0.24053 | 0.23105 | 0.035263 | 0.0078947 | -0.024737 | -0.057368 | -0.087895 | -0.11737 | -0.35632 | -0.64684 | -0.85737
|  | CONON FALLS | HT |  |  |  |  | 0.24263 | 0.23737 | 0.23211 | 0.22474 | 0.20368 | 0.18158 | 0.16158 | 0.13526 | 0.10158 | -0.11316 | -0.33737 | -0.48684 | 0.25 | 0.23947 | 0.23105 | 0.22263 | 0.20158 | 0.17947 | 0.15842 | 0.13421 | 0.10474 | -0.10684 | -0.34579 | -0.50895 | 0.24579 | 0.23632 | 0.22684 | 0.21842 | 0.19211 | 0.16579 | 0.14053 | 0.11105 | 0.076316 | -0.15842 | -0.41105 | -0.58158
|  | CONON FALLS | HE |  |  |  |  | 0.24895 | 0.24684 | 0.24263 | 0.23947 | 0.21421 | 0.19421 | 0.17211 | 0.14895 | 0.10895 | -0.061579 | -0.25947 | -0.47421 | 0.26158 | 0.25737 | 0.25211 | 0.24895 | 0.22579 | 0.20263 | 0.17421 | 0.14895 | 0.11105 | -0.048947 | -0.24368 | -0.45632 | 0.24579 | 0.23632 | 0.22684 | 0.21842 | 0.19211 | 0.16579 | 0.14053 | 0.11105 | 0.076316 | -0.15842 | -0.41105 | -0.58158
|  | CONON FALLS | CF |  |  |  |  | 0.25211 | 0.25105 | 0.24789 | 0.24684 | 0.23737 | 0.22895 | 0.22053 | 0.21316 | 0.20579 | 0.12263 | -0.000526 | -0.13211 | 0.26579 | 0.26368 | 0.26053 | 0.25842 | 0.25 | 0.24158 | 0.23211 | 0.21526 | 0.19632 | 0.11211 | -0.012105 | -0.14895 | 0.26263 | 0.26053 | 0.25632 | 0.25421 | 0.24368 | 0.23316 | 0.22158 | 0.20474 | 0.18474 | 0.092105 | -0.043684 | -0.1921
| DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | YES | 0 | 33.2158 | 33.0579 | 32.8937 | 32.7326 | 32.5337 | 32.3368 | 32.1768 | 31.9821 | 31.6579 | 30.2021 | 29.0895 | 28.1526 | 29.94 | 29.7568 | 29.56 | 29.3821 | 29.1495 | 28.9158 | 28.7326 | 28.5 | 28.2705 | 26.9579 | 25.7284 | 24.68 | 31.4847 | 31.3405 | 31.0689 | 30.8247 | 30.43 | 30.0226 | 29.6816 | 29.2574 | 28.8374 | 27.4647 | 26.4174 | 25.5405
|  | CONSTABLE STREET | EE |  |  |  |  | 33.3379 | 33.2211 | 33.0968 | 32.9705 | 32.8316 | 32.6937 | 32.5379 | 32.3884 | 32.2779 | 31.1884 | 30.2947 | 29.5926 | 30.0747 | 29.9368 | 29.7821 | 29.6453 | 29.4989 | 29.3547 | 29.1632 | 28.9789 | 28.8495 | 28.0474 | 27.0737 | 26.2884 | 31.5995 | 31.4953 | 31.3732 | 31.1837 | 30.9816 | 30.7795 | 30.4089 | 30.05 | 29.7689 | 28.3984 | 27.5521 | 26.8953
|  | CONSTABLE STREET | HT |  |  |  |  | 33.2158 | 33.0579 | 32.8937 | 32.7326 | 32.5337 | 32.3368 | 32.1768 | 31.9821 | 31.6579 | 30.2021 | 29.0895 | 28.1526 | 29.94 | 29.7568 | 29.56 | 29.3821 | 29.1495 | 28.9158 | 28.7326 | 28.5 | 28.2705 | 26.9579 | 25.7284 | 24.68 | 31.4847 | 31.3405 | 31.0689 | 30.8247 | 30.43 | 30.0226 | 29.6816 | 29.2574 | 28.8374 | 27.4647 | 26.4174 | 25.5405
|  | CONSTABLE STREET | HE |  |  |  |  | 33.4 | 33.2989 | 33.1853 | 33.0747 | 32.9484 | 32.8316 | 32.7063 | 32.5863 | 32.4389 | 32.0116 | 31.4179 | 31.0074 | 30.1526 | 30.0358 | 29.8989 | 29.7811 | 29.6516 | 29.5326 | 29.3874 | 29.2453 | 29.0526 | 28.5095 | 28.2232 | 27.8032 | 31.4847 | 31.3405 | 31.0689 | 30.8247 | 30.43 | 30.0226 | 29.6816 | 29.2574 | 28.8374 | 27.4647 | 26.4174 | 25.5405
|  | CONSTABLE STREET | CF |  |  |  |  | 33.4474 | 33.3758 | 33.3011 | 33.2295 | 33.1526 | 33.0758 | 32.9968 | 32.9147 | 32.8337 | 32.4674 | 32.26 | 32.1463 | 30.2126 | 30.1316 | 30.0442 | 29.9663 | 29.8853 | 29.8032 | 29.72 | 29.6263 | 29.5295 | 29.0853 | 28.8337 | 28.6937 | 31.6921 | 31.6268 | 31.5595 | 31.4911 | 31.4174 | 31.3437 | 31.27 | 31.1963 | 31.1216 | 30.3058 | 29.8079 | 29.5132
| ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | YES | 0 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.10211 | 0.1 | 0.094737 | 0.090526 | 0.081053 | 0.025263 | -0.057895 | -0.12 | 0.10316 | 0.10211 | 0.10105 | 0.1 | 0.098947 | 0.094737 | 0.090526 | 0.085263 | 0.074737 | 0.0084211 | -0.087368 | -0.16105 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.078947 | 0.0094737 | -0.087368 | -0.16105
|  | CONTULLICH | EE |  |  |  |  | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.10211 | 0.10211 | 0.098947 | 0.095789 | 0.041053 | -0.02 | -0.089474 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.1 | 0.098947 | 0.098947 | 0.096842 | 0.091579 | 0.029474 | -0.043158 | -0.12316 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.098947 | 0.098947 | 0.095789 | 0.092632 | 0.028421 | -0.043158 | -0.12421
|  | CONTULLICH | HT |  |  |  |  | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.10211 | 0.10105 | 0.1 | 0.095789 | 0.08421 | 0.025263 | -0.057895 | -0.12 | 0.10316 | 0.10211 | 0.10105 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.092632 | 0.078947 | 0.0084211 | -0.087368 | -0.16105 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.078947 | 0.0094737 | -0.087368 | -0.16105
|  | CONTULLICH | HE |  |  |  |  | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10421 | 0.1 | 0.094737 | 0.090526 | 0.081053 | 0.045263 | -0.010526 | -0.071579 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10105 | 0.094737 | 0.090526 | 0.085263 | 0.074737 | 0.032632 | -0.031579 | -0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.078947 | 0.0094737 | -0.087368 | -0.16105
|  | CONTULLICH | CF |  |  |  |  | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10526 | 0.10316 | 0.098947 | 0.092632 | 0.070526 | 0.034737 | -0.012632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10316 | 0.098947 | 0.093684 | 0.087368 | 0.061053 | 0.017895 | -0.035789 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10316 | 0.098947 | 0.094737 | 0.088421 | 0.061053 | 0.018947 | -0.035789
| FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | NO | 0 | 1.1179 | 1.0968 | 0.08 | 0.06 | -0.008421 | -0.084211 | -0.16316 | -0.23263 | -0.30105 | -0.78947 | -1.5242 | -2.0684 | 1.0347 | 1.0116 | 0.10211 | 0.078947 | 0.017895 | -0.050526 | -0.12 | -0.18316 | -0.24421 | -0.65579 | -1.2158 | -1.7326 | 1.0505 | 1.0221 | -0.057895 | -0.082105 | -0.15263 | -0.22947 | -0.30842 | -0.37895 | -0.44737 | -1.0095 | -1.8126 | -2.4411
|  | CORRAN | EE |  |  |  |  | 1.1295 | 1.1105 | 0.08 | 0.06 | -0.008421 | -0.084211 | -0.16316 | -0.23263 | -0.30105 | -0.78947 | -1.5242 | -2.0684 | 1.0463 | 1.0295 | 0.10211 | 0.078947 | 0.017895 | -0.050526 | -0.12 | -0.18316 | -0.24421 | -0.65579 | -1.2158 | -1.7326 | 1.0684 | 1.0442 | -0.057895 | -0.082105 | -0.15263 | -0.22947 | -0.30842 | -0.37895 | -0.44737 | -1.0095 | -1.8126 | -2.4411
|  | CORRAN | HT |  |  |  |  | 1.1179 | 1.0968 | 1.0758 | 1.0516 | 0.97474 | 0.9 | 0.82632 | 0.74316 | 0.66105 | 0.072632 | -0.59895 | -1.0537 | 1.0347 | 1.0116 | 0.97579 | 0.94105 | 0.87158 | 0.80421 | 0.73789 | 0.66316 | 0.59158 | 0.0031579 | -0.72421 | -1.2295 | 1.0505 | 1.0221 | 0.99263 | 0.96421 | 0.89789 | 0.83263 | 0.75789 | 0.67263 | 0.59053 | -0.058947 | -0.83158 | -1.3621
|  | CORRAN | HE |  |  |  |  | 1.1442 | 1.1337 | 1.1232 | 1.1105 | 1.0474 | 0.99368 | 0.93368 | 0.85158 | 0.74 | 0.27263 | -0.28632 | -0.88632 | 1.0621 | 1.0526 | 1.0411 | 1.0284 | 0.98421 | 0.92737 | 0.85368 | 0.77895 | 0.67053 | 0.22105 | -0.34316 | -0.95579 | 1.0505 | 1.0221 | 0.99263 | 0.96421 | 0.89789 | 0.83263 | 0.75789 | 0.67263 | 0.59053 | -0.058947 | -0.83158 | -1.3621
|  | CORRAN | CF |  |  |  |  | 1.1547 | 1.1484 | 1.1421 | 1.1368 | 1.1116 | 1.0905 | 1.0684 | 1.0484 | 1.0074 | 0.76421 | 0.40947 | 0.027368 | 1.0726 | 1.0674 | 1.06 | 1.0547 | 1.04 | 1.0263 | 1.0084 | 0.96947 | 0.91263 | 0.66737 | 0.30737 | -0.10105 | 1.1053 | 1.0979 | 1.0884 | 1.08 | 1.0537 | 1.0295 | 1.0042 | 0.97263 | 0.93474 | 0.67368 | 0.27684 | -0.16105
| KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 0 | 2.8537 | 2.7537 | 2.6463 | 2.54 | 2.1484 | 1.6758 | 1.1579 | 0.70842 | 0.24526 | -3.3568 | -7.4674 | -10.2779 | 2.8747 | 2.7695 | 2.6579 | 2.5474 | 2.2147 | 1.8632 | 1.4253 | 1.0421 | 0.65368 | -2.6863 | -6.5484 | -9.4884 | 2.8884 | 2.7779 | 2.6642 | 2.5484 | 2.1432 | 1.66 | 1.1253 | 0.65579 | 0.18 | -3.6684 | -8.0916 | -11.2147
|  | COSHIEVILLE | EE |  |  |  |  | 2.8853 | 2.8158 | 2.72 | 2.6221 | 2.1789 | 1.6758 | 1.1579 | 0.70842 | 0.24526 | -3.3568 | -7.4674 | -10.2779 | 2.9126 | 2.8495 | 2.7547 | 2.6611 | 2.2926 | 1.8632 | 1.4253 | 1.0421 | 0.65368 | -2.6863 | -6.5484 | -9.4884 | 2.9211 | 2.8484 | 2.7453 | 2.64 | 2.1811 | 1.66 | 1.1253 | 0.65579 | 0.18 | -3.6684 | -8.0916 | -11.2147
|  | COSHIEVILLE | HT |  |  |  |  | 2.8537 | 2.7537 | 2.6463 | 2.54 | 2.1484 | 1.7726 | 1.3926 | 0.94947 | 0.48211 | -2.7295 | -6.1147 | -8.34 | 2.8747 | 2.7695 | 2.6579 | 2.5474 | 2.2147 | 1.8937 | 1.5611 | 1.1779 | 0.77053 | -2.3737 | -5.9558 | -8.4011 | 2.8884 | 2.7779 | 2.6642 | 2.5484 | 2.1432 | 1.7526 | 1.3579 | 0.89684 | 0.41158 | -3.08 | -6.8716 | -9.4179
|  | COSHIEVILLE | HE |  |  |  |  | 2.9326 | 2.9053 | 2.8579 | 2.8095 | 2.3684 | 1.9337 | 1.4758 | 1.0337 | 0.43368 | -2.1495 | -5.1958 | -8.5042 | 2.9579 | 2.9326 | 2.8842 | 2.8347 | 2.4695 | 2.0832 | 1.6716 | 1.2789 | 0.71158 | -1.6968 | -4.6811 | -7.9442 | 2.8884 | 2.7779 | 2.6642 | 2.5484 | 2.1432 | 1.7526 | 1.3579 | 0.89684 | 0.41158 | -3.08 | -6.8716 | -9.4179
|  | COSHIEVILLE | CF |  |  |  |  | 2.9579 | 2.94 | 2.9168 | 2.8989 | 2.7337 | 2.5884 | 2.3768 | 2.1284 | 1.8632 | 0.58737 | -1.3158 | -3.3189 | 2.9789 | 2.9642 | 2.9463 | 2.9263 | 2.7926 | 2.6663 | 2.4705 | 2.2295 | 1.9526 | 0.70316 | -1.1842 | -3.28 | 2.9768 | 2.9653 | 2.9526 | 2.9358 | 2.7653 | 2.6126 | 2.3905 | 2.1211 | 1.8274 | 0.44526 | -1.6274 | -3.8747
| COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | YES | 0 | 16.0016 | 15.85 | 15.6953 | 15.4153 | 14.7753 | 14.0932 | 13.3732 | 12.7163 | 11.8542 | 7.4995 | 1.5089 | -3.1426 | 14.4 | 14.2326 | 14.0632 | 13.7211 | 13.0947 | 12.5179 | 11.9253 | 11.1926 | 10.3168 | 6.1674 | 0.0063158 | -4.6316 | 15.0445 | 14.8739 | 14.7013 | 14.3582 | 13.6487 | 12.9455 | 12.2066 | 11.4855 | 10.5108 | 5.9013 | -0.69132 | -5.9039
|  | COUPAR ANGUS | EE |  |  |  |  | 16.0953 | 15.9574 | 15.8237 | 15.6174 | 14.9416 | 14.0932 | 13.3732 | 12.7163 | 11.9721 | 7.4995 | 1.5089 | -3.1426 | 14.5105 | 14.3611 | 14.2147 | 13.9726 | 13.3263 | 12.5421 | 11.9305 | 11.3579 | 10.6768 | 6.4274 | 0.43368 | -4.6316 | 15.1539 | 14.9982 | 14.8466 | 14.5992 | 13.8497 | 12.9455 | 12.2066 | 11.5255 | 10.7361 | 5.9013 | -0.69132 | -5.9039
|  | COUPAR ANGUS | HT |  |  |  |  | 16.0016 | 15.85 | 15.6953 | 15.4153 | 14.7753 | 14.1563 | 13.5226 | 12.7458 | 11.8542 | 7.7637 | 2.0942 | -1.7826 | 14.4 | 14.2326 | 14.0632 | 13.7211 | 13.0947 | 12.5179 | 11.9253 | 11.1926 | 10.3168 | 6.1674 | 0.0063158 | -4.34 | 15.0445 | 14.8739 | 14.7013 | 14.3582 | 13.6487 | 12.9929 | 12.3171 | 11.4855 | 10.5108 | 5.9918 | -0.39132 | -4.8524
|  | COUPAR ANGUS | HE |  |  |  |  | 16.2047 | 16.1258 | 16.0458 | 15.8679 | 15.1668 | 14.4489 | 13.8279 | 13.1637 | 12.4353 | 9.0605 | 4.4016 | -0.68368 | 14.6389 | 14.5495 | 14.4589 | 14.2368 | 13.5558 | 12.8632 | 12.2947 | 11.6674 | 10.9589 | 7.6737 | 2.8758 | -2.3411 | 15.0445 | 14.8739 | 14.7013 | 14.3582 | 13.6487 | 12.9929 | 12.3171 | 11.4855 | 10.5108 | 5.9918 | -0.39132 | -4.8524
|  | COUPAR ANGUS | CF |  |  |  |  | 16.2921 | 16.2468 | 16.1974 | 16.1353 | 15.9005 | 15.6721 | 15.4268 | 15.1511 | 14.7321 | 12.8163 | 9.89 | 6.6079 | 14.7474 | 14.6947 | 14.6379 | 14.5632 | 14.3484 | 14.1295 | 13.8863 | 13.5905 | 13.1126 | 11.0926 | 8.0421 | 4.5084 | 15.3887 | 15.335 | 15.2771 | 15.2024 | 14.9476 | 14.6929 | 14.4139 | 14.0897 | 13.5982 | 11.4245 | 8.1655 | 4.4792
| CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | YES | 0.205 | 23.5045 | 23.3255 | 23.1455 | 22.9655 | 22.7603 | 22.5613 | 22.3003 | 21.995 | 21.6929 | 20.7287 | 19.9876 | 19.3592 | 22.3055 | 22.1234 | 21.9424 | 21.7582 | 21.5518 | 21.3539 | 21.0761 | 20.7403 | 20.4087 | 19.3539 | 18.5276 | 17.8108 | 22.3329 | 22.1508 | 21.9676 | 21.7845 | 21.5771 | 21.375 | 21.0961 | 20.7582 | 20.4234 | 19.3582 | 18.5255 | 17.8076
|  | CRAIGIEBUCKLER | EE |  |  |  |  | 23.6245 | 23.4887 | 23.3455 | 23.2003 | 23.0371 | 22.8792 | 22.7266 | 22.5855 | 22.4466 | 21.5329 | 20.915 | 20.4687 | 22.4287 | 22.2897 | 22.1445 | 21.9971 | 21.835 | 21.6792 | 21.5276 | 21.3876 | 21.2508 | 20.2603 | 19.5887 | 19.0845 | 22.4561 | 22.3171 | 22.1708 | 22.0234 | 21.8592 | 21.7003 | 21.5434 | 21.4013 | 21.2613 | 20.255 | 19.5645 | 19.0561
|  | CRAIGIEBUCKLER | HT |  |  |  |  | 23.5045 | 23.3255 | 23.1455 | 22.9655 | 22.7603 | 22.5613 | 22.3003 | 21.995 | 21.6929 | 20.7287 | 19.9876 | 19.3592 | 22.3055 | 22.1234 | 21.9424 | 21.7582 | 21.5518 | 21.3539 | 21.0761 | 20.7403 | 20.4087 | 19.3539 | 18.5276 | 17.8108 | 22.3329 | 22.1508 | 21.9676 | 21.7845 | 21.5771 | 21.375 | 21.0961 | 20.7582 | 20.4234 | 19.3582 | 18.5255 | 17.8076
|  | CRAIGIEBUCKLER | HE |  |  |  |  | 23.7592 | 23.675 | 23.5834 | 23.4803 | 23.3561 | 23.2424 | 23.1297 | 23.0255 | 22.9266 | 22.5792 | 22.3592 | 22.1055 | 22.5666 | 22.4824 | 22.3876 | 22.2824 | 22.1603 | 22.0487 | 21.9382 | 21.835 | 21.7382 | 21.3971 | 21.1813 | 20.9087 | 22.3329 | 22.1508 | 21.9676 | 21.7845 | 21.5771 | 21.375 | 21.0961 | 20.7582 | 20.4234 | 19.3582 | 18.5255 | 17.8076
|  | CRAIGIEBUCKLER | CF |  |  |  |  | 23.8392 | 23.7939 | 23.7476 | 23.6992 | 23.6466 | 23.5887 | 23.5318 | 23.475 | 23.4203 | 23.1687 | 23.0139 | 22.9234 | 22.6466 | 22.6013 | 22.555 | 22.5066 | 22.4539 | 22.3939 | 22.3371 | 22.2813 | 22.2255 | 21.9729 | 21.8234 | 21.7339 | 22.6739 | 22.6287 | 22.5824 | 22.5339 | 22.4782 | 22.4192 | 22.3613 | 22.3045 | 22.2466 | 21.9908 | 21.8339 | 21.7392
| REDMOSS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | YES | 0.54 | 23.4999 | 23.4188 | 23.2715 | 23.1241 | 22.9557 | 22.7925 | 22.6304 | 22.4694 | 22.3104 | 21.6525 | 21.0925 | 20.5894 | 22.2925 | 22.1252 | 21.9599 | 21.7925 | 21.6104 | 21.4325 | 21.2557 | 21.082 | 20.9115 | 20.1831 | 19.5546 | 18.9957 | 22.7641 | 22.5967 | 22.4304 | 22.2631 | 22.0778 | 21.8978 | 21.7167 | 21.5388 | 21.3631 | 20.6188 | 19.9809 | 19.4188
|  | CRAIGINCHES | EE |  |  |  |  | 23.5494 | 23.4925 | 23.4346 | 23.3262 | 23.1915 | 23.0546 | 22.9209 | 22.7915 | 22.6652 | 22.0725 | 21.5757 | 21.202 | 22.4125 | 22.2852 | 22.1557 | 22.0241 | 21.8788 | 21.7346 | 21.5915 | 21.4536 | 21.3188 | 20.6852 | 20.1504 | 19.7231 | 22.8831 | 22.7546 | 22.6252 | 22.4936 | 22.3452 | 22.1957 | 22.0473 | 21.9052 | 21.7652 | 21.1052 | 20.5441 | 20.1083
|  | CRAIGINCHES | HT |  |  |  |  | 23.4999 | 23.4188 | 23.2715 | 23.1241 | 22.9557 | 22.7925 | 22.6304 | 22.4694 | 22.3104 | 21.6525 | 21.0925 | 20.5894 | 22.2925 | 22.1252 | 21.9599 | 21.7925 | 21.6104 | 21.4325 | 21.2557 | 21.082 | 20.9115 | 20.1831 | 19.5546 | 18.9957 | 22.7641 | 22.5967 | 22.4304 | 22.2631 | 22.0778 | 21.8978 | 21.7167 | 21.5388 | 21.3631 | 20.6188 | 19.9809 | 19.4188
|  | CRAIGINCHES | HE |  |  |  |  | 23.5852 | 23.5388 | 23.4883 | 23.4346 | 23.362 | 23.2946 | 23.2304 | 23.1388 | 23.0515 | 22.6873 | 22.3999 | 22.1473 | 22.4788 | 22.4325 | 22.362 | 22.2683 | 22.1578 | 22.0557 | 21.9557 | 21.8588 | 21.7673 | 21.3831 | 21.0757 | 20.8062 | 22.7641 | 22.5967 | 22.4304 | 22.2631 | 22.0778 | 21.8978 | 21.7167 | 21.5388 | 21.3631 | 20.6188 | 19.9809 | 19.4188
|  | CRAIGINCHES | CF |  |  |  |  | 23.6125 | 23.582 | 23.5515 | 23.5178 | 23.4799 | 23.442 | 23.4041 | 23.3662 | 23.3294 | 23.0894 | 22.8694 | 22.7009 | 22.5062 | 22.4757 | 22.4452 | 22.4115 | 22.3609 | 22.2946 | 22.2273 | 22.1631 | 22.0967 | 21.7936 | 21.5546 | 21.3673 | 22.9483 | 22.9178 | 22.8873 | 22.8536 | 22.8157 | 22.762 | 22.6946 | 22.6273 | 22.5599 | 22.2504 | 22.0009 | 21.8062
| CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | NO | YES | 0.2 | 13.5663 | 12.6926 | 11.6232 | 10.5463 | 9.2116 | 8.0021 | 6.7926 | 5.5211 | 4.3021 | -1.1568 | -2.2853 | -2.8758 | 13.2011 | 12.1811 | 10.9263 | 9.6537 | 8.1179 | 6.7305 | 5.3442 | 3.8926 | 2.5021 | -3.7947 | -4.8768 | -5.5337 | 10.9432 | 9.9284 | 8.6821 | 7.4263 | 5.8884 | 4.4968 | 3.1074 | 1.6474 | 0.24737 | -6.0558 | -7.1905 | -7.8674
|  | CRAIGTON | EE |  |  |  |  | 13.6916 | 12.8905 | 11.8621 | 10.8221 | 9.5126 | 8.3305 | 7.1411 | 5.9758 | 4.7811 | -0.90737 | -2.2853 | -2.8758 | 13.3337 | 12.4 | 11.1905 | 9.9611 | 8.46 | 7.1232 | 5.7789 | 4.4526 | 3.0884 | -3.3821 | -4.6568 | -5.2368 | 11.0758 | 10.1453 | 8.9432 | 7.7284 | 6.2211 | 4.8674 | 3.5063 | 2.1674 | 0.79474 | -5.7337 | -7.1716 | -7.8084
|  | CRAIGTON | HT |  |  |  |  | 13.5663 | 12.6926 | 11.6232 | 10.5463 | 9.2116 | 8.0021 | 6.7926 | 5.5211 | 4.3021 | -1.1568 | -2.2074 | -2.8253 | 13.2011 | 12.1811 | 10.9263 | 9.6537 | 8.1179 | 6.7305 | 5.3442 | 3.8926 | 2.5021 | -3.7947 | -4.8768 | -5.5337 | 10.9432 | 9.9284 | 8.6821 | 7.4263 | 5.8884 | 4.4968 | 3.1074 | 1.6474 | 0.24737 | -6.0558 | -7.1905 | -7.8674
|  | CRAIGTON | HE |  |  |  |  | 13.8 | 13.1568 | 12.1937 | 11.2211 | 9.9589 | 8.8684 | 7.7589 | 6.6558 | 5.5516 | 0.31684 | -0.57579 | -1.2379 | 13.4442 | 12.6905 | 11.5484 | 10.3926 | 8.9474 | 7.6979 | 6.4263 | 5.1589 | 3.8895 | -2.1632 | -3.0053 | -3.5611 | 10.9432 | 9.9284 | 8.6821 | 7.4263 | 5.8884 | 4.4968 | 3.1074 | 1.6474 | 0.24737 | -6.0558 | -7.1905 | -7.8674
|  | CRAIGTON | CF |  |  |  |  | 14.4 | 14.0179 | 13.5821 | 13.1589 | 12.6379 | 12.14 | 11.6032 | 11.0316 | 10.4242 | 7.1505 | 6.5389 | 6.1916 | 14.1442 | 13.7 | 13.1895 | 12.6895 | 12.0958 | 11.5274 | 10.9063 | 10.2432 | 9.5295 | 5.7053 | 5.1189 | 4.8011 | 11.8884 | 11.4421 | 10.9316 | 10.4337 | 9.8337 | 9.2589 | 8.6368 | 7.9737 | 7.2653 | 3.4495 | 2.8042 | 2.4442
| BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 0.23 | 24.3195 | 23.9205 | 23.4889 | 23.0837 | 22.1732 | 21.3037 | 20.4353 | 19.4479 | 18.4511 | 13.1058 | 5.3363 | -0.36684 | 22.5763 | 22.1184 | 21.6311 | 21.1879 | 20.33 | 19.5079 | 18.6942 | 17.8058 | 16.9163 | 11.9689 | 4.2763 | -1.4805 | 22.8626 | 22.4184 | 21.9458 | 21.5195 | 20.5489 | 19.6216 | 18.6953 | 17.6679 | 16.6374 | 11.1121 | 2.6795 | -3.7595
|  | CRIEFF | EE |  |  |  |  | 24.4237 | 24.1732 | 23.8005 | 23.4363 | 22.4974 | 21.4932 | 20.4479 | 19.4911 | 18.5279 | 13.1058 | 5.3363 | -0.36684 | 22.7889 | 22.4058 | 21.9889 | 21.5868 | 20.7289 | 19.8426 | 18.9153 | 18.0784 | 17.2289 | 12.3605 | 4.7542 | -1.4805 | 23.0689 | 22.6889 | 22.2805 | 21.8837 | 20.8805 | 19.8258 | 18.7195 | 17.73 | 16.7332 | 11.1121 | 2.6795 | -3.7595
|  | CRIEFF | HT |  |  |  |  | 24.3195 | 23.9205 | 23.4889 | 23.0837 | 22.1732 | 21.3037 | 20.4353 | 19.4479 | 18.4511 | 13.3626 | 6.2911 | 1.4753 | 22.5763 | 22.1184 | 21.6311 | 21.1879 | 20.33 | 19.5079 | 18.6942 | 17.8058 | 16.9163 | 11.9689 | 4.2763 | -1.1037 | 22.8626 | 22.4184 | 21.9458 | 21.5195 | 20.5489 | 19.6216 | 18.6953 | 17.6679 | 16.6374 | 11.2005 | 3.2974 | -2.1174
|  | CRIEFF | HE |  |  |  |  | 24.5447 | 24.4468 | 24.2468 | 23.9763 | 23.0689 | 22.2784 | 21.4984 | 20.7016 | 19.9153 | 15.2911 | 9.41 | 3.0268 | 23.0605 | 22.7826 | 22.47 | 22.1605 | 21.35 | 20.6342 | 19.9289 | 19.1942 | 18.5037 | 14.0921 | 8.0879 | 1.5984 | 22.8626 | 22.4184 | 21.9458 | 21.5195 | 20.5489 | 19.6216 | 18.6953 | 17.6679 | 16.6374 | 11.2005 | 3.2974 | -2.1174
|  | CRIEFF | CF |  |  |  |  | 24.6205 | 24.5647 | 24.5068 | 24.4489 | 24.1353 | 23.8005 | 23.4584 | 23.1321 | 22.8511 | 20.4553 | 16.7353 | 12.6816 | 23.2268 | 23.1289 | 22.9605 | 22.8016 | 22.4595 | 22.1342 | 21.8037 | 21.4889 | 21.2058 | 18.7384 | 14.9121 | 10.5574 | 23.3689 | 23.3132 | 23.2268 | 23.0774 | 22.6774 | 22.3047 | 21.9279 | 21.5774 | 21.2721 | 18.65 | 14.5679 | 10.0511
| PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 0 | 0.93474 | 0.90421 | 0.87263 | 0.84316 | 0.74 | 0.61684 | 0.47789 | 0.35474 | 0.22947 | -0.48421 | -1.3242 | -1.8158 | 0.91579 | 0.88526 | 0.85368 | 0.82421 | 0.74842 | 0.64632 | 0.54316 | 0.43789 | 0.33158 | -0.29158 | -1.0589 | -1.5547 | 0.93579 | 0.90105 | 0.86526 | 0.83158 | 0.72842 | 0.61158 | 0.47158 | 0.34737 | 0.22105 | -0.51368 | -1.4063 | -1.9621
|  | CRINAN | EE |  |  |  |  | 0.95158 | 0.92211 | 0.89263 | 0.86211 | 0.74737 | 0.61684 | 0.47789 | 0.35474 | 0.22947 | -0.48421 | -1.3242 | -1.8158 | 0.93474 | 0.90526 | 0.87684 | 0.84737 | 0.76526 | 0.66211 | 0.54316 | 0.43789 | 0.33158 | -0.29158 | -1.0589 | -1.5547 | 0.95579 | 0.92211 | 0.88842 | 0.85579 | 0.74105 | 0.61158 | 0.47158 | 0.34737 | 0.22105 | -0.51368 | -1.4063 | -1.9621
|  | CRINAN | HT |  |  |  |  | 0.93474 | 0.90421 | 0.87263 | 0.84316 | 0.74 | 0.62737 | 0.51789 | 0.39684 | 0.27368 | -0.28105 | -0.88211 | -1.26 | 0.91579 | 0.88526 | 0.85368 | 0.82421 | 0.74842 | 0.64632 | 0.54947 | 0.44421 | 0.33474 | -0.17474 | -0.78105 | -1.1874 | 0.93579 | 0.90105 | 0.86526 | 0.83158 | 0.72842 | 0.61263 | 0.5 | 0.37684 | 0.25263 | -0.33368 | -1.0084 | -1.44
|  | CRINAN | HE |  |  |  |  | 0.97789 | 0.96316 | 0.94632 | 0.93263 | 0.82 | 0.72632 | 0.62947 | 0.52632 | 0.40316 | -0.14 | -0.72526 | -1.3611 | 0.96316 | 0.94737 | 0.93158 | 0.91579 | 0.83368 | 0.76 | 0.68211 | 0.59263 | 0.47789 | -0.013684 | -0.57053 | -1.1653 | 0.93579 | 0.90105 | 0.86526 | 0.83158 | 0.72842 | 0.61263 | 0.5 | 0.37684 | 0.25263 | -0.33368 | -1.0084 | -1.44
|  | CRINAN | CF |  |  |  |  | 0.99158 | 0.98316 | 0.97474 | 0.96632 | 0.92316 | 0.88316 | 0.84526 | 0.80632 | 0.75895 | 0.50211 | 0.14211 | -0.21158 | 0.97895 | 0.96842 | 0.96 | 0.95158 | 0.92105 | 0.89053 | 0.85895 | 0.82842 | 0.78211 | 0.54 | 0.19263 | -0.15895 | 0.98947 | 0.98316 | 0.97895 | 0.97263 | 0.92947 | 0.89053 | 0.85158 | 0.81053 | 0.75474 | 0.47895 | 0.08421 | -0.30842
| PORT ANN | CROMALT | MINIMUM HEADROOM | NN 08395 07755 | YES | YES | 0 | 2.6042 | 2.5863 | 2.5695 | 3.0516 | 3.0253 | 2.9989 | 2.9716 | 2.9432 | 2.9158 | 2.7242 | 2.4684 | 2.2874 | 2.6158 | 2.6021 | 2.5842 | 3.0663 | 3.0411 | 3.0158 | 2.9905 | 2.9653 | 2.94 | 2.7442 | 2.4589 | 2.2537 | 2.6242 | 2.6137 | 2.6021 | 3.0832 | 3.0558 | 3.0284 | 3.0011 | 2.9726 | 2.9442 | 2.7389 | 2.4558 | 2.2547
|  | CROMALT | EE |  |  |  |  | 2.6168 | 2.6011 | 2.5863 | 3.0737 | 3.0463 | 3.0168 | 2.9895 | 2.9642 | 2.9379 | 2.7474 | 2.5042 | 2.2979 | 2.6221 | 2.6137 | 2.6042 | 3.0895 | 3.0653 | 3.0411 | 3.0147 | 2.9926 | 2.9695 | 2.7853 | 2.5326 | 2.3 | 2.6305 | 2.6211 | 2.6126 | 3.1032 | 3.0779 | 3.0495 | 3.0211 | 2.9947 | 2.9695 | 2.7695 | 2.5053 | 2.2768
|  | CROMALT | HT |  |  |  |  | 2.6042 | 2.5863 | 2.5695 | 3.0516 | 3.0253 | 2.9989 | 2.9716 | 2.9432 | 2.9158 | 2.7242 | 2.4684 | 2.2874 | 2.6158 | 2.6021 | 2.5842 | 3.0663 | 3.0411 | 3.0158 | 2.9905 | 2.9653 | 2.94 | 2.7442 | 2.4589 | 2.2537 | 2.6242 | 2.6137 | 2.6021 | 3.0832 | 3.0558 | 3.0284 | 3.0011 | 2.9726 | 2.9442 | 2.7389 | 2.4558 | 2.2547
|  | CROMALT | HE |  |  |  |  | 2.6316 | 2.6242 | 2.6147 | 3.1042 | 3.0811 | 3.0611 | 3.0411 | 3.0137 | 2.9768 | 2.8211 | 2.6284 | 2.4211 | 2.6295 | 2.6242 | 2.6179 | 3.1116 | 3.0989 | 3.0853 | 3.0674 | 3.0411 | 3.0042 | 2.8495 | 2.6432 | 2.4211 | 2.6242 | 2.6137 | 2.6021 | 3.0832 | 3.0558 | 3.0284 | 3.0011 | 2.9726 | 2.9442 | 2.7389 | 2.4558 | 2.2547
|  | CROMALT | CF |  |  |  |  | 2.64 | 2.6347 | 2.6295 | 3.1253 | 3.1137 | 3.1032 | 3.0937 | 3.0842 | 3.0621 | 2.9737 | 2.8505 | 2.7095 | 2.6347 | 2.6316 | 2.6284 | 3.1253 | 3.12 | 3.1147 | 3.1095 | 3.1032 | 3.0832 | 2.9926 | 2.8632 | 2.7063 | 2.6432 | 2.64 | 2.6368 | 3.1337 | 3.1263 | 3.1179 | 3.1116 | 3.1042 | 3.0958 | 3 | 2.8642 | 2.7084
| ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | YES | 0 | 16.4963 | 16.29 | 16.0858 | 15.7879 | 14.7216 | 13.79 | 12.8605 | 12.01 | 11.4689 | 9.4353 | 8.2658 | 6.2679 | 14.9389 | 14.7011 | 14.4674 | 14.1116 | 12.9242 | 11.8989 | 10.8768 | 9.9632 | 9.3347 | 7.7895 | 6.7347 | 5.0211 | 15.6592 | 15.4897 | 15.2624 | 14.9192 | 13.7582 | 12.7129 | 11.6645 | 10.7066 | 10.0792 | 8.3487 | 7.115 | 5.4508
|  | CROSSHILLS | EE |  |  |  |  | 16.6247 | 16.4511 | 16.2763 | 16.0132 | 15.7153 | 15.3795 | 14.4079 | 13.4805 | 12.7668 | 10.0826 | 8.5679 | 7.31 | 15.0484 | 14.9 | 14.7042 | 14.3832 | 14.0389 | 13.7347 | 12.6958 | 11.6916 | 10.8484 | 8.2253 | 6.8958 | 5.5853 | 15.7276 | 15.6171 | 15.4824 | 15.1729 | 14.8392 | 14.4918 | 13.4455 | 12.4076 | 11.5855 | 8.6845 | 7.115 | 5.7118
|  | CROSSHILLS | HT |  |  |  |  | 16.4963 | 16.29 | 16.0858 | 15.7879 | 14.7216 | 13.79 | 12.8605 | 12.01 | 11.4689 | 9.8268 | 8.7658 | 7.2447 | 14.9389 | 14.7011 | 14.4674 | 14.1116 | 12.9242 | 11.8989 | 10.8768 | 9.9632 | 9.3347 | 7.7895 | 6.7347 | 5.0211 | 15.6592 | 15.4897 | 15.2624 | 14.9192 | 13.7582 | 12.7129 | 11.6645 | 10.7066 | 10.0792 | 8.3487 | 7.2055 | 5.4508
|  | CROSSHILLS | HE |  |  |  |  | 16.77 | 16.6942 | 16.5647 | 16.3837 | 15.95 | 15.6658 | 15.0258 | 14.3805 | 11.6742 | 9.4353 | 8.2658 | 6.2679 | 15.1463 | 15.0758 | 14.9989 | 14.8084 | 14.3716 | 14.1232 | 13.4305 | 12.7463 | 10.4926 | 8.2126 | 7.0958 | 5.0747 | 15.6592 | 15.4897 | 15.2624 | 14.9192 | 13.7582 | 12.7129 | 11.6645 | 10.7066 | 10.0792 | 8.3487 | 7.2055 | 5.4508
|  | CROSSHILLS | CF |  |  |  |  | 16.8311 | 16.7932 | 16.7532 | 16.6711 | 16.4858 | 16.3521 | 16.2216 | 15.9321 | 15.6195 | 14.1532 | 13.3226 | 11.9953 | 15.2105 | 15.1716 | 15.1316 | 15.0884 | 14.9526 | 14.8274 | 14.7042 | 14.3484 | 13.9874 | 12.4 | 11.5853 | 10.1421 | 15.8834 | 15.8455 | 15.8055 | 15.7655 | 15.6634 | 15.5697 | 15.4308 | 15.0803 | 14.7297 | 13.1255 | 12.2287 | 10.7308
| KEITH 1 | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 0 | 7.3421 | 7.2558 | 7.1705 | 7.0484 | 6.6474 | 6.2358 | 5.76 | 5.3463 | 4.9274 | 0.49263 | -3.4316 | -6.3811 | 7.0495 | 6.8232 | 6.5832 | 6.3789 | 6.0137 | 5.6526 | 5.2842 | 4.9305 | 4.5716 | 0.53474 | -3.3884 | -6.4242 | 7.1632 | 6.9642 | 6.7547 | 6.5716 | 6.1716 | 5.7495 | 5.2695 | 4.8516 | 4.4221 | -0.18421 | -4.4011 | -7.7916
|  | CULLEN | EE |  |  |  |  | 7.3863 | 7.3084 | 7.2274 | 7.1453 | 6.7663 | 6.2358 | 5.76 | 5.3463 | 4.9274 | 0.49263 | -3.4316 | -6.3811 | 7.1695 | 7.0021 | 6.7789 | 6.5726 | 6.1663 | 5.6905 | 5.2842 | 4.9305 | 4.5716 | 0.64526 | -3.2168 | -6.4242 | 7.2674 | 7.1137 | 6.9168 | 6.7326 | 6.2789 | 5.7495 | 5.2695 | 4.8516 | 4.4221 | -0.18421 | -4.4011 | -7.7916
|  | CULLEN | HT |  |  |  |  | 7.3421 | 7.2558 | 7.1705 | 7.0484 | 6.6474 | 6.2495 | 5.8695 | 5.4484 | 5.0305 | 0.68211 | -2.9432 | -5.4305 | 7.0495 | 6.8232 | 6.5832 | 6.3789 | 6.0137 | 5.6526 | 5.3137 | 4.9442 | 4.5832 | 0.53474 | -3.3884 | -6.1632 | 7.1632 | 6.9642 | 6.7547 | 6.5716 | 6.1716 | 5.7716 | 5.3811 | 4.9474 | 4.5189 | -0.047368 | -4.18 | -7.0358
|  | CULLEN | HE |  |  |  |  | 7.4463 | 7.4032 | 7.3558 | 7.3053 | 6.9747 | 6.6032 | 6.2621 | 5.9274 | 5.5221 | 2.3221 | -0.67895 | -3.9495 | 7.2968 | 7.1621 | 6.9716 | 6.8147 | 6.4168 | 6.0495 | 5.76 | 5.4779 | 5.1095 | 2.1358 | -0.92526 | -4.2611 | 7.1632 | 6.9642 | 6.7547 | 6.5716 | 6.1716 | 5.7716 | 5.3811 | 4.9474 | 4.5189 | -0.047368 | -4.18 | -7.0358
|  | CULLEN | CF |  |  |  |  | 7.4853 | 7.4621 | 7.4368 | 7.4126 | 7.2853 | 7.1716 | 7.0579 | 6.96 | 6.8821 | 5.5884 | 3.6768 | 1.5779 | 7.3611 | 7.3368 | 7.2821 | 7.2137 | 7.0579 | 6.8979 | 6.7105 | 6.5811 | 6.3189 | 5.0095 | 3.0632 | 0.79684 | 7.4463 | 7.4232 | 7.3663 | 7.3053 | 7.1305 | 6.9579 | 6.7653 | 6.6221 | 6.3874 | 5.0484 | 2.9463 | 0.56737
| INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | YES | 0.058 | 17.1325 | 30.3567 | 29.4525 | 28.6209 | 27.5199 | 26.4399 | 25.3757 | 24.2999 | 23.7325 | 21.2473 | 19.4209 | 18.102 | 15.9936 | 27.5957 | 26.5788 | 25.6473 | 24.4673 | 23.3094 | 22.1704 | 21.0304 | 20.4894 | 18.0262 | 16.1673 | 14.7588 | 16.2557 | 28.6025 | 27.5825 | 26.6478 | 25.4288 | 24.2331 | 23.0531 | 21.8636 | 21.2731 | 18.6194 | 16.6446 | 15.1899
|  | CULLODEN | EE |  |  |  |  | 17.3831 | 30.7125 | 29.8799 | 29.1146 | 28.0904 | 27.0367 | 25.9694 | 24.9504 | 24.4399 | 21.8852 | 19.5725 | 18.3315 | 16.2904 | 27.9841 | 27.0483 | 26.1894 | 25.1041 | 24.0031 | 22.8852 | 21.8094 | 21.3304 | 18.9473 | 16.8241 | 15.5736 | 16.4799 | 28.9888 | 28.0488 | 27.1867 | 26.052 | 24.8931 | 23.7152 | 22.5878 | 22.0552 | 19.3846 | 16.9552 | 15.6088
|  | CULLODEN | HT |  |  |  |  | 17.1325 | 30.3567 | 29.4525 | 28.6209 | 27.5199 | 26.4399 | 25.3757 | 24.2999 | 23.7325 | 21.2473 | 19.4209 | 18.102 | 15.9936 | 27.5957 | 26.5788 | 25.6473 | 24.4673 | 23.3094 | 22.1704 | 21.0304 | 20.4894 | 18.0262 | 16.1673 | 14.7588 | 16.2557 | 28.6025 | 27.5825 | 26.6478 | 25.4288 | 24.2331 | 23.0531 | 21.8636 | 21.2731 | 18.6194 | 16.6446 | 15.1899
|  | CULLODEN | HE |  |  |  |  | 17.7146 | 31.2031 | 30.4925 | 29.8431 | 28.8915 | 27.9978 | 27.0999 | 26.2136 | 25.8452 | 24.3178 | 23.0862 | 21.8599 | 16.6841 | 28.5146 | 27.7052 | 26.9694 | 25.9704 | 25.0199 | 24.0673 | 23.1252 | 22.7873 | 21.4146 | 20.3315 | 19.2494 | 16.2557 | 28.6025 | 27.5825 | 26.6478 | 25.4288 | 24.2331 | 23.0531 | 21.8636 | 21.2731 | 18.6194 | 16.6446 | 15.1899
|  | CULLODEN | CF |  |  |  |  | 17.9631 | 31.9736 | 31.6199 | 31.3315 | 30.8999 | 30.4557 | 29.9852 | 29.4978 | 29.2736 | 28.3388 | 27.4694 | 26.8357 | 17.2767 | 29.4925 | 29.0252 | 28.6609 | 28.202 | 27.7231 | 27.2136 | 26.6788 | 26.4473 | 25.5452 | 24.7483 | 24.1546 | 16.7715 | 30.0499 | 29.9752 | 29.6699 | 29.1909 | 28.6941 | 28.1678 | 27.6183 | 27.3762 | 26.3941 | 25.4836 | 24.812
| CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | YES | 0 | 11.8032 | 11.4442 | 11.06 | 10.6495 | 10.1242 | 9.6958 | 9.2579 | 8.7684 | 8.2232 | 6.4758 | 4.4979 | 2.2368 | 11.1063 | 10.6884 | 10.2684 | 9.8179 | 9.2916 | 8.8779 | 8.4526 | 7.9789 | 7.4421 | 5.7705 | 3.6968 | 1.4705 | 11.2558 | 10.8979 | 10.5337 | 10.0989 | 9.5411 | 9.0895 | 8.6284 | 8.1105 | 7.5263 | 5.68 | 3.4863 | 1.0926
|  | CULTER | EE |  |  |  |  | 11.8853 | 11.6495 | 11.3084 | 10.9368 | 10.4232 | 10.0126 | 9.5737 | 9.1705 | 8.7526 | 6.5189 | 4.5589 | 2.2368 | 11.2779 | 10.9116 | 10.54 | 10.1316 | 9.6284 | 9.2589 | 8.8579 | 8.4853 | 8.0958 | 6.0042 | 4.2295 | 1.7021 | 11.4074 | 11.0916 | 10.7737 | 10.3989 | 9.8611 | 9.4368 | 8.9811 | 8.5632 | 8.1284 | 5.78 | 3.7242 | 1.0926
|  | CULTER | HT |  |  |  |  | 11.8032 | 11.4442 | 11.06 | 10.6495 | 10.1242 | 9.6958 | 9.2579 | 8.7684 | 8.2232 | 6.4758 | 4.4979 | 2.4916 | 11.1063 | 10.6884 | 10.2684 | 9.8179 | 9.2916 | 8.8779 | 8.4526 | 7.9789 | 7.4421 | 5.7705 | 3.6968 | 1.4705 | 11.2558 | 10.8979 | 10.5337 | 10.0989 | 9.5411 | 9.0895 | 8.6284 | 8.1105 | 7.5263 | 5.68 | 3.4863 | 1.1989
|  | CULTER | HE |  |  |  |  | 11.9874 | 11.9147 | 11.6589 | 11.3611 | 10.8895 | 10.5937 | 10.2516 | 9.8937 | 9.5242 | 8.0253 | 6.2989 | 3.8463 | 11.4884 | 11.2284 | 10.9116 | 10.5789 | 10.1274 | 9.8632 | 9.5453 | 9.2084 | 8.8558 | 7.4621 | 5.7642 | 3.2389 | 11.2558 | 10.8979 | 10.5337 | 10.0989 | 9.5411 | 9.0895 | 8.6284 | 8.1105 | 7.5263 | 5.68 | 3.4863 | 1.1989
|  | CULTER | CF |  |  |  |  | 12.0505 | 12.0084 | 11.9653 | 11.9211 | 11.78 | 11.6358 | 11.4905 | 11.3463 | 11.2105 | 10.2611 | 9.1547 | 7.5568 | 11.56 | 11.5137 | 11.4358 | 11.2747 | 11.0726 | 10.9379 | 10.8021 | 10.6632 | 10.5284 | 9.5821 | 8.4853 | 6.7611 | 11.7463 | 11.6832 | 11.5484 | 11.4116 | 11.2095 | 11.0653 | 10.9211 | 10.7779 | 10.6463 | 9.7 | 8.5295 | 6.72
| ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 0.113 | 23.7696 | 23.5244 | 23.2149 | 22.9559 | 22.7738 | 22.5959 | 22.4223 | 22.2444 | 22.0728 | 21.4581 | 20.8317 | 20.3086 | 23.5459 | 23.4396 | 23.3302 | 23.2207 | 23.0902 | 22.9302 | 22.7249 | 22.5154 | 22.3123 | 21.5375 | 20.5554 | 19.6691 | 24.3809 | 24.2736 | 24.1641 | 23.9757 | 23.7536 | 23.5325 | 23.3178 | 23.0988 | 22.8873 | 22.0841 | 21.1031 | 20.2294
|  | CUMMING STREET | EE |  |  |  |  | 23.8675 | 23.6791 | 23.4181 | 23.1738 | 22.9833 | 22.8086 | 22.6559 | 22.5128 | 22.3717 | 21.7265 | 21.3012 | 20.9023 | 23.6091 | 23.5238 | 23.4344 | 23.3407 | 23.2354 | 23.1312 | 23.0228 | 22.8565 | 22.6944 | 21.9333 | 21.4333 | 20.8017 | 24.4441 | 24.3588 | 24.2673 | 24.1736 | 24.0315 | 23.8041 | 23.6188 | 23.4441 | 23.2725 | 22.462 | 21.9336 | 21.2862
|  | CUMMING STREET | HT |  |  |  |  | 23.7696 | 23.5244 | 23.2149 | 22.9559 | 22.7738 | 22.5959 | 22.4223 | 22.2444 | 22.0728 | 21.4581 | 20.8317 | 20.3086 | 23.5459 | 23.4396 | 23.3302 | 23.2207 | 23.0902 | 22.9302 | 22.7249 | 22.5154 | 22.3123 | 21.5375 | 20.5554 | 19.6691 | 24.3809 | 24.2736 | 24.1641 | 23.9757 | 23.7536 | 23.5325 | 23.3178 | 23.0988 | 22.8873 | 22.0841 | 21.1031 | 20.2294
|  | CUMMING STREET | HE |  |  |  |  | 23.9896 | 23.8307 | 23.5959 | 23.3812 | 23.237 | 23.1159 | 23.0044 | 22.8959 | 22.7949 | 22.4002 | 22.0612 | 21.8349 | 23.6838 | 23.6217 | 23.5533 | 23.4807 | 23.3923 | 23.3123 | 23.2344 | 23.1596 | 23.0912 | 22.7975 | 22.3754 | 22.1144 | 24.3809 | 24.2736 | 24.1641 | 23.9757 | 23.7536 | 23.5325 | 23.3178 | 23.0988 | 22.8873 | 22.0841 | 21.1031 | 20.2294
|  | CUMMING STREET | CF |  |  |  |  | 24.0633 | 23.9886 | 23.8875 | 23.7981 | 23.7212 | 23.6412 | 23.5612 | 23.4907 | 23.4202 | 23.1075 | 22.8917 | 22.7423 | 23.7333 | 23.6965 | 23.6586 | 23.6196 | 23.5765 | 23.5323 | 23.4881 | 23.4449 | 23.4038 | 23.2175 | 23.1081 | 23.0481 | 24.5683 | 24.5315 | 24.4925 | 24.4536 | 24.4062 | 24.3588 | 24.3115 | 24.2652 | 24.222 | 24.0167 | 23.8831 | 23.8052
| ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | YES | 0 | 6.4063 | 6.2926 | 6.1389 | 5.9779 | 5.7242 | 5.4958 | 5.2358 | 4.9905 | 4.7389 | 3.4389 | 1.9726 | 1.0579 | 6.0832 | 5.9263 | 5.7516 | 5.5726 | 5.3474 | 5.1463 | 4.9495 | 4.72 | 4.4968 | 3.4442 | 2.1611 | 1.2284 | 6.1568 | 6.0011 | 5.8274 | 5.6484 | 5.3874 | 5.1526 | 4.8916 | 4.6432 | 4.3874 | 3.0789 | 1.5632 | 0.53368
|  | DALCHONZIE | EE |  |  |  |  | 6.4368 | 6.3895 | 6.2716 | 6.1421 | 5.8326 | 5.52 | 5.2358 | 4.9905 | 4.7389 | 3.4389 | 1.9726 | 1.0579 | 6.1432 | 6.0421 | 5.9063 | 5.76 | 5.4779 | 5.2042 | 4.9653 | 4.7589 | 4.5421 | 3.4442 | 2.1611 | 1.2284 | 6.2316 | 6.1147 | 5.9789 | 5.8305 | 5.5053 | 5.1821 | 4.8916 | 4.6432 | 4.3884 | 3.0789 | 1.5632 | 0.53368
|  | DALCHONZIE | HT |  |  |  |  | 6.4063 | 6.2926 | 6.1389 | 5.9779 | 5.7242 | 5.4958 | 5.2695 | 5.0063 | 4.7474 | 3.7695 | 2.7316 | 2.0042 | 6.0832 | 5.9263 | 5.7516 | 5.5726 | 5.3474 | 5.1463 | 4.9495 | 4.72 | 4.4968 | 3.6411 | 2.6179 | 1.84 | 6.1568 | 6.0011 | 5.8274 | 5.6484 | 5.3874 | 5.1526 | 4.9211 | 4.6516 | 4.3874 | 3.3842 | 2.2558 | 1.4442
|  | DALCHONZIE | HE |  |  |  |  | 6.4747 | 6.4474 | 6.3958 | 6.2874 | 5.9937 | 5.7716 | 5.5674 | 5.3653 | 5.1642 | 4.2853 | 3.1737 | 1.9474 | 6.2084 | 6.1421 | 6.0368 | 5.9095 | 5.6474 | 5.4568 | 5.2874 | 5.1168 | 4.9474 | 4.2147 | 3.1737 | 2.0274 | 6.1568 | 6.0011 | 5.8274 | 5.6484 | 5.3874 | 5.1526 | 4.9211 | 4.6516 | 4.3874 | 3.3842 | 2.2558 | 1.4442
|  | DALCHONZIE | CF |  |  |  |  | 6.4989 | 6.4842 | 6.4684 | 6.4526 | 6.3747 | 6.3 | 6.1905 | 6.1042 | 6.0316 | 5.5989 | 4.9137 | 4.2379 | 6.2653 | 6.2358 | 6.2032 | 6.1695 | 6.0863 | 5.9842 | 5.8811 | 5.8042 | 5.7337 | 5.3516 | 4.7063 | 4.0347 | 6.3274 | 6.3126 | 6.2947 | 6.2589 | 6.1432 | 6.0274 | 5.9095 | 5.8211 | 5.7421 | 5.2968 | 4.5589 | 3.8158
| NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 0 | 15.1258 | 14.7732 | 14.3437 | 13.7637 | 12.7574 | 11.7532 | 10.7384 | 9.7511 | 9.3774 | 7.9658 | 6.6332 | 6.1542 | 13.9642 | 13.5484 | 13.04 | 12.3495 | 11.2116 | 10.0737 | 8.9274 | 7.8305 | 7.4758 | 6.4137 | 5.3695 | 4.9621 | 14.5045 | 14.1055 | 13.6076 | 12.9266 | 11.7561 | 10.5845 | 9.4024 | 8.2624 | 7.8613 | 6.4687 | 5.1424 | 4.6539
|  | DALCROSS | EE |  |  |  |  | 15.1605 | 14.8121 | 14.3868 | 13.8111 | 12.9753 | 12.0963 | 11.0216 | 9.9805 | 9.5374 | 7.9658 | 6.6332 | 6.1542 | 14.0032 | 13.5937 | 13.0916 | 12.4084 | 11.4905 | 10.5421 | 9.3568 | 8.1989 | 7.7632 | 6.4137 | 5.3695 | 4.9621 | 14.5413 | 14.1476 | 13.6561 | 12.9824 | 12.0213 | 11.0192 | 9.7803 | 8.5761 | 8.0929 | 6.4687 | 5.1424 | 4.6539
|  | DALCROSS | HT |  |  |  |  | 15.1258 | 14.7732 | 14.3437 | 13.7637 | 12.7574 | 11.7532 | 10.7384 | 9.7511 | 9.3774 | 8.4205 | 7.7953 | 7.4837 | 13.9642 | 13.5484 | 13.04 | 12.3495 | 11.2116 | 10.0737 | 8.9274 | 7.8305 | 7.4758 | 6.6884 | 6.1589 | 5.8758 | 14.5045 | 14.1055 | 13.6076 | 12.9266 | 11.7561 | 10.5845 | 9.4024 | 8.2624 | 7.8613 | 6.8929 | 6.255 | 5.9276
|  | DALCROSS | HE |  |  |  |  | 15.2079 | 14.8858 | 14.4879 | 13.9374 | 13.0953 | 12.2879 | 11.3626 | 10.4374 | 10.1279 | 8.7553 | 7.9616 | 7.1205 | 14.0547 | 13.6705 | 13.1947 | 12.5347 | 11.6158 | 10.7242 | 9.6874 | 8.6537 | 8.3632 | 7.0853 | 6.48 | 5.8358 | 14.5045 | 14.1055 | 13.6076 | 12.9266 | 11.7561 | 10.5845 | 9.4024 | 8.2624 | 7.8613 | 6.8929 | 6.255 | 5.9276
|  | DALCROSS | CF |  |  |  |  | 15.4689 | 15.3016 | 15.11 | 14.8605 | 14.5068 | 14.1332 | 13.7311 | 13.2426 | 13.0784 | 12.3732 | 11.8195 | 11.4121 | 14.3558 | 14.1684 | 13.9389 | 13.64 | 13.2516 | 12.8316 | 12.3779 | 11.8158 | 11.6379 | 10.9432 | 10.4863 | 10.1432 | 14.8803 | 14.695 | 14.4834 | 14.1971 | 13.7982 | 13.3708 | 12.9097 | 12.3361 | 12.1487 | 11.3782 | 10.815 | 10.3961
| TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0 | 1.0442 | 1.0368 | 1.0316 | 1.0253 | 1.0189 | 1.0137 | 1.0074 | 1.0021 | 0.99684 | 0.97579 | 0.96 | 0.94737 | 1.0221 | 1.0179 | 1.0147 | 1.0105 | 1.0063 | 1 | 0.99474 | 0.98842 | 0.98211 | 0.96105 | 0.94316 | 0.92947 | 1.0253 | 1.0179 | 1.0116 | 1.0053 | 0.99789 | 0.99263 | 0.98632 | 0.98 | 0.97474 | 0.95158 | 0.93474 | 0.92
|  | DALMALLY | EE |  |  |  |  | 1.0484 | 1.0432 | 1.0379 | 1.0347 | 1.0295 | 1.0253 | 1.02 | 1.0158 | 1.0116 | 0.99474 | 0.98211 | 0.97368 | 1.0242 | 1.0211 | 1.0179 | 1.0158 | 1.0126 | 1.0095 | 1.0063 | 1.0032 | 0.99895 | 0.98105 | 0.96737 | 0.95684 | 1.0305 | 1.0242 | 1.0189 | 1.0147 | 1.0095 | 1.0053 | 1 | 0.99474 | 0.99158 | 0.97263 | 0.95895 | 0.94842
|  | DALMALLY | HT |  |  |  |  | 1.0442 | 1.0368 | 1.0316 | 1.0253 | 1.0189 | 1.0137 | 1.0074 | 1.0021 | 0.99684 | 0.97579 | 0.96 | 0.94737 | 1.0221 | 1.0179 | 1.0147 | 1.0105 | 1.0063 | 1 | 0.99474 | 0.98842 | 0.98211 | 0.96105 | 0.94316 | 0.92947 | 1.0253 | 1.0179 | 1.0116 | 1.0053 | 0.99789 | 0.99263 | 0.98632 | 0.98 | 0.97474 | 0.95158 | 0.93474 | 0.92
|  | DALMALLY | HE |  |  |  |  | 1.0537 | 1.0516 | 1.0484 | 1.0453 | 1.0421 | 1.0389 | 1.0358 | 1.0326 | 1.0295 | 1.0211 | 1.0095 | 0.99474 | 1.0274 | 1.0253 | 1.0232 | 1.0211 | 1.0189 | 1.0168 | 1.0147 | 1.0126 | 1.0105 | 1.0053 | 0.99579 | 0.97895 | 1.0253 | 1.0179 | 1.0116 | 1.0053 | 0.99789 | 0.99263 | 0.98632 | 0.98 | 0.97474 | 0.95158 | 0.93474 | 0.92
|  | DALMALLY | CF |  |  |  |  | 1.0579 | 1.0558 | 1.0537 | 1.0526 | 1.0505 | 1.0484 | 1.0474 | 1.0453 | 1.0432 | 1.0358 | 1.0305 | 1.0189 | 1.0295 | 1.0284 | 1.0274 | 1.0263 | 1.0253 | 1.0242 | 1.0232 | 1.0221 | 1.0211 | 1.0168 | 1.0147 | 1.0053 | 1.0368 | 1.0358 | 1.0347 | 1.0337 | 1.0326 | 1.0305 | 1.0284 | 1.0263 | 1.0242 | 1.0168 | 1.0105 | 0.99684
| TAYNUILT | DALMALLY SCHOOL | MINIMUM HEADROOM | NN 17249 27128 | YES | YES | 0 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725
|  | DALMALLY SCHOOL | EE |  |  |  |  | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933
|  | DALMALLY SCHOOL | HT |  |  |  |  | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657
|  | DALMALLY SCHOOL | HE |  |  |  |  | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725
|  | DALMALLY SCHOOL | CF |  |  |  |  | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445
| INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | YES | 0.275 | 12.6934 | 12.3734 | 12.0524 | 11.7313 | 11.365 | 11.0039 | 10.5987 | 10.2018 | 9.8208 | 8.0229 | 6.5871 | 5.3703 | 12.9334 | 12.5008 | 12.0734 | 11.6471 | 11.1713 | 10.7145 | 10.2724 | 9.8513 | 9.4513 | 7.4997 | 5.9218 | 4.5639 | 13.2945 | 13.0587 | 12.7755 | 12.365 | 11.8987 | 11.4513 | 11.005 | 10.5797 | 10.1734 | 8.2029 | 6.6124 | 5.2513
|  | DALNEIGH | EE |  |  |  |  | 12.8903 | 12.6324 | 12.3671 | 12.0976 | 11.805 | 11.5187 | 11.2313 | 10.9576 | 10.685 | 9.1913 | 7.9934 | 7.0608 | 13.1261 | 12.8745 | 12.525 | 12.1734 | 11.8061 | 11.4524 | 11.0861 | 10.7355 | 10.4018 | 8.8124 | 7.5261 | 6.4903 | 13.425 | 13.2334 | 13.0313 | 12.8239 | 12.5061 | 12.1566 | 11.7934 | 11.4492 | 11.1197 | 9.4987 | 8.1808 | 7.1355
|  | DALNEIGH | HT |  |  |  |  | 12.6934 | 12.3734 | 12.0524 | 11.7313 | 11.365 | 11.0039 | 10.5987 | 10.2018 | 9.8208 | 8.0229 | 6.5871 | 5.3703 | 12.9334 | 12.5008 | 12.0734 | 11.6471 | 11.1713 | 10.7145 | 10.2724 | 9.8513 | 9.4513 | 7.4997 | 5.9218 | 4.5639 | 13.2945 | 13.0587 | 12.7755 | 12.365 | 11.8987 | 11.4513 | 11.005 | 10.5797 | 10.1734 | 8.2029 | 6.6124 | 5.2513
|  | DALNEIGH | HE |  |  |  |  | 13.1587 | 12.9839 | 12.7976 | 12.6039 | 12.3766 | 12.1713 | 11.9661 | 11.7671 | 11.5861 | 10.925 | 10.4924 | 10.0429 | 13.3029 | 13.1671 | 13.0197 | 12.8639 | 12.6303 | 12.3839 | 12.1334 | 11.8924 | 11.6734 | 10.8587 | 10.2913 | 9.7797 | 13.2945 | 13.0587 | 12.7755 | 12.365 | 11.8987 | 11.4513 | 11.005 | 10.5797 | 10.1734 | 8.2029 | 6.6124 | 5.2513
|  | DALNEIGH | CF |  |  |  |  | 13.3345 | 13.2197 | 13.1103 | 12.9997 | 12.8776 | 12.7566 | 12.6355 | 12.5134 | 12.3955 | 11.8608 | 11.5039 | 11.2587 | 13.4176 | 13.3387 | 13.2587 | 13.1766 | 13.0892 | 13.0018 | 12.9134 | 12.7734 | 12.6166 | 11.9145 | 11.4176 | 11.0387 | 13.7176 | 13.6418 | 13.5597 | 13.4766 | 13.3861 | 13.2945 | 13.2039 | 13.1134 | 13.025 | 12.5976 | 12.1071 | 11.7397
| COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | NO | YES | 0 | 2.84 | 2.8053 | 2.7558 | 2.6884 | 2.5716 | 2.4611 | 2.3516 | 2.2358 | 2.1168 | 1.5579 | 1.1568 | 0.89895 | 2.6053 | 2.5463 | 2.4874 | 2.4137 | 2.3042 | 2.2 | 2.0968 | 1.9905 | 1.8821 | 1.38 | 1.1 | 0.83684 | 2.6211 | 2.5653 | 2.5095 | 2.44 | 2.3211 | 2.2095 | 2.0958 | 1.9768 | 1.8516 | 1.2653 | 0.86 | 0.57895
|  | DALRULZION | EE |  |  |  |  | 2.8558 | 2.8263 | 2.7968 | 2.7653 | 2.6632 | 2.5453 | 2.4274 | 2.3211 | 2.2147 | 1.6747 | 1.1568 | 0.89895 | 2.6432 | 2.5968 | 2.5495 | 2.5053 | 2.4158 | 2.3126 | 2.2095 | 2.1147 | 2.0221 | 1.5558 | 1.1 | 0.85158 | 2.6558 | 2.6095 | 2.5642 | 2.5189 | 2.4137 | 2.2937 | 2.1726 | 2.0642 | 1.9547 | 1.3989 | 0.86 | 0.57895
|  | DALRULZION | HT |  |  |  |  | 2.84 | 2.8053 | 2.7558 | 2.6884 | 2.5716 | 2.4611 | 2.3516 | 2.2358 | 2.1168 | 1.5579 | 1.2979 | 1.0495 | 2.6053 | 2.5463 | 2.4874 | 2.4137 | 2.3042 | 2.2 | 2.0968 | 1.9905 | 1.8821 | 1.38 | 1.1011 | 0.83684 | 2.6211 | 2.5653 | 2.5095 | 2.44 | 2.3211 | 2.2095 | 2.0958 | 1.9768 | 1.8516 | 1.2653 | 0.97684 | 0.70211
|  | DALRULZION | HE |  |  |  |  | 2.8821 | 2.8642 | 2.8453 | 2.8274 | 2.7505 | 2.6853 | 2.62 | 2.5568 | 2.4821 | 2.1326 | 1.8242 | 1.5137 | 2.6811 | 2.6653 | 2.64 | 2.6116 | 2.54 | 2.4758 | 2.4137 | 2.3526 | 2.2905 | 1.9937 | 1.7263 | 1.4568 | 2.6211 | 2.5653 | 2.5095 | 2.44 | 2.3211 | 2.2095 | 2.0958 | 1.9768 | 1.8516 | 1.2653 | 0.97684 | 0.70211
|  | DALRULZION | CF |  |  |  |  | 2.8979 | 2.8874 | 2.88 | 2.8705 | 2.84 | 2.8126 | 2.7853 | 2.7621 | 2.7411 | 2.6011 | 2.4011 | 2.2495 | 2.6968 | 2.6874 | 2.68 | 2.6705 | 2.64 | 2.6095 | 2.5789 | 2.5526 | 2.5263 | 2.3842 | 2.2095 | 2.0747 | 2.7021 | 2.6916 | 2.6842 | 2.6758 | 2.6442 | 2.6095 | 2.5747 | 2.5442 | 2.5158 | 2.3505 | 2.1474 | 1.9905
| BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 0 | 1.2863 | 1.2705 | 1.2547 | 1.2368 | 1.08 | 0.87895 | 0.67158 | 0.47579 | 0.18737 | -1.5158 | -3.4968 | -4.9789 | 1.1221 | 1.1 | 1.0779 | 1.0558 | 0.93789 | 0.75579 | 0.56632 | 0.38632 | 0.10105 | -1.4632 | -3.4116 | -5.0284 | 1.1989 | 1.1758 | 1.1516 | 1.1274 | 0.96947 | 0.76842 | 0.56 | 0.38105 | 0.11053 | -1.7926 | -3.9516 | -5.6379
|  | DALWHINNIE | EE |  |  |  |  | 1.2916 | 1.2737 | 1.2558 | 1.2368 | 1.08 | 0.87895 | 0.67158 | 0.49263 | 0.26737 | -1.5158 | -3.4968 | -4.9789 | 1.1326 | 1.1116 | 1.0895 | 1.0663 | 0.93895 | 0.78105 | 0.62 | 0.48 | 0.28211 | -1.4632 | -3.4116 | -5.0284 | 1.2095 | 1.1853 | 1.16 | 1.1347 | 0.96947 | 0.76842 | 0.56 | 0.38105 | 0.14632 | -1.7926 | -3.9516 | -5.6379
|  | DALWHINNIE | HT |  |  |  |  | 1.2863 | 1.2705 | 1.2547 | 1.2379 | 1.0968 | 0.95368 | 0.80842 | 0.60632 | 0.26421 | -1.3242 | -3.1211 | -4.3379 | 1.1221 | 1.1 | 1.0779 | 1.0558 | 0.94211 | 0.82632 | 0.71053 | 0.53684 | 0.19263 | -1.44 | -3.3863 | -4.7453 | 1.1989 | 1.1758 | 1.1516 | 1.1274 | 0.98421 | 0.84 | 0.69263 | 0.48632 | 0.11053 | -1.6463 | -3.6916 | -5.0947
|  | DALWHINNIE | HE |  |  |  |  | 1.2979 | 1.2916 | 1.2853 | 1.2779 | 1.0895 | 0.88526 | 0.67684 | 0.47579 | 0.18737 | -1.0432 | -2.5642 | -4.2305 | 1.1474 | 1.1389 | 1.1295 | 1.1189 | 0.93789 | 0.75579 | 0.56632 | 0.38632 | 0.10105 | -1.0926 | -2.6474 | -4.3432 | 1.1989 | 1.1758 | 1.1516 | 1.1274 | 0.98421 | 0.84 | 0.69263 | 0.48632 | 0.11053 | -1.6463 | -3.6916 | -5.0947
|  | DALWHINNIE | CF |  |  |  |  | 1.3032 | 1.2979 | 1.2947 | 1.2905 | 1.2326 | 1.1842 | 1.0737 | 0.95158 | 0.81368 | 0.18842 | -0.77263 | -1.8337 | 1.1558 | 1.1484 | 1.1432 | 1.1368 | 1.0842 | 1.04 | 0.91895 | 0.79263 | 0.64316 | 0.0073684 | -0.97789 | -2.1137 | 1.2316 | 1.2242 | 1.2189 | 1.2126 | 1.1432 | 1.0863 | 0.95684 | 0.82421 | 0.66842 | -0.022105 | -1.0895 | -2.2905
| WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | YES | 0 | 24.3689 | 24.2679 | 24.1605 | 24.0479 | 23.9226 | 23.7995 | 23.6784 | 23.5605 | 23.4437 | 23.0174 | 22.4963 | 21.6605 | 21.0537 | 20.9558 | 20.8526 | 20.7453 | 20.6242 | 20.5084 | 20.3916 | 20.28 | 20.1684 | 19.7695 | 19.4663 | 19.2295 | 21.5745 | 21.4808 | 21.385 | 21.2839 | 21.1703 | 21.0587 | 20.9482 | 20.8408 | 20.7345 | 20.3618 | 20.0882 | 19.8829
|  | DENBURN | EE |  |  |  |  | 24.4468 | 24.3742 | 24.2963 | 24.2121 | 24.1184 | 24.0258 | 23.9342 | 23.8447 | 23.7574 | 23.3763 | 23.1205 | 22.9174 | 21.1305 | 21.0589 | 20.9842 | 20.9021 | 20.8137 | 20.7274 | 20.6411 | 20.5568 | 20.4747 | 20.12 | 19.8916 | 19.7295 | 21.6482 | 21.5797 | 21.5071 | 21.4303 | 21.3461 | 21.2629 | 21.1797 | 21.0987 | 21.0197 | 20.6808 | 20.4661 | 20.3239
|  | DENBURN | HT |  |  |  |  | 24.3689 | 24.2679 | 24.1605 | 24.0479 | 23.9226 | 23.7995 | 23.6784 | 23.5605 | 23.4437 | 23.0174 | 22.4963 | 21.6605 | 21.0537 | 20.9558 | 20.8526 | 20.7453 | 20.6242 | 20.5084 | 20.3916 | 20.28 | 20.1684 | 19.7695 | 19.4663 | 19.2295 | 21.5745 | 21.4808 | 21.385 | 21.2839 | 21.1703 | 21.0587 | 20.9482 | 20.8408 | 20.7345 | 20.3618 | 20.0882 | 19.8829
|  | DENBURN | HE |  |  |  |  | 24.4879 | 24.4226 | 24.3532 | 24.2805 | 24.1995 | 24.1258 | 24.0511 | 23.9816 | 23.9163 | 23.6721 | 23.5205 | 23.4216 | 21.1684 | 21.1053 | 21.0368 | 20.9642 | 20.8874 | 20.8147 | 20.7453 | 20.6779 | 20.6158 | 20.3884 | 20.2537 | 20.1705 | 21.5745 | 21.4808 | 21.385 | 21.2839 | 21.1703 | 21.0587 | 20.9482 | 20.8408 | 20.7345 | 20.3618 | 20.0882 | 19.8829
|  | DENBURN | CF |  |  |  |  | 24.5121 | 24.4647 | 24.4163 | 24.3679 | 24.3174 | 24.2658 | 24.2132 | 24.1626 | 24.1111 | 23.8879 | 23.7605 | 23.6858 | 21.1926 | 21.1474 | 21.0989 | 21.0516 | 21.0011 | 20.9526 | 20.9021 | 20.8526 | 20.8021 | 20.5863 | 20.4695 | 20.4042 | 21.7061 | 21.6618 | 21.6155 | 21.5692 | 21.5208 | 21.4713 | 21.4218 | 21.3734 | 21.325 | 21.1145 | 21.0029 | 20.945
| TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42441 51227 | YES | YES | 0 | 3.9305 | 3.8547 | 3.7589 | 3.6632 | 3.5663 | 3.4305 | 3.3179 | 3.2158 | 3.1211 | 2.6968 | 1.5747 | 1.2558 | 3.8453 | 3.7611 | 3.6547 | 3.5495 | 3.4421 | 3.2905 | 3.1632 | 3.0505 | 2.9453 | 2.4916 | 1.5116 | 1.1453 | 3.8653 | 3.7863 | 3.6821 | 3.5789 | 3.4737 | 3.3253 | 3.2021 | 3.0895 | 2.9874 | 2.5253 | 1.3274 | 0.96842
|  | DERVAIG | EE |  |  |  |  | 3.9716 | 3.9211 | 3.8453 | 3.7853 | 3.6968 | 3.6284 | 3.5358 | 3.4453 | 3.3632 | 4.8389 | 3.7968 | 3.5558 | 3.8895 | 3.8347 | 3.7516 | 3.6874 | 3.5916 | 3.5179 | 3.4126 | 3.3137 | 3.2221 | 5.1579 | 4.24 | 3.9684 | 3.8958 | 3.8537 | 3.7758 | 3.7116 | 3.6168 | 3.5432 | 3.4411 | 3.3432 | 3.2526 | 4.9137 | 3.8032 | 3.5305
|  | DERVAIG | HT |  |  |  |  | 3.9305 | 3.8547 | 3.7589 | 3.6632 | 3.5663 | 3.4305 | 3.3179 | 3.2158 | 3.1211 | 2.6968 | 1.5747 | 1.2558 | 3.8453 | 3.7611 | 3.6547 | 3.5495 | 3.4421 | 3.2905 | 3.1632 | 3.0505 | 2.9453 | 2.4916 | 1.5116 | 1.1453 | 3.8653 | 3.7863 | 3.6821 | 3.5789 | 3.4737 | 3.3253 | 3.2021 | 3.0895 | 2.9874 | 2.5253 | 1.3274 | 0.96842
|  | DERVAIG | HE |  |  |  |  | 4.0263 | 3.9979 | 3.9337 | 3.8916 | 3.8074 | 3.7505 | 3.7105 | 3.6716 | 3.6379 | 3.4516 | 2.9168 | 2.7895 | 3.9526 | 3.9179 | 3.8463 | 3.8021 | 3.7074 | 3.6442 | 3.6011 | 3.5589 | 3.5242 | 3.3284 | 2.8779 | 2.7326 | 3.8653 | 3.7863 | 3.6821 | 3.5789 | 3.4737 | 3.3253 | 3.2021 | 3.0895 | 2.9874 | 2.5253 | 1.3274 | 0.96842
|  | DERVAIG | CF |  |  |  |  | 4.0474 | 4.0358 | 4.0179 | 3.9979 | 3.9716 | 3.9484 | 3.9189 | 3.8905 | 3.8579 | 3.7368 | 3.6074 | 3.5105 | 3.9842 | 3.9642 | 3.94 | 3.9179 | 3.8895 | 3.8632 | 3.8316 | 3.8 | 3.7621 | 3.6284 | 3.4832 | 3.3705 | 3.9653 | 3.9505 | 3.9316 | 3.9158 | 3.8968 | 3.8789 | 3.8547 | 3.8253 | 3.7884 | 3.6579 | 3.5147 | 3.4053
| BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | YES | 0.718 | 13.2646 | 13.1225 | 12.972 | 12.8194 | 12.4152 | 11.9573 | 11.4488 | 10.7857 | 10.1288 | 7.732 | 4.9667 | 1.8962 | 12.5104 | 12.3525 | 12.1841 | 12.0062 | 11.7083 | 11.3683 | 10.7125 | 10.0915 | 9.4831 | 7.7767 | 4.8799 | 2.0494 | 12.7423 | 12.6002 | 12.4507 | 12.2981 | 11.9075 | 11.3296 | 10.6033 | 9.8928 | 9.1949 | 7.1065 | 3.8212 | 0.45805
|  | DINGWALL | EE |  |  |  |  | 13.2646 | 13.1225 | 12.972 | 12.8194 | 12.4152 | 11.9573 | 11.4931 | 10.9509 | 10.2709 | 8.0762 | 4.9667 | 2.0941 | 12.5104 | 12.3767 | 12.2304 | 12.0757 | 11.7978 | 11.5062 | 11.2104 | 10.6136 | 9.9799 | 7.9641 | 5.2273 | 2.0494 | 12.7423 | 12.6002 | 12.4507 | 12.2981 | 11.9075 | 11.4644 | 10.8738 | 10.1665 | 9.437 | 7.1065 | 3.8212 | 0.45805
|  | DINGWALL | HT |  |  |  |  | 13.3815 | 13.2162 | 13.0509 | 12.8836 | 12.4952 | 12.1141 | 11.4488 | 10.7857 | 10.1288 | 8.3678 | 5.6373 | 3.172 | 12.5157 | 12.3525 | 12.1841 | 12.0062 | 11.7083 | 11.3683 | 10.7125 | 10.0915 | 9.4831 | 7.7767 | 4.8799 | 2.1136 | 12.9686 | 12.8054 | 12.6402 | 12.4728 | 12.0959 | 11.3296 | 10.6033 | 9.8928 | 9.1949 | 7.2938 | 4.1802 | 1.3233
|  | DINGWALL | HE |  |  |  |  | 13.5825 | 13.492 | 13.3962 | 13.2931 | 12.8931 | 12.5509 | 12.212 | 11.8794 | 11.5541 | 7.732 | 5.0499 | 1.8962 | 12.7209 | 12.6336 | 12.5367 | 12.4209 | 12.1641 | 11.9452 | 11.7283 | 11.5167 | 11.3136 | 8.2209 | 5.5494 | 2.3125 | 12.9686 | 12.8054 | 12.6402 | 12.4728 | 12.0959 | 11.3296 | 10.6033 | 9.8928 | 9.1949 | 7.2938 | 4.1802 | 1.3233
|  | DINGWALL | CF |  |  |  |  | 13.6562 | 13.6057 | 13.5531 | 13.4994 | 13.3394 | 13.192 | 13.0457 | 12.9131 | 12.8025 | 12.1867 | 10.9625 | 9.0046 | 12.7946 | 12.7462 | 12.6957 | 12.6409 | 12.5325 | 12.4315 | 12.3336 | 12.2388 | 12.1546 | 11.7241 | 10.4799 | 8.3009 | 13.2444 | 13.1938 | 13.1412 | 13.0875 | 12.9328 | 12.7896 | 12.6475 | 12.5191 | 12.4128 | 11.8159 | 10.1265 | 7.7959
| CARRADALE 1 | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 0 | 1.1189 | 1.0937 | 1.0632 | 1.0316 | 0.99684 | 0.96316 | 0.92947 | 0.89474 | 0.85684 | 0.69789 | 0.49474 | 0.31263 | 1.0474 | 1.0189 | 0.98632 | 0.95158 | 0.91684 | 0.88211 | 0.84737 | 0.81368 | 0.77474 | 0.60947 | 0.38842 | 0.18105 | 1.0326 | 1.0042 | 0.97053 | 0.93684 | 0.9 | 0.86316 | 0.82737 | 0.79158 | 0.75053 | 0.57789 | 0.35368 | 0.14737
|  | DIPPEN | EE |  |  |  |  | 1.1326 | 1.1158 | 1.0947 | 1.0705 | 1.04 | 1.0021 | 0.97053 | 0.94 | 0.91263 | 0.75684 | 0.57684 | 0.37474 | 1.0653 | 1.0442 | 1.0211 | 0.99579 | 0.96421 | 0.92632 | 0.89474 | 0.86421 | 0.83684 | 0.68211 | 0.49789 | 0.27368 | 1.0505 | 1.0295 | 1.0053 | 0.98 | 0.94737 | 0.90526 | 0.87368 | 0.84105 | 0.81158 | 0.64421 | 0.44737 | 0.22105
|  | DIPPEN | HT |  |  |  |  | 1.1189 | 1.0937 | 1.0632 | 1.0316 | 0.99684 | 0.96316 | 0.92947 | 0.89474 | 0.85684 | 0.69789 | 0.49474 | 0.31263 | 1.0474 | 1.0189 | 0.98632 | 0.95158 | 0.91684 | 0.88211 | 0.84737 | 0.81368 | 0.77474 | 0.60947 | 0.38842 | 0.18105 | 1.0326 | 1.0042 | 0.97053 | 0.93684 | 0.9 | 0.86316 | 0.82737 | 0.79158 | 0.75053 | 0.57789 | 0.35368 | 0.14737
|  | DIPPEN | HE |  |  |  |  | 1.1442 | 1.1368 | 1.1274 | 1.1074 | 1.0768 | 1.0474 | 1.0232 | 0.99579 | 0.96737 | 0.85684 | 0.69368 | 0.50211 | 1.0811 | 1.0737 | 1.0558 | 1.0337 | 1.0021 | 0.97263 | 0.94842 | 0.92105 | 0.89158 | 0.78105 | 0.60737 | 0.40105 | 1.0326 | 1.0042 | 0.97053 | 0.93684 | 0.9 | 0.86316 | 0.82737 | 0.79158 | 0.75053 | 0.57789 | 0.35368 | 0.14737
|  | DIPPEN | CF |  |  |  |  | 1.1516 | 1.1474 | 1.1442 | 1.14 | 1.1326 | 1.1263 | 1.1158 | 1.1074 | 1.0958 | 1.0137 | 0.89684 | 0.76316 | 1.0884 | 1.0842 | 1.0811 | 1.0768 | 1.0705 | 1.0589 | 1.0474 | 1.0379 | 1.0253 | 0.93789 | 0.81368 | 0.66526 | 1.0884 | 1.0811 | 1.0758 | 1.0684 | 1.0568 | 1.0432 | 1.0295 | 1.0211 | 1.0074 | 0.91684 | 0.78737 | 0.63474
| BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | YES | 0.05 | 5.1826 | 5.0879 | 4.9742 | 4.8574 | 4.5405 | 4.2079 | 3.9858 | 3.7384 | 3.4953 | 2.4226 | 1.2405 | 0.31947 | 4.4995 | 4.3784 | 4.2605 | 4.1426 | 3.8511 | 3.5416 | 3.3416 | 3.1226 | 2.9058 | 2.0111 | 0.99526 | 0.13421 | 4.3689 | 4.2458 | 4.1237 | 4.0026 | 3.6911 | 3.3637 | 3.1468 | 2.9111 | 2.6774 | 1.6732 | 0.46368 | -0.54895
|  | DORNOCH | EE |  |  |  |  | 5.2216 | 5.1574 | 5.0837 | 4.9868 | 4.7637 | 4.5195 | 4.1721 | 3.8311 | 3.6016 | 2.4226 | 1.2405 | 0.31947 | 4.5763 | 4.4774 | 4.3784 | 4.2795 | 4.0742 | 3.8532 | 3.5426 | 3.2363 | 3.0353 | 2.0111 | 0.99526 | 0.13421 | 4.4489 | 4.3468 | 4.2437 | 4.1416 | 3.9205 | 3.6784 | 3.3447 | 3.0142 | 2.7953 | 1.6732 | 0.46368 | -0.54895
|  | DORNOCH | HT |  |  |  |  | 5.1826 | 5.0879 | 4.9742 | 4.8574 | 4.5405 | 4.2079 | 3.9858 | 3.7384 | 3.4953 | 2.5037 | 1.6795 | 0.92579 | 4.4995 | 4.3784 | 4.2605 | 4.1426 | 3.8511 | 3.5416 | 3.3416 | 3.1226 | 2.9058 | 2.0237 | 1.2679 | 0.45842 | 4.3689 | 4.2458 | 4.1237 | 4.0026 | 3.6911 | 3.3637 | 3.1468 | 2.9111 | 2.6774 | 1.7237 | 0.85526 | 0.01
|  | DORNOCH | HE |  |  |  |  | 5.2763 | 5.2384 | 5.1953 | 5.1521 | 4.9784 | 4.8153 | 4.6026 | 4.3921 | 4.1742 | 3.3395 | 2.3037 | 1.1932 | 4.6795 | 4.6237 | 4.5626 | 4.5005 | 4.3111 | 4.1532 | 3.9532 | 3.7595 | 3.5668 | 2.8426 | 1.9258 | 0.93947 | 4.3689 | 4.2458 | 4.1237 | 4.0026 | 3.6911 | 3.3637 | 3.1468 | 2.9111 | 2.6774 | 1.7237 | 0.85526 | 0.01
|  | DORNOCH | CF |  |  |  |  | 5.3111 | 5.2911 | 5.2689 | 5.2479 | 5.1795 | 5.1174 | 5.0542 | 4.99 | 4.9079 | 4.4616 | 3.85 | 3.2016 | 4.7153 | 4.6953 | 4.6668 | 4.6342 | 4.5532 | 4.4795 | 4.4047 | 4.3153 | 4.2332 | 3.8205 | 3.2795 | 2.6942 | 4.6174 | 4.5805 | 4.5447 | 4.5079 | 4.4205 | 4.3405 | 4.2595 | 4.1626 | 4.0763 | 3.6311 | 3.0416 | 2.41
| CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 0 | 1.0416 | 1.0184 | 0.98684 | 0.95421 | 0.92158 | 0.88895 | 0.85842 | 0.82895 | 0.79947 | 0.67211 | 0.56053 | 0.45737 | 1.0416 | 1.0174 | 0.98158 | 0.94579 | 0.91105 | 0.87526 | 0.84158 | 0.80895 | 0.77632 | 0.63316 | 0.50684 | 0.38789 | 1.0521 | 1.0279 | 0.99316 | 0.95842 | 0.92368 | 0.88789 | 0.85526 | 0.82368 | 0.79105 | 0.65211 | 0.52789 | 0.41211
|  | DOUGLAS PIER | EE |  |  |  |  | 1.0574 | 1.0395 | 1.0205 | 0.99737 | 0.97211 | 0.94789 | 0.92368 | 0.89947 | 0.87842 | 0.77526 | 0.69105 | 0.61421 | 1.0595 | 1.0395 | 1.0205 | 0.99526 | 0.96684 | 0.93947 | 0.91421 | 0.88684 | 0.86263 | 0.74895 | 0.65316 | 0.56368 | 1.0679 | 1.05 | 1.0311 | 1.0058 | 0.97842 | 0.95211 | 0.92684 | 0.90053 | 0.87632 | 0.76474 | 0.67105 | 0.58474
|  | DOUGLAS PIER | HT |  |  |  |  | 1.0416 | 1.0184 | 0.98684 | 0.95421 | 0.92158 | 0.88895 | 0.85842 | 0.82895 | 0.79947 | 0.67211 | 0.56053 | 0.45737 | 1.0416 | 1.0174 | 0.98158 | 0.94579 | 0.91105 | 0.87526 | 0.84158 | 0.80895 | 0.77632 | 0.63316 | 0.50684 | 0.38789 | 1.0521 | 1.0279 | 0.99316 | 0.95842 | 0.92368 | 0.88789 | 0.85526 | 0.82368 | 0.79105 | 0.65211 | 0.52789 | 0.41211
|  | DOUGLAS PIER | HE |  |  |  |  | 1.0784 | 1.0668 | 1.0553 | 1.0437 | 1.0321 | 1.0205 | 1.0079 | 0.99211 | 0.97842 | 0.91947 | 0.87316 | 0.83211 | 1.0805 | 1.0689 | 1.0574 | 1.0447 | 1.0332 | 1.0216 | 1.0068 | 0.99105 | 0.97526 | 0.91 | 0.85632 | 0.80895 | 1.0521 | 1.0279 | 0.99316 | 0.95842 | 0.92368 | 0.88789 | 0.85526 | 0.82368 | 0.79105 | 0.65211 | 0.52789 | 0.41211
|  | DOUGLAS PIER | CF |  |  |  |  | 1.0911 | 1.0837 | 1.0763 | 1.0711 | 1.0637 | 1.0563 | 1.05 | 1.0437 | 1.0363 | 0.99316 | 0.95632 | 0.92579 | 1.0932 | 1.0858 | 1.0784 | 1.0721 | 1.0647 | 1.0574 | 1.0511 | 1.0447 | 1.0363 | 0.99 | 0.94789 | 0.91105 | 1.0995 | 1.0921 | 1.0847 | 1.0795 | 1.0732 | 1.0658 | 1.0605 | 1.0542 | 1.0468 | 1.0016 | 0.95947 | 0.92474
| ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 0 | 2.4316 | 2.4074 | 2.3821 | 2.3579 | 2.3326 | 2.3095 | 2.2863 | 2.2642 | 2.2421 | 2.1589 | 1.7958 | 1.7368 | 2.6358 | 2.6095 | 2.5832 | 2.5558 | 2.5295 | 2.5053 | 2.48 | 2.4558 | 2.4337 | 2.3432 | 2.0442 | 1.9779 | 2.4253 | 2.3989 | 2.3726 | 2.3463 | 2.3189 | 2.2947 | 2.2695 | 2.2463 | 2.2232 | 2.1326 | 1.7632 | 1.6968
|  | DRIMORE | EE |  |  |  |  | 2.4474 | 2.4274 | 2.4074 | 2.3863 | 2.3674 | 2.3474 | 2.3284 | 2.3116 | 2.2947 | 2.2221 | 1.8747 | 1.8326 | 2.6537 | 2.6316 | 2.6095 | 2.5884 | 2.5674 | 2.5463 | 2.5263 | 2.5074 | 2.4895 | 2.4126 | 2.1337 | 2.0842 | 2.4421 | 2.4211 | 2.4 | 2.3779 | 2.3568 | 2.3358 | 2.3168 | 2.2979 | 2.28 | 2.2021 | 1.8495 | 1.8021
|  | DRIMORE | HT |  |  |  |  | 2.4316 | 2.4074 | 2.3821 | 2.3579 | 2.3326 | 2.3095 | 2.2863 | 2.2642 | 2.2421 | 2.1589 | 1.7958 | 1.7368 | 2.6358 | 2.6095 | 2.5832 | 2.5558 | 2.5295 | 2.5053 | 2.48 | 2.4558 | 2.4337 | 2.3432 | 2.0442 | 1.9779 | 2.4253 | 2.3989 | 2.3726 | 2.3463 | 2.3189 | 2.2947 | 2.2695 | 2.2463 | 2.2232 | 2.1326 | 1.7632 | 1.6968
|  | DRIMORE | HE |  |  |  |  | 2.4716 | 2.4579 | 2.4442 | 2.4305 | 2.4168 | 2.4032 | 2.3916 | 2.3789 | 2.3674 | 2.3263 | 2.1537 | 2.1347 | 2.68 | 2.6642 | 2.6505 | 2.6358 | 2.6221 | 2.6074 | 2.5947 | 2.5821 | 2.5695 | 2.5263 | 2.3863 | 2.3642 | 2.4253 | 2.3989 | 2.3726 | 2.3463 | 2.3189 | 2.2947 | 2.2695 | 2.2463 | 2.2232 | 2.1326 | 1.7632 | 1.6968
|  | DRIMORE | CF |  |  |  |  | 2.4842 | 2.4768 | 2.4695 | 2.4611 | 2.4537 | 2.4453 | 2.4379 | 2.4295 | 2.4221 | 2.3874 | 2.3632 | 2.3463 | 2.6937 | 2.6853 | 2.6768 | 2.6674 | 2.66 | 2.6505 | 2.6432 | 2.6337 | 2.6263 | 2.5884 | 2.5632 | 2.5432 | 2.48 | 2.4726 | 2.4642 | 2.4558 | 2.4484 | 2.44 | 2.4326 | 2.4232 | 2.4158 | 2.3789 | 2.3526 | 2.3326
| CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | NO | 0 | 5.4411 | 5.3379 | 5.2347 | 5.1347 | 4.8495 | 4.4884 | 4.1158 | 3.7874 | 3.4526 | 1.2326 | -2.4821 | -4.4421 | 5.5316 | 5.4274 | 5.3242 | 5.2232 | 4.9895 | 4.7516 | 4.4526 | 4.1853 | 3.9158 | 1.94 | -1.3589 | -3.2326 | 5.5 | 5.3905 | 5.28 | 5.1737 | 4.8832 | 4.52 | 4.1432 | 3.8053 | 3.4642 | 1.1189 | -1.3053 | -3.1779
|  | DRUMNADROCHIT | EE |  |  |  |  | 5.4842 | 5.3779 | 5.2726 | 5.1632 | 4.8495 | 4.4884 | 4.1158 | 3.7874 | 3.4526 | 1.2326 | -1.0126 | -2.68 | 5.5863 | 5.4884 | 5.3926 | 5.2905 | 5.0442 | 4.7516 | 4.4526 | 4.1853 | 3.9158 | 1.94 | -0.16947 | -1.8968 | 5.5474 | 5.4337 | 5.32 | 5.2042 | 4.8832 | 4.52 | 4.1432 | 3.8053 | 3.4642 | 1.1189 | -1.3053 | -3.1779
|  | DRUMNADROCHIT | HT |  |  |  |  | 5.4411 | 5.3379 | 5.2347 | 5.1347 | 4.8589 | 4.5832 | 4.3053 | 3.9863 | 3.6758 | 1.7979 | -0.085263 | -1.3958 | 5.5316 | 5.4274 | 5.3242 | 5.2232 | 4.9895 | 4.7516 | 4.5137 | 4.2474 | 3.9874 | 2.1863 | 0.19368 | -1.2147 | 5.5 | 5.3905 | 5.28 | 5.1737 | 4.8905 | 4.6095 | 4.3263 | 4.0053 | 3.6905 | 1.6653 | -0.45895 | -1.9474
|  | DRUMNADROCHIT | HE |  |  |  |  | 5.5789 | 5.5274 | 5.4737 | 5.42 | 5.1189 | 4.8642 | 4.5695 | 4.2747 | 3.9011 | 2.2821 | -2.4821 | -4.4421 | 5.6811 | 5.6305 | 5.5779 | 5.5242 | 5.2863 | 5.0779 | 4.8253 | 4.5716 | 4.2211 | 2.74 | -1.3589 | -3.2326 | 5.5 | 5.3905 | 5.28 | 5.1737 | 4.8905 | 4.6095 | 4.3263 | 4.0053 | 3.6905 | 1.6653 | -0.45895 | -1.9474
|  | DRUMNADROCHIT | CF |  |  |  |  | 5.6263 | 5.5979 | 5.5684 | 5.5389 | 5.4211 | 5.3126 | 5.2053 | 5.0737 | 4.9137 | 4.1221 | 0.75474 | -0.38632 | 5.7305 | 5.7011 | 5.6695 | 5.6411 | 5.5432 | 5.4526 | 5.3632 | 5.2379 | 5.0726 | 4.3084 | 1.4579 | 0.29053 | 5.6642 | 5.6453 | 5.6253 | 5.6074 | 5.4884 | 5.3779 | 5.2705 | 5.1295 | 4.9516 | 4.0979 | 0.63053 | -0.63895
| GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | NO | 0 | 0.21158 | 0.20421 | 0.19789 | 0.19263 | 0.18632 | 0.17895 | 0.17263 | 0.16526 | 0.15789 | 0.13053 | 0.10632 | 0.085263 | 0.19263 | 0.18421 | 0.17789 | 0.17158 | 0.16421 | 0.15684 | 0.15053 | 0.14211 | 0.13474 | 0.10421 | 0.077895 | 0.053684 | 0.19789 | 0.19053 | 0.18421 | 0.17789 | 0.17158 | 0.16421 | 0.15684 | 0.14947 | 0.14211 | 0.11158 | 0.085263 | 0.062105
|  | DRUMRUNIE | EE |  |  |  |  | 0.21474 | 0.21053 | 0.20632 | 0.20105 | 0.19579 | 0.19158 | 0.18526 | 0.18105 | 0.17579 | 0.15263 | 0.13579 | 0.11895 | 0.19684 | 0.19158 | 0.18632 | 0.18 | 0.17579 | 0.17053 | 0.16421 | 0.16 | 0.15368 | 0.12842 | 0.10947 | 0.090526 | 0.20316 | 0.19684 | 0.19263 | 0.18632 | 0.18211 | 0.17684 | 0.17158 | 0.16632 | 0.16105 | 0.13579 | 0.11684 | 0.097895
|  | DRUMRUNIE | HT |  |  |  |  | 0.21158 | 0.20421 | 0.19789 | 0.19263 | 0.18632 | 0.17895 | 0.17263 | 0.16526 | 0.15789 | 0.13053 | 0.10632 | 0.085263 | 0.19263 | 0.18421 | 0.17789 | 0.17158 | 0.16421 | 0.15684 | 0.15053 | 0.14211 | 0.13474 | 0.10421 | 0.077895 | 0.053684 | 0.19789 | 0.19053 | 0.18421 | 0.17789 | 0.17158 | 0.16421 | 0.15684 | 0.14947 | 0.14211 | 0.11158 | 0.085263 | 0.062105
|  | DRUMRUNIE | HE |  |  |  |  | 0.21789 | 0.21579 | 0.21368 | 0.21158 | 0.20842 | 0.20526 | 0.20211 | 0.19895 | 0.19579 | 0.18526 | 0.17474 | 0.16737 | 0.20421 | 0.2 | 0.19684 | 0.19263 | 0.18947 | 0.18632 | 0.18316 | 0.17895 | 0.17579 | 0.16421 | 0.15263 | 0.14421 | 0.19789 | 0.19053 | 0.18421 | 0.17789 | 0.17158 | 0.16421 | 0.15684 | 0.14947 | 0.14211 | 0.11158 | 0.085263 | 0.062105
|  | DRUMRUNIE | CF |  |  |  |  | 0.22 | 0.21895 | 0.21789 | 0.21684 | 0.21579 | 0.21368 | 0.21263 | 0.21158 | 0.20947 | 0.20211 | 0.19684 | 0.18947 | 0.20632 | 0.20526 | 0.20316 | 0.20105 | 0.19895 | 0.19579 | 0.19368 | 0.19263 | 0.19053 | 0.18211 | 0.17579 | 0.16842 | 0.21158 | 0.21053 | 0.20842 | 0.20632 | 0.20526 | 0.20211 | 0.2 | 0.19789 | 0.19579 | 0.18842 | 0.18211 | 0.17474
| STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | 0 | 0.78632 | 0.69579 | 0.58947 | 0.47263 | 0.32526 | 0.17368 | 0.021053 | -0.13579 | -0.27684 | -0.97263 | -1.5695 | -2.0768 | 0.83579 | 0.73684 | 0.61895 | 0.48842 | 0.33263 | 0.17053 | 0.0063158 | -0.1579 | -0.2979 | -1.0495 | -1.7105 | -2.2905 | 0.86211 | 0.75895 | 0.64 | 0.50842 | 0.34632 | 0.17895 | 0.0073684 | -0.16632 | -0.31263 | -1.0989 | -1.7832 | -2.3758
|  | DRYMEN | EE |  |  |  |  | 0.82947 | 0.74947 | 0.65579 | 0.54737 | 0.40737 | 0.26947 | 0.11895 | -0.02 | -0.1579 | -0.84526 | -1.4853 | -1.9495 | 0.88421 | 0.80316 | 0.70211 | 0.58632 | 0.44316 | 0.30526 | 0.15368 | 0.012632 | -0.12842 | -0.82 | -1.4695 | -1.9737 | 0.90842 | 0.81895 | 0.71474 | 0.59263 | 0.43789 | 0.28632 | 0.12316 | -0.031579 | -0.18421 | -0.9379 | -1.6505 | -2.1874
|  | DRYMEN | HT |  |  |  |  | 0.78632 | 0.69579 | 0.58947 | 0.47263 | 0.32526 | 0.17368 | 0.021053 | -0.13579 | -0.27684 | -0.97263 | -1.5695 | -2.0768 | 0.83579 | 0.73684 | 0.61895 | 0.48842 | 0.33263 | 0.17053 | 0.0063158 | -0.1579 | -0.2979 | -1.0495 | -1.7105 | -2.2905 | 0.86211 | 0.75895 | 0.64 | 0.50842 | 0.34632 | 0.17895 | 0.0073684 | -0.16632 | -0.31263 | -1.0989 | -1.7832 | -2.3758
|  | DRYMEN | HE |  |  |  |  | 0.89895 | 0.84632 | 0.77789 | 0.69684 | 0.57474 | 0.46842 | 0.34421 | 0.23158 | 0.11789 | -0.41895 | -0.91368 | -1.3705 | 0.93789 | 0.9 | 0.82632 | 0.73579 | 0.61158 | 0.50105 | 0.37263 | 0.25368 | 0.13474 | -0.43263 | -0.96632 | -1.4463 | 0.86211 | 0.75895 | 0.64 | 0.50842 | 0.34632 | 0.17895 | 0.0073684 | -0.16632 | -0.31263 | -1.0989 | -1.7832 | -2.3758
|  | DRYMEN | CF |  |  |  |  | 0.93895 | 0.91053 | 0.87684 | 0.84 | 0.78737 | 0.73579 | 0.68 | 0.62421 | 0.56737 | 0.26 | -0.035789 | -0.28526 | 0.96842 | 0.94842 | 0.92737 | 0.89263 | 0.83895 | 0.78316 | 0.72421 | 0.66316 | 0.60105 | 0.26632 | -0.051579 | -0.32526 | 1.0284 | 0.99684 | 0.96 | 0.91789 | 0.86 | 0.80105 | 0.74105 | 0.67789 | 0.61368 | 0.26526 | -0.069474 | -0.35579
| DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | YES | 1.2 | 1.2011 | 1.1495 | 1.0716 | 0.99474 | 0.71263 | 0.36211 | -0.024211 | -0.36105 | -0.71053 | -4.0116 | -7.7063 | -10.5063 | 1.2368 | 1.1558 | 1.0758 | 0.99789 | 0.74947 | 0.48737 | 0.16211 | -0.12316 | -0.45684 | -3.6653 | -7.2926 | -10.3284 | 1.2 | 1.1158 | 1.0326 | 0.95158 | 0.66842 | 0.33368 | -0.064211 | -0.4179 | -0.76842 | -4.4011 | -8.4316 | -11.6316
|  | DRYNOCH | EE |  |  |  |  | 1.2242 | 1.1726 | 1.1211 | 1.0526 | 0.73474 | 0.36211 | -0.024211 | -0.36105 | -0.71053 | -4.0116 | -7.7063 | -10.5063 | 1.2632 | 1.2147 | 1.1421 | 1.0695 | 0.8 | 0.48737 | 0.16211 | -0.12316 | -0.40842 | -3.6653 | -7.2926 | -10.3284 | 1.2484 | 1.1705 | 1.0937 | 1.0158 | 0.70316 | 0.33368 | -0.064211 | -0.4179 | -0.76842 | -4.4011 | -8.4316 | -11.6316
|  | DRYNOCH | HT |  |  |  |  | 1.2011 | 1.1495 | 1.0716 | 0.99474 | 0.71263 | 0.42737 | 0.14211 | -0.18526 | -0.48105 | -3.4579 | -6.8611 | -9.1747 | 1.2368 | 1.1558 | 1.0758 | 0.99789 | 0.74947 | 0.50211 | 0.25368 | -0.027368 | -0.38 | -3.4579 | -7.1453 | -9.7463 | 1.2 | 1.1158 | 1.0326 | 0.95158 | 0.66842 | 0.38421 | 0.098947 | -0.23895 | -0.59368 | -3.9495 | -7.8179 | -10.481
|  | DRYNOCH | HE |  |  |  |  | 1.2568 | 1.2326 | 1.2053 | 1.1789 | 0.87789 | 0.50105 | 0.11895 | -0.004211 | -0.52947 | -2.5589 | -5.4105 | -8.5116 | 1.3 | 1.2768 | 1.2495 | 1.2242 | 0.94526 | 0.59053 | 0.22737 | 0.081053 | -0.45684 | -2.5011 | -5.3947 | -8.5621 | 1.2 | 1.1158 | 1.0326 | 0.95158 | 0.66842 | 0.38421 | 0.098947 | -0.23895 | -0.59368 | -3.9495 | -7.8179 | -10.481
|  | DRYNOCH | CF |  |  |  |  | 1.2768 | 1.2632 | 1.2505 | 1.2368 | 1.1284 | 1.0316 | 0.88 | 0.73368 | 0.48316 | -0.58842 | -2.3674 | -4.3516 | 1.3221 | 1.3095 | 1.2968 | 1.2832 | 1.2158 | 1.1189 | 0.93684 | 0.76105 | 0.47895 | -0.66632 | -2.5 | -4.6305 | 1.3021 | 1.2884 | 1.2758 | 1.2611 | 1.1568 | 1.0432 | 0.84632 | 0.67158 | 0.38316 | -0.84632 | -2.8453 | -5.0937
| KEITH 2 | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 0 | 6.0779 | 6.0011 | 5.8232 | 15.1763 | 14.5184 | 13.5911 | 12.7111 | 11.9542 | 11.1847 | 2.7784 | -4.4858 | -9.7184 | 5.6789 | 5.6147 | 5.4432 | 14.0305 | 13.4589 | 12.72 | 11.9884 | 11.3589 | 10.72 | 3.0389 | -4.0432 | -9.5663 | 6.02 | 5.8895 | 5.7537 | 14.7076 | 14.0329 | 13.1129 | 12.2287 | 11.4687 | 10.695 | 1.7603 | -6.2587 | -12.185
|  | DUFFTOWN | EE |  |  |  |  | 6.1074 | 6.0253 | 5.9358 | 15.3111 | 14.5332 | 13.5911 | 12.7111 | 11.9542 | 11.1847 | 2.7784 | -4.4858 | -9.7184 | 5.7084 | 5.6474 | 5.5789 | 14.2011 | 13.5347 | 12.72 | 11.9884 | 11.3589 | 10.72 | 3.0389 | -4.0432 | -9.5663 | 6.0653 | 5.9505 | 5.8242 | 14.8624 | 14.0813 | 13.1129 | 12.2287 | 11.4687 | 10.695 | 1.7603 | -6.2587 | -12.185
|  | DUFFTOWN | HT |  |  |  |  | 6.0779 | 6.0011 | 5.8232 | 15.1763 | 14.5184 | 13.8616 | 13.2289 | 12.4932 | 11.6058 | 3.7784 | -2.5321 | -6.8279 | 5.6789 | 5.6147 | 5.4432 | 14.0305 | 13.4589 | 12.8895 | 12.3484 | 11.7305 | 10.9368 | 3.4421 | -3.3 | -8.0337 | 6.02 | 5.8895 | 5.7537 | 14.7076 | 14.0329 | 13.3603 | 12.7171 | 11.975 | 11.0466 | 2.5045 | -4.6618 | -9.5934
|  | DUFFTOWN | HE |  |  |  |  | 6.1484 | 6.1137 | 6.0737 | 15.5426 | 14.7289 | 14.0005 | 13.3016 | 12.5247 | 11.4605 | 5.8342 | 0.34895 | -5.7068 | 5.7495 | 5.7179 | 5.6821 | 14.4179 | 13.7253 | 13.0874 | 12.4832 | 11.7842 | 10.7421 | 5.5063 | 0.0063158 | -6.0621 | 6.02 | 5.8895 | 5.7537 | 14.7076 | 14.0329 | 13.3603 | 12.7171 | 11.975 | 11.0466 | 2.5045 | -4.6618 | -9.5934
|  | DUFFTOWN | CF |  |  |  |  | 6.1758 | 6.1537 | 6.1326 | 15.6595 | 15.4216 | 15.2142 | 14.8826 | 14.4374 | 13.9605 | 11.6795 | 8.2658 | 4.4774 | 5.7768 | 5.7579 | 5.74 | 14.52 | 14.3968 | 14.1947 | 13.8937 | 13.4453 | 12.9305 | 10.6358 | 7.1379 | 3.1621 | 6.1663 | 6.1347 | 6.1042 | 15.2424 | 14.9697 | 14.7213 | 14.4424 | 13.9624 | 13.4045 | 10.8466 | 6.9897 | 2.7392
| BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 0.16 | 14.5861 | 14.2103 | 13.7092 | 13.1082 | 12.0629 | 11.405 | 10.3218 | 9.1829 | 8.0303 | 2.8945 | -2.4034 | -5.6803 | 12.4358 | 11.9789 | 11.4158 | 10.78 | 9.7789 | 9.1063 | 8.0379 | 6.9116 | 5.7695 | 0.57895 | -3.9221 | -7.3463 | 13.3283 | 12.8704 | 12.3093 | 11.6557 | 10.5178 | 9.7736 | 8.5862 | 7.3451 | 6.0893 | 0.45461 | -5.0507 | -8.7064
|  | DUNBLANE | EE |  |  |  |  | 14.7155 | 14.4482 | 14.0566 | 13.5397 | 12.5239 | 12.0092 | 10.8492 | 9.7945 | 8.7282 | 3.0997 | -2.4034 | -5.6803 | 12.6589 | 12.2758 | 11.7968 | 11.2516 | 10.2947 | 9.7568 | 8.6726 | 7.68 | 6.6779 | 1.2874 | -3.9221 | -7.3295 | 13.5472 | 13.1578 | 12.6714 | 12.123 | 11.0514 | 10.4536 | 9.1999 | 8.0546 | 6.8978 | 0.84934 | -5.0507 | -8.7064
|  | DUNBLANE | HT |  |  |  |  | 14.5861 | 14.2103 | 13.7092 | 13.1082 | 12.0629 | 11.405 | 10.3218 | 9.1829 | 8.0303 | 2.8945 | -1.2655 | -4.5087 | 12.4358 | 11.9789 | 11.4158 | 10.78 | 9.7789 | 9.1063 | 8.0379 | 6.9116 | 5.7695 | 0.57895 | -3.7716 | -7.3463 | 13.3283 | 12.8704 | 12.3093 | 11.6557 | 10.5178 | 9.7736 | 8.5862 | 7.3451 | 6.0893 | 0.45461 | -4.1696 | -7.8559
|  | DUNBLANE | HE |  |  |  |  | 14.8534 | 14.7534 | 14.5018 | 14.1418 | 13.1671 | 12.7408 | 11.8176 | 10.9124 | 10.0029 | 5.5976 | 1.5366 | -2.5013 | 12.9379 | 12.6684 | 12.2979 | 11.8579 | 10.9495 | 10.4863 | 9.6063 | 8.7505 | 7.8905 | 3.5884 | -0.40737 | -4.3337 | 13.3283 | 12.8704 | 12.3093 | 11.6557 | 10.5178 | 9.7736 | 8.5862 | 7.3451 | 6.0893 | 0.45461 | -4.1696 | -7.8559
|  | DUNBLANE | CF |  |  |  |  | 14.9397 | 14.8818 | 14.825 | 14.7397 | 14.3797 | 14.2092 | 13.8282 | 13.4397 | 13.0776 | 10.8576 | 8.4608 | 5.8239 | 13.1211 | 12.9747 | 12.7926 | 12.5926 | 12.22 | 11.9968 | 11.6126 | 11.2305 | 10.8642 | 8.6874 | 6.3505 | 3.5968 | 13.9767 | 13.863 | 13.6799 | 13.482 | 13.0725 | 12.8514 | 12.4378 | 12.0314 | 11.6483 | 9.1693 | 6.5314 | 3.5799
| DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 0 | 19.3737 | 19.1211 | 18.8568 | 18.5642 | 18.2558 | 17.9516 | 17.6558 | 17.4463 | 17.2421 | 16.4432 | 15.7705 | 15.1779 | 18.6611 | 18.4547 | 18.2284 | 17.9453 | 17.6453 | 17.3505 | 17.0642 | 16.8589 | 16.6589 | 15.8811 | 15.2305 | 14.6316 | 18.9042 | 18.7789 | 18.6505 | 18.5105 | 18.2463 | 17.9189 | 17.6 | 17.3779 | 17.1621 | 16.3095 | 15.5832 | 14.9358
|  | DUNOON | EE |  |  |  |  | 19.5232 | 19.3158 | 19.0989 | 18.8516 | 18.5884 | 18.3316 | 18.08 | 17.9137 | 17.7547 | 17.0674 | 16.5632 | 16.1358 | 18.7811 | 18.6126 | 18.4368 | 18.2232 | 17.9684 | 17.72 | 17.4768 | 17.3137 | 17.1579 | 16.4874 | 16.0011 | 15.5884 | 18.9747 | 18.8726 | 18.7653 | 18.6537 | 18.5305 | 18.3253 | 18.0537 | 17.8779 | 17.7095 | 16.9811 | 16.4368 | 15.9695
|  | DUNOON | HT |  |  |  |  | 19.3737 | 19.1211 | 18.8568 | 18.5642 | 18.2558 | 17.9516 | 17.6558 | 17.4463 | 17.2421 | 16.4432 | 15.7705 | 15.1779 | 18.6611 | 18.4547 | 18.2284 | 17.9453 | 17.6453 | 17.3505 | 17.0642 | 16.8589 | 16.6589 | 15.8811 | 15.2305 | 14.6316 | 18.9042 | 18.7789 | 18.6505 | 18.5105 | 18.2463 | 17.9189 | 17.6 | 17.3779 | 17.1621 | 16.3095 | 15.5832 | 14.9358
|  | DUNOON | HE |  |  |  |  | 19.6526 | 19.5684 | 19.4063 | 19.2084 | 18.9947 | 18.7842 | 18.5832 | 18.4674 | 18.36 | 17.9737 | 17.7095 | 17.5116 | 18.9358 | 18.8147 | 18.6821 | 18.5253 | 18.3558 | 18.16 | 17.9653 | 17.8505 | 17.7453 | 17.3674 | 17.1116 | 16.9211 | 18.9042 | 18.7789 | 18.6505 | 18.5105 | 18.2463 | 17.9189 | 17.6 | 17.3779 | 17.1621 | 16.3095 | 15.5832 | 14.9358
|  | DUNOON | CF |  |  |  |  | 19.7116 | 19.6674 | 19.6211 | 19.5421 | 19.4326 | 19.3179 | 19.1947 | 19.1126 | 19.0295 | 18.6674 | 18.4253 | 18.2463 | 19.0305 | 18.9579 | 18.8821 | 18.7968 | 18.7105 | 18.62 | 18.5242 | 18.4547 | 18.3842 | 18.0432 | 17.8095 | 17.6368 | 19.1221 | 19.0779 | 19.0316 | 18.9842 | 18.9368 | 18.8884 | 18.84 | 18.7916 | 18.7432 | 18.5337 | 18.4211 | 18.2347
| DUNVEGAN | DUNVEGAN | MINIMUM HEADROOM | NG 27646 47150 | YES | YES | 0 | 3.7274 | 2.9032 | 2.8263 | 2.7411 | 2.6558 | 2.5747 | 2.4905 | 2.2789 | 1.8989 | -3.8305 | -7.2368 | -9.5947 | 3.5579 | 2.9126 | 2.8253 | 2.7368 | 2.6505 | 2.5684 | 2.4832 | 2.2421 | 1.8453 | -3.4158 | -7.1516 | -9.7811 | 3.5611 | 2.7053 | 2.6189 | 2.5305 | 2.4411 | 2.3558 | 2.2663 | 2.0368 | 1.6063 | -4.5032 | -8.3695 | -11.0779
|  | DUNVEGAN | EE |  |  |  |  | 3.7758 | 2.9032 | 2.8263 | 2.7411 | 2.6558 | 2.5747 | 2.4905 | 2.4042 | 2.0579 | -0.91158 | -4.64 | -7.4758 | 3.5905 | 2.9126 | 2.8253 | 2.7368 | 2.6505 | 2.5684 | 2.4832 | 2.3968 | 2.1021 | -0.89053 | -4.5811 | -7.6747 | 3.6158 | 2.7053 | 2.6189 | 2.5305 | 2.4411 | 2.3558 | 2.2663 | 2.1747 | 1.8116 | -1.4789 | -5.5474 | -8.7716
|  | DUNVEGAN | HT |  |  |  |  | 3.7274 | 3.6316 | 3.5347 | 3.4411 | 3.1389 | 2.8389 | 2.7589 | 2.2789 | 1.8989 | -3.8305 | -7.2368 | -9.5947 | 3.5579 | 3.4579 | 3.3558 | 3.2579 | 2.9958 | 2.7358 | 2.6474 | 2.2421 | 1.8453 | -3.4158 | -7.1516 | -9.7811 | 3.5611 | 3.4558 | 3.3526 | 3.2516 | 2.94 | 2.6242 | 2.5379 | 2.0368 | 1.6063 | -4.5032 | -8.3695 | -11.0779
|  | DUNVEGAN | HE |  |  |  |  | 3.84 | 3.8011 | 3.7589 | 3.7168 | 3.3926 | 3.0116 | 2.8621 | 2.4916 | 1.9579 | -1.7905 | -4.6495 | -7.7579 | 3.6337 | 3.6063 | 3.5747 | 3.5421 | 3.2947 | 2.9358 | 2.76 | 2.4116 | 1.8642 | -1.5389 | -4.4695 | -7.6716 | 3.5611 | 3.4558 | 3.3526 | 3.2516 | 2.94 | 2.6242 | 2.5379 | 2.0368 | 1.6063 | -4.5032 | -8.3695 | -11.0779
|  | DUNVEGAN | CF |  |  |  |  | 3.8758 | 3.8537 | 3.8305 | 3.8084 | 3.6863 | 3.5758 | 3.5 | 3.3484 | 3.0926 | 0.26211 | -1.5421 | -3.5263 | 3.6589 | 3.6453 | 3.6295 | 3.6147 | 3.5547 | 3.4653 | 3.3716 | 3.1853 | 2.8937 | 0.35684 | -1.5021 | -3.66 | 3.6821 | 3.6663 | 3.6505 | 3.6337 | 3.5263 | 3.4011 | 3.3232 | 3.1432 | 2.8421 | -0.18947 | -2.1937 | -4.4379
| DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 0 | 22.0495 | 21.6432 | 21.2168 | 20.7811 | 20.2337 | 19.9411 | 19.6579 | 19.4042 | 19.1526 | 18.0863 | 16.8642 | 15.8379 | 20.6779 | 20.2 | 19.7095 | 19.2189 | 18.6421 | 18.3632 | 18.0937 | 17.8684 | 17.6453 | 16.7116 | 15.7568 | 14.5832 | 21.0916 | 20.6095 | 20.1158 | 19.6116 | 19 | 18.6947 | 18.4 | 18.1453 | 17.8926 | 16.8389 | 15.5958 | 14.4568
|  | DYCE NORTH | EE |  |  |  |  | 22.1958 | 21.8389 | 21.4579 | 21.0484 | 20.5042 | 20.1705 | 19.8505 | 19.6179 | 19.3863 | 18.0863 | 16.8642 | 15.8379 | 20.8463 | 20.4263 | 19.9789 | 19.5189 | 18.9526 | 18.6432 | 18.3505 | 18.1484 | 17.9505 | 16.8063 | 15.7568 | 14.6842 | 21.26 | 20.8368 | 20.3853 | 19.9158 | 19.3095 | 18.9621 | 18.6326 | 18.4 | 18.1716 | 16.8389 | 15.5958 | 14.4568
|  | DYCE NORTH | HT |  |  |  |  | 22.0495 | 21.6432 | 21.2168 | 20.7811 | 20.2337 | 19.9411 | 19.6579 | 19.4042 | 19.1526 | 18.1189 | 17.3021 | 16.0842 | 20.6779 | 20.2 | 19.7095 | 19.2189 | 18.6421 | 18.3632 | 18.0937 | 17.8684 | 17.6453 | 16.7116 | 15.9232 | 14.5832 | 21.0916 | 20.6095 | 20.1158 | 19.6116 | 19 | 18.6947 | 18.4 | 18.1453 | 17.8926 | 16.8463 | 15.9811 | 14.5779
|  | DYCE NORTH | HE |  |  |  |  | 22.2916 | 22.0179 | 21.7053 | 21.3516 | 20.8368 | 20.6411 | 20.4474 | 20.2558 | 20.0484 | 19.1568 | 18.4032 | 16.96 | 20.9474 | 20.6221 | 20.2474 | 19.8389 | 19.3084 | 19.1389 | 18.9726 | 18.8074 | 18.6232 | 17.8411 | 17.18 | 15.7305 | 21.0916 | 20.6095 | 20.1158 | 19.6116 | 19 | 18.6947 | 18.4 | 18.1453 | 17.8926 | 16.8463 | 15.9811 | 14.5779
|  | DYCE NORTH | CF |  |  |  |  | 22.5737 | 22.5379 | 22.4642 | 22.3811 | 22.2232 | 22.06 | 21.8937 | 21.7358 | 21.5874 | 20.9726 | 20.4137 | 19.6147 | 21.1989 | 21.1642 | 21.1305 | 21.0726 | 20.9116 | 20.7411 | 20.5663 | 20.3989 | 20.2368 | 19.6211 | 19.1011 | 18.2568 | 21.6453 | 21.5832 | 21.5189 | 21.4505 | 21.3126 | 21.1305 | 20.9442 | 20.7674 | 20.5979 | 19.9274 | 19.3347 | 18.4337
| THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | YES | 0 | 0.98211 | 0.96947 | 0.95895 | 0.94737 | 0.84421 | -1.9042 | -4.6579 | -7.3937 | -10.1379 | -13.2726 | -13.8821 | -14.5411 | 0.98 | 0.96737 | 0.95789 | 0.94632 | 0.86737 | -1.8621 | -4.5947 | -7.3126 | -10.0358 | -13.1379 | -13.7021 | -14.3137 | 0.98 | 0.96737 | 0.95579 | 0.94526 | 0.84211 | -1.9137 | -4.6726 | -7.4116 | -10.1558 | -10.9947 | -11.9158 | -12.4463
|  | EDAY | EE |  |  |  |  | 0.98632 | 0.97263 | 0.96105 | 0.94737 | 0.84421 | -1.9042 | -4.6579 | -7.3937 | -10.1379 | -10.9442 | -11.8158 | -12.2947 | 0.98421 | 0.97263 | 0.96105 | 0.94947 | 0.86737 | -1.8621 | -4.5947 | -7.3126 | -10.0358 | -10.7537 | -11.54 | -12.019 | 0.98421 | 0.97158 | 0.95789 | 0.94632 | 0.84211 | -1.9137 | -4.6726 | -7.4116 | -10.1558 | -10.9947 | -11.9158 | -12.4463
|  | EDAY | HT |  |  |  |  | 0.98211 | 0.96947 | 0.95895 | 0.94842 | 0.86316 | -1.8484 | -4.5642 | -7.2937 | -10.0695 | -10.7021 | -11.2916 | -11.6463 | 0.98 | 0.96737 | 0.95789 | 0.94632 | 0.87895 | -1.8168 | -4.5179 | -7.2316 | -9.9926 | -10.581 | -11.1684 | -11.5463 | 0.98 | 0.96737 | 0.95579 | 0.94526 | 0.86105 | -1.8537 | -4.5716 | -7.3063 | -10.0874 | -10.7632 | -11.4063 | -11.8042
|  | EDAY | HE |  |  |  |  | 0.99263 | 0.98842 | 0.98211 | 0.97789 | 0.86421 | 0.75789 | 0.65263 | -2.0789 | -4.8326 | -13.2726 | -13.8821 | -14.5411 | 0.99158 | 0.98632 | 0.98105 | 0.97579 | 0.88421 | 0.79474 | 0.70211 | -2.0137 | -4.7558 | -13.1379 | -13.7021 | -14.3137 | 0.98 | 0.96737 | 0.95579 | 0.94526 | 0.86105 | -1.8537 | -4.5716 | -7.3063 | -10.0874 | -10.7632 | -11.4063 | -11.8042
|  | EDAY | CF |  |  |  |  | 0.99684 | 0.99368 | 0.98842 | 0.98632 | 0.94526 | 0.90842 | 0.86211 | 0.81263 | 0.76632 | 0.50737 | 0.13158 | -0.23053 | 0.99474 | 0.99263 | 0.98842 | 0.98421 | 0.95158 | 0.92316 | 0.88211 | 0.83579 | 0.78842 | 0.55158 | 0.2 | -0.15895 | 0.99474 | 0.99263 | 0.98842 | 0.98421 | 0.94421 | 0.90632 | 0.85789 | 0.80842 | 0.75684 | 0.48211 | 0.078947 | -0.31474
| THURSO | EDAY TIDAL | MINIMUM HEADROOM | HY 54226 31320 | YES | YES | 0 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158
|  | EDAY TIDAL | EE |  |  |  |  | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158
|  | EDAY TIDAL | HT |  |  |  |  | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158
|  | EDAY TIDAL | HE |  |  |  |  | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158
|  | EDAY TIDAL | CF |  |  |  |  | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158
| FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | YES | 0.09 | 3.81 | 3.6868 | 3.5574 | 3.4426 | 3.1058 | 2.5889 | 2.0268 | 1.2889 | 0.35737 | -2.5111 | -6.0647 | -9.41 | 3.6163 | 3.4805 | 3.3353 | 3.21 | 2.9174 | 2.3942 | 1.8163 | 1.0416 | 0.061579 | -2.4889 | -6.3921 | -9.6237 | 3.67 | 3.5311 | 3.3816 | 3.2521 | 2.91 | 2.3342 | 1.7037 | 0.86263 | -0.18895 | -3.1795 | -7.0658 | -10.8763
|  | EDZELL | EE |  |  |  |  | 3.8795 | 3.7689 | 3.6479 | 3.5047 | 3.1237 | 2.6889 | 2.1416 | 1.6268 | 1.0184 | -2.5111 | -6.0647 | -9.41 | 3.6963 | 3.5784 | 3.4468 | 3.2879 | 2.9637 | 2.6016 | 2.1016 | 1.6142 | 1.0142 | -2.4889 | -5.9532 | -9.6237 | 3.7511 | 3.6279 | 3.4911 | 3.3247 | 2.9405 | 2.5037 | 1.9268 | 1.3732 | 0.70368 | -3.1795 | -7.0489 | -10.8763
|  | EDZELL | HT |  |  |  |  | 3.81 | 3.6868 | 3.5574 | 3.4426 | 3.1058 | 2.5889 | 2.0268 | 1.2889 | 0.35737 | -1.8005 | -5.8016 | -8.6047 | 3.6163 | 3.4805 | 3.3353 | 3.21 | 2.9174 | 2.3942 | 1.8163 | 1.0416 | 0.061579 | -2.0037 | -6.3921 | -9.5721 | 3.67 | 3.5311 | 3.3816 | 3.2521 | 2.91 | 2.3342 | 1.7037 | 0.86263 | -0.18895 | -2.5005 | -7.0658 | -10.2995
|  | EDZELL | HE |  |  |  |  | 3.9521 | 3.8868 | 3.8068 | 3.6942 | 3.31 | 2.9837 | 2.5679 | 2.1216 | 1.6395 | -0.91316 | -4.1984 | -7.7816 | 3.7784 | 3.7047 | 3.6132 | 3.4816 | 3.1616 | 2.8889 | 2.5026 | 2.0753 | 1.6026 | -0.97421 | -4.3889 | -8.1058 | 3.67 | 3.5311 | 3.3816 | 3.2521 | 2.91 | 2.3342 | 1.7037 | 0.86263 | -0.18895 | -2.5005 | -7.0658 | -10.2995
|  | EDZELL | CF |  |  |  |  | 4.0247 | 3.9942 | 3.9553 | 3.9068 | 3.7374 | 3.6005 | 3.4616 | 3.2658 | 2.9668 | 1.6342 | -0.44684 | -2.7984 | 3.8647 | 3.8321 | 3.7868 | 3.7321 | 3.5795 | 3.4626 | 3.3426 | 3.1416 | 2.7974 | 1.37 | -0.80684 | -3.3753 | 3.9195 | 3.8868 | 3.8416 | 3.7847 | 3.6079 | 3.4689 | 3.3279 | 3.1068 | 2.7468 | 1.2068 | -1.1289 | -3.8079
| MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | YES | 0 | 10.3695 | 10.2811 | 10.1916 | 10.0747 | 9.9305 | 9.7853 | 9.6442 | 9.5137 | 9.3821 | 8.7905 | 8.3432 | 7.9811 | 10.0863 | 9.9916 | 9.8432 | 9.6905 | 9.5347 | 9.3758 | 9.2232 | 9.0832 | 8.9411 | 8.2926 | 7.7989 | 7.3968 | 10.1884 | 10.0337 | 9.8811 | 9.7295 | 9.5726 | 9.4126 | 9.2579 | 9.1158 | 8.9747 | 8.3211 | 7.8253 | 7.4211
|  | EDZELL STREET | EE |  |  |  |  | 10.4253 | 10.3547 | 10.2821 | 10.2074 | 10.1263 | 10.0368 | 9.9211 | 9.8084 | 9.7074 | 9.2326 | 8.88 | 8.6116 | 10.1484 | 10.0726 | 9.9947 | 9.9011 | 9.7768 | 9.6589 | 9.5326 | 9.4095 | 9.3 | 8.7863 | 8.4032 | 8.1021 | 10.2779 | 10.18 | 10.06 | 9.9379 | 9.8137 | 9.6947 | 9.5663 | 9.4421 | 9.3316 | 8.8116 | 8.42 | 8.1168
|  | EDZELL STREET | HT |  |  |  |  | 10.3695 | 10.2811 | 10.1916 | 10.0747 | 9.9305 | 9.7853 | 9.6442 | 9.5137 | 9.3821 | 8.7905 | 8.3432 | 7.9811 | 10.0863 | 9.9916 | 9.8432 | 9.6905 | 9.5347 | 9.3758 | 9.2232 | 9.0832 | 8.9411 | 8.2926 | 7.7989 | 7.3968 | 10.1884 | 10.0337 | 9.8811 | 9.7295 | 9.5726 | 9.4126 | 9.2579 | 9.1158 | 8.9747 | 8.3211 | 7.8253 | 7.4211
|  | EDZELL STREET | HE |  |  |  |  | 10.4958 | 10.4484 | 10.3968 | 10.3411 | 10.2789 | 10.2232 | 10.1653 | 10.1126 | 10.0632 | 9.8221 | 9.6242 | 9.4726 | 10.2253 | 10.1758 | 10.1211 | 10.0632 | 10 | 9.9421 | 9.8821 | 9.8274 | 9.7663 | 9.4368 | 9.2158 | 9.0484 | 10.1884 | 10.0337 | 9.8811 | 9.7295 | 9.5726 | 9.4126 | 9.2579 | 9.1158 | 8.9747 | 8.3211 | 7.8253 | 7.4211
|  | EDZELL STREET | CF |  |  |  |  | 10.5389 | 10.5137 | 10.4874 | 10.46 | 10.4305 | 10.3989 | 10.3705 | 10.3389 | 10.3116 | 10.1821 | 10.0621 | 9.9453 | 10.2737 | 10.2453 | 10.2158 | 10.1874 | 10.1547 | 10.1232 | 10.0916 | 10.06 | 10.0284 | 9.8589 | 9.6789 | 9.5432 | 10.3916 | 10.3653 | 10.3389 | 10.3126 | 10.2821 | 10.2526 | 10.2232 | 10.1716 | 10.1232 | 9.8937 | 9.7116 | 9.5737
| ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 0 | 10.6684 | 10.3042 | 9.9516 | 9.62 | 8.9505 | 7.8137 | 6.5695 | 5.0747 | 3.2695 | -3.1958 | -7.8 | -10.4021 | 9.3674 | 8.94 | 8.5284 | 8.1411 | 7.4368 | 6.1274 | 4.7716 | 3.1389 | 1.1442 | -5.9832 | -11.0747 | -13.239 | 9.9105 | 9.5232 | 9.1495 | 8.7968 | 8.0474 | 6.6895 | 5.2832 | 3.5895 | 1.5326 | -5.8316 | -11.0663 | -13.8063
|  | ELGIN | EE |  |  |  |  | 10.8021 | 10.4747 | 10.1526 | 9.8505 | 9.1737 | 8.3147 | 7.3053 | 6.2547 | 5.1063 | -2.0053 | -7.8 | -10.4021 | 9.52 | 9.1368 | 8.7621 | 8.4126 | 7.7189 | 6.8168 | 5.7242 | 4.6095 | 3.3884 | -4.2884 | -10.4074 | -13.239 | 10.0516 | 9.7032 | 9.36 | 9.04 | 8.3116 | 7.3347 | 6.1642 | 4.9842 | 3.6958 | -4.3453 | -10.8547 | -13.8063
|  | ELGIN | HT |  |  |  |  | 10.6684 | 10.3042 | 9.9516 | 9.62 | 8.9505 | 7.8137 | 6.5695 | 5.0747 | 3.2695 | -3.1958 | -7.7758 | -9.3105 | 9.3674 | 8.94 | 8.5284 | 8.1411 | 7.4368 | 6.1274 | 4.7716 | 3.1389 | 1.1442 | -5.9832 | -11.0747 | -12.7474 | 9.9105 | 9.5232 | 9.1495 | 8.7968 | 8.0474 | 6.6895 | 5.2832 | 3.5895 | 1.5326 | -5.8316 | -11.0663 | -12.7958
|  | ELGIN | HE |  |  |  |  | 10.9863 | 10.7295 | 10.4768 | 10.2389 | 9.5832 | 8.8326 | 7.8905 | 6.88 | 5.7863 | 1.2389 | -2.2053 | -5.2674 | 9.7305 | 9.4221 | 9.12 | 8.8379 | 8.1747 | 7.3579 | 6.2958 | 5.1989 | 4.0168 | -0.85579 | -4.4779 | -7.6295 | 9.9105 | 9.5232 | 9.1495 | 8.7968 | 8.0474 | 6.6895 | 5.2832 | 3.5895 | 1.5326 | -5.8316 | -11.0663 | -12.7958
|  | ELGIN | CF |  |  |  |  | 11.0979 | 11.0474 | 10.9211 | 10.8021 | 10.5411 | 10.2295 | 9.8947 | 9.52 | 9.1116 | 6.6737 | 4.2211 | 2.2463 | 9.9663 | 9.8042 | 9.6526 | 9.5137 | 9.2463 | 8.9084 | 8.5379 | 8.1105 | 7.6274 | 4.8832 | 2.2579 | 0.11895 | 10.4547 | 10.3095 | 10.1747 | 10.0484 | 9.7747 | 9.4442 | 9.0874 | 8.6874 | 8.1947 | 5.3505 | 2.5821 | 0.33895
| ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | 0 | 2.22 | 2.1779 | 1.9979 | 1.8768 | 1.7716 | 1.6716 | 1.5716 | 1.4674 | 1.3653 | 0.95053 | 0.62842 | 0.41263 | 1.1842 | 0.88842 | 0.58737 | 0.45263 | 0.35263 | 0.25789 | 0.16316 | 0.067368 | -0.026316 | -0.41684 | -0.71263 | -0.96 | 1.9189 | 1.6168 | 1.3116 | 1.1737 | 1.0653 | 0.96 | 0.85579 | 0.74632 | 0.64211 | 0.20421 | -0.12316 | -0.38316
|  | ELLIOT DEPOT | EE |  |  |  |  | 2.2453 | 2.2095 | 2.0779 | 1.9674 | 1.8726 | 1.7705 | 1.6684 | 1.5758 | 1.4842 | 1.0326 | 0.62842 | 0.42632 | 1.2411 | 0.96 | 0.67579 | 0.55263 | 0.46632 | 0.37474 | 0.28526 | 0.20211 | 0.12211 | -0.27474 | -0.61895 | -0.81053 | 1.9758 | 1.6895 | 1.3989 | 1.2747 | 1.1758 | 1.0705 | 0.96632 | 0.87158 | 0.77684 | 0.31053 | -0.10737 | -0.32421
|  | ELLIOT DEPOT | HT |  |  |  |  | 2.22 | 2.1779 | 1.9979 | 1.8768 | 1.7716 | 1.6716 | 1.5716 | 1.4674 | 1.3653 | 0.95053 | 0.64632 | 0.41263 | 1.1842 | 0.88842 | 0.58737 | 0.45263 | 0.35263 | 0.25789 | 0.16316 | 0.067368 | -0.026316 | -0.41684 | -0.71263 | -0.96 | 1.9189 | 1.6168 | 1.3116 | 1.1737 | 1.0653 | 0.96 | 0.85579 | 0.74632 | 0.64211 | 0.20421 | -0.12316 | -0.38316
|  | ELLIOT DEPOT | HE |  |  |  |  | 2.2768 | 2.2526 | 2.1842 | 2.0937 | 2.0126 | 1.94 | 1.8684 | 1.7979 | 1.7305 | 1.4474 | 1.2158 | 0.99158 | 1.3105 | 1.0526 | 0.78842 | 0.68947 | 0.61789 | 0.55368 | 0.49158 | 0.43158 | 0.37368 | 0.13263 | -0.058947 | -0.23895 | 1.9189 | 1.6168 | 1.3116 | 1.1737 | 1.0653 | 0.96 | 0.85579 | 0.74632 | 0.64211 | 0.20421 | -0.12316 | -0.38316
|  | ELLIOT DEPOT | CF |  |  |  |  | 2.2968 | 2.2832 | 2.2695 | 2.2558 | 2.2274 | 2.2021 | 2.1758 | 2.1516 | 2.1305 | 2.0147 | 1.9042 | 1.8305 | 1.4642 | 1.3379 | 1.2158 | 1.1674 | 1.1316 | 1.0979 | 1.0632 | 1.0295 | 0.99895 | 0.84316 | 0.70211 | 0.59789 | 2.0811 | 2.0611 | 1.9495 | 1.8989 | 1.8589 | 1.8221 | 1.7821 | 1.7453 | 1.7137 | 1.5368 | 1.3684 | 1.2453
| DYCE | ELLON | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 0.846 | 38.9687 | 38.3551 | 37.6351 | 36.8435 | 35.6951 | 34.6203 | 33.4887 | 32.1887 | 30.7708 | 22.6066 | 16.4603 | 14.3835 | 37.2477 | 36.5193 | 35.6435 | 34.6708 | 33.4698 | 32.3698 | 31.2803 | 30.0319 | 28.6487 | 21.6129 | 16.0308 | 14.0982 | 38.4761 | 37.8235 | 36.9993 | 36.0614 | 34.7751 | 33.5856 | 32.4056 | 31.0277 | 29.5077 | 21.0393 | 14.614 | 12.4182
|  | ELLON | EE |  |  |  |  | 39.3035 | 38.8214 | 38.2677 | 37.5866 | 36.4035 | 34.9687 | 33.8014 | 32.7203 | 31.5929 | 22.6066 | 16.4603 | 14.3835 | 37.6466 | 37.0866 | 36.4319 | 35.6045 | 34.3898 | 32.8929 | 31.8287 | 30.8435 | 29.8108 | 21.6445 | 16.0308 | 14.0982 | 38.8224 | 38.3224 | 37.7266 | 36.9414 | 35.6151 | 33.9877 | 32.7603 | 31.6403 | 30.4687 | 21.0393 | 14.614 | 12.4182
|  | ELLON | HT |  |  |  |  | 38.9687 | 38.3551 | 37.6351 | 36.8435 | 35.6951 | 34.6203 | 33.4887 | 32.1887 | 30.7708 | 23.0982 | 19.1561 | 16.8614 | 37.2477 | 36.5193 | 35.6435 | 34.6708 | 33.4698 | 32.3698 | 31.2803 | 30.0319 | 28.6487 | 21.6129 | 17.6224 | 15.1972 | 38.4761 | 37.8235 | 36.9993 | 36.0614 | 34.7751 | 33.5856 | 32.4056 | 31.0277 | 29.5077 | 21.5045 | 17.2014 | 14.6393
|  | ELLON | HE |  |  |  |  | 39.7035 | 39.374 | 38.9477 | 38.3856 | 37.1687 | 35.9898 | 35.0593 | 34.0245 | 32.9056 | 26.8814 | 22.9782 | 19.2877 | 38.1151 | 37.7193 | 37.1961 | 36.4887 | 35.2329 | 33.9635 | 33.0361 | 32.0435 | 30.9603 | 25.3719 | 21.7329 | 18.4014 | 38.4761 | 37.8235 | 36.9993 | 36.0614 | 34.7751 | 33.5856 | 32.4056 | 31.0277 | 29.5077 | 21.5045 | 17.2014 | 14.6393
|  | ELLON | CF |  |  |  |  | 39.9393 | 39.7814 | 39.6151 | 39.4024 | 38.9887 | 38.5456 | 38.0845 | 37.7119 | 37.3456 | 34.6298 | 31.5393 | 29.4719 | 38.3887 | 38.2045 | 38.0066 | 37.7487 | 37.3414 | 36.8782 | 36.3866 | 36.0024 | 35.5961 | 32.5887 | 29.5193 | 27.4919 | 39.4772 | 39.3151 | 39.1414 | 38.9203 | 38.4845 | 38.0172 | 37.5235 | 37.1172 | 36.7108 | 33.5814 | 30.2487 | 27.9961
| TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0 | 0.18421 | 0.12842 | 0.069474 | 0.0084211 | -0.094737 | -0.20105 | -0.31053 | -0.41158 | -0.51579 | -1.0326 | -1.5263 | -1.8284 | 0.17684 | 0.12421 | 0.067368 | 0.0094737 | -0.082105 | -0.17263 | -0.26526 | -0.35474 | -0.44526 | -0.89158 | -1.32 | -1.5905 | 0.16947 | 0.11474 | 0.054737 | -0.006316 | -0.11368 | -0.22105 | -0.33158 | -0.43474 | -0.54105 | -1.0705 | -1.5758 | -1.8832
|  | EREDINE | EE |  |  |  |  | 0.18421 | 0.12842 | 0.069474 | 0.0084211 | -0.094737 | -0.20105 | -0.31053 | -0.41158 | -0.51579 | -1.0326 | -1.5263 | -1.8284 | 0.17684 | 0.12421 | 0.067368 | 0.0094737 | -0.082105 | -0.17263 | -0.26526 | -0.35474 | -0.44526 | -0.89158 | -1.32 | -1.5905 | 0.16947 | 0.11474 | 0.054737 | -0.006316 | -0.11368 | -0.22105 | -0.33158 | -0.43474 | -0.54105 | -1.0705 | -1.5758 | -1.8832
|  | EREDINE | HT |  |  |  |  | 0.20947 | 0.19474 | 0.17895 | 0.16105 | 0.10737 | 0.053684 | 0 | -0.063158 | -0.12632 | -0.38632 | -0.57895 | -0.70632 | 0.20632 | 0.18947 | 0.17263 | 0.15579 | 0.10842 | 0.063158 | 0.016842 | -0.036842 | -0.089474 | -0.31263 | -0.48211 | -0.59579 | 0.20105 | 0.18316 | 0.16421 | 0.14526 | 0.089474 | 0.034737 | -0.02 | -0.085263 | -0.15053 | -0.41895 | -0.61789 | -0.74737
|  | EREDINE | HE |  |  |  |  | 0.21579 | 0.20211 | 0.18842 | 0.17053 | 0.10526 | 0.049474 | -0.009474 | -0.065263 | -0.12211 | -0.39158 | -0.64842 | -0.91895 | 0.20947 | 0.19684 | 0.18105 | 0.16421 | 0.11053 | 0.062105 | 0.013684 | -0.033684 | -0.081053 | -0.31053 | -0.52947 | -0.75895 | 0.20105 | 0.18316 | 0.16421 | 0.14526 | 0.089474 | 0.034737 | -0.02 | -0.085263 | -0.15053 | -0.41895 | -0.61789 | -0.74737
|  | EREDINE | CF |  |  |  |  | 0.22526 | 0.22105 | 0.21789 | 0.21158 | 0.19053 | 0.16947 | 0.15158 | 0.13263 | 0.11895 | 0.027368 | -0.094737 | -0.18632 | 0.21368 | 0.21158 | 0.21053 | 0.20737 | 0.19368 | 0.17579 | 0.16105 | 0.14526 | 0.13368 | 0.058947 | -0.041053 | -0.11368 | 0.21579 | 0.21053 | 0.20737 | 0.20211 | 0.18105 | 0.15895 | 0.14 | 0.12211 | 0.10842 | 0.012632 | -0.11579 | -0.20842
| INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | YES | 0 | 1.0274 | 1.0032 | 0.97474 | 0.94421 | 0.76421 | 0.54737 | 0.32 | 0.098947 | -0.22632 | -2.2084 | -4.4726 | -6.2242 | 1.0263 | 1.0053 | 0.98211 | 0.95263 | 0.80947 | 0.61158 | 0.40105 | 0.20105 | -0.11579 | -1.8926 | -4.1116 | -5.9937 | 1.0179 | 0.99368 | 0.96842 | 0.93895 | 0.75579 | 0.53474 | 0.30737 | 0.10947 | -0.20526 | -2.4295 | -4.9032 | -6.9021
|  | ERROGIE | EE |  |  |  |  | 1.0274 | 1.0032 | 0.97474 | 0.94421 | 0.76421 | 0.54737 | 0.32421 | 0.12947 | -0.17053 | -2.2084 | -4.4726 | -6.2242 | 1.0263 | 1.0053 | 0.98211 | 0.95263 | 0.80947 | 0.64105 | 0.46842 | 0.31579 | 0.056842 | -1.8926 | -4.1116 | -5.9937 | 1.0179 | 0.99368 | 0.96842 | 0.93895 | 0.75579 | 0.53474 | 0.30737 | 0.10947 | -0.20526 | -2.4295 | -4.9032 | -6.9021
|  | ERROGIE | HT |  |  |  |  | 1.0305 | 1.0158 | 1.0032 | 0.98737 | 0.84421 | 0.7 | 0.50737 | 0.27895 | -0.10632 | -1.9126 | -3.98 | -5.3947 | 1.0295 | 1.0189 | 1.0084 | 0.99789 | 0.88421 | 0.76842 | 0.59789 | 0.39474 | 0.016842 | -1.8274 | -4.0705 | -5.66 | 1.0232 | 1.0095 | 0.99684 | 0.98526 | 0.84211 | 0.69579 | 0.49368 | 0.25579 | -0.16947 | -2.1747 | -4.5326 | -6.1663
|  | ERROGIE | HE |  |  |  |  | 1.0347 | 1.0284 | 1.0211 | 1.0158 | 0.77684 | 0.54947 | 0.32 | 0.098947 | -0.22632 | -1.6137 | -3.3579 | -5.2632 | 1.0337 | 1.0305 | 1.0242 | 1.0168 | 0.81579 | 0.61158 | 0.40105 | 0.20105 | -0.11579 | -1.46 | -3.2347 | -5.1789 | 1.0232 | 1.0095 | 0.99684 | 0.98526 | 0.84211 | 0.69579 | 0.49368 | 0.25579 | -0.16947 | -2.1747 | -4.5326 | -6.1663
|  | ERROGIE | CF |  |  |  |  | 1.0368 | 1.0347 | 1.0305 | 1.0284 | 0.96526 | 0.90421 | 0.76211 | 0.62316 | 0.46526 | -0.24421 | -1.3326 | -2.5505 | 1.0358 | 1.0337 | 1.0316 | 1.0295 | 0.98421 | 0.93474 | 0.79158 | 0.64947 | 0.47895 | -0.23895 | -1.3589 | -2.6726 | 1.0305 | 1.0284 | 1.0242 | 1.0211 | 0.96526 | 0.90526 | 0.74737 | 0.59368 | 0.41579 | -0.36947 | -1.5821 | -2.9642
| ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 0.05 | 4.9321 | 4.6974 | 4.43 | 4.1121 | 3.4447 | 2.8521 | 2.2205 | 1.5921 | 0.95947 | -3.6563 | -11.5995 | -16.2626 | 4.8574 | 4.6047 | 4.3142 | 3.9784 | 3.3658 | 2.83 | 2.3216 | 1.7626 | 1.1953 | -3.0879 | -11.2521 | -16.3616 | 4.9721 | 4.7195 | 4.4258 | 4.0753 | 3.3721 | 2.7542 | 2.1311 | 1.4911 | 0.84368 | -4.1111 | -12.9605 | -18.2763
|  | ERROL | EE |  |  |  |  | 5.0416 | 4.8395 | 4.6079 | 4.3374 | 3.6395 | 2.9163 | 2.2205 | 1.5921 | 0.95947 | -3.6563 | -11.5995 | -16.2626 | 4.9774 | 4.7647 | 4.5142 | 4.2268 | 3.6111 | 2.9879 | 2.39 | 1.8447 | 1.2995 | -3.0879 | -11.2521 | -16.3616 | 5.09 | 4.8732 | 4.6205 | 4.3195 | 3.5889 | 2.8416 | 2.1311 | 1.4911 | 0.84579 | -4.1111 | -12.9605 | -18.2763
|  | ERROL | HT |  |  |  |  | 4.9321 | 4.6974 | 4.43 | 4.1121 | 3.4447 | 2.8521 | 2.2816 | 1.6426 | 1.0047 | -3.0784 | -8.7753 | -12.6795 | 4.8574 | 4.6047 | 4.3142 | 3.9784 | 3.3658 | 2.83 | 2.3216 | 1.7626 | 1.1953 | -2.85 | -9.0995 | -13.5068 | 4.9721 | 4.7195 | 4.4258 | 4.0753 | 3.3721 | 2.7542 | 2.1616 | 1.5016 | 0.84368 | -3.6121 | -10.0932 | -14.5826
|  | ERROL | HE |  |  |  |  | 5.1405 | 5.05 | 4.8805 | 4.6742 | 3.9826 | 3.4184 | 2.89 | 2.3721 | 1.6647 | -2.11 | -8.6974 | -13.7574 | 5.1216 | 4.9837 | 4.7942 | 4.5616 | 3.9689 | 3.4732 | 3.0205 | 2.5721 | 1.8879 | -1.7911 | -8.8268 | -14.0395 | 4.9721 | 4.7195 | 4.4258 | 4.0753 | 3.3721 | 2.7542 | 2.1616 | 1.5016 | 0.84368 | -3.6121 | -10.0932 | -14.5826
|  | ERROL | CF |  |  |  |  | 5.1868 | 5.1574 | 5.1047 | 5.0121 | 4.7437 | 4.5079 | 4.2805 | 4.0637 | 3.6332 | 1.6437 | -1.3068 | -4.5879 | 5.1679 | 5.1395 | 5.0437 | 4.9395 | 4.7121 | 4.5163 | 4.3205 | 4.1226 | 3.6395 | 1.6111 | -1.4426 | -5.0058 | 5.2637 | 5.2353 | 5.1532 | 5.0511 | 4.7816 | 4.5363 | 4.2995 | 4.0732 | 3.5753 | 1.3805 | -1.9058 | -5.6311
| FASNAKYLE | FASNAKYLE | MINIMUM HEADROOM | NH 31948 29998 | YES | YES | 0 | 0.97579 | 0.95474 | 0.93474 | 0.91158 | 0.84947 | 0.77474 | 0.70316 | 0.63684 | 0.52737 | -0.24421 | -1.1705 | -1.9432 | 0.96947 | 0.94842 | 0.92947 | 0.90947 | 0.86421 | 0.80842 | 0.74947 | 0.67474 | 0.54 | -0.26105 | -1.3189 | -2.0863 | 0.96526 | 0.94105 | 0.92 | 0.89474 | 0.82947 | 0.75368 | 0.68105 | 0.61263 | 0.50105 | -0.36421 | -1.4516 | -2.2895
|  | FASNAKYLE | EE |  |  |  |  | 0.98211 | 0.95895 | 0.93474 | 0.91158 | 0.84947 | 0.77474 | 0.70316 | 0.63684 | 0.56421 | -0.24421 | -1.1421 | -1.9432 | 0.98 | 0.95895 | 0.93895 | 0.91789 | 0.86947 | 0.80842 | 0.75053 | 0.69579 | 0.63474 | -0.18105 | -1.1053 | -1.9916 | 0.97158 | 0.94632 | 0.92 | 0.89474 | 0.82947 | 0.75368 | 0.68105 | 0.61263 | 0.53789 | -0.36211 | -1.3674 | -2.2895
|  | FASNAKYLE | HT |  |  |  |  | 0.97579 | 0.95474 | 0.93579 | 0.91579 | 0.86316 | 0.80947 | 0.75579 | 0.69474 | 0.54105 | -0.22526 | -1.1705 | -1.8442 | 0.96947 | 0.94842 | 0.92947 | 0.90947 | 0.86421 | 0.82 | 0.77684 | 0.72737 | 0.56421 | -0.26105 | -1.3189 | -2.0863 | 0.96526 | 0.94105 | 0.92105 | 0.89895 | 0.84421 | 0.79053 | 0.73579 | 0.67368 | 0.50105 | -0.36421 | -1.4516 | -2.2326
|  | FASNAKYLE | HE |  |  |  |  | 0.99789 | 0.99053 | 0.98105 | 0.96947 | 0.90105 | 0.82 | 0.73579 | 0.65684 | 0.52737 | -0.014737 | -0.73474 | -1.5211 | 0.99895 | 0.98842 | 0.97895 | 0.96842 | 0.90947 | 0.83158 | 0.74947 | 0.67474 | 0.54 | -0.016842 | -0.78632 | -1.6284 | 0.96526 | 0.94105 | 0.92105 | 0.89895 | 0.84421 | 0.79053 | 0.73579 | 0.67368 | 0.50105 | -0.36421 | -1.4516 | -2.2326
|  | FASNAKYLE | CF |  |  |  |  | 1.0053 | 1 | 0.99789 | 0.99368 | 0.97053 | 0.95053 | 0.90421 | 0.84737 | 0.77684 | 0.48211 | 0.028421 | -0.51053 | 1.0063 | 1.0011 | 0.99684 | 0.99053 | 0.97368 | 0.95579 | 0.90737 | 0.84211 | 0.76316 | 0.44737 | -0.043158 | -0.64632 | 1.0032 | 0.99684 | 0.99158 | 0.98421 | 0.96211 | 0.94 | 0.88947 | 0.82316 | 0.74211 | 0.41158 | -0.10316 | -0.7221
| TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0 | 0.10211 | 0.1 | 0.097895 | 0.095789 | 0.077895 | 0.052632 | 0.025263 | 0.0021053 | -0.027368 | -0.23053 | -0.45789 | -0.61368 | 0.10105 | 0.1 | 0.097895 | 0.095789 | 0.08 | 0.058947 | 0.036842 | 0.014737 | -0.016842 | -0.20211 | -0.41895 | -0.58737 | 0.098947 | 0.096842 | 0.095789 | 0.092632 | 0.074737 | 0.049474 | 0.022105 | 0 | -0.028421 | -0.25263 | -0.49895 | -0.67579
|  | FINCASTLE | EE |  |  |  |  | 0.10211 | 0.10105 | 0.098947 | 0.096842 | 0.077895 | 0.052632 | 0.025263 | 0.0021053 | -0.024211 | -0.23053 | -0.45789 | -0.61368 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.08 | 0.058947 | 0.036842 | 0.018947 | -0.005263 | -0.20211 | -0.41895 | -0.58737 | 0.098947 | 0.097895 | 0.095789 | 0.093684 | 0.074737 | 0.049474 | 0.022105 | 0 | -0.028421 | -0.25263 | -0.49895 | -0.67579
|  | FINCASTLE | HT |  |  |  |  | 0.10211 | 0.1 | 0.097895 | 0.095789 | 0.08 | 0.061053 | 0.04421 | 0.018947 | -0.021053 | -0.19579 | -0.38632 | -0.51579 | 0.10105 | 0.1 | 0.097895 | 0.095789 | 0.08 | 0.065263 | 0.051579 | 0.029474 | -0.009474 | -0.18632 | -0.39158 | -0.53368 | 0.098947 | 0.096842 | 0.095789 | 0.092632 | 0.076842 | 0.057895 | 0.041053 | 0.014737 | -0.027368 | -0.22421 | -0.44105 | -0.58737
|  | FINCASTLE | HE |  |  |  |  | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.078947 | 0.055789 | 0.029474 | 0.0052632 | -0.027368 | -0.16842 | -0.33684 | -0.52316 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.081053 | 0.06 | 0.036842 | 0.014737 | -0.016842 | -0.15158 | -0.32105 | -0.50632 | 0.098947 | 0.096842 | 0.095789 | 0.092632 | 0.076842 | 0.057895 | 0.041053 | 0.014737 | -0.027368 | -0.22421 | -0.44105 | -0.58737
|  | FINCASTLE | CF |  |  |  |  | 0.10421 | 0.10316 | 0.10316 | 0.10211 | 0.094737 | 0.088421 | 0.077895 | 0.065263 | 0.051579 | -0.02 | -0.12421 | -0.23895 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.097895 | 0.091579 | 0.08 | 0.066316 | 0.050526 | -0.021053 | -0.12737 | -0.24842 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.092632 | 0.086316 | 0.074737 | 0.06 | 0.04421 | -0.034737 | -0.15263 | -0.28
| SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 0 | 1.2147 | 0.82105 | 0.3 | -0.34632 | -1.1253 | -1.4947 | -2.2505 | -3.3168 | -4.3537 | -5.1021 | -7.0811 | -7.1232 | 0.88737 | 0.42526 | -0.18842 | -0.94947 | -1.8642 | -2.2968 | -3.1853 | -4.44 | -5.6653 | -6.5242 | -8.0284 | -8.0642 | 0.92737 | 0.46526 | -0.14632 | -0.90632 | -1.8211 | -2.2558 | -3.1432 | -4.3958 | -5.6211 | -6.4895 | -6.6042 | -6.6453
|  | FIRTH | EE |  |  |  |  | 1.2242 | 0.83158 | 0.31474 | -0.32947 | -1.1042 | -1.4737 | -2.2295 | -3.2926 | -4.3537 | -5.1021 | -5.2074 | -5.2453 | 0.89789 | 0.43579 | -0.17368 | -0.93158 | -1.8432 | -2.2737 | -3.1611 | -4.4137 | -5.6653 | -6.5242 | -6.6316 | -6.6674 | 0.93789 | 0.47684 | -0.13158 | -0.88947 | -1.8 | -2.2337 | -3.1211 | -4.3726 | -5.6211 | -6.4895 | -6.6042 | -6.6453
|  | FIRTH | HT |  |  |  |  | 1.2147 | 0.82105 | 0.3 | -0.34632 | -1.1253 | -1.4947 | -2.2505 | -3.3168 | -4.3042 | -5.0411 | -5.1347 | -5.1758 | 0.88737 | 0.42526 | -0.18842 | -0.94947 | -1.8642 | -2.2968 | -3.1853 | -4.44 | -5.6032 | -6.4568 | -6.5558 | -6.5979 | 0.92737 | 0.46526 | -0.14632 | -0.90632 | -1.8211 | -2.2558 | -3.1432 | -4.3958 | -5.5589 | -6.4168 | -6.5179 | -6.5621
|  | FIRTH | HE |  |  |  |  | 1.2368 | 0.85158 | 0.33789 | -0.3 | -1.0726 | -1.4368 | -2.1863 | -3.2432 | -4.3 | -5.0126 | -7.0811 | -7.1232 | 0.91053 | 0.45684 | -0.14842 | -0.90211 | -1.8116 | -2.2368 | -3.1179 | -4.3642 | -5.6105 | -6.4368 | -8.0284 | -8.0642 | 0.92737 | 0.46526 | -0.14632 | -0.90632 | -1.8211 | -2.2558 | -3.1432 | -4.3958 | -5.5589 | -6.4168 | -6.5179 | -6.5621
|  | FIRTH | CF |  |  |  |  | 1.5147 | 1.4126 | 1.2695 | 1.0947 | 0.88105 | 0.63053 | 0.35053 | 0.032632 | -0.14632 | -0.35368 | -0.38526 | -0.40526 | 1.2421 | 1.1168 | 0.94947 | 0.74316 | 0.49263 | 0.2 | -0.13158 | -0.50421 | -0.71474 | -0.95158 | -0.97895 | -0.99684 | 1.2695 | 1.1547 | 0.98947 | 0.78316 | 0.53158 | 0.23895 | -0.091579 | -0.46421 | -0.67474 | -0.91474 | -0.94632 | -0.96737
| FORT WILLIAM | FISHNISH | MINIMUM HEADROOM | NM 66623 42191 | YES | NO | 0 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19789 | 0.19789 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19684
|  | FISHNISH | EE |  |  |  |  | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.19895 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19895
|  | FISHNISH | HT |  |  |  |  | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19789 | 0.19789 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19684
|  | FISHNISH | HE |  |  |  |  | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19684
|  | FISHNISH | CF |  |  |  |  | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.19895 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2
| THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | YES | 0 | -1.2832 | -1.2874 | -1.2916 | -1.2947 | -1.2937 | -1.2958 | -1.2989 | -1.3032 | -1.2853 | 0.49158 | 0.48632 | 0.48316 | -1.26 | -1.2653 | -1.2695 | -1.2726 | -1.2716 | -1.2737 | -1.2779 | -1.2832 | -1.2621 | 0.32526 | 0.32 | 0.31684 | 0.92526 | 0.92105 | 0.91789 | 0.91368 | 0.91579 | 0.91263 | 0.90947 | 0.90526 | 0.92316 | 2.9768 | 2.9716 | 2.9684
|  | FLOTTA | EE |  |  |  |  | -1.2811 | -1.2842 | -1.2874 | -1.2905 | -1.2937 | -1.2958 | -1.2989 | -1.3032 | 0.50316 | 0.49579 | 0.49263 | 0.49053 | -1.2568 | -1.2611 | -1.2642 | -1.2684 | -1.2716 | -1.2737 | -1.2779 | -1.2832 | 0.33684 | 0.32947 | 0.32632 | 0.32421 | 0.92842 | 0.92421 | 0.92211 | 0.91789 | 0.91579 | 0.91263 | 0.90947 | 0.90526 | 2.9884 | 2.9811 | 2.9779 | 2.9758
|  | FLOTTA | HT |  |  |  |  | -1.2832 | -1.2874 | -1.2916 | -1.2947 | 0.50737 | 0.50526 | 0.50211 | 0.5 | 0.49789 | 0.49158 | 0.48632 | 0.48316 | -1.26 | -1.2653 | -1.2695 | -1.2726 | 0.34105 | 0.33895 | 0.33579 | 0.33368 | 0.33158 | 0.32526 | 0.32 | 0.31684 | 0.92526 | 0.92105 | 0.91789 | 0.91368 | 2.9926 | 2.9905 | 2.9874 | 2.9853 | 2.9832 | 2.9768 | 2.9716 | 2.9684
|  | FLOTTA | HE |  |  |  |  | -1.2789 | -1.28 | -1.2821 | -1.2842 | -1.2863 | -1.2874 | -1.2905 | -1.2916 | 0.50842 | 0.50421 | 0.50211 | 0.50211 | -1.2547 | -1.2558 | -1.2579 | -1.26 | -1.2621 | -1.2642 | -1.2674 | -1.2684 | 0.34211 | 0.33789 | 0.33579 | 0.33579 | 0.92526 | 0.92105 | 0.91789 | 0.91368 | 2.9926 | 2.9905 | 2.9874 | 2.9853 | 2.9832 | 2.9768 | 2.9716 | 2.9684
|  | FLOTTA | CF |  |  |  |  | -1.2758 | -1.2768 | -1.2789 | -1.2789 | -1.28 | -1.2821 | -1.2821 | -1.2842 | -1.2853 | 0.51158 | 0.51053 | 0.50947 | -1.2516 | -1.2526 | -1.2547 | -1.2547 | -1.2558 | -1.2579 | -1.2579 | -1.26 | -1.2621 | 0.34526 | 0.34421 | 0.34316 | 0.93368 | 0.93263 | 0.93053 | 0.92947 | 0.92842 | 0.92737 | 0.92737 | 0.92526 | 0.92316 | 2.9968 | 2.9958 | 2.9947
| ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 0 | 15.5079 | 15.2889 | 15.07 | 14.8079 | 14.3911 | 13.8258 | 13.2553 | 12.5489 | 11.6542 | 9.0205 | 7.1637 | 5.1511 | 14.2526 | 14.0021 | 13.7558 | 13.4505 | 13.0558 | 12.4663 | 11.8737 | 11.1263 | 10.1905 | 7.8074 | 6.2653 | 4.1147 | 14.8003 | 14.5697 | 14.3403 | 14.0476 | 13.6108 | 12.995 | 12.3739 | 11.5971 | 10.6434 | 7.8739 | 5.9603 | 3.7571
|  | FOCHABERS | EE |  |  |  |  | 15.6142 | 15.43 | 15.2563 | 15.0489 | 14.6089 | 14.0532 | 13.53 | 13.0216 | 12.4553 | 9.0205 | 7.1637 | 5.1511 | 14.3726 | 14.1663 | 13.9758 | 13.7421 | 13.3379 | 12.8095 | 12.3263 | 11.8358 | 11.2758 | 7.8074 | 6.2653 | 4.1147 | 14.9118 | 14.7182 | 14.5371 | 14.3182 | 13.8592 | 13.2708 | 12.7213 | 12.1792 | 11.5697 | 7.8739 | 5.9603 | 3.7571
|  | FOCHABERS | HT |  |  |  |  | 15.5079 | 15.2889 | 15.07 | 14.8079 | 14.3911 | 13.8258 | 13.2553 | 12.5489 | 11.6542 | 9.3595 | 7.9068 | 5.91 | 14.2526 | 14.0021 | 13.7558 | 13.4505 | 13.0558 | 12.4663 | 11.8737 | 11.1263 | 10.1905 | 7.9284 | 6.4916 | 4.2621 | 14.8003 | 14.5697 | 14.3403 | 14.0476 | 13.6108 | 12.995 | 12.3739 | 11.5971 | 10.6434 | 8.2203 | 6.6466 | 4.3645
|  | FOCHABERS | HE |  |  |  |  | 15.7574 | 15.6311 | 15.5047 | 15.3332 | 14.8932 | 14.4511 | 14.0658 | 13.6826 | 13.2774 | 11.4289 | 9.3405 | 6.7153 | 14.5347 | 14.3895 | 14.2453 | 14.0432 | 13.6421 | 13.2116 | 12.8558 | 12.4989 | 12.1126 | 10.3474 | 8.2358 | 5.5684 | 14.8003 | 14.5697 | 14.3403 | 14.0476 | 13.6108 | 12.995 | 12.3739 | 11.5971 | 10.6434 | 8.2203 | 6.6466 | 4.3645
|  | FOCHABERS | CF |  |  |  |  | 15.8511 | 15.7847 | 15.7321 | 15.6689 | 15.5089 | 15.3374 | 15.1616 | 15.0016 | 14.8426 | 13.83 | 12.3995 | 10.7426 | 14.6421 | 14.5663 | 14.5074 | 14.4358 | 14.2937 | 14.1295 | 13.9579 | 13.8011 | 13.6326 | 12.5937 | 11.0874 | 9.2968 | 15.1603 | 15.0897 | 15.035 | 14.9687 | 14.8055 | 14.6287 | 14.4466 | 14.2803 | 14.1129 | 13.015 | 11.4339 | 9.6424
| NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 0.06 | 16.7384 | 16.3563 | 15.8868 | 38.9074 | 37.6842 | 36.3063 | 35.0126 | 33.5295 | 31.7811 | 24.7758 | 17.9242 | 11.0421 | 14.3568 | 13.8232 | 13.1063 | 35.2579 | 34.0168 | 32.6705 | 31.4189 | 29.9947 | 28.2526 | 22.1337 | 15.2979 | 8.3253 | 14.9961 | 14.4761 | 13.7855 | 36.5989 | 35.2337 | 33.7463 | 32.36 | 30.7695 | 28.8611 | 21.5579 | 14.3453 | 6.4
|  | FORRES | EE |  |  |  |  | 16.8995 | 16.5932 | 16.1763 | 39.2811 | 38.1147 | 36.6568 | 35.3179 | 34.1284 | 32.8516 | 24.7758 | 17.9242 | 11.0421 | 14.6305 | 14.1737 | 13.5526 | 35.8768 | 34.6168 | 33.2453 | 32.0632 | 31.0032 | 29.8442 | 22.1337 | 15.9547 | 8.3253 | 15.2582 | 14.8045 | 14.2003 | 37.1695 | 35.7474 | 34.1842 | 32.7947 | 31.5611 | 30.2284 | 21.5579 | 14.3453 | 6.4
|  | FORRES | HT |  |  |  |  | 16.7384 | 16.3563 | 15.8868 | 38.9074 | 37.6842 | 36.3063 | 35.0126 | 33.5295 | 31.7811 | 25.8295 | 19.1347 | 13.2863 | 14.3568 | 13.8232 | 13.1063 | 35.2579 | 34.0168 | 32.6705 | 31.4189 | 29.9947 | 28.2526 | 22.4653 | 15.2979 | 8.7358 | 14.9961 | 14.4761 | 13.7855 | 36.5989 | 35.2337 | 33.7463 | 32.36 | 30.7695 | 28.8611 | 22.4316 | 14.8821 | 8.1821
|  | FORRES | HE |  |  |  |  | 17.0626 | 16.9363 | 16.6668 | 39.8611 | 38.6979 | 37.6179 | 36.5705 | 35.5653 | 34.5105 | 29.4168 | 22.9084 | 15.2979 | 14.9968 | 14.6821 | 14.1874 | 36.5937 | 35.3674 | 34.1916 | 33.2432 | 32.3421 | 31.38 | 26.6526 | 20.0768 | 12.2505 | 14.9961 | 14.4761 | 13.7855 | 36.5989 | 35.2337 | 33.7463 | 32.36 | 30.7695 | 28.8611 | 22.4316 | 14.8821 | 8.1821
|  | FORRES | CF |  |  |  |  | 17.1679 | 17.0942 | 17.0216 | 40.4958 | 40.0526 | 39.6474 | 39.2621 | 38.9305 | 38.6411 | 36.0811 | 31.6084 | 26.7579 | 15.1421 | 15.0726 | 14.8705 | 37.6432 | 37.1663 | 36.7316 | 36.34 | 36.0137 | 35.6863 | 32.7642 | 28.14 | 22.8505 | 15.7087 | 15.6361 | 15.4855 | 38.8916 | 38.3484 | 37.8579 | 37.4063 | 37.0284 | 36.6695 | 33.5653 | 28.5821 | 23.0274
| DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | YES | 0 | 0.15158 | 0.10842 | 0.065263 | 0.01579 | -0.035789 | -0.095789 | -2.4579 | -2.8432 | -4.9084 | -8.3305 | -12.6116 | -15.7432 | 0.29895 | 0.25789 | 0.21789 | 0.16842 | 0.11895 | 0.023158 | -1.8253 | -2.1379 | -3.8916 | -7.2221 | -11.3568 | -14.7158 | 0.14421 | 0.1 | 0.055789 | 0.0021053 | -0.051579 | -0.096842 | -2.4821 | -2.8695 | -4.9463 | -8.7211 | -13.3832 | -16.9411
|  | FORSS | EE |  |  |  |  | 0.16842 | 0.12105 | 0.072632 | 0.021053 | -0.033684 | -0.082105 | -2.4579 | -2.8432 | -4.9084 | -8.3305 | -12.6116 | -15.7432 | 0.31684 | 0.27579 | 0.23053 | 0.18316 | 0.13158 | 0.087368 | -1.8253 | -2.1379 | -3.8368 | -7.2221 | -11.3568 | -14.7158 | 0.16211 | 0.11368 | 0.064211 | 0.010526 | -0.046316 | -0.096842 | -2.4821 | -2.8695 | -4.9463 | -8.7211 | -13.3832 | -16.9411
|  | FORSS | HT |  |  |  |  | 0.15158 | 0.10842 | 0.065263 | 0.01579 | -0.035789 | -0.078947 | -2.0758 | -2.5316 | -4.8189 | -8.0032 | -11.7979 | -14.3863 | 0.29895 | 0.25789 | 0.21789 | 0.16842 | 0.11895 | 0.077895 | -1.5326 | -1.9326 | -3.8916 | -7.1547 | -11.2368 | -14.12 | 0.14421 | 0.1 | 0.055789 | 0.0021053 | -0.051579 | -0.096842 | -2.0947 | -2.5663 | -4.9168 | -8.4947 | -12.8 | -15.7811
|  | FORSS | HE |  |  |  |  | 0.18947 | 0.17368 | 0.15684 | 0.13158 | 0.04 | -0.095789 | -1.6526 | -2.0853 | -3.4747 | -5.5379 | -8.8042 | -12.3958 | 0.34105 | 0.32526 | 0.30737 | 0.28316 | 0.18105 | 0.023158 | -1.2695 | -1.6621 | -2.8863 | -4.9526 | -8.2495 | -11.8916 | 0.14421 | 0.1 | 0.055789 | 0.0021053 | -0.051579 | -0.096842 | -2.0947 | -2.5663 | -4.9168 | -8.4947 | -12.8 | -15.7811
|  | FORSS | CF |  |  |  |  | 0.20105 | 0.19053 | 0.18105 | 0.16947 | 0.16 | 0.14737 | -0.79368 | -1.0516 | -1.3326 | -2.6105 | -4.6747 | -6.9474 | 0.35368 | 0.34421 | 0.33368 | 0.32211 | 0.31263 | 0.3 | -0.49789 | -0.76316 | -1.0663 | -2.3474 | -4.4547 | -6.8811 | 0.19368 | 0.18421 | 0.17368 | 0.16211 | 0.15158 | 0.14 | -0.82105 | -1.1084 | -1.4379 | -2.8516 | -5.1358 | -7.7063
| BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 1.796 | 2.7524 | 2.7029 | 2.6524 | 2.6008 | 2.3966 | 2.1682 | 1.9082 | 1.6829 | 1.3577 | -0.41916 | -2.3371 | -3.5392 | 1.9998 | 1.9524 | 1.904 | 1.8535 | 1.6882 | 1.5282 | 1.3261 | 1.1103 | 0.77874 | -0.77179 | -2.5518 | -3.8213 | 2.0998 | 2.0503 | 2.0008 | 1.9482 | 1.7472 | 1.524 | 1.2672 | 1.044 | 0.68084 | -1.1792 | -3.2234 | -4.5665
|  | FORTEVIOT | EE |  |  |  |  | 2.7766 | 2.7335 | 2.6903 | 2.6472 | 2.4229 | 2.1682 | 1.9082 | 1.6829 | 1.3798 | -0.41916 | -2.3371 | -3.5392 | 2.024 | 1.984 | 1.944 | 1.904 | 1.7272 | 1.5282 | 1.3261 | 1.1503 | 0.88295 | -0.77179 | -2.5518 | -3.8213 | 2.124 | 2.0808 | 2.0377 | 1.9956 | 1.7745 | 1.524 | 1.2672 | 1.044 | 0.72821 | -1.1792 | -3.2234 | -4.5665
|  | FORTEVIOT | HT |  |  |  |  | 2.7524 | 2.7029 | 2.6524 | 2.6008 | 2.3966 | 2.2051 | 1.9703 | 1.7114 | 1.3577 | -0.15705 | -1.6455 | -2.596 | 1.9998 | 1.9524 | 1.904 | 1.8535 | 1.6882 | 1.5335 | 1.3293 | 1.1103 | 0.77874 | -0.69074 | -2.2623 | -3.3171 | 2.0998 | 2.0503 | 2.0008 | 1.9482 | 1.7472 | 1.5587 | 1.3187 | 1.0556 | 0.68084 | -0.9581 | -2.6339 | -3.7286
|  | FORTEVIOT | HE |  |  |  |  | 2.8061 | 2.784 | 2.7598 | 2.7335 | 2.4693 | 2.2377 | 2.0029 | 1.7766 | 1.4893 | 0.25137 | -1.1297 | -2.6192 | 2.0535 | 2.0324 | 2.0082 | 1.9829 | 1.7619 | 1.5629 | 1.3608 | 1.1672 | 0.90084 | -0.22442 | -1.5602 | -3.0034 | 2.0998 | 2.0503 | 2.0008 | 1.9482 | 1.7472 | 1.5587 | 1.3187 | 1.0556 | 0.68084 | -0.9581 | -2.6339 | -3.7286
|  | FORTEVIOT | CF |  |  |  |  | 2.8251 | 2.8124 | 2.8008 | 2.7872 | 2.6998 | 2.6219 | 2.4935 | 2.3735 | 2.2535 | 1.6451 | 0.78189 | -0.085474 | 2.0724 | 2.0608 | 2.0482 | 2.0356 | 1.9672 | 1.9061 | 1.7829 | 1.6661 | 1.5419 | 0.95874 | 0.11874 | -0.78232 | 2.1724 | 2.1598 | 2.1482 | 2.1345 | 2.0482 | 1.9724 | 1.8335 | 1.7051 | 1.5714 | 0.91663 | -0.023368 | -0.996
| INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | YES | 0 | 1.0537 | 1.0474 | 1.04 | 1.0316 | 1.0221 | 1.0126 | 1.0021 | 0.99368 | 0.98421 | 0.92526 | 0.83368 | 0.76842 | 1.0495 | 1.0453 | 1.04 | 1.0305 | 1.0221 | 1.0116 | 1.0021 | 0.99263 | 0.98526 | 0.91895 | 0.81684 | 0.74211 | 1.0368 | 1.0284 | 1.0211 | 1.0116 | 1.0021 | 0.99158 | 0.98105 | 0.97158 | 0.96316 | 0.89474 | 0.78947 | 0.71474
|  | FOYERS | EE |  |  |  |  | 1.0589 | 1.0537 | 1.0463 | 1.0411 | 1.0326 | 1.0242 | 1.0147 | 1.0063 | 0.99895 | 0.94 | 0.86211 | 0.78947 | 1.0526 | 1.0495 | 1.0453 | 1.0421 | 1.0326 | 1.0253 | 1.0168 | 1.0095 | 1.0011 | 0.94105 | 0.85684 | 0.77474 | 1.0421 | 1.0368 | 1.0284 | 1.0232 | 1.0137 | 1.0042 | 0.99474 | 0.98737 | 0.97789 | 0.91368 | 0.82526 | 0.74
|  | FOYERS | HT |  |  |  |  | 1.0537 | 1.0474 | 1.04 | 1.0316 | 1.0221 | 1.0126 | 1.0021 | 0.99368 | 0.98421 | 0.92526 | 0.83368 | 0.76842 | 1.0495 | 1.0453 | 1.04 | 1.0305 | 1.0221 | 1.0116 | 1.0021 | 0.99263 | 0.98526 | 0.91895 | 0.81684 | 0.74211 | 1.0368 | 1.0284 | 1.0211 | 1.0116 | 1.0021 | 0.99158 | 0.98105 | 0.97158 | 0.96316 | 0.89474 | 0.78947 | 0.71474
|  | FOYERS | HE |  |  |  |  | 1.0663 | 1.0621 | 1.0589 | 1.0547 | 1.0474 | 1.0411 | 1.0347 | 1.0284 | 1.0158 | 0.96526 | 0.90211 | 0.83053 | 1.0558 | 1.0537 | 1.0516 | 1.0484 | 1.0442 | 1.04 | 1.0368 | 1.0316 | 1.0189 | 0.96316 | 0.89368 | 0.81579 | 1.0368 | 1.0284 | 1.0211 | 1.0116 | 1.0021 | 0.99158 | 0.98105 | 0.97158 | 0.96316 | 0.89474 | 0.78947 | 0.71474
|  | FOYERS | CF |  |  |  |  | 1.0695 | 1.0674 | 1.0653 | 1.0632 | 1.06 | 1.0547 | 1.0537 | 1.0505 | 1.0442 | 1.0147 | 0.97474 | 0.92632 | 1.0579 | 1.0568 | 1.0558 | 1.0547 | 1.0526 | 1.0505 | 1.0495 | 1.0474 | 1.0453 | 1.0137 | 0.96737 | 0.91263 | 1.0537 | 1.0516 | 1.0495 | 1.0474 | 1.0432 | 1.0379 | 1.0358 | 1.0337 | 1.0253 | 0.99263 | 0.94421 | 0.88842
| FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | YES | 1.691 | 38.0743 | 37.4743 | 36.7806 | 35.9764 | 34.7122 | 33.6964 | 32.6301 | 31.4743 | 30.6701 | 24.8858 | 20.8353 | 19.0795 | 34.8385 | 34.1543 | 33.3553 | 32.4164 | 31.0511 | 30.0164 | 28.9374 | 27.7816 | 27.0522 | 21.749 | 18.2964 | 16.5785 | 36.9301 | 36.3406 | 35.6606 | 34.8153 | 33.4301 | 32.3227 | 31.1722 | 29.9237 | 29.0879 | 23.0437 | 18.7732 | 16.8879
|  | FRASERBURGH | EE |  |  |  |  | 38.3648 | 37.8774 | 37.3027 | 36.6311 | 35.489 | 34.4037 | 33.3143 | 32.2922 | 31.2174 | 24.8858 | 20.8353 | 19.0795 | 35.1669 | 34.6195 | 33.9637 | 33.189 | 31.9985 | 30.9164 | 29.8753 | 28.8816 | 27.8258 | 22.0164 | 18.2964 | 16.5785 | 37.2153 | 36.7353 | 36.1711 | 35.5016 | 34.2964 | 33.1301 | 31.9679 | 30.8722 | 29.7143 | 23.0437 | 18.7732 | 16.8879
|  | FRASERBURGH | HT |  |  |  |  | 38.0743 | 37.4743 | 36.7806 | 35.9764 | 34.7122 | 33.6964 | 32.6301 | 31.4743 | 30.6701 | 25.0058 | 22.1164 | 20.3564 | 34.8385 | 34.1543 | 33.3553 | 32.4164 | 31.0511 | 30.0164 | 28.9374 | 27.7816 | 27.0522 | 21.749 | 18.8048 | 16.9385 | 36.9301 | 36.3406 | 35.6606 | 34.8153 | 33.4301 | 32.3227 | 31.1722 | 29.9237 | 29.0879 | 23.0795 | 19.9427 | 18.0101
|  | FRASERBURGH | HE |  |  |  |  | 38.6101 | 38.3332 | 37.9269 | 37.3827 | 36.3111 | 35.4406 | 34.6079 | 33.749 | 32.8522 | 29.0827 | 26.0364 | 23.8711 | 35.4269 | 35.1174 | 34.6501 | 34.0079 | 32.909 | 32.0258 | 31.1911 | 30.3522 | 29.4637 | 26.0711 | 23.1164 | 21.2395 | 36.9301 | 36.3406 | 35.6606 | 34.8153 | 33.4301 | 32.3227 | 31.1722 | 29.9237 | 29.0879 | 23.0795 | 19.9427 | 18.0101
|  | FRASERBURGH | CF |  |  |  |  | 38.8143 | 38.709 | 38.5922 | 38.4595 | 38.1343 | 37.7816 | 37.4111 | 37.0437 | 36.6785 | 34.8606 | 32.8048 | 31.7048 | 35.6511 | 35.5416 | 35.4185 | 35.2764 | 34.9648 | 34.6122 | 34.2332 | 33.8501 | 33.4522 | 31.5732 | 29.5501 | 28.5353 | 37.6606 | 37.5553 | 37.4395 | 37.3079 | 36.9774 | 36.6216 | 36.2479 | 35.8816 | 35.5195 | 33.629 | 31.4353 | 30.269
| LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | YES | 0 | 5.8958 | 5.7926 | 5.6389 | 5.4811 | 5.1326 | 4.7589 | 4.3095 | 3.9074 | 3.4989 | -0.82737 | -3.6695 | -5.8958 | 5.7347 | 5.6105 | 5.4495 | 5.2789 | 4.98 | 4.6842 | 4.3389 | 4.0105 | 3.68 | -1.0021 | -3.8758 | -5.8221 | 5.5474 | 5.4211 | 5.2537 | 5.0811 | 4.7263 | 4.3611 | 3.9063 | 3.5074 | 3.1042 | -1.7979 | -4.8558 | -7.1421
|  | FRIOCKHEIM | EE |  |  |  |  | 5.9411 | 5.86 | 5.7526 | 5.6116 | 5.2126 | 4.7589 | 4.3095 | 3.9074 | 3.4989 | 0.65053 | -3.6695 | -5.8958 | 5.8137 | 5.7084 | 5.5779 | 5.4326 | 5.0926 | 4.7126 | 4.3389 | 4.0105 | 3.68 | 1.0737 | -3.2189 | -5.5674 | 5.6263 | 5.5147 | 5.38 | 5.2274 | 4.8211 | 4.3611 | 3.9063 | 3.5074 | 3.1042 | 0.095789 | -4.6421 | -7.1421
|  | FRIOCKHEIM | HT |  |  |  |  | 5.8958 | 5.7926 | 5.6389 | 5.4811 | 5.1326 | 4.7884 | 4.4442 | 4.0484 | 3.6495 | -0.82737 | -3.5558 | -5.3379 | 5.7347 | 5.6105 | 5.4495 | 5.2789 | 4.98 | 4.6842 | 4.3874 | 4.0526 | 3.7158 | -1.0021 | -3.8758 | -5.8221 | 5.5474 | 5.4211 | 5.2537 | 5.0811 | 4.7263 | 4.3758 | 4.0253 | 3.6232 | 3.2189 | -1.7979 | -4.8558 | -6.8832
|  | FRIOCKHEIM | HE |  |  |  |  | 6.0032 | 5.9611 | 5.9105 | 5.84 | 5.4463 | 5.1158 | 4.7916 | 4.4053 | 3.9074 | 1.7558 | -1.6821 | -4.3432 | 5.92 | 5.8611 | 5.7716 | 5.66 | 5.3347 | 5.0589 | 4.7926 | 4.4579 | 3.9811 | 1.9779 | -1.56 | -4.1674 | 5.5474 | 5.4211 | 5.2537 | 5.0811 | 4.7263 | 4.3758 | 4.0253 | 3.6232 | 3.2189 | -1.7979 | -4.8558 | -6.8832
|  | FRIOCKHEIM | CF |  |  |  |  | 6.04 | 6.0158 | 5.9895 | 5.9621 | 5.8168 | 5.6863 | 5.5589 | 5.4063 | 5.1853 | 4.1116 | 2.5642 | 0.96947 | 5.9758 | 5.9389 | 5.9 | 5.8547 | 5.7189 | 5.5926 | 5.4684 | 5.3158 | 5.0863 | 4.0421 | 2.5179 | 0.86105 | 5.7884 | 5.7526 | 5.7116 | 5.6653 | 5.5021 | 5.3526 | 5.2053 | 5.0326 | 4.7863 | 3.6274 | 1.94 | 0.15895
| KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 0.175 | -5.0476 | -5.1961 | -5.355 | -5.5192 | -6.2055 | -7.0297 | -9.3855 | -10.1182 | -12.9897 | -23.2582 | -32.0339 | -36.5466 | 1.4218 | 1.2724 | 1.1113 | 0.94395 | 0.35658 | -0.315 | -2.2761 | -2.8961 | -5.4013 | -14.9087 | -23.5476 | -28.4255 | -1.335 | -1.4224 | -1.5845 | -1.7529 | -2.415 | -3.1908 | -5.4571 | -6.2161 | -9.2024 | -20.1403 | -29.736 | -34.8266
|  | FYVIE | EE |  |  |  |  | -4.9739 | -5.1108 | -5.255 | -5.4087 | -6.1455 | -7.0297 | -9.3855 | -10.1182 | -12.9897 | -20.4992 | -30.2424 | -35.8066 | 1.4997 | 1.3703 | 1.2303 | 1.0797 | 0.445 | -0.315 | -2.2761 | -2.8961 | -5.2782 | -12.3234 | -21.3708 | -27.1234 | -1.2992 | -1.3876 | -1.4782 | -1.6329 | -2.3403 | -3.1908 | -5.4571 | -6.2161 | -9.2024 | -17.1929 | -27.6097 | -33.8192
|  | FYVIE | HT |  |  |  |  | -5.0476 | -5.1961 | -5.355 | -5.5192 | -6.2055 | -6.7655 | -8.8887 | -9.6108 | -12.9276 | -23.2582 | -32.0339 | -36.5466 | 1.4218 | 1.2724 | 1.1113 | 0.94395 | 0.35658 | -0.13079 | -1.9055 | -2.5213 | -5.4013 | -14.9087 | -23.5476 | -28.4255 | -1.335 | -1.4224 | -1.5845 | -1.7529 | -2.415 | -2.9539 | -4.9792 | -5.6908 | -9.1424 | -20.1403 | -29.736 | -34.8266
|  | FYVIE | HE |  |  |  |  | -4.8782 | -4.9476 | -5.0308 | -5.1203 | -5.8803 | -6.6761 | -8.2655 | -9.0666 | -11.2592 | -18.1097 | -24.9729 | -31.3234 | 1.5966 | 1.5303 | 1.445 | 1.3534 | 0.70711 | -0.008684 | -1.3908 | -2.115 | -4.075 | -10.3161 | -16.896 | -23.1424 | -1.335 | -1.4224 | -1.5845 | -1.7529 | -2.415 | -2.9539 | -4.9792 | -5.6908 | -9.1424 | -20.1403 | -29.736 | -34.8266
|  | FYVIE | CF |  |  |  |  | -4.8234 | -4.8634 | -4.9034 | -4.9455 | -5.2329 | -5.4992 | -5.8792 | -6.3603 | -6.8866 | -13.6255 | -17.2961 | -21.2676 | 1.6503 | 1.6134 | 1.5755 | 1.5355 | 1.2913 | 1.0618 | 0.70395 | 0.23026 | -0.30868 | -6.2403 | -9.8634 | -13.9582 | -1.2192 | -1.2424 | -1.2655 | -1.2876 | -1.5203 | -1.7245 | -2.0761 | -2.5676 | -3.1171 | -10.0129 | -14.0329 | -18.4634
| GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | NO | 0 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.095789 | 0.090526 | 0.086316 | 0.082105 | 0.077895 | 0.046316 | 0.011579 | -0.009474 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.095789 | 0.091579 | 0.088421 | 0.086316 | 0.081053 | 0.051579 | 0.02 | -0.001053 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.095789 | 0.090526 | 0.086316 | 0.082105 | 0.076842 | 0.043158 | 0.0063158 | -0.016842
|  | GARBAT FOREST | EE |  |  |  |  | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.095789 | 0.090526 | 0.086316 | 0.082105 | 0.077895 | 0.046316 | 0.011579 | -0.009474 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.096842 | 0.092632 | 0.089474 | 0.086316 | 0.081053 | 0.051579 | 0.02 | -0.001053 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.095789 | 0.090526 | 0.086316 | 0.082105 | 0.076842 | 0.043158 | 0.0063158 | -0.016842
|  | GARBAT FOREST | HT |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.098947 | 0.095789 | 0.093684 | 0.089474 | 0.086316 | 0.08 | 0.054737 | 0.029474 | 0.012632 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.096842 | 0.094737 | 0.091579 | 0.087368 | 0.082105 | 0.056842 | 0.031579 | 0.013684 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.095789 | 0.093684 | 0.089474 | 0.085263 | 0.078947 | 0.050526 | 0.023158 | 0.0031579
|  | GARBAT FOREST | HE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.095789 | 0.091579 | 0.087368 | 0.08421 | 0.078947 | 0.056842 | 0.031579 | 0.0052632 | 0.1 | 0.1 | 0.1 | 0.1 | 0.095789 | 0.091579 | 0.088421 | 0.086316 | 0.081053 | 0.061053 | 0.03579 | 0.011579 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.095789 | 0.093684 | 0.089474 | 0.085263 | 0.078947 | 0.050526 | 0.023158 | 0.0031579
|  | GARBAT FOREST | CF |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.096842 | 0.095789 | 0.092632 | 0.091579 | 0.081053 | 0.065263 | 0.049474 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.095789 | 0.092632 | 0.092632 | 0.081053 | 0.066316 | 0.049474 | 0.1 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.096842 | 0.094737 | 0.091579 | 0.091579 | 0.078947 | 0.062105 | 0.04421
| STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | 0 | 0.93368 | 0.91158 | 0.89053 | 2.3684 | 2.3463 | 2.3242 | 2.3053 | 2.2853 | 2.2663 | 2.1926 | 2.1326 | 2.0821 | 0.99474 | 0.97053 | 0.94737 | 2.4232 | 2.3989 | 2.3758 | 2.3537 | 2.3326 | 2.3116 | 2.2295 | 2.1611 | 2.1021 | 1.0674 | 1.0421 | 1.0189 | 2.4947 | 2.4705 | 2.4463 | 2.4253 | 2.4042 | 2.3821 | 2.3011 | 2.2326 | 2.1726
|  | GISLA | EE |  |  |  |  | 0.94737 | 0.93053 | 0.91263 | 2.3947 | 2.3768 | 2.3611 | 2.3432 | 2.3295 | 2.3147 | 2.2516 | 2.2063 | 2.1695 | 1.0105 | 0.99158 | 0.97263 | 2.4526 | 2.4337 | 2.4158 | 2.3979 | 2.3821 | 2.3663 | 2.2958 | 2.2442 | 2.2021 | 1.0821 | 1.0642 | 1.0442 | 2.5242 | 2.5053 | 2.4874 | 2.4684 | 2.4526 | 2.4368 | 2.3674 | 2.3147 | 2.2737
|  | GISLA | HT |  |  |  |  | 0.93368 | 0.91158 | 0.89053 | 2.3684 | 2.3463 | 2.3242 | 2.3053 | 2.2853 | 2.2663 | 2.1926 | 2.1326 | 2.0821 | 0.99474 | 0.97053 | 0.94737 | 2.4232 | 2.3989 | 2.3758 | 2.3537 | 2.3326 | 2.3116 | 2.2295 | 2.1611 | 2.1021 | 1.0674 | 1.0421 | 1.0189 | 2.4947 | 2.4705 | 2.4463 | 2.4253 | 2.4042 | 2.3821 | 2.3011 | 2.2326 | 2.1726
|  | GISLA | HE |  |  |  |  | 0.96842 | 0.95684 | 0.94526 | 2.4337 | 2.4211 | 2.4105 | 2.3989 | 2.3884 | 2.3779 | 2.3421 | 2.32 | 2.3032 | 1.0337 | 1.0211 | 1.0084 | 2.4958 | 2.4832 | 2.4705 | 2.4589 | 2.4484 | 2.4368 | 2.3979 | 2.3726 | 2.3526 | 1.0674 | 1.0421 | 1.0189 | 2.4947 | 2.4705 | 2.4463 | 2.4253 | 2.4042 | 2.3821 | 2.3011 | 2.2326 | 2.1726
|  | GISLA | CF |  |  |  |  | 0.98 | 0.97263 | 0.96526 | 2.4589 | 2.4516 | 2.4453 | 2.4379 | 2.4305 | 2.4242 | 2.3937 | 2.3716 | 2.3579 | 1.0463 | 1.0379 | 1.0305 | 2.5232 | 2.5147 | 2.5084 | 2.5 | 2.4926 | 2.4842 | 2.4516 | 2.4274 | 2.4105 | 1.1095 | 1.1042 | 1.0989 | 2.5937 | 2.5874 | 2.58 | 2.5726 | 2.5642 | 2.5568 | 2.5232 | 2.4979 | 2.4811
| ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | YES | 0 | 1.3795 | 1.3058 | 1.2374 | 1.1668 | 1.0847 | 1.0026 | 0.92368 | 0.85105 | 0.78053 | 0.46053 | -0.47421 | -0.66368 | 1.3647 | 1.2858 | 1.2121 | 1.1384 | 1.0511 | 0.96684 | 0.88474 | 0.81105 | 0.73842 | 0.40158 | -0.39526 | -0.60368 | 1.3584 | 1.2805 | 1.2068 | 1.1311 | 1.0437 | 0.95632 | 0.87316 | 0.79632 | 0.72158 | 0.37421 | -0.58368 | -0.79421
|  | GLASTULLICH | EE |  |  |  |  | 1.4258 | 1.3689 | 1.3121 | 1.2542 | 1.1889 | 1.1237 | 1.0542 | 0.99105 | 0.92789 | 0.65 | -0.20158 | -0.34579 | 1.4153 | 1.3553 | 1.2942 | 1.2332 | 1.1658 | 1.1016 | 1.0311 | 0.96579 | 0.90158 | 0.62263 | -0.095263 | -0.25421 | 1.4089 | 1.3489 | 1.2879 | 1.2268 | 1.1574 | 1.0889 | 1.0153 | 0.94789 | 0.88158 | 0.58684 | -0.28263 | -0.44474
|  | GLASTULLICH | HT |  |  |  |  | 1.3795 | 1.3058 | 1.2374 | 1.1668 | 1.0847 | 1.0026 | 0.92368 | 0.85105 | 0.78053 | 0.46053 | -0.47421 | -0.66368 | 1.3647 | 1.2858 | 1.2121 | 1.1384 | 1.0511 | 0.96684 | 0.88474 | 0.81105 | 0.73842 | 0.40158 | -0.39526 | -0.60368 | 1.3584 | 1.2805 | 1.2068 | 1.1311 | 1.0437 | 0.95632 | 0.87316 | 0.79632 | 0.72158 | 0.37421 | -0.58368 | -0.79421
|  | GLASTULLICH | HE |  |  |  |  | 1.4911 | 1.4563 | 1.4195 | 1.3795 | 1.3321 | 1.2858 | 1.2426 | 1.1995 | 1.1605 | 1.0047 | 0.62368 | 0.56474 | 1.4868 | 1.4489 | 1.41 | 1.3689 | 1.3216 | 1.2763 | 1.2332 | 1.1911 | 1.1521 | 0.99947 | 0.67842 | 0.61526 | 1.3584 | 1.2805 | 1.2068 | 1.1311 | 1.0437 | 0.95632 | 0.87316 | 0.79632 | 0.72158 | 0.37421 | -0.58368 | -0.79421
|  | GLASTULLICH | CF |  |  |  |  | 1.5258 | 1.5058 | 1.4837 | 1.4616 | 1.4353 | 1.4079 | 1.3826 | 1.3584 | 1.3332 | 1.2195 | 1.13 | 1.0647 | 1.5237 | 1.5016 | 1.4784 | 1.4553 | 1.4279 | 1.4005 | 1.3742 | 1.3489 | 1.3226 | 1.2047 | 1.1142 | 1.0489 | 1.5089 | 1.4932 | 1.4721 | 1.4489 | 1.4205 | 1.3921 | 1.3658 | 1.3395 | 1.3132 | 1.1911 | 1.0953 | 1.0237
| SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | NO | 0 | 2.72 | 2.6684 | 2.6158 | 2.5642 | 2.3105 | 2.0947 | 1.8874 | 1.7084 | 1.5253 | -0.35474 | -2.6147 | -4.4958 | 2.4568 | 2.4021 | 2.3453 | 2.2926 | 2.0358 | 1.8421 | 1.7 | 1.5537 | 1.3316 | -0.54737 | -3.0653 | -4.8716 | 2.5442 | 2.4905 | 2.4347 | 2.3811 | 2.1179 | 1.9116 | 1.72 | 1.5516 | 1.3695 | -0.68316 | -3.2158 | -5.3284
|  | GLEDFIELD | EE |  |  |  |  | 2.7526 | 2.7021 | 2.6537 | 2.6063 | 2.3421 | 2.0947 | 1.8874 | 1.7084 | 1.5253 | -0.35474 | -2.6147 | -4.4958 | 2.4916 | 2.4421 | 2.3947 | 2.3463 | 2.0884 | 1.8663 | 1.7 | 1.5537 | 1.4063 | -0.4779 | -2.7789 | -4.8526 | 2.5789 | 2.5274 | 2.4779 | 2.4284 | 2.1568 | 1.9126 | 1.72 | 1.5516 | 1.3695 | -0.68316 | -3.1705 | -5.3284
|  | GLEDFIELD | HT |  |  |  |  | 2.72 | 2.6684 | 2.6158 | 2.5642 | 2.3105 | 2.1021 | 1.9421 | 1.9011 | 1.6926 | -0.22526 | -2.5032 | -4.0916 | 2.4568 | 2.4021 | 2.3453 | 2.2926 | 2.0358 | 1.8421 | 1.7042 | 1.6611 | 1.4747 | -0.54737 | -3.0653 | -4.8716 | 2.5442 | 2.4905 | 2.4347 | 2.3811 | 2.1179 | 1.9116 | 1.7558 | 1.7137 | 1.5095 | -0.60737 | -3.2158 | -5.0537
|  | GLEDFIELD | HE |  |  |  |  | 2.7937 | 2.7695 | 2.7442 | 2.7179 | 2.4516 | 2.2589 | 2.0863 | 1.8737 | 1.54 | 0.14947 | -1.6505 | -3.6063 | 2.54 | 2.5147 | 2.4853 | 2.4589 | 2.2032 | 2.0263 | 1.8768 | 1.6768 | 1.3316 | -0.070526 | -1.9568 | -4.0137 | 2.5442 | 2.4905 | 2.4347 | 2.3811 | 2.1179 | 1.9116 | 1.7558 | 1.7137 | 1.5095 | -0.60737 | -3.2158 | -5.0537
|  | GLEDFIELD | CF |  |  |  |  | 2.8179 | 2.8032 | 2.7874 | 2.7737 | 2.6674 | 2.5853 | 2.5232 | 2.3874 | 2.2158 | 1.4674 | 0.32526 | -0.98632 | 2.5653 | 2.5495 | 2.5337 | 2.5189 | 2.4147 | 2.3389 | 2.2863 | 2.1368 | 1.9442 | 1.1589 | -0.045263 | -1.4832 | 2.6505 | 2.6337 | 2.6179 | 2.6021 | 2.4937 | 2.4126 | 2.3537 | 2.2053 | 2.0189 | 1.2305 | -0.046316 | -1.5463
| FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.088421 | 0.076842 | 0.067368 | 0.055789 | 0.037895 | -0.064211 | -0.20526 | -0.30421 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.089474 | 0.078947 | 0.068421 | 0.057895 | 0.037895 | -0.071579 | -0.23158 | -0.34526 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.093684 | 0.085263 | 0.077895 | 0.068421 | 0.042105 | -0.083158 | -0.24632 | -0.36211
|  | GLEN LAOGH | EE |  |  |  |  | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.092632 | 0.085263 | 0.077895 | 0.071579 | 0.055789 | -0.056842 | -0.18526 | -0.30421 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.094737 | 0.088421 | 0.083158 | 0.077895 | 0.061053 | -0.056842 | -0.19158 | -0.32526 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.093684 | 0.085263 | 0.077895 | 0.071579 | 0.053684 | -0.072632 | -0.21684 | -0.35368
|  | GLEN LAOGH | HT |  |  |  |  | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.093684 | 0.089474 | 0.078947 | 0.069474 | 0.047368 | -0.064211 | -0.20526 | -0.30421 | 0.1 | 0.1 | 0.1 | 0.1 | 0.095789 | 0.092632 | 0.082105 | 0.072632 | 0.048421 | -0.071579 | -0.23158 | -0.34526 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.094737 | 0.089474 | 0.077895 | 0.068421 | 0.042105 | -0.083158 | -0.24632 | -0.36211
|  | GLEN LAOGH | HE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.088421 | 0.076842 | 0.067368 | 0.055789 | 0.037895 | -0.04 | -0.14632 | -0.26421 | 0.1 | 0.1 | 0.1 | 0.1 | 0.089474 | 0.078947 | 0.068421 | 0.057895 | 0.037895 | -0.043158 | -0.1579 | -0.28526 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.094737 | 0.089474 | 0.077895 | 0.068421 | 0.042105 | -0.083158 | -0.24632 | -0.36211
|  | GLEN LAOGH | CF |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.095789 | 0.086316 | 0.077895 | 0.068421 | 0.025263 | -0.043158 | -0.12421 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.087368 | 0.077895 | 0.066316 | 0.02 | -0.053684 | -0.14632 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.097895 | 0.096842 | 0.085263 | 0.075789 | 0.064211 | 0.01579 | -0.062105 | -0.15579
| KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 0 | 3.2205 | 3.1921 | 3.1616 | 3.1311 | 3.0953 | 3.0616 | 3.0289 | 2.9963 | 2.9637 | 2.8332 | 2.7226 | 2.5721 | 3.2184 | 3.1784 | 3.1258 | 3.0753 | 3.0163 | 2.9595 | 2.9047 | 2.8553 | 2.8089 | 2.5953 | 2.4153 | 2.2584 | 3.4689 | 3.4395 | 3.3847 | 3.3332 | 3.2711 | 3.2089 | 3.1511 | 3.0984 | 3.0479 | 2.8153 | 2.6205 | 2.4521
|  | GLENCOE | EE |  |  |  |  | 3.2311 | 3.2026 | 3.17 | 3.1384 | 3.1026 | 3.0668 | 3.0342 | 3.0005 | 2.9689 | 2.8332 | 2.7353 | 2.5889 | 3.2332 | 3.2068 | 3.1626 | 3.1163 | 3.0689 | 3.0184 | 2.9679 | 2.9174 | 2.8753 | 2.6658 | 2.49 | 2.3437 | 3.4774 | 3.4458 | 3.4079 | 3.3626 | 3.3079 | 3.2521 | 3.1942 | 3.1363 | 3.0889 | 2.8479 | 2.6416 | 2.4721
|  | GLENCOE | HT |  |  |  |  | 3.2205 | 3.1921 | 3.1616 | 3.1311 | 3.0953 | 3.0616 | 3.0289 | 2.9963 | 2.9637 | 2.8542 | 2.7226 | 2.5721 | 3.2184 | 3.1784 | 3.1258 | 3.0753 | 3.0163 | 2.9595 | 2.9047 | 2.8553 | 2.8089 | 2.5953 | 2.4153 | 2.2584 | 3.4689 | 3.4395 | 3.3847 | 3.3332 | 3.2711 | 3.2089 | 3.1511 | 3.0984 | 3.0479 | 2.8153 | 2.6205 | 2.4521
|  | GLENCOE | HE |  |  |  |  | 3.2584 | 3.2416 | 3.2226 | 3.2037 | 3.1784 | 3.1563 | 3.1342 | 3.1132 | 3.0932 | 3.0174 | 2.9679 | 2.9268 | 3.2584 | 3.2426 | 3.2247 | 3.2068 | 3.1847 | 3.1658 | 3.1363 | 3.1089 | 3.0847 | 2.9826 | 2.9079 | 2.8458 | 3.4689 | 3.4395 | 3.3847 | 3.3332 | 3.2711 | 3.2089 | 3.1511 | 3.0984 | 3.0479 | 2.8153 | 2.6205 | 2.4521
|  | GLENCOE | CF |  |  |  |  | 3.2742 | 3.2658 | 3.2563 | 3.2479 | 3.2363 | 3.2268 | 3.2153 | 3.2068 | 3.1963 | 3.1511 | 3.1226 | 3.1047 | 3.2742 | 3.2658 | 3.2563 | 3.2479 | 3.2384 | 3.2289 | 3.2184 | 3.21 | 3.1995 | 3.1395 | 3.0858 | 3.0447 | 3.5226 | 3.5142 | 3.5058 | 3.4963 | 3.4858 | 3.4753 | 3.4647 | 3.4553 | 3.4447 | 3.3963 | 3.3353 | 3.2889
| DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0 | 0.024474 | 0.0023684 | -0.018684 | -0.041842 | -0.082895 | -0.12395 | -0.16921 | -0.20921 | -0.24816 | -0.45026 | -0.64395 | -0.75342 | 0.0097368 | -0.011316 | -0.034474 | -0.057632 | -0.094474 | -0.13132 | -0.17026 | -0.20711 | -0.24289 | -0.42605 | -0.60184 | -0.70816 | -0.000789 | -0.022895 | -0.047105 | -0.070263 | -0.11237 | -0.15553 | -0.20395 | -0.24605 | -0.28816 | -0.50184 | -0.70605 | -0.8229
|  | GLENDARUEL | EE |  |  |  |  | 0.024474 | 0.0023684 | -0.018684 | -0.041842 | -0.082895 | -0.12395 | -0.16921 | -0.20921 | -0.24816 | -0.45026 | -0.64395 | -0.75342 | 0.0097368 | -0.011316 | -0.034474 | -0.057632 | -0.094474 | -0.13132 | -0.17026 | -0.20711 | -0.24289 | -0.42605 | -0.60184 | -0.70816 | -0.000789 | -0.022895 | -0.047105 | -0.070263 | -0.11237 | -0.15553 | -0.20395 | -0.24605 | -0.28816 | -0.50184 | -0.70605 | -0.8229
|  | GLENDARUEL | HT |  |  |  |  | 0.033947 | 0.022368 | 0.013947 | 0.0044737 | -0.020789 | -0.046053 | -0.071316 | -0.098684 | -0.1271 | -0.24289 | -0.3429 | -0.41447 | 0.016053 | 0.0044737 | -0.005 | -0.016579 | -0.039737 | -0.063947 | -0.087105 | -0.11237 | -0.13868 | -0.24921 | -0.33026 | -0.38921 | 0.0076316 | -0.005 | -0.015526 | -0.027105 | -0.054474 | -0.081842 | -0.11026 | -0.13868 | -0.17026 | -0.30079 | -0.41132 | -0.49237
|  | GLENDARUEL | HE |  |  |  |  | 0.040263 | 0.031842 | 0.024474 | 0.016053 | -0.010263 | -0.036579 | -0.059737 | -0.083947 | -0.10921 | -0.22079 | -0.32184 | -0.42921 | 0.024474 | 0.016053 | 0.0086842 | 0.0013158 | -0.021842 | -0.043947 | -0.065 | -0.085 | -0.10605 | -0.20289 | -0.29553 | -0.39132 | 0.0076316 | -0.005 | -0.015526 | -0.027105 | -0.054474 | -0.081842 | -0.11026 | -0.13868 | -0.17026 | -0.30079 | -0.41132 | -0.49237
|  | GLENDARUEL | CF |  |  |  |  | 0.35921 | 0.35816 | 0.35605 | 0.35395 | 0.34447 | 0.33605 | 0.32868 | 0.32132 | 0.31605 | 0.275 | 0.21289 | 0.16658 | 0.33816 | 0.33605 | 0.335 | 0.33395 | 0.32868 | 0.32342 | 0.31921 | 0.315 | 0.30974 | 0.26553 | 0.21079 | 0.17079 | 0.34868 | 0.34658 | 0.34447 | 0.34237 | 0.33395 | 0.32447 | 0.31711 | 0.30974 | 0.30447 | 0.25184 | 0.18553 | 0.13816
| ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 0.14 | 2.7137 | 2.6474 | 2.5811 | 2.5126 | 2.1789 | 1.7137 | 1.2874 | 0.92316 | 0.54632 | -2.2853 | -5.6895 | -7.9695 | 2.8674 | 2.8011 | 2.7368 | 2.6684 | 2.3916 | 2.0032 | 1.6474 | 1.3442 | 1.0295 | -1.5853 | -4.8263 | -7.2168 | 2.7021 | 2.6558 | 2.6095 | 2.5621 | 2.2442 | 1.8053 | 1.3547 | 0.96947 | 0.57263 | -2.4547 | -6.1221 | -8.6758
|  | GLENDEVON | EE |  |  |  |  | 2.7442 | 2.6789 | 2.6137 | 2.5463 | 2.1789 | 1.7137 | 1.2874 | 0.92316 | 0.54632 | -2.2853 | -5.6895 | -7.9695 | 2.9011 | 2.8421 | 2.7811 | 2.7189 | 2.4095 | 2.0032 | 1.6474 | 1.3442 | 1.0295 | -1.5853 | -4.8263 | -7.2168 | 2.7168 | 2.6674 | 2.6168 | 2.5663 | 2.2442 | 1.8053 | 1.3547 | 0.96947 | 0.57263 | -2.4547 | -6.1221 | -8.6758
|  | GLENDEVON | HT |  |  |  |  | 2.7137 | 2.6474 | 2.5811 | 2.5126 | 2.1926 | 1.8895 | 1.5853 | 1.2021 | 0.76842 | -1.7442 | -4.4968 | -6.2968 | 2.8674 | 2.8011 | 2.7368 | 2.6684 | 2.3916 | 2.1316 | 1.8716 | 1.5389 | 1.1495 | -1.3126 | -4.2063 | -6.1589 | 2.7021 | 2.6558 | 2.6095 | 2.5621 | 2.2884 | 1.9989 | 1.6768 | 1.2716 | 0.80947 | -1.8874 | -4.9916 | -7.0632
|  | GLENDEVON | HE |  |  |  |  | 2.7789 | 2.7589 | 2.7326 | 2.7011 | 2.3095 | 1.9779 | 1.6768 | 1.3789 | 0.90526 | -1.2421 | -3.7474 | -6.4663 | 2.9368 | 2.9168 | 2.8926 | 2.8611 | 2.5263 | 2.2421 | 1.9905 | 1.7432 | 1.2926 | -0.73263 | -3.2 | -5.8842 | 2.7021 | 2.6558 | 2.6095 | 2.5621 | 2.2884 | 1.9989 | 1.6768 | 1.2716 | 0.80947 | -1.8874 | -4.9916 | -7.0632
|  | GLENDEVON | CF |  |  |  |  | 2.7937 | 2.7832 | 2.7705 | 2.7579 | 2.6232 | 2.5021 | 2.3779 | 2.2716 | 2.1232 | 1.0674 | -0.49789 | -2.1274 | 2.9516 | 2.9411 | 2.9295 | 2.9179 | 2.8053 | 2.7021 | 2.5979 | 2.5063 | 2.3589 | 1.3242 | -0.22947 | -1.9221 | 2.7611 | 2.7505 | 2.7389 | 2.7263 | 2.6021 | 2.4937 | 2.3853 | 2.2937 | 2.2242 | 1.1032 | -0.59053 | -2.4305
| FORT AUGUSTUS | GLENDOE | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 0 | 7.6895 | 7.6642 | 7.6389 | 7.6116 | 7.3274 | 7.2842 | 7.2389 | 7.1989 | 7.16 | 6.96 | 6.6284 | 6.2347 | 7.58 | 7.5674 | 7.5547 | 7.5326 | 7.2021 | 7.1695 | 7.1326 | 7.1021 | 7.0705 | 6.9147 | 6.5337 | 6.1537 | 7.6863 | 7.6568 | 7.6232 | 7.5853 | 7.2137 | 7.1695 | 7.1221 | 7.0789 | 7.0358 | 6.8232 | 6.44 | 5.9632
|  | GLENDOE | EE |  |  |  |  | 7.6895 | 7.6642 | 7.6389 | 7.6116 | 7.3274 | 7.2842 | 7.2389 | 7.1989 | 7.16 | 6.96 | 6.6284 | 6.2347 | 7.5811 | 7.5695 | 7.5547 | 7.5326 | 7.2021 | 7.1695 | 7.1326 | 7.1021 | 7.0705 | 6.9147 | 6.5884 | 6.1537 | 7.6863 | 7.6568 | 7.6232 | 7.5853 | 7.2137 | 7.1695 | 7.1221 | 7.0789 | 7.0358 | 6.8232 | 6.44 | 5.9632
|  | GLENDOE | HT |  |  |  |  | 7.6937 | 7.6758 | 7.6611 | 7.6347 | 7.36 | 7.3295 | 7.2979 | 7.2632 | 7.2316 | 7.0989 | 6.7095 | 6.3789 | 7.58 | 7.5674 | 7.5558 | 7.5411 | 7.2095 | 7.1832 | 7.1547 | 7.1253 | 7.0979 | 6.9832 | 6.5337 | 6.16 | 7.6874 | 7.66 | 7.6284 | 7.5968 | 7.2537 | 7.22 | 7.1874 | 7.1516 | 7.1179 | 6.9768 | 6.4979 | 6.1095
|  | GLENDOE | HE |  |  |  |  | 7.7074 | 7.6968 | 7.6853 | 7.6747 | 7.4074 | 7.3811 | 7.3547 | 7.3295 | 7.3053 | 7.1947 | 6.9347 | 6.5926 | 7.5926 | 7.5842 | 7.5779 | 7.5695 | 7.2642 | 7.2421 | 7.2211 | 7.2 | 7.18 | 7.0937 | 6.8147 | 6.4326 | 7.6874 | 7.66 | 7.6284 | 7.5968 | 7.2537 | 7.22 | 7.1874 | 7.1516 | 7.1179 | 6.9768 | 6.4979 | 6.1095
|  | GLENDOE | CF |  |  |  |  | 7.7158 | 7.7116 | 7.7063 | 7.7011 | 7.6116 | 7.6 | 7.5884 | 7.5789 | 7.5705 | 7.4968 | 7.3021 | 7.0737 | 7.5979 | 7.5937 | 7.5895 | 7.5874 | 7.4989 | 7.4874 | 7.4789 | 7.4684 | 7.4611 | 7.3884 | 7.1684 | 6.8989 | 7.7232 | 7.7168 | 7.7084 | 7.7021 | 7.56 | 7.5474 | 7.5358 | 7.5263 | 7.5147 | 7.4347 | 7.1989 | 6.9158
| BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | 2.06 | 16.3384 | 16.1679 | 15.9868 | 15.6574 | 14.8216 | 14.0479 | 13.2553 | 12.31 | 11.2163 | 7.4468 | 2.6142 | -1.5468 | 14.2442 | 13.7884 | 13.3621 | 12.8484 | 12.0347 | 11.2853 | 10.5158 | 9.5926 | 8.4863 | 5.4084 | 0.73684 | -3.6611 | 14.9655 | 14.5455 | 14.1497 | 13.6782 | 12.7845 | 11.9434 | 11.0803 | 10.0434 | 8.8255 | 4.8318 | -0.3629 | -5.0608
|  | GLENEAGLES | EE |  |  |  |  | 16.43 | 16.2911 | 16.0984 | 15.95 | 15.1111 | 14.1184 | 13.2584 | 12.4605 | 11.5026 | 7.4468 | 2.6142 | -1.5468 | 14.4347 | 14.0421 | 13.6474 | 13.2389 | 12.44 | 11.4968 | 10.7242 | 9.9905 | 9.0579 | 5.4084 | 0.88947 | -3.6611 | 15.0687 | 14.7782 | 14.3634 | 13.9855 | 13.0929 | 12.0245 | 11.1045 | 10.2445 | 9.1876 | 4.8318 | -0.3629 | -5.0608
|  | GLENEAGLES | HT |  |  |  |  | 16.3384 | 16.1679 | 15.9868 | 15.6574 | 14.8216 | 14.0479 | 13.2553 | 12.31 | 11.2163 | 8.4458 | 3.7195 | 0.21526 | 14.2442 | 13.7884 | 13.3621 | 12.8484 | 12.0347 | 11.2853 | 10.5158 | 9.5926 | 8.4863 | 6.0526 | 0.73684 | -3.1526 | 14.9655 | 14.5455 | 14.1497 | 13.6782 | 12.7845 | 11.9434 | 11.0803 | 10.0434 | 8.8255 | 5.9718 | 0.45711 | -3.5397
|  | GLENEAGLES | HE |  |  |  |  | 16.5395 | 16.4574 | 16.3679 | 16.2732 | 15.6363 | 14.8111 | 14.0847 | 13.3079 | 12.4626 | 9.8426 | 5.5121 | 0.86368 | 14.6779 | 14.38 | 14.1095 | 13.7674 | 12.9632 | 12.1495 | 11.4632 | 10.7095 | 9.8663 | 7.5832 | 3.0021 | -1.7989 | 14.9655 | 14.5455 | 14.1497 | 13.6782 | 12.7845 | 11.9434 | 11.0803 | 10.0434 | 8.8255 | 5.9718 | 0.45711 | -3.5397
|  | GLENEAGLES | CF |  |  |  |  | 16.6089 | 16.5616 | 16.5142 | 16.4647 | 16.2447 | 16.05 | 15.8553 | 15.6826 | 15.5468 | 13.8858 | 11.2753 | 8.45 | 14.8411 | 14.7084 | 14.5653 | 14.4211 | 14.1505 | 13.8747 | 13.5705 | 13.3021 | 12.9926 | 11.2905 | 8.5558 | 5.3874 | 15.2476 | 15.2003 | 15.1529 | 15.1045 | 14.8182 | 14.5118 | 14.1792 | 13.8897 | 13.5803 | 11.7582 | 8.7813 | 5.4624
| RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0 | 0.26 | 0.24421 | 0.22421 | 0.20211 | 0.18 | 0.16 | 0.14 | 0.12 | 0.097895 | 0.0031579 | -0.08 | -0.16526 | 0.25579 | 0.23684 | 0.21474 | 0.19474 | 0.17263 | 0.15263 | 0.13474 | 0.11474 | 0.094737 | 0.0010526 | -0.078947 | -0.1621 | 0.27053 | 0.24947 | 0.22842 | 0.20526 | 0.18316 | 0.16316 | 0.14316 | 0.12316 | 0.10105 | 0.0042105 | -0.078947 | -0.16421
|  | GLENETIVE | EE |  |  |  |  | 0.26 | 0.24421 | 0.22421 | 0.20211 | 0.18 | 0.16 | 0.14 | 0.12 | 0.097895 | 0.0031579 | -0.08 | -0.16526 | 0.25579 | 0.23684 | 0.21474 | 0.19474 | 0.17263 | 0.15263 | 0.13474 | 0.11474 | 0.094737 | 0.0010526 | -0.078947 | -0.1621 | 0.27053 | 0.24947 | 0.22842 | 0.20526 | 0.18316 | 0.16316 | 0.14316 | 0.12316 | 0.10105 | 0.0042105 | -0.078947 | -0.16421
|  | GLENETIVE | HT |  |  |  |  | 0.26737 | 0.26421 | 0.26 | 0.25368 | 0.24842 | 0.24211 | 0.23579 | 0.23053 | 0.22421 | 0.19368 | 0.16421 | 0.13368 | 0.26632 | 0.26 | 0.25368 | 0.24737 | 0.24211 | 0.23579 | 0.22947 | 0.22316 | 0.21684 | 0.18421 | 0.15263 | 0.12105 | 0.28211 | 0.27579 | 0.26947 | 0.26211 | 0.25684 | 0.24947 | 0.24316 | 0.23789 | 0.23158 | 0.19789 | 0.16421 | 0.13053
|  | GLENETIVE | HE |  |  |  |  | 0.26737 | 0.26421 | 0.26 | 0.25684 | 0.25263 | 0.24632 | 0.24105 | 0.23684 | 0.23053 | 0.2 | 0.16842 | 0.13579 | 0.26737 | 0.26316 | 0.25789 | 0.25158 | 0.24737 | 0.24 | 0.23368 | 0.22842 | 0.22316 | 0.19158 | 0.16 | 0.12842 | 0.28211 | 0.27579 | 0.26947 | 0.26211 | 0.25684 | 0.24947 | 0.24316 | 0.23789 | 0.23158 | 0.19789 | 0.16421 | 0.13053
|  | GLENETIVE | CF |  |  |  |  | 0.26947 | 0.26842 | 0.26737 | 0.26737 | 0.26632 | 0.26526 | 0.26526 | 0.26421 | 0.26316 | 0.26 | 0.25474 | 0.24842 | 0.27158 | 0.27053 | 0.26842 | 0.26737 | 0.26632 | 0.26421 | 0.26316 | 0.26211 | 0.26 | 0.25368 | 0.24737 | 0.24211 | 0.28842 | 0.28632 | 0.28526 | 0.28316 | 0.28211 | 0.28105 | 0.27895 | 0.27684 | 0.27579 | 0.26947 | 0.26316 | 0.25579
| FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | NO | 0 | 0.12105 | 0.12 | 0.11895 | 0.11789 | 0.11684 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.10737 | 0.10421 | 0.098947 | 0.11158 | 0.11053 | 0.10947 | 0.10842 | 0.10737 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.098947 | 0.095789 | 0.089474 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.10842 | 0.10316 | 0.1 | 0.093684
|  | GLENUIG | EE |  |  |  |  | 0.12105 | 0.12105 | 0.12 | 0.11895 | 0.11789 | 0.11789 | 0.11684 | 0.11579 | 0.11579 | 0.11158 | 0.10842 | 0.10632 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10842 | 0.10842 | 0.10737 | 0.10632 | 0.10632 | 0.10421 | 0.1 | 0.098947 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.11263 | 0.11158 | 0.11053 | 0.11053 | 0.10842 | 0.10421 | 0.10316
|  | GLENUIG | HT |  |  |  |  | 0.12105 | 0.12 | 0.11895 | 0.11789 | 0.11684 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.10737 | 0.10421 | 0.098947 | 0.11158 | 0.11053 | 0.10947 | 0.10842 | 0.10737 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.098947 | 0.095789 | 0.089474 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.10842 | 0.10316 | 0.1 | 0.093684
|  | GLENUIG | HE |  |  |  |  | 0.12211 | 0.12105 | 0.12105 | 0.12 | 0.12 | 0.11895 | 0.11895 | 0.11789 | 0.11789 | 0.11684 | 0.11579 | 0.11579 | 0.11263 | 0.11158 | 0.11158 | 0.11053 | 0.11053 | 0.10947 | 0.10947 | 0.10842 | 0.10842 | 0.10737 | 0.10632 | 0.10632 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.10842 | 0.10316 | 0.1 | 0.093684
|  | GLENUIG | CF |  |  |  |  | 0.12211 | 0.12211 | 0.12211 | 0.12211 | 0.12105 | 0.12105 | 0.12105 | 0.12105 | 0.12 | 0.11895 | 0.11895 | 0.11895 | 0.11263 | 0.11263 | 0.11263 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.10947 | 0.11684 | 0.11684 | 0.11684 | 0.11684 | 0.11579 | 0.11579 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11368 | 0.11368
| BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | YES | 0 | 3.44 | 3.4011 | 3.3442 | 3.2853 | 3.1053 | 2.9168 | 2.7232 | 2.5779 | 2.4326 | 1.1789 | -0.46737 | -1.7411 | 3.1453 | 3.0768 | 3.0095 | 2.9442 | 2.7547 | 2.5674 | 2.3758 | 2.2495 | 2.1242 | 0.80105 | -1.0653 | -2.4021 | 3.2505 | 3.1874 | 3.12 | 3.0547 | 2.8526 | 2.6526 | 2.4474 | 2.2989 | 2.1505 | 0.76105 | -1.1221 | -2.4842
|  | GOLSPIE | EE |  |  |  |  | 3.4579 | 3.4232 | 3.3874 | 3.3389 | 3.2042 | 3.0484 | 2.8411 | 2.6463 | 2.4432 | 1.2232 | -0.39053 | -1.7411 | 3.1874 | 3.1326 | 3.0747 | 3.0158 | 2.8979 | 2.7663 | 2.5632 | 2.3758 | 2.1821 | 0.98632 | -0.68105 | -2.2147 | 3.2684 | 3.2337 | 3.1779 | 3.1179 | 2.9768 | 2.8158 | 2.5884 | 2.38 | 2.1663 | 0.85158 | -0.93579 | -2.4842
|  | GOLSPIE | HT |  |  |  |  | 3.44 | 3.4011 | 3.3442 | 3.2853 | 3.1053 | 2.9168 | 2.7232 | 2.5779 | 2.4326 | 1.1789 | -0.46737 | -1.6411 | 3.1453 | 3.0768 | 3.0095 | 2.9442 | 2.7547 | 2.5674 | 2.3758 | 2.2495 | 2.1242 | 0.80105 | -1.0653 | -2.4021 | 3.2505 | 3.1874 | 3.12 | 3.0547 | 2.8526 | 2.6526 | 2.4474 | 2.2989 | 2.1505 | 0.76105 | -1.1221 | -2.48
|  | GOLSPIE | HE |  |  |  |  | 3.4863 | 3.4653 | 3.4442 | 3.42 | 3.3116 | 3.1895 | 3.0295 | 2.8789 | 2.6389 | 1.6305 | 0.34947 | -1.0368 | 3.2495 | 3.2147 | 3.1821 | 3.1463 | 3.0368 | 2.9084 | 2.7474 | 2.5968 | 2.3442 | 1.3189 | -0.055789 | -1.5453 | 3.2505 | 3.1874 | 3.12 | 3.0547 | 2.8526 | 2.6526 | 2.4474 | 2.2989 | 2.1505 | 0.76105 | -1.1221 | -2.48
|  | GOLSPIE | CF |  |  |  |  | 3.5053 | 3.4937 | 3.4821 | 3.4705 | 3.4284 | 3.3895 | 3.3516 | 3.2653 | 3.1505 | 2.5989 | 1.7821 | 0.85158 | 3.2832 | 3.2621 | 3.2421 | 3.2211 | 3.1737 | 3.1295 | 3.0758 | 2.9568 | 2.8095 | 2.2232 | 1.3442 | 0.29263 | 3.3168 | 3.3053 | 3.2926 | 3.2811 | 3.24 | 3.2011 | 3.1568 | 3.0358 | 2.8937 | 2.2916 | 1.3747 | 0.30842
| BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 0.07 | 14.6392 | 14.4487 | 14.2487 | 14.0371 | 13.7971 | 13.4624 | 13.0539 | 12.6803 | 12.3434 | 10.9666 | 10.0003 | 9.1571 | 13.2405 | 13.0163 | 12.7658 | 12.3889 | 11.9142 | 11.4847 | 11.0353 | 10.6268 | 10.2616 | 8.8205 | 7.7458 | 6.7963 | 13.7204 | 13.5299 | 13.2941 | 12.8214 | 12.3509 | 11.9267 | 11.4814 | 11.0762 | 10.7151 | 9.2351 | 8.1593 | 7.2088
|  | GOODLYBURN | EE |  |  |  |  | 14.7476 | 14.6108 | 14.4666 | 14.3161 | 14.1561 | 14.0024 | 13.8076 | 13.5382 | 13.2718 | 12.0466 | 11.3445 | 10.7508 | 13.3658 | 13.2111 | 13.0321 | 12.8405 | 12.6037 | 12.1668 | 11.85 | 11.5574 | 11.2668 | 9.9868 | 9.2016 | 8.53 | 13.8288 | 13.692 | 13.5478 | 13.392 | 13.0278 | 12.5993 | 12.2857 | 11.9941 | 11.7057 | 10.393 | 9.6151 | 8.9414
|  | GOODLYBURN | HT |  |  |  |  | 14.6392 | 14.4487 | 14.2487 | 14.0371 | 13.7971 | 13.4624 | 13.0539 | 12.6803 | 12.3434 | 10.9666 | 10.0003 | 9.1571 | 13.2405 | 13.0163 | 12.7658 | 12.3889 | 11.9142 | 11.4847 | 11.0353 | 10.6268 | 10.2616 | 8.8205 | 7.7458 | 6.7963 | 13.7204 | 13.5299 | 13.2941 | 12.8214 | 12.3509 | 11.9267 | 11.4814 | 11.0762 | 10.7151 | 9.2351 | 8.1593 | 7.2088
|  | GOODLYBURN | HE |  |  |  |  | 14.8655 | 14.7634 | 14.6518 | 14.5329 | 14.4024 | 14.2824 | 14.1645 | 14.0529 | 13.9518 | 13.3718 | 12.9887 | 12.7055 | 13.4963 | 13.3932 | 13.2637 | 13.1132 | 12.9426 | 12.7616 | 12.4868 | 12.2679 | 12.09 | 11.4121 | 10.9847 | 10.6616 | 13.7204 | 13.5299 | 13.2941 | 12.8214 | 12.3509 | 11.9267 | 11.4814 | 11.0762 | 10.7151 | 9.2351 | 8.1593 | 7.2088
|  | GOODLYBURN | CF |  |  |  |  | 14.9424 | 14.8813 | 14.8182 | 14.7539 | 14.6866 | 14.6171 | 14.5497 | 14.4813 | 14.4139 | 14.1224 | 13.9676 | 13.7266 | 13.5732 | 13.5121 | 13.4489 | 13.3774 | 13.3026 | 13.2226 | 13.1247 | 13.0384 | 12.95 | 12.45 | 12.0532 | 11.7511 | 14.0236 | 13.9625 | 13.8993 | 13.8351 | 13.7678 | 13.6993 | 13.632 | 13.5636 | 13.4962 | 12.8772 | 12.4836 | 12.1846
| CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | YES | 0.091 | 6.6585 | 6.4385 | 6.1743 | 5.8901 | 5.4511 | 5.1627 | 4.8679 | 4.3343 | 3.9648 | 2.9322 | 1.8627 | 0.31426 | 6.0353 | 5.7764 | 5.4637 | 5.1437 | 4.6806 | 4.3964 | 4.1037 | 3.5385 | 3.1669 | 2.3585 | 1.2079 | -0.26258 | 6.1753 | 5.9658 | 5.7006 | 5.3848 | 4.9006 | 4.5901 | 4.2711 | 3.6806 | 3.2764 | 2.2153 | 1.109 | -0.61942
|  | GOURDIE | EE |  |  |  |  | 6.7311 | 6.5479 | 6.3279 | 6.0816 | 5.6732 | 5.2501 | 4.8722 | 4.5827 | 4.2553 | 2.9322 | 1.8627 | 0.31426 | 6.1185 | 5.9037 | 5.6416 | 5.3616 | 4.9406 | 4.5153 | 4.1458 | 3.8679 | 3.549 | 2.3585 | 1.4785 | -0.21732 | 6.2458 | 6.0711 | 5.8616 | 5.5953 | 5.1458 | 4.6827 | 4.2732 | 3.9595 | 3.6048 | 2.2153 | 1.109 | -0.61942
|  | GOURDIE | HT |  |  |  |  | 6.6585 | 6.4385 | 6.1743 | 5.8901 | 5.4511 | 5.1627 | 4.8679 | 4.3343 | 3.9648 | 3.1143 | 1.9501 | 0.64058 | 6.0353 | 5.7764 | 5.4637 | 5.1437 | 4.6806 | 4.3964 | 4.1037 | 3.5385 | 3.1669 | 2.4143 | 1.2079 | -0.26258 | 6.1753 | 5.9658 | 5.7006 | 5.3848 | 4.9006 | 4.5901 | 4.2711 | 3.6806 | 3.2764 | 2.3932 | 1.1195 | -0.351
|  | GOURDIE | HE |  |  |  |  | 6.7837 | 6.6479 | 6.4616 | 6.249 | 5.849 | 5.4469 | 5.1027 | 4.6869 | 4.4501 | 3.6627 | 2.8816 | 1.2132 | 6.1743 | 6.0101 | 5.7837 | 5.5332 | 5.1269 | 4.7069 | 4.3543 | 3.9185 | 3.6922 | 3.0006 | 2.3111 | 0.59321 | 6.1753 | 5.9658 | 5.7006 | 5.3848 | 4.9006 | 4.5901 | 4.2711 | 3.6806 | 3.2764 | 2.3932 | 1.1195 | -0.351
|  | GOURDIE | CF |  |  |  |  | 6.8101 | 6.7932 | 6.7753 | 6.7469 | 6.6364 | 6.5016 | 6.3416 | 6.1722 | 5.9785 | 5.3501 | 4.7785 | 3.7058 | 6.3069 | 6.2458 | 6.2048 | 6.1343 | 6.0258 | 5.8858 | 5.709 | 5.5206 | 5.3027 | 4.6648 | 4.1227 | 2.9511 | 6.4037 | 6.3532 | 6.3185 | 6.2616 | 6.1564 | 6.0301 | 5.8785 | 5.7069 | 5.4848 | 4.7974 | 4.1774 | 2.9701
| BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 0 | 12.8463 | 12.6832 | 12.5189 | 12.3589 | 12.1832 | 12.0126 | 11.8505 | 11.6968 | 11.5389 | 10.8463 | 10.2979 | 9.8442 | 11.3968 | 11.2063 | 11.0158 | 10.8305 | 10.6305 | 10.4368 | 10.2526 | 10.0789 | 9.9105 | 9.1579 | 8.5537 | 8.0474 | 11.5926 | 11.4084 | 11.2253 | 11.0453 | 10.8505 | 10.6611 | 10.4821 | 10.3116 | 10.1474 | 9.42 | 8.8137 | 8.3074
|  | GRANTOWN | EE |  |  |  |  | 12.9558 | 12.8263 | 12.6958 | 12.5621 | 12.4253 | 12.2937 | 12.1611 | 12.0358 | 11.92 | 11.3589 | 10.9147 | 10.5716 | 11.5263 | 11.3768 | 11.2263 | 11.0726 | 10.92 | 10.7705 | 10.62 | 10.4779 | 10.3474 | 9.7242 | 9.2411 | 8.8579 | 11.7168 | 11.5726 | 11.4263 | 11.2779 | 11.1274 | 10.9811 | 10.8347 | 10.6958 | 10.5674 | 9.9568 | 9.4874 | 9.1074
|  | GRANTOWN | HT |  |  |  |  | 12.8463 | 12.6832 | 12.5189 | 12.3589 | 12.1832 | 12.0126 | 11.8505 | 11.6968 | 11.5389 | 10.8463 | 10.2979 | 9.8442 | 11.3968 | 11.2063 | 11.0158 | 10.8305 | 10.6305 | 10.4368 | 10.2526 | 10.0789 | 9.9105 | 9.1579 | 8.5537 | 8.0474 | 11.5926 | 11.4084 | 11.2253 | 11.0453 | 10.8505 | 10.6611 | 10.4821 | 10.3116 | 10.1474 | 9.42 | 8.8137 | 8.3074
|  | GRANTOWN | HE |  |  |  |  | 13.0842 | 13.0179 | 12.9316 | 12.8389 | 12.7389 | 12.6474 | 12.5558 | 12.4716 | 12.3926 | 12.1053 | 11.92 | 11.7653 | 11.7011 | 11.6053 | 11.5063 | 11.4021 | 11.2937 | 11.1905 | 11.0905 | 10.9968 | 10.9095 | 10.5895 | 10.3768 | 10.1905 | 11.5926 | 11.4084 | 11.2253 | 11.0453 | 10.8505 | 10.6611 | 10.4821 | 10.3116 | 10.1474 | 9.42 | 8.8137 | 8.3074
|  | GRANTOWN | CF |  |  |  |  | 13.1347 | 13.1053 | 13.0747 | 13.0389 | 12.9832 | 12.9295 | 12.8768 | 12.8221 | 12.7695 | 12.5305 | 12.3726 | 12.2568 | 11.8158 | 11.7495 | 11.6895 | 11.6295 | 11.5663 | 11.5032 | 11.4442 | 11.38 | 11.32 | 11.0421 | 10.8558 | 10.7116 | 11.9947 | 11.9316 | 11.8737 | 11.8147 | 11.7537 | 11.6926 | 11.6347 | 11.5726 | 11.5126 | 11.2442 | 11.0611 | 10.9232
| SHETLAND | GREMISTA | MINIMUM HEADROOM | HU4646842756 | NO | YES | 224.814 | -192.4814 | -192.6972 | -192.9161 | -193.554 | -194.8056 | -195.6414 | -196.4772 | -196.9908 | -197.5003 | -163.5224 | -164.6003 | -165.1751 | -196.454 | -197.0351 | -197.9151 | -198.8814 | -200.1814 | -201.0172 | -201.8529 | -202.2961 | -202.7319 | -151.9119 | -153.2582 | -156.2919 | -192.9382 | -193.4951 | -194.3329 | -195.2498 | -196.5572 | -197.4172 | -198.2782 | -198.7856 | -199.2866 | -154.9014 | -155.9361 | -158.3266
|  | GREMISTA | EE |  |  |  |  | -192.3687 | -192.5466 | -192.7329 | -193.1898 | -194.4361 | -195.3224 | -196.2045 | -196.6803 | -197.154 | -160.8919 | -162.8603 | -163.5961 | -196.1866 | -196.774 | -197.5919 | -198.4919 | -199.7593 | -200.6151 | -201.4614 | -201.8614 | -202.254 | -147.854 | -148.9908 | -151.4329 | -192.6814 | -193.2414 | -194.0182 | -194.8729 | -196.1677 | -197.0751 | -197.9772 | -198.4445 | -198.9087 | -151.5898 | -153.4445 | -154.1456
|  | GREMISTA | HT |  |  |  |  | -192.4814 | -192.6972 | -192.9161 | -193.554 | -194.8056 | -195.6414 | -196.4772 | -196.9908 | -197.5003 | -163.5224 | -164.6003 | -165.1751 | -196.454 | -197.0351 | -197.9151 | -198.8814 | -200.1814 | -201.0172 | -201.8529 | -202.2961 | -202.7319 | -151.9119 | -153.2582 | -156.2919 | -192.9382 | -193.4951 | -194.3329 | -195.2498 | -196.5572 | -197.4172 | -198.2782 | -198.7856 | -199.2866 | -154.9014 | -155.9361 | -158.3266
|  | GREMISTA | HE |  |  |  |  | -192.1919 | -192.3161 | -192.4508 | -192.6856 | -193.8329 | -194.4414 | -195.2761 | -196.3351 | -197.3035 | -162.1098 | -163.2993 | -164.4708 | -195.8961 | -196.4319 | -197.1424 | -197.9614 | -199.1329 | -199.7087 | -200.5487 | -201.6519 | -202.6498 | -150.5698 | -151.2393 | -153.6035 | -192.9382 | -193.4951 | -194.3329 | -195.2498 | -196.5572 | -197.4172 | -198.2782 | -198.7856 | -199.2866 | -154.9014 | -155.9361 | -158.3266
|  | GREMISTA | CF |  |  |  |  | -190.2529 | -192.1435 | -192.2119 | -192.2824 | -192.4635 | -192.6235 | -192.7835 | -192.9287 | -193.0529 | -160.1424 | -160.8908 | -161.3951 | -194.1351 | -195.7203 | -195.8698 | -196.1056 | -196.474 | -196.874 | -197.3066 | -197.754 | -198.0814 | -149.2582 | -149.6961 | -149.9761 | -190.1687 | -192.2298 | -192.3751 | -192.5993 | -192.9835 | -193.3898 | -193.8256 | -194.2729 | -194.5993 | -151.6182 | -152.3256 | -152.7993
| WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | YES | 0.16 | 24.4326 | 24.3053 | 24.0116 | 23.5137 | 22.9495 | 22.6547 | 22.3474 | 22.0032 | 21.5916 | 20.7063 | 19.8579 | 19.0516 | 22.94 | 22.7537 | 22.4989 | 21.9884 | 21.3189 | 20.9926 | 20.6579 | 20.28 | 19.8253 | 18.9737 | 18.0442 | 17.1453 | 23.5242 | 23.3768 | 23.2263 | 23.0232 | 22.3632 | 22.0358 | 21.7 | 21.32 | 20.8621 | 20.0663 | 19.1316 | 18.2295
|  | GREYFRIARS | EE |  |  |  |  | 24.5295 | 24.4358 | 24.3389 | 23.9632 | 23.4547 | 22.9442 | 22.72 | 22.4989 | 22.2558 | 21.2284 | 20.5547 | 19.9811 | 23.0505 | 22.9411 | 22.7547 | 22.5053 | 21.8968 | 21.2895 | 21.0474 | 20.8095 | 20.5442 | 19.5253 | 18.8021 | 18.1653 | 23.6358 | 23.5232 | 23.4042 | 23.2737 | 22.9347 | 22.3305 | 22.0863 | 21.8453 | 21.5779 | 20.6105 | 19.8716 | 19.2295
|  | GREYFRIARS | HT |  |  |  |  | 24.4326 | 24.3053 | 24.0116 | 23.5137 | 22.9495 | 22.6547 | 22.3474 | 22.0032 | 21.5916 | 20.7063 | 19.8579 | 19.0516 | 22.94 | 22.7537 | 22.4989 | 21.9884 | 21.3189 | 20.9926 | 20.6579 | 20.28 | 19.8253 | 18.9737 | 18.0442 | 17.1453 | 23.5242 | 23.3768 | 23.2263 | 23.0232 | 22.3632 | 22.0358 | 21.7 | 21.32 | 20.8621 | 20.0663 | 19.1316 | 18.2295
|  | GREYFRIARS | HE |  |  |  |  | 24.5789 | 24.4979 | 24.4116 | 24.3168 | 24.2095 | 24.1095 | 23.9989 | 23.7126 | 23.4158 | 21.8021 | 20.9821 | 20.5505 | 23.1053 | 23.0189 | 22.9263 | 22.8242 | 22.7137 | 22.5695 | 22.4084 | 22.2432 | 21.9295 | 19.9484 | 19.0221 | 18.5463 | 23.5242 | 23.3768 | 23.2263 | 23.0232 | 22.3632 | 22.0358 | 21.7 | 21.32 | 20.8621 | 20.0663 | 19.1316 | 18.2295
|  | GREYFRIARS | CF |  |  |  |  | 24.6147 | 24.5579 | 24.4989 | 24.4389 | 24.3737 | 24.3084 | 24.2442 | 24.1789 | 24.1168 | 23.3168 | 22.7295 | 22.3389 | 23.1474 | 23.0884 | 23.0263 | 22.9632 | 22.8958 | 22.8284 | 22.7611 | 22.6895 | 22.6147 | 21.8021 | 21.1063 | 20.6579 | 23.7358 | 23.6768 | 23.6137 | 23.5484 | 23.48 | 23.4095 | 23.3389 | 23.2674 | 23.1989 | 22.8305 | 22.14 | 21.6874
| SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 0 | 0.95684 | 0.94211 | 0.92737 | 0.91263 | 0.89789 | 0.88526 | 0.87158 | 0.85789 | 0.84632 | 0.79684 | 0.75579 | 0.72211 | 0.95263 | 0.93684 | 0.92105 | 0.90526 | 0.88947 | 0.87579 | 0.86105 | 0.84737 | 0.83368 | 0.78105 | 0.73684 | 0.69789 | 0.95263 | 0.93789 | 0.92211 | 0.90632 | 0.89053 | 0.87684 | 0.86211 | 0.84737 | 0.83474 | 0.78105 | 0.73684 | 0.69895
|  | GUTCHER | EE |  |  |  |  | 0.96632 | 0.95474 | 0.94316 | 0.93158 | 0.92 | 0.90842 | 0.89789 | 0.88737 | 0.87895 | 0.83579 | 0.80526 | 0.78105 | 0.96316 | 0.95053 | 0.93789 | 0.92526 | 0.91263 | 0.90105 | 0.88947 | 0.87789 | 0.86947 | 0.82316 | 0.79053 | 0.76316 | 0.96316 | 0.95053 | 0.93789 | 0.92632 | 0.91368 | 0.90211 | 0.89053 | 0.87895 | 0.86947 | 0.82421 | 0.79158 | 0.76316
|  | GUTCHER | HT |  |  |  |  | 0.95684 | 0.94211 | 0.92737 | 0.91263 | 0.89789 | 0.88526 | 0.87158 | 0.85789 | 0.84632 | 0.79684 | 0.75579 | 0.72211 | 0.95263 | 0.93684 | 0.92105 | 0.90526 | 0.88947 | 0.87579 | 0.86105 | 0.84737 | 0.83368 | 0.78105 | 0.73684 | 0.69789 | 0.95263 | 0.93789 | 0.92211 | 0.90632 | 0.89053 | 0.87684 | 0.86211 | 0.84737 | 0.83474 | 0.78105 | 0.73684 | 0.69895
|  | GUTCHER | HE |  |  |  |  | 0.98105 | 0.97263 | 0.96526 | 0.95684 | 0.94947 | 0.94105 | 0.93474 | 0.92737 | 0.92 | 0.89684 | 0.88211 | 0.87053 | 0.97895 | 0.96947 | 0.96105 | 0.95263 | 0.94421 | 0.93684 | 0.92947 | 0.92211 | 0.91474 | 0.89053 | 0.87368 | 0.86 | 0.95263 | 0.93789 | 0.92211 | 0.90632 | 0.89053 | 0.87684 | 0.86211 | 0.84737 | 0.83474 | 0.78105 | 0.73684 | 0.69895
|  | GUTCHER | CF |  |  |  |  | 0.98737 | 0.98316 | 0.97789 | 0.97368 | 0.96947 | 0.96421 | 0.96 | 0.95579 | 0.94947 | 0.92947 | 0.91684 | 0.90632 | 0.98526 | 0.98 | 0.97579 | 0.97053 | 0.96526 | 0.96105 | 0.95579 | 0.95053 | 0.94526 | 0.92316 | 0.90947 | 0.89684 | 0.98526 | 0.98105 | 0.97579 | 0.97053 | 0.96632 | 0.96105 | 0.95684 | 0.95158 | 0.94632 | 0.92421 | 0.91053 | 0.89789
| THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | YES | 0 | 6.6895 | 6.5853 | 6.4811 | 6.38 | 5.7316 | 4.9053 | 4.0105 | 3.2221 | 1.9937 | -5.2011 | -12.9305 | -19.3642 | 6.58 | 6.4779 | 6.3758 | 6.2779 | 5.7632 | 5.0695 | 4.2726 | 3.5221 | 2.3021 | -4.3621 | -12.6474 | -19.1147 | 6.5968 | 6.4874 | 6.3779 | 6.2716 | 5.64 | 4.8442 | 3.96 | 3.1905 | 2.0105 | -6 | -14.54 | -21.8758
|  | HALKIRK | EE |  |  |  |  | 6.74 | 6.6316 | 6.5242 | 6.4179 | 5.7316 | 4.9053 | 4.0105 | 3.2358 | 2.3611 | -5.2011 | -12.9305 | -19.3642 | 6.6347 | 6.5358 | 6.4358 | 6.3379 | 5.8105 | 5.1663 | 4.4242 | 3.7758 | 3.0179 | -4.3263 | -12.1084 | -19.1147 | 6.6516 | 6.54 | 6.4284 | 6.3189 | 5.6474 | 4.8442 | 3.96 | 3.1905 | 2.2958 | -6 | -14.54 | -21.8758
|  | HALKIRK | HT |  |  |  |  | 6.6895 | 6.5853 | 6.4811 | 6.38 | 5.7547 | 5.1263 | 4.4842 | 3.7463 | 2.2863 | -4.5453 | -12.0432 | -17.3263 | 6.58 | 6.4779 | 6.3758 | 6.2779 | 5.7632 | 5.2505 | 4.7221 | 4.1074 | 2.6579 | -4.3621 | -12.6474 | -18.6021 | 6.5968 | 6.4874 | 6.3779 | 6.2716 | 5.64 | 5.0095 | 4.3653 | 3.6368 | 2.0105 | -5.5968 | -14.1737 | -20.2663
|  | HALKIRK | HE |  |  |  |  | 6.8053 | 6.7621 | 6.7158 | 6.6674 | 5.8 | 4.9421 | 4.0621 | 3.2221 | 1.9937 | -3.2337 | -9.2674 | -16.3863 | 6.6905 | 6.6632 | 6.6179 | 6.5695 | 5.8421 | 5.0695 | 4.2726 | 3.5221 | 2.3021 | -2.7758 | -9.0705 | -16.3621 | 6.5968 | 6.4874 | 6.3779 | 6.2716 | 5.64 | 5.0095 | 4.3653 | 3.6368 | 2.0105 | -5.5968 | -14.1737 | -20.2663
|  | HALKIRK | CF |  |  |  |  | 6.8411 | 6.8126 | 6.7853 | 6.7568 | 6.4779 | 6.2326 | 5.7411 | 5.2158 | 4.6189 | 1.9168 | -1.9211 | -6.4905 | 6.7126 | 6.6968 | 6.6821 | 6.6642 | 6.4505 | 6.2621 | 5.7621 | 5.2158 | 4.5674 | 1.8274 | -2.1979 | -7.1337 | 6.7632 | 6.7347 | 6.7063 | 6.6758 | 6.4032 | 6.1632 | 5.6126 | 5.0232 | 4.3442 | 1.36 | -2.9411 | -8.1242
| ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 0 | 22.6021 | 22.3484 | 21.9789 | 21.5189 | 21.0484 | 20.6 | 20.1989 | 19.8011 | 19.3326 | 18.1284 | 17.2821 | 16.6295 | 21.8284 | 21.3274 | 20.8642 | 20.2747 | 19.76 | 19.2821 | 18.86 | 18.4463 | 17.9484 | 16.7263 | 15.8568 | 15.1568 | 21.7326 | 21.5695 | 21.2653 | 20.6768 | 20.1463 | 19.6558 | 19.2189 | 18.7884 | 18.2726 | 16.9853 | 16.0737 | 15.3579
|  | HARBOUR | EE |  |  |  |  | 22.6895 | 22.5905 | 22.2884 | 21.9074 | 21.5116 | 21.0347 | 20.6905 | 20.4 | 20.0168 | 18.6589 | 17.72 | 17.1695 | 21.9221 | 21.6421 | 21.2326 | 20.7368 | 20.2705 | 19.7547 | 19.4053 | 19.1126 | 18.7095 | 17.3537 | 16.4726 | 15.9063 | 21.8263 | 21.7105 | 21.5853 | 21.1379 | 20.6537 | 20.1158 | 19.7463 | 19.4347 | 19.0137 | 17.5568 | 16.5695 | 15.9705
|  | HARBOUR | HT |  |  |  |  | 22.6021 | 22.3484 | 21.9789 | 21.5189 | 21.0484 | 20.6 | 20.1989 | 19.8011 | 19.3326 | 18.1284 | 17.2821 | 16.6295 | 21.8284 | 21.3274 | 20.8642 | 20.2747 | 19.76 | 19.2821 | 18.86 | 18.4463 | 17.9484 | 16.7263 | 15.8568 | 15.1568 | 21.7326 | 21.5695 | 21.2653 | 20.6768 | 20.1463 | 19.6558 | 19.2189 | 18.7884 | 18.2726 | 16.9853 | 16.0737 | 15.3579
|  | HARBOUR | HE |  |  |  |  | 22.7747 | 22.7032 | 22.5379 | 22.1958 | 21.8221 | 21.4316 | 21.1158 | 20.8295 | 20.5084 | 19.7379 | 19.1937 | 18.6937 | 22.0126 | 21.8768 | 21.5263 | 21.0737 | 20.6326 | 20.1747 | 19.8432 | 19.5463 | 19.2063 | 18.4632 | 17.9589 | 17.5042 | 21.7326 | 21.5695 | 21.2653 | 20.6768 | 20.1463 | 19.6558 | 19.2189 | 18.7884 | 18.2726 | 16.9853 | 16.0737 | 15.3579
|  | HARBOUR | CF |  |  |  |  | 22.8305 | 22.7884 | 22.7453 | 22.7021 | 22.6316 | 22.4979 | 22.3368 | 22.2179 | 22.0726 | 21.3516 | 20.9568 | 20.6589 | 22.0737 | 22.0274 | 21.9779 | 21.8853 | 21.7105 | 21.5126 | 21.3211 | 21.1821 | 21.0063 | 20.1432 | 19.7537 | 19.4632 | 21.9821 | 21.9326 | 21.8821 | 21.8295 | 21.7537 | 21.6811 | 21.6063 | 21.5411 | 21.3821 | 20.4916 | 20.0621 | 19.7421
| ARDMORE | HARRIS GRID | MINIMUM HEADROOM | NG 13500 94249 | YES | YES | 0 | 29.9611 | 29.9421 | 29.9221 | 29.9032 | 29.8632 | 29.8379 | 29.8095 | 29.7789 | 29.7463 | 29.3874 | 27.6021 | 27.2579 | 29.9558 | 29.9358 | 29.9137 | 29.8916 | 29.8547 | 29.8326 | 29.8105 | 29.7874 | 29.7589 | 29.3758 | 27.8253 | 27.4863 | 29.9558 | 29.9358 | 29.9126 | 29.8916 | 29.8495 | 29.8232 | 29.7958 | 29.7674 | 29.7337 | 29.3274 | 27.4726 | 27.1042
|  | HARRIS GRID | EE |  |  |  |  | 29.9811 | 29.9463 | 29.9295 | 29.9084 | 29.88 | 29.8453 | 29.8095 | 29.7789 | 29.7463 | 29.3989 | 27.6189 | 27.2579 | 29.9789 | 29.9411 | 29.92 | 29.9 | 29.8758 | 29.8463 | 29.8179 | 29.7926 | 29.7642 | 29.4168 | 27.8968 | 27.5074 | 29.9789 | 29.94 | 29.92 | 29.8979 | 29.8684 | 29.8326 | 29.7989 | 29.7674 | 29.7337 | 29.3537 | 27.5189 | 27.1042
|  | HARRIS GRID | HT |  |  |  |  | 29.9611 | 29.9421 | 29.9221 | 29.9032 | 29.8632 | 29.8379 | 29.8105 | 29.7821 | 29.7526 | 29.3874 | 27.6021 | 27.2947 | 29.9558 | 29.9358 | 29.9137 | 29.8916 | 29.8547 | 29.8326 | 29.8105 | 29.7874 | 29.7632 | 29.3758 | 27.8253 | 27.4863 | 29.9558 | 29.9358 | 29.9126 | 29.8916 | 29.8495 | 29.8232 | 29.7958 | 29.7674 | 29.7368 | 29.3274 | 27.4726 | 27.1179
|  | HARRIS GRID | HE |  |  |  |  | 29.9884 | 29.9568 | 29.9411 | 29.9263 | 29.8968 | 29.8716 | 29.8453 | 29.8147 | 29.7516 | 29.4842 | 28.4695 | 28.0958 | 29.9874 | 29.9516 | 29.9337 | 29.9168 | 29.8937 | 29.8726 | 29.8516 | 29.8242 | 29.7589 | 29.4884 | 28.5968 | 28.2 | 29.9558 | 29.9358 | 29.9126 | 29.8916 | 29.8495 | 29.8232 | 29.7958 | 29.7674 | 29.7368 | 29.3274 | 27.4726 | 27.1179
|  | HARRIS GRID | CF |  |  |  |  | 29.9926 | 29.9895 | 29.9789 | 29.9747 | 29.9611 | 29.9463 | 29.9326 | 29.9074 | 29.8747 | 29.7274 | 29.5074 | 29.2505 | 29.9926 | 29.9884 | 29.9768 | 29.9726 | 29.96 | 29.9463 | 29.9337 | 29.9084 | 29.8716 | 29.7168 | 29.4811 | 29.1968 | 29.9926 | 29.9884 | 29.9768 | 29.9726 | 29.9579 | 29.9421 | 29.9274 | 29.9 | 29.8621 | 29.6979 | 29.4495 | 29.1558
| DYCE | HARVEST AVENUE | MINIMUM HEADROOM | NJ 86978 11769 | NO | YES | 0 | 23.8979 | 23.8853 | 23.8726 | 23.86 | 23.8358 | 23.8126 | 23.7884 | 23.7632 | 23.7368 | 23.6179 | 23.4495 | 23.2832 | 22.5653 | 22.5568 | 22.5453 | 22.5358 | 22.5211 | 22.5074 | 22.4895 | 22.4568 | 22.4263 | 22.2874 | 22.1179 | 21.9579 | 23.2537 | 23.2474 | 23.2295 | 23.2063 | 23.1726 | 23.1389 | 23.1042 | 23.0695 | 23.0337 | 22.8811 | 22.7011 | 22.5105
|  | HARVEST AVENUE | EE |  |  |  |  | 23.9032 | 23.8958 | 23.8853 | 23.8747 | 23.8495 | 23.8221 | 23.7958 | 23.7705 | 23.7453 | 23.6179 | 23.4495 | 23.2832 | 22.5695 | 22.5642 | 22.5558 | 22.5484 | 22.5337 | 22.5179 | 22.5032 | 22.4884 | 22.4663 | 22.3232 | 22.1389 | 21.9589 | 23.2568 | 23.2516 | 23.2453 | 23.2379 | 23.2032 | 23.1695 | 23.1347 | 23.1032 | 23.0695 | 22.9074 | 22.7011 | 22.5105
|  | HARVEST AVENUE | HT |  |  |  |  | 23.8979 | 23.8853 | 23.8726 | 23.86 | 23.8358 | 23.8126 | 23.7884 | 23.7632 | 23.7368 | 23.6189 | 23.46 | 23.3189 | 22.5653 | 22.5568 | 22.5453 | 22.5358 | 22.5211 | 22.5074 | 22.4895 | 22.4568 | 22.4263 | 22.2874 | 22.1179 | 21.9579 | 23.2537 | 23.2474 | 23.2295 | 23.2063 | 23.1726 | 23.1389 | 23.1042 | 23.0695 | 23.0337 | 22.8811 | 22.7011 | 22.5379
|  | HARVEST AVENUE | HE |  |  |  |  | 23.9105 | 23.9063 | 23.9021 | 23.8968 | 23.8747 | 23.8558 | 23.8358 | 23.8158 | 23.7947 | 23.6958 | 23.5621 | 23.3832 | 22.5768 | 22.5726 | 22.5695 | 22.5642 | 22.5516 | 22.5411 | 22.5305 | 22.52 | 22.5084 | 22.4095 | 22.2389 | 22.0547 | 23.2537 | 23.2474 | 23.2295 | 23.2063 | 23.1726 | 23.1389 | 23.1042 | 23.0695 | 23.0337 | 22.8811 | 22.7011 | 22.5379
|  | HARVEST AVENUE | CF |  |  |  |  | 23.9137 | 23.9116 | 23.9084 | 23.9063 | 23.8979 | 23.8905 | 23.8821 | 23.8737 | 23.8642 | 23.8137 | 23.7474 | 23.6453 | 22.5789 | 22.5779 | 22.5747 | 22.5737 | 22.5684 | 22.5632 | 22.5589 | 22.5547 | 22.5484 | 22.5179 | 22.4305 | 22.3032 | 23.2642 | 23.2632 | 23.2611 | 23.2589 | 23.2516 | 23.2442 | 23.2368 | 23.2316 | 23.2263 | 23.1516 | 23.0337 | 22.9011
| THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | YES | 0 | 3.1396 | 3.0154 | 2.8817 | 2.7469 | 2.1691 | -0.91832 | -4.0488 | -7.072 | -10.1088 | -17.6752 | -23.0667 | -26.2752 | 2.6754 | 2.5512 | 2.4091 | 2.2648 | 1.7933 | -1.0752 | -4.0667 | -6.9731 | -9.8867 | -17.0815 | -22.8152 | -26.072 | 2.6764 | 2.5227 | 2.3712 | 2.2217 | 1.6385 | -1.4267 | -4.5562 | -7.5794 | -10.6162 | -18.552 | -24.6741 | -28.0141
|  | HASTIGROW | EE |  |  |  |  | 3.1817 | 3.0891 | 2.9638 | 2.8364 | 2.1891 | -0.91832 | -4.0488 | -7.072 | -10.1088 | -17.6752 | -22.0057 | -25.7509 | 2.7459 | 2.6312 | 2.5133 | 2.3954 | 1.8806 | -1.0752 | -4.0667 | -6.9731 | -9.8867 | -17.0815 | -21.3646 | -25.3036 | 2.7638 | 2.6217 | 2.4785 | 2.3375 | 1.6827 | -1.4267 | -4.5562 | -7.5794 | -10.6162 | -18.552 | -23.3562 | -27.5562
|  | HASTIGROW | HT |  |  |  |  | 3.1396 | 3.0154 | 2.8817 | 2.7469 | 2.1691 | -0.74042 | -3.6541 | -6.0941 | -8.6488 | -15.4562 | -23.0667 | -26.0015 | 2.6754 | 2.5512 | 2.4091 | 2.2648 | 1.7933 | -1.0067 | -3.8215 | -6.2678 | -8.8583 | -15.632 | -22.8152 | -26.072 | 2.6764 | 2.5227 | 2.3712 | 2.2217 | 1.6385 | -1.2762 | -4.1952 | -6.6436 | -9.2383 | -16.5057 | -24.6741 | -28.0141
|  | HASTIGROW | HE |  |  |  |  | 3.2375 | 3.1954 | 3.1491 | 3.1006 | 2.448 | 1.8175 | 1.1343 | -1.8709 | -5.0625 | -15.7794 | -21.6552 | -26.2752 | 2.8364 | 2.7838 | 2.7238 | 2.6617 | 2.1333 | 1.6238 | 1.0143 | -1.9109 | -5.0594 | -15.5225 | -20.9657 | -25.4141 | 2.6764 | 2.5227 | 2.3712 | 2.2217 | 1.6385 | -1.2762 | -4.1952 | -6.6436 | -9.2383 | -16.5057 | -24.6741 | -28.0141
|  | HASTIGROW | CF |  |  |  |  | 3.2733 | 3.2491 | 3.2248 | 3.1996 | 2.9869 | 2.7659 | 2.5069 | 2.1859 | 1.8312 | 0.04379 | -4.3994 | -7.0973 | 2.8891 | 2.8585 | 2.8269 | 2.7922 | 2.5869 | 2.4038 | 2.1922 | 1.8838 | 1.5006 | -0.252 | -4.2499 | -7.0678 | 2.9491 | 2.9048 | 2.8638 | 2.8206 | 2.5564 | 2.3217 | 2.0417 | 1.6585 | 1.2522 | -0.71305 | -5.4267 | -8.4478
| STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | YES | 0.36 | 5.7874 | 5.6053 | 5.3926 | 5.1737 | 4.4337 | 3.4379 | 2.3705 | 1.4905 | 0.56421 | -7.6653 | -15.4295 | -20.9726 | 5.34 | 5.1474 | 4.9147 | 4.6726 | 4.0379 | 3.2274 | 2.3168 | 1.5358 | 0.74737 | -6.6358 | -14.1147 | -20.1211 | 5.4663 | 5.2674 | 5.0295 | 4.7832 | 4.0274 | 3.0305 | 1.9242 | 1.0221 | 0.063158 | -8.5989 | -17.0453 | -23.3358
|  | HATTON | EE |  |  |  |  | 5.8558 | 5.7063 | 5.5053 | 5.2926 | 4.4558 | 3.4379 | 2.3705 | 1.4905 | 0.56421 | -7.6653 | -15.4295 | -20.9726 | 5.4137 | 5.2695 | 5.0568 | 4.8305 | 4.1242 | 3.2474 | 2.3168 | 1.5663 | 0.76421 | -6.6358 | -14.1147 | -20.1211 | 5.5389 | 5.3842 | 5.1632 | 4.9274 | 4.0811 | 3.0305 | 1.9242 | 1.0221 | 0.063158 | -8.5989 | -17.0453 | -23.3358
|  | HATTON | HT |  |  |  |  | 5.7874 | 5.6053 | 5.3926 | 5.1737 | 4.4337 | 3.5663 | 2.6663 | 1.72 | 0.81789 | -6.7989 | -13.5305 | -18.0905 | 5.34 | 5.1474 | 4.9147 | 4.6726 | 4.0379 | 3.2274 | 2.3832 | 1.5358 | 0.74737 | -6.3726 | -13.6874 | -18.7621 | 5.4663 | 5.2674 | 5.0295 | 4.7832 | 4.0274 | 3.1053 | 2.1453 | 1.1537 | 0.22 | -7.9326 | -15.6358 | -20.8916
|  | HATTON | HE |  |  |  |  | 5.9305 | 5.8621 | 5.7705 | 5.6463 | 4.7916 | 4.0063 | 3.1842 | 2.4389 | 1.4411 | -4.4568 | -10.3316 | -16.7042 | 5.4905 | 5.4211 | 5.3221 | 5.1832 | 4.4747 | 3.7884 | 3.0537 | 2.4137 | 1.4579 | -4.0305 | -9.9316 | -16.3884 | 5.4663 | 5.2674 | 5.0295 | 4.7832 | 4.0274 | 3.1053 | 2.1453 | 1.1537 | 0.22 | -7.9326 | -15.6358 | -20.8916
|  | HATTON | CF |  |  |  |  | 5.98 | 5.9484 | 5.9126 | 5.8768 | 5.5779 | 5.2737 | 4.9526 | 4.6232 | 4.1137 | 1.6684 | -2.0221 | -5.9779 | 5.5442 | 5.5137 | 5.4789 | 5.4442 | 5.2053 | 4.9432 | 4.6558 | 4.3432 | 3.78 | 1.3053 | -2.4505 | -6.7232 | 5.6695 | 5.6368 | 5.6011 | 5.5632 | 5.2768 | 4.9632 | 4.6263 | 4.2726 | 3.6747 | 0.94105 | -3.1642 | -7.6884
| PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | NO | 0.13 | 21.1426 | 20.9932 | 20.8426 | 20.6868 | 20.5058 | 20.3279 | 20.1542 | 19.9616 | 19.7016 | 18.6689 | 17.79 | 16.97 | 19.5595 | 19.4132 | 19.2605 | 18.9911 | 18.7068 | 18.4247 | 18.1511 | 17.8805 | 17.6089 | 16.5111 | 15.5574 | 14.6437 | 19.9426 | 19.7384 | 19.5311 | 19.3237 | 19.0942 | 18.8679 | 18.6468 | 18.4279 | 18.2121 | 17.3858 | 16.4321 | 15.5163
|  | HAUDAGAIN | EE |  |  |  |  | 21.2405 | 21.1247 | 21.0026 | 20.8742 | 20.7289 | 20.5847 | 20.4416 | 20.3047 | 20.1732 | 19.3616 | 18.6311 | 18.0458 | 19.6553 | 19.5426 | 19.4216 | 19.2963 | 19.1142 | 18.8879 | 18.6658 | 18.4521 | 18.2447 | 17.2805 | 16.5153 | 15.87 | 20.0816 | 19.9226 | 19.7584 | 19.5868 | 19.4016 | 19.2184 | 19.0363 | 18.8616 | 18.6932 | 17.9321 | 17.3574 | 16.7026
|  | HAUDAGAIN | HT |  |  |  |  | 21.1426 | 20.9932 | 20.8426 | 20.6868 | 20.5058 | 20.3279 | 20.1542 | 19.9616 | 19.7016 | 18.6689 | 17.79 | 16.97 | 19.5595 | 19.4132 | 19.2605 | 18.9911 | 18.7068 | 18.4247 | 18.1511 | 17.8805 | 17.6089 | 16.5111 | 15.5574 | 14.6437 | 19.9426 | 19.7384 | 19.5311 | 19.3237 | 19.0942 | 18.8679 | 18.6468 | 18.4279 | 18.2121 | 17.3858 | 16.4321 | 15.5163
|  | HAUDAGAIN | HE |  |  |  |  | 21.3195 | 21.2332 | 21.1384 | 21.0342 | 20.9089 | 20.7921 | 20.6805 | 20.5721 | 20.4742 | 20.1089 | 19.8826 | 19.6289 | 19.7416 | 19.6521 | 19.5542 | 19.4511 | 19.3353 | 19.2279 | 19.1237 | 19.0247 | 18.9342 | 18.3553 | 17.9363 | 17.5995 | 19.9426 | 19.7384 | 19.5311 | 19.3237 | 19.0942 | 18.8679 | 18.6468 | 18.4279 | 18.2121 | 17.3858 | 16.4321 | 15.5163
|  | HAUDAGAIN | CF |  |  |  |  | 21.3742 | 21.3184 | 21.2616 | 21.2026 | 21.1363 | 21.0689 | 21.0005 | 20.9332 | 20.8668 | 20.5689 | 20.39 | 20.2847 | 19.8005 | 19.7426 | 19.6826 | 19.6226 | 19.5563 | 19.4921 | 19.4258 | 19.3626 | 19.2984 | 18.9595 | 18.5911 | 18.3068 | 20.3153 | 20.2374 | 20.1584 | 20.0763 | 19.9879 | 19.9005 | 19.8121 | 19.7247 | 19.6374 | 19.2395 | 18.97 | 18.7816
| WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | YES | 0 | 22.1142 | 22.1037 | 22.1026 | 22.0311 | 21.9479 | 21.5511 | 21.4616 | 21.3732 | 20.9689 | 19.9458 | 19.3037 | 18.6963 | 21.4821 | 21.4747 | 21.4747 | 21.4011 | 21.3211 | 20.9137 | 20.8011 | 20.5821 | 20.3137 | 19.3263 | 18.6326 | 17.9642 | 21.4371 | 21.4245 | 21.5161 | 21.4718 | 21.3687 | 21.2413 | 21.1129 | 20.9687 | 20.5045 | 19.3845 | 18.6866 | 18.0192
|  | HAYTON | EE |  |  |  |  | 22.1816 | 22.1037 | 22.2932 | 22.2079 | 22.1111 | 22.0153 | 21.9205 | 21.8311 | 21.7426 | 20.4205 | 19.89 | 19.4458 | 21.5537 | 21.4747 | 21.7263 | 21.6389 | 21.5453 | 21.4537 | 21.36 | 21.2695 | 21.1789 | 19.8695 | 19.3147 | 18.8358 | 21.5076 | 21.4245 | 21.7129 | 21.6224 | 21.5203 | 21.4213 | 21.3182 | 21.2192 | 21.1192 | 19.8908 | 19.3161 | 18.8266
|  | HAYTON | HT |  |  |  |  | 22.1142 | 22.2847 | 22.1858 | 22.0826 | 21.9626 | 21.8447 | 21.7289 | 21.3868 | 20.9689 | 19.9458 | 19.3037 | 18.6963 | 21.4821 | 21.7137 | 21.6116 | 21.5021 | 21.3832 | 21.2621 | 21.1389 | 20.9095 | 20.4442 | 19.3263 | 18.6326 | 17.9642 | 21.4371 | 21.7076 | 21.6024 | 21.4929 | 21.3687 | 21.2413 | 21.1129 | 20.9687 | 20.5045 | 19.3845 | 18.6866 | 18.0192
|  | HAYTON | HE |  |  |  |  | 22.2311 | 22.1689 | 22.1026 | 22.0311 | 21.9479 | 21.5511 | 21.4616 | 21.3732 | 21.2258 | 20.3826 | 19.9584 | 19.7226 | 21.6063 | 21.5421 | 21.4747 | 21.4011 | 21.3211 | 20.9137 | 20.8011 | 20.5821 | 20.3137 | 19.3811 | 18.9211 | 18.6779 | 21.4371 | 21.7076 | 21.6024 | 21.4929 | 21.3687 | 21.2413 | 21.1129 | 20.9687 | 20.5045 | 19.3845 | 18.6866 | 18.0192
|  | HAYTON | CF |  |  |  |  | 22.2679 | 22.2279 | 22.1858 | 22.1437 | 22.0974 | 22.0511 | 22.0047 | 21.9574 | 21.9142 | 21.6553 | 21.1942 | 21.0047 | 21.6442 | 21.6021 | 21.56 | 21.5168 | 21.4695 | 21.4242 | 21.3779 | 21.3305 | 21.2842 | 21.0189 | 20.5053 | 20.2979 | 21.6003 | 21.5582 | 21.5161 | 21.4718 | 21.4234 | 21.375 | 21.3287 | 21.2782 | 21.2297 | 20.9992 | 20.4866 | 20.2761
| BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | YES | 0 | 1.5795 | 1.5363 | 1.4847 | 1.43 | 1.0984 | 0.67947 | 0.21842 | -0.22263 | -0.89632 | -4.8121 | -9.4216 | -13.0574 | 1.3647 | 1.3153 | 1.2616 | 1.2121 | 0.97421 | 0.58789 | 0.15421 | -0.25421 | -0.92579 | -4.61 | -9.4311 | -13.1321 | 1.3963 | 1.3405 | 1.2847 | 1.2216 | 0.85947 | 0.42789 | -0.037368 | -0.44474 | -0.96684 | -5.3753 | -10.4616 | -14.6616
|  | HELMSDALE | EE |  |  |  |  | 1.5911 | 1.5395 | 1.4847 | 1.43 | 1.0984 | 0.67947 | 0.21842 | -0.18474 | -0.64895 | -4.8121 | -9.4216 | -13.0574 | 1.3868 | 1.3332 | 1.2784 | 1.2226 | 0.98789 | 0.65 | 0.27316 | -0.059474 | -0.45947 | -4.5584 | -9.1426 | -13.1321 | 1.4142 | 1.35 | 1.2858 | 1.2216 | 0.85947 | 0.42789 | -0.037368 | -0.44474 | -0.90053 | -5.3753 | -10.4616 | -14.6616
|  | HELMSDALE | HT |  |  |  |  | 1.5795 | 1.5363 | 1.49 | 1.4447 | 1.1289 | 0.80263 | 0.46368 | 0.09 | -0.72053 | -4.4816 | -8.8563 | -11.89 | 1.3647 | 1.3153 | 1.2616 | 1.2121 | 0.97421 | 0.69737 | 0.40684 | 0.098421 | -0.71526 | -4.61 | -9.4311 | -12.8668 | 1.3963 | 1.3405 | 1.2847 | 1.2311 | 0.90684 | 0.58053 | 0.24368 | -0.13316 | -0.96684 | -5.1921 | -10.2237 | -13.7289
|  | HELMSDALE | HE |  |  |  |  | 1.6195 | 1.5984 | 1.5763 | 1.5542 | 1.15 | 0.69421 | 0.22368 | -0.22263 | -0.89632 | -3.7395 | -7.3195 | -11.2563 | 1.4279 | 1.4026 | 1.3763 | 1.3511 | 1.0089 | 0.58789 | 0.15421 | -0.25421 | -0.92579 | -3.7216 | -7.4184 | -11.4995 | 1.3963 | 1.3405 | 1.2847 | 1.2311 | 0.90684 | 0.58053 | 0.24368 | -0.13316 | -0.96684 | -5.1921 | -10.2237 | -13.7289
|  | HELMSDALE | CF |  |  |  |  | 1.6342 | 1.6226 | 1.6121 | 1.6005 | 1.4795 | 1.3721 | 1.1216 | 0.83 | 0.49842 | -0.97947 | -3.2342 | -5.7953 | 1.45 | 1.4353 | 1.4205 | 1.4058 | 1.3174 | 1.2353 | 0.96684 | 0.66263 | 0.30263 | -1.2132 | -3.5595 | -6.37 | 1.4732 | 1.4574 | 1.4426 | 1.4279 | 1.2837 | 1.1553 | 0.90895 | 0.65 | 0.26684 | -1.3889 | -3.9374 | -6.87
| INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | YES | 0.534 | 24.4839 | 23.9344 | 23.3902 | 22.8281 | 22.2007 | 21.5986 | 21.0386 | 20.5113 | 20.0123 | 17.6555 | 15.7797 | 14.1871 | 22.9523 | 22.366 | 21.7871 | 21.1871 | 20.5207 | 19.8807 | 19.2892 | 18.7334 | 18.2081 | 15.6607 | 13.5986 | 11.8249 | 23.9471 | 23.5039 | 22.9271 | 22.3292 | 21.6628 | 21.0228 | 20.4302 | 19.8723 | 19.3449 | 16.7955 | 14.7418 | 12.9586
|  | HILTON | EE |  |  |  |  | 24.8281 | 24.4155 | 23.9776 | 23.5113 | 23.0281 | 22.5618 | 22.1113 | 21.6797 | 21.2723 | 19.3607 | 17.8702 | 16.686 | 23.3218 | 22.8839 | 22.4197 | 21.9228 | 21.4123 | 20.9228 | 20.4481 | 19.9934 | 19.5649 | 17.5334 | 15.926 | 14.6134 | 24.1249 | 23.8765 | 23.5534 | 23.0618 | 22.5502 | 22.0565 | 21.5797 | 21.1228 | 20.6902 | 18.6449 | 17.0218 | 15.7176
|  | HILTON | HT |  |  |  |  | 24.4839 | 23.9344 | 23.3902 | 22.8281 | 22.2007 | 21.5986 | 21.0386 | 20.5113 | 20.0123 | 17.6555 | 15.7797 | 14.1871 | 22.9523 | 22.366 | 21.7871 | 21.1871 | 20.5207 | 19.8807 | 19.2892 | 18.7334 | 18.2081 | 15.6607 | 13.5986 | 11.8249 | 23.9471 | 23.5039 | 22.9271 | 22.3292 | 21.6628 | 21.0228 | 20.4302 | 19.8723 | 19.3449 | 16.7955 | 14.7418 | 12.9586
|  | HILTON | HE |  |  |  |  | 25.0828 | 24.786 | 24.4639 | 24.1123 | 23.7397 | 23.5239 | 23.3113 | 23.1102 | 22.8681 | 21.8807 | 21.226 | 20.6681 | 23.5797 | 23.2649 | 22.9218 | 22.5481 | 22.1565 | 21.9428 | 21.7323 | 21.5344 | 21.2849 | 20.2544 | 19.5639 | 18.966 | 23.9471 | 23.5039 | 22.9271 | 22.3292 | 21.6628 | 21.0228 | 20.4302 | 19.8723 | 19.3449 | 16.7955 | 14.7418 | 12.9586
|  | HILTON | CF |  |  |  |  | 25.4102 | 25.2797 | 25.1439 | 25.0071 | 24.8355 | 24.6313 | 24.4418 | 24.2407 | 24.0481 | 23.1871 | 22.6039 | 22.1734 | 23.7839 | 23.6828 | 23.5776 | 23.4713 | 23.3365 | 23.1207 | 22.9197 | 22.706 | 22.5018 | 21.5881 | 20.9639 | 20.4923 | 24.5102 | 24.4113 | 24.3081 | 24.2028 | 24.0944 | 23.9828 | 23.8713 | 23.7618 | 23.6239 | 22.7155 | 22.086 | 21.6113
| ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 0 | 24.6105 | 24.4705 | 24.3295 | 24.1842 | 23.9537 | 23.7274 | 23.5042 | 23.2695 | 23.0368 | 21.5368 | 20.5811 | 19.9558 | 23.5179 | 23.2589 | 22.9989 | 22.74 | 22.4168 | 22.1021 | 21.7926 | 21.4726 | 21.1537 | 19.3463 | 18.3537 | 17.6789 | 24.4768 | 24.2147 | 23.9526 | 23.6916 | 23.3495 | 23.0158 | 22.6853 | 22.3442 | 22.0021 | 20.0947 | 19.0442 | 18.3432
|  | HUME STREET | EE |  |  |  |  | 24.6947 | 24.5811 | 24.4632 | 24.3389 | 24.1253 | 23.8968 | 23.6663 | 23.4579 | 23.2505 | 22.26 | 21.0253 | 20.2989 | 23.6979 | 23.4916 | 23.2842 | 23.0716 | 22.7905 | 22.5 | 22.2105 | 21.94 | 21.6758 | 20.3568 | 19.1853 | 18.4168 | 24.5811 | 24.4484 | 24.2389 | 24.0232 | 23.72 | 23.4021 | 23.0832 | 22.7895 | 22.5 | 21.0442 | 19.7274 | 18.9105
|  | HUME STREET | HT |  |  |  |  | 24.6105 | 24.4705 | 24.3295 | 24.1842 | 23.9537 | 23.7274 | 23.5042 | 23.2695 | 23.0368 | 21.5368 | 20.5811 | 19.9558 | 23.5179 | 23.2589 | 22.9989 | 22.74 | 22.4168 | 22.1021 | 21.7926 | 21.4726 | 21.1537 | 19.3463 | 18.3537 | 17.6789 | 24.4768 | 24.2147 | 23.9526 | 23.6916 | 23.3495 | 23.0158 | 22.6853 | 22.3442 | 22.0021 | 20.0947 | 19.0442 | 18.3432
|  | HUME STREET | HE |  |  |  |  | 24.7747 | 24.6884 | 24.5979 | 24.4989 | 24.2968 | 24.1189 | 23.9432 | 23.7737 | 23.6116 | 22.9495 | 22.4442 | 21.6589 | 23.9032 | 23.7632 | 23.62 | 23.4684 | 23.2358 | 23.0253 | 22.8189 | 22.6211 | 22.4316 | 21.6211 | 20.5568 | 19.8074 | 24.4768 | 24.2147 | 23.9526 | 23.6916 | 23.3495 | 23.0158 | 22.6853 | 22.3442 | 22.0021 | 20.0947 | 19.0442 | 18.3432
|  | HUME STREET | CF |  |  |  |  | 24.8305 | 24.7768 | 24.7211 | 24.6653 | 24.5716 | 24.4821 | 24.3937 | 24.3084 | 24.2316 | 23.8368 | 23.4979 | 23.2811 | 24.0053 | 23.9526 | 23.8968 | 23.84 | 23.7147 | 23.5916 | 23.4684 | 23.3484 | 23.2358 | 22.6716 | 22.1789 | 21.8074 | 24.7168 | 24.6632 | 24.6074 | 24.5516 | 24.4621 | 24.3758 | 24.2905 | 24.2095 | 24.1337 | 23.5568 | 23.0084 | 22.6
| KEITH 2 | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 0 | 15.0953 | 14.9437 | 14.7942 | 14.4068 | 13.9637 | 12.9142 | 11.6805 | 10.8774 | 9.9447 | -0.058421 | -13.6363 | -21.1605 | 13.2421 | 12.9568 | 12.5095 | 11.9758 | 11.4695 | 10.6989 | 10.2905 | 9.4274 | 8.0789 | -1.7653 | -15.9232 | -24.2537 | 14.0434 | 13.7645 | 13.3455 | 12.8518 | 12.3824 | 11.3403 | 10.1624 | 9.3192 | 8.3497 | -2.4387 | -17.7345 | -26.3187
|  | HUNTLY | EE |  |  |  |  | 15.1521 | 14.9921 | 14.8279 | 14.6226 | 14.1963 | 12.9142 | 12.7489 | 11.3342 | 9.9447 | -0.058421 | -11.8142 | -21.1605 | 13.3747 | 13.1453 | 12.7463 | 12.2747 | 11.8011 | 10.7716 | 10.5832 | 9.4811 | 8.4284 | -1.2621 | -12.8358 | -22.8347 | 14.1655 | 13.9234 | 13.5371 | 13.0876 | 12.6361 | 11.3403 | 11.1676 | 9.7434 | 8.3497 | -2.4387 | -15.2808 | -25.7724
|  | HUNTLY | HT |  |  |  |  | 15.0953 | 14.9437 | 14.7942 | 14.4068 | 13.9637 | 13.0279 | 12.8458 | 11.4826 | 9.9837 | 0.34684 | -13.6363 | -21.1279 | 13.2421 | 12.9568 | 12.5095 | 11.9758 | 11.4695 | 10.6989 | 10.4958 | 9.4274 | 8.1979 | -1.7653 | -15.9232 | -24.2537 | 14.0434 | 13.7645 | 13.3455 | 12.8518 | 12.3824 | 11.4339 | 11.2445 | 9.8718 | 8.3529 | -2.3134 | -17.7345 | -26.3187
|  | HUNTLY | HE |  |  |  |  | 15.23 | 15.1584 | 15.0805 | 14.9974 | 14.7953 | 13.6353 | 13.4437 | 11.9984 | 10.0668 | 2.6563 | -8.75 | -19.6774 | 13.5495 | 13.3958 | 13.1179 | 12.7463 | 12.3684 | 11.4453 | 11.2168 | 9.9621 | 8.0789 | 0.83158 | -10.2463 | -21.0989 | 14.0434 | 13.7645 | 13.3455 | 12.8518 | 12.3824 | 11.4339 | 11.2445 | 9.8718 | 8.3529 | -2.3134 | -17.7345 | -26.3187
|  | HUNTLY | CF |  |  |  |  | 15.2805 | 15.2353 | 15.1921 | 15.1458 | 15.1016 | 14.7447 | 11.6805 | 10.8774 | 10.0321 | 6.4921 | 0.34368 | -6.3574 | 13.6421 | 13.5684 | 13.4916 | 13.4105 | 13.3295 | 12.9642 | 10.2905 | 9.4632 | 8.5232 | 4.7842 | -1.52 | -8.5926 | 14.3824 | 14.3203 | 14.255 | 14.1855 | 14.1055 | 13.6529 | 10.1624 | 9.3192 | 8.4161 | 4.5382 | -2.3503 | -9.8324
| BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | YES | 0 | 2.7621 | 2.7253 | 2.6832 | 2.6442 | 2.2347 | 1.7305 | 1.2179 | 0.72737 | 0.025263 | -4.1863 | -9.0537 | -12.6095 | 2.6621 | 2.6284 | 2.5958 | 2.5589 | 2.1832 | 1.7284 | 1.2621 | 0.81789 | 0.14 | -3.7011 | -8.3758 | -12.1653 | 2.6905 | 2.6516 | 2.6032 | 2.5568 | 2.1358 | 1.6305 | 1.1116 | 0.66526 | 0.03579 | -4.6674 | -9.9432 | -13.9863
|  | INCHBARE | EE |  |  |  |  | 2.7653 | 2.7253 | 2.6832 | 2.6442 | 2.24 | 1.7379 | 1.2221 | 0.77895 | 0.15789 | -4.1863 | -9.0537 | -12.6095 | 2.6726 | 2.6358 | 2.5979 | 2.5589 | 2.2232 | 1.8232 | 1.4095 | 1.0547 | 0.48 | -3.7011 | -8.3758 | -12.1653 | 2.7 | 2.6516 | 2.6032 | 2.5568 | 2.1358 | 1.6305 | 1.1116 | 0.66526 | 0.03579 | -4.6674 | -9.9432 | -13.9863
|  | INCHBARE | HT |  |  |  |  | 2.7621 | 2.7316 | 2.7032 | 2.6716 | 2.3347 | 1.9916 | 1.5832 | 1.0642 | 0.24316 | -3.6105 | -7.8874 | -10.7579 | 2.6621 | 2.6284 | 2.5958 | 2.56 | 2.2863 | 2.0095 | 1.6516 | 1.1926 | 0.38 | -3.4611 | -8.0537 | -11.279 | 2.6905 | 2.6516 | 2.6137 | 2.5737 | 2.2284 | 1.8832 | 1.4705 | 0.94947 | 0.064211 | -4.1968 | -9.0516 | -12.359
|  | INCHBARE | HE |  |  |  |  | 2.7768 | 2.7653 | 2.7537 | 2.7389 | 2.2347 | 1.7305 | 1.2179 | 0.72737 | 0.025263 | -3.0021 | -6.7126 | -10.7568 | 2.6926 | 2.68 | 2.6663 | 2.6516 | 2.1832 | 1.7284 | 1.2621 | 0.81789 | 0.14 | -2.7295 | -6.4368 | -10.5 | 2.6905 | 2.6516 | 2.6137 | 2.5737 | 2.2284 | 1.8832 | 1.4705 | 0.94947 | 0.064211 | -4.1968 | -9.0516 | -12.359
|  | INCHBARE | CF |  |  |  |  | 2.7842 | 2.7768 | 2.7684 | 2.76 | 2.6095 | 2.4779 | 2.1947 | 1.8968 | 1.5663 | 0.04 | -2.2884 | -4.8263 | 2.7032 | 2.6947 | 2.6853 | 2.6768 | 2.5484 | 2.4305 | 2.1337 | 1.8389 | 1.5 | -0.014737 | -2.3568 | -5.0716 | 2.7295 | 2.72 | 2.7084 | 2.6979 | 2.5295 | 2.3821 | 2.0884 | 1.7716 | 1.3968 | -0.28 | -2.8568 | -5.7232
| DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 0 | 2.7021 | 2.6389 | 2.5758 | 2.4958 | 2.3316 | 2.1505 | 1.9516 | 1.7558 | 1.5716 | 0.70526 | -0.11895 | -0.43579 | 2.5989 | 2.5305 | 2.4632 | 2.3768 | 2.2284 | 2.06 | 1.8811 | 1.6853 | 1.5211 | 0.82316 | 0.12947 | -0.14842 | 2.54 | 2.4737 | 2.4063 | 2.32 | 2.1547 | 1.9705 | 1.7779 | 1.5632 | 1.3705 | 0.49474 | -0.34526 | -0.67474
|  | INNELLAN | EE |  |  |  |  | 2.7347 | 2.6853 | 2.6284 | 2.5589 | 2.3853 | 2.1505 | 1.9516 | 1.7684 | 1.5832 | 0.70526 | -0.11895 | -0.43579 | 2.6347 | 2.5842 | 2.5253 | 2.4537 | 2.2989 | 2.0821 | 1.9116 | 1.7484 | 1.5821 | 0.82316 | 0.12947 | -0.14842 | 2.5747 | 2.5242 | 2.4621 | 2.3895 | 2.2147 | 1.9747 | 1.7789 | 1.5895 | 1.3947 | 0.49474 | -0.34526 | -0.67474
|  | INNELLAN | HT |  |  |  |  | 2.7021 | 2.6389 | 2.5758 | 2.4958 | 2.3316 | 2.1516 | 1.9642 | 1.7558 | 1.5716 | 0.95368 | 0.53895 | 0.30842 | 2.5989 | 2.5305 | 2.4632 | 2.3768 | 2.2284 | 2.06 | 1.8811 | 1.6853 | 1.5211 | 0.98632 | 0.61368 | 0.39579 | 2.54 | 2.4737 | 2.4063 | 2.32 | 2.1547 | 1.9705 | 1.7779 | 1.5632 | 1.3705 | 0.73474 | 0.30316 | 0.06
|  | INNELLAN | HE |  |  |  |  | 2.7842 | 2.7495 | 2.7137 | 2.6621 | 2.4821 | 2.28 | 2.1084 | 1.9611 | 1.8221 | 1.2632 | 0.76737 | 0.25158 | 2.6874 | 2.6505 | 2.6126 | 2.5558 | 2.3979 | 2.2063 | 2.0463 | 1.9147 | 1.7958 | 1.3242 | 0.90842 | 0.48211 | 2.54 | 2.4737 | 2.4063 | 2.32 | 2.1547 | 1.9705 | 1.7779 | 1.5632 | 1.3705 | 0.73474 | 0.30316 | 0.06
|  | INNELLAN | CF |  |  |  |  | 2.8084 | 2.7916 | 2.7716 | 2.7537 | 2.6884 | 2.6211 | 2.5474 | 2.4789 | 2.4126 | 2.1021 | 1.7884 | 1.5632 | 2.7137 | 2.6947 | 2.6758 | 2.6558 | 2.6 | 2.5379 | 2.4674 | 2.4021 | 2.3347 | 2.0526 | 1.7874 | 1.5947 | 2.6537 | 2.6347 | 2.6158 | 2.5947 | 2.5305 | 2.4621 | 2.3863 | 2.3147 | 2.2453 | 1.9337 | 1.6147 | 1.3842
| KEITH 2 | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 0 | 8.4297 | 15.3753 | 15.0195 | 14.7353 | 13.6468 | 12.5489 | 11.2689 | 10.17 | 9.1089 | 0.56368 | -8.8658 | -15.1037 | 6.1137 | 12.6537 | 12.2716 | 11.9758 | 10.9916 | 10.1716 | 9.0916 | 8.1621 | 7.2853 | -0.61053 | -10.8526 | -16.9284 | 6.4412 | 13.1582 | 12.7676 | 12.4613 | 11.3097 | 10.2255 | 8.9445 | 7.8287 | 6.7613 | -2.3103 | -13.0808 | -19.6755
|  | INSCH | EE |  |  |  |  | 8.6013 | 15.5805 | 15.2658 | 14.9521 | 13.8195 | 12.5489 | 11.2689 | 10.17 | 9.1089 | 0.56368 | -8.3226 | -15.1037 | 6.3105 | 12.8937 | 12.5589 | 12.2337 | 11.2484 | 10.1716 | 9.0916 | 8.1621 | 7.2853 | -0.61053 | -9.1695 | -16.4705 | 6.637 | 13.3929 | 13.0424 | 12.7013 | 11.5171 | 10.2255 | 8.9445 | 7.8287 | 6.7613 | -2.3103 | -11.9576 | -19.6755
|  | INSCH | HT |  |  |  |  | 8.4297 | 15.3753 | 15.0195 | 14.7353 | 13.6468 | 12.7416 | 11.8237 | 10.7489 | 9.7416 | 1.8974 | -8.8658 | -14.3879 | 6.1137 | 12.6537 | 12.2716 | 11.9758 | 10.9916 | 10.2074 | 9.4347 | 8.5263 | 7.6979 | -0.041053 | -10.8526 | -16.9284 | 6.4412 | 13.1582 | 12.7676 | 12.4613 | 11.3097 | 10.3718 | 9.4466 | 8.3771 | 7.3824 | -1.205 | -13.0808 | -19.3934
|  | INSCH | HE |  |  |  |  | 8.7982 | 15.8963 | 15.7047 | 15.4847 | 14.2405 | 13.2868 | 12.3511 | 11.4026 | 9.9216 | 3.5479 | -5.4321 | -13.4689 | 6.5316 | 13.2316 | 13.0147 | 12.7653 | 11.6716 | 10.8537 | 10.0621 | 9.2537 | 7.8463 | 1.8726 | -6.6726 | -14.6758 | 6.4412 | 13.1582 | 12.7676 | 12.4613 | 11.3097 | 10.3718 | 9.4466 | 8.3771 | 7.3824 | -1.205 | -13.0808 | -19.3934
|  | INSCH | CF |  |  |  |  | 8.9255 | 16.1142 | 16.0132 | 15.9237 | 15.4921 | 15.0858 | 14.7079 | 14.1942 | 13.5384 | 10.3784 | 4.1711 | -0.70895 | 6.6758 | 13.4811 | 13.3674 | 13.2684 | 12.9011 | 12.5389 | 12.2063 | 11.6947 | 11.0011 | 7.8768 | 2.0211 | -3.1389 | 7.0022 | 13.9929 | 13.8771 | 13.775 | 13.3266 | 12.8992 | 12.5055 | 11.9318 | 11.1887 | 7.7318 | 1.0718 | -4.4503
| BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | YES | 0 | 24.5432 | 24.3053 | 23.9768 | 23.5663 | 23.0789 | 22.5916 | 22.1021 | 21.6158 | 21.1274 | 18.64 | 16.0989 | 14.0979 | 22.7453 | 22.4168 | 22.0011 | 21.5032 | 20.9158 | 20.3295 | 19.74 | 19.1537 | 18.5663 | 15.6316 | 12.6116 | 10.2642 | 23.7779 | 23.4863 | 23.1021 | 22.6358 | 22.0568 | 21.4789 | 20.8989 | 20.3189 | 19.7411 | 16.8253 | 13.9937 | 11.6537
|  | INVERALMOND | EE |  |  |  |  | 24.5432 | 24.3053 | 23.9768 | 23.5663 | 23.08 | 22.5916 | 22.1021 | 21.6158 | 21.1274 | 18.64 | 16.1968 | 14.2032 | 22.7453 | 22.4168 | 22.0011 | 21.5032 | 20.9168 | 20.3295 | 19.74 | 19.1537 | 18.5663 | 15.6316 | 12.7947 | 10.4526 | 23.7779 | 23.4863 | 23.1021 | 22.6358 | 22.0579 | 21.48 | 20.8989 | 20.3189 | 19.7411 | 16.8253 | 13.9937 | 11.6537
|  | INVERALMOND | HT |  |  |  |  | 24.5432 | 24.3053 | 23.9779 | 23.5674 | 23.0789 | 22.5926 | 22.1053 | 21.6189 | 21.1316 | 18.7095 | 16.2211 | 14.2305 | 22.7453 | 22.4168 | 22.0021 | 21.5042 | 20.9158 | 20.3295 | 19.7432 | 19.1558 | 18.5695 | 15.7379 | 12.8126 | 10.4716 | 23.7779 | 23.4863 | 23.1032 | 22.6368 | 22.0568 | 21.4789 | 20.9021 | 20.3232 | 19.7453 | 16.94 | 14.0179 | 11.6811
|  | INVERALMOND | HE |  |  |  |  | 24.5432 | 24.3053 | 23.9779 | 23.5674 | 23.0811 | 22.5926 | 22.1074 | 21.62 | 21.1337 | 18.6505 | 16.0989 | 14.0979 | 22.7453 | 22.4168 | 22.0021 | 21.5042 | 20.9179 | 20.3305 | 19.7442 | 19.1579 | 18.5716 | 15.64 | 12.6116 | 10.2642 | 23.7779 | 23.4863 | 23.1032 | 22.6368 | 22.0568 | 21.4789 | 20.9021 | 20.3232 | 19.7453 | 16.94 | 14.0179 | 11.6811
|  | INVERALMOND | CF |  |  |  |  | 24.5432 | 24.5432 | 24.4411 | 24.2789 | 24.0926 | 23.8853 | 23.6495 | 23.3905 | 23.1084 | 21.5916 | 20.0589 | 18.8116 | 22.9211 | 22.7674 | 22.5895 | 22.3832 | 22.1495 | 21.8895 | 21.6053 | 21.2916 | 20.9516 | 19.1232 | 17.2926 | 15.8263 | 23.9284 | 23.7979 | 23.6453 | 23.4558 | 23.2389 | 22.9979 | 22.7347 | 22.4274 | 22.0926 | 20.2895 | 18.4863 | 17.0232
| CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 0 | 2.6284 | 2.5884 | 2.5411 | 2.9863 | 2.8979 | 2.8095 | 2.7084 | 2.6105 | 2.4589 | 1.9126 | 0.96 | 0.17895 | 2.3674 | 2.3242 | 2.2737 | 2.7126 | 2.6347 | 2.5632 | 2.4874 | 2.3811 | 2.2347 | 1.72 | 0.68 | -0.071579 | 2.5379 | 2.5253 | 2.4716 | 2.9095 | 2.8158 | 2.7274 | 2.6221 | 2.5084 | 2.3389 | 1.7484 | 0.65789 | -0.20737
|  | INVERARAY | EE |  |  |  |  | 2.6579 | 2.6326 | 2.5958 | 3.0537 | 2.9463 | 2.8095 | 2.7084 | 2.6105 | 2.4958 | 1.9126 | 0.96 | 0.17895 | 2.3968 | 2.3737 | 2.3347 | 2.7895 | 2.6958 | 2.5726 | 2.4905 | 2.4063 | 2.3042 | 1.7842 | 0.83053 | -0.046316 | 2.5411 | 2.5326 | 2.5242 | 2.9874 | 2.8737 | 2.7274 | 2.6221 | 2.5158 | 2.3905 | 1.76 | 0.69579 | -0.20737
|  | INVERARAY | HT |  |  |  |  | 2.6284 | 2.5884 | 2.5411 | 2.9863 | 2.8979 | 2.8158 | 2.7284 | 2.6116 | 2.4589 | 1.9253 | 0.98 | 0.32421 | 2.3674 | 2.3242 | 2.2737 | 2.7126 | 2.6347 | 2.5632 | 2.4874 | 2.3811 | 2.2347 | 1.72 | 0.68 | -0.071579 | 2.5379 | 2.5253 | 2.4716 | 2.9095 | 2.8158 | 2.7295 | 2.6368 | 2.5084 | 2.3389 | 1.7484 | 0.65789 | -0.10632
|  | INVERARAY | HE |  |  |  |  | 2.6663 | 2.6411 | 2.6063 | 3.0663 | 2.9579 | 2.8453 | 2.7526 | 2.6505 | 2.5305 | 2.0989 | 1.3442 | 0.52 | 2.4032 | 2.3811 | 2.3442 | 2.7989 | 2.7042 | 2.6011 | 2.52 | 2.4274 | 2.3147 | 1.9253 | 1.1484 | 0.28 | 2.5379 | 2.5253 | 2.4716 | 2.9095 | 2.8158 | 2.7295 | 2.6368 | 2.5084 | 2.3389 | 1.7484 | 0.65789 | -0.10632
|  | INVERARAY | CF |  |  |  |  | 2.78 | 2.7768 | 2.7747 | 3.2726 | 3.2411 | 3.2042 | 3.1611 | 3.1242 | 3.0621 | 2.7484 | 2.2705 | 1.7211 | 2.5179 | 2.5074 | 2.4979 | 2.9895 | 2.9621 | 2.9284 | 2.8895 | 2.8558 | 2.7905 | 2.4789 | 1.9863 | 1.3853 | 2.6621 | 2.6589 | 2.6568 | 3.1547 | 3.1305 | 3.1105 | 3.0905 | 3.0737 | 3.0053 | 2.6558 | 2.1137 | 1.4811
| LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | YES | 0 | 1.0021 | 0.97789 | 0.94737 | 0.90947 | 0.56105 | 0.15263 | -0.26737 | -0.66632 | -1.2505 | -7.5516 | -11.5674 | -14.5589 | 0.95368 | 0.92632 | 0.89684 | 0.86842 | 0.56737 | 0.19684 | -0.18526 | -0.54421 | -1.1189 | -6.5474 | -10.4568 | -13.7116 | 0.97684 | 0.94632 | 0.91579 | 0.88 | 0.57895 | 0.18842 | -0.21579 | -0.56421 | -1.0979 | -7.9263 | -12.3074 | -15.7116
|  | INVERARITY | EE |  |  |  |  | 1.0074 | 0.97789 | 0.94737 | 0.90947 | 0.58421 | 0.19474 | -0.20947 | -0.55368 | -1.0642 | -7.5516 | -11.5674 | -14.5589 | 0.96526 | 0.93474 | 0.90211 | 0.86842 | 0.61474 | 0.31053 | -0.004211 | -0.27263 | -0.74316 | -6.5474 | -10.4568 | -13.7116 | 0.98842 | 0.95368 | 0.91684 | 0.88 | 0.57895 | 0.18842 | -0.21579 | -0.56421 | -1.0979 | -7.9263 | -12.3074 | -15.7116
|  | INVERARITY | HT |  |  |  |  | 1.0021 | 0.97895 | 0.94737 | 0.91684 | 0.65158 | 0.63579 | 0.30526 | -0.11158 | -0.80737 | -6.3263 | -9.9653 | -12.4453 | 0.95368 | 0.92632 | 0.89684 | 0.86947 | 0.65895 | 0.64211 | 0.35579 | -0.011579 | -0.70316 | -5.7884 | -9.7158 | -12.4863 | 0.97684 | 0.94632 | 0.91579 | 0.88526 | 0.63895 | 0.62316 | 0.28526 | -0.15158 | -0.91579 | -6.7926 | -10.9316 | -13.7937
|  | INVERARITY | HE |  |  |  |  | 1.0147 | 1.0053 | 0.99579 | 0.98526 | 0.56105 | 0.15263 | -0.26737 | -0.66632 | -1.2505 | -5.1832 | -8.2674 | -11.6621 | 0.98105 | 0.96842 | 0.95684 | 0.94526 | 0.56737 | 0.19684 | -0.18526 | -0.54421 | -1.1189 | -4.6568 | -7.7947 | -11.2337 | 0.97684 | 0.94632 | 0.91579 | 0.88526 | 0.63895 | 0.62316 | 0.28526 | -0.15158 | -0.91579 | -6.7926 | -10.9316 | -13.7937
|  | INVERARITY | CF |  |  |  |  | 1.02 | 1.0137 | 1.0084 | 1.0021 | 0.88421 | 0.77263 | 0.52105 | 0.27263 | -0.007368 | -2.7147 | -4.6589 | -6.8232 | 0.98947 | 0.98211 | 0.97579 | 0.96737 | 0.86421 | 0.77368 | 0.51895 | 0.26526 | -0.032632 | -2.4442 | -4.4295 | -6.7284 | 1.0126 | 1.0042 | 0.99684 | 0.98737 | 0.86737 | 0.76105 | 0.49053 | 0.21579 | -0.10105 | -2.9463 | -5.1032 | -7.5568
| INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | YES | 0 | 2.4158 | 2.3684 | 2.3211 | 2.2653 | 1.9168 | 1.4611 | 0.98421 | 0.53474 | -0.15895 | -4.1305 | -8.9137 | -12.7547 | 2.4095 | 2.3653 | 2.3232 | 2.28 | 1.9821 | 1.5537 | 1.1126 | 0.69789 | 0.0042105 | -3.8168 | -8.8884 | -12.6832 | 2.4084 | 2.3579 | 2.3084 | 2.2516 | 1.9011 | 1.48 | 1.0474 | 0.67263 | -0.082105 | -4.6084 | -9.8747 | -14.2716
|  | INVERARNIE | EE |  |  |  |  | 2.4295 | 2.3768 | 2.3211 | 2.2653 | 1.9168 | 1.4968 | 1.0663 | 0.69474 | 0.12947 | -4.1305 | -8.9137 | -12.7547 | 2.4263 | 2.3821 | 2.3347 | 2.2884 | 2.0074 | 1.6674 | 1.3179 | 1.0168 | 0.49895 | -3.7 | -8.4832 | -12.6832 | 2.4221 | 2.3674 | 2.3084 | 2.2516 | 1.9011 | 1.48 | 1.0474 | 0.67263 | 0.071579 | -4.6084 | -9.8747 | -14.2716
|  | INVERARNIE | HT |  |  |  |  | 2.4158 | 2.3684 | 2.3242 | 2.2779 | 1.9937 | 1.7011 | 1.3537 | 0.88737 | 0.06 | -3.8632 | -8.4632 | -11.641 | 2.4095 | 2.3653 | 2.3232 | 2.28 | 2.0484 | 1.8105 | 1.5063 | 1.0842 | 0.25895 | -3.8168 | -8.8884 | -12.4968 | 2.4084 | 2.3579 | 2.3116 | 2.2632 | 1.9779 | 1.6853 | 1.3263 | 0.83474 | -0.082105 | -4.4663 | -9.7316 | -13.4084
|  | INVERARNIE | HE |  |  |  |  | 2.4621 | 2.4421 | 2.4211 | 2.3979 | 1.9242 | 1.4611 | 0.98421 | 0.53474 | -0.15895 | -3.0947 | -6.8495 | -10.9505 | 2.4589 | 2.44 | 2.42 | 2.3979 | 1.9821 | 1.5537 | 1.1126 | 0.69789 | 0.0042105 | -2.8968 | -6.7863 | -11.0421 | 2.4084 | 2.3579 | 2.3116 | 2.2632 | 1.9779 | 1.6853 | 1.3263 | 0.83474 | -0.082105 | -4.4663 | -9.7316 | -13.4084
|  | INVERARNIE | CF |  |  |  |  | 2.4768 | 2.4663 | 2.4516 | 2.4411 | 2.3 | 2.1789 | 1.8863 | 1.5811 | 1.2316 | -0.30737 | -2.6758 | -5.3684 | 2.4747 | 2.4632 | 2.4505 | 2.4411 | 2.3284 | 2.2284 | 1.9316 | 1.6147 | 1.2347 | -0.35263 | -2.8295 | -5.7768 | 2.4737 | 2.4621 | 2.4474 | 2.4368 | 2.2958 | 2.1737 | 1.8474 | 1.5074 | 1.1074 | -0.60526 | -3.2568 | -6.3263
| FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | YES | 0.147 | 4.4604 | 4.3035 | 4.1246 | 3.8772 | 3.4214 | 3.0646 | 2.6004 | 1.9446 | 1.2277 | -1.3417 | -5.0702 | -6.4681 | 3.6583 | 3.493 | 3.3014 | 3.0298 | 2.6056 | 2.2941 | 1.8709 | 1.2151 | 0.49616 | -1.6881 | -4.9986 | -6.5691 | 3.9351 | 3.7667 | 3.5709 | 3.2962 | 2.8098 | 2.4393 | 1.9541 | 1.2267 | 0.43826 | -2.2228 | -6.1112 | -7.7028
|  | INVERBERVIE | EE |  |  |  |  | 4.5551 | 4.4204 | 4.2635 | 4.0488 | 3.5267 | 3.0646 | 2.6004 | 2.1909 | 1.6551 | -1.3417 | -4.3249 | -5.6596 | 3.7614 | 3.6246 | 3.4593 | 3.2267 | 2.7593 | 2.3709 | 1.9793 | 1.6362 | 1.1393 | -1.6881 | -4.0681 | -5.6365 | 4.0372 | 3.8951 | 3.7246 | 3.4867 | 2.933 | 2.453 | 1.9793 | 1.5635 | 0.99405 | -2.2228 | -5.2238 | -6.7933
|  | INVERBERVIE | HT |  |  |  |  | 4.4604 | 4.3035 | 4.1246 | 3.8772 | 3.4214 | 3.0646 | 2.6098 | 1.9446 | 1.2277 | -0.73437 | -5.0702 | -6.4681 | 3.6583 | 3.493 | 3.3014 | 3.0298 | 2.6056 | 2.2941 | 1.8709 | 1.2151 | 0.49616 | -1.3459 | -4.9986 | -6.5691 | 3.9351 | 3.7667 | 3.5709 | 3.2962 | 2.8098 | 2.4393 | 1.9541 | 1.2267 | 0.43826 | -1.6544 | -6.1112 | -7.7028
|  | INVERBERVIE | HE |  |  |  |  | 4.6793 | 4.5962 | 4.4614 | 4.293 | 3.8183 | 3.4709 | 3.1372 | 2.8204 | 2.3783 | 0.40037 | -3.127 | -5.4281 | 3.9025 | 3.8088 | 3.6593 | 3.4698 | 3.0498 | 2.7541 | 2.4741 | 2.2214 | 1.8077 | -0.028053 | -3.0133 | -5.2607 | 3.9351 | 3.7667 | 3.5709 | 3.2962 | 2.8098 | 2.4393 | 1.9541 | 1.2267 | 0.43826 | -1.6544 | -6.1112 | -7.7028
|  | INVERBERVIE | CF |  |  |  |  | 4.7593 | 4.7256 | 4.6825 | 4.6362 | 4.4741 | 4.3277 | 4.1741 | 4.0362 | 3.9025 | 2.8783 | -0.074368 | -1.3954 | 3.9993 | 3.9646 | 3.9162 | 3.8625 | 3.7277 | 3.6035 | 3.4667 | 3.3425 | 3.2077 | 2.2046 | -0.29858 | -1.6975 | 4.2688 | 4.233 | 4.1856 | 4.133 | 3.9667 | 3.813 | 3.6498 | 3.5046 | 3.3562 | 2.2404 | -0.81016 | -2.3081
| GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | NO | 0 | 0.20316 | 0.19579 | 0.18947 | 0.18421 | 0.17789 | 0.17053 | 0.16421 | 0.16 | 0.15474 | 0.13368 | 0.11684 | 0.10211 | 0.18842 | 0.18 | 0.17368 | 0.16737 | 0.16 | 0.15368 | 0.14632 | 0.14211 | 0.13579 | 0.11368 | 0.094737 | 0.078947 | 0.19368 | 0.18632 | 0.17895 | 0.17263 | 0.16632 | 0.15895 | 0.15263 | 0.14737 | 0.14211 | 0.12 | 0.10105 | 0.085263
|  | INVERBROOM | EE |  |  |  |  | 0.20737 | 0.20211 | 0.19684 | 0.19263 | 0.18737 | 0.18211 | 0.17684 | 0.17368 | 0.16842 | 0.15158 | 0.13895 | 0.12947 | 0.19263 | 0.18737 | 0.18105 | 0.17579 | 0.17158 | 0.16526 | 0.16 | 0.15684 | 0.15158 | 0.13263 | 0.11895 | 0.10842 | 0.19789 | 0.19263 | 0.18632 | 0.18211 | 0.17684 | 0.17053 | 0.16632 | 0.16211 | 0.15684 | 0.13895 | 0.12526 | 0.11474
|  | INVERBROOM | HT |  |  |  |  | 0.20316 | 0.19579 | 0.18947 | 0.18421 | 0.17789 | 0.17053 | 0.16421 | 0.16 | 0.15474 | 0.13368 | 0.11684 | 0.10211 | 0.18842 | 0.18 | 0.17368 | 0.16737 | 0.16 | 0.15368 | 0.14632 | 0.14211 | 0.13579 | 0.11368 | 0.094737 | 0.078947 | 0.19368 | 0.18632 | 0.17895 | 0.17263 | 0.16632 | 0.15895 | 0.15263 | 0.14737 | 0.14211 | 0.12 | 0.10105 | 0.085263
|  | INVERBROOM | HE |  |  |  |  | 0.21158 | 0.20947 | 0.20737 | 0.20421 | 0.2 | 0.19684 | 0.19368 | 0.19053 | 0.18842 | 0.17895 | 0.17263 | 0.16737 | 0.2 | 0.19579 | 0.19263 | 0.18842 | 0.18526 | 0.18211 | 0.17895 | 0.17474 | 0.17263 | 0.16316 | 0.15474 | 0.15053 | 0.19368 | 0.18632 | 0.17895 | 0.17263 | 0.16632 | 0.15895 | 0.15263 | 0.14737 | 0.14211 | 0.12 | 0.10105 | 0.085263
|  | INVERBROOM | CF |  |  |  |  | 0.21368 | 0.21263 | 0.21158 | 0.21053 | 0.20947 | 0.20737 | 0.20632 | 0.20421 | 0.20211 | 0.19368 | 0.18842 | 0.18421 | 0.20316 | 0.20105 | 0.19895 | 0.19684 | 0.19474 | 0.19263 | 0.19053 | 0.18947 | 0.18737 | 0.17684 | 0.17158 | 0.16737 | 0.20842 | 0.20632 | 0.20421 | 0.20211 | 0.2 | 0.19789 | 0.19684 | 0.19474 | 0.19263 | 0.18316 | 0.17684 | 0.17368
| FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 0 | 0.97579 | 0.96 | 0.94316 | 0.92632 | 0.87895 | 0.82526 | 0.76737 | 0.71789 | 0.63579 | 0.011579 | -0.71263 | -1.3421 | 0.99789 | 0.98632 | 0.97368 | 0.96105 | 0.91684 | 0.87053 | 0.81684 | 0.75579 | 0.64842 | 0.032632 | -0.79158 | -1.3853 | 1.0063 | 0.99053 | 0.97053 | 0.95474 | 0.9 | 0.84211 | 0.78 | 0.72526 | 0.63895 | -0.074737 | -0.89895 | -1.6084
|  | INVERGARRY | EE |  |  |  |  | 0.97579 | 0.96 | 0.94316 | 0.92632 | 0.87895 | 0.82526 | 0.76737 | 0.71789 | 0.65263 | 0.011579 | -0.71263 | -1.3421 | 1.0032 | 0.98842 | 0.97579 | 0.96105 | 0.91684 | 0.87053 | 0.82 | 0.77474 | 0.71789 | 0.073684 | -0.66105 | -1.3547 | 1.0084 | 0.99053 | 0.97053 | 0.95474 | 0.9 | 0.84211 | 0.78 | 0.72526 | 0.65158 | -0.074737 | -0.88211 | -1.6084
|  | INVERGARRY | HT |  |  |  |  | 0.97684 | 0.96526 | 0.95368 | 0.94421 | 0.90632 | 0.86947 | 0.82947 | 0.77789 | 0.65789 | 0.052632 | -0.68632 | -1.2105 | 0.99789 | 0.98632 | 0.97368 | 0.96105 | 0.92842 | 0.89474 | 0.86105 | 0.81053 | 0.67895 | 0.032632 | -0.79158 | -1.3853 | 1.0063 | 0.99263 | 0.97895 | 0.96632 | 0.92316 | 0.88316 | 0.84 | 0.78 | 0.63895 | -0.048421 | -0.89895 | -1.5063
|  | INVERGARRY | HE |  |  |  |  | 0.98842 | 0.98105 | 0.97368 | 0.96842 | 0.91895 | 0.86526 | 0.8 | 0.73684 | 0.63579 | 0.20211 | -0.37263 | -0.99789 | 1.0158 | 1.0084 | 1.0021 | 0.99684 | 0.94316 | 0.88105 | 0.81684 | 0.75579 | 0.64842 | 0.20737 | -0.4 | -1.0632 | 1.0063 | 0.99263 | 0.97895 | 0.96632 | 0.92316 | 0.88316 | 0.84 | 0.78 | 0.63895 | -0.048421 | -0.89895 | -1.5063
|  | INVERGARRY | CF |  |  |  |  | 0.99158 | 0.98947 | 0.98526 | 0.98316 | 0.96737 | 0.95263 | 0.92632 | 0.88842 | 0.83684 | 0.60316 | 0.24526 | -0.17684 | 1.0211 | 1.0168 | 1.0126 | 1.0105 | 0.99579 | 0.98211 | 0.94 | 0.89053 | 0.82842 | 0.58 | 0.19158 | -0.2779 | 1.0263 | 1.0242 | 1.0211 | 1.0179 | 1.0011 | 0.98316 | 0.94 | 0.88737 | 0.82316 | 0.55789 | 0.15053 | -0.33474
| ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | YES | 0.05 | 14.3284 | 14.1958 | 13.9337 | 13.6568 | 12.6611 | 11.6347 | 10.6 | 9.4484 | 8.4137 | 7.1232 | 5.7853 | 5.1916 | 13.6089 | 13.4647 | 13.1721 | 12.8626 | 11.7532 | 10.6047 | 9.4458 | 8.1637 | 7.0258 | 5.9511 | 4.8742 | 4.3258 | 13.8766 | 13.7345 | 13.4471 | 13.1429 | 12.0429 | 10.8839 | 9.6966 | 8.3776 | 7.2039 | 5.8966 | 4.5187 | 3.8903
|  | INVERGORDON | EE |  |  |  |  | 14.4084 | 14.2968 | 14.0779 | 13.8326 | 13.4442 | 13.1305 | 12.2232 | 11.04 | 9.9874 | 7.1232 | 5.7853 | 5.1916 | 13.6763 | 13.5805 | 13.3374 | 13.0658 | 12.6847 | 12.4079 | 11.4184 | 10.0974 | 8.9395 | 6.0058 | 4.8742 | 4.3258 | 13.9639 | 13.8439 | 13.6029 | 13.3345 | 12.9261 | 12.6103 | 11.6124 | 10.2566 | 9.0597 | 5.8966 | 4.5187 | 3.8903
|  | INVERGORDON | HT |  |  |  |  | 14.3284 | 14.1958 | 13.9337 | 13.6568 | 12.6611 | 11.6347 | 10.6 | 9.4484 | 8.4137 | 7.2432 | 6.4126 | 5.8768 | 13.6089 | 13.4647 | 13.1721 | 12.8626 | 11.7532 | 10.6047 | 9.4458 | 8.1637 | 7.0258 | 5.9511 | 5.1616 | 4.6142 | 13.8766 | 13.7345 | 13.4471 | 13.1429 | 12.0429 | 10.8839 | 9.6966 | 8.3776 | 7.2039 | 5.9755 | 5.0945 | 4.5124
|  | INVERGORDON | HE |  |  |  |  | 14.5168 | 14.4221 | 14.2421 | 14.0347 | 13.6579 | 13.4158 | 13.0316 | 12.3053 | 11.7253 | 9.2589 | 7.4663 | 6.6316 | 13.7679 | 13.6911 | 13.5047 | 13.27 | 12.9047 | 12.6921 | 12.3026 | 11.5016 | 10.8795 | 8.2742 | 6.4342 | 5.7374 | 13.8766 | 13.7345 | 13.4471 | 13.1429 | 12.0429 | 10.8839 | 9.6966 | 8.3776 | 7.2039 | 5.9755 | 5.0945 | 4.5124
|  | INVERGORDON | CF |  |  |  |  | 14.5758 | 14.5326 | 14.4884 | 14.4032 | 14.2495 | 14.1484 | 14.0495 | 13.6811 | 13.3853 | 11.8716 | 10.6547 | 10.1811 | 13.8195 | 13.7826 | 13.7447 | 13.6805 | 13.5405 | 13.4521 | 13.3637 | 12.9468 | 12.6121 | 10.9447 | 9.6679 | 9.2268 | 14.0682 | 14.0418 | 14.0124 | 13.9566 | 13.7945 | 13.6934 | 13.5945 | 13.1808 | 12.8503 | 11.1661 | 9.8018 | 9.2955
| FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | NO | 0.199 | 15.7499 | 30.1715 | 30.041 | 29.9084 | 29.6252 | 28.9536 | 27.8968 | 27.0052 | 26.1021 | 24.3789 | 22.5463 | 20.1157 | 13.6557 | 27.3326 | 27.2073 | 27.081 | 26.7147 | 25.5936 | 24.4599 | 23.5242 | 22.5757 | 20.9831 | 19.3621 | 16.5326 | 14.6276 | 28.6742 | 28.5436 | 28.411 | 28.0257 | 26.8363 | 25.6394 | 24.6394 | 23.6278 | 21.8436 | 19.9184 | 17.1363
|  | INVERLOCHY | EE |  |  |  |  | 15.8163 | 30.2515 | 30.1326 | 30.0115 | 29.7168 | 29.3842 | 29.0505 | 28.3568 | 27.3042 | 24.3789 | 22.5463 | 20.1157 | 13.7221 | 27.4178 | 27.3073 | 27.1957 | 27.001 | 26.7905 | 26.2031 | 25.1273 | 24.0126 | 21.1273 | 19.4926 | 16.8726 | 14.6928 | 28.7531 | 28.6331 | 28.5121 | 28.2247 | 27.8878 | 27.4005 | 26.2321 | 25.0405 | 21.8436 | 19.9184 | 17.1363
|  | INVERLOCHY | HT |  |  |  |  | 15.7499 | 30.1715 | 30.041 | 29.9084 | 29.6252 | 28.9536 | 27.8968 | 27.0052 | 26.1021 | 24.4284 | 22.8347 | 20.3094 | 13.6557 | 27.3326 | 27.2073 | 27.081 | 26.7147 | 25.5936 | 24.4599 | 23.5242 | 22.5757 | 20.9831 | 19.3621 | 16.5326 | 14.6276 | 28.6742 | 28.5436 | 28.411 | 28.0257 | 26.8363 | 25.6394 | 24.6394 | 23.6278 | 21.8447 | 20.0878 | 17.1731
|  | INVERLOCHY | HE |  |  |  |  | 15.9099 | 30.3894 | 30.3126 | 30.2305 | 29.9431 | 29.6968 | 29.4547 | 29.2136 | 28.981 | 26.4221 | 24.8726 | 21.8757 | 13.8157 | 27.5463 | 27.4705 | 27.3915 | 27.2115 | 27.0557 | 26.901 | 26.4905 | 25.7863 | 23.1852 | 21.6926 | 18.5557 | 14.6276 | 28.6742 | 28.5436 | 28.411 | 28.0257 | 26.8363 | 25.6394 | 24.6394 | 23.6278 | 21.8447 | 20.0878 | 17.1731
|  | INVERLOCHY | CF |  |  |  |  | 15.9699 | 30.481 | 30.4378 | 30.3968 | 30.2821 | 30.1757 | 30.0694 | 29.9726 | 29.8926 | 29.2094 | 28.1231 | 26.1168 | 13.8747 | 27.6368 | 27.5968 | 27.5568 | 27.481 | 27.4084 | 27.3378 | 27.2705 | 27.2115 | 25.9368 | 24.8631 | 22.6873 | 14.8465 | 28.9826 | 28.9415 | 28.9005 | 28.7889 | 28.6847 | 28.5826 | 28.4878 | 28.4078 | 27.1247 | 25.9331 | 23.6268
| PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 0 | 2.5984 | 2.5711 | 2.5437 | 2.5111 | 2.3837 | 2.2132 | 2.0647 | 1.9205 | 1.7826 | 0.80789 | -0.42368 | -1.3521 | 2.8658 | 2.8332 | 2.8005 | 2.77 | 2.6479 | 2.4963 | 2.3658 | 2.2363 | 2.1132 | 1.21 | 0.032105 | -0.95737 | 2.6311 | 2.5984 | 2.5658 | 2.5321 | 2.3837 | 2.1932 | 2.0342 | 1.8795 | 1.7311 | 0.68158 | -0.65526 | -1.7111
|  | INVERNEIL | EE |  |  |  |  | 2.6037 | 2.5742 | 2.5437 | 2.5111 | 2.3837 | 2.2132 | 2.0647 | 1.9205 | 1.7826 | 0.80789 | -0.42368 | -1.3521 | 2.8816 | 2.8511 | 2.8195 | 2.7889 | 2.6584 | 2.4963 | 2.3658 | 2.2363 | 2.1132 | 1.21 | 0.032105 | -0.95737 | 2.6426 | 2.6079 | 2.5711 | 2.5363 | 2.3837 | 2.1932 | 2.0342 | 1.8795 | 1.7311 | 0.68158 | -0.65526 | -1.7111
|  | INVERNEIL | HT |  |  |  |  | 2.5984 | 2.5711 | 2.5447 | 2.5184 | 2.4026 | 2.2847 | 2.1595 | 1.9889 | 1.8447 | 0.96158 | -0.14263 | -0.89316 | 2.8658 | 2.8332 | 2.8005 | 2.77 | 2.6479 | 2.5363 | 2.4195 | 2.2553 | 2.1226 | 1.2468 | 0.05 | -0.7879 | 2.6311 | 2.5984 | 2.5658 | 2.5321 | 2.3974 | 2.2668 | 2.1311 | 1.9416 | 1.7879 | 0.81947 | -0.43421 | -1.2974
|  | INVERNEIL | HE |  |  |  |  | 2.6258 | 2.6111 | 2.5974 | 2.5816 | 2.4584 | 2.3237 | 2.2016 | 2.0679 | 1.9532 | 1.19 | 0.25947 | -0.75 | 2.91 | 2.8932 | 2.8763 | 2.8595 | 2.7216 | 2.5868 | 2.4732 | 2.3437 | 2.2395 | 1.5111 | 0.57526 | -0.44579 | 2.6311 | 2.5984 | 2.5658 | 2.5321 | 2.3974 | 2.2668 | 2.1311 | 1.9416 | 1.7879 | 0.81947 | -0.43421 | -1.2974
|  | INVERNEIL | CF |  |  |  |  | 2.6353 | 2.6289 | 2.6216 | 2.6142 | 2.5721 | 2.5321 | 2.4921 | 2.4363 | 2.3563 | 1.9721 | 1.3921 | 0.75526 | 2.9247 | 2.9132 | 2.9047 | 2.8942 | 2.8532 | 2.8079 | 2.7584 | 2.6921 | 2.5995 | 2.2037 | 1.6079 | 0.92263 | 2.6858 | 2.6774 | 2.6668 | 2.6563 | 2.61 | 2.5605 | 2.5068 | 2.4342 | 2.3363 | 1.9037 | 1.2574 | 0.53632
| INVERNESS | INVERNESS | MINIMUM HEADROOM | NH 65302 42625 | NO | YES | 0 | 16.0921 | 15.4174 | 14.5605 | 13.6489 | 12.4416 | 11.2984 | 10.3489 | 9.4353 | 9.0026 | 7.1174 | 5.73 | 4.73 | 13.5568 | 12.8337 | 11.86 | 10.8242 | 9.4968 | 8.2442 | 7.22 | 6.2505 | 5.8463 | 4.0126 | 2.6221 | 1.5642 | 14.875 | 14.1624 | 13.2034 | 12.1824 | 10.8371 | 9.5466 | 8.4782 | 7.4571 | 7.0024 | 4.975 | 3.4634 | 2.3561
|  | INVERNESS | EE |  |  |  |  | 16.2942 | 15.6058 | 14.8721 | 14.0068 | 12.8847 | 11.9953 | 11.0458 | 10.1374 | 9.6953 | 7.7205 | 5.9111 | 4.9532 | 13.7768 | 13 | 12.2063 | 11.2232 | 10.0042 | 8.9842 | 7.9863 | 7.0179 | 6.6032 | 4.8105 | 3.1979 | 2.2558 | 15.0918 | 14.3224 | 13.5371 | 12.5676 | 11.3171 | 10.3066 | 9.2424 | 8.2203 | 7.7487 | 5.6613 | 3.7392 | 2.6908
|  | INVERNESS | HT |  |  |  |  | 16.0921 | 15.4174 | 14.5605 | 13.6489 | 12.4416 | 11.2984 | 10.3489 | 9.4353 | 9.0026 | 7.1174 | 5.73 | 4.73 | 13.5568 | 12.8337 | 11.86 | 10.8242 | 9.4968 | 8.2442 | 7.22 | 6.2505 | 5.8463 | 4.0126 | 2.6221 | 1.5642 | 14.875 | 14.1624 | 13.2034 | 12.1824 | 10.8371 | 9.5466 | 8.4782 | 7.4571 | 7.0024 | 4.975 | 3.4634 | 2.3561
|  | INVERNESS | HE |  |  |  |  | 16.5605 | 15.9679 | 15.2542 | 14.4795 | 13.4121 | 12.4437 | 11.63 | 10.8226 | 10.5037 | 9.2816 | 8.3205 | 7.2847 | 14.0663 | 13.3884 | 12.5695 | 11.6789 | 10.5242 | 9.4705 | 8.5989 | 7.7347 | 7.4421 | 6.3642 | 5.5463 | 4.6168 | 14.875 | 14.1624 | 13.2034 | 12.1824 | 10.8371 | 9.5466 | 8.4782 | 7.4571 | 7.0024 | 4.975 | 3.4634 | 2.3561
|  | INVERNESS | CF |  |  |  |  | 17.0542 | 16.7321 | 16.37 | 15.9889 | 15.5047 | 15.0079 | 14.6005 | 14.1563 | 13.9532 | 13.1995 | 12.5289 | 12.0342 | 14.6326 | 14.2653 | 13.8495 | 13.4116 | 12.8811 | 12.3326 | 11.8905 | 11.4 | 11.1863 | 10.4653 | 9.8674 | 9.42 | 15.9024 | 15.5718 | 15.1645 | 14.7339 | 14.1939 | 13.6361 | 13.1824 | 12.6855 | 12.4645 | 11.6613 | 10.9476 | 10.4161
| KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 0.158 | 30.1452 | 29.8136 | 28.6304 | 27.2515 | 25.6031 | 24.0062 | 22.3452 | 20.5852 | 19.2746 | 13.1146 | 9.0136 | 7.0336 | 28.0378 | 26.8115 | 25.3683 | 23.7357 | 21.9504 | 20.242 | 18.502 | 16.6788 | 15.3831 | 10.2925 | 6.8483 | 4.9494 | 29.4683 | 28.2757 | 26.8788 | 25.2988 | 23.4736 | 21.7241 | 19.942 | 18.0188 | 16.6115 | 10.3588 | 6.1599 | 4.0462
|  | INVERURIE | EE |  |  |  |  | 30.3146 | 30.0588 | 29.2567 | 27.9883 | 26.1988 | 24.4199 | 22.7852 | 21.2767 | 20.1115 | 13.1146 | 9.0136 | 7.0336 | 28.4452 | 27.3862 | 26.0936 | 24.5915 | 22.6599 | 20.7862 | 19.1315 | 17.6031 | 16.4788 | 10.3788 | 6.8483 | 4.9494 | 29.7957 | 28.8325 | 27.5778 | 26.1209 | 24.1336 | 22.1778 | 20.4262 | 18.8199 | 17.5809 | 10.3588 | 6.1599 | 4.0462
|  | INVERURIE | HT |  |  |  |  | 30.1452 | 29.8136 | 28.6304 | 27.2515 | 25.6031 | 24.0062 | 22.3452 | 20.5852 | 19.2746 | 13.4399 | 10.8157 | 8.9336 | 28.0378 | 26.8115 | 25.3683 | 23.7357 | 21.9504 | 20.242 | 18.502 | 16.6788 | 15.3831 | 10.2925 | 7.7736 | 5.8231 | 29.4683 | 28.2757 | 26.8788 | 25.2988 | 23.4736 | 21.7241 | 19.942 | 18.0188 | 16.6115 | 10.6252 | 7.8452 | 5.7883
|  | INVERURIE | HE |  |  |  |  | 30.5357 | 30.3725 | 29.9641 | 28.8483 | 27.1452 | 25.6273 | 24.2409 | 22.8536 | 21.8609 | 17.6115 | 15.1388 | 12.6431 | 28.9283 | 28.0262 | 26.882 | 25.5188 | 23.6999 | 22.0631 | 20.5946 | 19.1683 | 18.1967 | 14.5094 | 12.3662 | 10.2473 | 29.4683 | 28.2757 | 26.8788 | 25.2988 | 23.4736 | 21.7241 | 19.942 | 18.0188 | 16.6115 | 10.6252 | 7.8452 | 5.7883
|  | INVERURIE | CF |  |  |  |  | 30.6746 | 30.5831 | 30.4883 | 30.3936 | 30.0746 | 29.4294 | 28.6957 | 28.0652 | 27.6399 | 25.6736 | 24.0536 | 22.8346 | 29.3357 | 28.9231 | 28.4136 | 27.8409 | 27.1136 | 26.3673 | 25.5578 | 24.8652 | 24.4073 | 22.4452 | 21.0199 | 19.9157 | 30.1894 | 30.0978 | 29.8409 | 29.2862 | 28.5367 | 27.7725 | 26.9494 | 26.2462 | 25.7778 | 23.6715 | 22.0009 | 20.7273
| BROADFORD | KALNAKIL | MINIMUM HEADROOM | NG 69146 53941 | YES | YES | 0 | 2.5779 | 2.5632 | 2.5484 | 2.5337 | 2.5179 | 2.5042 | 2.4895 | 2.4768 | 2.4632 | 2.4074 | 2.3589 | 2.3147 | 2.5979 | 2.5832 | 2.5674 | 2.5516 | 2.5358 | 2.5211 | 2.5053 | 2.4926 | 2.4779 | 2.4168 | 2.3621 | 2.3137 | 2.6179 | 2.6021 | 2.5874 | 2.5716 | 2.5547 | 2.54 | 2.5242 | 2.5116 | 2.4979 | 2.4358 | 2.3811 | 2.3316
|  | KALNAKIL | EE |  |  |  |  | 2.5884 | 2.5768 | 2.5653 | 2.5537 | 2.5411 | 2.5305 | 2.5189 | 2.5074 | 2.4979 | 2.4526 | 2.4137 | 2.3821 | 2.6032 | 2.5968 | 2.5853 | 2.5726 | 2.56 | 2.5484 | 2.5379 | 2.5263 | 2.5158 | 2.4674 | 2.4242 | 2.3884 | 2.6253 | 2.6168 | 2.6053 | 2.5926 | 2.58 | 2.5684 | 2.5568 | 2.5453 | 2.5358 | 2.4853 | 2.4421 | 2.4063
|  | KALNAKIL | HT |  |  |  |  | 2.5779 | 2.5632 | 2.5484 | 2.5337 | 2.5179 | 2.5042 | 2.4895 | 2.4768 | 2.4632 | 2.4074 | 2.3589 | 2.3147 | 2.5979 | 2.5832 | 2.5674 | 2.5516 | 2.5358 | 2.5211 | 2.5053 | 2.4926 | 2.4779 | 2.4168 | 2.3621 | 2.3137 | 2.6179 | 2.6021 | 2.5874 | 2.5716 | 2.5547 | 2.54 | 2.5242 | 2.5116 | 2.4979 | 2.4358 | 2.3811 | 2.3316
|  | KALNAKIL | HE |  |  |  |  | 2.6011 | 2.5937 | 2.5874 | 2.58 | 2.5705 | 2.5642 | 2.5547 | 2.5474 | 2.5411 | 2.5179 | 2.4979 | 2.4789 | 2.6105 | 2.6053 | 2.6011 | 2.5958 | 2.5895 | 2.5842 | 2.5768 | 2.5684 | 2.5621 | 2.5379 | 2.5168 | 2.4968 | 2.6179 | 2.6021 | 2.5874 | 2.5716 | 2.5547 | 2.54 | 2.5242 | 2.5116 | 2.4979 | 2.4358 | 2.3811 | 2.3316
|  | KALNAKIL | CF |  |  |  |  | 2.6084 | 2.6042 | 2.6011 | 2.5958 | 2.5916 | 2.5874 | 2.5821 | 2.5789 | 2.5737 | 2.5537 | 2.5411 | 2.5326 | 2.6147 | 2.6126 | 2.6105 | 2.6074 | 2.6053 | 2.6021 | 2.6 | 2.5979 | 2.5947 | 2.5747 | 2.5611 | 2.5505 | 2.6368 | 2.6347 | 2.6326 | 2.6295 | 2.6274 | 2.6242 | 2.6211 | 2.6189 | 2.6137 | 2.5937 | 2.58 | 2.5695
| DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 0 | 2.4505 | 2.4095 | 2.3632 | 2.3179 | 2.2432 | 2.1716 | 2.1011 | 2.04 | 1.9916 | 1.8579 | 1.7463 | 1.6505 | 2.4368 | 2.3916 | 2.34 | 2.2905 | 2.2084 | 2.1284 | 2.0484 | 1.9821 | 1.9284 | 1.7832 | 1.6621 | 1.5568 | 2.4011 | 2.3558 | 2.3063 | 2.2568 | 2.1726 | 2.0937 | 2.0137 | 1.9463 | 1.8926 | 1.7463 | 1.6253 | 1.5179
|  | KAMES | EE |  |  |  |  | 2.4726 | 2.4432 | 2.4074 | 2.3705 | 2.3042 | 2.2179 | 2.1674 | 2.1253 | 2.0811 | 1.9432 | 1.8547 | 1.7821 | 2.4621 | 2.4295 | 2.3905 | 2.3516 | 2.2768 | 2.18 | 2.1242 | 2.0779 | 2.0316 | 1.8821 | 1.7895 | 1.7105 | 2.4274 | 2.3937 | 2.3547 | 2.3137 | 2.2389 | 2.1421 | 2.0863 | 2.0379 | 1.9916 | 1.84 | 1.7442 | 1.6632
|  | KAMES | HT |  |  |  |  | 2.4505 | 2.4095 | 2.3632 | 2.3179 | 2.2432 | 2.1716 | 2.1011 | 2.04 | 1.9916 | 1.8579 | 1.7463 | 1.6505 | 2.4368 | 2.3916 | 2.34 | 2.2905 | 2.2084 | 2.1284 | 2.0484 | 1.9821 | 1.9284 | 1.7832 | 1.6621 | 1.5568 | 2.4011 | 2.3558 | 2.3063 | 2.2568 | 2.1726 | 2.0937 | 2.0137 | 1.9463 | 1.8926 | 1.7463 | 1.6253 | 1.5179
|  | KAMES | HE |  |  |  |  | 2.4968 | 2.4811 | 2.4621 | 2.4337 | 2.3663 | 2.2811 | 2.2358 | 2.2063 | 2.1842 | 2.1189 | 2.0737 | 2.0411 | 2.5021 | 2.4779 | 2.4505 | 2.4168 | 2.3421 | 2.2442 | 2.1937 | 2.1621 | 2.1389 | 2.0695 | 2.0211 | 1.9853 | 2.4011 | 2.3558 | 2.3063 | 2.2568 | 2.1726 | 2.0937 | 2.0137 | 1.9463 | 1.8926 | 1.7463 | 1.6253 | 1.5179
|  | KAMES | CF |  |  |  |  | 2.5137 | 2.5042 | 2.4947 | 2.4842 | 2.4737 | 2.4558 | 2.4179 | 2.3926 | 2.3663 | 2.2821 | 2.2442 | 2.2147 | 2.5253 | 2.5116 | 2.4979 | 2.4842 | 2.4663 | 2.4421 | 2.3989 | 2.3705 | 2.3411 | 2.2453 | 2.2042 | 2.1726 | 2.4874 | 2.4747 | 2.4621 | 2.4474 | 2.4305 | 2.4063 | 2.3632 | 2.3358 | 2.3053 | 2.2116 | 2.1705 | 2.1368
| KEITH 2 | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 0 | 15.8889 | 15.7458 | 15.6047 | 15.3584 | 14.6237 | 13.7321 | 12.8037 | 11.9774 | 11.1058 | 3.9426 | -3.7942 | -10.1784 | 15.1126 | 14.8347 | 14.6074 | 14.2568 | 13.5758 | 12.8463 | 12.0337 | 11.3084 | 10.5684 | 3.7 | -4.0642 | -11.0505 | 15.6561 | 15.3666 | 15.1297 | 14.7676 | 13.9761 | 13.0487 | 12.0624 | 11.1992 | 10.3161 | 2.5497 | -5.9755 | -13.3629
|  | KEITH | EE |  |  |  |  | 15.9542 | 15.8174 | 15.6805 | 15.5342 | 14.7247 | 13.7321 | 12.8037 | 11.9774 | 11.1058 | 3.9426 | -3.7942 | -10.1784 | 15.2411 | 14.9979 | 14.8011 | 14.4968 | 13.7568 | 12.8463 | 12.0337 | 11.3084 | 10.5684 | 3.7 | -4.0642 | -11.0505 | 15.7929 | 15.5297 | 15.3203 | 15.0013 | 14.1287 | 13.0487 | 12.0624 | 11.1992 | 10.3161 | 2.5497 | -5.9755 | -13.3629
|  | KEITH | HT |  |  |  |  | 15.8889 | 15.7458 | 15.6047 | 15.3584 | 14.6237 | 13.8805 | 13.1363 | 12.91 | 12.0426 | 5.4479 | -2.0005 | -7.3216 | 15.1126 | 14.8347 | 14.6074 | 14.2568 | 13.5758 | 12.88 | 12.2021 | 11.9484 | 11.1747 | 4.4453 | -3.8095 | -9.8032 | 15.6561 | 15.3666 | 15.1297 | 14.7676 | 13.9761 | 13.1729 | 12.3824 | 12.1266 | 11.2076 | 3.8445 | -4.8103 | -10.9797
|  | KEITH | HE |  |  |  |  | 16.0426 | 15.9711 | 15.8942 | 15.8047 | 15.0963 | 14.3058 | 13.6195 | 12.7742 | 11.55 | 6.1858 | 0.12789 | -6.9721 | 15.3632 | 15.2632 | 15.1484 | 14.9137 | 14.1611 | 13.4158 | 12.8053 | 12.0042 | 10.7505 | 5.5411 | -0.74947 | -8.0368 | 15.6561 | 15.3666 | 15.1297 | 14.7676 | 13.9761 | 13.1729 | 12.3824 | 12.1266 | 11.2076 | 3.8445 | -4.8103 | -10.9797
|  | KEITH | CF |  |  |  |  | 16.0984 | 16.0584 | 16.0163 | 15.9742 | 15.71 | 15.4742 | 15.2321 | 14.8637 | 14.3089 | 11.6205 | 4.3079 | -0.20789 | 15.4263 | 15.3842 | 15.3411 | 15.2716 | 14.9884 | 14.7158 | 14.4242 | 13.9211 | 13.2632 | 10.4463 | 3.7158 | -1.14 | 15.9339 | 15.8939 | 15.8529 | 15.8139 | 15.4897 | 15.1708 | 14.8276 | 14.2666 | 13.5666 | 10.4792 | 2.7255 | -2.4713
| KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 0 | 14.8826 | 14.6879 | 14.5174 | 14.3742 | 14.1111 | 13.8542 | 13.5974 | 13.3195 | 13.0447 | 11.6532 | 9.4826 | 7.8447 | 13.5168 | 13.2484 | 13.0274 | 12.8779 | 12.6379 | 12.4011 | 12.1642 | 11.9116 | 11.6632 | 10.3137 | 8.1189 | 6.5611 | 14.0034 | 13.7382 | 13.5192 | 13.3687 | 13.095 | 12.8266 | 12.5603 | 12.2729 | 11.9866 | 10.5024 | 8.1845 | 6.3603
|  | KEMNAY | EE |  |  |  |  | 14.9668 | 14.83 | 14.6668 | 14.5289 | 14.2489 | 13.9468 | 13.6553 | 13.3953 | 13.1353 | 11.6553 | 9.4826 | 7.8447 | 13.6305 | 13.4505 | 13.2326 | 13.0547 | 12.7989 | 12.5295 | 12.2716 | 12.0411 | 11.8116 | 10.4705 | 8.3337 | 6.5611 | 14.1034 | 13.9361 | 13.7182 | 13.5392 | 13.2424 | 12.9287 | 12.6266 | 12.3571 | 12.0887 | 10.5361 | 8.1845 | 6.3603
|  | KEMNAY | HT |  |  |  |  | 14.8826 | 14.6879 | 14.5174 | 14.3742 | 14.1111 | 13.8542 | 13.5974 | 13.3195 | 13.0447 | 11.6532 | 9.6205 | 8.2321 | 13.5168 | 13.2484 | 13.0274 | 12.8779 | 12.6379 | 12.4011 | 12.1642 | 11.9116 | 11.6632 | 10.3137 | 8.1189 | 6.5705 | 14.0034 | 13.7382 | 13.5192 | 13.3687 | 13.095 | 12.8266 | 12.5603 | 12.2729 | 11.9866 | 10.5024 | 8.2445 | 6.6908
|  | KEMNAY | HE |  |  |  |  | 15.0732 | 14.9647 | 14.8405 | 14.75 | 14.5005 | 14.2921 | 14.0858 | 13.8816 | 13.6837 | 12.3805 | 10.7258 | 8.9574 | 13.7663 | 13.6147 | 13.4379 | 13.3211 | 13.1021 | 12.9179 | 12.7337 | 12.5558 | 12.3821 | 11.1021 | 9.4179 | 7.6105 | 14.0034 | 13.7382 | 13.5192 | 13.3687 | 13.095 | 12.8266 | 12.5603 | 12.2729 | 11.9866 | 10.5024 | 8.2445 | 6.6908
|  | KEMNAY | CF |  |  |  |  | 15.1468 | 15.1047 | 15.0553 | 15.0037 | 14.8921 | 14.7837 | 14.6774 | 14.5858 | 14.5068 | 13.8605 | 12.8089 | 11.6742 | 13.8642 | 13.8105 | 13.7442 | 13.6737 | 13.5653 | 13.4526 | 13.3411 | 13.2495 | 13.1632 | 12.4579 | 11.3789 | 10.1632 | 14.3066 | 14.2582 | 14.2003 | 14.1424 | 14.0234 | 13.9066 | 13.7824 | 13.6803 | 13.5876 | 12.8276 | 11.675 | 10.4108
| TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0 | 1.0547 | 1.0474 | 1.04 | 1.0347 | 1.0053 | 0.97263 | 0.93895 | 0.91158 | 0.88105 | 0.68526 | 0.46737 | 0.33789 | 1.0284 | 1.0253 | 1.02 | 1.0168 | 1.0032 | 0.97684 | 0.94947 | 0.92632 | 0.90105 | 0.72947 | 0.53368 | 0.40632 | 1.0337 | 1.0274 | 1.0189 | 1.0126 | 0.98421 | 0.95053 | 0.91789 | 0.88947 | 0.85789 | 0.65368 | 0.42316 | 0.27895
|  | KENMORE | EE |  |  |  |  | 1.0558 | 1.0495 | 1.0421 | 1.0358 | 1.0053 | 0.97263 | 0.93895 | 0.91158 | 0.88105 | 0.68526 | 0.46737 | 0.33789 | 1.0284 | 1.0253 | 1.0221 | 1.0179 | 1.0032 | 0.97684 | 0.94947 | 0.92632 | 0.90105 | 0.72947 | 0.53368 | 0.40632 | 1.0358 | 1.0274 | 1.0211 | 1.0137 | 0.98421 | 0.95053 | 0.91789 | 0.88947 | 0.85789 | 0.65368 | 0.42316 | 0.27895
|  | KENMORE | HT |  |  |  |  | 1.0547 | 1.0474 | 1.04 | 1.0347 | 1.0105 | 0.98632 | 0.96421 | 0.93579 | 0.90737 | 0.74842 | 0.59368 | 0.49895 | 1.0284 | 1.0253 | 1.02 | 1.0168 | 1.0032 | 0.98421 | 0.96421 | 0.94 | 0.91789 | 0.76842 | 0.61263 | 0.51158 | 1.0337 | 1.0274 | 1.0189 | 1.0126 | 0.98947 | 0.96526 | 0.94105 | 0.91368 | 0.88526 | 0.71579 | 0.54316 | 0.43474
|  | KENMORE | HE |  |  |  |  | 1.0621 | 1.0589 | 1.0558 | 1.0526 | 1.0253 | 1 | 0.97368 | 0.94842 | 0.91579 | 0.77789 | 0.62526 | 0.46211 | 1.0326 | 1.0305 | 1.0284 | 1.0263 | 1.0137 | 1 | 0.97579 | 0.95474 | 0.92526 | 0.80211 | 0.65895 | 0.50632 | 1.0337 | 1.0274 | 1.0189 | 1.0126 | 0.98947 | 0.96526 | 0.94105 | 0.91368 | 0.88526 | 0.71579 | 0.54316 | 0.43474
|  | KENMORE | CF |  |  |  |  | 1.0663 | 1.0642 | 1.0611 | 1.0589 | 1.0495 | 1.0389 | 1.0295 | 1.0179 | 1.0053 | 0.94105 | 0.84737 | 0.75684 | 1.0337 | 1.0326 | 1.0326 | 1.0316 | 1.0263 | 1.0221 | 1.0179 | 1.0126 | 1 | 0.94105 | 0.85158 | 0.76105 | 1.0421 | 1.0411 | 1.0389 | 1.0379 | 1.0295 | 1.0189 | 1.0095 | 0.99789 | 0.98421 | 0.91474 | 0.81368 | 0.71368
| STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 0.015 | 6.1026 | 5.9426 | 5.75 | 13.7771 | 13.3782 | 12.9813 | 12.5645 | 12.1171 | 11.6666 | 9.5866 | 7.3992 | 6.1939 | 5.6618 | 5.4861 | 5.2713 | 12.8461 | 12.4576 | 12.0713 | 11.6629 | 11.2324 | 10.8018 | 8.9082 | 6.9587 | 5.7113 | 5.8201 | 5.6422 | 5.4243 | 13.2166 | 12.7871 | 12.3597 | 11.9103 | 11.4303 | 10.9482 | 8.805 | 6.4829 | 5.1418
|  | KEPCULLOCH | EE |  |  |  |  | 6.1658 | 6.0384 | 5.8721 | 13.9255 | 13.5213 | 13.0855 | 12.6203 | 12.2024 | 11.7803 | 9.5866 | 7.3992 | 6.1939 | 5.7439 | 5.5955 | 5.4113 | 13.0187 | 12.6418 | 12.2429 | 11.8145 | 11.4187 | 11.0229 | 8.9829 | 6.9587 | 5.7113 | 5.9012 | 5.7507 | 5.5622 | 13.3839 | 12.9566 | 12.4966 | 12.0071 | 11.5629 | 11.1145 | 8.805 | 6.4829 | 5.1418
|  | KEPCULLOCH | HT |  |  |  |  | 6.1026 | 5.9426 | 5.75 | 13.7771 | 13.3782 | 12.9813 | 12.5645 | 12.1171 | 11.6666 | 9.7434 | 8.2024 | 7.0497 | 5.6618 | 5.4861 | 5.2713 | 12.8461 | 12.4576 | 12.0713 | 11.6629 | 11.2324 | 10.8018 | 8.9082 | 7.3145 | 6.0397 | 5.8201 | 5.6422 | 5.4243 | 13.2166 | 12.7871 | 12.3597 | 11.9103 | 11.4303 | 10.9482 | 8.8703 | 7.1555 | 5.8334
|  | KEPCULLOCH | HE |  |  |  |  | 6.2521 | 6.1732 | 6.0542 | 14.1487 | 13.7603 | 13.4139 | 13.0476 | 12.6887 | 12.3287 | 10.5908 | 9.0224 | 7.4571 | 5.8534 | 5.7461 | 5.6029 | 13.2513 | 12.8966 | 12.5755 | 12.2282 | 11.8882 | 11.5439 | 9.8566 | 8.3439 | 6.8566 | 5.8201 | 5.6422 | 5.4243 | 13.2166 | 12.7871 | 12.3597 | 11.9103 | 11.4303 | 10.9482 | 8.8703 | 7.1555 | 5.8334
|  | KEPCULLOCH | CF |  |  |  |  | 6.3005 | 6.2574 | 6.2068 | 14.3939 | 14.2361 | 14.0866 | 13.9266 | 13.775 | 13.6339 | 12.7697 | 11.8171 | 11.0487 | 5.9187 | 5.8618 | 5.7913 | 13.5313 | 13.3839 | 13.2429 | 13.0892 | 12.9397 | 12.7945 | 11.9324 | 11.0176 | 10.2566 | 6.0759 | 6.018 | 5.9475 | 13.9039 | 13.7376 | 13.5787 | 13.4071 | 13.2429 | 13.0871 | 12.1439 | 11.1166 | 10.2766
| TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0 | 0.31895 | 0.31684 | 0.31579 | 0.31263 | 0.31053 | 0.30947 | 0.30632 | 0.30421 | 0.30211 | 0.29474 | 0.28947 | 0.28421 | 0.30947 | 0.30842 | 0.30737 | 0.30526 | 0.30421 | 0.30316 | 0.30105 | 0.29895 | 0.29684 | 0.28842 | 0.28211 | 0.27684 | 0.31263 | 0.31053 | 0.30842 | 0.30526 | 0.30316 | 0.30105 | 0.29789 | 0.29579 | 0.29474 | 0.28526 | 0.28 | 0.27368
|  | KERRERA | EE |  |  |  |  | 0.32105 | 0.31895 | 0.31684 | 0.31579 | 0.31474 | 0.31263 | 0.31053 | 0.30947 | 0.30842 | 0.30211 | 0.29789 | 0.29474 | 0.31053 | 0.30947 | 0.30842 | 0.30737 | 0.30632 | 0.30526 | 0.30421 | 0.30316 | 0.30211 | 0.29579 | 0.29158 | 0.28842 | 0.31368 | 0.31263 | 0.31053 | 0.30842 | 0.30737 | 0.30526 | 0.30316 | 0.30105 | 0.3 | 0.29368 | 0.28842 | 0.28526
|  | KERRERA | HT |  |  |  |  | 0.31895 | 0.31684 | 0.31579 | 0.31263 | 0.31053 | 0.30947 | 0.30632 | 0.30421 | 0.30211 | 0.29474 | 0.28947 | 0.28421 | 0.30947 | 0.30842 | 0.30737 | 0.30526 | 0.30421 | 0.30316 | 0.30105 | 0.29895 | 0.29684 | 0.28842 | 0.28211 | 0.27684 | 0.31263 | 0.31053 | 0.30842 | 0.30526 | 0.30316 | 0.30105 | 0.29789 | 0.29579 | 0.29474 | 0.28526 | 0.28 | 0.27368
|  | KERRERA | HE |  |  |  |  | 0.32316 | 0.32211 | 0.32105 | 0.32 | 0.31895 | 0.31684 | 0.31684 | 0.31474 | 0.31368 | 0.31053 | 0.30842 | 0.30737 | 0.31158 | 0.31053 | 0.31053 | 0.30947 | 0.30842 | 0.30737 | 0.30737 | 0.30632 | 0.30526 | 0.30316 | 0.30211 | 0.30211 | 0.31263 | 0.31053 | 0.30842 | 0.30526 | 0.30316 | 0.30105 | 0.29789 | 0.29579 | 0.29474 | 0.28526 | 0.28 | 0.27368
|  | KERRERA | CF |  |  |  |  | 0.32421 | 0.32316 | 0.32316 | 0.32316 | 0.32211 | 0.32105 | 0.32 | 0.32 | 0.31895 | 0.31579 | 0.31368 | 0.31263 | 0.31263 | 0.31158 | 0.31158 | 0.31158 | 0.31053 | 0.31053 | 0.30947 | 0.30947 | 0.30947 | 0.30737 | 0.30632 | 0.30632 | 0.31579 | 0.31474 | 0.31474 | 0.31474 | 0.31368 | 0.31368 | 0.31263 | 0.31263 | 0.31263 | 0.30947 | 0.30632 | 0.30526
| GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | NO | 2 | -1.4789 | -1.5337 | -1.5895 | -1.6484 | -1.7305 | -1.8147 | -1.8989 | -1.9505 | -2.0211 | -2.2695 | -2.4611 | -2.6326 | -1.0211 | -1.06 | -1.1232 | -1.1832 | -1.2905 | -1.3979 | -1.5053 | -1.5611 | -1.6147 | -1.8453 | -2.0379 | -2.2084 | -1.7021 | -1.7568 | -1.8137 | -1.88 | -1.9537 | -2.0368 | -2.1221 | -2.1768 | -2.2621 | -2.5189 | -2.7189 | -2.9011
|  | KERRY FALLS | EE |  |  |  |  | -1.4611 | -1.5221 | -1.5842 | -1.6484 | -1.7116 | -1.7705 | -1.8537 | -1.9379 | -2.0211 | -2.2695 | -2.4611 | -2.6326 | -1.0084 | -1.0484 | -1.0895 | -1.1463 | -1.2053 | -1.2611 | -1.3558 | -1.4516 | -1.5484 | -1.7821 | -1.9684 | -2.1337 | -1.6853 | -1.7484 | -1.8137 | -1.88 | -1.9453 | -2.0063 | -2.0916 | -2.1768 | -2.2621 | -2.5189 | -2.7189 | -2.9011
|  | KERRY FALLS | HT |  |  |  |  | -1.4789 | -1.5337 | -1.5895 | -1.6453 | -1.7305 | -1.8147 | -1.8989 | -1.9505 | -2 | -2.2032 | -2.3716 | -2.5189 | -1.0211 | -1.06 | -1.1232 | -1.1832 | -1.2905 | -1.3979 | -1.5053 | -1.5611 | -1.6147 | -1.8453 | -2.0379 | -2.2084 | -1.7021 | -1.7568 | -1.8137 | -1.8684 | -1.9537 | -2.0368 | -2.1221 | -2.1747 | -2.2242 | -2.4453 | -2.6758 | -2.8821
|  | KERRY FALLS | HE |  |  |  |  | -1.4 | -1.4326 | -1.4653 | -1.5 | -1.5337 | -1.5653 | -1.6179 | -1.6684 | -1.7168 | -1.8474 | -1.9295 | -1.9947 | -0.97158 | -0.99368 | -1.0179 | -1.0421 | -1.0684 | -1.0916 | -1.1379 | -1.2 | -1.2621 | -1.4032 | -1.4811 | -1.5421 | -1.7021 | -1.7568 | -1.8137 | -1.8684 | -1.9537 | -2.0368 | -2.1221 | -2.1747 | -2.2242 | -2.4453 | -2.6758 | -2.8821
|  | KERRY FALLS | CF |  |  |  |  | -0.17579 | -0.18632 | -0.19684 | -0.20842 | -0.21895 | -0.23053 | -0.24105 | -0.25158 | -0.26316 | -0.31684 | -0.36211 | -0.39368 | -0.2179 | -0.22842 | -0.23895 | -0.24947 | -0.26105 | -0.27158 | -0.2821 | -0.29368 | -0.30421 | -0.41158 | -0.46421 | -0.50211 | -0.15895 | -0.17368 | -0.18947 | -0.20737 | -0.22316 | -0.23895 | -0.25474 | -0.28105 | -0.30842 | -0.41474 | -0.47579 | -0.52211
| TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0 | 0.96211 | 0.93684 | 0.91158 | 0.88632 | 0.76316 | 0.61579 | 0.46421 | 0.32947 | 0.16737 | -1.1137 | -2.5389 | -3.6211 | 0.95368 | 0.92947 | 0.90526 | 0.88 | 0.79368 | 0.67474 | 0.55368 | 0.43579 | 0.23158 | -0.92421 | -2.3084 | -3.4695 | 0.94842 | 0.92526 | 0.90316 | 0.87579 | 0.75895 | 0.60842 | 0.45579 | 0.31684 | 0.16737 | -1.2421 | -2.7937 | -4.0242
|  | KILCHRENAN | EE |  |  |  |  | 0.97368 | 0.94421 | 0.91789 | 0.88947 | 0.76316 | 0.61579 | 0.46421 | 0.32947 | 0.18316 | -1.1137 | -2.5389 | -3.6211 | 0.96632 | 0.94105 | 0.91579 | 0.89158 | 0.79368 | 0.67474 | 0.55368 | 0.44421 | 0.32105 | -0.92421 | -2.3084 | -3.4695 | 0.95684 | 0.92947 | 0.90316 | 0.87579 | 0.75895 | 0.60842 | 0.45579 | 0.31684 | 0.16737 | -1.2421 | -2.7937 | -4.0242
|  | KILCHRENAN | HT |  |  |  |  | 0.96211 | 0.93684 | 0.91158 | 0.88632 | 0.78 | 0.67158 | 0.56105 | 0.53895 | 0.29789 | -0.85579 | -2.1442 | -3.0221 | 0.95368 | 0.92947 | 0.90526 | 0.88 | 0.79368 | 0.70211 | 0.60842 | 0.58526 | 0.34947 | -0.81474 | -2.2168 | -3.2011 | 0.94842 | 0.92526 | 0.90316 | 0.87895 | 0.77684 | 0.66526 | 0.55263 | 0.52842 | 0.26632 | -1.0084 | -2.4758 | -3.4853
|  | KILCHRENAN | HE |  |  |  |  | 0.99579 | 0.98316 | 0.97053 | 0.95789 | 0.81579 | 0.66947 | 0.52 | 0.37474 | 0.16737 | -0.71789 | -1.8084 | -2.9937 | 0.98842 | 0.97579 | 0.96421 | 0.95263 | 0.83579 | 0.70316 | 0.56632 | 0.43579 | 0.23158 | -0.61579 | -1.72 | -2.9242 | 0.94842 | 0.92526 | 0.90316 | 0.87895 | 0.77684 | 0.66526 | 0.55263 | 0.52842 | 0.26632 | -1.0084 | -2.4758 | -3.4853
|  | KILCHRENAN | CF |  |  |  |  | 1.0053 | 1 | 0.99263 | 0.98526 | 0.93684 | 0.89474 | 0.81579 | 0.72842 | 0.62842 | 0.17474 | -0.50947 | -1.2611 | 1 | 0.99368 | 0.98632 | 0.97895 | 0.94316 | 0.90737 | 0.83263 | 0.74316 | 0.63684 | 0.18211 | -0.51684 | -1.3295 | 0.98632 | 0.98211 | 0.97579 | 0.96842 | 0.92421 | 0.88526 | 0.81368 | 0.71579 | 0.60211 | 0.10316 | -0.65579 | -1.5084
| STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | 0 | 1.3705 | 1.2253 | 1.0326 | 0.80316 | 0.38105 | -0.04 | -0.49684 | -0.9379 | -1.4105 | -3.7484 | -7.2863 | -10.359 | 1.0863 | 0.92737 | 0.70211 | 0.44 | 0.02 | -0.39895 | -0.83053 | -1.2863 | -1.74 | -3.8895 | -8.0063 | -10.9589 | 0.98105 | 0.81684 | 0.59053 | 0.32526 | -0.12737 | -0.5821 | -1.0484 | -1.5463 | -2.0432 | -4.4505 | -8.5874 | -11.8537
|  | KILLEARN | EE |  |  |  |  | 1.4168 | 1.3074 | 1.1432 | 0.94632 | 0.50842 | -0.014737 | -0.49684 | -0.9379 | -1.3874 | -3.7484 | -7.2842 | -10.359 | 1.1526 | 1.0221 | 0.83684 | 0.60737 | 0.18526 | -0.3221 | -0.77895 | -1.1947 | -1.6189 | -3.8337 | -7.3926 | -10.7832 | 1.0495 | 0.91263 | 0.72105 | 0.48737 | 0.022105 | -0.5379 | -1.0484 | -1.5105 | -1.98 | -4.4505 | -8.3274 | -11.8537
|  | KILLEARN | HT |  |  |  |  | 1.3705 | 1.2253 | 1.0326 | 0.80316 | 0.38105 | -0.04 | -0.47158 | -0.9379 | -1.4105 | -3.5653 | -7.2863 | -9.8789 | 1.0863 | 0.92737 | 0.70211 | 0.44 | 0.02 | -0.39895 | -0.83053 | -1.2863 | -1.74 | -3.8895 | -8.0063 | -10.9589 | 0.98105 | 0.81684 | 0.59053 | 0.32526 | -0.12737 | -0.5821 | -1.0474 | -1.5463 | -2.0432 | -4.3579 | -8.5874 | -11.5853
|  | KILLEARN | HE |  |  |  |  | 1.4505 | 1.4042 | 1.2632 | 1.0947 | 0.65368 | 0.22316 | -0.15895 | -0.53684 | -0.9221 | -2.7905 | -5.7074 | -8.92 | 1.2189 | 1.1189 | 0.95895 | 0.75684 | 0.32947 | -0.094737 | -0.46526 | -0.83053 | -1.1968 | -3.0011 | -6.0516 | -9.4221 | 0.98105 | 0.81684 | 0.59053 | 0.32526 | -0.12737 | -0.5821 | -1.0474 | -1.5463 | -2.0432 | -4.3579 | -8.5874 | -11.5853
|  | KILLEARN | CF |  |  |  |  | 1.4716 | 1.4579 | 1.4442 | 1.3937 | 1.2347 | 1.0779 | 0.89474 | 0.73263 | 0.57579 | -0.59474 | -2.4674 | -4.6168 | 1.2842 | 1.2389 | 1.1789 | 1.1084 | 0.95789 | 0.80211 | 0.61263 | 0.44421 | 0.27684 | -0.94842 | -2.9211 | -5.2853 | 1.1874 | 1.14 | 1.0758 | 1.0032 | 0.83368 | 0.66105 | 0.45579 | 0.27474 | 0.1 | -1.1937 | -3.2632 | -5.6811
| KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 0 | 2.6863 | 2.6421 | 2.5916 | 2.5305 | 2.3958 | 2.2621 | 2.1 | 1.9526 | 1.8021 | 0.88632 | 1.4326 | 0.79263 | 2.4263 | 2.3768 | 2.32 | 2.2547 | 2.1337 | 2.0116 | 1.8832 | 1.7442 | 1.6042 | 0.77579 | 1.1663 | 0.46842 | 2.5158 | 2.4832 | 2.4305 | 2.3684 | 2.2274 | 2.0863 | 1.9242 | 1.7705 | 1.6137 | 0.64105 | 1.1589 | 0.42211
|  | KILLIN TOWN | EE |  |  |  |  | 2.7084 | 2.6674 | 2.6232 | 2.5705 | 2.4274 | 2.2674 | 2.1 | 1.9526 | 1.8021 | 0.88632 | 4.3758 | 3.46 | 2.4516 | 2.4095 | 2.3611 | 2.3032 | 2.1821 | 2.0432 | 1.8958 | 1.7663 | 1.6326 | 0.78737 | 4.2968 | 3.2916 | 2.5253 | 2.5032 | 2.4642 | 2.4084 | 2.2653 | 2.0979 | 1.9242 | 1.7705 | 1.6137 | 0.64105 | 4.0189 | 2.9653
|  | KILLIN TOWN | HT |  |  |  |  | 2.6863 | 2.6421 | 2.5916 | 2.5305 | 2.3958 | 2.2621 | 2.1232 | 1.9726 | 1.8179 | 0.98421 | 4.5905 | 3.8411 | 2.4263 | 2.3768 | 2.32 | 2.2547 | 2.1337 | 2.0116 | 1.8832 | 1.7442 | 1.6042 | 0.77579 | 4.2726 | 3.4211 | 2.5158 | 2.4832 | 2.4305 | 2.3684 | 2.2274 | 2.0863 | 1.94 | 1.78 | 1.6189 | 0.70947 | 4.1453 | 3.2663
|  | KILLIN TOWN | HE |  |  |  |  | 2.7368 | 2.7126 | 2.6821 | 2.6432 | 2.5042 | 2.38 | 2.2526 | 2.1253 | 2.0011 | 1.2326 | 5.0137 | 4.0021 | 2.4842 | 2.4558 | 2.4211 | 2.3779 | 2.26 | 2.1516 | 2.0358 | 1.9211 | 1.8095 | 1.0663 | 4.8232 | 3.7832 | 2.5158 | 2.4832 | 2.4305 | 2.3684 | 2.2274 | 2.0863 | 1.94 | 1.78 | 1.6189 | 0.70947 | 4.1453 | 3.2663
|  | KILLIN TOWN | CF |  |  |  |  | 2.7558 | 2.7411 | 2.7232 | 2.7084 | 2.6537 | 2.6032 | 2.5526 | 2.5021 | 2.4232 | 2.0232 | 1.4326 | 0.79263 | 2.5032 | 2.4874 | 2.4695 | 2.4505 | 2.4032 | 2.36 | 2.3137 | 2.2684 | 2.1821 | 1.7747 | 1.1663 | 0.46842 | 2.5505 | 2.5442 | 2.5368 | 2.5305 | 2.4926 | 2.4495 | 2.3979 | 2.3474 | 2.2589 | 1.82 | 1.1589 | 0.42211
| TAYNUILT | KILMELFORD | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | 0 | 1.3611 | 1.3137 | 1.2663 | 1.2116 | 1.1537 | 5.1979 | 5.1432 | 5.0905 | 5.0368 | 4.8284 | 4.7232 | 4.6179 | 0.89579 | 0.84421 | 0.79158 | 0.73158 | 0.66842 | 4.7053 | 4.6453 | 4.5863 | 4.5284 | 4.2937 | 4.1821 | 4.0663 | 0.89368 | 0.84211 | 0.78947 | 0.72947 | 0.66632 | 4.7042 | 4.6442 | 4.5853 | 4.5274 | 4.2937 | 4.1811 | 4.0642
|  | KILMELFORD | EE |  |  |  |  | 1.3842 | 1.3432 | 1.2989 | 1.2495 | 1.1968 | 5.2453 | 5.1968 | 5.1484 | 5.1011 | 4.8979 | 4.8116 | 4.7379 | 0.92211 | 0.87895 | 0.83263 | 0.77789 | 0.72211 | 4.7663 | 4.7126 | 4.66 | 4.6095 | 4.3874 | 4.3 | 4.2253 | 0.91895 | 0.87368 | 0.82632 | 0.77053 | 0.71263 | 4.7558 | 4.7011 | 4.6474 | 4.5947 | 4.3674 | 4.2726 | 4.1916
|  | KILMELFORD | HT |  |  |  |  | 1.3611 | 1.3137 | 1.2663 | 1.2116 | 1.1537 | 5.1979 | 5.1432 | 5.0905 | 5.0368 | 4.8284 | 4.7232 | 4.6179 | 0.89579 | 0.84421 | 0.79158 | 0.73158 | 0.66842 | 4.7053 | 4.6453 | 4.5863 | 4.5284 | 4.2937 | 4.1821 | 4.0663 | 0.89368 | 0.84211 | 0.78947 | 0.72947 | 0.66632 | 4.7042 | 4.6442 | 4.5853 | 4.5274 | 4.2937 | 4.1811 | 4.0642
|  | KILMELFORD | HE |  |  |  |  | 1.4211 | 1.3947 | 1.3632 | 1.3263 | 1.2853 | 5.3463 | 5.3084 | 5.2705 | 5.2337 | 5.0884 | 5.0453 | 5.0126 | 0.96 | 0.93053 | 0.89789 | 0.85579 | 0.81158 | 4.8684 | 4.8263 | 4.7832 | 4.7432 | 4.5789 | 4.5337 | 4.5 | 0.89368 | 0.84211 | 0.78947 | 0.72947 | 0.66632 | 4.7042 | 4.6442 | 4.5853 | 4.5274 | 4.2937 | 4.1811 | 4.0642
|  | KILMELFORD | CF |  |  |  |  | 1.4432 | 1.4284 | 1.4137 | 1.3947 | 1.3758 | 5.4547 | 5.4337 | 5.4137 | 5.3905 | 5.2884 | 5.2537 | 5.2295 | 0.98526 | 0.96947 | 0.95158 | 0.93053 | 0.90947 | 4.9874 | 4.9632 | 4.94 | 4.9137 | 4.7968 | 4.7589 | 4.7326 | 0.98316 | 0.96737 | 0.95053 | 0.92947 | 0.90842 | 4.9853 | 4.9621 | 4.9389 | 4.9126 | 4.7968 | 4.7589 | 4.7337
| TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | 0.075 | 0.71237 | 0.66289 | 0.61447 | 0.56711 | 0.51763 | 0.47026 | 0.425 | 0.38184 | 0.33974 | 0.15868 | -0.003421 | -0.24763 | 0.73342 | 0.67974 | 0.62711 | 0.57658 | 0.525 | 0.47447 | 0.42605 | 0.37974 | 0.33447 | 0.13553 | -0.046579 | -0.28553 | 0.72921 | 0.67658 | 0.62395 | 0.57237 | 0.51974 | 0.46816 | 0.41974 | 0.37237 | 0.32816 | 0.12711 | -0.055 | -0.31921
|  | KILNINVER | EE |  |  |  |  | 0.74395 | 0.70395 | 0.66395 | 0.62184 | 0.58289 | 0.545 | 0.50816 | 0.47132 | 0.43974 | 0.29132 | 0.165 | -0.045526 | 0.76921 | 0.72711 | 0.68395 | 0.64079 | 0.59868 | 0.55974 | 0.52079 | 0.48289 | 0.44921 | 0.29237 | 0.15237 | -0.045526 | 0.765 | 0.72184 | 0.67763 | 0.63237 | 0.59132 | 0.54921 | 0.51026 | 0.47132 | 0.43658 | 0.27553 | 0.13237 | -0.093947
|  | KILNINVER | HT |  |  |  |  | 0.71237 | 0.66289 | 0.61447 | 0.56711 | 0.51763 | 0.47026 | 0.425 | 0.38184 | 0.33974 | 0.15868 | -0.003421 | -0.24763 | 0.73342 | 0.67974 | 0.62711 | 0.57658 | 0.525 | 0.47447 | 0.42605 | 0.37974 | 0.33447 | 0.13553 | -0.046579 | -0.28553 | 0.72921 | 0.67658 | 0.62395 | 0.57237 | 0.51974 | 0.46816 | 0.41974 | 0.37237 | 0.32816 | 0.12711 | -0.055 | -0.31921
|  | KILNINVER | HE |  |  |  |  | 0.79132 | 0.76605 | 0.73974 | 0.71237 | 0.685 | 0.66079 | 0.63553 | 0.61342 | 0.59132 | 0.51237 | 0.45553 | 0.34816 | 0.82079 | 0.79237 | 0.765 | 0.73658 | 0.70816 | 0.68289 | 0.65553 | 0.63237 | 0.60921 | 0.52711 | 0.465 | 0.36184 | 0.72921 | 0.67658 | 0.62395 | 0.57237 | 0.51974 | 0.46816 | 0.41974 | 0.37237 | 0.32816 | 0.12711 | -0.055 | -0.31921
|  | KILNINVER | CF |  |  |  |  | 0.81447 | 0.80184 | 0.785 | 0.76921 | 0.75553 | 0.73868 | 0.72289 | 0.70921 | 0.69342 | 0.62711 | 0.58079 | 0.54816 | 0.845 | 0.83026 | 0.81342 | 0.79658 | 0.78184 | 0.76395 | 0.74711 | 0.73132 | 0.71342 | 0.64184 | 0.59237 | 0.55447 | 0.84079 | 0.82711 | 0.80921 | 0.79342 | 0.77763 | 0.75974 | 0.74289 | 0.72711 | 0.71026 | 0.63868 | 0.58711 | 0.54921
| BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | YES | 0 | 5.8968 | 5.8421 | 5.7863 | 5.7295 | 5.5526 | 5.3768 | 5.1926 | 5.0484 | 4.9095 | 4.1979 | 3.3516 | 2.78 | 5.7063 | 5.6453 | 5.5842 | 5.5253 | 5.3537 | 5.1842 | 5.0053 | 4.8789 | 4.7589 | 4.1895 | 3.4295 | 2.8379 | 5.7421 | 5.6821 | 5.6211 | 5.5632 | 5.3779 | 5.1937 | 4.9968 | 4.8474 | 4.7042 | 3.9821 | 3.0968 | 2.4537
|  | KILTARLITY | EE |  |  |  |  | 5.9316 | 5.8832 | 5.8368 | 5.7905 | 5.6568 | 5.5042 | 5.3021 | 5.12 | 4.9274 | 4.1979 | 3.3516 | 2.78 | 5.7474 | 5.6958 | 5.6453 | 5.5947 | 5.4821 | 5.3547 | 5.1674 | 4.9937 | 4.8095 | 4.1895 | 3.4295 | 2.8379 | 5.7811 | 5.7295 | 5.6779 | 5.6274 | 5.4916 | 5.3347 | 5.1242 | 4.9316 | 4.7263 | 3.9821 | 3.0968 | 2.4537
|  | KILTARLITY | HT |  |  |  |  | 5.8968 | 5.8421 | 5.7863 | 5.7295 | 5.5526 | 5.3768 | 5.1926 | 5.0484 | 4.9095 | 4.3284 | 3.7105 | 3.2453 | 5.7063 | 5.6453 | 5.5842 | 5.5253 | 5.3537 | 5.1842 | 5.0053 | 4.8789 | 4.7589 | 4.2358 | 3.6116 | 3.1105 | 5.7421 | 5.6821 | 5.6211 | 5.5632 | 5.3779 | 5.1937 | 4.9968 | 4.8474 | 4.7042 | 4.0968 | 3.4263 | 2.9063
|  | KILTARLITY | HE |  |  |  |  | 5.9768 | 5.9516 | 5.9232 | 5.8958 | 5.7674 | 5.6568 | 5.5105 | 5.3653 | 5.2274 | 4.6853 | 4.0179 | 3.2947 | 5.8011 | 5.7726 | 5.7421 | 5.7116 | 5.6063 | 5.5147 | 5.3758 | 5.24 | 5.1126 | 4.64 | 3.9937 | 3.3021 | 5.7421 | 5.6821 | 5.6211 | 5.5632 | 5.3779 | 5.1937 | 4.9968 | 4.8474 | 4.7042 | 4.0968 | 3.4263 | 2.9063
|  | KILTARLITY | CF |  |  |  |  | 6.0021 | 5.9863 | 5.9695 | 5.9558 | 5.9011 | 5.8537 | 5.8063 | 5.7463 | 5.6937 | 5.42 | 4.9958 | 4.5779 | 5.8305 | 5.8126 | 5.7937 | 5.7768 | 5.7305 | 5.6895 | 5.6484 | 5.5853 | 5.5295 | 5.2747 | 4.8653 | 4.4389 | 5.8611 | 5.8442 | 5.8253 | 5.8095 | 5.7537 | 5.7042 | 5.6547 | 5.5863 | 5.5284 | 5.2411 | 4.7884 | 4.3305
| REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | YES | 5.075 | 10.4995 | 9.9111 | 9.7405 | 9.57 | 9.3784 | 9.1932 | 9.0111 | 8.83 | 8.6563 | 7.9816 | 7.4016 | 6.8879 | 9.2461 | 8.5713 | 8.3903 | 8.2061 | 8.0071 | 7.8145 | 7.625 | 7.4387 | 7.2576 | 6.5692 | 5.9482 | 5.3818 | 8.9112 | 8.2522 | 8.0712 | 7.8901 | 7.6891 | 7.4933 | 7.3017 | 7.1122 | 6.928 | 6.2354 | 5.6112 | 5.0396
|  | KINCORTH | EE |  |  |  |  | 10.5963 | 10.3037 | 9.9237 | 9.6511 | 9.4216 | 9.2226 | 9.0658 | 8.9163 | 8.7732 | 8.0974 | 7.6237 | 7.2405 | 9.4966 | 9.0218 | 8.5892 | 8.285 | 8.0376 | 7.8292 | 7.6692 | 7.5166 | 7.3713 | 6.6797 | 6.2197 | 5.8071 | 9.1491 | 8.6912 | 8.268 | 7.9691 | 7.7196 | 7.508 | 7.3428 | 7.187 | 7.0364 | 6.3217 | 5.8428 | 5.4249
|  | KINCORTH | HT |  |  |  |  | 10.4995 | 9.9111 | 9.7405 | 9.57 | 9.3784 | 9.1932 | 9.0111 | 8.83 | 8.6563 | 7.9816 | 7.4016 | 6.8879 | 9.2461 | 8.5713 | 8.3903 | 8.2061 | 8.0071 | 7.8145 | 7.625 | 7.4387 | 7.2576 | 6.5692 | 5.9482 | 5.3818 | 8.9112 | 8.2522 | 8.0712 | 7.8901 | 7.6891 | 7.4933 | 7.3017 | 7.1122 | 6.928 | 6.2354 | 5.6112 | 5.0396
|  | KINCORTH | HE |  |  |  |  | 10.6595 | 10.3826 | 10.0742 | 9.9016 | 9.7584 | 9.6363 | 9.5247 | 9.4184 | 9.3163 | 8.9111 | 8.5847 | 8.3437 | 9.6387 | 9.0997 | 8.7482 | 8.5576 | 8.4103 | 8.2871 | 8.1734 | 8.0661 | 7.9639 | 7.5545 | 7.205 | 6.9661 | 8.9112 | 8.2522 | 8.0712 | 7.8901 | 7.6891 | 7.4933 | 7.3017 | 7.1122 | 6.928 | 6.2354 | 5.6112 | 5.0396
|  | KINCORTH | CF |  |  |  |  | 10.7005 | 10.6647 | 10.6279 | 10.5911 | 10.5458 | 10.4037 | 10.2374 | 10.1289 | 10.0079 | 9.5858 | 9.3342 | 9.1521 | 9.7103 | 9.6724 | 9.6218 | 9.4745 | 9.3303 | 9.1439 | 8.9608 | 8.8418 | 8.7082 | 8.2545 | 7.9913 | 7.7997 | 9.3743 | 9.3333 | 9.2543 | 9.1333 | 8.9901 | 8.808 | 8.6249 | 8.5059 | 8.3733 | 7.9186 | 7.647 | 7.4491
| FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | NO | 0 | 0.12211 | 0.12105 | 0.12 | 0.11684 | 0.11263 | 0.11053 | 0.10737 | 0.10316 | 0.10105 | -0.21474 | -0.22526 | -0.23789 | 0.11158 | 0.11158 | 0.11158 | 0.10947 | 0.10737 | 0.10421 | 0.10211 | 0.098947 | 0.095789 | -0.15368 | -0.16526 | -0.17474 | 0.11474 | 0.11368 | 0.11158 | 0.10842 | 0.10737 | 0.10526 | 0.10316 | 0.098947 | 0.095789 | -0.2221 | -0.23368 | -0.24737
|  | KINGAIRLOCH | EE |  |  |  |  | 0.12211 | 0.12105 | 0.12 | 0.11684 | 0.11263 | 0.11053 | 0.10737 | 0.10316 | 0.10105 | -0.21474 | -0.22526 | -0.23789 | 0.11158 | 0.11158 | 0.11158 | 0.10947 | 0.10737 | 0.10526 | 0.10316 | 0.098947 | 0.095789 | -0.15368 | -0.16316 | -0.17368 | 0.11474 | 0.11368 | 0.11158 | 0.10842 | 0.10737 | 0.10526 | 0.10316 | 0.098947 | 0.095789 | -0.2221 | -0.23368 | -0.24737
|  | KINGAIRLOCH | HT |  |  |  |  | 0.12316 | 0.12211 | 0.12105 | 0.11789 | 0.11579 | 0.11263 | 0.11053 | 0.10947 | 0.10526 | -0.20737 | -0.2179 | -0.22737 | 0.11263 | 0.11263 | 0.11158 | 0.10947 | 0.10842 | 0.10421 | 0.10211 | 0.1 | 0.096842 | -0.15368 | -0.16526 | -0.17474 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.10842 | 0.10632 | 0.10316 | 0.1 | -0.21158 | -0.22421 | -0.23579
|  | KINGAIRLOCH | HE |  |  |  |  | 0.12421 | 0.12211 | 0.12211 | 0.12211 | 0.12105 | 0.12 | 0.11895 | 0.11895 | 0.11895 | -0.038947 | -0.044211 | -0.049474 | 0.11368 | 0.11263 | 0.11263 | 0.11158 | 0.11158 | 0.11053 | 0.11053 | 0.11053 | 0.11053 | -0.013684 | -0.017895 | -0.023158 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.10842 | 0.10632 | 0.10316 | 0.1 | -0.21158 | -0.22421 | -0.23579
|  | KINGAIRLOCH | CF |  |  |  |  | 0.12421 | 0.12421 | 0.12421 | 0.12316 | 0.12316 | 0.12316 | 0.12316 | 0.12316 | 0.12211 | 0.12105 | 0.11684 | 0.11474 | 0.11368 | 0.11368 | 0.11368 | 0.11263 | 0.11263 | 0.11263 | 0.11263 | 0.11263 | 0.11263 | 0.11158 | 0.10842 | 0.10632 | 0.11789 | 0.11789 | 0.11684 | 0.11579 | 0.11579 | 0.11579 | 0.11579 | 0.11579 | 0.11579 | 0.11474 | 0.11263 | 0.11053
| DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 1 | 12.4447 | 12.3142 | 12.0658 | 11.6121 | 10.9711 | 10.3816 | 9.6963 | 9.0763 | 8.4668 | 6.1637 | 2.6647 | -0.47737 | 11.5105 | 11.38 | 11.1095 | 10.5968 | 9.9663 | 9.4032 | 8.8242 | 8.2379 | 7.6463 | 5.7358 | 2.2358 | -0.96842 | 11.8887 | 11.755 | 11.4803 | 10.9666 | 10.275 | 9.6508 | 8.9287 | 8.2697 | 7.6234 | 5.2813 | 1.535 | -2.0313
|  | KINGSEAT | EE |  |  |  |  | 12.5174 | 12.4037 | 12.2879 | 11.8553 | 11.1089 | 10.3816 | 9.6963 | 9.0763 | 8.4668 | 6.1637 | 2.6647 | -0.47737 | 11.5874 | 11.4768 | 11.3632 | 10.8758 | 10.1411 | 9.4558 | 8.8242 | 8.2432 | 7.6747 | 5.7358 | 2.4337 | -0.96842 | 11.9655 | 11.8487 | 11.7297 | 11.2382 | 10.4297 | 9.6529 | 8.9287 | 8.2697 | 7.6234 | 5.2813 | 1.535 | -2.0313
|  | KINGSEAT | HT |  |  |  |  | 12.4447 | 12.3142 | 12.0658 | 11.6121 | 10.9711 | 10.3879 | 9.8068 | 9.1689 | 8.5416 | 6.7932 | 3.1816 | 0.56368 | 11.5105 | 11.38 | 11.1095 | 10.5968 | 9.9663 | 9.4032 | 8.8421 | 8.2379 | 7.6463 | 6.1253 | 2.2358 | -0.69579 | 11.8887 | 11.755 | 11.4803 | 10.9666 | 10.275 | 9.6508 | 9.0287 | 8.3497 | 7.6824 | 5.8876 | 1.8076 | -1.1924
|  | KINGSEAT | HE |  |  |  |  | 12.5995 | 12.5479 | 12.4858 | 12.1332 | 11.4405 | 10.8858 | 10.3479 | 9.8163 | 9.3005 | 7.7416 | 4.8879 | 1.4226 | 11.6695 | 11.6189 | 11.5579 | 11.1537 | 10.4905 | 9.9642 | 9.4579 | 8.9568 | 8.4716 | 7.1758 | 4.3295 | 0.80211 | 11.8887 | 11.755 | 11.4803 | 10.9666 | 10.275 | 9.6508 | 9.0287 | 8.3497 | 7.6824 | 5.8876 | 1.8076 | -1.1924
|  | KINGSEAT | CF |  |  |  |  | 12.6458 | 12.6174 | 12.5868 | 12.5574 | 12.3953 | 12.2374 | 12.0689 | 11.8353 | 11.5963 | 10.8121 | 8.8142 | 6.6037 | 11.7158 | 11.6874 | 11.6589 | 11.6295 | 11.4979 | 11.3632 | 11.2147 | 10.9832 | 10.7337 | 10.0421 | 8.0032 | 5.6263 | 12.0939 | 12.0655 | 12.035 | 12.0055 | 11.8424 | 11.6813 | 11.5066 | 11.2529 | 10.9887 | 10.1771 | 7.9655 | 5.4655
| BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 0.016 | 7.3224 | 7.1572 | 6.9582 | 6.7414 | 6.5014 | 6.2635 | 6.0835 | 5.9087 | 5.7835 | 5.2793 | 4.2561 | 3.8951 | 6.3356 | 6.1145 | 5.8777 | 5.6272 | 5.3472 | 5.0714 | 4.8672 | 4.6651 | 4.5293 | 3.9672 | 3.0229 | 2.6008 | 6.6832 | 6.4653 | 6.2306 | 5.9822 | 5.7043 | 5.4306 | 5.2274 | 5.0274 | 4.8916 | 4.3379 | 3.259 | 2.8401
|  | KINGUSSIE | EE |  |  |  |  | 7.4066 | 7.2666 | 7.1098 | 6.9182 | 6.7119 | 6.514 | 6.3614 | 6.2129 | 6.1151 | 5.6961 | 4.7708 | 4.4961 | 6.4451 | 6.2566 | 6.0514 | 5.8293 | 5.5872 | 5.3566 | 5.1819 | 5.0114 | 4.9051 | 4.4482 | 3.6187 | 3.2987 | 6.779 | 6.6043 | 6.4001 | 6.179 | 5.939 | 5.7085 | 5.5358 | 5.3653 | 5.259 | 4.8074 | 3.8379 | 3.5169
|  | KINGUSSIE | HT |  |  |  |  | 7.3224 | 7.1572 | 6.9582 | 6.7414 | 6.5014 | 6.2635 | 6.0835 | 5.9087 | 5.7835 | 5.2793 | 4.2561 | 3.8951 | 6.3356 | 6.1145 | 5.8777 | 5.6272 | 5.3472 | 5.0714 | 4.8672 | 4.6651 | 4.5293 | 3.9672 | 3.0229 | 2.6008 | 6.6832 | 6.4653 | 6.2306 | 5.9822 | 5.7043 | 5.4306 | 5.2274 | 5.0274 | 4.8916 | 4.3379 | 3.259 | 2.8401
|  | KINGUSSIE | HE |  |  |  |  | 7.5224 | 7.4193 | 7.3035 | 7.1677 | 6.9951 | 6.8319 | 6.7119 | 6.5961 | 6.5308 | 6.3024 | 5.834 | 5.7214 | 6.5914 | 6.4493 | 6.2882 | 6.1082 | 5.904 | 5.7124 | 5.5724 | 5.4387 | 5.3682 | 5.1187 | 4.6914 | 4.5598 | 6.6832 | 6.4653 | 6.2306 | 5.9822 | 5.7043 | 5.4306 | 5.2274 | 5.0274 | 4.8916 | 4.3379 | 3.259 | 2.8401
|  | KINGUSSIE | CF |  |  |  |  | 7.6193 | 7.5603 | 7.4961 | 7.4277 | 7.3551 | 7.2845 | 7.2256 | 7.1508 | 7.1045 | 6.9077 | 6.7803 | 6.6898 | 6.724 | 6.6408 | 6.5535 | 6.4556 | 6.3514 | 6.2503 | 6.1714 | 6.0829 | 6.0314 | 5.8114 | 5.6661 | 5.5587 | 6.9748 | 6.9506 | 6.8769 | 6.7958 | 6.7001 | 6.599 | 6.5211 | 6.4337 | 6.3832 | 6.1653 | 6.0201 | 5.9137
| TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | 0 | 1.2474 | 1.2116 | 1.1768 | 1.1337 | 1.0884 | 1.0358 | 0.98211 | 0.93158 | 0.88105 | 0.66737 | 0.48105 | 0.31053 | 0.80842 | 0.76105 | 0.71579 | 0.65474 | 0.59263 | 0.53263 | 0.47368 | 0.41789 | 0.36316 | 0.12421 | -0.086316 | -0.2821 | 0.58 | 0.53895 | 0.49789 | 0.44526 | 0.39158 | 0.34 | 0.28842 | 0.24 | 0.19263 | -0.007368 | -0.21684 | -0.41158
|  | KINLOCH | EE |  |  |  |  | 1.2716 | 1.2432 | 1.2137 | 1.1863 | 1.1537 | 1.12 | 1.0884 | 1.0526 | 1.0158 | 0.84105 | 0.70105 | 0.57474 | 0.84 | 0.80316 | 0.76737 | 0.73158 | 0.68842 | 0.64105 | 0.59684 | 0.55263 | 0.51053 | 0.31789 | 0.15895 | 0.013684 | 0.60842 | 0.57579 | 0.54316 | 0.51053 | 0.47263 | 0.43158 | 0.39368 | 0.35474 | 0.31895 | 0.15474 | 0.025263 | -0.11579
|  | KINLOCH | HT |  |  |  |  | 1.2474 | 1.2116 | 1.1768 | 1.1337 | 1.0884 | 1.0358 | 0.98211 | 0.93158 | 0.88105 | 0.66737 | 0.48105 | 0.31053 | 0.80842 | 0.76105 | 0.71579 | 0.65474 | 0.59263 | 0.53263 | 0.47368 | 0.41789 | 0.36316 | 0.12421 | -0.086316 | -0.2821 | 0.58 | 0.53895 | 0.49789 | 0.44526 | 0.39158 | 0.34 | 0.28842 | 0.24 | 0.19263 | -0.007368 | -0.21684 | -0.41158
|  | KINLOCH | HE |  |  |  |  | 1.3032 | 1.2842 | 1.2663 | 1.2463 | 1.2263 | 1.2074 | 1.1905 | 1.1726 | 1.1537 | 1.0768 | 1.0074 | 0.94105 | 0.88316 | 0.86105 | 0.83789 | 0.81368 | 0.79053 | 0.76737 | 0.74632 | 0.72526 | 0.70105 | 0.58842 | 0.50105 | 0.42421 | 0.58 | 0.53895 | 0.49789 | 0.44526 | 0.39158 | 0.34 | 0.28842 | 0.24 | 0.19263 | -0.007368 | -0.21684 | -0.41158
|  | KINLOCH | CF |  |  |  |  | 1.3211 | 1.3116 | 1.3011 | 1.2905 | 1.28 | 1.2695 | 1.2589 | 1.2484 | 1.2379 | 1.1874 | 1.1442 | 1.1032 | 0.90737 | 0.89474 | 0.88105 | 0.86737 | 0.85368 | 0.84 | 0.82632 | 0.81263 | 0.79895 | 0.72947 | 0.65895 | 0.6 | 0.66737 | 0.65579 | 0.64421 | 0.63158 | 0.62 | 0.60737 | 0.59474 | 0.58316 | 0.57158 | 0.51053 | 0.45263 | 0.40632
| TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | 0 | 0.96105 | 0.93158 | 0.90105 | 0.86211 | 0.78316 | 0.68316 | 0.58 | 0.49053 | 0.39684 | -0.23789 | -1.0263 | -1.6253 | 0.94842 | 0.91053 | 0.87158 | 0.83263 | 0.76105 | 0.69053 | 0.61895 | 0.54105 | 0.46105 | -0.10632 | -0.86 | -1.4842 | 0.97263 | 0.93158 | 0.89158 | 0.84947 | 0.76632 | 0.66316 | 0.55474 | 0.45895 | 0.36105 | -0.31895 | -1.1758 | -1.8558
|  | KINLOCH RANNOCH | EE |  |  |  |  | 0.96632 | 0.94211 | 0.90632 | 0.87579 | 0.78526 | 0.68316 | 0.58 | 0.49053 | 0.39684 | -0.23789 | -1.0263 | -1.6253 | 0.96105 | 0.93263 | 0.89474 | 0.85895 | 0.78632 | 0.70737 | 0.62105 | 0.54632 | 0.46842 | -0.10632 | -0.86 | -1.4842 | 0.97368 | 0.94947 | 0.90632 | 0.86526 | 0.76947 | 0.66316 | 0.55474 | 0.45895 | 0.36105 | -0.31895 | -1.1758 | -1.8558
|  | KINLOCH RANNOCH | HT |  |  |  |  | 0.96105 | 0.93158 | 0.90105 | 0.86211 | 0.78316 | 0.70316 | 0.62211 | 0.53368 | 0.44421 | -0.098947 | -0.79474 | -1.2705 | 0.94842 | 0.91053 | 0.87158 | 0.83263 | 0.76105 | 0.69053 | 0.61895 | 0.54105 | 0.46105 | -0.071579 | -0.81579 | -1.34 | 0.97263 | 0.93158 | 0.89158 | 0.84947 | 0.76632 | 0.68105 | 0.59684 | 0.50421 | 0.40947 | -0.18316 | -0.97158 | -1.5179
|  | KINLOCH RANNOCH | HE |  |  |  |  | 0.98316 | 0.97474 | 0.96316 | 0.95368 | 0.87474 | 0.8 | 0.72421 | 0.64737 | 0.53474 | 0.049474 | -0.54 | -1.18 | 0.97895 | 0.96947 | 0.96 | 0.94737 | 0.88526 | 0.81684 | 0.74105 | 0.67053 | 0.56 | 0.098947 | -0.49053 | -1.1326 | 0.97263 | 0.93158 | 0.89158 | 0.84947 | 0.76632 | 0.68105 | 0.59684 | 0.50421 | 0.40947 | -0.18316 | -0.97158 | -1.5179
|  | KINLOCH RANNOCH | CF |  |  |  |  | 0.99158 | 0.98632 | 0.98211 | 0.97684 | 0.94842 | 0.92211 | 0.88947 | 0.84947 | 0.8 | 0.55579 | 0.19053 | -0.20737 | 0.98947 | 0.98316 | 0.97684 | 0.97263 | 0.94842 | 0.92842 | 0.89474 | 0.84316 | 0.78632 | 0.54211 | 0.17053 | -0.25579 | 0.99474 | 0.99053 | 0.98632 | 0.98316 | 0.95789 | 0.93579 | 0.90105 | 0.84737 | 0.78632 | 0.51789 | 0.11368 | -0.33684
| GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | NO | 0 | 1.0179 | 0.99368 | 0.97053 | 0.94526 | 0.92105 | 0.89789 | 0.87579 | 0.85474 | 0.83368 | 0.73579 | 0.65053 | 0.57263 | 0.96316 | 0.93684 | 0.91368 | 0.88842 | 0.86526 | 0.84 | 0.81789 | 0.79579 | 0.77579 | 0.67263 | 0.58526 | 0.50316 | 0.98 | 0.95368 | 0.92947 | 0.90316 | 0.87789 | 0.85368 | 0.83053 | 0.80737 | 0.78526 | 0.67684 | 0.58316 | 0.49684
|  | KINLOCHEWE | EE |  |  |  |  | 1.0274 | 1.0032 | 0.97789 | 0.95368 | 0.92842 | 0.90526 | 0.88105 | 0.86 | 0.83895 | 0.73579 | 0.65053 | 0.57263 | 0.97579 | 0.95368 | 0.93053 | 0.90842 | 0.88526 | 0.86421 | 0.84211 | 0.82211 | 0.80316 | 0.71053 | 0.63158 | 0.55789 | 0.99053 | 0.96421 | 0.93789 | 0.91158 | 0.88421 | 0.86 | 0.83368 | 0.80947 | 0.78737 | 0.67684 | 0.58316 | 0.49684
|  | KINLOCHEWE | HT |  |  |  |  | 1.0179 | 0.99368 | 0.97053 | 0.94526 | 0.92105 | 0.89789 | 0.87579 | 0.85474 | 0.83368 | 0.73579 | 0.65158 | 0.57368 | 0.96316 | 0.93684 | 0.91368 | 0.88842 | 0.86526 | 0.84 | 0.81789 | 0.79579 | 0.77579 | 0.67263 | 0.58526 | 0.50316 | 0.98 | 0.95368 | 0.92947 | 0.90316 | 0.87789 | 0.85368 | 0.83053 | 0.80737 | 0.78526 | 0.67895 | 0.58632 | 0.49895
|  | KINLOCHEWE | HE |  |  |  |  | 1.0442 | 1.0368 | 1.0274 | 1.0137 | 1 | 0.98842 | 0.97474 | 0.96316 | 0.95158 | 0.90632 | 0.86632 | 0.82947 | 1.0011 | 0.98842 | 0.97579 | 0.96211 | 0.94947 | 0.93789 | 0.92421 | 0.91368 | 0.90211 | 0.85895 | 0.82211 | 0.78526 | 0.98 | 0.95368 | 0.92947 | 0.90316 | 0.87789 | 0.85368 | 0.83053 | 0.80737 | 0.78526 | 0.67895 | 0.58632 | 0.49895
|  | KINLOCHEWE | CF |  |  |  |  | 1.0537 | 1.0495 | 1.0453 | 1.0411 | 1.0368 | 1.0326 | 1.0253 | 1.0189 | 1.0126 | 0.98316 | 0.96211 | 0.94632 | 1.0137 | 1.0084 | 1 | 0.99474 | 0.98526 | 0.98 | 0.97158 | 0.96632 | 0.95789 | 0.92737 | 0.90526 | 0.88842 | 1.0295 | 1.0263 | 1.0179 | 1.0116 | 1.0032 | 0.99579 | 0.98842 | 0.98316 | 0.97474 | 0.94316 | 0.92105 | 0.90316
| KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 0 | 0.78211 | 0.69158 | 0.60105 | 0.50526 | 0.36421 | 0.22421 | 0.047368 | -0.13053 | -0.30842 | -1.0389 | -1.9853 | -2.8274 | 0.70211 | 0.6 | 0.49684 | 0.39263 | 0.26316 | 0.13895 | -0.029474 | -0.19474 | -0.36 | -1.0095 | -1.8505 | -2.6368 | 1.0474 | 0.94316 | 0.83579 | 0.72842 | 0.57368 | 0.42 | 0.22842 | 0.027368 | -0.17158 | -0.9579 | -2.0284 | -2.9895
|  | KINLOCHLEVEN | EE |  |  |  |  | 0.78211 | 0.69158 | 0.60105 | 0.50526 | 0.36421 | 0.22421 | 0.047368 | -0.13053 | -0.30842 | -1.0389 | -1.9853 | -2.8274 | 0.70211 | 0.6 | 0.49684 | 0.39263 | 0.26316 | 0.13895 | -0.029474 | -0.19474 | -0.36 | -1.0095 | -1.8505 | -2.6368 | 1.0474 | 0.94316 | 0.83579 | 0.72842 | 0.57368 | 0.42 | 0.22842 | 0.027368 | -0.17158 | -0.9579 | -2.0284 | -2.9895
|  | KINLOCHLEVEN | HT |  |  |  |  | 0.80947 | 0.76421 | 0.71474 | 0.65684 | 0.51579 | 0.37789 | 0.24105 | 0.14737 | 0.052632 | -0.48316 | -1.3137 | -1.9242 | 0.72316 | 0.66526 | 0.60632 | 0.54842 | 0.42632 | 0.30421 | 0.17474 | 0.094737 | 0.01579 | -0.47158 | -1.3421 | -1.9821 | 1.0632 | 1 | 0.93579 | 0.87263 | 0.71684 | 0.56526 | 0.41474 | 0.31368 | 0.21474 | -0.37158 | -1.3221 | -2.0232
|  | KINLOCHLEVEN | HE |  |  |  |  | 0.84632 | 0.81263 | 0.77789 | 0.74211 | 0.66737 | 0.59789 | 0.51263 | 0.41368 | 0.30737 | -0.24 | -0.90316 | -1.6116 | 0.76737 | 0.73579 | 0.70105 | 0.66 | 0.59474 | 0.53158 | 0.44316 | 0.35684 | 0.26842 | -0.21579 | -0.85474 | -1.5568 | 1.0632 | 1 | 0.93579 | 0.87263 | 0.71684 | 0.56526 | 0.41474 | 0.31368 | 0.21474 | -0.37158 | -1.3221 | -2.0232
|  | KINLOCHLEVEN | CF |  |  |  |  | 0.87263 | 0.86 | 0.84737 | 0.83368 | 0.80526 | 0.78 | 0.75474 | 0.72842 | 0.67684 | 0.40526 | 0.027368 | -0.39789 | 0.78632 | 0.77789 | 0.76632 | 0.75368 | 0.73368 | 0.71368 | 0.68842 | 0.65263 | 0.59789 | 0.32526 | -0.067368 | -0.53053 | 1.1674 | 1.1484 | 1.1305 | 1.1105 | 1.0758 | 1.0432 | 1.0116 | 0.96421 | 0.89368 | 0.59053 | 0.16421 | -0.32421
| FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | NO | 0 | 1.0084 | 0.98842 | 0.96842 | 0.94737 | 0.92526 | 0.90632 | 0.88632 | 0.86632 | 0.84421 | 0.75053 | 0.66947 | 0.58737 | 1.0032 | 0.98316 | 0.96421 | 0.94211 | 0.92211 | 0.90316 | 0.88421 | 0.86526 | 0.84316 | 0.75368 | 0.67474 | 0.59579 | 0.99895 | 0.98105 | 0.96316 | 0.94 | 0.91895 | 0.89895 | 0.87895 | 0.85895 | 0.83684 | 0.74211 | 0.66 | 0.57789
|  | KINLOCHMOIDART | EE |  |  |  |  | 1.0084 | 0.98842 | 0.96842 | 0.94737 | 0.92526 | 0.90632 | 0.88632 | 0.86632 | 0.84421 | 0.75053 | 0.66947 | 0.58737 | 1.0032 | 0.98316 | 0.96421 | 0.94211 | 0.92211 | 0.90316 | 0.88421 | 0.86526 | 0.84316 | 0.75368 | 0.67474 | 0.59579 | 0.99895 | 0.98105 | 0.96316 | 0.94 | 0.91895 | 0.89895 | 0.87895 | 0.85895 | 0.83684 | 0.74211 | 0.66 | 0.57789
|  | KINLOCHMOIDART | HT |  |  |  |  | 1.0158 | 1.0116 | 1.0074 | 1.0011 | 0.99579 | 0.98947 | 0.98316 | 0.97579 | 0.97053 | 0.93895 | 0.90842 | 0.87579 | 1.0084 | 1.0074 | 1.0011 | 0.99579 | 0.98947 | 0.98421 | 0.97789 | 0.96947 | 0.96421 | 0.93263 | 0.90211 | 0.86947 | 1.0095 | 1.0042 | 0.99895 | 0.99368 | 0.98737 | 0.98211 | 0.97579 | 0.96842 | 0.96316 | 0.93053 | 0.89789 | 0.86526
|  | KINLOCHMOIDART | HE |  |  |  |  | 1.0168 | 1.0126 | 1.0095 | 1.0042 | 0.99895 | 0.99263 | 0.98632 | 0.98 | 0.97474 | 0.94421 | 0.91263 | 0.88105 | 1.0095 | 1.0084 | 1.0042 | 0.99789 | 0.99263 | 0.98737 | 0.98105 | 0.97474 | 0.96947 | 0.94 | 0.90842 | 0.87789 | 1.0095 | 1.0042 | 0.99895 | 0.99368 | 0.98737 | 0.98211 | 0.97579 | 0.96842 | 0.96316 | 0.93053 | 0.89789 | 0.86526
|  | KINLOCHMOIDART | CF |  |  |  |  | 1.02 | 1.0179 | 1.0168 | 1.0168 | 1.0158 | 1.0147 | 1.0137 | 1.0137 | 1.0116 | 1.0074 | 1.0021 | 0.99684 | 1.0126 | 1.0105 | 1.0105 | 1.0095 | 1.0095 | 1.0095 | 1.0084 | 1.0084 | 1.0063 | 1.0021 | 0.99579 | 0.99158 | 1.0147 | 1.0126 | 1.0105 | 1.0095 | 1.0095 | 1.0074 | 1.0063 | 1.0063 | 1.0032 | 0.99895 | 0.99474 | 0.99053
| ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 2.08 | 12.2258 | 12.1289 | 12.0321 | 11.9332 | 11.7426 | 11.5584 | 11.3805 | 11.1953 | 11.01 | 9.9837 | 8.53 | 7.4647 | 11.4505 | 11.3463 | 11.2421 | 11.1347 | 10.9589 | 10.7874 | 10.6232 | 10.4568 | 10.2905 | 9.3453 | 7.9232 | 6.8368 | 11.8255 | 11.7213 | 11.6161 | 11.5076 | 11.3097 | 11.1171 | 10.9318 | 10.7413 | 10.5508 | 9.4855 | 7.9108 | 6.7066
|  | KINLOSS | EE |  |  |  |  | 12.2795 | 12.1974 | 12.1121 | 12.0226 | 11.8311 | 11.6195 | 11.41 | 11.2342 | 11.0563 | 9.9837 | 8.53 | 7.4647 | 11.5095 | 11.4221 | 11.3316 | 11.2379 | 11.0642 | 10.8758 | 10.6905 | 10.5358 | 10.3811 | 9.4 | 7.9874 | 6.8368 | 11.8845 | 11.7961 | 11.7034 | 11.6076 | 11.4076 | 11.1887 | 10.9729 | 10.7929 | 10.6097 | 9.4855 | 7.9108 | 6.7066
|  | KINLOSS | HT |  |  |  |  | 12.2258 | 12.1289 | 12.0321 | 11.9332 | 11.7426 | 11.5584 | 11.3805 | 11.1953 | 11.01 | 10.0374 | 8.7132 | 7.8184 | 11.4505 | 11.3463 | 11.2421 | 11.1347 | 10.9589 | 10.7874 | 10.6232 | 10.4568 | 10.2905 | 9.3453 | 7.9232 | 6.9263 | 11.8255 | 11.7213 | 11.6161 | 11.5076 | 11.3097 | 11.1171 | 10.9318 | 10.7413 | 10.5508 | 9.5066 | 8.015 | 6.9939
|  | KINLOSS | HE |  |  |  |  | 12.3542 | 12.3005 | 12.2437 | 12.1826 | 12.0016 | 11.8416 | 11.6889 | 11.5489 | 11.4079 | 10.4732 | 9.3721 | 8.1932 | 11.5895 | 11.5337 | 11.4716 | 11.4053 | 11.2453 | 11.1032 | 10.9663 | 10.8463 | 10.7242 | 9.8232 | 8.7105 | 7.5179 | 11.8255 | 11.7213 | 11.6161 | 11.5076 | 11.3097 | 11.1171 | 10.9318 | 10.7413 | 10.5508 | 9.5066 | 8.015 | 6.9939
|  | KINLOSS | CF |  |  |  |  | 12.3974 | 12.3658 | 12.3332 | 12.3005 | 12.2226 | 12.15 | 12.0795 | 12.0184 | 11.9637 | 11.4668 | 10.77 | 10.0237 | 11.6368 | 11.6032 | 11.5684 | 11.5316 | 11.4611 | 11.3937 | 11.3305 | 11.2737 | 11.2211 | 10.7221 | 10.0137 | 9.2158 | 12.0118 | 11.9782 | 11.9424 | 11.9066 | 11.8255 | 11.7487 | 11.6761 | 11.6129 | 11.555 | 11.0139 | 10.2434 | 9.4013
| BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 0 | 8.88 | 8.7053 | 8.4926 | 8.2558 | 7.9368 | 7.6232 | 7.2905 | 6.9547 | 6.6179 | 5.0863 | 1.5568 | 0.44 | 7.1305 | 6.9368 | 6.6989 | 6.4337 | 6.0958 | 5.7611 | 5.4063 | 5.0516 | 4.6958 | 3.0316 | -0.12632 | -1.4074 | 7.5463 | 7.36 | 7.1316 | 6.8747 | 6.5358 | 6.2 | 5.8432 | 5.4842 | 5.1242 | 3.4368 | -0.27684 | -1.5568
|  | KIPPEN | EE |  |  |  |  | 8.9716 | 8.8284 | 8.6474 | 8.4484 | 8.1632 | 7.8726 | 7.5547 | 7.26 | 6.9653 | 5.4632 | 1.9 | 0.90526 | 7.2316 | 7.0726 | 6.8716 | 6.6495 | 6.3537 | 6.0589 | 5.7295 | 5.4221 | 5.1168 | 3.5547 | 0.44105 | -0.66737 | 7.6442 | 7.4905 | 7.2968 | 7.0811 | 6.7779 | 6.4716 | 6.1316 | 5.8168 | 5.5021 | 3.8874 | 0.16842 | -0.9621
|  | KIPPEN | HT |  |  |  |  | 8.88 | 8.7053 | 8.4926 | 8.2558 | 7.9368 | 7.6232 | 7.2905 | 6.9547 | 6.6179 | 5.0863 | 1.5568 | 0.44 | 7.1305 | 6.9368 | 6.6989 | 6.4337 | 6.0958 | 5.7611 | 5.4063 | 5.0516 | 4.6958 | 3.0316 | -0.12632 | -1.4074 | 7.5463 | 7.36 | 7.1316 | 6.8747 | 6.5358 | 6.2 | 5.8432 | 5.4842 | 5.1242 | 3.4368 | -0.27684 | -1.5568
|  | KIPPEN | HE |  |  |  |  | 9.0895 | 8.9853 | 8.8453 | 8.6832 | 8.4232 | 8.1811 | 7.9179 | 7.6621 | 7.4074 | 6.1895 | 4.0095 | 2.9537 | 7.36 | 7.2432 | 7.0863 | 6.9021 | 6.6358 | 6.3853 | 6.1074 | 5.8389 | 5.5705 | 4.2758 | 2.2653 | 1.1474 | 7.5463 | 7.36 | 7.1316 | 6.8747 | 6.5358 | 6.2 | 5.8432 | 5.4842 | 5.1242 | 3.4368 | -0.27684 | -1.5568
|  | KIPPEN | CF |  |  |  |  | 9.1484 | 9.1137 | 9.0463 | 8.9737 | 8.8642 | 8.7547 | 8.6379 | 8.5179 | 8.4 | 7.7263 | 7.1 | 6.5316 | 7.4232 | 7.3853 | 7.3116 | 7.2284 | 7.1158 | 7 | 6.8747 | 6.7463 | 6.6168 | 5.8842 | 5.2063 | 4.5863 | 7.8295 | 7.7937 | 7.7211 | 7.6421 | 7.5263 | 7.4095 | 7.2821 | 7.1537 | 7.0263 | 6.2968 | 5.6168 | 4.9989
| THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | YES | 7.5 | 18.5684 | 18.4442 | 18.1958 | 17.1684 | 16.0684 | 15.4547 | 14.8484 | 14.0547 | 12.6147 | 9.8158 | 8.3684 | 7.0358 | 15.2853 | 15.0021 | 14.1642 | 13.0095 | 11.8011 | 11.1579 | 10.5232 | 9.6726 | 8.0663 | 5.1632 | 3.5632 | 2.0874 | 15.9147 | 15.7947 | 15.4432 | 14.3442 | 13.1695 | 12.5253 | 11.8905 | 11.0484 | 9.5 | 6.5505 | 4.9516 | 3.4589
|  | KIRKWALL | EE |  |  |  |  | 19.6716 | 19.3284 | 18.6947 | 17.8474 | 16.8705 | 16.2642 | 15.7063 | 15.1684 | 14.6295 | 21.1442 | 19.4811 | 18.3411 | 15.8316 | 15.4126 | 14.7126 | 13.7632 | 12.6968 | 12.0674 | 11.4926 | 10.9358 | 10.3768 | 19.0463 | 17.4032 | 16.1842 | 16.9926 | 16.6358 | 15.9695 | 15.0621 | 14.0211 | 13.3811 | 12.7937 | 12.2284 | 11.66 | 19.1726 | 17.4116 | 16.1579
|  | KIRKWALL | HT |  |  |  |  | 19.4295 | 18.9505 | 18.1958 | 17.1684 | 16.0684 | 15.4547 | 14.8484 | 14.0547 | 12.6147 | 9.8158 | 8.3684 | 7.0358 | 15.5168 | 15.0021 | 14.1642 | 13.0095 | 11.8011 | 11.1579 | 10.5232 | 9.6726 | 8.0663 | 5.1632 | 3.5632 | 2.0874 | 16.7379 | 16.2463 | 15.4432 | 14.3442 | 13.1695 | 12.5253 | 11.8905 | 11.0484 | 9.5 | 6.5505 | 4.9516 | 3.4589
|  | KIRKWALL | HE |  |  |  |  | 20.0242 | 19.72 | 19.2337 | 18.4863 | 17.5905 | 17.1042 | 16.6653 | 16.2263 | 15.9105 | 13.12 | 12.0221 | 11.0663 | 16.2863 | 15.8705 | 15.2821 | 14.4379 | 13.46 | 12.9505 | 12.4947 | 12.04 | 11.7232 | 8.6863 | 7.5653 | 6.6168 | 16.7379 | 16.2463 | 15.4432 | 14.3442 | 13.1695 | 12.5253 | 11.8905 | 11.0484 | 9.5 | 6.5505 | 4.9516 | 3.4589
|  | KIRKWALL | CF |  |  |  |  | 18.5684 | 18.4442 | 18.3126 | 18.1895 | 18.0168 | 17.8389 | 17.6663 | 17.4505 | 17.2084 | 14.64 | 13.7979 | 13.2147 | 15.2853 | 15.1295 | 14.9611 | 14.8095 | 14.6147 | 14.4042 | 14.2042 | 13.9242 | 13.6074 | 10.6989 | 9.8274 | 9.2189 | 15.9147 | 15.7947 | 15.6663 | 15.5463 | 15.3779 | 15.1832 | 14.9874 | 14.7232 | 14.4211 | 11.6232 | 10.7263 | 10.1032
| BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 0 | 0.42 | 0.41474 | -0.053684 | -0.057895 | -0.062105 | -0.065263 | -0.069474 | -0.072632 | -0.075789 | -0.089474 | -0.096842 | -0.10105 | 0.45579 | 0.44947 | 0.0042105 | -0.001053 | -0.005263 | -0.009474 | -0.014737 | -0.017895 | -0.022105 | -0.038947 | -0.049474 | -0.057895 | 0.29158 | 0.28421 | -0.16421 | -0.16947 | -0.17368 | -0.17684 | -0.1821 | -0.18526 | -0.18947 | -0.20421 | -0.2179 | -0.22842
|  | KISHORNHILL | EE |  |  |  |  | 0.42211 | 0.41895 | -0.053684 | -0.057895 | -0.062105 | -0.065263 | -0.069474 | -0.072632 | -0.075789 | -0.089474 | -0.096842 | -0.10105 | 0.45895 | 0.45474 | 0.0042105 | -0.001053 | -0.005263 | -0.009474 | -0.014737 | -0.017895 | -0.022105 | -0.038947 | -0.049474 | -0.057895 | 0.29474 | 0.29053 | -0.16421 | -0.16947 | -0.17368 | -0.17684 | -0.1821 | -0.18526 | -0.18947 | -0.20421 | -0.2179 | -0.22842
|  | KISHORNHILL | HT |  |  |  |  | 0.42 | 0.41474 | 0.41053 | 0.40526 | 0.4 | 0.39474 | 0.39053 | 0.38526 | 0.38105 | 0.36632 | 0.35684 | 0.35053 | 0.45579 | 0.44947 | 0.44421 | 0.43789 | 0.43158 | 0.42526 | 0.42 | 0.41474 | 0.40947 | 0.39053 | 0.37579 | 0.36421 | 0.29158 | 0.28421 | 0.27789 | 0.27158 | 0.26421 | 0.25789 | 0.25158 | 0.24526 | 0.24 | 0.21789 | 0.2 | 0.18421
|  | KISHORNHILL | HE |  |  |  |  | 0.42632 | 0.42421 | 0.42105 | 0.41789 | 0.41474 | 0.41263 | 0.40947 | 0.40737 | 0.40421 | 0.39684 | 0.39263 | 0.39053 | 0.46421 | 0.46105 | 0.45789 | 0.45474 | 0.45053 | 0.44842 | 0.44421 | 0.44211 | 0.43895 | 0.42947 | 0.42421 | 0.42 | 0.29158 | 0.28421 | 0.27789 | 0.27158 | 0.26421 | 0.25789 | 0.25158 | 0.24526 | 0.24 | 0.21789 | 0.2 | 0.18421
|  | KISHORNHILL | CF |  |  |  |  | 0.42947 | 0.42737 | 0.42632 | 0.42526 | 0.42316 | 0.42211 | 0.42105 | 0.41895 | 0.41789 | 0.41158 | 0.40842 | 0.40737 | 0.46737 | 0.46526 | 0.46421 | 0.46211 | 0.46 | 0.45895 | 0.45684 | 0.45474 | 0.45368 | 0.44632 | 0.44105 | 0.43895 | 0.30421 | 0.30211 | 0.30105 | 0.29895 | 0.29684 | 0.29474 | 0.29263 | 0.29053 | 0.28947 | 0.28 | 0.27474 | 0.27158
| BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 0 | 7.2074 | 7.1526 | 7.0968 | 7.0421 | 6.9126 | 6.7874 | 6.6632 | 6.5905 | 6.5211 | 6.22 | 5.9884 | 5.8137 | 6.7832 | 6.7526 | 6.72 | 6.6874 | 6.6032 | 6.4695 | 6.3368 | 6.2684 | 6.2011 | 5.9053 | 5.6684 | 5.4811 | 6.8842 | 6.8516 | 6.8168 | 6.7653 | 6.6232 | 6.4853 | 6.3484 | 6.2726 | 6.2 | 5.8789 | 5.6295 | 5.4358
|  | KYLE | EE |  |  |  |  | 7.2337 | 7.2 | 7.1547 | 7.1074 | 7.0421 | 6.9726 | 6.8495 | 6.7305 | 6.62 | 6.3084 | 6.0232 | 5.86 | 6.8011 | 6.7747 | 6.7484 | 6.7189 | 6.6821 | 6.6442 | 6.5568 | 6.4337 | 6.3168 | 6.0305 | 5.7684 | 5.6032 | 6.9042 | 6.8768 | 6.8463 | 6.8158 | 6.7684 | 6.6958 | 6.5611 | 6.4305 | 6.3084 | 5.9842 | 5.6832 | 5.5053
|  | KYLE | HT |  |  |  |  | 7.2074 | 7.1526 | 7.0968 | 7.0421 | 6.9126 | 6.7874 | 6.6632 | 6.5905 | 6.5211 | 6.22 | 5.9884 | 5.8137 | 6.7832 | 6.7526 | 6.72 | 6.6874 | 6.6032 | 6.4695 | 6.3368 | 6.2684 | 6.2011 | 5.9053 | 5.6684 | 5.4811 | 6.8842 | 6.8516 | 6.8168 | 6.7653 | 6.6232 | 6.4853 | 6.3484 | 6.2726 | 6.2 | 5.8789 | 5.6295 | 5.4358
|  | KYLE | HE |  |  |  |  | 7.2579 | 7.2411 | 7.2211 | 7.2011 | 7.1526 | 7.1042 | 7.0253 | 6.9474 | 6.8747 | 6.6284 | 6.4779 | 6.2737 | 6.8253 | 6.8084 | 6.7895 | 6.7695 | 6.7358 | 6.7084 | 6.68 | 6.6516 | 6.5926 | 6.3568 | 6.2253 | 6.0305 | 6.8842 | 6.8516 | 6.8168 | 6.7653 | 6.6232 | 6.4853 | 6.3484 | 6.2726 | 6.2 | 5.8789 | 5.6295 | 5.4358
|  | KYLE | CF |  |  |  |  | 7.2747 | 7.2653 | 7.2537 | 7.2442 | 7.2242 | 7.2074 | 7.1895 | 7.1526 | 7.1137 | 6.9421 | 6.8358 | 6.7358 | 6.8421 | 6.8326 | 6.8221 | 6.8126 | 6.7979 | 6.7842 | 6.7705 | 6.7568 | 6.7453 | 6.6484 | 6.5516 | 6.4537 | 6.9474 | 6.9379 | 6.9253 | 6.9158 | 6.8968 | 6.88 | 6.8621 | 6.8453 | 6.8295 | 6.6558 | 6.5442 | 6.4358
| LAIRG | LAIRG | MINIMUM HEADROOM | NC 58798 07111 | YES | YES | 0 | 1.1179 | 1.0421 | 2.4653 | 2.3895 | 1.9463 | 1.3926 | 1.3568 | 0.80842 | 0.02421 | -6.3474 | -14.0716 | -18.1526 | 0.86737 | 0.79158 | 2.2137 | 2.1379 | 1.8168 | 1.3737 | 1.2453 | 0.75158 | -0.042105 | -5.7316 | -12.8737 | -17.3084 | 0.91579 | 0.83789 | 2.2579 | 2.1768 | 1.7368 | 1.1811 | 1.1442 | 0.59263 | -0.001053 | -7.0568 | -15.3 | -19.9411
|  | LAIRG | EE |  |  |  |  | 1.1505 | 1.0716 | 2.4926 | 2.4126 | 1.9463 | 1.3926 | 1.3568 | 0.81368 | 0.23158 | -6.3474 | -14.0716 | -18.1526 | 0.90316 | 0.82947 | 2.2526 | 2.1779 | 1.8168 | 1.3737 | 1.3347 | 0.87263 | 0.36842 | -5.7316 | -12.8737 | -17.3084 | 0.94947 | 0.86947 | 2.2874 | 2.2053 | 1.7368 | 1.1811 | 1.1442 | 0.59263 | -0.001053 | -7.0568 | -15.3 | -19.9411
|  | LAIRG | HT |  |  |  |  | 1.1179 | 1.0421 | 2.4653 | 2.3895 | 1.9916 | 1.5337 | 1.4032 | 0.92737 | 0.29158 | -5.6547 | -12.8695 | -16.2674 | 0.86737 | 0.79158 | 2.2137 | 2.1379 | 1.8232 | 1.4326 | 1.2747 | 0.89684 | 0.31684 | -5.4316 | -12.5947 | -16.3863 | 0.91579 | 0.83789 | 2.2579 | 2.1768 | 1.7779 | 1.3032 | 1.1484 | 0.67474 | 0.0021053 | -6.48 | -14.3495 | -18.2653
|  | LAIRG | HE |  |  |  |  | 1.1821 | 1.1526 | 2.6179 | 2.5768 | 2.0811 | 1.5505 | 1.36 | 0.80842 | 0.02421 | -2.6611 | -8.0053 | -12.6211 | 0.93579 | 0.90632 | 2.3705 | 2.3284 | 1.9505 | 1.4821 | 1.2453 | 0.75158 | -0.042105 | -2.8074 | -7.9811 | -12.6874 | 0.91579 | 0.83789 | 2.2579 | 2.1768 | 1.7779 | 1.3032 | 1.1484 | 0.67474 | 0.0021053 | -6.48 | -14.3495 | -18.2653
|  | LAIRG | CF |  |  |  |  | 1.2074 | 1.1926 | 2.6768 | 2.6611 | 2.4768 | 2.3105 | 2.2347 | 1.9021 | 1.5379 | -1.2179 | -3.8832 | -6.8305 | 0.96421 | 0.95053 | 2.4347 | 2.4211 | 2.2811 | 2.1526 | 2.0589 | 1.7032 | 1.2863 | -1.2737 | -4.0095 | -7.1842 | 1.0084 | 0.99263 | 2.4768 | 2.4611 | 2.2768 | 2.1095 | 2.0274 | 1.6484 | 1.2179 | -1.7516 | -4.6853 | -8.0211
| MYBSTER 1 | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | YES | 0.075 | 3.1008 | 3.005 | 2.9124 | 2.8197 | 2.3882 | 1.8808 | 1.2955 | 0.78184 | 0.14921 | -4.4413 | -9.675 | -13.5476 | 2.945 | 2.8492 | 2.7545 | 2.6629 | 2.2955 | 1.9103 | 1.4134 | 0.97553 | 0.25132 | -3.9813 | -9.1034 | -13.3687 | 2.9661 | 2.8639 | 2.765 | 2.6692 | 2.2261 | 1.7282 | 1.1303 | 0.605 | -0.013947 | -5.0203 | -10.7234 | -15.1287
|  | LATHERON | EE |  |  |  |  | 3.1503 | 3.0597 | 2.9692 | 2.8787 | 2.4239 | 1.8808 | 1.2955 | 0.78184 | 0.25132 | -4.4413 | -9.675 | -13.5476 | 3.0008 | 2.9145 | 2.8282 | 2.7408 | 2.3629 | 1.9103 | 1.4134 | 0.97553 | 0.52079 | -3.9813 | -9.0982 | -13.3687 | 3.0197 | 2.925 | 2.8303 | 2.7355 | 2.2766 | 1.7282 | 1.1303 | 0.605 | 0.061842 | -5.0203 | -10.7234 | -15.1287
|  | LATHERON | HT |  |  |  |  | 3.1008 | 3.005 | 2.9124 | 2.8197 | 2.3882 | 1.9597 | 1.5166 | 1.0429 | 0.24289 | -3.9908 | -8.6855 | -11.9171 | 2.945 | 2.8492 | 2.7545 | 2.6629 | 2.2955 | 1.9208 | 1.5324 | 1.1324 | 0.36921 | -3.9413 | -9.1034 | -12.7045 | 2.9661 | 2.8639 | 2.765 | 2.6692 | 2.2261 | 1.7861 | 1.3292 | 0.84816 | -0.013947 | -4.6939 | -10.0529 | -13.7718
|  | LATHERON | HE |  |  |  |  | 3.2208 | 3.1787 | 3.1334 | 3.0882 | 2.565 | 2.0145 | 1.4545 | 0.91763 | 0.14921 | -3.1224 | -7.1224 | -11.4708 | 3.0776 | 3.0334 | 2.9882 | 2.9429 | 2.4987 | 1.9976 | 1.4839 | 0.99868 | 0.25132 | -2.8971 | -6.9961 | -11.4624 | 2.9661 | 2.8639 | 2.765 | 2.6692 | 2.2261 | 1.7861 | 1.3292 | 0.84816 | -0.013947 | -4.6939 | -10.0529 | -13.7718
|  | LATHERON | CF |  |  |  |  | 3.2597 | 3.2334 | 3.2082 | 3.1808 | 2.9966 | 2.8334 | 2.5503 | 2.2208 | 1.8545 | 0.18079 | -2.3371 | -5.0897 | 3.1208 | 3.0934 | 3.0671 | 3.0397 | 2.8871 | 2.7492 | 2.4766 | 2.1461 | 1.7608 | 0.058684 | -2.5392 | -5.5308 | 3.1387 | 3.1103 | 3.0839 | 3.0534 | 2.8671 | 2.7018 | 2.3955 | 2.0313 | 1.6176 | -0.22553 | -3.0171 | -6.1455
| FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | YES | 0.17 | 14.4168 | 14.0632 | 13.6674 | 13.2379 | 12.2189 | 11.1053 | 9.8716 | 8.7463 | 7.4505 | -2.2147 | -11.9379 | -19.2916 | 13.3321 | 12.9405 | 12.51 | 12.0374 | 11.1142 | 10.1637 | 9.1395 | 7.9932 | 6.65 | -1.6416 | -11.3647 | -19.1521 | 13.4945 | 13.0966 | 12.6576 | 12.1766 | 11.1018 | 9.9682 | 8.6945 | 7.5282 | 6.0397 | -3.8371 | -14.495 | -22.9108
|  | LAURENCEKIRK | EE |  |  |  |  | 14.5768 | 14.2505 | 13.8726 | 13.4558 | 12.3379 | 11.1053 | 9.8716 | 8.7463 | 7.5632 | -2.2147 | -11.9379 | -19.2916 | 13.5153 | 13.1574 | 12.75 | 12.2995 | 11.3121 | 10.2216 | 9.1395 | 8.1384 | 7.0753 | -1.5711 | -11.1279 | -19.1521 | 13.6808 | 13.3082 | 12.8871 | 12.4229 | 11.2503 | 9.9682 | 8.6945 | 7.5282 | 6.2945 | -3.8371 | -14.495 | -22.9108
|  | LAURENCEKIRK | HT |  |  |  |  | 14.4168 | 14.0632 | 13.6674 | 13.2379 | 12.2189 | 11.1884 | 10.1316 | 8.8642 | 7.4505 | -1.52 | -10.4853 | -16.5821 | 13.3321 | 12.9405 | 12.51 | 12.0374 | 11.1142 | 10.1637 | 9.1753 | 7.9932 | 6.65 | -1.6416 | -11.3647 | -18.1932 | 13.4945 | 13.0966 | 12.6576 | 12.1766 | 11.1018 | 10.0124 | 8.8913 | 7.5471 | 6.0397 | -3.4771 | -13.6708 | -20.6866
|  | LAURENCEKIRK | HE |  |  |  |  | 14.6958 | 14.5158 | 14.2516 | 13.9368 | 12.8211 | 11.8642 | 10.8747 | 9.9442 | 9.0042 | 1.5684 | -5.9295 | -14.0968 | 13.6426 | 13.4395 | 13.1321 | 12.7795 | 11.8142 | 10.9584 | 10.0616 | 9.2363 | 8.3995 | 1.4289 | -6.2258 | -14.5658 | 13.4945 | 13.0966 | 12.6576 | 12.1766 | 11.1018 | 10.0124 | 8.8913 | 7.5471 | 6.0397 | -3.4771 | -13.6708 | -20.6866
|  | LAURENCEKIRK | CF |  |  |  |  | 14.7568 | 14.7168 | 14.6021 | 14.4632 | 14.0232 | 13.6179 | 13.2084 | 12.8232 | 12.2074 | 9.0389 | 4.2979 | -0.93158 | 13.7058 | 13.6679 | 13.5405 | 13.3753 | 12.99 | 12.6289 | 12.2511 | 11.8868 | 11.2353 | 8.0289 | 3.1626 | -2.4784 | 13.8724 | 13.8324 | 13.6976 | 13.5324 | 13.0724 | 12.6461 | 12.2134 | 11.8008 | 11.1092 | 7.6187 | 2.3534 | -3.5739
| STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | 0 | 6.4611 | 6.4179 | 6.3747 | 6.3316 | 6.2063 | 6.0663 | 5.9084 | 5.7695 | 5.5821 | 3.8189 | 1.74 | 0.14842 | 6.3432 | 6.2674 | 6.1926 | 6.1189 | 5.9811 | 5.8463 | 5.7116 | 5.5642 | 5.3379 | 3.4821 | 1.1716 | -0.48737 | 6.3032 | 6.2263 | 6.1516 | 6.0768 | 5.9126 | 5.7526 | 5.5905 | 5.4126 | 5.1558 | 3.2095 | 0.85789 | -0.84
|  | LAXAY | EE |  |  |  |  | 6.48 | 6.4411 | 6.4 | 6.3589 | 6.2242 | 6.0663 | 5.9084 | 5.7695 | 5.6284 | 3.8842 | 1.8537 | 0.14842 | 6.3863 | 6.3263 | 6.2632 | 6.1989 | 6.0589 | 5.9032 | 5.7484 | 5.6095 | 5.4695 | 3.7074 | 1.6432 | -0.25368 | 6.3453 | 6.2821 | 6.2179 | 6.1516 | 5.9811 | 5.7863 | 5.5905 | 5.4168 | 5.2421 | 3.3158 | 1.0895 | -0.84
|  | LAXAY | HT |  |  |  |  | 6.4611 | 6.4179 | 6.3747 | 6.3316 | 6.2063 | 6.0842 | 5.9611 | 5.82 | 5.5821 | 3.8189 | 1.74 | 0.28211 | 6.3432 | 6.2674 | 6.1926 | 6.1189 | 5.9811 | 5.8463 | 5.7116 | 5.5642 | 5.3379 | 3.4821 | 1.1716 | -0.48737 | 6.3032 | 6.2263 | 6.1516 | 6.0768 | 5.9126 | 5.7526 | 5.5916 | 5.4126 | 5.1558 | 3.2095 | 0.85789 | -0.82632
|  | LAXAY | HE |  |  |  |  | 6.5105 | 6.4874 | 6.4632 | 6.4368 | 6.3 | 6.1821 | 6.0663 | 5.9242 | 5.6179 | 4.3526 | 2.7358 | 0.98421 | 6.4168 | 6.3947 | 6.3705 | 6.3432 | 6.2137 | 6.0453 | 5.8484 | 5.6663 | 5.3558 | 4.0895 | 2.3874 | 0.54105 | 6.3032 | 6.2263 | 6.1516 | 6.0768 | 5.9126 | 5.7526 | 5.5916 | 5.4126 | 5.1558 | 3.2095 | 0.85789 | -0.82632
|  | LAXAY | CF |  |  |  |  | 6.5305 | 6.5168 | 6.5053 | 6.4905 | 6.4368 | 6.3895 | 6.3411 | 6.2968 | 6.24 | 5.5463 | 4.5158 | 3.3316 | 6.4368 | 6.4242 | 6.4126 | 6.3989 | 6.3663 | 6.3147 | 6.2421 | 6.0937 | 5.9137 | 5.1905 | 4.0989 | 2.7916 | 6.4411 | 6.4179 | 6.3968 | 6.3747 | 6.3042 | 6.2432 | 6.1621 | 6.0095 | 5.8274 | 5.0642 | 3.9211 | 2.5874
| COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | YES | 0 | -0.65474 | -0.78947 | -0.92105 | -1.0484 | -1.4232 | -1.8147 | -2.2947 | -2.7179 | -3.1432 | -6.9379 | -11.28 | -14.5326 | -0.084211 | -0.22316 | -0.3579 | -0.49053 | -0.81579 | -1.1368 | -1.5147 | -1.88 | -2.3011 | -5.8432 | -10.0905 | -13.6137 | -0.69895 | -0.84 | -0.97789 | -1.1126 | -1.4937 | -1.8968 | -2.3937 | -2.8305 | -3.2695 | -7.2789 | -12.0074 | -15.7021
|  | LEOCH | EE |  |  |  |  | -0.57684 | -0.69474 | -0.81158 | -0.92737 | -1.3389 | -1.8147 | -2.2947 | -2.7179 | -3.1432 | -6.9379 | -11.28 | -14.5326 | 0 | -0.11895 | -0.23579 | -0.35158 | -0.70316 | -1.1021 | -1.5147 | -1.88 | -2.2463 | -5.8432 | -10.0905 | -13.6137 | -0.61684 | -0.73895 | -0.86105 | -0.98105 | -1.4053 | -1.8968 | -2.3937 | -2.8305 | -3.2695 | -7.2789 | -12.0074 | -15.7021
|  | LEOCH | HT |  |  |  |  | -0.65474 | -0.78947 | -0.92105 | -1.0484 | -1.4232 | -1.7916 | -2.1621 | -2.5874 | -3.0432 | -6.5811 | -10.5432 | -13.2337 | -0.084211 | -0.22316 | -0.3579 | -0.49053 | -0.81579 | -1.1368 | -1.4589 | -1.8232 | -2.2221 | -5.7863 | -10.0716 | -13.0695 | -0.69895 | -0.84 | -0.97789 | -1.1126 | -1.4937 | -1.8747 | -2.2568 | -2.6968 | -3.1695 | -7.0126 | -11.5063 | -14.5968
|  | LEOCH | HE |  |  |  |  | -0.46947 | -0.53368 | -0.59895 | -0.66316 | -1.0747 | -1.5095 | -1.9832 | -2.4347 | -3.0853 | -5.8663 | -9.1895 | -12.7863 | 0.11474 | 0.048421 | -0.018947 | -0.086316 | -0.42842 | -0.81895 | -1.2547 | -1.6663 | -2.3011 | -5.0168 | -8.3926 | -12.0547 | -0.69895 | -0.84 | -0.97789 | -1.1126 | -1.4937 | -1.8747 | -2.2568 | -2.6968 | -3.1695 | -7.0126 | -11.5063 | -14.5968
|  | LEOCH | CF |  |  |  |  | -0.41158 | -0.44842 | -0.48947 | -0.52842 | -0.69579 | -0.8421 | -1.0253 | -1.3084 | -1.6221 | -3.0463 | -5.1474 | -7.4411 | 0.17579 | 0.13684 | 0.095789 | 0.054737 | -0.087368 | -0.21474 | -0.3821 | -0.66737 | -1 | -2.4368 | -4.5853 | -7.0411 | -0.44526 | -0.48421 | -0.52632 | -0.56632 | -0.73895 | -0.89053 | -1.0821 | -1.3832 | -1.7284 | -3.2926 | -5.62 | -8.2168
| NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 0 | 4.1968 | 4.1074 | 4.0168 | 3.9126 | 2.9926 | 1.8768 | 0.74 | -0.35158 | -1.9253 | -11.3 | -20.4168 | -28.9105 | 4.0789 | 3.9958 | 3.9147 | 3.8305 | 3.0579 | 2.04 | 0.99368 | 0.0021053 | -1.6 | -10.261 | -20.7568 | -28.9263 | 4.1221 | 4.0232 | 3.9284 | 3.8305 | 2.9495 | 1.8874 | 0.78947 | -0.15684 | -1.8495 | -12.4568 | -22.6979 | -32.3
|  | LETHEN | EE |  |  |  |  | 4.2295 | 4.1263 | 4.0211 | 3.9126 | 3.0263 | 1.9642 | 0.86737 | -0.074737 | -1.4442 | -11.3 | -20.4168 | -28.9105 | 4.1168 | 4.0295 | 3.9432 | 3.8484 | 3.1663 | 2.3495 | 1.4737 | 0.71368 | -0.54737 | -10.261 | -19.6874 | -28.9263 | 4.1632 | 4.0516 | 3.9411 | 3.8305 | 2.9495 | 1.8874 | 0.78947 | -0.15684 | -1.6011 | -12.4568 | -22.6116 | -32.3
|  | LETHEN | HT |  |  |  |  | 4.1968 | 4.1074 | 4.0168 | 3.9242 | 3.1832 | 2.4453 | 1.5758 | 0.43158 | -1.4505 | -10.3495 | -19.8168 | -26.7726 | 4.0789 | 3.9958 | 3.9147 | 3.8305 | 3.2516 | 2.6747 | 1.9379 | 0.93158 | -1.0011 | -10.2137 | -20.7568 | -28.6011 | 4.1221 | 4.0232 | 3.9284 | 3.8305 | 3.0979 | 2.36 | 1.4642 | 0.26632 | -1.8495 | -11.8021 | -22.6979 | -30.7274
|  | LETHEN | HE |  |  |  |  | 4.2632 | 4.2347 | 4.2011 | 4.1621 | 2.9926 | 1.8768 | 0.74 | -0.35158 | -1.9253 | -8.7705 | -16.0916 | -25.499 | 4.1558 | 4.1305 | 4.0979 | 4.06 | 3.0579 | 2.04 | 0.99368 | 0.0021053 | -1.6 | -8.2958 | -16.0821 | -25.7063 | 4.1221 | 4.0232 | 3.9284 | 3.8305 | 3.0979 | 2.36 | 1.4642 | 0.26632 | -1.8495 | -11.8021 | -22.6979 | -30.7274
|  | LETHEN | CF |  |  |  |  | 4.28 | 4.2621 | 4.2432 | 4.2263 | 3.8811 | 3.5705 | 2.8937 | 2.48 | 1.7389 | -1.7895 | -6.4684 | -12.5042 | 4.1716 | 4.1568 | 4.1411 | 4.1274 | 3.8726 | 3.6316 | 2.9274 | 2.4042 | 1.5568 | -2.0337 | -7.0263 | -13.5484 | 4.2179 | 4.2 | 4.18 | 4.1632 | 3.8179 | 3.5053 | 2.7411 | 2.2179 | 1.3263 | -2.5884 | -7.8789 | -14.7274
| GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | NO | 0 | 0.098947 | 0.096842 | 0.094737 | 0.092632 | 0.089474 | 0.088421 | 0.086316 | 0.083158 | 0.082105 | 0.071579 | 0.064211 | 0.054737 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.090526 | 0.089474 | 0.086316 | 0.08421 | 0.082105 | 0.072632 | 0.064211 | 0.055789 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.089474 | 0.088421 | 0.086316 | 0.083158 | 0.081053 | 0.070526 | 0.063158 | 0.053684
|  | LETTEREWE | EE |  |  |  |  | 0.098947 | 0.096842 | 0.094737 | 0.092632 | 0.089474 | 0.088421 | 0.086316 | 0.083158 | 0.082105 | 0.071579 | 0.064211 | 0.054737 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.090526 | 0.089474 | 0.086316 | 0.08421 | 0.082105 | 0.072632 | 0.064211 | 0.055789 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.089474 | 0.088421 | 0.086316 | 0.083158 | 0.081053 | 0.070526 | 0.063158 | 0.053684
|  | LETTEREWE | HT |  |  |  |  | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.091579 | 0.088421 | 0.085263 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.091579 | 0.087368 | 0.08421 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.094737 | 0.090526 | 0.087368 | 0.083158
|  | LETTEREWE | HE |  |  |  |  | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.092632 | 0.089474 | 0.086316 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.086316 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.094737 | 0.090526 | 0.087368 | 0.083158
|  | LETTEREWE | CF |  |  |  |  | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.096842 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842
| ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 0 | 4.7789 | 4.5968 | 4.4316 | 4.3442 | 4.1632 | 3.9842 | 3.8063 | 3.6126 | 3.4179 | 2.5284 | 1.4526 | 0.55895 | 4.6484 | 4.3968 | 4.2137 | 4.1211 | 3.9589 | 3.8011 | 3.64 | 3.4663 | 3.2926 | 2.6189 | 1.6537 | 0.72737 | 4.6632 | 4.4158 | 4.2347 | 4.1421 | 3.9526 | 3.7674 | 3.5842 | 3.3811 | 3.1789 | 2.3126 | 1.1842 | 0.19684
|  | LHANBRYDE | EE |  |  |  |  | 4.82 | 4.6884 | 4.5463 | 4.4411 | 4.2368 | 4.0179 | 3.8063 | 3.6189 | 3.4316 | 2.5284 | 1.4526 | 0.55895 | 4.7168 | 4.5 | 4.3442 | 4.2305 | 4.0516 | 3.8579 | 3.6758 | 3.5105 | 3.3484 | 2.6189 | 1.6537 | 0.72737 | 4.7295 | 4.5158 | 4.36 | 4.2463 | 4.0326 | 3.8042 | 3.5874 | 3.3926 | 3.1979 | 2.3126 | 1.1842 | 0.19684
|  | LHANBRYDE | HT |  |  |  |  | 4.7789 | 4.5968 | 4.4316 | 4.3442 | 4.1632 | 3.9842 | 3.8074 | 3.6126 | 3.4179 | 2.7274 | 1.8284 | 1.0989 | 4.6484 | 4.3968 | 4.2137 | 4.1211 | 3.9589 | 3.8011 | 3.64 | 3.4663 | 3.2926 | 2.7189 | 1.8 | 1.0084 | 4.6632 | 4.4158 | 4.2347 | 4.1421 | 3.9526 | 3.7674 | 3.5842 | 3.3811 | 3.1789 | 2.5095 | 1.5295 | 0.71684
|  | LHANBRYDE | HE |  |  |  |  | 4.8705 | 4.7811 | 4.6653 | 4.5874 | 4.3979 | 4.2442 | 4.0905 | 3.9421 | 3.7947 | 3.1389 | 2.1863 | 1.1316 | 4.7968 | 4.5989 | 4.4674 | 4.3811 | 4.2211 | 4.0884 | 3.9568 | 3.8284 | 3.7021 | 3.1432 | 2.1947 | 1.1632 | 4.6632 | 4.4158 | 4.2347 | 4.1421 | 3.9526 | 3.7674 | 3.5842 | 3.3811 | 3.1789 | 2.5095 | 1.5295 | 0.71684
|  | LHANBRYDE | CF |  |  |  |  | 4.9253 | 4.8842 | 4.8537 | 4.8305 | 4.7568 | 4.6895 | 4.6242 | 4.5663 | 4.5179 | 4.1842 | 3.6232 | 2.9926 | 4.9126 | 4.8232 | 4.7642 | 4.7242 | 4.6505 | 4.5758 | 4.5021 | 4.4389 | 4.3821 | 4.0789 | 3.5389 | 2.8853 | 4.9221 | 4.8337 | 4.7758 | 4.7368 | 4.6495 | 4.5642 | 4.4821 | 4.4095 | 4.3474 | 3.9979 | 3.3947 | 2.7
| FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | NO | 0 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211
|  | LIDDESDALE | EE |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211
|  | LIDDESDALE | HT |  |  |  |  | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211
|  | LIDDESDALE | HE |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211
|  | LIDDESDALE | CF |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316
| KEITH 1 | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 0 | 1.0121 | 0.93316 | 0.84053 | 0.74684 | 0.17526 | -0.54368 | -1.2637 | -1.8858 | -2.8816 | -9.1911 | -15.3195 | -20.5468 | 1.0016 | 0.92684 | 0.83947 | 0.74789 | 0.27737 | -0.3321 | -0.93842 | -1.5563 | -2.4774 | -8.2111 | -14.409 | -20.0332 | 1.0921 | 1.0079 | 0.90895 | 0.80579 | 0.24579 | -0.47316 | -1.2142 | -1.8668 | -2.7711 | -9.0047 | -16.73 | -22.6542
|  | LIMEHILLOCKS | EE |  |  |  |  | 1.0468 | 0.96474 | 0.87526 | 0.78158 | 0.17526 | -0.54368 | -1.2637 | -1.8858 | -2.6395 | -8.2911 | -15.3195 | -20.5468 | 1.0374 | 0.96158 | 0.87842 | 0.79316 | 0.27737 | -0.3321 | -0.93842 | -1.4616 | -2.1184 | -7.4911 | -14.409 | -20.0332 | 1.1321 | 1.0458 | 0.95105 | 0.85105 | 0.24579 | -0.47316 | -1.2142 | -1.8668 | -2.6553 | -9.0047 | -16.73 | -22.6542
|  | LIMEHILLOCKS | HT |  |  |  |  | 1.0121 | 0.93316 | 0.84053 | 0.74684 | 0.23737 | -0.26789 | -0.77211 | -1.4489 | -2.6426 | -7.9395 | -14.2426 | -18.4995 | 1.0016 | 0.92684 | 0.83947 | 0.74789 | 0.31211 | -0.11842 | -0.54895 | -1.1342 | -2.2437 | -7.5553 | -14.349 | -19.1637 | 1.0921 | 1.0079 | 0.90895 | 0.80579 | 0.29421 | -0.2121 | -0.71632 | -1.4174 | -2.7711 | -8.7353 | -15.9237 | -20.8616
|  | LIMEHILLOCKS | HE |  |  |  |  | 1.0963 | 1.0616 | 1.0142 | 0.96474 | 0.25737 | -0.45842 | -1.1868 | -1.8847 | -2.8816 | -9.1911 | -14.5774 | -20.451 | 1.0858 | 1.0532 | 1.0079 | 0.95737 | 0.34789 | -0.28684 | -0.93632 | -1.5563 | -2.4774 | -8.2111 | -13.6826 | -19.6595 | 1.0921 | 1.0079 | 0.90895 | 0.80579 | 0.29421 | -0.2121 | -0.71632 | -1.4174 | -2.7711 | -8.7353 | -15.9237 | -20.8616
|  | LIMEHILLOCKS | CF |  |  |  |  | 1.1226 | 1.1016 | 1.0784 | 1.0574 | 0.81842 | 0.60579 | 0.20895 | -0.2121 | -0.67842 | -2.8479 | -6.2342 | -9.9563 | 1.1132 | 1.0932 | 1.0711 | 1.0489 | 0.85 | 0.66789 | 0.30053 | -0.097368 | -0.54895 | -2.6068 | -6.0689 | -10.029 | 1.2163 | 1.1932 | 1.1689 | 1.1447 | 0.90895 | 0.69421 | 0.25316 | -0.22789 | -0.77632 | -3.2121 | -6.9479 | -11.189
| ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 0 | 10.0785 | 10.0743 | 10.0691 | 10.0638 | 10.0575 | 10.0522 | 10.0469 | 10.0417 | 10.0375 | 10.0217 | 10.0101 | 10.0027 | 9.7227 | 9.7133 | 9.7038 | 9.6943 | 9.6848 | 9.6743 | 9.6659 | 9.6575 | 9.6501 | 9.6164 | 9.5891 | 9.5648 | 10.0006 | 9.9901 | 9.9817 | 9.9722 | 9.9627 | 9.9522 | 9.9438 | 9.9354 | 9.928 | 9.8943 | 9.8669 | 9.8427
|  | LOCH CARNAN | EE |  |  |  |  | 10.0817 | 10.0775 | 10.0722 | 10.068 | 10.0638 | 10.0596 | 10.0543 | 10.0512 | 10.0469 | 16.1606 | 16.1522 | 16.1469 | 9.7301 | 9.7217 | 9.7133 | 9.7048 | 9.6985 | 9.6912 | 9.6827 | 9.6775 | 9.6701 | 17.8069 | 17.7985 | 17.7933 | 10.0069 | 9.9996 | 9.9901 | 9.9827 | 9.9754 | 9.9691 | 9.9606 | 9.9554 | 9.948 | 17.2543 | 17.2459 | 17.2406
|  | LOCH CARNAN | HT |  |  |  |  | 10.0785 | 10.0743 | 10.0691 | 10.0638 | 10.0575 | 10.0522 | 10.0469 | 10.0417 | 10.0375 | 10.0217 | 10.0101 | 10.0027 | 9.7227 | 9.7133 | 9.7038 | 9.6943 | 9.6848 | 9.6743 | 9.6659 | 9.6575 | 9.6501 | 9.6164 | 9.5891 | 9.5648 | 10.0006 | 9.9901 | 9.9817 | 9.9722 | 9.9627 | 9.9522 | 9.9438 | 9.9354 | 9.928 | 9.8943 | 9.8669 | 9.8427
|  | LOCH CARNAN | HE |  |  |  |  | 10.0859 | 10.0827 | 10.0796 | 10.0754 | 10.0722 | 10.0691 | 10.0659 | 10.0627 | 10.0596 | 10.0501 | 10.0459 | 10.0438 | 9.7385 | 9.7333 | 9.728 | 9.7227 | 9.7175 | 9.7122 | 9.708 | 9.7038 | 9.6985 | 9.6827 | 9.6722 | 9.6648 | 10.0006 | 9.9901 | 9.9817 | 9.9722 | 9.9627 | 9.9522 | 9.9438 | 9.9354 | 9.928 | 9.8943 | 9.8669 | 9.8427
|  | LOCH CARNAN | CF |  |  |  |  | 10.088 | 10.0869 | 10.0848 | 10.0838 | 10.0817 | 10.0796 | 10.0785 | 10.0764 | 10.0754 | 10.068 | 10.0638 | 10.0617 | 9.7438 | 9.7406 | 9.7375 | 9.7343 | 9.7312 | 9.728 | 9.7259 | 9.7217 | 9.7196 | 9.7059 | 9.6964 | 9.6891 | 10.0206 | 10.0175 | 10.0143 | 10.0112 | 10.0091 | 10.0048 | 10.0027 | 9.9985 | 9.9975 | 9.9838 | 9.9743 | 9.9669
| GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | NO | 0 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49579 | 0.49158 | 0.48842 | 0.48526 | 0.47895 | 0.44947 | 0.41368 | 0.38842 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49579 | 0.49158 | 0.49053 | 0.48737 | 0.48105 | 0.45474 | 0.42 | 0.39263 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49579 | 0.49263 | 0.48842 | 0.48632 | 0.48 | 0.44632 | 0.40842 | 0.37895
|  | LOCH GLASCARNOCH | EE |  |  |  |  | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49579 | 0.49263 | 0.48842 | 0.48632 | 0.48105 | 0.44947 | 0.41368 | 0.38842 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49684 | 0.49368 | 0.49158 | 0.48947 | 0.48421 | 0.45474 | 0.42 | 0.39263 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49579 | 0.49263 | 0.48842 | 0.48632 | 0.48 | 0.44632 | 0.40842 | 0.37895
|  | LOCH GLASCARNOCH | HT |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49684 | 0.49474 | 0.49158 | 0.48737 | 0.48211 | 0.45263 | 0.42421 | 0.40316 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49789 | 0.49579 | 0.49263 | 0.48947 | 0.48421 | 0.45579 | 0.42316 | 0.4 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49684 | 0.49474 | 0.49158 | 0.48737 | 0.48105 | 0.44947 | 0.41579 | 0.39158
|  | LOCH GLASCARNOCH | HE |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.49579 | 0.49158 | 0.48842 | 0.48526 | 0.47895 | 0.45789 | 0.43158 | 0.40211 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49579 | 0.49158 | 0.49053 | 0.48737 | 0.48105 | 0.46105 | 0.43368 | 0.40421 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49684 | 0.49474 | 0.49158 | 0.48737 | 0.48105 | 0.44947 | 0.41579 | 0.39158
|  | LOCH GLASCARNOCH | CF |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49684 | 0.49474 | 0.49368 | 0.49158 | 0.48 | 0.46316 | 0.44421 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49789 | 0.49474 | 0.49368 | 0.49158 | 0.48 | 0.46316 | 0.44316 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49684 | 0.49474 | 0.49263 | 0.49053 | 0.47789 | 0.46 | 0.43895
| FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | NO | 0 | 0.95789 | 0.94105 | 0.92316 | 0.90421 | 0.88526 | 0.86737 | 0.84947 | 0.83158 | 0.81474 | 0.73789 | 0.67895 | 0.62421 | 1.0032 | 0.98632 | 0.96737 | 0.94737 | 0.92947 | 0.91158 | 0.89474 | 0.87684 | 0.85895 | 0.78421 | 0.72632 | 0.67158 | 0.95474 | 0.93684 | 0.91789 | 0.89579 | 0.87579 | 0.85684 | 0.83789 | 0.81789 | 0.8 | 0.71789 | 0.65263 | 0.59263
|  | LOCHALINE | EE |  |  |  |  | 0.96211 | 0.94316 | 0.92316 | 0.90421 | 0.88526 | 0.86737 | 0.84947 | 0.83158 | 0.81474 | 0.73789 | 0.67895 | 0.62421 | 1.0053 | 0.98632 | 0.96737 | 0.94737 | 0.92947 | 0.91158 | 0.89474 | 0.87684 | 0.85895 | 0.78421 | 0.72632 | 0.67158 | 0.95895 | 0.93789 | 0.91789 | 0.89579 | 0.87579 | 0.85684 | 0.83789 | 0.81789 | 0.8 | 0.71789 | 0.65263 | 0.59263
|  | LOCHALINE | HT |  |  |  |  | 0.95789 | 0.94105 | 0.92526 | 0.90842 | 0.89158 | 0.87684 | 0.86105 | 0.84632 | 0.83158 | 0.77263 | 0.72316 | 0.67789 | 1.0032 | 0.98842 | 0.97474 | 0.96105 | 0.94526 | 0.93263 | 0.91895 | 0.90421 | 0.89263 | 0.84105 | 0.79684 | 0.75789 | 0.95474 | 0.93684 | 0.92 | 0.90211 | 0.88421 | 0.86842 | 0.85263 | 0.83579 | 0.82105 | 0.75789 | 0.70316 | 0.65263
|  | LOCHALINE | HE |  |  |  |  | 0.98 | 0.97158 | 0.96211 | 0.95053 | 0.94 | 0.93263 | 0.92211 | 0.91368 | 0.90526 | 0.87053 | 0.84421 | 0.82105 | 1.02 | 1.0126 | 1.0032 | 0.99368 | 0.98421 | 0.97579 | 0.96632 | 0.95789 | 0.95053 | 0.91684 | 0.89158 | 0.86947 | 0.95474 | 0.93684 | 0.92 | 0.90211 | 0.88421 | 0.86842 | 0.85263 | 0.83579 | 0.82105 | 0.75789 | 0.70316 | 0.65263
|  | LOCHALINE | CF |  |  |  |  | 0.98947 | 0.98421 | 0.97895 | 0.97474 | 0.96947 | 0.96421 | 0.95895 | 0.95368 | 0.95053 | 0.92842 | 0.91263 | 0.9 | 1.0295 | 1.0253 | 1.0211 | 1.0158 | 1.0126 | 1.0074 | 1.0042 | 1 | 0.99579 | 0.97579 | 0.96316 | 0.95474 | 0.98842 | 0.98316 | 0.97789 | 0.97263 | 0.96737 | 0.96105 | 0.95684 | 0.95158 | 0.94632 | 0.92316 | 0.90632 | 0.89263
| GRUDIE BRIDGE | LOCHCARRON | MINIMUM HEADROOM | NG 91944 41839 | YES | NO | 0 | 2.6147 | 2.5274 | 2.4389 | 2.3474 | 2.2568 | 2.1726 | 2.0221 | 1.8726 | 1.7137 | 1.3337 | 1.0295 | 0.74 | 2.4642 | 2.3863 | 2.3032 | 2.2232 | 2.14 | 2.0221 | 1.8695 | 1.7453 | 1.5758 | 1.1853 | 0.86842 | 0.56632 | 2.5232 | 2.4326 | 2.3368 | 2.2421 | 2.1453 | 2.0505 | 1.8747 | 1.6947 | 1.5021 | 1.0989 | 0.77474 | 0.46842
|  | LOCHCARRON | EE |  |  |  |  | 2.6147 | 2.5274 | 2.4389 | 2.3474 | 2.2568 | 2.1726 | 2.0221 | 1.8726 | 1.7137 | 1.3337 | 1.0295 | 0.74 | 2.4642 | 2.3863 | 2.3032 | 2.2232 | 2.14 | 2.0579 | 1.9 | 1.7453 | 1.5758 | 1.1853 | 0.86842 | 0.56632 | 2.5232 | 2.4326 | 2.3368 | 2.2421 | 2.1453 | 2.0579 | 1.8747 | 1.6947 | 1.5021 | 1.0989 | 0.77474 | 0.46842
|  | LOCHCARRON | HT |  |  |  |  | 2.6295 | 2.5747 | 2.5211 | 2.4663 | 2.3442 | 2.2126 | 2.0737 | 2.0242 | 1.9758 | 1.7484 | 1.5558 | 1.3863 | 2.4663 | 2.4126 | 2.3589 | 2.3042 | 2.1642 | 2.0221 | 1.8695 | 1.8232 | 1.7768 | 1.5579 | 1.3674 | 1.2021 | 2.5347 | 2.4737 | 2.4147 | 2.3537 | 2.2021 | 2.0505 | 1.8895 | 1.8347 | 1.7811 | 1.5274 | 1.3116 | 1.1221
|  | LOCHCARRON | HE |  |  |  |  | 2.6884 | 2.6537 | 2.6179 | 2.58 | 2.5432 | 2.5074 | 2.4211 | 2.3368 | 2.2411 | 2.0442 | 1.9242 | 1.8084 | 2.5358 | 2.5021 | 2.4674 | 2.4316 | 2.3958 | 2.3621 | 2.2653 | 2.1695 | 2.0642 | 1.8674 | 1.7537 | 1.6495 | 2.5347 | 2.4737 | 2.4147 | 2.3537 | 2.2021 | 2.0505 | 1.8895 | 1.8347 | 1.7811 | 1.5274 | 1.3116 | 1.1221
|  | LOCHCARRON | CF |  |  |  |  | 2.7221 | 2.7074 | 2.6926 | 2.6758 | 2.6621 | 2.6463 | 2.6326 | 2.5905 | 2.5474 | 2.4074 | 2.3589 | 2.3232 | 2.5674 | 2.5526 | 2.5379 | 2.5221 | 2.5074 | 2.4905 | 2.4768 | 2.4263 | 2.3716 | 2.2137 | 2.1674 | 2.1326 | 2.6411 | 2.6253 | 2.6074 | 2.5895 | 2.5747 | 2.5568 | 2.5411 | 2.4874 | 2.4305 | 2.2642 | 2.2105 | 2.1705
| TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0 | 1.3316 | 1.3137 | 1.2274 | 1.1832 | 1.1316 | 1.0842 | 1.0347 | 0.96 | 0.86526 | 0.80632 | 0.76 | 0.72105 | 1.1874 | 1.1758 | 1.0874 | 1.0295 | 0.97053 | 0.91684 | 0.86105 | 0.77474 | 0.66632 | 0.60316 | 0.55158 | 0.50842 | 1.1874 | 1.1768 | 1.0947 | 1.0368 | 0.97684 | 0.92316 | 0.86632 | 0.77895 | 0.66947 | 0.60632 | 0.55474 | 0.51158
|  | LOCHDONHEAD | EE |  |  |  |  | 1.34 | 1.3295 | 1.2779 | 1.2442 | 1.1926 | 1.1189 | 1.0853 | 1.0442 | 0.97789 | 0.84 | 0.80526 | 0.77684 | 1.1937 | 1.1853 | 1.1537 | 1.1095 | 1.0421 | 0.95368 | 0.91684 | 0.86947 | 0.79368 | 0.63789 | 0.6 | 0.56842 | 1.1937 | 1.1853 | 1.1474 | 1.1116 | 1.0495 | 0.96 | 0.92211 | 0.87474 | 0.79895 | 0.64105 | 0.60316 | 0.57053
|  | LOCHDONHEAD | HT |  |  |  |  | 1.3316 | 1.3137 | 1.2274 | 1.1832 | 1.1316 | 1.0842 | 1.0347 | 0.96 | 0.86526 | 0.80632 | 0.76 | 0.72105 | 1.1874 | 1.1758 | 1.0874 | 1.0295 | 0.97053 | 0.91684 | 0.86105 | 0.77474 | 0.66632 | 0.60316 | 0.55158 | 0.50842 | 1.1874 | 1.1768 | 1.0947 | 1.0368 | 0.97684 | 0.92316 | 0.86632 | 0.77895 | 0.66947 | 0.60632 | 0.55474 | 0.51158
|  | LOCHDONHEAD | HE |  |  |  |  | 1.3484 | 1.3432 | 1.2884 | 1.2547 | 1.2032 | 1.1263 | 1.0726 | 1.0053 | 0.94842 | 0.92211 | 0.90316 | 0.89053 | 1.2021 | 1.1968 | 1.1621 | 1.1179 | 1.0495 | 0.95895 | 0.89789 | 0.82105 | 0.75579 | 0.72632 | 0.70632 | 0.69263 | 1.1874 | 1.1768 | 1.0947 | 1.0368 | 0.97684 | 0.92316 | 0.86632 | 0.77895 | 0.66947 | 0.60632 | 0.55474 | 0.51158
|  | LOCHDONHEAD | CF |  |  |  |  | 1.3537 | 1.3505 | 1.3474 | 1.3432 | 1.3337 | 1.3168 | 1.2937 | 1.2726 | 1.2242 | 1.1095 | 1.0937 | 1.0821 | 1.2074 | 1.2042 | 1.2011 | 1.1979 | 1.1937 | 1.1905 | 1.1705 | 1.1432 | 1.0768 | 0.94 | 0.92316 | 0.91053 | 1.2074 | 1.2042 | 1.2011 | 1.1979 | 1.1947 | 1.1884 | 1.1632 | 1.1411 | 1.0842 | 0.94632 | 0.92947 | 0.91579
| KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | 0.1 | -0.043158 | -0.094737 | -0.22842 | -0.28316 | -0.49158 | -0.72526 | -0.96421 | -1.1747 | -1.3884 | -3.0168 | -5.2526 | -7.0189 | -0.43474 | -0.46421 | -0.50316 | -0.53474 | -0.63684 | -0.75053 | -0.86842 | -0.96947 | -1.0737 | -2.8516 | -5.1021 | -6.98 | -0.56526 | -0.62737 | -0.75368 | -0.83053 | -1.0768 | -1.3505 | -1.6263 | -1.8726 | -2.1242 | -4.2695 | -6.7568 | -8.7337
|  | LOCHEARNHEAD | EE |  |  |  |  | -0.043158 | -0.094737 | -0.22842 | -0.28316 | -0.49158 | -0.72526 | -0.96421 | -1.1747 | -1.3884 | -3.0168 | -5.2526 | -7.0189 | -0.42526 | -0.45474 | -0.50316 | -0.53474 | -0.63684 | -0.75053 | -0.86842 | -0.96947 | -1.0737 | -2.8516 | -5.1021 | -6.98 | -0.54737 | -0.61579 | -0.75368 | -0.83053 | -1.0768 | -1.3505 | -1.6263 | -1.8726 | -2.1242 | -4.2695 | -6.7568 | -8.7337
|  | LOCHEARNHEAD | HT |  |  |  |  | -0.04 | -0.078947 | -0.11684 | -0.15263 | -0.31789 | -0.47895 | -0.64 | -0.82947 | -1.0221 | -2.5905 | -4.6589 | -6.0853 | -0.43474 | -0.46421 | -0.49368 | -0.52105 | -0.61158 | -0.69895 | -0.78526 | -0.88421 | -0.98421 | -2.7716 | -5.02 | -6.5979 | -0.56526 | -0.62737 | -0.69368 | -0.75895 | -0.96526 | -1.1653 | -1.3737 | -1.6095 | -1.8968 | -3.8937 | -6.2147 | -7.8221
|  | LOCHEARNHEAD | HE |  |  |  |  | -0.008421 | -0.029474 | -0.052632 | -0.073684 | -0.26737 | -0.43368 | -0.59789 | -0.76 | -0.93368 | -2.2189 | -3.9074 | -5.8189 | -0.40316 | -0.41684 | -0.43474 | -0.44947 | -0.54737 | -0.63053 | -0.71263 | -0.79474 | -0.90421 | -2.2821 | -4.06 | -5.9968 | -0.56526 | -0.62737 | -0.69368 | -0.75895 | -0.96526 | -1.1653 | -1.3737 | -1.6095 | -1.8968 | -3.8937 | -6.2147 | -7.8221
|  | LOCHEARNHEAD | CF |  |  |  |  | 0.0084211 | -0.002105 | -0.011579 | -0.021053 | -0.093684 | -0.15895 | -0.22105 | -0.27684 | -0.32 | -0.83684 | -1.8116 | -2.9874 | -0.38947 | -0.39789 | -0.40632 | -0.41263 | -0.45053 | -0.48421 | -0.51684 | -0.54632 | -0.57053 | -0.98316 | -2.1042 | -3.3968 | -0.46947 | -0.48842 | -0.50632 | -0.52737 | -0.61895 | -0.70105 | -0.79368 | -0.94842 | -1.1232 | -1.9032 | -3.0747 | -4.4147
| LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | YES | 0.1 | 23.5859 | 23.488 | 23.3869 | 23.2848 | 23.1648 | 23.0385 | 22.8796 | 22.7196 | 22.5543 | 21.748 | 21.1185 | 20.6027 | 22.0705 | 21.9611 | 21.7958 | 21.6305 | 21.4526 | 21.2747 | 21.0958 | 20.9316 | 20.76 | 19.8832 | 19.1611 | 18.5611 | 22.7055 | 22.5729 | 22.4066 | 22.2445 | 22.0676 | 21.8929 | 21.715 | 21.5518 | 21.3803 | 20.4382 | 19.7129 | 19.1118
|  | LOCHEE | EE |  |  |  |  | 23.6543 | 23.5796 | 23.4996 | 23.4175 | 23.3259 | 23.2343 | 23.1438 | 23.0343 | 22.9196 | 22.2891 | 21.7827 | 21.3996 | 22.1474 | 22.0632 | 21.9737 | 21.8442 | 21.7011 | 21.5663 | 21.4126 | 21.2705 | 21.1421 | 20.4832 | 19.9326 | 19.4884 | 22.7739 | 22.6992 | 22.5855 | 22.4529 | 22.3118 | 22.1771 | 22.0255 | 21.8834 | 21.755 | 21.0539 | 20.4687 | 20.0224
|  | LOCHEE | HT |  |  |  |  | 23.5859 | 23.488 | 23.3869 | 23.2848 | 23.1648 | 23.0385 | 22.8796 | 22.7196 | 22.5543 | 21.748 | 21.1185 | 20.6027 | 22.0705 | 21.9611 | 21.7958 | 21.6305 | 21.4526 | 21.2747 | 21.0958 | 20.9316 | 20.76 | 19.8832 | 19.1611 | 18.5611 | 22.7055 | 22.5729 | 22.4066 | 22.2445 | 22.0676 | 21.8929 | 21.715 | 21.5518 | 21.3803 | 20.4382 | 19.7129 | 19.1118
|  | LOCHEE | HE |  |  |  |  | 23.7091 | 23.6491 | 23.5848 | 23.5154 | 23.4354 | 23.3617 | 23.2901 | 23.2217 | 23.1596 | 22.8869 | 22.6006 | 22.3954 | 22.2105 | 22.1474 | 22.0768 | 22.0021 | 21.9221 | 21.8474 | 21.7674 | 21.6674 | 21.5695 | 21.1168 | 20.8137 | 20.6 | 22.7055 | 22.5729 | 22.4066 | 22.2445 | 22.0676 | 21.8929 | 21.715 | 21.5518 | 21.3803 | 20.4382 | 19.7129 | 19.1118
|  | LOCHEE | CF |  |  |  |  | 23.748 | 23.7112 | 23.6722 | 23.6322 | 23.5891 | 23.5469 | 23.5027 | 23.4596 | 23.4185 | 23.2322 | 23.1291 | 23.0354 | 22.2505 | 22.2137 | 22.1747 | 22.1347 | 22.0937 | 22.0516 | 22.0053 | 21.9589 | 21.9147 | 21.6821 | 21.4379 | 21.2663 | 22.8676 | 22.8308 | 22.7918 | 22.7518 | 22.7087 | 22.6666 | 22.6234 | 22.5803 | 22.5392 | 22.2866 | 22.0445 | 21.8761
| PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 0.165 | 24.8487 | 24.6055 | 24.2908 | 23.9855 | 23.6761 | 23.2339 | 22.8087 | 22.3476 | 21.9182 | 19.4234 | 18.5234 | 17.1497 | 22.2045 | 21.9445 | 21.6003 | 21.2676 | 20.9339 | 20.5371 | 20.1034 | 19.6087 | 19.1971 | 17.435 | 16.6561 | 15.3571 | 23.1655 | 23.0424 | 22.8076 | 22.4634 | 22.1213 | 21.6697 | 21.2266 | 20.6866 | 20.2339 | 18.6866 | 17.1129 | 16.3613
|  | LOCHGILPHEAD | EE |  |  |  |  | 24.9771 | 24.7897 | 24.5455 | 24.2308 | 23.7739 | 23.2339 | 22.8087 | 22.3824 | 21.9655 | 20.3845 | 18.8497 | 18.1403 | 22.3476 | 22.1529 | 21.8929 | 21.5992 | 21.1582 | 20.6266 | 20.235 | 19.8266 | 19.4339 | 17.9929 | 16.6739 | 16.0192 | 23.2255 | 23.1171 | 23.0034 | 22.7466 | 22.2561 | 21.6697 | 21.2276 | 20.7718 | 20.3308 | 18.6866 | 17.1129 | 16.3613
|  | LOCHGILPHEAD | HT |  |  |  |  | 24.8487 | 24.6055 | 24.2908 | 23.9855 | 23.6761 | 23.2813 | 22.8466 | 22.3476 | 21.9182 | 20.6445 | 19.6687 | 19.0266 | 22.2045 | 21.9445 | 21.6003 | 21.2676 | 20.9339 | 20.5371 | 20.1034 | 19.6087 | 19.1971 | 18.0034 | 17.0771 | 16.4266 | 23.1655 | 23.0424 | 22.8076 | 22.4634 | 22.1213 | 21.695 | 21.2266 | 20.6866 | 20.2339 | 18.9045 | 17.8739 | 17.175
|  | LOCHGILPHEAD | HE |  |  |  |  | 25.1066 | 25.0371 | 24.8476 | 24.6497 | 24.2013 | 23.7424 | 23.3529 | 23.0024 | 22.7266 | 19.4234 | 18.5234 | 17.1497 | 22.5434 | 22.4129 | 22.2045 | 21.9887 | 21.5529 | 21.0908 | 20.7108 | 20.3718 | 20.1234 | 17.435 | 16.6561 | 15.3571 | 23.1655 | 23.0424 | 22.8076 | 22.4634 | 22.1213 | 21.695 | 21.2266 | 20.6866 | 20.2339 | 18.9045 | 17.8739 | 17.175
|  | LOCHGILPHEAD | CF |  |  |  |  | 25.1655 | 25.1287 | 25.0897 | 25.0413 | 24.8897 | 24.7287 | 24.5182 | 24.3497 | 24.1687 | 21.2013 | 20.6045 | 19.8718 | 22.6097 | 22.5739 | 22.4982 | 22.415 | 22.2729 | 22.1129 | 21.8992 | 21.7276 | 21.5371 | 19.0655 | 18.5339 | 17.8097 | 23.3782 | 23.3424 | 23.3024 | 23.2645 | 23.1666 | 23.0771 | 22.9866 | 22.8897 | 22.6918 | 19.6687 | 19.0529 | 18.255
| CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | 0 | -0.11158 | -0.13789 | -0.16842 | -0.19789 | -0.22842 | -0.25579 | -0.28421 | -0.31263 | -0.3421 | -0.47579 | -0.58632 | -0.69474 | -0.28 | -0.29368 | -0.31895 | -0.34947 | -0.38 | -0.40947 | -0.44211 | -0.47263 | -0.50421 | -0.64737 | -0.76421 | -0.88421 | 0.30632 | 0.27368 | 0.23789 | 0.20316 | 0.16632 | 0.13263 | 0.096842 | 0.063158 | 0.029474 | -0.12842 | -0.25368 | -0.37895
|  | LOCHGOILHEAD | EE |  |  |  |  | -0.11158 | -0.13789 | -0.16842 | -0.19789 | -0.22842 | -0.25579 | -0.28421 | -0.31263 | -0.3421 | -0.47579 | -0.58632 | -0.69474 | -0.28 | -0.29368 | -0.31895 | -0.34947 | -0.38 | -0.40947 | -0.44211 | -0.47263 | -0.50421 | -0.64737 | -0.76421 | -0.88421 | 0.30632 | 0.27368 | 0.23789 | 0.20316 | 0.16632 | 0.13263 | 0.096842 | 0.063158 | 0.029474 | -0.12842 | -0.25368 | -0.37895
|  | LOCHGOILHEAD | HT |  |  |  |  | -0.10632 | -0.11789 | -0.12947 | -0.14526 | -0.16421 | -0.18421 | -0.2 | -0.21684 | -0.23368 | -0.30526 | -0.37053 | -0.43053 | -0.28 | -0.28947 | -0.3 | -0.30947 | -0.32105 | -0.33579 | -0.34947 | -0.36421 | -0.38105 | -0.45474 | -0.52211 | -0.58526 | 0.31474 | 0.29579 | 0.27579 | 0.25684 | 0.23789 | 0.21789 | 0.2 | 0.18211 | 0.16316 | 0.085263 | 0.014737 | -0.051579
|  | LOCHGOILHEAD | HE |  |  |  |  | -0.096842 | -0.10526 | -0.11368 | -0.12211 | -0.13368 | -0.14316 | -0.15579 | -0.16632 | -0.17684 | -0.22316 | -0.26632 | -0.30842 | -0.26947 | -0.27684 | -0.28316 | -0.28947 | -0.29684 | -0.30316 | -0.31053 | -0.32105 | -0.32947 | -0.37684 | -0.42105 | -0.46632 | 0.31474 | 0.29579 | 0.27579 | 0.25684 | 0.23789 | 0.21789 | 0.2 | 0.18211 | 0.16316 | 0.085263 | 0.014737 | -0.051579
|  | LOCHGOILHEAD | CF |  |  |  |  | -0.089474 | -0.092632 | -0.095789 | -0.098947 | -0.10211 | -0.10526 | -0.10947 | -0.11263 | -0.11474 | -0.12842 | -0.13895 | -0.15368 | -0.26421 | -0.26632 | -0.26842 | -0.27158 | -0.27474 | -0.2779 | -0.28105 | -0.28421 | -0.28632 | -0.2979 | -0.30526 | -0.31053 | 0.34316 | 0.33789 | 0.33368 | 0.32842 | 0.32421 | 0.31895 | 0.31368 | 0.30842 | 0.30316 | 0.28 | 0.26421 | 0.24947
| GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | NO | 0 | 1.2274 | 1.1874 | 1.1158 | 1.0442 | 0.96947 | 0.91579 | 0.86211 | 0.81053 | 0.76211 | 0.58316 | 0.41895 | 0.27158 | 1.0811 | 1.0484 | 0.97579 | 0.90316 | 0.82737 | 0.77263 | 0.71579 | 0.66105 | 0.60842 | 0.41579 | 0.23158 | 0.065263 | 1.1547 | 1.0947 | 1.0179 | 0.94105 | 0.86 | 0.80316 | 0.74632 | 0.69158 | 0.64 | 0.44947 | 0.26842 | 0.10632
|  | LOCHINVER | EE |  |  |  |  | 1.2516 | 1.2232 | 1.1779 | 1.1158 | 1.0558 | 1.0126 | 0.97158 | 0.93158 | 0.89474 | 0.74842 | 0.62421 | 0.51789 | 1.1 | 1.0758 | 1.0389 | 0.97579 | 0.91474 | 0.87053 | 0.82947 | 0.78947 | 0.75158 | 0.59474 | 0.45789 | 0.33684 | 1.1958 | 1.1516 | 1.0842 | 1.0179 | 0.95263 | 0.90632 | 0.86211 | 0.82105 | 0.78105 | 0.62632 | 0.49158 | 0.37263
|  | LOCHINVER | HT |  |  |  |  | 1.2274 | 1.1874 | 1.1158 | 1.0442 | 0.96947 | 0.91579 | 0.86211 | 0.81053 | 0.76211 | 0.58316 | 0.41895 | 0.27158 | 1.0811 | 1.0484 | 0.97579 | 0.90316 | 0.82737 | 0.77263 | 0.71579 | 0.66105 | 0.60842 | 0.41579 | 0.23158 | 0.065263 | 1.1547 | 1.0947 | 1.0179 | 0.94105 | 0.86 | 0.80316 | 0.74632 | 0.69158 | 0.64 | 0.44947 | 0.26842 | 0.10632
|  | LOCHINVER | HE |  |  |  |  | 1.2832 | 1.2621 | 1.2389 | 1.2095 | 1.1632 | 1.1337 | 1.1053 | 1.0789 | 1.0589 | 0.97684 | 0.90842 | 0.85263 | 1.1253 | 1.1084 | 1.0905 | 1.0716 | 1.0232 | 0.99368 | 0.96526 | 0.93895 | 0.91895 | 0.83579 | 0.76632 | 0.70421 | 1.1547 | 1.0947 | 1.0179 | 0.94105 | 0.86 | 0.80316 | 0.74632 | 0.69158 | 0.64 | 0.44947 | 0.26842 | 0.10632
|  | LOCHINVER | CF |  |  |  |  | 1.3 | 1.2916 | 1.2821 | 1.2716 | 1.2611 | 1.2495 | 1.2379 | 1.2274 | 1.2158 | 1.1495 | 1.0926 | 1.0505 | 1.1421 | 1.1337 | 1.1242 | 1.1158 | 1.1063 | 1.0968 | 1.0874 | 1.0779 | 1.0684 | 1.0095 | 0.95263 | 0.90947 | 1.2537 | 1.2453 | 1.2358 | 1.2274 | 1.2137 | 1.1958 | 1.1779 | 1.1621 | 1.1453 | 1.0547 | 0.99263 | 0.94526
| LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | YES | 5.98 | 17.6179 | 17.4895 | 17.3558 | 17.2158 | 16.9863 | 16.7432 | 16.5 | 16.2779 | 15.9842 | 14.3442 | 12.7726 | 11.5853 | 15.6463 | 15.5189 | 15.3874 | 15.2484 | 15.0379 | 14.8168 | 14.5968 | 14.3947 | 14.1084 | 12.4768 | 10.9042 | 9.6158 | 16.7547 | 16.6253 | 16.4926 | 16.3516 | 16.12 | 15.8737 | 15.6284 | 15.4042 | 15.0937 | 13.3295 | 11.6158 | 10.2747
|  | LOCHSIDE | EE |  |  |  |  | 17.6179 | 17.4895 | 17.3558 | 17.2158 | 16.9863 | 16.7432 | 16.5 | 16.2779 | 15.9842 | 14.3442 | 12.7726 | 11.5853 | 15.6463 | 15.5189 | 15.3874 | 15.2484 | 15.0379 | 14.8168 | 14.5968 | 14.3947 | 14.1084 | 12.4768 | 10.9042 | 9.6158 | 16.7547 | 16.6253 | 16.4926 | 16.3516 | 16.12 | 15.8737 | 15.6284 | 15.4042 | 15.0937 | 13.3295 | 11.6158 | 10.2747
|  | LOCHSIDE | HT |  |  |  |  | 20.52 | 20.3484 | 20.1695 | 19.8137 | 19.3158 | 18.8242 | 18.4084 | 18.0232 | 17.7368 | 16.5621 | 15.5368 | 14.7442 | 19.4084 | 19.1632 | 18.7516 | 18.3021 | 17.7768 | 17.2589 | 16.8305 | 16.44 | 16.1653 | 15.0137 | 13.9579 | 13.1095 | 20.2716 | 20.1189 | 19.9137 | 19.4474 | 18.9011 | 18.3632 | 17.9137 | 17.5 | 17.2053 | 15.9653 | 14.8537 | 13.9789
|  | LOCHSIDE | HE |  |  |  |  | 19.5768 | 17.6326 | 17.5347 | 17.4295 | 17.1789 | 16.9505 | 16.72 | 16.5 | 16.2274 | 15.1316 | 13.9642 | 12.7726 | 17.9126 | 15.6611 | 15.5632 | 15.4589 | 15.2221 | 15.0021 | 14.7811 | 14.5716 | 14.2968 | 13.2116 | 12.0084 | 10.7737 | 20.2716 | 20.1189 | 19.9137 | 19.4474 | 18.9011 | 18.3632 | 17.9137 | 17.5 | 17.2053 | 15.9653 | 14.8537 | 13.9789
|  | LOCHSIDE | CF |  |  |  |  | 19.6474 | 17.7411 | 17.6853 | 17.6284 | 17.5347 | 17.4442 | 17.2989 | 17.1611 | 17.0105 | 16.3537 | 15.5895 | 14.8084 | 17.9832 | 15.7695 | 15.7137 | 15.6568 | 15.5716 | 15.4874 | 15.3389 | 15.1968 | 15.0389 | 14.3705 | 13.5779 | 12.7358 | 19.1179 | 16.8779 | 16.8211 | 16.7653 | 16.6705 | 16.58 | 16.4242 | 16.2747 | 16.1105 | 15.4032 | 14.5579 | 13.6716
| BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | YES | 0 | 5.0347 | 5.0095 | 4.9853 | 4.9621 | 4.8284 | 4.6547 | 4.4937 | 4.3389 | 4.08 | 2.4937 | 0.78632 | -0.56526 | 4.9568 | 4.9316 | 4.9074 | 4.8832 | 4.7789 | 4.6368 | 4.4895 | 4.3284 | 4.0747 | 2.5221 | 0.88421 | -0.54316 | 5.0032 | 4.9758 | 4.9495 | 4.9242 | 4.7926 | 4.6179 | 4.4705 | 4.3168 | 4.0663 | 2.2684 | 0.44632 | -1.1021
|  | LOGIE PERT | EE |  |  |  |  | 5.0474 | 5.0221 | 4.9979 | 4.9726 | 4.8284 | 4.6547 | 4.4937 | 4.34 | 4.1453 | 2.5537 | 0.78632 | -0.56526 | 4.9705 | 4.9474 | 4.9242 | 4.9 | 4.7789 | 4.6368 | 4.52 | 4.3937 | 4.2221 | 2.6758 | 0.93368 | -0.54316 | 5.0168 | 4.9905 | 4.9653 | 4.9379 | 4.7926 | 4.6179 | 4.4705 | 4.3168 | 4.1158 | 2.3821 | 0.44632 | -1.1021
|  | LOGIE PERT | HT |  |  |  |  | 5.0347 | 5.0095 | 4.9853 | 4.9621 | 4.8579 | 4.7337 | 4.6042 | 4.4337 | 4.1242 | 2.4937 | 1.0526 | -0.064211 | 4.9568 | 4.9316 | 4.9074 | 4.8832 | 4.8105 | 4.7063 | 4.5968 | 4.4495 | 4.1432 | 2.5221 | 0.88421 | -0.37474 | 5.0032 | 4.9758 | 4.9495 | 4.9242 | 4.8347 | 4.7095 | 4.5768 | 4.4021 | 4.0663 | 2.2684 | 0.59684 | -0.69158
|  | LOGIE PERT | HE |  |  |  |  | 5.0632 | 5.0516 | 5.0411 | 5.0284 | 4.8779 | 4.72 | 4.5168 | 4.3389 | 4.08 | 2.9821 | 1.6158 | 0.11895 | 4.9895 | 4.9779 | 4.9663 | 4.9537 | 4.8295 | 4.6905 | 4.4895 | 4.3284 | 4.0747 | 3.0084 | 1.6084 | 0.075789 | 5.0032 | 4.9758 | 4.9495 | 4.9242 | 4.8347 | 4.7095 | 4.5768 | 4.4021 | 4.0663 | 2.2684 | 0.59684 | -0.69158
|  | LOGIE PERT | CF |  |  |  |  | 5.0726 | 5.0653 | 5.06 | 5.0516 | 4.9947 | 4.9442 | 4.8905 | 4.8011 | 4.6768 | 4.1116 | 3.2495 | 2.2863 | 4.9989 | 4.9926 | 4.9853 | 4.9779 | 4.9295 | 4.8863 | 4.8421 | 4.7526 | 4.6211 | 4.0474 | 3.1547 | 2.1137 | 5.0453 | 5.0379 | 5.0305 | 5.0232 | 4.9632 | 4.9116 | 4.8589 | 4.76 | 4.6179 | 3.9884 | 3.0242 | 1.9316
| MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | YES | 5 | 18.59 | 18.1037 | 17.7489 | 17.1058 | 16.1626 | 15.8132 | 15.4679 | 15.1026 | 14.7395 | 12.7668 | 11.1984 | 10.1037 | 18.5142 | 18.2732 | 18.0511 | 17.3353 | 16.3226 | 16.0058 | 15.6942 | 15.3711 | 15.05 | 13.1205 | 11.5247 | 10.3605 | 18.5416 | 18.3142 | 18.0974 | 17.85 | 17.2016 | 16.8521 | 16.5058 | 16.1395 | 15.7763 | 13.6889 | 11.9995 | 10.8016
|  | LONGHAUGH | EE |  |  |  |  | 18.7721 | 18.4784 | 18.0953 | 17.5247 | 16.6826 | 16.2847 | 15.8868 | 15.5258 | 15.1679 | 13.2216 | 11.2995 | 10.2363 | 18.6426 | 18.4447 | 18.2405 | 17.7995 | 16.9132 | 16.5616 | 16.21 | 15.8879 | 15.5711 | 13.8132 | 12.0616 | 10.99 | 18.6605 | 18.47 | 18.2721 | 18.0511 | 17.6911 | 17.3532 | 16.9711 | 16.6047 | 16.2426 | 14.2374 | 12.2247 | 11.0774
|  | LONGHAUGH | HT |  |  |  |  | 18.59 | 18.1037 | 17.7489 | 17.1058 | 16.1626 | 15.8132 | 15.4679 | 15.1026 | 14.7395 | 12.7668 | 11.1984 | 10.1037 | 18.5142 | 18.2732 | 18.0511 | 17.3353 | 16.3226 | 16.0058 | 15.6942 | 15.3711 | 15.05 | 13.1205 | 11.5247 | 10.3605 | 18.5416 | 18.3142 | 18.0974 | 17.85 | 17.2016 | 16.8521 | 16.5058 | 16.1395 | 15.7763 | 13.6889 | 11.9995 | 10.8016
|  | LONGHAUGH | HE |  |  |  |  | 18.9184 | 18.8005 | 18.41 | 17.8742 | 17.0626 | 16.7605 | 16.4626 | 16.1711 | 15.8921 | 14.7195 | 13.85 | 11.9732 | 18.8058 | 18.6626 | 18.4911 | 18.1489 | 17.2974 | 17.0289 | 16.7647 | 16.5058 | 16.2605 | 15.2458 | 14.5311 | 12.6405 | 18.5416 | 18.3142 | 18.0974 | 17.85 | 17.2016 | 16.8521 | 16.5058 | 16.1395 | 15.7763 | 13.6889 | 11.9995 | 10.8016
|  | LONGHAUGH | CF |  |  |  |  | 19.0174 | 18.9511 | 18.8826 | 18.8142 | 18.6847 | 18.5616 | 18.3763 | 18.1626 | 17.9553 | 17.0584 | 16.3395 | 15.2247 | 18.9258 | 18.8563 | 18.7826 | 18.7058 | 18.5963 | 18.4879 | 18.3784 | 18.2732 | 18.1732 | 17.4868 | 16.8332 | 15.6553 | 18.9289 | 18.8616 | 18.7889 | 18.7142 | 18.5837 | 18.4574 | 18.3311 | 18.2111 | 18.1037 | 17.5489 | 17.0647 | 16.2668
| INVERNESS | LONGMAN DRIVE | MINIMUM HEADROOM | NH 67139 46770 | NO | YES | 0 | 25.7785 | 25.6563 | 24.4092 | 24.3246 | 24.1692 | 24.09 | 23.841 | 23.5964 | 23.2668 | 22.5754 | 22.4835 | 22.2608 | 25.1809 | 25.0696 | 24.0432 | 23.958 | 23.7903 | 23.7164 | 23.44 | 23.1683 | 22.8388 | 22.1192 | 22.0802 | 21.809 | 25.8259 | 25.742 | 24.3631 | 24.2891 | 24.0666 | 23.9707 | 23.5127 | 23.0561 | 22.5705 | 21.7706 | 21.7701 | 21.4975
|  | LONGMAN DRIVE | EE |  |  |  |  | 25.8266 | 25.7267 | 24.4092 | 24.3246 | 24.1692 | 24.09 | 23.841 | 23.5964 | 23.2668 | 22.5754 | 22.4835 | 22.2608 | 25.2221 | 25.1311 | 24.0432 | 23.958 | 23.7903 | 23.7164 | 23.44 | 23.1683 | 22.8388 | 22.1192 | 22.0802 | 21.809 | 25.8586 | 25.7905 | 24.3631 | 24.2891 | 24.0666 | 23.9707 | 23.5127 | 23.0561 | 22.5705 | 21.7706 | 21.7701 | 21.4975
|  | LONGMAN DRIVE | HT |  |  |  |  | 25.7785 | 25.6563 | 25.5179 | 25.3865 | 25.0414 | 24.7495 | 24.3809 | 24.1122 | 23.8513 | 23.6242 | 23.2675 | 22.955 | 25.1809 | 25.0696 | 24.9391 | 24.817 | 24.4452 | 24.1274 | 23.7693 | 23.51 | 23.2546 | 23.1208 | 22.6981 | 22.2813 | 25.8259 | 25.742 | 25.6486 | 25.5101 | 24.8886 | 24.3552 | 23.8303 | 23.5193 | 23.2223 | 23.0822 | 22.6298 | 22.2139
|  | LONGMAN DRIVE | HE |  |  |  |  | 25.8841 | 25.8135 | 25.7347 | 25.6483 | 25.4892 | 25.4138 | 25.269 | 25.131 | 24.9984 | 24.5923 | 24.406 | 23.8207 | 25.2713 | 25.2074 | 25.1362 | 25.0576 | 24.9009 | 24.8275 | 24.6729 | 24.5232 | 24.3784 | 23.9482 | 23.9398 | 23.1455 | 25.8259 | 25.742 | 25.6486 | 25.5101 | 24.8886 | 24.3552 | 23.8303 | 23.5193 | 23.2223 | 23.0822 | 22.6298 | 22.2139
|  | LONGMAN DRIVE | CF |  |  |  |  | 25.9383 | 25.9112 | 25.8754 | 25.8386 | 25.7724 | 25.7271 | 25.6903 | 25.6079 | 25.5222 | 25.1894 | 25.0096 | 24.8661 | 25.3258 | 25.2922 | 25.2579 | 25.2228 | 25.1622 | 25.1212 | 25.0884 | 25.002 | 24.9112 | 24.5584 | 24.3752 | 24.2251 | 25.9377 | 25.9117 | 25.8848 | 25.8562 | 25.8124 | 25.7806 | 25.7527 | 25.6743 | 25.5367 | 25.0038 | 24.7289 | 24.4903
| ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 0 | 11.6168 | 11.5084 | 11.3989 | 11.2884 | 11.1116 | 10.8463 | 10.5884 | 10.3274 | 10.0716 | 9.0147 | 8.3726 | 7.8421 | 12.7189 | 12.4684 | 12.2105 | 11.9432 | 11.6505 | 11.3579 | 11.0726 | 10.7842 | 10.5021 | 9.3421 | 8.6484 | 8.0611 | 11.4011 | 11.2926 | 11.1832 | 10.9537 | 10.6642 | 10.3758 | 10.0947 | 9.8095 | 9.5305 | 8.3453 | 7.6337 | 7.0358
|  | LOSSIEMOUTH | EE |  |  |  |  | 11.6726 | 11.5842 | 11.4895 | 11.3916 | 11.2705 | 11.1147 | 10.8842 | 10.6611 | 10.4432 | 9.4021 | 8.7958 | 8.3842 | 12.8526 | 12.6453 | 12.4232 | 12.1884 | 11.9274 | 11.6674 | 11.4179 | 11.1716 | 10.9337 | 9.7905 | 9.1821 | 8.7358 | 11.4568 | 11.3684 | 11.2737 | 11.1758 | 10.9295 | 10.6695 | 10.42 | 10.1758 | 9.9379 | 8.7726 | 8.1295 | 7.6695
|  | LOSSIEMOUTH | HT |  |  |  |  | 11.6168 | 11.5084 | 11.3989 | 11.2884 | 11.1116 | 10.8463 | 10.5884 | 10.3274 | 10.0716 | 9.0147 | 8.3726 | 7.8421 | 12.7189 | 12.4684 | 12.2105 | 11.9432 | 11.6505 | 11.3579 | 11.0726 | 10.7842 | 10.5021 | 9.3421 | 8.6484 | 8.0611 | 11.4011 | 11.2926 | 11.1832 | 10.9537 | 10.6642 | 10.3758 | 10.0947 | 9.8095 | 9.5305 | 8.3453 | 7.6337 | 7.0358
|  | LOSSIEMOUTH | HE |  |  |  |  | 11.7568 | 11.6937 | 11.6253 | 11.5526 | 11.4505 | 11.36 | 11.2695 | 11.1632 | 10.9926 | 10.2568 | 9.8853 | 9.6147 | 12.9526 | 12.8853 | 12.7263 | 12.5463 | 12.3305 | 12.1274 | 11.9263 | 11.7305 | 11.5421 | 10.7232 | 10.3295 | 10.06 | 11.4011 | 11.2926 | 11.1832 | 10.9537 | 10.6642 | 10.3758 | 10.0947 | 9.8095 | 9.5305 | 8.3453 | 7.6337 | 7.0358
|  | LOSSIEMOUTH | CF |  |  |  |  | 11.8105 | 11.7747 | 11.7379 | 11.7011 | 11.6537 | 11.6074 | 11.5611 | 11.5158 | 11.4737 | 11.1958 | 10.9179 | 10.7284 | 13.0095 | 12.9716 | 12.9326 | 12.8895 | 12.7832 | 12.6747 | 12.5632 | 12.4495 | 12.3305 | 11.7432 | 11.4474 | 11.24 | 11.5947 | 11.5589 | 11.5221 | 11.4853 | 11.4389 | 11.3937 | 11.3474 | 11.3032 | 11.2611 | 10.7432 | 10.4411 | 10.2316
| BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 0 | 1.1726 | 1.1368 | 1.1032 | 1.0684 | 0.93158 | 0.74947 | 0.56211 | 0.4 | 0.21263 | -1.3053 | -2.9895 | -4.2158 | 1.1484 | 1.1116 | 1.0779 | 1.0432 | 0.93053 | 0.79579 | 0.64421 | 0.51158 | 0.27895 | -1.1011 | -2.7379 | -4.0611 | 1.1621 | 1.1316 | 1.0989 | 1.0653 | 0.92211 | 0.73684 | 0.54526 | 0.38105 | 0.20316 | -1.4326 | -3.2653 | -4.6789
|  | LOWER OLLACH | EE |  |  |  |  | 1.1905 | 1.1558 | 1.12 | 1.0874 | 0.93158 | 0.74947 | 0.56211 | 0.4 | 0.23579 | -1.3053 | -2.9895 | -4.2158 | 1.1674 | 1.1347 | 1.1021 | 1.0705 | 0.94316 | 0.79579 | 0.64421 | 0.51158 | 0.37895 | -1.1011 | -2.7379 | -4.0611 | 1.1705 | 1.1474 | 1.1147 | 1.0811 | 0.92211 | 0.73684 | 0.54526 | 0.38105 | 0.21263 | -1.4326 | -3.2653 | -4.6789
|  | LOWER OLLACH | HT |  |  |  |  | 1.1726 | 1.1368 | 1.1032 | 1.0684 | 0.93368 | 0.8 | 0.66526 | 0.50526 | 0.22842 | -1.1263 | -2.6074 | -3.6032 | 1.1484 | 1.1116 | 1.0779 | 1.0432 | 0.93053 | 0.81789 | 0.70526 | 0.57474 | 0.30526 | -1.0663 | -2.6779 | -3.8116 | 1.1621 | 1.1316 | 1.0989 | 1.0653 | 0.92842 | 0.79158 | 0.65474 | 0.49368 | 0.20316 | -1.3011 | -3.0084 | -4.1737
|  | LOWER OLLACH | HE |  |  |  |  | 1.2179 | 1.2011 | 1.1853 | 1.1674 | 0.99789 | 0.81895 | 0.63579 | 0.46105 | 0.21263 | -0.84316 | -2.1189 | -3.5042 | 1.1968 | 1.18 | 1.1632 | 1.1453 | 1.0063 | 0.84421 | 0.67789 | 0.52211 | 0.27895 | -0.73158 | -2.0211 | -3.4221 | 1.1621 | 1.1316 | 1.0989 | 1.0653 | 0.92842 | 0.79158 | 0.65474 | 0.49368 | 0.20316 | -1.3011 | -3.0084 | -4.1737
|  | LOWER OLLACH | CF |  |  |  |  | 1.2316 | 1.22 | 1.2105 | 1.2011 | 1.1379 | 1.0842 | 0.99789 | 0.89158 | 0.77684 | 0.23895 | -0.56105 | -1.4295 | 1.2063 | 1.2011 | 1.1895 | 1.1811 | 1.1284 | 1.0832 | 1.0011 | 0.89368 | 0.77053 | 0.23263 | -0.5821 | -1.5179 | 1.1937 | 1.1874 | 1.18 | 1.1758 | 1.1263 | 1.0747 | 0.99053 | 0.88526 | 0.75368 | 0.15895 | -0.73474 | -1.7316
| KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19579 | 0.19474 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19158 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19158
|  | LUBNAIG | EE |  |  |  |  | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19579 | 0.19579 | 0.19474 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19579 | 0.19579 | 0.19474
|  | LUBNAIG | HT |  |  |  |  | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19579 | 0.19474 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19158 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19158
|  | LUBNAIG | HE |  |  |  |  | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19789 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19158
|  | LUBNAIG | CF |  |  |  |  | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895
| LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | YES | 0.968 | 13.1315 | 12.8978 | 12.6631 | 12.4283 | 11.3388 | 10.3946 | 9.3809 | 8.042 | 6.1009 | -4.458 | -17.7875 | -28.8391 | 11.7509 | 11.5162 | 11.2815 | 11.0467 | 10.2594 | 9.4394 | 8.6141 | 7.4625 | 5.5036 | -5.3659 | -17.6638 | -29.8427 | 12.047 | 11.7965 | 11.5459 | 11.2954 | 10.247 | 9.2912 | 8.2849 | 7.0881 | 5.0396 | -7.1614 | -21.3467 | -34.1383
|  | LUNANHEAD | EE |  |  |  |  | 13.2346 | 13.0041 | 12.7673 | 12.5294 | 11.3388 | 11.2073 | 9.7915 | 8.5652 | 7.3178 | -4.3296 | -17.7875 | -28.8391 | 11.8636 | 11.6436 | 11.4194 | 11.1941 | 10.2857 | 10.1478 | 9.0215 | 8.0425 | 7.0499 | -4.4227 | -17.6638 | -29.8427 | 12.1596 | 11.9154 | 11.667 | 11.4165 | 10.247 | 10.1059 | 8.7144 | 7.4944 | 6.2523 | -6.5983 | -21.3467 | -34.1383
|  | LUNANHEAD | HT |  |  |  |  | 13.1315 | 12.8978 | 12.6631 | 12.4283 | 11.3988 | 10.3946 | 9.3809 | 8.182 | 6.2967 | -4.458 | -15.2959 | -23.719 | 11.7509 | 11.5162 | 11.2815 | 11.0467 | 10.2594 | 9.4394 | 8.6141 | 7.6446 | 5.832 | -5.3659 | -17.1869 | -26.6806 | 12.047 | 11.7965 | 11.5459 | 11.2954 | 10.2775 | 9.2912 | 8.2849 | 7.0881 | 5.0396 | -7.1614 | -19.572 | -29.2698
|  | LUNANHEAD | HE |  |  |  |  | 13.3399 | 13.2388 | 13.1178 | 12.9831 | 11.7378 | 10.7104 | 9.4125 | 8.042 | 6.1009 | -2.1601 | -12.4906 | -24.697 | 11.972 | 11.8678 | 11.7457 | 11.6057 | 10.6815 | 9.8646 | 8.7088 | 7.4625 | 5.5036 | -2.6606 | -13.1859 | -25.8617 | 12.047 | 11.7965 | 11.5459 | 11.2954 | 10.2775 | 9.2912 | 8.2849 | 7.0881 | 5.0396 | -7.1614 | -19.572 | -29.2698
|  | LUNANHEAD | CF |  |  |  |  | 13.4325 | 13.3778 | 13.322 | 13.2662 | 12.7978 | 12.3736 | 11.9546 | 11.3799 | 10.4662 | 6.2441 | -0.22432 | -7.3927 | 12.072 | 12.0204 | 11.9688 | 11.9152 | 11.5752 | 11.2615 | 10.9236 | 10.3657 | 9.3394 | 4.9309 | -1.8154 | -9.6354 | 12.3712 | 12.3144 | 12.2586 | 12.2017 | 11.7449 | 11.327 | 10.9154 | 10.2881 | 9.1944 | 4.3744 | -2.9277 | -11.1372
| PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0 | 0.10526 | 0.10421 | 0.10316 | 0.10211 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.095789 | 0.092632 | 0.088421 | 0.08421 | 0.10211 | 0.10105 | 0.1 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.092632 | 0.088421 | 0.08421 | 0.08 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.085263 | 0.081053
|  | LUSSAGIVEN | EE |  |  |  |  | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.098947 | 0.094737 | 0.092632 | 0.089474 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.091579 | 0.088421 | 0.086316 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.097895 | 0.097895 | 0.096842 | 0.092632 | 0.089474 | 0.087368
|  | LUSSAGIVEN | HT |  |  |  |  | 0.10526 | 0.10421 | 0.10316 | 0.10211 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.095789 | 0.092632 | 0.088421 | 0.08421 | 0.10211 | 0.10105 | 0.1 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.092632 | 0.088421 | 0.08421 | 0.08 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.085263 | 0.081053
|  | LUSSAGIVEN | HE |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.1 | 0.098947 | 0.096842 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.097895 | 0.096842 | 0.093684 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.085263 | 0.081053
|  | LUSSAGIVEN | CF |  |  |  |  | 0.10737 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10105 | 0.1 | 0.10526 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.10526 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.098947 | 0.097895
| LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | YES | 0 | 15.9089 | 15.8532 | 15.7963 | 15.7374 | 15.6658 | 15.6016 | 15.5384 | 15.4763 | 15.4163 | 15.1932 | 14.8668 | 14.5942 | 14.6989 | 14.6453 | 14.5895 | 14.5316 | 14.4653 | 14.4042 | 14.3453 | 14.2884 | 14.2189 | 13.8053 | 13.4105 | 13.1 | 15.2255 | 15.1718 | 15.115 | 15.0571 | 14.9876 | 14.9234 | 14.8613 | 14.8013 | 14.7413 | 14.4066 | 14.0118 | 13.7034
|  | LYNDHURST | EE |  |  |  |  | 15.9395 | 15.8953 | 15.8479 | 15.7974 | 15.7363 | 15.6816 | 15.6268 | 15.5763 | 15.5268 | 15.3089 | 15.1563 | 14.9637 | 14.7295 | 14.6874 | 14.6389 | 14.5905 | 14.5358 | 14.4863 | 14.4368 | 14.3905 | 14.3463 | 14.1042 | 13.7905 | 13.5495 | 15.2561 | 15.2129 | 15.1655 | 15.1171 | 15.0582 | 15.0034 | 14.9508 | 14.8992 | 14.8508 | 14.6382 | 14.3708 | 14.1287
|  | LYNDHURST | HT |  |  |  |  | 15.9089 | 15.8532 | 15.7963 | 15.7374 | 15.6658 | 15.6016 | 15.5384 | 15.4763 | 15.4163 | 15.1932 | 14.8668 | 14.5942 | 14.6989 | 14.6453 | 14.5895 | 14.5316 | 14.4653 | 14.4042 | 14.3453 | 14.2884 | 14.2189 | 13.8053 | 13.4105 | 13.1 | 15.2255 | 15.1718 | 15.115 | 15.0571 | 14.9876 | 14.9234 | 14.8613 | 14.8013 | 14.7413 | 14.4066 | 14.0118 | 13.7034
|  | LYNDHURST | HE |  |  |  |  | 15.9763 | 15.9416 | 15.9037 | 15.8626 | 15.8111 | 15.7679 | 15.7247 | 15.6847 | 15.6489 | 15.5132 | 15.4216 | 15.3563 | 14.7653 | 14.7316 | 14.6947 | 14.6547 | 14.6084 | 14.5695 | 14.5316 | 14.4947 | 14.4621 | 14.3442 | 14.2526 | 14.1526 | 15.2255 | 15.1718 | 15.115 | 15.0571 | 14.9876 | 14.9234 | 14.8613 | 14.8013 | 14.7413 | 14.4066 | 14.0118 | 13.7034
|  | LYNDHURST | CF |  |  |  |  | 16.0016 | 15.9816 | 15.9605 | 15.9405 | 15.9163 | 15.8911 | 15.8679 | 15.8437 | 15.8205 | 15.7153 | 15.6468 | 15.6079 | 14.7905 | 14.7705 | 14.7495 | 14.7295 | 14.7084 | 14.6842 | 14.6621 | 14.6389 | 14.6179 | 14.5211 | 14.4632 | 14.4326 | 15.3171 | 15.2982 | 15.2771 | 15.2571 | 15.2329 | 15.2076 | 15.1845 | 15.1603 | 15.1392 | 15.0361 | 14.9697 | 14.9318
| THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | YES | 0 | 0.97895 | 0.96316 | 0.94947 | 0.93368 | 0.91789 | 0.90316 | 0.88842 | 0.87474 | 0.86105 | 0.80842 | 0.76421 | 0.72 | 0.96947 | 0.95158 | 0.93579 | 0.91895 | 0.90105 | 0.88526 | 0.86947 | 0.85474 | 0.84 | 0.78211 | 0.73368 | 0.68421 | 0.97263 | 0.95474 | 0.94 | 0.92316 | 0.90526 | 0.88947 | 0.87368 | 0.85895 | 0.84421 | 0.78737 | 0.73895 | 0.68947
|  | LYNESS | EE |  |  |  |  | 0.98947 | 0.97684 | 0.96421 | 0.95158 | 0.94 | 0.92737 | 0.91684 | 0.90526 | 0.89579 | 0.84947 | 0.81789 | 0.78842 | 0.98 | 0.96737 | 0.95368 | 0.94 | 0.92632 | 0.91263 | 0.90105 | 0.88842 | 0.87789 | 0.82737 | 0.79263 | 0.76 | 0.98421 | 0.97053 | 0.95684 | 0.94316 | 0.93053 | 0.91684 | 0.90526 | 0.89263 | 0.88211 | 0.83263 | 0.79789 | 0.76421
|  | LYNESS | HT |  |  |  |  | 0.97895 | 0.96316 | 0.94947 | 0.93368 | 0.91789 | 0.90316 | 0.88842 | 0.87474 | 0.86105 | 0.80842 | 0.76421 | 0.72 | 0.96947 | 0.95158 | 0.93579 | 0.91895 | 0.90105 | 0.88526 | 0.86947 | 0.85474 | 0.84 | 0.78211 | 0.73368 | 0.68421 | 0.97263 | 0.95474 | 0.94 | 0.92316 | 0.90526 | 0.88947 | 0.87368 | 0.85895 | 0.84421 | 0.78737 | 0.73895 | 0.68947
|  | LYNESS | HE |  |  |  |  | 1.0032 | 0.99684 | 0.98737 | 0.98 | 0.97053 | 0.96211 | 0.95474 | 0.94737 | 0.94 | 0.91579 | 0.89895 | 0.88737 | 0.98947 | 0.98421 | 0.97789 | 0.97053 | 0.96211 | 0.95263 | 0.94421 | 0.93684 | 0.92842 | 0.90211 | 0.88211 | 0.86947 | 0.97263 | 0.95474 | 0.94 | 0.92316 | 0.90526 | 0.88947 | 0.87368 | 0.85895 | 0.84421 | 0.78737 | 0.73895 | 0.68947
|  | LYNESS | CF |  |  |  |  | 1.0126 | 1.0074 | 1.0032 | 0.99789 | 0.99263 | 0.98947 | 0.98421 | 0.97895 | 0.97368 | 0.95263 | 0.93789 | 0.92842 | 0.99579 | 0.99368 | 0.98947 | 0.98526 | 0.98211 | 0.97895 | 0.97474 | 0.96947 | 0.96421 | 0.94 | 0.92421 | 0.91263 | 1.0084 | 1.0042 | 0.99895 | 0.99368 | 0.98737 | 0.98316 | 0.97789 | 0.97263 | 0.96737 | 0.94421 | 0.92842 | 0.91684
| STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0 | 0.20526 | 0.20316 | 0.2 | 0.19789 | 0.18105 | 0.15684 | 0.13158 | 0.10842 | 0.068421 | -0.15368 | -0.43789 | -0.66632 | 0.19368 | 0.19053 | 0.18842 | 0.18526 | 0.17053 | 0.14632 | 0.12105 | 0.097895 | 0.056842 | -0.17684 | -0.49579 | -0.72421 | 0.20842 | 0.20526 | 0.20211 | 0.2 | 0.18316 | 0.16211 | 0.13895 | 0.12 | 0.070526 | -0.19053 | -0.51789 | -0.76105
|  | MAARUIG | EE |  |  |  |  | 0.20632 | 0.20421 | 0.20105 | 0.19895 | 0.18105 | 0.16 | 0.13789 | 0.11895 | 0.090526 | -0.15158 | -0.43053 | -0.66632 | 0.19474 | 0.19263 | 0.18947 | 0.18632 | 0.17263 | 0.15368 | 0.13684 | 0.12105 | 0.093684 | -0.15579 | -0.44211 | -0.70421 | 0.21053 | 0.20737 | 0.20316 | 0.20105 | 0.18421 | 0.16211 | 0.13895 | 0.12 | 0.089474 | -0.18316 | -0.49053 | -0.76105
|  | MAARUIG | HT |  |  |  |  | 0.20526 | 0.20316 | 0.2 | 0.19789 | 0.18211 | 0.16632 | 0.15053 | 0.12632 | 0.08 | -0.15368 | -0.43789 | -0.63789 | 0.19368 | 0.19053 | 0.18842 | 0.18526 | 0.17158 | 0.15895 | 0.14526 | 0.12211 | 0.070526 | -0.17684 | -0.49579 | -0.72421 | 0.20842 | 0.20526 | 0.20211 | 0.2 | 0.18316 | 0.16842 | 0.15158 | 0.12526 | 0.070526 | -0.19053 | -0.51789 | -0.74947
|  | MAARUIG | HE |  |  |  |  | 0.20842 | 0.20632 | 0.20421 | 0.20421 | 0.18211 | 0.15684 | 0.13158 | 0.10842 | 0.068421 | -0.10105 | -0.32526 | -0.57053 | 0.19789 | 0.19579 | 0.19263 | 0.19263 | 0.17053 | 0.14632 | 0.12105 | 0.097895 | 0.056842 | -0.11579 | -0.35263 | -0.61263 | 0.20842 | 0.20526 | 0.20211 | 0.2 | 0.18316 | 0.16842 | 0.15158 | 0.12526 | 0.070526 | -0.19053 | -0.51789 | -0.74947
|  | MAARUIG | CF |  |  |  |  | 0.20842 | 0.20842 | 0.20737 | 0.20526 | 0.19895 | 0.19368 | 0.17895 | 0.16211 | 0.14211 | 0.052632 | -0.089474 | -0.25579 | 0.19789 | 0.19789 | 0.19684 | 0.19474 | 0.18947 | 0.18526 | 0.16632 | 0.14842 | 0.12421 | 0.028421 | -0.12316 | -0.30737 | 0.21158 | 0.21158 | 0.21158 | 0.20947 | 0.20421 | 0.19789 | 0.18 | 0.15895 | 0.13474 | 0.033684 | -0.12526 | -0.31579
| LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | YES | 0 | 16.4463 | 16.2853 | 16.1211 | 15.9568 | 15.6937 | 15.3674 | 15.0295 | 14.6832 | 14.2779 | 12.9674 | 12.0074 | 11.2653 | 15.8968 | 15.7284 | 15.4558 | 15.1558 | 14.8453 | 14.4874 | 14.1221 | 13.7484 | 13.3032 | 11.8789 | 10.82 | 9.9916 | 15.9484 | 15.7789 | 15.4821 | 15.1853 | 14.8737 | 14.5147 | 14.1484 | 13.7737 | 13.3284 | 11.9063 | 10.8463 | 10.0221
|  | MACALPINE ROAD | EE |  |  |  |  | 16.5389 | 16.4095 | 16.2737 | 16.1316 | 15.9737 | 15.8168 | 15.58 | 15.3179 | 15.0547 | 13.8137 | 13.0011 | 12.4337 | 15.9958 | 15.8611 | 15.7189 | 15.5421 | 15.2863 | 15.0389 | 14.74 | 14.4526 | 14.1705 | 12.8358 | 11.9653 | 11.3379 | 16.0474 | 15.9116 | 15.7695 | 15.5674 | 15.3084 | 15.0579 | 14.7558 | 14.4674 | 14.1811 | 12.84 | 11.9495 | 11.32
|  | MACALPINE ROAD | HT |  |  |  |  | 16.4463 | 16.2853 | 16.1211 | 15.9568 | 15.6937 | 15.3674 | 15.0295 | 14.6832 | 14.2779 | 12.9674 | 12.0074 | 11.2653 | 15.8968 | 15.7284 | 15.4558 | 15.1558 | 14.8453 | 14.4874 | 14.1221 | 13.7484 | 13.3032 | 11.8789 | 10.82 | 9.9916 | 15.9484 | 15.7789 | 15.4821 | 15.1853 | 14.8737 | 14.5147 | 14.1484 | 13.7737 | 13.3284 | 11.9063 | 10.8463 | 10.0221
|  | MACALPINE ROAD | HE |  |  |  |  | 16.6611 | 16.5695 | 16.4695 | 16.3632 | 16.2347 | 16.1168 | 16.0032 | 15.8926 | 15.7916 | 14.9158 | 14.4305 | 14.0863 | 16.1263 | 16.0316 | 15.9284 | 15.8189 | 15.6968 | 15.5832 | 15.4716 | 15.2516 | 14.9989 | 14 | 13.4789 | 13.1147 | 15.9484 | 15.7789 | 15.4821 | 15.1853 | 14.8737 | 14.5147 | 14.1484 | 13.7737 | 13.3284 | 11.9063 | 10.8463 | 10.0221
|  | MACALPINE ROAD | CF |  |  |  |  | 16.7421 | 16.6916 | 16.6389 | 16.5842 | 16.5242 | 16.4632 | 16.4032 | 16.3432 | 16.2853 | 16 | 15.6421 | 15.3832 | 16.2116 | 16.1579 | 16.1032 | 16.0474 | 15.9874 | 15.9274 | 15.8674 | 15.8063 | 15.7474 | 15.1747 | 14.7758 | 14.4895 | 16.2632 | 16.2095 | 16.1547 | 16.0979 | 16.0358 | 15.9726 | 15.9105 | 15.8474 | 15.7874 | 15.1916 | 14.7863 | 14.4968
| MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | YES | 0.019 | 20.8399 | 20.5252 | 20.1315 | 19.6326 | 18.6684 | 17.8789 | 17.0747 | 16.0831 | 14.7042 | 10.7252 | 5.0368 | 3.6315 | 17.5115 | 17.0778 | 16.6399 | 16.0673 | 15.0684 | 14.2915 | 13.4957 | 12.4968 | 11.0021 | 7.3905 | 2.9736 | 0.18521 | 19.0831 | 18.7189 | 18.3515 | 17.8589 | 16.8999 | 16.1136 | 15.3126 | 14.2905 | 12.7642 | 8.6063 | 2.8473 | 0.87574
|  | MACDUFF | EE |  |  |  |  | 20.9526 | 20.7652 | 20.4884 | 20.1073 | 19.1863 | 18.2905 | 17.4084 | 16.6021 | 15.7705 | 10.7252 | 5.0368 | 16.6242 | 17.7778 | 17.4294 | 17.0578 | 16.6336 | 15.7199 | 14.8799 | 14.0631 | 13.3021 | 12.5126 | 7.4905 | 2.9736 | 19.6389 | 19.2978 | 18.9968 | 18.6789 | 18.3242 | 17.4115 | 16.5168 | 15.6347 | 14.8294 | 14.001 | 8.6063 | 2.8473 | 18.801
|  | MACDUFF | HT |  |  |  |  | 20.8399 | 20.5252 | 20.1315 | 19.6326 | 18.6684 | 17.8789 | 17.0747 | 16.0831 | 14.7042 | 11.0894 | 6.5421 | 3.6315 | 17.5115 | 17.0778 | 16.6399 | 16.0673 | 15.0684 | 14.2915 | 13.4957 | 12.4968 | 11.0021 | 7.3905 | 3.5242 | 0.18521 | 19.0831 | 18.7189 | 18.3515 | 17.8589 | 16.8999 | 16.1136 | 15.3126 | 14.2905 | 12.7642 | 8.8821 | 4.2042 | 0.87574
|  | MACDUFF | HE |  |  |  |  | 21.1094 | 20.9915 | 20.8631 | 20.7263 | 19.8568 | 19.1642 | 18.4947 | 17.8326 | 17.1568 | 14.3252 | 10.041 | 6.2105 | 18.1273 | 17.8978 | 17.6431 | 17.3094 | 16.4621 | 15.8052 | 15.1757 | 14.5515 | 13.9094 | 11.281 | 7.3357 | 3.3515 | 19.0831 | 18.7189 | 18.3515 | 17.8589 | 16.8999 | 16.1136 | 15.3126 | 14.2905 | 12.7642 | 8.8821 | 4.2042 | 0.87574
|  | MACDUFF | CF |  |  |  |  | 21.2115 | 21.1442 | 21.0768 | 21.0073 | 20.8052 | 20.6189 | 20.4336 | 20.2073 | 19.9642 | 18.2526 | 16.1326 | 13.7757 | 18.3505 | 18.2199 | 18.0831 | 17.941 | 17.6873 | 17.4421 | 17.1957 | 16.9452 | 16.6894 | 14.9326 | 12.7568 | 10.1126 | 19.7357 | 19.6536 | 19.5389 | 19.421 | 19.1473 | 18.8894 | 18.6326 | 18.3821 | 18.1473 | 16.4757 | 14.341 | 11.6778
| CARRADALE 1 | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 0 | 2.7726 | 2.7274 | 2.6758 | 2.6242 | 2.5695 | 2.5179 | 2.4674 | 2.4179 | 2.3716 | 2.1979 | 2.0821 | 1.98 | 2.5937 | 2.5442 | 2.4863 | 2.4274 | 2.3663 | 2.3074 | 2.2505 | 2.1947 | 2.1421 | 1.9421 | 1.8084 | 1.6947 | 2.6274 | 2.5779 | 2.52 | 2.4611 | 2.4 | 2.3411 | 2.2842 | 2.2284 | 2.1758 | 1.9758 | 1.8421 | 1.7284
|  | MACHRIE | EE |  |  |  |  | 2.8032 | 2.7674 | 2.7253 | 2.6821 | 2.6379 | 2.5958 | 2.5537 | 2.5137 | 2.4758 | 2.3253 | 2.24 | 2.1705 | 2.6295 | 2.5895 | 2.5421 | 2.4926 | 2.4432 | 2.3947 | 2.3474 | 2.3011 | 2.2579 | 2.0853 | 1.9874 | 1.9063 | 2.6632 | 2.6232 | 2.5758 | 2.5263 | 2.4768 | 2.4284 | 2.3811 | 2.3347 | 2.2916 | 2.1189 | 2.0211 | 1.94
|  | MACHRIE | HT |  |  |  |  | 2.7726 | 2.7274 | 2.6758 | 2.6242 | 2.5695 | 2.5179 | 2.4674 | 2.4179 | 2.3716 | 2.1979 | 2.0821 | 1.98 | 2.5937 | 2.5442 | 2.4863 | 2.4274 | 2.3663 | 2.3074 | 2.2505 | 2.1947 | 2.1421 | 1.9421 | 1.8084 | 1.6947 | 2.6274 | 2.5779 | 2.52 | 2.4611 | 2.4 | 2.3411 | 2.2842 | 2.2284 | 2.1758 | 1.9758 | 1.8421 | 1.7284
|  | MACHRIE | HE |  |  |  |  | 2.8453 | 2.8221 | 2.7937 | 2.7621 | 2.7284 | 2.6968 | 2.6653 | 2.6358 | 2.6074 | 2.5105 | 2.4663 | 2.4347 | 2.6768 | 2.6516 | 2.6189 | 2.5832 | 2.5453 | 2.5095 | 2.4737 | 2.4389 | 2.4063 | 2.2958 | 2.2453 | 2.2074 | 2.6274 | 2.5779 | 2.52 | 2.4611 | 2.4 | 2.3411 | 2.2842 | 2.2284 | 2.1758 | 1.9758 | 1.8421 | 1.7284
|  | MACHRIE | CF |  |  |  |  | 2.8684 | 2.8558 | 2.84 | 2.8232 | 2.8063 | 2.7895 | 2.7716 | 2.7526 | 2.7347 | 2.6589 | 2.62 | 2.5926 | 2.7032 | 2.6884 | 2.6705 | 2.6505 | 2.6316 | 2.6126 | 2.5916 | 2.5705 | 2.5495 | 2.4611 | 2.4168 | 2.3832 | 2.7168 | 2.7095 | 2.7011 | 2.6842 | 2.6653 | 2.6463 | 2.6253 | 2.6042 | 2.5832 | 2.4947 | 2.4505 | 2.4168
| FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | NO | 0 | 2.1066 | 2.0708 | 2.0361 | 2.0003 | 1.8887 | 1.7866 | 1.6834 | 1.6508 | 1.6203 | 1.4761 | 1.3561 | 1.2466 | 2.2097 | 2.1697 | 2.1308 | 2.0918 | 1.9603 | 1.8371 | 1.7139 | 1.6782 | 1.6455 | 1.4824 | 1.3445 | 1.2224 | 2.1097 | 2.075 | 2.0403 | 2.0034 | 1.8697 | 1.7455 | 1.6213 | 1.5855 | 1.5518 | 1.3887 | 1.2497 | 1.1255
|  | MALLAIG | EE |  |  |  |  | 2.1318 | 2.1034 | 2.0739 | 2.0455 | 2.0171 | 1.9897 | 1.895 | 1.8003 | 1.7076 | 1.5918 | 1.5024 | 1.4213 | 2.2371 | 2.2066 | 2.175 | 2.1434 | 2.1129 | 2.0834 | 1.9687 | 1.855 | 1.7434 | 1.6129 | 1.5097 | 1.4139 | 2.1339 | 2.1066 | 2.0782 | 2.0497 | 2.0224 | 1.9939 | 1.8792 | 1.7645 | 1.6508 | 1.5203 | 1.4161 | 1.3192
|  | MALLAIG | HT |  |  |  |  | 2.1066 | 2.0708 | 2.0361 | 2.0003 | 1.8887 | 1.7866 | 1.6834 | 1.6508 | 1.6203 | 1.4761 | 1.3561 | 1.2466 | 2.2097 | 2.1697 | 2.1308 | 2.0918 | 1.9603 | 1.8371 | 1.7139 | 1.6782 | 1.6455 | 1.4824 | 1.3445 | 1.2224 | 2.1097 | 2.075 | 2.0403 | 2.0034 | 1.8697 | 1.7455 | 1.6213 | 1.5855 | 1.5518 | 1.3887 | 1.2497 | 1.1255
|  | MALLAIG | HE |  |  |  |  | 2.1645 | 2.1466 | 2.1276 | 2.1076 | 2.0887 | 2.0697 | 1.9971 | 1.9234 | 1.8529 | 1.7539 | 1.7171 | 1.6897 | 2.2592 | 2.2466 | 2.2339 | 2.2129 | 2.1929 | 2.1718 | 2.0845 | 1.9961 | 1.9108 | 1.7971 | 1.7539 | 1.7234 | 2.1097 | 2.075 | 2.0403 | 2.0034 | 1.8697 | 1.7455 | 1.6213 | 1.5855 | 1.5518 | 1.3887 | 1.2497 | 1.1255
|  | MALLAIG | CF |  |  |  |  | 2.1824 | 2.1718 | 2.1592 | 2.1487 | 2.1361 | 2.1255 | 2.1139 | 2.0729 | 2.0297 | 1.9182 | 1.8845 | 1.8603 | 2.2718 | 2.2645 | 2.2571 | 2.2497 | 2.2424 | 2.2308 | 2.2182 | 2.1687 | 2.1161 | 1.9855 | 1.9476 | 1.9182 | 2.1834 | 2.1729 | 2.1603 | 2.1508 | 2.1382 | 2.1276 | 2.1161 | 2.0782 | 2.0276 | 1.895 | 1.8571 | 1.8276
| KEITH 1 | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 0 | 1.4105 | 1.2916 | 1.1737 | 1.0568 | 0.44737 | -0.39053 | -1.2937 | -2.0789 | -2.8853 | -7.3547 | -13.0432 | -17.8526 | 3.3053 | 3.1179 | 2.9147 | 2.7074 | 2.1411 | 1.4811 | 0.71474 | 0.037895 | -0.67053 | -5.6432 | -10.5716 | -15.3242 | 1.6358 | 1.5189 | 1.4021 | 1.2874 | 0.71895 | 0.013684 | -0.70842 | -1.4305 | -2.1916 | -7.2379 | -14.5568 | -19.7632
|  | MARNOCH | EE |  |  |  |  | 1.4516 | 1.3326 | 1.2105 | 1.0895 | 0.44737 | -0.39053 | -1.2937 | -2.0789 | -2.8853 | -6.7684 | -13.0432 | -17.8526 | 3.3895 | 3.2263 | 3.0484 | 2.8663 | 2.2284 | 1.4811 | 0.71474 | 0.037895 | -0.67053 | -4.8768 | -10.5716 | -15.3242 | 1.6768 | 1.5611 | 1.4411 | 1.3232 | 0.71895 | 0.013684 | -0.70842 | -1.4305 | -2.1916 | -6.8347 | -14.5568 | -19.7632
|  | MARNOCH | HT |  |  |  |  | 1.4105 | 1.2916 | 1.1737 | 1.0568 | 0.50526 | -0.12526 | -0.79368 | -1.58 | -2.4032 | -5.9232 | -10.5926 | -14.5632 | 3.3053 | 3.1179 | 2.9147 | 2.7074 | 2.1411 | 1.54 | 0.90316 | 0.17053 | -0.64421 | -5.6432 | -9.5358 | -13.5537 | 1.6358 | 1.5189 | 1.4021 | 1.2874 | 0.76632 | 0.25158 | -0.32842 | -1.0884 | -1.9042 | -7.2379 | -12.3979 | -16.76
|  | MARNOCH | HE |  |  |  |  | 1.5305 | 1.4747 | 1.4158 | 1.3547 | 0.69579 | 0.13158 | -0.53158 | -1.1947 | -1.9379 | -7.3547 | -9.3832 | -16.7874 | 3.5274 | 3.4368 | 3.3274 | 3.2116 | 2.5789 | 2.02 | 1.4242 | 0.82 | -0.027368 | -5.2095 | -7.5642 | -14.1316 | 1.6358 | 1.5189 | 1.4021 | 1.2874 | 0.76632 | 0.25158 | -0.32842 | -1.0884 | -1.9042 | -7.2379 | -12.3979 | -16.76
|  | MARNOCH | CF |  |  |  |  | 1.5347 | 1.4811 | 1.4274 | 1.3726 | 1.1011 | 0.85789 | 0.61579 | 0.40316 | 0.16 | -1.4379 | -4.9768 | -7.2211 | 3.56 | 3.4884 | 3.4147 | 3.3389 | 3.0758 | 2.8316 | 2.5832 | 2.2042 | 1.7979 | -0.13684 | -3.9463 | -6.9021 | 1.76 | 1.7063 | 1.6537 | 1.6 | 1.3432 | 1.1126 | 0.88421 | 0.68316 | 0.52632 | -1.16 | -5.5316 | -8.6789
| BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | YES | 0 | 3.9368 | 3.6211 | 3.2442 | 2.8358 | 2.3547 | 1.9063 | 1.4358 | 0.96947 | 0.49263 | -1.6737 | -3.6716 | -5.6168 | 3.7926 | 3.4737 | 3.08 | 2.6758 | 2.2147 | 1.7863 | 1.3189 | 0.85263 | 0.37263 | -1.7232 | -3.8221 | -5.7368 | 3.7158 | 3.3716 | 2.9737 | 2.5589 | 2.0705 | 1.6084 | 1.1021 | 0.60105 | 0.089474 | -2.1684 | -4.4147 | -6.7611
|  | MARYBANK | EE |  |  |  |  | 3.9368 | 3.6211 | 3.2442 | 2.8358 | 2.3547 | 1.9063 | 1.4358 | 0.96947 | 0.49263 | -1.6737 | -3.6716 | -5.6168 | 3.7926 | 3.4737 | 3.08 | 2.6758 | 2.2147 | 1.7863 | 1.3189 | 0.85263 | 0.37263 | -1.7232 | -3.8221 | -5.7368 | 3.7158 | 3.3716 | 2.9737 | 2.5589 | 2.0705 | 1.6084 | 1.1021 | 0.60105 | 0.089474 | -2.1684 | -4.4147 | -6.7611
|  | MARYBANK | HT |  |  |  |  | 4.1074 | 3.9937 | 3.88 | 3.7589 | 3.5253 | 3.2674 | 3 | 2.8021 | 2.6042 | 1.4968 | -0.096842 | -1.3589 | 3.9126 | 3.8084 | 3.6926 | 3.5621 | 3.3137 | 3.0642 | 2.8074 | 2.64 | 2.4716 | 1.4295 | -0.10947 | -1.3495 | 3.8895 | 3.7484 | 3.6084 | 3.4663 | 3.1705 | 2.8726 | 2.5642 | 2.3589 | 2.1526 | 0.9 | -0.93474 | -2.3758
|  | MARYBANK | HE |  |  |  |  | 4.1484 | 4.0505 | 3.9526 | 3.8526 | 3.6821 | 3.5147 | 3.3168 | 3.1158 | 2.8968 | 1.8274 | 0.52105 | -0.91895 | 3.9926 | 3.9147 | 3.8126 | 3.7063 | 3.5547 | 3.3937 | 3.2084 | 3.0126 | 2.7958 | 1.7853 | 0.53789 | -0.78842 | 3.8895 | 3.7484 | 3.6084 | 3.4663 | 3.1705 | 2.8726 | 2.5642 | 2.3589 | 2.1526 | 0.9 | -0.93474 | -2.3758
|  | MARYBANK | CF |  |  |  |  | 4.2242 | 4.1937 | 4.1653 | 4.1368 | 4.0821 | 4.0337 | 3.9842 | 3.9347 | 3.8695 | 3.4368 | 2.78 | 2.0432 | 4.0558 | 4.0284 | 4.0021 | 3.9737 | 3.9274 | 3.8821 | 3.8347 | 3.7421 | 3.6284 | 3.1758 | 2.5137 | 1.7326 | 4.0547 | 4.0168 | 3.9811 | 3.9453 | 3.88 | 3.8211 | 3.76 | 3.6537 | 3.5284 | 3.0116 | 2.2653 | 1.42
| LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | YES | 0 | 15.3395 | 14.9879 | 14.6184 | 14.2984 | 13.2595 | 11.9953 | 10.6153 | 9.41 | 8.2258 | -1.1237 | -11.93 | -19.751 | 13.1989 | 12.8147 | 12.4116 | 12.0674 | 11.1811 | 10.2789 | 9.1558 | 8.1674 | 7.1832 | -1.6758 | -12.1674 | -20.681 | 13.7845 | 13.3918 | 12.9792 | 12.6276 | 11.5687 | 10.3339 | 8.9403 | 7.7234 | 6.5382 | -3.5829 | -15.3397 | -24.2071
|  | MARYTON | EE |  |  |  |  | 15.5026 | 15.1721 | 14.8226 | 14.5153 | 13.35 | 11.9953 | 10.6153 | 9.41 | 8.2258 | -1.1237 | -11.93 | -19.751 | 13.3853 | 13.0389 | 12.6653 | 12.3484 | 11.3853 | 10.2789 | 9.1558 | 8.1674 | 7.1832 | -1.6758 | -12.1674 | -20.681 | 13.9666 | 13.6024 | 13.2129 | 12.8803 | 11.7003 | 10.3339 | 8.9403 | 7.7234 | 6.5382 | -3.5829 | -15.3397 | -24.2071
|  | MARYTON | HT |  |  |  |  | 15.3395 | 14.9879 | 14.6184 | 14.2984 | 13.2595 | 12.2311 | 11.1921 | 9.9984 | 8.8258 | 0.37421 | -9.1458 | -15.6068 | 13.1989 | 12.8147 | 12.4116 | 12.0674 | 11.1811 | 10.3042 | 9.4232 | 8.4263 | 7.4663 | -1.2084 | -11.5505 | -18.6926 | 13.7845 | 13.3918 | 12.9792 | 12.6276 | 11.5687 | 10.5171 | 9.4592 | 8.2476 | 7.0666 | -2.3492 | -13.224 | -20.626
|  | MARYTON | HE |  |  |  |  | 15.7142 | 15.5205 | 15.2911 | 15.1047 | 13.9184 | 12.9111 | 11.8237 | 10.6311 | 9.0174 | 2.1111 | -6.2511 | -15.2605 | 13.6295 | 13.4053 | 13.1484 | 12.9453 | 11.9842 | 11.1621 | 10.24 | 9.1768 | 7.5789 | 0.89474 | -7.7105 | -16.8074 | 13.7845 | 13.3918 | 12.9792 | 12.6276 | 11.5687 | 10.5171 | 9.4592 | 8.2476 | 7.0666 | -2.3492 | -13.224 | -20.626
|  | MARYTON | CF |  |  |  |  | 15.7858 | 15.7332 | 15.6405 | 15.5374 | 15.07 | 14.6437 | 14.2205 | 13.6426 | 12.9132 | 9.4384 | 4.3279 | -1.2363 | 13.8116 | 13.6842 | 13.5463 | 13.4337 | 13.0442 | 12.6874 | 12.3295 | 11.7505 | 10.9389 | 7.3821 | 2.0705 | -3.8989 | 14.3771 | 14.2571 | 14.1224 | 14.0087 | 13.5339 | 13.0992 | 12.6676 | 12.0297 | 11.1813 | 7.2961 | 1.5108 | -4.8429
| STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | YES | 0 | 7.4 | 7.2263 | 7.0421 | 6.8884 | 6.2779 | 5.4695 | 4.5747 | 3.7768 | 2.7989 | -2.8347 | -9.7432 | -14.6137 | 6.9642 | 6.7811 | 6.5874 | 6.4284 | 5.9284 | 5.2547 | 4.5137 | 3.6432 | 2.7126 | -2.2916 | -8.8895 | -14.1337 | 7.1653 | 6.9758 | 6.7758 | 6.6105 | 6 | 5.1789 | 4.2621 | 3.3747 | 2.3095 | -3.5916 | -11.0621 | -16.5653
|  | MAUD | EE |  |  |  |  | 7.4958 | 7.3295 | 7.1526 | 6.9642 | 6.2779 | 5.4695 | 4.5747 | 3.7768 | 2.8705 | -2.8347 | -9.7432 | -14.6137 | 7.0705 | 6.9011 | 6.7189 | 6.5263 | 5.96 | 5.2821 | 4.5137 | 3.8211 | 3.0053 | -2.2916 | -8.8895 | -14.1337 | 7.2716 | 7.0916 | 6.9 | 6.6958 | 6 | 5.1789 | 4.2621 | 3.4421 | 2.4895 | -3.5916 | -11.0621 | -16.5653
|  | MAUD | HT |  |  |  |  | 7.4 | 7.2263 | 7.0421 | 6.8884 | 6.2905 | 5.5505 | 4.7979 | 3.8 | 2.7989 | -2.0063 | -7.9547 | -11.9137 | 6.9642 | 6.7811 | 6.5874 | 6.4284 | 5.9284 | 5.2547 | 4.5705 | 3.6432 | 2.7126 | -1.9905 | -8.3547 | -12.761 | 7.1653 | 6.9758 | 6.7758 | 6.6105 | 6.0011 | 5.2253 | 4.4347 | 3.3747 | 2.3095 | -2.9084 | -9.6316 | -14.1716
|  | MAUD | HE |  |  |  |  | 7.5979 | 7.5063 | 7.4042 | 7.2916 | 6.5411 | 5.9368 | 5.1821 | 4.4432 | 3.4284 | -0.92105 | -6.1168 | -11.7768 | 7.1811 | 7.0832 | 6.9726 | 6.8505 | 6.2253 | 5.7168 | 5.0389 | 4.3779 | 3.4053 | -0.70316 | -5.9011 | -11.5621 | 7.1653 | 6.9758 | 6.7758 | 6.6105 | 6.0011 | 5.2253 | 4.4347 | 3.3747 | 2.3095 | -2.9084 | -9.6316 | -14.1716
|  | MAUD | CF |  |  |  |  | 7.6579 | 7.6137 | 7.56 | 7.5011 | 7.2158 | 6.9484 | 6.6979 | 6.2695 | 5.8053 | 3.6116 | 0.33789 | -3.1674 | 7.2474 | 7.2021 | 7.1421 | 7.08 | 6.8389 | 6.6095 | 6.3937 | 5.9674 | 5.4779 | 3.3032 | 0.011579 | -3.6968 | 7.4484 | 7.4011 | 7.34 | 7.2758 | 6.9832 | 6.7084 | 6.4526 | 5.9821 | 5.46 | 3.0632 | -0.5421 | -4.4874
| DOUNREAY | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | YES | 0.06 | 0.93579 | 0.87895 | 0.68737 | 0.63158 | 0.35368 | -0.21474 | -0.83789 | -1.4347 | -2.3221 | -7.4221 | -13.519 | -18.1916 | 0.81684 | 0.76842 | 0.61368 | 0.56421 | 0.33368 | -0.18421 | -0.75895 | -1.3011 | -2.1789 | -6.9179 | -12.9874 | -18.179 | 0.82632 | 0.76737 | 0.57263 | 0.51579 | 0.23263 | -0.33053 | -0.90842 | -1.4074 | -2.1168 | -8.0842 | -14.7621 | -20.1684
|  | MELVICH | EE |  |  |  |  | 0.93579 | 0.87895 | 0.68737 | 0.63158 | 0.35368 | -0.20105 | -0.77158 | -1.2621 | -1.9421 | -7.4221 | -13.519 | -18.1916 | 0.81684 | 0.76842 | 0.61368 | 0.56421 | 0.33368 | -0.12316 | -0.59158 | -0.99684 | -1.5979 | -6.9179 | -12.9874 | -18.179 | 0.82632 | 0.76737 | 0.57263 | 0.51579 | 0.23263 | -0.33053 | -0.90842 | -1.4074 | -2.1168 | -8.0842 | -14.7621 | -20.1684
|  | MELVICH | HT |  |  |  |  | 0.96421 | 0.91579 | 0.86737 | 0.82 | 0.43789 | 0.41158 | 0.0084211 | -0.60947 | -1.6726 | -6.6021 | -12.2695 | -16.1821 | 0.83263 | 0.78737 | 0.74421 | 0.7 | 0.39474 | 0.36842 | 0.031579 | -0.51368 | -1.5611 | -6.6821 | -12.9726 | -17.4074 | 0.85368 | 0.80421 | 0.75263 | 0.70421 | 0.31684 | 0.29053 | -0.12105 | -0.76421 | -1.9326 | -7.4232 | -13.9589 | -18.48
|  | MELVICH | HE |  |  |  |  | 0.99789 | 0.98211 | 0.96316 | 0.94211 | 0.39474 | -0.21474 | -0.83789 | -1.4347 | -2.3221 | -6.0874 | -10.8105 | -15.9779 | 0.86842 | 0.85474 | 0.83579 | 0.81684 | 0.36421 | -0.18421 | -0.75895 | -1.3011 | -2.1789 | -5.8716 | -10.7705 | -16.1316 | 0.85368 | 0.80421 | 0.75263 | 0.70421 | 0.31684 | 0.29053 | -0.12105 | -0.76421 | -1.9326 | -7.4232 | -13.9589 | -18.48
|  | MELVICH | CF |  |  |  |  | 1.0063 | 0.99684 | 0.98632 | 0.97684 | 0.79263 | 0.62947 | 0.33368 | -0.048421 | -0.48 | -2.4221 | -5.3979 | -8.7263 | 0.87684 | 0.86842 | 0.85895 | 0.85158 | 0.70947 | 0.57474 | 0.3 | -0.095789 | -0.57158 | -2.5726 | -5.6863 | -9.3516 | 0.89789 | 0.88842 | 0.87789 | 0.86737 | 0.68 | 0.51474 | 0.19789 | -0.22842 | -0.71789 | -2.8695 | -6.2105 | -10.0432
| CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | YES | 0 | 22.0068 | 21.8426 | 21.6753 | 21.5037 | 21.3026 | 21.1068 | 20.9153 | 20.7268 | 20.5458 | 19.6332 | 18.5511 | 17.6984 | 19.9695 | 19.8063 | 19.6389 | 19.4684 | 19.2747 | 19.0863 | 18.9032 | 18.5516 | 18.2189 | 16.6579 | 15.4747 | 14.5316 | 21.5987 | 21.4345 | 21.1429 | 20.8461 | 20.5282 | 20.1924 | 19.8524 | 19.5018 | 19.1734 | 17.6461 | 16.4692 | 15.5376
|  | MENZIESHILL | EE |  |  |  |  | 22.1111 | 21.9816 | 21.8447 | 21.7037 | 21.5384 | 21.3774 | 21.2174 | 21.0658 | 20.9226 | 20.3205 | 19.5795 | 18.9447 | 20.0737 | 19.9442 | 19.8095 | 19.6684 | 19.5137 | 19.3642 | 19.2168 | 19.0768 | 18.8947 | 17.6263 | 16.6558 | 15.9611 | 21.7029 | 21.5734 | 21.4366 | 21.2092 | 20.9355 | 20.6734 | 20.3776 | 20.0987 | 19.825 | 18.5692 | 17.5882 | 16.8934
|  | MENZIESHILL | HT |  |  |  |  | 22.0068 | 21.8426 | 21.6753 | 21.5037 | 21.3026 | 21.1068 | 20.9153 | 20.7268 | 20.5458 | 19.6332 | 18.5511 | 17.6984 | 19.9695 | 19.8063 | 19.6389 | 19.4684 | 19.2747 | 19.0863 | 18.9032 | 18.5516 | 18.2189 | 16.6579 | 15.4747 | 14.5316 | 21.5987 | 21.4345 | 21.1429 | 20.8461 | 20.5282 | 20.1924 | 19.8524 | 19.5018 | 19.1734 | 17.6461 | 16.4692 | 15.5376
|  | MENZIESHILL | HE |  |  |  |  | 22.2226 | 22.1258 | 22.0216 | 21.9111 | 21.7732 | 21.6479 | 21.5237 | 21.4068 | 21.2984 | 20.8932 | 20.6574 | 20.4911 | 20.1853 | 20.0884 | 19.9853 | 19.8747 | 19.7463 | 19.6305 | 19.5158 | 19.4074 | 19.3084 | 18.8042 | 18.2179 | 17.8084 | 21.5987 | 21.4345 | 21.1429 | 20.8461 | 20.5282 | 20.1924 | 19.8524 | 19.5018 | 19.1734 | 17.6461 | 16.4692 | 15.5376
|  | MENZIESHILL | CF |  |  |  |  | 22.2953 | 22.2384 | 22.1784 | 22.1184 | 22.05 | 21.9816 | 21.9132 | 21.8458 | 21.7795 | 21.4837 | 21.3068 | 21.2089 | 20.2579 | 20.2011 | 20.1421 | 20.0821 | 20.0168 | 19.9526 | 19.8863 | 19.8221 | 19.7579 | 19.48 | 19.3253 | 19.1589 | 21.8871 | 21.8303 | 21.7703 | 21.7103 | 21.6429 | 21.5745 | 21.5061 | 21.4397 | 21.3734 | 20.8482 | 20.3976 | 20.0818
| KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 0.11 | 3.1321 | 3.0732 | 3.0142 | 2.9553 | 2.6026 | 2.1511 | 1.6447 | 1.1721 | -1.13 | -4.4311 | -7.5416 | -9.4374 | 2.8237 | 2.7279 | 2.6332 | 2.5384 | 2.2153 | 1.8332 | 1.3826 | 0.99 | -0.87421 | -3.73 | -6.6216 | -8.5679 | 2.9047 | 2.8132 | 2.7216 | 2.63 | 2.2374 | 1.7047 | 1.1574 | 0.68263 | -0.18579 | -4.5826 | -8.0489 | -9.9268
|  | METHLICK | EE |  |  |  |  | 3.1584 | 3.0995 | 3.0395 | 2.9784 | 2.6026 | 2.1511 | 1.6447 | 1.1721 | 1.0995 | -4.0732 | -7.5416 | -9.4342 | 2.8816 | 2.7953 | 2.7079 | 2.6205 | 2.2574 | 1.8332 | 1.3826 | 0.99 | 0.90895 | -3.4763 | -6.6216 | -8.5679 | 2.9553 | 2.8689 | 2.7805 | 2.6921 | 2.2374 | 1.7047 | 1.1574 | 0.68263 | 0.61211 | -4.5826 | -8.0489 | -9.9268
|  | METHLICK | HT |  |  |  |  | 3.1321 | 3.0732 | 3.0142 | 2.9553 | 2.6342 | 2.3132 | 1.9111 | 1.4089 | 1.3237 | -3.21 | -5.5468 | -6.9995 | 2.8237 | 2.7279 | 2.6332 | 2.5384 | 2.2153 | 1.8805 | 1.5437 | 1.11 | 1.0153 | -2.9205 | -5.2995 | -6.8311 | 2.9047 | 2.8132 | 2.7216 | 2.63 | 2.2374 | 1.8342 | 1.4279 | 0.92474 | 0.83947 | -3.7047 | -6.0058 | -7.3858
|  | METHLICK | HE |  |  |  |  | 3.1932 | 3.1658 | 3.1384 | 3.1068 | 2.7132 | 2.3784 | 2.0437 | 1.6489 | -1.13 | -4.4311 | -6.8405 | -9.4374 | 2.9553 | 2.9111 | 2.8647 | 2.8142 | 2.4468 | 2.1342 | 1.7605 | 1.3953 | -0.87421 | -3.73 | -5.9942 | -8.4405 | 2.9047 | 2.8132 | 2.7216 | 2.63 | 2.2374 | 1.8342 | 1.4279 | 0.92474 | 0.83947 | -3.7047 | -6.0058 | -7.3858
|  | METHLICK | CF |  |  |  |  | 3.2153 | 3.1995 | 3.1837 | 3.1689 | 3.0195 | 2.8879 | 2.7584 | 2.6447 | 0.31105 | -0.73 | -2.2184 | -3.6226 | 2.9942 | 2.9689 | 2.9426 | 2.9153 | 2.77 | 2.6395 | 2.5111 | 2.3374 | 0.34474 | -0.62789 | -2.0405 | -3.4532 | 3.0553 | 3.0311 | 3.0058 | 2.9805 | 2.7984 | 2.6363 | 2.4763 | 2.2911 | -0.18579 | -1.2247 | -2.71 | -4.1047
| SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | 0 | 1.1905 | 1.1632 | 1.1358 | 1.1084 | 1.0821 | 1.0558 | 1.0305 | 1.0053 | 0.98211 | 0.89053 | 0.81684 | 0.75263 | 1.0432 | 1.0126 | 0.98316 | 0.95474 | 0.92632 | 0.89895 | 0.87158 | 0.84526 | 0.82 | 0.72105 | 0.64 | 0.56842 | 1.1168 | 1.0863 | 1.0579 | 1.0295 | 1.0011 | 0.97368 | 0.94737 | 0.92105 | 0.89579 | 0.79789 | 0.71789 | 0.64737
|  | MID YELL | EE |  |  |  |  | 1.2084 | 1.1853 | 1.1642 | 1.1421 | 1.12 | 1.1 | 1.0789 | 1.06 | 1.0421 | 0.96316 | 0.90737 | 0.86211 | 1.0621 | 1.0379 | 1.0147 | 0.99158 | 0.96737 | 0.94737 | 0.92421 | 0.90421 | 0.88526 | 0.8 | 0.73895 | 0.68842 | 1.1358 | 1.1116 | 1.0895 | 1.0653 | 1.0421 | 1.0211 | 0.99895 | 0.97895 | 0.96105 | 0.87579 | 0.81579 | 0.76632
|  | MID YELL | HT |  |  |  |  | 1.1905 | 1.1632 | 1.1358 | 1.1084 | 1.0821 | 1.0558 | 1.0305 | 1.0053 | 0.98211 | 0.89053 | 0.81684 | 0.75263 | 1.0432 | 1.0126 | 0.98316 | 0.95474 | 0.92632 | 0.89895 | 0.87158 | 0.84526 | 0.82 | 0.72105 | 0.64 | 0.56842 | 1.1168 | 1.0863 | 1.0579 | 1.0295 | 1.0011 | 0.97368 | 0.94737 | 0.92105 | 0.89579 | 0.79789 | 0.71789 | 0.64737
|  | MID YELL | HE |  |  |  |  | 1.2347 | 1.2189 | 1.2053 | 1.1905 | 1.1747 | 1.1621 | 1.1463 | 1.1347 | 1.1232 | 1.0768 | 1.0495 | 1.0284 | 1.0905 | 1.0747 | 1.06 | 1.0442 | 1.0274 | 1.0137 | 0.99789 | 0.98526 | 0.97263 | 0.92421 | 0.89368 | 0.87053 | 1.1168 | 1.0863 | 1.0579 | 1.0295 | 1.0011 | 0.97368 | 0.94737 | 0.92105 | 0.89579 | 0.79789 | 0.71789 | 0.64737
|  | MID YELL | CF |  |  |  |  | 1.2474 | 1.2389 | 1.2305 | 1.2211 | 1.2137 | 1.2053 | 1.1958 | 1.1874 | 1.1789 | 1.1389 | 1.1147 | 1.0947 | 1.1042 | 1.0958 | 1.0863 | 1.0768 | 1.0684 | 1.0589 | 1.0495 | 1.04 | 1.0305 | 0.98842 | 0.96105 | 0.93895 | 1.1768 | 1.1684 | 1.16 | 1.1495 | 1.1411 | 1.1326 | 1.1232 | 1.1126 | 1.1042 | 1.0621 | 1.0347 | 1.0137
| KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 0 | 4.3495 | 4.1832 | 4.0032 | 6.6084 | 6.4568 | 5.7537 | 5.0147 | 4.3789 | 3.7295 | -2.1221 | -9.0126 | -14.2305 | 4.3579 | 4.1768 | 3.9789 | 6.1726 | 6.0105 | 5.4663 | 4.8537 | 4.3253 | 3.6463 | -1.9074 | -8.7905 | -14.3021 | 4.2295 | 4.0474 | 3.8484 | 6.2411 | 6.0768 | 5.3737 | 4.6284 | 3.9874 | 3.3337 | -3.0316 | -10.5411 | -16.4842
|  | MIDMAR | EE |  |  |  |  | 4.4337 | 4.2842 | 4.1221 | 6.7042 | 6.5189 | 5.7537 | 5.0147 | 4.3789 | 3.7295 | -2.1221 | -9.0126 | -14.2305 | 4.4516 | 4.2989 | 4.1284 | 6.2958 | 6.1116 | 5.4663 | 4.8537 | 4.3253 | 3.7863 | -1.88 | -8.6326 | -14.3021 | 4.3232 | 4.1621 | 3.9863 | 6.3495 | 6.1516 | 5.3737 | 4.6284 | 3.9874 | 3.3337 | -3.0316 | -10.5411 | -16.4842
|  | MIDMAR | HT |  |  |  |  | 4.3495 | 4.1832 | 4.0032 | 6.6084 | 6.4568 | 5.9789 | 5.4421 | 4.8105 | 3.9337 | -1.6516 | -7.9684 | -12.2632 | 4.3579 | 4.1768 | 3.9789 | 6.1726 | 6.0105 | 5.6074 | 5.1547 | 4.6221 | 3.7989 | -1.9074 | -8.7905 | -13.6253 | 4.2295 | 4.0474 | 3.8484 | 6.2411 | 6.0768 | 5.5916 | 5.0463 | 4.4074 | 3.4779 | -2.7284 | -9.9147 | -14.8621
|  | MIDMAR | HE |  |  |  |  | 4.9811 | 4.8926 | 4.7832 | 7.4095 | 6.7421 | 6.1768 | 5.5116 | 4.8189 | 3.8347 | -0.45053 | -5.76 | -11.5358 | 4.9042 | 4.8021 | 4.6768 | 6.8789 | 6.3389 | 5.8632 | 5.2632 | 4.6295 | 3.6463 | -0.50316 | -5.9137 | -11.8137 | 4.2295 | 4.0474 | 3.8484 | 6.2411 | 6.0768 | 5.5916 | 5.0463 | 4.4074 | 3.4779 | -2.7284 | -9.9147 | -14.8621
|  | MIDMAR | CF |  |  |  |  | 5.0484 | 5.0116 | 4.9611 | 7.6663 | 7.3937 | 7.16 | 6.9242 | 6.5042 | 6.0316 | 3.8137 | 0.46526 | -3.2326 | 4.9832 | 4.9432 | 4.8853 | 7.1832 | 6.9547 | 6.7547 | 6.5495 | 6.1074 | 5.5842 | 3.3379 | -0.10211 | -4.0916 | 4.9474 | 4.9126 | 4.8558 | 7.3558 | 7.0758 | 6.8358 | 6.5926 | 6.1274 | 5.5789 | 3.1326 | -0.58632 | -4.7789
| BRIDGE OF DUN | MILL RD | MINIMUM HEADROOM | NO 71317 57683 | NO | YES | 0.752 | 13.5975 | 13.488 | 13.2848 | 13.0669 | 12.7491 | 12.4333 | 12.1227 | 11.7933 | 11.4659 | 10.1333 | 9.0469 | 8.3048 | 12.0785 | 11.8838 | 11.6469 | 11.4112 | 11.0964 | 10.7859 | 10.4806 | 10.1596 | 9.8438 | 8.5322 | 7.4754 | 6.6291 | 12.5963 | 12.4931 | 12.3637 | 12.1247 | 11.7879 | 11.4531 | 11.1226 | 10.7752 | 10.4289 | 9.0016 | 7.8658 | 6.9784
|  | MILL RD | EE |  |  |  |  | 13.6617 | 13.5712 | 13.4775 | 13.3375 | 13.0427 | 12.7269 | 12.4101 | 12.1206 | 11.8312 | 10.3901 | 9.0469 | 8.3048 | 12.1722 | 12.0522 | 11.8985 | 11.7122 | 11.4312 | 11.1343 | 10.8375 | 10.5627 | 10.2891 | 8.9448 | 7.708 | 6.9564 | 12.6552 | 12.57 | 12.4816 | 12.3889 | 12.1216 | 11.7931 | 11.4616 | 11.1573 | 10.8542 | 9.3479 | 7.9405 | 7.1258
|  | MILL RD | HT |  |  |  |  | 13.5975 | 13.488 | 13.2848 | 13.0669 | 12.7491 | 12.4333 | 12.1227 | 11.7933 | 11.4659 | 10.1333 | 9.0964 | 8.3069 | 12.0785 | 11.8838 | 11.6469 | 11.4112 | 11.0964 | 10.7859 | 10.4806 | 10.1596 | 9.8438 | 8.5322 | 7.4754 | 6.6291 | 12.5963 | 12.4931 | 12.3637 | 12.1247 | 11.7879 | 11.4531 | 11.1226 | 10.7752 | 10.4289 | 9.0016 | 7.8658 | 6.9784
|  | MILL RD | HE |  |  |  |  | 13.7291 | 13.6648 | 13.5964 | 13.5227 | 13.3312 | 13.1638 | 12.9869 | 12.7669 | 12.5554 | 11.6227 | 10.8259 | 10.0438 | 12.2406 | 12.1764 | 12.1069 | 12.0354 | 11.8343 | 11.6491 | 11.448 | 11.2438 | 11.0501 | 10.1933 | 9.4659 | 8.7617 | 12.5963 | 12.4931 | 12.3637 | 12.1247 | 11.7879 | 11.4531 | 11.1226 | 10.7752 | 10.4289 | 9.0016 | 7.8658 | 6.9784
|  | MILL RD | CF |  |  |  |  | 13.7722 | 13.7322 | 13.6912 | 13.6491 | 13.5638 | 13.4827 | 13.4027 | 13.3291 | 13.2627 | 12.7733 | 12.228 | 11.8164 | 12.2838 | 12.2438 | 12.2027 | 12.1606 | 12.0975 | 12.0238 | 11.9227 | 11.8248 | 11.7364 | 11.2238 | 10.7133 | 10.3196 | 12.7573 | 12.7184 | 12.6794 | 12.6394 | 12.5584 | 12.4816 | 12.4058 | 12.3342 | 12.2721 | 11.8658 | 11.291 | 10.85
| ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 0.09 | 16.8916 | 39.9237 | 39.4342 | 38.9732 | 37.6153 | 36.3311 | 34.7605 | 33.3353 | 31.8784 | 20.5005 | 6.5416 | -3.6195 | 14.5279 | 36.8605 | 36.2489 | 35.7374 | 34.5795 | 33.47 | 32.3489 | 31.0774 | 29.9332 | 19.0279 | 5.3521 | -5.2447 | 15.4418 | 38.3984 | 37.7847 | 37.2668 | 35.8774 | 34.5637 | 33.0205 | 31.5626 | 30.0763 | 18.09 | 2.9237 | -8.6026
|  | MILNATHORT | EE |  |  |  |  | 17.1474 | 40.2689 | 39.8479 | 39.4689 | 38.0226 | 36.3911 | 34.7605 | 33.3353 | 31.8784 | 20.5005 | 6.5416 | -3.6195 | 14.8584 | 37.3216 | 36.8047 | 36.3605 | 35.1342 | 33.7479 | 32.39 | 31.1805 | 29.9332 | 19.3816 | 5.7816 | -5.2447 | 15.7671 | 38.8437 | 38.3174 | 37.8605 | 36.3584 | 34.6795 | 33.0205 | 31.5626 | 30.0763 | 18.09 | 2.9237 | -8.6026
|  | MILNATHORT | HT |  |  |  |  | 16.8916 | 39.9237 | 39.4342 | 38.9732 | 37.6153 | 36.3311 | 35.0405 | 33.5574 | 32.3374 | 21.2363 | 8.7911 | 0.41632 | 14.5279 | 36.8605 | 36.2489 | 35.7374 | 34.5795 | 33.47 | 32.3489 | 31.0774 | 30.2279 | 19.0279 | 5.3521 | -4.2047 | 15.4418 | 38.3984 | 37.7847 | 37.2668 | 35.8774 | 34.5637 | 33.2426 | 31.7268 | 30.69 | 18.5079 | 4.3184 | -5.4763
|  | MILNATHORT | HE |  |  |  |  | 17.4442 | 40.7058 | 40.43 | 40.1879 | 38.7574 | 37.5521 | 36.3668 | 35.0121 | 32.9711 | 23.8689 | 13.2889 | 1.8353 | 15.2395 | 37.8426 | 37.4784 | 37.1742 | 35.9984 | 34.9816 | 33.9921 | 32.7184 | 30.6805 | 21.7574 | 11.0574 | -0.64263 | 15.4418 | 38.3984 | 37.7847 | 37.2668 | 35.8774 | 34.5637 | 33.2426 | 31.7268 | 30.69 | 18.5079 | 4.3184 | -5.4763
|  | MILNATHORT | CF |  |  |  |  | 17.6642 | 41.0689 | 40.9268 | 40.7953 | 40.2258 | 39.71 | 39.1974 | 38.6342 | 37.8037 | 33.2637 | 26.5932 | 19.3921 | 15.5311 | 38.3416 | 38.1605 | 37.9921 | 37.5016 | 37.0405 | 36.5795 | 35.9879 | 34.9374 | 30.3647 | 23.51 | 15.6774 | 16.4345 | 39.8668 | 39.6826 | 39.5153 | 38.9226 | 38.3753 | 37.83 | 37.1647 | 36.0595 | 31.0858 | 23.7089 | 15.4995
| MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | YES | 0 | 18.2789 | 18.1789 | 18.0789 | 17.9758 | 18.2853 | 18.2411 | 18.1968 | 18.1526 | 18.1105 | 24.3284 | 23.7789 | 23.2242 | 16.3084 | 16.2095 | 16.0895 | 15.8968 | 16.3168 | 16.2758 | 16.2326 | 16.1916 | 16.1505 | 21.9811 | 21.2926 | 20.6779 | 17.1484 | 17.0484 | 16.9484 | 16.8453 | 17.1547 | 17.1105 | 17.0663 | 17.0232 | 16.98 | 22.3768 | 21.6442 | 21.0411
|  | MILTON OF CRAIGIE | EE |  |  |  |  | 18.34 | 18.2611 | 18.1779 | 18.0916 | 25.3179 | 25.2179 | 25.1189 | 25.0263 | 24.9368 | 24.5495 | 24.2937 | 23.9905 | 16.3695 | 16.2916 | 16.2084 | 16.0895 | 23.2726 | 23.1421 | 23.0253 | 22.9147 | 22.8116 | 22.3305 | 21.9863 | 21.5579 | 17.2095 | 17.1305 | 17.0474 | 16.9611 | 24.1874 | 24.0884 | 23.9895 | 23.8705 | 23.7179 | 22.9305 | 22.3158 | 21.8779
|  | MILTON OF CRAIGIE | HT |  |  |  |  | 18.2789 | 18.1789 | 18.0789 | 17.9758 | 25.1789 | 25.0589 | 24.9432 | 24.8274 | 24.7147 | 24.3284 | 23.7789 | 23.2242 | 16.3084 | 16.2095 | 16.0895 | 15.8968 | 23.0811 | 22.9421 | 22.8042 | 22.6705 | 22.5389 | 21.9811 | 21.2926 | 20.6779 | 17.1484 | 17.0484 | 16.9484 | 16.8453 | 24.0484 | 23.9295 | 23.7474 | 23.5568 | 23.3663 | 22.3768 | 21.6442 | 21.0411
|  | MILTON OF CRAIGIE | HE |  |  |  |  | 18.4011 | 18.3411 | 18.2758 | 18.2053 | 25.4453 | 25.3663 | 25.2895 | 25.2158 | 25.1484 | 24.9021 | 24.7526 | 24.6474 | 16.4305 | 16.3705 | 16.3053 | 16.2358 | 23.4526 | 23.3653 | 23.2789 | 23.1968 | 23.1189 | 22.8011 | 22.6053 | 22.4747 | 17.1484 | 17.0484 | 16.9484 | 16.8453 | 24.0484 | 23.9295 | 23.7474 | 23.5568 | 23.3663 | 22.3768 | 21.6442 | 21.0411
|  | MILTON OF CRAIGIE | CF |  |  |  |  | 18.4442 | 18.4074 | 18.3695 | 18.3295 | 18.2853 | 18.2411 | 18.1968 | 18.1526 | 18.1105 | 25.2453 | 25.1316 | 25.0695 | 16.4737 | 16.4368 | 16.3989 | 16.36 | 16.3168 | 16.2758 | 16.2326 | 16.1916 | 16.1505 | 23.2589 | 23.1042 | 23.0063 | 17.3137 | 17.2768 | 17.2389 | 17.1989 | 17.1547 | 17.1105 | 17.0663 | 17.0232 | 16.98 | 24.1168 | 24.0032 | 23.9421
| STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | YES | 0.086 | 12.3114 | 11.9882 | 11.6187 | 11.2145 | 10.5935 | 9.9387 | 9.2777 | 8.4745 | 7.7356 | 2.0145 | -1.0886 | -2.0539 | 12.1308 | 11.7603 | 11.3319 | 10.8603 | 10.2277 | 9.5477 | 8.8593 | 8.0182 | 7.2551 | 2.2119 | -0.69021 | -1.5807 | 11.6543 | 11.2964 | 10.8848 | 10.409 | 9.7164 | 8.9764 | 8.2279 | 7.3132 | 6.4764 | 0.44795 | -2.8552 | -3.8689
|  | MINTLAW | EE |  |  |  |  | 12.4451 | 12.1556 | 11.8229 | 11.4545 | 10.824 | 10.1398 | 9.4429 | 8.7882 | 8.0587 | 2.0145 | -1.0886 | -2.0539 | 12.2803 | 11.9519 | 11.5687 | 11.1414 | 10.5161 | 9.8477 | 9.1698 | 8.5161 | 7.7708 | 2.2119 | -0.69021 | -1.5807 | 11.7985 | 11.4774 | 11.1079 | 10.6837 | 9.9827 | 9.2269 | 8.4564 | 7.7258 | 6.9006 | 0.44795 | -2.8552 | -3.8689
|  | MINTLAW | HT |  |  |  |  | 12.3114 | 11.9882 | 11.6187 | 11.2145 | 10.5935 | 9.9387 | 9.2777 | 8.4745 | 7.7356 | 2.3829 | 0.25137 | -1.2013 | 12.1308 | 11.7603 | 11.3319 | 10.8603 | 10.2277 | 9.5477 | 8.8593 | 8.0182 | 7.2551 | 2.3129 | 0.10874 | -1.4618 | 11.6543 | 11.2964 | 10.8848 | 10.409 | 9.7164 | 8.9764 | 8.2279 | 7.3132 | 6.4764 | 0.74584 | -1.6194 | -3.2499
|  | MINTLAW | HE |  |  |  |  | 12.624 | 12.4061 | 12.1419 | 11.8345 | 11.224 | 10.6661 | 10.0766 | 9.4682 | 8.8208 | 4.7366 | 2.524 | 0.92189 | 12.4814 | 12.2256 | 11.9119 | 11.5466 | 10.9529 | 10.3961 | 9.7961 | 9.1719 | 8.4972 | 4.5508 | 2.414 | 1.0414 | 11.6543 | 11.2964 | 10.8848 | 10.409 | 9.7164 | 8.9764 | 8.2279 | 7.3132 | 6.4764 | 0.74584 | -1.6194 | -3.2499
|  | MINTLAW | CF |  |  |  |  | 12.8293 | 12.7177 | 12.5935 | 12.4545 | 12.2114 | 11.9661 | 11.7103 | 11.4587 | 11.2008 | 9.3861 | 8.0398 | 6.8524 | 12.7245 | 12.594 | 12.4477 | 12.2824 | 12.0445 | 11.7972 | 11.5361 | 11.2687 | 10.9814 | 8.9645 | 7.614 | 6.3508 | 12.1711 | 12.0974 | 11.9574 | 11.8006 | 11.5353 | 11.2669 | 10.9858 | 10.7058 | 10.4174 | 8.2806 | 6.7606 | 5.3837
| BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | YES | 0.001 | 16.0132 | 15.6122 | 15.1911 | 38.3169 | 37.9137 | 37.4022 | 36.9727 | 36.4274 | 35.8253 | 35.0632 | 34.3664 | 34.0716 | 14.9885 | 14.4148 | 13.8001 | 36.0264 | 35.4579 | 34.8948 | 34.4264 | 33.7453 | 33.0653 | 32.4095 | 31.7622 | 31.4516 | 15.4761 | 15.1435 | 14.4603 | 37.3106 | 36.7348 | 36.1622 | 35.6853 | 35.099 | 34.4548 | 33.5706 | 32.8443 | 32.5253
|  | MONTROSE NORTH | EE |  |  |  |  | 16.149 | 15.7953 | 15.4206 | 38.5748 | 38.1895 | 37.6327 | 37.0485 | 36.4769 | 35.9085 | 35.0632 | 34.3664 | 34.0716 | 15.1664 | 14.6579 | 14.1158 | 36.439 | 35.7927 | 35.1443 | 34.499 | 33.8622 | 33.2295 | 32.4095 | 31.7622 | 31.4516 | 15.5972 | 15.3045 | 14.8287 | 37.7232 | 37.0664 | 36.4053 | 35.7464 | 35.099 | 34.4548 | 33.5706 | 32.8443 | 32.5253
|  | MONTROSE NORTH | HT |  |  |  |  | 16.0132 | 15.6122 | 15.1911 | 38.3169 | 37.9137 | 37.4022 | 36.9727 | 36.539 | 36.1885 | 35.8443 | 34.7611 | 34.1832 | 14.9885 | 14.4148 | 13.8001 | 36.0264 | 35.4579 | 34.8948 | 34.4264 | 33.9569 | 33.5822 | 33.3158 | 32.2801 | 31.6379 | 15.4761 | 15.1435 | 14.4603 | 37.3106 | 36.7348 | 36.1622 | 35.6853 | 35.2043 | 34.8201 | 34.5127 | 33.3664 | 32.7232
|  | MONTROSE NORTH | HE |  |  |  |  | 16.2406 | 15.9332 | 15.5974 | 38.7853 | 38.3822 | 37.8032 | 37.1137 | 36.4274 | 35.8253 | 35.2611 | 34.8664 | 34.5516 | 15.2622 | 14.8106 | 14.3127 | 36.6979 | 35.9937 | 35.3022 | 34.5222 | 33.7453 | 33.0653 | 32.5179 | 32.1443 | 31.8601 | 15.4761 | 15.1435 | 14.4603 | 37.3106 | 36.7348 | 36.1622 | 35.6853 | 35.2043 | 34.8201 | 34.5127 | 33.3664 | 32.7232
|  | MONTROSE NORTH | CF |  |  |  |  | 16.4153 | 16.3364 | 16.2637 | 39.7558 | 39.6811 | 39.5685 | 39.439 | 39.3116 | 39.1853 | 38.7401 | 38.3716 | 38.0106 | 15.5095 | 15.4074 | 15.3158 | 38.2495 | 38.1716 | 38.0337 | 37.8674 | 37.7043 | 37.5348 | 37.0095 | 36.5495 | 35.9327 | 15.8329 | 15.7635 | 15.6982 | 39.2706 | 39.2011 | 39.1032 | 38.9937 | 38.8843 | 38.7779 | 38.3411 | 37.7779 | 37.1422
| TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | YES | 0 | 2.8221 | 2.6284 | 2.4516 | 7.5232 | 6.8568 | 6.2442 | 5.6137 | 4.86 | 3.8179 | -1.2263 | -10.0916 | -15.0137 | 2.1516 | 1.9442 | 1.7558 | 6.8147 | 6.24 | 5.7379 | 5.2158 | 4.5958 | 3.6189 | -1.22 | -9.22 | -14.4526 | 2.1537 | 1.94 | 1.7432 | 6.7937 | 6.0979 | 5.4779 | 4.8463 | 4.0947 | 3.1432 | -2.4221 | -11.8505 | -17.3874
|  | MOSSAT | EE |  |  |  |  | 2.9179 | 2.7253 | 2.5463 | 7.6158 | 7.4116 | 6.7011 | 5.8105 | 5.04 | 4.2495 | -1.2263 | -10.0916 | -15.0137 | 2.2589 | 2.0589 | 1.8737 | 6.9347 | 6.72 | 6.1189 | 5.3979 | 4.7705 | 4.1263 | -1.0674 | -9.22 | -14.4526 | 2.2621 | 2.0484 | 1.8516 | 6.9021 | 6.6758 | 5.94 | 5.0463 | 4.2811 | 3.4937 | -2.4221 | -11.8505 | -17.3874
|  | MOSSAT | HT |  |  |  |  | 2.8221 | 2.6284 | 2.4516 | 7.5232 | 6.8568 | 6.2442 | 5.6137 | 4.86 | 3.9453 | -0.97263 | -8.5084 | -12.4621 | 2.1516 | 1.9442 | 1.7558 | 6.8147 | 6.24 | 5.7379 | 5.2158 | 4.5958 | 3.7874 | -1.22 | -8.7958 | -13.1453 | 2.1537 | 1.94 | 1.7432 | 6.7937 | 6.0979 | 5.4779 | 4.8463 | 4.0947 | 3.1432 | -2.3126 | -10.6116 | -15.1379
|  | MOSSAT | HE |  |  |  |  | 3.0074 | 2.8926 | 2.7579 | 7.8632 | 7.0368 | 6.3074 | 5.6579 | 4.8716 | 3.8179 | -0.23263 | -6.4232 | -12.341 | 2.3589 | 2.2305 | 2.08 | 7.1674 | 6.4716 | 5.8526 | 5.3253 | 4.6316 | 3.6189 | -0.23053 | -6.1832 | -12.0305 | 2.1537 | 1.94 | 1.7432 | 6.7937 | 6.0979 | 5.4779 | 4.8463 | 4.0947 | 3.1432 | -2.3126 | -10.6116 | -15.1379
|  | MOSSAT | CF |  |  |  |  | 3.0558 | 3.0189 | 2.9505 | 8.1368 | 7.8189 | 7.5221 | 7.2242 | 6.8537 | 6.3916 | 4.2389 | 0.82632 | -2.7611 | 2.4126 | 2.3726 | 2.2979 | 7.4768 | 7.2053 | 6.9516 | 6.6926 | 6.3326 | 5.8421 | 3.7105 | 0.32526 | -3.4263 | 2.4147 | 2.3726 | 2.2968 | 7.4737 | 7.1421 | 6.8358 | 6.5284 | 6.1221 | 5.5989 | 3.2463 | -0.49158 | -4.5126
| THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | YES | 0.45 | 15.3926 | 15.2558 | 15.0789 | 14.7463 | 14.5158 | 14.3137 | 14.0042 | 13.6789 | 13.4316 | 12.4032 | 11.5011 | 10.8421 | 13.8942 | 13.5437 | 13.1374 | 12.7268 | 12.4974 | 12.3174 | 11.9974 | 11.6689 | 11.43 | 10.4205 | 9.6426 | 8.9953 | 14.3366 | 13.9892 | 13.5861 | 13.1776 | 12.925 | 12.7176 | 12.3955 | 12.0461 | 11.7829 | 10.6871 | 9.7661 | 9.0524
|  | MOUNT PLEASANT | EE |  |  |  |  | 15.4474 | 15.3253 | 15.1937 | 14.9389 | 14.5158 | 14.3137 | 14.1095 | 13.9274 | 13.7379 | 12.5326 | 11.5011 | 10.8421 | 13.9689 | 13.6963 | 13.3363 | 12.9553 | 12.4974 | 12.3174 | 12.1374 | 11.9742 | 11.8026 | 10.6626 | 9.7258 | 9.0521 | 14.4134 | 14.1387 | 13.7818 | 13.4029 | 12.925 | 12.7176 | 12.5071 | 12.3197 | 12.1229 | 10.8482 | 9.7661 | 9.0524
|  | MOUNT PLEASANT | HT |  |  |  |  | 15.3926 | 15.2558 | 15.0789 | 14.7463 | 14.5453 | 14.3474 | 14.0042 | 13.6789 | 13.4316 | 12.4032 | 11.6284 | 11.0189 | 13.8942 | 13.5437 | 13.1374 | 12.7268 | 12.5384 | 12.3521 | 11.9974 | 11.6689 | 11.43 | 10.4205 | 9.6426 | 8.9953 | 14.3366 | 13.9892 | 13.5861 | 13.1776 | 12.9713 | 12.7661 | 12.3955 | 12.0461 | 11.7829 | 10.6871 | 9.8576 | 9.1945
|  | MOUNT PLEASANT | HE |  |  |  |  | 15.5232 | 15.4326 | 15.3295 | 15.1263 | 14.8674 | 14.5516 | 14.2305 | 13.9137 | 13.6011 | 12.9274 | 12.3926 | 11.7853 | 14.0426 | 13.8216 | 13.5016 | 13.15 | 12.8858 | 12.5521 | 12.2184 | 11.89 | 11.5658 | 10.9563 | 10.4963 | 9.9532 | 14.3366 | 13.9892 | 13.5861 | 13.1776 | 12.9713 | 12.7661 | 12.3955 | 12.0461 | 11.7829 | 10.6871 | 9.8576 | 9.1945
|  | MOUNT PLEASANT | CF |  |  |  |  | 15.5895 | 15.5505 | 15.5126 | 15.4726 | 15.3958 | 15.32 | 15.2442 | 15.1737 | 15.1084 | 14.6642 | 14.2726 | 13.6432 | 14.09 | 14.0574 | 14.0237 | 13.9879 | 13.9353 | 13.8353 | 13.7037 | 13.5795 | 13.4542 | 12.7911 | 12.4216 | 11.7047 | 14.5345 | 14.5008 | 14.4671 | 14.4313 | 14.3639 | 14.2587 | 14.1208 | 13.9903 | 13.8608 | 13.1639 | 12.7408 | 11.9934
| BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | YES | 0 | 21.7442 | 21.4242 | 21.1 | 20.7726 | 19.4126 | 18.0621 | 16.7242 | 15.4979 | 14.2779 | 11.5989 | 8.78 | 7.3074 | 21.6 | 21.2495 | 20.8947 | 20.5379 | 19.0221 | 17.5168 | 16.0295 | 14.7379 | 13.4589 | 11.2211 | 8.9053 | 7.4747 | 21.5316 | 21.1863 | 20.8347 | 20.4811 | 18.9516 | 17.3842 | 15.8295 | 14.4737 | 13.1274 | 10.4116 | 7.5084 | 5.9221
|  | MUIR OF ORD | EE |  |  |  |  | 21.9305 | 21.66 | 21.3779 | 21.0905 | 20.48 | 19.8053 | 18.3968 | 17.0758 | 15.7432 | 11.5989 | 8.78 | 7.3074 | 21.8074 | 21.5179 | 21.2137 | 20.9042 | 20.3421 | 19.7368 | 18.2211 | 16.7832 | 15.3347 | 11.3263 | 8.9053 | 7.4747 | 21.7347 | 21.4442 | 21.1389 | 20.8284 | 20.1958 | 19.4979 | 17.9305 | 16.4211 | 14.8821 | 10.4116 | 7.5084 | 5.9221
|  | MUIR OF ORD | HT |  |  |  |  | 21.7442 | 21.4242 | 21.1 | 20.7726 | 19.4126 | 18.0621 | 16.7242 | 15.4979 | 14.2779 | 11.8232 | 10.1305 | 8.4042 | 21.6 | 21.2495 | 20.8947 | 20.5379 | 19.0221 | 17.5168 | 16.0295 | 14.7379 | 13.4589 | 11.2211 | 9.6168 | 7.7442 | 21.5316 | 21.1863 | 20.8347 | 20.4811 | 18.9516 | 17.3842 | 15.8295 | 14.4737 | 13.1274 | 10.5579 | 8.7674 | 6.8389
|  | MUIR OF ORD | HE |  |  |  |  | 22.1032 | 22.0095 | 21.8326 | 21.6379 | 21.0611 | 20.5589 | 19.8137 | 19.0958 | 18.3695 | 15.5779 | 13.1663 | 9.6663 | 22.0905 | 21.9042 | 21.7032 | 21.4895 | 20.9747 | 20.5242 | 19.7684 | 19.0442 | 18.3095 | 15.5937 | 13.2674 | 9.6737 | 21.5316 | 21.1863 | 20.8347 | 20.4811 | 18.9516 | 17.3842 | 15.8295 | 14.4737 | 13.1274 | 10.5579 | 8.7674 | 6.8389
|  | MUIR OF ORD | CF |  |  |  |  | 22.1874 | 22.1358 | 22.0842 | 22.0295 | 21.78 | 21.5474 | 21.3379 | 21.0021 | 20.6842 | 19.0789 | 17.4768 | 15.3358 | 22.2684 | 22.1547 | 22.0389 | 21.92 | 21.6884 | 21.4695 | 21.2779 | 20.92 | 20.5695 | 18.9011 | 17.3158 | 14.94 | 22.1821 | 22.0747 | 21.9589 | 21.8411 | 21.5821 | 21.3379 | 21.1211 | 20.7505 | 20.3958 | 18.64 | 16.8937 | 14.3821
| BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | YES | 0 | 3.0694 | 2.9578 | 2.8715 | 2.7873 | 2.5557 | 2.3262 | 2.0904 | 1.8809 | 1.6788 | 0.68305 | -0.32958 | -0.72958 | 2.8578 | 2.7262 | 2.6283 | 2.5346 | 2.2999 | 2.0683 | 1.8273 | 1.642 | 1.4652 | 0.70095 | -0.15695 | -0.53274 | 2.9515 | 2.8273 | 2.7346 | 2.6441 | 2.3925 | 2.1378 | 1.8725 | 1.6536 | 1.4431 | 0.44305 | -0.60642 | -1.0422
|  | MUIREND | EE |  |  |  |  | 3.1231 | 3.0273 | 2.9515 | 2.8788 | 2.6841 | 2.4652 | 2.1988 | 1.9578 | 1.7083 | 0.68305 | -0.32958 | -0.72958 | 2.922 | 2.8094 | 2.7283 | 2.6483 | 2.4788 | 2.2915 | 2.0409 | 1.8104 | 1.5683 | 0.70095 | -0.15695 | -0.53274 | 3.0104 | 2.9041 | 2.8231 | 2.7452 | 2.5462 | 2.3209 | 2.0378 | 1.7799 | 1.5041 | 0.44305 | -0.60642 | -1.0422
|  | MUIREND | HT |  |  |  |  | 3.0694 | 2.9578 | 2.8715 | 2.7873 | 2.5557 | 2.3262 | 2.0904 | 1.8809 | 1.6788 | 0.85989 | 0.30937 | -0.004316 | 2.8578 | 2.7262 | 2.6283 | 2.5346 | 2.2999 | 2.0683 | 1.8273 | 1.642 | 1.4652 | 0.71463 | 0.19042 | -0.14011 | 2.9515 | 2.8273 | 2.7346 | 2.6441 | 2.3925 | 2.1378 | 1.8725 | 1.6536 | 1.4431 | 0.56832 | -0.029579 | -0.38958
|  | MUIREND | HE |  |  |  |  | 3.1978 | 3.1325 | 3.0883 | 3.0441 | 2.8578 | 2.6978 | 2.5062 | 2.3188 | 2.1378 | 1.4157 | 0.82621 | 0.21674 | 3.0115 | 2.9325 | 2.8831 | 2.8346 | 2.6788 | 2.5452 | 2.3673 | 2.1915 | 2.0252 | 1.4083 | 0.92937 | 0.43463 | 2.9515 | 2.8273 | 2.7346 | 2.6441 | 2.3925 | 2.1378 | 1.8725 | 1.6536 | 1.4431 | 0.56832 | -0.029579 | -0.38958
|  | MUIREND | CF |  |  |  |  | 3.2567 | 3.2167 | 3.1873 | 3.1609 | 3.0831 | 3.0115 | 2.9399 | 2.8588 | 2.7915 | 2.4188 | 2.042 | 1.7736 | 3.0841 | 3.0357 | 2.9988 | 2.9694 | 2.9009 | 2.8378 | 2.7736 | 2.6915 | 2.6199 | 2.2662 | 1.9536 | 1.7273 | 3.1588 | 3.1136 | 3.0809 | 3.0525 | 2.9704 | 2.8967 | 2.8241 | 2.7357 | 2.6631 | 2.2694 | 1.8809 | 1.6031
| NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 0.707 | 16.1956 | 15.8314 | 15.3893 | 14.8883 | 13.9219 | 12.9483 | 11.9546 | 10.9588 | 10.0251 | 8.0156 | 6.5262 | 5.4251 | 14.1225 | 13.6383 | 13.1362 | 12.5604 | 11.4541 | 10.3667 | 9.2919 | 8.2225 | 7.2246 | 5.2056 | 3.6772 | 2.4983 | 14.728 | 14.2596 | 13.7743 | 13.2185 | 12.1333 | 11.0659 | 9.9838 | 8.8733 | 7.8364 | 5.6838 | 4.0691 | 2.8522
|  | NAIRN CENTRAL | EE |  |  |  |  | 16.3146 | 16.1304 | 15.7504 | 15.3072 | 14.703 | 14.0809 | 13.1462 | 12.2167 | 11.3346 | 8.6746 | 6.8956 | 5.9051 | 14.3814 | 13.9751 | 13.5467 | 13.0362 | 12.3941 | 11.7414 | 10.6951 | 9.6793 | 8.7372 | 6.0677 | 4.3962 | 3.3877 | 14.9785 | 14.5848 | 14.168 | 13.6754 | 13.0185 | 12.3459 | 11.3006 | 10.2922 | 9.3238 | 6.4522 | 4.5754 | 3.4985
|  | NAIRN CENTRAL | HT |  |  |  |  | 16.1956 | 15.8314 | 15.3893 | 14.8883 | 13.9219 | 12.9483 | 11.9546 | 10.9588 | 10.0251 | 8.0156 | 6.5262 | 5.4251 | 14.1225 | 13.6383 | 13.1362 | 12.5604 | 11.4541 | 10.3667 | 9.2919 | 8.2225 | 7.2246 | 5.2056 | 3.6772 | 2.4983 | 14.728 | 14.2596 | 13.7743 | 13.2185 | 12.1333 | 11.0659 | 9.9838 | 8.8733 | 7.8364 | 5.6838 | 4.0691 | 2.8522
|  | NAIRN CENTRAL | HE |  |  |  |  | 16.4725 | 16.3577 | 16.2356 | 15.9125 | 15.3725 | 14.8788 | 14.2988 | 13.7272 | 13.2209 | 11.6072 | 10.223 | 8.8619 | 14.7288 | 14.4372 | 14.1172 | 13.7098 | 13.1446 | 12.6204 | 11.9867 | 11.3614 | 10.8151 | 9.1972 | 7.8288 | 6.4909 | 14.728 | 14.2596 | 13.7743 | 13.2185 | 12.1333 | 11.0659 | 9.9838 | 8.8733 | 7.8364 | 5.6838 | 4.0691 | 2.8522
|  | NAIRN CENTRAL | CF |  |  |  |  | 16.5735 | 16.5104 | 16.4462 | 16.3819 | 16.2651 | 16.1125 | 15.8588 | 15.5546 | 15.2809 | 14.263 | 13.3398 | 12.5967 | 15.0141 | 14.9014 | 14.7225 | 14.5172 | 14.2519 | 13.9814 | 13.7025 | 13.3583 | 13.0446 | 11.9562 | 10.9993 | 10.2035 | 15.5406 | 15.4775 | 15.3069 | 15.1101 | 14.8385 | 14.5659 | 14.2859 | 13.9459 | 13.6385 | 12.5291 | 11.5227 | 10.7006
| STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | YES | 0 | 5.0705 | 5.0326 | 4.9937 | 4.9537 | 4.8463 | 4.7347 | 4.6 | 4.4821 | 4.3642 | 2.1147 | 0.77579 | -0.86842 | 5.0632 | 5.0263 | 4.9884 | 4.9495 | 4.8789 | 4.8 | 4.6221 | 4.3989 | 4.1242 | 2.04 | 0.78842 | -0.88526 | 4.9274 | 4.8674 | 4.8042 | 4.7326 | 4.5916 | 4.4084 | 4.2158 | 3.9747 | 3.6853 | 2.8821 | -0.075789 | -2.5053
|  | NEW PITSLIGO | EE |  |  |  |  | 5.0905 | 5.0568 | 5.0211 | 4.9842 | 4.8684 | 4.7347 | 4.6 | 4.4821 | 4.3642 | 3.8632 | 1.32 | -0.86842 | 5.0842 | 5.0526 | 5.02 | 4.9863 | 4.9168 | 4.8389 | 4.7316 | 4.5716 | 4.3968 | 3.4547 | 1.0789 | -0.88526 | 4.9642 | 4.9126 | 4.8589 | 4.8042 | 4.6547 | 4.4832 | 4.2874 | 4.1053 | 3.9095 | 2.8821 | -0.075789 | -2.5053
|  | NEW PITSLIGO | HT |  |  |  |  | 5.0705 | 5.0326 | 4.9937 | 4.9537 | 4.8463 | 4.74 | 4.6337 | 4.5137 | 4.3926 | 4.0432 | 1.8358 | -0.33263 | 5.0632 | 5.0263 | 4.9884 | 4.9495 | 4.8789 | 4.8 | 4.6221 | 4.3989 | 4.1242 | 3.5084 | 1.4211 | -0.50105 | 4.9274 | 4.8674 | 4.8042 | 4.7326 | 4.5916 | 4.4084 | 4.2158 | 3.9747 | 3.6853 | 3.0211 | 0.40737 | -1.9579
|  | NEW PITSLIGO | HE |  |  |  |  | 5.1189 | 5.0989 | 5.0779 | 5.0537 | 4.9368 | 4.8389 | 4.7411 | 4.6442 | 4.5495 | 2.1147 | 0.77579 | -0.53474 | 5.1126 | 5.0937 | 5.0726 | 5.0484 | 4.9832 | 4.9263 | 4.8684 | 4.7316 | 4.5232 | 2.04 | 0.78842 | -0.45263 | 4.9274 | 4.8674 | 4.8042 | 4.7326 | 4.5916 | 4.4084 | 4.2158 | 3.9747 | 3.6853 | 3.0211 | 0.40737 | -1.9579
|  | NEW PITSLIGO | CF |  |  |  |  | 5.1368 | 5.1263 | 5.1147 | 5.1032 | 5.0579 | 5.0168 | 4.9758 | 4.94 | 4.9116 | 4.7221 | 4.4989 | 4.3442 | 5.1305 | 5.1211 | 5.1095 | 5.0989 | 5.0726 | 5.0474 | 5.0232 | 5.0011 | 4.9811 | 4.6347 | 4.4032 | 4.2326 | 5.0179 | 5.0074 | 4.9947 | 4.9842 | 4.9295 | 4.8768 | 4.8242 | 4.7779 | 4.7263 | 4.2158 | 3.9274 | 3.72
| DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0 | 0.32632 | 0.32105 | 0.31474 | 0.30947 | 0.29684 | 0.28105 | 0.26737 | 0.25368 | 0.23895 | 0.17263 | 0.11263 | 0.063158 | 0.30842 | 0.30316 | 0.29895 | 0.29053 | 0.27895 | 0.26737 | 0.25789 | 0.24526 | 0.23368 | 0.17895 | 0.12632 | 0.082105 | 0.31789 | 0.31053 | 0.30316 | 0.29474 | 0.27789 | 0.26316 | 0.24737 | 0.23263 | 0.21789 | 0.14737 | 0.08421 | 0.028421
|  | NEWTON | EE |  |  |  |  | 0.32737 | 0.32105 | 0.31474 | 0.30947 | 0.29684 | 0.28105 | 0.26737 | 0.25368 | 0.23895 | 0.17263 | 0.11263 | 0.063158 | 0.31053 | 0.30526 | 0.30105 | 0.29368 | 0.28105 | 0.26947 | 0.25789 | 0.24632 | 0.23368 | 0.17895 | 0.12632 | 0.082105 | 0.31789 | 0.31053 | 0.30316 | 0.29474 | 0.27789 | 0.26316 | 0.24737 | 0.23263 | 0.21789 | 0.14737 | 0.08421 | 0.028421
|  | NEWTON | HT |  |  |  |  | 0.32632 | 0.32105 | 0.31579 | 0.31053 | 0.29789 | 0.28737 | 0.27684 | 0.26316 | 0.25053 | 0.20105 | 0.16526 | 0.12842 | 0.30842 | 0.30316 | 0.29895 | 0.29053 | 0.27895 | 0.26737 | 0.25789 | 0.24526 | 0.23474 | 0.19053 | 0.15789 | 0.12105 | 0.31789 | 0.31263 | 0.30316 | 0.29474 | 0.28105 | 0.26842 | 0.25684 | 0.24421 | 0.22947 | 0.17789 | 0.14 | 0.1
|  | NEWTON | HE |  |  |  |  | 0.33263 | 0.32947 | 0.32632 | 0.32316 | 0.31474 | 0.30737 | 0.3 | 0.29263 | 0.28526 | 0.24842 | 0.20421 | 0.15474 | 0.31579 | 0.31263 | 0.30947 | 0.30632 | 0.3 | 0.29579 | 0.29158 | 0.28211 | 0.27474 | 0.24211 | 0.2 | 0.15579 | 0.31789 | 0.31263 | 0.30316 | 0.29474 | 0.28105 | 0.26842 | 0.25684 | 0.24421 | 0.22947 | 0.17789 | 0.14 | 0.1
|  | NEWTON | CF |  |  |  |  | 0.33579 | 0.33474 | 0.33368 | 0.33053 | 0.32737 | 0.32421 | 0.32211 | 0.32 | 0.31579 | 0.30316 | 0.28211 | 0.25684 | 0.31789 | 0.31684 | 0.31579 | 0.31368 | 0.31158 | 0.30842 | 0.30632 | 0.30421 | 0.30316 | 0.29053 | 0.26526 | 0.24 | 0.32737 | 0.32526 | 0.32421 | 0.32211 | 0.31895 | 0.31474 | 0.31263 | 0.31053 | 0.30842 | 0.29158 | 0.26421 | 0.23474
| REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | YES | 0.3 | 15.4353 | 15.2489 | 29.3526 | 28.5747 | 27.4768 | 26.3916 | 25.3137 | 24.2705 | 23.2316 | 12.7874 | 5.3884 | 4.2232 | 13.5842 | 12.9642 | 26.0695 | 25.1958 | 24.0326 | 22.8842 | 21.7432 | 20.6611 | 19.5853 | 8.0358 | 0.38632 | -0.73579 | 14.4066 | 13.8171 | 27.2921 | 26.4132 | 25.1963 | 23.9932 | 22.7984 | 21.6489 | 20.5079 | 8.5784 | 0.29211 | -0.95316
|  | NEWTONHILL | EE |  |  |  |  | 15.5416 | 15.3847 | 29.6779 | 28.9495 | 27.8642 | 26.7316 | 25.6032 | 24.6074 | 23.6147 | 12.7874 | 5.3884 | 4.2232 | 13.8126 | 13.2579 | 26.4274 | 25.6084 | 24.4737 | 23.3042 | 22.1432 | 21.1179 | 20.0958 | 8.2768 | 0.38632 | -0.73579 | 14.5203 | 14.1087 | 27.6479 | 26.8205 | 25.6195 | 24.3732 | 23.1311 | 22.0363 | 20.9437 | 8.6321 | 0.29211 | -0.95316
|  | NEWTONHILL | HT |  |  |  |  | 15.4353 | 15.2489 | 29.3526 | 28.5747 | 27.4768 | 26.3916 | 25.3137 | 24.2705 | 23.2316 | 12.8063 | 6.2621 | 5.1368 | 13.5842 | 12.9642 | 26.0695 | 25.1958 | 24.0326 | 22.8842 | 21.7432 | 20.6611 | 19.5853 | 8.0358 | 0.74632 | -0.42105 | 14.4066 | 13.8171 | 27.2921 | 26.4132 | 25.1963 | 23.9932 | 22.7984 | 21.6489 | 20.5079 | 8.5784 | 1.0711 | -0.16053
|  | NEWTONHILL | HE |  |  |  |  | 15.6858 | 15.5879 | 30.0316 | 29.4695 | 28.4958 | 27.5221 | 26.5558 | 25.6695 | 24.8011 | 14.84 | 8.4232 | 6.9832 | 14.0221 | 13.6474 | 26.8958 | 26.1505 | 25.1484 | 24.1263 | 23.1116 | 22.1884 | 21.2842 | 10.2568 | 3.2337 | 2.0074 | 14.4066 | 13.8171 | 27.2921 | 26.4132 | 25.1963 | 23.9932 | 22.7984 | 21.6489 | 20.5079 | 8.5784 | 1.0711 | -0.16053
|  | NEWTONHILL | CF |  |  |  |  | 15.7742 | 15.7205 | 30.2168 | 30.1611 | 30.0116 | 29.6863 | 29.2168 | 28.7779 | 28.3421 | 22.3126 | 18.2495 | 17.58 | 14.2737 | 14.1642 | 27.7137 | 27.3884 | 26.9347 | 26.4621 | 25.96 | 25.4874 | 25.0105 | 18.2274 | 13.8084 | 13.2116 | 14.7666 | 14.7097 | 28.8195 | 28.6184 | 28.1374 | 27.6416 | 27.1163 | 26.6247 | 26.1332 | 19.2068 | 14.5668 | 13.8689
| ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | YES | 0 | 1.2884 | 1.2884 | 1.2884 | 1.2874 | 1.2863 | 1.2863 | 1.2863 | 1.2853 | 1.2842 | 1.2821 | 1.2789 | 1.2768 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1747 | 1.1747 | 1.1747 | 1.1747
|  | NIGG | EE |  |  |  |  | 1.2895 | 1.2884 | 1.2884 | 1.2884 | 1.2874 | 1.2874 | 1.2863 | 1.2863 | 1.2863 | 1.2842 | 1.2821 | 1.28 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1747 | 1.1747 | 1.1747
|  | NIGG | HT |  |  |  |  | 1.2884 | 1.2884 | 1.2884 | 1.2874 | 1.2863 | 1.2863 | 1.2863 | 1.2853 | 1.2842 | 1.2821 | 1.2789 | 1.2768 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1747 | 1.1747 | 1.1747 | 1.1747
|  | NIGG | HE |  |  |  |  | 1.2895 | 1.2895 | 1.2895 | 1.2884 | 1.2884 | 1.2884 | 1.2884 | 1.2884 | 1.2884 | 1.2863 | 1.2863 | 1.2842 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1747 | 1.1747 | 1.1747 | 1.1747
|  | NIGG | CF |  |  |  |  | 1.2895 | 1.2895 | 1.2895 | 1.2895 | 1.2895 | 1.2895 | 1.2884 | 1.2884 | 1.2884 | 1.2884 | 1.2863 | 1.2863 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758
| CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | YES | 0.85 | 15.7674 | 15.5042 | 15.1842 | 14.6211 | 14.54 | 14.4642 | 14.3863 | 14.3147 | 14.2358 | 13.8558 | 13.4358 | 13.0874 | 14.5542 | 14.3711 | 14.0447 | 13.4595 | 13.3847 | 13.3132 | 13.2416 | 13.1753 | 13.1005 | 12.7111 | 12.2721 | 11.9016 | 14.9692 | 14.8608 | 14.5071 | 13.8682 | 13.7861 | 13.7092 | 13.6303 | 13.5587 | 13.4766 | 13.0892 | 12.6576 | 12.2787
|  | NINEWELLS | EE |  |  |  |  | 15.8495 | 15.6084 | 15.3105 | 14.6211 | 14.54 | 14.4642 | 14.3863 | 14.3147 | 14.2358 | 13.86 | 13.5684 | 13.3463 | 14.5984 | 14.4816 | 14.1826 | 13.4595 | 13.3847 | 13.3132 | 13.2416 | 13.1753 | 13.1005 | 12.7447 | 12.47 | 12.2521 | 15.0092 | 14.9439 | 14.6418 | 13.8682 | 13.7861 | 13.7092 | 13.6303 | 13.5587 | 13.4766 | 13.0892 | 12.7861 | 12.5461
|  | NINEWELLS | HT |  |  |  |  | 15.7674 | 15.5042 | 15.1842 | 15.0558 | 14.9168 | 14.7853 | 14.6526 | 14.5295 | 14.4021 | 13.8558 | 13.4358 | 13.0874 | 14.5542 | 14.3711 | 14.0447 | 13.9163 | 13.7774 | 13.6468 | 13.5153 | 13.3942 | 13.27 | 12.7111 | 12.2721 | 11.9016 | 14.9692 | 14.8608 | 14.5071 | 14.3724 | 14.2271 | 14.0903 | 13.9513 | 13.8229 | 13.6903 | 13.1071 | 12.6576 | 12.2787
|  | NINEWELLS | HE |  |  |  |  | 15.9642 | 15.7642 | 15.5042 | 15.4347 | 15.3537 | 15.2811 | 15.2021 | 15.1295 | 15.06 | 14.7632 | 14.5547 | 14.4021 | 14.6521 | 14.6121 | 14.3689 | 14.2995 | 14.2216 | 14.15 | 14.0732 | 14.0016 | 13.9332 | 13.6468 | 13.4468 | 13.3058 | 14.9692 | 14.8608 | 14.5071 | 14.3724 | 14.2271 | 14.0903 | 13.9513 | 13.8229 | 13.6903 | 13.1071 | 12.6576 | 12.2787
|  | NINEWELLS | CF |  |  |  |  | 16.0874 | 15.9863 | 15.8621 | 15.8232 | 15.7779 | 15.7326 | 15.6874 | 15.6442 | 15.6011 | 15.4032 | 15.2484 | 15.1421 | 14.6858 | 14.6647 | 14.6405 | 14.6174 | 14.5921 | 14.5658 | 14.5395 | 14.5153 | 14.4732 | 14.2753 | 14.1226 | 14.0184 | 15.1008 | 15.0797 | 15.0555 | 15.0324 | 15.005 | 14.9766 | 14.9482 | 14.9218 | 14.8955 | 14.7629 | 14.5976 | 14.4829
| THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | YES | 0 | 0.20737 | 0.20526 | 0.20421 | 0.2 | 0.19895 | 0.19579 | 0.19368 | 0.19158 | 0.18842 | 0.17684 | 0.16842 | 0.15895 | 0.19368 | 0.19158 | 0.18947 | 0.18526 | 0.18316 | 0.18 | 0.17789 | 0.17474 | 0.17158 | 0.15895 | 0.14947 | 0.13895 | 0.19684 | 0.19474 | 0.19263 | 0.18947 | 0.18737 | 0.18316 | 0.18211 | 0.17895 | 0.17579 | 0.16316 | 0.15474 | 0.14421
|  | NORTH HOY | EE |  |  |  |  | 0.20842 | 0.20737 | 0.20632 | 0.20421 | 0.20211 | 0.2 | 0.19789 | 0.19579 | 0.19474 | 0.18526 | 0.17895 | 0.17263 | 0.19579 | 0.19474 | 0.19263 | 0.19053 | 0.18737 | 0.18526 | 0.18316 | 0.18105 | 0.17895 | 0.16842 | 0.16105 | 0.15368 | 0.2 | 0.19789 | 0.19579 | 0.19368 | 0.19053 | 0.18947 | 0.18737 | 0.18421 | 0.18211 | 0.17263 | 0.16526 | 0.15789
|  | NORTH HOY | HT |  |  |  |  | 0.20737 | 0.20526 | 0.20421 | 0.2 | 0.19895 | 0.19579 | 0.19368 | 0.19158 | 0.18842 | 0.17684 | 0.16842 | 0.15895 | 0.19368 | 0.19158 | 0.18947 | 0.18526 | 0.18316 | 0.18 | 0.17789 | 0.17474 | 0.17158 | 0.15895 | 0.14947 | 0.13895 | 0.19684 | 0.19474 | 0.19263 | 0.18947 | 0.18737 | 0.18316 | 0.18211 | 0.17895 | 0.17579 | 0.16316 | 0.15474 | 0.14421
|  | NORTH HOY | HE |  |  |  |  | 0.20947 | 0.20842 | 0.20842 | 0.20737 | 0.20632 | 0.20526 | 0.20421 | 0.20211 | 0.20211 | 0.19684 | 0.19368 | 0.19053 | 0.19789 | 0.19579 | 0.19579 | 0.19474 | 0.19368 | 0.19158 | 0.19053 | 0.18842 | 0.18842 | 0.18211 | 0.17789 | 0.17368 | 0.19684 | 0.19474 | 0.19263 | 0.18947 | 0.18737 | 0.18316 | 0.18211 | 0.17895 | 0.17579 | 0.16316 | 0.15474 | 0.14421
|  | NORTH HOY | CF |  |  |  |  | 0.21053 | 0.20947 | 0.20947 | 0.20947 | 0.20842 | 0.20842 | 0.20737 | 0.20737 | 0.20632 | 0.20421 | 0.20105 | 0.19895 | 0.2 | 0.19789 | 0.19789 | 0.19789 | 0.19579 | 0.19579 | 0.19474 | 0.19474 | 0.19368 | 0.19053 | 0.18632 | 0.18421 | 0.20316 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.19789 | 0.19789 | 0.19684 | 0.19368 | 0.19053 | 0.18737
| BEAULY | NORTH KESSOCK | MINIMUM HEADROOM | NH 65004 48461 | YES | YES | 0 | 4.1284 | 4.0632 | 3.9968 | 3.9326 | 3.8032 | 3.6726 | 3.5453 | 3.4042 | 3.2695 | 2.3853 | 1.2158 | 0.31684 | 3.8789 | 3.8053 | 3.7316 | 3.6589 | 3.5358 | 3.4147 | 3.2947 | 3.1653 | 3.0453 | 2.1305 | 0.89368 | 0.018947 | 3.9811 | 3.9084 | 3.8358 | 3.7653 | 3.6263 | 3.4905 | 3.3537 | 3.2053 | 3.0653 | 2.0979 | 0.81579 | -0.18632
|  | NORTH KESSOCK | EE |  |  |  |  | 4.1653 | 4.1158 | 4.06 | 4.0053 | 3.8768 | 3.7316 | 3.5832 | 3.4495 | 3.3158 | 2.3937 | 1.2158 | 0.31684 | 3.9284 | 3.8695 | 3.8084 | 3.7484 | 3.6347 | 3.5084 | 3.3789 | 3.26 | 3.1421 | 2.24 | 1.0663 | 0.063158 | 4.0284 | 3.9695 | 3.9084 | 3.8484 | 3.7147 | 3.5642 | 3.4084 | 3.2695 | 3.1305 | 2.1316 | 0.84947 | -0.18632
|  | NORTH KESSOCK | HT |  |  |  |  | 4.1284 | 4.0632 | 3.9968 | 3.9326 | 3.8032 | 3.6726 | 3.5453 | 3.4042 | 3.2695 | 2.3853 | 1.2716 | 0.50211 | 3.8789 | 3.8053 | 3.7316 | 3.6589 | 3.5358 | 3.4147 | 3.2947 | 3.1653 | 3.0453 | 2.1305 | 0.89368 | 0.018947 | 3.9811 | 3.9084 | 3.8358 | 3.7653 | 3.6263 | 3.4905 | 3.3537 | 3.2053 | 3.0653 | 2.0979 | 0.81579 | -0.075789
|  | NORTH KESSOCK | HE |  |  |  |  | 4.2 | 4.1779 | 4.1537 | 4.1284 | 4.0063 | 3.9021 | 3.7916 | 3.6674 | 3.4989 | 2.7695 | 1.8653 | 0.89684 | 3.9968 | 3.9611 | 3.9242 | 3.8874 | 3.7842 | 3.6958 | 3.5979 | 3.48 | 3.2979 | 2.5579 | 1.6189 | 0.60947 | 3.9811 | 3.9084 | 3.8358 | 3.7653 | 3.6263 | 3.4905 | 3.3537 | 3.2053 | 3.0653 | 2.0979 | 0.81579 | -0.075789
|  | NORTH KESSOCK | CF |  |  |  |  | 4.2211 | 4.2084 | 4.1968 | 4.1842 | 4.1421 | 4.1053 | 4.0568 | 4.0053 | 3.9253 | 3.5547 | 2.9832 | 2.3568 | 4.0337 | 4.0126 | 3.9905 | 3.9695 | 3.9221 | 3.8811 | 3.8389 | 3.7874 | 3.6884 | 3.2747 | 2.6737 | 1.9853 | 4.1305 | 4.1095 | 4.0874 | 4.0663 | 4.0116 | 3.9632 | 3.9137 | 3.8579 | 3.76 | 3.3295 | 2.6968 | 1.9758
| BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | 0 | 0.78632 | 0.69895 | 0.61368 | 0.52737 | 0.35895 | 0.19368 | 0.027368 | -0.14737 | -0.3221 | -1.6716 | -3.3063 | -4.6232 | 0.81368 | 0.71895 | 0.62842 | 0.54 | 0.38421 | 0.23158 | 0.077895 | -0.077895 | -0.23263 | -1.6358 | -3.4505 | -4.74 | 0.80526 | 0.71158 | 0.62105 | 0.52947 | 0.35684 | 0.18421 | 0.013684 | -0.16526 | -0.3421 | -1.8232 | -3.6926 | -5.1168
|  | NOSTIE BRIDGE | EE |  |  |  |  | 0.84316 | 0.76947 | 0.69579 | 0.62105 | 0.45368 | 0.26737 | 0.075789 | -0.094737 | -0.26105 | -1.6326 | -3.2905 | -4.6232 | 0.87474 | 0.79895 | 0.72211 | 0.64737 | 0.5 | 0.33789 | 0.17158 | 0.021053 | -0.12421 | -1.4674 | -3.1484 | -4.6263 | 0.86526 | 0.78737 | 0.70947 | 0.63053 | 0.46105 | 0.27053 | 0.075789 | -0.098947 | -0.26842 | -1.7568 | -3.5863 | -5.1168
|  | NOSTIE BRIDGE | HT |  |  |  |  | 0.78632 | 0.69895 | 0.61368 | 0.52737 | 0.35895 | 0.19368 | 0.027368 | -0.14737 | -0.3221 | -1.6716 | -3.3063 | -4.4411 | 0.81368 | 0.71895 | 0.62842 | 0.54 | 0.38421 | 0.23158 | 0.077895 | -0.077895 | -0.23263 | -1.6358 | -3.4505 | -4.74 | 0.80526 | 0.71158 | 0.62105 | 0.52947 | 0.35684 | 0.18421 | 0.013684 | -0.16526 | -0.3421 | -1.8232 | -3.6926 | -5.0042
|  | NOSTIE BRIDGE | HE |  |  |  |  | 0.92105 | 0.87789 | 0.83579 | 0.78947 | 0.63579 | 0.50105 | 0.32737 | 0.15474 | -0.097895 | -1.1463 | -2.44 | -3.8305 | 0.95895 | 0.91368 | 0.86737 | 0.82211 | 0.69053 | 0.57579 | 0.41263 | 0.25053 | -0.005263 | -1.0547 | -2.4116 | -3.8768 | 0.80526 | 0.71158 | 0.62105 | 0.52947 | 0.35684 | 0.18421 | 0.013684 | -0.16526 | -0.3421 | -1.8232 | -3.6926 | -5.0042
|  | NOSTIE BRIDGE | CF |  |  |  |  | 0.96421 | 0.93895 | 0.91474 | 0.88842 | 0.82316 | 0.76316 | 0.70316 | 0.60842 | 0.47684 | -0.091579 | -0.91158 | -1.8316 | 0.99053 | 0.97684 | 0.95263 | 0.92526 | 0.86737 | 0.81368 | 0.76105 | 0.66211 | 0.51789 | -0.072632 | -0.93895 | -1.9547 | 0.96316 | 0.94842 | 0.93368 | 0.91579 | 0.84842 | 0.78737 | 0.72526 | 0.62211 | 0.47579 | -0.14632 | -1.0568 | -2.1021
| TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 0 | 28.5958 | 28.4105 | 28.2232 | 28.0011 | 27.3579 | 26.7453 | 26.1126 | 25.4905 | 25.0421 | 23.8811 | 22.9137 | 22.0737 | 25.1726 | 24.9874 | 24.8 | 24.1589 | 23.4411 | 22.7579 | 22.0495 | 21.3516 | 20.8568 | 19.6053 | 18.5484 | 17.6158 | 23.3011 | 22.7853 | 22.1705 | 21.3947 | 20.6758 | 19.9926 | 19.2842 | 18.5874 | 18.0916 | 16.8368 | 15.7779 | 14.8453
|  | OBAN | EE |  |  |  |  | 28.7105 | 28.5642 | 28.4105 | 28.2516 | 28.0853 | 27.28 | 26.8368 | 26.3905 | 25.9737 | 24.6621 | 23.9284 | 23.3211 | 25.2874 | 25.1411 | 24.9884 | 24.8295 | 24.2737 | 23.3316 | 22.84 | 22.3421 | 21.8789 | 20.4463 | 19.6484 | 18.9747 | 23.5768 | 23.2421 | 22.7905 | 22.2137 | 21.5074 | 20.5653 | 20.0737 | 19.5747 | 19.1105 | 17.6726 | 16.8695 | 16.1937
|  | OBAN | HT |  |  |  |  | 28.5958 | 28.4105 | 28.2232 | 28.0011 | 27.3579 | 26.7453 | 26.1126 | 25.4905 | 25.0421 | 23.8811 | 22.9137 | 22.0737 | 25.1726 | 24.9874 | 24.8 | 24.1589 | 23.4411 | 22.7579 | 22.0495 | 21.3516 | 20.8568 | 19.6053 | 18.5484 | 17.6158 | 23.3011 | 22.7853 | 22.1705 | 21.3947 | 20.6758 | 19.9926 | 19.2842 | 18.5874 | 18.0916 | 16.8368 | 15.7779 | 14.8453
|  | OBAN | HE |  |  |  |  | 28.84 | 28.7326 | 28.6158 | 28.4916 | 28.3568 | 27.7211 | 27.2084 | 26.8042 | 26.5821 | 26.0168 | 25.6295 | 25.3347 | 25.4168 | 25.3095 | 25.1926 | 25.0684 | 24.6842 | 23.7958 | 23.2158 | 22.7611 | 22.5189 | 21.9221 | 21.5063 | 21.1832 | 23.3011 | 22.7853 | 22.1705 | 21.3947 | 20.6758 | 19.9926 | 19.2842 | 18.5874 | 18.0916 | 16.8368 | 15.7779 | 14.8453
|  | OBAN | CF |  |  |  |  | 28.9253 | 28.8621 | 28.7979 | 28.7316 | 28.6632 | 28.5937 | 28.5242 | 28.4547 | 28.3863 | 27.6905 | 27.3421 | 27.0842 | 25.5021 | 25.4389 | 25.3747 | 25.3084 | 25.24 | 25.1726 | 25.1032 | 25.0337 | 24.8589 | 23.7863 | 23.4074 | 23.1189 | 23.8516 | 23.7884 | 23.7242 | 23.6579 | 23.4568 | 23.1874 | 22.8158 | 22.4916 | 22.0916 | 21.02 | 20.6379 | 20.3484
| MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | YES | 0 | 10.8726 | 10.5505 | 10.3032 | 10.0937 | 9.8695 | 9.6432 | 9.4189 | 9.2084 | 9 | 7.9926 | 7.2432 | 6.6537 | 10.9411 | 10.7926 | 10.5221 | 10.2958 | 10.0589 | 9.8189 | 9.58 | 9.3579 | 9.1379 | 8.0484 | 7.2158 | 6.5505 | 11.1653 | 10.9579 | 10.7263 | 10.5021 | 10.2632 | 10.0232 | 9.7842 | 9.5611 | 9.3379 | 8.2611 | 7.4337 | 6.7779
|  | OLD CRAIGIE ROAD | EE |  |  |  |  | 11.0305 | 10.7442 | 10.5284 | 10.3495 | 10.1642 | 9.9842 | 9.7853 | 9.5989 | 9.4326 | 8.5926 | 7.9989 | 7.5453 | 11.0189 | 10.9126 | 10.7684 | 10.5747 | 10.38 | 10.1916 | 9.9842 | 9.7853 | 9.6095 | 8.7105 | 8.0968 | 7.5905 | 11.2747 | 11.0979 | 10.9474 | 10.7779 | 10.5811 | 10.3884 | 10.1779 | 9.9779 | 9.8011 | 8.8916 | 8.2705 | 7.7684
|  | OLD CRAIGIE ROAD | HT |  |  |  |  | 10.8726 | 10.5505 | 10.3032 | 10.0937 | 9.8695 | 9.6432 | 9.4189 | 9.2084 | 9 | 7.9926 | 7.2432 | 6.6537 | 10.9411 | 10.7926 | 10.5221 | 10.2958 | 10.0589 | 9.8189 | 9.58 | 9.3579 | 9.1379 | 8.0484 | 7.2158 | 6.5505 | 11.1653 | 10.9579 | 10.7263 | 10.5021 | 10.2632 | 10.0232 | 9.7842 | 9.5611 | 9.3379 | 8.2611 | 7.4337 | 6.7779
|  | OLD CRAIGIE ROAD | HE |  |  |  |  | 11.2137 | 10.9779 | 10.8211 | 10.6958 | 10.5579 | 10.4295 | 10.3 | 10.1716 | 10.0453 | 9.46 | 9.0295 | 8.7474 | 11.1126 | 11.0326 | 10.9537 | 10.8705 | 10.7768 | 10.6832 | 10.5495 | 10.4147 | 10.2842 | 9.6526 | 9.1611 | 8.86 | 11.1653 | 10.9579 | 10.7263 | 10.5021 | 10.2632 | 10.0232 | 9.7842 | 9.5611 | 9.3379 | 8.2611 | 7.4337 | 6.7779
|  | OLD CRAIGIE ROAD | CF |  |  |  |  | 11.4526 | 11.3295 | 11.2368 | 11.1568 | 11.0747 | 10.9884 | 10.9021 | 10.8179 | 10.7379 | 10.3632 | 10.0663 | 9.8558 | 11.18 | 11.1358 | 11.0916 | 11.0474 | 11.0011 | 10.9537 | 10.9074 | 10.8589 | 10.8137 | 10.6105 | 10.3063 | 10.0716 | 11.5284 | 11.4632 | 11.4 | 11.3411 | 11.28 | 11.2158 | 11.1526 | 11.0895 | 11.0305 | 10.7547 | 10.4874 | 10.2505
| KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 0.217 | 7.7641 | 7.4325 | 28.3083 | 27.8019 | 27.283 | 26.7746 | 26.2356 | 25.6346 | 25.1283 | 23.1683 | 21.2241 | 20.3904 | 6.7756 | 6.4114 | 26.1335 | 25.5672 | 25.0577 | 24.5609 | 24.0293 | 23.4409 | 22.9651 | 21.3662 | 19.7241 | 18.9567 | 7.2609 | 6.9104 | 27.1888 | 26.6267 | 26.0719 | 25.5309 | 24.9541 | 24.3109 | 23.7751 | 21.753 | 19.7383 | 18.8572
|  | OLDMELDRUM | EE |  |  |  |  | 7.8883 | 7.6398 | 28.6283 | 28.2304 | 27.6125 | 26.8251 | 26.2925 | 25.8019 | 25.3241 | 23.1683 | 21.2241 | 20.3904 | 6.9093 | 6.6409 | 26.4946 | 26.0525 | 25.443 | 24.6546 | 24.1662 | 23.7083 | 23.2683 | 21.3662 | 19.7241 | 18.9567 | 7.3904 | 7.1293 | 27.5414 | 27.1014 | 26.4362 | 25.5835 | 25.0235 | 24.5046 | 24.0014 | 21.753 | 19.7383 | 18.8572
|  | OLDMELDRUM | HT |  |  |  |  | 7.7641 | 7.4325 | 28.3083 | 27.8019 | 27.283 | 26.7746 | 26.2356 | 25.6346 | 25.1283 | 23.5546 | 22.4535 | 21.7419 | 6.7756 | 6.4114 | 26.1335 | 25.5672 | 25.0577 | 24.5609 | 24.0293 | 23.4409 | 22.9651 | 21.5546 | 20.5346 | 19.8198 | 7.2609 | 6.9104 | 27.1888 | 26.6267 | 26.0719 | 25.5309 | 24.9541 | 24.3109 | 23.7751 | 22.1362 | 20.9783 | 20.2141
|  | OLDMELDRUM | HE |  |  |  |  | 8.0556 | 7.8567 | 28.8746 | 28.4914 | 27.8651 | 27.2272 | 26.7672 | 26.3262 | 25.9914 | 24.6619 | 23.5062 | 22.3072 | 7.0893 | 6.8683 | 26.7462 | 26.3114 | 25.6977 | 25.0504 | 24.6114 | 24.1914 | 23.8956 | 22.7693 | 21.8041 | 20.8104 | 7.2609 | 6.9104 | 27.1888 | 26.6267 | 26.0719 | 25.5309 | 24.9541 | 24.3109 | 23.7751 | 22.1362 | 20.9783 | 20.2141
|  | OLDMELDRUM | CF |  |  |  |  | 8.2198 | 8.1356 | 29.3746 | 29.2619 | 29.0609 | 28.8314 | 28.5346 | 28.3241 | 28.1114 | 27.2398 | 26.4998 | 25.9714 | 7.2714 | 7.1798 | 27.3083 | 27.1819 | 26.9914 | 26.7641 | 26.4567 | 26.2451 | 26.023 | 25.1872 | 24.5556 | 24.1041 | 7.7377 | 7.6493 | 28.333 | 28.2119 | 28.0014 | 27.7604 | 27.4446 | 27.2183 | 26.9856 | 26.0572 | 25.2888 | 24.7383
| THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | NO | YES | 0 | 15.1521 | 14.9774 | 14.8068 | 14.6374 | 13.9689 | 13.3037 | 12.6258 | 12.2795 | 11.7047 | 9.8563 | 7.1279 | 4.6363 | 14.3284 | 14.1758 | 13.9958 | 13.8158 | 13.1189 | 12.4242 | 11.7158 | 11.3189 | 10.7558 | 9.2737 | 6.3842 | 3.9526 | 14.8476 | 14.6708 | 14.4982 | 14.3255 | 13.6424 | 12.9308 | 12.1845 | 11.7961 | 11.1782 | 9.3045 | 6.3887 | 3.5771
|  | ORMLIE | EE |  |  |  |  | 15.2489 | 15.1005 | 14.9489 | 14.7984 | 14.6489 | 14.3153 | 13.5837 | 12.8974 | 12.2005 | 9.8563 | 7.1279 | 4.6363 | 14.3789 | 14.2874 | 14.1558 | 14.0021 | 13.8474 | 13.5568 | 12.8242 | 12.1274 | 11.4189 | 9.2737 | 6.6884 | 3.9526 | 14.9424 | 14.7961 | 14.6413 | 14.4908 | 14.3392 | 13.9992 | 13.2497 | 12.5276 | 11.7655 | 9.3045 | 6.3887 | 3.5771
|  | ORMLIE | HT |  |  |  |  | 15.1521 | 14.9774 | 14.8068 | 14.6374 | 13.9689 | 13.3037 | 12.6258 | 12.2795 | 11.7047 | 10.0732 | 7.4132 | 5.3026 | 14.3284 | 14.1758 | 13.9958 | 13.8158 | 13.1189 | 12.4242 | 11.7158 | 11.3189 | 10.7558 | 9.2779 | 6.3842 | 3.9895 | 14.8476 | 14.6708 | 14.4982 | 14.3255 | 13.6424 | 12.9308 | 12.1845 | 11.7961 | 11.1782 | 9.4792 | 6.4992 | 4.0571
|  | ORMLIE | HE |  |  |  |  | 15.3932 | 15.3089 | 15.2205 | 15.13 | 14.7879 | 14.4932 | 14.0216 | 13.5553 | 13.0816 | 11.2332 | 8.7689 | 6.1289 | 14.46 | 14.4053 | 14.3463 | 14.2853 | 14.06 | 13.8095 | 13.3484 | 12.8916 | 12.4242 | 10.6684 | 8.1358 | 5.4158 | 14.8476 | 14.6708 | 14.4982 | 14.3255 | 13.6424 | 12.9308 | 12.1845 | 11.7961 | 11.1782 | 9.4792 | 6.4992 | 4.0571
|  | ORMLIE | CF |  |  |  |  | 15.4437 | 15.3795 | 15.3153 | 15.2458 | 15.0889 | 14.9426 | 14.7974 | 14.5668 | 14.3521 | 13.1837 | 11.5479 | 9.7837 | 14.48 | 14.4368 | 14.3926 | 14.3442 | 14.26 | 14.1811 | 14.0758 | 13.8389 | 13.6116 | 12.4221 | 10.7305 | 8.8084 | 15.0434 | 14.9992 | 14.9539 | 14.9045 | 14.7813 | 14.6361 | 14.4887 | 14.2529 | 14.0339 | 12.8318 | 11.0318 | 9.0487
| DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | 0 | 0.98842 | 0.96526 | 0.94211 | 0.91579 | 0.83474 | 0.75474 | 0.65263 | 0.56316 | 0.46947 | -0.010526 | -0.54842 | -0.82421 | 0.98526 | 0.96316 | 0.93895 | 0.90947 | 0.83895 | 0.76842 | 0.69053 | 0.61368 | 0.53579 | 0.12947 | -0.33684 | -0.60632 | 0.95789 | 0.93474 | 0.91053 | 0.88211 | 0.80526 | 0.72737 | 0.63158 | 0.54526 | 0.45789 | -0.026316 | -0.5821 | -0.88737
|  | OTTER FERRY | EE |  |  |  |  | 1.0021 | 0.98 | 0.95895 | 0.93895 | 0.85368 | 0.75474 | 0.65263 | 0.56316 | 0.46947 | -0.010526 | -0.54842 | -0.82421 | 0.99895 | 0.97895 | 0.95789 | 0.93789 | 0.86526 | 0.77789 | 0.69053 | 0.61368 | 0.53579 | 0.12947 | -0.33684 | -0.60632 | 0.97053 | 0.94947 | 0.92737 | 0.90632 | 0.82526 | 0.72947 | 0.63158 | 0.54526 | 0.45789 | -0.026316 | -0.5821 | -0.88737
|  | OTTER FERRY | HT |  |  |  |  | 0.98842 | 0.96526 | 0.94211 | 0.91579 | 0.83474 | 0.75684 | 0.67789 | 0.58842 | 0.49895 | 0.14105 | -0.16526 | -0.36737 | 0.98526 | 0.96316 | 0.93895 | 0.90947 | 0.83895 | 0.76842 | 0.69895 | 0.62 | 0.54105 | 0.22421 | -0.067368 | -0.27053 | 0.95789 | 0.93474 | 0.91053 | 0.88211 | 0.80526 | 0.72737 | 0.65158 | 0.56421 | 0.47684 | 0.11474 | -0.21684 | -0.43895
|  | OTTER FERRY | HE |  |  |  |  | 1.0179 | 1.0074 | 0.99789 | 0.98737 | 0.90632 | 0.83579 | 0.76632 | 0.69684 | 0.62 | 0.25263 | -0.12105 | -0.51895 | 1.0189 | 1.0084 | 0.99789 | 0.98526 | 0.91474 | 0.85579 | 0.79789 | 0.74105 | 0.67368 | 0.35474 | 0.016842 | -0.34632 | 0.95789 | 0.93474 | 0.91053 | 0.88211 | 0.80526 | 0.72737 | 0.65158 | 0.56421 | 0.47684 | 0.11474 | -0.21684 | -0.43895
|  | OTTER FERRY | CF |  |  |  |  | 1.0274 | 1.0211 | 1.0158 | 1.0105 | 0.97895 | 0.95053 | 0.92211 | 0.89684 | 0.87368 | 0.70947 | 0.47895 | 0.27368 | 1.0305 | 1.0242 | 1.0179 | 1.0116 | 0.98211 | 0.95789 | 0.93368 | 0.91158 | 0.89053 | 0.74 | 0.52947 | 0.33368 | 0.99474 | 0.99053 | 0.98632 | 0.98105 | 0.94947 | 0.92316 | 0.89579 | 0.87158 | 0.84947 | 0.68632 | 0.45895 | 0.24
| DUDHOPE | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | YES | 0.05 | 41.5174 | 41.4668 | 41.3942 | 41.3321 | 39.9184 | 39.8868 | 39.8542 | 39.6953 | 39.6047 | 39.4174 | 38.6732 | 38.4195 | 38.5774 | 38.4447 | 38.1584 | 37.9426 | 36.2563 | 35.9668 | 35.7479 | 35.6237 | 35.5542 | 35.3953 | 34.6026 | 34.3216 | 38.8926 | 38.8158 | 38.6726 | 38.5589 | 38.4516 | 38.3484 | 38.2063 | 38.0947 | 37.9642 | 37.6074 | 35.7011 | 35.42
|  | OVERGATE | EE |  |  |  |  | 41.5553 | 41.5195 | 42.1153 | 42.0647 | 42.0037 | 41.9353 | 41.8826 | 41.7005 | 41.4732 | 40.9742 | 40.7468 | 40.5489 | 38.6668 | 38.5616 | 39.3942 | 39.3511 | 39.3026 | 39.2395 | 39.0847 | 38.9511 | 38.7668 | 38.2121 | 37.9616 | 37.7437 | 38.9474 | 38.8884 | 40.2558 | 40.2084 | 40.1537 | 40.0811 | 39.9937 | 39.9168 | 39.8032 | 39.38 | 39.1326 | 38.9189
|  | OVERGATE | HT |  |  |  |  | 41.5174 | 41.4668 | 41.3942 | 41.3321 | 41.2658 | 41.1426 | 40.7889 | 40.4921 | 40.2521 | 39.8774 | 38.6732 | 38.4195 | 38.5774 | 38.4447 | 38.1584 | 37.9426 | 37.7511 | 37.5721 | 37.2974 | 37.0953 | 36.8826 | 36.4689 | 34.6026 | 34.3216 | 38.8926 | 38.8158 | 38.6726 | 38.5589 | 38.4516 | 38.3484 | 38.2063 | 38.0947 | 37.9642 | 37.6074 | 35.7011 | 35.42
|  | OVERGATE | HE |  |  |  |  | 41.57 | 41.5332 | 41.4732 | 41.4226 | 39.9184 | 39.8868 | 39.8542 | 39.6953 | 39.6047 | 39.4174 | 39.2753 | 39.1605 | 38.7016 | 38.5805 | 38.31 | 38.1089 | 36.2563 | 35.9668 | 35.7479 | 35.6237 | 35.5542 | 35.3953 | 35.2479 | 35.1237 | 38.8926 | 38.8158 | 38.6726 | 38.5589 | 38.4516 | 38.3484 | 38.2063 | 38.0947 | 37.9642 | 37.6074 | 35.7011 | 35.42
|  | OVERGATE | CF |  |  |  |  | 41.5816 | 41.5616 | 41.5342 | 41.51 | 41.4847 | 41.4542 | 41.4132 | 41.3837 | 41.3511 | 41.2384 | 41.8363 | 41.8037 | 38.7321 | 38.6974 | 38.6079 | 38.5479 | 38.4879 | 38.3963 | 38.2226 | 38.1374 | 38.0289 | 37.75 | 39.15 | 39.1226 | 38.9874 | 38.9621 | 38.9137 | 38.8779 | 38.8411 | 38.7905 | 38.7063 | 38.6568 | 38.6 | 38.4316 | 39.9905 | 39.9589
| CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | YES | 0 | 0.15105 | 0.14684 | 0.14053 | 0.13421 | 0.080526 | 0.015263 | -0.051053 | -0.11526 | -0.22474 | -0.80263 | -1.5868 | -2.2005 | 0.14895 | 0.14579 | 0.14053 | 0.13632 | 0.083684 | 0.022632 | -0.043684 | -0.10368 | -0.21632 | -0.83316 | -1.7153 | -2.3521 | 0.14789 | 0.14368 | 0.13737 | 0.13105 | 0.09 | 0.040526 | -0.012105 | -0.058421 | -0.19947 | -0.91421 | -1.8174 | -2.4774
|  | OVERSCAIG | EE |  |  |  |  | 0.15105 | 0.14684 | 0.14053 | 0.13421 | 0.094211 | 0.044737 | -0.006842 | -0.052105 | -0.14158 | -0.79947 | -1.5447 | -2.2005 | 0.14895 | 0.14579 | 0.14053 | 0.13632 | 0.10368 | 0.064737 | 0.023684 | -0.012105 | -0.099474 | -0.77105 | -1.5405 | -2.2763 | 0.14789 | 0.14368 | 0.13737 | 0.13105 | 0.09 | 0.040526 | -0.012105 | -0.058421 | -0.15421 | -0.88579 | -1.7184 | -2.4774
|  | OVERSCAIG | HT |  |  |  |  | 0.15211 | 0.14789 | 0.14684 | 0.14158 | 0.11 | 0.076316 | 0.019474 | -0.044737 | -0.17316 | -0.80263 | -1.5868 | -2.1426 | 0.15 | 0.14579 | 0.14368 | 0.13947 | 0.11526 | 0.088947 | 0.035263 | -0.024737 | -0.15737 | -0.83316 | -1.7153 | -2.3521 | 0.14895 | 0.14579 | 0.14474 | 0.13842 | 0.10789 | 0.073158 | 0.012105 | -0.056316 | -0.19947 | -0.91421 | -1.8174 | -2.4626
|  | OVERSCAIG | HE |  |  |  |  | 0.15211 | 0.15 | 0.15 | 0.14895 | 0.080526 | 0.015263 | -0.051053 | -0.11526 | -0.22474 | -0.67316 | -1.2784 | -1.9416 | 0.15 | 0.14789 | 0.14789 | 0.14789 | 0.083684 | 0.022632 | -0.043684 | -0.10368 | -0.21632 | -0.67632 | -1.3247 | -2.0363 | 0.14895 | 0.14579 | 0.14474 | 0.13842 | 0.10789 | 0.073158 | 0.012105 | -0.056316 | -0.19947 | -0.91421 | -1.8174 | -2.4626
|  | OVERSCAIG | CF |  |  |  |  | 0.15316 | 0.15105 | 0.15105 | 0.15 | 0.13421 | 0.12053 | 0.071053 | 0.022632 | -0.036316 | -0.28053 | -0.66474 | -1.1195 | 0.15105 | 0.15 | 0.14895 | 0.14895 | 0.13632 | 0.12579 | 0.072105 | 0.020526 | -0.045789 | -0.30684 | -0.72053 | -1.2289 | 0.15105 | 0.14895 | 0.14789 | 0.14789 | 0.13211 | 0.11842 | 0.062632 | 0.0078947 | -0.059474 | -0.33526 | -0.77105 | -1.2942
| KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | YES | 0 | 1.3368 | 1.2737 | 1.1768 | 1.0579 | 0.73895 | 0.38 | -0.012632 | -0.35263 | -0.84947 | -4.4189 | -8.6589 | -12.0705 | 0.99053 | 0.88737 | 0.76105 | 0.62842 | 0.34842 | 0.08421 | -0.23263 | -0.50421 | -1.1084 | -4.7284 | -9.3021 | -12.5516 | 1.0989 | 1 | 0.88 | 0.75579 | 0.42105 | 0.042105 | -0.36842 | -0.71895 | -1.1653 | -5.1232 | -9.8453 | -13.6442
|  | PARK | EE |  |  |  |  | 1.3674 | 1.3116 | 1.2505 | 1.1653 | 0.80632 | 0.38 | -0.012632 | -0.35263 | -0.7021 | -4.4189 | -8.6589 | -12.0705 | 1.0505 | 0.96737 | 0.86842 | 0.76105 | 0.45263 | 0.08421 | -0.23263 | -0.50421 | -0.78842 | -4.46 | -8.72 | -12.4958 | 1.1547 | 1.0716 | 0.97263 | 0.86737 | 0.48947 | 0.042105 | -0.36842 | -0.71895 | -1.0779 | -5.0737 | -9.7389 | -13.6442
|  | PARK | HT |  |  |  |  | 1.3368 | 1.2737 | 1.1768 | 1.0579 | 0.73895 | 0.44316 | 0.14421 | -0.20632 | -0.79474 | -4.3505 | -8.4811 | -11.341 | 0.99053 | 0.88737 | 0.76105 | 0.62842 | 0.34842 | 0.093684 | -0.16 | -0.44842 | -1.0168 | -4.7284 | -9.3021 | -12.5516 | 1.0989 | 1 | 0.88 | 0.75579 | 0.42105 | 0.11158 | -0.2 | -0.56105 | -1.1653 | -5.1232 | -9.8453 | -13.1484
|  | PARK | HE |  |  |  |  | 1.4074 | 1.3779 | 1.3453 | 1.3095 | 0.96211 | 0.61368 | 0.18737 | -0.22105 | -0.84947 | -3.4726 | -6.8084 | -10.4368 | 1.1274 | 1.0747 | 1.0042 | 0.92737 | 0.61368 | 0.30105 | -0.10105 | -0.47474 | -1.1084 | -3.7032 | -7.1779 | -10.9663 | 1.0989 | 1 | 0.88 | 0.75579 | 0.42105 | 0.11158 | -0.2 | -0.56105 | -1.1653 | -5.1232 | -9.8453 | -13.1484
|  | PARK | CF |  |  |  |  | 1.4305 | 1.4158 | 1.3989 | 1.3811 | 1.2674 | 1.1632 | 1.0147 | 0.74632 | 0.43053 | -0.96105 | -3.0726 | -5.4716 | 1.1653 | 1.1411 | 1.1095 | 1.0758 | 0.96105 | 0.84316 | 0.66842 | 0.37579 | 0.027368 | -1.4137 | -3.6274 | -6.2579 | 1.2611 | 1.2368 | 1.2074 | 1.1747 | 1.0316 | 0.89158 | 0.70316 | 0.42 | 0.085263 | -1.4642 | -3.8284 | -6.5632
| ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | NO | YES | 0 | 2.8358 | 2.8074 | 2.7768 | 2.7453 | 2.6432 | 2.5453 | 2.4463 | 2.3421 | 2.2358 | 1.7221 | 1.1916 | 0.95895 | 2.6116 | 2.5621 | 2.5105 | 2.4621 | 2.3642 | 2.2684 | 2.1726 | 2.0758 | 1.9768 | 1.5337 | 1.0537 | 0.83474 | 2.6389 | 2.5905 | 2.54 | 2.4926 | 2.3832 | 2.2768 | 2.1695 | 2.0579 | 1.9442 | 1.4 | 0.83053 | 0.58316
|  | PEDDIESTON | EE |  |  |  |  | 2.8505 | 2.8253 | 2.7968 | 2.7695 | 2.6874 | 2.5779 | 2.46 | 2.3547 | 2.2547 | 1.7221 | 1.1916 | 0.95895 | 2.6442 | 2.6021 | 2.56 | 2.5168 | 2.4232 | 2.3211 | 2.2116 | 2.1137 | 2.0221 | 1.5337 | 1.0537 | 0.83474 | 2.6695 | 2.6274 | 2.5853 | 2.5421 | 2.4358 | 2.3158 | 2.1905 | 2.0779 | 1.9716 | 1.4 | 0.83053 | 0.58316
|  | PEDDIESTON | HT |  |  |  |  | 2.8358 | 2.8074 | 2.7768 | 2.7453 | 2.6432 | 2.5453 | 2.4463 | 2.3421 | 2.2358 | 1.8053 | 1.4958 | 1.3011 | 2.6116 | 2.5621 | 2.5105 | 2.4621 | 2.3642 | 2.2684 | 2.1726 | 2.0758 | 1.9768 | 1.5695 | 1.2758 | 1.0811 | 2.6389 | 2.5905 | 2.54 | 2.4926 | 2.3832 | 2.2768 | 2.1695 | 2.0579 | 1.9442 | 1.4811 | 1.1547 | 0.94632
|  | PEDDIESTON | HE |  |  |  |  | 2.8716 | 2.8558 | 2.84 | 2.8211 | 2.7389 | 2.6684 | 2.5989 | 2.5295 | 2.4589 | 2.1105 | 1.7905 | 1.4284 | 2.6895 | 2.6642 | 2.6389 | 2.6116 | 2.5263 | 2.4516 | 2.3768 | 2.3042 | 2.2326 | 1.9221 | 1.6326 | 1.2937 | 2.6389 | 2.5905 | 2.54 | 2.4926 | 2.3832 | 2.2768 | 2.1695 | 2.0579 | 1.9442 | 1.4811 | 1.1547 | 0.94632
|  | PEDDIESTON | CF |  |  |  |  | 2.8842 | 2.8758 | 2.8674 | 2.8579 | 2.8253 | 2.7947 | 2.7653 | 2.74 | 2.7179 | 2.58 | 2.3842 | 2.2253 | 2.7116 | 2.6958 | 2.6811 | 2.6642 | 2.6263 | 2.5905 | 2.5558 | 2.5253 | 2.4979 | 2.3368 | 2.16 | 2.0063 | 2.7337 | 2.7189 | 2.7032 | 2.6874 | 2.6442 | 2.6053 | 2.5653 | 2.5305 | 2.5011 | 2.3179 | 2.1095 | 1.9358
| PETERHEAD GRANGE | PETERHEAD GRANGE | MINIMUM HEADROOM | NK 11738 46516 | NO | YES | 0.914 | 23.6292 | 23.3628 | 23.0923 | 22.7607 | 21.9418 | 21.1681 | 20.4471 | 19.6576 | 18.8071 | 14.7986 | 11.3397 | 8.2271 | 22.586 | 21.9702 | 21.1302 | 20.3492 | 19.506 | 18.7123 | 17.9807 | 17.186 | 16.3165 | 12.066 | 8.2776 | 4.7355 | 22.5344 | 22.006 | 21.306 | 20.6523 | 19.8871 | 19.1639 | 18.4881 | 17.7544 | 16.9649 | 13.2776 | 9.3428 | 5.7207
|  | PETERHEAD GRANGE | EE |  |  |  |  | 23.7797 | 23.5586 | 23.3271 | 23.0892 | 22.6628 | 21.8692 | 21.1934 | 20.5681 | 19.926 | 15.7786 | 11.5428 | 8.3334 | 22.8207 | 22.4776 | 21.8049 | 21.1849 | 20.4007 | 19.5334 | 18.8849 | 18.2797 | 17.6534 | 13.4176 | 9.0449 | 5.4586 | 22.7481 | 22.4344 | 21.8702 | 21.3439 | 20.6249 | 19.8313 | 19.2018 | 18.6197 | 18.0228 | 14.2207 | 9.7839 | 6.0692
|  | PETERHEAD GRANGE | HT |  |  |  |  | 23.6292 | 23.3628 | 23.0923 | 22.7607 | 21.9418 | 21.1681 | 20.4471 | 19.6576 | 18.8071 | 14.7986 | 11.3397 | 8.2271 | 22.586 | 21.9702 | 21.1302 | 20.3492 | 19.506 | 18.7123 | 17.9807 | 17.186 | 16.3165 | 12.066 | 8.2776 | 4.7355 | 22.5344 | 22.006 | 21.306 | 20.6523 | 19.8871 | 19.1639 | 18.4881 | 17.7544 | 16.9649 | 13.2776 | 9.3428 | 5.7207
|  | PETERHEAD GRANGE | HE |  |  |  |  | 23.9776 | 23.8292 | 23.6681 | 23.4965 | 23.1039 | 22.7628 | 22.2344 | 21.6428 | 21.026 | 17.7902 | 14.8955 | 12.0018 | 23.0502 | 22.8534 | 22.4828 | 21.9565 | 21.2376 | 20.5113 | 19.9534 | 19.3628 | 18.7397 | 15.3649 | 12.326 | 9.2955 | 22.5344 | 22.006 | 21.306 | 20.6523 | 19.8871 | 19.1639 | 18.4881 | 17.7544 | 16.9649 | 13.2776 | 9.3428 | 5.7207
|  | PETERHEAD GRANGE | CF |  |  |  |  | 24.1049 | 24.0218 | 23.9355 | 23.8481 | 23.6818 | 23.5249 | 23.3692 | 23.2218 | 23.0944 | 22.0165 | 19.7786 | 17.8155 | 23.2207 | 23.1302 | 23.0355 | 22.9376 | 22.7428 | 22.5292 | 22.2976 | 22.0576 | 21.7955 | 19.7228 | 17.3113 | 15.1471 | 23.1302 | 23.0407 | 22.9471 | 22.8523 | 22.6544 | 22.4471 | 22.226 | 22.0018 | 21.7681 | 19.9997 | 17.9744 | 16.206
| PETERHEAD GRANGE | PETERHEAD NORTH STREET | MINIMUM HEADROOM | NK 13470 46450 | NO | YES | 0.531 | 24.469 | 24.4301 | 24.3195 | 24.1922 | 24.0627 | 23.9332 | 23.8069 | 23.6837 | 23.5595 | 23.2206 | 22.7237 | 22.2595 | 22.8258 | 22.7185 | 22.6132 | 22.5079 | 22.3985 | 22.269 | 22.1301 | 21.9943 | 21.8585 | 21.6079 | 21.0479 | 20.5216 | 23.8016 | 23.6606 | 23.5237 | 23.3848 | 23.2437 | 23.1048 | 22.9669 | 22.8332 | 22.7006 | 22.4532 | 21.9006 | 21.3827
|  | PETERHEAD NORTH STREET | EE |  |  |  |  | 24.4953 | 24.4648 | 24.4332 | 24.3711 | 24.2701 | 24.169 | 24.0711 | 23.9722 | 23.8774 | 23.4279 | 23.2416 | 22.8922 | 22.9027 | 22.8206 | 22.7385 | 22.6553 | 22.5701 | 22.4869 | 22.4058 | 22.3195 | 22.2143 | 21.7216 | 21.6437 | 21.2479 | 23.8374 | 23.7953 | 23.6869 | 23.5795 | 23.4701 | 23.3606 | 23.2553 | 23.1501 | 23.0469 | 22.5564 | 22.4764 | 22.0869
|  | PETERHEAD NORTH STREET | HT |  |  |  |  | 24.469 | 24.4301 | 24.3195 | 24.1922 | 24.0627 | 23.9332 | 23.8069 | 23.6837 | 23.5595 | 23.2206 | 22.7237 | 22.2595 | 22.8258 | 22.7185 | 22.6132 | 22.5079 | 22.3985 | 22.269 | 22.1301 | 21.9943 | 21.8585 | 21.6079 | 21.0479 | 20.5216 | 23.8016 | 23.6606 | 23.5237 | 23.3848 | 23.2437 | 23.1048 | 22.9669 | 22.8332 | 22.7006 | 22.4532 | 21.9006 | 21.3827
|  | PETERHEAD NORTH STREET | HE |  |  |  |  | 24.5143 | 24.489 | 24.4627 | 24.4343 | 24.3995 | 24.369 | 24.3385 | 24.3079 | 24.2458 | 23.9806 | 23.7585 | 23.5585 | 22.9437 | 22.9185 | 22.8774 | 22.8195 | 22.7585 | 22.7016 | 22.6448 | 22.5911 | 22.5395 | 22.3227 | 22.0985 | 21.8764 | 23.8016 | 23.6606 | 23.5237 | 23.3848 | 23.2437 | 23.1048 | 22.9669 | 22.8332 | 22.7006 | 22.4532 | 21.9006 | 21.3827
|  | PETERHEAD NORTH STREET | CF |  |  |  |  | 24.5279 | 24.5122 | 24.4953 | 24.4785 | 24.4585 | 24.4406 | 24.4216 | 24.4027 | 24.3848 | 24.2437 | 24.0669 | 23.9164 | 22.9574 | 22.9416 | 22.9248 | 22.9079 | 22.8785 | 22.8395 | 22.8006 | 22.7606 | 22.7216 | 22.5406 | 22.3985 | 22.2606 | 23.8701 | 23.8543 | 23.8374 | 23.8206 | 23.8016 | 23.7816 | 23.7616 | 23.7332 | 23.6837 | 23.4501 | 23.2564 | 23.089
| FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | NO | 0 | 13.7389 | 13.5537 | 13.3558 | 13.1442 | 12.8842 | 12.6295 | 12.38 | 12.1337 | 11.9884 | 11.3389 | 10.8379 | 10.4368 | 12.2526 | 12.1758 | 12.0979 | 11.8758 | 11.5958 | 11.32 | 11.0495 | 10.7832 | 10.6389 | 9.9663 | 9.4358 | 8.9968 | 12.6684 | 12.5516 | 12.3705 | 12.1579 | 11.9011 | 11.6495 | 11.3916 | 11.1189 | 10.9663 | 10.2642 | 9.7158 | 9.2705
|  | PINEGROVE | EE |  |  |  |  | 13.8232 | 13.6642 | 13.4916 | 13.2989 | 13.0674 | 12.8337 | 12.5968 | 12.3674 | 12.2453 | 11.6358 | 11.12 | 10.7821 | 12.2979 | 12.2347 | 12.1684 | 12.0463 | 11.7979 | 11.5474 | 11.2958 | 11.0495 | 10.9295 | 10.3253 | 9.82 | 9.4611 | 12.7105 | 12.6516 | 12.4958 | 12.3137 | 12.0853 | 11.8526 | 11.6189 | 11.3758 | 11.2463 | 10.5989 | 10.0453 | 9.6726
|  | PINEGROVE | HT |  |  |  |  | 13.7389 | 13.5537 | 13.3558 | 13.1442 | 12.8842 | 12.6295 | 12.38 | 12.1337 | 11.9884 | 11.3389 | 10.8379 | 10.4368 | 12.2526 | 12.1758 | 12.0979 | 11.8758 | 11.5958 | 11.32 | 11.0495 | 10.7832 | 10.6389 | 9.9663 | 9.4358 | 8.9968 | 12.6684 | 12.5516 | 12.3705 | 12.1579 | 11.9011 | 11.6495 | 11.3916 | 11.1189 | 10.9663 | 10.2642 | 9.7158 | 9.2705
|  | PINEGROVE | HE |  |  |  |  | 13.9326 | 13.8084 | 13.6663 | 13.5074 | 13.3011 | 13.1053 | 12.9095 | 12.7189 | 12.6326 | 12.2884 | 12.0347 | 11.7958 | 12.3505 | 12.3042 | 12.2547 | 12.2 | 12.0516 | 11.84 | 11.6326 | 11.4253 | 11.3421 | 11.0147 | 10.7768 | 10.5547 | 12.6684 | 12.5516 | 12.3705 | 12.1579 | 11.9011 | 11.6495 | 11.3916 | 11.1189 | 10.9663 | 10.2642 | 9.7158 | 9.2705
|  | PINEGROVE | CF |  |  |  |  | 14.0105 | 13.9779 | 13.9253 | 13.8421 | 13.7432 | 13.6379 | 13.5316 | 13.4179 | 13.3611 | 13.1095 | 12.9116 | 12.7621 | 12.3905 | 12.3632 | 12.3347 | 12.3063 | 12.2716 | 12.2379 | 12.2032 | 12.1684 | 12.1274 | 11.8726 | 11.6789 | 11.5295 | 12.7937 | 12.7695 | 12.7432 | 12.7179 | 12.6821 | 12.6326 | 12.5358 | 12.4337 | 12.3779 | 12.1316 | 11.9379 | 11.7926
| TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 0.1 | 5.552 | 5.3867 | 5.2141 | 5.033 | 4.6678 | 4.3257 | 3.9846 | 3.6078 | 3.2783 | 1.7436 | -0.48171 | -1.9375 | 5.2837 | 5.1047 | 4.9153 | 4.7184 | 4.3816 | 4.0637 | 3.7468 | 3.4079 | 3.1226 | 1.9163 | -0.17947 | -1.7416 | 5.3284 | 5.1568 | 4.9652 | 4.7641 | 4.3915 | 4.0389 | 3.6905 | 3.3073 | 2.9841 | 1.4684 | -0.90112 | -2.5948
|  | PITLOCHRY | EE |  |  |  |  | 5.6372 | 5.4993 | 5.353 | 5.2014 | 4.8372 | 4.4393 | 4.0393 | 3.6793 | 3.3636 | 1.7436 | -0.48171 | -1.9375 | 5.3763 | 5.23 | 5.0742 | 4.91 | 4.5932 | 4.2479 | 3.9016 | 3.5753 | 3.3026 | 1.9163 | -0.17947 | -1.7416 | 5.3747 | 5.281 | 5.1189 | 4.9494 | 4.582 | 4.1831 | 3.7831 | 3.4199 | 3.1136 | 1.4684 | -0.90112 | -2.5948
|  | PITLOCHRY | HT |  |  |  |  | 5.552 | 5.3867 | 5.2141 | 5.033 | 4.6678 | 4.3257 | 3.9846 | 3.6078 | 3.2783 | 1.992 | 0.17303 | -1.0049 | 5.2837 | 5.1047 | 4.9153 | 4.7184 | 4.3816 | 4.0637 | 3.7468 | 3.4079 | 3.1226 | 1.9784 | -0.015263 | -1.3721 | 5.3284 | 5.1568 | 4.9652 | 4.7641 | 4.3915 | 4.0389 | 3.6905 | 3.3073 | 2.9841 | 1.6852 | -0.4327 | -1.8464
|  | PITLOCHRY | HE |  |  |  |  | 5.7446 | 5.6541 | 5.5551 | 5.4436 | 5.0962 | 4.7951 | 4.4951 | 4.1983 | 3.9541 | 2.6899 | 1.0488 | -0.70592 | 5.4963 | 5.3963 | 5.2847 | 5.1626 | 4.8742 | 4.61 | 4.3458 | 4.0774 | 3.8679 | 2.7395 | 1.1184 | -0.63632 | 5.3284 | 5.1568 | 4.9652 | 4.7641 | 4.3915 | 4.0389 | 3.6905 | 3.3073 | 2.9841 | 1.6852 | -0.4327 | -1.8464
|  | PITLOCHRY | CF |  |  |  |  | 5.7899 | 5.7657 | 5.712 | 5.6551 | 5.513 | 5.3793 | 5.2446 | 5.1172 | 5.033 | 4.3909 | 3.3604 | 2.333 | 5.5426 | 5.5205 | 5.4605 | 5.3974 | 5.2753 | 5.1584 | 5.0395 | 4.9216 | 4.8458 | 4.2479 | 3.21 | 2.0932 | 5.4684 | 5.4452 | 5.421 | 5.3968 | 5.3052 | 5.1705 | 5.0315 | 4.8989 | 4.8147 | 4.1515 | 3.042 | 1.8515
| ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 0 | 3.7758 | 3.6821 | 3.5874 | 3.4926 | 3.3958 | 3.3032 | 3.2137 | 3.1274 | 3.0453 | 1.9042 | 1.6442 | 1.4232 | 3.5884 | 3.4779 | 3.3684 | 3.2589 | 3.1484 | 3.0421 | 2.9411 | 2.8421 | 2.7484 | 1.7632 | 1.4453 | 1.1705 | 3.4526 | 3.3958 | 3.3368 | 3.2768 | 3.2116 | 3.1495 | 3.0895 | 3 | 2.9063 | 1.7284 | 1.4105 | 1.1347
|  | POLLACHAR | EE |  |  |  |  | 3.8347 | 3.7579 | 3.68 | 3.6011 | 3.5242 | 3.4484 | 3.3758 | 3.3084 | 3.2432 | 3.4884 | 3.2916 | 3.1316 | 3.66 | 3.5716 | 3.4821 | 3.3916 | 3.3032 | 3.2179 | 3.1358 | 3.0579 | 2.9842 | 3.7211 | 3.4821 | 3.2811 | 3.4811 | 3.4326 | 3.3821 | 3.3295 | 3.2768 | 3.2253 | 3.1758 | 3.1295 | 3.0853 | 3.4695 | 3.2758 | 3.0789
|  | POLLACHAR | HT |  |  |  |  | 3.7758 | 3.6821 | 3.5874 | 3.4926 | 3.3958 | 3.3032 | 3.2137 | 3.1274 | 3.0453 | 1.9042 | 1.6442 | 1.4232 | 3.5884 | 3.4779 | 3.3684 | 3.2589 | 3.1484 | 3.0421 | 2.9411 | 2.8421 | 2.7484 | 1.7632 | 1.4453 | 1.1705 | 3.4526 | 3.3958 | 3.3368 | 3.2768 | 3.2116 | 3.1495 | 3.0895 | 3 | 2.9063 | 1.7284 | 1.4105 | 1.1347
|  | POLLACHAR | HE |  |  |  |  | 3.9232 | 3.8737 | 3.8211 | 3.7653 | 3.7105 | 3.66 | 3.6095 | 3.5621 | 3.5179 | 2.9505 | 2.8474 | 2.7758 | 3.7147 | 3.6811 | 3.6442 | 3.5884 | 3.5274 | 3.4716 | 3.4158 | 3.3632 | 3.3137 | 2.8316 | 2.7074 | 2.6168 | 3.4526 | 3.3958 | 3.3368 | 3.2768 | 3.2116 | 3.1495 | 3.0895 | 3 | 2.9063 | 1.7284 | 1.4105 | 1.1347
|  | POLLACHAR | CF |  |  |  |  | 3.9747 | 3.9453 | 3.9147 | 3.8842 | 3.8547 | 3.8242 | 3.7947 | 3.7642 | 3.7326 | 3.5989 | 3.5116 | 3.4474 | 3.7474 | 3.7284 | 3.7095 | 3.6905 | 3.6716 | 3.6516 | 3.6179 | 3.5821 | 3.5474 | 3.3916 | 3.2842 | 3.2021 | 3.5611 | 3.5421 | 3.5232 | 3.5042 | 3.4853 | 3.4653 | 3.4463 | 3.4263 | 3.4063 | 3.3232 | 3.2821 | 3.2611
| FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | NO | 0 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.096842 | 0.093684 | 0.089474 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.089474 | 0.085263 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.093684 | 0.090526 | 0.086316
|  | POOR HOUSE | EE |  |  |  |  | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10316 | 0.10211 | 0.10105 | 0.098947 | 0.096842 | 0.093684 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.098947 | 0.095789 | 0.092632 | 0.090526 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.096842 | 0.093684 | 0.091579
|  | POOR HOUSE | HT |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.096842 | 0.093684 | 0.089474 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.089474 | 0.085263 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.093684 | 0.090526 | 0.086316
|  | POOR HOUSE | HE |  |  |  |  | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10211 | 0.10105 | 0.1 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.098947 | 0.096842 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.093684 | 0.090526 | 0.086316
|  | POOR HOUSE | CF |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10316 | 0.10211 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10105
| PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | NO | YES | 0 | 1.6155 | 1.5997 | 1.5818 | 1.5439 | 1.5028 | 1.4586 | 1.4186 | 1.3797 | 1.3428 | 1.1934 | 1.0144 | 0.89021 | 1.4828 | 1.4618 | 1.4239 | 1.3818 | 1.3376 | 1.2881 | 1.2439 | 1.1997 | 1.1597 | 0.99126 | 0.80389 | 0.66074 | 1.5597 | 1.5292 | 1.4902 | 1.4492 | 1.406 | 1.3586 | 1.3144 | 1.2723 | 1.2334 | 1.0692 | 0.87758 | 0.73968
|  | PORT ASKAIG | EE |  |  |  |  | 1.6249 | 1.6123 | 1.5986 | 1.5839 | 1.5639 | 1.5334 | 1.4997 | 1.4702 | 1.4397 | 1.3144 | 1.1702 | 1.0765 | 1.4934 | 1.4797 | 1.4639 | 1.4386 | 1.4049 | 1.3723 | 1.3355 | 1.3018 | 1.2681 | 1.1281 | 0.97863 | 0.87126 | 1.5692 | 1.5565 | 1.5323 | 1.5049 | 1.4723 | 1.4397 | 1.4039 | 1.3702 | 1.3376 | 1.2018 | 1.0481 | 0.94389
|  | PORT ASKAIG | HT |  |  |  |  | 1.6155 | 1.5997 | 1.5818 | 1.5439 | 1.5028 | 1.4586 | 1.4186 | 1.3797 | 1.3428 | 1.1934 | 1.0144 | 0.89021 | 1.4828 | 1.4618 | 1.4239 | 1.3818 | 1.3376 | 1.2881 | 1.2439 | 1.1997 | 1.1597 | 0.99126 | 0.80389 | 0.66074 | 1.5597 | 1.5292 | 1.4902 | 1.4492 | 1.406 | 1.3586 | 1.3144 | 1.2723 | 1.2334 | 1.0692 | 0.87758 | 0.73968
|  | PORT ASKAIG | HE |  |  |  |  | 1.6386 | 1.6292 | 1.6197 | 1.6092 | 1.5986 | 1.5892 | 1.5786 | 1.5702 | 1.5618 | 1.4881 | 1.4092 | 1.3607 | 1.5081 | 1.4986 | 1.4881 | 1.4776 | 1.466 | 1.4565 | 1.4439 | 1.426 | 1.4039 | 1.3228 | 1.2407 | 1.1849 | 1.5597 | 1.5292 | 1.4902 | 1.4492 | 1.406 | 1.3586 | 1.3144 | 1.2723 | 1.2334 | 1.0692 | 0.87758 | 0.73968
|  | PORT ASKAIG | CF |  |  |  |  | 1.6471 | 1.6418 | 1.6376 | 1.6323 | 1.6281 | 1.6228 | 1.6176 | 1.6134 | 1.6081 | 1.586 | 1.5386 | 1.5007 | 1.5165 | 1.5113 | 1.5071 | 1.5018 | 1.4976 | 1.4913 | 1.486 | 1.4807 | 1.4755 | 1.4281 | 1.3744 | 1.3302 | 1.5913 | 1.586 | 1.5818 | 1.5765 | 1.5723 | 1.5671 | 1.5618 | 1.5576 | 1.5523 | 1.4944 | 1.4418 | 1.3997
| PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 0 | 4.7937 | 4.7053 | 4.6516 | 4.6021 | 4.5579 | 4.5137 | 4.4737 | 4.4326 | 4.3947 | 4.2295 | 4.0589 | 3.9063 | 4.42 | 4.3063 | 4.2432 | 4.1832 | 4.1326 | 4.0832 | 4.0368 | 3.9905 | 3.9484 | 3.7484 | 3.5316 | 3.3326 | 4.8326 | 4.7442 | 4.6853 | 4.6305 | 4.5832 | 4.5368 | 4.4926 | 4.4495 | 4.4095 | 4.2253 | 4.0305 | 3.8368
|  | PORT ELLEN | EE |  |  |  |  | 4.8221 | 4.7411 | 4.6968 | 4.6537 | 4.6179 | 4.5842 | 4.5516 | 4.5211 | 4.4895 | 4.3611 | 4.2495 | 4.1368 | 4.4526 | 4.3495 | 4.2968 | 4.2463 | 4.2053 | 4.1674 | 4.1305 | 4.0947 | 4.06 | 3.9116 | 3.7716 | 3.6242 | 4.8474 | 4.7842 | 4.7358 | 4.6884 | 4.6505 | 4.6137 | 4.5789 | 4.5453 | 4.5126 | 4.3737 | 4.2474 | 4.1168
|  | PORT ELLEN | HT |  |  |  |  | 4.7937 | 4.7053 | 4.6516 | 4.6021 | 4.5579 | 4.5137 | 4.4737 | 4.4326 | 4.3947 | 4.2295 | 4.0589 | 3.9063 | 4.42 | 4.3063 | 4.2432 | 4.1832 | 4.1326 | 4.0832 | 4.0368 | 3.9905 | 3.9484 | 3.7484 | 3.5316 | 3.3326 | 4.8326 | 4.7442 | 4.6853 | 4.6305 | 4.5832 | 4.5368 | 4.4926 | 4.4495 | 4.4095 | 4.2253 | 4.0305 | 3.8368
|  | PORT ELLEN | HE |  |  |  |  | 4.8611 | 4.7916 | 4.7589 | 4.7274 | 4.7021 | 4.6779 | 4.6547 | 4.6347 | 4.6147 | 4.5411 | 4.4926 | 4.4589 | 4.4958 | 4.4105 | 4.3716 | 4.3337 | 4.3063 | 4.2789 | 4.2537 | 4.2316 | 4.2095 | 4.1253 | 4.0674 | 4.0242 | 4.8326 | 4.7442 | 4.6853 | 4.6305 | 4.5832 | 4.5368 | 4.4926 | 4.4495 | 4.4095 | 4.2253 | 4.0305 | 3.8368
|  | PORT ELLEN | CF |  |  |  |  | 4.9147 | 4.8789 | 4.8611 | 4.8432 | 4.8284 | 4.8126 | 4.7989 | 4.7842 | 4.7695 | 4.7042 | 4.6611 | 4.6305 | 4.5589 | 4.5168 | 4.4958 | 4.4768 | 4.4611 | 4.4442 | 4.4284 | 4.4126 | 4.3968 | 4.3221 | 4.2695 | 4.2305 | 4.8811 | 4.8726 | 4.8632 | 4.8537 | 4.8442 | 4.8347 | 4.8253 | 4.8158 | 4.8063 | 4.7516 | 4.7042 | 4.6695
| DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | YES | 0 | 8.9274 | 8.8316 | 8.7337 | 8.6368 | 7.8326 | 7.3368 | 6.8442 | 6.4884 | 6.1337 | 4.9842 | 3.8989 | 3.3042 | 7.76 | 7.6705 | 7.5789 | 7.4874 | 6.54 | 5.9853 | 5.4358 | 5.0653 | 4.6979 | 3.74 | 2.9074 | 2.3695 | 8.2789 | 8.1821 | 8.0832 | 7.9842 | 6.8884 | 6.3095 | 5.7337 | 5.3316 | 4.9316 | 3.7316 | 2.5737 | 1.9168
|  | PORTREE | EE |  |  |  |  | 8.9621 | 8.8653 | 8.7642 | 8.6611 | 8.1779 | 7.9147 | 7.3937 | 6.8916 | 6.3947 | 4.9842 | 3.8989 | 3.3042 | 7.8032 | 7.7232 | 7.6379 | 7.5495 | 7.0389 | 6.8063 | 6.2505 | 5.7105 | 5.1779 | 3.8537 | 2.9074 | 2.3695 | 8.3095 | 8.2074 | 8.1 | 7.9895 | 7.32 | 7.0432 | 6.4389 | 5.8547 | 5.2768 | 3.7316 | 2.5737 | 1.9168
|  | PORTREE | HT |  |  |  |  | 8.9274 | 8.8316 | 8.7337 | 8.6368 | 7.8326 | 7.3368 | 6.8442 | 6.4884 | 6.1337 | 5.1442 | 4.4189 | 3.8916 | 7.76 | 7.6705 | 7.5789 | 7.4874 | 6.54 | 5.9853 | 5.4358 | 5.0653 | 4.6979 | 3.74 | 3.0232 | 2.4958 | 8.2789 | 8.1821 | 8.0832 | 7.9842 | 6.8884 | 6.3095 | 5.7337 | 5.3316 | 4.9316 | 3.8558 | 3.0558 | 2.4768
|  | PORTREE | HE |  |  |  |  | 9.0463 | 8.9905 | 8.9316 | 8.8695 | 8.5768 | 8.4032 | 8.06 | 7.7179 | 7.3832 | 6.1968 | 5.6158 | 5.0389 | 7.8789 | 7.8274 | 7.7737 | 7.7147 | 7.4116 | 7.2579 | 6.8884 | 6.5211 | 6.1611 | 4.9411 | 4.4453 | 3.9589 | 8.2789 | 8.1821 | 8.0832 | 7.9842 | 6.8884 | 6.3095 | 5.7337 | 5.3316 | 4.9316 | 3.8558 | 3.0558 | 2.4768
|  | PORTREE | CF |  |  |  |  | 9.0947 | 9.0674 | 9.0389 | 9.0105 | 8.9463 | 8.8874 | 8.8305 | 8.7747 | 8.6968 | 7.9063 | 7.54 | 7.2716 | 7.9253 | 7.8989 | 7.8726 | 7.8453 | 7.8011 | 7.7568 | 7.7137 | 7.6737 | 7.5568 | 6.68 | 6.3474 | 6.0989 | 8.4484 | 8.42 | 8.3916 | 8.3621 | 8.3011 | 8.2421 | 8.1853 | 8.1116 | 7.9126 | 6.9874 | 6.5979 | 6.3095
| MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | YES | 0.35 | 1.3901 | 1.3396 | -0.48779 | -0.52358 | -0.792 | -1.0541 | -1.3215 | -1.5531 | -1.7888 | -3.8341 | -6.5309 | -8.4804 | 1.8396 | 1.7912 | 0.248 | 0.18589 | -0.089895 | -0.35832 | -0.62779 | -0.86147 | -1.0994 | -3.3025 | -5.9236 | -8.032 | 1.9869 | 1.9133 | -0.13937 | -0.192 | -0.50463 | -0.8099 | -1.1204 | -1.3878 | -1.6615 | -3.8994 | -6.7646 | -8.8973
|  | PORTSOY | EE |  |  |  |  | 1.4133 | 1.3659 | -0.48779 | -0.52358 | -0.792 | -1.0541 | -1.3215 | -1.5531 | -1.7888 | -3.8341 | -6.5309 | -8.4804 | 1.8648 | 1.8238 | 0.248 | 0.18589 | -0.089895 | -0.35832 | -0.62779 | -0.86147 | -1.0994 | -3.3025 | -5.9236 | -8.032 | 2.0269 | 1.9617 | -0.13937 | -0.192 | -0.50463 | -0.8099 | -1.1204 | -1.3878 | -1.6615 | -3.8994 | -6.7646 | -8.8973
|  | PORTSOY | HT |  |  |  |  | 1.3901 | 1.3396 | 1.288 | 1.2364 | 1.0396 | 0.84168 | 0.64484 | 0.41537 | 0.18379 | -1.5362 | -4.0141 | -5.5373 | 1.8396 | 1.7912 | 1.7406 | 1.6912 | 1.5059 | 1.2922 | 1.0806 | 0.83958 | 0.55853 | -1.6667 | -4.3088 | -6.0109 | 1.9869 | 1.9133 | 1.8396 | 1.7669 | 1.5312 | 1.2954 | 1.0617 | 0.78905 | 0.49221 | -1.6025 | -4.3025 | -6.0331
|  | PORTSOY | HE |  |  |  |  | 1.4469 | 1.4217 | 1.3954 | 1.3659 | 1.1343 | 0.93958 | 0.74484 | 0.55221 | 0.36484 | -0.98989 | -3.0257 | -5.2299 | 1.9017 | 1.8764 | 1.8501 | 1.8206 | 1.6964 | 1.5164 | 1.2427 | 0.98168 | 0.59221 | -1.0415 | -3.0962 | -5.3246 | 1.9869 | 1.9133 | 1.8396 | 1.7669 | 1.5312 | 1.2954 | 1.0617 | 0.78905 | 0.49221 | -1.6025 | -4.3025 | -6.0331
|  | PORTSOY | CF |  |  |  |  | 1.468 | 1.4533 | 1.4385 | 1.4217 | 1.3333 | 1.2543 | 1.1743 | 1.1038 | 1.0522 | 0.68063 | -0.5299 | -1.9215 | 1.9248 | 1.9101 | 1.8954 | 1.8785 | 1.8291 | 1.7848 | 1.7364 | 1.6122 | 1.4122 | 0.53326 | -0.77305 | -2.2499 | 2.1122 | 2.0912 | 2.0712 | 2.0459 | 1.9417 | 1.8469 | 1.7427 | 1.6027 | 1.4596 | 0.74168 | -0.56884 | -2.0752
| WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 0 | 15.1208 | 14.9671 | 14.8113 | 31.6242 | 31.4389 | 31.2579 | 31.0821 | 30.9084 | 30.7411 | 29.7232 | 28.8179 | 27.9926 | 13.5242 | 13.3621 | 13.2 | 29.1316 | 28.9453 | 28.76 | 28.5653 | 28.2726 | 27.9811 | 26.7989 | 25.7716 | 24.8105 | 13.9051 | 13.7514 | 13.5957 | 29.9721 | 29.7868 | 29.6068 | 29.4311 | 29.2058 | 28.9142 | 27.7363 | 26.7153 | 25.7689
|  | QUEENS LANE NORTH | EE |  |  |  |  | 15.2197 | 15.0987 | 14.9724 | 31.8147 | 31.6663 | 31.52 | 31.3768 | 31.24 | 31.1084 | 30.4779 | 29.7505 | 29.1568 | 13.6274 | 13.5 | 13.3684 | 29.3316 | 29.1853 | 29.0411 | 28.9011 | 28.7663 | 28.6295 | 27.66 | 26.8537 | 26.1674 | 14.0041 | 13.883 | 13.7578 | 30.1616 | 30.0142 | 29.8689 | 29.7268 | 29.5911 | 29.4605 | 28.5732 | 27.7584 | 27.0784
|  | QUEENS LANE NORTH | HT |  |  |  |  | 15.1208 | 14.9671 | 14.8113 | 31.6242 | 31.4389 | 31.2579 | 31.0821 | 30.9084 | 30.7411 | 29.7232 | 28.8179 | 27.9926 | 13.5242 | 13.3621 | 13.2 | 29.1316 | 28.9453 | 28.76 | 28.5653 | 28.2726 | 27.9811 | 26.7989 | 25.7716 | 24.8105 | 13.9051 | 13.7514 | 13.5957 | 29.9721 | 29.7868 | 29.6068 | 29.4311 | 29.2058 | 28.9142 | 27.7363 | 26.7153 | 25.7689
|  | QUEENS LANE NORTH | HE |  |  |  |  | 15.3092 | 15.2145 | 15.1113 | 31.9758 | 31.8484 | 31.7316 | 31.6179 | 31.5084 | 31.4105 | 31.0547 | 30.8484 | 30.7137 | 13.7232 | 13.6232 | 13.5168 | 29.5053 | 29.38 | 29.2663 | 29.1547 | 29.0484 | 28.9537 | 28.6116 | 28.4074 | 28.0632 | 13.9051 | 13.7514 | 13.5957 | 29.9721 | 29.7868 | 29.6068 | 29.4311 | 29.2058 | 28.9142 | 27.7363 | 26.7153 | 25.7689
|  | QUEENS LANE NORTH | CF |  |  |  |  | 15.3629 | 15.2997 | 15.2345 | 32.1432 | 32.0716 | 32 | 31.9274 | 31.8558 | 31.7863 | 31.4768 | 31.3053 | 31.2147 | 13.78 | 13.7126 | 13.6453 | 29.6768 | 29.6053 | 29.5326 | 29.46 | 29.3874 | 29.3168 | 29.0063 | 28.8368 | 28.6674 | 14.1472 | 14.0841 | 14.0188 | 30.49 | 30.4195 | 30.3468 | 30.2753 | 30.2037 | 30.1342 | 29.8268 | 29.6574 | 29.5679
| THURSO | RACKWICK | MINIMUM HEADROOM | ND 20206 99857 | YES | YES | 0 | 0.10421 | 0.10421 | 0.10316 | 0.1 | 0.1 | 0.097895 | 0.095789 | 0.094737 | 0.092632 | 0.086316 | 0.08 | 0.074737 | 0.096842 | 0.095789 | 0.094737 | 0.091579 | 0.090526 | 0.088421 | 0.086316 | 0.085263 | 0.083158 | 0.075789 | 0.068421 | 0.062105 | 0.098947 | 0.098947 | 0.096842 | 0.093684 | 0.092632 | 0.091579 | 0.089474 | 0.087368 | 0.085263 | 0.077895 | 0.071579 | 0.065263
|  | RACKWICK | EE |  |  |  |  | 0.10526 | 0.10421 | 0.10316 | 0.10316 | 0.10105 | 0.1 | 0.098947 | 0.098947 | 0.096842 | 0.090526 | 0.086316 | 0.083158 | 0.097895 | 0.096842 | 0.094737 | 0.094737 | 0.092632 | 0.091579 | 0.090526 | 0.089474 | 0.087368 | 0.081053 | 0.075789 | 0.071579 | 0.1 | 0.098947 | 0.097895 | 0.096842 | 0.094737 | 0.093684 | 0.092632 | 0.091579 | 0.090526 | 0.08421 | 0.077895 | 0.074737
|  | RACKWICK | HT |  |  |  |  | 0.10421 | 0.10421 | 0.10316 | 0.1 | 0.1 | 0.097895 | 0.095789 | 0.094737 | 0.092632 | 0.086316 | 0.08 | 0.074737 | 0.096842 | 0.095789 | 0.094737 | 0.091579 | 0.090526 | 0.088421 | 0.086316 | 0.085263 | 0.083158 | 0.075789 | 0.068421 | 0.062105 | 0.098947 | 0.098947 | 0.096842 | 0.093684 | 0.092632 | 0.091579 | 0.089474 | 0.087368 | 0.085263 | 0.077895 | 0.071579 | 0.065263
|  | RACKWICK | HE |  |  |  |  | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.098947 | 0.095789 | 0.094737 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.093684 | 0.093684 | 0.090526 | 0.086316 | 0.085263 | 0.098947 | 0.098947 | 0.096842 | 0.093684 | 0.092632 | 0.091579 | 0.089474 | 0.087368 | 0.085263 | 0.077895 | 0.071579 | 0.065263
|  | RACKWICK | CF |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.094737 | 0.091579 | 0.089474 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.093684 | 0.092632
| FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | NO | 0 | 1.0032 | 0.99263 | 0.98211 | 0.97053 | 0.95789 | 0.94842 | 0.93789 | 0.92737 | 0.91684 | 0.86842 | 0.82632 | 0.78316 | 1 | 0.99053 | 0.98 | 0.96947 | 0.95789 | 0.94842 | 0.93895 | 0.92842 | 0.91789 | 0.87158 | 0.83158 | 0.79053 | 0.99789 | 0.98947 | 0.97895 | 0.96737 | 0.95474 | 0.94526 | 0.93474 | 0.92421 | 0.91368 | 0.86421 | 0.82211 | 0.77895
|  | RAHOY | EE |  |  |  |  | 1.0032 | 0.99263 | 0.98211 | 0.97053 | 0.95789 | 0.94842 | 0.93789 | 0.92737 | 0.91684 | 0.86842 | 0.82632 | 0.78316 | 1 | 0.99053 | 0.98 | 0.96947 | 0.95789 | 0.94842 | 0.93895 | 0.92842 | 0.91789 | 0.87158 | 0.83158 | 0.79053 | 0.99789 | 0.98947 | 0.97895 | 0.96737 | 0.95474 | 0.94526 | 0.93474 | 0.92421 | 0.91368 | 0.86421 | 0.82211 | 0.77895
|  | RAHOY | HT |  |  |  |  | 1.0074 | 1.0053 | 1.0032 | 0.99895 | 0.99579 | 0.99263 | 0.99053 | 0.98737 | 0.98421 | 0.96947 | 0.95263 | 0.93474 | 1.0042 | 1.0032 | 1.0011 | 0.99684 | 0.99368 | 0.99158 | 0.98947 | 0.98632 | 0.98316 | 0.96842 | 0.95263 | 0.93579 | 1.0042 | 1.0021 | 0.99895 | 0.99474 | 0.99263 | 0.98947 | 0.98737 | 0.98421 | 0.98211 | 0.96632 | 0.94947 | 0.93158
|  | RAHOY | HE |  |  |  |  | 1.0074 | 1.0053 | 1.0032 | 1 | 0.99684 | 0.99474 | 0.99158 | 0.98737 | 0.98421 | 0.96842 | 0.95263 | 0.93579 | 1.0042 | 1.0032 | 1.0011 | 0.99789 | 0.99474 | 0.99263 | 0.98947 | 0.98632 | 0.98316 | 0.96737 | 0.95263 | 0.93684 | 1.0042 | 1.0021 | 0.99895 | 0.99474 | 0.99263 | 0.98947 | 0.98737 | 0.98421 | 0.98211 | 0.96632 | 0.94947 | 0.93158
|  | RAHOY | CF |  |  |  |  | 1.0095 | 1.0084 | 1.0084 | 1.0074 | 1.0074 | 1.0063 | 1.0063 | 1.0063 | 1.0053 | 1.0032 | 1 | 0.99789 | 1.0053 | 1.0053 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0032 | 1.0032 | 1.0032 | 1.0011 | 0.99789 | 0.99579 | 1.0063 | 1.0063 | 1.0053 | 1.0042 | 1.0042 | 1.0032 | 1.0021 | 1.0021 | 1.0021 | 0.99895 | 0.99579 | 0.99368
| INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | YES | 0.512 | 24.6929 | 24.5546 | 21.9303 | 21.8615 | 21.7841 | 21.7339 | 21.6622 | 21.5942 | 21.5203 | 21.1842 | 20.9313 | 20.7163 | 24.4327 | 24.313 | 22.1652 | 22.0964 | 22.0212 | 21.9846 | 21.9151 | 21.8485 | 21.7668 | 21.3597 | 21.0344 | 20.742 | 25.0905 | 25.0102 | 22.1036 | 22.0348 | 21.9581 | 21.9244 | 21.8534 | 21.7854 | 21.703 | 21.2909 | 20.9598 | 20.6681
|  | RAIGMORE | EE |  |  |  |  | 24.7445 | 24.6312 | 21.9303 | 21.8615 | 21.7841 | 21.7339 | 21.6622 | 21.5942 | 21.5203 | 21.1842 | 20.9313 | 20.7163 | 24.4778 | 24.3811 | 22.1652 | 22.0964 | 22.0212 | 21.9846 | 21.9151 | 21.8485 | 21.7668 | 21.3597 | 21.0344 | 20.742 | 25.1234 | 25.0589 | 22.1036 | 22.0348 | 21.9581 | 21.9244 | 21.8534 | 21.7854 | 21.703 | 21.2909 | 20.9598 | 20.6681
|  | RAIGMORE | HT |  |  |  |  | 24.6929 | 24.5546 | 24.4127 | 24.2937 | 24.1418 | 24.0286 | 23.9203 | 23.815 | 23.724 | 23.3843 | 23.0511 | 22.7573 | 24.4327 | 24.313 | 24.1911 | 24.1066 | 23.9747 | 23.8715 | 23.7726 | 23.6766 | 23.5913 | 23.2846 | 22.8496 | 22.3716 | 25.0905 | 25.0102 | 24.9285 | 24.8633 | 24.687 | 24.5501 | 24.4197 | 24.2929 | 24.1925 | 23.7833 | 23.291 | 22.8195
|  | RAIGMORE | HE |  |  |  |  | 24.7911 | 24.7129 | 24.6234 | 24.5245 | 24.4155 | 24.346 | 24.2794 | 24.2249 | 24.1748 | 23.9913 | 23.8587 | 23.7369 | 24.5222 | 24.4549 | 24.3789 | 24.2943 | 24.2048 | 24.1431 | 24.0829 | 24.0321 | 23.9855 | 23.8206 | 23.7124 | 23.6021 | 25.0905 | 25.0102 | 24.9285 | 24.8633 | 24.687 | 24.5501 | 24.4197 | 24.2929 | 24.1925 | 23.7833 | 23.291 | 22.8195
|  | RAIGMORE | CF |  |  |  |  | 24.857 | 24.824 | 24.7903 | 24.7559 | 24.7144 | 24.6699 | 24.6248 | 24.5796 | 24.5345 | 24.3589 | 24.2486 | 24.1812 | 24.5767 | 24.5466 | 24.5151 | 24.4828 | 24.4463 | 24.4076 | 24.3696 | 24.3302 | 24.2908 | 24.1367 | 24.0464 | 23.9934 | 25.1937 | 25.1679 | 25.1414 | 25.1148 | 25.0855 | 25.0568 | 25.0281 | 24.9987 | 24.9701 | 24.8461 | 24.7773 | 24.7422
| ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | 0 | 0.30421 | -2.3105 | -2.3758 | -2.4411 | -2.8442 | -3.3232 | -3.8116 | -4.2347 | -4.92 | -9.2811 | -15.9053 | -19.4505 | -0.27579 | -3.3558 | -3.4147 | -3.4737 | -3.7905 | -4.1653 | -4.5463 | -4.8779 | -5.5126 | -9.7316 | -16.54 | -20.3947 | -0.068421 | -3.1642 | -3.2305 | -3.2947 | -3.6979 | -4.1768 | -4.6663 | -5.0895 | -5.8179 | -10.5389 | -17.9053 | -21.9358
|  | REDFORD | EE |  |  |  |  | 0.35684 | -2.3105 | -2.3758 | -2.4411 | -2.8442 | -3.3232 | -3.8116 | -4.2347 | -4.92 | -9.2811 | -15.9053 | -19.4505 | -0.21684 | -3.3558 | -3.4147 | -3.4737 | -3.7905 | -4.1653 | -4.5463 | -4.8779 | -5.5126 | -9.7316 | -16.54 | -20.3947 | -0.008421 | -3.1642 | -3.2305 | -3.2947 | -3.6979 | -4.1768 | -4.6663 | -5.0895 | -5.8179 | -10.5389 | -17.9053 | -21.9358
|  | REDFORD | HT |  |  |  |  | 0.30421 | 0.21053 | 0.11895 | 0.028421 | -0.33684 | -0.7 | -1.0726 | -1.5137 | -2.3105 | -5.8253 | -10.1221 | -13.0263 | -0.27579 | -0.37263 | -0.46842 | -0.5621 | -0.87474 | -1.1884 | -1.5053 | -1.8779 | -2.6474 | -6.1495 | -10.7958 | -14.0547 | -0.068421 | -0.17053 | -0.26947 | -0.36842 | -0.74211 | -1.1158 | -1.4916 | -1.9316 | -2.7979 | -6.6663 | -11.5442 | -14.8853
|  | REDFORD | HE |  |  |  |  | 0.42526 | 0.38526 | 0.34211 | 0.29684 | -0.16316 | -0.65263 | -1.1684 | -1.6611 | -2.3632 | -5.3474 | -10.8463 | -14.82 | -0.13895 | -0.18316 | -0.22842 | -0.27474 | -0.66842 | -1.1253 | -1.5958 | -2.0411 | -2.7263 | -5.6011 | -11.4326 | -15.4653 | -0.068421 | -0.17053 | -0.26947 | -0.36842 | -0.74211 | -1.1158 | -1.4916 | -1.9316 | -2.7979 | -6.6663 | -11.5442 | -14.8853
|  | REDFORD | CF |  |  |  |  | 0.45789 | 0.43579 | 0.41263 | 0.38737 | 0.22 | 0.067368 | -0.16842 | -0.45684 | -0.78947 | -2.3253 | -4.6274 | -7.1453 | -0.097895 | -0.12526 | -0.15263 | -0.18 | -0.32 | -0.44842 | -0.68526 | -0.99158 | -1.3442 | -2.8789 | -5.2263 | -7.9295 | 0.11158 | 0.083158 | 0.054737 | 0.026316 | -0.14421 | -0.2979 | -0.56526 | -0.89895 | -1.2768 | -2.9642 | -5.5147 | -8.3632
| BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 0.199 | 14.7373 | 14.1373 | 13.4436 | 12.6499 | 11.1699 | 9.7489 | 8.2047 | 6.7499 | 5.2457 | -2.4827 | -8.4827 | -12.3058 | 12.9852 | 12.2778 | 11.4536 | 10.5073 | 8.9684 | 7.5652 | 6.1621 | 4.7252 | 3.1831 | -3.9737 | -9.1379 | -13.0569 | 13.7392 | 13.0539 | 12.2381 | 11.3044 | 9.6339 | 8.0571 | 6.3507 | 4.7792 | 3.1644 | -5.1135 | -11.3451 | -15.5672
|  | REDGORTON | EE |  |  |  |  | 14.8836 | 14.3226 | 13.6678 | 12.9236 | 11.371 | 9.7489 | 8.2047 | 6.7499 | 5.2457 | -2.4827 | -8.4827 | -12.3058 | 13.1505 | 12.4926 | 11.7178 | 10.8315 | 9.2578 | 7.6547 | 6.1621 | 4.7694 | 3.3326 | -3.9737 | -9.1379 | -13.0569 | 13.8918 | 13.2592 | 12.4865 | 11.6055 | 9.8644 | 8.0571 | 6.3507 | 4.7792 | 3.1644 | -5.1135 | -11.3451 | -15.5672
|  | REDGORTON | HT |  |  |  |  | 14.7373 | 14.1373 | 13.4436 | 12.6499 | 11.1699 | 9.8068 | 8.4784 | 6.9752 | 5.391 | -0.87321 | -4.2006 | -9.1827 | 12.9852 | 12.2778 | 11.4536 | 10.5073 | 8.9684 | 7.5652 | 6.2094 | 4.7252 | 3.1831 | -2.9758 | -6.139 | -11.6622 | 13.7392 | 13.0539 | 12.2381 | 11.3044 | 9.6339 | 8.1023 | 6.6128 | 4.9634 | 3.2528 | -3.5703 | -7.1282 | -12.8261
|  | REDGORTON | HE |  |  |  |  | 15.0752 | 14.6131 | 14.0542 | 13.3963 | 11.8426 | 10.4689 | 9.1794 | 7.8657 | 6.4973 | 0.51732 | -3.4932 | -8.5101 | 13.3673 | 12.8042 | 12.1231 | 11.3199 | 9.7568 | 8.3547 | 7.0568 | 5.7421 | 4.4052 | -1.3822 | -4.9432 | -9.6232 | 13.7392 | 13.0539 | 12.2381 | 11.3044 | 9.6339 | 8.1023 | 6.6128 | 4.9634 | 3.2528 | -3.5703 | -7.1282 | -12.8261
|  | REDGORTON | CF |  |  |  |  | 15.3521 | 15.1194 | 14.8552 | 14.5657 | 13.9636 | 13.3973 | 12.8257 | 12.2752 | 11.7457 | 8.5647 | 6.0721 | 2.3931 | 13.6989 | 13.4189 | 13.0999 | 12.7484 | 12.141 | 11.5568 | 10.9663 | 10.3842 | 9.7989 | 6.4021 | 4.1715 | 0.30837 | 14.3865 | 14.1371 | 13.8549 | 13.5192 | 12.8444 | 12.2055 | 11.5602 | 10.9318 | 10.3202 | 6.6749 | 4.0413 | -0.075579
| REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | YES | 0.5 | 39.8516 | 39.5632 | 38.6684 | 37.4295 | 36.1579 | 34.8989 | 33.6821 | 32.4168 | 31.0726 | 28.5505 | 27.7621 | 27.0242 | 38.7484 | 38.4537 | 37.3568 | 35.8179 | 34.2895 | 32.7789 | 31.3168 | 29.8053 | 28.1916 | 26.0389 | 24.9158 | 23.9495 | 40.2326 | 39.9389 | 38.9021 | 37.3989 | 35.8789 | 34.3768 | 32.9011 | 31.3621 | 29.7189 | 27.4758 | 26.2863 | 25.2958
|  | REDMOSS | EE |  |  |  |  | 39.8516 | 39.7095 | 39.1779 | 38.1147 | 36.7779 | 35.1989 | 34.0747 | 32.9716 | 31.8274 | 29.4221 | 28.0674 | 27.3189 | 38.7484 | 38.6095 | 37.9716 | 36.6495 | 35.0411 | 33.1337 | 31.8116 | 30.5 | 29.1379 | 26.4968 | 25.24 | 24.4558 | 40.2326 | 40.0905 | 39.4863 | 38.2116 | 36.6074 | 34.7074 | 33.3653 | 32.0263 | 30.6316 | 27.8611 | 26.4326 | 25.5937
|  | REDMOSS | HT |  |  |  |  | 40.1063 | 39.5632 | 38.6684 | 37.4295 | 36.1579 | 34.8989 | 33.6821 | 32.4168 | 31.0726 | 29.1137 | 28.04 | 27.1842 | 39.1021 | 38.4537 | 37.3568 | 35.8179 | 34.2895 | 32.7789 | 31.3168 | 29.8053 | 28.1916 | 26.0389 | 24.9158 | 23.9495 | 40.5537 | 39.9389 | 38.9021 | 37.3989 | 35.8789 | 34.3768 | 32.9011 | 31.3621 | 29.7189 | 27.4758 | 26.2863 | 25.2958
|  | REDMOSS | HE |  |  |  |  | 39.9832 | 39.8895 | 39.5158 | 38.4558 | 37.1484 | 35.6947 | 34.6232 | 33.5074 | 32.2558 | 28.5505 | 27.7621 | 27.0242 | 38.88 | 38.7874 | 38.3358 | 37.0063 | 35.4316 | 33.6526 | 32.3663 | 31.02 | 29.4968 | 26.3463 | 25.6263 | 24.9726 | 40.5537 | 39.9389 | 38.9021 | 37.3989 | 35.8789 | 34.3768 | 32.9011 | 31.3621 | 29.7189 | 27.4758 | 26.2863 | 25.2958
|  | REDMOSS | CF |  |  |  |  | 40.0632 | 40.0105 | 39.9579 | 39.9042 | 39.8021 | 39.3337 | 38.7053 | 38.1274 | 37.4663 | 33.6747 | 33.1147 | 32.7158 | 38.96 | 38.9084 | 38.8558 | 38.8021 | 38.7126 | 38.1495 | 37.3811 | 36.6768 | 35.8558 | 32.4158 | 31.8768 | 31.4884 | 40.4442 | 40.3916 | 40.3389 | 40.2853 | 40.1832 | 39.6442 | 38.9021 | 38.2042 | 37.3979 | 33.3705 | 32.7716 | 32.3379
| CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | YES | 0.095 | 1.0661 | 1.0334 | 0.99868 | 0.965 | 0.925 | 0.87026 | 0.81763 | 0.76816 | 0.71974 | 0.51132 | 0.34921 | 0.18921 | 0.90395 | 0.86395 | 0.80289 | 0.74395 | 0.685 | 0.62711 | 0.57237 | 0.51974 | 0.46921 | 0.24395 | 0.065 | -0.11079 | 0.93132 | 0.89868 | 0.865 | 0.83026 | 0.77237 | 0.71447 | 0.65868 | 0.60605 | 0.55553 | 0.32816 | 0.14816 | -0.030789
|  | RHICONICH | EE |  |  |  |  | 1.0861 | 1.0587 | 1.0303 | 1.0008 | 0.97237 | 0.94395 | 0.91553 | 0.88289 | 0.845 | 0.67026 | 0.54921 | 0.43342 | 0.925 | 0.89763 | 0.87026 | 0.82289 | 0.77763 | 0.73132 | 0.68816 | 0.64816 | 0.60921 | 0.425 | 0.29342 | 0.16711 | 0.95237 | 0.92395 | 0.89553 | 0.86605 | 0.83658 | 0.80816 | 0.77026 | 0.72921 | 0.68921 | 0.50079 | 0.36605 | 0.23553
|  | RHICONICH | HT |  |  |  |  | 1.0661 | 1.0334 | 0.99868 | 0.965 | 0.925 | 0.87026 | 0.81763 | 0.76816 | 0.71974 | 0.51132 | 0.34921 | 0.18921 | 0.90395 | 0.86395 | 0.80289 | 0.74395 | 0.685 | 0.62711 | 0.57237 | 0.51974 | 0.46921 | 0.24395 | 0.065 | -0.11079 | 0.93132 | 0.89868 | 0.865 | 0.83026 | 0.77237 | 0.71447 | 0.65868 | 0.60605 | 0.55553 | 0.32816 | 0.14816 | -0.030789
|  | RHICONICH | HE |  |  |  |  | 1.1145 | 1.0955 | 1.0766 | 1.0566 | 1.0345 | 1.0145 | 0.99553 | 0.97658 | 0.95974 | 0.90289 | 0.87447 | 0.81342 | 0.95237 | 0.93447 | 0.91553 | 0.89447 | 0.87342 | 0.85342 | 0.83447 | 0.81658 | 0.79237 | 0.69868 | 0.63763 | 0.57026 | 0.93132 | 0.89868 | 0.865 | 0.83026 | 0.77237 | 0.71447 | 0.65868 | 0.60605 | 0.55553 | 0.32816 | 0.14816 | -0.030789
|  | RHICONICH | CF |  |  |  |  | 1.1313 | 1.1229 | 1.1134 | 1.1039 | 1.0945 | 1.085 | 1.0755 | 1.0661 | 1.0555 | 1.0145 | 0.99447 | 0.985 | 0.96921 | 0.96079 | 0.95132 | 0.94184 | 0.93237 | 0.92289 | 0.91342 | 0.90395 | 0.89447 | 0.84079 | 0.78816 | 0.74921 | 0.99763 | 0.98921 | 0.97868 | 0.96921 | 0.95974 | 0.95026 | 0.94079 | 0.93132 | 0.92184 | 0.88079 | 0.85974 | 0.83658
| DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | YES | 0.4 | 25.0153 | 24.8226 | 24.6226 | 24.4068 | 24.1595 | 23.9174 | 23.6774 | 23.4437 | 23.2132 | 21.6289 | 20.1963 | 18.9732 | 21.56 | 21.2789 | 20.9263 | 20.6368 | 20.3232 | 20.0105 | 19.6958 | 19.3979 | 19.0979 | 17.4 | 15.7968 | 14.4116 | 22.2308 | 22.0013 | 21.7392 | 21.3961 | 21.0182 | 20.6371 | 20.2497 | 19.8887 | 19.5182 | 17.5529 | 16.0171 | 14.6982
|  | ROSEBANK STREET | EE |  |  |  |  | 25.1668 | 25.0258 | 24.8784 | 24.7195 | 24.5363 | 24.3532 | 24.1668 | 23.9879 | 23.8163 | 22.91 | 21.7668 | 20.8753 | 21.7347 | 21.5705 | 21.3168 | 21.0726 | 20.8295 | 20.5916 | 20.3358 | 20.0895 | 19.8632 | 18.7484 | 17.5653 | 16.5579 | 22.4118 | 22.2413 | 22.0497 | 21.855 | 21.6266 | 21.3318 | 21.0045 | 20.6908 | 20.4055 | 18.9108 | 17.6855 | 16.7234
|  | ROSEBANK STREET | HT |  |  |  |  | 25.0153 | 24.8226 | 24.6226 | 24.4068 | 24.1595 | 23.9174 | 23.6774 | 23.4437 | 23.2132 | 21.6289 | 20.1963 | 18.9732 | 21.56 | 21.2789 | 20.9263 | 20.6368 | 20.3232 | 20.0105 | 19.6958 | 19.3979 | 19.0979 | 17.4 | 15.7968 | 14.4116 | 22.2308 | 22.0013 | 21.7392 | 21.3961 | 21.0182 | 20.6371 | 20.2497 | 19.8887 | 19.5182 | 17.5529 | 16.0171 | 14.6982
|  | ROSEBANK STREET | HE |  |  |  |  | 25.2416 | 25.1184 | 24.9847 | 24.8416 | 24.6805 | 24.5311 | 24.3858 | 24.2479 | 24.1163 | 23.5984 | 23.29 | 22.8521 | 21.8095 | 21.6863 | 21.5526 | 21.3621 | 21.1632 | 20.9811 | 20.7947 | 20.6116 | 20.4368 | 19.6084 | 19.0842 | 18.7221 | 22.2308 | 22.0013 | 21.7392 | 21.3961 | 21.0182 | 20.6371 | 20.2497 | 19.8887 | 19.5182 | 17.5529 | 16.0171 | 14.6982
|  | ROSEBANK STREET | CF |  |  |  |  | 25.3016 | 25.2163 | 25.1289 | 25.0384 | 24.9437 | 24.8479 | 24.7511 | 24.6563 | 24.5616 | 24.1405 | 23.8858 | 23.7416 | 21.8695 | 21.7842 | 21.6968 | 21.6074 | 21.5137 | 21.4095 | 21.2768 | 21.1432 | 21.0126 | 20.4168 | 19.9874 | 19.6916 | 22.5982 | 22.4992 | 22.3971 | 22.2908 | 22.1813 | 22.0697 | 21.9571 | 21.8445 | 21.7361 | 21.1803 | 20.5782 | 20.1361
| KEITH 2 | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 0 | 5.6589 | 5.5758 | 5.4926 | 5.4105 | 4.9274 | 1.2442 | 0.63368 | 0.047368 | -0.75789 | -3.8179 | -3.34 | -6.1516 | 4.3084 | 4.2305 | 4.1516 | 4.0747 | 3.6989 | 0.66316 | 0.11158 | -0.41474 | -1.1863 | -4.1316 | -3.9768 | -6.9842 | 5.2979 | 5.2137 | 5.1305 | 5.0474 | 4.5421 | 1.6937 | 1.2779 | 0.89263 | 0.46737 | -2.3832 | -4.3032 | -7.4568
|  | ROTHES | EE |  |  |  |  | 5.6874 | 5.6042 | 5.5168 | 5.4305 | 4.9274 | 4.8737 | 4.2737 | 3.7484 | 2.9358 | -1.5326 | 1.2821 | -2.6621 | 4.3368 | 4.26 | 4.1811 | 4.1011 | 3.7011 | 3.6474 | 3.1737 | 2.7316 | 1.9832 | -2.3705 | 0.63789 | -3.6084 | 5.3263 | 5.2411 | 5.1526 | 5.0642 | 4.5421 | 4.4884 | 3.8653 | 3.3232 | 2.4642 | -2.3832 | -0.012632 | -4.4653
|  | ROTHES | HT |  |  |  |  | 5.6589 | 5.5758 | 5.4926 | 5.4105 | 4.9832 | 4.9179 | 4.3568 | 3.7337 | 2.7568 | -1.1137 | 2.4411 | -0.78632 | 4.3084 | 4.2305 | 4.1516 | 4.0747 | 3.7295 | 3.6642 | 3.1495 | 2.6032 | 1.6526 | -2.3811 | 0.81368 | -2.7821 | 5.2979 | 5.2137 | 5.1305 | 5.0474 | 4.6042 | 4.5389 | 3.9295 | 3.2663 | 2.2084 | -2.0853 | 0.85579 | -2.8316
|  | ROTHES | HE |  |  |  |  | 5.7389 | 5.7011 | 5.6579 | 5.6158 | 4.9737 | 1.2442 | 0.63368 | 0.047368 | -0.75789 | -3.8179 | 0.40632 | -4.0474 | 4.3884 | 4.3516 | 4.3105 | 4.2695 | 3.6989 | 0.66316 | 0.11158 | -0.41474 | -1.1863 | -4.1316 | 0.13895 | -4.3495 | 5.2979 | 5.2137 | 5.1305 | 5.0474 | 4.6042 | 4.5389 | 3.9295 | 3.2663 | 2.2084 | -2.0853 | 0.85579 | -2.8316
|  | ROTHES | CF |  |  |  |  | 6.7684 | 5.7095 | 5.6747 | 5.6389 | 5.4284 | 2.1274 | 1.7453 | 1.3926 | 1.0116 | -0.69579 | -3.34 | -6.1516 | 5.8758 | 4.36 | 4.3263 | 4.2916 | 4.1221 | 1.4737 | 1.0979 | 0.74842 | 0.35474 | -1.3358 | -3.9768 | -6.9842 | 6.9 | 5.3484 | 5.3137 | 5.2768 | 5.0589 | 1.6937 | 1.2779 | 0.89263 | 0.46737 | -1.4 | -4.3032 | -7.4568
| DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 0 | 16.1711 | 16.0689 | 15.9658 | 15.8595 | 15.7437 | 15.61 | 15.4279 | 15.25 | 15.0763 | 14.3584 | 13.7384 | 13.1837 | 14.3189 | 14.2179 | 14.1168 | 14.0105 | 13.8874 | 13.6926 | 13.5032 | 13.3179 | 13.1368 | 12.3832 | 11.7274 | 11.1253 | 15.2318 | 15.1203 | 14.9455 | 14.7634 | 14.5592 | 14.3582 | 14.1613 | 13.9697 | 13.7824 | 12.9971 | 12.3108 | 11.6897
|  | ROTHESAY | EE |  |  |  |  | 16.2353 | 16.1542 | 16.0711 | 15.9826 | 15.8921 | 15.8047 | 15.7184 | 15.6374 | 15.5205 | 14.9184 | 14.4511 | 14.0447 | 14.3821 | 14.3021 | 14.22 | 14.1316 | 14.0421 | 13.9568 | 13.8716 | 13.7421 | 13.6021 | 12.9726 | 12.4779 | 12.0442 | 15.295 | 15.215 | 15.1318 | 14.9971 | 14.855 | 14.7108 | 14.5582 | 14.4097 | 14.2655 | 13.6118 | 13.0939 | 12.6371
|  | ROTHESAY | HT |  |  |  |  | 16.1711 | 16.0689 | 15.9658 | 15.8595 | 15.7437 | 15.61 | 15.4279 | 15.25 | 15.0763 | 14.3584 | 13.7384 | 13.1837 | 14.3189 | 14.2179 | 14.1168 | 14.0105 | 13.8874 | 13.6926 | 13.5032 | 13.3179 | 13.1368 | 12.3832 | 11.7274 | 11.1253 | 15.2318 | 15.1203 | 14.9455 | 14.7634 | 14.5592 | 14.3582 | 14.1613 | 13.9697 | 13.7824 | 12.9971 | 12.3108 | 11.6897
|  | ROTHESAY | HE |  |  |  |  | 16.2963 | 16.2374 | 16.1711 | 16.1005 | 16.0258 | 15.9553 | 15.8868 | 15.8216 | 15.7637 | 15.5626 | 15.3858 | 15.1742 | 14.4421 | 14.3832 | 14.3179 | 14.2474 | 14.1737 | 14.1042 | 14.0358 | 13.9716 | 13.9137 | 13.7158 | 13.4653 | 13.2389 | 15.2318 | 15.1203 | 14.9455 | 14.7634 | 14.5592 | 14.3582 | 14.1613 | 13.9697 | 13.7824 | 12.9971 | 12.3108 | 11.6897
|  | ROTHESAY | CF |  |  |  |  | 16.3353 | 16.2984 | 16.2605 | 16.2216 | 16.1816 | 16.1384 | 16.0974 | 16.0553 | 16.0132 | 15.8332 | 15.7363 | 15.67 | 14.4811 | 14.4442 | 14.4063 | 14.3674 | 14.3274 | 14.2853 | 14.2442 | 14.2032 | 14.1611 | 13.9832 | 13.8884 | 13.7537 | 15.3939 | 15.3571 | 15.3192 | 15.2803 | 15.2403 | 15.1982 | 15.1571 | 15.1161 | 15.0739 | 14.8224 | 14.6076 | 14.4192
| THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | YES | 0 | -0.21368 | -0.22105 | -0.22842 | -0.23789 | -0.24947 | -0.26105 | -0.27368 | -0.28316 | -0.29368 | -0.33263 | -0.36421 | -1.2632 | -0.16 | -0.17158 | -0.18526 | -0.19684 | -0.21053 | -0.2221 | -0.23579 | -0.24632 | -0.25684 | -0.30105 | -0.33684 | -1.0695 | -0.30526 | -0.31579 | -0.32737 | -0.3379 | -0.35053 | -0.36105 | -0.37263 | -0.3821 | -0.39263 | -0.43895 | -0.47684 | -1.3768
|  | ROUSAY | EE |  |  |  |  | -0.20947 | -0.21579 | -0.22316 | -0.22947 | -0.23579 | -0.24316 | -0.25158 | -0.26 | -0.26737 | -0.30211 | -0.32526 | -1.2158 | -0.15158 | -0.16105 | -0.17263 | -0.18316 | -0.19263 | -0.20211 | -0.21053 | -0.22 | -0.22947 | -0.26632 | -0.29263 | -1.0189 | -0.29684 | -0.30632 | -0.31684 | -0.32526 | -0.33474 | -0.34421 | -0.35158 | -0.36 | -0.36737 | -0.40105 | -0.42947 | -1.3284
|  | ROUSAY | HT |  |  |  |  | -0.21368 | -0.22105 | -0.22842 | -0.23789 | -0.24947 | -0.26105 | -0.27368 | -0.28316 | -0.29368 | -0.33263 | -0.36421 | -1.2632 | -0.16 | -0.17158 | -0.18526 | -0.19684 | -0.21053 | -0.2221 | -0.23579 | -0.24632 | -0.25684 | -0.30105 | -0.33684 | -1.0695 | -0.30526 | -0.31579 | -0.32737 | -0.3379 | -0.35053 | -0.36105 | -0.37263 | -0.3821 | -0.39263 | -0.43895 | -0.47684 | -1.3768
|  | ROUSAY | HE |  |  |  |  | -0.20211 | -0.20632 | -0.21158 | -0.21684 | -0.2221 | -0.22632 | -0.23053 | -0.23684 | -0.24 | -0.25474 | -0.26526 | -0.70947 | -0.13895 | -0.14526 | -0.15263 | -0.15895 | -0.16737 | -0.17263 | -0.17895 | -0.18632 | -0.19053 | -0.21263 | -0.22632 | -0.58842 | -0.30526 | -0.31579 | -0.32737 | -0.3379 | -0.35053 | -0.36105 | -0.37263 | -0.3821 | -0.39263 | -0.43895 | -0.47684 | -1.3768
|  | ROUSAY | CF |  |  |  |  | -0.19895 | -0.20105 | -0.20316 | -0.20632 | -0.20842 | -0.21158 | -0.21474 | -0.21684 | -0.21895 | -0.23053 | -0.23789 | -0.24632 | -0.13368 | -0.13684 | -0.14105 | -0.14632 | -0.14947 | -0.15368 | -0.15895 | -0.1621 | -0.16632 | -0.18526 | -0.19789 | -0.20737 | -0.28105 | -0.28421 | -0.28842 | -0.29263 | -0.29579 | -0.3 | -0.30421 | -0.30737 | -0.31053 | -0.32842 | -0.33895 | -0.34632
| CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | YES | 0.38 | 24.82 | 24.66 | 24.4979 | 24.3326 | 24.1379 | 23.9505 | 23.7695 | 23.5895 | 23.3379 | 22.3211 | 21.3926 | 20.5442 | 23.1442 | 22.9789 | 22.8084 | 22.5442 | 22.2337 | 21.9358 | 21.6432 | 21.3568 | 21.0768 | 20.1032 | 19.1653 | 18.3021 | 23.8137 | 23.6453 | 23.4737 | 23.3011 | 23.0989 | 22.9063 | 22.7179 | 22.4274 | 22.1295 | 21.1032 | 20.0905 | 19.1505
|  | RUTHRIESTON | EE |  |  |  |  | 24.9168 | 24.7884 | 24.6558 | 24.5158 | 24.3589 | 24.2053 | 24.0526 | 23.9095 | 23.7726 | 22.9832 | 22.3158 | 21.7095 | 23.2432 | 23.1137 | 22.9758 | 22.8316 | 22.66 | 22.4168 | 22.1768 | 21.9495 | 21.7295 | 20.7337 | 20.1211 | 19.5084 | 23.9105 | 23.7821 | 23.6421 | 23.4958 | 23.3337 | 23.1768 | 23.02 | 22.8726 | 22.7305 | 21.7568 | 21.1011 | 20.4316
|  | RUTHRIESTON | HT |  |  |  |  | 24.82 | 24.66 | 24.4979 | 24.3326 | 24.1379 | 23.9505 | 23.7695 | 23.5895 | 23.3379 | 22.3211 | 21.3926 | 20.5442 | 23.1442 | 22.9789 | 22.8084 | 22.5442 | 22.2337 | 21.9358 | 21.6432 | 21.3568 | 21.0768 | 20.1032 | 19.1653 | 18.3021 | 23.8137 | 23.6453 | 23.4737 | 23.3011 | 23.0989 | 22.9063 | 22.7179 | 22.4274 | 22.1295 | 21.1032 | 20.0905 | 19.1505
|  | RUTHRIESTON | HE |  |  |  |  | 25.0232 | 24.9274 | 24.8221 | 24.7116 | 24.58 | 24.46 | 24.3411 | 24.2295 | 24.1274 | 23.76 | 23.5442 | 23.4021 | 23.3505 | 23.2547 | 23.1495 | 23.0389 | 22.9137 | 22.7968 | 22.6832 | 22.5747 | 22.4768 | 21.9179 | 21.4979 | 21.1737 | 23.8137 | 23.6453 | 23.4737 | 23.3011 | 23.0989 | 22.9063 | 22.7179 | 22.4274 | 22.1295 | 21.1032 | 20.0905 | 19.1505
|  | RUTHRIESTON | CF |  |  |  |  | 25.0905 | 25.0316 | 24.9716 | 24.9084 | 24.8411 | 24.7737 | 24.7042 | 24.6358 | 24.5695 | 24.2768 | 24.1084 | 24.0179 | 23.4179 | 23.3589 | 23.2989 | 23.2368 | 23.1705 | 23.1053 | 23.0379 | 22.9684 | 22.9021 | 22.5621 | 22.1947 | 21.9221 | 24.0842 | 24.0253 | 23.9653 | 23.9021 | 23.8358 | 23.7674 | 23.7 | 23.6284 | 23.56 | 23.2537 | 23.0758 | 22.9747
| TAYNUILT | SALEN | MINIMUM HEADROOM | NM 57252 42849 | NO | YES | 0 | 6.8842 | 6.84 | 6.72 | 6.5874 | 6.4032 | 6.2674 | 6.2074 | 6.1442 | 6.0863 | 5.9032 | 5.7547 | 5.58 | 6.5558 | 6.5032 | 6.3663 | 6.2158 | 6.0032 | 5.8484 | 5.7832 | 5.7126 | 5.6516 | 5.4537 | 5.2916 | 5.0937 | 6.6042 | 6.5726 | 6.5179 | 6.3653 | 6.1495 | 5.9926 | 5.9274 | 5.8568 | 5.7958 | 5.5937 | 5.4295 | 5.2284
|  | SALEN | EE |  |  |  |  | 6.9021 | 6.8758 | 6.7842 | 6.66 | 6.4863 | 6.3621 | 6.3158 | 6.2716 | 6.22 | 6.04 | 5.9263 | 5.8326 | 6.5737 | 6.5484 | 6.4389 | 6.2979 | 6.0968 | 5.9558 | 5.9063 | 5.86 | 5.8042 | 5.6116 | 5.4895 | 5.3884 | 6.6221 | 6.5958 | 6.5684 | 6.4453 | 6.2411 | 6.0968 | 6.0474 | 5.9989 | 5.9421 | 5.7442 | 5.6168 | 5.5105
|  | SALEN | HT |  |  |  |  | 6.8842 | 6.84 | 6.72 | 6.5874 | 6.4032 | 6.2674 | 6.2074 | 6.1442 | 6.0863 | 5.9032 | 5.7547 | 5.58 | 6.5558 | 6.5032 | 6.3663 | 6.2158 | 6.0032 | 5.8484 | 5.7832 | 5.7126 | 5.6516 | 5.4537 | 5.2916 | 5.0937 | 6.6042 | 6.5726 | 6.5179 | 6.3653 | 6.1495 | 5.9926 | 5.9274 | 5.8568 | 5.7958 | 5.5937 | 5.4295 | 5.2284
|  | SALEN | HE |  |  |  |  | 6.9284 | 6.9095 | 6.8642 | 6.7558 | 6.5863 | 6.4705 | 6.4337 | 6.3979 | 6.3705 | 6.2811 | 6.2221 | 6.18 | 6.6 | 6.5821 | 6.5253 | 6.4011 | 6.2021 | 6.0695 | 6.0284 | 5.9895 | 5.96 | 5.8663 | 5.8032 | 5.7568 | 6.6042 | 6.5726 | 6.5179 | 6.3653 | 6.1495 | 5.9926 | 5.9274 | 5.8568 | 5.7958 | 5.5937 | 5.4295 | 5.2284
|  | SALEN | CF |  |  |  |  | 6.9442 | 6.9347 | 6.9253 | 6.9147 | 6.8558 | 6.8042 | 6.7832 | 6.7579 | 6.7295 | 6.6305 | 6.5789 | 6.5421 | 6.6158 | 6.6063 | 6.5968 | 6.5821 | 6.5126 | 6.4537 | 6.4295 | 6.4021 | 6.3695 | 6.2589 | 6.2042 | 6.1621 | 6.6653 | 6.6558 | 6.6453 | 6.6347 | 6.6253 | 6.6042 | 6.5811 | 6.5526 | 6.52 | 6.4095 | 6.3526 | 6.3105
| FORT WILLIAM | SALEN 2 | MINIMUM HEADROOM | NM 69002 65519 | YES | NO | 0 | 3.6353 | 3.5805 | 3.5268 | 3.4742 | 3.4216 | 3.3689 | 3.3205 | 3.2732 | 3.2279 | 3.0584 | 2.9121 | 2.7974 | 3.7942 | 3.7374 | 3.6805 | 3.6258 | 3.57 | 3.5163 | 3.4658 | 3.4163 | 3.3689 | 3.1995 | 3.0363 | 2.9089 | 3.7195 | 3.6626 | 3.6068 | 3.5511 | 3.4963 | 3.4426 | 3.3911 | 3.3426 | 3.2953 | 3.1353 | 2.9784 | 2.8563
|  | SALEN 2 | EE |  |  |  |  | 3.6721 | 3.63 | 3.5879 | 3.5458 | 3.5058 | 3.4647 | 3.4268 | 3.3921 | 3.3563 | 3.23 | 3.1195 | 3.0395 | 3.8332 | 3.79 | 3.7447 | 3.7016 | 3.6595 | 3.6163 | 3.5774 | 3.5405 | 3.5037 | 3.3847 | 3.2647 | 3.1742 | 3.7595 | 3.7153 | 3.6711 | 3.6279 | 3.5847 | 3.5426 | 3.5037 | 3.4668 | 3.43 | 3.3163 | 3.1984 | 3.1121
|  | SALEN 2 | HT |  |  |  |  | 3.6353 | 3.5805 | 3.5268 | 3.4742 | 3.4216 | 3.3689 | 3.3205 | 3.2732 | 3.2279 | 3.0584 | 2.9121 | 2.7974 | 3.7942 | 3.7374 | 3.6805 | 3.6258 | 3.57 | 3.5163 | 3.4658 | 3.4163 | 3.3689 | 3.1995 | 3.0363 | 2.9089 | 3.7195 | 3.6626 | 3.6068 | 3.5511 | 3.4963 | 3.4426 | 3.3911 | 3.3426 | 3.2953 | 3.1353 | 2.9784 | 2.8563
|  | SALEN 2 | HE |  |  |  |  | 3.7226 | 3.6974 | 3.6689 | 3.6416 | 3.6132 | 3.5868 | 3.5605 | 3.5374 | 3.5142 | 3.4332 | 3.3805 | 3.3437 | 3.8868 | 3.8605 | 3.8311 | 3.8026 | 3.7732 | 3.7458 | 3.7184 | 3.6942 | 3.6711 | 3.5858 | 3.53 | 3.49 | 3.7195 | 3.6626 | 3.6068 | 3.5511 | 3.4963 | 3.4426 | 3.3911 | 3.3426 | 3.2953 | 3.1353 | 2.9784 | 2.8563
|  | SALEN 2 | CF |  |  |  |  | 3.7511 | 3.7353 | 3.7205 | 3.7037 | 3.6889 | 3.6732 | 3.6574 | 3.6405 | 3.6258 | 3.5574 | 3.5111 | 3.4784 | 3.9163 | 3.9005 | 3.8847 | 3.8668 | 3.8511 | 3.8353 | 3.8184 | 3.8005 | 3.7858 | 3.7132 | 3.6637 | 3.6279 | 3.8416 | 3.8258 | 3.81 | 3.7932 | 3.7763 | 3.7605 | 3.7437 | 3.7268 | 3.7111 | 3.6395 | 3.59 | 3.5542
| THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | YES | 0 | 1.1263 | 1.1011 | 1.0747 | 1.0474 | -2.4558 | -2.5589 | -2.6589 | -2.7474 | -2.8358 | -5.6379 | -6.2832 | -6.6621 | 1.1379 | 1.1105 | 1.0842 | 1.0558 | -1.7526 | -1.8411 | -1.9253 | -2 | -2.0758 | -4.3684 | -4.9547 | -5.3347 | 1.1063 | 1.0789 | 1.0547 | 1.0274 | -2.5 | -2.6053 | -2.7053 | -2.7926 | -2.8832 | -5.7011 | -6.3453 | -6.7484
|  | SANDAY | EE |  |  |  |  | 1.1421 | 1.1179 | 1.0937 | 1.0695 | -2.4558 | -2.5589 | -2.6589 | -2.7474 | -2.8358 | -5.6379 | -6.2832 | -6.6621 | 1.1537 | 1.1305 | 1.1063 | 1.0811 | -1.7526 | -1.8411 | -1.9253 | -2 | -2.0758 | -4.3684 | -4.9547 | -5.3347 | 1.1211 | 1.0979 | 1.0726 | 1.0484 | -2.5 | -2.6053 | -2.7053 | -2.7926 | -2.8832 | -5.7011 | -6.3453 | -6.7484
|  | SANDAY | HT |  |  |  |  | 1.1263 | 1.1011 | 1.0747 | 1.0474 | -1.7821 | -1.8589 | -1.9347 | -2.0221 | -2.1116 | -4.8189 | -5.2853 | -5.5768 | 1.1379 | 1.1105 | 1.0842 | 1.0558 | -1.22 | -1.2863 | -1.3526 | -1.4274 | -1.5053 | -3.7358 | -4.2032 | -4.5126 | 1.1063 | 1.0789 | 1.0547 | 1.0274 | -1.8221 | -1.8979 | -1.9747 | -2.0632 | -2.1526 | -4.8747 | -5.3558 | -5.6863
|  | SANDAY | HE |  |  |  |  | 1.1632 | 1.1505 | 1.1368 | 1.1221 | -0.68316 | -0.75895 | -0.83263 | -0.90842 | -1.0053 | -2.5495 | -3.0053 | -3.4937 | 1.1758 | 1.1632 | 1.1495 | 1.1358 | -0.31789 | -0.38316 | -0.44421 | -0.51053 | -0.59789 | -1.88 | -2.3053 | -2.7705 | 1.1063 | 1.0789 | 1.0547 | 1.0274 | -1.8221 | -1.8979 | -1.9747 | -2.0632 | -2.1526 | -4.8747 | -5.3558 | -5.6863
|  | SANDAY | CF |  |  |  |  | 1.1747 | 1.1663 | 1.1589 | 1.1495 | -0.60526 | -0.63789 | -0.66737 | -0.69684 | -0.73474 | -0.93684 | -1.2211 | -1.4958 | 1.1832 | 1.1789 | 1.1726 | 1.1632 | -0.24737 | -0.27684 | -0.30211 | -0.32632 | -0.36421 | -0.55368 | -0.82105 | -1.1 | 1.1432 | 1.1368 | 1.1326 | 1.1263 | -0.63789 | -0.67158 | -0.70105 | -0.72947 | -0.76737 | -0.96947 | -1.2516 | -1.5516
| DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 0.19 | 7.6384 | 7.5374 | 7.4342 | 7.3311 | 7.2247 | 7.1068 | 6.9742 | 6.8216 | 6.6511 | 6.2953 | 6.0058 | 5.7595 | 6.6353 | 6.5384 | 6.4311 | 6.3237 | 6.2111 | 6.0889 | 5.9479 | 5.7826 | 5.5995 | 5.2247 | 4.9058 | 4.6332 | 7.0363 | 6.9268 | 6.8163 | 6.7058 | 6.5921 | 6.4647 | 6.3195 | 6.1489 | 5.9595 | 5.5732 | 5.2553 | 4.9816
|  | SANDBANK | EE |  |  |  |  | 7.6921 | 7.6226 | 7.5395 | 7.4532 | 7.3679 | 7.2647 | 7.1732 | 7.0732 | 6.9521 | 6.5574 | 6.3353 | 6.1532 | 6.6689 | 6.6205 | 6.5426 | 6.4542 | 6.3658 | 6.2574 | 6.1605 | 6.0542 | 5.9247 | 5.5089 | 5.2753 | 5.0784 | 7.1068 | 7.0195 | 6.9289 | 6.8384 | 6.7479 | 6.6353 | 6.5353 | 6.4268 | 6.2921 | 5.8595 | 5.6153 | 5.4111
|  | SANDBANK | HT |  |  |  |  | 7.6384 | 7.5374 | 7.4342 | 7.3311 | 7.2247 | 7.1068 | 6.9742 | 6.8216 | 6.6511 | 6.2953 | 6.0058 | 5.7595 | 6.6353 | 6.5384 | 6.4311 | 6.3237 | 6.2111 | 6.0889 | 5.9479 | 5.7826 | 5.5995 | 5.2247 | 4.9058 | 4.6332 | 7.0363 | 6.9268 | 6.8163 | 6.7058 | 6.5921 | 6.4647 | 6.3195 | 6.1489 | 5.9595 | 5.5732 | 5.2553 | 4.9816
|  | SANDBANK | HE |  |  |  |  | 7.7405 | 7.7058 | 7.67 | 7.63 | 7.57 | 7.4711 | 7.3805 | 7.2711 | 7.1795 | 7.0058 | 6.8921 | 6.8068 | 6.7174 | 6.6837 | 6.6479 | 6.6079 | 6.5668 | 6.4721 | 6.3732 | 6.2553 | 6.1574 | 5.9784 | 5.8584 | 5.7679 | 7.0363 | 6.9268 | 6.8163 | 6.7058 | 6.5921 | 6.4647 | 6.3195 | 6.1489 | 5.9595 | 5.5732 | 5.2553 | 4.9816
|  | SANDBANK | CF |  |  |  |  | 7.7721 | 7.7542 | 7.7353 | 7.7163 | 7.6963 | 7.6763 | 7.65 | 7.6163 | 7.5837 | 7.3763 | 7.2742 | 7.2016 | 6.7489 | 6.7311 | 6.7121 | 6.6932 | 6.6732 | 6.6542 | 6.6342 | 6.6142 | 6.5889 | 6.3658 | 6.2595 | 6.1805 | 7.2047 | 7.1868 | 7.1668 | 7.1479 | 7.1205 | 7.0847 | 7.0489 | 7.0132 | 6.9784 | 6.7468 | 6.6363 | 6.5542
| SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 0 | 3.5432 | 3.4526 | 8.1242 | 8.0368 | 7.9232 | 7.8137 | 7.7063 | 7.5947 | 7.4863 | 7.0684 | 6.7558 | 6.5274 | 3.2663 | 3.1684 | 7.4295 | 7.3337 | 7.2189 | 7.1074 | 6.9979 | 6.8884 | 6.78 | 6.3579 | 6.0295 | 5.7768 | 3.3379 | 3.2453 | 7.7095 | 7.6137 | 7.4937 | 7.3768 | 7.2632 | 7.1484 | 7.0337 | 6.5832 | 6.2379 | 5.9768
|  | SANDWICK | EE |  |  |  |  | 3.6 | 3.5274 | 8.2137 | 8.14 | 8.0389 | 7.9326 | 7.8284 | 7.7337 | 7.64 | 7.1937 | 6.8158 | 6.6095 | 3.3316 | 3.2526 | 7.5316 | 7.4516 | 7.3516 | 7.2495 | 7.1505 | 7.0568 | 6.9663 | 6.5379 | 6.1842 | 5.9705 | 3.3989 | 3.3232 | 7.8074 | 7.7305 | 7.6253 | 7.5158 | 7.4084 | 7.3095 | 7.2137 | 6.7442 | 6.3463 | 6.1168
|  | SANDWICK | HT |  |  |  |  | 3.5432 | 3.4526 | 8.1242 | 8.0368 | 7.9232 | 7.8137 | 7.7063 | 7.5947 | 7.4863 | 7.0684 | 6.7558 | 6.5274 | 3.2663 | 3.1684 | 7.4295 | 7.3337 | 7.2189 | 7.1074 | 6.9979 | 6.8884 | 6.78 | 6.3579 | 6.0295 | 5.7768 | 3.3379 | 3.2453 | 7.7095 | 7.6137 | 7.4937 | 7.3768 | 7.2632 | 7.1484 | 7.0337 | 6.5832 | 6.2379 | 5.9768
|  | SANDWICK | HE |  |  |  |  | 3.6811 | 3.6347 | 8.3484 | 8.3 | 8.2168 | 8.1421 | 8.0695 | 7.9989 | 7.9326 | 7.6568 | 7.4411 | 7.2411 | 3.3916 | 3.3621 | 7.6832 | 7.6305 | 7.5516 | 7.4811 | 7.4126 | 7.3453 | 7.2832 | 7.0274 | 6.8284 | 6.6505 | 3.3379 | 3.2453 | 7.7095 | 7.6137 | 7.4937 | 7.3768 | 7.2632 | 7.1484 | 7.0337 | 6.5832 | 6.2379 | 5.9768
|  | SANDWICK | CF |  |  |  |  | 3.7253 | 3.6979 | 8.4295 | 8.4011 | 8.3611 | 8.3211 | 8.2821 | 8.2442 | 8.2105 | 8.0316 | 7.8768 | 7.7642 | 3.4189 | 3.4032 | 7.7474 | 7.7305 | 7.6989 | 7.6589 | 7.6211 | 7.5821 | 7.5463 | 7.3663 | 7.2179 | 7.1063 | 3.4989 | 3.4832 | 8.0263 | 8.0021 | 7.9611 | 7.92 | 7.88 | 7.8411 | 7.8063 | 7.6221 | 7.4621 | 7.3442
| SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | 0 | 2.2274 | 2.0474 | 8.6158 | 8.4874 | 8.2326 | 7.9811 | 7.7316 | 7.4568 | 7.18 | 5.6158 | 3.3884 | 1.7537 | 1.5326 | 1.3326 | 7.48 | 7.3421 | 7.1032 | 6.8674 | 6.6347 | 6.3842 | 6.1284 | 4.68 | 2.5305 | 0.85895 | 1.68 | 1.4789 | 7.8253 | 7.6863 | 7.4253 | 7.1684 | 6.9147 | 6.6358 | 6.3537 | 4.7305 | 2.3253 | 0.50737
|  | SCALLOWAY | EE |  |  |  |  | 2.3411 | 2.1821 | 8.7695 | 8.5853 | 8.3253 | 8.0347 | 7.74 | 7.48 | 7.2189 | 5.6158 | 3.3884 | 1.7537 | 1.6642 | 1.4874 | 7.6579 | 7.4505 | 7.2147 | 6.9537 | 6.6916 | 6.4589 | 6.2242 | 4.7505 | 2.5968 | 0.85895 | 1.8074 | 1.6326 | 8 | 7.7926 | 7.5295 | 7.2379 | 6.9411 | 6.6789 | 6.4158 | 4.7305 | 2.3253 | 0.50737
|  | SCALLOWAY | HT |  |  |  |  | 2.2274 | 2.0474 | 8.6158 | 8.4874 | 8.2326 | 7.9811 | 7.7316 | 7.4568 | 7.18 | 5.6863 | 3.66 | 2.2874 | 1.5326 | 1.3326 | 7.48 | 7.3421 | 7.1032 | 6.8674 | 6.6347 | 6.3842 | 6.1284 | 4.68 | 2.5305 | 1.0368 | 1.68 | 1.4789 | 7.8253 | 7.6863 | 7.4253 | 7.1684 | 6.9147 | 6.6358 | 6.3537 | 4.7705 | 2.5211 | 0.95579
|  | SCALLOWAY | HE |  |  |  |  | 2.4074 | 2.36 | 9.0116 | 8.8958 | 8.5937 | 8.3558 | 8.1453 | 7.94 | 7.74 | 6.3653 | 4.6842 | 2.8842 | 1.7716 | 1.6832 | 7.9232 | 7.7916 | 7.5074 | 7.2863 | 7.1021 | 6.9189 | 6.74 | 5.4137 | 3.7274 | 1.9179 | 1.68 | 1.4789 | 7.8253 | 7.6863 | 7.4253 | 7.1684 | 6.9147 | 6.6358 | 6.3537 | 4.7705 | 2.5211 | 0.95579
|  | SCALLOWAY | CF |  |  |  |  | 2.4453 | 2.4221 | 9.1568 | 9.1221 | 8.9947 | 8.8747 | 8.7642 | 8.6779 | 8.6032 | 7.8895 | 6.8295 | 5.6895 | 1.8095 | 1.7863 | 8.1137 | 8.0442 | 7.9221 | 7.8042 | 7.6979 | 7.6179 | 7.5463 | 6.8084 | 5.7316 | 4.5316 | 1.9042 | 1.8811 | 8.4168 | 8.3895 | 8.2568 | 8.1284 | 8.0147 | 7.9263 | 7.8495 | 7.0684 | 5.9316 | 4.6642
| TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0 | 0.11789 | 0.11474 | 0.11368 | 0.11158 | 0.10947 | 0.10737 | 0.10526 | 0.10316 | 0.10105 | 0.094737 | 0.089474 | 0.08421 | 0.10947 | 0.10737 | 0.10632 | 0.10526 | 0.10421 | 0.10105 | 0.1 | 0.097895 | 0.095789 | 0.088421 | 0.082105 | 0.076842 | 0.11158 | 0.10842 | 0.10632 | 0.10421 | 0.10211 | 0.098947 | 0.096842 | 0.094737 | 0.093684 | 0.085263 | 0.08 | 0.073684
|  | SCAMMADALE | EE |  |  |  |  | 0.11895 | 0.11684 | 0.11474 | 0.11368 | 0.11263 | 0.11053 | 0.10842 | 0.10842 | 0.10737 | 0.1 | 0.096842 | 0.092632 | 0.10947 | 0.10842 | 0.10737 | 0.10632 | 0.10526 | 0.10421 | 0.10316 | 0.10211 | 0.10105 | 0.094737 | 0.090526 | 0.086316 | 0.11158 | 0.11053 | 0.10842 | 0.10632 | 0.10526 | 0.10316 | 0.10105 | 0.1 | 0.098947 | 0.092632 | 0.088421 | 0.083158
|  | SCAMMADALE | HT |  |  |  |  | 0.11789 | 0.11474 | 0.11368 | 0.11158 | 0.10947 | 0.10737 | 0.10526 | 0.10316 | 0.10105 | 0.094737 | 0.089474 | 0.08421 | 0.10947 | 0.10737 | 0.10632 | 0.10526 | 0.10421 | 0.10105 | 0.1 | 0.097895 | 0.095789 | 0.088421 | 0.082105 | 0.076842 | 0.11158 | 0.10842 | 0.10632 | 0.10421 | 0.10211 | 0.098947 | 0.096842 | 0.094737 | 0.093684 | 0.085263 | 0.08 | 0.073684
|  | SCAMMADALE | HE |  |  |  |  | 0.12105 | 0.12105 | 0.11895 | 0.11789 | 0.11684 | 0.11579 | 0.11474 | 0.11263 | 0.11263 | 0.10947 | 0.10737 | 0.10526 | 0.11053 | 0.11053 | 0.10947 | 0.10842 | 0.10842 | 0.10737 | 0.10632 | 0.10526 | 0.10526 | 0.10316 | 0.10211 | 0.1 | 0.11158 | 0.10842 | 0.10632 | 0.10421 | 0.10211 | 0.098947 | 0.096842 | 0.094737 | 0.093684 | 0.085263 | 0.08 | 0.073684
|  | SCAMMADALE | CF |  |  |  |  | 0.12211 | 0.12211 | 0.12105 | 0.12105 | 0.12105 | 0.11895 | 0.11895 | 0.11789 | 0.11684 | 0.11474 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.11053 | 0.11053 | 0.10947 | 0.10947 | 0.10947 | 0.10842 | 0.10737 | 0.10632 | 0.10632 | 0.11474 | 0.11474 | 0.11368 | 0.11368 | 0.11368 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10842 | 0.10526 | 0.10421
| ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 1.582 | 13.7122 | 13.3785 | 13.0112 | 12.6143 | 12.1227 | 11.6522 | 11.1891 | 10.7259 | 10.2638 | 8.2512 | 7.2638 | 6.648 | 12.0875 | 11.7043 | 11.2843 | 10.8285 | 10.2959 | 9.7875 | 9.2875 | 8.7875 | 8.2969 | 6.1338 | 5.0938 | 4.4391 | 12.8004 | 12.4088 | 11.9793 | 11.5141 | 10.9625 | 10.4362 | 9.9172 | 9.3972 | 8.8856 | 6.633 | 5.5477 | 4.8709
|  | SCONE | EE |  |  |  |  | 13.8564 | 13.588 | 13.1869 | 12.9417 | 12.5238 | 12.0933 | 11.6701 | 11.2648 | 10.8606 | 8.8985 | 7.8975 | 7.3996 | 12.2559 | 11.9348 | 11.4643 | 11.1885 | 10.7264 | 10.2643 | 9.8127 | 9.378 | 8.9412 | 6.8591 | 5.8569 | 5.3422 | 12.9709 | 12.6435 | 12.1604 | 11.8793 | 11.3962 | 10.9119 | 10.4393 | 9.9825 | 9.5256 | 7.3351 | 6.2519 | 5.7077
|  | SCONE | HT |  |  |  |  | 13.7122 | 13.3785 | 13.0112 | 12.6143 | 12.1227 | 11.6522 | 11.1891 | 10.7259 | 10.2638 | 8.2512 | 7.2638 | 6.648 | 12.0875 | 11.7043 | 11.2843 | 10.8285 | 10.2959 | 9.7875 | 9.2875 | 8.7875 | 8.2969 | 6.1338 | 5.0938 | 4.4391 | 12.8004 | 12.4088 | 11.9793 | 11.5141 | 10.9625 | 10.4362 | 9.9172 | 9.3972 | 8.8856 | 6.633 | 5.5477 | 4.8709
|  | SCONE | HE |  |  |  |  | 14.0396 | 13.8364 | 13.5933 | 13.3122 | 12.9448 | 12.5912 | 12.2322 | 11.8785 | 11.5343 | 9.9554 | 9.308 | 8.9227 | 12.4706 | 12.218 | 11.9285 | 11.6012 | 11.1917 | 10.798 | 10.4096 | 10.0285 | 9.6538 | 7.9496 | 7.2948 | 6.9369 | 12.8004 | 12.4088 | 11.9793 | 11.5141 | 10.9625 | 10.4362 | 9.9172 | 9.3972 | 8.8856 | 6.633 | 5.5477 | 4.8709
|  | SCONE | CF |  |  |  |  | 14.1775 | 14.068 | 13.9501 | 13.8227 | 13.6585 | 13.4869 | 13.3048 | 13.1227 | 12.9312 | 11.9101 | 11.4448 | 11.1922 | 12.6369 | 12.5022 | 12.3538 | 12.1959 | 12.0085 | 11.8138 | 11.6075 | 11.3969 | 11.1759 | 10.038 | 9.5548 | 9.3001 | 13.3604 | 13.2214 | 13.0709 | 12.9077 | 12.713 | 12.5098 | 12.2951 | 12.0772 | 11.8488 | 10.6646 | 10.1488 | 9.873
| THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | YES | 0 | 1 | 0.98316 | 0.96842 | 0.95158 | 0.82737 | 0.67579 | 0.51684 | 0.36316 | 0.14 | -1.1726 | -2.6958 | -3.8358 | 0.96421 | 0.94842 | 0.93158 | 0.91474 | 0.82 | 0.68105 | 0.53368 | 0.39474 | 0.17789 | -1.0284 | -2.52 | -3.7558 | 0.96421 | 0.94632 | 0.92947 | 0.91158 | 0.78842 | 0.63368 | 0.47474 | 0.33789 | 0.12421 | -1.3411 | -3 | -4.2916
|  | SHAPINSAY | EE |  |  |  |  | 1.0074 | 0.98947 | 0.97263 | 0.95474 | 0.82737 | 0.67579 | 0.52105 | 0.38526 | 0.20526 | -1.1726 | -2.6958 | -3.8358 | 0.97263 | 0.95579 | 0.93895 | 0.92316 | 0.82 | 0.69474 | 0.56737 | 0.45579 | 0.29579 | -1.0284 | -2.52 | -3.7558 | 0.97263 | 0.95368 | 0.93474 | 0.91684 | 0.78842 | 0.63368 | 0.47474 | 0.33789 | 0.15053 | -1.3411 | -3 | -4.2916
|  | SHAPINSAY | HT |  |  |  |  | 1 | 0.98316 | 0.96842 | 0.95158 | 0.84421 | 0.73789 | 0.62737 | 0.46526 | 0.2 | -1.0242 | -2.4011 | -3.3316 | 0.96421 | 0.94842 | 0.93158 | 0.91474 | 0.83053 | 0.74105 | 0.64737 | 0.50421 | 0.24421 | -1.0011 | -2.4926 | -3.54 | 0.96421 | 0.94632 | 0.92947 | 0.91158 | 0.80421 | 0.69579 | 0.58211 | 0.41474 | 0.12421 | -1.2242 | -2.7905 | -3.8642
|  | SHAPINSAY | HE |  |  |  |  | 1.0168 | 1.0095 | 1.0021 | 0.99474 | 0.83474 | 0.67789 | 0.51684 | 0.36316 | 0.14 | -0.80737 | -1.98 | -3.2589 | 0.98421 | 0.97684 | 0.96842 | 0.96105 | 0.82316 | 0.68105 | 0.53368 | 0.39474 | 0.17789 | -0.73789 | -1.9284 | -3.2295 | 0.96421 | 0.94632 | 0.92947 | 0.91158 | 0.80421 | 0.69579 | 0.58211 | 0.41474 | 0.12421 | -1.2242 | -2.7905 | -3.8642
|  | SHAPINSAY | CF |  |  |  |  | 1.0211 | 1.0158 | 1.0126 | 1.0074 | 0.95684 | 0.91368 | 0.82316 | 0.72737 | 0.62316 | 0.13684 | -0.60105 | -1.4147 | 0.98947 | 0.98421 | 0.97895 | 0.97474 | 0.93474 | 0.89684 | 0.80842 | 0.71053 | 0.59789 | 0.10737 | -0.64632 | -1.52 | 0.98947 | 0.98316 | 0.97895 | 0.97368 | 0.92105 | 0.87474 | 0.77684 | 0.67158 | 0.55368 | 0.022105 | -0.79684 | -1.7179
| BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 0 | -1.5168 | -1.5632 | -1.6116 | -1.6611 | -1.7116 | -1.7558 | -1.8 | -1.8463 | -1.8926 | -2.1042 | -2.2789 | -2.4537 | -1.3968 | -1.4421 | -1.4895 | -1.5368 | -1.5863 | -1.6305 | -1.6737 | -1.72 | -1.7653 | -1.9747 | -2.1474 | -2.3211 | -1.5389 | -1.5853 | -1.6347 | -1.6842 | -1.7347 | -1.7811 | -1.8263 | -1.8737 | -1.92 | -2.1368 | -2.3147 | -2.4926
|  | SHIELDAIG | EE |  |  |  |  | -1.5168 | -1.5632 | -1.6116 | -1.6611 | -1.7116 | -1.7558 | -1.8 | -1.8463 | -1.8926 | -2.1042 | -2.2789 | -2.4537 | -1.3968 | -1.4421 | -1.4895 | -1.5368 | -1.5863 | -1.6305 | -1.6737 | -1.72 | -1.7653 | -1.9747 | -2.1474 | -2.3211 | -1.5389 | -1.5853 | -1.6347 | -1.6842 | -1.7347 | -1.7811 | -1.8263 | -1.8737 | -1.92 | -2.1368 | -2.3147 | -2.4926
|  | SHIELDAIG | HT |  |  |  |  | -1.4926 | -1.5095 | -1.5274 | -1.5453 | -1.5642 | -1.5821 | -1.6 | -1.6179 | -1.6347 | -1.7147 | -1.7895 | -1.8653 | -1.3747 | -1.3926 | -1.4105 | -1.4295 | -1.4505 | -1.4695 | -1.4884 | -1.5074 | -1.5263 | -1.6126 | -1.6937 | -1.7737 | -1.5137 | -1.5326 | -1.5505 | -1.5684 | -1.5874 | -1.6063 | -1.6263 | -1.6442 | -1.6621 | -1.7463 | -1.8242 | -1.9032
|  | SHIELDAIG | HE |  |  |  |  | -1.4842 | -1.4989 | -1.5147 | -1.5305 | -1.5463 | -1.5621 | -1.5779 | -1.5926 | -1.6084 | -1.68 | -1.7495 | -1.8189 | -1.3642 | -1.3789 | -1.3947 | -1.4105 | -1.4263 | -1.4411 | -1.4568 | -1.4716 | -1.4874 | -1.56 | -1.6305 | -1.6989 | -1.5137 | -1.5326 | -1.5505 | -1.5684 | -1.5874 | -1.6063 | -1.6263 | -1.6442 | -1.6621 | -1.7463 | -1.8242 | -1.9032
|  | SHIELDAIG | CF |  |  |  |  | -1.4716 | -1.4768 | -1.4811 | -1.4863 | -1.4895 | -1.4947 | -1.4989 | -1.5042 | -1.5074 | -1.5263 | -1.54 | -1.5505 | -1.3516 | -1.3579 | -1.3611 | -1.3663 | -1.3695 | -1.3758 | -1.3789 | -1.3853 | -1.3884 | -1.4095 | -1.4253 | -1.4389 | -1.4916 | -1.4979 | -1.5021 | -1.5074 | -1.5116 | -1.5168 | -1.52 | -1.5253 | -1.5284 | -1.5495 | -1.5632 | -1.5758
| SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | NO | 0 | 2.1158 | 1.6116 | 1.0832 | 0.53263 | -0.082105 | -0.64421 | -1.2168 | -1.7926 | -2.3779 | -5.1095 | -7.5074 | -9.6832 | 2.0758 | 1.58 | 1.0695 | 0.54632 | -0.031579 | -0.55684 | -1.0895 | -1.6284 | -2.1758 | -4.8179 | -7.16 | -9.3526 | 2.0421 | 1.54 | 1.0105 | 0.46 | -0.1621 | -0.73053 | -1.3095 | -1.8905 | -2.4811 | -5.3011 | -7.8253 | -10.1305
|  | SHIN | EE |  |  |  |  | 2.1158 | 1.6116 | 1.0832 | 0.53263 | -0.082105 | -0.64421 | -1.2168 | -1.7926 | -2.3779 | -5.1095 | -7.5074 | -9.6832 | 2.0758 | 1.58 | 1.0695 | 0.54632 | -0.031579 | -0.55684 | -1.0895 | -1.6284 | -2.1758 | -4.8179 | -7.16 | -9.3526 | 2.0421 | 1.54 | 1.0105 | 0.46 | -0.1621 | -0.73053 | -1.3095 | -1.8905 | -2.4811 | -5.3011 | -7.8253 | -10.1305
|  | SHIN | HT |  |  |  |  | 2.4326 | 2.2821 | 2.1284 | 1.9695 | 1.7663 | 1.5621 | 1.3589 | 1.1442 | 0.92211 | -0.12842 | -1.3758 | -2.4253 | 2.3884 | 2.24 | 2.0842 | 1.9284 | 1.7379 | 1.5453 | 1.3558 | 1.1558 | 0.94 | -0.13158 | -1.2905 | -2.3642 | 2.3579 | 2.2011 | 2.0442 | 1.8874 | 1.6842 | 1.48 | 1.2747 | 1.0558 | 0.81684 | -0.39684 | -1.8453 | -3.0484
|  | SHIN | HE |  |  |  |  | 2.4516 | 2.3032 | 2.1558 | 2.0032 | 1.7916 | 1.5853 | 1.3737 | 1.1674 | 0.96105 | -0.068421 | -1.1568 | -2.3821 | 2.4126 | 2.2621 | 2.1158 | 1.9642 | 1.7695 | 1.5747 | 1.3726 | 1.1768 | 0.97158 | -0.038947 | -1.1137 | -2.2358 | 2.3579 | 2.2011 | 2.0442 | 1.8874 | 1.6842 | 1.48 | 1.2747 | 1.0558 | 0.81684 | -0.39684 | -1.8453 | -3.0484
|  | SHIN | CF |  |  |  |  | 2.5484 | 2.5147 | 2.48 | 2.4453 | 2.3863 | 2.3305 | 2.2716 | 2.2074 | 2.1347 | 1.78 | 1.3021 | 0.79579 | 2.5042 | 2.4705 | 2.4389 | 2.4063 | 2.3526 | 2.3021 | 2.2463 | 2.1905 | 2.1221 | 1.8011 | 1.38 | 0.89789 | 2.4884 | 2.4463 | 2.4084 | 2.3705 | 2.3105 | 2.2526 | 2.1884 | 2.1232 | 2.0337 | 1.6326 | 1.1021 | 0.53053
| FORT WILLIAM | SHONA BEG | MINIMUM HEADROOM | NM 67173 74363 | YES | NO | 0 | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10211 | 0.10105 | 0.098947 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.096842 | 0.094737 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.098947 | 0.096842
|  | SHONA BEG | EE |  |  |  |  | 0.10737 | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10105 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.097895 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.1
|  | SHONA BEG | HT |  |  |  |  | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10211 | 0.10105 | 0.098947 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.096842 | 0.094737 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.098947 | 0.096842
|  | SHONA BEG | HE |  |  |  |  | 0.10842 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.098947 | 0.096842
|  | SHONA BEG | CF |  |  |  |  | 0.10842 | 0.10842 | 0.10842 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421
| KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 0.041 | 33.2927 | 33.0843 | 32.8706 | 32.5632 | 32.0464 | 31.4369 | 30.8232 | 30.1243 | 29.3243 | 26.9537 | 25.2148 | 23.6443 | 31.8443 | 31.6401 | 31.4316 | 31.119 | 30.6316 | 30.0274 | 29.4201 | 28.7211 | 27.8716 | 25.4695 | 23.9979 | 22.1264 | 29.3053 | 29.0506 | 28.7937 | 28.5348 | 28.1127 | 27.6653 | 27.2232 | 26.7358 | 26.2201 | 24.5369 | 22.8601 | 21.9832
|  | SKENE | EE |  |  |  |  | 33.419 | 33.2464 | 33.0674 | 32.8832 | 32.5053 | 31.9864 | 31.4158 | 30.8864 | 30.3253 | 27.2485 | 25.2148 | 23.6443 | 31.9706 | 31.8053 | 31.6337 | 31.4558 | 31.159 | 30.7032 | 30.1853 | 29.6779 | 29.1232 | 26.019 | 24.1843 | 22.5095 | 29.4664 | 29.2579 | 29.0422 | 28.8243 | 28.4169 | 27.979 | 27.5232 | 27.1127 | 26.6937 | 24.5506 | 22.8601 | 21.9832
|  | SKENE | HT |  |  |  |  | 33.2927 | 33.0843 | 32.8706 | 32.5632 | 32.0464 | 31.4369 | 30.8232 | 30.1243 | 29.3243 | 26.9537 | 25.479 | 23.7927 | 31.8443 | 31.6401 | 31.4316 | 31.119 | 30.6316 | 30.0274 | 29.4201 | 28.7211 | 27.8716 | 25.4695 | 23.9979 | 22.1264 | 29.3053 | 29.0506 | 28.7937 | 28.5348 | 28.1127 | 27.6653 | 27.2232 | 26.7358 | 26.2201 | 24.5369 | 23.4801 | 22.2853
|  | SKENE | HE |  |  |  |  | 33.5832 | 33.4737 | 33.3548 | 33.2285 | 32.9032 | 32.619 | 32.3379 | 31.9927 | 31.5706 | 29.7201 | 27.9169 | 25.5979 | 32.1348 | 32.0264 | 31.9085 | 31.7843 | 31.5611 | 31.3622 | 31.1664 | 30.8337 | 30.4337 | 28.6274 | 26.8085 | 24.3822 | 29.3053 | 29.0506 | 28.7937 | 28.5348 | 28.1127 | 27.6653 | 27.2232 | 26.7358 | 26.2201 | 24.5369 | 23.4801 | 22.2853
|  | SKENE | CF |  |  |  |  | 33.6832 | 33.6243 | 33.5632 | 33.5022 | 33.3674 | 33.2411 | 33.1179 | 33.0011 | 32.9011 | 32.1074 | 30.9464 | 29.4864 | 32.2348 | 32.1769 | 32.1169 | 32.0569 | 31.9611 | 31.8674 | 31.7769 | 31.6885 | 31.6085 | 30.8737 | 29.7116 | 28.0769 | 29.8095 | 29.7379 | 29.6622 | 29.5853 | 29.4285 | 29.2811 | 29.1369 | 28.9969 | 28.8716 | 28.1401 | 27.3769 | 26.6569
| BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | 0 | 7.0263 | 6.9232 | 6.8168 | 6.6853 | 6.3821 | 6.0821 | 5.7842 | 5.4937 | 5.2242 | 4.5411 | 3.7358 | 2.7189 | 6.5463 | 6.4337 | 6.3179 | 6.1768 | 5.8747 | 5.5695 | 5.2589 | 4.9632 | 4.6916 | 4.0579 | 3.2232 | 2.2558 | 6.6116 | 6.5042 | 6.3926 | 6.2579 | 5.9337 | 5.6042 | 5.2758 | 4.9589 | 4.6663 | 3.9558 | 3.0674 | 1.9863
|  | SKULAMUS | EE |  |  |  |  | 7.0747 | 7 | 6.9074 | 6.7937 | 6.5895 | 6.3684 | 6.0516 | 5.7747 | 5.5263 | 4.5411 | 3.7358 | 2.7189 | 6.6126 | 6.52 | 6.4211 | 6.2958 | 6.1095 | 5.9084 | 5.5905 | 5.3095 | 5.0642 | 4.14 | 3.4263 | 2.32 | 6.6747 | 6.5842 | 6.4874 | 6.3674 | 6.1579 | 5.9326 | 5.5895 | 5.2874 | 5.0189 | 3.9779 | 3.1421 | 1.9863
|  | SKULAMUS | HT |  |  |  |  | 7.0263 | 6.9232 | 6.8168 | 6.6853 | 6.3821 | 6.0821 | 5.7842 | 5.4937 | 5.2242 | 4.5442 | 3.7421 | 2.8716 | 6.5463 | 6.4337 | 6.3179 | 6.1768 | 5.8747 | 5.5695 | 5.2589 | 4.9632 | 4.6916 | 4.0579 | 3.2232 | 2.2558 | 6.6116 | 6.5042 | 6.3926 | 6.2579 | 5.9337 | 5.6042 | 5.2758 | 4.9589 | 4.6663 | 3.9558 | 3.0674 | 2.0737
|  | SKULAMUS | HE |  |  |  |  | 7.1179 | 7.0895 | 7.0484 | 6.9632 | 6.7726 | 6.6021 | 6.3495 | 6.1168 | 5.9168 | 5.2042 | 4.4863 | 3.4063 | 6.6832 | 6.6411 | 6.5716 | 6.4747 | 6.3053 | 6.1484 | 5.8926 | 5.6579 | 5.4579 | 4.7832 | 4.0853 | 2.9737 | 6.6116 | 6.5042 | 6.3926 | 6.2579 | 5.9337 | 5.6042 | 5.2758 | 4.9589 | 4.6663 | 3.9558 | 3.0674 | 2.0737
|  | SKULAMUS | CF |  |  |  |  | 7.1453 | 7.1295 | 7.1137 | 7.0979 | 7.0358 | 6.9589 | 6.8789 | 6.7589 | 6.6684 | 6.2242 | 5.7495 | 5.0474 | 6.7126 | 6.6968 | 6.68 | 6.6442 | 6.5705 | 6.4968 | 6.4211 | 6.2937 | 6.1979 | 5.7547 | 5.2874 | 4.5284 | 6.8168 | 6.7842 | 6.7484 | 6.7042 | 6.6211 | 6.5411 | 6.4579 | 6.3305 | 6.2358 | 5.7621 | 5.2463 | 4.4484
| WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 0.145 | 41.575 | 41.0297 | 40.3845 | 39.7297 | 38.9445 | 37.9371 | 36.9171 | 35.7718 | 34.4161 | 29.375 | 25.1382 | 22.7455 | 40.1182 | 39.8434 | 39.5045 | 38.8782 | 38.0592 | 36.9782 | 35.8792 | 34.6403 | 33.1371 | 27.5276 | 22.7045 | 19.9782 | 41.3371 | 41.0803 | 40.735 | 40.1876 | 39.3497 | 38.2287 | 37.0876 | 35.8003 | 34.2561 | 28.495 | 23.5982 | 20.8445
|  | SPRINGHILL | EE |  |  |  |  | 41.9497 | 41.4318 | 40.9792 | 40.4139 | 39.7255 | 39.0266 | 38.2139 | 37.4045 | 36.5424 | 31.2497 | 26.6961 | 24.175 | 40.3161 | 40.0455 | 39.8234 | 39.5308 | 38.9129 | 38.1982 | 37.3497 | 36.4961 | 35.5782 | 29.7771 | 24.7771 | 21.9213 | 41.5382 | 41.2603 | 41.0561 | 40.7561 | 40.1887 | 39.455 | 38.5634 | 37.6676 | 36.7055 | 30.6813 | 25.4718 | 22.5571
|  | SPRINGHILL | HT |  |  |  |  | 41.575 | 41.0297 | 40.3845 | 39.7297 | 38.9445 | 37.9371 | 36.9171 | 35.7718 | 34.4161 | 29.375 | 25.1382 | 22.7455 | 40.1182 | 39.8434 | 39.5045 | 38.8782 | 38.0592 | 36.9782 | 35.8792 | 34.6403 | 33.1371 | 27.5276 | 22.7045 | 19.9782 | 41.3371 | 41.0803 | 40.735 | 40.1876 | 39.3497 | 38.2287 | 37.0876 | 35.8003 | 34.2561 | 28.495 | 23.5982 | 20.8445
|  | SPRINGHILL | HE |  |  |  |  | 42.4276 | 42.0666 | 41.6739 | 41.2561 | 40.6813 | 40.0645 | 39.2666 | 38.3971 | 37.4245 | 33.2203 | 29.9129 | 27.6897 | 40.5582 | 40.3655 | 40.1582 | 39.9371 | 39.6497 | 39.2361 | 38.3771 | 37.4361 | 36.3708 | 31.7034 | 28.0192 | 25.6097 | 41.3371 | 41.0803 | 40.735 | 40.1876 | 39.3497 | 38.2287 | 37.0876 | 35.8003 | 34.2561 | 28.495 | 23.5982 | 20.8445
|  | SPRINGHILL | CF |  |  |  |  | 42.7045 | 42.495 | 42.2666 | 42.0329 | 41.7413 | 41.4539 | 41.1592 | 40.8139 | 40.4245 | 37.6782 | 35.2782 | 33.475 | 40.7118 | 40.6003 | 40.4845 | 40.3676 | 40.2276 | 40.0897 | 39.9508 | 39.8118 | 39.6245 | 36.575 | 33.8897 | 31.8497 | 41.9413 | 41.8276 | 41.7097 | 41.5887 | 41.4266 | 41.2697 | 41.1118 | 40.955 | 40.8013 | 37.735 | 34.9539 | 32.8497
| BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | YES | 0.013 | 3.7312 | 3.6565 | 3.5649 | 3.4681 | 3.2133 | 2.9312 | 2.5902 | 2.2912 | 2.0302 | 0.62384 | -2.6814 | -3.7772 | 4.4438 | 4.3502 | 4.2186 | 4.0754 | 3.8081 | 3.5428 | 3.2754 | 2.9996 | 2.7796 | 1.5975 | -1.5593 | -2.5677 | 3.7186 | 3.6249 | 3.4975 | 3.3586 | 3.0565 | 2.7575 | 2.3996 | 2.0902 | 1.827 | 0.39963 | -3.1319 | -4.1856
|  | ST CYRUS | EE |  |  |  |  | 3.7681 | 3.7017 | 3.6238 | 3.5323 | 3.2512 | 2.9312 | 2.5902 | 2.2912 | 2.0302 | 0.62384 | -2.1425 | -3.1088 | 4.4923 | 4.4133 | 4.3102 | 4.1775 | 3.8944 | 3.5859 | 3.2817 | 3.0144 | 2.7944 | 1.5975 | -0.90774 | -2.0098 | 3.7659 | 3.6849 | 3.5817 | 3.4512 | 3.1259 | 2.7596 | 2.3996 | 2.0902 | 1.827 | 0.39963 | -2.5004 | -3.6162
|  | ST CYRUS | HT |  |  |  |  | 3.7312 | 3.6565 | 3.5649 | 3.4681 | 3.2133 | 2.9449 | 2.6575 | 2.3491 | 2.0828 | 0.92805 | -2.6814 | -3.5898 | 4.4438 | 4.3502 | 4.2186 | 4.0754 | 3.8081 | 3.5428 | 3.2754 | 2.9996 | 2.7796 | 1.7333 | -1.5593 | -2.5677 | 3.7186 | 3.6249 | 3.4975 | 3.3586 | 3.0565 | 2.7575 | 2.4544 | 2.1354 | 1.8638 | 0.66279 | -3.1319 | -4.1856
|  | ST CYRUS | HE |  |  |  |  | 3.8081 | 3.7754 | 3.7344 | 3.6765 | 3.3933 | 3.1502 | 2.9091 | 2.6733 | 2.4681 | 1.3502 | -2.2151 | -3.7772 | 4.5375 | 4.4996 | 4.4438 | 4.3544 | 4.0817 | 3.8375 | 3.5996 | 3.3786 | 3.207 | 2.2102 | -0.90142 | -2.4404 | 3.7186 | 3.6249 | 3.4975 | 3.3586 | 3.0565 | 2.7575 | 2.4544 | 2.1354 | 1.8638 | 0.66279 | -3.1319 | -4.1856
|  | ST CYRUS | CF |  |  |  |  | 3.8354 | 3.8196 | 3.8028 | 3.7859 | 3.687 | 3.5849 | 3.4817 | 3.3912 | 3.3312 | 2.8281 | 1.9175 | 0.99226 | 4.5681 | 4.5523 | 4.5333 | 4.5154 | 4.4323 | 4.3249 | 4.2144 | 4.1196 | 4.0638 | 3.5144 | 2.6017 | 1.6133 | 3.8396 | 3.8238 | 3.8049 | 3.7859 | 3.6828 | 3.5617 | 3.4354 | 3.3281 | 3.2638 | 2.6459 | 1.6554 | 0.61542
| PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | NO | 0.19 | 23.2532 | 23.1247 | 22.9942 | 22.8595 | 22.8037 | 22.6489 | 22.3984 | 22.0689 | 21.6858 | 20.5426 | 19.7195 | 18.9416 | 21.6847 | 21.4447 | 21.2079 | 20.9668 | 21.0226 | 20.7079 | 20.3837 | 20.0195 | 19.5889 | 18.2942 | 17.3574 | 16.4489 | 21.05 | 20.9142 | 20.7763 | 20.6342 | 20.7037 | 20.5374 | 20.3068 | 19.9279 | 19.4784 | 18.1626 | 17.2132 | 16.2953
|  | ST MACHAR | EE |  |  |  |  | 23.3542 | 23.2605 | 23.1637 | 23.0574 | 22.9395 | 22.8216 | 22.8068 | 22.6932 | 22.5216 | 21.2595 | 20.6016 | 20.0458 | 21.8637 | 21.6837 | 21.5037 | 21.3132 | 21.1163 | 20.9195 | 21.0058 | 20.7763 | 20.53 | 19.1005 | 18.37 | 17.7247 | 21.1563 | 21.0574 | 20.9542 | 20.8426 | 20.7205 | 20.5963 | 20.7058 | 20.5858 | 20.4437 | 18.9658 | 18.2153 | 17.5605
|  | ST MACHAR | HT |  |  |  |  | 23.2532 | 23.1247 | 22.9942 | 22.8595 | 22.8037 | 22.6489 | 22.3984 | 22.0689 | 21.6858 | 20.5426 | 19.7195 | 18.9416 | 21.6847 | 21.4447 | 21.2079 | 20.9668 | 21.0226 | 20.7079 | 20.3837 | 20.0195 | 19.5889 | 18.2942 | 17.3574 | 16.4489 | 21.05 | 20.9142 | 20.7763 | 20.6342 | 20.7037 | 20.5374 | 20.3068 | 19.9279 | 19.4784 | 18.1626 | 17.2132 | 16.2953
|  | ST MACHAR | HE |  |  |  |  | 23.4026 | 23.3205 | 23.2321 | 23.1363 | 23.0279 | 22.9268 | 22.7258 | 22.6332 | 22.5479 | 21.7089 | 21.3395 | 21.0426 | 22.0174 | 21.8858 | 21.7479 | 21.6016 | 21.4426 | 21.3005 | 20.7795 | 20.5563 | 20.3153 | 19.3732 | 18.9774 | 18.6616 | 21.05 | 20.9142 | 20.7763 | 20.6342 | 20.7037 | 20.5374 | 20.3068 | 19.9279 | 19.4784 | 18.1626 | 17.2132 | 16.2953
|  | ST MACHAR | CF |  |  |  |  | 23.4405 | 23.3826 | 23.3247 | 23.2647 | 23.1995 | 23.1342 | 23.0689 | 23.0047 | 22.9405 | 22.5058 | 22.1784 | 21.9279 | 22.0858 | 21.9889 | 21.8911 | 21.7911 | 21.6868 | 21.5795 | 21.4732 | 21.3574 | 21.23 | 20.3542 | 19.9995 | 19.7205 | 21.2521 | 21.1911 | 21.1311 | 21.0679 | 21.0016 | 20.9321 | 20.8637 | 20.7974 | 20.7289 | 20.2795 | 19.9068 | 19.6111
| THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | YES | 0 | 0.74105 | 0.65158 | 0.55053 | 0.45474 | 0.35684 | 0.13684 | -0.13263 | -0.52737 | -0.91368 | -3.6432 | -3.9611 | -4.76 | 0.70526 | 0.60526 | 0.49053 | 0.38421 | 0.27579 | 0.012632 | -0.31158 | -0.76632 | -1.2116 | -3.4305 | -3.7758 | -4.4989 | 0.71474 | 0.61474 | 0.50105 | 0.39474 | 0.28526 | 0.023158 | -0.3 | -0.75474 | -1.1989 | -3.9726 | -4.32 | -5.16
|  | ST MARYS | EE |  |  |  |  | 0.8 | 0.72842 | 0.64737 | 0.56737 | 0.48737 | 0.4 | 0.26632 | 0.08421 | -0.18 | -3.3937 | -3.6358 | -4.3547 | 0.77053 | 0.69158 | 0.60105 | 0.51158 | 0.42316 | 0.32526 | 0.16737 | -0.052632 | -0.36737 | -3.1589 | -3.4263 | -4.0568 | 0.77895 | 0.70105 | 0.61053 | 0.52211 | 0.43368 | 0.33579 | 0.17789 | -0.042105 | -0.35684 | -3.7011 | -3.9695 | -4.7158
|  | ST MARYS | HT |  |  |  |  | 0.74105 | 0.65158 | 0.55053 | 0.45474 | 0.35684 | 0.13684 | -0.13263 | -0.52737 | -0.91368 | -3.6432 | -3.9611 | -4.76 | 0.70526 | 0.60526 | 0.49053 | 0.38421 | 0.27579 | 0.012632 | -0.31158 | -0.76632 | -1.2116 | -3.4305 | -3.7758 | -4.4989 | 0.71474 | 0.61474 | 0.50105 | 0.39474 | 0.28526 | 0.023158 | -0.3 | -0.75474 | -1.1989 | -3.9726 | -4.32 | -5.16
|  | ST MARYS | HE |  |  |  |  | 0.88211 | 0.83474 | 0.78421 | 0.73158 | 0.67263 | 0.60842 | 0.44421 | 0.23895 | -0.025263 | -1.7832 | -1.9337 | -2.3095 | 0.86421 | 0.81158 | 0.75579 | 0.69895 | 0.63368 | 0.56105 | 0.36105 | 0.11053 | -0.21053 | -1.7632 | -1.9284 | -2.2653 | 0.71474 | 0.61474 | 0.50105 | 0.39474 | 0.28526 | 0.023158 | -0.3 | -0.75474 | -1.1989 | -3.9726 | -4.32 | -5.16
|  | ST MARYS | CF |  |  |  |  | 0.92632 | 0.89895 | 0.87263 | 0.84316 | 0.81263 | 0.77579 | 0.74421 | 0.69368 | 0.62105 | 0.0073684 | -0.096842 | -0.19158 | 0.91263 | 0.88316 | 0.85368 | 0.82 | 0.78632 | 0.74421 | 0.70842 | 0.64947 | 0.56105 | -0.18526 | -0.30211 | -0.40947 | 0.91789 | 0.88842 | 0.86 | 0.82737 | 0.79368 | 0.75368 | 0.71789 | 0.65895 | 0.57158 | -0.17474 | -0.29053 | -0.39789
| WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | YES | 0 | 18.2663 | 18.0779 | 17.7211 | 17.2453 | 16.64 | 16.4516 | 16.3379 | 16.2011 | 16.0537 | 15.4558 | 14.9337 | 14.4305 | 17.5232 | 17.2274 | 16.8579 | 16.3 | 15.6147 | 15.3863 | 15.2674 | 15.1516 | 14.9968 | 14.3579 | 13.7905 | 13.2305 | 17.5684 | 17.4695 | 17.1021 | 16.4916 | 15.7947 | 15.56 | 15.4379 | 15.3211 | 15.1695 | 14.5189 | 13.9432 | 13.3811
|  | ST NICHOLAS | EE |  |  |  |  | 18.3495 | 18.2611 | 18.0084 | 17.5905 | 17.02 | 16.4516 | 16.3379 | 16.2284 | 16.12 | 15.6105 | 15.2168 | 14.8695 | 17.5989 | 17.4926 | 17.1505 | 16.6811 | 16.0326 | 15.3863 | 15.2674 | 15.1516 | 15.0389 | 14.5 | 14.0779 | 13.6916 | 17.6295 | 17.5705 | 17.48 | 16.8779 | 16.2179 | 15.56 | 15.4379 | 15.3211 | 15.2053 | 14.6547 | 14.2221 | 13.8337
|  | ST NICHOLAS | HT |  |  |  |  | 18.2663 | 18.0779 | 17.7211 | 17.2453 | 16.64 | 16.4916 | 16.3442 | 16.2011 | 16.0537 | 15.4558 | 14.9337 | 14.4305 | 17.5232 | 17.2274 | 16.8579 | 16.3 | 15.6147 | 15.4579 | 15.3042 | 15.1526 | 14.9968 | 14.3579 | 13.7905 | 13.2305 | 17.5684 | 17.4695 | 17.1021 | 16.4916 | 15.7947 | 15.6358 | 15.48 | 15.3274 | 15.1695 | 14.5189 | 13.9432 | 13.3811
|  | ST NICHOLAS | HE |  |  |  |  | 18.3853 | 18.3221 | 18.2547 | 18.1821 | 18.08 | 17.9558 | 17.8326 | 17.7116 | 17.5968 | 16.9632 | 16.3253 | 15.7326 | 17.6326 | 17.5737 | 17.5116 | 17.3905 | 17.2358 | 17.1095 | 16.9811 | 16.8579 | 16.7389 | 16.0337 | 15.3158 | 14.6442 | 17.5684 | 17.4695 | 17.1021 | 16.4916 | 15.7947 | 15.6358 | 15.48 | 15.3274 | 15.1695 | 14.5189 | 13.9432 | 13.3811
|  | ST NICHOLAS | CF |  |  |  |  | 18.4116 | 18.3726 | 18.3295 | 18.2853 | 18.2389 | 18.1916 | 18.1463 | 18.1 | 18.0558 | 17.6884 | 17.3484 | 16.9505 | 17.6568 | 17.6189 | 17.5789 | 17.5368 | 17.4926 | 17.4505 | 17.4063 | 17.3337 | 17.2495 | 16.8358 | 16.4926 | 16.0116 | 17.6821 | 17.6453 | 17.6095 | 17.5716 | 17.5326 | 17.4916 | 17.4516 | 17.4095 | 17.3663 | 17.1684 | 16.6842 | 16.1937
| ARDMORE / HARRIS GRID | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | 0 | 0.99158 | 0.96842 | 0.94211 | 0.91474 | 0.85263 | 0.79053 | 0.72316 | 0.65579 | 0.58737 | 0.053684 | -0.58 | -1.0442 | 1.0011 | 0.97158 | 0.94316 | 0.91579 | 0.86 | 0.80526 | 0.75158 | 0.69053 | 0.62842 | 0.12211 | -0.49368 | -0.98526 | 0.96526 | 0.93684 | 0.90947 | 0.88316 | 0.81789 | 0.75263 | 0.67895 | 0.60842 | 0.53789 | -0.031579 | -0.71579 | -1.24
|  | STOCKINISH | EE |  |  |  |  | 1.0042 | 0.98421 | 0.96316 | 0.94211 | 0.87579 | 0.8 | 0.72316 | 0.65579 | 0.58737 | 0.053684 | -0.58 | -1.0442 | 1.0158 | 0.99474 | 0.97053 | 0.94632 | 0.88947 | 0.82526 | 0.75789 | 0.69895 | 0.63789 | 0.13053 | -0.48316 | -0.98526 | 0.98211 | 0.95789 | 0.93368 | 0.90947 | 0.84 | 0.76 | 0.67895 | 0.60842 | 0.53789 | -0.031579 | -0.71579 | -1.24
|  | STOCKINISH | HT |  |  |  |  | 0.99158 | 0.96842 | 0.94211 | 0.91474 | 0.85263 | 0.79053 | 0.72947 | 0.66 | 0.58947 | 0.088421 | -0.48211 | -0.86947 | 1.0011 | 0.97158 | 0.94316 | 0.91579 | 0.86 | 0.80526 | 0.75158 | 0.69053 | 0.62842 | 0.12211 | -0.49368 | -0.92526 | 0.96526 | 0.93684 | 0.90947 | 0.88316 | 0.81789 | 0.75263 | 0.68842 | 0.61579 | 0.54421 | -0.006316 | -0.65158 | -1.0947
|  | STOCKINISH | HE |  |  |  |  | 1.0232 | 1.0116 | 0.99789 | 0.98632 | 0.92526 | 0.87263 | 0.80632 | 0.73895 | 0.64316 | 0.24421 | -0.23474 | -0.75053 | 1.0274 | 1.0189 | 1.0084 | 0.99895 | 0.94842 | 0.90211 | 0.83789 | 0.77474 | 0.68211 | 0.29474 | -0.18947 | -0.71263 | 0.96526 | 0.93684 | 0.90947 | 0.88316 | 0.81789 | 0.75263 | 0.68842 | 0.61579 | 0.54421 | -0.006316 | -0.65158 | -1.0947
|  | STOCKINISH | CF |  |  |  |  | 1.0337 | 1.0263 | 1.02 | 1.0116 | 0.98737 | 0.96526 | 0.94316 | 0.91474 | 0.86842 | 0.66 | 0.35895 | 0.034737 | 1.0347 | 1.0305 | 1.0253 | 1.02 | 1.0042 | 0.98842 | 0.96632 | 0.93263 | 0.88316 | 0.67474 | 0.36526 | 0.016842 | 1.0189 | 1.0105 | 1.0021 | 0.99263 | 0.96421 | 0.93895 | 0.91368 | 0.87895 | 0.83053 | 0.60316 | 0.26737 | -0.1
| PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | 0 | 0.32237 | 0.31711 | 0.31395 | 0.30974 | 0.295 | 0.21605 | 0.13711 | 0.11395 | 0.090789 | -0.040789 | -0.285 | -0.50711 | 0.31816 | 0.31289 | 0.30974 | 0.30658 | 0.29289 | 0.20553 | 0.11816 | 0.098158 | 0.077105 | -0.032368 | -0.32395 | -0.53658 | 0.32026 | 0.31395 | 0.31079 | 0.30763 | 0.29184 | 0.20132 | 0.11079 | 0.086579 | 0.061316 | -0.072368 | -0.36184 | -0.59763
|  | STONEFIELD | EE |  |  |  |  | 0.32342 | 0.32026 | 0.31605 | 0.31395 | 0.29605 | 0.27395 | 0.21184 | 0.14763 | 0.092895 | -0.040789 | -0.285 | -0.50711 | 0.32026 | 0.31711 | 0.31289 | 0.30974 | 0.295 | 0.27816 | 0.21289 | 0.14447 | 0.087632 | -0.032368 | -0.28079 | -0.52605 | 0.32132 | 0.31816 | 0.31395 | 0.31184 | 0.29184 | 0.27079 | 0.20132 | 0.12868 | 0.067632 | -0.072368 | -0.3429 | -0.59763
|  | STONEFIELD | HT |  |  |  |  | 0.32237 | 0.31711 | 0.31395 | 0.30974 | 0.295 | 0.21605 | 0.13711 | 0.11395 | 0.090789 | -0.018684 | -0.285 | -0.47237 | 0.31816 | 0.31289 | 0.30974 | 0.30658 | 0.29289 | 0.20553 | 0.11816 | 0.098158 | 0.077105 | -0.027105 | -0.32395 | -0.53658 | 0.32026 | 0.31395 | 0.31079 | 0.30763 | 0.29184 | 0.20132 | 0.11079 | 0.086579 | 0.061316 | -0.055526 | -0.36184 | -0.57868
|  | STONEFIELD | HE |  |  |  |  | 0.32342 | 0.32342 | 0.32342 | 0.32237 | 0.29605 | 0.27289 | 0.23289 | 0.17184 | 0.11921 | 0.018158 | -0.1871 | -0.41868 | 0.32026 | 0.32026 | 0.32026 | 0.31816 | 0.29605 | 0.27289 | 0.23184 | 0.16658 | 0.11079 | 0.018158 | -0.19763 | -0.44079 | 0.32026 | 0.31395 | 0.31079 | 0.30763 | 0.29184 | 0.20132 | 0.11079 | 0.086579 | 0.061316 | -0.055526 | -0.36184 | -0.57868
|  | STONEFIELD | CF |  |  |  |  | 0.32553 | 0.32447 | 0.32342 | 0.32237 | 0.31605 | 0.31079 | 0.29289 | 0.27711 | 0.25711 | 0.16974 | 0.037105 | -0.11868 | 0.32237 | 0.32132 | 0.32026 | 0.31921 | 0.31395 | 0.30974 | 0.29184 | 0.275 | 0.25184 | 0.16237 | 0.01921 | -0.15237 | 0.32342 | 0.32237 | 0.32132 | 0.32026 | 0.315 | 0.30974 | 0.28974 | 0.27184 | 0.24868 | 0.15184 | 0.0013158 | -0.17763
| FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | YES | 0.2 | 17.8042 | 17.5695 | 17.1863 | 16.6389 | 15.8947 | 14.6105 | 13.3695 | 12.2947 | 11.3137 | 4.8653 | -5.1926 | -12.8811 | 17.1168 | 16.4042 | 15.8074 | 15.2116 | 14.4874 | 13.5211 | 12.4558 | 11.5316 | 10.7253 | 4.0863 | -6.1853 | -13.8326 | 17.16 | 16.4716 | 15.8916 | 15.3 | 14.5179 | 13.1589 | 11.8526 | 10.72 | 9.6926 | 2.6884 | -8.2663 | -16.8832
|  | STONEHAVEN | EE |  |  |  |  | 17.9295 | 17.7189 | 17.5 | 17.0211 | 15.8947 | 14.6105 | 13.3695 | 12.2947 | 11.3137 | 4.8653 | -5.1926 | -12.8811 | 17.4063 | 16.7716 | 16.2347 | 15.6442 | 14.6474 | 13.5211 | 12.4558 | 11.5316 | 10.7253 | 4.4589 | -5.4263 | -13.8326 | 17.4432 | 16.8179 | 16.2895 | 15.7095 | 14.5179 | 13.1589 | 11.8526 | 10.72 | 9.6926 | 2.6884 | -8.2663 | -16.8832
|  | STONEHAVEN | HT |  |  |  |  | 17.8042 | 17.5695 | 17.1863 | 16.6389 | 15.9779 | 15.14 | 14.1832 | 13.1137 | 12.1453 | 5.1484 | -4.2305 | -10.6063 | 17.1168 | 16.4042 | 15.8074 | 15.2116 | 14.4874 | 13.7189 | 12.8737 | 11.9484 | 11.1442 | 4.0863 | -6.1853 | -13.3726 | 17.16 | 16.4716 | 15.8916 | 15.3 | 14.5779 | 13.6937 | 12.6874 | 11.5674 | 10.5589 | 2.9558 | -7.6305 | -14.9895
|  | STONEHAVEN | HE |  |  |  |  | 18.0853 | 17.9642 | 17.8316 | 17.6916 | 16.5189 | 15.5358 | 14.62 | 13.8168 | 12.8632 | 5.0411 | -2.7632 | -11.22 | 17.7558 | 17.2968 | 16.9274 | 16.5211 | 15.2926 | 14.4232 | 13.6316 | 12.9716 | 12.1316 | 4.7526 | -3.2684 | -11.9484 | 17.16 | 16.4716 | 15.8916 | 15.3 | 14.5779 | 13.6937 | 12.6874 | 11.5674 | 10.5589 | 2.9558 | -7.6305 | -14.9895
|  | STONEHAVEN | CF |  |  |  |  | 18.1832 | 18.1137 | 18.04 | 17.9674 | 17.6263 | 17.3116 | 17 | 16.7232 | 16.3842 | 7.5632 | 2.6453 | -2.7389 | 18.0168 | 17.7821 | 17.5916 | 17.3905 | 16.9358 | 16.5621 | 16.2042 | 15.8968 | 15.2747 | 7.5842 | 2.4747 | -3.3674 | 17.9211 | 17.7537 | 17.6105 | 17.4189 | 16.8926 | 16.4526 | 16.0305 | 15.6653 | 15.0316 | 5.6558 | 0.17684 | -5.8737
| STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 6773 4109 | YES | YES | 0 | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6874 | 3.6853 | 3.6832 | 3.68 | 3.6779 | 3.6579 | 3.6337 | 3.6168 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3832 | 3.3811 | 3.38 | 3.3779 | 3.3737 | 3.3579 | 3.3379 | 3.32 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5674 | 3.5663 | 3.5632 | 3.5611 | 3.5579 | 3.5347 | 3.5095 | 3.4916
|  | STONEYHILL | EE |  |  |  |  | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6874 | 3.6853 | 3.6832 | 3.6811 | 3.6789 | 3.6579 | 3.6337 | 3.6168 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3832 | 3.3821 | 3.3811 | 3.3789 | 3.3758 | 3.3579 | 3.3379 | 3.32 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5674 | 3.5663 | 3.5632 | 3.5611 | 3.5579 | 3.5347 | 3.5095 | 3.4916
|  | STONEYHILL | HT |  |  |  |  | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6874 | 3.6863 | 3.6842 | 3.6821 | 3.6789 | 3.6611 | 3.64 | 3.6253 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3842 | 3.3832 | 3.3811 | 3.3789 | 3.3758 | 3.3589 | 3.3379 | 3.3232 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5684 | 3.5674 | 3.5642 | 3.5611 | 3.5579 | 3.5379 | 3.5147 | 3.4989
|  | STONEYHILL | HE |  |  |  |  | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6874 | 3.6863 | 3.6832 | 3.68 | 3.6779 | 3.6632 | 3.6453 | 3.6263 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3832 | 3.3811 | 3.38 | 3.3779 | 3.3737 | 3.3611 | 3.3453 | 3.3284 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5684 | 3.5674 | 3.5642 | 3.5611 | 3.5579 | 3.5379 | 3.5147 | 3.4989
|  | STONEYHILL | CF |  |  |  |  | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6884 | 3.6874 | 3.6874 | 3.6874 | 3.6842 | 3.6768 | 3.6663 | 3.6537 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3842 | 3.3842 | 3.3832 | 3.3811 | 3.38 | 3.3726 | 3.3621 | 3.3505 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5695 | 3.5684 | 3.5674 | 3.5653 | 3.5642 | 3.5558 | 3.5442 | 3.5295
| PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | NO | 0 | 24.3032 | 23.6347 | 22.8926 | 22.2032 | 21.3789 | 20.2737 | 19.1326 | 18.3842 | 17.4895 | 15.5242 | 13.0642 | 11.6158 | 23.1505 | 22.3579 | 21.4768 | 20.6611 | 19.6979 | 18.3958 | 17.0495 | 16.1832 | 15.1368 | 12.3979 | 9.4968 | 7.8453 | 23.9221 | 23.1842 | 22.3632 | 21.6021 | 20.6684 | 19.36 | 18.0095 | 17.1326 | 16.08 | 14.3863 | 11.7463 | 10.7358
|  | STONEYWOOD T1&T2 | EE |  |  |  |  | 24.3884 | 23.7474 | 23.0242 | 22.3579 | 21.5505 | 20.7389 | 19.7695 | 19.3147 | 18.9011 | 16.4337 | 13.9568 | 12.6221 | 23.2442 | 22.4811 | 21.6232 | 20.8316 | 19.8916 | 18.9495 | 17.8168 | 17.3021 | 16.8368 | 14.4168 | 11.6095 | 10.0589 | 24.0126 | 23.3032 | 22.5032 | 21.7653 | 20.8579 | 19.9053 | 18.7611 | 18.2368 | 17.7611 | 15.4463 | 12.5832 | 11.0105
|  | STONEYWOOD T1&T2 | HT |  |  |  |  | 24.3032 | 23.6347 | 22.8926 | 22.2032 | 21.3789 | 20.2737 | 19.1326 | 18.3842 | 17.4895 | 15.5263 | 13.2874 | 12.4189 | 23.1505 | 22.3579 | 21.4768 | 20.6611 | 19.6979 | 18.3958 | 17.0495 | 16.1832 | 15.1368 | 13.3105 | 10.6968 | 9.6958 | 23.9221 | 23.1842 | 22.3632 | 21.6021 | 20.6684 | 19.36 | 18.0095 | 17.1326 | 16.08 | 14.3863 | 11.7463 | 10.7358
|  | STONEYWOOD T1&T2 | HE |  |  |  |  | 24.5011 | 23.8947 | 23.2126 | 22.5779 | 21.7968 | 21.0305 | 20.0179 | 19.4737 | 18.9547 | 15.5242 | 13.0642 | 11.6158 | 23.3695 | 22.6453 | 21.8295 | 21.0747 | 20.1642 | 19.2663 | 18.0716 | 17.4421 | 16.8421 | 12.3979 | 9.4968 | 7.8453 | 23.9221 | 23.1842 | 22.3632 | 21.6021 | 20.6684 | 19.36 | 18.0095 | 17.1326 | 16.08 | 14.3863 | 11.7463 | 10.7358
|  | STONEYWOOD T1&T2 | CF |  |  |  |  | 24.8295 | 24.5358 | 24.2263 | 23.9495 | 23.6242 | 23.2716 | 22.8895 | 22.7168 | 22.5726 | 21.2337 | 19.4347 | 18.0653 | 23.7589 | 23.4095 | 23.0411 | 22.7126 | 22.3337 | 21.92 | 21.4705 | 21.2747 | 21.1116 | 19.5516 | 17.4389 | 15.8242 | 24.1916 | 24.1653 | 23.8263 | 23.5211 | 23.1632 | 22.7726 | 22.3516 | 22.1632 | 22.0063 | 20.4958 | 18.3632 | 16.7347
| DYCE | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | NO | YES | 0 | 23.0684 | 23.0442 | 23.0211 | 22.9968 | 22.9695 | 22.9432 | 22.9189 | 22.8926 | 22.8705 | 22.7842 | 22.72 | 22.6695 | 22.8895 | 22.8716 | 22.8537 | 22.8347 | 22.8137 | 22.7937 | 22.7684 | 22.7358 | 22.7063 | 22.5842 | 22.4863 | 22.4021 | 23.6242 | 23.6063 | 23.5884 | 23.5695 | 23.5474 | 23.5263 | 23.5021 | 23.4695 | 23.4389 | 23.3158 | 23.2158 | 23.1326
|  | STONEYWOOD T3 | EE |  |  |  |  | 23.0832 | 23.0632 | 23.0442 | 23.0221 | 23.0011 | 22.9789 | 22.9568 | 22.9368 | 22.92 | 22.8368 | 22.7789 | 22.74 | 22.8989 | 22.8842 | 22.8695 | 22.8526 | 22.8358 | 22.8189 | 22.8021 | 22.7863 | 22.7737 | 22.6705 | 22.5884 | 22.5253 | 23.6337 | 23.6189 | 23.6042 | 23.5863 | 23.5695 | 23.5516 | 23.5337 | 23.5168 | 23.5021 | 23.4 | 23.3158 | 23.2526
|  | STONEYWOOD T3 | HT |  |  |  |  | 23.0684 | 23.0442 | 23.0211 | 22.9968 | 22.9695 | 22.9432 | 22.9189 | 22.8926 | 22.8705 | 22.7842 | 22.72 | 22.6695 | 22.8895 | 22.8716 | 22.8537 | 22.8347 | 22.8137 | 22.7937 | 22.7684 | 22.7358 | 22.7063 | 22.5842 | 22.4863 | 22.4021 | 23.6242 | 23.6063 | 23.5884 | 23.5695 | 23.5474 | 23.5263 | 23.5021 | 23.4695 | 23.4389 | 23.3158 | 23.2158 | 23.1326
|  | STONEYWOOD T3 | HE |  |  |  |  | 23.1042 | 23.0916 | 23.0779 | 23.0642 | 23.0474 | 23.0316 | 23.0158 | 23.0011 | 22.9884 | 22.9379 | 22.9063 | 22.8821 | 22.9137 | 22.9032 | 22.8926 | 22.8811 | 22.8674 | 22.8547 | 22.8421 | 22.8305 | 22.8211 | 22.7832 | 22.7642 | 22.74 | 23.6242 | 23.6063 | 23.5884 | 23.5695 | 23.5474 | 23.5263 | 23.5021 | 23.4695 | 23.4389 | 23.3158 | 23.2158 | 23.1326
|  | STONEYWOOD T3 | CF |  |  |  |  | 23.1168 | 23.1095 | 23.1021 | 23.0937 | 23.0853 | 23.0768 | 23.0684 | 23.06 | 23.0526 | 23.0137 | 22.9895 | 22.9726 | 22.9232 | 22.9179 | 22.9126 | 22.9063 | 22.9 | 22.8937 | 22.8874 | 22.8811 | 22.8758 | 22.8474 | 22.8326 | 22.8242 | 23.6579 | 23.6526 | 23.6474 | 23.6411 | 23.6337 | 23.6284 | 23.6211 | 23.6137 | 23.6084 | 23.5779 | 23.5611 | 23.5516
| CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 0 | 0.96526 | 0.93158 | 0.9 | 0.86421 | 0.79895 | 0.73368 | 0.69158 | 0.64421 | 0.57579 | 0.39895 | 0.25158 | 0.16211 | 0.92105 | 0.88526 | 0.84947 | 0.81263 | 0.74316 | 0.68105 | 0.63789 | 0.58316 | 0.51053 | 0.38526 | 0.26842 | 0.18947 | 0.92 | 0.88211 | 0.84737 | 0.80737 | 0.73684 | 0.66316 | 0.61789 | 0.56526 | 0.49053 | 0.30105 | 0.14526 | 0.047368
|  | STRACHUR | EE |  |  |  |  | 0.97684 | 0.94632 | 0.91474 | 0.88211 | 0.81684 | 0.73368 | 0.69158 | 0.65158 | 0.60947 | 0.39895 | 0.25158 | 0.16211 | 0.93579 | 0.90526 | 0.87474 | 0.84105 | 0.77684 | 0.69158 | 0.65474 | 0.61789 | 0.58105 | 0.38842 | 0.26842 | 0.18947 | 0.93158 | 0.89789 | 0.86421 | 0.82842 | 0.75579 | 0.66316 | 0.61789 | 0.57368 | 0.52947 | 0.30105 | 0.14526 | 0.047368
|  | STRACHUR | HT |  |  |  |  | 0.96526 | 0.93158 | 0.9 | 0.86421 | 0.79895 | 0.74 | 0.69895 | 0.64421 | 0.57579 | 0.44211 | 0.33895 | 0.26421 | 0.92105 | 0.88526 | 0.84947 | 0.81263 | 0.74316 | 0.68105 | 0.63789 | 0.58316 | 0.51053 | 0.38526 | 0.28737 | 0.21474 | 0.92 | 0.88211 | 0.84737 | 0.80737 | 0.73684 | 0.67158 | 0.62526 | 0.56526 | 0.49053 | 0.34737 | 0.23474 | 0.15368
|  | STRACHUR | HE |  |  |  |  | 1.0042 | 0.98737 | 0.96947 | 0.94526 | 0.87789 | 0.80842 | 0.77789 | 0.74632 | 0.71263 | 0.60211 | 0.52526 | 0.44842 | 0.96421 | 0.94526 | 0.92632 | 0.90105 | 0.83053 | 0.75263 | 0.72526 | 0.69368 | 0.66211 | 0.56316 | 0.5 | 0.43684 | 0.92 | 0.88211 | 0.84737 | 0.80737 | 0.73684 | 0.67158 | 0.62526 | 0.56526 | 0.49053 | 0.34737 | 0.23474 | 0.15368
|  | STRACHUR | CF |  |  |  |  | 1.0168 | 1.0095 | 1.0021 | 0.99474 | 0.97895 | 0.96105 | 0.94526 | 0.93158 | 0.91684 | 0.80421 | 0.75474 | 0.71789 | 0.97895 | 0.96947 | 0.96211 | 0.95368 | 0.93684 | 0.91895 | 0.90211 | 0.88842 | 0.87368 | 0.75053 | 0.70632 | 0.67368 | 0.97684 | 0.96947 | 0.96 | 0.95263 | 0.93474 | 0.91368 | 0.89789 | 0.88316 | 0.86632 | 0.74 | 0.68947 | 0.65053
| TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | YES | 0 | 1.0305 | 1.0032 | 0.97684 | 0.94316 | 0.86737 | 0.79158 | 0.71474 | 0.63053 | 0.54421 | -0.04 | -0.74421 | -1.2653 | 0.99368 | 0.96421 | 0.93474 | 0.89789 | 0.83053 | 0.76316 | 0.69474 | 0.62 | 0.54526 | -0.003158 | -0.70737 | -1.2684 | 0.97368 | 0.94316 | 0.91368 | 0.87684 | 0.79684 | 0.71895 | 0.63895 | 0.55158 | 0.46421 | -0.15895 | -0.94105 | -1.5368
|  | STRATHDON | EE |  |  |  |  | 1.0474 | 1.0232 | 1.0011 | 0.97895 | 0.89789 | 0.80737 | 0.71579 | 0.63263 | 0.54842 | -0.04 | -0.74421 | -1.2653 | 1.0116 | 0.98737 | 0.96421 | 0.94 | 0.87368 | 0.79789 | 0.71789 | 0.64632 | 0.57263 | 0.011579 | -0.69158 | -1.2684 | 0.99158 | 0.96632 | 0.94211 | 0.91789 | 0.83579 | 0.74316 | 0.64842 | 0.56421 | 0.47789 | -0.15895 | -0.94105 | -1.5368
|  | STRATHDON | HT |  |  |  |  | 1.0305 | 1.0032 | 0.97684 | 0.94316 | 0.86737 | 0.79158 | 0.71474 | 0.63053 | 0.54421 | 0.014737 | -0.62211 | -1.0642 | 0.99368 | 0.96421 | 0.93474 | 0.89789 | 0.83053 | 0.76316 | 0.69474 | 0.62 | 0.54526 | -0.003158 | -0.70737 | -1.2 | 0.97368 | 0.94316 | 0.91368 | 0.87684 | 0.79684 | 0.71895 | 0.63895 | 0.55158 | 0.46421 | -0.13158 | -0.85789 | -1.3642
|  | STRATHDON | HE |  |  |  |  | 1.0684 | 1.0558 | 1.0432 | 1.0295 | 0.95684 | 0.88737 | 0.80632 | 0.73053 | 0.62421 | 0.17579 | -0.35368 | -0.9421 | 1.0368 | 1.0221 | 1.0095 | 0.99579 | 0.93789 | 0.87895 | 0.80421 | 0.73474 | 0.63053 | 0.18842 | -0.36842 | -0.97053 | 0.97368 | 0.94316 | 0.91368 | 0.87684 | 0.79684 | 0.71895 | 0.63895 | 0.55158 | 0.46421 | -0.13158 | -0.85789 | -1.3642
|  | STRATHDON | CF |  |  |  |  | 1.08 | 1.0726 | 1.0663 | 1.0579 | 1.0274 | 1.0011 | 0.97579 | 0.93053 | 0.88105 | 0.65053 | 0.31579 | -0.048421 | 1.0505 | 1.0411 | 1.0337 | 1.0253 | 1.0011 | 0.98 | 0.95789 | 0.91053 | 0.85579 | 0.61684 | 0.26211 | -0.14 | 1.0295 | 1.0211 | 1.0126 | 1.0042 | 0.97368 | 0.94737 | 0.92105 | 0.86947 | 0.81158 | 0.55368 | 0.17158 | -0.24632
| STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | YES | 0.65 | 5.6868 | 5.4595 | 4.4658 | 4.1921 | 4.01 | 3.1889 | 2.3374 | 1.6037 | 0.85526 | -7.8016 | -15.43 | -20.7205 | 6.2532 | 6.0995 | 5.5932 | 5.3268 | 5.0942 | 4.4311 | 3.7521 | 3.1668 | 2.57 | -4.8984 | -12.1637 | -17.8816 | 6.5711 | 6.2889 | 5.2163 | 4.8521 | 4.6174 | 3.7858 | 2.9321 | 2.1995 | 1.4489 | -7.4342 | -15.6816 | -21.7321
|  | STRICHEN | EE |  |  |  |  | 5.7384 | 5.5111 | 4.4658 | 4.1921 | 4.01 | 3.1889 | 2.3374 | 1.6037 | 0.85526 | -7.8016 | -15.43 | -20.7205 | 6.2984 | 6.1489 | 5.5932 | 5.3268 | 5.0942 | 4.4311 | 3.7521 | 3.1668 | 2.57 | -4.8984 | -12.1637 | -17.8816 | 6.63 | 6.3489 | 5.2163 | 4.8521 | 4.6174 | 3.7858 | 2.9321 | 2.1995 | 1.4489 | -7.4342 | -15.6816 | -21.7321
|  | STRICHEN | HT |  |  |  |  | 5.6868 | 5.4595 | 5.1889 | 4.87 | 4.1553 | 3.5732 | 2.9742 | 2.2605 | 1.5511 | -7.0542 | -13.5205 | -17.8142 | 6.2532 | 6.0995 | 5.9184 | 5.7079 | 5.1721 | 4.6921 | 4.2068 | 3.6332 | 3.0721 | -4.71 | -11.6247 | -16.3679 | 6.5711 | 6.2889 | 5.9437 | 5.5332 | 4.7532 | 4.1605 | 3.5605 | 2.8447 | 2.1437 | -6.9184 | -14.2342 | -19.1584
|  | STRICHEN | HE |  |  |  |  | 5.7932 | 5.6395 | 5.43 | 5.1668 | 4.4353 | 3.8226 | 3.2111 | 2.6068 | 1.9974 | -7.1795 | -12.8784 | -19.0805 | 6.35 | 6.2458 | 6.1079 | 5.9384 | 5.5542 | 5.0521 | 4.5532 | 4.0584 | 3.5647 | -4.3753 | -10.0437 | -16.251 | 6.5711 | 6.2889 | 5.9437 | 5.5332 | 4.7532 | 4.1605 | 3.5605 | 2.8447 | 2.1437 | -6.9184 | -14.2342 | -19.1584
|  | STRICHEN | CF |  |  |  |  | 5.89 | 5.8342 | 5.7658 | 5.6858 | 5.3784 | 5.0995 | 4.8205 | 4.5774 | 4.3879 | 0.72895 | -2.8668 | -6.6995 | 6.4195 | 6.3795 | 6.3332 | 6.2805 | 6.1163 | 5.9658 | 5.8163 | 5.6837 | 5.5774 | 2.3121 | -1.29 | -5.3268 | 6.8121 | 6.7416 | 6.6574 | 6.5553 | 6.2279 | 5.9279 | 5.63 | 5.3668 | 5.1595 | 1.2268 | -2.7289 | -7.0384
| THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | YES | 0 | 9.0621 | 8.9653 | 8.8674 | 8.7137 | 8.4232 | 8.2295 | 8.0632 | 7.9126 | 7.7126 | 7.0926 | 6.5411 | 4.9768 | 8.0474 | 7.8295 | 7.5884 | 7.2674 | 6.9358 | 6.7242 | 6.5442 | 6.3821 | 6.1611 | 5.4747 | 4.8589 | 3.4905 | 8.1042 | 7.9042 | 7.6842 | 7.3947 | 7.0947 | 6.8989 | 6.7295 | 6.5779 | 6.3747 | 5.7421 | 5.1263 | 3.5063
|  | STROMNESS | EE |  |  |  |  | 9.1137 | 9.0347 | 8.9516 | 8.8653 | 8.6747 | 8.5021 | 8.3579 | 8.2295 | 8.1484 | 7.5411 | 7.1211 | 5.6863 | 8.1695 | 7.9905 | 7.7895 | 7.5074 | 7.2147 | 7.0242 | 6.8663 | 6.7284 | 6.6442 | 5.9716 | 5.4968 | 4.2811 | 8.2168 | 8.0526 | 7.8674 | 7.6137 | 7.3505 | 7.1758 | 7.0295 | 6.8989 | 6.8179 | 6.2 | 5.7632 | 4.2968
|  | STROMNESS | HT |  |  |  |  | 9.0621 | 8.9653 | 8.8674 | 8.7137 | 8.4232 | 8.2295 | 8.0632 | 7.9126 | 7.7126 | 7.0926 | 6.5411 | 4.9768 | 8.0474 | 7.8295 | 7.5884 | 7.2674 | 6.9358 | 6.7242 | 6.5442 | 6.3821 | 6.1611 | 5.4747 | 4.8589 | 3.4905 | 8.1042 | 7.9042 | 7.6842 | 7.3947 | 7.0947 | 6.8989 | 6.7295 | 6.5779 | 6.3747 | 5.7421 | 5.1263 | 3.5063
|  | STROMNESS | HE |  |  |  |  | 9.1937 | 9.1379 | 9.0789 | 9.0147 | 8.9389 | 8.8053 | 8.6947 | 8.6305 | 8.5726 | 8.2758 | 8.0253 | 7.2832 | 8.3611 | 8.2189 | 8.0042 | 7.7611 | 7.5053 | 7.3516 | 7.2295 | 7.1642 | 7.1042 | 6.7811 | 6.4979 | 5.8579 | 8.1042 | 7.9042 | 7.6842 | 7.3947 | 7.0947 | 6.8989 | 6.7295 | 6.5779 | 6.3747 | 5.7421 | 5.1263 | 3.5063
|  | STROMNESS | CF |  |  |  |  | 9.2442 | 9.2147 | 9.1842 | 9.1526 | 9.1211 | 9.0895 | 9.0568 | 9.0253 | 8.9926 | 8.8484 | 8.6716 | 8.5116 | 8.4621 | 8.3968 | 8.3274 | 8.2547 | 8.1916 | 8.1211 | 8.0537 | 7.9842 | 7.9021 | 7.4158 | 7.2095 | 7.0221 | 8.4011 | 8.3695 | 8.3368 | 8.2958 | 8.2368 | 8.1716 | 8.1095 | 8.0453 | 7.9705 | 7.5347 | 7.3474 | 7.1832
| THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | YES | 0 | 1.0789 | 1.06 | 1.04 | 1.0221 | 0.86105 | 0.66316 | 0.46421 | 0.28316 | 0.010526 | -1.6137 | -3.4842 | -4.8547 | 0.96211 | 0.94421 | 0.92526 | 0.90842 | 0.78 | 0.60316 | 0.42211 | 0.25158 | -0.011579 | -1.4968 | -3.3095 | -4.7947 | 0.96842 | 0.94842 | 0.92842 | 0.90842 | 0.74842 | 0.54947 | 0.34947 | 0.17789 | -0.070526 | -1.8811 | -3.9137 | -5.4705
|  | STRONSAY | EE |  |  |  |  | 1.0863 | 1.0653 | 1.0432 | 1.0221 | 0.86105 | 0.66316 | 0.46421 | 0.29368 | 0.069474 | -1.6137 | -3.4842 | -4.8547 | 0.97053 | 0.95053 | 0.93053 | 0.91158 | 0.78 | 0.61895 | 0.45895 | 0.31895 | 0.12105 | -1.4968 | -3.3095 | -4.7947 | 0.97579 | 0.95474 | 0.93263 | 0.91053 | 0.74842 | 0.54947 | 0.34947 | 0.17789 | -0.053684 | -1.8811 | -3.9137 | -5.4705
|  | STRONSAY | HT |  |  |  |  | 1.0789 | 1.06 | 1.04 | 1.0221 | 0.88842 | 0.75474 | 0.60842 | 0.40632 | 0.086316 | -1.4042 | -3.0632 | -4.1779 | 0.96211 | 0.94421 | 0.92526 | 0.90842 | 0.79684 | 0.68737 | 0.56526 | 0.38737 | 0.071579 | -1.4316 | -3.2211 | -4.4716 | 0.96842 | 0.94842 | 0.92842 | 0.90842 | 0.77368 | 0.63895 | 0.49158 | 0.28211 | -0.070526 | -1.7137 | -3.5989 | -4.8832
|  | STRONSAY | HE |  |  |  |  | 1.0979 | 1.0895 | 1.0811 | 1.0716 | 0.86737 | 0.67263 | 0.47368 | 0.28316 | 0.010526 | -1.1547 | -2.5842 | -4.1442 | 0.98316 | 0.97474 | 0.96632 | 0.95579 | 0.78 | 0.60316 | 0.42211 | 0.25158 | -0.011579 | -1.1263 | -2.5705 | -4.1474 | 0.96842 | 0.94842 | 0.92842 | 0.90842 | 0.77368 | 0.63895 | 0.49158 | 0.28211 | -0.070526 | -1.7137 | -3.5989 | -4.8832
|  | STRONSAY | CF |  |  |  |  | 1.1042 | 1.0979 | 1.0937 | 1.0874 | 1.0221 | 0.96526 | 0.85368 | 0.73895 | 0.61053 | 0.017895 | -0.88105 | -1.8632 | 0.98842 | 0.98421 | 0.97789 | 0.97263 | 0.91895 | 0.87158 | 0.76316 | 0.64842 | 0.51053 | -0.083158 | -0.99579 | -2.0442 | 0.99158 | 0.98526 | 0.98 | 0.97579 | 0.90947 | 0.85158 | 0.73368 | 0.60632 | 0.46105 | -0.18947 | -1.1853 | -2.2947
| FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | NO | 0 | 1.1021 | 1.0895 | 1.0768 | 1.0653 | 1.0442 | 1.0232 | 1.0042 | 0.98632 | 0.96737 | 0.89368 | 0.83789 | 0.79053 | 0.98842 | 0.96737 | 0.94526 | 0.92526 | 0.90316 | 0.88211 | 0.86211 | 0.84316 | 0.82421 | 0.74842 | 0.69053 | 0.64211 | 1.0368 | 1.0179 | 0.99684 | 0.97789 | 0.95684 | 0.93474 | 0.91368 | 0.89474 | 0.87579 | 0.79579 | 0.73579 | 0.68526
|  | STRONTIAN | EE |  |  |  |  | 1.1095 | 1.0989 | 1.0874 | 1.0758 | 1.0642 | 1.0526 | 1.0379 | 1.0221 | 1.0084 | 0.94526 | 0.9 | 0.86211 | 1.0042 | 0.98737 | 0.96947 | 0.95053 | 0.93368 | 0.91684 | 0.90105 | 0.88632 | 0.87263 | 0.81053 | 0.76526 | 0.72947 | 1.0442 | 1.0337 | 1.0158 | 0.99789 | 0.98211 | 0.96421 | 0.94947 | 0.93368 | 0.91895 | 0.85053 | 0.80211 | 0.76
|  | STRONTIAN | HT |  |  |  |  | 1.1021 | 1.0895 | 1.0768 | 1.0653 | 1.0442 | 1.0232 | 1.0042 | 0.98632 | 0.96737 | 0.89368 | 0.83789 | 0.79053 | 0.98842 | 0.96737 | 0.94526 | 0.92526 | 0.90316 | 0.88211 | 0.86211 | 0.84316 | 0.82421 | 0.74842 | 0.69053 | 0.64211 | 1.0368 | 1.0179 | 0.99684 | 0.97789 | 0.95684 | 0.93474 | 0.91368 | 0.89474 | 0.87579 | 0.79579 | 0.73579 | 0.68526
|  | STRONTIAN | HE |  |  |  |  | 1.12 | 1.1126 | 1.1063 | 1.0989 | 1.0895 | 1.0832 | 1.0758 | 1.0695 | 1.0621 | 1.0411 | 1.0232 | 1.0074 | 1.0253 | 1.0137 | 1.0042 | 0.99263 | 0.98105 | 0.97053 | 0.95895 | 0.95053 | 0.94105 | 0.90632 | 0.88421 | 0.86842 | 1.0368 | 1.0179 | 0.99684 | 0.97789 | 0.95684 | 0.93474 | 0.91368 | 0.89474 | 0.87579 | 0.79579 | 0.73579 | 0.68526
|  | STRONTIAN | CF |  |  |  |  | 1.1263 | 1.1232 | 1.12 | 1.1168 | 1.1126 | 1.1095 | 1.1063 | 1.1021 | 1.0979 | 1.0832 | 1.0758 | 1.0674 | 1.0326 | 1.0295 | 1.0242 | 1.0189 | 1.0116 | 1.0053 | 1 | 0.99263 | 0.98526 | 0.95789 | 0.94 | 0.92632 | 1.0621 | 1.0589 | 1.0547 | 1.0516 | 1.0474 | 1.0442 | 1.0411 | 1.0368 | 1.0337 | 1.0095 | 0.99158 | 0.98
| SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | 0 | 1.4221 | 1.38 | 1.3389 | 1.2989 | 1.2568 | 1.2168 | 1.1779 | 1.1411 | 1.1053 | 0.96526 | 0.85158 | 0.75474 | 1.2789 | 1.2537 | 1.2253 | 1.1895 | 1.1505 | 1.1105 | 1.0695 | 1.0305 | 0.99263 | 0.84211 | 0.71895 | 0.61263 | 1.3242 | 1.3 | 1.2768 | 1.2526 | 1.2242 | 1.1832 | 1.1432 | 1.1042 | 1.0684 | 0.92105 | 0.79684 | 0.68947
|  | SUMBURGH | EE |  |  |  |  | 1.4495 | 1.4158 | 1.3821 | 1.3484 | 1.3158 | 1.2832 | 1.2537 | 1.2242 | 1.1958 | 1.0758 | 0.99158 | 0.92211 | 1.2926 | 1.2716 | 1.2505 | 1.2295 | 1.2021 | 1.1726 | 1.1453 | 1.1189 | 1.0895 | 0.96316 | 0.87053 | 0.79368 | 1.3368 | 1.3168 | 1.2968 | 1.2758 | 1.2547 | 1.2337 | 1.2147 | 1.1916 | 1.1621 | 1.0389 | 0.94947 | 0.87263
|  | SUMBURGH | HT |  |  |  |  | 1.4221 | 1.38 | 1.3389 | 1.2989 | 1.2568 | 1.2168 | 1.1779 | 1.1411 | 1.1053 | 0.96526 | 0.85158 | 0.75474 | 1.2789 | 1.2537 | 1.2253 | 1.1895 | 1.1505 | 1.1105 | 1.0695 | 1.0305 | 0.99263 | 0.84211 | 0.71895 | 0.61263 | 1.3242 | 1.3 | 1.2768 | 1.2526 | 1.2242 | 1.1832 | 1.1432 | 1.1042 | 1.0684 | 0.92105 | 0.79684 | 0.68947
|  | SUMBURGH | HE |  |  |  |  | 1.4884 | 1.4663 | 1.4453 | 1.4221 | 1.3989 | 1.3779 | 1.3568 | 1.3368 | 1.3189 | 1.2505 | 1.2074 | 1.1758 | 1.3126 | 1.2979 | 1.2832 | 1.2684 | 1.2505 | 1.2358 | 1.2211 | 1.2053 | 1.1926 | 1.1389 | 1.1011 | 1.0695 | 1.3242 | 1.3 | 1.2768 | 1.2526 | 1.2242 | 1.1832 | 1.1432 | 1.1042 | 1.0684 | 0.92105 | 0.79684 | 0.68947
|  | SUMBURGH | CF |  |  |  |  | 1.5095 | 1.4968 | 1.4832 | 1.4695 | 1.4568 | 1.4432 | 1.4295 | 1.4168 | 1.4042 | 1.3453 | 1.3063 | 1.2768 | 1.3253 | 1.3179 | 1.3105 | 1.3011 | 1.2937 | 1.2863 | 1.2779 | 1.2695 | 1.2611 | 1.2274 | 1.1958 | 1.1716 | 1.3684 | 1.3611 | 1.3537 | 1.3453 | 1.3379 | 1.3305 | 1.3221 | 1.3147 | 1.3063 | 1.2737 | 1.2568 | 1.2442
| ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | YES | 0.068 | 16.2567 | 16.1631 | 16.0683 | 24.7036 | 24.0004 | 23.1973 | 22.392 | 21.6541 | 20.9941 | 19.7804 | 18.472 | 17.8731 | 14.8394 | 14.7499 | 14.6225 | 22.6362 | 21.6573 | 20.7794 | 19.8983 | 19.1067 | 18.4046 | 17.2583 | 16.2225 | 15.6446 | 15.1144 | 15.0217 | 14.927 | 23.3373 | 22.412 | 21.5141 | 20.6152 | 19.7941 | 19.0636 | 17.7815 | 16.3973 | 15.752
|  | TAIN | EE |  |  |  |  | 16.3062 | 16.2262 | 16.1431 | 24.7867 | 24.5773 | 24.3415 | 23.5867 | 22.7867 | 21.9815 | 19.7804 | 18.472 | 17.8731 | 14.8888 | 14.8152 | 14.7373 | 22.8331 | 22.4867 | 22.2173 | 21.3246 | 20.4604 | 19.5909 | 17.3857 | 16.2225 | 15.6446 | 15.1638 | 15.0849 | 15.0017 | 23.4215 | 23.2036 | 22.892 | 21.9815 | 21.0878 | 20.1888 | 17.7846 | 16.3973 | 15.752
|  | TAIN | HT |  |  |  |  | 16.2567 | 16.1631 | 16.0683 | 24.7036 | 24.0004 | 23.1973 | 22.392 | 21.6541 | 20.9941 | 19.792 | 18.9488 | 18.4004 | 14.8394 | 14.7499 | 14.6225 | 22.6362 | 21.6573 | 20.7794 | 19.8983 | 19.1067 | 18.4046 | 17.2583 | 16.4362 | 15.8709 | 15.1144 | 15.0217 | 14.927 | 23.3373 | 22.412 | 21.5141 | 20.6152 | 19.7941 | 19.0636 | 17.7815 | 16.8762 | 16.2804
|  | TAIN | HE |  |  |  |  | 16.3725 | 16.322 | 16.2673 | 24.9383 | 24.7331 | 24.5573 | 24.2973 | 23.7931 | 23.2941 | 21.3699 | 20.1899 | 19.3173 | 14.9552 | 14.9057 | 14.852 | 23.0741 | 22.8152 | 22.6215 | 22.0836 | 21.5531 | 21.0267 | 19.032 | 17.8783 | 17.0909 | 15.1144 | 15.0217 | 14.927 | 23.3373 | 22.412 | 21.5141 | 20.6152 | 19.7941 | 19.0636 | 17.7815 | 16.8762 | 16.2804
|  | TAIN | CF |  |  |  |  | 16.4167 | 16.3873 | 16.3588 | 25.0583 | 24.9762 | 24.8994 | 24.8236 | 24.7541 | 24.6973 | 23.5373 | 22.7067 | 22.0467 | 14.9994 | 14.9709 | 14.9436 | 23.1941 | 23.1383 | 23.0857 | 23.0341 | 22.7762 | 22.4962 | 21.2162 | 20.3815 | 19.7067 | 15.2744 | 15.2459 | 15.2165 | 23.692 | 23.6109 | 23.5362 | 23.4636 | 23.3952 | 23.2057 | 21.8899 | 20.9783 | 20.2499
| ARDMORE / HARRIS GRID | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | 0 | 1.1442 | 1.1063 | 0.23368 | 0.18842 | 0.025263 | -0.13368 | -0.29368 | -0.43368 | -0.57684 | -1.9084 | -3.4737 | -4.7989 | 1.0379 | 0.97263 | 0.25053 | 0.20105 | 0.058947 | -0.08 | -0.21684 | -0.3421 | -0.46526 | -1.8116 | -3.4126 | -4.8853 | 1.0074 | 0.94316 | 0.031579 | -0.015789 | -0.18105 | -0.34105 | -0.50211 | -0.64526 | -0.78947 | -2.2516 | -4.0021 | -5.5274
|  | TARBERT | EE |  |  |  |  | 1.1621 | 1.1274 | 0.23368 | 0.18842 | 0.025263 | -0.13368 | -0.29368 | -0.43368 | -0.57684 | -1.9084 | -3.4737 | -4.7989 | 1.0789 | 1.0242 | 0.25053 | 0.20105 | 0.058947 | -0.08 | -0.21684 | -0.3421 | -0.46526 | -1.8116 | -3.4126 | -4.8853 | 1.0463 | 0.99158 | 0.031579 | -0.015789 | -0.18105 | -0.34105 | -0.50211 | -0.64526 | -0.78947 | -2.2516 | -4.0021 | -5.5274
|  | TARBERT | HT |  |  |  |  | 1.1442 | 1.1063 | 1.0684 | 1.0221 | 0.88947 | 0.75684 | 0.62421 | 0.48 | 0.31789 | -1.0337 | -2.6611 | -3.7989 | 1.0379 | 0.97263 | 0.90632 | 0.84211 | 0.72105 | 0.60211 | 0.48211 | 0.35263 | 0.20526 | -1.2495 | -3.0474 | -4.3411 | 1.0074 | 0.94316 | 0.87895 | 0.81579 | 0.68211 | 0.54737 | 0.41263 | 0.26526 | 0.098947 | -1.4474 | -3.3074 | -4.6211
|  | TARBERT | HE |  |  |  |  | 1.1895 | 1.1695 | 1.1474 | 1.1232 | 1.0137 | 0.91895 | 0.76421 | 0.60842 | 0.37579 | -0.59368 | -1.86 | -3.2316 | 1.1105 | 1.0916 | 1.0684 | 1.0368 | 0.92105 | 0.79368 | 0.63579 | 0.48737 | 0.24632 | -0.75789 | -2.0905 | -3.5337 | 1.0074 | 0.94316 | 0.87895 | 0.81579 | 0.68211 | 0.54737 | 0.41263 | 0.26526 | 0.098947 | -1.4474 | -3.3074 | -4.6211
|  | TARBERT | CF |  |  |  |  | 1.2074 | 1.1958 | 1.1842 | 1.1726 | 1.1295 | 1.0895 | 1.0505 | 1.0011 | 0.87895 | 0.35368 | -0.44526 | -1.3705 | 1.1295 | 1.1179 | 1.1063 | 1.0958 | 1.0579 | 1.0105 | 0.96105 | 0.84842 | 0.71263 | 0.14 | -0.71263 | -1.7284 | 1.1326 | 1.1137 | 1.0916 | 1.0737 | 1.0168 | 0.96211 | 0.90737 | 0.79579 | 0.66421 | 0.053684 | -0.85158 | -1.9095
| PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.19895 | 0.19895 | 0.19789 | 0.19579 | 0.19474 | 0.19053 | 0.18632 | 0.18316 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19684 | 0.19579 | 0.19474 | 0.19263 | 0.19158 | 0.18632 | 0.18211 | 0.17789 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19263 | 0.18737 | 0.18316 | 0.17895
|  | TARBERT JURA | EE |  |  |  |  | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19789 | 0.19474 | 0.19158 | 0.18737 | 0.20105 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19474 | 0.19053 | 0.18737 | 0.18316 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19158 | 0.18842 | 0.18421
|  | TARBERT JURA | HT |  |  |  |  | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.19895 | 0.19895 | 0.19789 | 0.19579 | 0.19474 | 0.19053 | 0.18632 | 0.18316 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19684 | 0.19579 | 0.19474 | 0.19263 | 0.19158 | 0.18632 | 0.18211 | 0.17789 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19263 | 0.18737 | 0.18316 | 0.17895
|  | TARBERT JURA | HE |  |  |  |  | 0.20526 | 0.20526 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20105 | 0.19895 | 0.19789 | 0.19579 | 0.20316 | 0.20316 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.19684 | 0.19474 | 0.19263 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19263 | 0.18737 | 0.18316 | 0.17895
|  | TARBERT JURA | CF |  |  |  |  | 0.20526 | 0.20526 | 0.20526 | 0.20526 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.2 | 0.2 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.19895 | 0.19789
| PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 0 | 3.1179 | 3.0663 | 3.0137 | 2.9568 | 2.6263 | 2.1232 | 1.6653 | 1.2684 | 0.86947 | -2.7063 | -6.8326 | -9.8484 | 2.8326 | 2.7021 | 2.6179 | 2.4884 | 2.2168 | 1.8232 | 1.4568 | 1.1189 | 0.75684 | -2.5968 | -6.6 | -9.8495 | 2.9 | 2.7768 | 2.6947 | 2.5684 | 2.2284 | 1.7042 | 1.2326 | 0.82211 | 0.40947 | -3.4232 | -7.8895 | -11.28
|  | TARBERT LOCH FYNE | EE |  |  |  |  | 3.1389 | 3.0874 | 3.0337 | 2.9779 | 2.6453 | 2.1232 | 1.6653 | 1.2684 | 0.86947 | -2.7063 | -6.8326 | -9.8484 | 2.8958 | 2.7968 | 2.7137 | 2.5989 | 2.2684 | 1.8232 | 1.4568 | 1.1189 | 0.78211 | -2.5968 | -6.6 | -9.8495 | 2.9568 | 2.8568 | 2.7716 | 2.6579 | 2.2442 | 1.7042 | 1.2326 | 0.82211 | 0.40947 | -3.4232 | -7.8895 | -11.28
|  | TARBERT LOCH FYNE | HT |  |  |  |  | 3.1179 | 3.0663 | 3.0137 | 2.9568 | 2.6263 | 2.2747 | 1.9368 | 1.5421 | 1.0189 | -2.3095 | -5.9632 | -8.4232 | 2.8326 | 2.7021 | 2.6179 | 2.4884 | 2.2168 | 1.9189 | 1.6389 | 1.3137 | 0.84105 | -2.5232 | -6.4768 | -9.2284 | 2.9 | 2.7768 | 2.6947 | 2.5684 | 2.2284 | 1.8632 | 1.5147 | 1.1053 | 0.55474 | -3.0842 | -7.2189 | -10.0442
|  | TARBERT LOCH FYNE | HE |  |  |  |  | 3.1674 | 3.1411 | 3.1126 | 3.0832 | 2.7389 | 2.3947 | 1.9958 | 1.5663 | 0.95895 | -1.6274 | -4.7642 | -8.1705 | 2.9568 | 2.8853 | 2.8358 | 2.7326 | 2.4147 | 2.0737 | 1.7274 | 1.3474 | 0.75684 | -1.7242 | -4.8842 | -8.3242 | 2.9 | 2.7768 | 2.6947 | 2.5684 | 2.2284 | 1.8632 | 1.5147 | 1.1053 | 0.55474 | -3.0842 | -7.2189 | -10.0442
|  | TARBERT LOCH FYNE | CF |  |  |  |  | 3.1863 | 3.1705 | 3.1547 | 3.1379 | 3.0074 | 2.8905 | 2.7758 | 2.6105 | 2.3232 | 0.99895 | -0.97579 | -3.1179 | 3.0158 | 2.9842 | 2.9558 | 2.9147 | 2.7863 | 2.6474 | 2.5021 | 2.2389 | 1.9295 | 0.60526 | -1.3979 | -3.6884 | 3.0674 | 3.0379 | 3.0084 | 2.9705 | 2.8074 | 2.6432 | 2.4737 | 2.2095 | 1.8905 | 0.44842 | -1.7295 | -4.1495
| TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | NO | YES | 0 | 2.5863 | 2.4453 | 2.3 | 2.1505 | 1.9747 | 1.8179 | 1.6589 | 1.4979 | 1.3347 | 0.59579 | -0.02 | -0.62526 | 2.4284 | 2.2737 | 2.1105 | 1.9453 | 1.7747 | 1.6232 | 1.4674 | 1.3105 | 1.1516 | 0.43474 | -0.1621 | -0.75158 | 2.3853 | 2.24 | 2.0895 | 1.9368 | 1.7789 | 1.6326 | 1.4695 | 1.3063 | 1.1411 | 0.38947 | -0.23895 | -0.85474
|  | TAYNUILT | EE |  |  |  |  | 2.5863 | 2.4453 | 2.3 | 2.1505 | 1.9747 | 1.8179 | 1.6589 | 1.4979 | 1.3347 | 0.59579 | -0.02 | -0.62526 | 2.4284 | 2.2737 | 2.1105 | 1.9453 | 1.7747 | 1.6232 | 1.4674 | 1.3105 | 1.1516 | 0.43474 | -0.1621 | -0.75158 | 2.3853 | 2.24 | 2.0895 | 1.9368 | 1.7789 | 1.6326 | 1.4695 | 1.3063 | 1.1411 | 0.38947 | -0.23895 | -0.85474
|  | TAYNUILT | HT |  |  |  |  | 2.6316 | 2.5684 | 2.5032 | 2.4389 | 2.3726 | 2.3063 | 2.24 | 2.18 | 2.1179 | 1.8337 | 1.5747 | 1.3274 | 2.4916 | 2.4263 | 2.3579 | 2.2905 | 2.2221 | 2.1526 | 2.0853 | 2.0221 | 1.9568 | 1.6621 | 1.3895 | 1.1284 | 2.44 | 2.3695 | 2.2989 | 2.2284 | 2.1568 | 2.0842 | 2.0137 | 1.9474 | 1.88 | 1.5737 | 1.2895 | 1.0179
|  | TAYNUILT | HE |  |  |  |  | 2.6884 | 2.64 | 2.5916 | 2.54 | 2.4874 | 2.4347 | 2.3821 | 2.3295 | 2.2789 | 2.0463 | 1.8021 | 1.5568 | 2.5421 | 2.4884 | 2.4358 | 2.38 | 2.3232 | 2.2684 | 2.2105 | 2.1547 | 2.1011 | 1.8463 | 1.6042 | 1.3663 | 2.44 | 2.3695 | 2.2989 | 2.2284 | 2.1568 | 2.0842 | 2.0137 | 1.9474 | 1.88 | 1.5737 | 1.2895 | 1.0179
|  | TAYNUILT | CF |  |  |  |  | 2.7284 | 2.7095 | 2.6905 | 2.6726 | 2.6547 | 2.6368 | 2.6168 | 2.6021 | 2.5832 | 2.5021 | 2.4389 | 2.3895 | 2.5853 | 2.5663 | 2.5484 | 2.5305 | 2.5126 | 2.4958 | 2.4768 | 2.46 | 2.4421 | 2.36 | 2.2968 | 2.2474 | 2.5432 | 2.5232 | 2.5032 | 2.4832 | 2.4642 | 2.4432 | 2.4242 | 2.4053 | 2.3853 | 2.2989 | 2.2305 | 2.1747
| BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 0 | 27.48 | 27.1811 | 26.9263 | 26.6568 | 26.3684 | 26.1021 | 25.8337 | 25.5547 | 25.2832 | 24.1821 | 23.2526 | 22.4326 | 25.9789 | 25.6737 | 25.4147 | 25.14 | 24.8484 | 24.58 | 24.3063 | 24.0221 | 23.7453 | 22.62 | 21.6653 | 20.8211 | 25.8284 | 25.6358 | 25.4463 | 25.2442 | 25.0189 | 24.8147 | 24.6147 | 24.4158 | 24.2232 | 23.5211 | 22.9863 | 22.5547
|  | THIMBLEROW | EE |  |  |  |  | 27.68 | 27.4747 | 27.2547 | 27.0432 | 26.8358 | 26.6358 | 26.4526 | 26.2747 | 26.0979 | 25.2937 | 24.6274 | 24.0579 | 26.1821 | 25.9726 | 25.7474 | 25.5316 | 25.32 | 25.1179 | 24.9316 | 24.7505 | 24.5716 | 23.7516 | 23.0674 | 22.48 | 25.9632 | 25.8316 | 25.6937 | 25.5505 | 25.4053 | 25.2632 | 25.1274 | 24.9947 | 24.8674 | 24.3137 | 23.9474 | 23.6737
|  | THIMBLEROW | HT |  |  |  |  | 27.48 | 27.1811 | 26.9263 | 26.6568 | 26.3684 | 26.1021 | 25.8337 | 25.5547 | 25.2832 | 24.1821 | 23.2526 | 22.4326 | 25.9789 | 25.6737 | 25.4147 | 25.14 | 24.8484 | 24.58 | 24.3063 | 24.0221 | 23.7453 | 22.62 | 21.6653 | 20.8211 | 25.8284 | 25.6358 | 25.4463 | 25.2442 | 25.0189 | 24.8147 | 24.6147 | 24.4158 | 24.2232 | 23.5211 | 22.9863 | 22.5547
|  | THIMBLEROW | HE |  |  |  |  | 27.8253 | 27.6611 | 27.4821 | 27.3189 | 27.1579 | 27.0074 | 26.8663 | 26.7326 | 26.6042 | 26.1295 | 25.8084 | 25.5705 | 26.3389 | 26.1632 | 25.9811 | 25.8147 | 25.6516 | 25.5 | 25.3568 | 25.2211 | 25.0916 | 24.6084 | 24.28 | 24.0347 | 25.8284 | 25.6358 | 25.4463 | 25.2442 | 25.0189 | 24.8147 | 24.6147 | 24.4158 | 24.2232 | 23.5211 | 22.9863 | 22.5547
|  | THIMBLEROW | CF |  |  |  |  | 27.9221 | 27.8295 | 27.7316 | 27.6232 | 27.5168 | 27.4042 | 27.2895 | 27.1842 | 27.0768 | 26.6084 | 26.3147 | 26.1011 | 26.4484 | 26.3474 | 26.24 | 26.1274 | 26.0179 | 25.9042 | 25.7863 | 25.6789 | 25.5705 | 25.0937 | 24.7926 | 24.5726 | 26.1147 | 26.0442 | 25.9716 | 25.8958 | 25.8211 | 25.7453 | 25.6663 | 25.5916 | 25.5158 | 25.1895 | 25.0137 | 24.9116
| TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0 | 0.21158 | 0.21053 | 0.20737 | 0.20632 | 0.20421 | 0.20211 | 0.2 | 0.19789 | 0.19684 | 0.18842 | 0.18211 | 0.17579 | 0.20632 | 0.20526 | 0.20421 | 0.20316 | 0.20105 | 0.19789 | 0.19684 | 0.19368 | 0.19263 | 0.18316 | 0.17579 | 0.16842 | 0.20632 | 0.20526 | 0.20316 | 0.20105 | 0.19895 | 0.19579 | 0.19368 | 0.19158 | 0.19053 | 0.18105 | 0.17368 | 0.16632
|  | TIRORAN BRIDGE | EE |  |  |  |  | 0.21263 | 0.21158 | 0.21053 | 0.20842 | 0.20737 | 0.20526 | 0.20421 | 0.20316 | 0.20105 | 0.19474 | 0.18947 | 0.18421 | 0.20632 | 0.20632 | 0.20526 | 0.20421 | 0.20421 | 0.20211 | 0.20105 | 0.19895 | 0.19684 | 0.19053 | 0.18421 | 0.17895 | 0.20737 | 0.20632 | 0.20526 | 0.20421 | 0.20316 | 0.2 | 0.19895 | 0.19684 | 0.19474 | 0.18842 | 0.18211 | 0.17684
|  | TIRORAN BRIDGE | HT |  |  |  |  | 0.21158 | 0.21053 | 0.20737 | 0.20632 | 0.20421 | 0.20211 | 0.2 | 0.19789 | 0.19684 | 0.18842 | 0.18211 | 0.17579 | 0.20632 | 0.20526 | 0.20421 | 0.20316 | 0.20105 | 0.19789 | 0.19684 | 0.19368 | 0.19263 | 0.18316 | 0.17579 | 0.16842 | 0.20632 | 0.20526 | 0.20316 | 0.20105 | 0.19895 | 0.19579 | 0.19368 | 0.19158 | 0.19053 | 0.18105 | 0.17368 | 0.16632
|  | TIRORAN BRIDGE | HE |  |  |  |  | 0.21368 | 0.21368 | 0.21263 | 0.21263 | 0.21158 | 0.21053 | 0.20947 | 0.20842 | 0.20737 | 0.20421 | 0.20105 | 0.19895 | 0.20737 | 0.20737 | 0.20632 | 0.20632 | 0.20526 | 0.20526 | 0.20421 | 0.20421 | 0.20316 | 0.20105 | 0.19684 | 0.19474 | 0.20632 | 0.20526 | 0.20316 | 0.20105 | 0.19895 | 0.19579 | 0.19368 | 0.19158 | 0.19053 | 0.18105 | 0.17368 | 0.16632
|  | TIRORAN BRIDGE | CF |  |  |  |  | 0.21368 | 0.21368 | 0.21368 | 0.21368 | 0.21263 | 0.21263 | 0.21263 | 0.21263 | 0.21053 | 0.20737 | 0.20632 | 0.20526 | 0.20737 | 0.20737 | 0.20737 | 0.20737 | 0.20632 | 0.20632 | 0.20632 | 0.20632 | 0.20526 | 0.20421 | 0.20316 | 0.20105 | 0.20947 | 0.20947 | 0.20947 | 0.20947 | 0.20737 | 0.20737 | 0.20737 | 0.20737 | 0.20526 | 0.20316 | 0.20105 | 0.19895
| BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 0 | 1.1568 | 1.1326 | 1.1 | 1.0684 | 0.61263 | 0.15474 | -0.31368 | -0.6779 | -1.0684 | -3.3263 | -6.5284 | -8.9474 | 1.0568 | 1.04 | 1.0232 | 1.0053 | 0.54947 | 0.087368 | -0.38632 | -0.7221 | -0.99053 | -3.0705 | -6.2168 | -8.8421 | 1.02 | 0.98526 | 0.95263 | 0.91895 | 0.41158 | -0.094737 | -0.61579 | -1.0053 | -1.3905 | -3.7958 | -7.2926 | -10.0484
|  | TOMATIN | EE |  |  |  |  | 1.1642 | 1.1368 | 1.1084 | 1.0737 | 0.82421 | 0.50842 | -0.028421 | -0.54105 | -1.0684 | -3.3263 | -6.5284 | -8.9474 | 1.0642 | 1.0463 | 1.0284 | 1.0095 | 0.80842 | 0.55263 | 0.021053 | -0.4779 | -0.99053 | -3.0705 | -6.2168 | -8.8421 | 1.0358 | 0.99895 | 0.96211 | 0.92632 | 0.66947 | 0.35579 | -0.24947 | -0.81158 | -1.3905 | -3.7958 | -7.2926 | -10.0484
|  | TOMATIN | HT |  |  |  |  | 1.1568 | 1.1326 | 1.1 | 1.0684 | 0.61263 | 0.15474 | -0.31368 | -0.6779 | -0.9379 | -3.0347 | -5.9505 | -7.9263 | 1.0568 | 1.04 | 1.0232 | 1.0053 | 0.54947 | 0.087368 | -0.38632 | -0.7221 | -0.93474 | -3.0305 | -6.1989 | -8.4253 | 1.02 | 0.98526 | 0.95263 | 0.91895 | 0.41158 | -0.094737 | -0.61579 | -1.0053 | -1.2726 | -3.5895 | -6.9095 | -9.1884
|  | TOMATIN | HE |  |  |  |  | 1.1747 | 1.1653 | 1.1537 | 1.1432 | 0.82421 | 0.50211 | 0.17474 | -0.15053 | -0.60105 | -2.5737 | -5.0474 | -7.7495 | 1.0737 | 1.0663 | 1.0579 | 1.0484 | 0.80211 | 0.50211 | 0.19684 | -0.10632 | -0.54632 | -2.4737 | -4.9916 | -7.7442 | 1.02 | 0.98526 | 0.95263 | 0.91895 | 0.41158 | -0.094737 | -0.61579 | -1.0053 | -1.2726 | -3.5895 | -6.9095 | -9.1884
|  | TOMATIN | CF |  |  |  |  | 1.1811 | 1.1758 | 1.1684 | 1.1632 | 1.0737 | 0.98842 | 0.79895 | 0.59895 | 0.37579 | -0.63368 | -2.1726 | -3.8842 | 1.08 | 1.0758 | 1.0695 | 1.0653 | 1.02 | 0.96211 | 0.77053 | 0.56842 | 0.32632 | -0.70526 | -2.3 | -4.1558 | 1.0674 | 1.0579 | 1.0474 | 1.04 | 0.93579 | 0.84421 | 0.62842 | 0.40526 | 0.15158 | -0.97579 | -2.7053 | -4.6579
| LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | YES | 0 | 0.10211 | 0.1 | 0.098947 | 0.096842 | 0.075789 | 0.051579 | 0.026316 | 0.0021053 | -0.04 | -0.27053 | -0.59263 | -0.82316 | 0.10105 | 0.098947 | 0.097895 | 0.095789 | 0.075789 | 0.051579 | 0.026316 | 0.0031579 | -0.042105 | -0.29158 | -0.6579 | -0.92526 | 0.10105 | 0.098947 | 0.097895 | 0.094737 | 0.082105 | 0.066316 | 0.049474 | 0.027368 | -0.030526 | -0.31684 | -0.69053 | -0.95895
|  | TORBOLL | EE |  |  |  |  | 0.10211 | 0.10105 | 0.1 | 0.096842 | 0.083158 | 0.067368 | 0.051579 | 0.037895 | 0.0031579 | -0.25158 | -0.54316 | -0.81263 | 0.10105 | 0.1 | 0.1 | 0.095789 | 0.085263 | 0.073684 | 0.06 | 0.048421 | 0.014737 | -0.25263 | -0.5621 | -0.86737 | 0.10105 | 0.1 | 0.098947 | 0.094737 | 0.082105 | 0.066316 | 0.049474 | 0.03579 | -0.001053 | -0.28842 | -0.61684 | -0.92842
|  | TORBOLL | HT |  |  |  |  | 0.10211 | 0.1 | 0.098947 | 0.097895 | 0.087368 | 0.076842 | 0.055789 | 0.031579 | -0.017895 | -0.27053 | -0.59263 | -0.82316 | 0.10105 | 0.098947 | 0.097895 | 0.097895 | 0.088421 | 0.081053 | 0.058947 | 0.037895 | -0.016842 | -0.29158 | -0.6579 | -0.92526 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.086316 | 0.075789 | 0.052632 | 0.027368 | -0.030526 | -0.31684 | -0.69053 | -0.95895
|  | TORBOLL | HE |  |  |  |  | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.075789 | 0.051579 | 0.026316 | 0.0021053 | -0.04 | -0.21474 | -0.45684 | -0.7221 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.075789 | 0.051579 | 0.026316 | 0.0031579 | -0.042105 | -0.22421 | -0.48842 | -0.77895 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.086316 | 0.075789 | 0.052632 | 0.027368 | -0.030526 | -0.31684 | -0.69053 | -0.95895
|  | TORBOLL | CF |  |  |  |  | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.096842 | 0.091579 | 0.071579 | 0.051579 | 0.027368 | -0.069474 | -0.22526 | -0.41158 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.096842 | 0.092632 | 0.070526 | 0.049474 | 0.022105 | -0.084211 | -0.25368 | -0.46526 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.095789 | 0.090526 | 0.067368 | 0.045263 | 0.016842 | -0.093684 | -0.27053 | -0.48526
| KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 0.812 | 23.8859 | 23.4764 | 23.0154 | 22.4975 | 21.4606 | 20.4396 | 19.4238 | 18.3459 | 17.2733 | 12.5764 | 9.6512 | 7.3869 | 20.7596 | 20.2901 | 19.7564 | 19.1501 | 18.0396 | 16.9469 | 15.8596 | 14.7312 | 13.6091 | 9.1175 | 6.6796 | 4.3227 | 22.0806 | 21.6743 | 21.2196 | 20.6943 | 19.5848 | 18.4312 | 17.2827 | 16.0754 | 14.8722 | 9.7796 | 6.7901 | 4.2817
|  | TORRYBURN | EE |  |  |  |  | 24.0406 | 23.6848 | 23.2743 | 22.8143 | 21.7354 | 20.5975 | 19.4796 | 18.4385 | 17.3943 | 12.5764 | 9.6512 | 7.3869 | 20.9301 | 20.5248 | 20.0522 | 19.5185 | 18.3817 | 17.2091 | 16.0669 | 14.9848 | 13.9038 | 9.1175 | 6.6796 | 4.3227 | 22.2343 | 21.8817 | 21.4764 | 21.0217 | 19.8901 | 18.6322 | 17.3891 | 16.2227 | 15.0543 | 9.7796 | 6.7901 | 4.2817
|  | TORRYBURN | HT |  |  |  |  | 23.8859 | 23.4764 | 23.0154 | 22.4975 | 21.4606 | 20.4396 | 19.4238 | 18.3459 | 17.2733 | 13.0596 | 11.4112 | 8.3301 | 20.7596 | 20.2901 | 19.7564 | 19.1501 | 18.0396 | 16.9469 | 15.8596 | 14.7312 | 13.6091 | 9.2869 | 7.7575 | 4.3469 | 22.0806 | 21.6743 | 21.2196 | 20.6943 | 19.5848 | 18.4312 | 17.2827 | 16.0754 | 14.8722 | 10.2112 | 8.4848 | 4.9648
|  | TORRYBURN | HE |  |  |  |  | 24.1859 | 23.9427 | 23.6301 | 23.2459 | 22.2806 | 21.3322 | 20.4027 | 19.4796 | 18.5691 | 14.7575 | 13.008 | 9.9217 | 21.0806 | 20.7964 | 20.4259 | 19.9669 | 18.9817 | 17.9796 | 17.0006 | 16.028 | 15.0691 | 11.1512 | 9.7027 | 6.7027 | 22.0806 | 21.6743 | 21.2196 | 20.6943 | 19.5848 | 18.4312 | 17.2827 | 16.0754 | 14.8722 | 10.2112 | 8.4848 | 4.9648
|  | TORRYBURN | CF |  |  |  |  | 24.4122 | 24.3312 | 24.2375 | 24.1343 | 23.8491 | 23.4112 | 22.9554 | 22.5112 | 22.0764 | 19.9522 | 18.8206 | 16.4691 | 21.3469 | 21.2564 | 21.1533 | 21.0364 | 20.7648 | 20.2912 | 19.7943 | 19.3017 | 18.8038 | 16.4869 | 15.5333 | 12.8922 | 22.6027 | 22.5217 | 22.4291 | 22.3269 | 22.0417 | 21.608 | 21.1564 | 20.7133 | 20.2469 | 17.8438 | 16.6869 | 13.928
| LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | YES | 0 | 0.54947 | 0.52316 | 0.49789 | 0.47158 | 0.27789 | 0.023158 | -0.23895 | -0.49053 | -0.86 | -3.0316 | -5.64 | -7.6874 | 0.48421 | 0.45895 | 0.43474 | 0.40842 | 0.25579 | 0.018947 | -0.22632 | -0.45789 | -0.83579 | -2.9116 | -5.6274 | -7.7042 | 0.49263 | 0.46737 | 0.44211 | 0.41474 | 0.22105 | -0.016842 | -0.26526 | -0.4779 | -0.88632 | -3.3421 | -6.1937 | -8.5347
|  | TRESSADY | EE |  |  |  |  | 0.56105 | 0.53368 | 0.50421 | 0.47579 | 0.27789 | 0.041053 | -0.20421 | -0.41579 | -0.72105 | -3.0316 | -5.64 | -7.6874 | 0.49789 | 0.47263 | 0.44632 | 0.42105 | 0.26632 | 0.074737 | -0.12421 | -0.29579 | -0.57684 | -2.8632 | -5.4642 | -7.7042 | 0.50421 | 0.47684 | 0.44842 | 0.42 | 0.22105 | -0.016842 | -0.26526 | -0.4779 | -0.78947 | -3.3421 | -6.1937 | -8.5347
|  | TRESSADY | HT |  |  |  |  | 0.54947 | 0.52316 | 0.49789 | 0.47158 | 0.30526 | 0.13789 | -0.051579 | -0.31368 | -0.75684 | -2.8811 | -5.3495 | -7.0421 | 0.48421 | 0.45895 | 0.43474 | 0.40842 | 0.28105 | 0.14211 | -0.02 | -0.25579 | -0.70632 | -2.9116 | -5.6274 | -7.5442 | 0.49263 | 0.46737 | 0.44211 | 0.41474 | 0.24842 | 0.08 | -0.11263 | -0.38526 | -0.88632 | -3.2526 | -6.0716 | -8.0295
|  | TRESSADY | HE |  |  |  |  | 0.57579 | 0.56632 | 0.55579 | 0.54316 | 0.27895 | 0.023158 | -0.23895 | -0.49053 | -0.86 | -2.4663 | -4.5084 | -6.7368 | 0.51579 | 0.50421 | 0.49368 | 0.48211 | 0.25579 | 0.018947 | -0.22632 | -0.45789 | -0.83579 | -2.4179 | -4.5211 | -6.8221 | 0.49263 | 0.46737 | 0.44211 | 0.41474 | 0.24842 | 0.08 | -0.11263 | -0.38526 | -0.88632 | -3.2526 | -6.0716 | -8.0295
|  | TRESSADY | CF |  |  |  |  | 0.58211 | 0.57684 | 0.57158 | 0.56526 | 0.48526 | 0.41368 | 0.25895 | 0.1 | -0.078947 | -0.9179 | -2.2074 | -3.6568 | 0.52526 | 0.51789 | 0.51158 | 0.50526 | 0.44421 | 0.38842 | 0.22632 | 0.054737 | -0.15263 | -1.0116 | -2.3516 | -3.9295 | 0.52632 | 0.52 | 0.51368 | 0.50737 | 0.42632 | 0.35368 | 0.18947 | 0.0073684 | -0.20421 | -1.1295 | -2.5695 | -4.2189
| SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 0 | 6.6421 | 6.5642 | 6.4863 | 6.4095 | 6.2295 | 6.0505 | 5.8442 | 5.6484 | 5.4516 | 4.1284 | 2.5505 | 1.4937 | 6.1463 | 6.0653 | 5.9832 | 5.9042 | 5.7432 | 5.5842 | 5.4253 | 5.2505 | 5.0747 | 3.9011 | 2.4074 | 1.2905 | 6.1884 | 6.1042 | 6.0211 | 5.94 | 5.7547 | 5.5716 | 5.3674 | 5.1653 | 4.9621 | 3.5653 | 1.8737 | 0.70316
|  | TUMBLIN | EE |  |  |  |  | 6.6874 | 6.62 | 6.5495 | 6.4811 | 6.2916 | 6.0695 | 5.8442 | 5.6484 | 5.4516 | 4.1284 | 2.5505 | 1.4937 | 6.1947 | 6.1263 | 6.0547 | 5.9863 | 5.8211 | 5.6326 | 5.4421 | 5.2747 | 5.1074 | 3.9011 | 2.4074 | 1.2905 | 6.2368 | 6.1653 | 6.0905 | 6.0189 | 5.8253 | 5.5989 | 5.3674 | 5.1653 | 4.9621 | 3.5653 | 1.8737 | 0.70316
|  | TUMBLIN | HT |  |  |  |  | 6.6421 | 6.5642 | 6.4863 | 6.4095 | 6.2295 | 6.0505 | 5.8705 | 5.6695 | 5.4684 | 4.3095 | 3.0053 | 2.1474 | 6.1463 | 6.0653 | 5.9832 | 5.9042 | 5.7432 | 5.5842 | 5.4253 | 5.2505 | 5.0747 | 3.9558 | 2.58 | 1.6442 | 6.1884 | 6.1042 | 6.0211 | 5.94 | 5.7547 | 5.5716 | 5.3874 | 5.1811 | 4.9716 | 3.7316 | 2.2726 | 1.3
|  | TUMBLIN | HE |  |  |  |  | 6.7516 | 6.7147 | 6.6758 | 6.6326 | 6.4453 | 6.2832 | 6.1221 | 5.9368 | 5.6968 | 4.6779 | 3.5179 | 2.2747 | 6.2663 | 6.2263 | 6.1863 | 6.1421 | 5.9842 | 5.8474 | 5.7116 | 5.5474 | 5.3179 | 4.3642 | 3.2263 | 2.0053 | 6.1884 | 6.1042 | 6.0211 | 5.94 | 5.7547 | 5.5716 | 5.3874 | 5.1811 | 4.9716 | 3.7316 | 2.2726 | 1.3
|  | TUMBLIN | CF |  |  |  |  | 6.7726 | 6.7589 | 6.74 | 6.7158 | 6.6379 | 6.5663 | 6.4937 | 6.4284 | 6.3211 | 5.8 | 5.0726 | 4.3221 | 6.3042 | 6.2779 | 6.2526 | 6.2274 | 6.16 | 6.0968 | 6.0347 | 5.9747 | 5.8642 | 5.3558 | 4.6368 | 3.8558 | 6.3463 | 6.3189 | 6.2947 | 6.2684 | 6.1895 | 6.1158 | 6.0421 | 5.9737 | 5.8547 | 5.2947 | 4.5011 | 3.6621
| TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 0 | 1.1389 | 1.0811 | 1.02 | 0.96316 | 0.32526 | -0.42316 | -1.1916 | -1.9263 | -2.9621 | -9.3147 | -16.5989 | -21.8947 | 1.0116 | 0.98842 | 0.96 | 0.93053 | 0.34421 | -0.33053 | -1.0284 | -1.6895 | -2.7032 | -8.4547 | -15.4821 | -21.2179 | 1.0484 | 0.99789 | 0.94421 | 0.89263 | 0.24421 | -0.51895 | -1.3011 | -1.9737 | -2.9421 | -10.0389 | -17.9526 | -24.0116
|  | TUMMEL BRIDGE | EE |  |  |  |  | 1.1389 | 1.0811 | 1.02 | 0.96316 | 0.33474 | -0.41368 | -1.1811 | -1.8453 | -2.7958 | -9.3147 | -16.5989 | -21.8947 | 1.0179 | 0.98947 | 0.96 | 0.93053 | 0.40842 | -0.20211 | -0.82526 | -1.3621 | -2.2137 | -8.4547 | -15.4821 | -21.2179 | 1.0495 | 0.99789 | 0.94421 | 0.89263 | 0.24421 | -0.51895 | -1.3011 | -1.9737 | -2.9421 | -10.0389 | -17.9526 | -24.0116
|  | TUMMEL BRIDGE | HT |  |  |  |  | 1.1389 | 1.0989 | 1.0579 | 1.0084 | 0.48737 | -0.021053 | -0.63368 | -1.4095 | -2.6358 | -8.3484 | -14.74 | -19.0358 | 1.0116 | 0.98842 | 0.96526 | 0.94 | 0.51053 | 0.092632 | -0.44316 | -1.12 | -2.3295 | -8.1189 | -15.0105 | -19.8179 | 1.0484 | 1.0137 | 0.97579 | 0.93263 | 0.40316 | -0.11368 | -0.74737 | -1.5432 | -2.9 | -9.2705 | -16.5337 | -21.479
|  | TUMMEL BRIDGE | HE |  |  |  |  | 1.1568 | 1.1411 | 1.1232 | 1.1053 | 0.32526 | -0.42316 | -1.1916 | -1.9263 | -2.9621 | -7.4832 | -13.0063 | -19.0705 | 1.0284 | 1.0189 | 1.0095 | 0.99895 | 0.34421 | -0.33053 | -1.0284 | -1.6895 | -2.7032 | -7.0147 | -12.6032 | -18.7137 | 1.0484 | 1.0137 | 0.97579 | 0.93263 | 0.40316 | -0.11368 | -0.74737 | -1.5432 | -2.9 | -9.2705 | -16.5337 | -21.479
|  | TUMMEL BRIDGE | CF |  |  |  |  | 1.1663 | 1.1568 | 1.1463 | 1.1368 | 0.90421 | 0.69579 | 0.26737 | -0.1621 | -0.63474 | -2.8968 | -6.3747 | -10.1737 | 1.0358 | 1.0295 | 1.0232 | 1.0179 | 0.88316 | 0.70842 | 0.26947 | -0.17474 | -0.69895 | -2.9758 | -6.5053 | -10.5642 | 1.0737 | 1.0653 | 1.0568 | 1.0474 | 0.83895 | 0.62 | 0.13474 | -0.35684 | -0.91263 | -3.4179 | -7.2716 | -11.5621
| MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | YES | 0.111 | 4.3958 | 4.0095 | 3.4927 | 2.8548 | 1.5885 | 0.19268 | -1.3442 | -2.7315 | -6.0515 | -10.4136 | -17.9915 | -23.9568 | 6.149 | 5.669 | 5.1027 | 4.3943 | 3.2227 | 2.0816 | 0.75637 | -0.47521 | -3.0942 | -6.8415 | -13.9405 | -20.1668 | 5.6461 | 5.3556 | 5.0356 | 4.5124 | 3.1672 | 1.6787 | 0.045053 | -1.4286 | -4.9444 | -9.5234 | -17.5118 | -23.8971
|  | TURRIFF | EE |  |  |  |  | 4.4916 | 4.2432 | 3.7916 | 3.219 | 1.8032 | 0.19268 | -1.3442 | -2.7315 | -6.0515 | -10.4136 | -17.9915 | -23.9568 | 6.3406 | 5.9353 | 5.4511 | 4.8237 | 3.5406 | 2.0985 | 0.75637 | -0.47521 | -3.0942 | -6.8415 | -13.9405 | -20.1668 | 5.7693 | 5.5051 | 5.2114 | 4.8672 | 3.3924 | 1.6787 | 0.045053 | -1.4286 | -4.9444 | -9.5234 | -17.5118 | -23.8971
|  | TURRIFF | HT |  |  |  |  | 4.3958 | 4.0095 | 3.4927 | 2.8548 | 1.5885 | 0.35058 | -0.90732 | -2.3294 | -5.6368 | -9.0315 | -15.9063 | -20.6189 | 6.149 | 5.669 | 5.1027 | 4.3943 | 3.2227 | 2.0816 | 0.92163 | -0.36574 | -2.991 | -6.1047 | -13.41 | -18.5573 | 5.6461 | 5.3556 | 5.0356 | 4.5124 | 3.1672 | 1.8524 | 0.51558 | -0.99495 | -4.4981 | -8.1002 | -15.4697 | -20.7486
|  | TURRIFF | HE |  |  |  |  | 4.619 | 4.5116 | 4.2516 | 3.7748 | 2.3369 | 1.0453 | -0.17047 | -1.3442 | -3.3705 | -6.4389 | -12.4694 | -19.7536 | 6.5774 | 6.3016 | 5.9164 | 5.3743 | 4.0869 | 2.9058 | 1.8111 | 0.76689 | -0.84574 | -3.511 | -9.4184 | -16.4047 | 5.6461 | 5.3556 | 5.0356 | 4.5124 | 3.1672 | 1.8524 | 0.51558 | -0.99495 | -4.4981 | -8.1002 | -15.4697 | -20.7486
|  | TURRIFF | CF |  |  |  |  | 4.7043 | 4.6443 | 4.5801 | 4.5127 | 4.0158 | 3.4853 | 2.9043 | 2.4043 | 2.0401 | -0.34732 | -4.5136 | -8.7599 | 6.7248 | 6.6153 | 6.4753 | 6.2606 | 5.7743 | 5.2848 | 4.7343 | 4.2574 | 3.9122 | 1.7332 | -2.3278 | -6.7289 | 6.0493 | 5.964 | 5.8693 | 5.7598 | 5.3072 | 4.8861 | 4.4461 | 4.0198 | 3.6324 | 1.0914 | -3.3865 | -7.976
| RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 0 | 0.66105 | 0.65158 | 0.64105 | 0.63158 | 0.57368 | 0.50737 | 0.43684 | 0.37263 | 0.29053 | -0.16842 | -0.73895 | -1.0842 | 0.86737 | 0.85895 | 0.85053 | 0.84211 | 0.81158 | 0.77684 | 0.73895 | 0.70632 | 0.65474 | 0.26105 | -0.26632 | -0.62632 | 0.92737 | 0.91789 | 0.90842 | 0.89789 | 0.84421 | 0.77895 | 0.71053 | 0.65368 | 0.59263 | 0.13158 | -0.48 | -0.87053
|  | TYNDRUM | EE |  |  |  |  | 0.66316 | 0.65263 | 0.64316 | 0.63158 | 0.57368 | 0.50737 | 0.43684 | 0.37263 | 0.29053 | -0.16842 | -0.73895 | -1.0842 | 0.87053 | 0.86211 | 0.85579 | 0.84526 | 0.81368 | 0.77684 | 0.73895 | 0.70632 | 0.65474 | 0.26105 | -0.26632 | -0.62632 | 0.93053 | 0.92 | 0.91053 | 0.89789 | 0.84421 | 0.77895 | 0.71053 | 0.65368 | 0.59263 | 0.13158 | -0.48 | -0.87053
|  | TYNDRUM | HT |  |  |  |  | 0.66105 | 0.65158 | 0.64105 | 0.63158 | 0.58105 | 0.53474 | 0.48737 | 0.41579 | 0.33684 | -0.031579 | -0.45684 | -0.73158 | 0.86737 | 0.85895 | 0.85053 | 0.84211 | 0.81158 | 0.78526 | 0.75789 | 0.72526 | 0.67579 | 0.33474 | -0.10421 | -0.39684 | 0.92737 | 0.91789 | 0.90842 | 0.89895 | 0.85158 | 0.80737 | 0.76 | 0.70316 | 0.64737 | 0.25474 | -0.21684 | -0.52211
|  | TYNDRUM | HE |  |  |  |  | 0.67053 | 0.66526 | 0.66 | 0.65474 | 0.59474 | 0.54526 | 0.49684 | 0.44632 | 0.39579 | 0.04 | -0.36316 | -0.80632 | 0.87684 | 0.87263 | 0.86737 | 0.86211 | 0.82947 | 0.80211 | 0.77579 | 0.74947 | 0.72316 | 0.42421 | 0.033684 | -0.38947 | 0.92737 | 0.91789 | 0.90842 | 0.89895 | 0.85158 | 0.80737 | 0.76 | 0.70316 | 0.64737 | 0.25474 | -0.21684 | -0.52211
|  | TYNDRUM | CF |  |  |  |  | 0.67474 | 0.67158 | 0.66842 | 0.66632 | 0.64421 | 0.62421 | 0.60421 | 0.58737 | 0.57474 | 0.45789 | 0.20737 | -0.046316 | 0.88105 | 0.87895 | 0.87579 | 0.87263 | 0.86105 | 0.84947 | 0.83789 | 0.82842 | 0.82105 | 0.76842 | 0.53684 | 0.28 | 0.94211 | 0.93895 | 0.93474 | 0.93263 | 0.91158 | 0.89263 | 0.87368 | 0.85789 | 0.84632 | 0.75368 | 0.49684 | 0.21789
| DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | YES | 0 | 2.8 | 2.7421 | 2.6853 | 2.6295 | 2.5642 | 2.5021 | 2.4379 | 2.38 | 2.3263 | 2.0895 | 1.9021 | 1.7463 | 2.5811 | 2.5147 | 2.4484 | 2.3853 | 2.3116 | 2.2432 | 2.1737 | 2.1116 | 2.0547 | 1.7968 | 1.5863 | 1.4095 | 2.7021 | 2.6347 | 2.5695 | 2.5053 | 2.4316 | 2.3611 | 2.2905 | 2.2263 | 2.1684 | 1.9042 | 1.6905 | 1.5116
|  | UIG | EE |  |  |  |  | 2.8389 | 2.7926 | 2.7463 | 2.7011 | 2.6516 | 2.5989 | 2.5484 | 2.5 | 2.4568 | 2.2463 | 2.0758 | 1.9484 | 2.6274 | 2.5758 | 2.5221 | 2.4705 | 2.4189 | 2.3632 | 2.3063 | 2.2547 | 2.2084 | 1.9884 | 1.8053 | 1.6632 | 2.7284 | 2.6958 | 2.6421 | 2.5895 | 2.5347 | 2.4768 | 2.4179 | 2.3632 | 2.3158 | 2.0832 | 1.8905 | 1.7442
|  | UIG | HT |  |  |  |  | 2.8 | 2.7421 | 2.6853 | 2.6295 | 2.5642 | 2.5021 | 2.4379 | 2.38 | 2.3263 | 2.0895 | 1.9021 | 1.7463 | 2.5811 | 2.5147 | 2.4484 | 2.3853 | 2.3116 | 2.2432 | 2.1737 | 2.1116 | 2.0547 | 1.7968 | 1.5863 | 1.4095 | 2.7021 | 2.6347 | 2.5695 | 2.5053 | 2.4316 | 2.3611 | 2.2905 | 2.2263 | 2.1684 | 1.9042 | 1.6905 | 1.5116
|  | UIG | HE |  |  |  |  | 2.8842 | 2.8642 | 2.8347 | 2.8042 | 2.7684 | 2.7358 | 2.7021 | 2.6716 | 2.6432 | 2.5326 | 2.4558 | 2.3958 | 2.6905 | 2.6589 | 2.6253 | 2.5916 | 2.5547 | 2.5189 | 2.4853 | 2.4516 | 2.4221 | 2.3074 | 2.2263 | 2.1621 | 2.7021 | 2.6347 | 2.5695 | 2.5053 | 2.4316 | 2.3611 | 2.2905 | 2.2263 | 2.1684 | 1.9042 | 1.6905 | 1.5116
|  | UIG | CF |  |  |  |  | 2.9032 | 2.8937 | 2.8832 | 2.8726 | 2.8537 | 2.8358 | 2.8179 | 2.7989 | 2.7821 | 2.7032 | 2.6432 | 2.6021 | 2.7242 | 2.7063 | 2.6863 | 2.6684 | 2.6474 | 2.6263 | 2.6074 | 2.5863 | 2.5674 | 2.4768 | 2.4116 | 2.3632 | 2.7779 | 2.7684 | 2.7568 | 2.7474 | 2.7358 | 2.7242 | 2.7116 | 2.7011 | 2.6853 | 2.5937 | 2.5242 | 2.4737
| GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | NO | NO | 0 | 0.82737 | 0.76947 | 0.71263 | 3.6568 | 3.5947 | 3.5337 | 3.4758 | 3.4242 | 3.3747 | 3.1516 | 2.9684 | 2.8084 | 0.81263 | 0.75053 | 0.68947 | 3.6295 | 3.5621 | 3.4979 | 3.4347 | 3.38 | 3.3274 | 3.0821 | 2.8789 | 2.7 | 0.81263 | 0.75158 | 0.69053 | 3.6305 | 3.5632 | 3.4989 | 3.4358 | 3.3811 | 3.3284 | 3.0832 | 2.8811 | 2.7021
|  | ULLAPOOL | EE |  |  |  |  | 0.86526 | 0.82 | 0.77474 | 3.7274 | 3.6821 | 3.6389 | 3.5916 | 3.5463 | 3.5084 | 3.3274 | 3.1863 | 3.0632 | 0.85474 | 0.80632 | 0.75684 | 3.7074 | 3.6589 | 3.6126 | 3.5621 | 3.5126 | 3.4716 | 3.2768 | 3.1189 | 2.9811 | 0.85474 | 0.80632 | 0.75684 | 3.7074 | 3.6589 | 3.6137 | 3.5621 | 3.5137 | 3.4726 | 3.2779 | 3.12 | 2.9832
|  | ULLAPOOL | HT |  |  |  |  | 0.82737 | 0.76947 | 0.71263 | 3.6568 | 3.5947 | 3.5337 | 3.4758 | 3.4242 | 3.3747 | 3.1516 | 2.9684 | 2.8084 | 0.81263 | 0.75053 | 0.68947 | 3.6295 | 3.5621 | 3.4979 | 3.4347 | 3.38 | 3.3274 | 3.0821 | 2.8789 | 2.7 | 0.81263 | 0.75158 | 0.69053 | 3.6305 | 3.5632 | 3.4989 | 3.4358 | 3.3811 | 3.3284 | 3.0832 | 2.8811 | 2.7021
|  | ULLAPOOL | HE |  |  |  |  | 0.91895 | 0.89053 | 0.86 | 3.8284 | 3.7968 | 3.7663 | 3.7379 | 3.7105 | 3.6863 | 3.5916 | 3.5316 | 3.4874 | 0.91263 | 0.88316 | 0.85053 | 3.8168 | 3.7842 | 3.7516 | 3.7221 | 3.6926 | 3.6663 | 3.5663 | 3.5011 | 3.4516 | 0.81263 | 0.75158 | 0.69053 | 3.6305 | 3.5632 | 3.4989 | 3.4358 | 3.3811 | 3.3284 | 3.0832 | 2.8811 | 2.7021
|  | ULLAPOOL | CF |  |  |  |  | 0.94737 | 0.93053 | 0.91158 | 3.8947 | 3.8758 | 3.8568 | 3.8379 | 3.82 | 3.8011 | 3.72 | 3.6653 | 3.6263 | 0.94316 | 0.92421 | 0.90526 | 3.8863 | 3.8663 | 3.8453 | 3.8263 | 3.8063 | 3.7863 | 3.6989 | 3.6389 | 3.5937 | 0.94316 | 0.92421 | 0.90526 | 3.8863 | 3.8663 | 3.8463 | 3.8263 | 3.8063 | 3.7874 | 3.7 | 3.6389 | 3.5947
| SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | 0 | 1.48 | 1.4453 | 1.4126 | 1.38 | 1.3453 | 1.3116 | 1.28 | 1.2484 | 1.2189 | 1.0947 | 0.98316 | 0.88737 | 1.2263 | 1.1842 | 1.1432 | 1.1011 | 1.0579 | 1.0158 | 0.97684 | 0.93684 | 0.9 | 0.75263 | 0.62842 | 0.52316 | 1.1305 | 1.0863 | 1.0432 | 1.0011 | 0.95789 | 0.91579 | 0.87684 | 0.83684 | 0.80105 | 0.65368 | 0.53158 | 0.42632
|  | UNST | EE |  |  |  |  | 1.5 | 1.4737 | 1.4463 | 1.4179 | 1.3895 | 1.3632 | 1.3379 | 1.3137 | 1.2905 | 1.1937 | 1.1189 | 1.0505 | 1.2537 | 1.2211 | 1.1874 | 1.1537 | 1.12 | 1.0863 | 1.0547 | 1.0253 | 0.99579 | 0.86947 | 0.77789 | 0.70211 | 1.1589 | 1.1253 | 1.0895 | 1.0547 | 1.02 | 0.98632 | 0.95474 | 0.92526 | 0.89579 | 0.77053 | 0.68 | 0.60421
|  | UNST | HT |  |  |  |  | 1.48 | 1.4453 | 1.4126 | 1.38 | 1.3453 | 1.3116 | 1.28 | 1.2484 | 1.2189 | 1.0947 | 0.98316 | 0.88737 | 1.2263 | 1.1842 | 1.1432 | 1.1011 | 1.0579 | 1.0158 | 0.97684 | 0.93684 | 0.9 | 0.75263 | 0.62842 | 0.52316 | 1.1305 | 1.0863 | 1.0432 | 1.0011 | 0.95789 | 0.91579 | 0.87684 | 0.83684 | 0.80105 | 0.65368 | 0.53158 | 0.42632
|  | UNST | HE |  |  |  |  | 1.5305 | 1.5126 | 1.4947 | 1.4747 | 1.4547 | 1.4368 | 1.4179 | 1.4011 | 1.3853 | 1.3305 | 1.2958 | 1.2737 | 1.2926 | 1.2705 | 1.2505 | 1.2274 | 1.2042 | 1.1832 | 1.1621 | 1.1432 | 1.1242 | 1.0568 | 1.0095 | 0.97474 | 1.1305 | 1.0863 | 1.0432 | 1.0011 | 0.95789 | 0.91579 | 0.87684 | 0.83684 | 0.80105 | 0.65368 | 0.53158 | 0.42632
|  | UNST | CF |  |  |  |  | 1.5474 | 1.5379 | 1.5274 | 1.5158 | 1.5053 | 1.4947 | 1.4842 | 1.4726 | 1.4621 | 1.4147 | 1.3853 | 1.3653 | 1.3126 | 1.3011 | 1.2884 | 1.2737 | 1.2611 | 1.2484 | 1.2347 | 1.2211 | 1.2084 | 1.1505 | 1.1084 | 1.0768 | 1.2179 | 1.2095 | 1.1958 | 1.1811 | 1.1674 | 1.1537 | 1.14 | 1.1253 | 1.1116 | 1.0505 | 1.0074 | 0.97684
| SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 0 | 9.4168 | 9.3042 | 9.1926 | 9.0589 | 8.7484 | 8.4263 | 8.0326 | 7.6874 | 7.3284 | 4.8737 | 1.9632 | 0.055789 | 8.3768 | 8.2874 | 8.1737 | 8.0379 | 7.7811 | 7.5253 | 7.2232 | 6.9158 | 6.5926 | 4.3516 | 1.6189 | -0.40105 | 8.1916 | 8.0726 | 7.9568 | 7.8168 | 7.4905 | 7.1495 | 6.7347 | 6.3705 | 5.9989 | 3.4274 | 0.35789 | -1.7137
|  | VOE | EE |  |  |  |  | 9.48 | 9.3789 | 9.2779 | 9.1632 | 8.8242 | 8.4263 | 8.0326 | 7.6874 | 7.3284 | 4.8737 | 1.9632 | 0.055789 | 8.4053 | 8.3495 | 8.2716 | 8.1568 | 7.8874 | 7.5611 | 7.2232 | 6.9158 | 6.6032 | 4.3516 | 1.6189 | -0.40105 | 8.2579 | 8.1516 | 8.0463 | 7.9263 | 7.5695 | 7.1495 | 6.7347 | 6.3705 | 5.9989 | 3.4274 | 0.35789 | -1.7137
|  | VOE | HT |  |  |  |  | 9.4168 | 9.3042 | 9.1926 | 9.0589 | 8.7484 | 8.4379 | 8.1263 | 7.7684 | 7.3895 | 5.2895 | 2.9358 | 1.38 | 8.3768 | 8.2874 | 8.1737 | 8.0379 | 7.7811 | 7.5253 | 7.2474 | 6.9316 | 6.5926 | 4.54 | 2.0389 | 0.34 | 8.1916 | 8.0726 | 7.9568 | 7.8168 | 7.4905 | 7.1642 | 6.8358 | 6.4579 | 6.0579 | 3.8168 | 1.2768 | -0.39368
|  | VOE | HE |  |  |  |  | 9.5747 | 9.5189 | 9.4621 | 9.3842 | 9.0411 | 8.74 | 8.4516 | 8.1337 | 7.7011 | 5.8484 | 3.7211 | 1.4316 | 8.4516 | 8.4179 | 8.38 | 8.34 | 8.1084 | 7.8705 | 7.6221 | 7.3337 | 6.9189 | 5.1811 | 3.0926 | 0.83684 | 8.1916 | 8.0726 | 7.9568 | 7.8168 | 7.4905 | 7.1642 | 6.8358 | 6.4579 | 6.0579 | 3.8168 | 1.2768 | -0.39368
|  | VOE | CF |  |  |  |  | 9.6263 | 9.5905 | 9.5547 | 9.5189 | 9.3832 | 9.2568 | 9.1305 | 8.9916 | 8.8 | 7.8737 | 6.5495 | 5.1832 | 8.4821 | 8.4632 | 8.4432 | 8.4232 | 8.3589 | 8.3011 | 8.2021 | 8.08 | 7.8895 | 6.9811 | 5.6579 | 4.2232 | 8.4095 | 8.3726 | 8.3358 | 8.2979 | 8.1558 | 8.0221 | 7.8884 | 7.7411 | 7.5358 | 6.5453 | 5.1211 | 3.6432
| DUDHOPE | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | YES | 0 | 24.6516 | 24.54 | 24.4126 | 24.2421 | 23.9568 | 23.7347 | 23.5105 | 23.2937 | 23.0768 | 22.4947 | 21.6547 | 20.8989 | 22.9453 | 22.8379 | 22.5263 | 22.2063 | 21.8789 | 21.6632 | 21.4516 | 21.2453 | 21.0421 | 20.7074 | 19.86 | 19.1253 | 23.6358 | 23.5021 | 23.3116 | 23.0305 | 22.6874 | 22.4568 | 22.2295 | 22.0074 | 21.7695 | 21.3126 | 20.3558 | 19.4905
|  | WALTON | EE |  |  |  |  | 24.6884 | 24.5653 | 24.4221 | 24.2716 | 23.9621 | 23.7347 | 23.5105 | 23.2937 | 23.0768 | 22.4947 | 21.6547 | 20.8989 | 23.0074 | 22.9074 | 22.7189 | 22.4232 | 22.1137 | 21.9084 | 21.7084 | 21.4874 | 21.2653 | 20.8853 | 20.0305 | 19.2537 | 23.6547 | 23.5021 | 23.3284 | 23.0326 | 22.7284 | 22.4916 | 22.2442 | 22.0074 | 21.7695 | 21.3126 | 20.3558 | 19.4905
|  | WALTON | HT |  |  |  |  | 24.6516 | 24.54 | 24.4126 | 24.2421 | 23.9568 | 23.7516 | 23.5505 | 23.3463 | 23.1432 | 22.6547 | 21.8179 | 21.0853 | 22.9453 | 22.8379 | 22.5263 | 22.2063 | 21.8789 | 21.6632 | 21.4516 | 21.2453 | 21.0421 | 20.7074 | 19.86 | 19.1253 | 23.6358 | 23.5158 | 23.3116 | 23.0305 | 22.6874 | 22.4568 | 22.2295 | 22.0084 | 21.7905 | 21.4589 | 20.5274 | 19.7095
|  | WALTON | HE |  |  |  |  | 24.7579 | 24.6821 | 24.6011 | 24.5063 | 24.4021 | 24.3084 | 24.2179 | 24.0979 | 24.0042 | 23.1905 | 22.7432 | 22.3747 | 23.0579 | 22.9874 | 22.9084 | 22.7747 | 22.5295 | 22.3905 | 22.2611 | 22.14 | 22.0579 | 21.1558 | 20.7168 | 20.3663 | 23.6358 | 23.5158 | 23.3116 | 23.0305 | 22.6874 | 22.4568 | 22.2295 | 22.0084 | 21.7905 | 21.4589 | 20.5274 | 19.7095
|  | WALTON | CF |  |  |  |  | 24.7947 | 24.7484 | 24.7011 | 24.6537 | 24.6021 | 24.5505 | 24.5011 | 24.4505 | 24.4 | 24.1621 | 23.9926 | 23.7979 | 23.0905 | 23.0453 | 22.9989 | 22.9516 | 22.9032 | 22.8537 | 22.8042 | 22.7547 | 22.7042 | 22.2853 | 21.9674 | 21.7411 | 23.7842 | 23.7358 | 23.6863 | 23.6379 | 23.5842 | 23.5316 | 23.48 | 23.4274 | 23.3758 | 23.0642 | 22.7863 | 22.5484
| INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | YES | 0 | 39.3661 | 39.315 | 39.2511 | 39.1836 | 38.9396 | 38.7268 | 38.4436 | 38.2482 | 38.0537 | 37.9778 | 37.8146 | 37.6589 | 38.364 | 38.3149 | 38.2494 | 38.176 | 37.8997 | 37.6596 | 37.3819 | 37.1909 | 36.999 | 36.9196 | 36.813 | 36.6414 | 39.3738 | 39.3326 | 39.2835 | 39.1873 | 38.7071 | 38.289 | 37.8758 | 37.6517 | 37.429 | 37.3476 | 37.2777 | 37.1041
|  | WATERLOO PLACE | EE |  |  |  |  | 39.3875 | 39.3458 | 39.3002 | 39.2535 | 39.1474 | 39.0978 | 38.9058 | 38.7164 | 38.4535 | 37.9778 | 38.0016 | 37.893 | 38.3818 | 38.3411 | 38.2975 | 38.2504 | 38.1323 | 38.0817 | 37.8645 | 37.6502 | 37.3908 | 36.9196 | 37.0208 | 36.9013 | 39.3891 | 39.3554 | 39.3182 | 39.281 | 39.1149 | 39.0434 | 38.665 | 38.2865 | 37.8882 | 37.3476 | 37.4855 | 37.3645
|  | WATERLOO PLACE | HT |  |  |  |  | 39.3661 | 39.315 | 39.2511 | 39.1836 | 38.9396 | 38.7268 | 38.4436 | 38.2482 | 38.0537 | 37.9932 | 37.8146 | 37.6589 | 38.364 | 38.3149 | 38.2494 | 38.176 | 37.8997 | 37.6596 | 37.3819 | 37.1909 | 36.999 | 37.0079 | 36.813 | 36.6414 | 39.3738 | 39.3326 | 39.2835 | 39.1873 | 38.7071 | 38.289 | 37.8758 | 37.6517 | 37.429 | 37.4751 | 37.2777 | 37.1041
|  | WATERLOO PLACE | HE |  |  |  |  | 39.4192 | 39.389 | 39.3562 | 39.3205 | 39.2243 | 39.1861 | 39.0849 | 38.9847 | 38.8875 | 38.6023 | 38.4917 | 38.021 | 38.4071 | 38.3783 | 38.3466 | 38.3119 | 38.2097 | 38.17 | 38.0574 | 37.9453 | 37.8357 | 37.5213 | 37.559 | 36.8973 | 39.3738 | 39.3326 | 39.2835 | 39.1873 | 38.7071 | 38.289 | 37.8758 | 37.6517 | 37.429 | 37.4751 | 37.2777 | 37.1041
|  | WATERLOO PLACE | CF |  |  |  |  | 39.44 | 39.4296 | 39.4118 | 39.3934 | 39.3518 | 39.3299 | 39.316 | 39.2615 | 39.2039 | 38.9807 | 38.8667 | 38.767 | 38.4329 | 38.4155 | 38.3982 | 38.3803 | 38.3416 | 38.3213 | 38.3079 | 38.2474 | 38.1829 | 37.9329 | 37.8074 | 37.6958 | 39.4303 | 39.4179 | 39.405 | 39.3906 | 39.3638 | 39.3475 | 39.3346 | 39.277 | 39.1664 | 38.7434 | 38.5271 | 38.3292
| LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | YES | 0 | 16.9363 | 16.4732 | 16.0163 | 15.5984 | 15.2195 | 14.8974 | 14.5889 | 14.3016 | 14.0216 | 12.6174 | 11.6184 | 10.8553 | 22.2905 | 21.9368 | 21.5863 | 21.2611 | 20.9611 | 20.6979 | 20.4463 | 20.2126 | 19.9853 | 18.6726 | 17.5979 | 16.7653 | 16.3939 | 15.8792 | 15.3739 | 14.9139 | 14.5087 | 14.1655 | 13.8392 | 13.5371 | 13.2445 | 11.7308 | 10.6592 | 9.8255
|  | WEST KIRKTON | EE |  |  |  |  | 17.1395 | 16.7679 | 16.3447 | 15.9753 | 15.5826 | 15.2479 | 14.9721 | 14.7184 | 14.4911 | 13.3226 | 12.4111 | 11.8258 | 22.4526 | 22.1695 | 21.8495 | 21.5653 | 21.2684 | 21.0126 | 20.7947 | 20.5937 | 20.4126 | 19.4789 | 18.5379 | 17.9095 | 16.615 | 16.2045 | 15.7329 | 15.3266 | 14.8992 | 14.5413 | 14.2497 | 13.9813 | 13.7445 | 12.5045 | 11.5371 | 10.9087
|  | WEST KIRKTON | HT |  |  |  |  | 16.9363 | 16.4732 | 16.0163 | 15.5984 | 15.2195 | 14.8974 | 14.5889 | 14.3016 | 14.0216 | 12.6174 | 11.6184 | 10.8553 | 22.2905 | 21.9368 | 21.5863 | 21.2611 | 20.9611 | 20.6979 | 20.4463 | 20.2126 | 19.9853 | 18.6726 | 17.5979 | 16.7653 | 16.3939 | 15.8792 | 15.3739 | 14.9139 | 14.5087 | 14.1655 | 13.8392 | 13.5371 | 13.2445 | 11.7308 | 10.6592 | 9.8255
|  | WEST KIRKTON | HE |  |  |  |  | 17.3721 | 17.0553 | 16.6868 | 16.3795 | 16.0458 | 15.8289 | 15.6511 | 15.4732 | 15.2984 | 14.4774 | 13.9247 | 13.5205 | 22.6432 | 22.4074 | 22.1358 | 21.9011 | 21.6526 | 21.4832 | 21.3389 | 21.1958 | 21.0568 | 20.4505 | 20.0621 | 19.7274 | 16.3939 | 15.8792 | 15.3739 | 14.9139 | 14.5087 | 14.1655 | 13.8392 | 13.5371 | 13.2445 | 11.7308 | 10.6592 | 9.8255
|  | WEST KIRKTON | CF |  |  |  |  | 17.6142 | 17.4974 | 17.3384 | 17.1879 | 17.0542 | 16.8995 | 16.7447 | 16.6226 | 16.4984 | 15.8879 | 15.4805 | 15.2016 | 22.8442 | 22.7358 | 22.6137 | 22.4979 | 22.3947 | 22.2768 | 22.16 | 22.0642 | 21.9663 | 21.5 | 21.2074 | 21.0158 | 17.0192 | 16.9434 | 16.8318 | 16.6655 | 16.5213 | 16.3529 | 16.1845 | 16.0529 | 15.9182 | 15.2592 | 14.8213 | 14.5171
| KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | 0 | 0.092632 | 0.090526 | 0.088421 | 0.086316 | 0.066316 | 0.043158 | 0.017895 | -0.002105 | -0.027368 | -0.19263 | -0.37368 | -0.48316 | 0.092632 | 0.091579 | 0.089474 | 0.087368 | 0.072632 | 0.053684 | 0.032632 | 0.016842 | -0.006316 | -0.15684 | -0.32316 | -0.43368 | 0.091579 | 0.089474 | 0.087368 | 0.085263 | 0.066316 | 0.043158 | 0.016842 | -0.003158 | -0.028421 | -0.20526 | -0.39684 | -0.52
|  | WESTER DRUMMOND | EE |  |  |  |  | 0.093684 | 0.090526 | 0.089474 | 0.086316 | 0.066316 | 0.043158 | 0.017895 | -0.002105 | -0.027368 | -0.19263 | -0.37368 | -0.48316 | 0.094737 | 0.091579 | 0.090526 | 0.087368 | 0.072632 | 0.053684 | 0.032632 | 0.016842 | -0.005263 | -0.15684 | -0.32316 | -0.43368 | 0.093684 | 0.089474 | 0.088421 | 0.085263 | 0.066316 | 0.043158 | 0.016842 | -0.003158 | -0.028421 | -0.20526 | -0.39684 | -0.52
|  | WESTER DRUMMOND | HT |  |  |  |  | 0.092632 | 0.091579 | 0.088421 | 0.087368 | 0.070526 | 0.054737 | 0.037895 | 0.014737 | -0.016842 | -0.14947 | -0.2821 | -0.36632 | 0.092632 | 0.091579 | 0.089474 | 0.088421 | 0.074737 | 0.062105 | 0.047368 | 0.028421 | 0 | -0.12842 | -0.26526 | -0.35684 | 0.091579 | 0.090526 | 0.087368 | 0.086316 | 0.069474 | 0.054737 | 0.036842 | 0.012632 | -0.017895 | -0.16526 | -0.31158 | -0.40737
|  | WESTER DRUMMOND | HE |  |  |  |  | 0.093684 | 0.093684 | 0.092632 | 0.091579 | 0.068421 | 0.048421 | 0.026316 | 0.0052632 | -0.021053 | -0.13474 | -0.26632 | -0.40632 | 0.094737 | 0.094737 | 0.093684 | 0.092632 | 0.073684 | 0.056842 | 0.036842 | 0.018947 | -0.006316 | -0.11053 | -0.23368 | -0.36737 | 0.091579 | 0.090526 | 0.087368 | 0.086316 | 0.069474 | 0.054737 | 0.036842 | 0.012632 | -0.017895 | -0.16526 | -0.31158 | -0.40737
|  | WESTER DRUMMOND | CF |  |  |  |  | 0.095789 | 0.093684 | 0.092632 | 0.092632 | 0.085263 | 0.077895 | 0.068421 | 0.058947 | 0.047368 | -0.005263 | -0.087368 | -0.16842 | 0.096842 | 0.094737 | 0.093684 | 0.093684 | 0.088421 | 0.082105 | 0.072632 | 0.063158 | 0.051579 | 0.0021053 | -0.077895 | -0.15895 | 0.094737 | 0.093684 | 0.092632 | 0.092632 | 0.085263 | 0.077895 | 0.067368 | 0.056842 | 0.04421 | -0.012632 | -0.10211 | -0.19053
| THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | YES | 0.05 | 1.4511 | 1.4374 | 1.4237 | 1.4089 | 1.3932 | 1.3784 | 1.3647 | 1.3511 | 1.3374 | -0.31526 | -0.39842 | -0.47316 | 1.2647 | 1.2511 | 1.2321 | 1.2058 | 1.1805 | 1.1563 | 1.1342 | 1.1111 | 1.0837 | -0.33737 | -0.43211 | -0.51632 | 1.4079 | 1.3826 | 1.3563 | 1.3311 | 1.3058 | 1.2826 | 1.2616 | 1.2384 | 1.2132 | -0.54474 | -0.63316 | -0.71316
|  | WESTRAY | EE |  |  |  |  | 1.4584 | 1.4468 | 1.4353 | 1.4226 | 1.41 | 1.3984 | 1.3868 | 1.3763 | 1.3658 | -0.24158 | -0.30368 | -0.36158 | 1.2721 | 1.2605 | 1.2489 | 1.2363 | 1.2174 | 1.1921 | 1.1742 | 1.1563 | 1.1395 | -0.25526 | -0.32579 | -0.3921 | 1.4163 | 1.4037 | 1.3805 | 1.3616 | 1.3416 | 1.3174 | 1.2995 | 1.2826 | 1.2658 | -0.46684 | -0.53316 | -0.59526
|  | WESTRAY | HT |  |  |  |  | 1.4511 | 1.4374 | 1.4237 | 1.4089 | 1.3932 | 1.3784 | 1.3647 | 1.3511 | 1.3374 | -0.31526 | -0.39842 | -0.47316 | 1.2647 | 1.2511 | 1.2321 | 1.2058 | 1.1805 | 1.1563 | 1.1342 | 1.1111 | 1.0837 | -0.33737 | -0.43211 | -0.51632 | 1.4079 | 1.3826 | 1.3563 | 1.3311 | 1.3058 | 1.2826 | 1.2616 | 1.2384 | 1.2132 | -0.54474 | -0.63316 | -0.71316
|  | WESTRAY | HE |  |  |  |  | 1.47 | 1.4616 | 1.4532 | 1.4437 | 1.4342 | 1.4258 | 1.4174 | 1.4089 | 1.4016 | 0.65 | 0.63842 | 0.61947 | 1.2837 | 1.2753 | 1.2668 | 1.2574 | 1.2479 | 1.2395 | 1.2311 | 1.2226 | 1.2153 | 0.52053 | 0.48263 | 0.43632 | 1.4079 | 1.3826 | 1.3563 | 1.3311 | 1.3058 | 1.2826 | 1.2616 | 1.2384 | 1.2132 | -0.54474 | -0.63316 | -0.71316
|  | WESTRAY | CF |  |  |  |  | 1.4774 | 1.4732 | 1.4689 | 1.4637 | 1.4595 | 1.4553 | 1.45 | 1.4458 | 1.4405 | 1.4216 | 1.4111 | 1.4068 | 1.2911 | 1.2868 | 1.2826 | 1.2774 | 1.2732 | 1.2689 | 1.2637 | 1.2595 | 1.2542 | 1.2342 | 1.2026 | 1.1679 | 1.4353 | 1.4311 | 1.4268 | 1.4216 | 1.4174 | 1.4132 | 1.4079 | 1.3995 | 1.3911 | 1.3574 | 1.3279 | 1.2953
| TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | YES | 2.401 | 2.9537 | 2.8337 | 2.7137 | 2.5927 | 2.2769 | 1.9443 | 1.5601 | 1.1327 | 0.70847 | -1.2957 | -4.1842 | -6.0905 | 3.3548 | 3.1716 | 3.0053 | 2.8401 | 2.5158 | 2.2011 | 1.8874 | 1.5411 | 1.1695 | -0.53153 | -3.2694 | -5.2568 | 3.4769 | 3.3569 | 3.2369 | 3.0843 | 2.7316 | 2.3411 | 1.9506 | 1.5179 | 1.0885 | -0.94732 | -4.0684 | -6.1873
|  | WHITEHOUSE | EE |  |  |  |  | 3.019 | 2.9148 | 2.8074 | 2.6969 | 2.3601 | 1.979 | 1.5937 | 1.2369 | 0.83584 | -1.2957 | -4.1842 | -6.0905 | 3.4569 | 3.3032 | 3.1601 | 3.0169 | 2.6874 | 2.3211 | 1.9569 | 1.6337 | 1.3085 | -0.53153 | -3.2694 | -5.2568 | 3.5422 | 3.4369 | 3.3295 | 3.2179 | 2.8779 | 2.4927 | 2.0516 | 1.6495 | 1.2453 | -0.94732 | -4.0684 | -6.1873
|  | WHITEHOUSE | HT |  |  |  |  | 2.9537 | 2.8337 | 2.7137 | 2.5927 | 2.2769 | 1.9443 | 1.5601 | 1.1327 | 0.70847 | -1.0684 | -3.4463 | -5.0052 | 3.3548 | 3.1716 | 3.0053 | 2.8401 | 2.5158 | 2.2011 | 1.8874 | 1.5411 | 1.1695 | -0.49047 | -2.9799 | -4.6705 | 3.4769 | 3.3569 | 3.2369 | 3.0843 | 2.7316 | 2.3411 | 1.9506 | 1.5179 | 1.0885 | -0.73679 | -3.3684 | -5.1421
|  | WHITEHOUSE | HE |  |  |  |  | 3.1074 | 3.0464 | 2.9801 | 2.9106 | 2.5779 | 2.2958 | 2.0148 | 1.739 | 1.4695 | -0.16205 | -2.2589 | -4.4905 | 3.5822 | 3.4969 | 3.4085 | 3.3179 | 3.0064 | 2.7401 | 2.4779 | 2.2222 | 1.9716 | 0.47795 | -1.5852 | -3.7852 | 3.4769 | 3.3569 | 3.2369 | 3.0843 | 2.7316 | 2.3411 | 1.9506 | 1.5179 | 1.0885 | -0.73679 | -3.3684 | -5.1421
|  | WHITEHOUSE | CF |  |  |  |  | 3.1632 | 3.1306 | 3.0958 | 3.0611 | 2.9316 | 2.8137 | 2.6958 | 2.5927 | 2.5085 | 1.9685 | 0.65795 | -0.6789 | 3.6485 | 3.6085 | 3.5695 | 3.5295 | 3.4022 | 3.2832 | 3.1653 | 3.0579 | 2.9685 | 2.2948 | 1.1064 | -0.27995 | 3.6864 | 3.6537 | 3.6179 | 3.5843 | 3.4537 | 3.3337 | 3.2158 | 3.1106 | 3.0264 | 2.3864 | 0.98532 | -0.46521
| PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | NO | 0 | 9.3984 | 8.7332 | 8.0016 | 7.2037 | 8.8426 | 8.4311 | 7.9984 | 7.5468 | 7.0774 | 4.6353 | 2.2984 | 0.08579 | 9.3042 | 8.5684 | 7.7547 | 6.8642 | 8.6937 | 8.2432 | 7.7674 | 7.2684 | 6.7474 | 4.0368 | 1.4484 | -1.0537 | 9.5887 | 8.8582 | 8.0487 | 7.1624 | 8.975 | 8.5224 | 8.0434 | 7.5424 | 7.0213 | 4.2834 | 1.6455 | -0.96395
|  | WHITESTRIPES | EE |  |  |  |  | 9.6132 | 9.0205 | 8.3489 | 7.61 | 16.8437 | 15.9689 | 15.1037 | 14.2595 | 13.4226 | 9.3511 | 5.5311 | 2.0121 | 9.5032 | 8.88 | 8.1316 | 7.3053 | 16.4589 | 15.5074 | 14.5653 | 13.64 | 12.7263 | 8.2758 | 4.0821 | 0.097895 | 9.8203 | 9.1666 | 8.4224 | 7.6003 | 16.7424 | 15.7739 | 14.8076 | 13.8613 | 12.9234 | 8.3508 | 4.0571 | 0.045526
|  | WHITESTRIPES | HT |  |  |  |  | 9.3984 | 8.7332 | 8.0016 | 7.2037 | 16.3826 | 15.4668 | 14.5616 | 13.6563 | 12.7542 | 8.6711 | 4.8279 | 1.1216 | 9.3042 | 8.5684 | 7.7547 | 6.8642 | 15.9558 | 14.9505 | 13.9579 | 12.9674 | 11.9821 | 7.4863 | 3.1621 | -1.0537 | 9.5887 | 8.8582 | 8.0487 | 7.1624 | 16.2466 | 15.2287 | 14.2192 | 13.2076 | 12.2003 | 7.6192 | 3.2592 | -0.96395
|  | WHITESTRIPES | HE |  |  |  |  | 9.8384 | 9.4868 | 8.9395 | 8.3142 | 17.6479 | 16.8984 | 16.1553 | 15.4216 | 14.6984 | 11.29 | 8.0658 | 4.9837 | 9.72 | 9.3758 | 8.76 | 8.0526 | 17.3116 | 16.4853 | 15.6653 | 14.8547 | 14.0558 | 10.2674 | 6.6274 | 3.1495 | 9.5887 | 8.8582 | 8.0487 | 7.1624 | 16.2466 | 15.2287 | 14.2192 | 13.2076 | 12.2003 | 7.6192 | 3.2592 | -0.96395
|  | WHITESTRIPES | CF |  |  |  |  | 9.8553 | 9.7342 | 9.5742 | 9.2321 | 8.8426 | 8.4311 | 7.9984 | 7.5468 | 7.0774 | 4.6353 | 2.2984 | 0.08579 | 9.7368 | 9.6158 | 9.4726 | 9.1168 | 8.6937 | 8.2432 | 7.7674 | 7.2684 | 6.7474 | 4.0368 | 1.4484 | -1.0232 | 10.0645 | 9.9434 | 9.7771 | 9.4013 | 8.975 | 8.5224 | 8.0434 | 7.5424 | 7.0213 | 4.2834 | 1.6455 | -0.865
| CARRADALE 1 | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 0 | 5.8758 | 5.8274 | 5.7779 | 5.7274 | 5.6726 | 5.62 | 5.5705 | 5.5232 | 5.4768 | 5.2747 | 5.0747 | 4.9063 | 6.3126 | 6.2432 | 6.1737 | 6.1042 | 6.0263 | 5.9474 | 5.8716 | 5.7979 | 5.7274 | 5.46 | 5.2368 | 5.0358 | 6.2137 | 6.1642 | 6.1147 | 6.0505 | 5.9832 | 5.92 | 5.8495 | 5.7737 | 5.7032 | 5.4263 | 5.2 | 4.9947
|  | WHITING BAY | EE |  |  |  |  | 5.9042 | 5.8632 | 5.8211 | 5.7779 | 5.7337 | 5.6916 | 5.6505 | 5.6126 | 5.5758 | 5.4316 | 5.3253 | 5.2074 | 6.3579 | 6.3021 | 6.2453 | 6.1874 | 6.1295 | 6.0758 | 6.0221 | 5.9684 | 5.9147 | 5.6853 | 5.5253 | 5.3958 | 6.2421 | 6.2011 | 6.1589 | 6.1158 | 6.0705 | 6.0189 | 5.9695 | 5.9221 | 5.8789 | 5.6505 | 5.4832 | 5.3463
|  | WHITING BAY | HT |  |  |  |  | 5.8758 | 5.8274 | 5.7779 | 5.7274 | 5.6726 | 5.62 | 5.5705 | 5.5232 | 5.4768 | 5.2747 | 5.0747 | 4.9063 | 6.3126 | 6.2432 | 6.1737 | 6.1042 | 6.0263 | 5.9474 | 5.8716 | 5.7979 | 5.7274 | 5.46 | 5.2368 | 5.0358 | 6.2137 | 6.1642 | 6.1147 | 6.0505 | 5.9832 | 5.92 | 5.8495 | 5.7737 | 5.7032 | 5.4263 | 5.2 | 4.9947
|  | WHITING BAY | HE |  |  |  |  | 5.9453 | 5.9189 | 5.8905 | 5.86 | 5.8274 | 5.7968 | 5.7684 | 5.7421 | 5.7158 | 5.6326 | 5.5895 | 5.5663 | 6.4221 | 6.3863 | 6.3495 | 6.3105 | 6.2705 | 6.2337 | 6.1968 | 6.1642 | 6.1337 | 6.0221 | 5.9526 | 5.8926 | 6.2137 | 6.1642 | 6.1147 | 6.0505 | 5.9832 | 5.92 | 5.8495 | 5.7737 | 5.7032 | 5.4263 | 5.2 | 4.9947
|  | WHITING BAY | CF |  |  |  |  | 5.9716 | 5.9589 | 5.9442 | 5.9295 | 5.9158 | 5.9011 | 5.8863 | 5.8716 | 5.8579 | 5.7958 | 5.7653 | 5.7495 | 6.4589 | 6.44 | 6.4189 | 6.3979 | 6.3779 | 6.3579 | 6.3368 | 6.3158 | 6.2958 | 6.2063 | 6.1516 | 6.1105 | 6.3095 | 6.2968 | 6.2821 | 6.2674 | 6.2537 | 6.2389 | 6.2242 | 6.2095 | 6.1947 | 6.1326 | 6.0947 | 6.0632
| MYBSTER 1 | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | YES | 0.15 | 10.1121 | 9.8742 | 9.57 | 9.2658 | 8.4563 | 7.6605 | 6.8479 | 3.6553 | 2.8489 | -1.7963 | -7.1574 | -11.1058 | 11.1921 | 10.87 | 10.5542 | 10.2395 | 9.5111 | 8.7984 | 8.0689 | 5.6353 | 4.9226 | 0.39842 | -5.4858 | -9.8521 | 10.8879 | 10.5637 | 10.2405 | 9.9184 | 9.0774 | 8.2521 | 7.4079 | 4.1995 | 3.3679 | -1.6742 | -7.7774 | -12.2795
|  | WICK | EE |  |  |  |  | 10.1932 | 10.0163 | 9.8121 | 9.5374 | 9.1689 | 8.4595 | 7.5753 | 7.2932 | 6.4058 | 1.6205 | -3.7721 | -8.5963 | 11.3879 | 11.1163 | 10.8395 | 10.5647 | 10.1784 | 9.5826 | 8.8668 | 8.5605 | 7.8016 | 3.4216 | -1.9584 | -7.1047 | 11.0647 | 10.7942 | 10.5068 | 10.2174 | 9.8184 | 9.0953 | 8.1995 | 7.89 | 6.9784 | 1.8847 | -4.0458 | -9.49
|  | WICK | HT |  |  |  |  | 10.1121 | 9.8742 | 9.57 | 9.2658 | 8.4563 | 7.6605 | 6.8479 | 3.6553 | 2.8489 | -1.7963 | -7.1574 | -11.1058 | 11.1921 | 10.87 | 10.5542 | 10.2395 | 9.5111 | 8.7984 | 8.0689 | 5.6353 | 4.9226 | 0.39842 | -5.4858 | -9.8521 | 10.8879 | 10.5637 | 10.2405 | 9.9184 | 9.0774 | 8.2521 | 7.4079 | 4.1995 | 3.3679 | -1.6742 | -7.7774 | -12.2795
|  | WICK | HE |  |  |  |  | 10.3205 | 10.2205 | 10.1132 | 9.9974 | 9.2005 | 8.5447 | 7.9047 | 5.7889 | 4.77 | 0.86158 | -3.39 | -8.8721 | 11.6553 | 11.5037 | 11.3374 | 11.0711 | 10.3468 | 9.8079 | 9.2879 | 7.67 | 6.7216 | 2.9868 | -1.3995 | -6.8321 | 10.8879 | 10.5637 | 10.2405 | 9.9184 | 9.0774 | 8.2521 | 7.4079 | 4.1995 | 3.3679 | -1.6742 | -7.7774 | -12.2795
|  | WICK | CF |  |  |  |  | 10.4005 | 10.3447 | 10.2858 | 10.2289 | 9.9679 | 9.73 | 9.4974 | 7.7637 | 7.2858 | 5.3247 | 2.6658 | -0.7121 | 11.7784 | 11.6953 | 11.61 | 11.51 | 11.2511 | 11.0111 | 10.7742 | 9.3237 | 8.8595 | 6.8742 | 4.0984 | 0.53421 | 11.3879 | 11.3195 | 11.2521 | 11.1679 | 10.8732 | 10.5974 | 10.3121 | 8.47 | 7.9405 | 5.8026 | 2.8216 | -0.98579
| WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 0.06 | 16.9642 | 16.6516 | 16.2558 | 15.8632 | 15.4389 | 15.0263 | 14.6232 | 14.2263 | 13.8653 | 11.7789 | 11.1095 | 9.9095 | 15.8368 | 15.5158 | 15.0937 | 14.6758 | 14.2316 | 13.8 | 13.3779 | 12.9663 | 13.0853 | 11.2937 | 10.2884 | 8.9663 | 16.78 | 16.4768 | 16.0537 | 15.6347 | 15.1853 | 14.7474 | 14.3221 | 13.9032 | 14.0389 | 13.0326 | 11.0537 | 9.7147
|  | WOODHILL | EE |  |  |  |  | 17.0947 | 16.92 | 16.6832 | 16.3568 | 16.0137 | 15.6747 | 15.3442 | 15.0337 | 14.7495 | 13.9526 | 12.5537 | 11.7105 | 16.1221 | 15.7895 | 15.5537 | 15.2063 | 14.8516 | 14.5011 | 14.1589 | 13.8358 | 13.5337 | 13.12 | 11.8516 | 10.9242 | 16.9242 | 16.7358 | 16.5158 | 16.1663 | 15.8042 | 15.4463 | 15.0979 | 14.7695 | 14.4663 | 14.06 | 12.6316 | 11.6895
|  | WOODHILL | HT |  |  |  |  | 16.9642 | 16.6516 | 16.2558 | 15.8632 | 15.4389 | 15.0263 | 14.6232 | 14.2263 | 14.1474 | 12.96 | 11.1095 | 9.9095 | 15.8368 | 15.5158 | 15.0937 | 14.6758 | 14.2316 | 13.8 | 13.3779 | 12.9663 | 13.0853 | 12.0832 | 10.2884 | 8.9663 | 16.78 | 16.4768 | 16.0537 | 15.6347 | 15.1853 | 14.7474 | 14.3221 | 13.9032 | 14.0389 | 13.0326 | 11.0537 | 9.7147
|  | WOODHILL | HE |  |  |  |  | 17.2295 | 17.0947 | 16.9484 | 16.7937 | 16.6095 | 16.28 | 16.0779 | 15.8484 | 13.8653 | 11.7789 | 11.2295 | 11.0284 | 16.4547 | 16.2305 | 15.9884 | 15.7432 | 15.4737 | 15.1179 | 14.8737 | 14.6389 | 13.1642 | 11.2937 | 10.5505 | 10.0537 | 16.78 | 16.4768 | 16.0537 | 15.6347 | 15.1853 | 14.7474 | 14.3221 | 13.9032 | 14.0389 | 13.0326 | 11.0537 | 9.7147
|  | WOODHILL | CF |  |  |  |  | 17.3211 | 17.2379 | 17.1505 | 17.0632 | 16.9663 | 16.8684 | 16.7716 | 16.6495 | 16.4947 | 15.7832 | 15.2674 | 14.8811 | 16.5926 | 16.4674 | 16.3168 | 16.16 | 15.9958 | 15.8295 | 15.6611 | 15.4979 | 15.3347 | 14.5832 | 14.04 | 13.6232 | 17.1768 | 17.0874 | 16.9937 | 16.8989 | 16.7958 | 16.6916 | 16.5884 | 16.4495 | 16.2842 | 15.5242 | 14.9684 | 14.5411

## Local Authority Reference
#VALUE! | Local Authority | Grid Supply Point | Primary Substation
| Aberdeen City | CLAYHILLS | BALNAGASK
| Aberdeen City | PERSLEY | BRIDGE OF DON
| Aberdeen City | CLAYHILLS | CLAYHILLS
| Aberdeen City | CLAYHILLS | COMMERCE STREET
| Aberdeen City | CRAIGIEBUCKLER | CRAIGIEBUCKLER
| Aberdeen City | REDMOSS | CRAIGINCHES
| Aberdeen City | CRAIGIEBUCKLER | CRAIGTON
| Aberdeen City | CRAIGIEBUCKLER | CULTER
| Aberdeen City | WILLOWDALE | DENBURN
| Aberdeen City | DYCE | DYCE NORTH
| Aberdeen City | WILLOWDALE | GREYFRIARS
| Aberdeen City | DYCE | HARVEST AVENUE
| Aberdeen City | PERSLEY | HAUDAGAIN
| Aberdeen City | WILLOWDALE | HAYTON
| Aberdeen City | REDMOSS | KINCORTH
| Aberdeen City | PERSLEY | NORTHFIELD
| Aberdeen City | KINTORE | PARK
| Aberdeen City | WOODHILL | QUEENS LANE NORTH
| Aberdeen City | REDMOSS | REDMOSS
| Aberdeen City | CRAIGIEBUCKLER | RUTHRIESTON
| Aberdeen City | KINTORE | SKENE
| Aberdeen City | WOODHILL | SPRINGHILL
| Aberdeen City | PERSLEY | ST MACHAR
| Aberdeen City | WILLOWDALE | ST NICHOLAS
| Aberdeen City | PERSLEY | STONEYWOOD T1&T2
| Aberdeen City | PERSLEY | STONEYWOOD T3
| Aberdeen City | KINTORE | TORRYBURN
| Aberdeen City | PERSLEY | WHITESTRIPES
| Aberdeen City | WOODHILL | WOODHILL
| Aberdeenshire | TARLAND | ABOYNE
| Aberdeenshire | BOAT OF GARTEN | AVIEMORE
| Aberdeenshire | TARLAND | BALLATER
| Aberdeenshire | BOAT OF GARTEN | BALLINDALLOCH
| Aberdeenshire | DYCE | BALMEDIE
| Aberdeenshire | KINTORE | BANCHORY
| Aberdeenshire | PETERHEAD SHELL | BODDAM
| Aberdeenshire | TUMMEL BRIDGE | BONSKEID
| Aberdeenshire | PERSLEY | BRIDGE OF DON
| Aberdeenshire | CRAIGIEBUCKLER | CRAIGTON
| Aberdeenshire | KEITH | CULLEN
| Aberdeenshire | CRAIGIEBUCKLER | CULTER
| Aberdeenshire | COUPAR ANGUS | DALRULZION
| Aberdeenshire | KEITH | DUFFTOWN
| Aberdeenshire | DYCE | DYCE NORTH
| Aberdeenshire | FIDDES | EDZELL
| Aberdeenshire | DYCE | ELLON
| Aberdeenshire | FRASERBURGH | FRASERBURGH
| Aberdeenshire | KINTORE | FYVIE
| Aberdeenshire | STRICHEN | HATTON
| Aberdeenshire | KEITH | HUNTLY
| Aberdeenshire | BRIDGE OF DUN | INCHBARE
| Aberdeenshire | KEITH | INSCH
| Aberdeenshire | FIDDES | INVERBERVIE
| Aberdeenshire | KINTORE | INVERURIE
| Aberdeenshire | KEITH | KEITH
| Aberdeenshire | KINTORE | KEMNAY
| Aberdeenshire | REDMOSS | KINCORTH
| Aberdeenshire | DYCE | KINGSEAT
| Aberdeenshire | FIDDES | LAURENCEKIRK
| Aberdeenshire | KEITH | LIMEHILLOCKS
| Aberdeenshire | BRIDGE OF DUN | LOGIE PERT
| Aberdeenshire | MACDUFF | MACDUFF
| Aberdeenshire | KEITH | MARNOCH
| Aberdeenshire | LUNANHEAD | MARYTON
| Aberdeenshire | STRICHEN | MAUD
| Aberdeenshire | KINTORE | METHLICK
| Aberdeenshire | KINTORE | MIDMAR
| Aberdeenshire | STRICHEN | MINTLAW
| Aberdeenshire | BRIDGE OF DUN | MONTROSE NORTH
| Aberdeenshire | TARLAND | MOSSAT
| Aberdeenshire | STRICHEN | NEW PITSLIGO
| Aberdeenshire | REDMOSS | NEWTONHILL
| Aberdeenshire | KINTORE | OLDMELDRUM
| Aberdeenshire | KINTORE | PARK
| Aberdeenshire | PETERHEAD GRANGE | PETERHEAD GRANGE
| Aberdeenshire | PETERHEAD GRANGE | PETERHEAD NORTH STREET
| Aberdeenshire | MACDUFF | PORTSOY
| Aberdeenshire | REDMOSS | REDMOSS
| Aberdeenshire | CRAIGIEBUCKLER | RUTHRIESTON
| Aberdeenshire | KINTORE | SKENE
| Aberdeenshire | WOODHILL | SPRINGHILL
| Aberdeenshire | BRIDGE OF DUN | ST CYRUS
| Aberdeenshire | ST FERGUS GAS | ST FERGUS GAS TERM
| Aberdeenshire | FIDDES | STONEHAVEN
| Aberdeenshire | STRICHEN | STONEYHILL
| Aberdeenshire | TARLAND | STRATHDON
| Aberdeenshire | STRICHEN | STRICHEN
| Aberdeenshire | KINTORE | TORRYBURN
| Aberdeenshire | MACDUFF | TURRIFF
| Aberdeenshire | TARLAND | WHITEHOUSE
| Aberdeenshire | PERSLEY | WHITESTRIPES
| Angus | COUPAR ANGUS | ALYTH
| Angus | MILTON OF CRAIGIE | ASHLUDIE
| Angus | ABERNETHY | BALBEGGIE
| Angus | MILTON OF CRAIGIE | BALDOVIE
| Angus | TARLAND | BALLATER
| Angus | KINTORE | BANCHORY
| Angus | BRIDGE OF DUN | BRECHIN
| Angus | BRIDGE OF DUN | BRIDGE OF DUN
| Angus | MILTON OF CRAIGIE | BROUGHTY FERRY
| Angus | ARBROATH | CARNOUSTIE
| Angus | ARBROATH | CHARLES AVENUE
| Angus | COUPAR ANGUS | COUPAR ANGUS
| Angus | COUPAR ANGUS | DALRULZION
| Angus | FIDDES | EDZELL
| Angus | MILTON OF CRAIGIE | EDZELL STREET
| Angus | ARBROATH | ELLIOT DEPOT
| Angus | LUNANHEAD | FRIOCKHEIM
| Angus | CHARLESTON | GOURDIE
| Angus | ARBROATH | HUME STREET
| Angus | BRIDGE OF DUN | INCHBARE
| Angus | LUNANHEAD | INVERARITY
| Angus | FIDDES | LAURENCEKIRK
| Angus | COUPAR ANGUS | LEOCH
| Angus | LUNANHEAD | LOCHSIDE
| Angus | BRIDGE OF DUN | LOGIE PERT
| Angus | MILTON OF CRAIGIE | LONGHAUGH
| Angus | LUNANHEAD | LUNANHEAD
| Angus | LYNDHURST | MACALPINE ROAD
| Angus | LUNANHEAD | MARYTON
| Angus | BRIDGE OF DUN | MILL ROAD MONTROSE
| Angus | BRIDGE OF DUN | MONTROSE NORTH
| Angus | ARBROATH | REDFORD
| Angus | BRIDGE OF DUN | ST CYRUS
| Angus | LYNDHURST | WEST KIRKTON
| Argyll and Bute | PORT ANN | AIRIGH-NA-BRODAIG
| Argyll and Bute | CARRADALE | BALLURE
| Argyll and Bute | TAYNUILT | BARCALDINE
| Argyll and Bute | RANNOCH | BLACKMOUNT
| Argyll and Bute | PORT ANN | BOWMORE
| Argyll and Bute | DUNOON | BRUCHAG
| Argyll and Bute | CLACHAN | BUTTERBRIDGE
| Argyll and Bute | CARRADALE | CAMPBELTOWN
| Argyll and Bute | KILLIN | CASHLIE
| Argyll and Bute | KILLIN | CHAORACH
| Argyll and Bute | CARRADALE | CLAONAIG
| Argyll and Bute | DUNOON | COLINTRAIVE
| Argyll and Bute | TAYNUILT | CONNEL
| Argyll and Bute | PORT ANN | CRINAN
| Argyll and Bute | PORT ANN | CROMALT
| Argyll and Bute | TAYNUILT | DALMALLY
| Argyll and Bute | TAYNUILT | DERVAIG
| Argyll and Bute | CARRADALE | DIPPEN
| Argyll and Bute | CLACHAN | DOUGLAS PIER
| Argyll and Bute | STRATHLEVEN | DRYMEN
| Argyll and Bute | DUNOON | DUNOON
| Argyll and Bute | TAYNUILT | EREDINE
| Argyll and Bute | DUNOON | GLENDARUEL
| Argyll and Bute | RANNOCH | GLENETIVE
| Argyll and Bute | DUNOON | INNELLAN
| Argyll and Bute | CLACHAN | INVERARAY
| Argyll and Bute | PORT ANN | INVERNEIL
| Argyll and Bute | DUNOON | KAMES
| Argyll and Bute | TAYNUILT | KENMORE
| Argyll and Bute | TAYNUILT | KERRERA
| Argyll and Bute | TAYNUILT | KILCHRENAN
| Argyll and Bute | TAYNUILT | KILMELFORD
| Argyll and Bute | TAYNUILT | KILNINVER
| Argyll and Bute | TAYNUILT | KINLOCH
| Argyll and Bute | TUMMEL BRIDGE | KINLOCH RANNOCH
| Argyll and Bute | TAYNUILT | LOCHDONHEAD
| Argyll and Bute | PORT ANN | LOCHGILPHEAD
| Argyll and Bute | CLACHAN | LOCHGOILHEAD
| Argyll and Bute | PORT ANN | LUSSAGIVEN
| Argyll and Bute | DUNOON | NEWTON
| Argyll and Bute | TAYNUILT | OBAN
| Argyll and Bute | DUNOON | OTTER FERRY
| Argyll and Bute | PORT ANN | PORT ASKAIG
| Argyll and Bute | PORT ANN | PORT ELLEN
| Argyll and Bute | DUNOON | ROTHESAY
| Argyll and Bute | FORT WILLIAM | SALEN 2
| Argyll and Bute | DUNOON | SANDBANK
| Argyll and Bute | TAYNUILT | SCAMMADALE
| Argyll and Bute | PORT ANN | STONEFIELD
| Argyll and Bute | CLACHAN | STRACHUR
| Argyll and Bute | PORT ANN | TARBERT JURA
| Argyll and Bute | PORT ANN | TARBERT LOCH FYNE
| Argyll and Bute | TAYNUILT | TAYNUILT
| Argyll and Bute | TAYNUILT | TIRORAN BRIDGE
| Argyll and Bute | RANNOCH | TYNDRUM
| Argyll and Bute | CARRADALE | WESTPARK FERGUS
| Clackmannanshire | ABERNETHY | GLENDEVON
| Clackmannanshire | BRACO | GLENEAGLES
| Clackmannanshire | ABERNETHY | MILNATHORT
| Dundee City | MILTON OF CRAIGIE | ASHLUDIE
| Dundee City | MILTON OF CRAIGIE | BALDOVIE
| Dundee City | MILTON OF CRAIGIE | BROUGHTY FERRY
| Dundee City | CHARLESTON | CHARLESTON
| Dundee City | DUDHOPE | CONSTABLE STREET
| Dundee City | MILTON OF CRAIGIE | EDZELL STREET
| Dundee City | CHARLESTON | GOURDIE
| Dundee City | COUPAR ANGUS | LEOCH
| Dundee City | LYNDHURST | LOCHEE
| Dundee City | MILTON OF CRAIGIE | LONGHAUGH
| Dundee City | LYNDHURST | LYNDHURST
| Dundee City | LYNDHURST | MACALPINE ROAD
| Dundee City | CHARLESTON | MENZIESHILL
| Dundee City | MILTON OF CRAIGIE | MILTON OF CRAIGIE
| Dundee City | CHARLESTON | NINEWELLS
| Dundee City | MILTON OF CRAIGIE | OLD CRAIGIE ROAD
| Dundee City | GLENAGNES | OVERGATE
| Dundee City | DUDHOPE | ROSEBANK STREET
| Dundee City | GLENAGNES | WALTON
| Dundee City | LYNDHURST | WEST KIRKTON
| East Dunbartonshire | STRATHLEVEN | KEPCULLOCH
| East Dunbartonshire | STRATHLEVEN | KILLEARN
| East Dunbartonshire | BRACO | KIPPEN
| Eilean Siar | ARDMORE | AIRD
| Eilean Siar | STORNOWAY | ARNISH
| Eilean Siar | STORNOWAY | BARVAS
| Eilean Siar | STORNOWAY | BATTERY POINT
| Eilean Siar | STORNOWAY | CALLANISH
| Eilean Siar | ARDMORE | CLACHAN
| Eilean Siar | STORNOWAY | COLL
| Eilean Siar | ARDMORE | DRIMORE
| Eilean Siar | STORNOWAY | GISLA
| Eilean Siar | ARDMORE | HARRIS GRID
| Eilean Siar | STORNOWAY | LAXAY
| Eilean Siar | ARDMORE | LOCH CARNAN
| Eilean Siar | STORNOWAY | MAARUIG
| Eilean Siar | ARDMORE | POLLACHAR
| Eilean Siar | ARDMORE / HARRIS GRID | STOCKINISH
| Eilean Siar | ARDMORE / HARRIS GRID | TARBERT
| Fife | ABERNETHY | ABERNETHY
| Fife | ABERNETHY | BRIDGE OF EARN
| Fife | ABERNETHY | GLENDEVON
| Fife | ABERNETHY | MILNATHORT
| Highland | FORT AUGUSTUS | ABERCHALDER
| Highland | KEITH | ABERLOUR
| Highland | GRUDIE BRIDGE | ACHILTIBUIE
| Highland | BROADFORD | ACHINTEE
| Highland | BEAULY | AIGAS
| Highland | FORT WILLIAM | ANNAT
| Highland | NAIRN | ARDERSIER
| Highland | FORT AUGUSTUS | ARDOCHY
| Highland | FORT WILLIAM | ARISAIG
| Highland | GRUDIE BRIDGE | AULTBEA
| Highland | BOAT OF GARTEN | AVIEMORE
| Highland | ALNESS | BALALDIE
| Highland | BOAT OF GARTEN | BALLINDALLOCH
| Highland | TAYNUILT | BARCALDINE
| Highland | DOUNREAY | BETTYHILL
| Highland | GRUDIE BRIDGE | BIDEN CLAN RAONAILD
| Highland | RANNOCH | BLACKMOUNT
| Highland | BEAULY | BLACKSTAND
| Highland | BOAT OF GARTEN | BOAT OF GARTEN
| Highland | TUMMEL BRIDGE | BONSKEID
| Highland | RANNOCH | BRIDGE OF GAUR
| Highland | BROADFORD | BROADFORD
| Highland | FORT AUGUSTUS | BUNOICH
| Highland | TUMMEL BRIDGE | CALVINE
| Highland | DOUNREAY | COLDBACKIE
| Highland | ST FILLANS | COMRIE
| Highland | BEAULY | CONON BRIDGE
| Highland | BEAULY | CONON FALLS
| Highland | ALNESS | CONTULLICH
| Highland | FORT WILLIAM | CORRAN
| Highland | ALNESS | CROSSHILLS
| Highland | INVERNESS | CULLODEN
| Highland | NAIRN | DALCROSS
| Highland | INVERNESS | DALNEIGH
| Highland | BOAT OF GARTEN | DALWHINNIE
| Highland | BEAULY | DINGWALL
| Highland | BRORA | DORNOCH
| Highland | DOUNREAY | DOUNREAY
| Highland | CEANNACROC | DRUMNADROCHIT
| Highland | GRUDIE BRIDGE | DRUMRUNIE
| Highland | DUNVEGAN | DRYNOCH
| Highland | DUNOON | DUNOON
| Highland | DUNVEGAN | DUNVEGAN GRID
| Highland | INVERNESS | ERROGIE
| Highland | FORT WILLIAM | FISHNISH
| Highland | NAIRN | FORRES
| Highland | DOUNREAY | FORSS
| Highland | INVERNESS | FOYERS
| Highland | GRUDIE BRIDGE | GARBAT FOREST
| Highland | ALNESS | GLASTULLICH
| Highland | SHIN | GLEDFIELD
| Highland | FORT AUGUSTUS | GLEN LAOGH
| Highland | KINLOCHLEVEN | GLENCOE
| Highland | FORT AUGUSTUS | GLENDOE PRIMARY
| Highland | RANNOCH | GLENETIVE
| Highland | FORT WILLIAM | GLENUIG
| Highland | BRORA | GOLSPIE
| Highland | BOAT OF GARTEN | GRANTOWN
| Highland | GRUDIE BRIDGE | GRUDIE BRIDGE
| Highland | THURSO | HALKIRK
| Highland | THURSO | HASTIGROW
| Highland | BRORA | HELMSDALE
| Highland | INVERNESS | HILTON
| Highland | INVERNESS | INVERARNIE
| Highland | GRUDIE BRIDGE | INVERBROOM
| Highland | FORT AUGUSTUS | INVERGARRY
| Highland | ALNESS | INVERGORDON
| Highland | FORT WILLIAM | INVERLOCHY
| Highland | INVERNESS | INVERNESS
| Highland | BROADFORD | KALNAKIL
| Highland | GRUDIE BRIDGE | KERRY FALLS
| Highland | BEAULY | KILTARLITY
| Highland | FORT WILLIAM | KINGAIRLOCH
| Highland | BOAT OF GARTEN | KINGUSSIE
| Highland | TUMMEL BRIDGE | KINLOCH RANNOCH
| Highland | GRUDIE BRIDGE | KINLOCHEWE
| Highland | KINLOCHLEVEN | KINLOCHLEVEN
| Highland | FORT WILLIAM | KINLOCHMOIDART
| Highland | BROADFORD | KISHORNHILL
| Highland | BROADFORD | KYLE
| Highland | LAIRG | LAIRG GRID
| Highland | MYBSTER | LATHERON
| Highland | NAIRN | LETHEN
| Highland | GRUDIE BRIDGE | LETTEREWE
| Highland | FORT WILLIAM | LIDDESDALE
| Highland | GRUDIE BRIDGE | LOCH GLASCARNOCH
| Highland | FORT WILLIAM | LOCHALINE
| Highland | GRUDIE BRIDGE | LOCHINVER
| Highland | BROADFORD | LOWER OLLACH
| Highland | FORT WILLIAM | MALLAIG
| Highland | BEAULY | MARYBANK
| Highland | MYBSTER | MELVICH
| Highland | THURSO | MOUNT PLEASANT
| Highland | BEAULY | MUIR OF ORD
| Highland | BEAULY | MUIREND
| Highland | NAIRN | NAIRN CENTRAL
| Highland | ALNESS | NIGG
| Highland | BROADFORD | NOSTIE BRIDGE
| Highland | THURSO | ORMLIE
| Highland | CASSLEY | OVERSCAIG
| Highland | ALNESS | PEDDIESTON
| Highland | FORT WILLIAM | PINEGROVE
| Highland | FORT WILLIAM | POOR HOUSE
| Highland | DUNVEGAN | PORTREE
| Highland | QUOICH | QUOICH PRIMARY
| Highland | FORT WILLIAM | RAHOY
| Highland | INVERNESS | RAIGMORE
| Highland | INVERNESS | LONGMAN DRIVE
| Highland | CASSLEY | RHICONICH
| Highland | TAYNUILT | SALEN
| Highland | BROADFORD | SHIELDAIG
| Highland | SHIN | SHIN
| Highland | FORT WILLIAM | SHONA BEAG
| Highland | BROADFORD | SKULAMUS
| Highland | FORT WILLIAM | STRONTIAN
| Highland | ALNESS | TAIN
| Highland | BOAT OF GARTEN | TOMATIN
| Highland | LAIRG | TORBOLL
| Highland | LAIRG | TRESSADY
| Highland | DUNVEGAN | UIG
| Highland | GRUDIE BRIDGE | ULLAPOOL
| Highland | INVERNESS | WATERLOO PLACE
| Highland | KILLIN | WESTER DRUMMOND
| Highland | MYBSTER | WICK
| Moray | KEITH | ABERLOUR
| Moray | ELGIN | ASHGROVE
| Moray | BOAT OF GARTEN | AVIEMORE
| Moray | TARLAND | BALLATER
| Moray | BOAT OF GARTEN | BALLINDALLOCH
| Moray | ELGIN | BILBOHALL
| Moray | KEITH | BUCKIE
| Moray | ELGIN | BURGHEAD
| Moray | KEITH | CULLEN
| Moray | ELGIN | CUMMING STREET
| Moray | KEITH | DUFFTOWN
| Moray | ELGIN | ELGIN
| Moray | ELGIN | FOCHABERS
| Moray | NAIRN | FORRES
| Moray | BOAT OF GARTEN | GRANTOWN
| Moray | KEITH | HUNTLY
| Moray | KEITH | KEITH
| Moray | ELGIN | KINLOSS
| Moray | NAIRN | LETHEN
| Moray | ELGIN | LHANBRYDE
| Moray | KEITH | LIMEHILLOCKS
| Moray | ELGIN | LOSSIEMOUTH
| Moray | KEITH | MARNOCH
| Moray | TARLAND | MOSSAT
| Moray | NAIRN | NAIRN CENTRAL
| Moray | MACDUFF | PORTSOY
| Moray | KEITH | ROTHES
| Moray | TARLAND | STRATHDON
| North Ayrshire | CARRADALE | BALLIEKINE
| North Ayrshire | CARRADALE | BRODICK
| North Ayrshire | DUNOON | BRUCHAG
| North Ayrshire | CARRADALE | MACHRIE
| North Ayrshire | CARRADALE | WHITING BAY
| North Lanarkshire | BRACO | KIPPEN
| Orkney Islands | THURSO | BURGARHILL
| Orkney Islands | THURSO | EDAY
| Orkney Islands | THURSO | EDAY TIDAL
| Orkney Islands | THURSO | FLOTTA
| Orkney Islands | THURSO | KIRKWALL
| Orkney Islands | THURSO | LYNESS
| Orkney Islands | THURSO | NORTH HOY
| Orkney Islands | THURSO | RACKWICK
| Orkney Islands | THURSO | ROUSAY
| Orkney Islands | THURSO | SANDAY
| Orkney Islands | THURSO | SHAPINSAY
| Orkney Islands | THURSO | ST MARYS
| Orkney Islands | THURSO | STROMNESS
| Orkney Islands | THURSO | STRONSAY
| Orkney Islands | THURSO | WESTRAY
| Perth and Kinross | TUMMEL BRIDGE | ABERFELDY
| Perth and Kinross | ABERNETHY | ABERNETHY
| Perth and Kinross | COUPAR ANGUS | ALYTH
| Perth and Kinross | BOAT OF GARTEN | AVIEMORE
| Perth and Kinross | ABERNETHY | BALBEGGIE
| Perth and Kinross | TARLAND | BALLATER
| Perth and Kinross | RANNOCH | BLACKMOUNT
| Perth and Kinross | COUPAR ANGUS | BLAIRGOWRIE
| Perth and Kinross | TUMMEL BRIDGE | BONSKEID
| Perth and Kinross | ABERNETHY | BRIDGE OF EARN
| Perth and Kinross | RANNOCH | BRIDGE OF GAUR
| Perth and Kinross | BURGHMUIR | BURGHMUIR
| Perth and Kinross | BRACO | CALLANDER
| Perth and Kinross | TUMMEL BRIDGE | CALVINE
| Perth and Kinross | COUPAR ANGUS | CAPUTH
| Perth and Kinross | KILLIN | CASHLIE
| Perth and Kinross | KILLIN | CHAORACH
| Perth and Kinross | KILLIN | COSHIEVILLE
| Perth and Kinross | COUPAR ANGUS | COUPAR ANGUS
| Perth and Kinross | BRACO | CRIEFF
| Perth and Kinross | ST FILLANS | DALCHONZIE
| Perth and Kinross | COUPAR ANGUS | DALRULZION
| Perth and Kinross | BOAT OF GARTEN | DALWHINNIE
| Perth and Kinross | BRACO | DUNBLANE
| Perth and Kinross | ABERNETHY | ERROL
| Perth and Kinross | TUMMEL BRIDGE | FINCASTLE
| Perth and Kinross | BRACO | FORTEVIOT
| Perth and Kinross | ABERNETHY | GLENDEVON
| Perth and Kinross | BRACO | GLENEAGLES
| Perth and Kinross | RANNOCH | GLENETIVE
| Perth and Kinross | BURGHMUIR | GOODLYBURN
| Perth and Kinross | CHARLESTON | GOURDIE
| Perth and Kinross | ABERNETHY | HARBOUR
| Perth and Kinross | BURGHMUIR | INVERALMOND
| Perth and Kinross | FORT WILLIAM | INVERLOCHY
| Perth and Kinross | KILLIN | KILLIN TOWN
| Perth and Kinross | BOAT OF GARTEN | KINGUSSIE
| Perth and Kinross | TUMMEL BRIDGE | KINLOCH RANNOCH
| Perth and Kinross | COUPAR ANGUS | LEOCH
| Perth and Kinross | KILLIN | LOCHEARNHEAD
| Perth and Kinross | LUNANHEAD | MARYTON
| Perth and Kinross | ABERNETHY | MILNATHORT
| Perth and Kinross | CHARLESTON | NINEWELLS
| Perth and Kinross | TUMMEL BRIDGE | PITLOCHRY
| Perth and Kinross | BURGHMUIR | REDGORTON
| Perth and Kinross | ABERNETHY | SCONE
| Perth and Kinross | ST FILLANS | ST FILLANS
| Perth and Kinross | BURGHMUIR | THIMBLEROW
| Perth and Kinross | RANNOCH | TYNDRUM
| Shetland Islands | WOODHILL | BRAE
| Shetland Islands | SHETLAND | FIRTH
| Shetland Islands | SHETLAND | GUTCHER
| Shetland Islands | SHETLAND | MID YELL
| Shetland Islands | SHETLAND | SANDWICK
| Shetland Islands | SHETLAND | SCALLOWAY
| Shetland Islands | SHETLAND | SUMBURGH
| Shetland Islands | SHETLAND | TUMBLIN
| Shetland Islands | SHETLAND | UNST
| Shetland Islands | SHETLAND | VOE
| Stirling | STRATHLEVEN | ABERFOYLE
| Stirling | KILLIN | ARCHYLE
| Stirling | BRACO | CALLANDER
| Stirling | KILLIN | CASHLIE
| Stirling | KILLIN | CHAORACH
| Stirling | KILLIN | COSHIEVILLE
| Stirling | ST FILLANS | DALCHONZIE
| Stirling | TAYNUILT | DALMALLY
| Stirling | STRATHLEVEN | DRYMEN
| Stirling | BRACO | DUNBLANE
| Stirling | BRACO | GLENEAGLES
| Stirling | STRATHLEVEN | KEPCULLOCH
| Stirling | STRATHLEVEN | KILLEARN
| Stirling | KILLIN | KILLIN TOWN
| Stirling | BRACO | KIPPEN
| Stirling | KILLIN | LOCHEARNHEAD
| Stirling | KILLIN | LUBNAIG
| Stirling | ST FILLANS | ST FILLANS
| Stirling | RANNOCH | TYNDRUM
| West Dunbartonshire | STRATHLEVEN | BLAIRLINNANS
| West Dunbartonshire | STRATHLEVEN | DRYMEN
| West Dunbartonshire | STRATHLEVEN | KILLEARN

## EISD
#VALUE! | GSPs in November 2025 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Abernethy | 2028 | Under active review | 2028 | Under active review
| Braco | 2025 | Under active review | 2035 | Under active review
| Burghmuir | 2028 | Under active review | 2028 | Under active review
| Coupar Angus | NA |  | 2029 | Under active review
| Killin | 2025 | Under active review | 2030 | Under active review
| Rannoch | 2025 | Under active review | 2025 | Under active review
| St Fillans | 2025 | Under active review | 2028 | Under active review
| Tummel Bridge | 2025 | Under active review | 2026 | Under active review
| Redmoss | NA |  | 2031
| Woodhill | NA |  | NA
| Ardkinglas | 2025 | Under active review | 2030 | Under active review
| Ardmore | 2028 | Under active review | 2028 | Under active review
| Cassley | NA | Under active review | 2028 | Under active review
| Charleston | 2030 | Under active review | 2028 | Under active review
| Clayhills | NA |  | 2025 | Under active review
| Lyndhurst | 2032 | Under active review | 2035 | Under active review
| Peterhead Grange | 2033 | Under active review | 2033 | Under active review
| Dunbeath | NA |  | NA | Under active review
| Alness | NA |  | 2030 | Under active review
| Beauly | NA |  | 2030 | Under active review
| Broadford | 2028 | Under active review | 2028 | Under active review
| Brora | NA |  | 2034 | Under active review
| Dunvegan | NA |  | 2028 | Under active review
| Fasnakyle | 2025 | Under active review | 2035 | Under active review
| Grudie Bridge | NA |  | NA
| Lairg | NA |  | 2033 | Under active review
| Shin | NA |  | NA | Under active review
| Orrin | NA |  | NA
| Dounreay | NA |  | 2033 | Under active review
| Fraserburgh | 2033 | Under active review | 2033 | Under active review
| Dallas | 2025 | Under active review | N/A
| Kinlochleven | 2025 | Under active review | N/A
| Glenfarclas | 2025 | Under active review | N/A
| Berryburn | 2024 | Under active review | 2030 | Under active review
| Fetteresso | NA |  | 2029 | Under active review
| Craigiebuckler | NA |  | 2032
| Kintore | 2032 | Under active review | 2032 | Under active review
| Tarland | NA |  | 2032 | Under active review
| Willowdale | NA |  | 2030
| Dyce | 2025 | Under active review | 2025 | Under active review
| Persley | NA |  | NA
| Peterhead Shell | NA |  | NA
| Strichen | 2033 | Under active review | 2033 | Under active review
| Arbroath | 2026 | Under active review | 2032 | Under active review
| Bridge of Dun | NA |  | 2032 | Under active review
| Fiddes | NA |  | 2032 | Under active review
| Lunanhead | 2028 | Under active review | 2028 | Under active review
| Milton of Craigie | NA |  | 2033 | Under active review
| Ceannacroc | NA |  | NA
| Fort Augustus | 2035 | Under active review | 2035 | Under active review
| Quoich | 2028 |  | 2028
| Boat of Garten | 2025 | Under active review | 2030 | Under active review
| Inverness | NA |  | 2030 | Under active review
| Nairn | 2027 | Under active review | 2027 | Under active review
| Rothienorman | 2033 | Under active review | 2033 | Under active review
| Cairnford | NA |  | NA
| Elgin | 2025 | Under active review | 2027 | Under active review
| Keith 1 | 2028 | Under active review | 2028 | Under active review
| Keith 2 | 2028 | Under active review | 2028 | Under active review
| MacDuff | NA |  | 2029 | Under active review
| Carradale 1 | 2025 | Under active review | 2034 | Under active review
| Carradale 2 | 2025 | Under active review | 2034 | Under active review
| Clachan | 2025 | Under active review | 2030 | Under active review
| Dunoon | 2025 | Under active review | 2028 | Under active review
| Fort William | NA | Under active review | NA | Under active review
| Port Ann | 2029 | Under active review | 2034 | Under active review
| Taynuilt | 2025 | Under active review | 2034 | Under active review
| Dudhope | NA |  | 2028 | Under active review
| Mybster 1 | NA |  | 2035
| Mybster 2 | NA |  | NA
| Thurso | NA |  | 2033
| Sloy | 2025 | Under active review | 2030 | Under active review
| St Fergus Gas | NA |  | 2033 | Under active review
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.ssen-transmission.co.uk/customer-connections/transmission-owner-reinforcement-instruction-tori-quarterly-update-reports/
2025-04-11 | Transmission Owner's freeze date
SHEPD | DNO Licence area
SSEN Transmisson | Transmision Owner providing
V1.1 11/04/2025 | Last update (version, date)
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 The above EISD's are likely to be subject to change on completion of NESO's Connections Reform Project TMO4+, further information can be found at:
https://www.neso.energy/industry-information/connections-reform
3 For storage, both the demand and generation EISDs may be relevant.
4 Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
5 Where the tranmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
6 The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
7 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
8 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.