## ON-P Fixed Inputs
Fixed Inputs
GUIDANCE
- This tab contains all fixed parameters as per the Ofgem CBA template, and should be updated accordingly for RIIO ED2 - The user should enter the Pre-tax WACC and CI and CML prices as per their business plan - The CPIH Index can be used to help the user convert all costs and benefits to the tool price base. The tool price base is currently set at 2018/19 prices. This should be updated once the price base year for RIIO ED2 is determined.
|  | Parameters |  |  |  |  | Prices
|  | Capitalisation rates | 85%
|  | Pre-tax WACC | 3.6% | enter DNO specific pre-tax WACC figure |  |  | Losses (£/MWh) |  |  | 59.7406 | BEIS Traded Carbon Price (Central) | https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/671191/Updated_short-term_traded_carbon_values_for_modelling_purposes.pdf
|  | Discount Rate <= 30 years | 3.5% | HMRC Green Book (see Discount Factors spreadsheet 'Standard Discount Factors' tab | https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/685903/The_Green_Book.pdf |  | Cost per litre oil (£/litre) |  |  | 44.5161
|  | Discount Rate > 30 years | 3% | HMRC Green Book (see Discount Factors spreadsheet 'Standard Discount Factors' tab | https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/685912/Discount_Factors.xlsx |  | CI (£s per interruption, 2012/13 prices) |  |  | 15.4435
|  | Discount rate for safety <= 30 years | 1.5% | HMRC Green Book (see Discount Factors spreadsheet 'Health Discount Factors' tab | https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/685912/Discount_Factors.xlsx |  | CML (£s per minute lost, 2012/13 prices) |  |  | 0.37667
|  | Discount rate for safety > 30 years | 1.286% | HMRC Green Book (see Discount Factors spreadsheet 'Health Discount Factors' tab | https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/685912/Discount_Factors.xlsx |  | CI (£s per interruption, 2018/19 prices) |  |  | 17.0185
|  | Assumed Asset Life (Years) | 45 |  |  |  | CML (£s per minute lost, 2018/19 prices) |  |  | 0.41508
|  | Cost per Fatality (£m) | 1.617 |  | http://www.hse.gov.uk/economics/eauappraisal.htm
|  | Cost per Non Fatal injury (£m) | 0.0084 |  | http://www.hse.gov.uk/statistics/cost.htm
| Decarbonisation of electricity assumption: Power sector emissions are anticipated to reduce to 10g/kWh by 2050. Assume a linear decarbonisation pathway from 2017/18 until 2050. Power sector emissions reduce by 11.35 g/kWh p.a. between now and 2030. Beyond 2050 keep emissions at 10g/kWh 1,000 kg = 1 tonne; 1,000 kWh = 1 MWh; 1 kg = 1,000g | [7 empty] | CPIH Index
| Calendar Year | Average Index | g CO2e per kWh (Defra) | Traded carbon price (£/t 2016/17)1 | Traded carbon price (£/t 2018/19 prices) | Electricity GHG conversion factor (tonnes per MWh)3 |  |  | Regulatory Year | Average Index | Calendar Year | Conversion from FY to 2018/19
| 2004 | [7 empty] | 2003/04 | 76.975 | 2004 | 1.3827
| 2005 | [7 empty] | 2004/05 | 78.125 | 2005 | 1.3623
| 2006 | [7 empty] | 2005/06 | 79.825 | 2006 | 1.3333
| 2007 | [7 empty] | 2006/07 | 81.9167 | 2007 | 1.2993
| 2008 | [7 empty] | 2007/08 | 83.825 | 2008 | 1.2697
| 2009 | [7 empty] | 2008/09 | 86.8583 | 2009 | 1.2254
| 2010 | 223.558 | 499.33 | [5 empty] | 2009/10 | 88.4333 | 2010 | 1.2035
| 2011 | 235.18 | 490.56 | 14.2275 | 16.6572 | 0.49056 |  |  | 2010/11 | 90.9083 | 2011 | 1.1708
| 2012 | 242.725 | 553.89 | 6.0704 | 6.8509 | 0.55389 |  |  | 2011/12 | 94.3083 | 2012 | 1.1286
| 2013 | 250.1083 | 518.7 | 3.6781 | 4.0532 | 0.5187 |  |  | 2012/13 | 96.5833 | 2013 | 1.102
| 2014 | 256.0333 | 465.34 | 4.7214 | 5.0965 | 0.46534 |  |  | 2013/14 | 98.6 | 2014 | 1.0794
| 2015 | 258.5417 | 394.12 | 6.2601 | 6.6812 | 0.39412 |  |  | 2014/15 | 99.725 | 2015 | 1.0673
| 2016 | 263.05 | 309.13 | 4.3298 | 4.6006 | 0.30913 |  |  | 2015/16 | 100.1667 | 2016 | 1.0626
1 | 2017 | 272.475 | 384.43 | 4.13 | 4.3289 | 0.38443 |  | 1 | 2016/17 | 101.5417 | 2017 | 1.0482
2 | 2018 | 282.0116 | 373.0836 | 4.19 | 4.2791 | 0.37308 |  | 2 | 2017/18 | 104.2167 | 2018 | 1.0213
3 | 2019 | 290.754 | 361.7373 | 4.37 | 4.37 | 0.36174 |  | 3 | 2018/19 | 106.433 | 2019 | 1
4 | 2020 | 299.4766 | 350.3909 | 4.56 | 4.4706 | 0.35039 |  | 4 | 2019/20 | 108.5617 | 2020 | 0.98039
5 | 2021 | 308.4609 | 339.0445 | 4.76 | 4.5752 | 0.33904 |  | 5 | 2020/21 | 110.7329 | 2021 | 0.96117
6 | 2022 | 317.7147 | 327.6982 | 4.94 | 4.6551 | 0.3277 |  | 6 | 2021/22 | 112.9476 | 2022 | 0.94232
7 | 2023 | 327.2462 | 316.3518 | 6.44 | 5.9496 | 0.31635 |  | 7 | 2022/23 | 115.2065 | 2023 | 0.92385
8 | 2024 | 337.0636 | 305.0055 | 10.18 | 9.2203 | 0.30501 |  | 8 | 2023/24 | 117.5106 | 2024 | 0.90573
9 | 2025 | 347.1755 | 293.6591 | 13.21 | 11.7301 | 0.29366 |  | 9 | 2024/25 | 119.8608 | 2025 | 0.88797
10 | 2026 | 357.5907 | 282.3127 | 17.83 | 15.5221 | 0.28231 |  | 10 | 2025/26 | 122.2581 | 2026 | 0.87056
11 | 2027 | 368.3184 | 270.9664 | 24.2 | 20.6545 | 0.27097 |  | 11 | 2026/27 | 124.7032 | 2027 | 0.85349
12 | 2028 | 379.368 | 259.62 | 28.82 | 24.1153 | 0.25962 |  | 12 | 2027/28 | 127.1973 | 2028 | 0.83676
13 | 2029 | 390.749 | 248.2736 | 32.98 | 27.0551 | 0.24827 |  | 13 | 2028/29 | 129.7412 | 2029 | 0.82035
14 | 2030 | 402.4715 | 236.9273 | 39.41 | 31.696 | 0.23693 |  | 14 | 2029/30 | 132.3361 | 2030 | 0.80426
15 | 2031 | 414.5457 | 225.5809 | 39.41 | 31.0745 | 0.22558 |  | 15 | 2030/31 | 134.9828 | 2031 | 0.78849
16 | 2032 | 426.982 | 214.2345 | 39.41 | 30.4652 | 0.21423 |  | 16 | 2031/32 | 137.6824 | 2032 | 0.77303
17 | 2033 | 439.7915 | 202.8882 | 39.41 | 29.8679 | 0.20289 |  | 17 | 2032/33 | 140.4361 | 2033 | 0.75788
18 | 2034 | 452.9852 | 191.5418 | 39.41 | 29.2822 | 0.19154 |  | 18 | 2033/34 | 143.2448 | 2034 | 0.74301
19 | 2035 | 466.5748 | 180.1955 | 39.41 | 28.708 | 0.1802 |  | 19 | 2034/35 | 146.1097 | 2035 | 0.72845
20 | 2036 | 480.572 | 168.8491 | 39.41 | 28.1451 | 0.16885 |  | 20 | 2035/36 | 149.0319 | 2036 | 0.71416
21 | 2037 |  | 157.5027 | 39.41 | 27.5933 | 0.1575 |  | 21 | 2036/37 | 152.0125 | 2037 | 0.70016
22 | 2038 |  | 146.1564 | 39.41 | 27.0522 | 0.14616 |  | 22 | 2037/38 | 155.0528 | 2038 | 0.68643
23 | 2039 |  | 134.81 | 39.41 | 26.5218 | 0.13481 |  | 23 | 2038/39 | 158.1538 | 2039 | 0.67297
24 | 2040 |  | 123.4636 | 39.41 | 26.0018 | 0.12346 |  | 24 | 2039/40 | 161.3169 | 2040 | 0.65978
25 | 2041 |  | 112.1173 | 39.41 | 25.4919 | 0.11212 |  | 25 | 2040/41 | 164.5433 | 2041 | 0.64684
26 | 2042 |  | 100.7709 | 39.41 | 24.9921 | 0.10077 |  | 26 | 2041/42 | 167.8341 | 2042 | 0.63416
27 | 2043 |  | 89.4245 | 39.41 | 24.502 | 0.089425 |  | 27 | 2042/43 | 171.1908 | 2043 | 0.62172
28 | 2044 |  | 78.0782 | 39.41 | 24.0216 | 0.078078 |  | 28 | 2043/44 | 174.6146 | 2044 | 0.60953
29 | 2045 |  | 66.7318 | 39.41 | 23.5506 | 0.066732 |  | 29 | 2044/45 | 178.1069 | 2045 | 0.59758
30 | 2046 |  | 55.3855 | 39.41 | 23.0888 | 0.055385 |  | 30 | 2045/46 | 181.669 | 2046 | 0.58586
31 | 2047 |  | 44.0391 | 39.41 | 22.6361 | 0.044039 |  | 31 | 2046/47 | 185.3024 | 2047 | 0.57437
32 | 2048 |  | 32.6927 | 39.41 | 22.1923 | 0.032693 |  | 32 | 2047/48 | 189.0085 | 2048 | 0.56311
33 | 2049 |  | 21.3464 | 39.41 | 21.7571 | 0.021346 |  | 33 | 2048/49 | 192.7886 | 2049 | 0.55207
34 | 2050 |  | 10 | 39.41 | 21.3305 | 0.01 |  | 34 | 2049/50 | 196.6444 | 2050 | 0.54125
35 | 2051 |  | 10 | 39.41 | 20.9123 | 0.01 |  | 35 | 2050/51 | 200.5773 | 2051 | 0.53063
36 | 2052 |  | 10 | 39.41 | 20.5022 | 0.01 |  | 36 | 2051/52 | 204.5889 | 2052 | 0.52023
37 | 2053 |  | 10 | 39.41 | 20.1002 | 0.01 |  | 37 | 2052/53 | 208.6806 | 2053 | 0.51003
38 | 2054 |  | 10 | 39.41 | 19.7061 | 0.01 |  | 38 | 2053/54 | 212.8542 | 2054 | 0.50003
39 | 2055 |  | 10 | 39.41 | 19.3197 | 0.01 |  | 39 | 2054/55 | 217.1113 | 2055 | 0.49022
40 | 2056 |  | 10 | 39.41 | 18.9409 | 0.01 |  | 40 | 2055/56 | 221.4536 | 2056 | 0.48061
41 | 2057 |  | 10 | 39.41 | 18.5695 | 0.01 |  | 41 | 2056/57 | 225.8826 | 2057 | 0.47119
42 | 2058 |  | 10 | 39.41 | 18.2054 | 0.01 |  | 42 | 2057/58 | 230.4003 | 2058 | 0.46195
43 | 2059 |  | 10 | 39.41 | 17.8484 | 0.01 |  | 43 | 2058/59 | 235.0083 | 2059 | 0.45289
44 | 2060 |  | 10 | 39.41 | 17.4984 | 0.01 |  | 44 | 2059/60 | 239.7085 | 2060 | 0.44401
45 | 2061 |  | 10 | 39.41 | 17.1553 | 0.01 |  | 45 | 2060/61 | 244.5026 | 2061 | 0.4353
46 | 2062 |  | 10 | 39.41 | 16.819 | 0.01 |  | 46 | 2061/62 | 249.3927 | 2062 | 0.42677
47 | 2063 |  | 10 | 39.41 | 16.4892 | 0.01 |  | 47 | 2062/63 | 254.3805 | 2063 | 0.4184
48 | 2064 |  | 10 | 39.41 | 16.1659 | 0.01 |  | 48 | 2063/64 | 259.4681 | 2064 | 0.4102
49 | 2065 |  | 10 | 39.41 | 15.8489 | 0.01 |  | 49 | 2064/65 | 264.6575 | 2065 | 0.40215
50 | 2066 |  | 10 | 39.41 | 15.5381 | 0.01 |  | 50 | 2065/66 | 269.9506 | 2066 | 0.39427
51 | 2067 |  | 10 | 39.41 | 15.2334 | 0.01 |  | 51 | 2066/67 | 275.3497 | 2067 | 0.38654
52 | 2068 |  | 10 | 39.41 | 14.9348 | 0.01 |  | 52 | 2067/68 | 280.8567 | 2068 | 0.37896
53 | 2069 |  | 10 | 39.41 | 14.6419 | 0.01 |  | 53 | 2068/69 | 286.4738 | 2069 | 0.37153
54 | 2070 |  | 10 | 39.41 | 14.3548 | 0.01 |  | 54 | 2069/70 | 292.2033 | 2070 | 0.36424
55 | 2071 |  | 10 | 39.41 | 14.0734 | 0.01 |  | 55 | 2070/71 | 298.0473 | 2071 | 0.3571
56 | 2072 |  | 10 | 39.41 | 13.7974 | 0.01 |  | 56 | 2071/72 | 304.0083 | 2072 | 0.3501
57 | 2073 |  | 10 | 39.41 | 13.5269 | 0.01 |  | 57 | 2072/73 | 310.0884 | 2073 | 0.34323
58 | 2074 |  | 10 | 39.41 | 13.2616 | 0.01 |  | 58 | 2073/74 | 316.2902 | 2074 | 0.3365
59 | 2075 |  | 10 | 39.41 | 13.0016 | 0.01 |  | 59 | 2074/75 | 322.616 | 2075 | 0.32991
60 | 2076 |  | 10 | 39.41 | 12.7467 | 0.01 |  | 60 | 2075/76 | 329.0683 | 2076 | 0.32344
61 | 2077 |  | 10 | 39.41 | 12.4967 | 0.01 |  | 61 | 2076/77 | 335.6497 | 2077 | 0.3171
62 | 2078 |  | 10 | 39.41 | 12.2517 | 0.01 |  | 62 | 2077/78 | 342.3627 | 2078 | 0.31088
63 | 2079 |  | 10 | 39.41 | 12.0115 | 0.01 |  | 63 | 2078/79 | 349.2099 | 2079 | 0.30478
64 | 2080 |  | 10 | 39.41 | 11.776 | 0.01 |  | 64 | 2079/80 | 356.1941 | 2080 | 0.29881
65 | 2081 |  | 10 | 39.41 | 11.545 | 0.01 |  | 65 | 2080/81 | 363.318 | 2081 | 0.29295
66 | 2082 |  | 10 | 39.41 | 11.3187 | 0.01 |  | 66 | 2081/82 | 370.5844 | 2082 | 0.2872
67 | 2083 |  | 10 | 39.41 | 11.0967 | 0.01 |  | 67 | 2082/83 | 377.9961 | 2083 | 0.28157
68 | 2084 |  | 10 | 39.41 | 10.8792 | 0.01 |  | 68 | 2083/84 | 385.556 | 2084 | 0.27605
69 | 2085 |  | 10 | 39.41 | 10.6658 | 0.01 |  | 69 | 2084/85 | 393.2671 | 2085 | 0.27064
70 | 2086 |  | 10 | 39.41 | 10.4567 | 0.01 |  | 70 | 2085/86 | 401.1325 | 2086 | 0.26533
[8 empty] | 71 | 2086/87 | 409.1551 | 2087 | 0.26013
|  |  |  | 11.3464 | p.a. reduction in carbon intensity
CPIH INDEX 00: ALL ITEMS 2015=100; Identifier = L522 |  |  |  | note: Values taken from Central scenario from Updated short-term carbon values used for modelling purposes (2017)
https://www.ons.gov.uk/economy/inflationandpriceindices/timeseries/l522/mm23 |  |  |  | 1 https://www.gov.uk/carbon-valuation
https://www.ons.gov.uk/generator?format=xls&uri=/economy/inflationandpriceindices/timeseries/l522/mm23

## Flexible Service Valuation Mech
Value Stream | 1.06 Section | Valuation | Reference Section in this report 1.07 | Equation Type | Equation | Actions | Closed?
Proposed Short Term Flexible Service Valuation | 2.1 | Traditional Reinforcement Net Present Value (NPV) | 3.B.II.Construction Projects | Fixed Equation | NPV = Construction Cost/(1+discount)^t | Completed | Yes
| 2.2 | Network Losses |  | Fixed Equation | = Calculated Losses * Cost of Losses | Completed | Yes
| 2.3 | Flexibility Service Administration and Management Costs | 3.A.X. Contract Information | Fixed Equation | = admin cost/year * simulation length | Completed | Yes
Possible Future Flexible Service Valuation | 3.1 | Remaining Asset Life Value | 3.D.IV. Remaining Value of Replaced Assets | Equation Editor | Remaining value of replaced asset = (1-(age/average asset lifespan)) * ( Total investment * Capitalisation rate) | Completed | Yes
| 3.2 | Asset Life Costs (NPV+) | Modeled as part of this project |  | NPV = (Construction Cost+life-time maintenance costs)/(1+discount)^t | Completed | Yes
| 3.3 | Net Avoided Outage Costs (Asset Health) | 3.A.II. Probability of asset failure | Fixed Equation | F(f) = 1 - e~(t/(n+b((6-HI)-0.5)))^B | Completed | Yes | *Check CBRM
Possible Future Plus Flexible Service Valuation | 4.1 | Loss of Export Capacity | 3.D.II. Tracking Cost of Running the System | Scenarios | Run 2 scenarios, compare results of export capacity | Completed | Yes
| 4.2 | Avoided Energy | 3.D.II. Tracking Cost of Running the System | Fixed Equation | = Energy_traditional - Energy_Flex | Completed | Yes
| 4.3 | Community Generation Credit | 2.A.VIII. Societal Cost | Fixed Equation | = Community Generation Credit/year * Simulation Length | Completed | Yes | *Should be a percentage value rather than 0.5p as value of money changes over time
| 4.4 | Net Avoided Greenhouse Gasses (GHG) | 3.C.IX. CO2 Emissions | Fixed Equation | = (CO2_Bulk + CO2_DER)_Trad - (CO2_Bulk + CO2_DER)_Flex | Completed | Yes | *Be careful of double counting
Alternative Value Stream Option | 5.1 | Operating Assets Beyond Capacity | 3.A.VI.Cost of rating violations | Equation Editor | F(f) = 1 - e~(t/(n+b((6-HI)-0.5)))^B | Completed | Yes
Key
|  |  |  | Fixed Equation | Formula is set as shown
|  |  |  | Equation Editor | User can modify the specific formula, but the variables in the equation are set
|  |  |  | Scenarios | Evaluated by running multiple scenarios and determining a cost from the difference in the scenario results
| Below no longer included |  |  |  | = Net Non-Energy Costs Value/year * Simulation Length
| 2.2 | Customer Interruption (CI) and Customer Minutes Lost (CML) | 3.A.II.Probability of asset failure
| 2.3 | Backup Generation Costs (Diesel generators as DER)
| 2.4 | Fault Likelihood/Outage Risk
| 3.3 | Asset Redeployment Value | 3.D.IV.Remaining Value of Replaced Assets
| 3.4 | Activity Labour Costs | 3.A.IX.Asset OPEX Cost
3.6
3.8
| 3.9 | Net Avoided Outage Costs | 3.A.II. Probability of asset failure
| 3.11 | Avoided Generation Capacity Cost | 3.D.II. Tracking Cost of Running the System
| 3.12 | Valuing Risk and Reward
| 3.13 | Location Multiplier
| 3.14 | Optionality
| 3.15 | Ancillary Service Cost
| 3.16 | Lost Utility Revenue
| 3.17 | Net Avoided Restoration Costs
| 3.18 | Avoided Distribution Capacity Infrastructure
| 3.19 | Wholesale Market Price Impacts
| 3.2 | Avoided Ancillary Services
| 3.21 | Avoided Transmission Losses
| 3.22 | Avoided Transmission Capacity Infrastructure and O&M
| 4.5 | Net Avoided Air Pollutants
| 4.6 | Avoided Water Impacts
| 4.7 | Avoided Land Impacts
| 4.8 | Net Non-Energy Benefits
| 4.9 | Net Non-Energy Costs
F(f) = 1 - e~(t/(n+b((6-HI)-0.5)))^B

## 2.1 Traditional NPV
Traditional Reinforcement Net Present Value (NPV)
Cost of Traditional Solution
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
Asset cost | 0 | 0 | 0 | 0 | 1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Deferred Asset Cost (deferment depends on load forecast) | 0 | 0 | 0 | 0 | 0 | 1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DER admin Cost | 0 | 0 | 0 | 0 | 8513.5135 | 8513.5135 | 8513.5135 | 8513.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Deferred Cost | 0 | 0 | 0 | 0 | 8513.5135 | 1008513.5135 | 8513.5135 | 8513.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest Rate | 4% | *Interest rate is variable in Grid OS IDP
Asset NPV Cost | 854804.191
Deferred Asset NPV Cost | 821927.1068
Total Deferred NPV Cost | 849399.9053
Deferrment Saving | 5404.2857
Availability Percentage | 95%
Utilisation Percentage | 5%
Max Availability Payment | 5134.0715
Max Utilisaiton Payment | 270.2143
Number of availability hours required | 100 | *Determined by Grid OS IDP model run
Number of availability MW required | 5 | *Determined by Grid OS IDP model run
Number of uilisation hours required | 1 | *Determined by Grid OS IDP model run
Number of utilisation MW required | 10 | *Determined by Grid OS IDP model run
Availability Price (£/MWhr) | 10.2681
Utilisation Price (£/MWhr) | 27.0214
Costs
DER Admin Costs | 8513.5135 | *Asset deferrment saving divided by 2.26 (Needs checking by flex solution team)
CCCM Doc costs to be input here by Opus One
Asset costs recorded in Asset Library of Grid OS IDP

## 2.2 Network Losses
Network Losses
59.7406 | per MWhr
Losses (MW) | 1.1 | Calculated from simulation
Cost of Losses | 65.7147

## 2.3 Flexibility Service Admin
Flexibility Service Administration and Management Costs (incurred by DNO)
Total annual hours | 140
Total annual days | 18.9189
SSEN day rate (including overheads) = £450 | 450
Annual cost of flexible service admin to SSEN (per service) | 8513.5135
Length of simulation (years) | 1.5
Admin Cost | 12770.2703
Annual 3rd party charges (estimate) | 160000

## 3.1 Remaining Asset Life Value
Remaining Asset Life Value
Average Asset lifespan (years) | 45
RIIO-ED1
| 1 | 2 | 3 | 4 | 5 | 6
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Total Investment (million) | 10 | 15 | 5 | 10 | 12
Capitalisation rate (%) | 70 | 70 | 70 | 70 | 70
Capitalised investment (million) | 7 | 10.5 | 3.5 | 7 | 8.4
Depreciation | [6 empty] | Total Depreciation | Remaining Value | Remaining Value(Opus One Formula)
2016 |  | 0.15556 | 0.15556 | 0.15556 | 0.15556 | 0.15556 | 0.77778 | 6.2222 | 6.2222
2017 |  |  | 0.23333 | 0.23333 | 0.23333 | 0.23333 | 0.93333 | 9.5667 | 9.5667
2018 |  |  |  | 0.077778 | 0.077778 | 0.077778 | 0.23333 | 3.2667 | 3.2667
2019 |  |  |  |  | 0.15556 | 0.15556 | 0.31111 | 6.6889 | 6.6889
2020 | [5 empty] | 0.18667 | 0.18667 | 8.2133 | 8.2133
Total project cost will be = Total equipment cost + Total labor cost - Remaining value of replaced asset.
Remaining value of replaced asset = (1-(age/average asset lifespan)) * ( Total investment * Capitalisation rate)
Remaining value of replaced asset = ((1 – (age/average asset lifespan)) (1 – (health/total health”5”)) * (Total investment * Capitalisation rate)). | [9 empty] | *Asset health removed, so this formula no longer in use.

## 3.2 Asset Life Costs (NPV+)
Traditional Reinforcement Net Present Value (NPV)
Cost of Traditional Solution
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
Asset cost | 0 | 0 | 0 | 0 | 1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Deferred Asset Cost (deferment depends on load forecast) | 0 | 0 | 0 | 0 | 0 | 1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DER admin Cost | 0 | 0 | 0 | 0 | 8513.5135 | 8513.5135 | 8513.5135 | 8513.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Deferred Cost | 0 | 0 | 0 | 0 | 8513.5135 | 1008513.5135 | 8513.5135 | 8513.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest Rate | 4% | *Interest rate is variable in Grid OS IDP
Asset NPV Cost | 854804.191
Deferred Asset NPV Cost | 821927.1068
Total Deferred NPV Cost | 849399.9053
Deferrment Saving | 5404.2857
Availability Percentage | 95%
Utilisation Percentage | 5%
Max Availability Payment | 5134.0715
Max Utilisaiton Payment | 270.2143
Number of availability hours required | 100 | *Determined by Grid OS IDP model run
Number of availability MW required | 5 | *Determined by Grid OS IDP model run
Number of uilisation hours required | 1 | *Determined by Grid OS IDP model run
Number of utilisation MW required | 10 | *Determined by Grid OS IDP model run
Availability Price (£/MWhr) | 10.2681
Utilisation Price (£/MWhr) | 27.0214
Costs
DER Admin Costs | 8513.5135 | *Asset deferrment saving divided by 2.26 (Needs checking by flex solution team)
CCCM Doc costs to be input here by Opus One
Asset costs recorded in Asset Library of Grid OS IDP
Ongoing Costs
Typical Maintenance Period | x | hours
Typical Number of Staff Required | x | #
Number of affected customers | x | #
Planned outage length | x | hours
Number of maintenance events in life span | x | #
Size of generation required | x | MWhrs
Maintenance Costs Labour
Maintenance Costs CI CML
Maintenance Costs Backup-Gen
Total Maintenance Cost
Diesel Generator Guidance | Cost per customer | Source
<10 Customers | 148.6368 | Live Line Harvester Mobile Generation Calculator
<50 Customers | 99.3242 | Live Line Harvester Mobile Generation Calculator
<100 Customer | 75.0499 | Live Line Harvester Mobile Generation Calculator
<150 Customers | 35.1105 | Live Line Harvester Mobile Generation Calculator
>150 Customers | 27.2757 | Live Line Harvester Mobile Generation Calculator
Large Industrial Customers | Variable | This will need to be calculated on per customer basis or a new calculation created based on customer load/demand.

## 3.3 Net avoided outage costs
Original PoF and CoF
|  | % over threshold | Duration(hours) |  |  |  |  | % over threshold | Duration(hours) | [5 empty] | % over threshold | Duration(hours)
| 1 | 3 | 2 |  |  |  | 1 | 5 | 1 |  |  |  |  | 1 | 8 | 2
| 2 | 2 | 1 |  |  |  | 2 | 3 | 5 |  |  |  |  | 2 | 9 | 4
| 3 | 1 | 5 |  |  |  | 3 | 2 | 6 |  |  |  |  | 3 | 12 | 13
| 4 | 1 | 1 |  |  |  | 4 | 6 | 3 |  |  |  |  | 4 | 8 | 7
| 5 | 2 | 2 |  |  |  | 5 | 8 | 9 |  |  |  |  | 5 | 3 | 3
| 6 | 2 | 1 |  |  |  | 6 | 2 | 5 |  |  |  |  | 6 | 2 | 7
| 7 | 1 | 2 |  |  |  | 7 | 1 | 2 |  |  |  |  | 7 | 5 | 9
| 8 | 1 | 3 |  |  |  | 8 | 5 | 6 |  |  |  |  | 8 | 6 | 5
| 9 | 1 | 1 |  |  |  | 9 | 3 | 3 |  |  |  |  | 9 | 3 | 6
| 10 | 1 | 1 |  |  |  | 10 | 1 | 1 |  |  |  |  | 10 | 8 | 4
| Average | 1.5 | 1.9 |  |  |  | Average | 3.6 | 4.1 |  |  |  |  | Average | 6.4 | 6
[19 empty] | Characteristic life | η
| Asset 1 | [5 empty] | Asset 2 | [6 empty] | Asset 3 |  |  |  |  | Shape parameter | β
| Number of Customers | 50 | # |  |  |  | Number of Customers | 50 | # |  |  |  |  | Number of Customers | 50 | # |  |  | HI shift Factor | b
| CML cost | 0.37667 | £ |  |  |  | CML cost | 0.37667 | £ |  |  |  |  | CML cost | 0.37667 | £ |  |  | Health Index | HI
| CI cost | 15.4435 | £ |  |  |  | CI cost | 15.4435 | £ |  |  |  |  | CI cost | 15.4435 | £
| Characteristic life | 40 | η |  |  |  | Characteristic life | 40 | η |  |  |  |  | Characteristic life | 40 | η
| Shape parameter | 3 | β |  |  |  | Shape parameter | 3 | β |  |  |  |  | Shape parameter | 3 | β
| HI shift Factor | 20 | b |  |  |  | HI shift Factor | 20 | b |  |  |  |  | HI shift Factor | 20 | b
| HI | 5 | HI |  |  |  | HI | 3 | HI |  |  |  |  | HI | 1 | HI
| Time to restore(mins) | 145 | mins |  |  |  | Time to restore(mins) | 145 | mins |  |  |  |  | Time to restore(mins) | 145 | mins
| Age | P.O.F | CI | CML | CI CML Cost |  | Age | P.O.F | CI | CML | CI CML Cost |  |  | Age | P.O.F | CI | CML | CI CML Cost
| 10 | 0.0079681 | 0.3984 | 57.7686 | 27.9125 |  | 10 | 0.0013708 | 0.06854 | 9.9383 | 4.802 |  |  | 10 | 0.00045506 | 0.022753 | 3.2992 | 1.5941
| 15 | 0.026639 | 1.3319 | 193.131 | 93.3167 |  | 15 | 0.0046189 | 0.23095 | 33.4872 | 16.1803 |  |  | 15 | 0.001535 | 0.07675 | 11.1288 | 5.3772
| 20 | 0.061995 | 3.0998 | 449.4638 | 217.1711 |  | 20 | 0.010914 | 0.5457 | 79.1261 | 38.232 |  |  | 20 | 0.0036347 | 0.18174 | 26.3516 | 12.7325
| 25 | 0.1175 | 5.8752 | 851.8975 | 411.6183 |  | 25 | 0.021205 | 1.0603 | 153.7392 | 74.2834 |  |  | 25 | 0.0070867 | 0.35434 | 51.3789 | 24.8252
| 30 | 0.19426 | 9.7132 | 1408.4191 | 680.5175 |  | 30 | 0.03636 | 1.818 | 263.6068 | 127.3691 |  |  | 30 | 0.012214 | 0.61071 | 88.5535 | 42.7871
| 35 | 0.29036 | 14.5181 | 2105.123 | 1017.1497 |  | 35 | 0.057117 | 2.8559 | 414.1008 | 200.0845 |  |  | 35 | 0.019326 | 0.9663 | 140.1139 | 67.7
| 40 | 0.4007 | 20.0352 | 2905.1055 | 1403.6839 |  | 40 | 0.084048 | 4.2024 | 609.3492 | 294.4243 |  |  | 40 | 0.02871 | 1.4355 | 208.1506 | 100.5738
| 45 | 0.51761 | 25.8804 | 3752.6642 | 1813.2059 |  | 45 | 0.1175 | 5.8752 | 851.8975 | 411.6183 |  |  | 45 | 0.040629 | 2.0314 | 294.5574 | 142.3238
| 50 | 0.63212 | 31.606 | 4582.8741 | 2214.3452 |  | 50 | 0.15757 | 7.8786 | 1142.4012 | 551.9834 |  |  | 50 | 0.055307 | 2.7654 | 400.9791 | 193.7444
| 55 | 0.73579 | 36.7894 | 5334.4564 | 2577.4934 |  | 55 | 0.20405 | 10.2027 | 1479.3895 | 714.8089 |  |  | 55 | 0.072932 | 3.6466 | 528.7564 | 255.4836
| 60 | 0.82236 | 41.118 | 5962.1148 | 2880.7644 |  | 60 | 0.25643 | 12.8216 | 1859.1387 | 898.2954 |  |  | 60 | 0.093637 | 4.6819 | 678.8715 | 328.016
| 65 | 0.88886 | 44.4432 | 6444.2635 | 3113.7282 |  | 65 | 0.31389 | 15.6944 | 2275.6894 | 1099.5637 |  |  | 65 | 0.1175 | 5.8752 | 851.8975 | 411.6183
| 70 | 0.93569 | 46.7844 | 6783.7338 | 3277.7528 |  | 70 | 0.37531 | 18.7657 | 2721.0328 | 1314.7439 |  |  | 70 | 0.14455 | 7.2273 | 1047.9525 | 506.3479
| 75 | 0.96578 | 48.2891 | 7001.9186 | 3383.175 |  | 75 | 0.43938 | 21.9688 | 3185.4714 | 1539.1506 |  |  | 75 | 0.17471 | 8.7356 | 1266.6641 | 612.0246
| 80 | 0.98336 | 49.168 | 7129.3665 | 3444.7551 |  | 80 | 0.50457 | 25.2286 | 3658.1424 | 1767.535 |  |  | 80 | 0.20788 | 10.3941 | 1507.1454 | 728.2199
| 85 | 0.99265 | 49.6325 | 7196.7096 | 3477.2938 |  | 85 | 0.56933 | 28.4667 | 4127.6674 | 1994.3992 |  |  | 85 | 0.24386 | 12.193 | 1767.9859 | 854.2524
| 90 | 0.99707 | 49.8534 | 7228.7415 | 3492.7709 |  | 90 | 0.63212 | 31.606 | 4582.8741 | 2214.3452 |  |  | 90 | 0.28238 | 14.119 | 2047.2603 | 989.1917
| 95 | 0.99895 | 49.9475 | 7242.3878 | 3499.3645 |  | 95 | 0.69152 | 34.576 | 5013.518 | 2422.423 |  |  | 95 | 0.32311 | 16.1556 | 2342.5552 | 1131.8718
| 100 | 0.99966 | 49.9832 | 7247.5679 | 3501.8674 |  | 100 | 0.74634 | 37.3168 | 5410.9312 | 2614.4444 |  |  | 100 | 0.36566 | 18.2829 | 2651.0164 | 1280.9135
|  | Avg. % over Threshold | Shift factor
|  | 0 | 20
|  | 0-2 | 15
|  | 3-5 | 10
|  | 6-8 | 5
|  | 9+ | 0
New PoF and CoF
Probability of Failure
| Functional Failure Category | K-Value | C-Value | Health Score Limit |  |  | Health Score to Derive Average PoF
| LV UGB | 7.7e-05 | 1.087 | 4 |  |  | HI1 | 4
| LV Circuit Breaker | 4.1e-05 | 1.087 | 4 |  |  | HI2 | 4.75
| LV Pillar (ID) | 4.6e-05 | 1.087 | 4 |  |  | HI3 | 6
| LV Pillar (OD at Substation) / LV Pillar (OD not at a Substation) | 4.6e-05 | 1.087 | 4 |  |  | HI4 | 7.25
| LV Board (WM) | 6.9e-05 | 1.087 | 4 |  |  | HI5 | 10
| HV Switchgear (GM) - Primary | 5.2e-05 | 1.087 | 4
| HV Switchgear (GM) - Distribution (GM) | 6.7e-05 | 1.087 | 4
| EHV Switchgear (GM) (33kV & 22kV assets only) | 0.000223 | 1.087 | 4
| EHV Switchgear (GM) (66kV assets only) | 0.000512 | 1.087 | 4
| 132kV CBs | 0.000431 | 1.087 | 4
| HV Transformer (GM) | 7.8e-05 | 1.087 | 4
| EHV Transformer/ 132kV Transformer | 0.000454 | 1.087 | 4
| Poles | 0.000285 | 1.087 | 4
| Towers | 0.000545 | 1.087 | 4
| Fittings | 9.6e-05 | 1.087 | 4
| OHL Conductor | 8e-05 | 1.087 | 4
| Pressurised Cable (EHV UG Cable (Oil) and 132kV UG Cable (Oil)) | 0.020944 | 1.087 | 4
| Pressurised Cable (EHV UG Cable (Gas) and 132kV UG Cable (Gas)) | 0.045036 | 1.087 | 4
| Submarine Cables | 0.000202 | 1.087 | 4
| Non Pressurised Cable | 0.000658 | 1.087 | 4
| PoF = K x [1 +(C x H) + ((C x H)^2) / 2) + ((C x H)^3) / 6)] | *Taken from DNO CNAIM v1.1
Consequence of failure
| Asset Register Category | Financial | Safety | Environmental | Network Performance | Total
| 6.6/11kV Poles | 1592 | 179 | 75 | 1297 | 3143
| 20kV Poles | 1910 | 179 | 75 | 1297 | 3461
| 33kV Pole | 2053 | 179 | 75 | 57 | 2364
| 33kV Tower | 5618 | 334 | 155 | 362 | 6469
| 33kV Fittings | 189 | 1336 | 80 | 167 | 1772
| 33kV OHL (Tower Line) Conductor | 14811 | 1336 | 80 | 833 | 17060
| 33kV UG Cable (Non Pressurised) | 26340 | 2 | 605 | 2572 | 29519
| 33kV UG Cable (Oil) | 108 | 2 | 4898 | 3 | 5011
| 33kV UG Cable (Gas) | 264 | 2 | 45 | 26 | 337
| 6.6/11kV CB (GM) Primary | 6315 | 20771 | 1141 | 9725 | 37952
| 6.6/11kV CB (GM) Secondary | 5792 | 4262 | 1108 | 7780 | 18942
| 6.6/11kV Switch (GM) | 4384 | 4262 | 1108 | 7780 | 17534
| 6.6/11kV RMU | 8190 | 4262 | 1108 | 7780 | 21340
| 6.6/11kV X-type RMU | 11083 | 4262 | 1108 | 7780 | 24233
| 20kV CB (GM) Primary | 7911 | 20771 | 1141 | 9725 | 39548
| 20kV CB (GM) Secondary | 6005 | 4262 | 1108 | 7780 | 19155
| 20kV Switch (GM) | 5081 | 4262 | 1108 | 7780 | 18231
| 20kV RMU | 8343 | 4262 | 1108 | 7780 | 21493
| 33kV CB (Air Insulated Busbars)(ID) (GM) | 12081 | 20771 | 2589 | 24248 | 59689
| 33kV CB (Air Insulated Busbars)(OD) (GM) | 14874 | 20771 | 2589 | 12274 | 50508
| 33kV CB (Gas Insulated Busbars)(ID) (GM) | 18299 | 20771 | 2589 | 24248 | 65907
| 33kV CB (Gas Insulated Busbars)(OD) (GM) | 18299 | 20771 | 2589 | 12274 | 53933
| 33kV Switch (GM) | 8537 | 20771 | 2589 | 12274 | 44171
| 33kV RMU | 21099 | 20771 | 2589 | 12274 | 56733
| 6.6/11kV Transformer (GM) | 7739 | 4262 | 3171 | 4862 | 20034
| 20kV Transformer (GM) | 8811 | 4262 | 3171 | 4862 | 21106
| 33kV Transformer (GM) | 73000 | 20771 | 14190 | 48197 | 156158
Load Factor = Actual Load At Risk Associated With The Failure Of The Asset Under Consideration / Maximum Demand Used to Derive Reference Network Performance Cost Of Failure
Network Performance Cost of Failure (CI CML) x load factor = Financial Impact of additional load
For example, if the Reference Network Performance Cost of Failure has been derived using a reference maximum demand of 12MVA, but for a specific asset the actual load at risk was 6MVA then a Load Factor of 0.5 would be applied.
Worked Example
Asset 1
| Number of Customers | 50 | #
| CML cost | 0.37667 | £
| CI cost | 15.4435 | £
| Asset Type K Value | 0.000285 | K
| C Value | 1.087 | C
| Health Score | 10 | H
| Time to restore(mins) | 145 | mins
| Asset Type | 6.6/11kV Transformer (GM) | Type
| Financial CoF | 7739 | £
| Safety CoF | 4262 | £
| Environmental CoF | 3171 | £
| Actual Load At Risk Associated With The Failure Of The Asset Under Consideration | 5 | MVA
| Maximum Demand Used to Derive Reference Network Performance Cost Of Failure | 2 | MVA
| Load Factor | 2.5 | Lf
| HI | P.O.F | CI | CML | CI CML Cost | Financial CoF | Safety CoF | Environmental CoF | Total CoF
| Year 1 | 0.5699% | 0.28497 | 41.3212 | 43.3123 | 44.1083 | 24.2912 | 18.0731 | 129.7849
| Year 2 | 0.632% | 0.31602 | 45.8227 | 48.0307 | 48.9134 | 26.9374 | 20.0419 | 143.9234
| Year 3 | 0.7021% | 0.35106 | 50.904 | 53.3568 | 54.3374 | 29.9245 | 22.2644 | 159.8832
| Year 4 | 0.7813% | 0.39066 | 56.6452 | 59.3747 | 60.4658 | 33.2996 | 24.7754 | 177.9155
| Year 5 | 0.8709% | 0.43543 | 63.1378 | 66.1801 | 67.3963 | 37.1163 | 27.6152 | 198.3079
| Year 6 | 0.9722% | 0.48611 | 70.4865 | 73.8829 | 75.2407 | 41.4363 | 30.8293 | 221.3893
| Year 7 | 1.087% | 0.54353 | 78.8112 | 82.6088 | 84.1269 | 46.3301 | 34.4704 | 247.5362
| Year 8 | 1.217% | 0.60862 | 88.2493 | 92.5016 | 94.2015 | 51.8784 | 38.5984 | 277.1799
| Year 9 | 1.365% | 0.68247 | 98.9578 | 103.7261 | 105.6324 | 58.1736 | 43.2821 | 310.8142
| Year 10 | 1.533% | 0.76633 | 111.1172 | 116.4714 | 118.6119 | 65.3216 | 48.6004 | 349.0053
Asset Register Category & Sub-division |  | Normal Expected Life
LV Poles | Concrete | 60
| Steel | 50
| Wood | 55
| Other (e.g. fibreglass) | 80
| LV Circuit Breaker | 60
| LV Pillar (ID) | 60
| LV Pillar (OD at Substation) | 60
| LV Pillar (OD not at a Substation) | 60
| LV Board (WM) | 60
| LV UGB | 55
| LV Board (X-type Network) (WM) | 60
6.6/11kV Poles | Concrete | 60
| Steel | 50
| Wood | 55
| Other (e.g. fibreglass) | 80
| 20kV Poles | 60
| Steel | 50
| Wood | 55
| Other (e.g. fibreglass) | 80
| HV Sub Cable | 60
| 6.6/11kV CB (GM) Primary | 55
| 6.6/11kV CB (GM) Secondary | 55
| 6.6/11kV Switch (GM) | 55
| 6.6/11kV RMU | 55
| 6.6/11kV X-type RMU | 55
| 20kV CB (GM) Primary | 55
| 20kV CB (GM) Secondary | 55
| 20kV Switch (GM) | 55
| 20kV RMU | 55
| 6.6/11kV Transformer (GM) | 60
| 20kV Transformer (GM) | 60
33kV Pole | 33kV Pole | 60
| Steel | 50
| Wood | 55
| Other (e.g. fibreglass) | 80
66kV Pole | Concrete | 60
| Steel | 50
| Wood | 55
| Other (e.g. fibreglass) | 80
33kV OHL (Tower Line) Conductor | ACSR - greased | 55
| ACSR - non-greased | 50
| AAAC | 60
| Cad Cu | 50
| Cu | 70
| Other | 50
33kV Tower | Steelwork | 80
| Foundation - Fully Encased Concrete | 95
| Foundation - Earth Grillage | 60
| Paint System - Galvanising | 30
| Paint System - Paint | 20
| 33kV Fittings | 40
66kV OHL (Tower Line) Conductor | ACSR - greased | 55
| ACSR - non-greased | 50
| AAAC | 60
| Cad Cu | 50
| Cu | 70
| Other | 50
66kV Tower | Steelwork | 80
| Foundation - Fully Encased Concrete | 95
| Foundation - Earth Grillage | 60
| Paint System - Galvanising | 30
| Paint System - Paint | 20
| 66kV Fittings | 40
33kV UG Cable (Non Pressurised) | Aluminium sheath - Aluminium conductor | 100
| Aluminium sheath - Copper conductor | 100
| Lead sheath - Aluminium conductor | 100
| Lead sheath - Copper conductor | 100
33kV UG Cable (Oil) | Aluminium sheath - Aluminium conductor | 75
| Aluminium sheath - Copper conductor | 75
| Lead sheath - Aluminium conductor | 80
| Lead sheath - Copper conductor | 80
33kV UG Cable (Gas) | Aluminium sheath - Aluminium conductor | 65
| Aluminium sheath - Copper conductor | 70
| Lead sheath - Aluminium conductor | 75
| Lead sheath - Copper conductor | 75
66kV UG Cable (Non Pressurised) | Aluminium sheath - Aluminium conductor | 100
| Aluminium sheath - Copper conductor | 100
| Lead sheath - Aluminium conductor | 100
| Lead sheath - Copper conductor | 100
66kV UG Cable (Oil) | Aluminium sheath - Aluminium conductor | 75
| Aluminium sheath - Copper conductor | 75
| Lead sheath - Aluminium conductor | 80
| Lead sheath - Copper conductor | 80
66kV UG Cable (Gas) | Aluminium sheath - Aluminium conductor | 65
| Aluminium sheath - Copper conductor | 70
| Lead sheath - Aluminium conductor | 75
| Lead sheath - Copper conductor | 75
| EHV Sub Cable | 60
| 33kV CB (Air Insulated Busbars)(ID) (GM) | 60
| 33kV CB (Air Insulated Busbars)(OD) (GM) | 50
| 33kV CB (Gas Insulated Busbars)(ID)(GM) | 60
| 33kV CB (Gas Insulated Busbars)(OD)(GM) | 50
| 33kV Switch (GM) | 55
| 33kV RMU | 55
| 66kV CB (Air Insulated Busbars)(ID) (GM) | 50
| 66kV CB (Air Insulated Busbars)(OD) (GM) | 55
| 66kV CB (Gas Insulated Busbars)(ID)(GM) | 55
| 66kV CB (Gas Insulated Busbars)(OD)(GM) | 50
33kV Transformer (GM) | Transformer - Pre 1980 | 60
| Transformer - Post 1980 | 50
| Tapchanger | 60
66kV Transformer (GM) | Transformer - Pre 1980 | 60
| Transformer - Post 1980 | 50
| Tapchanger | 60
132kV OHL (Tower Line) Conductor | ACSR - greased | 55
| ACSR - non-greased | 50
| AAAC | 60
| Cad Cu | 50
| Cu | 70
| Other | 50
132kV Tower | Steelwork | 80
| Foundation - Fully Encased Concrete | 95
| Foundation - Earth Grillage | 60
| Paint System - Galvanising | 30
| Paint System - Paint | 20
| 132kV Fittings | 40
132kV UG Cable (Non Pressurised) | Aluminium sheath - Aluminium conductor | 100
| Aluminium sheath - Copper conductor | 100
| Lead sheath - Aluminium conductor | 100
| Lead sheath - Copper conductor | 100
132kV UG Cable (Oil) | Aluminium sheath - Aluminium conductor | 75
| Aluminium sheath - Copper conductor | 75
| Lead sheath - Aluminium conductor | 80
| Lead sheath - Copper conductor | 80
132kV UG Cable (Gas) | Aluminium sheath - Aluminium conductor | 65
| Aluminium sheath - Copper conductor | 70
| Lead sheath - Aluminium conductor | 75
| Lead sheath - Copper conductor | 75
| 132kV Sub Cable | 60
| 132kV CB (Air Insulated Busbars)(ID) (GM) | 60
| 132kV CB (Air Insulated Busbars)(OD) (GM) | 50
| 132kV CB (Gas Insulated Busbars)(ID) (GM) | 60
| 132kV CB (Gas Insulated Busbars)(OD) (GM) | 55
132kV Transformer (GM) | Transformer - Pre 1980 | 60
| Transformer - Post 1980 | 50
| Tapchanger | 60
Age | Uncapped HI Score (normal expected life 20 years) | P.O.F | Uncapped HI Score (normal expected life 30 years) | P.O.F | Uncapped HI Score (normal expected life 40 years) | P.O.F | Uncapped HI Score (normal expected life 50 years) | P.O.F | Uncapped HI Score (normal expected life 55 years) | P.O.F | Uncapped HI Score (normal expected life 60 years) | P.O.F | Uncapped HI Score (normal expected life 65 years) | P.O.F | Uncapped HI Score (normal expected life 70 years) | P.O.F | Uncapped HI Score (normal expected life 75 years) | P.O.F | Uncapped HI Score (normal expected life 80 years) | P.O.F | Uncapped HI Score (normal expected life 95 years) | P.O.F | Uncapped HI Score (normal expected life 100 years) | P.O.F
0 | 0.5 | 0.04896% | 0.5 | 0.04896% | 0.5 | 0.04896% | 0.5 | 0.04896% | 0.5 | 0.04896% | 0.5 | 0.04896% | 0.5 | 0.04896% | 0.5 | 0.04896% | 0.5 | 0.04896% | 0.5 | 0.04896% | 0.5 | 0.04896% | 0.5 | 0.04896%
1 | 0.56369 | 0.05241% | 0.54161 | 0.05119% | 0.53089 | 0.05061% | 0.52456 | 0.05026% | 0.52228 | 0.05014% | 0.52039 | 0.05004% | 0.51879 | 0.04996% | 0.51742 | 0.04988% | 0.51624 | 0.04982% | 0.51521 | 0.04976% | 0.51278 | 0.04964% | 0.51213 | 0.0496%
2 | 0.63549 | 0.05655% | 0.58667 | 0.0537% | 0.56369 | 0.05241% | 0.55033 | 0.05167% | 0.54556 | 0.0514% | 0.54161 | 0.05119% | 0.53829 | 0.05101% | 0.53546 | 0.05085% | 0.53302 | 0.05072% | 0.53089 | 0.05061% | 0.52589 | 0.05034% | 0.52456 | 0.05026%
3 | 0.71644 | 0.06158% | 0.63549 | 0.05655% | 0.59851 | 0.05438% | 0.57737 | 0.05317% | 0.56987 | 0.05275% | 0.56369 | 0.05241% | 0.55851 | 0.05212% | 0.55412 | 0.05187% | 0.55033 | 0.05167% | 0.54704 | 0.05148% | 0.53933 | 0.05106% | 0.53729 | 0.05095%
4 | 0.8077 | 0.06772% | 0.68837 | 0.05979% | 0.63549 | 0.05655% | 0.60573 | 0.0548% | 0.59526 | 0.05419% | 0.58667 | 0.0537% | 0.5795 | 0.05329% | 0.57343 | 0.05295% | 0.56821 | 0.05266% | 0.56369 | 0.05241% | 0.55312 | 0.05182% | 0.55033 | 0.05167%
5 | 0.91058 | 0.07528% | 0.74565 | 0.06349% | 0.67475 | 0.05894% | 0.63549 | 0.05655% | 0.62179 | 0.05574% | 0.61059 | 0.05508% | 0.60128 | 0.05454% | 0.59341 | 0.05409% | 0.58667 | 0.0537% | 0.58084 | 0.05337% | 0.56726 | 0.0526% | 0.56369 | 0.05241%
6 | 1.0266 | 0.08465% | 0.8077 | 0.06772% | 0.71644 | 0.06158% | 0.66671 | 0.05845% | 0.6495 | 0.0574% | 0.63549 | 0.05655% | 0.62388 | 0.05586% | 0.61409 | 0.05529% | 0.60573 | 0.0548% | 0.59851 | 0.05438% | 0.58176 | 0.05342% | 0.57737 | 0.05317%
7 | 1.1573 | 0.09636% | 0.87491 | 0.07258% | 0.7607 | 0.06449% | 0.69946 | 0.06049% | 0.67844 | 0.05917% | 0.6614 | 0.05812% | 0.64732 | 0.05726% | 0.63549 | 0.05655% | 0.62541 | 0.05595% | 0.61673 | 0.05544% | 0.59663 | 0.05427% | 0.59138 | 0.05397%
8 | 1.3047 | 0.1111% | 0.94771 | 0.07817% | 0.8077 | 0.06772% | 0.73383 | 0.06271% | 0.70867 | 0.06108% | 0.68837 | 0.05979% | 0.67165 | 0.05875% | 0.65764 | 0.05789% | 0.64573 | 0.05717% | 0.63549 | 0.05655% | 0.61188 | 0.05516% | 0.60573 | 0.0548%
9 | 1.4709 | 0.1299% | 1.0266 | 0.08465% | 0.8576 | 0.0713% | 0.76988 | 0.06511% | 0.74025 | 0.06313% | 0.71644 | 0.06158% | 0.69689 | 0.06033% | 0.68056 | 0.0593% | 0.66671 | 0.05845% | 0.65483 | 0.05772% | 0.62752 | 0.05608% | 0.62043 | 0.05566%
10 | 1.6583 | 0.154% | 1.112 | 0.09216% | 0.91058 | 0.07528% | 0.8077 | 0.06772% | 0.77324 | 0.06534% | 0.74565 | 0.06349% | 0.72308 | 0.06201% | 0.70427 | 0.0608% | 0.68837 | 0.05979% | 0.67475 | 0.05894% | 0.64356 | 0.05704% | 0.63549 | 0.05655%
11 | 1.8695 | 0.1851% | 1.2045 | 0.1009% | 0.96684 | 0.0797% | 0.84738 | 0.07055% | 0.8077 | 0.06772% | 0.77605 | 0.06553% | 0.75025 | 0.0638% | 0.72882 | 0.06238% | 0.71073 | 0.06121% | 0.69528 | 0.06023% | 0.66001 | 0.05804% | 0.65091 | 0.05748%
12 | 2.1077 | 0.2257% | 1.3047 | 0.1111% | 1.0266 | 0.08465% | 0.88901 | 0.07363% | 0.84369 | 0.07029% | 0.8077 | 0.06772% | 0.77844 | 0.0657% | 0.75421 | 0.06406% | 0.73383 | 0.06271% | 0.71644 | 0.06158% | 0.67688 | 0.05908% | 0.66671 | 0.05845%
13 | 2.3762 | 0.279% | 1.4133 | 0.1231% | 1.09 | 0.09017% | 0.93268 | 0.07699% | 0.88129 | 0.07305% | 0.84063 | 0.07006% | 0.8077 | 0.06772% | 0.7805 | 0.06584% | 0.75767 | 0.06429% | 0.73824 | 0.063% | 0.69419 | 0.06016% | 0.68289 | 0.05945%
14 | 2.6788 | 0.3496% | 1.5309 | 0.1373% | 1.1573 | 0.09636% | 0.9785 | 0.08065% | 0.92056 | 0.07605% | 0.87491 | 0.07258% | 0.83805 | 0.06988% | 0.8077 | 0.06772% | 0.78228 | 0.06596% | 0.7607 | 0.06449% | 0.71193 | 0.06129% | 0.69946 | 0.06049%
15 | 3.0201 | 0.4437% | 1.6583 | 0.154% | 1.2288 | 0.1033% | 1.0266 | 0.08465% | 0.96158 | 0.07928% | 0.91058 | 0.07528% | 0.86954 | 0.07218% | 0.83584 | 0.06972% | 0.8077 | 0.06772% | 0.78385 | 0.06607% | 0.73013 | 0.06247% | 0.71644 | 0.06158%
16 | 3.4047 | 0.5699% | 1.7963 | 0.1738% | 1.3047 | 0.1111% | 1.077 | 0.08902% | 1.0044 | 0.08279% | 0.94771 | 0.07817% | 0.90222 | 0.07464% | 0.86497 | 0.07184% | 0.83394 | 0.06958% | 0.8077 | 0.06772% | 0.74879 | 0.0637% | 0.73383 | 0.06271%
17 | 3.8384 | 0.7405% | 1.9458 | 0.1975% | 1.3854 | 0.12% | 1.1299 | 0.0938% | 1.0492 | 0.08658% | 0.98635 | 0.08129% | 0.93613 | 0.07726% | 0.89512 | 0.0741% | 0.86103 | 0.07155% | 0.83227 | 0.06946% | 0.76794 | 0.06498% | 0.75163 | 0.06389%
18 | 4.3274 | 0.9722% | 2.1077 | 0.2257% | 1.4709 | 0.1299% | 1.1854 | 0.09905% | 1.0959 | 0.09071% | 1.0266 | 0.08465% | 0.97131 | 0.08007% | 0.92631 | 0.07649% | 0.88901 | 0.07363% | 0.8576 | 0.0713% | 0.78757 | 0.06632% | 0.76988 | 0.06511%
19 | 4.8786 | 1.289% | 2.2831 | 0.2596% | 1.5618 | 0.1412% | 1.2437 | 0.1048% | 1.1448 | 0.09518% | 1.0684 | 0.08826% | 1.0078 | 0.08307% | 0.95859 | 0.07904% | 0.91789 | 0.07584% | 0.88369 | 0.07323% | 0.8077 | 0.06772% | 0.78856 | 0.06639%
20 | 5.5 | 1.723% | 2.473 | 0.3004% | 1.6583 | 0.154% | 1.3047 | 0.1111% | 1.1958 | 0.1001% | 1.112 | 0.09216% | 1.0457 | 0.08628% | 0.992 | 0.08176% | 0.94771 | 0.07817% | 0.91058 | 0.07528% | 0.82834 | 0.06918% | 0.8077 | 0.06772%
21 | 6.2006 | 2.322% | 2.6788 | 0.3496% | 1.7608 | 0.1686% | 1.3688 | 0.1181% | 1.2491 | 0.1054% | 1.1573 | 0.09636% | 1.085 | 0.08972% | 1.0266 | 0.08465% | 0.9785 | 0.08065% | 0.93829 | 0.07743% | 0.84952 | 0.07071% | 0.8273 | 0.06911%
22 | 6.9904 | 3.152% | 2.9017 | 0.4092% | 1.8695 | 0.1851% | 1.4361 | 0.1258% | 1.3047 | 0.1111% | 1.2045 | 0.1009% | 1.1257 | 0.09342% | 1.0623 | 0.08773% | 1.0103 | 0.08327% | 0.96684 | 0.0797% | 0.87123 | 0.07231% | 0.84738 | 0.07055%
23 | 7.8808 | 4.304% | 3.1432 | 0.4817% | 1.985 | 0.2041% | 1.5066 | 0.1343% | 1.3629 | 0.1174% | 1.2536 | 0.1058% | 1.1681 | 0.09738% | 1.0994 | 0.09101% | 1.0431 | 0.08606% | 0.99625 | 0.08211% | 0.8935 | 0.07397% | 0.86794 | 0.07206%
24 | 8.8847 | 5.911% | 3.4047 | 0.5699% | 2.1077 | 0.2257% | 1.5807 | 0.1436% | 1.4236 | 0.1243% | 1.3047 | 0.1111% | 1.2119 | 0.1016% | 1.1377 | 0.09452% | 1.077 | 0.08902% | 1.0266 | 0.08465% | 0.91634 | 0.07572% | 0.88901 | 0.07363%
25 | 10.0164 | 8.159% | 3.6881 | 0.6778% | 2.2379 | 0.2505% | 1.6583 | 0.154% | 1.4871 | 0.1319% | 1.3579 | 0.1169% | 1.2575 | 0.1062% | 1.1773 | 0.09827% | 1.112 | 0.09216% | 1.0578 | 0.08733% | 0.93977 | 0.07755% | 0.91058 | 0.07528%
26 | 11.2923 | 11.31% | 3.9949 | 0.8099% | 2.3762 | 0.279% | 1.7398 | 0.1655% | 1.5533 | 0.1401% | 1.4133 | 0.1231% | 1.3047 | 0.1111% | 1.2184 | 0.1023% | 1.1481 | 0.0955% | 1.09 | 0.09017% | 0.96379 | 0.07946% | 0.93268 | 0.07699%
27 | 12.7306 | 15.74% | 4.3274 | 0.9722% | 2.523 | 0.3118% | 1.8252 | 0.1782% | 1.6226 | 0.1492% | 1.4709 | 0.1299% | 1.3538 | 0.1164% | 1.2608 | 0.1066% | 1.1854 | 0.09905% | 1.1232 | 0.09318% | 0.98843 | 0.08146% | 0.95531 | 0.07878%
28 | 14.3522 | 21.98% | 4.6874 | 1.172% | 2.6788 | 0.3496% | 1.9149 | 0.1924% | 1.6949 | 0.1591% | 1.5309 | 0.1373% | 1.4047 | 0.1221% | 1.3047 | 0.1111% | 1.2239 | 0.1028% | 1.1573 | 0.09636% | 1.0137 | 0.08356% | 0.9785 | 0.08065%
29 | 16.1804 | 30.78% | 5.0775 | 1.418% | 2.8443 | 0.3932% | 2.009 | 0.2082% | 1.7704 | 0.17% | 1.5933 | 0.1453% | 1.4574 | 0.1283% | 1.3502 | 0.116% | 1.2637 | 0.1068% | 1.1925 | 0.09974% | 1.0396 | 0.08576% | 1.0022 | 0.0826%
30 | 18.2414 | 43.23% | 5.5 | 1.723% | 3.0201 | 0.4437% | 2.1077 | 0.2257% | 1.8493 | 0.182% | 1.6583 | 0.154% | 1.5122 | 0.1349% | 1.3973 | 0.1213% | 1.3047 | 0.1111% | 1.2288 | 0.1033% | 1.0662 | 0.08806% | 1.0266 | 0.08465%
31 | 20.565 | 60.85% | 5.9577 | 2.101% | 3.2066 | 0.5021% | 2.2112 | 0.2453% | 1.9317 | 0.1951% | 1.7259 | 0.1635% | 1.569 | 0.1421% | 1.446 | 0.1269% | 1.3471 | 0.1157% | 1.2662 | 0.1071% | 1.0934 | 0.09048% | 1.0515 | 0.08678%
32 | 23.1845 | 85.83% | 6.4534 | 2.569% | 3.4047 | 0.5699% | 2.3199 | 0.2671% | 2.0178 | 0.2097% | 1.7963 | 0.1738% | 1.628 | 0.1499% | 1.4964 | 0.133% | 1.3909 | 0.1206% | 1.3047 | 0.1111% | 1.1214 | 0.09302% | 1.077 | 0.08902%
33 | 26.1377 | 121.3% | 6.9904 | 3.152% | 3.6151 | 0.6488% | 2.4338 | 0.2916% | 2.1077 | 0.2257% | 1.8695 | 0.1851% | 1.6892 | 0.1583% | 1.5485 | 0.1395% | 1.4361 | 0.1258% | 1.3444 | 0.1154% | 1.1501 | 0.09568% | 1.1031 | 0.09135%
34 | 29.4671 | 171.7% | 7.5721 | 3.877% | 3.8384 | 0.7405% | 2.5534 | 0.3189% | 2.2016 | 0.2434% | 1.9458 | 0.1975% | 1.7527 | 0.1674% | 1.6025 | 0.1465% | 1.4828 | 0.1313% | 1.3854 | 0.12% | 1.1794 | 0.09847% | 1.1299 | 0.0938%
35 | 33.2206 | 243.3% | 8.2022 | 4.782% | 4.0756 | 0.8474% | 2.6788 | 0.3496% | 2.2997 | 0.263% | 2.0251 | 0.211% | 1.8185 | 0.1772% | 1.6583 | 0.154% | 1.5309 | 0.1373% | 1.4275 | 0.1248% | 1.2096 | 0.1014% | 1.1573 | 0.09636%
36 | 37.4522 | 345.3% | 8.8847 | 5.911% | 4.3274 | 0.9722% | 2.8104 | 0.384% | 2.4022 | 0.2846% | 2.1077 | 0.2257% | 1.8869 | 0.1879% | 1.7161 | 0.1621% | 1.5807 | 0.1436% | 1.4709 | 0.1299% | 1.2405 | 0.1045% | 1.1854 | 0.09905%
37 | 42.2227 | 490.6% | 9.624 | 7.324% | 4.5947 | 1.118% | 2.9485 | 0.4226% | 2.5092 | 0.3086% | 2.1936 | 0.2419% | 1.9578 | 0.1995% | 1.7759 | 0.1708% | 1.632 | 0.1504% | 1.5157 | 0.1354% | 1.2722 | 0.1077% | 1.2142 | 0.1019%
38 | 47.601 | 697.7% | 10.4248 | 9.093% | 4.8786 | 1.289% | 3.0933 | 0.466% | 2.6211 | 0.3352% | 2.2831 | 0.2596% | 2.0313 | 0.212% | 1.8378 | 0.1802% | 1.685 | 0.1577% | 1.5618 | 0.1412% | 1.3047 | 0.1111% | 1.2437 | 0.1048%
39 | 53.6643 | 993% | 11.2923 | 11.31% | 5.18 | 1.489% | 3.2453 | 0.5149% | 2.7379 | 0.3647% | 2.3762 | 0.279% | 2.1077 | 0.2257% | 1.9018 | 0.1903% | 1.7398 | 0.1655% | 1.6093 | 0.1474% | 1.3381 | 0.1147% | 1.2738 | 0.1079%
40 | 60.5 | 1415% | 12.2319 | 14.09% | 5.5 | 1.723% | 3.4047 | 0.5699% | 2.8599 | 0.3975% | 2.473 | 0.3004% | 2.1869 | 0.2406% | 1.9681 | 0.2012% | 1.7963 | 0.1738% | 1.6583 | 0.154% | 1.3723 | 0.1185% | 1.3047 | 0.1111%
41 | 68.2064 | 2016% | 13.2497 | 17.59% | 5.8398 | 1.999% | 3.572 | 0.632% | 2.9873 | 0.4339% | 2.5739 | 0.3238% | 2.2691 | 0.2568% | 2.0367 | 0.213% | 1.8547 | 0.1828% | 1.7088 | 0.161% | 1.4074 | 0.1225% | 1.3364 | 0.1145%
42 | 76.8944 | 2876% | 14.3522 | 21.98% | 6.2006 | 2.322% | 3.7475 | 0.7021% | 3.1204 | 0.4745% | 2.6788 | 0.3496% | 2.3543 | 0.2744% | 2.1077 | 0.2257% | 1.9149 | 0.1924% | 1.7608 | 0.1686% | 1.4434 | 0.1266% | 1.3688 | 0.1181%
43 | 86.6891 | 4104% | 15.5465 | 27.5% | 6.5837 | 2.703% | 3.9316 | 0.7813% | 3.2595 | 0.5196% | 2.7881 | 0.378% | 2.4428 | 0.2936% | 2.1811 | 0.2395% | 1.9771 | 0.2027% | 1.8143 | 0.1766% | 1.4803 | 0.131% | 1.4021 | 0.1218%
44 | 97.7314 | 5859% | 16.8401 | 34.46% | 6.9904 | 3.152% | 4.1247 | 0.8709% | 3.4047 | 0.5699% | 2.9017 | 0.4092% | 2.5346 | 0.3145% | 2.2571 | 0.2544% | 2.0414 | 0.2138% | 1.8695 | 0.1851% | 1.5181 | 0.1357% | 1.4361 | 0.1258%
45 | 110.1802 | 8368% | 18.2414 | 43.23% | 7.4223 | 3.681% | 4.3274 | 0.9722% | 3.5565 | 0.6261% | 3.0201 | 0.4437% | 2.6299 | 0.3374% | 2.3358 | 0.2705% | 2.1077 | 0.2257% | 1.9264 | 0.1943% | 1.5569 | 0.1406% | 1.4709 | 0.1299%
46 | 124.2148 | 11956% | 19.7593 | 54.28% | 7.8808 | 4.304% | 4.54 | 1.087% | 3.715 | 0.6887% | 3.1432 | 0.4817% | 2.7287 | 0.3624% | 2.4172 | 0.2879% | 2.1762 | 0.2385% | 1.985 | 0.2041% | 1.5967 | 0.1457% | 1.5066 | 0.1343%
47 | 140.037 | 17088% | 21.4035 | 68.22% | 8.3677 | 5.041% | 4.763 | 1.217% | 3.8805 | 0.7587% | 3.2714 | 0.5236% | 2.8312 | 0.3896% | 2.5014 | 0.3068% | 2.2469 | 0.2523% | 2.0454 | 0.2145% | 1.6375 | 0.1512% | 1.5432 | 0.1388%
48 | 157.8747 | 24431% | 23.1845 | 85.83% | 8.8847 | 5.911% | 4.997 | 1.365% | 4.0534 | 0.837% | 3.4047 | 0.5699% | 2.9376 | 0.4195% | 2.5886 | 0.3273% | 2.3199 | 0.2671% | 2.1077 | 0.2257% | 1.6794 | 0.1569% | 1.5807 | 0.1436%
49 | 177.9845 | 34937% | 25.1137 | 108.1% | 9.4336 | 6.941% | 5.2425 | 1.533% | 4.2341 | 0.9246% | 3.5436 | 0.6212% | 3.048 | 0.4521% | 2.6788 | 0.3496% | 2.3952 | 0.2831% | 2.1718 | 0.2377% | 1.7223 | 0.163% | 1.619 | 0.1487%
50 | 200.6558 | 49972% | 27.2035 | 136.1% | 10.0164 | 8.159% | 5.5 | 1.723% | 4.4227 | 1.023% | 3.6881 | 0.6778% | 3.1626 | 0.4879% | 2.7722 | 0.3737% | 2.473 | 0.3004% | 2.2379 | 0.2505% | 1.7663 | 0.1694% | 1.6583 | 0.154%
51 | 226.215 | 71492% | 29.4671 | 171.7% | 10.6352 | 9.601% | 5.7702 | 1.94% | 4.6198 | 1.133% | 3.8384 | 0.7405% | 3.2814 | 0.527% | 2.8688 | 0.4% | 2.5534 | 0.3189% | 2.306 | 0.2643% | 1.8115 | 0.1761% | 1.6986 | 0.1596%
52 | 255.0298 | 102297% | 31.9191 | 216.6% | 11.2923 | 11.31% | 6.0537 | 2.187% | 4.8257 | 1.256% | 3.9949 | 0.8099% | 3.4047 | 0.5699% | 2.9688 | 0.4285% | 2.6363 | 0.339% | 2.3762 | 0.279% | 1.8578 | 0.1833% | 1.7398 | 0.1655%
53 | 287.5151 | 146399% | 34.5751 | 273.4% | 11.9899 | 13.34% | 6.3511 | 2.467% | 5.0407 | 1.394% | 4.1578 | 0.8869% | 3.5327 | 0.617% | 3.0722 | 0.4595% | 2.722 | 0.3606% | 2.4485 | 0.2948% | 1.9053 | 0.1908% | 1.782 | 0.1717%
54 | 324.1382 | 209544% | 37.4522 | 345.3% | 12.7306 | 15.74% | 6.6631 | 2.787% | 5.2654 | 1.549% | 4.3274 | 0.9722% | 3.6654 | 0.6687% | 3.1793 | 0.4932% | 2.8104 | 0.384% | 2.523 | 0.3118% | 1.954 | 0.1988% | 1.8252 | 0.1782%
55 | 365.4264 | 299962% | 40.5686 | 436.3% | 13.5171 | 18.59% | 6.9904 | 3.152% | 5.5 | 1.723% | 4.5038 | 1.067% | 3.8032 | 0.7255% | 3.2901 | 0.53% | 2.9017 | 0.4092% | 2.5997 | 0.33% | 2.0039 | 0.2073% | 1.8695 | 0.1851%
56 | 411.9737 | 429441% | 43.9443 | 551.6% | 14.3522 | 21.98% | 7.3338 | 3.568% | 5.7451 | 1.919% | 4.6874 | 1.172% | 3.9461 | 0.7878% | 3.4047 | 0.5699% | 2.996 | 0.4365% | 2.6788 | 0.3496% | 2.0552 | 0.2162% | 1.9149 | 0.1924%
57 | 464.4502 | 614870% | 47.601 | 697.7% | 15.2389 | 26% | 7.6941 | 4.042% | 6.0011 | 2.139% | 4.8786 | 1.289% | 4.0944 | 0.8564% | 3.5234 | 0.6135% | 3.0933 | 0.466% | 2.7603 | 0.3706% | 2.1077 | 0.2257% | 1.9614 | 0.2001%
58 | 523.611 | 880440% | 51.5619 | 882.7% | 16.1804 | 30.78% | 8.0721 | 4.584% | 6.2685 | 2.387% | 5.0775 | 1.418% | 4.2483 | 0.9317% | 3.6462 | 0.661% | 3.1938 | 0.498% | 2.8443 | 0.3932% | 2.1616 | 0.2357% | 2.009 | 0.2082%
59 | 590.3077 | 1260810% | 55.8525 | 1117% | 17.18 | 36.47% | 8.4686 | 5.204% | 6.5479 | 2.666% | 5.2845 | 1.563% | 4.4079 | 1.015% | 3.7732 | 0.7129% | 3.2976 | 0.5325% | 2.9309 | 0.4175% | 2.2168 | 0.2464% | 2.0577 | 0.2167%
60 | 665.5 | 1805630% | 60.5 | 1415% | 18.2414 | 43.23% | 8.8847 | 5.911% | 6.8397 | 2.98% | 5.5 | 1.723% | 4.5736 | 1.106% | 3.9047 | 0.7694% | 3.4047 | 0.5699% | 3.0201 | 0.4437% | 2.2735 | 0.2576% | 2.1077 | 0.2257%
61 | 750.2702 | 2586032% | 65.5343 | 1791% | 19.3684 | 51.27% | 9.3211 | 6.721% | 7.1445 | 3.334% | 5.7243 | 1.902% | 4.7454 | 1.207% | 4.0408 | 0.8311% | 3.5154 | 0.6105% | 3.1119 | 0.4718% | 2.3316 | 0.2696% | 2.1588 | 0.2352%
62 | 845.8383 | 3703924% | 70.9874 | 2269% | 20.565 | 60.85% | 9.7791 | 7.647% | 7.4628 | 3.733% | 5.9577 | 2.101% | 4.9238 | 1.317% | 4.1816 | 0.8986% | 3.6296 | 0.6545% | 3.2066 | 0.5021% | 2.3912 | 0.2823% | 2.2112 | 0.2453%
63 | 953.5796 | 5305309% | 76.8944 | 2876% | 21.8355 | 72.25% | 10.2595 | 8.707% | 7.7954 | 4.183% | 6.2006 | 2.322% | 5.1088 | 1.44% | 4.3274 | 0.9722% | 3.7475 | 0.7021% | 3.3042 | 0.5348% | 2.4523 | 0.2957% | 2.2649 | 0.2559%
64 | 1075.0449 | 7599367% | 83.2929 | 3645% | 23.1845 | 85.83% | 10.7635 | 9.92% | 8.1428 | 4.691% | 6.4534 | 2.569% | 5.3008 | 1.574% | 4.4782 | 1.053% | 3.8692 | 0.7538% | 3.4047 | 0.5699% | 2.515 | 0.31% | 2.3199 | 0.2671%
65 | 1211.9822 | 10885798% | 90.2237 | 4621% | 24.6169 | 102% | 11.2923 | 11.31% | 8.5056 | 5.264% | 6.7165 | 2.845% | 5.5 | 1.723% | 4.6342 | 1.141% | 3.9949 | 0.8099% | 3.5083 | 0.6079% | 2.5793 | 0.3251% | 2.3762 | 0.279%
66 | 1366.3623 | 15593994% | 97.7314 | 5859% | 26.1377 | 121.3% | 11.847 | 12.9% | 8.8847 | 5.911% | 6.9904 | 3.152% | 5.7067 | 1.887% | 4.7957 | 1.237% | 4.1247 | 0.8709% | 3.6151 | 0.6488% | 2.6452 | 0.3412% | 2.4338 | 0.2916%
67 | 1540.4071 | 22339173% | 105.8637 | 7430% | 27.7525 | 144.3% | 12.429 | 14.73% | 9.2806 | 6.643% | 7.2754 | 3.495% | 5.9211 | 2.069% | 4.9629 | 1.343% | 4.2587 | 0.937% | 3.7251 | 0.6929% | 2.7129 | 0.3583% | 2.4929 | 0.3049%
68 | 1736.6213 | 32002803% | 114.6727 | 9424% | 29.4671 | 171.7% | 13.0396 | 16.82% | 9.6942 | 7.469% | 7.5721 | 3.877% | 6.1437 | 2.269% | 5.1358 | 1.458% | 4.3971 | 1.009% | 3.8384 | 0.7405% | 2.7822 | 0.3764% | 2.5534 | 0.3189%
69 | 1957.829 | 45847842% | 124.2148 | 11956% | 31.2876 | 204.3% | 13.6802 | 19.22% | 10.1262 | 8.403% | 7.8808 | 4.304% | 6.3745 | 2.49% | 5.3148 | 1.585% | 4.54 | 1.087% | 3.9552 | 0.7919% | 2.8533 | 0.3957% | 2.6154 | 0.3338%
70 | 2207.2138 | 65683850% | 134.5508 | 15170% | 33.2206 | 243.3% | 14.3522 | 21.98% | 10.5774 | 9.46% | 8.2022 | 4.782% | 6.6141 | 2.735% | 5.5 | 1.723% | 4.6874 | 1.172% | 4.0756 | 0.8474% | 2.9263 | 0.4162% | 2.6788 | 0.3496%
71 | 2488.3647 | 94103575% | 145.7469 | 19250% | 35.273 | 289.8% | 15.0573 | 25.14% | 11.0488 | 10.65% | 8.5366 | 5.315% | 6.8626 | 3.006% | 5.6917 | 1.875% | 4.8397 | 1.264% | 4.1996 | 0.9074% | 3.0011 | 0.438% | 2.7438 | 0.3663%
72 | 2805.3282 | 134821944% | 157.8747 | 24431% | 37.4522 | 345.3% | 15.797 | 28.77% | 11.5411 | 12.01% | 8.8847 | 5.911% | 7.1205 | 3.305% | 5.89 | 2.042% | 4.997 | 1.365% | 4.3274 | 0.9722% | 3.0778 | 0.4612% | 2.8104 | 0.384%
73 | 3162.6658 | 193161780% | 171.0116 | 31009% | 39.766 | 411.5% | 16.5731 | 32.94% | 12.0554 | 13.54% | 9.2469 | 6.578% | 7.3881 | 3.637% | 6.0953 | 2.224% | 5.1593 | 1.474% | 4.459 | 1.042% | 3.1564 | 0.4859% | 2.8786 | 0.4027%
74 | 3565.5205 | 276749770% | 185.2416 | 39363% | 42.2227 | 490.6% | 17.3873 | 37.73% | 12.5926 | 15.27% | 9.624 | 7.324% | 7.6658 | 4.004% | 6.3077 | 2.425% | 5.3269 | 1.593% | 4.5947 | 1.118% | 3.2371 | 0.5122% | 2.9485 | 0.4226%
75 | 4019.6901 | 396513685% | 200.6558 | 49972% | 44.8313 | 585% | 18.2414 | 43.23% | 13.1538 | 17.23% | 10.0164 | 8.159% | 7.9538 | 4.41% | 6.5275 | 2.645% | 5.5 | 1.723% | 4.7345 | 1.2% | 3.3199 | 0.5402% | 3.0201 | 0.4437%
76 | 4531.711 | 568111245% | 217.3526 | 63446% | 47.601 | 697.7% | 19.1376 | 49.55% | 13.74 | 19.46% | 10.4248 | 9.093% | 8.2527 | 4.86% | 6.755 | 2.886% | 5.6787 | 1.865% | 4.8786 | 1.289% | 3.4047 | 0.5699% | 3.0933 | 0.466%
77 | 5108.9522 | 813977496% | 235.4387 | 80559% | 50.5418 | 832.3% | 20.0777 | 56.82% | 14.3522 | 21.98% | 10.8499 | 10.14% | 8.5629 | 5.359% | 6.9904 | 3.152% | 5.8632 | 2.019% | 5.027 | 1.385% | 3.4918 | 0.6017% | 3.1684 | 0.4897%
78 | 5759.7214 | 1166258411% | 255.0298 | 102297% | 53.6643 | 993% | 21.0641 | 65.17% | 14.9918 | 24.83% | 11.2923 | 11.31% | 8.8847 | 5.911% | 7.234 | 3.443% | 6.0537 | 2.187% | 5.18 | 1.489% | 3.581 | 0.6355% | 3.2453 | 0.5149%
79 | 6493.3844 | 1671014336% | 276.2511 | 129909% | 56.9798 | 1185% | 22.0989 | 74.78% | 15.6599 | 28.07% | 11.7527 | 12.62% | 9.2186 | 6.524% | 7.4861 | 3.763% | 6.2503 | 2.37% | 5.3376 | 1.601% | 3.6726 | 0.6716% | 3.3241 | 0.5416%
80 | 7320.5 | 2394242963% | 299.2383 | 164985% | 60.5 | 1415% | 23.1845 | 85.83% | 16.3577 | 31.74% | 12.2319 | 14.09% | 9.565 | 7.204% | 7.747 | 4.115% | 6.4534 | 2.569% | 5.5 | 1.723% | 3.7665 | 0.71% | 3.4047 | 0.5699%
81 | 8252.9721 | 3430509456% | 324.1382 | 209544% | 64.2377 | 1689% | 24.3235 | 98.54% | 17.0867 | 35.91% | 12.7306 | 15.74% | 9.9244 | 7.958% | 8.017 | 4.503% | 6.6631 | 2.787% | 5.6674 | 1.855% | 3.8627 | 0.751% | 3.4874 | 0.6001%
82 | 9304.2209 | 4915312255% | 351.1101 | 266152% | 68.2064 | 2016% | 25.5184 | 113.2% | 17.8481 | 40.63% | 13.2497 | 17.59% | 10.2974 | 8.794% | 8.2964 | 4.928% | 6.8795 | 3.025% | 5.8398 | 1.999% | 3.9615 | 0.7947% | 3.572 | 0.632%
83 | 10489.3759 | 7042801671% | 380.3264 | 338070% | 72.4202 | 2408% | 26.7721 | 130% | 18.6434 | 45.99% | 13.79 | 19.66% | 10.6844 | 9.723% | 8.5855 | 5.396% | 7.103 | 3.284% | 6.0175 | 2.154% | 4.0627 | 0.8414% | 3.6587 | 0.666%
84 | 11825.4937 | 10091168303% | 411.9737 | 429441% | 76.8944 | 2876% | 28.0873 | 149.4% | 19.4742 | 52.07% | 14.3522 | 21.98% | 11.0859 | 10.75% | 8.8847 | 5.911% | 7.3338 | 3.568% | 6.2006 | 2.322% | 4.1666 | 0.8912% | 3.7475 | 0.7021%
85 | 13331.8039 | 14459021365% | 446.2545 | 545530% | 81.645 | 3435% | 29.4671 | 171.7% | 20.3421 | 58.98% | 14.9374 | 24.58% | 11.5025 | 11.9% | 9.1943 | 6.478% | 7.5721 | 3.877% | 6.3892 | 2.505% | 4.2731 | 0.9443% | 3.8384 | 0.7405%
86 | 15029.9851 | 20717514117% | 483.3878 | 693029% | 86.6891 | 4104% | 30.9147 | 197.3% | 21.2486 | 66.82% | 15.5465 | 27.5% | 11.9347 | 13.17% | 9.5147 | 7.102% | 7.8181 | 4.215% | 6.5837 | 2.703% | 4.3823 | 1.001% | 3.9316 | 0.7813%
87 | 16944.4776 | 29685032950% | 523.611 | 880440% | 92.0448 | 4903% | 32.4335 | 226.9% | 22.1954 | 75.72% | 16.1804 | 30.78% | 12.3832 | 14.58% | 9.8463 | 7.79% | 8.0721 | 4.584% | 6.784 | 2.918% | 4.4943 | 1.062% | 4.027 | 0.8247%
88 | 19102.8348 | 42534217288% | 567.1813 | 1118569% | 97.7314 | 5859% | 34.0268 | 260.9% | 23.1845 | 85.83% | 16.8401 | 34.46% | 12.8486 | 16.15% | 10.1894 | 8.546% | 8.3343 | 4.988% | 6.9904 | 3.152% | 4.6092 | 1.126% | 4.1247 | 0.8709%
89 | 21536.1195 | 60945305519% | 614.377 | 1421149% | 103.7693 | 7001% | 35.6984 | 300.1% | 24.2177 | 97.31% | 17.5268 | 38.59% | 13.3314 | 17.89% | 10.5445 | 9.38% | 8.6051 | 5.429% | 7.2031 | 3.405% | 4.7271 | 1.196% | 4.2248 | 0.92%
90 | 24279.3518 | 87325860277% | 665.5 | 1805630% | 110.1802 | 8368% | 37.4522 | 345.3% | 25.2969 | 110.3% | 18.2414 | 43.23% | 13.8324 | 19.83% | 10.912 | 10.3% | 8.8847 | 5.911% | 7.4223 | 3.681% | 4.8479 | 1.269% | 4.3274 | 0.9722%
91 | 27372.012 | 1251256070.4574 | 720.877 | 2294190% | 116.9872 | 10002% | 39.2921 | 397.3% | 26.4242 | 125.2% | 18.9852 | 48.43% | 14.3522 | 21.98% | 11.2923 | 11.31% | 9.1733 | 6.439% | 7.6481 | 3.98% | 4.9718 | 1.348% | 4.4324 | 1.028%
92 | 30858.6097 | 1792875582.3274 | 780.8619 | 2915015% | 124.2148 | 11956% | 41.2223 | 457.3% | 27.6017 | 142% | 19.7593 | 54.28% | 14.8916 | 24.37% | 11.6858 | 12.43% | 9.4713 | 7.016% | 7.8808 | 4.304% | 5.0989 | 1.433% | 4.54 | 1.087%
93 | 34789.324 | 2568944173.2452 | 845.8383 | 3703924% | 131.8888 | 14293% | 43.2474 | 526.3% | 28.8317 | 161.1% | 20.565 | 60.85% | 15.4512 | 27.03% | 12.093 | 13.65% | 9.7791 | 7.647% | 8.1206 | 4.657% | 5.2292 | 1.523% | 4.6501 | 1.15%
94 | 39220.7256 | 3680947950.6415 | 916.2214 | 4706438% | 140.037 | 17088% | 45.372 | 605.9% | 30.1165 | 182.9% | 21.4035 | 68.22% | 16.0319 | 29.99% | 12.5144 | 15.01% | 10.0968 | 8.337% | 8.3677 | 5.041% | 5.3629 | 1.62% | 4.763 | 1.217%
95 | 44216.5912 | 5274303614.323 | 992.4611 | 5980411% | 148.6886 | 20432% | 47.601 | 697.7% | 31.4586 | 207.6% | 22.2762 | 76.51% | 16.6343 | 33.28% | 12.9506 | 16.5% | 10.4248 | 9.093% | 8.6223 | 5.458% | 5.5 | 1.723% | 4.8786 | 1.289%
96 | 49848.8212 | 7557374888.1054 | 1075.0449 | 7599367% | 157.8747 | 24431% | 49.9395 | 803.4% | 32.8605 | 235.7% | 23.1845 | 85.83% | 17.2594 | 36.95% | 13.4019 | 18.15% | 10.7635 | 9.92% | 8.8847 | 5.911% | 5.6406 | 1.834% | 4.997 | 1.365%
97 | 56198.4746 | 10828720696.9251 | 1164.5005 | 9656750% | 167.6283 | 29214% | 52.3928 | 925.3% | 34.3248 | 267.7% | 24.1299 | 96.29% | 17.9081 | 41.02% | 13.8689 | 19.97% | 11.1132 | 10.83% | 9.155 | 6.405% | 5.7848 | 1.952% | 5.1182 | 1.446%
98 | 63356.9353 | 15516138414.3938 | 1261.3999 | 12271316% | 177.9845 | 34937% | 54.9667 | 1066% | 35.8544 | 304% | 25.1137 | 108.1% | 18.581 | 45.55% | 14.3522 | 21.98% | 11.4742 | 11.82% | 9.4336 | 6.941% | 5.9327 | 2.079% | 5.2425 | 1.533%
99 | 71427.228 | 22232607984.8813 | 1366.3623 | 15593994% | 188.9805 | 41782% | 57.667 | 1228% | 37.4522 | 345.3% | 26.1377 | 121.3% | 19.2793 | 50.6% | 14.8524 | 24.19% | 11.847 | 12.9% | 9.7206 | 7.524% | 6.0843 | 2.214% | 5.3697 | 1.625%
100 | 80525.5 | 31856452906.4344 | 1480.0588 | 19816602% | 200.6558 | 49972% | 60.5 | 1415% | 39.1211 | 392.3% | 27.2035 | 136.1% | 20.0038 | 56.22% | 15.37 | 26.63% | 12.2319 | 14.09% | 10.0164 | 8.159% | 6.2398 | 2.36% | 5.5 | 1.723%
Today | year 0 | [6 empty] | Notes
current HS1 | 0.69946 | age reduction factor1 | 1 |  |  |  |  | For case 1 I got the same results that you (HS and POF) because r=1
current HS2 | 6.3511 | age reduction factor2 | 1.5 |  |  |  |  | For case 2 the results differ because r=1.5
Hnew | 0.5
age1 | 7
age2 | 53
year | future HS1 | Beta2 1 | POF1 | future HS2 | Beta2 2 | POF2
0 | 0.69946 | 0.047958 | 0.06049% | 6.3511 | 0.047958 | 2.467%
1 | 0.73383 | 0.047958 | 0.06271% | 6.5574 | 0.047958 | 2.676%
2 | 0.76988 | 0.047958 | 0.06511% | 6.7704 | 0.047958 | 2.903%
3 | 0.8077 | 0.047958 | 0.06772% | 6.9904 | 0.047958 | 3.152%
4 | 0.84738 | 0.047958 | 0.07055% | 7.2175 | 0.047958 | 3.423%
5 | 0.88901 | 0.047958 | 0.07363% | 7.452 | 0.047958 | 3.719%
6 | 0.93268 | 0.047958 | 0.07699% | 7.6941 | 0.047958 | 4.042%
7 | 0.9785 | 0.047958 | 0.08065% | 7.9441 | 0.047958 | 4.396%
8 | 1.0266 | 0.047958 | 0.08465% | 8.2022 | 0.047958 | 4.782%
9 | 1.077 | 0.047958 | 0.08902% | 8.4686 | 0.047958 | 5.204%
10 | 1.1299 | 0.047958 | 0.0938% | 8.7438 | 0.047958 | 5.665%
11 | 1.1854 | 0.047958 | 0.09905% | 9.0278 | 0.047958 | 6.169%
12 | 1.2437 | 0.047958 | 0.1048% | 9.3211 | 0.047958 | 6.721%
13 | 1.3047 | 0.047958 | 0.1111% | 9.624 | 0.047958 | 7.324%
14 | 1.3688 | 0.047958 | 0.1181% | 9.9366 | 0.047958 | 7.984%
15 | 1.4361 | 0.047958 | 0.1258% | 10.2595 | 0.047958 | 8.707%
16 | 1.5066 | 0.047958 | 0.1343% | 10.5928 | 0.047958 | 9.497% |  | year | initial expected HS | with ageing factor (1) HS | with ageing factor (1.5) HS | POF (yours) | POF1 | POF2
17 | 1.5807 | 0.047958 | 0.1436% | 10.9369 | 0.047958 | 10.36% |  | 0 | 0.5 |  |  | 0.04896%
18 | 1.6583 | 0.047958 | 0.154% | 11.2923 | 0.047958 | 11.31% |  | 1 | 0.52456 |  |  | 0.05026%
19 | 1.7398 | 0.047958 | 0.1655% | 11.6591 | 0.047958 | 12.35% |  | 2 | 0.55033 |  |  | 0.05167%
20 | 1.8252 | 0.047958 | 0.1782% | 12.0379 | 0.047958 | 13.48% |  | 3 | 0.57737 |  |  | 0.05317%
21 | 1.9149 | 0.047958 | 0.1924% | 12.429 | 0.047958 | 14.73% |  | 4 | 0.60573 |  |  | 0.0548%
22 | 2.009 | 0.047958 | 0.2082% | 12.8328 | 0.047958 | 16.09% |  | 5 | 0.63549 |  |  | 0.05655%
23 | 2.1077 | 0.047958 | 0.2257% | 13.2497 | 0.047958 | 17.59% |  | 6 | 0.66671 |  |  | 0.05845%
24 | 2.2112 | 0.047958 | 0.2453% | 13.6802 | 0.047958 | 19.22% |  | 7 | 0.69946 | 0.69946 |  | 0.06049% | 0.06049%
25 | 2.3199 | 0.047958 | 0.2671% | 14.1246 | 0.047958 | 21.02% |  | 8 | 0.73383 | 0.73383 |  | 0.06271% | 0.06271%
26 | 2.4338 | 0.047958 | 0.2916% | 14.5835 | 0.047958 | 22.98% |  | 9 | 0.76988 | 0.76988 |  | 0.06511% | 0.06511%
27 | 2.5534 | 0.047958 | 0.3189% | 15 | 0.047958 | 24.87% |  | 10 | 0.8077 | 0.8077 |  | 0.06772% | 0.06772%
28 | 2.6788 | 0.047958 | 0.3496% | 15 | 0.047958 | 24.87% |  | 11 | 0.84738 | 0.84738 |  | 0.07055% | 0.07055%
29 | 2.8104 | 0.047958 | 0.384% | 15 | 0.047958 | 24.87% |  | 12 | 0.88901 | 0.88901 |  | 0.07363% | 0.07363%
30 | 2.9485 | 0.047958 | 0.4226% | 15 | 0.047958 | 24.87% |  | 13 | 0.93268 | 0.93268 |  | 0.07699% | 0.07699%
31 | 3.0933 | 0.047958 | 0.466% | 15 | 0.047958 | 24.87% |  | 14 | 0.9785 | 0.9785 |  | 0.08065% | 0.08065%
32 | 3.2453 | 0.047958 | 0.5149% | 15 | 0.047958 | 24.87% |  | 15 | 1.0266 | 1.0266 |  | 0.08465% | 0.08465%
33 | 3.4047 | 0.047958 | 0.5699% | 15 | 0.047958 | 24.87% |  | 16 | 1.077 | 1.077 |  | 0.08902% | 0.08902%
34 | 3.572 | 0.047958 | 0.632% | 15 | 0.047958 | 24.87% |  | 17 | 1.1299 | 1.1299 |  | 0.0938% | 0.0938%
35 | 3.7475 | 0.047958 | 0.7021% | 15 | 0.047958 | 24.87% |  | 18 | 1.1854 | 1.1854 |  | 0.09905% | 0.09905%
36 | 3.9316 | 0.047958 | 0.7813% | 15 | 0.047958 | 24.87% |  | 19 | 1.2437 | 1.2437 |  | 0.1048% | 0.1048%
37 | 4.1247 | 0.047958 | 0.8709% | 15 | 0.047958 | 24.87% |  | 20 | 1.3047 | 1.3047 |  | 0.1111% | 0.1111%
38 | 4.3274 | 0.047958 | 0.9722% | 15 | 0.047958 | 24.87% |  | 21 | 1.3688 | 1.3688 |  | 0.1181% | 0.1181%
39 | 4.54 | 0.047958 | 1.087% | 15 | 0.047958 | 24.87% |  | 22 | 1.4361 | 1.4361 |  | 0.1258% | 0.1258%
40 | 4.763 | 0.047958 | 1.217% | 15 | 0.047958 | 24.87% |  | 23 | 1.5066 | 1.5066 |  | 0.1343% | 0.1343%
41 | 4.997 | 0.047958 | 1.365% | 15 | 0.047958 | 24.87% |  | 24 | 1.5807 | 1.5807 |  | 0.1436% | 0.1436%
42 | 5.2425 | 0.047958 | 1.533% | 15 | 0.047958 | 24.87% |  | 25 | 1.6583 | 1.6583 |  | 0.154% | 0.154%
43 | 5.5 | 0.047958 | 1.723% | 15 | 0.047958 | 24.87% |  | 26 | 1.7398 | 1.7398 |  | 0.1655% | 0.1655%
44 | 5.7702 | 0.047958 | 1.94% | 15 | 0.047958 | 24.87% |  | 27 | 1.8252 | 1.8252 |  | 0.1782% | 0.1782%
45 | 6.0537 | 0.047958 | 2.187% | 15 | 0.047958 | 24.87% |  | 28 | 1.9149 | 1.9149 |  | 0.1924% | 0.1924%
46 | 6.3511 | 0.047958 | 2.467% | 15 | 0.047958 | 24.87% |  | 29 | 2.009 | 2.009 |  | 0.2082% | 0.2082%
47 | 6.6631 | 0.047958 | 2.787% | 15 | 0.047958 | 24.87% |  | 30 | 2.1077 | 2.1077 |  | 0.2257% | 0.2257%
48 | 6.9904 | 0.047958 | 3.152% | 15 | 0.047958 | 24.87% |  | 31 | 2.2112 | 2.2112 |  | 0.2453% | 0.2453%
49 | 7.3338 | 0.047958 | 3.568% | 15 | 0.047958 | 24.87% |  | 32 | 2.3199 | 2.3199 |  | 0.2671% | 0.2671%
50 | 7.6941 | 0.047958 | 4.042% | 15 | 0.047958 | 24.87% |  | 33 | 2.4338 | 2.4338 |  | 0.2916% | 0.2916%
51 | 8.0721 | 0.047958 | 4.584% | 15 | 0.047958 | 24.87% |  | 34 | 2.5534 | 2.5534 |  | 0.3189% | 0.3189%
52 | 8.4686 | 0.047958 | 5.204% | 15 | 0.047958 | 24.87% |  | 35 | 2.6788 | 2.6788 |  | 0.3496% | 0.3496%
53 | 8.8847 | 0.047958 | 5.911% | 15 | 0.047958 | 24.87% |  | 36 | 2.8104 | 2.8104 |  | 0.384% | 0.384%
54 | 9.3211 | 0.047958 | 6.721% | 15 | 0.047958 | 24.87% |  | 37 | 2.9485 | 2.9485 |  | 0.4226% | 0.4226%
55 | 9.7791 | 0.047958 | 7.647% | 15 | 0.047958 | 24.87% |  | 38 | 3.0933 | 3.0933 |  | 0.466% | 0.466%
56 | 10.2595 | 0.047958 | 8.707% | 15 | 0.047958 | 24.87% |  | 39 | 3.2453 | 3.2453 |  | 0.5149% | 0.5149%
57 | 10.7635 | 0.047958 | 9.92% | 15 | 0.047958 | 24.87% |  | 40 | 3.4047 | 3.4047 |  | 0.5699% | 0.5699%
58 | 11.2923 | 0.047958 | 11.31% | 15 | 0.047958 | 24.87% |  | 41 | 3.572 | 3.572 |  | 0.632% | 0.632%
59 | 11.847 | 0.047958 | 12.9% | 15 | 0.047958 | 24.87% |  | 42 | 3.7475 | 3.7475 |  | 0.7021% | 0.7021%
60 | 12.429 | 0.047958 | 14.73% | 15 | 0.047958 | 24.87% |  | 43 | 3.9316 | 3.9316 |  | 0.7813% | 0.7813%
61 | 13.0396 | 0.047958 | 16.82% | 15 | 0.047958 | 24.87% |  | 44 | 4.1247 | 4.1247 |  | 0.8709% | 0.8709%
62 | 13.6802 | 0.047958 | 19.22% | 15 | 0.047958 | 24.87% |  | 45 | 4.3274 | 4.3274 |  | 0.9722% | 0.9722%
63 | 14.3522 | 0.047958 | 21.98% | 15 | 0.047958 | 24.87% |  | 46 | 4.54 | 4.54 |  | 1.087% | 1.087%
[8 empty] | 47 | 4.763 | 4.763 |  | 1.217% | 1.217%
[8 empty] | 48 | 4.997 | 4.997 |  | 1.365% | 1.365%
[8 empty] | 49 | 5.2425 | 5.2425 |  | 1.533% | 1.533%
[8 empty] | 50 | 5.5 | 5.5 |  | 1.723% | 1.723%
| age reduction factor (r) | [6 empty] | 51 | 5.7702 | 5.7702 |  | 1.94% | 1.94%
[8 empty] | 52 | 6.0537 | 6.0537 |  | 2.187% | 2.187%
| Beta 2=Beta 1= ageing rate | [6 empty] | 53 | 6.3511 | 6.3511 | 6.3511 | 2.467% | 2.467% | 2.467%
| ageing reduction factor=(current HS-2)/7+1 | see p. 149 | [5 empty] | 54 | 6.6631 | 6.6631 | 6.5574 | 2.787% | 2.787% | 2.676%
[8 empty] | 55 | 6.9904 | 6.9904 | 6.7704 | 3.152% | 3.152% | 2.903%
| if HS<2=1 | [6 empty] | 56 | 7.3338 | 7.3338 | 6.9904 | 3.568% | 3.568% | 3.152%
| ifHS>5.5=1.5 | [6 empty] | 57 | 7.6941 | 7.6941 | 7.2175 | 4.042% | 4.042% | 3.423%
| if HS is between 2 and 5.5=(current HS-2)/7+1 | [6 empty] | 58 | 8.0721 | 8.0721 | 7.452 | 4.584% | 4.584% | 3.719%
[8 empty] | 59 | 8.4686 | 8.4686 | 7.6941 | 5.204% | 5.204% | 4.042%
[8 empty] | 60 | 8.8847 | 8.8847 | 7.9441 | 5.911% | 5.911% | 4.396%
[8 empty] | 61 | 9.3211 | 9.3211 | 8.2022 | 6.721% | 6.721% | 4.782%
[8 empty] | 62 | 9.7791 | 9.7791 | 8.4686 | 7.647% | 7.647% | 5.204%
[8 empty] | 63 | 10.2595 | 10.2595 | 8.7438 | 8.707% | 8.707% | 5.665%
[8 empty] | 64 | 10.7635 | 10.7635 | 9.0278 | 9.92% | 9.92% | 6.169%
[8 empty] | 65 | 11.2923 | 11.2923 | 9.3211 | 11.31% | 11.31% | 6.721%
[8 empty] | 66 | 11.847 | 11.847 | 9.624 | 12.9% | 12.9% | 7.324%
[8 empty] | 67 | 12.429 | 12.429 | 9.9366 | 14.73% | 14.73% | 7.984%
[8 empty] | 68 | 13.0396 | 13.0396 | 10.2595 | 16.82% | 16.82% | 8.707%
| Beta 2 | [6 empty] | 69 | 13.6802 | 13.6802 | 10.5928 | 19.22% | 19.22% | 9.497%
| Beta2=Beta1 (due to assumptions in 3.3b) | [6 empty] | 70 | 14.3522 | 14.3522 | 10.9369 | 21.98% | 21.98% | 10.36%
0.53 x e^((0.05827 / 1) x 8)) = 0.84
0.53
0.46616
0.84475

## 3.3b Base or Normal wear
Age | Initial Health Score | Uncapped | HI2 Threshold | HI3 Threshold | HI4 Threshold | HI5 Threshold | HI Band | uncapped HI Band | expected life | aging rate |  | Normal Expected life | Duty Factor | Location Factor | actual expected life
0 | 0.5 | 0.5 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 | 50 | 0.047958 |  | 50 | 1 | 1 | 50
1 | 0.52456 | 0.52456 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  | (Beta 1 value)
2 | 0.55033 | 0.55033 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
3 | 0.57737 | 0.57737 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
4 | 0.60573 | 0.60573 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
5 | 0.63549 | 0.63549 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
6 | 0.66671 | 0.66671 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
7 | 0.69946 | 0.69946 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
8 | 0.73383 | 0.73383 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
9 | 0.76988 | 0.76988 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
10 | 0.8077 | 0.8077 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
11 | 0.84738 | 0.84738 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
12 | 0.88901 | 0.88901 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
13 | 0.93268 | 0.93268 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
14 | 0.9785 | 0.9785 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
15 | 1.0266 | 1.0266 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
16 | 1.077 | 1.077 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
17 | 1.1299 | 1.1299 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
18 | 1.1854 | 1.1854 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
19 | 1.2437 | 1.2437 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
20 | 1.3047 | 1.3047 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
21 | 1.3688 | 1.3688 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
22 | 1.4361 | 1.4361 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | Age | (Multiple Items) |  | Age | (Multiple Items)
23 | 1.5066 | 1.5066 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
24 | 1.5807 | 1.5807 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | Row Labels | Count of HI Band | Count of HI Band2 | Row Labels | Count of uncapped HI Band | Count of uncapped HI Band2
25 | 1.6583 | 1.6583 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | HI1 | 53 | 86.89% | HI1 | 53 | 86.89%
26 | 1.7398 | 1.7398 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | HI2 | 7 | 11.48% | HI2 | 7 | 11.48%
27 | 1.8252 | 1.8252 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | HI3 | 1 | 1.639% | HI3 | 1 | 1.639%
28 | 1.9149 | 1.9149 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | Grand Total | 61 | 100% | Grand Total | 61 | 100%
29 | 2.009 | 2.009 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
30 | 2.1077 | 2.1077 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
31 | 2.2112 | 2.2112 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
32 | 2.3199 | 2.3199 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
33 | 2.4338 | 2.4338 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
34 | 2.5534 | 2.5534 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
35 | 2.6788 | 2.6788 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
36 | 2.8104 | 2.8104 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
37 | 2.9485 | 2.9485 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
38 | 3.0933 | 3.0933 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
39 | 3.2453 | 3.2453 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
40 | 3.4047 | 3.4047 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
41 | 3.572 | 3.572 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
42 | 3.7475 | 3.7475 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
43 | 3.9316 | 3.9316 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
44 | 4.1247 | 4.1247 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
45 | 4.3274 | 4.3274 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
46 | 4.54 | 4.54 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
47 | 4.763 | 4.763 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
48 | 4.997 | 4.997 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
49 | 5.2425 | 5.2425 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
50 | 5.5 | 5.5 | 4 | 5.5 | 6.5 | 8 | HI3 | HI3
51 | 5.5 | 5.7702 | 4 | 5.5 | 6.5 | 8 | HI3 | HI3
52 | 5.5 | 6.0537 | 4 | 5.5 | 6.5 | 8 | HI3 | HI3
53 | 5.5 | 6.3511 | 4 | 5.5 | 6.5 | 8 | HI3 | HI3
54 | 5.5 | 6.6631 | 4 | 5.5 | 6.5 | 8 | HI3 | HI4
55 | 5.5 | 6.9904 | 4 | 5.5 | 6.5 | 8 | HI3 | HI4
56 | 5.5 | 7.3338 | 4 | 5.5 | 6.5 | 8 | HI3 | HI4
57 | 5.5 | 7.6941 | 4 | 5.5 | 6.5 | 8 | HI3 | HI4
58 | 5.5 | 8.0721 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
59 | 5.5 | 8.4686 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
60 | 5.5 | 8.8847 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
61 | 5.5 | 9.3211 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
62 | 5.5 | 9.7791 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
63 | 5.5 | 10.2595 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
64 | 5.5 | 10.7635 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
65 | 5.5 | 11.2923 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
66 | 5.5 | 11.847 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
67 | 5.5 | 12.429 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | Assumptions
68 | 5.5 | 13.0396 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
69 | 5.5 | 13.6802 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | Expected life=normal expected life |  | no assumptions for duty factor and location factor
70 | 5.5 | 14.3522 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
71 | 5.5 | 15.0573 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | H expected life | 5.5
72 | 5.5 | 15.797 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | Hnew is HS of new asset | 0.5
73 | 5.5 | 16.5731 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
74 | 5.5 | 17.3873 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  | initial HS | initial HS: initial estimate of Asset Health but does not take into account any actual health measurement or assessment thaty may have been carried out
75 | 5.5 | 18.2414 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | This provides an initial age-based indication of health up to a maximum HS or 5.5., which needs to be modified in the next stage to take account of available data regarding the health of the asset
76 | 5.5 | 19.1376 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
77 | 5.5 | 20.0777 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  | current HS | for its estimation we need
78 | 5.5 | 21.0641 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
79 | 5.5 | 22.0989 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
80 | 5.5 | 23.1845 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
81 | 5.5 | 24.3235 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
82 | 5.5 | 25.5184 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
83 | 5.5 | 26.7721 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
84 | 5.5 | 28.0873 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
85 | 5.5 | 29.4671 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
86 | 5.5 | 30.9147 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
87 | 5.5 | 32.4335 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
88 | 5.5 | 34.0268 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
89 | 5.5 | 35.6984 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
90 | 5.5 | 37.4522 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
91 | 5.5 | 39.2921 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
92 | 5.5 | 41.2223 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
93 | 5.5 | 43.2474 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
94 | 5.5 | 45.372 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
95 | 5.5 | 47.601 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
96 | 5.5 | 49.9395 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
97 | 5.5 | 52.3928 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
98 | 5.5 | 54.9667 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
99 | 5.5 | 57.667 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
100 | 5.5 | 60.5 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5

## 3.3c Base or Normal wear
Age | Initial Health Score Capped | Future Health Score Capped @5.5 | B2 | R | Initial Health Score Capped @15 | Future Health Score capped @15 | HI2 Threshold | HI3 Threshold | HI4 Threshold | HI5 Threshold | HI Band | uncapped HI Band | expected life | aging rate |  | Normal Expected life | Duty Factor | Location Factor | actual expected life
0 | 0.5 | 0.52456 | 0.047958 | 1 | 0.5 | 0.5 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 | 50 | 0.047958 |  | 50 | 1 | 1 | 50
1 | 0.52456 | 0.55033 | 0.047958 | 1 | 0.52456 | 0.52456 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  | (Beta 1 value)
2 | 0.55033 | 0.57737 | 0.047958 | 1 | 0.55033 | 0.55033 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
3 | 0.57737 | 0.60573 | 0.047958 | 1 | 0.57737 | 0.57737 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
4 | 0.60573 | 0.63549 | 0.047958 | 1 | 0.60573 | 0.60573 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 | 1 | if HS<2=1
5 | 0.63549 | 0.66671 | 0.047958 | 1 | 0.63549 | 0.63549 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 | 1.5 | ifHS>5.5=1.5
6 | 0.66671 | 0.69946 | 0.047958 | 1 | 0.66671 | 0.66671 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 | (current HS-2)/7+1 | if HS is between 2 and 5.5=(current HS-2)/7+1
7 | 0.69946 | 0.73383 | 0.047958 | 1 | 0.69946 | 0.69946 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
8 | 0.73383 | 0.76988 | 0.047958 | 1 | 0.73383 | 0.73383 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
9 | 0.76988 | 0.8077 | 0.047958 | 1 | 0.76988 | 0.76988 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
10 | 0.8077 | 0.84738 | 0.047958 | 1 | 0.8077 | 0.8077 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
11 | 0.84738 | 0.88901 | 0.047958 | 1 | 0.84738 | 0.84738 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
12 | 0.88901 | 0.93268 | 0.047958 | 1 | 0.88901 | 0.88901 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
13 | 0.93268 | 0.9785 | 0.047958 | 1 | 0.93268 | 0.93268 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
14 | 0.9785 | 1.0266 | 0.047958 | 1 | 0.9785 | 0.9785 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
15 | 1.0266 | 1.077 | 0.047958 | 1 | 1.0266 | 1.0266 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
16 | 1.077 | 1.1299 | 0.047958 | 1 | 1.077 | 1.077 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
17 | 1.1299 | 1.1854 | 0.047958 | 1 | 1.1299 | 1.1299 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
18 | 1.1854 | 1.2437 | 0.047958 | 1 | 1.1854 | 1.1854 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
19 | 1.2437 | 1.3047 | 0.047958 | 1 | 1.2437 | 1.2437 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
20 | 1.3047 | 1.3688 | 0.047958 | 1 | 1.3047 | 1.3047 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
21 | 1.3688 | 1.4361 | 0.047958 | 1 | 1.3688 | 1.3688 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
22 | 1.4361 | 1.5066 | 0.047958 | 1 | 1.4361 | 1.4361 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | Age | (Multiple Items) |  | Age | (Multiple Items)
23 | 1.5066 | 1.5807 | 0.047958 | 1 | 1.5066 | 1.5066 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
24 | 1.5807 | 1.6583 | 0.047958 | 1 | 1.5807 | 1.5807 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | Row Labels | Count of HI Band | Count of HI Band2 | Row Labels | Count of uncapped HI Band | Count of uncapped HI Band2
25 | 1.6583 | 1.7398 | 0.047958 | 1 | 1.6583 | 1.6583 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | HI1 | 53 | 86.89% | HI1 | 53 | 86.89%
26 | 1.7398 | 1.8252 | 0.047958 | 1 | 1.7398 | 1.7398 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | HI2 | 7 | 11.48% | HI2 | 7 | 11.48%
27 | 1.8252 | 1.9149 | 0.047958 | 1 | 1.8252 | 1.8252 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | HI3 | 1 | 1.639% | HI3 | 1 | 1.639%
28 | 1.9149 | 2.009 | 0.047958 | 1 | 1.9149 | 1.9149 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1 |  |  |  | Grand Total | 61 | 100% | Grand Total | 61 | 100%
29 | 2.009 | 2.1076 | 0.047958 | 1.0013 | 2.009 | 2.009 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
30 | 2.1077 | 2.2096 | 0.047958 | 1.0154 | 2.1077 | 2.1076 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
31 | 2.2112 | 2.3166 | 0.047958 | 1.0302 | 2.2112 | 2.2096 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
32 | 2.3199 | 2.4287 | 0.047958 | 1.0457 | 2.3199 | 2.3166 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
33 | 2.4338 | 2.5463 | 0.047958 | 1.062 | 2.4338 | 2.4287 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
34 | 2.5534 | 2.6694 | 0.047958 | 1.0791 | 2.5534 | 2.5463 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
35 | 2.6788 | 2.7985 | 0.047958 | 1.097 | 2.6788 | 2.6694 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
36 | 2.8104 | 2.9339 | 0.047958 | 1.1158 | 2.8104 | 2.7985 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
37 | 2.9485 | 3.0757 | 0.047958 | 1.1355 | 2.9485 | 2.9339 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
38 | 3.0933 | 3.2244 | 0.047958 | 1.1562 | 3.0933 | 3.0757 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
39 | 3.2453 | 3.3802 | 0.047958 | 1.1779 | 3.2453 | 3.2244 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
40 | 3.4047 | 3.5435 | 0.047958 | 1.2007 | 3.4047 | 3.3802 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
41 | 3.572 | 3.7147 | 0.047958 | 1.2246 | 3.572 | 3.5435 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
42 | 3.7475 | 3.8941 | 0.047958 | 1.2496 | 3.7475 | 3.7147 | 4 | 5.5 | 6.5 | 8 | HI1 | HI1
43 | 3.9316 | 4.0822 | 0.047958 | 1.2759 | 3.9316 | 3.8941 | 4 | 5.5 | 6.5 | 8 | HI2 | HI1
44 | 4.1247 | 4.2793 | 0.047958 | 1.3035 | 4.1247 | 4.0822 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
45 | 4.3274 | 4.4859 | 0.047958 | 1.3325 | 4.3274 | 4.2793 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
46 | 4.54 | 4.7026 | 0.047958 | 1.3629 | 4.54 | 4.4859 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
47 | 4.763 | 4.9296 | 0.047958 | 1.3947 | 4.763 | 4.7026 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
48 | 4.997 | 5.1676 | 0.047958 | 1.4281 | 4.997 | 4.9296 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
49 | 5.2425 | 5.4171 | 0.047958 | 1.4632 | 5.2425 | 5.1676 | 4 | 5.5 | 6.5 | 8 | HI2 | HI2
50 | 5.5 | 5.5 | 0.047958 | 1.5 | 5.5 | 5.4171 | 4 | 5.5 | 6.5 | 8 | HI3 | HI2
51 | 5.5 | 5.5 | 0.047958 | 1.5 | 5.7702 | 5.6787 | 4 | 5.5 | 6.5 | 8 | HI3 | HI3
52 | 5.5 | 5.5 | 0.047958 | 1.5 | 6.0537 | 5.9577 | 4 | 5.5 | 6.5 | 8 | HI3 | HI3
53 | 5.5 | 5.5 | 0.047958 | 1.5 | 6.3511 | 6.2503 | 4 | 5.5 | 6.5 | 8 | HI3 | HI3
54 | 5.5 | 5.5 | 0.047958 | 1.5 | 6.6631 | 6.5574 | 4 | 5.5 | 6.5 | 8 | HI3 | HI4
55 | 5.5 | 5.5 | 0.047958 | 1.5 | 6.9904 | 6.8795 | 4 | 5.5 | 6.5 | 8 | HI3 | HI4
56 | 5.5 | 5.5 | 0.047958 | 1.5 | 7.3338 | 7.2175 | 4 | 5.5 | 6.5 | 8 | HI3 | HI4
57 | 5.5 | 5.5 | 0.047958 | 1.5 | 7.6941 | 7.5721 | 4 | 5.5 | 6.5 | 8 | HI3 | HI4
58 | 5.5 | 5.5 | 0.047958 | 1.5 | 8.0721 | 7.9441 | 4 | 5.5 | 6.5 | 8 | HI3 | HI4
59 | 5.5 | 5.5 | 0.047958 | 1.5 | 8.4686 | 8.3343 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
60 | 5.5 | 5.5 | 0.047958 | 1.5 | 8.8847 | 8.7438 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
61 | 5.5 | 5.5 | 0.047958 | 1.5 | 9.3211 | 9.1733 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
62 | 5.5 | 5.5 | 0.047958 | 1.5 | 9.7791 | 9.624 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
63 | 5.5 | 5.5 | 0.047958 | 1.5 | 10.2595 | 10.0968 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
64 | 5.5 | 5.5 | 0.047958 | 1.5 | 10.7635 | 10.5928 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
65 | 5.5 | 5.5 | 0.047958 | 1.5 | 11.2923 | 11.1132 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
66 | 5.5 | 5.5 | 0.047958 | 1.5 | 11.847 | 11.6591 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
67 | 5.5 | 5.5 | 0.047958 | 1.5 | 12.429 | 12.2319 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | Assumptions
68 | 5.5 | 5.5 | 0.047958 | 1.5 | 13.0396 | 12.8328 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
69 | 5.5 | 5.5 | 0.047958 | 1.5 | 13.6802 | 13.4632 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | Expected life=normal expected life |  | no assumptions for duty factor and location factor
70 | 5.5 | 5.5 | 0.047958 | 1.5 | 14.3522 | 14.1246 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
71 | 5.5 | 5.5 | 0.047904 | 1.5 | 15 | 14.8185 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | H expected life | 5.5
72 | 5.5 | 5.5 | 0.047239 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | Hnew is HS of new asset | 0.5
73 | 5.5 | 5.5 | 0.046592 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
74 | 5.5 | 5.5 | 0.045962 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  | initial HS | initial HS: initial estimate of Asset Health but does not take into account any actual health measurement or assessment thaty may have been carried out
75 | 5.5 | 5.5 | 0.045349 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | This provides an initial age-based indication of health up to a maximum HS or 5.5., which needs to be modified in the next stage to take account of available data regarding the health of the asset
76 | 5.5 | 5.5 | 0.044753 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
77 | 5.5 | 5.5 | 0.044171 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  | current HS | for its estimation we need
78 | 5.5 | 5.5 | 0.043605 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
79 | 5.5 | 5.5 | 0.043053 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
80 | 5.5 | 5.5 | 0.042515 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | age reduction factor (r)
81 | 5.5 | 5.5 | 0.04199 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
82 | 5.5 | 5.5 | 0.041478 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | Beta 2=Beta 1= ageing rate
83 | 5.5 | 5.5 | 0.040978 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | ageing reduction factor=(current HS-2)/7+1 | see p. 149
84 | 5.5 | 5.5 | 0.04049 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
85 | 5.5 | 5.5 | 0.040014 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | if HS<2=1
86 | 5.5 | 5.5 | 0.039549 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | ifHS>5.5=1.5
87 | 5.5 | 5.5 | 0.039094 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | if HS is between 2 and 5.5=(current HS-2)/7+1
88 | 5.5 | 5.5 | 0.03865 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
89 | 5.5 | 5.5 | 0.038216 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
90 | 5.5 | 5.5 | 0.037791 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
91 | 5.5 | 5.5 | 0.037376 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
92 | 5.5 | 5.5 | 0.03697 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
93 | 5.5 | 5.5 | 0.036572 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
94 | 5.5 | 5.5 | 0.036183 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
95 | 5.5 | 5.5 | 0.035802 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
96 | 5.5 | 5.5 | 0.035429 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
97 | 5.5 | 5.5 | 0.035064 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5
98 | 5.5 | 5.5 | 0.034706 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | Beta 2
99 | 5.5 | 5.5 | 0.034356 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5 |  |  |  | Beta2=Beta1 (due to assumptions in 3.3b)
100 | 5.5 | 5.5 | 0.034012 | 1.5 | 15 | 15 | 4 | 5.5 | 6.5 | 8 | HI3 | HI5

## 4.1 Loss of Export Capacity
Run 2 scenarios, compare results of export capacity
Export capacity of generators e.g. Hydro may be restricted if there is a three year build of a new substation. This might not occur if there is a flexible service

## 4.2 Avoided Energy
Avoided Energy
= Energy_traditional - Energy_Flex
Energy required by the DSO traditionally (MW) | 180 | Determined by system loading
Energy required by the DSO from traditional and flexibility (MW) | 170 | Determined by procured flexiblity and subsequent substation energy
Energy Saved (MW) | 10
Cost Saved (£) | 500 | Cost of energy at the substation | £50/MW assumption entered here

## 4.3 Community Generation Credit
Community Generation Credit
= Community Generation Credit/year * Simulation Length
Community Generation Credit (£/MWh-yr) | 100
Simulation Length (yr) | 1.2
Cost (£) | 120
Community Generation Credit
= Community Generation Credit/year * Simulation Length
Cambridge's notes
Community Generation Credit
A value of 0.5p/kWh seems reasonable (see justification below). The thing we need to think is the way how this will be introduced in the CBA (i.e. set conditions, others).
Community credit is what citizens are willing to pay for the 'community' aspect of an energy project, on top of the pure environmental aspects.
A behavioural economics approach would suggest that the basic answer to any question of 'what would you be willing to pay for some societal benefit?' is around £10, as that is what might be given if someone asked you in the pub for a contribution to saving the whales, saving the pub etc.
On that basis if a typical household participating in a community energy scheme generates 2000 kWh per year, that equates to 0.5p/kWh (i.e. 2000/1000).
Actually we have some real evidence from CESP - the Community Energy Savings Programme which ran from 2009-2012.
The CESP scheme supported community energy projects including district heating by paying towards carbon savings.
It explicitly paid a community area bonus if at least 25% of a community was treated with an energy savings measure.
The bonus rate was a carbon credit of x%/2 where x% was the percentage of the community treated. So at 50% treated the bonus rate was additional carbon credit savings of 25%.
The average cost of the scheme was roughly £18 / tonne of CO2 saved, so a 25% area bonus was £4.50 per tonne of CO2 saved, rising to a bonus of 50% or £9 for 100% coverage.
To convert this into a willingness to pay for additional community renewables we might assume that the marginal saving on CO2 per unit of zero carbon energy is 0.4 tonnes per MWh (assuming gas is the marginal fuel).
That gives c.£4 / MWh (9*0.4), or 0.4p / kWh. Given that underlying UK carbon prices have increased by 400% since 2012 (from £10 in the EUETS to £40 with the EUETS + CPF), 0.5p/kWh seems a reasonable figure.
See legislation here
https://www.legislation.gov.uk/ukdsi/2009/9780111481929/contents
Evaluation of CESP
https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/350722/CERT_CESP_Evaluation_FINAL_Report.pdf

## 4.4 Net Avoided GHG
Net Avoided Greenhouse Gasses (GHG) |  |  | TBC
= (CO2_Bulk + CO2_DER)_Trad - (CO2_Bulk + CO2_DER)_Flex
CO2_Bulk system_traditional | 300 | kg
CO2_DER_flex_traditional | 10 | kg
CO2_Bulk system_flex | 250 | kg
CO2_DER_flex_flex | 25 | kg
Cost of CO2 (£/tonne CO2) | 4.4706 | *Refer to ON-P data inputs tab. Changes per year
Cost of Avoided GHG | 156.4706
Diesel cost per MW | £k per MW | 270
Diesel cost per MWh | £k per MWh | 0.243
How much diesel is required per customer per hour
Assumption: How much time is required for diesel gen in construction to supply customers
Customer Interruption (CI) and Customer Minutes Lost (CML)
| Unplanned | Planned
CI | 15.44 | 7.72
CML | 0.38 | 0.19
*These numbers are configurable within the tool
Cambridge's notes:
CO2
We need to define the kind of input we would need here, apart from the cost of CO2.
To keep this simply we can consider those that are related to energy, I mean expressed in MWh or KWh.
This can be for instance saving in distribution losses, avoided energy (4.3), net avoided outage(3.3? )
Both types of inputs (distribution losses, energy) refer to Scope 2 emissions according to the latest SSE PLC sustainability report – 2019
However according to the latest recommendation from DEFRA 2020, scope 3 emissions are the ones that enclose T&D losses, need to check it in order to allocate the corresponding conversion factors.
See SSE report (p. 17)
https://www.sse.com/media/onej35am/sse-sustainability-report-2019-final-spreads.pdf
And latest report from DEFRA (2020):
https://www.gov.uk/government/publications/greenhouse-gas-reporting-conversion-factors-2020
SF6
The other option is to consider CO2 costs associated to others (excluding losses), for instance in distribution activities (i.e. the operation of substations: leakage from electricity substations, magnesium smelters, others),
Don’t know if SSEN has this information per type of asset/item.
However, this seems to be very small in comparison with the CO2 emissions from distribution losses.
ENA is also proposing to include in the common methodology the impact of GHG (avoidance), I would suggest be aligned with them.

## 5.1 Operating assets beyond cap
| % over threshold | Duration(hours) |  |  |  | % over threshold | Duration(hours) |  |  |  | % over threshold | Duration(hours)
1 | 3 | 2 |  |  | 1 | 5 | 1 |  |  | 1 | 8 | 2
2 | 2 | 1 |  |  | 2 | 3 | 5 |  |  | 2 | 9 | 4
3 | 1 | 5 |  |  | 3 | 2 | 6 |  |  | 3 | 12 | 13
4 | 1 | 1 |  |  | 4 | 6 | 3 |  |  | 4 | 8 | 7
5 | 2 | 2 |  |  | 5 | 8 | 9 |  |  | 5 | 3 | 3
6 | 2 | 1 |  |  | 6 | 2 | 5 |  |  | 6 | 2 | 7
7 | 1 | 2 |  |  | 7 | 1 | 2 |  |  | 7 | 5 | 9
8 | 1 | 3 |  |  | 8 | 5 | 6 |  |  | 8 | 6 | 5
9 | 1 | 1 |  |  | 9 | 3 | 3 |  |  | 9 | 3 | 6
10 | 1 | 1 |  |  | 10 | 1 | 1 |  |  | 10 | 8 | 4
Average | 1.5 | 1.9 |  |  | Average | 3.6 | 4.1 |  |  | Average | 6.4 | 6
[15 empty] | Characteristic life | η
Asset 1 |  |  |  |  | Asset 2 |  |  |  |  | Asset 3 |  |  |  |  | Shape parameter | β
Number of Customers | 50 | # |  |  | Number of Customers | 50 | # |  |  | Number of Customers | 50 | # |  |  | HI shift Factor | b
CML cost | 0.37667 | £ |  |  | CML cost | 0.37667 | £ |  |  | CML cost | 0.37667 | £ |  |  | Health Index | HI
CI cost | 15.4435 | £ |  |  | CI cost | 15.4435 | £ |  |  | CI cost | 15.4435 | £
Characteristic life | 40 | η |  |  | Characteristic life | 40 | η |  |  | Characteristic life | 40 | η
Shape parameter | 3 | β |  |  | Shape parameter | 3 | β |  |  | Shape parameter | 3 | β
HI shift Factor | 20 | b |  |  | HI shift Factor | 10 | b |  |  | HI shift Factor | 5 | b
HI | 5 | HI |  |  | HI | 3 | HI |  |  | HI | 1 | HI
Time to restore(mins) | 145 | mins |  |  | Time to restore(mins) | 145 | mins |  |  | Time to restore(mins) | 145 | mins
Age | P.O.F | CI | CML | CI CML Cost | Age | P.O.F | CI | CML | CI CML Cost | Age | P.O.F | CI | CML | CI CML Cost
10 | 0.0079681 | 0.3984 | 57.7686 | 27.9125 | 10 | 0.0036347 | 0.18174 | 26.3516 | 12.7325 | 10 | 0.0040876 | 0.20438 | 29.6353 | 14.3191
15 | 0.026639 | 1.3319 | 193.131 | 93.3167 | 15 | 0.012214 | 0.61071 | 88.5535 | 42.7871 | 15 | 0.013729 | 0.68644 | 99.5344 | 48.0929
20 | 0.061995 | 3.0998 | 449.4638 | 217.1711 | 20 | 0.02871 | 1.4355 | 208.1506 | 100.5738 | 20 | 0.032237 | 1.6118 | 233.7179 | 112.9274
25 | 0.1175 | 5.8752 | 851.8975 | 411.6183 | 25 | 0.055307 | 2.7654 | 400.9791 | 193.7444 | 25 | 0.061995 | 3.0998 | 449.4638 | 217.1711
30 | 0.19426 | 9.7132 | 1408.4191 | 680.5175 | 30 | 0.093637 | 4.6819 | 678.8715 | 328.016 | 30 | 0.1047 | 5.2348 | 759.0463 | 366.7547
35 | 0.29036 | 14.5181 | 2105.123 | 1017.1497 | 35 | 0.14455 | 7.2273 | 1047.9525 | 506.3479 | 35 | 0.16106 | 8.053 | 1167.6845 | 564.1998
40 | 0.4007 | 20.0352 | 2905.1055 | 1403.6839 | 40 | 0.20788 | 10.3941 | 1507.1454 | 728.2199 | 40 | 0.2306 | 11.53 | 1671.8484 | 807.8008
45 | 0.51761 | 25.8804 | 3752.6642 | 1813.2059 | 45 | 0.28238 | 14.119 | 2047.2603 | 989.1917 | 45 | 0.31151 | 15.5753 | 2258.4151 | 1091.2171
50 | 0.63212 | 31.606 | 4582.8741 | 2214.3452 | 50 | 0.36566 | 18.2829 | 2651.0164 | 1280.9135 | 50 | 0.4007 | 20.0352 | 2905.1055 | 1403.6839
55 | 0.73579 | 36.7894 | 5334.4564 | 2577.4934 | 55 | 0.45438 | 22.7188 | 3294.2297 | 1591.7003 | 55 | 0.49413 | 24.7064 | 3582.4294 | 1730.9521
60 | 0.82236 | 41.118 | 5962.1148 | 2880.7644 | 60 | 0.54458 | 27.2288 | 3948.1782 | 1907.6739 | 60 | 0.58718 | 29.3588 | 4257.0322 | 2056.9055
65 | 0.88886 | 44.4432 | 6444.2635 | 3113.7282 | 65 | 0.63212 | 31.606 | 4582.8741 | 2214.3452 | 65 | 0.6753 | 33.7652 | 4895.9495 | 2365.6165
70 | 0.93569 | 46.7844 | 6783.7338 | 3277.7528 | 70 | 0.7132 | 35.6601 | 5170.7119 | 2498.3757 | 70 | 0.75462 | 37.7308 | 5470.9608 | 2643.4494
75 | 0.96578 | 48.2891 | 7001.9186 | 3383.175 | 75 | 0.7848 | 39.24 | 5689.7973 | 2749.1865 | 75 | 0.82236 | 41.118 | 5962.1148 | 2880.7644
80 | 0.98336 | 49.168 | 7129.3665 | 3444.7551 | 80 | 0.845 | 42.2502 | 6126.2841 | 2960.0874 | 80 | 0.87719 | 43.8597 | 6359.6588 | 3072.849
85 | 0.99265 | 49.6325 | 7196.7096 | 3477.2938 | 85 | 0.89314 | 44.657 | 6475.2615 | 3128.7057 | 85 | 0.91917 | 45.9587 | 6664.0112 | 3219.9055
90 | 0.99707 | 49.8534 | 7228.7415 | 3492.7709 | 90 | 0.92967 | 46.4834 | 6740.0933 | 3256.6667 | 90 | 0.94951 | 47.4755 | 6883.949 | 3326.1746
95 | 0.99895 | 49.9475 | 7242.3878 | 3499.3645 | 95 | 0.95593 | 47.7965 | 6930.4952 | 3348.6648 | 95 | 0.97016 | 48.5079 | 7033.6389 | 3398.5015
100 | 0.99966 | 49.9832 | 7247.5679 | 3501.8674 | 100 | 0.97378 | 48.6891 | 7059.9233 | 3411.2016 | 100 | 0.98336 | 49.168 | 7129.3665 | 3444.7551
| Avg. % over Threshold | Shift factor
| 0 | 20
| 0-2 | 15
| 3-5 | 10
| 6-8 | 5
| 9+ | 0