## Contents
SEPD Network Scenario Headroom Report 2026 Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations and Bulk Supply Points (BSP) up to 2050. SSEN have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN's best view of the future demand and generation needs on our network is aligned to the Holistic Transition scenario. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Demand | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Generation | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Demand | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Generation | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
LEP Reference | This tab provides information on the LEPs, local authorities and the connected GSPs, BSPs and Primaries that support those areas
EISD | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
Apr 2026 Version 1.1

## Key Information
SEPD Network Scenario Headroom Report 2026 Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our other documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. In order to identify future overloaded network assets, forecasts are created which combine our long term DFES projections with the estimated contribution from our connections pipeline after appropriate diversity factors have been applied. The DFES incorporates transitional Regional Energy Strategic Plan (tRESP) insights to ensure alignment and consistency with National Energy System Operator (NESO)'s energy infrastructure needs. Forecast headroom and outstanding contracted generation capacity are indicative and subject to external policy drivers. Actual outcomes will be influenced by Clean Power 2030 (CP2030) programme and Connections Reform, which may materially affect connection queue management. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportunities to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SEPD. Please note that our DFES scenario naming convention has been updated yearly to align with the updated NESO Future Energy Scenario (FES) pathways framework. Published annually, the FES framework outlines different scenarios for the future of the whole energy system. SSEN's DFES builds on the FES scenarios by engaging a diverse and expert range of stakeholders, undertaking detailed investigations into the pipeline of projects seeking to connect, and reflecting extensive industry and local area insight to forecast future load on SSEN’s network.
New DFES Scenario | Previous DFES Scenario | FES Pathway Description
Electric Engagement (EE) | Electric Engagement (formerly Consumer Transformation) | Net zero met through mainly electrified demand. Consumers are highly engaged in the energy transition through smart technologies that reduce energy demands, utilising technologies such as electric heat pumps and electric vehicles.
Holistic Transition (HT) | Holistic Transition (formerly Leading the Way) | Net zero met through a mix of electrification and hydrogen, with hydrogen mainly around industrial clusters. Consumer engagement in the transition is very strong with demand shifting, with smart homes and electric vehicles providing flexibility to the grid.
Hydrogen Evolution (HE) | Hydrogen Evolution (formerly System Transformation) | Net zero met through fast progress for hydrogen in industry and heat. Some consumers will have hydrogen boilers, although most heat is electrified. There are low levels of consumer engagement. Hydrogen will be prevalent for heavy goods vehicles but electric car uptake is strong.
Falling Behind (FB) | Falling Behind (formerly Counterfactual (formerly Falling Short)) | Net zero missed, though some progress is made for decarbonisation compared to today. There is still a heavy reliance on unabated fossil fuel.
`
Apr 2026
Version 1.1

## Primary Headroom Demand
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Demand (MVA) | Demand Headroom Winter (MVA) | [11 empty] | Demand Headroom Summer (MVA) | [11 empty] | Demand Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH BSP | ALDERNEY PRIMARY | MINIMUM HEADROOM | SZ 04270 95141 | NO | YES | 13.45 | -3.7192 | 12.751 | 12.6959 | 12.4816 | 12.2 | 11.7081 | 11.1551 | 10.5979 | 9.9898 | 7.4836 | 5.6836 | 4.9704 | -4.123 | 11.1592 | 11.0439 | 10.7928 | 10.3888 | 9.9326 | 9.3183 | 8.8092 | 8.249 | 6.149 | 4.4245 | 2.0959 | -4.799 | 11.2285 | 11.1928 | 11.0296 | 10.802 | 10.451 | 10.0377 | 9.6326 | 9.2265 | 7.8296 | 6.6153 | 6.2306
|  | ALDERNEY PRIMARY | EE |  |  |  |  | -3.7161 | 12.7592 | 12.7224 | 12.5336 | 12.2826 | 11.8245 | 11.302 | 10.7296 | 10.1061 | 7.9388 | 6.2847 | 5.549 | -4.1199 | 11.1592 | 11.0847 | 10.8265 | 10.4428 | 10.0092 | 9.4765 | 8.9775 | 8.4775 | 6.149 | 4.4245 | 3.5265 | -4.798 | 11.2357 | 11.2112 | 11.0836 | 10.8898 | 10.5785 | 10.2163 | 9.851 | 9.4979 | 8.2724 | 6.8153 | 6.3326
|  | ALDERNEY PRIMARY | HT |  |  |  |  | -3.7192 | 12.751 | 12.6959 | 12.4816 | 12.2 | 11.7081 | 11.1551 | 10.5979 | 9.9898 | 7.4836 | 5.6836 | 4.9704 | -4.123 | 11.1704 | 11.0439 | 10.7928 | 10.3888 | 9.9326 | 9.3183 | 8.8092 | 8.249 | 6.2928 | 5.1357 | 4.9418 | -4.799 | 11.2285 | 11.1928 | 11.0296 | 10.802 | 10.451 | 10.0377 | 9.6326 | 9.2265 | 7.8296 | 6.6153 | 6.2306
|  | ALDERNEY PRIMARY | HE |  |  |  |  | -3.7141 | 12.7734 | 12.7326 | 12.5367 | 12.2826 | 11.8888 | 11.4234 | 10.9622 | 10.4163 | 8.5836 | 7.3796 | 6.8 | -4.122 | 11.1847 | 11.0734 | 10.8357 | 10.4673 | 10.0459 | 9.4826 | 9.0132 | 8.5173 | 6.55 | 5.2 | 4.2888 | -4.7949 | 11.2469 | 11.2163 | 11.0857 | 10.8857 | 10.6081 | 10.2694 | 9.9357 | 9.6102 | 8.5653 | 7.8928 | 7.5224
|  | ALDERNEY PRIMARY | FB |  |  |  |  | -3.6059 | 12.9877 | 12.9653 | 12.9602 | 12.9102 | 12.8571 | 12.7796 | 12.6714 | 12.5449 | 11.6643 | 10.2602 | 9.4408 | -4.0505 | 11.5428 | 11.2469 | 11.1755 | 10.9847 | 10.7939 | 10.5826 | 10.2847 | 9.9255 | 7.8612 | 5.0112 | 2.0959 | -4.6929 | 11.4551 | 11.4265 | 11.4143 | 11.3775 | 11.3469 | 11.2775 | 11.1796 | 11.0643 | 10.2816 | 9.2979 | 8.7092
FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT PRIMARY | MINIMUM HEADROOM | SU 85976 48834 | NO | YES | 2.963 | 12.9184 | 12.896 | 12.7888 | 12.5551 | 12.2 | 11.6388 | 11.0245 | 10.3664 | 9.7582 | 7.7837 | 6.5541 | 6.4347 | 14.7322 | 14.5495 | 14.3485 | 14.0638 | 13.674 | 13.121 | 12.5016 | 11.8434 | 11.2199 | 9.2261 | 6.8016 | 2.9791 | 13.8531 | 13.7276 | 13.5837 | 13.3276 | 12.9551 | 12.397 | 11.7847 | 11.1286 | 10.5062 | 8.5204 | 7.3623 | 7.2919
|  | ALDERSHOT PRIMARY | EE |  |  |  |  | 12.9276 | 12.9449 | 12.8909 | 12.7398 | 12.4847 | 12.0582 | 11.5878 | 11.097 | 10.6256 | 8.649 | 7.2429 | 7.0827 | 14.7393 | 14.5771 | 14.4067 | 14.1628 | 13.8261 | 13.3485 | 12.8026 | 12.2261 | 11.6832 | 9.2822 | 7.4883 | 6.3985 | 13.8592 | 13.7643 | 13.6602 | 13.4745 | 13.1827 | 12.7347 | 12.2276 | 11.697 | 11.1929 | 9.2613 | 7.9613 | 7.8511
|  | ALDERSHOT PRIMARY | HT |  |  |  |  | 12.9184 | 12.896 | 12.7888 | 12.5551 | 12.2 | 11.6388 | 11.0245 | 10.3664 | 9.7582 | 7.7837 | 6.5541 | 6.4347 | 14.7322 | 14.5495 | 14.3485 | 14.0638 | 13.674 | 13.121 | 12.5016 | 11.8434 | 11.2199 | 9.2261 | 8.1587 | 7.9659 | 13.8531 | 13.7276 | 13.5837 | 13.3276 | 12.9551 | 12.397 | 11.7847 | 11.1286 | 10.5062 | 8.5204 | 7.3623 | 7.2919
|  | ALDERSHOT PRIMARY | HE |  |  |  |  | 12.9317 | 12.9531 | 12.9031 | 12.746 | 12.4756 | 12.049 | 11.6011 | 11.1072 | 10.6133 | 8.8888 | 7.9358 | 7.6837 | 14.7414 | 14.5791 | 14.4087 | 14.1628 | 13.822 | 13.3383 | 12.8128 | 12.2291 | 11.6618 | 9.4097 | 7.8903 | 6.5852 | 13.8653 | 13.7735 | 13.6745 | 13.4796 | 13.1756 | 12.7245 | 12.2449 | 11.7092 | 11.1827 | 9.4888 | 8.599 | 8.3807
|  | ALDERSHOT PRIMARY | FB |  |  |  |  | 13.1286 | 13.2613 | 13.3684 | 13.4868 | 13.3858 | 13.2786 | 13.1041 | 12.9347 | 12.7296 | 11.3735 | 9.4347 | 8.4613 | 14.8689 | 14.821 | 14.7659 | 14.7567 | 14.3995 | 14.1138 | 13.724 | 13.3526 | 12.9434 | 10.374 | 6.8016 | 2.9791 | 14.0827 | 14.1613 | 14.2266 | 14.2623 | 14.1123 | 13.9847 | 13.7715 | 13.5735 | 13.3358 | 11.8429 | 9.9592 | 9.0378
MELKSHAM GSP | CHIPPENHAM BSP | ALDERTON PRIMARY | MINIMUM HEADROOM | ST 84609 84059 | NO | YES | 0.26 | 1.0092 | 1.0306 | 1.052 | 11.1939 | 11.0918 | 10.9276 | 10.8439 | 10.6143 | 10.4153 | 9.7357 | 9.3622 | 9.5429 | 1.7347 | 1.7173 | 1.7041 | 11.0357 | 10.8867 | 10.7051 | 10.5969 | 10.3755 | 10.1806 | 9.4786 | 9.0408 | 9.0755 | 1.5071 | 1.5143 | 1.5133 | 11.1378 | 10.9571 | 10.7663 | 10.6806 | 10.45 | 10.249 | 9.5571 | 9.1847 | 9.3592
|  | ALDERTON PRIMARY | EE |  |  |  |  | 1.0122 | 1.0337 | 1.0541 | 11.2071 | 11.1459 | 10.9541 | 10.8561 | 10.6408 | 10.4765 | 9.7888 | 9.3949 | 9.5429 | 1.7378 | 1.7204 | 1.7051 | 11.0449 | 10.9388 | 10.7439 | 10.6255 | 10.4255 | 10.2745 | 9.5408 | 9.0592 | 9.0755 | 1.5092 | 1.5153 | 1.5143 | 11.1429 | 10.999 | 10.7918 | 10.6929 | 10.4735 | 10.3071 | 9.6061 | 9.2112 | 9.3592
|  | ALDERTON PRIMARY | HT |  |  |  |  | 1.0122 | 1.0327 | 1.052 | 11.1939 | 11.0918 | 10.9276 | 10.8439 | 10.6143 | 10.4153 | 9.7357 | 9.3622 | 9.5735 | 1.7378 | 1.7194 | 1.7041 | 11.0357 | 10.8867 | 10.7051 | 10.5969 | 10.3755 | 10.1806 | 9.4786 | 9.0408 | 9.1857 | 1.5082 | 1.5153 | 1.5143 | 11.1378 | 10.9571 | 10.7663 | 10.6816 | 10.45 | 10.249 | 9.5571 | 9.1847 | 9.399
|  | ALDERTON PRIMARY | HE |  |  |  |  | 1.0092 | 1.0306 | 1.0531 | 11.2612 | 11.1408 | 10.9429 | 10.8439 | 10.6429 | 10.4276 | 9.9724 | 9.748 | 9.7643 | 1.7347 | 1.7173 | 1.7041 | 11.1071 | 10.9327 | 10.7327 | 10.6133 | 10.4255 | 10.2204 | 9.7429 | 9.4531 | 9.3194 | 1.5071 | 1.5143 | 1.5133 | 11.2 | 10.9918 | 10.7806 | 10.6806 | 10.4755 | 10.2571 | 9.7867 | 9.5633 | 9.5796
|  | ALDERTON PRIMARY | FB |  |  |  |  | 1.0755 | 1.1255 | 1.1643 | 11.5327 | 11.5612 | 11.5531 | 11.5347 | 11.3102 | 11.2173 | 10.751 | 10.2735 | 9.9337 | 1.7908 | 1.7908 | 1.7918 | 11.3724 | 11.3653 | 11.3224 | 11.2714 | 11.0061 | 10.8878 | 10.3286 | 9.7194 | 9.0786 | 1.5653 | 1.5918 | 1.6082 | 11.5092 | 11.4929 | 11.451 | 11.4102 | 11.15 | 11.0429 | 10.5612 | 10.0806 | 9.7388
FLEET-BRAMLEY GSP | ALTON BSP | ALRESFORD PRIMARY | MINIMUM HEADROOM | SU 59684 32511 | NO | NO | 2.979 | 1.5571 | 19.3378 | 19.0122 | 18.7031 | 18.2143 | 17.5653 | 16.9122 | 16.1306 | 15.2949 | 12.9633 | 11.8184 | 11.6653 | 5.999 | 17.6255 | 17.3133 | 17.0327 | 16.5969 | 16.0316 | 15.4418 | 14.7224 | 13.9418 | 11.7449 | 10.8602 | 9.2286 | 3.4541 | 19.0327 | 18.7153 | 18.3939 | 17.9112 | 17.3184 | 16.699 | 15.9561 | 15.1133 | 12.748 | 11.9969 | 12.0612
|  | ALRESFORD PRIMARY | EE |  |  |  |  | 1.5571 | 19.3378 | 19.0265 | 18.7714 | 18.3816 | 17.8347 | 17.2459 | 16.5255 | 15.8041 | 13.5143 | 12.349 | 12.102 | 5.999 | 17.6255 | 17.3286 | 17.0867 | 16.7255 | 16.2408 | 15.6969 | 15.0306 | 14.3561 | 12.0367 | 10.8602 | 10.3286 | 3.4541 | 19.0327 | 18.7327 | 18.4592 | 18.0867 | 17.5765 | 16.9276 | 16.1214 | 15.3265 | 13.0143 | 12.2163 | 12.3816
|  | ALRESFORD PRIMARY | HT |  |  |  |  | 1.5592 | 19.3439 | 19.0122 | 18.7031 | 18.2143 | 17.5653 | 16.9122 | 16.1306 | 15.2949 | 12.9633 | 11.8184 | 11.6653 | 6 | 17.6286 | 17.3133 | 17.0327 | 16.5969 | 16.0316 | 15.4418 | 14.7224 | 13.9418 | 11.7449 | 10.9888 | 11.0765 | 3.4561 | 19.0378 | 18.7153 | 18.3939 | 17.9112 | 17.3184 | 16.699 | 15.9561 | 15.1133 | 12.748 | 11.9969 | 12.0612
|  | ALRESFORD PRIMARY | HE |  |  |  |  | 1.5582 | 19.3408 | 19.0265 | 18.7571 | 18.3867 | 17.7806 | 17.1949 | 16.4847 | 15.75 | 14.0867 | 12.9694 | 12.5173 | 6.001 | 17.6265 | 17.3276 | 17.0827 | 16.752 | 16.2255 | 15.7 | 15.052 | 14.3827 | 12.5531 | 11.4531 | 10.6622 | 3.4561 | 19.0347 | 18.7316 | 18.451 | 18.1041 | 17.5429 | 16.9112 | 16.1245 | 15.3306 | 13.5092 | 12.752 | 12.6378
|  | ALRESFORD PRIMARY | FB |  |  |  |  | 1.7541 | 19.5194 | 19.5612 | 19.6367 | 19.3704 | 19.2051 | 19.0561 | 18.9041 | 18.6735 | 17.0592 | 15.3633 | 14.2092 | 6.1541 | 17.7306 | 17.6888 | 17.7082 | 17.4276 | 17.1765 | 16.9286 | 16.6867 | 16.3704 | 14.2663 | 11.7908 | 9.2286 | 3.6704 | 19.2286 | 19.2531 | 19.3143 | 19.0388 | 18.85 | 18.6847 | 18.5235 | 18.2816 | 16.3531 | 14.551 | 13.5429
FLEET-BRAMLEY GSP | ALTON BSP | ALTON LOCAL PRIMARY | MINIMUM HEADROOM | SU 72434 39606 | NO | NO | 6.559 | 21.0269 | 20.3014 | 19.5749 | 19.1841 | 18.5851 | 17.7667 | 16.6382 | 15.5402 | 14.4535 | 10.8167 | 8.6739 | 8.0086 | 27.932 | 27.1035 | 26.3116 | 25.8259 | 25.1157 | 24.2851 | 23.08 | 21.9555 | 20.8535 | 17.1759 | 14.9086 | 9.7708 | 24.0055 | 23.229 | 22.4831 | 22.0198 | 21.3137 | 20.4739 | 19.2453 | 18.1055 | 16.981 | 13.0933 | 11.3504 | 10.9045
|  | ALTON LOCAL PRIMARY | EE |  |  |  |  | 21.0269 | 20.3055 | 19.7024 | 19.5137 | 19.1524 | 18.579 | 17.7035 | 16.8667 | 16.0371 | 12.48 | 10.129 | 9.1178 | 27.9331 | 27.1076 | 26.38 | 26.0065 | 25.4402 | 24.7331 | 23.6698 | 22.6943 | 21.7371 | 17.5504 | 14.9086 | 12.979 | 24.0065 | 23.2331 | 22.58 | 22.2678 | 21.7586 | 21.0963 | 20.0586 | 19.0198 | 17.8198 | 13.8167 | 12.1984 | 11.432
|  | ALTON LOCAL PRIMARY | HT |  |  |  |  | 21.028 | 20.3024 | 19.5749 | 19.1841 | 18.5851 | 17.7667 | 16.6382 | 15.5402 | 14.4535 | 10.8167 | 8.6739 | 8.0086 | 27.9341 | 27.1035 | 26.3116 | 25.8259 | 25.1157 | 24.2851 | 23.08 | 21.9555 | 20.8535 | 17.1759 | 15.4014 | 14.9861 | 24.0055 | 23.229 | 22.4831 | 22.0198 | 21.3137 | 20.4739 | 19.2453 | 18.1055 | 16.981 | 13.0933 | 11.3504 | 10.9045
|  | ALTON LOCAL PRIMARY | HE |  |  |  |  | 21.0269 | 20.3014 | 19.7035 | 19.5269 | 19.1371 | 18.6035 | 17.7657 | 16.9473 | 16.1749 | 13.1943 | 11.3647 | 10.4831 | 27.932 | 27.1045 | 26.38 | 26.029 | 25.4259 | 24.7402 | 23.6933 | 22.7116 | 21.7871 | 18.0861 | 15.8045 | 13.8616 | 24.0055 | 23.23 | 22.58 | 22.2902 | 21.7412 | 21.1157 | 20.1076 | 19.0331 | 17.8739 | 14.2851 | 12.9647 | 12.6555
|  | ALTON LOCAL PRIMARY | FB |  |  |  |  | 21.2524 | 20.7555 | 20.3239 | 20.4341 | 20.5055 | 20.3708 | 20.1912 | 19.9178 | 19.6218 | 17.3698 | 14.3157 | 12.3157 | 28.0647 | 27.3984 | 26.7831 | 26.6351 | 26.4269 | 25.9922 | 25.4922 | 24.9096 | 24.3218 | 20.3392 | 15.1239 | 9.7708 | 24.2096 | 23.6688 | 23.1484 | 23.1341 | 23.0698 | 22.9106 | 22.6973 | 22.3647 | 21.9973 | 18.8606 | 15.4341 | 13.6994
MELKSHAM GSP | ANDOVER BSP | ANDOVER PRIMARY | MINIMUM HEADROOM | SU 35240 46643 | NO | NO | 2.339 | 21.9868 | 21.7756 | 21.1501 | 20.2256 | 19.1971 | 17.9185 | 16.6511 | 15.445 | 14.3307 | 11.1215 | 9.496 | 8.6185 | 24.2124 | 24.0868 | 23.8573 | 23.4828 | 23.0522 | 22.5154 | 21.9573 | 21.3909 | 20.8705 | 18.8266 | 17.7297 | 15.2511 | 22.8522 | 22.7113 | 22.3215 | 21.6644 | 20.9266 | 20.0124 | 19.0889 | 18.1858 | 17.3603 | 14.7654 | 13.5307 | 12.9787
|  | ANDOVER PRIMARY | EE |  |  |  |  | 21.9868 | 21.7756 | 21.1501 | 20.2256 | 19.1971 | 17.9185 | 16.6511 | 15.445 | 14.3307 | 11.1215 | 9.496 | 8.6185 | 24.2124 | 24.0879 | 23.8573 | 23.4828 | 23.0522 | 22.5205 | 21.9634 | 21.3909 | 20.8705 | 18.8266 | 17.7358 | 16.9083 | 22.8522 | 22.7113 | 22.3215 | 21.6644 | 20.9266 | 20.0124 | 19.0889 | 18.1858 | 17.3603 | 14.7654 | 13.5307 | 12.9787
|  | ANDOVER PRIMARY | HT |  |  |  |  | 21.9879 | 21.7817 | 21.1756 | 20.293 | 19.3175 | 18.0909 | 16.8746 | 15.7603 | 14.7481 | 11.4246 | 9.6981 | 8.8011 | 24.2134 | 24.0868 | 23.8583 | 23.4868 | 23.0613 | 22.5307 | 21.9634 | 21.4083 | 20.895 | 19.1981 | 18.5103 | 18.2889 | 22.8552 | 22.7185 | 22.3399 | 21.7011 | 20.9909 | 20.1032 | 19.1981 | 18.3522 | 17.5807 | 14.9777 | 13.7236 | 13.2103
|  | ANDOVER PRIMARY | HE |  |  |  |  | 21.9909 | 21.7838 | 21.1593 | 20.296 | 19.2328 | 17.9583 | 16.7032 | 15.5175 | 14.4154 | 11.6644 | 10.2562 | 9.4848 | 24.2134 | 24.0868 | 23.8573 | 23.5328 | 23.0522 | 22.5154 | 21.9573 | 21.394 | 20.8736 | 19.0909 | 17.9868 | 17.0644 | 22.8562 | 22.7195 | 22.3328 | 21.7328 | 20.944 | 20.0307 | 19.1164 | 18.2287 | 17.4113 | 15.244 | 14.1644 | 13.642
|  | ANDOVER PRIMARY | FB |  |  |  |  | 22.1511 | 22.0491 | 21.5695 | 20.9817 | 20.3613 | 19.695 | 18.8134 | 18.1726 | 17.5562 | 15.3715 | 13.844 | 12.7001 | 24.295 | 24.1981 | 23.9797 | 23.7389 | 23.4675 | 23.1766 | 22.6297 | 22.2654 | 21.8787 | 19.9062 | 17.7297 | 15.2511 | 23.0032 | 22.9328 | 22.6562 | 22.2848 | 21.8603 | 21.4246 | 20.7287 | 20.2654 | 19.7991 | 17.9562 | 16.5532 | 15.5062
MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST PRIMARY | MINIMUM HEADROOM | SU 37953 46433 | NO | NO | 6.363 | 6.7298 | 6.238 | 5.8533 | 5.4064 | 4.939 | 4.5584 | 3.9574 | 3.3094 | 2.6451 | -0.87731 | -3.5365 | -5.1151 | 9.5788 | 9.1104 | 8.7747 | 8.3309 | 7.8431 | 7.3972 | 6.8156 | 6.2319 | 5.6247 | 2.6788 | 0.42167 | -3.3896 | 7.4145 | 7.0278 | 6.7074 | 6.3094 | 5.9339 | 5.6533 | 5.2186 | 4.7247 | 4.0849 | 0.77065 | -1.5885 | -2.9457
|  | ANDOVER EAST PRIMARY | EE |  |  |  |  | 6.736 | 6.4758 | 6.087 | 5.6421 | 5.1023 | 4.5635 | 3.9737 | 3.3094 | 2.6451 | -0.81506 | -3.5365 | -5.1151 | 9.5911 | 9.3196 | 8.986 | 8.538 | 7.988 | 7.4166 | 6.8451 | 6.2492 | 5.6451 | 2.6788 | 0.42167 | -1.3436 | 7.4196 | 7.2768 | 6.9533 | 6.5574 | 6.1104 | 5.6553 | 5.2268 | 4.7278 | 4.0849 | 0.85943 | -1.5885 | -2.9457
|  | ANDOVER EAST PRIMARY | HT |  |  |  |  | 6.7441 | 6.238 | 5.8533 | 5.4064 | 4.939 | 4.5584 | 3.9574 | 3.3094 | 2.6533 | -0.87731 | -3.2498 | -4.462 | 9.5911 | 9.1104 | 8.7747 | 8.3309 | 7.8431 | 7.3972 | 6.8156 | 6.2319 | 5.6247 | 3.0207 | 1.6023 | 0.98392 | 7.4268 | 7.0278 | 6.7074 | 6.3094 | 5.9339 | 5.6533 | 5.2186 | 4.7247 | 4.0849 | 0.77065 | -1.26 | -2.1977
|  | ANDOVER EAST PRIMARY | HE |  |  |  |  | 6.7298 | 6.4911 | 6.1115 | 5.6574 | 5.1094 | 4.6033 | 4.0472 | 3.4268 | 2.7921 | -0.12118 | -1.9324 | -2.964 | 9.5788 | 9.3196 | 8.986 | 8.537 | 7.9809 | 7.4217 | 6.8431 | 6.2676 | 5.6594 | 3.0278 | 1.2135 | -0.25792 | 7.4145 | 7.29 | 6.9747 | 6.5686 | 6.1135 | 5.6788 | 5.2645 | 4.8043 | 4.1778 | 1.5053 | -0.095673 | -0.92629
|  | ANDOVER EAST PRIMARY | FB |  |  |  |  | 6.8778 | 6.8513 | 6.6115 | 6.3339 | 6.1094 | 5.7676 | 5.3472 | 4.9941 | 4.6656 | 2.4084 | -0.14771 | -1.9957 | 9.6196 | 9.5492 | 9.2737 | 8.939 | 8.6288 | 8.1809 | 7.6717 | 7.2319 | 6.8186 | 4.0492 | 0.43698 | -3.3896 | 7.5451 | 7.5625 | 7.44 | 7.1747 | 6.9502 | 6.6207 | 6.287 | 6.0656 | 5.8472 | 4.0094 | 1.5156 | -0.25282
MELKSHAM GSP | ANDOVER BSP | ANDOVER TOWN PRIMARY | MINIMUM HEADROOM | SU 36207 45078 | NO | NO | 0.763 | 6.5056 | 6.527 | 6.525 | 6.4668 | 6.3148 | 5.9791 | 5.4617 | 4.9352 | 4.4179 | 2.3209 | 0.4852 | -0.70357 | 7.052 | 7.051 | 7.0092 | 6.9133 | 6.7551 | 6.5551 | 6.348 | 6.1153 | 5.8786 | 4.3327 | 2.9255 | 0.43878 | 7.4133 | 7.4143 | 7.3847 | 7.3286 | 7.1235 | 6.7724 | 6.3929 | 5.9939 | 5.5857 | 3.7286 | 2.5102 | 1.8082
|  | ANDOVER TOWN PRIMARY | EE |  |  |  |  | 6.5056 | 6.5291 | 6.525 | 6.4883 | 6.3291 | 5.9791 | 5.4617 | 4.9352 | 4.4179 | 2.3209 | 0.60459 | -0.52704 | 7.0541 | 7.052 | 7.0092 | 6.952 | 6.7643 | 6.5745 | 6.3582 | 6.1194 | 5.8939 | 4.3327 | 3.2745 | 2.3418 | 7.4133 | 7.4153 | 7.3847 | 7.4041 | 7.1408 | 6.7939 | 6.3929 | 5.9939 | 5.5857 | 3.7286 | 2.5102 | 1.8082
|  | ANDOVER TOWN PRIMARY | HT |  |  |  |  | 6.5066 | 6.527 | 6.5383 | 6.4934 | 6.3413 | 5.9964 | 5.5036 | 5.0158 | 4.5311 | 2.3811 | 0.4852 | -0.70357 | 7.0541 | 7.052 | 7.0163 | 6.951 | 6.7684 | 6.5551 | 6.348 | 6.1153 | 5.8796 | 4.752 | 4.0214 | 3.798 | 7.4143 | 7.4143 | 7.4 | 7.4082 | 7.152 | 6.7724 | 6.402 | 6.0337 | 5.6214 | 3.9204 | 2.6071 | 2.0082
|  | ANDOVER TOWN PRIMARY | HE |  |  |  |  | 6.5097 | 6.5342 | 6.5485 | 6.4668 | 6.3148 | 5.9832 | 5.4719 | 4.9668 | 4.4505 | 2.6209 | 1.0821 | 0.18622 | 7.052 | 7.051 | 7.0133 | 6.9133 | 6.7551 | 6.5806 | 6.3551 | 6.1173 | 5.8786 | 4.5051 | 3.3888 | 2.4745 | 7.4163 | 7.4184 | 7.4041 | 7.3286 | 7.1235 | 6.8265 | 6.4143 | 6.0276 | 5.6 | 4.0582 | 2.9031 | 2.3694
|  | ANDOVER TOWN PRIMARY | FB |  |  |  |  | 6.6015 | 6.6638 | 6.7066 | 6.7332 | 6.727 | 6.7311 | 6.6781 | 6.6107 | 6.5362 | 5.5944 | 4.2964 | 3.374 | 7.1367 | 7.1561 | 7.1755 | 7.1582 | 7.1265 | 7.101 | 7.0306 | 6.95 | 6.8551 | 5.2255 | 2.9255 | 0.43878 | 7.5551 | 7.6133 | 7.6531 | 7.6622 | 7.6531 | 7.6469 | 7.5918 | 7.5204 | 7.4408 | 6.4459 | 5.0306 | 4.2112
BRAMLEY (BASI) GSP | READING BSP | ARBORFIELD PRIMARY | MINIMUM HEADROOM | SU 75949 65766 | NO | NO | 9.793 | 5.827 | 5.7821 | 5.5158 | 5.0596 | 4.3433 | 3.5392 | 2.6341 | 1.6331 | 0.53106 | -3.0649 | -5.0996 | -6.0026 | 8.779 | 8.6851 | 8.43 | 8.077 | 7.476 | 6.7831 | 6.0382 | 5.2025 | 4.2555 | 1.0392 | -0.75568 | -1.7904 | 7.0055 | 6.9321 | 6.6586 | 6.2351 | 5.5392 | 4.7586 | 3.9168 | 2.9729 | 1.9004 | -1.5383 | -3.3955 | -4.324
|  | ARBORFIELD PRIMARY | EE |  |  |  |  | 5.827 | 5.7892 | 5.5413 | 5.1219 | 4.4494 | 3.6851 | 2.8066 | 1.8372 | 0.78514 | -2.8812 | -5.0179 | -6.0026 | 8.78 | 8.6902 | 8.4474 | 8.1127 | 7.5402 | 6.8719 | 6.1474 | 5.328 | 4.4168 | 1.0994 | -0.75568 | -1.7904 | 7.0076 | 6.9372 | 6.678 | 6.2831 | 5.6229 | 4.8749 | 4.0535 | 3.1321 | 2.1035 | -1.423 | -3.3863 | -4.324
|  | ARBORFIELD PRIMARY | HT |  |  |  |  | 5.827 | 5.7821 | 5.5158 | 5.0596 | 4.3433 | 3.5392 | 2.6341 | 1.6331 | 0.53106 | -3.0649 | -5.0996 | -5.9496 | 8.779 | 8.6851 | 8.43 | 8.077 | 7.476 | 6.7831 | 6.0382 | 5.2025 | 4.2555 | 1.0392 | -0.64751 | -1.3496 | 7.0055 | 6.9321 | 6.6586 | 6.2351 | 5.5392 | 4.7586 | 3.9168 | 2.9729 | 1.9004 | -1.5383 | -3.3955 | -4.1751
|  | ARBORFIELD PRIMARY | HE |  |  |  |  | 5.828 | 5.7892 | 5.5413 | 5.1158 | 4.4362 | 3.6668 | 2.8106 | 1.827 | 0.77289 | -2.2087 | -4.0802 | -4.9577 | 8.779 | 8.6892 | 8.4443 | 8.1096 | 7.5321 | 6.8576 | 6.1535 | 5.3219 | 4.4117 | 1.8994 | 0.33208 | -0.70364 | 7.0066 | 6.9372 | 6.678 | 6.278 | 5.6106 | 4.8566 | 4.0596 | 3.1239 | 2.0964 | -0.62302 | -2.2761 | -3.0761
|  | ARBORFIELD PRIMARY | FB |  |  |  |  | 5.9964 | 5.979 | 5.8086 | 5.4535 | 5.0688 | 4.7158 | 4.1045 | 3.5515 | 2.9117 | -0.026086 | -2.5904 | -4.3118 | 8.9137 | 8.8188 | 8.6249 | 8.3474 | 8.0494 | 7.7637 | 7.2637 | 6.8372 | 6.3249 | 3.6678 | 0.97493 | -1.5812 | 7.1668 | 7.1106 | 6.93 | 6.6158 | 6.2851 | 5.9851 | 5.4402 | 4.9749 | 4.4147 | 1.7127 | -0.69751 | -2.4791
LOVEDEAN GSP | CHICHESTER BSP | ARGYLE ROAD PRIMARY | MINIMUM HEADROOM | SZ 93193 99152 | NO | YES | 0.852 | 12.6929 | 12.7888 | 12.9214 | 12.8061 | 12.6184 | 12.1704 | 11.5776 | 10.9878 | 10.4 | 7.65 | 5.0745 | 3.7704 | 21.6061 | 21.6214 | 21.6276 | 21.552 | 21.3816 | 21.0806 | 20.6265 | 20.1959 | 19.7398 | 17.7724 | 14.302 | 9.4357 | 15.7092 | 15.75 | 15.7867 | 15.6735 | 15.4429 | 15.0571 | 14.5041 | 13.9847 | 13.4429 | 11.1776 | 9.2235 | 8.2143
|  | ARGYLE ROAD PRIMARY | EE |  |  |  |  | 12.6929 | 12.7888 | 12.9214 | 12.8061 | 12.6398 | 12.1704 | 11.5908 | 11.0418 | 10.4867 | 8.052 | 5.5847 | 4.0837 | 21.6061 | 21.6245 | 21.6582 | 21.5684 | 21.4031 | 21.1306 | 20.7082 | 20.3245 | 19.9122 | 17.7724 | 15.8092 | 13.8214 | 15.7092 | 15.75 | 15.7867 | 15.6847 | 15.4592 | 15.0806 | 14.5469 | 14.0735 | 13.5745 | 11.4469 | 9.5255 | 8.4204
|  | ARGYLE ROAD PRIMARY | HT |  |  |  |  | 12.699 | 12.8061 | 12.9582 | 12.8265 | 12.6439 | 12.1704 | 11.5776 | 10.9878 | 10.4 | 7.65 | 5.0745 | 3.7704 | 21.6071 | 21.6214 | 21.6541 | 21.552 | 21.3816 | 21.0806 | 20.6265 | 20.1959 | 19.7398 | 18.2143 | 17.1122 | 16.5439 | 15.7163 | 15.7694 | 15.8163 | 15.6929 | 15.4541 | 15.0571 | 14.5041 | 13.9847 | 13.4429 | 11.1776 | 9.2235 | 8.2143
|  | ARGYLE ROAD PRIMARY | HE |  |  |  |  | 12.7082 | 12.8316 | 12.9612 | 12.8184 | 12.6184 | 12.1939 | 11.6541 | 11.152 | 10.6112 | 8.8194 | 6.7398 | 5.5337 | 21.6133 | 21.6327 | 21.6724 | 21.5816 | 21.4071 | 21.1408 | 20.7194 | 20.3612 | 19.9367 | 18.0398 | 16.0469 | 14.0592 | 15.7173 | 15.7541 | 15.7918 | 15.6735 | 15.4429 | 15.0908 | 14.5827 | 14.1561 | 13.6561 | 12.1092 | 10.4633 | 9.5531
|  | ARGYLE ROAD PRIMARY | FB |  |  |  |  | 12.8653 | 13.0337 | 13.1612 | 13.2796 | 13.4082 | 13.4082 | 13.3837 | 13.3357 | 13.2724 | 12.2867 | 10.1388 | 8.5735 | 21.6398 | 21.6469 | 21.6276 | 21.5888 | 21.5408 | 21.3673 | 21.1592 | 20.8908 | 20.598 | 18.1878 | 14.302 | 9.4357 | 15.8347 | 15.9296 | 16.0031 | 16.0265 | 16.0541 | 16.0204 | 15.9694 | 15.902 | 15.7949 | 14.752 | 12.7133 | 11.2939
COWLEY GSP | HEADINGTON BSP | ARNCOTT PRIMARY | MINIMUM HEADROOM | SP 60730 18095 | NO | NO | 16.941 | 2.1087 | 1.6158 | 1.1464 | 0.39437 | -1.7169 | -5.922 | -7.6209 | -9.1822 | -13.4291 | -15.9087 | -17.0505 | -17.1005 | 3.458 | 3.0825 | 2.6846 | 2.1499 | 0.30192 | -3.8216 | -5.2562 | -6.5736 | -11.2818 | -12.7777 | -13.3052 | -13.2807 | 2.0076 | 1.5158 | 1.0719 | 0.59845 | -1.4954 | -5.6873 | -7.2128 | -8.6107 | -13.1209 | -14.9342 | -15.6352 | -15.5985
|  | ARNCOTT PRIMARY | EE |  |  |  |  | 2.2199 | 1.8087 | 1.4811 | 1.0117 | 0.63008 | -3.8107 | -5.1271 | -6.5128 | -10.8311 | -14.2893 | -15.2526 | -15.3413 | 3.5315 | 3.2305 | 2.9387 | 2.5264 | 2.2019 | -2.1236 | -3.3726 | -4.6144 | -9.3175 | -12.0634 | -12.5471 | -12.6542 | 2.1209 | 1.7107 | 1.374 | 0.99539 | 0.71886 | -3.7893 | -5.0618 | -6.3607 | -10.7954 | -13.8464 | -14.4138 | -14.3852
|  | ARNCOTT PRIMARY | HT |  |  |  |  | 2.1087 | 1.6158 | 1.1464 | 0.39437 | -1.7169 | -5.922 | -7.6209 | -9.1822 | -13.4291 | -15.9087 | -17.0505 | -17.1005 | 3.458 | 3.0825 | 2.6846 | 2.1499 | 0.30192 | -3.8216 | -5.2562 | -6.5736 | -11.2818 | -12.7777 | -13.3052 | -13.2807 | 2.0076 | 1.5158 | 1.0719 | 0.59845 | -1.4954 | -5.6873 | -7.2128 | -8.6107 | -13.1209 | -14.9342 | -15.6352 | -15.5985
|  | ARNCOTT PRIMARY | HE |  |  |  |  | 2.2199 | 1.8076 | 1.4791 | 1.0087 | 0.66171 | -3.8546 | -5.2128 | -6.5638 | -10.9087 | -14.0026 | -15.1485 | -15.2536 | 3.5315 | 3.2305 | 2.9387 | 2.5254 | 2.255 | -2.1634 | -3.4542 | -4.6991 | -9.4032 | -11.9348 | -12.4889 | -12.6389 | 2.1209 | 1.7107 | 1.374 | 0.99437 | 0.72804 | -3.8301 | -5.1424 | -6.4352 | -10.8638 | -13.6801 | -14.3526 | -14.3454
|  | ARNCOTT PRIMARY | FB |  |  |  |  | 2.2913 | 1.9015 | 1.5862 | 1.3107 | 1.0301 | -2.5913 | -4.1985 | -5.0138 | -8.9975 | -13.1322 | -14.3903 | -14.6903 | 3.5897 | 3.305 | 3.0233 | 2.7754 | 2.5397 | -0.80318 | -2.3909 | -3.1777 | -7.6716 | -11.2736 | -12.2736 | -12.9246 | 2.1842 | 1.7933 | 1.475 | 1.1974 | 0.93722 | -2.6516 | -4.223 | -5.0148 | -9.074 | -12.9056 | -13.9332 | -14.0689
FLEET-BRAMLEY GSP | BRACKNELL BSP | ASCOT PRIMARY | MINIMUM HEADROOM | SU 91615 68855 | NO | NO | 2.382 | 16.0081 | 15.7693 | 15.7101 | 15.154 | 14.6673 | 14.1346 | 13.6469 | 13.0581 | 12.5009 | 10.1152 | 8.3479 | 7.5458 | 18.6275 | 18.3336 | 18.2622 | 17.8856 | 17.5346 | 17.1581 | 16.7479 | 16.2652 | 15.8173 | 14.002 | 11.9713 | 8.9173 | 16.9152 | 16.6081 | 16.5397 | 16.0805 | 15.653 | 15.1989 | 14.7356 | 14.1785 | 13.6703 | 11.505 | 10.104 | 9.6122
|  | ASCOT PRIMARY | EE |  |  |  |  | 16.0081 | 15.7693 | 15.754 | 15.3652 | 14.9775 | 14.5091 | 13.9632 | 13.4173 | 12.9142 | 10.7305 | 9.0071 | 8.1244 | 18.6285 | 18.3336 | 18.2877 | 17.9754 | 17.6448 | 17.2948 | 16.8703 | 16.4264 | 16.0224 | 14.002 | 12.5397 | 11.3775 | 16.9152 | 16.6081 | 16.5785 | 16.2264 | 15.852 | 15.4367 | 14.9428 | 14.4234 | 13.9591 | 11.8877 | 10.454 | 9.8387
|  | ASCOT PRIMARY | HT |  |  |  |  | 16.0101 | 15.7724 | 15.7101 | 15.154 | 14.6673 | 14.1346 | 13.6469 | 13.0581 | 12.5009 | 10.1152 | 8.3479 | 7.5458 | 18.6275 | 18.3336 | 18.2622 | 17.8856 | 17.5346 | 17.1581 | 16.7479 | 16.2652 | 15.8173 | 14.1132 | 13.2162 | 12.9009 | 16.9173 | 16.6091 | 16.5397 | 16.0805 | 15.653 | 15.1989 | 14.7356 | 14.1785 | 13.6703 | 11.505 | 10.104 | 9.6122
|  | ASCOT PRIMARY | HE |  |  |  |  | 16.0244 | 15.805 | 15.804 | 15.4203 | 15.0142 | 14.5754 | 14.0652 | 13.504 | 13.0183 | 11.1346 | 9.6907 | 9.0632 | 18.6356 | 18.3479 | 18.3101 | 18.005 | 17.6683 | 17.3203 | 16.8989 | 16.4397 | 16.0224 | 14.0969 | 12.703 | 11.5836 | 16.9285 | 16.6326 | 16.6183 | 16.2713 | 15.8805 | 15.4826 | 15.004 | 14.4754 | 14.0162 | 12.204 | 11.0244 | 10.6224
|  | ASCOT PRIMARY | FB |  |  |  |  | 16.1887 | 16.1897 | 16.2091 | 16.0162 | 15.7132 | 15.603 | 15.4326 | 15.2877 | 15.1234 | 14.0213 | 12.2316 | 11.2132 | 18.6897 | 18.6142 | 18.5407 | 18.3622 | 18.006 | 17.7724 | 17.4693 | 17.1724 | 16.853 | 14.8979 | 11.9713 | 8.9173 | 17.053 | 17.0418 | 17.0377 | 16.8836 | 16.5785 | 16.4734 | 16.2877 | 16.1091 | 15.9101 | 14.7193 | 12.9356 | 11.9948
LOVEDEAN GSP | CHICHESTER BSP | ASHLING ROAD PRIMARY | MINIMUM HEADROOM | SU 84085 06737 | NO | YES | 11.308 | -2.1659 | -2.4618 | -2.9179 | 8.3821 | 7.4331 | 5.6719 | 3.7117 | 1.8474 | 0.024939 | -7.1526 | -12.0444 | -14.6761 | -4.4322 | -4.6404 | -4.9506 | 7.677 | 7.0739 | 6.3004 | 5.377 | 4.4739 | 3.6137 | 0.51576 | -1.4424 | -5.8424 | -3.6771 | -3.874 | -4.1873 | 7.3678 | 6.6953 | 5.6545 | 4.5025 | 3.3872 | 2.0821 | -3.5761 | -6.9628 | -8.4261
|  | ASHLING ROAD PRIMARY | EE |  |  |  |  | -2.1516 | -2.3822 | -2.721 | 8.7504 | 7.9943 | 6.3045 | 4.4004 | 2.6566 | 0.94841 | -5.6587 | -10.4567 | -13.0842 | -4.423 | -4.5934 | -4.8373 | 7.8953 | 7.4362 | 6.7596 | 5.9545 | 5.18 | 4.4464 | 1.5504 | -1.4424 | -3.6373 | -3.6669 | -3.8169 | -4.0322 | 7.6678 | 7.1647 | 6.2433 | 5.2107 | 4.2504 | 2.9453 | -2.3455 | -5.8638 | -7.5761
|  | ASHLING ROAD PRIMARY | HT |  |  |  |  | -2.1659 | -2.4618 | -2.9179 | 8.3821 | 7.4331 | 5.6719 | 3.7117 | 1.8474 | 0.024939 | -7.1526 | -12.0444 | -14.6761 | -4.4322 | -4.6404 | -4.9506 | 7.677 | 7.0739 | 6.3004 | 5.377 | 4.4739 | 3.6137 | 0.51576 | -1.0863 | -1.6842 | -3.6771 | -3.874 | -4.1873 | 7.3678 | 6.6953 | 5.6545 | 4.5025 | 3.3872 | 2.0821 | -3.5761 | -6.9628 | -8.4261
|  | ASHLING ROAD PRIMARY | HE |  |  |  |  | -2.1444 | -2.373 | -2.7047 | 8.6862 | 7.8494 | 6.128 | 4.1627 | 2.3413 | 0.57188 | -4.7036 | -8.8098 | -10.7138 | -4.422 | -4.5975 | -4.8383 | 7.8862 | 7.4127 | 6.7392 | 5.9219 | 5.1392 | 4.4035 | 1.7668 | -0.71384 | -2.7944 | -3.6649 | -3.8118 | -4.0261 | 7.6382 | 7.0984 | 6.1668 | 5.1117 | 4.1035 | 2.7443 | -1.5832 | -4.5138 | -5.7506
|  | ASHLING ROAD PRIMARY | FB |  |  |  |  | -1.8108 | -1.7751 | -1.8312 | 10.1504 | 9.9515 | 9.48 | 8.9249 | 8.4688 | 7.9872 | 4.7647 | 0.4678 | -1.6914 | -4.1791 | -4.1914 | -4.2965 | 8.6913 | 8.5198 | 8.2402 | 7.8984 | 7.5933 | 7.2749 | 5.0464 | -0.59853 | -5.8424 | -3.4373 | -3.4424 | -3.4791 | 8.529 | 8.3545 | 8.0321 | 7.6566 | 7.3576 | 7.0311 | 5.0086 | 1.6362 | -0.25771
MELKSHAM GSP | NORRINGTON BSP | ASHTON PARK PRIMARY | MINIMUM HEADROOM | ST 87141 57741 | NO | YES | 19.333 | -7.4686 | -7.9288 | -8.4768 | -9.5798 | -11.1819 | -13.4023 | 16.261 | 13.4498 | 10.6232 | 1.5008 | -4.1747 | -7.5788 | 1.9783 | 1.6896 | 1.2906 | 0.68446 | -0.29922 | -1.3737 | 25.8457 | 24.3916 | 22.9385 | 18.5171 | 16.3171 | 13.8518 | -5.3329 | -5.687 | -6.1594 | -6.9911 | -8.2513 | -10.0462 | 18.2681 | 16.0824 | 13.9314 | 7.1253 | 3.3549 | 1.4487
|  | ASHTON PARK PRIMARY | EE |  |  |  |  | -7.4686 | -7.9278 | -8.4615 | -9.49 | -11.1727 | -13.3268 | 16.51 | 14.0559 | 11.7038 | 3.114 | -2.1676 | -5.3829 | 1.9783 | 1.6896 | 1.3018 | 0.73956 | -0.29411 | -1.3268 | 26.0436 | 24.7804 | 23.5702 | 18.7681 | 16.3171 | 14.8171 | -5.3329 | -5.687 | -6.14 | -6.8992 | -8.2411 | -9.9247 | 18.5589 | 16.6079 | 14.7518 | 8.1753 | 4.5069 | 2.511
|  | ASHTON PARK PRIMARY | HT |  |  |  |  | -7.4686 | -7.9237 | -8.4768 | -9.5798 | -11.1033 | -13.4023 | 16.261 | 13.4498 | 10.6232 | 1.5008 | -4.1747 | -7.5788 | 1.9794 | 1.6906 | 1.2906 | 0.68446 | -0.22881 | -1.3737 | 25.8457 | 24.3916 | 22.9385 | 18.5171 | 16.7212 | 16.262 | -5.3319 | -5.6819 | -6.1594 | -6.9911 | -8.2247 | -10.0462 | 18.2681 | 16.0824 | 13.9314 | 7.1253 | 3.3549 | 1.4487
|  | ASHTON PARK PRIMARY | HE |  |  |  |  | -7.4686 | -7.9288 | -8.4645 | -9.4982 | -11.1819 | -13.3502 | 16.4569 | 13.9671 | 11.5824 | 3.9967 | -0.94411 | -3.3084 | 1.9783 | 1.6906 | 1.3018 | 0.73548 | -0.29922 | -1.3206 | 26.0396 | 24.7722 | 23.5569 | 19.314 | 16.964 | 15.6579 | -5.3319 | -5.6849 | -6.1421 | -6.9074 | -8.2513 | -9.9349 | 18.5375 | 16.5681 | 14.6916 | 8.911 | 5.4743 | 4.0406
|  | ASHTON PARK PRIMARY | FB |  |  |  |  | -7.1615 | -7.3911 | -7.6247 | -8.1594 | -9.3196 | -10.4247 | 20.7518 | 19.6661 | 18.6385 | 13.7722 | 9.76 | 7.3845 | 2.1089 | 1.964 | 1.9192 | 1.6702 | 0.90384 | 0.17731 | 28.0794 | 27.3304 | 26.5324 | 22.21 | 17.7283 | 13.8518 | -4.939 | -5.0319 | -5.0421 | -5.5125 | -6.4033 | -7.3094 | 22.2181 | 21.2896 | 20.3651 | 15.9192 | 12.2467 | 10.1947
FLEET-BRAMLEY GSP | BRACKNELL BSP | BAGSHOT PRIMARY | MINIMUM HEADROOM | SU 91122 63523 | NO | NO | 5.057 | 8.7701 | 8.8477 | 8.5681 | 8.3681 | 8.0844 | 7.6048 | 6.9915 | 6.3293 | 5.6558 | 4.0028 | 3.1619 | 3.1956 | 13.3528 | 13.3477 | 12.9711 | 12.6793 | 12.2895 | 11.7803 | 11.1221 | 10.4293 | 9.7109 | 7.8354 | 6.0609 | 2.664 | 10.4864 | 10.5293 | 10.1905 | 9.9538 | 9.6293 | 9.1456 | 8.515 | 7.8456 | 7.1538 | 5.4109 | 4.566 | 4.6221
|  | BAGSHOT PRIMARY | EE |  |  |  |  | 8.7711 | 8.8517 | 8.5926 | 8.4293 | 8.2701 | 7.8946 | 7.4109 | 6.9099 | 6.3813 | 4.7517 | 3.7813 | 3.5201 | 13.3548 | 13.3507 | 12.9874 | 12.7191 | 12.4272 | 11.9456 | 11.363 | 10.7783 | 10.1395 | 7.9487 | 6.4915 | 5.4099 | 10.4885 | 10.5334 | 10.2089 | 10.0048 | 9.7956 | 9.367 | 8.8354 | 8.2977 | 7.7232 | 5.9497 | 4.9742 | 4.7487
|  | BAGSHOT PRIMARY | HT |  |  |  |  | 8.7701 | 8.8477 | 8.5681 | 8.3681 | 8.0844 | 7.6048 | 6.9915 | 6.3293 | 5.6558 | 4.0028 | 3.1619 | 3.1956 | 13.3528 | 13.3477 | 12.9711 | 12.6793 | 12.2895 | 11.7803 | 11.1221 | 10.4293 | 9.7109 | 7.8354 | 7.0181 | 6.9732 | 10.4864 | 10.5293 | 10.1905 | 9.9538 | 9.6293 | 9.1456 | 8.515 | 7.8456 | 7.1538 | 5.4109 | 4.566 | 4.6221
|  | BAGSHOT PRIMARY | HE |  |  |  |  | 8.7711 | 8.8497 | 8.5926 | 8.4262 | 8.2466 | 7.8691 | 7.4262 | 6.914 | 6.3854 | 4.8619 | 4.1446 | 3.9344 | 13.3538 | 13.3477 | 12.9854 | 12.714 | 12.3987 | 11.9232 | 11.3772 | 10.7691 | 10.1323 | 8.0313 | 6.7905 | 5.6201 | 10.4874 | 10.5313 | 10.2089 | 9.9987 | 9.765 | 9.3456 | 8.8517 | 8.2966 | 7.7272 | 6.0701 | 5.366 | 5.163
|  | BAGSHOT PRIMARY | FB |  |  |  |  | 9.0119 | 9.0803 | 9.1058 | 9.2201 | 9.2813 | 9.2374 | 8.9732 | 8.7926 | 8.6568 | 7.314 | 5.6589 | 4.9038 | 13.5119 | 13.4487 | 13.3507 | 13.3385 | 13.2221 | 12.9895 | 12.5119 | 12.1426 | 11.8048 | 9.3079 | 6.0609 | 2.664 | 10.7232 | 10.7558 | 10.7497 | 10.8385 | 10.8579 | 10.7874 | 10.4589 | 10.2395 | 10.0691 | 8.5497 | 6.8211 | 6.0313
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BALL HILL PRIMARY | MINIMUM HEADROOM | SU 42417 63142 | NO | NO | 0.81 | 8.8184 | 8.8418 | 8.8224 | 8.7633 | 8.5694 | 8.3316 | 7.9102 | 7.1041 | 5.7765 | 4.4633 | 2.8306 | 1.1786 | 11.7143 | 11.7 | 11.6643 | 11.6122 | 11.4102 | 11.2612 | 10.8459 | 10.052 | 8.5459 | 7.0327 | 5.4551 | 3.498 | 10.0071 | 10.0122 | 9.9847 | 9.9184 | 9.7133 | 9.5357 | 9.1 | 8.2357 | 6.6898 | 5.2398 | 3.5918 | 1.7408
|  | BALL HILL PRIMARY | EE |  |  |  |  | 8.8184 | 8.8418 | 8.8224 | 8.7776 | 8.6796 | 8.3796 | 8.0786 | 7.6561 | 7.1378 | 5.8276 | 3.7265 | 2.8847 | 11.7153 | 11.702 | 11.6704 | 11.6255 | 11.5327 | 11.2867 | 11.0439 | 10.6582 | 10.1469 | 8.8663 | 6.6 | 5.7398 | 10.0071 | 10.0122 | 9.9867 | 9.9316 | 9.8398 | 9.5663 | 9.2929 | 8.8745 | 8.3327 | 7.0327 | 4.7388 | 3.9561
|  | BALL HILL PRIMARY | HT |  |  |  |  | 8.8204 | 8.8469 | 8.8286 | 8.7633 | 8.5694 | 8.3459 | 7.9224 | 7.4735 | 6.75 | 5.4051 | 3.3204 | 1.8755 | 11.7143 | 11.7031 | 11.6643 | 11.6122 | 11.4102 | 11.2612 | 10.8459 | 10.4061 | 9.6102 | 8.2327 | 6.2306 | 5.002 | 10.0071 | 10.0153 | 9.9847 | 9.9184 | 9.7133 | 9.5357 | 9.1 | 8.6316 | 7.8173 | 6.3878 | 4.1949 | 2.7786
|  | BALL HILL PRIMARY | HE |  |  |  |  | 8.8204 | 8.8449 | 8.8306 | 8.7653 | 8.6459 | 8.3316 | 7.9102 | 7.1041 | 5.7765 | 4.4633 | 2.8306 | 1.1786 | 11.7143 | 11.7 | 11.6714 | 11.6235 | 11.5286 | 11.2786 | 10.901 | 10.052 | 8.5459 | 7.0327 | 5.4551 | 3.498 | 10.0082 | 10.0133 | 9.9898 | 9.9439 | 9.8214 | 9.5378 | 9.1214 | 8.2357 | 6.6898 | 5.2398 | 3.5918 | 1.7408
|  | BALL HILL PRIMARY | FB |  |  |  |  | 8.9429 | 8.998 | 9.0551 | 9.0582 | 9.0806 | 9.0459 | 8.9745 | 8.9296 | 8.7224 | 7.6214 | 6.4857 | 5.6888 | 11.7847 | 11.7939 | 11.7959 | 11.7735 | 11.751 | 11.6745 | 11.5551 | 11.4643 | 11.1816 | 9.8102 | 8.2286 | 6.699 | 10.1041 | 10.1408 | 10.1673 | 10.1684 | 10.151 | 10.1173 | 10.0316 | 9.951 | 9.7112 | 8.5714 | 7.3316 | 6.401
MELKSHAM GSP | ANDOVER BSP | BARTON STACEY PRIMARY | MINIMUM HEADROOM | SU 42075 42720 | NO | NO | 0.57 | 7.4179 | 7.4413 | 7.4454 | 7.426 | 7.2515 | 7.1954 | 6.8566 | 6.2189 | 4.9342 | 3.7505 | 2.4842 | 0.97704 | 9.1255 | 9.1071 | 9.0745 | 9.0255 | 8.751 | 8.6867 | 8.2561 | 7.4857 | 5.9122 | 4.3571 | 2.7694 | 0.76939 | 8.0439 | 8.048 | 8.049 | 8.0071 | 7.8816 | 7.8051 | 7.4653 | 6.7378 | 5.1449 | 3.6214 | 2.1786 | 0.44286
|  | BARTON STACEY PRIMARY | EE |  |  |  |  | 7.4189 | 7.4434 | 7.4526 | 7.4372 | 7.3362 | 7.2485 | 7.0689 | 6.7423 | 6.3036 | 5.2485 | 3.377 | 2.7872 | 9.1276 | 9.1071 | 9.0776 | 9.0327 | 8.8684 | 8.7194 | 8.499 | 8.1112 | 7.5847 | 6.2296 | 3.8592 | 2.9663 | 8.0449 | 8.048 | 8.051 | 8.0122 | 7.9214 | 7.8235 | 7.6459 | 7.3449 | 6.8214 | 5.502 | 3.2898 | 2.6633
|  | BARTON STACEY PRIMARY | HT |  |  |  |  | 7.4179 | 7.4413 | 7.4454 | 7.426 | 7.2515 | 7.1954 | 6.8566 | 6.4668 | 5.7791 | 4.5821 | 2.8587 | 1.8281 | 9.1255 | 9.1071 | 9.0745 | 9.0255 | 8.751 | 8.6867 | 8.2561 | 7.7969 | 6.9673 | 5.5031 | 3.4449 | 2.1765 | 8.0439 | 8.048 | 8.049 | 8.0071 | 7.8816 | 7.8051 | 7.4653 | 7.0633 | 6.2184 | 4.7061 | 2.6878 | 1.5296
|  | BARTON STACEY PRIMARY | HE |  |  |  |  | 7.4189 | 7.4444 | 7.4495 | 7.4342 | 7.3393 | 7.2852 | 6.9372 | 6.2189 | 4.9342 | 3.7505 | 2.4842 | 0.97704 | 9.1276 | 9.1082 | 9.0755 | 9.0316 | 8.8673 | 8.7857 | 8.3592 | 7.4857 | 5.9122 | 4.3571 | 2.7694 | 0.76939 | 8.0449 | 8.048 | 8.051 | 8.0112 | 7.9224 | 7.8408 | 7.501 | 6.7378 | 5.1449 | 3.6214 | 2.1786 | 0.44286
|  | BARTON STACEY PRIMARY | FB |  |  |  |  | 7.4974 | 7.5403 | 7.5801 | 7.6158 | 7.6383 | 7.6179 | 7.5536 | 7.4709 | 7.3454 | 6.6862 | 5.7791 | 4.7689 | 9.1694 | 9.1745 | 9.1612 | 9.151 | 9.1296 | 9.0551 | 8.9347 | 8.7867 | 8.5755 | 7.5418 | 6.1367 | 4.3551 | 8.0959 | 8.1143 | 8.1316 | 8.1378 | 8.1429 | 8.1184 | 8.0408 | 7.9367 | 7.7245 | 6.9612 | 5.9806 | 4.8827
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | BASINGSTOKE PRIMARY | MINIMUM HEADROOM | SU 65155 52705 | NO | NO | 2.036 | 18.0469 | 17.9398 | 17.8776 | 17.6827 | 16.9418 | 16.0235 | 15.2347 | 14.4204 | 13.7163 | 10.3551 | 8.0031 | 6.7551 | 15.3765 | 15.2388 | 15.1582 | 15.0582 | 14.5041 | 13.9 | 13.2143 | 12.3602 | 11.7592 | 9.3418 | 7.6378 | 6.2306 | 15.2939 | 15.1765 | 15.0959 | 14.9459 | 14.3582 | 13.6724 | 12.9622 | 12.1959 | 11.4367 | 8.5704 | 6.6316 | 5.701
|  | BASINGSTOKE PRIMARY | EE |  |  |  |  | 18.049 | 18.0092 | 17.8786 | 17.7265 | 17.1367 | 16.2582 | 15.5602 | 14.7347 | 13.9378 | 10.3551 | 8.0031 | 6.7551 | 15.3796 | 15.3143 | 15.1633 | 15.0755 | 14.6337 | 14.1 | 13.4469 | 12.5878 | 11.9878 | 9.3418 | 7.6378 | 6.5265 | 15.2949 | 15.2469 | 15.0969 | 14.9724 | 14.5449 | 13.8867 | 13.2286 | 12.4255 | 11.651 | 8.5704 | 6.6316 | 5.701
|  | BASINGSTOKE PRIMARY | HT |  |  |  |  | 18.05 | 17.9398 | 17.8776 | 17.6827 | 16.9418 | 16.0235 | 15.2347 | 14.4204 | 13.7163 | 10.3827 | 8.0602 | 7.2143 | 15.3776 | 15.2388 | 15.1602 | 15.0582 | 14.5041 | 13.9 | 13.2143 | 12.3602 | 11.7592 | 9.601 | 8.3163 | 8.0367 | 15.298 | 15.1765 | 15.0959 | 14.9459 | 14.3582 | 13.6724 | 12.9622 | 12.1959 | 11.4367 | 8.6 | 6.7388 | 6.2245
|  | BASINGSTOKE PRIMARY | HE |  |  |  |  | 18.0469 | 18.0102 | 17.8806 | 17.702 | 17.1 | 16.202 | 15.5092 | 14.6714 | 13.8888 | 10.7724 | 9.4776 | 8.8102 | 15.3765 | 15.3102 | 15.1582 | 15.0684 | 14.6296 | 14.0622 | 13.4367 | 12.5408 | 11.951 | 9.5776 | 8.5796 | 7.6969 | 15.2939 | 15.251 | 15.099 | 14.9612 | 14.5224 | 13.8429 | 13.1949 | 12.3633 | 11.6122 | 8.9327 | 7.9663 | 7.4898
|  | BASINGSTOKE PRIMARY | FB |  |  |  |  | 18.1561 | 18.1776 | 18.1776 | 18.0694 | 17.7367 | 17.4235 | 17.2143 | 16.9633 | 16.6153 | 14.8673 | 13.1806 | 11.6684 | 15.452 | 15.4204 | 15.3653 | 15.2133 | 15.0286 | 14.8143 | 14.502 | 14.1122 | 13.6531 | 11.4337 | 8.9143 | 6.2306 | 15.399 | 15.4071 | 15.3969 | 15.2673 | 15.0439 | 14.8286 | 14.6276 | 14.3847 | 14.0796 | 12.4592 | 10.648 | 9.2235
NURSLING GSP | VELMORE BSP | BASSETT PRIMARY | MINIMUM HEADROOM | SU 42193 15958 | NO | YES | 4.695 | 11.3981 | 11.2951 | 11.3338 | 11.2155 | 10.9787 | 10.5389 | 9.9124 | 9.2338 | 8.5706 | 5.9124 | 4.2155 | 3.4859 | 12.8144 | 12.6206 | 12.6124 | 12.4757 | 12.1185 | 11.7583 | 11.3675 | 10.8971 | 10.4604 | 8.6563 | 5.8706 | 1.9379 | 11.0777 | 10.9226 | 10.9451 | 10.8063 | 10.3685 | 9.8961 | 9.3716 | 8.7798 | 8.2216 | 6.0634 | 4.7502 | 4.2379
|  | BASSETT PRIMARY | EE |  |  |  |  | 11.3981 | 11.4491 | 11.3522 | 11.2736 | 11.0889 | 10.6287 | 9.9124 | 9.241 | 8.6012 | 6.0461 | 4.3277 | 3.4859 | 12.8144 | 12.7798 | 12.6389 | 12.541 | 12.2328 | 11.8971 | 11.4787 | 11.041 | 10.6328 | 8.6563 | 7.141 | 5.6461 | 11.0777 | 11.0838 | 10.9634 | 10.8777 | 10.5104 | 10.0236 | 9.4359 | 8.8706 | 8.3379 | 6.1859 | 4.8277 | 4.2379
|  | BASSETT PRIMARY | HT |  |  |  |  | 11.4012 | 11.2951 | 11.3338 | 11.2155 | 10.9787 | 10.5389 | 9.9236 | 9.2338 | 8.5706 | 5.9124 | 4.2155 | 3.6644 | 12.8155 | 12.6206 | 12.6124 | 12.4757 | 12.1185 | 11.7583 | 11.3675 | 10.8971 | 10.4604 | 9.0563 | 8.3236 | 8.1042 | 11.0838 | 10.9226 | 10.9451 | 10.8063 | 10.3685 | 9.8961 | 9.3716 | 8.7798 | 8.2216 | 6.0634 | 4.7502 | 4.4389
|  | BASSETT PRIMARY | HE |  |  |  |  | 11.4042 | 11.4583 | 11.3695 | 11.2614 | 11.0563 | 10.6451 | 9.993 | 9.3859 | 8.7859 | 6.7155 | 5.394 | 4.7644 | 12.8165 | 12.7706 | 12.642 | 12.5379 | 12.2318 | 11.8971 | 11.4838 | 11.0624 | 10.6512 | 8.7828 | 7.3491 | 5.8512 | 11.0879 | 11.0849 | 10.9828 | 10.8726 | 10.4808 | 10.0338 | 9.4798 | 8.9604 | 8.4481 | 6.6787 | 5.6685 | 5.24
|  | BASSETT PRIMARY | FB |  |  |  |  | 11.5155 | 11.641 | 11.7308 | 11.6349 | 11.6849 | 11.6563 | 11.591 | 11.494 | 11.4053 | 10.3849 | 8.644 | 7.5726 | 12.8736 | 12.8522 | 12.8073 | 12.5828 | 12.5165 | 12.2961 | 12.0267 | 11.7277 | 11.4379 | 9.1236 | 5.8706 | 1.9379 | 11.2665 | 11.3604 | 11.4185 | 11.2859 | 11.3726 | 11.3083 | 11.2042 | 11.0593 | 10.9226 | 9.4991 | 7.8644 | 6.8706
NORTH HYDE GSP | NORTH HYDE BSP | BATH ROAD EAST PRIMARY | MINIMUM HEADROOM | TQ 09097 76885 | NO | YES | 4.275 | 2.1429 | 1.9092 | 1.8857 | 26.8806 | 26.7459 | 26.5663 | 26.4204 | 26.1112 | 25.899 | 24.9102 | 24.2133 | 23.9235 | 2.3214 | 2.0367 | 1.9755 | 24.951 | 24.8122 | 24.6429 | 24.5122 | 24.2316 | 24.0306 | 22.948 | 21.2173 | 18.8245 | 1.9765 | 1.7388 | 1.7 | 25.3857 | 25.2469 | 25.0837 | 24.949 | 24.648 | 24.451 | 23.5163 | 22.8776 | 22.549
|  | BATH ROAD EAST PRIMARY | EE |  |  |  |  | 2.1429 | 2.1082 | 1.8857 | 26.8888 | 26.8061 | 26.602 | 26.5 | 26.2357 | 26.0327 | 25.0306 | 24.298 | 23.9235 | 2.3224 | 2.2551 | 1.9827 | 24.9653 | 24.8571 | 24.6612 | 24.5653 | 24.3122 | 24.1153 | 22.948 | 21.9735 | 20.9643 | 1.9765 | 1.9255 | 1.7 | 25.3949 | 25.3 | 25.1031 | 25.0082 | 24.7439 | 24.5469 | 23.5724 | 22.8939 | 22.549
|  | BATH ROAD EAST PRIMARY | HT |  |  |  |  | 2.148 | 1.9092 | 1.8878 | 26.8806 | 26.7459 | 26.5663 | 26.4204 | 26.1112 | 25.899 | 24.9102 | 24.2133 | 24.0173 | 2.3214 | 2.0367 | 1.9755 | 24.951 | 24.8122 | 24.6429 | 24.5122 | 24.2316 | 24.0306 | 23.2143 | 22.6306 | 22.3918 | 1.9816 | 1.7388 | 1.7031 | 25.3857 | 25.2469 | 25.0837 | 24.949 | 24.648 | 24.451 | 23.5163 | 22.8776 | 22.7327
|  | BATH ROAD EAST PRIMARY | HE |  |  |  |  | 2.1469 | 2.1153 | 1.8969 | 26.8939 | 26.8133 | 26.6153 | 26.502 | 26.2398 | 26.0469 | 25.3765 | 24.75 | 24.6041 | 2.3224 | 2.2551 | 1.9837 | 24.9633 | 24.8582 | 24.6643 | 24.551 | 24.2939 | 24.1031 | 23.1245 | 22.1163 | 21.2602 | 1.9806 | 1.9337 | 1.7112 | 25.399 | 25.3051 | 25.1122 | 25.0031 | 24.7398 | 24.5541 | 23.9061 | 23.3143 | 23.2163
|  | BATH ROAD EAST PRIMARY | FB |  |  |  |  | 2.4867 | 2.3378 | 2.3031 | 27.1724 | 27.1204 | 27.0765 | 27.0337 | 26.9602 | 26.8959 | 26.4847 | 25.5827 | 24.9786 | 2.5357 | 2.3602 | 2.2673 | 25.0561 | 24.9235 | 24.7724 | 24.6133 | 24.4337 | 24.2643 | 23.1755 | 21.2173 | 18.8245 | 2.3173 | 2.1612 | 2.1082 | 25.6724 | 25.6133 | 25.5592 | 25.502 | 25.4245 | 25.352 | 24.9184 | 24.0184 | 23.4296
IVER 132KV GSP | LONGFORD BSP | BATH ROAD WEST PRIMARY | MINIMUM HEADROOM | TQ 05814 76820 | NO | YES | 8.135 | 9.6463 | 9.6208 | 9.5698 | 9.4525 | 9.3443 | 9.1861 | 9.0086 | 8.8198 | 8.6606 | 7.9759 | 7.1933 | 6.9494 | 9.6208 | 9.6035 | 9.5668 | 9.4841 | 9.4178 | 9.3035 | 9.1504 | 8.9606 | 8.8147 | 8.2851 | 7.7841 | 7.2137 | 10.2749 | 10.2382 | 10.1719 | 10.0606 | 9.9627 | 9.8168 | 9.6147 | 9.3974 | 9.2188 | 8.5249 | 7.8555 | 7.6729
|  | BATH ROAD WEST PRIMARY | EE |  |  |  |  | 9.6463 | 9.6341 | 9.6025 | 9.5361 | 9.4719 | 9.3617 | 9.2341 | 9.1004 | 8.9831 | 8.4678 | 7.6137 | 7.2494 | 9.6208 | 9.6096 | 9.5851 | 9.527 | 9.479 | 9.3851 | 9.2423 | 9.1014 | 8.9647 | 8.3606 | 7.7841 | 7.3892 | 10.2749 | 10.2412 | 10.1933 | 10.0953 | 10.0198 | 9.9239 | 9.7637 | 9.6045 | 9.4433 | 8.8096 | 8.1535 | 7.8484
|  | BATH ROAD WEST PRIMARY | HT |  |  |  |  | 9.6474 | 9.6208 | 9.5698 | 9.4525 | 9.3443 | 9.1861 | 9.0086 | 8.8198 | 8.6606 | 7.9759 | 7.1933 | 6.9494 | 9.6208 | 9.6035 | 9.5668 | 9.4841 | 9.4178 | 9.3035 | 9.1504 | 8.9606 | 8.8147 | 8.2851 | 7.8739 | 7.7606 | 10.277 | 10.2382 | 10.1719 | 10.0606 | 9.9627 | 9.8168 | 9.6147 | 9.3974 | 9.2188 | 8.5249 | 7.8555 | 7.6729
|  | BATH ROAD WEST PRIMARY | HE |  |  |  |  | 9.6474 | 9.6361 | 9.6076 | 9.5392 | 9.4739 | 9.3678 | 9.2463 | 9.1178 | 9.0066 | 8.628 | 8.2627 | 8.1617 | 9.6219 | 9.6096 | 9.5861 | 9.53 | 9.481 | 9.3841 | 9.2443 | 9.0902 | 8.9596 | 8.4412 | 8.1157 | 7.877 | 10.277 | 10.2463 | 10.2014 | 10.1025 | 10.0229 | 9.927 | 9.7759 | 9.6106 | 9.4606 | 8.9698 | 8.7035 | 8.6392
|  | BATH ROAD WEST PRIMARY | FB |  |  |  |  | 9.7157 | 9.7361 | 9.7412 | 9.6892 | 9.6617 | 9.6412 | 9.6086 | 9.5525 | 9.5188 | 9.2729 | 8.9566 | 8.6657 | 9.681 | 9.6831 | 9.6831 | 9.628 | 9.5974 | 9.5566 | 9.5035 | 9.4157 | 9.3474 | 8.8453 | 8.0637 | 7.2137 | 10.3729 | 10.3841 | 10.3821 | 10.2923 | 10.2474 | 10.2168 | 10.1749 | 10.1025 | 10.0872 | 9.7668 | 9.2586 | 8.88
IVER 132KV GSP | DENHAM BSP | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | MINIMUM HEADROOM | SU 93668 91219 | NO | YES | 3.568 | 0.54189 | 0.69087 | 0.7572 | 0.73985 | 20.4592 | 19.6776 | 18.8062 | 17.899 | 17.0378 | 13.8715 | 11.2827 | 9.9103 | 3.6021 | 3.6531 | 3.6674 | 6.5776 | 23.5501 | 23.2001 | 22.7715 | 22.2919 | 21.8684 | 20.4786 | 20.0225 | 20.1358 | 2.3603 | 2.4592 | 2.5266 | 5.4368 | 22.4888 | 21.9184 | 21.2552 | 20.5572 | 19.8939 | 17.5735 | 16.0245 | 15.4011
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | EE |  |  |  |  | 0.54189 | 0.69087 | 0.78679 | 0.87761 | 20.7286 | 20.0531 | 19.2633 | 18.4011 | 17.5858 | 14.6164 | 12.145 | 10.7735 | 3.6052 | 3.6552 | 3.6827 | 6.6592 | 23.6633 | 23.3572 | 22.9827 | 22.548 | 22.1735 | 20.7674 | 20.295 | 20.3399 | 2.3613 | 2.4592 | 2.5307 | 5.5541 | 22.6735 | 22.1817 | 21.5796 | 20.9194 | 20.3011 | 18.0317 | 16.495 | 15.8041
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | HT |  |  |  |  | 0.54291 | 0.69291 | 0.7572 | 0.73985 | 20.4592 | 19.6776 | 18.8062 | 17.899 | 17.0378 | 13.8715 | 11.2827 | 9.9103 | 3.6021 | 3.6562 | 3.6674 | 6.5776 | 23.5501 | 23.2001 | 22.7715 | 22.2919 | 21.8684 | 20.4786 | 20.0225 | 20.1358 | 2.3603 | 2.4623 | 2.5266 | 5.4368 | 22.4888 | 21.9184 | 21.2552 | 20.5572 | 19.8939 | 17.5735 | 16.0245 | 15.4011
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | HE |  |  |  |  | 0.54291 | 0.69087 | 0.78577 | 0.85924 | 20.6868 | 19.9184 | 19.0756 | 18.1603 | 17.2868 | 14.8899 | 12.649 | 11.6358 | 3.6031 | 3.6531 | 3.6796 | 6.6552 | 23.6868 | 23.3388 | 22.9582 | 22.5215 | 22.145 | 21.0399 | 20.5215 | 20.4256 | 2.3603 | 2.4592 | 2.5296 | 5.5419 | 22.6756 | 22.1041 | 21.4735 | 20.7858 | 20.1327 | 18.3419 | 16.9021 | 16.3276
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | FB |  |  |  |  | 0.69802 | 0.88169 | 1.0735 | 1.195 | 21.4592 | 21.4684 | 21.3786 | 21.3133 | 21.1745 | 20.1521 | 18.7225 | 18.1133 | 3.7256 | 3.8215 | 3.9113 | 6.8786 | 24.1674 | 24.147 | 24.0715 | 24.0286 | 23.898 | 22.9776 | 22.0164 | 21.7337 | 2.5154 | 2.6756 | 2.8276 | 5.8399 | 23.3511 | 23.3266 | 23.2388 | 23.2103 | 23.0715 | 22.0643 | 20.8572 | 20.396
IVER 132KV GSP | UPTON BSP | BEACONSFIELD (END BUSBARS) PRIMARY | MINIMUM HEADROOM | SU 93668 91219 | NO | YES | 0.669 | Demand Headroom Winter (MVA) 2027: 1.7776; Demand Headroom Winter (MVA) 2028: 1.6745; Demand Headroom Winter (MVA) 2029: 1.5561; Demand Headroom Winter (MVA) 2030: 1.3929 | 3.1327 | 3.0449 | 2.9602 | 2.8408 | [8 empty] | 2.5531 | 2.4551 | 2.349 | 5.0918
|  | BEACONSFIELD (END BUSBARS) PRIMARY | EE |  |  |  |  | Demand Headroom Winter (MVA) 2027: 1.7776; Demand Headroom Winter (MVA) 2028: 1.6745; Demand Headroom Winter (MVA) 2029: 1.5704; Demand Headroom Winter (MVA) 2030: 1.4367 | 3.1337 | 3.0469 | 2.9653 | 2.8592 | [8 empty] | 2.5531 | 2.4551 | 2.3582 | 5.1204
|  | BEACONSFIELD (END BUSBARS) PRIMARY | HT |  |  |  |  | Demand Headroom Winter (MVA) 2027: 1.7786; Demand Headroom Winter (MVA) 2028: 1.6745; Demand Headroom Winter (MVA) 2029: 1.5561; Demand Headroom Winter (MVA) 2030: 1.3929 | 3.1337 | 3.0449 | 2.9602 | 2.8408 | [8 empty] | 2.5531 | 2.4571 | 2.349 | 5.0918
|  | BEACONSFIELD (END BUSBARS) PRIMARY | HE |  |  |  |  | Demand Headroom Winter (MVA) 2027: 1.7786; Demand Headroom Winter (MVA) 2028: 1.6745; Demand Headroom Winter (MVA) 2029: 1.5714; Demand Headroom Winter (MVA) 2030: 1.4163 | 3.1327 | 3.0459 | 2.9643 | 2.8541 | [8 empty] | 2.5531 | 2.4561 | 2.3582 | 5.1092
|  | BEACONSFIELD (END BUSBARS) PRIMARY | FB |  |  |  |  | Demand Headroom Winter (MVA) 2027: 1.9102; Demand Headroom Winter (MVA) 2028: 1.8398; Demand Headroom Winter (MVA) 2029: 1.7878; Demand Headroom Winter (MVA) 2030: 1.7173 | 3.25 | 3.1898 | 3.1398 | 3.0878 | [8 empty] | 2.6796 | 2.6184 | 2.5684 | 5.402
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BEENHAM PRIMARY | MINIMUM HEADROOM | SU 58204 69025 | NO | NO | 0.73 | 5.999 | 6.0347 | 5.848 | 5.7122 | 5.499 | 5.302 | 5.0173 | 4.6194 | 4.3245 | 3.1745 | 2.3643 | 1.8959 | 8.2837 | 8.2755 | 8.0102 | 7.8551 | 7.6051 | 7.4694 | 7.2378 | 6.8776 | 6.6367 | 5.5714 | 5.1153 | 4.8347 | 7.3408 | 7.352 | 7.1582 | 6.9959 | 6.7653 | 6.6061 | 6.3439 | 5.9582 | 5.6878 | 4.5612 | 3.948 | 3.7265
|  | BEENHAM PRIMARY | EE |  |  |  |  | 5.999 | 6.0347 | 5.8551 | 5.7469 | 5.549 | 5.3837 | 5.1102 | 4.7551 | 4.4908 | 3.2786 | 2.5194 | 2.1133 | 8.2837 | 8.2755 | 8.0173 | 7.8724 | 7.6306 | 7.5235 | 7.2867 | 6.9592 | 6.7418 | 5.6398 | 5.1153 | 4.8786 | 7.3408 | 7.352 | 7.1622 | 7.0194 | 6.8 | 6.6694 | 6.4122 | 6.0571 | 5.8133 | 4.65 | 4.0316 | 3.7653
|  | BEENHAM PRIMARY | HT |  |  |  |  | 6 | 6.0378 | 5.848 | 5.7122 | 5.499 | 5.302 | 5.0173 | 4.6194 | 4.3245 | 3.1745 | 2.3643 | 1.8959 | 8.2837 | 8.2765 | 8.0102 | 7.8551 | 7.6051 | 7.4694 | 7.2378 | 6.8776 | 6.6367 | 5.5714 | 5.1398 | 5.0949 | 7.3408 | 7.3541 | 7.1582 | 6.9959 | 6.7653 | 6.6061 | 6.3439 | 5.9582 | 5.6878 | 4.5612 | 3.948 | 3.7265
|  | BEENHAM PRIMARY | HE |  |  |  |  | 5.999 | 6.0357 | 5.8602 | 5.7327 | 5.5592 | 5.3367 | 5.0602 | 4.6898 | 4.4194 | 3.5163 | 2.9561 | 2.5878 | 8.2847 | 8.2755 | 8.0173 | 7.8724 | 7.6776 | 7.5102 | 7.2949 | 6.9643 | 6.7602 | 5.8296 | 5.6276 | 5.3888 | 7.3408 | 7.3531 | 7.1653 | 7.0122 | 6.8337 | 6.6418 | 6.3898 | 6.0316 | 5.7888 | 4.8684 | 4.5337 | 4.2929
|  | BEENHAM PRIMARY | FB |  |  |  |  | 6.0939 | 6.1643 | 6.2102 | 6.2429 | 6.098 | 6.0102 | 5.9724 | 5.8816 | 5.8255 | 5.1898 | 4.3541 | 3.8367 | 8.349 | 8.3571 | 8.3439 | 8.3408 | 8.1031 | 7.9765 | 7.9143 | 7.7806 | 7.6878 | 6.9286 | 5.852 | 4.8347 | 7.399 | 7.4337 | 7.452 | 7.4612 | 7.3327 | 7.2224 | 7.1745 | 7.0735 | 7.0041 | 6.3255 | 5.5071 | 4.9439
MANNINGTON GSP | SALISBURY BSP | BEMERTON PRIMARY | MINIMUM HEADROOM | SU 11583 31233 | NO | NO | 2.196 | 19.0967 | 18.6763 | 18.1886 | 17.8702 | 17.2467 | 16.5498 | 15.7723 | 14.9876 | 14.0998 | 10.9702 | 8.3457 | 7.0865 | 23.3161 | 22.9876 | 22.6396 | 22.4049 | 21.8916 | 21.4774 | 20.961 | 20.3274 | 19.6916 | 17.6927 | 16.1131 | 13.9978 | 20.6947 | 20.3233 | 19.91 | 19.6416 | 19.061 | 18.5182 | 17.9049 | 17.1916 | 16.4386 | 13.8978 | 11.909 | 11.1733
|  | BEMERTON PRIMARY | EE |  |  |  |  | 19.0967 | 18.6763 | 18.1906 | 17.8702 | 17.2467 | 16.5508 | 15.7723 | 14.9957 | 14.311 | 11.2498 | 8.8733 | 7.5274 | 23.3161 | 22.9876 | 22.6641 | 22.4376 | 21.911 | 21.5008 | 21.0018 | 20.4733 | 20.0345 | 17.6927 | 16.1131 | 14.9865 | 20.6947 | 20.3233 | 19.9151 | 19.6427 | 19.0702 | 18.5294 | 17.9049 | 17.2672 | 16.7161 | 14.1212 | 12.2631 | 11.2906
|  | BEMERTON PRIMARY | HT |  |  |  |  | 19.1029 | 18.7263 | 18.208 | 17.9151 | 17.4416 | 16.7182 | 15.859 | 14.9876 | 14.0998 | 10.9702 | 8.3457 | 7.0865 | 23.3172 | 23.0294 | 22.6396 | 22.4049 | 22.0172 | 21.559 | 20.961 | 20.3274 | 19.6916 | 17.7202 | 16.4233 | 16.1876 | 20.6998 | 20.3692 | 19.91 | 19.6498 | 19.2223 | 18.6386 | 17.9253 | 17.1916 | 16.4386 | 13.8978 | 11.909 | 11.1733
|  | BEMERTON PRIMARY | HE |  |  |  |  | 19.0978 | 18.7345 | 18.1886 | 17.8753 | 17.2467 | 16.5498 | 15.7937 | 14.9988 | 14.3161 | 11.8753 | 10.062 | 9.0498 | 23.3161 | 23.0427 | 22.6569 | 22.4253 | 21.8916 | 21.4774 | 20.9927 | 20.4427 | 19.9957 | 17.9192 | 16.7457 | 15.7447 | 20.6967 | 20.3825 | 19.912 | 19.6416 | 19.061 | 18.5182 | 17.9151 | 17.259 | 16.7059 | 14.5978 | 13.2641 | 12.5518
|  | BEMERTON PRIMARY | FB |  |  |  |  | 19.2416 | 19.1641 | 18.9202 | 18.8937 | 18.2508 | 18.0131 | 17.8018 | 17.6427 | 17.4069 | 15.7192 | 13.7529 | 12.2988 | 23.4018 | 23.3182 | 23.0998 | 23.0335 | 22.3723 | 22.0957 | 21.8294 | 21.6018 | 21.2967 | 19.2467 | 16.7712 | 13.9978 | 20.8376 | 20.7651 | 20.562 | 20.5376 | 19.8967 | 19.6967 | 19.5018 | 19.3488 | 19.1212 | 17.5304 | 15.7682 | 14.4529
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | BERINSFIELD PRIMARY | MINIMUM HEADROOM | SU 58382 95467 | NO | NO | 5.4 | 9.927 | 9.2923 | 8.3729 | 7.2943 | 5.9912 | 18.2711 | 15.3977 | 12.2783 | 10.4916 | -2.086 | -16.4248 | -26.4207 | 12.7657 | 12.4514 | 12.1076 | 11.6963 | 11.178 | 22.2171 | 19.8905 | 17.1599 | 16.1273 | 5.8048 | -8.935 | -19.1248 | 11.6708 | 11.2463 | 10.6882 | 10.0331 | 9.2525 | 21.0701 | 18.2854 | 15.1946 | 13.6691 | 1.7987 | -13.9911 | -24.9901
|  | BERINSFIELD PRIMARY | EE |  |  |  |  | 10.0157 | 9.78 | 8.9678 | 7.9249 | 6.6984 | 19.0456 | 16.8028 | 14.0222 | 10.4916 | -0.37478 | -14.838 | -20.788 | 12.8382 | 12.7147 | 12.4382 | 12.0892 | 11.6606 | 22.9262 | 21.4691 | 19.3436 | 16.2507 | 7.3201 | -8.5146 | -14.6809 | 11.7555 | 11.6219 | 11.1382 | 10.5576 | 9.8668 | 21.8191 | 19.8487 | 17.2252 | 13.6691 | 3.364 | -13.1166 | -19.4748
|  | BERINSFIELD PRIMARY | HT |  |  |  |  | 9.927 | 9.2923 | 8.3729 | 7.2943 | 5.9912 | 18.2711 | 15.3977 | 12.2783 | 10.5069 | -2.086 | -16.4248 | -26.4207 | 12.7657 | 12.4514 | 12.1076 | 11.6963 | 11.178 | 22.2171 | 19.8905 | 17.1599 | 16.1273 | 5.8048 | -8.935 | -19.1248 | 11.6708 | 11.2463 | 10.6882 | 10.0331 | 9.2525 | 21.0701 | 18.2854 | 15.1946 | 13.7926 | 1.7987 | -13.9911 | -24.9901
|  | BERINSFIELD PRIMARY | HE |  |  |  |  | 10.0168 | 9.7821 | 9.1535 | 8.28 | 7.2239 | 19.7222 | 17.0232 | 15.3579 | 13.6446 | 2.6824 | -9.1646 | -17.8687 | 12.8382 | 12.7127 | 12.4892 | 12.1902 | 11.8117 | 23.1283 | 21.0558 | 20.2252 | 19.3334 | 9.3201 | -2.2207 | -11.7115 | 11.7566 | 11.6229 | 11.2382 | 10.7555 | 10.1647 | 22.2916 | 19.6762 | 18.3875 | 17.0548 | 5.962 | -6.5595 | -16.2258
|  | BERINSFIELD PRIMARY | FB |  |  |  |  | 10.1902 | 10.1504 | 9.8892 | 9.4259 | 8.8219 | 21.9589 | 20.8191 | 19.4956 | 17.4732 | 9.6558 | 1.0507 | -5.9452 | 12.9188 | 12.8821 | 12.7514 | 12.5545 | 12.331 | 23.8007 | 23.0599 | 22.0518 | 20.1334 | 13.5007 | 5.1558 | -2.734 | 11.8831 | 11.8514 | 11.6729 | 11.3494 | 10.9953 | 23.4691 | 22.5987 | 21.5313 | 19.6028 | 12.1528 | 3.4864 | -3.8962
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | BEVOIS VALLEY PRIMARY | MINIMUM HEADROOM | SU 42648 13187 | NO | YES | 3.088 | 6.0689 | 6.1475 | 6.1873 | 5.9832 | 5.576 | 5.2424 | 4.6964 | 3.9709 | 3.5067 | 0.73829 | -1.624 | -2.7821 | 11.8169 | 11.6934 | 11.5026 | 11.2128 | 10.7699 | 10.4383 | 9.9036 | 9.1903 | 8.7597 | 6.0577 | 3.3444 | -2.4066 | 8.1434 | 8.0791 | 7.9526 | 7.6862 | 7.2771 | 6.9658 | 6.4516 | 5.7546 | 5.3301 | 2.825 | 0.64849 | -0.35457
|  | BEVOIS VALLEY PRIMARY | EE |  |  |  |  | 6.0689 | 6.1475 | 6.1954 | 6.0271 | 5.6801 | 5.276 | 4.6964 | 3.9801 | 3.5618 | 0.80665 | -1.624 | -2.7821 | 11.8169 | 11.6934 | 11.5148 | 11.2475 | 10.8464 | 10.474 | 9.9332 | 9.226 | 8.823 | 6.0577 | 3.5536 | 1.5046 | 8.1434 | 8.0791 | 7.9526 | 7.7189 | 7.376 | 7.0077 | 6.4679 | 5.7781 | 5.3903 | 2.8291 | 0.64849 | -0.35457
|  | BEVOIS VALLEY PRIMARY | HT |  |  |  |  | 6.072 | 6.1536 | 6.1873 | 5.9832 | 5.576 | 5.2424 | 4.6995 | 3.9709 | 3.5067 | 0.73829 | -1.328 | -2.0648 | 11.822 | 11.6954 | 11.5026 | 11.2128 | 10.7699 | 10.4383 | 9.9036 | 9.1903 | 8.7597 | 6.5322 | 4.9097 | 4.2628 | 8.1516 | 8.0954 | 7.9567 | 7.6862 | 7.2771 | 6.9658 | 6.4516 | 5.7546 | 5.3301 | 2.825 | 0.99951 | 0.40359
|  | BEVOIS VALLEY PRIMARY | HE |  |  |  |  | 6.0791 | 6.175 | 6.2342 | 6.0454 | 5.6832 | 5.326 | 4.7883 | 4.1005 | 3.7107 | 1.7791 | 0.84747 | 0.13114 | 11.823 | 11.7026 | 11.522 | 11.2475 | 10.8424 | 10.4873 | 9.9516 | 9.2516 | 8.8485 | 6.5811 | 5.1709 | 3.4087 | 8.1536 | 8.1036 | 7.9801 | 7.7301 | 7.374 | 7.0413 | 6.5301 | 5.8618 | 5.4903 | 3.6567 | 2.8913 | 2.3077
|  | BEVOIS VALLEY PRIMARY | FB |  |  |  |  | 6.1271 | 6.2311 | 6.2893 | 6.276 | 6.323 | 6.273 | 6.1189 | 5.9495 | 5.8618 | 4.5179 | 2.4209 | 0.46686 | 11.8781 | 11.7852 | 11.6046 | 11.376 | 11.1567 | 10.9352 | 10.623 | 10.2832 | 10.0067 | 7.5138 | 3.3444 | -2.4066 | 8.2883 | 8.3016 | 8.224 | 8.0832 | 7.9975 | 7.926 | 7.7709 | 7.5975 | 7.5056 | 6.1383 | 4.122 | 2.2444
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER PRIMARY | MINIMUM HEADROOM | SP 58381 21988 | NO | YES | 24.329 | 6.3351 | 5.4484 | 1.8698 | -0.078171 | -2.3741 | -6.4323 | -9.6649 | -13.0169 | -16.418 | -26.8823 | -33.6894 | -35.3118 | 14.6535 | 14.2269 | 11.4545 | 10.8575 | 9.982 | 7.7637 | 6.4575 | 5.0096 | 3.5004 | -2.1823 | -5.4414 | -7.2792 | 10.5606 | 9.9933 | 6.5708 | 5.3065 | 3.6565 | 0.55754 | -1.769 | -4.1506 | -6.5925 | -15.1363 | -20.0874 | -21.0669
|  | BICESTER PRIMARY | EE |  |  |  |  | 6.3351 | 5.4484 | 1.8698 | -0.071029 | -2.3465 | -6.4118 | -9.6567 | -12.9863 | -16.3669 | -26.221 | -32.169 | -33.622 | 14.68 | 14.3116 | 11.6075 | 11.1157 | 10.3524 | 8.3769 | 7.2739 | 5.9331 | 4.5126 | -0.79552 | -4.0343 | -5.5527 | 10.5606 | 9.9933 | 6.5708 | 5.3147 | 3.6759 | 0.68203 | -1.5618 | -3.969 | -6.4578 | -14.4874 | -19.2384 | -20.4139
|  | BICESTER PRIMARY | HT |  |  |  |  | 6.379 | 5.5453 | 2.0412 | 0.15958 | -1.9669 | -6.119 | -9.32 | -12.5016 | -15.7129 | -26.8823 | -33.6894 | -35.3118 | 14.6535 | 14.2269 | 11.4545 | 10.8575 | 9.982 | 7.7637 | 6.4575 | 5.0096 | 3.5004 | -2.1823 | -5.4414 | -5.9527 | 10.5647 | 10.031 | 6.6269 | 5.3065 | 3.7075 | 0.55754 | -1.769 | -4.1506 | -6.5925 | -15.1363 | -20.0874 | -21.0669
|  | BICESTER PRIMARY | HE |  |  |  |  | 6.3392 | 5.4596 | 1.8892 | -0.078171 | -2.3741 | -6.4323 | -9.6649 | -13.0169 | -16.418 | -25.1761 | -30.569 | -31.3057 | 14.678 | 14.3086 | 11.6035 | 11.1075 | 10.3453 | 8.3708 | 7.2728 | 5.9453 | 4.5402 | -0.16389 | -3.2649 | -4.5853 | 10.5647 | 10.0055 | 6.5892 | 5.3126 | 3.6565 | 0.66979 | -1.5629 | -3.971 | -6.4608 | -13.5343 | -17.8516 | -18.4802
|  | BICESTER PRIMARY | FB |  |  |  |  | 6.8208 | 6.1922 | 3.1667 | 1.9433 | 0.56367 | -1.9792 | -3.6435 | -5.3282 | -7.3129 | -16.6027 | -23.3527 | -25.2843 | 14.8647 | 14.4545 | 11.7616 | 11.3933 | 10.8065 | 9.128 | 8.3473 | 7.5494 | 6.628 | 1.6555 | -3.3935 | -7.2792 | 10.9728 | 10.5239 | 7.4484 | 6.7035 | 5.7535 | 3.8188 | 2.6126 | 1.3892 | -0.0496 | -7.2986 | -12.9159 | -14.9374
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH PRIMARY | MINIMUM HEADROOM | SP 59720 23735 | NO | YES | 35.918 | -15.3653 | -15.397 | -15.6347 | -16.0582 | -18.9704 | -21.7582 | -25.0847 | -28.0684 | -30.6245 | -8.1613 | -12.8919 | -15.4745 | -11.7051 | -11.7164 | -11.7807 | -11.9858 | -14.5939 | -16.6919 | -19.1643 | -21.4041 | -23.2143 | 0.57649 | -1.2245 | -1.946 | -14.8541 | -14.8317 | -14.9898 | -15.2766 | -18.1347 | -20.5847 | -23.4909 | -26.1133 | -28.3153 | -4.6735 | -7.1674 | -8.4072
|  | BICESTER NORTH PRIMARY | EE |  |  |  |  | -15.3653 | -15.397 | -15.6347 | -16.0398 | -16.5664 | -19.0521 | -21.9113 | -24.7878 | -27.4388 | -6.9276 | -11.4368 | -13.8521 | -11.6847 | -11.6796 | -11.7 | -11.8643 | -12.3184 | -14.0409 | -16.1204 | -18.1837 | -19.9215 | 1.704 | -0.021469 | -0.76637 | -14.8521 | -14.8317 | -14.9898 | -15.2735 | -15.6786 | -17.9225 | -20.5215 | -23.1225 | -25.3102 | -4.2021 | -6.6664 | -7.85
|  | BICESTER NORTH PRIMARY | HT |  |  |  |  | -15.3541 | -15.3725 | -15.6092 | -16.0072 | -18.9704 | -21.7582 | -25.0847 | -28.0684 | -30.6245 | -8.1613 | -12.8919 | -15.4745 | -11.7051 | -11.7164 | -11.7807 | -11.9858 | -14.5939 | -16.6919 | -19.1643 | -21.4041 | -23.2143 | 0.57649 | -1.2245 | -1.946 | -14.8541 | -14.8225 | -14.9725 | -15.2572 | -18.1347 | -20.5847 | -23.4909 | -26.1133 | -28.3153 | -4.6735 | -7.1674 | -8.4072
|  | BICESTER NORTH PRIMARY | HE |  |  |  |  | -15.3643 | -15.3888 | -15.6215 | -16.0582 | -16.6051 | -19.1092 | -21.9868 | -24.7337 | -27.2317 | -5.5 | -10.0327 | -12.8 | -11.6888 | -11.6868 | -11.7092 | -11.8776 | -12.3317 | -14.1102 | -16.2562 | -18.3521 | -20.0715 | 2.2091 | 0.43159 | -0.60922 | -14.8531 | -14.8296 | -14.9674 | -15.2766 | -15.7062 | -17.9878 | -20.6388 | -23.15 | -25.2551 | -3.3735 | -5.9113 | -7.3551
|  | BICESTER NORTH PRIMARY | FB |  |  |  |  | -15.2184 | -15.1541 | -15.2796 | -15.4684 | -15.6715 | -16.0735 | -18.0378 | -19.7204 | -21.2602 | -1.4051 | -5.9725 | -9.5307 | -11.5807 | -11.5082 | -11.5215 | -11.5949 | -11.6184 | -11.8429 | -13.498 | -15.0082 | -16.2133 | 3.4816 | 1.2336 | -0.50208 | -14.7143 | -14.6317 | -14.6847 | -14.8153 | -14.9521 | -15.2358 | -17.0909 | -18.7 | -20.0735 | -0.47147 | -3.5929 | -5.5378
LOVEDEAN GSP | CHICHESTER BSP | BILLINGSHURST PRIMARY | MINIMUM HEADROOM | TQ 08305 26315 | YES | YES | 1.787 | 6.1092 | 6.1122 | 6.0724 | 5.9561 | 5.7673 | 5.4837 | 5.05 | 4.5673 | 4.1224 | 2.5857 | 1.6653 | 1.2776 | 5.9784 | 5.8998 | 5.7733 | 5.5263 | 5.1233 | 4.762 | 4.2978 | 3.8029 | 3.3202 | 1.7222 | 1.1967 | 0.15694 | 6.3998 | 6.3743 | 6.3161 | 6.159 | 5.9029 | 5.5865 | 5.161 | 4.6794 | 4.2182 | 2.6376 | 1.8406 | 1.6182
|  | BILLINGSHURST PRIMARY | EE |  |  |  |  | 6.1153 | 6.1265 | 6.1061 | 6.0071 | 5.8031 | 5.6 | 5.2806 | 4.948 | 4.6327 | 3.3122 | 2.248 | 1.8418 | 5.9814 | 5.9039 | 5.7824 | 5.5396 | 5.1233 | 4.7947 | 4.3488 | 3.912 | 3.4661 | 2.058 | 1.3049 | 1.2957 | 6.4059 | 6.3855 | 6.3427 | 6.1967 | 5.9314 | 5.6753 | 5.3304 | 4.9702 | 4.6018 | 3.2294 | 2.2192 | 1.9304
|  | BILLINGSHURST PRIMARY | HT |  |  |  |  | 6.1092 | 6.1122 | 6.0724 | 5.9561 | 5.7673 | 5.4837 | 5.05 | 4.5673 | 4.1224 | 2.5857 | 1.6653 | 1.2776 | 5.9784 | 5.8998 | 5.7733 | 5.5263 | 5.1284 | 4.762 | 4.2978 | 3.8029 | 3.3202 | 1.7222 | 1.1967 | 1.3539 | 6.3998 | 6.3743 | 6.3161 | 6.159 | 5.9029 | 5.5865 | 5.161 | 4.6794 | 4.2182 | 2.6376 | 1.8406 | 1.6182
|  | BILLINGSHURST PRIMARY | HE |  |  |  |  | 6.1153 | 6.1235 | 6.1071 | 5.9949 | 5.8133 | 5.5653 | 5.2551 | 4.898 | 4.5714 | 3.4561 | 2.5357 | 2.0959 | 5.9794 | 5.9018 | 5.7784 | 5.5345 | 5.1355 | 4.7743 | 4.3559 | 3.8967 | 3.4396 | 2.1243 | 1.4967 | 1.3233 | 6.4029 | 6.3835 | 6.3406 | 6.1876 | 5.9355 | 5.6457 | 5.3233 | 4.9386 | 4.559 | 3.3722 | 2.5376 | 2.1886
|  | BILLINGSHURST PRIMARY | FB |  |  |  |  | 6.248 | 6.3061 | 6.352 | 6.3612 | 6.3837 | 6.4296 | 6.2418 | 6.1541 | 6.0622 | 5.1122 | 3.948 | 3.0867 | 6.0559 | 6.0437 | 6.01 | 5.9304 | 5.8437 | 5.8467 | 5.5243 | 5.3722 | 5.1743 | 3.7967 | 2.3284 | 0.15694 | 6.5376 | 6.5498 | 6.558 | 6.5284 | 6.5069 | 6.4967 | 6.3631 | 6.26 | 6.1324 | 5.0314 | 3.8539 | 2.9549
LOVEDEAN GSP | CHICHESTER BSP | BILSHAM PRIMARY | MINIMUM HEADROOM | SU 97366 01594 | NO | YES | 18.122 | -2.142 | -2.988 | 25.4233 | 23.7141 | 21.4304 | 18.5039 | 15.609 | 12.5906 | 9.7549 | 1.0467 | -2.9145 | -5.6094 | 2.3325 | 1.9039 | 31.4508 | 30.9131 | 30.2498 | 29.4886 | 28.6039 | 27.4835 | 26.4916 | 22.161 | 20.0478 | 17.5774 | 0.37429 | -0.28285 | 28.7488 | 27.7355 | 26.2845 | 24.4202 | 22.5192 | 20.4774 | 18.6008 | 11.9763 | 8.9294 | 7.2192
|  | BILSHAM PRIMARY | EE |  |  |  |  | -2.142 | -2.9012 | 25.4233 | 23.7437 | 21.5018 | 18.8151 | 16.1212 | 13.3396 | 10.7427 | 1.0467 | -2.342 | -4.5237 | 2.3345 | 2.0957 | 31.4549 | 30.9212 | 30.2661 | 29.5222 | 28.6661 | 27.5682 | 26.6141 | 22.161 | 20.0478 | 18.4508 | 0.37531 | -0.14408 | 28.7488 | 27.7478 | 26.3345 | 24.5998 | 22.808 | 20.8967 | 19.159 | 11.9763 | 9.2396 | 7.6947
|  | BILSHAM PRIMARY | HT |  |  |  |  | -2.1288 | -2.988 | 25.7855 | 24.3835 | 22.4427 | 19.9876 | 17.4855 | 14.8447 | 12.409 | 1.4743 | -2.9145 | -5.6094 | 2.3335 | 1.9039 | 31.4814 | 30.9518 | 30.3018 | 29.5529 | 28.7161 | 27.5927 | 26.608 | 22.41 | 20.7498 | 19.9753 | 0.38041 | -0.28285 | 28.9069 | 27.9906 | 26.8447 | 25.2406 | 23.5498 | 21.7059 | 20.0447 | 12.1529 | 8.9294 | 7.2192
|  | BILSHAM PRIMARY | HE |  |  |  |  | -2.14 | -2.892 | 25.4335 | 23.7141 | 21.4304 | 18.5039 | 15.609 | 12.5906 | 9.7549 | 1.312 | -0.86142 | -2.3308 | 2.3325 | 2.0927 | 31.4508 | 30.9131 | 30.2498 | 29.4886 | 28.6039 | 27.4835 | 26.4916 | 22.4161 | 20.809 | 19.3151 | 0.37429 | -0.14204 | 28.7498 | 27.7355 | 26.2845 | 24.4202 | 22.5192 | 20.4774 | 18.6008 | 12.3406 | 10.6825 | 9.6141
|  | BILSHAM PRIMARY | FB |  |  |  |  | -1.941 | -2.4349 | 26.5845 | 25.4335 | 24.2774 | 22.7233 | 21.2437 | 19.7753 | 18.2171 | 10.2467 | 7.4018 | 5.2284 | 2.4437 | 2.2284 | 31.9539 | 31.458 | 31.0569 | 30.5661 | 29.9243 | 29.2151 | 28.4294 | 24.259 | 21.1539 | 17.5774 | 0.54776 | 0.14572 | 29.4927 | 28.6804 | 27.908 | 27.0202 | 26.1753 | 25.3192 | 24.2733 | 18.6978 | 16.0651 | 14.0049
FAWLEY GSP | COWES BSP | BINSTEAD PRIMARY | MINIMUM HEADROOM | SZ 56409 91399 | NO | YES | 0.137 | 9.1372 | 9.1383 | 9.0934 | 8.9291 | 8.6821 | 8.1709 | 7.5893 | 7.0097 | 6.3995 | 4.1189 | 2.2923 | 1.2342 | 9.9541 | 9.9357 | 9.8816 | 9.7949 | 9.5939 | 9.3306 | 9.0071 | 8.6959 | 8.3592 | 7.198 | 6.4327 | 4.8327 | 9.6745 | 9.65 | 9.5724 | 9.3888 | 9.1286 | 8.7143 | 8.2153 | 7.7541 | 7.2837 | 5.6092 | 4.4357 | 3.8765
|  | BINSTEAD PRIMARY | EE |  |  |  |  | 9.1372 | 9.1454 | 9.125 | 9.0087 | 8.8199 | 8.3209 | 7.7923 | 7.2505 | 6.6791 | 4.6801 | 3.0434 | 2.0883 | 9.9551 | 9.9408 | 9.898 | 9.8316 | 9.6592 | 9.3959 | 9.1255 | 8.798 | 8.4459 | 7.2908 | 6.4327 | 5.7643 | 9.6776 | 9.6551 | 9.5949 | 9.4459 | 9.2245 | 8.8122 | 8.3765 | 7.9459 | 7.5071 | 5.9724 | 4.8724 | 4.3143
|  | BINSTEAD PRIMARY | HT |  |  |  |  | 9.1372 | 9.1383 | 9.0934 | 8.9291 | 8.6821 | 8.1709 | 7.5893 | 7.0097 | 6.3995 | 4.1189 | 2.2923 | 1.2342 | 9.9561 | 9.9357 | 9.8816 | 9.7949 | 9.5939 | 9.3306 | 9.0071 | 8.6959 | 8.3592 | 7.198 | 6.7204 | 6.5327 | 9.6776 | 9.65 | 9.5724 | 9.3888 | 9.1286 | 8.7143 | 8.2153 | 7.7541 | 7.2837 | 5.6092 | 4.4357 | 3.8765
|  | BINSTEAD PRIMARY | HE |  |  |  |  | 9.1372 | 9.1434 | 9.124 | 8.9913 | 8.7842 | 8.2832 | 7.7281 | 7.1495 | 6.5801 | 4.877 | 3.4434 | 2.7097 | 9.9541 | 9.9388 | 9.8969 | 9.8265 | 9.648 | 9.4031 | 9.1133 | 8.7643 | 8.4367 | 7.4173 | 6.6684 | 5.9755 | 9.6745 | 9.6531 | 9.5949 | 9.4347 | 9.202 | 8.8031 | 8.3367 | 7.8735 | 7.4541 | 6.1429 | 5.2276 | 4.7796
|  | BINSTEAD PRIMARY | FB |  |  |  |  | 9.2515 | 9.3046 | 9.3515 | 9.3923 | 9.3934 | 9.3515 | 9.3485 | 9.2566 | 9.0474 | 8.2026 | 7.1046 | 6.3862 | 10.0133 | 10.0061 | 9.9959 | 9.9735 | 9.9194 | 9.8173 | 9.7582 | 9.6133 | 9.3276 | 8.1092 | 6.5745 | 4.8327 | 9.7939 | 9.8163 | 9.8398 | 9.8449 | 9.8316 | 9.7969 | 9.8 | 9.7 | 9.3816 | 8.4092 | 7.4245 | 6.8398
LOVEDEAN GSP | CHICHESTER BSP | BIRDHAM PRIMARY | MINIMUM HEADROOM | SZ 81965 99422 | NO | YES | 4.59 | -0.62958 | -0.74795 | -0.94081 | 13.9582 | 13.3245 | 12.2092 | 11.1286 | 9.8969 | 8.9163 | 5.3714 | 2.5521 | 1.0582 | 1.9174 | 1.7429 | 1.5969 | 15.4847 | 15.0847 | 14.4623 | 13.8663 | 13.0714 | 12.5347 | 10.4429 | 9.1867 | 7.4684 | 0.68981 | 0.57246 | 0.46532 | 14.748 | 14.3051 | 13.5214 | 12.7541 | 11.849 | 11.148 | 8.4806 | 6.6133 | 5.8337
|  | BIRDHAM PRIMARY | EE |  |  |  |  | -0.62244 | -0.69795 | -0.78672 | 14.2663 | 13.7735 | 12.7898 | 11.8072 | 10.7031 | 9.8786 | 6.8265 | 4.2827 | 2.898 | 1.9235 | 1.7694 | 1.6551 | 15.5929 | 15.2276 | 14.6837 | 14.1398 | 13.3816 | 12.9143 | 10.6367 | 9.1867 | 8.2674 | 0.69491 | 0.60613 | 0.56838 | 14.9469 | 14.5939 | 13.901 | 13.199 | 12.3755 | 11.7725 | 9.4541 | 7.7163 | 6.9051
|  | BIRDHAM PRIMARY | HT |  |  |  |  | -0.62958 | -0.74795 | -0.94081 | 13.9582 | 13.3245 | 12.2092 | 11.1286 | 9.8969 | 8.9163 | 5.3714 | 2.5521 | 1.0582 | 1.9174 | 1.7429 | 1.5969 | 15.4847 | 15.0847 | 14.4623 | 13.8663 | 13.0714 | 12.5347 | 10.4429 | 9.4133 | 9.2092 | 0.68981 | 0.57246 | 0.46532 | 14.748 | 14.3051 | 13.5214 | 12.7541 | 11.849 | 11.148 | 8.4806 | 6.6133 | 5.8337
|  | BIRDHAM PRIMARY | HE |  |  |  |  | -0.61938 | -0.69591 | -0.78366 | 14.2296 | 13.6837 | 12.6184 | 11.5694 | 10.3776 | 9.4449 | 6.9796 | 4.8878 | 3.8367 | 1.9245 | 1.7684 | 1.6531 | 15.5867 | 15.2041 | 14.6531 | 14.1133 | 13.349 | 12.8572 | 10.7837 | 9.701 | 8.7398 | 0.69797 | 0.60715 | 0.56838 | 14.9265 | 14.5367 | 13.8 | 13.0663 | 12.1939 | 11.5296 | 9.5908 | 8.2316 | 7.5878
|  | BIRDHAM PRIMARY | FB |  |  |  |  | -0.31938 | -0.21121 | -0.13468 | 15.1133 | 15.001 | 14.8021 | 14.5072 | 14.2674 | 14.0541 | 12.3745 | 10.4918 | 9.2459 | 2.1633 | 2.1867 | 2.1643 | 16.1429 | 15.999 | 15.7704 | 15.4316 | 15.1276 | 14.8265 | 12.6816 | 10.1612 | 7.4684 | 0.97144 | 1.0735 | 1.1296 | 15.6143 | 15.5765 | 15.4327 | 15.201 | 15.0082 | 14.8276 | 13.4102 | 11.8776 | 10.848
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM PRIMARY | MINIMUM HEADROOM | SU 56691 16683 | NO | NO | 2.202 | 6.5146 | 21.7948 | 21.7315 | 21.4774 | 21.0305 | 20.2662 | 19.453 | 18.5387 | 17.7877 | 14.8326 | 13.6795 | 13.5683 | 10.6813 | 24.9091 | 24.7448 | 24.4703 | 24.005 | 23.2121 | 22.3621 | 21.4111 | 20.6142 | 17.504 | 15.8417 | 13.9162 | 8.2023 | 23.0244 | 22.9244 | 22.6703 | 22.2091 | 21.353 | 20.4213 | 19.3877 | 18.5264 | 15.2683 | 14.2662 | 14.4958
|  | BISHOPS WALTHAM PRIMARY | EE |  |  |  |  | 6.5166 | 21.7979 | 21.7519 | 21.5489 | 21.1672 | 20.453 | 19.9142 | 18.9907 | 18.3826 | 15.8897 | 14.2989 | 13.9611 | 10.6854 | 24.9132 | 24.7632 | 24.5295 | 24.1121 | 23.3479 | 22.7121 | 21.7407 | 21.0499 | 17.9203 | 15.8417 | 14.6621 | 8.2064 | 23.0285 | 22.9468 | 22.7397 | 22.2815 | 21.4326 | 20.707 | 19.6132 | 18.8315 | 15.9907 | 14.5764 | 14.5254
|  | BISHOPS WALTHAM PRIMARY | HT |  |  |  |  | 6.5146 | 21.7968 | 21.7315 | 21.4774 | 21.0305 | 20.2662 | 19.453 | 18.5387 | 17.7877 | 14.8326 | 13.6795 | 13.5683 | 10.6813 | 24.9101 | 24.7448 | 24.4703 | 24.005 | 23.2121 | 22.3621 | 21.4111 | 20.6142 | 17.504 | 16.2734 | 16.0448 | 8.2023 | 23.0254 | 22.9244 | 22.6703 | 22.2091 | 21.353 | 20.4213 | 19.3877 | 18.5264 | 15.2683 | 14.2662 | 14.4958
|  | BISHOPS WALTHAM PRIMARY | HE |  |  |  |  | 6.5146 | 21.7948 | 21.7499 | 21.5295 | 21.1407 | 20.4652 | 19.9142 | 18.9703 | 18.3581 | 16.3826 | 15.3601 | 15.4019 | 10.6834 | 24.9091 | 24.7591 | 24.5152 | 24.0866 | 23.3519 | 22.6999 | 21.704 | 21.0019 | 18.3336 | 16.7132 | 15.7948 | 8.2023 | 23.0244 | 22.9407 | 22.7213 | 22.2519 | 21.4326 | 20.6948 | 19.5774 | 18.7887 | 16.4172 | 15.4846 | 15.6887
|  | BISHOPS WALTHAM PRIMARY | FB |  |  |  |  | 6.7074 | 22.105 | 22.3448 | 22.4642 | 22.5754 | 22.4652 | 22.3948 | 22.1356 | 21.8968 | 20.106 | 18.1438 | 16.7132 | 10.8374 | 25.1417 | 25.2162 | 25.1877 | 25.1366 | 24.8713 | 24.6081 | 24.2264 | 23.8172 | 20.9764 | 17.5438 | 13.9162 | 8.4289 | 23.3703 | 23.5836 | 23.6795 | 23.7805 | 23.6499 | 23.4989 | 23.1315 | 22.7795 | 20.404 | 18.2121 | 16.8591
NURSLING GSP | VELMORE BSP | BISHOPSTOKE PRIMARY | MINIMUM HEADROOM | SU 46463 18472 | NO | YES | 3.005 | 6.2342 | 6.2321 | 6.2301 | 6.2301 | 6.174 | 6.1607 | 6.1434 | 6.1219 | 6.1056 | 6.0617 | 6.0393 | 6.0372 | 6.55 | 6.548 | 6.549 | 6.549 | 6.4755 | 6.4602 | 6.4378 | 6.4092 | 6.3949 | 6.2765 | 6.1469 | 6.1388 | 6.548 | 6.548 | 6.5459 | 6.5459 | 6.499 | 6.4847 | 6.4694 | 6.452 | 6.4357 | 6.3837 | 6.3561 | 6.3592
|  | BISHOPSTOKE PRIMARY | EE |  |  |  |  | 6.2362 | 6.2342 | 6.2332 | 6.2342 | 6.2026 | 6.1668 | 6.1536 | 6.1332 | 6.1087 | 6.0628 | 6.0393 | 6.0454 | 6.5541 | 6.5541 | 6.5541 | 6.5541 | 6.5163 | 6.4673 | 6.4531 | 6.4265 | 6.398 | 6.2765 | 6.1469 | 6.1388 | 6.55 | 6.551 | 6.55 | 6.549 | 6.5245 | 6.4918 | 6.4827 | 6.4643 | 6.4408 | 6.3837 | 6.3571 | 6.3592
|  | BISHOPSTOKE PRIMARY | HT |  |  |  |  | 6.2352 | 6.2321 | 6.2321 | 6.2332 | 6.174 | 6.1648 | 6.1434 | 6.1219 | 6.1148 | 6.0617 | 6.0403 | 6.0485 | 6.5531 | 6.552 | 6.5541 | 6.5541 | 6.4755 | 6.4673 | 6.4378 | 6.4122 | 6.4061 | 6.2847 | 6.152 | 6.1694 | 6.548 | 6.549 | 6.548 | 6.548 | 6.499 | 6.4908 | 6.4694 | 6.4531 | 6.4469 | 6.3857 | 6.3561 | 6.3653
|  | BISHOPSTOKE PRIMARY | HE |  |  |  |  | 6.2352 | 6.2321 | 6.2301 | 6.2301 | 6.1964 | 6.1607 | 6.1454 | 6.123 | 6.1056 | 6.0709 | 6.0811 | 6.0852 | 6.552 | 6.551 | 6.55 | 6.549 | 6.5112 | 6.4602 | 6.4418 | 6.4092 | 6.3949 | 6.3531 | 6.3724 | 6.3837 | 6.549 | 6.548 | 6.5459 | 6.5459 | 6.5184 | 6.4847 | 6.4704 | 6.452 | 6.4357 | 6.4 | 6.4102 | 6.4133
|  | BISHOPSTOKE PRIMARY | FB |  |  |  |  | 6.2342 | 6.2362 | 6.2362 | 6.2342 | 6.2352 | 6.2332 | 6.2291 | 6.2281 | 6.226 | 6.1372 | 6.0893 | 6.0372 | 6.55 | 6.548 | 6.549 | 6.549 | 6.548 | 6.5469 | 6.5429 | 6.5398 | 6.5388 | 6.4337 | 6.3714 | 6.2806 | 6.548 | 6.549 | 6.549 | 6.55 | 6.549 | 6.5459 | 6.5439 | 6.5429 | 6.5429 | 6.4643 | 6.4194 | 6.3663
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE PRIMARY | MINIMUM HEADROOM | SU 45116 13082 | NO | NO | 0.5 | 3.8939 | 3.9684 | 4.0163 | 3.9469 | 3.8184 | 3.6439 | 3.3092 | 2.9633 | 2.5684 | 1.0684 | 0.27347 | -0.044898 | 5.3602 | 5.2888 | 5.2357 | 5.0633 | 4.8357 | 4.5276 | 3.9755 | 3.4959 | 3.0551 | 0.83469 | -3.5122 | -9.3939 | 4.748 | 4.7837 | 4.8224 | 4.7316 | 4.5949 | 4.3806 | 3.9378 | 3.5296 | 3.1694 | 1.7286 | 0.99898 | 0.77857
|  | BITTERNE PRIMARY | EE |  |  |  |  | 3.8939 | 3.9735 | 4.052 | 4.0449 | 3.9878 | 3.749 | 3.4255 | 3.1408 | 2.7663 | 1.2929 | 0.32143 | -0.044898 | 5.3622 | 5.2969 | 5.2643 | 5.1194 | 4.9316 | 4.5276 | 4.0439 | 3.6214 | 3.1765 | 0.83469 | -1.149 | -3.3612 | 4.748 | 4.7837 | 4.8449 | 4.801 | 4.7173 | 4.4092 | 4.0214 | 3.7061 | 3.3286 | 1.9327 | 1.0633 | 0.77857
|  | BITTERNE PRIMARY | HT |  |  |  |  | 3.8959 | 3.9684 | 4.0163 | 3.9469 | 3.8184 | 3.6439 | 3.3092 | 2.9633 | 2.5684 | 1.0684 | 0.27347 | 0.16939 | 5.3602 | 5.2888 | 5.2357 | 5.0633 | 4.8357 | 4.5398 | 3.9755 | 3.4959 | 3.0551 | 1.5347 | 0.74286 | 0.32857 | 4.749 | 4.7847 | 4.8224 | 4.7316 | 4.5949 | 4.3806 | 3.9378 | 3.5296 | 3.1694 | 1.7286 | 0.99898 | 0.94694
|  | BITTERNE PRIMARY | HE |  |  |  |  | 3.901 | 3.9847 | 4.0704 | 4.0531 | 3.9878 | 3.7592 | 3.45 | 3.1714 | 2.7827 | 1.5918 | 0.8102 | 0.52041 | 5.3633 | 5.299 | 5.2673 | 5.1235 | 4.9347 | 4.5316 | 4.0469 | 3.6224 | 3.1714 | 0.9449 | -1.0541 | -3.3469 | 4.751 | 4.7949 | 4.8602 | 4.8112 | 4.7194 | 4.4153 | 4.0367 | 3.7235 | 3.348 | 2.201 | 1.4867 | 1.2388
|  | BITTERNE PRIMARY | FB |  |  |  |  | 4.0673 | 4.2061 | 4.3163 | 4.4061 | 4.5153 | 4.5041 | 4.4663 | 4.4071 | 4.35 | 3.7622 | 2.502 | 1.7541 | 5.4306 | 5.3633 | 5.2684 | 5.1388 | 4.9959 | 4.6673 | 4.3061 | 3.9265 | 3.5378 | 0.86224 | -3.5122 | -9.3939 | 4.949 | 5.0561 | 5.1398 | 5.2031 | 5.298 | 5.2663 | 5.2041 | 5.1173 | 5.0286 | 4.2541 | 2.9531 | 2.2653
MINETY GSP | STRATTON (RESERVE) BSP | BLACK BOURTON PRIMARY | MINIMUM HEADROOM | SP 28349 03818 | NO | NO | 0.978 | 7.9796 | 7.9939 | 7.9786 | 7.8041 | 7.6898 | 7.349 | 7.0408 | 6.7 | 6.3378 | 5.1918 | 4.1959 | 3.5959 | 9.2622 | 9.2408 | 9.1847 | 8.949 | 8.8143 | 8.5602 | 8.349 | 8.0929 | 7.8531 | 7.1 | 6.6 | 5.8173 | 8.7602 | 8.751 | 8.7071 | 8.4837 | 8.4031 | 8.1122 | 7.8694 | 7.5612 | 7.2745 | 6.3082 | 5.6122 | 5.2765
|  | BLACK BOURTON PRIMARY | EE |  |  |  |  | 7.9806 | 7.9939 | 7.9939 | 7.8561 | 7.751 | 7.4245 | 7.0653 | 6.7643 | 6.4418 | 5.199 | 4.2378 | 3.7265 | 9.2653 | 9.2408 | 9.202 | 8.9724 | 8.848 | 8.6163 | 8.349 | 8.1439 | 7.9173 | 7.151 | 6.6 | 6.2194 | 8.7612 | 8.7541 | 8.7265 | 8.5286 | 8.4622 | 8.1867 | 7.8796 | 7.6296 | 7.3541 | 6.35 | 5.6561 | 5.3418
|  | BLACK BOURTON PRIMARY | HT |  |  |  |  | 7.9816 | 7.9949 | 7.9786 | 7.8041 | 7.6898 | 7.349 | 7.0602 | 6.7041 | 6.3735 | 5.1918 | 4.1959 | 3.5959 | 9.2622 | 9.2408 | 9.1847 | 8.949 | 8.8143 | 8.5602 | 8.3582 | 8.0929 | 7.8531 | 7.1 | 6.7357 | 6.6408 | 8.7602 | 8.751 | 8.7071 | 8.4837 | 8.4031 | 8.1122 | 7.8694 | 7.5612 | 7.2745 | 6.3082 | 5.6122 | 5.2765
|  | BLACK BOURTON PRIMARY | HE |  |  |  |  | 7.9796 | 7.9939 | 7.9959 | 7.8418 | 7.7255 | 7.3786 | 7.0408 | 6.7 | 6.3378 | 5.4051 | 4.6418 | 4.1847 | 9.2643 | 9.2408 | 9.202 | 8.9714 | 8.8408 | 8.6061 | 8.3796 | 8.1449 | 7.8939 | 7.2776 | 6.8755 | 6.4469 | 8.7602 | 8.752 | 8.7276 | 8.5184 | 8.4469 | 8.1571 | 7.8755 | 7.5939 | 7.2867 | 6.5143 | 6.0133 | 5.7102
|  | BLACK BOURTON PRIMARY | FB |  |  |  |  | 8.0561 | 8.099 | 8.1224 | 8.1327 | 8.1408 | 8.1306 | 8.1 | 8.1 | 7.9092 | 7.2245 | 6.4561 | 5.9347 | 9.352 | 9.352 | 9.3276 | 9.3122 | 9.2837 | 9.2092 | 9.1245 | 9.0949 | 8.8071 | 7.9847 | 6.9327 | 5.8173 | 8.8765 | 8.9071 | 8.9163 | 8.9276 | 8.9306 | 8.8908 | 8.8398 | 8.8643 | 8.5827 | 7.9276 | 7.2286 | 6.7418
MANNINGTON GSP | LYTCHETT BSP | BLANDFORD PRIMARY | MINIMUM HEADROOM | ST 88810 05536 | NO | NO | 4.748 | 21.4576 | 21.3454 | 21.0087 | 20.4107 | 19.6944 | 18.5954 | 17.3689 | 16.1678 | 14.7689 | 9.7087 | 5.9607 | 3.6658 | 25.2495 | 25.125 | 24.9536 | 24.6709 | 24.3168 | 23.6933 | 22.775 | 22.0036 | 21.1923 | 18.2464 | 16.326 | 13.5668 | 22.9556 | 22.8229 | 22.5556 | 22.0862 | 21.4311 | 20.477 | 19.2474 | 18.1729 | 17.0791 | 13.1342 | 10.4964 | 9.0831
|  | BLANDFORD PRIMARY | EE |  |  |  |  | 21.4729 | 21.378 | 21.1209 | 20.6791 | 20.126 | 19.1219 | 18.0301 | 16.9566 | 15.9066 | 11.4791 | 8.027 | 5.8607 | 25.2576 | 25.1413 | 24.9984 | 24.7954 | 24.5168 | 23.9852 | 23.1811 | 22.4801 | 21.7627 | 18.4536 | 16.326 | 14.7148 | 22.9678 | 22.8464 | 22.6311 | 22.3219 | 21.8556 | 20.977 | 19.9291 | 18.9801 | 18.0219 | 14.326 | 11.7658 | 10.2607
|  | BLANDFORD PRIMARY | HT |  |  |  |  | 21.4576 | 21.3454 | 21.0087 | 20.4107 | 19.6944 | 18.5954 | 17.3689 | 16.1678 | 14.7689 | 9.7087 | 5.9607 | 3.6658 | 25.2495 | 25.125 | 24.9536 | 24.6709 | 24.3168 | 23.6933 | 22.775 | 22.0036 | 21.1923 | 18.2464 | 16.676 | 16.0811 | 22.9556 | 22.8229 | 22.5556 | 22.0862 | 21.4311 | 20.477 | 19.2474 | 18.1729 | 17.0791 | 13.1342 | 10.4964 | 9.0831
|  | BLANDFORD PRIMARY | HE |  |  |  |  | 21.4729 | 21.3872 | 21.1403 | 20.6638 | 20.0944 | 19.0678 | 17.9689 | 16.874 | 15.7974 | 12.3138 | 9.4678 | 7.8352 | 25.2566 | 25.1536 | 25.0178 | 24.7882 | 24.5056 | 23.9464 | 23.1729 | 22.4729 | 21.7505 | 19.0189 | 17.325 | 15.8362 | 22.9678 | 22.8474 | 22.6689 | 22.3036 | 21.8178 | 20.9209 | 19.9005 | 18.9423 | 17.9729 | 15.0433 | 13.0066 | 11.8648
|  | BLANDFORD PRIMARY | FB |  |  |  |  | 21.6587 | 21.624 | 21.5342 | 21.4444 | 21.2648 | 21.0433 | 20.7964 | 20.5117 | 20.2036 | 18.3127 | 15.775 | 13.6801 | 25.3617 | 25.3046 | 25.2454 | 25.2168 | 25.1138 | 24.8382 | 24.5199 | 24.1484 | 23.7117 | 20.9944 | 17.475 | 13.5668 | 23.1158 | 23.0648 | 22.9984 | 22.9617 | 22.827 | 22.6566 | 22.4668 | 22.2291 | 21.8515 | 19.6546 | 17.1811 | 15.3127
COWLEY GSP | WITNEY BSP | BLEDINGTON PRIMARY | MINIMUM HEADROOM | SP 25641 22580 | YES | NO | 1.009 | 9.3775 | 9.401 | 9.4184 | 9.3878 | 9.1643 | 9.1378 | 8.9969 | 8.8194 | 8.6439 | 8.2051 | 7.8816 | 7.749 | 11.5571 | 11.5398 | 11.5122 | 11.4653 | 11.2224 | 11.1969 | 11.0367 | 10.852 | 10.6826 | 10.1541 | 9.8041 | 9.1194 | 10.0796 | 10.0908 | 10.0929 | 10.0612 | 9.8102 | 9.7888 | 9.6245 | 9.4398 | 9.2643 | 8.8153 | 8.5571 | 8.5031
|  | BLEDINGTON PRIMARY | EE |  |  |  |  | 9.3775 | 9.401 | 9.4204 | 9.4092 | 9.2775 | 9.1816 | 9.0612 | 8.8306 | 8.6663 | 8.2316 | 7.9398 | 7.8143 | 11.5582 | 11.5408 | 11.5204 | 11.4878 | 11.3357 | 11.2235 | 11.1051 | 10.8735 | 10.7071 | 10.1541 | 9.8041 | 9.5326 | 10.0796 | 10.0908 | 10.0959 | 10.0806 | 9.9357 | 9.8153 | 9.6959 | 9.4735 | 9.3071 | 8.8571 | 8.6051 | 8.5235
|  | BLEDINGTON PRIMARY | HT |  |  |  |  | 9.3847 | 9.4112 | 9.4184 | 9.3878 | 9.1643 | 9.1378 | 8.9969 | 8.8194 | 8.648 | 8.2051 | 7.8816 | 7.749 | 11.5571 | 11.5398 | 11.5122 | 11.4653 | 11.2224 | 11.1969 | 11.0367 | 10.852 | 10.6826 | 10.1929 | 9.9541 | 9.9143 | 10.0826 | 10.0959 | 10.0929 | 10.0612 | 9.8102 | 9.7888 | 9.6245 | 9.4398 | 9.2643 | 8.8153 | 8.5571 | 8.5031
|  | BLEDINGTON PRIMARY | HE |  |  |  |  | 9.3796 | 9.4041 | 9.4235 | 9.399 | 9.2806 | 9.1571 | 9.0275 | 8.8316 | 8.6439 | 8.3255 | 8.0755 | 7.95 | 11.5592 | 11.5418 | 11.5224 | 11.4857 | 11.3347 | 11.2153 | 11.0959 | 10.902 | 10.7235 | 10.2337 | 9.949 | 9.6806 | 10.0806 | 10.0918 | 10.098 | 10.0745 | 9.9275 | 9.802 | 9.6908 | 9.4908 | 9.3041 | 8.948 | 8.7541 | 8.6704
|  | BLEDINGTON PRIMARY | FB |  |  |  |  | 9.4704 | 9.5214 | 9.5714 | 9.6092 | 9.6224 | 9.6255 | 9.6082 | 9.5796 | 9.549 | 9.3837 | 8.7908 | 8.5 | 11.6245 | 11.6224 | 11.6224 | 11.6133 | 11.5816 | 11.5347 | 11.4694 | 11.398 | 11.3204 | 10.8908 | 9.9714 | 9.1194 | 10.1602 | 10.1888 | 10.2153 | 10.2326 | 10.2337 | 10.2337 | 10.2194 | 10.1959 | 10.1541 | 9.9439 | 9.3388 | 9.0326
FLEET-BRAMLEY GSP | ALTON BSP | BORDON PRIMARY | MINIMUM HEADROOM | SU 82256 35269 | NO | NO | 7.347 | 8.366 | 8.0456 | 6.9211 | 5.8732 | 4.7028 | 2.7579 | 0.64256 | -1.6136 | -3.6258 | -10.5901 | -15.6829 | -18.8687 | 14.8681 | 14.5691 | 13.5762 | 13.0375 | 12.3997 | 11.4956 | 10.4068 | 9.2395 | 8.2324 | 4.7895 | 2.5426 | -2.585 | 11.1681 | 10.8201 | 9.5732 | 8.7273 | 7.7436 | 6.2548 | 4.5681 | 2.8477 | 1.3436 | -3.8778 | -7.3217 | -9.2023
|  | BORDON PRIMARY | EE |  |  |  |  | 8.3681 | 8.0466 | 7.0201 | 6.2813 | 5.4722 | 3.8324 | 2.0497 | 0.19664 | -1.4738 | -7.3962 | -12.0554 | -14.9166 | 14.8701 | 14.5711 | 13.6497 | 13.2415 | 12.7405 | 11.9599 | 11.0528 | 10.0538 | 9.1854 | 5.3232 | 2.5997 | 0.47318 | 11.1681 | 10.8201 | 9.6609 | 9.0395 | 8.3242 | 7.0497 | 5.6324 | 4.1803 | 2.914 | -1.7564 | -5.1074 | -6.988
|  | BORDON PRIMARY | HT |  |  |  |  | 8.3742 | 8.0824 | 6.9211 | 5.8732 | 4.7028 | 2.7579 | 0.64256 | -1.6136 | -3.6258 | -10.5901 | -15.6829 | -18.8687 | 14.8701 | 14.5742 | 13.5762 | 13.0375 | 12.3997 | 11.4956 | 10.4068 | 9.2395 | 8.2324 | 4.7895 | 2.9405 | 2.1997 | 11.1722 | 10.8385 | 9.5732 | 8.7273 | 7.7436 | 6.2548 | 4.5681 | 2.8477 | 1.3436 | -3.8778 | -7.3217 | -9.2023
|  | BORDON PRIMARY | HE |  |  |  |  | 8.366 | 8.0456 | 7.0181 | 6.2824 | 5.4548 | 3.812 | 1.9844 | 0.098686 | -1.585 | -6.6789 | -10.7574 | -12.9299 | 14.8681 | 14.5691 | 13.6477 | 13.2395 | 12.7324 | 11.9895 | 11.0589 | 10.0589 | 9.2058 | 5.5895 | 3.1099 | 0.99154 | 11.1681 | 10.8201 | 9.6579 | 9.0385 | 8.3109 | 7.063 | 5.6089 | 4.1395 | 2.8762 | -1.2125 | -4.1013 | -5.5717
|  | BORDON PRIMARY | FB |  |  |  |  | 8.6242 | 8.5038 | 7.9599 | 7.8334 | 7.3609 | 6.7987 | 6.1885 | 5.6344 | 5.1813 | 2.1589 | -1.6952 | -3.9064 | 14.9528 | 14.7007 | 14.0017 | 13.866 | 13.4303 | 12.9609 | 12.4568 | 11.913 | 11.3507 | 7.6089 | 2.5426 | -2.585 | 11.4283 | 11.2528 | 10.6364 | 10.5466 | 10.0558 | 9.5671 | 9.0589 | 8.5171 | 8.066 | 5.1007 | 1.6742 | -0.25846
FLEET-BRAMLEY GSP | ALTON BSP | BORDON NORTH PRIMARY | MINIMUM HEADROOM | SU 82256 35269 | NO | NO | 20 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6
|  | BORDON NORTH PRIMARY | EE |  |  |  |  | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6
|  | BORDON NORTH PRIMARY | HT |  |  |  |  | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6
|  | BORDON NORTH PRIMARY | HE |  |  |  |  | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6
|  | BORDON NORTH PRIMARY | FB |  |  |  |  | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | BOSCOMBE DOWN PRIMARY | MINIMUM HEADROOM | SU 17186 41044 | NO | NO | 1.527 | 9.764 | 9.7589 | 9.7324 | 9.5732 | 9.4334 | 9.1253 | 8.7783 | 8.4008 | 8.0396 | 5.7661 | 4.3692 | 3.5681 | 11.2151 | 11.2049 | 11.1743 | 11.0794 | 11.012 | 10.8181 | 10.5763 | 10.3243 | 10.0957 | 8.9885 | 8.3875 | 7.11 | 10.7222 | 10.712 | 10.6671 | 10.5365 | 10.412 | 10.1763 | 9.8692 | 9.5375 | 9.2273 | 7.6406 | 6.7263 | 6.2977
|  | BOSCOMBE DOWN PRIMARY | EE |  |  |  |  | 9.764 | 9.7589 | 9.7324 | 9.5926 | 9.4936 | 9.2069 | 8.9008 | 8.5834 | 8.2865 | 6.2202 | 5.0375 | 4.3334 | 11.2151 | 11.2059 | 11.1763 | 11.0926 | 11.0528 | 10.8824 | 10.6569 | 10.4324 | 10.2416 | 9.0273 | 8.3875 | 7.864 | 10.7222 | 10.712 | 10.6671 | 10.5477 | 10.4579 | 10.2324 | 9.9508 | 9.6579 | 9.3926 | 7.9487 | 7.1038 | 6.6385
|  | BOSCOMBE DOWN PRIMARY | HT |  |  |  |  | 9.764 | 9.76 | 9.7334 | 9.5732 | 9.4334 | 9.1253 | 8.7783 | 8.4008 | 8.0396 | 5.7661 | 4.3692 | 3.5681 | 11.2151 | 11.2049 | 11.1743 | 11.0794 | 11.012 | 10.8181 | 10.5763 | 10.3243 | 10.0957 | 8.9885 | 8.5477 | 8.3763 | 10.7253 | 10.713 | 10.6712 | 10.5365 | 10.412 | 10.1763 | 9.8692 | 9.5375 | 9.2273 | 7.6406 | 6.7263 | 6.2977
|  | BOSCOMBE DOWN PRIMARY | HE |  |  |  |  | 9.7651 | 9.762 | 9.7355 | 9.5916 | 9.4865 | 9.211 | 8.9192 | 8.6018 | 8.3069 | 6.4794 | 5.4416 | 4.8804 | 11.2151 | 11.2059 | 11.1743 | 11.0926 | 11.0508 | 10.8794 | 10.6712 | 10.4426 | 10.2355 | 9.1569 | 8.5814 | 8.061 | 10.7243 | 10.7161 | 10.6732 | 10.5508 | 10.4549 | 10.2355 | 9.9722 | 9.6743 | 9.4059 | 8.1314 | 7.5232 | 7.1549
|  | BOSCOMBE DOWN PRIMARY | FB |  |  |  |  | 9.8375 | 9.8508 | 9.864 | 9.8538 | 9.8416 | 9.7947 | 9.7732 | 9.712 | 9.6049 | 8.4794 | 7.7906 | 7.3783 | 11.264 | 11.2528 | 11.2416 | 11.2243 | 11.1875 | 11.1243 | 11.0926 | 11.0181 | 10.8028 | 9.6518 | 8.4375 | 7.11 | 10.7906 | 10.7957 | 10.7987 | 10.7875 | 10.7569 | 10.7089 | 10.6957 | 10.6375 | 10.5181 | 9.5518 | 8.8661 | 8.4753
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST PRIMARY | MINIMUM HEADROOM | SZ 11636 92447 | NO | NO | 13.284 | 7.3622 | 7.3143 | 7.2776 | 7.0143 | 6.7173 | 6.0153 | 5.2653 | 4.45 | 3.6296 | 0.40612 | -1.9347 | -2.8653 | 9.1827 | 9.0714 | 8.9633 | 8.7 | 8.4184 | 7.951 | 7.402 | 6.7857 | 6.1378 | 3.8173 | 1.1888 | -3.4602 | 7.8806 | 7.8592 | 7.8531 | 7.5918 | 7.2745 | 6.6724 | 6.0051 | 5.2643 | 4.499 | 1.6878 | -0.15816 | -0.91429
|  | BOSCOMBE EAST PRIMARY | EE |  |  |  |  | 7.3673 | 7.4031 | 7.3408 | 7.149 | 6.9224 | 6.3102 | 5.6276 | 4.8888 | 4.151 | 0.98878 | -1.398 | -2.7061 | 9.1898 | 9.1714 | 8.999 | 8.7796 | 8.5265 | 8.1439 | 7.6745 | 7.1133 | 6.5408 | 3.8173 | 1.7786 | -0.10714 | 7.8806 | 7.9061 | 7.8684 | 7.6776 | 7.4143 | 6.9031 | 6.2908 | 5.6051 | 4.9092 | 2.0306 | 0.079592 | -0.91429
|  | BOSCOMBE EAST PRIMARY | HT |  |  |  |  | 7.3622 | 7.3143 | 7.2776 | 7.0143 | 6.7173 | 6.0153 | 5.2653 | 4.45 | 3.6296 | 0.40612 | -1.9347 | -2.8653 | 9.1827 | 9.0714 | 8.9633 | 8.7 | 8.4184 | 7.951 | 7.402 | 6.7857 | 6.1378 | 4.0969 | 2.952 | 2.4653 | 7.8837 | 7.8592 | 7.8531 | 7.5918 | 7.2745 | 6.6724 | 6.0051 | 5.2643 | 4.499 | 1.6878 | -0.15816 | -0.78776
|  | BOSCOMBE EAST PRIMARY | HE |  |  |  |  | 7.3765 | 7.3622 | 7.3765 | 7.1418 | 6.8765 | 6.3316 | 5.7286 | 5.0776 | 4.4163 | 2.1633 | 0.25306 | -0.71122 | 9.1898 | 9.1102 | 9.0276 | 8.8031 | 8.552 | 8.149 | 7.699 | 7.1724 | 6.6112 | 4.3888 | 2.4327 | 0.64898 | 7.8898 | 7.8929 | 7.8847 | 7.6898 | 7.399 | 6.9112 | 6.3561 | 5.7408 | 5.0939 | 3.0551 | 1.501 | 0.78367
|  | BOSCOMBE EAST PRIMARY | FB |  |  |  |  | 7.5347 | 7.6592 | 7.752 | 7.7959 | 7.7418 | 7.652 | 7.5235 | 7.399 | 7.2592 | 6.0469 | 3.9847 | 2.4051 | 9.2378 | 9.2112 | 9.151 | 9.0653 | 8.8367 | 8.5408 | 8.1969 | 7.8714 | 7.5235 | 5.0224 | 1.1888 | -3.4602 | 8.0031 | 8.0929 | 8.1571 | 8.151 | 8.0918 | 8.0122 | 7.9061 | 7.7939 | 7.6724 | 6.3337 | 4.2918 | 2.7378
EALING GSP |  | BOSTON MANOR PRIMARY | MINIMUM HEADROOM | TQ 17043 78092 | NO | NO | 12.454 | 7.2706 | 6.9941 | 45.1432 | 44.937 | 44.5758 | 44.2636 | 43.9513 | 43.6595 | 43.3799 | 42.4411 | 41.1483 | 40.4595 | 4.7206 | 4.5288 | 39.4891 | 39.337 | 39.0217 | 38.7738 | 38.4768 | 38.2146 | 37.9544 | 36.2278 | 33.2156 | 29.2176 | 7.1369 | 6.889 | 42.9809 | 42.7983 | 42.4625 | 42.1789 | 41.8819 | 41.6095 | 41.3452 | 40.538 | 40.0727 | 39.8299
|  | BOSTON MANOR PRIMARY | EE |  |  |  |  | 7.2706 | 6.9941 | 45.1432 | 44.937 | 44.7156 | 44.4136 | 44.1442 | 43.885 | 43.6411 | 42.4778 | 41.1483 | 40.4595 | 4.7206 | 4.5288 | 39.4891 | 39.337 | 39.1758 | 38.9258 | 38.6636 | 38.4146 | 38.1748 | 36.2278 | 34.5544 | 32.7605 | 7.1369 | 6.889 | 42.9809 | 42.7983 | 42.6013 | 42.3238 | 42.0676 | 41.8187 | 41.587 | 40.7064 | 40.2329 | 39.8299
|  | BOSTON MANOR PRIMARY | HT |  |  |  |  | 7.2747 | 7.0084 | 45.1687 | 44.9554 | 44.5758 | 44.2636 | 43.9513 | 43.6595 | 43.3799 | 42.4411 | 41.3625 | 41.0136 | 4.7206 | 4.5298 | 39.4921 | 39.338 | 39.0217 | 38.7738 | 38.4768 | 38.2146 | 37.9544 | 36.787 | 35.9666 | 35.437 | 7.14 | 6.9023 | 43.0034 | 42.8146 | 42.4625 | 42.1789 | 41.8819 | 41.6095 | 41.3452 | 40.538 | 40.0727 | 39.935
|  | BOSTON MANOR PRIMARY | HE |  |  |  |  | 7.2737 | 7.0002 | 45.1564 | 44.9391 | 44.7125 | 44.4166 | 44.1452 | 43.8952 | 43.6595 | 42.9462 | 42.3136 | 41.9289 | 4.7206 | 4.5288 | 39.4921 | 39.337 | 39.1748 | 38.9248 | 38.6574 | 38.4125 | 38.185 | 36.5054 | 35.0921 | 33.4391 | 7.139 | 6.8951 | 42.9942 | 42.8013 | 42.6003 | 42.3268 | 42.0656 | 41.8248 | 41.5983 | 40.9105 | 40.6136 | 40.4891
|  | BOSTON MANOR PRIMARY | FB |  |  |  |  | 7.3288 | 7.089 | 45.2758 | 45.136 | 44.984 | 44.838 | 44.7136 | 44.584 | 44.5207 | 43.8401 | 43.2799 | 42.4962 | 4.7574 | 4.5849 | 39.5585 | 39.4697 | 39.3636 | 39.2023 | 38.8748 | 38.538 | 38.3013 | 36.2432 | 33.2156 | 29.2176 | 7.1931 | 6.9839 | 43.1034 | 42.984 | 42.8534 | 42.7278 | 42.6044 | 42.4748 | 42.4105 | 41.7207 | 41.1727 | 40.8503
MANNINGTON GSP | BOURNEMOUTH BSP | BOURNE VALLEY PRIMARY | MINIMUM HEADROOM | SZ 06207 92415 | NO | YES | 4.952 | 4.8133 | 4.6306 | 4.2031 | 3.45 | 2.7429 | 0.92449 | -0.97857 | -3.0214 | -5.0378 | -11.1459 | -15.5857 | -17.5418 | 9.851 | 9.6327 | 9.25 | 8.7224 | 8.248 | 7.3541 | 6.3367 | 5.2214 | 4.1102 | 0.89388 | -2.7531 | -9.7245 | 7.0541 | 6.8949 | 6.4827 | 5.7969 | 5.1653 | 3.7857 | 2.3031 | 0.7 | -0.88163 | -5.8204 | -9.2224 | -10.4092
|  | BOURNE VALLEY PRIMARY | EE |  |  |  |  | 4.85 | 4.7908 | 4.4786 | 4.0245 | 3.5133 | 2.1796 | 0.68776 | -0.91224 | -2.3704 | -8.0286 | -12.348 | -14.7082 | 9.8724 | 9.7163 | 9.349 | 8.9418 | 8.4786 | 7.8214 | 6.951 | 5.9724 | 5.1408 | 1.0235 | -2.0367 | -4.5949 | 7.0735 | 6.9714 | 6.6357 | 6.2 | 5.6755 | 4.6633 | 3.4541 | 2.1357 | 0.97959 | -3.7867 | -7.1847 | -8.8439
|  | BOURNE VALLEY PRIMARY | HT |  |  |  |  | 4.8133 | 4.6306 | 4.2031 | 3.45 | 2.7429 | 0.92449 | -0.97857 | -3.0214 | -5.0378 | -11.1459 | -15.5857 | -17.5418 | 9.851 | 9.6327 | 9.25 | 8.7224 | 8.248 | 7.3541 | 6.3367 | 5.2214 | 4.1102 | 0.89388 | -0.8949 | -1.4306 | 7.0541 | 6.8949 | 6.4827 | 5.7969 | 5.1653 | 3.7857 | 2.3031 | 0.7 | -0.88163 | -5.8204 | -9.2224 | -10.4092
|  | BOURNE VALLEY PRIMARY | HE |  |  |  |  | 4.8612 | 4.8122 | 4.5408 | 3.9827 | 3.402 | 2.2378 | 0.8551 | -0.59796 | -1.9214 | -6.5153 | -10.0949 | -11.9429 | 9.8755 | 9.7214 | 9.399 | 8.9357 | 8.4643 | 7.849 | 6.9592 | 6.0133 | 5.2061 | 1.4663 | -1.3786 | -3.9551 | 7.0837 | 7.0112 | 6.7143 | 6.1724 | 5.6031 | 4.7071 | 3.5459 | 2.3265 | 1.2561 | -2.6388 | -5.3755 | -6.6837
|  | BOURNE VALLEY PRIMARY | FB |  |  |  |  | 5.1245 | 5.2194 | 5.3439 | 5.3592 | 5.0857 | 4.8643 | 4.699 | 4.4224 | 4.1459 | 1.6888 | -2.0439 | -4.45 | 9.9173 | 9.7776 | 9.6602 | 9.5102 | 9.0449 | 8.5704 | 8.1245 | 7.5898 | 7.05 | 3.049 | -2.7531 | -9.7245 | 7.3296 | 7.3806 | 7.4582 | 7.4939 | 7.2265 | 6.9724 | 6.7796 | 6.4388 | 6.1173 | 3.6112 | 0.13265 | -2.1296
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON PRIMARY | MINIMUM HEADROOM | ST 77363 30262 | NO | NO | 2.119 | 3.5206 | 3.5002 | 3.3655 | 2.9655 | 2.5176 | 1.7624 | 0.95735 | 0.15224 | -0.63449 | -3.0365 | -4.8182 | -5.7304 | 5.9308 | 5.8624 | 5.7604 | 5.4676 | 5.1594 | 4.7206 | 4.2206 | 3.7022 | 3.2012 | 1.7033 | 0.56041 | -1.7794 | 4.6788 | 4.6278 | 4.5308 | 4.1839 | 3.7971 | 3.1849 | 2.5278 | 1.8594 | 1.2094 | -0.72939 | -1.9804 | -2.4447
|  | BOURTON PRIMARY | EE |  |  |  |  | 3.5308 | 3.5278 | 3.4451 | 3.2227 | 2.7706 | 2.1247 | 1.4186 | 0.70122 | 0.059388 | -2.0702 | -3.6916 | -4.509 | 5.941 | 5.8767 | 5.7992 | 5.6318 | 5.2604 | 4.8737 | 4.4441 | 3.9696 | 3.5635 | 1.7951 | 0.56041 | -0.33245 | 4.688 | 4.6482 | 4.591 | 4.4033 | 3.9727 | 3.4543 | 2.8788 | 2.2757 | 1.7482 | -0.052857 | -1.261 | -1.7539
|  | BOURTON PRIMARY | HT |  |  |  |  | 3.5206 | 3.5002 | 3.3655 | 2.9655 | 2.5176 | 1.7624 | 0.95735 | 0.15224 | -0.63449 | -3.0365 | -4.8182 | -5.7304 | 5.9308 | 5.8624 | 5.7604 | 5.4676 | 5.1594 | 4.7206 | 4.2206 | 3.7022 | 3.2012 | 1.7033 | 0.90837 | 0.73388 | 4.6788 | 4.6278 | 4.5308 | 4.1839 | 3.7971 | 3.1849 | 2.5278 | 1.8594 | 1.2094 | -0.72939 | -1.9804 | -2.4447
|  | BOURTON PRIMARY | HE |  |  |  |  | 3.5257 | 3.5278 | 3.4431 | 3.1359 | 2.7543 | 2.089 | 1.3951 | 0.64 | -0.014082 | -1.8131 | -3.2324 | -3.9294 | 5.9349 | 5.8767 | 5.7951 | 5.5461 | 5.2482 | 4.8563 | 4.4563 | 3.9563 | 3.5553 | 1.9308 | 0.86959 | -0.064082 | 4.6829 | 4.6482 | 4.588 | 4.3084 | 3.9614 | 3.4278 | 2.8706 | 2.2369 | 1.7073 | 0.15633 | -0.8498 | -1.2937
|  | BOURTON PRIMARY | FB |  |  |  |  | 3.7298 | 3.8084 | 3.7686 | 3.7737 | 3.7778 | 3.6461 | 3.491 | 3.3482 | 3.1839 | 1.7727 | 0.28796 | -0.60796 | 6.0584 | 6.0431 | 5.9359 | 5.8553 | 5.79 | 5.591 | 5.3686 | 5.1471 | 4.9033 | 3.0165 | 0.72265 | -1.7794 | 4.8798 | 4.9288 | 4.8798 | 4.8533 | 4.8798 | 4.7584 | 4.6186 | 4.4829 | 4.3267 | 2.9502 | 1.5982 | 0.78184
MANNINGTON GSP | WAREHAM BSP | BOVINGTON PRIMARY | MINIMUM HEADROOM | SY 83933 87831 | NO | YES | 0.117 | 4.1737 | 4.1472 | 4.1166 | 4.0135 | 3.8931 | 3.7135 | 3.4594 | 3.1962 | 2.9635 | 1.8992 | 1.1013 | 0.59515 | 4.8867 | 4.8673 | 4.8398 | 4.7898 | 4.7296 | 4.6714 | 4.5112 | 4.35 | 4.2163 | 3.7531 | 3.4122 | 2.5806 | 4.5449 | 4.5245 | 4.4939 | 4.4296 | 4.3378 | 4.201 | 3.9867 | 3.7633 | 3.5684 | 2.8816 | 2.3929 | 2.1082
|  | BOVINGTON PRIMARY | EE |  |  |  |  | 4.1758 | 4.1574 | 4.1441 | 4.0666 | 3.9758 | 3.8115 | 3.5737 | 3.3278 | 3.1125 | 2.1819 | 1.4645 | 1.039 | 4.8867 | 4.8735 | 4.8592 | 4.8224 | 4.7776 | 4.7388 | 4.6061 | 4.4663 | 4.3571 | 3.8061 | 3.4122 | 3.0694 | 4.5469 | 4.5316 | 4.5143 | 4.4694 | 4.3959 | 4.2724 | 4.0714 | 3.849 | 3.6612 | 3.0622 | 2.5908 | 2.3286
|  | BOVINGTON PRIMARY | HT |  |  |  |  | 4.1737 | 4.1472 | 4.1166 | 4.0135 | 3.8931 | 3.7135 | 3.4594 | 3.1962 | 2.9635 | 1.8992 | 1.1013 | 0.59515 | 4.8867 | 4.8673 | 4.8398 | 4.7898 | 4.7296 | 4.6714 | 4.5112 | 4.35 | 4.2163 | 3.7531 | 3.5071 | 3.3908 | 4.5449 | 4.5245 | 4.4939 | 4.4296 | 4.3378 | 4.201 | 3.9867 | 3.7633 | 3.5684 | 2.8816 | 2.3929 | 2.1082
|  | BOVINGTON PRIMARY | HE |  |  |  |  | 4.1758 | 4.1584 | 4.1441 | 4.0666 | 3.9768 | 3.8125 | 3.5727 | 3.339 | 3.1074 | 2.4166 | 1.7207 | 1.3829 | 4.8878 | 4.8735 | 4.8612 | 4.8224 | 4.7776 | 4.7378 | 4.6071 | 4.4878 | 4.3561 | 3.8796 | 3.4827 | 3.1388 | 4.5469 | 4.5316 | 4.5143 | 4.4694 | 4.3969 | 4.2745 | 4.0704 | 3.8633 | 3.6571 | 3.1663 | 2.7745 | 2.5602
|  | BOVINGTON PRIMARY | FB |  |  |  |  | 4.2237 | 4.2452 | 4.2472 | 4.2339 | 4.2288 | 4.1992 | 4.1564 | 4.1074 | 4.0625 | 3.7503 | 3.3727 | 3.0645 | 4.9265 | 4.9327 | 4.9255 | 4.902 | 4.8776 | 4.8265 | 4.7643 | 4.6969 | 4.6255 | 4.1857 | 3.4449 | 2.5806 | 4.5888 | 4.6051 | 4.6092 | 4.598 | 4.5867 | 4.5673 | 4.5418 | 4.501 | 4.4551 | 4.1449 | 3.7796 | 3.552
AMERSHAM GSP | LOUDWATER BSP | BOWERDEAN PRIMARY | MINIMUM HEADROOM | SU 87718 93880 | NO | YES | 5.388 | 3.2213 | 2.9304 | 2.4968 | 1.7039 | 0.9029 | -0.72976 | -2.4185 | -4.1389 | -5.9318 | -12.2502 | -16.6696 | -18.4093 | 9.1019 | 8.7825 | 8.3937 | 7.8111 | 7.1804 | 6.2029 | 5.0519 | 3.8702 | 2.6529 | -1.0308 | -3.7002 | -8.7512 | 6.4131 | 6.0764 | 5.6366 | 4.8907 | 4.11 | 2.7335 | 1.2192 | -0.31241 | -1.8828 | -6.9042 | -9.9757 | -10.7634
|  | BOWERDEAN PRIMARY | EE |  |  |  |  | 3.2213 | 2.9304 | 2.5192 | 1.8141 | 1.0968 | -0.47976 | -2.1257 | -3.8236 | -5.6012 | -11.3644 | -15.5849 | -17.5226 | 9.1019 | 8.7825 | 8.4233 | 7.9049 | 7.309 | 6.4304 | 5.3488 | 4.257 | 3.11 | -1.0308 | -3.7002 | -5.5798 | 6.4131 | 6.0764 | 5.656 | 4.9907 | 4.2662 | 2.9723 | 1.509 | 0.042694 | -1.4849 | -6.2318 | -9.3155 | -10.4747
|  | BOWERDEAN PRIMARY | HT |  |  |  |  | 3.2253 | 2.9396 | 2.4968 | 1.7039 | 0.9029 | -0.72976 | -2.4185 | -4.1389 | -5.9318 | -12.2502 | -16.6696 | -18.4093 | 9.1029 | 8.7825 | 8.3937 | 7.8111 | 7.1804 | 6.2029 | 5.0519 | 3.8702 | 2.6529 | -0.89404 | -2.49 | -2.6216 | 6.4182 | 6.0866 | 5.6366 | 4.8907 | 4.11 | 2.7335 | 1.2192 | -0.31241 | -1.8828 | -6.9042 | -9.9757 | -10.7634
|  | BOWERDEAN PRIMARY | HE |  |  |  |  | 3.2304 | 2.9478 | 2.5458 | 1.8111 | 1.0672 | -0.50424 | -2.1328 | -3.8185 | -5.6114 | -10.3747 | -14.1634 | -15.5675 | 9.1029 | 8.7856 | 8.4304 | 7.9049 | 7.3131 | 6.4172 | 5.3509 | 4.2488 | 3.0958 | -0.69914 | -3.3665 | -5.3114 | 6.4202 | 6.0927 | 5.6804 | 4.9947 | 4.2529 | 2.9488 | 1.5131 | 0.043714 | -1.4849 | -5.4747 | -8.2471 | -9.093
|  | BOWERDEAN PRIMARY | FB |  |  |  |  | 3.6702 | 3.7111 | 3.6488 | 3.5131 | 3.4335 | 3.1641 | 2.9468 | 2.6927 | 2.3366 | 0.022286 | -3.5869 | -5.4267 | 9.3988 | 9.2733 | 9.0641 | 8.8366 | 8.559 | 8.0509 | 7.51 | 6.96 | 6.2611 | 2.2304 | -3.2777 | -8.7512 | 6.8958 | 6.8886 | 6.7947 | 6.6407 | 6.5182 | 6.1978 | 5.8825 | 5.5498 | 5.0641 | 2.3325 | -1.1389 | -2.9196
FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL PRIMARY | MINIMUM HEADROOM | SU 86075 69397 | NO | NO | 15.464 | 32.9054 | 32.8156 | 32.5594 | 32.1829 | 31.4186 | 30.3707 | 28.9135 | 27.1043 | 25.1105 | 18.5768 | 14.6227 | 12.8564 | 35.686 | 35.5645 | 35.336 | 35.0564 | 34.436 | 33.7033 | 32.686 | 31.3349 | 29.8911 | 24.4319 | 21.037 | 17.5492 | 33.7441 | 33.6788 | 33.4972 | 33.24 | 32.6268 | 31.7911 | 30.4523 | 28.8125 | 27.0676 | 20.9298 | 17.3686 | 15.8564
|  | BRACKNELL PRIMARY | EE |  |  |  |  | 32.9054 | 32.8156 | 32.5594 | 32.2482 | 31.7676 | 30.8002 | 28.9135 | 27.1043 | 25.1105 | 18.5768 | 14.6227 | 12.8564 | 35.6931 | 35.5656 | 35.3554 | 35.1298 | 34.7768 | 34.1686 | 32.7278 | 31.3349 | 29.8911 | 24.4319 | 21.037 | 18.5594 | 33.7441 | 33.6788 | 33.4972 | 33.2788 | 32.9288 | 32.1839 | 30.4523 | 28.8125 | 27.0676 | 20.9298 | 17.3686 | 15.8564
|  | BRACKNELL PRIMARY | HT |  |  |  |  | 32.9145 | 32.8411 | 32.5727 | 32.1829 | 31.4186 | 30.3707 | 28.938 | 27.3115 | 25.5268 | 19.5247 | 16.0502 | 14.8737 | 35.686 | 35.5645 | 35.336 | 35.0564 | 34.436 | 33.7033 | 32.686 | 31.4054 | 30.088 | 26.3298 | 24.4217 | 23.7686 | 33.7513 | 33.7002 | 33.5196 | 33.24 | 32.6268 | 31.7911 | 30.5584 | 29.0941 | 27.536 | 22.237 | 19.2013 | 18.3605
|  | BRACKNELL PRIMARY | HE |  |  |  |  | 32.9207 | 32.8472 | 32.6094 | 32.2798 | 31.7778 | 30.9002 | 29.4349 | 27.9564 | 26.2666 | 21.4676 | 18.9543 | 17.9717 | 35.69 | 35.5686 | 35.3656 | 35.14 | 34.7819 | 34.1798 | 33.1635 | 32.089 | 30.9278 | 26.9411 | 24.4931 | 22.3962 | 33.7564 | 33.7084 | 33.5451 | 33.3094 | 32.94 | 32.236 | 30.9798 | 29.7064 | 28.2911 | 24.0472 | 21.9594 | 21.1982
|  | BRACKNELL PRIMARY | FB |  |  |  |  | 33.3135 | 33.2125 | 33.2084 | 33.2156 | 33.1074 | 32.8349 | 32.1258 | 31.4319 | 30.439 | 26.6227 | 23.488 | 21.5094 | 35.8502 | 35.6441 | 35.5309 | 35.3992 | 35.1492 | 34.7482 | 34.0217 | 33.2931 | 32.39 | 27.9543 | 23.1064 | 17.5492 | 34.0921 | 34.0054 | 34.0421 | 34.0543 | 33.986 | 33.7921 | 33.2717 | 32.7462 | 31.989 | 28.4768 | 25.4247 | 23.5554
MELKSHAM GSP | NORRINGTON BSP | BRADFORD-ON-AVON PRIMARY | MINIMUM HEADROOM | ST 81260 60564 | NO | YES | 2.885 | 8.332 | 8.3167 | 8.2687 | 8.1167 | 7.7738 | 7.4044 | 6.884 | 6.2901 | 5.6493 | 3.7187 | 2.6371 | 2.2697 | 13.5554 | 13.4513 | 13.3269 | 13.1156 | 12.7656 | 12.3564 | 11.8197 | 11.2064 | 10.5554 | 8.5871 | 7.0891 | 3.8646 | 11.1789 | 11.1462 | 11.0942 | 10.9442 | 10.6391 | 10.2677 | 9.7646 | 9.2034 | 8.5881 | 6.7044 | 5.6636 | 5.2238
|  | BRADFORD-ON-AVON PRIMARY | EE |  |  |  |  | 8.333 | 8.3177 | 8.282 | 8.1575 | 7.9003 | 7.485 | 7.0258 | 6.4901 | 5.9248 | 3.9932 | 2.8381 | 2.2911 | 13.5575 | 13.4513 | 13.3391 | 13.1483 | 12.832 | 12.4167 | 11.9299 | 11.3656 | 10.7758 | 8.5871 | 7.133 | 5.9789 | 11.1799 | 11.1493 | 11.1064 | 10.982 | 10.7422 | 10.3381 | 9.9095 | 9.3809 | 8.8371 | 6.9085 | 5.7707 | 5.2238
|  | BRADFORD-ON-AVON PRIMARY | HT |  |  |  |  | 8.332 | 8.3167 | 8.2687 | 8.1167 | 7.7738 | 7.4044 | 6.884 | 6.2901 | 5.6493 | 3.7187 | 2.6371 | 2.2697 | 13.5554 | 13.4513 | 13.3269 | 13.1156 | 12.7656 | 12.3564 | 11.8197 | 11.2064 | 10.5554 | 8.6116 | 7.684 | 7.4667 | 11.1789 | 11.1462 | 11.0942 | 10.9442 | 10.6391 | 10.2677 | 9.7646 | 9.2034 | 8.5881 | 6.7044 | 5.6636 | 5.3187
|  | BRADFORD-ON-AVON PRIMARY | HE |  |  |  |  | 8.333 | 8.3187 | 8.2789 | 8.1473 | 7.882 | 7.4901 | 6.9942 | 6.4473 | 5.8626 | 4.3269 | 3.0769 | 2.7309 | 13.5575 | 13.4513 | 13.336 | 13.1422 | 12.8218 | 12.4075 | 11.9064 | 11.332 | 10.7207 | 8.8718 | 7.3044 | 6.2779 | 11.1799 | 11.1483 | 11.1044 | 10.9748 | 10.7289 | 10.3371 | 9.8809 | 9.3493 | 8.783 | 7.2422 | 6.0064 | 5.6626
|  | BRADFORD-ON-AVON PRIMARY | FB |  |  |  |  | 8.735 | 8.8779 | 8.7299 | 8.7922 | 8.8167 | 8.6575 | 8.5279 | 8.333 | 8.1452 | 6.7677 | 4.9299 | 3.7401 | 13.8881 | 13.9054 | 13.6554 | 13.6136 | 13.5177 | 13.2269 | 12.9738 | 12.6544 | 12.3269 | 10.1289 | 7.0891 | 3.8646 | 11.5809 | 11.7044 | 11.5534 | 11.6116 | 11.633 | 11.4769 | 11.3462 | 11.1452 | 10.9575 | 9.5728 | 7.7442 | 6.5534
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BRAMLEY GREEN PRIMARY | MINIMUM HEADROOM | SU 67431 58511 | NO | NO | 0.833 | 10.3439 | 10.2439 | 10.0918 | 9.9051 | 9.8378 | 9.5286 | 9.0357 | 8.3806 | 7.8582 | 6.4357 | 5.548 | 5.0031 | 11.5888 | 11.5541 | 11.4816 | 11.3857 | 11.3071 | 11.1745 | 10.9724 | 10.6051 | 10.3214 | 9.5276 | 9.1561 | 8.8847 | 10.898 | 10.8133 | 10.7082 | 10.5571 | 10.5235 | 10.2816 | 9.9102 | 9.3194 | 8.9031 | 7.8051 | 7.2531 | 6.9755
|  | BRAMLEY GREEN PRIMARY | EE |  |  |  |  | 10.3449 | 10.252 | 10.0918 | 9.9327 | 9.9031 | 9.6245 | 9.299 | 8.6694 | 8.1204 | 6.4939 | 5.6755 | 5.1561 | 11.5898 | 11.5551 | 11.4857 | 11.4041 | 11.3388 | 11.2194 | 11.0694 | 10.7327 | 10.4357 | 9.5276 | 9.1561 | 8.8847 | 10.9 | 10.8143 | 10.7092 | 10.5867 | 10.5755 | 10.3592 | 10.1041 | 9.5653 | 9.1235 | 7.8541 | 7.3194 | 7.0265
|  | BRAMLEY GREEN PRIMARY | HT |  |  |  |  | 10.3439 | 10.2439 | 10.0949 | 9.9051 | 9.8378 | 9.5286 | 9.0357 | 8.3806 | 7.8582 | 6.4357 | 5.548 | 5.0031 | 11.5898 | 11.5551 | 11.4816 | 11.3857 | 11.3071 | 11.1745 | 10.9724 | 10.6051 | 10.3214 | 9.548 | 9.2898 | 9.2265 | 10.898 | 10.8184 | 10.7082 | 10.5571 | 10.5235 | 10.2816 | 9.9102 | 9.3194 | 8.9031 | 7.8051 | 7.2531 | 6.9755
|  | BRAMLEY GREEN PRIMARY | HE |  |  |  |  | 10.3449 | 10.2531 | 10.0918 | 9.9265 | 9.8878 | 9.5898 | 9.2439 | 8.7388 | 8.249 | 6.9265 | 6.1306 | 5.7704 | 11.5888 | 11.5541 | 11.4857 | 11.402 | 11.3347 | 11.2153 | 11.0612 | 10.8735 | 10.6735 | 9.9204 | 9.5031 | 9.1908 | 10.9 | 10.8133 | 10.7082 | 10.5806 | 10.5653 | 10.3388 | 10.0724 | 9.6929 | 9.3347 | 8.3327 | 7.7929 | 7.5776
|  | BRAMLEY GREEN PRIMARY | FB |  |  |  |  | 10.4837 | 10.4327 | 10.3673 | 10.3041 | 10.3031 | 10.2561 | 10.2092 | 10.2041 | 9.9939 | 8.9235 | 8.3112 | 8.0541 | 11.6561 | 11.6316 | 11.6031 | 11.5755 | 11.552 | 11.5082 | 11.4633 | 11.4357 | 11.2918 | 10.4806 | 9.6878 | 8.9459 | 11.0367 | 11.001 | 10.9388 | 10.9082 | 10.9031 | 10.8551 | 10.8061 | 10.8082 | 10.6449 | 9.7796 | 9.2235 | 9.0051
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD PRIMARY | MINIMUM HEADROOM | SZ 64712 98665 | NO | YES | 2.432 | 11.9655 | 12.1083 | 12.1981 | 12.1451 | 12.0726 | 11.7226 | 11.0696 | 10.3124 | 9.6471 | 5.5696 | 2.2461 | 0.19406 | 15.1757 | 15.1655 | 15.1236 | 15.0328 | 14.8543 | 14.4277 | 13.8655 | 13.2053 | 12.6277 | 9.0553 | 2.5859 | -6.357 | 13.2859 | 13.3665 | 13.2685 | 13.089 | 12.8134 | 12.3757 | 11.8022 | 11.1298 | 10.5522 | 7.0798 | 3.942 | 2.2134
|  | BRANDON ROAD PRIMARY | EE |  |  |  |  | 11.9655 | 12.1083 | 12.2012 | 12.1971 | 12.143 | 11.8277 | 11.2226 | 10.5185 | 9.9032 | 6.093 | 2.2461 | 0.19406 | 15.2012 | 15.2022 | 15.1736 | 15.0808 | 14.9369 | 14.5257 | 14.0063 | 13.3747 | 12.8277 | 9.0553 | 5.2849 | 1.4777 | 13.2859 | 13.3665 | 13.2685 | 13.1257 | 12.8859 | 12.4573 | 11.9267 | 11.2828 | 10.7441 | 7.2818 | 3.942 | 2.2134
|  | BRANDON ROAD PRIMARY | HT |  |  |  |  | 11.9767 | 12.1236 | 12.1981 | 12.1451 | 12.0726 | 11.7226 | 11.0696 | 10.3124 | 9.6471 | 5.5696 | 2.3492 | 0.98589 | 15.2002 | 15.1981 | 15.1522 | 15.0328 | 14.8543 | 14.4277 | 13.8655 | 13.2053 | 12.6277 | 10.1706 | 8.2757 | 7.193 | 13.3083 | 13.4012 | 13.2941 | 13.089 | 12.8134 | 12.3757 | 11.8022 | 11.1298 | 10.5522 | 7.0798 | 4.4624 | 3.4992
|  | BRANDON ROAD PRIMARY | HE |  |  |  |  | 11.993 | 12.1604 | 12.2798 | 12.2604 | 12.19 | 11.9492 | 11.4553 | 10.8941 | 10.342 | 7.8073 | 5.3879 | 3.8247 | 15.2094 | 15.2206 | 15.1981 | 15.1134 | 14.9604 | 14.593 | 14.0971 | 13.5379 | 12.9869 | 9.7247 | 6.3665 | 2.6808 | 13.3114 | 13.4185 | 13.34 | 13.1777 | 12.9134 | 12.5777 | 12.1196 | 11.6032 | 11.0981 | 8.8696 | 6.7777 | 5.4971
|  | BRANDON ROAD PRIMARY | FB |  |  |  |  | 12.0655 | 12.2685 | 12.44 | 12.6134 | 12.7318 | 12.7094 | 12.7124 | 12.6808 | 12.5339 | 11.4196 | 8.3604 | 5.7614 | 15.1757 | 15.1655 | 15.1236 | 15.0961 | 14.9624 | 14.5981 | 14.1461 | 13.6359 | 13.0492 | 9.2002 | 2.5859 | -6.357 | 13.4532 | 13.6257 | 13.7706 | 13.943 | 14.0328 | 13.7971 | 13.7349 | 13.591 | 13.3614 | 11.8818 | 8.9532 | 6.4726
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | BRAYWICK ROAD PRIMARY | MINIMUM HEADROOM | SU 88887 80726 | NO | NO | 6.338 | 9.3728 | 9.2534 | 9.085 | 8.4054 | 7.5391 | 6.3238 | 5.4452 | 4.5452 | 3.7687 | -2.5068 | -4.7976 | -5.817 | 9.1238 | 9.0565 | 8.9503 | 8.6432 | 8.235 | 7.6687 | 7.1126 | 6.4065 | 5.8626 | 1.1105 | -0.46701 | -3.6211 | 8.2116 | 8.0483 | 7.8534 | 7.3718 | 6.7085 | 5.8871 | 5.2942 | 4.5483 | 3.9687 | -1.3088 | -2.9293 | -3.4997
|  | BRAYWICK ROAD PRIMARY | EE |  |  |  |  | 9.3728 | 9.2534 | 9.0952 | 8.4279 | 7.5983 | 6.3585 | 5.5054 | 4.6218 | 3.8963 | -2.0303 | -4.3272 | -5.4191 | 9.1238 | 9.0575 | 8.9656 | 8.6595 | 8.2667 | 7.6779 | 7.1901 | 6.5697 | 6.1279 | 1.1524 | -0.39252 | -1.4742 | 8.2126 | 8.0514 | 7.8646 | 7.3861 | 6.7412 | 5.9003 | 5.3422 | 4.6565 | 4.1677 | -0.9364 | -2.6639 | -3.3507
|  | BRAYWICK ROAD PRIMARY | HT |  |  |  |  | 9.3748 | 9.2565 | 9.085 | 8.4422 | 7.6116 | 6.4646 | 5.5687 | 4.6014 | 3.7687 | -2.5068 | -4.7976 | -5.817 | 9.1238 | 9.0565 | 8.9503 | 8.6432 | 8.235 | 7.6687 | 7.1126 | 6.4065 | 5.8626 | 1.1105 | 0.11666 | -0.18334 | 8.2126 | 8.0514 | 7.8534 | 7.3789 | 6.7095 | 5.9299 | 5.3095 | 4.5483 | 3.9687 | -1.3088 | -2.9293 | -3.4997
|  | BRAYWICK ROAD PRIMARY | HE |  |  |  |  | 9.3758 | 9.2534 | 9.1024 | 8.4054 | 7.5391 | 6.3238 | 5.4452 | 4.5452 | 3.8228 | -1.4997 | -3.3558 | -4.1078 | 9.1248 | 9.0575 | 8.9626 | 8.6534 | 8.2626 | 7.6861 | 7.1687 | 6.5371 | 6.0983 | 1.4687 | 0.11156 | -0.98028 | 8.2116 | 8.0483 | 7.8646 | 7.3718 | 6.7085 | 5.8871 | 5.2942 | 4.5881 | 4.1034 | -0.45783 | -1.8139 | -2.2915
|  | BRAYWICK ROAD PRIMARY | FB |  |  |  |  | 9.5024 | 9.482 | 9.3993 | 9.0095 | 8.5136 | 7.934 | 7.6054 | 7.4044 | 7.1789 | 5.5636 | 0.97381 | -0.12211 | 9.2095 | 9.1922 | 9.1309 | 8.9207 | 8.6728 | 8.2707 | 7.9116 | 7.6279 | 7.3248 | 5.0728 | -0.46701 | -3.6211 | 8.3993 | 8.3187 | 8.1932 | 7.8758 | 7.5585 | 7.1565 | 6.8626 | 6.6493 | 6.4024 | 4.7697 | 1.0422 | 0.047276
EALING GSP | EALING BSP | BRENTFORD PRIMARY | MINIMUM HEADROOM | TQ 17659 78277 | NO | NO | 13.703 | 5.756 | 5.3009 | 4.8825 | 4.4121 | 3.4355 | 2.3458 | 0.94167 | -0.7267 | -2.1369 | -6.9328 | -10.4287 | -12.3042 | 10.0294 | 9.5458 | 9.1447 | 8.6958 | 7.6906 | 6.6509 | 5.2947 | 3.6876 | 2.3529 | -2.6879 | -9.1553 | -18.892 | 7.2253 | 6.7978 | 6.4121 | 5.956 | 4.9917 | 3.959 | 2.61 | 0.99269 | -0.33792 | -5.0614 | -8.3542 | -10.1216
|  | BRENTFORD PRIMARY | EE |  |  |  |  | 5.756 | 5.4682 | 4.9162 | 4.4121 | 3.806 | 2.9376 | 1.7906 | 0.3784 | -0.7318 | -6.9328 | -10.4287 | -12.3042 | 10.0294 | 9.7182 | 9.2192 | 8.7396 | 8.1182 | 7.2825 | 6.1284 | 4.7345 | 3.6223 | -2.6879 | -6.6532 | -10.7675 | 7.2253 | 6.9355 | 6.4202 | 5.956 | 5.3651 | 4.5366 | 3.4019 | 2.0111 | 0.92738 | -5.0614 | -8.3542 | -10.1216
|  | BRENTFORD PRIMARY | HT |  |  |  |  | 5.7896 | 5.3009 | 4.8825 | 4.4284 | 3.4355 | 2.3458 | 0.94167 | -0.7267 | -2.1369 | -6.742 | -9.2869 | -10.1879 | 10.0315 | 9.5458 | 9.1447 | 8.6958 | 7.6906 | 6.6509 | 5.2947 | 3.6876 | 2.3529 | -1.54 | -3.6196 | -4.7542 | 7.258 | 6.7978 | 6.4121 | 5.9855 | 4.9917 | 3.959 | 2.61 | 0.99269 | -0.33792 | -4.791 | -7.142 | -7.9185
|  | BRENTFORD PRIMARY | HE |  |  |  |  | 5.7733 | 5.4988 | 5.0141 | 4.5366 | 3.9009 | 3.0192 | 1.8743 | 0.49983 | -0.58996 | -5.3012 | -7.6206 | -8.9726 | 10.0304 | 9.7223 | 9.2539 | 8.8049 | 8.1804 | 7.3049 | 6.1366 | 4.7437 | 3.6141 | -2.0042 | -5.5226 | -9.3716 | 7.2417 | 6.9662 | 6.506 | 6.0641 | 5.4458 | 4.5998 | 3.4672 | 2.1049 | 1.0315 | -3.5767 | -5.7359 | -6.9594
|  | BRENTFORD PRIMARY | FB |  |  |  |  | 6.0049 | 5.8631 | 5.6478 | 5.2529 | 4.9866 | 4.6611 | 4.1539 | 3.458 | 2.9641 | -1.3104 | -4.6624 | -7.2594 | 10.0355 | 9.7264 | 9.3406 | 8.8304 | 8.3294 | 7.6947 | 6.8111 | 5.7662 | 4.8886 | -1.7716 | -9.1553 | -18.892 | 7.4733 | 7.3315 | 7.1264 | 6.7702 | 6.5151 | 6.2049 | 5.709 | 5.0111 | 4.5233 | 0.27942 | -3.0185 | -5.5604
EALING GSP |  | BRIDGE ROAD PRIMARY | MINIMUM HEADROOM | TQ 14778 75741 | NO | NO | 27.371 | 26.0488 | 25.6671 | 24.9743 | 100.2948 | 98.9724 | 97.053 | 94.5948 | 91.7602 | 89.102 | 80.9081 | 75.7459 | 72.7571 | 34.3528 | 34.0426 | 33.7947 | 109.6112 | 108.7489 | 107.7377 | 106.3081 | 104.5724 | 102.8244 | 96.4989 | 89.1928 | 77.105 | 28.4814 | 28.1028 | 27.5212 | 103.0214 | 101.8693 | 100.2622 | 98.1397 | 95.6214 | 93.3336 | 86.4091 | 81.6714 | 79.1744
|  | BRIDGE ROAD PRIMARY | EE |  |  |  |  | 26.0488 | 25.6671 | 24.9743 | 100.2948 | 99.1081 | 97.4653 | 95.3285 | 92.8571 | 90.5653 | 81.5561 | 75.7459 | 72.7571 | 34.3539 | 34.1926 | 33.7947 | 109.6112 | 109.0918 | 108.3244 | 107.2285 | 105.9173 | 104.4071 | 96.4989 | 91.1704 | 86.0948 | 28.4814 | 28.1028 | 27.5212 | 103.0214 | 102.051 | 100.6979 | 98.8806 | 96.7357 | 94.7969 | 86.6816 | 81.6714 | 79.1744
|  | BRIDGE ROAD PRIMARY | HT |  |  |  |  | 26.0957 | 25.6722 | 25.1365 | 100.4571 | 98.9724 | 97.053 | 94.5948 | 91.7602 | 89.102 | 80.9081 | 76.0632 | 74.1959 | 34.3528 | 34.0426 | 33.8008 | 109.6204 | 108.7489 | 107.7377 | 106.3081 | 104.5724 | 102.8244 | 97.501 | 94.5755 | 93.252 | 28.5314 | 28.111 | 27.6722 | 103.1622 | 101.8693 | 100.2622 | 98.1397 | 95.6214 | 93.3336 | 86.4091 | 82.4408 | 81.1755
|  | BRIDGE ROAD PRIMARY | HE |  |  |  |  | 26.0845 | 25.7314 | 25.0682 | 100.3755 | 99.1826 | 97.6061 | 95.5622 | 93.1428 | 90.9377 | 83.7999 | 80.1653 | 77.8102 | 34.3539 | 34.1967 | 33.7998 | 109.6173 | 109.0999 | 108.3265 | 107.2346 | 105.9061 | 104.5193 | 97.2061 | 92.8275 | 87.9877 | 28.5161 | 28.1661 | 27.6161 | 103.0959 | 102.1102 | 100.8102 | 99.0724 | 96.9653 | 95.0989 | 88.5989 | 85.5704 | 83.6755
|  | BRIDGE ROAD PRIMARY | FB |  |  |  |  | 26.3763 | 26.2824 | 26.0528 | 101.754 | 101.2836 | 100.6387 | 99.7785 | 98.7479 | 97.8255 | 92.2306 | 87.0428 | 83.1938 | 34.5273 | 34.4947 | 34.412 | 110.2755 | 110.0306 | 109.7224 | 109.1785 | 108.0704 | 106.9295 | 98.7683 | 89.1928 | 77.105 | 28.8569 | 28.813 | 28.6406 | 104.4183 | 104.001 | 103.4979 | 102.7683 | 101.8571 | 101.0704 | 95.655 | 90.7744 | 87.1744
LOVEDEAN GSP | HAVANT BSP | BROCKHAMPTON PRIMARY | MINIMUM HEADROOM | SU 70868 05828 | NO | YES | 5.213 | 13.6795 | 13.3438 | 12.8979 | 12.4418 | 11.8173 | 11.1469 | 10.6611 | 10.153 | 9.6785 | 8.3356 | 7.0479 | 6.6091 | 13.4887 | 13.1479 | 12.7489 | 12.3489 | 11.8948 | 11.5081 | 11.1999 | 10.8754 | 10.5805 | 10.053 | 9.1254 | 7.6224 | 14.3662 | 14.0367 | 13.6162 | 13.1734 | 12.6458 | 12.1234 | 11.7346 | 11.3305 | 10.9571 | 10.003 | 9.0234 | 8.7356
|  | BROCKHAMPTON PRIMARY | EE |  |  |  |  | 13.6795 | 13.655 | 13.2173 | 12.7724 | 12.1356 | 11.405 | 10.7877 | 10.2713 | 9.7907 | 8.4581 | 7.2703 | 6.7989 | 13.4887 | 13.4805 | 13.0867 | 12.6948 | 12.2418 | 11.8234 | 11.3989 | 11.0775 | 10.7867 | 10.053 | 9.1254 | 8.4601 | 14.3662 | 14.3611 | 13.9499 | 13.5224 | 12.9989 | 12.4367 | 11.9264 | 11.5213 | 11.1499 | 10.0928 | 9.1724 | 8.7601
|  | BROCKHAMPTON PRIMARY | HT |  |  |  |  | 13.6826 | 13.3438 | 12.8979 | 12.4418 | 11.8173 | 11.1469 | 10.6611 | 10.153 | 9.6785 | 8.3356 | 7.0479 | 6.6091 | 13.4897 | 13.1479 | 12.7489 | 12.3489 | 11.8948 | 11.5081 | 11.1999 | 10.8754 | 10.5805 | 10.055 | 9.5764 | 9.3938 | 14.3683 | 14.0367 | 13.6162 | 13.1734 | 12.6458 | 12.1234 | 11.7346 | 11.3305 | 10.9571 | 10.003 | 9.0234 | 8.7356
|  | BROCKHAMPTON PRIMARY | HE |  |  |  |  | 13.6836 | 13.6642 | 13.2285 | 12.7652 | 12.1091 | 11.3928 | 10.802 | 10.2969 | 9.8346 | 8.8254 | 7.8601 | 7.5336 | 13.4897 | 13.4805 | 13.0856 | 12.6928 | 12.2397 | 11.8203 | 11.403 | 11.0785 | 10.7948 | 10.1754 | 9.5264 | 8.9009 | 14.3693 | 14.3662 | 13.9601 | 13.5203 | 12.9867 | 12.4316 | 11.9346 | 11.5377 | 11.1764 | 10.3958 | 9.6693 | 9.4316
|  | BROCKHAMPTON PRIMARY | FB |  |  |  |  | 13.7407 | 13.7489 | 13.7418 | 13.3938 | 12.8928 | 12.4152 | 12.0397 | 11.656 | 11.4428 | 10.5611 | 9.5591 | 9.0693 | 13.5244 | 13.5234 | 13.5162 | 13.1713 | 12.7448 | 12.3264 | 11.9367 | 11.5611 | 11.3642 | 10.5132 | 9.2407 | 7.6224 | 14.4203 | 14.4346 | 14.4387 | 14.103 | 13.6316 | 13.202 | 12.8295 | 12.4571 | 12.2591 | 11.4805 | 10.7091 | 10.3448
LOVEDEAN GSP | FAREHAM (MAIN) BSP | BROCKHURST PRIMARY | MINIMUM HEADROOM | SU 59381 02061 | NO | YES | 4.112 | 8.6557 | 8.5037 | 8.2853 | 8.0843 | 7.7945 | 35.6424 | 35.0598 | 34.322 | 33.7486 | 31.1006 | 29.7373 | 28.8098 | 11.5282 | 11.3078 | 11.0496 | 10.8353 | 10.5292 | 36.8067 | 36.321 | 35.72 | 35.1894 | 32.6047 | 29.3067 | 24.4271 | 9.8108 | 9.6537 | 9.4169 | 9.2129 | 8.9149 | 36.0751 | 35.4965 | 34.7588 | 34.1843 | 31.4833 | 30.1486 | 29.3312
|  | BROCKHURST PRIMARY | EE |  |  |  |  | 8.6669 | 8.5282 | 8.3353 | 8.2169 | 7.9731 | 35.8914 | 35.3578 | 34.6496 | 34.1445 | 31.5659 | 29.7424 | 28.8098 | 11.5414 | 11.3343 | 11.0976 | 10.922 | 10.6241 | 36.9465 | 36.4976 | 35.9231 | 35.4322 | 32.6047 | 30.5149 | 28.5506 | 9.8159 | 9.6629 | 9.4424 | 9.3016 | 9.0271 | 36.2445 | 35.7333 | 35.0282 | 34.5118 | 31.8751 | 30.1557 | 29.3312
|  | BROCKHURST PRIMARY | HT |  |  |  |  | 8.6557 | 8.5037 | 8.2853 | 8.0843 | 7.7945 | 35.6424 | 35.0598 | 34.322 | 33.7486 | 31.1006 | 29.7373 | 29.3527 | 11.5282 | 11.3078 | 11.0496 | 10.8353 | 10.5292 | 36.8067 | 36.321 | 35.72 | 35.1894 | 32.9731 | 31.8935 | 31.4527 | 9.8108 | 9.6537 | 9.4169 | 9.2129 | 8.9149 | 36.0751 | 35.4965 | 34.7588 | 34.1843 | 31.4833 | 30.1486 | 29.822
|  | BROCKHURST PRIMARY | HE |  |  |  |  | 8.6761 | 8.5496 | 8.371 | 8.2333 | 7.9741 | 35.8935 | 35.3771 | 34.6731 | 34.1731 | 32.218 | 31.0302 | 30.4476 | 11.5384 | 11.3322 | 11.0955 | 10.918 | 10.6169 | 36.9394 | 36.4986 | 35.9292 | 35.4363 | 32.9629 | 31.1027 | 29.1914 | 9.8261 | 9.6863 | 9.4761 | 9.318 | 9.022 | 36.2445 | 35.7547 | 35.0567 | 34.5496 | 32.5506 | 31.3996 | 30.8476
|  | BROCKHURST PRIMARY | FB |  |  |  |  | 8.8282 | 8.772 | 8.7088 | 8.7394 | 8.6271 | 36.7741 | 36.6261 | 36.3169 | 36.1373 | 34.7037 | 32.6139 | 31.1812 | 11.5873 | 11.3924 | 11.2129 | 11.1016 | 10.8251 | 37.1455 | 36.8016 | 36.3363 | 35.9598 | 33.372 | 29.3067 | 24.4271 | 9.9863 | 9.8986 | 9.8118 | 9.769 | 9.6067 | 37.0231 | 36.8812 | 36.6424 | 36.472 | 34.92 | 32.7945 | 31.3139
MELKSHAM GSP | NORRINGTON BSP | BROMHAM PRIMARY | MINIMUM HEADROOM | ST 98670 65994 | YES | YES | 0.336 | 2.4791 | 5.642 | 5.6329 | 5.5482 | 5.4186 | 5.2135 | 5.0696 | 4.8359 | 4.5982 | 3.7594 | 3.0441 | 2.7308 | 2.8286 | 5.832 | 5.8096 | 5.6739 | 5.5116 | 5.3433 | 5.2514 | 5.079 | 4.9167 | 4.3667 | 3.98 | 3.7606 | 2.6408 | 5.6606 | 5.6412 | 5.4902 | 5.3014 | 5.1106 | 4.981 | 4.7678 | 4.5647 | 3.8545 | 3.3361 | 3.2269
|  | BROMHAM PRIMARY | EE |  |  |  |  | 2.4791 | 5.642 | 5.6359 | 5.59 | 5.4339 | 5.2676 | 5.1349 | 4.9237 | 4.6849 | 3.8716 | 3.1971 | 2.938 | 2.8286 | 5.832 | 5.8116 | 5.7678 | 5.5116 | 5.3882 | 5.2933 | 5.1229 | 4.9422 | 4.3667 | 3.98 | 3.8667 | 2.6408 | 5.6616 | 5.6443 | 5.5963 | 5.3116 | 5.1698 | 5.0433 | 4.8371 | 4.6178 | 3.93 | 3.432 | 3.3188
|  | BROMHAM PRIMARY | HT |  |  |  |  | 2.4801 | 5.642 | 5.6329 | 5.5941 | 5.4186 | 5.2135 | 5.0696 | 4.8359 | 4.5982 | 3.7594 | 3.0441 | 2.7308 | 2.8286 | 5.8331 | 5.8096 | 5.7627 | 5.5198 | 5.3433 | 5.2514 | 5.079 | 4.9167 | 4.3739 | 4.0586 | 4.0922 | 2.6408 | 5.6616 | 5.6412 | 5.5861 | 5.3116 | 5.1106 | 4.981 | 4.7678 | 4.5647 | 3.8545 | 3.3361 | 3.2269
|  | BROMHAM PRIMARY | HE |  |  |  |  | 2.4801 | 5.642 | 5.638 | 5.5482 | 5.4196 | 5.2431 | 5.1012 | 4.8727 | 4.6737 | 4.0227 | 3.4951 | 3.2186 | 2.8286 | 5.8341 | 5.8116 | 5.6739 | 5.5116 | 5.381 | 5.2861 | 5.1076 | 4.9759 | 4.4678 | 4.2545 | 4.079 | 2.6408 | 5.6606 | 5.6453 | 5.4902 | 5.3014 | 5.1535 | 5.0198 | 4.7984 | 4.6331 | 4.0729 | 3.7443 | 3.5902
|  | BROMHAM PRIMARY | FB |  |  |  |  | 2.5423 | 5.7339 | 5.7543 | 5.7492 | 5.7522 | 5.7196 | 5.7084 | 5.6767 | 5.639 | 5.1614 | 4.6012 | 4.3471 | 2.8735 | 5.9014 | 5.8933 | 5.8688 | 5.8576 | 5.8004 | 5.7504 | 5.6933 | 5.6341 | 4.9769 | 4.3229 | 3.7606 | 2.7 | 5.7402 | 5.7402 | 5.7229 | 5.7147 | 5.6984 | 5.6667 | 5.63 | 5.5922 | 5.0198 | 4.5188 | 4.2494
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | BROOK STREET PRIMARY | MINIMUM HEADROOM | SU 63480 52228 | NO | NO | 2.843 | 15.3242 | 15.365 | 15.3905 | 15.3874 | 15.3405 | 15.2762 | 15.1099 | 14.8732 | 14.6344 | 13.468 | 12.7793 | 12.4058 | 16.466 | 16.4497 | 16.416 | 16.3936 | 16.3446 | 16.2129 | 16.0538 | 15.8895 | 15.5691 | 14.1068 | 11.8262 | 8.714 | 15.7487 | 15.7548 | 15.7405 | 15.6976 | 15.568 | 15.3691 | 15.1813 | 14.8711 | 14.514 | 13.2844 | 12.6538 | 12.367
|  | BROOK STREET PRIMARY | EE |  |  |  |  | 15.3242 | 15.365 | 15.3905 | 15.4048 | 15.3711 | 15.3038 | 15.2415 | 15.0201 | 14.7578 | 13.6354 | 12.9405 | 12.6017 | 16.466 | 16.4578 | 16.4415 | 16.4252 | 16.3701 | 16.3038 | 16.2497 | 15.9527 | 15.6068 | 14.1068 | 12.9742 | 11.7374 | 15.7487 | 15.7548 | 15.7405 | 15.7089 | 15.5803 | 15.3691 | 15.2466 | 14.9293 | 14.565 | 13.2844 | 12.6538 | 12.367
|  | BROOK STREET PRIMARY | HT |  |  |  |  | 15.3293 | 15.3691 | 15.3915 | 15.3874 | 15.3405 | 15.2762 | 15.1099 | 14.8732 | 14.6344 | 13.468 | 12.7793 | 12.4058 | 16.468 | 16.4599 | 16.4415 | 16.415 | 16.3517 | 16.2946 | 16.1895 | 15.916 | 15.5783 | 14.568 | 14.0568 | 13.7854 | 15.7558 | 15.764 | 15.7497 | 15.6976 | 15.568 | 15.3762 | 15.1813 | 14.8711 | 14.514 | 13.3487 | 12.8885 | 12.8374
|  | BROOK STREET PRIMARY | HE |  |  |  |  | 15.3334 | 15.3803 | 15.4109 | 15.4313 | 15.3976 | 15.3415 | 15.2487 | 15.0283 | 14.764 | 13.7374 | 13.1803 | 12.9405 | 16.4691 | 16.4629 | 16.4497 | 16.4344 | 16.3783 | 16.3119 | 16.2436 | 15.9609 | 15.5691 | 14.2701 | 13.1558 | 12.1221 | 15.7599 | 15.7752 | 15.7691 | 15.7313 | 15.5936 | 15.4048 | 15.2752 | 14.9803 | 14.5793 | 13.6283 | 13.1578 | 13.164
|  | BROOK STREET PRIMARY | FB |  |  |  |  | 15.3783 | 15.4364 | 15.4793 | 15.5252 | 15.568 | 15.5813 | 15.5803 | 15.5742 | 15.4864 | 14.8446 | 14.2629 | 13.6599 | 16.4691 | 16.4497 | 16.416 | 16.3936 | 16.3446 | 16.2129 | 16.0538 | 15.8895 | 15.6711 | 14.168 | 11.8262 | 8.714 | 15.8385 | 15.8629 | 15.8783 | 15.9119 | 15.9129 | 15.9027 | 15.8772 | 15.8007 | 15.6415 | 14.7334 | 13.8354 | 13.118
MELKSHAM GSP | FROME BSP | BRUTON PRIMARY | MINIMUM HEADROOM | ST 69094 35148 | NO | NO | 1.13 | 2.1763 | 2.1886 | 2.1947 | 2.1059 | 1.8671 | 1.5692 | 1.3059 | 1.0039 | 0.76102 | -0.12878 | -0.86551 | -1.3033 | 2.6741 | 2.6557 | 2.6394 | 2.5078 | 2.2669 | 2.0588 | 1.9108 | 1.668 | 1.4904 | 0.80265 | 0.36592 | -0.16673 | 2.1008 | 2.0998 | 2.0967 | 1.9427 | 1.6651 | 1.3763 | 1.1518 | 0.87224 | 0.65082 | -0.17469 | -0.70429 | -0.97571
|  | BRUTON PRIMARY | EE |  |  |  |  | 2.1763 | 2.1886 | 2.1947 | 2.1692 | 1.9978 | 1.7039 | 1.3814 | 1.0335 | 0.80898 | -0.12878 | -0.86551 | -1.3033 | 2.6741 | 2.6557 | 2.6394 | 2.6016 | 2.3435 | 2.1659 | 1.9455 | 1.721 | 1.5424 | 0.80265 | 0.36592 | 0.081224 | 2.1008 | 2.0998 | 2.0967 | 2.0498 | 1.7692 | 1.5284 | 1.2182 | 0.91 | 0.67735 | -0.17469 | -0.70429 | -0.97571
|  | BRUTON PRIMARY | HT |  |  |  |  | 2.1794 | 2.1906 | 2.1978 | 2.1784 | 1.8671 | 1.5692 | 1.3059 | 1.059 | 0.85082 | -0.010408 | -0.73592 | -1.2176 | 2.6771 | 2.6588 | 2.6394 | 2.6037 | 2.2669 | 2.0588 | 1.9108 | 1.668 | 1.4904 | 0.87714 | 0.59755 | 0.50776 | 2.1018 | 2.1018 | 2.0978 | 2.0549 | 1.6651 | 1.3763 | 1.1518 | 0.87224 | 0.65082 | -0.11041 | -0.59918 | -0.86551
|  | BRUTON PRIMARY | HE |  |  |  |  | 2.1784 | 2.1906 | 2.1957 | 2.1059 | 1.9773 | 1.6753 | 1.3447 | 1.0039 | 0.76102 | 0.08449 | -0.48796 | -0.81551 | 2.6761 | 2.6588 | 2.6404 | 2.5078 | 2.3394 | 2.1557 | 1.9343 | 1.7394 | 1.5333 | 0.93327 | 0.63633 | 0.39143 | 2.1029 | 2.1018 | 2.0967 | 1.9427 | 1.7733 | 1.5059 | 1.1906 | 0.9049 | 0.65082 | 0.0038776 | -0.36755 | -0.55735
|  | BRUTON PRIMARY | FB |  |  |  |  | 2.2447 | 2.2865 | 2.3182 | 2.3233 | 2.3345 | 2.3345 | 2.1773 | 2.0263 | 1.8651 | 1.2835 | 0.78857 | 0.39571 | 2.7271 | 2.7282 | 2.72 | 2.6996 | 2.6812 | 2.6404 | 2.5088 | 2.3873 | 2.2527 | 1.3802 | 0.6302 | -0.16673 | 2.1692 | 2.2008 | 2.2192 | 2.2161 | 2.2222 | 2.2069 | 2.0753 | 1.9376 | 1.7967 | 0.99469 | 0.47735 | 0.098776
COWLEY GSP | WITNEY BSP | BURFORD PRIMARY | MINIMUM HEADROOM | SP 25671 12529 | NO | NO | 0.981 | 6.2931 | 6.3012 | 6.3094 | 6.2798 | 6.2502 | 6.1676 | 6.0624 | 5.9461 | 5.8676 | 5.64 | 5.3451 | 5.0686 | 7.0515 | 7.0403 | 7.024 | 7.0036 | 6.9607 | 6.9107 | 6.8434 | 6.7628 | 6.774 | 6.525 | 6.1587 | 5.623 | 6.5859 | 6.589 | 6.5859 | 6.5645 | 6.5216 | 6.4716 | 6.3869 | 6.2961 | 6.2961 | 6.1033 | 5.8931 | 5.7645
|  | BURFORD PRIMARY | EE |  |  |  |  | 6.2931 | 6.3012 | 6.3094 | 6.3043 | 6.2604 | 6.1992 | 6.1022 | 6.0002 | 5.9308 | 5.64 | 5.3584 | 5.1737 | 7.0515 | 7.0413 | 7.0291 | 7.0148 | 6.975 | 6.926 | 6.8577 | 6.7801 | 6.7923 | 6.525 | 6.3148 | 6.1485 | 6.5859 | 6.589 | 6.589 | 6.5737 | 6.5349 | 6.49 | 6.4114 | 6.3257 | 6.3278 | 6.1033 | 5.9043 | 5.8053
|  | BURFORD PRIMARY | HT |  |  |  |  | 6.3022 | 6.3145 | 6.3104 | 6.2798 | 6.2522 | 6.1982 | 6.1196 | 6.0308 | 5.9686 | 5.692 | 5.3451 | 5.0686 | 7.0536 | 7.0403 | 7.024 | 7.0036 | 6.9607 | 6.9107 | 6.8434 | 6.7628 | 6.774 | 6.5658 | 6.4444 | 6.4179 | 6.592 | 6.5971 | 6.5859 | 6.5645 | 6.5216 | 6.4798 | 6.4043 | 6.3186 | 6.3257 | 6.1063 | 5.8931 | 5.7645
|  | BURFORD PRIMARY | HE |  |  |  |  | 6.2951 | 6.3012 | 6.3104 | 6.292 | 6.2502 | 6.1676 | 6.0624 | 5.9461 | 5.8676 | 5.6839 | 5.3839 | 5.2124 | 7.0526 | 7.0403 | 7.0291 | 7.0128 | 6.974 | 6.923 | 6.8505 | 6.7719 | 6.7883 | 6.5281 | 6.2985 | 6.1117 | 6.5869 | 6.59 | 6.589 | 6.5676 | 6.5216 | 6.4716 | 6.3869 | 6.2961 | 6.2961 | 6.1216 | 5.8992 | 5.7767
|  | BURFORD PRIMARY | FB |  |  |  |  | 6.3278 | 6.3594 | 6.388 | 6.3941 | 6.3941 | 6.3849 | 6.391 | 6.3839 | 6.3727 | 6.2349 | 5.9992 | 5.8604 | 7.075 | 7.0791 | 7.0801 | 7.0709 | 7.0526 | 7.0128 | 6.9821 | 6.9352 | 6.8923 | 6.6403 | 6.1587 | 5.623 | 6.6359 | 6.6584 | 6.6869 | 6.689 | 6.6859 | 6.6727 | 6.6665 | 6.64 | 6.6237 | 6.5165 | 6.2716 | 6.1573
MANNINGTON GSP | WAREHAM BSP | BUSHEY PRIMARY | MINIMUM HEADROOM | SY 97671 83532 | YES | YES | 0.074 | 4.0444 | 4.0383 | 4.0393 | 3.9985 | 3.9005 | 3.8107 | 3.6852 | 3.5495 | 3.4526 | 3.074 | 2.8301 | 2.723 | 3.6378 | 3.6224 | 3.6194 | 3.5949 | 3.4786 | 3.4082 | 3.2796 | 3.2214 | 3.1031 | 2.8327 | 2.6929 | 2.6561 | 4.0163 | 4.0071 | 4.0071 | 3.9755 | 3.8469 | 3.7571 | 3.6061 | 3.5276 | 3.399 | 3.0755 | 2.9143 | 2.9163
|  | BUSHEY PRIMARY | EE |  |  |  |  | 4.0444 | 4.0485 | 4.0393 | 4.0066 | 3.9821 | 3.9423 | 3.7587 | 3.5852 | 3.4995 | 3.074 | 2.8301 | 2.723 | 3.6388 | 3.6316 | 3.6194 | 3.5949 | 3.5806 | 3.5541 | 3.3969 | 3.2429 | 3.1847 | 2.8327 | 2.6929 | 2.6561 | 4.0163 | 4.0153 | 4.0071 | 3.9786 | 3.9469 | 3.898 | 3.7102 | 3.548 | 3.4622 | 3.0786 | 2.9143 | 2.9163
|  | BUSHEY PRIMARY | HT |  |  |  |  | 4.0454 | 4.0403 | 4.0434 | 4.0148 | 3.9005 | 3.8107 | 3.6852 | 3.6148 | 3.4832 | 3.1342 | 2.9107 | 2.8148 | 3.6378 | 3.6224 | 3.6204 | 3.598 | 3.4786 | 3.4082 | 3.2796 | 3.2214 | 3.1031 | 2.8337 | 2.7561 | 2.8 | 4.0173 | 4.0092 | 4.0082 | 3.9847 | 3.8469 | 3.7571 | 3.6061 | 3.5337 | 3.399 | 3.0755 | 2.9612 | 3
|  | BUSHEY PRIMARY | HE |  |  |  |  | 4.0444 | 4.0383 | 4.0393 | 3.9985 | 3.9719 | 3.9281 | 3.7372 | 3.5495 | 3.4526 | 3.2168 | 3.0454 | 2.9546 | 3.6388 | 3.6235 | 3.6194 | 3.5949 | 3.5786 | 3.5531 | 3.3878 | 3.2245 | 3.1602 | 2.9612 | 2.8959 | 2.8531 | 4.0163 | 4.0071 | 4.0082 | 3.9755 | 3.9439 | 3.8949 | 3.7092 | 3.5276 | 3.4367 | 3.2 | 3.1082 | 3.0918
|  | BUSHEY PRIMARY | FB |  |  |  |  | 4.076 | 4.0903 | 4.0944 | 4.0985 | 4.0974 | 4.0781 | 4.0668 | 4.0423 | 4.0168 | 3.8934 | 3.7403 | 3.4158 | 3.6643 | 3.6653 | 3.6592 | 3.6602 | 3.6541 | 3.6306 | 3.6143 | 3.5888 | 3.5582 | 3.4153 | 3.2449 | 2.8571 | 4.0469 | 4.0551 | 4.0582 | 4.0633 | 4.0622 | 4.0398 | 4.0245 | 3.9888 | 3.95 | 3.7765 | 3.6224 | 3.3031
FAWLEY GSP | LANGLEY BSP | BUTTS ASH PRIMARY | MINIMUM HEADROOM | SU 41923 05772 | NO | NO | 1.371 | 9.3247 | 9.3645 | 9.0747 | 8.5094 | 7.7553 | 6.49 | 5.1329 | 3.6737 | 2.192 | -2.5069 | -5.9212 | -7.2835 | 12.8431 | 12.8604 | 12.6012 | 12.2951 | 11.8604 | 11.2482 | 10.5094 | 9.7186 | 8.9257 | 6.4002 | 4.2553 | -0.10286 | 10.4196 | 10.4267 | 10.0441 | 9.5257 | 8.789 | 7.7982 | 6.6961 | 5.5839 | 4.4573 | 0.72878 | -1.7569 | -2.4743
|  | BUTTS ASH PRIMARY | EE |  |  |  |  | 9.3533 | 9.492 | 9.339 | 9.0176 | 8.5727 | 7.5492 | 6.4298 | 5.1716 | 3.9451 | -0.2151 | -3.4896 | -4.912 | 12.8624 | 12.9237 | 12.7176 | 12.492 | 12.1543 | 11.6727 | 11.04 | 10.3114 | 9.6227 | 6.6012 | 4.3594 | 2.8829 | 10.4492 | 10.4941 | 10.2084 | 9.8471 | 9.3094 | 8.491 | 7.5563 | 6.542 | 5.5808 | 2.0757 | -0.45592 | -1.2835
|  | BUTTS ASH PRIMARY | HT |  |  |  |  | 9.3247 | 9.3645 | 9.0747 | 8.5094 | 7.7553 | 6.49 | 5.1329 | 3.6737 | 2.192 | -2.5069 | -5.9212 | -7.2835 | 12.8431 | 12.8604 | 12.6012 | 12.2951 | 11.8604 | 11.2482 | 10.5094 | 9.7186 | 8.9257 | 6.4002 | 5.0237 | 4.742 | 10.4196 | 10.4267 | 10.0441 | 9.5257 | 8.789 | 7.7982 | 6.6961 | 5.5839 | 4.4573 | 0.72878 | -1.7569 | -2.4743
|  | BUTTS ASH PRIMARY | HE |  |  |  |  | 9.3624 | 9.5053 | 9.3584 | 9.0033 | 8.5492 | 7.6349 | 6.6308 | 5.5073 | 4.4063 | 0.79204 | -1.9682 | -3.0784 | 12.8645 | 12.9237 | 12.7176 | 12.49 | 12.1706 | 11.6706 | 11.0359 | 10.3461 | 9.6767 | 6.8635 | 4.7982 | 3.1788 | 10.4563 | 10.5053 | 10.2257 | 9.8461 | 9.3176 | 8.5196 | 7.6359 | 6.7206 | 5.8247 | 2.7839 | 0.75327 | 0.060408
|  | BUTTS ASH PRIMARY | FB |  |  |  |  | 9.6451 | 9.8216 | 10.0349 | 10.0818 | 10.0869 | 9.8716 | 9.69 | 9.4818 | 9.2686 | 7.4104 | 4.4308 | 2.7645 | 13.0176 | 13.0216 | 13.0655 | 12.9941 | 12.8594 | 12.439 | 12.0716 | 11.6869 | 11.2971 | 8.4624 | 4.2553 | -0.10286 | 10.7257 | 10.8043 | 10.9257 | 10.9227 | 10.8716 | 10.5094 | 10.2502 | 9.9798 | 9.7084 | 7.6053 | 4.8165 | 3.2165
MELKSHAM GSP | CHIPPENHAM BSP | CALNE PRIMARY | MINIMUM HEADROOM | SU 00521 72497 | NO | YES | 4.034 | 3.2943 | 3.4422 | 2.8616 | 2.1137 | 1.3076 | 0.1351 | -1.1751 | -2.5812 | -3.8812 | -8.4282 | -12.2853 | -14.8598 | 7.5065 | 7.5606 | 7.0882 | 6.6963 | 6.2331 | 5.632 | 4.9188 | 4.1137 | 3.3106 | 0.74939 | -1.2078 | -4.5557 | 5.5504 | 5.6596 | 5.1596 | 4.5708 | 3.88 | 2.9647 | 1.9218 | 0.77694 | -0.33429 | -4.0333 | -6.6476 | -8.1384
|  | CALNE PRIMARY | EE |  |  |  |  | 3.2943 | 3.4422 | 2.8892 | 2.228 | 1.5014 | 0.46571 | -0.69959 | -1.9108 | -2.9751 | -7.1322 | -10.8139 | -13.0414 | 7.5065 | 7.5606 | 7.0994 | 6.7402 | 6.3076 | 5.7616 | 5.0984 | 4.3708 | 3.6657 | 0.79531 | -1.2078 | -2.5822 | 5.5504 | 5.6596 | 5.178 | 4.6494 | 4.0178 | 3.1943 | 2.2422 | 1.2239 | 0.27388 | -3.2384 | -5.8659 | -7.1914
|  | CALNE PRIMARY | HT |  |  |  |  | 3.2943 | 3.4453 | 2.8616 | 2.1137 | 1.3076 | 0.1351 | -1.1751 | -2.5812 | -3.8812 | -8.4282 | -12.2853 | -14.8598 | 7.5065 | 7.5627 | 7.0882 | 6.6963 | 6.2331 | 5.632 | 4.9188 | 4.1137 | 3.3106 | 0.74939 | -0.66082 | -1.2435 | 5.5524 | 5.6616 | 5.1596 | 4.5708 | 3.88 | 2.9647 | 1.9218 | 0.77694 | -0.33429 | -4.0333 | -6.6476 | -8.1384
|  | CALNE PRIMARY | HE |  |  |  |  | 3.2943 | 3.4433 | 2.8892 | 2.2198 | 1.4851 | 0.42898 | -0.70878 | -1.9098 | -2.9812 | -6.3476 | -9.868 | -11.7445 | 7.5096 | 7.5606 | 7.0994 | 6.7392 | 6.3004 | 5.7361 | 5.1045 | 4.3861 | 3.6769 | 1.2269 | -0.7802 | -2.2924 | 5.5524 | 5.6596 | 5.178 | 4.6433 | 4.0065 | 3.1565 | 2.2412 | 1.2371 | 0.28408 | -2.5231 | -5.0537 | -6.2751
|  | CALNE PRIMARY | FB |  |  |  |  | 3.5371 | 3.6667 | 3.4984 | 3.2606 | 2.8412 | 2.5443 | 2.1963 | 1.8229 | 1.5688 | -0.42 | -3.318 | -5.1986 | 7.6484 | 7.6382 | 7.4882 | 7.3963 | 6.9647 | 6.6412 | 6.2841 | 5.8882 | 5.4994 | 2.8841 | -0.7751 | -4.5557 | 5.7504 | 5.8422 | 5.7494 | 5.6208 | 5.2831 | 5.0035 | 4.68 | 4.3351 | 4.0473 | 1.9922 | -0.7098 | -2.5149
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY PRIMARY | MINIMUM HEADROOM | SU 86584 59452 | NO | NO | 11.475 | 47.673 | 47.5516 | 47.2343 | 46.8404 | 46.3353 | 45.5516 | 44.6679 | 43.5037 | 42.62 | 38.97 | 36.3986 | 35.7669 | 46.7771 | 46.5037 | 46.1241 | 45.7679 | 45.2424 | 44.5741 | 43.7332 | 42.6598 | 41.8822 | 38.421 | 35.3669 | 29.6884 | 47.1455 | 46.9128 | 46.5649 | 46.2394 | 45.722 | 44.9986 | 44.1292 | 43.0557 | 42.2608 | 38.87 | 36.5343 | 35.9169
|  | CAMBERLEY PRIMARY | EE |  |  |  |  | 47.673 | 47.5516 | 47.2608 | 47.0016 | 46.6465 | 45.9986 | 45.1741 | 44.0843 | 43.2914 | 39.7486 | 37.069 | 35.8751 | 46.7792 | 46.5098 | 46.1465 | 45.8414 | 45.37 | 44.7761 | 43.9822 | 42.9649 | 42.2557 | 38.421 | 35.5118 | 33.4016 | 47.1455 | 46.9128 | 46.5781 | 46.3455 | 45.9271 | 45.3037 | 44.4924 | 43.4781 | 42.7598 | 39.4475 | 36.9751 | 35.9169
|  | CAMBERLEY PRIMARY | HT |  |  |  |  | 47.6781 | 47.5567 | 47.2343 | 46.8404 | 46.3353 | 45.5516 | 44.6679 | 43.5037 | 42.62 | 38.97 | 36.3986 | 35.7669 | 46.7792 | 46.5088 | 46.1241 | 45.7679 | 45.2424 | 44.5741 | 43.7332 | 42.6598 | 41.8822 | 38.6506 | 36.6598 | 36.2435 | 47.1516 | 46.9261 | 46.5649 | 46.2394 | 45.722 | 44.9986 | 44.1292 | 43.0557 | 42.2608 | 38.87 | 36.5343 | 36.1098
|  | CAMBERLEY PRIMARY | HE |  |  |  |  | 47.6792 | 47.5608 | 47.2771 | 47.0588 | 46.62 | 45.9996 | 45.1904 | 44.3445 | 43.3659 | 40.3822 | 38.6904 | 37.8873 | 46.7771 | 46.5037 | 46.1384 | 45.921 | 45.3659 | 44.7649 | 43.9547 | 43.1751 | 42.2271 | 38.7506 | 36.6884 | 34.7149 | 47.1465 | 46.9169 | 46.5884 | 46.3679 | 45.9108 | 45.2945 | 44.4935 | 43.7118 | 42.7955 | 39.9863 | 38.5404 | 37.8669
|  | CAMBERLEY PRIMARY | FB |  |  |  |  | 47.8975 | 47.773 | 47.6914 | 47.7128 | 47.6741 | 47.5955 | 47.3965 | 47.1057 | 46.921 | 44.8302 | 41.9384 | 39.9649 | 46.8863 | 46.6281 | 46.3873 | 46.2445 | 45.8904 | 45.5261 | 45.0414 | 44.4669 | 44.02 | 40.4037 | 35.3669 | 29.6884 | 47.3026 | 47.1241 | 46.9445 | 46.8965 | 46.7955 | 46.6853 | 46.5353 | 46.2639 | 46.0516 | 43.8557 | 41.0802 | 39.1373
WILLESDEN GSP |  | CANAL BANK 11KV PRIMARY | MINIMUM HEADROOM | TQ 20927 83082 | NO | YES | 22.81 | 15.6865 | 15.4825 | 15.2325 | 14.9263 | 10.6284 | 6.0896 | 1.1631 | -3.7512 | -7.238 | -12.7614 | -14.0849 | -14.4624 | 10.2855 | 10.1845 | 10.0845 | 9.9396 | 4.7753 | 0.56205 | -4.0798 | -8.7971 | -12.3318 | -18.2318 | -19.9471 | -20.4298 | 15.8549 | 15.7171 | 15.5651 | 15.3702 | 10.6784 | 6.2814 | 1.4355 | -3.488 | -7.0686 | -13.4216 | -15.1155 | -15.5992
|  | CANAL BANK 11KV PRIMARY | EE |  |  |  |  | 15.6865 | 15.5325 | 15.2855 | 14.9774 | 14.762 | 12.0457 | 8.0733 | 2.7661 | -1.7941 | -12.7614 | -14.0849 | -14.4624 | 10.2865 | 10.2192 | 10.1192 | 9.9753 | 9.8845 | 6.6437 | 1.81 | -3.2216 | -7.342 | -18.2318 | -19.9471 | -20.4298 | 15.8549 | 15.7549 | 15.6018 | 15.409 | 15.2743 | 12.3355 | 7.8437 | 2.6059 | -1.8829 | -13.4216 | -15.1155 | -15.5992
|  | CANAL BANK 11KV PRIMARY | HT |  |  |  |  | 15.6876 | 15.4825 | 15.2325 | 14.9263 | 10.6284 | 6.0896 | 1.1631 | -3.7512 | -7.238 | -10.7053 | -11.6737 | -11.9624 | 10.2855 | 10.1845 | 10.0845 | 9.9396 | 4.7753 | 0.56205 | -4.0798 | -8.7971 | -12.3318 | -15.842 | -16.939 | -17.2247 | 15.8549 | 15.7171 | 15.5651 | 15.3702 | 10.6784 | 6.2814 | 1.4355 | -3.488 | -7.0686 | -10.8359 | -11.992 | -12.3257
|  | CANAL BANK 11KV PRIMARY | HE |  |  |  |  | 15.6998 | 15.562 | 15.3263 | 15.0345 | 14.7631 | 11.9059 | 8.361 | 3.7998 | -0.018565 | -9.2257 | -9.6196 | -9.6839 | 10.2927 | 10.2304 | 10.1416 | 10.0141 | 9.911 | 6.5182 | 2.3049 | -2.1043 | -5.6165 | -13.8533 | -14.2543 | -14.3533 | 15.8661 | 15.7753 | 15.6335 | 15.4539 | 15.2896 | 12.209 | 8.3243 | 3.859 | 0.13246 | -9.089 | -9.5645 | -9.6665
|  | CANAL BANK 11KV PRIMARY | FB |  |  |  |  | 15.7171 | 15.6039 | 15.4723 | 15.259 | 15.0386 | 14.96 | 12.4223 | 9.962 | 7.0692 | -7.0063 | -8.0308 | -8.1329 | 10.2978 | 10.2396 | 10.1774 | 10.0927 | 10.01 | 9.9804 | 6.8559 | 3.8845 | 1.3345 | -12.0686 | -12.8594 | -12.9502 | 15.8784 | 15.7988 | 15.7131 | 15.5886 | 15.4641 | 15.4233 | 12.6314 | 9.9223 | 7.1784 | -6.8992 | -7.8645 | -7.9614
COWLEY GSP | WITNEY BSP | CARTERTON PRIMARY | MINIMUM HEADROOM | SP 28261 07823 | NO | NO | 2.163 | 13.6041 | 13.1541 | 12.652 | 12.1316 | 11.698 | 10.9837 | 10.2367 | 9.3969 | 8.5765 | 5.2949 | 2.4082 | 0.52857 | 18.4541 | 18.2694 | 17.8898 | 17.6102 | 17.302 | 16.9071 | 16.4286 | 15.8878 | 15.3571 | 13.4092 | 11.949 | 8.7214 | 15.5857 | 15.3163 | 14.8061 | 14.3796 | 13.9735 | 13.3847 | 12.7245 | 11.9827 | 11.2551 | 8.6 | 6.6867 | 5.5888
|  | CARTERTON PRIMARY | EE |  |  |  |  | 13.6041 | 13.1541 | 12.7398 | 12.3918 | 12.0286 | 11.3112 | 10.4867 | 9.6265 | 8.8357 | 6.0592 | 3.5153 | 1.8551 | 18.5367 | 18.3918 | 18.1031 | 17.8867 | 17.6347 | 17.2776 | 16.798 | 16.2398 | 15.7827 | 13.5327 | 11.95 | 10.6112 | 15.6173 | 15.3469 | 14.9337 | 14.6286 | 14.2929 | 13.7265 | 13.0194 | 12.2388 | 11.5724 | 9.151 | 7.3469 | 6.25
|  | CARTERTON PRIMARY | HT |  |  |  |  | 13.6092 | 13.1939 | 12.652 | 12.1316 | 11.698 | 10.9837 | 10.2367 | 9.3969 | 8.5765 | 5.2949 | 2.4082 | 0.52857 | 18.4541 | 18.2694 | 17.8898 | 17.6102 | 17.302 | 16.9071 | 16.4286 | 15.8878 | 15.3571 | 13.4092 | 12.3296 | 11.8214 | 15.5857 | 15.3163 | 14.8061 | 14.3796 | 13.9735 | 13.3847 | 12.7245 | 11.9827 | 11.2551 | 8.6 | 6.6867 | 5.5888
|  | CARTERTON PRIMARY | HE |  |  |  |  | 13.6061 | 13.1571 | 12.7316 | 12.3694 | 11.9949 | 11.252 | 10.4112 | 9.548 | 8.7337 | 6.6153 | 4.248 | 2.9449 | 18.5367 | 18.3929 | 18.102 | 17.8796 | 17.6265 | 17.2684 | 16.7827 | 16.249 | 15.7888 | 13.8276 | 12.2582 | 10.9031 | 15.6184 | 15.349 | 14.9276 | 14.6153 | 14.2704 | 13.6867 | 12.9704 | 12.2092 | 11.5337 | 9.6041 | 7.899 | 7.0102
|  | CARTERTON PRIMARY | FB |  |  |  |  | 13.998 | 13.7755 | 13.6306 | 13.6337 | 13.5949 | 13.4122 | 13.2918 | 13.1347 | 12.9531 | 11.6745 | 9.701 | 8.4878 | 18.6837 | 18.5245 | 18.4102 | 18.3969 | 18.2755 | 17.9306 | 17.6816 | 17.4092 | 17.0857 | 15.0061 | 11.949 | 8.7214 | 15.9449 | 15.7949 | 15.698 | 15.7378 | 15.7071 | 15.4316 | 15.3 | 15.1051 | 14.8765 | 13.4286 | 11.4735 | 10.3235
AXMINSTER GSP | YEOVIL BSP | CASTLE CARY PRIMARY | MINIMUM HEADROOM | ST 64534 31039 | NO | NO | 2.488 | 7.8796 | 7.6296 | 7.197 | 6.7439 | 6.4235 | 6.046 | 5.6909 | 5.3072 | 4.9398 | 3.6398 | 2.6654 | 2.096 | 8.7699 | 8.6536 | 8.4965 | 8.1699 | 7.9424 | 7.7516 | 7.5128 | 7.2567 | 7.0679 | 6.2679 | 5.7761 | 5.0904 | 8.1077 | 7.9199 | 7.6393 | 7.2526 | 6.9965 | 6.7087 | 6.3944 | 6.0393 | 5.7577 | 4.6506 | 3.9271 | 3.5699
|  | CASTLE CARY PRIMARY | EE |  |  |  |  | 7.8796 | 7.8837 | 7.4531 | 6.8827 | 6.4235 | 6.046 | 5.7368 | 5.3327 | 4.947 | 3.6398 | 2.6654 | 2.096 | 8.7699 | 8.7679 | 8.6077 | 8.2526 | 7.9873 | 7.8138 | 7.6046 | 7.3352 | 7.1128 | 6.2679 | 5.7761 | 5.3689 | 8.1077 | 8.1026 | 7.8118 | 7.3546 | 6.9965 | 6.7087 | 6.4301 | 6.071 | 5.7577 | 4.6506 | 3.9271 | 3.5699
|  | CASTLE CARY PRIMARY | HT |  |  |  |  | 7.8807 | 7.6296 | 7.197 | 6.7439 | 6.4766 | 6.1419 | 5.7541 | 5.3409 | 5.0817 | 3.947 | 2.9409 | 2.3041 | 8.7699 | 8.6536 | 8.4965 | 8.1699 | 7.9424 | 7.7516 | 7.5128 | 7.2567 | 7.0679 | 6.3067 | 5.9393 | 5.8873 | 8.1077 | 7.9199 | 7.6393 | 7.2526 | 7.0057 | 6.7261 | 6.3944 | 6.0393 | 5.8087 | 4.8332 | 4.124 | 3.7608
|  | CASTLE CARY PRIMARY | HE |  |  |  |  | 7.8796 | 7.8837 | 7.5929 | 7.1562 | 6.7296 | 6.1888 | 5.6909 | 5.3072 | 4.9398 | 3.8613 | 3.0807 | 2.6511 | 8.7699 | 8.7669 | 8.6485 | 8.3342 | 8.0669 | 7.8526 | 7.5944 | 7.3587 | 7.1363 | 6.4189 | 6.0689 | 5.6904 | 8.1077 | 8.1026 | 7.8995 | 7.5271 | 7.1904 | 6.7985 | 6.3995 | 6.0699 | 5.7618 | 4.8455 | 4.3169 | 4.0506
|  | CASTLE CARY PRIMARY | FB |  |  |  |  | 7.9429 | 7.9756 | 7.998 | 7.8307 | 7.6133 | 7.348 | 7.0694 | 6.8643 | 6.6654 | 5.8562 | 5.1817 | 4.7143 | 8.8108 | 8.8179 | 8.8199 | 8.7393 | 8.6261 | 8.5077 | 8.373 | 8.2373 | 7.9924 | 7.1679 | 6.1659 | 5.0904 | 8.1995 | 8.2179 | 8.2363 | 8.1097 | 7.9506 | 7.7689 | 7.574 | 7.4189 | 7.1842 | 6.3873 | 5.7118 | 5.2301
LALEHAM GSP | STAINES BSP | CAUSEWAY PRIMARY | MINIMUM HEADROOM | TQ 02763 71680 | NO | NO | 6.541 | 26.0451 | 25.9808 | 25.9298 | 25.6614 | 25.2583 | 24.6553 | 23.941 | 23.2185 | 22.4787 | 18.9236 | 17.0696 | 16.2226 | 27.8093 | 27.7491 | 27.7318 | 27.5798 | 27.3563 | 27.0685 | 26.694 | 26.291 | 25.8696 | 23.5604 | 21.2308 | 16.9379 | 28.1165 | 28.1032 | 28.1063 | 27.9379 | 27.6706 | 27.2267 | 26.6624 | 26.0012 | 25.3042 | 21.5655 | 20.043 | 19.6257
|  | CAUSEWAY PRIMARY | EE |  |  |  |  | 26.0451 | 25.9808 | 25.9298 | 25.7144 | 25.3991 | 24.84 | 24.1532 | 23.4798 | 22.7838 | 19.4471 | 17.7175 | 16.843 | 27.8104 | 27.7512 | 27.7379 | 27.6175 | 27.4359 | 27.1889 | 26.8634 | 26.5063 | 26.14 | 23.5604 | 21.7522 | 20.0655 | 28.1165 | 28.1032 | 28.1063 | 27.9981 | 27.8053 | 27.4063 | 26.8961 | 26.342 | 25.7196 | 22.0798 | 20.4502 | 19.7165
|  | CAUSEWAY PRIMARY | HT |  |  |  |  | 26.0532 | 25.994 | 25.9542 | 25.6614 | 25.2583 | 24.6553 | 23.941 | 23.2185 | 22.4787 | 18.9236 | 17.0696 | 16.2226 | 27.8134 | 27.7512 | 27.7318 | 27.5798 | 27.3563 | 27.0685 | 26.694 | 26.291 | 25.8696 | 23.7134 | 22.7165 | 22.341 | 28.1206 | 28.1073 | 28.1104 | 27.9379 | 27.6706 | 27.2267 | 26.6624 | 26.0012 | 25.3042 | 21.5655 | 20.043 | 19.6257
|  | CAUSEWAY PRIMARY | HE |  |  |  |  | 26.0512 | 25.9889 | 25.9451 | 25.6961 | 25.3389 | 24.8012 | 24.1155 | 23.4359 | 22.7379 | 20.0114 | 18.6114 | 17.9277 | 27.8093 | 27.7491 | 27.7359 | 27.6104 | 27.4206 | 27.1828 | 26.8542 | 26.5002 | 26.1369 | 23.7491 | 22.3002 | 20.6461 | 28.1165 | 28.1032 | 28.1083 | 27.9838 | 27.7685 | 27.3869 | 26.8726 | 26.3359 | 25.7155 | 22.7583 | 21.6042 | 21.0706
|  | CAUSEWAY PRIMARY | FB |  |  |  |  | 26.1991 | 26.2604 | 26.2155 | 26.19 | 26.1593 | 26.0389 | 25.9124 | 25.7175 | 25.4655 | 24.0675 | 22.0267 | 21.0287 | 27.8859 | 27.8787 | 27.7961 | 27.7287 | 27.6798 | 27.5022 | 27.3053 | 27.0583 | 26.7665 | 25.0389 | 21.2308 | 16.9379 | 28.2481 | 28.3257 | 28.3298 | 28.3308 | 28.3583 | 28.2971 | 28.2196 | 28.0685 | 27.8461 | 26.5298 | 24.2277 | 22.7389
FLEET-BRAMLEY GSP | READING TOWN BSP | CAVERSHAM PRIMARY | MINIMUM HEADROOM | SU 71512 75747 | NO | NO | 0.7 | 17.2224 | 17.3143 | 17.2714 | 17.0398 | 16.8 | 16.0082 | 15.0949 | 14.1286 | 13.2122 | 9.9714 | 7.5337 | 6.2714 | 19.4878 | 19.4878 | 19.3592 | 19.1653 | 18.9449 | 18.5612 | 18.0643 | 17.5204 | 17.0082 | 14.6235 | 11.7112 | 7.4429 | 18.1051 | 18.152 | 18.0918 | 17.8867 | 17.6684 | 17.0949 | 16.3939 | 15.6408 | 14.9337 | 12.2878 | 10.5306 | 9.7327
|  | CAVERSHAM PRIMARY | EE |  |  |  |  | 17.2224 | 17.3786 | 17.3255 | 17.1122 | 16.8306 | 16.0082 | 15.0949 | 14.1286 | 13.2122 | 9.9714 | 7.5337 | 6.2714 | 19.4888 | 19.5173 | 19.3908 | 19.2112 | 18.9847 | 18.5918 | 18.0857 | 17.5255 | 17.0082 | 14.6235 | 12.9755 | 11.4316 | 18.1051 | 18.1949 | 18.1286 | 17.9429 | 17.7041 | 17.0949 | 16.3939 | 15.6408 | 14.9337 | 12.2878 | 10.5306 | 9.7327
|  | CAVERSHAM PRIMARY | HT |  |  |  |  | 17.2296 | 17.3143 | 17.2714 | 17.0398 | 16.802 | 16.1041 | 15.3133 | 14.4857 | 13.7061 | 10.2837 | 7.8245 | 6.6663 | 19.4878 | 19.4878 | 19.3592 | 19.1653 | 18.9449 | 18.5612 | 18.0643 | 17.5204 | 17.0184 | 15.1684 | 14.3133 | 14.0388 | 18.1112 | 18.152 | 18.0918 | 17.8867 | 17.6684 | 17.1306 | 16.499 | 15.8265 | 15.1969 | 12.4908 | 10.8173 | 10.2143
|  | CAVERSHAM PRIMARY | HE |  |  |  |  | 17.2337 | 17.3949 | 17.35 | 17.1082 | 16.8 | 16.0194 | 15.1408 | 14.2133 | 13.3286 | 10.5418 | 8.3908 | 7.3918 | 19.4908 | 19.5214 | 19.3949 | 19.2112 | 18.9878 | 18.599 | 18.098 | 17.5459 | 17.0327 | 14.6959 | 13.0357 | 11.4071 | 18.1143 | 18.2122 | 18.151 | 17.9449 | 17.6898 | 17.1092 | 16.4306 | 15.7061 | 15.0184 | 12.6847 | 11.151 | 10.4878
|  | CAVERSHAM PRIMARY | FB |  |  |  |  | 17.499 | 17.6551 | 17.8541 | 17.8888 | 17.8786 | 17.7582 | 17.598 | 17.4061 | 17.1939 | 15.5969 | 13.5704 | 12.5102 | 19.6276 | 19.5898 | 19.5908 | 19.4898 | 19.3255 | 19.0347 | 18.7031 | 18.348 | 17.9653 | 15.3214 | 11.7112 | 7.4429 | 18.3724 | 18.4714 | 18.6092 | 18.6327 | 18.6082 | 18.4847 | 18.3255 | 18.1367 | 17.9224 | 16.3051 | 14.4755 | 13.5388
MANNINGTON GSP | BOURNEMOUTH BSP | CENTRAL PRIMARY | MINIMUM HEADROOM | SZ 10293 91931 | NO | YES | 1.592 | 6.5592 | 6.6694 | 6.1122 | 5.7857 | 4.2929 | 3.3 | 1.6429 | 0.54184 | -0.74796 | -5.9459 | -10.1612 | -11.5806 | 11.7531 | 11.6408 | 11.2561 | 10.9327 | 10 | 9.2745 | 8.1031 | 7.2714 | 6.2306 | 1.7255 | -4.5959 | -13.8796 | 8.699 | 8.7327 | 8.199 | 7.8469 | 6.6429 | 5.7806 | 4.3582 | 3.402 | 2.2173 | -2.4092 | -6.3398 | -7.7643
|  | CENTRAL PRIMARY | EE |  |  |  |  | 6.5735 | 6.7102 | 6.2939 | 6.0439 | 4.552 | 3.8 | 2.3316 | 1.5265 | 0.65102 | -4.6653 | -9.4235 | -11.2622 | 11.7704 | 11.7612 | 11.399 | 11.0622 | 10.1235 | 9.5 | 8.4102 | 7.702 | 6.8918 | 1.7255 | -2.8541 | -6.2929 | 8.7041 | 8.7429 | 8.3347 | 7.998 | 6.7776 | 6.0541 | 4.7337 | 3.9908 | 3.148 | -1.9939 | -6.3398 | -7.7643
|  | CENTRAL PRIMARY | HT |  |  |  |  | 6.5592 | 6.6694 | 6.1122 | 5.7857 | 4.2929 | 3.3 | 1.6429 | 0.54184 | -0.74796 | -5.9459 | -10.1612 | -11.5806 | 11.7531 | 11.7286 | 11.2561 | 10.9327 | 10 | 9.2745 | 8.1031 | 7.2714 | 6.2306 | 2.6857 | -0.019388 | -0.97245 | 8.699 | 8.7327 | 8.199 | 7.8469 | 6.6429 | 5.7806 | 4.3582 | 3.402 | 2.2173 | -2.4092 | -6.1031 | -7.1837
|  | CENTRAL PRIMARY | HE |  |  |  |  | 6.598 | 6.8041 | 6.3388 | 6.1694 | 4.7102 | 4.0388 | 2.6684 | 1.9061 | 1.0929 | -2.4531 | -5.6867 | -7.3306 | 11.7837 | 11.8296 | 11.4122 | 11.1694 | 10.2561 | 9.6663 | 8.6296 | 7.9214 | 7.1224 | 2.9541 | -0.95306 | -4.5388 | 8.7265 | 8.8367 | 8.3704 | 8.1449 | 6.9459 | 6.301 | 5.0684 | 4.3449 | 3.5531 | 0.18776 | -2.7367 | -4.0071
|  | CENTRAL PRIMARY | FB |  |  |  |  | 6.7337 | 6.9806 | 6.8276 | 6.9224 | 5.9735 | 5.8408 | 5.1643 | 5.0551 | 4.8337 | 2.6051 | -1.4398 | -4.5408 | 11.7602 | 11.6408 | 11.3071 | 11.1286 | 10.3388 | 9.7959 | 8.9184 | 8.401 | 7.7612 | 3.0286 | -4.5959 | -13.8796 | 8.9612 | 9.0592 | 8.8378 | 8.8408 | 8.1286 | 7.9398 | 7.3265 | 7.1929 | 6.9255 | 4.3949 | 0.32755 | -2.7367
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CENTRAL BRIDGE PRIMARY | MINIMUM HEADROOM | SU 42591 11255 | NO | YES | 2.61 | 21.3078 | 21.1874 | 21.0915 | 20.9149 | 20.5619 | 19.4507 | 17.3956 | 15.42 | 12.3404 | 7.4762 | -1.3116 | -7.0953 | 23.9802 | 23.8272 | 23.6813 | 23.4802 | 23.1037 | 22.368 | 20.4251 | 17.1394 | 14.5629 | 8.7609 | -2.2106 | -10.682 | 21.9496 | 21.8027 | 21.6772 | 21.4782 | 21.1109 | 20.2129 | 18.1098 | 15.0843 | 12.1935 | 6.4088 | -4.4085 | -11.6738
|  | CENTRAL BRIDGE PRIMARY | EE |  |  |  |  | 21.3078 | 21.1874 | 21.1078 | 20.97 | 20.7435 | 20.3629 | 19.8068 | 17.866 | 15.4149 | 10.8272 | 1.2047 | -1.781 | 23.9966 | 23.8282 | 23.6956 | 23.5109 | 23.2558 | 22.8527 | 22.1792 | 20.4333 | 17.9976 | 12.3343 | -0.21057 | -5.2044 | 21.9496 | 21.8027 | 21.6833 | 21.519 | 21.2619 | 20.867 | 20.2211 | 18.3058 | 15.717 | 10.4843 | -1.3289 | -5.0412
|  | CENTRAL BRIDGE PRIMARY | HT |  |  |  |  | 21.3139 | 21.1904 | 21.0915 | 20.9149 | 20.5619 | 19.4507 | 17.3956 | 15.7496 | 12.3404 | 7.4762 | -1.3116 | -7.0953 | 23.9986 | 23.8272 | 23.6813 | 23.4802 | 23.1037 | 22.368 | 20.4251 | 18.6517 | 14.5629 | 8.7609 | -2.2106 | -9.7891 | 21.9578 | 21.8047 | 21.6772 | 21.4782 | 21.1109 | 20.2129 | 18.1098 | 16.2956 | 12.1935 | 6.4088 | -4.4085 | -11.6738
|  | CENTRAL BRIDGE PRIMARY | HE |  |  |  |  | 21.32 | 21.2007 | 21.1292 | 20.9945 | 20.7792 | 20.4098 | 19.2496 | 15.42 | 14.517 | 8.5598 | 2.267 | -5.63 | 24.0007 | 23.8302 | 23.6976 | 23.5119 | 23.2527 | 22.868 | 21.4404 | 17.1394 | 16.4853 | 9.0782 | 0.49453 | -10.682 | 21.9558 | 21.8078 | 21.6945 | 21.5221 | 21.2588 | 20.8864 | 19.4884 | 15.0843 | 14.3292 | 7.3558 | -0.39935 | -10.2759
|  | CENTRAL BRIDGE PRIMARY | FB |  |  |  |  | 21.419 | 21.3904 | 21.3609 | 21.319 | 21.2874 | 21.1384 | 20.7731 | 20.2578 | 18.7496 | 14.3415 | 9.817 | 5.6323 | 23.9802 | 23.8476 | 23.7047 | 23.5394 | 23.3547 | 23.0394 | 22.4282 | 21.6211 | 19.967 | 14.4456 | 7.2894 | -0.85547 | 22.0507 | 22.0098 | 21.9425 | 21.8598 | 21.7966 | 21.6282 | 21.1915 | 20.5588 | 18.9619 | 14.2017 | 8.8874 | 3.8588
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS PRIMARY | MINIMUM HEADROOM | ST 66140 01039 | YES | NO | 0.021 | 2.6429 | 2.6439 | 2.6286 | 2.6071 | 2.5704 | 2.5418 | 2.4959 | 2.4388 | 2.4133 | 2.3184 | 2.2429 | 2.2163 | 3.1847 | 3.1816 | 3.1673 | 3.152 | 3.1235 | 3.102 | 3.0653 | 3.0224 | 3.0061 | 2.9163 | 2.8306 | 2.6561 | 2.8071 | 2.8071 | 2.7969 | 2.7786 | 2.7469 | 2.7194 | 2.6724 | 2.6194 | 2.6061 | 2.5143 | 2.4561 | 2.4398
|  | CERNE ABBAS PRIMARY | EE |  |  |  |  | 2.6429 | 2.6439 | 2.6286 | 2.6071 | 2.5735 | 2.5418 | 2.5031 | 2.449 | 2.4276 | 2.3184 | 2.252 | 2.2378 | 3.1867 | 3.1827 | 3.1673 | 3.152 | 3.1245 | 3.1031 | 3.0673 | 3.0235 | 3.0082 | 2.9184 | 2.8816 | 2.8286 | 2.8092 | 2.8071 | 2.7969 | 2.7786 | 2.749 | 2.7214 | 2.6755 | 2.6265 | 2.6061 | 2.5153 | 2.4663 | 2.4653
|  | CERNE ABBAS PRIMARY | HT |  |  |  |  | 2.6439 | 2.6449 | 2.6327 | 2.6153 | 2.5837 | 2.5561 | 2.5102 | 2.4684 | 2.449 | 2.3408 | 2.2663 | 2.25 | 3.1878 | 3.1816 | 3.1684 | 3.152 | 3.1245 | 3.102 | 3.0653 | 3.0224 | 3.0071 | 2.9163 | 2.8847 | 2.9061 | 2.8092 | 2.8082 | 2.8 | 2.7827 | 2.7541 | 2.7286 | 2.6837 | 2.6367 | 2.6184 | 2.5245 | 2.4745 | 2.4786
|  | CERNE ABBAS PRIMARY | HE |  |  |  |  | 2.6429 | 2.6439 | 2.6316 | 2.6092 | 2.5704 | 2.548 | 2.4959 | 2.4388 | 2.4133 | 2.3184 | 2.2429 | 2.2163 | 3.1847 | 3.1816 | 3.1694 | 3.1531 | 3.1235 | 3.1031 | 3.0663 | 3.0224 | 3.0061 | 2.9173 | 2.8704 | 2.8071 | 2.8071 | 2.8071 | 2.801 | 2.7806 | 2.7469 | 2.7194 | 2.6724 | 2.6194 | 2.6082 | 2.5143 | 2.4561 | 2.4398
|  | CERNE ABBAS PRIMARY | FB |  |  |  |  | 2.6622 | 2.6684 | 2.6694 | 2.6684 | 2.6571 | 2.6551 | 2.6439 | 2.6286 | 2.6092 | 2.5122 | 2.4143 | 2.3765 | 3.1969 | 3.1959 | 3.1908 | 3.1898 | 3.1776 | 3.1724 | 3.1571 | 3.1408 | 3.1184 | 2.9969 | 2.8306 | 2.6561 | 2.8286 | 2.8347 | 2.8357 | 2.8327 | 2.8204 | 2.8204 | 2.8061 | 2.7898 | 2.7704 | 2.6735 | 2.5714 | 2.5327
LOVEDEAN GSP |  | CHALCRAFT LANE PRIMARY | MINIMUM HEADROOM | TBC | NO | YES | 0 |  |  |  | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | EE | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | HT | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | HE | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | FB | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
IVER 132KV GSP | CHALVEY BSP | CHALVEY PRIMARY | MINIMUM HEADROOM | SU 96669 79364 | NO | YES | 10.937 | 35.3107 | 35.3627 | 35.1087 | 34.4199 | 33.4066 | 32.3301 | 30.7944 | 28.8954 | 26.9597 | 19.577 | 14.9668 | 13.0189 | 43.2893 | 43.1219 | 42.6689 | 41.8668 | 40.8087 | 39.6923 | 38.0576 | 36.077 | 34.0801 | 25.7689 | 20.2893 | 12.6668 | 36.2944 | 36.1597 | 35.6893 | 34.8964 | 33.8893 | 32.8005 | 31.176 | 29.1995 | 27.2025 | 19.5127 | 14.9219 | 13.0138
|  | CHALVEY PRIMARY | EE |  |  |  |  | 35.3107 | 35.3627 | 35.1087 | 34.4199 | 33.4066 | 32.3301 | 30.7944 | 28.8954 | 26.9597 | 19.577 | 14.9668 | 13.0189 | 43.2893 | 43.1219 | 42.6709 | 41.8668 | 40.8087 | 39.6923 | 38.0576 | 36.077 | 34.0801 | 25.7689 | 20.2893 | 15.9923 | 36.2944 | 36.1597 | 35.6893 | 34.8964 | 33.8893 | 32.8005 | 31.176 | 29.1995 | 27.2025 | 19.5127 | 14.9219 | 13.0138
|  | CHALVEY PRIMARY | HT |  |  |  |  | 35.3433 | 35.428 | 35.1648 | 34.4403 | 33.6311 | 32.5729 | 31.2474 | 29.1546 | 27.0352 | 20.5536 | 17.3036 | 16.7382 | 43.2933 | 43.126 | 42.6689 | 41.8699 | 41.0229 | 39.925 | 38.6393 | 36.6321 | 34.5811 | 28.2719 | 25.1903 | 24.2893 | 36.324 | 36.2138 | 35.7505 | 34.9229 | 34.1015 | 33.0331 | 31.7321 | 29.6638 | 27.5546 | 20.824 | 17.4464 | 16.875
|  | CHALVEY PRIMARY | HE |  |  |  |  | 35.3495 | 35.4352 | 35.2097 | 34.4923 | 33.476 | 32.4311 | 31.2903 | 29.676 | 28.0076 | 23.2087 | 20.4587 | 19.3638 | 43.2954 | 43.1393 | 42.6984 | 41.8995 | 40.8627 | 39.7352 | 38.5515 | 36.8842 | 35.178 | 29.0362 | 24.574 | 20.6658 | 36.328 | 36.2199 | 35.7791 | 34.9648 | 33.9515 | 32.8882 | 31.7444 | 30.1138 | 28.4382 | 23.526 | 20.7454 | 19.6933
|  | CHALVEY PRIMARY | FB |  |  |  |  | 35.5984 | 35.8301 | 35.8046 | 35.7036 | 35.2168 | 34.6209 | 34.1648 | 33.4862 | 32.7362 | 29.0811 | 24.378 | 21.0229 | 43.4536 | 43.4648 | 43.0505 | 42.5546 | 41.5872 | 40.6148 | 39.7862 | 38.774 | 37.7148 | 31.5617 | 22.875 | 12.6668 | 36.8464 | 37.0995 | 36.8321 | 36.5331 | 35.8546 | 35.2536 | 34.7801 | 34.1015 | 33.3617 | 29.5607 | 24.8566 | 21.5291
NURSLING GSP | VELMORE BSP | CHANDLERS FORD PRIMARY | MINIMUM HEADROOM | SU 43494 21552 | NO | YES | 4.641 | 9.6645 | 9.6992 | 9.6288 | 9.3778 | 8.9645 | 7.9706 | 6.8033 | 5.5492 | 4.2747 | -0.23245 | -3.4069 | -4.6978 | 13.9002 | 13.8594 | 13.7033 | 13.4655 | 12.9818 | 12.4186 | 11.6767 | 10.8502 | 10.0349 | 7.2145 | 4.5165 | -0.13041 | 11.7482 | 11.7757 | 11.7002 | 11.4573 | 10.8594 | 10.1512 | 9.2237 | 8.1829 | 7.1431 | 3.5002 | 1.3563 | 0.73286
|  | CHANDLERS FORD PRIMARY | EE |  |  |  |  | 9.6645 | 9.6992 | 9.6288 | 9.4002 | 9.0329 | 8.04 | 6.8614 | 5.6267 | 4.3971 | 0.11755 | -2.9376 | -4.5192 | 13.9033 | 13.8665 | 13.7084 | 13.4951 | 13.0961 | 12.5573 | 11.8329 | 11.0553 | 10.3288 | 7.2145 | 5.19 | 3.439 | 11.7482 | 11.7757 | 11.7002 | 11.4747 | 10.9737 | 10.242 | 9.2584 | 8.2512 | 7.2818 | 3.8318 | 1.6849 | 0.73286
|  | CHANDLERS FORD PRIMARY | HT |  |  |  |  | 9.6676 | 9.7063 | 9.6482 | 9.4043 | 8.99 | 8.0727 | 6.9563 | 5.6951 | 4.4196 | -0.23245 | -3.4069 | -4.6978 | 13.9002 | 13.8594 | 13.7033 | 13.4655 | 12.9818 | 12.4186 | 11.6767 | 10.8502 | 10.0349 | 7.4676 | 6.3033 | 6.0206 | 11.7522 | 11.7839 | 11.7114 | 11.4573 | 10.8594 | 10.1512 | 9.2237 | 8.1829 | 7.1431 | 3.5002 | 1.3563 | 0.74204
|  | CHANDLERS FORD PRIMARY | HE |  |  |  |  | 9.6716 | 9.7084 | 9.6431 | 9.3778 | 8.9645 | 7.9706 | 6.8033 | 5.5492 | 4.2747 | 0.58184 | -2.0865 | -3.2794 | 13.9022 | 13.8655 | 13.7053 | 13.4869 | 13.0798 | 12.54 | 11.8329 | 11.0655 | 10.3073 | 7.4329 | 5.4461 | 3.5798 | 11.7563 | 11.7829 | 11.7124 | 11.4624 | 10.939 | 10.1982 | 9.2339 | 8.2247 | 7.2176 | 4.238 | 2.3696 | 1.59
|  | CHANDLERS FORD PRIMARY | FB |  |  |  |  | 9.9318 | 9.9869 | 10.1655 | 10.2063 | 10.1971 | 10.0594 | 9.8573 | 9.6002 | 9.2553 | 7.1247 | 4.6869 | 3.4063 | 14.0716 | 13.9849 | 13.9859 | 13.8767 | 13.6992 | 13.3584 | 12.9563 | 12.5155 | 11.9951 | 8.7053 | 4.5165 | -0.13041 | 12.038 | 12.1012 | 12.2308 | 12.2176 | 12.1482 | 11.9839 | 11.7604 | 11.488 | 11.1441 | 8.9206 | 6.7961 | 5.6308
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CHAPEL PRIMARY | MINIMUM HEADROOM | SU 42849 11983 | NO | YES | 2.998 | 8.9718 | 9.0433 | 9.0106 | 8.981 | 8.8963 | 8.6096 | 8.3759 | 8.2035 | 8.0616 | 6.9198 | 6.2718 | 5.9688 | 12.8937 | 12.8661 | 12.8222 | 12.7682 | 12.6059 | 12.2253 | 11.8978 | 11.5059 | 11.1784 | 9.8376 | 7.709 | 3.7733 | 10.6555 | 10.7127 | 10.6514 | 10.6208 | 10.4922 | 10.0596 | 9.6963 | 9.3024 | 8.9667 | 7.8259 | 7.2596 | 6.9627
|  | CHAPEL PRIMARY | EE |  |  |  |  | 8.9718 | 9.0433 | 9.0269 | 9.0443 | 9.029 | 8.9678 | 8.8892 | 8.5229 | 8.3045 | 7.1861 | 6.3443 | 5.9688 | 12.9539 | 12.9712 | 12.8835 | 12.8376 | 12.7161 | 12.4682 | 12.2478 | 11.7437 | 11.3692 | 9.8376 | 8.6345 | 7.4324 | 10.6555 | 10.7127 | 10.6576 | 10.6616 | 10.6331 | 10.4014 | 10.1953 | 9.6229 | 9.2167 | 7.98 | 7.2596 | 6.9627
|  | CHAPEL PRIMARY | HT |  |  |  |  | 8.9739 | 9.0443 | 9.0106 | 8.981 | 8.8963 | 8.6096 | 8.3759 | 8.2035 | 8.0616 | 6.9198 | 6.2718 | 6.079 | 12.9539 | 12.9671 | 12.8692 | 12.8018 | 12.6059 | 12.2253 | 11.8978 | 11.5059 | 11.1784 | 10.0824 | 9.5233 | 9.2631 | 10.6596 | 10.7157 | 10.6514 | 10.6208 | 10.4922 | 10.0596 | 9.6963 | 9.3024 | 8.9667 | 7.8259 | 7.3045 | 7.1963
|  | CHAPEL PRIMARY | HE |  |  |  |  | 8.982 | 9.0586 | 9.0504 | 9.0667 | 9.0647 | 9.0259 | 8.9586 | 8.6963 | 8.4912 | 7.8259 | 7.331 | 7.1055 | 12.9539 | 12.9702 | 12.8855 | 12.8324 | 12.7171 | 12.4957 | 12.2692 | 11.8284 | 11.4427 | 10.2631 | 9.1998 | 8.0865 | 10.6616 | 10.7239 | 10.678 | 10.6759 | 10.6422 | 10.4473 | 10.2453 | 9.7749 | 9.3616 | 8.5616 | 8.1239 | 7.9616
|  | CHAPEL PRIMARY | FB |  |  |  |  | 8.9882 | 9.0555 | 9.1086 | 9.1667 | 9.1739 | 9.1769 | 9.1606 | 9.129 | 8.9596 | 8.432 | 7.9392 | 6.8973 | 12.8937 | 12.8661 | 12.8222 | 12.7682 | 12.6192 | 12.459 | 12.2722 | 12.0692 | 11.7784 | 10.161 | 7.709 | 3.7733 | 10.6739 | 10.73 | 10.7718 | 10.8208 | 10.8096 | 10.8014 | 10.778 | 10.73 | 10.5382 | 9.5463 | 8.6239 | 7.6076
COWLEY GSP | YARNTON BSP | CHARLBURY PRIMARY | MINIMUM HEADROOM | SP 36034 18376 | NO | YES | 0.435 | 8.6423 | 8.6668 | 8.6413 | 8.5485 | 8.1974 | 7.8352 | 7.325 | 6.8138 | 6.3566 | 4.7801 | 3.3056 | 2.2617 | 7.7378 | 7.7378 | 7.6878 | 7.6429 | 7.4582 | 7.3296 | 7.15 | 6.9765 | 6.8061 | 6.2724 | 5.798 | 4.3612 | 7.9551 | 7.9673 | 7.9204 | 7.8796 | 7.6673 | 7.4755 | 7.2429 | 6.9918 | 6.7571 | 5.6173 | 4.6582 | 4.0765
|  | CHARLBURY PRIMARY | EE |  |  |  |  | 8.6423 | 8.6668 | 8.674 | 8.6342 | 8.3546 | 7.9546 | 7.4291 | 6.9526 | 6.4699 | 4.9607 | 3.676 | 2.8689 | 7.7388 | 7.7398 | 7.7092 | 7.6867 | 7.5316 | 7.4082 | 7.2408 | 7.0633 | 6.8959 | 6.398 | 5.8949 | 5.2867 | 7.9561 | 7.9673 | 7.9459 | 7.9429 | 7.7612 | 7.5582 | 7.3092 | 7.0602 | 6.8112 | 5.7714 | 4.8939 | 4.4143
|  | CHARLBURY PRIMARY | HT |  |  |  |  | 8.6577 | 8.6872 | 8.6413 | 8.5485 | 8.1974 | 7.8352 | 7.3689 | 6.9097 | 6.4801 | 4.7801 | 3.3056 | 2.2617 | 7.7398 | 7.7378 | 7.6878 | 7.6429 | 7.4582 | 7.3296 | 7.15 | 6.9765 | 6.8061 | 6.2724 | 6.0388 | 5.9031 | 7.9633 | 7.9755 | 7.9204 | 7.8796 | 7.6673 | 7.4755 | 7.2429 | 6.9918 | 6.7571 | 5.6173 | 4.6582 | 4.0765
|  | CHARLBURY PRIMARY | HE |  |  |  |  | 8.6434 | 8.6679 | 8.676 | 8.6087 | 8.2944 | 7.8709 | 7.325 | 6.8138 | 6.3566 | 5.1495 | 4.0066 | 3.3719 | 7.7378 | 7.7408 | 7.7071 | 7.6806 | 7.5276 | 7.402 | 7.2306 | 7.0531 | 6.8959 | 6.4306 | 5.9684 | 5.3684 | 7.9551 | 7.9673 | 7.9469 | 7.9276 | 7.7347 | 7.5255 | 7.2673 | 7.0082 | 6.7571 | 5.9122 | 5.152 | 4.7704
|  | CHARLBURY PRIMARY | FB |  |  |  |  | 8.7372 | 8.8005 | 8.8485 | 8.8872 | 8.8209 | 8.7964 | 8.7832 | 8.7291 | 8.6648 | 7.825 | 6.8291 | 6.1607 | 7.802 | 7.8204 | 7.8296 | 7.8378 | 7.798 | 7.7622 | 7.7378 | 7.6806 | 7.6112 | 7.0449 | 5.798 | 4.3612 | 8.0388 | 8.0806 | 8.1143 | 8.1306 | 8.0908 | 8.0714 | 8.0622 | 8.0102 | 7.9469 | 7.4347 | 6.8357 | 6.4
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER PRIMARY | MINIMUM HEADROOM | SY 67309 93186 | NO | NO | 1.895 | 5.8832 | 5.7495 | 5.5393 | 5.1801 | 4.6474 | 3.876 | 2.9944 | 2.2117 | 1.3015 | -1.5995 | -3.7791 | -5.1862 | 7.7806 | 7.602 | 7.4714 | 7.2735 | 6.9378 | 6.5031 | 5.9357 | 5.4837 | 4.8786 | 3.101 | 2.1857 | 1.0388 | 6.8673 | 6.6898 | 6.5347 | 6.2551 | 5.8163 | 5.2153 | 4.498 | 3.8867 | 3.1327 | 0.81837 | -0.71735 | -1.5827
|  | CHARMINSTER PRIMARY | EE |  |  |  |  | 5.8934 | 5.7862 | 5.6209 | 5.3515 | 4.9383 | 4.2862 | 3.524 | 2.8597 | 2.0597 | -0.57704 | -2.5668 | -3.8321 | 7.7888 | 7.6245 | 7.5173 | 7.3602 | 7.0939 | 6.7245 | 6.2398 | 5.8439 | 5.3082 | 3.3694 | 2.1857 | 1.3327 | 6.8776 | 6.7184 | 6.601 | 6.3643 | 5.9408 | 5.4541 | 4.848 | 4.3286 | 3.6806 | 1.5051 | 0.0040816 | -0.88061
|  | CHARMINSTER PRIMARY | HT |  |  |  |  | 5.8832 | 5.7495 | 5.5393 | 5.1801 | 4.6474 | 3.876 | 2.9944 | 2.2117 | 1.3015 | -1.5995 | -3.7791 | -5.1862 | 7.7806 | 7.602 | 7.4714 | 7.2735 | 6.9378 | 6.5031 | 5.9357 | 5.4837 | 4.8786 | 3.101 | 2.2816 | 1.9306 | 6.8673 | 6.6898 | 6.5347 | 6.2551 | 5.8163 | 5.2153 | 4.498 | 3.8867 | 3.1327 | 0.81837 | -0.71735 | -1.5827
|  | CHARMINSTER PRIMARY | HE |  |  |  |  | 5.8923 | 5.7872 | 5.623 | 5.3474 | 4.923 | 4.2362 | 3.4393 | 2.776 | 1.9577 | 0.14337 | -1.6332 | -2.7281 | 7.7857 | 7.6224 | 7.5163 | 7.3582 | 7.0796 | 6.7153 | 6.2184 | 5.8469 | 5.3173 | 3.8867 | 2.8224 | 1.9316 | 6.8745 | 6.7184 | 6.602 | 6.3602 | 5.9306 | 5.4286 | 4.8041 | 4.299 | 3.648 | 2.1561 | 0.83367 | 0.030612
|  | CHARMINSTER PRIMARY | FB |  |  |  |  | 6.1413 | 6.2026 | 6.2291 | 5.9352 | 5.8015 | 5.6883 | 5.5464 | 5.3148 | 5.0842 | 3.5964 | 1.875 | 0.4852 | 7.9684 | 7.9561 | 7.9214 | 7.6541 | 7.5143 | 7.3786 | 7.2143 | 6.9592 | 6.699 | 5.1194 | 3.1755 | 1.0388 | 7.1296 | 7.15 | 7.1276 | 6.8449 | 6.6776 | 6.598 | 6.4602 | 6.2347 | 6.002 | 4.5786 | 3.2112 | 2.0031
LOVEDEAN GSP | CHICHESTER BSP | CHICHESTER PRIMARY | MINIMUM HEADROOM | SU 92198 07420 | NO | YES | 14.369 | -5.6943 | -5.9218 | 10.0013 | 9.3626 | 8.7279 | 7.5554 | 6.233 | 4.7677 | 3.3064 | -1.565 | -5.5854 | -8.014 | -1.7134 | -1.8134 | 15.4248 | 14.8554 | 14.3105 | 13.5993 | 12.8095 | 11.885 | 10.9258 | 8.0136 | 6.5115 | 3.486 | -3.4142 | -3.5693 | 12.9728 | 12.4248 | 11.8687 | 10.9034 | 9.8391 | 8.634 | 7.4238 | 3.5615 | 0.79828 | -0.59662
|  | CHICHESTER PRIMARY | EE |  |  |  |  | -5.6943 | -5.9218 | 10.0013 | 9.3891 | 8.7952 | 7.7197 | 6.433 | 5.2024 | 3.8758 | -0.44662 | -4.0946 | -6.2558 | -1.7103 | -1.8001 | 15.4564 | 14.936 | 14.4156 | 13.8258 | 13.0248 | 12.2881 | 11.4136 | 8.3411 | 6.5115 | 5.0758 | -3.4131 | -3.5693 | 12.9728 | 12.4483 | 11.9411 | 11.1034 | 10.0595 | 9.0656 | 7.9687 | 4.4085 | 1.7799 | 0.40849
|  | CHICHESTER PRIMARY | HT |  |  |  |  | -5.6851 | -5.8841 | 10.0922 | 9.4166 | 8.7697 | 7.5554 | 6.233 | 4.7677 | 3.3064 | -1.565 | -5.5854 | -8.014 | -1.7113 | -1.8134 | 15.4248 | 14.8554 | 14.3105 | 13.5993 | 12.8095 | 11.885 | 10.9258 | 8.0136 | 6.584 | 6.2554 | -3.4121 | -3.554 | 13.0075 | 12.4248 | 11.8687 | 10.9034 | 9.8391 | 8.634 | 7.4238 | 3.5615 | 0.79828 | -0.59662
|  | CHICHESTER PRIMARY | HE |  |  |  |  | -5.6912 | -5.9157 | 10.0136 | 9.3626 | 8.7279 | 7.6105 | 6.3258 | 4.9626 | 3.5524 | 0.30951 | -3.0599 | -4.9895 | -1.7134 | -1.8042 | 15.4544 | 14.9299 | 14.4003 | 13.832 | 13.0973 | 12.282 | 11.3911 | 8.886 | 7.0646 | 5.4187 | -3.4142 | -3.5642 | 12.9799 | 12.4309 | 11.8942 | 11.0442 | 10.0309 | 8.935 | 7.7871 | 5.0646 | 2.6422 | 1.3187
|  | CHICHESTER PRIMARY | FB |  |  |  |  | -5.3514 | -5.4565 | 10.8371 | 10.8024 | 10.5075 | 10.1973 | 9.8942 | 9.4503 | 9.0401 | 6.632 | 3.4707 | 1.1309 | -1.5787 | -1.6287 | 15.9238 | 15.8585 | 15.4656 | 15.1666 | 14.8932 | 14.4707 | 14.0228 | 11.1973 | 7.4799 | 3.486 | -3.1019 | -3.1866 | 13.6932 | 13.6738 | 13.3748 | 13.1003 | 12.833 | 12.4289 | 12.0483 | 9.8269 | 7.0881 | 5.0942
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL PRIMARY | MINIMUM HEADROOM | SY 65479 80511 | NO | NO | 1.554 | 10.8982 | 10.8318 | 10.738 | 10.5227 | 10.3002 | 9.8849 | 9.3624 | 8.7982 | 8.2196 | 5.4971 | 3.3482 | 2.6176 | 11.2531 | 11.2041 | 11.148 | 11.0306 | 10.9163 | 10.7357 | 10.5143 | 10.2918 | 9.8735 | 8.001 | 6.502 | 5.898 | 11.4318 | 11.3757 | 11.2839 | 11.1124 | 10.9114 | 10.5696 | 10.138 | 9.7329 | 9.3155 | 7.2706 | 5.6002 | 5.2165
|  | CHICKERELL PRIMARY | EE |  |  |  |  | 10.9022 | 10.8451 | 10.7645 | 10.5808 | 10.4043 | 10.0063 | 9.5441 | 9.0053 | 8.4604 | 6.0063 | 3.9502 | 3.1135 | 11.2561 | 11.2133 | 11.1653 | 11.0643 | 10.9755 | 10.8112 | 10.6133 | 10.4112 | 10.0582 | 8.0092 | 6.502 | 5.898 | 11.4359 | 11.3869 | 11.3002 | 11.1533 | 10.989 | 10.64 | 10.2298 | 9.8349 | 9.4359 | 7.6176 | 5.9737 | 5.4186
|  | CHICKERELL PRIMARY | HT |  |  |  |  | 10.8982 | 10.8318 | 10.738 | 10.5227 | 10.3002 | 9.8849 | 9.3624 | 8.7982 | 8.2196 | 5.4971 | 3.3482 | 2.6176 | 11.2531 | 11.2041 | 11.148 | 11.0306 | 10.9163 | 10.7357 | 10.5143 | 10.2918 | 9.8735 | 8.001 | 6.7561 | 6.6969 | 11.4318 | 11.3757 | 11.2839 | 11.1124 | 10.9114 | 10.5696 | 10.138 | 9.7329 | 9.3155 | 7.2706 | 5.6002 | 5.2165
|  | CHICKERELL PRIMARY | HE |  |  |  |  | 10.9033 | 10.8471 | 10.7686 | 10.5798 | 10.4002 | 9.9992 | 9.5298 | 8.9951 | 8.4471 | 6.6176 | 5.2441 | 4.6206 | 11.2561 | 11.2133 | 11.1673 | 11.0653 | 10.9816 | 10.8173 | 10.6173 | 10.4194 | 10.0837 | 8.5265 | 7.5929 | 6.9837 | 11.4369 | 11.39 | 11.3063 | 11.1563 | 10.99 | 10.641 | 10.2237 | 9.8329 | 9.4298 | 8.1808 | 7.142 | 6.7063
|  | CHICKERELL PRIMARY | FB |  |  |  |  | 10.9971 | 10.9482 | 10.9176 | 10.8931 | 10.838 | 10.7522 | 10.6706 | 10.6033 | 10.4767 | 9.7645 | 8.3808 | 7.2584 | 11.3327 | 11.2745 | 11.2439 | 11.2245 | 11.1847 | 11.1163 | 11.049 | 10.9898 | 10.8633 | 9.8714 | 7.9918 | 6.0847 | 11.5278 | 11.4788 | 11.4441 | 11.4084 | 11.3696 | 11.2829 | 11.2022 | 11.1349 | 11.0033 | 10.242 | 9.2961 | 8.2624
AXMINSTER GSP | YEOVIL BSP | CHILTON CANTELO PRIMARY | MINIMUM HEADROOM | ST 57910 21616 | NO | NO | 4.61 | 1.9423 | 1.9515 | 1.9668 | 1.9454 | 1.925 | 1.6934 | 1.4719 | 1.1883 | 0.9852 | 0.44235 | 0.087245 | -0.047449 | 2.6959 | 2.6816 | 2.6653 | 2.6255 | 2.5857 | 2.4306 | 2.2663 | 2.0051 | 1.801 | 1.0061 | 0.56531 | 0.053061 | 2.2082 | 2.2112 | 2.2143 | 2.1959 | 2.1827 | 1.998 | 1.8092 | 1.5786 | 1.4184 | 1.002 | 0.79796 | 0.73061
|  | CHILTON CANTELO PRIMARY | EE |  |  |  |  | 1.9423 | 1.976 | 1.9668 | 1.9485 | 1.9321 | 1.8301 | 1.7393 | 1.4719 | 1.1883 | 0.44235 | 0.087245 | -0.047449 | 2.6959 | 2.6939 | 2.6653 | 2.6255 | 2.5959 | 2.4939 | 2.3816 | 2.1888 | 1.9031 | 1.0061 | 0.56531 | 0.31122 | 2.2082 | 2.2276 | 2.2143 | 2.1969 | 2.1898 | 2.0949 | 1.9663 | 1.7306 | 1.5235 | 1.002 | 0.79796 | 0.73061
|  | CHILTON CANTELO PRIMARY | HT |  |  |  |  | 1.9434 | 1.9515 | 1.9709 | 1.9495 | 1.925 | 1.6934 | 1.4719 | 1.1883 | 0.9852 | 0.51378 | 0.2199 | 0.11684 | 2.6959 | 2.6816 | 2.6663 | 2.6265 | 2.5857 | 2.4306 | 2.2663 | 2.0051 | 1.801 | 1.098 | 0.82755 | 0.78469 | 2.2082 | 2.2112 | 2.2153 | 2.199 | 2.1827 | 1.998 | 1.8092 | 1.5786 | 1.4184 | 1.0173 | 0.83469 | 0.83878
|  | CHILTON CANTELO PRIMARY | HE |  |  |  |  | 1.9434 | 1.9781 | 1.9811 | 1.9454 | 1.925 | 1.8209 | 1.7291 | 1.4913 | 1.2342 | 0.55969 | 0.22194 | 0.047449 | 2.698 | 2.6939 | 2.6714 | 2.6255 | 2.5949 | 2.4918 | 2.3816 | 2.1949 | 1.9551 | 1.1673 | 0.80918 | 0.53469 | 2.2092 | 2.2276 | 2.2235 | 2.1959 | 2.1847 | 2.0857 | 1.9571 | 1.7388 | 1.5469 | 1.0684 | 0.87347 | 0.77041
|  | CHILTON CANTELO PRIMARY | FB |  |  |  |  | 2.0056 | 2.0577 | 2.0944 | 2.1087 | 2.1179 | 2.1087 | 2.0934 | 2.1107 | 1.9791 | 1.324 | 0.82908 | 0.55357 | 2.7459 | 2.7561 | 2.75 | 2.7429 | 2.7235 | 2.6816 | 2.6367 | 2.6224 | 2.5153 | 1.7663 | 0.8898 | 0.053061 | 2.2694 | 2.3082 | 2.3265 | 2.3378 | 2.3449 | 2.3306 | 2.3082 | 2.3224 | 2.2276 | 1.6561 | 1.2806 | 1.0816
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | CHINEHAM PRIMARY | MINIMUM HEADROOM | SU 65105 55805 | NO | NO | 6.975 | 13.8366 | 13.7713 | 13.705 | 13.3376 | 12.8713 | 11.9509 | 10.6703 | 9.3774 | 8.1509 | 5.0335 | 3.2815 | 2.3162 | 16.5774 | 16.5284 | 16.5294 | 16.308 | 16.0805 | 15.6325 | 14.9856 | 14.3141 | 13.7131 | 11.955 | 10.8141 | 8.4611 | 14.9488 | 14.9019 | 14.9152 | 14.5631 | 14.207 | 13.4856 | 12.4682 | 11.4254 | 10.4713 | 8.0448 | 6.8192 | 6.1019
|  | CHINEHAM PRIMARY | EE |  |  |  |  | 13.8366 | 13.7713 | 13.7131 | 13.4233 | 13.0243 | 12.2203 | 11.2386 | 9.8835 | 8.5978 | 5.2396 | 3.6203 | 2.5386 | 16.5784 | 16.5305 | 16.5448 | 16.356 | 16.1774 | 15.8499 | 15.3519 | 14.6845 | 14.0866 | 11.955 | 10.8141 | 9.8448 | 14.9488 | 14.9019 | 14.9152 | 14.6376 | 14.3601 | 13.7366 | 12.9631 | 11.8886 | 10.907 | 8.1121 | 6.8345 | 6.1019
|  | CHINEHAM PRIMARY | HT |  |  |  |  | 13.8448 | 13.7896 | 13.705 | 13.3376 | 12.8713 | 11.9509 | 10.6703 | 9.3774 | 8.1509 | 5.0335 | 3.2815 | 2.3162 | 16.5794 | 16.5315 | 16.5294 | 16.308 | 16.0805 | 15.6325 | 14.9856 | 14.3141 | 13.7131 | 12.1815 | 11.4835 | 11.2111 | 14.9539 | 14.9141 | 14.9162 | 14.5631 | 14.207 | 13.4856 | 12.4682 | 11.4254 | 10.4713 | 8.0448 | 6.8192 | 6.2886
|  | CHINEHAM PRIMARY | HE |  |  |  |  | 13.8448 | 13.7835 | 13.7305 | 13.4039 | 12.9692 | 12.2141 | 11.259 | 10.1641 | 9.1223 | 6.5356 | 4.6009 | 3.8733 | 16.5774 | 16.5284 | 16.5427 | 16.3509 | 16.1662 | 15.8509 | 15.3417 | 14.7692 | 14.2468 | 12.3978 | 11.158 | 10.1876 | 14.9529 | 14.9111 | 14.9345 | 14.6254 | 14.3305 | 13.7468 | 12.9723 | 12.0948 | 11.2754 | 9.1111 | 7.6662 | 7.1264
|  | CHINEHAM PRIMARY | FB |  |  |  |  | 13.9611 | 13.9784 | 13.9886 | 13.9478 | 13.7978 | 13.509 | 13.1978 | 12.7866 | 12.1856 | 10.1182 | 8.1407 | 6.8927 | 16.6641 | 16.6499 | 16.6192 | 16.5743 | 16.5152 | 16.2948 | 16.0539 | 15.7233 | 15.2631 | 13.2784 | 10.9366 | 8.4611 | 15.1366 | 15.1641 | 15.1784 | 15.1386 | 15.0611 | 14.859 | 14.6407 | 14.3315 | 13.8131 | 11.9274 | 10.0723 | 8.9662
COWLEY GSP | YARNTON BSP | CHIPPING NORTON PRIMARY | MINIMUM HEADROOM | SP 31382 26792 | NO | YES | 2.666 | 3.3729 | 3.3872 | 3.1821 | 3.1117 | 2.7994 | 2.3566 | 1.7657 | 1.1494 | 0.56778 | -0.72406 | -1.3169 | -1.5975 | 5.5897 | 5.5591 | 5.305 | 5.1948 | 4.8846 | 4.4816 | 3.9744 | 3.452 | 2.9632 | 1.6438 | 1.0489 | -0.64702 | 4.454 | 4.4601 | 4.2203 | 4.1499 | 3.8642 | 3.4611 | 2.9203 | 2.3479 | 1.8101 | 0.47951 | -0.09498 | -0.33376
|  | CHIPPING NORTON PRIMARY | EE |  |  |  |  | 3.379 | 3.4137 | 3.2596 | 3.2504 | 3.1178 | 2.7453 | 2.2545 | 1.7361 | 1.2627 | -0.11794 | -0.77814 | -1.1271 | 5.5938 | 5.5734 | 5.3428 | 5.2683 | 5.0969 | 4.7203 | 4.2826 | 3.8091 | 3.3683 | 1.8458 | 1.0489 | 0.44176 | 4.4571 | 4.4785 | 4.2754 | 4.253 | 4.1183 | 3.7611 | 3.3091 | 2.8071 | 2.3428 | 0.91318 | 0.2489 | -0.082735
|  | CHIPPING NORTON PRIMARY | HT |  |  |  |  | 3.3729 | 3.3872 | 3.1821 | 3.1117 | 2.7994 | 2.3566 | 1.7657 | 1.1494 | 0.56778 | -0.72406 | -1.3169 | -1.5975 | 5.5897 | 5.5591 | 5.305 | 5.1948 | 4.8846 | 4.4816 | 3.9744 | 3.452 | 2.9632 | 1.6438 | 1.0938 | 0.87645 | 4.454 | 4.4601 | 4.2203 | 4.1499 | 3.8642 | 3.4611 | 2.9203 | 2.3479 | 1.8101 | 0.47951 | -0.09498 | -0.33376
|  | CHIPPING NORTON PRIMARY | HE |  |  |  |  | 3.381 | 3.4137 | 3.2596 | 3.2504 | 3.1168 | 2.7372 | 2.2392 | 1.7341 | 1.2525 | 0.10961 | -0.43733 | -0.79141 | 5.5938 | 5.5744 | 5.3448 | 5.2683 | 5.0928 | 4.7091 | 4.2652 | 3.803 | 3.3642 | 2.0734 | 1.3958 | 0.73257 | 4.4591 | 4.4795 | 4.2764 | 4.252 | 4.1162 | 3.7499 | 3.2928 | 2.8009 | 2.3397 | 1.1693 | 0.64278 | 0.31318
|  | CHIPPING NORTON PRIMARY | FB |  |  |  |  | 3.4902 | 3.5372 | 3.5749 | 3.5974 | 3.5668 | 3.4219 | 3.0484 | 2.7249 | 2.3831 | 1.2994 | 0.36676 | -0.28733 | 5.6775 | 5.6469 | 5.6193 | 5.5795 | 5.4877 | 5.3091 | 4.9356 | 4.6275 | 4.2948 | 2.8295 | 1.1764 | -0.64702 | 4.5642 | 4.5999 | 4.6264 | 4.6418 | 4.6254 | 4.5091 | 4.154 | 3.8887 | 3.5928 | 2.454 | 1.4428 | 0.72849
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE PRIMARY | MINIMUM HEADROOM | SU 80226 89155 | NO | NO | 0.863 | 3.749 | 3.7561 | 3.7439 | 3.5092 | 3.3908 | 3.1429 | 2.952 | 2.7745 | 2.5694 | 1.8459 | 1.2704 | 0.97551 | 4.0668 | 4.0577 | 4.026 | 3.7791 | 3.6413 | 3.4566 | 3.3332 | 3.2077 | 3.0515 | 2.4332 | 2.1117 | 1.9505 | 3.4643 | 3.4694 | 3.452 | 3.2133 | 3.0949 | 2.9041 | 2.7561 | 2.6102 | 2.4327 | 1.7643 | 1.3449 | 1.1878
|  | CHISBRIDGE PRIMARY | EE |  |  |  |  | 3.749 | 3.7561 | 3.7602 | 3.5194 | 3.4276 | 3.1898 | 3.0082 | 2.8276 | 2.6245 | 1.8755 | 1.3235 | 1.0745 | 4.0668 | 4.0577 | 4.0464 | 3.7842 | 3.6842 | 3.4934 | 3.3597 | 3.2403 | 3.0923 | 2.4699 | 2.1117 | 1.9505 | 3.4643 | 3.4694 | 3.4694 | 3.2194 | 3.1327 | 2.9408 | 2.7888 | 2.6367 | 2.4643 | 1.8082 | 1.3796 | 1.2204
|  | CHISBRIDGE PRIMARY | HT |  |  |  |  | 3.7622 | 3.7755 | 3.7531 | 3.5092 | 3.3908 | 3.1561 | 2.9908 | 2.8041 | 2.6 | 1.8459 | 1.2704 | 0.97551 | 4.0699 | 4.0587 | 4.026 | 3.7791 | 3.6413 | 3.4566 | 3.3332 | 3.2077 | 3.0515 | 2.4332 | 2.1587 | 2.123 | 3.4745 | 3.4806 | 3.4561 | 3.2214 | 3.0949 | 2.9041 | 2.7653 | 2.6102 | 2.4327 | 1.7643 | 1.3449 | 1.1878
|  | CHISBRIDGE PRIMARY | HE |  |  |  |  | 3.7541 | 3.7592 | 3.7439 | 3.5102 | 3.4031 | 3.1429 | 2.952 | 2.7745 | 2.5694 | 2.0429 | 1.6898 | 1.4541 | 4.0689 | 4.0577 | 4.0291 | 3.7852 | 3.6821 | 3.4852 | 3.3495 | 3.2485 | 3.1087 | 2.6005 | 2.473 | 2.2883 | 3.4684 | 3.4724 | 3.452 | 3.2133 | 3.1163 | 2.9092 | 2.7561 | 2.6133 | 2.4418 | 1.9571 | 1.7316 | 1.5704
|  | CHISBRIDGE PRIMARY | FB |  |  |  |  | 3.8255 | 3.8592 | 3.8878 | 3.9051 | 3.9031 | 3.8959 | 3.8745 | 3.6357 | 3.5908 | 3.1337 | 2.7173 | 2.3582 | 4.1138 | 4.125 | 4.124 | 4.1199 | 4.0974 | 4.0832 | 4.0485 | 3.776 | 3.7168 | 3.2128 | 2.6954 | 2.0985 | 3.5337 | 3.5582 | 3.5776 | 3.5929 | 3.5888 | 3.5796 | 3.5602 | 3.3051 | 3.2592 | 2.8388 | 2.4551 | 2.1041
MINETY GSP | TOOTHILL BSP | CHISLEDON PRIMARY | MINIMUM HEADROOM | SU 18894 79934 | NO | NO | 0.619 | 10.326 | 9.9515 | 8.9628 | 7.6872 | 6.4587 | 4.974 | 2.8454 | 0.7301 | -1.3515 | -7.5434 | -9.4964 | -10.1903 | 10.8837 | 10.7133 | 10.3867 | 9.8837 | 9.2786 | 8.551 | 7.5571 | 6.3582 | 5.249 | 1.4898 | 0.065306 | -0.40204 | 10.6194 | 10.3704 | 9.7143 | 8.7949 | 7.9031 | 6.8102 | 5.1939 | 3.5112 | 1.8939 | -3.1796 | -4.9357 | -5.4735
|  | CHISLEDON PRIMARY | EE |  |  |  |  | 10.3291 | 9.9546 | 8.973 | 7.6923 | 6.5352 | 5.1097 | 2.8454 | 0.7301 | -1.3515 | -7.5434 | -9.4964 | -10.1903 | 10.8857 | 10.7163 | 10.3898 | 9.8878 | 9.449 | 8.8286 | 7.5571 | 6.3582 | 5.249 | 1.4898 | 0.065306 | -0.40204 | 10.6224 | 10.3745 | 9.7194 | 8.8 | 8.0102 | 6.9898 | 5.1939 | 3.5112 | 1.8939 | -3.1796 | -4.9357 | -5.4735
|  | CHISLEDON PRIMARY | HT |  |  |  |  | 10.3393 | 9.973 | 9.026 | 7.7872 | 6.4587 | 4.974 | 3.0811 | 1.0893 | -0.83622 | -6.3658 | -8.2434 | -8.9566 | 10.8888 | 10.7173 | 10.3949 | 9.8898 | 9.2786 | 8.551 | 7.6929 | 6.5602 | 5.5429 | 2.6908 | 1.651 | 1.4408 | 10.6276 | 10.3816 | 9.75 | 8.849 | 7.9031 | 6.8102 | 5.4551 | 3.8806 | 2.4031 | -1.8816 | -3.4031 | -3.8714
|  | CHISLEDON PRIMARY | HE |  |  |  |  | 10.326 | 9.9515 | 8.9628 | 7.6872 | 6.5607 | 5.0168 | 3.0107 | 1.0107 | -0.95765 | -5.9332 | -7.0974 | -7.5046 | 10.8837 | 10.7133 | 10.3867 | 9.8837 | 9.4694 | 8.8102 | 7.9745 | 7.0153 | 6.1439 | 3.6704 | 3.0969 | 2.7235 | 10.6194 | 10.3704 | 9.7143 | 8.7949 | 8.0327 | 6.9337 | 5.5235 | 4.0459 | 2.6316 | -1.0755 | -1.9398 | -2.2286
|  | CHISLEDON PRIMARY | FB |  |  |  |  | 10.4679 | 10.1944 | 9.3913 | 8.4526 | 7.5434 | 6.6566 | 5.3015 | 4.0219 | 2.6107 | -2.1587 | -3.2852 | -3.7138 | 10.9776 | 10.8214 | 10.5296 | 10.2245 | 9.8847 | 9.5286 | 8.9245 | 8.3235 | 7.6714 | 5.0806 | 4.0684 | 3.202 | 10.75 | 10.5643 | 10.0276 | 9.4051 | 8.8 | 8.1918 | 7.252 | 6.35 | 5.2929 | 1.7357 | 0.78163 | 0.36939
FLEET-BRAMLEY GSP | BRACKNELL BSP | CHOBHAM PRIMARY | MINIMUM HEADROOM | SU 97173 63223 | NO | NO | 4.905 | 10.0463 | 9.98 | 10.03 | 9.9147 | 9.7188 | 9.3535 | 8.8943 | 8.2933 | 7.6637 | 5.9933 | 5.3922 | 5.5688 | 12.6314 | 12.3906 | 12.3569 | 12.1324 | 11.8386 | 11.3906 | 10.8273 | 10.2151 | 9.5539 | 7.7243 | 6.7896 | 4.808 | 10.929 | 10.7494 | 10.7453 | 10.5463 | 10.2596 | 9.8106 | 9.2392 | 8.6137 | 7.9382 | 6.1433 | 5.5688 | 5.7749
|  | CHOBHAM PRIMARY | EE |  |  |  |  | 10.0463 | 9.982 | 10.0484 | 9.9596 | 9.8218 | 9.5504 | 9.2167 | 8.7463 | 8.231 | 6.5576 | 5.8565 | 5.8402 | 12.6324 | 12.3947 | 12.3661 | 12.159 | 11.8906 | 11.4876 | 11.0263 | 10.4692 | 9.8845 | 7.808 | 6.7896 | 6.1845 | 10.93 | 10.7504 | 10.7616 | 10.579 | 10.3361 | 9.9494 | 9.5065 | 8.9637 | 8.3871 | 6.5984 | 5.9269 | 5.9361
|  | CHOBHAM PRIMARY | HT |  |  |  |  | 10.0463 | 9.98 | 10.03 | 9.9147 | 9.7188 | 9.3535 | 8.8943 | 8.2933 | 7.6637 | 5.9933 | 5.3922 | 5.5688 | 12.6314 | 12.3906 | 12.3569 | 12.1324 | 11.8386 | 11.3906 | 10.8273 | 10.2151 | 9.5539 | 7.7243 | 7.0886 | 7.161 | 10.93 | 10.7494 | 10.7453 | 10.5463 | 10.2596 | 9.8106 | 9.2392 | 8.6137 | 7.9382 | 6.1433 | 5.5688 | 5.7749
|  | CHOBHAM PRIMARY | HE |  |  |  |  | 10.0484 | 9.9841 | 10.0514 | 9.9586 | 9.8371 | 9.5494 | 9.2351 | 8.7667 | 8.2708 | 7.0494 | 6.4443 | 6.1861 | 12.6324 | 12.3937 | 12.3671 | 12.1569 | 11.9141 | 11.4784 | 11.0345 | 10.4865 | 9.909 | 8.2549 | 7.2916 | 6.4365 | 10.929 | 10.7494 | 10.7627 | 10.58 | 10.3616 | 9.9422 | 9.5218 | 8.9882 | 8.4218 | 7.082 | 6.5014 | 6.2606
|  | CHOBHAM PRIMARY | FB |  |  |  |  | 10.1953 | 10.3147 | 10.4147 | 10.3678 | 10.4484 | 10.378 | 10.2994 | 10.1861 | 10.0708 | 9.2004 | 7.9616 | 7.0147 | 12.7447 | 12.7447 | 12.7386 | 12.5018 | 12.4539 | 12.2294 | 11.9957 | 11.7202 | 11.4518 | 9.6559 | 7.3539 | 4.808 | 11.0861 | 11.1729 | 11.2473 | 11.0871 | 11.13 | 10.9973 | 10.8678 | 10.6851 | 10.5147 | 9.3331 | 7.9871 | 7.0014
COWLEY GSP | DRAYTON BSP | CHOLSEY PRIMARY | MINIMUM HEADROOM | SU 58223 84685 | NO | YES | 0.653 | 8.2393 | 8.1434 | 7.8423 | 7.6546 | 7.3974 | 7.0036 | 6.1893 | 4.4505 | 1.1434 | -1.8913 | -5.4393 | -9.5383 | 9.5245 | 9.4643 | 9.1582 | 9.0531 | 8.8888 | 8.6388 | 7.8224 | 5.95 | 2.0531 | -1.4286 | -5.4633 | -10.5867 | 9.0949 | 9.0153 | 8.6694 | 8.5071 | 8.3122 | 7.9694 | 7.1112 | 5.1173 | 1.1592 | -2.2735 | -6.2878 | -11.1755
|  | CHOLSEY PRIMARY | EE |  |  |  |  | 8.2474 | 8.2454 | 7.9168 | 7.7015 | 7.3974 | 7.0464 | 6.525 | 5.774 | 4.725 | 2.024 | -2.9321 | -4.8515 | 9.5449 | 9.5082 | 9.2092 | 9.1133 | 8.9408 | 8.6816 | 8.2469 | 7.5408 | 6.451 | 3.6724 | -2.0592 | -4.3418 | 9.1 | 9.0847 | 8.7316 | 8.5633 | 8.3122 | 7.9969 | 7.4939 | 6.7276 | 5.5816 | 2.748 | -2.9857 | -5.0857
|  | CHOLSEY PRIMARY | HT |  |  |  |  | 8.2393 | 8.1434 | 7.8423 | 7.6546 | 7.5015 | 7.176 | 6.3883 | 5.5383 | 3.8128 | 0.68929 | -4.0158 | -7.3607 | 9.5245 | 9.4643 | 9.1582 | 9.0531 | 8.8888 | 8.6388 | 7.8224 | 6.9418 | 4.9796 | 1.8806 | -3.2449 | -6.8408 | 9.0949 | 9.0153 | 8.6694 | 8.5071 | 8.3173 | 8.0194 | 7.1714 | 6.251 | 4.2316 | 0.93061 | -4.4051 | -8.1551
|  | CHOLSEY PRIMARY | HE |  |  |  |  | 8.2474 | 8.2474 | 7.9587 | 7.777 | 7.5087 | 7.0036 | 6.1893 | 4.4505 | 1.1434 | -1.8913 | -5.4393 | -9.5383 | 9.5449 | 9.5082 | 9.2184 | 9.1337 | 8.9673 | 8.6684 | 7.8847 | 5.95 | 2.0531 | -1.4286 | -5.4633 | -10.5867 | 9.099 | 9.0837 | 8.7531 | 8.6041 | 8.3735 | 7.9694 | 7.1112 | 5.1173 | 1.1592 | -2.2735 | -6.2878 | -11.1755
|  | CHOLSEY PRIMARY | FB |  |  |  |  | 8.373 | 8.423 | 8.4689 | 8.4138 | 8.3332 | 8.2087 | 7.8617 | 7.6301 | 7.1026 | 5.2526 | 2.8097 | 0.74541 | 9.6286 | 9.6122 | 9.5929 | 9.5398 | 9.4592 | 9.3408 | 8.9367 | 8.6071 | 7.9 | 5.5194 | 2.2908 | -0.96122 | 9.1806 | 9.199 | 9.2112 | 9.1653 | 9.1082 | 9.0204 | 8.6224 | 8.3378 | 7.6735 | 5.549 | 2.7878 | 0.38571
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH PRIMARY | MINIMUM HEADROOM | SZ 15698 93141 | NO | NO | 5.496 | 5.5508 | 5.3916 | 4.912 | 4.509 | 3.9773 | 2.6304 | 1.0141 | -0.71247 | -2.4206 | -8.389 | -12.5512 | -14.3625 | 10.2753 | 9.9488 | 9.5273 | 9.1865 | 8.6355 | 7.8539 | 6.8692 | 5.7855 | 4.6732 | 1.2508 | -1.3941 | -6.8829 | 7.6365 | 7.2345 | 6.6212 | 6.0967 | 5.3253 | 4.1263 | 2.7365 | 1.2365 | -0.29104 | -5.1808 | -8.2706 | -9.3063
|  | CHRISTCHURCH PRIMARY | EE |  |  |  |  | 5.5712 | 5.461 | 4.9916 | 4.7304 | 4.3355 | 3.359 | 2.012 | 0.55998 | -0.86961 | -6.1012 | -10.0492 | -12.2543 | 10.2916 | 9.9886 | 9.5875 | 9.3345 | 8.8641 | 8.1824 | 7.3457 | 6.3794 | 5.3947 | 1.3181 | -1.3941 | -3.5563 | 7.6528 | 7.2784 | 6.6773 | 6.312 | 5.6865 | 4.659 | 3.4896 | 2.1804 | 0.85896 | -3.6941 | -6.7665 | -8.3165
|  | CHRISTCHURCH PRIMARY | HT |  |  |  |  | 5.5508 | 5.3916 | 4.912 | 4.509 | 3.9773 | 2.6304 | 1.0141 | -0.71247 | -2.4206 | -8.389 | -12.5512 | -14.3625 | 10.2753 | 9.9488 | 9.5273 | 9.1865 | 8.6355 | 7.8539 | 6.8692 | 5.7855 | 4.6732 | 1.2508 | -0.45532 | -0.85328 | 7.6365 | 7.2345 | 6.6212 | 6.0967 | 5.3253 | 4.1263 | 2.7365 | 1.2365 | -0.29104 | -5.1808 | -8.2706 | -9.3063
|  | CHRISTCHURCH PRIMARY | HE |  |  |  |  | 5.5743 | 5.4753 | 5.012 | 4.712 | 4.2773 | 3.4049 | 2.1447 | 0.80896 | -0.52981 | -4.6808 | -8.0359 | -9.6768 | 10.2886 | 10.01 | 9.6181 | 9.3386 | 8.8539 | 8.2079 | 7.3498 | 6.4171 | 5.4314 | 2.0335 | -0.52675 | -2.7074 | 7.6559 | 7.3181 | 6.7365 | 6.311 | 5.6406 | 4.6988 | 3.5569 | 2.3355 | 1.062 | -2.4972 | -5.0625 | -6.2268
|  | CHRISTCHURCH PRIMARY | FB |  |  |  |  | 5.7661 | 5.81 | 5.6671 | 5.7069 | 5.6906 | 5.5875 | 5.4467 | 5.2661 | 5.0743 | 3.2671 | -0.22981 | -2.74 | 10.3937 | 10.1263 | 9.9396 | 9.8273 | 9.6426 | 9.2508 | 8.8161 | 8.3314 | 7.8294 | 4.1243 | -1.138 | -6.8829 | 7.9171 | 7.6896 | 7.5079 | 7.4967 | 7.4518 | 7.2243 | 6.959 | 6.6069 | 6.2743 | 3.6681 | 0.22223 | -2.1237
LALEHAM GSP | EAST BEDFONT BSP | CHURCH ROAD PRIMARY | MINIMUM HEADROOM | TQ 06820 71722 | NO | NO | 1.681 | 3.8089 | 3.8793 | 3.8681 | 3.661 | 3.4232 | 3.0079 | 2.5487 | 2.0059 | 1.4895 | -0.48393 | -1.936 | -2.2105 | 7.8378 | 7.7918 | 7.6551 | 7.2408 | 6.8867 | 6.3806 | 5.8112 | 5.1582 | 4.5347 | 1.9918 | -1.0306 | -5.7806 | 5.7908 | 5.8306 | 5.7582 | 5.3469 | 5.0133 | 4.5265 | 3.9878 | 3.3643 | 2.7878 | 0.62755 | -0.95816 | -1.1714
|  | CHURCH ROAD PRIMARY | EE |  |  |  |  | 3.8089 | 3.9589 | 3.8875 | 3.7344 | 3.5426 | 3.2069 | 2.7814 | 2.3018 | 1.8171 | -0.29413 | -1.936 | -2.2105 | 7.8408 | 7.8663 | 7.6806 | 7.2888 | 6.948 | 6.501 | 5.9439 | 5.3429 | 4.7102 | 1.9918 | -0.1398 | -1.6245 | 5.7908 | 5.8949 | 5.7724 | 5.401 | 5.1 | 4.6847 | 4.1633 | 3.601 | 3.0173 | 0.71531 | -0.95816 | -1.1714
|  | CHURCH ROAD PRIMARY | HT |  |  |  |  | 3.813 | 3.8793 | 3.8681 | 3.661 | 3.4232 | 3.0079 | 2.5487 | 2.0059 | 1.4895 | -0.48393 | -1.8696 | -1.9727 | 7.8388 | 7.7918 | 7.6551 | 7.2408 | 6.8867 | 6.3806 | 5.8112 | 5.1582 | 4.5347 | 2.4633 | 1.3204 | 1.0867 | 5.7969 | 5.8306 | 5.7582 | 5.3469 | 5.0133 | 4.5265 | 3.9878 | 3.3643 | 2.7878 | 0.62755 | -0.78163 | -0.86531
|  | CHURCH ROAD PRIMARY | HE |  |  |  |  | 3.813 | 3.9753 | 3.913 | 3.7457 | 3.5355 | 3.211 | 2.8018 | 2.3487 | 1.8793 | 0.23648 | -0.74719 | -1.1441 | 7.8378 | 7.8643 | 7.6765 | 7.2816 | 6.9276 | 6.4776 | 5.9276 | 5.3367 | 4.7071 | 2.2204 | 0.45 | -1.3541 | 5.798 | 5.9051 | 5.7888 | 5.4102 | 5.0806 | 4.6735 | 4.1694 | 3.6327 | 3.0633 | 1.2357 | 0.2602 | -0.11224
|  | CHURCH ROAD PRIMARY | FB |  |  |  |  | 4.0253 | 4.1732 | 4.2936 | 4.3599 | 4.4253 | 4.411 | 4.3681 | 4.2059 | 4.0375 | 2.7773 | 0.79158 | -0.50536 | 7.9918 | 7.9398 | 7.8755 | 7.7847 | 7.6265 | 7.348 | 7.0265 | 6.5133 | 6.0316 | 3.1469 | -1.0306 | -5.7806 | 6.0459 | 6.1337 | 6.2061 | 6.2541 | 6.2684 | 6.2071 | 6.1082 | 5.7745 | 5.4949 | 3.902 | 1.7571 | 0.43673
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN PRIMARY | MINIMUM HEADROOM | SP 02761 00827 | NO | NO | 11.973 | -5.1725 | -5.3256 | 12.604 | 12.0713 | 11.5458 | 10.7377 | 9.1999 | 6.5254 | 4.4234 | -2.3542 | -10.9133 | -17.2531 | 0.65298 | 0.5142 | 16.2846 | 15.9387 | 15.5673 | 15.0591 | 13.6326 | 10.5734 | 8.6081 | 2.552 | -6.3307 | -12.5929 | -2.5072 | -2.6164 | 14.4111 | 14.0224 | 13.6336 | 13.0703 | 11.602 | 8.5856 | 6.5622 | -0.20824 | -9.7072 | -16.5042
|  | CIRENCESTER TOWN PRIMARY | EE |  |  |  |  | -5.1725 | -5.3236 | 12.6275 | 12.1601 | 11.7122 | 11.0234 | 10.0479 | 8.7193 | 6.8938 | 1.1081 | -7.9368 | -11.9664 | 0.65298 | 0.52747 | 16.3071 | 16.005 | 15.6387 | 15.254 | 14.4591 | 13.1969 | 11.3418 | 5.8489 | -4.0491 | -8.2093 | -2.5072 | -2.6093 | 14.4346 | 14.0969 | 13.7632 | 13.2999 | 12.4897 | 11.256 | 9.3856 | 3.6264 | -6.5225 | -10.594
|  | CIRENCESTER TOWN PRIMARY | HT |  |  |  |  | -5.1654 | -5.3256 | 12.604 | 12.0713 | 11.5458 | 10.7377 | 9.1999 | 7.5346 | 4.4234 | -2.3542 | -10.9133 | -17.2531 | 0.65298 | 0.5142 | 16.2846 | 15.9387 | 15.5673 | 15.0591 | 13.6326 | 11.9969 | 8.6081 | 2.552 | -6.3307 | -12.5929 | -2.5042 | -2.6164 | 14.4111 | 14.0224 | 13.6336 | 13.0703 | 11.602 | 9.9928 | 6.5622 | -0.20824 | -9.7072 | -16.5042
|  | CIRENCESTER TOWN PRIMARY | HE |  |  |  |  | -5.1582 | -5.296 | 12.6703 | 12.2081 | 11.7111 | 10.9805 | 9.5254 | 6.5254 | 5.7336 | -0.69498 | -7.1225 | -14.4572 | 0.66012 | 0.54278 | 16.3305 | 16.0346 | 15.6897 | 15.2499 | 13.8989 | 10.5734 | 10.0407 | 3.5111 | -3.4736 | -12.2062 | -2.496 | -2.5889 | 14.4662 | 14.1367 | 13.7744 | 13.2795 | 11.8887 | 8.5856 | 8.0316 | 1.3856 | -5.7542 | -14.2174
|  | CIRENCESTER TOWN PRIMARY | FB |  |  |  |  | -5.044 | -5.1113 | 13.0193 | 12.7764 | 12.4683 | 12.2264 | 11.7989 | 11.2285 | 10.2479 | 6.9173 | 2.2724 | -1.3582 | 0.78053 | 0.68767 | 16.654 | 16.4918 | 16.1101 | 15.8856 | 15.4285 | 14.7407 | 13.5754 | 9.4632 | 3.4979 | -2.1531 | -2.3838 | -2.447 | 14.7397 | 14.5632 | 14.352 | 14.1785 | 13.7693 | 13.206 | 12.1213 | 8.6897 | 3.8326 | -0.36335
IVER 132KV GSP | CIPPENHAM BSP | CLARENCE ROAD PRIMARY | MINIMUM HEADROOM | SU 95654 76652 | NO | YES | 12.271 | 14.8652 | 14.9539 | 14.8162 | 14.4897 | 14.0835 | 13.4386 | 12.4621 | 11.3682 | 10.3182 | 6.5723 | 4.1315 | 3.2407 | 21.9407 | 21.8611 | 21.6376 | 21.3141 | 20.9223 | 20.2631 | 19.1907 | 18.0539 | 16.9437 | 12.9182 | 9.2468 | 2.4744 | 15.3356 | 15.2754 | 15.0488 | 14.6295 | 14.1274 | 13.3968 | 12.3295 | 11.2019 | 10.1111 | 6.007 | 3.6835 | 2.7478
|  | CLARENCE ROAD PRIMARY | EE |  |  |  |  | 14.8652 | 14.9539 | 14.8662 | 14.6978 | 14.3039 | 13.7856 | 12.9386 | 12.2233 | 11.5519 | 7.8121 | 4.7478 | 3.2407 | 21.9458 | 21.8682 | 21.6774 | 21.4131 | 21.0182 | 20.4876 | 19.4641 | 18.5478 | 17.6519 | 12.9182 | 9.4325 | 6.5499 | 15.3356 | 15.2754 | 15.0764 | 14.7764 | 14.2713 | 13.6754 | 12.6723 | 11.8264 | 11.0009 | 6.9029 | 4.0019 | 2.7478
|  | CLARENCE ROAD PRIMARY | HT |  |  |  |  | 14.8723 | 14.9611 | 14.8162 | 14.4897 | 14.0835 | 13.4386 | 12.4621 | 11.3682 | 10.3182 | 6.5723 | 4.1315 | 3.5774 | 21.9407 | 21.8611 | 21.6376 | 21.3141 | 20.9223 | 20.2631 | 19.1907 | 18.0539 | 16.9437 | 12.958 | 10.8886 | 10.2111 | 15.3448 | 15.2876 | 15.0488 | 14.6295 | 14.1274 | 13.3968 | 12.3295 | 11.2019 | 10.1111 | 6.007 | 3.6835 | 3.2295
|  | CLARENCE ROAD PRIMARY | HE |  |  |  |  | 14.8795 | 14.9835 | 14.9111 | 14.7182 | 14.4274 | 13.9376 | 13.1203 | 12.355 | 11.6978 | 8.9356 | 6.7621 | 5.7499 | 21.9417 | 21.8641 | 21.6713 | 21.4009 | 21.055 | 20.5529 | 19.5182 | 18.5427 | 17.6437 | 13.4009 | 10.2682 | 7.4927 | 15.3488 | 15.2999 | 15.1141 | 14.7937 | 14.3478 | 13.7723 | 12.7937 | 11.8948 | 11.0835 | 7.9029 | 5.8407 | 4.9713
|  | CLARENCE ROAD PRIMARY | FB |  |  |  |  | 15.1723 | 15.4274 | 15.5968 | 15.6764 | 15.6039 | 15.4519 | 15.1846 | 14.9784 | 14.7386 | 13.0274 | 9.3713 | 6.9999 | 22.1295 | 22.158 | 22.1233 | 21.9825 | 21.656 | 21.1897 | 20.6141 | 20.0825 | 19.4999 | 15.6244 | 9.2468 | 2.4744 | 15.6917 | 15.8223 | 15.9192 | 15.9264 | 15.8213 | 15.6141 | 15.2927 | 15.0244 | 14.7019 | 12.4692 | 8.708 | 6.3917
MELKSHAM GSP | CHIPPENHAM BSP | COCKLEBURY PRIMARY | MINIMUM HEADROOM | ST 92447 73890 | NO | YES | 6.767 | 15.1036 | 14.7005 | 14.2076 | 13.7219 | 13.1893 | 12.1821 | 11.025 | 9.8525 | 8.5964 | 4.425 | 1.8648 | 0.69131 | 20.4923 | 20.1076 | 19.8546 | 19.5413 | 19.0995 | 18.524 | 17.7444 | 17.0484 | 16.3178 | 13.6158 | 11.9056 | 8.9474 | 18.5372 | 18.0362 | 17.625 | 17.2178 | 16.7097 | 15.8689 | 14.826 | 13.8382 | 12.8158 | 9.2148 | 7.2087 | 6.525
|  | COCKLEBURY PRIMARY | EE |  |  |  |  | 15.1036 | 14.7138 | 14.2076 | 13.7536 | 13.277 | 12.3617 | 11.2801 | 10.227 | 9.1729 | 5.3546 | 2.8209 | 1.4372 | 20.4923 | 20.1189 | 19.8627 | 19.5729 | 19.1158 | 18.6505 | 17.8648 | 17.2311 | 16.5658 | 13.6158 | 11.9056 | 10.6668 | 18.5372 | 18.0423 | 17.625 | 17.2617 | 16.775 | 16.0617 | 15.0484 | 14.1648 | 13.2556 | 9.824 | 7.778 | 6.7729
|  | COCKLEBURY PRIMARY | HT |  |  |  |  | 15.1036 | 14.7178 | 14.2229 | 13.7219 | 13.1893 | 12.1821 | 11.025 | 9.8525 | 8.5964 | 4.425 | 1.8648 | 0.69131 | 20.4923 | 20.1178 | 19.8546 | 19.5413 | 19.0995 | 18.524 | 17.7444 | 17.0484 | 16.3178 | 13.6944 | 12.5219 | 12.2729 | 18.5413 | 18.0505 | 17.627 | 17.2178 | 16.7097 | 15.8689 | 14.826 | 13.8382 | 12.8158 | 9.2148 | 7.2087 | 6.525
|  | COCKLEBURY PRIMARY | HE |  |  |  |  | 15.1046 | 14.7005 | 14.2168 | 13.7515 | 13.2597 | 12.3882 | 11.3464 | 10.3352 | 9.3301 | 6.0474 | 3.9627 | 2.9464 | 20.4933 | 20.1076 | 19.8648 | 19.5678 | 19.1321 | 18.6495 | 17.8556 | 17.2025 | 16.5393 | 13.9352 | 12.478 | 11.3913 | 18.5423 | 18.0362 | 17.6331 | 17.2617 | 16.7831 | 16.078 | 15.0831 | 14.2046 | 13.3219 | 10.4138 | 8.8209 | 8.1372
|  | COCKLEBURY PRIMARY | FB |  |  |  |  | 15.2423 | 15.0199 | 14.7178 | 14.6331 | 14.4076 | 14.0087 | 13.627 | 13.2117 | 12.7933 | 10.6903 | 8.3862 | 7.0342 | 20.674 | 20.3995 | 20.1382 | 20.074 | 19.8117 | 19.4117 | 19.0393 | 18.5913 | 18.1515 | 15.4229 | 12.1729 | 8.9474 | 18.8127 | 18.5056 | 18.1729 | 18.1464 | 17.9474 | 17.577 | 17.225 | 16.8036 | 16.3913 | 14.1291 | 11.7658 | 10.4525
MELKSHAM GSP | FROME BSP | CODFORD PRIMARY | MINIMUM HEADROOM | ST 97372 39559 | YES | NO | 1.735 | 1.4383 | 1.4393 | 1.425 | 1.3811 | 1.3423 | 1.2852 | 1.0872 | 0.90459 | 0.78418 | 0.49235 | 0.33929 | 0.13827 | 0.53776 | 0.54082 | 0.52653 | 0.51224 | 0.49898 | 0.44388 | 0.26429 | 0.087755 | 0.0071429 | -0.24694 | -0.29592 | -0.27041 | 1.2 | 1.2061 | 1.1959 | 1.1735 | 1.1469 | 1.1 | 0.95714 | 0.77347 | 0.67653 | 0.3949 | 0.27143 | 0.20816
|  | CODFORD PRIMARY | EE |  |  |  |  | 1.4393 | 1.4423 | 1.425 | 1.3903 | 1.3505 | 1.2954 | 1.1036 | 0.96684 | 0.80867 | 0.49235 | 0.33929 | 0.20357 | 0.54082 | 0.54388 | 0.52653 | 0.51531 | 0.50306 | 0.44796 | 0.26735 | 0.15102 | 0.011224 | -0.24694 | -0.29592 | -0.27041 | 1.2 | 1.2092 | 1.1959 | 1.1786 | 1.1551 | 1.1112 | 0.96633 | 0.8398 | 0.6898 | 0.3949 | 0.27143 | 0.20816
|  | CODFORD PRIMARY | HT |  |  |  |  | 1.4383 | 1.4393 | 1.4301 | 1.3832 | 1.3423 | 1.2903 | 1.1036 | 0.90459 | 0.80765 | 0.54133 | 0.36888 | 0.13827 | 0.53776 | 0.54082 | 0.53469 | 0.51224 | 0.49898 | 0.44388 | 0.26939 | 0.087755 | 0.011224 | -0.21531 | -0.25204 | -0.19082 | 1.2 | 1.2061 | 1.201 | 1.1755 | 1.15 | 1.1031 | 0.96429 | 0.77347 | 0.68776 | 0.43061 | 0.29082 | 0.21735
|  | CODFORD PRIMARY | HE |  |  |  |  | 1.4383 | 1.4403 | 1.4321 | 1.3811 | 1.3566 | 1.2852 | 1.0872 | 0.94337 | 0.78418 | 0.70561 | 0.47194 | 0.29847 | 0.53776 | 0.54388 | 0.53367 | 0.51429 | 0.50204 | 0.44898 | 0.26429 | 0.14286 | 0.0071429 | -0.05 | -0.11327 | -0.12245 | 1.2 | 1.2082 | 1.202 | 1.1735 | 1.1469 | 1.1 | 0.95714 | 0.82449 | 0.67653 | 0.60408 | 0.45408 | 0.35918
|  | CODFORD PRIMARY | FB |  |  |  |  | 1.4658 | 1.4811 | 1.4913 | 1.4872 | 1.475 | 1.4617 | 1.4362 | 1.423 | 1.3934 | 1.223 | 1.0832 | 0.79439 | 0.5602 | 0.56633 | 0.56735 | 0.56531 | 0.55714 | 0.54286 | 0.52551 | 0.51122 | 0.48776 | 0.30306 | 0.2102 | -0.15306 | 1.2245 | 1.2388 | 1.249 | 1.251 | 1.2469 | 1.2388 | 1.2204 | 1.2082 | 1.1857 | 1.0418 | 0.95 | 0.61633
IVER 132KV GSP | DENHAM BSP | COKES LANE PRIMARY | MINIMUM HEADROOM | SU 99240 97483 | NO | YES | 0.653 | 10.1518 | 10.0824 | 9.9548 | 9.8681 | 9.8242 | 9.5089 | 9.1538 | 8.7875 | 8.4375 | 7.2834 | 6.4089 | 6.0253 | 11.4561 | 11.401 | 11.3327 | 11.2735 | 11.2653 | 11.1082 | 10.9092 | 10.6959 | 10.5153 | 9.8837 | 9.3082 | 8.1745 | 10.7122 | 10.6459 | 10.5673 | 10.4959 | 10.4745 | 10.2418 | 9.9745 | 9.6908 | 9.4255 | 8.6153 | 8.1092 | 7.9622
|  | COKES LANE PRIMARY | EE |  |  |  |  | 10.1518 | 10.0824 | 9.9569 | 9.9018 | 9.9079 | 9.6273 | 9.2977 | 8.9375 | 8.5997 | 7.5885 | 6.7763 | 6.3875 | 11.4592 | 11.402 | 11.3459 | 11.2898 | 11.3 | 11.1602 | 10.9755 | 10.7755 | 10.6112 | 9.8867 | 9.3949 | 8.9776 | 10.7133 | 10.6459 | 10.5735 | 10.5194 | 10.5316 | 10.3265 | 10.0755 | 9.8031 | 9.552 | 8.8082 | 8.3133 | 8.1367
|  | COKES LANE PRIMARY | HT |  |  |  |  | 10.1538 | 10.0855 | 9.9548 | 9.8681 | 9.8242 | 9.5089 | 9.1538 | 8.7875 | 8.4375 | 7.2834 | 6.4089 | 6.0253 | 11.4561 | 11.401 | 11.3327 | 11.2735 | 11.2653 | 11.1082 | 10.9092 | 10.6959 | 10.5153 | 9.949 | 9.6898 | 9.6418 | 10.7133 | 10.648 | 10.5673 | 10.4959 | 10.4745 | 10.2418 | 9.9745 | 9.6908 | 9.4255 | 8.6153 | 8.1092 | 7.9622
|  | COKES LANE PRIMARY | HE |  |  |  |  | 10.1538 | 10.0834 | 9.9599 | 9.8895 | 9.8712 | 9.5651 | 9.2089 | 8.8283 | 8.464 | 7.5681 | 6.8232 | 6.5314 | 11.4571 | 11.401 | 11.3398 | 11.2867 | 11.2949 | 11.15 | 10.9694 | 10.7827 | 10.5969 | 9.8837 | 9.3714 | 8.8806 | 10.7122 | 10.6469 | 10.5724 | 10.5112 | 10.5112 | 10.2908 | 10.0286 | 9.7449 | 9.4776 | 8.7969 | 8.3235 | 8.1592
|  | COKES LANE PRIMARY | FB |  |  |  |  | 10.3089 | 10.2773 | 10.2497 | 10.2814 | 10.2824 | 10.2487 | 10.2804 | 10.2191 | 10.1528 | 9.7008 | 9.1997 | 9.0375 | 11.5459 | 11.5092 | 11.4684 | 11.4541 | 11.4082 | 11.3255 | 11.2929 | 11.1918 | 11.0755 | 10.3153 | 9.3082 | 8.1745 | 10.8582 | 10.8378 | 10.8071 | 10.8286 | 10.8398 | 10.8061 | 10.8224 | 10.7694 | 10.7112 | 10.2969 | 9.8592 | 9.7276
LOVEDEAN GSP | PORTSMOUTH BSP | COLLEGE PARK PRIMARY | MINIMUM HEADROOM | SU 65893 02686 | NO | YES | 0.626 | 4.4536 | 4.4536 | 4.3913 | 4.1985 | 3.9342 | 3.5107 | 3.0434 | 2.5189 | 2.0036 | -0.87398 | -2.8495 | -3.876 | 6.7765 | 6.7378 | 6.5367 | 6.4122 | 6.1276 | 5.7857 | 5.3959 | 4.8959 | 4.3929 | 1.95 | -1.7867 | -7.3908 | 5.7439 | 5.7327 | 5.5122 | 5.3776 | 5.0561 | 4.6643 | 4.2204 | 3.6673 | 3.1092 | 0.53673 | -0.96327 | -1.8204
|  | COLLEGE PARK PRIMARY | EE |  |  |  |  | 4.4536 | 4.4536 | 4.3913 | 4.2199 | 3.9719 | 3.5903 | 3.1536 | 2.6801 | 2.2015 | -0.089286 | -2.4964 | -3.824 | 6.7765 | 6.751 | 6.6378 | 6.4582 | 6.1612 | 5.8633 | 5.4949 | 5.0459 | 4.5684 | 1.95 | -0.36531 | -2.751 | 5.7439 | 5.7327 | 5.5929 | 5.4184 | 5.0918 | 4.7643 | 4.348 | 3.8622 | 3.3408 | 0.96531 | -0.84898 | -1.8204
|  | COLLEGE PARK PRIMARY | HT |  |  |  |  | 4.4719 | 4.4872 | 4.3954 | 4.1985 | 3.9342 | 3.5107 | 3.0434 | 2.5189 | 2.0036 | -0.87398 | -2.8495 | -3.876 | 6.7776 | 6.7469 | 6.5367 | 6.4122 | 6.1276 | 5.7857 | 5.3959 | 4.8959 | 4.3929 | 2.5102 | 1.349 | 0.64388 | 5.7561 | 5.749 | 5.5122 | 5.3776 | 5.0561 | 4.6643 | 4.2204 | 3.6673 | 3.1092 | 0.53673 | -0.96327 | -1.6153
|  | COLLEGE PARK PRIMARY | HE |  |  |  |  | 4.474 | 4.4903 | 4.426 | 4.2515 | 3.9883 | 3.6658 | 3.273 | 2.8638 | 2.4413 | 0.72296 | -0.59235 | -1.5872 | 6.7765 | 6.7531 | 6.5571 | 6.4622 | 6.2031 | 5.9051 | 5.4847 | 5.0724 | 4.602 | 2.3459 | 0.24286 | -2.0633 | 5.7592 | 5.7582 | 5.5439 | 5.4418 | 5.151 | 4.8418 | 4.3949 | 3.9643 | 3.4684 | 1.8 | 0.57143 | -0.15714
|  | COLLEGE PARK PRIMARY | FB |  |  |  |  | 4.574 | 4.6332 | 4.6862 | 4.6617 | 4.6301 | 4.5332 | 4.3597 | 4.2066 | 4.0617 | 3.0077 | 1.6087 | -0.010714 | 6.7847 | 6.7378 | 6.6643 | 6.5541 | 6.4327 | 6.1592 | 5.7224 | 5.3449 | 4.998 | 2.4388 | -1.7867 | -7.3908 | 5.8643 | 5.9408 | 5.9765 | 5.9643 | 6.0061 | 5.9449 | 5.6265 | 5.4388 | 5.301 | 4.0806 | 2.2153 | 0.77143
EALING GSP |  | COPLEY DENE PRIMARY | MINIMUM HEADROOM | TQ 17445 80798 | NO | NO | 13.892 | 2.6159 | 2.8476 | 2.7527 | 40.6834 | 40.117 | 39.3874 | 38.3119 | 36.916 | 35.6711 | 29.2048 | 24.2538 | 21.5436 | 11.7374 | 11.7374 | 11.4496 | 49.2619 | 48.6507 | 48.068 | 47.1925 | 46.065 | 45.1405 | 40.4772 | 35.3374 | 26.6272 | 5.1322 | 5.222 | 4.9822 | 42.8568 | 42.2252 | 41.5864 | 40.6395 | 39.3936 | 38.3578 | 33.0782 | 28.5925 | 26.3191
|  | COPLEY DENE PRIMARY | EE |  |  |  |  | 2.6159 | 2.8476 | 2.7527 | 40.6946 | 40.3548 | 39.3874 | 38.3476 | 37.314 | 36.015 | 29.5425 | 24.2538 | 21.5436 | 11.7394 | 11.7404 | 11.4506 | 49.2731 | 48.8476 | 48.0854 | 47.2691 | 46.4742 | 45.4721 | 40.4772 | 36.2915 | 32.6109 | 5.1322 | 5.222 | 4.9822 | 42.8568 | 42.4436 | 41.5864 | 40.6925 | 39.8303 | 38.7119 | 33.1548 | 28.5925 | 26.3191
|  | COPLEY DENE PRIMARY | HT |  |  |  |  | 2.6425 | 2.8976 | 2.8292 | 40.7517 | 40.164 | 39.4272 | 38.3119 | 36.916 | 35.6711 | 29.2048 | 24.5017 | 22.8231 | 11.7374 | 11.7374 | 11.4496 | 49.2619 | 48.6507 | 48.068 | 47.1925 | 46.065 | 45.1405 | 41.3844 | 38.9527 | 38.0078 | 5.1598 | 5.269 | 5.0537 | 42.9038 | 42.2446 | 41.6068 | 40.6395 | 39.3936 | 38.3578 | 33.0782 | 29.1405 | 27.9099
|  | COPLEY DENE PRIMARY | HE |  |  |  |  | 2.6282 | 2.8731 | 2.7935 | 40.6834 | 40.117 | 39.4109 | 38.4293 | 37.4589 | 36.1966 | 31.5507 | 27.7334 | 25.7966 | 11.7384 | 11.7435 | 11.4567 | 49.2711 | 48.6813 | 48.0987 | 47.2823 | 46.4915 | 45.4691 | 41.0344 | 37.2425 | 33.9089 | 5.1476 | 5.2435 | 5.0159 | 42.8599 | 42.2252 | 41.6099 | 40.7425 | 39.915 | 38.7997 | 34.8231 | 31.5497 | 30.018
|  | COPLEY DENE PRIMARY | FB |  |  |  |  | 3.0016 | 3.2884 | 3.5088 | 41.5793 | 41.4721 | 41.3129 | 41.1038 | 40.9334 | 40.6925 | 38.7823 | 34.0946 | 30.8854 | 11.9169 | 11.8394 | 11.7516 | 49.7252 | 49.4017 | 48.8762 | 48.2507 | 47.8007 | 47.2058 | 42.8721 | 35.3374 | 26.6272 | 5.4935 | 5.6282 | 5.7394 | 43.8874 | 43.7915 | 43.5619 | 43.2538 | 43.1282 | 42.8538 | 40.5252 | 36.264 | 33.2527
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | CORDWALLIS PRIMARY | MINIMUM HEADROOM | SU 88285 81857 | NO | NO | 7.888 | 7.9688 | 8.0005 | 7.8637 | 7.5739 | 7.1984 | 6.529 | 5.7525 | 4.8525 | 3.9158 | -0.056665 | -2.5761 | -3.5771 | 10.8178 | 10.8046 | 10.5882 | 10.3229 | 9.9607 | 9.476 | 8.9321 | 8.2617 | 7.5903 | 5.0699 | 2.3005 | -1.8424 | 8.5515 | 8.5821 | 8.4097 | 8.1535 | 7.7821 | 7.2076 | 6.5433 | 5.7556 | 4.9648 | 1.5484 | -0.47401 | -1.2077
|  | CORDWALLIS PRIMARY | EE |  |  |  |  | 7.9688 | 8.0005 | 7.8637 | 7.5739 | 7.1984 | 6.529 | 5.7525 | 4.9729 | 4.1852 | 0.51374 | -2.1689 | -3.5281 | 10.8188 | 10.8076 | 10.6076 | 10.3423 | 9.9903 | 9.5688 | 9.0229 | 8.4903 | 7.929 | 5.0699 | 3.0576 | 1.3954 | 8.5515 | 8.5821 | 8.4097 | 8.1535 | 7.7821 | 7.2239 | 6.5546 | 5.8954 | 5.2168 | 1.9862 | -0.20258 | -1.2077
|  | CORDWALLIS PRIMARY | HT |  |  |  |  | 7.9739 | 8.0148 | 7.8658 | 7.5933 | 7.2362 | 6.5658 | 5.778 | 4.8525 | 3.9158 | -0.056665 | -2.5761 | -3.5771 | 10.8178 | 10.8046 | 10.5882 | 10.3229 | 9.9607 | 9.476 | 8.9321 | 8.2617 | 7.5903 | 5.1495 | 3.9372 | 3.526 | 8.5597 | 8.5974 | 8.4178 | 8.1617 | 7.7944 | 7.2076 | 6.5433 | 5.7556 | 4.9648 | 1.5484 | -0.47401 | -1.1199
|  | CORDWALLIS PRIMARY | HE |  |  |  |  | 7.9944 | 8.0505 | 7.9403 | 7.6301 | 7.2372 | 6.5372 | 5.8495 | 5.1403 | 4.4301 | 1.5137 | -0.49544 | -1.5077 | 10.829 | 10.825 | 10.6352 | 10.375 | 10.026 | 9.5403 | 9.027 | 8.4944 | 7.9515 | 5.3862 | 3.5729 | 2.0015 | 8.5739 | 8.6199 | 8.4729 | 8.1995 | 7.8127 | 7.2117 | 6.6137 | 5.9964 | 5.3688 | 2.7933 | 1.1882 | 0.47293
|  | CORDWALLIS PRIMARY | FB |  |  |  |  | 8.3158 | 8.3699 | 8.3872 | 8.3005 | 8.1678 | 8.0117 | 7.8362 | 7.675 | 7.4597 | 5.9035 | 3.2035 | 1.6566 | 11.1178 | 11.0342 | 10.9331 | 10.6984 | 10.4423 | 10.1556 | 9.7586 | 9.427 | 8.9964 | 6.3964 | 2.3005 | -1.8424 | 8.9739 | 9.0117 | 9.027 | 8.878 | 8.7525 | 8.6137 | 8.3913 | 8.2148 | 7.9535 | 6.3495 | 3.7474 | 2.3403
MANNINGTON GSP | LYTCHETT BSP | CORFE MULLEN PRIMARY | MINIMUM HEADROOM | SY 98583 96071 | NO | NO | 2.919 | 16.1066 | 16.0474 | 15.8076 | 15.5066 | 15.076 | 14.3831 | 13.6097 | 12.7893 | 12.0015 | 9.1291 | 7.2842 | 6.9617 | 18.3484 | 18.3178 | 17.9209 | 17.5852 | 17.1168 | 16.5219 | 15.7944 | 14.9903 | 14.2444 | 11.9199 | 10.178 | 6.6413 | 17.5872 | 17.6015 | 17.2036 | 16.8525 | 16.3658 | 15.6678 | 14.8403 | 13.928 | 13.0566 | 10.424 | 8.9423 | 8.925
|  | CORFE MULLEN PRIMARY | EE |  |  |  |  | 16.1168 | 16.0791 | 15.8729 | 15.6331 | 15.2831 | 14.6291 | 13.9066 | 13.1484 | 12.4219 | 10.1699 | 8.3464 | 7.8311 | 18.3587 | 18.3495 | 17.977 | 17.7056 | 17.327 | 16.7668 | 16.0995 | 15.4219 | 14.727 | 12.0056 | 10.178 | 9.1291 | 17.6005 | 17.6454 | 17.2842 | 17.0219 | 16.6607 | 16.0036 | 15.2576 | 14.4719 | 13.6944 | 11.178 | 9.626 | 9.3882
|  | CORFE MULLEN PRIMARY | HT |  |  |  |  | 16.1066 | 16.0474 | 15.8076 | 15.5066 | 15.076 | 14.3831 | 13.6097 | 12.7893 | 12.0015 | 9.1291 | 7.2842 | 6.9617 | 18.3484 | 18.3178 | 17.9209 | 17.5852 | 17.1168 | 16.5219 | 15.7944 | 14.9903 | 14.2444 | 11.9199 | 10.7587 | 10.7719 | 17.5872 | 17.6015 | 17.2036 | 16.8525 | 16.3658 | 15.6678 | 14.8403 | 13.928 | 13.0566 | 10.424 | 8.9423 | 8.925
|  | CORFE MULLEN PRIMARY | HE |  |  |  |  | 16.1158 | 16.0791 | 15.874 | 15.6087 | 15.2321 | 14.5852 | 13.8536 | 13.0964 | 12.3525 | 10.3933 | 8.8515 | 8.3158 | 18.3576 | 18.3484 | 17.9821 | 17.6933 | 17.3107 | 16.7699 | 16.1015 | 15.4311 | 14.7209 | 12.2321 | 10.626 | 9.3301 | 17.5995 | 17.6454 | 17.2913 | 16.9995 | 16.6209 | 15.9984 | 15.2393 | 14.4638 | 13.6658 | 11.4291 | 10.175 | 9.8015
|  | CORFE MULLEN PRIMARY | FB |  |  |  |  | 16.2903 | 16.3393 | 16.3566 | 16.3117 | 16.176 | 16.0209 | 15.8495 | 15.6536 | 15.4433 | 14.0117 | 12.6066 | 11.7842 | 18.5464 | 18.4913 | 18.4862 | 18.376 | 18.0148 | 17.6627 | 17.2933 | 16.9178 | 16.5015 | 13.7495 | 10.3474 | 6.6413 | 17.877 | 17.9372 | 18.0311 | 18.0189 | 17.7576 | 17.5413 | 17.3209 | 17.1107 | 16.8393 | 15.0066 | 13.1556 | 12.1668
MELKSHAM GSP | NORRINGTON BSP | CORSHAM PRIMARY | MINIMUM HEADROOM | ST 86766 69583 | NO | YES | 1.872 | 3.0309 | 3.0514 | 2.9534 | 2.6279 | 2.285 | 1.7299 | 1.086 | 0.23503 | -0.61293 | -4.0007 | -6.6088 | -8.114 | 5.2442 | 5.2422 | 5.1381 | 4.9524 | 4.7585 | 4.4065 | 3.8014 | 3.1391 | 2.5116 | -0.26497 | -2.0293 | -3.1813 | 4.1126 | 4.1258 | 3.9871 | 3.7422 | 3.4197 | 2.9167 | 2.2371 | 1.4524 | 0.68503 | -2.4333 | -4.5129 | -5.5527
|  | CORSHAM PRIMARY | EE |  |  |  |  | 3.0309 | 3.0514 | 2.9697 | 2.6809 | 2.3881 | 1.8769 | 1.136 | 0.32482 | -0.4762 | -3.9466 | -6.5956 | -8.0905 | 5.2442 | 5.2422 | 5.1422 | 4.9697 | 4.7901 | 4.4514 | 3.8014 | 3.1391 | 2.5116 | -0.26497 | -2.0293 | -3.1813 | 4.1126 | 4.1258 | 3.9983 | 3.7789 | 3.4891 | 3.0034 | 2.2371 | 1.4524 | 0.68503 | -2.4333 | -4.5129 | -5.5527
|  | CORSHAM PRIMARY | HT |  |  |  |  | 3.032 | 3.0534 | 2.9534 | 2.6279 | 2.285 | 1.7299 | 1.086 | 0.23503 | -0.61293 | -4.0007 | -6.6088 | -8.114 | 5.2452 | 5.2422 | 5.1381 | 4.9524 | 4.7585 | 4.4065 | 3.9167 | 3.3034 | 2.7054 | 0.47176 | -0.76293 | -1.2129 | 4.1136 | 4.1279 | 3.9871 | 3.7422 | 3.4197 | 2.9167 | 2.2942 | 1.5207 | 0.75544 | -2.1384 | -4.0599 | -4.9905
|  | CORSHAM PRIMARY | HE |  |  |  |  | 3.033 | 3.0524 | 2.9697 | 2.6809 | 2.3677 | 1.8493 | 1.2871 | 0.6136 | -0.042522 | -2.368 | -4.5548 | -5.6762 | 5.2452 | 5.2422 | 5.1432 | 4.9779 | 4.7871 | 4.4391 | 4.0116 | 3.536 | 3.0881 | 1.3054 | -0.034359 | -1.0568 | 4.1136 | 4.1279 | 3.9993 | 3.7952 | 3.4748 | 2.9809 | 2.435 | 1.834 | 1.2524 | -0.71089 | -2.3017 | -3.0619
|  | CORSHAM PRIMARY | FB |  |  |  |  | 3.1667 | 3.2381 | 3.2952 | 3.185 | 2.9963 | 2.9473 | 2.8503 | 2.7452 | 2.6085 | 1.5289 | -0.15273 | -1.4476 | 5.3258 | 5.3503 | 5.3667 | 5.3024 | 5.1493 | 5.0034 | 4.7912 | 4.5932 | 4.3289 | 2.6248 | 0.3238 | -2.2252 | 4.2156 | 4.2544 | 4.284 | 4.1932 | 4.0493 | 3.9891 | 3.9003 | 3.8054 | 3.6575 | 2.3973 | 0.81258 | -0.34967
EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD PRIMARY | MINIMUM HEADROOM | SP 59021 31128 | YES | YES | 0.606 | -1.5728 | -1.7024 | -1.9248 | -2.0248 | -3.8156 | -5.2575 | -6.8197 | -8.2105 | -9.3809 | -10.7289 | -11.1891 | -11.4105 | -0.62176 | -0.70748 | -0.92176 | -1.0238 | -2.7116 | -4.2085 | -5.8585 | -7.3534 | -8.5279 | -9.3544 | -9.4932 | -9.585 | -1.0799 | -1.1881 | -1.432 | -1.533 | -3.2983 | -4.7779 | -6.4207 | -7.9156 | -9.0963 | -10.0738 | -10.2983 | -10.3912
|  | COTTISFORD PRIMARY | EE |  |  |  |  | -1.5718 | -1.6718 | -1.8973 | -1.9881 | -2.1207 | -3.3524 | -4.9687 | -6.3748 | -7.5463 | -10.7289 | -11.1891 | -11.3738 | -0.61564 | -0.68299 | -0.89625 | -0.99523 | -1.133 | -2.2503 | -3.6799 | -5.1707 | -6.3452 | -9.3544 | -9.4932 | -9.532 | -1.0758 | -1.1595 | -1.4054 | -1.5116 | -1.6452 | -2.8167 | -4.3371 | -5.835 | -7.0228 | -10.0738 | -10.2983 | -10.3667
|  | COTTISFORD PRIMARY | HT |  |  |  |  | -1.5728 | -1.7024 | -1.9248 | -2.0248 | -3.8156 | -5.2575 | -6.8197 | -8.2105 | -9.3809 | -10.5901 | -11.1116 | -11.4105 | -0.62176 | -0.70748 | -0.92176 | -1.0238 | -2.7116 | -4.2085 | -5.8585 | -7.3534 | -8.5279 | -9.3463 | -9.4493 | -9.4452 | -1.0799 | -1.1881 | -1.432 | -1.533 | -3.2983 | -4.7779 | -6.4207 | -7.9156 | -9.0963 | -10.0187 | -10.2748 | -10.3912
|  | COTTISFORD PRIMARY | HE |  |  |  |  | -1.5687 | -1.6687 | -1.8932 | -1.9963 | -2.1432 | -3.4401 | -5.135 | -6.6146 | -7.832 | -10.4707 | -10.9238 | -11.1636 | -0.6136 | -0.68095 | -0.89523 | -0.99523 | -1.134 | -2.2993 | -3.8116 | -5.3575 | -6.5789 | -9.282 | -9.4177 | -9.5054 | -1.0728 | -1.1575 | -1.4034 | -1.5167 | -1.6412 | -2.8809 | -4.483 | -6.0473 | -7.284 | -9.9605 | -10.1789 | -10.2667
|  | COTTISFORD PRIMARY | FB |  |  |  |  | -1.4983 | -1.5718 | -1.5575 | -1.5514 | -1.5636 | -1.784 | -2.8289 | -3.9432 | -4.7381 | -9.2575 | -9.833 | -10.2616 | -0.57687 | -0.63197 | -0.63809 | -0.64217 | -0.6636 | -0.87176 | -1.8605 | -3.0626 | -3.9177 | -8.8014 | -9.3003 | -9.585 | -1.0299 | -1.0758 | -1.0769 | -1.085 | -1.1034 | -1.3146 | -2.3626 | -3.5605 | -4.3983 | -9.1667 | -9.6218 | -9.8146
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | COURAGES PRIMARY | MINIMUM HEADROOM | SU 70990 69570 | NO | NO | 12.547 | 7.4226 | 7.0114 | 6.8869 | 6.6981 | 6.2124 | 3.8563 | 3.6706 | 3.4053 | 3.2757 | -0.62941 | -1.6406 | -1.9294 | 9.4032 | 9.0206 | 8.9594 | 8.8818 | 8.5155 | 5.7002 | 5.5941 | 5.4767 | 5.4216 | 1.9634 | 0.98692 | -0.29369 | 8.8022 | 8.439 | 8.3665 | 8.2512 | 7.8655 | 5.4043 | 5.2328 | 4.9441 | 4.789 | 1.4543 | 0.61243 | 0.40631
|  | COURAGES PRIMARY | EE |  |  |  |  | 7.4226 | 7.0186 | 6.8971 | 6.7114 | 6.2124 | 3.939 | 3.6706 | 3.4053 | 3.2757 | -0.50492 | -1.4427 | -1.6784 | 9.4043 | 9.0298 | 8.9737 | 8.8951 | 8.54 | 5.9992 | 5.8553 | 5.7124 | 5.6277 | 1.9634 | 1.143 | 0.70631 | 8.8022 | 8.44 | 8.3665 | 8.2543 | 7.8655 | 5.5226 | 5.2328 | 4.9441 | 4.789 | 1.4543 | 0.61243 | 0.40631
|  | COURAGES PRIMARY | HT |  |  |  |  | 7.4247 | 7.0114 | 6.8869 | 6.6981 | 6.5032 | 4.2247 | 3.9788 | 3.6798 | 3.5634 | -0.62941 | -1.6406 | -1.9294 | 9.4063 | 9.0277 | 8.9665 | 8.8828 | 8.7992 | 6.2492 | 6.1257 | 5.9451 | 5.8737 | 2.0134 | 1.3114 | 1.1971 | 8.8083 | 8.439 | 8.3686 | 8.2512 | 8.1359 | 5.7624 | 5.5461 | 5.1471 | 5.0359 | 1.4634 | 0.70937 | 0.57161
|  | COURAGES PRIMARY | HE |  |  |  |  | 7.4247 | 7.0226 | 6.8992 | 6.7216 | 6.2257 | 3.9532 | 3.6869 | 3.4369 | 3.3155 | -0.3192 | -1.0988 | -1.3019 | 9.4053 | 9.0318 | 8.9767 | 8.9012 | 8.5492 | 6.0063 | 5.8696 | 5.742 | 5.6645 | 2.092 | 1.3349 | 1.0247 | 8.8083 | 8.4481 | 8.3788 | 8.2716 | 7.8859 | 5.5502 | 5.2624 | 5.0247 | 4.8828 | 1.8032 | 1.1481 | 1.0206
|  | COURAGES PRIMARY | FB |  |  |  |  | 7.4492 | 7.0594 | 6.9594 | 6.8216 | 6.3634 | 3.8563 | 3.69 | 3.5124 | 3.4675 | 3.342 | -0.45186 | -0.67022 | 9.4032 | 9.0206 | 8.9594 | 8.8818 | 8.5155 | 5.7002 | 5.5941 | 5.4767 | 5.4216 | 5.0604 | 0.98692 | -0.29369 | 8.8318 | 8.4757 | 8.4145 | 8.3349 | 7.9686 | 5.4043 | 5.3063 | 5.191 | 5.1563 | 5.0379 | 1.5186 | 1.1951
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | COVE PRIMARY | MINIMUM HEADROOM | SU 85415 55937 | NO | NO | 3.032 | 10.979 | 10.6831 | 10.7698 | 10.7106 | 10.4331 | 10.1371 | 9.679 | 9.0167 | 8.3208 | 5.9055 | 4.5055 | 4.0545 | 13.6018 | 13.2661 | 13.2865 | 13.1753 | 12.8457 | 12.5345 | 12.0488 | 11.3253 | 10.6845 | 7.5896 | 5.858 | 3.4447 | 12.8718 | 12.5657 | 12.5412 | 12.4422 | 12.1912 | 11.881 | 11.429 | 10.7443 | 10.03 | 7.2555 | 5.7984 | 5.3382
|  | COVE PRIMARY | EE |  |  |  |  | 10.979 | 10.6831 | 10.78 | 10.7504 | 10.6024 | 10.3004 | 9.8198 | 9.1861 | 8.6535 | 5.9055 | 4.5055 | 4.0545 | 13.6029 | 13.2692 | 13.2957 | 13.1927 | 12.9682 | 12.609 | 12.0488 | 11.3253 | 10.708 | 7.5896 | 5.858 | 4.6386 | 12.8718 | 12.5657 | 12.5412 | 12.4576 | 12.2943 | 11.9994 | 11.4606 | 10.7443 | 10.1484 | 7.2555 | 5.7984 | 5.3382
|  | COVE PRIMARY | HT |  |  |  |  | 10.9831 | 10.6902 | 10.7698 | 10.7106 | 10.4331 | 10.1371 | 9.679 | 9.0167 | 8.3208 | 5.9606 | 4.8137 | 4.6749 | 13.6018 | 13.2671 | 13.2865 | 13.1753 | 12.8457 | 12.5345 | 12.0773 | 11.3927 | 10.6845 | 8.3743 | 7.3937 | 7.1804 | 12.8759 | 12.579 | 12.5494 | 12.4422 | 12.1912 | 11.881 | 11.429 | 10.7443 | 10.03 | 7.5984 | 6.4371 | 6.3045
|  | COVE PRIMARY | HE |  |  |  |  | 10.9861 | 10.6912 | 10.7943 | 10.7576 | 10.5994 | 10.3004 | 9.9902 | 9.5116 | 9.0218 | 6.9831 | 6.1361 | 5.8892 | 13.6029 | 13.2661 | 13.2916 | 13.1896 | 12.9641 | 12.6008 | 12.2427 | 11.7018 | 11.1529 | 8.7314 | 7.3988 | 6.2722 | 12.8769 | 12.581 | 12.5657 | 12.4688 | 12.2922 | 11.9973 | 11.6657 | 11.1422 | 10.6096 | 8.5453 | 7.7096 | 7.4749
|  | COVE PRIMARY | FB |  |  |  |  | 11.131 | 10.9076 | 10.9871 | 11.0433 | 11.1463 | 10.978 | 10.9024 | 10.781 | 10.6402 | 9.031 | 7.3963 | 6.5555 | 13.6733 | 13.3559 | 13.312 | 13.2518 | 13.2212 | 12.909 | 12.6722 | 12.4029 | 12.11 | 9.608 | 6.61 | 3.4447 | 13.0127 | 12.7035 | 12.7351 | 12.7198 | 12.7045 | 12.5004 | 12.4014 | 12.2627 | 12.1055 | 10.3943 | 9.0167 | 8.1535
FAWLEY GSP | COWES BSP | COWES PRIMARY | MINIMUM HEADROOM | SP 56113 03074 | NO | YES | 4.224 | 7.0082 | 6.9306 | 6.451 | 5.7082 | 4.7776 | 3.2929 | 1.8939 | 0.50714 | -0.85816 | -6.6663 | -11.1541 | -13.2918 | 10.6071 | 10.5429 | 10.2714 | 9.9306 | 9.4551 | 8.7551 | 7.8735 | 6.9959 | 6.1388 | 3.0306 | 0.54286 | -2.85 | 8.9878 | 8.9653 | 8.652 | 8.1306 | 7.2796 | 6.0061 | 4.7204 | 3.4765 | 2.252 | -2.5337 | -5.9408 | -7.0551
|  | COWES PRIMARY | EE |  |  |  |  | 7.0082 | 6.9316 | 6.4653 | 5.8092 | 4.9653 | 3.6235 | 2.3959 | 1.1929 | 0.031633 | -4.8888 | -9.202 | -11.5041 | 10.6092 | 10.5531 | 10.3122 | 10.0337 | 9.6173 | 9.0122 | 8.2071 | 7.4296 | 6.6571 | 3.1643 | 0.54286 | -1.0602 | 8.9878 | 8.9653 | 8.6592 | 8.2296 | 7.4592 | 6.3184 | 5.1592 | 4.0612 | 2.9765 | -1.3551 | -4.7643 | -6.2327
|  | COWES PRIMARY | HT |  |  |  |  | 7.0153 | 6.9306 | 6.451 | 5.7082 | 4.7776 | 3.2929 | 1.8939 | 0.50714 | -0.85816 | -6.6663 | -11.1541 | -13.2918 | 10.6071 | 10.5429 | 10.2714 | 9.9306 | 9.4551 | 8.7551 | 7.8735 | 6.9959 | 6.1388 | 3.0306 | 1.1888 | 0.92245 | 8.9929 | 8.9684 | 8.652 | 8.1306 | 7.2796 | 6.0061 | 4.7204 | 3.4765 | 2.252 | -2.5337 | -5.9408 | -7.0551
|  | COWES PRIMARY | HE |  |  |  |  | 7.0184 | 6.9459 | 6.4878 | 5.8255 | 4.9847 | 3.6827 | 2.5122 | 1.3602 | 0.25918 | -3.7704 | -7.0867 | -9.0571 | 10.6092 | 10.552 | 10.3092 | 10.0296 | 9.6214 | 9.0143 | 8.2296 | 7.4439 | 6.6908 | 3.6184 | 1.5796 | -0.23673 | 8.9959 | 8.9796 | 8.6806 | 8.2418 | 7.4755 | 6.349 | 5.2398 | 4.1622 | 3.1245 | -0.41224 | -2.8276 | -4.202
|  | COWES PRIMARY | FB |  |  |  |  | 7.3133 | 7.3837 | 7.2 | 6.9622 | 6.6459 | 6.2602 | 6.05 | 5.8102 | 5.5745 | 3.549 | 0.23061 | -2.0653 | 10.799 | 10.7612 | 10.5796 | 10.4041 | 10.1612 | 9.8153 | 9.4888 | 9.1184 | 8.748 | 5.8367 | 1.4296 | -2.85 | 9.2776 | 9.351 | 9.2653 | 9.1378 | 8.9449 | 8.652 | 8.4224 | 8.102 | 7.8092 | 5.399 | 2.0143 | -0.077551
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL PRIMARY | MINIMUM HEADROOM | SP 56113 03074 | NO | NO | 38.085 | 26.3633 | 26.0245 | 25.8378 | 25.1878 | 23.3521 | 21.2623 | 18.8398 | 16.2378 | 13.4378 | 6.3153 | 3.2021 | 2.1388 | 28.7531 | 28.4408 | 28.1827 | 27.7725 | 26.2368 | 24.5541 | 22.5011 | 20.0031 | 17.4296 | 12.1357 | 8.6245 | 2.2806 | 26.5755 | 26.2643 | 26.0643 | 25.5337 | 23.8511 | 21.9419 | 19.6755 | 17.1521 | 14.3908 | 7.5704 | 4.9898 | 3.5378
|  | COWLEY LOCAL PRIMARY | EE |  |  |  |  | 26.3633 | 26.0245 | 25.85 | 25.3102 | 24.5194 | 22.8184 | 20.8286 | 18.8092 | 16.7419 | 7.7215 | 3.8225 | 2.1388 | 28.7735 | 28.4766 | 28.2511 | 27.9296 | 27.3521 | 26.0153 | 24.3347 | 22.547 | 20.7306 | 12.3429 | 9.0388 | 6.3653 | 26.5755 | 26.2643 | 26.0694 | 25.6368 | 24.947 | 23.4225 | 21.5653 | 19.6051 | 17.5868 | 8.3694 | 4.9898 | 3.5378
|  | COWLEY LOCAL PRIMARY | HT |  |  |  |  | 26.3817 | 26.0633 | 25.8378 | 25.1878 | 23.3521 | 21.2623 | 18.8398 | 16.2378 | 13.4378 | 6.3153 | 3.2021 | 2.3653 | 28.7531 | 28.4408 | 28.1827 | 27.7725 | 26.2368 | 24.5541 | 22.5011 | 20.0031 | 17.4296 | 12.1357 | 10.0092 | 9.3653 | 26.5817 | 26.2888 | 26.0643 | 25.5337 | 23.8511 | 21.9419 | 19.6755 | 17.1521 | 14.3908 | 7.5704 | 5.0572 | 4.549
|  | COWLEY LOCAL PRIMARY | HE |  |  |  |  | 26.3827 | 26.0623 | 25.9051 | 25.3674 | 24.5929 | 22.9184 | 20.9541 | 18.9704 | 16.9378 | 9.3378 | 6.5786 | 5.4347 | 28.7786 | 28.4837 | 28.2633 | 27.946 | 27.3868 | 26.0204 | 24.3143 | 22.5123 | 20.6725 | 13.2133 | 10.3725 | 7.9745 | 26.597 | 26.3011 | 26.1255 | 25.6868 | 25.0062 | 23.4868 | 21.6357 | 19.6939 | 17.6796 | 9.8837 | 7.5368 | 6.6286
|  | COWLEY LOCAL PRIMARY | FB |  |  |  |  | 26.8704 | 26.5235 | 26.498 | 26.4306 | 26.1225 | 25.4378 | 24.4806 | 23.4806 | 22.5021 | 14.6562 | 10.5011 | 7.9419 | 29.1174 | 28.6664 | 28.4633 | 28.3602 | 27.9837 | 27.2419 | 26.2021 | 25.0725 | 23.9531 | 14.247 | 8.6245 | 2.2806 | 27.0623 | 26.7347 | 26.6704 | 26.6327 | 26.3653 | 25.7521 | 24.8643 | 23.898 | 22.9235 | 14.5174 | 10.5419 | 8.047
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | COXMOOR WOOD PRIMARY | MINIMUM HEADROOM | SU 78275 50779 | YES | NO | 1.109 | 1.2143 | 1.1531 | 1.001 | 0.84592 | 0.58367 | 0.14286 | -0.35408 | -0.88878 | -1.4551 | -3.6224 | -5.2173 | -6.1071 | 4.3122 | 4.2704 | 4.0531 | 3.9061 | 3.5796 | 3.2367 | 2.7939 | 2.2949 | 1.9337 | 0.56224 | -0.090816 | -0.30612 | 3.4306 | 3.35 | 3.0551 | 2.9153 | 2.6102 | 2.1735 | 1.6378 | 1.0551 | 0.58061 | -1.2061 | -2.3633 | -2.9102
|  | COXMOOR WOOD PRIMARY | EE |  |  |  |  | 1.2143 | 1.1531 | 1.0235 | 0.90918 | 0.69184 | 0.25408 | -0.20612 | -0.71429 | -1.1714 | -3.0265 | -4.5388 | -5.3908 | 4.3122 | 4.2704 | 4.0888 | 3.9959 | 3.7388 | 3.4316 | 3.1235 | 2.6918 | 2.3878 | 1.0204 | 0.28878 | -0.045918 | 3.4327 | 3.35 | 3.099 | 3.0378 | 2.7908 | 2.3827 | 1.9643 | 1.4316 | 1.0122 | -0.69286 | -1.8398 | -2.4235
|  | COXMOOR WOOD PRIMARY | HT |  |  |  |  | 1.2153 | 1.1561 | 1.001 | 0.84592 | 0.58367 | 0.14286 | -0.35408 | -0.88878 | -1.4551 | -3.6224 | -5.2173 | -6.1071 | 4.3133 | 4.2714 | 4.0531 | 3.9061 | 3.5796 | 3.2367 | 2.7939 | 2.2949 | 1.9337 | 0.56224 | -0.090816 | -0.23571 | 3.4306 | 3.35 | 3.0551 | 2.9153 | 2.6102 | 2.1735 | 1.6378 | 1.0551 | 0.58061 | -1.2061 | -2.3633 | -2.9102
|  | COXMOOR WOOD PRIMARY | HE |  |  |  |  | 1.2153 | 1.1541 | 1.0245 | 0.89592 | 0.65714 | 0.22653 | -0.26122 | -0.77143 | -1.2378 | -2.7622 | -3.9092 | -4.5429 | 4.3133 | 4.2714 | 4.0878 | 3.9939 | 3.7133 | 3.4684 | 3.1031 | 2.6969 | 2.4122 | 1.2133 | 0.84082 | 0.51735 | 3.4306 | 3.35 | 3.099 | 3.0265 | 2.7561 | 2.3959 | 1.9235 | 1.4102 | 1.002 | -0.46327 | -1.25 | -1.7031
|  | COXMOOR WOOD PRIMARY | FB |  |  |  |  | 1.2918 | 1.2541 | 1.2724 | 1.2469 | 1.151 | 1.0806 | 0.98571 | 0.85306 | 0.73061 | -0.089796 | -1.0031 | -1.8122 | 4.3796 | 4.352 | 4.3653 | 4.3469 | 4.1673 | 4.0857 | 3.9888 | 3.7684 | 3.6 | 2.5204 | 1.3837 | -0.30612 | 3.5439 | 3.5061 | 3.5255 | 3.5286 | 3.3082 | 3.2459 | 3.1755 | 2.9796 | 2.8276 | 1.798 | 0.68878 | -0.12041
MANNINGTON GSP | LYTCHETT BSP | CREEKMOOR PRIMARY | MINIMUM HEADROOM | SZ 00552 94121 | NO | NO | 2.205 | 16.2709 | 16.1709 | 15.9689 | 15.5474 | 15.0015 | 13.8505 | 12.627 | 11.3107 | 10.1352 | 6.0331 | 3.0709 | 1.7913 | 18.9107 | 18.726 | 18.4954 | 18.1729 | 17.726 | 17.1138 | 16.375 | 15.5321 | 14.8678 | 12.4525 | 10.5678 | 6.4964 | 17.777 | 17.6791 | 17.4954 | 17.1505 | 16.6893 | 15.924 | 15.0484 | 13.8903 | 12.926 | 9.5311 | 7.377 | 6.6301
|  | CREEKMOOR PRIMARY | EE |  |  |  |  | 16.2821 | 16.2301 | 16.078 | 15.7903 | 15.3117 | 14.3444 | 13.3005 | 12.1933 | 11.2066 | 7.5923 | 4.8535 | 3.3342 | 18.9209 | 18.7597 | 18.5423 | 18.2913 | 17.8658 | 17.3495 | 16.6995 | 15.9678 | 15.3923 | 12.4964 | 10.5678 | 8.9719 | 17.7831 | 17.7076 | 17.5474 | 17.2821 | 16.8158 | 16.1597 | 15.4331 | 14.5678 | 13.7433 | 10.5821 | 8.4974 | 7.4444
|  | CREEKMOOR PRIMARY | HT |  |  |  |  | 16.2709 | 16.1709 | 15.9689 | 15.5474 | 15.0015 | 13.8505 | 12.627 | 11.3107 | 10.1352 | 6.0331 | 3.0709 | 1.7913 | 18.9107 | 18.726 | 18.4954 | 18.1729 | 17.726 | 17.1138 | 16.375 | 15.5321 | 14.8678 | 12.4525 | 11.2393 | 10.9086 | 17.777 | 17.6791 | 17.4954 | 17.1505 | 16.6893 | 15.924 | 15.0484 | 13.8903 | 12.926 | 9.5311 | 7.377 | 6.6301
|  | CREEKMOOR PRIMARY | HE |  |  |  |  | 16.2831 | 16.2362 | 16.0913 | 15.7617 | 15.2515 | 14.3535 | 13.3586 | 12.3148 | 11.3862 | 8.2678 | 5.8913 | 4.9433 | 18.9199 | 18.7607 | 18.5556 | 18.275 | 17.8403 | 17.3423 | 16.6913 | 15.9821 | 15.4178 | 12.7923 | 11.0076 | 9.5464 | 17.7842 | 17.7158 | 17.5648 | 17.2719 | 16.7811 | 16.1658 | 15.4668 | 14.6403 | 13.8535 | 11.1127 | 9.3444 | 8.7311
|  | CREEKMOOR PRIMARY | FB |  |  |  |  | 16.5403 | 16.6617 | 16.6158 | 16.6709 | 16.5178 | 16.3913 | 16.2423 | 16.0311 | 15.8342 | 14.1586 | 12.0056 | 10.5046 | 19.078 | 19.0393 | 18.7893 | 18.7189 | 18.4352 | 18.1321 | 17.8046 | 17.4097 | 17.0311 | 14.2709 | 10.6454 | 6.4964 | 17.9658 | 18.0117 | 17.9535 | 17.9331 | 17.7199 | 17.5872 | 17.4331 | 17.2403 | 17.0464 | 15.6025 | 13.5189 | 12.0658
MINETY GSP | CIRENCESTER BSP | CRICKLADE PRIMARY | MINIMUM HEADROOM | SU 09400 93270 | NO | NO | 1.839 | 5.626 | 5.4179 | 5.3526 | 5.274 | 5.0485 | 4.7107 | 4.2954 | 3.8464 | 3.325 | 1.876 | 1.2209 | 1.1158 | 7.3357 | 7.0612 | 6.9378 | 6.798 | 6.5051 | 6.1296 | 5.6724 | 5.1765 | 4.6092 | 2.95 | 2.049 | 1.048 | 5.9102 | 5.7041 | 5.6286 | 5.549 | 5.3347 | 5.0163 | 4.6194 | 4.1847 | 3.698 | 2.2816 | 1.6296 | 1.5551
|  | CRICKLADE PRIMARY | EE |  |  |  |  | 5.626 | 5.4179 | 5.3587 | 5.2964 | 5.076 | 4.7444 | 4.3883 | 3.9597 | 3.4903 | 2.0128 | 1.3158 | 1.227 | 7.3357 | 7.0612 | 6.9429 | 6.8092 | 6.5143 | 6.1327 | 5.7184 | 5.2388 | 4.7102 | 2.95 | 2.049 | 1.6031 | 5.9102 | 5.7041 | 5.6357 | 5.5653 | 5.3551 | 5.0367 | 4.6806 | 4.2694 | 3.8214 | 2.3622 | 1.6612 | 1.6061
|  | CRICKLADE PRIMARY | HT |  |  |  |  | 5.627 | 5.4209 | 5.3526 | 5.274 | 5.0485 | 4.7107 | 4.2954 | 3.8464 | 3.325 | 1.876 | 1.2209 | 1.1158 | 7.3378 | 7.0643 | 6.9378 | 6.798 | 6.5061 | 6.1296 | 5.6724 | 5.1765 | 4.6092 | 2.9949 | 2.3367 | 2.2459 | 5.9112 | 5.7061 | 5.6286 | 5.549 | 5.3347 | 5.0163 | 4.6194 | 4.1847 | 3.698 | 2.2816 | 1.6296 | 1.5551
|  | CRICKLADE PRIMARY | HE |  |  |  |  | 5.626 | 5.4189 | 5.3566 | 5.2923 | 5.0638 | 4.7638 | 4.3811 | 3.9464 | 3.4668 | 2.4434 | 1.7872 | 1.4852 | 7.3367 | 7.0612 | 6.9398 | 6.8071 | 6.5051 | 6.1612 | 5.7153 | 5.2306 | 4.6969 | 3.4224 | 2.5673 | 1.8857 | 5.9112 | 5.7051 | 5.6337 | 5.5622 | 5.3449 | 5.0551 | 4.6745 | 4.2592 | 3.8031 | 2.8337 | 2.1837 | 1.8918
|  | CRICKLADE PRIMARY | FB |  |  |  |  | 5.775 | 5.826 | 5.8872 | 5.7179 | 5.6791 | 5.6689 | 5.5944 | 5.4628 | 5.3199 | 4.3495 | 3.1689 | 2.3036 | 7.451 | 7.4173 | 7.4 | 7.15 | 7.0296 | 6.9286 | 6.7724 | 6.5459 | 6.3173 | 4.8449 | 3.0031 | 1.048 | 6.0398 | 6.0531 | 6.0867 | 5.9663 | 5.9204 | 5.9061 | 5.8276 | 5.6918 | 5.55 | 4.5939 | 3.4765 | 2.5724
MELKSHAM GSP | FROME BSP | CROCKERTON PRIMARY | MINIMUM HEADROOM | ST 87736 43371 | NO | NO | 1.582 | -0.27816 | -0.26796 | -0.23633 | -0.4098 | -0.64143 | -1.1322 | -1.6843 | -2.2863 | -2.8904 | -5.7016 | -8.1037 | -9.5537 | 3.3294 | 3.2488 | 3.2049 | 3.0386 | 2.8314 | 2.5406 | 2.21 | 1.7702 | 1.1488 | -0.82571 | -2.1859 | -4.4614 | 1.6943 | 1.6637 | 1.6698 | 1.5351 | 1.3433 | 0.95245 | 0.38102 | -0.23633 | -0.92714 | -3.2353 | -4.8516 | -5.6669
|  | CROCKERTON PRIMARY | EE |  |  |  |  | -0.27816 | -0.26694 | -0.23224 | -0.38429 | -0.59755 | -1.07 | -1.6261 | -2.2241 | -2.8118 | -5.5996 | -7.9251 | -9.2904 | 3.3294 | 3.2498 | 3.211 | 3.058 | 2.8702 | 2.5988 | 2.2978 | 1.8886 | 1.3314 | -0.82571 | -2.1859 | -3.188 | 1.6943 | 1.6637 | 1.6729 | 1.5545 | 1.378 | 1.0035 | 0.46163 | -0.15061 | -0.77612 | -3.1384 | -4.77 | -5.6251
|  | CROCKERTON PRIMARY | HT |  |  |  |  | -0.27714 | -0.26592 | -0.23633 | -0.4098 | -0.64143 | -1.1322 | -1.6751 | -2.2822 | -2.8904 | -5.7016 | -8.1037 | -9.5537 | 3.3294 | 3.2498 | 3.2049 | 3.0386 | 2.8314 | 2.5406 | 2.21 | 1.7702 | 1.1488 | -0.73796 | -1.6951 | -2.0145 | 1.6943 | 1.6647 | 1.6698 | 1.5351 | 1.3433 | 0.95245 | 0.38102 | -0.23633 | -0.92714 | -3.2353 | -4.8516 | -5.6669
|  | CROCKERTON PRIMARY | HE |  |  |  |  | -0.27612 | -0.26796 | -0.23224 | -0.38939 | -0.62918 | -1.1149 | -1.6843 | -2.2863 | -2.8853 | -5.0129 | -7.2914 | -8.3588 | 3.3314 | 3.2488 | 3.209 | 3.0712 | 2.8651 | 2.5845 | 2.2906 | 1.8804 | 1.3212 | -0.46347 | -1.8349 | -2.7757 | 1.6953 | 1.6647 | 1.6718 | 1.5565 | 1.3627 | 0.95755 | 0.41776 | -0.18633 | -0.82 | -2.6567 | -4.2578 | -4.9231
|  | CROCKERTON PRIMARY | FB |  |  |  |  | -0.17204 | -0.079184 | -0.0016327 | 0.041224 | -0.0046939 | -0.14755 | -0.22816 | -0.32816 | -0.44041 | -1.4241 | -2.8016 | -3.9894 | 3.411 | 3.4457 | 3.4773 | 3.4692 | 3.3569 | 3.211 | 3.11 | 2.9896 | 2.7243 | 0.82939 | -1.7584 | -4.4614 | 1.7841 | 1.8473 | 1.8994 | 1.9127 | 1.8698 | 1.7371 | 1.6627 | 1.5698 | 1.4637 | 0.3749 | -1.3006 | -2.3649
FLEET-BRAMLEY GSP | PYESTOCK BSP | CROOKHAM PRIMARY | MINIMUM HEADROOM | SU 81702 53403 | NO | NO | 0.758 | 19.7082 | 19.8061 | 19.5429 | 19.0388 | 18.4173 | 17.202 | 15.8888 | 14.3622 | 13.0276 | 8.9969 | 6.0653 | 4.548 | 19.8296 | 19.8439 | 19.652 | 19.3827 | 19.0745 | 18.5531 | 17.9255 | 17.0429 | 16.3582 | 14.5041 | 13.5286 | 10.248 | 19.0592 | 19.1163 | 18.9265 | 18.5602 | 18.1061 | 17.2459 | 16.2867 | 15.1112 | 14.1245 | 11.2459 | 9.4306 | 8.701
|  | CROOKHAM PRIMARY | EE |  |  |  |  | 19.7082 | 19.8061 | 19.7133 | 19.4663 | 19.1306 | 18.1551 | 17.002 | 15.798 | 14.7398 | 11.3071 | 8.7337 | 7.3265 | 19.8296 | 19.8439 | 19.7082 | 19.5184 | 19.2888 | 18.8796 | 18.249 | 17.5684 | 17.0398 | 14.9133 | 13.6286 | 12.5867 | 19.0592 | 19.1163 | 19.0378 | 18.8418 | 18.5735 | 17.8806 | 17.001 | 16.0735 | 15.2888 | 12.748 | 11.0949 | 10.3408
|  | CROOKHAM PRIMARY | HT |  |  |  |  | 19.7082 | 19.8143 | 19.5429 | 19.0388 | 18.4173 | 17.202 | 15.8888 | 14.3622 | 13.0276 | 8.9969 | 6.0653 | 4.548 | 19.8306 | 19.8439 | 19.652 | 19.3827 | 19.0745 | 18.5531 | 17.9255 | 17.0429 | 16.3582 | 14.5041 | 13.7184 | 13.5418 | 19.0592 | 19.1214 | 18.9265 | 18.5602 | 18.1061 | 17.2459 | 16.2867 | 15.1112 | 14.1245 | 11.2459 | 9.4306 | 8.701
|  | CROOKHAM PRIMARY | HE |  |  |  |  | 19.7092 | 19.8112 | 19.7184 | 19.4286 | 19.0582 | 18.0837 | 16.9224 | 15.7582 | 14.6347 | 11.598 | 9.1235 | 7.9939 | 19.8306 | 19.8449 | 19.7082 | 19.5143 | 19.2816 | 18.8755 | 18.2398 | 17.6255 | 17.0347 | 15.0276 | 13.6714 | 12.4745 | 19.0602 | 19.1204 | 19.0418 | 18.8204 | 18.5337 | 17.8408 | 16.9592 | 16.0776 | 15.2357 | 12.948 | 11.3286 | 10.6643
|  | CROOKHAM PRIMARY | FB |  |  |  |  | 19.9571 | 20.048 | 20.201 | 20.2204 | 20.1796 | 20.0449 | 19.8806 | 19.6735 | 19.4367 | 17.7929 | 15.8673 | 14.7112 | 19.9969 | 19.9612 | 19.9827 | 19.9051 | 19.7694 | 19.5184 | 19.2347 | 18.9173 | 18.5765 | 16.3908 | 13.5286 | 10.248 | 19.2949 | 19.3673 | 19.4765 | 19.5102 | 19.4867 | 19.3786 | 19.2061 | 18.999 | 18.7776 | 17.2969 | 15.6878 | 14.7622
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CROWTHORNE PRIMARY | MINIMUM HEADROOM | SU 84470 64352 | NO | NO | 2.351 | 30.3444 | 29.5944 | 28.9995 | 28.4362 | 27.4015 | 25.8015 | 24.0311 | 22.2893 | 20.6801 | 15.4842 | 12.2821 | 11.3648 | 44.2062 | 43.5113 | 42.9777 | 42.4521 | 41.4695 | 40.2715 | 38.8501 | 37.4664 | 36.145 | 32.0185 | 29.3542 | 25.4266 | 31.0534 | 30.4228 | 29.934 | 29.4574 | 28.434 | 27.0217 | 25.4177 | 23.8421 | 22.3534 | 17.7523 | 15.2187 | 14.7605
|  | CROWTHORNE PRIMARY | EE |  |  |  |  | 30.3444 | 29.5974 | 29.0332 | 28.6036 | 27.9423 | 26.4872 | 24.6791 | 22.9219 | 21.3321 | 16.2423 | 13.1311 | 12.2923 | 44.2072 | 43.5215 | 43.0246 | 42.5654 | 41.8746 | 40.8205 | 39.4226 | 38.0807 | 36.8307 | 32.095 | 29.3542 | 28.0287 | 31.0564 | 30.4279 | 29.9626 | 29.5819 | 28.9646 | 27.6962 | 26.0779 | 24.5095 | 23.0758 | 18.334 | 15.7656 | 15.3003
|  | CROWTHORNE PRIMARY | HT |  |  |  |  | 30.3464 | 29.5944 | 28.9995 | 28.4362 | 27.4015 | 25.8015 | 24.0311 | 22.2893 | 20.6801 | 15.4842 | 12.2821 | 11.3648 | 44.2072 | 43.5113 | 42.9777 | 42.4521 | 41.4695 | 40.2715 | 38.8501 | 37.4664 | 36.145 | 32.0185 | 30.0093 | 29.7409 | 31.0554 | 30.4228 | 29.934 | 29.4574 | 28.434 | 27.0217 | 25.4177 | 23.8421 | 22.3534 | 17.7523 | 15.2187 | 14.7605
|  | CROWTHORNE PRIMARY | HE |  |  |  |  | 30.3444 | 29.5944 | 29.0281 | 28.5934 | 27.9107 | 26.4219 | 24.6056 | 22.825 | 21.2117 | 16.6179 | 13.9546 | 13.1607 | 44.2062 | 43.5174 | 43.0226 | 42.5593 | 41.8603 | 40.7919 | 39.4195 | 38.0787 | 36.8317 | 32.495 | 30.1419 | 28.596 | 31.0534 | 30.4248 | 29.9605 | 29.5738 | 28.9401 | 27.6462 | 26.0319 | 24.4523 | 23.0126 | 18.733 | 16.6013 | 16.0615
|  | CROWTHORNE PRIMARY | FB |  |  |  |  | 30.625 | 30.1372 | 29.8423 | 29.6862 | 29.5066 | 29.0495 | 28.2699 | 27.4495 | 26.6811 | 22.6281 | 19.1995 | 17.7628 | 44.3613 | 43.8521 | 43.5093 | 43.2072 | 42.8817 | 42.3634 | 41.5185 | 40.6766 | 39.8664 | 35.0083 | 30.0144 | 25.4266 | 31.3217 | 30.9595 | 30.7432 | 30.6013 | 30.4523 | 30.0656 | 29.2921 | 28.5238 | 27.8044 | 23.784 | 20.5217 | 19.1442
COWLEY GSP |  | CULHAM PRIMARY | MINIMUM HEADROOM | SU 50731 95053 | NO | NO | 19.2 | 16.2808 | 16.2808 | 16.2798 | 16.2798 | 16.2788 | 16.2778 | 16.2788 | 16.2737 | 16.2747 | 15.6696 | 15.6614 | 15.6573 | 16.3839 | 16.3829 | 16.3829 | 16.3829 | 16.3818 | 16.3818 | 16.3818 | 16.3798 | 16.3808 | 15.6461 | 15.642 | 15.639 | 15.2196 | 15.2196 | 15.2196 | 15.2186 | 15.2186 | 15.2176 | 15.2165 | 15.2135 | 15.2114 | 14.6502 | 14.6431 | 14.639
|  | CULHAM PRIMARY | EE |  |  |  |  | 16.2818 | 16.2818 | 16.2818 | 16.2808 | 16.2808 | 16.2798 | 16.2798 | 16.2737 | 16.2747 | 15.6696 | 15.6614 | 15.6573 | 16.3849 | 16.3839 | 16.3849 | 16.3849 | 16.3849 | 16.3849 | 16.3849 | 16.3798 | 16.3808 | 15.6461 | 15.642 | 15.639 | 15.2196 | 15.2206 | 15.2196 | 15.2186 | 15.2196 | 15.2186 | 15.2176 | 15.2135 | 15.2114 | 14.6502 | 14.6431 | 14.639
|  | CULHAM PRIMARY | HT |  |  |  |  | 16.2818 | 16.2818 | 16.2818 | 16.2808 | 16.2808 | 16.2808 | 16.2798 | 16.2747 | 16.2757 | 15.6727 | 15.6655 | 15.6604 | 16.3849 | 16.3839 | 16.3849 | 16.3849 | 16.3849 | 16.3859 | 16.3859 | 16.3818 | 16.3839 | 15.6512 | 15.6471 | 15.6441 | 15.2196 | 15.2206 | 15.2196 | 15.2186 | 15.2196 | 15.2186 | 15.2176 | 15.2135 | 15.2124 | 14.6522 | 14.6451 | 14.64
|  | CULHAM PRIMARY | HE |  |  |  |  | 16.2818 | 16.2818 | 16.2818 | 16.2808 | 16.2808 | 16.2808 | 16.2798 | 16.2747 | 16.2757 | 15.6798 | 15.6818 | 15.6829 | 16.3849 | 16.3839 | 16.3849 | 16.3849 | 16.3849 | 16.3859 | 16.3859 | 16.3818 | 16.3839 | 15.6594 | 15.6655 | 15.6706 | 15.2196 | 15.2206 | 15.2196 | 15.2186 | 15.2196 | 15.2186 | 15.2176 | 15.2135 | 15.2124 | 14.6563 | 14.6553 | 14.6543
|  | CULHAM PRIMARY | FB |  |  |  |  | 16.2808 | 16.2808 | 16.2798 | 16.2798 | 16.2788 | 16.2778 | 16.2788 | 16.2778 | 16.2767 | 16.2716 | 15.6931 | 15.6931 | 16.3839 | 16.3829 | 16.3829 | 16.3829 | 16.3818 | 16.3818 | 16.3818 | 16.3818 | 16.3818 | 16.3778 | 15.6573 | 15.6584 | 15.2206 | 15.2196 | 15.2196 | 15.2186 | 15.2186 | 15.2176 | 15.2165 | 15.2176 | 15.2165 | 15.2114 | 14.6706 | 14.6706
EALING GSP | EALING BSP | DEAN GARDENS PRIMARY | MINIMUM HEADROOM | TQ 16546 80368 | YES | NO | 3.783 | 2.018 | 1.9669 | 2.0598 | 2.1231 | 1.871 | 1.5588 | 1.5159 | 1.4098 | 1.3027 | 1.0414 | 0.55469 | 0.30163 | 3.7312 | 3.7731 | 3.8394 | 3.8578 | 3.6516 | 3.3751 | 3.2129 | 3.0629 | 2.8863 | 1.5588 | -1.5127 | -6.4586 | 2.7884 | 2.8843 | 3.0506 | 3.1833 | 3.1088 | 2.9731 | 2.9976 | 2.9108 | 2.8169 | 2.8231 | 2.5496 | 2.4414
|  | DEAN GARDENS PRIMARY | EE |  |  |  |  | 2.018 | 1.9669 | 2.0598 | 2.1231 | 1.871 | 1.5588 | 1.5159 | 1.4098 | 1.3027 | 1.0414 | 0.55469 | 0.30163 | 3.7945 | 3.8914 | 4.0251 | 4.1139 | 4.0527 | 3.9363 | 3.9241 | 3.8271 | 3.7016 | 2.919 | 1.4465 | -0.62388 | 2.7884 | 2.8843 | 3.0506 | 3.1833 | 3.1088 | 2.9731 | 2.9976 | 2.9108 | 2.8169 | 2.8302 | 2.5496 | 2.4414
|  | DEAN GARDENS PRIMARY | HT |  |  |  |  | 2.0251 | 1.9782 | 2.0751 | 2.1343 | 1.8812 | 1.5894 | 1.5486 | 1.4455 | 1.3271 | 1.0598 | 0.71286 | 0.59551 | 3.7955 | 3.8904 | 4.0251 | 4.1159 | 4.0537 | 3.9445 | 3.9271 | 3.8282 | 3.6924 | 3.7118 | 3.3537 | 2.9098 | 2.7955 | 2.8945 | 3.0659 | 3.1935 | 3.1149 | 2.9924 | 3.0159 | 2.9261 | 2.819 | 2.8231 | 2.6527 | 2.6486
|  | DEAN GARDENS PRIMARY | HE |  |  |  |  | 2.0241 | 1.9761 | 2.0731 | 2.1312 | 1.8771 | 1.5761 | 1.5424 | 1.4476 | 1.3455 | 1.3435 | 1.1037 | 0.95571 | 3.7955 | 3.8935 | 4.0282 | 4.118 | 4.0578 | 3.9435 | 3.9353 | 3.8353 | 3.7098 | 3.0067 | 1.6139 | -0.41265 | 2.7945 | 2.8924 | 3.0639 | 3.1924 | 3.1159 | 2.9873 | 3.02 | 2.9363 | 2.8465 | 3.0608 | 2.9649 | 2.9506
|  | DEAN GARDENS PRIMARY | FB |  |  |  |  | 2.072 | 2.0404 | 2.1516 | 2.2424 | 2.02 | 1.7812 | 1.819 | 1.8618 | 1.8873 | 1.972 | 1.6976 | 1.3986 | 3.7312 | 3.7731 | 3.8394 | 3.8578 | 3.6516 | 3.3751 | 3.2129 | 3.0629 | 2.8863 | 1.5588 | -1.5127 | -6.4586 | 2.8394 | 2.9465 | 3.1322 | 3.2894 | 3.2353 | 3.1527 | 3.2414 | 3.3302 | 3.4037 | 3.7118 | 3.5608 | 3.3567
COWLEY GSP | YARNTON BSP | DEDDINGTON PRIMARY | MINIMUM HEADROOM | SP 46729 30325 | NO | YES | 0.7 | 2.3133 | 2.2888 | 2.2898 | 2.052 | 1.8408 | 1.4286 | 0.98878 | 0.62857 | 0.21837 | -0.7602 | -1.599 | -1.9888 | 3.6163 | 3.5776 | 3.549 | 3.2806 | 3.0918 | 2.8959 | 2.6082 | 2.4276 | 2.1694 | 1.4714 | 0.86327 | 0.57959 | 2.8367 | 2.8082 | 2.7939 | 2.5735 | 2.4061 | 2.1133 | 1.7745 | 1.5306 | 1.2112 | 0.39796 | -0.24184 | -0.46531
|  | DEDDINGTON PRIMARY | EE |  |  |  |  | 2.3133 | 2.2888 | 2.2898 | 2.0643 | 1.9286 | 1.5827 | 1.1347 | 0.68469 | 0.22653 | -0.7602 | -1.599 | -1.9531 | 3.6163 | 3.5776 | 3.5531 | 3.2837 | 3.1724 | 3.0122 | 2.7582 | 2.5122 | 2.248 | 1.4714 | 0.86327 | 0.57959 | 2.8367 | 2.8082 | 2.7939 | 2.5827 | 2.4837 | 2.2408 | 1.9041 | 1.5622 | 1.2112 | 0.39796 | -0.24184 | -0.46531
|  | DEDDINGTON PRIMARY | HT |  |  |  |  | 2.3306 | 2.3173 | 2.3041 | 2.099 | 1.8408 | 1.4286 | 0.98878 | 0.73061 | 0.40306 | -0.57755 | -1.498 | -1.9888 | 3.6173 | 3.5786 | 3.549 | 3.2806 | 3.0918 | 2.8959 | 2.6082 | 2.4276 | 2.1694 | 1.5163 | 1.0418 | 0.93061 | 2.8459 | 2.8255 | 2.8092 | 2.5918 | 2.4061 | 2.1133 | 1.7745 | 1.5582 | 1.2796 | 0.4898 | -0.18061 | -0.4602
|  | DEDDINGTON PRIMARY | HE |  |  |  |  | 2.3173 | 2.2929 | 2.2929 | 2.052 | 1.9 | 1.5459 | 1.1429 | 0.62857 | 0.21837 | -0.63367 | -1.15 | -1.4643 | 3.6173 | 3.5776 | 3.551 | 3.2827 | 3.1684 | 2.9939 | 2.7684 | 2.5071 | 2.2816 | 1.5592 | 1.2704 | 0.95612 | 2.8378 | 2.8112 | 2.7939 | 2.5735 | 2.4622 | 2.2163 | 1.9133 | 1.5306 | 1.2184 | 0.50714 | 0.16429 | -0.045918
|  | DEDDINGTON PRIMARY | FB |  |  |  |  | 2.4143 | 2.4327 | 2.4327 | 2.4153 | 2.3929 | 2.3684 | 2.2602 | 1.9969 | 1.7571 | 1.0357 | 0.39592 | -0.026531 | 3.6673 | 3.6602 | 3.648 | 3.6388 | 3.602 | 3.552 | 3.4561 | 3.1388 | 2.9592 | 2.2561 | 1.4418 | 0.60306 | 2.9173 | 2.9296 | 2.9388 | 2.9378 | 2.9184 | 2.902 | 2.8378 | 2.5571 | 2.3673 | 1.7837 | 1.2163 | 0.85
IVER 132KV GSP | DENHAM BSP | DENHAM AVENUE PRIMARY | MINIMUM HEADROOM | TQ 03761 86587 | NO | YES | 3.058 | 2.7449 | 2.7551 | 2.7265 | 2.6347 | 27.3622 | 27.0439 | 26.6847 | 26.2459 | 25.8582 | 24.4265 | 23.2867 | 22.649 | 4.1816 | 4.1806 | 4.149 | 4.0929 | 27.1378 | 27.0122 | 26.8582 | 26.6673 | 26.4959 | 25.7612 | 25.0031 | 23.5296 | 3.8092 | 3.8071 | 3.7745 | 3.7051 | 27.4633 | 27.2255 | 26.9296 | 26.5214 | 26.1847 | 25.0071 | 24.2612 | 23.9398
|  | DENHAM AVENUE PRIMARY | EE |  |  |  |  | 2.7449 | 2.7592 | 2.751 | 2.702 | 27.4806 | 27.2061 | 26.8837 | 26.4653 | 26.099 | 24.6541 | 23.4776 | 22.8 | 4.1827 | 4.1816 | 4.1582 | 4.1163 | 27.1816 | 27.0745 | 26.9357 | 26.7643 | 26.6194 | 25.7612 | 25.0031 | 24.3296 | 3.8092 | 3.8092 | 3.7939 | 3.7347 | 27.5255 | 27.3245 | 27.0786 | 26.6847 | 26.3673 | 25.1745 | 24.3735 | 23.9837
|  | DENHAM AVENUE PRIMARY | HT |  |  |  |  | 2.7469 | 2.7551 | 2.7265 | 2.6347 | 27.3622 | 27.0439 | 26.6847 | 26.2459 | 25.8582 | 24.4265 | 23.2867 | 22.649 | 4.1827 | 4.1806 | 4.149 | 4.0929 | 27.1378 | 27.0122 | 26.8582 | 26.6673 | 26.4959 | 25.8357 | 25.4122 | 25.2459 | 3.8092 | 3.8071 | 3.7745 | 3.7051 | 27.4633 | 27.2255 | 26.9296 | 26.5214 | 26.1847 | 25.0071 | 24.2612 | 23.9398
|  | DENHAM AVENUE PRIMARY | HE |  |  |  |  | 2.7469 | 2.7592 | 2.752 | 2.6929 | 27.4622 | 27.1837 | 26.8541 | 26.4959 | 26.1531 | 25.0776 | 24.0143 | 23.4867 | 4.1816 | 4.1806 | 4.1582 | 4.1153 | 27.1796 | 27.0704 | 26.9367 | 26.7847 | 26.649 | 26.0571 | 25.2918 | 24.5786 | 3.8102 | 3.8092 | 3.7949 | 3.7276 | 27.5173 | 27.3102 | 27.0612 | 26.7684 | 26.4929 | 25.6204 | 24.8765 | 24.5439
|  | DENHAM AVENUE PRIMARY | FB |  |  |  |  | 2.8796 | 2.9245 | 2.9735 | 2.9969 | 27.8204 | 27.7847 | 27.801 | 27.7388 | 27.6745 | 27.15 | 26.3102 | 25.8888 | 4.248 | 4.2551 | 4.2551 | 4.2449 | 27.3082 | 27.2357 | 27.1959 | 27.1082 | 27.0163 | 26.3582 | 25.0469 | 23.5296 | 3.948 | 3.9816 | 4.0143 | 4.0337 | 27.8184 | 27.7724 | 27.7439 | 27.6939 | 27.6245 | 27.1378 | 26.4214 | 26.0765
MELKSHAM GSP | NORRINGTON BSP | DEVIZES PRIMARY | MINIMUM HEADROOM | SU 00106 60986 | NO | YES | 4.301 | 14.536 | 14.2319 | 13.6319 | 13.2452 | 12.6554 | 11.6809 | 10.5513 | 9.4452 | 8.3319 | 3.7482 | -0.39869 | -2.6926 | 18.6248 | 18.3044 | 17.7309 | 17.3829 | 16.834 | 16.1942 | 15.3156 | 14.5523 | 13.787 | 10.6738 | 8.0166 | 4.1972 | 16.5136 | 16.2615 | 15.6972 | 15.2921 | 14.6391 | 13.7615 | 12.6707 | 11.7146 | 10.7503 | 7.0217 | 4.0095 | 2.6493
|  | DEVIZES PRIMARY | EE |  |  |  |  | 14.536 | 14.2319 | 13.6452 | 13.3023 | 12.7564 | 11.838 | 10.7738 | 9.7687 | 8.7666 | 4.2533 | 0.19008 | -1.8436 | 18.6258 | 18.3044 | 17.7391 | 17.4187 | 16.8829 | 16.2993 | 15.4431 | 14.7452 | 14.0513 | 10.6738 | 8.0166 | 6.3931 | 16.5136 | 16.2625 | 15.7084 | 15.3401 | 14.7166 | 13.9013 | 12.8472 | 11.9748 | 11.1003 | 7.3401 | 4.2523 | 2.9656
|  | DEVIZES PRIMARY | HT |  |  |  |  | 14.536 | 14.234 | 13.6319 | 13.2452 | 12.6554 | 11.6809 | 10.5513 | 9.4452 | 8.3319 | 3.7482 | -0.39869 | -2.6926 | 18.6278 | 18.3064 | 17.7309 | 17.3829 | 16.834 | 16.1942 | 15.3156 | 14.5523 | 13.787 | 10.885 | 8.9554 | 8.3493 | 16.5136 | 16.2625 | 15.6972 | 15.2921 | 14.6391 | 13.7615 | 12.6707 | 11.7146 | 10.7503 | 7.0217 | 4.0095 | 2.6493
|  | DEVIZES PRIMARY | HE |  |  |  |  | 14.537 | 14.2319 | 13.6452 | 13.284 | 12.7217 | 11.7982 | 10.7421 | 9.7452 | 8.7217 | 5.0738 | 1.7197 | -0.010939 | 18.6248 | 18.3064 | 17.737 | 17.4136 | 16.8738 | 16.2768 | 15.4401 | 14.7595 | 14.0421 | 11.0605 | 8.9391 | 7.187 | 16.5146 | 16.2615 | 15.7064 | 15.3278 | 14.6921 | 13.8666 | 12.8299 | 11.9748 | 11.0768 | 8.0166 | 5.6299 | 4.4625
|  | DEVIZES PRIMARY | FB |  |  |  |  | 14.8503 | 14.6503 | 14.1707 | 14.1278 | 13.9289 | 13.6666 | 13.4411 | 13.2748 | 13.0401 | 11.0442 | 8.2044 | 6.3319 | 18.9207 | 18.5942 | 18.1166 | 17.9574 | 17.6391 | 17.2421 | 16.8033 | 16.4238 | 15.9013 | 12.8431 | 8.6972 | 4.1972 | 16.8452 | 16.6319 | 16.235 | 16.2044 | 16.0207 | 15.7442 | 15.4482 | 15.2238 | 14.8605 | 12.4625 | 9.7758 | 8.0707
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH PRIMARY | MINIMUM HEADROOM | SU 19288 83540 | NO | NO | 6.688 | 9.9067 | 9.9088 | 9.8782 | 9.8394 | 9.6639 | 9.368 | 9.0516 | 8.7588 | 8.4435 | 7.6322 | 6.9639 | 6.6373 | 11.2363 | 11.2241 | 11.1822 | 11.1516 | 10.9629 | 10.6965 | 10.4312 | 10.1812 | 9.9057 | 9.1731 | 8.5924 | 7.3669 | 10.2629 | 10.2516 | 10.2261 | 10.1843 | 10.0445 | 9.8271 | 9.519 | 9.2149 | 8.9404 | 8.2935 | 7.7812 | 7.5108
|  | DORCAN SOUTH PRIMARY | EE |  |  |  |  | 9.9067 | 9.9088 | 9.8782 | 9.8394 | 9.7098 | 9.5159 | 9.219 | 8.9496 | 8.6424 | 7.6322 | 6.9639 | 6.6373 | 11.2384 | 11.2241 | 11.1822 | 11.1527 | 11.0047 | 10.8455 | 10.5863 | 10.3649 | 10.0945 | 9.1731 | 8.5924 | 8.0894 | 10.2629 | 10.2516 | 10.2261 | 10.1843 | 10.1037 | 9.9741 | 9.7333 | 9.4588 | 9.1935 | 8.2945 | 7.7812 | 7.5108
|  | DORCAN SOUTH PRIMARY | HT |  |  |  |  | 9.9088 | 9.9129 | 9.8873 | 9.8465 | 9.6639 | 9.368 | 9.0516 | 8.7588 | 8.4435 | 7.6578 | 7.0292 | 6.7884 | 11.2363 | 11.2241 | 11.1833 | 11.1516 | 10.9629 | 10.6965 | 10.4312 | 10.1812 | 9.9057 | 9.3731 | 9.0027 | 8.8843 | 10.2659 | 10.2598 | 10.2384 | 10.1904 | 10.0445 | 9.8271 | 9.519 | 9.2149 | 8.9404 | 8.2935 | 7.8088 | 7.5965
|  | DORCAN SOUTH PRIMARY | HE |  |  |  |  | 9.9088 | 9.9139 | 9.8914 | 9.8496 | 9.7118 | 9.5322 | 9.2384 | 9.0139 | 8.6945 | 7.8945 | 7.5047 | 7.2618 | 11.2384 | 11.2241 | 11.1863 | 11.1547 | 11.0057 | 10.8445 | 10.5812 | 10.3955 | 10.1057 | 9.3251 | 8.8771 | 8.3935 | 10.2659 | 10.2598 | 10.2394 | 10.1935 | 10.1067 | 9.9853 | 9.7455 | 9.4914 | 9.222 | 8.4945 | 8.1833 | 7.9914
|  | DORCAN SOUTH PRIMARY | FB |  |  |  |  | 9.971 | 9.9843 | 10.0006 | 9.9904 | 9.9884 | 9.971 | 9.9108 | 9.8108 | 9.6822 | 8.9853 | 8.4965 | 7.9302 | 11.2669 | 11.2445 | 11.2261 | 11.1894 | 11.1455 | 11.0873 | 10.972 | 10.8312 | 10.6669 | 9.7108 | 8.7608 | 7.3669 | 10.2955 | 10.2996 | 10.3037 | 10.2873 | 10.272 | 10.2537 | 10.1812 | 10.0833 | 9.9567 | 9.2027 | 8.8159 | 8.4404
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER PRIMARY | MINIMUM HEADROOM | SY 69113 90401 | NO | NO | 3.209 | 10.3359 | 10.3155 | 10.1196 | 9.6808 | 9.1451 | 8.1226 | 6.8104 | 5.3553 | 4.1318 | -1.0498 | -5.6029 | -8.3753 | 12.9879 | 12.9226 | 12.7655 | 12.4665 | 12.0971 | 11.6318 | 11.0573 | 10.4022 | 9.7145 | 6.4277 | 3.5145 | 0.030804 | 10.941 | 10.94 | 10.7645 | 10.3573 | 9.8635 | 9.0135 | 8.0053 | 6.8502 | 5.9237 | 1.7492 | -1.7029 | -3.4865
|  | DORCHESTER PRIMARY | EE |  |  |  |  | 10.3502 | 10.3624 | 10.2186 | 9.8522 | 9.393 | 8.5084 | 7.2726 | 5.8971 | 4.7665 | -0.0794 | -4.4345 | -7.0865 | 12.9961 | 12.9533 | 12.8349 | 12.5941 | 12.2839 | 11.8879 | 11.39 | 10.8053 | 10.3033 | 6.543 | 3.5145 | 1.2747 | 10.9553 | 10.9839 | 10.8512 | 10.5165 | 10.0961 | 9.2961 | 8.3482 | 7.2543 | 6.4002 | 2.3859 | -1.0743 | -3.0151
|  | DORCHESTER PRIMARY | HT |  |  |  |  | 10.3359 | 10.3155 | 10.1196 | 9.6808 | 9.1451 | 8.1226 | 6.8104 | 5.3553 | 4.1318 | -1.0498 | -5.6029 | -8.3753 | 12.9879 | 12.9226 | 12.7655 | 12.4665 | 12.0971 | 11.6318 | 11.0573 | 10.4022 | 9.7145 | 6.4277 | 4.1328 | 3.1788 | 10.941 | 10.94 | 10.7645 | 10.3573 | 9.8635 | 9.0135 | 8.0053 | 6.8502 | 5.9237 | 1.7492 | -1.7029 | -3.4865
|  | DORCHESTER PRIMARY | HE |  |  |  |  | 10.3492 | 10.3635 | 10.2186 | 9.8328 | 9.3584 | 8.4665 | 7.2186 | 5.843 | 4.6971 | 0.96652 | -2.3039 | -4.1661 | 12.9951 | 12.9522 | 12.8318 | 12.59 | 12.2726 | 11.8849 | 11.3828 | 10.8043 | 10.2951 | 7.0798 | 4.8951 | 2.9237 | 10.9533 | 10.9828 | 10.8502 | 10.4971 | 10.0543 | 9.2747 | 8.3226 | 7.2379 | 6.3737 | 3.2665 | 0.8706 | -0.47634
|  | DORCHESTER PRIMARY | FB |  |  |  |  | 10.4941 | 10.5614 | 10.5696 | 10.5471 | 10.44 | 10.2553 | 10.0624 | 9.843 | 9.5879 | 7.5573 | 4.4747 | 2.2492 | 13.1206 | 13.1379 | 13.1094 | 13.0777 | 12.9686 | 12.8084 | 12.6502 | 12.4675 | 12.1094 | 8.9655 | 4.7655 | 0.030804 | 11.1471 | 11.1992 | 11.2206 | 11.2441 | 11.1788 | 11.0145 | 10.8328 | 10.6002 | 10.2645 | 8.0022 | 5.4226 | 3.3655
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | DOWN GRANGE PRIMARY | MINIMUM HEADROOM | SU 61604 50238 | NO | NO | 0.99 | 8.7541 | 8.2684 | 7.3153 | 6.2071 | 5.0153 | 3.1286 | 1.2929 | -0.58265 | -2.4143 | -9.2633 | -14.25 | -17.0163 | 14.3684 | 14.0939 | 13.6735 | 13.149 | 12.4745 | 11.5439 | 10.5082 | 9.3908 | 8.3184 | 4.2786 | 0.52143 | -6.2571 | 12.1867 | 11.8469 | 11.1888 | 10.4184 | 9.4571 | 8.0112 | 6.5408 | 5.0163 | 3.5408 | -1.6765 | -5.1571 | -7.2235
|  | DOWN GRANGE PRIMARY | EE |  |  |  |  | 8.7541 | 8.2684 | 7.3153 | 6.2071 | 5.1357 | 3.3602 | 1.4276 | -0.47959 | -2.3367 | -8.5316 | -12.8327 | -16.2765 | 14.3684 | 14.0939 | 13.6908 | 13.2337 | 12.6541 | 11.8092 | 10.7704 | 9.6418 | 8.5582 | 4.2786 | 1.1714 | -1.6918 | 12.1867 | 11.8469 | 11.1888 | 10.4704 | 9.6612 | 8.3327 | 6.8296 | 5.2765 | 3.7684 | -1.4898 | -5.1571 | -7.2235
|  | DOWN GRANGE PRIMARY | HT |  |  |  |  | 8.7786 | 8.349 | 7.4357 | 6.2265 | 5.0153 | 3.1286 | 1.2929 | -0.58265 | -2.4 | -9.2633 | -14.25 | -17.0163 | 14.3684 | 14.1031 | 13.6735 | 13.149 | 12.4745 | 11.5439 | 10.5082 | 9.3908 | 8.3184 | 5.0327 | 3.3571 | 2.6571 | 12.201 | 11.8939 | 11.2388 | 10.4184 | 9.4571 | 8.0112 | 6.5408 | 5.0163 | 3.5408 | -1.6765 | -5.148 | -6.8367
|  | DOWN GRANGE PRIMARY | HE |  |  |  |  | 8.7745 | 8.3092 | 7.3724 | 6.2276 | 5.101 | 3.3173 | 1.3827 | -0.55408 | -2.4143 | -7.8102 | -11.45 | -13.0755 | 14.3684 | 14.0959 | 13.6939 | 13.2378 | 12.6541 | 11.8173 | 10.7786 | 9.6276 | 8.6092 | 4.5112 | 1.5347 | -1.2449 | 12.199 | 11.8724 | 11.2286 | 10.4867 | 9.6459 | 8.3265 | 6.8224 | 5.251 | 3.7969 | -0.82143 | -3.7735 | -5.0582
|  | DOWN GRANGE PRIMARY | FB |  |  |  |  | 9.1235 | 8.9765 | 8.4816 | 8.0112 | 7.6071 | 7.1276 | 6.6765 | 6.1622 | 5.5367 | 1.899 | -1.0643 | -2.4143 | 14.5663 | 14.4776 | 14.2031 | 13.9418 | 13.6153 | 13.0969 | 12.5388 | 11.9265 | 11.2347 | 6.6133 | 0.52143 | -6.2571 | 12.6041 | 12.6194 | 12.3378 | 12.0847 | 11.8776 | 11.5265 | 11.1735 | 10.748 | 10.2194 | 6.7888 | 3.3337 | 1.4602
MINETY GSP | STRATTON (MAIN) BSP | DRAKES WAY PRIMARY | MINIMUM HEADROOM | SU 16899 85647 | NO | NO | 0.98 | 5.9107 | 5.7832 | 5.7138 | 5.6587 | 5.3801 | 5.0444 | 4.527 | 3.9913 | 3.577 | 2.6944 | 2.125 | 1.8474 | 8.6245 | 8.4888 | 8.4306 | 8.3929 | 8.0776 | 7.7357 | 7.1888 | 6.6173 | 6.202 | 5.2429 | 4.4092 | 2.851 | 7.1745 | 7.0327 | 6.9102 | 6.8143 | 6.4684 | 6.0908 | 5.5173 | 4.8867 | 4.4551 | 3.3949 | 2.6888 | 2.2908
|  | DRAKES WAY PRIMARY | EE |  |  |  |  | 5.9128 | 5.9117 | 5.7138 | 5.6587 | 5.5964 | 5.3638 | 4.9832 | 4.5117 | 4.1138 | 2.7311 | 2.2097 | 1.9474 | 8.6286 | 8.6286 | 8.4306 | 8.3929 | 8.3388 | 8.1143 | 7.7255 | 7.2327 | 6.8347 | 5.2429 | 4.4092 | 3.6878 | 7.1745 | 7.1653 | 6.9102 | 6.8143 | 6.6643 | 6.3806 | 5.9337 | 5.3704 | 4.9408 | 3.3949 | 2.6888 | 2.2908
|  | DRAKES WAY PRIMARY | HT |  |  |  |  | 5.9117 | 5.7832 | 5.7219 | 5.6689 | 5.3801 | 5.0444 | 4.527 | 3.9913 | 3.577 | 2.6944 | 2.125 | 1.8474 | 8.6245 | 8.4888 | 8.4316 | 8.3949 | 8.0776 | 7.7357 | 7.1888 | 6.6173 | 6.202 | 5.4327 | 4.8724 | 4.6306 | 7.1765 | 7.0327 | 6.9204 | 6.8224 | 6.4684 | 6.0908 | 5.5173 | 4.8867 | 4.4551 | 3.4296 | 2.7959 | 2.5337
|  | DRAKES WAY PRIMARY | HE |  |  |  |  | 5.9107 | 5.9158 | 5.7219 | 5.6668 | 5.6046 | 5.373 | 4.9852 | 4.5066 | 4.1158 | 3.0015 | 2.6301 | 2.4107 | 8.6245 | 8.6286 | 8.4306 | 8.3939 | 8.3408 | 8.1092 | 7.7041 | 7.1969 | 6.7878 | 5.651 | 5.0235 | 4.3653 | 7.1755 | 7.1724 | 6.9184 | 6.8214 | 6.6684 | 6.3827 | 5.9276 | 5.3643 | 4.9429 | 3.8561 | 3.4449 | 3.2031
|  | DRAKES WAY PRIMARY | FB |  |  |  |  | 5.9423 | 5.9597 | 5.973 | 5.8321 | 5.7811 | 5.7403 | 5.5791 | 5.3577 | 5.1454 | 3.7566 | 3.325 | 2.9801 | 8.6449 | 8.652 | 8.648 | 8.4796 | 8.4133 | 8.3531 | 8.1327 | 7.8551 | 7.5796 | 5.801 | 4.5735 | 2.851 | 7.2071 | 7.2194 | 7.2204 | 7.0704 | 6.9969 | 6.9347 | 6.7357 | 6.499 | 6.2714 | 4.7265 | 4.1327 | 3.4837
NURSLING GSP | WINCHESTER BSP | DUNBRIDGE PRIMARY | MINIMUM HEADROOM | SU 31520 26244 | NO | NO | 1.591 | 6.2559 | 10.5998 | 10.5467 | 10.3467 | 10.0722 | 9.6222 | 7.4804 | 5.4283 | 3.9538 | -3.0472 | -15.037 | -20.5288 | 8.8023 | 12.3987 | 12.2477 | 12.06 | 11.6273 | 11.1549 | 8.6896 | 6.1008 | 4.6018 | -3.6339 | -17.2829 | -23.9023 | 3.0243 | 6.8253 | 6.7314 | 6.5824 | 6.2661 | 5.7814 | 3.3243 | 0.88956 | -0.67982 | -8.7278 | -22.8227 | -29.3523
|  | DUNBRIDGE PRIMARY | EE |  |  |  |  | 6.2559 | 10.6743 | 10.5467 | 10.3712 | 10.1263 | 9.7181 | 8.5824 | 6.8334 | 3.9538 | -2.7186 | -15.037 | -20.5288 | 8.8054 | 12.4661 | 12.2508 | 12.0681 | 11.6549 | 11.1977 | 9.9661 | 7.9865 | 4.6018 | -2.9053 | -17.2829 | -23.9023 | 3.0243 | 6.8936 | 6.7314 | 6.5977 | 6.3018 | 5.8406 | 4.6253 | 2.6814 | -0.67982 | -8.187 | -22.8227 | -29.3523
|  | DUNBRIDGE PRIMARY | HT |  |  |  |  | 6.26 | 10.5998 | 10.5477 | 10.412 | 10.1845 | 9.7967 | 7.6518 | 5.4283 | 4.8263 | -3.0472 | -7.1033 | -17.2951 | 8.8023 | 12.3987 | 12.2528 | 12.0661 | 11.6273 | 11.1549 | 8.6896 | 6.1008 | 5.5416 | -3.6339 | -7.6145 | -19.5023 | 3.0243 | 6.8253 | 6.7406 | 6.5977 | 6.3059 | 5.8549 | 3.4253 | 0.88956 | 0.36916 | -8.7278 | -13.0808 | -25.4002
|  | DUNBRIDGE PRIMARY | HE |  |  |  |  | 6.259 | 10.6804 | 10.5559 | 10.3467 | 10.0722 | 9.6222 | 7.4804 | 6.86 | 6.2436 | -2.2921 | -9.6829 | -15.4421 | 8.8033 | 12.4641 | 12.2477 | 12.06 | 11.6436 | 11.1794 | 8.7253 | 8.1865 | 7.6538 | -2.6319 | -10.9349 | -17.8737 | 3.0243 | 6.8947 | 6.7314 | 6.5824 | 6.2661 | 5.7814 | 3.3243 | 2.7896 | 2.2641 | -7.8737 | -16.5074 | -23.3951
|  | DUNBRIDGE PRIMARY | FB |  |  |  |  | 6.3732 | 10.9232 | 10.8753 | 10.7549 | 10.7253 | 10.663 | 10.1936 | 9.5212 | 7.959 | 2.9528 | -3.8594 | -9.9676 | 8.936 | 12.9161 | 12.6161 | 12.4641 | 12.3436 | 12.2681 | 11.5987 | 10.6814 | 8.6559 | 2.4977 | -5.9472 | -14.1594 | 3.1906 | 7.3028 | 7.1569 | 7.0569 | 6.9957 | 6.9559 | 6.3651 | 5.4987 | 3.5222 | -2.3462 | -10.3257 | -17.739
EALING GSP |  | EALING PRIMARY | MINIMUM HEADROOM | SZ 06789 95116 | NO | NO | 17.45 | 62.5956 | 62.1242 | 61.3548 | 60.564 | 59.7007 | 58.6681 | 57.4263 | 56.0967 | 54.5385 | 48.712 | 44.7456 | 42.465 | 65.7916 | 65.3303 | 64.8661 | 64.2293 | 63.513 | 62.663 | 61.6671 | 60.5773 | 59.2844 | 54.4232 | 48.0344 | 38.4895 | 61.3875 | 61.0212 | 60.3824 | 59.7518 | 58.9548 | 57.9038 | 56.6987 | 55.4273 | 53.9181 | 48.6232 | 44.6875 | 42.6803
|  | EALING PRIMARY | EE |  |  |  |  | 62.5956 | 62.1436 | 61.3548 | 60.564 | 59.7252 | 58.7344 | 57.6201 | 56.4814 | 55.2058 | 49.2997 | 44.7456 | 42.465 | 65.7946 | 65.4416 | 64.8661 | 64.2324 | 63.5558 | 62.8365 | 61.962 | 61.0518 | 59.9344 | 54.4232 | 50.0895 | 46.0844 | 61.3875 | 61.0405 | 60.3824 | 59.7518 | 58.961 | 57.9977 | 56.8946 | 55.812 | 54.561 | 48.8752 | 44.6875 | 42.6803
|  | EALING PRIMARY | HT |  |  |  |  | 62.6201 | 62.1242 | 61.4405 | 60.6385 | 59.762 | 58.6681 | 57.4263 | 56.0967 | 54.5385 | 48.712 | 44.8079 | 43.3875 | 65.7916 | 65.3303 | 64.8681 | 64.2293 | 63.513 | 62.663 | 61.6671 | 60.5773 | 59.2844 | 55.3865 | 52.9456 | 51.8385 | 61.412 | 61.0212 | 60.4661 | 59.815 | 58.9793 | 57.9038 | 56.6987 | 55.4273 | 53.9181 | 48.6232 | 45.1885 | 44.1548
|  | EALING PRIMARY | HE |  |  |  |  | 62.612 | 62.1783 | 61.4089 | 60.5793 | 59.7007 | 58.8558 | 57.7303 | 56.6477 | 55.3895 | 50.9905 | 47.9334 | 46.415 | 65.7926 | 65.4416 | 64.8742 | 64.2385 | 63.563 | 62.8967 | 61.9865 | 61.065 | 59.911 | 54.9599 | 51.161 | 47.5579 | 61.4048 | 61.0752 | 60.4365 | 59.7722 | 58.9548 | 58.1395 | 56.9793 | 55.9242 | 54.6793 | 50.3936 | 47.6058 | 46.3854
|  | EALING PRIMARY | FB |  |  |  |  | 62.9518 | 62.5538 | 62.0538 | 61.6405 | 60.9191 | 60.4375 | 60.0854 | 59.7548 | 59.3375 | 56.5252 | 52.7242 | 49.8528 | 65.8977 | 65.5028 | 64.9048 | 64.4365 | 63.5834 | 62.8416 | 62.1507 | 61.4497 | 60.6956 | 55.4283 | 48.0344 | 38.4895 | 61.7405 | 61.4416 | 61.0569 | 60.7824 | 60.1956 | 59.7497 | 59.3589 | 59.0344 | 58.5375 | 55.3028 | 51.4507 | 48.6079
LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT PRIMARY | MINIMUM HEADROOM | TQ 08394 73826 | NO | NO | 17.259 | 6.902 | 6.9 | 6.8724 | 6.7184 | 6.499 | 6.1194 | 5.5551 | 4.7398 | 3.852 | 0.032653 | -1.8163 | -2.5102 | 12.2765 | 12.2439 | 12.2776 | 12.1082 | 11.8735 | 11.4786 | 10.8796 | 10.0061 | 9.1816 | 4.6857 | 2.0255 | -1.048 | 10.2969 | 10.3163 | 10.3939 | 10.15 | 9.9316 | 9.4765 | 8.848 | 7.9296 | 7.0745 | 2.8531 | 0.58571 | -0.28265
|  | EAST BEDFONT PRIMARY | EE |  |  |  |  | 6.902 | 6.9 | 6.8724 | 6.7184 | 6.5653 | 6.2714 | 5.5551 | 4.7541 | 3.9837 | 0.032653 | -1.8163 | -2.5102 | 12.2765 | 12.2551 | 12.2776 | 12.1082 | 11.9745 | 11.6663 | 10.8796 | 10.0061 | 9.1827 | 4.6857 | 2.0255 | -0.11224 | 10.2969 | 10.3163 | 10.3939 | 10.15 | 10.0184 | 9.651 | 8.848 | 7.9296 | 7.0745 | 2.8531 | 0.58571 | -0.28265
|  | EAST BEDFONT PRIMARY | HT |  |  |  |  | 6.9214 | 6.9316 | 6.9388 | 6.7776 | 6.499 | 6.1194 | 5.5939 | 4.7398 | 3.852 | 0.85918 | -0.62959 | -1.0776 | 12.2806 | 12.2439 | 12.2816 | 12.1153 | 11.8735 | 11.4786 | 10.9724 | 10.0857 | 9.1816 | 6.3878 | 5.0908 | 4.5704 | 10.3112 | 10.3337 | 10.4408 | 10.1867 | 9.9316 | 9.4765 | 8.9531 | 8.0041 | 7.0878 | 4.0214 | 2.5173 | 2.201
|  | EAST BEDFONT PRIMARY | HE |  |  |  |  | 6.9133 | 6.9296 | 6.9143 | 6.7439 | 6.5735 | 6.2918 | 5.8959 | 5.352 | 4.8061 | 2.1153 | 1.0867 | 0.55918 | 12.2816 | 12.2602 | 12.2837 | 12.1133 | 11.9765 | 11.6735 | 11.2786 | 10.7153 | 10.1633 | 6.9612 | 5.1286 | 3.15 | 10.3122 | 10.3429 | 10.4316 | 10.1765 | 10.0265 | 9.6704 | 9.2663 | 8.6857 | 8.1255 | 5.5092 | 4.4745 | 3.9112
|  | EAST BEDFONT PRIMARY | FB |  |  |  |  | 7.0194 | 7.102 | 7.1735 | 7.1643 | 7.1663 | 7.1255 | 7.0092 | 6.7684 | 6.5755 | 4.2469 | 2.8163 | 1.9408 | 12.3224 | 12.3143 | 12.2847 | 12.2071 | 12.1367 | 11.9245 | 11.6327 | 11.202 | 10.8418 | 7.4561 | 3.6541 | -1.048 | 10.4776 | 10.5939 | 10.6796 | 10.7306 | 10.8408 | 10.8245 | 10.7357 | 10.3816 | 10.2071 | 8.0031 | 6.1847 | 4.9194
MANNINGTON GSP | REDHILL BSP | EAST HOWE PRIMARY | MINIMUM HEADROOM | SZ 06789 95116 | NO | NO | 8.334 | -0.31532 | -0.70206 | -1.1765 | -1.8337 | -2.5602 | -4.35 | -6.3072 | -8.2735 | -10.2827 | -16.6663 | -21.3368 | -23.5837 | 4.5618 | 4.173 | 3.8546 | 3.42 | 2.9138 | 2.0475 | 1.0016 | 0.0046449 | -1.1005 | -4.2515 | -6.7025 | -12.3352 | 2.0432 | 1.633 | 1.2432 | 0.66871 | 0.022788 | -1.3395 | -2.8517 | -4.3313 | -5.9037 | -10.8017 | -13.9558 | -15.168
|  | EAST HOWE PRIMARY | EE |  |  |  |  | -0.30206 | -0.62145 | -1.05 | -1.4806 | -2.0347 | -3.4817 | -5.0959 | -6.7408 | -8.3908 | -13.8959 | -18.1398 | -20.5 | 4.5781 | 4.2291 | 3.9291 | 3.6046 | 3.1424 | 2.4679 | 1.5618 | 0.6873 | -0.24944 | -4.0127 | -6.5045 | -8.5872 | 2.0534 | 1.6932 | 1.3238 | 0.92075 | 0.38707 | -0.70782 | -2.0007 | -3.2752 | -4.5803 | -9.0629 | -12.1221 | -13.6313
|  | EAST HOWE PRIMARY | HT |  |  |  |  | -0.31532 | -0.70206 | -1.1765 | -1.8337 | -2.5602 | -4.35 | -6.3072 | -8.2735 | -10.2827 | -16.6663 | -21.3368 | -23.5837 | 4.5618 | 4.173 | 3.8546 | 3.42 | 2.9138 | 2.0475 | 1.0016 | 0.0046449 | -1.1005 | -4.2515 | -5.7127 | -6.0566 | 2.0432 | 1.633 | 1.2432 | 0.66871 | 0.022788 | -1.3395 | -2.8517 | -4.3313 | -5.9037 | -10.8017 | -13.9558 | -15.168
|  | EAST HOWE PRIMARY | HE |  |  |  |  | -0.29594 | -0.60206 | -1.0153 | -1.4908 | -2.051 | -3.4265 | -4.9694 | -6.5327 | -8.1051 | -12.7439 | -16.4388 | -18.3806 | 4.5781 | 4.2353 | 3.9567 | 3.5985 | 3.171 | 2.4832 | 1.5802 | 0.72199 | -0.1974 | -3.5964 | -5.9413 | -8.2382 | 2.0575 | 1.7105 | 1.3656 | 0.91258 | 0.39218 | -0.67415 | -1.9221 | -3.1405 | -4.3966 | -8.1629 | -10.7313 | -12.0619
|  | EAST HOWE PRIMARY | FB |  |  |  |  | 0.016308 | 0.064267 | 0.054063 | -0.010222 | -0.096957 | -0.2541 | -0.45002 | -0.71634 | -1 | -3.401 | -6.8908 | -9.1092 | 4.6822 | 4.6006 | 4.5404 | 4.2404 | 3.9648 | 3.5608 | 3.1353 | 2.6169 | 2.072 | -1.5903 | -6.7025 | -12.3352 | 2.3565 | 2.3799 | 2.4156 | 2.2442 | 2.1371 | 1.9381 | 1.7136 | 1.4003 | 1.0687 | -1.4364 | -4.6374 | -6.6905
MELKSHAM GSP | NORRINGTON BSP | EASTERTON PRIMARY | MINIMUM HEADROOM | SU 01568 54730 | NO | YES | 1.567 | 5.7038 | 5.7619 | 5.764 | 5.4803 | 5.2028 | 4.8089 | 4.3385 | 3.865 | 3.4221 | 2.0926 | 1.1997 | 0.49561 | 8.1727 | 8.139 | 8.092 | 7.9135 | 7.7757 | 7.5176 | 7.1553 | 6.8094 | 6.4747 | 5.4369 | 4.8757 | 3.4706 | 6.541 | 6.5522 | 6.5053 | 6.242 | 5.9767 | 5.6349 | 5.1951 | 4.7818 | 4.3665 | 3.1471 | 2.5257 | 2.292
|  | EASTERTON PRIMARY | EE |  |  |  |  | 5.7038 | 5.7619 | 5.764 | 5.4915 | 5.2283 | 4.8313 | 4.4017 | 3.9191 | 3.5262 | 2.1201 | 1.3089 | 0.94357 | 8.1727 | 8.139 | 8.092 | 7.9247 | 7.8002 | 7.5176 | 7.1859 | 6.8094 | 6.5186 | 5.4869 | 4.8757 | 4.4196 | 6.541 | 6.5522 | 6.5053 | 6.2512 | 5.9971 | 5.638 | 5.2451 | 4.8012 | 4.4471 | 3.2022 | 2.6104 | 2.5267
|  | EASTERTON PRIMARY | HT |  |  |  |  | 5.7048 | 5.7701 | 5.767 | 5.4803 | 5.2028 | 4.8232 | 4.3395 | 3.8834 | 3.4221 | 2.0926 | 1.1997 | 0.49561 | 8.1727 | 8.14 | 8.0931 | 7.9135 | 7.7757 | 7.5237 | 7.1553 | 6.8186 | 6.4747 | 5.4369 | 5.1073 | 5.0808 | 6.541 | 6.5553 | 6.5073 | 6.242 | 5.9767 | 5.638 | 5.1951 | 4.7839 | 4.3665 | 3.1471 | 2.5257 | 2.292
|  | EASTERTON PRIMARY | HE |  |  |  |  | 5.7038 | 5.7691 | 5.7691 | 5.5395 | 5.2028 | 4.8089 | 4.3385 | 3.865 | 3.4364 | 2.3344 | 1.5844 | 1.1548 | 8.1727 | 8.141 | 8.092 | 7.9737 | 7.7951 | 7.5318 | 7.1767 | 6.8247 | 6.5124 | 5.6084 | 5.0655 | 4.5135 | 6.541 | 6.5543 | 6.5094 | 6.3043 | 5.9839 | 5.6349 | 5.2094 | 4.7818 | 4.3992 | 3.3716 | 2.8584 | 2.6808
|  | EASTERTON PRIMARY | FB |  |  |  |  | 5.813 | 5.8936 | 5.967 | 6.0017 | 5.964 | 5.9987 | 5.913 | 5.7946 | 5.4589 | 4.3221 | 3.2905 | 2.7619 | 8.2757 | 8.2737 | 8.2614 | 8.2298 | 8.1737 | 8.141 | 8.0155 | 7.8716 | 7.5359 | 6.3471 | 4.9522 | 3.4706 | 6.6747 | 6.7329 | 6.7798 | 6.7482 | 6.6798 | 6.7104 | 6.6186 | 6.4961 | 6.1553 | 5.0502 | 4.0767 | 3.5778
FLEET-BRAMLEY GSP | BRACKNELL BSP | EASTHAMPSTEAD PRIMARY | MINIMUM HEADROOM | SU 86148 67194 | NO | NO | 3.474 | 10.0533 | 10.3095 | 10.2768 | 9.8605 | 9.2013 | 8.2207 | 7.2431 | 6.0656 | 4.8289 | -0.40482 | -5.4997 | -8.963 | 13.3962 | 13.4982 | 13.3993 | 13.1472 | 12.6666 | 12.135 | 11.4799 | 10.6227 | 9.7421 | 5.4625 | 1.9217 | -3.8752 | 11.6911 | 11.8778 | 11.8523 | 11.5033 | 10.8064 | 10.0268 | 9.1503 | 8.0636 | 6.9584 | 2.3503 | -1.5803 | -3.9834
|  | EASTHAMPSTEAD PRIMARY | EE |  |  |  |  | 10.0533 | 10.3095 | 10.3523 | 10.0901 | 9.6309 | 8.6687 | 7.3748 | 6.0656 | 4.8289 | -0.40482 | -5.4997 | -8.963 | 13.3962 | 13.4982 | 13.4421 | 13.2666 | 12.9125 | 12.4095 | 11.5258 | 10.6227 | 9.7421 | 5.4625 | 1.9217 | -1.0946 | 11.6911 | 11.8778 | 11.8982 | 11.6799 | 11.1676 | 10.4084 | 9.234 | 8.0636 | 6.9584 | 2.3503 | -1.5803 | -3.9834
|  | EASTHAMPSTEAD PRIMARY | HT |  |  |  |  | 10.0595 | 10.3156 | 10.2768 | 9.8605 | 9.2013 | 8.2207 | 7.2431 | 6.1044 | 5.0207 | -0.01502 | -4.8701 | -8.4109 | 13.3993 | 13.5003 | 13.3993 | 13.1472 | 12.6666 | 12.135 | 11.4799 | 10.6584 | 9.8452 | 6.6248 | 4.3636 | 3.1176 | 11.6972 | 11.8819 | 11.8523 | 11.5033 | 10.8064 | 10.0268 | 9.1503 | 8.1105 | 7.1258 | 2.8064 | -0.79869 | -3.0977
|  | EASTHAMPSTEAD PRIMARY | HE |  |  |  |  | 10.0595 | 10.3187 | 10.3656 | 10.1187 | 9.6727 | 8.8023 | 7.7533 | 6.6615 | 5.6136 | 1.7676 | -2.3885 | -4.6813 | 13.3993 | 13.5023 | 13.4482 | 13.2778 | 12.9309 | 12.4421 | 11.7697 | 11.0544 | 10.3166 | 6.8574 | 3.7758 | 1.0646 | 11.6972 | 11.885 | 11.9095 | 11.7003 | 11.1952 | 10.488 | 9.5676 | 8.6227 | 7.6952 | 4.3013 | 1.1564 | -0.46502
|  | EASTHAMPSTEAD PRIMARY | FB |  |  |  |  | 10.3084 | 10.5952 | 10.8809 | 10.9952 | 11.0462 | 10.8768 | 10.6411 | 10.3676 | 10.0891 | 8.0095 | 4.2727 | 1.9156 | 13.4901 | 13.5248 | 13.5799 | 13.4942 | 13.3033 | 12.9503 | 12.5299 | 12.0891 | 11.6105 | 8.0462 | 2.4564 | -3.8752 | 11.935 | 12.1411 | 12.3605 | 12.4625 | 12.4972 | 12.3625 | 12.1309 | 11.8584 | 11.5625 | 9.2095 | 5.7748 | 3.6605
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH PRIMARY | MINIMUM HEADROOM | SU 45426 18958 | NO | YES | 5.402 | 9.6073 | 9.2431 | 8.6278 | 7.6482 | 6.3645 | 4.1584 | 1.6747 | -0.32531 | -2.2814 | -9.8784 | -15.4488 | -17.661 | 15.5349 | 15.2512 | 14.8676 | 14.2798 | 13.5349 | 12.5155 | 11.1369 | 9.8124 | 8.5869 | 4.3267 | 0.52061 | -6.4141 | 10.9216 | 10.5686 | 10.0257 | 9.2073 | 8.0747 | 6.4278 | 4.4073 | 2.6267 | 0.99714 | -4.9998 | -9.0631 | -10.2182
|  | EASTLEIGH NORTH PRIMARY | EE |  |  |  |  | 9.6073 | 9.2431 | 8.6278 | 7.6482 | 6.3757 | 4.1584 | 1.6747 | -0.27327 | -1.9906 | -8.7784 | -14.3569 | -16.8957 | 15.5369 | 15.2563 | 14.8747 | 14.3288 | 13.6257 | 12.641 | 11.3155 | 10.1124 | 9.0176 | 4.3267 | 0.72061 | -1.7345 | 10.9216 | 10.5686 | 10.0257 | 9.2073 | 8.1094 | 6.4339 | 4.4073 | 2.7961 | 1.3471 | -4.1886 | -8.4661 | -10.1304
|  | EASTLEIGH NORTH PRIMARY | HT |  |  |  |  | 9.6227 | 9.2818 | 8.7176 | 7.69 | 6.3859 | 4.2869 | 1.8431 | -0.32531 | -2.2814 | -9.8784 | -15.4488 | -17.661 | 15.538 | 15.2533 | 14.8706 | 14.2798 | 13.5349 | 12.5155 | 11.1369 | 9.8124 | 8.5869 | 4.591 | 2.2308 | 1.8135 | 10.9359 | 10.6043 | 10.0941 | 9.2165 | 8.0747 | 6.4451 | 4.4145 | 2.6267 | 0.99714 | -4.9998 | -9.0631 | -10.2182
|  | EASTLEIGH NORTH PRIMARY | HE |  |  |  |  | 9.6216 | 9.2747 | 8.6716 | 7.6676 | 6.3645 | 4.1706 | 1.7176 | -0.26204 | -1.9876 | -7.5998 | -11.8845 | -14.0702 | 15.5349 | 15.2512 | 14.8676 | 14.3145 | 13.6063 | 12.6176 | 11.2982 | 10.091 | 8.9829 | 4.6135 | 1.5227 | -1.1427 | 10.9349 | 10.5941 | 10.0624 | 9.2186 | 8.091 | 6.4278 | 4.4308 | 2.8012 | 1.3461 | -3.2855 | -6.461 | -7.9743
|  | EASTLEIGH NORTH PRIMARY | FB |  |  |  |  | 9.9257 | 9.8451 | 9.5594 | 9.1176 | 8.5359 | 7.589 | 6.6298 | 5.839 | 5.2165 | 1.8176 | -2.9682 | -6.1692 | 15.6543 | 15.5114 | 15.2349 | 14.8849 | 14.389 | 13.6186 | 12.8073 | 12.0604 | 11.3573 | 6.9839 | 0.52061 | -6.4141 | 11.2869 | 11.2288 | 10.9951 | 10.639 | 10.1563 | 9.3492 | 8.5288 | 7.8186 | 7.2073 | 3.7798 | -0.57837 | -3.4406
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY PRIMARY | MINIMUM HEADROOM | SZ 66357 99040 | NO | YES | 0.602 | 17.0726 | 17.0644 | 17.0512 | 16.9379 | 16.7134 | 16.3869 | 16.044 | 15.591 | 15.2359 | 13.4093 | 11.9297 | 11.1246 | 17.8175 | 17.7716 | 17.7053 | 17.5951 | 17.3665 | 17.1042 | 16.8277 | 16.4389 | 16.1451 | 14.2297 | 10.5604 | 5.4787 | 17.5706 | 17.5604 | 17.5287 | 17.4308 | 17.2287 | 16.9553 | 16.6787 | 16.2838 | 15.9981 | 14.4838 | 13.3848 | 12.7267
|  | EASTNEY PRIMARY | EE |  |  |  |  | 17.0726 | 17.0644 | 17.0512 | 16.9726 | 16.7808 | 16.4155 | 16.09 | 15.7053 | 15.3716 | 13.9338 | 12.1859 | 11.1655 | 17.8185 | 17.7777 | 17.7195 | 17.6297 | 17.4267 | 17.1206 | 16.8542 | 16.5206 | 16.2359 | 14.7206 | 12.6461 | 10.4093 | 17.5706 | 17.5604 | 17.5287 | 17.4655 | 17.3379 | 17.0348 | 16.793 | 16.49 | 16.2389 | 14.9144 | 13.5359 | 12.7267
|  | EASTNEY PRIMARY | HT |  |  |  |  | 17.0869 | 17.0879 | 17.0634 | 16.9379 | 16.7134 | 16.3869 | 16.044 | 15.591 | 15.2359 | 13.4093 | 11.9297 | 11.1246 | 17.8175 | 17.7716 | 17.7053 | 17.5951 | 17.3665 | 17.1042 | 16.8277 | 16.4389 | 16.1451 | 14.9757 | 14.1685 | 13.593 | 17.5777 | 17.5706 | 17.5287 | 17.4308 | 17.2287 | 16.9553 | 16.6787 | 16.2838 | 15.9981 | 14.4838 | 13.3848 | 12.7797
|  | EASTNEY PRIMARY | HE |  |  |  |  | 17.0889 | 17.093 | 17.094 | 16.9981 | 16.7848 | 16.4502 | 16.1573 | 15.7951 | 15.5216 | 14.2777 | 13.493 | 12.9665 | 17.8216 | 17.7797 | 17.7216 | 17.6348 | 17.4297 | 17.1216 | 16.8532 | 16.5144 | 16.2614 | 14.943 | 13.1246 | 10.9328 | 17.5808 | 17.5767 | 17.5532 | 17.4808 | 17.341 | 17.0614 | 16.842 | 16.5522 | 16.3481 | 15.2002 | 14.5195 | 14.1746
|  | EASTNEY PRIMARY | FB |  |  |  |  | 17.1573 | 17.1971 | 17.2297 | 17.2144 | 17.1879 | 17.1165 | 17.0604 | 16.9757 | 16.8757 | 15.8104 | 14.7257 | 13.7369 | 17.8287 | 17.7736 | 17.7114 | 17.6124 | 17.4512 | 17.2114 | 17.0022 | 16.7308 | 16.4389 | 14.2297 | 10.5604 | 5.4787 | 17.64 | 17.6859 | 17.7277 | 17.7114 | 17.6838 | 17.64 | 17.6012 | 17.5287 | 17.4471 | 16.5532 | 15.5063 | 14.5563
LALEHAM GSP | STAINES BSP | EGHAM PRIMARY | MINIMUM HEADROOM | TQ 01030 71404 | NO | NO | 4.555 | 5.952 | 5.9224 | 33.9133 | 33.7112 | 33.3643 | 32.849 | 32.2184 | 31.5133 | 30.7337 | 28.4939 | 27.2816 | 27.1724 | 9.6327 | 9.5449 | 35.9949 | 35.7735 | 35.4551 | 35.0694 | 34.5969 | 33.9286 | 33.1571 | 30.9959 | 29.3071 | 25.1888 | 6.4622 | 6.4337 | 33.5847 | 33.3194 | 32.9112 | 32.3745 | 31.7153 | 30.9673 | 30.202 | 27.902 | 26.7071 | 26.6173
|  | EGHAM PRIMARY | EE |  |  |  |  | 5.952 | 5.9224 | 33.9133 | 33.8673 | 33.7449 | 33.4163 | 33.0296 | 32.5 | 31.9378 | 29.7551 | 28.3092 | 27.7378 | 9.6347 | 9.548 | 35.998 | 35.8439 | 35.6224 | 35.3235 | 34.9673 | 34.4724 | 33.8276 | 31.2286 | 29.502 | 28.0888 | 6.4622 | 6.4337 | 33.5847 | 33.4378 | 33.2041 | 32.7898 | 32.3296 | 31.7408 | 31.1418 | 28.8082 | 27.3704 | 26.8143
|  | EGHAM PRIMARY | HT |  |  |  |  | 5.9561 | 5.9286 | 33.9255 | 33.7112 | 33.3643 | 32.849 | 32.2184 | 31.5133 | 30.7337 | 28.4939 | 27.2816 | 27.1724 | 9.6337 | 9.5469 | 35.9959 | 35.7735 | 35.4551 | 35.0694 | 34.5969 | 33.9286 | 33.1571 | 30.9959 | 30.0378 | 29.8602 | 6.4643 | 6.4418 | 33.598 | 33.3194 | 32.9112 | 32.3745 | 31.7153 | 30.9673 | 30.202 | 27.902 | 26.7071 | 26.6173
|  | EGHAM PRIMARY | HE |  |  |  |  | 5.9602 | 5.9367 | 33.9388 | 33.8816 | 33.7429 | 33.4347 | 33.0449 | 32.5255 | 31.9735 | 30.4051 | 29.2571 | 28.8561 | 9.6327 | 9.5449 | 35.9949 | 35.8388 | 35.6112 | 35.3133 | 34.95 | 34.4571 | 33.8082 | 31.6 | 29.8745 | 28.4735 | 6.4663 | 6.4459 | 33.6071 | 33.449 | 33.1908 | 32.799 | 32.3265 | 31.7571 | 31.1704 | 29.4643 | 28.2898 | 27.9082
|  | EGHAM PRIMARY | FB |  |  |  |  | 6.1796 | 6.1551 | 34.452 | 34.6827 | 34.6898 | 34.6286 | 34.5092 | 34.3959 | 34.2643 | 33.0224 | 30.9 | 29.3663 | 9.7714 | 9.7408 | 36.3724 | 36.4112 | 36.3235 | 36.2204 | 36.0827 | 35.8582 | 35.4969 | 32.9327 | 29.3071 | 25.1888 | 6.7071 | 6.6847 | 34.2388 | 34.4276 | 34.2816 | 34.1653 | 33.9837 | 33.8184 | 33.6347 | 32.1153 | 29.9408 | 28.3735
MANNINGTON GSP | BOURNEMOUTH BSP | ELECTRIC HOUSE PRIMARY | MINIMUM HEADROOM | SZ 08757 91379 | NO | YES | 4.559 | 8.2376 | 8.0948 | 7.7611 | 6.7876 | 6.3805 | 6.1162 | 5.9019 | 5.6907 | 5.458 | 2.6846 | 0.80293 | 0.63558 | 12.7121 | 12.5805 | 12.2723 | 11.6244 | 11.2091 | 10.7948 | 10.4376 | 10.0223 | 9.5784 | 6.4907 | 4.1233 | -0.22666 | 10.2091 | 10.0152 | 9.6488 | 8.7397 | 8.305 | 7.956 | 7.6642 | 7.2386 | 6.8427 | 4.0162 | 2.2101 | 2.0958
|  | ELECTRIC HOUSE PRIMARY | EE |  |  |  |  | 8.2386 | 8.0948 | 7.7611 | 6.7876 | 6.3805 | 6.1162 | 5.9386 | 5.6907 | 5.458 | 2.6846 | 0.80293 | 0.63558 | 12.7907 | 12.6509 | 12.3468 | 11.658 | 11.2091 | 10.7948 | 10.4958 | 10.0223 | 9.5784 | 6.4907 | 4.1233 | 2.9193 | 10.2091 | 10.0152 | 9.6488 | 8.7397 | 8.305 | 7.956 | 7.704 | 7.2386 | 6.8427 | 4.0162 | 2.2101 | 2.0958
|  | ELECTRIC HOUSE PRIMARY | HT |  |  |  |  | 8.2448 | 8.1152 | 7.804 | 6.9019 | 6.5458 | 6.2621 | 5.9805 | 5.7601 | 5.4958 | 3.0886 | 1.4468 | 1.2029 | 12.7968 | 12.6682 | 12.3713 | 11.6886 | 11.3448 | 10.9846 | 10.4948 | 10.258 | 9.8693 | 7.4448 | 5.9101 | 5.4662 | 10.2305 | 10.057 | 9.706 | 8.8295 | 8.4703 | 8.1601 | 7.7346 | 7.5019 | 7.1101 | 4.4764 | 2.9631 | 2.7642
|  | ELECTRIC HOUSE PRIMARY | HE |  |  |  |  | 8.2376 | 8.0988 | 7.7682 | 6.8213 | 6.4284 | 6.155 | 5.9019 | 5.708 | 5.4631 | 3.656 | 2.4182 | 2.3121 | 12.806 | 12.6856 | 12.404 | 11.7346 | 11.3162 | 10.9254 | 10.4376 | 10.1754 | 9.6988 | 7.2091 | 5.2682 | 4.0642 | 10.2356 | 10.0652 | 9.7264 | 8.8427 | 8.4284 | 8.1019 | 7.6642 | 7.4172 | 7.0019 | 4.9621 | 3.7835 | 3.7295
|  | ELECTRIC HOUSE PRIMARY | FB |  |  |  |  | 8.2815 | 8.2182 | 7.9754 | 7.205 | 6.9131 | 6.7631 | 6.7233 | 6.6091 | 6.5203 | 5.4244 | 4.208 | 2.6652 | 12.7121 | 12.5805 | 12.2723 | 11.6244 | 11.2529 | 10.9152 | 10.6907 | 10.3152 | 10.006 | 7.5897 | 4.2162 | -0.22666 | 10.254 | 10.1784 | 9.8866 | 9.1713 | 8.8856 | 8.6927 | 8.658 | 8.4886 | 8.3897 | 6.8968 | 5.3672 | 3.8713
FLEET-BRAMLEY GSP | WOKINGHAM BSP | ELMS ROAD PRIMARY | MINIMUM HEADROOM | SU 81057 68532 | NO | NO | 3.466 | 5.2583 | 5.3012 | 5.0859 | 4.5594 | 3.8226 | 2.6012 | 1.2992 | -0.1386 | -1.5988 | -5.9192 | -8.7427 | -10.2978 | 4.9792 | 4.8976 | 4.6721 | 4.2976 | 3.7476 | 3.1119 | 2.3404 | 1.4343 | 0.48737 | -2.231 | -4.2443 | -8.4902 | 5.2632 | 5.1856 | 4.9458 | 4.4581 | 3.7418 | 2.8203 | 1.7979 | 0.62645 | -0.58376 | -4.2052 | -6.3082 | -7.1756
|  | ELMS ROAD PRIMARY | EE |  |  |  |  | 5.2583 | 5.3298 | 5.2104 | 4.8757 | 4.3828 | 3.3257 | 2.1094 | 0.75323 | -0.59166 | -4.5447 | -7.2304 | -9.0172 | 4.9802 | 4.9139 | 4.7231 | 4.419 | 3.9761 | 3.4149 | 2.6935 | 1.8506 | 0.96798 | -2.2075 | -4.2443 | -5.9718 | 5.2632 | 5.203 | 5.0224 | 4.6571 | 4.1132 | 3.2979 | 2.3377 | 1.2387 | 0.104 | -3.4429 | -5.6164 | -6.8848
|  | ELMS ROAD PRIMARY | HT |  |  |  |  | 5.2614 | 5.3012 | 5.0859 | 4.5594 | 3.8226 | 2.6012 | 1.2992 | -0.1386 | -1.5988 | -5.9192 | -8.7427 | -10.2978 | 4.9792 | 4.8976 | 4.6721 | 4.2976 | 3.7476 | 3.1119 | 2.3404 | 1.4343 | 0.48737 | -2.231 | -3.5739 | -4.082 | 5.2652 | 5.1856 | 4.9458 | 4.4581 | 3.7418 | 2.8203 | 1.7979 | 0.62645 | -0.58376 | -4.2052 | -6.3082 | -7.1756
|  | ELMS ROAD PRIMARY | HE |  |  |  |  | 5.2624 | 5.3359 | 5.2257 | 4.8461 | 4.3104 | 3.3441 | 2.2043 | 0.90221 | -0.36207 | -3.5968 | -5.6519 | -6.957 | 4.9802 | 4.9088 | 4.72 | 4.4078 | 3.9547 | 3.4108 | 2.7017 | 1.8455 | 0.9792 | -1.8034 | -3.4983 | -5.0841 | 5.2673 | 5.2091 | 5.0356 | 4.6448 | 4.0683 | 3.3081 | 2.3969 | 1.3111 | 0.23257 | -2.6562 | -4.194 | -5.0848
|  | ELMS ROAD PRIMARY | FB |  |  |  |  | 5.6104 | 5.7645 | 5.7563 | 5.8206 | 5.7247 | 5.4594 | 5.1145 | 4.6318 | 4.2543 | 2.1481 | -0.41309 | -2.5437 | 5.2863 | 5.2568 | 4.9721 | 4.8914 | 4.6496 | 4.2884 | 3.8731 | 3.3455 | 2.9068 | -0.064673 | -3.9616 | -8.4902 | 5.7244 | 5.7999 | 5.5509 | 5.5448 | 5.3775 | 5.1173 | 4.7979 | 4.3346 | 3.9785 | 1.7509 | -0.76641 | -2.8399
LOVEDEAN GSP | HAVANT BSP | EMSWORTH PRIMARY | MINIMUM HEADROOM | SU 74861 05807 | NO | YES | 7.765 | -1.2702 | -1.3732 | -1.4008 | 13.6553 | 13.137 | 12.3298 | 11.4502 | 10.5002 | 9.6308 | 6.6359 | 4.9563 | 4.1512 | 0.95533 | 0.78492 | 0.7339 | 14.6553 | 14.2319 | 13.6298 | 12.9798 | 12.2717 | 11.6288 | 9.4217 | 7.3992 | 4.0614 | -0.43957 | -0.57018 | -0.59569 | 13.7176 | 13.2421 | 12.541 | 11.7859 | 10.9645 | 10.2155 | 7.6268 | 6.29 | 5.7329
|  | EMSWORTH PRIMARY | EE |  |  |  |  | -1.263 | -1.2334 | -1.2814 | 13.8757 | 13.4921 | 12.8298 | 12.041 | 11.2319 | 10.4829 | 7.587 | 5.888 | 5.041 | 0.95839 | 0.89716 | 0.79512 | 14.7635 | 14.4053 | 13.8972 | 13.2931 | 12.6574 | 12.0666 | 9.4604 | 7.8012 | 6.389 | -0.43345 | -0.44263 | -0.50998 | 13.8666 | 13.4992 | 12.9186 | 12.2278 | 11.5145 | 10.8502 | 8.2768 | 6.8717 | 6.2063
|  | EMSWORTH PRIMARY | HT |  |  |  |  | -1.2702 | -1.3732 | -1.4008 | 13.6553 | 13.137 | 12.3298 | 11.4502 | 10.5002 | 9.6308 | 6.6359 | 4.9563 | 4.1512 | 0.95533 | 0.78492 | 0.7339 | 14.6553 | 14.2319 | 13.6298 | 12.9798 | 12.2717 | 11.6288 | 9.4217 | 8.3451 | 7.8737 | -0.43957 | -0.57018 | -0.59569 | 13.7176 | 13.2421 | 12.541 | 11.7859 | 10.9645 | 10.2155 | 7.6268 | 6.29 | 5.7329
|  | EMSWORTH PRIMARY | HE |  |  |  |  | -1.2651 | -1.2365 | -1.2834 | 13.8645 | 13.4645 | 12.7778 | 11.9992 | 11.1931 | 10.4604 | 7.9431 | 6.4645 | 5.8472 | 0.95635 | 0.89512 | 0.789 | 14.7584 | 14.3931 | 13.8645 | 13.2696 | 12.6461 | 12.0778 | 9.6778 | 8.1441 | 6.7849 | -0.43651 | -0.44671 | -0.51202 | 13.8574 | 13.4798 | 12.8717 | 12.1982 | 11.4951 | 10.8574 | 8.6114 | 7.4166 | 6.9472
|  | EMSWORTH PRIMARY | FB |  |  |  |  | -1.0794 | -0.97631 | -0.9059 | 14.3727 | 14.3696 | 14.1155 | 13.7533 | 13.3717 | 13.0206 | 10.7359 | 8.7696 | 7.7584 | 1.0584 | 1.0349 | 0.98186 | 15.0043 | 14.8982 | 14.5737 | 14.1686 | 13.7543 | 13.3523 | 10.5666 | 7.3992 | 4.0614 | -0.25794 | -0.19263 | -0.15386 | 14.3268 | 14.2829 | 14.0951 | 13.8053 | 13.4717 | 13.1747 | 11.0268 | 9.1951 | 8.2441
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | ENFORD PRIMARY | MINIMUM HEADROOM | SU 13728 51712 | NO | NO | 0.269 | 7.0143 | 7.0051 | 6.9582 | 6.8929 | 6.7918 | 6.6724 | 6.5255 | 6.4969 | 6.3592 | 5.9837 | 5.7173 | 5.5204 | 7.401 | 7.3959 | 7.3755 | 7.3551 | 7.3306 | 7.2806 | 7.2184 | 7.1929 | 7.1337 | 6.9531 | 6.6878 | 6.1786 | 7.4633 | 7.4469 | 7.3959 | 7.3265 | 7.2327 | 7.1378 | 7.0051 | 6.9949 | 6.8735 | 6.5235 | 6.3429 | 6.2949
|  | ENFORD PRIMARY | EE |  |  |  |  | 7.0143 | 7.0051 | 6.9582 | 6.8939 | 6.7969 | 6.6857 | 6.5429 | 6.5214 | 6.3918 | 5.9837 | 5.7429 | 5.6571 | 7.401 | 7.3959 | 7.3765 | 7.3551 | 7.3347 | 7.2888 | 7.2286 | 7.2061 | 7.1541 | 6.9582 | 6.849 | 6.6929 | 7.4633 | 7.4469 | 7.3959 | 7.3265 | 7.2327 | 7.1439 | 7.0133 | 7.0071 | 6.8898 | 6.5337 | 6.3612 | 6.3367
|  | ENFORD PRIMARY | HT |  |  |  |  | 7.0153 | 7.0071 | 6.9612 | 6.899 | 6.802 | 6.6929 | 6.551 | 6.5265 | 6.3949 | 5.9908 | 5.7173 | 5.5204 | 7.402 | 7.3959 | 7.3755 | 7.3551 | 7.3306 | 7.2806 | 7.2184 | 7.1929 | 7.1337 | 6.9531 | 6.8837 | 6.8898 | 7.4633 | 7.449 | 7.3969 | 7.3296 | 7.2347 | 7.1449 | 7.0143 | 7.0041 | 6.8847 | 6.5235 | 6.3429 | 6.3224
|  | ENFORD PRIMARY | HE |  |  |  |  | 7.0153 | 7.0061 | 6.9592 | 6.8929 | 6.7918 | 6.6724 | 6.5255 | 6.4969 | 6.3592 | 6.0071 | 5.7357 | 5.6367 | 7.402 | 7.3969 | 7.3765 | 7.3561 | 7.3347 | 7.2867 | 7.2265 | 7.2031 | 7.152 | 6.9602 | 6.8398 | 6.6449 | 7.4633 | 7.4469 | 7.3959 | 7.3265 | 7.2398 | 7.1378 | 7.0051 | 6.9949 | 6.8735 | 6.5429 | 6.3459 | 6.2949
|  | ENFORD PRIMARY | FB |  |  |  |  | 7.0602 | 7.0735 | 7.0755 | 7.0592 | 7.0163 | 6.9939 | 6.952 | 6.9133 | 6.8684 | 6.6235 | 6.2724 | 6.1531 | 7.4265 | 7.4296 | 7.4276 | 7.4214 | 7.4071 | 7.3888 | 7.3633 | 7.3367 | 7.3061 | 7.1204 | 6.6878 | 6.1786 | 7.5071 | 7.5122 | 7.5061 | 7.4857 | 7.4398 | 7.4163 | 7.3633 | 7.3204 | 7.2745 | 7.0429 | 6.7122 | 6.6061
COWLEY GSP | YARNTON BSP | EYNSHAM PRIMARY | MINIMUM HEADROOM | SP 42236 10266 | NO | YES | 9.184 | 7.5079 | 7.4681 | 7.2813 | 7.1017 | 6.6232 | 5.8956 | 5.0242 | 4.2517 | 3.5221 | -0.72684 | -2.0136 | -2.2932 | 9.0344 | 8.9487 | 8.6558 | 8.4997 | 8.1109 | 7.5966 | 6.9762 | 6.4028 | 5.865 | 2.4783 | 1.4813 | -0.15235 | 8.0823 | 8.0415 | 7.7977 | 7.6242 | 7.1834 | 6.5895 | 5.8691 | 5.2181 | 4.5874 | 0.79357 | -0.31459 | -0.52684
|  | EYNSHAM PRIMARY | EE |  |  |  |  | 7.5323 | 7.514 | 7.3956 | 7.3007 | 7.0221 | 6.4211 | 5.6895 | 5.0528 | 4.413 | 0.62929 | -0.54112 | -0.88092 | 9.0507 | 8.9823 | 8.7374 | 8.6395 | 8.3497 | 7.9038 | 7.3579 | 6.865 | 6.3507 | 3.0283 | 1.8007 | 1.0364 | 8.1007 | 8.0793 | 7.9007 | 7.8048 | 7.4885 | 6.9823 | 6.3599 | 5.8099 | 5.2313 | 1.8762 | 0.81908 | 0.52214
|  | EYNSHAM PRIMARY | HT |  |  |  |  | 7.5079 | 7.4681 | 7.2813 | 7.1017 | 6.6232 | 5.8956 | 5.0242 | 4.2517 | 3.5221 | -0.72684 | -2.0136 | -2.2932 | 9.0344 | 8.9487 | 8.6558 | 8.4997 | 8.1109 | 7.5966 | 6.9762 | 6.4028 | 5.865 | 2.4783 | 1.4813 | 1.2334 | 8.0823 | 8.0415 | 7.7977 | 7.6242 | 7.1834 | 6.5895 | 5.8691 | 5.2181 | 4.5874 | 0.79357 | -0.31459 | -0.52684
|  | EYNSHAM PRIMARY | HE |  |  |  |  | 7.5313 | 7.513 | 7.3956 | 7.2987 | 7.0119 | 6.4344 | 5.6966 | 5.0783 | 4.415 | 0.79663 | -0.25949 | -0.39929 | 9.0497 | 8.9813 | 8.7354 | 8.6354 | 8.3456 | 7.917 | 7.3681 | 6.8772 | 6.3579 | 3.1711 | 2.0579 | 1.4089 | 8.1007 | 8.0793 | 7.8997 | 7.8007 | 7.4793 | 6.9977 | 6.3701 | 5.8201 | 5.2364 | 2.0395 | 1.1283 | 1.0385
|  | EYNSHAM PRIMARY | FB |  |  |  |  | 7.6079 | 7.6109 | 7.5844 | 7.5232 | 7.3752 | 7.0619 | 6.6579 | 6.2313 | 5.8232 | 3.8915 | 0.92214 | 0.18439 | 9.1323 | 9.0762 | 9.0089 | 8.913 | 8.7477 | 8.3487 | 7.9242 | 7.5548 | 7.1926 | 5.2477 | 1.8619 | -0.15235 | 8.1732 | 8.1691 | 8.1456 | 8.0895 | 7.9681 | 7.713 | 7.2977 | 6.9507 | 6.6191 | 4.9313 | 2.2354 | 1.4977
MINETY GSP | CIRENCESTER BSP | FAIRFORD PRIMARY | MINIMUM HEADROOM | SP 14418 00559 | NO | NO | 2.349 | 5.2388 | 5.2531 | 5.1786 | 4.9378 | 4.6112 | 4.0276 | 3.3663 | 2.7163 | 2.0898 | 0.071449 | -1.5704 | -2.4877 | 8.4561 | 8.447 | 8.3888 | 8.2204 | 7.997 | 7.6572 | 7.2551 | 6.8388 | 6.4449 | 5.1806 | 4.3714 | 3.4378 | 6.5561 | 6.5388 | 6.4929 | 6.2827 | 6.0031 | 5.551 | 5.0143 | 4.498 | 4 | 2.4072 | 1.3041 | 0.92043
|  | FAIRFORD PRIMARY | EE |  |  |  |  | 5.2398 | 5.2582 | 5.1786 | 5.0429 | 4.7959 | 4.2919 | 3.7847 | 3.2796 | 2.748 | 0.76227 | -0.7459 | -1.4796 | 8.4561 | 8.45 | 8.3888 | 8.2633 | 8.0439 | 7.7143 | 7.397 | 7.0541 | 6.6868 | 5.247 | 4.3714 | 3.9908 | 6.5582 | 6.5459 | 6.4929 | 6.351 | 6.1163 | 5.701 | 5.2888 | 4.8796 | 4.4419 | 2.847 | 1.801 | 1.4786
|  | FAIRFORD PRIMARY | HT |  |  |  |  | 5.2459 | 5.2531 | 5.2398 | 4.9378 | 4.6112 | 4.0276 | 3.3663 | 2.7163 | 2.0898 | 0.071449 | -1.5704 | -2.4877 | 8.4572 | 8.447 | 8.4388 | 8.2204 | 7.997 | 7.6572 | 7.2551 | 6.8388 | 6.4449 | 5.1806 | 4.549 | 4.5582 | 6.5602 | 6.5388 | 6.5592 | 6.2827 | 6.0031 | 5.551 | 5.0143 | 4.498 | 4 | 2.4072 | 1.3041 | 0.92043
|  | FAIRFORD PRIMARY | HE |  |  |  |  | 5.2388 | 5.2561 | 5.2674 | 5.0184 | 4.7674 | 4.2704 | 3.7123 | 3.1429 | 2.6112 | 1.1684 | -0.19182 | -1.0459 | 8.4561 | 8.449 | 8.448 | 8.2572 | 8.0459 | 7.7561 | 7.4112 | 7.0388 | 6.6959 | 5.5368 | 4.8163 | 4.1786 | 6.5561 | 6.5439 | 6.5786 | 6.3378 | 6.1021 | 5.7133 | 5.2663 | 4.8072 | 4.3827 | 3.2163 | 2.3317 | 1.7949
|  | FAIRFORD PRIMARY | FB |  |  |  |  | 5.4194 | 5.4847 | 5.5245 | 5.5694 | 5.597 | 5.597 | 5.5245 | 5.2449 | 5.1276 | 4.1235 | 2.9419 | 2.1102 | 8.5429 | 8.5633 | 8.5643 | 8.5623 | 8.5388 | 8.5184 | 8.398 | 8.0602 | 7.899 | 6.6704 | 5.1123 | 3.4378 | 6.7337 | 6.7796 | 6.7939 | 6.8306 | 6.8255 | 6.797 | 6.7255 | 6.4857 | 6.3735 | 5.4439 | 4.4061 | 3.6755
MINETY GSP | STRATTON (RESERVE) BSP | FARINGDON PRIMARY | MINIMUM HEADROOM | SU 28819 94924 | NO | NO | 12.734 | -4.8169 | -4.9199 | 18.0543 | 17.8339 | 17.5033 | 16.8523 | 16.1002 | 15.3604 | 14.5849 | 11.7625 | 9.6462 | 8.2227 | -1.4738 | -1.5922 | 19.7421 | 19.5206 | 19.2084 | 18.7349 | 18.1911 | 17.6543 | 17.0829 | 15.1819 | 13.9584 | 12.5308 | -3.3887 | -3.4938 | 18.84 | 18.6431 | 18.3268 | 17.7676 | 17.1186 | 16.4931 | 15.8319 | 13.5625 | 12.1064 | 11.2411
|  | FARINGDON PRIMARY | EE |  |  |  |  | -4.7485 | -4.826 | 18.1584 | 17.9502 | 17.6308 | 16.989 | 16.2757 | 15.5329 | 14.7737 | 11.9002 | 9.8462 | 8.5431 | -1.433 | -1.5392 | 19.8043 | 19.6002 | 19.29 | 18.8431 | 18.3492 | 17.8115 | 17.2717 | 15.1819 | 13.9584 | 12.9972 | -3.3326 | -3.4163 | 18.9227 | 18.74 | 18.4329 | 17.8911 | 17.289 | 16.6625 | 16.0298 | 13.7298 | 12.2778 | 11.4349
|  | FARINGDON PRIMARY | HT |  |  |  |  | -4.8169 | -4.9199 | 18.0543 | 17.8339 | 17.5033 | 16.8523 | 16.1002 | 15.3604 | 14.5849 | 11.7625 | 9.6462 | 8.2227 | -1.4738 | -1.5922 | 19.7421 | 19.5206 | 19.2084 | 18.7349 | 18.1911 | 17.6543 | 17.0829 | 15.2186 | 14.3298 | 13.9125 | -3.3887 | -3.4938 | 18.84 | 18.6431 | 18.3268 | 17.7676 | 17.1186 | 16.4931 | 15.8319 | 13.5625 | 12.1064 | 11.2411
|  | FARINGDON PRIMARY | HE |  |  |  |  | -4.7495 | -4.8281 | 18.1584 | 17.9196 | 17.5951 | 16.9033 | 16.1523 | 15.4074 | 14.6196 | 12.4972 | 10.6125 | 9.6033 | -1.4351 | -1.5412 | 19.8013 | 19.5931 | 19.2921 | 18.8186 | 18.3155 | 17.8074 | 17.2604 | 15.5941 | 14.436 | 13.49 | -3.3336 | -3.4183 | 18.9217 | 18.7227 | 18.4166 | 17.8349 | 17.2104 | 16.5972 | 15.9451 | 14.2288 | 12.9013 | 12.2247
|  | FARINGDON PRIMARY | FB |  |  |  |  | -4.5444 | -4.5373 | 18.636 | 18.6839 | 18.5431 | 18.4257 | 18.2645 | 18.0982 | 17.8686 | 16.5166 | 14.7574 | 13.6982 | -1.2922 | -1.3524 | 20.1686 | 20.1257 | 19.8911 | 19.6931 | 19.4431 | 19.1992 | 18.9176 | 17.19 | 14.8339 | 12.5308 | -3.1357 | -3.1398 | 19.4166 | 19.4319 | 19.289 | 19.1686 | 19.0023 | 18.838 | 18.6298 | 17.3696 | 15.7625 | 14.8298
LOVEDEAN GSP | PORTSMOUTH BSP | FARLINGTON PRIMARY | MINIMUM HEADROOM | SU 67400 04843 | NO | YES | 8.935 | 11.2508 | 11.2376 | 11.1927 | 11.1049 | 10.9845 | 10.8814 | 10.7161 | 10.5233 | 10.358 | 9.5508 | 8.9651 | 8.7263 | 12.7814 | 12.7641 | 12.7161 | 12.6559 | 12.559 | 12.4876 | 12.358 | 12.2069 | 12.0763 | 11.1988 | 10.2692 | 8.5039 | 11.7876 | 11.7753 | 11.7355 | 11.6671 | 11.5171 | 11.4049 | 11.1171 | 10.76 | 10.4927 | 9.2529 | 8.5661 | 8.2794
|  | FARLINGTON PRIMARY | EE |  |  |  |  | 11.2508 | 11.2376 | 11.1927 | 11.1222 | 11.0192 | 10.9222 | 10.7651 | 10.5835 | 10.4396 | 9.7467 | 9.2406 | 8.9529 | 12.7814 | 12.7651 | 12.7233 | 12.6712 | 12.5814 | 12.5202 | 12.3988 | 12.2569 | 12.1416 | 11.1988 | 10.2692 | 9.4814 | 11.7876 | 11.7753 | 11.7386 | 11.6855 | 11.5488 | 11.4641 | 11.1824 | 10.8314 | 10.6059 | 9.3773 | 8.6355 | 8.2794
|  | FARLINGTON PRIMARY | HT |  |  |  |  | 11.2539 | 11.2427 | 11.1927 | 11.1049 | 10.9845 | 10.8814 | 10.7161 | 10.5233 | 10.358 | 9.5508 | 8.9651 | 8.7263 | 12.7824 | 12.7641 | 12.7161 | 12.6559 | 12.559 | 12.4876 | 12.358 | 12.2069 | 12.0763 | 11.3549 | 10.7508 | 10.5222 | 11.7896 | 11.7763 | 11.7355 | 11.6671 | 11.5171 | 11.4049 | 11.1171 | 10.76 | 10.4927 | 9.2529 | 8.5661 | 8.3671
|  | FARLINGTON PRIMARY | HE |  |  |  |  | 11.2559 | 11.2478 | 11.2059 | 11.1253 | 11.011 | 10.9304 | 10.7835 | 10.61 | 10.4661 | 9.9682 | 9.6365 | 9.4692 | 12.7824 | 12.7671 | 12.7233 | 12.6661 | 12.5804 | 12.5202 | 12.4049 | 12.2641 | 12.1498 | 11.5478 | 10.808 | 10.1039 | 11.7916 | 11.7835 | 11.7478 | 11.6804 | 11.5467 | 11.462 | 11.1988 | 10.859 | 10.6192 | 9.8151 | 9.3712 | 9.1937
|  | FARLINGTON PRIMARY | FB |  |  |  |  | 11.3018 | 11.3192 | 11.3324 | 11.3324 | 11.3161 | 11.2437 | 11.1865 | 11.1406 | 11.1029 | 10.7151 | 10.2294 | 9.8814 | 12.8161 | 12.8212 | 12.8222 | 12.8202 | 12.7988 | 12.7314 | 12.6773 | 12.6059 | 12.5416 | 11.9335 | 10.5212 | 8.5039 | 11.8294 | 11.8488 | 11.86 | 11.8641 | 11.8529 | 11.7927 | 11.7518 | 11.7151 | 11.6702 | 11.0682 | 10.2161 | 9.51
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FARNBOROUGH PRIMARY | MINIMUM HEADROOM | SU 88404 53930 | NO | NO | 7.562 | 11.4434 | 11.3689 | 11.1883 | 10.9128 | 10.4679 | 9.5811 | 8.5046 | 7.5342 | 6.4709 | 2.5873 | 0.18012 | -0.51171 | 14.3913 | 14.2618 | 14.0148 | 13.7271 | 13.3189 | 12.6342 | 11.7485 | 10.9301 | 10.0301 | 6.9362 | 3.8893 | -1.2474 | 11.4077 | 11.3362 | 11.1138 | 10.7873 | 10.3026 | 9.4811 | 8.4862 | 7.573 | 6.5781 | 2.9209 | 0.81584 | 0.36992
|  | FARNBOROUGH PRIMARY | EE |  |  |  |  | 11.4607 | 11.4199 | 11.2995 | 11.1567 | 10.7699 | 10.0536 | 9.1434 | 8.2975 | 7.4097 | 3.7087 | 1.1699 | 0.076041 | 14.4005 | 14.2944 | 14.0862 | 13.8516 | 13.5036 | 12.9281 | 12.1373 | 11.4138 | 10.6434 | 6.9597 | 4.3403 | 2.4434 | 11.4179 | 11.3689 | 11.1842 | 10.9648 | 10.5811 | 9.9301 | 9.0954 | 8.3036 | 7.4811 | 3.8342 | 1.4454 | 0.54237
|  | FARNBOROUGH PRIMARY | HT |  |  |  |  | 11.4434 | 11.3689 | 11.1883 | 10.9128 | 10.4679 | 9.5811 | 8.5046 | 7.5342 | 6.4709 | 2.5873 | 0.18012 | -0.51171 | 14.3913 | 14.2618 | 14.0148 | 13.7271 | 13.3189 | 12.6342 | 11.7485 | 10.9301 | 10.0301 | 6.9362 | 5.2332 | 4.7924 | 11.4077 | 11.3362 | 11.1138 | 10.7873 | 10.3026 | 9.4811 | 8.4862 | 7.573 | 6.5781 | 2.9209 | 0.81584 | 0.36992
|  | FARNBOROUGH PRIMARY | HE |  |  |  |  | 11.4628 | 11.4291 | 11.3107 | 11.1577 | 10.7516 | 10.0291 | 9.1322 | 8.2995 | 7.4209 | 4.2628 | 2.5056 | 1.9567 | 14.3995 | 14.2913 | 14.0811 | 13.8464 | 13.4903 | 12.9087 | 12.126 | 11.4128 | 10.6475 | 7.3016 | 5.1138 | 3.5169 | 11.4199 | 11.375 | 11.1944 | 10.9648 | 10.5607 | 9.9138 | 9.0924 | 8.3158 | 7.5067 | 4.425 | 2.726 | 2.3403
|  | FARNBOROUGH PRIMARY | FB |  |  |  |  | 11.7934 | 11.7607 | 11.8464 | 11.8791 | 11.9067 | 11.6352 | 11.4056 | 11.0709 | 10.6699 | 8.1556 | 5.4332 | 3.9281 | 14.6403 | 14.4577 | 14.375 | 14.2077 | 14.0005 | 13.5107 | 13.0597 | 12.5842 | 12.0577 | 8.6546 | 3.8893 | -1.2474 | 11.8311 | 11.7903 | 11.8495 | 11.7934 | 11.7495 | 11.4444 | 11.1791 | 10.8648 | 10.4893 | 8.0577 | 5.2577 | 3.6413
FLEET-BRAMLEY GSP | PYESTOCK BSP | FARNBORO AIRFIELD PRIMARY | MINIMUM HEADROOM | SU 85838 54449 | NO | NO | 2.815 | 26.9047 | 26.9037 | 26.8414 | 26.7955 | 26.719 | 26.6394 | 26.5475 | 26.4394 | 26.3455 | 25.9506 | 25.6894 | 25.5975 | 25.0302 | 25.0302 | 24.9537 | 24.9098 | 24.8312 | 24.7588 | 24.6833 | 24.5567 | 24.4537 | 24.0455 | 23.6873 | 23.4649 | 26.4343 | 26.4333 | 26.3863 | 26.3496 | 26.2853 | 26.2139 | 26.1445 | 26.0639 | 25.9853 | 25.5761 | 25.3057 | 25.2261
|  | FARNBORO AIRFIELD PRIMARY | EE |  |  |  |  | 26.9047 | 26.9037 | 26.8414 | 26.7955 | 26.722 | 26.6465 | 26.5771 | 26.4639 | 26.4047 | 26.0659 | 25.8098 | 25.7567 | 25.0302 | 25.0322 | 24.9577 | 24.9128 | 24.8373 | 24.7618 | 24.7047 | 24.5608 | 24.4894 | 24.0496 | 23.6873 | 23.5537 | 26.4343 | 26.4343 | 26.3863 | 26.3496 | 26.2904 | 26.223 | 26.173 | 26.0771 | 26.0261 | 25.6628 | 25.3914 | 25.3312
|  | FARNBORO AIRFIELD PRIMARY | HT |  |  |  |  | 26.9077 | 26.9067 | 26.8475 | 26.8016 | 26.7241 | 26.6394 | 26.5475 | 26.4394 | 26.3455 | 25.9506 | 25.6894 | 25.5975 | 25.0312 | 25.0322 | 24.9567 | 24.9139 | 24.8363 | 24.7588 | 24.6833 | 24.5618 | 24.4537 | 24.0455 | 23.7894 | 23.7271 | 26.4353 | 26.4353 | 26.3884 | 26.3526 | 26.2914 | 26.2139 | 26.1445 | 26.0639 | 25.9853 | 25.5761 | 25.3057 | 25.2261
|  | FARNBORO AIRFIELD PRIMARY | HE |  |  |  |  | 26.9088 | 26.9067 | 26.8445 | 26.7955 | 26.719 | 26.6404 | 26.5782 | 26.4802 | 26.4322 | 26.1577 | 25.9965 | 25.9751 | 25.0312 | 25.0302 | 24.9537 | 24.9098 | 24.8312 | 24.7639 | 24.6884 | 24.5567 | 24.4945 | 24.1384 | 23.9179 | 23.8516 | 26.4363 | 26.4333 | 26.3873 | 26.3496 | 26.2853 | 26.223 | 26.1649 | 26.0771 | 26.0465 | 25.7618 | 25.5986 | 25.5884
|  | FARNBORO AIRFIELD PRIMARY | FB |  |  |  |  | 26.9251 | 26.9302 | 26.9312 | 26.9271 | 26.922 | 26.8567 | 26.8179 | 26.8067 | 26.7608 | 26.5424 | 26.272 | 26.1108 | 25.0465 | 25.0496 | 25.0475 | 25.0465 | 25.0394 | 24.9649 | 24.9241 | 24.9118 | 24.8455 | 24.4384 | 23.9292 | 23.4649 | 26.4537 | 26.4557 | 26.4608 | 26.4577 | 26.4537 | 26.4016 | 26.37 | 26.3588 | 26.321 | 26.1251 | 25.8424 | 25.6618
FLEET-BRAMLEY GSP | ALDERSHOT BSP | FARNHAM PRIMARY | MINIMUM HEADROOM | SU 84517 47217 | NO | YES | 7.81 | 5.9344 | 5.7793 | 5.6436 | 5.3915 | 5.0017 | 4.4007 | 3.6436 | 2.9609 | 2.3129 | 0.039469 | -1.2044 | -1.3003 | 11.5027 | 11.2854 | 11.1262 | 10.7629 | 10.3007 | 9.7466 | 9.0354 | 8.3905 | 7.766 | 5.5354 | 4.0384 | 1.066 | 7.617 | 7.3691 | 7.1976 | 6.8303 | 6.366 | 5.7956 | 5.0436 | 4.3793 | 3.7303 | 1.3068 | 0.082327 | 0.0078367
|  | FARNHAM PRIMARY | EE |  |  |  |  | 5.9395 | 5.8211 | 5.7282 | 5.5599 | 5.3068 | 4.8589 | 4.1946 | 3.664 | 3.1619 | 0.90376 | -0.55135 | -1.0973 | 11.5099 | 11.3129 | 11.1782 | 10.8762 | 10.4711 | 10.018 | 9.3364 | 8.7803 | 8.2333 | 5.6793 | 4.0384 | 2.8446 | 7.6201 | 7.4078 | 7.2772 | 6.9905 | 6.614 | 6.1599 | 5.4538 | 4.9017 | 4.365 | 1.9589 | 0.58743 | 0.089469
|  | FARNHAM PRIMARY | HT |  |  |  |  | 5.9344 | 5.7793 | 5.6436 | 5.3915 | 5.0017 | 4.4007 | 3.6436 | 2.9609 | 2.3129 | 0.039469 | -1.2044 | -1.3003 | 11.5027 | 11.2854 | 11.1262 | 10.7629 | 10.3007 | 9.7466 | 9.0354 | 8.3905 | 7.766 | 5.5354 | 4.4599 | 4.2793 | 7.617 | 7.3691 | 7.1976 | 6.8303 | 6.366 | 5.7956 | 5.0436 | 4.3793 | 3.7303 | 1.3068 | 0.082327 | 0.0078367
|  | FARNHAM PRIMARY | HE |  |  |  |  | 5.9425 | 5.8262 | 5.7374 | 5.5599 | 5.2946 | 4.8721 | 4.2048 | 3.6844 | 3.1864 | 1.5303 | 0.44763 | 0.28437 | 11.5099 | 11.3119 | 11.1793 | 10.8782 | 10.4619 | 10.0293 | 9.3364 | 8.7895 | 8.2211 | 6.116 | 4.6364 | 3.7099 | 7.6262 | 7.4191 | 7.2936 | 6.9966 | 6.6017 | 6.1731 | 5.4599 | 4.9272 | 4.3701 | 2.5874 | 1.5395 | 1.4446
|  | FARNHAM PRIMARY | FB |  |  |  |  | 6.1048 | 6.014 | 5.9629 | 5.9282 | 5.8293 | 5.7109 | 5.5987 | 5.4701 | 5.3303 | 3.9762 | 1.9895 | 0.88233 | 11.6905 | 11.5211 | 11.4415 | 11.3548 | 11.0844 | 10.7915 | 10.465 | 10.1058 | 9.665 | 7.3803 | 4.1987 | 1.066 | 8.0793 | 7.818 | 7.716 | 7.6782 | 7.5027 | 7.3242 | 7.1262 | 6.8731 | 6.5446 | 5.0038 | 2.9956 | 1.9221
IVER 132KV GSP | SLOUGH BSP | FARNHAM ROYAL PRIMARY | MINIMUM HEADROOM | SU 95597 82844 | NO | YES | 8.942 | 17.2255 | 17.1387 | 16.9244 | 16.5132 | 15.7653 | 14.552 | 11.7898 | 9.0163 | 6.3418 | -4.7766 | -12.3551 | -15.697 | 24.3714 | 24.1275 | 23.7785 | 23.3204 | 22.5969 | 21.6785 | 18.7959 | 16.0234 | 13.3663 | 1.8704 | -5.4725 | -9.8062 | 22.0275 | 21.9438 | 21.6602 | 21.2173 | 20.4122 | 19.3622 | 16.3969 | 13.504 | 10.7234 | -0.78167 | -8.147 | -11.1929
|  | FARNHAM ROYAL PRIMARY | EE |  |  |  |  | 17.2255 | 17.1387 | 16.9244 | 16.5653 | 15.9398 | 14.7887 | 11.7898 | 9.0163 | 6.3418 | -4.7766 | -12.3551 | -15.697 | 24.3714 | 24.1275 | 23.7857 | 23.353 | 22.6744 | 21.7836 | 18.7959 | 16.0234 | 13.3663 | 1.8704 | -5.4725 | -9.8062 | 22.0275 | 21.9438 | 21.6602 | 21.2469 | 20.5377 | 19.5398 | 16.3969 | 13.504 | 10.7234 | -0.78167 | -8.147 | -11.1929
|  | FARNHAM ROYAL PRIMARY | HT |  |  |  |  | 17.2479 | 17.1836 | 16.9602 | 16.5132 | 15.7653 | 14.552 | 12.7918 | 10.4857 | 8.05 | -1.1949 | -7.0092 | -8.8184 | 24.3724 | 24.1316 | 23.7785 | 23.3204 | 22.5969 | 21.6785 | 20.254 | 18.0683 | 15.7561 | 7.5214 | 3.1132 | 1.8989 | 22.0561 | 22.0051 | 21.7132 | 21.2173 | 20.4122 | 19.3622 | 17.7765 | 15.4663 | 13.0183 | 3.7387 | -1.6572 | -3.0602
|  | FARNHAM ROYAL PRIMARY | HE |  |  |  |  | 17.254 | 17.1887 | 17 | 16.5816 | 15.8898 | 14.804 | 13.1571 | 11.4214 | 9.7336 | 3.8857 | -0.053102 | -2.0837 | 24.3765 | 24.1357 | 23.7969 | 23.3642 | 22.6775 | 21.801 | 20.4387 | 18.8918 | 17.3949 | 11.2438 | 7.0418 | 3.4285 | 22.0571 | 21.9989 | 21.7275 | 21.2775 | 20.5204 | 19.5704 | 18.0734 | 16.4347 | 14.8479 | 9.2449 | 5.9173 | 4.2806
|  | FARNHAM ROYAL PRIMARY | FB |  |  |  |  | 17.7326 | 17.8387 | 17.9571 | 18.0683 | 18.0265 | 17.8438 | 17.5071 | 17.152 | 16.7683 | 13.6183 | 8.6612 | 5.3847 | 24.6755 | 24.4857 | 24.3234 | 24.1632 | 23.8408 | 23.3193 | 22.6642 | 21.9775 | 21.2612 | 16.1428 | 8.6132 | 0.44078 | 22.3755 | 22.4755 | 22.5449 | 22.5173 | 22.4204 | 22.2581 | 21.9163 | 21.5193 | 21.101 | 17.8285 | 13.2908 | 10.404
LALEHAM GSP | EAST BEDFONT BSP | FELTHAM PRIMARY | MINIMUM HEADROOM | TQ 10628 72811 | NO | NO | 2.213 | 11.7835 | 11.6682 | 11.4243 | 11.1621 | 10.8723 | 10.407 | 9.808 | 9.1254 | 8.4631 | 6.2305 | 4.908 | 4.3182 | 15.1927 | 15.1294 | 15.0305 | 14.9376 | 14.7488 | 14.4876 | 14.1407 | 13.7468 | 13.305 | 12.1764 | 11.6192 | 11.109 | 13.4529 | 13.3774 | 13.1192 | 12.9315 | 12.7101 | 12.3172 | 11.8182 | 11.2611 | 10.7305 | 8.9101 | 7.8243 | 7.3631
|  | FELTHAM PRIMARY | EE |  |  |  |  | 11.7835 | 11.6682 | 11.4243 | 11.1621 | 10.8846 | 10.4478 | 9.9131 | 9.2621 | 8.6264 | 6.2305 | 4.908 | 4.3182 | 15.1927 | 15.157 | 15.0305 | 14.9376 | 14.8652 | 14.6519 | 14.3631 | 14.0121 | 13.6121 | 12.2182 | 11.6192 | 11.307 | 13.4529 | 13.3794 | 13.1192 | 12.9315 | 12.7713 | 12.3978 | 11.9611 | 11.4284 | 10.9152 | 8.9101 | 7.8243 | 7.3631
|  | FELTHAM PRIMARY | HT |  |  |  |  | 11.7978 | 11.6713 | 11.4764 | 11.2294 | 10.8723 | 10.407 | 9.808 | 9.1254 | 8.4631 | 6.2397 | 5.2448 | 4.8417 | 15.1948 | 15.1294 | 15.0346 | 14.9427 | 14.7488 | 14.4876 | 14.1407 | 13.7468 | 13.305 | 12.1764 | 11.8019 | 11.7243 | 13.4641 | 13.3774 | 13.157 | 12.9784 | 12.7101 | 12.3172 | 11.8182 | 11.2611 | 10.7305 | 9.0162 | 8.1417 | 7.8662
|  | FELTHAM PRIMARY | HE |  |  |  |  | 11.7886 | 11.6805 | 11.4427 | 11.1754 | 10.8937 | 10.4815 | 9.9682 | 9.3346 | 8.7274 | 6.8621 | 5.9825 | 5.4652 | 15.1948 | 15.159 | 15.0315 | 14.9427 | 14.8672 | 14.657 | 14.3631 | 14.0121 | 13.6274 | 12.4539 | 11.9662 | 11.6294 | 13.4621 | 13.3937 | 13.1437 | 12.958 | 12.7897 | 12.4478 | 11.9978 | 11.4774 | 10.9907 | 9.455 | 8.7376 | 8.3376
|  | FELTHAM PRIMARY | FB |  |  |  |  | 11.8733 | 11.8182 | 11.7243 | 11.5652 | 11.4233 | 11.1907 | 10.9509 | 10.6478 | 10.2784 | 8.6305 | 7.407 | 6.4101 | 15.2499 | 15.2294 | 15.1999 | 15.1315 | 15.0815 | 14.9641 | 14.8203 | 14.6437 | 14.4335 | 13.1274 | 12.1039 | 11.109 | 13.5652 | 13.5294 | 13.4784 | 13.3713 | 13.2948 | 13.0478 | 12.8488 | 12.608 | 12.306 | 10.8529 | 9.7488 | 8.8376
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN PRIMARY | MINIMUM HEADROOM | SU 06593 00685 | NO | NO | 7.305 | 18.8532 | 18.8042 | 18.6113 | 18.2848 | 17.8317 | 17.2532 | 14.7032 | 11.9032 | 11.0236 | 1.0705 | -5.9213 | -12.5622 | 25.1358 | 25.0317 | 24.8215 | 24.4409 | 23.9083 | 23.2011 | 19.8113 | 15.9501 | 14.5062 | 2.0685 | -8.153 | -16.4213 | 21.6409 | 21.543 | 21.3052 | 20.9399 | 20.3919 | 19.5409 | 16.1062 | 12.2736 | 11.1021 | -1.3713 | -10.5224 | -17.9458
|  | FERNDOWN PRIMARY | EE |  |  |  |  | 18.8766 | 18.8613 | 18.7603 | 18.5552 | 18.244 | 17.7868 | 16.6042 | 14.4664 | 11.0236 | 3.2052 | -0.6244 | -7.607 | 25.1491 | 25.0613 | 24.8991 | 24.6511 | 24.2338 | 23.5072 | 21.9185 | 18.945 | 14.5062 | 3.446 | -1.4009 | -10.8917 | 21.6603 | 21.5797 | 21.4113 | 21.1307 | 20.7389 | 19.9256 | 18.3878 | 15.4838 | 11.1021 | 0.56336 | -3.8132 | -12.3999
|  | FERNDOWN PRIMARY | HT |  |  |  |  | 18.8532 | 18.8042 | 18.6113 | 18.2848 | 17.8317 | 17.2532 | 14.7032 | 11.9032 | 11.2083 | 1.0705 | -3.8183 | -12.5622 | 25.1358 | 25.0317 | 24.8215 | 24.4409 | 23.9083 | 23.2011 | 19.8113 | 15.9501 | 14.9266 | 2.0685 | -3.753 | -14.6856 | 21.6409 | 21.543 | 21.3052 | 20.9399 | 20.3919 | 19.5409 | 16.1062 | 12.2736 | 11.2695 | -1.3713 | -7.1132 | -17.9458
|  | FERNDOWN PRIMARY | HE |  |  |  |  | 18.8715 | 18.8664 | 18.7521 | 18.5491 | 18.2338 | 17.8195 | 15.3725 | 14.646 | 14.0389 | 3.4552 | -5.9213 | -9.3264 | 25.145 | 25.0644 | 24.896 | 24.6378 | 24.2083 | 23.6205 | 20.3654 | 19.1511 | 18.2552 | 3.695 | -8.153 | -13.3693 | 21.6542 | 21.5868 | 21.4032 | 21.1256 | 20.7256 | 20.094 | 16.8501 | 15.7072 | 14.8766 | 0.85418 | -10.5224 | -14.6173
|  | FERNDOWN PRIMARY | FB |  |  |  |  | 19.0358 | 19.1368 | 19.194 | 19.1817 | 19.1195 | 18.9827 | 18.3572 | 17.4664 | 15.4205 | 9.1409 | 0.77969 | -6.9785 | 25.2593 | 25.2532 | 25.2256 | 25.1246 | 24.8695 | 24.4491 | 23.4276 | 22.0736 | 19.2368 | 10.0072 | -2.9764 | -16.4213 | 21.8521 | 21.8981 | 21.9062 | 21.8511 | 21.7419 | 21.5562 | 20.7725 | 19.6634 | 17.1052 | 8.743 | -2.2642 | -12.2397
FLEET-BRAMLEY GSP | FERNHURST BSP | FIVE OAKS PRIMARY | MINIMUM HEADROOM | TQ 10647 29057 | NO | NO | 3.821 | 3.5582 | 3.2306 | 3 | 2.7286 | 2.2245 | 1.6541 | 1.0306 | 0.51224 | -0.18061 | -1.9837 | -2.8929 | -3.0969 | 6.226 | 5.9097 | 5.6923 | 5.4474 | 4.9617 | 4.5087 | 3.9158 | 3.4097 | 2.7617 | 0.90765 | 0.14643 | -0.077041 | 5.3444 | 4.9934 | 4.7556 | 4.4934 | 3.9903 | 3.4515 | 2.8281 | 2.3046 | 1.6117 | -0.23622 | -1.0934 | -1.2566
|  | FIVE OAKS PRIMARY | EE |  |  |  |  | 3.5622 | 3.2337 | 3.0112 | 2.7357 | 2.2255 | 1.6643 | 1.152 | 0.68265 | 0.076531 | -1.6806 | -2.6041 | -3.0204 | 6.2281 | 5.9097 | 5.6944 | 5.4505 | 4.9628 | 4.5097 | 3.9628 | 3.4638 | 2.8423 | 0.99745 | 0.23622 | -0.077041 | 5.3474 | 4.9944 | 4.7648 | 4.4995 | 3.9903 | 3.4597 | 2.9219 | 2.4464 | 1.8199 | 0.002551 | -0.87908 | -1.2566
|  | FIVE OAKS PRIMARY | HT |  |  |  |  | 3.5582 | 3.2306 | 3 | 2.7286 | 2.2245 | 1.6541 | 1.0306 | 0.51224 | -0.18061 | -1.9837 | -2.8929 | -3.0969 | 6.226 | 5.9128 | 5.6923 | 5.4474 | 4.9617 | 4.5087 | 3.9158 | 3.4097 | 2.7617 | 0.90765 | 0.14643 | 0.062755 | 5.3444 | 4.9934 | 4.7556 | 4.4934 | 3.9923 | 3.4515 | 2.8281 | 2.3046 | 1.6117 | -0.23622 | -1.0934 | -1.2454
|  | FIVE OAKS PRIMARY | HE |  |  |  |  | 3.5633 | 3.2347 | 3.0102 | 2.7347 | 2.2418 | 1.6694 | 1.148 | 0.69184 | 0.091837 | -1.1214 | -1.7918 | -2.1735 | 6.2281 | 5.9107 | 5.6944 | 5.4495 | 4.9821 | 4.5168 | 3.9607 | 3.477 | 2.8668 | 1.5464 | 0.98316 | 0.78112 | 5.3474 | 4.9944 | 4.7638 | 4.4985 | 4.0128 | 3.4638 | 2.9189 | 2.4526 | 1.8383 | 0.59337 | -0.064796 | -0.40561
|  | FIVE OAKS PRIMARY | FB |  |  |  |  | 3.6367 | 3.5582 | 3.2827 | 3.0469 | 2.7745 | 2.4755 | 2.2714 | 2.0867 | 1.8408 | 0.67143 | -0.6602 | -1.4847 | 6.2913 | 6.2046 | 5.9474 | 5.7658 | 5.5617 | 5.3985 | 5.1811 | 4.9709 | 4.7148 | 3.3536 | 1.9546 | 0.8648 | 5.4189 | 5.3372 | 5.0434 | 4.8209 | 4.576 | 4.3015 | 4.0852 | 3.8862 | 3.6281 | 2.3801 | 1.0077 | 0.16276
AMERSHAM GSP | LOUDWATER BSP | FLACKWELL HEATH PRIMARY | MINIMUM HEADROOM | SU 90667 89318 | NO | YES | 3.034 | 16.2904 | 16.2363 | 16.0935 | 15.722 | 15.2588 | 14.3547 | 13.3649 | 12.2792 | 11.1618 | 7.5384 | 5.2547 | 4.4333 | 17.921 | 17.8404 | 17.7343 | 17.4751 | 17.0812 | 16.5476 | 15.9271 | 15.2067 | 14.4516 | 12.32 | 11.0924 | 9.0251 | 17.1547 | 17.0598 | 16.9373 | 16.6282 | 16.2424 | 15.5394 | 14.7567 | 13.8802 | 12.9924 | 10.118 | 8.4955 | 8.1251
|  | FLACKWELL HEATH PRIMARY | EE |  |  |  |  | 16.2904 | 16.2363 | 16.1373 | 15.8659 | 15.5282 | 14.7169 | 13.8037 | 12.7618 | 11.7139 | 8.2884 | 6.0598 | 5.0986 | 17.9241 | 17.8424 | 17.7496 | 17.5322 | 17.1945 | 16.72 | 16.1547 | 15.468 | 14.768 | 12.4955 | 11.0924 | 10.2608 | 17.1547 | 17.0598 | 16.9486 | 16.7231 | 16.4261 | 15.7935 | 15.0608 | 14.222 | 13.3894 | 10.618 | 8.9639 | 8.3884
|  | FLACKWELL HEATH PRIMARY | HT |  |  |  |  | 16.2935 | 16.2373 | 16.0935 | 15.722 | 15.2588 | 14.3547 | 13.3649 | 12.2792 | 11.1618 | 7.5384 | 5.2547 | 4.4333 | 17.9241 | 17.8404 | 17.7343 | 17.4751 | 17.0812 | 16.5476 | 15.9271 | 15.2067 | 14.4516 | 12.32 | 11.5741 | 11.6639 | 17.1567 | 17.0608 | 16.9373 | 16.6282 | 16.2424 | 15.5394 | 14.7567 | 13.8802 | 12.9924 | 10.118 | 8.4955 | 8.1251
|  | FLACKWELL HEATH PRIMARY | HE |  |  |  |  | 16.2935 | 16.2424 | 16.1486 | 15.8445 | 15.4741 | 14.6741 | 13.7894 | 12.7751 | 11.7567 | 9.1108 | 7.1792 | 6.2894 | 17.921 | 17.8404 | 17.7496 | 17.5282 | 17.1894 | 16.6986 | 16.1527 | 15.4812 | 14.8027 | 13.0302 | 11.7088 | 10.6394 | 17.1557 | 17.0649 | 16.9588 | 16.7108 | 16.3945 | 15.7629 | 15.0588 | 14.2384 | 13.4312 | 11.3057 | 9.8986 | 9.2761
|  | FLACKWELL HEATH PRIMARY | FB |  |  |  |  | 16.4751 | 16.5894 | 16.6741 | 16.7047 | 16.67 | 16.5231 | 16.3567 | 16.1302 | 15.9353 | 14.2557 | 12.322 | 10.9598 | 18.0404 | 18.0924 | 18.1078 | 18.0373 | 17.9771 | 17.8414 | 17.6333 | 17.3435 | 17.0516 | 14.8373 | 12.1016 | 9.0251 | 17.3506 | 17.4139 | 17.4404 | 17.3649 | 17.3047 | 17.1853 | 17.0445 | 16.8649 | 16.6965 | 15.1731 | 13.4414 | 12.2006
NURSLING GSP | ROWNHAMS BSP | FLETCHWOOD PRIMARY | MINIMUM HEADROOM | SU 33800 12142 | NO | YES | 9.08 | 7.962 | 7.7712 | 7.2467 | 6.3569 | 5.3548 | 3.6783 | 1.9079 | 0.044641 | -1.8676 | -8.7931 | -13.2247 | -15.4901 | 13.5089 | 13.2314 | 12.9038 | 12.364 | 11.764 | 10.8171 | 9.8069 | 8.6793 | 7.4885 | 3.7059 | 2.0059 | -1.2247 | 11.0008 | 10.7171 | 10.2946 | 9.5671 | 8.7334 | 7.3161 | 5.8385 | 4.2212 | 2.5324 | -2.8115 | -5.7574 | -6.9329
|  | FLETCHWOOD PRIMARY | EE |  |  |  |  | 7.9895 | 7.8895 | 7.4957 | 6.8242 | 6.0967 | 4.5487 | 2.8722 | 1.2273 | -0.44107 | -6.237 | -10.3258 | -12.5513 | 13.5355 | 13.3048 | 13.0314 | 12.5814 | 12.0997 | 11.2579 | 10.3559 | 9.3497 | 8.2783 | 4.1824 | 2.0059 | 0.53954 | 11.0395 | 10.8283 | 10.513 | 9.963 | 9.365 | 8.1038 | 6.765 | 5.3569 | 3.8671 | -1.0503 | -3.8941 | -5.2421
|  | FLETCHWOOD PRIMARY | HT |  |  |  |  | 7.962 | 7.7712 | 7.2467 | 6.3569 | 5.3548 | 3.6783 | 1.9079 | 0.044641 | -1.8676 | -8.7931 | -13.2247 | -15.4901 | 13.5089 | 13.2314 | 12.9038 | 12.364 | 11.764 | 10.8171 | 9.8069 | 8.6793 | 7.4885 | 3.7059 | 2.1589 | 1.8824 | 11.0008 | 10.7171 | 10.2946 | 9.5671 | 8.7334 | 7.3161 | 5.8385 | 4.2212 | 2.5324 | -2.8115 | -5.7574 | -6.9329
|  | FLETCHWOOD PRIMARY | HE |  |  |  |  | 7.9895 | 7.8936 | 7.5079 | 6.7732 | 5.9783 | 4.3753 | 2.6232 | 0.85689 | -0.90944 | -5.6186 | -9.4707 | -11.1105 | 13.5324 | 13.3018 | 13.0253 | 12.565 | 12.0773 | 11.2406 | 10.3202 | 9.3018 | 8.2202 | 4.6069 | 2.414 | 0.89566 | 11.0375 | 10.8293 | 10.513 | 9.9304 | 9.2926 | 8.0171 | 6.6344 | 5.164 | 3.6304 | -0.52067 | -3.2339 | -4.2768
|  | FLETCHWOOD PRIMARY | FB |  |  |  |  | 8.1844 | 8.2589 | 8.1467 | 7.9222 | 7.6681 | 7.2865 | 6.8099 | 6.2804 | 5.7079 | 2.8763 | -0.49107 | -2.4176 | 13.715 | 13.6191 | 13.5212 | 13.3375 | 13.1018 | 12.6691 | 12.1671 | 11.6497 | 11.0304 | 7.513 | 2.9079 | -1.2247 | 11.3426 | 11.3283 | 11.2936 | 11.1518 | 10.9824 | 10.6334 | 10.165 | 9.6702 | 9.0742 | 6.0385 | 2.6324 | 0.91913
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE PRIMARY | MINIMUM HEADROOM | SU 14069 15523 | NO | NO | 4.175 | 5.1951 | 5.0594 | 4.6461 | 4.4471 | 4.0696 | 3.6308 | 3.1339 | 2.6165 | 2.1063 | 0.6359 | -0.23859 | -0.46001 | 6.6487 | 6.514 | 6.0742 | 5.864 | 5.4456 | 5.0415 | 4.5721 | 4.0823 | 3.6262 | 2.2354 | 1.5027 | 0.90172 | 5.6293 | 5.5109 | 5.114 | 4.9231 | 4.5129 | 4.0936 | 3.6089 | 3.0987 | 2.6272 | 1.216 | 0.40988 | 0.27111
|  | FORDINGBRIDGE PRIMARY | EE |  |  |  |  | 5.2073 | 5.1237 | 4.693 | 4.5502 | 4.2481 | 3.8298 | 3.3655 | 2.8124 | 2.3706 | 0.97672 | 0.065496 | 0.029782 | 6.6568 | 6.5589 | 6.0946 | 5.9405 | 5.568 | 5.1936 | 4.7487 | 4.2231 | 3.8385 | 2.4619 | 1.5344 | 1.3058 | 5.6405 | 5.5619 | 5.1415 | 5.0089 | 4.6446 | 4.2548 | 3.7905 | 3.2476 | 2.8446 | 1.4895 | 0.60988 | 0.63335
|  | FORDINGBRIDGE PRIMARY | HT |  |  |  |  | 5.1951 | 5.0594 | 4.6461 | 4.4471 | 4.0696 | 3.6308 | 3.1339 | 2.6165 | 2.1063 | 0.6359 | -0.23859 | -0.46001 | 6.6487 | 6.514 | 6.0742 | 5.864 | 5.4456 | 5.0415 | 4.5721 | 4.0823 | 3.6262 | 2.2354 | 1.5027 | 1.4221 | 5.6293 | 5.5109 | 5.114 | 4.9231 | 4.5129 | 4.0936 | 3.6089 | 3.0987 | 2.6272 | 1.216 | 0.40988 | 0.27111
|  | FORDINGBRIDGE PRIMARY | HE |  |  |  |  | 5.2073 | 5.1226 | 4.6941 | 4.5471 | 4.2665 | 3.839 | 3.3461 | 2.8226 | 2.3675 | 1.3206 | 0.66039 | 0.46243 | 6.6558 | 6.5568 | 6.1017 | 5.9323 | 5.5915 | 5.2017 | 4.718 | 4.2425 | 3.8425 | 2.7568 | 2.1568 | 1.7374 | 5.6395 | 5.5589 | 5.1456 | 5.0017 | 4.6691 | 4.264 | 3.764 | 3.264 | 2.8466 | 1.8283 | 1.2497 | 1.0997
|  | FORDINGBRIDGE PRIMARY | FB |  |  |  |  | 5.2839 | 5.2665 | 5.1084 | 4.9808 | 4.7186 | 4.492 | 4.3441 | 4.1543 | 3.9471 | 3.0818 | 2.0645 | 1.4706 | 6.7415 | 6.6701 | 6.5344 | 6.4078 | 6.0476 | 5.7905 | 5.6272 | 5.418 | 5.1772 | 3.868 | 2.364 | 0.90172 | 5.7589 | 5.7252 | 5.5936 | 5.4885 | 5.1956 | 4.9589 | 4.8119 | 4.6242 | 4.4109 | 3.3905 | 2.3793 | 1.765
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK PRIMARY | MINIMUM HEADROOM | SU 66139 00180 | NO | YES | 5.967 | 1.0031 | 1.1306 | 1.1113 | 0.72044 | 0.28472 | -0.57854 | -1.5112 | -2.5 | -3.4255 | -9.4183 | -13.9347 | -16.4806 | 7.8908 | 7.9 | 7.6939 | 7.297 | 6.7592 | 6.0521 | 5.2541 | 4.3337 | 3.5357 | -0.52344 | -5.3194 | -13.6153 | 3.6062 | 3.5562 | 3.4031 | 3.0888 | 2.6031 | 1.8735 | 0.94084 | -0.10405 | -1.0245 | -6.2663 | -9.903 | -12.2469
|  | FRATTON PARK PRIMARY | EE |  |  |  |  | 1.0031 | 1.1306 | 1.1113 | 0.8337 | 0.43982 | -0.31018 | -1.1438 | -2.003 | -2.803 | -7.8867 | -13.45 | -16.4806 | 7.8908 | 7.9092 | 7.7255 | 7.3827 | 6.849 | 6.2225 | 5.4582 | 4.6143 | 3.8776 | -0.52344 | -4.5704 | -8.0316 | 3.6062 | 3.5562 | 3.4031 | 3.0888 | 2.6613 | 2.0194 | 1.2419 | 0.31636 | -0.50507 | -5.1745 | -9.8081 | -12.2469
|  | FRATTON PARK PRIMARY | HT |  |  |  |  | 1.0337 | 1.1766 | 1.1204 | 0.72044 | 0.28472 | -0.57854 | -1.5112 | -2.5 | -3.4255 | -9.4183 | -13.9347 | -16.3143 | 7.8929 | 7.9 | 7.6939 | 7.297 | 6.7592 | 6.0521 | 5.2541 | 4.3337 | 3.5357 | 0.089824 | -2.2245 | -3.3887 | 3.6531 | 3.647 | 3.5082 | 3.0949 | 2.6031 | 1.8735 | 0.94084 | -0.10405 | -1.0245 | -6.2663 | -9.903 | -11.6418
|  | FRATTON PARK PRIMARY | HE |  |  |  |  | 1.0388 | 1.1939 | 1.2072 | 0.90309 | 0.49493 | -0.089767 | -0.7612 | -1.4551 | -2.0938 | -5.8234 | -8.9418 | -11.1806 | 7.8959 | 7.9184 | 7.7368 | 7.3939 | 6.8868 | 6.2664 | 5.5133 | 4.6959 | 3.9857 | 0.10819 | -2.9959 | -6.399 | 3.6562 | 3.6521 | 3.551 | 3.1868 | 2.7092 | 2.1684 | 1.4939 | 0.67554 | -0.039767 | -3.4438 | -6.053 | -7.8836
|  | FRATTON PARK PRIMARY | FB |  |  |  |  | 1.2755 | 1.501 | 1.6878 | 1.6296 | 1.5623 | 1.3613 | 1.1725 | 0.97554 | 0.7388 | -1.0234 | -5.2224 | -8.7551 | 7.9592 | 7.9459 | 7.8929 | 7.6888 | 7.4041 | 6.9664 | 6.4888 | 5.9592 | 5.3847 | 1.3908 | -5.3194 | -13.6153 | 3.8266 | 3.9347 | 3.9939 | 3.8296 | 3.6602 | 3.4429 | 3.2204 | 2.9735 | 2.701 | 0.77248 | -3.1204 | -6.4122
COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD PRIMARY | MINIMUM HEADROOM | SP 50426 08256 | NO | YES | 6.111 | 6.9806 | 6.9479 | 6.9224 | 6.7969 | 6.4571 | 6.051 | 5.6357 | 5.0775 | 4.7071 | 3.0173 | 1.7132 | 1.2336 | 9.4071 | 9.3265 | 9.2194 | 9.0357 | 8.7898 | 8.4724 | 8.1214 | 7.6163 | 7.3377 | 5.903 | 4.3928 | 1.8092 | 7.7622 | 7.703 | 7.6469 | 7.5194 | 7.2275 | 6.8959 | 6.5275 | 6.0061 | 5.6959 | 4.25 | 2.951 | 2.5836
|  | FRENCHAY ROAD PRIMARY | EE |  |  |  |  | 6.9806 | 6.9479 | 6.9224 | 6.8122 | 6.504 | 6.1122 | 5.7275 | 5.2561 | 4.9561 | 3.1989 | 1.7132 | 1.2336 | 9.4102 | 9.3296 | 9.2326 | 9.0704 | 8.7949 | 8.55 | 8.2204 | 7.7785 | 7.5357 | 5.9285 | 4.5051 | 3.6387 | 7.7622 | 7.703 | 7.6469 | 7.5194 | 7.254 | 6.9449 | 6.5938 | 6.1469 | 5.8887 | 4.2989 | 2.951 | 2.5836
|  | FRENCHAY ROAD PRIMARY | HT |  |  |  |  | 6.9938 | 6.9734 | 6.9357 | 6.7969 | 6.5347 | 6.051 | 5.6357 | 5.0775 | 4.7071 | 3.0173 | 1.9224 | 1.8673 | 9.4071 | 9.3265 | 9.2194 | 9.0357 | 8.8214 | 8.4724 | 8.1214 | 7.6163 | 7.3377 | 5.9612 | 5.0061 | 4.9479 | 7.7734 | 7.7265 | 7.6653 | 7.5224 | 7.301 | 6.8959 | 6.5275 | 6.0061 | 5.6959 | 4.25 | 3.3112 | 3.3989
|  | FRENCHAY ROAD PRIMARY | HE |  |  |  |  | 6.9826 | 6.9561 | 6.9367 | 6.7969 | 6.4571 | 6.0877 | 5.7347 | 5.2928 | 4.9755 | 3.5051 | 2.7959 | 2.502 | 9.4081 | 9.3306 | 9.2336 | 9.0734 | 8.7898 | 8.5336 | 8.2081 | 7.7724 | 7.4877 | 5.903 | 5.0285 | 4.2347 | 7.7673 | 7.7122 | 7.6612 | 7.5265 | 7.2275 | 6.9265 | 6.5989 | 6.1734 | 5.8908 | 4.5214 | 3.9398 | 3.7449
|  | FRENCHAY ROAD PRIMARY | FB |  |  |  |  | 7.0592 | 7.0653 | 7.1061 | 7.1245 | 6.9836 | 6.7581 | 6.6796 | 6.6428 | 6.5428 | 5.753 | 4.4132 | 3.5347 | 9.4459 | 9.3306 | 9.2602 | 9.1959 | 9.0122 | 8.7316 | 8.5408 | 8.3877 | 8.1745 | 6.6673 | 4.3928 | 1.8092 | 7.8377 | 7.8102 | 7.8296 | 7.8357 | 7.7132 | 7.5071 | 7.4214 | 7.3775 | 7.2704 | 6.4357 | 5.104 | 4.2316
FAWLEY GSP | COWES BSP | FRESHWATER PRIMARY | MINIMUM HEADROOM | SZ 34325 86965 | NO | YES | 0.092 | 8.2321 | 8.2526 | 8.1597 | 8.026 | 7.6995 | 7.0903 | 6.5066 | 5.8607 | 5.2781 | 2.875 | 0.84643 | -0.36173 | 8.9439 | 8.9316 | 8.8551 | 8.8418 | 8.5694 | 8.3051 | 8.0286 | 7.6898 | 7.4112 | 6.3408 | 5.4694 | 4.0796 | 8.5316 | 8.5306 | 8.449 | 8.3847 | 8.0684 | 7.6327 | 7.2102 | 6.7276 | 6.3041 | 4.6082 | 3.3184 | 2.6857
|  | FRESHWATER PRIMARY | EE |  |  |  |  | 8.2342 | 8.2597 | 8.1852 | 8.0781 | 7.8117 | 7.177 | 6.6403 | 6.027 | 5.4383 | 3.3209 | 1.4658 | 0.375 | 8.9469 | 8.9367 | 8.8694 | 8.8745 | 8.6643 | 8.3704 | 8.1388 | 7.8245 | 7.5388 | 6.3408 | 5.4694 | 4.8265 | 8.5337 | 8.5357 | 8.4694 | 8.4296 | 8.1724 | 7.702 | 7.3224 | 6.8633 | 6.4316 | 4.8755 | 3.6265 | 2.9704
|  | FRESHWATER PRIMARY | HT |  |  |  |  | 8.2321 | 8.2526 | 8.1597 | 8.026 | 7.6995 | 7.0903 | 6.5066 | 5.8607 | 5.2781 | 2.875 | 0.84643 | -0.36173 | 8.9449 | 8.9316 | 8.8551 | 8.8418 | 8.5694 | 8.3051 | 8.0286 | 7.6898 | 7.4112 | 6.3663 | 5.7735 | 5.6265 | 8.5316 | 8.5306 | 8.449 | 8.3847 | 8.0684 | 7.6327 | 7.2102 | 6.7276 | 6.3041 | 4.6082 | 3.3184 | 2.6857
|  | FRESHWATER PRIMARY | HE |  |  |  |  | 8.2332 | 8.2607 | 8.1842 | 8.0617 | 7.775 | 7.1791 | 6.5556 | 5.9077 | 5.3423 | 3.5832 | 1.923 | 1.0883 | 8.9439 | 8.9357 | 8.8694 | 8.8724 | 8.6571 | 8.4286 | 8.1276 | 7.8051 | 7.5673 | 6.4724 | 5.6776 | 5.0102 | 8.5316 | 8.5357 | 8.4673 | 8.4194 | 8.151 | 7.7296 | 7.2745 | 6.7949 | 6.399 | 5.099 | 4.0041 | 3.4939
|  | FRESHWATER PRIMARY | FB |  |  |  |  | 8.3444 | 8.4097 | 8.427 | 8.4026 | 8.3546 | 8.2648 | 8.2597 | 8.177 | 8.0954 | 7.3332 | 6.1352 | 5.2526 | 9.0112 | 9.0153 | 8.9959 | 8.9592 | 8.9 | 8.7816 | 8.7306 | 8.599 | 8.4571 | 7.4337 | 5.8878 | 4.0796 | 8.651 | 8.699 | 8.7041 | 8.7041 | 8.6745 | 8.602 | 8.6102 | 8.5276 | 8.4388 | 7.7265 | 6.7143 | 5.901
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FRIMLEY PRIMARY | MINIMUM HEADROOM | SU 87745 57942 | NO | NO | 16.276 | -1.4088 | -1.6425 | -1.9109 | -2.4293 | -3.0037 | -3.916 | -4.9405 | -6.0354 | -7.1078 | -10.8793 | -13.5813 | -14.4925 | 3.2963 | 3.1738 | 2.9769 | 2.4983 | 1.9595 | 1.231 | 0.39422 | -0.5568 | -1.5282 | -4.2813 | -7.1201 | -12.0742 | 0.75442 | 0.55646 | 0.24524 | -0.22721 | -0.78231 | -1.6558 | -2.665 | -3.7966 | -4.9476 | -8.418 | -10.4293 | -10.8772
|  | FRIMLEY PRIMARY | EE |  |  |  |  | -1.4088 | -1.6425 | -1.9109 | -2.3762 | -2.8762 | -3.8109 | -4.8456 | -5.9344 | -6.9925 | -10.3548 | -12.7466 | -13.9854 | 3.2993 | 3.1769 | 2.9881 | 2.5544 | 2.0789 | 1.4697 | 0.73911 | -0.10374 | -0.9466 | -4.2446 | -6.4129 | -8.2129 | 0.75442 | 0.55646 | 0.24524 | -0.1864 | -0.65272 | -1.4211 | -2.3303 | -3.3303 | -4.3395 | -7.7027 | -9.8252 | -10.7599
|  | FRIMLEY PRIMARY | HT |  |  |  |  | -1.4027 | -1.6221 | -1.8874 | -2.3742 | -2.9374 | -3.8884 | -4.9405 | -6.0354 | -7.1078 | -10.8793 | -13.5813 | -14.4925 | 3.2963 | 3.1769 | 2.9769 | 2.4983 | 1.9595 | 1.231 | 0.39422 | -0.5568 | -1.5282 | -4.2813 | -5.5384 | -5.8333 | 0.75646 | 0.5636 | 0.24626 | -0.22721 | -0.78231 | -1.6558 | -2.665 | -3.7966 | -4.9476 | -8.418 | -10.4293 | -10.8772
|  | FRIMLEY PRIMARY | HE |  |  |  |  | -1.4037 | -1.6293 | -1.8946 | -2.4293 | -3.0037 | -3.916 | -4.9374 | -6.0099 | -7.069 | -10.0344 | -12.1578 | -12.8578 | 3.2963 | 3.1738 | 2.985 | 2.5432 | 2.0524 | 1.4442 | 0.71156 | -0.12313 | -0.98027 | -3.9711 | -6.2078 | -7.9395 | 0.75646 | 0.5585 | 0.25544 | -0.21191 | -0.72313 | -1.4813 | -2.3823 | -3.3619 | -4.3793 | -7.2344 | -9.1854 | -9.719
|  | FRIMLEY PRIMARY | FB |  |  |  |  | -1.1293 | -1.2497 | -1.3293 | -1.5813 | -1.7844 | -2.0507 | -2.268 | -2.5078 | -2.7895 | -4.6435 | -6.6895 | -7.7109 | 3.4361 | 3.3146 | 3.235 | 3.0228 | 2.8177 | 2.3371 | 1.8758 | 1.4095 | 0.84728 | -2.5537 | -7.1201 | -12.0742 | 1.2452 | 1.131 | 1.1258 | 0.77993 | 0.62177 | 0.37381 | 0.12891 | -0.13027 | -0.48129 | -2.6201 | -5.2119 | -6.7262
MELKSHAM GSP | FROME BSP | FROME PRIMARY | MINIMUM HEADROOM | ST 78850 48051 | NO | NO | 9.952 | 12.2664 | 11.7317 | 10.9481 | 9.9991 | 8.9246 | 7.1807 | 5.0991 | 2.9491 | 1.0848 | -7.1897 | -13.8274 | -17.3295 | 20.9736 | 20.5328 | 19.9879 | 19.3858 | 18.5246 | 17.5675 | 16.3624 | 15.0001 | 13.9644 | 8.493 | 4.4277 | -0.62948 | 16.4175 | 15.8899 | 15.1736 | 14.3409 | 13.2603 | 11.8654 | 10.2144 | 8.445 | 7.0011 | 0.35929 | -4.7499 | -7.2754
|  | FROME PRIMARY | EE |  |  |  |  | 12.2705 | 11.7348 | 10.9501 | 10.0226 | 8.9695 | 7.2185 | 5.1001 | 2.9491 | 1.0879 | -7.1897 | -13.8274 | -17.3295 | 20.9746 | 20.5338 | 19.9889 | 19.393 | 18.5368 | 17.5817 | 16.3624 | 15.0001 | 13.9675 | 8.493 | 4.4277 | 1.7022 | 16.4185 | 15.893 | 15.1746 | 14.3552 | 13.2909 | 11.8909 | 10.2144 | 8.445 | 7.0011 | 0.35929 | -4.7499 | -7.2754
|  | FROME PRIMARY | HT |  |  |  |  | 12.2685 | 11.7317 | 10.9675 | 10.093 | 9.097 | 7.4613 | 5.4583 | 3.4389 | 1.6715 | -6.5346 | -13.1805 | -16.8815 | 20.9736 | 20.5328 | 19.9879 | 19.395 | 18.5511 | 17.6175 | 16.4144 | 15.0593 | 13.9991 | 9.2695 | 6.2195 | 5.0593 | 16.4175 | 15.8899 | 15.1828 | 14.394 | 13.3644 | 12.0317 | 10.4236 | 8.7256 | 7.3164 | 0.83889 | -4.0489 | -6.4662
|  | FROME PRIMARY | HE |  |  |  |  | 12.2664 | 11.7338 | 10.9481 | 9.9991 | 8.9246 | 7.1807 | 5.0991 | 2.9501 | 1.0848 | -5.9683 | -11.4652 | -14.0417 | 20.9736 | 20.5338 | 19.9889 | 19.3858 | 18.5246 | 17.5675 | 16.3797 | 15.0113 | 13.9644 | 9.0583 | 5.8307 | 3.3491 | 16.4175 | 15.8919 | 15.1736 | 14.3409 | 13.2603 | 11.8654 | 10.2256 | 8.4583 | 7.0052 | 1.3368 | -2.6254 | -4.4397
|  | FROME PRIMARY | FB |  |  |  |  | 12.5124 | 12.1675 | 11.7154 | 11.1787 | 10.6685 | 10.0144 | 9.2613 | 8.5909 | 7.9409 | 3.2215 | -2.0162 | -4.8376 | 21.1001 | 20.7379 | 20.4205 | 19.947 | 19.4654 | 18.8511 | 18.1246 | 17.3562 | 16.6685 | 11.8093 | 5.5409 | -0.62948 | 16.693 | 16.3593 | 15.993 | 15.5001 | 15.0481 | 14.4736 | 13.7817 | 13.094 | 12.4807 | 8.2899 | 3.6073 | 0.8695
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE PRIMARY | MINIMUM HEADROOM | SU 84935 93873 | NO | NO | 1.326 | 12.5357 | 12.5367 | 12.4786 | 12.1347 | 11.6276 | 10.6622 | 9.4173 | 8.2429 | 7.0735 | 2.4806 | -0.49184 | -1.7112 | 16.2469 | 16.2214 | 16.1071 | 15.8796 | 15.5235 | 14.9439 | 14.0286 | 13.1908 | 12.349 | 9.1776 | 6.8888 | 2.5735 | 14.4173 | 14.3276 | 14.2051 | 13.8469 | 13.3133 | 12.5306 | 11.4908 | 10.498 | 9.4939 | 5.5398 | 3.2235 | 2.2469
|  | FRYERS LANE PRIMARY | EE |  |  |  |  | 12.5357 | 12.5367 | 12.4786 | 12.1929 | 11.7908 | 10.8969 | 9.7133 | 8.6214 | 7.5378 | 3.1816 | 0.12449 | -1.4102 | 16.2469 | 16.2214 | 16.1255 | 15.9418 | 15.6398 | 15.1347 | 14.2541 | 13.4857 | 12.7092 | 9.1776 | 6.8888 | 5.1469 | 14.4173 | 14.3276 | 14.2051 | 13.8929 | 13.4408 | 12.7265 | 11.7367 | 10.8347 | 9.9133 | 6.002 | 3.4561 | 2.2469
|  | FRYERS LANE PRIMARY | HT |  |  |  |  | 12.5622 | 12.6092 | 12.5031 | 12.1347 | 11.6276 | 10.6622 | 9.4173 | 8.2429 | 7.0735 | 2.4806 | -0.49184 | -1.7112 | 16.2561 | 16.2276 | 16.1071 | 15.8796 | 15.5235 | 14.9439 | 14.0286 | 13.1908 | 12.349 | 9.351 | 7.9276 | 7.5735 | 14.449 | 14.3633 | 14.2245 | 13.8469 | 13.3133 | 12.5306 | 11.4908 | 10.498 | 9.4939 | 5.5398 | 3.2235 | 2.4867
|  | FRYERS LANE PRIMARY | HE |  |  |  |  | 12.552 | 12.5592 | 12.5143 | 12.1888 | 11.7663 | 10.8837 | 9.8092 | 8.7724 | 7.7276 | 4.348 | 2.1214 | 0.91939 | 16.2531 | 16.2255 | 16.1347 | 15.948 | 15.6582 | 15.1122 | 14.299 | 13.5408 | 12.7633 | 9.7582 | 7.9224 | 6.1867 | 14.4347 | 14.3469 | 14.2388 | 13.901 | 13.4408 | 12.7133 | 11.8143 | 10.95 | 10.0571 | 7.0337 | 5.298 | 4.3673
|  | FRYERS LANE PRIMARY | FB |  |  |  |  | 12.7959 | 12.85 | 12.9357 | 13.0612 | 13.0673 | 12.9602 | 12.8 | 12.5571 | 12.3153 | 10.0765 | 7.2224 | 5.0653 | 16.3582 | 16.2837 | 16.2235 | 16.2133 | 16.0816 | 15.8347 | 15.5469 | 15.1796 | 14.7551 | 11.6429 | 7.4245 | 2.5735 | 14.7173 | 14.6224 | 14.6173 | 14.7347 | 14.7051 | 14.5622 | 14.3633 | 14.0704 | 13.7939 | 11.5684 | 8.8265 | 6.6367
COWLEY GSP | DRAYTON BSP | FULSCOT PRIMARY | MINIMUM HEADROOM | SU 54413 89511 | NO | YES | 7.803 | 10.3524 | 9.8841 | 9.4524 | 9.0973 | 8.6188 | 7.8137 | 6.481 | 4.2565 | 0.87794 | -3.117 | -7.2129 | -10.9251 | 17.1892 | 16.8596 | 16.4626 | 16.13 | 15.6983 | 15.1912 | 14.1637 | 12.1698 | 8.5361 | 4.5402 | 0.44427 | -4.5149 | 11.9483 | 11.582 | 11.179 | 10.8443 | 10.4065 | 9.7463 | 8.5728 | 6.3688 | 2.6096 | -1.4445 | -5.6772 | -9.8966
|  | FULSCOT PRIMARY | EE |  |  |  |  | 10.3606 | 9.929 | 9.5075 | 9.1188 | 8.679 | 7.831 | 6.6932 | 5.3116 | 3.8086 | -0.19145 | -5.5017 | -7.6363 | 17.2126 | 16.9555 | 16.6055 | 16.282 | 15.8718 | 15.3708 | 14.5545 | 13.4983 | 12.2055 | 8.7443 | 3.2647 | 0.62998 | 11.9739 | 11.6432 | 11.2596 | 10.9147 | 10.5188 | 9.8555 | 8.9004 | 7.6892 | 6.2657 | 2.4922 | -3.1833 | -5.269
|  | FULSCOT PRIMARY | HT |  |  |  |  | 10.3524 | 9.8841 | 9.4524 | 9.0973 | 8.6188 | 7.8137 | 6.5708 | 5.1514 | 3.1167 | -1.4517 | -6.5547 | -9.9027 | 17.1892 | 16.8596 | 16.4626 | 16.13 | 15.6983 | 15.1912 | 14.1637 | 12.9473 | 10.8841 | 7.0045 | 2.3892 | -0.4139 | 11.9483 | 11.582 | 11.179 | 10.8443 | 10.4065 | 9.7463 | 8.5728 | 7.2453 | 5.1004 | 0.84937 | -4.4037 | -7.7914
|  | FULSCOT PRIMARY | HE |  |  |  |  | 10.3626 | 9.933 | 9.5106 | 9.1167 | 8.6677 | 7.8453 | 6.481 | 4.2565 | 0.87794 | -3.117 | -7.2129 | -10.9251 | 17.2126 | 16.9555 | 16.6055 | 16.281 | 15.8647 | 15.3851 | 14.28 | 12.1698 | 8.5361 | 4.5402 | 0.44427 | -4.5149 | 11.9749 | 11.6453 | 11.2647 | 10.9126 | 10.5086 | 9.8759 | 8.631 | 6.3688 | 2.6096 | -1.4445 | -5.6772 | -9.8966
|  | FULSCOT PRIMARY | FB |  |  |  |  | 10.5932 | 10.4055 | 10.2279 | 10.2402 | 10.1534 | 9.8157 | 9.4055 | 8.8851 | 8.181 | 5.6279 | 2.4718 | 0.24835 | 17.3514 | 17.1688 | 17.0075 | 16.9769 | 16.8239 | 16.3953 | 15.9086 | 15.3371 | 14.482 | 11.0534 | 6.3902 | 1.6024 | 12.2065 | 12.0443 | 11.9045 | 11.9351 | 11.8575 | 11.4963 | 11.0871 | 10.5718 | 9.7953 | 7.0606 | 3.7004 | 1.231
COWLEY GSP | WITNEY BSP | FYFIELD PRIMARY | MINIMUM HEADROOM | SU 42256 99551 | NO | NO | 7.492 | 0.63867 | 0.37439 | -0.097041 | -0.72153 | -1.3613 | -2.3317 | -2.9521 | -3.6083 | -4.2134 | -5.843 | -7.4032 | -8.5001 | 1.5831 | 1.4341 | 1.1371 | 0.85551 | 0.51776 | 0.07898 | -0.32408 | -0.75776 | -1.1384 | -2.4894 | -3.0445 | -4.2027 | 2.2922 | 2.13 | 1.7331 | 1.2902 | 0.83102 | 0.13816 | -0.34551 | -0.87306 | -1.3465 | -2.8465 | -3.8496 | -4.4312
|  | FYFIELD PRIMARY | EE |  |  |  |  | 0.63867 | 0.37439 | -0.095 | -0.68888 | -1.3501 | -2.2021 | -2.8287 | -3.4246 | -3.9919 | -5.7113 | -6.9644 | -7.796 | 1.5841 | 1.4555 | 1.18 | 0.93306 | 0.62286 | 0.25959 | -0.13939 | -0.52714 | -0.95571 | -2.3455 | -3.0445 | -3.5833 | 2.2922 | 2.13 | 1.7351 | 1.3086 | 0.83102 | 0.21776 | -0.28429 | -0.76694 | -1.2231 | -2.6404 | -3.4996 | -3.97
|  | FYFIELD PRIMARY | HT |  |  |  |  | 0.66827 | 0.42643 | 0.013163 | -0.52765 | -1.1491 | -2.0021 | -2.6072 | -3.2307 | -3.8083 | -5.843 | -7.4032 | -8.5001 | 1.5831 | 1.4341 | 1.1371 | 0.85551 | 0.51776 | 0.07898 | -0.32408 | -0.75776 | -1.1384 | -2.4894 | -2.8996 | -3.0506 | 2.3045 | 2.1504 | 1.7647 | 1.3535 | 0.8851 | 0.2402 | -0.25163 | -0.77204 | -1.2435 | -2.8465 | -3.8496 | -4.4312
|  | FYFIELD PRIMARY | HE |  |  |  |  | 0.64173 | 0.37541 | -0.097041 | -0.72153 | -1.3613 | -2.3317 | -2.9521 | -3.6083 | -4.2134 | -5.443 | -6.5879 | -7.3123 | 1.5851 | 1.4545 | 1.179 | 0.93 | 0.66367 | 0.23 | -0.12408 | -0.53837 | -0.95776 | -2.1578 | -2.7669 | -3.3914 | 2.2933 | 2.132 | 1.7331 | 1.2902 | 0.83918 | 0.13816 | -0.34551 | -0.87306 | -1.3465 | -2.4261 | -3.1965 | -3.6537
|  | FYFIELD PRIMARY | FB |  |  |  |  | 0.83765 | 0.73255 | 0.50806 | 0.23867 | 0.015204 | -0.32255 | -0.51439 | -0.69092 | -0.81235 | -1.9134 | -3.0838 | -3.8583 | 1.7004 | 1.6065 | 1.4912 | 1.3586 | 1.2586 | 1.0504 | 0.78816 | 0.56265 | 0.38714 | -0.94041 | -2.5486 | -4.2027 | 2.4147 | 2.3422 | 2.229 | 2.0708 | 1.9259 | 1.7208 | 1.4412 | 1.2708 | 1.1535 | 0.14224 | -0.89959 | -1.5424
LOVEDEAN GSP | HAVANT BSP | GABLE HEAD PRIMARY | MINIMUM HEADROOM | SZ 72204 99904 | NO | YES | 2.065 | 16.7782 | 16.8761 | 16.6863 | 16.1782 | 15.6761 | 14.6455 | 13.5812 | 12.4445 | 11.3384 | 7.2363 | 3.9139 | 1.9169 | 18.2353 | 18.2516 | 18.1026 | 17.7741 | 17.4435 | 16.9251 | 16.3547 | 15.7026 | 15.0935 | 13.0894 | 11.0914 | 7.3159 | 17.4077 | 17.4537 | 17.3006 | 16.8445 | 16.4057 | 15.6077 | 14.7853 | 13.8833 | 13.02 | 10.0506 | 7.9547 | 6.8955
|  | GABLE HEAD PRIMARY | EE |  |  |  |  | 16.7822 | 16.9098 | 16.7914 | 16.3822 | 16.0057 | 15.0455 | 14.0424 | 12.9873 | 11.9618 | 8.4047 | 5.4261 | 3.5343 | 18.2384 | 18.272 | 18.1557 | 17.872 | 17.5945 | 17.1333 | 16.6077 | 16.0047 | 15.4526 | 13.0894 | 11.3353 | 9.8128 | 17.4128 | 17.4802 | 17.3771 | 16.9924 | 16.6445 | 15.9179 | 15.1475 | 14.3047 | 13.5108 | 10.8333 | 8.8537 | 7.7547
|  | GABLE HEAD PRIMARY | HT |  |  |  |  | 16.7782 | 16.8761 | 16.6863 | 16.1782 | 15.6761 | 14.6455 | 13.5812 | 12.4445 | 11.3384 | 7.2363 | 3.9139 | 1.9169 | 18.2353 | 18.2516 | 18.1026 | 17.7741 | 17.4435 | 16.9251 | 16.3547 | 15.7026 | 15.0935 | 13.1669 | 12.1037 | 11.6955 | 17.4077 | 17.4537 | 17.3006 | 16.8445 | 16.4057 | 15.6077 | 14.7853 | 13.8833 | 13.02 | 10.0506 | 7.9547 | 6.8955
|  | GABLE HEAD PRIMARY | HE |  |  |  |  | 16.7792 | 16.9098 | 16.7894 | 16.3312 | 15.8965 | 14.8577 | 13.7588 | 12.6241 | 11.4771 | 8.573 | 5.9965 | 4.5526 | 18.2363 | 18.271 | 18.1516 | 17.8618 | 17.569 | 17.1067 | 16.5598 | 15.9792 | 15.4006 | 13.22 | 11.5965 | 9.9833 | 17.4108 | 17.4782 | 17.3741 | 16.9628 | 16.5771 | 15.8077 | 14.9771 | 14.1179 | 13.2455 | 11.0026 | 9.3057 | 8.4016
|  | GABLE HEAD PRIMARY | FB |  |  |  |  | 17.0455 | 17.1649 | 17.2455 | 17.3179 | 17.3057 | 17.2261 | 17.1149 | 16.9659 | 16.6322 | 15.0659 | 12.9822 | 11.6904 | 18.3945 | 18.3812 | 18.3302 | 18.3169 | 18.1812 | 17.9547 | 17.6822 | 17.3853 | 16.9088 | 14.5016 | 11.0914 | 7.3159 | 17.672 | 17.7404 | 17.77 | 17.8567 | 17.8353 | 17.7435 | 17.622 | 17.4608 | 17.073 | 15.5047 | 13.6384 | 12.5741
MINETY GSP |  | GALILEO PRIMARY | MINIMUM HEADROOM | SU 10596 83733 | NO | NO | 4.591 | 28.5208 | 28.3779 | 28.3249 | 28.2198 | 27.9881 | 27.5616 | 26.9932 | 26.4198 | 25.9341 | 24.5851 | 23.5483 | 23.0534 | 28.9943 | 28.8473 | 28.8157 | 28.7626 | 28.5922 | 28.3198 | 27.8932 | 27.4606 | 27.0953 | 26.0494 | 24.5126 | 22.2494 | 28.9841 | 28.8463 | 28.8065 | 28.7259 | 28.5432 | 28.2116 | 27.7402 | 27.2626 | 26.8698 | 25.8912 | 25.0596 | 24.6269
|  | GALILEO PRIMARY | EE |  |  |  |  | 28.5208 | 28.4851 | 28.3249 | 28.2259 | 28.1239 | 27.7749 | 27.2841 | 26.7208 | 26.23 | 24.5953 | 23.682 | 23.1636 | 28.9943 | 28.9698 | 28.8157 | 28.7647 | 28.7412 | 28.5555 | 28.2249 | 27.7973 | 27.4616 | 26.0494 | 25.131 | 24.1861 | 28.9841 | 28.9585 | 28.8065 | 28.7259 | 28.682 | 28.431 | 28.0443 | 27.5861 | 27.1973 | 25.8912 | 25.0596 | 24.6269
|  | GALILEO PRIMARY | HT |  |  |  |  | 28.5269 | 28.3779 | 28.3402 | 28.2351 | 27.9881 | 27.5616 | 26.9932 | 26.4198 | 25.9341 | 24.5851 | 23.5483 | 23.0534 | 28.9943 | 28.8473 | 28.8167 | 28.7647 | 28.5922 | 28.3198 | 27.8932 | 27.4606 | 27.0953 | 26.4085 | 25.9708 | 25.7402 | 28.9881 | 28.8463 | 28.8177 | 28.732 | 28.5432 | 28.2116 | 27.7402 | 27.2626 | 26.8698 | 25.9024 | 25.1881 | 24.8769
|  | GALILEO PRIMARY | HE |  |  |  |  | 28.5259 | 28.4953 | 28.3443 | 28.2198 | 28.1014 | 27.7881 | 27.3269 | 26.7871 | 26.333 | 24.932 | 24.1902 | 23.7932 | 28.9943 | 28.9698 | 28.8208 | 28.7626 | 28.7392 | 28.5534 | 28.2198 | 27.779 | 27.4279 | 26.1341 | 25.3004 | 24.3636 | 28.9892 | 28.9677 | 28.8239 | 28.7402 | 28.6718 | 28.4371 | 28.0636 | 27.6126 | 27.233 | 26.1453 | 25.5667 | 25.2534
|  | GALILEO PRIMARY | FB |  |  |  |  | 28.6126 | 28.6239 | 28.6126 | 28.4596 | 28.4412 | 28.383 | 28.2514 | 28.083 | 27.8871 | 26.6514 | 25.9188 | 25.43 | 29.0341 | 29.0126 | 28.9759 | 28.8198 | 28.7626 | 28.6412 | 28.4381 | 28.2228 | 27.9565 | 26.2412 | 24.5126 | 22.2494 | 29.0636 | 29.0739 | 29.0688 | 28.9279 | 28.9085 | 28.8626 | 28.7626 | 28.6157 | 28.4341 | 27.3055 | 26.7075 | 26.28
LOVEDEAN GSP | PORTSMOUTH BSP | GAMBLE ROAD PRIMARY | MINIMUM HEADROOM | SU 64771 01769 | NO | YES | 9.36 | 4.5048 | 4.3364 | 4.0191 | 3.4456 | 2.4905 | 1.3089 | -0.17788 | -1.5391 | -2.9401 | -9.636 | -13.5167 | -15.9156 | 7.2936 | 7.0772 | 6.818 | 6.4293 | 5.7568 | 5.1017 | 4.0976 | 3.2568 | 2.366 | -2.5483 | -8.2707 | -16.8952 | 5.4303 | 5.4007 | 5.1415 | 4.665 | 3.8538 | 2.9374 | 1.6895 | 0.58947 | -0.55135 | -6.382 | -10.0034 | -12.0513
|  | GAMBLE ROAD PRIMARY | EE |  |  |  |  | 4.5048 | 4.5425 | 4.2333 | 3.7242 | 3.0762 | 1.8303 | 0.52722 | -0.93094 | -2.2983 | -8.8513 | -13.5116 | -15.9156 | 7.2936 | 7.1925 | 6.9446 | 6.5833 | 6.068 | 5.3262 | 4.5344 | 3.5517 | 2.6752 | -2.5483 | -6.5779 | -10.3289 | 5.4303 | 5.4997 | 5.2813 | 4.8691 | 4.3119 | 3.3242 | 2.2813 | 1.0691 | -0.045224 | -5.9116 | -10.0034 | -12.0513
|  | GAMBLE ROAD PRIMARY | HT |  |  |  |  | 4.5384 | 4.3364 | 4.0191 | 3.4456 | 2.4905 | 1.3089 | -0.17788 | -1.5391 | -2.9401 | -9.636 | -13.5167 | -15.2993 | 7.2997 | 7.0772 | 6.818 | 6.4293 | 5.7568 | 5.1017 | 4.0976 | 3.2568 | 2.366 | -1.5218 | -3.7962 | -4.8258 | 5.4589 | 5.4007 | 5.1415 | 4.665 | 3.8538 | 2.9374 | 1.6895 | 0.58947 | -0.55135 | -6.382 | -9.6564 | -10.984
|  | GAMBLE ROAD PRIMARY | HE |  |  |  |  | 4.5354 | 4.6017 | 4.3884 | 3.9333 | 3.3456 | 2.416 | 1.3242 | 0.33947 | -0.72278 | -6.0799 | -9.6503 | -11.3728 | 7.3017 | 7.2038 | 6.9854 | 6.6466 | 6.1782 | 5.4976 | 4.6395 | 3.9201 | 3.1099 | -1.5891 | -5.1697 | -8.6809 | 5.4589 | 5.5487 | 5.415 | 5.0333 | 4.515 | 3.7344 | 2.7782 | 1.9476 | 1.0333 | -3.6656 | -6.7218 | -8.1564
|  | GAMBLE ROAD PRIMARY | FB |  |  |  |  | 4.6936 | 4.8609 | 5.0078 | 4.8048 | 4.6201 | 4.2313 | 3.667 | 3.1527 | 2.5405 | -1.0269 | -6.4534 | -9.4952 | 7.3078 | 7.217 | 7.1058 | 6.8089 | 6.4936 | 5.9793 | 5.3007 | 4.6803 | 3.9527 | -0.67278 | -8.2707 | -16.8952 | 5.567 | 5.7231 | 5.8538 | 5.7742 | 5.6293 | 5.3119 | 4.8425 | 4.4282 | 3.9089 | 0.74049 | -4.1687 | -7.0503
IVER 132KV GSP | DENHAM BSP | GERRARDS CROSS PRIMARY | MINIMUM HEADROOM | SU 99973 87964 | NO | YES | 1.763 | -0.76505 | -0.75689 | -0.73342 | -0.98444 | 24.6724 | 23.9827 | 23.2224 | 22.4041 | 21.601 | 18.8143 | 16.7255 | 15.6102 | 2.7974 | 2.7383 | 2.7546 | 2.6128 | 26.9122 | 26.5704 | 26.1724 | 25.6163 | 25.1541 | 23.8082 | 22.901 | 21.6633 | -0.23469 | -0.2602 | -0.25918 | -0.41531 | 24.6306 | 24.1633 | 23.6102 | 22.8827 | 22.25 | 20.2459 | 18.9765 | 18.4857
|  | GERRARDS CROSS PRIMARY | EE |  |  |  |  | -0.76403 | -0.71301 | -0.69158 | -0.87526 | 24.8837 | 24.2714 | 23.5745 | 22.7827 | 22.048 | 19.6133 | 17.6408 | 16.5929 | 2.7974 | 2.7842 | 2.773 | 2.6709 | 27.0041 | 26.7122 | 26.3531 | 25.8296 | 25.4061 | 23.8316 | 22.901 | 22.2041 | -0.23265 | -0.20612 | -0.23367 | -0.34184 | 24.7694 | 24.3571 | 23.8673 | 23.2122 | 22.6214 | 20.7398 | 19.4888 | 18.952
|  | GERRARDS CROSS PRIMARY | HT |  |  |  |  | -0.76505 | -0.75689 | -0.73342 | -0.98444 | 24.6724 | 23.9827 | 23.2224 | 22.4041 | 21.601 | 18.8143 | 16.7255 | 15.6102 | 2.7974 | 2.7383 | 2.7546 | 2.6128 | 26.9122 | 26.5704 | 26.1724 | 25.6163 | 25.1541 | 23.8082 | 23.2602 | 23.1745 | -0.23469 | -0.2602 | -0.25918 | -0.41531 | 24.6306 | 24.1633 | 23.6102 | 22.8827 | 22.25 | 20.2459 | 18.9765 | 18.4857
|  | GERRARDS CROSS PRIMARY | HE |  |  |  |  | -0.76403 | -0.6273 | -0.6926 | -0.91607 | 24.7949 | 24.1316 | 23.3735 | 22.5592 | 21.7765 | 19.8408 | 18.1531 | 17.3561 | 2.7974 | 2.876 | 2.7679 | 2.6577 | 26.9827 | 26.6878 | 26.3276 | 25.901 | 25.5163 | 24.1327 | 23.1765 | 22.3673 | -0.23367 | -0.14592 | -0.23367 | -0.36531 | 24.7214 | 24.2827 | 23.7633 | 23.1816 | 22.6041 | 21.0663 | 19.9041 | 19.4633
|  | GERRARDS CROSS PRIMARY | FB |  |  |  |  | -0.53036 | -0.41097 | -0.36199 | -0.35689 | 25.6 | 25.5214 | 25.4153 | 25.2776 | 25.1296 | 24.1745 | 23.2439 | 22.9337 | 2.9617 | 2.9974 | 2.9923 | 3.0107 | 27.4316 | 27.2847 | 27.1102 | 26.9112 | 26.6908 | 25.3112 | 23.5153 | 21.6633 | -0.057143 | 0.033673 | 0.077551 | 0.072449 | 25.3582 | 25.3153 | 25.2347 | 25.1143 | 24.9888 | 24.1704 | 23.301 | 22.9663
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM PRIMARY | MINIMUM HEADROOM | ST 80185 25765 | NO | NO | 9.028 | 26.1092 | 26.0878 | 26.0551 | 25.8082 | 25.5123 | 25.1725 | 24.8551 | 24.4684 | 24.0847 | 22.5796 | 21.6041 | 20.9929 | 26.3899 | 26.3664 | 26.3368 | 26.1246 | 25.9297 | 25.7338 | 25.5542 | 25.3073 | 25.0777 | 24.1113 | 23.494 | 22.7011 | 25.696 | 25.6675 | 25.6266 | 25.4471 | 25.2185 | 24.9705 | 24.7358 | 24.4379 | 24.144 | 23.0073 | 22.3389 | 21.9654
|  | GILLINGHAM PRIMARY | EE |  |  |  |  | 26.1102 | 26.097 | 26.0653 | 25.8123 | 25.5939 | 25.3102 | 24.9888 | 24.6368 | 24.2786 | 22.898 | 21.9592 | 21.3745 | 26.392 | 26.3726 | 26.3501 | 26.1246 | 25.9573 | 25.8093 | 25.6185 | 25.3991 | 25.1828 | 24.1113 | 23.494 | 23.0001 | 25.6981 | 25.6766 | 25.6491 | 25.4481 | 25.2797 | 25.0787 | 24.844 | 24.5705 | 24.292 | 23.2175 | 22.542 | 22.1501
|  | GILLINGHAM PRIMARY | HT |  |  |  |  | 26.1092 | 26.0878 | 26.0551 | 25.8082 | 25.5123 | 25.1725 | 24.8551 | 24.4684 | 24.0847 | 22.5796 | 21.6041 | 20.9929 | 26.3899 | 26.3664 | 26.3368 | 26.1542 | 25.9297 | 25.7338 | 25.5542 | 25.3073 | 25.0777 | 24.1185 | 23.7062 | 23.5185 | 25.696 | 25.6675 | 25.6266 | 25.4471 | 25.2185 | 24.9705 | 24.7358 | 24.4379 | 24.144 | 23.0073 | 22.3389 | 21.9654
|  | GILLINGHAM PRIMARY | HE |  |  |  |  | 26.1102 | 26.097 | 26.0664 | 25.8664 | 25.5766 | 25.2796 | 25.0092 | 24.649 | 24.2439 | 23.2153 | 22.4449 | 22.0388 | 26.392 | 26.3746 | 26.3501 | 26.1787 | 25.946 | 25.7848 | 25.6481 | 25.4236 | 25.1634 | 24.3307 | 23.8236 | 23.394 | 25.6981 | 25.6777 | 25.6501 | 25.493 | 25.2664 | 25.0511 | 24.8644 | 24.5858 | 24.2726 | 23.4715 | 22.9287 | 22.6634
|  | GILLINGHAM PRIMARY | FB |  |  |  |  | 26.1592 | 26.1745 | 26.1755 | 26.1633 | 26.1633 | 26.1337 | 25.9021 | 25.8266 | 25.7021 | 25.0572 | 24.2521 | 23.6419 | 26.4338 | 26.4358 | 26.4307 | 26.4154 | 26.3787 | 26.3011 | 26.0185 | 25.9226 | 25.7777 | 24.9909 | 23.9144 | 22.7011 | 25.7664 | 25.7848 | 25.7868 | 25.7766 | 25.7715 | 25.7287 | 25.5379 | 25.4746 | 25.3715 | 24.8348 | 24.1501 | 23.6481
FLEET-BRAMLEY GSP | ALDERSHOT BSP | GODALMING PRIMARY | MINIMUM HEADROOM | SU 96743 44375 | NO | YES | 3.967 | 10.048 | 9.7653 | 9.2582 | 8.6918 | 8.0602 | 7.2071 | 6.1378 | 5.0776 | 3.8959 | 0.57245 | -1.1429 | -1.6898 | 14.0204 | 13.75 | 13.2847 | 12.7418 | 12.1541 | 11.3847 | 10.4612 | 9.548 | 8.5235 | 5.4745 | 3.0602 | -1.4459 | 11.2633 | 11.0184 | 10.5765 | 10.0714 | 9.4827 | 8.6643 | 7.6571 | 6.6827 | 5.5592 | 2.3408 | 0.73878 | 0.35
|  | GODALMING PRIMARY | EE |  |  |  |  | 10.0724 | 9.8908 | 9.5214 | 9.1347 | 8.6837 | 8.0949 | 7.2929 | 6.5398 | 5.7745 | 2.449 | 0.46735 | -0.44592 | 14.0316 | 13.8173 | 13.4184 | 12.9755 | 12.4531 | 11.8418 | 11.052 | 10.3163 | 9.5684 | 6.0163 | 3.7092 | 1.9316 | 11.2786 | 11.1031 | 10.7531 | 10.3806 | 9.9276 | 9.3 | 8.5041 | 7.7653 | 7.002 | 3.6939 | 1.8082 | 0.99388
|  | GODALMING PRIMARY | HT |  |  |  |  | 10.048 | 9.7653 | 9.2582 | 8.6918 | 8.0602 | 7.2071 | 6.1378 | 5.0776 | 3.8959 | 0.57245 | -1.1429 | -1.6898 | 14.0204 | 13.75 | 13.2847 | 12.7418 | 12.1541 | 11.3847 | 10.4612 | 9.548 | 8.5235 | 5.4745 | 3.9918 | 3.5306 | 11.2633 | 11.0184 | 10.5765 | 10.0714 | 9.4827 | 8.6643 | 7.6571 | 6.6827 | 5.5592 | 2.3408 | 0.73878 | 0.35
|  | GODALMING PRIMARY | HE |  |  |  |  | 10.0704 | 9.8918 | 9.5184 | 9.1173 | 8.6796 | 8.1194 | 7.2582 | 6.5071 | 5.7133 | 2.8551 | 1.0061 | 0.35408 | 14.0316 | 13.8153 | 13.4153 | 12.9694 | 12.4592 | 11.8796 | 11.0296 | 10.2898 | 9.5092 | 6.2745 | 4.0245 | 2.3541 | 11.2765 | 11.1031 | 10.751 | 10.3663 | 9.9194 | 9.3582 | 8.4735 | 7.7367 | 6.9449 | 4.1102 | 2.3633 | 1.8224
|  | GODALMING PRIMARY | FB |  |  |  |  | 10.348 | 10.1459 | 10.0031 | 9.802 | 9.6082 | 9.3694 | 9.0612 | 8.7071 | 8.3551 | 5.8949 | 3.199 | 1.6939 | 14.2112 | 13.9102 | 13.6857 | 13.3704 | 13.0235 | 12.6061 | 12.1 | 11.5439 | 11.0082 | 7.4816 | 3.0602 | -1.4459 | 11.5531 | 11.3561 | 11.2296 | 11.0347 | 10.8439 | 10.6102 | 10.3082 | 9.9439 | 9.5724 | 7.0449 | 4.3439 | 2.8388
WILLESDEN GSP | ACTON LANE BSP | GOLDSMITHS PRIMARY | MINIMUM HEADROOM | TQ 21089 80758 | NO | YES | 2.015 | 5.153 | 5.107 | 5.1346 | 5.0244 | 3.8999 | 2.6468 | 1.1223 | -0.36338 | -1.5001 | -3.7766 | -5.2144 | -5.8705 | 6.8356 | 6.7274 | 6.7101 | 6.3672 | 5.2111 | 4.2234 | 2.7887 | 1.4458 | 0.42234 | -1.3368 | -4.5664 | -8.5532 | 5.6427 | 5.5509 | 5.5601 | 5.3387 | 3.9356 | 2.6601 | 1.0642 | -0.44501 | -1.6052 | -3.7573 | -5.0368 | -5.443
|  | GOLDSMITHS PRIMARY | EE |  |  |  |  | 5.153 | 5.2101 | 5.1346 | 5.0336 | 4.9489 | 4.1734 | 3.0713 | 1.6193 | 0.36622 | -3.7419 | -5.2144 | -5.8705 | 6.8458 | 6.8509 | 6.7101 | 6.3672 | 6.1632 | 5.5764 | 4.5336 | 3.3815 | 2.3376 | -1.3164 | -2.8685 | -4.4573 | 5.6427 | 5.6907 | 5.5601 | 5.3387 | 5.2611 | 4.353 | 3.0734 | 1.5846 | 0.34275 | -3.7573 | -5.0368 | -5.443
|  | GOLDSMITHS PRIMARY | HT |  |  |  |  | 5.1621 | 5.107 | 5.1672 | 5.0642 | 3.8999 | 2.6468 | 1.1223 | -0.36338 | -1.5001 | -3.7766 | -5.0766 | -5.5501 | 6.8448 | 6.7274 | 6.7111 | 6.3672 | 5.2111 | 4.2234 | 2.7887 | 1.4458 | 0.42234 | -0.75929 | -1.4562 | -1.9103 | 5.654 | 5.5509 | 5.5917 | 5.3672 | 3.9356 | 2.6601 | 1.0642 | -0.44501 | -1.6052 | -3.7185 | -4.8124 | -5.1562
|  | GOLDSMITHS PRIMARY | HE |  |  |  |  | 5.1601 | 5.2244 | 5.1458 | 5.0244 | 4.9101 | 4.1081 | 2.9785 | 1.5366 | 0.28764 | -3.1083 | -3.943 | -4.4644 | 6.8478 | 6.8509 | 6.7101 | 6.3683 | 6.156 | 5.5468 | 4.4744 | 3.2846 | 2.1927 | -1.0736 | -2.3654 | -3.9501 | 5.6489 | 5.7019 | 5.5713 | 5.3478 | 5.2397 | 4.2989 | 2.9825 | 1.4938 | 0.23866 | -3.2226 | -3.8991 | -4.2797
|  | GOLDSMITHS PRIMARY | FB |  |  |  |  | 5.2336 | 5.3468 | 5.4305 | 5.3407 | 5.3999 | 5.4172 | 4.7611 | 4.1356 | 3.1478 | -1.0573 | -2.4644 | -3.4297 | 6.8356 | 6.8346 | 6.806 | 6.6172 | 6.5315 | 6.3927 | 5.5917 | 4.8254 | 3.7672 | -1.3368 | -4.5664 | -8.5532 | 5.7397 | 5.8397 | 5.9183 | 5.7897 | 5.8325 | 5.856 | 5.053 | 4.2836 | 3.204 | -1.3226 | -2.7675 | -3.6266
NURSLING GSP | WINCHESTER BSP | GORDON ROAD PRIMARY | MINIMUM HEADROOM | SU 48217 29991 | NO | NO | 4.242 | 6.3625 | 6.1951 | 5.9461 | 5.6063 | 5.0676 | 4.391 | 3.7196 | 3.0747 | 2.3808 | -0.6712 | -3.4375 | -4.4314 | 8.9186 | 8.6278 | 8.2706 | 7.99 | 7.3053 | 6.7084 | 5.9686 | 5.3349 | 4.4614 | 1.7666 | -0.64467 | -3.9763 | 6.9788 | 6.8329 | 6.6186 | 6.3604 | 5.9084 | 5.3859 | 4.8421 | 4.3247 | 3.488 | 0.26859 | -2.0243 | -2.6937
|  | GORDON ROAD PRIMARY | EE |  |  |  |  | 6.3625 | 6.1951 | 5.9461 | 5.6247 | 5.1543 | 4.5217 | 3.8961 | 3.3798 | 2.838 | 0.015531 | -2.9651 | -3.9865 | 8.9206 | 8.6308 | 8.2839 | 8.0359 | 7.489 | 6.8921 | 6.0859 | 5.537 | 4.8972 | 1.7666 | -0.64467 | -1.8079 | 6.9788 | 6.8329 | 6.6186 | 6.3727 | 5.988 | 5.5063 | 4.9972 | 4.5747 | 3.9584 | 0.6992 | -1.8253 | -2.5426
|  | GORDON ROAD PRIMARY | HT |  |  |  |  | 6.3717 | 6.2186 | 5.9727 | 5.6114 | 5.0676 | 4.391 | 3.7196 | 3.0747 | 2.3808 | -0.6712 | -3.4375 | -4.4314 | 8.9206 | 8.6278 | 8.2706 | 7.99 | 7.3053 | 6.7084 | 5.9686 | 5.3349 | 4.4614 | 1.8676 | 0.12471 | -0.33855 | 6.99 | 6.8594 | 6.6502 | 6.3655 | 5.9084 | 5.3859 | 4.8421 | 4.3247 | 3.488 | 0.26859 | -2.0243 | -2.6937
|  | GORDON ROAD PRIMARY | HE |  |  |  |  | 6.3635 | 6.1992 | 5.9543 | 5.6063 | 5.1206 | 4.4941 | 3.891 | 3.3635 | 2.8298 | 0.82573 | -1.163 | -2.1192 | 8.9186 | 8.6298 | 8.3023 | 8.0247 | 7.5043 | 6.8655 | 6.0604 | 5.4737 | 4.8278 | 2.2145 | 0.23288 | -1.1222 | 6.9798 | 6.84 | 6.6329 | 6.3604 | 5.9655 | 5.4798 | 4.9829 | 4.5512 | 3.9543 | 1.5074 | -0.27222 | -0.99569
|  | GORDON ROAD PRIMARY | FB |  |  |  |  | 6.4523 | 6.3768 | 6.239 | 6.0074 | 5.738 | 5.4461 | 5.1778 | 4.9574 | 4.6839 | 3.5482 | 1.9778 | -0.016102 | 8.9482 | 8.7757 | 8.5217 | 8.2625 | 7.9339 | 7.5819 | 7.0819 | 6.7625 | 6.2278 | 3.6012 | -0.08651 | -3.9763 | 7.0666 | 7.0074 | 6.9002 | 6.7186 | 6.5053 | 6.2778 | 6.0461 | 5.8676 | 5.6217 | 4.5288 | 2.0084 | 0.1492
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | GORING PRIMARY | MINIMUM HEADROOM | SU 60305 82895 | NO | NO | 0.207 | 9.5602 | 9.5561 | 9.5531 | 9.5255 | 9.3592 | 9.1694 | 8.899 | 8.5918 | 8.3459 | 7.5571 | 6.9316 | 6.6398 | 10.5949 | 10.5612 | 10.5337 | 10.4959 | 10.3173 | 10.1541 | 9.9776 | 9.7816 | 9.5959 | 9.0694 | 8.6643 | 7.9367 | 8.101 | 8.0929 | 8.0939 | 8.0449 | 7.9408 | 7.8337 | 7.6571 | 7.4673 | 7.3051 | 6.8388 | 6.5112 | 6.4051
|  | GORING PRIMARY | EE |  |  |  |  | 9.5602 | 9.5786 | 9.5531 | 9.5255 | 9.3714 | 9.2245 | 8.9418 | 8.6531 | 8.3796 | 7.5571 | 6.9418 | 6.7 | 10.5959 | 10.5806 | 10.5357 | 10.5041 | 10.3173 | 10.249 | 10.05 | 9.85 | 9.6653 | 9.0694 | 8.6643 | 8.4286 | 8.101 | 8.1041 | 8.0939 | 8.05 | 7.9541 | 7.8531 | 7.6806 | 7.4959 | 7.3306 | 6.85 | 6.552 | 6.4663
|  | GORING PRIMARY | HT |  |  |  |  | 9.5602 | 9.5561 | 9.5541 | 9.5316 | 9.4704 | 9.1694 | 8.9296 | 8.6714 | 8.4153 | 7.5847 | 6.9316 | 6.6398 | 10.5959 | 10.5612 | 10.5337 | 10.4959 | 10.4143 | 10.1541 | 9.9776 | 9.7816 | 9.5959 | 9.1153 | 8.848 | 8.8286 | 8.102 | 8.0929 | 8.0949 | 8.0531 | 7.9786 | 7.8337 | 7.6796 | 7.5143 | 7.3571 | 6.8388 | 6.5112 | 6.4051
|  | GORING PRIMARY | HE |  |  |  |  | 9.5612 | 9.5582 | 9.5571 | 9.5367 | 9.3592 | 9.1969 | 8.899 | 8.5918 | 8.3459 | 7.6776 | 7.1898 | 7.0112 | 10.5949 | 10.5633 | 10.5388 | 10.5041 | 10.3173 | 10.2459 | 10.0418 | 9.8327 | 9.6867 | 9.1837 | 8.8827 | 8.5847 | 8.1031 | 8.0939 | 8.0959 | 8.0449 | 7.9408 | 7.8357 | 7.6571 | 7.4673 | 7.3051 | 6.8929 | 6.6357 | 6.5684
|  | GORING PRIMARY | FB |  |  |  |  | 9.6378 | 9.6724 | 9.7061 | 9.7347 | 9.7306 | 9.7102 | 9.6612 | 9.5929 | 9.6224 | 9.1847 | 8.7622 | 8.3296 | 10.65 | 10.6469 | 10.6418 | 10.6367 | 10.599 | 10.5429 | 10.4714 | 10.3908 | 10.3878 | 9.8582 | 9.0827 | 7.9367 | 8.152 | 8.1704 | 8.1786 | 8.1827 | 8.1827 | 8.1582 | 8.1235 | 8.0837 | 8.0643 | 7.8 | 7.5245 | 7.3531
IVER 132KV GSP | DENHAM BSP | GRASSINGHAM ROAD PRIMARY | MINIMUM HEADROOM | TQ 00165 90988 | NO | YES | 1.126 | 2.1635 | 2.2339 | 2.2594 | 2.0441 | 1.7584 | 0.99617 | 0.14617 | -0.76403 | -1.6497 | -4.8977 | -7.6293 | -9.061 | 6.1431 | 6.1349 | 6.1554 | 6.0258 | 5.8513 | 5.539 | 5.1268 | 4.6737 | 4.2503 | 2.8972 | 2.1951 | 2.0982 | 3.7707 | 3.7982 | 3.8492 | 3.6584 | 3.3849 | 2.8288 | 2.2125 | 1.5666 | 0.90229 | -1.3773 | -3.163 | -4.0518
|  | GRASSINGHAM ROAD PRIMARY | EE |  |  |  |  | 2.1645 | 2.2349 | 2.2962 | 2.1594 | 1.986 | 1.3054 | 0.51045 | -0.38342 | -1.2549 | -4.2273 | -6.8049 | -8.2528 | 6.1462 | 6.14 | 6.1737 | 6.0778 | 5.9462 | 5.6778 | 5.3125 | 4.8982 | 4.5115 | 3.2339 | 2.5533 | 2.4196 | 3.7717 | 3.8023 | 3.8778 | 3.7217 | 3.5084 | 2.986 | 2.3911 | 1.7421 | 1.1196 | -0.98648 | -2.6875 | -3.5946
|  | GRASSINGHAM ROAD PRIMARY | HT |  |  |  |  | 2.1635 | 2.236 | 2.2594 | 2.0441 | 1.7584 | 0.99617 | 0.14617 | -0.76403 | -1.6497 | -4.8977 | -7.6293 | -9.061 | 6.1431 | 6.136 | 6.1554 | 6.0258 | 5.8513 | 5.539 | 5.1268 | 4.6737 | 4.2503 | 2.8972 | 2.1951 | 2.0982 | 3.7717 | 3.8013 | 3.8492 | 3.6584 | 3.3849 | 2.8288 | 2.2125 | 1.5666 | 0.91658 | -1.3773 | -3.163 | -4.0518
|  | GRASSINGHAM ROAD PRIMARY | HE |  |  |  |  | 2.1635 | 2.2339 | 2.2962 | 2.1145 | 1.889 | 1.1574 | 0.30127 | -0.64975 | -1.5875 | -4.1742 | -6.5926 | -7.6212 | 6.1431 | 6.1349 | 6.1696 | 6.0656 | 5.9278 | 5.6533 | 5.2788 | 4.8594 | 4.4666 | 3.2166 | 2.4788 | 2.2686 | 3.7707 | 3.7982 | 3.8543 | 3.69 | 3.4441 | 2.889 | 2.2554 | 1.5676 | 0.90229 | -0.95077 | -2.562 | -3.2212
|  | GRASSINGHAM ROAD PRIMARY | FB |  |  |  |  | 2.3564 | 2.4829 | 2.6074 | 2.6707 | 2.7482 | 2.6982 | 2.6125 | 2.4972 | 2.3758 | 1.3186 | -0.27832 | -0.9671 | 6.3278 | 6.3778 | 6.4145 | 6.4462 | 6.5237 | 6.4676 | 6.3778 | 6.2686 | 6.1329 | 5.1615 | 3.99 | 3.537 | 3.9666 | 4.0696 | 4.136 | 4.1339 | 4.1421 | 4.0717 | 3.9747 | 3.8564 | 3.7258 | 2.7482 | 1.4788 | 0.8829
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | GREEN PARK PRIMARY | MINIMUM HEADROOM | SU 70508 70222 | NO | NO | 23.461 | 8.8765 | 8.8745 | 8.4714 | 8.4653 | 8.4643 | 8.4643 | 8.4622 | 8.4592 | 8.4592 | 8.4602 | 8.4602 | 8.4592 | 8.3163 | 8.3163 | 7.8337 | 7.8286 | 7.8286 | 7.8276 | 7.8276 | 7.8255 | 7.8255 | 7.8204 | 7.8184 | 7.8163 | 9.2857 | 9.2857 | 8.8878 | 8.8827 | 8.8827 | 8.8857 | 8.8857 | 8.8847 | 8.8816 | 8.8776 | 8.8765 | 8.8755
|  | GREEN PARK PRIMARY | EE |  |  |  |  | 8.8765 | 8.8745 | 8.4714 | 8.4653 | 8.4643 | 8.4643 | 8.4633 | 8.4602 | 8.4602 | 8.4602 | 8.4602 | 8.4592 | 8.3173 | 8.3173 | 7.8347 | 7.8296 | 7.8296 | 7.8276 | 7.8276 | 7.8255 | 7.8255 | 7.8214 | 7.8204 | 7.8184 | 9.2857 | 9.2857 | 8.8878 | 8.8878 | 8.8857 | 8.8857 | 8.8857 | 8.8847 | 8.8827 | 8.8776 | 8.8765 | 8.8755
|  | GREEN PARK PRIMARY | HT |  |  |  |  | 8.8765 | 8.8765 | 8.4806 | 8.4755 | 8.4755 | 8.4745 | 8.4735 | 8.4714 | 8.4714 | 8.4643 | 8.4612 | 8.4602 | 8.3163 | 8.3163 | 7.8337 | 7.8286 | 7.8286 | 7.8276 | 7.8276 | 7.8265 | 7.8265 | 7.8204 | 7.8184 | 7.8163 | 9.2867 | 9.2878 | 8.8939 | 8.8878 | 8.8878 | 8.8867 | 8.8867 | 8.8857 | 8.8837 | 8.8796 | 8.8776 | 8.8755
|  | GREEN PARK PRIMARY | HE |  |  |  |  | 8.8765 | 8.8745 | 8.4714 | 8.4663 | 8.4663 | 8.4643 | 8.4622 | 8.4592 | 8.4592 | 8.4602 | 8.4622 | 8.4633 | 8.3173 | 8.3173 | 7.8347 | 7.8296 | 7.8296 | 7.8276 | 7.8276 | 7.8255 | 7.8255 | 7.8235 | 7.8224 | 7.8214 | 9.2857 | 9.2857 | 8.8878 | 8.8827 | 8.8827 | 8.8867 | 8.8857 | 8.8847 | 8.8816 | 8.8776 | 8.8796 | 8.8786
|  | GREEN PARK PRIMARY | FB |  |  |  |  | 8.8776 | 8.8776 | 8.4867 | 8.4827 | 8.4837 | 8.4837 | 8.4796 | 8.4796 | 8.4796 | 8.4765 | 8.4735 | 8.4714 | 8.3163 | 8.3163 | 7.8367 | 7.8327 | 7.8337 | 7.8327 | 7.8316 | 7.8306 | 7.8316 | 7.8276 | 7.8235 | 7.8224 | 9.2867 | 9.2878 | 8.898 | 8.8949 | 8.8949 | 8.8949 | 8.8939 | 8.8918 | 8.8918 | 8.8878 | 8.8867 | 8.8867
WILLESDEN GSP |  | GREENFORD PRIMARY | MINIMUM HEADROOM | TQ 14695 83785 | NO | YES | 31.16 | 11.5359 | 11.4737 | 11.0839 | 10.6492 | 9.7675 | 8.5798 | 7.192 | 6.3451 | 4.7431 | -1.459 | -5.81 | -8.0457 | 21.5012 | 21.4206 | 21.0818 | 20.7767 | 20.189 | 19.4767 | 18.5216 | 17.4971 | 16.1951 | 11.788 | 6.0349 | -2.7529 | 16.9971 | 16.9808 | 16.6788 | 16.3777 | 15.6104 | 14.6777 | 13.5441 | 12.6492 | 11.1186 | 5.69 | 1.9584 | -0.14164
|  | GREENFORD PRIMARY | EE |  |  |  |  | 11.5359 | 11.4737 | 11.0839 | 10.691 | 9.8777 | 8.7094 | 7.3196 | 6.3451 | 5.1471 | -0.53246 | -5.6039 | -8.0457 | 21.5012 | 21.4206 | 21.0839 | 20.7767 | 20.2002 | 19.4767 | 18.5461 | 17.6716 | 16.5696 | 11.788 | 7.6267 | 4.142 | 16.9971 | 16.9808 | 16.6788 | 16.3808 | 15.6655 | 14.7257 | 13.5747 | 12.6747 | 11.5451 | 6.4186 | 1.9584 | -0.14164
|  | GREENFORD PRIMARY | HT |  |  |  |  | 11.5675 | 11.588 | 11.2124 | 10.8084 | 9.9257 | 9.09 | 7.8084 | 6.4777 | 4.7431 | -1.459 | -5.81 | -7.3192 | 21.5043 | 21.4257 | 21.091 | 20.7869 | 20.19 | 19.5145 | 18.5216 | 17.4971 | 16.1951 | 12.4328 | 9.9788 | 9.192 | 17.0277 | 17.0604 | 16.7951 | 16.4686 | 15.6869 | 14.9492 | 13.8216 | 12.6492 | 11.1186 | 5.69 | 1.9604 | 0.83387
|  | GREENFORD PRIMARY | HE |  |  |  |  | 11.5604 | 11.5165 | 11.0941 | 10.6492 | 9.7675 | 8.5798 | 7.192 | 6.3502 | 5.239 | 1.2747 | -2.1631 | -3.7763 | 21.5033 | 21.4216 | 21.0818 | 20.7869 | 20.189 | 19.4839 | 18.5716 | 17.6757 | 16.5777 | 12.3992 | 8.742 | 5.6104 | 17.0247 | 17.0277 | 16.7206 | 16.3777 | 15.6104 | 14.6777 | 13.5441 | 12.7165 | 11.6461 | 8.0267 | 5.0247 | 3.7104
|  | GREENFORD PRIMARY | FB |  |  |  |  | 11.9145 | 12.038 | 12.0267 | 11.9206 | 11.7961 | 11.542 | 11.1267 | 10.8737 | 10.5022 | 7.4614 | 2.6237 | -0.80899 | 21.6492 | 21.5359 | 21.3808 | 21.1145 | 20.7584 | 20.2318 | 19.5767 | 19.0165 | 18.3696 | 13.5982 | 6.0349 | -2.7529 | 17.3757 | 17.4869 | 17.5288 | 17.4777 | 17.39 | 17.1482 | 16.7553 | 16.5155 | 16.1645 | 13.2451 | 8.7206 | 5.5165
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET PRIMARY | MINIMUM HEADROOM | SU 64445 00178 | NO | YES | 1.431 | 16.2939 | 16.3224 | 16.3347 | 16.3265 | 16.0827 | 15.7724 | 15.4071 | 15.0786 | 14.7571 | 13.3286 | 12.2408 | 11.5949 | 17.7429 | 17.6908 | 17.6286 | 17.5469 | 17.3816 | 17.1041 | 16.8582 | 16.5755 | 16.2857 | 14.502 | 11.5 | 7.1265 | 16.3367 | 16.3337 | 16.248 | 16.1694 | 15.9245 | 15.6561 | 15.3204 | 15.0327 | 14.752 | 13.4541 | 12.399 | 11.8418
|  | GREETHAM STREET PRIMARY | EE |  |  |  |  | 16.2939 | 16.3224 | 16.3408 | 16.3551 | 16.2602 | 15.9653 | 15.6347 | 15.3541 | 15.0327 | 13.4765 | 12.2408 | 11.5949 | 17.8061 | 17.7408 | 17.6663 | 17.601 | 17.4663 | 17.2612 | 17.0194 | 16.8173 | 16.5704 | 14.849 | 13.1847 | 11.2867 | 16.3398 | 16.3337 | 16.248 | 16.1867 | 16.0235 | 15.7755 | 15.4735 | 15.2367 | 14.9337 | 13.4745 | 12.399 | 11.8418
|  | GREETHAM STREET PRIMARY | HT |  |  |  |  | 16.299 | 16.3286 | 16.3347 | 16.3265 | 16.0827 | 15.7724 | 15.4071 | 15.0786 | 14.7571 | 13.3286 | 12.2714 | 11.8327 | 17.8112 | 17.7408 | 17.6582 | 17.5765 | 17.3816 | 17.1755 | 16.9265 | 16.6816 | 16.4551 | 15.5327 | 14.7908 | 14.2459 | 16.3469 | 16.349 | 16.2571 | 16.1694 | 15.9245 | 15.6561 | 15.3204 | 15.0327 | 14.752 | 13.4541 | 12.5745 | 12.2367
|  | GREETHAM STREET PRIMARY | HE |  |  |  |  | 16.299 | 16.3429 | 16.3684 | 16.3714 | 16.3112 | 16.102 | 15.8306 | 15.6255 | 15.4 | 14.2439 | 13.5143 | 13.1602 | 17.8041 | 17.752 | 17.6806 | 17.6184 | 17.5092 | 17.3357 | 17.1051 | 16.9255 | 16.7357 | 15.298 | 13.8653 | 12.1959 | 16.3367 | 16.3398 | 16.2714 | 16.2102 | 16.0898 | 15.8878 | 15.6122 | 15.4296 | 15.2102 | 14.2173 | 13.598 | 13.3592
|  | GREETHAM STREET PRIMARY | FB |  |  |  |  | 16.3153 | 16.3735 | 16.4265 | 16.4724 | 16.5163 | 16.45 | 16.3561 | 16.25 | 16.1337 | 15.3878 | 14.4663 | 13.5663 | 17.7429 | 17.6908 | 17.6286 | 17.5469 | 17.4153 | 17.1041 | 16.8582 | 16.5755 | 16.2857 | 14.502 | 11.5 | 7.1265 | 16.3663 | 16.4041 | 16.4357 | 16.4439 | 16.4439 | 16.3776 | 16.3082 | 16.1867 | 16.0378 | 15.2653 | 14.3551 | 13.4765
COWLEY GSP | DRAYTON BSP | GROVE PRIMARY | MINIMUM HEADROOM | SU 39515 89611 | NO | YES | 8.891 | -8.4622 | 7.6179 | 6.8812 | 6.0435 | 5.1618 | 3.6935 | 2.2618 | 0.70366 | -0.55349 | -5.4392 | -9.1484 | -11.0535 | -5.1098 | 10.0853 | 9.6771 | 9.1955 | 8.7047 | 7.971 | 7.2302 | 6.2873 | 5.6047 | 2.6271 | 1.0975 | -0.42185 | -7.2713 | 8.3884 | 7.8588 | 7.2128 | 6.52 | 5.421 | 4.3567 | 3.0894 | 2.1332 | -2.0851 | -4.6923 | -5.8606
|  | GROVE PRIMARY | EE |  |  |  |  | -8.4622 | 7.6179 | 6.8894 | 6.0781 | 5.1843 | 3.8006 | 2.3935 | 0.86794 | -0.34124 | -4.9229 | -7.9749 | -9.5127 | -5.0873 | 10.1292 | 9.7445 | 9.3271 | 8.871 | 8.1914 | 7.4863 | 6.5945 | 5.9771 | 2.8894 | 1.0975 | -0.094302 | -7.2499 | 8.3935 | 7.8618 | 7.2322 | 6.5435 | 5.4914 | 4.4261 | 3.17 | 2.2394 | -1.5688 | -3.8474 | -4.9555
|  | GROVE PRIMARY | HT |  |  |  |  | -8.4469 | 7.6639 | 6.9884 | 6.2047 | 5.3353 | 3.9965 | 2.6363 | 1.121 | -0.10553 | -5.4392 | -9.1484 | -11.0535 | -5.1098 | 10.0853 | 9.6771 | 9.1955 | 8.7047 | 7.971 | 7.2302 | 6.2873 | 5.6047 | 2.6271 | 1.1149 | 0.59447 | -7.2713 | 8.3884 | 7.873 | 7.2363 | 6.52 | 5.4598 | 4.4077 | 3.1292 | 2.1649 | -2.0851 | -4.6923 | -5.8606
|  | GROVE PRIMARY | HE |  |  |  |  | -8.4622 | 7.62 | 6.8812 | 6.0435 | 5.1618 | 3.6935 | 2.2618 | 0.70366 | -0.55349 | -4.2402 | -6.879 | -8.0321 | -5.0883 | 10.1261 | 9.7435 | 9.321 | 8.8822 | 8.1618 | 7.4781 | 6.5935 | 5.9751 | 3.4649 | 1.9353 | 0.80468 | -7.2509 | 8.3924 | 7.8588 | 7.2128 | 6.5322 | 5.421 | 4.3567 | 3.0894 | 2.1332 | -0.90349 | -2.8208 | -3.6555
|  | GROVE PRIMARY | FB |  |  |  |  | -8.2337 | 8.2139 | 7.569 | 7.1679 | 6.7639 | 6.1894 | 5.57 | 4.9292 | 4.3741 | 1.2353 | -1.4116 | -2.8341 | -4.9485 | 10.5302 | 9.97 | 9.7026 | 9.4761 | 9.1332 | 8.722 | 8.2812 | 7.8618 | 5.2179 | 2.4037 | -0.42185 | -7.0428 | 9.0088 | 8.371 | 8.0414 | 7.7526 | 7.323 | 6.8424 | 6.3332 | 5.8751 | 3.1577 | 0.84447 | -0.60961
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL PRIMARY | MINIMUM HEADROOM | ST 98638 11417 | YES | NO | 0.045 | 4.6138 | 4.6026 | 4.5791 | 4.5505 | 4.5056 | 4.4668 | 4.3964 | 4.3413 | 4.273 | 4.126 | 3.9883 | 3.8995 | 4.151 | 4.1398 | 4.1214 | 4.1112 | 4.0806 | 4.0551 | 4.0092 | 3.9786 | 3.9357 | 3.8531 | 3.8235 | 3.6929 | 4.5214 | 4.5133 | 4.4959 | 4.4745 | 4.4388 | 4.4 | 4.3439 | 4.3194 | 4.2643 | 4.1541 | 4.0745 | 4.0398
|  | GUSSAGE ST MICHAEL PRIMARY | EE |  |  |  |  | 4.6158 | 4.6077 | 4.5862 | 4.5648 | 4.5352 | 4.5077 | 4.4485 | 4.4066 | 4.3485 | 4.2179 | 4.1138 | 4.0556 | 4.151 | 4.1418 | 4.1255 | 4.1133 | 4.0929 | 4.0724 | 4.0316 | 4.0082 | 3.9704 | 3.8847 | 3.8337 | 3.8 | 4.5214 | 4.5143 | 4.502 | 4.4816 | 4.4541 | 4.4255 | 4.3694 | 4.3367 | 4.2949 | 4.1898 | 4.1408 | 4.1378
|  | GUSSAGE ST MICHAEL PRIMARY | HT |  |  |  |  | 4.6138 | 4.6026 | 4.5791 | 4.5505 | 4.5056 | 4.4668 | 4.3964 | 4.3413 | 4.273 | 4.126 | 3.9883 | 3.8995 | 4.152 | 4.1398 | 4.1214 | 4.1112 | 4.0806 | 4.0551 | 4.0092 | 3.9786 | 3.9357 | 3.8531 | 3.8235 | 3.8337 | 4.5214 | 4.5133 | 4.4959 | 4.4745 | 4.4388 | 4.4 | 4.3439 | 4.3194 | 4.2643 | 4.1541 | 4.0745 | 4.0398
|  | GUSSAGE ST MICHAEL PRIMARY | HE |  |  |  |  | 4.6158 | 4.6087 | 4.5883 | 4.5628 | 4.5352 | 4.5005 | 4.4362 | 4.3872 | 4.327 | 4.2332 | 4.1087 | 4.0372 | 4.151 | 4.1429 | 4.1265 | 4.1133 | 4.0918 | 4.0714 | 4.0327 | 4.0061 | 3.9684 | 3.8847 | 3.8235 | 3.7643 | 4.5214 | 4.5153 | 4.5031 | 4.4806 | 4.4541 | 4.4204 | 4.3673 | 4.3418 | 4.2888 | 4.1949 | 4.1357 | 4.1122
|  | GUSSAGE ST MICHAEL PRIMARY | FB |  |  |  |  | 4.6454 | 4.6495 | 4.6474 | 4.6423 | 4.6352 | 4.625 | 4.6117 | 4.5893 | 4.5781 | 4.476 | 4.374 | 4.3219 | 4.1755 | 4.1714 | 4.1633 | 4.1582 | 4.148 | 4.1367 | 4.1235 | 4.099 | 4.0857 | 3.9663 | 3.8327 | 3.6929 | 4.5388 | 4.5408 | 4.5388 | 4.5337 | 4.5265 | 4.5173 | 4.5071 | 4.4918 | 4.4816 | 4.3684 | 4.2735 | 4.2561
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE PRIMARY | MINIMUM HEADROOM | SU 47370 08794 | NO | NO | 0.97 | 11.1836 | 11.1917 | 11.1784 | 11.0315 | 10.8325 | 10.2887 | 9.6958 | 9.0509 | 8.357 | 5.7836 | 3.7907 | 2.608 | 13.2468 | 13.2029 | 13.1193 | 12.8417 | 12.5887 | 12.256 | 11.9193 | 11.5458 | 11.1254 | 9.6652 | 9.0448 | 6.8774 | 12.5468 | 12.5438 | 12.4815 | 12.2162 | 11.9489 | 11.5029 | 11.0346 | 10.5295 | 9.9672 | 7.9978 | 6.6519 | 5.9836
|  | HAMBLE PRIMARY | EE |  |  |  |  | 11.1856 | 11.1948 | 11.1784 | 11.0397 | 10.8652 | 10.3336 | 9.7825 | 9.1489 | 8.4917 | 6.0805 | 4.1733 | 3.0672 | 13.2478 | 13.206 | 13.1223 | 12.858 | 12.656 | 12.3254 | 12.0376 | 11.6621 | 11.257 | 9.7672 | 9.058 | 8.2029 | 12.5499 | 12.5458 | 12.4815 | 12.2325 | 12.0162 | 11.5601 | 11.1397 | 10.6274 | 10.104 | 8.1856 | 6.805 | 6.0887
|  | HAMBLE PRIMARY | HT |  |  |  |  | 11.1836 | 11.1968 | 11.1836 | 11.0315 | 10.8325 | 10.2887 | 9.6958 | 9.0509 | 8.357 | 5.7836 | 3.7907 | 2.608 | 13.2478 | 13.204 | 13.1193 | 12.8417 | 12.5887 | 12.256 | 11.9193 | 11.5458 | 11.1254 | 9.6652 | 9.0448 | 8.9621 | 12.5468 | 12.5478 | 12.4866 | 12.2162 | 11.9489 | 11.5029 | 11.0346 | 10.5295 | 9.9672 | 7.9978 | 6.6519 | 5.9836
|  | HAMBLE PRIMARY | HE |  |  |  |  | 11.1846 | 11.1917 | 11.2325 | 11.0478 | 10.8448 | 10.307 | 9.7489 | 9.0989 | 8.4499 | 6.4591 | 4.8305 | 3.9856 | 13.2468 | 13.2029 | 13.2019 | 12.9193 | 12.6468 | 12.3101 | 12.0193 | 11.6346 | 11.2499 | 9.906 | 9.3407 | 8.5376 | 12.5478 | 12.5438 | 12.4989 | 12.2856 | 11.9989 | 11.5387 | 11.1142 | 10.5917 | 10.0887 | 8.4897 | 7.3836 | 6.8223
|  | HAMBLE PRIMARY | FB |  |  |  |  | 11.3244 | 11.3805 | 11.4193 | 11.4478 | 11.4448 | 11.4458 | 11.3805 | 11.2305 | 11.1274 | 9.9478 | 8.4744 | 7.5621 | 13.3621 | 13.3591 | 13.3397 | 13.3009 | 13.2397 | 13.2254 | 13.1274 | 12.7815 | 12.6315 | 11.407 | 9.3376 | 6.8774 | 12.6478 | 12.6744 | 12.6927 | 12.6703 | 12.6305 | 12.605 | 12.5274 | 12.357 | 12.2223 | 11.0009 | 9.6519 | 8.7907
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | HAMWORTHY PRIMARY | MINIMUM HEADROOM | SZ 00104 90800 | NO | NO | 4.051 | 6.5574 | 6.4605 | 39.8901 | 39.1972 | 38.1115 | 36.6319 | 35.0972 | 33.1003 | 31.0891 | 25.7942 | 22.8717 | 21.535 | 9.8166 | 9.6625 | 39.8207 | 39.4523 | 38.9738 | 38.3952 | 37.6472 | 36.4717 | 35.2493 | 31.6983 | 29.1656 | 24.6901 | 7.6105 | 7.5013 | 39.3268 | 38.8197 | 38.0676 | 36.9268 | 35.7003 | 34.1085 | 32.4911 | 27.9585 | 25.5972 | 24.7044
|  | HAMWORTHY PRIMARY | EE |  |  |  |  | 6.5758 | 6.5217 | 39.9799 | 39.388 | 38.3768 | 37.0727 | 35.6472 | 33.7401 | 31.8095 | 27.1085 | 24.3105 | 22.6901 | 9.8248 | 9.6921 | 39.8778 | 39.5585 | 39.1278 | 38.6421 | 38.0462 | 36.9605 | 35.8074 | 31.6983 | 29.1656 | 27.1003 | 7.6207 | 7.5472 | 39.386 | 38.9493 | 38.2534 | 37.2942 | 36.134 | 34.6238 | 33.0758 | 28.8687 | 26.4442 | 25.1176
|  | HAMWORTHY PRIMARY | HT |  |  |  |  | 6.5574 | 6.4605 | 39.8901 | 39.1972 | 38.1115 | 36.6319 | 35.0972 | 33.1003 | 31.0891 | 25.7942 | 22.8717 | 21.535 | 9.8166 | 9.6625 | 39.8207 | 39.4523 | 38.9738 | 38.3952 | 37.6472 | 36.4717 | 35.2493 | 31.7115 | 30.0493 | 29.4727 | 7.6105 | 7.5013 | 39.3268 | 38.8197 | 38.0676 | 36.9268 | 35.7003 | 34.1085 | 32.4911 | 27.9585 | 25.5972 | 24.7044
|  | HAMWORTHY PRIMARY | HE |  |  |  |  | 6.5829 | 6.5309 | 39.9901 | 39.4125 | 38.4136 | 37.1187 | 35.7146 | 33.837 | 31.9452 | 28.2962 | 26.136 | 24.9003 | 9.8248 | 9.6921 | 39.8758 | 39.5574 | 39.1258 | 38.638 | 38.0421 | 36.9789 | 35.8625 | 32.5421 | 30.3432 | 28.3136 | 7.6258 | 7.5564 | 39.3932 | 38.9625 | 38.2697 | 37.3054 | 36.1666 | 34.686 | 33.1799 | 29.9666 | 28.1534 | 27.1472
|  | HAMWORTHY PRIMARY | FB |  |  |  |  | 6.8238 | 6.9044 | 40.7105 | 40.4727 | 39.987 | 39.4472 | 38.8697 | 37.9534 | 36.9625 | 34.0095 | 31.1962 | 29.0309 | 9.9391 | 9.9156 | 40.2748 | 40.1503 | 39.9136 | 39.6891 | 39.2095 | 38.5676 | 37.8452 | 34.4125 | 29.9166 | 24.6901 | 7.8585 | 7.9136 | 40.035 | 39.8738 | 39.5299 | 39.1585 | 38.7452 | 38.135 | 37.4227 | 34.6819 | 31.9585 | 29.788
IVER 132KV GSP | DENHAM BSP | HAREFIELD PRIMARY | MINIMUM HEADROOM | TQ 04001 91227 | NO | YES | 0.651 | 8.9278 | 8.9084 | 8.8676 | 8.5727 | 8.3308 | 7.988 | 7.5717 | 7.191 | 6.8074 | 5.2125 | 4.2308 | 3.6319 | 9.7645 | 9.741 | 9.7053 | 9.5012 | 9.341 | 9.1329 | 8.8523 | 8.6074 | 8.3614 | 7.3196 | 6.8563 | 6.4206 | 9.6819 | 9.6696 | 9.6319 | 9.4053 | 9.2043 | 8.9421 | 8.5992 | 8.2849 | 7.9666 | 6.6808 | 5.9808 | 5.5982
|  | HAREFIELD PRIMARY | EE |  |  |  |  | 8.9278 | 8.9268 | 8.9043 | 8.6625 | 8.44 | 8.187 | 7.8268 | 7.4339 | 7.0788 | 5.5278 | 4.5543 | 3.9747 | 9.7645 | 9.7523 | 9.7298 | 9.5461 | 9.3574 | 9.241 | 8.9808 | 8.6931 | 8.4482 | 7.4114 | 6.8563 | 6.4206 | 9.6829 | 9.6757 | 9.6543 | 9.4819 | 9.2237 | 9.0614 | 8.7594 | 8.4257 | 8.1319 | 6.9431 | 6.2166 | 5.8145
|  | HAREFIELD PRIMARY | HT |  |  |  |  | 8.9288 | 8.9084 | 8.8676 | 8.5727 | 8.3308 | 7.988 | 7.5717 | 7.191 | 6.8074 | 5.2125 | 4.2308 | 3.6319 | 9.7645 | 9.741 | 9.7053 | 9.5012 | 9.341 | 9.1329 | 8.8523 | 8.6074 | 8.3614 | 7.3196 | 6.9859 | 6.8186 | 9.6819 | 9.6696 | 9.6319 | 9.4053 | 9.2043 | 8.9421 | 8.5992 | 8.2849 | 7.9666 | 6.6808 | 5.9808 | 5.5982
|  | HAREFIELD PRIMARY | HE |  |  |  |  | 8.9288 | 8.9257 | 8.9043 | 8.6604 | 8.437 | 8.2145 | 7.8063 | 7.4176 | 7.0676 | 5.9584 | 5.1196 | 4.6992 | 9.7645 | 9.7502 | 9.7278 | 9.5451 | 9.3645 | 9.2717 | 8.9676 | 8.69 | 8.4451 | 7.6359 | 7.191 | 6.787 | 9.6819 | 9.6768 | 9.6553 | 9.4788 | 9.2298 | 9.091 | 8.7431 | 8.4155 | 8.1217 | 7.2125 | 6.6635 | 6.3645
|  | HAREFIELD PRIMARY | FB |  |  |  |  | 9.0125 | 9.0512 | 9.0717 | 9.0604 | 9.0696 | 9.039 | 8.9798 | 8.7023 | 8.6308 | 8.0319 | 7.2237 | 6.6217 | 9.8227 | 9.8319 | 9.8257 | 9.8002 | 9.7778 | 9.7257 | 9.641 | 9.3859 | 9.2972 | 8.5839 | 7.5604 | 6.4492 | 9.7308 | 9.7482 | 9.7594 | 9.7451 | 9.7319 | 9.7176 | 9.6961 | 9.4461 | 9.3533 | 8.7217 | 8.0186 | 7.5686
NURSLING GSP | WINCHESTER BSP | HARESTOCK PRIMARY | MINIMUM HEADROOM | SU 45908 31300 | NO | NO | 6.15 | 9.9892 | 10.0586 | 9.9514 | 9.6688 | 9.2841 | 8.5372 | 7.2943 | 5.4504 | 1.7443 | -3.2812 | -8.7424 | -13.072 | 13.7555 | 13.9208 | 13.678 | 13.4749 | 13.1565 | 12.7249 | 11.6106 | 9.8086 | 5.8627 | 1.6208 | -2.9496 | -8.3557 | 11.5555 | 11.73 | 11.5688 | 11.3014 | 10.9106 | 10.2198 | 8.8525 | 6.7923 | 2.6219 | -2.0843 | -7.0526 | -12.1281
|  | HARESTOCK PRIMARY | EE |  |  |  |  | 9.9892 | 10.0586 | 9.9545 | 9.7208 | 9.4178 | 8.6974 | 7.7708 | 6.679 | 5.0382 | 0.033078 | -6.5475 | -9.3792 | 13.7586 | 13.9229 | 13.6943 | 13.5392 | 13.3106 | 12.9474 | 12.279 | 11.2963 | 9.9331 | 6.2453 | 0.18614 | -2.423 | 11.5555 | 11.73 | 11.577 | 11.3708 | 11.0851 | 10.4372 | 9.5025 | 8.2933 | 6.7076 | 2.3361 | -4.32 | -6.8588
|  | HARESTOCK PRIMARY | HT |  |  |  |  | 9.9923 | 10.0657 | 9.9514 | 9.6688 | 9.2841 | 8.5372 | 7.2943 | 5.8637 | 3.4423 | -2.2802 | -8.7424 | -12.8577 | 13.7555 | 13.9219 | 13.678 | 13.4749 | 13.1565 | 12.7249 | 11.6106 | 10.3657 | 8.0708 | 4.1698 | -1.0455 | -4.4567 | 11.5555 | 11.7321 | 11.5688 | 11.3014 | 10.9106 | 10.2198 | 8.8525 | 7.3647 | 4.8331 | -0.22713 | -6.5761 | -10.6281
|  | HARESTOCK PRIMARY | HE |  |  |  |  | 9.9933 | 10.0637 | 9.9637 | 9.6933 | 9.3565 | 8.6514 | 7.479 | 5.4504 | 1.7443 | -3.2812 | -8.4108 | -13.072 | 13.7565 | 13.9208 | 13.6902 | 13.529 | 13.2933 | 12.9331 | 11.9341 | 9.8086 | 5.8627 | 1.6208 | -2.9496 | -8.3557 | 11.5576 | 11.7321 | 11.5872 | 11.3504 | 11.0382 | 10.4004 | 9.1474 | 6.7923 | 2.6219 | -2.0843 | -7.0526 | -12.1281
|  | HARESTOCK PRIMARY | FB |  |  |  |  | 10.1627 | 10.2647 | 10.3433 | 10.3708 | 10.329 | 10.2351 | 9.9729 | 9.6708 | 9.1321 | 6.8637 | 3.5392 | 0.84634 | 13.9474 | 14.0616 | 14.1259 | 14.2433 | 14.2208 | 14.0719 | 13.5402 | 13.0678 | 12.3443 | 9.0698 | 4.3974 | -0.38121 | 11.83 | 12.0096 | 12.1474 | 12.3229 | 12.3688 | 12.3096 | 11.8851 | 11.4902 | 10.8423 | 8.0116 | 4.2504 | 1.3841
EALING GSP | EALING BSP | HARVARD LANE PRIMARY | MINIMUM HEADROOM | TQ 20021 78030 | NO | NO | 3.383 | 2.7617 | 2.7485 | 53.7587 | 53.6393 | 53.4281 | 53.0444 | 52.5026 | 52.0454 | 51.5648 | 49.6005 | 47.0821 | 45.7209 | 5.673 | 5.5362 | 56.4964 | 56.276 | 55.9148 | 55.473 | 54.8699 | 54.3383 | 53.7842 | 51.4281 | 47.6066 | 41.5546 | 4.2546 | 4.2168 | 55.2005 | 55.0566 | 54.8117 | 54.4138 | 53.8515 | 53.373 | 52.873 | 50.7546 | 48.3209 | 47.0046
|  | HARVARD LANE PRIMARY | EE |  |  |  |  | 2.7617 | 2.7485 | 53.7587 | 53.6393 | 53.4791 | 53.1811 | 52.7138 | 52.3526 | 51.975 | 49.6005 | 47.0821 | 45.7209 | 5.675 | 5.5638 | 56.5005 | 56.2852 | 56.0148 | 55.6413 | 55.0821 | 54.6117 | 54.1189 | 51.4281 | 48.7668 | 46.1954 | 4.2546 | 4.2168 | 55.2005 | 55.0566 | 54.8597 | 54.5393 | 54.0301 | 53.624 | 53.2005 | 50.7546 | 48.3209 | 47.0046
|  | HARVARD LANE PRIMARY | HT |  |  |  |  | 2.7832 | 2.7648 | 53.8301 | 53.7005 | 53.4281 | 53.0444 | 52.5026 | 52.0454 | 51.5648 | 49.8505 | 48.1689 | 47.6454 | 5.674 | 5.5362 | 56.4964 | 56.276 | 55.9148 | 55.473 | 54.8699 | 54.3383 | 53.7842 | 52.1189 | 50.6423 | 49.9179 | 4.276 | 4.2352 | 55.274 | 55.1168 | 54.8117 | 54.4138 | 53.8515 | 53.373 | 52.873 | 51.0464 | 49.3791 | 48.8995
|  | HARVARD LANE PRIMARY | HE |  |  |  |  | 2.7679 | 2.7628 | 53.7883 | 53.6587 | 53.4872 | 53.1893 | 52.7556 | 52.3974 | 52.0321 | 50.5393 | 48.9403 | 47.9709 | 5.673 | 5.5628 | 56.5015 | 56.2852 | 56.0138 | 55.6219 | 55.0781 | 54.5944 | 54.0985 | 51.6934 | 49.4158 | 47.0556 | 4.2597 | 4.2301 | 55.2291 | 55.075 | 54.8658 | 54.5383 | 54.0597 | 53.6577 | 53.2464 | 51.6117 | 50.0628 | 49.177
|  | HARVARD LANE PRIMARY | FB |  |  |  |  | 3.024 | 3.1097 | 54.1474 | 54.1209 | 54.1342 | 54.1413 | 54.0444 | 53.9393 | 53.8617 | 52.9923 | 50.8597 | 48.9597 | 5.7913 | 5.6893 | 56.5413 | 56.3617 | 56.1454 | 55.8883 | 55.5209 | 55.1117 | 54.7352 | 52.0801 | 47.6066 | 41.5546 | 4.5168 | 4.5781 | 55.5934 | 55.5536 | 55.5321 | 55.5179 | 55.4046 | 55.2556 | 55.1413 | 54.0872 | 51.9995 | 50.1781
COWLEY GSP |  | HARWELL PRIMARY | MINIMUM HEADROOM | SU 47395 86969 | NO | NO | 6.678 | 25.9665 | 25.9573 | 25.9492 | 25.9288 | 25.9063 | 25.8553 | 25.8237 | 25.7543 | 25.6767 | 25.092 | 24.9655 | 24.888 | 27.539 | 27.5349 | 27.5298 | 27.5196 | 27.5084 | 27.489 | 27.4696 | 27.3982 | 27.3716 | 26.7757 | 26.7043 | 26.6339 | 26.2676 | 26.2594 | 26.2502 | 26.2318 | 26.2104 | 26.1696 | 26.1298 | 26.04 | 25.9961 | 25.4624 | 25.3696 | 25.3237
|  | HARWELL PRIMARY | EE |  |  |  |  | 25.9676 | 25.9594 | 25.9492 | 25.9308 | 25.9084 | 25.8563 | 25.8267 | 25.7706 | 25.6767 | 25.092 | 24.9655 | 24.891 | 27.539 | 27.5349 | 27.5298 | 27.5206 | 27.5084 | 27.489 | 27.4716 | 27.441 | 27.3716 | 26.7757 | 26.7043 | 26.6339 | 26.2686 | 26.2594 | 26.2502 | 26.2339 | 26.2124 | 26.1716 | 26.1308 | 26.0829 | 25.9961 | 25.4624 | 25.3696 | 25.3237
|  | HARWELL PRIMARY | HT |  |  |  |  | 25.9686 | 25.9614 | 25.9553 | 25.938 | 25.9176 | 25.8757 | 25.8308 | 25.7543 | 25.7114 | 25.1114 | 24.9706 | 24.888 | 27.539 | 27.5349 | 27.5308 | 27.5196 | 27.5094 | 27.491 | 27.4696 | 27.3982 | 27.3747 | 26.7941 | 26.7522 | 26.7257 | 26.2676 | 26.2604 | 26.2533 | 26.238 | 26.2196 | 26.1818 | 26.1461 | 26.04 | 26.0012 | 25.4696 | 25.3737 | 25.3247
|  | HARWELL PRIMARY | HE |  |  |  |  | 25.9665 | 25.9573 | 25.9502 | 25.9288 | 25.9063 | 25.8553 | 25.8237 | 25.7727 | 25.7288 | 25.2124 | 25.1237 | 25.088 | 27.539 | 27.5349 | 27.5308 | 27.5196 | 27.5084 | 27.49 | 27.4706 | 27.4461 | 27.4257 | 26.8706 | 26.8247 | 26.7747 | 26.2676 | 26.2594 | 26.2502 | 26.2318 | 26.2104 | 26.1696 | 26.1298 | 26.0829 | 26.0624 | 25.5951 | 25.5257 | 25.4941
|  | HARWELL PRIMARY | FB |  |  |  |  | 25.9788 | 25.9767 | 25.9706 | 25.9686 | 25.9604 | 25.9461 | 25.938 | 25.9257 | 25.9104 | 25.839 | 25.3788 | 25.3543 | 27.5471 | 27.5461 | 27.541 | 27.54 | 27.5339 | 27.5227 | 27.5124 | 27.5022 | 27.4829 | 27.4002 | 26.8022 | 26.6716 | 26.2808 | 26.2747 | 26.2696 | 26.2665 | 26.2584 | 26.2451 | 26.2359 | 26.2257 | 26.2094 | 26.139 | 25.7012 | 25.6716
FLEET-BRAMLEY GSP | FERNHURST BSP | HASLEMERE PRIMARY | MINIMUM HEADROOM | SU 89300 31710 | NO | NO | 3.609 | 9.6898 | 9.8735 | 9.6286 | 9.3071 | 8.8837 | 8.1633 | 7.2704 | 6.3276 | 5.3806 | 2.7235 | 0.7949 | 0.0091837 | 14.6051 | 14.6765 | 14.2745 | 13.9092 | 13.4602 | 12.8857 | 12.1398 | 11.3776 | 10.601 | 8.2929 | 7.0398 | 3.3653 | 11.8724 | 12.0255 | 11.6816 | 11.3622 | 10.9367 | 10.3041 | 9.499 | 8.6602 | 7.8214 | 5.3949 | 3.8592 | 3.4735
|  | HASLEMERE PRIMARY | EE |  |  |  |  | 9.701 | 9.95 | 9.8306 | 9.698 | 9.4847 | 8.9214 | 8.2929 | 7.5878 | 6.8765 | 4.3847 | 2.4214 | 1.7939 | 14.6082 | 14.7143 | 14.3684 | 14.0898 | 13.7388 | 13.2224 | 12.6398 | 12 | 11.3459 | 8.8582 | 7.1929 | 6.1653 | 11.8796 | 12.0796 | 11.8276 | 11.6398 | 11.3633 | 10.8357 | 10.248 | 9.5816 | 8.9102 | 6.552 | 4.899 | 4.5786
|  | HASLEMERE PRIMARY | HT |  |  |  |  | 9.6898 | 9.8735 | 9.6286 | 9.3071 | 8.8837 | 8.1633 | 7.2704 | 6.3276 | 5.3806 | 2.7235 | 0.7949 | 0.0091837 | 14.6051 | 14.6765 | 14.2745 | 13.9092 | 13.4602 | 12.8857 | 12.1398 | 11.3776 | 10.601 | 8.2929 | 7.1245 | 7.0224 | 11.8724 | 12.0255 | 11.6816 | 11.3622 | 10.9367 | 10.3041 | 9.499 | 8.6602 | 7.8214 | 5.3949 | 3.8592 | 3.4735
|  | HASLEMERE PRIMARY | HE |  |  |  |  | 9.7031 | 9.952 | 9.8337 | 9.6735 | 9.4357 | 8.9071 | 8.2082 | 7.5061 | 6.7888 | 4.7847 | 3.0429 | 2.3408 | 14.6082 | 14.7143 | 14.3694 | 14.0857 | 13.7265 | 13.2704 | 12.6214 | 11.999 | 11.3612 | 9.1357 | 7.6418 | 6.3704 | 11.8816 | 12.0796 | 11.8296 | 11.6245 | 11.3316 | 10.8551 | 10.1939 | 9.5439 | 8.8806 | 6.9306 | 5.5327 | 5.0592
|  | HASLEMERE PRIMARY | FB |  |  |  |  | 9.9582 | 10.2122 | 10.4847 | 10.6214 | 10.7082 | 10.5235 | 10.4235 | 10.2469 | 10.0969 | 8.5031 | 6.3153 | 5.2224 | 14.7439 | 14.7949 | 14.8694 | 14.8316 | 14.7235 | 14.3816 | 14.0827 | 13.6918 | 13.35 | 10.6684 | 7.0398 | 3.3653 | 12.1235 | 12.301 | 12.4949 | 12.5898 | 12.6316 | 12.4173 | 12.2765 | 12.0306 | 11.8439 | 10.1184 | 7.9898 | 6.9367
FLEET-BRAMLEY GSP | FERNHURST BSP | HASLINGBOURNE PRIMARY | MINIMUM HEADROOM | SU 98188 20276 | NO | NO | 0.965 | 16.1698 | 16.1973 | 16.1178 | 15.8912 | 15.6963 | 15.3147 | 14.9269 | 14.4443 | 13.9841 | 12.6943 | 11.579 | 10.9453 | 17.4865 | 17.4682 | 17.2284 | 17.0753 | 16.9376 | 16.6824 | 16.3814 | 16.0284 | 15.6396 | 14.6467 | 13.911 | 12.9018 | 16.7014 | 16.7208 | 16.5688 | 16.4402 | 16.3127 | 16.0055 | 15.6484 | 15.2443 | 14.7933 | 13.5953 | 12.629 | 12.3606
|  | HASLINGBOURNE PRIMARY | EE |  |  |  |  | 16.1729 | 16.2147 | 16.1269 | 15.9065 | 15.7535 | 15.3555 | 14.9545 | 14.479 | 14.028 | 12.6943 | 11.7994 | 11.3351 | 17.4876 | 17.4794 | 17.2569 | 17.1314 | 17.0631 | 16.7906 | 16.5151 | 16.1814 | 15.8753 | 14.7508 | 13.911 | 13.5222 | 16.7024 | 16.729 | 16.6004 | 16.5157 | 16.4382 | 16.1208 | 15.7922 | 15.3963 | 15.0127 | 13.7973 | 12.8555 | 12.5851
|  | HASLINGBOURNE PRIMARY | HT |  |  |  |  | 16.1698 | 16.1973 | 16.1178 | 15.8912 | 15.6963 | 15.3576 | 14.9565 | 14.5116 | 14.031 | 12.7024 | 11.579 | 10.9453 | 17.4865 | 17.4682 | 17.2284 | 17.0753 | 16.9376 | 16.6824 | 16.3814 | 16.0284 | 15.6396 | 14.6467 | 14.0059 | 13.9886 | 16.7014 | 16.7208 | 16.5688 | 16.4402 | 16.3127 | 16.0055 | 15.6484 | 15.2443 | 14.7933 | 13.5953 | 12.629 | 12.3606
|  | HASLINGBOURNE PRIMARY | HE |  |  |  |  | 16.1729 | 16.2147 | 16.129 | 15.8943 | 15.7076 | 15.3147 | 14.9269 | 14.4443 | 13.9841 | 12.8473 | 12.1004 | 11.8514 | 17.4876 | 17.4794 | 17.259 | 17.1294 | 17.0386 | 16.7784 | 16.5304 | 16.209 | 15.8865 | 14.8437 | 14.1478 | 13.8243 | 16.7035 | 16.728 | 16.6024 | 16.5045 | 16.4065 | 16.0841 | 15.7749 | 15.3718 | 14.979 | 13.9678 | 13.18 | 13.028
|  | HASLINGBOURNE PRIMARY | FB |  |  |  |  | 16.2535 | 16.3116 | 16.3596 | 16.3871 | 16.4055 | 16.3769 | 16.2331 | 16.128 | 15.9596 | 14.9371 | 13.8871 | 13.2973 | 17.5784 | 17.5824 | 17.5804 | 17.5702 | 17.5324 | 17.4427 | 17.2192 | 17.1008 | 16.9161 | 15.8161 | 14.3712 | 12.9018 | 16.781 | 16.8178 | 16.8422 | 16.8565 | 16.8422 | 16.8004 | 16.7259 | 16.6606 | 16.5729 | 15.8106 | 14.7963 | 14.1249
MELKSHAM GSP | FROME BSP | HAWKERIDGE PRIMARY | MINIMUM HEADROOM | ST 86422 53026 | NO | NO | 0.1 | 2.2888 | 2.2265 | 2.1653 | 2.1245 | 2.049 | 1.9571 | 1.851 | 1.752 | 1.6367 | 1.0888 | 0.44286 | 0.23265 | 3.549 | 3.4622 | 3.3888 | 3.3469 | 3.2571 | 3.1673 | 3.052 | 2.9592 | 2.8684 | 1.7643 | 0.87041 | 0.73469 | 3.5786 | 3.4908 | 3.4184 | 3.3745 | 3.2816 | 3.1786 | 3.048 | 2.9388 | 2.8357 | 1.9286 | 0.95612 | 0.78673
|  | HAWKERIDGE PRIMARY | EE |  |  |  |  | 2.2908 | 2.2265 | 2.1663 | 2.1245 | 2.0531 | 1.9582 | 1.851 | 1.752 | 1.6367 | 1.0888 | 0.44286 | 0.28265 | 3.55 | 3.4622 | 3.3898 | 3.348 | 3.2643 | 3.1704 | 3.0571 | 2.9592 | 2.8694 | 1.7643 | 0.87041 | 0.77755 | 3.5806 | 3.4908 | 3.4214 | 3.3765 | 3.2878 | 3.1806 | 3.052 | 2.9388 | 2.8357 | 1.9286 | 0.95612 | 0.81327
|  | HAWKERIDGE PRIMARY | HT |  |  |  |  | 2.2908 | 2.2265 | 2.1653 | 2.1255 | 2.049 | 1.9571 | 1.851 | 1.7602 | 1.6418 | 1.1143 | 0.51429 | 0.23265 | 3.55 | 3.4622 | 3.3888 | 3.349 | 3.2571 | 3.1673 | 3.052 | 2.9612 | 2.8684 | 1.7776 | 0.93878 | 0.73469 | 3.5806 | 3.4908 | 3.4184 | 3.3776 | 3.2816 | 3.1786 | 3.048 | 2.9418 | 2.8408 | 1.9551 | 1.0357 | 0.78673
|  | HAWKERIDGE PRIMARY | HE |  |  |  |  | 2.2888 | 2.2265 | 2.1653 | 2.1245 | 2.052 | 1.9592 | 1.851 | 1.7673 | 1.6469 | 1.2949 | 1.1122 | 1.0378 | 3.549 | 3.4622 | 3.3888 | 3.3469 | 3.2633 | 3.1724 | 3.0602 | 2.9786 | 2.8878 | 2.2337 | 1.9184 | 1.8296 | 3.5786 | 3.4908 | 3.4184 | 3.3745 | 3.2867 | 3.1827 | 3.0541 | 2.9541 | 2.8551 | 2.4337 | 2.0969 | 1.9898
|  | HAWKERIDGE PRIMARY | FB |  |  |  |  | 2.302 | 2.2347 | 2.1724 | 2.1561 | 2.1388 | 2.1092 | 2.0806 | 2.0561 | 2.0031 | 1.7888 | 1.4878 | 1.2255 | 3.5612 | 3.4673 | 3.3949 | 3.3714 | 3.3531 | 3.3224 | 3.2796 | 3.2551 | 3.1939 | 2.9531 | 2.4153 | 1.7367 | 3.5929 | 3.498 | 3.4296 | 3.4061 | 3.3888 | 3.3531 | 3.3133 | 3.2857 | 3.2214 | 2.9673 | 2.6776 | 1.9888
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | HAWLEY PRIMARY | MINIMUM HEADROOM | SU 85973 57691 | NO | NO | 1.272 | 17.4684 | 17.5551 | 17.6153 | 17.5459 | 17.4551 | 17.1867 | 16.7929 | 16.3041 | 15.8531 | 14.0469 | 12.8459 | 12.1806 | 19.0796 | 19.0714 | 19.0816 | 18.7898 | 18.5735 | 18.2092 | 17.7755 | 17.252 | 16.7612 | 14.6194 | 11.2153 | 6.7398 | 17.8082 | 17.85 | 17.9224 | 17.7173 | 17.5418 | 17.1816 | 16.751 | 16.2286 | 15.7592 | 13.8204 | 12.6061 | 12.0398
|  | HAWLEY PRIMARY | EE |  |  |  |  | 17.4684 | 17.5551 | 17.6153 | 17.5459 | 17.4653 | 17.2929 | 16.9724 | 16.5714 | 16.2041 | 14.3133 | 12.8459 | 12.1806 | 19.0806 | 19.0714 | 19.0847 | 18.7898 | 18.6102 | 18.2684 | 17.8704 | 17.3949 | 16.949 | 14.6194 | 12.8204 | 11.1796 | 17.8082 | 17.85 | 17.9224 | 17.7173 | 17.5867 | 17.2684 | 16.8969 | 16.4551 | 16.0357 | 14.0214 | 12.6061 | 12.0398
|  | HAWLEY PRIMARY | HT |  |  |  |  | 17.4735 | 17.5714 | 17.6357 | 17.5602 | 17.4551 | 17.1867 | 16.7929 | 16.3041 | 15.8531 | 14.0469 | 12.95 | 12.7592 | 19.0796 | 19.0755 | 19.0898 | 18.7969 | 18.5735 | 18.2092 | 17.7755 | 17.252 | 16.7612 | 15.0347 | 14.1806 | 13.9327 | 17.8143 | 17.8704 | 17.95 | 17.7367 | 17.5418 | 17.1816 | 16.751 | 16.2286 | 15.7592 | 13.8204 | 12.75 | 12.6204
|  | HAWLEY PRIMARY | HE |  |  |  |  | 17.4755 | 17.5694 | 17.6327 | 17.5571 | 17.4673 | 17.2959 | 17.0112 | 16.6429 | 16.3082 | 14.8235 | 13.8357 | 13.3918 | 19.0816 | 19.0735 | 19.0898 | 18.7949 | 18.6153 | 18.2745 | 17.8806 | 17.4235 | 17 | 14.8153 | 13.1633 | 11.5051 | 17.8184 | 17.8704 | 17.9551 | 17.7367 | 17.5918 | 17.2857 | 16.9235 | 16.5041 | 16.1306 | 14.5102 | 13.5663 | 13.1724
|  | HAWLEY PRIMARY | FB |  |  |  |  | 17.5857 | 17.7367 | 17.8255 | 17.9306 | 17.9622 | 17.952 | 17.9173 | 17.8582 | 17.7847 | 16.9184 | 14.8949 | 13.6929 | 19.1316 | 19.1337 | 19.0816 | 19.0765 | 18.9388 | 18.6949 | 18.4163 | 18.1173 | 17.7959 | 15.1745 | 11.2153 | 6.7398 | 17.9959 | 18.1214 | 18.1959 | 18.3286 | 18.3612 | 18.3204 | 18.252 | 18.1541 | 18.0173 | 16.602 | 14.5459 | 13.3245
NORTH HYDE GSP |  | HAYES PRIMARY | MINIMUM HEADROOM | TQ 09519 79541 | NO | YES | 22.787 | 25.8157 | 25.5054 | 24.3759 | 23.4667 | 22.2738 | 20.9106 | 19.4126 | 17.2014 | 15.0636 | 6.0738 | -0.18843 | -3.2221 | 31.8168 | 31.5903 | 30.6189 | 30.1434 | 29.477 | 28.7291 | 27.6087 | 25.2209 | 23.2026 | 13.9138 | 7.4026 | 3.6199 | 26.9893 | 26.8321 | 25.8607 | 25.2556 | 24.4209 | 23.4209 | 22.1607 | 19.7077 | 17.5658 | 7.8332 | 0.96378 | -1.8872
|  | HAYES PRIMARY | EE |  |  |  |  | 25.8157 | 25.6575 | 25.1493 | 23.9963 | 23.1983 | 22.1483 | 19.9371 | 17.6779 | 15.5585 | 6.7891 | -0.18843 | -3.2221 | 31.8189 | 31.7852 | 31.4577 | 30.5311 | 30.127 | 29.5536 | 27.6087 | 25.2209 | 23.2026 | 13.9138 | 7.4026 | 3.6199 | 26.9893 | 26.9893 | 26.6454 | 25.7046 | 25.2026 | 24.4393 | 22.2628 | 19.9454 | 17.726 | 7.8332 | 0.96378 | -1.8872
|  | HAYES PRIMARY | HT |  |  |  |  | 25.8554 | 25.5054 | 24.3759 | 23.4667 | 22.2738 | 20.9106 | 19.4126 | 17.2014 | 15.0636 | 6.0738 | -0.026184 | -2.5537 | 31.8168 | 31.5903 | 30.6189 | 30.1434 | 29.477 | 28.7291 | 27.8372 | 25.7444 | 23.923 | 17.0883 | 12.925 | 11.4577 | 27.0128 | 26.8321 | 25.8607 | 25.2556 | 24.4209 | 23.4209 | 22.1607 | 19.7077 | 17.5658 | 8.8974 | 3.2505 | 1.1505
|  | HAYES PRIMARY | HE |  |  |  |  | 25.8401 | 25.7044 | 25.2197 | 24.0544 | 23.2422 | 22.2636 | 21.1422 | 19.7065 | 18.3534 | 13.683 | 10.4922 | 8.3973 | 31.8209 | 31.7883 | 31.4648 | 30.5413 | 30.1372 | 29.5883 | 28.9372 | 27.524 | 26.3944 | 21.3474 | 18.0485 | 15.0005 | 27.0097 | 27.0321 | 26.7066 | 25.7607 | 25.2515 | 24.5536 | 23.7097 | 22.4015 | 21.1056 | 16.1056 | 13.0332 | 11.275
|  | HAYES PRIMARY | FB |  |  |  |  | 26.1106 | 26.1565 | 26.0799 | 25.783 | 24.9085 | 24.631 | 24.2391 | 23.885 | 23.4728 | 20.984 | 17.9432 | 14.6065 | 31.9597 | 31.8974 | 31.8107 | 31.524 | 30.5791 | 30.1842 | 29.6648 | 29.1862 | 28.6434 | 24.9883 | 18.7811 | 11.1944 | 27.325 | 27.423 | 27.4668 | 27.3209 | 26.5954 | 26.4352 | 26.1434 | 25.8954 | 25.5679 | 23.3056 | 19.4219 | 16.1872
COWLEY GSP | HEADINGTON BSP | HEADINGTON PRIMARY | MINIMUM HEADROOM | SP 54440 08085 | NO | NO | 8.08 | 15.8566 | 15.6382 | 15.4709 | 15.3372 | 15.1066 | 14.8454 | 14.4392 | 14.0188 | 13.5627 | 12.4341 | 11.4607 | 10.9056 | 16.3198 | 16.125 | 15.9974 | 15.8239 | 15.4403 | 15.1005 | 14.6209 | 14.1709 | 13.6688 | 12.2005 | 9.6954 | 5.679 | 15.678 | 15.5341 | 15.4443 | 15.3341 | 15.0321 | 14.7433 | 14.3117 | 13.8903 | 13.425 | 12.1168 | 11.0801 | 10.6056
|  | HEADINGTON PRIMARY | EE |  |  |  |  | 15.9158 | 15.7617 | 15.6862 | 15.6433 | 15.5188 | 15.2576 | 14.9811 | 14.6556 | 14.3892 | 12.7617 | 11.4607 | 10.9056 | 16.3596 | 16.2137 | 16.1382 | 16.0158 | 15.7464 | 15.3709 | 14.9954 | 14.5688 | 14.2158 | 12.2035 | 10.6688 | 9.2076 | 15.7107 | 15.6056 | 15.5709 | 15.525 | 15.3607 | 15.0362 | 14.7168 | 14.3372 | 14.0045 | 12.3127 | 11.0801 | 10.6056
|  | HEADINGTON PRIMARY | HT |  |  |  |  | 15.8566 | 15.6382 | 15.4709 | 15.3372 | 15.1066 | 14.8454 | 14.4392 | 14.0188 | 13.5627 | 12.4341 | 12.0362 | 12.175 | 16.3198 | 16.125 | 15.9974 | 15.8239 | 15.4403 | 15.1005 | 14.6209 | 14.1709 | 13.6688 | 12.2005 | 11.4872 | 11.2586 | 15.678 | 15.5341 | 15.4443 | 15.3341 | 15.0321 | 14.7433 | 14.3117 | 13.8903 | 13.425 | 12.1168 | 11.6474 | 11.8433
|  | HEADINGTON PRIMARY | HE |  |  |  |  | 15.928 | 15.779 | 15.7229 | 15.6678 | 15.5311 | 15.3127 | 15.0168 | 14.7341 | 14.4352 | 13.3362 | 12.578 | 12.2423 | 16.3607 | 16.2066 | 16.1423 | 16.0239 | 15.7535 | 15.425 | 15.0066 | 14.6229 | 14.2107 | 12.425 | 11.0515 | 9.6178 | 15.7219 | 15.6209 | 15.6076 | 15.5505 | 15.3719 | 15.1025 | 14.7474 | 14.4219 | 13.9974 | 12.578 | 12.0066 | 11.8198
|  | HEADINGTON PRIMARY | FB |  |  |  |  | 16.0841 | 16.0076 | 15.926 | 15.9627 | 16.1056 | 16.1117 | 16.0923 | 16.0545 | 15.9943 | 15.2443 | 13.7596 | 12.775 | 16.4025 | 16.2688 | 16.1188 | 16.0321 | 15.979 | 15.7903 | 15.5617 | 15.3168 | 15.0525 | 12.9994 | 9.6954 | 5.679 | 15.8801 | 15.8484 | 15.8076 | 15.8423 | 15.9637 | 15.9525 | 15.9147 | 15.8617 | 15.7852 | 14.7168 | 13.327 | 12.4209
NURSLING GSP | VELMORE BSP | HEDGE END PRIMARY | MINIMUM HEADROOM | SU 49035 15685 | NO | YES | 17.927 | -3.7345 | -3.9549 | -4.2682 | -4.3151 | -4.661 | -5.1508 | -5.6437 | -6.258 | -6.8386 | -8.9427 | -10.361 | -11.0784 | -1.7376 | -1.8692 | -2.0212 | -2.0335 | -2.361 | -2.6304 | -2.8947 | -3.2865 | -3.5784 | -4.6722 | -5.4916 | -7.1794 | -2.8069 | -2.9763 | -3.2008 | -3.2253 | -3.6192 | -4.0131 | -4.3794 | -4.8947 | -5.312 | -6.9253 | -7.91 | -8.3406
|  | HEDGE END PRIMARY | EE |  |  |  |  | -3.7345 | -3.9549 | -4.2682 | -4.3069 | -4.5998 | -5.0845 | -5.5529 | -6.0467 | -6.4998 | -8.2824 | -9.559 | -10.3131 | -1.7365 | -1.8671 | -2.0141 | -2.0171 | -2.2794 | -2.5222 | -2.7804 | -3.1335 | -3.3855 | -4.6233 | -5.3967 | -6.059 | -2.8069 | -2.9763 | -3.2008 | -3.2202 | -3.5355 | -3.9131 | -4.2763 | -4.7161 | -5.0559 | -6.4733 | -7.3753 | -7.8692
|  | HEDGE END PRIMARY | HT |  |  |  |  | -3.7304 | -3.9396 | -4.2161 | -4.2957 | -4.661 | -5.1508 | -5.6437 | -6.258 | -6.8386 | -8.9427 | -10.361 | -11.0784 | -1.7376 | -1.8661 | -2.0212 | -2.0335 | -2.361 | -2.6304 | -2.8947 | -3.2865 | -3.5784 | -4.6722 | -5.1937 | -5.3947 | -2.8059 | -2.9692 | -3.1773 | -3.2233 | -3.6192 | -4.0131 | -4.3794 | -4.8947 | -5.312 | -6.9253 | -7.91 | -8.3406
|  | HEDGE END PRIMARY | HE |  |  |  |  | -3.7304 | -3.9498 | -4.258 | -4.3151 | -4.6284 | -5.1141 | -5.5794 | -6.059 | -6.5243 | -8.0773 | -9.162 | -9.6886 | -1.7376 | -1.8692 | -2.0141 | -2.0212 | -2.2876 | -2.5304 | -2.7947 | -3.112 | -3.3763 | -4.5069 | -5.2059 | -5.8784 | -2.8049 | -2.9753 | -3.1947 | -3.2253 | -3.5539 | -3.9345 | -4.2957 | -4.6998 | -5.0569 | -6.2957 | -7.0447 | -7.3988
|  | HEDGE END PRIMARY | FB |  |  |  |  | -3.5978 | -3.7284 | -3.9039 | -3.909 | -3.9539 | -4.0376 | -4.0569 | -4.1478 | -4.258 | -5.3478 | -6.4794 | -7.1069 | -1.6682 | -1.7804 | -1.8886 | -1.9396 | -2.0222 | -2.1498 | -2.2212 | -2.3692 | -2.5324 | -3.8998 | -5.4916 | -7.1794 | -2.7049 | -2.7937 | -2.9131 | -2.9304 | -2.9784 | -3.0569 | -3.0671 | -3.1549 | -3.261 | -4.362 | -5.3692 | -5.9253
BRAMLEY (BASI) GSP | READING BSP | HENLEY PRIMARY | MINIMUM HEADROOM | SU 76070 82422 | NO | YES | 4.529 | 5.5147 | 5.4504 | 5.3555 | 5.232 | 5.0361 | 4.7177 | 4.3361 | 3.8677 | 3.3504 | 1.4269 | 0.35853 | 0.10751 | 11.6759 | 11.5861 | 11.4657 | 11.2953 | 11.0555 | 10.6942 | 10.1585 | 9.5167 | 8.8422 | 6.1504 | 4.5779 | 1.5687 | 8.3677 | 8.2289 | 8.082 | 7.8891 | 7.6106 | 7.2177 | 6.7575 | 6.1912 | 5.6065 | 3.4636 | 2.4044 | 2.1891
|  | HENLEY PRIMARY | EE |  |  |  |  | 5.5402 | 5.5085 | 5.4391 | 5.334 | 5.1922 | 4.8973 | 4.4993 | 4.0167 | 3.4912 | 1.4269 | 0.35853 | 0.10751 | 11.6881 | 11.6147 | 11.5044 | 11.3402 | 11.1269 | 10.8055 | 10.2504 | 9.5922 | 8.9187 | 6.1504 | 4.5779 | 3.5657 | 8.3891 | 8.2769 | 8.1483 | 7.9708 | 7.7391 | 7.3677 | 6.883 | 6.3014 | 5.7116 | 3.4636 | 2.4044 | 2.1891
|  | HENLEY PRIMARY | HT |  |  |  |  | 5.5147 | 5.4504 | 5.3555 | 5.232 | 5.0361 | 4.7177 | 4.3361 | 3.8677 | 3.3504 | 1.4504 | 0.61465 | 0.38404 | 11.6759 | 11.5861 | 11.4657 | 11.2953 | 11.0555 | 10.6942 | 10.1585 | 9.5167 | 8.8422 | 6.4708 | 5.4891 | 5.1728 | 8.3677 | 8.2289 | 8.082 | 7.8891 | 7.6106 | 7.2177 | 6.7575 | 6.1912 | 5.6065 | 3.5014 | 2.6575 | 2.4728
|  | HENLEY PRIMARY | HE |  |  |  |  | 5.5361 | 5.5034 | 5.432 | 5.3208 | 5.1677 | 4.8861 | 4.4953 | 4.0096 | 3.4657 | 1.8779 | 0.88404 | 0.67792 | 11.6861 | 11.6106 | 11.5004 | 11.333 | 11.1167 | 10.8024 | 10.2483 | 9.5789 | 8.883 | 6.5647 | 5.031 | 3.9881 | 8.384 | 8.2687 | 8.1412 | 7.9565 | 7.7167 | 7.3606 | 6.883 | 6.2932 | 5.6881 | 3.93 | 2.9228 | 2.7381
|  | HENLEY PRIMARY | FB |  |  |  |  | 5.7687 | 5.8881 | 5.9473 | 6.0361 | 6.033 | 6.0085 | 5.9596 | 5.8647 | 5.7412 | 4.7289 | 2.8136 | 1.7412 | 11.8177 | 11.8555 | 11.8575 | 11.8769 | 11.7891 | 11.6789 | 11.38 | 11.0606 | 10.7279 | 8.48 | 5.0504 | 1.5687 | 8.6279 | 8.7096 | 8.7585 | 8.9096 | 8.7728 | 8.6708 | 8.533 | 8.3647 | 8.1871 | 6.8912 | 4.8514 | 3.7269
AXMINSTER GSP | YEOVIL BSP | HENSTRIDGE PRIMARY | MINIMUM HEADROOM | ST 72676 19263 | NO | NO | 5.792 | 16.5305 | 16.4622 | 16.2897 | 16.1693 | 15.8356 | 15.4836 | 15.105 | 14.6826 | 14.2877 | 12.9948 | 11.755 | 11.4846 | 16.5993 | 16.5279 | 16.2983 | 16.2197 | 15.8728 | 15.5412 | 15.183 | 14.7769 | 14.4381 | 13.1207 | 12.1156 | 11.4401 | 15.4193 | 15.351 | 15.1887 | 15.0958 | 14.8122 | 14.5244 | 14.2101 | 13.8775 | 13.5724 | 12.6091 | 12.002 | 11.8724
|  | HENSTRIDGE PRIMARY | EE |  |  |  |  | 16.5438 | 16.501 | 16.3561 | 16.2367 | 15.9632 | 15.655 | 15.2989 | 14.9295 | 14.5785 | 13.2918 | 12.0744 | 11.8091 | 16.6218 | 16.5646 | 16.3452 | 16.2452 | 15.9391 | 15.631 | 15.284 | 14.9238 | 14.5758 | 13.1207 | 12.1156 | 11.8789 | 15.4326 | 15.3958 | 15.2397 | 15.1397 | 14.8989 | 14.6458 | 14.352 | 14.053 | 13.7703 | 12.8183 | 12.2275 | 12.0999
|  | HENSTRIDGE PRIMARY | HT |  |  |  |  | 16.5305 | 16.4622 | 16.2897 | 16.1693 | 15.8356 | 15.4836 | 15.105 | 14.6826 | 14.2877 | 12.9948 | 11.755 | 11.4846 | 16.5993 | 16.5279 | 16.2983 | 16.2197 | 15.8728 | 15.5412 | 15.183 | 14.7769 | 14.4381 | 13.1473 | 12.3728 | 12.4983 | 15.4193 | 15.351 | 15.1887 | 15.0958 | 14.8122 | 14.5244 | 14.2101 | 13.8775 | 13.5724 | 12.6091 | 12.002 | 11.8724
|  | HENSTRIDGE PRIMARY | HE |  |  |  |  | 16.5438 | 16.502 | 16.353 | 16.2224 | 15.9387 | 15.6265 | 15.2652 | 14.8816 | 14.5173 | 13.4999 | 12.6938 | 12.3152 | 16.6207 | 16.5656 | 16.3442 | 16.2452 | 15.932 | 15.6483 | 15.2932 | 14.9524 | 14.6126 | 13.434 | 12.8105 | 12.3279 | 15.4326 | 15.3958 | 15.2377 | 15.1305 | 14.8846 | 14.6346 | 14.3377 | 14.0356 | 13.7479 | 12.9693 | 12.4877 | 12.2999
|  | HENSTRIDGE PRIMARY | FB |  |  |  |  | 16.6193 | 16.6173 | 16.5969 | 16.5703 | 16.4152 | 16.3254 | 16.2775 | 16.1887 | 16.0632 | 15.3836 | 14.653 | 14.0071 | 16.6891 | 16.6524 | 16.6044 | 16.5595 | 16.3932 | 16.1718 | 16.1054 | 15.9269 | 15.6769 | 14.4738 | 13.0024 | 11.4401 | 15.505 | 15.4928 | 15.4714 | 15.4418 | 15.2816 | 15.2122 | 15.1775 | 15.0897 | 14.9581 | 14.2999 | 13.6612 | 13.3193
FLEET-BRAMLEY GSP | ALTON BSP | HERRIARD PRIMARY | MINIMUM HEADROOM | SU 66770 44972 | YES | NO | 0.092 | 5.5827 | 5.5837 | 5.5755 | 5.5439 | 5.5041 | 5.3061 | 5.2112 | 5.152 | 5.0469 | 4.752 | 4.5694 | 4.5031 | 6.0255 | 6.0184 | 6.0031 | 5.9888 | 5.948 | 5.6878 | 5.5714 | 5.5235 | 5.4173 | 5.15 | 5.0214 | 5.0204 | 5.2031 | 5.2031 | 5.1949 | 5.1796 | 5.1408 | 4.9214 | 4.8112 | 4.7582 | 4.6582 | 4.399 | 4.2735 | 4.2714
|  | HERRIARD PRIMARY | EE |  |  |  |  | 5.5837 | 5.5837 | 5.5755 | 5.55 | 5.5163 | 5.4204 | 5.2704 | 5.201 | 5.0867 | 4.752 | 4.5694 | 4.5122 | 6.0286 | 6.0204 | 6.0061 | 5.9929 | 5.9653 | 5.8173 | 5.6408 | 5.5908 | 5.4796 | 5.15 | 5.0214 | 5.0204 | 5.2041 | 5.2051 | 5.198 | 5.1847 | 5.1592 | 5.0286 | 4.8684 | 4.8071 | 4.7224 | 4.399 | 4.2735 | 4.2714
|  | HERRIARD PRIMARY | HT |  |  |  |  | 5.5827 | 5.5847 | 5.5765 | 5.5449 | 5.5041 | 5.3061 | 5.2112 | 5.152 | 5.0469 | 4.8041 | 4.5837 | 4.5031 | 6.0286 | 6.0204 | 6.0031 | 5.9888 | 5.948 | 5.6878 | 5.5714 | 5.5235 | 5.4173 | 5.1755 | 5.0469 | 5.102 | 5.2031 | 5.2051 | 5.1949 | 5.1796 | 5.1408 | 4.9214 | 4.8112 | 4.7582 | 4.6582 | 4.4235 | 4.2786 | 4.2796
|  | HERRIARD PRIMARY | HE |  |  |  |  | 5.5827 | 5.5837 | 5.5765 | 5.5439 | 5.5051 | 5.4694 | 5.349 | 5.1816 | 5.1092 | 4.8633 | 4.7276 | 4.7398 | 6.0255 | 6.0184 | 6.0041 | 5.9898 | 5.9622 | 5.9347 | 5.7592 | 5.5929 | 5.5357 | 5.2571 | 5.2041 | 5.2714 | 5.2031 | 5.2031 | 5.1959 | 5.1806 | 5.151 | 5.1153 | 4.9541 | 4.8163 | 4.7551 | 4.5 | 4.4398 | 4.4847
|  | HERRIARD PRIMARY | FB |  |  |  |  | 5.6071 | 5.6153 | 5.6214 | 5.6235 | 5.6163 | 5.6082 | 5.5898 | 5.5724 | 5.5633 | 5.4776 | 5.3724 | 5.1082 | 6.0561 | 6.0571 | 6.0459 | 6.049 | 6.0408 | 6.0296 | 6.002 | 5.9735 | 5.9612 | 5.8173 | 5.6663 | 5.2582 | 5.2357 | 5.2459 | 5.25 | 5.2571 | 5.2602 | 5.2541 | 5.2327 | 5.2112 | 5.2061 | 5.0867 | 4.9735 | 4.699
IVER 132KV GSP | CHALVEY | HERSCHEL STREET PRIMARY | MINIMUM HEADROOM | TBC | NO | YES | TBC |  |  |  | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | HERSCHEL STREET PRIMARY | EE | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | HERSCHEL STREET PRIMARY | HT | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | HERSCHEL STREET PRIMARY | HE | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | HERSCHEL STREET PRIMARY | FB | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE PRIMARY | MINIMUM HEADROOM | SU 84733 92200 | NO | NO | 7.471 | 3.3887 | 3.2806 | 3.1857 | 2.9214 | 2.5428 | 2.0122 | 1.4122 | 0.76935 | 0.12037 | -2.3562 | -3.9592 | -4.5592 | 22.4122 | 22.1 | 21.9704 | 21.5959 | 20.9826 | 20.5193 | 19.9173 | 19.2224 | 18.4581 | 16.0806 | 14.751 | 12.5816 | 5.201 | 5.1459 | 5.1173 | 4.9275 | 4.6163 | 4.2102 | 3.7336 | 3.2163 | 2.6847 | 0.62445 | -0.70514 | -1.1266
|  | HIGH WYCOMBE PRIMARY | EE |  |  |  |  | 3.3887 | 3.2806 | 3.1857 | 2.9214 | 2.5724 | 2.0489 | 1.4612 | 0.83976 | 0.20812 | -1.9531 | -3.2847 | -3.8939 | 22.4122 | 22.101 | 21.9744 | 21.6091 | 21.0204 | 20.5693 | 19.9898 | 19.3224 | 18.5673 | 16.1663 | 14.751 | 13.5622 | 5.201 | 5.1459 | 5.1173 | 4.9347 | 4.6479 | 4.2551 | 3.7969 | 3.301 | 2.7877 | 0.90404 | -0.24902 | -0.75106
|  | HIGH WYCOMBE PRIMARY | HT |  |  |  |  | 3.4204 | 3.3224 | 3.2296 | 2.9377 | 2.5428 | 2.0122 | 1.4122 | 0.76935 | 0.12037 | -2.3562 | -3.9592 | -4.5592 | 22.4142 | 22.1061 | 21.9704 | 21.5959 | 20.9826 | 20.5193 | 19.9173 | 19.2224 | 18.4581 | 16.0806 | 15.1959 | 15.1377 | 5.2153 | 5.1744 | 5.1255 | 4.9275 | 4.6163 | 4.2102 | 3.7336 | 3.2163 | 2.6847 | 0.62445 | -0.70514 | -1.1266
|  | HIGH WYCOMBE PRIMARY | HE |  |  |  |  | 3.3959 | 3.2938 | 3.204 | 2.9234 | 2.5551 | 2.102 | 1.5785 | 1.0224 | 0.45404 | -1.2919 | -2.4041 | -2.9245 | 22.4122 | 22.1 | 21.9755 | 21.6112 | 21.0153 | 20.5755 | 19.9949 | 19.3469 | 18.6183 | 16.8122 | 15.7204 | 14.6663 | 5.2051 | 5.153 | 5.1347 | 4.9428 | 4.6428 | 4.2928 | 3.8734 | 3.4204 | 2.9489 | 1.4816 | 0.56833 | 0.15608
|  | HIGH WYCOMBE PRIMARY | FB |  |  |  |  | 3.5479 | 3.4928 | 3.4887 | 3.4357 | 3.3561 | 3.2622 | 3.1336 | 2.9551 | 2.7877 | 1.6234 | 0.27445 | -0.64086 | 22.5285 | 22.2265 | 22.1102 | 21.9673 | 21.8102 | 21.6316 | 21.3898 | 21.0112 | 20.703 | 18.5438 | 15.7928 | 12.5816 | 5.3173 | 5.3071 | 5.3285 | 5.3071 | 5.252 | 5.202 | 5.102 | 4.9377 | 4.7847 | 3.7 | 2.4214 | 1.5071
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN PRIMARY | MINIMUM HEADROOM | SU 86304 92972 | NO | NO | 4.343 | 23.1837 | 23.1929 | 23.1868 | 23.0317 | 22.7898 | 22.3878 | 21.9072 | 21.1255 | 20.5235 | 17.7602 | 15.847 | 15.1755 | 28.9653 | 28.9398 | 28.9021 | 28.8235 | 28.6684 | 28.4368 | 28.0847 | 27.6 | 27.1378 | 24.5898 | 22.3439 | 18.3357 | 25.1225 | 25.1255 | 25.1082 | 25.0123 | 24.7939 | 24.4031 | 23.9102 | 23.3204 | 22.8745 | 20.7582 | 18.948 | 18.15
|  | HIGH WYCOMBE TOWN PRIMARY | EE |  |  |  |  | 23.1837 | 23.1949 | 23.1888 | 23.0684 | 22.8684 | 22.5174 | 22.1011 | 21.4153 | 20.8704 | 18.1745 | 16.1164 | 15.1755 | 28.9653 | 28.9419 | 28.9164 | 28.8633 | 28.7296 | 28.5541 | 28.2572 | 27.8164 | 27.3949 | 24.5898 | 22.3439 | 20.6908 | 25.1255 | 25.1276 | 25.1153 | 25.0551 | 24.8684 | 24.5164 | 24.0592 | 23.5021 | 23.0908 | 20.9684 | 19.0398 | 18.15
|  | HIGH WYCOMBE TOWN PRIMARY | HT |  |  |  |  | 23.2 | 23.2327 | 23.2072 | 23.0419 | 22.7898 | 22.3878 | 21.9072 | 21.1255 | 20.5235 | 17.7602 | 15.847 | 15.3623 | 28.9664 | 28.9408 | 28.9021 | 28.8235 | 28.6684 | 28.4368 | 28.0847 | 27.6 | 27.1378 | 24.8347 | 23.2929 | 22.9296 | 25.1388 | 25.1521 | 25.1204 | 25.0123 | 24.7939 | 24.4031 | 23.9102 | 23.3204 | 22.8745 | 20.7582 | 18.948 | 18.599
|  | HIGH WYCOMBE TOWN PRIMARY | HE |  |  |  |  | 23.1847 | 23.1929 | 23.1868 | 23.0317 | 22.8051 | 22.496 | 22.1113 | 21.5317 | 21.0378 | 18.95 | 17.8102 | 17.1572 | 28.9664 | 28.9398 | 28.9123 | 28.8572 | 28.7215 | 28.5531 | 28.2623 | 27.8184 | 27.4072 | 24.9602 | 23.5664 | 22.1572 | 25.1225 | 25.1255 | 25.1082 | 25.0276 | 24.8582 | 24.5388 | 24.1102 | 23.5776 | 23.197 | 21.5817 | 20.698 | 20.1766
|  | HIGH WYCOMBE TOWN PRIMARY | FB |  |  |  |  | 23.298 | 23.3796 | 23.4276 | 23.4225 | 23.397 | 23.3613 | 23.2786 | 23.1551 | 23.0521 | 22.1643 | 20.198 | 18.6419 | 28.9847 | 28.9653 | 28.9306 | 28.8837 | 28.8102 | 28.697 | 28.4674 | 28.1919 | 27.9551 | 25.9704 | 22.5215 | 18.3357 | 25.2266 | 25.2827 | 25.3245 | 25.3204 | 25.3164 | 25.298 | 25.2286 | 25.1255 | 25.0368 | 23.9347 | 22.2398 | 20.9062
IVER 66KV GSP |  | HILLINGDON PRIMARY | MINIMUM HEADROOM | TQ 07470 82827 | NO | NO | 4.208 | 10.4856 | 10.2938 | 9.9264 | 9.0897 | 8.108 | 6.3601 | 4.408 | 2.2244 | 0.11416 | -7.842 | -13.5613 | -16.0481 | 17.9723 | 17.705 | 17.356 | 16.7825 | 16.0836 | 15.0162 | 13.7233 | 12.1387 | 10.6233 | 4.9703 | 0.30192 | -5.4858 | 12.4856 | 12.2713 | 11.8968 | 11.154 | 10.2744 | 8.8519 | 7.1958 | 5.2672 | 3.4121 | -3.3328 | -8.2195 | -10.196
|  | HILLINGDON PRIMARY | EE |  |  |  |  | 10.4856 | 10.4142 | 10.0938 | 9.407 | 8.608 | 6.8713 | 4.6448 | 2.4284 | 0.18967 | -7.2471 | -13.0522 | -15.793 | 17.9744 | 17.8346 | 17.5448 | 17.1427 | 16.6407 | 15.7274 | 14.2366 | 12.754 | 11.254 | 4.9703 | 0.30192 | -2.9583 | 12.4856 | 12.3693 | 12.0489 | 11.4631 | 10.7836 | 9.4356 | 7.4999 | 5.5989 | 3.6519 | -3.2011 | -8.2195 | -10.196
|  | HILLINGDON PRIMARY | HT |  |  |  |  | 10.506 | 10.2938 | 9.9264 | 9.0897 | 8.108 | 6.3601 | 4.408 | 2.2244 | 0.11416 | -7.842 | -13.5613 | -16.0481 | 17.9723 | 17.705 | 17.356 | 16.7825 | 16.0836 | 15.0162 | 13.7233 | 12.1387 | 10.6233 | 5.7397 | 2.9274 | 2.1723 | 12.5029 | 12.2713 | 11.8968 | 11.154 | 10.2744 | 8.8519 | 7.1958 | 5.2672 | 3.4121 | -3.3328 | -7.8838 | -9.2909
|  | HILLINGDON PRIMARY | HE |  |  |  |  | 10.5029 | 10.4478 | 10.1448 | 9.4121 | 8.5693 | 6.8989 | 5.0458 | 3.0958 | 1.1356 | -3.7562 | -8.0501 | -10.2154 | 17.9723 | 17.8315 | 17.5427 | 17.1356 | 16.6274 | 15.7121 | 14.6172 | 13.408 | 12.1958 | 7.458 | 3.6417 | 0.35294 | 12.4999 | 12.3958 | 12.0917 | 11.4754 | 10.7601 | 9.4489 | 7.9427 | 6.3407 | 4.7152 | 0.2611 | -3.2399 | -4.8205
|  | HILLINGDON PRIMARY | FB |  |  |  |  | 11.0101 | 11.3509 | 11.4284 | 11.355 | 11.3264 | 11.0152 | 10.6336 | 10.2203 | 9.7591 | 6.6223 | 1.8458 | -1.245 | 18.2846 | 18.3397 | 18.0917 | 17.808 | 17.5172 | 16.9182 | 16.2631 | 15.5938 | 14.8611 | 9.9152 | 2.6376 | -5.4858 | 13.1407 | 13.4233 | 13.3387 | 13.2182 | 13.1621 | 12.8223 | 12.4478 | 12.0336 | 11.5713 | 8.4274 | 3.9427 | 1.0764
LOVEDEAN GSP | PORTSMOUTH BSP | HILSEA PRIMARY | MINIMUM HEADROOM | SU 66394 03806 | NO | YES | 0.41 | 11.4012 | 11.3951 | 11.3032 | 11.243 | 11.1542 | 11.0532 | 10.9461 | 10.8277 | 10.7063 | 10.2532 | 9.9063 | 9.8175 | 11.7185 | 11.7175 | 11.6604 | 11.6308 | 11.5787 | 11.5246 | 11.4532 | 11.3889 | 11.3185 | 11.0338 | 10.8318 | 10.7848 | 11.3644 | 11.3604 | 11.292 | 11.2512 | 11.1848 | 11.1104 | 11.0185 | 10.9328 | 10.8583 | 10.5012 | 10.244 | 10.1879
|  | HILSEA PRIMARY | EE |  |  |  |  | 11.4012 | 11.3951 | 11.3032 | 11.2471 | 11.1695 | 11.0532 | 10.9461 | 10.8277 | 10.7063 | 10.2532 | 9.9063 | 9.8175 | 11.7195 | 11.7175 | 11.6604 | 11.6308 | 11.5818 | 11.5246 | 11.4532 | 11.3889 | 11.3185 | 11.0338 | 10.8318 | 10.7848 | 11.3644 | 11.3604 | 11.292 | 11.2522 | 11.194 | 11.1104 | 11.0185 | 10.9328 | 10.8583 | 10.5012 | 10.244 | 10.1879
|  | HILSEA PRIMARY | HT |  |  |  |  | 11.4012 | 11.3961 | 11.3073 | 11.2563 | 11.1746 | 11.0746 | 10.9471 | 10.8553 | 10.7471 | 10.2767 | 9.9144 | 9.8532 | 11.7185 | 11.7175 | 11.6614 | 11.6328 | 11.5818 | 11.5308 | 11.4553 | 11.3961 | 11.3287 | 11.0665 | 10.8859 | 10.8787 | 11.3655 | 11.3614 | 11.2951 | 11.2553 | 11.1951 | 11.1216 | 11.0277 | 10.9471 | 10.8644 | 10.5175 | 10.2553 | 10.2206
|  | HILSEA PRIMARY | HE |  |  |  |  | 11.4042 | 11.3961 | 11.3053 | 11.243 | 11.1542 | 11.0563 | 10.9583 | 10.844 | 10.7297 | 10.4236 | 10.294 | 10.2206 | 11.7206 | 11.7175 | 11.6604 | 11.6318 | 11.5787 | 11.5297 | 11.4614 | 11.3971 | 11.3308 | 11.1593 | 11.1185 | 11.0869 | 11.3675 | 11.3614 | 11.294 | 11.2512 | 11.1848 | 11.1165 | 11.0267 | 10.943 | 10.8593 | 10.641 | 10.5593 | 10.5155
|  | HILSEA PRIMARY | FB |  |  |  |  | 11.4206 | 11.4134 | 11.4063 | 11.3981 | 11.3134 | 11.2757 | 11.2563 | 11.1981 | 11.1665 | 10.9328 | 10.7236 | 10.4879 | 11.7277 | 11.7246 | 11.7206 | 11.7155 | 11.6593 | 11.6379 | 11.6216 | 11.5828 | 11.5573 | 11.3848 | 11.2032 | 10.9971 | 11.3787 | 11.3767 | 11.3695 | 11.3644 | 11.2991 | 11.2746 | 11.2583 | 11.2134 | 11.1879 | 11.0022 | 10.8236 | 10.6308
MANNINGTON GSP | ARNEWOOD BSP | HINCHESLEA PRIMARY | MINIMUM HEADROOM | SU 27805 00447 | NO | NO | 0.495 | 7.3577 | 7.2995 | 7.1811 | 7.1015 | 6.8077 | 6.2699 | 5.7291 | 5.1515 | 4.5566 | 2.873 | 1.475 | 0.87194 | 8.3439 | 8.2398 | 8.1112 | 8.0429 | 7.8133 | 7.4857 | 7.1796 | 6.7214 | 6.4224 | 5.2939 | 4.652 | 4.0122 | 7.3653 | 7.2776 | 7.152 | 7.0714 | 6.8408 | 6.4337 | 6.0214 | 5.5163 | 5.0969 | 3.6398 | 2.6959 | 2.4265
|  | HINCHESLEA PRIMARY | EE |  |  |  |  | 7.374 | 7.2995 | 7.1913 | 7.1556 | 6.874 | 6.3638 | 5.824 | 5.1995 | 4.6995 | 2.925 | 1.6607 | 1.0434 | 8.3592 | 8.2398 | 8.1194 | 8.0969 | 7.8582 | 7.5694 | 7.248 | 6.8531 | 6.5622 | 5.348 | 4.652 | 4.2602 | 7.3806 | 7.2776 | 7.1612 | 7.1449 | 6.8898 | 6.498 | 6.0735 | 5.5602 | 5.1724 | 3.7612 | 2.8704 | 2.5112
|  | HINCHESLEA PRIMARY | HT |  |  |  |  | 7.3577 | 7.3209 | 7.1811 | 7.1015 | 6.8321 | 6.3383 | 5.8689 | 5.2474 | 4.774 | 2.873 | 1.475 | 0.87194 | 8.3439 | 8.2806 | 8.1112 | 8.0429 | 7.8133 | 7.4857 | 7.1796 | 6.7214 | 6.4224 | 5.2939 | 4.751 | 4.7327 | 7.3653 | 7.3133 | 7.152 | 7.0714 | 6.8408 | 6.4337 | 6.0531 | 5.5163 | 5.1276 | 3.6398 | 2.6959 | 2.4265
|  | HINCHESLEA PRIMARY | HE |  |  |  |  | 7.3638 | 7.3423 | 7.2128 | 7.1209 | 6.8077 | 6.2699 | 5.7291 | 5.1515 | 4.5566 | 3.0199 | 1.8403 | 1.5536 | 8.348 | 8.2929 | 8.1378 | 8.0827 | 7.8337 | 7.5357 | 7.2367 | 6.9122 | 6.552 | 5.4224 | 4.7408 | 4.4929 | 7.3704 | 7.3286 | 7.1837 | 7.1194 | 6.8449 | 6.4347 | 6.0214 | 5.5704 | 5.0969 | 3.8398 | 2.9969 | 2.8755
|  | HINCHESLEA PRIMARY | FB |  |  |  |  | 7.6515 | 7.6913 | 7.5709 | 7.4985 | 7.4923 | 7.325 | 7.2689 | 7.1393 | 7.0046 | 6.0689 | 4.924 | 4.4087 | 8.6571 | 8.6408 | 8.4102 | 8.3082 | 8.2612 | 8.0643 | 7.9765 | 7.8194 | 7.6531 | 6.5673 | 5.1541 | 4.0122 | 7.7133 | 7.7327 | 7.5296 | 7.452 | 7.4286 | 7.2694 | 7.2347 | 7.1133 | 6.9827 | 6.1061 | 5.0357 | 4.5602
FLEET-BRAMLEY GSP | ALDERSHOT BSP | HINDHEAD PRIMARY | MINIMUM HEADROOM | SU 88631 36479 | NO | YES | 2.777 | 9.8244 | 9.903 | 9.9581 | 9.6918 | 9.4111 | 8.8989 | 8.3601 | 7.7336 | 7.1264 | 5.4724 | 4.5724 | 4.3805 | 13.2744 | 13.2571 | 13.2673 | 12.8989 | 12.6224 | 12.204 | 11.7367 | 11.1867 | 10.6591 | 9.2111 | 8.4183 | 6.0938 | 11.2581 | 11.2989 | 11.3438 | 10.9805 | 10.6856 | 10.2407 | 9.753 | 9.1805 | 8.6295 | 7.1305 | 6.4326 | 6.4009
|  | HINDHEAD PRIMARY | EE |  |  |  |  | 9.8316 | 9.9509 | 10.0744 | 9.8999 | 9.7826 | 9.3775 | 8.9775 | 8.5234 | 8.0295 | 6.5071 | 5.5203 | 5.1958 | 13.2785 | 13.2826 | 13.3244 | 13.004 | 12.8326 | 12.4591 | 12.0764 | 11.6397 | 11.1724 | 9.5183 | 8.5071 | 7.803 | 11.2642 | 11.3336 | 11.4316 | 11.1458 | 10.9764 | 10.602 | 10.2213 | 9.7867 | 9.3101 | 7.8816 | 7.0662 | 6.8764
|  | HINDHEAD PRIMARY | HT |  |  |  |  | 9.8244 | 9.903 | 9.9581 | 9.6918 | 9.4111 | 8.8989 | 8.3601 | 7.7336 | 7.1264 | 5.4724 | 4.5724 | 4.3805 | 13.2744 | 13.2571 | 13.2673 | 12.8989 | 12.6224 | 12.204 | 11.7367 | 11.1867 | 10.6591 | 9.2111 | 8.6438 | 8.5928 | 11.2581 | 11.2989 | 11.3438 | 10.9805 | 10.6856 | 10.2407 | 9.753 | 9.1805 | 8.6295 | 7.1305 | 6.4326 | 6.4009
|  | HINDHEAD PRIMARY | HE |  |  |  |  | 9.8305 | 9.9499 | 10.0744 | 9.8897 | 9.7601 | 9.3489 | 8.9377 | 8.4979 | 8.006 | 6.6469 | 5.8224 | 5.5418 | 13.2775 | 13.2805 | 13.3244 | 13.002 | 12.8264 | 12.452 | 12.0642 | 11.654 | 11.1928 | 9.6244 | 8.7377 | 7.9673 | 11.2632 | 11.3346 | 11.4316 | 11.1387 | 10.9611 | 10.5856 | 10.1958 | 9.7836 | 9.3132 | 8.0162 | 7.3509 | 7.1632
|  | HINDHEAD PRIMARY | FB |  |  |  |  | 9.9969 | 10.1856 | 10.3111 | 10.4448 | 10.4856 | 10.4346 | 10.406 | 10.3693 | 10.1183 | 9.104 | 7.7785 | 7.0907 | 13.403 | 13.453 | 13.4469 | 13.4897 | 13.4142 | 13.2438 | 13.0652 | 12.8611 | 12.4316 | 10.7101 | 8.4183 | 6.0938 | 11.4428 | 11.5887 | 11.6775 | 11.7979 | 11.7969 | 11.7152 | 11.6469 | 11.5469 | 11.1877 | 10.0979 | 8.852 | 8.1836
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL PRIMARY | MINIMUM HEADROOM | SU 00702 06030 | YES | NO | 0.4 | 5.5209 | 5.5015 | 5.4576 | 5.4158 | 5.2525 | 5.0352 | 4.8811 | 4.6658 | 4.4709 | 4.0474 | 3.6444 | 3.4566 | 5.4661 | 5.4426 | 5.414 | 5.3865 | 5.2222 | 5.0446 | 4.9528 | 4.7946 | 4.6528 | 4.3732 | 4.214 | 4.1701 | 5.4762 | 5.4568 | 5.4211 | 5.3772 | 5.1843 | 4.9986 | 4.8956 | 4.7119 | 4.5415 | 4.2017 | 3.9282 | 3.868
|  | HINTON MARTELL PRIMARY | EE |  |  |  |  | 5.5219 | 5.5046 | 5.4729 | 5.4495 | 5.3087 | 5.1678 | 4.9709 | 4.7801 | 4.6495 | 4.2087 | 3.8781 | 3.7485 | 5.4661 | 5.4457 | 5.4222 | 5.4028 | 5.2446 | 5.1344 | 4.9854 | 4.8395 | 4.7508 | 4.4181 | 4.214 | 4.1701 | 5.4772 | 5.4588 | 5.4282 | 5.3915 | 5.2048 | 5.0925 | 4.9231 | 4.7568 | 4.6405 | 4.3272 | 4.0905 | 4.0425
|  | HINTON MARTELL PRIMARY | HT |  |  |  |  | 5.5209 | 5.5015 | 5.4576 | 5.4158 | 5.2525 | 5.0352 | 4.8811 | 4.6658 | 4.4709 | 4.0474 | 3.6444 | 3.4566 | 5.4661 | 5.4426 | 5.414 | 5.3865 | 5.2222 | 5.0446 | 4.9528 | 4.7946 | 4.6528 | 4.3732 | 4.2232 | 4.264 | 5.4762 | 5.4568 | 5.4211 | 5.3772 | 5.1843 | 4.9986 | 4.8956 | 4.7119 | 4.5415 | 4.2017 | 3.9282 | 3.868
|  | HINTON MARTELL PRIMARY | HE |  |  |  |  | 5.524 | 5.5097 | 5.477 | 5.4464 | 5.377 | 5.1862 | 4.9474 | 4.7964 | 4.5964 | 4.3495 | 4.0709 | 3.9189 | 5.4661 | 5.4477 | 5.4242 | 5.4018 | 5.3579 | 5.1803 | 4.9865 | 4.8936 | 4.7446 | 4.5212 | 4.4008 | 4.312 | 5.4772 | 5.4599 | 5.4303 | 5.3894 | 5.316 | 5.1313 | 4.918 | 4.7997 | 4.618 | 4.4446 | 4.2741 | 4.1894
|  | HINTON MARTELL PRIMARY | FB |  |  |  |  | 5.574 | 5.5791 | 5.5801 | 5.5689 | 5.5515 | 5.524 | 5.5209 | 5.4842 | 5.4597 | 5.227 | 5.0689 | 4.7168 | 5.5059 | 5.4957 | 5.4854 | 5.4763 | 5.4589 | 5.4212 | 5.3936 | 5.3477 | 5.314 | 5.0518 | 4.8191 | 4.2732 | 5.516 | 5.5119 | 5.5088 | 5.4935 | 5.4762 | 5.4456 | 5.4262 | 5.3864 | 5.3619 | 5.1486 | 5.066 | 4.715
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HITCHES LANE PRIMARY | MINIMUM HEADROOM | SU 79461 54769 | NO | NO | 9.465 | 9.8901 | 9.936 | 9.5023 | 8.8686 | 8.1605 | 6.8839 | 5.4441 | 3.9635 | 2.5543 | -2.113 | -5.7528 | -7.6161 | 12.0594 | 12.0676 | 11.8023 | 11.3941 | 10.9421 | 10.2941 | 9.437 | 8.5288 | 7.6972 | 5.0839 | 3.0829 | -1.1038 | 10.6901 | 10.7656 | 10.4288 | 9.9839 | 9.4574 | 8.5146 | 7.339 | 6.1207 | 4.9829 | 1.2227 | -1.3303 | -2.3201
|  | HITCHES LANE PRIMARY | EE |  |  |  |  | 9.8901 | 9.936 | 9.6472 | 9.2635 | 8.8656 | 7.8074 | 6.638 | 5.3982 | 4.2431 | 0.15333 | -3.2957 | -5.2803 | 12.0615 | 12.0697 | 11.8615 | 11.5543 | 11.2197 | 10.638 | 9.9166 | 9.1278 | 8.4227 | 5.4146 | 3.3237 | 1.7656 | 10.6901 | 10.7656 | 10.5197 | 10.2339 | 9.9146 | 9.1105 | 8.1401 | 7.0901 | 6.135 | 2.6737 | 0.16965 | -1.0314
|  | HITCHES LANE PRIMARY | HT |  |  |  |  | 9.8921 | 9.9492 | 9.5023 | 8.8686 | 8.1605 | 6.8839 | 5.4441 | 3.9635 | 2.5543 | -2.113 | -5.7528 | -7.6161 | 12.0594 | 12.0676 | 11.8023 | 11.3941 | 10.9421 | 10.2941 | 9.437 | 8.5288 | 7.6972 | 5.0839 | 3.7217 | 3.3594 | 10.6911 | 10.7727 | 10.4288 | 9.9839 | 9.4574 | 8.5146 | 7.339 | 6.1207 | 4.9829 | 1.2227 | -1.3303 | -2.3201
|  | HITCHES LANE PRIMARY | HE |  |  |  |  | 9.8941 | 9.9421 | 9.6543 | 9.2248 | 8.7768 | 7.7839 | 6.6523 | 5.4411 | 4.3288 | 0.90027 | -2.2048 | -3.6559 | 12.0605 | 12.0686 | 11.8564 | 11.5421 | 11.1992 | 10.6452 | 9.9197 | 9.1074 | 8.4074 | 5.6584 | 3.5411 | 1.9901 | 10.6931 | 10.7686 | 10.5258 | 10.2105 | 9.8523 | 9.0992 | 8.1523 | 7.1023 | 6.1737 | 3.2503 | 0.95435 | 0.078837
|  | HITCHES LANE PRIMARY | FB |  |  |  |  | 10.187 | 10.3013 | 10.4288 | 10.4278 | 10.4248 | 10.185 | 9.9737 | 9.7186 | 9.4299 | 7.4135 | 4.5094 | 2.8482 | 12.1646 | 12.1676 | 12.1819 | 12.1329 | 12.0421 | 11.6574 | 11.2513 | 10.8135 | 10.3421 | 7.2533 | 3.0829 | -1.1038 | 10.9748 | 11.089 | 11.2186 | 11.2339 | 11.238 | 11.0176 | 10.8227 | 10.5901 | 10.3115 | 8.1911 | 5.4646 | 3.9901
LOVEDEAN GSP | FAREHAM (MAIN) BSP | HOEFORD PRIMARY | MINIMUM HEADROOM | SU 57855 04433 | NO | YES | 8.021 | 0.062229 | 0.077535 | 0.074473 | -0.097976 | 28.1908 | 27.899 | 27.3428 | 26.7735 | 26.1449 | 23.3377 | 21.8316 | 20.9684 | 2.6888 | 2.5745 | 2.4357 | 2.1071 | 28.3735 | 27.8918 | 27.15 | 26.5653 | 25.9663 | 23.3112 | 21.2398 | 16.8847 | 0.70713 | 0.70304 | 0.68264 | 0.40611 | 27.6469 | 27.202 | 26.5439 | 26.0122 | 25.4632 | 22.8194 | 21.4541 | 20.6847
|  | HOEFORD PRIMARY | EE |  |  |  |  | 0.071412 | 0.101 | 0.13264 | 0.031616 | 28.3694 | 28.1255 | 27.7235 | 27.1449 | 26.5684 | 23.7837 | 21.9275 | 20.9684 | 2.6949 | 2.5959 | 2.4806 | 2.1898 | 28.4959 | 27.9939 | 27.3571 | 26.7918 | 26.2265 | 23.3112 | 21.3204 | 19.5602 | 0.71427 | 0.72141 | 0.72651 | 0.51427 | 27.8194 | 27.3837 | 26.8245 | 26.3194 | 25.8214 | 23.1949 | 21.5296 | 20.6847
|  | HOEFORD PRIMARY | HT |  |  |  |  | 0.062229 | 0.077535 | 0.074473 | -0.097976 | 28.1908 | 27.899 | 27.3428 | 26.7735 | 26.1449 | 23.3377 | 21.8316 | 21.3918 | 2.6888 | 2.5745 | 2.4357 | 2.1071 | 28.3735 | 27.8918 | 27.15 | 26.5653 | 25.9663 | 23.5806 | 22.4367 | 22.0184 | 0.70713 | 0.70304 | 0.68264 | 0.40611 | 27.6469 | 27.202 | 26.5439 | 26.0122 | 25.4632 | 22.8194 | 21.4541 | 21.1081
|  | HOEFORD PRIMARY | HE |  |  |  |  | 0.072433 | 0.10509 | 0.13672 | 0.023453 | 28.3449 | 28.1235 | 27.7316 | 27.1928 | 26.6479 | 24.6194 | 23.6735 | 22.9796 | 2.6898 | 2.5898 | 2.4704 | 2.1745 | 28.4663 | 27.9745 | 27.3194 | 26.7826 | 26.2367 | 23.8214 | 22.3755 | 20.6939 | 0.71631 | 0.72447 | 0.73978 | 0.51121 | 27.7918 | 27.3755 | 26.8122 | 26.3347 | 25.8632 | 23.9439 | 23.1194 | 22.5051
|  | HOEFORD PRIMARY | FB |  |  |  |  | 0.19386 | 0.29998 | 0.32141 | 0.34896 | 28.8286 | 28.7796 | 28.7388 | 28.6581 | 28.5694 | 27.5449 | 25.2224 | 23.5204 | 2.7653 | 2.7837 | 2.5867 | 2.452 | 28.9939 | 28.6847 | 28.4296 | 28.0439 | 27.6643 | 25.1214 | 21.2398 | 16.8847 | 0.83366 | 0.91427 | 0.91427 | 0.92753 | 28.501 | 28.4316 | 28.3775 | 28.1796 | 27.999 | 26.6204 | 24.3643 | 22.7357
MANNINGTON GSP | LYTCHETT BSP | HOLES BAY PRIMARY | MINIMUM HEADROOM | SZ 00725 91955 | NO | NO | 2.278 | 5.2689 | 5.2761 | 5.2904 | 5.2271 | 5.0934 | 4.8536 | 4.4842 | 4.1649 | 3.8496 | 2.8006 | 1.9914 | 1.7016 | 6.2122 | 6.204 | 6.2224 | 6.1857 | 6.0898 | 6.0183 | 5.8132 | 5.6622 | 5.5163 | 4.4204 | 3.552 | 2.9132 | 5.9291 | 5.9026 | 5.9047 | 5.8291 | 5.7118 | 5.5393 | 5.2251 | 4.9791 | 4.7312 | 3.8332 | 3.072 | 2.7057
|  | HOLES BAY PRIMARY | EE |  |  |  |  | 5.272 | 5.2761 | 5.3026 | 5.2638 | 5.1526 | 4.9057 | 4.57 | 4.272 | 3.9679 | 3.0791 | 2.3985 | 1.9944 | 6.2153 | 6.204 | 6.2367 | 6.2081 | 6.1296 | 6.0489 | 5.8816 | 5.75 | 5.6153 | 4.4255 | 3.552 | 2.9132 | 5.9291 | 5.9026 | 5.9128 | 5.8516 | 5.7567 | 5.5669 | 5.2853 | 5.0536 | 4.8108 | 3.97 | 3.2414 | 2.7057
|  | HOLES BAY PRIMARY | HT |  |  |  |  | 5.271 | 5.2802 | 5.2904 | 5.2271 | 5.0934 | 4.8536 | 4.4842 | 4.1649 | 3.8496 | 2.8006 | 1.9914 | 1.7016 | 6.2132 | 6.2091 | 6.2234 | 6.1857 | 6.0898 | 6.0183 | 5.8132 | 5.6622 | 5.5163 | 4.4204 | 3.7632 | 3.5979 | 5.9302 | 5.9118 | 5.9047 | 5.8291 | 5.7118 | 5.5393 | 5.2251 | 4.9791 | 4.7312 | 3.8332 | 3.072 | 2.8026
|  | HOLES BAY PRIMARY | HE |  |  |  |  | 5.2689 | 5.2853 | 5.2944 | 5.2373 | 5.1047 | 4.8985 | 4.572 | 4.2924 | 4.0159 | 3.3424 | 2.87 | 2.622 | 6.2122 | 6.2091 | 6.2224 | 6.1898 | 6.102 | 6.0408 | 5.8612 | 5.7265 | 5.6 | 4.9224 | 4.5428 | 3.9816 | 5.9302 | 5.9138 | 5.9087 | 5.8332 | 5.7189 | 5.5679 | 5.2883 | 5.0659 | 4.8424 | 4.2393 | 3.871 | 3.6332
|  | HOLES BAY PRIMARY | FB |  |  |  |  | 5.3393 | 5.372 | 5.4404 | 5.4914 | 5.5057 | 5.5496 | 5.5496 | 5.52 | 5.5128 | 5.1893 | 4.6444 | 4.1618 | 6.2418 | 6.2591 | 6.3091 | 6.3561 | 6.3653 | 6.3632 | 6.3428 | 6.302 | 6.2836 | 5.9183 | 4.9755 | 2.9265 | 5.9853 | 5.974 | 6.024 | 6.0536 | 6.0577 | 6.074 | 6.0659 | 6.0312 | 6.0128 | 5.7026 | 5.1761 | 4.6271
MELKSHAM GSP | FROME BSP | HOLWELL PRIMARY | MINIMUM HEADROOM | ST 72191 44633 | NO | NO | 0.641 | 3.1913 | 3.2005 | 3.2046 | 3.1342 | 3.1005 | 3.0046 | 2.874 | 2.7128 | 2.5893 | 1.9546 | 1.4628 | 1.1954 | 2.0531 | 2.0469 | 2.0357 | 1.9398 | 1.9082 | 1.8276 | 1.7398 | 1.6704 | 1.6071 | 1.3449 | 1.2051 | 1.1908 | 1.7 | 1.6929 | 1.6816 | 1.4214 | 1.3286 | 1.1459 | 0.97857 | 0.83163 | 0.75306 | 0.18673 | -0.18163 | -0.33878
|  | HOLWELL PRIMARY | EE |  |  |  |  | 3.1913 | 3.2015 | 3.2046 | 3.1342 | 3.1087 | 3.024 | 2.874 | 2.7352 | 2.6117 | 1.9546 | 1.4628 | 1.1954 | 2.0531 | 2.048 | 2.0378 | 1.9398 | 1.9122 | 1.8337 | 1.7398 | 1.6776 | 1.6071 | 1.3449 | 1.2051 | 1.1908 | 1.701 | 1.6949 | 1.6837 | 1.4214 | 1.3357 | 1.1755 | 0.97857 | 0.85816 | 0.75306 | 0.18673 | -0.18163 | -0.33878
|  | HOLWELL PRIMARY | HT |  |  |  |  | 3.1913 | 3.2015 | 3.2066 | 3.1372 | 3.1158 | 3.0321 | 2.9434 | 2.7291 | 2.6689 | 2.0485 | 1.5219 | 1.2505 | 2.0531 | 2.0469 | 2.0357 | 1.9408 | 1.9102 | 1.8286 | 1.7612 | 1.6704 | 1.6194 | 1.3531 | 1.2143 | 1.2245 | 1.7 | 1.6929 | 1.6816 | 1.4224 | 1.3357 | 1.1459 | 1.0367 | 0.83163 | 0.7898 | 0.22653 | -0.15612 | -0.28061
|  | HOLWELL PRIMARY | HE |  |  |  |  | 3.1923 | 3.2005 | 3.2046 | 3.1413 | 3.1005 | 3.0046 | 2.8954 | 2.7128 | 2.5893 | 2.1097 | 1.777 | 1.5291 | 2.0531 | 2.048 | 2.0367 | 1.9602 | 1.9082 | 1.8276 | 1.7561 | 1.6786 | 1.6071 | 1.3939 | 1.3092 | 1.2827 | 1.7031 | 1.6929 | 1.6816 | 1.4827 | 1.3286 | 1.1592 | 1.0153 | 0.85714 | 0.75714 | 0.32449 | 0.13878 | -0.0020408
|  | HOLWELL PRIMARY | FB |  |  |  |  | 3.226 | 3.2505 | 3.276 | 3.274 | 3.2791 | 3.2658 | 3.2689 | 3.2495 | 3.1832 | 2.9821 | 2.5026 | 2.1648 | 2.0796 | 2.0867 | 2.0929 | 2.0847 | 2.0786 | 2.0633 | 2.05 | 2.0449 | 1.9408 | 1.7388 | 1.502 | 1.3663 | 1.7418 | 1.751 | 1.7633 | 1.7541 | 1.75 | 1.7214 | 1.7102 | 1.6684 | 1.402 | 1.05 | 0.61633 | 0.31122
MANNINGTON GSP | SALISBURY BSP | HOMINGTON PRIMARY | MINIMUM HEADROOM | SU 11742 26037 | NO | NO | 0.247 | 8.2117 | 8.2311 | 8.2383 | 8.1413 | 8.0158 | 7.824 | 7.7566 | 7.5403 | 7.3607 | 6.7801 | 6.5495 | 6.5464 | 9.8796 | 9.8571 | 9.8316 | 9.6878 | 9.5031 | 9.2633 | 9.1898 | 8.9531 | 8.7592 | 8.0551 | 7.7398 | 7.5673 | 9.051 | 9.0531 | 9.0459 | 8.9276 | 8.7786 | 8.5684 | 8.5031 | 8.2684 | 8.0857 | 7.4561 | 7.2204 | 7.2296
|  | HOMINGTON PRIMARY | EE |  |  |  |  | 8.2117 | 8.2311 | 8.2434 | 8.2383 | 8.024 | 7.8403 | 7.776 | 7.6189 | 7.4689 | 6.9321 | 6.6791 | 6.6403 | 9.8796 | 9.8582 | 9.8337 | 9.7949 | 9.5102 | 9.2806 | 9.1898 | 9.0071 | 8.8265 | 8.102 | 7.7398 | 7.5673 | 9.051 | 9.0531 | 9.048 | 9.0306 | 8.7827 | 8.5806 | 8.5092 | 8.3398 | 8.1735 | 7.5684 | 7.302 | 7.2816
|  | HOMINGTON PRIMARY | HT |  |  |  |  | 8.2117 | 8.2311 | 8.2383 | 8.1413 | 8.0158 | 7.824 | 7.7566 | 7.5403 | 7.3607 | 6.7801 | 6.5495 | 6.5464 | 9.8796 | 9.8582 | 9.8316 | 9.6878 | 9.5092 | 9.2796 | 9.199 | 8.9531 | 8.7592 | 8.0551 | 7.7857 | 7.7612 | 9.051 | 9.0531 | 9.0459 | 8.9276 | 8.7796 | 8.5735 | 8.5031 | 8.2684 | 8.0857 | 7.4561 | 7.2204 | 7.2296
|  | HOMINGTON PRIMARY | HE |  |  |  |  | 8.2117 | 8.2311 | 8.2434 | 8.1526 | 8.0179 | 7.827 | 7.8015 | 7.5842 | 7.4393 | 7.0372 | 6.8811 | 6.7811 | 9.8796 | 9.8571 | 9.8347 | 9.6949 | 9.5031 | 9.2633 | 9.2276 | 8.9684 | 8.802 | 8.2265 | 7.9888 | 7.7806 | 9.051 | 9.0531 | 9.048 | 8.9357 | 8.7786 | 8.5684 | 8.5398 | 8.3 | 8.1449 | 7.6949 | 7.5357 | 7.4459
|  | HOMINGTON PRIMARY | FB |  |  |  |  | 8.2852 | 8.3362 | 8.376 | 8.3954 | 8.426 | 8.4219 | 8.3954 | 8.373 | 8.3444 | 7.8699 | 7.4036 | 7.1362 | 9.9418 | 9.9418 | 9.9408 | 9.9173 | 9.9082 | 9.8694 | 9.8041 | 9.7459 | 9.6837 | 8.9561 | 8.2459 | 7.6194 | 9.1255 | 9.1582 | 9.1857 | 9.1878 | 9.2071 | 9.1969 | 9.1622 | 9.1316 | 9.0949 | 8.5469 | 8.0622 | 7.7786
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HOOK PRIMARY | MINIMUM HEADROOM | SU 72602 53780 | NO | NO | 6.303 | 12.7698 | 12.8361 | 12.7259 | 12.5718 | 12.3259 | 12.0034 | 11.5932 | 11.1912 | 10.6075 | 8.8728 | 8.0983 | 8.0085 | 16.2198 | 16.2545 | 16.0208 | 15.7759 | 15.3759 | 14.8871 | 14.2279 | 13.6065 | 12.9647 | 10.9871 | 9.8392 | 7.5626 | 13.9749 | 14.0902 | 13.8238 | 13.6096 | 13.2381 | 12.7596 | 12.1136 | 11.5014 | 10.8759 | 9.0626 | 8.3208 | 8.2973
|  | HOOK PRIMARY | EE |  |  |  |  | 12.7698 | 12.8381 | 12.7596 | 12.6555 | 12.4698 | 12.2014 | 11.8851 | 11.5279 | 11.1881 | 9.4749 | 8.5708 | 8.2994 | 16.2198 | 16.2555 | 16.0504 | 15.8463 | 15.5014 | 15.0381 | 14.4749 | 13.8983 | 13.331 | 11.0881 | 9.8392 | 9.0024 | 13.9759 | 14.0922 | 13.8636 | 13.7116 | 13.4116 | 12.981 | 12.4494 | 11.9065 | 11.3698 | 9.5361 | 8.6596 | 8.4289
|  | HOOK PRIMARY | HT |  |  |  |  | 12.7708 | 12.8392 | 12.7259 | 12.5718 | 12.3259 | 12.0034 | 11.5932 | 11.1912 | 10.6075 | 8.8728 | 8.0983 | 8.0085 | 16.2218 | 16.2545 | 16.0208 | 15.7759 | 15.3759 | 14.8871 | 14.2279 | 13.6065 | 12.9647 | 10.9871 | 10.1728 | 10.0422 | 13.9779 | 14.0932 | 13.8238 | 13.6096 | 13.2381 | 12.7596 | 12.1136 | 11.5014 | 10.8759 | 9.0626 | 8.3208 | 8.2973
|  | HOOK PRIMARY | HE |  |  |  |  | 12.7698 | 12.8361 | 12.7596 | 12.6514 | 12.4565 | 12.1871 | 11.8738 | 11.5126 | 11.1687 | 9.8412 | 8.9994 | 8.7443 | 16.2208 | 16.2555 | 16.0483 | 15.8443 | 15.4912 | 15.0228 | 14.482 | 13.8922 | 13.334 | 11.4718 | 10.3096 | 9.4606 | 13.9749 | 14.0902 | 13.8626 | 13.7065 | 13.3963 | 12.9606 | 12.4524 | 11.8973 | 11.3667 | 9.9351 | 9.1392 | 8.9249
|  | HOOK PRIMARY | FB |  |  |  |  | 12.8912 | 12.9851 | 13.0422 | 13.0953 | 13.0902 | 12.983 | 12.8912 | 12.7943 | 12.6606 | 11.7483 | 10.6055 | 9.6371 | 16.3085 | 16.3157 | 16.3075 | 16.3177 | 16.2585 | 15.9473 | 15.6565 | 15.4126 | 15.08 | 12.8912 | 10.2677 | 7.5626 | 14.1932 | 14.2718 | 14.3381 | 14.43 | 14.4045 | 14.2045 | 14.0392 | 13.9085 | 13.6892 | 12.1963 | 10.6208 | 9.6167
LALEHAM GSP | EAST BEDFONT BSP | HOPE AND ANCHOR PRIMARY | MINIMUM HEADROOM | TQ 12710 72057 | YES | NO | 0.315 | -1.5735 | -1.548 | -1.5378 | -1.55 | -1.6143 | -1.7296 | -1.8878 | -2.0194 | -2.1765 | -2.7276 | -3.2255 | -3.5133 | -0.80204 | -0.86429 | -0.93571 | -1.0265 | -1.1582 | -1.3347 | -1.5071 | -1.7 | -1.8827 | -3.1439 | -5.5898 | -9.3786 | -1.2316 | -1.2153 | -1.2204 | -1.2439 | -1.3622 | -1.5184 | -1.6633 | -1.7786 | -1.9224 | -2.402 | -2.898 | -3.1459
|  | HOPE AND ANCHOR PRIMARY | EE |  |  |  |  | -1.5735 | -1.548 | -1.5378 | -1.55 | -1.6143 | -1.6816 | -1.8122 | -1.9633 | -2.0673 | -2.6541 | -3.2255 | -3.5133 | -0.74898 | -0.77347 | -0.80816 | -0.86429 | -1.0194 | -1.1388 | -1.3 | -1.4694 | -1.5796 | -2.6439 | -3.8449 | -5.3663 | -1.2316 | -1.2153 | -1.2204 | -1.2439 | -1.3622 | -1.451 | -1.5949 | -1.7378 | -1.8235 | -2.3867 | -2.898 | -3.1459
|  | HOPE AND ANCHOR PRIMARY | HT |  |  |  |  | -1.5663 | -1.5347 | -1.5204 | -1.5388 | -1.5582 | -1.7296 | -1.8878 | -2.0194 | -2.1765 | -2.7276 | -3.1969 | -3.3265 | -0.7449 | -0.77347 | -0.80306 | -0.85918 | -0.92143 | -1.2092 | -1.3663 | -1.502 | -1.6612 | -2.1612 | -2.6622 | -3.0173 | -1.2245 | -1.2061 | -1.2031 | -1.2265 | -1.2561 | -1.5184 | -1.6633 | -1.7786 | -1.9224 | -2.402 | -2.7959 | -2.8714
|  | HOPE AND ANCHOR PRIMARY | HE |  |  |  |  | -1.5694 | -1.5408 | -1.5306 | -1.55 | -1.552 | -1.6388 | -1.7765 | -1.8745 | -2.0439 | -2.352 | -2.6796 | -2.8939 | -0.74592 | -0.77245 | -0.80714 | -0.86122 | -0.90612 | -1.0878 | -1.2827 | -1.4082 | -1.5673 | -2.4857 | -3.5857 | -5.1061 | -1.2265 | -1.2122 | -1.2122 | -1.2347 | -1.251 | -1.3898 | -1.5653 | -1.6571 | -1.7857 | -2.0969 | -2.3755 | -2.551
|  | HOPE AND ANCHOR PRIMARY | FB |  |  |  |  | -1.5327 | -1.4939 | -1.4643 | -1.449 | -1.4367 | -1.4367 | -1.4347 | -1.451 | -1.4582 | -1.5469 | -1.9776 | -2.4796 | -0.80204 | -0.86429 | -0.93571 | -1.0265 | -1.1582 | -1.3347 | -1.5071 | -1.7 | -1.8827 | -3.1439 | -5.5898 | -9.3786 | -1.1918 | -1.1582 | -1.1367 | -1.1235 | -1.1173 | -1.1316 | -1.1347 | -1.1571 | -1.1714 | -1.2724 | -1.6663 | -2.2592
LOVEDEAN GSP | HAVANT BSP | HORNDEAN PRIMARY | MINIMUM HEADROOM | SU 70271 12802 | NO | YES | 13.016 | 1.2693 | 1.2397 | 0.79585 | 0.403 | 28.1948 | 27.3234 | 26.2367 | 25.0805 | 24.0367 | 21.3754 | 19.9734 | 19.6775 | 5.402 | 5.2489 | 4.7183 | 4.2571 | 30.3387 | 29.4438 | 28.3203 | 27.1336 | 26.0561 | 22.9561 | 19.004 | 12.1856 | 3.6173 | 3.4754 | 2.9224 | 2.4397 | 29.3693 | 28.452 | 27.3091 | 26.1081 | 25.0418 | 21.9918 | 20.5693 | 20.4193
|  | HORNDEAN PRIMARY | EE |  |  |  |  | 1.2714 | 1.2642 | 0.95504 | 0.76932 | 28.8173 | 28.2214 | 27.4265 | 26.553 | 25.805 | 23.1703 | 21.4744 | 20.8193 | 5.4091 | 5.2632 | 4.803 | 4.4673 | 30.6979 | 29.9387 | 28.9918 | 27.9642 | 27.0581 | 23.0887 | 20.2448 | 17.7203 | 3.6214 | 3.4928 | 3.0408 | 2.7183 | 29.8408 | 29.1101 | 28.1887 | 27.1999 | 26.3581 | 23.2499 | 21.5336 | 20.9663
|  | HORNDEAN PRIMARY | HT |  |  |  |  | 1.2693 | 1.2397 | 0.79585 | 0.403 | 28.1948 | 27.3234 | 26.2367 | 25.0805 | 24.0367 | 21.3754 | 19.9734 | 19.6775 | 5.402 | 5.2489 | 4.7183 | 4.2571 | 30.3387 | 29.4438 | 28.3203 | 27.1336 | 26.0561 | 22.9561 | 21.4316 | 21.0285 | 3.6193 | 3.4754 | 2.9224 | 2.4397 | 29.3693 | 28.452 | 27.3091 | 26.1081 | 25.0418 | 21.9918 | 20.5693 | 20.4193
|  | HORNDEAN PRIMARY | HE |  |  |  |  | 1.2693 | 1.2601 | 0.94993 | 0.7632 | 28.803 | 28.204 | 27.4142 | 26.5652 | 25.7908 | 23.3846 | 21.8244 | 21.0928 | 5.4061 | 5.2601 | 4.7979 | 4.4601 | 30.6836 | 29.9214 | 28.9703 | 27.9714 | 27.0346 | 23.2254 | 20.4765 | 17.7254 | 3.6173 | 3.4897 | 3.0356 | 2.7091 | 29.8254 | 29.0918 | 28.1693 | 27.2163 | 26.3418 | 23.4693 | 21.9652 | 21.304
|  | HORNDEAN PRIMARY | FB |  |  |  |  | 1.6163 | 1.8652 | 1.8805 | 2.0173 | 30.452 | 30.3571 | 30.0479 | 29.7724 | 29.5316 | 27.702 | 24.903 | 23.4795 | 5.5877 | 5.6254 | 5.4305 | 5.3305 | 31.8152 | 31.3805 | 30.6805 | 30.051 | 29.453 | 25.1918 | 19.004 | 12.1856 | 3.952 | 4.0816 | 4.0142 | 4.0428 | 31.6254 | 31.4561 | 31.003 | 30.6346 | 30.3173 | 27.9224 | 24.9663 | 23.4693
NURSLING GSP | WINCHESTER BSP | HOUGHTON PRIMARY | MINIMUM HEADROOM | SU 33784 31741 | NO | NO | 1.058 | 8.8337 | 8.8102 | 8.6745 | 8.451 | 8.2265 | 7.9418 | 6.9949 | 4.6622 | 3.9571 | 0.62245 | -6.0918 | -11.0092 | 11.2429 | 11.1949 | 10.9224 | 10.7633 | 10.5837 | 10.3745 | 9.2918 | 6.4765 | 5.2418 | 1.0347 | -6.7327 | -12.2122 | 9.1867 | 9.1571 | 9.0429 | 8.9031 | 8.75 | 8.551 | 7.5173 | 4.7388 | 3.7184 | -0.29898 | -8.2939 | -13.9622
|  | HOUGHTON PRIMARY | EE |  |  |  |  | 8.8337 | 8.8439 | 8.6745 | 8.4633 | 8.2408 | 8.0082 | 7.5184 | 6.7694 | 5.5214 | 2.6898 | -4.3796 | -7.0867 | 11.2449 | 11.2265 | 10.9235 | 10.7663 | 10.5908 | 10.401 | 9.8459 | 8.95 | 7.451 | 3.9378 | -4.6031 | -7.748 | 9.1878 | 9.198 | 9.0429 | 8.9092 | 8.7541 | 8.5847 | 8.1041 | 7.2755 | 5.8306 | 2.5173 | -6.048 | -9.1357
|  | HOUGHTON PRIMARY | HT |  |  |  |  | 8.8357 | 8.8102 | 8.6969 | 8.5122 | 8.3204 | 8.1204 | 7.2378 | 6.2867 | 3.9571 | 0.62245 | -6.0918 | -11.0092 | 11.2429 | 11.1949 | 10.9245 | 10.7673 | 10.5837 | 10.3745 | 9.2918 | 8.1296 | 5.2418 | 1.0347 | -6.7327 | -12.2122 | 9.1867 | 9.1571 | 9.0531 | 8.9347 | 8.7908 | 8.6357 | 7.6286 | 6.5398 | 3.7184 | -0.29898 | -8.2939 | -13.9622
|  | HOUGHTON PRIMARY | HE |  |  |  |  | 8.8347 | 8.849 | 8.6806 | 8.451 | 8.2265 | 7.9418 | 6.9949 | 4.6622 | 4.3969 | 0.72653 | -4.2347 | -10.4143 | 11.2449 | 11.2265 | 10.9224 | 10.7633 | 10.6245 | 10.3847 | 9.3133 | 6.4765 | 6.2653 | 1.4673 | -4.2163 | -11.7684 | 9.1888 | 9.199 | 9.0449 | 8.9031 | 8.75 | 8.551 | 7.5173 | 4.7388 | 4.5408 | 0.067347 | -5.698 | -13.1837
|  | HOUGHTON PRIMARY | FB |  |  |  |  | 8.9071 | 8.9469 | 8.9133 | 8.8204 | 8.7714 | 8.6551 | 8.4245 | 8.1378 | 7.4337 | 5.2571 | 2.3755 | -0.28061 | 11.3184 | 11.3204 | 11.2837 | 11.2163 | 11.1724 | 10.8908 | 10.5327 | 10.1653 | 9.2459 | 6.299 | 2.4173 | -1.549 | 9.25 | 9.2837 | 9.2602 | 9.1765 | 9.1592 | 9.0735 | 8.8051 | 8.4633 | 7.6071 | 5.1082 | 1.7235 | -1.6643
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | HOUNDMILLS PRIMARY | MINIMUM HEADROOM | SU 62187 52886 | NO | NO | 27.767 | 1.0261 | 0.90673 | 0.7751 | 0.39653 | -0.28714 | -1.0769 | -2.0004 | -3.1096 | -4.0729 | -8.7147 | -10.7973 | -11.6382 | 1.0833 | 0.99449 | 0.92204 | 0.79041 | 0.43531 | -0.042245 | -0.63408 | -1.4208 | -1.9831 | -4.6994 | -6.0453 | -7.3984 | 0.91694 | 0.80163 | 0.70571 | 0.48735 | -0.060612 | -0.72898 | -1.4739 | -2.3565 | -3.0851 | -6.6861 | -8.3116 | -8.9137
|  | HOUNDMILLS PRIMARY | EE |  |  |  |  | 1.0261 | 0.90673 | 0.7751 | 0.39959 | -0.22388 | -1.0198 | -1.9994 | -3.0739 | -4.0178 | -8.7147 | -10.7973 | -11.6382 | 1.0863 | 1.0016 | 0.92612 | 0.80571 | 0.54551 | 0.066939 | -0.52286 | -1.3106 | -1.8831 | -4.6994 | -6.0453 | -6.8433 | 0.91694 | 0.80163 | 0.70571 | 0.49347 | 0.02102 | -0.64837 | -1.4269 | -2.3218 | -3.0494 | -6.6851 | -8.3116 | -8.9137
|  | HOUNDMILLS PRIMARY | HT |  |  |  |  | 1.0312 | 0.92 | 0.78939 | 0.39755 | -0.28714 | -1.0769 | -1.9831 | -3.0392 | -3.9565 | -8.6871 | -10.6851 | -11.2973 | 1.0863 | 1.0016 | 0.92612 | 0.79041 | 0.43531 | -0.042245 | -0.63408 | -1.4208 | -1.9831 | -4.5106 | -5.4984 | -5.6994 | 0.92 | 0.8098 | 0.72102 | 0.48735 | -0.060612 | -0.72898 | -1.4739 | -2.3565 | -3.0678 | -6.6861 | -8.2004 | -8.5616
|  | HOUNDMILLS PRIMARY | HE |  |  |  |  | 1.0312 | 0.91184 | 0.78633 | 0.39653 | -0.2402 | -1.0331 | -2.0004 | -3.1096 | -4.0729 | -8.3412 | -9.6361 | -10.1667 | 1.0833 | 0.99449 | 0.92204 | 0.79653 | 0.52816 | 0.059796 | -0.53 | -1.3392 | -1.9024 | -4.528 | -5.4178 | -6.1555 | 0.92102 | 0.80469 | 0.72 | 0.49347 | 0.0097959 | -0.65347 | -1.43 | -2.3514 | -3.0851 | -6.378 | -7.3463 | -7.732
|  | HOUNDMILLS PRIMARY | FB |  |  |  |  | 1.119 | 1.0924 | 1.0771 | 0.80469 | 0.38531 | -0.050408 | -0.5249 | -1.0341 | -1.5678 | -5.0769 | -6.8341 | -8.0494 | 1.1343 | 1.1057 | 1.0843 | 0.94653 | 0.76184 | 0.55367 | 0.25367 | -0.16878 | -0.6249 | -3.1698 | -5.2096 | -7.3984 | 1.0149 | 1.0129 | 1.0078 | 0.80776 | 0.49143 | 0.16286 | -0.20245 | -0.60653 | -1.0198 | -3.6953 | -5.3729 | -6.4922
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | HUNGERFORD PRIMARY | MINIMUM HEADROOM | SU 34066 68957 | NO | NO | 1.799 | 5.9551 | 5.9735 | 5.8939 | 5.7765 | 5.649 | 5.3602 | 5.0602 | 4.7367 | 4.4235 | 3.2551 | 2.3194 | 1.7265 | 7.1755 | 7.1755 | 7.0602 | 6.9704 | 6.9296 | 6.751 | 6.5602 | 6.3469 | 6.1643 | 5.0643 | 4.3061 | 3.201 | 6.1857 | 6.2082 | 6.0806 | 5.9929 | 5.9388 | 5.6949 | 5.449 | 5.1704 | 4.8918 | 3.6255 | 2.8418 | 2.4959
|  | HUNGERFORD PRIMARY | EE |  |  |  |  | 5.9571 | 5.9755 | 5.9051 | 5.8 | 5.6847 | 5.3959 | 5.0847 | 4.7704 | 4.4643 | 3.3888 | 2.4459 | 1.8571 | 7.1765 | 7.1776 | 7.0684 | 6.9939 | 6.9724 | 6.8112 | 6.6143 | 6.4265 | 6.2622 | 5.0643 | 4.3061 | 3.7714 | 6.1867 | 6.2092 | 6.0918 | 6.0031 | 5.9857 | 5.7531 | 5.4908 | 5.2347 | 4.9888 | 3.7173 | 2.9082 | 2.5173
|  | HUNGERFORD PRIMARY | HT |  |  |  |  | 5.9571 | 5.9735 | 5.8939 | 5.7765 | 5.649 | 5.3602 | 5.0602 | 4.7367 | 4.4235 | 3.2551 | 2.3194 | 1.7265 | 7.1755 | 7.1765 | 7.0602 | 6.9704 | 6.9296 | 6.751 | 6.5602 | 6.3469 | 6.1643 | 5.1408 | 4.6031 | 4.4429 | 6.1878 | 6.2082 | 6.0806 | 5.9929 | 5.9388 | 5.6949 | 5.449 | 5.1704 | 4.8918 | 3.6255 | 2.8418 | 2.4959
|  | HUNGERFORD PRIMARY | HE |  |  |  |  | 5.9551 | 5.9735 | 5.9031 | 5.7898 | 5.6684 | 5.3796 | 5.0765 | 4.751 | 4.449 | 3.55 | 2.8571 | 2.5276 | 7.1755 | 7.1755 | 7.0673 | 6.9929 | 6.9633 | 6.8041 | 6.6184 | 6.4194 | 6.2684 | 5.1939 | 4.6867 | 4.2153 | 6.1857 | 6.2082 | 6.0898 | 5.9959 | 5.9694 | 5.7398 | 5.4929 | 5.2235 | 4.9888 | 3.9143 | 3.3602 | 3.0908
|  | HUNGERFORD PRIMARY | FB |  |  |  |  | 6.0122 | 6.0541 | 6.0765 | 6.0745 | 6.0898 | 6.049 | 5.9367 | 5.8837 | 5.8173 | 5.2531 | 4.6082 | 4.1867 | 7.2153 | 7.2214 | 7.2061 | 7.1898 | 7.1663 | 7.0898 | 6.9071 | 6.8408 | 6.7439 | 5.8949 | 4.6163 | 3.201 | 6.2694 | 6.3173 | 6.3449 | 6.3633 | 6.3673 | 6.3378 | 6.2296 | 6.2112 | 6.1602 | 5.5878 | 4.7214 | 4.0429
LOVEDEAN GSP | CHICHESTER BSP | HUNSTON PRIMARY | MINIMUM HEADROOM | SU 86949 02632 | NO | YES | 12.714 | 8.7059 | 8.6212 | 8.5416 | 8.4008 | 8.1232 | 7.7212 | 7.2732 | 6.8222 | 6.3763 | 3.7232 | 2.161 | 1.3651 | 12.5957 | 12.4651 | 12.3304 | 12.1753 | 11.909 | 11.5579 | 11.111 | 10.6967 | 10.2875 | 8.0794 | 6.7069 | 5.4018 | 10.4824 | 10.3753 | 10.2702 | 10.1202 | 9.8334 | 9.4732 | 9.0498 | 8.6324 | 8.2202 | 5.9498 | 4.4855 | 3.9151
|  | HUNSTON PRIMARY | EE |  |  |  |  | 8.71 | 8.713 | 8.61 | 8.512 | 8.3416 | 7.9926 | 7.5722 | 7.0712 | 6.5794 | 3.9936 | 2.559 | 1.8753 | 12.5988 | 12.5518 | 12.3834 | 12.2763 | 12.1079 | 11.8151 | 11.4212 | 11.0753 | 10.711 | 8.2528 | 6.7069 | 6.0028 | 10.4834 | 10.4508 | 10.2967 | 10.1896 | 9.9977 | 9.6732 | 9.2824 | 8.9059 | 8.5334 | 6.4151 | 4.9712 | 4.4365
|  | HUNSTON PRIMARY | HT |  |  |  |  | 8.7059 | 8.6212 | 8.5416 | 8.4008 | 8.1232 | 7.7212 | 7.2732 | 6.8222 | 6.3763 | 3.7232 | 2.161 | 1.3651 | 12.5957 | 12.4651 | 12.3304 | 12.1753 | 11.909 | 11.5579 | 11.111 | 10.6967 | 10.2875 | 8.0794 | 6.9039 | 6.5671 | 10.4824 | 10.3753 | 10.2702 | 10.1202 | 9.8334 | 9.4732 | 9.0498 | 8.6324 | 8.2202 | 5.9498 | 4.4855 | 3.9151
|  | HUNSTON PRIMARY | HE |  |  |  |  | 8.711 | 8.713 | 8.611 | 8.4988 | 8.3171 | 7.9722 | 7.5763 | 7.1059 | 6.6192 | 4.4579 | 3.363 | 2.7947 | 12.5977 | 12.5467 | 12.3804 | 12.2681 | 12.1059 | 11.7936 | 11.4018 | 11.0763 | 10.7059 | 8.6732 | 7.6385 | 6.861 | 10.4834 | 10.4559 | 10.3039 | 10.1855 | 9.9824 | 9.66 | 9.2763 | 8.913 | 8.5457 | 6.712 | 5.9488 | 5.5794
|  | HUNSTON PRIMARY | FB |  |  |  |  | 8.8171 | 8.8804 | 8.8671 | 8.7988 | 8.762 | 8.6855 | 8.6171 | 8.4906 | 8.3651 | 7.4896 | 5.7079 | 4.9232 | 12.6763 | 12.6896 | 12.5926 | 12.4814 | 12.3753 | 12.2059 | 12.0926 | 11.8702 | 11.6549 | 10.1702 | 7.5692 | 5.4018 | 10.6008 | 10.6365 | 10.5732 | 10.4865 | 10.4171 | 10.3447 | 10.2641 | 10.1202 | 9.9875 | 9.0243 | 7.3773 | 6.7365
MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT PRIMARY | MINIMUM HEADROOM | SU 39384 52476 | NO | NO | 1.804 | 2.2048 | 2.2324 | 2.2518 | 2.2313 | 2.1987 | 2.2058 | 2.1028 | 1.9844 | 1.864 | 1.512 | 1.3518 | 1.266 | 3.162 | 3.1487 | 3.1252 | 3.0875 | 3.0293 | 3.0303 | 2.9262 | 2.814 | 2.712 | 2.4211 | 2.2262 | 1.8222 | 2.7518 | 2.7558 | 2.7497 | 2.7181 | 2.6681 | 2.666 | 2.5609 | 2.466 | 2.363 | 2.0273 | 1.8824 | 1.8671
|  | HURSTBOURNE TARRANT PRIMARY | EE |  |  |  |  | 2.2048 | 2.2324 | 2.2538 | 2.2426 | 2.2171 | 2.2334 | 2.1283 | 2.0109 | 1.8793 | 1.512 | 1.3722 | 1.3742 | 3.162 | 3.1487 | 3.1252 | 3.0916 | 3.0375 | 3.0436 | 2.9436 | 2.8273 | 2.7252 | 2.4242 | 2.2732 | 2.1824 | 2.7518 | 2.7558 | 2.7497 | 2.7232 | 2.6803 | 2.6854 | 2.5813 | 2.4803 | 2.3793 | 2.0273 | 1.9109 | 1.9691
|  | HURSTBOURNE TARRANT PRIMARY | HT |  |  |  |  | 2.2048 | 2.2354 | 2.2518 | 2.2313 | 2.1987 | 2.2058 | 2.1028 | 1.9905 | 1.8783 | 1.5313 | 1.3875 | 1.3813 | 3.163 | 3.1518 | 3.1283 | 3.0875 | 3.0293 | 3.0303 | 2.9262 | 2.814 | 2.712 | 2.4354 | 2.362 | 2.4252 | 2.7518 | 2.7589 | 2.7497 | 2.7181 | 2.6681 | 2.666 | 2.5609 | 2.466 | 2.365 | 2.0293 | 1.9181 | 2.0089
|  | HURSTBOURNE TARRANT PRIMARY | HE |  |  |  |  | 2.2058 | 2.2344 | 2.2558 | 2.2405 | 2.212 | 2.2211 | 2.1099 | 1.9844 | 1.864 | 1.5324 | 1.3518 | 1.266 | 3.164 | 3.1487 | 3.1293 | 3.0926 | 3.0395 | 3.0436 | 2.9405 | 2.8232 | 2.7232 | 2.4211 | 2.2344 | 2.0813 | 2.7518 | 2.7569 | 2.7538 | 2.7242 | 2.6783 | 2.6793 | 2.5701 | 2.466 | 2.363 | 2.0395 | 1.8824 | 1.8671
|  | HURSTBOURNE TARRANT PRIMARY | FB |  |  |  |  | 2.2762 | 2.3283 | 2.3752 | 2.4079 | 2.4201 | 2.4273 | 2.4211 | 2.3926 | 2.362 | 2.1813 | 1.8324 | 1.7579 | 3.2344 | 3.2324 | 3.2354 | 3.2375 | 3.212 | 3.1824 | 3.1364 | 3.0793 | 3.0211 | 2.7089 | 2.2262 | 1.8222 | 2.8313 | 2.8548 | 2.8783 | 2.8977 | 2.8895 | 2.8742 | 2.8467 | 2.8089 | 2.763 | 2.5742 | 2.2722 | 2.1875
EALING GSP |  | IRONBRIDGE PRIMARY | MINIMUM HEADROOM | TQ 14226 80171 | NO | NO | 15.775 | 6.3598 | 6.1771 | 5.8343 | 5.3588 | 4.8077 | 4.0363 | 2.8353 | 1.5965 | 0.36386 | -4.5963 | -7.6923 | -8.9872 | 8.5547 | 8.3965 | 8.0914 | 7.7128 | 7.1924 | 6.5904 | 5.7108 | 4.7567 | 3.8628 | 0.43324 | -3.8443 | -11.0974 | 6.0292 | 5.8516 | 5.5812 | 5.1741 | 4.622 | 3.9292 | 2.8649 | 1.7383 | 0.66692 | -3.6239 | -6.2249 | -7.6637
|  | IRONBRIDGE PRIMARY | EE |  |  |  |  | 6.3598 | 6.1771 | 5.8343 | 5.3588 | 4.9669 | 4.1496 | 3.1159 | 2.023 | 1.0598 | -3.7606 | -7.2943 | -8.9872 | 8.5547 | 8.3965 | 8.0914 | 7.7128 | 7.3516 | 6.7353 | 5.9771 | 5.1292 | 4.4057 | 0.43324 | -2.6861 | -5.6994 | 6.0292 | 5.8516 | 5.5812 | 5.1741 | 4.7822 | 4.0577 | 3.1516 | 2.1567 | 1.3159 | -3.131 | -6.2249 | -7.6637
|  | IRONBRIDGE PRIMARY | HT |  |  |  |  | 6.3832 | 6.2312 | 5.9098 | 5.42 | 4.8077 | 4.0363 | 2.8353 | 1.5965 | 0.36386 | -4.5963 | -7.6923 | -8.9657 | 8.5618 | 8.3996 | 8.0986 | 7.723 | 7.1924 | 6.5904 | 5.7108 | 4.7567 | 3.8628 | 1.1098 | -0.46676 | -1.3106 | 6.0618 | 5.9149 | 5.6679 | 5.2302 | 4.622 | 3.9292 | 2.8649 | 1.7383 | 0.66692 | -3.6239 | -6.1882 | -7.1321
|  | IRONBRIDGE PRIMARY | HE |  |  |  |  | 6.3792 | 6.2179 | 5.8914 | 5.4006 | 4.9975 | 4.2843 | 3.2669 | 2.2608 | 1.1934 | -2.0453 | -4.5392 | -5.8912 | 8.5608 | 8.4067 | 8.1057 | 7.7322 | 7.3751 | 6.8047 | 6.023 | 5.2057 | 4.369 | 1.1169 | -1.7382 | -4.6739 | 6.0455 | 5.8873 | 5.6343 | 5.2169 | 4.8149 | 4.1771 | 3.271 | 2.3404 | 1.3598 | -1.5637 | -3.7474 | -4.8617
|  | IRONBRIDGE PRIMARY | FB |  |  |  |  | 6.67 | 6.622 | 6.5118 | 6.2639 | 6.172 | 5.9526 | 5.5618 | 5.2037 | 4.8353 | 2.8088 | -0.19533 | -2.6719 | 8.82 | 8.6445 | 8.4067 | 8.0445 | 7.7434 | 7.2843 | 6.7088 | 6.1057 | 5.5016 | 1.77 | -3.8443 | -11.0974 | 6.2741 | 6.2251 | 6.1159 | 5.8843 | 5.7649 | 5.6037 | 5.2934 | 5.0077 | 4.6863 | 2.5934 | -0.28614 | -2.6984
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | JAYS CLOSE PRIMARY | MINIMUM HEADROOM | SU 63055 50105 | NO | NO | 17.37 | 8.5907 | 8.5377 | 8.5611 | 8.307 | 7.9877 | 7.3499 | 6.7519 | 6.054 | 5.3152 | 2.3489 | 0.25909 | -0.83785 | 10.7683 | 10.6856 | 10.6438 | 10.4183 | 10.1315 | 9.7275 | 9.2264 | 8.603 | 7.9315 | 5.8366 | 4.3254 | 1.004 | 8.3275 | 8.1836 | 8.1724 | 7.957 | 7.6448 | 7.157 | 6.6815 | 6.0642 | 5.4111 | 2.8877 | 1.204 | 0.39072
|  | JAYS CLOSE PRIMARY | EE |  |  |  |  | 8.5907 | 8.5377 | 8.5611 | 8.3468 | 8.0775 | 7.5152 | 6.8458 | 6.1315 | 5.3877 | 2.3489 | 0.25909 | -0.83785 | 10.7703 | 10.6856 | 10.654 | 10.455 | 10.204 | 9.7652 | 9.2448 | 8.6264 | 7.9734 | 5.8366 | 4.3254 | 3.0672 | 8.3275 | 8.1836 | 8.1724 | 7.9917 | 7.7336 | 7.2703 | 6.7448 | 6.1285 | 5.4744 | 2.8877 | 1.204 | 0.39072
|  | JAYS CLOSE PRIMARY | HT |  |  |  |  | 8.6009 | 8.5632 | 8.5785 | 8.307 | 7.9877 | 7.3499 | 6.7519 | 6.054 | 5.3152 | 2.3703 | 0.49378 | -0.32459 | 10.7713 | 10.6877 | 10.6438 | 10.4183 | 10.1315 | 9.7275 | 9.2264 | 8.607 | 7.9407 | 6.0428 | 5.4152 | 5.1938 | 8.3377 | 8.2081 | 8.2019 | 7.957 | 7.6448 | 7.157 | 6.6815 | 6.0642 | 5.4111 | 2.9417 | 1.4856 | 0.98868
|  | JAYS CLOSE PRIMARY | HE |  |  |  |  | 8.5958 | 8.556 | 8.5846 | 8.355 | 8.0734 | 7.5866 | 6.9601 | 6.2479 | 5.5152 | 3.2601 | 1.604 | 0.90807 | 10.7683 | 10.6856 | 10.6509 | 10.454 | 10.1989 | 9.7693 | 9.2499 | 8.603 | 7.9315 | 6.1897 | 4.706 | 3.5866 | 8.3356 | 8.2009 | 8.1948 | 8.007 | 7.7377 | 7.3142 | 6.8183 | 6.1938 | 5.5438 | 3.6315 | 2.2938 | 1.8111
|  | JAYS CLOSE PRIMARY | FB |  |  |  |  | 8.7346 | 8.8489 | 8.9305 | 8.9407 | 8.8785 | 8.7815 | 8.6683 | 8.5193 | 8.3693 | 7.1193 | 4.9999 | 3.4499 | 10.8499 | 10.8662 | 10.8621 | 10.8193 | 10.7162 | 10.5183 | 10.2489 | 9.9315 | 9.6315 | 7.5468 | 4.4744 | 1.004 | 8.5234 | 8.6244 | 8.705 | 8.7346 | 8.6928 | 8.5775 | 8.4407 | 8.2489 | 8.0785 | 6.7407 | 4.7621 | 3.3091
MINETY GSP | CIRENCESTER BSP | KEMBLE RAF PRIMARY | MINIMUM HEADROOM | ST 96064 96012 | YES | NO | 0.707 | 9.7643 | 9.7602 | 9.7592 | 9.7092 | 9.6602 | 9.6255 | 9.599 | 9.5684 | 9.5265 | 9.2296 | 8.95 | 8.8429 | 9.1612 | 9.1592 | 9.1592 | 9.1133 | 9.0612 | 8.948 | 8.8898 | 8.7918 | 8.6602 | 8.251 | 7.9765 | 7.8663 | 9.6194 | 9.6194 | 9.6184 | 9.5602 | 9.5031 | 9.4622 | 9.4388 | 9.4031 | 9.2888 | 8.8857 | 8.6133 | 8.5102
|  | KEMBLE RAF PRIMARY | EE |  |  |  |  | 9.7643 | 9.7602 | 9.7592 | 9.7092 | 9.6684 | 9.6255 | 9.602 | 9.5724 | 9.5265 | 9.2296 | 8.95 | 8.8429 | 9.1612 | 9.1612 | 9.1592 | 9.1133 | 9.0704 | 8.9561 | 8.899 | 8.8143 | 8.6755 | 8.251 | 7.9765 | 7.8663 | 9.6194 | 9.6194 | 9.6184 | 9.5602 | 9.5122 | 9.4643 | 9.4408 | 9.4071 | 9.301 | 8.8857 | 8.6133 | 8.5102
|  | KEMBLE RAF PRIMARY | HT |  |  |  |  | 9.7643 | 9.7602 | 9.7592 | 9.7112 | 9.6602 | 9.6418 | 9.6041 | 9.5684 | 9.5276 | 9.251 | 8.9816 | 8.9133 | 9.1612 | 9.1602 | 9.1592 | 9.1153 | 9.0612 | 9.0143 | 8.902 | 8.7918 | 8.6602 | 8.2745 | 8.0102 | 7.9459 | 9.6194 | 9.6194 | 9.6194 | 9.5612 | 9.5031 | 9.4827 | 9.4429 | 9.4031 | 9.2888 | 8.9122 | 8.65 | 8.5847
|  | KEMBLE RAF PRIMARY | HE |  |  |  |  | 9.7643 | 9.7602 | 9.7592 | 9.7102 | 9.6684 | 9.6255 | 9.599 | 9.5745 | 9.5337 | 9.3745 | 9.3612 | 9.2939 | 9.1612 | 9.1602 | 9.1592 | 9.1143 | 9.0724 | 8.948 | 8.8898 | 8.8194 | 8.6918 | 8.4041 | 8.4061 | 8.3398 | 9.6194 | 9.6194 | 9.6194 | 9.5602 | 9.5133 | 9.4622 | 9.4388 | 9.4102 | 9.3184 | 9.0439 | 9.0429 | 8.9837
|  | KEMBLE RAF PRIMARY | FB |  |  |  |  | 9.7673 | 9.7633 | 9.7633 | 9.7592 | 9.7571 | 9.751 | 9.749 | 9.6888 | 9.6806 | 9.5796 | 9.5194 | 9.3296 | 9.1653 | 9.1592 | 9.1592 | 9.1592 | 9.1551 | 9.1531 | 9.151 | 9.0898 | 9.0816 | 8.8265 | 8.6429 | 8.3327 | 9.6276 | 9.6194 | 9.6184 | 9.6184 | 9.6153 | 9.6112 | 9.6102 | 9.5378 | 9.5286 | 9.4153 | 9.2765 | 8.9816
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | KENNINGTON PRIMARY | MINIMUM HEADROOM | SP 52881 01094 | YES | NO | 0.508 | 3.564 | 3.5538 | 3.5304 | 3.4304 | 3.3202 | 2.9191 | 2.5426 | 2.112 | 1.7171 | 0.51709 | -0.51352 | -1.1064 | 4.5515 | 4.524 | 4.4842 | 4.4209 | 4.2556 | 4.0934 | 3.8597 | 3.6128 | 3.4311 | 2.6515 | 2.0964 | 0.99745 | 4.051 | 4.0327 | 3.9949 | 3.9235 | 3.7367 | 3.4571 | 3.1633 | 2.8184 | 2.5296 | 1.5786 | 0.87347 | 0.56633
|  | KENNINGTON PRIMARY | EE |  |  |  |  | 3.5783 | 3.5538 | 3.5406 | 3.4446 | 3.3559 | 2.961 | 2.5916 | 2.1569 | 1.7753 | 0.51709 | -0.45026 | -0.98495 | 4.5689 | 4.5403 | 4.4985 | 4.4352 | 4.374 | 4.127 | 3.9291 | 3.677 | 3.4801 | 2.6515 | 2.0964 | 1.6944 | 4.0653 | 4.0388 | 3.9969 | 3.9327 | 3.8306 | 3.4847 | 3.1939 | 2.8316 | 2.551 | 1.5786 | 0.90918 | 0.5949
|  | KENNINGTON PRIMARY | HT |  |  |  |  | 3.564 | 3.5569 | 3.5304 | 3.4732 | 3.3293 | 3.0365 | 2.6895 | 2.3018 | 1.9538 | 0.58342 | -0.51352 | -1.1064 | 4.5515 | 4.524 | 4.4842 | 4.4209 | 4.2556 | 4.0934 | 3.8597 | 3.6128 | 3.4311 | 2.6974 | 2.3026 | 2.1903 | 4.051 | 4.0327 | 3.9949 | 3.9235 | 3.7367 | 3.5061 | 3.201 | 2.8806 | 2.6173 | 1.5857 | 0.87347 | 0.56633
|  | KENNINGTON PRIMARY | HE |  |  |  |  | 3.5793 | 3.5569 | 3.5446 | 3.4304 | 3.3202 | 2.9191 | 2.5426 | 2.112 | 1.7171 | 0.6926 | -0.11454 | -0.53699 | 4.5679 | 4.5393 | 4.4985 | 4.4321 | 4.3668 | 4.1189 | 3.9199 | 3.6862 | 3.4903 | 2.7485 | 2.3046 | 1.8607 | 4.0653 | 4.0388 | 4 | 3.9245 | 3.8092 | 3.4571 | 3.1633 | 2.8184 | 2.5296 | 1.7235 | 1.2031 | 0.92959
|  | KENNINGTON PRIMARY | FB |  |  |  |  | 3.6987 | 3.7263 | 3.7324 | 3.7375 | 3.7497 | 3.7059 | 3.6508 | 3.6559 | 3.5946 | 2.9569 | 2.2467 | 1.811 | 4.6383 | 4.626 | 4.5903 | 4.5689 | 4.5342 | 4.4474 | 4.3454 | 4.3128 | 4.2066 | 3.277 | 2.1974 | 0.99745 | 4.1816 | 4.199 | 4.1949 | 4.1969 | 4.1878 | 4.1429 | 4.1 | 4.1092 | 4.0459 | 3.3102 | 2.6714 | 2.2755
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | KENTWOOD HILL PRIMARY | MINIMUM HEADROOM | SU 67102 74048 | NO | NO | 0.914 | 5.3896 | 5.4865 | 5.4365 | 5.0253 | 4.5661 | 3.7478 | 2.8049 | 1.8192 | 0.84469 | -2.8788 | -5.4869 | -6.7849 | 11.2692 | 11.1498 | 10.9345 | 10.4284 | 9.9896 | 9.2784 | 8.3804 | 7.4498 | 6.5478 | 3.0416 | -2.2992 | -9.6461 | 7.8171 | 7.8131 | 7.708 | 7.212 | 6.7804 | 5.9549 | 4.961 | 3.9386 | 2.9396 | -0.43286 | -2.4043 | -3.2247
|  | KENTWOOD HILL PRIMARY | EE |  |  |  |  | 5.3896 | 5.5151 | 5.4692 | 5.109 | 4.6835 | 3.8222 | 2.8549 | 1.8202 | 0.84469 | -2.6359 | -5.4339 | -6.7849 | 11.2692 | 11.1682 | 10.9824 | 10.5304 | 10.1651 | 9.4722 | 8.6365 | 7.709 | 6.8488 | 3.0416 | 0.15796 | -2.5176 | 7.8171 | 7.8304 | 7.7569 | 7.3396 | 6.9998 | 6.1702 | 5.211 | 4.162 | 3.1865 | -0.18388 | -2.3808 | -3.2247
|  | KENTWOOD HILL PRIMARY | HT |  |  |  |  | 5.3967 | 5.4865 | 5.4365 | 5.0253 | 4.5661 | 3.7478 | 2.8049 | 1.8192 | 0.87224 | -2.8788 | -5.4869 | -6.5839 | 11.2712 | 11.1498 | 10.9345 | 10.4284 | 9.9896 | 9.2784 | 8.3804 | 7.4498 | 6.5478 | 3.7284 | 2.2937 | 1.8559 | 7.8222 | 7.8131 | 7.708 | 7.212 | 6.7804 | 5.9549 | 4.961 | 3.9386 | 2.9396 | -0.43286 | -2.4043 | -2.9216
|  | KENTWOOD HILL PRIMARY | HE |  |  |  |  | 5.3967 | 5.5324 | 5.4906 | 5.1243 | 4.6927 | 3.8671 | 2.9222 | 1.9222 | 0.97327 | -1.9573 | -4.4012 | -5.4941 | 11.2692 | 11.1692 | 10.9845 | 10.5355 | 10.1682 | 9.4855 | 8.6518 | 7.7498 | 6.908 | 3.2284 | 0.39673 | -2.4124 | 7.8222 | 7.8447 | 7.7763 | 7.358 | 7.0059 | 6.1998 | 5.2641 | 4.258 | 3.3202 | 0.33143 | -1.5747 | -2.3104
|  | KENTWOOD HILL PRIMARY | FB |  |  |  |  | 5.662 | 5.9498 | 6.061 | 6.0692 | 6.0141 | 5.86 | 5.6518 | 5.409 | 5.0804 | 3.2141 | 0.90082 | -0.76857 | 11.3682 | 11.3988 | 11.2855 | 11.1243 | 10.8559 | 10.3702 | 9.8161 | 9.2151 | 8.3896 | 4.0376 | -2.2992 | -9.6461 | 8.1171 | 8.3784 | 8.4988 | 8.5773 | 8.5927 | 8.4304 | 8.2049 | 7.9284 | 7.412 | 5.109 | 2.1804 | 0.58347
COWLEY GSP | YARNTON BSP | KIDDINGTON PRIMARY | MINIMUM HEADROOM | SP 43362 24301 | NO | YES | 9.195 | 6.1447 | 6.1783 | 6.1885 | 6.1396 | 6.0498 | 5.9294 | 5.7416 | 5.4896 | 5.2875 | 4.6222 | 4.2885 | 4.1998 | 9.5171 | 9.511 | 9.4977 | 9.4447 | 9.3324 | 9.2426 | 9.11 | 8.9273 | 8.7273 | 8.0181 | 7.6059 | 6.9161 | 8.1875 | 8.1957 | 8.1753 | 8.1263 | 7.9508 | 7.8232 | 7.6232 | 7.3671 | 7.162 | 6.5161 | 6.2283 | 6.1957
|  | KIDDINGTON PRIMARY | EE |  |  |  |  | 6.1447 | 6.1783 | 6.1936 | 6.1498 | 6.0651 | 5.9651 | 5.8038 | 5.5487 | 5.3222 | 4.6875 | 4.3651 | 4.2804 | 9.5191 | 9.512 | 9.5028 | 9.4589 | 9.3691 | 9.2651 | 9.1477 | 8.9885 | 8.7651 | 8.0181 | 7.6059 | 7.3212 | 8.1916 | 8.1967 | 8.1855 | 8.1477 | 7.9998 | 7.8549 | 7.6845 | 7.4457 | 7.2181 | 6.5814 | 6.2875 | 6.2253
|  | KIDDINGTON PRIMARY | HT |  |  |  |  | 6.1447 | 6.1794 | 6.1885 | 6.1396 | 6.0498 | 5.9294 | 5.7416 | 5.4896 | 5.2875 | 4.6222 | 4.2885 | 4.1998 | 9.5171 | 9.511 | 9.4977 | 9.4447 | 9.3324 | 9.2426 | 9.11 | 8.9273 | 8.7273 | 8.0518 | 7.7712 | 7.7385 | 8.1875 | 8.1967 | 8.1753 | 8.1263 | 7.9508 | 7.8232 | 7.6232 | 7.3671 | 7.162 | 6.5161 | 6.2283 | 6.1957
|  | KIDDINGTON PRIMARY | HE |  |  |  |  | 6.1447 | 6.1783 | 6.1936 | 6.1436 | 6.0518 | 5.9487 | 5.8018 | 5.5508 | 5.3753 | 4.8947 | 4.6416 | 4.5498 | 9.5191 | 9.513 | 9.5028 | 9.4579 | 9.3671 | 9.262 | 9.1538 | 9.0038 | 8.8426 | 8.2253 | 7.8753 | 7.5722 | 8.1896 | 8.1957 | 8.1845 | 8.1426 | 7.9916 | 7.8385 | 7.6926 | 7.461 | 7.2916 | 6.8028 | 6.5916 | 6.5273
|  | KIDDINGTON PRIMARY | FB |  |  |  |  | 6.2049 | 6.2589 | 6.2896 | 6.3008 | 6.312 | 6.2916 | 6.26 | 6.2498 | 6.2059 | 5.9324 | 5.4171 | 5.1038 | 9.5712 | 9.5794 | 9.5712 | 9.5651 | 9.5518 | 9.513 | 9.463 | 9.4498 | 9.3926 | 8.9232 | 7.8722 | 6.9161 | 8.2804 | 8.3212 | 8.3314 | 8.3498 | 8.361 | 8.3355 | 8.2906 | 8.3191 | 8.2681 | 7.9232 | 7.2324 | 6.9049
BRAMLEY (BASI) GSP | READING BSP | KIDMORE END PRIMARY | MINIMUM HEADROOM | SU 69953 78205 | NO | YES | 0.615 | 15.2545 | 15.2708 | 15.1708 | 15.0524 | 14.8647 | 14.532 | 14.1361 | 13.679 | 13.2535 | 12.1116 | 11.5545 | 11.4606 | 16.4569 | 16.3876 | 16.208 | 16.0222 | 15.7794 | 15.3967 | 14.962 | 14.458 | 13.9886 | 12.4518 | 11.4498 | 9.062 | 15.6739 | 15.6545 | 15.5024 | 15.3514 | 15.131 | 14.7616 | 14.3433 | 13.8759 | 13.4249 | 12.2249 | 11.6596 | 11.582
|  | KIDMORE END PRIMARY | EE |  |  |  |  | 15.2565 | 15.28 | 15.1851 | 15.0678 | 14.9086 | 14.5606 | 14.1739 | 13.7137 | 13.282 | 12.1504 | 11.5545 | 11.4606 | 16.459 | 16.3916 | 16.2161 | 16.0324 | 15.809 | 15.41 | 15.0018 | 14.4967 | 14.0253 | 12.4518 | 11.4498 | 10.7141 | 15.6769 | 15.6606 | 15.5137 | 15.3637 | 15.1667 | 14.779 | 14.3984 | 13.9116 | 13.4576 | 12.2463 | 11.6596 | 11.582
|  | KIDMORE END PRIMARY | HT |  |  |  |  | 15.2545 | 15.2708 | 15.1708 | 15.0524 | 14.8647 | 14.532 | 14.1361 | 13.679 | 13.2535 | 12.1116 | 11.5902 | 11.5994 | 16.4569 | 16.3876 | 16.208 | 16.0222 | 15.7794 | 15.3967 | 14.962 | 14.458 | 13.9886 | 12.6876 | 12.0998 | 12.0192 | 15.6739 | 15.6545 | 15.5024 | 15.3514 | 15.131 | 14.7616 | 14.3433 | 13.8759 | 13.4249 | 12.2249 | 11.7239 | 11.781
|  | KIDMORE END PRIMARY | HE |  |  |  |  | 15.2555 | 15.28 | 15.1841 | 15.0657 | 14.8963 | 14.5769 | 14.1504 | 13.6984 | 13.279 | 12.2412 | 11.7157 | 11.5453 | 16.458 | 16.3916 | 16.2151 | 16.0314 | 15.8049 | 15.4386 | 14.9886 | 14.5069 | 14.0559 | 12.5763 | 11.6743 | 10.8212 | 15.6749 | 15.6606 | 15.5137 | 15.3616 | 15.1586 | 14.8035 | 14.38 | 13.9096 | 13.4749 | 12.3555 | 11.8586 | 11.6902
|  | KIDMORE END PRIMARY | FB |  |  |  |  | 15.4463 | 15.5494 | 15.6382 | 15.6933 | 15.7943 | 15.5902 | 15.4627 | 15.3729 | 15.2229 | 14.3871 | 13.482 | 12.881 | 16.5906 | 16.562 | 16.5345 | 16.4753 | 16.46 | 16.111 | 15.8498 | 15.6314 | 15.3529 | 13.6916 | 11.5845 | 9.062 | 15.8657 | 15.9208 | 15.9667 | 15.979 | 16.0137 | 15.8402 | 15.679 | 15.5718 | 15.3912 | 14.4055 | 13.4402 | 12.7647
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | KINGS RIDE PRIMARY | MINIMUM HEADROOM | SU 87551 61530 | NO | NO | 1.728 | 11.0563 | 11.093 | 11.1124 | 10.9093 | 10.5899 | 10.1307 | 9.645 | 9.0665 | 8.5399 | 6.796 | 6.0246 | 6.1573 | 13.5475 | 13.473 | 13.4241 | 13.2139 | 12.9006 | 12.4557 | 11.9996 | 11.4241 | 10.9292 | 9.2598 | 7.5251 | 4.6526 | 11.5927 | 11.5764 | 11.5529 | 11.3489 | 11.0142 | 10.5407 | 10.0774 | 9.4846 | 8.9764 | 7.2784 | 6.5305 | 6.6376
|  | KINGS RIDE PRIMARY | EE |  |  |  |  | 11.0563 | 11.093 | 11.1124 | 10.9358 | 10.6736 | 10.3103 | 9.9001 | 9.4134 | 8.9665 | 7.2807 | 6.3532 | 6.2818 | 13.5475 | 13.4802 | 13.4302 | 13.2383 | 12.9353 | 12.5506 | 12.1169 | 11.5934 | 11.1516 | 9.3108 | 8.071 | 7.3261 | 11.5927 | 11.5764 | 11.5529 | 11.3703 | 11.058 | 10.6703 | 10.2509 | 9.7264 | 9.2835 | 7.6029 | 6.6713 | 6.6376
|  | KINGS RIDE PRIMARY | HT |  |  |  |  | 11.0614 | 11.095 | 11.1144 | 10.9093 | 10.5899 | 10.1307 | 9.645 | 9.0665 | 8.5399 | 6.796 | 6.0246 | 6.1573 | 13.5485 | 13.473 | 13.4241 | 13.2139 | 12.9006 | 12.4557 | 11.9996 | 11.4241 | 10.9292 | 9.3679 | 8.6863 | 8.7067 | 11.5989 | 11.5774 | 11.556 | 11.3489 | 11.0142 | 10.5407 | 10.0774 | 9.4846 | 8.9764 | 7.2784 | 6.5305 | 6.7029
|  | KINGS RIDE PRIMARY | HE |  |  |  |  | 11.0603 | 11.1022 | 11.1297 | 10.9522 | 10.6869 | 10.345 | 9.9226 | 9.443 | 8.9756 | 7.3624 | 6.8134 | 6.8154 | 13.5475 | 13.4812 | 13.4322 | 13.2404 | 12.9353 | 12.5669 | 12.1128 | 11.5914 | 11.1312 | 9.2598 | 8.269 | 7.5108 | 11.5989 | 11.5856 | 11.5672 | 11.3805 | 11.0631 | 10.6989 | 10.2642 | 9.7478 | 9.2927 | 7.6723 | 7.1509 | 7.1917
|  | KINGS RIDE PRIMARY | FB |  |  |  |  | 11.3409 | 11.494 | 11.4154 | 11.294 | 11.2848 | 11.1073 | 10.9103 | 10.7011 | 10.4583 | 9.2165 | 7.9644 | 7.1256 | 13.6945 | 13.7149 | 13.573 | 13.4118 | 13.322 | 13.0302 | 12.7179 | 12.4026 | 12.0536 | 10.0404 | 7.5251 | 4.6526 | 11.8927 | 12.007 | 11.8978 | 11.755 | 11.7468 | 11.5489 | 11.3397 | 11.1264 | 10.8764 | 9.5213 | 8.2121 | 7.3121
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINGSCLERE PRIMARY | MINIMUM HEADROOM | SU 51982 59358 | NO | NO | 0.784 | 7.6245 | 7.6306 | 7.4092 | 7.2531 | 7.0867 | 6.7276 | 6.3684 | 5.9265 | 5.5418 | 4.101 | 3.0622 | 2.4847 | 9.5663 | 9.5459 | 9.2939 | 9.152 | 8.9918 | 8.7602 | 8.4898 | 8.1653 | 7.9112 | 6.7388 | 6.0327 | 5.6 | 8.4571 | 8.4541 | 8.2041 | 8.0388 | 7.8745 | 7.5847 | 7.2653 | 6.8959 | 6.5735 | 5.2837 | 4.4827 | 4.098
|  | KINGSCLERE PRIMARY | EE |  |  |  |  | 7.6265 | 7.6347 | 7.4092 | 7.2643 | 7.0867 | 6.7643 | 6.3704 | 5.9622 | 5.598 | 4.101 | 3.0622 | 2.4847 | 9.5684 | 9.548 | 9.2959 | 9.1561 | 9 | 8.7827 | 8.4898 | 8.1888 | 7.9469 | 6.7388 | 6.0327 | 5.6153 | 8.4602 | 8.4571 | 8.2051 | 8.0398 | 7.8745 | 7.6082 | 7.2653 | 6.9092 | 6.6041 | 5.2837 | 4.4827 | 4.098
|  | KINGSCLERE PRIMARY | HT |  |  |  |  | 7.6276 | 7.6306 | 7.4133 | 7.2643 | 7.0939 | 6.7724 | 6.4408 | 6.0245 | 5.6949 | 4.2898 | 3.2143 | 2.5959 | 9.5673 | 9.5459 | 9.2939 | 9.152 | 8.9918 | 8.7602 | 8.5112 | 8.1653 | 7.9112 | 6.8459 | 6.3143 | 6.198 | 8.4582 | 8.4541 | 8.2041 | 8.0388 | 7.8755 | 7.598 | 7.3112 | 6.9214 | 6.6306 | 5.3857 | 4.6092 | 4.2867
|  | KINGSCLERE PRIMARY | HE |  |  |  |  | 7.6245 | 7.6316 | 7.4133 | 7.2531 | 7.1051 | 6.7276 | 6.3684 | 5.9265 | 5.5418 | 4.3745 | 3.6306 | 3.1724 | 9.5663 | 9.5469 | 9.2949 | 9.1551 | 9.0418 | 8.7745 | 8.5224 | 8.1959 | 7.9388 | 6.9173 | 6.5357 | 6.1398 | 8.4571 | 8.4541 | 8.2051 | 8.051 | 7.9112 | 7.5847 | 7.2857 | 6.8959 | 6.5735 | 5.5173 | 5.048 | 4.7327
|  | KINGSCLERE PRIMARY | FB |  |  |  |  | 7.7388 | 7.7796 | 7.8173 | 7.8184 | 7.8306 | 7.5837 | 7.4633 | 7.4194 | 7.3112 | 6.4184 | 5.5653 | 4.9337 | 9.649 | 9.6429 | 9.6357 | 9.6102 | 9.5776 | 9.2857 | 9.1286 | 9.049 | 8.9153 | 7.8837 | 6.7796 | 5.6 | 8.5602 | 8.5878 | 8.6122 | 8.6031 | 8.5908 | 8.3163 | 8.1969 | 8.148 | 8.0408 | 7.152 | 6.3378 | 5.6908
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINTBURY PRIMARY | MINIMUM HEADROOM | SU 37657 67143 | NO | NO | 0.219 | 7.5704 | 7.6184 | 7.6439 | 7.6327 | 7.6061 | 7.3949 | 7.25 | 7.1224 | 6.951 | 6.6224 | 6.4429 | 6.5367 | 9.6551 | 9.6439 | 9.6306 | 9.5939 | 9.548 | 9.3061 | 9.1367 | 9.0061 | 8.8173 | 8.3837 | 8.1347 | 7.7541 | 8.698 | 8.7265 | 8.7378 | 8.7224 | 8.651 | 8.4286 | 8.2286 | 8.0612 | 7.851 | 7.3622 | 7.1918 | 7.3378
|  | KINTBURY PRIMARY | EE |  |  |  |  | 7.5704 | 7.6214 | 7.6551 | 7.6622 | 7.6643 | 7.5816 | 7.3908 | 7.2857 | 7.1388 | 6.7265 | 6.5531 | 6.6327 | 9.6551 | 9.6469 | 9.6388 | 9.6122 | 9.5867 | 9.4663 | 9.248 | 9.1276 | 8.9561 | 8.4102 | 8.1347 | 8.0224 | 8.7 | 8.7276 | 8.749 | 8.749 | 8.6765 | 8.5602 | 8.3122 | 8.15 | 7.9541 | 7.4082 | 7.2469 | 7.3378
|  | KINTBURY PRIMARY | HT |  |  |  |  | 7.5714 | 7.6214 | 7.6439 | 7.6327 | 7.6061 | 7.3949 | 7.25 | 7.1224 | 6.951 | 6.6224 | 6.4429 | 6.5367 | 9.6571 | 9.648 | 9.6306 | 9.5939 | 9.548 | 9.3061 | 9.1367 | 9.0061 | 8.8173 | 8.3837 | 8.2102 | 8.2939 | 8.698 | 8.7286 | 8.7378 | 8.7224 | 8.651 | 8.4286 | 8.2286 | 8.0612 | 7.851 | 7.3622 | 7.1918 | 7.3551
|  | KINTBURY PRIMARY | HE |  |  |  |  | 7.5827 | 7.6184 | 7.6551 | 7.6633 | 7.6633 | 7.6827 | 7.4796 | 7.2571 | 7.149 | 6.8806 | 6.6929 | 6.6776 | 9.6684 | 9.6439 | 9.6367 | 9.6133 | 9.5837 | 9.5827 | 9.3582 | 9.1194 | 9.0031 | 8.5684 | 8.2806 | 8.1071 | 8.7112 | 8.7265 | 8.7469 | 8.749 | 8.6724 | 8.6724 | 8.4173 | 8.149 | 7.9929 | 7.5622 | 7.3857 | 7.4173
|  | KINTBURY PRIMARY | FB |  |  |  |  | 7.6531 | 7.7265 | 7.7908 | 7.8469 | 7.8735 | 7.8806 | 7.8735 | 7.8582 | 7.9112 | 7.7357 | 7.4714 | 7.1173 | 9.7214 | 9.7224 | 9.7276 | 9.7316 | 9.7082 | 9.6694 | 9.6184 | 9.5541 | 9.5602 | 9.1316 | 8.5684 | 7.7541 | 8.7745 | 8.8194 | 8.8541 | 8.8796 | 8.8837 | 8.9 | 8.8704 | 8.8122 | 8.8622 | 8.4806 | 8.1102 | 7.7551
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | KNOWL HILL PRIMARY | MINIMUM HEADROOM | SU 82849 79105 | NO | NO | 0.306 | 4.8767 | 4.8971 | 4.9043 | 4.8951 | 4.7288 | 4.6563 | 4.5767 | 4.4033 | 4.2788 | 3.8645 | 3.6747 | 3.7441 | 5.6321 | 5.6179 | 5.5954 | 5.5485 | 5.2781 | 5.1934 | 5.1015 | 4.924 | 4.7995 | 4.324 | 4.1209 | 3.8046 | 5.3696 | 5.3716 | 5.3686 | 5.3461 | 5.1186 | 5.041 | 4.9573 | 4.7829 | 4.6604 | 4.2237 | 4.0308 | 4.091
|  | KNOWL HILL PRIMARY | EE |  |  |  |  | 4.8767 | 4.8971 | 4.9094 | 4.9012 | 4.8247 | 4.6635 | 4.638 | 4.4951 | 4.3655 | 3.9941 | 3.8196 | 3.8369 | 5.6321 | 5.6179 | 5.5995 | 5.5515 | 5.3883 | 5.2015 | 5.1648 | 5.0015 | 4.8526 | 4.3852 | 4.1209 | 4.0321 | 5.3696 | 5.3716 | 5.3716 | 5.3512 | 5.2206 | 5.0482 | 5.0186 | 4.8665 | 4.7267 | 4.2747 | 4.088 | 4.141
|  | KNOWL HILL PRIMARY | HT |  |  |  |  | 4.8788 | 4.9012 | 4.9043 | 4.8951 | 4.7288 | 4.6563 | 4.5767 | 4.4033 | 4.2788 | 3.8645 | 3.6747 | 3.7441 | 5.6342 | 5.6189 | 5.5954 | 5.5485 | 5.2781 | 5.1934 | 5.1015 | 4.924 | 4.7995 | 4.324 | 4.1209 | 4.1689 | 5.3716 | 5.3747 | 5.3686 | 5.3461 | 5.1186 | 5.041 | 4.9573 | 4.7829 | 4.6604 | 4.2237 | 4.0308 | 4.091
|  | KNOWL HILL PRIMARY | HE |  |  |  |  | 4.8767 | 4.8971 | 4.9094 | 4.9002 | 4.8216 | 4.6563 | 4.6257 | 4.4686 | 4.3665 | 4.0869 | 3.992 | 3.991 | 5.6321 | 5.6179 | 5.5985 | 5.5515 | 5.3862 | 5.1964 | 5.1577 | 4.9832 | 4.8679 | 4.4872 | 4.3556 | 4.2362 | 5.3696 | 5.3716 | 5.3716 | 5.3492 | 5.2186 | 5.041 | 5.0084 | 4.841 | 4.7329 | 4.3767 | 4.3033 | 4.3288
|  | KNOWL HILL PRIMARY | FB |  |  |  |  | 4.9298 | 4.9676 | 4.9849 | 4.9961 | 5.0094 | 5.0002 | 5.0022 | 4.9859 | 4.9676 | 4.6451 | 4.3216 | 4.1339 | 5.676 | 5.676 | 5.6668 | 5.6587 | 5.6526 | 5.6066 | 5.5658 | 5.5179 | 5.4556 | 4.9148 | 4.3577 | 3.8046 | 5.4278 | 5.4553 | 5.4645 | 5.4767 | 5.4941 | 5.4706 | 5.4553 | 5.4247 | 5.3869 | 4.9737 | 4.6176 | 4.4247
FLEET-BRAMLEY GSP | ALDERSHOT BSP | LABURNUM ROAD PRIMARY | MINIMUM HEADROOM | SU 86017 50475 | NO | YES | 9.909 | 7.228 | 6.8545 | 6.1535 | 5.2566 | 4.5402 | 3.6341 | 2.6862 | 1.5433 | 0.61983 | -3.5751 | -6.0026 | -7.2485 | 14.2025 | 13.8351 | 13.3525 | 12.5974 | 11.977 | 11.376 | 10.5525 | 9.7708 | 9.0708 | 5.6994 | 2.2617 | -3.0914 | 9.7188 | 9.2382 | 8.5423 | 7.5382 | 6.7484 | 5.979 | 5.0974 | 4.1494 | 3.3229 | -0.43323 | -2.5343 | -3.6332
|  | LABURNUM ROAD PRIMARY | EE |  |  |  |  | 7.228 | 6.8545 | 6.1535 | 5.2566 | 4.5402 | 3.6341 | 2.6862 | 1.5433 | 0.61983 | -3.2873 | -5.9363 | -7.2485 | 14.2025 | 13.8362 | 13.3525 | 12.5974 | 11.978 | 11.376 | 10.6974 | 9.8229 | 9.1994 | 5.6994 | 3.3351 | 1.2627 | 9.7188 | 9.2382 | 8.5423 | 7.5382 | 6.7484 | 5.979 | 5.1627 | 4.1494 | 3.3821 | -0.23425 | -2.5343 | -3.6332
|  | LABURNUM ROAD PRIMARY | HT |  |  |  |  | 7.2341 | 6.8749 | 6.2372 | 5.3923 | 4.7443 | 3.8331 | 2.7168 | 1.6453 | 0.63922 | -3.5751 | -6.0026 | -6.7373 | 14.2025 | 13.8351 | 13.3566 | 12.6076 | 12.0351 | 11.4055 | 10.5525 | 9.7708 | 9.0708 | 6.1953 | 4.8127 | 4.4331 | 9.728 | 9.2647 | 8.6106 | 7.629 | 6.8994 | 6.0984 | 5.0974 | 4.1688 | 3.3229 | -0.43323 | -2.47 | -2.9424
|  | LABURNUM ROAD PRIMARY | HE |  |  |  |  | 7.2464 | 6.9015 | 6.2106 | 5.3351 | 4.5657 | 3.7219 | 2.8035 | 1.7127 | 0.83513 | -2.224 | -4.0557 | -4.9047 | 14.2066 | 13.8596 | 13.3606 | 12.6933 | 11.977 | 11.3872 | 10.6872 | 9.8055 | 9.1729 | 6.0892 | 4.0055 | 2.1933 | 9.7311 | 9.2923 | 8.5831 | 7.6668 | 6.7596 | 6.0311 | 5.226 | 4.2402 | 3.4984 | 0.66473 | -0.91895 | -1.571
|  | LABURNUM ROAD PRIMARY | FB |  |  |  |  | 7.3647 | 7.1004 | 6.5157 | 5.9086 | 5.479 | 5.1862 | 4.9331 | 4.5086 | 4.1433 | 2.0545 | -0.89242 | -2.8506 | 14.2617 | 13.9015 | 13.3811 | 12.827 | 12.3555 | 11.8892 | 11.3923 | 10.7933 | 10.3178 | 7.0535 | 2.2617 | -3.0914 | 9.926 | 9.5606 | 8.9739 | 8.3331 | 7.8504 | 7.4872 | 7.13 | 6.6596 | 6.3341 | 4.2096 | 1.3382 | -0.56282
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LAMBOURN PRIMARY | MINIMUM HEADROOM | SU 33280 78217 | NO | NO | 1.38 | 3.2459 | 16.4994 | 16.578 | 16.6627 | 16.7769 | 16.7422 | 16.629 | 16.4647 | 16.2871 | 15.3055 | 14.8882 | 15.181 | 5.1878 | 16.9641 | 16.8324 | 16.762 | 16.7396 | 16.5773 | 16.3059 | 16.0559 | 15.81 | 14.4029 | 13.9141 | 13.2406 | 4.0551 | 16.6065 | 16.5341 | 16.4922 | 16.5004 | 16.3586 | 16.1086 | 15.878 | 15.6463 | 14.3198 | 13.8259 | 14.0412
|  | LAMBOURN PRIMARY | EE |  |  |  |  | 3.2459 | 16.4994 | 16.5943 | 16.7024 | 16.8412 | 16.8392 | 16.7596 | 16.6351 | 16.482 | 15.4657 | 15.2259 | 15.181 | 5.1878 | 16.9682 | 16.8416 | 16.7804 | 16.7682 | 16.6253 | 16.3794 | 16.1529 | 15.91 | 14.4029 | 13.9141 | 13.5345 | 4.0551 | 16.6065 | 16.5463 | 16.5239 | 16.5453 | 16.431 | 16.2167 | 16.0198 | 15.7994 | 14.4412 | 14.131 | 14.0412
|  | LAMBOURN PRIMARY | HT |  |  |  |  | 3.2459 | 16.4994 | 16.578 | 16.6627 | 16.7769 | 16.7422 | 16.629 | 16.4647 | 16.2871 | 15.3055 | 14.8882 | 15.2229 | 5.1888 | 16.9641 | 16.8324 | 16.762 | 16.7396 | 16.5773 | 16.3059 | 16.0559 | 15.81 | 14.4365 | 13.9182 | 14.1284 | 4.0561 | 16.6065 | 16.5341 | 16.4922 | 16.5004 | 16.3586 | 16.1086 | 15.878 | 15.6463 | 14.3198 | 13.8259 | 14.1157
|  | LAMBOURN PRIMARY | HE |  |  |  |  | 3.2459 | 16.5004 | 16.5943 | 16.7045 | 16.8596 | 16.8331 | 16.7596 | 16.63 | 16.4739 | 15.7076 | 15.6576 | 15.6473 | 5.1878 | 16.9682 | 16.8427 | 16.7824 | 16.7967 | 16.6171 | 16.3814 | 16.1498 | 15.9049 | 14.6457 | 14.3192 | 13.9651 | 4.0561 | 16.6065 | 16.5473 | 16.5249 | 16.5749 | 16.4239 | 16.2157 | 16.0137 | 15.7933 | 14.7045 | 14.5678 | 14.5106
|  | LAMBOURN PRIMARY | FB |  |  |  |  | 3.3265 | 16.6035 | 16.8473 | 17.0698 | 17.1453 | 17.2218 | 17.2871 | 17.4198 | 17.4545 | 17.4729 | 16.378 | 16.0371 | 5.2551 | 17.0467 | 17.1437 | 17.2304 | 17.0916 | 17.0171 | 16.9406 | 16.9529 | 16.8386 | 16.0967 | 14.4233 | 13.2406 | 4.1143 | 16.6759 | 16.8269 | 16.9627 | 16.9647 | 16.9504 | 16.9382 | 17.0106 | 16.9555 | 16.5708 | 15.3198 | 14.881
FAWLEY GSP | LANGLEY BSP | LANGLEY PRIMARY | MINIMUM HEADROOM | SU 45158 01418 | NO | NO | 7.736 | 1.5536 | 1.5383 | 1.4332 | 1.0526 | 0.60867 | -0.15255 | -1.2811 | -2.4842 | -5.4015 | -9.2587 | -13.6536 | -16.8546 | 1.4531 | 1.4255 | 1.3918 | 1.2541 | 1.0735 | 0.8398 | 0.15102 | -1.1643 | -4.1367 | -7.4959 | -11.0296 | -15.1398 | 1.3908 | 1.3429 | 1.252 | 0.99286 | 0.68265 | 0.20204 | -0.71327 | -2.151 | -5.3388 | -9.0612 | -12.9214 | -16.7888
|  | LANGLEY PRIMARY | EE |  |  |  |  | 1.5719 | 1.5985 | 1.5668 | 1.2985 | 1.0026 | 0.33418 | -0.48418 | -1.4832 | -2.7036 | -6.4291 | -11.4699 | -13.6189 | 1.4602 | 1.4459 | 1.4276 | 1.3204 | 1.1888 | 0.9949 | 0.60918 | 0.022449 | -0.84898 | -3.7051 | -8.452 | -10.4816 | 1.4031 | 1.3806 | 1.3224 | 1.1245 | 0.89184 | 0.46122 | -0.14082 | -0.9398 | -2.0204 | -5.3439 | -10.4531 | -12.3888
|  | LANGLEY PRIMARY | HT |  |  |  |  | 1.5536 | 1.5383 | 1.4332 | 1.0526 | 0.60867 | -0.15255 | -1.2811 | -2.4811 | -4.327 | -8.6617 | -13.6536 | -16.8546 | 1.4531 | 1.4255 | 1.3918 | 1.2541 | 1.0735 | 0.8398 | 0.15102 | -0.60204 | -2.1714 | -5.3184 | -9.3673 | -12.0388 | 1.3908 | 1.3429 | 1.252 | 0.99286 | 0.68265 | 0.20204 | -0.71327 | -1.6939 | -3.5184 | -7.4806 | -12.3653 | -15.5092
|  | LANGLEY PRIMARY | HE |  |  |  |  | 1.5719 | 1.5995 | 1.5679 | 1.2913 | 0.9801 | 0.30051 | -0.7352 | -2.4842 | -5.4015 | -9.2587 | -13.2413 | -16.7495 | 1.4602 | 1.4459 | 1.4276 | 1.3194 | 1.1867 | 0.99082 | 0.34286 | -1.1643 | -4.1367 | -7.4959 | -11.0296 | -15.1398 | 1.4031 | 1.3816 | 1.3051 | 1.1214 | 0.88163 | 0.44592 | -0.42143 | -2.151 | -5.3388 | -9.0612 | -12.9214 | -16.7888
|  | LANGLEY PRIMARY | FB |  |  |  |  | 1.6872 | 1.7556 | 1.8066 | 1.8423 | 1.874 | 1.8209 | 1.674 | 1.3954 | 0.91071 | -1.076 | -3.9342 | -5.9454 | 1.5357 | 1.5439 | 1.5408 | 1.5184 | 1.5082 | 1.4235 | 1.2245 | 0.91939 | 0.36122 | -1.749 | -5.1633 | -8.6469 | 1.5061 | 1.5357 | 1.5643 | 1.549 | 1.5531 | 1.4796 | 1.2929 | 0.97857 | 0.45714 | -1.4316 | -4.1092 | -6.2316
FLEET-BRAMLEY GSP | FERNHURST BSP | LANGLEY COURT PRIMARY | MINIMUM HEADROOM | SU 80847 29056 | NO | NO | 8.796 | 7.5064 | 7.5636 | 7.5095 | 7.4646 | 7.1432 | 6.7728 | 6.3697 | 5.884 | 5.4575 | 4.2809 | 3.5228 | 3.2524 | 8.9691 | 8.9609 | 8.8844 | 8.8467 | 8.5222 | 8.2018 | 7.8538 | 7.4405 | 7.1058 | 5.9844 | 5.5538 | 4.2079 | 8.7554 | 8.7932 | 8.7422 | 8.6952 | 8.3564 | 8.0024 | 7.6167 | 7.1677 | 6.785 | 5.6707 | 5.0881 | 5.0156
|  | LANGLEY COURT PRIMARY | EE |  |  |  |  | 7.5075 | 7.5748 | 7.584 | 7.6401 | 7.4983 | 7.2371 | 6.9146 | 6.585 | 6.2432 | 5.183 | 4.4228 | 4.1187 | 8.9691 | 8.966 | 8.9222 | 8.9334 | 8.7436 | 8.464 | 8.1426 | 7.8262 | 7.5028 | 6.3303 | 5.6028 | 5.1069 | 8.7554 | 8.8013 | 8.7942 | 8.8269 | 8.6462 | 8.3738 | 8.0432 | 7.7197 | 7.385 | 6.3564 | 5.7187 | 5.5391
|  | LANGLEY COURT PRIMARY | HT |  |  |  |  | 7.5064 | 7.5636 | 7.5095 | 7.4646 | 7.1432 | 6.7728 | 6.3697 | 5.884 | 5.4575 | 4.2809 | 3.5228 | 3.2524 | 8.9691 | 8.9609 | 8.8844 | 8.8467 | 8.5222 | 8.2018 | 7.8538 | 7.4405 | 7.1058 | 5.9844 | 5.5538 | 5.5722 | 8.7564 | 8.7932 | 8.7422 | 8.6952 | 8.3564 | 8.0024 | 7.6167 | 7.1677 | 6.785 | 5.6707 | 5.0881 | 5.0156
|  | LANGLEY COURT PRIMARY | HE |  |  |  |  | 7.5126 | 7.5758 | 7.5881 | 7.6309 | 7.482 | 7.2513 | 6.935 | 6.5371 | 6.2013 | 5.3799 | 4.686 | 4.3493 | 8.9691 | 8.9681 | 8.9222 | 8.9334 | 8.7446 | 8.5181 | 8.1967 | 7.8232 | 7.5262 | 6.4977 | 5.863 | 5.3018 | 8.7585 | 8.8013 | 8.7962 | 8.8218 | 8.633 | 8.4187 | 8.085 | 7.6983 | 7.3769 | 6.5524 | 6.0248 | 5.8044
|  | LANGLEY COURT PRIMARY | FB |  |  |  |  | 7.6544 | 7.7564 | 7.833 | 7.8799 | 7.9034 | 7.8891 | 7.8595 | 7.7983 | 7.7218 | 7.132 | 6.3626 | 5.6503 | 9.0773 | 9.0905 | 9.0854 | 9.065 | 9.0283 | 8.9844 | 8.8558 | 8.713 | 8.5497 | 7.463 | 6.0038 | 4.2079 | 8.9044 | 8.984 | 9.0462 | 9.084 | 9.1167 | 9.1473 | 9.0962 | 9.0248 | 8.9299 | 8.2707 | 7.4718 | 6.7493
AXMINSTER GSP | YEOVIL BSP | LARKHILL PRIMARY | MINIMUM HEADROOM | ST 53677 16914 | NO | NO | 8.866 | 12.9558 | 12.8303 | 12.6456 | 12.314 | 11.8803 | 11.1446 | 10.4007 | 9.5925 | 8.8354 | 5.6752 | 3.516 | 2.4089 | 14.3885 | 14.2864 | 14.1293 | 13.8701 | 13.514 | 13.0323 | 12.518 | 11.9293 | 11.4466 | 9.1017 | 6.9048 | 2.9527 | 13.5946 | 13.5201 | 13.3385 | 13.0436 | 12.6364 | 12.0058 | 11.3589 | 10.6405 | 10.0548 | 7.4303 | 5.7232 | 4.9232
|  | LARKHILL PRIMARY | EE |  |  |  |  | 12.9558 | 12.8303 | 12.6456 | 12.314 | 11.8885 | 11.1446 | 10.4497 | 9.6395 | 8.8354 | 5.6752 | 3.516 | 2.4089 | 14.3895 | 14.2864 | 14.1293 | 13.8711 | 13.5201 | 13.0629 | 12.6007 | 11.9966 | 11.4823 | 9.1017 | 7.4395 | 5.9966 | 13.5946 | 13.5201 | 13.3385 | 13.0436 | 12.6436 | 12.0221 | 11.4252 | 10.6966 | 10.0548 | 7.4303 | 5.7232 | 4.9232
|  | LARKHILL PRIMARY | HT |  |  |  |  | 12.9589 | 12.866 | 12.6925 | 12.3589 | 11.9252 | 11.1456 | 10.4007 | 9.5925 | 8.8823 | 5.7476 | 3.7354 | 2.9068 | 14.3885 | 14.2885 | 14.1323 | 13.8772 | 13.514 | 13.0323 | 12.518 | 11.9293 | 11.4466 | 9.6221 | 8.7487 | 8.5211 | 13.5987 | 13.5436 | 13.3701 | 13.0701 | 12.6517 | 12.0058 | 11.3589 | 10.6405 | 10.0609 | 7.4936 | 5.9344 | 5.4395
|  | LARKHILL PRIMARY | HE |  |  |  |  | 12.9629 | 12.8446 | 12.6558 | 12.314 | 11.8803 | 11.2262 | 10.5987 | 9.8854 | 9.2027 | 6.3762 | 4.8099 | 3.9374 | 14.3885 | 14.2874 | 14.1293 | 13.8701 | 13.516 | 13.0885 | 12.6027 | 12.0293 | 11.5548 | 9.2374 | 7.8221 | 6.3527 | 13.6017 | 13.5364 | 13.3527 | 13.0497 | 12.6364 | 12.0823 | 11.5089 | 10.8436 | 10.2895 | 7.9303 | 6.7599 | 6.1405
|  | LARKHILL PRIMARY | FB |  |  |  |  | 13.1344 | 13.1415 | 13.1017 | 13.0078 | 12.9344 | 12.7854 | 12.6027 | 12.4517 | 12.2538 | 10.7803 | 8.7966 | 7.418 | 14.4711 | 14.3956 | 14.3027 | 14.1701 | 14.0517 | 13.7874 | 13.3854 | 13.0609 | 12.7415 | 10.2813 | 6.9048 | 2.9527 | 13.7527 | 13.7793 | 13.7823 | 13.7436 | 13.6976 | 13.5793 | 13.2925 | 13.1058 | 12.9099 | 11.3374 | 9.4752 | 8.1732
COWLEY GSP | WITNEY BSP | LEAFIELD PRIMARY | MINIMUM HEADROOM | SP 30282 15270 | NO | NO | 1.385 | 1.5347 | 1.5337 | 1.5071 | 1.4255 | 1.3255 | 1.001 | 0.72143 | 0.36735 | -0.0040816 | -0.96327 | -1.7929 | -2.351 | 5.1643 | 5.1439 | 5.0959 | 4.9694 | 4.799 | 4.5816 | 4.3837 | 4.1347 | 3.9388 | 3.2276 | 3.0908 | 2.4082 | 1.9786 | 1.9735 | 1.9429 | 1.8612 | 1.8 | 1.5245 | 1.3163 | 1.0582 | 0.80102 | -0.0040816 | -0.51939 | -0.79796
|  | LEAFIELD PRIMARY | EE |  |  |  |  | 1.5347 | 1.5337 | 1.5204 | 1.4561 | 1.3755 | 1.1898 | 0.80816 | 0.40306 | 0.079592 | -0.96327 | -1.6878 | -2.1112 | 5.1673 | 5.1449 | 5.1 | 4.9806 | 4.8194 | 4.798 | 4.5102 | 4.199 | 3.9663 | 3.2714 | 3.1092 | 2.8959 | 1.9786 | 1.9735 | 1.9541 | 1.8878 | 1.8408 | 1.7306 | 1.4214 | 1.0857 | 0.83163 | 0.019388 | -0.44286 | -0.66429
|  | LEAFIELD PRIMARY | HT |  |  |  |  | 1.5439 | 1.5531 | 1.5071 | 1.4255 | 1.3337 | 1.001 | 0.7398 | 0.42551 | 0.16531 | -0.94898 | -1.7929 | -2.351 | 5.1663 | 5.15 | 5.0959 | 4.9694 | 4.799 | 4.5816 | 4.3837 | 4.1347 | 3.9388 | 3.2276 | 3.0908 | 3.2173 | 1.9837 | 1.9827 | 1.9429 | 1.8612 | 1.8 | 1.5245 | 1.3163 | 1.0582 | 0.85204 | -0.0040816 | -0.51939 | -0.79796
|  | LEAFIELD PRIMARY | HE |  |  |  |  | 1.5347 | 1.5347 | 1.5184 | 1.4306 | 1.3255 | 1.1245 | 0.72143 | 0.36735 | -0.0040816 | -0.80306 | -1.5224 | -1.8908 | 5.1643 | 5.1439 | 5.098 | 4.9776 | 4.8163 | 4.7949 | 4.5041 | 4.2622 | 4.0031 | 3.3786 | 3.1776 | 2.9122 | 1.9786 | 1.9735 | 1.952 | 1.8888 | 1.8122 | 1.6939 | 1.3714 | 1.0959 | 0.80102 | 0.15102 | -0.32449 | -0.54592
|  | LEAFIELD PRIMARY | FB |  |  |  |  | 1.6429 | 1.6837 | 1.699 | 1.7122 | 1.7133 | 1.6898 | 1.6388 | 1.5786 | 1.5878 | 1.1388 | 0.57551 | 0.047959 | 5.2357 | 5.2357 | 5.2143 | 5.1969 | 5.1398 | 5.0765 | 4.998 | 4.899 | 4.9051 | 4.2918 | 3.4653 | 2.4082 | 2.0786 | 2.1092 | 2.1163 | 2.1276 | 2.1286 | 2.0898 | 2.0408 | 2.002 | 2.0133 | 1.6041 | 1.1153 | 0.62347
WILLESDEN GSP | ACTON LANE BSP | LEAMINGTON PARK PRIMARY | MINIMUM HEADROOM | TQ 20539 81536 | NO | YES | 7.646 | 10.3752 | 7.4364 | 6.7793 | 6.0967 | 5.266 | 4.4375 | 3.3926 | 3.0916 | 2.8762 | 1.1569 | 0.0058367 | -0.50233 | 13.1718 | 9.9146 | 9.5881 | 9.2758 | 8.7554 | 8.2789 | 7.9656 | 7.5309 | 7.183 | 5.1718 | 3.6585 | 1.7116 | 10.3575 | 7.735 | 6.9789 | 6.3442 | 5.4983 | 4.6779 | 3.9218 | 3.486 | 3.1636 | 1.1932 | 0.0023673 | -0.49967
|  | LEAMINGTON PARK PRIMARY | EE |  |  |  |  | 10.3752 | 10.265 | 7.2364 | 6.5589 | 5.8864 | 4.8864 | 3.3926 | 3.0916 | 2.8762 | 1.1569 | 0.0058367 | -0.50233 | 13.1728 | 13.1248 | 9.8371 | 9.5269 | 9.2228 | 8.7605 | 7.9656 | 7.5309 | 7.183 | 5.1718 | 3.6585 | 2.4401 | 10.3575 | 10.3054 | 7.4044 | 6.7667 | 6.1095 | 5.186 | 3.9218 | 3.486 | 3.1636 | 1.1932 | 0.0023673 | -0.49967
|  | LEAMINGTON PARK PRIMARY | HT |  |  |  |  | 10.3803 | 7.4364 | 6.7793 | 6.0967 | 5.266 | 4.4375 | 4.1007 | 3.6477 | 3.2762 | 1.663 | 0.67012 | 0.34257 | 13.1728 | 9.9146 | 9.5881 | 9.2758 | 8.7554 | 8.2789 | 8.0309 | 7.632 | 7.2973 | 6.1024 | 5.2513 | 4.8646 | 10.3605 | 7.735 | 6.9789 | 6.3442 | 5.4983 | 4.6779 | 4.3228 | 3.8238 | 3.436 | 1.8381 | 0.89727 | 0.6238
|  | LEAMINGTON PARK PRIMARY | HE |  |  |  |  | 10.3803 | 10.2671 | 7.513 | 7.0987 | 6.7191 | 6.0191 | 5.2834 | 4.7558 | 4.3609 | 2.515 | 2.0926 | 1.8201 | 13.1718 | 13.1238 | 9.9656 | 9.783 | 9.6064 | 9.2707 | 8.8738 | 8.4911 | 8.1973 | 6.5595 | 5.6483 | 4.5524 | 10.3575 | 10.3054 | 7.6616 | 7.2575 | 6.8391 | 6.1769 | 5.4075 | 4.8758 | 4.4962 | 2.7095 | 2.3452 | 2.1064
|  | LEAMINGTON PARK PRIMARY | FB |  |  |  |  | 10.416 | 10.3477 | 10.3375 | 7.6671 | 7.4028 | 7.0752 | 6.666 | 6.264 | 5.863 | 4.3436 | 3.4854 | 2.8364 | 13.1799 | 13.132 | 13.1146 | 9.9718 | 9.8197 | 9.6054 | 9.2891 | 8.9452 | 8.5136 | 6.4993 | 4.4677 | 1.7116 | 10.4024 | 10.3779 | 10.3799 | 7.9667 | 7.7483 | 7.3013 | 6.8799 | 6.5126 | 6.0697 | 4.4207 | 3.535 | 2.8809
MINETY GSP | STRATTON (RESERVE) BSP | LECHLADE PRIMARY | MINIMUM HEADROOM | SP 22074 00496 | NO | NO | 0.975 | 5.0206 | 5.04 | 5.0267 | 4.9747 | 4.8747 | 4.5941 | 4.2645 | 3.9604 | 3.6349 | 2.639 | 1.9063 | 1.5084 | 5.398 | 5.3786 | 5.3388 | 5.2827 | 5.1827 | 4.9969 | 4.7459 | 4.5367 | 4.3 | 3.6847 | 3.249 | 2.4908 | 4.9765 | 4.9816 | 4.9694 | 4.8949 | 4.8051 | 4.6224 | 4.401 | 4.1857 | 3.9684 | 3.3367 | 2.9449 | 2.7908
|  | LECHLADE PRIMARY | EE |  |  |  |  | 5.0216 | 5.0471 | 5.0502 | 5.0369 | 5.0461 | 4.8533 | 4.5461 | 4.2267 | 3.9941 | 3.0308 | 2.2961 | 1.8961 | 5.399 | 5.3806 | 5.3469 | 5.3061 | 5.3214 | 5.202 | 4.9296 | 4.651 | 4.4837 | 3.7204 | 3.249 | 2.9316 | 4.9786 | 4.9847 | 4.9816 | 4.9306 | 4.8806 | 4.75 | 4.5449 | 4.3286 | 4.1541 | 3.5673 | 3.1949 | 3.0367
|  | LECHLADE PRIMARY | HT |  |  |  |  | 5.0227 | 5.04 | 5.0267 | 4.9747 | 4.8747 | 4.5941 | 4.2645 | 3.9604 | 3.6349 | 2.639 | 1.9063 | 1.5084 | 5.401 | 5.3786 | 5.3388 | 5.2827 | 5.1827 | 4.9969 | 4.7459 | 4.5367 | 4.3 | 3.6847 | 3.4255 | 3.402 | 4.9776 | 4.9816 | 4.9694 | 4.8949 | 4.8051 | 4.6224 | 4.401 | 4.1857 | 3.9684 | 3.3367 | 2.9449 | 2.7908
|  | LECHLADE PRIMARY | HE |  |  |  |  | 5.0206 | 5.0451 | 5.0502 | 5.0257 | 5.0318 | 4.8278 | 4.5053 | 4.1635 | 3.9145 | 3.1635 | 2.4961 | 2.1267 | 5.398 | 5.3786 | 5.3469 | 5.302 | 5.3224 | 5.1939 | 4.9173 | 4.6306 | 4.4541 | 3.8347 | 3.4092 | 3.0327 | 4.9765 | 4.9837 | 4.9816 | 4.9245 | 4.8714 | 4.7337 | 4.5214 | 4.2959 | 4.1122 | 3.6214 | 3.2724 | 3.1173
|  | LECHLADE PRIMARY | FB |  |  |  |  | 5.1278 | 5.19 | 5.2237 | 5.2604 | 5.2829 | 5.2706 | 5.2247 | 5.242 | 5.1941 | 4.8135 | 4.2706 | 3.7982 | 5.4888 | 5.4949 | 5.4765 | 5.4714 | 5.451 | 5.3796 | 5.2939 | 5.2765 | 5.1816 | 4.5449 | 3.652 | 2.4908 | 5.052 | 5.0857 | 5.099 | 5.1102 | 5.1184 | 5.0867 | 5.0449 | 5.0235 | 4.9918 | 4.6449 | 4.2622 | 4.0286
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LECKHAMPSTEAD PRIMARY | MINIMUM HEADROOM | SU 43962 77635 | NO | NO | 0.401 | 3.8645 | 3.8747 | 3.8798 | 3.8431 | 3.5288 | 3.491 | 3.3104 | 3.0798 | 2.8543 | 2.3186 | 2.1278 | 2.19 | 4.4281 | 4.4077 | 4.3832 | 4.3413 | 4.0577 | 4.024 | 3.8577 | 3.6352 | 3.4372 | 2.8607 | 2.6964 | 2.3413 | 4.2522 | 4.2482 | 4.2094 | 4.1206 | 3.8043 | 3.7655 | 3.5778 | 3.3594 | 3.1502 | 2.6043 | 2.4339 | 2.5114
|  | LECKHAMPSTEAD PRIMARY | EE |  |  |  |  | 3.8757 | 3.8747 | 3.8798 | 3.8431 | 3.6206 | 3.4992 | 3.3247 | 3.091 | 2.9278 | 2.3186 | 2.1318 | 2.19 | 4.4393 | 4.4077 | 4.3862 | 4.3454 | 4.1679 | 4.027 | 3.8801 | 3.6505 | 3.4862 | 2.8668 | 2.6964 | 2.6077 | 4.2635 | 4.2482 | 4.2094 | 4.1216 | 3.8992 | 3.7716 | 3.5961 | 3.3737 | 3.2104 | 2.6084 | 2.4369 | 2.5114
|  | LECKHAMPSTEAD PRIMARY | HT |  |  |  |  | 3.8645 | 3.8757 | 3.8798 | 3.8441 | 3.5288 | 3.5094 | 3.3104 | 3.09 | 2.9084 | 2.3278 | 2.1278 | 2.1951 | 4.4281 | 4.4087 | 4.3832 | 4.3413 | 4.0577 | 4.026 | 3.8577 | 3.6352 | 3.4526 | 2.8607 | 2.7107 | 2.8168 | 4.2522 | 4.2482 | 4.2094 | 4.1206 | 3.8043 | 3.7778 | 3.5778 | 3.3594 | 3.1859 | 2.6043 | 2.4339 | 2.5257
|  | LECKHAMPSTEAD PRIMARY | HE |  |  |  |  | 3.8757 | 3.8757 | 3.8808 | 3.8441 | 3.6206 | 3.491 | 3.3278 | 3.0798 | 2.8543 | 2.44 | 2.2767 | 2.3033 | 4.4403 | 4.4087 | 4.3862 | 4.3464 | 4.1658 | 4.024 | 3.8944 | 3.6536 | 3.4372 | 2.9893 | 2.8434 | 2.726 | 4.2645 | 4.2492 | 4.2094 | 4.1227 | 3.8982 | 3.7655 | 3.6114 | 3.3706 | 3.1502 | 2.7298 | 2.5839 | 2.6206
|  | LECKHAMPSTEAD PRIMARY | FB |  |  |  |  | 3.9441 | 3.9818 | 4.0135 | 4.0359 | 4.0135 | 3.9778 | 3.9329 | 3.8696 | 3.9135 | 3.5288 | 2.8992 | 2.6614 | 4.4974 | 4.4872 | 4.4801 | 4.4781 | 4.4444 | 4.4015 | 4.3393 | 4.273 | 4.275 | 3.825 | 3.0087 | 2.3413 | 4.3298 | 4.3502 | 4.3482 | 4.3339 | 4.2818 | 4.2431 | 4.1931 | 4.1288 | 4.1686 | 3.7655 | 3.141 | 2.9043
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | LEE-ON-SOLENT PRIMARY | MINIMUM HEADROOM | SU 56858 00293 | NO | YES | 13.83 | 3.2928 | 3.052 | 2.6949 | 2.1836 | 1.6663 | 0.92956 | 0.10098 | -0.7582 | -1.5072 | -4.0868 | -5.7643 | -6.2306 | 4.7728 | 4.5238 | 4.083 | 3.5555 | 3.0024 | 2.3351 | 1.6096 | 0.84017 | 0.19323 | -2.3853 | -4.8282 | -9.6629 | 3.8663 | 3.6081 | 3.2755 | 2.7173 | 2.1163 | 1.3296 | 0.52037 | -0.33881 | -1.049 | -3.6806 | -5.1449 | -5.4551
|  | LEE-ON-SOLENT PRIMARY | EE |  |  |  |  | 3.3183 | 3.2908 | 2.8847 | 2.5224 | 2.1602 | 1.5357 | 0.75507 | -0.023506 | -0.67453 | -3.1388 | -4.9521 | -5.7317 | 4.7871 | 4.7004 | 4.1871 | 3.7177 | 3.231 | 2.631 | 1.9065 | 1.1677 | 0.58098 | -2.3853 | -4.4721 | -6.27 | 3.8836 | 3.8142 | 3.3785 | 2.9734 | 2.4816 | 1.7969 | 0.99384 | 0.202 | -0.43575 | -3.0113 | -4.6368 | -5.2684
|  | LEE-ON-SOLENT PRIMARY | HT |  |  |  |  | 3.2928 | 3.052 | 2.6949 | 2.1836 | 1.6663 | 0.92956 | 0.10098 | -0.7582 | -1.5072 | -4.0868 | -5.7643 | -6.2306 | 4.7728 | 4.5238 | 4.083 | 3.5555 | 3.0024 | 2.3351 | 1.6096 | 0.84017 | 0.19323 | -2.2098 | -3.4068 | -3.7813 | 3.8663 | 3.6081 | 3.2755 | 2.7173 | 2.1163 | 1.3296 | 0.52037 | -0.33881 | -1.049 | -3.6806 | -5.1449 | -5.4551
|  | LEE-ON-SOLENT PRIMARY | HE |  |  |  |  | 3.3245 | 3.304 | 2.9387 | 2.5867 | 2.2071 | 1.6632 | 0.92037 | 0.11527 | -0.55412 | -2.5909 | -3.7021 | -4.2296 | 4.7851 | 4.6994 | 4.2024 | 3.7504 | 3.2534 | 2.683 | 1.9902 | 1.2187 | 0.61874 | -2.1006 | -3.7486 | -5.5894 | 3.8887 | 3.8214 | 3.4091 | 3.0265 | 2.5132 | 1.8867 | 1.1245 | 0.30302 | -0.34289 | -2.5174 | -3.4715 | -3.9072
|  | LEE-ON-SOLENT PRIMARY | FB |  |  |  |  | 3.5132 | 3.4989 | 3.4265 | 3.251 | 3.1163 | 2.9877 | 2.7959 | 2.5653 | 2.3602 | 1.0408 | -0.79902 | -2.0643 | 4.9187 | 4.7636 | 4.5667 | 4.3167 | 3.8922 | 3.5034 | 3.1014 | 2.6116 | 2.1473 | -0.81902 | -4.8282 | -9.6629 | 4.0745 | 4.0204 | 3.9071 | 3.6275 | 3.4357 | 3.2908 | 3.1051 | 2.9081 | 2.6255 | 0.87751 | -1.0541 | -2.4092
LOVEDEAN GSP | HAVANT BSP | LEIGH PARK PRIMARY | MINIMUM HEADROOM | SU 72144 07875 | NO | YES | 3.857 | 16.9288 | 16.9553 | 16.938 | 16.8145 | 16.5849 | 16.1533 | 15.6349 | 15.0012 | 14.4165 | 11.4737 | 9.7982 | 8.5696 | 19.188 | 19.0829 | 18.8594 | 18.5686 | 18.1216 | 17.6737 | 17.1563 | 16.5155 | 15.9298 | 13.4339 | 10.9992 | 5.9706 | 17.9961 | 18.0033 | 17.94 | 17.7818 | 17.5012 | 17.1359 | 16.688 | 16.1237 | 15.5859 | 12.7502 | 11.1482 | 9.9604
|  | LEIGH PARK PRIMARY | EE |  |  |  |  | 16.9288 | 17.0339 | 16.9982 | 16.9747 | 16.9216 | 16.6767 | 16.2584 | 15.7849 | 15.3533 | 12.1971 | 10.0043 | 8.5696 | 19.188 | 19.1553 | 18.9094 | 18.6726 | 18.3298 | 18.0012 | 17.5196 | 16.9931 | 16.5135 | 13.8339 | 11.7726 | 9.5043 | 17.9961 | 18.0696 | 17.9655 | 17.8931 | 17.7543 | 17.5206 | 17.1441 | 16.7165 | 16.3012 | 13.2655 | 11.2369 | 9.9604
|  | LEIGH PARK PRIMARY | HT |  |  |  |  | 16.94 | 16.9553 | 16.938 | 16.8145 | 16.5849 | 16.1533 | 15.6349 | 15.0012 | 14.4165 | 11.4737 | 9.7982 | 8.8471 | 19.189 | 19.0829 | 18.8594 | 18.5686 | 18.1216 | 17.6737 | 17.1563 | 16.5155 | 15.9298 | 13.4339 | 12.3369 | 11.8757 | 18.0084 | 18.0033 | 17.94 | 17.7818 | 17.5012 | 17.1359 | 16.688 | 16.1237 | 15.5859 | 12.7502 | 11.1482 | 10.3084
|  | LEIGH PARK PRIMARY | HE |  |  |  |  | 16.941 | 17.0512 | 17.0237 | 16.9982 | 16.9298 | 16.6941 | 16.2859 | 15.8512 | 15.4196 | 12.9818 | 11.6094 | 10.5594 | 19.19 | 19.1573 | 18.9135 | 18.6808 | 18.3308 | 18.0002 | 17.5114 | 17.0175 | 16.5216 | 14.1063 | 12.5053 | 10.341 | 18.0094 | 18.092 | 17.9992 | 17.9155 | 17.7645 | 17.5441 | 17.1798 | 16.7849 | 16.3686 | 13.989 | 12.7022 | 11.7757
|  | LEIGH PARK PRIMARY | FB |  |  |  |  | 17.0635 | 17.2186 | 17.3237 | 17.3349 | 17.4706 | 17.4482 | 17.4257 | 17.3747 | 17.2737 | 16.0553 | 13.1257 | 11.3073 | 19.2839 | 19.3073 | 19.2747 | 19.1675 | 19.1675 | 18.841 | 18.6226 | 18.338 | 17.9971 | 15.6492 | 10.9992 | 5.9706 | 18.1349 | 18.2329 | 18.29 | 18.2329 | 18.2818 | 18.2339 | 18.1706 | 18.0818 | 17.9543 | 16.9043 | 14.0931 | 12.4308
BRAMLEY (BASI) GSP | READING BSP | LITTLE HUNGERFORD PRIMARY | MINIMUM HEADROOM | SU 75372 72019 | NO | YES | 10.533 | 7.8033 | 7.5931 | 7.2023 | 6.3257 | 5.3114 | 3.2257 | 0.99308 | -1.3753 | -3.4977 | -10.5926 | -15.4069 | -17.8661 | 12.041 | 11.6859 | 11.3166 | 10.7176 | 10.0023 | 8.8441 | 7.5472 | 6.1043 | 4.8717 | 0.95329 | -1.9039 | -7.512 | 9.3512 | 9.0614 | 8.6431 | 7.8349 | 6.9074 | 5.2196 | 3.4451 | 1.5268 | -0.15182 | -5.8263 | -9.3243 | -10.7794
|  | LITTLE HUNGERFORD PRIMARY | EE |  |  |  |  | 7.8033 | 7.6349 | 7.4196 | 6.8512 | 6.2084 | 4.4768 | 2.3696 | 0.31757 | -1.3998 | -8.0222 | -12.7222 | -15.4549 | 12.0441 | 11.7135 | 11.4023 | 10.9012 | 10.3308 | 9.3145 | 8.1033 | 6.7686 | 5.6788 | 1.0451 | -1.9039 | -4.2875 | 9.3512 | 9.091 | 8.791 | 8.1982 | 7.5339 | 6.0941 | 4.4237 | 2.7145 | 1.3084 | -4.1488 | -7.6386 | -9.4549
|  | LITTLE HUNGERFORD PRIMARY | HT |  |  |  |  | 7.8063 | 7.5931 | 7.2023 | 6.3257 | 5.3114 | 3.2257 | 0.99308 | -1.3753 | -3.4977 | -10.5926 | -15.4069 | -17.8661 | 12.041 | 11.6859 | 11.3166 | 10.7176 | 10.0023 | 8.8441 | 7.5472 | 6.1043 | 4.8717 | 0.95329 | -0.83855 | -1.3763 | 9.3553 | 9.0614 | 8.6431 | 7.8349 | 6.9074 | 5.2196 | 3.4451 | 1.5268 | -0.15182 | -5.8263 | -9.3243 | -10.7794
|  | LITTLE HUNGERFORD PRIMARY | HE |  |  |  |  | 7.8125 | 7.6543 | 7.4441 | 6.8237 | 6.1288 | 4.4921 | 2.4625 | 0.41145 | -1.312 | -6.961 | -10.7253 | -12.9232 | 12.0431 | 11.7135 | 11.4002 | 10.8941 | 10.3135 | 9.3145 | 8.1094 | 6.7788 | 5.6829 | 1.3308 | -1.2783 | -3.8437 | 9.3594 | 9.1084 | 8.8135 | 8.187 | 7.4839 | 6.1063 | 4.4819 | 2.7849 | 1.3768 | -3.3549 | -6.0324 | -7.5692
|  | LITTLE HUNGERFORD PRIMARY | FB |  |  |  |  | 8.2176 | 8.5155 | 8.6472 | 8.5441 | 8.4594 | 8.1186 | 7.7155 | 7.2686 | 6.8431 | 3.7492 | -0.12937 | -2.6324 | 12.2931 | 12.3257 | 12.2135 | 11.9053 | 11.6186 | 11.0553 | 10.4594 | 9.8339 | 9.1155 | 4.6114 | -1.2161 | -7.512 | 9.7859 | 10.0125 | 10.1084 | 9.9104 | 9.7727 | 9.3798 | 8.9594 | 8.4992 | 7.9961 | 4.8206 | 1.2308 | -1.0457
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW PRIMARY | MINIMUM HEADROOM | SU 86037 87794 | NO | NO | 4.852 | 3.3885 | 3.4966 | 3.4344 | 3.0956 | 2.6211 | 1.6864 | 0.63949 | -0.45847 | -1.5758 | -5.4503 | -8.633 | -10.3513 | 20.2548 | 20.2446 | 20.0538 | 19.6313 | 19.0007 | 18.4191 | 17.6803 | 16.8579 | 15.9905 | 13.5283 | 12.4109 | 9.0089 | 4.4028 | 4.3895 | 4.3313 | 4.0548 | 3.6589 | 3.0038 | 2.2681 | 1.4956 | 0.71398 | -2.0258 | -4.1728 | -5.3595
|  | LITTLE MARLOW PRIMARY | EE |  |  |  |  | 3.3895 | 3.4966 | 3.4415 | 3.1905 | 2.866 | 1.9405 | 0.9548 | -0.075816 | -1.1238 | -4.7003 | -7.7156 | -9.4626 | 20.2568 | 20.2456 | 20.067 | 19.665 | 19.1028 | 18.4783 | 17.7732 | 16.9844 | 16.1456 | 13.7048 | 12.4109 | 10.9885 | 4.4048 | 4.3895 | 4.3323 | 4.0864 | 3.765 | 3.0793 | 2.3558 | 1.6007 | 0.83031 | -1.6972 | -3.7268 | -4.8993
|  | LITTLE MARLOW PRIMARY | HT |  |  |  |  | 3.4242 | 3.5517 | 3.4344 | 3.0956 | 2.6211 | 1.6864 | 0.63949 | -0.45847 | -1.5758 | -5.4503 | -8.633 | -10.3513 | 20.2579 | 20.2507 | 20.0538 | 19.6313 | 19.0007 | 18.4191 | 17.6803 | 16.8579 | 15.9905 | 13.5283 | 12.713 | 12.7191 | 4.4272 | 4.4344 | 4.3395 | 4.0558 | 3.6589 | 3.0038 | 2.2681 | 1.4956 | 0.71398 | -2.0258 | -4.1728 | -5.3595
|  | LITTLE MARLOW PRIMARY | HE |  |  |  |  | 3.3885 | 3.4977 | 3.4385 | 3.1436 | 2.7732 | 1.8477 | 0.83949 | -0.21357 | -1.2819 | -4.1411 | -6.9452 | -8.0166 | 20.2548 | 20.2446 | 20.066 | 19.6619 | 19.0915 | 18.4772 | 17.7517 | 16.9466 | 16.1028 | 13.9364 | 12.6589 | 11.3701 | 4.4028 | 4.3895 | 4.3313 | 4.0548 | 3.6997 | 3.016 | 2.2772 | 1.5007 | 0.71806 | -1.3748 | -3.2381 | -4.0013
|  | LITTLE MARLOW PRIMARY | FB |  |  |  |  | 3.7844 | 3.816 | 3.9119 | 4.0221 | 3.9936 | 3.9058 | 3.7487 | 3.5426 | 3.3211 | 1.7048 | -0.46765 | -1.784 | 20.7017 | 20.4701 | 20.364 | 20.3742 | 20.1456 | 19.916 | 19.5813 | 19.1905 | 18.8007 | 16.1956 | 12.7344 | 9.0089 | 4.6579 | 4.6528 | 4.667 | 4.6977 | 4.6119 | 4.5221 | 4.3711 | 4.1915 | 4.0038 | 2.7119 | 1.1528 | 0.32929
NURSLING GSP | ROWNHAMS BSP | LORDSHILL PRIMARY | MINIMUM HEADROOM | SU 38746 16055 | NO | YES | 7.682 | 10.7181 | 10.7906 | 10.7712 | 10.7518 | 10.6212 | 10.5079 | 10.3334 | 10.1283 | 9.8202 | 7.4345 | 6.4661 | 5.8681 | 12.22 | 12.2118 | 12.1414 | 12.0659 | 11.7598 | 11.569 | 11.2557 | 10.9036 | 10.5475 | 8.0781 | 5.1271 | 1.2067 | 11.5171 | 11.563 | 11.5416 | 11.5416 | 11.261 | 11.0896 | 10.7988 | 10.463 | 10.1273 | 7.5681 | 6.712 | 6.2304
|  | LORDSHILL PRIMARY | EE |  |  |  |  | 10.7181 | 10.7906 | 10.7804 | 10.7743 | 10.6722 | 10.5222 | 10.3334 | 10.1304 | 9.8671 | 7.7926 | 6.4661 | 5.8681 | 12.22 | 12.2149 | 12.1536 | 12.1332 | 11.8404 | 11.5792 | 11.2904 | 10.9414 | 10.5965 | 8.0781 | 6.4169 | 4.8792 | 11.5171 | 11.563 | 11.5416 | 11.56 | 11.3488 | 11.0998 | 10.8212 | 10.4916 | 10.1681 | 7.8947 | 6.712 | 6.2304
|  | LORDSHILL PRIMARY | HT |  |  |  |  | 10.7222 | 10.7926 | 10.7712 | 10.7518 | 10.6212 | 10.5079 | 10.3355 | 10.1283 | 9.8202 | 7.4345 | 6.4916 | 6.0865 | 12.223 | 12.2149 | 12.1414 | 12.1026 | 11.7598 | 11.569 | 11.2557 | 10.9036 | 10.5475 | 8.3506 | 7.6618 | 7.2496 | 11.5222 | 11.5702 | 11.5426 | 11.5416 | 11.261 | 11.0896 | 10.7988 | 10.463 | 10.1273 | 7.5681 | 6.8008 | 6.5263
|  | LORDSHILL PRIMARY | HE |  |  |  |  | 10.7243 | 10.8039 | 10.7967 | 10.7977 | 10.7008 | 10.561 | 10.3885 | 10.209 | 10.0008 | 8.1865 | 7.362 | 6.9947 | 12.223 | 12.22 | 12.1618 | 12.1383 | 11.8608 | 11.5914 | 11.2914 | 10.9812 | 10.6547 | 8.2475 | 6.8016 | 5.3353 | 11.5263 | 11.5804 | 11.5712 | 11.5834 | 11.3773 | 11.1314 | 10.8528 | 10.5722 | 10.2763 | 8.2498 | 7.4957 | 7.212
|  | LORDSHILL PRIMARY | FB |  |  |  |  | 10.7957 | 10.8988 | 10.9436 | 10.9712 | 11.0069 | 11.0498 | 11.0294 | 10.9926 | 10.9498 | 10.4896 | 8.4926 | 7.6355 | 12.2302 | 12.2118 | 12.1496 | 12.0659 | 11.9516 | 11.821 | 11.5975 | 11.3659 | 11.1149 | 9.1241 | 5.1271 | 1.2067 | 11.6232 | 11.71 | 11.7528 | 11.7855 | 11.8181 | 11.863 | 11.8406 | 11.7967 | 11.7212 | 10.7916 | 8.4161 | 7.5926
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LOVE LANE PRIMARY | MINIMUM HEADROOM | SU 47334 68495 | NO | NO | 12.567 | 11.7167 | 11.2106 | 11.0127 | 10.6198 | 10.1076 | 9.3637 | 8.3055 | 6.7504 | 3.6606 | -0.1598 | -4.3782 | -8.122 | 14.1473 | 13.6351 | 13.5473 | 13.3729 | 13.1484 | 12.8637 | 12.0963 | 10.4555 | 6.931 | 2.78 | -1.4516 | -6.3955 | 11.3984 | 10.9708 | 10.8147 | 10.5127 | 10.1188 | 9.582 | 8.6024 | 6.882 | 3.3249 | -0.70469 | -4.919 | -9.3578
|  | LOVE LANE PRIMARY | EE |  |  |  |  | 11.7167 | 11.5443 | 11.0167 | 10.6882 | 10.2167 | 9.5096 | 8.7524 | 7.7708 | 6.5892 | 3.0147 | -2.2771 | -4.4027 | 14.1484 | 14.0473 | 13.5688 | 13.4341 | 13.2392 | 12.9902 | 12.5871 | 11.8494 | 10.7586 | 7.1116 | 1.3392 | -1.1578 | 11.3984 | 11.2606 | 10.8147 | 10.5729 | 10.2188 | 9.7178 | 9.0963 | 8.2127 | 7.0596 | 3.3035 | -2.671 | -4.8149
|  | LOVE LANE PRIMARY | HT |  |  |  |  | 11.7249 | 11.2106 | 11.0127 | 10.6198 | 10.1076 | 9.3637 | 8.3055 | 7.1371 | 5.2678 | 0.94224 | -4.3782 | -7.8486 | 14.1484 | 13.6351 | 13.5473 | 13.3729 | 13.1484 | 12.8637 | 12.0963 | 11.1422 | 9.2259 | 5.4422 | 0.57592 | -2.5537 | 11.4065 | 10.9708 | 10.8147 | 10.5127 | 10.1188 | 9.582 | 8.6024 | 7.5106 | 5.5147 | 1.1729 | -4.322 | -7.7424
|  | LOVE LANE PRIMARY | HE |  |  |  |  | 11.7208 | 11.5524 | 11.0269 | 10.681 | 10.2004 | 9.5259 | 8.5504 | 6.7504 | 3.6606 | -0.1598 | -4.1629 | -8.122 | 14.1473 | 14.0463 | 13.5647 | 13.4269 | 13.2351 | 12.9882 | 12.2708 | 10.4555 | 6.931 | 2.78 | -1.4516 | -6.3955 | 11.4035 | 11.2698 | 10.83 | 10.5718 | 10.2055 | 9.728 | 8.8127 | 6.882 | 3.3249 | -0.70469 | -4.919 | -9.3578
|  | LOVE LANE PRIMARY | FB |  |  |  |  | 11.8739 | 11.8229 | 11.7545 | 11.3218 | 11.1514 | 10.929 | 10.678 | 10.3729 | 9.8208 | 7.5637 | 4.7167 | 2.5861 | 14.2453 | 14.1902 | 14.131 | 13.6688 | 13.5963 | 13.4035 | 13.0912 | 12.7157 | 12.0453 | 9.1259 | 4.6484 | 0.073878 | 11.5443 | 11.5055 | 11.4586 | 11.0912 | 10.9637 | 10.7933 | 10.5422 | 10.2249 | 9.6086 | 7.279 | 4.0514 | 1.2851
COWLEY GSP | YARNTON BSP | LOVELACE ROAD PRIMARY | MINIMUM HEADROOM | SP 50395 10376 | YES | YES | 13.402 | -2.8343 | 23.1708 | 22.9004 | 22.7157 | 22.2984 | 21.6902 | 21.0443 | 20.3688 | 19.6637 | 18.5922 | 18.1453 | 18.0157 | -0.65163 | 23.7759 | 23.582 | 23.429 | 23.0943 | 22.6004 | 22.0647 | 21.479 | 20.9137 | 20.029 | 18.3984 | 16.2147 | -2.1588 | 22.8473 | 22.63 | 22.4831 | 22.1453 | 21.6127 | 21.031 | 20.4433 | 19.8524 | 18.9137 | 18.5239 | 18.3504
|  | LOVELACE ROAD PRIMARY | EE |  |  |  |  | -2.772 | 23.2963 | 23.0678 | 22.9239 | 22.8861 | 22.3616 | 21.7892 | 21.1943 | 20.5494 | 18.9902 | 18.2422 | 18.0157 | -0.61082 | 23.8647 | 23.7045 | 23.5943 | 23.5698 | 23.1667 | 22.7004 | 22.2076 | 21.6361 | 20.1473 | 19.2402 | 18.3555 | -2.1098 | 22.9463 | 22.7678 | 22.6504 | 22.6351 | 22.1973 | 21.7086 | 21.2004 | 20.5718 | 19.1708 | 18.5239 | 18.3504
|  | LOVELACE ROAD PRIMARY | HT |  |  |  |  | -2.8343 | 23.1708 | 22.9004 | 22.7157 | 22.2984 | 21.6902 | 21.0443 | 20.3688 | 19.6637 | 18.5922 | 18.1453 | 18.1892 | -0.65163 | 23.7759 | 23.582 | 23.429 | 23.0943 | 22.6004 | 22.0647 | 21.479 | 20.9137 | 20.029 | 19.5902 | 19.4055 | -2.1588 | 22.8473 | 22.63 | 22.4831 | 22.1453 | 21.6127 | 21.031 | 20.4433 | 19.8524 | 18.9137 | 18.5545 | 18.6198
|  | LOVELACE ROAD PRIMARY | HE |  |  |  |  | -2.771 | 23.3035 | 23.0769 | 22.928 | 22.8851 | 22.3637 | 21.7851 | 21.1188 | 20.5473 | 19.1943 | 18.6198 | 18.4841 | -0.61184 | 23.8647 | 23.7045 | 23.5933 | 23.5698 | 23.1627 | 22.6861 | 22.1096 | 21.6076 | 20.1902 | 19.3208 | 18.4371 | -2.1088 | 22.9535 | 22.7769 | 22.6535 | 22.6351 | 22.1973 | 21.7045 | 21.0984 | 20.5678 | 19.3392 | 18.8371 | 18.7259
|  | LOVELACE ROAD PRIMARY | FB |  |  |  |  | -2.6771 | 23.4433 | 23.2657 | 23.18 | 23.1463 | 22.9463 | 22.5545 | 22.2004 | 21.8678 | 20.3382 | 19.4688 | 19.0718 | -0.57408 | 23.8973 | 23.7473 | 23.6412 | 23.5443 | 23.332 | 22.9167 | 22.5361 | 22.1769 | 20.178 | 18.3984 | 16.2147 | -2.0129 | 23.0861 | 22.9514 | 22.879 | 22.8555 | 22.7004 | 22.3708 | 22.0524 | 21.7545 | 20.2576 | 19.6943 | 19.3443
MANNINGTON GSP | ARNEWOOD BSP | LYMINGTON PRIMARY | MINIMUM HEADROOM | SZ 31720 96856 | NO | NO | 3.408 | 10.9776 | 10.7704 | 10.349 | 9.5786 | 8.7592 | 7.3959 | 5.9163 | 4.4143 | 2.9276 | -2.9173 | -7.749 | -10.25 | 14.6143 | 14.4429 | 14.0837 | 13.6051 | 12.9418 | 12.1796 | 11.199 | 10.0265 | 9.1602 | 5.7724 | 3.1541 | 0.44286 | 12.2449 | 12.1459 | 11.798 | 11.2255 | 10.5092 | 9.4 | 8.0663 | 6.5582 | 5.3745 | 0.75816 | -2.7122 | -4.1735
|  | LYMINGTON PRIMARY | EE |  |  |  |  | 11.0122 | 10.9602 | 10.499 | 9.8041 | 9.2214 | 7.9163 | 6.4622 | 5.0255 | 3.7194 | -1.15 | -5.698 | -8.1051 | 14.649 | 14.5959 | 14.199 | 13.7 | 13.2133 | 12.5418 | 11.6173 | 10.5663 | 9.7867 | 5.9745 | 3.1541 | 1.3255 | 12.2878 | 12.3276 | 11.9541 | 11.4276 | 10.9653 | 9.9878 | 8.7245 | 7.3684 | 6.3041 | 1.902 | -1.5704 | -3.2327
|  | LYMINGTON PRIMARY | HT |  |  |  |  | 10.9776 | 10.7704 | 10.349 | 9.5786 | 8.7592 | 7.3959 | 5.9163 | 4.4143 | 2.9276 | -2.9173 | -7.749 | -10.25 | 14.6143 | 14.4429 | 14.0837 | 13.6051 | 12.9418 | 12.1796 | 11.199 | 10.0265 | 9.1602 | 5.7724 | 3.6765 | 3.1265 | 12.2449 | 12.1459 | 11.798 | 11.2255 | 10.5092 | 9.4 | 8.0663 | 6.5582 | 5.3745 | 0.75816 | -2.7122 | -4.1735
|  | LYMINGTON PRIMARY | HE |  |  |  |  | 11.0031 | 10.9531 | 10.4908 | 9.8061 | 9.1459 | 7.7898 | 6.3 | 4.7898 | 3.4286 | -0.3898 | -3.8582 | -5.5408 | 14.6265 | 14.5755 | 14.1776 | 13.7694 | 13.1847 | 12.5 | 11.5949 | 10.4969 | 9.7255 | 6.3816 | 4.3959 | 2.7622 | 12.2694 | 12.3133 | 11.9388 | 11.4653 | 10.9112 | 9.902 | 8.6469 | 7.2214 | 6.1469 | 2.55 | 0.12755 | -1.0082
|  | LYMINGTON PRIMARY | FB |  |  |  |  | 11.2286 | 11.2735 | 11.1888 | 10.8541 | 10.7082 | 10.4837 | 10.1816 | 9.8898 | 9.55 | 7.4724 | 4.5837 | 2.499 | 14.9245 | 14.7653 | 14.6847 | 14.3673 | 14.1163 | 13.7765 | 13.3367 | 12.8367 | 12.2418 | 8.9214 | 4.8265 | 0.44286 | 12.6408 | 12.648 | 12.6888 | 12.4561 | 12.3735 | 12.1939 | 11.9143 | 11.5959 | 11.1122 | 8.5459 | 5.6857 | 3.7112
MELKSHAM GSP | CHIPPENHAM BSP | LYNEHAM PRIMARY | MINIMUM HEADROOM | ST 99348 80481 | NO | YES | 2.627 | 3.4222 | 3.3906 | 17.7957 | 17.5375 | 17.1222 | 16.5283 | 15.9885 | 15.3048 | 14.7151 | 12.6671 | 11.01 | 9.9651 | 6.6207 | 6.5635 | 19.8355 | 19.7181 | 19.4395 | 19.1161 | 18.7712 | 18.2997 | 17.9181 | 16.5681 | 15.7661 | 15.0977 | 4.8589 | 4.8314 | 18.463 | 18.2671 | 17.9181 | 17.4436 | 17.0059 | 16.4263 | 15.9436 | 14.261 | 13.1375 | 12.5865
|  | LYNEHAM PRIMARY | EE |  |  |  |  | 3.4222 | 3.3906 | 17.7977 | 17.5742 | 17.1936 | 16.6232 | 16.1008 | 15.5742 | 15.0467 | 13.0151 | 11.4844 | 10.5671 | 6.6227 | 6.5645 | 19.8355 | 19.7344 | 19.4834 | 19.162 | 18.7997 | 18.4293 | 18.064 | 16.6171 | 15.7661 | 15.2426 | 4.8589 | 4.8314 | 18.4651 | 18.2916 | 17.9793 | 17.5191 | 17.0773 | 16.6314 | 16.1865 | 14.5293 | 13.4416 | 12.8855
|  | LYNEHAM PRIMARY | HT |  |  |  |  | 3.4242 | 3.3946 | 17.7957 | 17.5375 | 17.1222 | 16.5283 | 15.9885 | 15.3048 | 14.7151 | 12.6671 | 11.01 | 9.9651 | 6.6227 | 6.5635 | 19.8355 | 19.7181 | 19.4395 | 19.1161 | 18.7712 | 18.2997 | 17.9181 | 16.5681 | 15.9202 | 15.7732 | 4.86 | 4.8334 | 18.463 | 18.2671 | 17.9181 | 17.4436 | 17.0059 | 16.4263 | 15.9436 | 14.261 | 13.1375 | 12.5865
|  | LYNEHAM PRIMARY | HE |  |  |  |  | 3.4232 | 3.3936 | 17.8008 | 17.5906 | 17.1793 | 16.6191 | 16.0681 | 15.5253 | 14.9875 | 13.3497 | 12.062 | 11.2242 | 6.6207 | 6.5635 | 19.8365 | 19.7681 | 19.4793 | 19.1793 | 18.8069 | 18.4355 | 18.0773 | 16.7579 | 16.1916 | 15.6416 | 4.86 | 4.8324 | 18.4671 | 18.3232 | 17.9702 | 17.5253 | 17.064 | 16.6079 | 16.164 | 14.7671 | 13.9528 | 13.4202
|  | LYNEHAM PRIMARY | FB |  |  |  |  | 3.5548 | 3.5742 | 18.1875 | 18.0783 | 17.9844 | 17.7844 | 17.6467 | 17.5457 | 17.3202 | 16.1457 | 14.8487 | 14.0283 | 6.7258 | 6.7043 | 20.2028 | 20.1426 | 20.063 | 19.8038 | 19.613 | 19.4753 | 19.2314 | 18.0089 | 16.5202 | 15.0977 | 4.9467 | 4.9548 | 18.8467 | 18.7906 | 18.7038 | 18.5355 | 18.3834 | 18.2906 | 18.0824 | 17.0314 | 15.8865 | 15.1742
FLEET-BRAMLEY GSP | BRACKNELL BSP | MVEE PRIMARY | MINIMUM HEADROOM | SU 98120 65945 | NO | NO | 4.024 | 19.8561 | 19.7327 | 19.5071 | 19.2918 | 19.0806 | 18.9388 | 18.7908 | 18.6337 | 18.4633 | 17.9561 | 17.598 | 17.4959 | 17.4194 | 17.3714 | 17.302 | 17.2347 | 17.1194 | 17.0316 | 16.9704 | 16.8755 | 16.7908 | 16.4163 | 16.2082 | 15.9061 | 18.5316 | 18.4827 | 18.3551 | 18.2337 | 18.098 | 18.001 | 17.8939 | 17.7888 | 17.6684 | 17.3071 | 17.0592 | 16.998
|  | MVEE PRIMARY | EE |  |  |  |  | 19.8561 | 19.7327 | 19.5071 | 19.2918 | 19.0806 | 18.9388 | 18.7908 | 18.6337 | 18.4633 | 18.0388 | 17.7418 | 17.6102 | 17.4214 | 17.3714 | 17.3031 | 17.2347 | 17.1327 | 17.0612 | 16.9735 | 16.9224 | 16.8398 | 16.4469 | 16.2082 | 16.05 | 18.5327 | 18.4827 | 18.3551 | 18.2337 | 18.098 | 18.001 | 17.8939 | 17.7929 | 17.6684 | 17.349 | 17.1612 | 17.0888
|  | MVEE PRIMARY | HT |  |  |  |  | 19.8571 | 19.7459 | 19.5704 | 19.3735 | 19.152 | 18.9949 | 18.8622 | 18.7153 | 18.5469 | 17.9561 | 17.598 | 17.4959 | 17.4194 | 17.3745 | 17.3112 | 17.2408 | 17.1194 | 17.0316 | 16.9704 | 16.8755 | 16.7908 | 16.4163 | 16.2765 | 16.2867 | 18.5327 | 18.4878 | 18.3888 | 18.2745 | 18.1276 | 18.0194 | 17.9276 | 17.8173 | 17.6918 | 17.3071 | 17.0592 | 16.998
|  | MVEE PRIMARY | HE |  |  |  |  | 19.8571 | 19.7337 | 19.5082 | 19.299 | 19.0847 | 18.9398 | 18.8092 | 18.6337 | 18.4796 | 18.1735 | 17.9714 | 17.899 | 17.4224 | 17.3714 | 17.302 | 17.2347 | 17.1316 | 17.0602 | 16.9908 | 16.9133 | 16.8449 | 16.5796 | 16.449 | 16.3224 | 18.5316 | 18.4837 | 18.3551 | 18.2378 | 18.099 | 18.001 | 17.9092 | 17.7888 | 17.6796 | 17.4316 | 17.3071 | 17.2714
|  | MVEE PRIMARY | FB |  |  |  |  | 19.9173 | 19.8418 | 19.7112 | 19.5786 | 19.4816 | 19.4765 | 19.4633 | 19.4357 | 19.4122 | 19.1908 | 18.9439 | 18.7755 | 17.4531 | 17.4214 | 17.3827 | 17.3337 | 17.2949 | 17.2827 | 17.2827 | 17.2663 | 17.2418 | 16.9918 | 16.4796 | 15.9061 | 18.5735 | 18.5367 | 18.4878 | 18.4184 | 18.3602 | 18.3582 | 18.349 | 18.3245 | 18.3031 | 18.1204 | 17.9051 | 17.7837
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON PRIMARY | MINIMUM HEADROOM | SY 59138 97747 | NO | NO | 0.852 | 6.2714 | 6.2969 | 6.1888 | 6.0469 | 5.8439 | 5.6367 | 5.2765 | 4.9327 | 4.6122 | 3.7592 | 3.0337 | 2.5602 | 8.3786 | 8.3551 | 8.1306 | 7.9602 | 7.702 | 7.6245 | 7.3541 | 7.0551 | 6.8531 | 5.9327 | 5.6306 | 5.5153 | 7.6235 | 7.6102 | 7.4 | 7.2071 | 6.9194 | 6.8041 | 6.4592 | 6.1388 | 5.8398 | 4.8765 | 4.4388 | 4.3286
|  | MAIDEN NEWTON PRIMARY | EE |  |  |  |  | 6.2724 | 6.2969 | 6.1888 | 6.0602 | 5.8735 | 5.6949 | 5.3602 | 5.0449 | 4.7388 | 3.7592 | 3.0888 | 2.7286 | 8.3796 | 8.3561 | 8.1367 | 7.9714 | 7.7408 | 7.649 | 7.3643 | 7.1071 | 6.8653 | 5.9816 | 5.6306 | 5.5316 | 7.6245 | 7.6102 | 7.4 | 7.2143 | 6.9367 | 6.8255 | 6.4929 | 6.1724 | 5.8724 | 4.8837 | 4.4469 | 4.3286
|  | MAIDEN NEWTON PRIMARY | HT |  |  |  |  | 6.2714 | 6.3051 | 6.2041 | 6.0786 | 5.8806 | 5.7214 | 5.4163 | 5.0653 | 4.8041 | 3.8 | 3.0337 | 2.5602 | 8.3786 | 8.3551 | 8.1306 | 7.9602 | 7.702 | 7.6245 | 7.3653 | 7.0551 | 6.8531 | 5.9327 | 5.6459 | 5.651 | 7.6235 | 7.6133 | 7.4041 | 7.2163 | 6.9194 | 6.8276 | 6.5255 | 6.1653 | 5.9133 | 4.8765 | 4.4388 | 4.3582
|  | MAIDEN NEWTON PRIMARY | HE |  |  |  |  | 6.2724 | 6.301 | 6.1939 | 6.0469 | 5.8439 | 5.6367 | 5.2765 | 4.9327 | 4.6122 | 3.9816 | 3.3551 | 2.9745 | 8.3786 | 8.3561 | 8.1357 | 7.9694 | 7.7357 | 7.6429 | 7.3541 | 7.099 | 6.8663 | 6.1714 | 5.9357 | 5.7959 | 7.6235 | 7.6112 | 7.4 | 7.2071 | 6.9224 | 6.8041 | 6.4592 | 6.1388 | 5.8398 | 5.0776 | 4.7194 | 4.5571
|  | MAIDEN NEWTON PRIMARY | FB |  |  |  |  | 6.3643 | 6.4194 | 6.4633 | 6.4806 | 6.5031 | 6.4745 | 6.3286 | 6.2765 | 6.249 | 5.5745 | 4.8204 | 4.3306 | 8.4255 | 8.4327 | 8.4163 | 8.3939 | 8.3561 | 8.2949 | 8.002 | 7.9173 | 7.8735 | 7.1418 | 6.4041 | 5.5153 | 7.7 | 7.7173 | 7.7224 | 7.7 | 7.6592 | 7.5908 | 7.3255 | 7.2337 | 7.2194 | 6.4255 | 5.6255 | 5.1551
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | MAIDENHEAD PRIMARY | MINIMUM HEADROOM | SU 86485 79800 | NO | NO | 12.207 | 17.7087 | 17.5566 | 28.4696 | 27.7665 | 26.9002 | 25.5522 | 24.1441 | 22.8012 | 21.8063 | 18.3676 | 16.7992 | 16.8186 | 23.2935 | 23.0731 | 30.6114 | 30.2135 | 29.6982 | 28.8451 | 27.7206 | 26.5135 | 25.5931 | 22.2563 | 20.188 | 15.8196 | 19.7628 | 19.623 | 28.7308 | 28.0614 | 27.2329 | 25.9941 | 24.7053 | 23.4053 | 22.4471 | 18.8339 | 17.2696 | 17.3431
|  | MAIDENHEAD PRIMARY | EE |  |  |  |  | 17.7087 | 17.5566 | 28.5176 | 27.8788 | 27.0849 | 25.9747 | 24.8778 | 23.8737 | 23.1012 | 19.7706 | 17.7216 | 17.1992 | 23.2966 | 23.0772 | 30.639 | 30.2604 | 29.7971 | 29.1084 | 28.1604 | 27.1369 | 26.3451 | 22.7043 | 20.4553 | 19.089 | 19.7628 | 19.623 | 28.7625 | 28.1461 | 27.389 | 26.3318 | 25.2859 | 24.2512 | 23.4696 | 19.9727 | 17.9471 | 17.4869
|  | MAIDENHEAD PRIMARY | HT |  |  |  |  | 17.7117 | 17.5587 | 28.4696 | 27.7665 | 26.9002 | 25.5522 | 24.1441 | 22.8012 | 21.8063 | 18.3676 | 16.7992 | 16.8186 | 23.2935 | 23.0731 | 30.6114 | 30.2135 | 29.6982 | 28.8451 | 27.7206 | 26.5135 | 25.5931 | 22.2563 | 21.0104 | 20.9778 | 19.7658 | 19.6281 | 28.7308 | 28.0614 | 27.2329 | 25.9941 | 24.7053 | 23.4053 | 22.4471 | 18.8339 | 17.2696 | 17.3431
|  | MAIDENHEAD PRIMARY | HE |  |  |  |  | 17.7158 | 17.5699 | 28.5431 | 27.89 | 27.1135 | 26.1125 | 24.9553 | 23.9747 | 23.2543 | 20.1931 | 18.7982 | 18.3125 | 23.2956 | 23.0772 | 30.639 | 30.2604 | 29.8114 | 29.1982 | 28.1931 | 27.1747 | 26.3982 | 22.8298 | 20.9349 | 19.4349 | 19.7689 | 19.6362 | 28.7859 | 28.1553 | 27.4084 | 26.4665 | 25.3492 | 24.3359 | 23.591 | 20.3645 | 19.0053 | 18.5665
|  | MAIDENHEAD PRIMARY | FB |  |  |  |  | 18.123 | 17.9893 | 29.1961 | 28.7441 | 28.2757 | 27.6033 | 26.9665 | 26.6931 | 26.3359 | 23.7594 | 20.7992 | 19.1747 | 23.4517 | 23.27 | 30.9533 | 30.7043 | 30.4063 | 30.0104 | 29.439 | 28.941 | 28.4094 | 24.8002 | 20.188 | 15.8196 | 20.0822 | 19.9842 | 29.4441 | 29.091 | 28.6747 | 28.0431 | 27.4512 | 27.1125 | 26.7278 | 24.0186 | 20.9829 | 19.3696
MELKSHAM GSP | CHIPPENHAM BSP | MALMESBURY PRIMARY | MINIMUM HEADROOM | ST 92288 87493 | NO | YES | 1.603 | 1.9959 | 1.9969 | 1.9173 | 1.8663 | 1.7051 | 1.3929 | 0.97449 | 0.59184 | 0.24184 | -1 | -1.6673 | -1.851 | 4.4673 | 4.4439 | 4.3143 | 4.2378 | 4.0092 | 3.6673 | 3.2327 | 2.8245 | 2.4531 | 1.0143 | 0.046939 | -1.4776 | 3.2449 | 3.2337 | 3.1684 | 3.1327 | 2.9949 | 2.7796 | 2.348 | 1.949 | 1.5806 | 0.23163 | -0.45408 | -0.6602
|  | MALMESBURY PRIMARY | EE |  |  |  |  | 1.9959 | 1.9969 | 1.9276 | 1.8888 | 1.7459 | 1.5173 | 1.1316 | 0.80102 | 0.51429 | -0.72959 | -1.4949 | -1.7939 | 4.4673 | 4.4449 | 4.3184 | 4.2561 | 4.0582 | 3.7531 | 3.3255 | 2.9449 | 2.6061 | 1.0143 | 0.046939 | -0.61735 | 3.2449 | 3.2337 | 3.1755 | 3.1561 | 3.0418 | 2.85 | 2.4724 | 2.1051 | 1.7908 | 0.40306 | -0.36939 | -0.6602
|  | MALMESBURY PRIMARY | HT |  |  |  |  | 1.9959 | 1.998 | 1.9173 | 1.8663 | 1.7051 | 1.3929 | 0.97449 | 0.59184 | 0.24184 | -1 | -1.6673 | -1.851 | 4.4673 | 4.4439 | 4.3143 | 4.2378 | 4.0092 | 3.6673 | 3.2327 | 2.8245 | 2.4531 | 1.05 | 0.36735 | 0.20204 | 3.2449 | 3.2337 | 3.1684 | 3.1327 | 2.9949 | 2.7796 | 2.348 | 1.949 | 1.5806 | 0.23163 | -0.45408 | -0.60408
|  | MALMESBURY PRIMARY | HE |  |  |  |  | 1.9959 | 1.999 | 1.9276 | 1.899 | 1.7459 | 1.5041 | 1.1122 | 0.80816 | 0.5102 | -0.58878 | -1.1296 | -1.4194 | 4.4684 | 4.4449 | 4.3184 | 4.2663 | 4.0551 | 3.7418 | 3.3112 | 2.9582 | 2.6143 | 1.1439 | 0.41122 | -0.24898 | 3.2459 | 3.2347 | 3.1776 | 3.1643 | 3.0408 | 2.8449 | 2.4531 | 2.1194 | 1.7929 | 0.57245 | 0.055102 | -0.2102
|  | MALMESBURY PRIMARY | FB |  |  |  |  | 2.0847 | 2.1133 | 2.1531 | 2.1755 | 2.1571 | 2.0582 | 1.9878 | 1.9122 | 1.8204 | 1.0796 | 0.0020408 | -0.79592 | 4.5592 | 4.5541 | 4.5612 | 4.55 | 4.5082 | 4.2878 | 4.1143 | 3.902 | 3.6806 | 2.252 | 0.48367 | -1.4776 | 3.3357 | 3.351 | 3.3786 | 3.3949 | 3.3816 | 3.3061 | 3.2378 | 3.1704 | 3.0929 | 2.3112 | 1.2112 | 0.35612
MINETY GSP | SWINDON BSP | MANCHESTER ROAD PRIMARY | MINIMUM HEADROOM | SU 15254 85130 | NO | NO | 5.993 | 20.6051 | 20.5194 | 20.1582 | 19.4051 | 18.2847 | 16.8102 | 15.0663 | 13.6949 | 12.2786 | 6.4939 | 2.5133 | 0.28978 | 21.9326 | 21.8582 | 21.6939 | 21.4245 | 20.9235 | 20.3633 | 19.6755 | 19.0775 | 18.1949 | 13.3377 | 9.8888 | 2.7735 | 19.1459 | 19.0102 | 18.6347 | 18.1122 | 17.2684 | 16.1643 | 14.7918 | 13.7143 | 12.5969 | 7.0439 | 3.5306 | 1.6153
|  | MANCHESTER ROAD PRIMARY | EE |  |  |  |  | 20.6051 | 20.5194 | 20.1582 | 19.4051 | 18.2847 | 16.8102 | 15.0663 | 13.6949 | 12.2786 | 6.4939 | 2.5133 | 0.28978 | 21.9326 | 21.8582 | 21.6939 | 21.4245 | 21.0255 | 20.4755 | 19.7786 | 19.1704 | 18.201 | 13.3377 | 10.2663 | 7.25 | 19.1459 | 19.0102 | 18.6347 | 18.1122 | 17.2877 | 16.1643 | 14.7918 | 13.7143 | 12.5969 | 7.0439 | 3.5306 | 1.6153
|  | MANCHESTER ROAD PRIMARY | HT |  |  |  |  | 20.6214 | 20.551 | 20.2122 | 19.4908 | 18.3112 | 16.8888 | 15.1704 | 13.8306 | 12.452 | 6.6775 | 3.199 | 1.4367 | 21.9377 | 21.8643 | 21.702 | 21.4388 | 20.9235 | 20.3633 | 19.6755 | 19.0775 | 18.2408 | 14.15 | 12.1684 | 11.2184 | 19.1694 | 19.053 | 18.7061 | 18.1775 | 17.2684 | 16.1918 | 14.8367 | 13.7806 | 12.6918 | 7.2888 | 4.3806 | 3.0347
|  | MANCHESTER ROAD PRIMARY | HE |  |  |  |  | 20.6214 | 20.5479 | 20.201 | 19.4775 | 18.3582 | 16.9643 | 15.2653 | 13.9479 | 12.5714 | 8.1571 | 5.4837 | 3.9918 | 21.9377 | 21.8643 | 21.7041 | 21.4388 | 21.0439 | 20.5041 | 19.8102 | 19.201 | 18.1949 | 14.3775 | 11.6194 | 8.9786 | 19.1735 | 19.0592 | 18.7061 | 18.1765 | 17.3408 | 16.2806 | 14.9398 | 13.8939 | 12.801 | 8.7163 | 6.2786 | 5.0571
|  | MANCHESTER ROAD PRIMARY | FB |  |  |  |  | 20.7255 | 20.7194 | 20.4347 | 20.0286 | 19.4235 | 18.5214 | 17.5684 | 16.6857 | 15.8377 | 12.2306 | 8.7163 | 5.7133 | 21.9735 | 21.9082 | 21.7337 | 21.5082 | 21.2673 | 20.8857 | 20.4112 | 19.9398 | 19.4847 | 15.3857 | 9.8888 | 2.7735 | 19.3367 | 19.2694 | 18.9775 | 18.6143 | 18.2561 | 17.6255 | 16.9551 | 16.2847 | 15.65 | 12.6112 | 9.1684 | 5.9265
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON PRIMARY | MINIMUM HEADROOM | SU 07592 05256 | NO | NO | 2.182 | 6.6566 | 6.424 | 6.2617 | 6.0505 | 5.6648 | 5.0301 | 4.3434 | 3.5883 | 2.8005 | 0.24847 | -1.4781 | -2.0934 | 5.5265 | 5.3265 | 5.199 | 5.0602 | 4.7561 | 4.3796 | 3.9633 | 3.45 | 2.9173 | 1.3459 | 0.54592 | 0.12551 | 5.8143 | 5.5439 | 5.3663 | 5.1959 | 4.8337 | 4.3245 | 3.7541 | 3.1092 | 2.4429 | 0.38367 | -0.76735 | -1.0031
|  | MANNINGTON PRIMARY | EE |  |  |  |  | 6.6597 | 6.425 | 6.3015 | 6.126 | 5.8026 | 5.1781 | 4.5015 | 3.7485 | 2.9699 | 0.67806 | -0.87092 | -1.5505 | 5.5276 | 5.3306 | 5.2224 | 5.1061 | 4.8388 | 4.4827 | 4.0929 | 3.5969 | 3.0837 | 1.3888 | 0.54592 | 0.19694 | 5.8173 | 5.548 | 5.4 | 5.2592 | 4.9469 | 4.4531 | 3.9041 | 3.2684 | 2.6153 | 0.69286 | -0.38878 | -0.73367
|  | MANNINGTON PRIMARY | HT |  |  |  |  | 6.6566 | 6.424 | 6.2617 | 6.0505 | 5.6648 | 5.0301 | 4.3434 | 3.5883 | 2.8005 | 0.24847 | -1.4781 | -2.0934 | 5.5265 | 5.3265 | 5.199 | 5.0602 | 4.7561 | 4.3796 | 3.9633 | 3.45 | 2.9173 | 1.3459 | 0.70408 | 0.75714 | 5.8143 | 5.5439 | 5.3663 | 5.1959 | 4.8337 | 4.3245 | 3.7541 | 3.1092 | 2.4429 | 0.38367 | -0.76735 | -1.0031
|  | MANNINGTON PRIMARY | HE |  |  |  |  | 6.6597 | 6.4321 | 6.2954 | 6.1015 | 5.7566 | 5.1138 | 4.4026 | 3.6199 | 2.8301 | 1.1066 | -0.21071 | -0.89133 | 5.5276 | 5.3337 | 5.2173 | 5.0918 | 4.8224 | 4.4816 | 4.0796 | 3.5816 | 3.0867 | 1.8796 | 1.1714 | 0.58673 | 5.8184 | 5.5551 | 5.3918 | 5.2367 | 4.9143 | 4.4194 | 3.8459 | 3.1969 | 2.55 | 1.1541 | 0.2449 | -0.22449
|  | MANNINGTON PRIMARY | FB |  |  |  |  | 6.8056 | 6.8209 | 6.8311 | 6.6474 | 6.5526 | 6.4485 | 6.3046 | 6.1648 | 5.9628 | 4.7852 | 3.5781 | 2.5301 | 5.6031 | 5.601 | 5.5806 | 5.3939 | 5.2929 | 5.1622 | 4.9929 | 4.8286 | 4.5908 | 3.2714 | 1.8041 | 0.12551 | 5.952 | 5.9571 | 5.9602 | 5.7194 | 5.6153 | 5.5245 | 5.3837 | 5.251 | 5.0408 | 3.8714 | 2.7776 | 1.7939
LOVEDEAN GSP | CHICHESTER BSP | MARKET PRIMARY | MINIMUM HEADROOM | SU 86479 04732 | NO | YES | 4.773 | 10.6608 | 10.5884 | 10.4537 | 10.2976 | 9.9833 | 9.5139 | 8.9445 | 8.3302 | 7.7159 | 5.2465 | 3.5118 | 2.7435 | 12.1524 | 12.1035 | 12.0218 | 11.8922 | 11.5535 | 11.1637 | 10.6912 | 10.1565 | 9.578 | 7.7698 | 4.9718 | 0.36367 | 10.8322 | 10.7914 | 10.7016 | 10.5792 | 10.3618 | 10.07 | 9.7088 | 9.319 | 8.8924 | 6.5108 | 5.022 | 4.4639
|  | MARKET PRIMARY | EE |  |  |  |  | 10.6649 | 10.6251 | 10.5588 | 10.5384 | 10.3578 | 9.9863 | 9.519 | 9.0322 | 8.6516 | 6.3129 | 4.2955 | 3.1435 | 12.1565 | 12.1259 | 12.0739 | 12.0188 | 11.7249 | 11.3688 | 10.9667 | 10.5086 | 10.1912 | 7.7698 | 5.9473 | 4.1729 | 10.8322 | 10.8078 | 10.7598 | 10.721 | 10.5924 | 10.3853 | 10.1088 | 9.819 | 9.5771 | 7.3618 | 5.6608 | 4.7384
|  | MARKET PRIMARY | HT |  |  |  |  | 10.6608 | 10.5884 | 10.4537 | 10.2976 | 9.9833 | 9.5139 | 8.9445 | 8.3302 | 7.7159 | 5.2465 | 3.5118 | 2.7435 | 12.1524 | 12.1035 | 12.0218 | 11.8922 | 11.5535 | 11.1637 | 10.6912 | 10.1565 | 9.578 | 7.8259 | 6.8371 | 6.3994 | 10.8333 | 10.7914 | 10.7016 | 10.5792 | 10.3618 | 10.07 | 9.7088 | 9.319 | 8.8924 | 6.5108 | 5.022 | 4.4639
|  | MARKET PRIMARY | HE |  |  |  |  | 10.6771 | 10.6496 | 10.6016 | 10.5486 | 10.3404 | 10.0016 | 9.6016 | 9.1006 | 8.7322 | 7.0098 | 5.6578 | 4.8404 | 12.1535 | 12.1167 | 12.0667 | 12.0167 | 11.7096 | 11.3473 | 11.0106 | 10.4657 | 10.1259 | 7.9963 | 6.4014 | 4.7412 | 10.8322 | 10.8057 | 10.7608 | 10.7047 | 10.5547 | 10.3506 | 10.0976 | 9.7965 | 9.5547 | 7.9169 | 6.7516 | 6.1302
|  | MARKET PRIMARY | FB |  |  |  |  | 10.8098 | 10.8435 | 10.8761 | 10.9169 | 10.9384 | 10.972 | 10.8629 | 10.7027 | 10.6098 | 9.4894 | 7.6853 | 6.1567 | 12.1943 | 12.1749 | 12.1422 | 12.1076 | 11.9402 | 11.7882 | 11.5035 | 11.1249 | 10.8341 | 8.4514 | 4.9718 | 0.36367 | 10.9231 | 10.9465 | 10.9598 | 10.971 | 10.9506 | 10.9547 | 10.8669 | 10.7629 | 10.6822 | 9.9067 | 8.42 | 6.8118
MELKSHAM GSP | WEST GRAFTON BSP | MARLBOROUGH SOUTH PRIMARY | MINIMUM HEADROOM | SU 19293 68264 | NO | NO | 1.533 | 1.6821 | 1.6862 | 1.7128 | 1.4597 | 1.1138 | 0.51173 | -0.17908 | -0.94439 | -1.6107 | -4.2117 | -6.4536 | -7.7077 | 5.3765 | 5.2959 | 5.2316 | 4.9898 | 4.6704 | 4.2531 | 3.7592 | 3.0827 | 2.6531 | 0.68469 | -0.72857 | -2.4367 | 3.2888 | 3.2939 | 3.3133 | 3.1541 | 2.8592 | 2.3745 | 1.8061 | 1.0776 | 0.56224 | -1.6684 | -3.2857 | -4.0694
|  | MARLBOROUGH SOUTH PRIMARY | EE |  |  |  |  | 1.6821 | 1.6872 | 1.7168 | 1.4852 | 1.1464 | 0.57296 | -0.11378 | -0.88827 | -1.4699 | -4.1413 | -6.3791 | -7.6505 | 5.3765 | 5.299 | 5.2357 | 5.0082 | 4.6745 | 4.2765 | 3.7765 | 3.1653 | 2.7806 | 0.68469 | -0.72857 | -1.6776 | 3.2888 | 3.2939 | 3.3153 | 3.1724 | 2.8704 | 2.4071 | 1.8347 | 1.1541 | 0.67653 | -1.5755 | -3.2316 | -4.0694
|  | MARLBOROUGH SOUTH PRIMARY | HT |  |  |  |  | 1.6821 | 1.6883 | 1.7128 | 1.4648 | 1.1321 | 0.54643 | -0.12704 | -0.94439 | -1.5597 | -4.2117 | -6.4536 | -7.7077 | 5.3765 | 5.298 | 5.2316 | 4.9898 | 4.6704 | 4.2531 | 3.7592 | 3.0827 | 2.6531 | 0.76939 | -0.28061 | -0.56837 | 3.2898 | 3.2939 | 3.3133 | 3.1541 | 2.8602 | 2.3827 | 1.8214 | 1.0776 | 0.56224 | -1.6684 | -3.2857 | -4.0051
|  | MARLBOROUGH SOUTH PRIMARY | HE |  |  |  |  | 1.6832 | 1.6862 | 1.7199 | 1.4597 | 1.1138 | 0.51173 | -0.17908 | -0.83929 | -1.6107 | -3.875 | -5.7005 | -6.5628 | 5.3776 | 5.2959 | 5.2367 | 5.002 | 4.6867 | 4.2786 | 3.7878 | 3.3306 | 2.7408 | 0.77347 | -0.30612 | -1.0847 | 3.2898 | 3.2939 | 3.3163 | 3.1551 | 2.8592 | 2.3745 | 1.8061 | 1.2602 | 0.58776 | -1.3816 | -2.6622 | -3.198
|  | MARLBOROUGH SOUTH PRIMARY | FB |  |  |  |  | 2.0291 | 2.0372 | 2.0638 | 2.0505 | 2.0505 | 1.9301 | 1.7689 | 1.6056 | 1.3923 | 0.013776 | -1.7985 | -2.8934 | 5.7878 | 5.5663 | 5.4704 | 5.3592 | 5.2786 | 5.0694 | 4.8061 | 4.5531 | 4.2378 | 2.4031 | -0.066327 | -2.4367 | 3.6041 | 3.5745 | 3.599 | 3.5918 | 3.6316 | 3.5469 | 3.4163 | 3.2592 | 3.05 | 1.7265 | -0.0040816 | -1.0449
NURSLING GSP | ROWNHAMS BSP | MAYBUSH PRIMARY | MINIMUM HEADROOM | SU 38426 14930 | NO | YES | 4.799 | 1.8388 | 1.9296 | 2.0153 | 1.8194 | 1.4857 | 0.95411 | 0.35717 | -0.38161 | -0.99793 | -4.0765 | -6.3418 | -7.4694 | 6.6003 | 6.6003 | 6.5493 | 6.3595 | 6.135 | 5.8146 | 5.4105 | 4.8462 | 4.3697 | 1.7401 | -3.264 | -9.7752 | 3.3661 | 3.3834 | 3.4018 | 2.9998 | 2.6661 | 2.213 | 1.7008 | 1.061 | 0.52834 | -1.9615 | -3.8064 | -4.6961
|  | MAYBUSH PRIMARY | EE |  |  |  |  | 1.8388 | 1.9296 | 2.0276 | 1.8827 | 1.6551 | 1.0735 | 0.47962 | -0.19997 | -0.87752 | -3.8847 | -6.3418 | -7.4694 | 6.6003 | 6.6003 | 6.6278 | 6.4115 | 6.2544 | 5.9289 | 5.5197 | 5.0105 | 4.5023 | 1.8125 | -0.6038 | -3.1354 | 3.3661 | 3.3834 | 3.4018 | 3.0488 | 2.8212 | 2.3375 | 1.8457 | 1.2671 | 0.69365 | -1.79 | -3.8064 | -4.6961
|  | MAYBUSH PRIMARY | HT |  |  |  |  | 1.8541 | 1.9531 | 2.0153 | 1.8194 | 1.4857 | 0.95411 | 0.35717 | -0.38161 | -0.99793 | -4.0765 | -6.0826 | -6.7439 | 6.6044 | 6.6003 | 6.6044 | 6.3595 | 6.135 | 5.8146 | 5.4105 | 4.8462 | 4.3697 | 2.6125 | 1.6023 | 1.1309 | 3.3855 | 3.4049 | 3.4192 | 2.9998 | 2.6661 | 2.213 | 1.7008 | 1.061 | 0.52834 | -1.9615 | -3.5145 | -3.9502
|  | MAYBUSH PRIMARY | HE |  |  |  |  | 1.8694 | 1.997 | 2.1061 | 1.9674 | 1.7255 | 1.2664 | 0.6888 | 0.12248 | -0.50916 | -2.8418 | -4.4071 | -5.2092 | 6.6105 | 6.6176 | 6.6523 | 6.438 | 6.2829 | 6.0054 | 5.5738 | 5.1125 | 4.5891 | 2.0921 | -0.11911 | -2.5201 | 3.3926 | 3.4232 | 3.4732 | 3.1018 | 2.8671 | 2.4773 | 1.9722 | 1.4773 | 0.91814 | -1.0584 | -2.2564 | -2.791
|  | MAYBUSH PRIMARY | FB |  |  |  |  | 1.9857 | 2.1623 | 2.3051 | 2.4225 | 2.5327 | 2.5174 | 2.4572 | 2.2847 | 2.0439 | 0.52146 | -1.8612 | -3.5877 | 6.6084 | 6.6003 | 6.5493 | 6.4605 | 6.335 | 6.0289 | 5.6635 | 5.1676 | 4.7156 | 1.7401 | -3.264 | -9.7752 | 3.563 | 3.6661 | 3.7324 | 3.7722 | 3.8406 | 3.7743 | 3.6579 | 3.2875 | 3.0457 | 1.5345 | -0.57268 | -2.1145
MELKSHAM GSP | NORRINGTON BSP | MELKSHAM TOWN PRIMARY | MINIMUM HEADROOM | ST 90170 64096 | NO | YES | 8.264 | 6.9899 | 6.7991 | 6.1614 | 5.1481 | 3.8777 | 2.1063 | 0.25321 | -1.6886 | -3.2835 | -9.7499 | -15.0703 | -18.1121 | 14.1338 | 13.9593 | 13.4991 | 12.8757 | 12.0257 | 11.1022 | 9.9848 | 8.7093 | 7.7532 | 3.8124 | 0.62668 | -3.0662 | 12.4308 | 12.3675 | 11.9185 | 11.144 | 10.1522 | 8.8532 | 7.4246 | 5.8869 | 4.6573 | -0.28659 | -4.0182 | -5.8743
|  | MELKSHAM TOWN PRIMARY | EE |  |  |  |  | 6.9899 | 6.8012 | 6.1787 | 5.2308 | 4.0226 | 2.3042 | 0.55219 | -1.0386 | -2.705 | -8.907 | -14.0662 | -16.9672 | 14.1348 | 13.9614 | 13.5104 | 12.9246 | 12.1063 | 11.2216 | 10.1797 | 9.2114 | 8.1338 | 3.8124 | 0.62668 | -1.5192 | 12.4308 | 12.3695 | 11.9338 | 11.2083 | 10.2624 | 9.0063 | 7.6604 | 6.4277 | 5.1165 | 0.31137 | -3.4233 | -5.3437
|  | MELKSHAM TOWN PRIMARY | HT |  |  |  |  | 6.991 | 6.8032 | 6.1614 | 5.1481 | 3.8777 | 2.1063 | 0.25321 | -1.6886 | -3.2835 | -9.7499 | -15.0703 | -18.1121 | 14.1348 | 13.9624 | 13.4991 | 12.8757 | 12.0257 | 11.1022 | 9.9848 | 8.7093 | 7.7532 | 3.8899 | 1.4899 | 0.65423 | 12.4318 | 12.3695 | 11.9185 | 11.144 | 10.1522 | 8.8532 | 7.4246 | 5.8869 | 4.6573 | -0.28659 | -4.0182 | -5.8743
|  | MELKSHAM TOWN PRIMARY | HE |  |  |  |  | 6.9899 | 6.7991 | 6.1787 | 5.2083 | 3.9757 | 2.242 | 0.48484 | -1.1182 | -2.8243 | -7.9866 | -12.1458 | -14.3703 | 14.1338 | 13.9593 | 13.5104 | 12.9175 | 12.092 | 11.2032 | 10.1726 | 9.2104 | 8.1124 | 4.2848 | 1.945 | -0.060057 | 12.4308 | 12.3675 | 11.9338 | 11.191 | 10.2328 | 8.9665 | 7.6236 | 6.3899 | 5.0491 | 1.0175 | -1.8509 | -3.3386
|  | MELKSHAM TOWN PRIMARY | FB |  |  |  |  | 7.3787 | 7.2787 | 6.9808 | 6.5032 | 5.9124 | 5.2655 | 4.7032 | 4.1797 | 3.8226 | 0.71341 | -3.2203 | -5.6999 | 14.3981 | 14.2001 | 13.9461 | 13.5552 | 13.0665 | 12.5195 | 11.944 | 11.3369 | 10.8512 | 7.0675 | 2.0236 | -3.0662 | 12.7226 | 12.7297 | 12.6165 | 12.3012 | 11.8522 | 11.3665 | 10.9104 | 10.4604 | 10.144 | 7.3899 | 3.9522 | 1.6961
NURSLING GSP |  | MARCHWOOD PRIMARY | MINIMUM HEADROOM | SU 39234 11008 | NO | NO | 1.124 | 17.8567 | 17.6812 | 17.3975 | 17.2077 | 16.9679 | 16.6567 | 16.3955 | 16.0659 | 15.6904 | 14.4873 | 13.4679 | 13.1455 | 17.9986 | 17.8251 | 17.6465 | 17.5618 | 17.3567 | 17.1486 | 16.972 | 16.7057 | 16.4047 | 15.6118 | 14.8047 | 13.6812 | 18.2567 | 18.0761 | 17.8873 | 17.7894 | 17.5649 | 17.321 | 17.0996 | 16.8067 | 16.472 | 15.5057 | 14.7159 | 14.5465
|  | MARCHWOOD PRIMARY | EE |  |  |  |  | 17.8628 | 17.8516 | 17.52 | 17.2924 | 17.1067 | 16.7792 | 16.5496 | 16.2445 | 15.8761 | 14.7179 | 13.6965 | 13.2955 | 18.0037 | 17.9945 | 17.7598 | 17.6026 | 17.4598 | 17.2394 | 17.0904 | 16.8455 | 16.5547 | 15.6128 | 14.8047 | 14.3741 | 18.2588 | 18.2486 | 18.0067 | 17.8312 | 17.6894 | 17.4292 | 17.2435 | 16.969 | 16.6598 | 15.6945 | 14.8741 | 14.6159
|  | MARCHWOOD PRIMARY | HT |  |  |  |  | 17.8567 | 17.6812 | 17.3975 | 17.2077 | 16.9679 | 16.6567 | 16.3955 | 16.0659 | 15.6904 | 14.4873 | 13.4679 | 13.1455 | 17.9986 | 17.8251 | 17.6465 | 17.5618 | 17.3567 | 17.1486 | 16.972 | 16.7057 | 16.4047 | 15.6118 | 15.0149 | 14.9312 | 18.2567 | 18.0761 | 17.8873 | 17.7894 | 17.5649 | 17.321 | 17.0996 | 16.8067 | 16.472 | 15.5057 | 14.7159 | 14.5465
|  | MARCHWOOD PRIMARY | HE |  |  |  |  | 17.8639 | 17.8526 | 17.5179 | 17.2822 | 17.0741 | 16.7577 | 16.5537 | 16.2384 | 15.871 | 14.9159 | 14.1853 | 13.8333 | 18.0026 | 17.9914 | 17.7557 | 17.5965 | 17.4343 | 17.2282 | 17.1047 | 16.8608 | 16.5679 | 15.7475 | 15.1537 | 14.6475 | 18.2588 | 18.2475 | 18.0077 | 17.8251 | 17.6567 | 17.4108 | 17.2537 | 16.9751 | 16.6598 | 15.8669 | 15.3067 | 15.0465
|  | MARCHWOOD PRIMARY | FB |  |  |  |  | 17.9016 | 17.8986 | 17.8894 | 17.7037 | 17.572 | 17.3761 | 17.3302 | 17.2373 | 17.122 | 16.5873 | 15.8557 | 15.1435 | 18.0322 | 18.0384 | 18.0261 | 17.8373 | 17.7159 | 17.5424 | 17.4414 | 17.3067 | 17.1475 | 16.3333 | 15.1782 | 13.6812 | 18.2965 | 18.3077 | 18.2935 | 18.0955 | 17.9639 | 17.8649 | 17.8282 | 17.7792 | 17.6884 | 17.169 | 16.5088 | 15.8353
LOVEDEAN GSP | HAVANT BSP | MEYRICK ROAD PRIMARY | MINIMUM HEADROOM | SU 70849 06469 | NO | YES | 1.294 | 8.3684 | 8.2449 | 7.8939 | 7.4112 | 6.7633 | 5.8255 | 4.698 | 3.4949 | 2.3673 | -2.0367 | -5.2776 | -6.751 | 12.7735 | 12.6061 | 12.2592 | 11.898 | 11.4306 | 10.8071 | 10.0184 | 9.1459 | 8.3429 | 5.3592 | 1.348 | -5.0439 | 9.4837 | 9.3755 | 9.0276 | 8.6082 | 8.0653 | 7.2949 | 6.3429 | 5.3143 | 4.3541 | 0.6398 | -1.9122 | -2.8837
|  | MEYRICK ROAD PRIMARY | EE |  |  |  |  | 8.3684 | 8.3949 | 7.9673 | 7.601 | 7.0551 | 6.1765 | 5.1755 | 4.0796 | 3.0745 | -0.96633 | -4.2071 | -5.8918 | 12.7745 | 12.752 | 12.3235 | 12.0245 | 11.6265 | 11.0582 | 10.3653 | 9.5745 | 8.8704 | 5.3592 | 2.5092 | -0.16531 | 9.4837 | 9.5082 | 9.0847 | 8.7684 | 8.3408 | 7.6327 | 6.801 | 5.8796 | 5.0398 | 1.5847 | -1.0867 | -2.4061
|  | MEYRICK ROAD PRIMARY | HT |  |  |  |  | 8.3745 | 8.2449 | 7.8939 | 7.4112 | 6.7633 | 5.8255 | 4.698 | 3.4949 | 2.3673 | -2.0367 | -5.2776 | -6.751 | 12.7735 | 12.6061 | 12.2592 | 11.898 | 11.4306 | 10.8071 | 10.0184 | 9.1459 | 8.3429 | 5.6551 | 4.0837 | 3.4122 | 9.4908 | 9.3755 | 9.0276 | 8.6082 | 8.0653 | 7.2949 | 6.3429 | 5.3143 | 4.3541 | 0.6398 | -1.9122 | -2.8837
|  | MEYRICK ROAD PRIMARY | HE |  |  |  |  | 8.3816 | 8.4173 | 8.0051 | 7.6133 | 7.0429 | 6.1857 | 5.2418 | 4.1653 | 3.1602 | 0.040816 | -2.4582 | -3.7092 | 12.7745 | 12.752 | 12.3255 | 12.0245 | 11.6204 | 11.0551 | 10.3857 | 9.5959 | 8.8806 | 5.7612 | 3.0908 | 0.4398 | 9.4949 | 9.5316 | 9.1204 | 8.7816 | 8.3306 | 7.6429 | 6.8571 | 5.95 | 5.1112 | 2.449 | 0.40306 | -0.58469
|  | MEYRICK ROAD PRIMARY | FB |  |  |  |  | 8.6786 | 8.7755 | 8.9173 | 8.8184 | 8.798 | 8.4592 | 8.2214 | 8.0204 | 7.6684 | 5.6184 | 2.4633 | 0.47347 | 12.9276 | 12.8459 | 12.8214 | 12.5612 | 12.348 | 11.8163 | 11.3398 | 10.9 | 10.3296 | 6.8245 | 1.348 | -5.0439 | 9.7949 | 9.848 | 9.9796 | 9.8602 | 9.7959 | 9.5714 | 9.3592 | 9.1755 | 8.8561 | 6.9551 | 4.0673 | 2.2704
MELKSHAM GSP | ANDOVER BSP | MIDDLE WALLOP PRIMARY | MINIMUM HEADROOM | SU 30984 40155 | YES | NO | 0.705 | 3.6416 | 3.6334 | 3.4702 | 3.3773 | 3.2242 | 3.0293 | 2.8559 | 2.5885 | 2.3334 | 1.413 | 0.79974 | 0.41403 | 0.7852 | 0.77398 | 0.71276 | 0.6699 | 0.60255 | 0.53724 | 0.47194 | 0.36276 | 0.26276 | -0.097449 | -0.26786 | -0.51173 | 2.3541 | 2.349 | 2.2888 | 2.2408 | 2.1663 | 2.0806 | 1.9878 | 1.85 | 1.7194 | 1.2235 | 0.8949 | 0.72449
|  | MIDDLE WALLOP PRIMARY | EE |  |  |  |  | 3.6426 | 3.6334 | 3.4702 | 3.3773 | 3.2385 | 3.061 | 2.8753 | 2.6344 | 2.3722 | 1.413 | 0.79974 | 0.41403 | 0.78622 | 0.77398 | 0.71276 | 0.6699 | 0.60459 | 0.54337 | 0.47194 | 0.3699 | 0.26276 | -0.097449 | -0.26786 | -0.36582 | 2.3541 | 2.349 | 2.2888 | 2.2408 | 2.1663 | 2.0949 | 1.9969 | 1.8694 | 1.7388 | 1.2235 | 0.8949 | 0.72449
|  | MIDDLE WALLOP PRIMARY | HT |  |  |  |  | 3.6416 | 3.6355 | 3.4753 | 3.3865 | 3.2865 | 3.0538 | 2.9069 | 2.664 | 2.4191 | 1.5589 | 0.88444 | 0.43954 | 0.78622 | 0.77704 | 0.71378 | 0.67194 | 0.61173 | 0.53724 | 0.475 | 0.36276 | 0.26276 | -0.066837 | -0.18929 | -0.18724 | 2.3541 | 2.349 | 2.2918 | 2.2459 | 2.1837 | 2.0939 | 2.0092 | 1.8816 | 1.7561 | 1.2918 | 0.92857 | 0.72653
|  | MIDDLE WALLOP PRIMARY | HE |  |  |  |  | 3.6416 | 3.6334 | 3.4732 | 3.413 | 3.2242 | 3.0293 | 2.8559 | 2.5885 | 2.3334 | 1.6855 | 1.0538 | 0.69056 | 0.7852 | 0.77602 | 0.71378 | 0.68112 | 0.60255 | 0.53929 | 0.475 | 0.36684 | 0.26684 | -0.029082 | -0.18418 | -0.31684 | 2.3541 | 2.349 | 2.2908 | 2.249 | 2.1745 | 2.0806 | 1.9878 | 1.85 | 1.7194 | 1.3592 | 1.0255 | 0.86633
|  | MIDDLE WALLOP PRIMARY | FB |  |  |  |  | 3.7181 | 3.7426 | 3.7569 | 3.7457 | 3.7385 | 3.7365 | 3.5406 | 3.4446 | 3.3926 | 2.9038 | 2.3293 | 1.9253 | 0.82194 | 0.82398 | 0.81786 | 0.80255 | 0.79133 | 0.76786 | 0.6852 | 0.62908 | 0.58418 | 0.29439 | -0.10561 | -0.51173 | 2.4 | 2.4143 | 2.4214 | 2.4143 | 2.4082 | 2.3959 | 2.3173 | 2.2714 | 2.2327 | 1.9878 | 1.6827 | 1.4949
FLEET-BRAMLEY GSP | FERNHURST BSP | MIDHURST PRIMARY | MINIMUM HEADROOM | SU 88127 19555 | NO | NO | 2.687 | 16.7439 | 16.7755 | 16.5531 | 16.2102 | 15.7163 | 14.9439 | 14.1357 | 13.2755 | 12.4418 | 9.6082 | 7.1184 | 5.5439 | 18.999 | 18.9561 | 18.7378 | 18.5214 | 18.1541 | 17.7531 | 17.2531 | 16.7204 | 16.2255 | 14.4939 | 13.301 | 11.249 | 17.7888 | 17.7867 | 17.6031 | 17.3347 | 16.9265 | 16.3378 | 15.6959 | 15.0092 | 14.352 | 12.1255 | 10.4347 | 9.552
|  | MIDHURST PRIMARY | EE |  |  |  |  | 16.7531 | 16.8041 | 16.6929 | 16.4776 | 16.1786 | 15.4898 | 14.7816 | 14.0459 | 13.3541 | 10.6663 | 8.3643 | 7.0153 | 19.0041 | 18.9755 | 18.7888 | 18.6112 | 18.3541 | 17.9684 | 17.5051 | 17.0224 | 16.599 | 14.6316 | 13.301 | 12.3949 | 17.7959 | 17.8214 | 17.7031 | 17.5245 | 17.2663 | 16.7378 | 16.1663 | 15.5714 | 15.0255 | 12.8622 | 11.2122 | 10.3612
|  | MIDHURST PRIMARY | HT |  |  |  |  | 16.7439 | 16.7755 | 16.5531 | 16.2102 | 15.7163 | 14.9439 | 14.1357 | 13.2755 | 12.4418 | 9.6082 | 7.1184 | 5.5439 | 18.999 | 18.9561 | 18.7378 | 18.5214 | 18.1541 | 17.7531 | 17.2531 | 16.7204 | 16.2255 | 14.4939 | 13.55 | 13.2714 | 17.7888 | 17.7867 | 17.6031 | 17.3347 | 16.9265 | 16.3378 | 15.6959 | 15.0092 | 14.352 | 12.1255 | 10.4347 | 9.552
|  | MIDHURST PRIMARY | HE |  |  |  |  | 16.7541 | 16.8061 | 16.6939 | 16.4449 | 16.1143 | 15.4316 | 14.6908 | 13.9224 | 13.2061 | 11.1408 | 8.9918 | 8.0051 | 19.0031 | 18.9755 | 18.7908 | 18.6082 | 18.3439 | 17.9878 | 17.5153 | 17.0276 | 16.6041 | 14.8673 | 13.6347 | 12.8786 | 17.7969 | 17.8235 | 17.6847 | 17.5061 | 17.2286 | 16.7184 | 16.1255 | 15.5133 | 14.9531 | 13.2347 | 11.7092 | 11.1245
|  | MIDHURST PRIMARY | FB |  |  |  |  | 16.9122 | 17.0398 | 17.1327 | 17.2102 | 17.2898 | 17.048 | 16.8857 | 16.7122 | 16.5347 | 15.0582 | 13.148 | 11.9561 | 19.1235 | 19.1347 | 19.1296 | 19.1031 | 19.1082 | 18.7327 | 18.4765 | 18.2265 | 17.9755 | 16.1541 | 13.7408 | 11.249 | 17.9745 | 18.0776 | 18.1551 | 18.201 | 18.3102 | 18.0194 | 17.8612 | 17.6939 | 17.5224 | 16.1612 | 14.4796 | 13.449
AXMINSTER GSP | YEOVIL BSP | MILBORNE PORT PRIMARY | MINIMUM HEADROOM | ST 67929 19741 | YES | NO | 0.353 | 2.9168 | 2.9209 | 2.923 | 2.9138 | 2.8005 | 2.7056 | 2.6179 | 2.5219 | 2.3832 | 2.0413 | 1.8719 | 1.8454 | 2.4827 | 2.4653 | 2.4541 | 2.4327 | 2.3571 | 2.2867 | 2.2255 | 2.1296 | 1.999 | 1.5806 | 1.2071 | 0.51735 | 2.8837 | 2.8796 | 2.8745 | 2.8612 | 2.7571 | 2.6714 | 2.5898 | 2.4439 | 2.2255 | 1.8735 | 1.701 | 1.6888
|  | MILBORNE PORT PRIMARY | EE |  |  |  |  | 2.9179 | 2.9209 | 2.923 | 2.9158 | 2.8332 | 2.7617 | 2.7168 | 2.5668 | 2.3995 | 2.0413 | 1.9056 | 1.8781 | 2.4827 | 2.4673 | 2.4551 | 2.4347 | 2.3755 | 2.3163 | 2.2827 | 2.1551 | 2.0061 | 1.5806 | 1.3092 | 1.0582 | 2.8837 | 2.8796 | 2.8745 | 2.8622 | 2.7867 | 2.7153 | 2.6786 | 2.4847 | 2.2439 | 1.8735 | 1.7337 | 1.7184
|  | MILBORNE PORT PRIMARY | HT |  |  |  |  | 2.9168 | 2.923 | 2.925 | 2.9168 | 2.8005 | 2.7056 | 2.6179 | 2.5219 | 2.4097 | 2.073 | 1.9474 | 1.9679 | 2.4827 | 2.4653 | 2.4541 | 2.4327 | 2.3571 | 2.2867 | 2.2255 | 2.1296 | 2.0061 | 1.6857 | 1.552 | 1.5173 | 2.8837 | 2.8806 | 2.8755 | 2.8633 | 2.7571 | 2.6714 | 2.5898 | 2.4439 | 2.2531 | 1.9 | 1.7898 | 1.8112
|  | MILBORNE PORT PRIMARY | HE |  |  |  |  | 2.9179 | 2.9219 | 2.924 | 2.9138 | 2.8291 | 2.773 | 2.7158 | 2.5617 | 2.3832 | 2.0464 | 1.8719 | 1.8454 | 2.4827 | 2.4673 | 2.4571 | 2.4347 | 2.3755 | 2.3245 | 2.2816 | 2.1531 | 1.999 | 1.5827 | 1.2796 | 1.0184 | 2.8837 | 2.8796 | 2.8755 | 2.8612 | 2.7847 | 2.7265 | 2.6776 | 2.4786 | 2.2255 | 1.8755 | 1.701 | 1.6888
|  | MILBORNE PORT PRIMARY | FB |  |  |  |  | 2.9587 | 2.9862 | 3.0066 | 3.0077 | 2.9628 | 2.9566 | 2.9281 | 2.8944 | 2.8158 | 2.6281 | 2.4107 | 2.276 | 2.5133 | 2.5143 | 2.5102 | 2.4888 | 2.451 | 2.4153 | 2.3653 | 2.3163 | 2.2429 | 1.8551 | 1.2071 | 0.51735 | 2.9286 | 2.948 | 2.9582 | 2.9561 | 2.9163 | 2.9031 | 2.8735 | 2.8388 | 2.7643 | 2.5622 | 2.2622 | 2.1296
FLEET-BRAMLEY GSP | ALDERSHOT BSP | MILFORD PRIMARY | MINIMUM HEADROOM | SU 94719 43018 | NO | YES | 4.416 | 9.9568 | 9.9181 | 9.6262 | 9.2262 | 8.7844 | 8.2732 | 7.6262 | 6.915 | 6.3395 | 4.5905 | 3.7058 | 3.6038 | 14.766 | 14.6874 | 14.4211 | 14.0191 | 13.5619 | 13.0803 | 12.465 | 11.7701 | 11.2211 | 9.4313 | 8.613 | 6.1946 | 12.213 | 12.165 | 11.8823 | 11.5079 | 11.0864 | 10.5987 | 10.0007 | 9.3119 | 8.7619 | 7.0038 | 6.1834 | 6.166
|  | MILFORD PRIMARY | EE |  |  |  |  | 9.9681 | 9.9813 | 9.7477 | 9.4385 | 9.0915 | 8.7028 | 8.213 | 7.6385 | 7.2089 | 5.4558 | 4.4221 | 4.1038 | 14.7742 | 14.7201 | 14.4946 | 14.1497 | 13.7599 | 13.3446 | 12.8395 | 12.2354 | 11.7772 | 9.8252 | 8.613 | 7.8262 | 12.2232 | 12.216 | 11.9803 | 11.6803 | 11.3446 | 10.9477 | 10.4619 | 9.9028 | 9.4558 | 7.664 | 6.6956 | 6.4487
|  | MILFORD PRIMARY | HT |  |  |  |  | 9.9568 | 9.9181 | 9.6262 | 9.2262 | 8.7844 | 8.2732 | 7.6262 | 6.915 | 6.3395 | 4.5905 | 3.7058 | 3.6038 | 14.766 | 14.6874 | 14.4211 | 14.0191 | 13.5619 | 13.0803 | 12.465 | 11.7701 | 11.2211 | 9.4313 | 8.6793 | 8.6721 | 12.213 | 12.165 | 11.8823 | 11.5079 | 11.0864 | 10.5987 | 10.0007 | 9.3119 | 8.7619 | 7.0038 | 6.1834 | 6.166
|  | MILFORD PRIMARY | HE |  |  |  |  | 9.9701 | 9.9793 | 9.7487 | 9.4334 | 9.0783 | 8.7068 | 8.1895 | 7.6374 | 7.1987 | 5.8079 | 4.8517 | 4.5926 | 14.7742 | 14.7201 | 14.4966 | 14.1477 | 13.7538 | 13.3568 | 12.8221 | 12.2405 | 11.7793 | 10.1354 | 8.9793 | 8.1905 | 12.2242 | 12.215 | 11.9823 | 11.6772 | 11.3354 | 10.9558 | 10.4446 | 9.9068 | 9.4548 | 8.0058 | 7.115 | 6.9079
|  | MILFORD PRIMARY | FB |  |  |  |  | 10.1487 | 10.2374 | 10.2313 | 10.2619 | 10.1915 | 9.8742 | 9.7477 | 9.5334 | 9.3405 | 8.0426 | 6.515 | 5.6079 | 14.8966 | 14.8885 | 14.8028 | 14.7803 | 14.6374 | 14.2517 | 14.0089 | 13.6895 | 13.3793 | 11.367 | 8.8221 | 6.1946 | 12.4028 | 12.466 | 12.4497 | 12.4191 | 12.3426 | 12.113 | 11.9823 | 11.7579 | 11.5507 | 10.1354 | 8.5936 | 7.7079
MANNINGTON GSP | ARNEWOOD BSP | MILFORD-ON-SEA PRIMARY | MINIMUM HEADROOM | SZ 28252 93347 | NO | NO | 2.134 | 13.7268 | 13.4931 | 13.0696 | 12.4992 | 11.6656 | 10.3819 | 8.9278 | 7.5686 | 6.286 | 2.1023 | -1.1069 | -2.6844 | 14.7435 | 14.4976 | 14.165 | 13.8027 | 13.2752 | 12.6537 | 11.8629 | 11.1129 | 10.3068 | 7.8792 | 6.269 | 4.2088 | 14.0819 | 13.8319 | 13.4452 | 12.9686 | 12.2584 | 11.2952 | 10.1768 | 9.1248 | 8.0952 | 4.8574 | 2.6554 | 1.7748
|  | MILFORD-ON-SEA PRIMARY | EE |  |  |  |  | 13.7574 | 13.5574 | 13.2115 | 12.7778 | 12.1135 | 10.8819 | 9.489 | 8.2156 | 7.0574 | 3.487 | 0.57067 | -1.0181 | 14.7578 | 14.5272 | 14.2405 | 13.9303 | 13.4741 | 12.9129 | 12.1752 | 11.5017 | 10.7609 | 8.0313 | 6.269 | 5.0415 | 14.1043 | 13.8819 | 13.5584 | 13.1768 | 12.5911 | 11.6952 | 10.639 | 9.6717 | 8.739 | 5.7768 | 3.6339 | 2.5707
|  | MILFORD-ON-SEA PRIMARY | HT |  |  |  |  | 13.7268 | 13.4931 | 13.0696 | 12.4992 | 11.6656 | 10.3819 | 8.9278 | 7.5686 | 6.286 | 2.1023 | -1.1069 | -2.6844 | 14.7435 | 14.4976 | 14.165 | 13.8027 | 13.2752 | 12.6537 | 11.8629 | 11.1129 | 10.3068 | 7.8792 | 6.6068 | 6.3007 | 14.0819 | 13.8319 | 13.4452 | 12.9686 | 12.2584 | 11.2952 | 10.1768 | 9.1248 | 8.0952 | 4.8574 | 2.6554 | 1.7748
|  | MILFORD-ON-SEA PRIMARY | HE |  |  |  |  | 13.7584 | 13.5625 | 13.2043 | 12.7615 | 12.0758 | 10.8196 | 9.3758 | 8.0686 | 6.8696 | 4.1227 | 1.6013 | 0.48802 | 14.7568 | 14.5323 | 14.2292 | 13.9119 | 13.4456 | 12.8976 | 12.1476 | 11.4823 | 10.7405 | 8.5701 | 7.0221 | 5.8752 | 14.1043 | 13.887 | 13.5472 | 13.1605 | 12.5564 | 11.6564 | 10.5696 | 9.588 | 8.636 | 6.3901 | 4.5768 | 3.8135
|  | MILFORD-ON-SEA PRIMARY | FB |  |  |  |  | 13.989 | 13.9901 | 13.7686 | 13.7248 | 13.4533 | 13.1023 | 12.7329 | 12.3533 | 12.1054 | 10.1309 | 7.9431 | 6.5503 | 14.9058 | 14.8517 | 14.5343 | 14.4558 | 14.1823 | 13.8731 | 13.5496 | 13.1701 | 12.7884 | 10.2864 | 7.367 | 4.2088 | 14.3329 | 14.3227 | 14.0686 | 14.0329 | 13.7921 | 13.4992 | 13.2003 | 12.8462 | 12.5717 | 10.7084 | 8.7248 | 7.3931
MANNINGTON GSP | MANNINGTON BSP | MILL LANE PRIMARY | MINIMUM HEADROOM | SU 14691 05633 | NO | NO | 5.928 | 8.3829 | 8.3523 | 17.6595 | 17.334 | 16.8238 | 16.1085 | 15.1187 | 14.0217 | 12.9278 | 8.8452 | 7.5105 | 7.4544 | 11.9197 | 11.7615 | 20.3503 | 19.8676 | 19.1605 | 18.2299 | 16.9962 | 15.9187 | 14.8483 | 10.4748 | 8.4758 | 5.7656 | 8.4074 | 8.3003 | 17.2105 | 16.7085 | 15.9697 | 14.9993 | 13.7136 | 12.6023 | 11.4901 | 7.1391 | 5.6819 | 5.6003
|  | MILL LANE PRIMARY | EE |  |  |  |  | 8.4187 | 8.5238 | 17.8207 | 17.6207 | 17.2503 | 16.6911 | 15.886 | 14.9646 | 14.0462 | 9.984 | 8.4503 | 7.884 | 11.9411 | 11.888 | 20.4534 | 20.0483 | 19.4023 | 18.5717 | 17.4176 | 16.4462 | 15.4748 | 10.6983 | 8.4758 | 6.9738 | 8.4523 | 8.4503 | 17.3523 | 16.9564 | 16.3125 | 15.4809 | 14.3054 | 13.337 | 12.3605 | 7.9748 | 6.3034 | 5.6666
|  | MILL LANE PRIMARY | HT |  |  |  |  | 8.3829 | 8.3523 | 17.6595 | 17.334 | 16.8238 | 16.1085 | 15.1187 | 14.0217 | 12.9278 | 8.8452 | 7.5105 | 7.4544 | 11.9197 | 11.7615 | 20.3503 | 19.8676 | 19.1605 | 18.2299 | 16.9962 | 15.9187 | 14.8483 | 10.4748 | 8.8789 | 8.6166 | 8.4074 | 8.3003 | 17.2105 | 16.7085 | 15.9697 | 14.9993 | 13.7136 | 12.6023 | 11.4901 | 7.1391 | 5.6819 | 5.6003
|  | MILL LANE PRIMARY | HE |  |  |  |  | 8.4085 | 8.5136 | 17.8074 | 17.6034 | 17.236 | 16.6656 | 16.0238 | 14.9268 | 13.9932 | 10.7799 | 9.3768 | 8.9554 | 11.9319 | 11.8758 | 20.435 | 20.0207 | 19.3891 | 18.5258 | 17.6136 | 16.3993 | 15.4085 | 11.6013 | 9.5799 | 8.2034 | 8.4289 | 8.4309 | 17.3319 | 16.9238 | 16.2972 | 15.4309 | 14.5227 | 13.2911 | 12.2993 | 8.9125 | 7.4217 | 6.9666
|  | MILL LANE PRIMARY | FB |  |  |  |  | 8.6707 | 8.784 | 18.3738 | 18.2748 | 18.2044 | 17.9829 | 17.6707 | 17.4054 | 17.0289 | 14.9299 | 12.0523 | 9.9829 | 12.1197 | 12.0615 | 20.9064 | 20.6187 | 20.3636 | 19.9289 | 19.3411 | 18.8778 | 18.2085 | 14.735 | 10.3309 | 5.7656 | 8.7554 | 8.7554 | 18.0003 | 17.7901 | 17.637 | 17.3125 | 16.8248 | 16.4819 | 15.9146 | 13.2523 | 10.2432 | 7.8972
COWLEY GSP | DRAYTON BSP | MILTON PRIMARY | MINIMUM HEADROOM | SU 49992 92060 | NO | YES | 22.092 | 3.4989 | 2.6244 | 1.3927 | -0.42154 | -2.395 | -4.5287 | -6.9195 | -9.4389 | -11.7022 | -20.2481 | -25.2001 | -26.9022 | 9.0815 | 8.3846 | 7.5019 | 6.1295 | 4.6489 | 3.1325 | 1.3285 | -0.71542 | -2.5746 | -10.2522 | -14.4236 | -16.6675 | 6.4917 | 5.8203 | 4.8968 | 3.405 | 1.7887 | 0.022339 | -2.0277 | -4.2858 | -6.3358 | -14.7226 | -19.1328 | -20.5052
|  | MILTON PRIMARY | EE |  |  |  |  | 3.6387 | 2.9989 | 1.8672 | 0.62336 | -1.2205 | -3.5164 | -6.2838 | -8.943 | -11.2695 | -20.2481 | -25.2001 | -26.9022 | 9.1713 | 8.5999 | 7.804 | 6.9601 | 5.5958 | 4.053 | 1.7499 | -0.47154 | -2.4246 | -10.2522 | -14.4236 | -16.6675 | 6.5815 | 6.0601 | 5.2193 | 4.2652 | 2.7417 | 0.90499 | -1.6624 | -4.1307 | -6.2991 | -14.7226 | -19.1328 | -20.5052
|  | MILTON PRIMARY | HT |  |  |  |  | 3.4989 | 2.6244 | 1.3927 | -0.42154 | -2.395 | -4.5287 | -6.9195 | -9.4389 | -11.7022 | -19.9389 | -24.3777 | -25.7705 | 9.0815 | 8.3846 | 7.5019 | 6.1295 | 4.6489 | 3.1325 | 1.3285 | -0.71542 | -2.5746 | -9.0256 | -12.0511 | -12.8297 | 6.4917 | 5.8203 | 4.8968 | 3.405 | 1.7887 | 0.022339 | -2.0277 | -4.2858 | -6.3358 | -13.6011 | -17.3124 | -18.2195
|  | MILTON PRIMARY | HE |  |  |  |  | 3.6387 | 3.0019 | 1.9172 | 0.69479 | -0.62256 | -2.9389 | -5.346 | -7.5919 | -9.5777 | -16.7175 | -20.4144 | -21.6144 | 9.1693 | 8.5907 | 7.803 | 6.956 | 6.0397 | 4.407 | 2.7081 | 0.96826 | -0.57868 | -6.4491 | -9.3766 | -11.4001 | 6.5815 | 6.057 | 5.2448 | 4.2958 | 3.2591 | 1.355 | -0.65419 | -2.6256 | -4.3899 | -10.643 | -13.6236 | -14.5532
|  | MILTON PRIMARY | FB |  |  |  |  | 3.8713 | 3.4927 | 2.957 | 2.0356 | 0.68764 | -0.86236 | -2.4287 | -3.9634 | -5.0715 | -10.2664 | -14.5746 | -16.2491 | 9.3376 | 8.8907 | 8.406 | 7.6172 | 6.4632 | 5.1152 | 3.7734 | 2.4336 | 1.3866 | -3.8501 | -9.1705 | -14.0195 | 6.8601 | 6.4917 | 6.0601 | 5.3662 | 4.2111 | 2.9091 | 1.6111 | 0.31724 | -0.58174 | -5.1542 | -9.0093 | -10.6256
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON PRIMARY | MINIMUM HEADROOM | ST 96164 14520 | YES | NO | 1.122 | 2.8931 | 2.885 | 2.8727 | 2.7717 | 2.634 | 2.4666 | 2.2595 | 2.0666 | 1.9829 | 1.4452 | 0.99722 | 0.84008 | 4.313 | 4.3018 | 4.2855 | 4.1304 | 3.9334 | 3.7967 | 3.6039 | 3.4232 | 3.4049 | 2.913 | 2.7079 | 2.7528 | 2.5722 | 2.5641 | 2.5518 | 2.4661 | 2.3447 | 2.2345 | 2.0559 | 1.9039 | 1.8365 | 1.3896 | 1.0763 | 1.0365
|  | MINCHINGTON PRIMARY | EE |  |  |  |  | 2.8931 | 2.885 | 2.8727 | 2.8533 | 2.6482 | 2.4952 | 2.3156 | 2.137 | 2.0513 | 1.5033 | 1.086 | 0.98498 | 4.3141 | 4.3039 | 4.2896 | 4.2396 | 3.9416 | 3.8069 | 3.6457 | 3.462 | 3.4437 | 2.9569 | 2.7181 | 2.76 | 2.5732 | 2.5641 | 2.5528 | 2.5273 | 2.3569 | 2.2549 | 2.1049 | 1.9569 | 1.8947 | 1.4437 | 1.1386 | 1.1141
|  | MINCHINGTON PRIMARY | HT |  |  |  |  | 2.8942 | 2.8911 | 2.8727 | 2.7717 | 2.6421 | 2.487 | 2.2595 | 2.0789 | 1.9829 | 1.4452 | 0.99722 | 0.84008 | 4.3141 | 4.3018 | 4.2855 | 4.1304 | 3.9447 | 3.813 | 3.6039 | 3.4232 | 3.4049 | 2.913 | 2.7079 | 2.8273 | 2.5722 | 2.5671 | 2.5518 | 2.4661 | 2.3549 | 2.2488 | 2.0559 | 1.9039 | 1.8365 | 1.3896 | 1.0763 | 1.0365
|  | MINCHINGTON PRIMARY | HE |  |  |  |  | 2.8931 | 2.8891 | 2.8768 | 2.7789 | 2.634 | 2.4666 | 2.2615 | 2.0666 | 1.987 | 1.6227 | 1.3493 | 1.2044 | 4.313 | 4.3049 | 4.2896 | 4.1365 | 3.9334 | 3.7967 | 3.6202 | 3.4375 | 3.4426 | 3.0416 | 2.9732 | 2.9783 | 2.5722 | 2.5671 | 2.5559 | 2.4722 | 2.3447 | 2.2345 | 2.0661 | 1.9069 | 1.8569 | 1.5396 | 1.3661 | 1.2896
|  | MINCHINGTON PRIMARY | FB |  |  |  |  | 2.9513 | 2.9748 | 2.9982 | 2.9972 | 3.0023 | 2.9901 | 2.9625 | 2.9595 | 2.9248 | 2.4676 | 2.0921 | 1.8574 | 4.3426 | 4.3406 | 4.3426 | 4.3304 | 4.3263 | 4.31 | 4.261 | 4.2253 | 4.1671 | 3.6396 | 3.2039 | 2.7528 | 2.6253 | 2.6416 | 2.66 | 2.659 | 2.663 | 2.6539 | 2.6283 | 2.61 | 2.5773 | 2.2069 | 1.8957 | 1.6916
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE PRIMARY | MINIMUM HEADROOM | SU 01647 91932 | NO | NO | 0.248 | 11.0735 | 11.0939 | 10.8929 | 10.8286 | 10.6776 | 10.4541 | 10.1673 | 9.8224 | 9.5071 | 7.8204 | 6.351 | 6.15 | 12.4378 | 12.4214 | 12.1653 | 12.0704 | 11.8857 | 11.649 | 11.3867 | 11.0337 | 10.7265 | 9.299 | 8.4959 | 8.1714 | 11.4469 | 11.45 | 11.2 | 11.1184 | 10.95 | 10.7112 | 10.4388 | 10.1041 | 9.7939 | 8.299 | 7.2745 | 7.1357
|  | MINETY VILLAGE PRIMARY | EE |  |  |  |  | 11.0735 | 11.0939 | 10.8929 | 10.8337 | 10.699 | 10.4878 | 10.1847 | 9.8847 | 9.6194 | 7.849 | 6.3694 | 6.15 | 12.4378 | 12.4214 | 12.1673 | 12.0776 | 11.9071 | 11.6867 | 11.3867 | 11.0949 | 10.8388 | 9.3071 | 8.4959 | 8.1714 | 11.448 | 11.45 | 11.202 | 11.1255 | 10.9694 | 10.7449 | 10.4388 | 10.1622 | 9.9 | 8.3388 | 7.2847 | 7.1357
|  | MINETY VILLAGE PRIMARY | HT |  |  |  |  | 11.0745 | 11.0949 | 10.8929 | 10.8296 | 10.6776 | 10.4541 | 10.1867 | 9.8224 | 9.5071 | 7.8204 | 6.351 | 6.2102 | 12.4378 | 12.4214 | 12.1653 | 12.0704 | 11.8857 | 11.649 | 11.3888 | 11.0337 | 10.7265 | 9.299 | 8.6071 | 8.601 | 11.4469 | 11.45 | 11.2 | 11.1184 | 10.95 | 10.7112 | 10.4449 | 10.1041 | 9.7939 | 8.299 | 7.2745 | 7.2286
|  | MINETY VILLAGE PRIMARY | HE |  |  |  |  | 11.0776 | 11.0959 | 10.8959 | 10.8286 | 10.6806 | 10.4602 | 10.1673 | 9.8796 | 9.6173 | 8.1388 | 6.7296 | 6.6786 | 12.4418 | 12.4235 | 12.1704 | 12.0765 | 11.899 | 11.6755 | 11.398 | 11.1286 | 10.8816 | 9.5959 | 8.8969 | 8.7408 | 11.45 | 11.452 | 11.2031 | 11.1224 | 10.9561 | 10.7255 | 10.4531 | 10.1755 | 9.9224 | 8.6327 | 7.6694 | 7.6816
|  | MINETY VILLAGE PRIMARY | FB |  |  |  |  | 11.1888 | 11.248 | 11.2837 | 11.3173 | 11.3418 | 11.1255 | 11.0163 | 11.0429 | 10.8908 | 9.998 | 8.0908 | 7.6327 | 12.5367 | 12.5398 | 12.5224 | 12.5173 | 12.499 | 12.2214 | 12.0704 | 12.0551 | 11.8592 | 10.9255 | 9.3286 | 8.3347 | 11.55 | 11.5878 | 11.6061 | 11.6265 | 11.6327 | 11.3765 | 11.2541 | 11.2745 | 11.1112 | 10.2908 | 8.7673 | 8.3082
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | MORTIMER PRIMARY | MINIMUM HEADROOM | SU 62236 64103 | NO | NO | 2.647 | 5.1474 | 5.0168 | 4.7392 | 4.4505 | 4.1107 | 3.6086 | 3.0046 | 2.3392 | 1.6474 | -0.43831 | -1.7761 | -2.5097 | 7.402 | 7.2489 | 6.9091 | 6.6428 | 6.2867 | 5.9163 | 5.3908 | 4.9459 | 4.4102 | 2.5979 | 1.65 | 0.62037 | 6.1398 | 5.9663 | 5.6826 | 5.4102 | 5.0255 | 4.5734 | 3.9796 | 3.4255 | 2.7979 | 0.83465 | -0.20412 | -0.698
|  | MORTIMER PRIMARY | EE |  |  |  |  | 5.1474 | 5.0168 | 4.7474 | 4.4852 | 4.1852 | 3.6811 | 3.0729 | 2.4515 | 1.7494 | -0.43831 | -1.7761 | -2.5097 | 7.402 | 7.251 | 6.9193 | 6.6642 | 6.353 | 5.9928 | 5.4847 | 5.0408 | 4.4867 | 2.5979 | 1.65 | 1.0183 | 6.1408 | 5.9693 | 5.6908 | 5.4275 | 5.1 | 4.654 | 4.054 | 3.504 | 2.853 | 0.83465 | -0.20412 | -0.698
|  | MORTIMER PRIMARY | HT |  |  |  |  | 5.1484 | 5.0219 | 4.7392 | 4.4505 | 4.1107 | 3.6086 | 3.0311 | 2.4719 | 1.827 | -0.33116 | -1.7434 | -2.4475 | 7.402 | 7.251 | 6.9091 | 6.6428 | 6.2867 | 5.9163 | 5.3908 | 4.9459 | 4.4102 | 2.7296 | 2.0571 | 1.9306 | 6.1398 | 5.9693 | 5.6826 | 5.4102 | 5.0255 | 4.5734 | 3.9796 | 3.4693 | 2.8489 | 0.88159 | -0.14188 | -0.51127
|  | MORTIMER PRIMARY | HE |  |  |  |  | 5.1484 | 5.0168 | 4.7474 | 4.4678 | 4.1464 | 3.6219 | 3.0046 | 2.3392 | 1.6474 | 0.038224 | -1.2036 | -1.7138 | 7.402 | 7.2489 | 6.9204 | 6.6612 | 6.3418 | 5.9744 | 5.4836 | 5.002 | 4.4765 | 3.0336 | 2.1673 | 1.5489 | 6.1408 | 5.9663 | 5.6898 | 5.4193 | 5.0744 | 4.6142 | 4.0193 | 3.4255 | 2.7979 | 1.3408 | 0.39894 | 0.033633
|  | MORTIMER PRIMARY | FB |  |  |  |  | 5.3219 | 5.2474 | 5.1301 | 4.975 | 4.9199 | 4.8188 | 4.6443 | 4.5148 | 4.3688 | 3.329 | 1.8872 | 1.1341 | 7.5224 | 7.3949 | 7.254 | 7.1469 | 7.1255 | 6.9877 | 6.5979 | 6.3632 | 6.0908 | 4.4847 | 2.4622 | 0.62037 | 6.2612 | 6.1306 | 5.9857 | 5.8285 | 5.7398 | 5.6398 | 5.4908 | 5.3714 | 5.2347 | 4.0244 | 2.5724 | 1.7714
MANNINGTON GSP | SALISBURY BSP | NETHERHAMPTON PRIMARY | MINIMUM HEADROOM | SU 12478 29102 | NO | NO | 5.298 | 3.7767 | 3.5002 | 3.1635 | 2.6461 | 2.1553 | 1.5522 | 0.89918 | 0.31245 | -0.11306 | -1.0427 | -1.8182 | -2.2467 | 6.1829 | 5.8686 | 5.7329 | 5.4869 | 5.2543 | 5.0073 | 4.691 | 4.3747 | 4.0961 | 3.1471 | 2.592 | 1.6573 | 5.2206 | 4.8737 | 4.6247 | 4.2114 | 3.8176 | 3.3186 | 2.792 | 2.2869 | 1.9043 | 0.96653 | 0.36551 | 0.092041
|  | NETHERHAMPTON PRIMARY | EE |  |  |  |  | 3.7767 | 3.5002 | 3.1635 | 2.6461 | 2.1553 | 1.5522 | 0.89918 | 0.31245 | -0.095714 | -1.0427 | -1.808 | -2.2192 | 6.1829 | 5.8686 | 5.7329 | 5.49 | 5.2808 | 5.0073 | 4.7104 | 4.3931 | 4.1359 | 3.1471 | 2.592 | 2.1931 | 5.2206 | 4.8737 | 4.6247 | 4.2114 | 3.8176 | 3.3186 | 2.8002 | 2.2971 | 1.938 | 0.96653 | 0.36551 | 0.092041
|  | NETHERHAMPTON PRIMARY | HT |  |  |  |  | 3.79 | 3.5767 | 3.2767 | 2.8247 | 2.4012 | 1.9002 | 1.2512 | 0.74714 | 0.44204 | -0.89673 | -1.8182 | -2.2467 | 6.1859 | 5.9431 | 5.7471 | 5.492 | 5.2543 | 5.0492 | 4.7104 | 4.4124 | 4.1686 | 3.2747 | 2.9104 | 2.8227 | 5.2237 | 4.9716 | 4.6931 | 4.3022 | 3.9278 | 3.5247 | 2.9767 | 2.5288 | 2.2288 | 1.0502 | 0.39816 | 0.16245
|  | NETHERHAMPTON PRIMARY | HE |  |  |  |  | 3.7778 | 3.5349 | 3.1696 | 2.6747 | 2.1982 | 1.589 | 0.91347 | 0.31653 | -0.11306 | -0.82837 | -1.5365 | -1.7253 | 6.1829 | 5.94 | 5.74 | 5.4869 | 5.2696 | 5.0369 | 4.691 | 4.3747 | 4.0961 | 3.2645 | 2.6676 | 2.3961 | 5.2206 | 4.9482 | 4.6369 | 4.2227 | 3.8288 | 3.3624 | 2.792 | 2.2869 | 1.9043 | 1.1553 | 0.58184 | 0.50939
|  | NETHERHAMPTON PRIMARY | FB |  |  |  |  | 3.8737 | 3.7655 | 3.5584 | 3.2635 | 2.8757 | 2.5594 | 2.2165 | 1.9951 | 1.9165 | 1.4318 | 0.7798 | 0.23388 | 6.241 | 6.1624 | 6.0584 | 5.9247 | 5.5665 | 5.389 | 5.1706 | 4.9737 | 4.8706 | 4.0502 | 2.9186 | 1.6573 | 5.2869 | 5.2114 | 5.0931 | 4.8951 | 4.4543 | 4.2043 | 3.9043 | 3.6798 | 3.5971 | 2.9767 | 2.2104 | 1.639
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON PRIMARY | MINIMUM HEADROOM | SU 47615 12025 | NO | NO | 7.12 | 8.08 | 7.7973 | 7.1136 | 5.9269 | 4.5698 | 2.7983 | 1.0534 | -0.89657 | -2.6956 | -8.8404 | -13.2823 | -15.2649 | 13.8014 | 13.5249 | 13.1473 | 12.4565 | 11.6902 | 10.7187 | 9.6096 | 8.333 | 7.1279 | 2.4116 | -3.9098 | -13.6629 | 5.5861 | 5.3402 | 4.8575 | 3.9544 | 2.9473 | 1.6147 | 0.20139 | -1.4139 | -2.8833 | -7.8731 | -11.2435 | -12.4894
|  | NETLEY COMMON PRIMARY | EE |  |  |  |  | 8.08 | 7.8177 | 7.1136 | 5.9351 | 4.6075 | 2.8667 | 1.2493 | -0.48127 | -2.0558 | -7.7547 | -12.2802 | -14.6384 | 13.8014 | 13.5922 | 13.1667 | 12.5381 | 11.8208 | 10.881 | 9.8391 | 8.6942 | 7.633 | 2.4116 | -1.8058 | -5.6007 | 5.5861 | 5.4055 | 4.8575 | 3.9922 | 3.0238 | 1.73 | 0.43098 | -1.0027 | -2.2894 | -7.1466 | -10.7333 | -12.419
|  | NETLEY COMMON PRIMARY | HT |  |  |  |  | 8.0871 | 7.7973 | 7.1749 | 5.933 | 4.5871 | 2.7983 | 1.0534 | -0.89657 | -2.6956 | -8.8404 | -13.2823 | -15.2649 | 13.8075 | 13.5249 | 13.1473 | 12.4565 | 11.6902 | 10.7187 | 9.6096 | 8.333 | 7.1279 | 3.2228 | 0.89016 | -0.046571 | 5.5932 | 5.3402 | 4.8861 | 3.9544 | 2.9473 | 1.6147 | 0.20139 | -1.4139 | -2.8833 | -7.8731 | -11.2435 | -12.4894
|  | NETLEY COMMON PRIMARY | HE |  |  |  |  | 8.0871 | 7.8289 | 7.1391 | 5.9269 | 4.5698 | 2.8238 | 1.2412 | -0.43127 | -1.9649 | -6.5435 | -10.267 | -12.0251 | 13.8024 | 13.5922 | 13.1677 | 12.5391 | 11.8167 | 10.8687 | 9.8391 | 8.7208 | 7.6606 | 2.9249 | -1.0292 | -4.9394 | 5.5942 | 5.4157 | 4.8779 | 3.9871 | 2.9912 | 1.7024 | 0.42996 | -0.94861 | -2.2047 | -6.1384 | -9.0558 | -10.3588
|  | NETLEY COMMON PRIMARY | FB |  |  |  |  | 8.4677 | 8.6024 | 8.3851 | 7.9432 | 7.4259 | 6.8218 | 6.2636 | 5.9014 | 5.5238 | 2.282 | -2.219 | -4.8241 | 13.9412 | 13.8708 | 13.6177 | 13.1922 | 12.6983 | 11.9993 | 11.2116 | 10.5218 | 9.7565 | 4.3544 | -3.9098 | -13.6629 | 5.9912 | 6.1412 | 6.0106 | 5.6881 | 5.3514 | 4.9136 | 4.433 | 4.1126 | 3.7534 | 0.66261 | -3.4823 | -5.8547
MANNINGTON GSP | ARNEWOOD BSP | NEW MILTON PRIMARY | MINIMUM HEADROOM | SZ 23049 94942 | NO | NO | 1.574 | 12.3959 | 12.4061 | 12.3051 | 12.0531 | 11.6531 | 10.9684 | 10.048 | 9.1357 | 8.2194 | 5.35 | 3.8786 | 3.648 | 15.1551 | 15.0531 | 14.8592 | 14.5143 | 14.0265 | 13.35 | 12.4459 | 11.551 | 10.6622 | 7.4276 | 4.1857 | -1.4204 | 12.898 | 12.8245 | 12.65 | 12.3235 | 11.8255 | 11.1582 | 10.2755 | 9.3898 | 8.4796 | 5.4827 | 4.0582 | 3.8204
|  | NEW MILTON PRIMARY | EE |  |  |  |  | 12.4306 | 12.4735 | 12.4755 | 12.3643 | 12.1622 | 11.652 | 10.8939 | 10.1653 | 9.3408 | 6.4418 | 4.6296 | 3.9296 | 15.1735 | 15.0765 | 14.9418 | 14.6694 | 14.3092 | 13.7388 | 12.901 | 12.1122 | 11.2255 | 7.4276 | 4.7918 | 2.6173 | 12.9214 | 12.852 | 12.7653 | 12.5337 | 12.2041 | 11.6755 | 10.8959 | 10.1602 | 9.3204 | 6.2837 | 4.5265 | 3.8204
|  | NEW MILTON PRIMARY | HT |  |  |  |  | 12.3959 | 12.4061 | 12.3051 | 12.0531 | 11.6531 | 10.9684 | 10.048 | 9.1357 | 8.2194 | 5.35 | 3.8786 | 3.648 | 15.1551 | 15.0531 | 14.8592 | 14.5143 | 14.0265 | 13.35 | 12.4459 | 11.551 | 10.6622 | 7.5286 | 6.0112 | 5.6061 | 12.898 | 12.8245 | 12.65 | 12.3235 | 11.8255 | 11.1582 | 10.2755 | 9.3898 | 8.4796 | 5.4827 | 4.0582 | 3.9051
|  | NEW MILTON PRIMARY | HE |  |  |  |  | 12.4286 | 12.501 | 12.4867 | 12.3735 | 12.15 | 11.6224 | 10.901 | 10.1735 | 9.3592 | 7.1163 | 5.548 | 5.0786 | 15.1714 | 15.1041 | 14.9551 | 14.6867 | 14.3061 | 13.7112 | 12.9041 | 12.1143 | 11.2316 | 7.999 | 5.5459 | 3.4724 | 12.9194 | 12.8939 | 12.7806 | 12.5561 | 12.1969 | 11.6469 | 10.902 | 10.1704 | 9.3418 | 6.9867 | 5.4837 | 5.0714
|  | NEW MILTON PRIMARY | FB |  |  |  |  | 12.701 | 12.899 | 13.0031 | 13.1 | 13.1663 | 13.1031 | 12.9622 | 12.7929 | 12.5561 | 10.7214 | 7.9582 | 6.5031 | 15.301 | 15.2949 | 15.1694 | 15.048 | 14.8531 | 14.4908 | 14.0357 | 13.5551 | 13.0133 | 9.449 | 4.1857 | -1.4204 | 13.1867 | 13.3357 | 13.3684 | 13.3796 | 13.3429 | 13.2286 | 13.0531 | 12.8235 | 12.5092 | 10.5347 | 7.7265 | 6.2347
FAWLEY GSP | COWES BSP | NEWPORT PRIMARY | MINIMUM HEADROOM | SZ 50076 89544 | NO | YES | 7.348 | 28.9674 | 29.2562 | 29.2001 | 28.7868 | 28.0072 | 26.8052 | 25.3919 | 23.899 | 22.6143 | 17.849 | 13.7684 | 12.0939 | 30.5348 | 30.6246 | 30.5654 | 30.3266 | 29.7746 | 29.2052 | 28.4939 | 27.7276 | 27.1031 | 24.3552 | 21.3021 | 16.2143 | 28.947 | 29.1123 | 29.0623 | 28.6766 | 27.8531 | 26.8123 | 25.5368 | 24.0235 | 22.8225 | 18.2113 | 14.9592 | 13.8501
|  | NEWPORT PRIMARY | EE |  |  |  |  | 28.9674 | 29.2562 | 29.2225 | 28.9092 | 28.4062 | 27.3399 | 26.0552 | 24.8113 | 23.5684 | 19.2348 | 15.2001 | 13.248 | 30.5358 | 30.6317 | 30.6021 | 30.4143 | 30.1143 | 29.645 | 29.0215 | 28.4092 | 27.8164 | 24.3552 | 21.3021 | 19.0429 | 28.947 | 29.1133 | 29.0827 | 28.7756 | 28.2041 | 27.2654 | 26.0909 | 24.9266 | 23.648 | 19.1337 | 15.7929 | 14.2848
|  | NEWPORT PRIMARY | HT |  |  |  |  | 28.9776 | 29.2592 | 29.2001 | 28.7868 | 28.0072 | 26.8052 | 25.3919 | 23.899 | 22.6143 | 17.849 | 13.7684 | 12.0939 | 30.5368 | 30.6246 | 30.5654 | 30.3266 | 29.7746 | 29.2052 | 28.4939 | 27.7276 | 27.1031 | 24.3746 | 22.3429 | 21.7215 | 28.9521 | 29.1123 | 29.0623 | 28.6766 | 27.8531 | 26.8123 | 25.5368 | 24.0235 | 22.8225 | 18.2113 | 14.9592 | 13.8501
|  | NEWPORT PRIMARY | HE |  |  |  |  | 28.9848 | 29.2878 | 29.2705 | 28.9429 | 28.4205 | 27.4572 | 26.2899 | 25.1419 | 23.9909 | 20.5133 | 17.8899 | 16.4225 | 30.5348 | 30.6276 | 30.5939 | 30.4011 | 30.0939 | 29.6194 | 28.999 | 28.3756 | 27.7725 | 24.8001 | 22.5643 | 20.4582 | 28.9603 | 29.1327 | 29.1113 | 28.796 | 28.195 | 27.3194 | 26.2174 | 25.1113 | 23.8684 | 20.1715 | 18.0756 | 16.9766
|  | NEWPORT PRIMARY | FB |  |  |  |  | 29.2378 | 29.6154 | 29.8194 | 29.9378 | 29.8633 | 29.7215 | 29.3613 | 28.9388 | 28.5266 | 26.2643 | 23.0041 | 20.8399 | 30.6797 | 30.8113 | 30.8725 | 30.8919 | 30.7623 | 30.6552 | 30.3531 | 30.0184 | 29.7001 | 26.7113 | 21.6654 | 16.2143 | 29.1307 | 29.3276 | 29.4439 | 29.5082 | 29.3613 | 29.2133 | 28.8766 | 28.5041 | 28.0062 | 25.3439 | 21.8817 | 19.5113
FLEET-BRAMLEY GSP | ALDERSHOT BSP | NORMANDY PRIMARY | MINIMUM HEADROOM | SU 93221 52894 | YES | YES | 1.426 | 4.9678 | 4.9158 | 4.6781 | 4.4821 | 4.2383 | 3.8903 | 3.5536 | 3.1893 | 2.9127 | 1.8311 | 1.2536 | 1.0791 | 4.611 | 4.5885 | 4.513 | 4.4518 | 4.3354 | 4.1161 | 3.9232 | 3.6926 | 3.5497 | 2.7712 | 2.4844 | 2.5171 | 5.0272 | 4.9813 | 4.6894 | 4.5354 | 4.317 | 4.0231 | 3.7486 | 3.4313 | 3.2129 | 2.2354 | 1.816 | 1.7568
|  | NORMANDY PRIMARY | EE |  |  |  |  | 4.9852 | 4.9729 | 4.7923 | 4.6923 | 4.5852 | 4.3291 | 4.1015 | 3.877 | 3.6801 | 2.6852 | 2.1352 | 1.9556 | 4.6161 | 4.6059 | 4.5467 | 4.513 | 4.464 | 4.2722 | 4.114 | 3.9528 | 3.8161 | 2.9977 | 2.664 | 2.5661 | 5.0384 | 5.017 | 4.7752 | 4.668 | 4.5343 | 4.3017 | 4.0976 | 3.8915 | 3.7099 | 2.7925 | 2.3762 | 2.2884
|  | NORMANDY PRIMARY | HT |  |  |  |  | 4.9678 | 4.9158 | 4.6781 | 4.4821 | 4.2383 | 3.8903 | 3.5536 | 3.1893 | 2.9127 | 1.8311 | 1.2536 | 1.0791 | 4.611 | 4.5885 | 4.513 | 4.4518 | 4.3354 | 4.1161 | 3.9232 | 3.6926 | 3.5497 | 2.7712 | 2.4844 | 2.5171 | 5.0272 | 4.9813 | 4.6894 | 4.5354 | 4.317 | 4.0231 | 3.7486 | 3.4313 | 3.2129 | 2.2354 | 1.816 | 1.7568
|  | NORMANDY PRIMARY | HE |  |  |  |  | 4.9862 | 4.9729 | 4.7923 | 4.6852 | 4.5689 | 4.3352 | 4.0883 | 3.8352 | 3.6536 | 3.026 | 2.5536 | 2.324 | 4.6171 | 4.6059 | 4.5477 | 4.513 | 4.4579 | 4.2957 | 4.1242 | 3.9446 | 3.8314 | 3.315 | 3.0508 | 2.8528 | 5.0394 | 5.018 | 4.7762 | 4.6639 | 4.5221 | 4.3221 | 4.1027 | 3.867 | 3.7109 | 3.1303 | 2.7843 | 2.615
|  | NORMANDY PRIMARY | FB |  |  |  |  | 5.0281 | 5.0372 | 5.0342 | 5.0281 | 5.0117 | 4.8587 | 4.7566 | 4.7229 | 4.6413 | 4.2556 | 3.7872 | 3.2148 | 4.6406 | 4.6426 | 4.6385 | 4.6324 | 4.6201 | 4.565 | 4.5201 | 4.5028 | 4.3926 | 3.9477 | 3.3844 | 2.6222 | 5.0833 | 5.0894 | 5.0843 | 5.0741 | 5.0537 | 4.8252 | 4.7088 | 4.6782 | 4.568 | 4.1578 | 3.6813 | 3.0997
NURSLING GSP | ROWNHAMS BSP | NORTH BADDESLEY PRIMARY | MINIMUM HEADROOM | SU 38080 20568 | NO | YES | 15.286 | 7.0781 | 6.7209 | 6.3209 | 5.6434 | 4.9516 | 3.8985 | 1.9699 | -1.5576 | -3.328 | -12.2566 | -22.2464 | -29.1046 | 9.6985 | 9.4689 | 9.2036 | 8.7454 | 8.2832 | 7.6781 | 5.9648 | 2.1771 | 0.18625 | -7.9035 | -18.1923 | -26.0852 | 4.3097 | 3.9587 | 3.6087 | 3.0393 | 2.4587 | 1.625 | -0.29742 | -4.2842 | -6.2821 | -15.5393 | -26.676 | -34.3842
|  | NORTH BADDESLEY PRIMARY | EE |  |  |  |  | 7.0781 | 6.7587 | 6.3209 | 5.6618 | 4.9893 | 3.9158 | 2.4965 | 0.90258 | -1.4791 | -9.6056 | -20.2576 | -24.6291 | 9.6995 | 9.5475 | 9.2087 | 8.7556 | 8.3046 | 7.7067 | 6.6597 | 5.2689 | 2.9638 | -4.4903 | -16.1454 | -20.9352 | 4.3107 | 3.9975 | 3.6138 | 3.0546 | 2.4873 | 1.6414 | 0.36686 | -1.2025 | -3.7107 | -12.0035 | -24.0433 | -28.676
|  | NORTH BADDESLEY PRIMARY | HT |  |  |  |  | 7.0791 | 6.7209 | 6.3373 | 5.7026 | 5.0373 | 4.0505 | 2.1944 | 0.38931 | -3.328 | -12.2566 | -22.2464 | -29.1046 | 9.6985 | 9.4689 | 9.2087 | 8.7556 | 8.2832 | 7.6781 | 5.9648 | 4.2393 | 0.18625 | -7.9035 | -18.1923 | -25.376 | 4.3097 | 3.9587 | 3.6087 | 3.076 | 2.4985 | 1.6975 | -0.18518 | -2.0607 | -6.2821 | -15.5393 | -26.676 | -34.3842
|  | NORTH BADDESLEY PRIMARY | HE |  |  |  |  | 7.0781 | 6.7607 | 6.322 | 5.6434 | 4.9516 | 3.8985 | 1.9699 | -1.5576 | -2.6862 | -11.4301 | -19.2933 | -27.678 | 9.6995 | 9.5475 | 9.2036 | 8.7454 | 8.2903 | 7.6893 | 5.9791 | 2.1771 | 1.4332 | -7.3658 | -15.7872 | -26.0852 | 4.3097 | 3.9985 | 3.6148 | 3.0393 | 2.4587 | 1.625 | -0.29742 | -4.2842 | -5.226 | -14.6311 | -23.2923 | -33.175
|  | NORTH BADDESLEY PRIMARY | FB |  |  |  |  | 7.2495 | 7.1985 | 7.0056 | 6.7352 | 6.2087 | 5.8689 | 5.3393 | 4.7373 | 3.5669 | -0.9811 | -7.7168 | -12.2107 | 9.825 | 9.7811 | 9.6587 | 9.4271 | 8.9934 | 8.6424 | 8.0148 | 7.2852 | 5.8679 | 0.63625 | -7.6403 | -14.5903 | 4.5301 | 4.4414 | 4.2597 | 4.0342 | 3.574 | 3.274 | 2.7209 | 2.0699 | 0.72707 | -4.0893 | -11.6229 | -16.7025
LOVEDEAN GSP | FAREHAM (MAIN) BSP | NORTH FAREHAM PRIMARY | MINIMUM HEADROOM | SU 56427 07430 | NO | YES | 14.81 | -3.635 | -3.9881 | -4.5095 | 14.3547 | 13.8405 | 12.3874 | 10.8078 | 9.0394 | 7.2864 | 1.716 | -0.84321 | -2.1085 | -0.37893 | -0.66464 | -1.082 | 16.4405 | 15.9425 | 14.9813 | 13.8405 | 12.5119 | 11.2741 | 7.4323 | 5.7262 | 2.8792 | -1.9799 | -2.2891 | -2.7493 | 15.2068 | 14.7078 | 13.4884 | 12.1068 | 10.5323 | 9.017 | 4.2741 | 2.3609 | 1.6547
|  | NORTH FAREHAM PRIMARY | EE |  |  |  |  | -3.6136 | -3.584 | -4.0483 | 14.9252 | 14.5731 | 13.1741 | 11.7282 | 10.1782 | 8.6996 | 2.3405 | -0.16974 | -1.5279 | -0.36362 | -0.43811 | -0.82076 | 16.7813 | 16.3915 | 15.5374 | 14.5405 | 13.4333 | 12.4456 | 7.615 | 5.7262 | 4.2609 | -1.9657 | -1.9891 | -2.3963 | 15.6466 | 15.2792 | 14.1476 | 12.9058 | 11.5517 | 10.2986 | 4.7486 | 2.7833 | 1.867
|  | NORTH FAREHAM PRIMARY | HT |  |  |  |  | -3.635 | -3.9881 | -4.5095 | 14.3547 | 13.8405 | 12.3874 | 10.8078 | 9.0394 | 7.2864 | 1.716 | -0.84321 | -2.1085 | -0.37893 | -0.66464 | -1.082 | 16.4405 | 15.9425 | 14.9813 | 13.8405 | 12.5119 | 11.2741 | 7.4323 | 6.3323 | 6.1568 | -1.9799 | -2.2891 | -2.7493 | 15.2068 | 14.7078 | 13.4884 | 12.1068 | 10.5323 | 9.017 | 4.2741 | 2.3609 | 1.6547
|  | NORTH FAREHAM PRIMARY | HE |  |  |  |  | -3.6136 | -3.585 | -3.8167 | 15.3619 | 14.9864 | 14.066 | 12.8619 | 11.5241 | 10.1547 | 5.1598 | 2.4752 | 0.9772 | -0.3677 | -0.44219 | -0.7024 | 17.0507 | 16.6476 | 16.1088 | 15.266 | 14.2731 | 13.2425 | 9.0935 | 7.1088 | 5.4282 | -1.9667 | -1.9912 | -2.2197 | 15.9823 | 15.5956 | 14.8507 | 13.7976 | 12.5986 | 11.3639 | 6.9639 | 4.9364 | 3.9088
|  | NORTH FAREHAM PRIMARY | FB |  |  |  |  | -3.2881 | -3.1779 | -3.0779 | 16.3568 | 16.3241 | 16.0629 | 15.7813 | 15.3496 | 14.9201 | 10.9109 | 7.8231 | 5.7558 | -0.11362 | -0.14423 | -0.19117 | 17.6496 | 17.465 | 17.1088 | 16.7221 | 16.2068 | 15.6803 | 11.2129 | 7.1425 | 2.8792 | -1.6677 | -1.6136 | -1.5973 | 16.8762 | 16.8027 | 16.5864 | 16.3098 | 15.8803 | 15.4517 | 11.5996 | 8.7507 | 6.7711
LALEHAM GSP | EAST BEDFONT BSP | NORTH FELTHAM PRIMARY | MINIMUM HEADROOM | TQ 10987 74875 | NO | NO | 6.64 | 7.5818 | 7.5206 | 7.4542 | 7.3828 | 7.1083 | 6.6369 | 5.9757 | 5.3716 | 4.643 | 2.5757 | 1.0032 | 0.13384 | 8.4474 | 8.3668 | 8.3097 | 8.2117 | 7.9484 | 7.5413 | 6.9862 | 6.4168 | 5.8515 | 3.6056 | 0.12904 | -4.9597 | 7.8931 | 7.8146 | 7.7319 | 7.6523 | 7.4033 | 6.9656 | 6.3523 | 5.7411 | 4.9472 | 2.6584 | 1.0605 | 0.16558
|  | NORTH FELTHAM PRIMARY | EE |  |  |  |  | 7.5818 | 7.5308 | 7.4542 | 7.3828 | 7.2655 | 6.8838 | 6.391 | 5.8328 | 5.1757 | 2.5757 | 1.0032 | 0.13384 | 8.4484 | 8.3944 | 8.3117 | 8.2301 | 8.1341 | 7.8321 | 7.3903 | 6.8566 | 6.3382 | 3.6454 | 1.4862 | -0.66891 | 7.8931 | 7.8207 | 7.7319 | 7.6523 | 7.5564 | 7.1952 | 6.7227 | 6.1401 | 5.4217 | 2.6584 | 1.0605 | 0.16558
|  | NORTH FELTHAM PRIMARY | HT |  |  |  |  | 7.591 | 7.5206 | 7.4818 | 7.4114 | 7.1083 | 6.6369 | 5.9757 | 5.3716 | 4.643 | 2.5869 | 1.4104 | 1.0349 | 8.4495 | 8.3668 | 8.3137 | 8.2341 | 7.9484 | 7.5413 | 6.9862 | 6.4168 | 5.8515 | 4.1903 | 3.0005 | 2.3597 | 7.9033 | 7.8146 | 7.7635 | 7.6829 | 7.4033 | 6.9656 | 6.3523 | 5.7411 | 4.9472 | 2.7492 | 1.5339 | 1.1605
|  | NORTH FELTHAM PRIMARY | HE |  |  |  |  | 7.5869 | 7.543 | 7.4706 | 7.3961 | 7.2736 | 6.9379 | 6.3961 | 5.8491 | 5.192 | 3.4522 | 2.4726 | 1.8563 | 8.4474 | 8.3954 | 8.3097 | 8.228 | 8.1341 | 7.8444 | 7.3739 | 6.8413 | 6.3168 | 4.2127 | 2.5178 | 0.34843 | 7.8982 | 7.8309 | 7.7482 | 7.6646 | 7.5635 | 7.2462 | 6.7248 | 6.1554 | 5.435 | 3.6125 | 2.637 | 2.0166
|  | NORTH FELTHAM PRIMARY | FB |  |  |  |  | 7.7083 | 7.7502 | 7.6655 | 7.642 | 7.5808 | 7.4787 | 7.2675 | 7.0012 | 6.7298 | 5.1196 | 3.6594 | 2.2236 | 8.4648 | 8.4331 | 8.3178 | 8.2117 | 8.078 | 7.8127 | 7.4056 | 6.9566 | 6.4944 | 3.6056 | 0.12904 | -4.9597 | 8.039 | 8.0799 | 7.9595 | 7.9248 | 7.8676 | 7.7839 | 7.5931 | 7.3452 | 7.0911 | 5.4003 | 3.8758 | 2.338
COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY PRIMARY | MINIMUM HEADROOM | SP 48645 04403 | NO | YES | 2.844 | 1.7471 | 1.7481 | 1.6981 | 1.5308 | 1.3053 | 0.76342 | 0.19811 | -0.41515 | -0.96311 | -2.5927 | -3.9845 | -4.7998 | 3.8047 | 3.7639 | 3.7068 | 3.7088 | 3.5996 | 3.3986 | 3.1425 | 2.6843 | 2.3558 | 1.4201 | 0.80679 | -0.67178 | 3.0951 | 3.0726 | 3.0308 | 3.0297 | 2.8971 | 2.5471 | 2.1685 | 1.6828 | 1.2481 | -0.0018857 | -0.84066 | -1.2672
|  | NORTH HINKSEY PRIMARY | EE |  |  |  |  | 1.7471 | 1.7481 | 1.6981 | 1.5553 | 1.3553 | 0.82669 | 0.27975 | -0.26923 | -0.88046 | -2.5927 | -3.9845 | -4.7998 | 3.8047 | 3.7639 | 3.7098 | 3.7119 | 3.6088 | 3.4252 | 3.1956 | 2.9211 | 2.4701 | 1.4201 | 0.80679 | 0.24964 | 3.0951 | 3.0726 | 3.0308 | 3.04 | 2.9185 | 2.5818 | 2.2104 | 1.8236 | 1.2481 | -0.0018857 | -0.77842 | -1.158
|  | NORTH HINKSEY PRIMARY | HT |  |  |  |  | 1.7767 | 1.7757 | 1.7563 | 1.6563 | 1.4848 | 1.0634 | 0.60934 | 0.070563 | -0.40189 | -2.2621 | -3.8427 | -4.7723 | 3.8078 | 3.768 | 3.7068 | 3.715 | 3.5996 | 3.3986 | 3.1425 | 2.6843 | 2.3558 | 1.4639 | 1.067 | 0.90781 | 3.1083 | 3.094 | 3.0604 | 3.0818 | 2.9553 | 2.6573 | 2.3063 | 1.7379 | 1.3134 | 0.0032163 | -0.84066 | -1.2672
|  | NORTH HINKSEY PRIMARY | HE |  |  |  |  | 1.7481 | 1.7481 | 1.6991 | 1.5308 | 1.3053 | 0.76342 | 0.19811 | -0.41515 | -0.96311 | -2.3141 | -3.5917 | -4.1845 | 3.8058 | 3.7639 | 3.7068 | 3.7088 | 3.6047 | 3.4201 | 3.1894 | 2.819 | 2.5721 | 1.7598 | 1.0884 | 0.45781 | 3.0961 | 3.0736 | 3.0308 | 3.0297 | 2.8971 | 2.5471 | 2.1685 | 1.6828 | 1.3073 | 0.39505 | -0.35801 | -0.6978
|  | NORTH HINKSEY PRIMARY | FB |  |  |  |  | 1.8563 | 1.8787 | 1.9053 | 1.9073 | 1.8706 | 1.8338 | 1.7593 | 1.6746 | 1.5869 | 0.95424 | 0.23077 | -0.1825 | 3.8966 | 3.8813 | 3.867 | 3.8384 | 3.7966 | 3.7537 | 3.6201 | 3.4823 | 3.3262 | 2.315 | 0.95067 | -0.67178 | 3.2195 | 3.2461 | 3.2808 | 3.2889 | 3.29 | 3.3002 | 3.2328 | 3.1573 | 3.0706 | 2.4706 | 1.7491 | 1.2175
NORTH HYDE GSP |  | NORTH HYDE PRIMARY | MINIMUM HEADROOM | TQ 10367 79001 | NO | YES | 20.393 | 16.1437 | 16.1682 | 60.4794 | 60.2335 | 59.5315 | 58.856 | 57.6754 | 56.0284 | 54.3529 | 45.1417 | 38.9141 | 36.1621 | 17.0111 | 16.9315 | 65.6101 | 65.3917 | 64.7478 | 64.2948 | 62.7764 | 60.6315 | 58.4029 | 48.3396 | 41.3682 | 36.459 | 14.0866 | 14.0845 | 60.3988 | 60.1856 | 59.558 | 59.0733 | 57.6733 | 55.9815 | 54.3427 | 45.6611 | 39.1815 | 36.4499
|  | NORTH HYDE PRIMARY | EE |  |  |  |  | 16.1437 | 16.2315 | 60.507 | 60.3672 | 60.0866 | 59.3335 | 57.6754 | 56.0284 | 54.3529 | 45.1417 | 38.9141 | 36.1621 | 17.0111 | 17.0264 | 65.6529 | 65.4733 | 65.1825 | 64.5111 | 62.7764 | 60.6315 | 58.4029 | 48.3396 | 41.3682 | 36.459 | 14.0866 | 14.1315 | 60.3988 | 60.2539 | 60.009 | 59.3835 | 57.6733 | 55.9815 | 54.3427 | 45.6611 | 39.1815 | 36.4499
|  | NORTH HYDE PRIMARY | HT |  |  |  |  | 16.1692 | 16.1682 | 60.4794 | 60.2335 | 59.5315 | 58.856 | 57.9417 | 56.3978 | 54.6294 | 47.0437 | 42.5019 | 40.9835 | 17.0131 | 16.9315 | 65.6101 | 65.3917 | 64.7478 | 64.2948 | 63.5274 | 61.6478 | 59.6488 | 52.5948 | 48.5886 | 46.9907 | 14.1141 | 14.0845 | 60.408 | 60.1856 | 59.558 | 59.0733 | 58.4274 | 56.9917 | 55.5458 | 48.4927 | 43.8835 | 42.4243
|  | NORTH HYDE PRIMARY | HE |  |  |  |  | 16.1621 | 16.2703 | 60.5631 | 60.4192 | 60.1101 | 59.406 | 58.7876 | 57.9386 | 57.0192 | 52.4641 | 49.2254 | 47.5315 | 17.0131 | 17.0284 | 65.657 | 65.4835 | 65.1927 | 64.5325 | 64.0478 | 62.8539 | 61.5182 | 55.957 | 51.5182 | 47.4019 | 14.1029 | 14.1682 | 60.4488 | 60.2896 | 60.0192 | 59.4152 | 58.9631 | 58.2192 | 57.4672 | 54.0519 | 50.9978 | 49.4641
|  | NORTH HYDE PRIMARY | FB |  |  |  |  | 16.4427 | 16.7111 | 61.1754 | 61.2509 | 61.2733 | 61.2172 | 60.8396 | 60.6611 | 60.4682 | 58.3662 | 54.4672 | 50.7407 | 17.1019 | 17.156 | 65.9029 | 65.7784 | 65.6029 | 65.3417 | 64.7366 | 64.3427 | 63.6713 | 58.4172 | 50.5009 | 40.4264 | 14.2927 | 14.4764 | 60.9417 | 60.9203 | 60.9009 | 60.8366 | 60.4754 | 60.3356 | 60.1764 | 58.6305 | 56.1448 | 52.7274
MINETY GSP | CIRENCESTER BSP | NORTHLEACH PRIMARY | MINIMUM HEADROOM | SP 10557 14251 | NO | NO | 0.768 | 7.4224 | 7.4653 | 7.4653 | 7.348 | 7.1816 | 6.9031 | 6.5582 | 6.1827 | 5.8286 | 4.8429 | 3.8796 | 3.252 | 9.0827 | 9.0735 | 9.0378 | 8.8561 | 8.7153 | 8.5439 | 8.2469 | 8.0031 | 7.7582 | 6.9878 | 6.701 | 6.0898 | 8.4265 | 8.4541 | 8.4316 | 8.2133 | 8.0398 | 7.8041 | 7.4429 | 7.1194 | 6.8235 | 5.9714 | 5.5112 | 5.2582
|  | NORTHLEACH PRIMARY | EE |  |  |  |  | 7.4224 | 7.4653 | 7.4867 | 7.4061 | 7.2898 | 7.0643 | 6.7551 | 6.4235 | 6.1163 | 5.148 | 4.3939 | 3.9265 | 9.0847 | 9.0745 | 9.0459 | 8.8806 | 8.7388 | 8.5816 | 8.3306 | 8.0714 | 7.8347 | 7.0878 | 6.701 | 6.4755 | 8.4265 | 8.4541 | 8.4388 | 8.2276 | 8.0684 | 7.848 | 7.5541 | 7.251 | 6.9724 | 6.1337 | 5.6786 | 5.6449
|  | NORTHLEACH PRIMARY | HT |  |  |  |  | 7.4255 | 7.4653 | 7.4653 | 7.348 | 7.1816 | 6.9031 | 6.5582 | 6.1827 | 5.8286 | 4.8429 | 3.8796 | 3.252 | 9.0847 | 9.0735 | 9.0378 | 8.8561 | 8.7153 | 8.5439 | 8.2469 | 8.0031 | 7.7582 | 6.9878 | 6.7184 | 6.8041 | 8.4276 | 8.4541 | 8.4316 | 8.2133 | 8.0398 | 7.8041 | 7.4429 | 7.1194 | 6.8235 | 5.9714 | 5.5112 | 5.2582
|  | NORTHLEACH PRIMARY | HE |  |  |  |  | 7.4224 | 7.4663 | 7.4878 | 7.3847 | 7.2602 | 7.0112 | 6.699 | 6.3367 | 6.0439 | 5.2959 | 4.6622 | 4.1327 | 9.0827 | 9.0735 | 9.0439 | 8.8765 | 8.7367 | 8.5724 | 8.3163 | 8.0429 | 7.8286 | 7.1755 | 6.949 | 6.6051 | 8.4265 | 8.4551 | 8.4378 | 8.2276 | 8.0551 | 7.8255 | 7.5194 | 7.1918 | 6.9327 | 6.249 | 5.9327 | 5.8061
|  | NORTHLEACH PRIMARY | FB |  |  |  |  | 7.5398 | 7.6041 | 7.651 | 7.6684 | 7.7031 | 7.6653 | 7.6184 | 7.5929 | 7.5408 | 6.8439 | 6.1378 | 5.7684 | 9.1867 | 9.202 | 9.1939 | 9.1959 | 9.1796 | 9.1194 | 9.0449 | 9.0337 | 8.9418 | 8.0082 | 7.0684 | 6.0898 | 8.5235 | 8.5694 | 8.599 | 8.6153 | 8.6122 | 8.5622 | 8.5041 | 8.5418 | 8.4653 | 7.5837 | 6.9255 | 6.6
IVER 66KV GSP |  | NORTHOLT PRIMARY | MINIMUM HEADROOM | TQ 11550 83230 | NO | NO | 14.554 | 41.1009 | 41.3652 | 41.1478 | 40.8713 | 40.453 | 39.5958 | 38.605 | 37.4397 | 35.8968 | 29.3978 | 24.7887 | 22.0213 | 49.9611 | 50.0713 | 49.8754 | 49.6468 | 49.2723 | 48.657 | 47.7999 | 46.7407 | 45.554 | 40.7795 | 32.5897 | 20.9132 | 43.155 | 43.3672 | 43.1866 | 42.9825 | 42.5785 | 41.8142 | 40.9325 | 39.7132 | 38.2887 | 32.6336 | 28.3162 | 25.9336
|  | NORTHOLT PRIMARY | EE |  |  |  |  | 41.1009 | 41.3652 | 41.1478 | 40.8713 | 40.453 | 39.5958 | 38.605 | 37.4397 | 36.1785 | 30.2305 | 24.8142 | 22.0213 | 49.9968 | 50.1264 | 49.8815 | 49.6744 | 49.357 | 48.7376 | 47.9927 | 47.0693 | 46.0805 | 40.7795 | 35.9611 | 31.2968 | 43.155 | 43.3672 | 43.1866 | 42.9825 | 42.5785 | 41.8142 | 40.9325 | 39.8581 | 38.6856 | 33.157 | 28.3162 | 25.9336
|  | NORTHOLT PRIMARY | HT |  |  |  |  | 41.1438 | 41.4478 | 41.3254 | 41.0999 | 40.6468 | 39.8907 | 38.7764 | 37.4499 | 35.8968 | 29.3978 | 24.7887 | 23.053 | 50.0019 | 50.1254 | 49.8754 | 49.6468 | 49.2723 | 48.657 | 47.7999 | 46.7407 | 45.554 | 41.9091 | 39.6305 | 38.605 | 43.1968 | 43.4448 | 43.3285 | 43.1142 | 42.6448 | 41.9366 | 40.9417 | 39.7132 | 38.2887 | 32.6336 | 28.7938 | 27.5478
|  | NORTHOLT PRIMARY | HE |  |  |  |  | 41.1387 | 41.4376 | 41.2611 | 40.9907 | 40.5774 | 39.8407 | 38.9468 | 37.8815 | 36.7223 | 32.8448 | 29.2315 | 27.1938 | 50.005 | 50.1438 | 49.904 | 49.7091 | 49.4009 | 48.8172 | 48.0897 | 47.1856 | 46.2264 | 41.6989 | 37.2346 | 32.7152 | 43.1917 | 43.4376 | 43.2938 | 43.0825 | 42.6744 | 42.0019 | 41.1856 | 40.1805 | 39.0917 | 35.5203 | 32.3142 | 30.607
|  | NORTHOLT PRIMARY | FB |  |  |  |  | 41.3968 | 41.8897 | 42.2264 | 42.5223 | 42.6478 | 42.6509 | 42.5244 | 42.3703 | 42.157 | 40.0264 | 34.9509 | 31.0478 | 49.9611 | 50.0713 | 50.1111 | 50.0397 | 49.653 | 49.1152 | 48.4795 | 47.8366 | 47.1223 | 41.8489 | 32.5897 | 20.9132 | 43.4703 | 43.8876 | 44.2152 | 44.4601 | 44.5183 | 44.4907 | 44.3448 | 44.1591 | 43.9121 | 41.5581 | 36.6234 | 32.857
BRAMLEY (BASI) GSP | READING BSP | NORTHUMBERLAND AVENUE PRIMARY | MINIMUM HEADROOM | SU 72207 71092 | NO | YES | 4.447 | 4.8138 | 4.4863 | 4.1751 | 3.97 | 3.6016 | 3.0434 | 2.1781 | 1.5485 | 0.92303 | -2.3168 | -4.077 | -4.8596 | 6.2823 | 5.9803 | 5.5864 | 5.3599 | 5.1221 | 4.7711 | 4.318 | 3.8946 | 3.4997 | 1.3109 | -0.43707 | -3.5126 | 5.2603 | 4.9542 | 4.649 | 4.5195 | 4.3195 | 3.9613 | 3.3511 | 2.8807 | 2.4174 | -0.062176 | -1.4958 | -2.1295
|  | NORTHUMBERLAND AVENUE PRIMARY | EE |  |  |  |  | 4.8138 | 4.4934 | 4.1924 | 4.0098 | 3.6445 | 3.0434 | 2.1781 | 1.5485 | 0.92303 | -2.3168 | -4.077 | -4.8596 | 6.2833 | 5.9986 | 5.616 | 5.3884 | 5.168 | 4.8037 | 4.318 | 3.9078 | 3.4997 | 1.3109 | -0.055441 | -1.3514 | 5.2603 | 4.9633 | 4.6562 | 4.5429 | 4.3439 | 3.9613 | 3.3511 | 2.8807 | 2.4174 | -0.062176 | -1.4958 | -2.1295
|  | NORTHUMBERLAND AVENUE PRIMARY | HT |  |  |  |  | 4.821 | 4.4863 | 4.1751 | 3.97 | 3.6016 | 3.0567 | 2.2853 | 1.6383 | 1.0587 | -2.2913 | -3.9045 | -4.527 | 6.2823 | 5.9803 | 5.5864 | 5.3599 | 5.1221 | 4.7711 | 4.3272 | 3.8946 | 3.5252 | 1.7354 | 0.98333 | 0.64864 | 5.2654 | 4.9542 | 4.649 | 4.5195 | 4.3195 | 3.9654 | 3.4123 | 2.9337 | 2.5052 | -0.019318 | -1.305 | -1.7469
|  | NORTHUMBERLAND AVENUE PRIMARY | HE |  |  |  |  | 4.822 | 4.5098 | 4.2128 | 4.0475 | 3.6934 | 3.1516 | 2.273 | 1.6434 | 1.0455 | -1.5984 | -2.9055 | -3.4821 | 6.2864 | 6.0027 | 5.619 | 5.3956 | 5.1793 | 4.8497 | 4.3313 | 3.9252 | 3.5466 | 1.6507 | 0.37925 | -0.82789 | 5.2695 | 4.9817 | 4.6827 | 4.5735 | 4.3756 | 4.0388 | 3.4184 | 2.9552 | 2.5164 | 0.53068 | -0.48054 | -0.91116
|  | NORTHUMBERLAND AVENUE PRIMARY | FB |  |  |  |  | 4.9067 | 4.6169 | 4.372 | 4.3883 | 4.1934 | 4.0128 | 3.6873 | 3.3455 | 3.0108 | 1.0649 | -0.56167 | -1.5576 | 6.3558 | 6.0282 | 5.6588 | 5.6037 | 5.3864 | 5.1548 | 4.867 | 4.4833 | 4.1568 | 2.1374 | -0.43707 | -3.5126 | 5.3684 | 5.0939 | 4.8623 | 4.8888 | 4.7695 | 4.648 | 4.4531 | 4.2225 | 3.998 | 2.5103 | 1.1368 | 0.2664
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD PRIMARY | MINIMUM HEADROOM | SU 68329 86784 | YES | NO | 1.228 | 2.0802 | 2.0873 | 1.9506 | 1.8588 | 1.7394 | 1.4843 | 0.89041 | -0.69837 | -3.882 | -6.4565 | -9.6535 | -13.6351 | 3.9802 | 3.9598 | 3.7506 | 3.6486 | 3.5373 | 3.3618 | 2.7159 | 0.87306 | -2.9851 | -6.1024 | -9.8259 | -14.7259 | 2.9251 | 2.9231 | 2.7149 | 2.5945 | 2.4996 | 2.2741 | 1.6129 | -0.27592 | -4.1627 | -7.232 | -10.9892 | -15.8249
|  | NUFFIELD PRIMARY | EE |  |  |  |  | 2.0802 | 2.0873 | 1.9506 | 1.8751 | 1.7731 | 1.5394 | 1.2445 | 0.63429 | -0.25245 | -2.3902 | -6.9657 | -8.68 | 3.9822 | 3.9608 | 3.7516 | 3.6537 | 3.5618 | 3.3782 | 3.0955 | 2.4588 | 1.4527 | -0.91878 | -6.379 | -8.4147 | 2.9251 | 2.9231 | 2.7159 | 2.6047 | 2.519 | 2.3088 | 2.0067 | 1.3404 | 0.31388 | -2.0861 | -7.5698 | -9.5524
|  | NUFFIELD PRIMARY | HT |  |  |  |  | 2.0935 | 2.1098 | 1.9771 | 1.8986 | 1.7924 | 1.6047 | 1.0169 | 0.31796 | -1.2933 | -3.7576 | -8.08 | -11.1994 | 3.9843 | 3.9649 | 3.7516 | 3.6557 | 3.5373 | 3.3822 | 2.7159 | 1.9343 | 0.0036735 | -2.7831 | -7.7647 | -11.3096 | 2.9322 | 2.9373 | 2.7292 | 2.6261 | 2.4996 | 2.3424 | 1.6629 | 0.86184 | -1.079 | -3.9229 | -9.0331 | -12.6861
|  | NUFFIELD PRIMARY | HE |  |  |  |  | 2.0822 | 2.0884 | 1.9537 | 1.8588 | 1.7394 | 1.4843 | 0.89041 | -0.69837 | -3.882 | -6.4565 | -9.6535 | -13.6351 | 3.9802 | 3.9598 | 3.7506 | 3.6486 | 3.5527 | 3.3618 | 2.7261 | 0.87306 | -2.9851 | -6.1024 | -9.8259 | -14.7259 | 2.9251 | 2.9241 | 2.7149 | 2.5945 | 2.5006 | 2.2741 | 1.6129 | -0.27592 | -4.1627 | -7.232 | -10.9892 | -15.8249
|  | NUFFIELD PRIMARY | FB |  |  |  |  | 2.1731 | 2.2251 | 2.2649 | 2.2741 | 2.2935 | 2.2761 | 2.0047 | 1.8037 | 1.2914 | -0.23204 | -2.3035 | -4.1769 | 4.0445 | 4.0537 | 4.0465 | 4.0322 | 4.0231 | 3.9812 | 3.5873 | 3.3159 | 2.669 | 0.79143 | -1.8382 | -4.432 | 2.9843 | 3.0129 | 3.0282 | 3.0231 | 3.019 | 3.0129 | 2.6761 | 2.4241 | 1.7955 | 0.029184 | -2.4004 | -4.6606
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | OAKRIDGE PRIMARY | MINIMUM HEADROOM | SU 63496 53664 | NO | NO | 5.062 | 16.1394 | 15.9883 | 15.7812 | 15.2975 | 14.9863 | 14.42 | 13.6516 | 12.8577 | 12.0904 | 9.1842 | 6.4638 | 4.5251 | 17.2312 | 17.122 | 17.0363 | 16.6904 | 16.4251 | 16.0302 | 15.4863 | 14.9179 | 14.3791 | 12.2598 | 10.5128 | 7.0822 | 16.3618 | 16.2291 | 16.0873 | 15.5996 | 15.2863 | 14.7812 | 14.0853 | 13.371 | 12.6883 | 10.1761 | 8.0567 | 6.6965
|  | OAKRIDGE PRIMARY | EE |  |  |  |  | 16.1394 | 15.9883 | 15.7812 | 15.3485 | 15.0955 | 14.6332 | 14.0445 | 13.2189 | 12.4179 | 9.2536 | 6.4638 | 4.5251 | 17.2312 | 17.122 | 17.0434 | 16.7353 | 16.4802 | 16.1669 | 15.7251 | 15.1373 | 14.574 | 12.2598 | 10.5128 | 8.9383 | 16.3618 | 16.2291 | 16.0873 | 15.6424 | 15.3679 | 14.9649 | 14.4169 | 13.6761 | 12.9598 | 10.2067 | 8.0567 | 6.6965
|  | OAKRIDGE PRIMARY | HT |  |  |  |  | 16.1516 | 16.0149 | 15.8006 | 15.2975 | 14.9863 | 14.42 | 13.6516 | 12.8577 | 12.0904 | 9.1842 | 6.5618 | 5.0985 | 17.2312 | 17.1291 | 17.0363 | 16.6904 | 16.4251 | 16.0302 | 15.4863 | 14.9179 | 14.3791 | 12.6608 | 11.4445 | 11.0291 | 16.373 | 16.2557 | 16.1057 | 15.5996 | 15.2863 | 14.7812 | 14.0853 | 13.371 | 12.6883 | 10.1761 | 8.1781 | 7.2547
|  | OAKRIDGE PRIMARY | HE |  |  |  |  | 16.1496 | 16.0057 | 15.8087 | 15.3751 | 15.1098 | 14.673 | 14.1149 | 13.4036 | 12.72 | 10.1067 | 8.0904 | 6.8924 | 17.2353 | 17.1271 | 17.0506 | 16.7424 | 16.4863 | 16.171 | 15.7342 | 15.2026 | 14.7026 | 12.5945 | 11.0291 | 9.5955 | 16.373 | 16.2496 | 16.1169 | 15.6659 | 15.3812 | 14.9914 | 14.4638 | 13.8138 | 13.1955 | 10.9332 | 9.3485 | 8.4802
|  | OAKRIDGE PRIMARY | FB |  |  |  |  | 16.3036 | 16.2669 | 16.1291 | 16.0445 | 16.12 | 16.0557 | 15.8679 | 15.7363 | 15.4291 | 13.6924 | 11.5802 | 10.1108 | 17.3302 | 17.2526 | 17.1312 | 17.0353 | 17.0098 | 16.8342 | 16.4791 | 16.2342 | 15.8894 | 13.6363 | 10.5649 | 7.0822 | 16.5608 | 16.5189 | 16.422 | 16.3557 | 16.4353 | 16.3659 | 16.072 | 15.9312 | 15.6332 | 13.9036 | 11.9128 | 10.5394
COWLEY GSP | HEADINGTON BSP | OLD ROAD PRIMARY | MINIMUM HEADROOM | SP 55274 06426 | NO | NO | 0.666 | 9.8714 | 9.6418 | 9.4755 | 9.2714 | 8.9071 | 8.5418 | 7.9296 | 7.301 | 6.6082 | 4.9806 | 4.1806 | 3.6102 | 9.8122 | 9.6092 | 9.5765 | 9.5092 | 9.352 | 9.1561 | 8.8388 | 8.5143 | 8.1918 | 7.6408 | 5.7 | 2.3592 | 10.651 | 10.4061 | 10.3235 | 10.1898 | 9.9449 | 9.6918 | 9.2806 | 8.8622 | 8.3684 | 7.2551 | 6.3327 | 5.8765
|  | OLD ROAD PRIMARY | EE |  |  |  |  | 9.8827 | 9.6418 | 9.4755 | 9.3163 | 8.9714 | 8.6612 | 8.1633 | 7.6786 | 7.1327 | 5.4357 | 4.1806 | 3.6102 | 9.8214 | 9.6204 | 9.6184 | 9.5929 | 9.4276 | 9.2949 | 9.0684 | 8.8347 | 8.5939 | 8.0439 | 6.8541 | 5.4959 | 10.6551 | 10.4061 | 10.3296 | 10.2398 | 9.998 | 9.8061 | 9.4939 | 9.1561 | 8.7378 | 7.3663 | 6.3327 | 5.8765
|  | OLD ROAD PRIMARY | HT |  |  |  |  | 9.8908 | 9.6765 | 9.4867 | 9.2714 | 8.9071 | 8.5418 | 7.9296 | 7.301 | 6.6082 | 4.9806 | 4.1847 | 3.9531 | 9.8133 | 9.6092 | 9.5765 | 9.5092 | 9.352 | 9.1561 | 8.8388 | 8.5143 | 8.1918 | 7.6408 | 7.452 | 7.4 | 10.6643 | 10.4133 | 10.3235 | 10.1898 | 9.9449 | 9.6918 | 9.2806 | 8.8622 | 8.3684 | 7.2551 | 6.7306 | 6.6684
|  | OLD ROAD PRIMARY | HE |  |  |  |  | 9.8714 | 9.6612 | 9.499 | 9.3367 | 8.9929 | 8.7235 | 8.2571 | 7.8194 | 7.4959 | 6.3418 | 5.5133 | 5.0724 | 9.8122 | 9.6235 | 9.6204 | 9.5959 | 9.4347 | 9.301 | 9.0796 | 8.85 | 8.6745 | 8.2449 | 7.3357 | 6.0235 | 10.651 | 10.4153 | 10.3429 | 10.248 | 10.0031 | 9.8245 | 9.5265 | 9.2367 | 9.0061 | 8.1102 | 7.4714 | 7.1531
|  | OLD ROAD PRIMARY | FB |  |  |  |  | 10.0255 | 9.8714 | 9.8388 | 9.751 | 9.5776 | 9.401 | 9.3184 | 9.1908 | 9.1276 | 8.5592 | 7.4898 | 6.8031 | 9.8878 | 9.7031 | 9.7469 | 9.7765 | 9.6786 | 9.4327 | 9.3969 | 9.3388 | 9.3102 | 8.1459 | 5.7 | 2.3592 | 10.7357 | 10.5276 | 10.5316 | 10.4929 | 10.3469 | 10.1133 | 10.052 | 9.9694 | 9.9296 | 9.5735 | 8.7561 | 8.1306
COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD PRIMARY | MINIMUM HEADROOM | SP 50148 05901 | NO | NO | 19.76 | -3.8923 | -3.9097 | -3.9954 | -4.1454 | -6.5025 | -8.1831 | -10.1566 | -11.9413 | -13.4025 | -15.1138 | -15.8893 | -16.3413 | -1.7219 | -1.7678 | -1.8485 | -1.9801 | -3.6291 | -4.8015 | -6.2087 | -7.5934 | -8.7474 | -10.3454 | -12.0678 | -15.025 | -3.9485 | -4.0219 | -4.1505 | -4.3709 | -6.2597 | -7.7831 | -9.575 | -11.2005 | -12.5138 | -13.9954 | -15.1872 | -15.9923
|  | OXFORD PRIMARY | EE |  |  |  |  | -3.8923 | -3.9097 | -3.9954 | -4.1454 | -4.4587 | -5.9831 | -7.8872 | -9.678 | -11.0801 | -14.9597 | -15.8893 | -16.3413 | -1.7209 | -1.7678 | -1.8372 | -1.9566 | -2.1444 | -3.178 | -4.5342 | -5.8148 | -6.8178 | -10.3454 | -12.0678 | -13.4801 | -3.9485 | -4.0219 | -4.1505 | -4.3709 | -4.725 | -5.7291 | -7.4464 | -9.077 | -10.3434 | -13.8729 | -15.1872 | -15.9923
|  | OXFORD PRIMARY | HT |  |  |  |  | -3.8801 | -3.8872 | -3.9811 | -4.1403 | -6.5025 | -8.1831 | -10.1566 | -11.9413 | -13.4025 | -15.1138 | -15.7995 | -16.076 | -1.7219 | -1.7678 | -1.8485 | -1.9801 | -3.6291 | -4.8015 | -6.2087 | -7.5934 | -8.7474 | -10.1474 | -11.3536 | -11.7913 | -3.9372 | -4.0025 | -4.1342 | -4.3709 | -6.2597 | -7.7831 | -9.575 | -11.2005 | -12.5138 | -13.9954 | -14.725 | -15.0087
|  | OXFORD PRIMARY | HE |  |  |  |  | -3.8862 | -3.9015 | -3.9831 | -4.1423 | -4.4658 | -6.0311 | -7.9729 | -9.8117 | -11.2597 | -14.6036 | -15.2903 | -15.5372 | -1.7189 | -1.7668 | -1.8382 | -1.9566 | -2.1464 | -3.226 | -4.6189 | -5.9505 | -7.0311 | -9.9138 | -11.6097 | -12.5566 | -3.9393 | -4.0087 | -4.1331 | -4.3597 | -4.7229 | -5.7658 | -7.5423 | -9.226 | -10.5454 | -13.5974 | -14.2515 | -14.5005
|  | OXFORD PRIMARY | FB |  |  |  |  | -3.8352 | -3.827 | -3.8658 | -3.9301 | -4.1189 | -4.2607 | -5.6219 | -6.9627 | -7.8974 | -13.024 | -13.9709 | -14.6291 | -1.7036 | -1.7403 | -1.8036 | -1.8719 | -2.0076 | -2.1423 | -3.128 | -4.127 | -4.827 | -8.8934 | -11.3934 | -15.025 | -3.8638 | -3.9056 | -3.975 | -4.0627 | -4.2434 | -4.4525 | -5.427 | -6.6638 | -7.5117 | -12.2872 | -13.1464 | -14.1546
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | OXFORD SCIENCE PARK PRIMARY | MINIMUM HEADROOM | TBC | NO | NO | 27.185 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332
|  | OXFORD SCIENCE PARK PRIMARY | EE |  |  |  |  | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332
|  | OXFORD SCIENCE PARK PRIMARY | HT |  |  |  |  | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332
|  | OXFORD SCIENCE PARK PRIMARY | HE |  |  |  |  | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332
|  | OXFORD SCIENCE PARK PRIMARY | FB |  |  |  |  | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | 0.932 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | -0.388 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | OVERTON PRIMARY | MINIMUM HEADROOM | SU 52061 50913 | NO | NO | 1.96 | 23.9184 | 23.8388 | 23.6225 | 23.4399 | 23.1705 | 22.7205 | 20.9317 | 19.2154 | 17.5174 | 10.8388 | 8.345 | 7.8399 | 24.1562 | 24.099 | 23.9429 | 23.7715 | 23.595 | 23.3776 | 22.6858 | 21.9858 | 21.2848 | 17.4419 | 16.3205 | 15.8194 | 24.2827 | 24.198 | 23.9501 | 23.7674 | 23.545 | 23.2337 | 22.0429 | 20.8766 | 19.6735 | 14.2694 | 12.3899 | 12.0225
|  | OVERTON PRIMARY | EE |  |  |  |  | 23.9358 | 23.8388 | 23.6225 | 23.4501 | 23.197 | 22.7592 | 22.2327 | 20.3807 | 18.5776 | 11.248 | 8.4776 | 7.9694 | 24.1582 | 24.1001 | 23.945 | 23.7868 | 23.6348 | 23.4154 | 23.1225 | 22.4174 | 21.7327 | 17.5399 | 16.3205 | 15.9766 | 24.2827 | 24.198 | 23.9501 | 23.7786 | 23.5796 | 23.2592 | 22.8531 | 21.6419 | 20.4317 | 14.5103 | 12.3899 | 12.0225
|  | OVERTON PRIMARY | HT |  |  |  |  | 23.9215 | 23.8572 | 23.6378 | 23.4439 | 23.1715 | 22.747 | 20.9317 | 19.2154 | 17.5174 | 10.8388 | 8.345 | 7.8399 | 24.1582 | 24.1011 | 23.9429 | 23.7715 | 23.595 | 23.3776 | 22.6858 | 21.9858 | 21.2848 | 17.4419 | 16.4807 | 16.4194 | 24.2868 | 24.2062 | 23.9582 | 23.7674 | 23.545 | 23.2337 | 22.0429 | 20.8766 | 19.6735 | 14.2694 | 12.4072 | 12.1133
|  | OVERTON PRIMARY | HE |  |  |  |  | 23.9184 | 23.846 | 23.6317 | 23.4399 | 23.1705 | 22.7205 | 22.1929 | 20.9429 | 19.7745 | 14.3807 | 11.4776 | 9.6531 | 24.1562 | 24.099 | 23.945 | 23.7817 | 23.6307 | 23.397 | 23.1133 | 22.5531 | 22.0837 | 18.7021 | 17.4409 | 16.4674 | 24.2848 | 24.2041 | 23.9572 | 23.7725 | 23.5623 | 23.2337 | 22.8317 | 21.9623 | 21.1868 | 16.7674 | 14.5725 | 13.1694
|  | OVERTON PRIMARY | FB |  |  |  |  | 24.0205 | 24.0041 | 24.0205 | 24.0052 | 23.8756 | 23.7307 | 23.4684 | 23.4001 | 22.6654 | 19.0286 | 14.1633 | 11.8348 | 24.245 | 24.2041 | 24.196 | 24.1674 | 24.1021 | 23.9827 | 23.7439 | 23.6735 | 23.3348 | 21.4684 | 17.7143 | 15.8194 | 24.4123 | 24.3796 | 24.395 | 24.3766 | 24.3103 | 24.1939 | 23.845 | 23.7745 | 23.2909 | 20.6031 | 16.5256 | 14.597
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PADWORTH PRIMARY | MINIMUM HEADROOM | SU 62243 66052 | YES | NO | 0.121 | 5.0855 | 5.0957 | 5.0957 | 5.0865 | 4.9804 | 4.9018 | 4.8518 | 4.7385 | 4.6589 | 4.1885 | 4.0855 | 4.0844 | 4.5811 | 4.5811 | 4.5648 | 4.5526 | 4.3801 | 4.2964 | 4.2362 | 4.1199 | 4.0352 | 3.5403 | 3.3587 | 3.077 | 4.8806 | 4.8878 | 4.8837 | 4.8745 | 4.7765 | 4.7286 | 4.702 | 4.5653 | 4.4582 | 3.951 | 3.8184 | 3.7969
|  | PADWORTH PRIMARY | EE |  |  |  |  | 5.0855 | 5.0957 | 5.0967 | 5.0916 | 5.011 | 4.9651 | 4.8742 | 4.8008 | 4.7242 | 4.2395 | 4.1273 | 4.0987 | 4.5811 | 4.5811 | 4.5679 | 4.5587 | 4.4219 | 4.3474 | 4.2444 | 4.1648 | 4.077 | 3.5403 | 3.3587 | 3.2291 | 4.8806 | 4.8878 | 4.8867 | 4.8786 | 4.7969 | 4.7571 | 4.702 | 4.601 | 4.4898 | 3.9602 | 3.8245 | 3.7969
|  | PADWORTH PRIMARY | HT |  |  |  |  | 5.0855 | 5.0957 | 5.0957 | 5.0865 | 4.9804 | 4.9018 | 4.8518 | 4.7385 | 4.6589 | 4.1885 | 4.0855 | 4.0844 | 4.5821 | 4.5811 | 4.5648 | 4.5526 | 4.3801 | 4.2964 | 4.2362 | 4.1199 | 4.0352 | 3.5526 | 3.423 | 3.3944 | 4.8806 | 4.8878 | 4.8837 | 4.8745 | 4.7765 | 4.7286 | 4.7051 | 4.5653 | 4.4582 | 3.951 | 3.8184 | 3.8265
|  | PADWORTH PRIMARY | HE |  |  |  |  | 5.0855 | 5.0957 | 5.0967 | 5.0916 | 5.0099 | 4.963 | 4.9048 | 4.7855 | 4.7334 | 4.3375 | 4.3671 | 4.3661 | 4.5811 | 4.5811 | 4.5679 | 4.5587 | 4.4209 | 4.3464 | 4.277 | 4.1495 | 4.0883 | 3.6383 | 3.6056 | 3.5046 | 4.8806 | 4.8878 | 4.8857 | 4.8786 | 4.7969 | 4.7571 | 4.7276 | 4.5806 | 4.502 | 4.0959 | 4.1776 | 4.1929
|  | PADWORTH PRIMARY | FB |  |  |  |  | 5.1028 | 5.1161 | 5.1232 | 5.1314 | 5.1324 | 5.1334 | 5.1273 | 5.1161 | 5.114 | 4.9089 | 4.4497 | 4.2814 | 4.6056 | 4.6036 | 4.5944 | 4.5913 | 4.5832 | 4.5658 | 4.5342 | 4.5036 | 4.4821 | 4.076 | 3.4923 | 3.077 | 4.901 | 4.9092 | 4.9153 | 4.9224 | 4.9214 | 4.9163 | 4.9051 | 4.8918 | 4.8867 | 4.699 | 4.2449 | 4.0316
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PANGBOURNE PRIMARY | MINIMUM HEADROOM | SU 62960 76144 | NO | NO | 1.276 | 14.4926 | 14.564 | 14.4119 | 14.4089 | 14.2109 | 13.9946 | 13.6711 | 13.3099 | 12.9966 | 11.8926 | 11.4079 | 11.3915 | 17.9038 | 17.8874 | 17.6477 | 17.5905 | 17.3395 | 17.0936 | 16.7334 | 16.3211 | 15.9803 | 14.7548 | 14.0415 | 13.216 | 15.9405 | 15.9803 | 15.8007 | 15.7619 | 15.513 | 15.2762 | 14.9201 | 14.5058 | 14.1711 | 13.0079 | 12.5119 | 12.4507
|  | PANGBOURNE PRIMARY | EE |  |  |  |  | 14.4936 | 14.5681 | 14.4221 | 14.4589 | 14.3058 | 14.1028 | 13.8385 | 13.4874 | 13.2242 | 12.1007 | 11.5589 | 11.415 | 17.9048 | 17.8915 | 17.6507 | 17.6201 | 17.3977 | 17.1538 | 16.8313 | 16.4334 | 16.1313 | 14.7599 | 14.0415 | 13.614 | 15.9415 | 15.9823 | 15.8058 | 15.8017 | 15.5885 | 15.3568 | 15.0415 | 14.6477 | 14.3568 | 13.1599 | 12.5966 | 12.4507
|  | PANGBOURNE PRIMARY | HT |  |  |  |  | 14.4936 | 14.564 | 14.4119 | 14.4089 | 14.2109 | 13.9946 | 13.6711 | 13.3099 | 12.9966 | 11.8926 | 11.4079 | 11.3915 | 17.9058 | 17.8874 | 17.6477 | 17.5905 | 17.3395 | 17.0936 | 16.7334 | 16.3211 | 15.9803 | 14.7548 | 14.2323 | 14.1915 | 15.9415 | 15.9803 | 15.8007 | 15.7619 | 15.513 | 15.2762 | 14.9201 | 14.5058 | 14.1711 | 13.0079 | 12.5119 | 12.5109
|  | PANGBOURNE PRIMARY | HE |  |  |  |  | 14.4926 | 14.567 | 14.4323 | 14.4548 | 14.3313 | 14.1119 | 13.815 | 13.4834 | 13.2099 | 12.4028 | 11.9477 | 11.8283 | 17.9038 | 17.8915 | 17.6579 | 17.6181 | 17.4303 | 17.1711 | 16.8109 | 16.4385 | 16.1293 | 15.0528 | 14.4252 | 14.0089 | 15.9405 | 15.9813 | 15.815 | 15.7977 | 15.6221 | 15.3721 | 15.017 | 14.6466 | 14.367 | 13.4874 | 13.0242 | 12.9017
|  | PANGBOURNE PRIMARY | FB |  |  |  |  | 14.6079 | 14.7109 | 14.814 | 14.8885 | 14.9477 | 14.8426 | 14.763 | 14.7232 | 14.5885 | 13.9089 | 12.9997 | 12.4589 | 17.9895 | 17.9905 | 17.9936 | 17.9854 | 17.9558 | 17.7497 | 17.5752 | 17.4589 | 17.2293 | 16.0568 | 14.5966 | 13.216 | 16.0497 | 16.1119 | 16.1742 | 16.214 | 16.2313 | 16.1272 | 16.013 | 15.9538 | 15.7783 | 14.9385 | 13.9752 | 13.3854
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE PRIMARY | MINIMUM HEADROOM | SU 51369 08259 | NO | NO | 3.285 | 17.2459 | 17.2429 | 16.8551 | 16.3612 | 15.8378 | 14.7163 | 13.6133 | 12.4663 | 11.349 | 7.4327 | 4.5265 | 3.551 | 19.0663 | 19.0173 | 18.6276 | 18.2735 | 17.9102 | 17.2847 | 16.5571 | 15.7847 | 15.049 | 12.3857 | 10.4929 | 7.2286 | 18.1582 | 18.1378 | 17.7622 | 17.3439 | 16.8857 | 16.0163 | 15.099 | 14.1276 | 13.1878 | 10.0316 | 7.9378 | 7.5582
|  | PARK GATE PRIMARY | EE |  |  |  |  | 17.2541 | 17.3439 | 17.0204 | 16.6173 | 16.2327 | 15.202 | 14.0837 | 12.9429 | 11.8224 | 8.0102 | 5.1898 | 3.999 | 19.0714 | 19.0653 | 18.6847 | 18.3439 | 18.002 | 17.4245 | 16.6786 | 15.9327 | 15.2153 | 12.3857 | 10.4929 | 9.4235 | 18.1663 | 18.2092 | 17.8673 | 17.5051 | 17.1378 | 16.3286 | 15.3918 | 14.4316 | 13.4959 | 10.3082 | 8.1918 | 7.5582
|  | PARK GATE PRIMARY | HT |  |  |  |  | 17.2459 | 17.2429 | 16.8551 | 16.3612 | 15.8378 | 14.7163 | 13.6133 | 12.4663 | 11.349 | 7.4327 | 4.5265 | 3.551 | 19.0663 | 19.0173 | 18.6276 | 18.2735 | 17.9102 | 17.2847 | 16.5571 | 15.7847 | 15.049 | 12.7816 | 11.5816 | 11.6163 | 18.1582 | 18.1378 | 17.7622 | 17.3439 | 16.8857 | 16.0163 | 15.099 | 14.1276 | 13.1878 | 10.0316 | 7.9378 | 7.5653
|  | PARK GATE PRIMARY | HE |  |  |  |  | 17.2592 | 17.348 | 17.0541 | 16.6418 | 16.1847 | 15.2337 | 14.1633 | 13.0184 | 11.8898 | 8.6653 | 6.4806 | 5.6031 | 19.0694 | 19.0643 | 18.6918 | 18.3847 | 18.0051 | 17.4469 | 16.7255 | 15.9602 | 15.2265 | 12.6745 | 11.0786 | 9.7684 | 18.1653 | 18.2122 | 17.8918 | 17.5327 | 17.1071 | 16.3531 | 15.4561 | 14.4898 | 13.5469 | 10.8316 | 9.248 | 8.7031
|  | PARK GATE PRIMARY | FB |  |  |  |  | 17.5571 | 17.6673 | 17.7592 | 17.799 | 17.6347 | 17.4163 | 17.15 | 16.8745 | 16.5551 | 14.4765 | 12.3571 | 11.1929 | 19.2673 | 19.2316 | 19.1663 | 19.1265 | 18.8082 | 18.4571 | 18.0724 | 17.6755 | 17.2112 | 14.3347 | 10.8786 | 7.2286 | 18.4224 | 18.5061 | 18.5592 | 18.6204 | 18.4255 | 18.2102 | 17.95 | 17.6857 | 17.3582 | 15.2459 | 13.1969 | 12.1092
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PARK HOUSE PRIMARY | MINIMUM HEADROOM | SU 23138 43780 | NO | NO | 0.035 | 3.5133 | 3.5224 | 3.5133 | 3.4765 | 3.4643 | 3.3806 | 3.2898 | 3.1959 | 3.1071 | 2.999 | 2.8602 | 2.7582 | 3.7071 | 3.7112 | 3.7031 | 3.6847 | 3.6755 | 3.6439 | 3.5929 | 3.5337 | 3.4816 | 3.3673 | 3.1694 | 2.8878 | 3.75 | 3.7561 | 3.7459 | 3.7143 | 3.6939 | 3.6327 | 3.5786 | 3.5 | 3.4224 | 3.3429 | 3.2337 | 3.1643
|  | PARK HOUSE PRIMARY | EE |  |  |  |  | 3.5133 | 3.5224 | 3.5133 | 3.4776 | 3.4643 | 3.3857 | 3.3031 | 3.2112 | 3.1276 | 2.999 | 2.8755 | 2.8031 | 3.7082 | 3.7122 | 3.7031 | 3.6857 | 3.6755 | 3.6449 | 3.598 | 3.5367 | 3.4867 | 3.3704 | 3.2439 | 3.15 | 3.75 | 3.7561 | 3.7459 | 3.7153 | 3.6939 | 3.6398 | 3.5878 | 3.5082 | 3.4347 | 3.3449 | 3.2531 | 3.2082
|  | PARK HOUSE PRIMARY | HT |  |  |  |  | 3.5143 | 3.5235 | 3.5184 | 3.4888 | 3.4704 | 3.3969 | 3.3173 | 3.2306 | 3.152 | 3.0327 | 2.8949 | 2.8316 | 3.7071 | 3.7112 | 3.7041 | 3.6847 | 3.6765 | 3.6459 | 3.5969 | 3.5398 | 3.4867 | 3.4102 | 3.3306 | 3.3235 | 3.75 | 3.7561 | 3.748 | 3.7214 | 3.7051 | 3.648 | 3.5878 | 3.5194 | 3.4469 | 3.3602 | 3.2684 | 3.2449
|  | PARK HOUSE PRIMARY | HE |  |  |  |  | 3.5163 | 3.5255 | 3.5143 | 3.4765 | 3.4653 | 3.3806 | 3.2898 | 3.1959 | 3.1071 | 3 | 2.8602 | 2.7582 | 3.7102 | 3.7122 | 3.7041 | 3.6847 | 3.6765 | 3.6439 | 3.5929 | 3.5337 | 3.4816 | 3.3673 | 3.2255 | 3.1061 | 3.752 | 3.7571 | 3.7459 | 3.7143 | 3.6949 | 3.6327 | 3.5786 | 3.5 | 3.4224 | 3.3429 | 3.2337 | 3.1643
|  | PARK HOUSE PRIMARY | FB |  |  |  |  | 3.5571 | 3.5735 | 3.5857 | 3.5837 | 3.5837 | 3.5602 | 3.5367 | 3.5235 | 3.4867 | 3.2469 | 3.1337 | 3.0592 | 3.7265 | 3.7327 | 3.7337 | 3.7286 | 3.7214 | 3.6949 | 3.6745 | 3.6531 | 3.6265 | 3.402 | 3.1694 | 2.8878 | 3.7918 | 3.8041 | 3.8112 | 3.8092 | 3.8051 | 3.7867 | 3.7633 | 3.751 | 3.7245 | 3.5265 | 3.4378 | 3.3704
MINETY GSP | STRATTON (MAIN) BSP | PARK NORTH PRIMARY | MINIMUM HEADROOM | SU 18052 84542 | NO | NO | 4.55 | 8.0004 | 7.8208 | 7.6249 | 7.2167 | 6.8994 | 6.0341 | 5.0524 | 4.0065 | 3.0137 | -1.6435 | -5.3078 | -7.3527 | 11.4922 | 11.2361 | 11.0586 | 10.7341 | 10.4392 | 9.9351 | 9.3341 | 8.68 | 8.0678 | 4.8647 | 1.3769 | -4.0578 | 10.0851 | 9.9259 | 9.729 | 9.3494 | 9.03 | 8.3157 | 7.5269 | 6.6667 | 5.8698 | 2.0453 | -0.81184 | -2.3159
|  | PARK NORTH PRIMARY | EE |  |  |  |  | 8.0004 | 7.9963 | 7.6249 | 7.2167 | 6.929 | 6.0341 | 5.0524 | 4.0065 | 3.0137 | -1.6435 | -5.3078 | -7.3527 | 11.4922 | 11.4596 | 11.0586 | 10.7341 | 10.5004 | 9.9933 | 9.3861 | 8.7106 | 8.0739 | 4.8647 | 2.4014 | 0.08 | 10.0851 | 10.0882 | 9.729 | 9.3494 | 9.08 | 8.3576 | 7.5463 | 6.6667 | 5.8698 | 2.0453 | -0.81184 | -2.3159
|  | PARK NORTH PRIMARY | HT |  |  |  |  | 8.0208 | 7.8208 | 7.6739 | 7.2647 | 6.8994 | 6.0402 | 5.0912 | 4.1004 | 3.1616 | -1.3914 | -4.7782 | -6.4822 | 11.4953 | 11.2361 | 11.0667 | 10.7463 | 10.4392 | 9.9351 | 9.3341 | 8.68 | 8.0678 | 5.7412 | 4.3759 | 3.7922 | 10.0933 | 9.9259 | 9.779 | 9.3892 | 9.03 | 8.3157 | 7.5269 | 6.682 | 5.9208 | 2.2484 | -0.36388 | -1.5118
|  | PARK NORTH PRIMARY | HE |  |  |  |  | 8.0198 | 8.032 | 7.6749 | 7.2657 | 6.98 | 6.1555 | 5.2422 | 4.278 | 3.3331 | -0.5251 | -3.2098 | -4.8108 | 11.4973 | 11.4667 | 11.0688 | 10.7453 | 10.5167 | 10.0137 | 9.4137 | 8.7606 | 8.1086 | 5.1841 | 2.9861 | 0.71776 | 10.1035 | 10.1229 | 9.7831 | 9.3953 | 9.1167 | 8.4361 | 7.6698 | 6.8524 | 6.0759 | 2.9463 | 0.89531 | -0.25571
|  | PARK NORTH PRIMARY | FB |  |  |  |  | 8.2739 | 8.3076 | 8.2912 | 8.1453 | 8.0749 | 7.8443 | 7.5239 | 7.1841 | 6.832 | 4.4402 | 1.4555 | -0.60571 | 11.628 | 11.5341 | 11.4035 | 11.128 | 10.9055 | 10.5596 | 10.1127 | 9.6647 | 9.1882 | 5.9147 | 1.3769 | -4.0578 | 10.3718 | 10.3933 | 10.3922 | 10.2729 | 10.2127 | 10.03 | 9.7494 | 9.4463 | 9.131 | 6.8596 | 4.2157 | 2.3831
WILLESDEN GSP | ACTON LANE BSP | PARK ROYAL PRIMARY | MINIMUM HEADROOM | TQ 20137 82215 | NO | YES | 4.396 | 1.4885 | 0.76405 | 38.1599 | 38.115 | 38.0374 | 37.9517 | 37.6946 | 37.4272 | 37.1803 | 36.1772 | 35.5813 | 35.3762 | 3.9498 | 2.9528 | 37.9772 | 37.9527 | 37.8895 | 37.8313 | 37.5609 | 37.2701 | 36.9976 | 35.9017 | 35.2231 | 34.864 | 3.1263 | 2.3253 | 38.1497 | 38.1231 | 38.065 | 37.9997 | 37.6833 | 37.3691 | 37.0772 | 35.8874 | 35.167 | 34.9048
|  | PARK ROYAL PRIMARY | EE |  |  |  |  | 1.4885 | 1.4834 | 38.1619 | 38.1221 | 38.0405 | 37.9762 | 37.6946 | 37.4272 | 37.1803 | 36.1772 | 35.5813 | 35.3762 | 3.9528 | 3.9528 | 37.9844 | 37.9619 | 37.9089 | 37.867 | 37.5609 | 37.2701 | 36.9976 | 35.9017 | 35.2231 | 34.864 | 3.1263 | 3.1212 | 38.1538 | 38.1313 | 38.0803 | 38.0211 | 37.6833 | 37.3691 | 37.0772 | 35.8874 | 35.167 | 34.9048
|  | PARK ROYAL PRIMARY | HT |  |  |  |  | 1.4916 | 0.76405 | 38.1742 | 38.1344 | 38.0374 | 37.9578 | 37.864 | 37.6384 | 37.4323 | 36.6456 | 36.1762 | 36.016 | 3.9528 | 2.9528 | 37.9874 | 37.966 | 37.8895 | 37.8313 | 37.7578 | 37.5323 | 37.3303 | 36.6333 | 36.2211 | 36.0915 | 3.1273 | 2.3253 | 38.1609 | 38.1384 | 38.065 | 37.9997 | 37.9058 | 37.6405 | 37.415 | 36.5293 | 36.0007 | 35.8333
|  | PARK ROYAL PRIMARY | HE |  |  |  |  | 1.4896 | 1.4834 | 38.1599 | 38.115 | 38.0384 | 37.9517 | 37.8609 | 37.7405 | 37.6282 | 37.265 | 37.0538 | 36.9558 | 3.9508 | 3.9487 | 37.9772 | 37.9527 | 37.9058 | 37.8517 | 37.7711 | 37.6548 | 37.5466 | 37.1568 | 36.9048 | 36.6956 | 3.1263 | 3.1222 | 38.1497 | 38.1231 | 38.0762 | 38.0027 | 37.8987 | 37.767 | 37.6466 | 37.2507 | 37.015 | 36.9027
|  | PARK ROYAL PRIMARY | FB |  |  |  |  | 1.5028 | 1.5038 | 38.9864 | 38.2507 | 38.1711 | 38.1364 | 38.1099 | 38.0487 | 38.0099 | 37.7742 | 37.5813 | 37.3497 | 3.9498 | 3.9426 | 39.016 | 38.0017 | 37.9384 | 37.8997 | 37.8538 | 37.7905 | 37.7425 | 37.418 | 37.0446 | 36.4007 | 3.1365 | 3.1375 | 39.0191 | 38.216 | 38.167 | 38.1415 | 38.118 | 38.0731 | 38.0425 | 37.8048 | 37.5833 | 37.3119
MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE NORTH PRIMARY | MINIMUM HEADROOM | SZ 03222 92233 | NO | YES | 3.079 | 1.6959 | 1.4847 | 1.1163 | 0.37653 | -0.4898 | -2.3714 | -4.3439 | -6.298 | -8.2306 | -14.3143 | -18.1327 | -19.4786 | 6.7673 | 6.4939 | 6.2276 | 5.8184 | 5.25 | 4.3337 | 3.2796 | 2.1602 | 1.0306 | -2.398 | -6.55 | -13.4245 | 5.002 | 4.7541 | 4.4398 | 3.8337 | 3.0745 | 1.6398 | 0.088776 | -1.4939 | -3.0755 | -8.1286 | -11.0816 | -11.8694
|  | PARKSTONE NORTH PRIMARY | EE |  |  |  |  | 1.7 | 1.598 | 1.2878 | 0.71327 | 0.057143 | -1.5582 | -3.3408 | -4.9276 | -6.5694 | -12.0755 | -15.6367 | -17.5408 | 6.7816 | 6.5541 | 6.302 | 5.9204 | 5.4827 | 4.7143 | 3.7224 | 2.8235 | 1.8122 | -2.398 | -5.2388 | -7.8316 | 5.0163 | 4.8235 | 4.5378 | 4.051 | 3.4745 | 2.249 | 0.80612 | -0.47143 | -1.8582 | -6.65 | -9.498 | -10.8408
|  | PARKSTONE NORTH PRIMARY | HT |  |  |  |  | 1.6959 | 1.4847 | 1.1163 | 0.37653 | -0.4898 | -2.3714 | -4.3439 | -6.298 | -8.2306 | -14.3143 | -18.1327 | -19.4786 | 6.7673 | 6.4939 | 6.2276 | 5.8184 | 5.25 | 4.3337 | 3.2796 | 2.1602 | 1.0306 | -2.2653 | -3.7337 | -4.1122 | 5.002 | 4.7541 | 4.4398 | 3.8337 | 3.0745 | 1.6398 | 0.088776 | -1.4939 | -3.0755 | -8.1286 | -11.0816 | -11.8694
|  | PARKSTONE NORTH PRIMARY | HE |  |  |  |  | 1.7143 | 1.6245 | 1.3439 | 0.68673 | -0.097959 | -1.4765 | -3.0704 | -4.4418 | -5.848 | -10.4133 | -13.452 | -14.9929 | 6.7827 | 6.5602 | 6.3255 | 5.9602 | 5.4592 | 4.7327 | 3.7306 | 2.8602 | 1.902 | -1.8878 | -4.7296 | -7.4765 | 5.0265 | 4.8469 | 4.5939 | 4.0633 | 3.3704 | 2.2939 | 0.94286 | -0.20102 | -1.4245 | -5.3551 | -7.7541 | -8.8908
|  | PARKSTONE NORTH PRIMARY | FB |  |  |  |  | 1.9949 | 2.2235 | 2.3276 | 2.1388 | 1.9531 | 1.651 | 1.3122 | 1.0449 | 0.72857 | -1.9776 | -5.7051 | -7.9531 | 6.8653 | 6.8327 | 6.7735 | 6.4347 | 6.1163 | 5.6163 | 5.0888 | 4.5408 | 3.9173 | -0.35714 | -6.55 | -13.4245 | 5.3204 | 5.4908 | 5.6061 | 5.3541 | 5.1827 | 4.8918 | 4.5684 | 4.2673 | 3.9082 | 1.15 | -2.4194 | -4.5173
MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE SOUTH PRIMARY | MINIMUM HEADROOM | SZ 04762 89848 | NO | YES | 1.616 | 19.802 | 19.9551 | 19.9439 | 19.7796 | 19.3663 | 18.5796 | 17.7133 | 16.7857 | 15.9429 | 12.801 | 10.7337 | 9.9592 | 20.6449 | 20.698 | 20.6122 | 20.4592 | 20.0418 | 19.5939 | 19.0439 | 18.4357 | 17.9092 | 15.8367 | 13.8724 | 10.1204 | 19.2082 | 19.3031 | 19.2653 | 19.1 | 18.6602 | 18.052 | 17.3571 | 16.602 | 15.9398 | 13.3204 | 11.7286 | 10.999
|  | PARKSTONE SOUTH PRIMARY | EE |  |  |  |  | 19.8061 | 19.9684 | 19.9888 | 19.8663 | 19.5469 | 18.6939 | 17.8245 | 16.9184 | 16.0541 | 13.0888 | 11.0204 | 9.9592 | 20.651 | 20.7235 | 20.6531 | 20.5276 | 20.1959 | 19.7153 | 19.202 | 18.6551 | 18.1418 | 15.8367 | 14.199 | 12.8571 | 19.2122 | 19.3235 | 19.2857 | 19.1531 | 18.8408 | 18.1704 | 17.4898 | 16.7776 | 16.102 | 13.5061 | 11.7816 | 10.999
|  | PARKSTONE SOUTH PRIMARY | HT |  |  |  |  | 19.802 | 19.9551 | 19.9439 | 19.7796 | 19.3663 | 18.5796 | 17.7133 | 16.7857 | 15.9429 | 12.801 | 10.7337 | 10.0939 | 20.6449 | 20.698 | 20.6122 | 20.4592 | 20.0418 | 19.5939 | 19.0439 | 18.4357 | 17.9092 | 16.0306 | 15.1888 | 15.0041 | 19.2082 | 19.3031 | 19.2653 | 19.1051 | 18.6602 | 18.052 | 17.3571 | 16.602 | 15.9398 | 13.3204 | 11.7286 | 11.3622
|  | PARKSTONE SOUTH PRIMARY | HE |  |  |  |  | 19.8092 | 19.9755 | 19.999 | 19.8061 | 19.4255 | 18.699 | 17.9888 | 17.1735 | 16.4449 | 13.9776 | 12.2173 | 11.4612 | 20.652 | 20.7265 | 20.6551 | 20.5224 | 20.1827 | 19.6929 | 19.2469 | 18.6724 | 18.1918 | 16.0612 | 14.4592 | 13.1306 | 19.2153 | 19.3286 | 19.2959 | 19.1 | 18.7673 | 18.1663 | 17.6 | 16.9214 | 16.3327 | 14.202 | 12.7837 | 12.2224
|  | PARKSTONE SOUTH PRIMARY | FB |  |  |  |  | 20.0673 | 20.2592 | 20.4082 | 20.5316 | 20.4663 | 20.3867 | 20.2816 | 20.149 | 20.001 | 18.7357 | 16.6163 | 15.2969 | 20.7939 | 20.8071 | 20.7878 | 20.8163 | 20.7092 | 20.5 | 20.251 | 19.9704 | 19.6735 | 17.248 | 13.8724 | 10.1204 | 19.452 | 19.5745 | 19.6663 | 19.6684 | 19.6173 | 19.5337 | 19.4255 | 19.2878 | 19.1337 | 17.8224 | 15.8143 | 14.5388
FLEET-BRAMLEY GSP | WOKINGHAM BSP | PEACOCK FARM PRIMARY | MINIMUM HEADROOM | SU 84770 68709 | NO | NO | 6.854 | 6.2674 | 6.2583 | 6.1256 | 5.945 | 5.8409 | 5.6838 | 5.3134 | 4.8542 | 4.3379 | 2.394 | 1.0389 | 0.49602 | 6.0317 | 6.0032 | 5.8991 | 5.8001 | 5.6328 | 5.4215 | 4.9634 | 4.3817 | 3.8328 | 1.6868 | 0.26643 | -0.40092 | 6.7807 | 6.7613 | 6.6236 | 6.493 | 6.3603 | 6.1348 | 5.6603 | 5.0695 | 4.5154 | 2.3868 | 0.99092 | 0.495
|  | PEACOCK FARM PRIMARY | EE |  |  |  |  | 6.2674 | 6.2593 | 6.1317 | 5.9654 | 5.8756 | 5.7787 | 5.3134 | 4.8542 | 4.3379 | 2.394 | 1.0389 | 0.49602 | 6.0317 | 6.0062 | 5.9113 | 5.8277 | 5.6358 | 5.5583 | 4.9634 | 4.3817 | 3.8328 | 1.6868 | 0.26643 | -0.40092 | 6.7807 | 6.7613 | 6.6266 | 6.5154 | 6.3603 | 6.2685 | 5.6603 | 5.0695 | 4.5154 | 2.3868 | 0.99092 | 0.495
|  | PEACOCK FARM PRIMARY | HT |  |  |  |  | 6.2695 | 6.2583 | 6.1256 | 5.945 | 5.8409 | 5.6838 | 5.5307 | 5.1756 | 4.7501 | 3.096 | 1.9858 | 1.5797 | 6.0317 | 6.0032 | 5.8991 | 5.8001 | 5.695 | 5.4215 | 5.2226 | 4.8277 | 4.3899 | 2.8419 | 1.9552 | 1.7185 | 6.7828 | 6.7623 | 6.6236 | 6.493 | 6.3919 | 6.1348 | 5.9297 | 5.5154 | 5.0766 | 3.3797 | 2.3083 | 1.9817
|  | PEACOCK FARM PRIMARY | HE |  |  |  |  | 6.2685 | 6.2603 | 6.1338 | 5.9695 | 5.8787 | 5.7848 | 5.6338 | 5.4236 | 5.1511 | 4.2062 | 3.5583 | 3.2317 | 6.0317 | 6.0042 | 5.9103 | 5.8266 | 5.6328 | 5.5552 | 5.347 | 5.1021 | 4.8083 | 3.7919 | 3.143 | 2.6266 | 6.7807 | 6.7623 | 6.6307 | 6.5174 | 6.3603 | 6.2705 | 6.0562 | 5.797 | 5.5052 | 4.5756 | 3.995 | 3.7236
|  | PEACOCK FARM PRIMARY | FB |  |  |  |  | 6.3164 | 6.3246 | 6.2501 | 6.1542 | 6.1501 | 6.1287 | 6.097 | 6.0695 | 6.0542 | 5.7583 | 5.3787 | 4.7593 | 6.0695 | 6.043 | 5.9797 | 5.9144 | 5.8562 | 5.7797 | 5.6889 | 5.596 | 5.5634 | 4.8705 | 3.8409 | 2.4021 | 6.8583 | 6.8593 | 6.794 | 6.7389 | 6.7287 | 6.6991 | 6.6583 | 6.6195 | 6.6266 | 6.2338 | 5.6593 | 5.0736
WILLESDEN GSP |  | PERIVALE PRIMARY | MINIMUM HEADROOM | TQ 17544 82947 | NO | YES | 16.031 | 9.8157 | 9.7964 | 9.7913 | 9.6984 | 9.4433 | 8.9637 | 7.5535 | 4.4433 | 2.8392 | -4.024 | -14.3292 | -20.9302 | 13.9821 | 13.9811 | 13.9321 | 13.8902 | 13.6953 | 13.4035 | 11.7423 | 7.5933 | 5.6484 | -0.96793 | -12.3853 | -20.9332 | 11.727 | 11.7117 | 11.578 | 11.4178 | 10.9984 | 10.4913 | 8.7841 | 4.6953 | 2.7576 | -4.4598 | -16.3251 | -24.1455
|  | PERIVALE PRIMARY | EE |  |  |  |  | 9.8157 | 9.7964 | 9.7913 | 9.7219 | 9.4994 | 9.0372 | 8.2076 | 7.0882 | 5.3862 | -0.33323 | -11.573 | -15.8353 | 13.9831 | 13.9831 | 13.9351 | 13.8902 | 13.7351 | 13.4219 | 12.4974 | 10.9219 | 8.7729 | 2.6617 | -10.4179 | -16.0547 | 11.727 | 11.7117 | 11.578 | 11.4208 | 11.0331 | 10.5351 | 9.5443 | 8.0066 | 5.8739 | -0.14752 | -13.1394 | -17.9985
|  | PERIVALE PRIMARY | HT |  |  |  |  | 9.8321 | 9.8678 | 9.8423 | 9.7698 | 9.4872 | 9.178 | 7.828 | 6.2902 | 2.8392 | -4.024 | -14.3292 | -20.9302 | 13.9821 | 13.9831 | 13.9331 | 13.8913 | 13.6953 | 13.4076 | 11.7423 | 9.7586 | 5.6484 | -0.96793 | -12.3853 | -20.1118 | 11.7413 | 11.7525 | 11.6249 | 11.4566 | 11.0147 | 10.6137 | 8.9147 | 6.9229 | 2.7576 | -4.4598 | -16.3251 | -24.1455
|  | PERIVALE PRIMARY | HE |  |  |  |  | 9.8249 | 9.8137 | 9.7923 | 9.6984 | 9.4433 | 8.9637 | 7.5535 | 4.4433 | 4.1117 | -2.4914 | -9.8006 | -18.2853 | 13.9821 | 13.9811 | 13.9321 | 13.8923 | 13.728 | 13.4035 | 11.7637 | 7.5933 | 7.1229 | -0.73221 | -9.6996 | -20.9332 | 11.7362 | 11.7321 | 11.5964 | 11.4178 | 10.9984 | 10.4913 | 8.7841 | 4.6953 | 4.2739 | -3.1098 | -11.6271 | -21.8904
|  | PERIVALE PRIMARY | FB |  |  |  |  | 9.9494 | 10.0341 | 10.0974 | 10.1096 | 10.0698 | 10.078 | 9.726 | 9.2464 | 8.277 | 5.1178 | -0.51078 | -5.474 | 14.028 | 14.0402 | 14.0351 | 13.9994 | 13.9035 | 13.8423 | 13.2545 | 12.3923 | 10.9953 | 5.629 | -2.2894 | -10.8128 | 11.8464 | 11.9004 | 11.9515 | 11.9219 | 11.7739 | 11.7617 | 11.2392 | 10.5362 | 9.3076 | 5.0249 | -1.221 | -6.7985
FLEET-BRAMLEY GSP | FERNHURST BSP | PETERSFIELD PRIMARY | MINIMUM HEADROOM | SU 74173 23420 | NO | NO | 8.678 | 4.5588 | 4.669 | 4.5302 | 4.2924 | 3.9771 | 3.5251 | 2.9057 | 2.1935 | 1.4516 | -0.38614 | -1.5178 | -1.8872 | 9.1792 | 9.2567 | 8.9404 | 8.6496 | 8.2771 | 7.6935 | 7.0159 | 6.2812 | 5.5271 | 3.3894 | 1.5302 | -2.2892 | 6.0343 | 6.1128 | 5.9598 | 5.7006 | 5.3455 | 4.7598 | 4.0986 | 3.3659 | 2.5894 | 0.58733 | -0.47389 | -0.67798
|  | PETERSFIELD PRIMARY | EE |  |  |  |  | 4.5639 | 4.6771 | 4.6179 | 4.5037 | 4.319 | 4.0241 | 3.6537 | 3.22 | 2.7894 | 1.1108 | -0.22389 | -0.80247 | 9.1924 | 9.2639 | 9.0047 | 8.8067 | 8.5588 | 8.0996 | 7.5302 | 6.9169 | 6.2781 | 3.7873 | 2.0179 | 0.6506 | 6.0414 | 6.12 | 6.0292 | 5.8924 | 5.6832 | 5.3577 | 4.8394 | 4.2751 | 3.6781 | 1.7098 | 0.41284 | -0.077976
|  | PETERSFIELD PRIMARY | HT |  |  |  |  | 4.5608 | 4.669 | 4.5302 | 4.2924 | 3.9771 | 3.5251 | 2.9057 | 2.1935 | 1.4516 | -0.38614 | -1.5178 | -1.8872 | 9.1884 | 9.2567 | 8.9404 | 8.6496 | 8.2771 | 7.6935 | 7.0159 | 6.2812 | 5.5271 | 3.3894 | 2.2986 | 1.9812 | 6.0384 | 6.1128 | 5.9598 | 5.7006 | 5.3455 | 4.7598 | 4.0986 | 3.3659 | 2.5894 | 0.58733 | -0.47389 | -0.67798
|  | PETERSFIELD PRIMARY | HE |  |  |  |  | 4.5588 | 4.6771 | 4.619 | 4.4996 | 4.3088 | 4.0098 | 3.6475 | 3.2088 | 2.7996 | 1.37 | 0.19549 | -0.33206 | 9.1792 | 9.2639 | 9.0037 | 8.8026 | 8.5496 | 8.0904 | 7.5445 | 6.9302 | 6.3628 | 3.9353 | 2.3486 | 0.9557 | 6.0343 | 6.12 | 6.0292 | 5.8894 | 5.6771 | 5.3424 | 4.8557 | 4.2904 | 3.769 | 1.9526 | 0.91692 | 0.48427
|  | PETERSFIELD PRIMARY | FB |  |  |  |  | 4.7139 | 4.8832 | 5.0179 | 5.0741 | 5.0894 | 5.0465 | 4.9067 | 4.7781 | 4.6332 | 3.4598 | 1.7924 | 0.63733 | 9.3475 | 9.3649 | 9.4292 | 9.3792 | 9.269 | 9.0404 | 8.5914 | 8.223 | 7.8741 | 5.1935 | 1.5302 | -2.2892 | 6.1873 | 6.3251 | 6.4241 | 6.4506 | 6.4414 | 6.3771 | 6.2179 | 6.071 | 5.9108 | 4.5292 | 2.423 | 1.2281
IVER 132KV GSP | CHALVEY BSP | PETERSFIELD AVENUE PRIMARY | MINIMUM HEADROOM | SU 98108 80286 | NO | YES | 13.08 | 27.8161 | 26.9487 | 26.5079 | 25.4324 | 24.6038 | 23.6824 | 22.6498 | 21.5243 | 20.4773 | 15.1079 | 12.4814 | 11.3467 | 30.1366 | 29.0621 | 28.8468 | 27.9397 | 27.3488 | 26.8591 | 26.006 | 25.1325 | 24.257 | 19.0723 | 15.9427 | 13.5417 | 28.9627 | 28.0362 | 27.677 | 26.7097 | 26.0311 | 25.1944 | 24.0933 | 22.924 | 21.775 | 16.427 | 13.7229 | 12.5995
|  | PETERSFIELD AVENUE PRIMARY | EE |  |  |  |  | 27.8161 | 27.6273 | 26.5079 | 25.4324 | 24.6038 | 23.6824 | 22.6498 | 21.5243 | 20.4773 | 15.1079 | 12.4814 | 11.3467 | 30.1366 | 30.006 | 28.8468 | 27.9397 | 27.3488 | 26.8591 | 26.006 | 25.1325 | 24.257 | 19.0723 | 15.9427 | 13.5825 | 28.9627 | 28.7505 | 27.677 | 26.7097 | 26.0311 | 25.1944 | 24.0933 | 22.924 | 21.775 | 16.427 | 13.7229 | 12.5995
|  | PETERSFIELD AVENUE PRIMARY | HT |  |  |  |  | 27.8314 | 26.9487 | 26.561 | 25.4671 | 24.7192 | 23.7671 | 23.0324 | 21.9477 | 20.9314 | 16.1896 | 14.261 | 13.7875 | 30.1386 | 29.0621 | 28.8591 | 27.9529 | 27.5203 | 26.9774 | 26.4784 | 25.6784 | 24.8825 | 21.0488 | 19.3172 | 18.6846 | 28.976 | 28.0362 | 27.7219 | 26.7362 | 26.1444 | 25.2913 | 24.5719 | 23.4923 | 22.4066 | 17.8086 | 15.8311 | 15.3709
|  | PETERSFIELD AVENUE PRIMARY | HE |  |  |  |  | 27.8365 | 27.6671 | 26.5651 | 25.4804 | 24.6355 | 23.7559 | 23.0947 | 22.2334 | 21.4273 | 17.8008 | 16.2834 | 15.7038 | 30.1397 | 30.0152 | 28.856 | 27.955 | 27.3652 | 26.8835 | 26.4488 | 25.8825 | 25.2978 | 21.7233 | 19.3703 | 17.3376 | 28.976 | 28.7862 | 27.7127 | 26.7321 | 26.0372 | 25.2546 | 24.5964 | 23.7464 | 22.8933 | 19.5352 | 18.0076 | 17.4811
|  | PETERSFIELD AVENUE PRIMARY | FB |  |  |  |  | 27.9538 | 27.8753 | 27.5957 | 25.9926 | 25.413 | 24.5406 | 24.2508 | 23.8773 | 23.5987 | 20.9824 | 18.8845 | 17.2294 | 30.1907 | 30.1172 | 29.9366 | 28.1631 | 27.6948 | 27.0305 | 26.7784 | 26.458 | 26.0182 | 22.7488 | 18.6458 | 13.5417 | 29.0821 | 29.0005 | 28.7678 | 27.1617 | 26.6627 | 25.9882 | 25.7658 | 25.4984 | 25.2791 | 22.824 | 20.6393 | 18.9127
MANNINGTON GSP | SALISBURY BSP | PETERSFINGER PRIMARY | MINIMUM HEADROOM | SU 15608 29334 | NO | NO | 8.215 | 6.1942 | 6.1922 | 6.1055 | 5.9391 | 5.7004 | 5.2942 | 4.6912 | 3.9942 | 3.4759 | 1.3116 | -0.14556 | -0.57515 | 9.9075 | 9.8351 | 9.6106 | 9.3463 | 9.0116 | 8.5534 | 8.0157 | 7.382 | 6.9187 | 5.0861 | 3.5657 | 1.0912 | 6.9973 | 6.9687 | 6.7687 | 6.5269 | 6.2065 | 5.7269 | 5.1667 | 4.5055 | 4.0238 | 2.0197 | 0.76669 | 0.50546
|  | PETERSFINGER PRIMARY | EE |  |  |  |  | 6.1942 | 6.1922 | 6.1055 | 5.9718 | 5.7708 | 5.3963 | 4.832 | 4.2136 | 3.7014 | 1.7085 | 0.16669 | -0.3925 | 9.9106 | 9.8361 | 9.6106 | 9.384 | 9.084 | 8.6453 | 8.1391 | 7.5667 | 7.0932 | 5.0861 | 3.5657 | 2.5728 | 6.9973 | 6.9687 | 6.7687 | 6.5595 | 6.2861 | 5.832 | 5.3044 | 4.7187 | 4.234 | 2.3657 | 1.0014 | 0.56158
|  | PETERSFINGER PRIMARY | HT |  |  |  |  | 6.1953 | 6.2024 | 6.134 | 5.9391 | 5.7004 | 5.2942 | 4.6912 | 3.9942 | 3.4759 | 1.3116 | -0.14556 | -0.57515 | 9.9075 | 9.8351 | 9.6534 | 9.3463 | 9.0116 | 8.5534 | 8.0157 | 7.382 | 6.9187 | 5.1136 | 4.1197 | 3.9218 | 6.9993 | 6.98 | 6.8218 | 6.5269 | 6.2065 | 5.7269 | 5.1667 | 4.5055 | 4.0238 | 2.0197 | 0.76669 | 0.50546
|  | PETERSFINGER PRIMARY | HE |  |  |  |  | 6.1963 | 6.2004 | 6.1422 | 5.982 | 5.782 | 5.4004 | 4.8391 | 4.2422 | 3.7932 | 2.1595 | 0.98097 | 0.57077 | 9.9095 | 9.8361 | 9.6606 | 9.3769 | 9.0667 | 8.6238 | 8.1146 | 7.5555 | 7.1391 | 5.3095 | 4.0126 | 3.1136 | 7.0004 | 6.9769 | 6.831 | 6.5626 | 6.28 | 5.8228 | 5.2983 | 4.731 | 4.3085 | 2.7514 | 1.7289 | 1.4351
|  | PETERSFINGER PRIMARY | FB |  |  |  |  | 6.3606 | 6.434 | 6.4493 | 6.4718 | 6.5248 | 6.3616 | 6.2248 | 6.1238 | 5.9932 | 4.7963 | 3.0483 | 2.0044 | 10.0381 | 10.0065 | 9.93 | 9.8524 | 9.8167 | 9.4157 | 9.1146 | 8.8687 | 8.5473 | 6.4891 | 3.8065 | 1.0912 | 7.1942 | 7.2514 | 7.2483 | 7.2442 | 7.2983 | 6.9993 | 6.8024 | 6.6769 | 6.4718 | 5.1014 | 3.4259 | 2.4391
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PEWSEY PRIMARY | MINIMUM HEADROOM | SU 14710 59252 | NO | NO | 0.608 | 5.6576 | 5.6871 | 5.6504 | 5.3912 | 5.0627 | 4.6994 | 4.2667 | 3.7861 | 3.3208 | 1.8004 | 0.90959 | 0.55041 | 8.4763 | 8.4569 | 8.4131 | 8.2263 | 7.9253 | 7.66 | 7.3529 | 6.9855 | 6.6345 | 5.4273 | 4.9304 | 3.761 | 6.3178 | 6.3341 | 6.3076 | 6.1229 | 5.828 | 5.5004 | 5.1198 | 4.6698 | 4.2484 | 2.8616 | 2.1749 | 1.7912
|  | PEWSEY PRIMARY | EE |  |  |  |  | 5.6576 | 5.6871 | 5.6504 | 5.4024 | 5.0943 | 4.6994 | 4.3045 | 3.8555 | 3.4218 | 1.8892 | 1.1269 | 0.79531 | 8.4763 | 8.4569 | 8.4131 | 8.2324 | 7.9569 | 7.66 | 7.3641 | 7.0253 | 6.6916 | 5.4671 | 4.9304 | 4.4988 | 6.3178 | 6.3341 | 6.3076 | 6.132 | 5.8576 | 5.5004 | 5.1382 | 4.731 | 4.3341 | 2.9412 | 2.3892 | 2.1065
|  | PEWSEY PRIMARY | HT |  |  |  |  | 5.6596 | 5.6933 | 5.6586 | 5.4076 | 5.0708 | 4.7096 | 4.2831 | 3.7892 | 3.3208 | 1.8004 | 0.90959 | 0.55041 | 8.4773 | 8.46 | 8.4131 | 8.2263 | 7.9253 | 7.6661 | 7.3529 | 6.9855 | 6.6345 | 5.4273 | 5.0876 | 5.0335 | 6.3198 | 6.3371 | 6.3116 | 6.1249 | 5.828 | 5.5035 | 5.1198 | 4.6698 | 4.2484 | 2.8616 | 2.1749 | 1.7912
|  | PEWSEY PRIMARY | HE |  |  |  |  | 5.6596 | 5.6912 | 5.6555 | 5.3912 | 5.0627 | 4.7106 | 4.2667 | 3.7861 | 3.3382 | 2.1984 | 1.329 | 1.0106 | 8.4763 | 8.4569 | 8.4141 | 8.2314 | 7.9488 | 7.7049 | 7.3743 | 7.0161 | 6.6784 | 5.7018 | 5.1151 | 4.6478 | 6.3198 | 6.3361 | 6.3096 | 6.1229 | 5.8382 | 5.528 | 5.128 | 4.6912 | 4.2851 | 3.2127 | 2.5678 | 2.279
|  | PEWSEY PRIMARY | FB |  |  |  |  | 5.7565 | 5.8402 | 5.8943 | 5.8973 | 5.8555 | 5.7963 | 5.8371 | 5.5341 | 5.3841 | 4.2361 | 3.1147 | 2.4453 | 8.5488 | 8.5488 | 8.5488 | 8.5345 | 8.4937 | 8.408 | 8.3651 | 8.06 | 7.8835 | 6.6702 | 5.2539 | 3.761 | 6.4269 | 6.4759 | 6.5106 | 6.5239 | 6.5045 | 6.4892 | 6.4627 | 6.2208 | 6.0647 | 4.9484 | 3.8963 | 3.278
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE PRIMARY | MINIMUM HEADROOM | SY 70169 99809 | NO | NO | 0.592 | 3.9459 | 3.9306 | 3.8969 | 3.798 | 3.6102 | 3.4133 | 3.201 | 3 | 2.8745 | 2.1847 | 1.5561 | 1.25 | 6.0464 | 6.0189 | 5.9903 | 5.7883 | 5.573 | 5.4077 | 5.2209 | 5.0403 | 4.9811 | 4.3719 | 3.9781 | 3.9321 | 3.651 | 3.6418 | 3.6112 | 3.498 | 3.4082 | 3.2633 | 3.1469 | 3.0163 | 2.9 | 2.4469 | 1.9296 | 1.7857
|  | PIDDLETRENTHIDE PRIMARY | EE |  |  |  |  | 3.9459 | 3.9306 | 3.8969 | 3.8082 | 3.6541 | 3.4469 | 3.2582 | 3.0929 | 2.9439 | 2.2796 | 1.7357 | 1.6245 | 6.0464 | 6.0219 | 5.9985 | 5.8015 | 5.6291 | 5.4291 | 5.2587 | 5.1168 | 5.0015 | 4.4138 | 3.9934 | 4.0291 | 3.651 | 3.6418 | 3.6112 | 3.501 | 3.4204 | 3.2857 | 3.1694 | 3.0592 | 2.951 | 2.5163 | 2.0378 | 2.0582
|  | PIDDLETRENTHIDE PRIMARY | HT |  |  |  |  | 3.948 | 3.9316 | 3.9 | 3.798 | 3.6102 | 3.4133 | 3.201 | 3 | 2.8847 | 2.1847 | 1.5561 | 1.25 | 6.0464 | 6.0189 | 5.9903 | 5.7883 | 5.573 | 5.4077 | 5.2209 | 5.0403 | 4.9811 | 4.3719 | 3.9781 | 3.9321 | 3.652 | 3.6439 | 3.6173 | 3.5041 | 3.4082 | 3.2867 | 3.1592 | 3.0357 | 2.952 | 2.4469 | 1.9296 | 1.7857
|  | PIDDLETRENTHIDE PRIMARY | HE |  |  |  |  | 3.9469 | 3.9327 | 3.902 | 3.8051 | 3.6449 | 3.4163 | 3.2327 | 3.0296 | 2.8745 | 2.4643 | 2.0602 | 1.8551 | 6.0485 | 6.023 | 5.9985 | 5.8015 | 5.626 | 5.4219 | 5.2893 | 5.1199 | 5.0087 | 4.5964 | 4.3842 | 4.2832 | 3.652 | 3.6439 | 3.6143 | 3.498 | 3.4133 | 3.2633 | 3.1469 | 3.0163 | 2.9 | 2.6704 | 2.4082 | 2.2684
|  | PIDDLETRENTHIDE PRIMARY | FB |  |  |  |  | 3.9816 | 3.9939 | 3.9949 | 3.9816 | 3.9694 | 3.9531 | 3.9296 | 3.8092 | 3.7367 | 3.349 | 2.8806 | 2.5082 | 6.073 | 6.077 | 6.0709 | 6.0515 | 6.0362 | 5.9964 | 5.9597 | 5.675 | 5.5811 | 5.1464 | 4.6566 | 4.1668 | 3.6786 | 3.6898 | 3.6939 | 3.6806 | 3.6643 | 3.6429 | 3.6204 | 3.5061 | 3.4592 | 3.2265 | 2.9724 | 2.6571
FLEET-BRAMLEY GSP | FERNHURST BSP | PLAISTOW PRIMARY | MINIMUM HEADROOM | TQ 02071 29626 | NO | NO | 15.447 | -2.7811 | 11.3939 | 11.3439 | 11.2102 | 10.8898 | 10.552 | 10.1663 | 9.7449 | 9.3786 | 7.798 | 6.7878 | 6.1643 | -2.6143 | 10.7235 | 10.6776 | 10.6153 | 10.3878 | 10.1714 | 9.8959 | 9.6102 | 9.398 | 8.4286 | 8.0306 | 7.9276 | -2.248 | 11.5347 | 11.4653 | 11.3755 | 11.0265 | 10.7469 | 10.4143 | 10.0592 | 9.7694 | 8.498 | 7.8306 | 7.5643
|  | PLAISTOW PRIMARY | EE |  |  |  |  | -2.7811 | 11.4112 | 11.399 | 11.3306 | 11.1214 | 10.849 | 10.5337 | 10.1673 | 9.848 | 8.2418 | 7.3949 | 6.9316 | -2.6133 | 10.7327 | 10.7031 | 10.6643 | 10.5082 | 10.3112 | 10.0765 | 9.802 | 9.5806 | 8.5867 | 8.1255 | 7.9276 | -2.248 | 11.5469 | 11.5051 | 11.451 | 11.1969 | 10.9582 | 10.6776 | 10.3551 | 10.0827 | 8.8092 | 8.2102 | 7.9714
|  | PLAISTOW PRIMARY | HT |  |  |  |  | -2.7801 | 11.3939 | 11.3439 | 11.2102 | 10.8898 | 10.552 | 10.1663 | 9.7449 | 9.3786 | 7.798 | 6.7878 | 6.1643 | -2.6143 | 10.7235 | 10.6776 | 10.6153 | 10.3878 | 10.1714 | 9.8959 | 9.6102 | 9.398 | 8.4286 | 8.0306 | 7.9857 | -2.2469 | 11.5347 | 11.4653 | 11.3755 | 11.0265 | 10.7469 | 10.4143 | 10.0592 | 9.7694 | 8.498 | 7.8306 | 7.5643
|  | PLAISTOW PRIMARY | HE |  |  |  |  | -2.776 | 11.4163 | 11.4051 | 11.3173 | 11.0878 | 10.7867 | 10.4449 | 10.101 | 9.7429 | 8.5102 | 7.7724 | 7.3694 | -2.6112 | 10.7306 | 10.702 | 10.6622 | 10.501 | 10.298 | 10.0571 | 9.8316 | 9.5878 | 8.7745 | 8.4888 | 8.301 | -2.2449 | 11.55 | 11.5061 | 11.4459 | 11.1796 | 10.9255 | 10.6296 | 10.3459 | 10.0408 | 9.0439 | 8.6082 | 8.3929
|  | PLAISTOW PRIMARY | FB |  |  |  |  | -2.6597 | 11.5663 | 11.6122 | 11.6112 | 11.6357 | 11.6031 | 11.5735 | 11.5837 | 11.5224 | 10.1724 | 9.3949 | 8.9031 | -2.5265 | 10.8265 | 10.8327 | 10.8194 | 10.8082 | 10.7531 | 10.6969 | 10.6857 | 10.6071 | 9.5429 | 8.7296 | 7.9888 | -2.1408 | 11.6837 | 11.702 | 11.6857 | 11.6755 | 11.6327 | 11.599 | 11.6184 | 11.549 | 10.3296 | 9.6388 | 9.1939
MINETY GSP | STRATTON (MAIN) BSP | PLESSEY PRIMARY | MINIMUM HEADROOM | SU 16381 86720 | NO | NO | 2.58 | 7.5713 | 7.4703 | 7.355 | 7.1642 | 6.6907 | 5.9877 | 5.0846 | 4.1458 | 3.2887 | 0.57541 | -1.594 | -3.0991 | 8.1121 | 7.9744 | 7.853 | 7.753 | 7.2754 | 6.654 | 5.8734 | 5.0377 | 4.1407 | 1.2223 | -0.73786 | -3.8317 | 6.8499 | 6.8111 | 6.7693 | 6.753 | 6.3581 | 5.753 | 4.9642 | 4.1172 | 3.3172 | 0.32337 | -1.7134 | -2.9756
|  | PLESSEY PRIMARY | EE |  |  |  |  | 7.5713 | 7.5887 | 7.355 | 7.1642 | 6.8744 | 6.2877 | 5.5489 | 4.6662 | 3.8162 | 0.59173 | -1.594 | -3.0991 | 8.1121 | 8.0938 | 7.853 | 7.753 | 7.4581 | 6.9223 | 6.2897 | 5.5019 | 4.5856 | 1.2223 | -0.73786 | -2.4909 | 6.8499 | 6.9285 | 6.7693 | 6.753 | 6.554 | 6.054 | 5.4172 | 4.6223 | 3.7652 | 0.32337 | -1.7134 | -2.9756
|  | PLESSEY PRIMARY | HT |  |  |  |  | 7.5785 | 7.4703 | 7.3979 | 7.1989 | 6.6907 | 5.9877 | 5.0846 | 4.1458 | 3.2887 | 0.57541 | -1.4726 | -2.6368 | 8.1162 | 7.9744 | 7.8581 | 7.7611 | 7.2754 | 6.654 | 5.8734 | 5.0377 | 4.1407 | 1.7754 | 0.4448 | -0.36847 | 6.8591 | 6.8111 | 6.7968 | 6.7754 | 6.3581 | 5.753 | 4.9642 | 4.1172 | 3.3172 | 0.51418 | -1.3256 | -2.3501
|  | PLESSEY PRIMARY | HE |  |  |  |  | 7.5754 | 7.6111 | 7.3907 | 7.1968 | 6.907 | 6.3621 | 5.656 | 4.7938 | 3.9693 | 1.5152 | 0.097857 | -0.82969 | 8.1162 | 8.0958 | 7.857 | 7.756 | 7.4601 | 6.9326 | 6.2968 | 5.5019 | 4.5713 | 2.1468 | 0.62541 | -0.89704 | 6.8581 | 6.9428 | 6.7928 | 6.7744 | 6.5683 | 6.0948 | 5.4754 | 4.6897 | 3.8274 | 1.5856 | 0.27949 | -0.61439
|  | PLESSEY PRIMARY | FB |  |  |  |  | 7.6703 | 7.7152 | 7.6907 | 7.507 | 7.4366 | 7.3285 | 7.0805 | 6.753 | 6.3897 | 4.1111 | 2.5683 | 1.2274 | 8.1785 | 8.1142 | 8.0244 | 7.7979 | 7.6652 | 7.4377 | 7.1121 | 6.704 | 6.2366 | 3.2019 | 0.10398 | -3.8317 | 6.9877 | 7.0774 | 7.1346 | 7.0326 | 7.054 | 7.0203 | 6.8632 | 6.606 | 6.2989 | 4.2611 | 2.4019 | 0.41418
LOVEDEAN GSP | FAREHAM (MAIN) BSP | PLESSEY TITCHFIELD PRIMARY | MINIMUM HEADROOM | SU 53390 06922 | NO | YES | 5.524 | 18.2439 | 18.1102 | 18.0051 | 17.8102 | 17.55 | 17.0612 | 16.5612 | 16.0449 | 15.3224 | 12.7051 | 10.9275 | 10.2469 | 19.1603 | 18.9786 | 18.7858 | 18.598 | 18.3103 | 17.9296 | 17.5307 | 17.1001 | 16.7001 | 15.2133 | 13.4643 | 10.4521 | 18.7154 | 18.5582 | 18.4143 | 18.247 | 18.0092 | 17.6409 | 17.1899 | 16.6939 | 16.2266 | 14.396 | 13.1225 | 12.7664
|  | PLESSEY TITCHFIELD PRIMARY | EE |  |  |  |  | 18.253 | 18.2336 | 18.1051 | 17.8755 | 17.6592 | 17.1714 | 16.6285 | 16.0826 | 15.3663 | 12.9459 | 11.2704 | 10.403 | 19.1694 | 19.1021 | 18.898 | 18.6654 | 18.446 | 18.1205 | 17.7317 | 17.3194 | 16.9388 | 15.2133 | 13.8745 | 12.7256 | 18.7235 | 18.6899 | 18.5143 | 18.3164 | 18.1235 | 17.7694 | 17.2552 | 16.7388 | 16.2521 | 14.6021 | 13.3633 | 12.8072
|  | PLESSEY TITCHFIELD PRIMARY | HT |  |  |  |  | 18.2439 | 18.1102 | 18.0051 | 17.8102 | 17.55 | 17.0612 | 16.5612 | 16.0449 | 15.349 | 12.7051 | 10.9275 | 10.2469 | 19.1603 | 18.9786 | 18.7858 | 18.598 | 18.3103 | 17.9296 | 17.5307 | 17.1001 | 16.7001 | 15.3266 | 14.5439 | 14.3021 | 18.7154 | 18.5582 | 18.4143 | 18.247 | 18.0092 | 17.6409 | 17.1899 | 16.6939 | 16.2266 | 14.396 | 13.1225 | 12.7664
|  | PLESSEY TITCHFIELD PRIMARY | HE |  |  |  |  | 18.252 | 18.2316 | 18.103 | 17.8418 | 17.5908 | 17.1245 | 16.6061 | 16.0755 | 15.3224 | 13.3347 | 11.9622 | 11.5285 | 19.1664 | 19.097 | 18.8888 | 18.6552 | 18.4286 | 18.099 | 17.7215 | 17.3113 | 16.8888 | 15.299 | 14.0837 | 12.9541 | 18.7235 | 18.6919 | 18.5174 | 18.296 | 18.0807 | 17.7368 | 17.245 | 16.7409 | 16.2429 | 14.8837 | 13.8848 | 13.6429
|  | PLESSEY TITCHFIELD PRIMARY | FB |  |  |  |  | 18.3755 | 18.4296 | 18.4704 | 18.3704 | 18.3275 | 18.2316 | 18.1367 | 18.0398 | 17.9204 | 17.1306 | 15.9888 | 15.1581 | 19.2592 | 19.2184 | 19.1603 | 19.0011 | 18.898 | 18.5919 | 18.3337 | 18.0919 | 17.7899 | 16.0011 | 13.4643 | 10.4521 | 18.8266 | 18.8552 | 18.8725 | 18.7378 | 18.6684 | 18.5776 | 18.4848 | 18.3899 | 18.2694 | 17.3786 | 16.3664 | 15.8521
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | POOLE PRIMARY | MINIMUM HEADROOM | SZ 01091 90595 | NO | NO | 2.949 | 10.8293 | 22.5201 | 22.3916 | 22.0048 | 21.6283 | 21.3722 | 21.114 | 20.8212 | 20.5191 | 18.7905 | 17.7701 | 17.1773 | 13.7436 | 23.2691 | 23.1916 | 23.0058 | 22.7283 | 22.4732 | 22.213 | 21.9518 | 21.7446 | 19.6293 | 16.7007 | 12.7324 | 12.6916 | 23.3895 | 23.2803 | 22.9722 | 22.6803 | 22.4691 | 22.2569 | 22.0099 | 21.7558 | 20.3099 | 19.4232 | 18.9436
|  | POOLE PRIMARY | EE |  |  |  |  | 10.8293 | 22.5201 | 22.4007 | 22.0099 | 21.6283 | 21.4007 | 21.1844 | 20.9467 | 20.6916 | 19.0324 | 17.7701 | 17.1773 | 13.7446 | 23.2701 | 23.2069 | 23.0303 | 22.8069 | 22.6324 | 22.4375 | 22.2109 | 21.9324 | 19.9987 | 18.462 | 16.8028 | 12.6916 | 23.3895 | 23.2865 | 22.9875 | 22.6824 | 22.5109 | 22.3334 | 22.1344 | 21.9191 | 20.4691 | 19.4232 | 18.9436
|  | POOLE PRIMARY | HT |  |  |  |  | 10.8334 | 22.5201 | 22.3916 | 22.0048 | 21.6446 | 21.3722 | 21.114 | 20.8212 | 20.5191 | 18.7905 | 17.9242 | 17.6232 | 13.7436 | 23.2691 | 23.1916 | 23.0058 | 22.7967 | 22.6099 | 22.3946 | 22.1385 | 21.8446 | 20.6058 | 19.965 | 19.5946 | 12.6967 | 23.3895 | 23.2803 | 22.9722 | 22.6803 | 22.4691 | 22.2569 | 22.0099 | 21.7558 | 20.3099 | 19.5732 | 19.2191
|  | POOLE PRIMARY | HE |  |  |  |  | 10.8324 | 22.5252 | 22.3956 | 22.0109 | 21.6385 | 21.4212 | 21.2109 | 20.9742 | 20.7242 | 19.3089 | 18.7742 | 18.4895 | 13.7446 | 23.2752 | 23.2018 | 23.0252 | 22.8334 | 22.6865 | 22.4905 | 22.2579 | 21.9834 | 20.2946 | 18.865 | 17.3038 | 12.6926 | 23.3946 | 23.2834 | 22.9844 | 22.6844 | 22.5222 | 22.3497 | 22.1477 | 21.9334 | 20.7324 | 20.264 | 19.9926
|  | POOLE PRIMARY | FB |  |  |  |  | 10.9538 | 22.6742 | 22.5926 | 22.3048 | 22.0354 | 21.8977 | 21.7977 | 21.6905 | 21.6181 | 20.4201 | 19.7467 | 18.9875 | 13.8405 | 23.3609 | 23.2895 | 23.0273 | 22.7283 | 22.4732 | 22.213 | 21.9518 | 21.7446 | 19.6293 | 16.7007 | 12.7324 | 12.813 | 23.5293 | 23.4579 | 23.2314 | 23.013 | 22.9038 | 22.8181 | 22.7242 | 22.6671 | 21.6314 | 21.0007 | 20.2385
LOVEDEAN GSP | PORTSMOUTH BSP | PORTCHESTER PRIMARY | MINIMUM HEADROOM | SU 62043 05575 | NO | YES | 3.637 | 13.7625 | 13.784 | 13.4829 | 12.9799 | 12.3513 | 11.2391 | 9.8493 | 8.3809 | 6.9615 | 2.4533 | -0.28441 | -1.666 | 13.9574 | 13.8982 | 13.636 | 13.1748 | 12.6625 | 11.9789 | 11.1125 | 10.1676 | 9.2595 | 6.1656 | 3.0411 | -2.8711 | 13.836 | 13.8299 | 13.5503 | 13.0268 | 12.4238 | 11.5411 | 10.4329 | 9.2442 | 8.1023 | 4.5309 | 2.5748 | 1.8064
|  | PORTCHESTER PRIMARY | EE |  |  |  |  | 13.7768 | 13.9176 | 13.6758 | 13.2676 | 12.7493 | 11.736 | 10.6084 | 9.1411 | 7.6554 | 2.9574 | 0.28191 | -1.1099 | 13.9646 | 13.9595 | 13.735 | 13.3319 | 12.8778 | 12.288 | 11.5768 | 10.6972 | 9.7972 | 6.1656 | 3.7186 | 1.5115 | 13.8472 | 13.9125 | 13.6942 | 13.2472 | 12.734 | 11.9503 | 11.0513 | 9.9033 | 8.7227 | 4.9125 | 2.8299 | 1.8697
|  | PORTCHESTER PRIMARY | HT |  |  |  |  | 13.7625 | 13.784 | 13.4829 | 12.9799 | 12.3513 | 11.2391 | 9.8493 | 8.3809 | 6.9615 | 2.4533 | -0.28441 | -1.666 | 13.9574 | 13.8982 | 13.636 | 13.1748 | 12.6625 | 11.9789 | 11.1125 | 10.1676 | 9.2595 | 6.5615 | 5.2227 | 4.7095 | 13.836 | 13.8299 | 13.5503 | 13.0268 | 12.4238 | 11.5411 | 10.4329 | 9.2442 | 8.1023 | 4.5309 | 2.5748 | 1.8064
|  | PORTCHESTER PRIMARY | HE |  |  |  |  | 13.784 | 13.9207 | 13.6809 | 13.2789 | 12.8084 | 11.7707 | 10.638 | 9.286 | 8.034 | 4.2686 | 1.6727 | 0.62477 | 13.9676 | 13.9584 | 13.737 | 13.3319 | 12.9289 | 12.3238 | 11.6238 | 10.7686 | 10.0156 | 6.738 | 4.3238 | 2.0452 | 13.8533 | 13.9176 | 13.7013 | 13.2625 | 12.7952 | 11.9931 | 11.0982 | 10.0176 | 9.037 | 5.938 | 4.0013 | 3.2411
|  | PORTCHESTER PRIMARY | FB |  |  |  |  | 14.0595 | 14.2248 | 14.3574 | 14.3329 | 14.2676 | 14.0952 | 13.7595 | 13.4952 | 13.0482 | 10.284 | 7.4044 | 5.9564 | 14.1299 | 14.0768 | 14.036 | 13.8717 | 13.6289 | 13.2493 | 12.6258 | 12.1646 | 11.588 | 7.9564 | 3.0411 | -2.8711 | 14.138 | 14.2329 | 14.3309 | 14.286 | 14.2064 | 14.0329 | 13.5972 | 13.3248 | 12.9217 | 10.4544 | 7.8748 | 6.4574
CHICKERELL GSP | CHICKERELL BSP | PORTLAND PRIMARY | MINIMUM HEADROOM | SY 68307 73941 | NO | NO | 3.879 | 6.6268 | 6.486 | 6.2789 | 5.8789 | 5.3136 | 4.485 | 3.5166 | 2.3983 | 1.5309 | -2.464 | -5.9405 | -8.0864 | 8.9697 | 8.7564 | 8.5432 | 8.1911 | 7.6901 | 7.1605 | 6.4564 | 5.5656 | 4.9871 | 2.1666 | -0.27519 | -2.9885 | 7.7452 | 7.5932 | 7.4258 | 7.1034 | 6.6248 | 5.983 | 5.1932 | 4.2544 | 3.5626 | 0.22583 | -2.5793 | -4.0609
|  | PORTLAND PRIMARY | EE |  |  |  |  | 6.6391 | 6.5279 | 6.3717 | 6.0411 | 5.5401 | 4.7666 | 3.8626 | 2.8064 | 2.0064 | -1.764 | -5.2527 | -7.4405 | 8.9768 | 8.785 | 8.6075 | 8.3085 | 7.8452 | 7.383 | 6.7564 | 5.933 | 5.4258 | 2.3146 | -0.27519 | -2.2558 | 7.7544 | 7.6238 | 7.4962 | 7.2289 | 6.7973 | 6.2003 | 5.4697 | 4.582 | 3.9493 | 0.71767 | -2.118 | -3.8262
|  | PORTLAND PRIMARY | HT |  |  |  |  | 6.6268 | 6.486 | 6.2789 | 5.8789 | 5.3136 | 4.485 | 3.5166 | 2.3983 | 1.5309 | -2.464 | -5.9405 | -8.0864 | 8.9697 | 8.7564 | 8.5432 | 8.1911 | 7.6901 | 7.1605 | 6.4564 | 5.5656 | 4.9871 | 2.1666 | 0.12583 | -0.67315 | 7.7452 | 7.5932 | 7.4258 | 7.1034 | 6.6248 | 5.983 | 5.1932 | 4.2544 | 3.5626 | 0.22583 | -2.5793 | -4.0609
|  | PORTLAND PRIMARY | HE |  |  |  |  | 6.6401 | 6.5289 | 6.3717 | 6.0238 | 5.4983 | 4.7677 | 3.884 | 2.8432 | 2.0656 | -0.86601 | -3.1334 | -4.5436 | 8.9768 | 8.785 | 8.6075 | 8.3085 | 7.834 | 7.3901 | 6.7564 | 5.9289 | 5.4217 | 2.8391 | 1.2105 | -0.43948 | 7.7554 | 7.6238 | 7.4962 | 7.2187 | 6.7687 | 6.2064 | 5.484 | 4.6075 | 3.9871 | 1.4697 | -0.30682 | -1.418
|  | PORTLAND PRIMARY | FB |  |  |  |  | 6.8024 | 6.7799 | 6.7483 | 6.6799 | 6.5309 | 6.4289 | 6.1585 | 5.9075 | 5.5554 | 3.6524 | 1.2146 | -0.82417 | 9.083 | 8.9422 | 8.8075 | 8.6656 | 8.4166 | 8.2401 | 7.8809 | 7.5513 | 7.0962 | 4.5115 | 1.1054 | -2.9885 | 7.9126 | 7.8728 | 7.8228 | 7.7697 | 7.6299 | 7.5564 | 7.3095 | 7.084 | 6.7534 | 4.9891 | 2.7717 | 0.8146
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH PRIMARY | MINIMUM HEADROOM | SZ 63405 99685 | NO | YES | 3.73 | 24.6303 | 24.7068 | 24.418 | 24.0915 | 23.7405 | 23.617 | 23.5476 | 23.3537 | 23.1782 | 21.9639 | 20.6905 | 20.1496 | 27.7323 | 27.7578 | 27.6496 | 27.4466 | 27.1782 | 26.9843 | 26.8078 | 26.4047 | 26.1231 | 24.4384 | 21.2435 | 16.5609 | 25.3578 | 25.3874 | 25.1619 | 24.8721 | 24.568 | 24.4027 | 24.3384 | 24.1292 | 23.9425 | 22.769 | 21.5476 | 21.0894
|  | PORTSMOUTH PRIMARY | EE |  |  |  |  | 24.6303 | 24.7068 | 24.418 | 24.0915 | 23.7405 | 23.6221 | 23.5578 | 23.3803 | 23.219 | 22.0231 | 20.6905 | 20.1496 | 27.7323 | 27.7578 | 27.6547 | 27.4619 | 27.1986 | 27.0262 | 26.9129 | 26.6772 | 26.4639 | 24.7864 | 22.915 | 20.9823 | 25.3578 | 25.3884 | 25.1619 | 24.8721 | 24.568 | 24.4241 | 24.3456 | 24.1405 | 23.9598 | 22.769 | 21.5476 | 21.0894
|  | PORTSMOUTH PRIMARY | HT |  |  |  |  | 24.6415 | 24.7241 | 24.4435 | 24.1078 | 23.7609 | 23.617 | 23.5476 | 23.3537 | 23.1782 | 21.9639 | 20.8762 | 20.5976 | 27.7343 | 27.7578 | 27.6496 | 27.4466 | 27.1782 | 26.9843 | 26.8833 | 26.6456 | 26.4292 | 25.5323 | 24.6701 | 24.1986 | 25.366 | 25.3996 | 25.1843 | 24.8813 | 24.5741 | 24.4027 | 24.3384 | 24.1292 | 23.9425 | 22.8517 | 21.9262 | 21.768
|  | PORTSMOUTH PRIMARY | HE |  |  |  |  | 24.6405 | 24.7201 | 24.4507 | 24.1323 | 23.7813 | 23.7098 | 23.6364 | 23.4884 | 23.3221 | 22.7078 | 22.115 | 21.7364 | 27.7343 | 27.7598 | 27.6558 | 27.4823 | 27.217 | 27.0813 | 26.9445 | 26.7252 | 26.4854 | 25.1088 | 23.6262 | 21.7721 | 25.3578 | 25.3874 | 25.1915 | 24.9068 | 24.5986 | 24.5058 | 24.4129 | 24.2374 | 24.0333 | 23.4568 | 22.9598 | 22.6721
|  | PORTSMOUTH PRIMARY | FB |  |  |  |  | 24.6864 | 24.7976 | 24.6343 | 24.4476 | 24.2537 | 24.2609 | 24.2354 | 24.1466 | 24.1068 | 23.8833 | 22.9843 | 22.169 | 27.7486 | 27.7833 | 27.6894 | 27.4792 | 27.2292 | 27.0374 | 26.8078 | 26.4047 | 26.1231 | 24.4384 | 21.2435 | 16.5609 | 25.4007 | 25.4609 | 25.3466 | 25.1956 | 25.0394 | 25.0435 | 25.0272 | 24.9303 | 24.8609 | 24.5496 | 23.6201 | 22.8272
MELKSHAM GSP | ANDOVER BSP | PORTWAY PRIMARY | MINIMUM HEADROOM | SU 34402 46001 | NO | NO | 2.754 | 11.7345 | 11.6559 | 11.5814 | 11.4385 | 11.2263 | 10.8263 | 10.3804 | 9.9498 | 9.513 | 7.7967 | 6.3508 | 5.6334 | 13.3487 | 13.26 | 13.1875 | 13.0814 | 12.9406 | 12.7283 | 12.4702 | 12.2334 | 12.014 | 10.313 | 9.2253 | 7.9681 | 12.7171 | 12.6242 | 12.5396 | 12.4079 | 12.2232 | 11.9161 | 11.5681 | 11.2324 | 10.8957 | 9.1079 | 7.6345 | 6.9477
|  | PORTWAY PRIMARY | EE |  |  |  |  | 11.7355 | 11.6589 | 11.5814 | 11.461 | 11.26 | 10.8549 | 10.3916 | 9.9498 | 9.513 | 7.7967 | 6.513 | 5.7304 | 13.3538 | 13.2712 | 13.2028 | 13.1069 | 12.963 | 12.762 | 12.5049 | 12.2834 | 12.0589 | 10.313 | 9.2253 | 8.4722 | 12.7171 | 12.6242 | 12.5396 | 12.4222 | 12.2416 | 11.9355 | 11.5742 | 11.2324 | 10.8957 | 9.1079 | 7.7487 | 6.9477
|  | PORTWAY PRIMARY | HT |  |  |  |  | 11.7385 | 11.6661 | 11.5957 | 11.4763 | 11.2834 | 10.8814 | 10.4375 | 10.0202 | 9.612 | 7.8702 | 6.3508 | 5.6334 | 13.3538 | 13.2712 | 13.2038 | 13.1069 | 12.9681 | 12.761 | 12.5018 | 12.2691 | 12.0518 | 10.4977 | 9.3222 | 9.4283 | 12.7191 | 12.6324 | 12.5538 | 12.4324 | 12.2549 | 11.9457 | 11.5936 | 11.2651 | 10.9406 | 9.2385 | 7.6345 | 7.4283
|  | PORTWAY PRIMARY | HE |  |  |  |  | 11.7345 | 11.6559 | 11.5814 | 11.4385 | 11.2263 | 10.8263 | 10.3804 | 9.9538 | 9.5242 | 8.1028 | 7.0079 | 6.3416 | 13.3487 | 13.26 | 13.1875 | 13.0814 | 12.9406 | 12.7283 | 12.4702 | 12.2334 | 12.014 | 10.7242 | 10.0436 | 9.36 | 12.7171 | 12.6263 | 12.5447 | 12.4079 | 12.2232 | 11.9161 | 11.5681 | 11.2365 | 10.9018 | 9.6294 | 8.7579 | 8.1202
|  | PORTWAY PRIMARY | FB |  |  |  |  | 11.8171 | 11.764 | 11.7416 | 11.7151 | 11.6753 | 11.5926 | 11.514 | 11.4079 | 11.2559 | 10.3314 | 9.2957 | 8.4896 | 13.4171 | 13.3314 | 13.2947 | 13.2855 | 13.2385 | 13.1691 | 13.1059 | 13.0324 | 12.9079 | 12.0171 | 10.3161 | 7.9681 | 12.7998 | 12.7222 | 12.6865 | 12.6661 | 12.6028 | 12.5365 | 12.46 | 12.3702 | 12.2334 | 11.412 | 10.514 | 9.11
IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY | MINIMUM HEADROOM | TQ 03425 75555 | NO | YES | 7.932 | 6.7724 | 6.5418 | 6.4929 | 6.4051 | 6.2031 | 5.9571 | 5.6439 | 5.3143 | 5.0245 | 0.35714 | -0.76429 | -0.95 | 7.552 | 7.2561 | 7.2133 | 7.1837 | 7.0439 | 6.8745 | 6.5969 | 6.301 | 5.8531 | 0.79592 | -1.1265 | -2.8765 | 6.5173 | 6.2541 | 6.2051 | 6.1286 | 5.9418 | 5.7255 | 5.4255 | 5.1245 | 4.8704 | -0.77755 | -2.2867 | -2.4449
|  | POYLE PRIMARY | EE |  |  |  |  | 6.7724 | 6.5418 | 6.4929 | 6.4122 | 6.2286 | 6.0031 | 5.6908 | 5.3704 | 5.1061 | 0.94694 | -0.76429 | -0.95 | 7.5531 | 7.2561 | 7.2184 | 7.1929 | 7.0633 | 6.8908 | 6.6286 | 6.3439 | 5.9459 | 1.0398 | -1.1265 | -1.9071 | 6.5173 | 6.2541 | 6.2051 | 6.1357 | 5.9704 | 5.7582 | 5.4704 | 5.1827 | 4.9561 | -0.30918 | -2.2867 | -2.4449
|  | POYLE PRIMARY | HT |  |  |  |  | 6.7735 | 6.55 | 6.501 | 6.4051 | 6.2031 | 5.9571 | 5.6439 | 5.3143 | 5.0245 | 0.35714 | -0.59898 | -0.78163 | 7.552 | 7.2561 | 7.2143 | 7.1837 | 7.0439 | 6.8745 | 6.5969 | 6.301 | 5.8531 | 0.79592 | -0.37347 | -0.54694 | 6.5214 | 6.2643 | 6.2122 | 6.1286 | 5.9418 | 5.7255 | 5.4255 | 5.1245 | 4.8704 | -0.77755 | -2.1071 | -2.251
|  | POYLE PRIMARY | HE |  |  |  |  | 6.7724 | 6.548 | 6.5031 | 6.4173 | 6.2265 | 6.002 | 5.7031 | 5.401 | 5.1357 | 1.2765 | 0.31224 | 0.11327 | 7.552 | 7.2561 | 7.2133 | 7.1918 | 7.0622 | 6.901 | 6.6337 | 6.3582 | 5.9643 | 1.4133 | 0.12959 | -0.80408 | 6.5214 | 6.2612 | 6.2153 | 6.1398 | 5.9663 | 5.7714 | 5.4796 | 5.2071 | 4.9765 | 0.42653 | -0.7398 | -0.9102
|  | POYLE PRIMARY | FB |  |  |  |  | 6.8806 | 6.7071 | 6.7612 | 6.7071 | 6.6592 | 6.5857 | 6.5102 | 6.4112 | 6.3194 | 5.6857 | 1.5224 | 0.96429 | 7.6122 | 7.3429 | 7.348 | 7.2857 | 7.2163 | 7.1255 | 7.0398 | 6.9214 | 6.7969 | 5.8092 | -0.24082 | -2.8765 | 6.6327 | 6.4276 | 6.4633 | 6.402 | 6.3582 | 6.2908 | 6.2245 | 6.1316 | 6.0439 | 5.4449 | 0.84898 | -0.19286
MINETY GSP | STRATTON (MAIN) BSP | PRESSED STEEL SWINDON PRIMARY | MINIMUM HEADROOM | SU 16963 86368 | NO | NO | 7.537 | 30.4422 | 62.9468 | 62.8815 | 62.6529 | 62.3345 | 61.7376 | 60.9315 | 60.11 | 59.3713 | 57.1488 | 55.6998 | 54.9907 | 33.0933 | 62.3121 | 62.2131 | 62.0998 | 61.8192 | 61.4223 | 60.8182 | 60.1876 | 59.658 | 58.1611 | 56.3886 | 53.606 | 31.5817 | 62.0723 | 61.9835 | 61.7315 | 61.3702 | 60.7784 | 60.0039 | 59.2141 | 58.4866 | 56.4509 | 55.208 | 54.6713
|  | PRESSED STEEL SWINDON PRIMARY | EE |  |  |  |  | 30.4422 | 63.1325 | 62.9549 | 62.6529 | 62.4304 | 61.9009 | 61.2386 | 60.457 | 59.7366 | 57.1488 | 55.6998 | 54.9907 | 33.0933 | 62.5519 | 62.3039 | 62.1009 | 61.9641 | 61.6794 | 61.2345 | 60.6804 | 60.1815 | 58.1611 | 56.8958 | 55.7723 | 31.5817 | 62.2672 | 62.0509 | 61.7315 | 61.4672 | 60.9284 | 60.309 | 59.5611 | 58.8774 | 56.4509 | 55.208 | 54.6713
|  | PRESSED STEEL SWINDON PRIMARY | HT |  |  |  |  | 30.4493 | 62.9468 | 62.8815 | 62.6692 | 62.3345 | 61.7376 | 60.9315 | 60.11 | 59.3713 | 57.3549 | 55.9662 | 55.3733 | 33.0953 | 62.3121 | 62.2131 | 62.1019 | 61.8192 | 61.4223 | 60.8182 | 60.1876 | 59.658 | 58.6274 | 57.9427 | 57.6978 | 31.5858 | 62.0723 | 61.9835 | 61.7427 | 61.3702 | 60.7784 | 60.0039 | 59.2141 | 58.4866 | 56.6039 | 55.3988 | 54.9988
|  | PRESSED STEEL SWINDON PRIMARY | HE |  |  |  |  | 30.4483 | 63.1427 | 62.9733 | 62.6723 | 62.4549 | 61.9856 | 61.3458 | 60.5713 | 59.8825 | 57.657 | 56.5274 | 55.9233 | 33.0943 | 62.5509 | 62.3049 | 62.0998 | 61.9651 | 61.6886 | 61.2325 | 60.659 | 60.1468 | 58.3274 | 57.1927 | 56.0947 | 31.5878 | 62.2774 | 62.0682 | 61.7468 | 61.4774 | 61.0049 | 60.3866 | 59.6233 | 58.958 | 56.8845 | 55.9682 | 55.56
|  | PRESSED STEEL SWINDON PRIMARY | FB |  |  |  |  | 30.6197 | 63.3713 | 63.3866 | 63.1856 | 63.0723 | 63.0539 | 62.8927 | 62.556 | 62.2866 | 60.4141 | 59.106 | 58.2213 | 33.1719 | 62.6549 | 62.6437 | 62.3733 | 62.2315 | 62.1223 | 61.8743 | 61.4784 | 61.1029 | 58.6345 | 56.3886 | 53.606 | 31.7725 | 62.5213 | 62.506 | 62.2651 | 62.1437 | 62.1182 | 61.9509 | 61.5417 | 61.2488 | 59.2356 | 57.9386 | 57.0488
FLEET-BRAMLEY GSP | ALTON BSP | PRESTON CANDOVER PRIMARY | MINIMUM HEADROOM | SU 60879 41131 | NO | NO | 9.135 | 3.492 | 3.4563 | 3.4675 | 3.3747 | 3.2961 | 3.2093 | 3.0042 | 2.7471 | 2.5338 | -0.1029 | -0.48759 | -0.67841 | 6.0542 | 5.9726 | 5.9573 | 5.693 | 5.4777 | 5.3308 | 5.1032 | 4.844 | 4.6236 | 2.0144 | 1.694 | 1.5114 | 4.9093 | 4.8644 | 4.8461 | 4.5644 | 4.3032 | 4.1706 | 3.9298 | 3.641 | 3.3951 | 0.82465 | 0.54098 | 0.48588
|  | PRESTON CANDOVER PRIMARY | EE |  |  |  |  | 3.492 | 3.5287 | 3.4716 | 3.4002 | 3.3502 | 3.2767 | 3.0828 | 2.8522 | 2.6277 | -0.053918 | -0.4182 | -0.61106 | 6.0542 | 6.0542 | 5.9624 | 5.7083 | 5.5369 | 5.3798 | 5.1522 | 4.9287 | 4.7349 | 2.0471 | 1.694 | 1.5114 | 4.9093 | 4.9318 | 4.8481 | 4.5757 | 4.3481 | 4.2012 | 3.9532 | 3.6889 | 3.4604 | 0.84608 | 0.55424 | 0.48588
|  | PRESTON CANDOVER PRIMARY | HT |  |  |  |  | 3.494 | 3.4563 | 3.4675 | 3.3747 | 3.2961 | 3.2093 | 3.0042 | 2.7471 | 2.5338 | -0.1029 | -0.48759 | -0.67841 | 6.0593 | 5.9726 | 5.9573 | 5.693 | 5.4777 | 5.3308 | 5.1032 | 4.844 | 4.6236 | 2.0144 | 1.7349 | 1.693 | 4.9124 | 4.8644 | 4.8461 | 4.5644 | 4.3032 | 4.1706 | 3.9298 | 3.641 | 3.3951 | 0.82465 | 0.54098 | 0.49098
|  | PRESTON CANDOVER PRIMARY | HE |  |  |  |  | 3.492 | 3.5104 | 3.4736 | 3.391 | 3.3389 | 3.2736 | 3.1063 | 2.842 | 2.5961 | 0.15322 | -0.089633 | -0.24473 | 6.0542 | 6.0338 | 5.9624 | 5.7063 | 5.5298 | 5.4175 | 5.2093 | 4.9553 | 4.7175 | 2.3104 | 2.1532 | 1.9798 | 4.9104 | 4.9216 | 4.8481 | 4.5706 | 4.3389 | 4.2298 | 4.0002 | 3.7083 | 3.4389 | 1.0951 | 0.96955 | 0.92567
|  | PRESTON CANDOVER PRIMARY | FB |  |  |  |  | 3.5583 | 3.6032 | 3.6481 | 3.6247 | 3.643 | 3.6349 | 3.6216 | 3.5247 | 3.5451 | 3.1736 | 0.62363 | 0.35629 | 6.1144 | 6.1165 | 6.1175 | 6.0614 | 6.041 | 6.0002 | 5.944 | 5.6716 | 5.6716 | 4.9961 | 2.4696 | 1.6451 | 4.9563 | 4.9879 | 5.0144 | 4.9736 | 4.941 | 4.9053 | 4.8542 | 4.5787 | 4.6104 | 3.9573 | 1.6471 | 1.2196
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN PRIMARY | MINIMUM HEADROOM | SY 74226 95039 | NO | NO | 0.016 | 5.7624 | 5.739 | 5.692 | 5.4941 | 5.3104 | 5.0339 | 4.8145 | 4.6257 | 4.391 | 3.6114 | 3.0063 | 2.6788 | 6.0026 | 5.9821 | 5.9546 | 5.7923 | 5.6077 | 5.4066 | 5.2556 | 5.1628 | 4.9985 | 4.4423 | 4.1781 | 3.977 | 6.0247 | 5.9961 | 5.9563 | 5.739 | 5.59 | 5.3543 | 5.1737 | 5.0237 | 4.8257 | 4.1686 | 3.7186 | 3.5308
|  | PUDDLETOWN PRIMARY | EE |  |  |  |  | 5.7635 | 5.7451 | 5.6982 | 5.5237 | 5.3594 | 5.1176 | 4.8941 | 4.7369 | 4.5186 | 3.7808 | 3.2522 | 2.9614 | 6.0026 | 5.9862 | 5.9628 | 5.7995 | 5.6219 | 5.4423 | 5.2699 | 5.1913 | 5.0291 | 4.4719 | 4.1985 | 4.0117 | 6.0257 | 6.0033 | 5.9665 | 5.7645 | 5.6298 | 5.4267 | 5.239 | 5.1145 | 4.9329 | 4.2951 | 3.8798 | 3.6798
|  | PUDDLETOWN PRIMARY | HT |  |  |  |  | 5.7624 | 5.739 | 5.692 | 5.4941 | 5.3104 | 5.0339 | 4.8145 | 4.6257 | 4.391 | 3.6114 | 3.0063 | 2.6788 | 6.0046 | 5.9821 | 5.9546 | 5.7923 | 5.6077 | 5.4066 | 5.2556 | 5.1628 | 4.9985 | 4.4423 | 4.1781 | 4.1168 | 6.0247 | 5.9961 | 5.9563 | 5.739 | 5.59 | 5.3543 | 5.1737 | 5.0237 | 4.8257 | 4.1686 | 3.7186 | 3.5308
|  | PUDDLETOWN PRIMARY | HE |  |  |  |  | 5.7645 | 5.7441 | 5.7002 | 5.5196 | 5.3512 | 5.0961 | 4.8573 | 4.7022 | 4.492 | 3.9522 | 3.5716 | 3.3757 | 6.0046 | 5.9862 | 5.9638 | 5.7995 | 5.6189 | 5.4372 | 5.2607 | 5.1985 | 5.0505 | 4.5893 | 4.4638 | 4.3617 | 6.0257 | 6.0033 | 5.9686 | 5.7624 | 5.6247 | 5.4135 | 5.2155 | 5.0992 | 4.9257 | 4.4441 | 4.1829 | 4.0645
|  | PUDDLETOWN PRIMARY | FB |  |  |  |  | 5.8043 | 5.8104 | 5.8053 | 5.791 | 5.7594 | 5.7471 | 5.7053 | 5.6849 | 5.442 | 5.0033 | 4.5094 | 4.0645 | 6.0372 | 6.0362 | 6.0219 | 6.0107 | 5.9832 | 5.9556 | 5.9036 | 5.8617 | 5.6138 | 5.2128 | 4.6372 | 3.977 | 6.0798 | 6.089 | 6.0849 | 6.0767 | 6.0533 | 6.0298 | 5.9849 | 5.9451 | 5.6686 | 5.2808 | 4.8318 | 4.4135
AXMINSTER GSP | YEOVIL BSP | PULHAM PRIMARY | MINIMUM HEADROOM | ST 71579 09451 | NO | NO | 0.472 | 6.4367 | 6.4235 | 6.3357 | 6.1694 | 5.9918 | 5.749 | 5.3857 | 4.9776 | 4.6541 | 3.4959 | 2.3827 | 1.8276 | 7.4582 | 7.4398 | 7.2929 | 7.0929 | 6.8469 | 6.6786 | 6.3918 | 6.0531 | 5.7694 | 4.752 | 4.0898 | 4.0724 | 7.0684 | 7.0541 | 6.8837 | 6.6867 | 6.4776 | 6.2867 | 5.9847 | 5.6286 | 5.3398 | 4.3245 | 3.4776 | 3.1857
|  | PULHAM PRIMARY | EE |  |  |  |  | 6.4378 | 6.4255 | 6.3408 | 6.202 | 6.0561 | 5.8224 | 5.4735 | 5.0663 | 4.8235 | 3.5082 | 2.4469 | 2.1551 | 7.4602 | 7.4449 | 7.298 | 7.1082 | 6.8806 | 6.7184 | 6.4408 | 6.0531 | 5.8704 | 4.7878 | 4.0898 | 4.1255 | 7.0694 | 7.0571 | 6.8898 | 6.7112 | 6.5224 | 6.3388 | 6.0429 | 5.6724 | 5.4663 | 4.349 | 3.5143 | 3.4235
|  | PULHAM PRIMARY | HT |  |  |  |  | 6.4367 | 6.4265 | 6.3357 | 6.1694 | 5.9918 | 5.749 | 5.3959 | 5.0224 | 4.6541 | 3.4959 | 2.3827 | 1.8276 | 7.4582 | 7.4408 | 7.2929 | 7.0929 | 6.8469 | 6.6786 | 6.3918 | 6.0806 | 5.7694 | 4.752 | 4.1143 | 4.0724 | 7.0684 | 7.0561 | 6.8837 | 6.6867 | 6.4776 | 6.2867 | 5.9847 | 5.6612 | 5.3398 | 4.3245 | 3.4776 | 3.1857
|  | PULHAM PRIMARY | HE |  |  |  |  | 6.4388 | 6.4235 | 6.3398 | 6.1806 | 6.0388 | 5.7765 | 5.3857 | 4.9776 | 4.6673 | 3.8194 | 2.998 | 2.5184 | 7.4602 | 7.4398 | 7.2969 | 7.1061 | 6.9122 | 6.7337 | 6.4184 | 6.0643 | 5.8235 | 5.0827 | 4.701 | 4.4653 | 7.0704 | 7.0541 | 6.8888 | 6.699 | 6.5327 | 6.3214 | 5.9888 | 5.6286 | 5.3633 | 4.6235 | 4.05 | 3.7327
|  | PULHAM PRIMARY | FB |  |  |  |  | 6.5286 | 6.551 | 6.5735 | 6.5755 | 6.4918 | 6.4092 | 6.3592 | 6.2704 | 6.2418 | 5.4888 | 4.7847 | 4.2286 | 7.5316 | 7.5255 | 7.5184 | 7.5204 | 7.3541 | 7.2235 | 7.1541 | 6.9745 | 6.9276 | 6.1143 | 5.2847 | 4.4071 | 7.1663 | 7.1816 | 7.2 | 7.199 | 7.0204 | 6.9071 | 6.8714 | 6.7337 | 6.698 | 5.9776 | 5.3378 | 4.8163
LOVEDEAN GSP | FORT WIDLEY BSP | PURBROOK PRIMARY | MINIMUM HEADROOM | SU 67047 07819 | NO | YES | 2.146 | 6.3029 | 6.2478 | 6.0978 | 5.8794 | 5.5672 | 5.0458 | 4.4754 | 3.8774 | 3.2927 | 1.1764 | -0.23484 | -1.0583 | 7.2932 | 7.1963 | 7.0728 | 6.9718 | 6.7616 | 6.4636 | 6.0993 | 5.7034 | 5.333 | 4.1422 | 2.0085 | -1.0221 | 6.4463 | 6.3851 | 6.282 | 6.1504 | 5.9157 | 5.5218 | 5.0718 | 4.582 | 4.1024 | 2.4167 | 1.4034 | 0.90241
|  | PURBROOK PRIMARY | EE |  |  |  |  | 6.3029 | 6.2672 | 6.1274 | 5.957 | 5.708 | 5.2407 | 4.7284 | 4.1988 | 3.6784 | 1.8356 | 0.44169 | -0.4532 | 7.2932 | 7.2198 | 7.1024 | 7.032 | 6.8626 | 6.6157 | 6.3075 | 5.9698 | 5.6493 | 4.1422 | 2.9606 | 1.7351 | 6.4463 | 6.4034 | 6.3044 | 6.2136 | 6.0269 | 5.6738 | 5.2738 | 4.8504 | 4.4351 | 2.9218 | 1.9167 | 1.3493
|  | PURBROOK PRIMARY | HT |  |  |  |  | 6.3029 | 6.2478 | 6.0978 | 5.8794 | 5.5672 | 5.0458 | 4.4754 | 3.8774 | 3.2927 | 1.1764 | -0.23484 | -1.0583 | 7.2942 | 7.1963 | 7.0728 | 6.9718 | 6.7616 | 6.4636 | 6.0993 | 5.7034 | 5.333 | 4.183 | 3.5708 | 3.2473 | 6.4473 | 6.3851 | 6.282 | 6.1504 | 5.9157 | 5.5218 | 5.0718 | 4.582 | 4.1024 | 2.4167 | 1.4034 | 0.90241
|  | PURBROOK PRIMARY | HE |  |  |  |  | 6.306 | 6.2723 | 6.1397 | 5.957 | 5.6968 | 5.2335 | 4.7366 | 4.2101 | 3.6907 | 2.1846 | 1.0131 | 0.29271 | 7.2942 | 7.2198 | 7.1034 | 7.032 | 6.8606 | 6.6157 | 6.3075 | 5.9708 | 5.6524 | 4.1963 | 3.0014 | 1.7259 | 6.4504 | 6.4096 | 6.3147 | 6.2167 | 6.0198 | 5.6718 | 5.282 | 4.8616 | 4.4493 | 3.1585 | 2.2871 | 1.78
|  | PURBROOK PRIMARY | FB |  |  |  |  | 6.4509 | 6.4764 | 6.4437 | 6.3641 | 6.2794 | 6.2192 | 6.0856 | 5.9386 | 5.7703 | 4.855 | 3.6764 | 2.9243 | 7.3851 | 7.3208 | 7.231 | 7.1167 | 6.9667 | 6.8289 | 6.5942 | 6.3504 | 6.0922 | 4.4412 | 2.0085 | -1.0221 | 6.6085 | 6.6249 | 6.6157 | 6.5657 | 6.5065 | 6.4789 | 6.3616 | 6.233 | 6.0871 | 5.1983 | 4.0861 | 3.4473
FLEET-BRAMLEY GSP | PYESTOCK BSP | PYESTOCK PRIMARY | MINIMUM HEADROOM | SU 82940 54553 | NO | NO | 11.45 | 11.2322 | 10.9741 | 10.8098 | 10.6363 | 10.4914 | 10.3516 | 10.2139 | 10.0833 | 9.9404 | 9.5435 | 9.5853 | 9.6006 | 10.0163 | 9.899 | 9.8316 | 9.7643 | 9.7061 | 9.649 | 9.6031 | 9.552 | 9.4959 | 9.3031 | 9.3082 | 9.3102 | 10.2139 | 10.0067 | 9.8935 | 9.7741 | 9.6731 | 9.5771 | 9.4802 | 9.3904 | 9.2914 | 8.972 | 8.9924 | 9.0016
|  | PYESTOCK PRIMARY | EE |  |  |  |  | 11.2322 | 10.9741 | 10.8098 | 10.6363 | 10.4914 | 10.3516 | 10.2169 | 10.0904 | 9.9506 | 9.5547 | 9.5894 | 9.6037 | 10.0163 | 9.9 | 9.8316 | 9.7643 | 9.7082 | 9.65 | 9.6041 | 9.5531 | 9.4969 | 9.3051 | 9.3102 | 9.3122 | 10.2139 | 10.0067 | 9.8935 | 9.7741 | 9.6731 | 9.5771 | 9.4822 | 9.3945 | 9.2976 | 8.9771 | 8.9965 | 9.0047
|  | PYESTOCK PRIMARY | HT |  |  |  |  | 11.2333 | 10.9802 | 10.8394 | 10.6843 | 10.5547 | 10.4261 | 10.3016 | 10.1884 | 10.0618 | 9.6016 | 9.6027 | 9.6037 | 10.0163 | 9.899 | 9.8367 | 9.7704 | 9.7143 | 9.6561 | 9.6051 | 9.5541 | 9.5082 | 9.3102 | 9.3122 | 9.3122 | 10.2149 | 10.0098 | 9.9098 | 9.7996 | 9.7088 | 9.6169 | 9.5292 | 9.4476 | 9.3578 | 9.0027 | 9.0037 | 9.0047
|  | PYESTOCK PRIMARY | HE |  |  |  |  | 11.2322 | 10.9741 | 10.8098 | 10.6435 | 10.5027 | 10.3547 | 10.2139 | 10.0833 | 9.9404 | 9.5435 | 9.5853 | 9.6006 | 10.0163 | 9.9 | 9.8316 | 9.7653 | 9.7061 | 9.649 | 9.6031 | 9.552 | 9.4959 | 9.3031 | 9.3082 | 9.3102 | 10.2139 | 10.0067 | 9.8935 | 9.7771 | 9.6792 | 9.5771 | 9.4802 | 9.3904 | 9.2914 | 8.972 | 8.9924 | 9.0016
|  | PYESTOCK PRIMARY | FB |  |  |  |  | 11.2384 | 11.0108 | 10.8822 | 10.7353 | 10.6139 | 10.4914 | 10.3741 | 10.2659 | 10.1445 | 9.6924 | 9.6924 | 9.6924 | 10.0163 | 9.9041 | 9.8429 | 9.7755 | 9.7184 | 9.6653 | 9.6112 | 9.5612 | 9.5092 | 9.3153 | 9.3153 | 9.3153 | 10.2169 | 10.022 | 9.9322 | 9.8282 | 9.7404 | 9.6527 | 9.568 | 9.4894 | 9.4027 | 9.0608 | 9.0608 | 9.0618
MINETY GSP | TOOTHILL BSP | QUARRY ROAD PRIMARY | MINIMUM HEADROOM | SU 15334 83380 | NO | NO | 0.9 | 13.0992 | 13.0288 | 13.0063 | 12.7237 | 12.1757 | 11.4522 | 10.5676 | 9.7492 | 9.0451 | 5.8522 | 3.0104 | 1.7757 | 16.4888 | 16.3173 | 16.2347 | 15.9112 | 15.3612 | 14.8327 | 14.0235 | 13.3153 | 12.6622 | 9.852 | 7.4663 | 3.4908 | 15.5808 | 15.4624 | 15.4033 | 15.0788 | 14.4971 | 13.8584 | 12.9492 | 12.1614 | 11.4482 | 8.5033 | 6.0186 | 5.0716
|  | QUARRY ROAD PRIMARY | EE |  |  |  |  | 13.0992 | 13.0288 | 13.0063 | 12.7237 | 12.2624 | 11.5053 | 10.6186 | 9.8216 | 9.0992 | 5.8522 | 3.0104 | 1.7757 | 16.4888 | 16.3173 | 16.2347 | 15.9112 | 15.4602 | 14.9133 | 14.1224 | 13.4633 | 12.8092 | 9.852 | 7.4663 | 5.8582 | 15.5808 | 15.4624 | 15.4033 | 15.0788 | 14.5839 | 13.9073 | 13.0073 | 12.2563 | 11.5308 | 8.5033 | 6.0186 | 5.0716
|  | QUARRY ROAD PRIMARY | HT |  |  |  |  | 13.1247 | 13.0502 | 13.0359 | 12.7502 | 12.1757 | 11.4522 | 10.5676 | 9.7492 | 9.0451 | 5.9522 | 3.34 | 2.4859 | 16.5061 | 16.3194 | 16.2347 | 15.9112 | 15.3612 | 14.8327 | 14.0235 | 13.3153 | 12.6622 | 10.4184 | 8.7806 | 8.4378 | 15.6063 | 15.4808 | 15.4308 | 15.0982 | 14.4971 | 13.8584 | 12.9492 | 12.1614 | 11.4482 | 8.639 | 6.4186 | 5.9186
|  | QUARRY ROAD PRIMARY | HE |  |  |  |  | 13.1135 | 13.0665 | 13.0431 | 12.7492 | 12.2737 | 11.5818 | 10.7369 | 9.988 | 9.3114 | 6.8186 | 5.14 | 4.0645 | 16.4908 | 16.3204 | 16.2388 | 15.9163 | 15.4612 | 14.9337 | 14.1276 | 13.4633 | 12.8061 | 10.2847 | 8.6112 | 6.9378 | 15.5941 | 15.4859 | 15.441 | 15.1022 | 14.591 | 13.9635 | 13.0808 | 12.3543 | 11.6533 | 9.3594 | 8.0073 | 7.1727
|  | QUARRY ROAD PRIMARY | FB |  |  |  |  | 13.4584 | 13.5604 | 13.4002 | 13.2869 | 13.1971 | 12.9431 | 12.6308 | 12.3267 | 12.1084 | 10.3747 | 8.2165 | 6.1543 | 16.6704 | 16.6296 | 16.3847 | 16.1816 | 16.0194 | 15.6908 | 15.2357 | 14.8153 | 14.4224 | 11.5245 | 8.0102 | 3.4908 | 15.9033 | 15.9818 | 15.8196 | 15.6788 | 15.5971 | 15.3686 | 15.0369 | 14.7318 | 14.4859 | 12.4859 | 10.341 | 8.3471
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | QUEENSMEAD PRIMARY | MINIMUM HEADROOM | SU 87062 55683 | NO | NO | 4.555 | 3.9684 | 3.899 | 3.6837 | 3.5174 | 3.1347 | 2.8092 | 2.3255 | 1.8755 | 1.4398 | -0.47446 | -1.8122 | -2.1867 | 4.4113 | 4.2745 | 4.0715 | 3.8613 | 3.4766 | 3.2521 | 2.8113 | 2.3806 | 2.048 | 0.59187 | -1.2949 | -3.704 | 4.6786 | 4.5837 | 4.3796 | 4.1929 | 3.7745 | 3.4929 | 3.0092 | 2.5531 | 2.1551 | 0.53269 | -0.57446 | -0.83058
|  | QUEENSMEAD PRIMARY | EE |  |  |  |  | 3.9684 | 3.899 | 3.6837 | 3.5215 | 3.1511 | 2.8092 | 2.3255 | 1.9551 | 1.4623 | -0.4418 | -1.7887 | -2.1867 | 4.4123 | 4.2786 | 4.0745 | 3.8643 | 3.4919 | 3.2735 | 2.8429 | 2.596 | 2.1643 | 0.59187 | -0.69793 | -1.4612 | 4.6786 | 4.5837 | 4.3796 | 4.1939 | 3.7929 | 3.5 | 3.0174 | 2.697 | 2.2133 | 0.56534 | -0.57446 | -0.83058
|  | QUEENSMEAD PRIMARY | HT |  |  |  |  | 3.9725 | 3.9041 | 3.7062 | 3.5541 | 3.2368 | 2.8541 | 2.397 | 1.8755 | 1.5072 | -0.47446 | -1.8122 | -2.1745 | 4.4123 | 4.2786 | 4.0715 | 3.8653 | 3.55 | 3.2531 | 2.8725 | 2.3806 | 2.1286 | 0.8286 | -0.024457 | -0.18262 | 4.6817 | 4.5888 | 4.3949 | 4.2123 | 3.8684 | 3.5184 | 3.0796 | 2.5531 | 2.2296 | 0.53269 | -0.56323 | -0.76527
|  | QUEENSMEAD PRIMARY | HE |  |  |  |  | 3.9715 | 3.9 | 3.699 | 3.5174 | 3.1347 | 2.8113 | 2.3388 | 1.9725 | 1.4398 | -0.18568 | -1.3867 | -1.6745 | 4.4113 | 4.2745 | 4.0806 | 3.8613 | 3.4766 | 3.2521 | 2.8113 | 2.5449 | 2.048 | 0.62248 | -0.64793 | -1.4132 | 4.6817 | 4.5847 | 4.3949 | 4.1929 | 3.7745 | 3.4929 | 3.0092 | 2.6817 | 2.1551 | 0.74289 | -0.27752 | -0.45405
|  | QUEENSMEAD PRIMARY | FB |  |  |  |  | 4.1133 | 4.0817 | 3.9419 | 3.9031 | 3.647 | 3.5204 | 3.4408 | 3.3347 | 3.199 | 2.0521 | 0.67044 | -0.037722 | 4.5235 | 4.399 | 4.2306 | 4.1041 | 3.799 | 3.5511 | 3.3368 | 3.1184 | 2.8572 | 1.0562 | -1.2949 | -3.704 | 4.8204 | 4.7664 | 4.6419 | 4.5735 | 4.2857 | 4.1337 | 4.0194 | 3.897 | 3.7398 | 2.4949 | 1.1684 | 0.51024
MELKSHAM GSP | WEST GRAFTON BSP | RAMSBURY PRIMARY | MINIMUM HEADROOM | SU 27380 72108 | NO | NO | 1.451 | 4.0908 | 4.0632 | 4.0275 | 3.9959 | 3.9459 | 3.9449 | 3.7204 | 3.4796 | 3.352 | 2.85 | 2.7449 | 2.7877 | 5.099 | 5.0479 | 4.9969 | 4.9592 | 4.9102 | 4.8979 | 4.6847 | 4.45 | 4.3173 | 3.7826 | 3.5234 | 2.7867 | 4.349 | 4.3173 | 4.2816 | 4.2622 | 4.2224 | 4.2194 | 4.0051 | 3.7745 | 3.6459 | 3.0959 | 3.0041 | 3.0775
|  | RAMSBURY PRIMARY | EE |  |  |  |  | 4.0908 | 4.0643 | 4.0316 | 4.0112 | 3.9714 | 3.9847 | 3.7734 | 3.5459 | 3.4479 | 2.9857 | 2.8765 | 2.8959 | 5.099 | 5.049 | 5 | 4.9724 | 4.9296 | 4.9245 | 4.7183 | 4.4938 | 4.3826 | 3.7867 | 3.5234 | 3.3255 | 4.349 | 4.3204 | 4.2847 | 4.2755 | 4.2459 | 4.2581 | 4.0561 | 3.8377 | 3.7224 | 3.1612 | 3.0571 | 3.1347
|  | RAMSBURY PRIMARY | HT |  |  |  |  | 4.0908 | 4.0643 | 4.0275 | 3.9959 | 3.9459 | 3.9449 | 3.7204 | 3.4796 | 3.352 | 2.85 | 2.7449 | 2.7877 | 5.099 | 5.0479 | 4.9969 | 4.9592 | 4.9102 | 4.8979 | 4.6847 | 4.45 | 4.3173 | 3.7826 | 3.6347 | 3.6306 | 4.349 | 4.3204 | 4.2816 | 4.2622 | 4.2224 | 4.2194 | 4.0051 | 3.7745 | 3.6459 | 3.0959 | 3.0041 | 3.0775
|  | RAMSBURY PRIMARY | HE |  |  |  |  | 4.1 | 4.0632 | 4.0296 | 4.0081 | 3.9663 | 3.9836 | 3.7683 | 3.6112 | 3.4418 | 3.1132 | 2.9734 | 2.9428 | 5.1112 | 5.0479 | 4.999 | 4.9694 | 4.9255 | 4.9234 | 4.7163 | 4.549 | 4.3775 | 3.8938 | 3.602 | 3.353 | 4.3602 | 4.3173 | 4.2847 | 4.2734 | 4.2428 | 4.2561 | 4.051 | 3.8979 | 3.7163 | 3.2785 | 3.1418 | 3.149
|  | RAMSBURY PRIMARY | FB |  |  |  |  | 4.153 | 4.1561 | 4.1469 | 4.1673 | 4.1622 | 4.1469 | 4.1234 | 4.0908 | 4.0469 | 3.8612 | 3.5398 | 3.1275 | 5.152 | 5.1204 | 5.0857 | 5.0826 | 5.051 | 5.002 | 4.9398 | 4.8714 | 4.7959 | 4.3765 | 3.6979 | 2.7867 | 4.4214 | 4.4194 | 4.4102 | 4.4357 | 4.4377 | 4.4245 | 4.4 | 4.3663 | 4.3255 | 4.1245 | 3.7204 | 3.349
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | RATFYN PRIMARY | MINIMUM HEADROOM | SU 16215 42533 | NO | NO | 1.609 | 11.4763 | 11.5273 | 11.5845 | 11.3008 | 11.0437 | 10.4539 | 9.7998 | 9.1008 | 8.4151 | 5.662 | 3.4539 | 2.2335 | 13.6839 | 13.6522 | 13.6788 | 13.3859 | 13.1686 | 12.7869 | 12.3431 | 11.8676 | 11.4196 | 9.8278 | 8.6216 | 6.4757 | 12.2896 | 12.2845 | 12.3386 | 11.9896 | 11.7273 | 11.1978 | 10.6151 | 9.9927 | 9.3906 | 7.1784 | 5.609 | 4.9263
|  | RATFYN PRIMARY | EE |  |  |  |  | 11.4763 | 11.5304 | 11.5845 | 11.3222 | 11.1222 | 10.5529 | 9.9559 | 9.359 | 8.76 | 6.2631 | 4.1784 | 3.2253 | 13.6849 | 13.6594 | 13.6829 | 13.4145 | 13.2533 | 12.889 | 12.4757 | 12.0778 | 11.6686 | 9.8971 | 8.6216 | 7.888 | 12.2896 | 12.2876 | 12.3386 | 12.0141 | 11.8182 | 11.3018 | 10.7559 | 10.2284 | 9.6876 | 7.6131 | 6.059 | 5.5396
|  | RATFYN PRIMARY | HT |  |  |  |  | 11.4763 | 11.5345 | 11.5896 | 11.3008 | 11.0437 | 10.4539 | 9.7998 | 9.1008 | 8.4151 | 5.662 | 3.4539 | 2.2335 | 13.6839 | 13.6584 | 13.6788 | 13.3859 | 13.1686 | 12.7869 | 12.3431 | 11.8676 | 11.4196 | 9.8278 | 8.9298 | 8.6533 | 12.2906 | 12.2916 | 12.3406 | 11.9896 | 11.7273 | 11.1978 | 10.6151 | 9.9927 | 9.3906 | 7.1784 | 5.609 | 4.9263
|  | RATFYN PRIMARY | HE |  |  |  |  | 11.4804 | 11.5273 | 11.5947 | 11.3192 | 11.11 | 10.5518 | 9.9835 | 9.3855 | 8.7998 | 6.7386 | 4.96 | 4.0427 | 13.6859 | 13.6522 | 13.6849 | 13.4135 | 13.2492 | 12.8849 | 12.4971 | 12.0818 | 11.6778 | 10.0665 | 8.9839 | 8.0982 | 12.2927 | 12.2845 | 12.3498 | 12.0171 | 11.81 | 11.2998 | 10.7896 | 10.2478 | 9.7171 | 7.9835 | 6.76 | 6.1865
|  | RATFYN PRIMARY | FB |  |  |  |  | 11.6386 | 11.7467 | 11.8365 | 11.8835 | 11.9631 | 11.9029 | 11.8212 | 11.7182 | 11.4845 | 10.3406 | 8.6447 | 7.6406 | 13.7727 | 13.7686 | 13.7533 | 13.7124 | 13.7124 | 13.5635 | 13.3849 | 13.1849 | 12.7869 | 11.1094 | 8.7635 | 6.4757 | 12.458 | 12.5253 | 12.5794 | 12.5855 | 12.6733 | 12.5998 | 12.5049 | 12.3835 | 12.0406 | 10.7794 | 9.1518 | 8.2641
BRAMLEY (BASI) GSP | READING BSP | READING PRIMARY | MINIMUM HEADROOM | SU 74591 73788 | NO | YES | 18.868 | 3.1026 | 2.8822 | 2.5975 | 2.2659 | 1.7098 | 0.8404 | -0.17287 | -1.3443 | -2.5055 | -6.2851 | -8.382 | -8.8994 | 6.5773 | 6.1855 | 5.8069 | 5.3692 | 4.7426 | 3.8824 | 2.8763 | 1.6794 | 0.4906 | -3.539 | -7.4982 | -15.039 | 4.0139 | 3.6863 | 3.3608 | 2.969 | 2.3639 | 1.5108 | 0.50979 | -0.65348 | -1.8116 | -5.5433 | -7.4759 | -8.0963
|  | READING PRIMARY | EE |  |  |  |  | 3.1026 | 2.919 | 2.6822 | 2.47 | 2.0516 | 1.3108 | 0.34652 | -0.71266 | -1.7718 | -5.5218 | -7.9514 | -8.8994 | 6.5773 | 6.212 | 5.8651 | 5.4916 | 4.9447 | 4.1631 | 3.1539 | 2.0263 | 0.89264 | -3.539 | -6.5074 | -9.2074 | 4.0139 | 3.7118 | 3.418 | 3.1292 | 2.6404 | 1.8843 | 0.91795 | -0.15654 | -1.2382 | -5.0188 | -7.2963 | -8.0963
|  | READING PRIMARY | HT |  |  |  |  | 3.1108 | 2.8822 | 2.5975 | 2.2659 | 1.7098 | 0.8404 | -0.17287 | -1.3443 | -2.5055 | -6.2851 | -8.382 | -8.8759 | 6.5784 | 6.1855 | 5.8069 | 5.3692 | 4.7426 | 3.8824 | 2.8763 | 1.6794 | 0.4906 | -3.038 | -4.6512 | -5.04 | 4.0241 | 3.6863 | 3.3608 | 2.969 | 2.3639 | 1.5108 | 0.50979 | -0.65348 | -1.8116 | -5.5433 | -7.4759 | -7.7902
|  | READING PRIMARY | HE |  |  |  |  | 3.1169 | 2.9465 | 2.721 | 2.4843 | 2.0404 | 1.3465 | 0.41693 | -0.62287 | -1.6341 | -4.5433 | -6.3484 | -7.3269 | 6.5804 | 6.2151 | 5.8702 | 5.4916 | 4.9416 | 4.1794 | 3.1784 | 2.0467 | 0.93448 | -2.9216 | -5.8053 | -8.7931 | 4.0271 | 3.7363 | 3.4577 | 3.1455 | 2.6353 | 1.921 | 0.97918 | -0.082049 | -1.1198 | -4.0545 | -5.7545 | -6.628
|  | READING PRIMARY | FB |  |  |  |  | 3.421 | 3.6914 | 3.7526 | 3.7047 | 3.7077 | 3.521 | 3.2843 | 3.0037 | 2.6731 | 0.41591 | -2.7392 | -4.9678 | 6.7171 | 6.6977 | 6.5069 | 6.1406 | 5.81 | 5.2641 | 4.6631 | 4.0314 | 3.3498 | -1.1165 | -7.4982 | -15.039 | 4.3414 | 4.5394 | 4.5394 | 4.3424 | 4.2802 | 4.0496 | 3.7761 | 3.4639 | 3.0986 | 0.67305 | -2.4657 | -4.6678
FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN PRIMARY | MINIMUM HEADROOM | SU 71540 74122 | NO | NO | 14.43 | 53.4674 | 53.2337 | 52.947 | 52.3899 | 51.7368 | 50.6276 | 49.0664 | 47.6837 | 46.2521 | 42.2623 | 40.1388 | 39.048 | 61.5266 | 61.2756 | 61.1664 | 60.9888 | 60.7235 | 60.2521 | 59.1388 | 58.2531 | 57.2807 | 54.0613 | 50.5501 | 45.6991 | 57.347 | 57.1144 | 56.8807 | 56.4644 | 55.9542 | 55.1337 | 53.8858 | 52.8429 | 51.6521 | 48.0623 | 46.2654 | 45.4031
|  | READING TOWN PRIMARY | EE |  |  |  |  | 53.4674 | 53.2337 | 52.947 | 52.3899 | 51.7378 | 50.6276 | 49.0664 | 47.6837 | 46.2521 | 42.2623 | 40.1388 | 39.048 | 61.5378 | 61.2858 | 61.1746 | 61.0001 | 60.7358 | 60.2695 | 59.1715 | 58.2531 | 57.2807 | 54.0613 | 52.0807 | 50.1082 | 57.347 | 57.1144 | 56.8807 | 56.4644 | 55.9613 | 55.1337 | 53.8858 | 52.8429 | 51.6521 | 48.0623 | 46.2654 | 45.4031
|  | READING TOWN PRIMARY | HT |  |  |  |  | 53.4837 | 53.2429 | 52.996 | 52.4674 | 51.8582 | 50.8225 | 49.3164 | 48.0562 | 46.7184 | 42.6807 | 40.9235 | 40.2082 | 61.545 | 61.2756 | 61.1664 | 60.9888 | 60.7235 | 60.2858 | 59.1633 | 58.3205 | 57.3674 | 54.9195 | 54.0001 | 53.4837 | 57.3654 | 57.1317 | 56.9276 | 56.5123 | 56.0195 | 55.2348 | 54.0001 | 53.0348 | 51.997 | 48.3797 | 46.9511 | 46.4593
|  | READING TOWN PRIMARY | HE |  |  |  |  | 53.4746 | 53.247 | 52.9654 | 52.3991 | 51.7368 | 50.6633 | 49.1276 | 47.7715 | 46.3603 | 43.395 | 42.097 | 41.4174 | 61.548 | 61.295 | 61.1888 | 61.0195 | 60.7603 | 60.3195 | 59.2307 | 58.3205 | 57.3542 | 54.5684 | 52.8695 | 51.0705 | 57.3562 | 57.1307 | 56.9021 | 56.4746 | 55.9542 | 55.1531 | 53.9256 | 52.9001 | 51.8266 | 49.0858 | 47.9552 | 47.4572
|  | READING TOWN PRIMARY | FB |  |  |  |  | 53.5674 | 53.4521 | 53.3001 | 52.8817 | 52.3848 | 51.6368 | 50.4256 | 49.4337 | 48.396 | 46.1154 | 44.4409 | 42.8654 | 61.5266 | 61.3011 | 61.1929 | 61.0052 | 60.7246 | 60.2521 | 59.1388 | 58.3388 | 57.494 | 54.2888 | 50.5501 | 45.6991 | 57.446 | 57.3297 | 57.2184 | 56.9042 | 56.5052 | 55.945 | 54.9511 | 54.1899 | 53.398 | 51.3613 | 49.696 | 48.1848
MANNINGTON GSP | REDHILL BSP | REDHILL PRIMARY | MINIMUM HEADROOM | SZ 08512 96149 | NO | NO | 5.64 | 17.0511 | 16.7072 | 16.3 | 15.7909 | 15.148 | 13.6398 | 12.0296 | 10.3174 | 8.748 | 3.3704 | -0.83771 | -3.001 | 20.3551 | 20.0225 | 19.6562 | 19.3378 | 18.9449 | 18.2511 | 17.4194 | 16.4939 | 15.7011 | 13.1011 | 10.5592 | 5.6286 | 16.0521 | 15.7531 | 15.4113 | 15.0511 | 14.4143 | 13.2184 | 11.8653 | 10.3919 | 9.1204 | 4.746 | 1.9184 | 0.78269
|  | REDHILL PRIMARY | EE |  |  |  |  | 17.0745 | 16.8092 | 16.5 | 16.1245 | 15.6837 | 14.398 | 13.0082 | 11.5429 | 10.2123 | 5.5888 | 1.7358 | -0.40098 | 20.3643 | 20.0735 | 19.7582 | 19.4786 | 19.1745 | 18.6204 | 17.9102 | 17.1215 | 16.4521 | 13.2551 | 10.9245 | 8.9511 | 16.0643 | 15.8123 | 15.5337 | 15.25 | 14.8174 | 13.7939 | 12.6123 | 11.3327 | 10.2398 | 6.2215 | 3.4919 | 2.199
|  | REDHILL PRIMARY | HT |  |  |  |  | 17.0511 | 16.7072 | 16.3 | 15.7909 | 15.148 | 13.6398 | 12.0296 | 10.3174 | 8.748 | 3.3704 | -0.83771 | -3.001 | 20.3551 | 20.0225 | 19.6562 | 19.3378 | 18.9449 | 18.2511 | 17.4194 | 16.4939 | 15.7011 | 13.1011 | 11.6572 | 11.2082 | 16.0521 | 15.7531 | 15.4113 | 15.0511 | 14.4143 | 13.2184 | 11.8653 | 10.3919 | 9.1204 | 4.746 | 1.9184 | 0.78269
|  | REDHILL PRIMARY | HE |  |  |  |  | 17.0776 | 16.8164 | 16.5 | 16.1153 | 15.6062 | 14.3296 | 12.9194 | 11.4439 | 10.097 | 6.1 | 2.647 | 1.098 | 20.3643 | 20.0786 | 19.7551 | 19.497 | 19.1572 | 18.6204 | 17.9092 | 17.1317 | 16.4725 | 13.5572 | 11.3143 | 9.3623 | 16.0674 | 15.8194 | 15.5337 | 15.2531 | 14.7643 | 13.7592 | 12.5613 | 11.298 | 10.2072 | 6.7725 | 4.3521 | 3.4684
|  | REDHILL PRIMARY | FB |  |  |  |  | 17.3092 | 17.2715 | 17.2521 | 17.1817 | 17.1286 | 16.947 | 16.749 | 16.5266 | 16.2551 | 14.1653 | 11.347 | 9.8072 | 20.4715 | 20.297 | 20.1276 | 19.9511 | 19.7419 | 19.3653 | 18.9847 | 18.5735 | 18.1092 | 15.0174 | 10.5592 | 5.6286 | 16.2837 | 16.2276 | 16.1337 | 16.0847 | 16.0123 | 15.8704 | 15.7123 | 15.5307 | 15.2102 | 12.8776 | 10.1337 | 8.5847
CHICKERELL GSP | CHICKERELL BSP | REDLANDS PRIMARY | MINIMUM HEADROOM | SY 67131 82321 | NO | NO | 3.364 | 10.0427 | 11.6482 | 11.4911 | 11.0564 | 10.5411 | 9.5441 | 8.4839 | 7.3931 | 6.337 | 2.4839 | -0.43239 | -2.1997 | 12.456 | 12.7262 | 12.6741 | 12.3772 | 12.0578 | 11.5945 | 11.0772 | 10.516 | 9.9854 | 8.167 | 6.4282 | 3.2558 | 10.9733 | 11.938 | 11.8441 | 11.4064 | 10.9003 | 10.1931 | 9.438 | 8.6411 | 7.8809 | 5.1574 | 3.2268 | 2.2023
|  | REDLANDS PRIMARY | EE |  |  |  |  | 10.0499 | 11.685 | 11.5696 | 11.2278 | 10.8186 | 9.9564 | 8.936 | 7.9584 | 6.987 | 3.7574 | 1.1778 | -0.35178 | 12.4631 | 12.7486 | 12.7282 | 12.4843 | 12.2058 | 11.8445 | 11.3354 | 10.869 | 10.3966 | 8.2466 | 6.7119 | 5.4599 | 10.9805 | 11.9676 | 11.9094 | 11.5472 | 11.1084 | 10.5156 | 9.7594 | 9.0768 | 8.387 | 5.9696 | 4.2115 | 3.2625
|  | REDLANDS PRIMARY | HT |  |  |  |  | 10.0427 | 11.6482 | 11.4911 | 11.0564 | 10.5411 | 9.5441 | 8.4839 | 7.3931 | 6.337 | 2.4839 | -0.43239 | -2.1997 | 12.456 | 12.7262 | 12.6741 | 12.3772 | 12.0578 | 11.5945 | 11.0772 | 10.516 | 9.9854 | 8.167 | 7.2119 | 6.7956 | 10.9733 | 11.938 | 11.8441 | 11.4064 | 10.9003 | 10.1931 | 9.438 | 8.6411 | 7.8809 | 5.1574 | 3.2268 | 2.2023
|  | REDLANDS PRIMARY | HE |  |  |  |  | 10.0529 | 11.686 | 11.5727 | 11.2084 | 10.7768 | 9.9176 | 8.936 | 7.938 | 6.9482 | 4.2329 | 1.9431 | 0.80638 | 12.4631 | 12.7496 | 12.7303 | 12.4813 | 12.2007 | 11.8425 | 11.3772 | 10.8874 | 10.3966 | 8.4384 | 6.9527 | 5.6435 | 10.9825 | 11.9707 | 11.9156 | 11.5401 | 11.086 | 10.4962 | 9.7982 | 9.086 | 8.3768 | 6.3401 | 4.788 | 4.0492
|  | REDLANDS PRIMARY | FB |  |  |  |  | 10.2172 | 11.937 | 11.9503 | 11.9043 | 11.8666 | 11.7176 | 11.5482 | 11.3625 | 11.1625 | 9.6176 | 7.586 | 6.3952 | 12.5601 | 12.8772 | 12.816 | 12.7272 | 12.6537 | 12.4262 | 12.169 | 11.8915 | 11.5956 | 9.3537 | 6.4282 | 3.2558 | 11.1601 | 12.239 | 12.2135 | 12.1615 | 12.1472 | 12.0064 | 11.8421 | 11.6554 | 11.4431 | 9.7309 | 8.0258 | 7.0584
MANNINGTON GSP | SALISBURY BSP | REDLYNCH PRIMARY | MINIMUM HEADROOM | SU 19073 20576 | NO | NO | 0.657 | 3.8474 | 3.8699 | 3.7832 | 3.6128 | 3.4383 | 3.077 | 2.6362 | 2.1128 | 1.6934 | 0.31888 | -0.4199 | -0.59133 | 8.3541 | 8.3061 | 8.1133 | 7.9 | 7.6418 | 7.2704 | 6.8286 | 6.298 | 5.8939 | 4.4112 | 3.4531 | 2.1765 | 4.2071 | 4.2143 | 4.1367 | 3.9459 | 3.7327 | 3.3755 | 2.9724 | 2.4714 | 2.0776 | 0.75306 | 0.13571 | 0.078571
|  | REDLYNCH PRIMARY | EE |  |  |  |  | 3.8526 | 3.875 | 3.7832 | 3.6719 | 3.4913 | 3.2403 | 2.8393 | 2.3944 | 2.0403 | 0.69337 | -0.083163 | -0.32194 | 8.3541 | 8.3082 | 8.1133 | 7.9316 | 7.6592 | 7.3704 | 6.9408 | 6.4612 | 6.0959 | 4.4204 | 3.4531 | 2.8653 | 4.2082 | 4.2184 | 4.1367 | 3.9929 | 3.7704 | 3.5 | 3.1235 | 2.6888 | 2.3398 | 1.0224 | 0.34286 | 0.18571
|  | REDLYNCH PRIMARY | HT |  |  |  |  | 3.8474 | 3.8699 | 3.7985 | 3.6128 | 3.4383 | 3.077 | 2.6362 | 2.1128 | 1.6934 | 0.31888 | -0.4199 | -0.59133 | 8.3541 | 8.3061 | 8.1531 | 7.9 | 7.648 | 7.2704 | 6.8286 | 6.298 | 5.8939 | 4.4112 | 3.7541 | 3.6633 | 4.2071 | 4.2143 | 4.15 | 3.9459 | 3.7327 | 3.3755 | 2.9724 | 2.4714 | 2.0776 | 0.75306 | 0.13571 | 0.078571
|  | REDLYNCH PRIMARY | HE |  |  |  |  | 3.8536 | 3.877 | 3.8209 | 3.6597 | 3.4689 | 3.2056 | 2.8128 | 2.3556 | 2.0066 | 0.85051 | 0.31276 | 0.034184 | 8.3541 | 8.3102 | 8.1633 | 7.9224 | 7.6418 | 7.348 | 6.9388 | 6.4592 | 6.098 | 4.5969 | 3.9541 | 3.3194 | 4.2092 | 4.2204 | 4.1653 | 3.9816 | 3.752 | 3.4714 | 3.1071 | 2.6653 | 2.3235 | 1.1714 | 0.73776 | 0.52755
|  | REDLYNCH PRIMARY | FB |  |  |  |  | 4.025 | 4.1056 | 4.1434 | 4.1842 | 4.1352 | 4.0495 | 3.9862 | 3.8372 | 3.7148 | 2.7913 | 1.7077 | 1.0148 | 8.4867 | 8.4735 | 8.4255 | 8.3806 | 8.1969 | 7.9949 | 7.8327 | 7.5633 | 7.3367 | 5.8541 | 4.051 | 2.1765 | 4.3684 | 4.4286 | 4.448 | 4.4755 | 4.4378 | 4.3357 | 4.2541 | 4.0786 | 3.9337 | 2.9582 | 1.9306 | 1.2694
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | REGENTS PARK PRIMARY | MINIMUM HEADROOM | SU 39267 13050 | NO | NO | 1.228 | 15.1082 | 15.1122 | 15.0816 | 14.9592 | 14.7684 | 14.5214 | 12.1684 | 9.2929 | 7.9837 | -1.499 | -8.8949 | -15.6643 | 15.6653 | 15.6418 | 15.5898 | 15.499 | 15.3418 | 15.1265 | 12.4776 | 9.4582 | 7.9459 | -2.3704 | -12.3071 | -18.5541 | 15.1653 | 15.0418 | 14.8663 | 14.5878 | 14.1704 | 13.6857 | 10.7378 | 7.3592 | 5.8255 | -4.9816 | -14.2276 | -21.6184
|  | REGENTS PARK PRIMARY | EE |  |  |  |  | 15.1082 | 15.1122 | 15.0908 | 15.0133 | 14.9214 | 14.6265 | 13.5867 | 11.3612 | 7.9837 | -0.58367 | -4.502 | -11.7847 | 15.6653 | 15.6429 | 15.6051 | 15.5214 | 15.4449 | 15.2286 | 14.2133 | 11.9673 | 7.9459 | -1.6592 | -5.702 | -14.7878 | 15.1653 | 15.0418 | 14.8755 | 14.6306 | 14.3337 | 13.6857 | 12.4673 | 9.8827 | 5.8255 | -3.9786 | -8.1122 | -16.849
|  | REGENTS PARK PRIMARY | HT |  |  |  |  | 15.1112 | 15.1163 | 15.0816 | 14.9592 | 14.7684 | 14.5214 | 12.1684 | 9.2929 | 8.6878 | -1.499 | -6.5408 | -15.6643 | 15.6694 | 15.6429 | 15.5898 | 15.499 | 15.3418 | 15.1265 | 12.4776 | 9.4582 | 8.951 | -2.3704 | -7.5694 | -18.5541 | 15.1724 | 15.051 | 14.8663 | 14.5878 | 14.1704 | 13.7265 | 10.7378 | 7.3592 | 6.802 | -4.9816 | -10.55 | -21.6184
|  | REGENTS PARK PRIMARY | HE |  |  |  |  | 15.1143 | 15.1276 | 15.1051 | 15.0327 | 14.9429 | 14.6735 | 12.4439 | 11.6582 | 11.1204 | 0.16939 | -8.8949 | -12.3459 | 15.6673 | 15.6418 | 15.599 | 15.5163 | 15.4378 | 15.2245 | 12.6735 | 12.2184 | 11.7357 | -1.3306 | -12.3071 | -16.8173 | 15.1735 | 15.0582 | 14.8898 | 14.6439 | 14.3388 | 13.7173 | 10.9878 | 10.1898 | 9.6714 | -3.3806 | -14.2276 | -18.3071
|  | REGENTS PARK PRIMARY | FB |  |  |  |  | 15.1796 | 15.2194 | 15.251 | 15.2592 | 15.2582 | 15.2071 | 14.6837 | 13.902 | 11.9541 | 6.0378 | -2.2316 | -10.5316 | 15.7071 | 15.702 | 15.6847 | 15.652 | 15.598 | 15.5051 | 14.8214 | 13.8194 | 11.3684 | 3.951 | -6.6378 | -17.7735 | 15.2673 | 15.2255 | 15.1602 | 15.0745 | 14.9571 | 14.7847 | 14.0531 | 13.0286 | 10.4286 | 2.9531 | -6.949 | -16.8551
COWLEY GSP | WITNEY BSP | RISSINGTON PRIMARY | MINIMUM HEADROOM | SP 19225 19563 | YES | NO | 4.446 | 6.1827 | 6.197 | 6.2021 | 5.997 | 5.7664 | 5.3286 | 4.8715 | 4.3797 | 3.8378 | 1.8368 | 0.26434 | -0.77749 | 8.0633 | 8.0705 | 8.0399 | 7.849 | 7.7429 | 7.4643 | 7.2062 | 6.8919 | 6.5817 | 5.395 | 4.7429 | 4.2062 | 6.8194 | 6.8307 | 6.8266 | 6.6103 | 6.4858 | 6.1215 | 5.7256 | 5.295 | 4.8694 | 3.2797 | 2.1868 | 1.5745
|  | RISSINGTON PRIMARY | EE |  |  |  |  | 6.1827 | 6.197 | 6.2021 | 6.0215 | 5.848 | 5.4337 | 5.0164 | 4.5745 | 4.1378 | 2.3776 | 0.99088 | 0.30006 | 8.0633 | 8.0715 | 8.045 | 7.8776 | 7.8276 | 7.5725 | 7.3613 | 7.0307 | 6.7348 | 5.5164 | 4.7429 | 4.4256 | 6.8194 | 6.8307 | 6.8266 | 6.6409 | 6.5807 | 6.2501 | 5.9266 | 5.4899 | 5.099 | 3.6592 | 2.6439 | 2.2664
|  | RISSINGTON PRIMARY | HT |  |  |  |  | 6.2011 | 6.2194 | 6.2062 | 5.997 | 5.7664 | 5.3286 | 4.8715 | 4.3797 | 3.8378 | 1.8368 | 0.26434 | -0.77749 | 8.0643 | 8.0705 | 8.0399 | 7.849 | 7.7429 | 7.4643 | 7.2062 | 6.8919 | 6.5817 | 5.395 | 4.7735 | 4.5562 | 6.8307 | 6.8429 | 6.8286 | 6.6103 | 6.4858 | 6.1215 | 5.7256 | 5.295 | 4.8694 | 3.2797 | 2.1868 | 1.5745
|  | RISSINGTON PRIMARY | HE |  |  |  |  | 6.1837 | 6.2001 | 6.2031 | 6.0001 | 5.8266 | 5.3888 | 4.9511 | 4.4909 | 4.0399 | 2.6674 | 1.4725 | 0.83067 | 8.0633 | 8.0715 | 8.046 | 7.8766 | 7.8256 | 7.5654 | 7.3531 | 7.0337 | 6.7429 | 5.6919 | 5.0541 | 4.6439 | 6.8215 | 6.8327 | 6.8276 | 6.6317 | 6.5715 | 6.2245 | 5.8909 | 5.4582 | 5.0552 | 3.9041 | 3.0603 | 2.6674
|  | RISSINGTON PRIMARY | FB |  |  |  |  | 6.2745 | 6.3194 | 6.3572 | 6.3848 | 6.3735 | 6.3041 | 6.246 | 6.097 | 6.0021 | 5.295 | 4.2021 | 3.4317 | 8.1348 | 8.1501 | 8.1643 | 8.1735 | 8.1552 | 8.1154 | 8.0909 | 7.8194 | 7.696 | 6.7215 | 5.3939 | 4.2062 | 6.945 | 6.9929 | 7.0388 | 7.0643 | 7.0725 | 7.0348 | 6.9939 | 6.8348 | 6.7511 | 5.9582 | 4.8827 | 4.2297
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | RIVERSIDE PRIMARY | MINIMUM HEADROOM | SU 47846 67187 | NO | NO | 4.44 | 10.9024 | 10.7871 | 10.7371 | 10.5789 | 10.4096 | 10.2208 | 9.9504 | 9.6932 | 9.4238 | 8.0616 | 7.1177 | 6.7422 | 13.8131 | 13.658 | 13.5958 | 13.4968 | 13.3601 | 13.2274 | 13.0356 | 12.8621 | 12.6846 | 11.9458 | 10.7774 | 9.0784 | 12.8371 | 12.534 | 12.4249 | 12.1932 | 11.9238 | 11.6657 | 11.2514 | 10.9136 | 10.532 | 8.7922 | 7.4769 | 7.1544
|  | RIVERSIDE PRIMARY | EE |  |  |  |  | 10.9024 | 10.7871 | 10.7371 | 10.584 | 10.4177 | 10.23 | 9.9728 | 9.7279 | 9.4759 | 8.3228 | 7.4442 | 7.1187 | 13.8162 | 13.6611 | 13.6029 | 13.5121 | 13.3794 | 13.257 | 13.0754 | 12.9131 | 12.7519 | 12.0101 | 10.7774 | 10.0733 | 12.8381 | 12.534 | 12.4249 | 12.2065 | 11.9371 | 11.6983 | 11.2983 | 10.9718 | 10.6136 | 8.8677 | 7.4769 | 7.1544
|  | RIVERSIDE PRIMARY | HT |  |  |  |  | 10.9024 | 10.7912 | 10.7402 | 10.5963 | 10.4249 | 10.2208 | 9.9504 | 9.6932 | 9.4238 | 8.0616 | 7.1177 | 6.7422 | 13.8141 | 13.6611 | 13.5958 | 13.4968 | 13.3601 | 13.2274 | 13.0356 | 12.8621 | 12.6846 | 11.9458 | 11.3794 | 11.0713 | 12.8412 | 12.5412 | 12.4289 | 12.1932 | 11.9238 | 11.6657 | 11.2514 | 10.9136 | 10.532 | 8.7922 | 7.5861 | 7.3075
|  | RIVERSIDE PRIMARY | HE |  |  |  |  | 10.9034 | 10.7942 | 10.7391 | 10.5789 | 10.4096 | 10.2391 | 10.0014 | 9.7759 | 9.5453 | 8.5779 | 7.9963 | 7.6524 | 13.8131 | 13.658 | 13.5978 | 13.505 | 13.3743 | 13.2529 | 13.0672 | 12.9029 | 12.7315 | 12.1488 | 11.9141 | 11.0672 | 12.8371 | 12.5412 | 12.4351 | 12.2116 | 11.9473 | 11.7208 | 11.3289 | 11.0106 | 10.6708 | 9.4687 | 8.9014 | 8.5014
|  | RIVERSIDE PRIMARY | FB |  |  |  |  | 10.9453 | 10.9167 | 10.8636 | 10.8453 | 10.8044 | 10.7647 | 10.7075 | 10.6269 | 10.5759 | 9.9667 | 9.0749 | 8.5136 | 13.8519 | 13.8203 | 13.7039 | 13.6662 | 13.6366 | 13.609 | 13.5682 | 13.4978 | 13.4519 | 12.8478 | 11.4019 | 9.0784 | 12.884 | 12.8371 | 12.6371 | 12.5626 | 12.5218 | 12.4422 | 12.3677 | 12.2351 | 12.1881 | 11.2096 | 9.7391 | 8.68
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE PRIMARY | MINIMUM HEADROOM | SU 11617 17810 | YES | NO | 0.037 | 2.9206 | 2.9227 | 2.9135 | 2.8716 | 2.8482 | 2.7849 | 2.7043 | 2.6124 | 2.5298 | 2.442 | 2.2614 | 2.139 | 3.0645 | 3.0563 | 3.04 | 3.0073 | 2.99 | 2.9288 | 2.8716 | 2.8094 | 2.7502 | 2.6849 | 2.5788 | 2.3492 | 2.961 | 2.962 | 2.9518 | 2.9151 | 2.8957 | 2.8273 | 2.762 | 2.6916 | 2.6406 | 2.5661 | 2.459 | 2.4171
|  | ROCKBOURNE PRIMARY | EE |  |  |  |  | 2.9227 | 2.9247 | 2.9186 | 2.8788 | 2.8594 | 2.8012 | 2.7288 | 2.6482 | 2.5757 | 2.442 | 2.2869 | 2.2114 | 3.0655 | 3.0604 | 3.0471 | 3.0155 | 3.0043 | 2.9482 | 2.8961 | 2.839 | 2.788 | 2.6951 | 2.6033 | 2.542 | 2.9631 | 2.9661 | 2.959 | 2.9212 | 2.908 | 2.8386 | 2.7947 | 2.7294 | 2.6671 | 2.5794 | 2.4865 | 2.4641
|  | ROCKBOURNE PRIMARY | HT |  |  |  |  | 2.9206 | 2.9227 | 2.9135 | 2.8716 | 2.8482 | 2.789 | 2.7165 | 2.6329 | 2.5594 | 2.4492 | 2.2614 | 2.139 | 3.0645 | 3.0563 | 3.04 | 3.0073 | 2.99 | 2.9288 | 2.8716 | 2.8094 | 2.7502 | 2.6849 | 2.6369 | 2.6471 | 2.961 | 2.962 | 2.9518 | 2.9151 | 2.8957 | 2.8273 | 2.762 | 2.6916 | 2.6457 | 2.5661 | 2.459 | 2.4171
|  | ROCKBOURNE PRIMARY | HE |  |  |  |  | 2.9227 | 2.9247 | 2.9176 | 2.8737 | 2.8645 | 2.7849 | 2.7043 | 2.6124 | 2.5298 | 2.4665 | 2.2798 | 2.1808 | 3.0655 | 3.0594 | 3.0451 | 3.0165 | 3.0012 | 2.9451 | 2.8941 | 2.8369 | 2.7818 | 2.6961 | 2.588 | 2.4982 | 2.9631 | 2.9651 | 2.9569 | 2.9192 | 2.8988 | 2.8294 | 2.7804 | 2.708 | 2.6406 | 2.5916 | 2.4702 | 2.4192
|  | ROCKBOURNE PRIMARY | FB |  |  |  |  | 2.9655 | 2.9869 | 2.9992 | 3.0033 | 2.9992 | 2.989 | 2.9665 | 2.9563 | 2.9267 | 2.79 | 2.7043 | 2.6594 | 3.1012 | 3.1012 | 3.0971 | 3.0931 | 3.0778 | 3.0553 | 3.0196 | 2.9982 | 2.9573 | 2.7512 | 2.5788 | 2.3492 | 3.0049 | 3.0222 | 3.0304 | 3.0335 | 3.0294 | 3.0182 | 2.9947 | 2.9835 | 2.9539 | 2.809 | 2.759 | 2.7212
NURSLING GSP | ROWNHAMS BSP | ROMSEY PRIMARY | MINIMUM HEADROOM | SU 36092 21110 | NO | YES | 5.063 | -6.1286 | 18.3714 | 18.2194 | 17.9735 | 17.6214 | 17.2153 | 16.7296 | 15.9276 | 15.3357 | 12.3204 | 10.4408 | 9.548 | 2.1408 | 24.8347 | 24.6133 | 24.2551 | 23.7306 | 23.1643 | 22.4296 | 21.552 | 20.9357 | 17.599 | 15.4816 | 13.4214 | -2.6245 | 20.8408 | 20.6908 | 20.4112 | 19.9776 | 19.4878 | 18.7582 | 17.8918 | 17.2857 | 14.2735 | 12.3949 | 11.4949
|  | ROMSEY PRIMARY | EE |  |  |  |  | -6.1276 | 18.599 | 18.2194 | 17.9837 | 17.6388 | 17.2296 | 16.7561 | 15.948 | 15.3357 | 12.3204 | 10.4408 | 9.548 | 2.1418 | 25.0194 | 24.6173 | 24.2653 | 23.748 | 23.1888 | 22.4571 | 21.5796 | 20.9469 | 17.599 | 15.4816 | 14.0582 | -2.6245 | 21.051 | 20.6949 | 20.4255 | 20.001 | 19.5031 | 18.7765 | 17.9071 | 17.2857 | 14.2735 | 12.3949 | 11.4949
|  | ROMSEY PRIMARY | HT |  |  |  |  | -6.1276 | 18.3714 | 18.2214 | 17.9878 | 17.6469 | 17.2347 | 16.7398 | 15.95 | 15.3541 | 12.5918 | 10.8806 | 10.3633 | 2.1408 | 24.8347 | 24.6163 | 24.2592 | 23.7469 | 23.1643 | 22.4296 | 21.552 | 20.9357 | 18.0051 | 16.3878 | 15.9327 | -2.6245 | 20.8408 | 20.6939 | 20.4204 | 20.001 | 19.4878 | 18.7633 | 17.901 | 17.301 | 14.5102 | 12.8306 | 12.3663
|  | ROMSEY PRIMARY | HE |  |  |  |  | -6.1286 | 18.6 | 18.2194 | 17.9735 | 17.6214 | 17.2153 | 16.7296 | 15.9276 | 15.3408 | 12.8316 | 11.7929 | 11.1949 | 2.1418 | 25.0184 | 24.6133 | 24.2551 | 23.7306 | 23.1806 | 22.4429 | 21.5643 | 20.9663 | 18.0163 | 16.7061 | 15.4918 | -2.6235 | 21.048 | 20.6908 | 20.4112 | 19.9776 | 19.4888 | 18.7582 | 17.8918 | 17.3245 | 14.7765 | 13.8418 | 13.3265
|  | ROMSEY PRIMARY | FB |  |  |  |  | -5.9439 | 18.7898 | 18.6816 | 18.348 | 18.2061 | 18.0031 | 17.7816 | 17.548 | 17.2765 | 15.7837 | 13.6194 | 12.1439 | 2.498 | 25.2276 | 24.9724 | 24.5776 | 24.3571 | 23.9724 | 23.5847 | 23.1592 | 22.6388 | 20.099 | 16.8 | 13.4214 | -2.3276 | 21.3337 | 21.1867 | 20.8684 | 20.7653 | 20.5133 | 20.2592 | 19.9724 | 19.5755 | 17.7633 | 15.5714 | 14.0531
LOVEDEAN GSP | CHICHESTER BSP | ROSE GREEN PRIMARY | MINIMUM HEADROOM | SZ 89974 99335 | NO | YES | 7.872 | 10.0819 | 9.6819 | 8.5707 | 7.6452 | 6.6309 | 5.2411 | 3.7748 | 2.1748 | 0.71049 | -3.9048 | -7.2375 | -9.2089 | 11.5421 | 11.4074 | 11.0431 | 10.7085 | 10.338 | 9.8564 | 9.2105 | 8.5564 | 7.9074 | 5.4666 | 3.9187 | 0.67274 | 11.7942 | 11.5319 | 10.7666 | 10.136 | 9.436 | 8.5013 | 7.4942 | 6.3442 | 5.3391 | 1.8462 | -0.23951 | -1.314
|  | ROSE GREEN PRIMARY | EE |  |  |  |  | 10.0819 | 9.6819 | 8.5707 | 7.6585 | 6.6748 | 5.4115 | 4.0462 | 2.5697 | 1.1258 | -3.7242 | -6.4007 | -8.0813 | 11.5442 | 11.4085 | 11.0452 | 10.7125 | 10.3462 | 9.8748 | 9.3289 | 8.6421 | 7.9931 | 5.4666 | 4.0299 | 2.7738 | 11.7942 | 11.5319 | 10.7666 | 10.1442 | 9.4615 | 8.5931 | 7.6421 | 6.5595 | 5.5115 | 2.0105 | 0.24723 | -0.73951
|  | ROSE GREEN PRIMARY | HT |  |  |  |  | 10.0962 | 9.7625 | 8.8615 | 8.0656 | 7.2023 | 5.9972 | 4.587 | 3.1921 | 1.8146 | -3.9048 | -7.2375 | -9.2089 | 11.5472 | 11.4146 | 11.0676 | 10.737 | 10.3687 | 9.8748 | 9.2105 | 8.5564 | 7.9074 | 5.7054 | 4.7778 | 4.4064 | 11.8023 | 11.5748 | 10.9268 | 10.3564 | 9.7319 | 8.8829 | 7.8411 | 6.8187 | 5.8074 | 1.8462 | -0.23951 | -1.314
|  | ROSE GREEN PRIMARY | HE |  |  |  |  | 10.084 | 9.6901 | 8.5778 | 7.6452 | 6.6309 | 5.2411 | 3.7748 | 2.1748 | 0.71049 | -3.463 | -5.9048 | -7.2069 | 11.5421 | 11.4074 | 11.0431 | 10.7085 | 10.338 | 9.8564 | 9.3034 | 8.6003 | 8.036 | 5.688 | 4.1911 | 2.8227 | 11.7962 | 11.535 | 10.7707 | 10.136 | 9.436 | 8.5013 | 7.4942 | 6.3442 | 5.3391 | 2.286 | 0.62682 | -0.20277
|  | ROSE GREEN PRIMARY | FB |  |  |  |  | 10.3472 | 10.1125 | 9.4085 | 8.9911 | 8.5095 | 8.0472 | 7.5605 | 7.0462 | 6.5146 | 3.0942 | 0.89927 | -0.44155 | 11.7023 | 11.537 | 11.235 | 11.0962 | 10.8248 | 10.4901 | 10.1309 | 9.7482 | 9.3503 | 6.7778 | 3.9187 | 0.67274 | 12.0564 | 11.8758 | 11.3809 | 11.1278 | 10.7819 | 10.4309 | 10.0625 | 9.6605 | 9.2462 | 6.637 | 4.834 | 3.7564
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | ROSE HILL PRIMARY | MINIMUM HEADROOM | SP 53637 03027 | NO | NO | 28.21 | -8.8269 | 16.1312 | 15.9445 | 15.4078 | 14.4343 | 12.7323 | 10.7823 | 8.5904 | 6.6353 | 0.10267 | -2.5412 | -3.0504 | -6.3871 | 17.2843 | 17.2016 | 17.0108 | 16.0047 | 14.9241 | 13.6323 | 12.2251 | 10.818 | 6.0445 | 3.4496 | -1.3014 | -7.6484 | 15.5935 | 15.3741 | 14.8996 | 13.9843 | 12.5159 | 10.867 | 8.9435 | 7.2455 | 1.5659 | -0.57999 | -1.3371
|  | ROSE HILL PRIMARY | EE |  |  |  |  | -8.8269 | 16.1312 | 15.9445 | 15.4159 | 14.9496 | 13.2323 | 11.5282 | 9.8414 | 8.0496 | 1.369 | -1.7014 | -2.9626 | -6.3871 | 17.3037 | 17.2363 | 17.0772 | 16.8772 | 15.8578 | 14.6098 | 13.3547 | 12.0139 | 6.4782 | 3.8761 | 1.8772 | -7.6484 | 15.5935 | 15.3741 | 14.9231 | 14.5333 | 13.07 | 11.569 | 10.0772 | 8.4904 | 2.419 | -0.25448 | -1.3371
|  | ROSE HILL PRIMARY | HT |  |  |  |  | -8.7953 | 16.171 | 15.9629 | 15.4078 | 14.4343 | 12.7323 | 10.7823 | 8.5904 | 6.6353 | 0.10267 | -2.5412 | -3.0504 | -6.3861 | 17.2843 | 17.2016 | 17.0108 | 16.0047 | 14.9241 | 13.6323 | 12.2251 | 10.818 | 6.0445 | 4.1925 | 3.8047 | -7.6188 | 15.621 | 15.3874 | 14.8996 | 13.9843 | 12.5159 | 10.867 | 8.9435 | 7.2455 | 1.5659 | -0.57999 | -0.87284
|  | ROSE HILL PRIMARY | HE |  |  |  |  | -8.8167 | 16.1486 | 15.9751 | 15.4567 | 14.9823 | 13.2731 | 11.6333 | 9.8986 | 8.0476 | 2.2567 | -0.076927 | -0.67489 | -6.3861 | 17.3047 | 17.2425 | 17.0853 | 16.8823 | 15.8292 | 14.6027 | 13.268 | 11.8272 | 6.8027 | 4.4659 | 2.8608 | -7.6351 | 15.6129 | 15.4057 | 14.9578 | 14.5547 | 13.0874 | 11.6302 | 10.0782 | 8.4231 | 3.169 | 1.1618 | 0.7292
|  | ROSE HILL PRIMARY | FB |  |  |  |  | -8.6779 | 16.421 | 16.369 | 16.2353 | 15.9251 | 15.3598 | 14.2925 | 13.0823 | 11.9435 | 6.7261 | 3.2782 | 1.3884 | -6.3361 | 17.3863 | 17.3323 | 17.2496 | 17.1404 | 16.7945 | 15.8231 | 14.72 | 13.6823 | 8.2455 | 3.4496 | -1.3014 | -7.4728 | 15.9496 | 15.8037 | 15.6159 | 15.3455 | 14.8925 | 13.9292 | 12.8384 | 11.818 | 6.9414 | 3.6884 | 1.918
MELKSHAM GSP | CHIPPENHAM BSP | ROWDEN PRIMARY | MINIMUM HEADROOM | ST 90805 72608 | NO | YES | 10.667 | 5.116 | 4.1476 | 3.3956 | 2.068 | 0.085347 | -1.6626 | -0.21976 | -2.4759 | -4.8932 | -11.4851 | -14.6912 | -16.3973 | 9.0037 | 8.2047 | 7.9047 | 7.4945 | 6.4139 | 5.8078 | 9.3119 | 8.1109 | 6.7833 | 3.5221 | 1.4282 | -2.581 | 7.2139 | 6.2711 | 5.6935 | 4.6802 | 3.1129 | 1.7915 | 10.1649 | 8.4384 | 6.566 | 1.5221 | -0.78914 | -1.7636
|  | ROWDEN PRIMARY | EE |  |  |  |  | 5.118 | 4.1476 | 3.4027 | 2.1221 | 0.085347 | -1.6626 | -0.16465 | -2.0616 | -4.1167 | -10.3463 | -13.4351 | -15.2687 | 9.0068 | 8.2078 | 7.9129 | 7.5231 | 6.416 | 5.8139 | 9.3119 | 8.3649 | 7.3129 | 3.5221 | 1.5843 | 0.025143 | 7.2139 | 6.2711 | 5.6945 | 4.7262 | 3.1129 | 1.7915 | 10.1874 | 8.7578 | 7.1792 | 2.2333 | -0.11669 | -1.3555
|  | ROWDEN PRIMARY | HT |  |  |  |  | 5.116 | 4.1537 | 3.3956 | 2.068 | 0.53739 | -1.4606 | -0.21976 | -2.4759 | -4.8932 | -11.4851 | -14.6912 | -16.3973 | 9.0037 | 8.2047 | 7.9047 | 7.4945 | 6.9221 | 6.0221 | 9.3333 | 8.1109 | 6.7833 | 3.6007 | 2.3517 | 1.9282 | 7.216 | 6.2894 | 5.6935 | 4.6802 | 3.4813 | 1.967 | 10.1649 | 8.4384 | 6.566 | 1.5221 | -0.78914 | -1.7636
|  | ROWDEN PRIMARY | HE |  |  |  |  | 5.1241 | 4.1619 | 3.42 | 2.1639 | 0.12412 | -1.5963 | -0.050367 | -1.9269 | -3.9514 | -9.5728 | -12.2208 | -13.6187 | 9.0068 | 8.2088 | 7.9129 | 7.5313 | 6.4139 | 5.8078 | 9.3231 | 8.3629 | 7.3017 | 3.8558 | 1.9466 | 0.43229 | 7.2211 | 6.2874 | 5.7149 | 4.7813 | 3.1292 | 1.816 | 10.2558 | 8.8302 | 7.27 | 2.9262 | 0.90371 | -0.011592
|  | ROWDEN PRIMARY | FB |  |  |  |  | 5.3343 | 4.4384 | 4.0109 | 3.2445 | 1.5517 | 0.118 | 2.5925 | 1.6976 | 0.68433 | -3.5432 | -6.2851 | -8.132 | 9.0721 | 8.2476 | 8.0486 | 7.8333 | 6.7323 | 5.8272 | 9.8935 | 9.3843 | 8.6853 | 5.0925 | 1.4282 | -2.581 | 7.3721 | 6.5282 | 6.2241 | 5.717 | 4.3364 | 3.2394 | 12.5129 | 11.8129 | 10.9802 | 7.368 | 4.8119 | 3.0537
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ROWNER PARK PRIMARY | MINIMUM HEADROOM | SU 58018 00782 | NO | YES | 0.296 | 19.1689 | 19.2138 | 19.2199 | 19.1964 | 19.0679 | 18.7821 | 18.4668 | 18.1311 | 17.7791 | 16.2607 | 15.0597 | 14.4577 | 19.9996 | 19.9894 | 19.9424 | 19.9424 | 19.8465 | 19.67 | 19.4731 | 19.2404 | 19.0057 | 17.8333 | 15.3037 | 12.1343 | 19.4502 | 19.4839 | 19.4747 | 19.4094 | 19.2686 | 19.0573 | 18.8155 | 18.5594 | 18.291 | 17.0053 | 16.0727 | 15.5696
|  | ROWNER PARK PRIMARY | EE |  |  |  |  | 19.174 | 19.2281 | 19.2515 | 19.274 | 19.1832 | 18.927 | 18.623 | 18.3005 | 17.9893 | 16.577 | 15.1923 | 14.4577 | 20.0027 | 20.0006 | 19.968 | 19.9935 | 19.9129 | 19.7598 | 19.568 | 19.3639 | 19.1547 | 17.8669 | 16.5486 | 15.169 | 19.4522 | 19.488 | 19.4829 | 19.4431 | 19.3339 | 19.1441 | 18.9165 | 18.6747 | 18.4431 | 17.2308 | 16.1216 | 15.5696
|  | ROWNER PARK PRIMARY | HT |  |  |  |  | 19.1689 | 19.2138 | 19.2199 | 19.1964 | 19.0679 | 18.7821 | 18.4668 | 18.1311 | 17.7791 | 16.2607 | 15.0597 | 14.5689 | 19.9996 | 19.9894 | 19.9424 | 19.9424 | 19.8465 | 19.67 | 19.4731 | 19.2404 | 19.0057 | 18.2169 | 17.6363 | 17.3353 | 19.4502 | 19.4839 | 19.4747 | 19.4094 | 19.2686 | 19.0573 | 18.8155 | 18.5594 | 18.291 | 17.0053 | 16.0727 | 15.7614
|  | ROWNER PARK PRIMARY | HE |  |  |  |  | 19.1832 | 19.2434 | 19.275 | 19.2923 | 19.1944 | 18.9719 | 18.7005 | 18.4056 | 18.123 | 17.0709 | 16.0811 | 15.527 | 20.0047 | 20.0027 | 19.9731 | 19.9986 | 19.919 | 19.77 | 19.5833 | 19.3833 | 19.1812 | 17.9792 | 16.7384 | 15.3751 | 19.4604 | 19.5033 | 19.5063 | 19.4584 | 19.339 | 19.1665 | 18.9594 | 18.7308 | 18.5124 | 17.6084 | 16.792 | 16.3665
|  | ROWNER PARK PRIMARY | FB |  |  |  |  | 19.3036 | 19.4107 | 19.5056 | 19.5821 | 19.6189 | 19.6138 | 19.6393 | 19.5923 | 19.5352 | 18.9719 | 17.724 | 16.9321 | 20.0384 | 20.0384 | 20.02 | 19.9843 | 19.8986 | 19.7527 | 19.6333 | 19.4516 | 19.2547 | 17.8333 | 15.3037 | 12.1343 | 19.5655 | 19.6318 | 19.6767 | 19.69 | 19.6747 | 19.6573 | 19.6318 | 19.5716 | 19.5033 | 18.9614 | 17.9247 | 17.2104
FAWLEY GSP | COWES BSP | RYDE PRIMARY | MINIMUM HEADROOM | SZ 59554 91973 | NO | YES | 4.711 | 8.7729 | 8.6647 | 8.3086 | 7.581 | 6.6473 | 5.282 | 3.7473 | 2.1586 | 0.72286 | -5.2037 | -9.621 | -12.569 | 12.2678 | 12.2269 | 12.0086 | 11.6402 | 11.1341 | 10.4504 | 9.6535 | 8.6739 | 7.8892 | 4.5198 | 1.3861 | -4.2292 | 10.2943 | 10.279 | 10.0229 | 9.4922 | 8.7933 | 7.7504 | 6.6065 | 5.3065 | 4.1922 | -0.38327 | -3.6822 | -5.4527
|  | RYDE PRIMARY | EE |  |  |  |  | 8.7749 | 8.6759 | 8.3494 | 7.6647 | 6.8239 | 5.4024 | 3.981 | 2.3524 | 0.96367 | -4.6567 | -8.8292 | -11.4455 | 12.2688 | 12.2402 | 12.0504 | 11.7402 | 11.329 | 10.6718 | 9.9637 | 9.0331 | 8.329 | 4.5198 | 1.6524 | -0.78837 | 10.2973 | 10.2902 | 10.0627 | 9.582 | 8.9739 | 7.9045 | 6.8096 | 5.5351 | 4.4576 | 0.0065306 | -3.2445 | -5.018
|  | RYDE PRIMARY | HT |  |  |  |  | 8.7769 | 8.6647 | 8.3086 | 7.581 | 6.6473 | 5.2851 | 3.831 | 2.1953 | 0.79122 | -5.2037 | -9.621 | -12.569 | 12.2698 | 12.2269 | 12.0086 | 11.6402 | 11.1341 | 10.4504 | 9.6535 | 8.6739 | 7.8892 | 4.778 | 2.9657 | 2.2076 | 10.2984 | 10.279 | 10.0229 | 9.4922 | 8.7933 | 7.7504 | 6.6065 | 5.3065 | 4.1922 | -0.38327 | -3.6822 | -5.4527
|  | RYDE PRIMARY | HE |  |  |  |  | 8.7729 | 8.6749 | 8.3504 | 7.6188 | 6.7463 | 5.282 | 3.7473 | 2.1586 | 0.72286 | -3.9312 | -7.3822 | -9.2731 | 12.2678 | 12.2392 | 12.0504 | 11.7341 | 11.3239 | 10.6627 | 9.9004 | 9.0361 | 8.33 | 4.8688 | 2.3596 | -0.046531 | 10.2943 | 10.2892 | 10.0647 | 9.5494 | 8.9198 | 7.828 | 6.6576 | 5.4259 | 4.3229 | 0.65347 | -2.0302 | -3.3976
|  | RYDE PRIMARY | FB |  |  |  |  | 9.1402 | 9.1902 | 9.1596 | 8.7882 | 8.4739 | 8.0667 | 7.6412 | 7.1963 | 6.6892 | 3.7259 | 0.58204 | -1.4598 | 12.4596 | 12.428 | 12.3504 | 12.081 | 11.7943 | 11.3555 | 10.8841 | 10.3933 | 9.8484 | 6.3157 | 1.3861 | -4.2292 | 10.6565 | 10.7576 | 10.7871 | 10.5647 | 10.3657 | 10.0616 | 9.7361 | 9.3892 | 8.9831 | 6.5065 | 3.6627 | 1.8871
MANNINGTON GSP | SALISBURY BSP | SALISBURY CENTRAL PRIMARY | MINIMUM HEADROOM | SU 14215 30481 | NO | NO | 13.114 | 21.7442 | 21.7605 | 21.584 | 21.1983 | 20.7218 | 19.8626 | 18.5493 | 17.0412 | 15.3575 | 8.3044 | 3.6238 | 1.9718 | 25.2728 | 25.2452 | 24.9473 | 24.4973 | 23.8708 | 23.1422 | 21.9708 | 20.7646 | 19.5401 | 14.6218 | 11.1044 | 5.5197 | 23.1789 | 23.1912 | 22.9391 | 22.5269 | 21.934 | 21.0544 | 19.5779 | 18.0299 | 16.4544 | 10.1452 | 6.4024 | 5.2656
|  | SALISBURY CENTRAL PRIMARY | EE |  |  |  |  | 21.7452 | 21.7605 | 21.584 | 21.2014 | 20.7463 | 19.8912 | 18.6381 | 17.1259 | 15.6391 | 8.9401 | 4.2636 | 2.2412 | 25.2769 | 25.2514 | 24.9728 | 24.5585 | 23.9503 | 23.2748 | 22.2126 | 21.1789 | 20.1156 | 14.6218 | 11.1044 | 8.8901 | 23.181 | 23.1912 | 22.9391 | 22.533 | 21.9656 | 21.0963 | 19.7708 | 18.3861 | 16.9708 | 10.5993 | 6.685 | 5.2656
|  | SALISBURY CENTRAL PRIMARY | HT |  |  |  |  | 21.7524 | 21.7963 | 21.632 | 21.2208 | 20.732 | 19.8626 | 18.5493 | 17.0412 | 15.3575 | 8.3044 | 3.6238 | 1.9718 | 25.2728 | 25.2463 | 24.9473 | 24.4973 | 23.8708 | 23.1422 | 21.9708 | 20.7646 | 19.5401 | 14.9565 | 12.5044 | 12.1075 | 23.1789 | 23.2126 | 22.9697 | 22.5269 | 21.934 | 21.0544 | 19.5779 | 18.0299 | 16.4544 | 10.1452 | 6.4024 | 5.5208
|  | SALISBURY CENTRAL PRIMARY | HE |  |  |  |  | 21.7442 | 21.7687 | 21.5993 | 21.1983 | 20.7218 | 19.9187 | 18.7534 | 17.3208 | 15.9208 | 10.535 | 7.0963 | 5.3095 | 25.2728 | 25.2452 | 24.9595 | 24.5401 | 23.9126 | 23.231 | 22.2136 | 21.1514 | 20.1003 | 15.383 | 12.533 | 10.1503 | 23.1799 | 23.2034 | 22.9636 | 22.5381 | 21.9371 | 21.1095 | 19.8483 | 18.4871 | 17.132 | 11.9952 | 9.2452 | 7.9228
|  | SALISBURY CENTRAL PRIMARY | FB |  |  |  |  | 21.9105 | 22.0044 | 22.0044 | 21.9156 | 21.8075 | 21.4932 | 21.1259 | 20.7442 | 20.2697 | 17.0503 | 13.4789 | 10.6748 | 25.4105 | 25.3034 | 25.1054 | 24.9075 | 24.6228 | 24.0524 | 23.4146 | 22.8575 | 22.084 | 17.1626 | 11.5881 | 5.5197 | 23.4442 | 23.4565 | 23.4371 | 23.3799 | 23.2728 | 22.9156 | 22.481 | 22.1044 | 21.534 | 17.433 | 13.6432 | 10.9963
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | SANDHURST PRIMARY | MINIMUM HEADROOM | SU 83597 60930 | NO | NO | 2.631 | 7.4541 | 7.5663 | 7.449 | 7.1378 | 6.5551 | 5.6837 | 4.7449 | 3.7071 | 2.7561 | -0.88673 | -3.1469 | -4.0143 | 13.1806 | 13.1378 | 12.9418 | 12.5949 | 11.9082 | 11.0898 | 10.1633 | 9.1459 | 8.2286 | 5.152 | 1.8143 | -4.0418 | 10.3 | 10.3571 | 10.2418 | 9.9439 | 9.2296 | 8.3316 | 7.3449 | 6.2531 | 5.2776 | 1.8122 | 0.015306 | -0.47857
|  | SANDHURST PRIMARY | EE |  |  |  |  | 7.4541 | 7.5663 | 7.5714 | 7.4643 | 7.1347 | 6.451 | 5.6673 | 4.7796 | 3.9561 | 0.60102 | -1.7969 | -2.9786 | 13.1827 | 13.1378 | 13.0133 | 12.7612 | 12.2071 | 11.4888 | 10.6827 | 9.7622 | 8.902 | 5.2633 | 2.8163 | 0.79184 | 10.3 | 10.3571 | 10.3204 | 10.1806 | 9.6582 | 8.8969 | 8.049 | 7.0704 | 6.1714 | 2.851 | 0.81429 | -0.080612
|  | SANDHURST PRIMARY | HT |  |  |  |  | 7.4551 | 7.5694 | 7.449 | 7.1378 | 6.5551 | 5.6837 | 4.7449 | 3.7071 | 2.7561 | -0.88673 | -3.1469 | -4.0143 | 13.1806 | 13.1388 | 12.9418 | 12.5949 | 11.9082 | 11.0898 | 10.1633 | 9.1459 | 8.2286 | 5.152 | 3.749 | 3.3786 | 10.3 | 10.3612 | 10.2418 | 9.9439 | 9.2296 | 8.3316 | 7.3449 | 6.2531 | 5.2776 | 1.8122 | 0.015306 | -0.47857
|  | SANDHURST PRIMARY | HE |  |  |  |  | 7.4582 | 7.5724 | 7.5827 | 7.4612 | 7.1102 | 6.4398 | 5.6592 | 4.7704 | 3.9755 | 1.0092 | -1.15 | -2.0276 | 13.1816 | 13.1378 | 13.0133 | 12.7561 | 12.199 | 11.4806 | 10.6714 | 9.7316 | 8.9082 | 5.4796 | 3.0561 | 1.0071 | 10.3031 | 10.3633 | 10.3306 | 10.1755 | 9.6439 | 8.8857 | 8.0418 | 7.05 | 6.1959 | 3.2357 | 1.4112 | 0.75102
|  | SANDHURST PRIMARY | FB |  |  |  |  | 7.6969 | 8.0276 | 8.2194 | 8.3408 | 8.4265 | 8.3408 | 8.2041 | 8.0143 | 7.7908 | 5.7939 | 2.8592 | 1.2082 | 13.2612 | 13.3408 | 13.2857 | 13.1806 | 12.9847 | 12.6031 | 12.1582 | 11.6796 | 11.1653 | 7.1653 | 1.8143 | -4.0418 | 10.5378 | 10.8112 | 10.9204 | 10.9571 | 10.9449 | 10.8459 | 10.7163 | 10.4786 | 10.1735 | 7.5551 | 4.5112 | 2.902
FAWLEY GSP | COWES BSP | SANDOWN PRIMARY | MINIMUM HEADROOM | SZ 59877 85052 | NO | YES | 4.043 | -0.67553 | -0.74798 | -0.99288 | -1.3449 | -1.8214 | -2.6531 | -3.6378 | -4.6541 | -5.6368 | -9.3602 | -12.4429 | -14.3633 | 2.4291 | 2.3587 | 2.1546 | 1.8811 | 1.5209 | 1.1199 | 0.55151 | -0.036245 | -0.60359 | -2.6352 | -4.2495 | -7.2444 | 0.86171 | 0.80865 | 0.56069 | 0.20967 | -0.25359 | -0.88624 | -1.6862 | -2.5067 | -3.2964 | -6.1924 | -8.2658 | -9.3505
|  | SANDOWN PRIMARY | EE |  |  |  |  | -0.67247 | -0.74288 | -0.96124 | -1.2286 | -1.5561 | -2.297 | -3.198 | -4.1266 | -5.0092 | -8.3868 | -11.2337 | -12.9959 | 2.4331 | 2.3668 | 2.178 | 1.9413 | 1.6525 | 1.3097 | 0.77396 | 0.23008 | -0.28318 | -2.6352 | -4.2495 | -5.5587 | 0.8658 | 0.81376 | 0.58927 | 0.29845 | -0.061755 | -0.61584 | -1.3658 | -2.123 | -2.8444 | -5.6362 | -7.626 | -8.7505
|  | SANDOWN PRIMARY | HT |  |  |  |  | -0.67247 | -0.74798 | -0.99288 | -1.3449 | -1.8214 | -2.6531 | -3.6378 | -4.6541 | -5.6368 | -9.3602 | -12.4429 | -14.3633 | 2.4291 | 2.3587 | 2.1546 | 1.8811 | 1.5209 | 1.1199 | 0.55151 | -0.036245 | -0.60359 | -2.5607 | -3.6342 | -4.0393 | 0.86273 | 0.80865 | 0.56069 | 0.20967 | -0.25359 | -0.88624 | -1.6862 | -2.5067 | -3.2964 | -6.1924 | -8.2658 | -9.3505
|  | SANDOWN PRIMARY | HE |  |  |  |  | -0.67553 | -0.74492 | -0.96227 | -1.2429 | -1.5786 | -2.3633 | -3.2633 | -4.2204 | -5.1184 | -7.9276 | -10.4582 | -11.7714 | 2.4291 | 2.3658 | 2.1791 | 1.9372 | 1.6689 | 1.2882 | 0.78008 | 0.226 | -0.28318 | -2.372 | -3.8485 | -5.0995 | 0.86171 | 0.81273 | 0.58927 | 0.2862 | -0.056653 | -0.65971 | -1.3903 | -2.1669 | -2.8862 | -5.2118 | -6.9342 | -7.7658
|  | SANDOWN PRIMARY | FB |  |  |  |  | -0.52043 | -0.47349 | -0.47859 | -0.42961 | -0.35002 | -0.54186 | -0.70716 | -0.92145 | -1.1296 | -2.7051 | -4.851 | -6.1041 | 2.5076 | 2.4842 | 2.4342 | 2.3944 | 2.3729 | 2.0229 | 1.7372 | 1.425 | 1.1036 | -1.0475 | -4.0954 | -7.2444 | 0.99335 | 1.026 | 1.0566 | 1.0913 | 1.1403 | 0.88314 | 0.68722 | 0.45865 | 0.22804 | -1.4209 | -3.4862 | -4.6424
LOVEDEAN GSP | CHICHESTER BSP | SELSEY PRIMARY | MINIMUM HEADROOM | SZ 85667 94289 | NO | YES | 0.431 | 5.974 | 5.9628 | 5.875 | 5.4954 | 5.0505 | 4.2883 | 3.4964 | 2.6291 | 1.7423 | -1.1199 | -3.5158 | -4.9709 | 6.5939 | 6.5418 | 6.5133 | 6.2582 | 5.95 | 5.6071 | 5.2133 | 4.7714 | 4.3224 | 3.0224 | 2.0714 | -0.26429 | 6.2173 | 6.1714 | 6.1316 | 5.8 | 5.4133 | 4.8398 | 4.2439 | 3.5908 | 2.9245 | 0.85612 | -0.65918 | -1.4541
|  | SELSEY PRIMARY | EE |  |  |  |  | 5.9811 | 6.0128 | 6.026 | 5.7944 | 5.5199 | 4.9015 | 4.1495 | 3.4352 | 2.7342 | 0.27908 | -1.8842 | -3.1821 | 6.598 | 6.5602 | 6.5673 | 6.3592 | 6.1173 | 5.851 | 5.4378 | 5.0653 | 4.7224 | 3.1847 | 2.0714 | 1.1531 | 6.2235 | 6.2061 | 6.2367 | 6.0051 | 5.7337 | 5.2786 | 4.6939 | 4.1561 | 3.6398 | 1.7929 | 0.36122 | -0.41327
|  | SELSEY PRIMARY | HT |  |  |  |  | 5.974 | 5.9628 | 5.875 | 5.4954 | 5.0505 | 4.2883 | 3.4964 | 2.6291 | 1.7423 | -1.1199 | -3.5158 | -4.9709 | 6.5939 | 6.5418 | 6.5133 | 6.2582 | 5.95 | 5.6071 | 5.2133 | 4.7714 | 4.3224 | 3.0224 | 2.3204 | 2.0612 | 6.2173 | 6.1714 | 6.1316 | 5.8 | 5.4133 | 4.8398 | 4.2439 | 3.5908 | 2.9245 | 0.85612 | -0.65918 | -1.4541
|  | SELSEY PRIMARY | HE |  |  |  |  | 5.9842 | 6.0148 | 6.0281 | 5.773 | 5.4689 | 4.8077 | 4.0015 | 3.2628 | 2.4628 | 0.50459 | -1.4321 | -2.3964 | 6.5969 | 6.5612 | 6.5663 | 6.3561 | 6.1051 | 5.8367 | 5.4173 | 5.0755 | 4.6888 | 3.2959 | 2.2816 | 1.3449 | 6.2235 | 6.2082 | 6.2388 | 5.9929 | 5.7 | 5.2255 | 4.6082 | 4.0755 | 3.4878 | 1.9663 | 0.70408 | 0.10918
|  | SELSEY PRIMARY | FB |  |  |  |  | 6.1668 | 6.2434 | 6.3015 | 6.3301 | 6.3474 | 6.3474 | 6.2668 | 6.174 | 6.0464 | 4.8056 | 3.2709 | 2.3393 | 6.7245 | 6.7153 | 6.6837 | 6.6316 | 6.5592 | 6.4816 | 6.3122 | 6.1316 | 5.9316 | 4.2194 | 2.099 | -0.26429 | 6.4031 | 6.4469 | 6.4653 | 6.4704 | 6.4898 | 6.4694 | 6.401 | 6.3112 | 6.1847 | 4.9439 | 3.6449 | 2.8929
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY PRIMARY | MINIMUM HEADROOM | ST 85605 23325 | NO | NO | 2.366 | 11.5953 | 11.5586 | 11.3841 | 11.0229 | 10.5576 | 9.7994 | 8.8504 | 8.0208 | 7.0433 | 3.9576 | 1.8555 | 0.59735 | 12.8345 | 12.7794 | 12.6314 | 12.3273 | 11.9773 | 11.5702 | 10.9549 | 10.4539 | 9.8069 | 7.8794 | 6.7365 | 4.8222 | 12.1137 | 12.0831 | 11.9371 | 11.5627 | 11.129 | 10.5269 | 9.7259 | 9.0565 | 8.2269 | 5.6892 | 4.2024 | 3.4473
|  | SHAFTESBURY PRIMARY | EE |  |  |  |  | 11.5994 | 11.582 | 11.4402 | 11.1647 | 10.83 | 10.1729 | 9.3831 | 8.6535 | 7.8065 | 5.0504 | 3.128 | 1.981 | 12.8396 | 12.8008 | 12.6314 | 12.4008 | 12.1171 | 11.7253 | 11.2243 | 10.7773 | 10.211 | 8.0182 | 6.7365 | 5.7151 | 12.1198 | 12.1106 | 11.9586 | 11.6912 | 11.3524 | 10.7912 | 10.131 | 9.5422 | 8.8157 | 6.4331 | 4.9994 | 4.2157
|  | SHAFTESBURY PRIMARY | HT |  |  |  |  | 11.5953 | 11.5586 | 11.3841 | 11.0229 | 10.5576 | 9.7994 | 8.8504 | 8.0208 | 7.0433 | 3.9576 | 1.8555 | 0.59735 | 12.8345 | 12.7794 | 12.6314 | 12.3273 | 11.9773 | 11.5702 | 10.9549 | 10.4539 | 9.8069 | 7.8794 | 6.958 | 6.6008 | 12.1137 | 12.0831 | 11.9371 | 11.5627 | 11.129 | 10.5269 | 9.7259 | 9.0565 | 8.2269 | 5.6892 | 4.2024 | 3.4473
|  | SHAFTESBURY PRIMARY | HE |  |  |  |  | 11.6014 | 11.5841 | 11.4565 | 11.1647 | 10.8239 | 10.1596 | 9.3494 | 8.6147 | 7.7371 | 5.6524 | 3.9178 | 3.0524 | 12.8396 | 12.8018 | 12.6773 | 12.4161 | 12.1376 | 11.7284 | 11.2151 | 10.7733 | 10.1865 | 8.4641 | 7.258 | 6.3008 | 12.1198 | 12.1116 | 12.0096 | 11.7035 | 11.3729 | 10.7861 | 10.1106 | 9.5167 | 8.7708 | 6.9943 | 5.7137 | 5.128
|  | SHAFTESBURY PRIMARY | FB |  |  |  |  | 11.7127 | 11.7535 | 11.781 | 11.7402 | 11.6963 | 11.5208 | 11.3627 | 11.1984 | 11.0055 | 9.6463 | 7.8249 | 6.6769 | 12.9631 | 12.9498 | 12.9141 | 12.8651 | 12.8457 | 12.5029 | 12.2498 | 12.0008 | 11.6865 | 9.808 | 7.3437 | 4.8222 | 12.3076 | 12.3667 | 12.3912 | 12.3963 | 12.4657 | 12.181 | 11.9973 | 11.8137 | 11.5637 | 10.0943 | 8.4055 | 7.3402
FAWLEY GSP | COWES BSP | SHALFLEET PRIMARY | MINIMUM HEADROOM | SZ 40828 88643 | NO | YES | 0.866 | 8.1209 | 8.1138 | 7.9036 | 7.6954 | 7.4719 | 7.0556 | 6.5658 | 6.0199 | 5.5862 | 4.0138 | 2.5801 | 1.8219 | 9.2296 | 9.2041 | 8.9367 | 8.7724 | 8.6245 | 8.3398 | 7.9827 | 7.6786 | 7.3602 | 6.1673 | 5.2939 | 4.8643 | 8.7255 | 8.7224 | 8.4714 | 8.2612 | 8.0255 | 7.6959 | 7.2908 | 6.8388 | 6.4908 | 5.252 | 4.2378 | 3.852
|  | SHALFLEET PRIMARY | EE |  |  |  |  | 8.1209 | 8.1138 | 7.9056 | 7.7056 | 7.5087 | 7.124 | 6.6505 | 6.1046 | 5.6781 | 4.1046 | 2.7923 | 2.1403 | 9.2306 | 9.2051 | 8.9459 | 8.7908 | 8.6531 | 8.398 | 8.0684 | 7.6786 | 7.3949 | 6.1673 | 5.2939 | 4.8663 | 8.7255 | 8.7224 | 8.4765 | 8.2653 | 8.0449 | 7.7316 | 7.3316 | 6.8622 | 6.5102 | 5.2673 | 4.3776 | 3.9888
|  | SHALFLEET PRIMARY | HT |  |  |  |  | 8.124 | 8.1189 | 7.9087 | 7.6954 | 7.4852 | 7.0638 | 6.5689 | 6.1219 | 5.6434 | 4.0138 | 2.5801 | 1.8219 | 9.2296 | 9.2041 | 8.9388 | 8.7724 | 8.6245 | 8.3398 | 7.9827 | 7.6796 | 7.3602 | 6.1847 | 5.4898 | 5.402 | 8.7265 | 8.7224 | 8.4796 | 8.2663 | 8.0418 | 7.7092 | 7.302 | 6.9429 | 6.5551 | 5.252 | 4.2378 | 3.852
|  | SHALFLEET PRIMARY | HE |  |  |  |  | 8.124 | 8.1199 | 7.9036 | 7.6954 | 7.4719 | 7.0556 | 6.5658 | 6.0199 | 5.5862 | 4.5015 | 3.4015 | 2.8066 | 9.2327 | 9.2071 | 8.9367 | 8.7898 | 8.6418 | 8.3776 | 8.0469 | 7.6786 | 7.4041 | 6.4541 | 5.8429 | 5.3939 | 8.7296 | 8.7276 | 8.4714 | 8.2612 | 8.0255 | 7.6959 | 7.2908 | 6.8388 | 6.4908 | 5.5806 | 4.952 | 4.5694
|  | SHALFLEET PRIMARY | FB |  |  |  |  | 8.223 | 8.2617 | 8.2801 | 8.2842 | 8.1709 | 8.0434 | 7.9342 | 7.874 | 7.7689 | 6.726 | 5.725 | 4.9587 | 9.3378 | 9.3296 | 9.3061 | 9.2929 | 9.0418 | 8.8827 | 8.7378 | 8.65 | 8.5133 | 7.3847 | 6.1561 | 4.8643 | 8.8439 | 8.8847 | 8.8867 | 8.8633 | 8.6 | 8.4816 | 8.3551 | 8.3235 | 8.2102 | 7.2337 | 6.3459 | 5.7133
FAWLEY GSP | COWES BSP | SHANKLIN PRIMARY | MINIMUM HEADROOM | SZ 57809 81912 | NO | YES | 3.733 | 16.2622 | 16.2102 | 16.1286 | 15.8 | 15.2837 | 14.3398 | 13.2786 | 12.1143 | 11.0949 | 6.8 | 3.3031 | 1.298 | 16.4898 | 16.4602 | 16.4143 | 16.2765 | 16.05 | 15.7755 | 15.2612 | 14.5939 | 14.0592 | 11.8949 | 10.1857 | 8.2765 | 15.9561 | 15.948 | 15.9592 | 15.7888 | 15.4643 | 14.7694 | 13.9622 | 13.0612 | 12.298 | 9.1388 | 6.8092 | 5.6765
|  | SHANKLIN PRIMARY | EE |  |  |  |  | 16.2796 | 16.2153 | 16.1806 | 15.9224 | 15.5092 | 14.6204 | 13.6173 | 12.5265 | 11.5735 | 7.6714 | 4.4173 | 2.4316 | 16.4898 | 16.4663 | 16.4327 | 16.3245 | 16.1316 | 15.8959 | 15.4633 | 14.852 | 14.3622 | 11.8949 | 10.1857 | 8.9133 | 15.9561 | 15.95 | 15.9888 | 15.8653 | 15.6276 | 14.9786 | 14.2143 | 13.3704 | 12.6561 | 9.6469 | 7.3724 | 6.0949
|  | SHANKLIN PRIMARY | HT |  |  |  |  | 16.2643 | 16.2102 | 16.1286 | 15.8 | 15.2837 | 14.3398 | 13.2786 | 12.1143 | 11.0949 | 6.8 | 3.3031 | 1.298 | 16.4898 | 16.4602 | 16.4143 | 16.2765 | 16.05 | 15.7755 | 15.2612 | 14.5939 | 14.0592 | 11.9 | 10.6653 | 10.2602 | 15.9582 | 15.948 | 15.9592 | 15.7888 | 15.4643 | 14.7694 | 13.9622 | 13.0612 | 12.298 | 9.1388 | 6.8092 | 5.6765
|  | SHANKLIN PRIMARY | HE |  |  |  |  | 16.2622 | 16.2143 | 16.1786 | 15.8939 | 15.4316 | 14.5347 | 13.498 | 12.3776 | 11.4 | 8.1969 | 5.5673 | 4.0653 | 16.4898 | 16.4663 | 16.4327 | 16.3224 | 16.1235 | 15.8929 | 15.4592 | 14.852 | 14.3724 | 12.2388 | 10.9367 | 9.7092 | 15.9561 | 15.949 | 15.9878 | 15.8449 | 15.5765 | 14.9337 | 14.1541 | 13.301 | 12.5806 | 10.1163 | 8.3745 | 7.3878
|  | SHANKLIN PRIMARY | FB |  |  |  |  | 16.5449 | 16.6816 | 16.5929 | 16.5816 | 16.5602 | 16.4469 | 16.3173 | 16.1133 | 15.8633 | 14.1378 | 11.8235 | 10.4102 | 16.6061 | 16.6724 | 16.6449 | 16.6367 | 16.6071 | 16.4643 | 16.2959 | 16.0837 | 15.8367 | 13.8694 | 11.0602 | 8.2765 | 16.1337 | 16.2347 | 16.2418 | 16.2867 | 16.3173 | 16.2684 | 16.201 | 16.0898 | 15.8867 | 14.3306 | 12.3092 | 11.1071
AXMINSTER GSP | YEOVIL BSP | SHERBORNE PRIMARY | MINIMUM HEADROOM | ST 63978 18163 | NO | NO | 1.363 | 5.8565 | 5.8299 | 5.6401 | 5.3677 | 5.035 | 4.4238 | 3.784 | 3.1024 | 2.4003 | -0.24761 | -2.4323 | -3.5456 | 7.2641 | 7.2345 | 7.0978 | 6.8549 | 6.5366 | 6.1611 | 5.7753 | 5.3264 | 4.8845 | 3.3753 | 2.4519 | 1.4213 | 6.2927 | 6.2529 | 6.0131 | 5.7509 | 5.4172 | 4.908 | 4.3845 | 3.808 | 3.2407 | 1.1733 | -0.43384 | -1.0757
|  | SHERBORNE PRIMARY | EE |  |  |  |  | 5.8667 | 5.8626 | 5.7463 | 5.582 | 5.3922 | 4.9014 | 4.3493 | 3.7871 | 3.2259 | 0.65545 | -1.5221 | -2.5711 | 7.2713 | 7.2549 | 7.1498 | 6.9549 | 6.7039 | 6.406 | 6.0692 | 5.6692 | 5.2978 | 3.7764 | 2.4907 | 1.8345 | 6.3019 | 6.2825 | 6.0907 | 5.907 | 5.6804 | 5.2672 | 4.806 | 4.3182 | 3.8611 | 1.806 | 0.16106 | -0.5022
|  | SHERBORNE PRIMARY | HT |  |  |  |  | 5.8565 | 5.8299 | 5.6401 | 5.3677 | 5.035 | 4.4238 | 3.784 | 3.1024 | 2.4003 | -0.24761 | -2.4323 | -3.5456 | 7.2641 | 7.2345 | 7.0978 | 6.8549 | 6.5366 | 6.1611 | 5.7753 | 5.3264 | 4.8845 | 3.3753 | 2.4519 | 2.407 | 6.2927 | 6.2529 | 6.0131 | 5.7509 | 5.4172 | 4.908 | 4.3845 | 3.808 | 3.2407 | 1.1733 | -0.43384 | -1.0757
|  | SHERBORNE PRIMARY | HE |  |  |  |  | 5.8667 | 5.8626 | 5.7422 | 5.5565 | 5.3687 | 4.8565 | 4.3391 | 3.7738 | 3.2259 | 1.1667 | -0.44557 | -1.3446 | 7.2713 | 7.256 | 7.1498 | 6.9539 | 6.7386 | 6.3917 | 6.0876 | 5.6835 | 5.3243 | 4.0549 | 3.1907 | 2.3917 | 6.3029 | 6.2845 | 6.0886 | 5.8937 | 5.6876 | 5.2366 | 4.8131 | 4.3213 | 3.8774 | 2.2315 | 1.0804 | 0.45392
|  | SHERBORNE PRIMARY | FB |  |  |  |  | 5.9585 | 5.9881 | 6.0085 | 5.9871 | 5.9575 | 5.8146 | 5.684 | 5.5983 | 5.4697 | 4.4381 | 2.9157 | 1.8677 | 7.309 | 7.2988 | 7.2774 | 7.2335 | 7.1753 | 7.0009 | 6.8611 | 6.7549 | 6.5743 | 5.2856 | 3.3927 | 1.4213 | 6.4121 | 6.4366 | 6.4488 | 6.4345 | 6.41 | 6.1478 | 5.9927 | 5.9111 | 5.7753 | 4.7192 | 3.3478 | 2.4049
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE PRIMARY | MINIMUM HEADROOM | SP 03884 19102 | NO | NO | 0.26 | 2.4286 | 2.4357 | 2.4235 | 2.3265 | 2.1602 | 1.9367 | 1.7908 | 1.6745 | 1.4898 | 1.0378 | 0.62245 | 0.38673 | 3.1286 | 3.1347 | 3.1214 | 3.0898 | 3.0327 | 2.9602 | 2.9 | 2.8643 | 2.799 | 2.4408 | 2.2969 | 2.1929 | 3.0031 | 3.0133 | 3 | 2.9296 | 2.8071 | 2.601 | 2.4806 | 2.3939 | 2.2306 | 1.8316 | 1.5694 | 1.4816
|  | SHIPTON OLIFFE PRIMARY | EE |  |  |  |  | 2.4306 | 2.4357 | 2.4296 | 2.3459 | 2.1929 | 2.049 | 1.8571 | 1.7714 | 1.598 | 1.1184 | 0.79184 | 0.60102 | 3.1316 | 3.1357 | 3.1245 | 3.0959 | 3.0429 | 2.9939 | 2.9235 | 2.8939 | 2.8194 | 2.4592 | 2.3051 | 2.1929 | 3.0061 | 3.0143 | 3.0051 | 2.9439 | 2.8143 | 2.6786 | 2.4898 | 2.4255 | 2.2653 | 1.8663 | 1.6612 | 1.5888
|  | SHIPTON OLIFFE PRIMARY | HT |  |  |  |  | 2.4337 | 2.4367 | 2.4235 | 2.3265 | 2.1602 | 1.9367 | 1.7908 | 1.6745 | 1.4898 | 1.0378 | 0.62245 | 0.38673 | 3.1316 | 3.1347 | 3.1214 | 3.0898 | 3.0327 | 2.9602 | 2.9 | 2.8643 | 2.799 | 2.4408 | 2.2969 | 2.3286 | 3.0082 | 3.0133 | 3 | 2.9296 | 2.8071 | 2.601 | 2.4806 | 2.3939 | 2.2306 | 1.8316 | 1.5694 | 1.4816
|  | SHIPTON OLIFFE PRIMARY | HE |  |  |  |  | 2.4286 | 2.4378 | 2.4286 | 2.3388 | 2.2408 | 2.0755 | 1.8398 | 1.7857 | 1.598 | 1.2439 | 0.97857 | 0.78469 | 3.1286 | 3.1357 | 3.1245 | 3.0969 | 3.0663 | 3.001 | 2.9255 | 2.9061 | 2.8439 | 2.5582 | 2.4673 | 2.35 | 3.0031 | 3.0133 | 3.0051 | 2.9388 | 2.8969 | 2.7173 | 2.4888 | 2.4714 | 2.2898 | 1.9786 | 1.849 | 1.7673
|  | SHIPTON OLIFFE PRIMARY | FB |  |  |  |  | 2.4724 | 2.501 | 2.5173 | 2.4694 | 2.4347 | 2.4184 | 2.3939 | 2.3888 | 2.3592 | 2.1714 | 1.9449 | 1.599 | 3.1612 | 3.1755 | 3.1827 | 3.1714 | 3.151 | 3.1408 | 3.1184 | 3.1102 | 3.0857 | 2.9755 | 2.7918 | 2.2571 | 3.0357 | 3.0633 | 3.0827 | 3.0541 | 3.0204 | 3.0102 | 2.9918 | 2.9857 | 2.9806 | 2.8439 | 2.6439 | 2.2949
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | SHIRLEY PRIMARY | MINIMUM HEADROOM | SU 39988 13808 | NO | NO | 9.286 | 7.6847 | 7.4827 | 7.1153 | 6.6204 | 6.0194 | 5.3602 | 4.5469 | 3.5561 | 2.6082 | -1.8469 | -4.5031 | -5.6439 | 10.3827 | 10.2847 | 10.0224 | 9.6235 | 9.1214 | 8.6194 | 8 | 7.2439 | 6.5602 | 3.3755 | -1.2418 | -7.7643 | 8.2735 | 8.0745 | 7.7163 | 7.2745 | 6.7133 | 6.1286 | 5.4235 | 4.5643 | 3.7673 | 0.088776 | -2.0531 | -3.051
|  | SHIRLEY PRIMARY | EE |  |  |  |  | 7.6847 | 7.4827 | 7.1827 | 6.8173 | 6.3653 | 5.5796 | 4.6531 | 3.7337 | 2.9184 | -1.2367 | -4.1408 | -5.6439 | 10.3827 | 10.2918 | 10.0684 | 9.7245 | 9.3 | 8.7735 | 8.1214 | 7.4061 | 6.8071 | 3.3755 | 0.73061 | -1.9347 | 8.2735 | 8.0745 | 7.7408 | 7.4173 | 6.9806 | 6.3204 | 5.5378 | 4.7337 | 4.049 | 0.51837 | -1.8745 | -3.051
|  | SHIRLEY PRIMARY | HT |  |  |  |  | 7.6949 | 7.4837 | 7.1153 | 6.6204 | 6.0194 | 5.3602 | 4.5469 | 3.5561 | 2.6082 | -1.8469 | -4.5031 | -5.6224 | 10.3827 | 10.2847 | 10.0224 | 9.6235 | 9.1214 | 8.6194 | 8 | 7.2439 | 6.5602 | 3.9357 | 2.5357 | 1.8735 | 8.2837 | 8.0827 | 7.7163 | 7.2745 | 6.7133 | 6.1286 | 5.4235 | 4.5643 | 3.7673 | 0.088776 | -2.0531 | -2.8153
|  | SHIRLEY PRIMARY | HE |  |  |  |  | 7.7051 | 7.5224 | 7.2418 | 6.8398 | 6.351 | 5.6337 | 4.7867 | 3.9184 | 3.1612 | 0.018367 | -2.0918 | -3.3408 | 10.3867 | 10.3 | 10.0796 | 9.7347 | 9.3082 | 8.7918 | 8.1684 | 7.4571 | 6.8643 | 3.848 | 1.3847 | -1.2469 | 8.2898 | 8.1061 | 7.7908 | 7.4388 | 6.9755 | 6.3612 | 5.6469 | 4.8724 | 4.2255 | 1.5694 | -0.15306 | -1.1031
|  | SHIRLEY PRIMARY | FB |  |  |  |  | 7.8929 | 7.7918 | 7.6602 | 7.5929 | 7.4122 | 7.0337 | 6.7153 | 6.4296 | 6.0857 | 4.0265 | 1.348 | -0.59898 | 10.451 | 10.4102 | 10.201 | 10.0204 | 9.6837 | 9.0796 | 8.5347 | 8.0418 | 7.451 | 3.9347 | -1.2418 | -7.7643 | 8.4806 | 8.3806 | 8.2531 | 8.2051 | 8.048 | 7.6633 | 7.3622 | 7.099 | 6.7398 | 4.7704 | 2.2745 | 0.47143
MINETY GSP | STRATTON (RESERVE) BSP | SHRIVENHAM PRIMARY | MINIMUM HEADROOM | SU 23782 87902 | NO | NO | 0.238 | 9.2235 | 9.2327 | 9.2276 | 9.101 | 9.0082 | 8.798 | 8.5724 | 8.3337 | 8.1061 | 7.4867 | 7.0959 | 7.0918 | 10.8816 | 10.85 | 10.8082 | 10.6296 | 10.5153 | 10.2918 | 10.0582 | 9.8153 | 9.5847 | 8.8755 | 8.4173 | 7.9173 | 9.6357 | 9.6316 | 9.6153 | 9.4673 | 9.3816 | 9.1827 | 8.9673 | 8.7408 | 8.5276 | 7.9082 | 7.6071 | 7.6357
|  | SHRIVENHAM PRIMARY | EE |  |  |  |  | 9.2714 | 9.2796 | 9.2755 | 9.1949 | 9.1041 | 8.9357 | 8.7153 | 8.4888 | 8.2694 | 7.5663 | 7.1745 | 7.1439 | 10.9122 | 10.8816 | 10.8378 | 10.6786 | 10.5551 | 10.3847 | 10.1531 | 9.9153 | 9.6602 | 8.8755 | 8.4173 | 8.2194 | 9.6714 | 9.6663 | 9.651 | 9.5388 | 9.45 | 9.2878 | 9.0755 | 8.8561 | 8.6286 | 7.999 | 7.6755 | 7.6735
|  | SHRIVENHAM PRIMARY | HT |  |  |  |  | 9.2235 | 9.2327 | 9.2276 | 9.101 | 9.0082 | 8.798 | 8.5724 | 8.3337 | 8.1061 | 7.4867 | 7.0959 | 7.0918 | 10.8816 | 10.85 | 10.8082 | 10.6296 | 10.5153 | 10.2918 | 10.0582 | 9.8153 | 9.5847 | 8.8827 | 8.5276 | 8.5388 | 9.6357 | 9.6316 | 9.6153 | 9.4673 | 9.3816 | 9.1827 | 8.9673 | 8.7408 | 8.5276 | 7.9082 | 7.6071 | 7.6357
|  | SHRIVENHAM PRIMARY | HE |  |  |  |  | 9.2704 | 9.2796 | 9.2755 | 9.1888 | 9.1357 | 8.9622 | 8.7378 | 8.5092 | 8.3143 | 7.6908 | 7.4643 | 7.3653 | 10.9102 | 10.8816 | 10.8367 | 10.6735 | 10.5704 | 10.3969 | 10.1592 | 9.9071 | 9.7082 | 8.9857 | 8.6806 | 8.4122 | 9.6694 | 9.6663 | 9.65 | 9.5337 | 9.4776 | 9.3122 | 9.0939 | 8.8592 | 8.6714 | 8.0837 | 7.9112 | 7.8429
|  | SHRIVENHAM PRIMARY | FB |  |  |  |  | 9.3673 | 9.401 | 9.4163 | 9.4398 | 9.4122 | 9.35 | 9.2694 | 9.2 | 9.1735 | 8.6306 | 8.1184 | 7.8367 | 10.998 | 10.9847 | 10.9531 | 10.9429 | 10.8898 | 10.798 | 10.6837 | 10.5837 | 10.5306 | 9.6459 | 8.749 | 7.9173 | 9.7786 | 9.802 | 9.8092 | 9.8276 | 9.801 | 9.7378 | 9.6571 | 9.5908 | 9.5561 | 8.9724 | 8.4653 | 8.2224
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON PRIMARY | MINIMUM HEADROOM | ST 85356 13659 | NO | NO | 1.734 | 13.6408 | 13.4316 | 13.2469 | 12.7857 | 12.1827 | 11.2622 | 10.3031 | 9.2459 | 8.1469 | 4.9122 | 2.5653 | 1.0898 | 16.4184 | 16.1939 | 16.0898 | 15.8296 | 15.4776 | 15.0082 | 14.4714 | 13.8459 | 13.1816 | 11.3102 | 10.4194 | 9.0704 | 15.1194 | 14.9337 | 14.8061 | 14.4643 | 14.0102 | 13.3276 | 12.5969 | 11.7806 | 10.9245 | 8.4714 | 6.9276 | 6.1296
|  | SHROTON PRIMARY | EE |  |  |  |  | 13.652 | 13.4684 | 13.3673 | 13.0245 | 12.551 | 11.7541 | 10.8459 | 9.998 | 9.0204 | 6.0776 | 4.0255 | 2.7735 | 16.4286 | 16.2173 | 16.1541 | 15.9459 | 15.6418 | 15.2429 | 14.7112 | 14.2316 | 13.6276 | 11.5776 | 10.4194 | 9.5959 | 15.1255 | 14.9561 | 14.8939 | 14.6347 | 14.2663 | 13.6786 | 12.9765 | 12.3255 | 11.5592 | 9.2612 | 7.8429 | 7.0786
|  | SHROTON PRIMARY | HT |  |  |  |  | 13.6408 | 13.4316 | 13.2469 | 12.7857 | 12.1827 | 11.2622 | 10.3031 | 9.2459 | 8.1469 | 4.9122 | 2.5653 | 1.0898 | 16.4184 | 16.1939 | 16.0898 | 15.8296 | 15.4776 | 15.0082 | 14.4714 | 13.8459 | 13.1816 | 11.3102 | 10.4551 | 10.2143 | 15.1194 | 14.9337 | 14.8061 | 14.4643 | 14.0102 | 13.3276 | 12.5969 | 11.7806 | 10.9245 | 8.4714 | 6.9276 | 6.1296
|  | SHROTON PRIMARY | HE |  |  |  |  | 13.652 | 13.4714 | 13.3673 | 13 | 12.5296 | 11.6898 | 10.7367 | 9.8602 | 8.8429 | 6.7224 | 4.752 | 3.6245 | 16.4276 | 16.2163 | 16.149 | 15.9337 | 15.651 | 15.2367 | 14.6939 | 14.2153 | 13.6061 | 11.9969 | 10.9031 | 9.999 | 15.1265 | 14.9622 | 14.8898 | 14.6163 | 14.2612 | 13.6408 | 12.9122 | 12.249 | 11.4582 | 9.7765 | 8.4235 | 7.6867
|  | SHROTON PRIMARY | FB |  |  |  |  | 13.8102 | 13.8582 | 13.8867 | 13.7469 | 13.7143 | 13.5041 | 13.2837 | 13.049 | 12.7959 | 11.0378 | 9.2745 | 7.9745 | 16.55 | 16.5327 | 16.4939 | 16.2888 | 16.2316 | 15.998 | 15.7704 | 15.5204 | 15.248 | 13.4582 | 11.3439 | 9.0704 | 15.2878 | 15.3255 | 15.3429 | 15.2378 | 15.2194 | 15.0429 | 14.8622 | 14.6643 | 14.448 | 12.9469 | 11.4459 | 10.3643
LALEHAM GSP | STAINES BSP | SIDNEY ROAD PRIMARY | MINIMUM HEADROOM | TQ 04100 71760 | NO | NO | 2.658 | 14.021 | 13.7026 | 13.6118 | 13.2159 | 12.7026 | 11.972 | 11.122 | 10.2067 | 9.2935 | 5.2669 | 3.5384 | 2.7088 | 16.7935 | 16.5537 | 16.4465 | 16.1547 | 15.7965 | 15.3312 | 14.772 | 14.1669 | 13.5669 | 11.0026 | 8.769 | 5.3843 | 14.7384 | 14.4537 | 14.3547 | 14.0037 | 13.5557 | 12.9577 | 12.2475 | 11.4598 | 10.7006 | 7.3006 | 5.8863 | 5.269
|  | SIDNEY ROAD PRIMARY | EE |  |  |  |  | 14.021 | 13.7026 | 13.6353 | 13.2679 | 12.7771 | 12.0486 | 11.2128 | 10.2649 | 9.3363 | 5.3526 | 3.5384 | 2.7088 | 16.7975 | 16.5567 | 16.4751 | 16.2088 | 15.8639 | 15.4333 | 14.923 | 14.3128 | 13.7404 | 11.0026 | 9.4975 | 8.1588 | 14.7384 | 14.4537 | 14.371 | 14.0516 | 13.6241 | 13.0445 | 12.3516 | 11.5516 | 10.7975 | 7.3771 | 5.8863 | 5.269
|  | SIDNEY ROAD PRIMARY | HT |  |  |  |  | 14.0251 | 13.7139 | 13.6118 | 13.2159 | 12.7026 | 11.972 | 11.122 | 10.2067 | 9.2935 | 5.2669 | 3.571 | 2.9506 | 16.7935 | 16.5537 | 16.4465 | 16.1547 | 15.7965 | 15.3312 | 14.772 | 14.1669 | 13.5669 | 11.3139 | 10.4822 | 10.2373 | 14.7414 | 14.4649 | 14.3547 | 14.0037 | 13.5557 | 12.9577 | 12.2475 | 11.4598 | 10.7006 | 7.3006 | 5.9577 | 5.5812
|  | SIDNEY ROAD PRIMARY | HE |  |  |  |  | 14.0261 | 13.72 | 13.6547 | 13.271 | 12.7894 | 12.0455 | 11.2343 | 10.3373 | 9.4343 | 5.9537 | 4.5649 | 3.9782 | 16.7955 | 16.5577 | 16.4741 | 16.2026 | 15.8782 | 15.4149 | 14.9118 | 14.3179 | 13.7394 | 11.1547 | 9.7506 | 8.4792 | 14.7435 | 14.4679 | 14.3894 | 14.0547 | 13.6475 | 13.0343 | 12.3577 | 11.5955 | 10.8516 | 7.8557 | 6.7302 | 6.3292
|  | SIDNEY ROAD PRIMARY | FB |  |  |  |  | 14.3577 | 14.1435 | 14.12 | 13.8384 | 13.6312 | 13.3282 | 12.9271 | 12.5588 | 12.0077 | 9.3782 | 7.471 | 6.3649 | 16.9679 | 16.7965 | 16.7016 | 16.4149 | 16.2006 | 15.871 | 15.4557 | 15.069 | 14.5598 | 11.8679 | 8.769 | 5.3843 | 15.1067 | 14.9312 | 14.9047 | 14.5843 | 14.422 | 14.172 | 13.8179 | 13.5026 | 13.021 | 10.6465 | 8.8037 | 7.7445
NURSLING GSP | ROWNHAMS BSP | SILKSTEAD PRIMARY | MINIMUM HEADROOM | SU 44578 24565 | NO | YES | 2.32 | 3.4286 | 3.4469 | 3.4153 | 3.402 | 2.9745 | 2.7633 | 2.3898 | 2.0786 | 1.7561 | 0.72653 | 0.22653 | 0.10612 | 5.4469 | 5.4102 | 5.348 | 5.3184 | 4.8765 | 4.6704 | 4.3051 | 4.0031 | 3.6969 | 2.7204 | 2.2898 | 0.91531 | 2.9755 | 2.9704 | 2.9429 | 2.9469 | 2.5786 | 2.3745 | 2.0194 | 1.7173 | 1.4184 | 0.45714 | 0.0081633 | -0.060204
|  | SILKSTEAD PRIMARY | EE |  |  |  |  | 3.4316 | 3.45 | 3.4265 | 3.4388 | 3.1143 | 2.8745 | 2.6041 | 2.348 | 2.0898 | 1.1 | 0.54796 | 0.36633 | 5.449 | 5.4122 | 5.3582 | 5.349 | 5.001 | 4.75 | 4.4786 | 4.2184 | 3.9622 | 2.9347 | 2.2898 | 1.7806 | 2.9786 | 2.9735 | 2.9541 | 2.9837 | 2.7051 | 2.4755 | 2.2173 | 1.9755 | 1.7296 | 0.78469 | 0.24898 | 0.080612
|  | SILKSTEAD PRIMARY | HT |  |  |  |  | 3.4306 | 3.448 | 3.4153 | 3.402 | 2.9745 | 2.7633 | 2.3898 | 2.0786 | 1.7561 | 0.72653 | 0.22653 | 0.10612 | 5.449 | 5.4122 | 5.348 | 5.3184 | 4.8765 | 4.6704 | 4.3051 | 4.0031 | 3.6969 | 2.7204 | 2.3388 | 2.2939 | 2.9776 | 2.9724 | 2.9429 | 2.9469 | 2.5786 | 2.3745 | 2.0194 | 1.7173 | 1.4184 | 0.45714 | 0.0081633 | -0.060204
|  | SILKSTEAD PRIMARY | HE |  |  |  |  | 3.4286 | 3.4469 | 3.4255 | 3.4378 | 3.1061 | 2.9276 | 2.598 | 2.3735 | 2.1041 | 1.2867 | 0.83878 | 0.68878 | 5.4469 | 5.4102 | 5.3561 | 5.3469 | 4.9969 | 4.802 | 4.4663 | 4.2337 | 3.9602 | 3.0929 | 2.4827 | 1.9714 | 2.9755 | 2.9704 | 2.952 | 2.9806 | 2.699 | 2.5194 | 2.2122 | 1.9878 | 1.7408 | 0.95408 | 0.52041 | 0.37449
|  | SILKSTEAD PRIMARY | FB |  |  |  |  | 3.5459 | 3.5949 | 3.6286 | 3.6429 | 3.6418 | 3.6786 | 3.6245 | 3.5592 | 3.4745 | 2.4847 | 1.6653 | 1.2306 | 5.5378 | 5.5347 | 5.5184 | 5.4878 | 5.4418 | 5.4133 | 5.2939 | 5.1694 | 5.0235 | 3.7286 | 2.3316 | 0.91531 | 3.0959 | 3.1327 | 3.1684 | 3.1939 | 3.201 | 3.1888 | 3.1378 | 3.0776 | 3.0051 | 2.102 | 1.2969 | 0.87449
BRAMLEY (BASI) GSP | READING BSP | SILVER STREET PRIMARY | MINIMUM HEADROOM | SU 71957 72821 | NO | YES | 3.306 | 17.9753 | 18.0212 | 18.0345 | 17.8529 | 17.6784 | 17.1161 | 16.4386 | 15.9253 | 15.4273 | 13.0937 | 10.7273 | 9.4773 | 21.9333 | 21.9231 | 21.8833 | 21.7496 | 21.5996 | 21.3414 | 21.0343 | 20.7567 | 20.4894 | 18.32 | 14.2027 | 8.4578 | 18.5147 | 18.5188 | 18.481 | 18.331 | 18.1269 | 17.7178 | 17.2494 | 16.8627 | 16.4861 | 14.2065 | 12.4259 | 11.4086
|  | SILVER STREET PRIMARY | EE |  |  |  |  | 17.9753 | 18.0437 | 18.0467 | 17.8886 | 17.7427 | 17.1263 | 16.4386 | 15.9253 | 15.4273 | 13.0937 | 10.7273 | 9.4773 | 21.9333 | 21.9445 | 21.9067 | 21.7822 | 21.6445 | 21.371 | 21.0506 | 20.77 | 20.4945 | 18.32 | 15.9914 | 13.6037 | 18.5147 | 18.5198 | 18.481 | 18.331 | 18.1473 | 17.7239 | 17.2494 | 16.8627 | 16.4861 | 14.432 | 12.4259 | 11.4086
|  | SILVER STREET PRIMARY | HT |  |  |  |  | 17.9886 | 18.0212 | 18.0345 | 17.8529 | 17.6784 | 17.1161 | 16.509 | 16.008 | 15.5324 | 13.1518 | 11.2294 | 10.3814 | 21.9343 | 21.9231 | 21.8833 | 21.7496 | 21.5996 | 21.3414 | 21.0343 | 20.7567 | 20.4894 | 19.221 | 18.0445 | 17.3761 | 18.529 | 18.5188 | 18.4943 | 18.3412 | 18.1351 | 17.7178 | 17.2698 | 16.8718 | 16.4861 | 14.2065 | 12.4892 | 11.581
|  | SILVER STREET PRIMARY | HE |  |  |  |  | 17.9957 | 18.0814 | 18.0978 | 17.9304 | 17.7794 | 17.2192 | 16.6018 | 16.1447 | 15.6998 | 14.2222 | 12.9406 | 12.0651 | 21.9343 | 21.9455 | 21.9098 | 21.7853 | 21.6476 | 21.3802 | 21.069 | 20.7965 | 20.5302 | 18.7792 | 16.8761 | 14.6027 | 18.5229 | 18.5331 | 18.5045 | 18.3361 | 18.1269 | 17.7331 | 17.2933 | 16.9331 | 16.58 | 15.1259 | 13.9331 | 13.2127
|  | SILVER STREET PRIMARY | FB |  |  |  |  | 18.0927 | 18.21 | 18.2906 | 18.3222 | 18.31 | 18.0906 | 17.812 | 17.6722 | 17.511 | 16.5386 | 14.7335 | 13.2682 | 21.9588 | 21.972 | 21.9659 | 21.9333 | 21.8547 | 21.7057 | 21.5067 | 21.2057 | 20.8414 | 18.418 | 14.2027 | 8.4578 | 18.6014 | 18.6545 | 18.68 | 18.6606 | 18.6004 | 18.4239 | 18.1994 | 18.0524 | 17.8871 | 16.9984 | 15.7341 | 14.3586
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD PRIMARY | MINIMUM HEADROOM | SZ 18262 93590 | NO | NO | 1.447 | 8.3796 | 8.3449 | 8.199 | 7.5235 | 6.5459 | 4.7827 | 2.8898 | 0.86122 | -1.1633 | -6.7612 | -10.9939 | -12.8184 | 12.4612 | 12.399 | 12.2806 | 11.949 | 11.3827 | 10.5633 | 9.5755 | 8.4459 | 7.2735 | 3.8969 | 1.1112 | -5.1388 | 10.2122 | 10.1245 | 9.9622 | 9.4194 | 8.6082 | 7.3143 | 5.8643 | 4.2714 | 2.6622 | -1.9622 | -4.9878 | -6.0245
|  | SOMERFORD PRIMARY | EE |  |  |  |  | 8.4092 | 8.4398 | 8.4163 | 7.85 | 6.9867 | 5.3837 | 3.652 | 1.799 | -0.066327 | -4.9102 | -8.852 | -10.998 | 12.4765 | 12.4429 | 12.3949 | 12.1163 | 11.6286 | 10.9245 | 10.0469 | 9.0122 | 7.9133 | 3.8969 | 1.1112 | -1.2071 | 10.2286 | 10.1765 | 10.1133 | 9.648 | 8.9337 | 7.7612 | 6.4347 | 4.9755 | 3.4816 | -0.72245 | -3.7204 | -5.2
|  | SOMERFORD PRIMARY | HT |  |  |  |  | 8.3796 | 8.3449 | 8.199 | 7.5235 | 6.5459 | 4.7827 | 2.8898 | 0.86122 | -1.1633 | -6.7612 | -10.9939 | -12.8184 | 12.4612 | 12.399 | 12.2806 | 11.949 | 11.3827 | 10.5633 | 9.5755 | 8.4459 | 7.2735 | 3.9867 | 2.2908 | 1.8755 | 10.2122 | 10.1245 | 9.9622 | 9.4194 | 8.6082 | 7.3143 | 5.8643 | 4.2714 | 2.6622 | -1.9622 | -4.9878 | -6.0245
|  | SOMERFORD PRIMARY | HE |  |  |  |  | 8.4133 | 8.4633 | 8.4143 | 7.8276 | 6.9347 | 5.3806 | 3.6939 | 1.8612 | 0.05 | -3.8245 | -7.1173 | -8.6235 | 12.4755 | 12.4571 | 12.3816 | 12.102 | 11.6092 | 10.9184 | 10.0531 | 9.0122 | 7.9602 | 4.7051 | 2.1112 | -0.28469 | 10.2296 | 10.2051 | 10.1102 | 9.6347 | 8.8939 | 7.7551 | 6.4592 | 5.0122 | 3.5704 | 0.31429 | -2.1663 | -3.2327
|  | SOMERFORD PRIMARY | FB |  |  |  |  | 8.6929 | 8.8429 | 9.1378 | 9.1153 | 8.898 | 8.5265 | 8.1071 | 7.598 | 7.0776 | 4.7459 | 1.4398 | -0.61224 | 12.5367 | 12.5388 | 12.6388 | 12.5765 | 12.3531 | 11.948 | 11.499 | 10.9633 | 10.3806 | 6.7041 | 1.1929 | -5.1388 | 10.4429 | 10.5561 | 10.7684 | 10.7929 | 10.6398 | 10.35 | 10.0092 | 9.5776 | 9.1306 | 6.7929 | 3.6643 | 1.5663
LOVEDEAN GSP | CHICHESTER BSP | SOUTH BERSTED PRIMARY | MINIMUM HEADROOM | SU 94025 00705 | NO | YES | 13.488 | 2.9769 | 3.0463 | 2.9647 | 2.6014 | 2.1514 | 1.1208 | -0.075102 | -1.2129 | -2.4159 | -6.7067 | -10.6833 | -12.7945 | 5.7127 | 5.6596 | 5.5147 | 5.2004 | 4.8045 | 4.2259 | 3.4371 | 2.7127 | 1.879 | -1.0129 | -3.719 | -8.9843 | 4.0851 | 4.1351 | 4.0902 | 3.828 | 3.5014 | 2.7545 | 1.8055 | 0.90449 | -0.078163 | -3.6465 | -6.4282 | -7.7833
|  | SOUTH BERSTED PRIMARY | EE |  |  |  |  | 2.9769 | 3.0463 | 2.9647 | 2.631 | 2.2239 | 1.1892 | 0.019796 | -1.0965 | -2.2608 | -6.52 | -10.3486 | -12.6006 | 5.7167 | 5.6678 | 5.5218 | 5.2167 | 4.8535 | 4.2861 | 3.5463 | 2.8627 | 2.0973 | -1.0129 | -3.4149 | -5.5169 | 4.0851 | 4.1351 | 4.0902 | 3.8494 | 3.5555 | 2.7994 | 1.8678 | 0.97286 | 0.014694 | -3.4424 | -6.2476 | -7.7833
|  | SOUTH BERSTED PRIMARY | HT |  |  |  |  | 2.9851 | 3.0708 | 3.0269 | 2.6994 | 2.2902 | 1.3259 | 0.19327 | -0.89857 | -2.0557 | -6.7067 | -10.6833 | -12.7945 | 5.7157 | 5.6657 | 5.5249 | 5.2024 | 4.8045 | 4.2259 | 3.4371 | 2.7127 | 1.879 | -0.64551 | -2.1465 | -2.7955 | 4.0912 | 4.1565 | 4.128 | 3.8902 | 3.5759 | 2.8555 | 1.9178 | 1.0218 | 0.038163 | -3.6465 | -6.4282 | -7.7098
|  | SOUTH BERSTED PRIMARY | HE |  |  |  |  | 2.981 | 3.0524 | 2.978 | 2.6014 | 2.1514 | 1.1208 | -0.075102 | -1.2129 | -2.4159 | -5.7924 | -8.9618 | -10.7741 | 5.7127 | 5.6596 | 5.5147 | 5.2004 | 4.8259 | 4.278 | 3.5229 | 2.8443 | 2.0708 | -0.71184 | -2.9333 | -5.1761 | 4.0871 | 4.1392 | 4.0943 | 3.828 | 3.5014 | 2.7545 | 1.8055 | 0.90449 | -0.078163 | -2.8465 | -5.1322 | -6.4486
|  | SOUTH BERSTED PRIMARY | FB |  |  |  |  | 3.3463 | 3.5065 | 3.6331 | 3.6157 | 3.5882 | 3.4422 | 3.2708 | 3.032 | 2.778 | 0.90143 | -2.122 | -4.2027 | 5.9769 | 5.9657 | 5.9167 | 5.7147 | 5.5055 | 5.1596 | 4.7943 | 4.3565 | 3.9055 | 0.85755 | -3.719 | -8.9843 | 4.3994 | 4.531 | 4.6249 | 4.6402 | 4.6259 | 4.5116 | 4.3729 | 4.1749 | 3.9504 | 2.1076 | -0.63939 | -2.6006
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE PRIMARY | MINIMUM HEADROOM | SZ 13563 92074 | NO | NO | 5.346 | 7.3051 | 7.4082 | 7.3592 | 7.0296 | 6.6796 | 5.7316 | 4.7296 | 3.6327 | 2.6051 | -1.5102 | -4.4449 | -5.6408 | 9.9061 | 9.9204 | 9.7847 | 9.4173 | 9.0827 | 8.5316 | 7.9031 | 7.1929 | 6.5704 | 3.9653 | -0.10306 | -6.1745 | 8.502 | 8.5204 | 8.4082 | 8.0939 | 7.7224 | 7.0439 | 6.2429 | 5.3235 | 4.502 | 1.1755 | -1.0776 | -1.9163
|  | SOUTHBOURNE PRIMARY | EE |  |  |  |  | 7.3153 | 7.4633 | 7.448 | 7.1663 | 6.9184 | 6.0327 | 5.098 | 4.0633 | 3.0582 | -0.87551 | -3.7786 | -5.3857 | 9.9163 | 9.9571 | 9.848 | 9.4663 | 9.2194 | 8.7622 | 8.2235 | 7.5888 | 6.9969 | 3.9653 | 1.5653 | -0.84184 | 8.5071 | 8.5214 | 8.4082 | 8.1347 | 7.8214 | 7.1673 | 6.4602 | 5.699 | 4.9561 | 1.6633 | -0.64592 | -1.8286
|  | SOUTHBOURNE PRIMARY | HT |  |  |  |  | 7.3051 | 7.4082 | 7.3592 | 7.0296 | 6.6796 | 5.7316 | 4.7296 | 3.6327 | 2.6051 | -1.5102 | -4.4449 | -5.6408 | 9.9061 | 9.9204 | 9.7847 | 9.4173 | 9.0827 | 8.5316 | 7.9031 | 7.1929 | 6.5704 | 4.3286 | 3.0837 | 2.5622 | 8.502 | 8.5204 | 8.4173 | 8.0939 | 7.7224 | 7.0439 | 6.2429 | 5.3235 | 4.502 | 1.1755 | -1.0776 | -1.9163
|  | SOUTHBOURNE PRIMARY | HE |  |  |  |  | 7.3265 | 7.4847 | 7.4776 | 7.1663 | 6.8255 | 6.0541 | 5.2173 | 4.2908 | 3.4031 | 0.31327 | -2.0224 | -3.2602 | 9.9194 | 9.9653 | 9.8561 | 9.5286 | 9.2153 | 8.7704 | 8.2429 | 7.6408 | 7.0888 | 4.3612 | 2.0847 | -0.33571 | 8.5153 | 8.5255 | 8.4337 | 8.1082 | 7.7337 | 7.149 | 6.5 | 5.8 | 5.1367 | 2.6163 | 0.80102 | -0.13469
|  | SOUTHBOURNE PRIMARY | FB |  |  |  |  | 7.5541 | 7.7194 | 7.852 | 7.9673 | 7.9714 | 7.9153 | 7.8245 | 7.7071 | 7.4551 | 5.9122 | 3.2786 | 1.5327 | 10.0224 | 9.9714 | 9.899 | 9.8582 | 9.6673 | 9.3531 | 8.9949 | 8.5949 | 7.9714 | 4.849 | -0.10306 | -6.1745 | 8.7061 | 8.7898 | 8.8265 | 8.7959 | 8.6939 | 8.5765 | 8.4357 | 8.2643 | 8.0041 | 6.5429 | 4.3592 | 2.7459
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | SOUTHCOTE PRIMARY | MINIMUM HEADROOM | SU 68199 71325 | NO | NO | 5.592 | 8.6163 | 8.6663 | 8.6704 | 8.6847 | 8.5388 | 8.298 | 8.0224 | 7.7184 | 7.4265 | 5.999 | 5.1449 | 4.7173 | 10.5551 | 10.5296 | 10.4776 | 10.4398 | 10.2949 | 10.1031 | 9.8449 | 9.5837 | 9.3337 | 7.7224 | 4.8918 | 1.2898 | 9.3204 | 9.3357 | 9.3194 | 9.3194 | 9.1684 | 8.9214 | 8.6337 | 8.3449 | 8.0694 | 6.7378 | 5.9755 | 5.6102
|  | SOUTHCOTE PRIMARY | EE |  |  |  |  | 8.6163 | 8.6704 | 8.6898 | 8.7418 | 8.6265 | 8.3969 | 8.1357 | 7.851 | 7.5776 | 6.1745 | 5.1582 | 4.7173 | 10.5551 | 10.5347 | 10.499 | 10.5071 | 10.3827 | 10.1765 | 9.9357 | 9.6837 | 9.4561 | 7.9102 | 6.6765 | 5.2602 | 9.3204 | 9.3357 | 9.3286 | 9.3633 | 9.2469 | 9.0133 | 8.7378 | 8.4653 | 8.2112 | 6.8684 | 5.9755 | 5.6102
|  | SOUTHCOTE PRIMARY | HT |  |  |  |  | 8.6224 | 8.6663 | 8.6704 | 8.6847 | 8.5388 | 8.298 | 8.0224 | 7.7184 | 7.4265 | 5.999 | 5.1449 | 4.9337 | 10.5551 | 10.5296 | 10.4776 | 10.4684 | 10.3214 | 10.1031 | 9.8449 | 9.5837 | 9.3337 | 8.2796 | 7.7755 | 7.5714 | 9.3286 | 9.3408 | 9.3194 | 9.3194 | 9.1684 | 8.9214 | 8.6337 | 8.3449 | 8.0694 | 6.7378 | 6 | 5.8704
|  | SOUTHCOTE PRIMARY | HE |  |  |  |  | 8.6255 | 8.6918 | 8.7194 | 8.7776 | 8.6653 | 8.4602 | 8.2224 | 7.9541 | 7.7051 | 6.7276 | 5.999 | 5.6327 | 10.5561 | 10.5388 | 10.502 | 10.5122 | 10.3888 | 10.1888 | 9.948 | 9.7031 | 9.4745 | 8.1673 | 6.8918 | 5.4561 | 9.3296 | 9.3582 | 9.3561 | 9.3908 | 9.2694 | 9.052 | 8.7949 | 8.5357 | 8.298 | 7.3714 | 6.7235 | 6.4245
|  | SOUTHCOTE PRIMARY | FB |  |  |  |  | 8.7378 | 8.8469 | 8.9286 | 8.9867 | 8.9786 | 8.9724 | 8.902 | 8.8551 | 8.798 | 8.2306 | 7.0459 | 6.3133 | 10.5776 | 10.5571 | 10.5082 | 10.4398 | 10.2949 | 10.1214 | 9.8786 | 9.648 | 9.4071 | 7.7224 | 4.8918 | 1.2898 | 9.4582 | 9.5357 | 9.5929 | 9.6245 | 9.601 | 9.5796 | 9.4888 | 9.4245 | 9.3316 | 8.6418 | 7.5 | 6.8102
EALING GSP |  | SOUTHFIELD ROAD PRIMARY | MINIMUM HEADROOM | TQ 20533 79746 | NO | NO | 22.497 | 5.8041 | 27.0908 | 27.0224 | 26.7041 | 26.1561 | 25.3286 | 24.3826 | 23.551 | 22.3224 | 17.7643 | 13.6877 | 11.2643 | 12.5847 | 27.9939 | 27.8112 | 27.5357 | 26.951 | 26.3112 | 25.4918 | 24.7367 | 23.6734 | 19.5949 | 11.9102 | -0.11124 | 6.7469 | 25.2806 | 25.2367 | 25.0653 | 24.4908 | 23.7347 | 22.8388 | 22.0408 | 20.8877 | 16.5816 | 12.3786 | 10.0888
|  | SOUTHFIELD ROAD PRIMARY | EE |  |  |  |  | 5.8041 | 27.0908 | 27.0224 | 26.7041 | 26.1683 | 25.3479 | 24.5847 | 23.9388 | 23.0337 | 18.6092 | 13.7296 | 11.2643 | 12.5867 | 28.003 | 27.8837 | 27.5459 | 27.0286 | 26.4112 | 25.7163 | 25.0806 | 24.2092 | 19.5949 | 14.5847 | 9.6449 | 6.7469 | 25.2806 | 25.2367 | 25.0653 | 24.5071 | 23.7612 | 23.0194 | 22.3786 | 21.4877 | 16.9888 | 12.3786 | 10.0888
|  | SOUTHFIELD ROAD PRIMARY | HT |  |  |  |  | 5.8377 | 27.1622 | 27.1357 | 26.802 | 26.1561 | 25.3286 | 24.3826 | 23.551 | 22.3224 | 17.7643 | 13.6877 | 12.2449 | 12.5857 | 28 | 27.8755 | 27.5357 | 26.951 | 26.3112 | 25.4918 | 24.7367 | 23.6734 | 20.7581 | 18.0908 | 16.7837 | 6.7949 | 25.3796 | 25.3877 | 25.153 | 24.4908 | 23.7347 | 22.8388 | 22.0408 | 20.8877 | 16.5816 | 12.9316 | 11.751
|  | SOUTHFIELD ROAD PRIMARY | HE |  |  |  |  | 5.8173 | 27.1214 | 27.0714 | 26.7234 | 26.1571 | 25.4061 | 24.7286 | 24.1163 | 23.3071 | 20.7469 | 17.5612 | 15.8112 | 12.5847 | 28.0051 | 27.8877 | 27.552 | 27.0306 | 26.4326 | 25.7663 | 25.1092 | 24.2796 | 20.4326 | 16.0326 | 11.4653 | 6.7694 | 25.3234 | 25.3041 | 25.0908 | 24.5071 | 23.8163 | 23.1439 | 22.5183 | 21.7112 | 18.999 | 15.9714 | 14.3826
|  | SOUTHFIELD ROAD PRIMARY | FB |  |  |  |  | 6.1183 | 27.5969 | 27.6867 | 27.7194 | 27.5816 | 27.302 | 27.1694 | 27.2622 | 27.1326 | 26.249 | 22.5234 | 19.3357 | 12.5928 | 27.9939 | 27.8112 | 27.6428 | 27.2234 | 26.5867 | 25.9245 | 25.4592 | 24.7714 | 20.4183 | 11.9102 | -0.11124 | 6.8949 | 25.5755 | 25.6847 | 25.7122 | 25.6408 | 25.5388 | 25.3418 | 25.3388 | 25.1194 | 23.7908 | 20.0194 | 16.8081
AXMINSTER GSP | YEOVIL BSP | SPARKFORD PRIMARY | MINIMUM HEADROOM | ST 60767 25496 | NO | NO | 0.755 | 2.6582 | 2.65 | 2.6337 | 2.5939 | 2.4347 | 2.1561 | 1.9837 | 1.8449 | 1.6918 | 1.1173 | 0.64898 | 0.34592 | 3.8582 | 3.848 | 3.8265 | 3.7796 | 3.5367 | 3.35 | 3.2112 | 3.0724 | 2.9602 | 2.4265 | 2.1959 | 2.0816 | 3.3398 | 3.3367 | 3.3235 | 3.2806 | 3.0847 | 2.8388 | 2.6755 | 2.5306 | 2.3847 | 1.8194 | 1.4857 | 1.3306
|  | SPARKFORD PRIMARY | EE |  |  |  |  | 2.6582 | 2.65 | 2.6337 | 2.6071 | 2.4633 | 2.1969 | 2.0306 | 1.9112 | 1.7561 | 1.1173 | 0.64898 | 0.35816 | 3.8582 | 3.85 | 3.8276 | 3.7837 | 3.5959 | 3.3612 | 3.2224 | 3.1235 | 2.9602 | 2.4265 | 2.1959 | 2.0816 | 3.3408 | 3.3367 | 3.3235 | 3.2898 | 3.1286 | 2.8622 | 2.7051 | 2.5816 | 2.4061 | 1.8194 | 1.4857 | 1.3306
|  | SPARKFORD PRIMARY | HT |  |  |  |  | 2.6582 | 2.6541 | 2.6418 | 2.6143 | 2.4347 | 2.2184 | 2.0724 | 1.9316 | 1.7878 | 1.2306 | 0.73163 | 0.34592 | 3.8582 | 3.848 | 3.8265 | 3.7816 | 3.5367 | 3.3643 | 3.2265 | 3.0724 | 2.9633 | 2.452 | 2.2969 | 2.2735 | 3.3398 | 3.3367 | 3.3286 | 3.2918 | 3.0847 | 2.8806 | 2.7316 | 2.5592 | 2.4286 | 1.8745 | 1.549 | 1.3582
|  | SPARKFORD PRIMARY | HE |  |  |  |  | 2.6592 | 2.652 | 2.6337 | 2.5939 | 2.4388 | 2.1561 | 1.9837 | 1.8449 | 1.6918 | 1.2939 | 0.86837 | 0.57449 | 3.8582 | 3.85 | 3.8276 | 3.7796 | 3.5908 | 3.35 | 3.2112 | 3.102 | 2.9724 | 2.5827 | 2.448 | 2.3255 | 3.3408 | 3.3367 | 3.3245 | 3.2806 | 3.1143 | 2.8388 | 2.6755 | 2.5306 | 2.3847 | 1.9949 | 1.7367 | 1.5806
|  | SPARKFORD PRIMARY | FB |  |  |  |  | 2.7041 | 2.7214 | 2.7316 | 2.7255 | 2.6847 | 2.6245 | 2.602 | 2.5551 | 2.5133 | 2.1541 | 1.8041 | 1.5786 | 3.8908 | 3.8949 | 3.8857 | 3.8827 | 3.8449 | 3.8 | 3.7592 | 3.6949 | 3.6469 | 3.0704 | 2.5959 | 2.1378 | 3.3816 | 3.3959 | 3.4041 | 3.402 | 3.3582 | 3.3122 | 3.2898 | 3.2622 | 3.2214 | 2.7602 | 2.3949 | 2.1347
MELKSHAM GSP | NORRINGTON BSP | SPRING QUARRY WEST PRIMARY | MINIMUM HEADROOM | ST 84368 68717 | NO | YES | 0.617 | 20.0653 | 20.0306 | 19.9245 | 19.7612 | 19.6112 | 19.1653 | 18.4551 | 17.6827 | 16.9214 | 13.9061 | 11.6571 | 10.8898 | 19.1459 | 19.1184 | 19.0276 | 18.9327 | 18.85 | 18.702 | 18.1633 | 17.5204 | 16.898 | 14.2786 | 12.4214 | 11.8367 | 19.6612 | 19.6367 | 19.5316 | 19.3898 | 19.2122 | 18.8265 | 18.0969 | 17.3092 | 16.5378 | 13.5153 | 11.4378 | 10.9112
|  | SPRING QUARRY WEST PRIMARY | EE |  |  |  |  | 20.0663 | 20.0949 | 19.9929 | 19.8439 | 19.6367 | 19.2224 | 18.4551 | 17.6827 | 16.9214 | 13.9061 | 11.6571 | 10.8898 | 19.1459 | 19.1439 | 19.0561 | 18.9714 | 18.8704 | 18.7378 | 18.1633 | 17.5204 | 16.898 | 14.2786 | 12.4214 | 11.8367 | 19.6622 | 19.6765 | 19.5714 | 19.4551 | 19.2378 | 18.8816 | 18.0969 | 17.3092 | 16.5378 | 13.5153 | 11.4378 | 10.9112
|  | SPRING QUARRY WEST PRIMARY | HT |  |  |  |  | 20.0663 | 20.0306 | 19.9245 | 19.7612 | 19.6112 | 19.1653 | 18.6898 | 17.999 | 17.3204 | 14.6449 | 12.651 | 11.8735 | 19.1459 | 19.1184 | 19.0276 | 18.9327 | 18.85 | 18.702 | 18.4918 | 17.9643 | 17.4551 | 15.4582 | 14.1459 | 13.9765 | 19.6622 | 19.6367 | 19.5316 | 19.3898 | 19.2122 | 18.8265 | 18.4173 | 17.7439 | 17.0867 | 14.5388 | 12.8245 | 12.3867
|  | SPRING QUARRY WEST PRIMARY | HE |  |  |  |  | 20.0653 | 20.0939 | 20.0133 | 19.8745 | 19.6796 | 19.1796 | 18.7296 | 18.2071 | 17.6673 | 15.9194 | 14.5837 | 13.9398 | 19.1459 | 19.1439 | 19.0612 | 18.9847 | 18.8888 | 18.7347 | 18.5541 | 18.2214 | 17.8837 | 16.5796 | 15.7337 | 15.1449 | 19.6612 | 19.6765 | 19.5847 | 19.4765 | 19.2653 | 18.852 | 18.4653 | 17.9918 | 17.5031 | 15.9112 | 14.8918 | 14.4429
|  | SPRING QUARRY WEST PRIMARY | FB |  |  |  |  | 20.1398 | 20.1878 | 20.2265 | 20.2041 | 20.151 | 20.0255 | 19.951 | 19.8898 | 19.8214 | 18.7939 | 17.5786 | 16.8867 | 19.1939 | 19.1959 | 19.1959 | 19.1694 | 19.1204 | 19.0082 | 18.948 | 18.8673 | 18.7786 | 17.7429 | 16.3755 | 15.0418 | 19.7316 | 19.7582 | 19.7827 | 19.7571 | 19.7173 | 19.6031 | 19.5398 | 19.4776 | 19.3857 | 18.3602 | 17.2143 | 16.5704
NORTH HYDE GSP | NORTH HYDE BSP | SPRINGFIELD ROAD PRIMARY | MINIMUM HEADROOM | TQ 11409 80620 | NO | YES | 1.869 | 14.1614 | 13.8104 | 13.1492 | 14.1318 | 11.3563 | 8.8063 | 6.789 | 4.6196 | 2.8247 | -4.2631 | -10.2967 | -14.0212 | 18.1114 | 17.8083 | 17.3257 | 23.6094 | 22.2278 | 20.8227 | 19.4176 | 17.7369 | 16.2931 | 8.6543 | 2.2788 | -7.4345 | 15.2655 | 14.9818 | 14.4083 | 17.5553 | 15.3727 | 13.391 | 11.5114 | 9.5135 | 7.7665 | 0.43082 | -5.3386 | -8.6886
|  | SPRINGFIELD ROAD PRIMARY | EE |  |  |  |  | 14.1614 | 13.84 | 13.1492 | 14.1318 | 11.3563 | 8.8145 | 6.789 | 4.6196 | 2.8247 | -4.2631 | -10.2967 | -14.0212 | 18.1114 | 17.8645 | 17.3777 | 23.6982 | 22.3094 | 20.9288 | 19.4176 | 17.7369 | 16.2931 | 8.6543 | 2.2788 | -3.3202 | 15.2655 | 15.0053 | 14.4083 | 17.5553 | 15.3727 | 13.391 | 11.5114 | 9.5135 | 7.7665 | 0.43082 | -5.3386 | -8.6886
|  | SPRINGFIELD ROAD PRIMARY | HT |  |  |  |  | 14.1839 | 13.8104 | 13.1645 | 14.3114 | 11.592 | 9.1308 | 7.5308 | 5.4941 | 3.7665 | -3.7671 | -9.2008 | -12.3141 | 18.1124 | 17.8083 | 17.3257 | 23.6094 | 22.2278 | 20.8227 | 19.7869 | 18.2206 | 16.8502 | 11.2053 | 7.4767 | 5.2706 | 15.2839 | 14.9818 | 14.4114 | 17.6176 | 15.4471 | 13.4941 | 12.1267 | 10.2757 | 8.6584 | 1.4186 | -3.5039 | -6.1233
|  | SPRINGFIELD ROAD PRIMARY | HE |  |  |  |  | 14.1716 | 13.8635 | 13.189 | 14.1502 | 11.3757 | 8.8063 | 7.2757 | 5.5033 | 4.1553 | -0.20286 | -3.9386 | -6.6559 | 18.1114 | 17.8655 | 17.3798 | 23.7002 | 22.3522 | 20.938 | 20.0349 | 18.8563 | 17.9237 | 12.6084 | 7.9124 | 2.9859 | 15.2757 | 15.0318 | 14.4481 | 17.5808 | 15.4073 | 13.3992 | 12.1492 | 10.64 | 9.4563 | 5.0461 | 1.6573 | -0.67327
|  | SPRINGFIELD ROAD PRIMARY | FB |  |  |  |  | 14.3247 | 14.1267 | 13.8053 | 15.6849 | 13.5298 | 11.5594 | 10.6971 | 9.7992 | 9.1971 | 5.6869 | 0.71959 | -3.5855 | 18.1328 | 17.8553 | 17.54 | 23.9563 | 22.4808 | 20.9349 | 19.9961 | 19.0451 | 18.2114 | 12.8318 | 4.1155 | -7.4345 | 15.4461 | 15.2941 | 15.0767 | 18.9543 | 17.2624 | 15.638 | 14.941 | 14.1931 | 13.6533 | 10.3512 | 5.741 | 1.8165
NURSLING GSP | WINCHESTER BSP | ST CROSS PRIMARY | MINIMUM HEADROOM | SU 47287 28156 | NO | NO | 2.461 | -6.3446 | -6.5518 | -6.8773 | -7.2089 | -7.6977 | -8.5997 | -9.6854 | -10.863 | -11.915 | -16.014 | -18.8528 | -20.1507 | -0.34971 | -0.63441 | -0.99767 | -1.2324 | -1.5762 | -2.0507 | -2.6926 | -3.4242 | -4.0303 | -6.1232 | -7.1558 | -8.0844 | -4.4048 | -4.6038 | -4.9854 | -5.2844 | -5.712 | -6.4048 | -7.2783 | -8.2232 | -9.0528 | -12.2926 | -14.4232 | -15.2252
|  | ST CROSS PRIMARY | EE |  |  |  |  | -6.3446 | -6.5518 | -6.8599 | -7.0579 | -7.3477 | -8.0773 | -8.9211 | -9.8007 | -10.563 | -14.1722 | -17.0681 | -18.614 | -0.34665 | -0.62727 | -0.97012 | -1.1497 | -1.4069 | -1.7864 | -2.2926 | -2.8864 | -3.3426 | -5.4752 | -6.862 | -7.6252 | -4.4048 | -4.6038 | -4.9854 | -5.1722 | -5.4456 | -6.0058 | -6.6773 | -7.412 | -8.0171 | -10.9967 | -13.2701 | -14.3834
|  | ST CROSS PRIMARY | HT |  |  |  |  | -6.3375 | -6.5354 | -6.8773 | -7.2089 | -7.6977 | -8.5997 | -9.6854 | -10.863 | -11.915 | -16.014 | -18.8528 | -20.1507 | -0.34971 | -0.63237 | -0.99767 | -1.2324 | -1.5762 | -2.0507 | -2.6926 | -3.4242 | -4.0303 | -6.1232 | -7.1558 | -7.3834 | -4.3956 | -4.5864 | -4.9752 | -5.2844 | -5.712 | -6.4048 | -7.2783 | -8.2232 | -9.0528 | -12.2926 | -14.4232 | -15.2252
|  | ST CROSS PRIMARY | HE |  |  |  |  | -6.3354 | -6.5385 | -6.8385 | -7.065 | -7.4048 | -8.0691 | -8.8548 | -9.6926 | -10.4038 | -13.3109 | -15.6467 | -16.8405 | -0.34869 | -0.63441 | -0.97829 | -1.1497 | -1.4252 | -1.8069 | -2.315 | -2.9089 | -3.3691 | -5.1997 | -6.4752 | -7.2109 | -4.3967 | -4.5885 | -4.9671 | -5.164 | -5.4844 | -6.0079 | -6.6487 | -7.3579 | -7.9364 | -10.3048 | -12.1018 | -12.9395
|  | ST CROSS PRIMARY | FB |  |  |  |  | -6.1364 | -6.2507 | -6.3599 | -6.2416 | -6.2395 | -6.316 | -6.5711 | -6.7405 | -6.9364 | -8.8028 | -11.4334 | -13.2252 | -0.23441 | -0.47829 | -0.69359 | -0.63033 | -0.66604 | -0.78135 | -1.0548 | -1.3038 | -1.5762 | -3.4854 | -5.9507 | -8.0844 | -4.1885 | -4.2803 | -4.3742 | -4.2691 | -4.2538 | -4.3364 | -4.7058 | -4.9099 | -5.1375 | -6.8905 | -9.2803 | -10.9058
COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES PRIMARY | MINIMUM HEADROOM | SP 51259 05741 | NO | YES | 4.731 | 8.0994 | 8.2576 | 8.3137 | 7.9913 | 7.1729 | 6.5219 | 5.8066 | 5.1423 | 4.5402 | 3.78 | 2.8566 | 2.6331 | 11.5709 | 11.678 | 11.7035 | 11.5821 | 10.8127 | 10.2239 | 9.5851 | 8.977 | 8.4627 | 7.9556 | 6.8372 | 4.0045 | 9.4025 | 9.4964 | 9.5015 | 9.2872 | 8.5678 | 7.9964 | 7.3943 | 6.7913 | 6.2515 | 5.0872 | 4.0739 | 3.9362
|  | ST EBBES PRIMARY | EE |  |  |  |  | 8.0994 | 8.2576 | 8.326 | 8.0953 | 7.8698 | 7.3311 | 6.726 | 6.227 | 5.7576 | 4.6504 | 3.3402 | 3.0504 | 11.5729 | 11.679 | 11.7198 | 11.6556 | 11.5709 | 11.078 | 10.4923 | 9.978 | 9.5127 | 8.2576 | 7.0107 | 6.1209 | 9.4025 | 9.4964 | 9.5066 | 9.3596 | 9.18 | 8.678 | 8.1198 | 7.6586 | 7.1882 | 5.5647 | 4.2586 | 4.0413
|  | ST EBBES PRIMARY | HT |  |  |  |  | 8.1096 | 8.278 | 8.3137 | 7.9913 | 7.1729 | 6.5219 | 5.8066 | 5.1423 | 4.5402 | 3.78 | 2.8566 | 2.6331 | 11.5709 | 11.678 | 11.7035 | 11.5821 | 10.8127 | 10.2239 | 9.5851 | 8.977 | 8.4627 | 7.9556 | 7.3984 | 7.1402 | 9.4076 | 9.5117 | 9.5015 | 9.2872 | 8.5678 | 7.9964 | 7.3943 | 6.7913 | 6.2515 | 5.0872 | 4.0739 | 3.9362
|  | ST EBBES PRIMARY | HE |  |  |  |  | 8.0994 | 8.2576 | 8.328 | 8.0902 | 7.8617 | 7.3117 | 6.7076 | 6.1943 | 5.7096 | 4.879 | 4.4831 | 4.3158 | 11.5709 | 11.679 | 11.7229 | 11.6586 | 11.576 | 11.0627 | 10.4688 | 9.93 | 9.4423 | 8.4219 | 7.6627 | 6.8025 | 9.4096 | 9.5158 | 9.5341 | 9.3841 | 9.2076 | 8.6964 | 8.1576 | 7.6831 | 7.1943 | 6.1249 | 5.3392 | 5.226
|  | ST EBBES PRIMARY | FB |  |  |  |  | 8.126 | 8.3086 | 8.4239 | 8.2698 | 8.1545 | 8.0729 | 7.6811 | 7.3362 | 7.0698 | 5.9413 | 5.527 | 4.9678 | 11.5739 | 11.6872 | 11.7596 | 11.6943 | 11.6392 | 11.576 | 11.1229 | 10.6902 | 10.3566 | 8.6107 | 6.8372 | 4.0045 | 9.4209 | 9.5402 | 9.6066 | 9.5107 | 9.4484 | 9.3851 | 9.0249 | 8.6913 | 8.4178 | 7.1729 | 6.3504 | 5.4862
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | ST JOHNS PRIMARY | MINIMUM HEADROOM | SU 47113 66363 | NO | NO | 8.28 | -10.4759 | -10.4963 | -10.7239 | -11.13 | -11.5514 | -12.1086 | -12.8902 | -13.7137 | -14.3851 | -16.1086 | -17.0198 | -17.1433 | -4.1933 | -4.2433 | -4.4861 | -5.0525 | -5.5178 | -6.0606 | -6.7729 | -7.528 | -8.1565 | -10.2147 | -13.1035 | -17.2219 | -7.5137 | -7.5484 | -7.7984 | -8.431 | -8.9382 | -9.5229 | -10.2861 | -11.0892 | -11.7382 | -13.6157 | -14.4943 | -14.7239
|  | ST JOHNS PRIMARY | EE |  |  |  |  | -10.4759 | -10.4963 | -10.6749 | -11.0157 | -11.3525 | -11.8331 | -12.4872 | -13.2259 | -13.8392 | -15.58 | -16.7484 | -17.1433 | -4.1933 | -4.2423 | -4.4545 | -4.9688 | -5.3759 | -5.9198 | -6.5106 | -7.2106 | -7.829 | -10.2147 | -11.8076 | -13.1484 | -7.5137 | -7.5484 | -7.7719 | -8.3086 | -8.7453 | -9.3239 | -9.9504 | -10.6882 | -11.3178 | -13.2351 | -14.379 | -14.7239
|  | ST JOHNS PRIMARY | HT |  |  |  |  | -10.4719 | -10.4923 | -10.7239 | -11.13 | -11.5514 | -12.1086 | -12.8902 | -13.7137 | -14.3851 | -16.1086 | -17.0198 | -17.0392 | -4.1933 | -4.2433 | -4.4861 | -5.0525 | -5.5178 | -6.0606 | -6.7729 | -7.528 | -8.1565 | -10.0443 | -10.8157 | -10.8872 | -7.5076 | -7.5402 | -7.7984 | -8.431 | -8.9382 | -9.5229 | -10.2861 | -11.0892 | -11.7382 | -13.6157 | -14.4943 | -14.4453
|  | ST JOHNS PRIMARY | HE |  |  |  |  | -10.4596 | -10.4698 | -10.6361 | -10.9851 | -11.331 | -11.7912 | -12.4698 | -13.1882 | -13.8198 | -15.1525 | -16.0627 | -16.2668 | -4.1902 | -4.2392 | -4.4504 | -4.9657 | -5.381 | -5.8872 | -6.5198 | -7.2096 | -7.8535 | -10.0443 | -11.6198 | -12.9759 | -7.5014 | -7.528 | -7.7443 | -8.2923 | -8.7474 | -9.278 | -9.9443 | -10.6576 | -11.3065 | -12.8239 | -13.727 | -13.8923
|  | ST JOHNS PRIMARY | FB |  |  |  |  | -10.2923 | -10.3065 | -10.381 | -10.428 | -10.577 | -10.8116 | -11.079 | -11.3504 | -11.6719 | -12.7463 | -14.6719 | -15.7576 | -4.0637 | -4.1902 | -4.3514 | -4.4708 | -4.727 | -5.1137 | -5.5412 | -5.9851 | -6.6535 | -9.3035 | -13.1035 | -17.2219 | -7.2974 | -7.3168 | -7.4096 | -7.4555 | -7.6004 | -7.8504 | -8.1392 | -8.4453 | -9.0035 | -10.4759 | -12.4851 | -13.5994
COWLEY GSP | WITNEY BSP | STANDLAKE PRIMARY | MINIMUM HEADROOM | SP 38923 02349 | NO | NO | 1.357 | 7.2857 | 7.3143 | 7.1153 | 7.0357 | 6.899 | 6.8418 | 6.6643 | 6.4582 | 6.25 | 5.5388 | 5.2602 | 5.2102 | 8.1816 | 8.1796 | 8.0806 | 7.9786 | 7.8092 | 7.7306 | 7.5245 | 7.2959 | 7.0602 | 6.2041 | 5.7735 | 5.1929 | 7.6643 | 7.6755 | 7.4459 | 7.3531 | 7.2 | 7.1337 | 6.9439 | 6.7255 | 6.502 | 5.7031 | 5.4173 | 5.3918
|  | STANDLAKE PRIMARY | EE |  |  |  |  | 7.3 | 7.3276 | 7.151 | 7.0857 | 6.9918 | 6.9337 | 6.7796 | 6.5306 | 6.3857 | 5.6867 | 5.398 | 5.2796 | 8.1878 | 8.1847 | 8.0969 | 8.0051 | 7.8714 | 7.7816 | 7.5949 | 7.3184 | 7.1398 | 6.2041 | 5.7735 | 5.4592 | 7.6765 | 7.6857 | 7.4735 | 7.3918 | 7.2806 | 7.2092 | 7.0378 | 6.7745 | 6.6133 | 5.8102 | 5.5133 | 5.4112
|  | STANDLAKE PRIMARY | HT |  |  |  |  | 7.2857 | 7.3143 | 7.1153 | 7.0357 | 6.899 | 6.8418 | 6.6643 | 6.4582 | 6.25 | 5.5388 | 5.2602 | 5.2102 | 8.1816 | 8.1796 | 8.0806 | 7.9786 | 7.8092 | 7.7306 | 7.5245 | 7.2959 | 7.0602 | 6.2122 | 5.899 | 5.8245 | 7.6643 | 7.6755 | 7.4459 | 7.3531 | 7.2 | 7.1337 | 6.9439 | 6.7255 | 6.502 | 5.7031 | 5.4173 | 5.3918
|  | STANDLAKE PRIMARY | HE |  |  |  |  | 7.3 | 7.3265 | 7.151 | 7.0959 | 6.9888 | 6.9551 | 6.7673 | 6.5276 | 6.402 | 5.952 | 5.6949 | 5.5561 | 8.1878 | 8.1837 | 8.0969 | 8.0143 | 7.8673 | 7.8051 | 7.5878 | 7.3153 | 7.1643 | 6.4918 | 6.0918 | 5.7622 | 7.6765 | 7.6837 | 7.4755 | 7.402 | 7.2765 | 7.2316 | 7.0286 | 6.7704 | 6.6357 | 6.1173 | 5.8439 | 5.7184
|  | STANDLAKE PRIMARY | FB |  |  |  |  | 7.3571 | 7.398 | 7.4286 | 7.4541 | 7.4704 | 7.3276 | 7.2949 | 7.2184 | 7.1959 | 6.7224 | 6.249 | 5.7582 | 8.2296 | 8.2378 | 8.2388 | 8.2398 | 8.2388 | 8.1133 | 8.0296 | 7.9051 | 7.8327 | 7.0643 | 6.2316 | 5.1929 | 7.7357 | 7.7551 | 7.7684 | 7.7776 | 7.7857 | 7.6184 | 7.5735 | 7.4878 | 7.448 | 6.9112 | 6.4184 | 5.8724
MINETY GSP | STRATTON (RESERVE) BSP | STANTON FITZWARREN PRIMARY | MINIMUM HEADROOM | SU 17585 90987 | NO | YES | 8.078 | 8.5572 | 7.9358 | 7.7368 | 7.5031 | 7.0531 | 6.4347 | 5.5327 | 4.5123 | 3.4541 | -0.10098 | -1.7704 | -2.4071 | 8.9933 | 8.277 | 8.077 | 7.8198 | 7.3107 | 6.6719 | 5.7474 | 4.6484 | 3.6933 | 0.36576 | -1.4598 | -3.1751 | 8.7133 | 8.0633 | 7.8684 | 7.6388 | 7.1858 | 6.5766 | 5.698 | 4.6296 | 3.6347 | 0.39902 | -1.201 | -1.7714
|  | STANTON FITZWARREN PRIMARY | EE |  |  |  |  | 8.5572 | 8.1327 | 7.7398 | 7.5225 | 7.2256 | 6.7674 | 6.0368 | 5.048 | 4.0919 | -0.069343 | -1.7704 | -2.4071 | 8.9933 | 8.4872 | 8.08 | 7.828 | 7.4719 | 6.9933 | 6.1372 | 5.1107 | 4.2443 | 0.36576 | -1.4598 | -2.5465 | 8.7133 | 8.2582 | 7.8715 | 7.6531 | 7.3592 | 6.9133 | 6.1888 | 5.1378 | 4.249 | 0.39902 | -1.201 | -1.7714
|  | STANTON FITZWARREN PRIMARY | HT |  |  |  |  | 8.5592 | 7.9358 | 7.7368 | 7.5031 | 7.0531 | 6.4347 | 5.5327 | 4.5123 | 3.4541 | -0.10098 | -1.7459 | -2.1449 | 8.9943 | 8.277 | 8.077 | 7.8198 | 7.3107 | 6.6719 | 5.7474 | 4.6484 | 3.6933 | 0.64841 | -0.73628 | -1.0424 | 8.7143 | 8.0633 | 7.8684 | 7.6388 | 7.1858 | 6.5766 | 5.698 | 4.6296 | 3.6347 | 0.41637 | -1.1142 | -1.4183
|  | STANTON FITZWARREN PRIMARY | HE |  |  |  |  | 8.5674 | 8.1531 | 7.7766 | 7.5674 | 7.2184 | 6.75 | 6.0143 | 5.0205 | 4.0337 | 0.25821 | -0.94996 | -1.4316 | 8.9974 | 8.4964 | 8.0943 | 7.8494 | 7.4668 | 6.9698 | 6.1158 | 5.0892 | 4.1954 | 0.66474 | -0.722 | -1.7465 | 8.7205 | 8.2745 | 7.898 | 7.6837 | 7.35 | 6.9 | 6.1654 | 5.1123 | 4.2 | 0.74698 | -0.3122 | -0.72036
|  | STANTON FITZWARREN PRIMARY | FB |  |  |  |  | 8.6837 | 8.3592 | 8.2378 | 7.9643 | 7.7317 | 7.5031 | 7.1715 | 6.7694 | 6.2602 | 2.9194 | 0.87453 | -0.13873 | 9.0841 | 8.6586 | 8.5045 | 8.1709 | 7.9178 | 7.6576 | 7.3096 | 6.8545 | 6.3321 | 2.3954 | -0.60261 | -3.1751 | 8.8419 | 8.4827 | 8.3602 | 8.0807 | 7.8623 | 7.6419 | 7.3276 | 6.9286 | 6.4541 | 3.2643 | 1.2694 | 0.31637
LALEHAM GSP | STAINES BSP | STANWELL PRIMARY | MINIMUM HEADROOM | TQ 06003 72766 | NO | NO | 10.58 | 4.2984 | 4.2882 | 4.2484 | 4.0127 | 3.927 | 3.7341 | 3.0709 | 2.2974 | 1.7096 | -1.0598 | -2.8424 | -3.474 | 5.9351 | 5.9096 | 5.8617 | 5.6035 | 5.4964 | 5.2984 | 4.4698 | 3.5647 | 2.8168 | -0.70465 | -3.0373 | -4.4914 | 5.0188 | 4.98 | 4.9066 | 4.5127 | 4.3739 | 4.1749 | 3.3719 | 2.4821 | 1.7719 | -1.4302 | -3.4108 | -4.0802
|  | STANWELL PRIMARY | EE |  |  |  |  | 4.2984 | 4.2882 | 4.2504 | 4.0413 | 3.9943 | 3.7821 | 3.0709 | 2.2974 | 1.7096 | -1.0598 | -2.8424 | -3.474 | 5.9362 | 5.9127 | 5.8688 | 5.6331 | 5.5484 | 5.3168 | 4.4698 | 3.5647 | 2.8168 | -0.70465 | -3.0373 | -4.4914 | 5.0188 | 4.98 | 4.9066 | 4.5382 | 4.4515 | 4.2035 | 3.3719 | 2.4821 | 1.7719 | -1.4302 | -3.4108 | -4.0802
|  | STANWELL PRIMARY | HT |  |  |  |  | 4.3035 | 4.2994 | 4.2484 | 4.0127 | 3.927 | 3.7341 | 3.4504 | 2.83 | 2.3668 | 0.27902 | -0.91996 | -1.1883 | 5.9351 | 5.9158 | 5.8617 | 5.6035 | 5.4964 | 5.3076 | 5.0137 | 4.3045 | 3.7331 | 1.3831 | 0.082082 | -0.36996 | 5.0249 | 4.9943 | 4.9076 | 4.5127 | 4.3739 | 4.1749 | 3.8902 | 3.1974 | 2.6556 | 0.2678 | -1.072 | -1.37
|  | STANWELL PRIMARY | HE |  |  |  |  | 4.3025 | 4.2943 | 4.2596 | 4.0515 | 3.9831 | 3.779 | 3.5678 | 3.129 | 2.8729 | 1.7484 | 1.0035 | 0.78106 | 5.9351 | 5.9096 | 5.8627 | 5.628 | 5.5249 | 5.2984 | 5.0678 | 4.576 | 4.2362 | 2.5158 | 1.2015 | 0.10963 | 5.0229 | 4.9872 | 4.9188 | 4.5433 | 4.4229 | 4.1933 | 3.9811 | 3.5107 | 3.2137 | 1.9607 | 1.179 | 0.95759
|  | STANWELL PRIMARY | FB |  |  |  |  | 4.3698 | 4.3841 | 4.3749 | 4.3198 | 4.3035 | 4.2556 | 4.1841 | 4.1566 | 4.0137 | 3.4545 | 2.3147 | 1.4882 | 5.9504 | 5.9209 | 5.8658 | 5.7637 | 5.6382 | 5.4566 | 5.2494 | 5.0974 | 4.7637 | 3.326 | 0.89841 | -2.1832 | 5.1168 | 5.1209 | 5.0902 | 5.026 | 4.9902 | 4.9188 | 4.8311 | 4.8035 | 4.4984 | 3.7964 | 2.6556 | 1.8566
MANNINGTON GSP | SALISBURY BSP | STAPLEFORD PRIMARY | MINIMUM HEADROOM | SU 06871 37078 | NO | NO | 1.583 | 9.6126 | 9.6045 | 9.5718 | 9.3086 | 9.1188 | 8.8331 | 8.4739 | 8.1106 | 7.7157 | 6.4402 | 5.2953 | 4.5851 | 8.104 | 8.0785 | 8.0203 | 7.7693 | 7.655 | 7.4836 | 7.2295 | 6.9468 | 6.6907 | 5.8366 | 5.2662 | 4.9652 | 9.4213 | 9.405 | 9.354 | 9.0795 | 8.9438 | 8.6917 | 8.4019 | 8.0652 | 7.7397 | 6.6754 | 5.8887 | 5.5132
|  | STAPLEFORD PRIMARY | EE |  |  |  |  | 9.6126 | 9.6045 | 9.5718 | 9.3086 | 9.1422 | 8.8943 | 8.5249 | 8.2137 | 7.8596 | 6.6239 | 5.629 | 5.2902 | 8.105 | 8.0785 | 8.0213 | 7.7693 | 7.6805 | 7.4968 | 7.2427 | 7.0366 | 6.7907 | 5.8662 | 5.2662 | 5.1132 | 9.4213 | 9.405 | 9.354 | 9.0795 | 8.9693 | 8.7315 | 8.4213 | 8.1662 | 7.8662 | 6.8336 | 6.1101 | 5.9938
|  | STAPLEFORD PRIMARY | HT |  |  |  |  | 9.6167 | 9.6218 | 9.5728 | 9.3565 | 9.1351 | 8.9116 | 8.5177 | 8.1106 | 7.7157 | 6.4402 | 5.2953 | 4.5851 | 8.105 | 8.0795 | 8.0203 | 7.8111 | 7.655 | 7.4978 | 7.2295 | 6.9468 | 6.6907 | 5.8366 | 5.3601 | 5.2489 | 9.4234 | 9.4121 | 9.3632 | 9.1315 | 8.9438 | 8.7427 | 8.4101 | 8.0652 | 7.7397 | 6.6754 | 5.8887 | 5.5132
|  | STAPLEFORD PRIMARY | HE |  |  |  |  | 9.6147 | 9.6096 | 9.579 | 9.3443 | 9.1188 | 8.8331 | 8.4739 | 8.1106 | 7.7351 | 6.8331 | 6.0075 | 5.5535 | 8.104 | 8.0785 | 8.0203 | 7.8172 | 7.6723 | 7.4836 | 7.2509 | 7.0213 | 6.7917 | 5.9836 | 5.5846 | 5.2774 | 9.4234 | 9.406 | 9.357 | 9.1305 | 8.9499 | 8.6917 | 8.4019 | 8.105 | 7.7948 | 6.9989 | 6.4642 | 6.1989
|  | STAPLEFORD PRIMARY | FB |  |  |  |  | 9.7259 | 9.7535 | 9.7637 | 9.7688 | 9.782 | 9.731 | 9.6831 | 9.6045 | 9.4259 | 8.6647 | 7.8759 | 7.3882 | 8.1785 | 8.1601 | 8.1244 | 8.1132 | 8.0815 | 8.0019 | 7.9254 | 7.8417 | 7.6162 | 6.8234 | 5.8591 | 4.9652 | 9.5193 | 9.5305 | 9.5285 | 9.5285 | 9.5203 | 9.4672 | 9.4356 | 9.3805 | 9.1611 | 8.4917 | 7.7825 | 7.3703
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH PRIMARY | MINIMUM HEADROOM | SU 77124 94355 | NO | NO | 5.149 | 3.1709 | 3.1688 | 2.9066 | 2.7107 | 2.3729 | 1.9107 | 1.3464 | 0.77599 | 0.23313 | -1.7271 | -3.2128 | -4.1434 | 5.5255 | 5.4979 | 5.2612 | 5.1663 | 4.9326 | 4.6836 | 4.2908 | 3.9092 | 3.5683 | 2.2051 | 1.3428 | -0.058196 | 4.0551 | 4.0489 | 3.8428 | 3.7143 | 3.4398 | 3.0979 | 2.604 | 2.1285 | 1.6959 | 0.097927 | -0.90003 | -1.4011
|  | STOKENCHURCH PRIMARY | EE |  |  |  |  | 3.1709 | 3.1688 | 2.9066 | 2.7393 | 2.426 | 2.0005 | 1.4403 | 0.88415 | 0.33109 | -1.5322 | -2.9016 | -3.6914 | 5.5255 | 5.4989 | 5.2622 | 5.1836 | 4.9836 | 4.7663 | 4.401 | 4.0367 | 3.6683 | 2.2051 | 1.3428 | 0.72038 | 4.0551 | 4.0489 | 3.8428 | 3.7316 | 3.4796 | 3.1571 | 2.702 | 2.251 | 1.801 | 0.26425 | -0.71942 | -1.2164
|  | STOKENCHURCH PRIMARY | HT |  |  |  |  | 3.1995 | 3.2056 | 2.9597 | 2.7719 | 2.4107 | 1.9658 | 1.3586 | 0.77599 | 0.23823 | -1.7271 | -3.2128 | -4.1434 | 5.5296 | 5.504 | 5.2612 | 5.1663 | 4.9326 | 4.6836 | 4.2908 | 3.9092 | 3.5683 | 2.2377 | 1.6724 | 1.5265 | 4.0724 | 4.0836 | 3.8663 | 3.7357 | 3.4398 | 3.101 | 2.604 | 2.1285 | 1.6959 | 0.097927 | -0.90003 | -1.4011
|  | STOKENCHURCH PRIMARY | HE |  |  |  |  | 3.175 | 3.1739 | 2.9127 | 2.7107 | 2.3729 | 1.9107 | 1.3464 | 0.78007 | 0.23313 | -1.1158 | -2.4118 | -3.0505 | 5.5265 | 5.4979 | 5.2643 | 5.1867 | 4.9755 | 4.7398 | 4.3857 | 4.0296 | 3.6867 | 2.4571 | 1.6561 | 0.9867 | 4.0571 | 4.053 | 3.8459 | 3.7143 | 3.4489 | 3.0979 | 2.6469 | 2.1959 | 1.7592 | 0.59691 | -0.32248 | -0.74595
|  | STOKENCHURCH PRIMARY | FB |  |  |  |  | 3.3331 | 3.3893 | 3.4239 | 3.4046 | 3.378 | 3.3882 | 3.1995 | 3.0403 | 2.9331 | 1.8311 | 0.53823 | -0.1832 | 5.6387 | 5.6398 | 5.6255 | 5.5867 | 5.5316 | 5.4867 | 5.1755 | 4.9663 | 4.8102 | 3.4551 | 1.704 | -0.058196 | 4.2194 | 4.2775 | 4.3061 | 4.3224 | 4.3061 | 4.3071 | 4.102 | 3.953 | 3.8469 | 2.8265 | 1.652 | 1.001
MINETY GSP | STRATTON (RESERVE) BSP | STRATTON PRIMARY | MINIMUM HEADROOM | SU 16998 88837 | NO | YES | 19.329 | 1.8815 | 1.7652 | 1.5734 | 1.0744 | 0.3397 | -0.96234 | -2.5827 | -4.2399 | -5.6103 | -9.8409 | -12.2827 | -13.493 | 4.8499 | 4.5611 | 4.4081 | 4.0377 | 3.4489 | 2.5326 | 1.3632 | 0.10399 | -0.88887 | -3.8634 | -5.7481 | -8.5674 | 2.8989 | 2.7173 | 2.5846 | 2.1897 | 1.5622 | 0.4897 | -0.86744 | -2.2746 | -3.4368 | -7.1154 | -9.2307 | -10.097
|  | STRATTON PRIMARY | EE |  |  |  |  | 1.8815 | 1.7652 | 1.5734 | 1.0826 | 0.51725 | -0.58275 | -1.9868 | -3.6021 | -4.9776 | -9.8409 | -12.2827 | -13.493 | 4.8519 | 4.5611 | 4.4142 | 4.0428 | 3.606 | 2.8805 | 1.8968 | 0.7244 | -0.22662 | -3.8634 | -5.7481 | -6.9032 | 2.8989 | 2.7173 | 2.5846 | 2.1938 | 1.7305 | 0.85399 | -0.3052 | -1.6899 | -2.8481 | -7.1154 | -9.2307 | -10.097
|  | STRATTON PRIMARY | HT |  |  |  |  | 1.8887 | 1.7836 | 1.5979 | 1.106 | 0.3397 | -0.96234 | -2.5827 | -4.2399 | -5.6103 | -9.6766 | -12.0327 | -12.9674 | 4.853 | 4.5622 | 4.4142 | 4.0438 | 3.4489 | 2.5326 | 1.3632 | 0.10399 | -0.88887 | -3.497 | -4.7593 | -4.9552 | 2.907 | 2.7315 | 2.604 | 2.2081 | 1.5622 | 0.4897 | -0.86744 | -2.2746 | -3.4368 | -6.9981 | -9.0338 | -9.6215
|  | STRATTON PRIMARY | HE |  |  |  |  | 1.8866 | 1.7805 | 1.5897 | 1.0744 | 0.49787 | -0.55009 | -1.9276 | -3.5195 | -4.8572 | -9.1746 | -10.947 | -11.843 | 4.8499 | 4.5611 | 4.4081 | 4.0377 | 3.5999 | 2.8826 | 1.8764 | 0.68052 | -0.27356 | -3.6246 | -5.1072 | -6.243 | 2.904 | 2.7315 | 2.6009 | 2.1897 | 1.7173 | 0.87338 | -0.27867 | -1.6603 | -2.7981 | -6.5695 | -8.0297 | -8.6327
|  | STRATTON PRIMARY | FB |  |  |  |  | 2.0938 | 2.1785 | 2.0958 | 1.7458 | 1.5111 | 1.0652 | 0.47031 | -0.2654 | -0.97152 | -4.847 | -7.1297 | -8.8032 | 4.9907 | 4.9591 | 4.8489 | 4.4703 | 4.2744 | 3.8836 | 3.3652 | 2.7101 | 2.0683 | -1.8368 | -5.0542 | -8.5674 | 3.1162 | 3.1775 | 3.1254 | 2.8234 | 2.6713 | 2.3264 | 1.853 | 1.2356 | 0.63868 | -2.8583 | -5.0899 | -6.7613
LALEHAM GSP | STAINES BSP | SUNBURY CROSS PRIMARY | MINIMUM HEADROOM | TQ 10053 69996 | NO | NO | 11.081 | 21.1872 | 21.1209 | 20.9954 | 20.6209 | 19.9362 | 18.8301 | 17.7413 | 16.5158 | 15.2995 | 11.2658 | 8.3403 | 6.8229 | 25.126 | 25.1138 | 25.0168 | 24.7923 | 24.3811 | 23.8035 | 23.0525 | 21.8291 | 20.6025 | 16.1444 | 11.1627 | 2.2811 | 22.3474 | 22.1495 | 21.9158 | 21.5158 | 20.8158 | 19.7423 | 18.6668 | 17.4352 | 16.2005 | 12.0331 | 9.0852 | 7.6791
|  | SUNBURY CROSS PRIMARY | EE |  |  |  |  | 21.1872 | 21.1209 | 20.9954 | 20.6791 | 20.1189 | 19.1423 | 18.1689 | 17.076 | 16.0046 | 11.7474 | 8.3403 | 6.8229 | 25.1291 | 25.1189 | 25.0444 | 24.8423 | 24.5056 | 23.9954 | 23.3423 | 22.2035 | 21.0535 | 16.1444 | 12.2903 | 8.8791 | 22.3474 | 22.1495 | 21.9158 | 21.5627 | 20.9709 | 19.9995 | 19.0056 | 17.8791 | 16.7515 | 12.3352 | 9.0852 | 7.6791
|  | SUNBURY CROSS PRIMARY | HT |  |  |  |  | 21.2087 | 21.1627 | 21.0015 | 20.6209 | 19.9362 | 18.8301 | 17.7413 | 16.5158 | 15.2995 | 11.2658 | 8.6689 | 8.0597 | 25.1301 | 25.1189 | 25.0168 | 24.7923 | 24.3811 | 23.8035 | 23.0525 | 21.8291 | 20.6025 | 16.9107 | 14.8801 | 14.226 | 22.3678 | 22.1913 | 21.928 | 21.5158 | 20.8158 | 19.7423 | 18.6668 | 17.4352 | 16.2005 | 12.0331 | 9.5393 | 9.0444
|  | SUNBURY CROSS PRIMARY | HE |  |  |  |  | 21.2025 | 21.1535 | 21.0454 | 20.7178 | 20.1423 | 19.1974 | 18.2505 | 17.1903 | 16.176 | 13.2331 | 10.8046 | 9.6148 | 25.126 | 25.1138 | 25.0372 | 24.8321 | 24.4933 | 23.9821 | 23.3372 | 22.2015 | 21.0811 | 16.8658 | 13.3056 | 9.9117 | 22.3638 | 22.1791 | 21.9607 | 21.5893 | 20.976 | 20.0352 | 19.0617 | 17.9627 | 16.8842 | 13.726 | 11.3658 | 10.2617
|  | SUNBURY CROSS PRIMARY | FB |  |  |  |  | 21.5933 | 21.925 | 21.9709 | 22.0178 | 21.9719 | 21.7127 | 21.4525 | 21.1995 | 20.9484 | 18.6178 | 14.4729 | 11.3882 | 25.2729 | 25.4138 | 25.426 | 25.3831 | 25.2413 | 24.9689 | 24.6495 | 24.2984 | 23.6168 | 18.7066 | 11.1627 | 2.2811 | 22.725 | 23.0117 | 22.9331 | 22.9087 | 22.7811 | 22.4862 | 22.174 | 21.8587 | 21.5342 | 18.8587 | 14.7005 | 11.6158
FLEET-BRAMLEY GSP | BRACKNELL BSP | SUNNINGHILL PRIMARY | MINIMUM HEADROOM | SU 93757 67606 | NO | NO | 1.551 | 12.9576 | 12.9239 | 12.8963 | 12.7943 | 12.7157 | 12.5004 | 12.2167 | 11.8473 | 11.5076 | 10.2249 | 9.6994 | 9.6933 | 14.4641 | 14.3896 | 14.3141 | 14.1151 | 13.9692 | 13.7059 | 13.3957 | 13.0141 | 12.6712 | 11.3794 | 10.3937 | 8.5427 | 13.2116 | 13.1637 | 13.1208 | 12.9576 | 12.8484 | 12.6086 | 12.3137 | 11.9392 | 11.6004 | 10.2249 | 9.7076 | 9.7198
|  | SUNNINGHILL PRIMARY | EE |  |  |  |  | 12.9576 | 12.9239 | 12.9086 | 12.8127 | 12.7647 | 12.53 | 12.3351 | 12.0504 | 11.8127 | 10.5494 | 9.9208 | 9.7616 | 14.4651 | 14.3916 | 14.3253 | 14.1263 | 14.008 | 13.709 | 13.4702 | 13.1345 | 12.8427 | 11.3794 | 10.6478 | 10.1131 | 13.2116 | 13.1637 | 13.129 | 12.9708 | 12.8933 | 12.6208 | 12.4106 | 12.1004 | 11.8392 | 10.48 | 9.8739 | 9.7331
|  | SUNNINGHILL PRIMARY | HT |  |  |  |  | 12.9596 | 12.9269 | 12.8963 | 12.7943 | 12.7157 | 12.5004 | 12.2167 | 11.8473 | 11.5076 | 10.2249 | 9.6994 | 9.6933 | 14.4641 | 14.3896 | 14.3141 | 14.1151 | 13.9692 | 13.7059 | 13.3957 | 13.0141 | 12.6712 | 11.3814 | 10.9998 | 10.9753 | 13.2127 | 13.1667 | 13.1208 | 12.9576 | 12.8484 | 12.6086 | 12.3137 | 11.9392 | 11.6004 | 10.2249 | 9.7076 | 9.7198
|  | SUNNINGHILL PRIMARY | HE |  |  |  |  | 12.978 | 12.9616 | 12.9647 | 12.8147 | 12.7565 | 12.5667 | 12.3361 | 12.0769 | 11.8535 | 10.8678 | 10.2851 | 10.2096 | 14.4733 | 14.4069 | 14.3508 | 14.1273 | 14.0008 | 13.7529 | 13.4641 | 13.1478 | 12.8682 | 11.5733 | 10.7529 | 10.2171 | 13.2269 | 13.1933 | 13.1739 | 12.9739 | 12.8841 | 12.6688 | 12.4147 | 12.131 | 11.8851 | 10.7892 | 10.2157 | 10.1524
|  | SUNNINGHILL PRIMARY | FB |  |  |  |  | 13.1065 | 13.1382 | 13.1882 | 13.2147 | 13.2698 | 13.332 | 13.3076 | 13.078 | 12.9739 | 12.3218 | 11.1504 | 10.5616 | 14.5641 | 14.5212 | 14.4865 | 14.4406 | 14.3927 | 14.3396 | 14.1957 | 13.8529 | 13.6365 | 12.3569 | 10.3937 | 8.5427 | 13.3596 | 13.379 | 13.4106 | 13.4178 | 13.4453 | 13.4943 | 13.4453 | 13.1576 | 13.031 | 12.2769 | 11.0382 | 10.4678
MELKSHAM GSP | CHIPPENHAM BSP | SUTTON BENGER PRIMARY | MINIMUM HEADROOM | ST 93394 80051 | NO | YES | 9.422 | 1.2576 | 15.3214 | 15.3061 | 15.1806 | 14.9928 | 14.7755 | 14.6265 | 14.3765 | 14.1112 | 13.3244 | 12.65 | 12.1867 | 3.2418 | 16.5285 | 16.4959 | 16.3459 | 16.1387 | 15.9632 | 15.8663 | 15.6989 | 15.4877 | 14.9173 | 14.6571 | 14.3653 | 2.4132 | 16.1449 | 16.1214 | 16.0102 | 15.8183 | 15.6153 | 15.4959 | 15.2724 | 15.0244 | 14.3357 | 13.8826 | 13.6346
|  | SUTTON BENGER PRIMARY | EE |  |  |  |  | 1.2576 | 15.3214 | 15.3061 | 15.254 | 15.0377 | 14.8765 | 14.7102 | 14.5122 | 14.3377 | 13.553 | 12.9418 | 12.5653 | 3.2418 | 16.5295 | 16.4979 | 16.451 | 16.151 | 16.0295 | 15.8765 | 15.7163 | 15.5857 | 14.9765 | 14.6571 | 14.4489 | 2.4132 | 16.1449 | 16.1214 | 16.0898 | 15.8459 | 15.6979 | 15.5275 | 15.3408 | 15.1785 | 14.4918 | 14.0591 | 13.8357
|  | SUTTON BENGER PRIMARY | HT |  |  |  |  | 1.2596 | 15.3244 | 15.3061 | 15.2326 | 14.9928 | 14.7755 | 14.6265 | 14.3765 | 14.1112 | 13.3244 | 12.65 | 12.1867 | 3.2428 | 16.5285 | 16.4959 | 16.4418 | 16.1387 | 15.9632 | 15.8785 | 15.6989 | 15.4877 | 14.9173 | 14.6744 | 14.6173 | 2.4132 | 16.1449 | 16.1214 | 16.0755 | 15.8183 | 15.6153 | 15.4959 | 15.2724 | 15.0244 | 14.3357 | 13.8826 | 13.6346
|  | SUTTON BENGER PRIMARY | HE |  |  |  |  | 1.2596 | 15.3234 | 15.3091 | 15.1806 | 15.0214 | 14.8438 | 14.6642 | 14.4846 | 14.2683 | 13.6877 | 13.1469 | 12.8275 | 3.2428 | 16.5285 | 16.4979 | 16.3459 | 16.1489 | 16.0204 | 15.8663 | 15.752 | 15.5714 | 15.0795 | 14.8938 | 14.7183 | 2.4132 | 16.1449 | 16.1234 | 16.0102 | 15.8367 | 15.6785 | 15.4979 | 15.3449 | 15.1357 | 14.6163 | 14.2938 | 14.1153
|  | SUTTON BENGER PRIMARY | FB |  |  |  |  | 1.328 | 15.4428 | 15.4408 | 15.4224 | 15.4408 | 15.402 | 15.3693 | 15.3275 | 15.2683 | 14.702 | 14.2398 | 13.8622 | 3.2867 | 16.5979 | 16.5775 | 16.5479 | 16.5346 | 16.4755 | 16.4275 | 16.3673 | 16.2877 | 15.5704 | 15.002 | 14.3653 | 2.454 | 16.2142 | 16.2102 | 16.1949 | 16.1887 | 16.1683 | 16.1428 | 16.1112 | 16.0846 | 15.4632 | 15.0336 | 14.6785
IVER 132KV GSP | UPTON BSP | SUTTON LANE PRIMARY | MINIMUM HEADROOM | TQ 02185 78595 | NO | YES | 1.666 | 14.5956 | 14.6119 | 14.517 | 14.3385 | 13.9354 | 13.5803 | 13.2487 | 12.9068 | 12.566 | 11.3232 | 10.3834 | 9.9303 | 16.7058 | 16.6732 | 16.5762 | 16.4232 | 16.1487 | 15.866 | 15.5783 | 15.2854 | 14.9895 | 13.5354 | 11.3354 | 7.9354 | 15.6528 | 15.6589 | 15.5721 | 15.4048 | 15.1313 | 14.7956 | 14.4946 | 14.1732 | 13.8517 | 12.6548 | 11.8007 | 11.416
|  | SUTTON LANE PRIMARY | EE |  |  |  |  | 14.5956 | 14.6119 | 14.517 | 14.3385 | 14.0517 | 13.7466 | 13.3926 | 12.9956 | 12.7242 | 11.3426 | 10.3834 | 9.9303 | 16.7058 | 16.6732 | 16.5772 | 16.4568 | 16.2354 | 15.9874 | 15.6783 | 15.3415 | 15.0956 | 13.5354 | 12.2211 | 10.8497 | 15.6528 | 15.6589 | 15.5721 | 15.4048 | 15.1783 | 14.9436 | 14.6313 | 14.2528 | 13.9956 | 12.6732 | 11.8007 | 11.416
|  | SUTTON LANE PRIMARY | HT |  |  |  |  | 14.6028 | 14.6232 | 14.5334 | 14.3395 | 13.9354 | 13.5803 | 13.2487 | 12.9068 | 12.566 | 11.3232 | 10.5528 | 10.3742 | 16.7058 | 16.6762 | 16.5762 | 16.4538 | 16.1487 | 15.866 | 15.5783 | 15.2854 | 14.9895 | 13.9905 | 13.4272 | 13.1466 | 15.6609 | 15.6772 | 15.5946 | 15.413 | 15.1313 | 14.7956 | 14.4946 | 14.1732 | 13.8517 | 12.6548 | 11.9497 | 11.8119
|  | SUTTON LANE PRIMARY | HE |  |  |  |  | 14.6028 | 14.6232 | 14.5344 | 14.3426 | 14.0385 | 13.7568 | 13.416 | 13.1007 | 12.7701 | 11.7834 | 11.0721 | 10.7119 | 16.7068 | 16.6752 | 16.5803 | 16.4589 | 16.2354 | 15.9926 | 15.6854 | 15.3977 | 15.1017 | 13.6874 | 12.4201 | 11.0109 | 15.6599 | 15.6742 | 15.5915 | 15.4119 | 15.1681 | 14.9456 | 14.6313 | 14.3477 | 14.0283 | 13.0691 | 12.417 | 12.0987
|  | SUTTON LANE PRIMARY | FB |  |  |  |  | 14.7354 | 14.813 | 14.7895 | 14.5966 | 14.3823 | 14.3068 | 14.2721 | 14.215 | 14.1507 | 13.5915 | 12.5181 | 11.5721 | 16.7487 | 16.7089 | 16.615 | 16.4232 | 16.1823 | 16.0038 | 15.8058 | 15.6007 | 15.3783 | 13.8548 | 11.3354 | 7.9354 | 15.7466 | 15.7864 | 15.7609 | 15.6313 | 15.4701 | 15.3915 | 15.3456 | 15.2854 | 15.2181 | 14.6905 | 13.6691 | 12.7772
MANNINGTON GSP | WAREHAM BSP | SWANAGE PRIMARY | MINIMUM HEADROOM | SZ 02010 79296 | NO | YES | 1.205 | 4.0184 | 28.7857 | 28.6265 | 28.2194 | 27.65 | 26.6847 | 25.649 | 24.599 | 23.5286 | 19.6745 | 16.651 | 14.8745 | 6.2786 | 28.802 | 28.5806 | 28.3143 | 27.9704 | 27.4929 | 26.9286 | 26.3418 | 25.7337 | 23.6755 | 21.9745 | 18.9776 | 5.1439 | 28.8786 | 28.6276 | 28.2714 | 27.8143 | 27.0888 | 26.2908 | 25.4704 | 24.6327 | 21.7041 | 19.6469 | 18.5796
|  | SWANAGE PRIMARY | EE |  |  |  |  | 4.0255 | 28.8163 | 28.7143 | 28.4041 | 27.9398 | 27.0939 | 26.1602 | 25.1571 | 24.1551 | 20.6245 | 17.8082 | 16.1357 | 6.2857 | 28.8224 | 28.6255 | 28.3929 | 28.0837 | 27.7061 | 27.2184 | 26.6551 | 26.0959 | 23.6755 | 21.9745 | 20.5796 | 5.152 | 28.9071 | 28.699 | 28.4051 | 28.0245 | 27.4082 | 26.7041 | 25.9214 | 25.1408 | 22.2735 | 20.2112 | 19.0735
|  | SWANAGE PRIMARY | HT |  |  |  |  | 4.0184 | 28.7857 | 28.6265 | 28.2194 | 27.65 | 26.6847 | 25.649 | 24.599 | 23.5286 | 19.6745 | 16.651 | 14.8745 | 6.2786 | 28.802 | 28.5806 | 28.3143 | 27.9704 | 27.4929 | 26.9286 | 26.3418 | 25.7337 | 23.7122 | 22.6 | 22.1316 | 5.1439 | 28.8786 | 28.6276 | 28.2714 | 27.8143 | 27.0888 | 26.2908 | 25.4704 | 24.6327 | 21.7041 | 19.6469 | 18.5796
|  | SWANAGE PRIMARY | HE |  |  |  |  | 4.0286 | 28.8173 | 28.7173 | 28.399 | 27.9173 | 27.0041 | 26.0439 | 25.049 | 24.0265 | 21.2439 | 18.8673 | 17.5918 | 6.2857 | 28.8235 | 28.6316 | 28.4071 | 28.101 | 27.6806 | 27.1908 | 26.6592 | 26.1 | 24.0265 | 22.5133 | 21.149 | 5.1541 | 28.9092 | 28.7061 | 28.4092 | 28.0214 | 27.351 | 26.6327 | 25.8745 | 25.0878 | 22.85 | 21.1541 | 20.2612
|  | SWANAGE PRIMARY | FB |  |  |  |  | 4.1449 | 28.998 | 29.0337 | 28.9949 | 28.9224 | 28.7969 | 28.652 | 28.4561 | 28.1816 | 26.4786 | 24.1357 | 22.798 | 6.3908 | 28.9673 | 28.9276 | 28.8388 | 28.598 | 28.351 | 28.048 | 27.751 | 27.4173 | 25.3112 | 22.1898 | 18.9776 | 5.3418 | 29.1827 | 29.2061 | 29.2 | 29.0163 | 28.8571 | 28.652 | 28.4469 | 28.201 | 26.652 | 24.5102 | 23.2959
MINETY GSP | SWINDON BSP | SWINDON PRIMARY | MINIMUM HEADROOM | SU 12449 86967 | NO | NO | 4.686 | 16.3702 | 16.3824 | 16.1518 | 15.6712 | 14.9069 | 13.1773 | 11.113 | 8.9661 | 7.0212 | -0.62573 | -6.9859 | -10.7012 | 25.2161 | 25.012 | 24.51 | 24.0437 | 23.2355 | 22.012 | 20.4243 | 18.7049 | 17.2008 | 11.5773 | 6.6273 | -2.2737 | 19.8314 | 19.7365 | 19.2896 | 18.7998 | 17.91 | 16.3488 | 14.4335 | 12.3906 | 10.5835 | 4.1345 | -0.69103 | -3.3023
|  | SWINDON PRIMARY | EE |  |  |  |  | 16.3702 | 16.3824 | 16.1518 | 15.6998 | 15.0426 | 13.3784 | 11.4161 | 9.2824 | 7.3192 | -0.62573 | -6.9859 | -10.7012 | 25.2171 | 25.0171 | 24.513 | 24.059 | 23.3906 | 22.2733 | 20.8049 | 19.1375 | 17.6855 | 11.5773 | 7.3447 | 3.6702 | 19.8314 | 19.7365 | 19.2896 | 18.8069 | 18.0651 | 16.5875 | 14.7528 | 12.7416 | 10.9457 | 4.1345 | -0.69103 | -3.3023
|  | SWINDON PRIMARY | HT |  |  |  |  | 16.3865 | 16.41 | 16.1875 | 15.7222 | 14.9069 | 13.1773 | 11.113 | 8.9661 | 7.0212 | -0.34103 | -6.6308 | -9.7808 | 25.2171 | 25.012 | 24.512 | 24.0437 | 23.2355 | 22.012 | 20.4243 | 18.7049 | 17.2008 | 12.7804 | 10.2171 | 9.2202 | 19.8416 | 19.76 | 19.3202 | 18.8141 | 17.91 | 16.3488 | 14.4335 | 12.3906 | 10.5835 | 4.3508 | -0.36654 | -2.3951
|  | SWINDON PRIMARY | HE |  |  |  |  | 16.3814 | 16.4079 | 16.1875 | 15.6712 | 14.962 | 13.4151 | 11.5722 | 9.5294 | 7.659 | 0.91305 | -4.5359 | -7.4502 | 25.2161 | 25.0151 | 24.51 | 24.0498 | 23.3784 | 22.2641 | 20.8161 | 19.1396 | 17.6784 | 12.0151 | 7.8569 | 4.0998 | 19.8416 | 19.762 | 19.3273 | 18.7998 | 18.0171 | 16.6018 | 14.8518 | 12.8835 | 11.1406 | 5.313 | 1.1916 | -0.91756
|  | SWINDON PRIMARY | FB |  |  |  |  | 16.8294 | 17.1855 | 17.359 | 17.4018 | 17.3324 | 16.9763 | 16.5539 | 16.0416 | 15.4335 | 11.411 | 6.0182 | 2.5498 | 25.4967 | 25.5059 | 25.3539 | 25.1396 | 24.7794 | 23.9855 | 23.161 | 22.3059 | 21.2835 | 14.8345 | 6.6273 | -2.2737 | 20.3528 | 20.6059 | 20.7059 | 20.6926 | 20.5855 | 20.0845 | 19.5773 | 19.0182 | 18.3059 | 13.863 | 8.7855 | 5.6967
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | TADLEY PRIMARY | MINIMUM HEADROOM | SU 57753 62717 | NO | NO | 2.203 | 15.5522 | 15.5848 | 15.5042 | 15.3053 | 15.0124 | 14.4593 | 13.8593 | 13.1318 | 12.4889 | 9.8053 | 8.0471 | 7.0165 | 17.2093 | 17.1828 | 17.0226 | 16.8491 | 16.5502 | 16.2022 | 15.7797 | 15.2818 | 14.8869 | 12.6502 | 11.3971 | 9.3889 | 16.0093 | 16.0093 | 15.8502 | 15.6655 | 15.3461 | 14.8879 | 14.3716 | 13.7848 | 13.2573 | 10.7553 | 9.3961 | 8.7032
|  | TADLEY PRIMARY | EE |  |  |  |  | 15.5532 | 15.5869 | 15.5114 | 15.3338 | 15.0512 | 14.5267 | 13.8838 | 13.1318 | 12.4889 | 9.8053 | 8.0471 | 7.0165 | 17.2114 | 17.1848 | 17.0297 | 16.8757 | 16.5879 | 16.2879 | 15.8757 | 15.3359 | 14.9175 | 12.6502 | 11.3971 | 10.493 | 16.0114 | 16.0124 | 15.8583 | 15.693 | 15.3848 | 14.9706 | 14.4348 | 13.7848 | 13.2573 | 10.7553 | 9.3961 | 8.7032
|  | TADLEY PRIMARY | HT |  |  |  |  | 15.5522 | 15.5848 | 15.5042 | 15.3053 | 15.0124 | 14.4593 | 13.8593 | 13.2012 | 12.641 | 10.0491 | 8.1777 | 7.1767 | 17.2093 | 17.1828 | 17.0226 | 16.8491 | 16.5502 | 16.2022 | 15.7797 | 15.2818 | 14.8869 | 12.9961 | 12.0257 | 11.7716 | 16.0093 | 16.0093 | 15.8502 | 15.6655 | 15.3461 | 14.8879 | 14.3716 | 13.7889 | 13.3165 | 10.9502 | 9.5542 | 8.9695
|  | TADLEY PRIMARY | HE |  |  |  |  | 15.5522 | 15.5848 | 15.5104 | 15.3318 | 15.0818 | 14.5297 | 13.8838 | 13.1889 | 12.5379 | 10.4226 | 8.9308 | 8.2726 | 17.2114 | 17.1848 | 17.0297 | 16.8736 | 16.6277 | 16.2818 | 15.8563 | 15.3685 | 14.9328 | 13.0869 | 12.041 | 11.191 | 16.0104 | 16.0104 | 15.8573 | 15.692 | 15.4257 | 14.9685 | 14.4257 | 13.8308 | 13.292 | 11.2981 | 10.2155 | 9.7767
|  | TADLEY PRIMARY | FB |  |  |  |  | 15.7165 | 15.7971 | 15.8634 | 15.9195 | 15.9991 | 15.8002 | 15.6634 | 15.5583 | 15.3675 | 14.1746 | 12.4287 | 11.5216 | 17.3083 | 17.294 | 17.2644 | 17.2267 | 17.2155 | 16.8848 | 16.644 | 16.4481 | 16.141 | 14.4614 | 11.8328 | 9.3889 | 16.1746 | 16.2236 | 16.2604 | 16.2828 | 16.3512 | 16.1002 | 15.9461 | 15.8308 | 15.6042 | 14.4165 | 12.5593 | 11.6338
IVER 132KV GSP | SLOUGH BSP | TAPLOW PRIMARY | MINIMUM HEADROOM | SU 91721 81234 | NO | YES | 0.881 | 15.4255 | 15.5582 | 15.5551 | 15.3816 | 14.9439 | 14.3469 | 13.6408 | 12.9163 | 12.199 | 9.5184 | 7.7041 | 6.9265 | 17.1857 | 17.2276 | 17.1837 | 17.0755 | 16.8643 | 16.5551 | 16.0173 | 15.452 | 14.8867 | 12.4714 | 9.4429 | 4.5041 | 16.0776 | 16.1796 | 16.1429 | 16.0122 | 15.6061 | 15.0908 | 14.4684 | 13.8316 | 13.199 | 10.8888 | 9.4224 | 8.7857
|  | TAPLOW PRIMARY | EE |  |  |  |  | 15.4255 | 15.5582 | 15.5643 | 15.4439 | 15.1745 | 14.5745 | 13.9143 | 13.2102 | 12.5255 | 9.8143 | 7.8071 | 6.9265 | 17.1857 | 17.2276 | 17.1908 | 17.099 | 16.9357 | 16.6929 | 16.1714 | 15.6388 | 15.1071 | 12.4714 | 10.3429 | 8.352 | 16.0776 | 16.1796 | 16.1429 | 16.0531 | 15.8112 | 15.2796 | 14.698 | 14.0786 | 13.4796 | 11.0847 | 9.4224 | 8.7857
|  | TAPLOW PRIMARY | HT |  |  |  |  | 15.4316 | 15.5714 | 15.5551 | 15.3816 | 14.9439 | 14.3469 | 13.6408 | 12.9163 | 12.199 | 9.5184 | 7.7041 | 7.1388 | 17.1857 | 17.2276 | 17.1837 | 17.0755 | 16.8643 | 16.5551 | 16.0173 | 15.452 | 14.8867 | 12.9888 | 11.9051 | 11.5643 | 16.0816 | 16.1939 | 16.1439 | 16.0122 | 15.6061 | 15.0908 | 14.4684 | 13.8316 | 13.199 | 10.8888 | 9.4418 | 9.151
|  | TAPLOW PRIMARY | HE |  |  |  |  | 15.4357 | 15.5776 | 15.5878 | 15.4388 | 15.1357 | 14.5776 | 13.9755 | 13.2898 | 12.6459 | 10.5327 | 9.0847 | 8.4102 | 17.1857 | 17.2276 | 17.1908 | 17.098 | 16.9316 | 16.6969 | 16.2102 | 15.6643 | 15.1398 | 12.7327 | 10.8204 | 8.8112 | 16.0878 | 16.1969 | 16.1633 | 16.0561 | 15.7918 | 15.2908 | 14.7561 | 14.1429 | 13.5704 | 11.6837 | 10.5316 | 10.0388
|  | TAPLOW PRIMARY | FB |  |  |  |  | 15.6663 | 15.8092 | 15.9194 | 16.0612 | 16.098 | 16.0551 | 15.9796 | 15.8571 | 15.7133 | 14.35 | 12.5082 | 11.3776 | 17.2908 | 17.3439 | 17.3663 | 17.3949 | 17.352 | 17.0765 | 16.7612 | 16.4184 | 16.0541 | 13.3888 | 9.4429 | 4.5041 | 16.3306 | 16.4327 | 16.5163 | 16.6316 | 16.651 | 16.6082 | 16.5224 | 16.4031 | 16.2663 | 14.8704 | 13.1194 | 12.051
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON PRIMARY | MINIMUM HEADROOM | ST 94510 07307 | NO | NO | 0.653 | 4.2176 | 4.2063 | 4.1757 | 4.1237 | 4.0329 | 3.9247 | 3.8012 | 3.6808 | 3.5584 | 3.1686 | 2.7359 | 2.4482 | 4.8281 | 4.8189 | 4.8026 | 4.7668 | 4.7015 | 4.5883 | 4.4505 | 4.3444 | 4.2148 | 3.9158 | 3.7403 | 3.4607 | 4.9971 | 4.99 | 4.9655 | 4.9196 | 4.8512 | 4.7737 | 4.6176 | 4.4635 | 4.288 | 3.8349 | 3.5298 | 3.3573
|  | TARRANT RUSHTON PRIMARY | EE |  |  |  |  | 4.2186 | 4.2104 | 4.1869 | 4.1492 | 4.0696 | 3.9737 | 3.8655 | 3.7451 | 3.642 | 3.2073 | 2.8788 | 2.641 | 4.8291 | 4.8219 | 4.8087 | 4.7811 | 4.725 | 4.6281 | 4.526 | 4.375 | 4.3077 | 3.9566 | 3.7403 | 3.5546 | 4.9992 | 4.9951 | 4.9757 | 4.941 | 4.8737 | 4.8196 | 4.7073 | 4.5022 | 4.3971 | 3.9308 | 3.6451 | 3.4727
|  | TARRANT RUSHTON PRIMARY | HT |  |  |  |  | 4.2176 | 4.2063 | 4.1757 | 4.1237 | 4.0329 | 3.9247 | 3.8012 | 3.6808 | 3.5584 | 3.1686 | 2.7359 | 2.4482 | 4.8281 | 4.8189 | 4.8026 | 4.7668 | 4.7015 | 4.5883 | 4.4505 | 4.3444 | 4.2148 | 3.9158 | 3.7546 | 3.6842 | 4.9971 | 4.99 | 4.9655 | 4.9196 | 4.8512 | 4.7737 | 4.6176 | 4.4635 | 4.288 | 3.8349 | 3.5298 | 3.3573
|  | TARRANT RUSHTON PRIMARY | HE |  |  |  |  | 4.2186 | 4.2124 | 4.189 | 4.1502 | 4.0686 | 3.9696 | 3.8624 | 3.7451 | 3.6339 | 3.3298 | 3.0237 | 2.8614 | 4.8291 | 4.8219 | 4.8087 | 4.7811 | 4.7219 | 4.6219 | 4.5189 | 4.3934 | 4.3117 | 4.0485 | 3.8974 | 3.7454 | 5.0002 | 4.9951 | 4.9767 | 4.941 | 4.8737 | 4.8176 | 4.6982 | 4.5237 | 4.4012 | 4.0931 | 3.8951 | 3.7941
|  | TARRANT RUSHTON PRIMARY | FB |  |  |  |  | 4.2471 | 4.2522 | 4.2522 | 4.24 | 4.2278 | 4.2002 | 4.1829 | 4.1645 | 4.1318 | 3.8992 | 3.7339 | 3.5951 | 4.8515 | 4.8495 | 4.8464 | 4.8372 | 4.826 | 4.8046 | 4.7791 | 4.7597 | 4.7301 | 4.2832 | 3.8995 | 3.4607 | 5.0267 | 5.0318 | 5.0318 | 5.0237 | 5.0155 | 4.992 | 4.9696 | 4.9522 | 4.9247 | 4.6818 | 4.3829 | 4.1563
MANNINGTON GSP | SALISBURY BSP | TEFFONT PRIMARY | MINIMUM HEADROOM | ST 99837 30994 | NO | NO | 0.476 | 3.0714 | 3.0673 | 3.0388 | 2.8071 | 2.6214 | 2.3541 | 2.2582 | 2 | 1.7327 | 1.0071 | 0.27245 | -0.15612 | 3.3653 | 3.3459 | 3.3092 | 3.0663 | 2.9245 | 2.748 | 2.6378 | 2.4673 | 2.2857 | 1.652 | 1.1714 | 0.96735 | 2.7163 | 2.7102 | 2.6806 | 2.499 | 2.3918 | 2.2112 | 2.1102 | 1.9092 | 1.6796 | 1.001 | 0.42653 | 0.19082
|  | TEFFONT PRIMARY | EE |  |  |  |  | 3.0765 | 3.0673 | 3.05 | 2.8071 | 2.651 | 2.3837 | 2.2622 | 2.0327 | 1.7653 | 1.0071 | 0.38265 | 0.055102 | 3.3704 | 3.3459 | 3.3255 | 3.0663 | 2.9694 | 2.7612 | 2.6663 | 2.502 | 2.299 | 1.652 | 1.1714 | 0.96735 | 2.7204 | 2.7102 | 2.6929 | 2.499 | 2.4357 | 2.2388 | 2.1316 | 1.9429 | 1.6969 | 1.0173 | 0.49286 | 0.29286
|  | TEFFONT PRIMARY | HT |  |  |  |  | 3.0786 | 3.0796 | 3.0663 | 2.8684 | 2.6214 | 2.4316 | 2.2622 | 2.0306 | 1.7867 | 1.0092 | 0.27245 | -0.15612 | 3.3694 | 3.35 | 3.3265 | 3.1184 | 2.9245 | 2.7888 | 2.6378 | 2.4673 | 2.2857 | 1.652 | 1.2551 | 1.1755 | 2.7224 | 2.7184 | 2.7031 | 2.5439 | 2.3918 | 2.2704 | 2.1102 | 1.9153 | 1.699 | 1.001 | 0.42653 | 0.19082
|  | TEFFONT PRIMARY | HE |  |  |  |  | 3.0714 | 3.0745 | 3.0388 | 2.8551 | 2.6337 | 2.3541 | 2.2582 | 2 | 1.7327 | 1.1173 | 0.72347 | 0.39592 | 3.3653 | 3.351 | 3.3092 | 3.1245 | 2.9612 | 2.748 | 2.6857 | 2.499 | 2.2969 | 1.7357 | 1.5214 | 1.298 | 2.7163 | 2.7163 | 2.6806 | 2.5337 | 2.4214 | 2.2112 | 2.1224 | 1.9092 | 1.6796 | 1.1061 | 0.8449 | 0.62755
|  | TEFFONT PRIMARY | FB |  |  |  |  | 3.1408 | 3.1673 | 3.1827 | 3.1867 | 3.1765 | 3.151 | 3.1143 | 2.8286 | 2.7214 | 2.2102 | 1.6439 | 1.2694 | 3.4214 | 3.4204 | 3.4092 | 3.3969 | 3.3694 | 3.3347 | 3.2837 | 2.9969 | 2.8898 | 2.3612 | 1.7082 | 1.0582 | 2.7878 | 2.8092 | 2.8184 | 2.8255 | 2.8153 | 2.8 | 2.7724 | 2.5765 | 2.5061 | 2.0663 | 1.5378 | 1.1898
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | TEMPLE FARM PRIMARY | MINIMUM HEADROOM | SU 84178 83872 | YES | NO | 0.727 | 1.6869 | 1.692 | 1.6951 | 1.6778 | 1.6614 | 1.6196 | 1.5686 | 1.5022 | 1.4522 | 1.3288 | 1.1971 | 1.1176 | 2.0645 | 2.0645 | 2.0645 | 2.0573 | 2.0461 | 2.0237 | 2.0053 | 1.9808 | 1.9594 | 1.8573 | 1.7747 | 1.6053 | 1.8243 | 1.8273 | 1.8304 | 1.8131 | 1.7947 | 1.7529 | 1.7131 | 1.6784 | 1.6447 | 1.5447 | 1.4661 | 1.4324
|  | TEMPLE FARM PRIMARY | EE |  |  |  |  | 1.6869 | 1.6941 | 1.6951 | 1.6839 | 1.6696 | 1.6318 | 1.588 | 1.5247 | 1.4808 | 1.3288 | 1.1971 | 1.1176 | 2.0655 | 2.0645 | 2.0645 | 2.0584 | 2.0471 | 2.0247 | 2.0053 | 1.9808 | 1.9614 | 1.8573 | 1.789 | 1.741 | 1.8243 | 1.8294 | 1.8304 | 1.8151 | 1.7998 | 1.76 | 1.7233 | 1.6784 | 1.661 | 1.5447 | 1.4753 | 1.4467
|  | TEMPLE FARM PRIMARY | HT |  |  |  |  | 1.688 | 1.6931 | 1.7063 | 1.692 | 1.6849 | 1.638 | 1.6155 | 1.5614 | 1.5247 | 1.3992 | 1.2461 | 1.1288 | 2.0645 | 2.0645 | 2.0676 | 2.0584 | 2.0482 | 2.0257 | 2.0073 | 1.9839 | 1.9645 | 1.889 | 1.8522 | 1.8522 | 1.8253 | 1.8273 | 1.8396 | 1.8212 | 1.808 | 1.7743 | 1.7416 | 1.6998 | 1.6702 | 1.5835 | 1.508 | 1.4692
|  | TEMPLE FARM PRIMARY | HE |  |  |  |  | 1.688 | 1.692 | 1.7033 | 1.6778 | 1.6614 | 1.6196 | 1.5686 | 1.5022 | 1.4522 | 1.3492 | 1.2053 | 1.139 | 2.0645 | 2.0645 | 2.0676 | 2.0573 | 2.0461 | 2.0237 | 2.0053 | 1.9808 | 1.9594 | 1.8584 | 1.7798 | 1.7227 | 1.8253 | 1.8273 | 1.8376 | 1.8131 | 1.7947 | 1.7529 | 1.7131 | 1.6835 | 1.6447 | 1.5559 | 1.4661 | 1.4324
|  | TEMPLE FARM PRIMARY | FB |  |  |  |  | 1.7155 | 1.739 | 1.7522 | 1.7563 | 1.7573 | 1.7512 | 1.7471 | 1.7318 | 1.7176 | 1.642 | 1.5329 | 1.4982 | 2.0788 | 2.0869 | 2.089 | 2.091 | 2.092 | 2.0818 | 2.0757 | 2.0604 | 2.0471 | 1.9502 | 1.7747 | 1.6053 | 1.8498 | 1.8651 | 1.8702 | 1.8722 | 1.8722 | 1.8631 | 1.8569 | 1.8416 | 1.8304 | 1.7651 | 1.6631 | 1.6508
MELKSHAM GSP | CHIPPENHAM BSP | TETBURY PRIMARY | MINIMUM HEADROOM | ST 89708 93444 | NO | YES | 2.363 | 2.1115 | 2.0911 | 1.8452 | 1.585 | 1.2839 | 0.75638 | 0.1472 | -0.39974 | -1.0916 | -3.314 | -4.9763 | -5.8906 | 3.7198 | 3.6534 | 3.4575 | 3.2606 | 3.0412 | 2.6769 | 2.23 | 1.8646 | 1.3534 | -0.2078 | -1.2782 | -2.2149 | 2.6409 | 2.5807 | 2.3348 | 2.0796 | 1.7899 | 1.3174 | 0.73985 | 0.27557 | -0.35504 | -2.301 | -3.552 | -4.0979
|  | TETBURY PRIMARY | EE |  |  |  |  | 2.1115 | 2.1033 | 1.8758 | 1.6737 | 1.4299 | 0.99312 | 0.46965 | -0.0048408 | -0.60994 | -2.7355 | -4.3375 | -5.3293 | 3.7198 | 3.6565 | 3.4667 | 3.2922 | 3.0626 | 2.7279 | 2.3044 | 1.983 | 1.5044 | -0.2078 | -1.2782 | -1.9976 | 2.6409 | 2.5888 | 2.3541 | 2.1388 | 1.8684 | 1.4552 | 0.93679 | 0.52557 | -0.045861 | -1.952 | -3.1877 | -3.8816
|  | TETBURY PRIMARY | HT |  |  |  |  | 2.1125 | 2.0911 | 1.8452 | 1.585 | 1.2839 | 0.75638 | 0.1472 | -0.39974 | -1.0916 | -3.314 | -4.9763 | -5.8906 | 3.7228 | 3.6534 | 3.4575 | 3.2606 | 3.0412 | 2.6769 | 2.23 | 1.8646 | 1.3534 | -0.20474 | -1.0833 | -1.3211 | 2.6409 | 2.5807 | 2.3348 | 2.0796 | 1.7899 | 1.3174 | 0.73985 | 0.27557 | -0.35504 | -2.301 | -3.552 | -4.0979
|  | TETBURY PRIMARY | HE |  |  |  |  | 2.1125 | 2.1013 | 1.8758 | 1.6799 | 1.4268 | 0.97475 | 0.47781 | -0.033412 | -0.55586 | -2.2395 | -3.7089 | -4.364 | 3.7208 | 3.6565 | 3.4667 | 3.3095 | 3.0575 | 2.7106 | 2.3228 | 1.9626 | 1.582 | 0.16261 | -0.83535 | -1.3802 | 2.6409 | 2.5878 | 2.3541 | 2.1541 | 1.8654 | 1.4317 | 0.95312 | 0.50006 | 0.03169 | -1.4887 | -2.6346 | -3.054
|  | TETBURY PRIMARY | FB |  |  |  |  | 2.2645 | 2.2758 | 2.1931 | 2.1115 | 2.039 | 1.9268 | 1.8207 | 1.6931 | 1.4758 | 0.47169 | -0.96811 | -2.0304 | 3.8524 | 3.7861 | 3.7198 | 3.5953 | 3.48 | 3.3177 | 3.1524 | 2.9718 | 2.6738 | 1.331 | -0.48841 | -2.2149 | 2.8358 | 2.795 | 2.7225 | 2.6103 | 2.5164 | 2.3909 | 2.248 | 2.1092 | 1.8368 | 0.74598 | -0.69688 | -1.6652
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM PRIMARY | MINIMUM HEADROOM | SU 52758 66466 | NO | NO | 6.19 | 3.1194 | 2.9286 | 2.7908 | 2.4714 | 1.9959 | 1.1449 | 0.064286 | -1.2153 | -2.5296 | -6.7296 | -8.5837 | -8.8969 | 6.4582 | 6.2459 | 6.0867 | 5.7122 | 5.1418 | 4.2765 | 3.2296 | 2.0459 | 0.79388 | -3.3663 | -5.9459 | -10.749 | 4.0398 | 3.8316 | 3.6286 | 3.2561 | 2.7224 | 1.8531 | 0.75816 | -0.49286 | -1.7898 | -5.9612 | -7.6867 | -7.9837
|  | THATCHAM PRIMARY | EE |  |  |  |  | 3.1204 | 2.9286 | 2.8735 | 2.7041 | 2.3459 | 1.6653 | 0.71531 | -0.42041 | -1.5724 | -5.8245 | -8.0224 | -8.8163 | 6.4592 | 6.2459 | 6.1316 | 5.8408 | 5.3337 | 4.55 | 3.5959 | 2.4765 | 1.3133 | -3.3449 | -5.9459 | -7.7112 | 4.0408 | 3.8316 | 3.6888 | 3.4235 | 2.9796 | 2.2276 | 1.2735 | 0.13776 | -1.0337 | -5.2541 | -7.2969 | -7.9837
|  | THATCHAM PRIMARY | HT |  |  |  |  | 3.1194 | 2.9296 | 2.7908 | 2.4714 | 1.9959 | 1.1449 | 0.064286 | -1.2153 | -2.5296 | -6.7296 | -8.5837 | -8.8969 | 6.4592 | 6.2469 | 6.0867 | 5.7122 | 5.1418 | 4.2765 | 3.2296 | 2.0459 | 0.79388 | -3.3663 | -5.1347 | -5.4653 | 4.0398 | 3.8337 | 3.6286 | 3.2561 | 2.7224 | 1.8531 | 0.75816 | -0.49286 | -1.7898 | -5.9612 | -7.6867 | -7.8765
|  | THATCHAM PRIMARY | HE |  |  |  |  | 3.1214 | 2.9327 | 2.8776 | 2.702 | 2.3388 | 1.649 | 0.70714 | -0.42143 | -1.5357 | -5.0143 | -7.0031 | -7.5755 | 6.4582 | 6.248 | 6.1327 | 5.8398 | 5.3367 | 4.5357 | 3.5918 | 2.4786 | 1.3541 | -2.552 | -5.0082 | -6.7367 | 4.0418 | 3.8347 | 3.6929 | 3.4214 | 2.9776 | 2.2112 | 1.2694 | 0.14286 | -0.98673 | -4.4082 | -6.2622 | -6.7786
|  | THATCHAM PRIMARY | FB |  |  |  |  | 3.3398 | 3.3031 | 3.5051 | 3.6071 | 3.5724 | 3.3235 | 2.8837 | 2.4367 | 1.9459 | -1.1214 | -4.4939 | -6.3429 | 6.5122 | 6.3459 | 6.351 | 6.2735 | 6.0776 | 5.6878 | 5.0755 | 4.4724 | 3.7939 | -0.42857 | -5.6316 | -10.749 | 4.2276 | 4.1969 | 4.3418 | 4.3724 | 4.2816 | 4.001 | 3.5663 | 3.1316 | 2.6224 | -0.6 | -3.9265 | -5.8316
NORTH HYDE GSP | NORTH HYDE BSP | THE GREEN PRIMARY | MINIMUM HEADROOM | TQ 12414 79503 | NO | YES | 4.195 | Demand Headroom Winter (MVA) 2027: 2.0671; Demand Headroom Winter (MVA) 2028: 1.1589; Demand Headroom Winter (MVA) 2029: -0.42473 | 4.5283 | 4.0794 | 3.4334 | [9 empty] | 2.7406 | 2.0947 | 1.014
|  | THE GREEN PRIMARY | EE |  |  |  |  | Demand Headroom Winter (MVA) 2027: 2.0671; Demand Headroom Winter (MVA) 2028: 1.1589; Demand Headroom Winter (MVA) 2029: -0.42473 | 4.5283 | 4.0794 | 3.4334 | [9 empty] | 2.7406 | 2.0947 | 1.014
|  | THE GREEN PRIMARY | HT |  |  |  |  | Demand Headroom Winter (MVA) 2027: 2.0794; Demand Headroom Winter (MVA) 2028: 1.1957; Demand Headroom Winter (MVA) 2029: -0.31351 | 4.5294 | 4.0804 | 3.4385 | [9 empty] | 2.7518 | 2.1212 | 1.0834
|  | THE GREEN PRIMARY | HE |  |  |  |  | Demand Headroom Winter (MVA) 2027: 2.0712; Demand Headroom Winter (MVA) 2028: 1.1702; Demand Headroom Winter (MVA) 2029: -0.4084 | 4.5294 | 4.0794 | 3.4355 | [9 empty] | 2.7467 | 2.1049 | 1.0294
|  | THE GREEN PRIMARY | FB |  |  |  |  | Demand Headroom Winter (MVA) 2027: 2.2089; Demand Headroom Winter (MVA) 2028: 1.3916; Demand Headroom Winter (MVA) 2029: -0.016568 | 4.5671 | 4.1304 | 3.5028 | [9 empty] | 2.861 | 2.2753 | 1.3212
FLEET-BRAMLEY GSP | READING TOWN BSP | THE MALL PRIMARY | MINIMUM HEADROOM | SU 71319 73293 | NO | NO | 4.516 | 13.3134 | 13.395 | 13.3134 | 11.8981 | 11.393 | 11.0817 | 10.7664 | 10.4328 | 10.1103 | 9.445 | 8.5644 | 8.1307 | 16.2032 | 16.2185 | 16.147 | 14.5287 | 14.2634 | 14.1246 | 13.9705 | 13.7909 | 13.6093 | 12.1562 | 9.4481 | 5.6256 | 14.7368 | 14.7746 | 14.6715 | 13.3083 | 12.9144 | 12.6889 | 12.4542 | 12.195 | 11.9532 | 11.3205 | 10.8062 | 10.5062
|  | THE MALL PRIMARY | EE |  |  |  |  | 13.3134 | 13.4042 | 13.3144 | 11.8981 | 11.393 | 11.0817 | 10.7664 | 10.4328 | 10.1103 | 9.5052 | 8.5644 | 8.1307 | 16.2062 | 16.2266 | 16.1624 | 14.5379 | 14.2634 | 14.1307 | 13.9715 | 13.7909 | 13.6226 | 12.8144 | 11.4817 | 9.9593 | 14.7368 | 14.7777 | 14.6715 | 13.3083 | 12.9154 | 12.6889 | 12.4542 | 12.195 | 11.9532 | 11.3828 | 10.8542 | 10.5062
|  | THE MALL PRIMARY | HT |  |  |  |  | 13.3154 | 13.395 | 13.3134 | 11.9083 | 11.4552 | 11.146 | 10.846 | 10.5368 | 10.2328 | 9.445 | 8.8185 | 8.4593 | 16.2052 | 16.2185 | 16.1532 | 14.5287 | 14.2797 | 14.1317 | 13.9705 | 13.8001 | 13.6307 | 13.2062 | 12.9042 | 12.645 | 14.7419 | 14.7746 | 14.6807 | 13.3124 | 12.9562 | 12.7195 | 12.4889 | 12.2481 | 12.0093 | 11.3205 | 10.8062 | 10.5603
|  | THE MALL PRIMARY | HE |  |  |  |  | 13.3246 | 13.4246 | 13.3164 | 11.9032 | 11.4032 | 11.1011 | 10.7991 | 10.4726 | 10.1624 | 9.6756 | 9.2828 | 9.0787 | 16.2062 | 16.2287 | 16.1644 | 14.5419 | 14.2715 | 14.1399 | 13.9858 | 13.8042 | 13.6389 | 13.0501 | 11.8909 | 10.4246 | 14.7368 | 14.7787 | 14.6787 | 13.3093 | 12.9144 | 12.6981 | 12.4715 | 12.2236 | 11.9868 | 11.5328 | 11.1981 | 11.0379
|  | THE MALL PRIMARY | FB |  |  |  |  | 13.3491 | 13.4593 | 13.4042 | 12.0828 | 11.7001 | 11.4889 | 11.2981 | 11.1001 | 10.9317 | 10.6634 | 10.1511 | 9.6195 | 16.2032 | 16.2215 | 16.147 | 14.5317 | 14.2736 | 14.1246 | 13.9715 | 13.8113 | 13.6093 | 12.1562 | 9.4481 | 5.6256 | 14.7817 | 14.8501 | 14.7787 | 13.4562 | 13.1532 | 12.9991 | 12.8532 | 12.7001 | 12.5777 | 12.2817 | 11.7889 | 11.5297
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | THEALE PRIMARY | MINIMUM HEADROOM | SU 64755 71015 | NO | NO | 5.164 | 12.8893 | 12.7383 | 12.574 | 12.3668 | 12.1485 | 11.8628 | 11.5893 | 11.275 | 11.0485 | 8.7403 | 7.6056 | 6.9648 | 15.1393 | 15.0444 | 14.9423 | 14.824 | 14.6883 | 14.2597 | 13.8883 | 13.3372 | 12.8209 | 10.6301 | 9.5668 | 8.7444 | 14.024 | 13.8862 | 13.7495 | 13.5709 | 13.374 | 13.0474 | 12.6434 | 12.0454 | 11.5679 | 9.427 | 8.3709 | 7.7842
|  | THEALE PRIMARY | EE |  |  |  |  | 12.8893 | 12.7383 | 12.574 | 12.3668 | 12.1556 | 11.8628 | 11.5893 | 11.275 | 11.0485 | 8.7648 | 7.6056 | 6.9648 | 15.1403 | 15.0454 | 14.9474 | 14.8321 | 14.6964 | 14.2903 | 13.9158 | 13.3372 | 12.9577 | 10.6301 | 9.5668 | 8.877 | 14.024 | 13.8862 | 13.7495 | 13.5709 | 13.3821 | 13.073 | 12.6577 | 12.0454 | 11.6679 | 9.4434 | 8.3709 | 7.7842
|  | THEALE PRIMARY | HT |  |  |  |  | 12.8934 | 12.7474 | 12.5893 | 12.375 | 12.1832 | 11.9066 | 11.6332 | 11.3199 | 11.0883 | 8.7403 | 7.6066 | 7.2842 | 15.1403 | 15.0474 | 14.9423 | 14.824 | 14.7036 | 14.374 | 13.9944 | 13.4077 | 13.0281 | 10.7372 | 9.825 | 9.6128 | 14.0281 | 13.8934 | 13.7587 | 13.5719 | 13.4077 | 13.1597 | 12.7393 | 12.1158 | 11.7301 | 9.427 | 8.4066 | 8.1474
|  | THEALE PRIMARY | HE |  |  |  |  | 12.8913 | 12.7403 | 12.5801 | 12.3689 | 12.1485 | 11.8638 | 11.6026 | 11.3383 | 11.0556 | 9.1648 | 7.8628 | 7.7291 | 15.1393 | 15.0444 | 14.9464 | 14.8291 | 14.6883 | 14.2597 | 13.8883 | 13.4332 | 12.8209 | 10.9189 | 9.6413 | 9.4117 | 14.026 | 13.8883 | 13.7566 | 13.5719 | 13.374 | 13.0474 | 12.6434 | 12.1546 | 11.5679 | 9.7954 | 8.5923 | 8.5077
|  | THEALE PRIMARY | FB |  |  |  |  | 12.9199 | 12.8199 | 12.727 | 12.6281 | 12.4913 | 12.3444 | 12.2301 | 12.1281 | 11.9964 | 11.4087 | 9.9189 | 8.2883 | 15.1505 | 15.0811 | 15.0138 | 14.9515 | 14.8556 | 14.7566 | 14.6709 | 14.4934 | 14.1383 | 12.6832 | 10.8046 | 8.7444 | 14.0505 | 13.9628 | 13.8709 | 13.7923 | 13.6709 | 13.5383 | 13.4413 | 13.3505 | 13.1474 | 11.8852 | 10.3526 | 8.8026
MELKSHAM GSP | ANDOVER BSP | THRUXTON PRIMARY | MINIMUM HEADROOM | SU 29134 45674 | NO | NO | 0.915 | 3.7737 | 3.7553 | 3.4165 | 3.0849 | 2.5522 | 1.9186 | 1.1859 | 0.41959 | -0.34265 | -3.2467 | -4.0376 | -4.4049 | 5.2444 | 5.2291 | 4.9097 | 4.6923 | 4.4066 | 4.1617 | 3.8291 | 3.4546 | 3.1005 | 0.58724 | 0.21276 | -0.12908 | 4.7696 | 4.7696 | 4.4216 | 4.1308 | 3.7227 | 3.2716 | 2.7553 | 2.188 | 1.6308 | -1.3937 | -1.96 | -2.1722
|  | THRUXTON PRIMARY | EE |  |  |  |  | 3.7737 | 3.7553 | 3.4288 | 3.0849 | 2.5522 | 1.9186 | 1.2349 | 0.47776 | -0.26714 | -3.2467 | -4.0376 | -4.4049 | 5.2464 | 5.2291 | 4.9219 | 4.6923 | 4.4281 | 4.1617 | 3.8587 | 3.4709 | 3.1097 | 0.74235 | 0.21276 | 0.0076531 | 4.7696 | 4.7696 | 4.4308 | 4.1308 | 3.7227 | 3.2716 | 2.7859 | 2.2196 | 1.6696 | -1.2886 | -1.96 | -2.1722
|  | THRUXTON PRIMARY | HT |  |  |  |  | 3.7747 | 3.7604 | 3.4165 | 3.1012 | 2.5941 | 2.0502 | 1.3369 | 0.63592 | -0.048776 | -3.1937 | -3.8784 | -4.3508 | 5.2454 | 5.2301 | 4.9097 | 4.6964 | 4.4066 | 4.2199 | 3.8291 | 3.4546 | 3.1005 | 0.58724 | 0.32398 | 0.28316 | 4.7696 | 4.7727 | 4.4216 | 4.1471 | 3.7339 | 3.3686 | 2.8237 | 2.29 | 1.7757 | -1.3937 | -1.8539 | -2.0967
|  | THRUXTON PRIMARY | HE |  |  |  |  | 3.7737 | 3.7573 | 3.4308 | 3.1431 | 2.5543 | 1.9288 | 1.1859 | 0.41959 | -0.34265 | -3.011 | -3.7733 | -4.1457 | 5.2444 | 5.2301 | 4.9219 | 4.7556 | 4.427 | 4.1964 | 3.8423 | 3.4709 | 3.1128 | 0.94337 | 0.49133 | 0.21582 | 4.7696 | 4.7716 | 4.4329 | 4.19 | 3.7227 | 3.2951 | 2.7553 | 2.188 | 1.6308 | -1.0784 | -1.7039 | -1.9406
|  | THRUXTON PRIMARY | FB |  |  |  |  | 3.8482 | 3.8584 | 3.8002 | 3.589 | 3.2206 | 2.8002 | 2.2482 | 1.789 | 1.3584 | 0.019592 | -2.1284 | -2.6222 | 5.3077 | 5.2985 | 5.2536 | 5.1556 | 4.9985 | 4.8158 | 4.4046 | 4.1893 | 4.0046 | 3.0811 | 0.64949 | -0.12908 | 4.8431 | 4.8563 | 4.791 | 4.6584 | 4.4094 | 4.1176 | 3.6084 | 3.2798 | 2.9818 | 1.9002 | -0.58857 | -1.0386
MELKSHAM GSP | WEST GRAFTON BSP | TIDWORTH PRIMARY | MINIMUM HEADROOM | SU 24088 49593 | NO | NO | 3.203 | 6.7606 | 6.5984 | 6.1504 | 5.6504 | 5.1698 | 4.6351 | 3.9463 | 3.1014 | 2.2443 | -1.0873 | -2.5302 | -2.869 | 9.6672 | 9.511 | 9.1039 | 8.6845 | 8.1967 | 7.6967 | 7.059 | 6.3355 | 5.6376 | 2.9988 | 1.7957 | -0.91754 | 7.9023 | 7.7584 | 7.341 | 6.9104 | 6.4482 | 5.9523 | 5.3145 | 4.5553 | 3.8074 | 0.90531 | -0.36407 | -0.75387
|  | TIDWORTH PRIMARY | EE |  |  |  |  | 6.7606 | 6.5984 | 6.1637 | 5.6902 | 5.2586 | 4.7555 | 4.1463 | 3.3923 | 2.6086 | -0.73836 | -2.3098 | -2.8067 | 9.6672 | 9.511 | 9.1131 | 8.7141 | 8.2682 | 7.7743 | 7.1978 | 6.5457 | 5.8967 | 3.1539 | 1.7957 | 0.89164 | 7.9023 | 7.7584 | 7.3523 | 6.9431 | 6.5257 | 6.0431 | 5.4696 | 4.7869 | 4.092 | 1.142 | -0.27632 | -0.75387
|  | TIDWORTH PRIMARY | HT |  |  |  |  | 6.7606 | 6.5984 | 6.1504 | 5.6504 | 5.1698 | 4.6351 | 3.9463 | 3.1014 | 2.2443 | -1.0873 | -2.5302 | -2.869 | 9.6672 | 9.511 | 9.1039 | 8.6845 | 8.1967 | 7.6967 | 7.059 | 6.3355 | 5.6376 | 2.9988 | 1.8814 | 1.6365 | 7.9023 | 7.7584 | 7.341 | 6.9104 | 6.4482 | 5.9523 | 5.3145 | 4.5553 | 3.8074 | 0.90531 | -0.36407 | -0.66305
|  | TIDWORTH PRIMARY | HE |  |  |  |  | 6.7606 | 6.5984 | 6.1616 | 5.7423 | 5.2555 | 4.78 | 4.1616 | 3.4086 | 2.628 | -0.40775 | -1.7251 | -2.0567 | 9.6682 | 9.512 | 9.1141 | 8.7712 | 8.2549 | 7.7957 | 7.21 | 6.5549 | 5.91 | 3.4161 | 2.2784 | 1.4253 | 7.9023 | 7.7584 | 7.3502 | 6.9982 | 6.5186 | 6.0665 | 5.489 | 4.8053 | 4.1165 | 1.489 | 0.34307 | 0.041029
|  | TIDWORTH PRIMARY | FB |  |  |  |  | 6.9178 | 6.8147 | 6.5678 | 6.2647 | 6.182 | 5.9443 | 5.4045 | 4.9392 | 4.3953 | 1.6453 | -0.60367 | -1.5761 | 9.7763 | 9.6508 | 9.4467 | 9.2008 | 9.0978 | 8.8437 | 8.2814 | 7.8672 | 7.3947 | 4.811 | 1.8161 | -0.91754 | 8.0512 | 7.9584 | 7.7523 | 7.5165 | 7.4543 | 7.2472 | 6.7196 | 6.3186 | 5.8492 | 3.4716 | 1.3461 | 0.37368
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY PRIMARY | MINIMUM HEADROOM | ST 93438 29127 | NO | NO | 6.223 | 1.22 | 1.2628 | 1.2618 | 1.2139 | 1.072 | 0.87713 | 0.66182 | 0.34346 | 0.059784 | -0.63001 | -1.229 | -1.6565 | 2.6292 | 2.6282 | 2.5924 | 2.5679 | 2.369 | 2.2761 | 2.0914 | 1.8822 | 1.6863 | 1.0853 | 0.71387 | -0.0075633 | 1.9639 | 1.9771 | 1.973 | 1.92 | 1.7373 | 1.6169 | 1.4312 | 1.1526 | 0.93529 | 0.28325 | -0.085114 | -0.27593
|  | TISBURY PRIMARY | EE |  |  |  |  | 1.221 | 1.2628 | 1.2618 | 1.2251 | 1.0812 | 0.92407 | 0.72407 | 0.39856 | 0.15162 | -0.63001 | -1.181 | -1.5004 | 2.6302 | 2.6282 | 2.5924 | 2.572 | 2.37 | 2.2914 | 2.1455 | 1.8884 | 1.7465 | 1.0853 | 0.71387 | 0.44754 | 1.9649 | 1.9771 | 1.973 | 1.92 | 1.7373 | 1.6465 | 1.4598 | 1.1526 | 0.96182 | 0.28325 | -0.055522 | -0.22185
|  | TISBURY PRIMARY | HT |  |  |  |  | 1.223 | 1.272 | 1.2914 | 1.2475 | 1.1108 | 0.96999 | 0.75774 | 0.45672 | 0.17203 | -0.56573 | -1.229 | -1.6565 | 2.6292 | 2.6292 | 2.6088 | 2.5679 | 2.369 | 2.2792 | 2.0914 | 1.8822 | 1.6863 | 1.1475 | 0.90264 | 0.86999 | 1.9659 | 1.9843 | 1.9904 | 1.9343 | 1.7506 | 1.6537 | 1.4384 | 1.1853 | 0.9557 | 0.29142 | -0.085114 | -0.27593
|  | TISBURY PRIMARY | HE |  |  |  |  | 1.22 | 1.2639 | 1.2639 | 1.2139 | 1.072 | 0.87713 | 0.66182 | 0.34346 | 0.059784 | -0.43409 | -0.95552 | -1.2494 | 2.6292 | 2.6282 | 2.5924 | 2.571 | 2.4098 | 2.2761 | 2.1282 | 1.9047 | 1.7414 | 1.2139 | 0.90672 | 0.64244 | 1.9639 | 1.9792 | 1.9741 | 1.9333 | 1.773 | 1.6169 | 1.4312 | 1.1547 | 0.93529 | 0.42815 | 0.16591 | 0.0097837
|  | TISBURY PRIMARY | FB |  |  |  |  | 1.3139 | 1.3751 | 1.4118 | 1.4261 | 1.4496 | 1.4322 | 1.4057 | 1.3353 | 1.2884 | 0.8057 | 0.17917 | -0.10858 | 2.6965 | 2.6975 | 2.6996 | 2.6965 | 2.672 | 2.622 | 2.5577 | 2.473 | 2.4567 | 1.6496 | 0.78938 | -0.0075633 | 2.0251 | 2.0577 | 2.0843 | 2.0945 | 2.1026 | 2.0843 | 2.0557 | 2.021 | 1.9873 | 1.422 | 0.82407 | 0.57509
LOVEDEAN GSP | FAREHAM (MAIN) BSP | TITCHFIELD PRIMARY | MINIMUM HEADROOM | SU 54104 05695 | NO | YES | 1.414 | 10.8607 | 10.7872 | 10.6495 | 10.1913 | 9.7985 | 28.3153 | 26.8694 | 25.3316 | 23.9122 | 19.6408 | 17.3 | 16.0969 | 13.2357 | 13.1327 | 13.0663 | 12.6184 | 12.2327 | 30.0214 | 29.298 | 28.4612 | 27.7612 | 25.5082 | 24.0714 | 21.9867 | 12.0378 | 11.9367 | 11.8592 | 11.351 | 10.9235 | 28.8378 | 27.7429 | 26.549 | 25.4847 | 22.2173 | 20.5531 | 19.8531
|  | TITCHFIELD PRIMARY | EE |  |  |  |  | 10.875 | 10.8852 | 10.7923 | 10.4219 | 10.0454 | 28.6704 | 27.8898 | 26.2908 | 24.8143 | 20.1918 | 18.1194 | 16.9245 | 13.2429 | 13.1724 | 13.1265 | 12.7235 | 12.3694 | 30.2459 | 29.7286 | 28.9143 | 28.251 | 25.5082 | 24.0714 | 23.0041 | 12.048 | 12.0102 | 11.9694 | 11.5265 | 11.1296 | 29.1541 | 28.4969 | 27.2806 | 26.2 | 22.6296 | 21.0643 | 20.2663
|  | TITCHFIELD PRIMARY | HT |  |  |  |  | 10.8607 | 10.7872 | 10.6495 | 10.1913 | 9.7985 | 28.3153 | 26.8694 | 25.3316 | 23.9122 | 19.6408 | 17.3 | 16.0969 | 13.2357 | 13.1327 | 13.0663 | 12.6184 | 12.2327 | 30.0214 | 29.298 | 28.4612 | 27.7612 | 25.5194 | 24.499 | 24.1918 | 12.0378 | 11.9367 | 11.8592 | 11.351 | 10.9235 | 28.8378 | 27.7429 | 26.549 | 25.4847 | 22.2173 | 20.5531 | 19.8531
|  | TITCHFIELD PRIMARY | HE |  |  |  |  | 10.873 | 10.873 | 10.7964 | 10.3903 | 9.973 | 28.5592 | 27.7286 | 26.652 | 25.6561 | 22.552 | 20.1806 | 18.55 | 13.2398 | 13.1612 | 13.1245 | 12.7184 | 12.35 | 30.2214 | 29.6633 | 29.0378 | 28.5031 | 26.2714 | 25.0357 | 23.6714 | 12.0459 | 12.001 | 11.9694 | 11.5061 | 11.0837 | 29.0908 | 28.3816 | 27.5306 | 26.7684 | 24.248 | 22.6398 | 21.5357
|  | TITCHFIELD PRIMARY | FB |  |  |  |  | 11.0515 | 11.123 | 11.1791 | 11.1372 | 11.1046 | 30.2286 | 30.0459 | 29.8724 | 29.5398 | 27.4265 | 24.9714 | 23.0735 | 13.3786 | 13.352 | 13.3163 | 13.2296 | 13.1755 | 31.2592 | 30.8582 | 30.6082 | 30.1929 | 27.9041 | 25.0908 | 21.9867 | 12.25 | 12.2949 | 12.3255 | 12.2898 | 12.2908 | 30.75 | 30.4449 | 30.2786 | 29.9102 | 27.9143 | 25.849 | 24.2704
FLEET-BRAMLEY GSP | ALDERSHOT BSP | TONGHAM PRIMARY | MINIMUM HEADROOM | SU 88310 49487 | NO | YES | 2.838 | 14.601 | 14.4786 | 14.1684 | 13.7439 | 13.1582 | 12.0357 | 10.9327 | 9.6745 | 8.5867 | 4.3714 | 1.5551 | 0.19898 | 19.7592 | 19.5929 | 19.2602 | 18.948 | 18.5316 | 17.8184 | 17.1194 | 16.2582 | 15.5592 | 12.8347 | 10.0898 | 5.0337 | 17.4051 | 17.2765 | 16.9684 | 16.6327 | 16.1592 | 15.2337 | 14.3184 | 13.2184 | 12.3163 | 8.7408 | 6.5796 | 5.7714
|  | TONGHAM PRIMARY | EE |  |  |  |  | 14.6316 | 14.5765 | 14.3837 | 14.1204 | 13.7276 | 12.8031 | 11.8939 | 10.8143 | 9.9153 | 5.8357 | 2.8878 | 1.3531 | 19.7765 | 19.6429 | 19.3663 | 19.1245 | 18.7888 | 18.2163 | 17.6286 | 16.8776 | 16.2969 | 12.9663 | 10.5714 | 8.6255 | 17.4214 | 17.3378 | 17.1061 | 16.8745 | 16.5337 | 15.7837 | 15.0082 | 14.0418 | 13.2816 | 9.7337 | 7.3806 | 6.2929
|  | TONGHAM PRIMARY | HT |  |  |  |  | 14.601 | 14.4786 | 14.1684 | 13.7439 | 13.1582 | 12.0357 | 10.9327 | 9.6745 | 8.5867 | 4.3714 | 1.5551 | 0.19898 | 19.7592 | 19.5929 | 19.2602 | 18.948 | 18.5316 | 17.8184 | 17.1194 | 16.2582 | 15.5592 | 12.8347 | 11.3724 | 10.8673 | 17.4051 | 17.2765 | 16.9684 | 16.6327 | 16.1592 | 15.2337 | 14.3184 | 13.2184 | 12.3163 | 8.7408 | 6.5796 | 5.7714
|  | TONGHAM PRIMARY | HE |  |  |  |  | 14.6418 | 14.5837 | 14.399 | 14.1224 | 13.7082 | 12.802 | 11.8816 | 10.8133 | 9.9327 | 6.6245 | 4.3531 | 3.1694 | 19.7806 | 19.6398 | 19.3663 | 19.1214 | 18.7806 | 18.2224 | 17.6286 | 16.8929 | 16.3378 | 13.3582 | 11.4173 | 9.4378 | 17.4306 | 17.3439 | 17.1194 | 16.8765 | 16.5204 | 15.7878 | 15.0061 | 14.0551 | 13.3224 | 10.4163 | 8.7296 | 7.8398
|  | TONGHAM PRIMARY | FB |  |  |  |  | 14.8755 | 14.9582 | 15.0122 | 14.9745 | 14.9153 | 14.702 | 14.4643 | 14.2051 | 13.9224 | 11.8194 | 9.1969 | 7.4898 | 19.8867 | 19.8276 | 19.6776 | 19.4939 | 19.2837 | 18.9 | 18.4878 | 18.0582 | 17.599 | 14.4786 | 10.0898 | 5.0337 | 17.6469 | 17.7163 | 17.6816 | 17.65 | 17.5969 | 17.4051 | 17.1816 | 16.9418 | 16.6765 | 14.5714 | 12.0704 | 10.4031
MINETY GSP | TOOTHILL BSP | TOOTHILL PRIMARY | MINIMUM HEADROOM | SU 13215 83986 | NO | NO | 2.34 | 14.6373 | 14.4292 | 14.119 | 13.6802 | 13.1333 | 12.1445 | 10.8863 | 9.5384 | 8.2261 | 5.4088 | 3.2557 | 1.9486 | 13.5312 | 13.3363 | 13.0414 | 12.7435 | 12.2996 | 11.6537 | 10.8322 | 9.9169 | 9.0771 | 6.9241 | 5.0312 | 1.4884 | 14.7802 | 14.5169 | 14.072 | 13.6261 | 13.0547 | 12.1588 | 11.0955 | 9.9271 | 8.821 | 6.3476 | 4.5659 | 3.5231
|  | TOOTHILL PRIMARY | EE |  |  |  |  | 14.6373 | 14.4292 | 14.119 | 13.6833 | 13.2016 | 12.2496 | 11.0894 | 9.7435 | 8.4282 | 5.4088 | 3.2557 | 1.9486 | 13.5322 | 13.3363 | 13.0414 | 12.7435 | 12.3608 | 11.8312 | 11.1271 | 10.2547 | 9.4404 | 6.9241 | 5.2537 | 3.6731 | 14.7802 | 14.5169 | 14.072 | 13.6261 | 13.0873 | 12.3098 | 11.3537 | 10.2057 | 9.1149 | 6.3476 | 4.5659 | 3.5231
|  | TOOTHILL PRIMARY | HT |  |  |  |  | 14.6476 | 14.4476 | 14.1537 | 13.721 | 13.1333 | 12.1445 | 10.8863 | 9.5384 | 8.2261 | 5.518 | 3.4873 | 2.4751 | 13.5322 | 13.3394 | 13.0455 | 12.7506 | 12.2996 | 11.6537 | 10.8322 | 9.9169 | 9.0771 | 7.4884 | 6.521 | 6.0363 | 14.7914 | 14.5394 | 14.1047 | 13.6557 | 13.0547 | 12.1588 | 11.0955 | 9.9271 | 8.821 | 6.4516 | 4.8118 | 4.0771
|  | TOOTHILL PRIMARY | HE |  |  |  |  | 14.6424 | 14.4424 | 14.1333 | 13.6802 | 13.1976 | 12.2598 | 11.1384 | 9.8384 | 8.5578 | 6.2169 | 4.7016 | 3.7863 | 13.5312 | 13.3404 | 13.0455 | 12.7465 | 12.4006 | 11.8231 | 11.1261 | 10.2588 | 9.4445 | 7.2904 | 5.8455 | 4.3731 | 14.7884 | 14.5363 | 14.0996 | 13.6384 | 13.1343 | 12.3108 | 11.3812 | 10.2669 | 9.2016 | 7.0833 | 5.8598 | 5.1404
|  | TOOTHILL PRIMARY | FB |  |  |  |  | 14.7659 | 14.6322 | 14.4333 | 14.1476 | 13.8118 | 13.422 | 12.9373 | 12.3649 | 11.6465 | 9.6649 | 7.7996 | 6.3618 | 13.6241 | 13.4445 | 13.2414 | 13.0251 | 12.6302 | 12.2731 | 11.821 | 11.2363 | 10.6363 | 7.9598 | 5.0312 | 1.4884 | 14.9629 | 14.7945 | 14.568 | 14.3251 | 13.871 | 13.5006 | 13.0578 | 12.4516 | 11.822 | 9.8282 | 8.0863 | 6.7322
NURSLING GSP | ROWNHAMS BSP | TOTTON PRIMARY | MINIMUM HEADROOM | SU 35835 13428 | NO | YES | 8.846 | 7.4715 | 7.1572 | 7.0399 | 6.6868 | 6.2215 | 5.4746 | 4.6011 | 3.6644 | 2.7358 | -1.1652 | -3.8254 | -5.3244 | 9.2246 | 8.8817 | 8.8123 | 8.6235 | 8.3429 | 8.0052 | 7.5623 | 7.0888 | 6.6195 | 4.1327 | 2.0776 | -1.3561 | 8.5205 | 8.2062 | 8.2001 | 7.947 | 7.5817 | 6.9878 | 6.2501 | 5.4817 | 4.7133 | 1.1786 | -0.98055 | -2.0173
|  | TOTTON PRIMARY | EE |  |  |  |  | 7.4837 | 7.3797 | 7.1041 | 6.8297 | 6.4531 | 5.7368 | 4.8654 | 3.9817 | 3.0899 | -0.33565 | -3.0683 | -4.6214 | 9.2348 | 9.1327 | 8.8582 | 8.7041 | 8.4654 | 8.1837 | 7.7797 | 7.3541 | 6.9256 | 4.1899 | 2.0776 | 0.73578 | 8.5297 | 8.4184 | 8.249 | 8.0868 | 7.797 | 7.2623 | 6.5501 | 5.845 | 5.1103 | 1.7878 | -0.50198 | -1.6285
|  | TOTTON PRIMARY | HT |  |  |  |  | 7.4715 | 7.1572 | 7.0399 | 6.6868 | 6.2215 | 5.4746 | 4.6011 | 3.6644 | 2.7358 | -1.1652 | -3.8254 | -5.3244 | 9.2246 | 8.8817 | 8.8123 | 8.6235 | 8.3429 | 8.0052 | 7.5623 | 7.0888 | 6.6195 | 4.1327 | 2.8041 | 2.3184 | 8.5205 | 8.2062 | 8.2001 | 7.947 | 7.5817 | 6.9878 | 6.2501 | 5.4817 | 4.7133 | 1.1786 | -0.98055 | -2.0173
|  | TOTTON PRIMARY | HE |  |  |  |  | 7.4929 | 7.397 | 7.1317 | 6.8174 | 6.4123 | 5.7603 | 4.9388 | 4.0848 | 3.2378 | 0.34598 | -1.4683 | -2.7652 | 9.2317 | 9.1307 | 8.8531 | 8.6939 | 8.4541 | 8.1807 | 7.7746 | 7.3511 | 6.9327 | 4.6133 | 2.9674 | 1.5205 | 8.5327 | 8.4307 | 8.2664 | 8.0807 | 7.7705 | 7.2797 | 6.595 | 5.9123 | 5.2195 | 2.5215 | 0.92864 | -0.039731
|  | TOTTON PRIMARY | FB |  |  |  |  | 7.6225 | 7.698 | 7.6348 | 7.4001 | 7.3215 | 7.1929 | 6.9766 | 6.6623 | 6.348 | 4.3644 | 2.6041 | 0.78272 | 9.3388 | 9.399 | 9.3276 | 9.0786 | 9.0378 | 8.9521 | 8.8133 | 8.6103 | 8.4103 | 6.0429 | 2.5031 | -1.3561 | 8.6439 | 8.7317 | 8.7184 | 8.5041 | 8.5041 | 8.4399 | 8.3011 | 8.097 | 7.8327 | 5.995 | 3.8644 | 2.0276
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK PRIMARY | MINIMUM HEADROOM | SU 45156 14783 | NO | NO | 1.009 | 11.55 | 11.6337 | 11.6112 | 11.3408 | 10.9143 | 10.152 | 9.1561 | 8.0316 | 6.8571 | 2.9316 | 0.51122 | -0.2898 | 15.0173 | 14.9102 | 14.7102 | 14.1796 | 13.599 | 12.9163 | 12.0367 | 11.0776 | 10.0878 | 6.3969 | 1.6459 | -5.6735 | 12.6724 | 12.6551 | 12.5133 | 11.9459 | 11.3847 | 10.6969 | 9.7949 | 8.7806 | 7.7347 | 4.1459 | 2.0551 | 1.2561
|  | TOWNHILL PARK PRIMARY | EE |  |  |  |  | 11.55 | 11.6367 | 11.649 | 11.4969 | 11.2367 | 10.448 | 9.4786 | 8.4612 | 7.4592 | 3.5439 | 0.91327 | -0.2898 | 15.0194 | 14.9194 | 14.749 | 14.2776 | 13.7745 | 13.0827 | 12.2112 | 11.3102 | 10.4265 | 6.3969 | 3.3878 | 0.59082 | 12.6724 | 12.6551 | 12.5449 | 12.0847 | 11.649 | 10.9398 | 10.049 | 9.1153 | 8.2071 | 4.5429 | 2.2306 | 1.2561
|  | TOWNHILL PARK PRIMARY | HT |  |  |  |  | 11.5531 | 11.6337 | 11.6112 | 11.3408 | 10.9143 | 10.152 | 9.1561 | 8.0316 | 6.8571 | 2.9316 | 0.51122 | -0.15 | 15.0173 | 14.9102 | 14.7102 | 14.1796 | 13.599 | 12.9163 | 12.0367 | 11.0776 | 10.0878 | 6.9918 | 5.5153 | 5.0071 | 12.6786 | 12.6561 | 12.5133 | 11.9459 | 11.3847 | 10.6969 | 9.7949 | 8.7806 | 7.7347 | 4.1459 | 2.0551 | 1.6071
|  | TOWNHILL PARK PRIMARY | HE |  |  |  |  | 11.5643 | 11.6653 | 11.6939 | 11.5214 | 11.2541 | 10.4796 | 9.5847 | 8.6296 | 7.6694 | 4.5449 | 2.5551 | 1.6337 | 15.0224 | 14.9255 | 14.7592 | 14.3449 | 13.8296 | 13.0959 | 12.252 | 11.3622 | 10.4694 | 6.7969 | 3.9612 | 1.0776 | 12.6857 | 12.6755 | 12.5806 | 12.1531 | 11.6827 | 10.9633 | 10.1316 | 9.2449 | 8.3612 | 5.4143 | 3.702 | 2.9347
|  | TOWNHILL PARK PRIMARY | FB |  |  |  |  | 11.7673 | 11.9714 | 12.1898 | 12.3173 | 12.4 | 12.3776 | 12.302 | 12.1133 | 11.9653 | 9.6133 | 6.3143 | 4.3388 | 15.1296 | 15.0745 | 15.0673 | 14.9306 | 14.6837 | 14.2561 | 13.752 | 13.0306 | 12.4082 | 8.0316 | 1.6459 | -5.6735 | 12.949 | 13.0755 | 13.2531 | 13.3071 | 13.3051 | 13.2143 | 13.0398 | 12.5439 | 12.2347 | 9.8051 | 6.6367 | 4.7561
MINETY GSP | SWINDON BSP | TRADING ESTATE PRIMARY | MINIMUM HEADROOM | SU 13490 85868 | NO | NO | 5.44 | 7.0722 | 7.0569 | 7.0181 | 6.9375 | 6.6028 | 6.1089 | 5.4415 | 4.6477 | 3.9303 | 1.5609 | -0.030904 | -1.0278 | 9.1253 | 9.0467 | 8.9223 | 8.7019 | 8.1957 | 7.5661 | 6.8804 | 5.9825 | 5.0539 | 2.6396 | 1.1865 | -0.14713 | 7.8676 | 7.8349 | 7.7747 | 7.6757 | 7.2329 | 6.5778 | 5.8543 | 4.9196 | 3.9421 | 1.538 | 0.096137 | -0.80386
|  | TRADING ESTATE PRIMARY | EE |  |  |  |  | 7.0722 | 7.0569 | 7.0181 | 6.9375 | 6.7885 | 6.4252 | 5.9507 | 5.2977 | 4.6334 | 1.5609 | -0.030904 | -1.0278 | 9.1263 | 9.0631 | 8.9314 | 8.7019 | 8.3631 | 7.81 | 7.2927 | 6.5141 | 5.6355 | 2.6396 | 1.1865 | -0.030802 | 7.8676 | 7.8349 | 7.7747 | 7.6757 | 7.4104 | 6.838 | 6.2859 | 5.4767 | 4.5523 | 1.538 | 0.096137 | -0.80386
|  | TRADING ESTATE PRIMARY | HT |  |  |  |  | 7.0773 | 7.0681 | 7.0344 | 6.9497 | 6.6028 | 6.1089 | 5.4415 | 4.6477 | 3.9303 | 1.6079 | 0.1742 | -0.6605 | 9.1253 | 9.0661 | 8.9345 | 8.707 | 8.1957 | 7.5661 | 6.8804 | 5.9825 | 5.0539 | 2.9712 | 1.8733 | 1.2161 | 7.8747 | 7.8482 | 7.7941 | 7.688 | 7.2329 | 6.5778 | 5.8543 | 4.9196 | 3.9421 | 1.6084 | 0.31859 | -0.41203
|  | TRADING ESTATE PRIMARY | HE |  |  |  |  | 7.0762 | 7.0681 | 7.0344 | 6.9497 | 6.7926 | 6.4589 | 5.9915 | 5.3436 | 4.6609 | 2.6385 | 1.6671 | 0.99052 | 9.1263 | 9.0651 | 8.9335 | 8.7029 | 8.3498 | 7.8151 | 7.2916 | 6.5008 | 5.5957 | 3.5151 | 2.4835 | 1.4886 | 7.8737 | 7.8502 | 7.7951 | 7.69 | 7.3992 | 6.8543 | 6.3074 | 5.49 | 4.5512 | 2.5829 | 1.7247 | 1.1308
|  | TRADING ESTATE PRIMARY | FB |  |  |  |  | 7.1089 | 7.1079 | 7.0926 | 7.062 | 7.0313 | 6.9762 | 6.7834 | 6.5058 | 6.1987 | 4.1405 | 3.1222 | 1.4324 | 9.1427 | 9.0467 | 8.9223 | 8.809 | 8.6916 | 8.5202 | 8.1865 | 7.8539 | 7.4529 | 4.7049 | 2.5967 | -0.14713 | 7.9063 | 7.887 | 7.8523 | 7.8053 | 7.7594 | 7.6992 | 7.5125 | 7.2421 | 6.888 | 4.4716 | 2.9808 | 1.3451
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | TRASH GREEN PRIMARY | MINIMUM HEADROOM | SU 66254 68745 | NO | NO | 3.331 | 2.5438 | 2.5683 | 2.4122 | 2.3642 | 2.1785 | 1.905 | 1.5989 | 1.2407 | 0.87644 | -0.31437 | -0.66641 | -0.69192 | 4.2657 | 4.2188 | 3.9157 | 3.8076 | 3.5382 | 3.2198 | 2.8698 | 2.4474 | 2.0239 | 0.56981 | 0.22287 | -0.4006 | 3.2504 | 3.2606 | 3.0627 | 3.0004 | 2.7872 | 2.477 | 2.1382 | 1.729 | 1.3188 | -0.067943 | -0.39549 | -0.38835
|  | TRASH GREEN PRIMARY | EE |  |  |  |  | 2.5438 | 2.5713 | 2.4469 | 2.4581 | 2.3438 | 2.1142 | 1.8734 | 1.5785 | 1.2856 | 0.1142 | -0.3358 | -0.32356 | 4.2668 | 4.2208 | 3.9382 | 3.8616 | 3.6484 | 3.3402 | 3.0188 | 2.6372 | 2.2545 | 0.76165 | 0.22696 | 0.068792 | 3.2504 | 3.2616 | 3.0882 | 3.0678 | 2.9157 | 2.6351 | 2.3361 | 1.9759 | 1.6198 | 0.28002 | -0.14447 | -0.10774
|  | TRASH GREEN PRIMARY | HT |  |  |  |  | 2.5438 | 2.5693 | 2.4122 | 2.3642 | 2.1785 | 1.905 | 1.5989 | 1.2407 | 0.87644 | -0.31437 | -0.66641 | -0.69192 | 4.2657 | 4.2188 | 3.9157 | 3.8076 | 3.5382 | 3.2198 | 2.8698 | 2.4474 | 2.0239 | 0.56981 | 0.22287 | 0.20451 | 3.2504 | 3.2616 | 3.0627 | 3.0004 | 2.7872 | 2.477 | 2.1382 | 1.729 | 1.3188 | -0.067943 | -0.39549 | -0.38835
|  | TRASH GREEN PRIMARY | HE |  |  |  |  | 2.5438 | 2.5683 | 2.4469 | 2.4581 | 2.3418 | 2.1111 | 1.8815 | 1.5958 | 1.3122 | 0.37032 | -0.094984 | -0.23886 | 4.2668 | 4.2188 | 3.9361 | 3.8606 | 3.6433 | 3.331 | 3.0361 | 2.6555 | 2.277 | 1.0168 | 0.45349 | 0.129 | 3.2504 | 3.2606 | 3.0882 | 3.0668 | 2.9116 | 2.63 | 2.3555 | 1.9994 | 1.6463 | 0.529 | 0.085118 | -0.039371
|  | TRASH GREEN PRIMARY | FB |  |  |  |  | 2.6673 | 2.7387 | 2.7938 | 2.8336 | 2.8601 | 2.8948 | 2.7479 | 2.6805 | 2.5744 | 1.8754 | 0.94175 | 0.404 | 4.3729 | 4.3668 | 4.3474 | 4.3137 | 4.2627 | 4.2494 | 3.9127 | 3.7719 | 3.5759 | 2.3963 | 0.96675 | -0.4006 | 3.3678 | 3.4168 | 3.4555 | 3.481 | 3.4963 | 3.5239 | 3.3239 | 3.2382 | 3.1035 | 2.2168 | 1.1351 | 0.52593
MELKSHAM GSP | NORRINGTON BSP | TROWBRIDGE TOWN PRIMARY | MINIMUM HEADROOM | ST 84668 58036 | NO | YES | 5.759 | 13.3738 | 13.4524 | 13.5014 | 13.3881 | 13.1861 | 12.8065 | 12.3432 | 11.7901 | 11.2932 | 9.2565 | 7.4054 | 6.5708 | 17.0993 | 17.1085 | 17.0473 | 16.8912 | 16.6646 | 16.2544 | 15.7003 | 15.035 | 14.5575 | 12.2595 | 9.685 | 5.7728 | 14.6473 | 14.682 | 14.6881 | 14.5269 | 14.2708 | 13.8391 | 13.285 | 12.6218 | 12.1269 | 10.0432 | 8.3718 | 7.7412
|  | TROWBRIDGE TOWN PRIMARY | EE |  |  |  |  | 13.3738 | 13.4524 | 13.5146 | 13.4422 | 13.2718 | 12.9371 | 12.5452 | 12.0871 | 11.7014 | 9.6156 | 7.5973 | 6.6054 | 17.0993 | 17.1085 | 17.0534 | 16.9156 | 16.7034 | 16.3085 | 15.8075 | 15.1779 | 14.7677 | 12.2595 | 10.134 | 8.6534 | 14.6473 | 14.682 | 14.6952 | 14.5503 | 14.3238 | 13.9208 | 13.4269 | 12.8361 | 12.433 | 10.2871 | 8.4646 | 7.7412
|  | TROWBRIDGE TOWN PRIMARY | HT |  |  |  |  | 13.3738 | 13.4524 | 13.5014 | 13.3881 | 13.1861 | 12.8065 | 12.3432 | 11.7901 | 11.2932 | 9.2565 | 7.4054 | 6.5708 | 17.1003 | 17.1085 | 17.0473 | 16.8912 | 16.6646 | 16.2544 | 15.7003 | 15.035 | 14.5575 | 12.5116 | 11.0391 | 10.6983 | 14.6473 | 14.683 | 14.6881 | 14.5269 | 14.2708 | 13.8391 | 13.285 | 12.6218 | 12.1269 | 10.0432 | 8.3718 | 7.8973
|  | TROWBRIDGE TOWN PRIMARY | HE |  |  |  |  | 13.3738 | 13.4524 | 13.5136 | 13.4259 | 13.2463 | 12.9514 | 12.584 | 12.1391 | 11.782 | 10.0156 | 8.5412 | 7.8065 | 17.0993 | 17.1085 | 17.0534 | 16.9126 | 16.7034 | 16.3156 | 15.7952 | 15.1534 | 14.7442 | 12.3779 | 10.6544 | 9.181 | 14.6473 | 14.683 | 14.6952 | 14.5442 | 14.3054 | 13.931 | 13.4361 | 12.8524 | 12.4677 | 10.5779 | 9.2973 | 8.7473
|  | TROWBRIDGE TOWN PRIMARY | FB |  |  |  |  | 13.5248 | 13.6667 | 13.7493 | 13.7973 | 13.8493 | 13.732 | 13.6432 | 13.5136 | 13.3656 | 12.3391 | 10.3503 | 9.0881 | 17.1728 | 17.2146 | 17.1677 | 17.0891 | 16.9881 | 16.7034 | 16.4432 | 16.1238 | 15.735 | 13.2177 | 9.685 | 5.7728 | 14.7912 | 14.8759 | 14.9136 | 14.9228 | 14.8901 | 14.7565 | 14.6483 | 14.5065 | 14.3452 | 12.883 | 10.8871 | 9.6238
BRAMLEY (BASI) GSP | READING BSP | TWYFORD PRIMARY | MINIMUM HEADROOM | SU 78430 76339 | NO | YES | 0.91 | 2.524 | 2.6148 | 2.2699 | 1.9668 | 1.6066 | 1.0699 | 0.40969 | -0.31888 | -0.94541 | -2.8913 | -4.0077 | -4.5332 | 6.3745 | 6.3796 | 5.9673 | 5.6449 | 5.248 | 4.7582 | 4.1235 | 3.4204 | 2.8531 | 0.91327 | -0.41633 | -2.7194 | 2.9286 | 2.9908 | 2.6724 | 2.3806 | 1.9959 | 1.4745 | 0.80714 | 0.067347 | -0.54388 | -2.4949 | -3.4622 | -3.749
|  | TWYFORD PRIMARY | EE |  |  |  |  | 2.525 | 2.6281 | 2.3158 | 2.0658 | 1.7689 | 1.3077 | 0.67092 | -0.0066327 | -0.575 | -2.5536 | -3.7291 | -4.2526 | 6.3745 | 6.3878 | 5.9959 | 5.7071 | 5.351 | 4.9296 | 4.3276 | 3.6541 | 3.1245 | 0.91327 | -0.41633 | -1.398 | 2.9296 | 3.001 | 2.7051 | 2.4602 | 2.1286 | 1.6796 | 1.0439 | 0.3449 | -0.22245 | -2.2296 | -3.298 | -3.6878
|  | TWYFORD PRIMARY | HT |  |  |  |  | 2.524 | 2.6148 | 2.2699 | 1.9668 | 1.6066 | 1.0699 | 0.40969 | -0.31888 | -0.94541 | -2.8913 | -4.0077 | -4.5332 | 6.3755 | 6.3796 | 5.9673 | 5.6449 | 5.248 | 4.7582 | 4.1235 | 3.4204 | 2.8531 | 0.97959 | 0.12041 | -0.10306 | 2.9296 | 2.9908 | 2.6724 | 2.3806 | 1.9959 | 1.4745 | 0.80714 | 0.067347 | -0.54388 | -2.4949 | -3.4622 | -3.749
|  | TWYFORD PRIMARY | HE |  |  |  |  | 2.524 | 2.6281 | 2.3128 | 2.0628 | 1.7536 | 1.2974 | 0.67092 | -0.0045918 | -0.56888 | -2.2536 | -3.2015 | -3.7168 | 6.3745 | 6.3857 | 5.9929 | 5.7041 | 5.3286 | 4.9092 | 4.3082 | 3.6469 | 3.1306 | 1.0949 | 0.060204 | -0.99184 | 2.9286 | 3 | 2.702 | 2.4571 | 2.1082 | 1.6653 | 1.0327 | 0.34184 | -0.21224 | -1.952 | -2.6898 | -3.0908
|  | TWYFORD PRIMARY | FB |  |  |  |  | 2.7801 | 2.873 | 2.827 | 2.8607 | 2.7015 | 2.5638 | 2.4168 | 2.176 | 1.9587 | 0.79031 | -0.55255 | -1.3679 | 6.5673 | 6.5255 | 6.4092 | 6.3755 | 6.0459 | 5.7633 | 5.4969 | 5.1194 | 4.7714 | 2.6918 | 0.11429 | -2.7194 | 3.1827 | 3.2418 | 3.2071 | 3.248 | 3.0755 | 2.9276 | 2.7786 | 2.502 | 2.2592 | 0.9051 | -0.50204 | -1.4092
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | UNION STREET PRIMARY | MINIMUM HEADROOM | SP 52865 05849 | NO | NO | 4.137 | 6.4927 | 6.5171 | 6.4559 | 6.3794 | 5.812 | 5.0406 | 4.2998 | 3.4692 | 2.6355 | -0.049184 | -1.7543 | -2.9369 | 13.0435 | 12.9782 | 12.7996 | 12.6955 | 12.2924 | 11.8139 | 11.32 | 10.7567 | 10.1384 | 8.168 | 5.6853 | 1.4496 | 8.61 | 8.612 | 8.5069 | 8.4641 | 7.9957 | 7.3855 | 6.7865 | 6.1049 | 5.3896 | 3.1712 | 1.4457 | 0.44878
|  | UNION STREET PRIMARY | EE |  |  |  |  | 6.4927 | 6.5171 | 6.4559 | 6.408 | 5.8947 | 5.1661 | 4.5182 | 3.8416 | 3.3447 | 0.45286 | -1.7543 | -2.9369 | 13.0435 | 12.9782 | 12.8159 | 12.7465 | 12.3843 | 11.9486 | 11.5088 | 11.0333 | 10.6935 | 8.168 | 6.3149 | 4.5894 | 8.61 | 8.612 | 8.5069 | 8.4773 | 8.0559 | 7.4743 | 6.9416 | 6.3773 | 5.9753 | 3.3406 | 1.4457 | 0.44878
|  | UNION STREET PRIMARY | HT |  |  |  |  | 6.5253 | 6.5733 | 6.4855 | 6.3794 | 5.812 | 5.0406 | 4.2998 | 3.4692 | 2.6355 | -0.049184 | -1.5216 | -2.1165 | 13.0455 | 12.9792 | 12.7996 | 12.6955 | 12.2924 | 11.8139 | 11.32 | 10.7567 | 10.1384 | 8.2169 | 7.1782 | 6.7118 | 8.6376 | 8.66 | 8.5406 | 8.4641 | 7.9957 | 7.3855 | 6.7865 | 6.1049 | 5.3896 | 3.1712 | 2.0467 | 1.709
|  | UNION STREET PRIMARY | HE |  |  |  |  | 6.508 | 6.5437 | 6.4957 | 6.4212 | 5.8773 | 5.212 | 4.659 | 4.0376 | 3.5865 | 1.4692 | 0.13755 | -0.59204 | 13.0476 | 12.9822 | 12.8241 | 12.7567 | 12.3873 | 11.9506 | 11.5424 | 11.0608 | 10.7088 | 8.5812 | 7.0873 | 5.5567 | 8.6253 | 8.6386 | 8.5467 | 8.4998 | 8.0529 | 7.5069 | 7.0416 | 6.5029 | 6.1243 | 4.2284 | 3.1355 | 2.5896
|  | UNION STREET PRIMARY | FB |  |  |  |  | 6.6804 | 6.762 | 6.8151 | 6.8416 | 6.5896 | 6.3845 | 6.1437 | 5.9222 | 5.7141 | 4.3784 | 2.558 | 1.1437 | 13.12 | 13.0435 | 12.9404 | 12.8424 | 12.5833 | 12.3445 | 12.0006 | 11.7027 | 11.3506 | 9.0353 | 5.6853 | 1.4496 | 8.7937 | 8.8498 | 8.8712 | 8.8753 | 8.6896 | 8.5437 | 8.3304 | 8.1467 | 7.9396 | 6.5988 | 4.8539 | 3.458
COWLEY GSP | OXFORD (OSNEY) BSP | UNIVERSITY PARKS PRIMARY | MINIMUM HEADROOM | SP 51472 07052 | NO | YES | 0.982 | 18.7924 | 18.7241 | 18.67 | 18.6363 | 18.5965 | 18.5149 | 18.42 | 18.2751 | 18.1577 | 17.6424 | 17.2822 | 17.0669 | 22.9822 | 22.9414 | 22.9026 | 22.8761 | 22.8435 | 22.7904 | 22.7312 | 22.619 | 22.5343 | 22.2128 | 22.0261 | 21.8577 | 20.6792 | 20.622 | 20.5751 | 20.5465 | 20.5159 | 20.4496 | 20.3771 | 20.2557 | 20.1577 | 19.7649 | 19.5037 | 19.3506
|  | UNIVERSITY PARKS PRIMARY | EE |  |  |  |  | 18.8037 | 18.7445 | 18.6986 | 18.6761 | 18.6496 | 18.571 | 18.4986 | 18.3741 | 18.2822 | 17.769 | 17.3669 | 17.1271 | 22.9924 | 22.9577 | 22.9282 | 22.9077 | 22.8812 | 22.8343 | 22.7873 | 22.6833 | 22.6118 | 22.3016 | 22.0965 | 21.9741 | 20.6935 | 20.6404 | 20.6047 | 20.5873 | 20.5628 | 20.5057 | 20.4496 | 20.3435 | 20.271 | 19.8751 | 19.57 | 19.3904
|  | UNIVERSITY PARKS PRIMARY | HT |  |  |  |  | 18.7924 | 18.7241 | 18.67 | 18.6363 | 18.5965 | 18.5149 | 18.42 | 18.2751 | 18.1577 | 17.6424 | 17.2822 | 17.0669 | 22.9822 | 22.9414 | 22.9026 | 22.8761 | 22.8435 | 22.7904 | 22.7312 | 22.619 | 22.5343 | 22.2128 | 22.0261 | 21.9231 | 20.6792 | 20.622 | 20.5751 | 20.5465 | 20.5159 | 20.4496 | 20.3771 | 20.2557 | 20.1577 | 19.7649 | 19.5037 | 19.3506
|  | UNIVERSITY PARKS PRIMARY | HE |  |  |  |  | 18.8026 | 18.7465 | 18.6996 | 18.671 | 18.6373 | 18.57 | 18.5037 | 18.4077 | 18.3139 | 17.9986 | 17.7731 | 17.6669 | 22.9924 | 22.9577 | 22.9271 | 22.9067 | 22.8792 | 22.8343 | 22.7894 | 22.719 | 22.6363 | 22.4516 | 22.3435 | 22.3098 | 20.6935 | 20.6414 | 20.6067 | 20.5863 | 20.5577 | 20.5037 | 20.4526 | 20.3731 | 20.2945 | 20.0659 | 19.9088 | 19.8455
|  | UNIVERSITY PARKS PRIMARY | FB |  |  |  |  | 18.822 | 18.7741 | 18.7414 | 18.7292 | 18.7128 | 18.6924 | 18.669 | 18.6384 | 18.6108 | 18.4996 | 18.3271 | 18.2149 | 23.0037 | 22.9741 | 22.9537 | 22.9384 | 22.922 | 22.9057 | 22.8853 | 22.8588 | 22.8333 | 22.7251 | 22.5731 | 21.8577 | 20.7067 | 20.6659 | 20.6414 | 20.6261 | 20.6149 | 20.5965 | 20.5771 | 20.5506 | 20.5322 | 20.4343 | 20.2904 | 20.2047
EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD PRIMARY | MINIMUM HEADROOM | SP 51750 25667 | NO | YES | 5.45 | 2.5907 | 2.2632 | 1.2856 | 0.086633 | -2.5848 | -4.3603 | -6.2562 | -8.0379 | -9.845 | -12.4379 | -13.047 | -13.4756 | 4.8096 | 4.6106 | 4.1627 | 3.7137 | 1.6973 | 1.0576 | 0.43612 | -0.25469 | -0.94245 | -2.619 | -2.8771 | -2.9792 | 3.4535 | 3.1433 | 2.3667 | 1.579 | -0.94449 | -2.1659 | -3.3486 | -4.6149 | -5.869 | -8.1292 | -8.5792 | -8.8241
|  | UPPER HEYFORD PRIMARY | EE |  |  |  |  | 2.5917 | 2.2632 | 1.2856 | 0.086633 | -2.3726 | -4.3113 | -6.2562 | -8.0032 | -9.7532 | -11.6236 | -11.6879 | -11.794 | 4.8769 | 4.7167 | 4.3422 | 3.9412 | 2.081 | 1.5422 | 1.0076 | 0.41469 | -0.16796 | -1.7924 | -2.1271 | -2.3373 | 3.4953 | 3.2065 | 2.4514 | 1.6933 | -0.68939 | -1.9506 | -3.171 | -4.3639 | -5.5578 | -7.3057 | -7.4771 | -7.572
|  | UPPER HEYFORD PRIMARY | HT |  |  |  |  | 2.5989 | 2.2795 | 1.2856 | 0.098878 | -2.5848 | -4.3603 | -6.0695 | -7.8603 | -9.6368 | -12.4379 | -13.047 | -13.4756 | 4.8096 | 4.6106 | 4.1627 | 3.7137 | 1.6973 | 1.0576 | 0.43612 | -0.25469 | -0.94245 | -2.619 | -2.8771 | -2.9792 | 3.4535 | 3.1433 | 2.3667 | 1.579 | -0.94449 | -2.1659 | -3.3486 | -4.6149 | -5.869 | -8.1292 | -8.5792 | -8.8241
|  | UPPER HEYFORD PRIMARY | HE |  |  |  |  | 2.5907 | 2.2652 | 1.2907 | 0.086633 | -2.3736 | -4.3001 | -6.2174 | -8.0379 | -9.845 | -11.6083 | -11.4593 | -11.497 | 4.878 | 4.7178 | 4.3422 | 3.9422 | 2.0831 | 1.5535 | 1.0422 | 0.46163 | -0.10878 | -1.6843 | -1.8618 | -2.0578 | 3.4943 | 3.2076 | 2.4545 | 1.6943 | -0.68939 | -1.9414 | -3.1404 | -4.3578 | -5.5741 | -7.1802 | -7.1608 | -7.2231
|  | UPPER HEYFORD PRIMARY | FB |  |  |  |  | 2.7683 | 2.5785 | 2.0826 | 1.2295 | -0.82663 | -2.6256 | -3.9797 | -5.2083 | -6.4899 | -8.646 | -9.1583 | -9.495 | 4.9178 | 4.779 | 4.5402 | 4.2637 | 2.3545 | 1.1422 | 0.65959 | 0.22694 | -0.23633 | -1.1976 | -1.769 | -2.3751 | 3.6351 | 3.4443 | 3.0382 | 2.5147 | 0.40449 | -0.93837 | -1.8986 | -2.6996 | -3.5771 | -5.171 | -5.6965 | -6.0853
IVER 132KV GSP | UPTON BSP | UPTON PRIMARY | MINIMUM HEADROOM | TQ 00800 79434 | NO | YES | 4.681 | 11.9884 | 11.9976 | 11.9619 | 11.9343 | 11.7905 | 11.418 | 10.6129 | 9.9088 | 9.0731 | 5.6803 | 3.2711 | 2.2119 | 16.6767 | 16.6186 | 16.5012 | 16.3339 | 16.0645 | 15.7288 | 15.039 | 14.1992 | 13.2461 | 9.3716 | 6.6931 | 2.8339 | 12.6776 | 12.6929 | 12.5867 | 12.498 | 12.2541 | 11.8347 | 11.0429 | 10.2653 | 9.3592 | 5.7102 | 3.2724 | 2.2622
|  | UPTON PRIMARY | EE |  |  |  |  | 11.9884 | 11.9976 | 11.9619 | 11.9343 | 11.8027 | 11.4282 | 10.6129 | 9.9088 | 9.0731 | 5.6803 | 3.2711 | 2.2119 | 16.6767 | 16.6186 | 16.5012 | 16.3349 | 16.0645 | 15.7308 | 15.039 | 14.1992 | 13.2461 | 9.3716 | 6.6931 | 4.3594 | 12.6776 | 12.6929 | 12.5867 | 12.498 | 12.2571 | 11.8347 | 11.0429 | 10.2653 | 9.3592 | 5.7102 | 3.2724 | 2.2622
|  | UPTON PRIMARY | HT |  |  |  |  | 12.0037 | 12.0252 | 11.9986 | 11.9466 | 11.7905 | 11.418 | 10.7578 | 10.0547 | 9.219 | 6.3211 | 4.5578 | 4.218 | 16.6767 | 16.6206 | 16.5043 | 16.3339 | 16.0665 | 15.7288 | 15.2298 | 14.441 | 13.5267 | 10.5624 | 9.1216 | 8.7186 | 12.6929 | 12.7194 | 12.6265 | 12.5143 | 12.2541 | 11.8357 | 11.2418 | 10.4969 | 9.6184 | 6.4796 | 4.6622 | 4.3092
|  | UPTON PRIMARY | HE |  |  |  |  | 12.0088 | 12.0354 | 12.019 | 11.9792 | 11.8343 | 11.517 | 10.8752 | 10.2619 | 9.6282 | 7.6425 | 6.2649 | 5.6598 | 16.6798 | 16.6216 | 16.5073 | 16.339 | 16.0706 | 15.7553 | 15.2931 | 14.5604 | 13.8186 | 11.1502 | 9.0288 | 6.8482 | 12.698 | 12.7265 | 12.6388 | 12.5367 | 12.2776 | 11.9122 | 11.3429 | 10.6898 | 10.0071 | 7.8745 | 6.4898 | 5.9082
|  | UPTON PRIMARY | FB |  |  |  |  | 12.2109 | 12.2241 | 12.3701 | 12.5588 | 12.6456 | 12.568 | 12.4466 | 12.3752 | 12.1966 | 10.8996 | 8.3629 | 6.6945 | 16.8155 | 16.8135 | 16.8471 | 16.8716 | 16.8359 | 16.6971 | 16.5002 | 16.1573 | 15.6951 | 12.7176 | 8.0655 | 2.8339 | 12.9214 | 12.9367 | 13.0388 | 13.1898 | 13.2398 | 13.1061 | 12.9755 | 12.8592 | 12.6133 | 11.2071 | 8.6541 | 7.0031
IVER 66KV GSP |  | UXBRIDGE PRIMARY | MINIMUM HEADROOM | TQ 04984 83484 | NO | NO | 32.331 | 0.059094 | 40.1809 | 39.2871 | 38.3789 | 37.3156 | 36.1054 | 34.7799 | 33.4452 | 32.0717 | 28.7003 | 26.4371 | 25.5473 | 11.4162 | 48.2911 | 47.286 | 46.3197 | 45.2228 | 44.0605 | 42.785 | 41.4942 | 40.1728 | 38.0279 | 36.2483 | 32.185 | 7.0968 | 42.3279 | 41.3871 | 40.4422 | 39.3901 | 38.2146 | 36.9442 | 35.6503 | 34.3401 | 31.9238 | 29.9228 | 29.033
|  | UXBRIDGE PRIMARY | EE |  |  |  |  | 0.059094 | 41.3871 | 39.9993 | 39.033 | 38.0564 | 36.9095 | 35.6411 | 34.3666 | 33.0524 | 29.4809 | 27.4524 | 26.483 | 11.4173 | 49.582 | 48.1697 | 47.1146 | 46.0942 | 45.0105 | 43.8166 | 42.6115 | 41.383 | 38.5105 | 36.3615 | 34.736 | 7.0968 | 43.7034 | 42.2493 | 41.2707 | 40.334 | 39.2636 | 38.0993 | 36.9166 | 35.7136 | 32.2728 | 29.9228 | 29.033
|  | UXBRIDGE PRIMARY | HT |  |  |  |  | 0.072359 | 40.1809 | 39.2871 | 38.3789 | 37.3156 | 36.1054 | 34.7799 | 33.4452 | 32.0717 | 28.7003 | 26.4371 | 25.5473 | 11.4162 | 48.2911 | 47.286 | 46.3197 | 45.2228 | 44.0605 | 42.785 | 41.4942 | 40.1728 | 38.0279 | 37.0993 | 36.8279 | 7.1009 | 42.3279 | 41.3871 | 40.4422 | 39.3901 | 38.2146 | 36.9442 | 35.6503 | 34.3401 | 31.9238 | 30.0411 | 29.4544
|  | UXBRIDGE PRIMARY | HE |  |  |  |  | 0.065216 | 41.3983 | 40.0177 | 39.0238 | 38.1432 | 37.0003 | 35.733 | 34.4554 | 33.1442 | 30.1177 | 28.7677 | 28.0728 | 11.4183 | 49.5789 | 48.1687 | 47.1085 | 46.2309 | 45.1483 | 43.9575 | 42.7534 | 41.5299 | 38.8993 | 37.3891 | 35.7717 | 7.0968 | 43.7075 | 42.2564 | 41.2605 | 40.4585 | 39.3942 | 38.232 | 37.0483 | 35.8513 | 33.2085 | 31.8738 | 31.1187
|  | UXBRIDGE PRIMARY | FB |  |  |  |  | 0.24379 | 41.6636 | 41.6656 | 40.3677 | 39.4483 | 38.733 | 37.985 | 37.184 | 36.4166 | 33.6136 | 31.7401 | 30.5126 | 11.4887 | 49.6483 | 49.6105 | 48.4034 | 47.2309 | 46.2891 | 45.2983 | 44.286 | 43.2911 | 39.7279 | 36.2483 | 32.185 | 7.2652 | 43.9136 | 43.9575 | 42.5809 | 41.5881 | 40.8105 | 39.9901 | 39.1442 | 38.3177 | 35.6687 | 34.1473 | 32.4575
NURSLING GSP | VELMORE BSP | VELMORE PRIMARY | MINIMUM HEADROOM | SU 42935 19205 | NO | YES | 3.97 | 4.0579 | 3.911 | 3.7426 | 3.4406 | 3.0375 | 2.4181 | 1.7079 | 0.9018 | 0.10078 | -2.8645 | -4.3594 | -4.8717 | 9.3967 | 9.364 | 9.2467 | 9.0742 | 8.8447 | 8.512 | 8.1294 | 7.5263 | 6.7885 | 3.7559 | 0.85996 | -3.7645 | 6.0855 | 6.0436 | 5.8753 | 5.6191 | 5.2691 | 4.7732 | 4.2028 | 3.5079 | 2.7947 | -0.11351 | -1.436 | -1.7768
|  | VELMORE PRIMARY | EE |  |  |  |  | 4.0579 | 3.911 | 3.7426 | 3.4579 | 3.0804 | 2.4712 | 1.7824 | 1.0794 | 0.37425 | -2.2758 | -3.5227 | -4.0819 | 9.4018 | 9.3732 | 9.262 | 9.0936 | 8.8732 | 8.562 | 8.1906 | 7.6732 | 6.9671 | 3.7559 | 1.9528 | 0.27629 | 6.0875 | 6.0436 | 5.8753 | 5.6314 | 5.3028 | 4.8171 | 4.2559 | 3.6732 | 3.0263 | 0.19772 | -1.1798 | -1.7758
|  | VELMORE PRIMARY | HT |  |  |  |  | 4.063 | 3.9314 | 3.7783 | 3.4528 | 3.0416 | 2.4181 | 1.7079 | 0.9018 | 0.10078 | -2.8645 | -4.3594 | -4.8717 | 9.3987 | 9.3702 | 9.2549 | 9.0804 | 8.8447 | 8.512 | 8.1294 | 7.5263 | 6.7885 | 4.1406 | 3.0987 | 2.7538 | 6.0875 | 6.06 | 5.8998 | 5.6253 | 5.2691 | 4.7732 | 4.2028 | 3.5079 | 2.7947 | -0.11351 | -1.436 | -1.7768
|  | VELMORE PRIMARY | HE |  |  |  |  | 4.062 | 3.9181 | 3.7518 | 3.4406 | 3.0375 | 2.4732 | 1.8222 | 1.1447 | 0.46915 | -1.9258 | -3.0043 | -3.4992 | 9.3967 | 9.364 | 9.2467 | 9.0742 | 8.8487 | 8.5416 | 8.1559 | 7.6794 | 6.963 | 4.0457 | 2.4089 | 0.61915 | 6.0855 | 6.0549 | 5.8865 | 5.6191 | 5.2712 | 4.8212 | 4.2845 | 3.711 | 3.0773 | 0.60384 | -0.44106 | -0.95942
|  | VELMORE PRIMARY | FB |  |  |  |  | 4.214 | 4.1916 | 4.213 | 4.1691 | 3.9855 | 3.7753 | 3.563 | 3.2783 | 2.9885 | 1.1702 | -0.58289 | -1.4206 | 9.4661 | 9.4038 | 9.3589 | 9.314 | 9.1222 | 8.8763 | 8.614 | 8.3069 | 7.9549 | 5.0304 | 0.85996 | -3.7645 | 6.2753 | 6.2681 | 6.2834 | 6.2661 | 6.0957 | 5.9222 | 5.7518 | 5.51 | 5.2763 | 3.6661 | 1.6355 | 0.41813
FAWLEY GSP | COWES BSP | VENTNOR PRIMARY | MINIMUM HEADROOM | SZ 56148 77857 | NO | YES | 0.44 | 11.5455 | 11.619 | 11.521 | 11.2598 | 10.8935 | 10.3057 | 9.5884 | 8.818 | 8.1751 | 5.4496 | 3.1904 | 1.7976 | 13.9731 | 13.968 | 13.7884 | 13.5945 | 13.32 | 12.9904 | 12.5669 | 12.0771 | 11.7139 | 9.9792 | 8.6598 | 6.2853 | 12.7761 | 12.819 | 12.6333 | 12.4169 | 12.0822 | 11.6363 | 11.0649 | 10.4445 | 9.9588 | 7.8282 | 6.3373 | 5.6118
|  | VENTNOR PRIMARY | EE |  |  |  |  | 11.5455 | 11.6241 | 11.5527 | 11.3373 | 11.0231 | 10.4608 | 9.8455 | 9.0822 | 8.4914 | 5.8873 | 3.7924 | 2.6118 | 13.9731 | 13.9731 | 13.8067 | 13.6333 | 13.3822 | 13.07 | 12.7292 | 12.2302 | 11.8986 | 9.9792 | 8.6598 | 7.6863 | 12.7761 | 12.821 | 12.6578 | 12.4761 | 12.1792 | 11.7547 | 11.2802 | 10.6506 | 10.2078 | 8.1006 | 6.6118 | 5.9078
|  | VENTNOR PRIMARY | HT |  |  |  |  | 11.5486 | 11.619 | 11.521 | 11.2598 | 10.8935 | 10.3057 | 9.5884 | 8.818 | 8.1751 | 5.4496 | 3.1904 | 1.7976 | 13.9741 | 13.968 | 13.7884 | 13.5945 | 13.32 | 12.9904 | 12.5669 | 12.0771 | 11.7139 | 10.0945 | 9.2527 | 9.0098 | 12.7792 | 12.819 | 12.6333 | 12.4169 | 12.0822 | 11.6363 | 11.0649 | 10.4445 | 9.9588 | 7.8282 | 6.3373 | 5.6118
|  | VENTNOR PRIMARY | HE |  |  |  |  | 11.5455 | 11.6251 | 11.5567 | 11.3057 | 10.9496 | 10.4016 | 9.7261 | 9.0302 | 8.3343 | 6.3965 | 4.4006 | 3.4669 | 13.9741 | 13.972 | 13.8067 | 13.6292 | 13.3649 | 13.1027 | 12.7057 | 12.2986 | 11.8822 | 10.271 | 8.9884 | 8.0363 | 12.7771 | 12.822 | 12.6588 | 12.4598 | 12.1343 | 11.7363 | 11.2129 | 10.6761 | 10.1271 | 8.5476 | 7.1394 | 6.5802
|  | VENTNOR PRIMARY | FB |  |  |  |  | 11.7067 | 11.8435 | 11.9527 | 12.0292 | 12.0741 | 12.1037 | 11.8424 | 11.6373 | 11.4639 | 10.1384 | 8.4149 | 7.3873 | 14.0761 | 14.0873 | 14.0822 | 14.0424 | 13.9822 | 13.9149 | 13.5363 | 13.2547 | 12.9884 | 11.2506 | 8.8333 | 6.2853 | 12.9445 | 13.0404 | 13.1027 | 13.1271 | 13.1547 | 13.1853 | 12.8822 | 12.668 | 12.4924 | 11.2394 | 9.6843 | 8.7578
MANNINGTON GSP | MANNINGTON BSP | VERWOOD PRIMARY | MINIMUM HEADROOM | SU 07716 10226 | NO | NO | 0.558 | 3.7755 | 3.7551 | 3.4735 | 2.9908 | 2.3541 | 1.2388 | -0.030612 | -1.3367 | -2.599 | -6.7194 | -9.8357 | -11.4673 | 6.5765 | 6.5541 | 6.3592 | 6.1031 | 5.6724 | 5.1163 | 4.4704 | 3.7908 | 3.1602 | 1.299 | 0.3602 | -2.0224 | 5.7163 | 5.7071 | 5.4633 | 5.0816 | 4.4857 | 3.599 | 2.6286 | 1.6327 | 0.68571 | -2.2735 | -4.1878 | -4.9816
|  | VERWOOD PRIMARY | EE |  |  |  |  | 3.7898 | 3.8 | 3.6061 | 3.2714 | 2.799 | 1.7949 | 0.69592 | -0.54184 | -1.6459 | -5.0245 | -7.6878 | -9.1918 | 6.5867 | 6.5816 | 6.4255 | 6.2296 | 5.8398 | 5.3776 | 4.8388 | 4.1857 | 3.6643 | 1.5908 | 0.3602 | -0.51429 | 5.7286 | 5.7459 | 5.5694 | 5.2959 | 4.8102 | 4.0296 | 3.1898 | 2.2429 | 1.4316 | -1.1173 | -2.8214 | -3.6296
|  | VERWOOD PRIMARY | HT |  |  |  |  | 3.7755 | 3.7551 | 3.4735 | 2.9908 | 2.3541 | 1.2388 | -0.030612 | -1.3367 | -2.599 | -6.7194 | -9.8357 | -11.4673 | 6.5765 | 6.5541 | 6.3592 | 6.1031 | 5.6724 | 5.1163 | 4.4704 | 3.7908 | 3.1602 | 1.299 | 0.47653 | 0.34286 | 5.7163 | 5.7071 | 5.4633 | 5.0816 | 4.4857 | 3.599 | 2.6286 | 1.6327 | 0.68571 | -2.2735 | -4.1878 | -4.9816
|  | VERWOOD PRIMARY | HE |  |  |  |  | 3.7888 | 3.801 | 3.6082 | 3.251 | 2.7745 | 1.7 | 0.54694 | -0.71122 | -1.8857 | -4.9133 | -7.3939 | -8.5418 | 6.5857 | 6.5816 | 6.4235 | 6.2245 | 5.8755 | 5.3582 | 4.8153 | 4.1888 | 3.652 | 1.6969 | 0.46837 | -0.5051 | 5.7265 | 5.7459 | 5.5694 | 5.2827 | 4.8316 | 3.9694 | 3.1031 | 2.1592 | 1.3061 | -1.0092 | -2.6286 | -3.3031
|  | VERWOOD PRIMARY | FB |  |  |  |  | 4.0408 | 4.0939 | 4.0847 | 4.099 | 4.0051 | 3.8327 | 3.6286 | 3.3969 | 3.1602 | 1.351 | -0.69082 | -1.6429 | 6.7878 | 6.7337 | 6.6643 | 6.6582 | 6.5224 | 6.2929 | 6.0235 | 5.7388 | 5.4286 | 3.1714 | 0.51837 | -2.0224 | 6.0092 | 6.0204 | 6.0235 | 6.0622 | 5.9806 | 5.8133 | 5.6153 | 5.3918 | 5.1571 | 3.301 | 1.5286 | 0.75204
NORTH HYDE GSP |  | VICARAGE FARM ROAD PRIMARY | MINIMUM HEADROOM | TQ 12358 76435 | NO | YES | 41.166 | -16.89 | 20.8489 | 20.2162 | 19.3785 | 18.5652 | 17.1101 | 15.4356 | 13.5693 | 11.4897 | 4.6774 | 0.56009 | -1.8715 | -9.0349 | 28.6131 | 28.1121 | 27.4019 | 26.5325 | 25.4264 | 24.1591 | 22.6938 | 20.9948 | 16.3989 | 12.6397 | 4.4907 | -14.9237 | 22.805 | 22.2223 | 21.4825 | 20.7019 | 19.4407 | 17.9887 | 16.3438 | 14.4713 | 8.5621 | 4.6968 | 2.604
|  | VICARAGE FARM ROAD PRIMARY | EE |  |  |  |  | -16.89 | 20.9407 | 20.2162 | 19.3785 | 18.5887 | 17.1754 | 15.7101 | 14.0703 | 12.2468 | 5.108 | 0.56009 | -1.8715 | -9.0329 | 28.7734 | 28.1121 | 27.405 | 26.7836 | 25.6948 | 24.6407 | 23.4101 | 21.9917 | 16.3989 | 12.708 | 9.4662 | -14.9237 | 22.908 | 22.2223 | 21.4825 | 20.8172 | 19.5642 | 18.307 | 16.8764 | 15.2519 | 8.6968 | 4.6968 | 2.604
|  | VICARAGE FARM ROAD PRIMARY | HT |  |  |  |  | -16.8543 | 20.8489 | 20.358 | 19.5754 | 18.5652 | 17.1101 | 15.4356 | 13.5693 | 11.4897 | 4.6774 | 0.66519 | -0.99502 | -9.0349 | 28.6131 | 28.1121 | 27.408 | 26.5325 | 25.4264 | 24.1591 | 22.6938 | 20.9948 | 16.4172 | 14.4244 | 13.8254 | -14.8931 | 22.805 | 22.3295 | 21.6172 | 20.7019 | 19.4407 | 17.9887 | 16.3438 | 14.4713 | 8.5621 | 5.2999 | 4.1662
|  | VICARAGE FARM ROAD PRIMARY | HE |  |  |  |  | -16.8706 | 20.9774 | 20.2774 | 19.4203 | 18.6244 | 17.2927 | 15.8774 | 14.2703 | 12.4734 | 7.0693 | 3.8407 | 2.0234 | -9.0329 | 28.7764 | 28.1182 | 27.4019 | 26.7836 | 25.7142 | 24.6387 | 23.3713 | 21.9172 | 17.1938 | 14.0438 | 11.1172 | -14.9053 | 22.9448 | 22.2805 | 21.5193 | 20.8438 | 19.657 | 18.4203 | 16.9938 | 15.3785 | 10.4193 | 7.6774 | 6.2366
|  | VICARAGE FARM ROAD PRIMARY | FB |  |  |  |  | -16.4829 | 21.5315 | 21.2785 | 20.8642 | 20.4815 | 20.1876 | 19.606 | 19.055 | 18.3468 | 14.5631 | 9.8958 | 6.4734 | -8.788 | 29.107 | 28.7754 | 28.3458 | 27.8917 | 27.5182 | 26.7427 | 25.9887 | 25.0672 | 19.6723 | 12.6397 | 4.4907 | -14.5431 | 23.4529 | 23.205 | 22.8264 | 22.4713 | 22.2162 | 21.6468 | 21.1285 | 20.4336 | 16.6489 | 12.1754 | 8.9029
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | WALLINGFORD PRIMARY | MINIMUM HEADROOM | SU 59847 89486 | NO | NO | 4.111 | 5.2868 | 4.8899 | 4.5817 | 4.1521 | 3.6817 | 10.2215 | 8.1919 | 6.144 | 4.4011 | -2.9713 | -17.0683 | -26.0764 | 9.2593 | 9.0144 | 8.8317 | 8.5909 | 8.2878 | 13.4491 | 11.4246 | 9.0521 | 7.9072 | 0.21744 | -15.6856 | -24.9489 | 6.646 | 6.1787 | 5.945 | 5.5511 | 5.0838 | 10.9654 | 8.8256 | 6.3297 | 4.8093 | -3.2428 | -19.3407 | -29.6458
|  | WALLINGFORD PRIMARY | EE |  |  |  |  | 5.3144 | 4.9542 | 4.6501 | 4.195 | 3.7501 | 10.2817 | 9.0705 | 7.1399 | 4.4011 | -2.7081 | -17.0683 | -22.7183 | 9.3062 | 9.094 | 8.945 | 8.7134 | 8.4399 | 13.6746 | 12.6511 | 10.7674 | 7.9072 | 0.67968 | -15.6856 | -22.0683 | 6.695 | 6.2552 | 6.0368 | 5.6348 | 5.196 | 11.0664 | 9.8715 | 7.8266 | 4.8093 | -2.7101 | -19.3407 | -25.5366
|  | WALLINGFORD PRIMARY | HT |  |  |  |  | 5.2868 | 4.8899 | 4.5817 | 4.1521 | 3.6909 | 10.2736 | 8.3736 | 6.144 | 5.3848 | -2.9713 | -16.5111 | -26.0764 | 9.2593 | 9.0144 | 8.8317 | 8.5909 | 8.2878 | 13.4491 | 11.4246 | 9.0521 | 8.5378 | 0.21744 | -14.5509 | -24.9489 | 6.646 | 6.1787 | 5.945 | 5.5511 | 5.0838 | 10.9654 | 8.8297 | 6.3297 | 5.695 | -3.2428 | -18.7254 | -29.6458
|  | WALLINGFORD PRIMARY | HE |  |  |  |  | 5.3144 | 4.9532 | 4.6419 | 4.1644 | 3.6817 | 10.2215 | 8.1919 | 7.1613 | 6.3001 | -2.1775 | -12.0836 | -20.152 | 9.3062 | 9.0919 | 8.9419 | 8.7093 | 8.4225 | 13.6725 | 11.6378 | 10.9062 | 10.4134 | 0.87356 | -10.2683 | -20.1989 | 6.694 | 6.2532 | 6.0307 | 5.6164 | 5.1338 | 11.0348 | 8.8256 | 7.9215 | 7.2583 | -2.3295 | -13.6499 | -23.1815
|  | WALLINGFORD PRIMARY | FB |  |  |  |  | 5.5134 | 5.4276 | 5.1623 | 5.046 | 4.9154 | 12.1215 | 11.6644 | 11.046 | 9.6725 | 5.2246 | -1.1693 | -6.7744 | 9.4144 | 9.3613 | 9.1827 | 9.1042 | 9.0113 | 14.5736 | 13.9174 | 13.0593 | 11.2491 | 5.3011 | -2.9479 | -11.2346 | 6.9205 | 6.846 | 6.4787 | 6.4011 | 6.2899 | 12.7297 | 12.1654 | 11.3991 | 9.6838 | 4.3072 | -3.0438 | -9.6234
COWLEY GSP | DRAYTON BSP | WANTAGE PRIMARY | MINIMUM HEADROOM | SU 41290 88304 | NO | YES | 3.658 | 9.2885 | 8.9803 | 8.6395 | 7.913 | 7.4568 | 6.7436 | 6.014 | 5.2762 | 4.5477 | 2.2079 | -0.057445 | -1.6228 | 11.8838 | 11.7072 | 11.6052 | 11.1664 | 10.894 | 10.5532 | 10.1134 | 9.6695 | 9.2266 | 7.7593 | 6.5817 | 4.8481 | 10.715 | 10.4854 | 10.2956 | 9.7221 | 9.3375 | 8.8548 | 8.2834 | 7.713 | 7.1415 | 5.1017 | 3.5364 | 2.6385
|  | WANTAGE PRIMARY | EE |  |  |  |  | 9.2926 | 8.9803 | 8.6487 | 7.9395 | 7.4701 | 6.8272 | 6.1201 | 5.3966 | 4.6885 | 2.4181 | 0.50684 | -0.54418 | 11.9348 | 11.7766 | 11.695 | 11.3277 | 11.0685 | 10.7226 | 10.3154 | 9.8889 | 9.4685 | 7.7746 | 6.5817 | 5.8654 | 10.7436 | 10.5119 | 10.315 | 9.7589 | 9.3966 | 8.9048 | 8.3466 | 7.7742 | 7.2058 | 5.2864 | 3.8619 | 3.2854
|  | WANTAGE PRIMARY | HT |  |  |  |  | 9.2885 | 9.0038 | 8.7099 | 8.016 | 7.5415 | 6.9364 | 6.2405 | 5.5272 | 4.8109 | 2.2079 | -0.057445 | -1.6228 | 11.8838 | 11.7072 | 11.6052 | 11.1664 | 10.894 | 10.5532 | 10.1134 | 9.6695 | 9.2266 | 7.7593 | 6.8572 | 6.4838 | 10.715 | 10.4854 | 10.2956 | 9.7221 | 9.3375 | 8.8681 | 8.2966 | 7.7262 | 7.1446 | 5.1017 | 3.5364 | 2.6385
|  | WANTAGE PRIMARY | HE |  |  |  |  | 9.2915 | 8.9834 | 8.6395 | 7.913 | 7.4568 | 6.7436 | 6.014 | 5.2762 | 4.5477 | 2.7426 | 1.1752 | 0.24358 | 11.9348 | 11.7766 | 11.693 | 11.3236 | 11.0909 | 10.7062 | 10.3001 | 9.8828 | 9.4695 | 7.9021 | 6.943 | 6.0899 | 10.7446 | 10.5119 | 10.3089 | 9.7426 | 9.4017 | 8.8548 | 8.2834 | 7.713 | 7.1415 | 5.5405 | 4.464 | 3.8742
|  | WANTAGE PRIMARY | FB |  |  |  |  | 9.5885 | 9.4742 | 9.2538 | 9.0038 | 8.8926 | 8.816 | 8.5303 | 8.3946 | 8.213 | 6.9977 | 5.5303 | 4.564 | 12.0409 | 11.9389 | 11.8164 | 11.6879 | 11.594 | 11.4552 | 11.1154 | 10.9287 | 10.6807 | 9.0889 | 7.0042 | 4.8481 | 10.9619 | 10.8885 | 10.7375 | 10.5681 | 10.5068 | 10.4344 | 10.1232 | 9.9915 | 9.8068 | 8.6201 | 7.2415 | 6.3813
MANNINGTON GSP | WAREHAM BSP | WAREHAM TOWN PRIMARY | MINIMUM HEADROOM | SY 92036 87463 | NO | YES | 1.517 | 3.7903 | 26.8765 | 26.6367 | 26.2745 | 25.6684 | 24.749 | 23.8367 | 22.8449 | 21.7694 | 18.2286 | 15.7653 | 14.2367 | 5.5727 | 27.0714 | 26.9704 | 26.8102 | 26.5571 | 26.2541 | 25.9173 | 25.5388 | 25.1398 | 23.0857 | 21.9673 | 21.3541 | 5.125 | 27.2459 | 27.1112 | 26.8602 | 26.498 | 25.9653 | 25.4194 | 24.8337 | 23.9837 | 21.3163 | 19.701 | 18.651
|  | WAREHAM TOWN PRIMARY | EE |  |  |  |  | 3.8158 | 26.9204 | 26.7378 | 26.4653 | 25.9857 | 25.1204 | 24.2867 | 23.3704 | 22.3806 | 19.1245 | 16.8582 | 15.4439 | 5.5819 | 27.0888 | 27.0061 | 26.8806 | 26.6684 | 26.3939 | 26.0939 | 25.7531 | 25.3949 | 23.3724 | 22.1184 | 21.3541 | 5.1352 | 27.2643 | 27.1592 | 26.9571 | 26.6561 | 26.1531 | 25.6418 | 25.0908 | 24.351 | 21.7816 | 20.3041 | 19.2276
|  | WAREHAM TOWN PRIMARY | HT |  |  |  |  | 3.7903 | 26.8765 | 26.6367 | 26.2745 | 25.6684 | 24.749 | 23.8367 | 22.8449 | 21.7694 | 18.2286 | 15.7653 | 14.2367 | 5.5727 | 27.0714 | 26.9704 | 26.8102 | 26.5571 | 26.2541 | 25.9173 | 25.5388 | 25.1398 | 23.0857 | 21.9673 | 21.4653 | 5.125 | 27.2459 | 27.1112 | 26.8602 | 26.498 | 25.9653 | 25.4194 | 24.8337 | 23.9837 | 21.3163 | 19.701 | 18.651
|  | WAREHAM TOWN PRIMARY | HE |  |  |  |  | 3.8015 | 26.9082 | 26.7276 | 26.4439 | 25.9418 | 25.0755 | 24.2327 | 23.301 | 22.2969 | 19.9847 | 18.1051 | 17.0612 | 5.5788 | 27.0857 | 27.001 | 26.8735 | 26.6561 | 26.3837 | 26.0878 | 25.7469 | 25.3878 | 24.199 | 23.2714 | 22.6357 | 5.1321 | 27.2602 | 27.1561 | 26.948 | 26.6378 | 26.1296 | 25.6143 | 25.052 | 24.3163 | 22.6388 | 21.5092 | 20.7724
|  | WAREHAM TOWN PRIMARY | FB |  |  |  |  | 3.9679 | 27.1163 | 27.0449 | 26.9602 | 26.8612 | 26.7541 | 26.5 | 26.3163 | 26.0622 | 24.3898 | 22.4745 | 20.9184 | 5.6696 | 27.1929 | 27.1673 | 27.1214 | 27.0643 | 27.0051 | 26.8847 | 26.7857 | 26.65 | 25.7969 | 24.4071 | 22.5571 | 5.2372 | 27.3949 | 27.3571 | 27.3071 | 27.2276 | 27.1388 | 26.9847 | 26.8561 | 26.6949 | 25.4398 | 23.8316 | 22.4092
FLEET-BRAMLEY GSP | BRACKNELL BSP | WARFIELD PRIMARY | MINIMUM HEADROOM | SU 86960 71382 | NO | NO | 3.959 | 7.8 | 7.8092 | 7.6551 | 7.0786 | 6.1255 | 4.6133 | 2.4755 | 0.41735 | -1.251 | -4.6684 | -8.4337 | -10.549 | 11.799 | 11.8408 | 11.7633 | 11.5592 | 11.1929 | 10.7306 | 9.9786 | 9.0316 | 8.2327 | 5.9867 | 4.2469 | 0.72245 | 9.8949 | 9.9959 | 9.9051 | 9.5337 | 8.8061 | 7.7439 | 6.3469 | 4.848 | 3.6 | 0.67653 | -1.5122 | -2.4061
|  | WARFIELD PRIMARY | EE |  |  |  |  | 7.8 | 7.8092 | 7.6806 | 7.1857 | 6.3449 | 4.6939 | 2.5827 | 0.55102 | -1.0622 | -4.5429 | -7.7714 | -9.7204 | 11.799 | 11.8418 | 11.7847 | 11.6184 | 11.3367 | 10.8847 | 10.1765 | 9.2061 | 8.4439 | 5.9867 | 4.3418 | 3.0806 | 9.8949 | 9.9959 | 9.9408 | 9.648 | 9.0796 | 7.9245 | 6.4306 | 4.8929 | 3.701 | 0.9551 | -1.0847 | -2.048
|  | WARFIELD PRIMARY | HT |  |  |  |  | 7.8061 | 7.8255 | 7.6551 | 7.0786 | 6.1255 | 4.6449 | 2.8541 | 1.1337 | -0.26633 | -4.6684 | -8.4337 | -10.549 | 11.8 | 11.8408 | 11.7633 | 11.5592 | 11.1929 | 10.7306 | 9.9786 | 9.0316 | 8.2327 | 6.1776 | 5.1235 | 4.8265 | 9.898 | 10.0041 | 9.9051 | 9.5337 | 8.8061 | 7.7439 | 6.3469 | 4.9459 | 3.8082 | 0.67653 | -1.5122 | -2.4061
|  | WARFIELD PRIMARY | HE |  |  |  |  | 7.8071 | 7.8214 | 7.698 | 7.1561 | 6.2724 | 4.6133 | 2.4755 | 0.41735 | -1.251 | -4.2367 | -7.0316 | -8.402 | 11.8 | 11.8418 | 11.7847 | 11.6173 | 11.3357 | 10.8806 | 10.1684 | 9.2102 | 8.4031 | 6.1082 | 4.5 | 3.149 | 9.901 | 10.001 | 9.952 | 9.6378 | 9.0459 | 7.8898 | 6.3857 | 4.848 | 3.6 | 1.2 | -0.59184 | -1.3418
|  | WARFIELD PRIMARY | FB |  |  |  |  | 7.9735 | 8.0551 | 8.1061 | 7.95 | 7.5837 | 7.0204 | 6.101 | 5.2582 | 4.6602 | 2.9551 | 0.80102 | -0.32245 | 11.9388 | 11.9959 | 12.0612 | 12.0163 | 11.8898 | 11.6561 | 11.2959 | 10.8122 | 10.2969 | 7.8071 | 4.2469 | 0.72245 | 10.1827 | 10.299 | 10.4673 | 10.4429 | 10.2378 | 9.8061 | 9.0827 | 8.4082 | 7.9092 | 6.2449 | 3.9929 | 2.898
MELKSHAM GSP | FROME BSP | WARMINSTER PRIMARY | MINIMUM HEADROOM | ST 84936 44551 | NO | NO | 6.159 | 1.8458 | 1.7254 | 1.4673 | 0.97134 | 0.60195 | 0.035624 | -0.59805 | -1.2807 | -1.9205 | -3.6113 | -5.0705 | -5.7215 | 2.9545 | 2.8882 | 2.7596 | 2.3565 | 2.1484 | 1.8596 | 1.479 | 1.0321 | 0.62899 | -0.56591 | -1.5118 | -2.6975 | 2.2341 | 2.1514 | 1.9729 | 1.6637 | 1.4372 | 1.0178 | 0.49838 | -0.068967 | -0.59652 | -2.0088 | -3.0761 | -3.3792
|  | WARMINSTER PRIMARY | EE |  |  |  |  | 1.8468 | 1.7254 | 1.4693 | 0.98052 | 0.60501 | 0.041747 | -0.56233 | -1.1827 | -1.7603 | -3.497 | -4.9327 | -5.5154 | 2.9555 | 2.8892 | 2.7606 | 2.3688 | 2.1504 | 1.8708 | 1.5167 | 1.1249 | 0.78307 | -0.56591 | -1.5118 | -1.919 | 2.2341 | 2.1514 | 1.9739 | 1.6708 | 1.4392 | 1.027 | 0.53716 | 0.02389 | -0.44142 | -1.9271 | -2.9955 | -3.3179
|  | WARMINSTER PRIMARY | HT |  |  |  |  | 1.8458 | 1.7254 | 1.4673 | 0.97134 | 0.65399 | 0.038686 | -0.59805 | -1.2807 | -1.9205 | -3.6113 | -5.0705 | -5.7215 | 2.9545 | 2.8882 | 2.7596 | 2.3565 | 2.2014 | 1.8596 | 1.479 | 1.0321 | 0.62899 | -0.45876 | -1.1659 | -1.1679 | 2.2351 | 2.1514 | 1.9729 | 1.6637 | 1.4861 | 1.0178 | 0.49838 | -0.068967 | -0.59652 | -2.0088 | -3.0761 | -3.3792
|  | WARMINSTER PRIMARY | HE |  |  |  |  | 1.8458 | 1.7264 | 1.4683 | 1.0213 | 0.60195 | 0.035624 | -0.57152 | -1.2042 | -1.7613 | -3.2042 | -4.3613 | -4.8685 | 2.9565 | 2.8892 | 2.7606 | 2.427 | 2.1484 | 1.8616 | 1.5025 | 1.0933 | 0.78205 | -0.39142 | -1.1282 | -1.6026 | 2.2351 | 2.1514 | 1.9729 | 1.6963 | 1.4372 | 1.0178 | 0.52593 | -0.005702 | -0.44244 | -1.6751 | -2.5057 | -2.7884
|  | WARMINSTER PRIMARY | FB |  |  |  |  | 1.9101 | 1.8336 | 1.6479 | 1.4826 | 1.2244 | 0.78767 | 0.56216 | 0.39787 | 0.032563 | -0.89397 | -1.9552 | -2.5501 | 2.9902 | 2.9331 | 2.8188 | 2.7463 | 2.5637 | 2.2106 | 2.0463 | 1.9065 | 1.5841 | 0.3443 | -1.1975 | -2.6975 | 2.3147 | 2.2616 | 2.13 | 2.0361 | 1.8596 | 1.5127 | 1.3667 | 1.2402 | 1.0351 | 0.13103 | -0.90468 | -1.4751
LOVEDEAN GSP | FORT WIDLEY BSP | WATERLOOVILLE PRIMARY | MINIMUM HEADROOM | SU 67988 09282 | NO | YES | 14.326 | 24.0524 | 23.9351 | 23.6616 | 23.2341 | 22.7024 | 21.9463 | 21.0147 | 19.9933 | 19.1167 | 15.8524 | 13.9412 | 13.4218 | 26.8686 | 26.6675 | 26.389 | 25.8022 | 25.0155 | 24.09 | 23.0328 | 21.8716 | 20.9206 | 17.4267 | 14.2135 | 7.8563 | 25.9841 | 25.8371 | 25.4392 | 24.9361 | 24.3086 | 23.428 | 22.4045 | 21.2861 | 20.3545 | 16.6331 | 14.7147 | 14.3045
|  | WATERLOOVILLE PRIMARY | EE |  |  |  |  | 24.0535 | 23.9667 | 23.7647 | 23.4739 | 23.0994 | 22.5249 | 21.8177 | 21.0075 | 20.3208 | 17.0963 | 14.8912 | 13.9228 | 26.8706 | 26.6859 | 26.4431 | 25.9328 | 25.2237 | 24.4247 | 23.4808 | 22.4441 | 21.5869 | 17.79 | 14.8869 | 12.4737 | 25.9841 | 25.8596 | 25.5126 | 25.1177 | 24.6086 | 23.882 | 23.0024 | 22.0402 | 21.2361 | 17.5984 | 15.4228 | 14.581
|  | WATERLOOVILLE PRIMARY | HT |  |  |  |  | 24.0524 | 23.9351 | 23.6616 | 23.2341 | 22.7024 | 21.9463 | 21.0147 | 19.9933 | 19.1167 | 15.8524 | 13.9412 | 13.4218 | 26.8686 | 26.6675 | 26.389 | 25.8022 | 25.0155 | 24.09 | 23.0328 | 21.8716 | 20.9206 | 17.4267 | 16.0584 | 15.6492 | 25.9851 | 25.8371 | 25.4392 | 24.9361 | 24.3086 | 23.428 | 22.4045 | 21.2861 | 20.3545 | 16.6331 | 14.7147 | 14.3045
|  | WATERLOOVILLE PRIMARY | HE |  |  |  |  | 24.0596 | 23.982 | 23.7882 | 23.4841 | 23.1055 | 22.5463 | 21.8443 | 21.0402 | 20.382 | 17.5647 | 15.8086 | 15.0953 | 26.8696 | 26.6839 | 26.442 | 25.9298 | 25.24 | 24.4359 | 23.4737 | 22.4206 | 21.59 | 18.1226 | 15.4665 | 13.1614 | 25.9902 | 25.8698 | 25.532 | 25.1239 | 24.6198 | 23.8994 | 23.0218 | 22.0616 | 21.2933 | 18.1147 | 16.3953 | 15.8831
|  | WATERLOOVILLE PRIMARY | FB |  |  |  |  | 24.28 | 24.3198 | 24.4402 | 24.3912 | 24.2177 | 24.0157 | 23.7698 | 23.5228 | 23.2575 | 21.4198 | 18.2014 | 16.5086 | 27.0706 | 26.9482 | 26.9114 | 26.7696 | 26.5237 | 26.0349 | 25.4706 | 24.8941 | 24.2859 | 20.2584 | 14.2135 | 7.8563 | 26.2535 | 26.2688 | 26.38 | 26.3177 | 26.0341 | 25.78 | 25.4749 | 25.1433 | 24.7912 | 22.3892 | 19.0269 | 17.2504
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON PRIMARY | MINIMUM HEADROOM | SU 69106 94287 | NO | NO | 1.614 | 3.2123 | 3.25 | 3.1929 | 2.999 | 21.4459 | 21.0755 | 20.3786 | 18.899 | 16.2276 | 13.6765 | 10.7153 | 7.3816 | 5.0373 | 5.0515 | 4.9944 | 4.8505 | 22.0092 | 21.7755 | 21.0969 | 19.5296 | 16.4255 | 13.5194 | 10.3459 | 6.2776 | 4.3214 | 4.348 | 4.2755 | 4.049 | 21.7265 | 21.398 | 20.6847 | 18.9878 | 15.8194 | 12.9602 | 9.7306 | 5.8163
|  | WATLINGTON PRIMARY | EE |  |  |  |  | 3.2123 | 3.25 | 3.1949 | 3.0296 | 21.501 | 21.1572 | 20.6776 | 20.0133 | 19.1327 | 16.8429 | 12.6245 | 11.0347 | 5.0393 | 5.0515 | 5.0026 | 4.8638 | 22.0633 | 21.799 | 21.3929 | 20.7786 | 19.8908 | 17.6204 | 12.9174 | 11.1225 | 4.3214 | 4.348 | 4.2755 | 4.0643 | 21.7612 | 21.4388 | 20.9786 | 20.2918 | 19.349 | 17.0072 | 12.2367 | 10.5541
|  | WATLINGTON PRIMARY | HT |  |  |  |  | 3.2316 | 3.2776 | 3.1929 | 3.0531 | 21.5225 | 21.2408 | 20.5908 | 19.8918 | 18.4602 | 15.8745 | 11.8643 | 9.1031 | 5.0393 | 5.0526 | 4.9944 | 4.8505 | 22.0092 | 21.7755 | 21.0969 | 20.35 | 18.7235 | 16.1694 | 12.0153 | 9.2357 | 4.3337 | 4.3643 | 4.2796 | 4.049 | 21.7265 | 21.4592 | 20.7408 | 19.9674 | 18.301 | 15.5867 | 11.1612 | 8.1653
|  | WATLINGTON PRIMARY | HE |  |  |  |  | 3.2133 | 3.251 | 3.198 | 2.999 | 21.4459 | 21.0755 | 20.3786 | 18.899 | 16.2276 | 13.6765 | 10.7153 | 7.3816 | 5.0373 | 5.0526 | 5.0026 | 4.8648 | 22.0551 | 21.7847 | 21.1398 | 19.5296 | 16.4255 | 13.5194 | 10.3459 | 6.2776 | 4.3225 | 4.348 | 4.2765 | 4.05 | 21.7347 | 21.398 | 20.6847 | 18.9878 | 15.8194 | 12.9602 | 9.7306 | 5.8163
|  | WATLINGTON PRIMARY | FB |  |  |  |  | 3.3623 | 3.4286 | 3.4286 | 3.4051 | 22.0337 | 21.9939 | 21.9255 | 21.6255 | 21.2082 | 19.6847 | 17.6735 | 16.0255 | 5.1046 | 5.1219 | 5.1107 | 5.0975 | 22.4072 | 22.3714 | 22.248 | 21.7776 | 21.2051 | 19.1816 | 16.499 | 13.8561 | 4.4653 | 4.5041 | 4.5031 | 4.4898 | 22.3194 | 22.2745 | 22.1663 | 21.7469 | 21.2102 | 19.4 | 17.1357 | 15.2102
AMERSHAM GSP | LOUDWATER BSP | WELL END PRIMARY | MINIMUM HEADROOM | SU 88511 87957 | NO | YES | 2.646 | 7.6613 | 7.5521 | 7.3378 | 6.9552 | 6.5358 | 5.9409 | 5.2337 | 4.4623 | 3.7735 | 1.3398 | -0.12852 | -0.61729 | 12.9429 | 12.9286 | 12.7705 | 12.3633 | 11.998 | 11.5541 | 10.9786 | 10.3776 | 9.8592 | 7.9623 | 6.6368 | 4.3684 | 10.399 | 10.3909 | 10.2031 | 9.747 | 9.3317 | 8.7562 | 8.0592 | 7.3684 | 6.7684 | 4.5919 | 3.4164 | 3.1592
|  | WELL END PRIMARY | EE |  |  |  |  | 7.6613 | 7.5521 | 7.345 | 6.9756 | 6.5715 | 6.0092 | 5.348 | 4.7541 | 4.0919 | 1.9286 | 0.46026 | -0.16831 | 12.946 | 12.9317 | 12.7878 | 12.3929 | 12.0378 | 11.6613 | 11.1205 | 10.5858 | 10.0429 | 7.9623 | 6.6368 | 5.7133 | 10.4011 | 10.3919 | 10.2194 | 9.7847 | 9.3868 | 8.8817 | 8.2245 | 7.6235 | 7.0215 | 5.0062 | 3.7643 | 3.3072
|  | WELL END PRIMARY | HT |  |  |  |  | 7.6613 | 7.5552 | 7.3378 | 6.9552 | 6.5358 | 5.9409 | 5.2337 | 4.4623 | 3.7735 | 1.3398 | -0.12852 | -0.61729 | 12.9429 | 12.9286 | 12.7705 | 12.3633 | 11.998 | 11.5541 | 10.9786 | 10.3776 | 9.8592 | 7.9817 | 7.1164 | 6.9592 | 10.399 | 10.3909 | 10.2031 | 9.747 | 9.3317 | 8.7562 | 8.0592 | 7.3684 | 6.7684 | 4.5919 | 3.4164 | 3.1592
|  | WELL END PRIMARY | HE |  |  |  |  | 7.6623 | 7.5562 | 7.348 | 6.9623 | 6.5409 | 5.9745 | 5.3245 | 4.7562 | 4.0929 | 2.3062 | 1.1603 | 0.83067 | 12.945 | 12.9286 | 12.7827 | 12.3898 | 12.0296 | 11.6398 | 11.1286 | 10.6001 | 10.0501 | 8.1664 | 7.0419 | 6.2643 | 10.4011 | 10.3919 | 10.2205 | 9.7756 | 9.3674 | 8.8521 | 8.2296 | 7.6368 | 7.0327 | 5.3368 | 4.4194 | 4.2378
|  | WELL END PRIMARY | FB |  |  |  |  | 7.7909 | 7.7888 | 7.7113 | 7.6215 | 7.4888 | 7.3347 | 7.149 | 6.9664 | 6.8184 | 5.8072 | 4.297 | 3.4031 | 13.0909 | 13.0205 | 12.9205 | 12.9031 | 12.7735 | 12.5756 | 12.3276 | 11.9143 | 11.6143 | 9.6735 | 7.0307 | 4.3684 | 10.6296 | 10.6123 | 10.5715 | 10.5898 | 10.5205 | 10.395 | 10.2317 | 9.9092 | 9.7164 | 8.4409 | 6.7847 | 5.9072
WILLESDEN GSP |  | WESLEY AVENUE PRIMARY | MINIMUM HEADROOM | TQ 20927 83082 | NO | YES | 18.765 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911
|  | WESLEY AVENUE PRIMARY | EE |  |  |  |  | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911
|  | WESLEY AVENUE PRIMARY | HT |  |  |  |  | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911
|  | WESLEY AVENUE PRIMARY | HE |  |  |  |  | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911
|  | WESLEY AVENUE PRIMARY | FB |  |  |  |  | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.9982 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 46.8145 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911 | 45.2911
LOVEDEAN GSP | FAREHAM (MAIN) BSP | WEST END PRIMARY | MINIMUM HEADROOM | SU 57216 06147 | NO | YES | 7.399 | 10.9265 | 10.7959 | 10.6387 | 10.1938 | 9.5898 | 8.7265 | 7.7877 | 6.754 | 5.9826 | 2.4265 | -0.032694 | -0.97963 | 13.2612 | 13.0816 | 12.9173 | 12.5693 | 12.0857 | 11.5612 | 10.9132 | 10.1469 | 9.6275 | 7.3153 | 5.8428 | 1.7418 | 12.2244 | 12.0928 | 11.9653 | 11.5908 | 11.0826 | 10.3693 | 9.5653 | 8.6367 | 7.9112 | 4.9653 | 3.1255 | 2.4367
|  | WEST END PRIMARY | EE |  |  |  |  | 10.9438 | 10.8234 | 10.7316 | 10.3867 | 9.9285 | 9.0989 | 8.1265 | 7.101 | 6.3561 | 3.0367 | 0.47445 | -0.87147 | 13.2775 | 13.1112 | 12.9847 | 12.6959 | 12.3081 | 11.8173 | 11.1785 | 10.3938 | 9.8306 | 7.4867 | 6.0387 | 4.3602 | 12.2377 | 12.1132 | 12.0438 | 11.7622 | 11.2816 | 10.5816 | 9.7224 | 8.7663 | 8.0602 | 5.3122 | 3.4438 | 2.4367
|  | WEST END PRIMARY | HT |  |  |  |  | 10.9265 | 10.7959 | 10.6387 | 10.1938 | 9.5898 | 8.7265 | 7.7877 | 6.754 | 5.9826 | 2.4265 | -0.032694 | -0.97963 | 13.2612 | 13.0816 | 12.9173 | 12.5693 | 12.0857 | 11.5612 | 10.9132 | 10.1469 | 9.6275 | 7.3153 | 6.3632 | 6.3938 | 12.2244 | 12.0928 | 11.9653 | 11.5908 | 11.0826 | 10.3693 | 9.5653 | 8.6367 | 7.9112 | 4.9653 | 3.1255 | 2.5469
|  | WEST END PRIMARY | HE |  |  |  |  | 10.951 | 10.8408 | 10.754 | 10.3877 | 9.9 | 9.103 | 8.1775 | 7.1581 | 6.4244 | 3.7653 | 2.0908 | 1.2796 | 13.2755 | 13.1081 | 12.9806 | 12.6898 | 12.2867 | 11.7898 | 11.1612 | 10.3561 | 9.7744 | 7.4989 | 6.5163 | 4.9898 | 12.2438 | 12.1275 | 12.0663 | 11.7642 | 11.253 | 10.5602 | 9.7204 | 8.754 | 8.0398 | 5.5 | 4.4142 | 4.0847
|  | WEST END PRIMARY | FB |  |  |  |  | 11.4071 | 11.2591 | 11.2173 | 11.2887 | 11.1193 | 10.8693 | 10.6132 | 10.3061 | 10.0408 | 8.1653 | 6.0398 | 4.5387 | 13.503 | 13.4459 | 13.3265 | 13.3418 | 13.1244 | 12.8622 | 12.603 | 12.2836 | 11.9857 | 9.3785 | 5.8428 | 1.7418 | 12.6949 | 12.5489 | 12.4938 | 12.5857 | 12.4051 | 12.1714 | 11.9367 | 11.604 | 11.2673 | 9.0153 | 6.9683 | 5.8112
MELKSHAM GSP | WEST GRAFTON BSP | WEST GRAFTON VILLAGE PRIMARY | MINIMUM HEADROOM | SU 24639 60279 | NO | NO | 1.493 | 7.0184 | 7.0398 | 7.0071 | 6.9133 | 6.7969 | 6.5531 | 6.3653 | 6.102 | 5.8551 | 5.2663 | 5.1092 | 5.3061 | 8.76 | 8.7335 | 8.6988 | 8.61 | 8.4702 | 8.2243 | 8.0447 | 7.7845 | 7.5457 | 6.9406 | 6.7753 | 6.0947 | 7.9 | 7.8939 | 7.85 | 7.748 | 7.6235 | 7.3735 | 7.1796 | 6.9133 | 6.6602 | 6.0469 | 5.8857 | 6.0663
|  | WEST GRAFTON VILLAGE PRIMARY | EE |  |  |  |  | 7.0194 | 7.0398 | 7.0112 | 6.9224 | 6.9184 | 6.6796 | 6.399 | 6.2071 | 5.9745 | 5.398 | 5.199 | 5.3082 | 8.761 | 8.7335 | 8.7039 | 8.6161 | 8.5865 | 8.3416 | 8.0631 | 7.8702 | 7.6396 | 7.0243 | 6.8039 | 6.6682 | 7.902 | 7.8939 | 7.8541 | 7.7561 | 7.7418 | 7.498 | 7.2092 | 7.0112 | 6.7735 | 6.1673 | 5.9622 | 6.0663
|  | WEST GRAFTON VILLAGE PRIMARY | HT |  |  |  |  | 7.0184 | 7.0398 | 7.0071 | 6.9133 | 6.7969 | 6.5531 | 6.3653 | 6.102 | 5.8551 | 5.2663 | 5.1092 | 5.3061 | 8.761 | 8.7345 | 8.6988 | 8.61 | 8.4702 | 8.2243 | 8.0447 | 7.7845 | 7.5457 | 6.9406 | 6.7753 | 6.9447 | 7.9 | 7.8939 | 7.85 | 7.748 | 7.6235 | 7.3735 | 7.1796 | 6.9133 | 6.6602 | 6.0469 | 5.8857 | 6.0796
|  | WEST GRAFTON VILLAGE PRIMARY | HE |  |  |  |  | 7.0184 | 7.0398 | 7.0092 | 6.9214 | 6.9173 | 6.7918 | 6.5143 | 6.2082 | 6.0296 | 5.5102 | 5.3704 | 5.401 | 8.76 | 8.7335 | 8.7018 | 8.6151 | 8.5865 | 8.4559 | 8.1773 | 7.8743 | 7.6937 | 7.1406 | 6.9824 | 6.7763 | 7.9 | 7.8939 | 7.852 | 7.7551 | 7.7418 | 7.6092 | 7.3245 | 7.0133 | 6.8276 | 6.2806 | 6.1337 | 6.1592
|  | WEST GRAFTON VILLAGE PRIMARY | FB |  |  |  |  | 7.0969 | 7.152 | 7.1622 | 7.1663 | 7.1418 | 7.1031 | 7.048 | 7.098 | 7.0327 | 6.5622 | 6.0673 | 5.6735 | 8.8324 | 8.8233 | 8.808 | 8.8059 | 8.7794 | 8.7263 | 8.6539 | 8.6427 | 8.559 | 7.9529 | 7.1284 | 6.0947 | 7.9867 | 8.0092 | 8.0051 | 7.998 | 7.9663 | 7.9204 | 7.8582 | 7.902 | 7.8286 | 7.3296 | 6.8255 | 6.4265
AXMINSTER GSP | YEOVIL BSP | WEST HENDFORD PRIMARY | MINIMUM HEADROOM | ST 55000 15442 | NO | NO | 12.9 | 29.6506 | 29.621 | 29.571 | 29.4496 | 29.2986 | 29.0578 | 28.8098 | 28.5496 | 28.2782 | 27.4363 | 26.8323 | 26.7057 | 29.5782 | 29.5394 | 29.468 | 29.3414 | 29.1935 | 28.9629 | 28.5506 | 28.1476 | 27.7333 | 26.3986 | 25.2782 | 23.4812 | 29.7853 | 29.7455 | 29.6761 | 29.5516 | 29.3935 | 29.1557 | 28.9067 | 28.6363 | 28.3782 | 27.5914 | 27.0414 | 26.9588
|  | WEST HENDFORD PRIMARY | EE |  |  |  |  | 29.6506 | 29.621 | 29.571 | 29.4516 | 29.3118 | 29.0976 | 28.8425 | 28.5496 | 28.2986 | 27.4976 | 26.9516 | 26.7741 | 29.5792 | 29.5435 | 29.471 | 29.3465 | 29.2057 | 28.9812 | 28.5506 | 28.1476 | 27.7823 | 26.3986 | 25.2782 | 24.5384 | 29.7853 | 29.7455 | 29.6761 | 29.5527 | 29.4047 | 29.1884 | 28.9292 | 28.6363 | 28.3904 | 27.6384 | 27.1506 | 26.9863
|  | WEST HENDFORD PRIMARY | HT |  |  |  |  | 29.6567 | 29.6323 | 29.5843 | 29.4608 | 29.3078 | 29.0578 | 28.8098 | 28.5527 | 28.2986 | 27.4363 | 26.8323 | 26.7057 | 29.5802 | 29.5435 | 29.471 | 29.3465 | 29.1986 | 28.968 | 28.5761 | 28.1812 | 27.8037 | 26.6751 | 25.9506 | 25.871 | 29.7925 | 29.7588 | 29.6925 | 29.5608 | 29.3996 | 29.1557 | 28.9067 | 28.6404 | 28.3874 | 27.5914 | 27.0414 | 26.9588
|  | WEST HENDFORD PRIMARY | HE |  |  |  |  | 29.6537 | 29.6241 | 29.5772 | 29.4496 | 29.2986 | 29.0823 | 28.8363 | 28.5598 | 28.2782 | 27.5843 | 27.1751 | 27.0527 | 29.5782 | 29.5394 | 29.468 | 29.3414 | 29.1935 | 28.9629 | 28.5669 | 28.1731 | 27.7333 | 26.4139 | 25.621 | 25.0425 | 29.7894 | 29.7506 | 29.6863 | 29.5516 | 29.3935 | 29.1772 | 28.9272 | 28.6537 | 28.3782 | 27.7169 | 27.3496 | 27.2435
|  | WEST HENDFORD PRIMARY | FB |  |  |  |  | 29.7649 | 29.7751 | 29.7363 | 29.67 | 29.5792 | 29.4435 | 29.3445 | 29.2047 | 29.0414 | 28.5374 | 27.768 | 27.371 | 29.6986 | 29.6904 | 29.621 | 29.5639 | 29.4904 | 29.3629 | 29.1955 | 28.9527 | 28.7016 | 27.2935 | 25.3037 | 23.4812 | 29.9118 | 29.9088 | 29.8527 | 29.7874 | 29.6996 | 29.568 | 29.468 | 29.3343 | 29.1812 | 28.5976 | 27.8802 | 27.5159
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR PRIMARY | MINIMUM HEADROOM | ST 77699 22040 | NO | NO | 0.574 | 5.0469 | 5.0316 | 4.9867 | 4.6745 | 4.5112 | 4.1357 | 3.7306 | 3.3255 | 2.948 | 1.7612 | 0.79184 | 0.23571 | 6.2434 | 6.2168 | 6.1709 | 5.9454 | 5.873 | 5.6352 | 5.3607 | 5.0893 | 4.8546 | 3.9985 | 3.6199 | 3.3454 | 5.5867 | 5.5745 | 5.5306 | 5.2959 | 5.1776 | 4.8755 | 4.5429 | 4.2071 | 3.898 | 2.9408 | 2.2898 | 2.0173
|  | WEST STOUR PRIMARY | EE |  |  |  |  | 5.0469 | 5.0367 | 5.0061 | 4.6745 | 4.5643 | 4.1745 | 3.8204 | 3.451 | 3.0878 | 1.9031 | 1.0561 | 0.64898 | 6.2434 | 6.2219 | 6.1842 | 5.9454 | 5.9036 | 5.6505 | 5.4281 | 5.1923 | 4.9434 | 4.0597 | 3.6199 | 3.4138 | 5.5867 | 5.5786 | 5.5459 | 5.2959 | 5.2265 | 4.9143 | 4.6306 | 4.3296 | 4.0337 | 3.0837 | 2.4898 | 2.2735
|  | WEST STOUR PRIMARY | HT |  |  |  |  | 5.048 | 5.0316 | 4.9867 | 4.6888 | 4.5112 | 4.1357 | 3.7306 | 3.3255 | 2.948 | 1.7612 | 0.79184 | 0.23571 | 6.2454 | 6.2168 | 6.1709 | 5.9699 | 5.873 | 5.6352 | 5.3607 | 5.0893 | 4.8546 | 3.9985 | 3.6913 | 3.6679 | 5.5888 | 5.5745 | 5.5306 | 5.3082 | 5.1776 | 4.8755 | 4.5429 | 4.2071 | 3.898 | 2.9408 | 2.2898 | 2.0173
|  | WEST STOUR PRIMARY | HE |  |  |  |  | 5.049 | 5.0367 | 5.0102 | 4.7173 | 4.5306 | 4.1612 | 3.7816 | 3.349 | 2.9714 | 2.1184 | 1.3459 | 1.002 | 6.2434 | 6.2209 | 6.1842 | 5.9934 | 5.8923 | 5.6832 | 5.4597 | 5.1923 | 4.9474 | 4.1852 | 3.8709 | 3.6699 | 5.5878 | 5.5786 | 5.549 | 5.3378 | 5.2041 | 4.9173 | 4.6184 | 4.2673 | 3.9704 | 3.248 | 2.7316 | 2.5408
|  | WEST STOUR PRIMARY | FB |  |  |  |  | 5.152 | 5.1857 | 5.198 | 5.198 | 5.201 | 5.1449 | 5.0724 | 4.85 | 4.751 | 3.9224 | 3.2082 | 2.7327 | 6.3301 | 6.3301 | 6.3097 | 6.3026 | 6.2801 | 6.2168 | 6.1332 | 5.9372 | 5.8291 | 5.0138 | 4.174 | 3.3454 | 5.6582 | 5.6786 | 5.6827 | 5.6806 | 5.6724 | 5.6337 | 5.6071 | 5.4602 | 5.3745 | 4.651 | 4.0255 | 3.6235
MANNINGTON GSP | BOURNEMOUTH BSP | WESTBOURNE PRIMARY | MINIMUM HEADROOM | SZ 07642 91485 | NO | YES | 1.942 | 15.1449 | 15.2796 | 15.3653 | 15.2439 | 15.0724 | 14.649 | 14.2184 | 13.7173 | 13.0969 | 10.499 | 8.5602 | 7.5184 | 17.5816 | 17.5551 | 17.4929 | 17.3949 | 17.1816 | 16.8388 | 16.4735 | 16.0439 | 15.499 | 12.8908 | 7.9918 | 1.4622 | 16.0265 | 16.0796 | 16.1041 | 15.9429 | 15.7163 | 15.3051 | 14.9031 | 14.4316 | 13.8367 | 11.5122 | 9.55 | 8.6173
|  | WESTBOURNE PRIMARY | EE |  |  |  |  | 15.1469 | 15.3133 | 15.4898 | 15.3449 | 15.2724 | 14.9439 | 14.6041 | 14.2173 | 13.6816 | 10.9367 | 8.6204 | 7.5184 | 17.6102 | 17.6388 | 17.6969 | 17.45 | 17.301 | 16.9959 | 16.6837 | 16.3194 | 15.8092 | 12.9429 | 10.3378 | 7.7143 | 16.0265 | 16.0959 | 16.1561 | 15.9878 | 15.8582 | 15.5061 | 15.1633 | 14.7755 | 14.2255 | 11.6214 | 9.55 | 8.6173
|  | WESTBOURNE PRIMARY | HT |  |  |  |  | 15.1449 | 15.2796 | 15.3653 | 15.2439 | 15.0724 | 14.649 | 14.2184 | 13.7173 | 13.0969 | 10.499 | 8.5602 | 7.9735 | 17.6031 | 17.6071 | 17.5714 | 17.3949 | 17.1816 | 16.8388 | 16.4735 | 16.0439 | 15.499 | 13.7051 | 12.5 | 11.8531 | 16.0265 | 16.0796 | 16.1041 | 15.9429 | 15.7163 | 15.3051 | 14.9031 | 14.4316 | 13.8367 | 11.5122 | 9.9286 | 9.5367
|  | WESTBOURNE PRIMARY | HE |  |  |  |  | 15.1643 | 15.348 | 15.4704 | 15.4347 | 15.3112 | 15.102 | 14.7908 | 14.4418 | 13.9949 | 12.2398 | 10.6806 | 9.8531 | 17.6184 | 17.6582 | 17.6531 | 17.5184 | 17.3163 | 17.0908 | 16.7633 | 16.3847 | 15.9337 | 13.5235 | 11.149 | 8.649 | 16.0306 | 16.1031 | 16.1469 | 16.0837 | 15.8724 | 15.6602 | 15.3173 | 14.9449 | 14.4908 | 12.8255 | 11.5296 | 10.8643
|  | WESTBOURNE PRIMARY | FB |  |  |  |  | 15.302 | 15.5265 | 15.7061 | 15.8663 | 16.0429 | 16.0898 | 16.1051 | 15.9418 | 15.7857 | 14.8337 | 12.7735 | 11.0163 | 17.5816 | 17.5551 | 17.4929 | 17.4051 | 17.2959 | 17.0194 | 16.7 | 16.2122 | 15.7704 | 12.8908 | 7.9918 | 1.4622 | 16.1276 | 16.2459 | 16.3357 | 16.3816 | 16.4418 | 16.4367 | 16.4102 | 16.3214 | 16.1959 | 15.1224 | 13.0673 | 11.3255
MELKSHAM GSP | FROME BSP | WESTBURY PRIMARY | MINIMUM HEADROOM | ST 87654 51530 | NO | NO | 3.045 | 13.3082 | 13.3276 | 13.1969 | 12.9622 | 12.6143 | 12.0643 | 11.4092 | 10.6704 | 9.9357 | 7.9704 | 6.9878 | 6.7837 | 16.4663 | 16.2571 | 16.0133 | 15.6418 | 15.149 | 14.5398 | 13.8184 | 13.0214 | 12.2296 | 9.8867 | 8.1878 | 4.5735 | 14.8276 | 14.7245 | 14.5051 | 14.1541 | 13.7061 | 13.0633 | 12.348 | 11.5561 | 10.7673 | 8.5286 | 7.5163 | 7.3286
|  | WESTBURY PRIMARY | EE |  |  |  |  | 13.3082 | 13.3296 | 13.2163 | 13.0327 | 12.6184 | 12.1765 | 11.6776 | 11.1122 | 10.5327 | 8.5755 | 7.4347 | 7.0173 | 16.4684 | 16.2592 | 16.0235 | 15.6796 | 15.1551 | 14.5531 | 13.9418 | 13.2643 | 12.5551 | 9.9337 | 8.3449 | 7.1143 | 14.8286 | 14.7255 | 14.5194 | 14.2082 | 13.7133 | 13.1235 | 12.5367 | 11.8847 | 11.2071 | 8.9143 | 7.7459 | 7.3286
|  | WESTBURY PRIMARY | HT |  |  |  |  | 13.3082 | 13.3276 | 13.1969 | 12.9622 | 12.6347 | 12.0643 | 11.4092 | 10.6704 | 9.9357 | 7.9704 | 6.9878 | 6.7837 | 16.4663 | 16.2571 | 16.0133 | 15.6418 | 15.2041 | 14.5398 | 13.8184 | 13.0214 | 12.2296 | 9.8867 | 8.8459 | 8.6265 | 14.8276 | 14.7245 | 14.5051 | 14.1541 | 13.7306 | 13.0633 | 12.348 | 11.5561 | 10.7673 | 8.5286 | 7.5163 | 7.3449
|  | WESTBURY PRIMARY | HE |  |  |  |  | 13.3082 | 13.3276 | 13.2153 | 13.0265 | 12.6143 | 12.1796 | 11.6786 | 11.101 | 10.5204 | 8.8673 | 7.6633 | 7.2796 | 16.4663 | 16.2582 | 16.0235 | 15.6735 | 15.149 | 14.5622 | 13.9439 | 13.2531 | 12.5449 | 10.2551 | 8.5857 | 7.3367 | 14.8276 | 14.7245 | 14.5184 | 14.201 | 13.7061 | 13.1327 | 12.5378 | 11.8735 | 11.1959 | 9.1918 | 8.0306 | 7.6643
|  | WESTBURY PRIMARY | FB |  |  |  |  | 13.5112 | 13.6224 | 13.6469 | 13.7092 | 13.402 | 12.9214 | 12.7755 | 12.6969 | 12.55 | 11.2929 | 9.2245 | 7.9786 | 16.6255 | 16.5827 | 16.4918 | 16.4571 | 15.9316 | 15.3367 | 14.951 | 14.6531 | 14.2418 | 11.6959 | 8.1878 | 4.5735 | 15.0541 | 15.1367 | 15.1245 | 15.1622 | 14.7337 | 14.2531 | 13.9878 | 13.8235 | 13.5398 | 11.8367 | 9.6561 | 8.3133
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WESTERN ESPLANADE PRIMARY | MINIMUM HEADROOM | SU 41618 12009 | NO | NO | 6.304 | 27.2739 | 27.0647 | 26.8688 | 26.6861 | 25.8259 | 24.7514 | 23.5402 | 22.3177 | 21.23 | 17.3014 | 15.4188 | 14.4188 | 27.4116 | 27.0759 | 26.73 | 26.3524 | 25.433 | 24.3147 | 22.8728 | 21.6535 | 20.4412 | 16.2637 | 14.1157 | 8.9208 | 28.4177 | 28.079 | 27.7504 | 27.3994 | 26.4341 | 25.1912 | 23.683 | 22.3494 | 21.1004 | 17.3086 | 15.6116 | 14.7667
|  | WESTERN ESPLANADE PRIMARY | EE |  |  |  |  | 27.2739 | 27.0647 | 26.8688 | 26.7157 | 26.5096 | 25.7402 | 24.6984 | 23.4565 | 22.5433 | 17.3606 | 15.4188 | 14.4188 | 27.4116 | 27.0769 | 26.7504 | 26.3922 | 25.9586 | 25.0422 | 23.7453 | 22.5453 | 21.483 | 16.2637 | 14.1157 | 12.1698 | 28.4177 | 28.079 | 27.7504 | 27.4269 | 27.032 | 26.0739 | 24.7422 | 23.3851 | 22.2902 | 17.3086 | 15.6116 | 14.7667
|  | WESTERN ESPLANADE PRIMARY | HT |  |  |  |  | 27.282 | 27.0759 | 26.8779 | 26.6861 | 25.8259 | 24.7514 | 23.5402 | 22.3177 | 21.23 | 17.3014 | 15.6555 | 15.2269 | 27.4147 | 27.0759 | 26.73 | 26.3524 | 25.433 | 24.3147 | 22.8728 | 21.6535 | 20.4412 | 16.8382 | 15.5861 | 15.1647 | 28.432 | 28.0943 | 27.7647 | 27.3994 | 26.4341 | 25.1912 | 23.683 | 22.3494 | 21.1004 | 17.3718 | 15.9953 | 15.7249
|  | WESTERN ESPLANADE PRIMARY | HE |  |  |  |  | 27.2912 | 27.0953 | 26.9228 | 26.7698 | 26.5637 | 25.8045 | 24.7596 | 23.6259 | 22.7126 | 18.6994 | 17.1167 | 16.482 | 27.4177 | 27.081 | 26.7586 | 26.4188 | 25.9759 | 25.0586 | 23.7086 | 22.5575 | 21.4779 | 17.1361 | 15.081 | 13.4402 | 28.433 | 28.0973 | 27.779 | 27.4586 | 27.0453 | 26.0943 | 24.729 | 23.4657 | 22.3667 | 18.4698 | 17.081 | 16.5728
|  | WESTERN ESPLANADE PRIMARY | FB |  |  |  |  | 27.3463 | 27.1698 | 27.0382 | 26.9616 | 26.879 | 26.7075 | 26.1851 | 25.5922 | 25.0902 | 21.1198 | 19.2514 | 17.0259 | 27.4545 | 27.0882 | 26.7841 | 26.4616 | 26.2137 | 25.7116 | 24.9688 | 24.2626 | 23.5484 | 18.3851 | 14.1606 | 8.9208 | 28.5596 | 28.2657 | 28.0371 | 27.8147 | 27.6759 | 27.333 | 26.7218 | 26.1035 | 25.5157 | 21.1922 | 18.7382 | 16.5943
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON PRIMARY | MINIMUM HEADROOM | SU 45207 09912 | NO | NO | 1.395 | 15.4204 | 15.5235 | 15.6041 | 15.498 | 15.1571 | 14.8082 | 14.351 | 13.798 | 13.199 | 10.8429 | 9.2806 | 8.4684 | 17.5776 | 17.5306 | 17.499 | 17.3296 | 16.8786 | 16.4531 | 15.9439 | 15.4051 | 14.8378 | 12.3378 | 7.9796 | 1.8092 | 16.351 | 16.3929 | 16.4316 | 16.302 | 15.9 | 15.5143 | 15.0306 | 14.5133 | 13.9612 | 11.7857 | 10.3776 | 9.648
|  | WESTON PRIMARY | EE |  |  |  |  | 15.4204 | 15.5939 | 15.6214 | 15.5918 | 15.3439 | 14.9837 | 14.5316 | 13.9827 | 13.4847 | 11.1724 | 9.3235 | 8.4684 | 17.5776 | 17.6245 | 17.5235 | 17.3827 | 16.9714 | 16.5653 | 16.0673 | 15.5184 | 15.0194 | 12.3378 | 10.0235 | 7.652 | 16.351 | 16.4735 | 16.4408 | 16.3857 | 16.0439 | 15.6633 | 15.1929 | 14.6755 | 14.2082 | 12.0367 | 10.3776 | 9.648
|  | WESTON PRIMARY | HT |  |  |  |  | 15.4337 | 15.5235 | 15.6041 | 15.498 | 15.1571 | 14.8082 | 14.351 | 13.798 | 13.199 | 10.8429 | 9.2806 | 8.8378 | 17.5816 | 17.5306 | 17.499 | 17.3296 | 16.8786 | 16.4531 | 15.9439 | 15.4051 | 14.8378 | 12.9786 | 11.8571 | 11.3918 | 16.3622 | 16.3929 | 16.4316 | 16.302 | 15.9 | 15.5143 | 15.0306 | 14.5133 | 13.9612 | 11.7857 | 10.3847 | 10.0531
|  | WESTON PRIMARY | HE |  |  |  |  | 15.4408 | 15.5439 | 15.6704 | 15.6316 | 15.3684 | 15.0439 | 14.6224 | 14.1541 | 13.6755 | 11.9051 | 10.65 | 10.0878 | 17.5827 | 17.5408 | 17.5367 | 17.398 | 16.9878 | 16.5878 | 16.0949 | 15.6 | 15.0969 | 12.6194 | 10.5133 | 8.1857 | 16.3663 | 16.4112 | 16.4837 | 16.4173 | 16.0622 | 15.7092 | 15.2633 | 14.8184 | 14.3633 | 12.6796 | 11.549 | 11.0765
|  | WESTON PRIMARY | FB |  |  |  |  | 15.6378 | 15.8082 | 15.9184 | 16.0602 | 16.1163 | 16.1265 | 16.102 | 16.0561 | 15.9847 | 14.6908 | 12.6204 | 11.2755 | 17.6633 | 17.649 | 17.5663 | 17.5357 | 17.3459 | 17.0388 | 16.6765 | 16.301 | 15.9092 | 12.7755 | 7.9796 | 1.8092 | 16.5765 | 16.7102 | 16.7867 | 16.9235 | 16.951 | 16.9122 | 16.8429 | 16.7367 | 16.6214 | 15.1653 | 13.1704 | 11.898
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH PRIMARY | MINIMUM HEADROOM | SY 67443 79096 | NO | NO | 4.754 | 13.4414 | 13.4526 | 13.1781 | 12.5904 | 11.7618 | 10.2485 | 8.5904 | 6.8077 | 4.9761 | -1.9851 | -6.9902 | -9.4005 | 16.1424 | 16.0353 | 15.6893 | 15.2016 | 14.4924 | 13.573 | 12.5669 | 11.424 | 10.2108 | 6.2567 | 2.2944 | -4.9341 | 14.82 | 14.8271 | 14.5516 | 14.0434 | 13.2649 | 12.0557 | 10.7495 | 9.3281 | 7.8536 | 2.3036 | -1.4494 | -2.9668
|  | WEYMOUTH PRIMARY | EE |  |  |  |  | 13.4536 | 13.52 | 13.323 | 12.8965 | 12.2689 | 10.8649 | 9.3179 | 7.671 | 5.973 | -0.24025 | -5.2719 | -8.129 | 16.1587 | 16.0934 | 15.82 | 15.4414 | 14.8302 | 14.0485 | 13.1638 | 12.1557 | 11.0761 | 6.3455 | 2.7495 | -0.31576 | 14.8261 | 14.8649 | 14.6506 | 14.274 | 13.6506 | 12.5516 | 11.3587 | 10.0577 | 8.6965 | 3.4985 | -0.50045 | -2.6372
|  | WEYMOUTH PRIMARY | HT |  |  |  |  | 13.4414 | 13.4526 | 13.1781 | 12.5904 | 11.7618 | 10.2485 | 8.5904 | 6.8077 | 4.9761 | -1.9851 | -6.9902 | -9.4005 | 16.1424 | 16.0353 | 15.6893 | 15.2016 | 14.4924 | 13.573 | 12.5669 | 11.424 | 10.2108 | 6.2567 | 4.0302 | 3.2067 | 14.82 | 14.8271 | 14.5516 | 14.0434 | 13.2649 | 12.0557 | 10.7495 | 9.3281 | 7.8536 | 2.3036 | -1.4494 | -2.9668
|  | WEYMOUTH PRIMARY | HE |  |  |  |  | 13.4781 | 13.5628 | 13.3893 | 12.9281 | 12.271 | 10.9577 | 9.524 | 7.9557 | 6.3689 | 1.622 | -2.3709 | -4.5239 | 16.1638 | 16.1016 | 15.8322 | 15.4557 | 14.8598 | 14.0669 | 13.2098 | 12.1914 | 11.1322 | 7.1342 | 3.7944 | 0.88424 | 14.8465 | 14.9046 | 14.7067 | 14.3036 | 13.6649 | 12.622 | 11.5057 | 10.2485 | 8.97 | 5.0526 | 1.9251 | 0.32506
|  | WEYMOUTH PRIMARY | FB |  |  |  |  | 13.7536 | 13.9475 | 14.0628 | 14.0506 | 13.9608 | 13.7312 | 13.4669 | 13.1771 | 12.8087 | 9.7138 | 5.1628 | 1.8975 | 16.3587 | 16.2853 | 16.1455 | 15.924 | 15.5781 | 15.0465 | 14.474 | 13.8995 | 13.2271 | 8.771 | 2.2944 | -4.9341 | 15.1873 | 15.323 | 15.4108 | 15.3842 | 15.2853 | 15.0393 | 14.7404 | 14.4067 | 13.9934 | 11.1016 | 6.9689 | 4.0118
COWLEY GSP | HEADINGTON BSP | WHEATLEY PRIMARY | MINIMUM HEADROOM | SP 60777 05379 | NO | NO | 19.594 | 13.6326 | 13.1816 | 12.7479 | 12.3183 | 11.7989 | 11.0346 | 9.4969 | 6.8632 | 4.5938 | 0.080547 | -7.8541 | -13.3766 | 14.7683 | 14.5765 | 14.3561 | 14.0867 | 13.6316 | 13.051 | 11.4499 | 8.0979 | 5.9183 | 0.49177 | -9.2297 | -16.6113 | 13.7224 | 13.4479 | 13.0703 | 12.703 | 12.1948 | 11.5203 | 9.8408 | 6.5193 | 4.1663 | -1.2388 | -10.8521 | -17.596
|  | WHEATLEY PRIMARY | EE |  |  |  |  | 13.6387 | 13.2612 | 12.9203 | 12.5887 | 12.1693 | 11.4938 | 10.5703 | 9.2765 | 7.4336 | 3.5459 | -5.1225 | -8.2205 | 14.7744 | 14.6183 | 14.4397 | 14.2377 | 13.8622 | 13.3316 | 12.4622 | 11.1316 | 9.0581 | 4.1724 | -6.8552 | -11.4837 | 13.7275 | 13.5112 | 13.204 | 12.8999 | 12.504 | 11.8836 | 10.9418 | 9.5377 | 7.4152 | 2.8652 | -7.6541 | -11.3766
|  | WHEATLEY PRIMARY | HT |  |  |  |  | 13.6326 | 13.1816 | 12.7479 | 12.3183 | 11.7989 | 11.0346 | 9.4969 | 7.8622 | 4.5938 | 0.080547 | -7.8541 | -13.3766 | 14.7683 | 14.5765 | 14.3561 | 14.0867 | 13.6316 | 13.051 | 11.4499 | 9.7397 | 5.9183 | 0.49177 | -9.2297 | -16.1582 | 13.7224 | 13.4479 | 13.0703 | 12.703 | 12.1948 | 11.5203 | 9.8408 | 8.051 | 4.1663 | -1.2388 | -10.8521 | -17.596
|  | WHEATLEY PRIMARY | HE |  |  |  |  | 13.6377 | 13.2642 | 12.9254 | 12.5918 | 12.1703 | 11.5152 | 10.0581 | 6.8632 | 6.2673 | 1.3703 | -4.5113 | -11.9919 | 14.7734 | 14.6163 | 14.4397 | 14.2367 | 13.8612 | 13.3489 | 11.7989 | 8.0979 | 7.5795 | 1.2122 | -6.4766 | -16.6113 | 13.7265 | 13.5112 | 13.2071 | 12.901 | 12.4989 | 11.905 | 10.2897 | 6.5193 | 5.951 | 0.0019755 | -7.1123 | -16.3031
|  | WHEATLEY PRIMARY | FB |  |  |  |  | 13.7693 | 13.5979 | 13.3622 | 12.9418 | 12.6897 | 12.3214 | 11.7581 | 11.054 | 9.8948 | 7.0632 | 3.0989 | -0.4266 | 14.8234 | 14.7214 | 14.5928 | 14.3836 | 14.0999 | 13.7479 | 13.101 | 12.2979 | 10.8856 | 6.5408 | 0.22851 | -6.497 | 13.8132 | 13.7265 | 13.5744 | 13.2867 | 13.0571 | 12.754 | 12.1805 | 11.4489 | 10.1132 | 6.6275 | 1.7999 | -2.4521
MELKSHAM GSP | ANDOVER BSP | WHITCHURCH PRIMARY | MINIMUM HEADROOM | SU 45924 48466 | NO | NO | 0.825 | 1.4661 | 1.4478 | 1.4263 | 1.2743 | 1.1324 | 0.89265 | 0.21714 | -1.2553 | -4.3043 | -7.1635 | -10.5533 | -14.4767 | 2.1039 | 2.0876 | 2.0784 | 1.9733 | 1.8794 | 1.7804 | 1.1171 | -0.55327 | -4.1614 | -7.238 | -10.989 | -15.8186 | 1.8212 | 1.812 | 1.7988 | 1.6702 | 1.5682 | 1.4059 | 0.69571 | -1.0573 | -4.8012 | -8.0573 | -11.8788 | -16.5747
|  | WHITCHURCH PRIMARY | EE |  |  |  |  | 1.4671 | 1.4488 | 1.4406 | 1.3131 | 1.2069 | 0.98143 | 0.58449 | -0.017551 | -0.92061 | -3.34 | -8.2339 | -10.2094 | 2.1059 | 2.0896 | 2.0814 | 1.9886 | 1.9141 | 1.8151 | 1.5202 | 0.96918 | 0.045714 | -2.3186 | -7.8206 | -9.9778 | 1.8212 | 1.812 | 1.808 | 1.6957 | 1.6212 | 1.4682 | 1.11 | 0.47531 | -0.60122 | -3.2053 | -8.8257 | -10.941
|  | WHITCHURCH PRIMARY | HT |  |  |  |  | 1.4671 | 1.4488 | 1.4263 | 1.2743 | 1.1324 | 0.89265 | 0.21714 | -0.48796 | -2.0471 | -4.7951 | -9.3839 | -12.6441 | 2.1049 | 2.0886 | 2.0784 | 1.9733 | 1.8794 | 1.7804 | 1.1171 | 0.4151 | -1.3563 | -4.0308 | -8.991 | -12.4706 | 1.8222 | 1.812 | 1.7988 | 1.6702 | 1.5682 | 1.4059 | 0.69571 | -0.087959 | -2.0043 | -5.0084 | -10.2308 | -13.9114
|  | WHITCHURCH PRIMARY | HE |  |  |  |  | 1.4661 | 1.4478 | 1.4406 | 1.3222 | 1.1896 | 0.96 | 0.29469 | -1.2553 | -4.3043 | -7.1635 | -10.5533 | -14.4767 | 2.1039 | 2.0876 | 2.0814 | 2.0018 | 1.911 | 1.811 | 1.1814 | -0.55327 | -4.1614 | -7.238 | -10.989 | -15.8186 | 1.8212 | 1.812 | 1.8069 | 1.708 | 1.612 | 1.4539 | 0.76306 | -1.0573 | -4.8012 | -8.0573 | -11.8788 | -16.5747
|  | WHITCHURCH PRIMARY | FB |  |  |  |  | 1.5212 | 1.5284 | 1.5294 | 1.5202 | 1.4876 | 1.4794 | 1.3273 | 1.0478 | 0.60796 | -0.92878 | -2.8808 | -4.7727 | 2.1478 | 2.1539 | 2.1539 | 2.1508 | 2.1324 | 2.1192 | 1.9559 | 1.6651 | 1.1427 | -0.77878 | -3.591 | -6.4706 | 1.8671 | 1.8794 | 1.8865 | 1.8855 | 1.8692 | 1.8529 | 1.6865 | 1.3937 | 0.86714 | -0.84816 | -3.3033 | -5.5645
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY PRIMARY | MINIMUM HEADROOM | SU 52936 08794 | NO | NO | 17.021 | 0.16118 | 9.3571 | 9.0091 | 8.55 | 8.0714 | 7.4214 | 6.7551 | 6.0448 | 5.3183 | 3.0265 | 1.1285 | 0.45913 | 3.3846 | 12.1153 | 11.9163 | 11.6581 | 11.3877 | 11.0479 | 10.5551 | 10.0377 | 9.4785 | 7.6755 | 6.2244 | 4.7887 | 2.6397 | 10.4418 | 10.1295 | 9.7714 | 9.3785 | 8.7846 | 8.0377 | 7.301 | 6.551 | 4.254 | 2.7346 | 2.3326
|  | WHITELEY PRIMARY | EE |  |  |  |  | 0.17036 | 9.3959 | 9.0622 | 8.7081 | 8.3326 | 7.8285 | 7.2438 | 6.6397 | 6.0367 | 3.852 | 1.9653 | 1.0744 | 3.3887 | 12.151 | 11.9428 | 11.7153 | 11.4785 | 11.2255 | 10.8571 | 10.4265 | 10.0183 | 7.7642 | 6.2244 | 5.2897 | 2.6459 | 10.4704 | 10.1775 | 9.8591 | 9.553 | 9.1255 | 8.4418 | 7.7969 | 7.1663 | 4.7959 | 3.2408 | 2.6051
|  | WHITELEY PRIMARY | HT |  |  |  |  | 0.16118 | 9.3571 | 9.0091 | 8.55 | 8.0714 | 7.4214 | 6.7551 | 6.0448 | 5.3183 | 3.0265 | 1.1285 | 0.45913 | 3.3846 | 12.1153 | 11.9163 | 11.6581 | 11.3877 | 11.0479 | 10.5551 | 10.0377 | 9.4785 | 7.6755 | 6.5061 | 6.2408 | 2.6397 | 10.4418 | 10.1295 | 9.7714 | 9.3785 | 8.7846 | 8.0377 | 7.301 | 6.551 | 4.254 | 2.7346 | 2.3326
|  | WHITELEY PRIMARY | HE |  |  |  |  | 0.17138 | 9.3979 | 9.0642 | 8.6938 | 8.2785 | 7.7795 | 7.1857 | 6.5795 | 5.9612 | 4.2255 | 3.0193 | 2.6571 | 3.3867 | 12.1469 | 11.9377 | 11.7112 | 11.4622 | 11.2122 | 10.8255 | 10.3948 | 9.9704 | 8.0663 | 6.9459 | 6.2816 | 2.6469 | 10.4765 | 10.1806 | 9.852 | 9.5153 | 9.0979 | 8.3857 | 7.7489 | 7.0948 | 5.1795 | 4.1755 | 3.9663
|  | WHITELEY PRIMARY | FB |  |  |  |  | 0.27954 | 9.5602 | 9.3877 | 9.1744 | 8.9581 | 8.7795 | 8.6091 | 8.3979 | 8.1806 | 6.7571 | 5.6969 | 4.8877 | 3.4673 | 12.253 | 12.1285 | 11.9765 | 11.8183 | 11.6887 | 11.5071 | 11.2489 | 10.9785 | 9.1846 | 7.1418 | 4.7887 | 2.7448 | 10.6214 | 10.4724 | 10.2795 | 10.0765 | 9.9234 | 9.7724 | 9.601 | 9.4061 | 7.9112 | 6.3602 | 5.3673
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WHITLEY WOOD PRIMARY | MINIMUM HEADROOM | SU 72812 69667 | NO | NO | 4.877 | 10.3024 | 10.4116 | 10.3667 | 10.2351 | 9.8045 | 9.33 | 8.7892 | 8.2045 | 7.5382 | 5.478 | 4.378 | 4.0637 | 11.8922 | 11.9055 | 11.5545 | 11.2647 | 10.7524 | 10.2371 | 9.6453 | 8.98 | 8.3494 | 6.3045 | 3.7545 | -0.20265 | 11.0055 | 11.0963 | 10.881 | 10.6229 | 10.1086 | 9.5412 | 8.879 | 8.1443 | 7.4616 | 5.3841 | 4.3698 | 3.9667
|  | WHITLEY WOOD PRIMARY | EE |  |  |  |  | 10.3024 | 10.4229 | 10.3973 | 10.2749 | 10.0239 | 9.5871 | 9.0361 | 8.4535 | 7.9565 | 5.8351 | 4.5963 | 4.0637 | 11.8943 | 11.9198 | 11.5902 | 11.331 | 10.9902 | 10.5433 | 9.9382 | 9.2667 | 8.732 | 6.3045 | 4.7351 | 3.2698 | 11.0055 | 11.1045 | 10.9116 | 10.7096 | 10.4453 | 9.9422 | 9.2698 | 8.532 | 7.9433 | 5.6269 | 4.4524 | 3.9667
|  | WHITLEY WOOD PRIMARY | HT |  |  |  |  | 10.3065 | 10.4116 | 10.3667 | 10.2351 | 9.8045 | 9.33 | 8.7892 | 8.2045 | 7.5382 | 5.478 | 4.378 | 4.1024 | 11.8922 | 11.9055 | 11.5545 | 11.2647 | 10.7524 | 10.2371 | 9.6453 | 8.98 | 8.3494 | 6.5443 | 5.7035 | 5.382 | 11.0106 | 11.0963 | 10.881 | 10.6229 | 10.1086 | 9.5412 | 8.879 | 8.1443 | 7.4616 | 5.3841 | 4.3698 | 4.179
|  | WHITLEY WOOD PRIMARY | HE |  |  |  |  | 10.3076 | 10.432 | 10.4127 | 10.3004 | 10.0443 | 9.628 | 9.0922 | 8.5402 | 8.0769 | 6.3484 | 5.4422 | 4.982 | 11.8922 | 11.9198 | 11.5912 | 11.3351 | 10.9882 | 10.5361 | 9.9076 | 9.2606 | 8.7627 | 6.5565 | 5.0851 | 3.5688 | 11.0127 | 11.1167 | 10.9331 | 10.728 | 10.4402 | 9.9627 | 9.281 | 8.578 | 8.0382 | 6.1269 | 5.278 | 4.8769
|  | WHITLEY WOOD PRIMARY | FB |  |  |  |  | 10.4351 | 10.5698 | 10.6647 | 10.7514 | 10.7443 | 10.6392 | 10.3616 | 10.1065 | 9.8882 | 8.4851 | 7.1147 | 6.0371 | 12.0382 | 12.0055 | 11.9341 | 11.9106 | 11.7494 | 11.4718 | 10.9473 | 10.4657 | 10.0504 | 7.2392 | 3.7545 | -0.20265 | 11.1943 | 11.282 | 11.3484 | 11.4371 | 11.4361 | 11.3535 | 10.9076 | 10.5606 | 10.3014 | 8.5167 | 6.7382 | 5.6188
MINETY GSP | CIRENCESTER BSP | WHITEWAY PRIMARY | MINIMUM HEADROOM | SP 02076 03059 | NO | NO | 0.939 | 19.1602 | 19.201 | 19.2694 | 19.0449 | 18.7337 | 18.1561 | 17.5449 | 16.9194 | 16.2378 | 13.75 | 11.648 | 10.2888 | 20.3398 | 20.3194 | 20.3459 | 20.0908 | 19.7806 | 19.4092 | 18.9959 | 18.5561 | 18.1112 | 16.6837 | 15.4327 | 13.4827 | 19.3898 | 19.399 | 19.4449 | 19.1602 | 18.7847 | 18.2622 | 17.7112 | 17.1439 | 16.5694 | 14.6031 | 13.1235 | 12.3276
|  | WHITEWAY PRIMARY | EE |  |  |  |  | 19.1602 | 19.2102 | 19.3041 | 19.1551 | 18.9388 | 18.4643 | 17.9439 | 17.4173 | 16.8622 | 14.4571 | 12.3796 | 11.3092 | 20.3408 | 20.3265 | 20.3643 | 20.1449 | 19.8724 | 19.5429 | 19.1827 | 18.7939 | 18.4031 | 16.7286 | 15.4327 | 14.6418 | 19.3918 | 19.4041 | 19.4714 | 19.2408 | 18.9347 | 18.4888 | 18.0071 | 17.5092 | 17.0122 | 15.0561 | 13.5071 | 12.9163
|  | WHITEWAY PRIMARY | HT |  |  |  |  | 19.1643 | 19.201 | 19.2694 | 19.0449 | 18.7337 | 18.1561 | 17.5449 | 16.9194 | 16.2378 | 13.75 | 11.648 | 10.2888 | 20.3408 | 20.3194 | 20.3459 | 20.0908 | 19.7806 | 19.4092 | 18.9959 | 18.5561 | 18.1112 | 16.6837 | 15.8184 | 15.4724 | 19.3929 | 19.399 | 19.4449 | 19.1602 | 18.7847 | 18.2622 | 17.7112 | 17.1439 | 16.5694 | 14.6031 | 13.1235 | 12.3276
|  | WHITEWAY PRIMARY | HE |  |  |  |  | 19.1602 | 19.2102 | 19.3051 | 19.1367 | 18.9194 | 18.4337 | 17.9041 | 17.3673 | 16.7714 | 14.8378 | 13.1102 | 12.1827 | 20.3398 | 20.3265 | 20.3633 | 20.1378 | 19.8704 | 19.5367 | 19.1745 | 18.7908 | 18.3776 | 16.8714 | 15.8071 | 14.9051 | 19.3898 | 19.4061 | 19.4714 | 19.2306 | 18.9214 | 18.4714 | 17.9765 | 17.4837 | 16.9571 | 15.3541 | 14.1602 | 13.5857
|  | WHITEWAY PRIMARY | FB |  |  |  |  | 19.3306 | 19.4388 | 19.5235 | 19.5847 | 19.6235 | 19.6112 | 19.5316 | 19.4459 | 19.252 | 18.3122 | 16.8735 | 15.9592 | 20.4551 | 20.4704 | 20.4643 | 20.4398 | 20.3878 | 20.3082 | 20.1418 | 19.9724 | 19.6 | 17.9806 | 15.7551 | 13.4827 | 19.5816 | 19.6571 | 19.7133 | 19.7388 | 19.7735 | 19.7765 | 19.6929 | 19.5949 | 19.2684 | 18.0888 | 16.6449 | 15.8245
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WILSON ROAD PRIMARY | MINIMUM HEADROOM | SU 69235 73304 | NO | NO | 2.791 | 13.6711 | 13.7283 | 13.8058 | 13.5344 | 13.1344 | 12.4579 | 12.0038 | 11.5068 | 11.013 | 8.7466 | 6.2793 | 5.1466 | 16.7579 | 16.7048 | 16.5966 | 16.3272 | 16.015 | 15.5721 | 15.1823 | 14.8038 | 14.3793 | 12.1681 | 8.166 | 2.6742 | 14.5415 | 14.5446 | 14.4742 | 14.3119 | 13.9987 | 13.4334 | 13.0099 | 12.5487 | 12.0834 | 9.9823 | 7.8691 | 7.0344
|  | WILSON ROAD PRIMARY | EE |  |  |  |  | 13.6711 | 13.7793 | 13.8191 | 13.5905 | 13.1834 | 12.4579 | 12.0038 | 11.5068 | 11.013 | 8.7466 | 6.2793 | 5.1466 | 16.7579 | 16.7364 | 16.663 | 16.3711 | 16.0813 | 15.6048 | 15.2221 | 14.8038 | 14.3793 | 12.1681 | 9.9497 | 8.0619 | 14.5415 | 14.5579 | 14.4742 | 14.3262 | 14.0395 | 13.4334 | 13.0099 | 12.5487 | 12.0834 | 9.9823 | 7.8691 | 7.0344
|  | WILSON ROAD PRIMARY | HT |  |  |  |  | 13.6844 | 13.7283 | 13.8058 | 13.5344 | 13.1344 | 12.4987 | 12.0905 | 11.6936 | 11.2926 | 8.8415 | 6.5283 | 5.3609 | 16.7579 | 16.7048 | 16.6395 | 16.3272 | 16.015 | 15.5721 | 15.1823 | 14.8221 | 14.4466 | 12.917 | 11.7783 | 11.2681 | 14.5579 | 14.5446 | 14.4823 | 14.3119 | 13.9987 | 13.4354 | 13.0272 | 12.6497 | 12.2599 | 10.0477 | 8.3334 | 7.7446
|  | WILSON ROAD PRIMARY | HE |  |  |  |  | 13.6946 | 13.8221 | 13.8834 | 13.6395 | 13.2283 | 12.5803 | 12.1987 | 11.813 | 11.3813 | 9.7405 | 8.2466 | 7.2334 | 16.7609 | 16.7466 | 16.6752 | 16.3895 | 16.1017 | 15.6334 | 15.2609 | 14.8946 | 14.463 | 12.4232 | 10.6099 | 8.6017 | 14.5538 | 14.5762 | 14.5048 | 14.3426 | 14.0385 | 13.513 | 13.1364 | 12.7681 | 12.3354 | 10.7732 | 9.5456 | 8.7905
|  | WILSON ROAD PRIMARY | FB |  |  |  |  | 13.8313 | 14.0068 | 14.0599 | 14.1221 | 13.9956 | 13.6854 | 13.6405 | 13.4242 | 13.3007 | 12.3772 | 10.2507 | 8.6201 | 16.7997 | 16.7477 | 16.5966 | 16.5017 | 16.2926 | 15.867 | 15.6017 | 15.1466 | 14.7854 | 12.3517 | 8.166 | 2.6742 | 14.6517 | 14.717 | 14.6895 | 14.6762 | 14.5446 | 14.3099 | 14.2517 | 14.1272 | 14.0232 | 13.0211 | 10.9926 | 9.4446
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE PRIMARY | MINIMUM HEADROOM | SZ 02014 99989 | NO | NO | 3.581 | 2.8306 | 2.5857 | 20.1836 | 19.6193 | 18.9306 | 18.0102 | 16.8938 | 15.7755 | 14.6316 | 11.1357 | 8.85 | 8.0959 | 8.1642 | 7.8316 | 23.4714 | 23.0214 | 22.4918 | 21.8173 | 20.8744 | 19.9408 | 18.9663 | 15.951 | 13.9265 | 9.6183 | 5.2857 | 4.9387 | 20.4367 | 19.8867 | 19.2571 | 18.4459 | 17.4173 | 16.3948 | 15.3081 | 12.0275 | 10.2214 | 9.8234
|  | WIMBORNE PRIMARY | EE |  |  |  |  | 2.8336 | 2.5908 | 20.1867 | 19.6295 | 19.0489 | 18.3173 | 17.5265 | 16.4867 | 15.651 | 12.4989 | 10.2377 | 9.2632 | 8.1744 | 7.8683 | 23.5551 | 23.1816 | 22.7581 | 22.0836 | 21.3357 | 20.3653 | 19.6408 | 16.1612 | 13.9265 | 12.3479 | 5.3 | 4.9785 | 20.4969 | 20.0224 | 19.4897 | 18.7285 | 17.9163 | 16.8836 | 16.103 | 13.0469 | 11.1571 | 10.4795
|  | WIMBORNE PRIMARY | HT |  |  |  |  | 2.8306 | 2.5857 | 20.2489 | 19.6193 | 18.9306 | 18.0102 | 16.8938 | 15.7755 | 14.6316 | 11.1357 | 8.85 | 8.0959 | 8.1642 | 7.8316 | 23.4714 | 23.0214 | 22.4918 | 21.8173 | 20.8744 | 19.9408 | 18.9663 | 15.951 | 14.4693 | 14.1622 | 5.2857 | 4.9387 | 20.4367 | 19.8867 | 19.2571 | 18.4459 | 17.4173 | 16.3948 | 15.3081 | 12.0275 | 10.2214 | 9.8234
|  | WIMBORNE PRIMARY | HE |  |  |  |  | 2.8326 | 2.5938 | 20.1836 | 19.6591 | 19.0673 | 18.2887 | 17.4581 | 16.3959 | 15.5448 | 12.9642 | 10.9377 | 10.1326 | 8.1744 | 7.8704 | 23.5469 | 23.1928 | 22.7408 | 22.0755 | 21.3183 | 20.3367 | 19.6214 | 16.6153 | 14.5275 | 12.8071 | 5.2979 | 4.9816 | 20.4857 | 20.0459 | 19.4816 | 18.7132 | 17.8806 | 16.8255 | 16.0438 | 13.5418 | 11.8581 | 11.2469
|  | WIMBORNE PRIMARY | FB |  |  |  |  | 3.0408 | 3.0408 | 21.0326 | 20.752 | 20.5428 | 20.3857 | 20.1806 | 19.9612 | 19.7163 | 17.9183 | 15.4673 | 14.0051 | 8.2897 | 8.1887 | 24.1408 | 23.8132 | 23.5469 | 23.1785 | 22.7275 | 22.2775 | 21.7928 | 18.404 | 14.1479 | 9.6183 | 5.5479 | 5.5489 | 21.5285 | 21.2326 | 21.0755 | 20.8785 | 20.603 | 20.3193 | 20.003 | 17.7561 | 15.2897 | 13.8418
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES PRIMARY | MINIMUM HEADROOM | SU 03028 12678 | YES | NO | 0.027 | 4.775 | 4.7801 | 4.776 | 4.7587 | 4.7321 | 4.6974 | 4.6454 | 4.6056 | 4.5495 | 4.4474 | 4.3485 | 4.2985 | 4.4173 | 4.4122 | 4.4082 | 4.3969 | 4.3755 | 4.3531 | 4.3163 | 4.2949 | 4.2571 | 4.1571 | 4.0663 | 3.9102 | 4.501 | 4.502 | 4.5 | 4.4939 | 4.4755 | 4.452 | 4.4173 | 4.3939 | 4.3735 | 4.3184 | 4.2551 | 4.2296
|  | WIMBORNE ST GILES PRIMARY | EE |  |  |  |  | 4.775 | 4.7801 | 4.777 | 4.7597 | 4.7362 | 4.6974 | 4.6607 | 4.625 | 4.575 | 4.4474 | 4.3485 | 4.3026 | 4.4173 | 4.4143 | 4.4082 | 4.3969 | 4.3776 | 4.3561 | 4.3194 | 4.2959 | 4.2602 | 4.1571 | 4.0857 | 4.0459 | 4.501 | 4.5031 | 4.5 | 4.4939 | 4.4765 | 4.4582 | 4.4255 | 4.4051 | 4.3878 | 4.3184 | 4.2551 | 4.2367
|  | WIMBORNE ST GILES PRIMARY | HT |  |  |  |  | 4.776 | 4.7821 | 4.7821 | 4.7668 | 4.7505 | 4.7168 | 4.6709 | 4.6566 | 4.6128 | 4.5077 | 4.3883 | 4.3209 | 4.4173 | 4.4143 | 4.4092 | 4.399 | 4.3776 | 4.3582 | 4.3194 | 4.3 | 4.2643 | 4.1837 | 4.148 | 4.1561 | 4.501 | 4.5041 | 4.5031 | 4.499 | 4.4837 | 4.4673 | 4.4388 | 4.4224 | 4.3929 | 4.352 | 4.2816 | 4.25
|  | WIMBORNE ST GILES PRIMARY | HE |  |  |  |  | 4.776 | 4.7801 | 4.776 | 4.7587 | 4.7321 | 4.7036 | 4.6454 | 4.6056 | 4.5495 | 4.4658 | 4.3556 | 4.2985 | 4.4173 | 4.4122 | 4.4082 | 4.3969 | 4.3755 | 4.3531 | 4.3163 | 4.2949 | 4.2571 | 4.1612 | 4.0908 | 4.0296 | 4.501 | 4.502 | 4.502 | 4.4949 | 4.4755 | 4.452 | 4.4173 | 4.3939 | 4.3735 | 4.3265 | 4.2622 | 4.2296
|  | WIMBORNE ST GILES PRIMARY | FB |  |  |  |  | 4.8056 | 4.8138 | 4.8219 | 4.824 | 4.8209 | 4.8158 | 4.8077 | 4.7893 | 4.7811 | 4.6913 | 4.5974 | 4.5628 | 4.4398 | 4.4388 | 4.4347 | 4.4306 | 4.4194 | 4.4092 | 4.3949 | 4.3694 | 4.3551 | 4.2235 | 4.0663 | 3.9102 | 4.5204 | 4.5255 | 4.5306 | 4.5316 | 4.5296 | 4.5255 | 4.5235 | 4.5082 | 4.5051 | 4.4398 | 4.3796 | 4.3531
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON PRIMARY | MINIMUM HEADROOM | ST 71286 27802 | NO | NO | 4.042 | 1.4257 | 1.6012 | 1.7359 | 1.842 | 1.8155 | 1.6736 | 1.4328 | 1.1787 | 0.93996 | 0.3022 | -0.19473 | -0.37637 | 4.1042 | 4.2726 | 4.392 | 4.49 | 4.5114 | 4.4747 | 4.3155 | 4.1175 | 3.94 | 3.2747 | 2.7012 | 1.2808 | 2.2583 | 2.3583 | 2.4236 | 2.4461 | 2.3502 | 2.1787 | 1.9349 | 1.6787 | 1.4349 | 0.72567 | 0.29404 | 0.16853
|  | WINCANTON PRIMARY | EE |  |  |  |  | 1.4277 | 1.6012 | 1.7359 | 1.893 | 1.8155 | 1.6818 | 1.441 | 1.1787 | 0.93996 | 0.3022 | -0.19473 | -0.37637 | 4.1042 | 4.2726 | 4.392 | 4.5104 | 4.5134 | 4.4971 | 4.3267 | 4.1175 | 3.94 | 3.2747 | 2.7502 | 2.3389 | 2.2604 | 2.3583 | 2.4236 | 2.5298 | 2.3532 | 2.2104 | 1.943 | 1.6787 | 1.4349 | 0.72567 | 0.29404 | 0.16853
|  | WINCANTON PRIMARY | HT |  |  |  |  | 1.4277 | 1.6053 | 1.7461 | 1.8604 | 1.8512 | 1.6736 | 1.4624 | 1.2726 | 1.0726 | 0.45425 | -0.045754 | -0.24882 | 4.1042 | 4.2726 | 4.393 | 4.492 | 4.5155 | 4.4747 | 4.3236 | 4.14 | 3.94 | 3.4757 | 3.2338 | 3.2573 | 2.2593 | 2.3614 | 2.4298 | 2.4573 | 2.3604 | 2.1787 | 1.9614 | 1.7379 | 1.4981 | 0.82567 | 0.43078 | 0.34098
|  | WINCANTON PRIMARY | HE |  |  |  |  | 1.4257 | 1.6022 | 1.7369 | 1.842 | 1.8185 | 1.6808 | 1.4328 | 1.2114 | 0.95935 | 0.51751 | 0.10527 | -0.048816 | 4.1042 | 4.2726 | 4.392 | 4.49 | 4.5114 | 4.4951 | 4.3155 | 4.1512 | 3.9451 | 3.3879 | 2.9696 | 2.5491 | 2.2583 | 2.3604 | 2.4247 | 2.4461 | 2.3502 | 2.2042 | 1.9349 | 1.7165 | 1.4481 | 0.90118 | 0.57159 | 0.47057
|  | WINCANTON PRIMARY | FB |  |  |  |  | 1.5338 | 1.7451 | 1.9481 | 2.1104 | 2.241 | 2.3216 | 2.4226 | 2.4542 | 2.444 | 2.0267 | 1.4022 | 1.0277 | 4.1583 | 4.3389 | 4.5012 | 4.6318 | 4.7206 | 4.7349 | 4.7655 | 4.7461 | 4.694 | 3.9685 | 2.7012 | 1.2808 | 2.3757 | 2.5124 | 2.6461 | 2.7512 | 2.8298 | 2.8614 | 2.9287 | 2.9206 | 2.8869 | 2.2073 | 1.5236 | 1.1216
COWLEY GSP | WITNEY BSP | WINDRUSH PARK PRIMARY | MINIMUM HEADROOM | SP 33366 09758 | NO | NO | 11.939 | 11.3113 | 11.3184 | 11.1 | 10.8551 | 10.7256 | 10.3521 | 9.9643 | 9.5174 | 9.1174 | 7.5858 | 6.5051 | 5.8929 | 12.9745 | 12.9674 | 12.8868 | 12.7939 | 12.7409 | 12.6194 | 12.4847 | 12.3296 | 12.1725 | 11.0307 | 10.2021 | 8.2582 | 12.8347 | 12.8337 | 12.7449 | 12.6164 | 12.5388 | 12.2266 | 11.8756 | 11.4633 | 11.1092 | 9.7572 | 8.9286 | 8.5449
|  | WINDRUSH PARK PRIMARY | EE |  |  |  |  | 11.3307 | 11.3215 | 11.1684 | 10.9909 | 10.8949 | 10.5031 | 10.1031 | 9.6602 | 9.2694 | 7.8276 | 6.7133 | 6.0827 | 12.9909 | 12.9858 | 12.9256 | 12.8602 | 12.8245 | 12.7164 | 12.5898 | 12.449 | 12.3204 | 11.1164 | 10.2286 | 9.5021 | 12.846 | 12.849 | 12.7878 | 12.7011 | 12.6439 | 12.3541 | 12.0062 | 11.6051 | 11.2623 | 9.9204 | 8.998 | 8.5449
|  | WINDRUSH PARK PRIMARY | HT |  |  |  |  | 11.3113 | 11.3184 | 11.1 | 10.8551 | 10.7256 | 10.3521 | 9.9643 | 9.5174 | 9.1174 | 7.5858 | 6.5051 | 5.8929 | 12.9745 | 12.9674 | 12.8868 | 12.7939 | 12.7409 | 12.6194 | 12.4847 | 12.3296 | 12.1725 | 11.0307 | 10.4164 | 10.1847 | 12.8347 | 12.8337 | 12.7449 | 12.6164 | 12.5388 | 12.2266 | 11.8756 | 11.4633 | 11.1092 | 9.7572 | 8.9286 | 8.5521
|  | WINDRUSH PARK PRIMARY | HE |  |  |  |  | 11.3307 | 11.3245 | 11.1694 | 10.9888 | 10.8868 | 10.5347 | 10.1521 | 9.7092 | 9.3439 | 8.1909 | 7.2307 | 6.7398 | 12.9878 | 12.9837 | 12.9215 | 12.8551 | 12.8153 | 12.7123 | 12.5858 | 12.4378 | 12.3123 | 11.3317 | 10.4715 | 9.7684 | 12.847 | 12.8511 | 12.7919 | 12.7 | 12.6368 | 12.3766 | 12.0378 | 11.6215 | 11.3031 | 10.2521 | 9.4694 | 9.1215
|  | WINDRUSH PARK PRIMARY | FB |  |  |  |  | 11.4388 | 11.4643 | 11.4837 | 11.4817 | 11.4725 | 11.4337 | 11.3 | 11.2572 | 11.1296 | 10.3653 | 9.3123 | 8.5276 | 13.0327 | 13.046 | 13.0429 | 13.0409 | 13.0307 | 12.998 | 12.9031 | 12.8684 | 12.7949 | 11.8327 | 10.2021 | 8.2582 | 12.9164 | 12.9409 | 12.95 | 12.9541 | 12.949 | 12.9327 | 12.846 | 12.8184 | 12.7531 | 12.0021 | 10.95 | 10.1633
MANNINGTON GSP |  | WINFRITH HEATH PRIMARY | MINIMUM HEADROOM | SY 80748 86538 | NO | NO | 5.044 | 13.9489 | 13.9203 | 13.6693 | 13.3938 | 13.103 | 12.6346 | 12.1234 | 11.5387 | 11.0499 | 9.2591 | 7.9703 | 7.2764 | 21.4428 | 21.5081 | 21.3223 | 21.1917 | 21.0468 | 20.8234 | 20.5458 | 20.1928 | 19.9274 | 19.0091 | 18.6509 | 18.3274 | 15.6672 | 15.8407 | 15.8744 | 15.8448 | 15.7979 | 15.5611 | 15.2877 | 14.9519 | 14.6836 | 13.7336 | 12.9632 | 12.654
|  | WINFRITH HEATH PRIMARY | EE |  |  |  |  | 13.953 | 13.9397 | 13.6693 | 13.4642 | 13.2754 | 12.8366 | 12.3509 | 11.8795 | 11.4642 | 9.8254 | 8.6417 | 7.9836 | 21.4428 | 21.5213 | 21.3223 | 21.1917 | 21.0938 | 20.8642 | 20.5754 | 20.2968 | 20.0642 | 19.1377 | 18.7009 | 18.3274 | 15.6693 | 15.853 | 15.8785 | 15.9009 | 15.9254 | 15.7162 | 15.4621 | 15.207 | 14.9968 | 14.1591 | 13.457 | 13.1305
|  | WINFRITH HEATH PRIMARY | HT |  |  |  |  | 13.9489 | 13.9203 | 13.6774 | 13.3938 | 13.103 | 12.6346 | 12.1234 | 11.5387 | 11.0499 | 9.2591 | 7.9703 | 7.2764 | 21.4428 | 21.5081 | 21.3621 | 21.1968 | 21.0468 | 20.8234 | 20.5458 | 20.1928 | 19.9274 | 19.0091 | 18.6509 | 18.5907 | 15.6672 | 15.8407 | 15.8744 | 15.8448 | 15.7979 | 15.5611 | 15.2877 | 14.9519 | 14.6836 | 13.7336 | 12.9632 | 12.654
|  | WINFRITH HEATH PRIMARY | HE |  |  |  |  | 13.954 | 13.9397 | 13.7295 | 13.4928 | 13.2489 | 12.8264 | 12.3142 | 11.8172 | 11.3795 | 10.0621 | 9.2417 | 8.7132 | 21.4428 | 21.5213 | 21.3764 | 21.2213 | 21.0785 | 20.8774 | 20.5785 | 20.2938 | 20.055 | 19.2917 | 19.1632 | 18.8458 | 15.6693 | 15.854 | 15.9121 | 15.9183 | 15.9081 | 15.7091 | 15.4407 | 15.1703 | 14.9417 | 14.3458 | 13.9326 | 13.6917
|  | WINFRITH HEATH PRIMARY | FB |  |  |  |  | 14.0601 | 14.0989 | 14.0917 | 14.1019 | 14.0734 | 13.7866 | 13.6264 | 13.5601 | 13.4366 | 12.4917 | 11.5356 | 10.7877 | 21.5234 | 21.6244 | 21.6846 | 21.7244 | 21.7285 | 21.4999 | 21.3897 | 21.3877 | 21.303 | 20.5468 | 19.5326 | 18.4315 | 15.7611 | 15.9846 | 16.1489 | 16.2958 | 16.4152 | 16.3989 | 16.3856 | 16.4407 | 16.4377 | 16.1458 | 15.5417 | 15.057
COWLEY GSP | DRAYTON BSP | WINSMORE LANE PRIMARY | MINIMUM HEADROOM | SU 49513 96982 | NO | YES | 2.779 | 10.9245 | 11.0061 | 10.9908 | 10.8347 | 10.5776 | 10.1194 | 9.6184 | 9.0663 | 8.5347 | 5.8612 | 3.8041 | 2.6765 | 14.1786 | 14.1888 | 14.1082 | 13.8643 | 13.6327 | 13.2929 | 12.85 | 12.3622 | 11.8673 | 9.4469 | 6.8082 | 2.7765 | 12.2694 | 12.3133 | 12.2827 | 12.0765 | 11.749 | 11.2806 | 10.7745 | 10.1949 | 9.6184 | 6.9796 | 5.1388 | 4.2224
|  | WINSMORE LANE PRIMARY | EE |  |  |  |  | 10.9245 | 11.0061 | 10.9908 | 10.8347 | 10.5776 | 10.1194 | 9.6184 | 9.0663 | 8.5347 | 5.8612 | 3.8041 | 2.6765 | 14.1816 | 14.1918 | 14.1092 | 13.9429 | 13.6673 | 13.3388 | 12.9551 | 12.4847 | 12.0265 | 9.4469 | 7.5112 | 5.7867 | 12.2694 | 12.3133 | 12.2827 | 12.1061 | 11.749 | 11.2806 | 10.7745 | 10.202 | 9.6418 | 6.9796 | 5.1388 | 4.2224
|  | WINSMORE LANE PRIMARY | HT |  |  |  |  | 10.9429 | 11.0255 | 11.0204 | 10.8398 | 10.6214 | 10.202 | 9.701 | 9.152 | 8.6112 | 6.1265 | 4.301 | 3.2031 | 14.1806 | 14.1929 | 14.1082 | 13.8643 | 13.6327 | 13.2929 | 12.85 | 12.3622 | 11.8673 | 9.8245 | 8.6214 | 7.9929 | 12.2837 | 12.3367 | 12.3153 | 12.0765 | 11.7622 | 11.3163 | 10.7776 | 10.1949 | 9.6184 | 7.2173 | 5.7082 | 5.0235
|  | WINSMORE LANE PRIMARY | HE |  |  |  |  | 10.9316 | 11.0163 | 11.0082 | 10.8582 | 10.6694 | 10.2071 | 9.7306 | 9.2224 | 8.7408 | 6.652 | 5.1429 | 4.2929 | 14.1786 | 14.1888 | 14.1112 | 13.9429 | 13.7357 | 13.3571 | 12.9571 | 12.4878 | 12.0439 | 9.6806 | 8.0245 | 6.3765 | 12.2776 | 12.3224 | 12.2959 | 12.1184 | 11.8255 | 11.3388 | 10.8255 | 10.2714 | 9.7449 | 7.5918 | 6.3398 | 5.6867
|  | WINSMORE LANE PRIMARY | FB |  |  |  |  | 11.1153 | 11.2602 | 11.3714 | 11.4663 | 11.5245 | 11.4224 | 11.3204 | 11.198 | 11.0418 | 9.9133 | 7.752 | 6.4286 | 14.2561 | 14.2898 | 14.2663 | 14.2194 | 14.0939 | 13.7724 | 13.4949 | 13.2082 | 12.8714 | 10.6327 | 6.8082 | 2.7765 | 12.4347 | 12.5531 | 12.6459 | 12.7276 | 12.752 | 12.6398 | 12.4745 | 12.3071 | 12.0633 | 10.5633 | 8.1949 | 6.8704
MANNINGTON GSP | LYTCHETT BSP | WINTERBORNE KINGSTON PRIMARY | MINIMUM HEADROOM | SY 84631 98138 | NO | NO | 1.81 | 16.4943 | 16.481 | 16.3167 | 16.2218 | 15.9494 | 15.5086 | 14.9351 | 14.4126 | 13.7994 | 12.2708 | 10.9677 | 10.2147 | 17.2784 | 17.2335 | 17.0049 | 16.9314 | 16.6661 | 16.3957 | 16.0263 | 15.6784 | 15.3437 | 14.1202 | 13.4998 | 12.8661 | 16.4341 | 16.4004 | 16.1188 | 15.9708 | 15.5841 | 15.2341 | 14.7453 | 14.2922 | 13.7494 | 12.3677 | 11.6524 | 11.3933
|  | WINTERBORNE KINGSTON PRIMARY | EE |  |  |  |  | 16.4953 | 16.4841 | 16.3167 | 16.2218 | 15.9902 | 15.5514 | 15.0402 | 14.5218 | 13.9392 | 12.2708 | 11.029 | 10.3759 | 17.2824 | 17.2416 | 17.0049 | 16.9437 | 16.7375 | 16.4743 | 16.1467 | 15.8314 | 15.4416 | 14.2314 | 13.4998 | 13.0733 | 16.4371 | 16.4065 | 16.1188 | 15.9708 | 15.6239 | 15.2565 | 14.7933 | 14.3249 | 13.7912 | 12.3882 | 11.6769 | 11.4341
|  | WINTERBORNE KINGSTON PRIMARY | HT |  |  |  |  | 16.4943 | 16.481 | 16.3433 | 16.229 | 15.9494 | 15.5463 | 15.0392 | 14.5453 | 14.0586 | 12.3341 | 10.9677 | 10.2147 | 17.2784 | 17.2335 | 17.0314 | 16.9314 | 16.6661 | 16.3957 | 16.0263 | 15.6784 | 15.3437 | 14.1202 | 13.5865 | 13.5396 | 16.4341 | 16.4004 | 16.1688 | 15.9912 | 15.5841 | 15.2341 | 14.7708 | 14.3065 | 13.8596 | 12.3677 | 11.6524 | 11.3933
|  | WINTERBORNE KINGSTON PRIMARY | HE |  |  |  |  | 16.4984 | 16.4851 | 16.3586 | 16.23 | 15.979 | 15.5086 | 14.9351 | 14.4126 | 13.7994 | 12.5392 | 11.3504 | 10.9279 | 17.2824 | 17.2416 | 17.0498 | 16.9671 | 16.7579 | 16.4784 | 16.1324 | 15.8192 | 15.4263 | 14.3814 | 13.7222 | 13.3875 | 16.4392 | 16.4055 | 16.1759 | 15.9973 | 15.6433 | 15.2535 | 14.7453 | 14.2922 | 13.7494 | 12.5647 | 11.9228 | 11.8943
|  | WINTERBORNE KINGSTON PRIMARY | FB |  |  |  |  | 16.629 | 16.6718 | 16.7116 | 16.732 | 16.7188 | 16.6086 | 16.48 | 16.3892 | 16.2188 | 15.1402 | 14.0106 | 13.4749 | 17.3743 | 17.3682 | 17.3539 | 17.3284 | 17.2804 | 17.0753 | 16.8977 | 16.7733 | 16.5416 | 15.4365 | 14.0875 | 12.8661 | 16.5647 | 16.5912 | 16.5769 | 16.5157 | 16.4279 | 16.2228 | 16.0382 | 15.9147 | 15.6667 | 14.5504 | 13.4473 | 12.9269
MANNINGTON GSP | REDHILL BSP | WINTON PRIMARY | MINIMUM HEADROOM | SZ 09349 93822 | NO | NO | 1.448 | 6.9939 | 6.9673 | 13.501 | 12.9837 | 12.349 | 10.8255 | 9.1878 | 7.4173 | 5.7602 | 0.15306 | -3.5949 | -5.1194 | 10.8194 | 10.7214 | 17.2184 | 16.8847 | 16.4592 | 15.7704 | 14.9163 | 13.9571 | 13.1286 | 10.4071 | 6.8898 | 1.149 | 7.7398 | 7.7204 | 14.2857 | 13.902 | 13.4122 | 12.3551 | 11.1429 | 9.7816 | 8.5592 | 4.2796 | 1.4827 | 0.57245
|  | WINTON PRIMARY | EE |  |  |  |  | 7.0184 | 7.0806 | 13.6816 | 13.3602 | 12.9827 | 11.6622 | 10.2898 | 8.8133 | 7.3939 | 2.3 | -1.2347 | -3.202 | 10.8337 | 10.7776 | 17.2714 | 17.002 | 16.698 | 16.0898 | 15.3745 | 14.5806 | 13.8388 | 10.4071 | 7.9357 | 5.7245 | 7.7551 | 7.7714 | 14.3827 | 14.1306 | 13.8296 | 12.8888 | 11.8704 | 10.7449 | 9.6735 | 5.6194 | 2.9173 | 1.5663
|  | WINTON PRIMARY | HT |  |  |  |  | 6.9939 | 6.9673 | 13.501 | 12.9837 | 12.349 | 10.8255 | 9.1878 | 7.4173 | 5.7602 | 0.15306 | -3.5949 | -5.1194 | 10.8194 | 10.7214 | 17.2184 | 16.8847 | 16.4592 | 15.7704 | 14.9163 | 13.9571 | 13.1286 | 10.4255 | 9.1194 | 8.7398 | 7.7398 | 7.7204 | 14.2857 | 13.902 | 13.4122 | 12.3551 | 11.1429 | 9.7816 | 8.5592 | 4.2796 | 1.4827 | 0.57245
|  | WINTON PRIMARY | HE |  |  |  |  | 7.0276 | 7.1 | 13.7439 | 13.3286 | 12.8265 | 11.7133 | 10.4633 | 9.1429 | 7.8765 | 3.6633 | 0.69082 | -0.84286 | 10.8337 | 10.7816 | 17.3224 | 17.0429 | 16.6786 | 16.1337 | 15.3867 | 14.6173 | 13.8959 | 10.7633 | 8.3378 | 6.0061 | 7.7622 | 7.7918 | 14.4429 | 14.1296 | 13.7357 | 12.9276 | 11.9745 | 10.9439 | 9.9704 | 6.6245 | 4.401 | 3.3092
|  | WINTON PRIMARY | FB |  |  |  |  | 7.2949 | 7.5163 | 14.5469 | 14.5929 | 14.5653 | 14.4602 | 14.151 | 13.9378 | 13.6612 | 11.5194 | 8.1857 | 6.1939 | 10.9337 | 10.9184 | 17.7449 | 17.6327 | 17.4367 | 17.0939 | 16.5041 | 16.0571 | 15.5327 | 12.0643 | 6.8898 | 1.149 | 8.0194 | 8.1949 | 15.199 | 15.2449 | 15.2357 | 15.1316 | 14.8306 | 14.6296 | 14.3633 | 12.3622 | 9.3724 | 7.6092
COWLEY GSP | WITNEY BSP | WITNEY TOWN PRIMARY | MINIMUM HEADROOM | SP 35844 09625 | NO | NO | 3.563 | 17.8407 | 17.8448 | 17.704 | 16.9825 | 15.9784 | 14.4152 | 12.8427 | 11.206 | 9.605 | 4.6774 | 1.8162 | 0.20906 | 21.5805 | 21.4366 | 21.1856 | 20.6999 | 20.0529 | 19.1366 | 18.1417 | 17.0938 | 16.0376 | 12.7244 | 10.6774 | 6.154 | 18.4519 | 18.4601 | 18.3499 | 17.8846 | 17.0774 | 15.7968 | 14.4284 | 13.0091 | 11.6111 | 7.3866 | 5.1815 | 3.8448
|  | WITNEY TOWN PRIMARY | EE |  |  |  |  | 17.8407 | 17.8448 | 17.7305 | 17.1376 | 16.208 | 14.6142 | 12.9631 | 11.3397 | 9.7366 | 5.1142 | 1.9968 | 0.20906 | 21.5815 | 21.4376 | 21.255 | 20.8836 | 20.3346 | 19.5131 | 18.5662 | 17.6162 | 16.6427 | 12.9519 | 10.6774 | 8.8152 | 18.4519 | 18.4601 | 18.3591 | 17.9703 | 17.2856 | 16.0233 | 14.6499 | 13.305 | 11.9407 | 7.6856 | 5.1815 | 3.8448
|  | WITNEY TOWN PRIMARY | HT |  |  |  |  | 17.8764 | 17.9244 | 17.704 | 16.9825 | 15.9784 | 14.4152 | 12.8427 | 11.206 | 9.605 | 4.6774 | 1.8162 | 0.42437 | 21.5856 | 21.4397 | 21.1856 | 20.6999 | 20.0529 | 19.1366 | 18.1417 | 17.0938 | 16.0376 | 12.7244 | 11.2397 | 10.7182 | 18.4856 | 18.4958 | 18.3499 | 17.8846 | 17.0774 | 15.7968 | 14.4284 | 13.0091 | 11.6111 | 7.3866 | 5.3387 | 4.5866
|  | WITNEY TOWN PRIMARY | HE |  |  |  |  | 17.8509 | 17.8621 | 17.757 | 17.1101 | 16.1336 | 14.6244 | 13.0387 | 11.4815 | 9.9366 | 6.2223 | 3.8815 | 2.4815 | 21.5805 | 21.4366 | 21.2489 | 20.8754 | 20.3142 | 19.505 | 18.5591 | 17.6305 | 16.6672 | 13.4019 | 11.4927 | 9.6376 | 18.4611 | 18.4754 | 18.3836 | 17.9591 | 17.2295 | 16.0193 | 14.6836 | 13.3938 | 12.0693 | 8.5917 | 6.8029 | 5.7407
|  | WITNEY TOWN PRIMARY | FB |  |  |  |  | 18.1182 | 18.1744 | 18.307 | 18.1438 | 17.7438 | 17.1478 | 16.5397 | 15.8846 | 15.2101 | 12.6091 | 9.8121 | 7.5938 | 21.7468 | 21.5458 | 21.4958 | 21.306 | 20.9438 | 20.4274 | 19.8764 | 19.2805 | 18.6662 | 15.2938 | 10.9999 | 6.154 | 18.7142 | 18.7325 | 18.8346 | 18.7621 | 18.5152 | 18.1254 | 17.6519 | 17.0887 | 16.5111 | 13.6938 | 10.8295 | 8.6172
FLEET-BRAMLEY GSP | WOKINGHAM BSP | WOKINGHAM PRIMARY | MINIMUM HEADROOM | SU 79589 67665 | NO | NO | 1.804 | 19.3347 | 19.201 | 19.0714 | 18.7694 | 18.2582 | 17.3265 | 16.2653 | 15.1796 | 14.098 | 10.8867 | 8.9582 | 8.1898 | 20.4276 | 20.3204 | 20.2133 | 20.0214 | 19.6755 | 19.2133 | 18.5357 | 17.8959 | 17.2735 | 15.1745 | 14.0316 | 11.6347 | 19.8459 | 19.6041 | 19.502 | 19.1949 | 18.7286 | 18.0071 | 17.1102 | 16.2439 | 15.3959 | 12.6878 | 11.3082 | 10.9041
|  | WOKINGHAM PRIMARY | EE |  |  |  |  | 19.3347 | 19.2051 | 19.0776 | 18.8224 | 18.3592 | 17.3816 | 16.2918 | 15.1796 | 14.098 | 11.0735 | 9.3378 | 8.3745 | 20.4296 | 20.3245 | 20.2235 | 20.048 | 19.7551 | 19.2878 | 18.6622 | 18.0245 | 17.4102 | 15.1745 | 14.0316 | 13.1561 | 19.8459 | 19.6061 | 19.5122 | 19.2398 | 18.8255 | 18.0745 | 17.1898 | 16.2898 | 15.4153 | 12.8276 | 11.5439 | 10.9265
|  | WOKINGHAM PRIMARY | HT |  |  |  |  | 19.3388 | 19.201 | 19.0714 | 18.7694 | 18.2582 | 17.3265 | 16.2653 | 15.2235 | 14.199 | 10.8867 | 8.9582 | 8.1898 | 20.4296 | 20.3214 | 20.2133 | 20.0214 | 19.6755 | 19.2133 | 18.5357 | 17.8959 | 17.2735 | 15.3388 | 14.5969 | 14.4704 | 19.848 | 19.6041 | 19.502 | 19.1949 | 18.7286 | 18.0071 | 17.1102 | 16.2439 | 15.3959 | 12.6878 | 11.3082 | 10.9041
|  | WOKINGHAM PRIMARY | HE |  |  |  |  | 19.3378 | 19.2051 | 19.0847 | 18.7867 | 18.2847 | 17.3265 | 16.2908 | 15.2265 | 14.201 | 11.5429 | 10.152 | 9.4347 | 20.4276 | 20.3204 | 20.2184 | 20.0367 | 19.7418 | 19.2388 | 18.6408 | 18.0204 | 17.4429 | 15.4602 | 14.4806 | 13.4857 | 19.8469 | 19.6071 | 19.5153 | 19.2173 | 18.7765 | 18.0173 | 17.1765 | 16.3112 | 15.4898 | 13.2296 | 12.2439 | 11.7255
|  | WOKINGHAM PRIMARY | FB |  |  |  |  | 19.5337 | 19.6286 | 19.6051 | 19.5633 | 19.3765 | 19.0633 | 18.7408 | 18.3765 | 17.9806 | 16.199 | 14.6041 | 13.6367 | 20.5327 | 20.5602 | 20.5255 | 20.4531 | 20.3429 | 20.05 | 19.7367 | 19.3867 | 19.0031 | 16.8265 | 14.2806 | 11.6347 | 20.05 | 20.1061 | 20.0622 | 19.949 | 19.7765 | 19.501 | 19.2184 | 18.8929 | 18.5245 | 16.7571 | 15.1531 | 14.2337
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | WOODCOTE PRIMARY | MINIMUM HEADROOM | SU 64425 81624 | YES | NO | 1.329 | 3.5686 | 3.5472 | 3.5094 | 3.2207 | 3.0605 | 2.8564 | 2.7268 | 2.4809 | 2.2135 | 1.4615 | 1.0462 | 0.87679 | 3.8179 | 3.7934 | 3.7689 | 3.5362 | 3.4199 | 3.2648 | 3.2087 | 3.0097 | 2.8352 | 2.1934 | 1.8362 | 1.4668 | 3.8372 | 3.824 | 3.8005 | 3.5434 | 3.4158 | 3.2383 | 3.1209 | 2.8852 | 2.6311 | 1.8954 | 1.4658 | 1.3485
|  | WOODCOTE PRIMARY | EE |  |  |  |  | 3.5686 | 3.5472 | 3.5115 | 3.2247 | 3.1054 | 2.8747 | 2.7554 | 2.489 | 2.2452 | 1.4615 | 1.0523 | 0.88291 | 3.8189 | 3.7954 | 3.7719 | 3.5372 | 3.4638 | 3.2985 | 3.225 | 3.0291 | 2.8423 | 2.1934 | 1.8362 | 1.6648 | 3.8372 | 3.826 | 3.8036 | 3.5474 | 3.4607 | 3.2587 | 3.1444 | 2.8893 | 2.6597 | 1.8954 | 1.4658 | 1.3485
|  | WOODCOTE PRIMARY | HT |  |  |  |  | 3.5696 | 3.5472 | 3.5125 | 3.2227 | 3.0605 | 2.8594 | 2.7656 | 2.5227 | 2.2962 | 1.4931 | 1.0462 | 0.87679 | 3.8179 | 3.7964 | 3.7709 | 3.5372 | 3.4199 | 3.2648 | 3.2087 | 3.0097 | 2.8372 | 2.2587 | 1.9964 | 2.0056 | 3.8372 | 3.825 | 3.8056 | 3.5536 | 3.4158 | 3.2383 | 3.1495 | 2.9179 | 2.7056 | 1.9352 | 1.4872 | 1.3791
|  | WOODCOTE PRIMARY | HE |  |  |  |  | 3.5696 | 3.5472 | 3.5094 | 3.2207 | 3.0931 | 2.8564 | 2.7268 | 2.4809 | 2.2135 | 1.6564 | 1.4278 | 1.3033 | 3.8179 | 3.7934 | 3.7689 | 3.5362 | 3.4617 | 3.2903 | 3.2128 | 3.0372 | 2.8352 | 2.3464 | 2.1383 | 1.9383 | 3.8372 | 3.824 | 3.8005 | 3.5434 | 3.4495 | 3.2434 | 3.1209 | 2.8852 | 2.6311 | 2.0719 | 1.8168 | 1.7046
|  | WOODCOTE PRIMARY | FB |  |  |  |  | 3.6166 | 3.6217 | 3.6156 | 3.5849 | 3.5635 | 3.5145 | 3.486 | 3.4349 | 3.1513 | 2.736 | 2.2911 | 1.9605 | 3.8689 | 3.8648 | 3.8536 | 3.826 | 3.8117 | 3.7505 | 3.6974 | 3.6321 | 3.3648 | 2.8699 | 2.1974 | 1.4668 | 3.9026 | 3.9148 | 3.9128 | 3.8974 | 3.8842 | 3.8648 | 3.8352 | 3.7944 | 3.5291 | 3.1597 | 2.7087 | 2.3679
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WOODMILL LANE PRIMARY | MINIMUM HEADROOM | SU 43733 15470 | NO | NO | 3.086 | 13.8481 | 13.9093 | 13.694 | 13.5736 | 13.2695 | 12.942 | 12.5573 | 12.0665 | 11.5318 | 9.2604 | 7.6848 | 7.1491 | 15.0848 | 15.0757 | 14.7767 | 14.6726 | 14.3869 | 14.1277 | 13.8257 | 13.4338 | 13.0134 | 11.4379 | 8.3665 | 4.0226 | 14.4379 | 14.4797 | 14.2757 | 14.1828 | 13.8991 | 13.6155 | 13.2828 | 12.8502 | 12.3808 | 10.5063 | 9.2104 | 8.7859
|  | WOODMILL LANE PRIMARY | EE |  |  |  |  | 13.8634 | 13.9093 | 13.7216 | 13.6951 | 13.5073 | 13.09 | 12.6604 | 12.2012 | 11.7522 | 9.6971 | 7.9604 | 7.2348 | 15.1042 | 15.0828 | 14.8022 | 14.7359 | 14.5267 | 14.2175 | 13.9226 | 13.5308 | 13.1502 | 11.4379 | 9.7471 | 8.243 | 14.4491 | 14.4797 | 14.2981 | 14.2716 | 14.093 | 13.742 | 13.3859 | 12.9695 | 12.5604 | 10.8022 | 9.3144 | 8.7859
|  | WOODMILL LANE PRIMARY | HT |  |  |  |  | 13.8481 | 13.9124 | 13.694 | 13.5736 | 13.2695 | 12.942 | 12.5573 | 12.0665 | 11.5318 | 9.2604 | 7.6848 | 7.1491 | 15.0848 | 15.0787 | 14.7767 | 14.6726 | 14.3869 | 14.1277 | 13.8257 | 13.4338 | 13.0134 | 11.7073 | 10.8542 | 10.6389 | 14.4379 | 14.4889 | 14.2757 | 14.1828 | 13.8991 | 13.6155 | 13.2828 | 12.8502 | 12.3808 | 10.5063 | 9.2104 | 8.8848
|  | WOODMILL LANE PRIMARY | HE |  |  |  |  | 13.8502 | 13.9287 | 13.7491 | 13.6991 | 13.4848 | 13.1379 | 12.7124 | 12.3002 | 11.8808 | 10.3073 | 9.1348 | 8.4491 | 15.0869 | 15.0869 | 14.8093 | 14.7348 | 14.5236 | 14.2655 | 13.9236 | 13.5706 | 13.1961 | 11.5961 | 10.1532 | 8.5114 | 14.441 | 14.4991 | 14.3236 | 14.2777 | 14.0787 | 13.79 | 13.4195 | 13.0461 | 12.6634 | 11.2838 | 10.3277 | 9.8093
|  | WOODMILL LANE PRIMARY | FB |  |  |  |  | 13.9818 | 14.0787 | 14.1583 | 14.2042 | 14.2053 | 14.1655 | 13.9706 | 13.8695 | 13.743 | 12.8277 | 11.3124 | 10.1114 | 15.1216 | 15.0757 | 15.0195 | 14.9389 | 14.79 | 14.5767 | 14.241 | 13.9777 | 13.6767 | 11.6542 | 8.3665 | 4.0226 | 14.5604 | 14.6348 | 14.6961 | 14.7308 | 14.7471 | 14.7175 | 14.5297 | 14.4297 | 14.3042 | 13.3706 | 11.9134 | 10.7359
COWLEY GSP | YARNTON BSP | WOODSTOCK PRIMARY | MINIMUM HEADROOM | SP 44795 17462 | NO | YES | 1.705 | 6.0008 | 5.9967 | 5.8171 | 5.5671 | 5.3661 | 4.7059 | 4.0875 | 3.4926 | 2.8671 | 1.5967 | 1.0549 | 0.68753 | 8.0942 | 8.0482 | 7.9217 | 7.7574 | 7.6533 | 7.1564 | 6.7503 | 6.4248 | 6.0666 | 5.1625 | 4.7676 | 3.2931 | 6.9707 | 6.9523 | 6.784 | 6.5829 | 6.4329 | 5.7615 | 5.1921 | 4.7074 | 4.2033 | 3.0993 | 2.6758 | 2.4676
|  | WOODSTOCK PRIMARY | EE |  |  |  |  | 6.0396 | 6.0416 | 5.8753 | 5.6559 | 5.4753 | 5.1651 | 4.8018 | 4.1824 | 3.5988 | 2.0314 | 1.5498 | 1.2977 | 8.1217 | 8.086 | 7.9819 | 7.8574 | 7.7931 | 7.5942 | 7.2799 | 6.8942 | 6.5666 | 5.4095 | 4.7676 | 4.2574 | 7.0095 | 6.9962 | 6.8482 | 6.6911 | 6.5768 | 6.3095 | 5.9197 | 5.3421 | 4.8462 | 3.534 | 3.085 | 2.9268
|  | WOODSTOCK PRIMARY | HT |  |  |  |  | 6.0008 | 5.9967 | 5.8171 | 5.5671 | 5.3661 | 4.7059 | 4.0875 | 3.4926 | 2.8671 | 1.5967 | 1.0549 | 0.68753 | 8.0942 | 8.0482 | 7.9217 | 7.7574 | 7.6533 | 7.1564 | 6.7503 | 6.4248 | 6.0666 | 5.1625 | 4.786 | 4.6054 | 6.9707 | 6.9523 | 6.784 | 6.5829 | 6.4329 | 5.7615 | 5.1921 | 4.7074 | 4.2033 | 3.0993 | 2.6758 | 2.4676
|  | WOODSTOCK PRIMARY | HE |  |  |  |  | 6.0406 | 6.0416 | 5.8722 | 5.6508 | 5.4681 | 5.1447 | 4.7743 | 4.2243 | 3.7243 | 2.0957 | 1.7028 | 1.5049 | 8.1217 | 8.085 | 7.9789 | 7.8574 | 7.7891 | 7.588 | 7.2738 | 6.9146 | 6.6421 | 5.4533 | 4.8789 | 4.3391 | 7.0084 | 6.9952 | 6.8636 | 6.688 | 6.5727 | 6.2972 | 5.8993 | 5.3768 | 4.9636 | 3.5982 | 3.2625 | 3.1176
|  | WOODSTOCK PRIMARY | FB |  |  |  |  | 6.1365 | 6.1641 | 6.0732 | 5.9508 | 5.8212 | 5.6457 | 5.4886 | 5.3916 | 5.0988 | 3.812 | 3.0498 | 2.61 | 8.1982 | 8.1707 | 8.0982 | 7.9901 | 7.8789 | 7.7125 | 7.5544 | 7.4707 | 7.2554 | 6.134 | 4.838 | 3.2931 | 7.1207 | 7.1319 | 7.0687 | 6.9564 | 6.8707 | 6.7217 | 6.5809 | 6.5238 | 6.287 | 5.1789 | 4.4513 | 3.8972
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON PRIMARY | MINIMUM HEADROOM | SU 44145 11242 | NO | NO | 3.571 | 19.8724 | 19.899 | 19.7541 | 19.6265 | 19.3806 | 19.1276 | 18.7735 | 18.3745 | 17.9857 | 16.2694 | 15.2837 | 14.7765 | 21.1663 | 21.1357 | 20.9316 | 20.7949 | 20.5633 | 20.3449 | 20.0357 | 19.7 | 19.4092 | 17.8888 | 15.848 | 12.7184 | 19.7306 | 19.7357 | 19.5071 | 19.3653 | 19.099 | 18.8592 | 18.5122 | 18.1245 | 17.7786 | 16.302 | 15.4878 | 15.051
|  | WOOLSTON PRIMARY | EE |  |  |  |  | 19.8724 | 19.899 | 19.7724 | 19.6816 | 19.5265 | 19.2878 | 18.901 | 18.5122 | 18.1235 | 16.4071 | 15.3224 | 14.7765 | 21.1663 | 21.1408 | 20.9449 | 20.8276 | 20.6643 | 20.4776 | 20.1541 | 19.8429 | 19.549 | 17.8888 | 16.6755 | 15.4398 | 19.7306 | 19.7357 | 19.5163 | 19.3929 | 19.2214 | 19.0031 | 18.6255 | 18.2684 | 17.9224 | 16.399 | 15.4878 | 15.051
|  | WOOLSTON PRIMARY | HT |  |  |  |  | 19.8765 | 19.9 | 19.7541 | 19.6265 | 19.3806 | 19.1276 | 18.7735 | 18.3745 | 17.9857 | 16.2694 | 15.2837 | 14.9265 | 21.1694 | 21.1367 | 20.9316 | 20.7949 | 20.5633 | 20.3449 | 20.0357 | 19.7 | 19.4092 | 18.1969 | 17.551 | 17.2378 | 19.7357 | 19.7398 | 19.5071 | 19.3653 | 19.099 | 18.8592 | 18.5122 | 18.1245 | 17.7786 | 16.302 | 15.4949 | 15.252
|  | WOOLSTON PRIMARY | HE |  |  |  |  | 19.8776 | 19.9092 | 19.7878 | 19.7071 | 19.5133 | 19.2878 | 18.9541 | 18.5306 | 18.1704 | 16.8071 | 16.2418 | 15.8653 | 21.1694 | 21.1429 | 20.948 | 20.8551 | 20.6643 | 20.4745 | 20.1898 | 19.8306 | 19.5531 | 18.0408 | 17.1173 | 15.8776 | 19.7367 | 19.7449 | 19.5306 | 19.4276 | 19.2112 | 18.999 | 18.6827 | 18.2755 | 17.952 | 16.7286 | 16.2959 | 16.0112
|  | WOOLSTON PRIMARY | FB |  |  |  |  | 19.951 | 19.999 | 20.0357 | 20.0612 | 20.0684 | 19.9449 | 19.8602 | 19.7173 | 19.651 | 18.85 | 17.7898 | 16.9786 | 21.1827 | 21.1357 | 21.0806 | 21.0204 | 20.9082 | 20.602 | 20.3878 | 20.1173 | 19.9133 | 18.251 | 15.848 | 12.7184 | 19.8255 | 19.8571 | 19.8786 | 19.8949 | 19.8806 | 19.652 | 19.5765 | 19.4245 | 19.3469 | 18.4704 | 17.452 | 16.6888
MINETY GSP | SWINDON BSP | WOOTTON BASSETT PRIMARY | MINIMUM HEADROOM | SU 07587 81123 | NO | NO | 2.167 | 11.1598 | 11.1588 | 10.9465 | 10.5384 | 9.9833 | 9.2465 | 8.5384 | 7.6057 | 7.0067 | 4.6679 | 3.5037 | 3.271 | 14.4496 | 14.2577 | 13.972 | 13.6139 | 13.1537 | 12.4935 | 11.8526 | 10.9965 | 10.4139 | 8.1139 | 6.7322 | 4.7761 | 12.5996 | 12.4904 | 12.2159 | 11.8353 | 11.3302 | 10.6261 | 9.9628 | 9.071 | 8.4955 | 6.2486 | 5.1475 | 4.9577
|  | WOOTTON BASSETT PRIMARY | EE |  |  |  |  | 11.1608 | 11.1598 | 10.9598 | 10.5853 | 10.0455 | 9.3833 | 8.722 | 7.8639 | 7.3506 | 5.0833 | 3.8404 | 3.4108 | 14.4506 | 14.2588 | 13.9812 | 13.6475 | 13.1914 | 12.5853 | 11.97 | 11.17 | 10.6557 | 8.2088 | 6.7322 | 5.7873 | 12.6006 | 12.4904 | 12.2261 | 11.8771 | 11.3822 | 10.7465 | 10.122 | 9.2945 | 8.7965 | 6.572 | 5.371 | 4.9649
|  | WOOTTON BASSETT PRIMARY | HT |  |  |  |  | 11.1598 | 11.1608 | 10.9465 | 10.5384 | 9.9833 | 9.2465 | 8.5384 | 7.6057 | 7.0067 | 4.6679 | 3.5037 | 3.271 | 14.4496 | 14.2588 | 13.972 | 13.6139 | 13.1537 | 12.4935 | 11.8526 | 10.9965 | 10.4139 | 8.1139 | 7.0649 | 6.9506 | 12.5996 | 12.4904 | 12.2159 | 11.8353 | 11.3302 | 10.6261 | 9.9628 | 9.071 | 8.4955 | 6.2486 | 5.1475 | 4.9577
|  | WOOTTON BASSETT PRIMARY | HE |  |  |  |  | 11.1598 | 11.1588 | 10.9567 | 10.6149 | 10.0598 | 9.369 | 8.7302 | 7.8669 | 7.3751 | 5.3322 | 4.5547 | 4.1465 | 14.4496 | 14.2577 | 13.9802 | 13.6741 | 13.2067 | 12.569 | 11.97 | 11.1567 | 10.6547 | 8.4026 | 7.2955 | 6.2975 | 12.5996 | 12.4904 | 12.2251 | 11.9067 | 11.3986 | 10.7312 | 10.1169 | 9.2945 | 8.8139 | 6.8139 | 6.0577 | 5.669
|  | WOOTTON BASSETT PRIMARY | FB |  |  |  |  | 11.2771 | 11.3771 | 11.37 | 11.2496 | 11.0833 | 10.7496 | 10.4282 | 10.1343 | 9.8455 | 8.0537 | 6.3649 | 5.223 | 14.6128 | 14.6098 | 14.519 | 14.2486 | 13.9955 | 13.5955 | 13.2312 | 12.8812 | 12.5057 | 10.1792 | 7.519 | 4.7761 | 12.7659 | 12.8608 | 12.8679 | 12.6475 | 12.4292 | 12.0741 | 11.772 | 11.4894 | 11.2016 | 9.4486 | 7.773 | 6.6373
COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD PRIMARY | MINIMUM HEADROOM | SU 49244 98269 | NO | YES | 3.827 | -1.902 | -1.9398 | -2.4571 | -3.0836 | -3.4602 | -4.603 | -6.0724 | -7.5928 | -9.0796 | -14.3551 | -18.6367 | -21.8081 | 2.028 | 2.0443 | 1.6964 | 1.3657 | 0.98717 | 0.43309 | -0.27201 | -1.0241 | -1.7659 | -4.2934 | -6.3883 | -10.6792 | 0.39289 | 0.4235 | 0.069416 | -0.34589 | -0.64385 | -1.4887 | -2.5438 | -3.6561 | -4.7469 | -8.7102 | -11.5143 | -13.3571
|  | WOOTTON ROAD PRIMARY | EE |  |  |  |  | -1.902 | -1.9398 | -2.4571 | -3.0469 | -3.3806 | -4.603 | -6.0724 | -7.5928 | -9.0796 | -14.1857 | -18.2469 | -21.202 | 2.0545 | 2.079 | 1.7596 | 1.4525 | 1.1076 | 0.56472 | -0.067931 | -0.76793 | -1.4669 | -4.1679 | -6.2934 | -8.1149 | 0.39799 | 0.4235 | 0.069416 | -0.32956 | -0.59691 | -1.4857 | -2.5438 | -3.6561 | -4.7469 | -8.601 | -11.4847 | -13.3571
|  | WOOTTON ROAD PRIMARY | HT |  |  |  |  | -1.8775 | -1.8714 | -2.3296 | -2.8377 | -3.2132 | -4.3438 | -5.7449 | -7.2398 | -8.7122 | -14.3551 | -18.6367 | -21.8081 | 2.028 | 2.0443 | 1.6964 | 1.3657 | 0.98717 | 0.43309 | -0.27201 | -1.0241 | -1.7659 | -4.2934 | -5.9036 | -6.8649 | 0.39289 | 0.49493 | 0.11533 | -0.24385 | -0.55201 | -1.3918 | -2.449 | -3.5694 | -4.6755 | -8.7102 | -11.5143 | -13.3347
|  | WOOTTON ROAD PRIMARY | HE |  |  |  |  | -1.8928 | -1.9245 | -2.4438 | -3.0836 | -3.4602 | -4.5969 | -5.9796 | -7.4 | -8.799 | -13.2979 | -16.9316 | -19.7561 | 2.0535 | 2.078 | 1.7586 | 1.4494 | 1.0994 | 0.55044 | -0.079155 | -0.74752 | -1.4271 | -3.8934 | -5.9832 | -7.9904 | 0.40717 | 0.44493 | 0.085743 | -0.34589 | -0.64385 | -1.4887 | -2.4928 | -3.5336 | -4.5612 | -7.8847 | -10.4173 | -12.2734
|  | WOOTTON ROAD PRIMARY | FB |  |  |  |  | -1.5061 | -1.4224 | -1.449 | -1.6163 | -1.5938 | -2.0469 | -2.5551 | -3.051 | -3.6061 | -6.9041 | -10.9816 | -14.3857 | 2.1872 | 2.2259 | 2.2423 | 2.1913 | 2.1331 | 1.6913 | 1.281 | 0.87595 | 0.40656 | -2.4781 | -6.3883 | -10.6792 | 0.64697 | 0.80717 | 0.82554 | 0.74084 | 0.73064 | 0.48166 | 0.15513 | -0.20405 | -0.64385 | -3.2449 | -6.4887 | -9.0887
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | WRECCLESHAM PRIMARY | MINIMUM HEADROOM | SU 82093 44312 | NO | NO | 2.799 | 17.4543 | 17.5584 | 17.4645 | 17.0247 | 16.6594 | 16.0655 | 15.34 | 14.5553 | 13.7461 | 11.7206 | 10.6369 | 10.3645 | 21.7043 | 21.7359 | 21.5982 | 21.0992 | 20.738 | 20.2329 | 19.6022 | 18.9308 | 18.2227 | 16.3961 | 15.4971 | 12.8676 | 19.1043 | 19.1859 | 19.0737 | 18.5778 | 18.2288 | 17.6808 | 17.0063 | 16.2798 | 15.5186 | 13.6135 | 12.6951 | 12.5931
|  | WRECCLESHAM PRIMARY | EE |  |  |  |  | 17.4624 | 17.6196 | 17.6124 | 17.2869 | 17.0573 | 16.6461 | 16.1012 | 15.5012 | 14.9073 | 13.0869 | 11.942 | 11.5747 | 21.7104 | 21.7665 | 21.6686 | 21.2308 | 20.9155 | 20.5094 | 19.9624 | 19.3716 | 18.7798 | 16.7706 | 15.4971 | 14.6727 | 19.1094 | 19.2318 | 19.1869 | 18.7859 | 18.5063 | 18.1186 | 17.5747 | 16.9778 | 16.3869 | 14.6084 | 13.5931 | 13.3369
|  | WRECCLESHAM PRIMARY | HT |  |  |  |  | 17.4543 | 17.5584 | 17.4645 | 17.0247 | 16.6594 | 16.0655 | 15.34 | 14.5553 | 13.7461 | 11.7206 | 10.6369 | 10.3645 | 21.7043 | 21.7359 | 21.5982 | 21.0992 | 20.738 | 20.2329 | 19.6022 | 18.9308 | 18.2227 | 16.3961 | 15.5655 | 15.4757 | 19.1043 | 19.1859 | 19.0737 | 18.5778 | 18.2288 | 17.6808 | 17.0063 | 16.2798 | 15.5186 | 13.6135 | 12.6951 | 12.5931
|  | WRECCLESHAM PRIMARY | HE |  |  |  |  | 17.4624 | 17.6165 | 17.6135 | 17.2727 | 17.0349 | 16.6104 | 16.0869 | 15.4706 | 14.8869 | 13.2594 | 12.3278 | 11.9798 | 21.7104 | 21.7665 | 21.6686 | 21.2298 | 20.9104 | 20.5012 | 19.9849 | 19.389 | 18.8206 | 16.9359 | 15.9084 | 15.0104 | 19.1094 | 19.2298 | 19.189 | 18.7788 | 18.4931 | 18.0951 | 17.5849 | 16.9767 | 16.4043 | 14.789 | 14.0278 | 13.7665
|  | WRECCLESHAM PRIMARY | FB |  |  |  |  | 17.6645 | 17.8002 | 17.9033 | 18.0308 | 18.0022 | 17.9645 | 17.9135 | 17.8176 | 17.4655 | 16.1033 | 14.6022 | 13.7818 | 21.8737 | 21.8676 | 21.841 | 21.8788 | 21.7339 | 21.5359 | 21.3114 | 21.0471 | 20.5084 | 18.3267 | 15.6727 | 12.8676 | 19.3359 | 19.4349 | 19.5053 | 19.6267 | 19.5573 | 19.488 | 19.3961 | 19.2798 | 18.8369 | 17.3839 | 15.8859 | 15.0492
MINETY GSP | TOOTHILL BSP | WROUGHTON PRIMARY | MINIMUM HEADROOM | SU 14446 81504 | NO | NO | 4.447 | 10.5563 | 9.3828 | 9.2267 | 8.9624 | 8.7502 | 8.2716 | 7.6563 | 6.9767 | 6.2951 | 3.7808 | 2.1797 | 1.3655 | 12.7808 | 11.2685 | 11.0808 | 10.8348 | 10.6114 | 10.3287 | 9.9512 | 9.3675 | 8.8644 | 6.8002 | 5.6512 | 4.9175 | 11.2808 | 9.8083 | 9.6471 | 9.3981 | 9.1951 | 8.7451 | 8.1716 | 7.5124 | 6.8328 | 4.4226 | 3.092 | 2.5287
|  | WROUGHTON PRIMARY | EE |  |  |  |  | 10.5634 | 9.3828 | 9.2308 | 8.9644 | 8.8083 | 8.3583 | 7.6563 | 6.9767 | 6.2951 | 3.7808 | 2.1797 | 1.3655 | 12.7828 | 11.2685 | 11.0818 | 10.8359 | 10.6838 | 10.4716 | 9.9553 | 9.4226 | 8.8736 | 6.8002 | 5.6512 | 4.9175 | 11.2808 | 9.8104 | 9.6491 | 9.3981 | 9.2563 | 8.8614 | 8.1716 | 7.5124 | 6.8328 | 4.4226 | 3.092 | 2.5287
|  | WROUGHTON PRIMARY | HT |  |  |  |  | 10.5563 | 9.3869 | 9.2328 | 8.9726 | 8.7502 | 8.2716 | 7.744 | 7.0093 | 6.3869 | 4.4277 | 2.9206 | 2.0746 | 12.7808 | 11.2685 | 11.0808 | 10.8348 | 10.6114 | 10.3287 | 9.9512 | 9.3675 | 8.8644 | 7.6287 | 6.8961 | 6.6073 | 11.2848 | 9.8124 | 9.6532 | 9.4042 | 9.1951 | 8.7451 | 8.2614 | 7.5246 | 6.9093 | 5.1348 | 3.9675 | 3.4553
|  | WROUGHTON PRIMARY | HE |  |  |  |  | 10.5624 | 9.3828 | 9.2267 | 8.9624 | 8.8053 | 8.3451 | 7.8185 | 7.2308 | 6.6328 | 4.9012 | 3.7226 | 3.1073 | 12.7808 | 11.2685 | 11.0808 | 10.8348 | 10.6828 | 10.4644 | 10.1604 | 9.7593 | 9.3359 | 7.9461 | 7.2144 | 6.5726 | 11.2818 | 9.8083 | 9.6471 | 9.3991 | 9.2481 | 8.8481 | 8.3859 | 7.842 | 7.2797 | 5.7002 | 4.8726 | 4.4777
|  | WROUGHTON PRIMARY | FB |  |  |  |  | 10.7032 | 9.5022 | 9.4002 | 9.343 | 9.1542 | 9.1246 | 9.0144 | 8.8971 | 8.7144 | 7.5175 | 6.5481 | 5.9665 | 12.8624 | 11.3522 | 11.191 | 11.1155 | 10.891 | 10.8451 | 10.7093 | 10.5563 | 10.2614 | 8.7104 | 7.3869 | 5.9614 | 11.3971 | 9.9604 | 9.8359 | 9.7787 | 9.6083 | 9.59 | 9.4767 | 9.3716 | 9.1502 | 7.8144 | 6.9124 | 6.4012
AMERSHAM GSP | LOUDWATER BSP | WYCOMBE MARSH PRIMARY | MINIMUM HEADROOM | SU 88582 91845 | NO | YES | 4.443 | 12.7568 | 12.6629 | 12.6874 | 12.2792 | 11.9313 | 11.37 | 10.7476 | 10.0986 | 9.4833 | 6.9996 | 5.4241 | 4.9241 | 16.9874 | 16.9068 | 16.8884 | 16.3976 | 15.9496 | 15.4945 | 14.969 | 14.4129 | 13.8935 | 12.1047 | 11.417 | 8.7109 | 14.0915 | 14.0129 | 14.0333 | 13.6047 | 13.266 | 12.7884 | 12.2547 | 11.6956 | 11.1792 | 9.0925 | 7.8619 | 7.4353
|  | WYCOMBE MARSH PRIMARY | EE |  |  |  |  | 12.7568 | 12.6629 | 12.6935 | 12.3568 | 12.0925 | 11.6353 | 11.0629 | 10.47 | 9.9262 | 7.5333 | 5.8374 | 5.1486 | 16.9874 | 16.9068 | 16.8925 | 16.42 | 15.9904 | 15.5904 | 15.0568 | 14.5098 | 14.018 | 12.217 | 11.4282 | 10.5302 | 14.0915 | 14.0129 | 14.0333 | 13.6578 | 13.3823 | 12.9945 | 12.4813 | 11.9598 | 11.4915 | 9.3568 | 7.9486 | 7.4353
|  | WYCOMBE MARSH PRIMARY | HT |  |  |  |  | 12.767 | 12.6813 | 12.6874 | 12.2792 | 11.9313 | 11.37 | 10.7476 | 10.0986 | 9.4833 | 6.9996 | 5.4241 | 4.9241 | 16.9904 | 16.9098 | 16.8884 | 16.3976 | 15.9496 | 15.4945 | 14.969 | 14.4129 | 13.8935 | 12.1047 | 11.417 | 11.5109 | 14.1007 | 14.0292 | 14.0333 | 13.6047 | 13.266 | 12.7884 | 12.2547 | 11.6956 | 11.1792 | 9.0925 | 7.8619 | 7.5996
|  | WYCOMBE MARSH PRIMARY | HE |  |  |  |  | 12.77 | 12.6843 | 12.7241 | 12.3843 | 12.1251 | 11.6843 | 11.2068 | 10.6027 | 10.0904 | 8.1558 | 7.0047 | 6.4527 | 16.9925 | 16.9119 | 16.8966 | 16.4251 | 15.9996 | 15.5731 | 15.1139 | 14.516 | 14.0231 | 12.2629 | 11.6292 | 10.9772 | 14.1027 | 14.0333 | 14.0619 | 13.6823 | 13.4068 | 13.0149 | 12.6027 | 12.0456 | 11.5986 | 9.8394 | 8.9741 | 8.6129
|  | WYCOMBE MARSH PRIMARY | FB |  |  |  |  | 12.9404 | 12.9364 | 12.9945 | 13.0486 | 13.1517 | 13.1272 | 12.867 | 12.717 | 12.5384 | 11.3568 | 9.6517 | 8.5139 | 17.0884 | 17.0323 | 17.0037 | 16.966 | 16.969 | 16.8241 | 16.4364 | 16.1823 | 15.8874 | 14.0772 | 11.5272 | 8.7109 | 14.2711 | 14.2568 | 14.2966 | 14.3262 | 14.4139 | 14.3782 | 14.0629 | 13.8956 | 13.6966 | 12.4435 | 10.7833 | 9.6609
LOVEDEAN GSP | WYMERING BSP | WYMERING PRIMARY | MINIMUM HEADROOM | SU 64974 05375 | NO | YES | 14.319 | 37.6577 | 37.5475 | 37.3873 | 37.0465 | 36.5924 | 35.9333 | 34.8914 | 33.9435 | 32.9935 | 27.8965 | 24.7077 | 23.6628 | 37.1955 | 37.1486 | 37.0128 | 36.7822 | 36.4873 | 36.0455 | 35.4843 | 34.9159 | 34.3608 | 30.6026 | 27.5914 | 23.172 | 39.4424 | 39.4333 | 39.3343 | 39.0547 | 38.6424 | 38.0782 | 37.4118 | 36.6833 | 35.8435 | 31.019 | 27.8394 | 26.5057
|  | WYMERING PRIMARY | EE |  |  |  |  | 37.6577 | 37.5475 | 37.3873 | 37.0465 | 36.5924 | 36.0475 | 35.0343 | 34.119 | 33.1986 | 28.3588 | 25.0455 | 23.6628 | 37.1955 | 37.1496 | 37.0312 | 36.8445 | 36.5608 | 36.1771 | 35.6333 | 35.1026 | 34.5802 | 30.6026 | 27.5914 | 25.6435 | 39.4424 | 39.4333 | 39.3343 | 39.0547 | 38.6608 | 38.1384 | 37.4761 | 36.8312 | 36.0333 | 31.219 | 27.8394 | 26.5057
|  | WYMERING PRIMARY | HT |  |  |  |  | 37.6782 | 37.5914 | 37.4567 | 37.122 | 36.7108 | 35.9333 | 34.8914 | 33.9435 | 32.9935 | 27.8965 | 24.7077 | 23.8873 | 37.1986 | 37.1486 | 37.0128 | 36.7822 | 36.4873 | 36.0455 | 35.4843 | 34.9159 | 34.3608 | 31.0077 | 29.0159 | 28.622 | 39.4608 | 39.4628 | 39.3465 | 39.0669 | 38.6424 | 38.0782 | 37.4118 | 36.6833 | 35.8435 | 31.019 | 28.0496 | 27.2547
|  | WYMERING PRIMARY | HE |  |  |  |  | 37.672 | 37.5741 | 37.4292 | 37.1098 | 36.6761 | 36.2026 | 35.2261 | 34.3853 | 33.519 | 29.5782 | 27.6782 | 26.5333 | 37.1986 | 37.1547 | 37.0384 | 36.8506 | 36.572 | 36.2312 | 35.7139 | 35.2241 | 34.7322 | 31.2782 | 29.1506 | 27.1424 | 39.4567 | 39.4659 | 39.3812 | 39.12 | 38.7139 | 38.2506 | 37.6373 | 37.0486 | 36.3435 | 32.5455 | 30.6404 | 29.4904
|  | WYMERING PRIMARY | FB |  |  |  |  | 37.8067 | 37.8343 | 37.6914 | 37.6628 | 37.4659 | 37.3006 | 37.1261 | 36.9435 | 36.7057 | 34.6598 | 31.069 | 29.0496 | 37.3128 | 37.3016 | 37.1526 | 37.1557 | 36.8914 | 36.5986 | 36.2802 | 35.9445 | 35.5588 | 33.1108 | 28.0404 | 23.172 | 39.6384 | 39.6986 | 39.6659 | 39.7169 | 39.5618 | 39.4077 | 39.2077 | 38.9853 | 38.722 | 37.0649 | 33.4822 | 31.2924
COWLEY GSP | YARNTON BSP | YARNTON PRIMARY | MINIMUM HEADROOM | SP 48277 12108 | NO | YES | 43.367 | -13.4006 | -14.9823 | -16.2027 | -17.6057 | -19.5966 | -21.6833 | -23.8904 | -25.8139 | -27.3578 | -33.0272 | -36.4557 | -38.1537 | -7.367 | -9.066 | -9.57 | -10.1762 | -11.1904 | -12.1119 | -13.1445 | -14.0802 | -14.8466 | -18.1608 | -20.0476 | -22.8353 | -10.5272 | -12.1231 | -12.8466 | -13.7802 | -15.3557 | -17.016 | -18.8364 | -20.4353 | -21.8078 | -26.6435 | -29.1935 | -29.968
|  | YARNTON PRIMARY | EE |  |  |  |  | -13.4006 | -13.7762 | -16.1955 | -17.5864 | -19.4017 | -21.2792 | -23.2996 | -25.3057 | -27.0568 | -32.5904 | -35.5741 | -36.9741 | -7.3568 | -7.5608 | -9.4598 | -9.9853 | -10.6925 | -11.4445 | -12.3323 | -13.219 | -13.9915 | -17.7945 | -20.0476 | -21.3068 | -10.5251 | -10.7241 | -12.769 | -13.718 | -14.9955 | -16.4598 | -18.1129 | -19.7343 | -21.1782 | -26.0343 | -28.4935 | -29.2629
|  | YARNTON PRIMARY | HT |  |  |  |  | -13.3782 | -14.9823 | -16.1813 | -17.5823 | -19.5966 | -21.6833 | -23.8904 | -25.8139 | -27.3578 | -33.0272 | -36.4557 | -38.1537 | -7.367 | -9.066 | -9.57 | -10.1762 | -11.1904 | -12.1119 | -13.1445 | -14.0802 | -14.8466 | -18.1608 | -19.7782 | -19.9741 | -10.5272 | -12.1231 | -12.8466 | -13.7802 | -15.3557 | -17.016 | -18.8364 | -20.4353 | -21.8078 | -26.6435 | -29.1935 | -29.968
|  | YARNTON PRIMARY | HE |  |  |  |  | -13.3986 | -13.7731 | -16.2027 | -17.6057 | -19.4343 | -21.3506 | -23.4098 | -25.4476 | -27.2486 | -31.8588 | -34.3047 | -35.3915 | -7.3568 | -7.5608 | -9.4619 | -9.9864 | -10.6955 | -11.4568 | -12.3517 | -13.2415 | -14.0241 | -17.3578 | -19.0945 | -20.5078 | -10.5231 | -10.7241 | -12.7711 | -13.7272 | -15.018 | -16.4996 | -18.1782 | -19.8149 | -21.2915 | -25.3537 | -27.1333 | -27.8425
|  | YARNTON PRIMARY | FB |  |  |  |  | -13.0976 | -13.1986 | -14.0935 | -16.12 | -17.2313 | -18.0455 | -18.9843 | -19.7588 | -20.5588 | -24.5455 | -27.0037 | -28.2986 | -7.2108 | -7.2619 | -7.6302 | -9.418 | -9.8792 | -10.2343 | -10.7343 | -11.1925 | -11.6466 | -15.2986 | -19.02 | -22.8353 | -10.3466 | -10.3762 | -10.8598 | -12.7782 | -13.4466 | -13.9374 | -14.666 | -15.3537 | -16.068 | -19.7292 | -22.2874 | -23.6588
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | YATTENDON PRIMARY | MINIMUM HEADROOM | SU 53699 74307 | NO | NO | 1.469 | 5.6631 | 5.6978 | 5.4896 | 5.3324 | 5.0273 | 4.5927 | 3.6222 | 1.7324 | -1.8829 | -5.1053 | -9.2033 | -13.74 | 8.6416 | 8.6324 | 8.4202 | 8.3151 | 8.0743 | 7.7855 | 6.8518 | 4.9284 | 0.71918 | -2.9033 | -7.1798 | -12.54 | 6.9978 | 7.0141 | 6.7498 | 6.6182 | 6.3161 | 5.9549 | 4.9488 | 2.861 | -1.4482 | -5.092 | -9.5278 | -14.8206
|  | YATTENDON PRIMARY | EE |  |  |  |  | 5.6631 | 5.6978 | 5.4988 | 5.3661 | 5.0947 | 4.6947 | 4.0355 | 3.1927 | 2.0212 | -0.94714 | -6.3645 | -8.5073 | 8.6427 | 8.6324 | 8.4355 | 8.3631 | 8.1559 | 7.9131 | 7.3824 | 6.6192 | 5.4243 | 2.5222 | -3.492 | -5.7686 | 6.9978 | 7.0141 | 6.762 | 6.66 | 6.3967 | 6.0763 | 5.46 | 4.5988 | 3.3202 | 0.23857 | -5.8961 | -8.1247
|  | YATTENDON PRIMARY | HT |  |  |  |  | 5.6641 | 5.7039 | 5.4896 | 5.3324 | 5.0273 | 4.5927 | 3.6222 | 2.6161 | 0.64776 | -2.6655 | -7.8553 | -11.54 | 8.6416 | 8.6345 | 8.4202 | 8.3151 | 8.0743 | 7.7855 | 6.8518 | 5.862 | 3.6876 | 0.34061 | -5.0788 | -8.8145 | 6.9978 | 7.0171 | 6.7498 | 6.6182 | 6.3161 | 5.9549 | 4.9488 | 3.8824 | 1.611 | -1.9747 | -7.7043 | -11.6961
|  | YATTENDON PRIMARY | HE |  |  |  |  | 5.6651 | 5.7029 | 5.5039 | 5.3478 | 5.0478 | 4.6182 | 3.6243 | 1.7324 | -1.8829 | -5.1053 | -9.2033 | -13.74 | 8.6416 | 8.6335 | 8.4345 | 8.361 | 8.1427 | 7.8957 | 6.9824 | 4.9284 | 0.71918 | -2.9033 | -7.1798 | -12.54 | 6.9988 | 7.0171 | 6.7641 | 6.6518 | 6.3692 | 6.0355 | 5.0192 | 2.861 | -1.4482 | -5.092 | -9.5278 | -14.8206
|  | YATTENDON PRIMARY | FB |  |  |  |  | 5.8263 | 5.9233 | 5.9712 | 5.9855 | 5.9376 | 5.7712 | 5.5335 | 5.2345 | 4.6386 | 2.5396 | -0.11653 | -2.2686 | 8.7427 | 8.761 | 8.7467 | 8.7202 | 8.6835 | 8.4927 | 8.2059 | 7.8263 | 7.0814 | 4.5988 | 1.2855 | -1.8716 | 7.1008 | 7.1437 | 7.1702 | 7.1416 | 7.0978 | 6.9845 | 6.7202 | 6.3702 | 5.6447 | 3.2937 | 0.29265 | -2.238
MELKSHAM GSP | CHIPPENHAM BSP | YATTON KEYNELL PRIMARY | MINIMUM HEADROOM | ST 87300 75782 | YES | YES | 2.114 | 0.74235 | 0.74031 | 0.7301 | 0.56276 | 0.33827 | 0.18827 | -0.10663 | -0.40561 | -0.73724 | -1.924 | -2.6199 | -2.9821 | 0.05102 | 0.039796 | 0.02551 | -0.072449 | -0.23061 | -0.31837 | -0.5051 | -0.7102 | -0.93061 | -1.7612 | -2.1806 | -2.5347 | -0.1398 | -0.14898 | -0.16122 | -0.40714 | -0.60612 | -0.71122 | -0.9551 | -1.2102 | -1.4969 | -2.4816 | -2.9816 | -3.2
|  | YATTON KEYNELL PRIMARY | EE |  |  |  |  | 0.74235 | 0.74031 | 0.7301 | 0.56378 | 0.35561 | 0.19235 | -0.093367 | -0.36684 | -0.69439 | -1.924 | -2.6199 | -2.9821 | 0.05102 | 0.040816 | 0.02551 | -0.067347 | -0.23061 | -0.30714 | -0.49694 | -0.67245 | -0.89796 | -1.7612 | -2.1806 | -2.4153 | -0.1398 | -0.14898 | -0.1602 | -0.4051 | -0.60612 | -0.70918 | -0.95204 | -1.1867 | -1.4694 | -2.4816 | -2.9816 | -3.2
|  | YATTON KEYNELL PRIMARY | HT |  |  |  |  | 0.74745 | 0.74133 | 0.74031 | 0.56276 | 0.38827 | 0.19745 | -0.072959 | -0.36173 | -0.68112 | -1.825 | -2.5179 | -2.923 | 0.057143 | 0.039796 | 0.028571 | -0.072449 | -0.2102 | -0.31837 | -0.5051 | -0.7102 | -0.93061 | -1.7112 | -1.998 | -2.0673 | -0.12653 | -0.14898 | -0.16122 | -0.40714 | -0.57347 | -0.71122 | -0.94388 | -1.1949 | -1.4786 | -2.4347 | -2.9112 | -3.1245
|  | YATTON KEYNELL PRIMARY | HE |  |  |  |  | 0.74847 | 0.74235 | 0.74133 | 0.56378 | 0.33827 | 0.18827 | -0.10663 | -0.40561 | -0.73724 | -1.6291 | -2.327 | -2.6281 | 0.057143 | 0.039796 | 0.030612 | -0.062245 | -0.22857 | -0.29286 | -0.49082 | -0.68265 | -0.9102 | -1.5551 | -1.9633 | -2.1929 | -0.12653 | -0.14796 | -0.1602 | -0.40306 | -0.59388 | -0.70306 | -0.9551 | -1.2102 | -1.4969 | -2.2449 | -2.7418 | -2.9245
|  | YATTON KEYNELL PRIMARY | FB |  |  |  |  | 0.80051 | 0.81786 | 0.83112 | 0.8301 | 0.80867 | 0.80561 | 0.775 | 0.66276 | 0.54745 | -0.077041 | -0.7699 | -1.2954 | 0.094898 | 0.095918 | 0.091837 | 0.087755 | 0.064286 | 0.041837 | 0.0061224 | -0.14388 | -0.26837 | -0.9102 | -1.7133 | -2.5347 | -0.060204 | -0.041837 | -0.029592 | -0.021429 | -0.031633 | -0.053061 | -0.095918 | -0.32245 | -0.41837 | -0.99898 | -1.6306 | -2.0959
AXMINSTER GSP | YEOVIL BSP | YEOVIL PRIMARY | MINIMUM HEADROOM | ST 57690 16833 | NO | NO | 7.19 | 9.5322 | 9.3862 | 9.3005 | 8.9883 | 8.4383 | 7.9669 | 7.2964 | 6.4332 | 5.825 | 2.8454 | 0.88318 | -0.226 | 10.6516 | 10.4444 | 10.3138 | 9.9862 | 9.422 | 8.9495 | 8.3138 | 7.4271 | 6.8301 | 3.7107 | 1.3873 | -3.525 | 9.8893 | 9.7373 | 9.6516 | 9.3587 | 8.8352 | 8.3771 | 7.7352 | 6.8985 | 6.3128 | 3.4444 | 1.6138 | 0.61482
|  | YEOVIL PRIMARY | EE |  |  |  |  | 9.5322 | 9.3862 | 9.3005 | 8.9883 | 8.4403 | 7.9669 | 7.3281 | 6.4332 | 5.8587 | 2.8454 | 0.88318 | -0.226 | 10.6516 | 10.4505 | 10.3179 | 9.9862 | 9.4332 | 8.9597 | 8.3271 | 7.4638 | 6.9077 | 3.7107 | 1.6311 | -0.080082 | 9.8893 | 9.7373 | 9.6516 | 9.3587 | 8.8393 | 8.3771 | 7.7607 | 6.9026 | 6.3505 | 3.4444 | 1.6138 | 0.61482
|  | YEOVIL PRIMARY | HT |  |  |  |  | 9.5342 | 9.3903 | 9.3097 | 8.9964 | 8.5301 | 7.9811 | 7.2964 | 6.4883 | 5.9403 | 3.0413 | 1.4577 | 0.93522 | 10.6516 | 10.4444 | 10.3138 | 9.9862 | 9.5179 | 8.9903 | 8.325 | 7.526 | 6.9832 | 4.2658 | 2.9342 | 2.5036 | 9.8934 | 9.7424 | 9.6638 | 9.3658 | 8.925 | 8.3924 | 7.7352 | 6.9607 | 6.4301 | 3.6332 | 2.1413 | 1.6954
|  | YEOVIL PRIMARY | HE |  |  |  |  | 9.5383 | 9.3995 | 9.324 | 9.0097 | 8.4383 | 7.9771 | 7.3403 | 6.4342 | 5.825 | 3.3464 | 1.8801 | 1.3067 | 10.6536 | 10.4505 | 10.3199 | 9.9903 | 9.422 | 8.9495 | 8.3138 | 7.4271 | 6.8301 | 3.9689 | 2.1209 | 0.65665 | 9.8954 | 9.7485 | 9.672 | 9.374 | 8.8352 | 8.3832 | 7.7658 | 6.8985 | 6.3128 | 3.9158 | 2.5301 | 2.0271
|  | YEOVIL PRIMARY | FB |  |  |  |  | 9.6975 | 9.672 | 9.623 | 9.474 | 9.3546 | 9.1505 | 8.8944 | 8.4811 | 8.2209 | 6.1944 | 3.8148 | 1.8067 | 10.7434 | 10.6128 | 10.4618 | 10.2373 | 10.0189 | 9.7016 | 9.3291 | 8.7944 | 8.4322 | 5.474 | 1.3873 | -3.525 | 10.0607 | 10.0271 | 9.975 | 9.8362 | 9.7281 | 9.5342 | 9.2913 | 8.8873 | 8.6393 | 6.6546 | 4.3546 | 2.4454
AXMINSTER GSP | YEOVIL BSP | YETMINSTER PRIMARY | MINIMUM HEADROOM | ST 60294 10206 | NO | NO | 0.717 | 8.0418 | 8.0235 | 7.7347 | 7.5 | 7.0551 | 6.499 | 5.8622 | 5.2163 | 4.5622 | 2.702 | 0.95816 | 0.14796 | 9.9594 | 9.891 | 9.5471 | 9.391 | 9.0145 | 8.6818 | 8.2676 | 7.841 | 7.4002 | 6.0267 | 5.2849 | 5.5104 | 8.4055 | 8.3535 | 8.0565 | 7.8851 | 7.4933 | 7.0504 | 6.5147 | 5.9769 | 5.4269 | 3.8178 | 2.5759 | 2.279
|  | YETMINSTER PRIMARY | EE |  |  |  |  | 8.0469 | 8.0367 | 7.799 | 7.6714 | 7.3653 | 6.8786 | 6.3337 | 5.8143 | 5.3071 | 3.3194 | 1.7102 | 1.0724 | 9.9614 | 9.9012 | 9.5716 | 9.438 | 9.1339 | 8.8084 | 8.4359 | 8.0247 | 7.6186 | 6.2196 | 5.4278 | 5.5104 | 8.4096 | 8.3637 | 8.1035 | 8.0014 | 7.7198 | 7.3198 | 6.8545 | 6.3943 | 5.9433 | 4.2637 | 3.081 | 2.8096
|  | YETMINSTER PRIMARY | HT |  |  |  |  | 8.0418 | 8.0235 | 7.7347 | 7.5 | 7.0551 | 6.499 | 5.8622 | 5.2163 | 4.5622 | 2.702 | 0.95816 | 0.14796 | 9.9594 | 9.891 | 9.5471 | 9.391 | 9.0145 | 8.6818 | 8.2676 | 7.841 | 7.4002 | 6.0267 | 5.2849 | 5.5584 | 8.4055 | 8.3535 | 8.0565 | 7.8851 | 7.4933 | 7.0504 | 6.5147 | 5.9769 | 5.4269 | 3.8178 | 2.5759 | 2.279
|  | YETMINSTER PRIMARY | HE |  |  |  |  | 8.049 | 8.0398 | 7.799 | 7.6337 | 7.3 | 6.7776 | 6.2194 | 5.649 | 5.1398 | 3.7133 | 2.2704 | 1.5082 | 9.9594 | 9.9012 | 9.5706 | 9.4359 | 9.1237 | 8.7982 | 8.4492 | 8.0339 | 7.6686 | 6.5461 | 6.0716 | 5.9237 | 8.4096 | 8.3657 | 8.1035 | 7.981 | 7.681 | 7.2586 | 6.7984 | 6.3076 | 5.8688 | 4.6137 | 3.6249 | 3.1678
|  | YETMINSTER PRIMARY | FB |  |  |  |  | 8.1959 | 8.2551 | 8.2929 | 8.3041 | 8.1245 | 8.0439 | 7.899 | 7.7602 | 7.5929 | 6.3561 | 5.2235 | 4.5551 | 10.0492 | 10.0298 | 10.0053 | 9.9614 | 9.6727 | 9.5818 | 9.4257 | 9.2829 | 9.1084 | 7.9471 | 6.9512 | 5.7727 | 8.5504 | 8.5769 | 8.5973 | 8.5831 | 8.38 | 8.3045 | 8.1616 | 8.0259 | 7.8657 | 6.7004 | 5.6678 | 5.0565
IVER 66KV GSP |  | YIEWSLEY PRIMARY | MINIMUM HEADROOM | TQ 05643 80961 | NO | NO | 18.752 | 21.4555 | 21.4708 | 21.2412 | 20.8066 | 20.0372 | 19.0106 | 17.7423 | 16.3637 | 14.829 | 9.3698 | 5.5117 | 4.1188 | 27.7627 | 27.5912 | 27.2647 | 26.7851 | 25.6902 | 24.681 | 23.3851 | 21.9474 | 20.3382 | 15.1576 | 11.5147 | 7.3861 | 23.7627 | 23.6882 | 23.3912 | 22.9076 | 22.0759 | 21.1055 | 19.8821 | 18.531 | 17.0025 | 11.4739 | 7.381 | 5.8086
|  | YIEWSLEY PRIMARY | EE |  |  |  |  | 21.4555 | 21.5198 | 21.43 | 21.2657 | 20.7719 | 20.0239 | 18.8137 | 17.628 | 16.2963 | 10.5351 | 5.8433 | 4.1188 | 27.7627 | 27.6453 | 27.4076 | 26.9657 | 25.9168 | 25.0157 | 23.5555 | 22.1249 | 20.5351 | 15.1576 | 11.5147 | 9.0361 | 23.7627 | 23.7178 | 23.5229 | 23.2566 | 22.6678 | 21.93 | 20.6688 | 19.4463 | 18.0606 | 12.0994 | 7.381 | 5.8086
|  | YIEWSLEY PRIMARY | HT |  |  |  |  | 21.4821 | 21.4708 | 21.2412 | 20.8066 | 20.0372 | 19.0106 | 17.7423 | 16.3637 | 14.829 | 9.3698 | 5.5117 | 4.3463 | 27.7637 | 27.5912 | 27.2647 | 26.7851 | 25.6902 | 24.681 | 23.3851 | 21.9474 | 20.3382 | 15.3004 | 12.6943 | 12.4637 | 23.7882 | 23.6882 | 23.3912 | 22.9076 | 22.0759 | 21.1055 | 19.8821 | 18.531 | 17.0025 | 11.4739 | 7.6708 | 6.63
|  | YIEWSLEY PRIMARY | HE |  |  |  |  | 21.48 | 21.5668 | 21.5004 | 21.3076 | 20.7841 | 20.0729 | 19.1004 | 18.0821 | 16.9453 | 13.5351 | 10.8433 | 9.3668 | 27.7647 | 27.6504 | 27.4157 | 26.9637 | 25.9147 | 25.0106 | 23.8086 | 22.5474 | 21.1576 | 17.2637 | 15.2392 | 12.7617 | 23.7851 | 23.7596 | 23.5872 | 23.2933 | 22.6841 | 21.98 | 21.0025 | 19.9831 | 18.831 | 15.2861 | 12.7076 | 11.3372
|  | YIEWSLEY PRIMARY | FB |  |  |  |  | 21.8004 | 22.0086 | 22.2331 | 22.3106 | 22.3188 | 22.2392 | 22.0637 | 21.7841 | 21.527 | 18.9688 | 14.627 | 11.23 | 27.9055 | 27.8229 | 27.7668 | 27.5943 | 27.3025 | 26.8923 | 26.3831 | 25.7627 | 25.2096 | 20.9076 | 14.5014 | 7.3861 | 24.131 | 24.228 | 24.3606 | 24.3596 | 24.2861 | 24.1382 | 23.8974 | 23.5341 | 23.2617 | 20.5045 | 16.1963 | 12.8127
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ZETLAND ROAD PRIMARY | MINIMUM HEADROOM | SU 60592 00043 | NO | YES | 0 | 8.2569 | 8.3426 | 8.3028 | 7.8242 | 7.2058 | 6.3262 | 5.2528 | 4.012 | 3.0273 | -1.8472 | -5.3901 | -7.0472 | 11.762 | 11.6538 | 11.4742 | 11.1354 | 10.6834 | 10.0599 | 9.2415 | 8.2487 | 7.5038 | 3.7538 | -0.54519 | -7.8309 | 23.1752 | 22.9609 | 22.6701 | 22.0722 | 21.3089 | 20.5303 | 19.5232 | 18.3099 | 17.3783 | 13.0926 | 10.5109 | 9.3885
|  | ZETLAND ROAD PRIMARY | EE |  |  |  |  | 8.2722 | 8.3885 | 8.3926 | 8.0293 | 7.4344 | 6.6395 | 5.6201 | 4.413 | 3.5691 | -0.90641 | -5.0258 | -7.0472 | 11.7793 | 11.6956 | 11.5466 | 11.2671 | 10.7813 | 10.214 | 9.4446 | 8.4793 | 7.8171 | 3.7538 | 0.15175 | -2.8891 | 23.1803 | 22.9722 | 22.6966 | 22.1487 | 21.3609 | 20.614 | 19.6334 | 18.4426 | 17.5803 | 13.6456 | 11.0701 | 9.3885
|  | ZETLAND ROAD PRIMARY | HT |  |  |  |  | 8.2569 | 8.3426 | 8.3028 | 7.8242 | 7.2058 | 6.3262 | 5.2528 | 4.012 | 3.0273 | -1.8472 | -5.3901 | -6.587 | 11.762 | 11.6538 | 11.4742 | 11.1354 | 10.6834 | 10.0599 | 9.2415 | 8.2487 | 7.5038 | 4.2946 | 2.1528 | 1.4538 | 23.1752 | 22.9609 | 22.6701 | 22.0722 | 21.3089 | 20.5303 | 19.5232 | 18.3099 | 17.3783 | 13.0926 | 10.5109 | 9.9558
|  | ZETLAND ROAD PRIMARY | HE |  |  |  |  | 8.3038 | 8.4324 | 8.4548 | 8.0722 | 7.4895 | 6.7405 | 5.7875 | 4.6599 | 3.8691 | 0.50481 | -1.7391 | -3.0778 | 11.7905 | 11.6977 | 11.5528 | 11.2701 | 10.8109 | 10.2171 | 9.4375 | 8.4885 | 7.814 | 4.1926 | 1.5242 | -1.2391 | 23.1956 | 22.9844 | 22.715 | 22.1548 | 21.3813 | 20.6181 | 19.6446 | 18.4773 | 17.615 | 14.1375 | 12.3997 | 11.5926
|  | ZETLAND ROAD PRIMARY | FB |  |  |  |  | 8.5252 | 8.6538 | 8.7905 | 8.9109 | 8.8466 | 8.5926 | 8.3813 | 8.113 | 7.7589 | 5.6018 | 2.1334 | -0.71968 | 11.8558 | 11.714 | 11.565 | 11.4436 | 11.1283 | 10.6691 | 10.2262 | 9.7415 | 9.1609 | 5.3191 | -0.54519 | -7.8309 | 23.462 | 23.2977 | 23.1507 | 23.0079 | 22.7283 | 22.3681 | 22.0701 | 21.7038 | 21.213 | 18.3558 | 15.2956 | 13.2007

## Primary Headroom Generation
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Generation (MVA) | Generation Headroom Winter (MVA) | [11 empty] | Generation Headroom Summer (MVA) | [11 empty] | Generation Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH BSP | ALDERNEY PRIMARY | MINIMUM HEADROOM | SZ 04270 95141 | NO | YES | 0 | 22.8804 | 39.1758 | 38.9 | 38.5137 | 38.0747 | 37.4895 | 36.9274 | 36.3263 | 35.7326 | 34.3705 | 33.3926 | 32.5179 | 19.6429 | 34.9568 | 34.6558 | 34.2368 | 33.7621 | 33.12 | 32.5042 | 31.8432 | 31.1884 | 29.6905 | 28.6042 | 27.6295 | 20.1516 | 35.9895 | 35.6895 | 35.2695 | 34.7958 | 34.1547 | 33.54 | 32.8789 | 32.2253 | 30.7295 | 29.6442 | 28.6705
|  | ALDERNEY PRIMARY | EE |  |  |  |  | 22.8804 | 39.1758 | 38.9295 | 38.6474 | 38.3084 | 37.9811 | 37.6579 | 37.3232 | 37.0021 | 36.3253 | 35.6368 | 35.0526 | 19.6429 | 34.9568 | 34.6916 | 34.3926 | 34.04 | 33.6979 | 33.3579 | 33.0053 | 32.6674 | 31.9 | 31.1168 | 30.4505 | 20.1516 | 35.9895 | 35.7242 | 35.4253 | 35.0737 | 34.7305 | 34.3916 | 34.0389 | 33.7 | 32.9347 | 32.1526 | 31.4884
|  | ALDERNEY PRIMARY | HT |  |  |  |  | 22.9214 | 39.1947 | 38.9 | 38.5137 | 38.0747 | 37.4895 | 36.9274 | 36.3263 | 35.7326 | 34.3705 | 33.3926 | 32.5179 | 19.6882 | 34.9758 | 34.6558 | 34.2368 | 33.7621 | 33.12 | 32.5042 | 31.8432 | 31.1884 | 29.6905 | 28.6042 | 27.6295 | 20.1979 | 36.0084 | 35.6895 | 35.2695 | 34.7958 | 34.1547 | 33.54 | 32.8789 | 32.2253 | 30.7295 | 29.6442 | 28.6705
|  | ALDERNEY PRIMARY | HE |  |  |  |  | 23.0488 | 39.4095 | 39.2179 | 38.9789 | 38.6716 | 38.3853 | 38.1158 | 37.8368 | 37.5705 | 37.3168 | 36.8926 | 36.5326 | 19.8282 | 35.2189 | 35.02 | 34.7737 | 34.4568 | 34.1611 | 33.8842 | 33.5958 | 33.3221 | 33.0221 | 32.5295 | 32.1116 | 20.3432 | 36.2558 | 36.0537 | 35.8063 | 35.4884 | 35.1937 | 34.9168 | 34.6284 | 34.3547 | 34.0558 | 33.5642 | 33.1463
|  | ALDERNEY PRIMARY | FB |  |  |  |  | 23.1941 | 39.5968 | 39.4937 | 39.3842 | 39.2674 | 39.1516 | 39.04 | 38.9337 | 38.8253 | 38.34 | 37.8674 | 37.4589 | 19.9755 | 35.4116 | 35.3021 | 35.1863 | 35.0621 | 34.9368 | 34.8168 | 34.7032 | 34.5853 | 34.0558 | 33.5232 | 33.0568 | 20.4989 | 36.4505 | 36.3379 | 36.22 | 36.0947 | 35.9695 | 35.8495 | 35.7358 | 35.6189 | 35.0895 | 34.5568 | 34.0916
FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT PRIMARY | MINIMUM HEADROOM | SU 85976 48834 | NO | YES | 0.12211 | 22.7211 | 22.5305 | 22.3021 | 21.9905 | 21.6074 | 21.1842 | 20.4421 | 19.5116 | 18.5663 | 17.4926 | 16.3579 | 15.3579 | 18.6232 | 18.2684 | 17.8032 | 17.1232 | 16.2411 | 15.2211 | 14.2653 | 13.2811 | 12.2811 | 11.0779 | 9.8821 | 8.8284 | 18.8558 | 18.5853 | 18.2411 | 17.7516 | 17.1263 | 16.4147 | 15.7389 | 15.0505 | 14.3558 | 13.7884 | 12.9274 | 12.1705
|  | ALDERSHOT PRIMARY | EE |  |  |  |  | 22.7211 | 22.5305 | 22.3158 | 22.0316 | 21.6547 | 21.2853 | 20.9484 | 20.6084 | 20.2705 | 20.8442 | 20.1684 | 19.5337 | 18.6232 | 18.2684 | 17.9042 | 17.4337 | 16.82 | 16.2221 | 15.7684 | 15.3074 | 14.8316 | 14.76 | 13.9537 | 13.2737 | 18.8558 | 18.5853 | 18.2968 | 17.9242 | 17.4326 | 16.9516 | 16.5589 | 16.16 | 15.7547 | 16.0589 | 15.5463 | 15.1179
|  | ALDERSHOT PRIMARY | HT |  |  |  |  | 22.7316 | 22.5453 | 22.3021 | 21.9905 | 21.6074 | 21.1842 | 20.4421 | 19.5116 | 18.5663 | 17.4926 | 16.3579 | 15.3579 | 18.6832 | 18.2832 | 17.8032 | 17.1232 | 16.2411 | 15.2211 | 14.2653 | 13.2811 | 12.2811 | 11.0779 | 9.8821 | 8.8284 | 18.8895 | 18.6 | 18.2411 | 17.7516 | 17.1263 | 16.4147 | 15.7389 | 15.0505 | 14.3558 | 13.7884 | 12.9274 | 12.1705
|  | ALDERSHOT PRIMARY | HE |  |  |  |  | 22.7821 | 22.6084 | 22.4095 | 22.1389 | 21.7726 | 21.4242 | 21.0947 | 20.76 | 20.4295 | 21.2663 | 21.1863 | 21.1274 | 18.8726 | 18.6137 | 18.3316 | 17.9295 | 17.3653 | 16.8263 | 16.4347 | 16.0316 | 15.6179 | 16.0495 | 15.5716 | 15.1674 | 19.0074 | 18.7926 | 18.5537 | 18.2189 | 17.7579 | 17.3168 | 16.9579 | 16.5895 | 16.2189 | 16.9011 | 16.6284 | 16.4021
|  | ALDERSHOT PRIMARY | FB |  |  |  |  | 22.92 | 22.8305 | 22.7547 | 22.6663 | 22.5695 | 22.4695 | 22.3768 | 22.2916 | 22.1989 | 22.7011 | 22.4937 | 22.3537 | 19.1168 | 18.9189 | 18.7737 | 18.5905 | 18.3758 | 18.1453 | 17.9863 | 17.8326 | 17.6632 | 17.7726 | 17.1779 | 16.6779 | 19.1968 | 19.0558 | 18.9453 | 18.8116 | 18.6579 | 18.4937 | 18.3695 | 18.2516 | 18.1211 | 18.4758 | 18.0811 | 17.7663
MELKSHAM GSP | CHIPPENHAM BSP | ALDERTON PRIMARY | MINIMUM HEADROOM | ST 84609 84059 | NO | YES | 0 | 3.5674 | 3.4842 | 3.3989 | 14.5521 | 14.4289 | 14.2879 | 14.1426 | 13.9742 | 13.7984 | 13.3153 | 12.9174 | 12.5616 | 3.1747 | 3.0832 | 2.9905 | 13.2363 | 13.1005 | 12.9437 | 12.7826 | 12.5995 | 12.4068 | 11.8711 | 11.4237 | 11.0216 | 3.4032 | 3.3116 | 3.2189 | 13.9126 | 13.7768 | 13.6211 | 13.4589 | 13.2747 | 13.0821 | 12.5474 | 12.0979 | 11.6947
|  | ALDERTON PRIMARY | EE |  |  |  |  | 3.5674 | 3.4842 | 3.3989 | 14.5521 | 14.4405 | 14.3363 | 14.2258 | 14.1111 | 14.0058 | 13.7289 | 13.4163 | 13.1563 | 3.1747 | 3.0832 | 2.9905 | 13.2363 | 13.1195 | 13.01 | 12.89 | 12.7668 | 12.6542 | 12.3437 | 11.99 | 11.6932 | 3.4032 | 3.3116 | 3.2189 | 13.9126 | 13.7958 | 13.6842 | 13.5642 | 13.4411 | 13.3274 | 13.0147 | 12.66 | 12.3611
|  | ALDERTON PRIMARY | HT |  |  |  |  | 3.5874 | 3.5105 | 3.4221 | 14.5563 | 14.4289 | 14.2879 | 14.1426 | 13.9742 | 13.7984 | 13.3153 | 12.9174 | 12.5616 | 3.1979 | 3.1147 | 3.0179 | 13.2405 | 13.1005 | 12.9437 | 12.7826 | 12.5995 | 12.4068 | 11.8711 | 11.4237 | 11.0216 | 3.4274 | 3.3432 | 3.2453 | 13.9179 | 13.7768 | 13.6211 | 13.4589 | 13.2747 | 13.0821 | 12.5474 | 12.0979 | 11.6947
|  | ALDERTON PRIMARY | HE |  |  |  |  | 3.6358 | 3.5853 | 3.5316 | 14.7121 | 14.6237 | 14.5447 | 14.4679 | 14.3879 | 14.3111 | 14.2226 | 14.0289 | 13.8574 | 3.2526 | 3.1979 | 3.1411 | 13.4174 | 13.3247 | 13.2426 | 13.1626 | 13.0805 | 13.0005 | 12.8889 | 12.6584 | 12.4605 | 3.4821 | 3.4284 | 3.3705 | 14.0968 | 14.0042 | 13.9221 | 13.8421 | 13.76 | 13.6789 | 13.5674 | 13.3368 | 13.1389
|  | ALDERTON PRIMARY | FB |  |  |  |  | 3.6768 | 3.64 | 3.6116 | 14.8321 | 14.7995 | 14.7689 | 14.7374 | 14.7079 | 14.6774 | 14.5342 | 14.3658 | 14.2121 | 3.2979 | 3.2558 | 3.2242 | 13.5416 | 13.5058 | 13.4721 | 13.4363 | 13.4037 | 13.37 | 13.2079 | 13.0089 | 12.8342 | 3.5274 | 3.4853 | 3.4537 | 14.2211 | 14.1853 | 14.1516 | 14.1158 | 14.0832 | 14.0495 | 13.8874 | 13.6874 | 13.5116
FLEET-BRAMLEY GSP | ALTON BSP | ALRESFORD PRIMARY | MINIMUM HEADROOM | SU 59684 32511 | NO | YES | 5.0179 | 10.5432 | 27.3116 | 26.9642 | 26.3189 | 25.5137 | 24.6526 | 23.8874 | 23.0821 | 22.2611 | 20.2495 | 13.9221 | -0.95684 | 9.6442 | 26.2253 | 25.7705 | 25.0547 | 24.1579 | 23.2 | 22.3547 | 21.4611 | 20.5474 | 18.2989 | 10.7674 | -6.7389 | 7.4895 | 24.2789 | 24.0421 | 23.6905 | 23.2653 | 22.8032 | 22.3695 | 21.5821 | 20.6705 | 18.4274 | 10.9179 | -6.5368
|  | ALRESFORD PRIMARY | EE |  |  |  |  | 10.5432 | 27.3116 | 26.9642 | 26.4842 | 25.9221 | 25.4011 | 25.0063 | 24.6063 | 22.36 | 21.3579 | 13.9221 | -0.95684 | 9.6442 | 26.2253 | 25.7705 | 25.2453 | 24.6379 | 24.0789 | 23.6632 | 23.2421 | 20.6453 | 19.4979 | 10.7674 | -6.7389 | 7.4895 | 24.2789 | 24.0421 | 23.7474 | 23.3726 | 23.0147 | 22.7074 | 22.3937 | 20.7684 | 19.6221 | 10.9179 | -6.5368
|  | ALRESFORD PRIMARY | HT |  |  |  |  | 10.5558 | 27.3737 | 26.9737 | 26.3189 | 25.5137 | 24.6526 | 23.8874 | 23.0821 | 22.2611 | 20.2495 | 18.9011 | 5.2084 | 9.7095 | 26.3179 | 25.7863 | 25.0547 | 24.1579 | 23.2 | 22.3547 | 21.4611 | 20.5474 | 18.2989 | 16.7842 | 0.72 | 7.5095 | 24.3095 | 24.0421 | 23.6905 | 23.2653 | 22.8032 | 22.3695 | 21.5821 | 20.6705 | 18.4274 | 16.9168 | 0.89895
|  | ALRESFORD PRIMARY | HE |  |  |  |  | 10.5989 | 27.4379 | 27.2284 | 26.8589 | 26.3547 | 25.8863 | 25.5579 | 25.2274 | 23.0474 | 22.5411 | 15.4105 | 0.78421 | 9.8684 | 26.5368 | 26.1621 | 25.6989 | 25.1358 | 24.6326 | 24.2947 | 23.9547 | 21.4368 | 20.8358 | 12.4421 | -4.7821 | 7.5684 | 24.3842 | 24.1758 | 23.9 | 23.54 | 23.2084 | 22.9189 | 22.6274 | 21.5579 | 20.96 | 12.5916 | -4.5811
|  | ALRESFORD PRIMARY | FB |  |  |  |  | 10.7263 | 27.6442 | 27.5705 | 27.4895 | 27.3526 | 27.1926 | 27.0779 | 26.9705 | 26.8411 | 23.7105 | 17.3389 | 4.4695 | 10.1042 | 26.8811 | 26.6937 | 26.4884 | 26.2684 | 26.0558 | 25.9147 | 25.7821 | 25.64 | 21.9989 | 14.5189 | -0.62526 | 7.7105 | 24.6084 | 24.52 | 24.4221 | 24.3158 | 24.2105 | 24.1211 | 24.0389 | 23.9505 | 22.1221 | 14.6653 | -0.43368
FLEET-BRAMLEY GSP | ALTON BSP | ALTON LOCAL PRIMARY | MINIMUM HEADROOM | SU 72434 39606 | NO | YES | 0.42105 | 53.5847 | 53.2879 | 52.9426 | 52.4668 | 51.6163 | 50.15 | 48.7047 | 47.1363 | 45.4595 | 39.5426 | 27.7732 | 19.8447 | 52.1121 | 50.4816 | 48.8679 | 47.5174 | 45.9163 | 44.2089 | 42.5268 | 40.7247 | 38.8363 | 32.1342 | 18.4184 | 9.21 | 49.6468 | 48.0689 | 46.5058 | 45.19 | 43.63 | 41.9647 | 40.3247 | 38.5689 | 36.7311 | 30.2584 | 17.0511 | 8.1774
|  | ALTON LOCAL PRIMARY | EE |  |  |  |  | 53.5847 | 53.2879 | 52.9468 | 52.4932 | 51.8868 | 51.2942 | 50.7405 | 50.1784 | 49.5353 | 40.8226 | 34.5647 | 26.7247 | 52.1121 | 50.4816 | 48.9763 | 48.2026 | 47.3268 | 46.5247 | 45.6837 | 44.8132 | 43.89 | 33.4332 | 26.1195 | 16.93 | 49.6468 | 48.0689 | 46.61 | 45.8489 | 44.9826 | 44.1889 | 43.3605 | 42.5016 | 41.5921 | 31.5521 | 24.5142 | 15.6774
|  | ALTON LOCAL PRIMARY | HT |  |  |  |  | 53.5984 | 53.3142 | 52.9426 | 52.4668 | 51.6163 | 50.15 | 48.7047 | 47.1363 | 45.4595 | 39.5426 | 27.7732 | 19.8447 | 52.2416 | 50.6637 | 48.8679 | 47.5174 | 45.9163 | 44.2089 | 42.5268 | 40.7247 | 38.8363 | 32.1342 | 18.4184 | 9.21 | 49.7721 | 48.2447 | 46.5058 | 45.19 | 43.63 | 41.9647 | 40.3247 | 38.5689 | 36.7311 | 30.2584 | 17.0511 | 8.1774
|  | ALTON LOCAL PRIMARY | HE |  |  |  |  | 53.6511 | 53.3689 | 53.0426 | 52.6005 | 51.9974 | 51.4321 | 50.8784 | 50.3174 | 49.77 | 43.1247 | 37.4995 | 30.1879 | 52.55 | 51.0879 | 49.73 | 49.0774 | 48.2795 | 47.5837 | 46.9058 | 46.1974 | 45.4363 | 36.0226 | 29.4111 | 20.8068 | 50.0711 | 48.6542 | 47.3374 | 46.6932 | 45.9037 | 45.2132 | 44.5395 | 43.8363 | 43.0837 | 34.0437 | 27.69 | 19.4226
|  | ALTON LOCAL PRIMARY | FB |  |  |  |  | 53.8742 | 53.7384 | 53.6153 | 53.4784 | 53.3258 | 53.1711 | 53.0226 | 52.8847 | 52.7353 | 52.19 | 47.2458 | 40.7111 | 53.0258 | 52.3963 | 51.8395 | 51.5458 | 51.2426 | 50.9479 | 50.6647 | 50.3942 | 50.0732 | 47.2521 | 40.5058 | 32.8405 | 50.6321 | 49.9268 | 49.3868 | 49.0995 | 48.8016 | 48.5132 | 48.2342 | 47.97 | 47.6553 | 44.9237 | 38.4311 | 31.0626
MELKSHAM GSP | ANDOVER BSP | ANDOVER PRIMARY | MINIMUM HEADROOM | SU 35240 46643 | NO | YES | 0 | 32.5674 | 32.4253 | 32.0168 | 31.1105 | 29.9211 | 28.7242 | 27.5979 | 26.5821 | 25.6663 | 24.9095 | 23.9621 | 23.0189 | 30.8558 | 30.3884 | 29.58 | 28.5295 | 27.1937 | 25.8779 | 24.6421 | 23.5516 | 22.5674 | 22.0737 | 21.0358 | 19.9789 | 30.7295 | 30.2937 | 29.5453 | 28.5726 | 27.2421 | 25.8863 | 24.6158 | 23.4947 | 22.4842 | 21.7358 | 20.7053 | 19.6768
|  | ANDOVER PRIMARY | EE |  |  |  |  | 32.5674 | 32.4253 | 32.0168 | 31.1105 | 29.9211 | 28.7242 | 27.5979 | 26.5821 | 25.6663 | 25.3389 | 24.6747 | 24.0295 | 30.8558 | 30.3884 | 29.58 | 28.5295 | 27.1937 | 25.8779 | 24.6421 | 23.5516 | 22.5674 | 22.4989 | 21.7568 | 21.0189 | 30.7295 | 30.2937 | 29.5453 | 28.5726 | 27.2421 | 25.8863 | 24.6158 | 23.4947 | 22.4842 | 22.1579 | 21.4253 | 20.7105
|  | ANDOVER PRIMARY | HT |  |  |  |  | 32.5779 | 32.4432 | 32.0653 | 31.1558 | 31.5411 | 30.3032 | 29.1389 | 28.0979 | 27.1537 | 24.9095 | 23.9621 | 23.0189 | 30.9032 | 30.4568 | 29.6421 | 28.5874 | 29.2263 | 27.8653 | 26.5958 | 25.48 | 24.4684 | 22.0737 | 21.0358 | 19.9789 | 30.7737 | 30.3568 | 29.6011 | 28.6232 | 29.0811 | 27.6811 | 26.3768 | 25.2295 | 24.1916 | 21.7358 | 20.7053 | 19.6768
|  | ANDOVER PRIMARY | HE |  |  |  |  | 32.6095 | 32.4779 | 32.2379 | 31.3832 | 30.2284 | 29.0684 | 27.9916 | 27.0253 | 26.1579 | 26.1979 | 25.7737 | 25.3316 | 31.0168 | 30.6084 | 29.8526 | 28.8453 | 27.5326 | 26.2558 | 25.0716 | 24.0305 | 23.1011 | 23.4074 | 22.9474 | 22.4663 | 30.88 | 30.4979 | 29.7979 | 28.8653 | 27.5916 | 26.2768 | 25.0589 | 23.9884 | 23.0337 | 23.0874 | 22.6126 | 22.1168
|  | ANDOVER PRIMARY | FB |  |  |  |  | 32.6958 | 32.6284 | 32.5579 | 32.4758 | 32.1232 | 31.6368 | 31.1484 | 30.6863 | 30.2284 | 28.9874 | 30.1032 | 29.6789 | 31.1779 | 30.94 | 30.5905 | 30.1632 | 29.68 | 29.1105 | 28.5379 | 28.0074 | 27.5 | 26.1326 | 27.6137 | 27.1505 | 31.0337 | 30.8116 | 30.4884 | 30.0947 | 29.6484 | 29.1232 | 28.5968 | 28.0705 | 27.5474 | 26.14 | 27.4137 | 26.9368
MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST PRIMARY | MINIMUM HEADROOM | SU 37953 46433 | NO | YES | 0.42105 | 34.4037 | 34.1679 | 33.9047 | 33.3742 | 32.2732 | 31.4037 | 30.6184 | 29.5847 | 28.6058 | 26.7426 | 24.8847 | 22.9321 | 31.0442 | 30.2158 | 29.0095 | 27.9316 | 26.7516 | 25.8179 | 24.9789 | 23.8632 | 22.8053 | 20.9821 | 18.9842 | 16.8495 | 32.0926 | 31.2811 | 30.0168 | 28.8895 | 27.6621 | 26.6947 | 25.8242 | 24.6621 | 23.56 | 21.3442 | 19.2811 | 17.0453
|  | ANDOVER EAST PRIMARY | EE |  |  |  |  | 34.4037 | 34.1679 | 33.9047 | 33.4553 | 32.2732 | 31.4037 | 30.6184 | 29.5847 | 28.6058 | 26.7426 | 25.1047 | 23.6395 | 31.0442 | 30.3516 | 29.1242 | 28.0305 | 26.7516 | 25.8179 | 24.9789 | 23.8632 | 22.8053 | 20.9821 | 19.1884 | 17.5768 | 32.0926 | 31.4274 | 30.1389 | 28.9968 | 27.6621 | 26.6947 | 25.8242 | 24.6621 | 23.56 | 21.3442 | 19.4589 | 17.7653
|  | ANDOVER EAST PRIMARY | HT |  |  |  |  | 34.4542 | 34.2447 | 33.9868 | 33.3742 | 33.8932 | 33.3437 | 32.5584 | 31.57 | 30.6205 | 26.9437 | 24.8847 | 22.9321 | 31.1537 | 30.2158 | 29.0095 | 27.9316 | 28.7568 | 28.1811 | 27.3411 | 26.2726 | 25.2463 | 21.2326 | 18.9842 | 16.8495 | 32.1979 | 31.2811 | 30.0168 | 28.8895 | 29.4747 | 28.8853 | 28.0158 | 26.9032 | 25.8358 | 21.6326 | 19.2811 | 17.0453
|  | ANDOVER EAST PRIMARY | HE |  |  |  |  | 34.5595 | 34.4047 | 34.2332 | 33.9921 | 33.1226 | 32.3574 | 31.7132 | 30.8363 | 29.9795 | 28.8763 | 27.7563 | 26.7163 | 31.3863 | 30.8537 | 29.7863 | 28.8284 | 27.66 | 26.8379 | 26.1505 | 25.2032 | 24.2768 | 23.2389 | 21.9905 | 20.8284 | 32.4242 | 31.9253 | 30.8326 | 29.8316 | 28.6147 | 27.7621 | 27.0516 | 26.0653 | 25.1011 | 23.6937 | 22.3768 | 21.1495
|  | ANDOVER EAST PRIMARY | FB |  |  |  |  | 34.6711 | 34.5942 | 34.5237 | 34.4458 | 34.3584 | 34.2711 | 34.1847 | 34.1058 | 33.8142 | 31.7511 | 32.3079 | 31.4795 | 31.6937 | 31.3737 | 31.0421 | 30.6642 | 30.2432 | 29.8316 | 29.3358 | 28.8747 | 28.3905 | 26.1126 | 26.9621 | 26.0463 | 32.7147 | 32.4158 | 32.1074 | 31.7495 | 31.3095 | 30.8779 | 30.3589 | 29.8747 | 29.3674 | 26.9726 | 27.5758 | 26.6116
MELKSHAM GSP | ANDOVER BSP | ANDOVER TOWN PRIMARY | MINIMUM HEADROOM | SU 36207 45078 | NO | YES | 0 | 16.0887 | 15.8845 | 15.6687 | 15.4171 | 15.1108 | 14.8255 | 14.5076 | 14.1855 | 13.8739 | 12.8234 | 11.8024 | 10.7466 | 14.9668 | 14.8311 | 14.6037 | 14.3416 | 14.0268 | 13.7321 | 13.4068 | 13.0742 | 12.7521 | 11.6353 | 10.4784 | 9.2721 | 13.6042 | 13.4505 | 13.2853 | 13.0811 | 12.8147 | 12.5653 | 12.2863 | 12.0147 | 11.7495 | 10.9853 | 10.3442 | 9.2411
|  | ANDOVER TOWN PRIMARY | EE |  |  |  |  | 16.0887 | 15.8845 | 15.6687 | 15.4171 | 15.1108 | 14.8255 | 14.5403 | 14.2487 | 13.9624 | 13.2761 | 12.5739 | 11.8445 | 14.9668 | 14.8311 | 14.6037 | 14.3416 | 14.0268 | 13.7321 | 13.4374 | 13.1342 | 12.8374 | 12.0837 | 11.2732 | 10.4226 | 13.6042 | 13.4505 | 13.2853 | 13.0811 | 12.8147 | 12.5684 | 12.3316 | 12.0895 | 11.8495 | 11.4505 | 11.0505 | 10.3884
|  | ANDOVER TOWN PRIMARY | HT |  |  |  |  | 16.1034 | 15.9445 | 15.7213 | 15.4624 | 15.1739 | 14.8382 | 14.5076 | 14.1855 | 13.8739 | 12.8234 | 11.8024 | 10.7466 | 14.9763 | 14.8647 | 14.6626 | 14.3942 | 14.0963 | 13.7489 | 13.4068 | 13.0742 | 12.7521 | 11.6353 | 10.4784 | 9.2721 | 13.6179 | 13.4853 | 13.3084 | 13.0937 | 12.8453 | 12.5653 | 12.2863 | 12.0147 | 11.7495 | 10.9853 | 10.3442 | 9.2411
|  | ANDOVER TOWN PRIMARY | HE |  |  |  |  | 16.1445 | 16.0287 | 15.9003 | 15.6876 | 15.4024 | 15.1497 | 14.9034 | 14.6497 | 14.4024 | 14.0634 | 13.5803 | 13.0361 | 15.0068 | 14.8984 | 14.7784 | 14.6121 | 14.3468 | 14.0879 | 13.8363 | 13.5763 | 13.3237 | 12.9437 | 12.4089 | 11.7689 | 13.6558 | 13.5421 | 13.4158 | 13.2305 | 12.9747 | 12.7484 | 12.5284 | 12.3011 | 12.08 | 11.9295 | 11.6842 | 11.42
|  | ANDOVER TOWN PRIMARY | FB |  |  |  |  | 16.2287 | 16.1645 | 16.1087 | 16.0466 | 15.9487 | 15.8445 | 15.7424 | 15.6445 | 15.5413 | 15.1318 | 14.5782 | 14.1087 | 15.0847 | 15.0289 | 14.9805 | 14.9247 | 14.8637 | 14.7911 | 14.6837 | 14.5805 | 14.4721 | 14.0384 | 13.4321 | 12.9058 | 13.7389 | 13.6768 | 13.6232 | 13.5621 | 13.4863 | 13.4074 | 13.3305 | 13.2568 | 13.1789 | 12.88 | 12.5653 | 12.3116
BRAMLEY (BASI) GSP | READING BSP | ARBORFIELD PRIMARY | MINIMUM HEADROOM | SU 75949 65766 | NO | YES | 0.21053 | 22.7245 | 22.6298 | 22.5256 | 22.3845 | 21.1835 | 19.894 | 18.3298 | 16.715 | 15.0645 | 1.2235 | -7.5218 | -12.0713 | 21.8561 | 21.5835 | 21.0182 | 19.774 | 18.2108 | 16.7203 | 14.9045 | 13.0256 | 11.1066 | -5.1987 | -15.4734 | -20.7902 | 22.3056 | 22.1877 | 22.0245 | 20.9961 | 19.4877 | 18.0477 | 16.2961 | 14.4835 | 12.6329 | -3.3092 | -13.5565 | -18.8597
|  | ARBORFIELD PRIMARY | EE |  |  |  |  | 22.7245 | 22.6298 | 22.5256 | 22.3845 | 21.3371 | 20.175 | 18.6919 | 17.174 | 15.6413 | 6.895 | -0.81023 | -5.4323 | 21.8561 | 21.5835 | 21.0182 | 19.8635 | 18.3992 | 17.0582 | 15.3329 | 13.5677 | 11.7866 | 1.4603 | -7.6344 | -13.0692 | 22.3056 | 22.1877 | 22.0245 | 21.0782 | 19.6624 | 18.3656 | 16.7003 | 14.9971 | 13.2792 | 3.3182 | -5.7565 | -11.1797
|  | ARBORFIELD PRIMARY | HT |  |  |  |  | 22.7329 | 22.6435 | 22.5298 | 22.3845 | 21.1835 | 19.894 | 18.3298 | 16.715 | 15.0645 | 1.2235 | -7.5218 | -12.0713 | 21.8971 | 21.6266 | 21.0192 | 19.774 | 18.2108 | 16.7203 | 14.9045 | 13.0256 | 11.1066 | -5.1987 | -15.4734 | -20.7902 | 22.3203 | 22.2056 | 22.0287 | 20.9961 | 19.4877 | 18.0477 | 16.2961 | 14.4835 | 12.6329 | -3.3092 | -13.5565 | -18.8597
|  | ARBORFIELD PRIMARY | HE |  |  |  |  | 22.7519 | 22.6677 | 22.5719 | 22.4392 | 21.6098 | 20.4782 | 19.0456 | 17.5792 | 16.0992 | 7.7045 | 0.21187 | -4.2239 | 21.9919 | 21.775 | 21.255 | 20.1413 | 18.7056 | 17.3961 | 15.7308 | 14.0256 | 12.3035 | 2.3624 | -6.5018 | -11.7365 | 22.3477 | 22.2466 | 22.0961 | 21.3529 | 19.9666 | 18.7035 | 17.0961 | 15.4519 | 13.7919 | 4.2361 | -4.6018 | -9.8208
|  | ARBORFIELD PRIMARY | FB |  |  |  |  | 22.8192 | 22.7782 | 22.7424 | 22.7024 | 22.6561 | 22.6108 | 22.1929 | 21.4403 | 20.6182 | 16.775 | 12.4066 | 8.8119 | 22.1403 | 21.9971 | 21.755 | 21.2877 | 20.715 | 20.1413 | 19.3392 | 18.455 | 17.4908 | 12.9708 | 7.8161 | 3.5719 | 22.4256 | 22.3719 | 22.3087 | 22.2129 | 21.9129 | 21.3603 | 20.5877 | 19.7371 | 18.8087 | 14.4613 | 9.5066 | 5.4277
LOVEDEAN GSP | CHICHESTER BSP | ARGYLE ROAD PRIMARY | MINIMUM HEADROOM | SZ 93193 99152 | NO | YES | 0 | 31.5079 | 31.3521 | 31.17 | 30.9184 | 30.6163 | 30.2805 | 29.9447 | 29.6132 | 29.2837 | 28.4847 | 27.7279 | 25.1858 | 27.9537 | 27.7905 | 27.6042 | 27.3421 | 26.9253 | 26.1811 | 25.3958 | 24.5621 | 23.7274 | 21.2821 | 18.1853 | 15.2705 | 27.2863 | 27.0632 | 26.8263 | 26.5168 | 26.1189 | 25.6389 | 25.1442 | 24.6358 | 24.1274 | 22.7484 | 19.8463 | 16.94
|  | ARGYLE ROAD PRIMARY | EE |  |  |  |  | 31.5079 | 31.3521 | 31.1784 | 30.9437 | 30.6226 | 30.3111 | 30.0216 | 29.7216 | 29.4247 | 29.17 | 28.9479 | 28.7711 | 27.9537 | 27.7905 | 27.6084 | 27.3663 | 27.0379 | 26.5842 | 26.1137 | 25.64 | 25.1716 | 24.0084 | 21.7389 | 19.6421 | 27.2863 | 27.0632 | 26.8263 | 26.5347 | 26.1621 | 25.8011 | 25.4474 | 25.0863 | 24.7284 | 24.1537 | 23.2095 | 21.3011
|  | ARGYLE ROAD PRIMARY | HT |  |  |  |  | 31.5111 | 31.3647 | 31.17 | 30.9184 | 30.6163 | 30.2805 | 29.9447 | 29.6132 | 29.2837 | 28.4847 | 27.7279 | 25.1858 | 27.96 | 27.8063 | 27.6042 | 27.3421 | 26.9253 | 26.1811 | 25.3958 | 24.5621 | 23.7274 | 21.2821 | 18.1853 | 15.2705 | 27.3105 | 27.1053 | 26.8537 | 26.5168 | 26.1189 | 25.6389 | 25.1442 | 24.6358 | 24.1274 | 22.7484 | 19.8463 | 16.94
|  | ARGYLE ROAD PRIMARY | HE |  |  |  |  | 31.5311 | 31.3753 | 31.2005 | 30.9584 | 30.6247 | 30.3184 | 30.0163 | 29.71 | 29.4089 | 29.4226 | 29.3595 | 29.3174 | 27.9863 | 27.8253 | 27.6463 | 27.3989 | 27.0611 | 26.7505 | 26.4442 | 26.1337 | 25.8284 | 25.3916 | 23.5316 | 21.7905 | 27.3779 | 27.1842 | 26.9716 | 26.6926 | 26.3232 | 25.9821 | 25.6463 | 25.3074 | 24.9758 | 24.8053 | 24.1074 | 23.4453
|  | ARGYLE ROAD PRIMARY | FB |  |  |  |  | 31.6416 | 31.5584 | 31.4826 | 31.3984 | 31.3047 | 31.21 | 31.1184 | 31.0332 | 30.9416 | 30.6058 | 30.4174 | 30.2953 | 28.1011 | 28.0116 | 27.9326 | 27.8442 | 27.7463 | 27.6484 | 27.5526 | 27.4632 | 27.3684 | 26.7895 | 25.4 | 24.1137 | 27.5211 | 27.3947 | 27.2874 | 27.1737 | 27.0495 | 26.9232 | 26.8 | 26.6853 | 26.5632 | 26.0642 | 25.4516 | 24.9189
COWLEY GSP | HEADINGTON BSP | ARNCOTT PRIMARY | MINIMUM HEADROOM | SP 60730 18095 | NO | YES | 0.47368 | 17.8221 | 16.8695 | 14.6137 | 13.3305 | 9.1116 | 7.5905 | 4.2968 | 1.3116 | 0.043158 | -4.7684 | -8.9421 | -9.1358 | 15.1705 | 14.0579 | 11.4137 | 9.9179 | 4.9674 | 3.1958 | -0.66316 | -4.1589 | -5.6316 | -11.2526 | -16.2 | -16.4179 | 15.5021 | 14.3926 | 11.7568 | 10.2653 | 5.3295 | 3.5632 | -0.28421 | -3.7695 | -5.2389 | -10.8432 | -15.7758 | -15.9916
|  | ARNCOTT PRIMARY | EE |  |  |  |  | 18.2663 | 17.3842 | 15.3316 | 14.16 | 13.0474 | 12.16 | 9.7474 | 7.0147 | 5.7432 | -4.4526 | -8.9421 | -9.1358 | 15.6947 | 14.6653 | 12.2589 | 10.8937 | 9.6042 | 8.5768 | 5.7526 | 2.5516 | 1.0716 | -10.9242 | -16.2 | -16.4179 | 16.0253 | 14.9989 | 12.6 | 11.2389 | 9.9526 | 8.9284 | 6.1126 | 2.92 | 1.4453 | -10.5158 | -15.7758 | -15.9916
|  | ARNCOTT PRIMARY | HT |  |  |  |  | 17.8221 | 16.8695 | 14.6137 | 13.3305 | 9.1116 | 7.5905 | 4.2968 | 1.3116 | 0.043158 | -4.7684 | -7.1811 | -7.5874 | 15.1705 | 14.0579 | 11.4137 | 9.9179 | 4.9674 | 3.1958 | -0.66316 | -4.1589 | -5.6316 | -11.2526 | -14.0653 | -14.5189 | 15.5021 | 14.3926 | 11.7568 | 10.2653 | 5.3295 | 3.5632 | -0.28421 | -3.7695 | -5.2389 | -10.8432 | -13.6484 | -14.1011
|  | ARNCOTT PRIMARY | HE |  |  |  |  | 18.3484 | 17.5 | 15.4726 | 14.3232 | 13.2274 | 12.3579 | 9.9011 | 7.3032 | 6.2147 | -3.4705 | -8.2863 | -8.3726 | 15.7884 | 14.7968 | 12.42 | 11.08 | 9.8084 | 8.8032 | 5.9263 | 2.8832 | 1.6189 | -9.7905 | -15.4611 | -15.5589 | 16.1179 | 15.1305 | 12.76 | 11.4232 | 10.1558 | 9.1526 | 6.2853 | 3.2516 | 1.9905 | -9.3853 | -15.0379 | -15.1358
|  | ARNCOTT PRIMARY | FB |  |  |  |  | 20.4579 | 18.5916 | 18.12 | 17.6547 | 17.2105 | 14.5947 | 13.2684 | 12.3568 | 11.7495 | 6.4526 | 4.6063 | 4.4726 | 18.2674 | 16.0726 | 15.5211 | 14.9779 | 14.4589 | 11.3842 | 9.8263 | 8.7579 | 8.0463 | 1.8253 | -0.33895 | -0.49053 | 18.5895 | 16.4021 | 15.8526 | 15.3105 | 14.7937 | 11.7274 | 10.1747 | 9.1095 | 8.3989 | 2.1979 | 0.038947 | -0.11158
FLEET-BRAMLEY GSP | BRACKNELL BSP | ASCOT PRIMARY | MINIMUM HEADROOM | SU 91615 68855 | NO | YES | 0 | 35.8674 | 35.74 | 35.5884 | 34.5821 | 33.9547 | 33.4853 | 33.0158 | 32.6716 | 32.0863 | 30.2474 | 29.0211 | 27.9158 | 31.7516 | 31.2579 | 30.7779 | 29.5063 | 28.8168 | 28.3105 | 27.8042 | 27.4526 | 26.8758 | 24.8295 | 23.46 | 22.2253 | 34.7621 | 34.2642 | 33.7811 | 32.4968 | 31.8011 | 31.2926 | 30.7821 | 30.3779 | 29.7337 | 27.6705 | 26.2905 | 25.0442
|  | ASCOT PRIMARY | EE |  |  |  |  | 35.8674 | 35.74 | 35.5884 | 34.8316 | 33.9547 | 33.4853 | 33.0158 | 32.6811 | 32.3474 | 32.1726 | 31.32 | 30.5926 | 31.7516 | 31.2579 | 30.7895 | 29.7958 | 28.8168 | 28.3105 | 27.8042 | 27.4526 | 27.1042 | 26.9926 | 26.0232 | 25.1937 | 34.7621 | 34.2642 | 33.7926 | 32.7884 | 31.8011 | 31.2926 | 30.7821 | 30.4305 | 30.0811 | 29.8537 | 28.8737 | 28.0368
|  | ASCOT PRIMARY | HT |  |  |  |  | 35.8747 | 35.7537 | 35.5884 | 34.5821 | 34.3484 | 33.6905 | 33.2326 | 32.6716 | 32.0863 | 30.2474 | 29.0211 | 27.9158 | 31.8074 | 31.3326 | 30.7779 | 29.5063 | 29.3389 | 28.6158 | 28.1263 | 27.5147 | 26.8758 | 24.8295 | 23.46 | 22.2253 | 34.8189 | 34.34 | 33.7811 | 32.4968 | 32.2137 | 31.4853 | 30.9926 | 30.3779 | 29.7337 | 27.6705 | 26.2905 | 25.0442
|  | ASCOT PRIMARY | HE |  |  |  |  | 35.8947 | 35.7716 | 35.6295 | 35.1979 | 34.3705 | 33.9368 | 33.5084 | 33.0768 | 32.78 | 32.9853 | 32.3768 | 31.8537 | 31.9526 | 31.5537 | 31.1768 | 30.2705 | 29.2968 | 28.8305 | 28.3716 | 27.9095 | 27.6021 | 27.9032 | 27.2 | 26.5947 | 34.9653 | 34.5642 | 34.1842 | 33.2695 | 32.2874 | 31.8189 | 31.3568 | 30.8916 | 30.5842 | 30.7737 | 30.0632 | 29.4505
|  | ASCOT PRIMARY | FB |  |  |  |  | 35.9884 | 35.9284 | 35.8737 | 35.8126 | 35.7411 | 35.6137 | 35.4474 | 35.3347 | 35.2242 | 34.6926 | 34.7926 | 34.3074 | 32.2253 | 31.98 | 31.7937 | 31.4095 | 30.96 | 30.7579 | 30.5505 | 30.4179 | 30.2884 | 29.6621 | 29.8642 | 29.3126 | 35.0832 | 34.9926 | 34.8053 | 34.4168 | 33.9632 | 33.7589 | 33.5505 | 33.4168 | 33.2863 | 32.6558 | 32.7474 | 32.1895
LOVEDEAN GSP | CHICHESTER BSP | ASHLING ROAD PRIMARY | MINIMUM HEADROOM | SU 84085 06737 | NO | YES | 0.0063158 | 18.9463 | 18.3663 | 17.6274 | 34.7242 | 33.4874 | 32.0737 | 30.6821 | 29.4095 | 28.1853 | 24.1042 | 20.8789 | 17.9768 | 22.1221 | 21.1032 | 19.7442 | 33.5074 | 31.2211 | 28.5674 | 25.9611 | 23.6453 | 21.3884 | 14.4926 | 10.9326 | 7.7242 | 24.2326 | 23.2505 | 21.9442 | 36.9768 | 34.78 | 32.2305 | 29.7105 | 27.3411 | 25.04 | 17.9737 | 14.3295 | 11.0442
|  | ASHLING ROAD PRIMARY | EE |  |  |  |  | 18.9463 | 18.3663 | 17.7705 | 35.1263 | 34.1758 | 33.1463 | 32.1432 | 31.3032 | 29.7147 | 27.7937 | 26.5968 | 25.4126 | 22.1221 | 21.1032 | 20.0947 | 34.4968 | 33.0221 | 31.3053 | 29.5789 | 28.2979 | 25.0547 | 20.6642 | 18.1221 | 15.8979 | 24.2326 | 23.2505 | 22.2768 | 37.9158 | 36.4874 | 34.8284 | 33.1632 | 31.9189 | 28.8084 | 24.3 | 21.6884 | 19.4032
|  | ASHLING ROAD PRIMARY | HT |  |  |  |  | 18.9926 | 18.3884 | 17.6274 | 34.7242 | 33.4874 | 32.0737 | 30.6821 | 29.4095 | 28.1853 | 24.1042 | 20.8789 | 17.9768 | 22.2253 | 21.1147 | 19.7442 | 33.5074 | 31.2211 | 28.5674 | 25.9611 | 23.6453 | 21.3884 | 14.4926 | 10.9326 | 7.7242 | 24.3305 | 23.2621 | 21.9442 | 36.9768 | 34.78 | 32.2305 | 29.7105 | 27.3411 | 25.04 | 17.9737 | 14.3295 | 11.0442
|  | ASHLING ROAD PRIMARY | HE |  |  |  |  | 19.1579 | 18.6579 | 18.1337 | 35.5516 | 34.6453 | 33.6832 | 32.7347 | 31.9505 | 30.4168 | 29.1463 | 28.3758 | 27.7084 | 22.5621 | 21.7168 | 20.8621 | 35.3926 | 34.0095 | 32.4063 | 30.8158 | 29.6695 | 26.5579 | 23.1589 | 21.2821 | 19.62 | 24.6537 | 23.8368 | 23.0105 | 38.7737 | 37.4305 | 35.8821 | 34.3463 | 33.2295 | 30.2516 | 26.8453 | 24.9116 | 23.1979
|  | ASHLING ROAD PRIMARY | FB |  |  |  |  | 19.5484 | 19.2558 | 19.0179 | 36.8505 | 36.5442 | 36.1789 | 35.8021 | 35.5179 | 35.22 | 34.0105 | 32.9337 | 32.2579 | 23.2242 | 22.6884 | 22.2705 | 37.4011 | 36.8547 | 36.1579 | 35.4232 | 34.9126 | 34.3832 | 32.1358 | 29.8337 | 28.3926 | 25.2926 | 24.7768 | 24.3737 | 40.7221 | 40.1958 | 39.5274 | 38.8221 | 38.3316 | 37.8221 | 35.6621 | 33.4642 | 32.0863
MELKSHAM GSP | NORRINGTON BSP | ASHTON PARK PRIMARY | MINIMUM HEADROOM | ST 87141 57741 | NO | YES | 0 | 23.1379 | 22.2326 | 21.3863 | 20.0895 | 18.06 | 16.0063 | 45.8968 | 43.34 | 42.4684 | 35.2989 | 32.6853 | 30.3526 | 22.6558 | 21.5116 | 20.4611 | 18.8442 | 16.2347 | 13.6137 | 39.2326 | 35.8989 | 34.9495 | 25.4663 | 22.1526 | 19.1863 | 22.6611 | 21.5189 | 20.4705 | 18.8568 | 16.2526 | 13.6389 | 41.0653 | 37.74 | 37.0853 | 27.6253 | 24.3189 | 21.36
|  | ASHTON PARK PRIMARY | EE |  |  |  |  | 23.1379 | 22.2326 | 21.3863 | 20.1674 | 18.06 | 16.3263 | 46.7126 | 44.8084 | 43.0084 | 39.5632 | 37.7358 | 36.1684 | 22.6558 | 21.5116 | 20.4611 | 18.9337 | 16.2347 | 14.0411 | 40.3126 | 37.8642 | 35.5589 | 30.9179 | 28.5084 | 26.4316 | 22.6611 | 21.5189 | 20.4705 | 18.9474 | 16.2526 | 14.0642 | 42.1421 | 39.7 | 37.4 | 33.0653 | 30.6621 | 28.5916
|  | ASHTON PARK PRIMARY | HT |  |  |  |  | 23.2421 | 22.3842 | 21.4747 | 20.0895 | 18.1611 | 16.0063 | 45.8968 | 43.34 | 42.4684 | 35.2989 | 32.6853 | 30.3526 | 22.7937 | 21.7084 | 20.5895 | 18.8442 | 16.3758 | 13.6137 | 39.2326 | 35.8989 | 34.9495 | 25.4663 | 22.1526 | 19.1863 | 22.7989 | 21.7147 | 20.5989 | 18.8568 | 16.3947 | 13.6389 | 41.0653 | 37.74 | 37.0853 | 27.6253 | 24.3189 | 21.36
|  | ASHTON PARK PRIMARY | HE |  |  |  |  | 23.5053 | 22.7347 | 22.0063 | 20.8821 | 18.8411 | 17.1968 | 47.6726 | 45.8547 | 44.1337 | 41.6042 | 40.3189 | 39.2126 | 23.1326 | 22.1663 | 21.2726 | 19.8716 | 17.26 | 15.1768 | 41.5758 | 39.2474 | 37.0505 | 33.5147 | 31.7611 | 30.2411 | 23.1368 | 22.1726 | 21.28 | 19.8821 | 17.2768 | 15.1989 | 43.4021 | 41.08 | 38.8874 | 35.6568 | 33.9074 | 32.3916
|  | ASHTON PARK PRIMARY | FB |  |  |  |  | 23.94 | 23.4916 | 23.1411 | 22.7147 | 21.9263 | 21.1232 | 52.5747 | 51.7747 | 50.9895 | 47.9663 | 46.7484 | 45.7284 | 23.6579 | 23.0832 | 22.6411 | 22.0989 | 21.0537 | 19.9895 | 47.6 | 46.5337 | 45.4926 | 41.4737 | 39.8874 | 38.5337 | 23.6611 | 23.0874 | 22.6463 | 22.1063 | 21.0632 | 20.0011 | 49.4147 | 48.3516 | 47.3137 | 43.3042 | 41.7221 | 40.3716
FLEET-BRAMLEY GSP | BRACKNELL BSP | BAGSHOT PRIMARY | MINIMUM HEADROOM | SU 91122 63523 | NO | YES | 0 | 28.5076 | 28.3045 | 28.075 | 27.7687 | 27.4003 | 26.9887 | 26.355 | 25.5361 | 24.7213 | 22.9676 | 21.7897 | 20.7718 | 27.5076 | 27.115 | 26.5424 | 25.9287 | 25.1676 | 24.2245 | 23.2624 | 22.2676 | 21.2771 | 19.2582 | 17.9697 | 16.8571 | 23.4897 | 23.2803 | 23.0445 | 22.7308 | 22.3539 | 21.9329 | 21.5129 | 21.095 | 20.6824 | 19.7708 | 19.0108 | 17.8887
|  | BAGSHOT PRIMARY | EE |  |  |  |  | 28.5076 | 28.3045 | 28.0761 | 27.7908 | 27.4245 | 27.0655 | 26.7287 | 26.3866 | 26.0518 | 25.6424 | 24.9466 | 24.3718 | 27.5076 | 27.115 | 26.5424 | 25.9824 | 25.4971 | 25.0066 | 24.5139 | 24.0234 | 23.5497 | 22.5876 | 21.6982 | 20.9613 | 23.4897 | 23.2803 | 23.0445 | 22.7539 | 22.3855 | 22.0234 | 21.6845 | 21.3392 | 21.0024 | 20.7139 | 20.4592 | 20.2571
|  | BAGSHOT PRIMARY | HT |  |  |  |  | 28.5192 | 28.3276 | 28.075 | 27.7687 | 27.4003 | 26.9887 | 26.355 | 25.5361 | 24.7213 | 22.9676 | 21.7897 | 20.7718 | 27.5171 | 27.1897 | 26.595 | 25.9287 | 25.1676 | 24.2245 | 23.2624 | 22.2676 | 21.2771 | 19.2582 | 17.9697 | 16.8571 | 23.5024 | 23.3045 | 23.0455 | 22.7308 | 22.3539 | 21.9329 | 21.5129 | 21.095 | 20.6824 | 19.7708 | 19.0108 | 17.8887
|  | BAGSHOT PRIMARY | HE |  |  |  |  | 28.5676 | 28.3824 | 28.1697 | 27.895 | 27.5382 | 27.1992 | 26.8697 | 26.5392 | 26.2108 | 26.1961 | 26.1139 | 26.0192 | 27.5603 | 27.3697 | 26.9771 | 26.4971 | 26.0634 | 25.6329 | 25.2118 | 24.795 | 24.3866 | 23.9855 | 23.4466 | 23.0066 | 23.5529 | 23.3634 | 23.1455 | 22.8655 | 22.5076 | 22.1676 | 21.8361 | 21.5045 | 21.1739 | 21.1518 | 21.0603 | 20.9939
|  | BAGSHOT PRIMARY | FB |  |  |  |  | 28.7055 | 28.6118 | 28.5287 | 28.4392 | 28.3445 | 28.2497 | 28.1571 | 28.0708 | 27.9782 | 27.6318 | 27.4234 | 27.2834 | 27.6961 | 27.6076 | 27.5245 | 27.3529 | 27.2097 | 27.0687 | 26.9129 | 26.7455 | 26.5771 | 25.8276 | 25.1845 | 24.655 | 23.6939 | 23.5961 | 23.5097 | 23.4182 | 23.3213 | 23.2255 | 23.1318 | 23.0434 | 22.9497 | 22.595 | 22.3792 | 22.2308
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BALL HILL PRIMARY | MINIMUM HEADROOM | SU 42417 63142 | NO | YES | 0 | 17.0695 | 17.0063 | 16.9358 | 16.8253 | 16.6242 | 16.4074 | 16.2305 | 16.0505 | 15.8653 | 15.4063 | 15.0747 | 14.7126 | 15.5811 | 15.46 | 15.34 | 15.1505 | 14.9347 | 14.7032 | 14.5158 | 14.3253 | 14.1305 | 13.6389 | 13.28 | 12.8832 | 16.2558 | 16.1337 | 16.0126 | 15.8221 | 15.6053 | 15.3726 | 15.1853 | 14.9937 | 14.7968 | 14.3032 | 13.9421 | 13.5421
|  | BALL HILL PRIMARY | EE |  |  |  |  | 17.0695 | 17.0063 | 16.9389 | 16.8484 | 16.7168 | 16.5726 | 16.4284 | 16.2842 | 16.1432 | 15.9063 | 15.7116 | 15.48 | 15.5811 | 15.46 | 15.34 | 15.2021 | 15.0421 | 14.8916 | 14.7421 | 14.5905 | 14.4432 | 14.18 | 13.9642 | 13.7032 | 16.2558 | 16.1337 | 16.0126 | 15.8747 | 15.7137 | 15.5632 | 15.4126 | 15.2611 | 15.1137 | 14.8474 | 14.6295 | 14.3663
|  | BALL HILL PRIMARY | HT |  |  |  |  | 17.0726 | 17.0137 | 16.9358 | 16.8253 | 16.6242 | 16.4074 | 16.2305 | 16.0505 | 15.8653 | 15.4063 | 15.0747 | 14.7126 | 15.6032 | 15.4947 | 15.3505 | 15.1505 | 14.9347 | 14.7032 | 14.5158 | 14.3253 | 14.1305 | 13.6389 | 13.28 | 12.8832 | 16.2779 | 16.1695 | 16.0232 | 15.8221 | 15.6053 | 15.3726 | 15.1853 | 14.9937 | 14.7968 | 14.3032 | 13.9421 | 13.5421
|  | BALL HILL PRIMARY | HE |  |  |  |  | 17.0884 | 17.0337 | 16.9705 | 16.8863 | 16.7695 | 16.6611 | 16.5568 | 16.4537 | 16.3526 | 16.3147 | 16.2211 | 16.1316 | 15.6642 | 15.58 | 15.4884 | 15.3768 | 15.2337 | 15.1011 | 14.9737 | 14.8484 | 14.7242 | 14.6337 | 14.5284 | 14.4263 | 16.3389 | 16.2547 | 16.1632 | 16.0505 | 15.9074 | 15.7747 | 15.6474 | 15.5221 | 15.3968 | 15.3053 | 15.1989 | 15.0958
|  | BALL HILL PRIMARY | FB |  |  |  |  | 17.1337 | 17.1063 | 17.0821 | 17.0547 | 17.0253 | 16.9968 | 16.9663 | 16.94 | 16.9105 | 16.7705 | 16.6189 | 16.4947 | 15.7379 | 15.6737 | 15.6253 | 15.5726 | 15.5179 | 15.4642 | 15.4105 | 15.3611 | 15.3084 | 15.0916 | 14.9253 | 14.7853 | 16.4137 | 16.3495 | 16.3011 | 16.2474 | 16.1926 | 16.1389 | 16.0842 | 16.0337 | 15.9811 | 15.7632 | 15.5947 | 15.4547
MELKSHAM GSP | ANDOVER BSP | BARTON STACEY PRIMARY | MINIMUM HEADROOM | SU 42075 42720 | NO | YES | 12.8421 | 16.4497 | 16.3971 | 16.3392 | 16.2582 | 16.1571 | 16.0476 | 15.9308 | 14.1287 | 14.0076 | 12.2466 | 10.3929 | 9.3518 | 13.4458 | 13.3426 | 13.2405 | 13.1205 | 12.9626 | 12.7774 | 12.5889 | 10.4384 | 10.31 | 8.2511 | 6.0711 | 4.8668 | 14.7326 | 14.6768 | 14.6168 | 14.5326 | 14.3926 | 14.2084 | 14.0189 | 11.8589 | 11.7305 | 9.6642 | 7.4842 | 6.2821
|  | BARTON STACEY PRIMARY | EE |  |  |  |  | 16.4497 | 16.3971 | 16.3392 | 16.2624 | 16.1592 | 16.0613 | 15.9739 | 14.1287 | 14.0076 | 12.4655 | 11.6897 | 10.7013 | 13.4458 | 13.3426 | 13.2405 | 13.1205 | 12.9816 | 12.85 | 12.7237 | 10.4384 | 10.31 | 8.4732 | 7.5532 | 6.3921 | 14.7326 | 14.6768 | 14.6168 | 14.5368 | 14.4126 | 14.2811 | 14.1537 | 11.8589 | 11.7305 | 9.8863 | 8.9621 | 7.8042
|  | BARTON STACEY PRIMARY | HT |  |  |  |  | 16.4561 | 16.4045 | 16.3392 | 16.2582 | 16.1571 | 16.0476 | 15.9308 | 15.755 | 15.5792 | 12.2466 | 10.3929 | 9.3518 | 13.4679 | 13.3742 | 13.2637 | 13.1258 | 12.9626 | 12.7774 | 12.5889 | 12.3974 | 12.2068 | 8.2511 | 6.0711 | 4.8668 | 14.74 | 14.6863 | 14.6179 | 14.5326 | 14.3926 | 14.2084 | 14.0189 | 13.8274 | 13.6358 | 9.6642 | 7.4842 | 6.2821
|  | BARTON STACEY PRIMARY | HE |  |  |  |  | 16.4718 | 16.4245 | 16.3718 | 16.3003 | 16.2013 | 16.1108 | 16.0224 | 14.3255 | 14.2224 | 12.8276 | 12.1434 | 11.2455 | 13.5216 | 13.4489 | 13.3711 | 13.2721 | 13.1479 | 13.0374 | 12.9279 | 10.6668 | 10.5595 | 8.8847 | 8.0668 | 6.9995 | 14.7579 | 14.7084 | 14.6547 | 14.5811 | 14.4811 | 14.3895 | 14.2989 | 12.0884 | 11.9811 | 10.3 | 9.4779 | 8.4105
|  | BARTON STACEY PRIMARY | FB |  |  |  |  | 16.5055 | 16.4824 | 16.4613 | 16.4382 | 16.4118 | 16.3855 | 16.3613 | 16.3371 | 16.3129 | 16.195 | 15.515 | 14.7255 | 13.5805 | 13.5247 | 13.4826 | 13.4363 | 13.3889 | 13.3416 | 13.2953 | 13.2511 | 13.2047 | 12.8532 | 12.0458 | 11.1047 | 14.7937 | 14.7684 | 14.7463 | 14.7211 | 14.6937 | 14.6663 | 14.64 | 14.6147 | 14.5884 | 14.2832 | 13.4726 | 12.5274
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | BASINGSTOKE PRIMARY | MINIMUM HEADROOM | SU 65155 52705 | NO | YES | 0 | 24.3605 | 24.2184 | 24.0532 | 23.8479 | 23.5447 | 23.2237 | 22.9279 | 22.7647 | 22.5016 | 23.2732 | 22.99 | 22.7458 | 23.02 | 22.8874 | 22.7326 | 22.5379 | 21.7147 | 20.4221 | 19.4453 | 19.4716 | 18.6179 | 20.3642 | 19.8284 | 19.3663 | 24.5095 | 24.3768 | 24.2221 | 24.0274 | 23.1526 | 21.9811 | 21.0147 | 21.0442 | 20.18 | 21.9368 | 21.4042 | 20.9379
|  | BASINGSTOKE PRIMARY | EE |  |  |  |  | 24.3605 | 24.2184 | 24.0574 | 23.8668 | 23.5826 | 23.2879 | 23.0374 | 22.7647 | 22.5016 | 25.7847 | 25.6447 | 24.9753 | 23.0221 | 22.8874 | 22.7411 | 22.5568 | 22.2063 | 21.1189 | 20.4126 | 19.4716 | 18.6179 | 23.8358 | 23.6779 | 23.0389 | 24.5116 | 24.3768 | 24.2305 | 24.0463 | 23.5863 | 22.5968 | 21.9495 | 21.0442 | 20.18 | 26.2032 | 26.0842 | 25.7189
|  | BASINGSTOKE PRIMARY | HT |  |  |  |  | 24.3616 | 24.2205 | 24.0532 | 23.8479 | 23.5447 | 23.2237 | 22.9279 | 26.3205 | 26.0363 | 25.5089 | 24.8584 | 23.9521 | 23.02 | 22.8916 | 22.7326 | 22.5379 | 21.7147 | 20.4221 | 19.4453 | 24.2747 | 24.0368 | 23.5242 | 22.9547 | 21.9842 | 24.5095 | 24.3811 | 24.2221 | 24.0274 | 23.1526 | 21.9811 | 21.0147 | 26.6421 | 26.4042 | 25.9295 | 25.4653 | 24.6642
|  | BASINGSTOKE PRIMARY | HE |  |  |  |  | 24.4174 | 24.2974 | 24.1658 | 23.9953 | 23.73 | 23.4637 | 23.2332 | 22.9826 | 22.7479 | 26.2816 | 26.1795 | 26.1037 | 23.0695 | 22.9537 | 22.8337 | 22.6674 | 22.4432 | 21.5632 | 20.9168 | 20.0905 | 19.3611 | 24.2789 | 24.1916 | 24.1284 | 24.5589 | 24.4432 | 24.3232 | 24.1568 | 23.9326 | 23.0095 | 22.4158 | 21.6611 | 20.9326 | 26.6463 | 26.5589 | 26.4958
|  | BASINGSTOKE PRIMARY | FB |  |  |  |  | 24.4689 | 24.3868 | 24.3089 | 24.2226 | 24.1205 | 24.0153 | 23.9195 | 23.8268 | 23.7237 | 23.2732 | 22.99 | 22.7458 | 23.1179 | 23.04 | 22.9653 | 22.8863 | 22.8032 | 22.7179 | 22.6337 | 22.5253 | 22.16 | 20.3642 | 19.8284 | 19.3663 | 24.6074 | 24.5295 | 24.4547 | 24.3758 | 24.2926 | 24.2074 | 24.1232 | 23.8958 | 23.5642 | 21.9368 | 21.4042 | 20.9379
NURSLING GSP | VELMORE BSP | BASSETT PRIMARY | MINIMUM HEADROOM | SU 42193 15958 | NO | YES | 0 | 30.5358 | 30.3789 | 30.2063 | 29.9653 | 29.6621 | 29.3474 | 29.0263 | 28.7116 | 28.3211 | 26.4347 | 25.1684 | 24.0589 | 29.5905 | 29.4337 | 29.2432 | 28.7716 | 28.1674 | 27.7232 | 27.2274 | 26.6389 | 25.9611 | 23.7874 | 22.3747 | 21.1368 | 26.14 | 25.9684 | 25.76 | 25.4863 | 25.1505 | 24.8095 | 24.4632 | 24.1105 | 23.7484 | 22.8926 | 22.1474 | 21.1274
|  | BASSETT PRIMARY | EE |  |  |  |  | 30.5358 | 30.3789 | 30.2116 | 29.9832 | 29.6621 | 29.3632 | 29.0916 | 28.8095 | 28.5305 | 28.3147 | 27.62 | 26.9032 | 29.5905 | 29.4337 | 29.2653 | 28.9547 | 28.5253 | 28.1011 | 27.6537 | 27.2453 | 26.8568 | 26.0884 | 25.1505 | 24.2884 | 26.14 | 25.9684 | 25.7684 | 25.5284 | 25.1916 | 24.8758 | 24.5789 | 24.2789 | 23.9842 | 23.6926 | 23.4158 | 23.1947
|  | BASSETT PRIMARY | HT |  |  |  |  | 30.5421 | 30.3979 | 30.2063 | 29.9653 | 29.6716 | 29.3474 | 29.0263 | 28.7116 | 28.3211 | 26.4347 | 25.1684 | 24.0589 | 29.5968 | 29.4526 | 29.2432 | 28.7716 | 28.1674 | 27.7232 | 27.2274 | 26.6389 | 25.9611 | 23.7874 | 22.3747 | 21.1368 | 26.1495 | 25.9768 | 25.76 | 25.4863 | 25.1505 | 24.8095 | 24.4632 | 24.1105 | 23.7484 | 22.8926 | 22.1474 | 21.1274
|  | BASSETT PRIMARY | HE |  |  |  |  | 30.5705 | 30.4253 | 30.2632 | 30.04 | 29.72 | 29.4368 | 29.1611 | 28.8758 | 28.6 | 28.6253 | 28.5684 | 28.5295 | 29.6253 | 29.48 | 29.3179 | 29.0947 | 28.7747 | 28.4758 | 28.0632 | 27.6937 | 27.3463 | 27.0726 | 26.6737 | 26.2905 | 26.1926 | 26.0389 | 25.8516 | 25.62 | 25.2884 | 24.9916 | 24.6958 | 24.3989 | 24.1137 | 24.0968 | 23.9926 | 23.9053
|  | BASSETT PRIMARY | FB |  |  |  |  | 30.6779 | 30.6042 | 30.5368 | 30.4621 | 30.38 | 30.2958 | 30.2147 | 30.14 | 30.0579 | 29.7621 | 29.5958 | 29.4905 | 29.7326 | 29.6589 | 29.5916 | 29.5168 | 29.4347 | 29.3505 | 29.2695 | 29.1947 | 29.0863 | 28.5021 | 28.0421 | 27.6316 | 26.3074 | 26.2232 | 26.1495 | 26.0611 | 25.9705 | 25.8779 | 25.7863 | 25.7011 | 25.6105 | 25.2747 | 25.0674 | 24.9189
NORTH HYDE GSP | NORTH HYDE BSP | BATH ROAD EAST PRIMARY | MINIMUM HEADROOM | TQ 09097 76885 | NO | NO | 0 | 12.5179 | 12.2505 | 12.1411 | 40.0979 | 39.9063 | 39.6789 | 39.4305 | 39.1663 | 38.8989 | 38.3053 | 37.8274 | 37.3695 | 11.5211 | 11.4789 | 11.4316 | 39.4684 | 39.3832 | 39.3011 | 39.2137 | 39.0495 | 38.7568 | 38.1368 | 37.6116 | 37.1074 | 9.9432 | 9.9011 | 9.8537 | 37.8905 | 37.8053 | 37.7232 | 37.6358 | 37.4421 | 37.1326 | 36.4716 | 35.9168 | 35.3832
|  | BATH ROAD EAST PRIMARY | EE |  |  |  |  | 12.5284 | 12.4432 | 12.1411 | 40.1368 | 40.0105 | 39.8905 | 39.7621 | 39.6316 | 39.5021 | 39.1916 | 38.9042 | 38.6074 | 11.5211 | 11.4789 | 11.4316 | 39.4705 | 39.3832 | 39.3021 | 39.2263 | 39.1463 | 39.0684 | 39.0042 | 38.8021 | 38.4705 | 9.9432 | 9.9011 | 9.8537 | 37.8926 | 37.8053 | 37.7242 | 37.6484 | 37.5684 | 37.4905 | 37.4263 | 37.1789 | 36.8263
|  | BATH ROAD EAST PRIMARY | HT |  |  |  |  | 12.5179 | 12.2505 | 12.1421 | 40.0979 | 39.9063 | 39.6789 | 39.4305 | 39.1663 | 38.8989 | 38.3053 | 37.8274 | 37.3695 | 11.5242 | 11.4853 | 11.4358 | 39.4684 | 39.3884 | 39.3011 | 39.2137 | 39.0495 | 38.7568 | 38.1368 | 37.6116 | 37.1074 | 9.9463 | 9.9074 | 9.8579 | 37.8905 | 37.8105 | 37.7232 | 37.6358 | 37.4421 | 37.1326 | 36.4716 | 35.9168 | 35.3832
|  | BATH ROAD EAST PRIMARY | HE |  |  |  |  | 12.5779 | 12.5116 | 12.2295 | 40.2337 | 40.1158 | 40.0063 | 39.9011 | 39.7937 | 39.6863 | 39.5579 | 39.3389 | 39.14 | 11.5274 | 11.4863 | 11.4432 | 39.48 | 39.3905 | 39.3105 | 39.2326 | 39.1526 | 39.0737 | 39.0821 | 39.0653 | 39.0295 | 9.9495 | 9.9084 | 9.8653 | 37.9021 | 37.8126 | 37.7326 | 37.6547 | 37.5747 | 37.4958 | 37.5042 | 37.4874 | 37.4263
|  | BATH ROAD EAST PRIMARY | FB |  |  |  |  | 12.7389 | 12.6874 | 12.6442 | 40.6105 | 40.56 | 40.5095 | 40.4621 | 40.4147 | 40.3663 | 40.16 | 39.9358 | 39.7295 | 11.5547 | 11.5305 | 11.5084 | 39.5842 | 39.5568 | 39.5295 | 39.5032 | 39.4779 | 39.4516 | 39.3558 | 39.3 | 39.2653 | 9.9768 | 9.9526 | 9.9305 | 38.0063 | 37.9789 | 37.9516 | 37.9253 | 37.9 | 37.8737 | 37.7779 | 37.7221 | 37.6874
IVER 132KV GSP | LONGFORD BSP | BATH ROAD WEST PRIMARY | MINIMUM HEADROOM | TQ 05814 76820 | NO | NO | 2 | 33.4637 | 33.4363 | 33.4037 | 33.3605 | 33.3047 | 33.25 | 33.1932 | 33.1374 | 33.0805 | 32.6111 | 32.2132 | 31.8542 | 31.4095 | 31.3821 | 31.3495 | 31.3063 | 31.2505 | 31.0568 | 30.7937 | 30.5126 | 30.2284 | 29.5621 | 29.1147 | 28.7105 | 29.7937 | 29.7116 | 29.5842 | 29.3989 | 29.1758 | 28.9389 | 28.7042 | 28.4526 | 28.2 | 27.6189 | 27.2211 | 26.8632
|  | BATH ROAD WEST PRIMARY | EE |  |  |  |  | 33.4637 | 33.4363 | 33.4037 | 33.3616 | 33.3047 | 33.2511 | 33.1984 | 33.1458 | 33.0921 | 33.0605 | 33.0237 | 32.9963 | 31.4095 | 31.3821 | 31.3495 | 31.3074 | 31.2505 | 31.1968 | 31.1442 | 31.0916 | 31.0379 | 30.7853 | 30.4379 | 30.1253 | 29.7937 | 29.7326 | 29.66 | 29.5705 | 29.4674 | 29.36 | 29.2379 | 29.1168 | 28.9958 | 28.6853 | 28.3811 | 28.1074
|  | BATH ROAD WEST PRIMARY | HT |  |  |  |  | 33.4647 | 33.4384 | 33.4047 | 33.3605 | 33.3079 | 33.25 | 33.1932 | 33.1374 | 33.0805 | 32.6111 | 32.2132 | 31.8542 | 31.4105 | 31.3842 | 31.3505 | 31.3063 | 31.2537 | 31.0568 | 30.7937 | 30.5126 | 30.2284 | 29.5621 | 29.1147 | 28.7105 | 29.7968 | 29.7116 | 29.5842 | 29.3989 | 29.1758 | 28.9389 | 28.7042 | 28.4526 | 28.2 | 27.6189 | 27.2211 | 26.8632
|  | BATH ROAD WEST PRIMARY | HE |  |  |  |  | 33.4658 | 33.4405 | 33.4089 | 33.3679 | 33.31 | 33.2553 | 33.2026 | 33.15 | 33.0963 | 33.1121 | 33.0932 | 33.0868 | 31.4116 | 31.3863 | 31.3547 | 31.3137 | 31.2558 | 31.2011 | 31.1484 | 31.0958 | 31.0421 | 31.0579 | 30.8642 | 30.6337 | 29.8242 | 29.7758 | 29.7147 | 29.6358 | 29.5368 | 29.4358 | 29.3389 | 29.2442 | 29.1484 | 29.0021 | 28.7505 | 28.5516
|  | BATH ROAD WEST PRIMARY | FB |  |  |  |  | 33.4879 | 33.4742 | 33.4616 | 33.4479 | 33.4332 | 33.4174 | 33.4026 | 33.3889 | 33.3742 | 33.3195 | 33.2889 | 33.2689 | 31.4337 | 31.42 | 31.4074 | 31.3937 | 31.3789 | 31.3632 | 31.3484 | 31.3347 | 31.32 | 31.2653 | 31.2347 | 31.1526 | 29.8589 | 29.8253 | 29.7947 | 29.76 | 29.7242 | 29.6853 | 29.6442 | 29.6042 | 29.5642 | 29.3779 | 29.1926 | 29.0242
IVER 132KV GSP | DENHAM BSP | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | MINIMUM HEADROOM | SU 93668 91219 | NO | NO | 0.043158 | 12.9579 | 12.8705 | 12.7653 | 12.6242 | 41.2905 | 40.8895 | 40.4895 | 40.0905 | 39.6916 | 38.7337 | 38.0253 | 37.1895 | 12.8568 | 12.7642 | 12.6558 | 12.3263 | 36.4 | 35.7463 | 35.0779 | 34.3842 | 33.6916 | 32.02 | 30.92 | 29.9642 | 13.0621 | 12.9747 | 12.8695 | 12.7284 | 39.4053 | 39.0526 | 38.5821 | 37.9737 | 37.3663 | 35.7926 | 34.7032 | 33.7568
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | EE |  |  |  |  | 12.9579 | 12.8705 | 12.7705 | 12.6379 | 41.3716 | 41.0516 | 40.7411 | 40.4263 | 40.1179 | 39.7442 | 39.4316 | 39.1821 | 12.8568 | 12.7642 | 12.6611 | 12.4853 | 36.7189 | 36.3337 | 35.9189 | 35.4958 | 35.0832 | 34.2221 | 33.4726 | 32.8495 | 13.0621 | 12.9747 | 12.8747 | 12.7421 | 39.4495 | 39.1453 | 38.8537 | 38.5611 | 38.2726 | 37.7853 | 37.1674 | 36.6137
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | HT |  |  |  |  | 12.9589 | 12.8747 | 12.7653 | 12.6242 | 41.2905 | 40.8895 | 40.4895 | 40.0905 | 39.6916 | 38.7337 | 38.0253 | 37.1895 | 12.8589 | 12.7705 | 12.6558 | 12.3263 | 36.4 | 35.7463 | 35.0779 | 34.3842 | 33.6916 | 32.02 | 30.92 | 29.9642 | 13.0632 | 12.9789 | 12.8695 | 12.7284 | 39.4053 | 39.0526 | 38.5821 | 37.9737 | 37.3663 | 35.7926 | 34.7032 | 33.7568
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | HE |  |  |  |  | 12.9737 | 12.8895 | 12.7968 | 12.6674 | 41.4747 | 41.2 | 40.9316 | 40.6611 | 40.3937 | 40.3232 | 40.1947 | 40.0947 | 12.8768 | 12.7895 | 12.6958 | 12.5642 | 37.1358 | 36.8337 | 36.5179 | 36.1621 | 35.8158 | 35.4632 | 35.0368 | 34.6811 | 13.0779 | 12.9937 | 12.9011 | 12.7716 | 39.58 | 39.2968 | 39.0179 | 38.7368 | 38.4589 | 38.4379 | 38.3632 | 38.1863
|  | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY | FB |  |  |  |  | 13.0432 | 13.0032 | 12.9674 | 12.9274 | 42.1253 | 42.0516 | 41.9811 | 41.9147 | 41.8453 | 41.5179 | 41.2716 | 41.0884 | 12.9516 | 12.9084 | 12.8705 | 12.8284 | 37.8158 | 37.7147 | 37.6147 | 37.5189 | 37.4189 | 36.8579 | 36.3232 | 35.8737 | 13.1474 | 13.1074 | 13.0716 | 13.0316 | 40.2389 | 40.1568 | 40.0768 | 40 | 39.9211 | 39.6158 | 39.4263 | 39.2937
IVER 132KV GSP | UPTON BSP | BEACONSFIELD (END BUSBARS) PRIMARY | MINIMUM HEADROOM | SU 93668 91219 | NO | NO | 0 | Generation Headroom Winter (MVA) 2027: 6.4821; Generation Headroom Winter (MVA) 2028: 6.4232; Generation Headroom Winter (MVA) 2029: 6.3474; Generation Headroom Winter (MVA) 2030: 6.2326 | 4.4895 | 4.3674 | 4.2453 | 4.0684 | [8 empty] | 5.4979 | 5.4158 | 5.3263 | 5.2
|  | BEACONSFIELD (END BUSBARS) PRIMARY | EE |  |  |  |  | Generation Headroom Winter (MVA) 2027: 6.4821; Generation Headroom Winter (MVA) 2028: 6.4232; Generation Headroom Winter (MVA) 2029: 6.3558; Generation Headroom Winter (MVA) 2030: 6.2653 | 4.4895 | 4.3674 | 4.2453 | 4.1063 | [8 empty] | 5.4979 | 5.4158 | 5.3295 | 5.2221
|  | BEACONSFIELD (END BUSBARS) PRIMARY | HT |  |  |  |  | Generation Headroom Winter (MVA) 2027: 6.4821; Generation Headroom Winter (MVA) 2028: 6.4242; Generation Headroom Winter (MVA) 2029: 6.3474; Generation Headroom Winter (MVA) 2030: 6.2326 | 4.5126 | 4.4 | 4.2526 | 4.0684 | [8 empty] | 5.5053 | 5.4284 | 5.3263 | 5.2
|  | BEACONSFIELD (END BUSBARS) PRIMARY | HE |  |  |  |  | Generation Headroom Winter (MVA) 2027: 6.4968; Generation Headroom Winter (MVA) 2028: 6.4421; Generation Headroom Winter (MVA) 2029: 6.3811; Generation Headroom Winter (MVA) 2030: 6.2968 | 4.5768 | 4.4884 | 4.3989 | 4.2863 | [8 empty] | 5.5379 | 5.4716 | 5.4 | 5.3063
|  | BEACONSFIELD (END BUSBARS) PRIMARY | FB |  |  |  |  | Generation Headroom Winter (MVA) 2027: 6.5421; Generation Headroom Winter (MVA) 2028: 6.5168; Generation Headroom Winter (MVA) 2029: 6.4947; Generation Headroom Winter (MVA) 2030: 6.4695 | 4.6537 | 4.5874 | 4.5389 | 4.4874 | [8 empty] | 5.5937 | 5.5547 | 5.5232 | 5.4884
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BEENHAM PRIMARY | MINIMUM HEADROOM | SU 58204 69025 | NO | YES | 0 | 14.7053 | 14.6421 | 14.2074 | 14.0611 | 13.8863 | 13.7032 | 13.5253 | 13.3305 | 13.1337 | 12.3495 | 12.0221 | 11.7011 | 12.4863 | 12.3705 | 11.1589 | 10.9926 | 10.7968 | 10.5916 | 10.3916 | 10.1705 | 9.9442 | 9.0316 | 8.6726 | 8.3168 | 13.2716 | 13.1568 | 11.9768 | 11.8137 | 11.62 | 11.4189 | 11.2211 | 11.0042 | 10.7811 | 9.8874 | 9.5337 | 9.1842
|  | BEENHAM PRIMARY | EE |  |  |  |  | 14.7053 | 14.6421 | 14.2074 | 14.0884 | 13.9453 | 13.8116 | 13.6726 | 13.5305 | 13.4 | 12.8474 | 12.6126 | 12.3937 | 12.4863 | 12.3705 | 11.1589 | 11.0295 | 10.8779 | 10.7358 | 10.5853 | 10.4326 | 10.2926 | 9.6095 | 9.3316 | 9.0853 | 13.2716 | 13.1568 | 11.9768 | 11.8495 | 11.6979 | 11.5558 | 11.4063 | 11.2547 | 11.1147 | 10.4484 | 10.1747 | 9.9316
|  | BEENHAM PRIMARY | HT |  |  |  |  | 14.7137 | 14.6547 | 14.2211 | 14.0611 | 13.8863 | 13.7032 | 13.5253 | 13.3305 | 13.1337 | 12.3495 | 12.0221 | 11.7011 | 12.5137 | 12.4095 | 11.1726 | 10.9926 | 10.7968 | 10.5916 | 10.3916 | 10.1705 | 9.9442 | 9.0316 | 8.6726 | 8.3168 | 13.2989 | 13.1947 | 11.9926 | 11.8137 | 11.62 | 11.4189 | 11.2211 | 11.0042 | 10.7811 | 9.8874 | 9.5337 | 9.1842
|  | BEENHAM PRIMARY | HE |  |  |  |  | 14.7368 | 14.6905 | 14.3579 | 14.2684 | 14.1495 | 14.0432 | 13.9389 | 13.8358 | 13.7347 | 13.3916 | 13.2842 | 13.1842 | 12.58 | 12.5053 | 11.3337 | 11.2389 | 11.1158 | 11.0032 | 10.8937 | 10.7874 | 10.6821 | 10.2368 | 10.1032 | 9.9779 | 13.3642 | 13.2905 | 12.1516 | 12.0579 | 11.9347 | 11.8232 | 11.7147 | 11.6084 | 11.5042 | 11.0716 | 10.9421 | 10.82
|  | BEENHAM PRIMARY | FB |  |  |  |  | 14.7737 | 14.7526 | 14.4674 | 14.4295 | 14.3863 | 14.3432 | 14.3032 | 14.2642 | 14.2253 | 14.0684 | 13.7337 | 13.6011 | 12.6432 | 12.5874 | 11.4484 | 11.4053 | 11.3579 | 11.3095 | 11.2632 | 11.22 | 11.1768 | 10.9989 | 10.5832 | 10.4211 | 13.4263 | 13.3716 | 12.2653 | 12.2232 | 12.1758 | 12.1284 | 12.0832 | 12.04 | 11.9979 | 11.8232 | 11.4168 | 11.2589
MANNINGTON GSP | SALISBURY BSP | BEMERTON PRIMARY | MINIMUM HEADROOM | SU 11583 31233 | NO | YES | 0 | 33.1411 | 32.9695 | 32.7621 | 32.54 | 31.9116 | 31.4874 | 30.9989 | 30.5905 | 30.0526 | 30.4021 | 28.9747 | 27.6832 | 31.5021 | 31.3779 | 30.7074 | 30.1653 | 29.14 | 28.6337 | 28.0979 | 27.6589 | 27.0632 | 27.8042 | 26.1916 | 24.7305 | 29.5674 | 29.1937 | 28.6789 | 28.2989 | 27.6232 | 27.2358 | 26.8421 | 26.4968 | 26.0695 | 27.8705 | 26.2926 | 24.8316
|  | BEMERTON PRIMARY | EE |  |  |  |  | 33.1411 | 32.9695 | 32.7621 | 32.5432 | 31.9116 | 31.4874 | 30.9989 | 30.5905 | 30.0526 | 32.3589 | 31.3316 | 30.4253 | 31.5021 | 31.3779 | 30.7074 | 30.1884 | 29.14 | 28.6337 | 28.0979 | 27.6589 | 27.0632 | 30.0295 | 28.8474 | 27.8011 | 29.5674 | 29.1937 | 28.6789 | 28.3105 | 27.6232 | 27.2358 | 26.8421 | 26.4968 | 26.0695 | 29.92 | 28.9474 | 27.8989
|  | BEMERTON PRIMARY | HT |  |  |  |  | 33.1558 | 32.9916 | 32.7674 | 32.54 | 35.5789 | 35.1379 | 34.3116 | 33.5189 | 32.3684 | 30.4021 | 28.9747 | 27.6832 | 31.5116 | 31.3979 | 30.7074 | 30.1653 | 34.0211 | 33.1516 | 32.2211 | 31.3305 | 30.0189 | 27.8042 | 26.1916 | 24.7305 | 29.6042 | 29.22 | 28.6811 | 28.2989 | 32.5611 | 32.0242 | 31.4011 | 30.8 | 29.9684 | 27.9063 | 26.2926 | 24.8316
|  | BEMERTON PRIMARY | HE |  |  |  |  | 33.1884 | 33.0295 | 32.8295 | 32.6189 | 32.1253 | 31.7747 | 31.4189 | 31.0642 | 30.5579 | 33.3316 | 32.5716 | 31.8979 | 31.5326 | 31.4137 | 31.0179 | 30.5484 | 29.5295 | 29.0589 | 28.5832 | 28.2063 | 27.6505 | 31.1326 | 30.2453 | 29.4558 | 29.6832 | 29.3495 | 28.8674 | 28.5284 | 27.8547 | 27.4916 | 27.1295 | 26.82 | 26.4126 | 30.6358 | 30.1274 | 29.5589
|  | BEMERTON PRIMARY | FB |  |  |  |  | 33.2884 | 33.2042 | 33.1242 | 33.0526 | 32.9484 | 32.8505 | 32.7737 | 32.7074 | 32.6305 | 32.1442 | 35.2821 | 34.7021 | 31.6189 | 31.5589 | 31.5053 | 31.4453 | 31.3032 | 30.9379 | 30.7684 | 30.6484 | 30.4747 | 29.5253 | 33.2884 | 32.6189 | 29.8463 | 29.6558 | 29.46 | 29.3379 | 29.0684 | 28.8379 | 28.7158 | 28.6221 | 28.4979 | 27.8705 | 32.1832 | 31.7779
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | BERINSFIELD PRIMARY | MINIMUM HEADROOM | SU 58382 95467 | NO | YES | 0.13158 | 24.7024 | 23.8666 | 22.6392 | 21.115 | 19.1592 | 30.8874 | 28.6863 | 26.4695 | 23.4021 | 11.62 | 7.1284 | 3.8232 | 20.1108 | 19.0792 | 17.5908 | 15.8192 | 13.5424 | 22.6968 | 20.1326 | 17.5495 | 13.9579 | 0.16105 | -5.0758 | -8.92 | 21.4139 | 20.4603 | 19.0834 | 17.3161 | 15.0455 | 25.4084 | 22.8516 | 20.2747 | 16.6937 | 2.9358 | -2.2853 | -6.1179
|  | BERINSFIELD PRIMARY | EE |  |  |  |  | 24.7392 | 24.3603 | 23.2603 | 21.8845 | 20.1308 | 32.0989 | 30.0895 | 28.0779 | 25.6832 | 15.3947 | 11.4758 | 8.7284 | 20.1582 | 19.7076 | 18.3476 | 16.7276 | 14.6918 | 24.1274 | 21.7832 | 19.4379 | 16.6379 | 4.5232 | -0.070526 | -3.2863 | 21.4571 | 21.035 | 19.7782 | 18.2213 | 16.1908 | 26.8326 | 24.4958 | 22.1568 | 19.3663 | 7.2874 | 2.7074 | -0.5
|  | BERINSFIELD PRIMARY | HT |  |  |  |  | 24.7024 | 23.8666 | 22.6392 | 21.115 | 19.1592 | 30.8874 | 28.6863 | 26.4695 | 23.4021 | 11.62 | 7.1284 | 3.8232 | 20.1108 | 19.0792 | 17.5908 | 15.8192 | 13.5424 | 22.6968 | 20.1326 | 17.5495 | 13.9579 | 0.16105 | -5.0758 | -8.92 | 21.4139 | 20.4603 | 19.0834 | 17.3161 | 15.0455 | 25.4084 | 22.8516 | 20.2747 | 16.6937 | 2.9358 | -2.2853 | -6.1179
|  | BERINSFIELD PRIMARY | HE |  |  |  |  | 24.8824 | 24.5613 | 23.7024 | 22.6434 | 21.2087 | 33.5074 | 31.8326 | 30.1589 | 28.1042 | 19.6589 | 13.5232 | 9.9663 | 20.3308 | 19.9497 | 18.8918 | 17.6139 | 15.955 | 25.7789 | 23.8316 | 21.8842 | 19.4863 | 9.5 | 2.2789 | -1.9053 | 21.6182 | 21.2603 | 20.2824 | 19.0982 | 17.4518 | 28.48 | 26.5389 | 24.5968 | 22.2063 | 12.2495 | 5.0505 | 0.87895
|  | BERINSFIELD PRIMARY | FB |  |  |  |  | 25.1929 | 25.0097 | 24.7592 | 24.3203 | 23.7876 | 37.0737 | 36.2695 | 35.4063 | 34.4747 | 29.5863 | 25.4053 | 22.7474 | 20.7171 | 20.4855 | 20.1803 | 19.6382 | 18.9782 | 29.8926 | 28.9516 | 27.9379 | 26.8453 | 21.0947 | 16.1653 | 13.0316 | 21.9782 | 21.7613 | 21.4782 | 20.9771 | 20.3676 | 32.5516 | 31.6453 | 30.6337 | 29.5453 | 23.8116 | 18.8968 | 15.7726
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | BEVOIS VALLEY PRIMARY | MINIMUM HEADROOM | SU 42648 13187 | NO | YES | 0 | 29.2129 | 29.095 | 28.9445 | 28.6235 | 28.3445 | 28.1213 | 27.8782 | 27.5908 | 27.1424 | 25.8961 | 24.9866 | 24.1603 | 26.3329 | 26.1698 | 25.9403 | 25.3666 | 24.935 | 24.655 | 24.3329 | 23.9066 | 23.4319 | 22.1045 | 21.1719 | 20.3319 | 24.6603 | 24.574 | 24.4761 | 24.1656 | 23.7982 | 23.5424 | 23.254 | 22.8866 | 22.4835 | 21.3708 | 20.5919 | 19.8898
|  | BEVOIS VALLEY PRIMARY | EE |  |  |  |  | 29.2129 | 29.095 | 28.9708 | 28.7098 | 28.4961 | 28.2771 | 28.0445 | 27.8203 | 27.6045 | 27.0319 | 26.3677 | 25.7961 | 26.3329 | 26.1698 | 25.9992 | 25.5571 | 25.295 | 25.0077 | 24.675 | 24.3719 | 24.0866 | 23.3192 | 22.6024 | 21.9908 | 24.6603 | 24.5761 | 24.4856 | 24.3119 | 24.0708 | 23.8129 | 23.5224 | 23.2529 | 22.9971 | 22.3771 | 21.7971 | 21.3035
|  | BEVOIS VALLEY PRIMARY | HT |  |  |  |  | 29.2192 | 29.1045 | 28.9445 | 28.6235 | 28.3445 | 28.1213 | 27.8782 | 27.5908 | 27.1424 | 25.8961 | 24.9866 | 24.1603 | 26.3413 | 26.1761 | 25.9403 | 25.3666 | 24.935 | 24.655 | 24.3329 | 23.9066 | 23.4319 | 22.1045 | 21.1719 | 20.3319 | 24.6656 | 24.5877 | 24.4845 | 24.1656 | 23.7982 | 23.5424 | 23.254 | 22.8866 | 22.4835 | 21.3708 | 20.5919 | 19.8898
|  | BEVOIS VALLEY PRIMARY | HE |  |  |  |  | 29.2561 | 29.1466 | 29.0277 | 28.7635 | 28.5392 | 28.3192 | 28.1003 | 27.895 | 27.695 | 27.5908 | 27.3887 | 27.1003 | 26.415 | 26.2929 | 26.1466 | 25.7182 | 25.4571 | 25.1803 | 24.8982 | 24.6519 | 24.4182 | 24.1698 | 23.7677 | 23.3961 | 24.6656 | 24.574 | 24.4761 | 24.335 | 24.1371 | 23.9308 | 23.675 | 23.4456 | 23.2266 | 23.0392 | 22.7224 | 22.4308
|  | BEVOIS VALLEY PRIMARY | FB |  |  |  |  | 29.3582 | 29.2824 | 29.2171 | 29.1056 | 29.0266 | 28.9466 | 28.8613 | 28.7792 | 28.7013 | 28.3835 | 28.1266 | 27.9024 | 26.5108 | 26.4382 | 26.3761 | 26.2024 | 26.0961 | 25.9898 | 25.8677 | 25.7477 | 25.6435 | 25.1835 | 24.7456 | 24.3266 | 24.7245 | 24.6719 | 24.6235 | 24.5708 | 24.5108 | 24.4519 | 24.3929 | 24.3392 | 24.2813 | 23.9592 | 23.5982 | 23.2613
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER PRIMARY | MINIMUM HEADROOM | SP 58381 21988 | NO | YES | 1.0568 | 51.6063 | 51.4189 | 48.6695 | 46.5526 | 44.0053 | 37.9716 | 34.6832 | 31.4926 | 28.3147 | 15.3316 | 7.2705 | 5.3495 | 48.1526 | 46.8958 | 42.2653 | 39.8242 | 36.8863 | 29.8474 | 26.0432 | 22.3526 | 18.6758 | 3.5453 | -5.8505 | -8.0263 | 46.2989 | 45.0737 | 40.5716 | 38.1926 | 35.3305 | 28.4863 | 24.7821 | 21.1884 | 17.6084 | 2.8926 | -6.2453 | -8.3716
|  | BICESTER PRIMARY | EE |  |  |  |  | 51.6063 | 51.4189 | 49.1611 | 47.2368 | 44.9063 | 39.9358 | 37.4221 | 34.4084 | 31.4147 | 19.2937 | 12.3179 | 11.4284 | 48.2611 | 47.0695 | 42.8442 | 40.6242 | 37.94 | 32.1442 | 29.2389 | 25.7463 | 22.2779 | 8.0684 | -0.098947 | -1.1063 | 46.4032 | 45.2421 | 41.1326 | 38.9705 | 36.3558 | 30.72 | 27.8895 | 24.4895 | 21.1116 | 7.3074 | -0.62947 | -1.6147
|  | BICESTER PRIMARY | HT |  |  |  |  | 51.6326 | 51.4347 | 48.6695 | 46.5526 | 44.0053 | 37.9716 | 34.6832 | 31.4926 | 28.3147 | 15.3316 | 7.2705 | 5.3495 | 48.1526 | 46.8958 | 42.2653 | 39.8242 | 36.8863 | 29.8474 | 26.0432 | 22.3526 | 18.6758 | 3.5453 | -5.8505 | -8.0263 | 46.2989 | 45.0737 | 40.5716 | 38.1926 | 35.3305 | 28.4863 | 24.7821 | 21.1884 | 17.6084 | 2.8926 | -6.2453 | -8.3716
|  | BICESTER PRIMARY | HE |  |  |  |  | 51.6958 | 51.5432 | 49.6611 | 47.8126 | 45.5326 | 40.6242 | 38.2263 | 35.4726 | 32.7368 | 21.3368 | 14.5705 | 14.1211 | 48.5947 | 47.5305 | 43.4105 | 41.2758 | 38.6505 | 32.9263 | 30.1558 | 26.9695 | 23.8021 | 10.3968 | 2.4463 | 1.9295 | 46.7295 | 45.6926 | 41.6874 | 39.6074 | 37.0495 | 31.4832 | 28.7853 | 25.6821 | 22.5979 | 9.5811 | 1.8589 | 1.3558
|  | BICESTER PRIMARY | FB |  |  |  |  | 51.7937 | 51.7021 | 51.5737 | 51.4232 | 50.8189 | 48.7526 | 47.5884 | 46.3537 | 44.8116 | 37.1526 | 32.4421 | 31.8505 | 48.9621 | 48.3568 | 46.7568 | 45.8326 | 44.7632 | 42.3474 | 40.9937 | 39.5558 | 37.7579 | 28.8011 | 23.2895 | 22.6158 | 47.0895 | 46.4989 | 44.9442 | 44.0442 | 43.0021 | 40.6537 | 39.3379 | 37.9379 | 36.1895 | 27.4842 | 22.1274 | 21.4695
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH PRIMARY | MINIMUM HEADROOM | SP 59720 23735 | NO | YES | 0 | 32.1932 | 31.7563 | 30.9974 | 30.1026 | 29.0805 | 24.1142 | 21.4837 | 16.2658 | 11.7679 | 28.2274 | 22.0653 | 18.5642 | 27.8484 | 27.3558 | 26.4926 | 25.4768 | 24.3189 | 18.5242 | 15.4779 | 9.3863 | 4.1421 | 16.5095 | 9.2947 | 5.2021 | 23.8368 | 23.3453 | 22.4842 | 21.4695 | 20.3137 | 14.5295 | 11.4884 | 5.4074 | 0.17263 | 13.4674 | 6.2653 | 2.18
|  | BICESTER NORTH PRIMARY | EE |  |  |  |  | 32.4037 | 31.9763 | 31.2784 | 30.4647 | 29.5163 | 25.7258 | 21.5205 | 16.7974 | 12.71 | 28.2274 | 22.0653 | 18.5642 | 28.1 | 27.6179 | 26.8232 | 25.8979 | 24.8263 | 20.4074 | 15.4989 | 9.9832 | 5.2147 | 16.5095 | 9.2947 | 5.2021 | 24.0884 | 23.6074 | 22.8137 | 21.8895 | 20.82 | 16.4095 | 11.5095 | 6.0032 | 1.2432 | 13.4674 | 6.2653 | 2.18
|  | BICESTER NORTH PRIMARY | HT |  |  |  |  | 32.1932 | 31.7563 | 30.9974 | 30.1026 | 29.0805 | 24.1142 | 21.4837 | 16.2658 | 11.7679 | 31.3779 | 24.9484 | 20.9253 | 27.8484 | 27.3558 | 26.4926 | 25.4768 | 24.3189 | 18.5242 | 15.4779 | 9.3863 | 4.1421 | 20.3189 | 12.8253 | 8.1526 | 23.8368 | 23.3453 | 22.4842 | 21.4695 | 20.3137 | 14.5295 | 11.4884 | 5.4074 | 0.17263 | 17.2684 | 9.7874 | 5.1232
|  | BICESTER NORTH PRIMARY | HE |  |  |  |  | 32.6142 | 32.2679 | 31.6353 | 30.8732 | 29.9626 | 26.1026 | 21.8142 | 17.4816 | 13.8079 | 31.1316 | 24.3947 | 19.98 | 28.3358 | 27.9474 | 27.2263 | 26.3611 | 25.3326 | 20.8305 | 15.8242 | 10.7653 | 6.4832 | 19.8726 | 11.96 | 6.7737 | 24.3242 | 23.9358 | 23.2158 | 22.3516 | 21.3242 | 16.8316 | 11.8337 | 6.7842 | 2.5095 | 16.8242 | 8.9263 | 3.7495
|  | BICESTER NORTH PRIMARY | FB |  |  |  |  | 32.9089 | 32.6774 | 32.3742 | 32.0342 | 31.6595 | 31.1195 | 29.4132 | 27.8405 | 26.1142 | 44.8284 | 40.1705 | 36.8053 | 28.6695 | 28.4095 | 28.0632 | 27.6747 | 27.2463 | 26.6242 | 24.6295 | 22.7916 | 20.7716 | 35.8274 | 30.3726 | 26.4295 | 24.6568 | 24.3968 | 24.0516 | 23.6632 | 23.2358 | 22.6147 | 20.6232 | 18.7884 | 16.7737 | 32.7505 | 27.3053 | 23.3695
LOVEDEAN GSP | CHICHESTER BSP | BILLINGSHURST PRIMARY | MINIMUM HEADROOM | TQ 08305 26315 | YES | YES | 0 | 23.5516 | 23.3537 | 23.1358 | 22.8232 | 22.4968 | 22.1242 | 21.4789 | 20.7747 | 20.1505 | 18.2158 | 16.8053 | 15.5105 | 23.4947 | 23.2779 | 23.04 | 22.6968 | 22.3432 | 21.9379 | 21.2126 | 20.4158 | 19.7126 | 17.5116 | 15.8968 | 14.4137 | 23.4958 | 23.2789 | 23.0421 | 22.6989 | 22.3463 | 21.9421 | 21.2179 | 20.4232 | 19.7221 | 17.5263 | 15.9137 | 14.4347
|  | BILLINGSHURST PRIMARY | EE |  |  |  |  | 23.5516 | 23.3537 | 23.1358 | 22.8453 | 22.5368 | 22.2895 | 21.9832 | 21.6358 | 21.3747 | 20.3095 | 19.2895 | 18.3726 | 23.4947 | 23.2779 | 23.04 | 22.7211 | 22.3916 | 22.1316 | 21.8 | 21.4221 | 21.1442 | 19.9116 | 18.7295 | 17.6642 | 23.4958 | 23.2789 | 23.0421 | 22.7242 | 22.3947 | 22.1337 | 21.8021 | 21.4263 | 21.1484 | 19.9189 | 18.74 | 17.6779
|  | BILLINGSHURST PRIMARY | HT |  |  |  |  | 23.58 | 23.3884 | 23.1379 | 22.8232 | 22.4968 | 22.1242 | 21.4789 | 20.7747 | 20.1505 | 18.2158 | 16.8053 | 15.5105 | 23.5263 | 23.3168 | 23.0421 | 22.6968 | 22.3432 | 21.9379 | 21.2126 | 20.4158 | 19.7126 | 17.5116 | 15.8968 | 14.4137 | 23.5274 | 23.3179 | 23.0442 | 22.6989 | 22.3463 | 21.9421 | 21.2179 | 20.4232 | 19.7221 | 17.5263 | 15.9137 | 14.4347
|  | BILLINGSHURST PRIMARY | HE |  |  |  |  | 23.6737 | 23.52 | 23.3442 | 23.0884 | 22.8053 | 22.5884 | 22.3179 | 22.0105 | 21.7884 | 21.0263 | 20.1968 | 19.4411 | 23.6337 | 23.4684 | 23.2789 | 23 | 22.6989 | 22.4737 | 22.1853 | 21.8516 | 21.6189 | 20.7189 | 19.7474 | 18.8589 | 23.6347 | 23.4695 | 23.28 | 23.0021 | 22.7011 | 22.4758 | 22.1874 | 21.8547 | 21.6232 | 20.7253 | 19.7568 | 18.8705
|  | BILLINGSHURST PRIMARY | FB |  |  |  |  | 23.8126 | 23.7074 | 23.6189 | 23.5063 | 23.3968 | 23.3053 | 23.2074 | 23.0811 | 22.9947 | 22.3263 | 21.6905 | 21.1253 | 23.7874 | 23.6695 | 23.5737 | 23.4484 | 23.3274 | 23.2284 | 23.1211 | 22.98 | 22.8863 | 22.1295 | 21.3968 | 20.7411 | 23.7874 | 23.6705 | 23.5747 | 23.4495 | 23.3284 | 23.2295 | 23.1221 | 22.9821 | 22.8884 | 22.1326 | 21.4032 | 20.7484
LOVEDEAN GSP | CHICHESTER BSP | BILSHAM PRIMARY | MINIMUM HEADROOM | SU 97366 01594 | NO | YES | 4.2526 | 18.0842 | 16.8442 | 44.9695 | 43.1116 | 40.68 | 38.1853 | 35.8263 | 33.4011 | 30.8832 | 23.8084 | 21.4042 | 19.1916 | 11.8937 | 10.4705 | 38.3053 | 36.1695 | 33.3768 | 30.5084 | 27.7937 | 25.1463 | 22.2495 | 14.0779 | 11.3495 | 8.8347 | 15.0674 | 13.6442 | 41.4789 | 39.3442 | 36.5547 | 33.6895 | 30.9768 | 28.3526 | 25.5432 | 17.3874 | 14.6579 | 12.14
|  | BILSHAM PRIMARY | EE |  |  |  |  | 18.0842 | 16.8442 | 44.9695 | 43.1116 | 40.68 | 38.1853 | 35.8263 | 33.5421 | 31.2663 | 26.0284 | 24.2684 | 24.8579 | 11.8937 | 10.4705 | 38.3053 | 36.1695 | 33.3768 | 30.5084 | 27.7937 | 25.1674 | 22.5526 | 16.4516 | 14.4411 | 16.0621 | 15.0674 | 13.6442 | 41.4789 | 39.3442 | 36.5547 | 33.6895 | 30.9768 | 28.3526 | 25.74 | 19.6326 | 17.6053 | 19.6053
|  | BILSHAM PRIMARY | HT |  |  |  |  | 18.5579 | 17.16 | 45.54 | 43.6253 | 41.1432 | 38.4621 | 35.9179 | 33.4011 | 30.8832 | 23.8084 | 21.4042 | 19.1916 | 12.6032 | 10.9863 | 39.1211 | 36.9189 | 34.0589 | 30.9716 | 28.0432 | 25.1463 | 22.2495 | 14.0779 | 11.3495 | 8.8347 | 15.8558 | 14.2421 | 42.38 | 40.1821 | 37.3274 | 34.2474 | 31.3253 | 28.4337 | 25.5432 | 17.3874 | 14.6579 | 12.14
|  | BILSHAM PRIMARY | HE |  |  |  |  | 18.3389 | 17.1989 | 45.4168 | 43.6337 | 41.26 | 38.8379 | 36.5842 | 34.4053 | 32.2358 | 27.7095 | 26.4105 | 27.3968 | 12.1768 | 10.8642 | 38.7989 | 36.7453 | 34.0137 | 31.2221 | 28.6253 | 26.1179 | 23.6211 | 18.2853 | 16.7632 | 18.7989 | 15.3589 | 14.0495 | 41.9905 | 39.9432 | 37.2179 | 34.4337 | 31.8442 | 29.3432 | 26.8537 | 21.5337 | 20.0158 | 22.4547
|  | BILSHAM PRIMARY | FB |  |  |  |  | 18.8137 | 18.2074 | 47.5147 | 46.6568 | 45.7263 | 44.6642 | 43.5916 | 42.4842 | 41.2905 | 35.4589 | 34.3768 | 33.3979 | 12.7116 | 12.0126 | 41.2105 | 40.2158 | 39.1368 | 37.9021 | 36.6547 | 35.3653 | 33.9758 | 27.1674 | 25.9253 | 24.7937 | 15.8937 | 15.1958 | 44.3958 | 43.4032 | 42.3274 | 41.0968 | 39.8526 | 38.5674 | 37.1821 | 30.3926 | 29.1537 | 28.0253
FAWLEY GSP | COWES BSP | BINSTEAD PRIMARY | MINIMUM HEADROOM | SZ 56409 91399 | NO | YES | 0 | 15.3571 | 15.1613 | 14.9613 | 14.6497 | 14.2813 | 13.8739 | 13.4466 | 12.9939 | 12.5497 | 9.4908 | 8.5961 | 7.7897 | 13.6774 | 13.4647 | 13.2511 | 12.9142 | 12.5163 | 12.0742 | 11.61 | 11.1142 | 10.6279 | 7.1226 | 6.1216 | 5.2205 | 14.2937 | 14.0895 | 13.8821 | 13.5579 | 13.1705 | 12.7295 | 12.2642 | 11.7695 | 11.2832 | 7.7758 | 6.7758 | 5.8726
|  | BINSTEAD PRIMARY | EE |  |  |  |  | 15.3571 | 15.1613 | 14.9613 | 14.7318 | 14.4624 | 14.2013 | 13.9318 | 13.6424 | 13.3645 | 11.8329 | 11.2266 | 10.695 | 13.6774 | 13.4647 | 13.2511 | 13.0089 | 12.7279 | 12.4574 | 12.1721 | 11.8658 | 11.5721 | 9.7953 | 9.1026 | 8.4932 | 14.2937 | 14.0895 | 13.8821 | 13.6463 | 13.3716 | 13.1053 | 12.8263 | 12.5189 | 12.2253 | 10.4495 | 9.7568 | 9.1474
|  | BINSTEAD PRIMARY | HT |  |  |  |  | 15.3929 | 15.2034 | 14.9645 | 14.6497 | 14.2813 | 13.8739 | 13.4466 | 12.9939 | 12.5497 | 9.4908 | 8.5961 | 7.7897 | 13.7195 | 13.5142 | 13.2542 | 12.9142 | 12.5163 | 12.0742 | 11.61 | 11.1142 | 10.6279 | 7.1226 | 6.1216 | 5.2205 | 14.3326 | 14.1347 | 13.8853 | 13.5579 | 13.1705 | 12.7295 | 12.2642 | 11.7695 | 11.2832 | 7.7758 | 6.7758 | 5.8726
|  | BINSTEAD PRIMARY | HE |  |  |  |  | 15.4845 | 15.3403 | 15.1845 | 14.9918 | 14.7497 | 14.5224 | 14.2918 | 14.0434 | 13.8045 | 12.5845 | 12.175 | 11.8066 | 13.8237 | 13.6711 | 13.5079 | 13.3068 | 13.0584 | 12.8237 | 12.5858 | 12.3258 | 12.0784 | 10.6416 | 10.1647 | 9.7353 | 14.4305 | 14.2811 | 14.1221 | 13.9253 | 13.68 | 13.4495 | 13.2147 | 12.96 | 12.7168 | 11.2958 | 10.8189 | 10.3895
|  | BINSTEAD PRIMARY | FB |  |  |  |  | 15.6129 | 15.5076 | 15.4276 | 15.3413 | 15.2529 | 15.1624 | 15.075 | 14.9813 | 14.8897 | 14.4571 | 14.0529 | 13.6939 | 13.9605 | 13.8437 | 13.7563 | 13.6647 | 13.5689 | 13.4711 | 13.3763 | 13.2753 | 13.1753 | 12.6984 | 12.2416 | 11.83 | 14.5632 | 14.4516 | 14.3684 | 14.2789 | 14.1863 | 14.0926 | 14.0021 | 13.9042 | 13.8084 | 13.3537 | 12.8958 | 12.4853
LOVEDEAN GSP | CHICHESTER BSP | BIRDHAM PRIMARY | MINIMUM HEADROOM | SZ 81965 99422 | NO | YES | 0 | 12.5242 | 12.28 | 11.9263 | 29.8079 | 29.1584 | 28.4711 | 27.7942 | 27.0647 | 26.2858 | 24.4384 | 22.9953 | 21.7195 | 9.1389 | 8.8611 | 8.4463 | 24.5968 | 23.8189 | 23 | 22.1958 | 21.3926 | 20.6263 | 18.8074 | 17.3916 | 16.1389 | 12.04 | 11.7579 | 28.9347 | 28.3642 | 27.5011 | 26.5884 | 25.6821 | 24.7758 | 23.9126 | 21.8653 | 20.2453 | 18.8095
|  | BIRDHAM PRIMARY | EE |  |  |  |  | 12.5242 | 12.28 | 12.0074 | 30.0521 | 29.5889 | 29.1426 | 28.6921 | 28.2847 | 27.9142 | 25.5132 | 24.4911 | 23.6132 | 9.1389 | 8.8611 | 8.5516 | 24.9168 | 24.3968 | 23.8947 | 23.3779 | 22.9221 | 22.5147 | 19.8716 | 18.8716 | 18.0126 | 12.04 | 11.7579 | 29.0432 | 28.7053 | 28.1768 | 27.6368 | 27.0768 | 26.5884 | 26.1558 | 23.0137 | 21.8421 | 20.8337
|  | BIRDHAM PRIMARY | HT |  |  |  |  | 12.5579 | 12.2947 | 11.9263 | 29.8079 | 29.1584 | 28.4711 | 27.7942 | 27.0647 | 26.2858 | 24.4384 | 22.9953 | 21.7195 | 9.1832 | 8.8779 | 8.4463 | 24.5968 | 23.8189 | 23 | 22.1958 | 21.3926 | 20.6263 | 18.8074 | 17.3916 | 16.1389 | 12.0853 | 11.7747 | 28.9347 | 28.3642 | 27.5011 | 26.5884 | 25.6821 | 24.7758 | 23.9126 | 21.8653 | 20.2453 | 18.8095
|  | BIRDHAM PRIMARY | HE |  |  |  |  | 12.6779 | 12.4926 | 12.2758 | 30.3647 | 29.9374 | 29.5353 | 29.1395 | 28.7858 | 28.4679 | 26.7584 | 26.0532 | 25.4416 | 9.3316 | 9.1295 | 8.8895 | 25.3105 | 24.8337 | 24.3842 | 23.9411 | 23.5568 | 23.2179 | 21.0947 | 20.4063 | 19.8105 | 12.2379 | 12.0337 | 29.3905 | 29.1095 | 28.6263 | 28.1705 | 27.7179 | 27.3126 | 26.96 | 24.4168 | 23.5937 | 22.88
|  | BIRDHAM PRIMARY | FB |  |  |  |  | 12.8305 | 12.7 | 12.5958 | 30.8384 | 30.6837 | 30.5247 | 30.3658 | 30.2353 | 30.1163 | 29.6342 | 29.1111 | 28.67 | 9.5021 | 9.3495 | 9.2284 | 25.8063 | 25.6232 | 25.4347 | 25.2453 | 25.0926 | 24.9568 | 24.3979 | 23.7421 | 23.1789 | 12.4105 | 12.2547 | 29.7316 | 29.6074 | 29.4211 | 29.2295 | 29.0358 | 28.88 | 28.7432 | 28.1484 | 27.4042 | 26.7505
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM PRIMARY | MINIMUM HEADROOM | SU 56691 16683 | NO | YES | 0 | 21.1537 | 35.8284 | 35.2958 | 34.6358 | 33.8379 | 32.9168 | 31.9368 | 29.0737 | 28.0432 | 25.4526 | 23.6895 | 22.1263 | 14.8379 | 28.5842 | 27.9937 | 27.2705 | 26.4 | 25.3958 | 24.3221 | 21.0295 | 19.8926 | 17.0168 | 15.0474 | 13.2979 | 16.8589 | 31.0853 | 30.4958 | 29.7737 | 28.9042 | 27.9021 | 26.8305 | 23.5463 | 22.4116 | 19.5421 | 17.5758 | 15.8305
|  | BISHOPS WALTHAM PRIMARY | EE |  |  |  |  | 21.1537 | 35.8284 | 35.2958 | 34.7337 | 34.1579 | 33.5989 | 33.0274 | 31.5347 | 30.9747 | 26.9947 | 25.7863 | 24.7579 | 14.8379 | 28.5842 | 27.9937 | 27.3832 | 26.78 | 26.1958 | 25.5947 | 23.9084 | 23.3211 | 18.6758 | 17.2916 | 16.1105 | 16.8589 | 31.0853 | 30.4958 | 29.8863 | 29.2842 | 28.7 | 28.0989 | 26.4168 | 25.8295 | 21.1979 | 19.8168 | 18.6389
|  | BISHOPS WALTHAM PRIMARY | HT |  |  |  |  | 21.2263 | 35.9347 | 35.3526 | 34.6358 | 33.8379 | 32.9168 | 31.9368 | 29.0737 | 28.0432 | 25.4526 | 23.6895 | 22.1263 | 14.9242 | 28.7116 | 28.0642 | 27.2705 | 26.4 | 25.3958 | 24.3221 | 21.0295 | 19.8926 | 17.0168 | 15.0474 | 13.2979 | 16.9442 | 31.2126 | 30.5663 | 29.7737 | 28.9042 | 27.9021 | 26.8305 | 23.5463 | 22.4116 | 19.5421 | 17.5758 | 15.8305
|  | BISHOPS WALTHAM PRIMARY | HE |  |  |  |  | 21.4116 | 36.1874 | 35.7505 | 35.2663 | 34.7474 | 34.2589 | 33.7853 | 32.4011 | 31.9337 | 28.6474 | 27.8674 | 27.1979 | 15.1421 | 29.0095 | 28.5295 | 28.0105 | 27.4737 | 26.9684 | 26.48 | 24.9063 | 24.4274 | 20.5474 | 19.6368 | 18.8516 | 17.1611 | 31.5095 | 31.0295 | 30.5126 | 29.9758 | 29.4705 | 28.9821 | 27.4126 | 26.9337 | 23.0653 | 22.1568 | 21.3747
|  | BISHOPS WALTHAM PRIMARY | FB |  |  |  |  | 21.6874 | 36.5705 | 36.3558 | 36.1463 | 35.9579 | 35.7684 | 35.5874 | 35.4147 | 35.2379 | 34.3432 | 33.5084 | 32.7895 | 15.4389 | 29.4116 | 29.1705 | 28.9358 | 28.7295 | 28.5232 | 28.3253 | 28.1368 | 27.9442 | 26.9421 | 25.9947 | 25.1716 | 17.4579 | 31.9105 | 31.6705 | 31.4368 | 31.2305 | 31.0242 | 30.8274 | 30.6389 | 30.4463 | 29.4453 | 28.5011 | 27.68
NURSLING GSP | VELMORE BSP | BISHOPSTOKE PRIMARY | MINIMUM HEADROOM | SU 46463 18472 | NO | YES | 0 | 14.6224 | 14.6224 | 14.6203 | 14.6182 | 14.6182 | 14.6161 | 14.6118 | 14.6076 | 14.6024 | 14.5855 | 14.5718 | 14.5592 | 14.3468 | 14.3468 | 14.3447 | 14.3426 | 14.3416 | 14.3395 | 14.3353 | 14.3311 | 14.3247 | 14.3068 | 14.2911 | 14.2774 | 14.6358 | 14.6358 | 14.6337 | 14.6316 | 14.6316 | 14.6295 | 14.6284 | 14.6263 | 14.6232 | 14.6179 | 14.6116 | 14.6063
|  | BISHOPSTOKE PRIMARY | EE |  |  |  |  | 14.6224 | 14.6224 | 14.6203 | 14.6182 | 14.6182 | 14.6161 | 14.6118 | 14.6076 | 14.6024 | 14.5855 | 14.5718 | 14.5592 | 14.3468 | 14.3468 | 14.3447 | 14.3426 | 14.3416 | 14.3395 | 14.3353 | 14.3311 | 14.3247 | 14.3068 | 14.2911 | 14.2774 | 14.6358 | 14.6358 | 14.6337 | 14.6316 | 14.6316 | 14.6295 | 14.6284 | 14.6263 | 14.6232 | 14.6179 | 14.6126 | 14.6063
|  | BISHOPSTOKE PRIMARY | HT |  |  |  |  | 14.6224 | 14.6224 | 14.6213 | 14.6192 | 14.6192 | 14.6171 | 14.615 | 14.6097 | 14.6055 | 14.5897 | 14.5739 | 14.5613 | 14.3468 | 14.3468 | 14.3458 | 14.3437 | 14.3437 | 14.3405 | 14.3384 | 14.3342 | 14.3289 | 14.3111 | 14.2932 | 14.2795 | 14.6358 | 14.6358 | 14.6347 | 14.6326 | 14.6326 | 14.6305 | 14.6284 | 14.6263 | 14.6242 | 14.6179 | 14.6116 | 14.6063
|  | BISHOPSTOKE PRIMARY | HE |  |  |  |  | 14.6234 | 14.6224 | 14.6224 | 14.6203 | 14.6182 | 14.6182 | 14.6161 | 14.615 | 14.6129 | 14.6129 | 14.6045 | 14.5992 | 14.3479 | 14.3468 | 14.3468 | 14.3447 | 14.3426 | 14.3426 | 14.3405 | 14.3395 | 14.3374 | 14.3363 | 14.3279 | 14.3216 | 14.6358 | 14.6358 | 14.6358 | 14.6337 | 14.6316 | 14.6316 | 14.6295 | 14.6284 | 14.6263 | 14.6263 | 14.6232 | 14.6221
|  | BISHOPSTOKE PRIMARY | FB |  |  |  |  | 14.6245 | 14.6224 | 14.6224 | 14.6224 | 14.6213 | 14.6213 | 14.6213 | 14.6203 | 14.6192 | 14.6182 | 14.6097 | 14.6013 | 14.3489 | 14.3468 | 14.3468 | 14.3468 | 14.3458 | 14.3458 | 14.3458 | 14.3447 | 14.3437 | 14.3416 | 14.3332 | 14.3237 | 14.6368 | 14.6358 | 14.6358 | 14.6358 | 14.6347 | 14.6347 | 14.6347 | 14.6337 | 14.6326 | 14.6316 | 14.6284 | 14.6253
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE PRIMARY | MINIMUM HEADROOM | SU 45116 13082 | NO | YES | 0 | 13.1663 | 12.9926 | 12.7937 | 12.5189 | 12.1758 | 11.8274 | 11.4663 | 10.8842 | 10.16 | 8.2368 | 6.9895 | 5.9021 | 11.3189 | 10.9632 | 10.5179 | 9.8989 | 9.1421 | 8.6421 | 8.0779 | 7.38 | 6.5916 | 4.4716 | 3.0916 | 1.8905 | 12.1674 | 11.8368 | 11.4274 | 10.8568 | 10.16 | 9.6811 | 9.1463 | 8.4979 | 7.7716 | 5.8421 | 4.5895 | 3.4989
|  | BITTERNE PRIMARY | EE |  |  |  |  | 13.1663 | 12.9926 | 12.7958 | 12.5295 | 12.1758 | 11.8305 | 11.5063 | 11.1758 | 10.8526 | 10.2326 | 9.3916 | 8.7011 | 11.3189 | 10.9632 | 10.5832 | 10.1558 | 9.6305 | 9.1053 | 8.5758 | 8.1063 | 7.6558 | 6.6989 | 5.7453 | 4.96 | 12.1674 | 11.8368 | 11.4821 | 11.0789 | 10.5779 | 10.0789 | 9.5789 | 9.1284 | 8.6958 | 7.8453 | 6.9989 | 6.3063
|  | BITTERNE PRIMARY | HT |  |  |  |  | 13.1716 | 13.0074 | 12.7937 | 12.5189 | 12.1884 | 11.8274 | 11.4663 | 10.8842 | 10.16 | 8.2368 | 6.9895 | 5.9021 | 11.3642 | 11.0074 | 10.5179 | 9.8989 | 9.1421 | 8.6421 | 8.0779 | 7.38 | 6.5916 | 4.4716 | 3.0916 | 1.8905 | 12.2063 | 11.8768 | 11.4274 | 10.8568 | 10.16 | 9.6811 | 9.1463 | 8.4979 | 7.7716 | 5.8421 | 4.5895 | 3.4989
|  | BITTERNE PRIMARY | HE |  |  |  |  | 13.2 | 13.0337 | 12.8432 | 12.5832 | 12.2326 | 11.9011 | 11.5758 | 11.2505 | 10.9284 | 10.9516 | 10.9074 | 10.5611 | 11.5642 | 11.3032 | 11.0042 | 10.6463 | 10.1663 | 9.6968 | 9.2263 | 8.8284 | 8.4347 | 8.0853 | 7.5421 | 7.0411 | 12.3821 | 12.1347 | 11.8505 | 11.5063 | 11.0453 | 10.5958 | 10.1463 | 9.7579 | 9.3758 | 9.0789 | 8.6074 | 8.1737
|  | BITTERNE PRIMARY | FB |  |  |  |  | 13.3305 | 13.2537 | 13.1821 | 13.1032 | 13.0147 | 12.9263 | 12.84 | 12.7611 | 12.6737 | 12.36 | 12.1842 | 11.9989 | 11.7874 | 11.5895 | 11.4347 | 11.2737 | 11.0905 | 10.9021 | 10.7095 | 10.5253 | 10.3611 | 9.6926 | 9.08 | 8.5211 | 12.5232 | 12.4105 | 12.2684 | 12.1189 | 11.9495 | 11.7747 | 11.5979 | 11.4284 | 11.2747 | 10.6579 | 10.1074 | 9.6137
MINETY GSP | STRATTON (RESERVE) BSP | BLACK BOURTON PRIMARY | MINIMUM HEADROOM | SP 28349 03818 | NO | YES | 0 | 11.8537 | 11.7789 | 11.6305 | 11.4295 | 11.2337 | 11.0347 | 10.8495 | 10.64 | 10.4284 | 9.8284 | 9.3063 | 8.7611 | 9.6874 | 9.5674 | 9.4042 | 9.1842 | 8.9726 | 8.7589 | 8.5632 | 8.3368 | 8.1074 | 7.4495 | 6.8642 | 6.2474 | 10.9463 | 10.8263 | 10.6632 | 10.4432 | 10.2326 | 10.0189 | 9.8232 | 9.5968 | 9.3684 | 8.7116 | 8.1274 | 7.5126
|  | BLACK BOURTON PRIMARY | EE |  |  |  |  | 11.8537 | 11.7789 | 11.6684 | 11.5453 | 11.3947 | 11.2547 | 11.1105 | 10.9653 | 10.8221 | 10.5284 | 10.1905 | 9.8347 | 9.6874 | 9.5674 | 9.4484 | 9.3168 | 9.16 | 9.0126 | 8.86 | 8.7063 | 8.5558 | 8.2274 | 7.8432 | 7.4347 | 10.9463 | 10.8263 | 10.7074 | 10.5758 | 10.4189 | 10.2726 | 10.12 | 9.9663 | 9.8147 | 9.4874 | 9.1042 | 8.6979
|  | BLACK BOURTON PRIMARY | HT |  |  |  |  | 11.8589 | 11.7895 | 11.6305 | 11.4295 | 11.2337 | 11.0347 | 10.8495 | 10.64 | 10.4284 | 9.8284 | 9.3063 | 8.7611 | 9.6968 | 9.5779 | 9.4042 | 9.1842 | 8.9726 | 8.7589 | 8.5632 | 8.3368 | 8.1074 | 7.4495 | 6.8642 | 6.2474 | 10.9547 | 10.8368 | 10.6632 | 10.4432 | 10.2326 | 10.0189 | 9.8232 | 9.5968 | 9.3684 | 8.7116 | 8.1274 | 7.5126
|  | BLACK BOURTON PRIMARY | HE |  |  |  |  | 11.8853 | 11.8368 | 11.7789 | 11.7032 | 11.5916 | 11.4695 | 11.3495 | 11.2284 | 11.1126 | 10.9926 | 10.7684 | 10.5105 | 9.7874 | 9.7074 | 9.62 | 9.5158 | 9.3811 | 9.2547 | 9.1305 | 9.0053 | 8.8853 | 8.7484 | 8.4895 | 8.1884 | 11.0453 | 10.9663 | 10.8789 | 10.7747 | 10.64 | 10.5137 | 10.3895 | 10.2642 | 10.1442 | 10.0084 | 9.7505 | 9.4495
|  | BLACK BOURTON PRIMARY | FB |  |  |  |  | 11.9211 | 11.8926 | 11.8674 | 11.84 | 11.8084 | 11.7758 | 11.7242 | 11.6737 | 11.6221 | 11.4179 | 11.2021 | 10.9789 | 9.8526 | 9.7853 | 9.7347 | 9.6821 | 9.6232 | 9.5663 | 9.5105 | 9.4558 | 9.4 | 9.1768 | 8.9326 | 8.6768 | 11.1105 | 11.0432 | 10.9937 | 10.9411 | 10.8821 | 10.8253 | 10.7684 | 10.7147 | 10.6589 | 10.4358 | 10.1926 | 9.9379
MANNINGTON GSP | LYTCHETT BSP | BLANDFORD PRIMARY | MINIMUM HEADROOM | ST 88810 05536 | NO | YES | 0 | 37.6693 | 37.4693 | 37.244 | 36.9198 | 36.5714 | 36.2029 | 35.8587 | 35.5061 | 35.1577 | 34.2251 | 32.4293 | 30.8029 | 38.9798 | 38.5419 | 37.9187 | 37.0556 | 36.8387 | 35.6977 | 34.5619 | 33.3872 | 32.2145 | 29.2356 | 27.2345 | 25.4177 | 36.7966 | 36.3777 | 35.7851 | 34.9619 | 34.7366 | 33.6598 | 32.5787 | 31.4608 | 30.3451 | 27.5166 | 25.6198 | 23.8998
|  | BLANDFORD PRIMARY | EE |  |  |  |  | 37.6693 | 37.4693 | 37.2514 | 36.964 | 36.5714 | 36.2029 | 35.8587 | 35.5061 | 35.1577 | 35.4398 | 35.1177 | 32.824 | 38.9798 | 38.5419 | 38.064 | 37.5082 | 36.8387 | 36.204 | 35.5461 | 34.8893 | 34.2461 | 33.3882 | 31.9156 | 27.5619 | 36.7966 | 36.3777 | 35.9187 | 35.384 | 34.7366 | 34.1219 | 33.4882 | 32.8535 | 32.2324 | 31.4272 | 30.0419 | 25.9808
|  | BLANDFORD PRIMARY | HT |  |  |  |  | 37.6861 | 37.4966 | 37.244 | 36.9198 | 37.1608 | 36.7408 | 36.3187 | 35.8945 | 35.4745 | 34.2251 | 32.4293 | 30.8029 | 39.0387 | 38.5651 | 37.9187 | 37.0556 | 36.8387 | 35.6977 | 34.5619 | 33.3872 | 32.2145 | 29.2356 | 27.2345 | 25.4177 | 36.8524 | 36.4008 | 35.7851 | 34.9619 | 34.7461 | 33.6598 | 32.5787 | 31.4608 | 30.3451 | 27.5166 | 25.6198 | 23.8998
|  | BLANDFORD PRIMARY | HE |  |  |  |  | 37.7366 | 37.5545 | 37.3493 | 37.0714 | 36.6851 | 36.3377 | 35.9987 | 35.6535 | 35.3156 | 35.8914 | 35.7535 | 35.0177 | 39.2472 | 38.9103 | 38.5156 | 38.0293 | 37.4082 | 36.8366 | 36.2766 | 35.7198 | 35.1756 | 35.0324 | 33.9903 | 30.004 | 37.0493 | 36.724 | 36.344 | 35.8745 | 35.2703 | 34.7156 | 34.1724 | 33.6324 | 33.104 | 32.9798 | 32.0072 | 28.2977
|  | BLANDFORD PRIMARY | FB |  |  |  |  | 37.8651 | 37.7693 | 37.6851 | 37.5903 | 37.4861 | 37.3787 | 37.2766 | 37.1787 | 37.0756 | 36.6819 | 37.0703 | 36.9008 | 39.4798 | 39.2419 | 39.0429 | 38.8261 | 38.5893 | 38.3482 | 38.1082 | 37.8693 | 37.6229 | 36.5556 | 36.4314 | 35.5882 | 37.2735 | 37.0472 | 36.8577 | 36.6493 | 36.4229 | 36.1924 | 35.9619 | 35.7345 | 35.4987 | 34.4829 | 34.3629 | 33.5703
COWLEY GSP | WITNEY BSP | BLEDINGTON PRIMARY | MINIMUM HEADROOM | SP 25641 22580 | YES | YES | 0 | 14.9368 | 14.8916 | 14.8411 | 14.7684 | 14.6832 | 14.5905 | 14.4979 | 14.4074 | 14.3168 | 14.1053 | 13.9779 | 13.8653 | 15.4337 | 15.3389 | 15.2274 | 15.0642 | 14.9074 | 14.7505 | 14.6042 | 14.4263 | 14.2474 | 13.7158 | 13.2516 | 12.7874 | 14.7926 | 14.6989 | 14.5895 | 14.4295 | 14.2747 | 14.1189 | 13.9747 | 13.7989 | 13.6232 | 13.1011 | 12.6463 | 12.1926
|  | BLEDINGTON PRIMARY | EE |  |  |  |  | 14.9368 | 14.8916 | 14.8421 | 14.7779 | 14.6853 | 14.6021 | 14.5263 | 14.4453 | 14.3663 | 14.3042 | 14.2474 | 14.2021 | 15.4337 | 15.3389 | 15.2463 | 15.1411 | 15.0147 | 14.8968 | 14.7684 | 14.6368 | 14.5074 | 14.2263 | 13.9126 | 13.5874 | 14.7926 | 14.6989 | 14.6084 | 14.5042 | 14.3779 | 14.2611 | 14.1347 | 14.0042 | 13.8758 | 13.6011 | 13.2947 | 12.9789
|  | BLEDINGTON PRIMARY | HT |  |  |  |  | 14.9379 | 14.8968 | 14.8411 | 14.7684 | 14.6832 | 14.5905 | 14.4979 | 14.4074 | 14.3168 | 14.1053 | 13.9779 | 13.8653 | 15.4442 | 15.3537 | 15.2274 | 15.0642 | 14.9074 | 14.7505 | 14.6042 | 14.4263 | 14.2474 | 13.7158 | 13.2516 | 12.7874 | 14.8032 | 14.7147 | 14.5895 | 14.4295 | 14.2747 | 14.1189 | 13.9747 | 13.7989 | 13.6232 | 13.1011 | 12.6463 | 12.1926
|  | BLEDINGTON PRIMARY | HE |  |  |  |  | 14.9526 | 14.9126 | 14.8674 | 14.8053 | 14.7168 | 14.6411 | 14.5632 | 14.4863 | 14.4095 | 14.4116 | 14.3947 | 14.3821 | 15.5063 | 15.44 | 15.3716 | 15.2863 | 15.1747 | 15.0768 | 14.9779 | 14.8811 | 14.7842 | 14.7042 | 14.5095 | 14.2842 | 14.8642 | 14.7979 | 14.7305 | 14.6453 | 14.5347 | 14.4379 | 14.34 | 14.2432 | 14.1474 | 14.0695 | 13.8789 | 13.6611
|  | BLEDINGTON PRIMARY | FB |  |  |  |  | 14.98 | 14.96 | 14.9411 | 14.9221 | 14.8989 | 14.8768 | 14.8537 | 14.8337 | 14.8116 | 14.7305 | 14.6874 | 14.6589 | 15.56 | 15.5074 | 15.4674 | 15.4263 | 15.3811 | 15.3379 | 15.2926 | 15.2516 | 15.2084 | 15.0368 | 14.8358 | 14.6189 | 14.9168 | 14.8653 | 14.8253 | 14.7853 | 14.74 | 14.6979 | 14.6537 | 14.6126 | 14.5705 | 14.4011 | 14.2053 | 13.9937
FLEET-BRAMLEY GSP | ALTON BSP | BORDON PRIMARY | MINIMUM HEADROOM | SU 82256 35269 | NO | YES | 0 | 35.3411 | 34.96 | 34.4221 | 33.0874 | 31.3705 | 29.3558 | 27.3116 | 25.3937 | 23.6084 | 19.1632 | 16.6484 | 14.3747 | 30.0674 | 29.1568 | 27.5474 | 26.0053 | 24.2589 | 22.2084 | 20.02 | 17.8589 | 15.8537 | 10.84 | 8.0158 | 5.4558 | 30.7947 | 29.9 | 28.3263 | 26.8126 | 25.0989 | 22.9168 | 20.6126 | 18.4558 | 16.4526 | 11.4463 | 8.6242 | 6.0695
|  | BORDON PRIMARY | EE |  |  |  |  | 35.3411 | 34.96 | 34.4389 | 33.6737 | 32.5695 | 31.3242 | 30.0084 | 28.8832 | 27.9105 | 25.3516 | 23.5737 | 22.0221 | 30.0674 | 29.1568 | 27.6516 | 26.6095 | 25.4863 | 24.2242 | 22.8884 | 21.7463 | 20.7632 | 17.94 | 15.9011 | 14.1189 | 30.7947 | 29.9 | 28.4274 | 27.4021 | 26.2937 | 25.0495 | 23.7358 | 22.5337 | 21.48 | 18.5347 | 16.4989 | 14.72
|  | BORDON PRIMARY | HT |  |  |  |  | 35.3747 | 35.0116 | 34.4221 | 33.0874 | 31.3705 | 29.3558 | 27.3116 | 25.3937 | 23.6084 | 19.1632 | 16.6484 | 14.3747 | 30.1747 | 29.3084 | 27.5474 | 26.0053 | 24.2589 | 22.2084 | 20.02 | 17.8589 | 15.8537 | 10.84 | 8.0158 | 5.4558 | 30.9 | 30.0484 | 28.3263 | 26.8126 | 25.0989 | 22.9168 | 20.6126 | 18.4558 | 16.4526 | 11.4463 | 8.6242 | 6.0695
|  | BORDON PRIMARY | HE |  |  |  |  | 35.4579 | 35.1084 | 34.6179 | 34.1211 | 33.3042 | 32.1484 | 30.9495 | 29.9379 | 29.0789 | 27.4021 | 26.1705 | 25.0874 | 30.4221 | 29.6442 | 28.2547 | 27.3053 | 26.2484 | 25.0653 | 23.8495 | 22.8253 | 21.9579 | 20.2389 | 18.8316 | 17.5653 | 31.1421 | 30.3779 | 29.0168 | 28.0821 | 27.0389 | 25.8737 | 24.6758 | 23.6653 | 22.8074 | 20.8579 | 19.4253 | 18.1611
|  | BORDON PRIMARY | FB |  |  |  |  | 35.7453 | 35.5621 | 35.3674 | 35.2063 | 35.0074 | 34.8042 | 34.5947 | 34.4126 | 34.2326 | 32.8305 | 31.5642 | 30.5253 | 31.1253 | 30.6716 | 30.0937 | 29.7642 | 29.2905 | 28.7916 | 28.2463 | 27.8021 | 27.4168 | 25.7484 | 24.4579 | 23.3979 | 31.8316 | 31.3863 | 30.8211 | 30.4968 | 30.0316 | 29.5421 | 29.0084 | 28.5716 | 28.1937 | 26.5547 | 25.2916 | 24.2284
FLEET-BRAMLEY GSP | ALTON BSP | BORDON NORTH PRIMARY | MINIMUM HEADROOM | SU 82256 35269 | NO | YES | TBC | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6
|  | BORDON NORTH PRIMARY | EE |  |  |  |  | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6
|  | BORDON NORTH PRIMARY | HT |  |  |  |  | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6
|  | BORDON NORTH PRIMARY | HE |  |  |  |  | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6
|  | BORDON NORTH PRIMARY | FB |  |  |  |  | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 28.35 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | BOSCOMBE DOWN PRIMARY | MINIMUM HEADROOM | SU 17186 41044 | NO | YES | 0 | 29.3195 | 28.7479 | 28.5974 | 28.3921 | 28.1258 | 27.8226 | 27.5058 | 27.1574 | 26.7911 | 23.1184 | 22.3258 | 21.6163 | 21.0105 | 20.3368 | 20.1737 | 19.9516 | 19.6621 | 19.3305 | 18.9811 | 18.5937 | 18.1832 | 13.8305 | 12.9211 | 12.1032 | 22.6084 | 21.9789 | 21.82 | 21.6063 | 21.3263 | 21.0063 | 20.6716 | 20.3011 | 19.9095 | 15.8484 | 14.9884 | 14.2168
|  | BOSCOMBE DOWN PRIMARY | EE |  |  |  |  | 29.3195 | 28.7479 | 28.5974 | 28.4216 | 28.2163 | 28.0174 | 27.8226 | 27.63 | 27.4395 | 23.2963 | 22.7405 | 22.2489 | 21.0105 | 20.3368 | 20.1737 | 19.9853 | 19.7705 | 19.5621 | 19.3558 | 19.1516 | 18.9505 | 13.9768 | 13.3242 | 12.7463 | 22.6084 | 21.9789 | 21.82 | 21.6379 | 21.4274 | 21.2232 | 21.0211 | 20.8211 | 20.6242 | 16.0084 | 15.3968 | 14.8558
|  | BOSCOMBE DOWN PRIMARY | HT |  |  |  |  | 29.3468 | 28.7868 | 28.6184 | 28.3921 | 28.1258 | 27.8226 | 27.5058 | 27.1574 | 26.7911 | 23.1184 | 22.3258 | 21.6163 | 21.0421 | 20.3832 | 20.2011 | 19.9516 | 19.6621 | 19.3305 | 18.9811 | 18.5937 | 18.1832 | 13.8305 | 12.9211 | 12.1032 | 22.6389 | 22.0221 | 21.8453 | 21.6063 | 21.3263 | 21.0063 | 20.6716 | 20.3011 | 19.9095 | 15.8484 | 14.9884 | 14.2168
|  | BOSCOMBE DOWN PRIMARY | HE |  |  |  |  | 29.4205 | 28.8879 | 28.7711 | 28.6247 | 28.4374 | 28.2668 | 28.1016 | 27.9353 | 27.7753 | 23.8658 | 23.4511 | 23.0826 | 21.1284 | 20.5 | 20.3768 | 20.2232 | 20.0295 | 19.8516 | 19.6811 | 19.5084 | 19.3432 | 14.6295 | 14.1358 | 13.6937 | 22.7189 | 22.1316 | 22.0116 | 21.8611 | 21.6695 | 21.4947 | 21.3263 | 21.1568 | 20.9937 | 16.6242 | 16.1653 | 15.7537
|  | BOSCOMBE DOWN PRIMARY | FB |  |  |  |  | 30.7679 | 29.0079 | 28.9468 | 28.8826 | 28.8132 | 28.7447 | 28.6763 | 28.6153 | 28.5511 | 27.6689 | 27.3079 | 26.9984 | 22.7411 | 20.6263 | 20.5589 | 20.4874 | 20.4126 | 20.3368 | 20.2632 | 20.1958 | 20.1263 | 19.0905 | 18.6705 | 18.3074 | 24.2179 | 22.2558 | 22.1905 | 22.1221 | 22.0495 | 21.9768 | 21.9063 | 21.8411 | 21.7737 | 20.8042 | 20.4095 | 20.0695
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST PRIMARY | MINIMUM HEADROOM | SZ 11636 92447 | NO | YES | 0 | 32.1142 | 31.8205 | 31.4437 | 30.93 | 30.3395 | 29.5089 | 28.7132 | 27.8363 | 27.0247 | 25.0721 | 23.6226 | 22.31 | 26.4526 | 26.1305 | 25.72 | 25.1579 | 24.5137 | 23.5937 | 22.7126 | 21.7379 | 20.86 | 18.6947 | 17.0737 | 15.6042 | 28.9084 | 28.5863 | 28.1758 | 27.6137 | 26.9695 | 26.0484 | 25.1684 | 24.1926 | 23.3274 | 21.1611 | 19.5389 | 18.0684
|  | BOSCOMBE EAST PRIMARY | EE |  |  |  |  | 32.1142 | 31.8289 | 31.5374 | 31.1995 | 30.7932 | 30.3911 | 29.9742 | 29.5426 | 29.1289 | 28.1753 | 27.1121 | 26.1774 | 26.4526 | 26.1442 | 25.8305 | 25.4726 | 25.0484 | 24.6274 | 24.1863 | 23.7274 | 23.2905 | 22.2316 | 21.0189 | 19.9505 | 28.9084 | 28.6 | 28.2863 | 27.9284 | 27.5042 | 27.0821 | 26.6411 | 26.1832 | 25.7463 | 24.6989 | 23.4863 | 22.4168
|  | BOSCOMBE EAST PRIMARY | HT |  |  |  |  | 32.1532 | 31.8205 | 31.4437 | 30.93 | 30.3395 | 29.5089 | 28.7132 | 27.8363 | 27.0247 | 25.0721 | 23.6226 | 22.31 | 26.4968 | 26.1305 | 25.72 | 25.1579 | 24.5137 | 23.5937 | 22.7126 | 21.7379 | 20.86 | 18.6947 | 17.0737 | 15.6042 | 28.9526 | 28.5863 | 28.1758 | 27.6137 | 26.9695 | 26.0484 | 25.1684 | 24.1926 | 23.3274 | 21.1611 | 19.5389 | 18.0684
|  | BOSCOMBE EAST PRIMARY | HE |  |  |  |  | 32.2047 | 32.0553 | 31.8458 | 31.5489 | 31.1626 | 30.8005 | 30.4626 | 30.1132 | 29.7826 | 29.4132 | 28.7268 | 28.1184 | 26.6642 | 26.4326 | 26.1863 | 25.8779 | 25.48 | 25.1063 | 24.7579 | 24.3979 | 24.0579 | 23.6221 | 22.8284 | 22.1211 | 29.12 | 28.8895 | 28.6432 | 28.3347 | 27.9358 | 27.5621 | 27.2147 | 26.8537 | 26.5137 | 26.0779 | 25.2842 | 24.5758
|  | BOSCOMBE EAST PRIMARY | FB |  |  |  |  | 32.31 | 32.2332 | 32.1637 | 32.0321 | 31.8816 | 31.7332 | 31.59 | 31.4521 | 31.3121 | 30.6605 | 29.9584 | 29.3279 | 26.8495 | 26.6642 | 26.5221 | 26.3726 | 26.2105 | 26.0516 | 25.8968 | 25.7495 | 25.5989 | 24.8874 | 24.0937 | 23.3726 | 29.3063 | 29.1211 | 28.9779 | 28.8284 | 28.6663 | 28.5074 | 28.3526 | 28.2053 | 28.0558 | 27.3432 | 26.5495 | 25.8274
EALING GSP |  | BOSTON MANOR PRIMARY | MINIMUM HEADROOM | TQ 17043 78092 | NO | YES | 0 | 48.6093 | 48.5493 | 70.3747 | 70.2789 | 70.1589 | 70.0316 | 69.7042 | 69.1947 | 68.7063 | 67.8358 | 67.2453 | 66.6968 | 46.9493 | 46.8893 | 68.7147 | 68.6189 | 68.4989 | 68.2621 | 67.6853 | 67.1095 | 66.5558 | 65.5895 | 64.9295 | 64.3158 | 37.7503 | 37.3756 | 58.8463 | 58.4547 | 57.8316 | 57.2979 | 56.9505 | 56.6032 | 56.2684 | 55.6305 | 55.2032 | 54.8095
|  | BOSTON MANOR PRIMARY | EE |  |  |  |  | 48.6093 | 48.5493 | 70.3768 | 70.2832 | 70.1589 | 70.0358 | 69.92 | 69.8011 | 69.6821 | 69.1758 | 68.8032 | 68.46 | 46.9493 | 46.8893 | 68.7168 | 68.6232 | 68.4989 | 68.3747 | 68.2589 | 68.14 | 67.8842 | 67.1179 | 66.6916 | 66.2989 | 37.7608 | 37.4082 | 58.9147 | 58.5505 | 58.12 | 57.6716 | 57.4137 | 57.1621 | 56.9347 | 56.5168 | 56.2716 | 56.0495
|  | BOSTON MANOR PRIMARY | HT |  |  |  |  | 48.6114 | 48.5535 | 70.3747 | 70.2789 | 70.1611 | 70.0316 | 69.7042 | 69.1947 | 68.7063 | 67.8358 | 67.2453 | 66.6968 | 46.9514 | 46.8935 | 68.7147 | 68.6189 | 68.5011 | 68.2621 | 67.6853 | 67.1095 | 66.5558 | 65.5895 | 64.9295 | 64.3158 | 37.7503 | 37.3756 | 58.8463 | 58.4547 | 57.8316 | 57.2979 | 56.9505 | 56.6032 | 56.2684 | 55.6305 | 55.2032 | 54.8095
|  | BOSTON MANOR PRIMARY | HE |  |  |  |  | 48.6208 | 48.564 | 70.3958 | 70.3063 | 70.1842 | 70.0674 | 69.9526 | 69.8326 | 69.7168 | 69.7084 | 69.4853 | 69.2768 | 46.9608 | 46.904 | 68.7358 | 68.6463 | 68.5242 | 68.4074 | 68.2926 | 68.1726 | 68.0568 | 67.7221 | 67.4621 | 67.2168 | 37.8103 | 37.4766 | 59 | 58.6516 | 58.2316 | 57.7947 | 57.5526 | 57.3147 | 57.1032 | 56.8779 | 56.7442 | 56.6221
|  | BOSTON MANOR PRIMARY | FB |  |  |  |  | 48.6598 | 48.6272 | 70.4926 | 70.46 | 70.4221 | 70.3842 | 70.3484 | 70.3137 | 70.2768 | 70.1442 | 70.0684 | 70.02 | 46.9998 | 46.9672 | 68.8326 | 68.8 | 68.7621 | 68.7242 | 68.6884 | 68.6537 | 68.6168 | 68.4842 | 68.4084 | 68.36 | 37.9282 | 37.7556 | 59.4811 | 59.3337 | 59.1758 | 59.0168 | 58.9263 | 58.8347 | 58.7484 | 58.3526 | 58.1589 | 58
MANNINGTON GSP | BOURNEMOUTH BSP | BOURNE VALLEY PRIMARY | MINIMUM HEADROOM | SZ 06207 92415 | NO | YES | 0 | 33.5795 | 33.0005 | 32.2574 | 31.2426 | 30.0953 | 28.5068 | 26.9163 | 25.1826 | 23.4226 | 19.9974 | 17.6837 | 15.5774 | 31.2421 | 30.9368 | 30.3284 | 28.8653 | 27.4905 | 25.5189 | 23.5442 | 21.3653 | 19.1463 | 14.9316 | 12.0516 | 9.42 | 32.9958 | 32.1758 | 31.0463 | 29.5853 | 28.2126 | 26.2463 | 24.2758 | 22.1011 | 19.8874 | 15.6811 | 12.8084 | 10.1821
|  | BOURNE VALLEY PRIMARY | EE |  |  |  |  | 33.5795 | 33.0005 | 32.3689 | 31.6216 | 30.7458 | 29.9416 | 29.1437 | 28.2774 | 27.4268 | 25.6111 | 24.0384 | 22.6658 | 31.2421 | 30.9368 | 30.5526 | 29.5084 | 28.4126 | 27.5242 | 26.6242 | 25.6347 | 24.6684 | 22.2979 | 20.2495 | 18.4495 | 32.9958 | 32.1989 | 31.2695 | 30.2284 | 29.1337 | 28.2463 | 27.3474 | 26.3589 | 25.3926 | 23.0284 | 20.9853 | 19.1895
|  | BOURNE VALLEY PRIMARY | HT |  |  |  |  | 33.6353 | 33.0089 | 32.2574 | 31.2426 | 30.0953 | 28.5068 | 26.9163 | 25.1826 | 23.4226 | 19.9974 | 17.6837 | 15.5774 | 31.2621 | 30.9758 | 30.3284 | 28.8653 | 27.4905 | 25.5189 | 23.5442 | 21.3653 | 19.1463 | 14.9316 | 12.0516 | 9.42 | 33.0158 | 32.1758 | 31.0463 | 29.5853 | 28.2126 | 26.2463 | 24.2758 | 22.1011 | 19.8874 | 15.6811 | 12.8084 | 10.1821
|  | BOURNE VALLEY PRIMARY | HE |  |  |  |  | 33.8468 | 33.3595 | 32.8047 | 32.1174 | 31.29 | 30.6111 | 29.9363 | 29.2111 | 28.4437 | 27.4847 | 26.4563 | 25.55 | 31.3211 | 31.0284 | 30.7011 | 30.2505 | 29.3779 | 28.5905 | 27.7947 | 26.9116 | 26.0495 | 24.6958 | 23.3011 | 22.0611 | 33.0747 | 32.7821 | 32.0432 | 31.1179 | 30.0958 | 29.3095 | 28.5147 | 27.6316 | 26.7705 | 25.4221 | 24.0316 | 22.7947
|  | BOURNE VALLEY PRIMARY | FB |  |  |  |  | 34.2205 | 33.9289 | 33.6763 | 33.4342 | 33.1153 | 32.8311 | 32.5911 | 32.3532 | 32.1037 | 30.9353 | 29.8405 | 28.9184 | 31.5284 | 31.3821 | 31.2495 | 31.1021 | 30.9368 | 30.7716 | 30.6105 | 30.46 | 30.3 | 28.5989 | 27.1958 | 25.9874 | 33.2821 | 33.1358 | 33.0032 | 32.8558 | 32.4295 | 32.0242 | 31.7053 | 31.3789 | 31.04 | 29.32 | 27.92 | 26.7147
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON PRIMARY | MINIMUM HEADROOM | ST 77363 30262 | NO | YES | 0.21053 | 8.9916 | 8.6821 | 8.2095 | 7.6221 | 7.2821 | 6.5253 | 5.7263 | 4.4611 | 3.7305 | 1.8874 | 0.59263 | -0.56737 | 3.08 | 2.7695 | 2.2968 | 1.7095 | 1.3695 | 0.73895 | -0.06 | -1.3253 | -2.0558 | -3.8989 | -5.1947 | -6.3537 | 7.0526 | 6.7242 | 6.2063 | 5.5453 | 5.1937 | 4.3063 | 3.4063 | 1.9432 | 1.1221 | -0.95895 | -2.4326 | -3.7558
|  | BOURTON PRIMARY | EE |  |  |  |  | 8.9916 | 8.6821 | 8.2453 | 7.8126 | 7.2821 | 6.7495 | 6.2305 | 5.5295 | 5.1084 | 4.5411 | 3.6484 | 2.8747 | 3.08 | 2.7695 | 2.3337 | 1.9 | 1.3695 | 0.83789 | 0.31789 | -0.38316 | -0.80421 | -1.2442 | -2.1368 | -2.9116 | 7.0526 | 6.7242 | 6.2484 | 5.7705 | 5.1937 | 4.6137 | 4.04 | 3.2505 | 2.7979 | 2.1137 | 1.0737 | 0.16737
|  | BOURTON PRIMARY | HT |  |  |  |  | 9.0389 | 8.7274 | 8.2095 | 7.6221 | 7.3179 | 6.5253 | 5.7263 | 4.4611 | 3.7305 | 1.8874 | 0.59263 | -0.56737 | 3.1274 | 2.8147 | 2.2968 | 1.7095 | 1.5326 | 0.73895 | -0.06 | -1.3253 | -2.0558 | -3.8989 | -5.1947 | -6.3537 | 7.1042 | 6.7726 | 6.2063 | 5.5453 | 5.2 | 4.3063 | 3.4063 | 1.9432 | 1.1221 | -0.95895 | -2.4326 | -3.7558
|  | BOURTON PRIMARY | HE |  |  |  |  | 9.1853 | 8.9505 | 8.5789 | 8.1979 | 7.7063 | 7.2295 | 6.7611 | 6.1105 | 5.7432 | 5.6021 | 4.9832 | 4.4389 | 3.2737 | 3.0389 | 2.6674 | 2.2863 | 1.7947 | 1.3179 | 0.84842 | 0.19895 | -0.16842 | -0.18316 | -0.80316 | -1.3474 | 7.2642 | 7.0179 | 6.6211 | 6.22 | 5.6905 | 5.1705 | 4.6579 | 3.9295 | 3.54 | 3.3274 | 2.5905 | 1.94
|  | BOURTON PRIMARY | FB |  |  |  |  | 9.3632 | 9.2 | 9.0305 | 8.8811 | 8.6884 | 8.4926 | 8.2926 | 8.1432 | 7.9874 | 7.3147 | 7.0842 | 6.5695 | 3.4505 | 3.2884 | 3.1189 | 2.9695 | 2.7768 | 2.58 | 2.3811 | 2.2316 | 2.0747 | 1.4032 | 1.2979 | 0.78421 | 7.4505 | 7.2758 | 7.0937 | 6.9347 | 6.7274 | 6.5168 | 6.2947 | 6.1284 | 5.9547 | 5.1979 | 4.9126 | 4.3105
MANNINGTON GSP | WAREHAM BSP | BOVINGTON PRIMARY | MINIMUM HEADROOM | SY 83933 87831 | NO | YES | 0 | 7.6347 | 7.52 | 7.3621 | 7.1421 | 6.8768 | 6.5874 | 6.3 | 6.0074 | 3.7874 | 3.0653 | 2.5895 | 2.1632 | 5.2042 | 5.0779 | 4.9 | 4.6547 | 4.3589 | 4.0347 | 3.7137 | 3.3853 | 0.77684 | -0.034737 | -0.57158 | -1.0526 | 5.6189 | 5.4937 | 5.3189 | 5.0758 | 4.7832 | 4.4632 | 4.1453 | 3.8211 | 1.2432 | 0.43368 | -0.10211 | -0.58211
|  | BOVINGTON PRIMARY | EE |  |  |  |  | 7.6347 | 7.52 | 7.3947 | 7.2495 | 7.0737 | 6.9053 | 6.7411 | 6.5747 | 5.4474 | 5.0621 | 4.7232 | 4.4295 | 5.2042 | 5.0779 | 4.9389 | 4.7811 | 4.5926 | 4.4105 | 4.2337 | 4.0537 | 2.7368 | 2.2916 | 1.9032 | 1.5632 | 5.6189 | 5.4937 | 5.3568 | 5.2011 | 5.0126 | 4.8326 | 4.6568 | 4.4779 | 3.1821 | 2.7421 | 2.36 | 2.0253
|  | BOVINGTON PRIMARY | HT |  |  |  |  | 7.6505 | 7.5295 | 7.3621 | 7.1421 | 6.8768 | 6.5874 | 6.3 | 6.0074 | 3.7874 | 3.0653 | 2.5895 | 2.1632 | 5.2221 | 5.0874 | 4.9 | 4.6547 | 4.3589 | 4.0347 | 3.7137 | 3.3853 | 0.77684 | -0.034737 | -0.57158 | -1.0526 | 5.6368 | 5.5032 | 5.3189 | 5.0758 | 4.7832 | 4.4632 | 4.1453 | 3.8211 | 1.2432 | 0.43368 | -0.10211 | -0.58211
|  | BOVINGTON PRIMARY | HE |  |  |  |  | 7.7021 | 7.6147 | 7.5116 | 7.3832 | 7.22 | 7.0695 | 6.9211 | 6.7737 | 5.6653 | 5.4337 | 5.1937 | 4.9832 | 5.2811 | 5.1863 | 5.0737 | 4.9358 | 4.7611 | 4.6 | 4.4421 | 4.2832 | 2.9884 | 2.7126 | 2.4326 | 2.1842 | 5.6947 | 5.6011 | 5.4895 | 5.3526 | 5.1789 | 5.0189 | 4.8621 | 4.7042 | 3.4295 | 3.1589 | 2.8832 | 2.6389
|  | BOVINGTON PRIMARY | FB |  |  |  |  | 7.7642 | 7.7032 | 7.6526 | 7.5979 | 7.5368 | 7.4758 | 7.4126 | 7.3537 | 7.2905 | 7.0221 | 6.8 | 6.6032 | 5.3484 | 5.28 | 5.2242 | 5.1632 | 5.0968 | 5.0284 | 4.9589 | 4.8926 | 4.8232 | 4.5221 | 4.2684 | 4.0411 | 5.7621 | 5.6947 | 5.6389 | 5.5789 | 5.5126 | 5.4453 | 5.3768 | 5.3116 | 5.2421 | 4.9442 | 4.6947 | 4.4705
AMERSHAM GSP | LOUDWATER BSP | BOWERDEAN PRIMARY | MINIMUM HEADROOM | SU 87718 93880 | NO | YES | 0 | 22.5958 | 21.4768 | 20.3916 | 18.9937 | 17.5126 | 15.9516 | 14.6368 | 13.3011 | 11.9737 | 8.8305 | 6.8095 | 5.0463 | 20.1863 | 18.9411 | 17.7442 | 16.2095 | 14.5937 | 12.8947 | 11.48 | 10.04 | 8.6074 | 5.2137 | 3.0253 | 1.1147 | 22.0989 | 21.1453 | 20.2042 | 18.7189 | 16.9979 | 15.1905 | 13.6979 | 12.1747 | 10.6611 | 7.0716 | 4.7505 | 2.7253
|  | BOWERDEAN PRIMARY | EE |  |  |  |  | 22.5958 | 21.4768 | 20.3916 | 19.1895 | 18.0389 | 16.9389 | 16.0916 | 15.2274 | 14.3789 | 12.9189 | 11.6547 | 10.6032 | 20.1863 | 18.9411 | 17.7442 | 16.4316 | 15.2042 | 14.0347 | 13.1526 | 12.2484 | 11.3653 | 9.7368 | 8.3242 | 7.1453 | 22.0989 | 21.1453 | 20.2042 | 18.9337 | 17.6726 | 16.4505 | 15.54 | 14.6074 | 13.6947 | 11.9347 | 10.4063 | 9.1295
|  | BOWERDEAN PRIMARY | HT |  |  |  |  | 22.7063 | 21.6358 | 20.4411 | 18.9937 | 17.5126 | 15.9516 | 14.6368 | 13.3011 | 11.9737 | 8.8305 | 6.8095 | 5.0463 | 20.3116 | 19.1221 | 17.8032 | 16.2095 | 14.5937 | 12.8947 | 11.48 | 10.04 | 8.6074 | 5.2137 | 3.0253 | 1.1147 | 22.1874 | 21.2737 | 20.2432 | 18.7189 | 16.9979 | 15.1905 | 13.6979 | 12.1747 | 10.6611 | 7.0716 | 4.7505 | 2.7253
|  | BOWERDEAN PRIMARY | HE |  |  |  |  | 22.9832 | 22.0116 | 21.0558 | 19.9642 | 18.8863 | 17.8779 | 17.1253 | 16.3526 | 15.5989 | 14.9716 | 14.2568 | 13.6663 | 20.6242 | 19.5484 | 18.4989 | 17.3126 | 16.1684 | 15.1 | 14.3263 | 13.5305 | 12.7537 | 12.0211 | 11.2042 | 10.5253 | 22.4189 | 21.5842 | 20.7505 | 19.7737 | 18.6547 | 17.6084 | 16.8242 | 16.0105 | 15.2158 | 14.4011 | 13.5021 | 12.7558
|  | BOWERDEAN PRIMARY | FB |  |  |  |  | 23.6021 | 23.0326 | 22.5832 | 22.12 | 21.7116 | 21.3095 | 21.0221 | 20.7368 | 20.4421 | 19.2116 | 18.2432 | 17.4642 | 21.3011 | 20.6642 | 20.1642 | 19.6516 | 19.2053 | 18.7653 | 18.4579 | 18.1516 | 17.8358 | 16.5032 | 15.4337 | 14.5632 | 22.9621 | 22.4811 | 22.0968 | 21.7 | 21.3421 | 20.9884 | 20.7274 | 20.4705 | 20.2032 | 18.9853 | 17.9232 | 16.9811
FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL PRIMARY | MINIMUM HEADROOM | SU 86075 69397 | NO | YES | 0.11684 | 90.2326 | 90.0958 | 89.9737 | 89.8474 | 89.7032 | 100.1895 | 99.7389 | 98.6947 | 96.1579 | 90.5811 | 88.6242 | 86.8947 | 80.4968 | 80.3116 | 80.1474 | 79.9947 | 79.8126 | 93.5316 | 93.0905 | 91.3642 | 88.4505 | 82.0558 | 79.8674 | 77.9316 | 82.1579 | 82.0232 | 81.9032 | 81.7779 | 81.6347 | 91.7474 | 89.2884 | 86.8158 | 83.9021 | 77.5053 | 75.3158 | 73.3789
|  | BRACKNELL PRIMARY | EE |  |  |  |  | 101.88 | 101.6642 | 101.4137 | 101.0779 | 100.6295 | 100.1895 | 99.7737 | 99.3189 | 97.7926 | 92.4537 | 91.0579 | 89.8737 | 95.2232 | 95.0074 | 94.7568 | 94.4211 | 93.9716 | 93.5316 | 93.1168 | 92.6926 | 90.3621 | 84.1221 | 82.5284 | 81.1695 | 95.0947 | 94.8779 | 94.6284 | 94.2926 | 93.8432 | 93.2095 | 90.8558 | 88.5874 | 85.8137 | 79.5726 | 77.9779 | 76.6179
|  | BRACKNELL PRIMARY | HT |  |  |  |  | 101.8968 | 101.6926 | 101.4253 | 101.08 | 100.6632 | 100.2053 | 99.7389 | 98.6947 | 96.1579 | 90.5811 | 88.6242 | 86.8947 | 95.24 | 95.0358 | 94.7684 | 94.4232 | 94.0063 | 93.5484 | 93.0905 | 91.3642 | 88.4505 | 82.0558 | 79.8674 | 77.9316 | 95.1116 | 94.9074 | 94.6389 | 94.2947 | 93.5874 | 91.7474 | 89.2884 | 86.8158 | 83.9021 | 77.5053 | 75.3158 | 73.3789
|  | BRACKNELL PRIMARY | HE |  |  |  |  | 101.9179 | 101.6979 | 101.4463 | 101.1042 | 100.6358 | 100.1979 | 99.7716 | 99.3411 | 98.54 | 94.0453 | 93.1253 | 92.3484 | 95.2611 | 95.0411 | 94.7895 | 94.4474 | 93.9789 | 93.5411 | 93.1147 | 92.6842 | 91.2558 | 85.9432 | 84.8737 | 83.9674 | 95.1326 | 94.9126 | 94.6611 | 94.3189 | 93.8505 | 93.4126 | 91.6042 | 89.4105 | 86.7084 | 81.3947 | 80.3242 | 79.4179
|  | BRACKNELL PRIMARY | FB |  |  |  |  | 90.2326 | 90.0958 | 89.9737 | 89.8474 | 89.7032 | 101.5021 | 101.38 | 101.2642 | 101.1421 | 100.6084 | 99.8926 | 99.0832 | 80.4968 | 80.3116 | 80.1474 | 79.9947 | 79.8126 | 94.8453 | 94.7232 | 94.6074 | 94.4853 | 93.7105 | 92.5726 | 91.6432 | 82.1579 | 82.0232 | 81.9032 | 81.7779 | 81.6347 | 94.7168 | 94.5947 | 94.4789 | 93.7179 | 89.1632 | 88.0253 | 87.0958
MELKSHAM GSP | NORRINGTON BSP | BRADFORD-ON-AVON PRIMARY | MINIMUM HEADROOM | ST 81260 60564 | NO | YES | 0 | 24.4126 | 24.0705 | 23.7284 | 23.3105 | 22.6611 | 20.4179 | 19.7716 | 19.0611 | 18.32 | 16.2895 | 14.6663 | 13.1842 | 21.38 | 21.0095 | 20.64 | 20.1968 | 19.4905 | 16.9021 | 16.2053 | 15.4305 | 14.6189 | 12.3663 | 10.54 | 8.8663 | 22.4747 | 22.1011 | 21.7274 | 21.2832 | 20.5695 | 17.9421 | 17.24 | 16.4579 | 15.6389 | 13.36 | 11.5074 | 9.8126
|  | BRADFORD-ON-AVON PRIMARY | EE |  |  |  |  | 24.4126 | 24.0705 | 23.7284 | 23.3263 | 22.8421 | 21.4884 | 21.0305 | 20.5684 | 20.1147 | 19.0905 | 17.9263 | 16.8979 | 21.38 | 21.0095 | 20.64 | 20.2126 | 19.7095 | 18.1695 | 17.6853 | 17.1989 | 16.72 | 15.5526 | 14.2168 | 13.0347 | 22.4747 | 22.1011 | 21.7274 | 21.2979 | 20.7916 | 19.2284 | 18.7411 | 18.2505 | 17.7705 | 16.5842 | 15.2274 | 14.0253
|  | BRADFORD-ON-AVON PRIMARY | HT |  |  |  |  | 24.4832 | 24.1737 | 23.7968 | 23.3105 | 22.6611 | 20.4179 | 19.7716 | 19.0611 | 18.32 | 16.2895 | 14.6663 | 13.1842 | 21.4621 | 21.1253 | 20.72 | 20.1968 | 19.4905 | 16.9021 | 16.2053 | 15.4305 | 14.6189 | 12.3663 | 10.54 | 8.8663 | 22.5579 | 22.2189 | 21.8105 | 21.2832 | 20.5695 | 17.9421 | 17.24 | 16.4579 | 15.6389 | 13.36 | 11.5074 | 9.8126
|  | BRADFORD-ON-AVON PRIMARY | HE |  |  |  |  | 24.6484 | 24.3926 | 24.1263 | 23.7884 | 23.3453 | 22.0926 | 21.6653 | 21.2779 | 20.8989 | 20.4863 | 19.6926 | 18.9821 | 21.6463 | 21.3789 | 21.0958 | 20.7432 | 20.2874 | 18.8642 | 18.4168 | 18.0168 | 17.6263 | 17.1337 | 16.2084 | 15.3758 | 22.7484 | 22.4758 | 22.1916 | 21.8379 | 21.38 | 19.9368 | 19.4863 | 19.0863 | 18.6947 | 18.1916 | 17.2495 | 16.4032
|  | BRADFORD-ON-AVON PRIMARY | FB |  |  |  |  | 24.8537 | 24.6674 | 24.5253 | 24.3695 | 24.2084 | 24.0453 | 23.8663 | 23.6916 | 23.5368 | 22.8347 | 22.0726 | 21.4021 | 21.8621 | 21.6611 | 21.5074 | 21.34 | 21.1653 | 20.9884 | 20.7926 | 20.6011 | 20.4347 | 19.6621 | 18.7926 | 18.0189 | 22.9705 | 22.7621 | 22.6053 | 22.4358 | 22.2589 | 22.0811 | 21.8832 | 21.6905 | 21.5221 | 20.7421 | 19.8611 | 19.0758
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BRAMLEY GREEN PRIMARY | MINIMUM HEADROOM | SU 67431 58511 | NO | YES | 0 | 16.4726 | 16.4084 | 16.3358 | 16.2221 | 15.9937 | 15.7389 | 15.3147 | 14.8853 | 14.46 | 13.7189 | 13.3411 | 12.92 | 15.8579 | 15.7853 | 15.5895 | 15.2789 | 15.0284 | 14.7505 | 14.2695 | 13.7832 | 13.2989 | 12.4716 | 12.0558 | 11.5821 | 15.7516 | 15.5168 | 15.2568 | 14.9432 | 14.6916 | 14.4116 | 13.9263 | 13.4358 | 12.9474 | 12.1137 | 11.6947 | 11.2179
|  | BRAMLEY GREEN PRIMARY | EE |  |  |  |  | 16.4726 | 16.4084 | 16.3389 | 16.2453 | 16.1179 | 15.9558 | 15.8011 | 15.4105 | 15.0232 | 14.2895 | 14.0632 | 13.7768 | 15.8579 | 15.7853 | 15.5895 | 15.3537 | 15.1789 | 15.0074 | 14.8442 | 14.4021 | 13.9621 | 13.1032 | 12.8463 | 12.5158 | 15.7516 | 15.5168 | 15.2568 | 15.0189 | 14.8432 | 14.6716 | 14.5084 | 14.0621 | 13.6179 | 12.7484 | 12.4895 | 12.1558
|  | BRAMLEY GREEN PRIMARY | HT |  |  |  |  | 16.4737 | 16.4147 | 16.3358 | 16.2221 | 15.9937 | 15.7389 | 15.3147 | 14.8853 | 14.46 | 13.7189 | 13.3411 | 12.92 | 15.86 | 15.7937 | 15.5937 | 15.2789 | 15.0284 | 14.7505 | 14.2695 | 13.7832 | 13.2989 | 12.4716 | 12.0558 | 11.5821 | 15.7768 | 15.5568 | 15.2611 | 14.9432 | 14.6916 | 14.4116 | 13.9263 | 13.4358 | 12.9474 | 12.1137 | 11.6947 | 11.2179
|  | BRAMLEY GREEN PRIMARY | HE |  |  |  |  | 16.4863 | 16.4263 | 16.3621 | 16.2716 | 16.1463 | 16.0337 | 15.9221 | 15.6905 | 15.3716 | 14.7189 | 14.5874 | 14.4695 | 15.8758 | 15.8084 | 15.7368 | 15.5368 | 15.3789 | 15.2337 | 15.0926 | 14.7274 | 14.3684 | 13.5895 | 13.4358 | 13.2979 | 15.8421 | 15.6432 | 15.4158 | 15.2032 | 15.0453 | 14.9 | 14.7589 | 14.3905 | 14.0284 | 13.24 | 13.0853 | 12.9453
|  | BRAMLEY GREEN PRIMARY | FB |  |  |  |  | 16.5305 | 16.5032 | 16.4789 | 16.4505 | 16.4189 | 16.3884 | 16.3579 | 16.3295 | 16.2989 | 15.7358 | 15.5495 | 15.4 | 15.9211 | 15.8895 | 15.8611 | 15.8295 | 15.7968 | 15.7653 | 15.7326 | 15.6926 | 15.5042 | 14.7095 | 14.4979 | 14.3284 | 15.9263 | 15.8074 | 15.6979 | 15.6032 | 15.54 | 15.4789 | 15.4179 | 15.3611 | 15.1705 | 14.3674 | 14.1547 | 13.9832
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD PRIMARY | MINIMUM HEADROOM | SZ 64712 98665 | NO | YES | 0.057895 | 27.8574 | 27.5711 | 27.2774 | 26.8447 | 26.4005 | 25.8616 | 25.3121 | 24.7447 | 24.1742 | 22.5679 | 21.3837 | 20.3142 | 29.8042 | 29.5842 | 29.2326 | 28.5337 | 27.9211 | 27.1053 | 26.2768 | 25.3853 | 24.4895 | 21.7137 | 19.5232 | 17.5547 | 31.6337 | 31.4411 | 31.2179 | 30.9105 | 30.4853 | 30.0926 | 29.7105 | 29.3189 | 28.48 | 25.7063 | 23.5189 | 21.5537
|  | BRANDON ROAD PRIMARY | EE |  |  |  |  | 27.8574 | 27.5711 | 27.2784 | 26.9205 | 26.49 | 26.0668 | 25.6416 | 25.2037 | 24.7689 | 24.0489 | 23.2742 | 22.6226 | 29.8042 | 29.5842 | 29.2326 | 28.7211 | 28.1968 | 27.6758 | 27.1137 | 26.5411 | 25.9747 | 24.5705 | 22.9305 | 21.5284 | 31.6337 | 31.4526 | 31.2505 | 30.9726 | 30.5895 | 30.2179 | 29.8642 | 29.4958 | 29.1305 | 28.5589 | 26.9211 | 25.5211
|  | BRANDON ROAD PRIMARY | HT |  |  |  |  | 27.8889 | 27.6163 | 27.2774 | 26.8447 | 26.4005 | 25.8616 | 25.3121 | 24.7447 | 24.1742 | 22.5679 | 21.3837 | 20.3142 | 29.8211 | 29.6116 | 29.2347 | 28.5337 | 27.9211 | 27.1053 | 26.2768 | 25.3853 | 24.4895 | 21.7137 | 19.5232 | 17.5547 | 31.6411 | 31.4716 | 31.2484 | 30.9547 | 30.5989 | 30.2032 | 29.7958 | 29.3695 | 28.48 | 25.7063 | 23.5189 | 21.5537
|  | BRANDON ROAD PRIMARY | HE |  |  |  |  | 27.9405 | 27.67 | 27.3847 | 27.0226 | 26.5658 | 26.1416 | 25.73 | 25.31 | 24.8984 | 24.7742 | 24.4395 | 24.0816 | 29.8389 | 29.6137 | 29.3674 | 29.0389 | 28.6021 | 28.1368 | 27.6674 | 27.1926 | 26.7284 | 26.3568 | 25.5789 | 24.6779 | 31.6389 | 31.4411 | 31.2179 | 30.9105 | 30.4853 | 30.0926 | 29.7105 | 29.3189 | 28.9358 | 28.9389 | 28.8358 | 28.6674
|  | BRANDON ROAD PRIMARY | FB |  |  |  |  | 28.1174 | 27.9363 | 27.7889 | 27.6311 | 27.4689 | 27.2995 | 27.1395 | 26.99 | 26.8311 | 26.2142 | 25.7458 | 25.3026 | 29.9884 | 29.8484 | 29.7274 | 29.5947 | 29.4537 | 29.3074 | 29.1674 | 29.0095 | 28.7905 | 27.8811 | 27.0232 | 26.0611 | 31.7726 | 31.6568 | 31.5516 | 31.4347 | 31.3053 | 31.1737 | 31.0463 | 30.9284 | 30.8011 | 30.3358 | 30.0705 | 29.8747
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | BRAYWICK ROAD PRIMARY | MINIMUM HEADROOM | SU 88887 80726 | NO | YES | 0 | 33.9089 | 33.4826 | 32.9268 | 31.5605 | 29.7816 | 28.0279 | 26.9784 | 26.1026 | 25.1626 | 21.5879 | 20.3974 | 19.3279 | 30.8674 | 30.7326 | 30.5747 | 29.8305 | 27.7621 | 25.7263 | 24.5305 | 23.5411 | 22.4747 | 18.3347 | 16.9916 | 15.7821 | 31.6158 | 31.4358 | 31.2158 | 30.82 | 29.5863 | 27.5305 | 26.3242 | 25.3253 | 24.2495 | 20.0684 | 18.7147 | 17.4937
|  | BRAYWICK ROAD PRIMARY | EE |  |  |  |  | 33.9089 | 33.4826 | 32.9268 | 31.5616 | 29.7974 | 28.1995 | 27.4447 | 27.0732 | 26.7079 | 24.8016 | 23.8311 | 23.1026 | 30.8674 | 30.7326 | 30.58 | 29.8305 | 27.7811 | 25.9274 | 25.0768 | 24.6821 | 24.2958 | 22.0589 | 20.9326 | 20.0884 | 31.6158 | 31.4358 | 31.22 | 30.8326 | 29.6053 | 27.7337 | 26.8737 | 26.4779 | 26.0916 | 23.8305 | 22.6926 | 21.84
|  | BRAYWICK ROAD PRIMARY | HT |  |  |  |  | 33.9574 | 33.5468 | 32.93 | 31.5605 | 29.7816 | 28.0279 | 26.9784 | 26.1026 | 25.1626 | 21.5879 | 20.3974 | 19.3279 | 30.8726 | 30.7442 | 30.5747 | 29.8316 | 27.7621 | 25.7263 | 24.5305 | 23.5411 | 22.4747 | 18.3347 | 16.9916 | 15.7821 | 31.6284 | 31.4558 | 31.2158 | 30.82 | 29.5863 | 27.5305 | 26.3242 | 25.3253 | 24.2495 | 20.0684 | 18.7147 | 17.4937
|  | BRAYWICK ROAD PRIMARY | HE |  |  |  |  | 34.0742 | 33.7089 | 33.2058 | 31.8847 | 30.15 | 28.5858 | 27.8879 | 27.5679 | 27.2511 | 25.8279 | 25.1395 | 24.6511 | 30.8937 | 30.7632 | 30.6137 | 30.2084 | 28.1937 | 26.3811 | 25.5979 | 25.2653 | 24.9358 | 23.2379 | 22.4253 | 21.8495 | 31.6642 | 31.4968 | 31.2916 | 30.9126 | 30.0232 | 28.1916 | 27.4021 | 27.0684 | 26.7379 | 25.0211 | 24.1989 | 23.6158
|  | BRAYWICK ROAD PRIMARY | FB |  |  |  |  | 34.3826 | 34.1595 | 33.9205 | 33.3668 | 32.6816 | 32.0079 | 31.6942 | 31.5542 | 31.4279 | 30.8237 | 29.5068 | 29.0142 | 30.9947 | 30.9316 | 30.8737 | 30.8095 | 30.7379 | 30.3053 | 29.9453 | 29.7916 | 29.6547 | 28.9832 | 27.4411 | 26.8716 | 31.7979 | 31.7095 | 31.6232 | 31.4821 | 31.3137 | 31.1484 | 31.0389 | 30.9621 | 30.8842 | 30.5737 | 29.2632 | 28.6874
EALING GSP | EALING BSP | BRENTFORD PRIMARY | MINIMUM HEADROOM | TQ 17659 78277 | NO | YES | 0 | 38.0242 | 37.8158 | 37.4947 | 36.7189 | 34.3958 | 32.0032 | 29.2558 | 26.3232 | 23.4537 | 18.4653 | 16.4937 | 14.7789 | 35.84 | 35.2421 | 33.7495 | 32.2989 | 29.7811 | 27.1442 | 23.9663 | 20.5695 | 17.2474 | 11.5326 | 9.3242 | 7.4063 | 35.1147 | 34.5095 | 33.8021 | 32.5516 | 29.9589 | 27.2926 | 24.2242 | 20.9453 | 17.7379 | 12.2084 | 10.0589 | 8.1926
|  | BRENTFORD PRIMARY | EE |  |  |  |  | 38.0263 | 37.8495 | 37.5505 | 37.1379 | 35.82 | 34.2221 | 32.4084 | 30.4284 | 28.5895 | 22.9168 | 21.6442 | 20.6032 | 35.8421 | 35.6642 | 34.2411 | 32.7547 | 31.3432 | 29.6232 | 27.6663 | 25.4042 | 23.2937 | 16.6337 | 15.1737 | 13.9811 | 35.1568 | 34.7042 | 34.0021 | 33.0221 | 31.5747 | 29.8074 | 27.7947 | 25.5937 | 23.5526 | 17.1432 | 15.7316 | 14.5768
|  | BRENTFORD PRIMARY | HT |  |  |  |  | 38.0242 | 37.8158 | 37.4947 | 36.7189 | 34.3958 | 32.0032 | 29.2558 | 26.3232 | 23.4537 | 18.4653 | 16.4937 | 14.7789 | 35.84 | 35.2421 | 33.7495 | 32.2989 | 29.7811 | 27.1442 | 23.9663 | 20.5695 | 17.2474 | 11.5326 | 9.3242 | 7.4063 | 35.1147 | 34.5095 | 33.8021 | 32.5516 | 29.9589 | 27.2926 | 24.2242 | 20.9453 | 17.7379 | 12.2084 | 10.0589 | 8.1926
|  | BRENTFORD PRIMARY | HE |  |  |  |  | 38.04 | 37.8611 | 37.5979 | 37.24 | 36.4547 | 34.7589 | 32.8526 | 30.8947 | 29.0779 | 24.32 | 23.5253 | 22.9021 | 35.8558 | 35.6768 | 34.7368 | 33.44 | 32.0421 | 30.2147 | 28.1568 | 25.96 | 23.8758 | 18.24 | 17.3105 | 16.5789 | 35.2505 | 34.8305 | 34.1968 | 33.5295 | 32.2968 | 30.4189 | 28.3032 | 26.1274 | 24.1116 | 18.6989 | 17.8032 | 17.1
|  | BRENTFORD PRIMARY | FB |  |  |  |  | 38.1642 | 38.0516 | 37.9516 | 37.8389 | 37.7032 | 37.5411 | 37.3768 | 37.2063 | 36.9137 | 32.1874 | 31.0989 | 30.3653 | 35.98 | 35.8674 | 35.7674 | 35.6547 | 35.4358 | 34.8389 | 34.1589 | 33.3053 | 32.5232 | 27.3253 | 26.0832 | 25.2453 | 35.6074 | 35.3505 | 35.1021 | 34.7884 | 34.4979 | 34.1926 | 33.8579 | 33.4621 | 32.7863 | 27.4747 | 26.2716 | 25.46
EALING GSP |  | BRIDGE ROAD PRIMARY | MINIMUM HEADROOM | TQ 14778 75741 | NO | YES | 0.40737 | 89.128 | 88.6796 | 88.1164 | 163.6063 | 162.6853 | 159.6832 | 155.4874 | 150.6126 | 145.4653 | 135.7084 | 131.5853 | 127.8211 | 86.4396 | 84.9027 | 83.2101 | 157.4474 | 154.3716 | 151.0053 | 146.3632 | 140.7558 | 134.8284 | 123.68 | 119.0411 | 114.8042 | 85.0006 | 84.6175 | 82.7533 | 156.8021 | 153.4 | 149.5505 | 144.8179 | 139.6168 | 134.1221 | 123.7453 | 119.3937 | 115.4189
|  | BRIDGE ROAD PRIMARY | EE |  |  |  |  | 89.1396 | 88.7027 | 88.1848 | 163.7284 | 162.8747 | 162.0221 | 159.4642 | 156.6116 | 153.6368 | 145.0989 | 142.4674 | 140.1474 | 86.4796 | 85.1364 | 83.4164 | 157.8032 | 155.6189 | 153.3295 | 150.7684 | 147.8884 | 144.3811 | 134.4116 | 131.3895 | 128.7179 | 85.0091 | 84.6659 | 82.9785 | 157.1926 | 154.8063 | 152.3011 | 149.38 | 146.1779 | 142.9074 | 133.7326 | 130.9274 | 128.4495
|  | BRIDGE ROAD PRIMARY | HT |  |  |  |  | 89.128 | 88.6796 | 88.1164 | 163.6063 | 162.6853 | 159.6832 | 155.4874 | 150.6126 | 145.4653 | 135.7084 | 131.5853 | 127.8211 | 86.4396 | 84.9027 | 83.2101 | 157.4474 | 154.3716 | 151.0053 | 146.3632 | 140.7558 | 134.8284 | 123.68 | 119.0411 | 114.8042 | 85.0006 | 84.6175 | 82.7533 | 156.8021 | 153.4 | 149.5505 | 144.8179 | 139.6168 | 134.1221 | 123.7453 | 119.3937 | 115.4189
|  | BRIDGE ROAD PRIMARY | HE |  |  |  |  | 89.2154 | 88.8217 | 88.3343 | 163.9053 | 163.0737 | 162.2579 | 160.6084 | 157.8674 | 155.0505 | 147.9579 | 146.1674 | 144.5663 | 86.6206 | 85.6754 | 84.0933 | 158.5989 | 156.5 | 154.2989 | 151.8568 | 149.2326 | 146.0495 | 137.6516 | 135.5558 | 133.6779 | 85.068 | 84.7406 | 83.7375 | 158.0821 | 155.7916 | 153.3821 | 150.6811 | 147.6105 | 144.4516 | 136.7621 | 134.8358 | 133.1126
|  | BRIDGE ROAD PRIMARY | FB |  |  |  |  | 89.4469 | 89.2533 | 89.0301 | 164.9695 | 164.6968 | 164.4179 | 164.1326 | 163.8495 | 163.5453 | 159.5 | 157.5579 | 156.0389 | 86.8522 | 86.6596 | 86.0554 | 161.4263 | 160.6116 | 159.7558 | 158.7516 | 157.6347 | 156.4368 | 150.8737 | 148.6895 | 146.8737 | 85.2996 | 85.1069 | 84.9322 | 160.9295 | 160.2789 | 159.3358 | 158.2232 | 156.9811 | 155.6484 | 149.2211 | 147.0379 | 145.3516
LOVEDEAN GSP | HAVANT BSP | BROCKHAMPTON PRIMARY | MINIMUM HEADROOM | SU 70868 05828 | NO | YES | 0.21053 | 31.5174 | 31.4774 | 31.4426 | 31.3468 | 31.2121 | 42.1416 | 42.0216 | 41.9058 | 41.79 | 41.5153 | 40.7795 | 40.3521 | 26.4032 | 26.3379 | 26.2853 | 26.0663 | 25.7453 | 40.6695 | 40.5495 | 40.4337 | 40.0084 | 39.3432 | 38.1168 | 37.6547 | 30.1053 | 30.0789 | 30.0547 | 30.0284 | 29.9989 | 42.6779 | 42.3737 | 41.84 | 41.3032 | 40.6179 | 39.3379 | 38.86
|  | BROCKHAMPTON PRIMARY | EE |  |  |  |  | 42.5847 | 42.5258 | 42.4626 | 42.3763 | 42.2584 | 42.1458 | 42.0437 | 41.9363 | 41.8332 | 41.7542 | 41.2447 | 40.9489 | 41.1126 | 41.0537 | 40.9905 | 40.9042 | 40.7863 | 40.6737 | 40.5716 | 40.4642 | 40.3337 | 39.6832 | 38.5979 | 38.2716 | 43.1211 | 43.0621 | 42.9989 | 42.9126 | 42.7947 | 42.6821 | 42.5789 | 42.1084 | 41.6411 | 40.9632 | 39.8263 | 39.4863
|  | BROCKHAMPTON PRIMARY | HT |  |  |  |  | 42.5868 | 42.5311 | 42.4605 | 42.37 | 42.2605 | 42.1416 | 42.0216 | 41.9058 | 41.79 | 41.5153 | 40.7795 | 40.3521 | 41.1147 | 41.0589 | 40.9884 | 40.8979 | 40.7884 | 40.6695 | 40.5495 | 40.4337 | 40.0084 | 39.3432 | 38.1168 | 37.6547 | 43.1232 | 43.0674 | 42.9968 | 42.9063 | 42.7968 | 42.6779 | 42.3737 | 41.84 | 41.3032 | 40.6179 | 39.3379 | 38.86
|  | BROCKHAMPTON PRIMARY | HE |  |  |  |  | 42.5984 | 42.5458 | 42.4858 | 42.4037 | 42.2889 | 42.1837 | 42.0805 | 41.9763 | 41.8742 | 41.8837 | 41.8363 | 41.6826 | 41.1263 | 41.0737 | 41.0137 | 40.9316 | 40.8168 | 40.7116 | 40.6084 | 40.5042 | 40.4021 | 40.2337 | 39.2895 | 39.0842 | 43.1347 | 43.0821 | 43.0221 | 42.94 | 42.8253 | 42.72 | 42.6168 | 42.3979 | 41.9663 | 41.5347 | 40.5432 | 40.3284
|  | BROCKHAMPTON PRIMARY | FB |  |  |  |  | 31.5174 | 31.4774 | 31.4426 | 31.3468 | 31.2121 | 42.5037 | 42.4753 | 42.4489 | 42.4195 | 42.3153 | 42.2563 | 42.2195 | 26.4032 | 26.3379 | 26.2853 | 26.0663 | 25.7453 | 41.0316 | 41.0032 | 40.9768 | 40.9474 | 40.8432 | 40.7842 | 40.7474 | 30.1053 | 30.0789 | 30.0547 | 30.0284 | 29.9989 | 43.04 | 43.0116 | 42.9853 | 42.9558 | 42.8516 | 42.7926 | 42.7558
LOVEDEAN GSP | FAREHAM (MAIN) BSP | BROCKHURST PRIMARY | MINIMUM HEADROOM | SU 59381 02061 | NO | YES | 0.1 | 31.4405 | 30.9068 | 30.2921 | 29.6258 | 28.7921 | 56.1621 | 55.2737 | 54.1432 | 53.2221 | 50.2042 | 49.0011 | 47.9547 | 31.1863 | 30.5453 | 29.8053 | 29.0189 | 28.0347 | 53.5695 | 52.5221 | 51.16 | 50.0705 | 46.4105 | 45.0032 | 43.78 | 33.4484 | 32.9095 | 32.1705 | 31.3853 | 30.4021 | 56.8389 | 55.7958 | 54.4368 | 53.3495 | 49.6979 | 48.2926 | 47.0726
|  | BROCKHURST PRIMARY | EE |  |  |  |  | 31.4405 | 30.9068 | 30.3247 | 29.8037 | 29.0311 | 56.6158 | 55.8947 | 54.9284 | 54.2558 | 52.1495 | 51.3095 | 50.6347 | 31.1863 | 30.5453 | 29.8495 | 29.2484 | 28.3495 | 54.1558 | 53.3126 | 52.1558 | 51.3768 | 48.7379 | 47.7158 | 46.8968 | 33.4484 | 32.9095 | 32.2137 | 31.6137 | 30.7168 | 57.4253 | 56.5842 | 55.4295 | 54.6516 | 52.02 | 51.0011 | 50.1832
|  | BROCKHURST PRIMARY | HT |  |  |  |  | 31.4816 | 30.9405 | 30.2921 | 29.6258 | 28.7921 | 56.1621 | 55.2737 | 54.1432 | 53.2221 | 50.2042 | 49.0011 | 47.9547 | 31.2368 | 30.5832 | 29.8053 | 29.0189 | 28.0347 | 53.5695 | 52.5221 | 51.16 | 50.0705 | 46.4105 | 45.0032 | 43.78 | 33.4579 | 32.9463 | 32.1705 | 31.3853 | 30.4021 | 56.8389 | 55.7958 | 54.4368 | 53.3495 | 49.6979 | 48.2926 | 47.0726
|  | BROCKHURST PRIMARY | HE |  |  |  |  | 31.6321 | 31.1689 | 30.6489 | 30.1763 | 29.4353 | 57.0653 | 56.3968 | 55.4853 | 54.8726 | 53.3095 | 52.8263 | 52.4526 | 31.4242 | 30.8726 | 30.2537 | 29.7147 | 28.8568 | 54.7179 | 53.9453 | 52.86 | 52.1568 | 50.14 | 49.5337 | 49.0621 | 33.4821 | 33.2347 | 32.6179 | 32.0789 | 31.2232 | 57.9863 | 57.2147 | 56.1316 | 55.4295 | 53.4189 | 52.8137 | 52.3442
|  | BROCKHURST PRIMARY | FB |  |  |  |  | 31.8479 | 31.5858 | 31.3416 | 31.1321 | 30.8521 | 58.8621 | 58.5611 | 58.1242 | 57.8242 | 56.6179 | 55.8495 | 55.3758 | 31.6695 | 31.3558 | 31.0611 | 30.8147 | 30.4811 | 56.7695 | 56.4084 | 55.8695 | 55.5084 | 54.0495 | 53.1116 | 52.5358 | 33.5958 | 33.5137 | 33.4232 | 33.1779 | 32.8442 | 60.0337 | 59.6737 | 59.1358 | 58.7758 | 57.32 | 56.3853 | 55.8105
MELKSHAM GSP | NORRINGTON BSP | BROMHAM PRIMARY | MINIMUM HEADROOM | ST 98670 65994 | YES | YES | 0 | 5.2158 | 8.1095 | 7.9958 | 7.8779 | 7.7421 | 7.6189 | 7.4863 | 7.3389 | 7.1789 | 6.7295 | 6.3632 | 6.04 | 4.7642 | 7.6505 | 7.5305 | 7.4074 | 7.2663 | 7.1389 | 6.9979 | 6.8305 | 6.6579 | 6.1674 | 5.76 | 5.3989 | 4.28 | 7.1653 | 7.0432 | 6.9168 | 6.7737 | 6.6442 | 6.5032 | 6.3368 | 6.1632 | 5.6674 | 5.26 | 4.8989
|  | BROMHAM PRIMARY | EE |  |  |  |  | 5.2158 | 8.1095 | 7.9958 | 7.8779 | 7.7421 | 7.6189 | 7.4863 | 7.3495 | 7.2305 | 6.9074 | 6.5884 | 6.3295 | 4.7642 | 7.6505 | 7.5305 | 7.4074 | 7.2663 | 7.1389 | 7 | 6.8579 | 6.7337 | 6.38 | 6.0274 | 5.7379 | 4.28 | 7.1653 | 7.0432 | 6.9168 | 6.7737 | 6.6442 | 6.5032 | 6.3589 | 6.2337 | 5.8726 | 5.5126 | 5.2211
|  | BROMHAM PRIMARY | HT |  |  |  |  | 5.2463 | 8.1505 | 8.0432 | 7.9116 | 7.7758 | 7.6389 | 7.4937 | 7.3389 | 7.1789 | 6.7295 | 6.3632 | 6.04 | 4.7958 | 7.6947 | 7.5811 | 7.4411 | 7.2989 | 7.1537 | 6.9979 | 6.8305 | 6.6579 | 6.1674 | 5.76 | 5.3989 | 4.3137 | 7.2095 | 7.0947 | 6.9526 | 6.8084 | 6.6621 | 6.5063 | 6.3368 | 6.1632 | 5.6674 | 5.26 | 4.8989
|  | BROMHAM PRIMARY | HE |  |  |  |  | 5.3179 | 8.2663 | 8.2105 | 8.1389 | 8.0474 | 7.9663 | 7.8884 | 7.8105 | 7.7347 | 7.6474 | 7.4811 | 7.3442 | 4.8737 | 7.8189 | 7.76 | 7.6853 | 7.5926 | 7.5074 | 7.4274 | 7.3474 | 7.2705 | 7.1684 | 6.9779 | 6.82 | 4.3926 | 7.3368 | 7.2789 | 7.2042 | 7.1095 | 7.0253 | 6.9453 | 6.8653 | 6.7874 | 6.6842 | 6.4916 | 6.3316
|  | BROMHAM PRIMARY | FB |  |  |  |  | 5.3611 | 8.3221 | 8.2926 | 8.2621 | 8.2284 | 8.1937 | 8.1621 | 8.1326 | 8.1032 | 7.9589 | 7.8042 | 7.6758 | 4.9189 | 7.8768 | 7.8453 | 7.8116 | 7.7758 | 7.7389 | 7.7053 | 7.6726 | 7.6411 | 7.4842 | 7.3116 | 7.1653 | 4.4379 | 7.3958 | 7.3642 | 7.3295 | 7.2937 | 7.2568 | 7.2221 | 7.1905 | 7.1589 | 7.0011 | 6.8253 | 6.6789
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | BROOK STREET PRIMARY | MINIMUM HEADROOM | SU 63480 52228 | NO | YES | 0 | 28.1332 | 28.0395 | 27.9416 | 27.7858 | 27.6037 | 27.4016 | 27.0437 | 26.6689 | 26.29 | 25.3879 | 24.9637 | 24.4847 | 30.0695 | 30.0147 | 29.9505 | 29.8611 | 29.7379 | 29.6242 | 29.4968 | 29.3642 | 29.2274 | 28.8705 | 28.4126 | 27.8316 | 31.1589 | 31.1042 | 31.04 | 30.9526 | 30.8295 | 30.7168 | 30.6053 | 30.4947 | 30.3853 | 30.1337 | 29.8926 | 29.2926
|  | BROOK STREET PRIMARY | EE |  |  |  |  | 28.1332 | 28.0395 | 27.9416 | 27.8247 | 27.6837 | 27.5447 | 27.3868 | 27.0184 | 26.65 | 25.7153 | 25.4289 | 25.0932 | 30.0695 | 30.0147 | 29.9526 | 29.8684 | 29.7537 | 29.6432 | 29.5379 | 29.4158 | 29.2926 | 29.1147 | 28.9253 | 28.5021 | 31.1589 | 31.1063 | 31.0463 | 30.9642 | 30.8516 | 30.7432 | 30.6411 | 30.5358 | 30.4295 | 30.3589 | 30.2726 | 29.9758
|  | BROOK STREET PRIMARY | HT |  |  |  |  | 28.1511 | 28.0637 | 27.9468 | 27.7858 | 27.6037 | 27.4016 | 27.0437 | 26.6689 | 26.29 | 25.3879 | 24.9637 | 24.4847 | 30.0726 | 30.02 | 29.9505 | 29.8611 | 29.7505 | 29.6295 | 29.4968 | 29.3642 | 29.2274 | 28.8705 | 28.4126 | 27.8316 | 31.1621 | 31.1105 | 31.0442 | 30.9589 | 30.8537 | 30.7379 | 30.62 | 30.5042 | 30.3863 | 30.1337 | 29.8926 | 29.2926
|  | BROOK STREET PRIMARY | HE |  |  |  |  | 28.1826 | 28.1026 | 28.0174 | 27.91 | 27.7679 | 27.6342 | 27.5047 | 27.2058 | 26.9079 | 26.1363 | 25.99 | 25.8584 | 30.0726 | 30.0147 | 29.9505 | 29.8632 | 29.7379 | 29.6242 | 29.5116 | 29.3895 | 29.2674 | 29.2 | 29.1505 | 29.1084 | 31.1621 | 31.1042 | 31.04 | 30.9526 | 30.8295 | 30.7168 | 30.6053 | 30.4947 | 30.3853 | 30.3863 | 30.3589 | 30.3379
|  | BROOK STREET PRIMARY | FB |  |  |  |  | 28.2437 | 28.1837 | 28.1363 | 28.0847 | 28.03 | 27.9742 | 27.9205 | 27.8689 | 27.7174 | 26.9595 | 26.7511 | 26.5679 | 30.1137 | 30.0821 | 30.0537 | 30.0211 | 29.9842 | 29.9474 | 29.9116 | 29.8779 | 29.8368 | 29.6695 | 29.5884 | 29.5274 | 31.2032 | 31.1716 | 31.1432 | 31.1105 | 31.0747 | 31.0389 | 31.0042 | 30.9716 | 30.9379 | 30.8105 | 30.7379 | 30.6905
MELKSHAM GSP | FROME BSP | BRUTON PRIMARY | MINIMUM HEADROOM | ST 69094 35148 | NO | YES | 0 | 9.2211 | 9.1453 | 9.0653 | 8.9653 | 8.6463 | 8.3295 | 7.9979 | 7.8 | 7.6147 | 7.1989 | 6.9095 | 6.6232 | 7.0042 | 6.9579 | 6.9053 | 6.8 | 6.4389 | 6.0821 | 5.7084 | 5.4895 | 5.2874 | 4.8337 | 4.5158 | 4.1979 | 6.8368 | 6.7484 | 6.6621 | 6.5611 | 6.2411 | 5.9221 | 5.5895 | 5.3905 | 5.2053 | 4.7884 | 4.4979 | 4.2095
|  | BRUTON PRIMARY | EE |  |  |  |  | 9.2211 | 9.1453 | 9.0653 | 8.9653 | 8.8463 | 8.54 | 8.2158 | 7.8916 | 7.72 | 7.3737 | 7.1716 | 6.9716 | 7.0042 | 6.9579 | 6.9053 | 6.8 | 6.6758 | 6.3305 | 5.9621 | 5.5947 | 5.4074 | 5.0105 | 4.7832 | 4.5547 | 6.8368 | 6.7484 | 6.6621 | 6.5611 | 6.4421 | 6.1347 | 5.8095 | 5.4832 | 5.3105 | 4.9621 | 4.7589 | 4.5568
|  | BRUTON PRIMARY | HT |  |  |  |  | 9.2232 | 9.1695 | 9.0853 | 8.9884 | 8.6463 | 8.3295 | 7.9979 | 7.8 | 7.6147 | 7.1989 | 6.9095 | 6.6232 | 7.0063 | 6.9653 | 6.9095 | 6.8274 | 6.4389 | 6.0821 | 5.7084 | 5.4895 | 5.2874 | 4.8337 | 4.5158 | 4.1979 | 6.8547 | 6.7758 | 6.6863 | 6.5853 | 6.2411 | 5.9221 | 5.5895 | 5.3905 | 5.2053 | 4.7884 | 4.4979 | 4.2095
|  | BRUTON PRIMARY | HE |  |  |  |  | 9.2326 | 9.1905 | 9.1442 | 9.0737 | 8.9653 | 8.6811 | 8.3726 | 8.0663 | 7.9126 | 7.7347 | 7.6295 | 7.5105 | 7.0158 | 6.9737 | 6.9274 | 6.8642 | 6.7716 | 6.4895 | 6.1411 | 5.7947 | 5.6274 | 5.4168 | 5.2947 | 5.1568 | 6.8958 | 6.8316 | 6.7642 | 6.6811 | 6.5695 | 6.2758 | 5.9663 | 5.6589 | 5.5053 | 5.3263 | 5.22 | 5.1
|  | BRUTON PRIMARY | FB |  |  |  |  | 9.2653 | 9.2453 | 9.2274 | 9.2074 | 9.1853 | 9.1463 | 9.0263 | 8.8905 | 8.7505 | 8.4484 | 8.3042 | 8.1695 | 7.0484 | 7.0284 | 7.0105 | 6.9905 | 6.9684 | 6.9453 | 6.8558 | 6.6989 | 6.5379 | 6.1958 | 6.0347 | 5.8811 | 6.9547 | 6.9074 | 6.8726 | 6.8337 | 6.7937 | 6.7526 | 6.6221 | 6.4853 | 6.3453 | 6.0411 | 5.8968 | 5.7611
COWLEY GSP | WITNEY BSP | BURFORD PRIMARY | MINIMUM HEADROOM | SP 25671 12529 | NO | YES | 0 | 4.9853 | 4.9579 | 4.9274 | 4.8863 | 4.8326 | 4.7789 | 4.7232 | 4.6695 | 4.6147 | 4.4853 | 4.4063 | 4.3379 | 4.7705 | 4.7432 | 4.7126 | 4.6716 | 4.6179 | 4.5642 | 4.5084 | 4.4547 | 4.4 | 4.2705 | 4.1432 | 3.8768 | 4.8211 | 4.7937 | 4.7632 | 4.7221 | 4.6684 | 4.6147 | 4.5589 | 4.5053 | 4.4505 | 4.28 | 4.1337 | 3.9905
|  | BURFORD PRIMARY | EE |  |  |  |  | 4.9853 | 4.9579 | 4.9274 | 4.8884 | 4.8326 | 4.7811 | 4.7358 | 4.6863 | 4.6379 | 4.5968 | 4.5611 | 4.5316 | 4.7705 | 4.7432 | 4.7126 | 4.6737 | 4.6179 | 4.5663 | 4.5211 | 4.4716 | 4.4232 | 4.3821 | 4.3463 | 4.3105 | 4.8211 | 4.7937 | 4.7632 | 4.7242 | 4.6684 | 4.6168 | 4.5716 | 4.5221 | 4.4737 | 4.4326 | 4.3568 | 4.2726
|  | BURFORD PRIMARY | HT |  |  |  |  | 4.9884 | 4.9621 | 4.9295 | 4.8863 | 4.8358 | 4.7789 | 4.7232 | 4.6695 | 4.6147 | 4.4853 | 4.4063 | 4.3379 | 4.7737 | 4.7474 | 4.7147 | 4.6716 | 4.6211 | 4.5642 | 4.5084 | 4.4547 | 4.4 | 4.2705 | 4.1432 | 3.8768 | 4.8242 | 4.7979 | 4.7653 | 4.7221 | 4.6716 | 4.6147 | 4.5589 | 4.5053 | 4.4505 | 4.28 | 4.1337 | 3.9905
|  | BURFORD PRIMARY | HE |  |  |  |  | 4.9937 | 4.9695 | 4.9411 | 4.9032 | 4.8495 | 4.8 | 4.7526 | 4.7042 | 4.6579 | 4.6579 | 4.6463 | 4.6389 | 4.7789 | 4.7547 | 4.7263 | 4.6884 | 4.6347 | 4.5853 | 4.5379 | 4.4895 | 4.4432 | 4.4432 | 4.4316 | 4.4242 | 4.8295 | 4.8053 | 4.7768 | 4.7389 | 4.6853 | 4.6358 | 4.5884 | 4.54 | 4.4937 | 4.4937 | 4.4821 | 4.4747
|  | BURFORD PRIMARY | FB |  |  |  |  | 5.0116 | 4.9979 | 4.9863 | 4.9737 | 4.9589 | 4.9453 | 4.9305 | 4.9179 | 4.9032 | 4.8516 | 4.8232 | 4.8053 | 4.7968 | 4.7832 | 4.7716 | 4.7589 | 4.7442 | 4.7305 | 4.7158 | 4.7032 | 4.6884 | 4.6368 | 4.6084 | 4.5905 | 4.8474 | 4.8337 | 4.8221 | 4.8095 | 4.7947 | 4.7811 | 4.7663 | 4.7537 | 4.7389 | 4.6874 | 4.6589 | 4.6411
MANNINGTON GSP | WAREHAM BSP | BUSHEY PRIMARY | MINIMUM HEADROOM | SY 97671 83532 | YES | YES | 0 | 4.9263 | 4.8989 | 4.8716 | 4.8389 | 4.8032 | 4.7663 | 4.7242 | 4.6842 | 4.6432 | 4.5232 | 4.4253 | 4.3421 | 4.9168 | 4.8884 | 4.8589 | 4.8242 | 4.7874 | 4.7484 | 4.7042 | 4.66 | 4.6168 | 4.4884 | 4.38 | 4.2884 | 5.0874 | 5.0621 | 5.0358 | 5.0053 | 4.9695 | 4.9347 | 4.8947 | 4.8558 | 4.8168 | 4.7032 | 4.6126 | 4.5358
|  | BUSHEY PRIMARY | EE |  |  |  |  | 4.9263 | 4.8989 | 4.8716 | 4.8389 | 4.8032 | 4.7663 | 4.7242 | 4.6842 | 4.6432 | 4.5568 | 4.4811 | 4.4232 | 4.9168 | 4.8884 | 4.8589 | 4.8242 | 4.7874 | 4.7484 | 4.7042 | 4.66 | 4.6168 | 4.5189 | 4.4326 | 4.3663 | 5.0874 | 5.0621 | 5.0358 | 5.0053 | 4.9695 | 4.9347 | 4.8947 | 4.8558 | 4.8168 | 4.7389 | 4.6716 | 4.6189
|  | BUSHEY PRIMARY | HT |  |  |  |  | 4.9316 | 4.9074 | 4.88 | 4.8495 | 4.8147 | 4.7789 | 4.7411 | 4.7 | 4.6558 | 4.5232 | 4.4253 | 4.3421 | 4.9242 | 4.8979 | 4.8684 | 4.8358 | 4.8 | 4.7621 | 4.7242 | 4.68 | 4.6337 | 4.4884 | 4.38 | 4.2884 | 5.0926 | 5.0695 | 5.0442 | 5.0137 | 4.98 | 4.9453 | 4.9095 | 4.8695 | 4.8274 | 4.7032 | 4.6126 | 4.5358
|  | BUSHEY PRIMARY | HE |  |  |  |  | 4.9432 | 4.9221 | 4.9021 | 4.8758 | 4.8411 | 4.8095 | 4.7789 | 4.7484 | 4.7179 | 4.7042 | 4.6684 | 4.6432 | 4.9368 | 4.9147 | 4.8937 | 4.8663 | 4.8305 | 4.7989 | 4.7663 | 4.7358 | 4.7042 | 4.6874 | 4.6463 | 4.6168 | 5.0947 | 5.0789 | 5.0632 | 5.0368 | 5.0032 | 4.9726 | 4.9421 | 4.9126 | 4.8821 | 4.8716 | 4.84 | 4.8168
|  | BUSHEY PRIMARY | FB |  |  |  |  | 4.9611 | 4.9453 | 4.9347 | 4.9221 | 4.9084 | 4.8958 | 4.8842 | 4.8716 | 4.86 | 4.8105 | 4.76 | 4.7147 | 4.9568 | 4.9389 | 4.9274 | 4.9137 | 4.8989 | 4.8853 | 4.8726 | 4.86 | 4.8474 | 4.7937 | 4.7368 | 4.6853 | 5.1063 | 5.0989 | 5.0926 | 5.0832 | 5.0705 | 5.0579 | 5.0463 | 5.0358 | 5.0242 | 4.9779 | 4.9316 | 4.8916
FAWLEY GSP | LANGLEY BSP | BUTTS ASH PRIMARY | MINIMUM HEADROOM | SU 41923 05772 | NO | YES | 0 | 27.5684 | 27.3295 | 27.0537 | 26.6768 | 25.8263 | 24.7074 | 23.6168 | 22.5095 | 21.3747 | 18.8432 | 16.9842 | 15.4368 | 26.0095 | 25.5032 | 24.8105 | 23.8632 | 22.6947 | 21.4632 | 20.2674 | 19.0495 | 17.8 | 15.0221 | 12.9579 | 11.2442 | 25.3621 | 25.0484 | 24.3716 | 23.4453 | 22.3042 | 21.1021 | 19.9326 | 18.7432 | 17.5232 | 14.8074 | 12.7958 | 11.1242
|  | BUTTS ASH PRIMARY | EE |  |  |  |  | 27.5684 | 27.3295 | 27.0579 | 26.6947 | 26.2042 | 25.7295 | 25.2895 | 24.8442 | 24.3105 | 23.2389 | 21.9832 | 21.02 | 26.0095 | 25.5126 | 25.0074 | 24.4358 | 23.7779 | 23.1358 | 22.4979 | 21.8589 | 21.2337 | 20.0221 | 18.5926 | 17.4968 | 25.3621 | 25.0568 | 24.56 | 23.9968 | 23.3453 | 22.7105 | 22.08 | 21.4484 | 20.8284 | 19.6537 | 18.2674 | 17.2053
|  | BUTTS ASH PRIMARY | HT |  |  |  |  | 27.5758 | 27.3505 | 27.0537 | 26.6768 | 25.8263 | 24.7074 | 23.6168 | 22.5095 | 21.3747 | 18.8432 | 16.9842 | 15.4368 | 26.0653 | 25.5032 | 24.8105 | 23.8632 | 22.6947 | 21.4632 | 20.2674 | 19.0495 | 17.8 | 15.0221 | 12.9579 | 11.2442 | 25.3695 | 25.0484 | 24.3716 | 23.4453 | 22.3042 | 21.1021 | 19.9326 | 18.7432 | 17.5232 | 14.8074 | 12.7958 | 11.1242
|  | BUTTS ASH PRIMARY | HE |  |  |  |  | 27.6084 | 27.3779 | 27.12 | 26.7632 | 26.2768 | 25.8253 | 25.3853 | 24.9389 | 24.5021 | 24.5505 | 24.0832 | 23.5 | 26.2526 | 25.9832 | 25.5968 | 25.1189 | 24.5263 | 23.9674 | 23.4221 | 22.8726 | 22.34 | 21.8874 | 20.9495 | 20.2684 | 25.4021 | 25.1716 | 24.9137 | 24.5568 | 24.0674 | 23.5137 | 22.9716 | 22.4263 | 21.8979 | 21.4642 | 20.56 | 19.9032
|  | BUTTS ASH PRIMARY | FB |  |  |  |  | 27.7958 | 27.6874 | 27.5905 | 27.4811 | 27.36 | 27.2368 | 27.1189 | 27.0084 | 26.8895 | 26.4558 | 25.9726 | 25.3053 | 26.44 | 26.3316 | 26.1789 | 25.9568 | 25.7242 | 25.4895 | 25.2611 | 25.0411 | 24.8168 | 23.8611 | 22.8674 | 22.1074 | 25.5895 | 25.4811 | 25.3842 | 25.2747 | 25.1537 | 25.0305 | 24.8074 | 24.5916 | 24.3716 | 23.4358 | 22.4705 | 21.7337
MELKSHAM GSP | CHIPPENHAM BSP | CALNE PRIMARY | MINIMUM HEADROOM | SU 00521 72497 | NO | YES | 0 | 17.7253 | 17.3411 | 16.6684 | 15.8137 | 14.8389 | 14.1316 | 15.1779 | 16.2284 | 13.3095 | 13.8432 | 15.8884 | 14.0011 | 12.9358 | 12.5326 | 11.8158 | 10.9053 | 9.8663 | 9.0779 | 9.9842 | 10.9011 | 7.9989 | 10.0589 | 11.6305 | 9.4684 | 16.7232 | 16.2958 | 15.5126 | 14.5242 | 13.4158 | 12.6326 | 13.68 | 14.7379 | 12.0474 | 14.1253 | 16.3137 | 14.1674
|  | CALNE PRIMARY | EE |  |  |  |  | 17.7253 | 17.3411 | 16.6684 | 15.8137 | 14.8389 | 14.1316 | 15.1779 | 16.2284 | 16.1621 | 14.9579 | 20.66 | 19.3989 | 12.9358 | 12.5326 | 11.8158 | 10.9053 | 9.8663 | 9.0779 | 9.9842 | 10.9011 | 11.54 | 10.0979 | 17.2684 | 15.7368 | 16.7232 | 16.2958 | 15.5126 | 14.5242 | 13.4158 | 12.6326 | 13.68 | 14.7379 | 15.5547 | 14.1253 | 21.9074 | 20.3884
|  | CALNE PRIMARY | HT |  |  |  |  | 17.8032 | 17.4558 | 16.7368 | 17.5095 | 16.4642 | 15.4895 | 16.2232 | 16.8916 | 13.3095 | 13.8432 | 15.8884 | 14.0011 | 13.0189 | 12.6558 | 11.8905 | 13.6411 | 12.5305 | 11.4158 | 11.9484 | 12.3958 | 7.9989 | 10.0589 | 11.6305 | 9.4684 | 16.7874 | 16.4316 | 15.5989 | 17.4484 | 16.2453 | 15.1358 | 15.8126 | 16.4063 | 12.0474 | 14.4074 | 16.3137 | 14.1674
|  | CALNE PRIMARY | HE |  |  |  |  | 17.9863 | 17.7 | 17.1074 | 16.3211 | 15.3895 | 14.7463 | 15.8621 | 16.9895 | 17.0011 | 16.4505 | 22.5547 | 21.6347 | 13.2168 | 12.9211 | 12.2905 | 11.4537 | 10.4716 | 9.8011 | 10.8179 | 11.8295 | 12.5632 | 11.8663 | 19.4947 | 18.3526 | 16.9284 | 16.6716 | 16.0389 | 15.1326 | 14.0768 | 13.3684 | 14.5063 | 15.6589 | 16.5705 | 15.8811 | 24.1189 | 22.9884
|  | CALNE PRIMARY | FB |  |  |  |  | 18.2168 | 18.0063 | 17.7274 | 17.4042 | 17.0537 | 16.7821 | 18.2589 | 19.7411 | 19.5663 | 18.7326 | 21.8758 | 21.0674 | 13.4558 | 13.2337 | 12.9347 | 12.5884 | 12.2126 | 11.9242 | 13.3463 | 14.7726 | 14.5905 | 13.7053 | 16.5505 | 15.5684 | 17.1326 | 16.9579 | 16.7189 | 16.3411 | 15.9295 | 15.6168 | 17.14 | 18.6663 | 18.4747 | 17.5284 | 20.7 | 19.7263
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY PRIMARY | MINIMUM HEADROOM | SU 86584 59452 | NO | YES | 0 | 82.0558 | 81.6305 | 81.1558 | 80.6653 | 80.0316 | 79.2958 | 78.4579 | 77.5684 | 76.6821 | 74.5053 | 72.9389 | 71.5705 | 78.1558 | 77.4937 | 76.76 | 76.0905 | 75.1916 | 74.1537 | 73.2253 | 72.2326 | 71.2442 | 68.7989 | 67.02 | 65.4663 | 83.4032 | 83.0568 | 82.3305 | 81.6674 | 80.7779 | 79.7505 | 78.8316 | 77.8484 | 76.8705 | 74.4505 | 72.6926 | 71.1558
|  | CAMBERLEY PRIMARY | EE |  |  |  |  | 82.0558 | 81.6305 | 81.1558 | 80.7632 | 80.3011 | 79.8474 | 79.3937 | 78.9379 | 78.4874 | 77.5895 | 76.4926 | 75.5653 | 78.1558 | 77.4937 | 76.76 | 76.2705 | 75.7379 | 75.2126 | 74.6642 | 74.1147 | 73.5747 | 72.3653 | 71.0863 | 70 | 83.5958 | 83.0568 | 82.3305 | 81.8453 | 81.3158 | 80.7926 | 80.2463 | 79.7 | 79.1642 | 77.9705 | 76.7074 | 75.6379
|  | CAMBERLEY PRIMARY | HT |  |  |  |  | 82.1011 | 81.6958 | 81.1663 | 80.6653 | 80.0316 | 79.2958 | 78.4579 | 77.5684 | 76.6821 | 74.5053 | 72.9389 | 71.5705 | 78.24 | 77.6084 | 76.7874 | 76.0905 | 75.1916 | 74.1537 | 73.2253 | 72.2326 | 71.2442 | 68.7989 | 67.02 | 65.4663 | 83.6042 | 83.1705 | 82.3579 | 81.6674 | 80.7779 | 79.7505 | 78.8316 | 77.8484 | 76.8705 | 74.4505 | 72.6926 | 71.1558
|  | CAMBERLEY PRIMARY | HE |  |  |  |  | 82.2211 | 81.8505 | 81.4263 | 81.0779 | 80.64 | 80.2242 | 79.82 | 79.4095 | 79.0137 | 78.7726 | 78.3274 | 77.7474 | 78.4432 | 77.8853 | 77.2453 | 76.8358 | 76.3516 | 75.8916 | 75.4421 | 74.9874 | 74.5505 | 74.0516 | 73.2137 | 72.5032 | 83.6411 | 83.4432 | 82.8105 | 82.4021 | 81.92 | 81.4611 | 81.0126 | 80.56 | 80.1253 | 79.6347 | 78.8095 | 78.1105
|  | CAMBERLEY PRIMARY | FB |  |  |  |  | 82.0726 | 81.8705 | 81.6937 | 81.5516 | 81.4053 | 81.2589 | 81.1147 | 80.9768 | 80.8358 | 80.6358 | 80.1032 | 79.6716 | 78.3074 | 77.9926 | 77.7147 | 77.5232 | 77.3295 | 77.1368 | 76.9474 | 76.7632 | 76.5768 | 76.2337 | 75.3632 | 74.6221 | 83.4032 | 83.3126 | 83.2337 | 83.1274 | 82.9358 | 82.7442 | 82.5568 | 82.3737 | 82.1895 | 81.8053 | 80.9474 | 80.2158
WILLESDEN GSP |  | CANAL BANK 11KV PRIMARY | MINIMUM HEADROOM | TQ 20927 83082 | NO | NO | 0 | 72.5832 | 72.3821 | 71.8505 | 71.2074 | 70.6526 | 70.6263 | 70.6011 | 69.7389 | 65.1347 | 50.6326 | 49.3968 | 49.3337 | 69.0526 | 69.0411 | 69.0284 | 69.0095 | 68.9863 | 68.9611 | 68.9358 | 68.9105 | 67.1242 | 50.3053 | 48.8579 | 48.7853 | 71.2337 | 71.2221 | 71.2095 | 71.1905 | 71.1484 | 71.1221 | 71.0968 | 71.0716 | 67.3305 | 50.2958 | 48.8484 | 48.7758
|  | CANAL BANK 11KV PRIMARY | EE |  |  |  |  | 72.5832 | 72.5716 | 72.2389 | 71.6568 | 71.1716 | 70.8989 | 70.8684 | 70.8474 | 67.86 | 59.6621 | 59.6537 | 59.5621 | 69.0526 | 69.0411 | 69.0295 | 69.0126 | 68.9895 | 68.9663 | 68.9463 | 68.9253 | 68.9032 | 60.92 | 60.9547 | 60.8505 | 71.2337 | 71.2221 | 71.2105 | 71.1937 | 71.1705 | 71.1453 | 71.1242 | 71.1032 | 69.8621 | 60.9137 | 60.9684 | 60.8642
|  | CANAL BANK 11KV PRIMARY | HT |  |  |  |  | 72.5832 | 72.3821 | 71.8505 | 71.2074 | 70.6526 | 70.6263 | 70.6011 | 70.5758 | 65.1347 | 61.7674 | 61.6168 | 61.4853 | 69.0526 | 69.0421 | 69.0284 | 69.0095 | 68.9874 | 68.9611 | 68.9358 | 68.9105 | 67.1242 | 63.4432 | 63.2726 | 63.1263 | 71.2337 | 71.2232 | 71.2095 | 71.1905 | 71.1484 | 71.1221 | 71.0968 | 71.0716 | 67.3305 | 63.4579 | 63.2874 | 63.1411
|  | CANAL BANK 11KV PRIMARY | HE |  |  |  |  | 72.5853 | 72.5726 | 72.3632 | 71.8589 | 71.26 | 71.0442 | 70.8253 | 70.8021 | 67.7 | 57.8821 | 57.3821 | 57.3411 | 69.0547 | 69.0421 | 69.0295 | 69.0116 | 68.9863 | 68.9632 | 68.9421 | 68.9189 | 68.8947 | 58.8284 | 58.2421 | 58.1947 | 71.2358 | 71.2232 | 71.2105 | 71.1926 | 71.1674 | 71.1442 | 71.1179 | 71.0947 | 69.7442 | 58.8221 | 58.2358 | 58.1884
|  | CANAL BANK 11KV PRIMARY | FB |  |  |  |  | 72.5905 | 72.5821 | 72.5747 | 72.5663 | 72.5568 | 72.5484 | 71.4937 | 69.7389 | 66.4768 | 50.6326 | 49.3968 | 49.3337 | 69.06 | 69.0516 | 69.0442 | 69.0358 | 69.0263 | 69.0179 | 69.0084 | 69 | 68.3147 | 50.3053 | 48.8579 | 48.7853 | 71.2411 | 71.2326 | 71.2253 | 71.2168 | 71.2074 | 71.1989 | 71.1895 | 71.1 | 68.82 | 50.2958 | 48.8484 | 48.7758
COWLEY GSP | WITNEY BSP | CARTERTON PRIMARY | MINIMUM HEADROOM | SP 28261 07823 | NO | YES | 0.14737 | 33.76 | 33.5947 | 32.8947 | 32.1474 | 31.48 | 30.8895 | 30.3537 | 29.7316 | 29.1053 | 27.3411 | 25.7611 | 24.0947 | 27.5779 | 26.6737 | 25.8547 | 25.02 | 24.2874 | 23.6526 | 23.0821 | 22.4074 | 21.7295 | 19.7884 | 18.0116 | 16.1211 | 32.7126 | 32.3853 | 31.5663 | 30.7295 | 29.9979 | 29.3642 | 28.7937 | 28.1179 | 27.44 | 25.4989 | 23.7211 | 21.8305
|  | CARTERTON PRIMARY | EE |  |  |  |  | 33.76 | 33.5947 | 33.2053 | 32.7063 | 32.1789 | 31.7505 | 31.3305 | 30.9042 | 30.4874 | 27.8779 | 26.8726 | 25.7916 | 27.6958 | 26.8368 | 26.2211 | 25.6747 | 25.1137 | 24.6653 | 24.22 | 23.7705 | 23.3316 | 20.2979 | 19.1495 | 17.9063 | 32.7126 | 32.5474 | 31.9316 | 31.3863 | 30.8253 | 30.3768 | 29.9316 | 29.4821 | 29.0421 | 26.0084 | 24.86 | 23.6147
|  | CARTERTON PRIMARY | HT |  |  |  |  | 33.7747 | 33.6189 | 32.8947 | 32.1474 | 31.48 | 30.8895 | 30.3537 | 29.7316 | 29.1053 | 27.3411 | 25.7611 | 24.0947 | 27.5779 | 26.6737 | 25.8547 | 25.02 | 24.2874 | 23.6526 | 23.0821 | 22.4074 | 21.7295 | 19.7884 | 18.0116 | 16.1211 | 32.7274 | 32.3853 | 31.5663 | 30.7295 | 29.9979 | 29.3642 | 28.7937 | 28.1179 | 27.44 | 25.4989 | 23.7211 | 21.8305
|  | CARTERTON PRIMARY | HE |  |  |  |  | 33.8158 | 33.6632 | 33.4958 | 33.16 | 32.6737 | 32.3011 | 31.9379 | 31.5726 | 31.2137 | 29.1274 | 28.4516 | 27.6526 | 27.9611 | 27.2011 | 26.6695 | 26.1947 | 25.6811 | 25.2947 | 24.9179 | 24.5389 | 24.1684 | 21.7042 | 20.92 | 19.9853 | 32.7684 | 32.6158 | 32.3811 | 31.9063 | 31.3926 | 31.0063 | 30.6295 | 30.2505 | 29.88 | 27.4147 | 26.6305 | 25.6958
|  | CARTERTON PRIMARY | FB |  |  |  |  | 33.9211 | 33.8432 | 33.7726 | 33.6947 | 33.6074 | 33.52 | 33.4347 | 33.3547 | 33.2695 | 32.9063 | 32.2495 | 31.5579 | 28.4274 | 27.9895 | 27.7221 | 27.5 | 27.2937 | 27.1179 | 26.9463 | 26.7842 | 26.6158 | 25.9495 | 25.2074 | 24.4116 | 32.8737 | 32.7958 | 32.7253 | 32.6474 | 32.56 | 32.4726 | 32.3874 | 32.3074 | 32.2221 | 31.6621 | 30.9189 | 30.1221
AXMINSTER GSP | YEOVIL BSP | CASTLE CARY PRIMARY | MINIMUM HEADROOM | ST 64534 31039 | NO | YES | 0 | 14.2592 | 13.9203 | 13.4739 | 13.0392 | 12.6666 | 12.3603 | 12.1003 | 11.7634 | 11.5508 | 10.5761 | 10.1761 | 9.7855 | 11.8763 | 11.4647 | 10.9226 | 10.4005 | 9.9647 | 9.6111 | 9.3195 | 8.9405 | 8.7016 | 7.5953 | 7.15 | 6.7132 | 12.4389 | 12.0379 | 11.5116 | 11.0042 | 10.5779 | 10.2316 | 9.9432 | 9.5653 | 9.3274 | 8.2295 | 7.7874 | 7.3516
|  | CASTLE CARY PRIMARY | EE |  |  |  |  | 14.2592 | 14.1476 | 13.7076 | 13.1771 | 12.6666 | 12.3603 | 12.2045 | 11.8761 | 11.5508 | 10.8497 | 10.5645 | 10.2876 | 11.8763 | 11.7521 | 11.2174 | 10.5742 | 9.9647 | 9.6111 | 9.4416 | 9.07 | 8.7016 | 7.8774 | 7.55 | 7.2321 | 12.4389 | 12.3168 | 11.7958 | 11.1716 | 10.5779 | 10.2316 | 10.0632 | 9.6937 | 9.3274 | 8.5074 | 8.1832 | 7.8663
|  | CASTLE CARY PRIMARY | HT |  |  |  |  | 14.2803 | 13.9203 | 13.4739 | 13.0392 | 12.7382 | 12.4182 | 12.1003 | 11.7634 | 11.5855 | 10.5761 | 10.1761 | 9.7855 | 11.9016 | 11.4647 | 10.9226 | 10.4005 | 10.0521 | 9.6837 | 9.3195 | 8.9405 | 8.7511 | 7.5953 | 7.15 | 6.7132 | 12.4632 | 12.0379 | 11.5116 | 11.0042 | 10.6642 | 10.3021 | 9.9432 | 9.5653 | 9.3768 | 8.2295 | 7.7874 | 7.3516
|  | CASTLE CARY PRIMARY | HE |  |  |  |  | 14.3308 | 14.2476 | 13.9392 | 13.5603 | 13.1045 | 12.6613 | 12.3403 | 12.0908 | 11.8392 | 11.2845 | 11.1371 | 10.9782 | 11.9616 | 11.8721 | 11.5005 | 11.0479 | 10.5068 | 9.9784 | 9.6026 | 9.3195 | 9.0395 | 8.3711 | 8.1984 | 8.01 | 12.5221 | 12.4337 | 12.0726 | 11.6316 | 11.1042 | 10.5895 | 10.2221 | 9.9421 | 9.6642 | 9.0021 | 8.8316 | 8.6442
|  | CASTLE CARY PRIMARY | FB |  |  |  |  | 14.4182 | 14.3603 | 14.3161 | 14.1603 | 13.9866 | 13.7992 | 13.5982 | 13.4487 | 13.3318 | 12.9161 | 12.7308 | 12.5539 | 12.0584 | 11.9921 | 11.9426 | 11.7532 | 11.5437 | 11.3153 | 11.07 | 10.8889 | 10.7489 | 10.2521 | 10.0342 | 9.8205 | 12.6179 | 12.5526 | 12.5042 | 12.32 | 12.1158 | 11.8947 | 11.6568 | 11.48 | 11.3442 | 10.86 | 10.6474 | 10.44
LALEHAM GSP | STAINES BSP | CAUSEWAY PRIMARY | MINIMUM HEADROOM | TQ 02763 71680 | NO | YES | 0 | 49.7495 | 47.9358 | 47.66 | 47.2495 | 46.6516 | 45.9316 | 45.2053 | 44.28 | 43.2253 | 38.6916 | 37.5358 | 36.5158 | 50.5211 | 48.3263 | 48.0295 | 47.5853 | 46.9284 | 46.1326 | 45.3305 | 44.2947 | 43.1063 | 37.9179 | 36.6347 | 35.5021 | 49.3221 | 48.9158 | 48.7421 | 48.5084 | 48.2021 | 47.7137 | 46.9526 | 45.9758 | 44.8579 | 39.9568 | 38.6705 | 37.5347
|  | CAUSEWAY PRIMARY | EE |  |  |  |  | 49.7495 | 47.9358 | 47.66 | 47.3484 | 46.98 | 46.58 | 46.1695 | 45.6032 | 44.9337 | 41.8421 | 41.0411 | 40.3684 | 50.5211 | 48.3263 | 48.0295 | 47.7011 | 47.3179 | 46.8958 | 46.4579 | 45.84 | 45.0989 | 41.5105 | 40.6 | 39.8347 | 49.3221 | 48.9158 | 48.7421 | 48.52 | 48.2242 | 47.9337 | 47.6589 | 47.3558 | 46.6989 | 43.3747 | 42.5232 | 41.8074
|  | CAUSEWAY PRIMARY | HT |  |  |  |  | 49.8032 | 48.0179 | 47.7305 | 47.2495 | 46.6516 | 45.9316 | 45.2053 | 44.28 | 43.2253 | 38.6916 | 37.5358 | 36.5158 | 50.5863 | 48.4189 | 48.1105 | 47.5853 | 46.9284 | 46.1326 | 45.3305 | 44.2947 | 43.1063 | 37.9179 | 36.6347 | 35.5021 | 49.3389 | 48.9463 | 48.7621 | 48.5084 | 48.2021 | 47.7137 | 46.9526 | 45.9758 | 44.8579 | 39.9568 | 38.6705 | 37.5347
|  | CAUSEWAY PRIMARY | HE |  |  |  |  | 49.9168 | 48.18 | 47.9663 | 47.7042 | 47.3716 | 47.0189 | 46.6768 | 46.1789 | 45.5747 | 42.9895 | 42.4916 | 42.0737 | 50.7232 | 48.6063 | 48.38 | 48.1084 | 47.7663 | 47.3968 | 47.04 | 46.5 | 45.8368 | 42.8084 | 42.2326 | 41.7474 | 49.3726 | 48.9832 | 48.8274 | 48.6168 | 48.3316 | 48.0611 | 47.7989 | 47.5042 | 47.2 | 44.5926 | 44.0589 | 43.6095
|  | CAUSEWAY PRIMARY | FB |  |  |  |  | 50.0884 | 49.9411 | 49.8305 | 49.7105 | 49.5853 | 49.4432 | 49.3042 | 49.0947 | 48.8168 | 47.7442 | 46.6253 | 46.14 | 50.9137 | 50.7453 | 50.6211 | 50.4884 | 50.3495 | 50.1905 | 50.0337 | 49.7863 | 49.4558 | 48.1937 | 46.9105 | 46.3589 | 49.4842 | 49.4053 | 49.3389 | 49.2632 | 49.1821 | 49.0968 | 49.0137 | 48.9242 | 48.8189 | 48.4274 | 48.1326 | 47.9305
FLEET-BRAMLEY GSP | READING TOWN BSP | CAVERSHAM PRIMARY | MINIMUM HEADROOM | SU 71512 75747 | NO | YES | 0 | 32.0142 | 31.7816 | 31.4711 | 30.9153 | 30.3511 | 29.7426 | 29.1426 | 28.5437 | 27.9521 | 25.8553 | 24.4184 | 23.1237 | 28.3379 | 27.8916 | 27.4284 | 26.8337 | 26.2411 | 25.6042 | 24.9758 | 24.3484 | 23.7284 | 21.4221 | 19.8295 | 18.3895 | 26.4368 | 25.9958 | 25.5379 | 24.9505 | 24.3611 | 23.7295 | 23.1053 | 22.4821 | 21.8663 | 19.5937 | 18.0253 | 16.6063
|  | CAVERSHAM PRIMARY | EE |  |  |  |  | 32.0142 | 31.7816 | 31.4711 | 30.9742 | 30.3847 | 29.8037 | 29.2405 | 28.6753 | 28.1226 | 26.9574 | 26.0121 | 25.1816 | 28.3379 | 27.8916 | 27.4284 | 26.9 | 26.2811 | 25.6716 | 25.0789 | 24.4832 | 23.9032 | 22.5695 | 21.4905 | 20.5368 | 26.4368 | 25.9958 | 25.5379 | 25.0147 | 24.4011 | 23.7958 | 23.2063 | 22.6158 | 22.0389 | 20.7316 | 19.6737 | 18.74
|  | CAVERSHAM PRIMARY | HT |  |  |  |  | 32.0332 | 31.8026 | 31.4784 | 30.9153 | 30.3511 | 29.7426 | 29.1426 | 28.5437 | 27.9521 | 25.8553 | 24.4184 | 23.1237 | 28.4305 | 27.9305 | 27.4379 | 26.8337 | 26.2411 | 25.6042 | 24.9758 | 24.3484 | 23.7284 | 21.4221 | 19.8295 | 18.3895 | 26.5274 | 26.0337 | 25.5463 | 24.9505 | 24.3611 | 23.7295 | 23.1053 | 22.4821 | 21.8663 | 19.5937 | 18.0253 | 16.6063
|  | CAVERSHAM PRIMARY | HE |  |  |  |  | 32.0921 | 31.8774 | 31.6311 | 31.2995 | 30.8511 | 30.4289 | 29.9605 | 29.4542 | 28.9626 | 28.3542 | 27.7868 | 27.2805 | 28.6642 | 28.3389 | 27.9811 | 27.5379 | 26.9768 | 26.4389 | 25.9158 | 25.3916 | 24.8821 | 24.1558 | 23.4926 | 22.8968 | 26.7558 | 26.4347 | 26.0789 | 25.6389 | 25.0811 | 24.5463 | 24.0263 | 23.5042 | 22.9979 | 22.2905 | 21.6421 | 21.06
|  | CAVERSHAM PRIMARY | FB |  |  |  |  | 32.2553 | 32.1426 | 32.0458 | 31.9374 | 31.8174 | 31.6953 | 31.5774 | 31.4363 | 31.2384 | 30.2879 | 29.5932 | 29.0079 | 28.9379 | 28.6832 | 28.4884 | 28.2832 | 28.06 | 27.8326 | 27.6116 | 27.3968 | 27.1821 | 26.1263 | 25.3411 | 24.6705 | 27.0263 | 26.7758 | 26.5842 | 26.3811 | 26.1611 | 25.9368 | 25.7189 | 25.5063 | 25.2937 | 24.2547 | 23.4842 | 22.8263
MANNINGTON GSP | BOURNEMOUTH BSP | CENTRAL PRIMARY | MINIMUM HEADROOM | SZ 10293 91931 | NO | YES | 0 | 34.4879 | 34.2574 | 33.6047 | 32.9037 | 30.5332 | 29.3668 | 27.5563 | 26.3489 | 25.1489 | 22.5447 | 20.6174 | 18.8205 | 31.2316 | 30.7611 | 29.5684 | 28.6768 | 25.1695 | 23.5084 | 20.7558 | 19.0284 | 17.3168 | 13.6947 | 10.9474 | 8.3747 | 33.5011 | 33.1421 | 32.3768 | 31.7358 | 28.5716 | 27.0853 | 24.6663 | 23.1221 | 21.5916 | 18.3295 | 15.8726 | 13.3979
|  | CENTRAL PRIMARY | EE |  |  |  |  | 34.4879 | 34.2574 | 33.7795 | 33.3353 | 31.23 | 30.6774 | 29.4542 | 28.8858 | 28.3353 | 27.1089 | 25.7553 | 24.5458 | 31.2316 | 30.8421 | 29.8337 | 29.3232 | 26.3326 | 25.7147 | 23.9179 | 23.2463 | 22.6063 | 20.8053 | 18.7653 | 16.9211 | 33.5011 | 33.1758 | 32.5232 | 32.1 | 29.5853 | 28.9768 | 27.3811 | 26.7453 | 26.1358 | 24.5389 | 22.7411 | 21.1211
|  | CENTRAL PRIMARY | HT |  |  |  |  | 34.5016 | 34.2711 | 33.6047 | 32.9037 | 30.5332 | 29.3668 | 27.5563 | 26.3489 | 25.1489 | 22.5447 | 20.6174 | 18.8205 | 31.2537 | 30.7611 | 29.5684 | 28.6768 | 25.1695 | 23.5084 | 20.7558 | 19.0284 | 17.3168 | 13.6947 | 10.9474 | 8.3747 | 33.5284 | 33.1421 | 32.3768 | 31.7358 | 28.5716 | 27.0853 | 24.6663 | 23.1221 | 21.5916 | 18.3295 | 15.8726 | 13.3979
|  | CENTRAL PRIMARY | HE |  |  |  |  | 34.5258 | 34.2837 | 33.9626 | 33.59 | 31.4626 | 30.9205 | 29.7311 | 29.2047 | 28.7037 | 28.2153 | 27.3247 | 26.5247 | 31.3305 | 31.06 | 30.2253 | 29.7516 | 26.7579 | 26.1695 | 24.5263 | 23.9463 | 23.4053 | 22.58 | 21.1621 | 19.8705 | 33.5789 | 33.3463 | 32.7211 | 32.3 | 29.9811 | 29.4 | 27.8716 | 27.3116 | 26.7842 | 26.0779 | 24.8463 | 23.7284
|  | CENTRAL PRIMARY | FB |  |  |  |  | 34.6837 | 34.5363 | 34.3858 | 34.2405 | 33.6374 | 33.4184 | 32.8721 | 32.6721 | 32.4626 | 31.5174 | 30.6016 | 29.8005 | 31.5126 | 31.3284 | 31.0158 | 30.7768 | 29.5768 | 29.3221 | 28.5632 | 28.3295 | 28.0863 | 26.9221 | 25.6821 | 24.4737 | 33.7274 | 33.5937 | 33.3263 | 33.1347 | 32.4168 | 32.2105 | 31.7284 | 31.5 | 31.2611 | 30.1295 | 28.9379 | 27.8621
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CENTRAL BRIDGE PRIMARY | MINIMUM HEADROOM | SU 42591 11255 | NO | YES | 0 | 44.0116 | 43.9432 | 43.9832 | 43.94 | 43.8926 | 43.0284 | 40.6347 | 39.2232 | 38.2295 | 36.6105 | 35.8358 | 35.1389 | 35.0189 | 34.7326 | 35.0284 | 34.8989 | 34.7495 | 33.3937 | 30.5926 | 28.9484 | 27.7979 | 25.9389 | 25.0589 | 24.2695 | 36.2389 | 35.9621 | 36.2474 | 36.1211 | 35.9758 | 35.2463 | 32.64 | 31.0811 | 29.9684 | 28.1684 | 27.3158 | 26.5505
|  | CENTRAL BRIDGE PRIMARY | EE |  |  |  |  | 44.0158 | 43.9474 | 45.1547 | 45.0779 | 44.9674 | 44.8632 | 44.7621 | 42.9053 | 40.8853 | 38.3095 | 37.7032 | 37.1821 | 35.0453 | 34.7326 | 36.5095 | 36.4326 | 36.3211 | 36.2168 | 35.8053 | 33.28 | 30.9147 | 27.8947 | 27.2011 | 26.5989 | 36.2642 | 35.9621 | 38.2368 | 38.16 | 38.0484 | 37.9442 | 37.4768 | 35.1274 | 32.9274 | 30.0611 | 29.3874 | 28.8063
|  | CENTRAL BRIDGE PRIMARY | HT |  |  |  |  | 44.0116 | 45.2095 | 45.1432 | 45.0547 | 44.9474 | 43.0284 | 40.6347 | 39.2232 | 38.2295 | 36.6105 | 35.8358 | 35.1389 | 35.0189 | 36.5642 | 36.4979 | 36.4095 | 36.2432 | 33.3937 | 30.5926 | 28.9484 | 27.7979 | 25.9389 | 25.0589 | 24.2695 | 36.2389 | 38.2916 | 38.2253 | 38.1368 | 37.8958 | 35.2463 | 32.64 | 31.0811 | 29.9684 | 28.1684 | 27.3158 | 26.5505
|  | CENTRAL BRIDGE PRIMARY | HE |  |  |  |  | 44.0189 | 43.9432 | 45.1347 | 45.0442 | 44.9147 | 44.7989 | 44.6884 | 43.5537 | 41.9916 | 39.3958 | 38.6116 | 38.2779 | 35.1053 | 34.8105 | 36.4895 | 36.3989 | 36.2695 | 36.1537 | 35.9463 | 34.06 | 32.2368 | 29.1747 | 28.2579 | 27.8695 | 36.3221 | 36.0368 | 38.2168 | 38.1263 | 37.9968 | 37.8811 | 37.6021 | 35.8442 | 34.1463 | 31.2958 | 30.4095 | 30.0347
|  | CENTRAL BRIDGE PRIMARY | FB |  |  |  |  | 44.0684 | 44.0221 | 43.9832 | 43.94 | 43.8926 | 43.8432 | 43.7916 | 43.7442 | 43.4926 | 40.8253 | 42.1137 | 41.7642 | 35.3211 | 35.1474 | 35.0284 | 34.8989 | 34.7495 | 34.5853 | 34.3863 | 34.1937 | 33.2021 | 30.0695 | 32.3263 | 31.9242 | 36.5305 | 36.3621 | 36.2474 | 36.1211 | 35.9758 | 35.8168 | 35.6242 | 35.4368 | 34.4832 | 31.4684 | 34.2516 | 33.8747
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS PRIMARY | MINIMUM HEADROOM | ST 66140 01039 | YES | YES | 0 | 4.3284 | 4.3063 | 4.2853 | 4.2632 | 4.2316 | 4.2063 | 4.1789 | 4.1516 | 4.1253 | 4.0453 | 3.9863 | 3.9389 | 4.0116 | 3.9874 | 3.9642 | 3.94 | 3.9074 | 3.88 | 3.8516 | 3.8221 | 3.7958 | 3.7084 | 3.6432 | 3.5895 | 3.9453 | 3.9211 | 3.8979 | 3.8737 | 3.8411 | 3.8137 | 3.7853 | 3.7558 | 3.7284 | 3.6411 | 3.5758 | 3.5221
|  | CERNE ABBAS PRIMARY | EE |  |  |  |  | 4.3284 | 4.3063 | 4.2853 | 4.2632 | 4.2316 | 4.2063 | 4.1789 | 4.1516 | 4.1263 | 4.08 | 4.0411 | 4.0105 | 4.0116 | 3.9874 | 3.9642 | 3.94 | 3.9074 | 3.88 | 3.8516 | 3.8221 | 3.7958 | 3.7421 | 3.6958 | 3.66 | 3.9453 | 3.9211 | 3.8979 | 3.8737 | 3.8411 | 3.8137 | 3.7853 | 3.7558 | 3.7284 | 3.6747 | 3.6295 | 3.5926
|  | CERNE ABBAS PRIMARY | HT |  |  |  |  | 4.3316 | 4.3137 | 4.2916 | 4.2674 | 4.24 | 4.2116 | 4.1832 | 4.1537 | 4.1253 | 4.0453 | 3.9863 | 3.9389 | 4.0158 | 3.9958 | 3.9716 | 3.9463 | 3.9179 | 3.8874 | 3.8579 | 3.8263 | 3.7958 | 3.7084 | 3.6432 | 3.5895 | 3.9495 | 3.9295 | 3.9053 | 3.8789 | 3.8505 | 3.82 | 3.7905 | 3.76 | 3.7295 | 3.6411 | 3.5758 | 3.5221
|  | CERNE ABBAS PRIMARY | HE |  |  |  |  | 4.3421 | 4.3263 | 4.3105 | 4.2895 | 4.2632 | 4.2411 | 4.2179 | 4.1947 | 4.1716 | 4.1611 | 4.1432 | 4.1305 | 4.0284 | 4.0116 | 3.9947 | 3.9726 | 3.9453 | 3.9221 | 3.8979 | 3.8737 | 3.8505 | 3.8358 | 3.8147 | 3.8 | 3.9621 | 3.9453 | 3.9284 | 3.9053 | 3.8789 | 3.8558 | 3.8316 | 3.8074 | 3.7832 | 3.7695 | 3.7474 | 3.7326
|  | CERNE ABBAS PRIMARY | FB |  |  |  |  | 4.3537 | 4.3421 | 4.3337 | 4.3253 | 4.3158 | 4.3053 | 4.2968 | 4.2874 | 4.2779 | 4.2421 | 4.2137 | 4.1916 | 4.0411 | 4.0284 | 4.0189 | 4.0095 | 3.9989 | 3.9874 | 3.9779 | 3.9674 | 3.9568 | 3.9168 | 3.8842 | 3.8579 | 3.9747 | 3.9621 | 3.9526 | 3.9432 | 3.9316 | 3.9211 | 3.9116 | 3.9 | 3.8905 | 3.8495 | 3.8168 | 3.7905
LOVEDEAN GSP |  | CHALCRAFT LANE PRIMARY | MINIMUM HEADROOM | TBC | NO | YES | 0 |  |  |  | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | EE | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | HT | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | HE | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE PRIMARY | FB | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
IVER 132KV GSP | CHALVEY BSP | CHALVEY PRIMARY | MINIMUM HEADROOM | SU 96669 79364 | NO | NO | 0 | 88.8853 | 88.4474 | 86.4453 | 84.4832 | 81.7789 | 79.8716 | 77.9232 | 74.8042 | 71.4326 | 64.1632 | 60.9579 | 58.0895 | 79.54 | 78.9863 | 76.4074 | 74.0516 | 70.7958 | 68.5653 | 66.2663 | 62.4947 | 58.3832 | 49.5874 | 45.8137 | 42.4347 | 84.2874 | 83.9084 | 83.4747 | 82.1253 | 79.0758 | 76.8463 | 74.5505 | 70.7842 | 66.68 | 57.8979 | 54.1284 | 50.7526
|  | CHALVEY PRIMARY | EE |  |  |  |  | 88.8853 | 88.4474 | 86.4453 | 84.4832 | 81.7789 | 79.8716 | 77.9232 | 75.4968 | 73.0516 | 67.6853 | 65.4474 | 63.54 | 79.54 | 78.9863 | 76.4074 | 74.0516 | 70.7958 | 68.5653 | 66.2663 | 63.3568 | 60.4232 | 53.7 | 50.9726 | 48.6389 | 84.2874 | 83.9084 | 83.4747 | 82.1253 | 79.0758 | 76.8463 | 74.5505 | 71.6463 | 68.7158 | 62.0042 | 59.2811 | 56.9505
|  | CHALVEY PRIMARY | HT |  |  |  |  | 88.9147 | 88.5063 | 86.5979 | 84.6358 | 82.5179 | 80.4916 | 78.1705 | 74.8042 | 71.4326 | 64.1632 | 60.9579 | 58.0895 | 79.5905 | 79.0726 | 76.6011 | 74.2484 | 71.7316 | 69.3547 | 66.5979 | 62.4947 | 58.3832 | 49.5874 | 45.8137 | 42.4347 | 84.3084 | 83.9547 | 83.4884 | 82.3074 | 79.9389 | 77.6347 | 74.8821 | 70.7842 | 66.68 | 57.8979 | 54.1284 | 50.7526
|  | CHALVEY PRIMARY | HE |  |  |  |  | 88.9663 | 88.5442 | 87.1358 | 85.2705 | 82.6263 | 80.8095 | 78.9905 | 76.6737 | 74.3347 | 70.3958 | 69 | 67.8126 | 79.6853 | 79.1747 | 77.2811 | 75.0505 | 71.8789 | 69.7589 | 67.6326 | 64.8674 | 62.0726 | 56.9937 | 55.2347 | 53.7316 | 84.3368 | 83.96 | 83.5295 | 82.9411 | 80.0716 | 78.0389 | 75.9158 | 73.1537 | 70.3632 | 65.2937 | 63.5389 | 62.0368
|  | CHALVEY PRIMARY | FB |  |  |  |  | 89.2905 | 89.0642 | 88.8484 | 88.6053 | 88.3137 | 87.4432 | 86.6263 | 85.6126 | 84.5042 | 81.1695 | 79.5558 | 78.2621 | 80.0684 | 79.7768 | 79.4758 | 79.1389 | 78.6958 | 77.6453 | 76.6568 | 75.4084 | 74.0453 | 69.9779 | 68.0284 | 66.4442 | 84.6316 | 84.4389 | 84.2653 | 84.0695 | 83.8537 | 83.6347 | 83.4221 | 83.2263 | 82.1305 | 78.26 | 76.3126 | 74.7305
NURSLING GSP | VELMORE BSP | CHANDLERS FORD PRIMARY | MINIMUM HEADROOM | SU 43494 21552 | NO | YES | 0 | 29.2847 | 29.0447 | 28.7711 | 28.3932 | 27.9363 | 27.4374 | 26.7195 | 25.6163 | 24.2784 | 20.9268 | 18.8279 | 16.9426 | 28.3616 | 27.7332 | 27.2384 | 26.6521 | 25.8553 | 24.9321 | 23.8384 | 22.5616 | 20.9805 | 17.1995 | 14.8521 | 12.7395 | 24.5974 | 23.9795 | 23.49 | 22.9089 | 22.1216 | 21.2089 | 20.1311 | 18.8742 | 17.3216 | 13.6195 | 11.3153 | 9.2437
|  | CHANDLERS FORD PRIMARY | EE |  |  |  |  | 29.2847 | 29.0447 | 28.7847 | 28.4332 | 27.9363 | 27.4784 | 27.0637 | 26.5153 | 25.5658 | 23.6647 | 22.2047 | 20.93 | 28.3616 | 27.7332 | 27.2384 | 26.6753 | 26.0016 | 25.2932 | 24.5184 | 23.6647 | 22.5668 | 20.2353 | 18.5689 | 17.11 | 24.5974 | 23.9795 | 23.49 | 22.9332 | 22.2626 | 21.5605 | 20.7963 | 19.9532 | 18.8732 | 16.6016 | 14.9721 | 13.5468
|  | CHANDLERS FORD PRIMARY | HT |  |  |  |  | 29.2942 | 29.0689 | 28.7711 | 28.3932 | 27.9363 | 27.4374 | 26.7195 | 25.6163 | 24.2784 | 20.9268 | 18.8279 | 16.9426 | 28.4626 | 27.8816 | 27.3553 | 26.6521 | 25.8553 | 24.9321 | 23.8384 | 22.5616 | 20.9805 | 17.1995 | 14.8521 | 12.7395 | 24.6963 | 24.1237 | 23.6037 | 22.9089 | 22.1216 | 21.2089 | 20.1311 | 18.8742 | 17.3216 | 13.6195 | 11.3153 | 9.2437
|  | CHANDLERS FORD PRIMARY | HE |  |  |  |  | 29.3532 | 29.1332 | 28.8963 | 28.5595 | 28.0847 | 27.6626 | 27.25 | 26.8289 | 26.4142 | 25.2468 | 24.3068 | 23.4111 | 28.6774 | 28.2353 | 27.8668 | 27.4058 | 26.8121 | 26.1984 | 25.5142 | 24.7553 | 23.7489 | 22.0847 | 20.8995 | 19.8468 | 24.95 | 24.47 | 24.1058 | 23.6479 | 23.0563 | 22.4479 | 21.7711 | 21.0216 | 20.03 | 18.41 | 17.2542 | 16.2268
|  | CHANDLERS FORD PRIMARY | FB |  |  |  |  | 29.5174 | 29.4132 | 29.3195 | 29.2142 | 29.0953 | 28.9774 | 28.8626 | 28.7553 | 28.6405 | 27.8974 | 26.9868 | 26.2153 | 28.8416 | 28.7037 | 28.4984 | 28.2795 | 28.0458 | 27.7795 | 27.4753 | 27.1353 | 26.6384 | 24.9889 | 23.8868 | 22.9374 | 25.2626 | 24.9342 | 24.7311 | 24.5163 | 24.2847 | 24.0226 | 23.7226 | 23.3889 | 22.9016 | 21.2847 | 20.2047 | 19.2763
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CHAPEL PRIMARY | MINIMUM HEADROOM | SU 42849 11983 | NO | YES | 0 | 26.2084 | 26.1674 | 26.1105 | 26.0326 | 25.8179 | 24.7663 | 23.9653 | 23.4295 | 22.8811 | 21.8853 | 21.2253 | 20.6168 | 22.7084 | 22.6137 | 22.4358 | 22.1768 | 21.7684 | 20.54 | 19.6074 | 18.9895 | 18.3758 | 17.2368 | 16.48 | 15.7853 | 24.14 | 24.0989 | 24.0411 | 23.9632 | 23.86 | 22.7495 | 21.8421 | 21.2389 | 20.6516 | 19.54 | 18.8021 | 18.1221
|  | CHAPEL PRIMARY | EE |  |  |  |  | 26.2084 | 26.1674 | 26.1221 | 26.0611 | 25.9737 | 25.8874 | 25.8021 | 24.8611 | 24.16 | 23.2789 | 22.7642 | 22.3137 | 22.7179 | 22.6368 | 22.5411 | 22.4337 | 22.2768 | 22.0779 | 21.8316 | 20.6768 | 19.86 | 18.8526 | 18.2568 | 17.7347 | 24.14 | 24.0989 | 24.0537 | 23.9916 | 23.9042 | 23.8168 | 23.7295 | 22.8779 | 22.0842 | 21.1137 | 20.5337 | 20.0253
|  | CHAPEL PRIMARY | HT |  |  |  |  | 26.2105 | 26.1684 | 26.1105 | 26.0326 | 25.8179 | 24.7663 | 23.9653 | 23.4295 | 22.8811 | 21.8853 | 21.2253 | 20.6168 | 22.7084 | 22.6137 | 22.4358 | 22.1768 | 21.7684 | 20.54 | 19.6074 | 18.9895 | 18.3758 | 17.2368 | 16.48 | 15.7853 | 24.1411 | 24.1 | 24.0411 | 23.9632 | 23.86 | 22.7495 | 21.8421 | 21.2389 | 20.6516 | 19.54 | 18.8021 | 18.1221
|  | CHAPEL PRIMARY | HE |  |  |  |  | 26.2147 | 26.1695 | 26.12 | 26.0516 | 25.9537 | 25.8621 | 25.7705 | 25.2621 | 24.5853 | 23.7253 | 23.4032 | 23.0779 | 22.7663 | 22.7 | 22.6158 | 22.5158 | 22.3579 | 22.1632 | 21.9526 | 21.16 | 20.3737 | 19.3558 | 18.98 | 18.5979 | 24.1463 | 24.1011 | 24.0516 | 23.9832 | 23.8853 | 23.7926 | 23.7011 | 23.3463 | 22.5811 | 21.5926 | 21.2274 | 20.8558
|  | CHAPEL PRIMARY | FB |  |  |  |  | 26.2474 | 26.22 | 26.1958 | 26.1684 | 26.1379 | 26.1063 | 26.0737 | 26.0421 | 25.9842 | 24.9874 | 24.7158 | 24.4284 | 22.8874 | 22.8326 | 22.7853 | 22.7379 | 22.6758 | 22.6095 | 22.52 | 22.4316 | 21.9968 | 20.7968 | 20.4863 | 20.1537 | 24.18 | 24.1526 | 24.1274 | 24.1 | 24.0695 | 24.0379 | 24.0042 | 23.9737 | 23.9137 | 23 | 22.6968 | 22.3726
COWLEY GSP | YARNTON BSP | CHARLBURY PRIMARY | MINIMUM HEADROOM | SP 36034 18376 | NO | YES | 0 | 15.7918 | 15.6266 | 15.3897 | 15.0887 | 14.6697 | 14.3718 | 14.0992 | 13.7876 | 13.4729 | 10.8476 | 10.0687 | 9.2592 | 13.7468 | 13.5668 | 13.3068 | 12.9753 | 12.5079 | 12.1889 | 11.8995 | 11.5616 | 11.2205 | 8.1879 | 7.3111 | 6.3921 | 14.6168 | 14.4368 | 14.1768 | 13.8453 | 13.38 | 13.0611 | 12.7716 | 12.4347 | 12.0937 | 9.0695 | 8.1937 | 7.2768
|  | CHARLBURY PRIMARY | EE |  |  |  |  | 15.7918 | 15.6266 | 15.4624 | 15.2729 | 14.9287 | 14.7087 | 14.4918 | 14.2697 | 14.0561 | 12.8592 | 12.3655 | 11.8445 | 13.7489 | 13.5689 | 13.3911 | 13.19 | 12.8142 | 12.5837 | 12.3542 | 12.1205 | 11.8942 | 10.5005 | 9.9363 | 9.3342 | 14.6189 | 14.4389 | 14.2611 | 14.0611 | 13.6853 | 13.4537 | 13.2242 | 12.9916 | 12.7663 | 11.3768 | 10.8137 | 10.2126
|  | CHARLBURY PRIMARY | HT |  |  |  |  | 15.7918 | 15.6266 | 15.3897 | 15.0887 | 14.6697 | 14.3718 | 14.0992 | 13.7876 | 13.4729 | 10.8476 | 10.0687 | 9.2592 | 13.7468 | 13.5668 | 13.3068 | 12.9753 | 12.5079 | 12.1889 | 11.8995 | 11.5616 | 11.2205 | 8.1879 | 7.3111 | 6.3921 | 14.6168 | 14.4368 | 14.1768 | 13.8453 | 13.38 | 13.0611 | 12.7716 | 12.4347 | 12.0937 | 9.0695 | 8.1937 | 7.2768
|  | CHARLBURY PRIMARY | HE |  |  |  |  | 15.9171 | 15.7971 | 15.6718 | 15.5171 | 15.1961 | 15.0055 | 14.8213 | 14.6329 | 14.4518 | 13.5255 | 13.2013 | 12.8245 | 13.8921 | 13.7637 | 13.6321 | 13.4689 | 13.1205 | 12.9226 | 12.7321 | 12.5374 | 12.3489 | 11.2521 | 10.8753 | 10.4332 | 14.7589 | 14.6326 | 14.5011 | 14.3379 | 13.9905 | 13.7937 | 13.6021 | 13.4074 | 13.22 | 12.1263 | 11.7495 | 11.3095
|  | CHARLBURY PRIMARY | FB |  |  |  |  | 16.0118 | 15.9192 | 15.8487 | 15.7761 | 15.6497 | 15.5687 | 15.4887 | 15.4139 | 15.335 | 15.0255 | 14.6992 | 14.3582 | 13.9942 | 13.8921 | 13.8153 | 13.7353 | 13.5942 | 13.5058 | 13.4195 | 13.3384 | 13.2521 | 12.9142 | 12.5447 | 12.1511 | 14.86 | 14.76 | 14.6842 | 14.6053 | 14.4642 | 14.3758 | 14.2895 | 14.2084 | 14.1221 | 13.7853 | 13.4158 | 13.0242
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER PRIMARY | MINIMUM HEADROOM | SY 67309 93186 | NO | YES | 0 | 16.4739 | 16.3655 | 16.2487 | 15.9571 | 15.3624 | 14.7087 | 14.0603 | 13.395 | 12.7318 | 11.0866 | 9.9961 | 9.0034 | 12.8416 | 12.5742 | 12.1711 | 11.6216 | 10.9563 | 10.2258 | 9.5016 | 8.7563 | 8.0132 | 6.1626 | 4.9332 | 3.8121 | 15.4716 | 15.2084 | 14.8137 | 14.2747 | 13.6232 | 12.9084 | 12.1979 | 11.4684 | 10.7389 | 8.8916 | 7.6642 | 6.5474
|  | CHARMINSTER PRIMARY | EE |  |  |  |  | 16.4739 | 16.3655 | 16.2497 | 16.0908 | 15.8403 | 15.4782 | 15.1139 | 14.7466 | 14.3887 | 13.4887 | 12.6982 | 12.0034 | 12.8416 | 12.5742 | 12.2805 | 11.9374 | 11.5205 | 11.1311 | 10.7353 | 10.3374 | 9.95 | 8.9163 | 8.0089 | 7.2111 | 15.4716 | 15.2084 | 14.92 | 14.5821 | 14.1705 | 13.7863 | 13.3979 | 13.0063 | 12.6232 | 11.6158 | 10.7305 | 9.9368
|  | CHARMINSTER PRIMARY | HT |  |  |  |  | 16.4813 | 16.3803 | 16.2487 | 15.9571 | 15.3624 | 14.7087 | 14.0603 | 13.395 | 12.7318 | 11.0866 | 9.9961 | 9.0034 | 12.8753 | 12.5784 | 12.1711 | 11.6216 | 10.9563 | 10.2258 | 9.5016 | 8.7563 | 8.0132 | 6.1626 | 4.9332 | 3.8121 | 15.5042 | 15.2126 | 14.8137 | 14.2747 | 13.6232 | 12.9084 | 12.1979 | 11.4684 | 10.7389 | 8.8916 | 7.6642 | 6.5474
|  | CHARMINSTER PRIMARY | HE |  |  |  |  | 16.5013 | 16.3992 | 16.2897 | 16.1361 | 15.9139 | 15.7213 | 15.495 | 15.1761 | 14.8634 | 14.3445 | 13.7855 | 13.2908 | 12.9995 | 12.7932 | 12.5521 | 12.2532 | 11.8658 | 11.5174 | 11.1742 | 10.8332 | 10.4984 | 9.8837 | 9.2311 | 8.6532 | 15.6263 | 15.4221 | 15.1853 | 14.8895 | 14.5084 | 14.1642 | 13.8253 | 13.4884 | 13.1579 | 12.5611 | 11.9274 | 11.3653
|  | CHARMINSTER PRIMARY | FB |  |  |  |  | 16.5761 | 16.5276 | 16.4824 | 16.4329 | 16.3771 | 16.3213 | 16.2676 | 16.2171 | 16.1634 | 15.6971 | 15.1834 | 14.7371 | 13.1426 | 12.9984 | 12.8763 | 12.7437 | 12.5974 | 12.4489 | 12.2984 | 12.1511 | 11.9974 | 11.3353 | 10.75 | 10.2363 | 15.7663 | 15.6253 | 15.5053 | 15.3747 | 15.2316 | 15.0853 | 14.9379 | 14.7937 | 14.6432 | 13.9947 | 13.4232 | 12.9221
LOVEDEAN GSP | CHICHESTER BSP | CHICHESTER PRIMARY | MINIMUM HEADROOM | SU 92198 07420 | NO | YES | 0.017895 | 12.6655 | 11.9097 | 27.6 | 26.5095 | 25.3505 | 24.0442 | 22.6653 | 22.9579 | 20.8337 | 10.2221 | 7.2747 | 4.5474 | 7.0068 | 6.1563 | 20.5347 | 19.3137 | 18.0221 | 16.5674 | 15.0232 | 15.4221 | 13.1442 | 2.0442 | -1.3095 | -4.4189 | 7.9305 | 7.08 | 21.9684 | 20.7474 | 19.4558 | 18 | 16.4558 | 16.8547 | 14.5758 | 4.1558 | 0.80105 | -2.3095
|  | CHICHESTER PRIMARY | EE |  |  |  |  | 12.6655 | 11.9097 | 27.6 | 26.7063 | 25.7811 | 24.8789 | 23.9242 | 22.9579 | 20.9611 | 16.0947 | 14.2074 | 12.3137 | 7.0068 | 6.1563 | 20.5347 | 19.5411 | 18.5305 | 17.5432 | 16.4884 | 15.4221 | 13.1442 | 8.7105 | 6.6137 | 4.4242 | 7.9305 | 7.08 | 21.9684 | 20.9747 | 19.9642 | 18.9758 | 17.9211 | 16.8547 | 14.5758 | 10.7832 | 8.7263 | 6.5368
|  | CHICHESTER PRIMARY | HT |  |  |  |  | 12.7413 | 11.9918 | 27.6032 | 26.5095 | 25.3505 | 24.0442 | 22.6653 | 24.4189 | 20.8337 | 10.2221 | 7.2747 | 4.5474 | 7.0932 | 6.2489 | 20.5389 | 19.3137 | 18.0221 | 16.5674 | 15.0232 | 18.3863 | 14.2505 | 2.0442 | -1.3095 | -4.4189 | 8.0179 | 7.1726 | 21.9737 | 20.7474 | 19.4558 | 18 | 16.4558 | 20.4632 | 16.3253 | 4.1558 | 0.80105 | -2.3095
|  | CHICHESTER PRIMARY | HE |  |  |  |  | 12.9413 | 12.2992 | 28.0853 | 27.2747 | 26.4074 | 25.5789 | 24.7042 | 23.8179 | 21.8989 | 17.6926 | 16.0232 | 14.4832 | 7.3258 | 6.6016 | 21.0895 | 20.1905 | 19.2463 | 18.3411 | 17.3789 | 16.4053 | 14.2179 | 10.5021 | 8.5526 | 6.7495 | 8.2505 | 7.5253 | 22.5242 | 21.6242 | 20.68 | 19.7737 | 18.8126 | 17.8389 | 15.6505 | 12.5758 | 10.6253 | 8.8221
|  | CHICHESTER PRIMARY | FB |  |  |  |  | 15.9813 | 13.135 | 29.2326 | 28.8821 | 28.5453 | 28.1926 | 27.7989 | 27.3958 | 27.0063 | 25.6011 | 24.2926 | 23.1137 | 10.6026 | 7.5595 | 22.3705 | 21.9758 | 21.5989 | 21.2042 | 20.76 | 20.3042 | 19.8653 | 18.2821 | 16.7821 | 15.4221 | 12.1095 | 8.4832 | 23.8053 | 23.4105 | 23.0337 | 22.6379 | 22.1937 | 21.7379 | 21.2989 | 19.7158 | 18.2147 | 16.8537
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL PRIMARY | MINIMUM HEADROOM | SY 65479 80511 | NO | YES | 0 | 14.6263 | 14.4484 | 14.2253 | 13.9126 | 13.54 | 13.1316 | 12.7263 | 10.4695 | 10.0432 | 7.1063 | 6.3579 | 5.6937 | 14.5168 | 14.3211 | 14.0747 | 13.7295 | 13.3158 | 12.8642 | 12.4168 | 9.7789 | 9.3063 | 5.9053 | 5.0663 | 4.32 | 14.54 | 14.3516 | 14.1074 | 13.7621 | 13.3505 | 12.9 | 12.4526 | 9.8189 | 9.3463 | 5.9505 | 5.1126 | 4.3663
|  | CHICKERELL PRIMARY | EE |  |  |  |  | 14.6263 | 14.4484 | 14.2611 | 14.0368 | 13.7663 | 13.5105 | 13.2453 | 12.0611 | 11.7968 | 10.2484 | 9.7032 | 9.2337 | 14.5168 | 14.3211 | 14.1179 | 13.8747 | 13.5863 | 13.3137 | 13.0253 | 11.6526 | 11.3684 | 9.5589 | 8.9326 | 8.3958 | 14.54 | 14.3516 | 14.1495 | 13.9074 | 13.6189 | 13.3463 | 13.0568 | 11.6863 | 11.4032 | 9.5947 | 8.9695 | 8.4316
|  | CHICKERELL PRIMARY | HT |  |  |  |  | 14.6516 | 14.4663 | 14.2253 | 13.9126 | 13.54 | 13.1316 | 12.7263 | 10.4695 | 10.0432 | 7.1063 | 6.3579 | 5.6937 | 14.5463 | 14.3411 | 14.0747 | 13.7295 | 13.3158 | 12.8642 | 12.4168 | 9.7789 | 9.3063 | 5.9053 | 5.0663 | 4.32 | 14.5674 | 14.3716 | 14.1074 | 13.7621 | 13.3505 | 12.9 | 12.4526 | 9.8189 | 9.3463 | 5.9505 | 5.1126 | 4.3663
|  | CHICKERELL PRIMARY | HE |  |  |  |  | 14.7368 | 14.6 | 14.4495 | 14.2579 | 14.0084 | 13.7853 | 13.5653 | 12.4263 | 12.2095 | 10.9968 | 10.6463 | 10.3421 | 14.6421 | 14.4947 | 14.3316 | 14.1263 | 13.8621 | 13.6253 | 13.3916 | 12.0716 | 11.8421 | 10.4053 | 9.9947 | 9.6389 | 14.6579 | 14.5158 | 14.36 | 14.1579 | 13.8947 | 13.6589 | 13.4253 | 12.1084 | 11.8779 | 10.4442 | 10.0347 | 9.6789
|  | CHICKERELL PRIMARY | FB |  |  |  |  | 14.8358 | 14.7411 | 14.6642 | 14.5811 | 14.4905 | 14.3979 | 14.3074 | 14.2168 | 14.1253 | 13.7326 | 13.3758 | 13.0684 | 14.7495 | 14.6442 | 14.5579 | 14.4663 | 14.3674 | 14.2653 | 14.1653 | 14.0663 | 13.9653 | 13.5274 | 13.12 | 12.7663 | 14.7611 | 14.6611 | 14.58 | 14.4926 | 14.3979 | 14.2968 | 14.1979 | 14.1 | 13.9989 | 13.5621 | 13.1558 | 12.8021
AXMINSTER GSP | YEOVIL BSP | CHILTON CANTELO PRIMARY | MINIMUM HEADROOM | ST 57910 21616 | NO | YES | 0 | 12.8245 | 12.6866 | 12.515 | 12.3666 | 12.1929 | 11.6108 | 9.215 | 8.6529 | 8.2561 | 5.6318 | 2.7982 | 1.3139 | 8.9089 | 8.7574 | 8.57 | 8.4132 | 8.2321 | 7.5689 | 4.7732 | 4.1353 | 3.69 | 0.65421 | -2.6489 | -4.3668 | 10.2547 | 10.1032 | 9.9158 | 9.7589 | 9.5779 | 8.9168 | 6.1263 | 5.4884 | 5.0442 | 2.0137 | -1.2832 | -2.9989
|  | CHILTON CANTELO PRIMARY | EE |  |  |  |  | 12.8245 | 12.7003 | 12.515 | 12.3666 | 12.1929 | 12.0266 | 10.9445 | 10.3182 | 9.7708 | 6.3034 | 5.2055 | 3.7424 | 8.9089 | 8.7742 | 8.57 | 8.4132 | 8.2321 | 8.0584 | 6.8047 | 6.0889 | 5.4647 | 1.3995 | 0.12263 | -1.59 | 10.2547 | 10.12 | 9.9158 | 9.7589 | 9.5779 | 9.4053 | 8.1537 | 7.4389 | 6.8158 | 2.7568 | 1.4832 | -0.22632
|  | CHILTON CANTELO PRIMARY | HT |  |  |  |  | 12.8466 | 12.6866 | 12.5582 | 12.4108 | 12.2476 | 11.6108 | 9.215 | 8.6529 | 8.2561 | 5.6318 | 2.7982 | 1.3139 | 8.9342 | 8.7574 | 8.6195 | 8.4647 | 8.2953 | 7.5689 | 4.7732 | 4.1353 | 3.69 | 0.65421 | -2.6489 | -4.3668 | 10.28 | 10.1032 | 9.9663 | 9.8105 | 9.6411 | 8.9168 | 6.1263 | 5.4884 | 5.0442 | 2.0137 | -1.2832 | -2.9989
|  | CHILTON CANTELO PRIMARY | HE |  |  |  |  | 12.9003 | 12.8076 | 12.6792 | 12.5161 | 12.3529 | 12.2087 | 11.1476 | 10.6718 | 10.1897 | 6.7582 | 5.7845 | 4.4287 | 8.9953 | 8.8984 | 8.7584 | 8.5847 | 8.4153 | 8.2668 | 7.0395 | 6.4995 | 5.9532 | 1.9111 | 0.77 | -0.82368 | 10.3411 | 10.2442 | 10.1042 | 9.9305 | 9.7621 | 9.6126 | 8.3874 | 7.8484 | 7.3032 | 3.2684 | 2.1295 | 0.53895
|  | CHILTON CANTELO PRIMARY | FB |  |  |  |  | 13.9487 | 13.8876 | 13.8424 | 12.8034 | 12.7287 | 12.6729 | 12.6182 | 12.5687 | 12.3192 | 11.2087 | 10.1729 | 8.9497 | 10.2679 | 10.1984 | 10.1468 | 8.8858 | 8.8037 | 8.7437 | 8.6837 | 8.63 | 8.3416 | 7.0542 | 5.8458 | 4.4142 | 11.6116 | 11.5411 | 11.4895 | 10.2326 | 10.1495 | 10.0895 | 10.0305 | 9.9768 | 9.6884 | 8.4032 | 7.1968 | 5.7684
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | CHINEHAM PRIMARY | MINIMUM HEADROOM | SU 65105 55805 | NO | YES | 0.73684 | 34.0979 | 33.9811 | 33.8505 | 33.6758 | 33.4379 | 33.0547 | 31.7274 | 30.4147 | 29.1505 | 27.1663 | 26.4895 | 25.6558 | 32.7453 | 32.5011 | 32.2558 | 31.88 | 31.2579 | 30.1674 | 28.5505 | 26.9505 | 25.4116 | 23.0421 | 22.2811 | 21.3337 | 32.0158 | 31.7768 | 31.5368 | 31.1684 | 30.5621 | 29.5042 | 27.9421 | 26.3958 | 24.9084 | 22.6116 | 21.8674 | 20.9253
|  | CHINEHAM PRIMARY | EE |  |  |  |  | 34.0979 | 33.9811 | 33.8505 | 33.6758 | 33.4379 | 33.2074 | 32.7811 | 31.5042 | 30.2726 | 27.8947 | 27.4979 | 26.9663 | 32.7453 | 32.5011 | 32.2558 | 31.9789 | 31.4695 | 30.7874 | 29.8821 | 28.3232 | 26.82 | 23.8505 | 23.3874 | 22.7516 | 32.0158 | 31.7768 | 31.5368 | 31.2621 | 30.7642 | 30.1 | 29.2221 | 27.7168 | 26.2642 | 23.4053 | 22.9537 | 22.3389
|  | CHINEHAM PRIMARY | HT |  |  |  |  | 34.1053 | 33.9989 | 33.8558 | 33.6768 | 33.46 | 33.0547 | 31.7274 | 30.4147 | 29.1505 | 27.1663 | 26.4895 | 25.6558 | 32.7968 | 32.58 | 32.2863 | 31.88 | 31.2579 | 30.1674 | 28.5505 | 26.9505 | 25.4116 | 23.0421 | 22.2811 | 21.3337 | 32.0663 | 31.8537 | 31.5653 | 31.1684 | 30.5621 | 29.5042 | 27.9421 | 26.3958 | 24.9084 | 22.6116 | 21.8674 | 20.9253
|  | CHINEHAM PRIMARY | HE |  |  |  |  | 34.1221 | 34.0105 | 33.8863 | 33.7137 | 33.4758 | 33.2568 | 33.0453 | 32.2105 | 31.3316 | 29.8747 | 28.6979 | 28.3095 | 32.9126 | 32.7337 | 32.5453 | 32.3126 | 31.8326 | 31.1916 | 30.3179 | 29.2042 | 28.1474 | 26.2979 | 24.8168 | 24.3305 | 32.1779 | 32.0011 | 31.8158 | 31.5863 | 31.1158 | 30.4905 | 29.6432 | 28.5642 | 27.5411 | 25.7653 | 24.3411 | 23.8737
|  | CHINEHAM PRIMARY | FB |  |  |  |  | 34.2074 | 34.1526 | 34.1042 | 34.0495 | 33.9884 | 33.9274 | 33.8674 | 33.8126 | 33.7526 | 32.4463 | 31.5032 | 30.9958 | 33.0611 | 32.9221 | 32.8189 | 32.7084 | 32.5179 | 32.2368 | 31.9453 | 31.5537 | 31.0095 | 29.3147 | 28.1516 | 27.5305 | 32.3232 | 32.1884 | 32.0874 | 31.9789 | 31.7926 | 31.5211 | 31.2379 | 30.8611 | 30.3358 | 28.6989 | 27.5768 | 26.9768
COWLEY GSP | YARNTON BSP | CHIPPING NORTON PRIMARY | MINIMUM HEADROOM | SP 31382 26792 | NO | YES | 0 | 18.475 | 18.3676 | 18.1487 | 17.755 | 16.9729 | 16.0897 | 14.9729 | 13.8571 | 12.7403 | 10.8824 | 10.015 | 9.1266 | 16.3637 | 16.1037 | 15.7374 | 15.2984 | 14.4047 | 13.3963 | 12.11 | 10.8384 | 9.5574 | 7.4479 | 6.4742 | 5.4721 | 17.2789 | 17.0179 | 16.6526 | 16.2126 | 15.3189 | 14.3105 | 13.0242 | 11.76 | 10.4779 | 8.3674 | 7.3926 | 6.3916
|  | CHIPPING NORTON PRIMARY | EE |  |  |  |  | 18.475 | 18.3676 | 18.2434 | 17.9866 | 17.5339 | 16.795 | 15.7939 | 14.8055 | 13.8624 | 12.3792 | 11.8087 | 11.2203 | 16.4005 | 16.1447 | 15.87 | 15.5711 | 15.0679 | 14.2258 | 13.0732 | 11.9363 | 10.85 | 9.1426 | 8.4932 | 7.8195 | 17.3147 | 17.0589 | 16.7853 | 16.4853 | 15.9821 | 15.14 | 13.9874 | 12.8495 | 11.7642 | 10.0632 | 9.4137 | 8.7379
|  | CHIPPING NORTON PRIMARY | HT |  |  |  |  | 18.4813 | 18.3729 | 18.1487 | 17.755 | 16.9729 | 16.0897 | 14.9729 | 13.8571 | 12.7403 | 10.8824 | 10.015 | 9.1266 | 16.3637 | 16.1037 | 15.7374 | 15.2984 | 14.4047 | 13.3963 | 12.11 | 10.8384 | 9.5574 | 7.4479 | 6.4742 | 5.4721 | 17.2789 | 17.0179 | 16.6526 | 16.2126 | 15.3189 | 14.3105 | 13.0242 | 11.76 | 10.4779 | 8.3674 | 7.3926 | 6.3916
|  | CHIPPING NORTON PRIMARY | HE |  |  |  |  | 18.5182 | 18.4255 | 18.3182 | 18.1718 | 17.7961 | 17.0792 | 16.1192 | 15.1739 | 14.2718 | 13.1234 | 12.7603 | 12.3476 | 16.5426 | 16.3405 | 16.1121 | 15.8479 | 15.37 | 14.5521 | 13.4468 | 12.3595 | 11.3226 | 9.9679 | 9.5489 | 9.0679 | 17.4579 | 17.2558 | 17.0263 | 16.7632 | 16.2842 | 15.4674 | 14.3611 | 13.2737 | 12.2368 | 10.8811 | 10.4621 | 9.9811
|  | CHIPPING NORTON PRIMARY | FB |  |  |  |  | 18.5792 | 18.5276 | 18.4813 | 18.4308 | 18.3634 | 18.2139 | 17.7803 | 17.3182 | 16.8434 | 15.7339 | 15.3497 | 14.9676 | 16.6626 | 16.5216 | 16.4026 | 16.2795 | 16.0953 | 15.8058 | 15.3026 | 14.7647 | 14.2132 | 12.9353 | 12.4984 | 12.0574 | 17.5768 | 17.4368 | 17.3179 | 17.1947 | 17.0095 | 16.7211 | 16.2168 | 15.68 | 15.1274 | 13.8495 | 13.4116 | 12.9716
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE PRIMARY | MINIMUM HEADROOM | SU 80226 89155 | NO | YES | 0 | 8.8653 | 8.8232 | 8.7811 | 8.7158 | 8.6389 | 8.5526 | 8.4663 | 8.3758 | 8.2863 | 8.0674 | 7.9253 | 7.8021 | 7.3316 | 7.2811 | 7.2305 | 7.1537 | 7.0621 | 6.9579 | 6.8526 | 6.7421 | 6.6305 | 6.3568 | 6.1768 | 6.02 | 8.8747 | 8.8474 | 8.7968 | 8.7168 | 8.6179 | 8.5032 | 8.3863 | 8.2621 | 8.1379 | 7.8295 | 7.6232 | 7.4453
|  | CHISBRIDGE PRIMARY | EE |  |  |  |  | 8.8653 | 8.8232 | 8.7811 | 8.7274 | 8.6621 | 8.6011 | 8.5411 | 8.4779 | 8.4158 | 8.3147 | 8.2211 | 8.1432 | 7.3316 | 7.2811 | 7.2305 | 7.1684 | 7.0989 | 7.0316 | 6.9632 | 6.8905 | 6.8211 | 6.68 | 6.5495 | 6.4389 | 8.8747 | 8.8474 | 8.7968 | 8.7326 | 8.6611 | 8.5916 | 8.5189 | 8.4411 | 8.3653 | 8.2 | 8.0463 | 7.9147
|  | CHISBRIDGE PRIMARY | HT |  |  |  |  | 8.8726 | 8.8337 | 8.7832 | 8.7158 | 8.6389 | 8.5526 | 8.4663 | 8.3758 | 8.2863 | 8.0674 | 7.9253 | 7.8021 | 7.3421 | 7.2958 | 7.2347 | 7.1537 | 7.0621 | 6.9579 | 6.8526 | 6.7421 | 6.6305 | 6.3568 | 6.1768 | 6.02 | 8.8768 | 8.8505 | 8.8021 | 8.7168 | 8.6179 | 8.5032 | 8.3863 | 8.2621 | 8.1379 | 7.8295 | 7.6232 | 7.4453
|  | CHISBRIDGE PRIMARY | HE |  |  |  |  | 8.8916 | 8.8611 | 8.8263 | 8.7842 | 8.7221 | 8.6684 | 8.6158 | 8.5611 | 8.5074 | 8.4821 | 8.4305 | 8.3895 | 7.3684 | 7.3326 | 7.2937 | 7.2474 | 7.1832 | 7.1263 | 7.0695 | 7.0095 | 6.9526 | 6.9084 | 6.8326 | 6.7695 | 8.8842 | 8.86 | 8.8326 | 8.7968 | 8.7411 | 8.6926 | 8.6368 | 8.5768 | 8.5179 | 8.4663 | 8.3758 | 8.2989
|  | CHISBRIDGE PRIMARY | FB |  |  |  |  | 8.9179 | 8.8958 | 8.8789 | 8.8611 | 8.8411 | 8.8211 | 8.8011 | 8.7811 | 8.7611 | 8.68 | 8.6179 | 8.5684 | 7.3989 | 7.3716 | 7.3505 | 7.3284 | 7.3042 | 7.2811 | 7.2568 | 7.2337 | 7.2095 | 7.1084 | 7.0242 | 6.9547 | 8.9021 | 8.8895 | 8.8789 | 8.8674 | 8.8537 | 8.84 | 8.8263 | 8.8011 | 8.7758 | 8.6674 | 8.5705 | 8.4874
MINETY GSP | TOOTHILL BSP | CHISLEDON PRIMARY | MINIMUM HEADROOM | SU 18894 79934 | NO | YES | 0 | 14.6561 | 14.2645 | 13.3476 | 12.1024 | 10.3087 | 8.6024 | 6.3108 | 4.2245 | 2.1813 | -2.8197 | -3.8176 | -4.2724 | 12.7637 | 12.3311 | 11.4363 | 10.0363 | 7.9489 | 5.9647 | 3.2942 | 0.86263 | -1.5174 | -7.3468 | -8.4921 | -9.0037 | 13.8 | 13.3011 | 12.2516 | 10.8032 | 8.7158 | 6.7305 | 4.0589 | 1.6263 | -0.75474 | -6.5853 | -7.7316 | -8.2421
|  | CHISLEDON PRIMARY | EE |  |  |  |  | 14.6561 | 14.2645 | 13.3476 | 12.1024 | 10.6897 | 9.1466 | 6.9834 | 4.9582 | 2.9529 | -2.6029 | -3.4555 | -3.7639 | 12.7637 | 12.3311 | 11.4363 | 10.0363 | 8.3942 | 6.5984 | 4.0732 | 1.7111 | -0.62789 | -7.1342 | -8.1237 | -8.4763 | 13.8 | 13.3011 | 12.2516 | 10.8032 | 9.1611 | 7.3642 | 4.8389 | 2.4758 | 0.13579 | -6.3726 | -7.3621 | -7.7158
|  | CHISLEDON PRIMARY | HT |  |  |  |  | 14.675 | 14.2929 | 13.3697 | 12.1192 | 10.3087 | 8.6024 | 6.3108 | 4.2245 | 2.1813 | -2.8197 | -3.8176 | -4.2724 | 12.7858 | 12.3595 | 11.4574 | 10.0574 | 7.9489 | 5.9647 | 3.2942 | 0.86263 | -1.5174 | -7.3468 | -8.4921 | -9.0037 | 13.8253 | 13.3326 | 12.2789 | 10.8242 | 8.7158 | 6.7305 | 4.0589 | 1.6263 | -0.75474 | -6.5853 | -7.7316 | -8.2421
|  | CHISLEDON PRIMARY | HE |  |  |  |  | 14.7266 | 14.375 | 13.4834 | 12.2624 | 10.8676 | 9.3287 | 7.1655 | 5.1392 | 3.1308 | -2.2113 | -2.9682 | -3.1976 | 12.8426 | 12.4395 | 11.5689 | 10.2153 | 8.5942 | 6.8016 | 4.2774 | 1.9132 | -0.43 | -6.6974 | -7.5816 | -7.8489 | 13.8884 | 13.4221 | 12.4042 | 10.9821 | 9.36 | 7.5674 | 5.0421 | 2.6768 | 0.33368 | -5.9358 | -6.8211 | -7.0884
|  | CHISLEDON PRIMARY | FB |  |  |  |  | 14.8676 | 14.6866 | 14.3424 | 13.8318 | 13.2761 | 12.7118 | 11.7697 | 10.7992 | 9.7297 | 5.835 | 5.255 | 5.0529 | 13.0037 | 12.7942 | 12.4089 | 11.9111 | 11.3689 | 10.73 | 9.6289 | 8.4942 | 7.2416 | 2.6847 | 2.0132 | 1.7816 | 14.0726 | 13.8305 | 13.3811 | 12.8011 | 12.1568 | 11.4968 | 10.3958 | 9.26 | 8.0074 | 3.4495 | 2.7768 | 2.5463
FLEET-BRAMLEY GSP | BRACKNELL BSP | CHOBHAM PRIMARY | MINIMUM HEADROOM | SU 97173 63223 | NO | YES | 0 | 26.1726 | 26.0505 | 25.9063 | 25.7116 | 25.4779 | 25.2221 | 24.9695 | 24.6842 | 24.0316 | 22.5379 | 21.6737 | 20.9189 | 24.2211 | 23.9684 | 23.7105 | 23.3632 | 22.8453 | 22.1737 | 21.4895 | 20.7663 | 20.0411 | 18.3768 | 17.4168 | 16.5779 | 24.58 | 24.3358 | 24.0853 | 23.7474 | 23.2495 | 22.6095 | 21.9558 | 21.2674 | 20.5779 | 18.9926 | 18.08 | 17.2821
|  | CHOBHAM PRIMARY | EE |  |  |  |  | 26.1726 | 26.0505 | 25.9126 | 25.7284 | 25.4842 | 25.2442 | 25.0221 | 24.7968 | 24.5726 | 24.4316 | 24.1747 | 23.6884 | 24.2211 | 23.9684 | 23.7105 | 23.4168 | 23.0832 | 22.7558 | 22.4242 | 22.0916 | 21.7632 | 20.9126 | 20.24 | 19.6842 | 24.58 | 24.3358 | 24.0853 | 23.7989 | 23.4695 | 23.1495 | 22.8263 | 22.5011 | 22.1811 | 21.3821 | 20.7484 | 20.2263
|  | CHOBHAM PRIMARY | HT |  |  |  |  | 26.1747 | 26.0579 | 25.9063 | 25.7116 | 25.4779 | 25.2221 | 24.9695 | 24.6842 | 24.0316 | 22.5379 | 21.6737 | 20.9189 | 24.2326 | 24.0358 | 23.7379 | 23.3632 | 22.8453 | 22.1737 | 21.4895 | 20.7663 | 20.0411 | 18.3768 | 17.4168 | 16.5779 | 24.6253 | 24.4 | 24.1116 | 23.7474 | 23.2495 | 22.6095 | 21.9558 | 21.2674 | 20.5779 | 18.9926 | 18.08 | 17.2821
|  | CHOBHAM PRIMARY | HE |  |  |  |  | 26.2 | 26.0895 | 25.96 | 25.7832 | 25.5453 | 25.3189 | 25.1 | 24.8789 | 24.6611 | 24.6789 | 24.6516 | 24.6358 | 24.2632 | 24.1495 | 24.0168 | 23.7779 | 23.4789 | 23.2 | 22.9305 | 22.6632 | 22.3968 | 21.9853 | 21.5716 | 21.2337 | 24.7463 | 24.5705 | 24.3789 | 24.1411 | 23.8453 | 23.5695 | 23.3042 | 23.0389 | 22.7758 | 22.3937 | 22.0084 | 21.6947
|  | CHOBHAM PRIMARY | FB |  |  |  |  | 26.2937 | 26.24 | 26.1937 | 26.1411 | 26.0832 | 26.0221 | 25.9663 | 25.9126 | 25.8558 | 25.6463 | 25.5305 | 25.4589 | 24.36 | 24.3021 | 24.2537 | 24.1979 | 24.0863 | 23.9695 | 23.8621 | 23.7526 | 23.6463 | 23.1642 | 22.5874 | 22.1842 | 24.9021 | 24.7674 | 24.6695 | 24.5611 | 24.4484 | 24.3347 | 24.2316 | 24.1253 | 24.0221 | 23.5579 | 23.0147 | 22.6358
COWLEY GSP | DRAYTON BSP | CHOLSEY PRIMARY | MINIMUM HEADROOM | SU 58223 84685 | NO | YES | 0 | 13.7887 | 13.6466 | 13.4708 | 13.2603 | 13.0476 | 12.8655 | 12.6876 | 12.4992 | 12.3297 | 11.8487 | 11.5203 | 11.1961 | 13.6026 | 13.3005 | 12.9468 | 12.5353 | 12.2626 | 11.9974 | 11.7542 | 11.4942 | 11.2395 | 10.4353 | 9.8637 | 9.2195 | 14.0537 | 13.7516 | 13.3979 | 12.9863 | 12.7137 | 12.4484 | 12.2053 | 11.9453 | 11.6905 | 10.8863 | 10.3147 | 9.6705
|  | CHOLSEY PRIMARY | EE |  |  |  |  | 13.7887 | 13.6655 | 13.4971 | 13.2992 | 13.0476 | 12.8655 | 12.6876 | 12.4992 | 12.3297 | 12.0561 | 11.8329 | 11.6392 | 13.6437 | 13.4553 | 13.1174 | 12.7353 | 12.2826 | 12.0532 | 11.8184 | 11.5732 | 11.3511 | 10.8468 | 10.4321 | 10.0226 | 14.0947 | 13.9053 | 13.5663 | 13.1842 | 12.7326 | 12.5021 | 12.2663 | 12.0189 | 11.7958 | 11.2895 | 10.8716 | 10.4621
|  | CHOLSEY PRIMARY | HT |  |  |  |  | 13.7918 | 13.6466 | 13.4708 | 13.2603 | 13.0718 | 12.8855 | 12.7024 | 12.5182 | 12.3392 | 11.8487 | 11.5203 | 11.1961 | 13.6026 | 13.3005 | 12.9468 | 12.5353 | 12.2626 | 11.9974 | 11.7542 | 11.4942 | 11.2395 | 10.4353 | 9.8637 | 9.2195 | 14.0537 | 13.7516 | 13.3979 | 12.9863 | 12.7137 | 12.4484 | 12.2053 | 11.9453 | 11.6905 | 10.8863 | 10.3147 | 9.6705
|  | CHOLSEY PRIMARY | HE |  |  |  |  | 13.8803 | 13.7992 | 13.6855 | 13.5371 | 13.3361 | 13.1539 | 13.015 | 12.8708 | 12.7287 | 12.695 | 12.6255 | 12.5582 | 13.8089 | 13.6911 | 13.4626 | 13.1858 | 12.8395 | 12.5079 | 12.3395 | 12.1647 | 11.9942 | 11.8447 | 11.6563 | 11.4437 | 14.2621 | 14.1442 | 13.9158 | 13.6389 | 13.2937 | 12.9632 | 12.7947 | 12.62 | 12.4495 | 12.3011 | 12.1126 | 11.9
|  | CHOLSEY PRIMARY | FB |  |  |  |  | 13.9403 | 13.8908 | 13.8497 | 13.7918 | 13.7287 | 13.6624 | 13.5961 | 13.5508 | 13.5034 | 13.3213 | 13.2003 | 13.1055 | 13.9016 | 13.8089 | 13.7395 | 13.6111 | 13.4753 | 13.33 | 13.1763 | 13.1005 | 13.0247 | 12.7153 | 12.4616 | 12.2268 | 14.3537 | 14.2621 | 14.1916 | 14.0642 | 13.9284 | 13.7832 | 13.6295 | 13.5547 | 13.4789 | 13.1705 | 12.9168 | 12.6832
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH PRIMARY | MINIMUM HEADROOM | SZ 15698 93141 | NO | YES | 0.46316 | 33.6426 | 32.9668 | 31.9711 | 31.0995 | 30.6721 | 29.6195 | 28.3289 | 26.9163 | 25.5184 | 21.3016 | 9.4279 | 1.5732 | 29.8695 | 29.0937 | 27.9211 | 26.94 | 26.5505 | 25.4368 | 23.9768 | 22.4116 | 20.8621 | 16.1179 | 2.2042 | -6.9874 | 33.3674 | 33.0768 | 32.2263 | 31.2358 | 30.8495 | 29.5042 | 28.0295 | 26.4474 | 24.8811 | 20.0768 | 5.9337 | -3.3853
|  | CHRISTCHURCH PRIMARY | EE |  |  |  |  | 33.6426 | 32.9668 | 32.0647 | 31.4363 | 30.6721 | 29.9321 | 29.2142 | 28.4711 | 28.6068 | 21.9068 | 15.7321 | 7.8184 | 29.8695 | 29.0937 | 28.0389 | 27.3579 | 26.5505 | 25.7632 | 24.9926 | 24.1937 | 24.5653 | 16.6158 | 9.3642 | 0.038947 | 33.3674 | 33.0768 | 32.3453 | 31.66 | 30.8495 | 30.0579 | 29.2821 | 28.4789 | 28.6453 | 20.5642 | 13.1916 | 3.7074
|  | CHRISTCHURCH PRIMARY | HT |  |  |  |  | 33.7226 | 32.9984 | 31.9711 | 31.0995 | 30.9542 | 29.6195 | 28.3289 | 26.9163 | 25.5184 | 21.3016 | 9.4279 | 1.5732 | 29.9653 | 29.1232 | 27.9211 | 26.94 | 26.9632 | 25.4368 | 23.9768 | 22.4116 | 20.8621 | 16.1179 | 2.2042 | -6.9874 | 33.3863 | 33.1158 | 32.2263 | 31.2358 | 31.0474 | 29.5042 | 28.0295 | 26.4474 | 24.8811 | 20.0768 | 5.9337 | -3.3853
|  | CHRISTCHURCH PRIMARY | HE |  |  |  |  | 34.0016 | 33.4595 | 32.6732 | 32.1353 | 31.4353 | 30.7826 | 30.1721 | 29.5405 | 29.7868 | 24.0974 | 18.5089 | 11.0911 | 30.3011 | 29.6895 | 28.7768 | 28.2074 | 27.4789 | 26.7947 | 26.1589 | 25.5 | 26.0105 | 19.1032 | 12.5011 | 3.7253 | 33.4474 | 33.1737 | 32.8726 | 32.4516 | 31.7916 | 31.1053 | 30.4674 | 29.8053 | 30.1126 | 23.0842 | 16.3684 | 7.44
|  | CHRISTCHURCH PRIMARY | FB |  |  |  |  | 34.3363 | 33.9795 | 33.5995 | 33.3574 | 33.0995 | 32.8426 | 32.5932 | 32.3584 | 32.1174 | 30.8153 | 25.0637 | 18.3868 | 30.6716 | 30.2568 | 29.8084 | 29.5389 | 29.2516 | 28.9674 | 28.6905 | 28.4305 | 28.1642 | 26.7253 | 19.8979 | 12.0211 | 33.6453 | 33.5126 | 33.3926 | 33.2589 | 33.1105 | 32.96 | 32.8137 | 32.6789 | 32.4768 | 30.8011 | 23.86 | 15.8484
LALEHAM GSP | EAST BEDFONT BSP | CHURCH ROAD PRIMARY | MINIMUM HEADROOM | TQ 06820 71722 | NO | YES | 0 | 15.1253 | 14.9189 | 14.6789 | 14.3747 | 13.8905 | 13.2747 | 12.6505 | 12.0074 | 11.3179 | 9.4758 | 8.0474 | 6.7747 | 14.4811 | 14.1442 | 13.7158 | 13.2716 | 12.7189 | 12.0832 | 11.4989 | 10.8989 | 10.2621 | 8.5716 | 7.1989 | 5.7884 | 14.6116 | 14.4274 | 14.2189 | 13.9379 | 13.5568 | 13.1589 | 12.4979 | 11.8158 | 11.08 | 9.0863 | 7.5053 | 6.0947
|  | CHURCH ROAD PRIMARY | EE |  |  |  |  | 15.1253 | 14.9189 | 14.6789 | 14.3821 | 13.9547 | 13.5189 | 13.0926 | 12.6253 | 12.1453 | 11.3137 | 10.3579 | 9.5347 | 14.4811 | 14.1442 | 13.7158 | 13.3137 | 12.8263 | 12.3589 | 11.8947 | 11.4242 | 10.9674 | 10.2337 | 9.3989 | 8.6842 | 14.6116 | 14.4274 | 14.2189 | 13.94 | 13.5568 | 13.1916 | 12.8526 | 12.5053 | 12.0168 | 11.0958 | 10.0274 | 9.0874
|  | CHURCH ROAD PRIMARY | HT |  |  |  |  | 15.1453 | 14.9442 | 14.6905 | 14.3747 | 13.8905 | 13.2747 | 12.6505 | 12.0074 | 11.3179 | 9.4758 | 8.0474 | 6.7747 | 14.5442 | 14.1663 | 13.7495 | 13.2716 | 12.7189 | 12.0832 | 11.4989 | 10.8989 | 10.2621 | 8.5716 | 7.1989 | 5.7884 | 14.6242 | 14.4526 | 14.2274 | 13.9379 | 13.5926 | 13.1589 | 12.4979 | 11.8158 | 11.08 | 9.0863 | 7.5053 | 6.0947
|  | CHURCH ROAD PRIMARY | HE |  |  |  |  | 15.1884 | 15 | 14.7832 | 14.5021 | 14.1179 | 13.7653 | 13.4179 | 13.0684 | 12.7211 | 12.6232 | 12.1063 | 11.5905 | 14.6874 | 14.4284 | 14.0737 | 13.7284 | 13.2832 | 12.8737 | 12.4705 | 12.0674 | 11.6674 | 11.4547 | 10.9516 | 10.5137 | 14.6505 | 14.4747 | 14.2811 | 14.0105 | 13.6368 | 13.2937 | 12.9558 | 12.6147 | 12.2758 | 12.3158 | 11.9579 | 11.3716
|  | CHURCH ROAD PRIMARY | FB |  |  |  |  | 15.34 | 15.2379 | 15.1505 | 15.0484 | 14.9421 | 14.8337 | 14.7295 | 14.6316 | 14.5274 | 14.1095 | 13.5674 | 12.9884 | 14.9295 | 14.7421 | 14.5989 | 14.4095 | 14.2463 | 14.0811 | 13.9211 | 13.7674 | 13.6095 | 12.98 | 12.3779 | 11.8726 | 14.7874 | 14.7 | 14.6211 | 14.5337 | 14.4368 | 14.3389 | 14.2432 | 14.1547 | 14.06 | 13.7116 | 13.4484 | 12.8032
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN PRIMARY | MINIMUM HEADROOM | SP 02761 00827 | NO | YES | 1.0979 | 23.5263 | 23.3347 | 41.0505 | 40.0695 | 39.0358 | 37.9253 | 36.8232 | 35.6516 | 34.4832 | 29.7074 | 23.9989 | 22.8032 | 20.8326 | 20.2263 | 35.5442 | 34.3789 | 33.2011 | 31.9358 | 30.6821 | 29.3453 | 28.0105 | 22.4874 | 15.7053 | 14.3232 | 21.7232 | 21.1305 | 37.6684 | 36.5126 | 35.3368 | 34.0747 | 32.8242 | 31.4905 | 30.1589 | 24.6516 | 17.8905 | 16.5126
|  | CIRENCESTER TOWN PRIMARY | EE |  |  |  |  | 23.5263 | 23.3347 | 41.0526 | 40.2705 | 39.5137 | 38.7684 | 38.0116 | 37.2158 | 36.4337 | 29.8326 | 23.9989 | 22.8032 | 20.8326 | 20.2263 | 35.5505 | 34.6105 | 33.7589 | 32.9189 | 32.0632 | 31.1642 | 30.28 | 22.5453 | 15.7053 | 14.3232 | 21.7232 | 21.1305 | 37.6726 | 36.7442 | 35.8947 | 35.0579 | 34.2032 | 33.3053 | 32.4232 | 24.7105 | 17.8905 | 16.5126
|  | CIRENCESTER TOWN PRIMARY | HT |  |  |  |  | 23.5442 | 23.3811 | 41.0505 | 40.0695 | 39.0358 | 37.9253 | 36.8232 | 35.6516 | 34.4832 | 29.7074 | 28.2179 | 26.5832 | 20.8947 | 20.2832 | 35.5442 | 34.3789 | 33.2011 | 31.9358 | 30.6821 | 29.3453 | 28.0105 | 22.4874 | 20.7958 | 18.9263 | 21.7842 | 21.1874 | 37.6684 | 36.5126 | 35.3368 | 34.0747 | 32.8242 | 31.4905 | 30.1589 | 24.6516 | 22.9663 | 21.1011
|  | CIRENCESTER TOWN PRIMARY | HE |  |  |  |  | 23.5905 | 23.4632 | 41.3747 | 40.7263 | 39.8705 | 39.16 | 38.4684 | 37.7442 | 37.0305 | 30.8937 | 25.3442 | 24.3979 | 21.0547 | 20.5568 | 35.9768 | 35.1337 | 34.1653 | 33.3642 | 32.5863 | 31.7695 | 30.9642 | 23.7474 | 17.2242 | 16.1179 | 21.9411 | 21.4547 | 38.0905 | 37.2663 | 36.3 | 35.5011 | 34.7242 | 33.9105 | 33.1063 | 25.9116 | 19.4084 | 18.3042
|  | CIRENCESTER TOWN PRIMARY | FB |  |  |  |  | 23.6663 | 23.5905 | 41.8179 | 41.6832 | 41.3905 | 41.1274 | 40.8547 | 40.5063 | 40.14 | 38.5789 | 37.1758 | 36.4411 | 21.2663 | 20.9663 | 36.7411 | 36.3684 | 35.9789 | 35.6316 | 35.2705 | 34.8716 | 34.4516 | 32.6537 | 31.0253 | 30.1737 | 22.1495 | 21.8547 | 38.8379 | 38.4737 | 38.0937 | 37.7547 | 37.4021 | 37.0063 | 36.5863 | 34.7937 | 33.1695 | 32.3211
IVER 132KV GSP | CIPPENHAM BSP | CLARENCE ROAD PRIMARY | MINIMUM HEADROOM | SU 95654 76652 | NO | NO | 0 | 59.8168 | 59.5116 | 59.16 | 58.6716 | 58.0632 | 57.4326 | 56.7842 | 56.1474 | 54.2032 | 49.3789 | 46.6 | 44.0705 | 57.5326 | 57.2274 | 56.8716 | 56.34 | 55.7053 | 55.0105 | 53.5905 | 51.1695 | 48.8 | 43.3526 | 40.2484 | 37.4168 | 57.9358 | 57.6305 | 57.2789 | 56.7895 | 56.1821 | 55.5516 | 54.3558 | 51.9758 | 49.6053 | 44.1568 | 41.0516 | 38.2189
|  | CLARENCE ROAD PRIMARY | EE |  |  |  |  | 59.8168 | 59.5116 | 59.1632 | 58.6937 | 58.0632 | 57.4453 | 56.8663 | 56.2737 | 55.6853 | 55.0747 | 53.2726 | 51.5895 | 57.5326 | 57.2274 | 56.8726 | 56.3768 | 55.7053 | 55.0568 | 54.4358 | 53.8189 | 52.7379 | 50.0421 | 47.8147 | 45.8674 | 57.9358 | 57.6305 | 57.2811 | 56.8126 | 56.1821 | 55.5642 | 54.9853 | 54.3916 | 53.4968 | 50.8474 | 48.6189 | 46.6705
|  | CLARENCE ROAD PRIMARY | HT |  |  |  |  | 59.8295 | 59.54 | 59.16 | 58.6716 | 58.0821 | 57.4326 | 56.7842 | 56.1474 | 54.2032 | 49.3789 | 46.6 | 44.0705 | 57.5453 | 57.2558 | 56.8716 | 56.34 | 55.7084 | 55.0105 | 53.5905 | 51.1695 | 48.8 | 43.3526 | 40.2484 | 37.4168 | 57.9484 | 57.6589 | 57.2789 | 56.7895 | 56.2011 | 55.5516 | 54.3558 | 51.9758 | 49.6053 | 44.1568 | 41.0516 | 38.2189
|  | CLARENCE ROAD PRIMARY | HE |  |  |  |  | 59.8695 | 59.5695 | 59.2263 | 58.7579 | 58.1211 | 57.5189 | 56.9316 | 56.3326 | 55.7453 | 55.7779 | 55.6863 | 55.1884 | 57.5853 | 57.2853 | 56.9421 | 56.4737 | 55.8232 | 55.1937 | 54.5726 | 53.9484 | 53.3432 | 52.8032 | 51.3337 | 50.0326 | 57.9884 | 57.6884 | 57.3453 | 56.8768 | 56.24 | 55.6379 | 55.0505 | 54.4516 | 53.8642 | 53.5632 | 52.1295 | 50.8389
|  | CLARENCE ROAD PRIMARY | FB |  |  |  |  | 60.1 | 59.9495 | 59.8137 | 59.6611 | 59.4916 | 59.3211 | 59.1547 | 59 | 58.8347 | 58.2284 | 57.8884 | 57.6705 | 57.8158 | 57.6653 | 57.5295 | 57.3768 | 57.2074 | 57.0368 | 56.8526 | 56.6832 | 56.5042 | 55.8558 | 55.4516 | 54.4895 | 58.2189 | 58.0684 | 57.9326 | 57.78 | 57.6105 | 57.44 | 57.2737 | 57.1189 | 56.9537 | 56.3474 | 56.0074 | 55.2547
MELKSHAM GSP | CHIPPENHAM BSP | COCKLEBURY PRIMARY | MINIMUM HEADROOM | ST 92447 73890 | NO | YES | 0 | 41.8011 | 41.0316 | 40.2274 | 39.5895 | 38.9105 | 37.9495 | 36.8695 | 35.7158 | 34.4937 | 31.3747 | 29.6337 | 28.0726 | 36.1189 | 35.3389 | 34.6116 | 34.0179 | 33.3832 | 32.4958 | 31.5063 | 30.4516 | 29.2116 | 25.9537 | 24.1358 | 22.5053 | 38.58 | 37.9632 | 37.38 | 36.7242 | 36.0137 | 34.9989 | 33.8547 | 32.6295 | 31.3295 | 27.8053 | 25.8442 | 24.0853
|  | COCKLEBURY PRIMARY | EE |  |  |  |  | 41.8011 | 41.0316 | 40.2274 | 39.6389 | 39.0642 | 38.3116 | 37.4789 | 36.6474 | 35.8189 | 33.6063 | 32.3326 | 31.2316 | 36.1189 | 35.3389 | 34.6116 | 34.0653 | 33.5179 | 32.8179 | 32.0505 | 31.2832 | 30.52 | 28.2758 | 26.9379 | 25.7821 | 38.58 | 37.9632 | 37.38 | 36.7768 | 36.1821 | 35.3916 | 34.5095 | 33.6305 | 32.7547 | 30.2989 | 28.8411 | 27.5779
|  | COCKLEBURY PRIMARY | HT |  |  |  |  | 41.8232 | 41.1242 | 40.2832 | 39.5895 | 38.9105 | 37.9495 | 36.8695 | 35.7158 | 34.4937 | 31.3747 | 29.6337 | 28.0726 | 36.1779 | 35.4232 | 34.66 | 34.0179 | 33.3832 | 32.4958 | 31.5063 | 30.4516 | 29.2116 | 25.9537 | 24.1358 | 22.5053 | 38.6263 | 38.0295 | 37.4147 | 36.7242 | 36.0137 | 34.9989 | 33.8547 | 32.6295 | 31.3295 | 27.8053 | 25.8442 | 24.0853
|  | COCKLEBURY PRIMARY | HE |  |  |  |  | 41.8863 | 41.3421 | 40.6084 | 40.0768 | 39.5379 | 38.8411 | 38.0905 | 37.3432 | 36.5968 | 35.0516 | 34.16 | 33.3853 | 36.3242 | 35.62 | 34.9547 | 34.4579 | 33.9432 | 33.2947 | 32.6 | 31.9063 | 31.2158 | 29.7874 | 28.8453 | 28.0274 | 38.7442 | 38.1874 | 37.6526 | 37.2232 | 36.6895 | 35.9579 | 35.1674 | 34.38 | 33.5947 | 31.9126 | 30.9032 | 30.0011
|  | COCKLEBURY PRIMARY | FB |  |  |  |  | 42.0253 | 41.8842 | 41.6095 | 41.4 | 41.1737 | 40.8474 | 40.5284 | 40.2011 | 39.8537 | 38.4621 | 37.6326 | 36.9168 | 36.5642 | 36.1779 | 35.8695 | 35.6758 | 35.4674 | 35.1695 | 34.88 | 34.5832 | 34.2684 | 33.0095 | 32.2611 | 31.6189 | 38.9505 | 38.6474 | 38.4021 | 38.24 | 38.0642 | 37.8232 | 37.5884 | 37.3495 | 37 | 35.5116 | 34.6242 | 33.8537
MELKSHAM GSP | FROME BSP | CODFORD PRIMARY | MINIMUM HEADROOM | ST 97372 39559 | YES | YES | 0 | 4.6632 | 4.4642 | 4.24 | 4.0211 | 3.8032 | 3.62 | 3.3895 | 1.9642 | 1.7832 | 0.22737 | -1.7074 | -2.1021 | 4.6232 | 4.4137 | 4.1779 | 3.9495 | 3.7211 | 3.5305 | 3.2895 | 1.6316 | 1.4432 | -0.41789 | -2.48 | -2.8989 | 4.5716 | 4.3611 | 4.1232 | 3.8916 | 3.66 | 3.4674 | 3.2232 | 1.5684 | 1.3747 | -0.53789 | -2.6674 | -3.1
|  | CODFORD PRIMARY | EE |  |  |  |  | 4.6632 | 4.4642 | 4.24 | 4.0211 | 3.8032 | 3.62 | 3.3895 | 1.9642 | 1.7832 | 1.1011 | -1.7074 | -2.1021 | 4.6232 | 4.4137 | 4.1779 | 3.9495 | 3.7211 | 3.5305 | 3.2895 | 1.6316 | 1.4432 | 0.76947 | -2.48 | -2.8989 | 4.5716 | 4.3611 | 4.1232 | 3.8916 | 3.66 | 3.4674 | 3.2232 | 1.5684 | 1.3747 | 0.58947 | -2.6674 | -3.1
|  | CODFORD PRIMARY | HT |  |  |  |  | 4.7463 | 4.5758 | 4.4011 | 4.2063 | 4.7368 | 4.6463 | 4.5463 | 2.0705 | 1.9811 | 0.22737 | -0.097895 | -0.39474 | 4.7116 | 4.5316 | 4.3474 | 4.1411 | 4.8274 | 4.7305 | 4.6232 | 1.7053 | 1.6084 | -0.41789 | -0.76737 | -1.0853 | 4.6611 | 4.48 | 4.2958 | 4.0905 | 4.7105 | 4.6137 | 4.5053 | 1.5863 | 1.4895 | -0.53789 | -0.89368 | -1.2189
|  | CODFORD PRIMARY | HE |  |  |  |  | 4.9337 | 4.9042 | 4.8747 | 4.8358 | 4.7863 | 4.7421 | 4.6979 | 3.4874 | 3.4432 | 3.3789 | 0.99789 | 0.92632 | 4.9084 | 4.8768 | 4.8442 | 4.8042 | 4.7526 | 4.7074 | 4.6611 | 3.2168 | 3.1716 | 3.1421 | 0.33789 | 0.25474 | 4.8611 | 4.8316 | 4.8021 | 4.7642 | 4.7147 | 4.6705 | 4.6263 | 3.2189 | 3.1737 | 3.0547 | 0.25895 | 0.17474
|  | CODFORD PRIMARY | FB |  |  |  |  | 4.9589 | 4.9379 | 4.9211 | 4.9053 | 4.8863 | 4.8684 | 4.8516 | 4.8347 | 4.8189 | 4.7432 | 5.3432 | 5.2832 | 4.9358 | 4.9116 | 4.8937 | 4.8747 | 4.8547 | 4.8358 | 4.8158 | 4.7979 | 4.78 | 4.6947 | 5.4379 | 5.3653 | 4.8853 | 4.8653 | 4.8495 | 4.8326 | 4.8147 | 4.7968 | 4.78 | 4.7632 | 4.7474 | 4.6726 | 5.3537 | 5.28
IVER 132KV GSP | DENHAM BSP | COKES LANE PRIMARY | MINIMUM HEADROOM | SU 99240 97483 | NO | NO | 0 | 14.5568 | 14.4842 | 14.3958 | 14.2768 | 14.0695 | 13.84 | 13.6074 | 13.3579 | 13.1084 | 12.4979 | 12.0979 | 11.7463 | 12.8084 | 12.6221 | 12.4295 | 12.2621 | 12.0579 | 11.8337 | 11.6074 | 11.3726 | 11.1379 | 10.5642 | 10.1895 | 9.8621 | 13.0558 | 12.8316 | 12.6011 | 12.4158 | 12.1863 | 11.9337 | 11.6779 | 11.4105 | 11.1432 | 10.4853 | 10.0516 | 9.6716
|  | COKES LANE PRIMARY | EE |  |  |  |  | 14.5568 | 14.4842 | 14.4032 | 14.3063 | 14.1611 | 14.0084 | 13.8505 | 13.6874 | 13.5316 | 13.2337 | 12.9737 | 12.7632 | 12.8084 | 12.6221 | 12.4295 | 12.2989 | 12.1474 | 11.9958 | 11.8389 | 11.6779 | 11.5242 | 11.2463 | 11.0095 | 10.8179 | 13.0558 | 12.8316 | 12.6011 | 12.46 | 12.2989 | 12.1389 | 11.9684 | 11.7937 | 11.6263 | 11.2884 | 10.9979 | 10.7642
|  | COKES LANE PRIMARY | HT |  |  |  |  | 14.5568 | 14.4874 | 14.3958 | 14.2768 | 14.0695 | 13.84 | 13.6074 | 13.3579 | 13.1084 | 12.4979 | 12.0979 | 11.7463 | 12.8242 | 12.6463 | 12.4326 | 12.2621 | 12.0579 | 11.8337 | 11.6074 | 11.3726 | 11.1379 | 10.5642 | 10.1895 | 9.8621 | 13.0768 | 12.8632 | 12.6074 | 12.4158 | 12.1863 | 11.9337 | 11.6779 | 11.4105 | 11.1432 | 10.4853 | 10.0516 | 9.6716
|  | COKES LANE PRIMARY | HE |  |  |  |  | 14.5737 | 14.5095 | 14.4358 | 14.3474 | 14.2284 | 14.1147 | 14.0021 | 13.8905 | 13.78 | 13.7 | 13.5695 | 13.4663 | 12.8758 | 12.7179 | 12.5516 | 12.4432 | 12.3084 | 12.1789 | 12.0463 | 11.9126 | 11.78 | 11.6884 | 11.5621 | 11.4674 | 13.14 | 12.9516 | 12.7526 | 12.6389 | 12.4979 | 12.3642 | 12.2242 | 12.0832 | 11.9442 | 11.8189 | 11.6589 | 11.5368
|  | COKES LANE PRIMARY | FB |  |  |  |  | 14.6295 | 14.5979 | 14.5695 | 14.5421 | 14.5105 | 14.48 | 14.4505 | 14.4221 | 14.3926 | 14.2789 | 14.1589 | 14.0105 | 12.9905 | 12.8979 | 12.8189 | 12.7737 | 12.7242 | 12.6758 | 12.6274 | 12.5789 | 12.5305 | 12.3189 | 12.1463 | 12.0021 | 13.2747 | 13.1611 | 13.0653 | 13.0147 | 12.9589 | 12.9053 | 12.8505 | 12.7947 | 12.74 | 12.4958 | 12.2874 | 12.1105
LOVEDEAN GSP | PORTSMOUTH BSP | COLLEGE PARK PRIMARY | MINIMUM HEADROOM | SU 65893 02686 | NO | YES | 0 | 13.7076 | 13.4371 | 13.1834 | 12.8003 | 12.4097 | 11.8982 | 11.3834 | 10.8466 | 10.3076 | 8.7129 | 7.495 | 6.4118 | 15.0805 | 14.9437 | 14.7932 | 14.5942 | 14.3226 | 14.0605 | 13.7974 | 13.2921 | 12.7026 | 10.9321 | 9.5637 | 8.3468 | 15.86 | 15.7305 | 15.5863 | 15.3926 | 15.1253 | 14.8674 | 14.4547 | 13.8789 | 13.2989 | 11.5611 | 10.2211 | 9.0295
|  | COLLEGE PARK PRIMARY | EE |  |  |  |  | 13.7076 | 13.4371 | 13.1834 | 12.8887 | 12.5403 | 12.1982 | 11.8508 | 11.4992 | 11.1529 | 10.4171 | 9.5445 | 8.8013 | 15.0805 | 14.9437 | 14.7932 | 14.5942 | 14.3226 | 14.0605 | 13.8153 | 13.5637 | 13.3132 | 12.8679 | 11.8668 | 11.0153 | 15.86 | 15.7305 | 15.5863 | 15.3926 | 15.1253 | 14.8674 | 14.6274 | 14.3811 | 14.1368 | 13.4537 | 12.4768 | 11.6442
|  | COLLEGE PARK PRIMARY | HT |  |  |  |  | 13.7613 | 13.5045 | 13.1992 | 12.8003 | 12.4097 | 11.8982 | 11.3834 | 10.8466 | 10.3076 | 8.7129 | 7.495 | 6.4118 | 15.0942 | 14.97 | 14.8079 | 14.5995 | 14.3532 | 14.0763 | 13.7974 | 13.2921 | 12.7026 | 10.9321 | 9.5637 | 8.3468 | 15.8716 | 15.7547 | 15.6011 | 15.4032 | 15.1642 | 14.9 | 14.4547 | 13.8789 | 13.2989 | 11.5611 | 10.2211 | 9.0295
|  | COLLEGE PARK PRIMARY | HE |  |  |  |  | 13.8655 | 13.655 | 13.4497 | 13.1939 | 12.8676 | 12.5634 | 12.2655 | 11.9645 | 11.6708 | 11.475 | 11.075 | 10.5897 | 15.1089 | 14.9774 | 14.83 | 14.6289 | 14.3532 | 14.0974 | 13.8479 | 13.5921 | 13.3437 | 13.3447 | 13.2774 | 13.0447 | 15.8811 | 15.7547 | 15.6105 | 15.4126 | 15.1389 | 14.8863 | 14.6389 | 14.3863 | 14.14 | 14.1516 | 14.1032 | 13.6295
|  | COLLEGE PARK PRIMARY | FB |  |  |  |  | 14.0161 | 13.8582 | 13.7445 | 13.6213 | 13.4908 | 13.3487 | 13.2203 | 13.0992 | 12.9729 | 12.455 | 12.0034 | 11.5055 | 15.2037 | 15.13 | 15.0658 | 14.9942 | 14.9153 | 14.8342 | 14.7563 | 14.6847 | 14.6068 | 14.3205 | 14.1511 | 13.9805 | 15.9726 | 15.9042 | 15.8432 | 15.7737 | 15.6979 | 15.62 | 15.5453 | 15.4758 | 15.4011 | 15.1274 | 14.9737 | 14.5621
EALING GSP |  | COPLEY DENE PRIMARY | MINIMUM HEADROOM | TQ 17445 80798 | NO | YES | 0 | 44.7526 | 44.4579 | 44.1274 | 82.4 | 81.84 | 81.2895 | 80.6842 | 80.0242 | 78.5137 | 73.9242 | 72.0158 | 70.3 | 46.5821 | 46.3189 | 46.0211 | 84.3232 | 83.7895 | 83.2632 | 82.7579 | 81.8568 | 80.0421 | 74.9842 | 72.9263 | 71.0737 | 44.3547 | 43.82 | 43.2537 | 81.3032 | 80.36 | 79.5842 | 78.3526 | 76.9642 | 75.1568 | 70.1221 | 68.0716 | 66.2253
|  | COPLEY DENE PRIMARY | EE |  |  |  |  | 44.7526 | 44.4579 | 44.1274 | 82.4 | 81.84 | 81.2895 | 80.7547 | 80.2042 | 79.66 | 77.9326 | 76.7442 | 75.7316 | 46.5821 | 46.3189 | 46.0211 | 84.3232 | 83.7895 | 83.2632 | 82.7579 | 82.2379 | 81.7232 | 79.4368 | 78.1284 | 77.0084 | 44.3547 | 43.82 | 43.2537 | 81.3032 | 80.5516 | 79.8137 | 79.0621 | 78.2768 | 77.5053 | 74.5526 | 73.2495 | 72.1358
|  | COPLEY DENE PRIMARY | HT |  |  |  |  | 44.7789 | 44.5074 | 44.1663 | 82.4358 | 81.8821 | 81.3221 | 80.6842 | 80.0242 | 78.5137 | 73.9242 | 72.0158 | 70.3 | 46.6053 | 46.3653 | 46.0547 | 84.3558 | 83.8632 | 83.3316 | 82.7726 | 81.8568 | 80.0421 | 74.9842 | 72.9263 | 71.0737 | 44.4105 | 43.9011 | 43.3242 | 81.3516 | 80.36 | 79.5842 | 78.3526 | 76.9642 | 75.1568 | 70.1221 | 68.0716 | 66.2253
|  | COPLEY DENE PRIMARY | HE |  |  |  |  | 44.8274 | 44.5547 | 44.2484 | 82.5347 | 81.9832 | 81.4516 | 80.9284 | 80.3926 | 79.8621 | 79.5779 | 79.4084 | 78.9474 | 46.6221 | 46.3684 | 46.08 | 84.3853 | 83.8516 | 83.3368 | 82.8274 | 82.3074 | 81.7937 | 81.6695 | 81.0726 | 80.5516 | 44.6779 | 44.28 | 43.8347 | 81.9821 | 81.2968 | 80.6421 | 80.0158 | 79.3558 | 78.7095 | 76.7737 | 76.1811 | 75.6621
|  | COPLEY DENE PRIMARY | FB |  |  |  |  | 45.0211 | 44.8389 | 44.6811 | 83.2063 | 83.0137 | 82.8211 | 82.6358 | 82.4621 | 82.2747 | 81.5653 | 80.9737 | 80.5726 | 46.8011 | 46.64 | 46.4979 | 85.0389 | 84.8621 | 84.6853 | 84.5137 | 84.3537 | 84.1811 | 83.5442 | 83.0674 | 82.2253 | 44.8821 | 44.6474 | 44.3768 | 82.7853 | 82.4758 | 82.1705 | 81.8779 | 81.6 | 81.2979 | 80.0495 | 78.1726 | 77.3337
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | CORDWALLIS PRIMARY | MINIMUM HEADROOM | SU 88285 81857 | NO | YES | 0 | 35.7237 | 35.5437 | 35.3353 | 35.0479 | 34.69 | 34.3163 | 33.5163 | 32.4784 | 31.3637 | 28.6974 | 27.2395 | 25.8932 | 32.4779 | 32.1358 | 31.7537 | 31.2726 | 30.4147 | 29.7095 | 28.7547 | 27.5295 | 26.2042 | 23.0242 | 21.3516 | 19.8253 | 33.7158 | 33.5358 | 33.3274 | 32.8263 | 31.9737 | 31.2737 | 30.3274 | 29.1137 | 27.8011 | 24.6505 | 22.9926 | 21.4821
|  | CORDWALLIS PRIMARY | EE |  |  |  |  | 35.7237 | 35.5437 | 35.3353 | 35.0605 | 34.69 | 34.3258 | 33.9858 | 33.5774 | 33.1258 | 31.7816 | 30.8089 | 29.9637 | 32.4779 | 32.1358 | 31.7537 | 31.2726 | 30.4147 | 29.9042 | 29.4032 | 28.9158 | 28.4347 | 26.7832 | 25.5979 | 24.5611 | 33.7158 | 33.5358 | 33.3274 | 32.8263 | 31.9737 | 31.4653 | 30.9674 | 30.4821 | 30.0021 | 28.3695 | 27.1968 | 26.1716
|  | CORDWALLIS PRIMARY | HT |  |  |  |  | 35.7353 | 35.5626 | 35.3374 | 35.0479 | 34.7005 | 34.3163 | 33.5163 | 32.4784 | 31.3637 | 28.6974 | 27.2395 | 25.8932 | 32.52 | 32.1926 | 31.7663 | 31.2884 | 30.4453 | 29.7095 | 28.7547 | 27.5295 | 26.2042 | 23.0242 | 21.3516 | 19.8253 | 33.7274 | 33.5547 | 33.3295 | 32.8495 | 32.0053 | 31.2737 | 30.3274 | 29.1137 | 27.8011 | 24.6505 | 22.9926 | 21.4821
|  | CORDWALLIS PRIMARY | HE |  |  |  |  | 35.7626 | 35.5868 | 35.3816 | 35.1047 | 34.7279 | 34.3732 | 34.0268 | 33.6753 | 33.3311 | 32.9132 | 32.2763 | 31.7153 | 32.6221 | 32.3368 | 32.0063 | 31.5853 | 31.0495 | 30.4389 | 30.0042 | 29.5768 | 29.1411 | 28.1505 | 27.3495 | 26.6421 | 33.7547 | 33.5789 | 33.3737 | 33.0968 | 32.7168 | 31.9947 | 31.56 | 31.1347 | 30.7 | 29.7232 | 28.9326 | 28.2337
|  | CORDWALLIS PRIMARY | FB |  |  |  |  | 35.8942 | 35.8068 | 35.7268 | 35.6374 | 35.5384 | 35.4384 | 35.3416 | 35.2511 | 35.1542 | 34.7995 | 34.4868 | 33.9037 | 32.8189 | 32.6442 | 32.4916 | 32.3221 | 32.1358 | 31.9442 | 31.8095 | 31.6726 | 31.54 | 30.8779 | 29.8105 | 29.0979 | 33.8863 | 33.7989 | 33.7189 | 33.6295 | 33.5305 | 33.4305 | 33.3337 | 33.2432 | 33.1463 | 32.4326 | 31.3779 | 30.6726
MANNINGTON GSP | LYTCHETT BSP | CORFE MULLEN PRIMARY | MINIMUM HEADROOM | SY 98583 96071 | NO | YES | 13.8947 | 16.3816 | 16.1889 | 15.9616 | 15.2963 | 14.5068 | 13.6111 | 12.7279 | 11.8332 | 10.9416 | 7.7584 | 6.33 | 4.9111 | 12.2337 | 11.9347 | 11.5526 | 11.0326 | 10.4116 | 9.7147 | 9.0274 | 8.2726 | 7.1842 | 3.1053 | 1.3316 | -0.26526 | 14.2084 | 13.7716 | 13.1884 | 12.3937 | 11.4516 | 10.3789 | 9.3221 | 8.2442 | 7.1705 | 3.1632 | 1.4168 | -0.15263
|  | CORFE MULLEN PRIMARY | EE |  |  |  |  | 16.3816 | 16.1889 | 15.9742 | 15.5753 | 14.9984 | 14.4521 | 13.9205 | 13.3858 | 12.8647 | 11.2889 | 10.3353 | 9.5111 | 12.2337 | 11.9347 | 11.6074 | 11.2116 | 10.7084 | 10.2337 | 9.78 | 9.3211 | 8.8726 | 7.6853 | 6.4421 | 5.3611 | 14.2084 | 13.7716 | 13.3 | 12.7621 | 12.12 | 11.5095 | 10.9084 | 10.3053 | 9.72 | 7.66 | 6.44 | 5.38
|  | CORFE MULLEN PRIMARY | HT |  |  |  |  | 16.3879 | 16.2037 | 15.9616 | 15.2963 | 14.5068 | 13.6111 | 12.7279 | 11.8332 | 10.9416 | 7.7584 | 6.33 | 4.9111 | 12.2632 | 11.9526 | 11.5526 | 11.0326 | 10.4116 | 9.7147 | 9.0274 | 8.2726 | 7.1842 | 3.1053 | 1.3316 | -0.26526 | 14.2663 | 13.7947 | 13.1884 | 12.3937 | 11.4516 | 10.3789 | 9.3221 | 8.2442 | 7.1705 | 3.1632 | 1.4168 | -0.15263
|  | CORFE MULLEN PRIMARY | HE |  |  |  |  | 16.4374 | 16.2616 | 16.0647 | 15.7932 | 15.4111 | 15.0163 | 14.5468 | 14.07 | 13.6111 | 12.5458 | 11.9153 | 11.3647 | 12.3916 | 12.1505 | 11.8779 | 11.5263 | 11.0558 | 10.6274 | 10.2126 | 9.7905 | 9.3821 | 8.76 | 8.3621 | 7.6589 | 14.4979 | 14.1726 | 13.8011 | 13.3463 | 12.7632 | 12.2253 | 11.7063 | 11.1821 | 10.6768 | 9.2168 | 8.3789 | 7.6432
|  | CORFE MULLEN PRIMARY | FB |  |  |  |  | 16.5732 | 16.4889 | 16.4153 | 16.3311 | 16.2374 | 16.1437 | 16.0532 | 15.9679 | 15.8174 | 15.0195 | 14.3637 | 13.8058 | 12.5768 | 12.4274 | 12.3032 | 12.1663 | 12.0168 | 11.8674 | 11.7211 | 11.5789 | 11.4316 | 10.8221 | 10.3568 | 9.9789 | 14.7474 | 14.5126 | 14.3242 | 14.1179 | 13.8968 | 13.6758 | 13.4568 | 13.2421 | 13.0221 | 12.0568 | 11.2305 | 10.5137
MELKSHAM GSP | NORRINGTON BSP | CORSHAM PRIMARY | MINIMUM HEADROOM | ST 86766 69583 | NO | YES | 0.20842 | 13.1126 | 12.8789 | 12.6453 | 12.1337 | 11.6126 | 11.1621 | 10.6958 | 10.1758 | 9.6326 | 8.1547 | 6.9632 | 5.9021 | 11.3642 | 11.1116 | 10.86 | 10.2905 | 9.7179 | 9.2316 | 8.7263 | 8.1579 | 7.5621 | 5.9189 | 4.5758 | 3.3789 | 11.5895 | 11.3453 | 11.0989 | 10.5295 | 9.9568 | 9.4695 | 8.9653 | 8.3947 | 7.7989 | 6.1558 | 4.8137 | 3.6168
|  | CORSHAM PRIMARY | EE |  |  |  |  | 13.1126 | 12.8789 | 12.6453 | 12.1568 | 11.7053 | 11.3926 | 11.0789 | 10.7611 | 10.4474 | 9.6968 | 8.8295 | 8.0884 | 11.3642 | 11.1116 | 10.86 | 10.3158 | 9.8274 | 9.5011 | 9.1695 | 8.8337 | 8.5032 | 7.6474 | 6.6537 | 5.8011 | 11.5895 | 11.3453 | 11.0989 | 10.5537 | 10.0653 | 9.74 | 9.4074 | 9.0726 | 8.7411 | 7.8853 | 6.8895 | 6.0389
|  | CORSHAM PRIMARY | HT |  |  |  |  | 13.16 | 12.9495 | 12.6895 | 12.1337 | 11.6126 | 11.1621 | 10.6958 | 10.1758 | 9.6326 | 8.1547 | 6.9632 | 5.9021 | 11.4189 | 11.1916 | 10.9126 | 10.2905 | 9.7179 | 9.2316 | 8.7263 | 8.1579 | 7.5621 | 5.9189 | 4.5758 | 3.3789 | 11.6411 | 11.4221 | 11.1516 | 10.5295 | 9.9568 | 9.4695 | 8.9653 | 8.3947 | 7.7989 | 6.1558 | 4.8137 | 3.6168
|  | CORSHAM PRIMARY | HE |  |  |  |  | 13.2642 | 13.1021 | 12.92 | 12.4726 | 12.0474 | 11.7726 | 11.5137 | 11.2495 | 10.9958 | 10.6779 | 10.0716 | 9.5537 | 11.5495 | 11.3663 | 11.1737 | 10.6789 | 10.2211 | 9.9379 | 9.6705 | 9.3979 | 9.1379 | 8.76 | 8.0537 | 7.4484 | 11.7642 | 11.5863 | 11.3979 | 10.9179 | 10.46 | 10.1758 | 9.9084 | 9.6368 | 9.3768 | 8.9989 | 8.2926 | 7.6863
|  | CORSHAM PRIMARY | FB |  |  |  |  | 13.3474 | 13.2832 | 13.1863 | 13.0053 | 12.8358 | 12.7179 | 12.6095 | 12.5074 | 12.4 | 11.9053 | 11.3421 | 10.8516 | 11.6979 | 11.5558 | 11.4495 | 11.2453 | 11.0568 | 10.9284 | 10.8116 | 10.7021 | 10.5863 | 10.0421 | 9.4011 | 8.8358 | 11.9074 | 11.7716 | 11.6695 | 11.4758 | 11.2947 | 11.1674 | 11.0505 | 10.94 | 10.8242 | 10.2811 | 9.6389 | 9.0737
EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD PRIMARY | MINIMUM HEADROOM | SP 59021 31128 | YES | YES | 0.12105 | 1.4847 | 1.2584 | 1.19 | 1.1132 | 1.0279 | -1.3626 | -4.0195 | -8.4679 | -10.3195 | -12.2679 | -12.4268 | -12.5426 | 1.39 | 1.1289 | 1.0553 | 0.97316 | 0.88263 | -1.9132 | -5.0216 | -10.2332 | -12.3974 | -14.6837 | -14.8637 | -14.9942 | 1.39 | 1.1289 | 1.0553 | 0.97211 | 0.88263 | -1.9142 | -5.0237 | -10.2374 | -12.4026 | -14.69 | -14.8689 | -15.0005
|  | COTTISFORD PRIMARY | EE |  |  |  |  | 1.5205 | 1.31 | 1.2447 | 1.1753 | 1.0963 | -0.86579 | -3.3037 | -6.4174 | -8.1079 | -12.2679 | -12.4268 | -12.5426 | 1.4332 | 1.19 | 1.1195 | 1.0447 | 0.96158 | -1.3342 | -4.1868 | -7.8342 | -9.81 | -14.6837 | -14.8637 | -14.9942 | 1.4332 | 1.19 | 1.1195 | 1.0447 | 0.96158 | -1.3353 | -4.1889 | -7.8374 | -9.8142 | -14.69 | -14.8689 | -15.0005
|  | COTTISFORD PRIMARY | HT |  |  |  |  | 1.4847 | 1.2584 | 1.19 | 1.1132 | 1.0279 | -1.3626 | -4.0195 | -8.4679 | -10.3195 | -11.4753 | -11.6984 | -11.9079 | 1.39 | 1.1289 | 1.0553 | 0.97316 | 0.88263 | -1.9132 | -5.0216 | -10.2332 | -12.3974 | -13.7289 | -13.9763 | -14.2089 | 1.39 | 1.1289 | 1.0553 | 0.97211 | 0.88263 | -1.9142 | -5.0237 | -10.2374 | -12.4026 | -13.7342 | -13.9816 | -14.2142
|  | COTTISFORD PRIMARY | HE |  |  |  |  | 1.5689 | 1.3753 | 1.3268 | 1.27 | 1.1995 | -0.83947 | -3.3542 | -6.5342 | -8.2721 | -11.9763 | -12.0679 | -12.1205 | 1.4868 | 1.2637 | 1.2111 | 1.1511 | 1.0763 | -1.3079 | -4.2532 | -7.9774 | -10.01 | -14.3553 | -14.4595 | -14.5205 | 1.4868 | 1.2637 | 1.2111 | 1.1511 | 1.0763 | -1.3089 | -4.2553 | -7.9805 | -10.0142 | -14.3605 | -14.4647 | -14.5258
|  | COTTISFORD PRIMARY | FB |  |  |  |  | 1.6426 | 1.5374 | 1.5111 | 1.4826 | 1.4521 | 1.4216 | 0.55737 | -0.36263 | -1.0689 | -5.4616 | -5.7563 | -5.8363 | 1.57 | 1.4489 | 1.4205 | 1.3889 | 1.3563 | 1.3237 | 0.31105 | -0.76684 | -1.5932 | -6.7416 | -7.0826 | -7.1732 | 1.57 | 1.4489 | 1.4195 | 1.3889 | 1.3563 | 1.3226 | 0.31105 | -0.76789 | -1.5942 | -6.7447 | -7.0847 | -7.1763
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | COURAGES PRIMARY | MINIMUM HEADROOM | SU 70990 69570 | NO | YES | 2.1053 | 29.8437 | 29.5668 | 29.3489 | 29.0289 | 28.2542 | 24.7111 | 24.1847 | 23.6753 | 23.5142 | 20.9489 | 19.8595 | 19.5047 | 29.5774 | 29.1668 | 28.8521 | 28.3868 | 27.4311 | 23.6026 | 23.0184 | 22.4542 | 22.2795 | 19.4174 | 18.2047 | 17.8163 | 29.51 | 29.1679 | 28.9037 | 28.5142 | 27.5942 | 23.7574 | 23.1911 | 22.6289 | 22.45 | 19.49 | 18.2374 | 17.8374
|  | COURAGES PRIMARY | EE |  |  |  |  | 29.8437 | 29.5668 | 29.3616 | 29.0732 | 28.2542 | 24.7111 | 24.1847 | 23.6753 | 23.5142 | 22.1437 | 21.1563 | 20.9047 | 29.5774 | 29.17 | 28.8742 | 28.4553 | 27.4311 | 23.6026 | 23.0184 | 22.4542 | 22.2795 | 20.7458 | 19.6426 | 19.3637 | 29.51 | 29.17 | 28.9216 | 28.5689 | 27.5942 | 23.7574 | 23.1911 | 22.6289 | 22.45 | 20.8626 | 19.7195 | 19.4321
|  | COURAGES PRIMARY | HT |  |  |  |  | 29.8532 | 29.5668 | 29.3489 | 29.0289 | 28.6121 | 25.0142 | 24.4553 | 23.9016 | 23.6911 | 20.9489 | 19.8595 | 19.5047 | 29.5911 | 29.1668 | 28.8521 | 28.3868 | 27.8121 | 23.9426 | 23.3226 | 22.7089 | 22.4805 | 19.4174 | 18.2047 | 17.8163 | 29.5216 | 29.1679 | 28.9037 | 28.5142 | 27.9816 | 24.0858 | 23.4847 | 22.8911 | 22.6584 | 19.49 | 18.2374 | 17.8374
|  | COURAGES PRIMARY | HE |  |  |  |  | 29.8711 | 29.6016 | 29.4079 | 29.1216 | 28.3247 | 24.79 | 24.2763 | 23.7816 | 23.6332 | 21.6995 | 20.7816 | 20.5932 | 29.6163 | 29.2216 | 28.9416 | 28.5279 | 27.5079 | 23.6921 | 23.1226 | 22.5732 | 22.4142 | 20.2416 | 19.2132 | 19.0016 | 29.5426 | 29.2132 | 28.9774 | 28.6289 | 27.6721 | 23.8437 | 23.2921 | 22.7532 | 22.59 | 20.3395 | 19.2732 | 19.0553
|  | COURAGES PRIMARY | FB |  |  |  |  | 29.9121 | 29.8089 | 29.7205 | 29.6005 | 29.3479 | 27.9732 | 27.7279 | 27.4732 | 27.3995 | 27.2668 | 23.7363 | 23.5837 | 29.6679 | 29.5195 | 29.3911 | 29.2163 | 28.8384 | 27.1247 | 26.8647 | 26.5932 | 26.5163 | 26.3795 | 22.5047 | 22.3353 | 29.5889 | 29.4637 | 29.3563 | 29.21 | 28.8963 | 27.2805 | 27.0153 | 26.7405 | 26.6626 | 26.5237 | 22.6763 | 22.5016
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | COVE PRIMARY | MINIMUM HEADROOM | SU 85415 55937 | NO | YES | 0 | 25.4316 | 25.2968 | 25.1432 | 24.9295 | 24.6653 | 24.1516 | 23.9653 | 23.44 | 22.8863 | 23.8074 | 23.1253 | 22.7747 | 23.4758 | 22.8453 | 22.5537 | 22.2284 | 21.7821 | 21.0979 | 20.9221 | 20.3421 | 19.7284 | 20.6021 | 19.8105 | 19.4074 | 22.2137 | 21.7726 | 21.5337 | 21.2537 | 20.8747 | 20.3432 | 20.1442 | 19.6874 | 19.2116 | 20.1937 | 19.6516 | 19.3684
|  | COVE PRIMARY | EE |  |  |  |  | 25.4316 | 25.2968 | 25.1432 | 24.94 | 24.6653 | 24.3979 | 23.9653 | 23.44 | 22.8863 | 29.2853 | 29.1326 | 28.7758 | 23.4758 | 22.8453 | 22.5537 | 22.2284 | 21.8453 | 21.4253 | 20.9221 | 20.3421 | 19.7284 | 26.9737 | 26.8221 | 26.7032 | 22.2137 | 21.7726 | 21.5337 | 21.2537 | 20.9126 | 20.5505 | 20.1442 | 19.6874 | 19.2116 | 28.3189 | 28.1674 | 28.0484
|  | COVE PRIMARY | HT |  |  |  |  | 25.4411 | 25.3116 | 25.1432 | 24.9295 | 24.6705 | 24.1516 | 29.9274 | 29.6516 | 29.3789 | 28.4663 | 27.34 | 26.5674 | 23.5379 | 22.9295 | 22.6116 | 22.2379 | 21.7821 | 21.0979 | 27.6168 | 27.3411 | 27.0684 | 26.4495 | 26.0695 | 25.7379 | 22.2558 | 21.8295 | 21.5695 | 21.2558 | 20.8747 | 20.3432 | 28.9611 | 28.6853 | 28.4126 | 27.7947 | 27.4147 | 27.0832
|  | COVE PRIMARY | HE |  |  |  |  | 25.4684 | 25.34 | 25.1926 | 24.9916 | 24.7221 | 24.4653 | 24.2158 | 23.9116 | 23.3832 | 29.54 | 29.5011 | 29.4768 | 23.6021 | 23.1253 | 22.9 | 22.6253 | 22.2821 | 21.9021 | 21.44 | 20.8947 | 20.3095 | 27.2295 | 27.1905 | 27.1663 | 22.3547 | 21.9621 | 21.7663 | 21.52 | 21.2053 | 20.8716 | 20.4905 | 20.0558 | 19.6 | 28.5747 | 28.5358 | 28.5116
|  | COVE PRIMARY | FB |  |  |  |  | 25.5642 | 25.5032 | 25.4463 | 25.3842 | 25.3158 | 25.2463 | 25.1779 | 25.1147 | 25.0474 | 23.8074 | 23.1253 | 22.7747 | 23.6979 | 23.6368 | 23.5284 | 23.4011 | 23.2642 | 23.0021 | 22.8474 | 22.6674 | 22.4705 | 20.6021 | 19.8105 | 19.4074 | 22.5421 | 22.3495 | 22.2526 | 22.1495 | 22.0389 | 21.8505 | 21.7284 | 21.5937 | 21.4453 | 20.1937 | 19.6516 | 19.3684
FAWLEY GSP | COWES BSP | COWES PRIMARY | MINIMUM HEADROOM | SP 56113 03074 | NO | YES | 0 | 33.9847 | 33.2963 | 31.5111 | 30.3837 | 29.4395 | 28.3837 | 27.5595 | 26.1258 | 25.3363 | 18.5416 | 24.2384 | 17.7311 | 28.0863 | 27.2821 | 25.08 | 23.7579 | 22.7032 | 21.5063 | 20.5937 | 18.9526 | 18.1063 | 9.8905 | 16.3589 | 8.5895 | 29.9484 | 29.1442 | 26.94 | 25.6168 | 24.5632 | 23.3653 | 22.4526 | 20.8116 | 19.9653 | 11.7474 | 18.2168 | 10.4453
|  | COWES PRIMARY | EE |  |  |  |  | 33.9847 | 33.2963 | 31.5111 | 30.5858 | 29.4395 | 28.3837 | 27.5595 | 26.1258 | 25.3363 | 103.6637 | 103.3405 | 95.5142 | 28.0863 | 27.2821 | 25.08 | 24.0126 | 22.7032 | 21.5063 | 20.5937 | 18.9526 | 18.1063 | 122.3768 | 115.0674 | 105.7516 | 29.9484 | 29.1442 | 26.94 | 25.8737 | 24.5632 | 23.3653 | 22.4526 | 20.8116 | 19.9653 | 112.8547 | 105.5421 | 96.2232
|  | COWES PRIMARY | HT |  |  |  |  | 34.0816 | 33.4132 | 31.5216 | 30.3837 | 106.1732 | 105.5953 | 105.0216 | 104.4563 | 103.8974 | 102.5647 | 98.0142 | 90.0163 | 28.2074 | 27.4232 | 25.0926 | 23.7579 | 126.4537 | 125.8758 | 125.3021 | 124.7368 | 124.1779 | 122.7842 | 108.9432 | 99.6368 | 30.0695 | 29.2842 | 26.9537 | 25.6168 | 117.4379 | 116.86 | 116.2863 | 115.7221 | 115.1632 | 113.2621 | 99.4158 | 90.1074
|  | COWES PRIMARY | HE |  |  |  |  | 34.3026 | 33.7342 | 32.0553 | 31.2153 | 30.1226 | 29.1458 | 28.4353 | 27.1595 | 26.4995 | 18.5416 | 104.0942 | 98.8037 | 28.4811 | 27.8284 | 25.76 | 24.8 | 23.5611 | 22.4579 | 21.6937 | 20.2042 | 19.5032 | 9.8905 | 118.22 | 109.4621 | 30.3421 | 29.6895 | 27.6211 | 26.6611 | 25.4211 | 24.3179 | 23.5537 | 22.0632 | 21.3632 | 11.7474 | 108.6958 | 99.9347
|  | COWES PRIMARY | FB |  |  |  |  | 34.6489 | 34.2837 | 33.9489 | 33.5879 | 33.1742 | 32.7721 | 32.4942 | 32.2405 | 31.9847 | 29.7942 | 24.2384 | 17.7311 | 28.8653 | 28.4316 | 28.0358 | 27.6095 | 27.1189 | 26.6453 | 26.3284 | 26.04 | 25.7516 | 23.0874 | 16.3589 | 8.5895 | 30.7263 | 30.2926 | 29.8979 | 29.4716 | 28.9811 | 28.5063 | 28.1895 | 27.9011 | 27.6126 | 24.9484 | 18.2168 | 10.4453
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL PRIMARY | MINIMUM HEADROOM | SP 56113 03074 | NO | YES | 0 | 83.2442 | 83.0179 | 82.7284 | 81.5611 | 77.8768 | 74.0968 | 69.6905 | 65.1663 | 60.5821 | 54.06 | 50.5179 | 48.8505 | 78.0832 | 77.7463 | 76.7379 | 75.4337 | 71.2495 | 66.9095 | 61.8358 | 56.6042 | 51.2905 | 44.9253 | 40.8779 | 39.0242 | 80.7032 | 80.4758 | 80.2295 | 79.1 | 74.8442 | 70.4874 | 65.3947 | 60.1621 | 54.8589 | 48.9484 | 44.9116 | 43.0632
|  | COWLEY LOCAL PRIMARY | EE |  |  |  |  | 83.2442 | 83.0179 | 82.7705 | 82.0074 | 80.7074 | 77.9411 | 74.66 | 71.5316 | 68.6063 | 60.5874 | 57.6832 | 56.5432 | 78.0832 | 77.7705 | 76.9284 | 75.9537 | 74.5126 | 71.3526 | 67.5832 | 63.9947 | 60.6463 | 52.4537 | 49.0937 | 47.8 | 80.7032 | 80.4758 | 80.2295 | 79.5842 | 78.2 | 75.0274 | 71.2453 | 67.6432 | 64.28 | 56.4579 | 53.1063 | 51.8158
|  | COWLEY LOCAL PRIMARY | HT |  |  |  |  | 83.2695 | 83.06 | 82.7284 | 81.5611 | 77.8768 | 74.0968 | 69.6905 | 65.1663 | 60.5821 | 54.06 | 50.5179 | 48.8505 | 78.1084 | 77.7463 | 76.7379 | 75.4337 | 71.2495 | 66.9095 | 61.8358 | 56.6042 | 51.2905 | 44.9253 | 40.8779 | 39.0242 | 80.7284 | 80.5189 | 80.2432 | 79.1 | 74.8442 | 70.4874 | 65.3947 | 60.1621 | 54.8589 | 48.9484 | 44.9116 | 43.0632
|  | COWLEY LOCAL PRIMARY | HE |  |  |  |  | 83.3126 | 83.0937 | 82.8505 | 82.5147 | 81.3411 | 78.5705 | 75.2884 | 72.1674 | 69.2495 | 62.4368 | 60.0674 | 59.3958 | 78.1516 | 77.9326 | 77.5232 | 76.6337 | 75.2432 | 72.0747 | 68.3084 | 64.7305 | 61.3884 | 54.5558 | 51.7842 | 51.0074 | 80.7716 | 80.5526 | 80.3095 | 79.9737 | 78.8958 | 75.7537 | 71.9716 | 68.3811 | 65.0263 | 58.5547 | 55.7916 | 55.0168
|  | COWLEY LOCAL PRIMARY | FB |  |  |  |  | 83.4558 | 83.3368 | 83.2305 | 83.1095 | 82.9768 | 82.8432 | 81.8147 | 80.6211 | 79.4768 | 70.9042 | 68.9747 | 68.1758 | 78.2947 | 78.1758 | 78.0695 | 77.9484 | 77.7979 | 77.0042 | 75.6821 | 74.3074 | 72.9905 | 63.0463 | 60.8853 | 59.9758 | 80.9147 | 80.7958 | 80.6895 | 80.5684 | 80.4358 | 80.3021 | 79.3505 | 77.9905 | 76.6695 | 66.6853 | 64.4379 | 63.5295
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | COXMOOR WOOD PRIMARY | MINIMUM HEADROOM | SU 78275 50779 | YES | YES | 0 | 12.5368 | 12.4579 | 12.3684 | 12.2442 | 11.9189 | 11.3989 | 10.8695 | 10.3074 | 9.7484 | 8.5821 | 7.7432 | 6.9621 | 9.3621 | 9.0684 | 8.8105 | 8.38 | 7.8211 | 7.2074 | 6.5937 | 5.9674 | 5.3432 | 4.0474 | 3.1095 | 2.2347 | 11.8747 | 11.5821 | 11.3263 | 10.8979 | 10.3432 | 9.7337 | 9.1232 | 8.5021 | 7.8821 | 6.5947 | 5.6642 | 4.7947
|  | COXMOOR WOOD PRIMARY | EE |  |  |  |  | 12.5368 | 12.4579 | 12.3695 | 12.2505 | 12.0905 | 11.9358 | 11.7905 | 11.6432 | 11.4979 | 11.0684 | 10.5137 | 9.9747 | 9.3621 | 9.0684 | 8.9021 | 8.7137 | 8.4663 | 8.2263 | 7.9842 | 7.7389 | 7.5021 | 6.9284 | 6.2526 | 5.6389 | 11.8747 | 11.5821 | 11.4168 | 11.2284 | 10.9832 | 10.7432 | 10.5021 | 10.2579 | 10.0211 | 9.4526 | 8.7821 | 8.1726
|  | COXMOOR WOOD PRIMARY | HT |  |  |  |  | 12.54 | 12.4653 | 12.3684 | 12.2442 | 11.9189 | 11.3989 | 10.8695 | 10.3074 | 9.7484 | 8.5821 | 7.7432 | 6.9621 | 9.3947 | 9.1147 | 8.8105 | 8.38 | 7.8211 | 7.2074 | 6.5937 | 5.9674 | 5.3432 | 4.0474 | 3.1095 | 2.2347 | 11.9074 | 11.6284 | 11.3263 | 10.8979 | 10.3432 | 9.7337 | 9.1232 | 8.5021 | 7.8821 | 6.5947 | 5.6642 | 4.7947
|  | COXMOOR WOOD PRIMARY | HE |  |  |  |  | 12.5516 | 12.4768 | 12.3916 | 12.2758 | 12.1179 | 11.9695 | 11.8242 | 11.6789 | 11.5337 | 11.5442 | 11.1916 | 10.8116 | 9.4716 | 9.2232 | 9.0926 | 8.9358 | 8.7105 | 8.4958 | 8.2895 | 8.0789 | 7.8747 | 7.5611 | 7.0505 | 6.5758 | 11.9832 | 11.7358 | 11.6063 | 11.4495 | 11.2253 | 11.0105 | 10.8042 | 10.5947 | 10.3916 | 10.0811 | 9.5747 | 9.1042
|  | COXMOOR WOOD PRIMARY | FB |  |  |  |  | 12.6126 | 12.5768 | 12.5453 | 12.5095 | 12.4695 | 12.4295 | 12.3905 | 12.3547 | 12.3158 | 12.1737 | 12.0958 | 11.8358 | 9.6589 | 9.5074 | 9.4389 | 9.3674 | 9.2811 | 9.1958 | 9.1105 | 9.0274 | 8.9421 | 8.5537 | 8.12 | 7.7284 | 12.1242 | 12.0179 | 11.9505 | 11.8789 | 11.7926 | 11.7084 | 11.6232 | 11.5411 | 11.4568 | 11.0695 | 10.64 | 10.2516
MANNINGTON GSP | LYTCHETT BSP | CREEKMOOR PRIMARY | MINIMUM HEADROOM | SZ 00552 94121 | NO | YES | 0 | 33.4021 | 33.0684 | 32.66 | 32.1053 | 31.4274 | 30.5526 | 29.7063 | 28.8221 | 27.9579 | 26.0905 | 24.7863 | 23.6189 | 32.8484 | 32.4547 | 31.9632 | 31.3 | 30.4874 | 29.4074 | 28.3674 | 27.2695 | 26.1979 | 23.9116 | 22.2821 | 20.8158 | 32.2737 | 32.0821 | 31.8653 | 31.5632 | 31.1979 | 30.1579 | 29.1368 | 28.0589 | 27.0084 | 24.7621 | 23.1632 | 21.7263
|  | CREEKMOOR PRIMARY | EE |  |  |  |  | 33.4021 | 33.0684 | 32.7263 | 32.3253 | 31.6653 | 31.1916 | 30.7432 | 30.2832 | 29.84 | 29.0032 | 28.1347 | 27.3884 | 32.8484 | 32.4547 | 32.0547 | 31.6032 | 30.8274 | 30.3095 | 29.8137 | 29.3032 | 28.8168 | 27.7242 | 26.5789 | 25.5874 | 32.2737 | 32.0821 | 31.8716 | 31.5884 | 31.1979 | 30.8284 | 30.4916 | 30.0368 | 29.5547 | 28.4874 | 27.3684 | 26.4
|  | CREEKMOOR PRIMARY | HT |  |  |  |  | 33.4484 | 33.0811 | 32.66 | 32.1053 | 31.4274 | 30.5526 | 29.7063 | 28.8221 | 27.9579 | 26.0905 | 24.7863 | 23.6189 | 32.9105 | 32.4632 | 31.9632 | 31.3 | 30.4874 | 29.4074 | 28.3674 | 27.2695 | 26.1979 | 23.9116 | 22.2821 | 20.8158 | 32.2842 | 32.1021 | 31.8653 | 31.5632 | 31.2 | 30.1579 | 29.1368 | 28.0589 | 27.0084 | 24.7621 | 23.1632 | 21.7263
|  | CREEKMOOR PRIMARY | HE |  |  |  |  | 33.6221 | 33.3726 | 33.1011 | 32.7621 | 32.1421 | 31.7253 | 31.3347 | 30.9305 | 30.5442 | 30.2232 | 29.6811 | 29.2105 | 33.14 | 32.8589 | 32.5558 | 32.1884 | 31.4653 | 31.0179 | 30.6042 | 30.1726 | 29.7663 | 29.2947 | 28.5463 | 27.8905 | 32.3274 | 32.1516 | 31.9537 | 31.6832 | 31.2989 | 30.9537 | 30.6189 | 30.2758 | 29.9389 | 29.9663 | 29.2958 | 28.6579
|  | CREEKMOOR PRIMARY | FB |  |  |  |  | 33.8684 | 33.6895 | 33.5495 | 33.4011 | 33.1832 | 33.0232 | 32.8726 | 32.7263 | 32.5779 | 31.9158 | 31.3105 | 30.8 | 33.4347 | 33.2147 | 33.0474 | 32.8726 | 32.6032 | 32.4158 | 32.2389 | 32.0674 | 31.8958 | 31.0947 | 30.3095 | 29.6316 | 32.46 | 32.3758 | 32.2989 | 32.2137 | 32.1189 | 32.0221 | 31.9305 | 31.8432 | 31.7505 | 31.4116 | 31.0463 | 30.3842
MINETY GSP | CIRENCESTER BSP | CRICKLADE PRIMARY | MINIMUM HEADROOM | SU 09400 93270 | NO | YES | 0 | 17.215 | 17.0245 | 16.8455 | 16.5603 | 16.2876 | 15.9824 | 15.6729 | 15.3171 | 14.9476 | 13.2697 | 12.6476 | 12.1266 | 14.2511 | 14.0384 | 13.8426 | 13.5279 | 13.2342 | 12.9047 | 12.5689 | 12.1774 | 11.7679 | 9.7489 | 9.0237 | 8.4153 | 14.9632 | 14.7537 | 14.56 | 14.2505 | 13.96 | 13.6347 | 13.3021 | 12.9168 | 12.5137 | 10.5463 | 9.8368 | 9.2411
|  | CRICKLADE PRIMARY | EE |  |  |  |  | 17.215 | 17.0245 | 16.8455 | 16.5782 | 16.3592 | 16.1466 | 15.9139 | 15.675 | 15.4424 | 13.2697 | 12.6476 | 12.1266 | 14.2511 | 14.0384 | 13.8426 | 13.5447 | 13.3142 | 13.09 | 12.8395 | 12.5837 | 12.3342 | 9.7489 | 9.0237 | 8.4153 | 14.9632 | 14.7537 | 14.56 | 14.2674 | 14.0389 | 13.8158 | 13.5674 | 13.3147 | 13.0684 | 10.5463 | 9.8368 | 9.2411
|  | CRICKLADE PRIMARY | HT |  |  |  |  | 17.255 | 17.0729 | 16.8761 | 16.5603 | 16.2876 | 15.9824 | 15.6729 | 15.3171 | 14.9476 | 13.8961 | 13.0624 | 12.3224 | 14.2963 | 14.0942 | 13.8795 | 13.5279 | 13.2342 | 12.9047 | 12.5689 | 12.1774 | 11.7679 | 10.5868 | 9.6353 | 8.7889 | 15.0074 | 14.8084 | 14.5968 | 14.2505 | 13.96 | 13.6347 | 13.3021 | 12.9168 | 12.5137 | 11.3516 | 10.4179 | 9.5874
|  | CRICKLADE PRIMARY | HE |  |  |  |  | 17.3487 | 17.2097 | 17.0729 | 16.8424 | 16.6466 | 16.4666 | 16.2887 | 16.1097 | 15.9382 | 14.1266 | 13.7139 | 13.3729 | 14.4026 | 14.25 | 14.1026 | 13.8479 | 13.6437 | 13.4563 | 13.2721 | 13.0879 | 12.9111 | 10.7363 | 10.25 | 9.8437 | 15.1126 | 14.9611 | 14.8158 | 14.5642 | 14.3621 | 14.1758 | 13.9926 | 13.8084 | 13.6326 | 11.5137 | 11.0379 | 10.6421
|  | CRICKLADE PRIMARY | FB |  |  |  |  | 17.4676 | 17.3655 | 17.2918 | 17.2066 | 17.1055 | 17.0266 | 16.9497 | 16.8761 | 16.8013 | 16.4571 | 16.0634 | 15.7234 | 14.5363 | 14.4216 | 14.3395 | 14.2447 | 14.1321 | 14.0458 | 13.9626 | 13.8826 | 13.8005 | 13.4184 | 12.9616 | 12.5637 | 15.2432 | 15.1305 | 15.0495 | 14.9568 | 14.8453 | 14.76 | 14.6789 | 14.5989 | 14.5179 | 14.1421 | 13.6947 | 13.3063
MELKSHAM GSP | FROME BSP | CROCKERTON PRIMARY | MINIMUM HEADROOM | ST 87736 43371 | NO | YES | 0 | 12.8374 | 12.6058 | 12.3511 | 12.0458 | 11.6521 | 11.2932 | 10.9437 | 10.5742 | 10.2416 | 9.5395 | 8.5679 | 7.2363 | 14.2053 | 13.8253 | 13.4358 | 13.0095 | 12.3863 | 11.6547 | 10.9968 | 10.2684 | 9.5137 | 7.4263 | 5.7042 | 4.1505 | 14.7421 | 14.38 | 14.0063 | 13.5926 | 13.0211 | 12.3432 | 11.7189 | 10.9853 | 10.2253 | 8.12 | 6.38 | 4.8084
|  | CROCKERTON PRIMARY | EE |  |  |  |  | 12.8374 | 12.6058 | 12.3511 | 12.0458 | 11.6521 | 11.2932 | 10.9437 | 10.5742 | 10.2416 | 9.7321 | 9.2963 | 8.9532 | 14.2053 | 13.8253 | 13.4358 | 13.0095 | 12.4116 | 11.8326 | 11.3305 | 10.8168 | 10.3505 | 9.0379 | 7.6484 | 6.46 | 14.7421 | 14.38 | 14.0063 | 13.5926 | 13.0221 | 12.4705 | 11.9863 | 11.4884 | 11.0379 | 9.7242 | 8.3147 | 7.1074
|  | CROCKERTON PRIMARY | HT |  |  |  |  | 12.8858 | 12.6742 | 12.4216 | 12.1079 | 11.7647 | 11.4163 | 11.0689 | 10.7268 | 10.39 | 9.5395 | 8.5679 | 7.2363 | 14.3042 | 13.9642 | 13.5674 | 13.0516 | 12.3863 | 11.6547 | 10.9968 | 10.2684 | 9.5137 | 7.4263 | 5.7042 | 4.1505 | 14.8368 | 14.5116 | 14.1326 | 13.6411 | 13.0211 | 12.3432 | 11.7189 | 10.9853 | 10.2253 | 8.12 | 6.38 | 4.8084
|  | CROCKERTON PRIMARY | HE |  |  |  |  | 13.0037 | 12.8584 | 12.7016 | 12.4826 | 12.1679 | 11.8868 | 11.6216 | 11.35 | 11.0847 | 11.0658 | 10.9468 | 10.8563 | 14.5368 | 14.3147 | 14.0842 | 13.7937 | 13.3105 | 12.8463 | 12.5032 | 12.1621 | 11.8316 | 11.3516 | 10.4863 | 9.7274 | 15.0568 | 14.8453 | 14.6253 | 14.3453 | 13.8863 | 13.4484 | 13.1168 | 12.7853 | 12.4642 | 12.0505 | 11.22 | 10.4516
|  | CROCKERTON PRIMARY | FB |  |  |  |  | 13.1121 | 13.0384 | 12.9732 | 12.9016 | 12.8195 | 12.7332 | 12.6553 | 12.5816 | 12.5047 | 12.2111 | 12.0153 | 11.8784 | 14.7179 | 14.5474 | 14.4189 | 14.2842 | 14.1 | 13.8674 | 13.7263 | 13.5947 | 13.4589 | 12.7989 | 12.0168 | 11.3358 | 15.2274 | 15.0705 | 14.9516 | 14.8253 | 14.6558 | 14.4442 | 14.3126 | 14.1895 | 14.0621 | 13.4547 | 12.7526 | 12.0684
FLEET-BRAMLEY GSP | PYESTOCK BSP | CROOKHAM PRIMARY | MINIMUM HEADROOM | SU 81702 53403 | NO | YES | 0 | 28.85 | 28.6142 | 28.3163 | 27.8879 | 27.3605 | 26.5195 | 25.4784 | 24.43 | 23.3921 | 21.1458 | 19.5637 | 18.1353 | 25.8232 | 25.4284 | 24.9116 | 24.0695 | 23.0084 | 21.8442 | 20.6884 | 19.5221 | 18.3684 | 15.8758 | 14.1053 | 12.5032 | 26.7253 | 26.3305 | 25.8147 | 24.9747 | 23.9158 | 22.7537 | 21.6 | 20.4358 | 19.2842 | 16.7979 | 15.0305 | 13.4316
|  | CROOKHAM PRIMARY | EE |  |  |  |  | 28.85 | 28.6142 | 28.3574 | 28.0342 | 27.6089 | 27.1953 | 26.8058 | 26.4121 | 26.0258 | 25.4121 | 24.3384 | 23.4068 | 25.8232 | 25.4284 | 25.0274 | 24.5747 | 24.0074 | 23.4558 | 22.9232 | 22.3842 | 21.8621 | 20.7547 | 19.5253 | 18.4547 | 26.7253 | 26.3305 | 25.9305 | 25.4779 | 24.9116 | 24.36 | 23.8284 | 23.2905 | 22.7684 | 21.6642 | 20.4368 | 19.3695
|  | CROOKHAM PRIMARY | HT |  |  |  |  | 28.87 | 28.6447 | 28.3163 | 27.8879 | 27.3605 | 26.5195 | 25.4784 | 24.43 | 23.3921 | 21.1458 | 19.5637 | 18.1353 | 25.9011 | 25.5358 | 24.9116 | 24.0695 | 23.0084 | 21.8442 | 20.6884 | 19.5221 | 18.3684 | 15.8758 | 14.1053 | 12.5032 | 26.8021 | 26.4379 | 25.8147 | 24.9747 | 23.9158 | 22.7537 | 21.6 | 20.4358 | 19.2842 | 16.7979 | 15.0305 | 13.4316
|  | CROOKHAM PRIMARY | HE |  |  |  |  | 28.9511 | 28.7511 | 28.5247 | 28.2279 | 27.8258 | 27.4447 | 27.0742 | 26.6995 | 26.3311 | 26.2163 | 25.9163 | 25.2521 | 26.1063 | 25.8211 | 25.5147 | 25.1421 | 24.6337 | 24.1505 | 23.6853 | 23.2137 | 22.7537 | 22.1705 | 21.2905 | 20.5126 | 27.0074 | 26.7221 | 26.4168 | 26.0432 | 25.5368 | 25.0526 | 24.5884 | 24.1168 | 23.6579 | 23.0768 | 22.1989 | 21.4232
|  | CROOKHAM PRIMARY | FB |  |  |  |  | 29.1163 | 29.0026 | 28.9089 | 28.8068 | 28.6921 | 28.5753 | 28.4637 | 28.3574 | 28.2447 | 27.7995 | 27.4668 | 27.0963 | 26.3516 | 26.1337 | 25.9737 | 25.8053 | 25.6105 | 25.4147 | 25.2274 | 25.0411 | 24.8547 | 24.0126 | 23.1737 | 22.4558 | 27.2526 | 27.0347 | 26.8758 | 26.7063 | 26.5126 | 26.3168 | 26.1295 | 25.9442 | 25.7579 | 24.9168 | 24.08 | 23.3653
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CROWTHORNE PRIMARY | MINIMUM HEADROOM | SU 84470 64352 | NO | YES | 0.24211 | 59.4558 | 58.5137 | 57.3326 | 55.9968 | 53.9926 | 51.9158 | 49.7558 | 47.6558 | 45.6758 | 39.7768 | 36.1663 | 34.0368 | 47.5716 | 45.96 | 44.5568 | 42.9916 | 40.6853 | 38.3011 | 35.8453 | 33.4779 | 31.2505 | 24.5411 | 20.4358 | 18.0505 | 49.7295 | 48.1168 | 46.7126 | 45.1484 | 42.8421 | 40.4568 | 38 | 35.6326 | 33.4042 | 26.6937 | 22.5863 | 20.2
|  | CROWTHORNE PRIMARY | EE |  |  |  |  | 59.4558 | 58.5137 | 57.3611 | 56.3021 | 55.0411 | 53.4168 | 51.5095 | 49.7137 | 48.0611 | 43.1021 | 40.2147 | 38.8368 | 47.5716 | 45.96 | 44.5874 | 43.36 | 41.9442 | 40.0979 | 37.9021 | 35.8621 | 34.0084 | 28.2442 | 24.9032 | 23.3253 | 49.7295 | 48.1168 | 46.7442 | 45.5168 | 44.1011 | 42.2526 | 40.0568 | 38.0168 | 36.1632 | 30.3958 | 27.0547 | 25.4758
|  | CROWTHORNE PRIMARY | HT |  |  |  |  | 59.4705 | 58.6126 | 57.3326 | 55.9968 | 53.9926 | 51.9158 | 49.7558 | 47.6558 | 45.6758 | 39.7768 | 36.1663 | 34.0368 | 47.6853 | 46.0821 | 44.5568 | 42.9916 | 40.6853 | 38.3011 | 35.8453 | 33.4779 | 31.2505 | 24.5411 | 20.4358 | 18.0505 | 49.8432 | 48.24 | 46.7126 | 45.1484 | 42.8421 | 40.4568 | 38 | 35.6326 | 33.4042 | 26.6937 | 22.5863 | 20.2
|  | CROWTHORNE PRIMARY | HE |  |  |  |  | 59.5495 | 58.9811 | 57.9421 | 56.98 | 55.8105 | 54.2684 | 52.4474 | 50.7579 | 49.2105 | 45.0979 | 42.7179 | 41.7653 | 47.9811 | 46.5274 | 45.2926 | 44.1832 | 42.8505 | 41.0895 | 38.9979 | 37.0642 | 35.3253 | 30.4905 | 27.7084 | 26.5979 | 50.1389 | 48.6853 | 47.4505 | 46.3411 | 45.0074 | 43.2453 | 41.1537 | 39.22 | 37.48 | 32.6442 | 29.8611 | 28.7505
|  | CROWTHORNE PRIMARY | FB |  |  |  |  | 59.7968 | 59.6305 | 59.4905 | 59.2937 | 58.9063 | 58.3874 | 57.6411 | 56.9042 | 56.1884 | 52.6979 | 50.7674 | 49.8432 | 48.8232 | 48.0274 | 47.4484 | 46.9674 | 46.4389 | 45.8189 | 44.9116 | 44.0137 | 43.1568 | 39.0484 | 36.8126 | 35.7568 | 50.9821 | 50.1853 | 49.6063 | 49.1253 | 48.5968 | 47.9768 | 47.0695 | 46.1716 | 45.3137 | 41.2042 | 38.9684 | 37.9116
COWLEY GSP |  | CULHAM PRIMARY | MINIMUM HEADROOM | SU 50731 95053 | NO | YES | 0 | 40.5284 | 40.5284 | 40.5284 | 40.5284 | 40.5284 | 40.5284 | 40.5284 | 40.5284 | 40.5274 | 39.1105 | 39.1053 | 39.1011 | 35.9558 | 35.9558 | 35.9558 | 35.9558 | 35.9558 | 35.9558 | 35.9558 | 35.9547 | 35.9537 | 34.3011 | 34.2947 | 34.2905 | 37.5705 | 37.5705 | 37.5705 | 37.5705 | 37.5705 | 37.5705 | 37.5705 | 37.5695 | 37.5684 | 35.9305 | 35.9242 | 35.92
|  | CULHAM PRIMARY | EE |  |  |  |  | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5526 | 40.5526 | 40.5516 | 39.2632 | 39.2589 | 39.2558 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9842 | 35.9832 | 35.9821 | 34.48 | 34.4758 | 34.4705 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5979 | 37.5968 | 37.5958 | 36.1084 | 36.1042 | 36.1
|  | CULHAM PRIMARY | HT |  |  |  |  | 40.5284 | 40.5284 | 40.5284 | 40.5284 | 40.5284 | 40.5284 | 40.5284 | 40.5284 | 40.5274 | 39.1105 | 39.1053 | 39.1011 | 35.9558 | 35.9558 | 35.9558 | 35.9558 | 35.9558 | 35.9558 | 35.9558 | 35.9547 | 35.9537 | 34.3011 | 34.2947 | 34.2905 | 37.5705 | 37.5705 | 37.5705 | 37.5705 | 37.5705 | 37.5705 | 37.5705 | 37.5695 | 37.5684 | 35.9305 | 35.9242 | 35.92
|  | CULHAM PRIMARY | HE |  |  |  |  | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 39.2695 | 39.2695 | 39.2695 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 34.4874 | 34.4874 | 34.4874 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 36.1158 | 36.1158 | 36.1158
|  | CULHAM PRIMARY | FB |  |  |  |  | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 40.5537 | 39.7516 | 39.7516 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.9853 | 35.0484 | 35.0484 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 37.5989 | 36.6758 | 36.6758
EALING GSP | EALING BSP | DEAN GARDENS PRIMARY | MINIMUM HEADROOM | TQ 16546 80368 | YES | YES | 0.014737 | 7.1063 | 6.7895 | 6.72 | 6.6389 | 5.7989 | 5.0421 | 4.9084 | 4.7537 | 4.56 | 4.1221 | 3.8463 | 3.5926 | 7.0463 | 6.6779 | 6.6032 | 6.5158 | 5.5379 | 4.6579 | 4.5126 | 4.3421 | 4.1263 | 3.6421 | 3.3368 | 3.0579 | 7.0474 | 6.68 | 6.6053 | 6.5189 | 5.5432 | 4.6663 | 4.5211 | 4.3505 | 4.1358 | 3.6516 | 3.3474 | 3.0684
|  | DEAN GARDENS PRIMARY | EE |  |  |  |  | 7.1232 | 6.8253 | 6.7568 | 6.6768 | 5.92 | 5.1653 | 5.0642 | 4.9621 | 4.8589 | 4.6389 | 4.4516 | 4.2863 | 7.0663 | 6.7211 | 6.6474 | 6.5621 | 5.6821 | 4.8042 | 4.6979 | 4.5884 | 4.4789 | 4.2305 | 4.0179 | 3.8305 | 7.0674 | 6.7232 | 6.6495 | 6.5642 | 5.6874 | 4.8116 | 4.7053 | 4.5958 | 4.4863 | 4.2389 | 4.0274 | 3.8389
|  | DEAN GARDENS PRIMARY | HT |  |  |  |  | 7.1063 | 6.7895 | 6.72 | 6.6389 | 5.7989 | 5.0421 | 4.9084 | 4.7537 | 4.56 | 4.1221 | 3.8463 | 3.5926 | 7.0463 | 6.6779 | 6.6032 | 6.5158 | 5.5379 | 4.6579 | 4.5126 | 4.3421 | 4.1263 | 3.6421 | 3.3368 | 3.0579 | 7.0474 | 6.68 | 6.6053 | 6.5189 | 5.5432 | 4.6663 | 4.5211 | 4.3505 | 4.1358 | 3.6516 | 3.3474 | 3.0684
|  | DEAN GARDENS PRIMARY | HE |  |  |  |  | 7.16 | 6.8758 | 6.8189 | 6.7484 | 6.0011 | 5.2526 | 5.1716 | 5.0884 | 5.0063 | 4.9484 | 4.8663 | 4.7863 | 7.1095 | 6.7811 | 6.72 | 6.6463 | 5.7779 | 4.9095 | 4.8253 | 4.74 | 4.6547 | 4.5863 | 4.4916 | 4.3979 | 7.1105 | 6.7832 | 6.7221 | 6.6484 | 5.7821 | 4.9158 | 4.8326 | 4.7463 | 4.6621 | 4.5937 | 4.4989 | 4.4053
|  | DEAN GARDENS PRIMARY | FB |  |  |  |  | 7.28 | 7.1274 | 7.0937 | 7.0579 | 6.7547 | 6.4221 | 6.3842 | 6.3505 | 6.3126 | 6.1568 | 6.0211 | 5.9053 | 7.2474 | 7.0716 | 7.0347 | 6.9958 | 6.6442 | 6.2558 | 6.2158 | 6.1789 | 6.1379 | 5.9705 | 5.8189 | 5.6863 | 7.2474 | 7.0726 | 7.0358 | 6.9968 | 6.6463 | 6.2589 | 6.2189 | 6.1821 | 6.1421 | 5.9737 | 5.8232 | 5.6916
COWLEY GSP | YARNTON BSP | DEDDINGTON PRIMARY | MINIMUM HEADROOM | SP 46729 30325 | NO | YES | 0 | 4.8916 | 4.8421 | 4.7832 | 4.7053 | 4.5895 | 4.4389 | 4.3158 | 4.22 | 4.1232 | 1.8432 | 1.5316 | 1.2063 | 4.3705 | 4.2758 | 4.1674 | 4.0389 | 3.7158 | 3.2021 | 2.8663 | 2.7074 | 2.5484 | -0.20632 | -0.55263 | -0.91684 | 4.5474 | 4.4674 | 4.3737 | 4.2611 | 4.0011 | 3.5979 | 3.3274 | 3.1874 | 3.0474 | 0.66211 | 0.31895 | -0.04
|  | DEDDINGTON PRIMARY | EE |  |  |  |  | 4.8937 | 4.8421 | 4.7895 | 4.7179 | 4.6242 | 4.5105 | 4.4063 | 4.2947 | 4.1884 | 3.2 | 2.9884 | 2.8305 | 4.4011 | 4.3042 | 4.2021 | 4.0821 | 3.9453 | 3.6463 | 3.3453 | 3.0326 | 2.7242 | 1.3579 | 1.1179 | 0.94 | 4.5705 | 4.4874 | 4.3989 | 4.2947 | 4.1705 | 3.9284 | 3.6874 | 3.4368 | 3.1895 | 2.1642 | 1.9653 | 1.7895
|  | DEDDINGTON PRIMARY | HT |  |  |  |  | 4.8916 | 4.8442 | 4.7832 | 4.7053 | 4.5895 | 4.4389 | 4.3158 | 4.22 | 4.1232 | 1.8432 | 1.5316 | 1.2063 | 4.3705 | 4.2758 | 4.1674 | 4.0389 | 3.7158 | 3.2021 | 2.8663 | 2.7074 | 2.5484 | -0.20632 | -0.55263 | -0.91684 | 4.5474 | 4.4674 | 4.3737 | 4.2611 | 4.0011 | 3.5979 | 3.3274 | 3.1874 | 3.0474 | 0.66211 | 0.31895 | -0.04
|  | DEDDINGTON PRIMARY | HE |  |  |  |  | 4.9168 | 4.8747 | 4.8242 | 4.76 | 4.6705 | 4.5737 | 4.48 | 4.3663 | 4.2705 | 3.58 | 3.4537 | 3.3789 | 4.4716 | 4.4021 | 4.32 | 4.2211 | 4.0968 | 3.8737 | 3.6516 | 3.3147 | 3.0895 | 1.7958 | 1.6463 | 1.5579 | 4.6263 | 4.5653 | 4.4926 | 4.4042 | 4.2905 | 4.1053 | 3.9232 | 3.6537 | 3.4684 | 2.5137 | 2.3989 | 2.3316
|  | DEDDINGTON PRIMARY | FB |  |  |  |  | 4.9463 | 4.9232 | 4.9011 | 4.8768 | 4.8526 | 4.8253 | 4.7926 | 4.7611 | 4.7168 | 4.5989 | 4.5358 | 4.4937 | 4.5221 | 4.4695 | 4.4242 | 4.3768 | 4.3284 | 4.2758 | 4.1716 | 4.0663 | 3.8853 | 3.5274 | 3.3495 | 3.2179 | 4.6705 | 4.6263 | 4.5884 | 4.5484 | 4.5063 | 4.4621 | 4.38 | 4.2968 | 4.1568 | 3.8726 | 3.7305 | 3.6263
IVER 132KV GSP | DENHAM BSP | DENHAM AVENUE PRIMARY | MINIMUM HEADROOM | TQ 03761 86587 | NO | NO | 0 | 13.5074 | 13.4305 | 13.3368 | 13.2116 | 40.8632 | 40.6968 | 40.5326 | 40.2716 | 39.9579 | 29.2947 | 20.1011 | 15.8789 | 13.2211 | 13.1263 | 13.0126 | 12.8505 | 38.1663 | 37.7789 | 37.3842 | 36.9811 | 36.5747 | 23.9568 | 13.1295 | 8.1758 | 12.88 | 12.7979 | 12.6842 | 12.4516 | 38.9768 | 38.6726 | 38.3642 | 38.0526 | 37.7379 | 25.4284 | 14.6211 | 9.6758
|  | DENHAM AVENUE PRIMARY | EE |  |  |  |  | 13.5074 | 13.4305 | 13.3421 | 13.2232 | 40.8632 | 40.7074 | 40.5621 | 40.4147 | 40.2674 | 36.4505 | 33.1295 | 28.6105 | 13.2211 | 13.1263 | 13.0211 | 12.8874 | 38.3137 | 38.1442 | 37.9811 | 37.7516 | 37.5232 | 32.3558 | 28.4463 | 23.1168 | 12.88 | 12.7979 | 12.7 | 12.5358 | 39.1379 | 38.9432 | 38.7474 | 38.5495 | 38.3516 | 33.8126 | 29.9105 | 24.5905
|  | DENHAM AVENUE PRIMARY | HT |  |  |  |  | 13.5095 | 13.4337 | 13.3368 | 13.2116 | 40.8632 | 40.6968 | 40.5326 | 40.2716 | 39.9579 | 29.2947 | 20.1011 | 15.8789 | 13.2274 | 13.1337 | 13.0126 | 12.8505 | 38.1663 | 37.7789 | 37.3842 | 36.9811 | 36.5747 | 23.9568 | 13.1295 | 8.1758 | 12.8832 | 12.8021 | 12.6842 | 12.4516 | 38.9768 | 38.6726 | 38.3642 | 38.0526 | 37.7379 | 25.4284 | 14.6211 | 9.6758
|  | DENHAM AVENUE PRIMARY | HE |  |  |  |  | 13.5232 | 13.4484 | 13.3653 | 13.2484 | 40.8926 | 40.7432 | 40.5968 | 40.4516 | 40.3084 | 37.0084 | 33.8463 | 29.4611 | 13.2568 | 13.1726 | 13.08 | 12.9537 | 38.3884 | 38.2305 | 38.0737 | 37.9168 | 37.7621 | 32.9863 | 29.2505 | 24.0674 | 12.9011 | 12.8242 | 12.7379 | 12.6179 | 39.26 | 39.1084 | 38.9474 | 38.7684 | 38.5926 | 34.4421 | 30.7126 | 25.54
|  | DENHAM AVENUE PRIMARY | FB |  |  |  |  | 13.5832 | 13.5474 | 13.5147 | 13.4779 | 41.2379 | 41.1968 | 41.1579 | 41.12 | 41.0811 | 40.8211 | 37.6979 | 33.7979 | 13.3263 | 13.2779 | 13.2379 | 13.1926 | 38.7453 | 38.6958 | 38.6474 | 38.6 | 38.5516 | 37.5221 | 33.7021 | 29.1021 | 12.9642 | 12.9242 | 12.8895 | 12.8505 | 39.6084 | 39.5653 | 39.5232 | 39.48 | 39.4137 | 38.6021 | 35.1589 | 30.5663
MELKSHAM GSP | NORRINGTON BSP | DEVIZES PRIMARY | MINIMUM HEADROOM | SU 00106 60986 | NO | YES | 0 | 45.1821 | 44.2042 | 43.1295 | 42.3716 | 41.2558 | 40.1221 | 39.1274 | 38.1474 | 36.6221 | 34.0579 | 31.7768 | 29.7453 | 38.5368 | 37.4295 | 36.2095 | 35.3853 | 34.1505 | 32.9042 | 31.8189 | 30.7505 | 29.04 | 26.3389 | 23.7758 | 21.4947 | 41.3958 | 40.2832 | 39.0611 | 38.2337 | 36.9958 | 35.7453 | 34.6589 | 33.5874 | 31.8716 | 29.1747 | 26.6032 | 24.3126
|  | DEVIZES PRIMARY | EE |  |  |  |  | 45.1821 | 44.2042 | 43.1295 | 42.4116 | 41.4137 | 40.5305 | 39.7979 | 39.1779 | 38.3211 | 36.8484 | 35.4305 | 33.9979 | 38.5368 | 37.4295 | 36.2095 | 35.4253 | 34.3368 | 33.3779 | 32.5895 | 31.9347 | 31 | 29.3274 | 27.84 | 26.1989 | 41.3958 | 40.2832 | 39.0611 | 38.2747 | 37.1832 | 36.2221 | 35.4305 | 34.7758 | 33.8389 | 32.1589 | 30.6768 | 29.0284
|  | DEVIZES PRIMARY | HT |  |  |  |  | 45.2747 | 44.34 | 43.2168 | 42.3716 | 41.2558 | 40.1221 | 39.1274 | 38.1474 | 36.6221 | 34.0579 | 31.7768 | 29.7453 | 38.6421 | 37.5811 | 36.3137 | 35.3853 | 34.1505 | 32.9042 | 31.8189 | 30.7505 | 29.04 | 26.3389 | 23.7758 | 21.4947 | 41.5021 | 40.4379 | 39.1632 | 38.2337 | 36.9958 | 35.7453 | 34.6589 | 33.5874 | 31.8716 | 29.1747 | 26.6032 | 24.3126
|  | DEVIZES PRIMARY | HE |  |  |  |  | 45.4874 | 44.6221 | 43.6432 | 43.0021 | 42.0516 | 41.2442 | 40.6221 | 40.1179 | 39.3747 | 38.7905 | 37.6463 | 36.6611 | 38.8842 | 37.9053 | 36.7979 | 36.1032 | 35.0716 | 34.1968 | 33.5389 | 33.02 | 32.2189 | 31.5274 | 30.2011 | 29.0547 | 41.7442 | 40.7621 | 39.6516 | 38.9558 | 37.9211 | 37.0442 | 36.3853 | 35.8663 | 35.0642 | 34.3695 | 33.0379 | 31.8863
|  | DEVIZES PRIMARY | FB |  |  |  |  | 45.7968 | 45.3453 | 44.9221 | 44.6368 | 44.2758 | 43.9316 | 43.6632 | 43.4653 | 43.2611 | 42.3158 | 41.2389 | 40.2989 | 39.2189 | 38.7063 | 38.2263 | 37.9105 | 37.5074 | 37.1242 | 36.8284 | 36.6158 | 36.3968 | 35.3611 | 34.1379 | 33.06 | 42.08 | 41.5663 | 41.0842 | 40.7674 | 40.3632 | 39.9789 | 39.6821 | 39.4695 | 39.2505 | 38.2116 | 36.9842 | 35.9032
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH PRIMARY | MINIMUM HEADROOM | SU 19288 83540 | NO | YES | 0 | 26.3389 | 26.3042 | 26.2642 | 26.2137 | 26.1368 | 26.0463 | 25.7979 | 25.3074 | 24.9105 | 24.5958 | 24.1295 | 23.7874 | 27.5832 | 27.5484 | 27.5095 | 27.4589 | 27.2958 | 26.9547 | 26.3758 | 25.8011 | 25.3432 | 24.9758 | 24.4674 | 24.0789 | 26.8347 | 26.7632 | 26.6916 | 26.6116 | 26.3926 | 26.0526 | 25.4747 | 24.9011 | 24.4453 | 24.0789 | 23.5716 | 23.1842
|  | DORCAN SOUTH PRIMARY | EE |  |  |  |  | 26.3389 | 26.3042 | 26.2642 | 26.2147 | 26.1495 | 26.0758 | 25.9968 | 25.7937 | 25.46 | 24.5958 | 24.64 | 24.3989 | 27.5832 | 27.5484 | 27.5095 | 27.4611 | 27.3968 | 27.24 | 26.8905 | 26.4042 | 25.9863 | 24.9758 | 25.1432 | 24.8653 | 26.8347 | 26.7632 | 26.6916 | 26.6116 | 26.5211 | 26.3368 | 25.9874 | 25.5032 | 25.0863 | 24.0789 | 24.2989 | 24.0221
|  | DORCAN SOUTH PRIMARY | HT |  |  |  |  | 26.3442 | 26.3116 | 26.2684 | 26.2137 | 26.1368 | 26.0463 | 25.7979 | 25.3074 | 24.9105 | 24.7684 | 24.1295 | 23.7874 | 27.5874 | 27.5558 | 27.5126 | 27.4589 | 27.2958 | 26.9547 | 26.3758 | 25.8011 | 25.3432 | 25.3105 | 24.4674 | 24.0789 | 26.8516 | 26.7884 | 26.7147 | 26.6326 | 26.3926 | 26.0526 | 25.4747 | 24.9011 | 24.4453 | 24.4663 | 23.5716 | 23.1842
|  | DORCAN SOUTH PRIMARY | HE |  |  |  |  | 26.3558 | 26.3263 | 26.2905 | 26.2442 | 26.1789 | 26.1116 | 26.0305 | 25.8663 | 25.56 | 24.8432 | 24.6621 | 24.4779 | 27.5989 | 27.5695 | 27.5337 | 27.4884 | 27.4232 | 27.3589 | 27.0189 | 26.5242 | 26.1 | 25.2547 | 25.0442 | 24.8284 | 26.8905 | 26.8421 | 26.7863 | 26.7232 | 26.6411 | 26.4653 | 26.1158 | 25.6232 | 25.2 | 24.3579 | 24.1474 | 23.9316
|  | DORCAN SOUTH PRIMARY | FB |  |  |  |  | 26.3779 | 26.3589 | 26.3421 | 26.3242 | 26.3032 | 26.2832 | 26.2611 | 26.2358 | 26.2063 | 25.7663 | 25.5758 | 25.4242 | 27.62 | 27.6011 | 27.5853 | 27.5674 | 27.5474 | 27.5274 | 27.5074 | 27.4421 | 27.2832 | 26.3032 | 26.0853 | 25.9105 | 26.9305 | 26.8874 | 26.8547 | 26.82 | 26.7842 | 26.7484 | 26.6695 | 26.5379 | 26.38 | 25.4032 | 25.1853 | 25.0105
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER PRIMARY | MINIMUM HEADROOM | SY 69113 90401 | NO | YES | 0 | 33.2742 | 46.4721 | 46.2363 | 45.8984 | 45.4511 | 44.6711 | 43.5711 | 42.4289 | 41.2847 | 38.4195 | 36.4605 | 34.6974 | 29.2032 | 46.5379 | 46.3021 | 45.9642 | 44.7442 | 43.3811 | 42.0221 | 40.6021 | 39.1789 | 35.5768 | 33.0916 | 30.8526 | 31.4747 | 45.9495 | 45.7147 | 45.3768 | 44.9295 | 44.3168 | 42.9811 | 41.5863 | 40.1884 | 36.6611 | 34.2232 | 32.0274
|  | DORCHESTER PRIMARY | EE |  |  |  |  | 46.6932 | 46.4721 | 46.2363 | 45.9111 | 45.4511 | 45.0289 | 44.6458 | 44.2458 | 43.7216 | 42.1542 | 40.7395 | 39.5111 | 46.7589 | 46.5379 | 46.3021 | 45.9768 | 45.5168 | 44.9442 | 44.1337 | 43.32 | 42.5263 | 40.4589 | 38.5979 | 36.9758 | 46.1716 | 45.9495 | 45.7147 | 45.3895 | 44.9295 | 44.5074 | 44.1232 | 43.7242 | 43.3305 | 41.4368 | 39.6179 | 38.0305
|  | DORCHESTER PRIMARY | HT |  |  |  |  | 46.7058 | 46.5037 | 46.2384 | 45.8984 | 45.4879 | 44.6711 | 43.5711 | 42.4289 | 41.2847 | 38.4195 | 36.4605 | 34.6974 | 46.7716 | 46.5695 | 46.3042 | 45.9642 | 44.7442 | 43.3811 | 42.0221 | 40.6021 | 39.1789 | 35.5768 | 33.0916 | 30.8526 | 46.1842 | 45.9821 | 45.7158 | 45.3768 | 44.9663 | 44.3168 | 42.9811 | 41.5863 | 40.1884 | 36.6611 | 34.2232 | 32.0274
|  | DORCHESTER PRIMARY | HE |  |  |  |  | 46.7321 | 46.5184 | 46.2953 | 45.9753 | 45.5142 | 45.11 | 44.7195 | 44.3174 | 43.9226 | 43.8047 | 42.8363 | 42.0174 | 46.7979 | 46.5842 | 46.3611 | 46.0411 | 45.58 | 45.1758 | 44.7853 | 44.3295 | 43.6674 | 42.5905 | 41.2695 | 40.1474 | 46.2105 | 45.9968 | 45.7737 | 45.4537 | 44.9926 | 44.5884 | 44.1979 | 43.7958 | 43.4011 | 43.4832 | 42.2305 | 41.1368
|  | DORCHESTER PRIMARY | FB |  |  |  |  | 33.2742 | 46.7921 | 46.6974 | 46.5921 | 46.4742 | 46.3563 | 46.2416 | 46.1353 | 46.0205 | 45.6016 | 45.3068 | 44.5016 | 29.2032 | 46.8579 | 46.7632 | 46.6579 | 46.54 | 46.4221 | 46.3074 | 46.2011 | 46.0863 | 45.3347 | 44.1379 | 43.0737 | 31.4747 | 46.2705 | 46.1758 | 46.0705 | 45.9526 | 45.8347 | 45.72 | 45.6137 | 45.4989 | 45.08 | 44.8453 | 44.0221
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | DOWN GRANGE PRIMARY | MINIMUM HEADROOM | SU 61604 50238 | NO | YES | 0 | 32.5016 | 31.7774 | 30.91 | 29.8574 | 28.7289 | 27.5184 | 26.2668 | 24.9026 | 23.5511 | 20.3121 | 18.3395 | 16.0195 | 29.7126 | 28.5453 | 27.1147 | 25.4547 | 23.7642 | 21.9716 | 20.4895 | 19.0053 | 17.5358 | 14.0042 | 11.8547 | 9.2768 | 29.0263 | 27.9221 | 26.5716 | 24.9968 | 23.3863 | 21.6747 | 20.2516 | 18.8284 | 17.4179 | 14.0347 | 11.9737 | 9.5253
|  | DOWN GRANGE PRIMARY | EE |  |  |  |  | 32.5016 | 31.7774 | 30.91 | 29.9774 | 28.9511 | 27.99 | 27.1311 | 26.1268 | 24.8468 | 22.4689 | 21.3174 | 19.8026 | 29.7126 | 28.5453 | 27.1147 | 25.6947 | 24.2947 | 22.9979 | 21.8632 | 20.4316 | 19.0274 | 16.3095 | 15.0253 | 13.2968 | 29.0263 | 27.9221 | 26.5716 | 25.2189 | 23.8726 | 22.6242 | 21.5263 | 20.1558 | 18.8116 | 16.2642 | 15.0463 | 13.4253
|  | DOWN GRANGE PRIMARY | HT |  |  |  |  | 32.5805 | 31.9026 | 30.9595 | 29.8574 | 28.7289 | 27.5184 | 26.2668 | 24.9026 | 23.5511 | 20.3121 | 18.3395 | 16.0195 | 29.8621 | 28.7674 | 27.2147 | 25.4547 | 23.7642 | 21.9716 | 20.4895 | 19.0053 | 17.5358 | 14.0042 | 11.8547 | 9.2768 | 29.1674 | 28.1295 | 26.6642 | 24.9968 | 23.3863 | 21.6747 | 20.2516 | 18.8284 | 17.4179 | 14.0347 | 11.9737 | 9.5253
|  | DOWN GRANGE PRIMARY | HE |  |  |  |  | 32.77 | 32.1416 | 31.3647 | 30.5005 | 29.5195 | 28.6321 | 27.8216 | 26.9226 | 26.0405 | 24.7974 | 24.2553 | 23.7342 | 30.2074 | 29.2295 | 27.9716 | 26.6884 | 25.3779 | 24.2032 | 23.1737 | 21.9695 | 20.7874 | 18.9305 | 18.3095 | 17.7074 | 29.4905 | 28.5611 | 27.3716 | 26.1474 | 24.8832 | 23.7495 | 22.7505 | 21.5905 | 20.4495 | 18.7389 | 18.1579 | 17.5958
|  | DOWN GRANGE PRIMARY | FB |  |  |  |  | 33.1858 | 32.8363 | 32.4763 | 32.1279 | 31.7911 | 31.4605 | 31.1637 | 30.8711 | 30.5184 | 29.1195 | 28.4584 | 27.95 | 30.7358 | 30.2432 | 29.6305 | 29.06 | 28.54 | 28.0326 | 27.5916 | 27.1463 | 26.5832 | 24.2937 | 23.2726 | 22.4337 | 30.1095 | 29.5295 | 28.9526 | 28.4137 | 27.9189 | 27.4368 | 27.0168 | 26.5926 | 26.0589 | 23.8958 | 22.9263 | 22.1337
MINETY GSP | STRATTON (MAIN) BSP | DRAKES WAY PRIMARY | MINIMUM HEADROOM | SU 16899 85647 | NO | YES | 0 | 16.2845 | 16.2561 | 16.2234 | 16.1782 | 16.1213 | 15.8487 | 15.155 | 14.3866 | 13.7834 | 13.2308 | 12.8697 | 12.5203 | 14.8595 | 14.8068 | 14.7311 | 14.6774 | 14.2721 | 13.7226 | 12.8805 | 12.0142 | 11.3363 | 10.7268 | 10.3279 | 9.9311 | 15.0737 | 14.9053 | 14.7842 | 14.7168 | 14.2758 | 13.7474 | 12.9389 | 12.1084 | 11.4316 | 10.82 | 10.4211 | 10.0326
|  | DRAKES WAY PRIMARY | EE |  |  |  |  | 16.2845 | 16.2561 | 16.2234 | 16.1824 | 16.1245 | 16.0708 | 15.8234 | 15.2287 | 14.6676 | 13.2918 | 13.0234 | 12.7697 | 14.8595 | 14.8289 | 14.7311 | 14.6774 | 14.6089 | 14.2984 | 13.7026 | 12.9689 | 12.3374 | 10.7795 | 10.4784 | 10.1858 | 15.0737 | 15.0137 | 14.7842 | 14.7168 | 14.6358 | 14.2979 | 13.7263 | 13.0221 | 12.4168 | 10.8716 | 10.5716 | 10.2863
|  | DRAKES WAY PRIMARY | HT |  |  |  |  | 16.2887 | 16.2613 | 16.2245 | 16.1782 | 16.1213 | 15.8487 | 15.155 | 14.3866 | 13.7834 | 13.2308 | 12.8697 | 12.5203 | 14.8637 | 14.8068 | 14.7574 | 14.7005 | 14.2721 | 13.7226 | 12.8805 | 12.0142 | 11.3363 | 10.7268 | 10.3279 | 9.9311 | 15.0884 | 14.9053 | 14.8411 | 14.7716 | 14.2758 | 13.7474 | 12.9389 | 12.1084 | 11.4316 | 10.82 | 10.4211 | 10.0326
|  | DRAKES WAY PRIMARY | HE |  |  |  |  | 16.2982 | 16.2729 | 16.2413 | 16.2013 | 16.1455 | 16.0918 | 15.9034 | 15.3161 | 14.7497 | 13.595 | 13.4076 | 13.2245 | 14.8742 | 14.8479 | 14.7774 | 14.73 | 14.6668 | 14.3974 | 13.8037 | 13.0647 | 12.4279 | 11.1153 | 10.9058 | 10.6984 | 15.1232 | 15.08 | 14.8642 | 14.8084 | 14.7368 | 14.3937 | 13.8242 | 13.1158 | 12.5042 | 11.2095 | 10.9989 | 10.7905
|  | DRAKES WAY PRIMARY | FB |  |  |  |  | 16.3139 | 16.2992 | 16.2855 | 16.2697 | 16.2529 | 16.2361 | 16.2192 | 16.2034 | 16.1876 | 15.1361 | 14.9182 | 14.755 | 14.8911 | 14.8753 | 14.8605 | 14.8416 | 14.8237 | 14.8037 | 14.7279 | 14.5763 | 14.3447 | 12.8416 | 12.5974 | 12.4153 | 15.1547 | 15.1189 | 15.0905 | 14.9905 | 14.9589 | 14.9284 | 14.7811 | 14.5695 | 14.3474 | 12.9074 | 12.6726 | 12.4979
NURSLING GSP | WINCHESTER BSP | DUNBRIDGE PRIMARY | MINIMUM HEADROOM | SU 31520 26244 | NO | YES | 0 | 6.6558 | 13.21 | 12.9784 | 12.7911 | 12.5605 | 12.3458 | 12.1216 | 11.8953 | 11.6626 | 10.1237 | 3.7626 | -11.3247 | 6.5274 | 12.1605 | 11.9058 | 11.7068 | 11.4679 | 11.2437 | 11.0047 | 10.7658 | 10.5311 | 8.5753 | 1.0953 | -16.5142 | 6.5295 | 12.6137 | 12.3589 | 12.16 | 11.9221 | 11.6979 | 11.4589 | 11.2189 | 10.9853 | 9.0389 | 1.5811 | -15.9779
|  | DUNBRIDGE PRIMARY | EE |  |  |  |  | 6.6558 | 13.2426 | 12.9784 | 12.7911 | 12.5605 | 12.3458 | 12.1216 | 11.8953 | 11.6742 | 11.2521 | 3.9479 | -11.3247 | 6.5274 | 12.2005 | 11.9058 | 11.7068 | 11.4679 | 11.2437 | 11.0047 | 10.7658 | 10.5311 | 10.0511 | 1.4637 | -16.5142 | 6.5295 | 12.6537 | 12.3589 | 12.16 | 11.9221 | 11.6979 | 11.4589 | 11.2189 | 10.9853 | 10.5074 | 1.9453 | -15.9779
|  | DUNBRIDGE PRIMARY | HT |  |  |  |  | 6.6842 | 13.21 | 13.0395 | 12.8437 | 12.6289 | 12.3889 | 12.1521 | 11.9047 | 11.6626 | 10.9584 | 10.2963 | -3.5279 | 6.5611 | 12.1605 | 11.9784 | 11.7721 | 11.5489 | 11.2974 | 11.05 | 10.7889 | 10.5342 | 9.7721 | 9.0342 | -7.2153 | 6.5632 | 12.6137 | 12.4316 | 12.2263 | 12.0032 | 11.7516 | 11.5032 | 11.2432 | 10.9884 | 10.2284 | 9.4916 | -6.7084
|  | DUNBRIDGE PRIMARY | HE |  |  |  |  | 6.7695 | 13.4005 | 13.1774 | 13.0247 | 12.8226 | 12.6405 | 12.4637 | 12.2858 | 12.11 | 12.0047 | 4.8847 | -10.2353 | 6.6568 | 12.3816 | 12.1321 | 11.9732 | 11.7647 | 11.5774 | 11.3942 | 11.2111 | 11.0289 | 10.9005 | 2.5174 | -15.2911 | 6.6589 | 12.8337 | 12.5853 | 12.4263 | 12.2179 | 12.0305 | 11.8474 | 11.6642 | 11.4821 | 11.3547 | 2.9968 | -14.7568
|  | DUNBRIDGE PRIMARY | FB |  |  |  |  | 6.8663 | 13.53 | 13.4637 | 13.3542 | 13.2774 | 13.2037 | 13.1311 | 13.0626 | 12.99 | 10.1237 | 3.7626 | -9.5321 | 6.7611 | 12.5153 | 12.4426 | 12.3195 | 12.2374 | 12.1574 | 12.0795 | 12.0037 | 11.9268 | 8.5753 | 1.0953 | -14.5563 | 6.7632 | 12.9674 | 12.8958 | 12.7726 | 12.6905 | 12.6105 | 12.5326 | 12.4568 | 12.38 | 9.0389 | 1.5811 | -14.0232
EALING GSP |  | EALING PRIMARY | MINIMUM HEADROOM | SZ 06789 95116 | NO | YES | 0 | 86.8421 | 86.6158 | 86.3558 | 86.0074 | 84.8895 | 83.3337 | 81.6189 | 79.7432 | 77.7989 | 73.5526 | 71.7358 | 70.0905 | 89.5284 | 87.8832 | 86.0674 | 83.8968 | 81.8295 | 80.0537 | 78.0895 | 75.9295 | 73.6884 | 68.76 | 66.6695 | 64.7747 | 87.1263 | 85.4926 | 83.6411 | 81.4284 | 79.2568 | 77.4516 | 75.4537 | 73.2547 | 70.9716 | 66.0295 | 63.9726 | 62.1084
|  | EALING PRIMARY | EE |  |  |  |  | 86.8421 | 86.6158 | 86.3558 | 86.0074 | 85.1958 | 83.9432 | 82.7137 | 81.4558 | 80.4284 | 77.7053 | 76.5474 | 75.5537 | 89.5411 | 88.0926 | 86.2547 | 84.2442 | 82.1758 | 80.7653 | 79.3758 | 77.9568 | 76.8158 | 73.6495 | 72.3189 | 71.1758 | 87.1263 | 85.7084 | 83.8337 | 81.7842 | 79.68 | 78.2474 | 76.8368 | 75.3947 | 74.2379 | 70.9411 | 69.5874 | 68.4232
|  | EALING PRIMARY | HT |  |  |  |  | 86.8611 | 86.6579 | 86.3874 | 86.0389 | 84.8895 | 83.3337 | 81.6189 | 79.7432 | 77.7989 | 73.5526 | 71.7358 | 70.0905 | 89.5284 | 87.8832 | 86.0674 | 83.8968 | 81.8295 | 80.0537 | 78.0895 | 75.9295 | 73.6884 | 68.76 | 66.6695 | 64.7747 | 87.1453 | 85.4926 | 83.6411 | 81.4284 | 79.2568 | 77.4516 | 75.4537 | 73.2547 | 70.9716 | 66.0295 | 63.9726 | 62.1084
|  | EALING PRIMARY | HE |  |  |  |  | 86.8705 | 86.6484 | 86.3979 | 86.0516 | 85.5768 | 84.5842 | 83.4589 | 82.2989 | 81.3758 | 79.6474 | 79.1011 | 78.6242 | 89.6537 | 88.5147 | 86.7926 | 84.8737 | 82.8674 | 81.5242 | 80.2632 | 78.9621 | 77.9442 | 75.8979 | 75.2526 | 74.6874 | 87.1547 | 86.1389 | 84.3832 | 82.4274 | 80.3863 | 79.0232 | 77.7432 | 76.4232 | 75.3916 | 73.2316 | 72.5726 | 71.9947
|  | EALING PRIMARY | FB |  |  |  |  | 87.0253 | 86.8926 | 86.7716 | 86.6368 | 86.4863 | 86.3347 | 86.1884 | 86.0516 | 85.9053 | 85.3695 | 84.9368 | 84.1968 | 89.8084 | 89.6758 | 89.0053 | 88.2242 | 87.3095 | 86.6568 | 86.1863 | 85.6453 | 85.2221 | 82.7011 | 81.9958 | 81.1463 | 87.3095 | 87.1768 | 86.6389 | 85.8421 | 84.9095 | 84.2463 | 83.7684 | 83.2179 | 82.7874 | 80.2211 | 79.4411 | 78.5758
LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT PRIMARY | MINIMUM HEADROOM | TQ 08394 73826 | NO | YES | 0 | 39.7074 | 39.3916 | 39.0495 | 38.6558 | 37.9642 | 37.1 | 36.0105 | 34.7832 | 33.4242 | 30.3116 | 28.8863 | 27.5558 | 37.6305 | 37.2705 | 36.8895 | 36.4589 | 35.6632 | 34.6516 | 33.3505 | 31.8705 | 30.2211 | 26.4621 | 24.7811 | 23.2032 | 38.9242 | 38.6168 | 38.2811 | 37.8926 | 37.22 | 36.3811 | 35.3284 | 34.1432 | 32.8011 | 29.1274 | 27.48 | 25.9347
|  | EAST BEDFONT PRIMARY | EE |  |  |  |  | 39.7811 | 39.4726 | 39.1389 | 38.7674 | 38.3274 | 37.8211 | 37.2316 | 36.5768 | 35.8926 | 33.2768 | 32.4084 | 31.6168 | 37.7253 | 37.3747 | 36.9979 | 36.5895 | 36.1179 | 35.56 | 34.8863 | 34.1305 | 33.3379 | 30.0316 | 28.9695 | 27.9958 | 38.9947 | 38.6937 | 38.3663 | 38.0021 | 37.5674 | 37.0705 | 36.4947 | 35.8558 | 35.1916 | 32.6179 | 31.5821 | 30.6305
|  | EAST BEDFONT PRIMARY | HT |  |  |  |  | 39.7074 | 39.3916 | 39.0495 | 38.6558 | 37.9642 | 37.1 | 36.0105 | 34.7832 | 33.4242 | 30.3116 | 28.8863 | 27.5558 | 37.6305 | 37.2705 | 36.8895 | 36.4589 | 35.6632 | 34.6516 | 33.3505 | 31.8705 | 30.2211 | 26.4621 | 24.7811 | 23.2032 | 38.9242 | 38.6168 | 38.2811 | 37.8926 | 37.22 | 36.3811 | 35.3284 | 34.1432 | 32.8011 | 29.1274 | 27.48 | 25.9347
|  | EAST BEDFONT PRIMARY | HE |  |  |  |  | 39.9674 | 39.7305 | 39.4621 | 39.1432 | 38.7337 | 38.2684 | 37.7232 | 37.1053 | 36.4568 | 34.3547 | 33.7968 | 33.2684 | 37.9579 | 37.6968 | 37.4011 | 37.0611 | 36.6295 | 36.12 | 35.5042 | 34.7968 | 34.0484 | 31.3358 | 30.6316 | 29.9611 | 39.1737 | 38.94 | 38.6768 | 38.3621 | 37.9558 | 37.4979 | 36.9653 | 36.3621 | 35.7305 | 33.7337 | 33.2011 | 32.5547
|  | EAST BEDFONT PRIMARY | FB |  |  |  |  | 42.2568 | 40.12 | 39.9821 | 39.8295 | 39.6737 | 39.5158 | 39.3274 | 39.1179 | 38.8926 | 36.9495 | 36.2274 | 35.6821 | 40.8705 | 38.1432 | 37.9853 | 37.8137 | 37.6389 | 37.4621 | 37.2442 | 36.9979 | 36.7347 | 34.3263 | 33.4484 | 32.78 | 41.3558 | 39.32 | 39.1853 | 39.0368 | 38.8842 | 38.7295 | 38.5453 | 38.3421 | 38.1242 | 36.2611 | 35.5653 | 35.0411
MANNINGTON GSP | REDHILL BSP | EAST HOWE PRIMARY | MINIMUM HEADROOM | SZ 06789 95116 | NO | YES | 0 | 25.4691 | 24.7481 | 23.8449 | 22.8554 | 21.7628 | 20.3007 | 18.8997 | 17.4344 | 15.9923 | 12.8649 | 10.6754 | 8.5081 | 22.6141 | 21.7509 | 20.6562 | 19.4941 | 18.2298 | 16.4362 | 14.7183 | 12.9025 | 11.1172 | 7.2909 | 4.5541 | 2.0983 | 24.3082 | 23.4261 | 22.304 | 21.1177 | 19.8251 | 18.0272 | 16.3114 | 14.4998 | 12.7177 | 8.8998 | 6.1682 | 3.7177
|  | EAST HOWE PRIMARY | EE |  |  |  |  | 25.4691 | 24.7481 | 23.9765 | 23.2576 | 22.3933 | 21.5965 | 20.8576 | 20.086 | 19.3533 | 17.9828 | 16.5302 | 15.2902 | 22.6141 | 21.7509 | 20.8298 | 20.0235 | 19.0856 | 18.2235 | 17.4225 | 16.5825 | 15.7919 | 14.0119 | 12.0962 | 10.4477 | 24.3082 | 23.4261 | 22.4829 | 21.664 | 20.7166 | 19.8472 | 19.0366 | 18.1851 | 17.3829 | 15.604 | 13.6935 | 12.0493
|  | EAST HOWE PRIMARY | HT |  |  |  |  | 25.5439 | 24.7618 | 23.8449 | 22.8554 | 21.7628 | 20.3007 | 18.8997 | 17.4344 | 15.9923 | 12.8649 | 10.6754 | 8.5081 | 22.7098 | 21.7572 | 20.6562 | 19.4941 | 18.2298 | 16.4362 | 14.7183 | 12.9025 | 11.1172 | 7.2909 | 4.5541 | 2.0983 | 24.4072 | 23.4303 | 22.304 | 21.1177 | 19.8251 | 18.0272 | 16.3114 | 14.4998 | 12.7177 | 8.8998 | 6.1682 | 3.7177
|  | EAST HOWE PRIMARY | HE |  |  |  |  | 25.8386 | 25.2576 | 24.6049 | 23.9839 | 23.1912 | 22.4891 | 21.8354 | 21.1512 | 20.5049 | 19.9544 | 19.0312 | 18.2386 | 23.0835 | 22.4004 | 21.633 | 20.953 | 20.1067 | 19.3614 | 18.6751 | 17.9519 | 17.2762 | 16.5151 | 15.2677 | 14.1625 | 24.7914 | 24.0945 | 23.3114 | 22.624 | 21.7693 | 21.0177 | 20.3272 | 19.5987 | 18.9187 | 18.1282 | 16.8577 | 15.7566
|  | EAST HOWE PRIMARY | FB |  |  |  |  | 26.3302 | 25.9597 | 25.6428 | 25.387 | 25.0902 | 24.8239 | 24.567 | 24.3239 | 24.0733 | 22.9544 | 21.9397 | 21.0944 | 23.6709 | 23.2193 | 22.8351 | 22.5383 | 22.1951 | 21.8898 | 21.5983 | 21.3204 | 21.0362 | 19.7214 | 18.4572 | 17.3541 | 25.3924 | 24.9293 | 24.5356 | 24.2335 | 23.8829 | 23.5735 | 23.2766 | 22.9935 | 22.7051 | 21.3629 | 20.064 | 18.944
MELKSHAM GSP | NORRINGTON BSP | EASTERTON PRIMARY | MINIMUM HEADROOM | SU 01568 54730 | NO | YES | 0 | 15.8676 | 15.6908 | 15.515 | 15.2918 | 15.0045 | 14.6824 | 14.3518 | 13.995 | 13.6297 | 11.1382 | 10.3824 | 9.7182 | 13.2542 | 13.0563 | 12.8595 | 12.6195 | 12.3026 | 11.9468 | 11.5795 | 11.1774 | 10.7637 | 7.6911 | 6.7953 | 6.0089 | 14.1705 | 13.9747 | 13.7821 | 13.5442 | 13.2326 | 12.8821 | 12.5211 | 12.1263 | 11.72 | 8.7432 | 7.8705 | 7.1032
|  | EASTERTON PRIMARY | EE |  |  |  |  | 15.8676 | 15.6908 | 15.515 | 15.3066 | 15.0518 | 14.815 | 14.5866 | 14.3529 | 14.1266 | 12.8992 | 12.3771 | 11.935 | 13.2542 | 13.0563 | 12.8595 | 12.6332 | 12.3626 | 12.1111 | 11.8647 | 11.6132 | 11.3711 | 9.8289 | 9.19 | 8.6479 | 14.1705 | 13.9747 | 13.7821 | 13.5579 | 13.2905 | 13.04 | 12.7968 | 12.5495 | 12.3095 | 10.8189 | 10.2 | 9.6747
|  | EASTERTON PRIMARY | HT |  |  |  |  | 15.9024 | 15.7382 | 15.5424 | 15.2918 | 15.0045 | 14.6824 | 14.3518 | 13.995 | 13.6297 | 11.1382 | 10.3824 | 9.7182 | 13.2974 | 13.1142 | 12.8974 | 12.6195 | 12.3026 | 11.9468 | 11.5795 | 11.1774 | 10.7637 | 7.6911 | 6.7953 | 6.0089 | 14.2116 | 14.0316 | 13.8179 | 13.5442 | 13.2326 | 12.8821 | 12.5211 | 12.1263 | 11.72 | 8.7432 | 7.8705 | 7.1032
|  | EASTERTON PRIMARY | HE |  |  |  |  | 15.9876 | 15.8561 | 15.7224 | 15.5497 | 15.3192 | 15.1139 | 14.9182 | 14.7224 | 14.5287 | 13.5813 | 13.2329 | 12.9361 | 13.4005 | 13.2574 | 13.1121 | 12.9289 | 12.6889 | 12.4732 | 12.2689 | 12.0647 | 11.8626 | 10.6426 | 10.2037 | 9.83 | 14.3116 | 14.1705 | 14.0274 | 13.8453 | 13.6074 | 13.3937 | 13.1905 | 12.9874 | 12.7863 | 11.6116 | 11.1874 | 10.8263
|  | EASTERTON PRIMARY | FB |  |  |  |  | 16.1203 | 16.0287 | 15.9571 | 15.8813 | 15.8013 | 15.7203 | 15.6434 | 15.5708 | 15.495 | 15.1518 | 14.8013 | 14.5034 | 13.55 | 13.4437 | 13.3637 | 13.2774 | 13.1868 | 13.0974 | 13.0111 | 12.9289 | 12.8447 | 12.45 | 12.0247 | 11.6584 | 14.4589 | 14.3547 | 14.2758 | 14.1916 | 14.1021 | 14.0147 | 13.9295 | 13.8495 | 13.7663 | 13.38 | 12.9674 | 12.6116
FLEET-BRAMLEY GSP | BRACKNELL BSP | EASTHAMPSTEAD PRIMARY | MINIMUM HEADROOM | SU 86148 67194 | NO | YES | 0 | 34.3647 | 34.1237 | 33.8321 | 33.4405 | 32.6132 | 31.5026 | 30.6858 | 29.7889 | 28.9384 | 26.1753 | 23.7584 | 21.5953 | 29.5516 | 29.04 | 28.5147 | 27.4621 | 26.2126 | 24.9263 | 24.0168 | 23.0032 | 22.0495 | 18.9147 | 16.1947 | 13.7579 | 30.0674 | 29.5947 | 29.1053 | 28.1579 | 27.0253 | 25.8547 | 25.0063 | 24.0684 | 23.1821 | 20.34 | 17.9147 | 15.7021
|  | EASTHAMPSTEAD PRIMARY | EE |  |  |  |  | 34.3647 | 34.1237 | 33.8321 | 33.4405 | 32.9216 | 32.4026 | 31.6711 | 30.87 | 30.1384 | 28.7711 | 27.1468 | 25.6647 | 29.5516 | 29.04 | 28.5147 | 27.8474 | 27.0821 | 26.2 | 25.2989 | 24.4053 | 23.5979 | 21.9442 | 19.9832 | 18.2821 | 30.0674 | 29.5947 | 29.1053 | 28.4821 | 27.7537 | 26.9295 | 26.0926 | 25.2589 | 24.5021 | 23.0358 | 21.3147 | 19.8253
|  | EASTHAMPSTEAD PRIMARY | HT |  |  |  |  | 34.3942 | 34.1753 | 33.8721 | 33.4511 | 32.6132 | 31.5026 | 30.6858 | 29.7889 | 28.9384 | 26.1753 | 23.7584 | 21.5953 | 29.6758 | 29.2105 | 28.5284 | 27.4621 | 26.2126 | 24.9263 | 24.0168 | 23.0032 | 22.0495 | 18.9147 | 16.1947 | 13.7579 | 30.1779 | 29.7474 | 29.1232 | 28.1579 | 27.0253 | 25.8547 | 25.0063 | 24.0684 | 23.1821 | 20.34 | 17.9147 | 15.7021
|  | EASTHAMPSTEAD PRIMARY | HE |  |  |  |  | 34.4111 | 34.1679 | 33.8847 | 33.5016 | 32.9805 | 32.47 | 31.9679 | 31.4626 | 30.9058 | 30.2111 | 29.0721 | 28.0889 | 29.9021 | 29.5147 | 29.0958 | 28.5095 | 27.7884 | 26.9737 | 26.1432 | 25.3263 | 24.5905 | 23.6947 | 22.2558 | 21.0074 | 30.3737 | 30.0063 | 29.6074 | 29.0505 | 28.36 | 27.5916 | 26.8137 | 26.0453 | 25.3474 | 24.5842 | 23.3411 | 22.2663
|  | EASTHAMPSTEAD PRIMARY | FB |  |  |  |  | 34.5889 | 34.4637 | 34.35 | 34.2237 | 34.0837 | 33.9416 | 33.7911 | 33.6468 | 33.4942 | 32.8037 | 31.7216 | 30.8047 | 30.2758 | 29.9674 | 29.7358 | 29.4705 | 29.1779 | 28.8221 | 28.4484 | 28.0853 | 27.7442 | 26.4663 | 25.1547 | 24.0253 | 30.7179 | 30.4368 | 30.2221 | 29.9779 | 29.7063 | 29.3821 | 29.0432 | 28.7137 | 28.4032 | 27.2379 | 26.0768 | 25.0863
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH PRIMARY | MINIMUM HEADROOM | SU 45426 18958 | NO | YES | 0.031579 | 45.5105 | 44.4105 | 43.2 | 41.6137 | 39.4642 | 36.9442 | 34.3926 | 32.1411 | 30.1832 | 25.5189 | 22.2758 | 19.3495 | 39.6347 | 39.2084 | 38.7442 | 38.0926 | 36.1811 | 33.1442 | 30.0653 | 27.3705 | 25.0505 | 19.5158 | 15.6284 | 12.1495 | 42.7568 | 41.4442 | 39.9968 | 38.1158 | 35.5432 | 32.5147 | 29.4432 | 26.7537 | 24.4389 | 18.9221 | 15.0421 | 11.5716
|  | EASTLEIGH NORTH PRIMARY | EE |  |  |  |  | 45.5105 | 44.4105 | 43.2 | 41.6674 | 39.6842 | 37.4621 | 35.3505 | 33.7053 | 32.4442 | 29.8316 | 27.5653 | 25.58 | 39.6347 | 39.2084 | 38.7442 | 38.1253 | 36.4758 | 33.8095 | 31.2653 | 29.3305 | 27.8853 | 24.6568 | 21.8716 | 19.4168 | 42.7568 | 41.4442 | 39.9968 | 38.1768 | 35.8379 | 33.1768 | 30.6389 | 28.7074 | 27.2642 | 24.0453 | 21.2726 | 18.8232
|  | EASTLEIGH NORTH PRIMARY | HT |  |  |  |  | 45.6347 | 44.6 | 43.3442 | 41.6137 | 39.4642 | 36.9442 | 34.3926 | 32.1411 | 30.1832 | 25.5189 | 22.2758 | 19.3495 | 39.6663 | 39.2695 | 38.7589 | 38.0926 | 36.1811 | 33.1442 | 30.0653 | 27.3705 | 25.0505 | 19.5158 | 15.6284 | 12.1495 | 42.9105 | 41.6737 | 40.1832 | 38.1158 | 35.5432 | 32.5147 | 29.4432 | 26.7537 | 24.4389 | 18.9221 | 15.0421 | 11.5716
|  | EASTLEIGH NORTH PRIMARY | HE |  |  |  |  | 45.9316 | 44.9916 | 43.9211 | 42.5032 | 40.5979 | 38.4863 | 36.4979 | 34.9779 | 33.8411 | 32.32 | 30.7105 | 29.3126 | 39.7589 | 39.3674 | 38.9389 | 38.3463 | 37.5095 | 35.0684 | 32.6853 | 30.9116 | 29.6253 | 27.6495 | 25.6116 | 23.8337 | 43.2716 | 42.1589 | 40.8853 | 39.2074 | 36.9653 | 34.4337 | 32.0558 | 30.2853 | 29.0011 | 27.0316 | 25 | 23.2263
|  | EASTLEIGH NORTH PRIMARY | FB |  |  |  |  | 46.4537 | 45.8863 | 45.3663 | 44.7537 | 44.0242 | 43.1116 | 42.1926 | 41.4937 | 40.9779 | 39.1684 | 37.6579 | 36.3611 | 40.0253 | 39.8221 | 39.6389 | 39.4295 | 39.1926 | 38.9337 | 38.6811 | 38.4611 | 37.8705 | 35.7274 | 33.8863 | 32.2842 | 43.8747 | 43.1916 | 42.5663 | 41.8263 | 40.9411 | 39.8211 | 38.6926 | 37.8421 | 37.2316 | 35.0926 | 33.2568 | 31.6579
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY PRIMARY | MINIMUM HEADROOM | SZ 66357 99040 | NO | YES | 0 | 22.6192 | 22.4645 | 22.3171 | 22.075 | 21.8319 | 21.5077 | 21.1813 | 20.8382 | 20.495 | 19.4845 | 18.7108 | 18.0161 | 23.9403 | 23.8203 | 23.6992 | 23.5192 | 23.3171 | 23.0666 | 22.815 | 22.4403 | 21.9908 | 20.615 | 19.5308 | 18.5582 | 22.8708 | 22.7161 | 22.5677 | 22.3256 | 22.0813 | 21.7571 | 21.4308 | 21.0866 | 20.7435 | 19.7329 | 18.9582 | 18.2024
|  | EASTNEY PRIMARY | EE |  |  |  |  | 22.6192 | 22.4645 | 22.3171 | 22.1413 | 21.9235 | 21.714 | 21.4961 | 21.275 | 21.0571 | 20.6129 | 20.0635 | 19.5908 | 23.9403 | 23.8203 | 23.6992 | 23.5466 | 23.3508 | 23.1613 | 22.9708 | 22.7761 | 22.5856 | 22.2761 | 21.4677 | 20.7677 | 22.8708 | 22.7161 | 22.5677 | 22.3908 | 22.175 | 21.9645 | 21.7466 | 21.5256 | 21.3077 | 20.8613 | 20.3119 | 19.8392
|  | EASTNEY PRIMARY | HT |  |  |  |  | 22.6477 | 22.5013 | 22.3213 | 22.075 | 21.8319 | 21.5077 | 21.1813 | 20.8382 | 20.495 | 19.4845 | 18.7108 | 18.0161 | 23.9592 | 23.8477 | 23.7077 | 23.5192 | 23.3171 | 23.0666 | 22.815 | 22.4403 | 21.9908 | 20.615 | 19.5308 | 18.5582 | 22.8992 | 22.7529 | 22.5719 | 22.3256 | 22.0813 | 21.7571 | 21.4308 | 21.0866 | 20.7435 | 19.7329 | 18.9582 | 18.2024
|  | EASTNEY PRIMARY | HE |  |  |  |  | 22.694 | 22.5603 | 22.4308 | 22.2656 | 22.0508 | 21.8487 | 21.6529 | 21.4571 | 21.2624 | 21.1613 | 20.9119 | 20.6024 | 23.9824 | 23.8719 | 23.7571 | 23.6056 | 23.4045 | 23.215 | 23.0329 | 22.8477 | 22.6645 | 22.614 | 22.4687 | 22.234 | 22.9445 | 22.8119 | 22.6824 | 22.5171 | 22.3024 | 22.0992 | 21.9045 | 21.7077 | 21.514 | 21.4119 | 21.1624 | 20.8519
|  | EASTNEY PRIMARY | FB |  |  |  |  | 22.7803 | 22.6866 | 22.615 | 22.5382 | 22.455 | 22.3645 | 22.2835 | 22.2077 | 22.1277 | 21.8056 | 21.5287 | 21.215 | 24.0561 | 23.9835 | 23.9245 | 23.8624 | 23.7919 | 23.7182 | 23.6498 | 23.5866 | 23.5192 | 23.2571 | 23.0603 | 22.8645 | 23.0319 | 22.9371 | 22.8656 | 22.7898 | 22.7066 | 22.6161 | 22.535 | 22.4582 | 22.3782 | 22.0561 | 21.7792 | 21.4645
LALEHAM GSP | STAINES BSP | EGHAM PRIMARY | MINIMUM HEADROOM | TQ 01030 71404 | NO | YES | 0 | 34.0879 | 33.9037 | 62.3516 | 62.0779 | 61.7032 | 61.3463 | 61.0147 | 60.6726 | 60.3326 | 59.1811 | 57.6411 | 56.2642 | 29.9632 | 29.78 | 56.28 | 55.6674 | 54.5737 | 53.2547 | 51.9368 | 50.5884 | 49.2389 | 46.3147 | 44.52 | 42.9158 | 34.7168 | 34.5305 | 61.9284 | 61.6516 | 61.2758 | 60.3789 | 59.06 | 57.7095 | 56.3589 | 53.4295 | 51.6284 | 50.0179
|  | EGHAM PRIMARY | EE |  |  |  |  | 34.0879 | 33.9037 | 62.3516 | 62.0779 | 61.7032 | 61.3463 | 61.0147 | 60.6726 | 60.3326 | 60.0874 | 59.8558 | 59.6705 | 29.9632 | 29.78 | 56.28 | 55.9337 | 55.4358 | 54.8389 | 54.2253 | 53.6126 | 53.0168 | 51.5926 | 50.3021 | 49.1905 | 34.7168 | 34.5305 | 61.9284 | 61.6516 | 61.2758 | 60.9179 | 60.5821 | 60.2389 | 59.8989 | 58.6768 | 57.3695 | 56.2421
|  | EGHAM PRIMARY | HT |  |  |  |  | 34.1079 | 33.9426 | 62.3789 | 62.1042 | 61.7726 | 61.4105 | 61.0474 | 60.6905 | 60.3347 | 59.1811 | 57.6411 | 56.2642 | 29.9811 | 29.8168 | 56.3032 | 55.6674 | 54.5737 | 53.2547 | 51.9368 | 50.5884 | 49.2389 | 46.3147 | 44.52 | 42.9158 | 34.7389 | 34.5747 | 61.9589 | 61.6842 | 61.3516 | 60.3789 | 59.06 | 57.7095 | 56.3589 | 53.4295 | 51.6284 | 50.0179
|  | EGHAM PRIMARY | HE |  |  |  |  | 34.1258 | 33.9532 | 62.4095 | 62.1411 | 61.7737 | 61.4316 | 61.0968 | 60.7579 | 60.4253 | 60.4505 | 60.3905 | 60.3495 | 29.9979 | 29.8263 | 56.3326 | 56.0653 | 55.6979 | 55.3568 | 54.9505 | 54.4337 | 53.9337 | 53.1874 | 52.3295 | 51.5853 | 34.7579 | 34.5853 | 61.9905 | 61.7221 | 61.3537 | 61.0116 | 60.6758 | 60.3379 | 60.0042 | 60.0263 | 59.4442 | 58.6937
|  | EGHAM PRIMARY | FB |  |  |  |  | 34.2574 | 34.1689 | 62.7389 | 62.6495 | 62.5495 | 62.4495 | 62.3526 | 62.2621 | 62.1663 | 61.8105 | 61.6126 | 61.4853 | 30.1295 | 30.0411 | 56.6611 | 56.5716 | 56.4716 | 56.3716 | 56.2747 | 56.1842 | 56.0884 | 55.7326 | 55.0421 | 54.28 | 34.8905 | 34.8021 | 62.3221 | 62.2326 | 62.1326 | 62.0326 | 61.9358 | 61.8453 | 61.7495 | 61.3937 | 61.1958 | 61.0684
MANNINGTON GSP | BOURNEMOUTH BSP | ELECTRIC HOUSE PRIMARY | MINIMUM HEADROOM | SZ 08757 91379 | NO | YES | 0.063158 | 30.5274 | 30.44 | 30.2779 | 28.9105 | 28.0768 | 27.66 | 27.3968 | 27.0842 | 26.7684 | 24.5432 | 23.9084 | 23.3305 | 30.3863 | 30.3232 | 30.2337 | 30.0442 | 29.3116 | 28.8147 | 28.5116 | 28.1474 | 27.78 | 25.0484 | 24.2979 | 23.6158 | 28.8326 | 28.7758 | 28.7126 | 28.6263 | 28.5042 | 28.3937 | 28.2863 | 28.1779 | 27.9958 | 25.2221 | 24.4621 | 23.7705
|  | ELECTRIC HOUSE PRIMARY | EE |  |  |  |  | 30.5274 | 30.44 | 30.2926 | 29.0095 | 28.2358 | 27.9558 | 27.7842 | 27.6074 | 27.4358 | 25.5189 | 25.0221 | 24.5821 | 30.3863 | 30.3263 | 30.2474 | 30.0705 | 29.5084 | 29.1811 | 28.9884 | 28.7916 | 28.6011 | 26.2116 | 25.6105 | 25.0768 | 28.8326 | 28.7832 | 28.7316 | 28.6589 | 28.5547 | 28.4558 | 28.3611 | 28.2621 | 28.1621 | 26.4 | 25.7905 | 25.2495
|  | ELECTRIC HOUSE PRIMARY | HT |  |  |  |  | 30.5295 | 30.44 | 30.2779 | 28.9105 | 28.0768 | 27.66 | 27.3968 | 27.0842 | 26.7684 | 24.5432 | 23.9084 | 23.3305 | 30.3874 | 30.3274 | 30.2368 | 30.0484 | 29.3116 | 28.8147 | 28.5116 | 28.1474 | 27.78 | 25.0484 | 24.2979 | 23.6158 | 28.8326 | 28.7853 | 28.7232 | 28.6411 | 28.5411 | 28.4295 | 28.3147 | 28.2011 | 27.9958 | 25.2221 | 24.4621 | 23.7705
|  | ELECTRIC HOUSE PRIMARY | HE |  |  |  |  | 30.5368 | 30.4453 | 30.2905 | 29.0747 | 28.2947 | 28.0168 | 27.8905 | 27.76 | 27.6368 | 26.0821 | 25.7811 | 25.5126 | 30.3895 | 30.3232 | 30.2337 | 30.0442 | 29.5947 | 29.2737 | 29.1421 | 29.0063 | 28.8789 | 26.92 | 26.5505 | 26.22 | 28.8326 | 28.7758 | 28.7126 | 28.6263 | 28.5042 | 28.3937 | 28.2863 | 28.1779 | 28.0705 | 27.1211 | 26.7463 | 26.4105
|  | ELECTRIC HOUSE PRIMARY | FB |  |  |  |  | 30.5747 | 30.52 | 30.4474 | 30.2611 | 30.1674 | 30.1126 | 30.0716 | 30.0326 | 29.9916 | 28.8663 | 28.5505 | 28.2516 | 30.4242 | 30.3832 | 30.3411 | 30.2632 | 30.2095 | 30.1674 | 30.1284 | 30.0926 | 30.0547 | 29.86 | 29.7674 | 29.5905 | 28.8663 | 28.8316 | 28.8011 | 28.7663 | 28.7284 | 28.6905 | 28.6526 | 28.6179 | 28.5811 | 28.4442 | 28.3653 | 28.3137
FLEET-BRAMLEY GSP | WOKINGHAM BSP | ELMS ROAD PRIMARY | MINIMUM HEADROOM | SU 81057 68532 | NO | YES | 0.34737 | 29.2536 | 29.0578 | 28.8336 | 28.522 | 28.1378 | 27.6778 | 27.2167 | 26.5946 | 25.5251 | 23.3936 | 21.9536 | 20.1714 | 26.1018 | 25.7134 | 25.2587 | 24.4997 | 23.5671 | 22.3671 | 21.2334 | 20.0229 | 18.8187 | 16.4429 | 14.825 | 12.785 | 27.6979 | 27.4895 | 27.0295 | 26.3021 | 25.4084 | 24.2368 | 23.1189 | 21.9263 | 20.74 | 18.3779 | 16.7558 | 14.7084
|  | ELMS ROAD PRIMARY | EE |  |  |  |  | 29.2536 | 29.0578 | 28.8357 | 28.5378 | 28.1378 | 27.7483 | 27.3757 | 26.9714 | 26.5746 | 26.2451 | 25.443 | 24.2725 | 26.1018 | 25.7134 | 25.3145 | 24.8418 | 24.2924 | 23.5682 | 22.7503 | 21.9018 | 21.1239 | 19.8324 | 18.7945 | 17.4229 | 27.6979 | 27.4895 | 27.0853 | 26.6211 | 26.0832 | 25.3821 | 24.5947 | 23.7653 | 22.9968 | 21.7284 | 20.7063 | 19.3611
|  | ELMS ROAD PRIMARY | HT |  |  |  |  | 29.263 | 29.0778 | 28.8336 | 28.522 | 28.143 | 27.6778 | 27.2167 | 26.5946 | 25.5251 | 23.3936 | 21.9536 | 20.1714 | 26.1808 | 25.7839 | 25.2587 | 24.4997 | 23.5671 | 22.3671 | 21.2334 | 20.0229 | 18.8187 | 16.4429 | 14.825 | 12.785 | 27.7074 | 27.5221 | 27.0295 | 26.3021 | 25.4084 | 24.2368 | 23.1189 | 21.9263 | 20.74 | 18.3779 | 16.7558 | 14.7084
|  | ELMS ROAD PRIMARY | HE |  |  |  |  | 29.2957 | 29.1083 | 28.8914 | 28.5978 | 28.1978 | 27.822 | 27.4557 | 27.0841 | 26.7114 | 26.6893 | 26.5936 | 26.4883 | 26.3166 | 26.0745 | 25.7597 | 25.3692 | 24.8787 | 24.2429 | 23.5271 | 22.7766 | 22.0987 | 21.5492 | 20.9629 | 19.9787 | 27.74 | 27.5526 | 27.3358 | 27.0421 | 26.6421 | 26.0147 | 25.3232 | 24.5989 | 23.9432 | 23.4147 | 22.84 | 21.8768
|  | ELMS ROAD PRIMARY | FB |  |  |  |  | 29.442 | 29.3504 | 29.2683 | 29.1757 | 29.0725 | 28.9693 | 28.8693 | 28.7757 | 28.6757 | 28.303 | 28.062 | 27.8778 | 26.4682 | 26.3703 | 26.2197 | 26.0408 | 25.8492 | 25.5955 | 25.2987 | 24.9618 | 24.645 | 23.7092 | 22.9797 | 22.0913 | 27.8863 | 27.7947 | 27.7126 | 27.62 | 27.5168 | 27.3695 | 27.0705 | 26.7495 | 26.4474 | 25.5516 | 24.8442 | 23.9726
LOVEDEAN GSP | HAVANT BSP | EMSWORTH PRIMARY | MINIMUM HEADROOM | SU 74861 05807 | NO | YES | 0.84211 | 11.96 | 11.6379 | 11.2305 | 29.0384 | 28.1268 | 26.9205 | 25.59 | 24.2268 | 22.8995 | 18.3774 | 16.0805 | 14.6226 | 9.2063 | 8.8105 | 8.3168 | 25.2568 | 24.1011 | 22.5463 | 20.8168 | 19.04 | 17.4316 | 12.2663 | 9.6558 | 8.0158 | 10.1758 | 9.7989 | 9.3263 | 25.3832 | 24.2232 | 22.6632 | 20.9284 | 19.1442 | 17.5305 | 12.3463 | 9.7263 | 8.0811
|  | EMSWORTH PRIMARY | EE |  |  |  |  | 11.96 | 11.6937 | 11.2705 | 29.2447 | 28.5742 | 27.6405 | 26.5732 | 25.4974 | 24.5437 | 21.1605 | 19.3216 | 18.3153 | 9.2063 | 8.8937 | 8.3726 | 25.5389 | 24.7274 | 23.5432 | 22.1653 | 20.7789 | 19.56 | 15.4158 | 13.2958 | 12.1432 | 10.1758 | 9.8747 | 9.3779 | 25.6579 | 24.8526 | 23.6653 | 22.2821 | 20.8905 | 19.6684 | 15.5063 | 13.3789 | 12.2221
|  | EMSWORTH PRIMARY | HT |  |  |  |  | 12.0053 | 11.6379 | 11.2305 | 29.0384 | 28.1268 | 26.9205 | 25.59 | 24.2268 | 22.8995 | 18.3774 | 16.0805 | 14.6226 | 9.2663 | 8.8105 | 8.3168 | 25.2568 | 24.1011 | 22.5463 | 20.8168 | 19.04 | 17.4316 | 12.2663 | 9.6558 | 8.0158 | 10.2326 | 9.7989 | 9.3263 | 25.3832 | 24.2232 | 22.6632 | 20.9284 | 19.1442 | 17.5305 | 12.3463 | 9.7263 | 8.0811
|  | EMSWORTH PRIMARY | HE |  |  |  |  | 12.1326 | 11.9316 | 11.5705 | 29.5911 | 28.9563 | 28.0668 | 27.0489 | 26.0237 | 25.1226 | 22.3268 | 20.8005 | 20.0574 | 9.4316 | 9.2074 | 8.7674 | 25.9947 | 25.2305 | 24.1011 | 22.7916 | 21.4737 | 20.3263 | 16.7232 | 14.9453 | 14.0811 | 10.3884 | 10.1695 | 9.7495 | 26.0874 | 25.3547 | 24.2242 | 22.9105 | 21.5884 | 20.4368 | 16.8189 | 15.0326 | 14.1653
|  | EMSWORTH PRIMARY | FB |  |  |  |  | 12.3 | 12.1516 | 12.0253 | 30.1911 | 29.9553 | 29.5932 | 29.1311 | 28.6458 | 28.1942 | 26.2405 | 25.1679 | 24.6005 | 9.6221 | 9.4432 | 9.2926 | 26.6642 | 26.3674 | 25.8937 | 25.2811 | 24.6337 | 24.0347 | 21.4274 | 19.9947 | 19.2442 | 10.5737 | 10.4021 | 10.2579 | 26.74 | 26.4579 | 26.0116 | 25.4053 | 24.7568 | 24.1547 | 21.5379 | 20.1 | 19.3463
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | ENFORD PRIMARY | MINIMUM HEADROOM | SU 13728 51712 | NO | YES | 0 | 8.52 | 8.4874 | 8.4505 | 8.4011 | 8.3358 | 8.2716 | 8.1968 | 8.0895 | 7.9779 | 7.6821 | 7.4526 | 7.2484 | 7.9537 | 7.9211 | 7.8842 | 7.8347 | 7.7695 | 7.7053 | 7.6389 | 7.5737 | 7.5084 | 7.3589 | 7.1926 | 6.9558 | 8.4484 | 8.3811 | 8.3137 | 8.2379 | 8.14 | 8.0305 | 7.9179 | 7.7979 | 7.6737 | 7.3368 | 7.0684 | 6.8284
|  | ENFORD PRIMARY | EE |  |  |  |  | 8.52 | 8.4874 | 8.4505 | 8.4021 | 8.3358 | 8.2716 | 8.2137 | 8.1526 | 8.0937 | 7.9463 | 7.7926 | 7.6705 | 7.9537 | 7.9211 | 7.8842 | 7.8358 | 7.7695 | 7.7053 | 7.6474 | 7.5863 | 7.5274 | 7.4842 | 7.4442 | 7.4126 | 8.4484 | 8.3811 | 8.3137 | 8.2379 | 8.1495 | 8.0642 | 7.9821 | 7.8979 | 7.8168 | 7.64 | 7.4537 | 7.3053
|  | ENFORD PRIMARY | HT |  |  |  |  | 8.5221 | 8.4926 | 8.4526 | 8.4011 | 8.3389 | 8.2716 | 8.1968 | 8.0895 | 7.9779 | 7.6821 | 7.4526 | 7.2484 | 7.9558 | 7.9263 | 7.8863 | 7.8347 | 7.7726 | 7.7053 | 7.6389 | 7.5737 | 7.5084 | 7.3589 | 7.1926 | 6.9558 | 8.4632 | 8.4042 | 8.3305 | 8.2421 | 8.14 | 8.0305 | 7.9179 | 7.7979 | 7.6737 | 7.3368 | 7.0684 | 6.8284
|  | ENFORD PRIMARY | HE |  |  |  |  | 8.5295 | 8.4989 | 8.4632 | 8.4168 | 8.3495 | 8.2884 | 8.2295 | 8.1695 | 8.1105 | 8.1147 | 8.0579 | 7.9863 | 7.9632 | 7.9326 | 7.8968 | 7.8505 | 7.7832 | 7.7221 | 7.6632 | 7.6032 | 7.5442 | 7.5484 | 7.5358 | 7.5295 | 8.4979 | 8.4505 | 8.3979 | 8.3368 | 8.2558 | 8.1821 | 8.1105 | 8.0379 | 7.9674 | 7.8926 | 7.7695 | 7.6789
|  | ENFORD PRIMARY | FB |  |  |  |  | 8.5516 | 8.5368 | 8.5232 | 8.5084 | 8.4916 | 8.4747 | 8.4579 | 8.4432 | 8.4263 | 8.3674 | 8.3116 | 8.2211 | 7.9853 | 7.9705 | 7.9568 | 7.9421 | 7.9253 | 7.9084 | 7.8916 | 7.8768 | 7.86 | 7.8011 | 7.7674 | 7.7463 | 8.5379 | 8.5 | 8.4716 | 8.4421 | 8.4105 | 8.3789 | 8.3474 | 8.3189 | 8.2884 | 8.1558 | 8.0284 | 7.9179
COWLEY GSP | YARNTON BSP | EYNSHAM PRIMARY | MINIMUM HEADROOM | SP 42236 10266 | NO | YES | 0.21053 | 27.2824 | 27.1813 | 25.5939 | 25.075 | 24.3003 | 22.9961 | 21.4118 | 20.0761 | 18.3645 | 11.2518 | 9.6339 | 9.1561 | 26.4518 | 26.135 | 22.8961 | 22.2087 | 21.1592 | 19.6718 | 18.0045 | 16.6003 | 14.7918 | 6.4792 | 4.5824 | 4.0245 | 23.0308 | 22.7276 | 19.6729 | 19.0171 | 18.0192 | 16.6076 | 15.0276 | 13.6939 | 11.9866 | 4.8908 | 3.0992 | 2.5613
|  | EYNSHAM PRIMARY | EE |  |  |  |  | 27.2824 | 27.1813 | 25.8455 | 25.4529 | 24.7718 | 23.795 | 22.4392 | 21.3076 | 18.3645 | 14.3213 | 12.4971 | 11.8466 | 26.4518 | 26.1392 | 23.2634 | 22.7571 | 21.8529 | 20.5718 | 19.0918 | 17.9024 | 14.7918 | 10.1318 | 8.0066 | 7.2582 | 23.0308 | 22.7308 | 20.0192 | 19.5339 | 18.6708 | 17.4539 | 16.0518 | 14.9234 | 11.9866 | 7.9518 | 6.1308 | 5.4813
|  | EYNSHAM PRIMARY | HT |  |  |  |  | 27.2897 | 27.1939 | 25.5939 | 25.075 | 24.3003 | 22.9961 | 21.4118 | 20.0761 | 18.7645 | 14.1971 | 11.8971 | 10.8876 | 26.455 | 26.135 | 22.8961 | 22.2087 | 21.1592 | 19.6718 | 18.0045 | 16.6003 | 15.2213 | 10.0603 | 7.4045 | 6.2624 | 23.0339 | 22.7276 | 19.6729 | 19.0171 | 18.0192 | 16.6076 | 15.0276 | 13.6939 | 12.3855 | 7.8266 | 5.5308 | 4.5255
|  | EYNSHAM PRIMARY | HE |  |  |  |  | 27.3118 | 27.2203 | 26.0318 | 25.6666 | 25.0097 | 24.1024 | 22.8182 | 21.7297 | 18.8276 | 11.2518 | 9.6339 | 9.1561 | 26.595 | 26.3392 | 23.515 | 23.0445 | 22.1729 | 20.9255 | 19.4897 | 18.3455 | 15.2782 | 6.4792 | 4.5824 | 4.0245 | 23.1666 | 22.9213 | 20.2582 | 19.8076 | 18.9761 | 17.7918 | 16.4308 | 15.3445 | 12.4487 | 4.8908 | 3.0992 | 2.5613
|  | EYNSHAM PRIMARY | FB |  |  |  |  | 27.3813 | 27.3361 | 27.295 | 27.2497 | 27.1992 | 27.1476 | 26.8139 | 26.3992 | 25.9603 | 24.2024 | 20.435 | 20.0066 | 26.7887 | 26.6255 | 26.4508 | 26.2466 | 25.9192 | 25.3666 | 24.6729 | 24.0855 | 23.4645 | 20.9961 | 16.9445 | 16.4939 | 23.3529 | 23.1971 | 23.0308 | 22.8361 | 22.5255 | 22.0024 | 21.3466 | 20.7918 | 20.2045 | 17.8708 | 14.0539 | 13.6255
MINETY GSP | CIRENCESTER BSP | FAIRFORD PRIMARY | MINIMUM HEADROOM | SP 14418 00559 | NO | YES | 0.014737 | 18.0968 | 18.0074 | 17.9011 | 17.7526 | 17.5442 | 17.0779 | 16.6095 | 16.1379 | 15.6684 | 14.2895 | 13.4189 | 12.5032 | 15.8442 | 15.6 | 15.3347 | 15.02 | 14.5874 | 14.0811 | 13.5716 | 13.0589 | 12.5474 | 11.0295 | 10.0705 | 9.0537 | 17.0547 | 16.8032 | 16.5295 | 16.2063 | 15.7611 | 15.2389 | 14.7137 | 14.1842 | 13.6558 | 12.0842 | 11.0884 | 10.0326
|  | FAIRFORD PRIMARY | EE |  |  |  |  | 18.0968 | 18.0074 | 17.9053 | 17.7779 | 17.6053 | 17.44 | 17.2242 | 16.9495 | 16.6821 | 15.8695 | 15.2726 | 14.6263 | 15.8442 | 15.6 | 15.3347 | 15.1284 | 14.8547 | 14.5642 | 14.2621 | 13.9705 | 13.6874 | 12.78 | 12.1137 | 11.3853 | 17.0547 | 16.8032 | 16.5295 | 16.3189 | 16.04 | 15.7432 | 15.4337 | 15.1358 | 14.8463 | 13.9011 | 13.2074 | 12.4474
|  | FAIRFORD PRIMARY | HT |  |  |  |  | 18.1074 | 18.0179 | 17.9011 | 17.7526 | 17.5442 | 17.0779 | 16.6095 | 16.1379 | 15.6684 | 14.2895 | 13.4189 | 12.5032 | 15.8905 | 15.6442 | 15.3442 | 15.02 | 14.5874 | 14.0811 | 13.5716 | 13.0589 | 12.5474 | 11.0295 | 10.0705 | 9.0537 | 17.1021 | 16.8495 | 16.5389 | 16.2063 | 15.7611 | 15.2389 | 14.7137 | 14.1842 | 13.6558 | 12.0842 | 11.0884 | 10.0326
|  | FAIRFORD PRIMARY | HE |  |  |  |  | 18.1421 | 18.0705 | 17.98 | 17.86 | 17.6947 | 17.5421 | 17.3905 | 17.2358 | 17.0842 | 16.6716 | 16.2642 | 15.7758 | 16 | 15.82 | 15.6053 | 15.4379 | 15.2189 | 14.9653 | 14.7137 | 14.4737 | 14.2432 | 13.6653 | 13.2053 | 12.6495 | 17.2168 | 17.0316 | 16.8105 | 16.64 | 16.4189 | 16.1589 | 15.9032 | 15.6589 | 15.4242 | 14.8189 | 14.3389 | 13.7568
|  | FAIRFORD PRIMARY | FB |  |  |  |  | 18.1937 | 18.1526 | 18.1158 | 18.0747 | 18.0284 | 17.9811 | 17.9368 | 17.8947 | 17.8495 | 17.6853 | 17.3453 | 16.9368 | 16.1463 | 16.0137 | 15.9032 | 15.8189 | 15.7316 | 15.6232 | 15.5158 | 15.4158 | 15.3137 | 14.8968 | 14.3558 | 13.8958 | 17.3674 | 17.2305 | 17.1158 | 17.0295 | 16.94 | 16.8284 | 16.7179 | 16.6147 | 16.5105 | 16.08 | 15.5168 | 15.0368
MINETY GSP | STRATTON (RESERVE) BSP | FARINGDON PRIMARY | MINIMUM HEADROOM | SU 28819 94924 | NO | YES | 0 | 15.76 | 15.4105 | 41.3968 | 41.0684 | 40.6674 | 40.2526 | 39.8347 | 39.3705 | 38.8937 | 29.2526 | 21.4042 | 10.2579 | 12.4537 | 12.0516 | 35.8032 | 35.4432 | 35.0053 | 34.5547 | 34.1 | 33.5884 | 33.0611 | 22.2074 | 13.3979 | 0.33474 | 14.2579 | 13.8463 | 38.7905 | 38.4242 | 37.9789 | 37.52 | 37.0579 | 36.5368 | 35.9989 | 24.7168 | 15.5316 | 2.4653
|  | FARINGDON PRIMARY | EE |  |  |  |  | 15.78 | 15.4347 | 41.4453 | 41.1821 | 40.8316 | 40.5326 | 40.2305 | 39.9263 | 39.6274 | 29.2526 | 21.4042 | 10.2579 | 12.4821 | 12.0863 | 35.8621 | 35.5779 | 35.2011 | 34.8842 | 34.5611 | 34.2358 | 33.9168 | 22.2074 | 13.3979 | 0.33474 | 14.2884 | 13.8821 | 38.8516 | 38.5621 | 38.18 | 37.8611 | 37.5326 | 37.2042 | 36.8811 | 24.7168 | 15.5316 | 2.4653
|  | FARINGDON PRIMARY | HT |  |  |  |  | 15.76 | 15.4105 | 41.3968 | 41.0684 | 40.6674 | 40.2526 | 39.8347 | 39.3705 | 38.8937 | 37.64 | 36.5579 | 25.1042 | 12.4537 | 12.0516 | 35.8032 | 35.4432 | 35.0053 | 34.5547 | 34.1 | 33.5884 | 33.0611 | 31.6579 | 30.48 | 17.7137 | 14.2579 | 13.8463 | 38.7905 | 38.4242 | 37.9789 | 37.52 | 37.0579 | 36.5368 | 35.9989 | 34.5674 | 33.36 | 20.0568
|  | FARINGDON PRIMARY | HE |  |  |  |  | 15.9568 | 15.6789 | 41.7411 | 41.5253 | 41.2484 | 40.9421 | 40.6884 | 40.4326 | 40.1821 | 30.2305 | 22.6316 | 11.7021 | 12.6853 | 12.3674 | 36.2042 | 35.9758 | 35.6884 | 35.36 | 35.0947 | 34.8284 | 34.5684 | 23.2684 | 14.7705 | 1.9463 | 14.4968 | 14.1705 | 39.2032 | 38.9716 | 38.6821 | 38.3495 | 38.0811 | 37.8137 | 37.5505 | 25.8168 | 16.9053 | 4.0768
|  | FARINGDON PRIMARY | FB |  |  |  |  | 16.0684 | 15.9716 | 42.1463 | 42.04 | 41.9116 | 41.7989 | 41.6863 | 41.5821 | 41.4726 | 39.3884 | 34.7937 | 25.2611 | 12.9116 | 12.7011 | 36.66 | 36.5421 | 36.4 | 36.2758 | 36.1526 | 36.0379 | 35.9179 | 33.4232 | 28.2832 | 17.6368 | 14.6221 | 14.5126 | 39.6684 | 39.5484 | 39.4032 | 39.2768 | 39.1516 | 39.0347 | 38.9126 | 36.3358 | 31.0147 | 19.8684
LOVEDEAN GSP | PORTSMOUTH BSP | FARLINGTON PRIMARY | MINIMUM HEADROOM | SU 67400 04843 | NO | YES | 1.0516 | 18.5432 | 18.4326 | 18.3316 | 18.1695 | 18.0084 | 17.7979 | 17.5884 | 17.3653 | 17.14 | 16.4737 | 15.9653 | 15.52 | 20.2368 | 20.1116 | 20 | 19.8158 | 19.6389 | 19.4032 | 19.1674 | 18.9126 | 18.6568 | 17.8811 | 17.28 | 16.7537 | 20.3389 | 20.2158 | 20.1053 | 19.9242 | 19.7505 | 19.5168 | 19.2853 | 19.0347 | 18.7832 | 18.0221 | 17.4326 | 16.9179
|  | FARLINGTON PRIMARY | EE |  |  |  |  | 18.5432 | 18.4326 | 18.3316 | 18.2126 | 18.0705 | 17.9347 | 17.7905 | 17.6421 | 17.5 | 17.1916 | 16.8263 | 16.5189 | 20.2368 | 20.1116 | 20 | 19.8705 | 19.72 | 19.5758 | 19.4179 | 19.2579 | 19.1042 | 18.7337 | 18.2895 | 17.9137 | 20.3389 | 20.2158 | 20.1053 | 19.9779 | 19.8284 | 19.6853 | 19.5295 | 19.3705 | 19.2168 | 18.8558 | 18.4221 | 18.0558
|  | FARLINGTON PRIMARY | HT |  |  |  |  | 18.5611 | 18.4558 | 18.3337 | 18.1695 | 18.0084 | 17.7979 | 17.5884 | 17.3653 | 17.14 | 16.4737 | 15.9653 | 15.52 | 20.2589 | 20.1389 | 20.0021 | 19.8158 | 19.6389 | 19.4032 | 19.1674 | 18.9126 | 18.6568 | 17.8811 | 17.28 | 16.7537 | 20.3611 | 20.2421 | 20.1074 | 19.9242 | 19.7505 | 19.5168 | 19.2853 | 19.0347 | 18.7832 | 18.0221 | 17.4326 | 16.9179
|  | FARLINGTON PRIMARY | HE |  |  |  |  | 18.6084 | 18.5253 | 18.4463 | 18.3463 | 18.2168 | 18.0979 | 17.9821 | 17.8663 | 17.7516 | 17.6821 | 17.5168 | 17.3137 | 20.3158 | 20.2242 | 20.1389 | 20.0337 | 19.8989 | 19.7737 | 19.6537 | 19.5316 | 19.4126 | 19.3232 | 19.1179 | 18.8632 | 20.4158 | 20.3263 | 20.2421 | 20.1368 | 20.0021 | 19.8789 | 19.7589 | 19.6379 | 19.52 | 19.4326 | 19.2326 | 18.9853
|  | FARLINGTON PRIMARY | FB |  |  |  |  | 18.6695 | 18.6105 | 18.5684 | 18.5221 | 18.4747 | 18.4211 | 18.3747 | 18.3284 | 18.2821 | 18.0905 | 17.9126 | 17.7053 | 20.3832 | 20.3158 | 20.2684 | 20.2168 | 20.1632 | 20.1032 | 20.0516 | 20 | 19.9484 | 19.7326 | 19.5232 | 19.2695 | 20.4821 | 20.4168 | 20.3695 | 20.3189 | 20.2663 | 20.2063 | 20.1568 | 20.1053 | 20.0537 | 19.8421 | 19.6368 | 19.3884
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FARNBOROUGH PRIMARY | MINIMUM HEADROOM | SU 88404 53930 | NO | YES | 0.26421 | 27.1047 | 26.5679 | 26.05 | 25.4395 | 24.6805 | 23.5111 | 22.3195 | 21.1121 | 19.91 | 16.5374 | 15.0205 | 13.8911 | 28.1968 | 27.5221 | 26.8853 | 26.1537 | 25.2421 | 23.7674 | 22.2611 | 20.7274 | 19.2011 | 14.8305 | 12.9105 | 11.5137 | 30.3421 | 30.1421 | 29.7063 | 28.9716 | 28.0537 | 26.5663 | 25.0463 | 23.4989 | 21.96 | 17.5495 | 15.6316 | 14.2368
|  | FARNBOROUGH PRIMARY | EE |  |  |  |  | 27.1047 | 26.5679 | 26.1142 | 25.6721 | 25.1584 | 24.4311 | 23.6974 | 22.9616 | 22.2353 | 19.9932 | 18.8837 | 18.1605 | 28.1968 | 27.5221 | 26.9768 | 26.4789 | 25.9211 | 25.06 | 24.18 | 23.3 | 22.4305 | 19.3853 | 17.9189 | 16.9768 | 30.3421 | 30.1421 | 29.8 | 29.3 | 28.7411 | 27.8737 | 26.9874 | 26.1021 | 25.2263 | 22.1474 | 20.6674 | 19.7158
|  | FARNBOROUGH PRIMARY | HT |  |  |  |  | 27.1574 | 26.6047 | 26.05 | 25.4395 | 24.6805 | 23.5111 | 22.3195 | 21.1121 | 19.91 | 16.5374 | 15.0205 | 13.8911 | 28.2653 | 27.5653 | 26.8853 | 26.1537 | 25.2421 | 23.7674 | 22.2611 | 20.7274 | 19.2011 | 14.8305 | 12.9105 | 11.5137 | 30.3558 | 30.1663 | 29.7063 | 28.9716 | 28.0537 | 26.5663 | 25.0463 | 23.4989 | 21.96 | 17.5495 | 15.6316 | 14.2368
|  | FARNBOROUGH PRIMARY | HE |  |  |  |  | 27.3279 | 26.8689 | 26.4858 | 26.0974 | 25.6174 | 24.9384 | 24.2732 | 23.6058 | 22.9479 | 21.3037 | 20.5679 | 20.1637 | 28.4916 | 27.9253 | 27.4747 | 27.0516 | 26.5432 | 25.7453 | 24.9632 | 24.1789 | 23.4053 | 21.0863 | 20.0758 | 19.5232 | 30.3895 | 30.1968 | 29.9758 | 29.6726 | 29.2621 | 28.5663 | 27.7789 | 26.9905 | 26.2126 | 23.8653 | 22.8442 | 22.2853
|  | FARNBOROUGH PRIMARY | FB |  |  |  |  | 27.6226 | 27.3563 | 27.1689 | 27.0016 | 26.8258 | 26.4995 | 26.2205 | 25.9395 | 25.6416 | 24.17 | 23.3932 | 22.8742 | 28.8484 | 28.5116 | 28.2821 | 28.0863 | 27.8821 | 27.4674 | 27.1158 | 26.76 | 26.3821 | 24.4663 | 23.4579 | 22.7821 | 30.5347 | 30.4389 | 30.3547 | 30.2589 | 30.1516 | 30.0432 | 29.94 | 29.5821 | 29.2011 | 27.2663 | 26.2484 | 25.5663
FLEET-BRAMLEY GSP | PYESTOCK BSP | FARNBORO AIRFIELD PRIMARY | MINIMUM HEADROOM | SU 85838 54449 | NO | YES | 0 | 41.1158 | 41.1021 | 41.0863 | 41.0642 | 41.0368 | 41.0084 | 40.9811 | 40.9547 | 40.9263 | 40.8621 | 40.8221 | 40.7147 | 38.5074 | 38.4937 | 38.4779 | 38.4558 | 38.4284 | 38.4 | 38.3726 | 38.3463 | 38.2411 | 37.9863 | 37.7989 | 37.6221 | 39.8516 | 39.8379 | 39.8221 | 39.8 | 39.7726 | 39.7442 | 39.7021 | 39.5926 | 39.4821 | 39.2295 | 39.0421 | 38.8663
|  | FARNBORO AIRFIELD PRIMARY | EE |  |  |  |  | 41.1158 | 41.1021 | 41.0863 | 41.0642 | 41.0368 | 41.0084 | 40.9811 | 40.9547 | 40.9263 | 40.9074 | 40.8895 | 40.8747 | 38.5074 | 38.4937 | 38.4779 | 38.4558 | 38.4284 | 38.4 | 38.3726 | 38.3463 | 38.3179 | 38.2958 | 38.1442 | 38.0095 | 39.8516 | 39.8379 | 39.8221 | 39.8 | 39.7726 | 39.7442 | 39.7168 | 39.6905 | 39.6621 | 39.5358 | 39.3853 | 39.2516
|  | FARNBORO AIRFIELD PRIMARY | HT |  |  |  |  | 41.1168 | 41.1032 | 41.0874 | 41.0653 | 41.04 | 41.0116 | 40.9832 | 40.9547 | 40.9274 | 40.8621 | 40.8221 | 40.7147 | 38.5084 | 38.4947 | 38.4789 | 38.4568 | 38.4316 | 38.4032 | 38.3747 | 38.3463 | 38.2411 | 37.9863 | 37.7989 | 37.6221 | 39.8526 | 39.8389 | 39.8232 | 39.8011 | 39.7758 | 39.7474 | 39.7021 | 39.5926 | 39.4821 | 39.2295 | 39.0421 | 38.8663
|  | FARNBORO AIRFIELD PRIMARY | HE |  |  |  |  | 41.1179 | 41.1042 | 41.0895 | 41.0663 | 41.0379 | 41.0105 | 40.9832 | 40.9558 | 40.9284 | 40.9284 | 40.9232 | 40.92 | 38.5095 | 38.4958 | 38.4811 | 38.4579 | 38.4295 | 38.4021 | 38.3747 | 38.3474 | 38.32 | 38.32 | 38.3147 | 38.3116 | 39.8537 | 39.84 | 39.8253 | 39.8021 | 39.7737 | 39.7463 | 39.7189 | 39.6916 | 39.6642 | 39.6642 | 39.6589 | 39.5968
|  | FARNBORO AIRFIELD PRIMARY | FB |  |  |  |  | 41.1274 | 41.1211 | 41.1147 | 41.1074 | 41.1 | 41.0916 | 41.0842 | 41.0768 | 41.0695 | 41.0411 | 41.0253 | 41.0158 | 38.5189 | 38.5126 | 38.5063 | 38.4989 | 38.4916 | 38.4832 | 38.4758 | 38.4684 | 38.4611 | 38.4326 | 38.4168 | 38.4074 | 39.8632 | 39.8568 | 39.8505 | 39.8432 | 39.8358 | 39.8274 | 39.82 | 39.8126 | 39.8053 | 39.7768 | 39.7611 | 39.6958
FLEET-BRAMLEY GSP | ALDERSHOT BSP | FARNHAM PRIMARY | MINIMUM HEADROOM | SU 84517 47217 | NO | YES | 0 | 31.2926 | 31.1021 | 30.8737 | 30.5663 | 30.1274 | 29.1558 | 28.1979 | 27.1737 | 26.24 | 24.2768 | 23.0937 | 22.04 | 25.7211 | 25.3768 | 24.9253 | 24.3453 | 23.6695 | 22.9537 | 22.2568 | 21.5547 | 20.9232 | 18.8516 | 17.6011 | 16.4853 | 25.2095 | 24.7832 | 24.2116 | 23.4853 | 22.6432 | 21.7589 | 20.8989 | 20.0284 | 19.26 | 17.6358 | 16.6526 | 15.7789
|  | FARNHAM PRIMARY | EE |  |  |  |  | 31.2926 | 31.1021 | 30.8884 | 30.6063 | 30.2442 | 29.8947 | 29.4032 | 28.8421 | 28.4126 | 27.5905 | 26.7989 | 26.1042 | 25.7211 | 25.3768 | 24.9884 | 24.5189 | 23.9674 | 23.4547 | 22.9884 | 22.5305 | 22.1547 | 21.5811 | 21.0695 | 20.64 | 25.2095 | 24.7832 | 24.3011 | 23.7305 | 23.0779 | 22.4768 | 21.9347 | 21.4084 | 20.9968 | 20.2589 | 19.6011 | 19.0432
|  | FARNHAM PRIMARY | HT |  |  |  |  | 31.3021 | 31.1158 | 30.8737 | 30.5663 | 30.1274 | 29.1558 | 28.1979 | 27.1737 | 26.24 | 24.2768 | 23.0937 | 22.04 | 25.7484 | 25.3842 | 24.9253 | 24.3453 | 23.6695 | 22.9537 | 22.2568 | 21.5547 | 20.9232 | 18.8516 | 17.6011 | 16.4853 | 25.2463 | 24.7863 | 24.2116 | 23.4853 | 22.6432 | 21.7589 | 20.8989 | 20.0284 | 19.26 | 17.6358 | 16.6526 | 15.7789
|  | FARNHAM PRIMARY | HE |  |  |  |  | 31.3421 | 31.1663 | 30.9621 | 30.6884 | 30.3295 | 29.9958 | 29.6737 | 29.3537 | 29.0263 | 28.7253 | 28.3032 | 27.9516 | 25.8411 | 25.54 | 25.1884 | 24.7474 | 24.2137 | 23.7305 | 23.3011 | 22.8853 | 22.5474 | 22.3737 | 22.1032 | 21.88 | 25.3684 | 25 | 24.5684 | 24.0379 | 23.4095 | 22.8463 | 22.3589 | 21.8926 | 21.5358 | 21.2779 | 20.9074 | 20.6
|  | FARNHAM PRIMARY | FB |  |  |  |  | 31.4779 | 31.3863 | 31.3053 | 31.2137 | 31.1137 | 31.0137 | 30.9179 | 30.8305 | 30.7421 | 30.4168 | 30.2168 | 30.0768 | 26.06 | 25.8905 | 25.7326 | 25.5568 | 25.3726 | 25.1895 | 25.0274 | 24.8758 | 24.7579 | 24.2863 | 23.9105 | 23.6021 | 25.6316 | 25.4211 | 25.2211 | 25 | 24.7705 | 24.5421 | 24.3442 | 24.16 | 24.0253 | 23.4747 | 23.0042 | 22.6063
IVER 132KV GSP | SLOUGH BSP | FARNHAM ROYAL PRIMARY | MINIMUM HEADROOM | SU 95597 82844 | NO | NO | 0 | 50.1389 | 49.7316 | 49.2768 | 48.6726 | 47.8916 | 47.1032 | 46.2863 | 44.8968 | 43.4179 | 39.7653 | 33.9684 | 31.4516 | 49.0084 | 48.4389 | 47.6347 | 46.7179 | 45.5274 | 44.2074 | 42.5337 | 40.9168 | 39.3095 | 35.3368 | 28.7116 | 25.9284 | 47.6074 | 46.7947 | 46.0179 | 45.1274 | 43.9716 | 42.6916 | 41.0958 | 39.5442 | 37.9832 | 34.0179 | 27.4095 | 24.6305
|  | FARNHAM ROYAL PRIMARY | EE |  |  |  |  | 50.1389 | 49.7316 | 49.2768 | 48.68 | 47.8916 | 47.1179 | 46.3705 | 45.6242 | 44.9221 | 43.0484 | 39.6126 | 37.9747 | 49.0084 | 48.4389 | 47.6347 | 46.7179 | 45.6579 | 44.6263 | 43.2853 | 42.1989 | 41.1979 | 38.9474 | 34.9821 | 33.1189 | 47.6074 | 46.7947 | 46.0179 | 45.1274 | 44.0895 | 43.0789 | 41.7853 | 40.7284 | 39.7589 | 37.6211 | 33.6663 | 31.8074
|  | FARNHAM ROYAL PRIMARY | HT |  |  |  |  | 50.1684 | 49.7884 | 49.2968 | 48.6726 | 47.9232 | 47.1032 | 46.2863 | 44.8968 | 43.4179 | 39.7653 | 33.9684 | 31.4516 | 49.0347 | 48.6642 | 47.8116 | 46.7516 | 45.5274 | 44.2074 | 42.5337 | 40.9168 | 39.3095 | 35.3368 | 28.7116 | 25.9284 | 47.7589 | 47.0158 | 46.1832 | 45.1579 | 43.9716 | 42.6916 | 41.0958 | 39.5442 | 37.9832 | 34.0179 | 27.4095 | 24.6305
|  | FARNHAM ROYAL PRIMARY | HE |  |  |  |  | 50.2411 | 49.86 | 49.4326 | 48.8579 | 48.08 | 47.3453 | 46.6053 | 45.8747 | 45.1853 | 45.1453 | 43.2211 | 42.2716 | 49.0989 | 48.7253 | 48.3042 | 47.7337 | 46.8158 | 45.9105 | 44.7421 | 43.8326 | 43 | 42.0895 | 39.0158 | 37.9084 | 48.1 | 47.4758 | 46.8674 | 46.1158 | 45.1684 | 44.2779 | 43.1442 | 42.2495 | 41.4358 | 40.5895 | 37.6842 | 36.5811
|  | FARNHAM ROYAL PRIMARY | FB |  |  |  |  | 50.5453 | 50.3474 | 50.1737 | 49.9821 | 49.7705 | 49.5568 | 49.34 | 49.1453 | 48.9379 | 48.1632 | 47.6863 | 46.7137 | 49.3968 | 49.2074 | 49.0379 | 48.8505 | 48.6432 | 48.4211 | 47.9105 | 47.5421 | 47.1632 | 45.5474 | 44.0063 | 42.6979 | 48.5821 | 48.1811 | 47.8526 | 47.5032 | 47.1316 | 46.7632 | 46.2768 | 45.9221 | 45.5579 | 44.0105 | 42.5568 | 41.3284
LALEHAM GSP | EAST BEDFONT BSP | FELTHAM PRIMARY | MINIMUM HEADROOM | TQ 10628 72811 | NO | YES | 0 | 27.3263 | 27.0758 | 26.7811 | 26.3958 | 25.5621 | 24.6432 | 23.5905 | 22.4116 | 21.2789 | 18.5453 | 17.5947 | 16.8474 | 27.2853 | 26.9621 | 26.5874 | 26.1095 | 25.0189 | 23.8168 | 22.4305 | 20.8642 | 19.3642 | 15.7495 | 14.5463 | 13.6116 | 24.64 | 24.3379 | 23.9874 | 23.5663 | 22.9411 | 22.2516 | 21.4705 | 20.6032 | 19.7695 | 16.4863 | 15.2789 | 14.3411
|  | FELTHAM PRIMARY | EE |  |  |  |  | 27.3316 | 27.1 | 26.8211 | 26.4947 | 25.9074 | 25.2358 | 24.4905 | 23.6011 | 22.7484 | 20.4832 | 19.8547 | 19.4063 | 27.2926 | 26.9968 | 26.6379 | 26.2263 | 25.4905 | 24.6253 | 23.6526 | 22.4811 | 21.3611 | 18.2558 | 17.4263 | 16.8379 | 24.6463 | 24.3695 | 24.0347 | 23.6484 | 23.1842 | 22.6695 | 22.1084 | 21.4474 | 20.8116 | 19.0011 | 18.1684 | 17.5779
|  | FELTHAM PRIMARY | HT |  |  |  |  | 27.3263 | 27.0758 | 26.7811 | 26.3958 | 25.5621 | 24.6432 | 23.5905 | 22.4116 | 21.2789 | 18.5453 | 17.5947 | 16.8474 | 27.2853 | 26.9621 | 26.5874 | 26.1095 | 25.0189 | 23.8168 | 22.4305 | 20.8642 | 19.3642 | 15.7495 | 14.5463 | 13.6116 | 24.64 | 24.3379 | 23.9874 | 23.5663 | 22.9411 | 22.2516 | 21.4705 | 20.6032 | 19.7695 | 16.4863 | 15.2789 | 14.3411
|  | FELTHAM PRIMARY | HE |  |  |  |  | 27.3842 | 27.1705 | 26.9053 | 26.5884 | 26.0926 | 25.4358 | 24.7147 | 23.8463 | 23.0168 | 21.0684 | 20.6221 | 20.3316 | 27.3642 | 27.0937 | 26.7558 | 26.3589 | 25.7474 | 24.9021 | 23.9642 | 22.8242 | 21.7358 | 19.02 | 18.4116 | 18.0158 | 24.7116 | 24.4579 | 24.1421 | 23.7684 | 23.3116 | 22.8084 | 22.2611 | 21.6137 | 20.9926 | 19.6663 | 19.1568 | 18.7589
|  | FELTHAM PRIMARY | FB |  |  |  |  | 27.5053 | 27.3842 | 27.2674 | 27.1305 | 26.9926 | 26.8389 | 26.6579 | 26.3305 | 25.9126 | 24.2611 | 23.8158 | 23.5084 | 27.5095 | 27.3558 | 27.2063 | 27.0295 | 26.8526 | 26.6547 | 26.4168 | 25.9863 | 25.4253 | 23.2011 | 22.6232 | 22.2211 | 24.8505 | 24.7063 | 24.5663 | 24.4011 | 24.2358 | 24.0516 | 23.8305 | 23.5484 | 23.2474 | 22.06 | 21.7221 | 21.4895
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN PRIMARY | MINIMUM HEADROOM | SU 06593 00685 | NO | YES | 0 | 46.3659 | 46.0785 | 45.748 | 45.2922 | 44.7437 | 44.1448 | 42.9059 | 41.3343 | 39.7648 | 34.8964 | 24.6237 | 17.2774 | 44.4374 | 43.7553 | 42.8111 | 41.5143 | 39.9606 | 38.2659 | 36.5827 | 34.8532 | 33.1259 | 27.4953 | 16.7553 | 8.3774 | 45.4543 | 44.7637 | 43.8101 | 42.4995 | 40.9269 | 39.2143 | 37.5111 | 35.7616 | 34.0132 | 28.2869 | 17.3374 | 8.8269
|  | FERNDOWN PRIMARY | EE |  |  |  |  | 46.3659 | 46.0785 | 45.7616 | 45.3353 | 44.748 | 44.1943 | 43.689 | 43.169 | 42.6564 | 34.8964 | 30.5995 | 23.3985 | 44.4374 | 43.7553 | 43.0101 | 42.1511 | 41.1237 | 40.1459 | 39.1469 | 38.149 | 37.1774 | 27.4953 | 23.409 | 15.1048 | 45.4543 | 44.7637 | 44.0122 | 43.1459 | 42.1101 | 41.1237 | 40.1185 | 39.1111 | 38.1311 | 28.2869 | 24.0774 | 15.6332
|  | FERNDOWN PRIMARY | HT |  |  |  |  | 46.3785 | 46.1069 | 45.748 | 45.2922 | 44.7437 | 44.1448 | 42.9059 | 41.3343 | 39.7648 | 35.4522 | 24.6237 | 17.2774 | 44.5301 | 43.7953 | 42.8111 | 41.5143 | 39.9606 | 38.2659 | 36.5827 | 34.8532 | 33.1259 | 29.1816 | 16.7553 | 8.3774 | 45.548 | 44.8048 | 43.8101 | 42.4995 | 40.9269 | 39.2143 | 37.5111 | 35.7616 | 34.0132 | 29.968 | 17.3374 | 8.8269
|  | FERNDOWN PRIMARY | HE |  |  |  |  | 46.4469 | 46.1806 | 45.8848 | 45.4764 | 44.9016 | 44.3816 | 43.8785 | 43.3627 | 42.8595 | 37.1732 | 33.4627 | 26.7659 | 44.868 | 44.349 | 43.749 | 43.0122 | 42.0669 | 41.1953 | 40.3459 | 39.4943 | 38.6711 | 30.0385 | 26.5943 | 18.8364 | 45.8911 | 45.368 | 44.7627 | 44.0195 | 43.068 | 42.1901 | 41.3343 | 40.4764 | 39.648 | 30.8637 | 27.3048 | 19.4122
|  | FERNDOWN PRIMARY | FB |  |  |  |  | 46.6448 | 46.5174 | 46.4037 | 46.2753 | 46.1322 | 45.988 | 45.849 | 45.7185 | 45.5795 | 45.069 | 40.5637 | 34.6027 | 45.2427 | 44.8764 | 44.5743 | 44.2469 | 43.8869 | 43.5259 | 43.1627 | 42.8048 | 42.4374 | 39.728 | 33.6701 | 26.7848 | 46.268 | 45.8985 | 45.5932 | 45.2616 | 44.8985 | 44.5332 | 44.1659 | 43.8048 | 43.4332 | 40.6848 | 34.5259 | 27.5227
FLEET-BRAMLEY GSP | FERNHURST BSP | FIVE OAKS PRIMARY | MINIMUM HEADROOM | TQ 10647 29057 | NO | YES | 0 | 12.9466 | 12.6255 | 12.8666 | 12.5718 | 12.1939 | 11.2761 | 10.5908 | 9.935 | 9.1992 | 6.0076 | 4.9697 | 4.0361 | 9.4405 | 9.03 | 9.2889 | 8.9616 | 8.5321 | 8.0795 | 7.4795 | 6.7363 | 5.9005 | 2.2174 | 1.0363 | -0.025789 | 10.3537 | 9.9253 | 10.1926 | 9.8526 | 9.4242 | 8.9726 | 8.7347 | 7.9926 | 7.1558 | 3.4716 | 2.2905 | 1.2274
|  | FIVE OAKS PRIMARY | EE |  |  |  |  | 12.9466 | 12.6255 | 13.9476 | 13.1834 | 12.1939 | 11.295 | 10.8171 | 10.3887 | 9.8803 | 8.0908 | 7.3424 | 6.6855 | 9.4405 | 9.03 | 11.3121 | 10.4353 | 9.3016 | 8.2732 | 7.7374 | 7.2595 | 6.6879 | 4.6047 | 3.7405 | 2.9795 | 10.3537 | 9.9253 | 12.5684 | 11.6916 | 10.5579 | 9.5295 | 8.9937 | 8.5158 | 7.9432 | 5.8589 | 4.9947 | 4.2326
|  | FIVE OAKS PRIMARY | HT |  |  |  |  | 12.9497 | 14.4908 | 13.9645 | 13.1961 | 12.2403 | 11.2761 | 10.5908 | 9.935 | 9.1992 | 6.0076 | 4.9697 | 4.0361 | 9.4658 | 11.5689 | 11.3332 | 10.4532 | 9.3574 | 8.2542 | 7.4795 | 6.7363 | 5.9005 | 2.2174 | 1.0363 | -0.025789 | 10.3789 | 12.9958 | 12.5895 | 11.7095 | 10.6137 | 9.5105 | 8.7347 | 7.9926 | 7.1558 | 3.4716 | 2.2905 | 1.2274
|  | FIVE OAKS PRIMARY | HE |  |  |  |  | 12.9697 | 12.7718 | 14.1276 | 13.395 | 12.4276 | 11.555 | 11.1192 | 10.7297 | 10.2624 | 8.7445 | 8.1592 | 7.6413 | 9.5563 | 9.1911 | 11.5079 | 10.6774 | 9.5679 | 8.5689 | 8.0826 | 7.6511 | 7.1268 | 5.3426 | 4.6605 | 4.0542 | 10.4737 | 10.0926 | 12.7737 | 11.9337 | 10.8242 | 9.8253 | 9.3389 | 8.9063 | 8.3821 | 6.5979 | 5.9147 | 5.3095
|  | FIVE OAKS PRIMARY | FB |  |  |  |  | 13.0255 | 12.9918 | 12.8666 | 12.5718 | 12.2013 | 11.8108 | 11.6139 | 11.4434 | 11.2139 | 10.5992 | 11.9487 | 11.5276 | 9.7163 | 9.5195 | 9.2889 | 8.9616 | 8.5321 | 8.0795 | 7.8553 | 7.6605 | 7.3963 | 6.6984 | 9.0089 | 8.5226 | 10.6379 | 10.4337 | 10.1926 | 9.8526 | 9.4242 | 8.9726 | 8.7484 | 8.5537 | 8.2905 | 7.5926 | 10.2653 | 9.7789
AMERSHAM GSP | LOUDWATER BSP | FLACKWELL HEATH PRIMARY | MINIMUM HEADROOM | SU 90667 89318 | NO | YES | 0 | 28.4716 | 28.3179 | 28.1358 | 27.8916 | 27.5926 | 27.2726 | 26.7379 | 26.1021 | 25.4389 | 23.8305 | 22.7758 | 21.8505 | 26.9116 | 26.5884 | 26.26 | 25.7768 | 25.1568 | 24.4747 | 23.7768 | 23.0505 | 22.3253 | 20.5611 | 19.3989 | 18.3779 | 28.0947 | 27.7716 | 27.4421 | 26.9589 | 26.3389 | 25.6568 | 24.9589 | 24.2316 | 23.5063 | 21.7421 | 20.58 | 19.5589
|  | FLACKWELL HEATH PRIMARY | EE |  |  |  |  | 28.4716 | 28.3179 | 28.14 | 27.9042 | 27.5926 | 27.2811 | 26.9905 | 26.6947 | 26.4021 | 25.82 | 25.1326 | 24.5579 | 26.9116 | 26.5884 | 26.26 | 25.8916 | 25.4716 | 25.0579 | 24.6147 | 24.16 | 23.7158 | 22.8095 | 22.0137 | 21.3558 | 28.0947 | 27.7716 | 27.4421 | 27.0737 | 26.6547 | 26.2411 | 25.7979 | 25.3421 | 24.8979 | 23.9905 | 23.1958 | 22.5379
|  | FLACKWELL HEATH PRIMARY | HT |  |  |  |  | 28.4758 | 28.3295 | 28.1358 | 27.8916 | 27.5958 | 27.2726 | 26.7379 | 26.1021 | 25.4389 | 23.8305 | 22.7758 | 21.8505 | 26.9463 | 26.6832 | 26.2895 | 25.7768 | 25.1568 | 24.4747 | 23.7768 | 23.0505 | 22.3253 | 20.5611 | 19.3989 | 18.3779 | 28.16 | 27.8663 | 27.4726 | 26.9589 | 26.3389 | 25.6568 | 24.9589 | 24.2316 | 23.5063 | 21.7421 | 20.58 | 19.5589
|  | FLACKWELL HEATH PRIMARY | HE |  |  |  |  | 28.4989 | 28.3505 | 28.1779 | 27.9432 | 27.6337 | 27.3337 | 27.0411 | 26.7474 | 26.4568 | 26.4737 | 26.4389 | 26.1958 | 26.9695 | 26.8211 | 26.6421 | 26.3316 | 25.9537 | 25.5905 | 25.2158 | 24.8326 | 24.4579 | 24.0737 | 23.6116 | 23.2337 | 28.2274 | 28.0737 | 27.8242 | 27.5147 | 27.1368 | 26.7737 | 26.3989 | 26.0147 | 25.6411 | 25.2568 | 24.7937 | 24.4158
|  | FLACKWELL HEATH PRIMARY | FB |  |  |  |  | 28.62 | 28.5484 | 28.4853 | 28.4137 | 28.3347 | 28.2547 | 28.1768 | 28.1042 | 28.0274 | 27.7442 | 27.5863 | 27.3242 | 27.0905 | 27.0189 | 26.9558 | 26.8779 | 26.7253 | 26.5758 | 26.4232 | 26.2695 | 26.1137 | 25.4432 | 24.8653 | 24.3779 | 28.3537 | 28.2758 | 28.2042 | 28.06 | 27.9084 | 27.7589 | 27.6063 | 27.4526 | 27.2958 | 26.6263 | 26.0484 | 25.56
NURSLING GSP | ROWNHAMS BSP | FLETCHWOOD PRIMARY | MINIMUM HEADROOM | SU 33800 12142 | NO | YES | 5.7368 | 33.6311 | 33.1163 | 32.3595 | 31.3721 | 30.21 | 28.9226 | 27.6016 | 26.21 | 24.7953 | 24.1016 | 22.3468 | 20.8753 | 33.7437 | 33.1026 | 32.1563 | 30.9142 | 29.4574 | 27.8395 | 26.1732 | 24.4016 | 22.5942 | 22.9468 | 20.75 | 18.9089 | 33.7721 | 33.1426 | 32.2142 | 30.9942 | 29.5584 | 27.9426 | 26.2784 | 24.51 | 22.7058 | 23.4405 | 21.2921 | 19.4511
|  | FLETCHWOOD PRIMARY | EE |  |  |  |  | 33.6311 | 33.1247 | 32.5405 | 31.8689 | 31.1005 | 30.3089 | 29.4721 | 28.5742 | 27.6911 | 25.2858 | 27.2184 | 26.3026 | 33.7437 | 33.1289 | 32.41 | 31.6089 | 30.7342 | 29.8079 | 28.7984 | 27.7068 | 26.6332 | 23.3311 | 27.0268 | 25.8289 | 33.7721 | 33.1668 | 32.4595 | 31.6721 | 30.8068 | 29.8942 | 28.9005 | 27.81 | 26.7374 | 23.4405 | 27.6184 | 26.4089
|  | FLETCHWOOD PRIMARY | HT |  |  |  |  | 33.6721 | 33.1163 | 32.3595 | 31.3721 | 30.21 | 28.9226 | 27.6016 | 26.21 | 24.7953 | 24.1016 | 22.3468 | 20.8753 | 33.7963 | 33.1026 | 32.1563 | 30.9142 | 29.4574 | 27.8395 | 26.1732 | 24.4016 | 22.5942 | 22.9468 | 20.75 | 18.9089 | 33.8237 | 33.1426 | 32.2142 | 30.9942 | 29.5584 | 27.9426 | 26.2784 | 24.51 | 22.7058 | 23.4995 | 21.2921 | 19.4511
|  | FLETCHWOOD PRIMARY | HE |  |  |  |  | 33.9174 | 33.5226 | 33.0395 | 32.4542 | 31.75 | 31.0405 | 30.2816 | 29.4616 | 28.6584 | 26.9332 | 29.29 | 28.7363 | 34.1216 | 33.6563 | 33.0711 | 32.3837 | 31.5911 | 30.7658 | 29.8647 | 28.8826 | 27.9195 | 25.4321 | 29.6195 | 28.8574 | 34.0858 | 33.6826 | 33.1068 | 32.4289 | 31.6447 | 30.83 | 29.9426 | 28.9763 | 28.0216 | 25.5384 | 30.2332 | 29.4626
|  | FLETCHWOOD PRIMARY | FB |  |  |  |  | 34.1847 | 33.9226 | 33.6816 | 33.43 | 33.1774 | 32.8889 | 32.5668 | 32.2121 | 31.8416 | 30.6216 | 29.3332 | 28.7132 | 34.4289 | 34.1016 | 33.7995 | 33.4858 | 33.1763 | 32.8174 | 32.4079 | 31.9511 | 31.4711 | 29.9142 | 28.1774 | 27.3563 | 34.2658 | 34.1237 | 33.8268 | 33.5195 | 33.2153 | 32.8626 | 32.4616 | 32.0142 | 31.5447 | 30.0163 | 28.2826 | 27.4626
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE PRIMARY | MINIMUM HEADROOM | SU 14069 15523 | NO | YES | 0 | 13.8676 | 13.6655 | 13.3118 | 12.9613 | 12.5445 | 12.0803 | 11.5255 | 10.8097 | 10.1129 | 8.8571 | 8.1539 | 7.5687 | 13.9532 | 13.5384 | 12.7711 | 12.0605 | 11.2153 | 10.2721 | 9.4047 | 8.5911 | 7.7995 | 6.39 | 5.6058 | 4.9532 | 13.6768 | 13.5905 | 13.4926 | 13.0853 | 12.2495 | 11.3158 | 10.4579 | 9.6537 | 8.8705 | 7.4747 | 6.6968 | 6.0495
|  | FORDINGBRIDGE PRIMARY | EE |  |  |  |  | 13.8676 | 13.6782 | 13.3339 | 13.0413 | 12.6824 | 12.3076 | 11.9603 | 11.6382 | 11.1529 | 10.4024 | 9.9076 | 9.5213 | 13.9532 | 13.59 | 12.8247 | 12.2521 | 11.5858 | 10.8574 | 10.1816 | 9.5805 | 9.0132 | 8.1479 | 7.5826 | 7.1395 | 13.6768 | 13.5905 | 13.4958 | 13.2747 | 12.6158 | 11.8937 | 11.2253 | 10.6295 | 10.0674 | 9.2126 | 8.6537 | 8.2168
|  | FORDINGBRIDGE PRIMARY | HT |  |  |  |  | 13.8782 | 13.6655 | 13.3118 | 12.9613 | 12.5445 | 12.0803 | 11.5255 | 10.8097 | 10.1129 | 8.8571 | 8.1539 | 7.5687 | 13.9742 | 13.5384 | 12.7711 | 12.0605 | 11.2153 | 10.2721 | 9.4047 | 8.5911 | 7.7995 | 6.39 | 5.6058 | 4.9532 | 13.6811 | 13.6 | 13.4926 | 13.0853 | 12.2495 | 11.3158 | 10.4579 | 9.6537 | 8.8705 | 7.4747 | 6.6968 | 6.0495
|  | FORDINGBRIDGE PRIMARY | HE |  |  |  |  | 13.9329 | 13.7676 | 13.4424 | 13.1634 | 12.8182 | 12.4613 | 12.1339 | 11.8318 | 11.5403 | 11.1055 | 10.7897 | 10.5571 | 14.0837 | 13.7742 | 13.0521 | 12.5111 | 11.8721 | 11.1763 | 10.55 | 9.9974 | 9.4742 | 8.9447 | 8.5774 | 8.3058 | 13.7021 | 13.6232 | 13.5347 | 13.4105 | 12.8979 | 12.2095 | 11.5895 | 11.0421 | 10.5242 | 10.0011 | 9.6389 | 9.3705
|  | FORDINGBRIDGE PRIMARY | FB |  |  |  |  | 14.0266 | 13.9339 | 13.8003 | 13.6792 | 13.5571 | 13.4161 | 13.2803 | 13.1539 | 13.0266 | 12.7476 | 12.5234 | 12.3782 | 14.2384 | 14.0542 | 13.7542 | 13.4942 | 13.2384 | 12.9332 | 12.6384 | 12.3658 | 12.0942 | 11.6016 | 11.1458 | 10.8437 | 13.76 | 13.7221 | 13.6874 | 13.6495 | 13.6053 | 13.5632 | 13.5211 | 13.3884 | 13.1189 | 12.6316 | 12.1811 | 11.8821
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK PRIMARY | MINIMUM HEADROOM | SU 66139 00180 | NO | YES | 0 | 25.3768 | 24.8147 | 24.26 | 23.3095 | 22.3453 | 21.2105 | 20.1095 | 19.0284 | 17.9432 | 14.7011 | 12.2105 | 9.9884 | 32.3747 | 32.0989 | 31.7937 | 31.3779 | 30.6232 | 29.3379 | 28.0979 | 26.8789 | 25.6463 | 21.8842 | 18.9516 | 16.3368 | 32.6611 | 32.2832 | 31.8747 | 31.2568 | 30.48 | 29.1958 | 27.9568 | 26.7389 | 25.5168 | 21.7979 | 18.9 | 16.3168
|  | FRATTON PARK PRIMARY | EE |  |  |  |  | 25.3768 | 24.8147 | 24.26 | 23.48 | 22.5916 | 21.7937 | 21.0232 | 20.3063 | 19.6032 | 18.0937 | 16.2926 | 14.7579 | 32.3747 | 32.0989 | 31.7937 | 31.3779 | 30.8179 | 30.0905 | 29.2495 | 28.4821 | 27.7274 | 25.9579 | 23.7853 | 21.9263 | 32.6611 | 32.2832 | 31.8747 | 31.3084 | 30.6147 | 29.9474 | 29.1063 | 28.3389 | 27.5853 | 25.8179 | 23.6726 | 21.84
|  | FRATTON PARK PRIMARY | HT |  |  |  |  | 25.4853 | 24.9558 | 24.3011 | 23.3095 | 22.3453 | 21.2105 | 20.1095 | 19.0284 | 17.9432 | 14.7011 | 12.2105 | 9.9884 | 32.4095 | 32.1621 | 31.8368 | 31.4074 | 30.6232 | 29.3379 | 28.0979 | 26.8789 | 25.6463 | 21.8842 | 18.9516 | 16.3368 | 32.7053 | 32.3779 | 31.9168 | 31.2568 | 30.48 | 29.1958 | 27.9568 | 26.7389 | 25.5168 | 21.7979 | 18.9 | 16.3168
|  | FRATTON PARK PRIMARY | HE |  |  |  |  | 25.6674 | 25.2063 | 24.7347 | 24.0158 | 23.1558 | 22.4158 | 21.7358 | 21.1242 | 20.5221 | 20.1368 | 19.3126 | 18.3179 | 32.4242 | 32.1484 | 31.8379 | 31.4095 | 30.8232 | 30.2853 | 29.7589 | 29.2326 | 28.7126 | 28.4126 | 27.4126 | 26.1905 | 32.7389 | 32.4421 | 32.0958 | 31.5484 | 30.8495 | 30.2284 | 29.6389 | 29.0779 | 28.5242 | 28.2695 | 27.2705 | 26.0505
|  | FRATTON PARK PRIMARY | FB |  |  |  |  | 26.0642 | 25.7284 | 25.4705 | 25.1379 | 24.7937 | 24.4537 | 24.1568 | 23.9074 | 23.6495 | 22.5895 | 21.6537 | 20.6137 | 32.6211 | 32.4632 | 32.3232 | 32.1642 | 31.9884 | 31.8126 | 31.6432 | 31.4863 | 31.3211 | 30.7042 | 29.9 | 28.6568 | 32.9579 | 32.7789 | 32.6263 | 32.4484 | 32.2084 | 31.9653 | 31.7442 | 31.5495 | 31.3453 | 30.5463 | 29.7568 | 28.5158
COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD PRIMARY | MINIMUM HEADROOM | SP 50426 08256 | NO | YES | 0 | 18.2895 | 18.2137 | 18.1305 | 18.0105 | 17.8621 | 17.4242 | 17.0516 | 16.6063 | 16.1274 | 15.0937 | 14.5526 | 14.0737 | 17.2316 | 17.1516 | 17.0653 | 16.8211 | 16.14 | 15.4316 | 15 | 14.5032 | 13.9653 | 12.8116 | 12.2168 | 11.6895 | 14.5842 | 14.42 | 14.2232 | 13.9284 | 13.2411 | 12.5274 | 12.0968 | 11.6011 | 11.0642 | 9.9116 | 9.3179 | 8.7926
|  | FRENCHAY ROAD PRIMARY | EE |  |  |  |  | 18.2895 | 18.2137 | 18.1305 | 18.02 | 17.8621 | 17.7147 | 17.5526 | 17.3484 | 17.1484 | 16.7432 | 16.3674 | 16.0621 | 17.2316 | 17.1516 | 17.0653 | 16.9516 | 16.4189 | 15.8842 | 15.66 | 15.4316 | 15.2095 | 14.7053 | 14.2821 | 13.9389 | 14.5842 | 14.42 | 14.2568 | 14.0737 | 13.5221 | 12.9821 | 12.7579 | 12.5284 | 12.3053 | 11.8021 | 11.3789 | 11.0358
|  | FRENCHAY ROAD PRIMARY | HT |  |  |  |  | 18.2968 | 18.2253 | 18.1326 | 18.0105 | 17.8663 | 17.4242 | 17.0516 | 16.6063 | 16.1274 | 15.0937 | 14.5526 | 14.0737 | 17.2389 | 17.1642 | 17.0663 | 16.8211 | 16.14 | 15.4316 | 15 | 14.5032 | 13.9653 | 12.8116 | 12.2168 | 11.6895 | 14.5937 | 14.4379 | 14.2232 | 13.9284 | 13.2411 | 12.5274 | 12.0968 | 11.6011 | 11.0642 | 9.9116 | 9.3179 | 8.7926
|  | FRENCHAY ROAD PRIMARY | HE |  |  |  |  | 18.3095 | 18.2358 | 18.1516 | 18.0368 | 17.8726 | 17.7263 | 17.5853 | 17.44 | 17.2979 | 17.2947 | 17.1684 | 17.0516 | 17.2558 | 17.18 | 17.0937 | 16.9768 | 16.6484 | 16.1358 | 15.9558 | 15.7737 | 15.5989 | 15.4579 | 15.2537 | 15.1021 | 14.7011 | 14.5779 | 14.4495 | 14.2905 | 13.7547 | 13.2379 | 13.0579 | 12.8747 | 12.7 | 12.5568 | 12.3516 | 12.1989
|  | FRENCHAY ROAD PRIMARY | FB |  |  |  |  | 18.3579 | 18.3158 | 18.2789 | 18.2368 | 18.1895 | 18.1432 | 18.0968 | 18.0547 | 18.0095 | 17.8421 | 17.7484 | 17.6874 | 17.3063 | 17.2621 | 17.2232 | 17.1789 | 17.1242 | 16.9747 | 16.8895 | 16.8095 | 16.7284 | 16.3968 | 16.1011 | 15.8484 | 14.7916 | 14.6895 | 14.6147 | 14.5326 | 14.3137 | 14.0821 | 13.9958 | 13.9158 | 13.8337 | 13.5011 | 13.2021 | 12.9474
FAWLEY GSP | COWES BSP | FRESHWATER PRIMARY | MINIMUM HEADROOM | SZ 34325 86965 | NO | YES | 0 | 15.5403 | 15.3182 | 15.0403 | 14.6476 | 14.175 | 13.6613 | 13.2013 | 10.3508 | 9.8655 | 8.5297 | 7.5529 | 6.6529 | 13.9216 | 13.6711 | 13.3521 | 12.9026 | 12.3616 | 11.7732 | 11.2521 | 7.6574 | 7.1016 | 5.5489 | 4.3942 | 3.35 | 14.7811 | 14.5305 | 14.2116 | 13.7632 | 13.2221 | 12.6347 | 12.1147 | 8.5253 | 7.9705 | 6.42 | 5.2674 | 4.2242
|  | FRESHWATER PRIMARY | EE |  |  |  |  | 15.5403 | 15.3182 | 15.0403 | 14.715 | 14.3318 | 13.9592 | 13.6413 | 12.1276 | 11.8055 | 11.1234 | 10.4666 | 9.8887 | 13.9216 | 13.6711 | 13.3521 | 12.9868 | 12.5647 | 12.1532 | 11.8079 | 9.9268 | 9.5753 | 8.7426 | 7.9363 | 7.2226 | 14.7811 | 14.5305 | 14.2116 | 13.8463 | 13.4253 | 13.0147 | 12.6695 | 10.7895 | 10.4389 | 9.6084 | 8.8042 | 8.0905
|  | FRESHWATER PRIMARY | HT |  |  |  |  | 15.5803 | 15.3676 | 15.0497 | 14.6476 | 14.175 | 13.6613 | 13.2013 | 10.3508 | 9.8655 | 8.5297 | 7.5529 | 6.6529 | 13.9721 | 13.7321 | 13.3658 | 12.9026 | 12.3616 | 11.7732 | 11.2521 | 7.6574 | 7.1016 | 5.5489 | 4.3942 | 3.35 | 14.8316 | 14.5916 | 14.2263 | 13.7632 | 13.2221 | 12.6347 | 12.1147 | 8.5253 | 7.9705 | 6.42 | 5.2674 | 4.2242
|  | FRESHWATER PRIMARY | HE |  |  |  |  | 15.6782 | 15.5087 | 15.2792 | 14.9961 | 14.6382 | 14.2992 | 14.0276 | 12.5613 | 12.2813 | 11.9782 | 11.5561 | 11.1718 | 14.0932 | 13.9089 | 13.65 | 13.3363 | 12.9468 | 12.5753 | 12.29 | 10.4679 | 10.1711 | 9.7763 | 9.2405 | 8.7521 | 14.9516 | 14.7674 | 14.5095 | 14.1958 | 13.8074 | 13.4358 | 13.1495 | 11.3316 | 11.0347 | 10.64 | 10.1063 | 9.6189
|  | FRESHWATER PRIMARY | FB |  |  |  |  | 15.8234 | 15.7013 | 15.5876 | 15.4645 | 15.3308 | 15.195 | 15.0929 | 14.9876 | 14.8824 | 14.3961 | 13.9476 | 13.5497 | 14.2521 | 14.1121 | 13.9795 | 13.8374 | 13.6816 | 13.5247 | 13.4111 | 13.2911 | 13.1721 | 12.61 | 12.0668 | 11.5784 | 15.1116 | 14.9705 | 14.8389 | 14.6968 | 14.5411 | 14.3853 | 14.2716 | 14.1505 | 14.0326 | 13.4705 | 12.9284 | 12.4411
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FRIMLEY PRIMARY | MINIMUM HEADROOM | SU 87745 57942 | NO | YES | 0 | 32.2932 | 31.4889 | 30.6963 | 29.6184 | 28.7953 | 27.7016 | 26.5984 | 25.4847 | 24.3868 | 22.0132 | 20.1837 | 18.9468 | 28.9063 | 27.8684 | 26.8632 | 25.5021 | 24.5284 | 23.2779 | 21.9263 | 20.5558 | 19.2063 | 16.3063 | 13.9168 | 12.4105 | 31.4842 | 30.6274 | 29.7905 | 28.6505 | 27.7947 | 26.6695 | 25.3074 | 23.9263 | 22.5663 | 19.6453 | 17.1558 | 15.6368
|  | FRIMLEY PRIMARY | EE |  |  |  |  | 32.2932 | 31.4889 | 30.6963 | 29.7037 | 28.7953 | 28.2132 | 28.0384 | 27.4668 | 26.9058 | 25.8405 | 24.9121 | 24.15 | 28.9063 | 27.8684 | 26.8632 | 25.6116 | 24.5284 | 23.9011 | 23.9168 | 23.2937 | 22.6821 | 21.3063 | 20.1021 | 19.1126 | 31.4842 | 30.6274 | 29.7905 | 28.7411 | 27.7947 | 27.2032 | 27.32 | 26.6958 | 26.0811 | 24.6916 | 23.4768 | 22.4779
|  | FRIMLEY PRIMARY | HT |  |  |  |  | 32.3679 | 31.5974 | 30.7437 | 29.6184 | 28.8121 | 27.7016 | 26.5984 | 25.4847 | 24.3868 | 22.0132 | 20.1837 | 18.9468 | 29.0074 | 28.0126 | 26.9337 | 25.5021 | 24.6389 | 23.2779 | 21.9263 | 20.5558 | 19.2063 | 16.3063 | 13.9168 | 12.4105 | 31.5642 | 30.7453 | 29.8421 | 28.6505 | 28.04 | 26.6695 | 25.3074 | 23.9263 | 22.5663 | 19.6453 | 17.1558 | 15.6368
|  | FRIMLEY PRIMARY | HE |  |  |  |  | 32.5637 | 31.8584 | 31.15 | 30.2311 | 29.3689 | 28.8542 | 28.7437 | 28.2384 | 27.7395 | 26.8763 | 26.3332 | 25.9005 | 29.26 | 28.3579 | 27.4663 | 26.3126 | 25.2937 | 24.7505 | 24.8558 | 24.3242 | 23.8 | 22.4926 | 21.7537 | 21.1621 | 31.7726 | 31.0242 | 30.2758 | 29.3063 | 28.4095 | 27.8895 | 28.0884 | 27.5779 | 27.0737 | 25.8084 | 25.0611 | 24.4632
|  | FRIMLEY PRIMARY | FB |  |  |  |  | 33.0058 | 32.5995 | 32.2721 | 31.8847 | 31.5626 | 31.3132 | 31.1226 | 30.9405 | 30.7542 | 29.9574 | 29.2742 | 28.7216 | 29.8147 | 29.2853 | 28.8632 | 28.3621 | 27.9568 | 27.6558 | 27.4337 | 27.2232 | 27.0074 | 26.06 | 25.1937 | 24.4758 | 32.0968 | 31.8063 | 31.4579 | 31.0463 | 30.7063 | 30.4453 | 30.2474 | 30.06 | 29.8674 | 29.0368 | 28.3147 | 27.7253
MELKSHAM GSP | FROME BSP | FROME PRIMARY | MINIMUM HEADROOM | ST 78850 48051 | NO | YES | 0 | 51.8158 | 50.8968 | 49.3453 | 47.6853 | 45.8253 | 44.0221 | 42.1505 | 40.5516 | 35.9126 | 28.7653 | 23.8337 | 21.2874 | 43.3758 | 41.9021 | 40.2042 | 38.3958 | 36.3905 | 34.44 | 32.4063 | 30.6821 | 25.5642 | 18.1895 | 12.2926 | 9.5326 | 48.7779 | 47.3316 | 45.6684 | 43.8947 | 41.9221 | 39.9632 | 37.8526 | 36.0695 | 30.74 | 22.9684 | 16.9126 | 14.0495
|  | FROME PRIMARY | EE |  |  |  |  | 51.8158 | 50.8968 | 49.3453 | 47.6853 | 45.8253 | 44.0221 | 42.1505 | 40.5516 | 37.5105 | 31.7726 | 29.0105 | 27.2263 | 43.3758 | 41.9021 | 40.2042 | 38.3958 | 36.3905 | 34.44 | 32.4063 | 30.6821 | 27.3368 | 20.9547 | 18.3821 | 16.4253 | 48.7779 | 47.3316 | 45.6684 | 43.8947 | 41.9221 | 39.9632 | 37.8526 | 36.0695 | 32.5811 | 25.8926 | 23.1095 | 21.0632
|  | FROME PRIMARY | HT |  |  |  |  | 51.8558 | 51.0853 | 49.5189 | 47.8432 | 46.0316 | 44.1579 | 42.2326 | 40.5779 | 35.9126 | 28.7653 | 23.8337 | 21.2874 | 43.5211 | 42.1053 | 40.3947 | 38.5737 | 36.6116 | 34.5863 | 32.5042 | 30.7242 | 25.5642 | 18.1895 | 12.2926 | 9.5326 | 48.9211 | 47.5337 | 45.8579 | 44.0716 | 42.1442 | 40.1242 | 37.9695 | 36.1295 | 30.74 | 22.9684 | 16.9126 | 14.0495
|  | FROME PRIMARY | HE |  |  |  |  | 51.9442 | 51.4758 | 50.06 | 48.5053 | 46.7137 | 45.0105 | 43.2674 | 41.8158 | 38.9179 | 34.3021 | 31.1189 | 29.9347 | 43.8379 | 42.5358 | 40.9863 | 39.2958 | 37.3642 | 35.5211 | 33.6337 | 32.0737 | 28.8874 | 23.6989 | 19.9042 | 18.5853 | 49.2326 | 47.9558 | 46.4389 | 44.7811 | 42.8832 | 41.0737 | 39.1453 | 37.5347 | 34.2168 | 28.7642 | 24.8305 | 23.4495
|  | FROME PRIMARY | FB |  |  |  |  | 52.1895 | 51.9958 | 51.8158 | 51.2295 | 50.5337 | 49.8 | 48.9968 | 48.3242 | 47.6042 | 44.3242 | 42.0453 | 40.8726 | 44.4589 | 43.7116 | 42.9832 | 42.2474 | 41.4874 | 40.6832 | 39.8 | 39.0642 | 38.2747 | 34.6632 | 32.1432 | 30.8516 | 49.8432 | 49.1105 | 48.3979 | 47.6779 | 46.9337 | 46.1453 | 45.2821 | 44.5611 | 43.7884 | 40.1621 | 37.5316 | 36.1853
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE PRIMARY | MINIMUM HEADROOM | SU 84935 93873 | NO | YES | 0 | 24.4105 | 24.1895 | 23.9526 | 23.5989 | 23.1737 | 22.7042 | 22.2189 | 21.2463 | 20.2737 | 17.96 | 16.4379 | 15.0832 | 23.0242 | 22.7411 | 22.3211 | 21.6211 | 20.74 | 19.7579 | 18.7505 | 17.6905 | 16.6253 | 14.0926 | 12.42 | 10.9295 | 22.8179 | 22.5979 | 22.3632 | 22.0158 | 21.5958 | 20.8 | 19.7895 | 18.7347 | 17.6789 | 15.1695 | 13.4884 | 11.9863
|  | FRYERS LANE PRIMARY | EE |  |  |  |  | 24.4105 | 24.1895 | 23.9537 | 23.64 | 23.2042 | 22.8021 | 22.4295 | 22.0411 | 21.6568 | 21.1484 | 20.0589 | 19.1442 | 23.0242 | 22.7411 | 22.3211 | 21.8453 | 21.28 | 20.7474 | 20.1832 | 19.5863 | 19.0011 | 17.6632 | 16.4411 | 15.4126 | 22.8179 | 22.5979 | 22.3653 | 22.0537 | 21.62 | 21.2179 | 20.8484 | 20.4621 | 20.0442 | 18.7011 | 17.4916 | 16.4737
|  | FRYERS LANE PRIMARY | HT |  |  |  |  | 24.4337 | 24.2263 | 23.9526 | 23.5989 | 23.1737 | 22.7042 | 22.2189 | 21.2463 | 20.2737 | 17.96 | 16.4379 | 15.0832 | 23.0442 | 22.8421 | 22.3442 | 21.6211 | 20.74 | 19.7579 | 18.7505 | 17.6905 | 16.6253 | 14.0926 | 12.42 | 10.9295 | 22.8389 | 22.6337 | 22.3632 | 22.0158 | 21.5958 | 20.8 | 19.7895 | 18.7347 | 17.6789 | 15.1695 | 13.4884 | 11.9863
|  | FRYERS LANE PRIMARY | HE |  |  |  |  | 24.4937 | 24.2937 | 24.0726 | 23.7716 | 23.3411 | 22.9621 | 22.5905 | 22.2074 | 21.8326 | 21.8 | 21.6621 | 21.5632 | 23.1 | 22.9032 | 22.6853 | 22.3863 | 21.9505 | 21.4905 | 21.0168 | 20.5147 | 20.0253 | 19.4474 | 18.72 | 18.1147 | 22.8968 | 22.6979 | 22.4789 | 22.1789 | 21.7505 | 21.3716 | 21.0011 | 20.62 | 20.2463 | 20.2211 | 19.7611 | 19.1537
|  | FRYERS LANE PRIMARY | FB |  |  |  |  | 24.6337 | 24.5232 | 24.4253 | 24.3168 | 24.1979 | 24.0768 | 23.9589 | 23.8495 | 23.7316 | 23.2895 | 23.0211 | 22.8368 | 23.2379 | 23.1305 | 23.0347 | 22.9295 | 22.8126 | 22.6821 | 22.4705 | 22.2568 | 22.0368 | 21.0905 | 20.2621 | 19.5547 | 23.0358 | 22.9274 | 22.8295 | 22.7232 | 22.6053 | 22.4853 | 22.3695 | 22.26 | 22.1442 | 21.7084 | 21.3053 | 20.5947
COWLEY GSP | DRAYTON BSP | FULSCOT PRIMARY | MINIMUM HEADROOM | SU 54413 89511 | NO | YES | 0.21053 | 32.6605 | 32.3458 | 31.5616 | 30.9153 | 30.0679 | 29.2226 | 28.3668 | 27.3963 | 26.5437 | 24.3574 | 23.2416 | 21.9458 | 29.7116 | 28.7168 | 27.8295 | 27.1168 | 26.1768 | 25.2463 | 24.3011 | 23.22 | 22.2768 | 19.8484 | 18.6242 | 17.1758 | 30.4579 | 29.6084 | 28.7232 | 28.0105 | 27.0726 | 26.1442 | 25.2011 | 24.1221 | 23.1811 | 20.7568 | 19.5358 | 18.0905
|  | FULSCOT PRIMARY | EE |  |  |  |  | 32.6605 | 32.3742 | 31.6511 | 31.0489 | 30.3363 | 29.6447 | 28.8753 | 28.0153 | 27.2732 | 25.9258 | 25.2026 | 24.4868 | 29.7116 | 28.7537 | 27.9347 | 27.2705 | 26.4947 | 25.7379 | 24.8853 | 23.9253 | 23.1063 | 21.5653 | 20.7526 | 19.9421 | 30.4579 | 29.6453 | 28.8274 | 28.1653 | 27.3905 | 26.6347 | 25.7832 | 24.8253 | 24.0074 | 22.4705 | 21.66 | 20.8505
|  | FULSCOT PRIMARY | HT |  |  |  |  | 32.6742 | 32.3458 | 31.5616 | 30.9153 | 30.0679 | 29.2226 | 28.3668 | 27.3963 | 26.5437 | 24.3574 | 23.2416 | 21.9458 | 29.7253 | 28.7168 | 27.8295 | 27.1168 | 26.1768 | 25.2463 | 24.3011 | 23.22 | 22.2768 | 19.8484 | 18.6242 | 17.1758 | 30.4716 | 29.6084 | 28.7232 | 28.0105 | 27.0726 | 26.1442 | 25.2011 | 24.1221 | 23.1811 | 20.7568 | 19.5358 | 18.0905
|  | FULSCOT PRIMARY | HE |  |  |  |  | 32.7363 | 32.5216 | 32.0637 | 31.5268 | 30.8626 | 30.2289 | 29.5247 | 28.7289 | 28.0553 | 27.2721 | 26.8837 | 26.51 | 29.9884 | 29.1337 | 28.4063 | 27.8179 | 27.0979 | 26.4063 | 25.6284 | 24.7463 | 24.0074 | 23.0821 | 22.6379 | 22.2053 | 30.5158 | 30.0242 | 29.2979 | 28.7105 | 27.9916 | 27.3011 | 26.5253 | 25.6453 | 24.9063 | 23.9842 | 23.5421 | 23.1105
|  | FULSCOT PRIMARY | FB |  |  |  |  | 32.7647 | 32.6511 | 32.5553 | 32.4574 | 32.3511 | 32.2068 | 31.8816 | 31.5026 | 31.1668 | 30.2016 | 29.6616 | 29.21 | 30.1547 | 29.6695 | 29.3168 | 29.0463 | 28.7568 | 28.5716 | 28.2032 | 27.7716 | 27.3926 | 26.3137 | 25.7095 | 25.1989 | 30.5337 | 30.4526 | 30.22 | 29.9495 | 29.6611 | 29.4632 | 29.0958 | 28.6653 | 28.2863 | 27.2105 | 26.6074 | 26.0979
COWLEY GSP | WITNEY BSP | FYFIELD PRIMARY | MINIMUM HEADROOM | SU 42256 99551 | NO | YES | 0 | 13.8329 | 13.6445 | 13.4108 | 13.1276 | 12.7813 | 12.4171 | 12.1729 | 11.9308 | 11.6876 | 10.6034 | 10.1803 | 9.6234 | 15.0247 | 14.5279 | 13.9363 | 13.2384 | 12.3721 | 11.4837 | 11.1016 | 10.7174 | 10.3205 | 7.5879 | 7.1121 | 6.4742 | 15.8053 | 15.3168 | 14.7263 | 14.0274 | 13.16 | 12.28 | 11.9011 | 11.52 | 11.1253 | 8.4284 | 7.9568 | 7.3263
|  | FYFIELD PRIMARY | EE |  |  |  |  | 13.8371 | 13.6476 | 13.4403 | 13.1813 | 12.8508 | 12.5361 | 12.3434 | 12.1508 | 11.9624 | 10.6034 | 10.1803 | 9.6234 | 15.0563 | 14.5795 | 14.0363 | 13.3963 | 12.6426 | 11.9016 | 11.6226 | 11.3658 | 11.1163 | 7.5879 | 7.1121 | 6.4742 | 15.8368 | 15.3674 | 14.8263 | 14.1853 | 13.4284 | 12.6916 | 12.4147 | 12.16 | 11.9116 | 8.4284 | 7.9568 | 7.3263
|  | FYFIELD PRIMARY | HT |  |  |  |  | 13.8329 | 13.6445 | 13.4108 | 13.1276 | 12.7813 | 12.4171 | 12.1729 | 11.9308 | 11.6876 | 11.0929 | 10.6824 | 10.2508 | 15.0247 | 14.5279 | 13.9363 | 13.2384 | 12.3721 | 11.4837 | 11.1016 | 10.7174 | 10.3205 | 9.2858 | 8.4416 | 7.3795 | 15.8053 | 15.3168 | 14.7263 | 14.0274 | 13.16 | 12.28 | 11.9011 | 11.52 | 11.1253 | 10.0979 | 9.26 | 8.2084
|  | FYFIELD PRIMARY | HE |  |  |  |  | 13.9003 | 13.7361 | 13.5455 | 13.3034 | 12.9876 | 12.6929 | 12.5097 | 12.3297 | 12.1529 | 11.3308 | 11.0876 | 10.6834 | 15.2132 | 14.7995 | 14.3068 | 13.7111 | 12.9921 | 12.2932 | 12.0521 | 11.8363 | 11.6247 | 8.3995 | 8.1205 | 7.65 | 15.9916 | 15.5842 | 15.0979 | 14.5011 | 13.78 | 13.0811 | 12.8411 | 12.6253 | 12.4147 | 9.2326 | 8.9568 | 8.4926
|  | FYFIELD PRIMARY | FB |  |  |  |  | 14.0045 | 13.9161 | 13.8318 | 13.7361 | 13.6318 | 13.5224 | 13.4613 | 13.4066 | 13.3497 | 13.1266 | 12.9782 | 12.8403 | 15.4542 | 15.2153 | 14.9837 | 14.7216 | 14.4353 | 14.1279 | 14.0216 | 13.9311 | 13.8384 | 13.4595 | 13.1363 | 12.7447 | 16.2284 | 15.9937 | 15.7653 | 15.5084 | 15.2274 | 14.9179 | 14.8116 | 14.7211 | 14.6284 | 14.2495 | 13.9242 | 13.5316
LOVEDEAN GSP | HAVANT BSP | GABLE HEAD PRIMARY | MINIMUM HEADROOM | SZ 72204 99904 | NO | YES | 0 | 32.5584 | 32.3268 | 31.8542 | 31.1532 | 30.3774 | 29.5563 | 28.7384 | 27.8837 | 27.01 | 24.6974 | 23.1353 | 21.4047 | 26.3495 | 26.1253 | 25.8526 | 25.4779 | 24.8779 | 23.9842 | 23.0958 | 22.1611 | 21.2032 | 18.6495 | 16.9137 | 14.9642 | 26.7842 | 26.3747 | 25.8516 | 25.0726 | 24.2147 | 23.3232 | 22.4347 | 21.5011 | 20.5442 | 17.9937 | 16.2611 | 14.3158
|  | GABLE HEAD PRIMARY | EE |  |  |  |  | 32.5584 | 32.3268 | 31.8995 | 31.3774 | 30.8026 | 30.2932 | 29.7837 | 29.2563 | 28.7132 | 27.5721 | 26.5679 | 25.3879 | 26.3495 | 26.1253 | 25.8737 | 25.5432 | 25.1147 | 24.7116 | 24.3105 | 23.7505 | 23.1747 | 21.8779 | 20.74 | 19.3821 | 26.7842 | 26.3747 | 25.9042 | 25.3358 | 24.7253 | 24.1895 | 23.6484 | 23.0874 | 22.5126 | 21.2179 | 20.08 | 18.7263
|  | GABLE HEAD PRIMARY | HT |  |  |  |  | 32.5626 | 32.3742 | 31.8542 | 31.1532 | 30.3774 | 29.5563 | 28.7384 | 27.8837 | 27.01 | 24.6974 | 23.1353 | 21.4047 | 26.3642 | 26.1453 | 25.8526 | 25.4779 | 24.8779 | 23.9842 | 23.0958 | 22.1611 | 21.2032 | 18.6495 | 16.9137 | 14.9642 | 26.8621 | 26.4389 | 25.8516 | 25.0726 | 24.2147 | 23.3232 | 22.4347 | 21.5011 | 20.5442 | 17.9937 | 16.2611 | 14.3158
|  | GABLE HEAD PRIMARY | HE |  |  |  |  | 32.6089 | 32.4258 | 32.2216 | 31.8911 | 31.3711 | 30.9268 | 30.4963 | 30.0479 | 29.5868 | 29.0963 | 28.4984 | 27.6584 | 26.4326 | 26.2347 | 26.0095 | 25.7011 | 25.2916 | 24.9189 | 24.5547 | 24.1821 | 23.8137 | 23.5968 | 22.9011 | 21.9179 | 27.0821 | 26.7863 | 26.42 | 25.9368 | 25.3884 | 24.9274 | 24.4811 | 24.0137 | 23.5305 | 22.9337 | 22.2389 | 21.2579
|  | GABLE HEAD PRIMARY | FB |  |  |  |  | 32.7458 | 32.6563 | 32.5753 | 32.4837 | 32.3837 | 32.2332 | 32.0616 | 31.8953 | 31.71 | 30.9247 | 30.2489 | 29.4742 | 26.5832 | 26.4747 | 26.38 | 26.2716 | 26.1579 | 26.0432 | 25.9347 | 25.8305 | 25.7189 | 25.2926 | 24.7263 | 23.8358 | 27.3253 | 27.0947 | 26.9021 | 26.6842 | 26.4716 | 26.2789 | 26.0916 | 25.9095 | 25.7063 | 24.8347 | 24.0642 | 23.1758
MINETY GSP |  | GALILEO PRIMARY | MINIMUM HEADROOM | SU 10596 83733 | NO | YES | 0 | 50.2653 | 50.1947 | 50.1126 | 49.9947 | 49.8547 | 49.7 | 49.1158 | 48.4558 | 47.9126 | 47.2305 | 46.5874 | 45.9695 | 47.8768 | 47.6495 | 47.4042 | 47.2358 | 46.8558 | 46.3295 | 45.5621 | 44.8053 | 44.1853 | 43.46 | 42.7347 | 42.0358 | 45.7589 | 45.5737 | 45.3674 | 45.2158 | 44.8916 | 44.4579 | 43.8442 | 43.2389 | 42.7368 | 42.1463 | 41.5495 | 40.9779
|  | GALILEO PRIMARY | EE |  |  |  |  | 50.2653 | 50.1947 | 50.1137 | 50.0126 | 49.8747 | 49.7411 | 49.6179 | 49.0632 | 48.5684 | 47.4968 | 47.0484 | 46.6253 | 47.8768 | 47.7263 | 47.4042 | 47.2358 | 47.0421 | 46.6916 | 46.1642 | 45.5105 | 44.9453 | 43.7137 | 43.2011 | 42.7116 | 45.7589 | 45.6284 | 45.3674 | 45.2158 | 45.0358 | 44.74 | 44.3137 | 43.7905 | 43.3358 | 42.42 | 42.0084 | 41.6211
|  | GALILEO PRIMARY | HT |  |  |  |  | 50.2747 | 50.2053 | 50.1126 | 49.9947 | 49.8547 | 49.7 | 49.1158 | 48.4558 | 47.9126 | 47.2305 | 46.5874 | 45.9695 | 47.9147 | 47.6495 | 47.4895 | 47.3095 | 46.8558 | 46.3295 | 45.5621 | 44.8053 | 44.1853 | 43.46 | 42.7347 | 42.0358 | 45.7905 | 45.5737 | 45.4305 | 45.2663 | 44.8916 | 44.4579 | 43.8442 | 43.2389 | 42.7368 | 42.1463 | 41.5495 | 40.9779
|  | GALILEO PRIMARY | HE |  |  |  |  | 50.3011 | 50.2411 | 50.1684 | 50.0726 | 49.9389 | 49.8137 | 49.6926 | 49.3316 | 48.8411 | 47.9526 | 47.6368 | 47.3284 | 48.0042 | 47.9032 | 47.6211 | 47.4863 | 47.3147 | 46.9832 | 46.4674 | 45.8158 | 45.2537 | 44.2032 | 43.8358 | 43.4737 | 45.8642 | 45.7726 | 45.5432 | 45.4179 | 45.2558 | 44.9768 | 44.56 | 44.0389 | 43.5874 | 42.7895 | 42.5021 | 42.2242
|  | GALILEO PRIMARY | FB |  |  |  |  | 50.3411 | 50.3063 | 50.2758 | 50.2411 | 50.2032 | 50.1642 | 50.1263 | 50.0916 | 50.0547 | 49.3842 | 49.0579 | 48.7874 | 48.0853 | 47.9968 | 47.9316 | 47.7916 | 47.7179 | 47.6411 | 47.4947 | 47.2958 | 47.0779 | 45.8105 | 45.4358 | 45.1242 | 45.9347 | 45.86 | 45.8032 | 45.6895 | 45.6242 | 45.5579 | 45.4379 | 45.2811 | 45.1084 | 44.1232 | 43.8232 | 43.5768
LOVEDEAN GSP | PORTSMOUTH BSP | GAMBLE ROAD PRIMARY | MINIMUM HEADROOM | SU 64771 01769 | NO | YES | 0 | 34.3805 | 33.7563 | 32.8868 | 31.7858 | 30.2026 | 28.4395 | 26.6511 | 24.8016 | 22.9511 | 16.7174 | 14.79 | 13.0816 | 25.9547 | 25.2095 | 24.1768 | 22.8726 | 20.9768 | 18.8663 | 16.7253 | 14.5084 | 12.2895 | 4.7189 | 2.4695 | 0.47789 | 32.1295 | 31.5337 | 30.7063 | 29.6579 | 28.1516 | 26.4768 | 24.7768 | 22.9632 | 20.7811 | 13.1821 | 10.9274 | 8.9295
|  | GAMBLE ROAD PRIMARY | EE |  |  |  |  | 34.3805 | 33.9574 | 33.1553 | 32.2026 | 31.0742 | 29.5532 | 28.0047 | 26.4342 | 24.8721 | 18.9068 | 17.4763 | 16.2879 | 25.9547 | 25.4726 | 24.5232 | 23.4032 | 22.0926 | 20.2853 | 18.4347 | 16.5653 | 14.7021 | 7.3011 | 5.5895 | 4.1632 | 32.1295 | 31.72 | 30.9558 | 30.0453 | 28.9621 | 27.5147 | 26.04 | 24.5463 | 23.06 | 15.7716 | 14.0547 | 12.6242
|  | GAMBLE ROAD PRIMARY | HT |  |  |  |  | 34.4637 | 33.7563 | 32.8868 | 31.7858 | 30.2026 | 28.4395 | 26.6511 | 24.8016 | 22.9511 | 16.7174 | 14.79 | 13.0816 | 26.0526 | 25.2095 | 24.1768 | 22.8726 | 20.9768 | 18.8663 | 16.7253 | 14.5084 | 12.2895 | 4.7189 | 2.4695 | 0.47789 | 32.2074 | 31.5337 | 30.7063 | 29.6579 | 28.1516 | 26.4768 | 24.7768 | 22.9632 | 20.7811 | 13.1821 | 10.9274 | 8.9295
|  | GAMBLE ROAD PRIMARY | HE |  |  |  |  | 34.5942 | 34.2405 | 33.5742 | 32.7521 | 31.7405 | 30.6016 | 29.4637 | 28.3111 | 27.1711 | 22.0932 | 19.6995 | 18.9521 | 26.2179 | 25.8284 | 25.0526 | 24.1032 | 22.9484 | 21.6242 | 20.2989 | 18.9568 | 17.6284 | 11.2453 | 8.2621 | 7.34 | 32.3295 | 31.9853 | 31.3474 | 30.5568 | 29.5821 | 28.4895 | 27.3989 | 26.2937 | 25.2011 | 19.7337 | 16.7379 | 15.8126
|  | GAMBLE ROAD PRIMARY | FB |  |  |  |  | 34.8374 | 34.5774 | 34.3816 | 34.0195 | 33.6068 | 33.1647 | 32.6384 | 32.0911 | 31.5058 | 28.4342 | 25.4153 | 24.61 | 26.4874 | 26.1916 | 25.9737 | 25.5495 | 25.0653 | 24.5453 | 23.9179 | 23.2611 | 22.5589 | 18.8232 | 15.0989 | 14.1326 | 32.5663 | 32.3158 | 32.1253 | 31.7789 | 31.3842 | 30.9621 | 30.4621 | 29.9411 | 29.3853 | 26.4821 | 23.5558 | 22.6074
IVER 132KV GSP | DENHAM BSP | GERRARDS CROSS PRIMARY | MINIMUM HEADROOM | SU 99973 87964 | NO | NO | 0 | 15.2009 | 15.0809 | 14.9314 | 14.7367 | 38.4705 | 37.9947 | 37.5116 | 37.0158 | 36.5221 | 33.1221 | 30.4242 | 28.9232 | 14.6808 | 14.5608 | 14.4113 | 14.2166 | 35.7832 | 35.2253 | 34.6547 | 34.0642 | 33.4768 | 28.9705 | 25.3326 | 23.3537 | 15.6705 | 15.5421 | 15.3853 | 15.1768 | 37.3811 | 36.8189 | 36.2453 | 35.6505 | 35.0579 | 30.5421 | 26.9158 | 24.9411
|  | GERRARDS CROSS PRIMARY | EE |  |  |  |  | 15.2009 | 15.0809 | 14.943 | 14.7599 | 39.7674 | 39.4726 | 39.1684 | 38.8526 | 38.5463 | 37.0863 | 35.9368 | 34.5874 | 14.6808 | 14.5608 | 14.4229 | 14.2387 | 37.5716 | 37.2558 | 36.9189 | 36.5705 | 36.2316 | 34.2768 | 32.7432 | 30.9074 | 15.6705 | 15.5421 | 15.3947 | 15.2042 | 39.1589 | 38.8547 | 38.5337 | 38.1853 | 37.8453 | 35.8695 | 34.3179 | 32.4747
|  | GERRARDS CROSS PRIMARY | HT |  |  |  |  | 15.202 | 15.0862 | 14.9314 | 14.7367 | 38.4705 | 37.9947 | 37.5116 | 37.0158 | 36.5221 | 33.1221 | 30.4242 | 28.9232 | 14.6818 | 14.5661 | 14.4113 | 14.2166 | 35.7832 | 35.2253 | 34.6547 | 34.0642 | 33.4768 | 28.9705 | 25.3326 | 23.3537 | 15.6737 | 15.5495 | 15.3853 | 15.1768 | 37.3811 | 36.8189 | 36.2453 | 35.6505 | 35.0579 | 30.5421 | 26.9158 | 24.9411
|  | GERRARDS CROSS PRIMARY | HE |  |  |  |  | 15.2304 | 15.1178 | 14.9914 | 14.8167 | 40.0716 | 39.8158 | 39.5516 | 39.2779 | 39.0116 | 37.9 | 36.9726 | 35.8063 | 14.7103 | 14.5976 | 14.4713 | 14.2966 | 37.9653 | 37.6968 | 37.4158 | 37.1221 | 36.8368 | 35.2937 | 34.0221 | 32.4158 | 15.7084 | 15.5916 | 15.4589 | 15.2811 | 39.5105 | 39.2484 | 38.9758 | 38.6916 | 38.4158 | 36.8947 | 35.6084 | 33.9832
|  | GERRARDS CROSS PRIMARY | FB |  |  |  |  | 15.3209 | 15.2693 | 15.222 | 15.1693 | 41.0979 | 41.0389 | 40.9811 | 40.9274 | 40.8705 | 40.66 | 39.7326 | 38.6158 | 14.8008 | 14.7492 | 14.7018 | 14.6492 | 39.0653 | 39.0063 | 38.9484 | 38.8947 | 38.8379 | 38.6274 | 37.5063 | 35.9926 | 15.8032 | 15.7463 | 15.6958 | 15.6389 | 40.8768 | 40.8137 | 40.7526 | 40.6958 | 40.6347 | 40.3168 | 39.1095 | 37.5926
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM PRIMARY | MINIMUM HEADROOM | ST 80185 25765 | NO | YES | 0 | 30.6358 | 30.5274 | 30.3926 | 30.2042 | 29.9768 | 29.7274 | 29.4811 | 29.22 | 28.9611 | 28.2821 | 27.8158 | 27.4032 | 29.6884 | 29.5695 | 29.4211 | 29.2116 | 28.9589 | 28.6832 | 28.4105 | 28.1221 | 27.8337 | 27.0758 | 26.5537 | 26.0884 | 29.6884 | 29.5705 | 29.4211 | 29.2126 | 28.9611 | 28.6863 | 28.4137 | 28.1253 | 27.8379 | 27.0811 | 26.5589 | 26.0947
|  | GILLINGHAM PRIMARY | EE |  |  |  |  | 30.6358 | 30.5274 | 30.4126 | 30.2768 | 30.1147 | 29.9621 | 29.7979 | 29.6347 | 29.4758 | 29.0884 | 28.7463 | 28.4474 | 29.6884 | 29.5695 | 29.4432 | 29.2979 | 29.1242 | 28.9611 | 28.7853 | 28.6084 | 28.4358 | 27.9937 | 27.6042 | 27.26 | 29.6884 | 29.5705 | 29.4442 | 29.2979 | 29.1253 | 28.9621 | 28.7853 | 28.6084 | 28.4368 | 27.9926 | 27.6032 | 27.26
|  | GILLINGHAM PRIMARY | HT |  |  |  |  | 30.6516 | 30.54 | 30.3926 | 30.2042 | 29.9768 | 29.7274 | 29.4811 | 29.22 | 28.9611 | 28.2821 | 27.8158 | 27.4032 | 29.7063 | 29.5832 | 29.4211 | 29.2116 | 28.9589 | 28.6832 | 28.4105 | 28.1221 | 27.8337 | 27.0758 | 26.5537 | 26.0884 | 29.7063 | 29.5832 | 29.4211 | 29.2126 | 28.9611 | 28.6863 | 28.4137 | 28.1253 | 27.8379 | 27.0811 | 26.5589 | 26.0947
|  | GILLINGHAM PRIMARY | HE |  |  |  |  | 30.6989 | 30.6168 | 30.5211 | 30.4042 | 30.2526 | 30.1137 | 29.9789 | 29.8421 | 29.7116 | 29.5221 | 29.2989 | 29.1 | 29.76 | 29.6705 | 29.5684 | 29.4432 | 29.2821 | 29.1347 | 28.9916 | 28.8463 | 28.7084 | 28.4842 | 28.2242 | 27.9926 | 29.7611 | 29.6716 | 29.5695 | 29.4442 | 29.2832 | 29.1368 | 28.9937 | 28.8484 | 28.7095 | 28.4863 | 28.2274 | 27.9958
|  | GILLINGHAM PRIMARY | FB |  |  |  |  | 30.7589 | 30.7011 | 30.6526 | 30.6 | 30.5453 | 30.4874 | 30.4305 | 30.3726 | 30.3179 | 30.0726 | 29.8505 | 29.6516 | 29.8253 | 29.76 | 29.7063 | 29.6484 | 29.5895 | 29.5263 | 29.4632 | 29.4 | 29.3389 | 29.0663 | 28.8137 | 28.5853 | 29.8253 | 29.76 | 29.7074 | 29.6495 | 29.5895 | 29.5274 | 29.4642 | 29.4011 | 29.34 | 29.0684 | 28.8168 | 28.5884
FLEET-BRAMLEY GSP | ALDERSHOT BSP | GODALMING PRIMARY | MINIMUM HEADROOM | SU 96743 44375 | NO | YES | 0.018947 | 34.4647 | 34.2237 | 33.9205 | 33.5153 | 32.7921 | 31.5711 | 30.2184 | 28.7679 | 27.2816 | 24.3879 | 22.7374 | 21.2532 | 30.4389 | 29.9126 | 29.0747 | 28.06 | 26.8358 | 25.4042 | 23.8463 | 22.2168 | 20.5453 | 17.32 | 15.4863 | 13.8368 | 32.0663 | 31.7842 | 30.9611 | 29.9632 | 28.76 | 27.3537 | 25.8158 | 24.1863 | 22.5147 | 19.2884 | 17.4537 | 15.8032
|  | GODALMING PRIMARY | EE |  |  |  |  | 34.4647 | 34.2237 | 33.9437 | 33.5868 | 33.1153 | 32.6532 | 32.2226 | 31.7774 | 31.3384 | 30.3574 | 29.29 | 28.3174 | 30.4389 | 29.9705 | 29.3947 | 28.8474 | 28.2221 | 27.6126 | 27.0021 | 26.3632 | 25.6989 | 24.2874 | 22.9895 | 21.8789 | 32.0663 | 31.8263 | 31.2726 | 30.7316 | 30.1105 | 29.5042 | 28.8979 | 28.2653 | 27.6074 | 26.2242 | 24.9537 | 23.8484
|  | GODALMING PRIMARY | HT |  |  |  |  | 34.4816 | 34.2395 | 33.9205 | 33.5153 | 32.7921 | 31.5711 | 30.2184 | 28.7679 | 27.2816 | 24.3879 | 22.7374 | 21.2532 | 30.5105 | 29.9126 | 29.0747 | 28.06 | 26.8358 | 25.4042 | 23.8463 | 22.2168 | 20.5453 | 17.32 | 15.4863 | 13.8368 | 32.0821 | 31.7842 | 30.9611 | 29.9632 | 28.76 | 27.3537 | 25.8158 | 24.1863 | 22.5147 | 19.2884 | 17.4537 | 15.8032
|  | GODALMING PRIMARY | HE |  |  |  |  | 34.5395 | 34.3142 | 34.0511 | 33.7058 | 33.2384 | 32.7995 | 32.3721 | 31.9374 | 31.5089 | 31.4763 | 31.2468 | 30.6942 | 30.7747 | 30.4316 | 29.9642 | 29.5063 | 28.9389 | 28.4053 | 27.8937 | 27.3568 | 26.7937 | 26.14 | 25.3305 | 24.6326 | 32.1368 | 31.9137 | 31.6526 | 31.3084 | 30.8095 | 30.2789 | 29.7705 | 29.2358 | 28.6758 | 28.04 | 27.2495 | 26.5695
|  | GODALMING PRIMARY | FB |  |  |  |  | 34.7121 | 34.5963 | 34.4911 | 34.3774 | 34.2511 | 34.1268 | 34.0047 | 33.89 | 33.7668 | 33.3037 | 33.0216 | 32.4679 | 30.9895 | 30.7947 | 30.5516 | 30.3358 | 30.1084 | 29.8853 | 29.6684 | 29.4558 | 29.2147 | 28.1821 | 27.2653 | 26.4726 | 32.3084 | 32.1947 | 32.0916 | 31.9789 | 31.8547 | 31.7316 | 31.5411 | 31.3305 | 31.0926 | 30.0768 | 29.1779 | 28.4011
WILLESDEN GSP | ACTON LANE BSP | GOLDSMITHS PRIMARY | MINIMUM HEADROOM | TQ 21089 80758 | NO | NO | 0 | 14.6021 | 14.5305 | 14.4526 | 14.34 | 13.7337 | 11.4274 | 8.7589 | 6.16 | 4.8684 | 2.5263 | 1.9621 | 0.78842 | 13.7358 | 13.46 | 13.2474 | 13.0611 | 10.6821 | 7.8611 | 4.74 | 1.7063 | 0.47263 | -2.2084 | -2.8274 | -4.4189 | 14.0221 | 13.7537 | 13.5463 | 13.3632 | 11.0653 | 8.34 | 5.3263 | 2.3979 | 1.4411 | -1.1568 | -1.7632 | -3.5442
|  | GOLDSMITHS PRIMARY | EE |  |  |  |  | 14.6021 | 14.5305 | 14.4589 | 14.3568 | 14.2084 | 14.0484 | 12.9253 | 10.5863 | 8.4526 | 3.9168 | 3.5326 | 3.2095 | 13.7358 | 13.5737 | 13.2474 | 13.0611 | 12.8389 | 11.4305 | 9.7295 | 6.9116 | 4.4168 | -0.63579 | -1.0621 | -1.4242 | 14.0221 | 13.8632 | 13.5463 | 13.3632 | 13.1432 | 11.7811 | 10.1368 | 7.4158 | 5.0074 | 0.36947 | -0.045263 | -0.39684
|  | GOLDSMITHS PRIMARY | HT |  |  |  |  | 14.6053 | 14.54 | 14.4526 | 14.34 | 13.7337 | 11.4274 | 8.7589 | 6.16 | 4.8684 | 2.5263 | 1.9621 | 0.78842 | 13.7547 | 13.46 | 13.2853 | 13.0821 | 10.6821 | 7.8611 | 4.74 | 1.7063 | 0.47263 | -2.2084 | -2.8274 | -4.4189 | 14.0411 | 13.7537 | 13.5821 | 13.3821 | 11.0653 | 8.34 | 5.3263 | 2.3979 | 1.4411 | -1.1568 | -1.7632 | -3.5442
|  | GOLDSMITHS PRIMARY | HE |  |  |  |  | 14.6147 | 14.5442 | 14.4705 | 14.3663 | 14.2105 | 14.0674 | 13.0579 | 10.7547 | 8.6568 | 4.4968 | 3.3158 | 3.1611 | 13.8453 | 13.7253 | 13.4326 | 13.2747 | 13.0695 | 11.6326 | 9.8979 | 7.1116 | 4.66 | 0.023158 | -1.7379 | -1.9137 | 14.1284 | 14.0095 | 13.7253 | 13.5695 | 13.3663 | 11.9758 | 10.2989 | 7.6095 | 5.2411 | 1.0105 | -1.0453 | -1.2158
|  | GOLDSMITHS PRIMARY | FB |  |  |  |  | 14.6516 | 14.6042 | 14.5621 | 14.5147 | 14.4621 | 14.4084 | 14.3568 | 14.3095 | 13.8937 | 9.2158 | 8.6389 | 8.4074 | 13.9253 | 13.8158 | 13.7316 | 13.5705 | 13.4747 | 13.3768 | 12.7526 | 12.0979 | 10.8705 | 5.2484 | 4.5874 | 4.3274 | 14.1895 | 14.0989 | 14.0158 | 13.86 | 13.7653 | 13.6695 | 13.0653 | 12.4326 | 11.2484 | 5.8232 | 5.1821 | 4.9284
NURSLING GSP | WINCHESTER BSP | GORDON ROAD PRIMARY | MINIMUM HEADROOM | SU 48217 29991 | NO | YES | 0 | 34.5574 | 34.4216 | 33.8574 | 32.9416 | 31.7132 | 30.3921 | 29.2595 | 28.13 | 26.9847 | 24.4868 | 23.0321 | 21.7089 | 30.7674 | 30.5884 | 29.9474 | 29.1937 | 27.7905 | 26.2832 | 24.9979 | 23.7158 | 22.4147 | 19.5842 | 17.9432 | 16.4516 | 30.9168 | 30.7811 | 30.6347 | 30.4284 | 30.0947 | 28.5947 | 27.3105 | 26.0284 | 24.7263 | 21.8958 | 20.2547 | 18.7611
|  | GORDON ROAD PRIMARY | EE |  |  |  |  | 34.5574 | 34.4216 | 33.8574 | 33.0363 | 31.9984 | 30.9784 | 30.1732 | 29.4258 | 28.6805 | 27.1132 | 26.0205 | 25.0763 | 30.7674 | 30.5884 | 29.9474 | 29.3042 | 28.1305 | 26.9768 | 26.0705 | 25.2358 | 24.4011 | 22.5905 | 21.3389 | 20.2537 | 30.9168 | 30.7811 | 30.6347 | 30.4316 | 30.1453 | 29.2895 | 28.3832 | 27.5484 | 26.7137 | 24.9011 | 23.6484 | 22.5621
|  | GORDON ROAD PRIMARY | HT |  |  |  |  | 34.5679 | 34.4437 | 33.8942 | 32.9416 | 31.7132 | 30.3921 | 29.2595 | 28.13 | 26.9847 | 24.4868 | 23.0321 | 21.7089 | 30.7842 | 30.6179 | 29.9653 | 29.1937 | 27.7905 | 26.2832 | 24.9979 | 23.7158 | 22.4147 | 19.5842 | 17.9432 | 16.4516 | 30.9284 | 30.8042 | 30.6389 | 30.4284 | 30.0947 | 28.5947 | 27.3105 | 26.0284 | 24.7263 | 21.8958 | 20.2547 | 18.7611
|  | GORDON ROAD PRIMARY | HE |  |  |  |  | 34.5795 | 34.4426 | 34.1279 | 33.3458 | 32.3258 | 31.3426 | 30.6184 | 29.9542 | 29.2942 | 28.37 | 27.6511 | 27.03 | 30.8063 | 30.6316 | 30.0768 | 29.6168 | 28.5168 | 27.4042 | 26.5958 | 25.8589 | 25.1263 | 24.0316 | 23.1958 | 22.4705 | 30.94 | 30.8032 | 30.6547 | 30.4484 | 30.1505 | 29.7116 | 28.9095 | 28.1726 | 27.44 | 26.3453 | 25.5084 | 24.7832
|  | GORDON ROAD PRIMARY | FB |  |  |  |  | 34.6763 | 34.6037 | 34.5395 | 34.4668 | 34.3858 | 34.3047 | 34.2258 | 34.1521 | 33.8753 | 32.9079 | 32.2016 | 31.5742 | 30.9232 | 30.8284 | 30.7411 | 30.64 | 30.5253 | 30.4074 | 30.2147 | 30.0347 | 29.8421 | 29.2042 | 28.4 | 27.6789 | 31.0368 | 30.9642 | 30.9 | 30.8274 | 30.7463 | 30.6653 | 30.5863 | 30.5126 | 30.4337 | 30.1453 | 29.9821 | 29.8779
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | GORING PRIMARY | MINIMUM HEADROOM | SU 60305 82895 | NO | YES | 0 | 10.7789 | 10.6947 | 10.6011 | 10.4811 | 10.3347 | 10.1832 | 10.0368 | 9.8905 | 9.7421 | 9.3558 | 9.1063 | 8.8442 | 15.8 | 15.7495 | 15.66 | 15.5158 | 15.3379 | 15.1568 | 14.9863 | 14.8126 | 14.6347 | 14.1495 | 13.8316 | 13.4811 | 10.5663 | 10.48 | 10.3832 | 10.2611 | 10.1105 | 9.9558 | 9.8074 | 9.6579 | 9.5053 | 9.1084 | 8.8505 | 8.5789
|  | GORING PRIMARY | EE |  |  |  |  | 10.7789 | 10.6947 | 10.6053 | 10.5021 | 10.3768 | 10.2558 | 10.1358 | 10.0147 | 9.8926 | 9.72 | 9.5726 | 9.4411 | 15.8 | 15.7495 | 15.6653 | 15.5442 | 15.4053 | 15.2705 | 15.1326 | 14.9937 | 14.8537 | 14.6116 | 14.4063 | 14.2168 | 10.5663 | 10.48 | 10.3884 | 10.2832 | 10.1568 | 10.0337 | 9.9116 | 9.7884 | 9.6642 | 9.4821 | 9.3295 | 9.1905
|  | GORING PRIMARY | HT |  |  |  |  | 10.7821 | 10.7 | 10.6011 | 10.4811 | 10.3347 | 10.1832 | 10.0368 | 9.8905 | 9.7421 | 9.3558 | 9.1063 | 8.8442 | 15.8011 | 15.7526 | 15.66 | 15.5158 | 15.3379 | 15.1568 | 14.9863 | 14.8126 | 14.6347 | 14.1495 | 13.8316 | 13.4811 | 10.5705 | 10.4863 | 10.3832 | 10.2611 | 10.1105 | 9.9558 | 9.8074 | 9.6579 | 9.5053 | 9.1084 | 8.8505 | 8.5789
|  | GORING PRIMARY | HE |  |  |  |  | 10.8168 | 10.7642 | 10.6937 | 10.6053 | 10.4895 | 10.3811 | 10.2747 | 10.1663 | 10.0621 | 10.0095 | 9.9347 | 9.8737 | 15.8137 | 15.7653 | 15.7116 | 15.6389 | 15.5389 | 15.4442 | 15.3389 | 15.2211 | 15.1084 | 15.02 | 14.9063 | 14.8137 | 10.6211 | 10.5537 | 10.4811 | 10.3916 | 10.2758 | 10.1653 | 10.0579 | 9.9495 | 9.8432 | 9.7863 | 9.7074 | 9.6432
|  | GORING PRIMARY | FB |  |  |  |  | 10.8547 | 10.8295 | 10.8053 | 10.7674 | 10.7284 | 10.6884 | 10.6484 | 10.6105 | 10.5726 | 10.42 | 10.2989 | 10.2053 | 15.8495 | 15.8274 | 15.8074 | 15.7853 | 15.76 | 15.7347 | 15.7105 | 15.6768 | 15.6305 | 15.4368 | 15.2705 | 15.1368 | 10.6758 | 10.6295 | 10.5937 | 10.5558 | 10.5158 | 10.4737 | 10.4337 | 10.3947 | 10.3558 | 10.1979 | 10.0716 | 9.9737
IVER 132KV GSP | DENHAM BSP | GRASSINGHAM ROAD PRIMARY | MINIMUM HEADROOM | TQ 00165 90988 | NO | NO | 0 | 18.8602 | 18.7307 | 18.5844 | 18.3875 | 18.1202 | 17.8612 | 17.6191 | 17.3559 | 17.0307 | 15.6391 | 14.7033 | 13.8854 | 18.5938 | 18.4538 | 18.2528 | 17.8665 | 17.358 | 16.7949 | 16.2191 | 15.6065 | 14.998 | 13.4738 | 12.4433 | 11.5423 | 15.7517 | 15.4896 | 15.2244 | 14.8433 | 14.3423 | 13.7865 | 13.2191 | 12.6149 | 12.0159 | 10.5149 | 9.5012 | 8.6149
|  | GRASSINGHAM ROAD PRIMARY | EE |  |  |  |  | 18.8602 | 18.7307 | 18.5844 | 18.3875 | 18.1202 | 17.8612 | 17.6191 | 17.3707 | 17.1265 | 16.937 | 16.5875 | 16.0507 | 18.5938 | 18.4538 | 18.2528 | 17.9465 | 17.5938 | 17.2507 | 16.8717 | 16.4833 | 16.1012 | 15.2675 | 14.5338 | 13.9254 | 15.7517 | 15.4896 | 15.2244 | 14.9212 | 14.5707 | 14.2296 | 13.8549 | 13.4696 | 13.0917 | 12.2738 | 11.5559 | 10.9602
|  | GRASSINGHAM ROAD PRIMARY | HT |  |  |  |  | 18.8675 | 18.7475 | 18.5917 | 18.3917 | 18.1496 | 17.8823 | 17.6191 | 17.3559 | 17.0307 | 15.6391 | 14.7033 | 13.8854 | 18.6054 | 18.4759 | 18.2886 | 17.8665 | 17.358 | 16.7949 | 16.2191 | 15.6065 | 14.998 | 13.4738 | 12.4433 | 11.5423 | 15.8054 | 15.5707 | 15.2602 | 14.8433 | 14.3423 | 13.7865 | 13.2191 | 12.6149 | 12.0159 | 10.5149 | 9.5012 | 8.6149
|  | GRASSINGHAM ROAD PRIMARY | HE |  |  |  |  | 18.877 | 18.7517 | 18.6096 | 18.4149 | 18.1517 | 17.9012 | 17.6559 | 17.4086 | 17.1644 | 17.1907 | 17.1612 | 17.1402 | 18.6233 | 18.4928 | 18.3444 | 18.1454 | 17.878 | 17.6233 | 17.3675 | 17.0475 | 16.7328 | 16.4212 | 16.0117 | 15.678 | 15.9202 | 15.7275 | 15.5191 | 15.2644 | 14.9496 | 14.6496 | 14.338 | 14.0202 | 13.7075 | 13.4044 | 13.0044 | 12.6791
|  | GRASSINGHAM ROAD PRIMARY | FB |  |  |  |  | 18.9823 | 18.9212 | 18.8654 | 18.8044 | 18.7349 | 18.6654 | 18.598 | 18.5359 | 18.4686 | 18.2223 | 18.0854 | 17.998 | 18.7338 | 18.6654 | 18.6054 | 18.5391 | 18.4654 | 18.3907 | 18.3191 | 18.2328 | 18.0991 | 17.5296 | 17.017 | 16.5802 | 16.0928 | 15.9423 | 15.8296 | 15.7096 | 15.5833 | 15.458 | 15.3307 | 15.2044 | 15.0717 | 14.5107 | 14.0075 | 13.5812
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | GREEN PARK PRIMARY | MINIMUM HEADROOM | SU 70508 70222 | NO | YES | 0 | 41.4274 | 41.4274 | 40.8474 | 40.8463 | 40.8453 | 40.8453 | 40.8442 | 40.8442 | 40.8421 | 40.8389 | 40.8347 | 40.8337 | 38.8684 | 38.8684 | 38.2758 | 38.2747 | 38.2737 | 38.2737 | 38.2726 | 38.2716 | 38.2695 | 38.2663 | 38.2611 | 38.26 | 39.3158 | 39.3158 | 38.7863 | 38.7863 | 38.7853 | 38.7842 | 38.7842 | 38.7832 | 38.7811 | 38.7779 | 38.7726 | 38.7716
|  | GREEN PARK PRIMARY | EE |  |  |  |  | 41.4274 | 41.4274 | 40.8474 | 40.8463 | 40.8453 | 40.8453 | 40.8442 | 40.8442 | 40.8421 | 40.8389 | 40.8347 | 40.8337 | 38.8684 | 38.8684 | 38.2758 | 38.2747 | 38.2737 | 38.2737 | 38.2726 | 38.2716 | 38.2695 | 38.2663 | 38.2611 | 38.26 | 39.3158 | 39.3158 | 38.7863 | 38.7863 | 38.7853 | 38.7853 | 38.7842 | 38.7832 | 38.7811 | 38.7779 | 38.7726 | 38.7716
|  | GREEN PARK PRIMARY | HT |  |  |  |  | 41.4274 | 41.4274 | 40.8474 | 40.8474 | 40.8453 | 40.8453 | 40.8453 | 40.8442 | 40.8442 | 40.8389 | 40.8347 | 40.8347 | 38.8684 | 38.8684 | 38.2758 | 38.2758 | 38.2737 | 38.2737 | 38.2737 | 38.2726 | 38.2716 | 38.2663 | 38.2621 | 38.2611 | 39.3158 | 39.3158 | 38.7863 | 38.7863 | 38.7853 | 38.7853 | 38.7853 | 38.7842 | 38.7832 | 38.7779 | 38.7737 | 38.7726
|  | GREEN PARK PRIMARY | HE |  |  |  |  | 41.4274 | 41.4274 | 40.8474 | 40.8474 | 40.8474 | 40.8453 | 40.8453 | 40.8453 | 40.8453 | 40.8453 | 40.8453 | 40.8453 | 38.8684 | 38.8684 | 38.2758 | 38.2758 | 38.2758 | 38.2737 | 38.2737 | 38.2737 | 38.2737 | 38.2737 | 38.2737 | 38.2737 | 39.3158 | 39.3158 | 38.7863 | 38.7863 | 38.7863 | 38.7842 | 38.7842 | 38.7842 | 38.7842 | 38.7853 | 38.7853 | 38.7853
|  | GREEN PARK PRIMARY | FB |  |  |  |  | 41.5432 | 41.5432 | 41.3495 | 41.3495 | 41.3495 | 41.3495 | 41.3495 | 41.3495 | 41.3495 | 41.3484 | 41.3484 | 41.3484 | 38.9705 | 38.9705 | 38.8011 | 38.8011 | 38.8011 | 38.8011 | 38.8011 | 38.8011 | 38.8011 | 38.7989 | 38.7989 | 38.7989 | 39.3263 | 39.3263 | 39.3084 | 39.3084 | 39.3084 | 39.3084 | 39.3084 | 39.3084 | 39.3084 | 39.3074 | 39.3074 | 39.3074
WILLESDEN GSP |  | GREENFORD PRIMARY | MINIMUM HEADROOM | TQ 14695 83785 | NO | NO | 0 | 68.5484 | 68.2579 | 67.9368 | 67.5168 | 66.9632 | 66.4453 | 65.9737 | 65.4768 | 64.9863 | 65.6011 | 64.6516 | 63.8063 | 67.2474 | 66.9853 | 66.7105 | 66.32 | 65.78 | 65.2811 | 64.8305 | 64.3568 | 63.8884 | 64.3621 | 62.9505 | 61.6937 | 65.0168 | 64.7547 | 64.48 | 64.0895 | 63.5495 | 63.0505 | 62.6 | 62.1263 | 61.6579 | 59.0621 | 57.0863 | 55.3253
|  | GREENFORD PRIMARY | EE |  |  |  |  | 68.5484 | 68.2579 | 67.9368 | 67.5326 | 66.9632 | 66.4453 | 65.9737 | 65.4768 | 64.9863 | 66.9621 | 66.4611 | 66.0558 | 67.2474 | 66.9853 | 66.7105 | 66.3305 | 65.78 | 65.2811 | 64.8305 | 64.3568 | 63.8884 | 66.3358 | 65.9095 | 65.5705 | 65.0168 | 64.7547 | 64.48 | 64.1 | 63.5495 | 63.0505 | 62.6 | 62.1263 | 61.6579 | 63.7789 | 62.5368 | 61.4274
|  | GREENFORD PRIMARY | HT |  |  |  |  | 68.5716 | 68.3063 | 67.9432 | 67.5168 | 69.5411 | 68.9832 | 68.3853 | 67.78 | 67.14 | 65.6011 | 64.6516 | 63.8063 | 67.2726 | 67.0358 | 66.7232 | 66.32 | 68.7684 | 68.2326 | 67.6958 | 67.1663 | 66.6379 | 64.3621 | 62.9505 | 61.6937 | 65.0421 | 64.8053 | 64.4926 | 64.0895 | 66.2116 | 65.6758 | 65.1389 | 64.5389 | 62.6916 | 59.0621 | 57.0863 | 55.3253
|  | GREENFORD PRIMARY | HE |  |  |  |  | 68.6442 | 68.3821 | 68.0863 | 67.7053 | 67.1505 | 66.6684 | 66.2 | 65.7116 | 65.2326 | 67.7263 | 67.5495 | 67.4232 | 67.3158 | 67.0716 | 66.8137 | 66.4463 | 65.9053 | 65.4358 | 64.9779 | 64.5021 | 64.0347 | 66.9537 | 66.8179 | 66.7284 | 65.0853 | 64.8411 | 64.5832 | 64.2158 | 63.6747 | 63.2053 | 62.7474 | 62.2716 | 61.8042 | 64.3968 | 64.2611 | 64.1716
|  | GREENFORD PRIMARY | FB |  |  |  |  | 68.7968 | 68.6263 | 68.4653 | 68.2989 | 68.1147 | 67.9295 | 67.7505 | 67.5821 | 67.4032 | 66.7347 | 68.8926 | 68.6232 | 67.4568 | 67.3042 | 67.1653 | 67.0105 | 66.8379 | 66.6642 | 66.4958 | 66.3379 | 66.1705 | 65.5547 | 68.1421 | 67.92 | 65.2263 | 65.0737 | 64.9347 | 64.78 | 64.6074 | 64.4337 | 64.2653 | 64.1074 | 63.94 | 63.3242 | 65.5853 | 65.3632
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET PRIMARY | MINIMUM HEADROOM | SU 64445 00178 | NO | YES | 0 | 28.1153 | 28.0237 | 27.9258 | 27.7679 | 27.3763 | 26.9279 | 26.4763 | 26.0016 | 25.5174 | 24.7384 | 24.1732 | 23.6658 | 30.4211 | 30.3663 | 30.3042 | 30.2168 | 30.0968 | 29.6853 | 29.0189 | 28.3168 | 27.5968 | 26.5053 | 25.7021 | 24.9832 | 31.1579 | 31.0621 | 30.9389 | 30.7347 | 30.1653 | 29.5084 | 28.8432 | 28.1421 | 27.4232 | 26.3316 | 25.5295 | 24.8116
|  | GREETHAM STREET PRIMARY | EE |  |  |  |  | 28.1153 | 28.0237 | 27.9395 | 27.8353 | 27.7089 | 27.3426 | 26.9574 | 26.5679 | 26.1795 | 25.5216 | 25.1005 | 24.7416 | 30.4211 | 30.3695 | 30.3126 | 30.2358 | 30.1305 | 30.0053 | 29.7853 | 29.2137 | 28.6453 | 27.6411 | 27.0126 | 26.4758 | 31.1579 | 31.0621 | 30.9579 | 30.8368 | 30.6958 | 30.1674 | 29.6063 | 29.0379 | 28.4695 | 27.4663 | 26.84 | 26.3032
|  | GREETHAM STREET PRIMARY | HT |  |  |  |  | 28.13 | 28.0374 | 27.9258 | 27.7679 | 27.3763 | 26.9279 | 26.4763 | 26.0016 | 25.5174 | 24.7384 | 24.1732 | 23.6658 | 30.4253 | 30.3737 | 30.3084 | 30.2211 | 30.0968 | 29.6853 | 29.0189 | 28.3168 | 27.5968 | 26.5053 | 25.7021 | 24.9832 | 31.1653 | 31.0821 | 30.9389 | 30.7347 | 30.1653 | 29.5084 | 28.8432 | 28.1421 | 27.4232 | 26.3316 | 25.5295 | 24.8116
|  | GREETHAM STREET PRIMARY | HE |  |  |  |  | 28.1532 | 28.0689 | 27.9911 | 27.8889 | 27.7574 | 27.4837 | 27.2121 | 26.9395 | 26.6679 | 25.9342 | 25.7374 | 25.5037 | 30.4253 | 30.3663 | 30.3042 | 30.2168 | 30.0989 | 29.9768 | 29.8547 | 29.7326 | 29.4853 | 28.2916 | 27.9916 | 27.6253 | 31.1726 | 31.1063 | 31.0389 | 30.9389 | 30.7968 | 30.4232 | 30.0516 | 29.68 | 29.3074 | 28.1168 | 27.8168 | 27.4516
|  | GREETHAM STREET PRIMARY | FB |  |  |  |  | 28.2037 | 28.1437 | 28.0995 | 28.05 | 27.9974 | 27.9374 | 27.8132 | 27.6826 | 27.5437 | 26.8584 | 26.6132 | 26.37 | 30.4611 | 30.4263 | 30.3958 | 30.36 | 30.3221 | 30.2821 | 30.2379 | 30.1958 | 30.1505 | 29.5621 | 29.2084 | 28.8463 | 31.2137 | 31.1705 | 31.1358 | 31.0958 | 31.0484 | 30.9758 | 30.7979 | 30.6095 | 30.4084 | 29.3853 | 29.0326 | 28.6705
COWLEY GSP | DRAYTON BSP | GROVE PRIMARY | MINIMUM HEADROOM | SU 39515 89611 | NO | YES | 0.37895 | 15.7701 | 32.4521 | 31.9416 | 31.0153 | 30.0553 | 28.9826 | 27.9089 | 26.8142 | 25.1089 | 21.9521 | 19.6047 | 18.2005 | 9.2917 | 24.1853 | 23.0084 | 21.8916 | 20.7432 | 19.46 | 18.1737 | 16.8579 | 14.8463 | 11.3095 | 8.6474 | 7.0747 | 14.9208 | 30.3611 | 29.1989 | 28.0958 | 26.9579 | 25.6895 | 24.4179 | 23.1032 | 21.0716 | 17.5011 | 14.8126 | 13.2253
|  | GROVE PRIMARY | EE |  |  |  |  | 15.7701 | 32.4521 | 32.0805 | 31.3089 | 30.3658 | 29.4532 | 28.5447 | 27.65 | 25.1089 | 22.2068 | 20.4626 | 19.6153 | 9.3212 | 24.2589 | 23.1842 | 22.2579 | 21.1379 | 20.0495 | 18.96 | 17.8905 | 14.8463 | 11.5095 | 9.5137 | 8.5526 | 14.9503 | 30.4326 | 29.3716 | 28.4547 | 27.3484 | 26.2726 | 25.1958 | 24.1379 | 21.0716 | 17.6958 | 15.68 | 14.7084
|  | GROVE PRIMARY | HT |  |  |  |  | 15.7785 | 32.4721 | 31.9416 | 31.0153 | 30.0553 | 28.9826 | 27.9089 | 26.8142 | 25.8184 | 21.9521 | 19.6047 | 18.2005 | 9.2917 | 24.1853 | 23.0084 | 21.8916 | 20.7432 | 19.46 | 18.1737 | 16.8579 | 15.6926 | 11.3095 | 8.6474 | 7.0747 | 14.9208 | 30.3611 | 29.1989 | 28.0958 | 26.9579 | 25.6895 | 24.4179 | 23.1032 | 21.9284 | 17.5011 | 14.8126 | 13.2253
|  | GROVE PRIMARY | HE |  |  |  |  | 15.8143 | 32.51 | 32.3732 | 31.6616 | 30.8468 | 29.8858 | 29.03 | 28.1889 | 25.7479 | 23.3037 | 21.8489 | 21.2437 | 9.5369 | 24.5579 | 23.5537 | 22.6853 | 21.7263 | 20.5716 | 19.5495 | 18.5474 | 15.5716 | 12.7326 | 11.0526 | 10.3558 | 15.0556 | 30.7284 | 29.7368 | 28.8789 | 27.9295 | 26.7884 | 25.7768 | 24.7863 | 21.8032 | 18.9316 | 17.2316 | 16.5263
|  | GROVE PRIMARY | FB |  |  |  |  | 15.9037 | 32.6616 | 32.6047 | 32.5416 | 32.4711 | 32.4005 | 32.1037 | 31.6963 | 31.33 | 29.6416 | 28.5268 | 28.03 | 9.9327 | 25.3695 | 24.9453 | 24.5768 | 24.1537 | 23.6947 | 23.2063 | 22.7063 | 22.26 | 20.1863 | 18.8095 | 18.2032 | 15.1451 | 31.4579 | 31.1105 | 30.7474 | 30.3295 | 29.8758 | 29.3947 | 28.9011 | 28.46 | 26.4126 | 25.0547 | 24.4558
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL PRIMARY | MINIMUM HEADROOM | ST 98638 11417 | YES | YES | 0 | 4.7442 | 4.7242 | 4.6958 | 4.6516 | 4.5989 | 4.5421 | 4.4853 | 4.4284 | 4.3726 | 4.2379 | 4.1484 | 4.0642 | 4.9116 | 4.8926 | 4.8674 | 4.8284 | 4.78 | 4.7295 | 4.68 | 4.6284 | 4.5789 | 4.4589 | 4.3789 | 4.3053 | 4.5547 | 4.5347 | 4.5063 | 4.4621 | 4.4084 | 4.3526 | 4.2958 | 4.2379 | 4.1832 | 4.0474 | 3.9568 | 3.8737
|  | GUSSAGE ST MICHAEL PRIMARY | EE |  |  |  |  | 4.7442 | 4.7242 | 4.7011 | 4.6747 | 4.6432 | 4.6116 | 4.5811 | 4.5516 | 4.5211 | 4.4558 | 4.3958 | 4.3421 | 4.9116 | 4.8926 | 4.8716 | 4.8474 | 4.8179 | 4.7884 | 4.76 | 4.7326 | 4.7053 | 4.6484 | 4.5958 | 4.5495 | 4.5547 | 4.5347 | 4.5116 | 4.4853 | 4.4537 | 4.4211 | 4.3905 | 4.3611 | 4.3316 | 4.2653 | 4.2063 | 4.1516
|  | GUSSAGE ST MICHAEL PRIMARY | HT |  |  |  |  | 4.7463 | 4.7242 | 4.6958 | 4.6516 | 4.5989 | 4.5421 | 4.4853 | 4.4284 | 4.3726 | 4.2379 | 4.1484 | 4.0642 | 4.9126 | 4.8926 | 4.8674 | 4.8284 | 4.78 | 4.7295 | 4.68 | 4.6284 | 4.5789 | 4.4589 | 4.3789 | 4.3053 | 4.5568 | 4.5347 | 4.5063 | 4.4621 | 4.4084 | 4.3526 | 4.2958 | 4.2379 | 4.1832 | 4.0474 | 3.9568 | 3.8737
|  | GUSSAGE ST MICHAEL PRIMARY | HE |  |  |  |  | 4.7568 | 4.7411 | 4.7221 | 4.6979 | 4.6684 | 4.6389 | 4.6126 | 4.5842 | 4.5579 | 4.5168 | 4.4726 | 4.4347 | 4.9221 | 4.9074 | 4.8905 | 4.8684 | 4.84 | 4.8126 | 4.7884 | 4.7621 | 4.7368 | 4.7032 | 4.6653 | 4.6337 | 4.5674 | 4.5516 | 4.5326 | 4.5084 | 4.4779 | 4.4495 | 4.4232 | 4.3947 | 4.3684 | 4.3274 | 4.2821 | 4.2453
|  | GUSSAGE ST MICHAEL PRIMARY | FB |  |  |  |  | 4.7674 | 4.7568 | 4.7484 | 4.7389 | 4.7263 | 4.7158 | 4.7063 | 4.6958 | 4.6863 | 4.6368 | 4.5947 | 4.5558 | 4.9316 | 4.9221 | 4.9137 | 4.9063 | 4.8947 | 4.8853 | 4.8768 | 4.8674 | 4.8579 | 4.8147 | 4.7768 | 4.7442 | 4.5779 | 4.5674 | 4.5589 | 4.5495 | 4.5368 | 4.5263 | 4.5168 | 4.5063 | 4.4958 | 4.4474 | 4.4053 | 4.3663
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE PRIMARY | MINIMUM HEADROOM | SU 47370 08794 | NO | YES | 0 | 34.4605 | 34.3521 | 34.2289 | 34.0637 | 33.8437 | 33.6279 | 33.4142 | 33.1879 | 32.7121 | 31.1289 | 30.0132 | 29.0174 | 30.7842 | 30.5684 | 30.3474 | 30.0811 | 29.7126 | 29.32 | 28.8789 | 28.3663 | 27.7905 | 26.1137 | 24.9495 | 23.9095 | 31.7347 | 31.6263 | 31.5032 | 31.3379 | 31.1179 | 30.8147 | 30.4853 | 30.1232 | 29.7316 | 28.66 | 27.9347 | 27.2905
|  | HAMBLE PRIMARY | EE |  |  |  |  | 34.4605 | 34.3521 | 34.2289 | 34.0647 | 33.8437 | 33.6279 | 33.4258 | 33.2195 | 33.0163 | 32.5426 | 31.7658 | 31.0868 | 30.7842 | 30.5684 | 30.3474 | 30.0947 | 29.8 | 29.5105 | 29.2095 | 28.9095 | 28.5821 | 27.6158 | 26.78 | 26.06 | 31.7347 | 31.6263 | 31.5032 | 31.3389 | 31.1179 | 30.9021 | 30.6516 | 30.4 | 30.1347 | 29.5926 | 29.1232 | 28.7232
|  | HAMBLE PRIMARY | HT |  |  |  |  | 34.4668 | 34.3647 | 34.2321 | 34.0637 | 33.8605 | 33.6374 | 33.4142 | 33.1879 | 32.7121 | 31.1289 | 30.0132 | 29.0174 | 30.8274 | 30.6326 | 30.4021 | 30.0811 | 29.7126 | 29.32 | 28.8789 | 28.3663 | 27.7905 | 26.1137 | 24.9495 | 23.9095 | 31.7411 | 31.6389 | 31.5063 | 31.3379 | 31.12 | 30.8147 | 30.4853 | 30.1232 | 29.7316 | 28.66 | 27.9347 | 27.2905
|  | HAMBLE PRIMARY | HE |  |  |  |  | 34.4795 | 34.3742 | 34.2553 | 34.0921 | 33.8711 | 33.6626 | 33.4605 | 33.2532 | 33.0511 | 33.0658 | 32.8068 | 32.3279 | 30.9021 | 30.76 | 30.5853 | 30.3684 | 30.0979 | 29.8411 | 29.5916 | 29.3421 | 29.0663 | 28.4853 | 27.8884 | 27.3684 | 31.7537 | 31.6484 | 31.5295 | 31.3663 | 31.1453 | 30.9368 | 30.7347 | 30.5274 | 30.3253 | 30.1147 | 29.8084 | 29.5463
|  | HAMBLE PRIMARY | FB |  |  |  |  | 34.5616 | 34.5121 | 34.4679 | 34.4174 | 34.3616 | 34.3058 | 34.2511 | 34.2005 | 34.1458 | 33.9458 | 33.8311 | 33.5058 | 30.9989 | 30.9295 | 30.8453 | 30.7474 | 30.6432 | 30.5411 | 30.4389 | 30.3453 | 30.2347 | 29.6053 | 29.0589 | 28.5853 | 31.8358 | 31.7863 | 31.7421 | 31.6916 | 31.6358 | 31.58 | 31.5253 | 31.4747 | 31.42 | 31.1116 | 30.7884 | 30.5211
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | HAMWORTHY PRIMARY | MINIMUM HEADROOM | SZ 00104 90800 | NO | YES | 0 | 25.7884 | 25.5811 | 59.4516 | 59.1316 | 58.3379 | 57.1968 | 55.7116 | 53.66 | 48.9642 | 43.88 | 36.2537 | 26.1042 | 25.3653 | 24.8326 | 54.2084 | 52.9684 | 52.0726 | 50.7811 | 49.1053 | 46.72 | 41.2316 | 35.28 | 26.3421 | 14.4211 | 25.9316 | 25.3979 | 56.5737 | 55.3337 | 54.4379 | 53.1463 | 51.3158 | 48.9305 | 43.4411 | 37.4947 | 28.5842 | 16.6989
|  | HAMWORTHY PRIMARY | EE |  |  |  |  | 25.7884 | 25.5811 | 59.4516 | 59.1421 | 58.3379 | 57.1968 | 56.0568 | 54.5263 | 52.9811 | 43.88 | 36.2537 | 26.1042 | 25.3653 | 24.8326 | 54.3421 | 53.3895 | 52.0726 | 50.7811 | 49.4832 | 47.7168 | 45.9579 | 35.28 | 26.3421 | 14.4211 | 25.9316 | 25.3979 | 56.7074 | 55.7547 | 54.4379 | 53.1463 | 51.8474 | 50.0811 | 48.1684 | 37.4947 | 28.5842 | 16.6989
|  | HAMWORTHY PRIMARY | HT |  |  |  |  | 25.8053 | 25.6095 | 59.4547 | 59.1316 | 58.9737 | 57.3305 | 55.7116 | 53.66 | 48.9642 | 44.9811 | 40.2137 | 30.5526 | 25.4389 | 24.8484 | 54.2084 | 52.9684 | 52.8611 | 50.9674 | 49.1053 | 46.72 | 41.2316 | 36.7253 | 31.2179 | 19.9305 | 26.0053 | 25.4147 | 56.5737 | 55.3337 | 55.0726 | 53.1789 | 51.3158 | 48.9305 | 43.4411 | 38.9337 | 33.4411 | 22.1874
|  | HAMWORTHY PRIMARY | HE |  |  |  |  | 25.8474 | 25.6495 | 59.5284 | 59.2242 | 58.7968 | 57.8284 | 56.7768 | 55.3316 | 53.8726 | 45.5095 | 38.3242 | 28.5516 | 25.6821 | 25.2663 | 54.8747 | 54.0063 | 52.7411 | 51.5221 | 50.3305 | 48.6684 | 47.0126 | 37.1263 | 28.6768 | 17.1737 | 26.2484 | 25.8316 | 57.24 | 56.3716 | 55.1063 | 53.8874 | 52.6958 | 51.0326 | 49.2242 | 39.3379 | 30.9137 | 19.4453
|  | HAMWORTHY PRIMARY | FB |  |  |  |  | 25.9874 | 25.8895 | 59.9011 | 59.8021 | 59.6926 | 59.5821 | 59.4747 | 59.2347 | 58.4863 | 56.4863 | 49.2021 | 40.5516 | 25.9116 | 25.7158 | 55.7979 | 55.44 | 54.9189 | 54.3916 | 53.8368 | 53.0179 | 52.14 | 49.8337 | 41.2295 | 31.0695 | 26.5653 | 26.2821 | 58.1642 | 57.8053 | 57.2842 | 56.7579 | 56.2021 | 55.3832 | 54.5042 | 52.0453 | 43.4379 | 33.3032
IVER 132KV GSP | DENHAM BSP | HAREFIELD PRIMARY | MINIMUM HEADROOM | TQ 04001 91227 | NO | NO | 0 | 14.1611 | 14.1063 | 11.5116 | 11.2589 | 10.9611 | 10.6453 | 10.3326 | 10.0126 | 9.6958 | 8.9158 | 8.4158 | 7.9695 | 13.8147 | 13.7116 | 9.8526 | 9.5705 | 9.2379 | 8.8874 | 8.54 | 8.1832 | 7.8295 | 6.9589 | 6.4 | 5.9 | 12.3411 | 12.2589 | 10.0768 | 9.7937 | 9.4621 | 9.1126 | 8.7653 | 8.4095 | 8.0547 | 7.1863 | 6.6284 | 6.1295
|  | HAREFIELD PRIMARY | EE |  |  |  |  | 14.1611 | 14.1063 | 11.5895 | 11.4358 | 11.2611 | 11.0832 | 10.9011 | 10.72 | 10.5442 | 10.1389 | 9.7968 | 9.4989 | 13.8147 | 13.7337 | 9.9442 | 9.78 | 9.5937 | 9.4032 | 9.2084 | 9.0137 | 8.8253 | 8.3611 | 7.9716 | 7.6295 | 12.3411 | 12.2621 | 10.1674 | 10.0032 | 9.8179 | 9.6274 | 9.4326 | 9.2379 | 9.0495 | 8.5853 | 8.1958 | 7.8547
|  | HAREFIELD PRIMARY | HT |  |  |  |  | 14.1642 | 14.1137 | 11.5116 | 11.2589 | 10.9611 | 10.6453 | 10.3326 | 10.0126 | 9.6958 | 8.9158 | 8.4158 | 7.9695 | 13.8189 | 13.7116 | 9.8526 | 9.5705 | 9.2379 | 8.8874 | 8.54 | 8.1832 | 7.8295 | 6.9589 | 6.4 | 5.9 | 12.3442 | 12.2589 | 10.0768 | 9.7937 | 9.4621 | 9.1126 | 8.7653 | 8.4095 | 8.0547 | 7.1863 | 6.6284 | 6.1295
|  | HAREFIELD PRIMARY | HE |  |  |  |  | 14.1716 | 14.1189 | 11.7074 | 11.5747 | 11.4137 | 11.2516 | 11.0947 | 10.9358 | 10.7821 | 10.5589 | 10.3326 | 10.1316 | 13.8284 | 13.7747 | 10.0811 | 9.9389 | 9.7695 | 9.5968 | 9.4305 | 9.2621 | 9.1 | 8.8358 | 8.5705 | 8.3358 | 12.3758 | 12.3084 | 10.3042 | 10.1621 | 9.9926 | 9.8211 | 9.6537 | 9.4863 | 9.3242 | 9.06 | 8.7958 | 8.5611
|  | HAREFIELD PRIMARY | FB |  |  |  |  | 14.2147 | 14.1895 | 14.1663 | 14.1411 | 14.1126 | 14.0842 | 14.0558 | 14.0305 | 14.0021 | 13.9 | 13.8442 | 13.8084 | 13.8737 | 13.8463 | 13.8211 | 13.7947 | 13.7558 | 13.6842 | 13.6147 | 13.5463 | 13.4747 | 13.1621 | 12.9011 | 12.6716 | 12.4295 | 12.3884 | 12.3537 | 12.3158 | 12.2737 | 12.2305 | 12.1874 | 12.1463 | 12.1032 | 11.9263 | 11.7979 | 11.6937
NURSLING GSP | WINCHESTER BSP | HARESTOCK PRIMARY | MINIMUM HEADROOM | SU 45908 31300 | NO | YES | 0.070526 | 33.3205 | 33.1153 | 32.9584 | 32.7911 | 32.6132 | 32.59 | 31.53 | 30.4468 | 29.3521 | 26.7184 | 24.9637 | 23.3858 | 30.4663 | 30.2316 | 30.0558 | 29.8695 | 29.6726 | 29.9926 | 28.7716 | 27.5242 | 26.26 | 23.2053 | 21.1568 | 19.3105 | 31.2621 | 31.0758 | 30.9316 | 30.7768 | 30.6116 | 31.04 | 29.9337 | 28.8011 | 27.5274 | 24.4463 | 22.38 | 20.5179
|  | HARESTOCK PRIMARY | EE |  |  |  |  | 35.8005 | 35.4174 | 35.0342 | 34.5858 | 34.0416 | 33.5342 | 33.0553 | 32.5689 | 32.0911 | 30.8858 | 29.6816 | 28.6363 | 33.6063 | 33.18 | 32.7579 | 32.2737 | 31.6989 | 31.1642 | 30.6537 | 30.14 | 29.6316 | 28.1905 | 26.7463 | 25.4905 | 34.2137 | 33.9737 | 33.5779 | 33.12 | 32.5663 | 32.0516 | 31.5632 | 31.0684 | 30.5811 | 29.3063 | 28.0189 | 26.7495
|  | HARESTOCK PRIMARY | HT |  |  |  |  | 35.8711 | 35.5237 | 35.0658 | 34.4111 | 33.57 | 32.59 | 31.53 | 30.4468 | 29.3521 | 26.7184 | 24.9637 | 23.3858 | 33.6926 | 33.3084 | 32.8 | 32.0632 | 31.1095 | 29.9926 | 28.7716 | 27.5242 | 26.26 | 23.2053 | 21.1568 | 19.3105 | 34.2221 | 34.0295 | 33.6126 | 32.9347 | 32.06 | 31.04 | 29.9337 | 28.8011 | 27.5274 | 24.4463 | 22.38 | 20.5179
|  | HARESTOCK PRIMARY | HE |  |  |  |  | 36.0542 | 35.7689 | 35.4763 | 35.1037 | 34.6153 | 34.1784 | 33.7574 | 33.3321 | 32.9132 | 32.2479 | 31.3984 | 30.6521 | 33.9095 | 33.6011 | 33.2863 | 32.8916 | 32.3832 | 31.9274 | 31.4895 | 31.0484 | 30.6137 | 29.7705 | 28.7253 | 27.8042 | 34.2684 | 34.0789 | 33.8768 | 33.5905 | 33.1726 | 32.7305 | 32.3042 | 31.8747 | 31.4505 | 30.7337 | 29.8263 | 29.0295
|  | HARESTOCK PRIMARY | FB |  |  |  |  | 33.3205 | 33.1153 | 32.9584 | 32.7911 | 32.6132 | 35.4037 | 35.2321 | 35.0711 | 34.9058 | 33.9953 | 33.1858 | 32.4942 | 30.4663 | 30.2316 | 30.0558 | 29.8695 | 29.6726 | 33.1758 | 32.9863 | 32.8074 | 32.6253 | 31.5779 | 30.6179 | 29.7863 | 31.2621 | 31.0758 | 30.9316 | 30.7768 | 30.6116 | 33.9526 | 33.7863 | 33.6189 | 33.4484 | 32.4979 | 31.6442 | 30.9126
EALING GSP | EALING BSP | HARVARD LANE PRIMARY | MINIMUM HEADROOM | TQ 20021 78030 | NO | YES | 0 | 32.7547 | 32.6095 | 83.4179 | 83.1695 | 82.8653 | 82.5316 | 82.1926 | 82.0137 | 81.6989 | 79.58 | 77.44 | 75.8832 | 29.7368 | 29.5916 | 80.3495 | 79.8937 | 79.2811 | 78.4537 | 77.1905 | 76.9232 | 75.8537 | 73.5147 | 70.8547 | 69.1158 | 27.5495 | 27.2463 | 77.8979 | 77.4779 | 76.9168 | 76.2874 | 75.62 | 75.7568 | 75.3579 | 73.9811 | 72.0074 | 71.0589
|  | HARVARD LANE PRIMARY | EE |  |  |  |  | 32.7589 | 32.6147 | 83.4474 | 83.2179 | 82.9105 | 82.6074 | 82.3158 | 82.0158 | 81.7189 | 81.7632 | 81.4474 | 80.4958 | 29.7411 | 29.5958 | 80.3937 | 79.9705 | 79.5126 | 79.0105 | 78.4958 | 77.8937 | 77.3137 | 76.7937 | 75.6032 | 74.5137 | 27.5547 | 27.2758 | 77.94 | 77.5495 | 77.1168 | 76.6474 | 76.1705 | 75.7568 | 75.3579 | 75.68 | 75.1211 | 74.6253
|  | HARVARD LANE PRIMARY | HT |  |  |  |  | 32.7547 | 32.6095 | 83.4179 | 83.1695 | 82.8653 | 82.5316 | 82.1926 | 82.1421 | 81.6989 | 79.58 | 77.44 | 75.8832 | 29.7368 | 29.5916 | 80.3495 | 79.8937 | 79.2811 | 78.4537 | 77.1905 | 76.9232 | 75.8537 | 73.5147 | 70.8547 | 69.1158 | 27.5495 | 27.2463 | 77.8979 | 77.4779 | 76.9168 | 76.2874 | 75.62 | 75.9716 | 75.3747 | 73.9811 | 72.0074 | 71.0589
|  | HARVARD LANE PRIMARY | HE |  |  |  |  | 32.7747 | 32.6274 | 83.46 | 83.2305 | 82.9168 | 82.6158 | 82.3168 | 82.0137 | 81.7116 | 82.0179 | 81.5421 | 81.5116 | 29.7568 | 29.6095 | 80.4421 | 80.1516 | 79.7042 | 79.2189 | 78.7326 | 78.3263 | 77.9389 | 78.2042 | 76.2137 | 75.5053 | 27.6358 | 27.3832 | 78.0716 | 77.7021 | 77.2768 | 76.8221 | 76.3684 | 75.98 | 75.6063 | 76.3463 | 74.6147 | 74.3432
|  | HARVARD LANE PRIMARY | FB |  |  |  |  | 32.8747 | 32.7832 | 83.7021 | 83.6105 | 83.5084 | 83.4063 | 83.3063 | 83.2147 | 83.1147 | 82.7516 | 82.5442 | 82.4095 | 29.8568 | 29.7653 | 80.6842 | 80.5926 | 80.4905 | 80.3884 | 80.2863 | 80.1316 | 79.9768 | 79.3137 | 78.8368 | 78.2484 | 27.8221 | 27.6547 | 78.5063 | 78.3326 | 78.1726 | 78.0053 | 77.8274 | 77.6832 | 77.5368 | 76.9242 | 76.4926 | 76.1358
COWLEY GSP |  | HARWELL PRIMARY | MINIMUM HEADROOM | SU 47395 86969 | NO | YES | 0.21053 | 39.0305 | 39.0168 | 38.9989 | 38.7958 | 38.7884 | 39.2368 | 39.2147 | 39.1937 | 39.1695 | 39.1768 | 39.1211 | 39.0737 | 37.4358 | 37.4211 | 37.4021 | 37.1221 | 37.1147 | 37.6905 | 37.6674 | 37.6442 | 37.6189 | 37.7116 | 37.6505 | 37.5989 | 37.1705 | 37.1558 | 37.1368 | 36.9011 | 36.8937 | 37.4126 | 37.3895 | 37.3674 | 37.3421 | 37.3632 | 37.3032 | 37.2537
|  | HARWELL PRIMARY | EE |  |  |  |  | 39.3326 | 39.3168 | 39.3 | 39.2811 | 39.2589 | 39.2368 | 39.2147 | 39.1937 | 39.1695 | 39.6 | 39.5611 | 39.5305 | 37.7916 | 37.7737 | 37.7568 | 37.7368 | 37.7137 | 37.6905 | 37.6674 | 37.6442 | 37.6189 | 38.2032 | 38.1589 | 38.1242 | 37.5126 | 37.4947 | 37.4779 | 37.4579 | 37.4347 | 37.4126 | 37.3895 | 37.3674 | 37.3421 | 37.8379 | 37.7958 | 37.7621
|  | HARWELL PRIMARY | HT |  |  |  |  | 39.0305 | 39.0168 | 38.9989 | 38.9789 | 40.3011 | 40.2779 | 40.2558 | 40.2316 | 40.2063 | 39.1768 | 39.1211 | 39.0737 | 37.4358 | 37.4211 | 37.4021 | 37.38 | 39.0126 | 38.9895 | 38.9663 | 38.94 | 38.9137 | 37.7116 | 37.6505 | 37.5989 | 37.1705 | 37.1558 | 37.1368 | 37.1158 | 38.6221 | 38.5979 | 38.5758 | 38.5495 | 38.5232 | 37.3632 | 37.3032 | 37.2537
|  | HARWELL PRIMARY | HE |  |  |  |  | 39.3432 | 39.3305 | 39.3189 | 39.3042 | 39.2853 | 39.2663 | 39.2495 | 39.2316 | 39.2137 | 39.6821 | 39.6632 | 39.6505 | 37.8042 | 37.7905 | 37.7779 | 37.7632 | 37.7432 | 37.7242 | 37.7063 | 37.6874 | 37.6705 | 38.2958 | 38.2747 | 38.26 | 37.5242 | 37.5116 | 37.4979 | 37.4832 | 37.4642 | 37.4442 | 37.4274 | 37.4095 | 37.3916 | 37.9284 | 37.9074 | 37.8937
|  | HARWELL PRIMARY | FB |  |  |  |  | 41.2421 | 41.2358 | 41.2274 | 38.7958 | 38.7884 | 39.3147 | 39.3074 | 39.3011 | 39.2937 | 39.2642 | 40.04 | 40.0168 | 39.2874 | 39.2842 | 39.28 | 37.1221 | 37.1147 | 37.7726 | 37.7653 | 37.7579 | 37.7505 | 37.7179 | 38.7074 | 38.6811 | 39.6705 | 39.6621 | 39.6537 | 36.9011 | 36.8937 | 37.4937 | 37.4853 | 37.4789 | 37.4716 | 37.44 | 38.3263 | 38.3011
FLEET-BRAMLEY GSP | FERNHURST BSP | HASLEMERE PRIMARY | MINIMUM HEADROOM | SU 89300 31710 | NO | YES | 0.11579 | 30.6358 | 30.2621 | 29.6947 | 28.8958 | 27.8674 | 26.78 | 25.7168 | 24.58 | 23.4084 | 20.8989 | 19.2211 | 17.7158 | 27.0242 | 26.6042 | 25.9505 | 25.0274 | 23.8305 | 22.5705 | 21.3389 | 20.0137 | 18.6432 | 15.72 | 13.7516 | 11.9832 | 30.04 | 29.84 | 29.5484 | 28.6242 | 27.4284 | 26.1684 | 24.9368 | 23.6105 | 22.24 | 19.3158 | 17.3474 | 15.5789
|  | HASLEMERE PRIMARY | EE |  |  |  |  | 30.6358 | 30.2621 | 29.8611 | 29.3779 | 28.7453 | 28.1768 | 27.6579 | 27.1242 | 26.5632 | 25.42 | 24.2579 | 23.2589 | 27.0242 | 26.6042 | 26.16 | 25.6295 | 24.9389 | 24.3263 | 23.7684 | 23.1937 | 22.5853 | 21.2105 | 19.8032 | 18.5895 | 30.04 | 29.84 | 29.6063 | 29.2274 | 28.5368 | 27.9242 | 27.3674 | 26.7916 | 26.1821 | 24.8084 | 23.4 | 22.1853
|  | HASLEMERE PRIMARY | HT |  |  |  |  | 30.6968 | 30.2747 | 29.6947 | 28.8958 | 27.8674 | 26.78 | 25.7168 | 24.58 | 23.4084 | 20.8989 | 19.2211 | 17.7158 | 27.0979 | 26.6158 | 25.9505 | 25.0274 | 23.8305 | 22.5705 | 21.3389 | 20.0137 | 18.6432 | 15.72 | 13.7516 | 11.9832 | 30.0484 | 29.8558 | 29.5484 | 28.6242 | 27.4284 | 26.1684 | 24.9368 | 23.6105 | 22.24 | 19.3158 | 17.3474 | 15.5789
|  | HASLEMERE PRIMARY | HE |  |  |  |  | 30.8863 | 30.6032 | 30.2853 | 29.8684 | 29.2789 | 28.7705 | 28.3284 | 27.8758 | 27.3926 | 26.8737 | 26.0989 | 25.4253 | 27.3263 | 27.02 | 26.6758 | 26.2274 | 25.5905 | 25.0495 | 24.5884 | 24.1168 | 23.6053 | 22.9463 | 21.9832 | 21.1432 | 30.0905 | 29.8989 | 29.6789 | 29.3811 | 28.9737 | 28.5926 | 28.1874 | 27.7147 | 27.2032 | 26.5442 | 25.58 | 24.7411
|  | HASLEMERE PRIMARY | FB |  |  |  |  | 31.1811 | 30.9737 | 30.8116 | 30.6316 | 30.4179 | 30.2095 | 30.0358 | 29.8705 | 29.6779 | 28.8589 | 28.0632 | 27.3747 | 27.66 | 27.4221 | 27.24 | 27.0368 | 26.7926 | 26.5579 | 26.3653 | 26.1811 | 25.9642 | 25.0274 | 24.0768 | 23.2421 | 30.2368 | 30.1442 | 30.0621 | 29.9695 | 29.8674 | 29.7632 | 29.6621 | 29.5684 | 29.4674 | 28.6263 | 27.6747 | 26.8389
FLEET-BRAMLEY GSP | FERNHURST BSP | HASLINGBOURNE PRIMARY | MINIMUM HEADROOM | SU 98188 20276 | NO | YES | 0 | 22.5453 | 22.2926 | 22.08 | 21.7937 | 21.4547 | 21.0958 | 20.7442 | 20.3516 | 19.9379 | 18.9905 | 18.2379 | 17.56 | 21.0905 | 20.9474 | 20.7137 | 20.4011 | 20.0305 | 19.6368 | 19.2537 | 18.8221 | 18.3674 | 17.3211 | 16.4821 | 15.7242 | 21.8432 | 21.7126 | 21.5074 | 21.2284 | 20.9 | 20.5505 | 20.2084 | 19.8284 | 19.4295 | 18.5116 | 17.7853 | 17.1305
|  | HASLINGBOURNE PRIMARY | EE |  |  |  |  | 22.5453 | 22.2926 | 22.14 | 21.9768 | 21.7884 | 21.6053 | 21.4105 | 21.2063 | 20.9937 | 20.5463 | 20.0042 | 19.5316 | 21.0905 | 20.9474 | 20.7853 | 20.6126 | 20.4179 | 20.2284 | 20.0242 | 19.8095 | 19.5853 | 19.0811 | 18.4674 | 17.9316 | 21.8432 | 21.7126 | 21.5632 | 21.4042 | 21.2158 | 21.0358 | 20.8432 | 20.6421 | 20.4326 | 20.0011 | 19.4811 | 19.0274
|  | HASLINGBOURNE PRIMARY | HT |  |  |  |  | 22.5684 | 22.2979 | 22.08 | 21.7937 | 21.4547 | 21.0958 | 20.7442 | 20.3516 | 19.9379 | 18.9905 | 18.2379 | 17.56 | 21.1158 | 20.9516 | 20.7137 | 20.4011 | 20.0305 | 19.6368 | 19.2537 | 18.8221 | 18.3674 | 17.3211 | 16.4821 | 15.7242 | 21.8653 | 21.7189 | 21.5074 | 21.2284 | 20.9 | 20.5505 | 20.2084 | 19.8284 | 19.4295 | 18.5116 | 17.7853 | 17.1305
|  | HASLINGBOURNE PRIMARY | HE |  |  |  |  | 22.6337 | 22.4147 | 22.2916 | 22.1526 | 21.9768 | 21.8168 | 21.6589 | 21.4968 | 21.32 | 21.14 | 20.7579 | 20.42 | 21.1884 | 21.0842 | 20.9547 | 20.8105 | 20.6305 | 20.4663 | 20.3042 | 20.1368 | 19.9537 | 19.7442 | 19.3053 | 18.9158 | 21.9274 | 21.8305 | 21.7095 | 21.5726 | 21.3979 | 21.2389 | 21.0832 | 20.9211 | 20.7474 | 20.5768 | 20.2126 | 19.8905
|  | HASLINGBOURNE PRIMARY | FB |  |  |  |  | 22.7168 | 22.5242 | 22.4642 | 22.4032 | 22.3421 | 22.2779 | 22.2158 | 22.1568 | 22.0895 | 21.8105 | 21.46 | 21.1516 | 21.2768 | 21.1979 | 21.1337 | 21.0684 | 21.0021 | 20.9337 | 20.8684 | 20.8053 | 20.7326 | 20.4295 | 20.0358 | 19.6853 | 22.0095 | 21.9389 | 21.8811 | 21.8211 | 21.76 | 21.6979 | 21.6379 | 21.58 | 21.5137 | 21.2421 | 20.9053 | 20.6105
MELKSHAM GSP | FROME BSP | HAWKERIDGE PRIMARY | MINIMUM HEADROOM | ST 86422 53026 | NO | YES | 8 | 16.9074 | 16.8989 | 16.8874 | 16.8705 | 16.8537 | 16.8337 | 16.7926 | 16.7505 | 14.9526 | 14.8168 | 14.7032 | 14.6074 | 16.8958 | 16.88 | 16.8316 | 16.8137 | 16.7958 | 16.7747 | 16.7284 | 16.6821 | 14.5663 | 14.4084 | 14.2747 | 14.1632 | 15.8916 | 15.8758 | 15.8274 | 15.8105 | 15.7926 | 15.7716 | 15.7253 | 15.68 | 13.5989 | 13.4442 | 13.3126 | 13.2032
|  | HAWKERIDGE PRIMARY | EE |  |  |  |  | 16.9074 | 16.8989 | 16.8874 | 16.8705 | 16.8537 | 16.8337 | 16.7926 | 16.7505 | 14.9526 | 14.8168 | 14.7032 | 14.6074 | 16.8958 | 16.88 | 16.8316 | 16.8137 | 16.7958 | 16.7747 | 16.7284 | 16.6821 | 14.5663 | 14.4084 | 14.2747 | 14.1632 | 15.8916 | 15.8758 | 15.8274 | 15.8105 | 15.7926 | 15.7716 | 15.7253 | 15.68 | 13.5989 | 13.4442 | 13.3126 | 13.2032
|  | HAWKERIDGE PRIMARY | HT |  |  |  |  | 16.9074 | 16.9 | 16.8895 | 16.8726 | 16.8547 | 16.8368 | 16.8179 | 16.7779 | 16.7368 | 16.5811 | 16.4537 | 16.3474 | 16.8989 | 16.8853 | 16.8347 | 16.8168 | 16.7979 | 16.7789 | 16.76 | 16.7158 | 16.6695 | 16.4916 | 16.3453 | 16.2242 | 15.8947 | 15.8811 | 15.8305 | 15.8126 | 15.7947 | 15.7758 | 15.7558 | 15.7126 | 15.6674 | 15.4916 | 15.3474 | 15.2274
|  | HAWKERIDGE PRIMARY | HE |  |  |  |  | 16.9095 | 16.9032 | 16.8958 | 16.8853 | 16.8726 | 16.8589 | 16.8453 | 16.8305 | 15.0579 | 15.0505 | 14.9926 | 14.9453 | 16.9074 | 16.8968 | 16.8505 | 16.8368 | 16.8211 | 16.8053 | 16.7905 | 16.7747 | 14.6895 | 14.68 | 14.6126 | 14.5568 | 15.9032 | 15.8916 | 15.8474 | 15.8326 | 15.8179 | 15.8011 | 15.7863 | 15.7716 | 13.72 | 13.7116 | 13.6442 | 13.5895
|  | HAWKERIDGE PRIMARY | FB |  |  |  |  | 16.9147 | 16.9116 | 16.9084 | 16.9053 | 16.9021 | 16.8989 | 16.8958 | 16.8926 | 16.8895 | 16.8768 | 16.8284 | 16.7611 | 16.9305 | 16.9221 | 16.9042 | 16.8979 | 16.8916 | 16.8863 | 16.8789 | 16.8737 | 16.8674 | 16.8421 | 16.7663 | 16.6884 | 15.9263 | 15.9179 | 15.9 | 15.8937 | 15.8874 | 15.8811 | 15.8747 | 15.8684 | 15.8632 | 15.8379 | 15.7632 | 15.6863
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | HAWLEY PRIMARY | MINIMUM HEADROOM | SU 85973 57691 | NO | YES | 0 | 27.7574 | 27.4732 | 27.1679 | 26.8121 | 26.3826 | 25.8458 | 25.2153 | 24.5868 | 23.9658 | 22.3658 | 21.4542 | 20.6258 | 25.8895 | 25.5316 | 25.1568 | 24.7379 | 24.2579 | 23.5937 | 22.7895 | 21.9832 | 21.1884 | 19.0747 | 17.8968 | 16.8158 | 27.1063 | 26.8537 | 26.58 | 26.2526 | 25.8463 | 25.3663 | 24.8147 | 24.2663 | 23.7232 | 22.3547 | 21.5632 | 20.8484
|  | HAWLEY PRIMARY | EE |  |  |  |  | 27.7574 | 27.4732 | 27.1679 | 26.8121 | 26.3826 | 25.9679 | 25.5668 | 25.1647 | 24.7658 | 23.9521 | 23.3753 | 22.8763 | 25.8895 | 25.5316 | 25.1568 | 24.7379 | 24.2579 | 23.7947 | 23.3421 | 22.8884 | 22.44 | 21.2621 | 20.4505 | 19.7379 | 27.1063 | 26.8537 | 26.58 | 26.2526 | 25.8463 | 25.4537 | 25.0758 | 24.6947 | 24.3179 | 23.6695 | 23.1989 | 22.7958
|  | HAWLEY PRIMARY | HT |  |  |  |  | 27.8121 | 27.55 | 27.2416 | 26.8805 | 26.4437 | 25.8458 | 25.2153 | 24.5868 | 23.9658 | 22.3658 | 21.4542 | 20.6258 | 25.9705 | 25.6442 | 25.2716 | 24.8537 | 24.3453 | 23.5937 | 22.7895 | 21.9832 | 21.1884 | 19.0747 | 17.8968 | 16.8158 | 27.1484 | 26.9158 | 26.6347 | 26.2989 | 25.8968 | 25.3663 | 24.8147 | 24.2663 | 23.7232 | 22.3547 | 21.5632 | 20.8484
|  | HAWLEY PRIMARY | HE |  |  |  |  | 27.93 | 27.7037 | 27.4511 | 27.1332 | 26.7289 | 26.3511 | 25.9826 | 25.6132 | 25.25 | 24.8363 | 24.5258 | 24.2542 | 26.1453 | 25.8789 | 25.5853 | 25.2295 | 24.7905 | 24.3811 | 23.9842 | 23.5842 | 23.1947 | 22.5168 | 22.0453 | 21.6253 | 27.2411 | 27.0326 | 26.7979 | 26.4979 | 26.1084 | 25.7453 | 25.3905 | 25.0326 | 24.6832 | 24.3874 | 24.1495 | 23.9453
|  | HAWLEY PRIMARY | FB |  |  |  |  | 28.1089 | 27.9511 | 27.8258 | 27.6911 | 27.5468 | 27.4047 | 27.2668 | 27.1353 | 26.9984 | 26.4574 | 25.8689 | 25.5121 | 26.3611 | 26.1526 | 25.9947 | 25.8263 | 25.6495 | 25.4747 | 25.3063 | 25.1442 | 24.9779 | 24.2989 | 23.4558 | 22.9463 | 27.4042 | 27.2674 | 27.1568 | 27.0368 | 26.9084 | 26.78 | 26.6568 | 26.5389 | 26.4158 | 25.9358 | 25.4632 | 25.1747
NORTH HYDE GSP |  | HAYES PRIMARY | MINIMUM HEADROOM | TQ 09519 79541 | NO | NO | 0.99474 | 65.2811 | 64.8084 | 63.9579 | 63.1747 | 62.1232 | 61.1168 | 60.1116 | 59.0968 | 58.0811 | 55.6084 | 54.0484 | 51.1579 | 72.5853 | 72.3074 | 69.8737 | 67.9568 | 65.2105 | 62.7832 | 60.36 | 57.8747 | 55.3874 | 49.4632 | 45.7189 | 42.3011 | 58.3653 | 57.7937 | 56.7242 | 55.7853 | 54.5021 | 53.3021 | 52.1021 | 50.6989 | 48.2105 | 42.2853 | 38.5411 | 35.1221
|  | HAYES PRIMARY | EE |  |  |  |  | 65.3011 | 64.9021 | 64.4137 | 63.6305 | 62.8811 | 62.2011 | 61.5758 | 60.9326 | 60.3021 | 59.2305 | 58.2737 | 57.4516 | 72.5853 | 72.3211 | 71.7453 | 69.8126 | 68.48 | 67.2989 | 66.1947 | 65.08 | 63.9979 | 60.8358 | 58.0832 | 55.6421 | 58.4021 | 57.9484 | 57.3768 | 56.4337 | 55.6032 | 54.8547 | 54.1632 | 53.4547 | 52.7632 | 51.4053 | 50.2032 | 48.4663
|  | HAYES PRIMARY | HT |  |  |  |  | 65.2811 | 64.8084 | 63.9579 | 63.1747 | 62.1232 | 61.1168 | 60.1116 | 59.0968 | 58.0811 | 55.6084 | 54.0484 | 51.1579 | 72.6095 | 72.3074 | 69.8737 | 67.9568 | 65.2105 | 62.7832 | 60.36 | 57.8747 | 55.3874 | 49.4632 | 45.7189 | 42.3011 | 58.3653 | 57.7937 | 56.7242 | 55.7853 | 54.5021 | 53.3021 | 52.1021 | 50.6989 | 48.2105 | 42.2853 | 38.5411 | 35.1221
|  | HAYES PRIMARY | HE |  |  |  |  | 65.4453 | 65.0958 | 64.6547 | 63.9105 | 63.1884 | 62.5568 | 61.9642 | 61.3611 | 60.7716 | 60.3084 | 59.7253 | 59.2232 | 72.6442 | 72.3937 | 72.1274 | 70.6116 | 69.3589 | 68.2853 | 67.3389 | 66.3789 | 65.4537 | 63.4326 | 61.3884 | 59.5589 | 58.5811 | 58.1905 | 57.68 | 56.7863 | 55.9895 | 55.2979 | 54.6558 | 54.0032 | 53.3684 | 52.6916 | 51.9095 | 51.2253
|  | HAYES PRIMARY | FB |  |  |  |  | 65.7042 | 65.4884 | 65.2895 | 65.0737 | 64.7242 | 64.4958 | 64.26 | 64.0421 | 63.8147 | 62.8874 | 62.2063 | 61.6558 | 72.8095 | 72.6705 | 72.5442 | 72.4032 | 72.2463 | 71.9211 | 71.4411 | 71.0053 | 70.5589 | 68.5611 | 66.7947 | 65.2074 | 58.8779 | 58.6316 | 58.4032 | 58.1558 | 57.7284 | 57.4716 | 57.2021 | 56.9537 | 56.6958 | 55.6211 | 54.7905 | 54.0979
COWLEY GSP | HEADINGTON BSP | HEADINGTON PRIMARY | MINIMUM HEADROOM | SP 54440 08085 | NO | YES | 0 | 40.0632 | 39.8937 | 39.7116 | 39.4495 | 39.1126 | 38.7747 | 38.4232 | 38.1842 | 37.88 | 38.0895 | 37.3368 | 36.4495 | 34.9958 | 34.6295 | 34.1863 | 33.7579 | 33.3316 | 32.8684 | 32.3674 | 32.4242 | 32.0737 | 33.2453 | 32.6516 | 31.8737 | 39.88 | 39.7105 | 39.4011 | 38.6242 | 37.9768 | 37.28 | 36.4642 | 36.6 | 35.6274 | 35.6547 | 34.5442 | 33.5937
|  | HEADINGTON PRIMARY | EE |  |  |  |  | 40.0632 | 39.8937 | 39.7116 | 39.4642 | 39.1126 | 38.7884 | 38.4926 | 38.1842 | 37.88 | 38.7905 | 38.5463 | 38.3547 | 34.9958 | 34.6295 | 34.2432 | 33.8895 | 33.4958 | 33.1295 | 32.7821 | 32.4242 | 32.0737 | 33.9453 | 33.7011 | 33.5105 | 39.88 | 39.7105 | 39.5274 | 39.0032 | 38.52 | 38.0642 | 37.6084 | 37.1474 | 36.6989 | 38.7979 | 38.2242 | 37.6116
|  | HEADINGTON PRIMARY | HT |  |  |  |  | 40.0811 | 39.9211 | 39.7126 | 39.4495 | 39.1274 | 38.7747 | 38.4232 | 38.4537 | 38.1095 | 38.0895 | 37.3368 | 36.4495 | 35.0011 | 34.6337 | 34.1863 | 33.7579 | 33.3316 | 32.8684 | 32.3674 | 32.9032 | 32.3568 | 33.2453 | 32.6516 | 31.8737 | 39.8979 | 39.7379 | 39.4011 | 38.6242 | 37.9768 | 37.28 | 36.4642 | 36.6 | 35.6274 | 35.6547 | 34.5442 | 33.5937
|  | HEADINGTON PRIMARY | HE |  |  |  |  | 40.1158 | 39.9558 | 39.7779 | 39.5326 | 39.1779 | 38.8674 | 38.5663 | 38.2526 | 37.9474 | 38.7568 | 38.6768 | 38.6242 | 35.1147 | 34.7863 | 34.4305 | 34.0979 | 33.7147 | 33.3768 | 33.0495 | 32.7116 | 32.3853 | 33.9537 | 33.8737 | 33.8211 | 39.9326 | 39.7726 | 39.5947 | 39.3495 | 38.9947 | 38.6653 | 38.2842 | 37.8958 | 37.5232 | 38.7042 | 38.6242 | 38.5716
|  | HEADINGTON PRIMARY | FB |  |  |  |  | 40.2232 | 40.1389 | 40.0621 | 39.9747 | 39.8811 | 39.7842 | 39.6916 | 39.6032 | 39.5116 | 39.1705 | 38.9789 | 38.8568 | 35.2937 | 35.1063 | 34.9389 | 34.8 | 34.68 | 34.5558 | 34.4368 | 34.3232 | 34.2074 | 33.74 | 33.4284 | 33.1958 | 40.04 | 39.9558 | 39.8789 | 39.7916 | 39.6979 | 39.6011 | 39.5084 | 39.42 | 39.3284 | 38.9874 | 38.5926 | 38.1274
NURSLING GSP | VELMORE BSP | HEDGE END PRIMARY | MINIMUM HEADROOM | SU 49035 15685 | NO | YES | 0 | 19.8411 | 19.5074 | 19.1568 | 18.94 | 18.6095 | 18.2684 | 17.9158 | 17.5084 | 17.0463 | 15.7663 | 14.8695 | 14.0663 | 18.36 | 17.9884 | 17.5968 | 17.3674 | 17.0095 | 16.6421 | 16.26 | 15.8147 | 15.3074 | 13.9084 | 12.9074 | 12.0105 | 18.8242 | 18.4463 | 18.0505 | 17.8189 | 17.4579 | 17.0863 | 16.7011 | 16.2505 | 15.7368 | 14.3189 | 13.3042 | 12.3947
|  | HEDGE END PRIMARY | EE |  |  |  |  | 19.8411 | 19.5074 | 19.1568 | 18.9758 | 18.7168 | 18.4768 | 18.2737 | 18.0705 | 17.8453 | 17.1611 | 16.5274 | 15.9789 | 18.36 | 17.9884 | 17.5968 | 17.4063 | 17.1337 | 16.88 | 16.6674 | 16.4558 | 16.2179 | 15.4653 | 14.7484 | 14.1263 | 18.8242 | 18.4463 | 18.0505 | 17.8589 | 17.5842 | 17.3284 | 17.1147 | 16.9021 | 16.6621 | 15.8979 | 15.1684 | 14.5368
|  | HEDGE END PRIMARY | HT |  |  |  |  | 19.8726 | 19.5526 | 19.1905 | 18.94 | 18.6095 | 18.2684 | 17.9158 | 17.5084 | 17.0463 | 15.7663 | 14.8695 | 14.0663 | 18.3958 | 18.0389 | 17.6358 | 17.3674 | 17.0095 | 16.6421 | 16.26 | 15.8147 | 15.3074 | 13.9084 | 12.9074 | 12.0105 | 18.86 | 18.4979 | 18.0905 | 17.8189 | 17.4579 | 17.0863 | 16.7011 | 16.2505 | 15.7368 | 14.3189 | 13.3042 | 12.3947
|  | HEDGE END PRIMARY | HE |  |  |  |  | 19.8947 | 19.6589 | 19.3463 | 19.2 | 18.9642 | 18.7537 | 18.58 | 18.4074 | 18.2095 | 17.72 | 17.2337 | 16.8137 | 18.4821 | 18.1579 | 17.8095 | 17.6568 | 17.4105 | 17.1895 | 17.0095 | 16.8326 | 16.6263 | 16.0579 | 15.5011 | 15.0179 | 18.9474 | 18.62 | 18.2663 | 18.1126 | 17.8642 | 17.6421 | 17.4621 | 17.2842 | 17.0768 | 16.4979 | 15.9326 | 15.44
|  | HEDGE END PRIMARY | FB |  |  |  |  | 19.9484 | 19.9147 | 19.8747 | 19.8074 | 19.7179 | 19.6305 | 19.5579 | 19.4916 | 19.4095 | 18.9179 | 18.5084 | 18.1537 | 18.7484 | 18.5632 | 18.3979 | 18.3242 | 18.2284 | 18.1326 | 18.0558 | 17.9842 | 17.8958 | 17.3505 | 16.8895 | 16.4863 | 19.2179 | 19.0305 | 18.8621 | 18.7884 | 18.6905 | 18.5947 | 18.5168 | 18.4442 | 18.3558 | 17.8021 | 17.3347 | 16.9263
BRAMLEY (BASI) GSP | READING BSP | HENLEY PRIMARY | MINIMUM HEADROOM | SU 76070 82422 | NO | YES | 0 | 29.5729 | 29.3571 | 29.1234 | 28.8245 | 28.475 | 28.0992 | 27.7339 | 27.3697 | 27.0076 | 25.6845 | 24.7392 | 23.7392 | 26.7255 | 26.2876 | 25.8234 | 25.3539 | 24.8445 | 24.3224 | 23.8382 | 23.3203 | 22.8024 | 20.4003 | 19.2697 | 18.0634 | 28.115 | 27.9476 | 27.7624 | 27.5003 | 27.1697 | 26.6929 | 26.215 | 25.7097 | 25.2013 | 22.8918 | 21.7992 | 20.6371
|  | HENLEY PRIMARY | EE |  |  |  |  | 29.5729 | 29.3571 | 29.1266 | 28.8392 | 28.4782 | 28.1318 | 27.8045 | 27.4697 | 27.1392 | 26.6603 | 26.0508 | 25.5066 | 26.7255 | 26.2876 | 25.8392 | 25.3855 | 24.9371 | 24.5024 | 24.0571 | 23.5792 | 23.1087 | 21.5045 | 20.7329 | 20.0371 | 28.115 | 27.9476 | 27.7624 | 27.5118 | 27.1697 | 26.8424 | 26.4276 | 25.9571 | 25.495 | 23.9708 | 23.2297 | 22.5645
|  | HENLEY PRIMARY | HT |  |  |  |  | 29.5813 | 29.3782 | 29.1234 | 28.8245 | 28.475 | 28.0992 | 27.7339 | 27.3697 | 27.0076 | 25.6845 | 24.7392 | 23.7392 | 26.7361 | 26.3045 | 25.8234 | 25.3539 | 24.8445 | 24.3224 | 23.8382 | 23.3203 | 22.8024 | 20.4003 | 19.2697 | 18.0634 | 28.1224 | 27.9687 | 27.7624 | 27.5003 | 27.1855 | 26.6929 | 26.215 | 25.7097 | 25.2013 | 22.8918 | 21.7992 | 20.6371
|  | HENLEY PRIMARY | HE |  |  |  |  | 29.6371 | 29.4413 | 29.2266 | 28.9529 | 28.6013 | 28.2761 | 27.9592 | 27.635 | 27.3192 | 27.2024 | 27.1003 | 27.0255 | 26.9224 | 26.5613 | 26.1771 | 25.7782 | 25.3697 | 24.9834 | 24.6087 | 24.2266 | 23.855 | 22.9624 | 22.5708 | 22.235 | 28.1497 | 27.9897 | 27.8118 | 27.5655 | 27.2266 | 26.9139 | 26.6097 | 26.2982 | 25.9939 | 25.3645 | 24.9929 | 24.6739
|  | HENLEY PRIMARY | FB |  |  |  |  | 29.7813 | 29.6761 | 29.5834 | 29.4887 | 29.3897 | 29.2887 | 29.1929 | 29.1003 | 29.0024 | 28.6382 | 28.3466 | 28.1834 | 27.1697 | 26.9382 | 26.7476 | 26.5718 | 26.4182 | 26.2613 | 26.1076 | 25.9592 | 25.8055 | 25.1897 | 24.2918 | 23.8171 | 28.2718 | 28.195 | 28.1234 | 28.0455 | 27.9582 | 27.8697 | 27.7855 | 27.7055 | 27.6203 | 27.3097 | 26.6824 | 26.2287
AXMINSTER GSP | YEOVIL BSP | HENSTRIDGE PRIMARY | MINIMUM HEADROOM | ST 72676 19263 | NO | YES | 0 | 21.5789 | 21.2316 | 20.7579 | 20.4684 | 19.6842 | 19.2368 | 18.7874 | 18.4116 | 18.0284 | 16.4021 | 15.9274 | 15.4779 | 18.9274 | 18.5421 | 18.0189 | 17.7105 | 16.8389 | 16.3568 | 15.8705 | 15.4684 | 15.0568 | 13.2 | 12.6726 | 12.1716 | 20.0368 | 19.6432 | 19.1063 | 18.7937 | 17.9 | 17.4084 | 16.9137 | 16.5042 | 16.0863 | 14.1716 | 13.6305 | 13.1168
|  | HENSTRIDGE PRIMARY | EE |  |  |  |  | 21.5789 | 21.2863 | 20.8442 | 20.4768 | 19.7653 | 19.4863 | 19.2063 | 18.8474 | 18.5 | 16.4021 | 15.9274 | 15.4779 | 18.9274 | 18.6063 | 18.1168 | 17.7168 | 16.9316 | 16.64 | 16.3432 | 15.9568 | 15.5832 | 13.2 | 12.6726 | 12.1716 | 20.0368 | 19.7084 | 19.2074 | 18.8 | 17.9958 | 17.7 | 17.3989 | 17.0053 | 16.6263 | 14.1716 | 13.6305 | 13.1168
|  | HENSTRIDGE PRIMARY | HT |  |  |  |  | 21.6084 | 21.2316 | 20.7579 | 20.4684 | 19.6842 | 19.2368 | 18.7874 | 18.4116 | 18.0284 | 17.0379 | 16.3474 | 15.6832 | 18.96 | 18.5421 | 18.0189 | 17.7105 | 16.8389 | 16.3568 | 15.8705 | 15.4684 | 15.0568 | 13.9863 | 13.2347 | 12.5074 | 20.0705 | 19.6432 | 19.1063 | 18.7937 | 17.9 | 17.4084 | 16.9137 | 16.5042 | 16.0863 | 14.9958 | 14.2284 | 13.4853
|  | HENSTRIDGE PRIMARY | HE |  |  |  |  | 21.6989 | 21.4537 | 21.0526 | 20.7189 | 20.0337 | 19.7895 | 19.5442 | 19.2253 | 18.9189 | 17.1232 | 16.8326 | 16.54 | 19.0611 | 18.7926 | 18.3484 | 17.9874 | 17.2305 | 16.9747 | 16.7189 | 16.3789 | 16.0526 | 13.9947 | 13.6674 | 13.3347 | 20.1737 | 19.9 | 19.4453 | 19.0768 | 18.3021 | 18.0442 | 17.7842 | 17.4389 | 17.1074 | 14.9853 | 14.6484 | 14.3053
|  | HENSTRIDGE PRIMARY | FB |  |  |  |  | 21.8274 | 21.6832 | 21.5495 | 21.4126 | 21.0905 | 21.0032 | 20.9095 | 20.8179 | 20.6832 | 20.2442 | 19.9211 | 19.6179 | 19.1968 | 19.0368 | 18.8905 | 18.7389 | 18.3768 | 18.2821 | 18.1821 | 18.0821 | 17.9337 | 17.4547 | 17.0968 | 16.7579 | 20.3116 | 20.1484 | 19.9979 | 19.8432 | 19.4705 | 19.3747 | 19.2726 | 19.1705 | 19.0189 | 18.5295 | 18.1632 | 17.8147
FLEET-BRAMLEY GSP | ALTON BSP | HERRIARD PRIMARY | MINIMUM HEADROOM | SU 66770 44972 | YES | YES | 0 | 2.9705 | 2.6989 | 2.3832 | 2.0811 | 1.7895 | 0.27158 | 0.18211 | -0.042105 | -0.28526 | -1.2084 | -1.8611 | -2.3663 | 1.6842 | 1.4 | 1.0705 | 0.75684 | 0.45474 | -1.3842 | -1.4789 | -1.58 | -1.8347 | -2.8011 | -3.4842 | -4.0147 | 1.9232 | 1.6284 | 1.2863 | 0.96 | 0.64526 | -1.0611 | -1.1568 | -1.3263 | -1.5905 | -2.5968 | -3.3074 | -3.8589
|  | HERRIARD PRIMARY | EE |  |  |  |  | 2.9705 | 2.6989 | 2.3832 | 2.0811 | 1.7895 | 0.63474 | 0.31789 | -0.042105 | -0.28526 | -1.2084 | -1.8611 | -2.3663 | 1.6842 | 1.4 | 1.0705 | 0.75684 | 0.45474 | -0.87474 | -1.2042 | -1.58 | -1.8347 | -2.8011 | -3.4842 | -4.0147 | 1.9232 | 1.6284 | 1.2863 | 0.96 | 0.64526 | -0.59263 | -0.93474 | -1.3263 | -1.5905 | -2.5968 | -3.3074 | -3.8589
|  | HERRIARD PRIMARY | HT |  |  |  |  | 3.0947 | 2.8568 | 2.6211 | 2.3611 | 2.1874 | 0.27158 | 0.18211 | 0.098947 | 0.043158 | -0.31053 | -0.63368 | -0.97263 | 1.8158 | 1.5663 | 1.3211 | 1.0484 | 0.86632 | -1.3842 | -1.4789 | -1.5653 | -1.6232 | -1.9958 | -2.3368 | -2.6958 | 2.06 | 1.8021 | 1.5474 | 1.2674 | 1.0811 | -1.0611 | -1.1568 | -1.2453 | -1.3053 | -1.6874 | -2.04 | -2.4095
|  | HERRIARD PRIMARY | HE |  |  |  |  | 3.3705 | 3.3526 | 3.3305 | 3.3063 | 3.2747 | 2.3263 | 2.2989 | 2.2695 | 2.24 | 2.2221 | 2.2011 | 2.1789 | 2.1042 | 2.0842 | 2.0621 | 2.0358 | 2.0042 | 0.88947 | 0.86105 | 0.83053 | 0.80105 | 0.78 | 0.75474 | 0.72947 | 2.36 | 2.3421 | 2.32 | 2.2958 | 2.2642 | 1.2505 | 1.2232 | 1.1926 | 1.1632 | 1.1421 | 1.1189 | 1.0937
|  | HERRIARD PRIMARY | FB |  |  |  |  | 3.3863 | 3.3716 | 3.3621 | 3.3505 | 3.3379 | 3.3263 | 3.3158 | 3.3042 | 3.2916 | 3.2474 | 3.2084 | 3.1747 | 2.1211 | 2.1042 | 2.0937 | 2.0811 | 2.0674 | 2.0558 | 2.0442 | 2.0305 | 2.0179 | 1.9695 | 1.9253 | 1.8884 | 2.3758 | 2.3611 | 2.3516 | 2.34 | 2.3274 | 2.3158 | 2.3053 | 2.2937 | 2.2811 | 2.2368 | 2.1968 | 2.1642
IVER 132KV GSP | CHALVEY | HERSCHEL STREET PRIMARY | MINIMUM HEADROOM | TBC | NO | NO | TBC |  |  |  | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | HERSCHEL STREET PRIMARY | EE | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | HERSCHEL STREET PRIMARY | HT | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | HERSCHEL STREET PRIMARY | HE | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | HERSCHEL STREET PRIMARY | FB | [7 empty] | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 |  |  |  | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 |  |  |  | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE PRIMARY | MINIMUM HEADROOM | SU 84733 92200 | NO | YES | 0.73684 | 30.2595 | 30.0858 | 29.91 | 29.6268 | 29.2795 | 28.8942 | 28.5037 | 28.0963 | 27.69 | 26.7384 | 26.0995 | 25.5321 | 23.7526 | 23.5095 | 23.2726 | 22.8747 | 22.3758 | 21.8211 | 21.2516 | 20.6421 | 20.0316 | 18.5842 | 17.5947 | 16.7137 | 24.6611 | 24.4189 | 24.1811 | 23.7853 | 23.2863 | 22.7316 | 22.1632 | 21.5547 | 20.9453 | 19.5042 | 18.5179 | 17.6379
|  | HIGH WYCOMBE PRIMARY | EE |  |  |  |  | 30.2595 | 30.0858 | 29.91 | 29.6984 | 29.4258 | 29.1721 | 28.9132 | 28.6437 | 28.3753 | 27.9311 | 27.5089 | 27.1616 | 23.7526 | 23.5095 | 23.2726 | 23.0063 | 22.6905 | 22.3937 | 22.0621 | 21.7158 | 21.3726 | 20.5832 | 19.8463 | 19.2358 | 24.6611 | 24.4189 | 24.1811 | 23.9147 | 23.5989 | 23.3042 | 22.9726 | 22.6263 | 22.2832 | 21.4979 | 20.7642 | 20.1558
|  | HIGH WYCOMBE PRIMARY | HT |  |  |  |  | 30.2879 | 30.1289 | 29.9121 | 29.6268 | 29.2795 | 28.8942 | 28.5037 | 28.0963 | 27.69 | 26.7384 | 26.0995 | 25.5321 | 23.8042 | 23.5853 | 23.2821 | 22.8747 | 22.3758 | 21.8211 | 21.2516 | 20.6421 | 20.0316 | 18.5842 | 17.5947 | 16.7137 | 24.7126 | 24.4947 | 24.1905 | 23.7853 | 23.2863 | 22.7316 | 22.1632 | 21.5547 | 20.9453 | 19.5042 | 18.5179 | 17.6379
|  | HIGH WYCOMBE PRIMARY | HE |  |  |  |  | 30.3658 | 30.23 | 30.0837 | 29.8963 | 29.6426 | 29.4153 | 29.19 | 28.9511 | 28.7195 | 28.57 | 28.3384 | 28.1574 | 23.9368 | 23.7642 | 23.5842 | 23.3663 | 23.0842 | 22.8316 | 22.5716 | 22.2947 | 22.0242 | 21.6958 | 21.2537 | 20.8947 | 24.8442 | 24.6716 | 24.4926 | 24.2747 | 23.9937 | 23.7411 | 23.4811 | 23.2042 | 22.9337 | 22.6063 | 22.1653 | 21.8074
|  | HIGH WYCOMBE PRIMARY | FB |  |  |  |  | 30.4668 | 30.3732 | 30.2995 | 30.2195 | 30.1342 | 30.0489 | 29.9626 | 29.8784 | 29.79 | 29.4321 | 29.1395 | 28.9005 | 24.0716 | 23.9326 | 23.8295 | 23.72 | 23.6042 | 23.4916 | 23.3737 | 23.2558 | 23.1337 | 22.6105 | 22.1168 | 21.6895 | 24.9789 | 24.84 | 24.7379 | 24.6284 | 24.5137 | 24.4 | 24.2832 | 24.1642 | 24.0432 | 23.5211 | 23.0284 | 22.6021
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN PRIMARY | MINIMUM HEADROOM | SU 86304 92972 | NO | YES | 0 | 51.9905 | 51.88 | 51.7568 | 51.5884 | 51.3453 | 51.1284 | 51.3926 | 51.1526 | 50.9032 | 49.88 | 48.8158 | 47.8484 | 49.3716 | 49.2168 | 49.0537 | 48.8474 | 48.5695 | 48.3189 | 47.7484 | 47.0263 | 46.2979 | 44.5 | 43.2674 | 42.1716 | 50.7632 | 50.6526 | 50.5295 | 50.3611 | 50.1179 | 49.9011 | 50.2568 | 50.0168 | 49.7768 | 48.3926 | 47.1568 | 46.0579
|  | HIGH WYCOMBE TOWN PRIMARY | EE |  |  |  |  | 52.5284 | 52.4137 | 52.2905 | 52.1232 | 51.8842 | 51.6642 | 52.0326 | 51.82 | 51.6126 | 51.4189 | 51.2453 | 51.0653 | 50.1611 | 49.9632 | 49.7653 | 49.5326 | 49.2389 | 48.9642 | 49.5589 | 49.2242 | 48.8811 | 47.8147 | 46.8516 | 46.0347 | 51.3937 | 51.2789 | 51.1547 | 50.9874 | 50.7495 | 50.5295 | 50.9558 | 50.7432 | 50.5358 | 50.3421 | 50.1684 | 49.7821
|  | HIGH WYCOMBE TOWN PRIMARY | HT |  |  |  |  | 52.5358 | 52.4284 | 52.2842 | 52.1011 | 51.8811 | 51.6368 | 51.3926 | 51.1526 | 50.9032 | 49.88 | 48.8158 | 47.8484 | 50.1979 | 50.0179 | 49.7579 | 49.4011 | 48.9589 | 48.3958 | 47.7484 | 47.0263 | 46.2979 | 44.5 | 43.2674 | 42.1716 | 51.4011 | 51.2937 | 51.1495 | 50.9653 | 50.7453 | 50.5011 | 50.2568 | 50.0168 | 49.7768 | 48.3926 | 47.1568 | 46.0579
|  | HIGH WYCOMBE TOWN PRIMARY | HE |  |  |  |  | 51.9905 | 51.88 | 51.7568 | 51.5884 | 51.3453 | 51.1284 | 51.4895 | 51.2747 | 51.0653 | 51.0611 | 51.0021 | 50.9621 | 49.3716 | 49.2168 | 49.0537 | 48.8474 | 48.5695 | 48.3189 | 48.9789 | 48.7126 | 48.4516 | 48.1947 | 47.7032 | 47.2147 | 50.7632 | 50.6526 | 50.5295 | 50.3611 | 50.1179 | 49.9011 | 50.3547 | 50.14 | 49.9305 | 49.9263 | 49.8674 | 49.8274
|  | HIGH WYCOMBE TOWN PRIMARY | FB |  |  |  |  | 52.0621 | 52.0021 | 51.9474 | 51.8863 | 51.8189 | 51.7505 | 51.6853 | 51.6232 | 51.5568 | 51.3158 | 51.7505 | 51.6632 | 49.4842 | 49.3674 | 49.2768 | 49.18 | 49.0768 | 48.9726 | 48.8674 | 48.76 | 48.6495 | 48.1842 | 48.6084 | 48.0442 | 50.8347 | 50.7747 | 50.72 | 50.6589 | 50.5916 | 50.5232 | 50.4579 | 50.3958 | 50.3295 | 50.0884 | 50.6158 | 50.5284
IVER 66KV GSP |  | HILLINGDON PRIMARY | MINIMUM HEADROOM | TQ 07470 82827 | NO | NO | 0 | 49.2924 | 48.944 | 48.5429 | 47.9914 | 47.3019 | 46.6051 | 44.5493 | 42.1335 | 39.7251 | 33.8882 | 30.2019 | 26.8787 | 46.8598 | 46.4893 | 45.9598 | 43.7987 | 44.3208 | 42.6219 | 39.944 | 37.2261 | 34.5156 | 27.9556 | 23.8103 | 20.0682 | 43.1787 | 42.8314 | 42.4303 | 41.8777 | 41.1882 | 40.4914 | 39.8387 | 38.1556 | 35.4514 | 28.9051 | 24.7682 | 21.0345
|  | HILLINGDON PRIMARY | EE |  |  |  |  | 49.2924 | 48.944 | 48.5472 | 48.0166 | 47.3019 | 46.6051 | 45.9524 | 44.8051 | 43.6177 | 43.9693 | 41.3787 | 39.1314 | 46.8598 | 46.4893 | 46.0608 | 45.504 | 44.3208 | 42.8977 | 41.5608 | 40.2208 | 38.9219 | 39.5798 | 36.6061 | 34.0208 | 43.1787 | 42.8314 | 42.4335 | 41.904 | 41.1882 | 40.4914 | 39.8387 | 39.1735 | 38.5177 | 40.4966 | 37.5314 | 34.9535
|  | HILLINGDON PRIMARY | HT |  |  |  |  | 49.3051 | 48.9756 | 48.5429 | 47.9914 | 49.2682 | 46.9187 | 44.5493 | 42.1335 | 39.7251 | 33.8882 | 30.2019 | 26.8787 | 46.8724 | 46.504 | 45.9598 | 43.7987 | 45.3093 | 42.6219 | 39.944 | 37.2261 | 34.5156 | 27.9556 | 23.8103 | 20.0682 | 43.1924 | 42.8629 | 42.4303 | 41.8777 | 44.3156 | 43.5377 | 40.8661 | 38.1556 | 35.4514 | 28.9051 | 24.7682 | 21.0345
|  | HILLINGDON PRIMARY | HE |  |  |  |  | 49.3587 | 49.0303 | 48.6587 | 48.1482 | 47.4493 | 46.7893 | 46.144 | 45.4851 | 44.8366 | 46.7819 | 45.0324 | 43.4682 | 46.9482 | 46.6051 | 46.2114 | 45.6787 | 44.9598 | 44.2714 | 43.1103 | 41.9387 | 40.804 | 42.8093 | 40.7103 | 38.8651 | 43.2461 | 42.9177 | 42.5461 | 42.0356 | 41.3366 | 40.6766 | 40.0314 | 39.3724 | 38.724 | 41.8935 | 41.6282 | 39.7882
|  | HILLINGDON PRIMARY | FB |  |  |  |  | 49.5956 | 49.4114 | 49.244 | 49.0577 | 48.8503 | 48.6419 | 48.4387 | 48.2503 | 48.0482 | 47.3072 | 49.5608 | 48.0872 | 47.2103 | 47.0124 | 46.8335 | 46.6324 | 46.4124 | 46.1893 | 45.9703 | 45.7672 | 45.5493 | 43.5756 | 45.7535 | 44.0261 | 43.4829 | 43.2987 | 43.1314 | 42.9451 | 42.7377 | 42.5293 | 42.3261 | 42.1377 | 41.9356 | 41.1945 | 43.8851 | 43.6219
LOVEDEAN GSP | PORTSMOUTH BSP | HILSEA PRIMARY | MINIMUM HEADROOM | SU 66394 03806 | NO | YES | 0 | 25.1413 | 25.1298 | 25.1182 | 25.1024 | 25.1298 | 25.1235 | 25.1182 | 25.1129 | 25.1066 | 41.7919 | 41.7613 | 41.6698 | 22.7277 | 22.7119 | 22.6971 | 22.6782 | 22.715 | 22.7066 | 22.7003 | 22.6929 | 22.6856 | 39.3129 | 39.2508 | 39.1971 | 24.775 | 24.7635 | 24.7519 | 24.7361 | 24.7635 | 24.7571 | 24.7519 | 24.7466 | 24.7403 | 41.4256 | 41.3013 | 41.1919
|  | HILSEA PRIMARY | EE |  |  |  |  | 25.1413 | 25.1298 | 25.1182 | 25.1024 | 41.9224 | 41.9024 | 41.8835 | 41.8635 | 41.8435 | 41.8266 | 41.7898 | 41.7077 | 22.7277 | 22.7119 | 22.6971 | 22.6782 | 39.4961 | 39.474 | 39.4466 | 39.4182 | 39.3898 | 39.3361 | 39.2908 | 39.254 | 24.775 | 24.7635 | 24.7519 | 24.7361 | 41.5561 | 41.5361 | 41.5171 | 41.4971 | 41.4771 | 41.4287 | 41.3182 | 41.2256
|  | HILSEA PRIMARY | HT |  |  |  |  | 25.1424 | 25.1329 | 25.1203 | 25.1035 | 41.9266 | 41.9056 | 41.8845 | 41.8624 | 41.8424 | 41.7919 | 41.7613 | 41.6698 | 22.7298 | 22.7171 | 22.7013 | 22.6824 | 39.5035 | 39.4792 | 39.4571 | 39.4277 | 39.3992 | 39.3129 | 39.2508 | 39.1971 | 24.7761 | 24.7666 | 24.754 | 24.7371 | 41.5603 | 41.5392 | 41.5182 | 41.4961 | 41.4761 | 41.4256 | 41.3013 | 41.1919
|  | HILSEA PRIMARY | HE |  |  |  |  | 25.1435 | 25.134 | 25.1224 | 25.1066 | 41.9266 | 41.9066 | 41.8877 | 41.8666 | 41.8477 | 41.8477 | 41.8445 | 41.8413 | 22.7329 | 22.7224 | 22.7087 | 22.6919 | 39.5098 | 39.4887 | 39.4687 | 39.4466 | 39.4256 | 39.4203 | 39.4013 | 39.3845 | 24.7771 | 24.7677 | 24.7561 | 24.7403 | 41.5603 | 41.5403 | 41.5213 | 41.5003 | 41.4813 | 41.4813 | 41.4782 | 41.475
|  | HILSEA PRIMARY | FB |  |  |  |  | 25.1508 | 25.1456 | 25.1403 | 25.135 | 25.1298 | 25.1235 | 25.1182 | 25.1129 | 25.1066 | 41.9277 | 41.9161 | 41.9087 | 22.7424 | 22.735 | 22.7287 | 22.7213 | 22.715 | 22.7066 | 22.7003 | 22.6929 | 22.6856 | 39.5003 | 39.4708 | 39.4445 | 24.7845 | 24.7792 | 24.774 | 24.7687 | 24.7635 | 24.7571 | 24.7519 | 24.7466 | 24.7403 | 41.5613 | 41.5498 | 41.5424
MANNINGTON GSP | ARNEWOOD BSP | HINCHESLEA PRIMARY | MINIMUM HEADROOM | SU 27805 00447 | NO | YES | 0 | 16.7718 | 16.695 | 16.6045 | 16.4813 | 16.335 | 16.0055 | 15.6708 | 15.3276 | 14.975 | 14.1718 | 13.5824 | 13.0897 | 14.49 | 14.3332 | 14.1142 | 13.8205 | 13.4647 | 13.0879 | 12.7216 | 12.3447 | 11.9574 | 11.0742 | 10.4174 | 9.87 | 15.4947 | 15.3495 | 15.1495 | 14.8811 | 14.5547 | 14.2095 | 13.8737 | 13.5295 | 13.1758 | 12.3705 | 11.7779 | 11.2821
|  | HINCHESLEA PRIMARY | EE |  |  |  |  | 16.7718 | 16.695 | 16.6097 | 16.4961 | 16.3403 | 16.1939 | 16.0603 | 15.9224 | 15.7866 | 15.4824 | 15.0739 | 14.7571 | 14.49 | 14.3332 | 14.1732 | 13.9932 | 13.7837 | 13.5837 | 13.3795 | 13.1732 | 12.9711 | 12.5563 | 12.0911 | 11.7279 | 15.4947 | 15.3495 | 15.2 | 15.0305 | 14.8284 | 14.6358 | 14.4411 | 14.2453 | 14.0537 | 13.6853 | 13.2758 | 12.9558
|  | HINCHESLEA PRIMARY | HT |  |  |  |  | 16.775 | 16.7024 | 16.6045 | 16.4813 | 16.335 | 16.0055 | 15.6708 | 15.3276 | 14.975 | 14.1718 | 13.5824 | 13.0897 | 14.5121 | 14.3342 | 14.1142 | 13.8205 | 13.4647 | 13.0879 | 12.7216 | 12.3447 | 11.9574 | 11.0742 | 10.4174 | 9.87 | 15.5137 | 15.3516 | 15.1495 | 14.8811 | 14.5547 | 14.2095 | 13.8737 | 13.5295 | 13.1758 | 12.3705 | 11.7779 | 11.2821
|  | HINCHESLEA PRIMARY | HE |  |  |  |  | 16.795 | 16.7276 | 16.6497 | 16.5424 | 16.3908 | 16.255 | 16.1234 | 15.9876 | 15.8561 | 15.8666 | 15.8371 | 15.6466 | 14.5384 | 14.4711 | 14.3816 | 14.2353 | 14.0489 | 13.8795 | 13.7153 | 13.5479 | 13.3868 | 13.2447 | 12.9468 | 12.7247 | 15.5705 | 15.4968 | 15.3842 | 15.2442 | 15.0621 | 14.8979 | 14.7379 | 14.5758 | 14.4189 | 14.2989 | 14.0421 | 13.8505
|  | HINCHESLEA PRIMARY | FB |  |  |  |  | 16.8476 | 16.815 | 16.7855 | 16.7529 | 16.7161 | 16.6792 | 16.6434 | 16.6097 | 16.5739 | 16.4434 | 16.3708 | 16.1887 | 14.5911 | 14.5584 | 14.5289 | 14.4847 | 14.4132 | 14.3405 | 14.2711 | 14.2026 | 14.1342 | 13.8426 | 13.5279 | 13.2753 | 15.6232 | 15.5905 | 15.5505 | 15.4874 | 15.4211 | 15.3537 | 15.2884 | 15.2263 | 15.1621 | 14.8937 | 14.6147 | 14.3926
FLEET-BRAMLEY GSP | ALDERSHOT BSP | HINDHEAD PRIMARY | MINIMUM HEADROOM | SU 88631 36479 | NO | YES | 0.21053 | 25.3253 | 25.1863 | 25.0221 | 24.7958 | 24.3979 | 23.52 | 22.7379 | 21.9263 | 21.0853 | 19.2316 | 18.2063 | 17.2947 | 22.2874 | 21.9968 | 21.5495 | 20.8337 | 19.9989 | 19.0189 | 18.1505 | 17.2474 | 16.3095 | 14.2421 | 13.1063 | 12.0937 | 24.3453 | 24.0758 | 23.6684 | 23.0211 | 22.2526 | 21.2705 | 20.3989 | 19.4926 | 18.5526 | 16.48 | 15.3411 | 14.3253
|  | HINDHEAD PRIMARY | EE |  |  |  |  | 25.3253 | 25.1863 | 25.0253 | 24.8147 | 24.5305 | 24.2558 | 23.9979 | 23.7337 | 23.3779 | 22.4768 | 21.7653 | 21.1537 | 22.2874 | 21.9968 | 21.68 | 21.2179 | 20.6989 | 20.1589 | 19.7811 | 19.3905 | 18.9842 | 17.9568 | 17.1463 | 16.4495 | 24.3453 | 24.0758 | 23.7811 | 23.3526 | 22.8674 | 22.3653 | 22.0042 | 21.6305 | 21.2389 | 20.2074 | 19.3947 | 18.6958
|  | HINDHEAD PRIMARY | HT |  |  |  |  | 25.3316 | 25.1979 | 25.0221 | 24.7958 | 24.3979 | 23.52 | 22.7379 | 21.9263 | 21.0853 | 19.2316 | 18.2063 | 17.2947 | 22.34 | 22.0032 | 21.5495 | 20.8337 | 19.9989 | 19.0189 | 18.1505 | 17.2474 | 16.3095 | 14.2421 | 13.1063 | 12.0937 | 24.3916 | 24.0832 | 23.6684 | 23.0211 | 22.2526 | 21.2705 | 20.3989 | 19.4926 | 18.5526 | 16.48 | 15.3411 | 14.3253
|  | HINDHEAD PRIMARY | HE |  |  |  |  | 25.3642 | 25.2326 | 25.0821 | 24.8768 | 24.5989 | 24.3368 | 24.0811 | 23.8221 | 23.5663 | 23.5137 | 23.0684 | 22.6853 | 22.5 | 22.2874 | 22.0453 | 21.6368 | 21.1611 | 20.6695 | 20.3558 | 20.0316 | 19.6884 | 19.1263 | 18.6095 | 18.1642 | 24.5042 | 24.3326 | 24.1032 | 23.7232 | 23.2747 | 22.8158 | 22.5105 | 22.1958 | 21.8642 | 21.3821 | 20.8632 | 20.4147
|  | HINDHEAD PRIMARY | FB |  |  |  |  | 25.4632 | 25.4011 | 25.3453 | 25.2832 | 25.2137 | 25.1421 | 25.0747 | 25.0105 | 24.9421 | 24.6937 | 24.5337 | 24.1063 | 22.6979 | 22.5358 | 22.4074 | 22.2274 | 22.0421 | 21.8274 | 21.6979 | 21.5716 | 21.4274 | 20.8 | 20.1537 | 19.6674 | 24.6095 | 24.5411 | 24.4516 | 24.2884 | 24.1189 | 23.9242 | 23.8032 | 23.6853 | 23.5526 | 22.9779 | 22.4021 | 21.9211
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL PRIMARY | MINIMUM HEADROOM | SU 00702 06030 | YES | YES | 0 | 6.6095 | 6.5632 | 6.4926 | 6.3989 | 6.2832 | 6.1589 | 6.0337 | 5.9074 | 5.7842 | 5.5242 | 5.3274 | 5.1484 | 6.2189 | 6.1768 | 6.1126 | 6.0295 | 5.9253 | 5.8147 | 5.7032 | 5.5905 | 5.4811 | 5.2168 | 4.9947 | 4.7937 | 6.2537 | 6.2021 | 6.1242 | 6.0211 | 5.8937 | 5.7558 | 5.6189 | 5.4779 | 5.3421 | 5.0853 | 4.8663 | 4.6674
|  | HINTON MARTELL PRIMARY | EE |  |  |  |  | 6.6095 | 6.5632 | 6.5116 | 6.4505 | 6.38 | 6.3105 | 6.2411 | 6.1716 | 6.1053 | 5.9474 | 5.8579 | 5.7421 | 6.2189 | 6.1768 | 6.1295 | 6.0737 | 6.0074 | 5.9421 | 5.8779 | 5.8147 | 5.7537 | 5.6168 | 5.5874 | 5.4653 | 6.2537 | 6.2032 | 6.1463 | 6.0811 | 6.0053 | 5.9305 | 5.8558 | 5.7821 | 5.7105 | 5.5316 | 5.4611 | 5.3305
|  | HINTON MARTELL PRIMARY | HT |  |  |  |  | 6.6158 | 6.5632 | 6.4926 | 6.3989 | 6.2832 | 6.1589 | 6.0337 | 5.9074 | 5.7842 | 5.5242 | 5.3274 | 5.1484 | 6.2242 | 6.1768 | 6.1126 | 6.0295 | 5.9253 | 5.8147 | 5.7032 | 5.5905 | 5.4811 | 5.2168 | 4.9947 | 4.7937 | 6.26 | 6.2021 | 6.1242 | 6.0211 | 5.8937 | 5.7558 | 5.6189 | 5.4779 | 5.3421 | 5.0853 | 4.8663 | 4.6674
|  | HINTON MARTELL PRIMARY | HE |  |  |  |  | 6.6389 | 6.6021 | 6.5611 | 6.5063 | 6.4421 | 6.38 | 6.32 | 6.2589 | 6.2 | 6.0989 | 5.9989 | 5.9189 | 6.2442 | 6.2105 | 6.1726 | 6.1221 | 6.0621 | 6.0032 | 5.9484 | 5.8916 | 5.8358 | 5.7516 | 5.6674 | 5.5989 | 6.2863 | 6.2474 | 6.2021 | 6.1442 | 6.0747 | 6.0084 | 5.9453 | 5.8811 | 5.8168 | 5.7 | 5.5853 | 5.4926
|  | HINTON MARTELL PRIMARY | FB |  |  |  |  | 6.6632 | 6.6389 | 6.6189 | 6.5968 | 6.5716 | 6.5474 | 6.5242 | 6.4989 | 6.4737 | 6.3663 | 6.2758 | 6.1947 | 6.2674 | 6.2453 | 6.2274 | 6.2074 | 6.1842 | 6.1632 | 6.1421 | 6.1189 | 6.0958 | 6.0011 | 5.9211 | 5.8516 | 6.3126 | 6.2853 | 6.2642 | 6.2389 | 6.2116 | 6.1853 | 6.16 | 6.1326 | 6.1042 | 5.9853 | 5.8832 | 5.7916
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HITCHES LANE PRIMARY | MINIMUM HEADROOM | SU 79461 54769 | NO | YES | 0 | 45.0021 | 44.56 | 44.0389 | 43.2537 | 42.4737 | 41.3884 | 40.1947 | 38.9663 | 37.7474 | 31.1116 | 29.1095 | 27.3074 | 33.9916 | 33.4168 | 32.7411 | 31.7 | 30.6768 | 29.3958 | 28.1189 | 26.8021 | 25.4958 | 18.2042 | 16.0453 | 14.1 | 39.4853 | 38.9189 | 38.2547 | 37.2305 | 36.2032 | 34.9432 | 33.6863 | 32.3926 | 31.1084 | 23.98 | 21.86 | 19.9505
|  | HITCHES LANE PRIMARY | EE |  |  |  |  | 45.0021 | 44.56 | 44.0926 | 43.5558 | 42.9547 | 42.3674 | 41.7842 | 41.1905 | 40.6116 | 37.58 | 36.1768 | 34.9663 | 33.9916 | 33.4168 | 32.8263 | 32.1737 | 31.4937 | 30.8274 | 30.1505 | 29.4621 | 28.7947 | 25.3253 | 23.7895 | 22.46 | 39.4853 | 38.9189 | 38.3368 | 37.6926 | 37.0179 | 36.3568 | 35.6874 | 35.0053 | 34.3432 | 30.9379 | 29.4347 | 28.1358
|  | HITCHES LANE PRIMARY | HT |  |  |  |  | 45.0684 | 44.6516 | 44.0389 | 43.2537 | 42.4737 | 41.3884 | 40.1947 | 38.9663 | 37.7474 | 31.1116 | 29.1095 | 27.3074 | 34.0905 | 33.5526 | 32.7411 | 31.7 | 30.6768 | 29.3958 | 28.1189 | 26.8021 | 25.4958 | 18.2042 | 16.0453 | 14.1 | 39.5821 | 39.0526 | 38.2547 | 37.2305 | 36.2032 | 34.9432 | 33.6863 | 32.3926 | 31.1084 | 23.98 | 21.86 | 19.9505
|  | HITCHES LANE PRIMARY | HE |  |  |  |  | 45.2284 | 44.8611 | 44.4653 | 43.98 | 43.4137 | 42.8768 | 42.3558 | 41.8295 | 41.3147 | 39.3095 | 38.3779 | 37.5684 | 34.3232 | 33.8663 | 33.3842 | 32.8147 | 32.1905 | 31.5968 | 31.0242 | 30.4442 | 29.88 | 27.2116 | 26.1779 | 25.2789 | 39.8095 | 39.3589 | 38.8821 | 38.3189 | 37.6989 | 37.1084 | 36.54 | 35.9632 | 35.4021 | 32.7853 | 31.7768 | 30.9
|  | HITCHES LANE PRIMARY | FB |  |  |  |  | 45.5537 | 45.3158 | 45.1263 | 44.9274 | 44.7305 | 44.5347 | 44.3453 | 44.1611 | 43.9705 | 43.1695 | 42.5453 | 41.8811 | 34.7453 | 34.4284 | 34.1821 | 33.9263 | 33.6853 | 33.4442 | 33.2105 | 32.9811 | 32.7474 | 31.7211 | 30.8242 | 29.9137 | 40.2253 | 39.9126 | 39.6705 | 39.4189 | 39.1811 | 38.9432 | 38.7126 | 38.4863 | 38.2547 | 37.2442 | 36.3453 | 35.4547
LOVEDEAN GSP | FAREHAM (MAIN) BSP | HOEFORD PRIMARY | MINIMUM HEADROOM | SU 57855 04433 | NO | YES | 1.0516 | 20.0737 | 19.9116 | 19.7274 | 19.4632 | 47.6537 | 47.3126 | 46.9789 | 46.6495 | 46.2074 | 36.7263 | 28.6284 | 24.5537 | 15.0874 | 14.9021 | 14.6895 | 14.3737 | 40.7168 | 40.3221 | 39.9474 | 39.5716 | 39.1842 | 30.1242 | 20.6632 | 15.9484 | 19.6874 | 19.3747 | 18.9905 | 18.3779 | 45.3432 | 44.6326 | 44.0137 | 43.3726 | 42.66 | 31.0811 | 21.6168 | 16.9011
|  | HOEFORD PRIMARY | EE |  |  |  |  | 20.0737 | 19.9116 | 19.7305 | 19.4916 | 47.6716 | 47.3684 | 47.0832 | 46.7916 | 46.5042 | 43.38 | 42.2726 | 38.2821 | 15.0874 | 14.9021 | 14.7011 | 14.4368 | 40.7926 | 40.4747 | 40.1674 | 39.8558 | 39.5484 | 37.0674 | 37.4253 | 32.6463 | 19.6874 | 19.3747 | 19.0579 | 18.6453 | 45.76 | 45.3537 | 44.92 | 44.4863 | 44.0663 | 38.9811 | 38.7874 | 34.0063
|  | HOEFORD PRIMARY | HT |  |  |  |  | 20.0842 | 19.9284 | 19.7274 | 19.4632 | 47.6537 | 47.3126 | 46.9789 | 46.6495 | 46.2074 | 36.7263 | 28.6284 | 24.5537 | 15.1021 | 14.9211 | 14.6895 | 14.3737 | 40.7168 | 40.3221 | 39.9474 | 39.5716 | 39.1842 | 30.1242 | 20.6632 | 15.9484 | 19.6968 | 19.4 | 18.9905 | 18.3779 | 45.3432 | 44.6326 | 44.0137 | 43.3726 | 42.66 | 31.0811 | 21.6168 | 16.9011
|  | HOEFORD PRIMARY | HE |  |  |  |  | 20.12 | 19.9716 | 19.8074 | 19.58 | 47.7642 | 47.4789 | 47.2 | 46.9158 | 46.6379 | 44.6316 | 43.8368 | 40.1705 | 15.1589 | 14.9979 | 14.8232 | 14.5779 | 40.9432 | 40.6484 | 40.3589 | 40.0653 | 39.7779 | 38.32 | 39.1916 | 34.7789 | 19.7305 | 19.5832 | 19.4211 | 19.0937 | 46.2484 | 45.8968 | 45.5442 | 45.1958 | 44.8589 | 40.4253 | 40.54 | 36.1263
|  | HOEFORD PRIMARY | FB |  |  |  |  | 20.2347 | 20.1547 | 20.0853 | 20.0084 | 48.42 | 48.3326 | 48.2484 | 48.1716 | 48.0884 | 47.7284 | 45.6632 | 42.3179 | 15.2853 | 15.1895 | 15.1105 | 15.0242 | 41.62 | 41.5211 | 41.4263 | 41.3389 | 41.2474 | 40.7526 | 39.3505 | 36.0053 | 19.8432 | 19.7653 | 19.6979 | 19.6221 | 47.0495 | 46.8758 | 46.7253 | 46.5789 | 46.4337 | 45.1516 | 41.4684 | 37.4558
MANNINGTON GSP | LYTCHETT BSP | HOLES BAY PRIMARY | MINIMUM HEADROOM | SZ 00725 91955 | NO | YES | 0 | 22.9558 | 22.8842 | 22.7937 | 22.6484 | 22.4958 | 22.3032 | 22.1168 | 21.9032 | 21.6905 | 21.0589 | 20.5926 | 20.1642 | 21.0189 | 20.8905 | 20.74 | 20.5453 | 20.3579 | 20.1095 | 19.8695 | 19.5821 | 19.2958 | 18.5589 | 18.0063 | 17.5147 | 21.8411 | 21.7116 | 21.5611 | 21.3653 | 21.1768 | 20.9263 | 20.6853 | 20.3958 | 20.1074 | 19.3642 | 18.8063 | 18.3116
|  | HOLES BAY PRIMARY | EE |  |  |  |  | 22.9558 | 22.8842 | 22.8032 | 22.6863 | 22.5568 | 22.4326 | 22.2947 | 22.1547 | 22.0158 | 21.72 | 21.3832 | 21.0863 | 21.0189 | 20.8905 | 20.7558 | 20.6042 | 20.46 | 20.3189 | 20.1495 | 19.9758 | 19.8074 | 19.3547 | 18.9242 | 18.56 | 21.8411 | 21.7116 | 21.5758 | 21.4242 | 21.28 | 21.1379 | 20.9674 | 20.7926 | 20.6232 | 20.1663 | 19.7316 | 19.3632
|  | HOLES BAY PRIMARY | HT |  |  |  |  | 22.9611 | 22.8905 | 22.7937 | 22.6484 | 22.4958 | 22.3032 | 22.1168 | 21.9032 | 21.6905 | 21.0589 | 20.5926 | 20.1642 | 21.0347 | 20.9 | 20.74 | 20.5453 | 20.3579 | 20.1095 | 19.8695 | 19.5821 | 19.2958 | 18.5589 | 18.0063 | 17.5147 | 21.8579 | 21.7221 | 21.5611 | 21.3653 | 21.1768 | 20.9263 | 20.6853 | 20.3958 | 20.1074 | 19.3642 | 18.8063 | 18.3116
|  | HOLES BAY PRIMARY | HE |  |  |  |  | 22.9863 | 22.9274 | 22.8589 | 22.7716 | 22.6611 | 22.5579 | 22.4568 | 22.3558 | 22.2547 | 22.1863 | 22.0316 | 21.8989 | 21.0947 | 21 | 20.8895 | 20.7621 | 20.6326 | 20.5126 | 20.4021 | 20.2895 | 20.1811 | 20.0632 | 19.8126 | 19.5979 | 21.9189 | 21.8232 | 21.7116 | 21.5842 | 21.4537 | 21.3337 | 21.2221 | 21.1105 | 21.0011 | 20.8821 | 20.6284 | 20.4105
|  | HOLES BAY PRIMARY | FB |  |  |  |  | 23.0337 | 23 | 22.9705 | 22.94 | 22.9074 | 22.8758 | 22.8453 | 22.8158 | 22.7853 | 22.6368 | 22.4558 | 22.2947 | 21.1768 | 21.1116 | 21.0568 | 21.0063 | 20.9495 | 20.9 | 20.8526 | 20.8084 | 20.7621 | 20.5526 | 20.2821 | 20.0347 | 22.0011 | 21.9347 | 21.88 | 21.8284 | 21.7716 | 21.7221 | 21.6747 | 21.6295 | 21.5832 | 21.3726 | 21.1 | 20.8495
MELKSHAM GSP | FROME BSP | HOLWELL PRIMARY | MINIMUM HEADROOM | ST 72191 44633 | NO | YES | 1.0516 | 13.9129 | 13.8603 | 13.8076 | 13.7476 | 13.6739 | 13.6045 | 13.5339 | 13.4603 | 13.3897 | 11.0845 | 10.9613 | 10.8329 | 12.6521 | 12.5953 | 12.5395 | 12.4753 | 12.3974 | 12.3258 | 12.2511 | 12.1721 | 12.0984 | 10.4058 | 10.2711 | 10.13 | 13.1832 | 13.1284 | 13.0737 | 13.0116 | 12.9347 | 12.8642 | 12.7916 | 12.7147 | 12.6421 | 10.4411 | 10.2989 | 10.1495
|  | HOLWELL PRIMARY | EE |  |  |  |  | 13.9129 | 13.8603 | 13.8076 | 13.7476 | 13.6739 | 13.6045 | 13.5339 | 13.4603 | 13.3908 | 11.0845 | 10.9613 | 10.8329 | 12.6521 | 12.5953 | 12.5395 | 12.4753 | 12.3974 | 12.3258 | 12.2511 | 12.1721 | 12.0984 | 10.4058 | 10.2711 | 10.13 | 13.1832 | 13.1284 | 13.0737 | 13.0116 | 12.9347 | 12.8642 | 12.7916 | 12.7147 | 12.6421 | 10.4411 | 10.2989 | 10.1495
|  | HOLWELL PRIMARY | HT |  |  |  |  | 13.9234 | 13.875 | 13.8213 | 13.7603 | 13.6908 | 13.6182 | 13.5466 | 13.4697 | 13.3897 | 11.4055 | 11.2213 | 11.0361 | 12.6647 | 12.6121 | 12.5553 | 12.4911 | 12.4174 | 12.3426 | 12.2679 | 12.1858 | 12.1016 | 10.6321 | 10.4268 | 10.2184 | 13.1947 | 13.1442 | 13.0884 | 13.0253 | 12.9537 | 12.88 | 12.8063 | 12.7263 | 12.6442 | 10.7568 | 10.5495 | 10.3389
|  | HOLWELL PRIMARY | HE |  |  |  |  | 13.9487 | 13.9097 | 13.8676 | 13.8171 | 13.7518 | 13.6908 | 13.6329 | 13.5729 | 13.515 | 12.6129 | 12.5466 | 12.4655 | 12.6932 | 12.6521 | 12.6068 | 12.5553 | 12.4868 | 12.4237 | 12.3647 | 12.3026 | 12.2426 | 11.6005 | 11.5237 | 11.4289 | 13.2221 | 13.1821 | 13.1379 | 13.0863 | 13.02 | 12.9579 | 12.8989 | 12.8379 | 12.7789 | 11.9358 | 11.8632 | 11.7737
|  | HOLWELL PRIMARY | FB |  |  |  |  | 13.9803 | 13.9518 | 13.9308 | 13.9055 | 13.8824 | 13.8592 | 13.8361 | 13.8129 | 13.7897 | 13.6992 | 13.6118 | 13.5224 | 12.7268 | 12.6963 | 12.6732 | 12.6458 | 12.6205 | 12.5953 | 12.57 | 12.5447 | 12.5205 | 12.4205 | 12.3226 | 12.2195 | 13.2547 | 13.2253 | 13.2032 | 13.1768 | 13.1526 | 13.1284 | 13.1032 | 13.0789 | 13.0547 | 12.9589 | 12.8653 | 12.7684
MANNINGTON GSP | SALISBURY BSP | HOMINGTON PRIMARY | MINIMUM HEADROOM | SU 11742 26037 | NO | YES | 9.4737 | 4.3824 | 4.3076 | 4.235 | 4.1424 | 4.0182 | 3.8792 | 3.735 | 3.5792 | 3.4161 | 2.0192 | 1.7824 | 1.5792 | 3.4521 | 3.3647 | 3.2805 | 3.1763 | 3.0332 | 2.8732 | 2.7026 | 2.5163 | 2.3205 | 0.36789 | 0.055263 | -0.21526 | 5.0853 | 4.9989 | 4.9147 | 4.8095 | 4.6663 | 4.5063 | 4.3368 | 4.1516 | 3.9558 | 2.0084 | 1.6968 | 1.4274
|  | HOMINGTON PRIMARY | EE |  |  |  |  | 4.3824 | 4.3076 | 4.235 | 4.1497 | 4.0455 | 3.9466 | 3.8497 | 3.7497 | 3.6539 | 2.0192 | 1.7824 | 1.5792 | 3.4521 | 3.3647 | 3.2805 | 3.1847 | 3.0721 | 2.9637 | 2.8563 | 2.7458 | 2.6395 | 0.36789 | 0.055263 | -0.21526 | 5.0853 | 4.9989 | 4.9147 | 4.8189 | 4.7053 | 4.5979 | 4.4905 | 4.38 | 4.2737 | 2.0084 | 1.6968 | 1.4274
|  | HOMINGTON PRIMARY | HT |  |  |  |  | 4.395 | 4.3287 | 4.2466 | 4.1424 | 4.0182 | 3.8792 | 3.735 | 3.5792 | 3.4161 | 2.9782 | 2.6329 | 2.3245 | 3.47 | 3.3921 | 3.2974 | 3.1763 | 3.0332 | 2.8732 | 2.7026 | 2.5163 | 2.3205 | 1.7816 | 1.3437 | 0.95 | 5.1032 | 5.0253 | 4.9305 | 4.8095 | 4.6663 | 4.5063 | 4.3368 | 4.1516 | 3.9558 | 3.4179 | 2.9811 | 2.5874
|  | HOMINGTON PRIMARY | HE |  |  |  |  | 4.4297 | 4.3761 | 4.3171 | 4.2445 | 4.1518 | 4.0655 | 3.9813 | 3.8982 | 3.8161 | 2.3013 | 2.1382 | 1.995 | 3.5142 | 3.4532 | 3.3879 | 3.31 | 3.21 | 3.1195 | 3.0289 | 2.9405 | 2.8553 | 0.72895 | 0.50474 | 0.30579 | 5.1474 | 5.0863 | 5.0211 | 4.9432 | 4.8442 | 4.7526 | 4.6621 | 4.5737 | 4.4884 | 2.3684 | 2.1453 | 1.9474
|  | HOMINGTON PRIMARY | FB |  |  |  |  | 4.4718 | 4.435 | 4.4055 | 4.3729 | 4.3392 | 4.3055 | 4.2729 | 4.2413 | 4.2097 | 4.0655 | 3.9087 | 3.775 | 3.5626 | 3.5174 | 3.4826 | 3.4437 | 3.4047 | 3.3658 | 3.3279 | 3.29 | 3.2542 | 3.0784 | 2.8753 | 2.6963 | 5.1947 | 5.1505 | 5.1147 | 5.0768 | 5.0379 | 4.9989 | 4.9611 | 4.9242 | 4.8874 | 4.7126 | 4.5095 | 4.3316
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HOOK PRIMARY | MINIMUM HEADROOM | SU 72602 53780 | NO | YES | 0 | 33.0889 | 32.9395 | 32.7668 | 32.53 | 32.2426 | 31.7216 | 31.0279 | 30.3121 | 29.6016 | 27.9689 | 26.7932 | 25.7553 | 25.3389 | 25.0263 | 24.6821 | 24.1126 | 23.4084 | 22.6421 | 21.8821 | 21.0968 | 20.3179 | 18.5305 | 17.2253 | 16.0716 | 31.08 | 30.7789 | 30.4463 | 29.8863 | 29.1916 | 28.4358 | 27.6853 | 26.9105 | 26.1421 | 24.3516 | 23.0421 | 21.8853
|  | HOOK PRIMARY | EE |  |  |  |  | 33.0889 | 32.9395 | 32.7711 | 32.5458 | 32.2447 | 31.9511 | 31.6753 | 31.3974 | 31.1226 | 30.4321 | 29.6374 | 28.9426 | 25.3389 | 25.0263 | 24.7126 | 24.3579 | 23.9253 | 23.5011 | 23.0674 | 22.6337 | 22.2105 | 21.3021 | 20.4074 | 19.6158 | 31.08 | 30.7789 | 30.4747 | 30.1274 | 29.6968 | 29.2758 | 28.8453 | 28.4158 | 27.9947 | 27.1021 | 26.2253 | 25.44
|  | HOOK PRIMARY | HT |  |  |  |  | 33.0953 | 32.9542 | 32.7668 | 32.53 | 32.2426 | 31.7216 | 31.0279 | 30.3121 | 29.6016 | 27.9689 | 26.7932 | 25.7553 | 25.4021 | 25.12 | 24.6821 | 24.1126 | 23.4084 | 22.6421 | 21.8821 | 21.0968 | 20.3179 | 18.5305 | 17.2253 | 16.0716 | 31.14 | 30.8674 | 30.4463 | 29.8863 | 29.1916 | 28.4358 | 27.6853 | 26.9105 | 26.1421 | 24.3516 | 23.0421 | 21.8853
|  | HOOK PRIMARY | HE |  |  |  |  | 33.1268 | 32.99 | 32.83 | 32.6089 | 32.3142 | 32.0353 | 31.7637 | 31.4858 | 31.2142 | 31.2247 | 31.0384 | 30.5911 | 25.5611 | 25.34 | 25.0989 | 24.8021 | 24.4147 | 24.0432 | 23.6863 | 23.3211 | 22.9684 | 22.5716 | 21.9695 | 21.4505 | 31.2137 | 31.0737 | 30.8389 | 30.5474 | 30.1663 | 29.8011 | 29.4505 | 29.0895 | 28.7389 | 28.3505 | 27.7611 | 27.2526
|  | HOOK PRIMARY | FB |  |  |  |  | 33.2342 | 33.1679 | 33.1089 | 33.0416 | 32.9679 | 32.8921 | 32.8195 | 32.7521 | 32.6795 | 32.4142 | 32.2668 | 31.8511 | 25.7484 | 25.5768 | 25.4505 | 25.3137 | 25.1611 | 25.0105 | 24.8632 | 24.72 | 24.5747 | 23.94 | 23.3053 | 22.7526 | 31.3211 | 31.2547 | 31.1853 | 31.0537 | 30.9063 | 30.7611 | 30.6189 | 30.4811 | 30.3411 | 29.7147 | 29.0905 | 28.5484
LALEHAM GSP | EAST BEDFONT BSP | HOPE AND ANCHOR PRIMARY | MINIMUM HEADROOM | TQ 12710 72057 | YES | YES | 0 | 1.7253 | 1.6968 | 1.66 | 1.6116 | 1.5547 | 1.4821 | 1.4021 | 1.2316 | 1.0368 | 0.60421 | 0.25368 | -0.088421 | 1.4842 | 1.4232 | 1.3526 | 1.2726 | 1.1453 | 0.97368 | 0.76632 | 0.55474 | 0.33895 | -0.14211 | -0.53579 | -0.92105 | 1.5242 | 1.4958 | 1.4589 | 1.4105 | 1.2958 | 1.1242 | 0.91579 | 0.70421 | 0.48737 | 0.011579 | -0.37789 | -0.75895
|  | HOPE AND ANCHOR PRIMARY | EE |  |  |  |  | 1.7263 | 1.6968 | 1.6642 | 1.6189 | 1.56 | 1.5 | 1.4442 | 1.3853 | 1.3263 | 1.2663 | 1.0947 | 0.88632 | 1.4884 | 1.4232 | 1.3568 | 1.2821 | 1.1958 | 1.1084 | 1.0253 | 0.93895 | 0.85474 | 0.66421 | 0.41368 | 0.17789 | 1.5253 | 1.4958 | 1.4632 | 1.4179 | 1.3463 | 1.2589 | 1.1747 | 1.0895 | 1.0053 | 0.81263 | 0.56211 | 0.32632
|  | HOPE AND ANCHOR PRIMARY | HT |  |  |  |  | 1.7253 | 1.6979 | 1.66 | 1.6116 | 1.5547 | 1.4821 | 1.4021 | 1.2316 | 1.0368 | 0.60421 | 0.25368 | -0.088421 | 1.4842 | 1.4232 | 1.3526 | 1.2726 | 1.1453 | 0.97368 | 0.76632 | 0.55474 | 0.33895 | -0.14211 | -0.53579 | -0.92105 | 1.5242 | 1.4968 | 1.4589 | 1.4105 | 1.2958 | 1.1242 | 0.91579 | 0.70421 | 0.48737 | 0.011579 | -0.37789 | -0.75895
|  | HOPE AND ANCHOR PRIMARY | HE |  |  |  |  | 1.7284 | 1.6989 | 1.6653 | 1.6179 | 1.5547 | 1.4937 | 1.4347 | 1.3779 | 1.32 | 1.3221 | 1.2937 | 1.2147 | 1.5042 | 1.4737 | 1.4221 | 1.3558 | 1.2737 | 1.1937 | 1.1179 | 1.0474 | 0.97368 | 0.89053 | 0.71474 | 0.54421 | 1.5274 | 1.4979 | 1.4642 | 1.4168 | 1.3537 | 1.2926 | 1.2337 | 1.1768 | 1.1189 | 1.0411 | 0.86421 | 0.69368
|  | HOPE AND ANCHOR PRIMARY | FB |  |  |  |  | 1.7495 | 1.7337 | 1.7189 | 1.7011 | 1.6832 | 1.6642 | 1.6453 | 1.6295 | 1.6105 | 1.5442 | 1.5 | 1.4611 | 1.5274 | 1.5105 | 1.4947 | 1.4758 | 1.4463 | 1.4116 | 1.3768 | 1.3453 | 1.3116 | 1.1674 | 1.0042 | 0.85263 | 1.5484 | 1.5326 | 1.5179 | 1.5 | 1.4821 | 1.4632 | 1.4442 | 1.4284 | 1.4095 | 1.3179 | 1.1547 | 1.0032
LOVEDEAN GSP | HAVANT BSP | HORNDEAN PRIMARY | MINIMUM HEADROOM | SU 70271 12802 | NO | YES | 0 | 33.8258 | 32.8121 | 31.5005 | 29.8563 | 56.2821 | 54.2621 | 52.2495 | 48.6958 | 46.6832 | 42.1905 | 39.2242 | 36.2674 | 24.9663 | 23.7589 | 22.2126 | 20.3716 | 44.9232 | 42.6716 | 40.4295 | 36.3674 | 34.1221 | 29.1232 | 25.8063 | 22.4779 | 25.9021 | 24.72 | 23.2063 | 21.4042 | 46.8979 | 44.6916 | 42.4937 | 38.5305 | 36.3295 | 31.4284 | 28.18 | 24.9232
|  | HORNDEAN PRIMARY | EE |  |  |  |  | 33.8258 | 32.8121 | 31.6268 | 30.4868 | 57.5295 | 56.3337 | 55.1568 | 53.2105 | 52.0789 | 49.9305 | 47.9589 | 45.9811 | 24.9663 | 23.7589 | 22.3558 | 21.1032 | 46.3905 | 45.1011 | 43.8242 | 41.6453 | 40.4242 | 37.9726 | 35.7221 | 33.4474 | 25.9021 | 24.72 | 23.3463 | 22.1158 | 48.3221 | 47.0516 | 45.7947 | 43.66 | 42.4568 | 40.0632 | 37.8663 | 35.6484
|  | HORNDEAN PRIMARY | HT |  |  |  |  | 33.9374 | 32.9458 | 31.5005 | 29.8563 | 56.2821 | 54.2621 | 52.2495 | 48.6958 | 46.6832 | 42.1905 | 39.2242 | 36.2674 | 25.1074 | 23.9253 | 22.2126 | 20.3716 | 44.9232 | 42.6716 | 40.4295 | 36.3674 | 34.1221 | 29.1232 | 25.8063 | 22.4779 | 26.0389 | 24.8811 | 23.2063 | 21.4042 | 46.8979 | 44.6916 | 42.4937 | 38.5305 | 36.3295 | 31.4284 | 28.18 | 24.9232
|  | HORNDEAN PRIMARY | HE |  |  |  |  | 34.25 | 33.4005 | 32.3721 | 31.4089 | 58.5537 | 57.4768 | 56.42 | 54.5968 | 53.5905 | 52.4589 | 51.1442 | 49.7179 | 25.4863 | 24.4842 | 23.2621 | 22.1632 | 47.5621 | 46.4053 | 45.2705 | 43.2326 | 42.1558 | 40.8116 | 39.2779 | 37.6074 | 26.4095 | 25.4274 | 24.2305 | 23.1495 | 49.4663 | 48.3253 | 47.2053 | 45.2095 | 44.1463 | 42.8432 | 41.3516 | 39.7284
|  | HORNDEAN PRIMARY | FB |  |  |  |  | 34.7016 | 34.1911 | 33.7205 | 33.3079 | 61.2284 | 60.8021 | 60.3726 | 59.9337 | 59.4937 | 57.9463 | 56.6137 | 55.3189 | 25.9968 | 25.3842 | 24.82 | 24.3326 | 50.5305 | 50.0316 | 49.5274 | 49.0168 | 48.5284 | 46.8168 | 45.3074 | 43.82 | 26.9126 | 26.3126 | 25.7611 | 25.2832 | 52.3905 | 51.9011 | 51.4074 | 50.9063 | 50.4274 | 48.7474 | 47.2726 | 45.8232
NURSLING GSP | WINCHESTER BSP | HOUGHTON PRIMARY | MINIMUM HEADROOM | SU 33784 31741 | NO | YES | 0 | 11.3674 | 11.2568 | 11.0495 | 10.8295 | 10.5947 | 10.4611 | 10.3232 | 10.1811 | 10.0442 | 9.6284 | 7.3474 | 6.9737 | 15.22 | 15.0968 | 14.86 | 14.6105 | 14.3495 | 14.2105 | 14.0621 | 13.9105 | 13.7653 | 13.3179 | 10.5937 | 10.1684 | 10.7368 | 10.6168 | 10.3842 | 10.14 | 9.8832 | 9.7453 | 9.5979 | 9.4484 | 9.3042 | 8.8621 | 6.2105 | 5.7937
|  | HOUGHTON PRIMARY | EE |  |  |  |  | 11.3674 | 11.2653 | 11.0495 | 10.8295 | 10.5947 | 10.4611 | 10.3232 | 10.1811 | 10.0442 | 9.7832 | 8.5653 | 8.3095 | 15.22 | 15.1084 | 14.86 | 14.6105 | 14.3495 | 14.2105 | 14.0621 | 13.9105 | 13.7653 | 13.4632 | 12.0042 | 11.7042 | 10.7368 | 10.6274 | 10.3842 | 10.14 | 9.8832 | 9.7453 | 9.5979 | 9.4484 | 9.3042 | 9.0084 | 7.5884 | 7.2958
|  | HOUGHTON PRIMARY | HT |  |  |  |  | 11.3853 | 11.2568 | 11.0905 | 10.8695 | 10.6474 | 10.5032 | 10.3621 | 10.2105 | 10.0621 | 9.6284 | 7.3474 | 6.9737 | 15.2421 | 15.0968 | 14.9084 | 14.6589 | 14.4116 | 14.26 | 14.1105 | 13.9505 | 13.7926 | 13.3179 | 10.5937 | 10.1684 | 10.7589 | 10.6168 | 10.4316 | 10.1874 | 9.9432 | 9.7937 | 9.6453 | 9.4863 | 9.3305 | 8.8621 | 6.2105 | 5.7937
|  | HOUGHTON PRIMARY | HE |  |  |  |  | 11.4284 | 11.3526 | 11.1632 | 10.9621 | 10.7442 | 10.6274 | 10.5158 | 10.4032 | 10.2916 | 10.2316 | 9.1316 | 8.9726 | 15.2916 | 15.2116 | 14.9926 | 14.7663 | 14.5242 | 14.4042 | 14.2884 | 14.1716 | 14.0558 | 13.98 | 12.6537 | 12.4632 | 10.8074 | 10.7284 | 10.5147 | 10.2916 | 10.0537 | 9.9337 | 9.8189 | 9.7032 | 9.5884 | 9.5147 | 8.2253 | 8.04
|  | HOUGHTON PRIMARY | FB |  |  |  |  | 11.4937 | 11.44 | 11.3705 | 11.2621 | 11.1821 | 11.1326 | 11.0874 | 11.0442 | 10.9989 | 10.8137 | 10.6263 | 10.4526 | 15.3621 | 15.3021 | 15.2221 | 15.0968 | 15.0053 | 14.9516 | 14.9021 | 14.8547 | 14.8053 | 14.6011 | 14.3863 | 14.1832 | 10.8779 | 10.8179 | 10.74 | 10.6179 | 10.5274 | 10.4747 | 10.4263 | 10.3789 | 10.3305 | 10.1295 | 9.9189 | 9.7211
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | HOUNDMILLS PRIMARY | MINIMUM HEADROOM | SU 62187 52886 | NO | YES | 0 | 37.3705 | 37.1726 | 36.9832 | 36.5242 | 35.7295 | 34.9232 | 34.1674 | 33.4063 | 32.6537 | 29.5084 | 28.5653 | 28.0884 | 41.8095 | 41.7105 | 41.5526 | 40.7147 | 39.1968 | 37.6737 | 36.2547 | 34.8232 | 33.4095 | 27.0958 | 25.3484 | 24.5779 | 43.5905 | 43.4989 | 43.3874 | 42.7642 | 41.2589 | 39.7484 | 38.3421 | 36.9221 | 35.52 | 29.2853 | 27.5632 | 26.8021
|  | HOUNDMILLS PRIMARY | EE |  |  |  |  | 37.3705 | 37.1726 | 36.9832 | 36.5547 | 35.8368 | 35.0958 | 34.3495 | 33.6 | 32.8621 | 29.9516 | 29.1874 | 28.8905 | 41.8095 | 41.7105 | 41.5526 | 40.7832 | 39.4484 | 38.0579 | 36.6379 | 35.2158 | 33.8158 | 27.6737 | 26.1474 | 25.6042 | 43.5905 | 43.4989 | 43.3874 | 42.8305 | 41.5063 | 40.1263 | 38.72 | 37.3105 | 35.9211 | 29.8611 | 28.3579 | 27.8211
|  | HOUNDMILLS PRIMARY | HT |  |  |  |  | 37.3916 | 37.2074 | 37 | 36.5242 | 35.7295 | 34.9232 | 34.1674 | 33.4063 | 32.6537 | 29.5084 | 28.5653 | 28.0884 | 41.8179 | 41.7253 | 41.58 | 40.7147 | 39.1968 | 37.6737 | 36.2547 | 34.8232 | 33.4095 | 27.0958 | 25.3484 | 24.5779 | 43.5968 | 43.5147 | 43.3947 | 42.7642 | 41.2589 | 39.7484 | 38.3421 | 36.9221 | 35.52 | 29.2853 | 27.5632 | 26.8021
|  | HOUNDMILLS PRIMARY | HE |  |  |  |  | 37.4379 | 37.2653 | 37.1 | 36.6895 | 35.9811 | 35.2568 | 34.5337 | 33.8063 | 33.0905 | 30.4358 | 29.8179 | 29.7116 | 41.8326 | 41.7389 | 41.6368 | 41.0368 | 39.7232 | 38.36 | 36.9895 | 35.6158 | 34.2663 | 28.5211 | 27.2137 | 27.0053 | 43.6084 | 43.5232 | 43.4253 | 43.0832 | 41.78 | 40.4284 | 39.0695 | 37.7074 | 36.3684 | 30.6968 | 29.4105 | 29.2063
|  | HOUNDMILLS PRIMARY | FB |  |  |  |  | 37.5379 | 37.4379 | 37.3589 | 37.1916 | 36.9232 | 36.6326 | 36.3084 | 35.9611 | 35.5916 | 33.6853 | 33.1716 | 33.0137 | 41.9021 | 41.8547 | 41.8126 | 41.7589 | 41.3011 | 40.7295 | 40.0842 | 39.3884 | 38.6463 | 34.7379 | 33.74 | 33.4684 | 43.6737 | 43.6326 | 43.5947 | 43.5474 | 43.3474 | 42.7811 | 42.1411 | 41.4516 | 40.7158 | 36.8432 | 35.8537 | 35.5842
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | HUNGERFORD PRIMARY | MINIMUM HEADROOM | SU 34066 68957 | NO | YES | 0 | 13.6711 | 13.5574 | 13.4405 | 13.2616 | 13.0511 | 12.8247 | 12.6005 | 12.3563 | 12.1026 | 11.5142 | 11.1153 | 10.7374 | 14.3721 | 14.2279 | 14.0826 | 13.8521 | 13.5847 | 13.2995 | 13.0184 | 12.6995 | 12.3668 | 11.5879 | 11.0479 | 10.5279 | 15.3663 | 15.2221 | 15.0768 | 14.8474 | 14.5811 | 14.2958 | 14.0147 | 13.6968 | 13.3642 | 12.5874 | 12.0484 | 11.5284
|  | HUNGERFORD PRIMARY | EE |  |  |  |  | 13.6711 | 13.5574 | 13.4405 | 13.2984 | 13.1279 | 12.9637 | 12.7932 | 12.6216 | 12.4511 | 12.1721 | 11.9005 | 11.6574 | 14.3721 | 14.2279 | 14.0826 | 13.9142 | 13.7237 | 13.5384 | 13.3363 | 13.1332 | 12.9332 | 12.5247 | 12.1216 | 11.7553 | 15.3663 | 15.2221 | 15.0768 | 14.9095 | 14.7189 | 14.5337 | 14.3305 | 14.1284 | 13.9274 | 13.5221 | 13.1189 | 12.7537
|  | HUNGERFORD PRIMARY | HT |  |  |  |  | 13.6921 | 13.5889 | 13.4479 | 13.2616 | 13.0511 | 12.8247 | 12.6005 | 12.3563 | 12.1026 | 11.5142 | 11.1153 | 10.7374 | 14.4047 | 14.2732 | 14.0921 | 13.8521 | 13.5847 | 13.2995 | 13.0184 | 12.6995 | 12.3668 | 11.5879 | 11.0479 | 10.5279 | 15.3989 | 15.2684 | 15.0874 | 14.8474 | 14.5811 | 14.2958 | 14.0147 | 13.6968 | 13.3642 | 12.5874 | 12.0484 | 11.5284
|  | HUNGERFORD PRIMARY | HE |  |  |  |  | 13.7374 | 13.6479 | 13.5489 | 13.4268 | 13.2658 | 13.1163 | 12.9721 | 12.8247 | 12.6816 | 12.6279 | 12.4879 | 12.3563 | 14.4732 | 14.3679 | 14.2542 | 14.1174 | 13.9416 | 13.7805 | 13.6226 | 13.4637 | 13.3089 | 13.21 | 12.9889 | 12.7774 | 15.4674 | 15.3621 | 15.2484 | 15.1116 | 14.9368 | 14.7747 | 14.6179 | 14.4579 | 14.3042 | 14.2053 | 13.9853 | 13.7737
|  | HUNGERFORD PRIMARY | FB |  |  |  |  | 13.81 | 13.7489 | 13.7005 | 13.6479 | 13.5911 | 13.5353 | 13.4805 | 13.4279 | 13.3753 | 13.1647 | 12.9753 | 12.8058 | 14.5626 | 14.4805 | 14.4184 | 14.3521 | 14.2816 | 14.2111 | 14.1447 | 14.0784 | 14.0132 | 13.7468 | 13.4742 | 13.2184 | 15.5568 | 15.4747 | 15.4126 | 15.3463 | 15.2768 | 15.2063 | 15.1389 | 15.0737 | 15.0084 | 14.7421 | 14.4705 | 14.2158
LOVEDEAN GSP | CHICHESTER BSP | HUNSTON PRIMARY | MINIMUM HEADROOM | SU 86949 02632 | NO | YES | 0.21053 | 33.1632 | 32.9347 | 32.6284 | 32.2232 | 31.5884 | 30.9453 | 28.4842 | 27.7621 | 27.0274 | 21.3789 | 13.5821 | 6.9358 | 29.8158 | 29.5568 | 29.2095 | 28.7505 | 28.0189 | 27.2821 | 24.3895 | 23.5726 | 22.7421 | 16.1242 | 7.0758 | -0.68632 | 29.3432 | 29.0874 | 28.7432 | 28.2874 | 27.5642 | 26.8295 | 23.9358 | 23.1189 | 22.2874 | 15.6663 | 6.6168 | -1.1484
|  | HUNSTON PRIMARY | EE |  |  |  |  | 33.1632 | 32.9947 | 32.7242 | 32.5168 | 32.2053 | 31.8526 | 30.5632 | 30.1716 | 29.7726 | 21.3789 | 16.1011 | 10.7389 | 29.8158 | 29.6316 | 29.3263 | 29.1032 | 28.7653 | 28.3747 | 26.8547 | 26.4158 | 25.9695 | 16.1242 | 9.9474 | 4.3158 | 29.3432 | 29.1611 | 28.8579 | 28.6358 | 28.3 | 27.9126 | 26.4011 | 25.9632 | 25.5158 | 15.6663 | 9.4884 | 4.1947
|  | HUNSTON PRIMARY | HT |  |  |  |  | 33.1905 | 32.9347 | 32.6284 | 32.2232 | 31.5884 | 30.9453 | 28.4842 | 27.7621 | 27.0274 | 23.9695 | 13.5821 | 6.9358 | 29.8474 | 29.5568 | 29.2095 | 28.7505 | 28.0189 | 27.2821 | 24.3895 | 23.5726 | 22.7421 | 19.2253 | 7.0758 | -0.68632 | 29.3747 | 29.0874 | 28.7432 | 28.2874 | 27.5642 | 26.8295 | 23.9358 | 23.1189 | 22.2874 | 18.7695 | 6.6168 | -1.1484
|  | HUNSTON PRIMARY | HE |  |  |  |  | 33.2747 | 33.1505 | 32.9168 | 32.74 | 32.4474 | 32.1232 | 30.8905 | 30.5558 | 30.2147 | 22.2589 | 17.2211 | 12.0621 | 29.9474 | 29.8137 | 29.5526 | 29.3653 | 29.0495 | 28.6926 | 27.2411 | 26.8716 | 26.4937 | 17.1263 | 11.2147 | 5.8105 | 29.4726 | 29.34 | 29.0811 | 28.8947 | 28.5811 | 28.2263 | 26.7874 | 26.4179 | 26.04 | 16.6695 | 10.7568 | 5.6895
|  | HUNSTON PRIMARY | FB |  |  |  |  | 33.4705 | 33.3737 | 33.2937 | 33.1853 | 33.0716 | 32.9547 | 32.8147 | 32.6758 | 32.5253 | 30.6989 | 24.9063 | 18.9074 | 30.1705 | 30.0621 | 29.9737 | 29.8516 | 29.7232 | 29.5937 | 29.4337 | 29.2758 | 29.1042 | 26.9379 | 20.1337 | 13.1011 | 29.6937 | 29.5874 | 29.4989 | 29.3779 | 29.2516 | 29.1221 | 28.9642 | 28.8074 | 28.6379 | 26.4853 | 19.6789 | 12.6442
MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT PRIMARY | MINIMUM HEADROOM | SU 39384 52476 | NO | YES | 0.70421 | 5.7979 | 5.7505 | 5.7021 | 5.6326 | 5.5463 | 5.4547 | 5.3653 | 5.2779 | 5.1905 | 4.9863 | 4.8547 | 4.7368 | 6.3284 | 6.2421 | 6.1547 | 6.0568 | 5.9316 | 5.7916 | 5.6695 | 5.5495 | 5.4316 | 5.1011 | 4.7937 | 4.4674 | 5.8095 | 5.7653 | 5.72 | 5.6526 | 5.5705 | 5.4832 | 5.3968 | 5.3116 | 5.2274 | 5.0337 | 4.9179 | 4.7358
|  | HURSTBOURNE TARRANT PRIMARY | EE |  |  |  |  | 5.7979 | 5.7505 | 5.7021 | 5.6379 | 5.5474 | 5.4663 | 5.3916 | 5.3137 | 5.2358 | 5.1716 | 5.1084 | 5.0537 | 6.3284 | 6.2421 | 6.1547 | 6.0568 | 5.9379 | 5.8295 | 5.7242 | 5.6137 | 5.5032 | 5.3116 | 5.1158 | 4.8916 | 5.8095 | 5.7653 | 5.72 | 5.6589 | 5.5705 | 5.4926 | 5.42 | 5.3453 | 5.2705 | 5.2168 | 5.1653 | 5.1253
|  | HURSTBOURNE TARRANT PRIMARY | HT |  |  |  |  | 5.8011 | 5.7589 | 5.7032 | 5.6326 | 5.5463 | 5.4547 | 5.3653 | 5.2779 | 5.1905 | 4.9863 | 4.8547 | 4.7368 | 6.3463 | 6.2695 | 6.1747 | 6.0579 | 5.9316 | 5.7916 | 5.6695 | 5.5495 | 5.4316 | 5.1011 | 4.7937 | 4.4674 | 5.8116 | 5.7716 | 5.72 | 5.6526 | 5.5705 | 5.4832 | 5.3968 | 5.3116 | 5.2274 | 5.0337 | 4.9179 | 4.7358
|  | HURSTBOURNE TARRANT PRIMARY | HE |  |  |  |  | 5.8158 | 5.7768 | 5.7326 | 5.6716 | 5.5863 | 5.5116 | 5.4358 | 5.3621 | 5.2863 | 5.2853 | 5.2611 | 5.2421 | 6.3937 | 6.3337 | 6.2684 | 6.1863 | 6.0832 | 5.9905 | 5.8968 | 5.8021 | 5.7063 | 5.6389 | 5.5179 | 5.3895 | 5.8232 | 5.7853 | 5.7432 | 5.6842 | 5.6011 | 5.5274 | 5.4537 | 5.3811 | 5.3074 | 5.3116 | 5.2958 | 5.2863
|  | HURSTBOURNE TARRANT PRIMARY | FB |  |  |  |  | 5.8453 | 5.8263 | 5.8074 | 5.7874 | 5.7663 | 5.7442 | 5.7221 | 5.7042 | 5.6811 | 5.6032 | 5.5547 | 5.52 | 6.4432 | 6.3979 | 6.3611 | 6.3221 | 6.2832 | 6.2432 | 6.2021 | 6.1674 | 6.1253 | 5.9695 | 5.8263 | 5.6884 | 5.8505 | 5.8337 | 5.8168 | 5.7979 | 5.7789 | 5.7579 | 5.7379 | 5.7211 | 5.7 | 5.6284 | 5.5884 | 5.5632
EALING GSP |  | IRONBRIDGE PRIMARY | MINIMUM HEADROOM | TQ 14226 80171 | NO | YES | 0 | 44.3968 | 44.0653 | 43.6905 | 42.5789 | 41.8968 | 40.9684 | 39.78 | 38.6653 | 37.5505 | 33.8053 | 32.1526 | 30.6589 | 40.8632 | 40.3495 | 39.1558 | 37.6958 | 36.9326 | 35.8242 | 34.3621 | 33.1284 | 31.9337 | 27.7958 | 25.9432 | 24.2684 | 43.1053 | 42.0347 | 40.8116 | 39.3137 | 38.5421 | 37.4116 | 35.9158 | 34.6558 | 33.1021 | 28.8074 | 26.9537 | 25.2789
|  | IRONBRIDGE PRIMARY | EE |  |  |  |  | 44.3968 | 44.0653 | 43.6905 | 42.7379 | 41.8968 | 40.9684 | 39.78 | 38.6653 | 37.5863 | 38.2053 | 37.1842 | 36.3032 | 40.8632 | 40.4 | 39.2821 | 37.9221 | 36.9326 | 35.8242 | 34.3621 | 33.1284 | 31.9337 | 32.8389 | 31.6884 | 30.6947 | 43.1179 | 42.0884 | 40.9411 | 39.5484 | 38.5421 | 37.4116 | 35.9158 | 34.6558 | 33.4368 | 33.96 | 32.7811 | 31.7611
|  | IRONBRIDGE PRIMARY | HT |  |  |  |  | 44.4105 | 44.0884 | 43.6937 | 42.5789 | 44.1474 | 43.1042 | 41.32 | 39.5842 | 37.5505 | 33.8053 | 32.1526 | 30.6589 | 40.88 | 40.3495 | 39.1558 | 37.6958 | 39.6063 | 38.3411 | 36.2832 | 34.3253 | 32.0189 | 27.7958 | 25.9432 | 24.2684 | 43.1053 | 42.0347 | 40.8116 | 39.3137 | 40.8768 | 39.5853 | 37.4747 | 35.4684 | 33.1021 | 28.8074 | 26.9537 | 25.2789
|  | IRONBRIDGE PRIMARY | HE |  |  |  |  | 44.4705 | 44.1621 | 43.8137 | 43.1926 | 42.4 | 41.5253 | 40.4389 | 39.5105 | 38.5411 | 40.0126 | 39.5379 | 39.1116 | 40.9105 | 40.6747 | 39.7853 | 38.5168 | 37.5916 | 36.5505 | 35.2189 | 34.1053 | 33.0368 | 34.8811 | 34.3337 | 33.84 | 43.4095 | 42.4958 | 41.46 | 40.1611 | 39.2189 | 38.1579 | 36.7979 | 35.6611 | 34.5716 | 36.0526 | 35.4905 | 34.9821
|  | IRONBRIDGE PRIMARY | FB |  |  |  |  | 44.6674 | 44.4853 | 44.3168 | 44.1263 | 43.9547 | 43.78 | 43.5758 | 43.3442 | 42.9274 | 41.3926 | 43.4653 | 42.8811 | 41.0695 | 40.9305 | 40.8021 | 40.5989 | 40.2158 | 39.8095 | 39.2074 | 38.7168 | 38.1968 | 36.2832 | 38.8358 | 38.1063 | 43.9295 | 43.3884 | 42.8779 | 42.2926 | 41.9011 | 41.4853 | 40.8695 | 40.3663 | 39.8337 | 37.8747 | 40.0958 | 39.3495
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | JAYS CLOSE PRIMARY | MINIMUM HEADROOM | SU 63055 50105 | NO | YES | 0 | 43.7324 | 43.4682 | 43.1672 | 42.8135 | 42.3766 | 41.9787 | 41.5714 | 41.1377 | 40.7577 | 39.6829 | 38.6556 | 37.4861 | 42.0398 | 41.7703 | 41.4629 | 41.104 | 40.6629 | 40.2608 | 39.8482 | 39.4082 | 39.0229 | 38.3503 | 37.2872 | 36.0703 | 43.7187 | 43.2829 | 42.824 | 42.3293 | 41.744 | 41.0756 | 40.5756 | 40.0724 | 39.5293 | 38.1293 | 36.984 | 35.6514
|  | JAYS CLOSE PRIMARY | EE |  |  |  |  | 43.7324 | 43.4682 | 43.1672 | 42.8135 | 42.3766 | 41.9787 | 41.5714 | 41.1377 | 40.7577 | 39.8051 | 38.9924 | 38.1072 | 42.0398 | 41.7703 | 41.4629 | 41.104 | 40.6629 | 40.2608 | 39.8482 | 39.4082 | 39.0229 | 38.4177 | 37.6019 | 36.6703 | 43.7187 | 43.2829 | 42.824 | 42.3293 | 41.7735 | 41.2556 | 40.6851 | 40.0745 | 39.5293 | 38.2651 | 37.3461 | 36.3166
|  | JAYS CLOSE PRIMARY | HT |  |  |  |  | 43.7924 | 43.5545 | 43.2735 | 42.9314 | 42.5819 | 42.2387 | 41.8924 | 41.4714 | 41.0145 | 39.6829 | 38.6556 | 37.4861 | 42.1019 | 41.8598 | 41.5745 | 41.2282 | 40.8756 | 40.5324 | 40.1851 | 39.8482 | 39.5229 | 38.3503 | 37.2872 | 36.0703 | 43.8398 | 43.4524 | 42.9798 | 42.3608 | 41.744 | 41.0756 | 40.5756 | 40.0724 | 39.5872 | 38.1293 | 36.984 | 35.6514
|  | JAYS CLOSE PRIMARY | HE |  |  |  |  | 43.9272 | 43.7735 | 43.604 | 43.3682 | 43.044 | 42.7451 | 42.4545 | 42.1587 | 41.8682 | 41.8966 | 41.8472 | 41.7808 | 42.2419 | 42.0882 | 41.9187 | 41.6829 | 41.3587 | 41.0598 | 40.7693 | 40.4735 | 40.1829 | 40.2114 | 40.1619 | 40.1282 | 44.1082 | 43.8672 | 43.6135 | 43.2987 | 42.8977 | 42.524 | 42.1387 | 41.7429 | 41.3608 | 41.0429 | 40.7335 | 40.4377
|  | JAYS CLOSE PRIMARY | FB |  |  |  |  | 44.044 | 43.9693 | 43.9019 | 43.8261 | 43.7419 | 43.6577 | 43.5756 | 43.4987 | 43.4166 | 43.1166 | 42.9482 | 42.7914 | 42.3587 | 42.284 | 42.2166 | 42.1408 | 42.0566 | 41.9724 | 41.8903 | 41.8135 | 41.7314 | 41.4314 | 41.2629 | 41.1566 | 44.3061 | 44.1219 | 43.9819 | 43.8335 | 43.6745 | 43.5166 | 43.364 | 43.2072 | 43.0429 | 42.3556 | 41.8587 | 41.444
MINETY GSP | CIRENCESTER BSP | KEMBLE RAF PRIMARY | MINIMUM HEADROOM | ST 96064 96012 | YES | YES | 0 | 10.1232 | 10.1232 | 10.1221 | 10.12 | 10.1189 | 10.1168 | 10.1095 | 10.1 | 10.0916 | 10.0558 | 10.0242 | 9.9989 | 9.8211 | 9.82 | 9.8189 | 9.8179 | 9.8168 | 9.8147 | 9.8105 | 9.8042 | 9.7989 | 9.7632 | 9.7263 | 9.6968 | 9.6368 | 9.6368 | 9.6358 | 9.6337 | 9.6326 | 9.6305 | 9.6211 | 9.6105 | 9.6011 | 9.5589 | 9.5221 | 9.4926
|  | KEMBLE RAF PRIMARY | EE |  |  |  |  | 10.1232 | 10.1232 | 10.1221 | 10.12 | 10.1189 | 10.1168 | 10.1095 | 10.1 | 10.0916 | 10.0558 | 10.0242 | 9.9989 | 9.8211 | 9.82 | 9.8189 | 9.8179 | 9.8168 | 9.8147 | 9.8105 | 9.8042 | 9.7989 | 9.7632 | 9.7263 | 9.6968 | 9.6368 | 9.6368 | 9.6358 | 9.6337 | 9.6326 | 9.6305 | 9.6211 | 9.6105 | 9.6011 | 9.5589 | 9.5221 | 9.4926
|  | KEMBLE RAF PRIMARY | HT |  |  |  |  | 10.1232 | 10.1232 | 10.1221 | 10.1211 | 10.1189 | 10.1179 | 10.1147 | 10.1074 | 10.1 | 10.0621 | 10.0305 | 10.0053 | 9.8211 | 9.8211 | 9.8189 | 9.8179 | 9.8168 | 9.8158 | 9.8126 | 9.8084 | 9.8032 | 9.7716 | 9.7337 | 9.7042 | 9.6368 | 9.6368 | 9.6358 | 9.6347 | 9.6326 | 9.6316 | 9.6284 | 9.62 | 9.6105 | 9.5674 | 9.5295 | 9.5
|  | KEMBLE RAF PRIMARY | HE |  |  |  |  | 10.1253 | 10.1242 | 10.1232 | 10.1211 | 10.1211 | 10.12 | 10.1189 | 10.1179 | 10.1168 | 10.1147 | 10.1011 | 10.0884 | 9.8221 | 9.8211 | 9.8211 | 9.8189 | 9.8189 | 9.8168 | 9.8158 | 9.8147 | 9.8137 | 9.8126 | 9.8042 | 9.7968 | 9.6389 | 9.6379 | 9.6368 | 9.6347 | 9.6347 | 9.6337 | 9.6326 | 9.6316 | 9.6305 | 9.6284 | 9.6116 | 9.5968
|  | KEMBLE RAF PRIMARY | FB |  |  |  |  | 10.1253 | 10.1242 | 10.1242 | 10.1232 | 10.1232 | 10.1221 | 10.1221 | 10.1221 | 10.1221 | 10.1179 | 10.1053 | 10.0884 | 9.8221 | 9.8211 | 9.8211 | 9.8211 | 9.8211 | 9.82 | 9.8189 | 9.8189 | 9.8189 | 9.8158 | 9.8084 | 9.7989 | 9.6389 | 9.6379 | 9.6379 | 9.6368 | 9.6368 | 9.6358 | 9.6358 | 9.6358 | 9.6358 | 9.6316 | 9.6158 | 9.5968
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | KENNINGTON PRIMARY | MINIMUM HEADROOM | SP 52881 01094 | YES | YES | 1.0516 | 6.2968 | 6.2042 | 6.0926 | 5.9589 | 5.7853 | 5.5589 | 5.3168 | 5.0579 | 4.7926 | 4.1147 | 3.5568 | 2.8547 | 5.1926 | 5.0495 | 4.8884 | 4.7116 | 4.4558 | 4.2 | 3.9368 | 3.6537 | 3.3621 | 2.6095 | 1.9768 | 1.1632 | 5.1032 | 4.9611 | 4.8 | 4.6232 | 4.3674 | 4.1126 | 3.8495 | 3.5663 | 3.2758 | 2.5242 | 1.8926 | 1.0811
|  | KENNINGTON PRIMARY | EE |  |  |  |  | 6.3842 | 6.2895 | 6.1895 | 6.0663 | 5.9074 | 5.76 | 5.6232 | 5.4832 | 5.3463 | 5.1126 | 4.8211 | 4.4 | 5.4558 | 5.3084 | 5.1589 | 4.9916 | 4.7979 | 4.6147 | 4.4368 | 4.26 | 4.0874 | 3.7505 | 3.4147 | 2.92 | 5.3663 | 5.2189 | 5.0695 | 4.9021 | 4.7084 | 4.5253 | 4.3484 | 4.1705 | 3.9979 | 3.6621 | 3.3274 | 2.8347
|  | KENNINGTON PRIMARY | HT |  |  |  |  | 6.2968 | 6.2042 | 6.0926 | 5.9589 | 5.7853 | 5.5589 | 5.3168 | 5.0579 | 4.7926 | 4.1147 | 3.5568 | 2.8547 | 5.1926 | 5.0495 | 4.8884 | 4.7116 | 4.4558 | 4.2 | 3.9368 | 3.6537 | 3.3621 | 2.6095 | 1.9768 | 1.1632 | 5.1032 | 4.9611 | 4.8 | 4.6232 | 4.3674 | 4.1126 | 3.8495 | 3.5663 | 3.2758 | 2.5242 | 1.8926 | 1.0811
|  | KENNINGTON PRIMARY | HE |  |  |  |  | 6.4411 | 6.3663 | 6.2821 | 6.1747 | 6.0274 | 5.8968 | 5.7684 | 5.64 | 5.5116 | 5.4684 | 5.3832 | 5.1147 | 5.5705 | 5.4663 | 5.3537 | 5.2189 | 5.0484 | 4.8916 | 4.7379 | 4.5884 | 4.44 | 4.3063 | 4.1074 | 3.7263 | 5.48 | 5.3758 | 5.2642 | 5.1295 | 4.9579 | 4.8021 | 4.6484 | 4.4989 | 4.3505 | 4.2179 | 4.0189 | 3.6389
|  | KENNINGTON PRIMARY | FB |  |  |  |  | 6.5126 | 6.4642 | 6.4263 | 6.3832 | 6.3379 | 6.2916 | 6.2463 | 6.2042 | 6.16 | 5.9884 | 5.8653 | 5.7032 | 5.6989 | 5.6168 | 5.5558 | 5.4895 | 5.4221 | 5.3516 | 5.2832 | 5.2189 | 5.1526 | 4.8832 | 4.6526 | 4.3495 | 5.6084 | 5.5263 | 5.4653 | 5.3989 | 5.3316 | 5.2611 | 5.1937 | 5.1295 | 5.0632 | 4.7937 | 4.5642 | 4.2611
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | KENTWOOD HILL PRIMARY | MINIMUM HEADROOM | SU 67102 74048 | NO | YES | 0 | 26.3832 | 25.7063 | 25.0032 | 23.9368 | 22.7884 | 21.5516 | 20.3389 | 19.0779 | 17.7968 | 14.6674 | 12.4358 | 10.3337 | 25.46 | 24.7905 | 24.0937 | 23.0379 | 21.8968 | 20.6716 | 19.4684 | 18.2189 | 16.9484 | 13.5884 | 11.1589 | 8.8568 | 25.4011 | 24.6663 | 23.9095 | 22.7547 | 21.52 | 20.1958 | 18.8979 | 17.54 | 16.1568 | 12.7547 | 10.3011 | 7.9747
|  | KENTWOOD HILL PRIMARY | EE |  |  |  |  | 26.3832 | 25.7063 | 25.0032 | 24.2 | 23.2547 | 22.3211 | 21.4179 | 20.5095 | 19.6232 | 18.1989 | 16.7274 | 15.3853 | 25.46 | 24.7905 | 24.0937 | 23.2947 | 22.3547 | 21.4263 | 20.5274 | 19.6242 | 18.7421 | 17.3389 | 15.8126 | 14.3032 | 25.4011 | 24.6663 | 23.9095 | 23.0579 | 22.0705 | 21.0968 | 20.1474 | 19.1947 | 18.2663 | 16.6695 | 15 | 13.4705
|  | KENTWOOD HILL PRIMARY | HT |  |  |  |  | 26.5147 | 25.8368 | 25.0063 | 23.9368 | 22.7884 | 21.5516 | 20.3389 | 19.0779 | 17.7968 | 14.6674 | 12.4358 | 10.3337 | 25.5895 | 24.9189 | 24.0958 | 23.0379 | 21.8968 | 20.6716 | 19.4684 | 18.2189 | 16.9484 | 13.5884 | 11.1589 | 8.8568 | 25.5537 | 24.8126 | 23.9137 | 22.7547 | 21.52 | 20.1958 | 18.8979 | 17.54 | 16.1568 | 12.7547 | 10.3011 | 7.9747
|  | KENTWOOD HILL PRIMARY | HE |  |  |  |  | 26.8537 | 26.3516 | 25.8032 | 25.1263 | 24.2674 | 23.4463 | 22.6505 | 21.8547 | 21.0705 | 20.5895 | 19.7379 | 18.9211 | 25.9232 | 25.4242 | 24.88 | 24.2063 | 23.3505 | 22.5326 | 21.7389 | 20.9463 | 20.1653 | 19.6947 | 18.8589 | 18.0579 | 25.9389 | 25.4063 | 24.8295 | 24.1242 | 23.2368 | 22.3884 | 21.5663 | 20.7463 | 19.9379 | 19.3653 | 18.3779 | 17.4253
|  | KENTWOOD HILL PRIMARY | FB |  |  |  |  | 27.1684 | 26.8989 | 26.6126 | 26.3116 | 25.9874 | 25.6568 | 25.3358 | 25.0326 | 24.7211 | 23.4895 | 22.3937 | 21.4337 | 26.3379 | 25.9684 | 25.6863 | 25.3884 | 25.0663 | 24.74 | 24.4211 | 24.1211 | 23.8116 | 22.5937 | 21.5137 | 20.5684 | 26.3874 | 25.9747 | 25.6642 | 25.3379 | 24.9853 | 24.6295 | 24.2811 | 23.9526 | 23.6158 | 22.2779 | 21.0484 | 19.9547
COWLEY GSP | YARNTON BSP | KIDDINGTON PRIMARY | MINIMUM HEADROOM | SP 43362 24301 | NO | YES | 0.12105 | 23.5929 | 23.5213 | 23.4266 | 23.3108 | 23.1824 | 23.0434 | 22.9108 | 22.7718 | 22.635 | 22.275 | 22.0139 | 21.7561 | 23.3266 | 23.2192 | 23.0676 | 22.8897 | 22.7108 | 22.5224 | 22.3466 | 22.1497 | 21.955 | 21.3929 | 20.9255 | 20.4392 | 23.4276 | 23.3339 | 23.2034 | 23.0487 | 22.8897 | 22.7203 | 22.5603 | 22.3845 | 22.2129 | 21.7266 | 21.3371 | 20.9371
|  | KIDDINGTON PRIMARY | EE |  |  |  |  | 23.595 | 23.5213 | 23.4434 | 23.3476 | 23.2213 | 23.1045 | 22.9929 | 22.8803 | 22.7697 | 22.6182 | 22.4666 | 22.3297 | 23.3392 | 23.2266 | 23.1118 | 22.9813 | 22.8255 | 22.6782 | 22.5308 | 22.3834 | 22.2392 | 21.9413 | 21.6361 | 21.3424 | 23.4361 | 23.3382 | 23.2371 | 23.1192 | 22.975 | 22.8392 | 22.7055 | 22.5708 | 22.4403 | 22.1961 | 21.9497 | 21.7161
|  | KIDDINGTON PRIMARY | HT |  |  |  |  | 23.5929 | 23.5234 | 23.4266 | 23.3108 | 23.1824 | 23.0434 | 22.9108 | 22.7718 | 22.635 | 22.275 | 22.0139 | 21.7561 | 23.3266 | 23.2192 | 23.0676 | 22.8897 | 22.7108 | 22.5224 | 22.3466 | 22.1497 | 21.955 | 21.3929 | 20.9255 | 20.4392 | 23.4276 | 23.3339 | 23.2034 | 23.0487 | 22.8897 | 22.7203 | 22.5603 | 22.3845 | 22.2129 | 21.7266 | 21.3371 | 20.9371
|  | KIDDINGTON PRIMARY | HE |  |  |  |  | 23.6382 | 23.5782 | 23.5139 | 23.4276 | 23.3108 | 23.2055 | 23.1045 | 23.0024 | 22.9003 | 22.8624 | 22.7824 | 22.7087 | 23.4255 | 23.3434 | 23.2592 | 23.1508 | 23.0129 | 22.8866 | 22.7655 | 22.6445 | 22.5224 | 22.4045 | 22.2161 | 22.0234 | 23.5055 | 23.4318 | 23.355 | 23.255 | 23.1255 | 23.0076 | 22.8939 | 22.7803 | 22.6655 | 22.5782 | 22.4308 | 22.2824
|  | KIDDINGTON PRIMARY | FB |  |  |  |  | 23.6824 | 23.6455 | 23.6139 | 23.5803 | 23.5434 | 23.5066 | 23.4697 | 23.4361 | 23.4003 | 23.2603 | 23.8613 | 23.7708 | 23.4897 | 23.4266 | 23.3782 | 23.3266 | 23.2718 | 23.215 | 23.1603 | 23.1076 | 23.0539 | 22.8329 | 23.5013 | 23.3076 | 23.5624 | 23.5097 | 23.4666 | 23.4224 | 23.375 | 23.3245 | 23.2782 | 23.2318 | 23.1845 | 22.995 | 23.5645 | 23.4097
BRAMLEY (BASI) GSP | READING BSP | KIDMORE END PRIMARY | MINIMUM HEADROOM | SU 69953 78205 | NO | YES | 0 | 24.3221 | 24.1095 | 22.9189 | 22.6484 | 22.3116 | 21.9684 | 21.6547 | 21.3347 | 21.0168 | 20.0758 | 19.4547 | 18.8211 | 22.8011 | 22.5621 | 21.0979 | 20.8042 | 20.4368 | 20.0674 | 19.7347 | 19.3926 | 19.0505 | 18.0011 | 17.3011 | 16.5726 | 21.3274 | 21.0905 | 19.6442 | 19.3516 | 18.9874 | 18.6189 | 18.2874 | 17.9463 | 17.6063 | 16.5632 | 15.8674 | 15.1453
|  | KIDMORE END PRIMARY | EE |  |  |  |  | 24.3242 | 24.1105 | 23.0253 | 22.7684 | 22.4632 | 22.1674 | 21.88 | 21.5874 | 21.3042 | 20.8432 | 20.4632 | 20.1337 | 22.8042 | 22.5653 | 21.2284 | 20.9505 | 20.6263 | 20.3116 | 20.0021 | 19.6895 | 19.3853 | 18.8379 | 18.3895 | 17.9989 | 21.3316 | 21.0937 | 19.7726 | 19.4968 | 19.1737 | 18.8589 | 18.5526 | 18.24 | 17.9379 | 17.3958 | 16.9516 | 16.5642
|  | KIDMORE END PRIMARY | HT |  |  |  |  | 24.3221 | 24.1095 | 22.9189 | 22.6484 | 22.3116 | 21.9684 | 21.6547 | 21.3347 | 21.0168 | 20.0758 | 19.4547 | 18.8211 | 22.8011 | 22.5621 | 21.0979 | 20.8042 | 20.4368 | 20.0674 | 19.7347 | 19.3926 | 19.0505 | 18.0011 | 17.3011 | 16.5726 | 21.3274 | 21.0905 | 19.6442 | 19.3516 | 18.9874 | 18.6189 | 18.2874 | 17.9463 | 17.6063 | 16.5632 | 15.8674 | 15.1453
|  | KIDMORE END PRIMARY | HE |  |  |  |  | 24.4516 | 24.3032 | 23.2726 | 23.06 | 22.7874 | 22.5347 | 22.2832 | 22.0337 | 21.7874 | 21.6432 | 21.4547 | 21.3032 | 22.9737 | 22.7989 | 21.5284 | 21.3021 | 21.0168 | 20.7526 | 20.4884 | 20.2263 | 19.9695 | 19.7789 | 19.5484 | 19.3611 | 21.4989 | 21.3253 | 20.0695 | 19.8442 | 19.56 | 19.2958 | 19.0326 | 18.7716 | 18.5147 | 18.3284 | 18.1 | 17.9147
|  | KIDMORE END PRIMARY | FB |  |  |  |  | 24.5537 | 24.4842 | 24.4 | 23.4432 | 23.3442 | 23.2453 | 23.1463 | 23.0537 | 22.9579 | 22.5726 | 22.2747 | 22.0432 | 23.1232 | 22.9926 | 22.8937 | 21.6989 | 21.5884 | 21.4779 | 21.3663 | 21.2632 | 21.1558 | 20.72 | 20.3716 | 20.0968 | 21.6474 | 21.5179 | 21.42 | 20.24 | 20.1305 | 20.0211 | 19.9105 | 19.8074 | 19.7 | 19.2684 | 18.9232 | 18.6516
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | KINGS RIDE PRIMARY | MINIMUM HEADROOM | SU 87551 61530 | NO | YES | 0 | 27.3599 | 27.2136 | 27.022 | 26.6325 | 25.7325 | 24.8083 | 23.8883 | 22.962 | 21.9999 | 19.7009 | 18.8251 | 18.063 | 24.145 | 23.8987 | 23.4934 | 22.7892 | 21.8103 | 20.8082 | 19.8113 | 18.8061 | 17.7597 | 15.2692 | 14.3324 | 13.5187 | 25.1284 | 24.8968 | 24.5232 | 23.8811 | 22.9926 | 22.0811 | 21.1737 | 20.2611 | 19.3116 | 17.0621 | 16.1958 | 15.4432
|  | KINGS RIDE PRIMARY | EE |  |  |  |  | 27.3599 | 27.2136 | 27.022 | 26.6683 | 25.9209 | 25.2725 | 24.6125 | 23.9662 | 23.2799 | 21.6493 | 21.0609 | 20.5672 | 24.145 | 23.8987 | 23.4934 | 22.8282 | 22.0208 | 21.3261 | 20.6155 | 19.9197 | 19.1818 | 17.3766 | 16.7471 | 16.2071 | 25.1284 | 24.8968 | 24.5232 | 23.9158 | 23.1779 | 22.5379 | 21.8863 | 21.2474 | 20.5705 | 18.9674 | 18.4032 | 17.9158
|  | KINGS RIDE PRIMARY | HT |  |  |  |  | 27.3736 | 27.2336 | 27.023 | 26.6325 | 25.7325 | 24.8083 | 23.8883 | 22.962 | 21.9999 | 19.7009 | 18.8251 | 18.063 | 24.1934 | 23.9661 | 23.5261 | 22.7892 | 21.8103 | 20.8082 | 19.8113 | 18.8061 | 17.7597 | 15.2692 | 14.3324 | 13.5187 | 25.1716 | 24.9568 | 24.5516 | 23.8811 | 22.9926 | 22.0811 | 21.1737 | 20.2611 | 19.3116 | 17.0621 | 16.1958 | 15.4432
|  | KINGS RIDE PRIMARY | HE |  |  |  |  | 27.4136 | 27.282 | 27.1009 | 26.8336 | 26.2346 | 25.6199 | 25.0125 | 24.4178 | 23.7872 | 22.5809 | 22.2336 | 21.962 | 24.3113 | 24.1271 | 23.7724 | 23.1492 | 22.3692 | 21.7092 | 21.0587 | 20.4218 | 19.7439 | 18.3934 | 18.0103 | 17.7092 | 25.2768 | 25.1011 | 24.7726 | 24.2032 | 23.4874 | 22.8789 | 22.2789 | 21.6916 | 21.0684 | 19.8853 | 19.5442 | 19.2768
|  | KINGS RIDE PRIMARY | FB |  |  |  |  | 27.5167 | 27.4409 | 27.3651 | 27.2672 | 27.1599 | 27.0514 | 26.8462 | 26.5704 | 26.2504 | 25.1588 | 24.7262 | 24.3693 | 24.4639 | 24.3218 | 24.1492 | 23.8808 | 23.5882 | 23.2976 | 23.0018 | 22.7008 | 22.3503 | 21.1576 | 20.6903 | 20.3008 | 25.4221 | 25.2905 | 25.1316 | 24.8895 | 24.6253 | 24.3621 | 24.0947 | 23.8232 | 23.5084 | 22.4337 | 22.0063 | 21.6547
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINGSCLERE PRIMARY | MINIMUM HEADROOM | SU 51982 59358 | NO | YES | 0 | 12.1663 | 12.1042 | 12.0358 | 11.9389 | 11.8189 | 11.6979 | 11.5726 | 11.4105 | 11.2442 | 10.7684 | 10.4189 | 10.0621 | 9.6905 | 9.5653 | 9.44 | 9.2958 | 9.1126 | 8.9105 | 8.74 | 8.5653 | 8.3905 | 7.8811 | 7.5 | 7.1063 | 11.0274 | 10.9105 | 10.7937 | 10.6558 | 10.4832 | 10.2916 | 10.1284 | 9.9611 | 9.7947 | 9.3147 | 8.9337 | 8.5411
|  | KINGSCLERE PRIMARY | EE |  |  |  |  | 12.1663 | 12.1042 | 12.0368 | 11.9463 | 11.8189 | 11.7011 | 11.5916 | 11.4779 | 11.3221 | 11.0474 | 10.8232 | 10.6 | 9.6905 | 9.5653 | 9.44 | 9.2979 | 9.1274 | 8.9653 | 8.8042 | 8.6389 | 8.4747 | 8.1653 | 7.9137 | 7.6611 | 11.0274 | 10.9105 | 10.7937 | 10.66 | 10.4947 | 10.34 | 10.1853 | 10.0284 | 9.8726 | 9.5958 | 9.3474 | 9.0958
|  | KINGSCLERE PRIMARY | HT |  |  |  |  | 12.1684 | 12.1126 | 12.0358 | 11.9389 | 11.8253 | 11.6979 | 11.5726 | 11.4105 | 11.2442 | 10.7684 | 10.4189 | 10.0621 | 9.7168 | 9.6053 | 9.4674 | 9.2958 | 9.1126 | 8.9105 | 8.74 | 8.5653 | 8.3905 | 7.8811 | 7.5 | 7.1063 | 11.0495 | 10.9463 | 10.8168 | 10.6558 | 10.4832 | 10.2916 | 10.1284 | 9.9611 | 9.7947 | 9.3147 | 8.9337 | 8.5411
|  | KINGSCLERE PRIMARY | HE |  |  |  |  | 12.1789 | 12.1211 | 12.0568 | 11.9674 | 11.8432 | 11.7284 | 11.6221 | 11.5116 | 11.4 | 11.4116 | 11.3916 | 11.3116 | 9.78 | 9.6884 | 9.5937 | 9.4768 | 9.3221 | 9.18 | 9.0505 | 8.9137 | 8.7768 | 8.6789 | 8.5568 | 8.4611 | 11.0705 | 11.0105 | 10.9274 | 10.8147 | 10.6653 | 10.5263 | 10.4011 | 10.2674 | 10.1347 | 10.0526 | 9.9463 | 9.8621
|  | KINGSCLERE PRIMARY | FB |  |  |  |  | 12.2253 | 12.1989 | 12.1726 | 12.1453 | 12.1147 | 12.0842 | 12.0537 | 12.0253 | 11.9958 | 11.8853 | 11.8063 | 11.6663 | 9.8589 | 9.7884 | 9.7347 | 9.68 | 9.62 | 9.5611 | 9.5042 | 9.4516 | 9.3937 | 9.1568 | 8.9653 | 8.8063 | 11.1189 | 11.0895 | 11.0621 | 11.0147 | 10.9589 | 10.9042 | 10.8516 | 10.8021 | 10.7484 | 10.5295 | 10.3579 | 10.2158
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINTBURY PRIMARY | MINIMUM HEADROOM | SU 37657 67143 | NO | YES | 0 | 10.8842 | 10.7968 | 10.7063 | 10.5484 | 10.3747 | 10.1842 | 10.0021 | 9.8021 | 9.6 | 9.1695 | 8.8895 | 8.6232 | 10.2958 | 10.1989 | 10.1 | 9.9253 | 9.7337 | 9.5242 | 9.3242 | 9.1021 | 8.8768 | 8.4011 | 8.0895 | 7.7916 | 10.4811 | 10.3926 | 10.3011 | 10.1411 | 9.9653 | 9.7726 | 9.5884 | 9.3853 | 9.1747 | 8.6989 | 8.3874 | 8.0884
|  | KINTBURY PRIMARY | EE |  |  |  |  | 10.8842 | 10.7968 | 10.7084 | 10.6095 | 10.4863 | 10.3705 | 10.2579 | 10.1442 | 10.0337 | 9.8579 | 9.6726 | 9.4968 | 10.2958 | 10.1989 | 10.1042 | 9.9979 | 9.8695 | 9.7474 | 9.6284 | 9.5084 | 9.3926 | 9.1926 | 8.98 | 8.7758 | 10.4811 | 10.3926 | 10.3032 | 10.2032 | 10.08 | 9.9632 | 9.8495 | 9.7358 | 9.6242 | 9.4453 | 9.2568 | 9.0737
|  | KINTBURY PRIMARY | HT |  |  |  |  | 10.9021 | 10.8221 | 10.7063 | 10.5484 | 10.3747 | 10.1842 | 10.0021 | 9.8021 | 9.6 | 9.1695 | 8.8895 | 8.6232 | 10.3158 | 10.2284 | 10.1 | 9.9253 | 9.7337 | 9.5242 | 9.3242 | 9.1021 | 8.8768 | 8.4011 | 8.0895 | 7.7916 | 10.4989 | 10.4179 | 10.3011 | 10.1411 | 9.9653 | 9.7726 | 9.5884 | 9.3853 | 9.1747 | 8.6989 | 8.3874 | 8.0884
|  | KINTBURY PRIMARY | HE |  |  |  |  | 10.9421 | 10.8768 | 10.8105 | 10.7263 | 10.6137 | 10.5126 | 10.4147 | 10.3168 | 10.2211 | 10.1716 | 10.0684 | 9.9632 | 10.3621 | 10.2937 | 10.2232 | 10.1347 | 10.0179 | 9.9137 | 9.8126 | 9.7116 | 9.6126 | 9.5516 | 9.4305 | 9.3053 | 10.54 | 10.4747 | 10.4074 | 10.3221 | 10.2095 | 10.1084 | 10.0095 | 9.9116 | 9.8158 | 9.7653 | 9.6589 | 9.5516
|  | KINTBURY PRIMARY | FB |  |  |  |  | 10.9958 | 10.9484 | 10.9126 | 10.8758 | 10.8347 | 10.7937 | 10.7558 | 10.7158 | 10.6779 | 10.5263 | 10.3884 | 10.2589 | 10.42 | 10.3684 | 10.3284 | 10.2884 | 10.2432 | 10.1979 | 10.1568 | 10.1137 | 10.0716 | 9.9063 | 9.7495 | 9.5989 | 10.5937 | 10.5463 | 10.5095 | 10.4726 | 10.4316 | 10.3895 | 10.3516 | 10.3105 | 10.2726 | 10.12 | 9.9789 | 9.8474
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | KNOWL HILL PRIMARY | MINIMUM HEADROOM | SU 82849 79105 | NO | YES | 0.68421 | 6.2305 | 6.1716 | 6.1105 | 6.0421 | 5.9621 | 5.8526 | 5.7126 | 5.5379 | 5.3495 | 4.9537 | 4.7274 | 4.5242 | 5.1337 | 5.0705 | 5.0053 | 4.9316 | 4.8484 | 4.7305 | 4.5758 | 4.3811 | 4.1684 | 3.7263 | 3.4726 | 3.2463 | 4.64 | 4.5821 | 4.5211 | 4.4516 | 4.3716 | 4.2632 | 4.1221 | 3.9474 | 3.7579 | 3.3621 | 3.1347 | 2.9326
|  | KNOWL HILL PRIMARY | EE |  |  |  |  | 6.2305 | 6.1716 | 6.1105 | 6.0421 | 5.9621 | 5.8821 | 5.8053 | 5.7284 | 5.6579 | 5.4895 | 5.3326 | 5.2 | 5.1337 | 5.0705 | 5.0053 | 4.9316 | 4.8484 | 4.7653 | 4.6842 | 4.6032 | 4.5295 | 4.3379 | 4.1568 | 4.0042 | 4.64 | 4.5821 | 4.5211 | 4.4516 | 4.3726 | 4.2926 | 4.2158 | 4.1379 | 4.0674 | 3.8989 | 3.7421 | 3.6084
|  | KNOWL HILL PRIMARY | HT |  |  |  |  | 6.2411 | 6.1884 | 6.1168 | 6.0442 | 5.9621 | 5.8526 | 5.7126 | 5.5379 | 5.3495 | 4.9537 | 4.7274 | 4.5242 | 5.1474 | 5.0895 | 5.0116 | 4.9347 | 4.8484 | 4.7305 | 4.5758 | 4.3811 | 4.1684 | 3.7263 | 3.4726 | 3.2463 | 4.6516 | 4.5979 | 4.5263 | 4.4547 | 4.3716 | 4.2632 | 4.1221 | 3.9474 | 3.7579 | 3.3621 | 3.1347 | 2.9326
|  | KNOWL HILL PRIMARY | HE |  |  |  |  | 6.2684 | 6.2253 | 6.1779 | 6.12 | 6.0484 | 5.9768 | 5.9147 | 5.8463 | 5.7821 | 5.7095 | 5.6042 | 5.5137 | 5.1779 | 5.1326 | 5.0821 | 5.0221 | 4.9474 | 4.8737 | 4.8084 | 4.7389 | 4.6726 | 4.5853 | 4.4632 | 4.3568 | 4.6779 | 4.6358 | 4.5884 | 4.5305 | 4.4589 | 4.3874 | 4.3242 | 4.2568 | 4.1926 | 4.1189 | 4.0147 | 3.9232
|  | KNOWL HILL PRIMARY | FB |  |  |  |  | 6.3063 | 6.2737 | 6.2505 | 6.2242 | 6.1968 | 6.1695 | 6.1421 | 6.1137 | 6.0863 | 5.9663 | 5.8537 | 5.7568 | 5.2179 | 5.1832 | 5.1579 | 5.1284 | 5.0979 | 5.0695 | 5.04 | 5.0074 | 4.9789 | 4.8453 | 4.7179 | 4.6063 | 4.7168 | 4.6842 | 4.6611 | 4.6347 | 4.6074 | 4.58 | 4.5526 | 4.5232 | 4.4968 | 4.3758 | 4.2632 | 4.1663
FLEET-BRAMLEY GSP | ALDERSHOT BSP | LABURNUM ROAD PRIMARY | MINIMUM HEADROOM | SU 86017 50475 | NO | YES | 0 | 35.6021 | 35.28 | 34.8284 | 34.2705 | 33.6663 | 33.1421 | 32.6126 | 32.0811 | 31.5474 | 30.3905 | 29.7 | 29.0916 | 34.7863 | 33.5905 | 31.6716 | 29.4189 | 27.4042 | 25.8663 | 24.4284 | 22.9484 | 21.4368 | 18.5011 | 16.9305 | 15.5726 | 39.4032 | 38.1937 | 36.2558 | 33.9789 | 31.9453 | 30.3926 | 28.9432 | 27.4495 | 25.9242 | 22.9632 | 21.38 | 20.0116
|  | LABURNUM ROAD PRIMARY | EE |  |  |  |  | 35.6021 | 35.28 | 34.8284 | 34.2705 | 33.6663 | 33.1737 | 32.7295 | 32.2768 | 31.8221 | 31.3126 | 30.9368 | 30.6389 | 34.7863 | 33.5905 | 31.6716 | 29.4189 | 27.4042 | 26.1158 | 25.0495 | 23.9779 | 22.8695 | 20.9653 | 19.7811 | 18.8411 | 39.4032 | 38.1937 | 36.2558 | 33.9789 | 31.9453 | 30.6442 | 29.5695 | 28.4905 | 27.3726 | 25.4484 | 24.2547 | 23.3032
|  | LABURNUM ROAD PRIMARY | HT |  |  |  |  | 35.6263 | 35.3158 | 34.8537 | 34.2863 | 33.6968 | 33.1421 | 32.6126 | 32.0811 | 31.5474 | 30.3905 | 29.7 | 29.0916 | 34.8684 | 33.7063 | 31.7926 | 29.5411 | 27.4874 | 25.8663 | 24.4284 | 22.9484 | 21.4368 | 18.5011 | 16.9305 | 15.5726 | 39.4853 | 38.3116 | 36.3768 | 34.1021 | 32.0284 | 30.3926 | 28.9432 | 27.4495 | 25.9242 | 22.9632 | 21.38 | 20.0116
|  | LABURNUM ROAD PRIMARY | HE |  |  |  |  | 35.6674 | 35.3547 | 34.9105 | 34.3526 | 33.74 | 33.2537 | 32.8105 | 32.3653 | 31.9189 | 31.7495 | 31.5811 | 31.4589 | 35.0389 | 33.9316 | 32.0874 | 29.8916 | 27.9074 | 26.6653 | 25.6884 | 24.7074 | 23.6905 | 22.5137 | 21.7853 | 21.2337 | 39.6579 | 38.5389 | 36.6747 | 34.4568 | 32.4537 | 31.2021 | 30.2168 | 29.2295 | 28.2032 | 27.0126 | 26.2768 | 25.7189
|  | LABURNUM ROAD PRIMARY | FB |  |  |  |  | 35.8432 | 35.6758 | 35.4842 | 35.2726 | 35.0674 | 34.8989 | 34.7463 | 34.5968 | 34.4337 | 33.9284 | 33.6305 | 33.4168 | 35.4958 | 34.8863 | 34.0632 | 33.1526 | 32.3484 | 31.8032 | 31.3505 | 30.8789 | 30.3505 | 29.0632 | 28.2389 | 27.5663 | 40.1189 | 39.5032 | 38.6705 | 37.7505 | 36.9379 | 36.3874 | 35.9316 | 35.4547 | 34.9221 | 33.6232 | 32.7916 | 32.1126
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LAMBOURN PRIMARY | MINIMUM HEADROOM | SU 33280 78217 | NO | YES | 0 | 11.6863 | 24.6695 | 24.5505 | 24.3505 | 24.1284 | 23.8853 | 23.6495 | 23.3853 | 23.1158 | 19.6653 | 19.3705 | 19.1021 | 10.2042 | 21.7832 | 21.6968 | 21.4842 | 21.2442 | 20.9811 | 20.7253 | 20.4368 | 20.1411 | 16.0821 | 15.7474 | 15.4411 | 10.1663 | 22.4253 | 22.3032 | 22.0947 | 21.8632 | 21.6105 | 21.3663 | 21.0916 | 20.8105 | 17.0589 | 16.7274 | 16.4211
|  | LAMBOURN PRIMARY | EE |  |  |  |  | 11.6863 | 24.6695 | 24.5505 | 24.42 | 24.2537 | 24.0968 | 23.9379 | 23.7705 | 23.6137 | 19.6653 | 19.3705 | 19.1021 | 10.2042 | 21.7832 | 21.6968 | 21.5632 | 21.3916 | 21.2284 | 21.06 | 20.8853 | 20.72 | 16.0821 | 15.7474 | 15.4411 | 10.1663 | 22.4253 | 22.3032 | 22.1684 | 22 | 21.84 | 21.6758 | 21.5053 | 21.3432 | 17.0589 | 16.7274 | 16.4211
|  | LAMBOURN PRIMARY | HT |  |  |  |  | 11.7084 | 24.7053 | 24.5526 | 24.3505 | 24.1284 | 23.8853 | 23.6495 | 23.3853 | 23.1158 | 21.4232 | 21.0158 | 20.6284 | 10.2137 | 21.8011 | 21.6968 | 21.4842 | 21.2442 | 20.9811 | 20.7253 | 20.4368 | 20.1411 | 18.1968 | 17.7474 | 17.3168 | 10.1905 | 22.4632 | 22.3042 | 22.0947 | 21.8632 | 21.6105 | 21.3663 | 21.0916 | 20.8105 | 19.0053 | 18.5789 | 18.1726
|  | LAMBOURN PRIMARY | HE |  |  |  |  | 11.7632 | 24.7747 | 24.6863 | 24.5695 | 24.4242 | 24.2863 | 24.1558 | 24.0232 | 23.8947 | 20.1705 | 20.0105 | 19.8495 | 10.2411 | 21.8305 | 21.7589 | 21.66 | 21.5284 | 21.4063 | 21.2905 | 21.1705 | 21.04 | 16.6568 | 16.4716 | 16.2842 | 10.2495 | 22.5379 | 22.4474 | 22.3284 | 22.1821 | 22.0421 | 21.9095 | 21.7747 | 21.6442 | 17.6253 | 17.4484 | 17.2621
|  | LAMBOURN PRIMARY | FB |  |  |  |  | 11.8158 | 24.8853 | 24.8347 | 24.7863 | 24.7305 | 24.6737 | 24.6211 | 24.5695 | 24.5189 | 24.3137 | 23.4347 | 23.2474 | 10.3021 | 21.9221 | 21.8863 | 21.8526 | 21.8126 | 21.7716 | 21.7337 | 21.6968 | 21.6611 | 21.4495 | 20.4274 | 20.2147 | 10.3379 | 22.6505 | 22.5989 | 22.5484 | 22.4895 | 22.4316 | 22.3779 | 22.3232 | 22.2705 | 22.0589 | 21.1147 | 20.9158
FAWLEY GSP | LANGLEY BSP | LANGLEY PRIMARY | MINIMUM HEADROOM | SU 45158 01418 | NO | YES | 0 | 10.6108 | 10.3697 | 10.1245 | 9.8424 | 9.7487 | 9.1708 | 6.7771 | 6.2066 | 4.5224 | 2.6729 | 1.7108 | 0.90763 | 6.93 | 6.67 | 6.4089 | 6.1132 | 6.1816 | 5.55 | 2.7637 | 2.1353 | 0.18895 | -1.89 | -2.9626 | -3.8553 | 7.9 | 7.6411 | 7.3821 | 7.0863 | 6.9989 | 6.3737 | 3.6484 | 3.0211 | 1.08 | -0.99474 | -2.0674 | -2.9579
|  | LANGLEY PRIMARY | EE |  |  |  |  | 10.6108 | 10.3708 | 10.1245 | 9.8424 | 10.2097 | 9.8855 | 8.6487 | 8.3266 | 7.4655 | 6.3613 | 5.7129 | 5.2129 | 6.93 | 6.6721 | 6.4089 | 6.1132 | 6.7163 | 6.3805 | 4.9721 | 4.6342 | 3.6563 | 2.3795 | 1.6353 | 1.0637 | 7.9 | 7.6432 | 7.3821 | 7.0863 | 7.5284 | 7.1926 | 5.8053 | 5.4716 | 4.5158 | 3.2632 | 2.5211 | 1.9505
|  | LANGLEY PRIMARY | HT |  |  |  |  | 10.6382 | 10.3697 | 10.7371 | 10.2929 | 9.7487 | 9.1708 | 6.7771 | 6.2066 | 4.5224 | 2.6729 | 1.7108 | 0.90763 | 6.9616 | 6.67 | 7.2584 | 6.7742 | 6.1816 | 5.55 | 2.7637 | 2.1353 | 0.18895 | -1.89 | -2.9626 | -3.8553 | 7.9316 | 7.6411 | 8.0695 | 7.5884 | 6.9989 | 6.3737 | 3.6484 | 3.0211 | 1.08 | -0.99474 | -2.0674 | -2.9579
|  | LANGLEY PRIMARY | HE |  |  |  |  | 10.7697 | 10.5908 | 10.3992 | 10.1634 | 10.5582 | 10.2761 | 9.0813 | 8.8055 | 7.9876 | 7.2561 | 6.8434 | 6.5392 | 7.11 | 6.9226 | 6.7216 | 6.4774 | 7.1132 | 6.8226 | 5.4721 | 5.1889 | 4.2626 | 3.3921 | 2.9089 | 2.5532 | 8.0789 | 7.8916 | 7.6916 | 7.4474 | 7.9221 | 7.6326 | 6.2937 | 6.0116 | 5.1063 | 4.2621 | 3.7916 | 3.4368
|  | LANGLEY PRIMARY | FB |  |  |  |  | 10.9245 | 10.7929 | 10.6929 | 10.5876 | 10.4771 | 10.3624 | 10.2529 | 10.1487 | 10.7382 | 10.2855 | 9.4992 | 9.1508 | 7.2753 | 7.1321 | 7.0237 | 6.91 | 6.7911 | 6.6689 | 6.5521 | 6.4395 | 7.2711 | 6.7816 | 5.8868 | 5.4879 | 8.2432 | 8.1 | 7.9937 | 7.88 | 7.7621 | 7.64 | 7.5232 | 7.4116 | 8.0811 | 7.5947 | 6.7095 | 6.32
FLEET-BRAMLEY GSP | FERNHURST BSP | LANGLEY COURT PRIMARY | MINIMUM HEADROOM | SU 80847 29056 | NO | YES | 0 | 25.9411 | 25.8442 | 25.7295 | 25.5737 | 25.1758 | 24.6126 | 24.0611 | 23.4695 | 22.8474 | 21.4242 | 20.4568 | 19.5747 | 23.2726 | 23.0695 | 22.7726 | 22.2758 | 21.6768 | 21.0389 | 20.4147 | 19.7411 | 19.0316 | 17.4042 | 16.2905 | 15.2737 | 21.8621 | 21.7516 | 21.6126 | 21.4126 | 21.1737 | 20.9126 | 20.6568 | 20.3979 | 19.9211 | 18.2958 | 17.1842 | 16.1684
|  | LANGLEY COURT PRIMARY | EE |  |  |  |  | 25.9411 | 25.8442 | 25.7337 | 25.5874 | 25.3895 | 25.2 | 25.0221 | 24.84 | 24.6632 | 23.9874 | 23.3074 | 22.7105 | 23.2726 | 23.0695 | 22.8558 | 22.6021 | 22.3137 | 22.0568 | 21.7916 | 21.5126 | 21.2084 | 20.4168 | 19.6179 | 18.9137 | 21.8621 | 21.7516 | 21.6274 | 21.4674 | 21.2579 | 21.0589 | 20.8705 | 20.6758 | 20.4821 | 20.2747 | 20.0821 | 19.8032
|  | LANGLEY COURT PRIMARY | HT |  |  |  |  | 25.9432 | 25.8505 | 25.7295 | 25.5737 | 25.1758 | 24.6126 | 24.0611 | 23.4695 | 22.8474 | 21.4242 | 20.4568 | 19.5747 | 23.3095 | 23.1105 | 22.7726 | 22.2758 | 21.6768 | 21.0389 | 20.4147 | 19.7411 | 19.0316 | 17.4042 | 16.2905 | 15.2737 | 21.8684 | 21.7621 | 21.6126 | 21.4126 | 21.1737 | 20.9126 | 20.6568 | 20.3979 | 19.9211 | 18.2958 | 17.1842 | 16.1684
|  | LANGLEY COURT PRIMARY | HE |  |  |  |  | 25.9653 | 25.8768 | 25.7716 | 25.6316 | 25.4379 | 25.26 | 25.0832 | 24.9032 | 24.7284 | 24.7179 | 24.2253 | 23.7853 | 23.4179 | 23.2716 | 23.1063 | 22.8947 | 22.6358 | 22.4147 | 22.1968 | 21.9674 | 21.7116 | 21.2589 | 20.6695 | 20.1411 | 21.9021 | 21.8063 | 21.6926 | 21.5442 | 21.3421 | 21.1579 | 20.9758 | 20.7895 | 20.6042 | 20.5526 | 20.4547 | 20.3716
|  | LANGLEY COURT PRIMARY | FB |  |  |  |  | 26.0358 | 25.9937 | 25.9558 | 25.9126 | 25.8653 | 25.8158 | 25.7695 | 25.7263 | 25.6789 | 25.5095 | 25.2305 | 24.8411 | 23.5411 | 23.4295 | 23.3453 | 23.2516 | 23.1547 | 23.0611 | 22.9705 | 22.8853 | 22.7768 | 22.2621 | 21.7379 | 21.28 | 21.98 | 21.9284 | 21.8842 | 21.8347 | 21.7811 | 21.7253 | 21.6737 | 21.6253 | 21.5695 | 21.3558 | 21.2042 | 21.0937
AXMINSTER GSP | YEOVIL BSP | LARKHILL PRIMARY | MINIMUM HEADROOM | ST 53677 16914 | NO | YES | 0 | 31.4279 | 31.1153 | 30.6995 | 30.0826 | 29.3458 | 28.5995 | 27.9195 | 27.2111 | 26.6774 | 25.0805 | 23.8447 | 22.5174 | 27.9789 | 27.4474 | 26.8674 | 26.1905 | 25.3884 | 24.5726 | 23.8368 | 23.0674 | 22.5021 | 20.7653 | 19.4011 | 17.9158 | 29.5326 | 29.0516 | 28.5253 | 27.8695 | 27.0811 | 26.2779 | 25.5526 | 24.7958 | 24.2316 | 22.4968 | 21.1358 | 19.6537
|  | LARKHILL PRIMARY | EE |  |  |  |  | 31.4279 | 31.1153 | 30.6995 | 30.0826 | 29.3458 | 28.7205 | 28.2626 | 27.5847 | 26.9184 | 25.8795 | 25.0363 | 24.1226 | 27.9789 | 27.4474 | 26.8674 | 26.1905 | 25.3884 | 24.7137 | 24.2295 | 23.4884 | 22.76 | 21.5779 | 20.6221 | 19.5789 | 29.5326 | 29.0516 | 28.5253 | 27.8695 | 27.0811 | 26.4158 | 25.9368 | 25.2063 | 24.4884 | 23.3105 | 22.3568 | 21.3147
|  | LARKHILL PRIMARY | HT |  |  |  |  | 31.4626 | 31.1689 | 30.7826 | 30.1626 | 29.4616 | 28.5995 | 27.9195 | 27.2111 | 26.6774 | 25.0805 | 23.8447 | 22.5174 | 28.0537 | 27.5547 | 26.9663 | 26.2874 | 25.5221 | 24.5726 | 23.8368 | 23.0674 | 22.5021 | 20.7653 | 19.4011 | 17.9158 | 29.5968 | 29.1463 | 28.6105 | 27.9621 | 27.2105 | 26.2779 | 25.5526 | 24.7958 | 24.2316 | 22.4968 | 21.1358 | 19.6537
|  | LARKHILL PRIMARY | HE |  |  |  |  | 31.5489 | 31.2763 | 30.9721 | 30.5111 | 29.8111 | 29.2395 | 28.8553 | 28.3363 | 27.8279 | 27.2384 | 26.7658 | 26.1679 | 28.2284 | 27.7895 | 27.2937 | 26.6821 | 25.9232 | 25.3084 | 24.9116 | 24.3579 | 23.8158 | 23.1158 | 22.5705 | 21.8747 | 29.7516 | 29.3516 | 28.9 | 28.3389 | 27.6021 | 26.9958 | 26.6011 | 26.0547 | 25.5189 | 24.84 | 24.3011 | 23.6063
|  | LARKHILL PRIMARY | FB |  |  |  |  | 31.7237 | 31.6037 | 31.4742 | 31.3279 | 31.1679 | 31.0195 | 30.8826 | 30.7405 | 30.5163 | 29.6089 | 29.0342 | 28.4311 | 28.5453 | 28.2716 | 28.0358 | 27.7737 | 27.4863 | 27.2305 | 27.0674 | 26.9126 | 26.6642 | 25.6495 | 25.0021 | 24.3095 | 30.0421 | 29.7979 | 29.5863 | 29.3505 | 29.0937 | 28.8632 | 28.7116 | 28.5684 | 28.3358 | 27.3421 | 26.7095 | 26.0337
COWLEY GSP | WITNEY BSP | LEAFIELD PRIMARY | MINIMUM HEADROOM | SP 30282 15270 | NO | YES | 0 | 4.7905 | 4.6863 | 4.5632 | 4.3947 | 4.2242 | 4.0484 | 3.8863 | 3.7042 | 3.5242 | 3.0137 | 2.5863 | 2.1695 | 4.7674 | 4.6537 | 4.52 | 4.3358 | 4.1537 | 3.9663 | 3.7947 | 3.6 | 3.4074 | 2.8516 | 2.3758 | 1.9084 | 4.7684 | 4.6547 | 4.5211 | 4.3368 | 4.1547 | 3.9684 | 3.7968 | 3.6021 | 3.4095 | 2.8547 | 2.38 | 1.9137
|  | LEAFIELD PRIMARY | EE |  |  |  |  | 4.7905 | 4.6863 | 4.5842 | 4.4642 | 4.3189 | 4.1853 | 4.0526 | 3.9168 | 3.7863 | 3.5421 | 3.2758 | 3.0042 | 4.7674 | 4.6537 | 4.5432 | 4.4168 | 4.2653 | 4.1253 | 3.9853 | 3.8432 | 3.7063 | 3.4316 | 3.1295 | 2.82 | 4.7684 | 4.6547 | 4.5442 | 4.4168 | 4.2663 | 4.1263 | 3.9863 | 3.8442 | 3.7084 | 3.4337 | 3.1326 | 2.8232
|  | LEAFIELD PRIMARY | HT |  |  |  |  | 4.8032 | 4.7 | 4.5632 | 4.3947 | 4.2242 | 4.0484 | 3.8863 | 3.7042 | 3.5242 | 3.0137 | 2.5863 | 2.1695 | 4.7821 | 4.6684 | 4.52 | 4.3358 | 4.1537 | 3.9663 | 3.7947 | 3.6 | 3.4074 | 2.8516 | 2.3758 | 1.9084 | 4.7821 | 4.6695 | 4.5211 | 4.3368 | 4.1547 | 3.9684 | 3.7968 | 3.6021 | 3.4095 | 2.8547 | 2.38 | 1.9137
|  | LEAFIELD PRIMARY | HE |  |  |  |  | 4.8705 | 4.7958 | 4.7179 | 4.6179 | 4.4916 | 4.3747 | 4.2621 | 4.1484 | 4.0368 | 3.9568 | 3.7947 | 3.6095 | 4.8568 | 4.7779 | 4.6958 | 4.5916 | 4.4611 | 4.3411 | 4.2242 | 4.1074 | 3.9916 | 3.8979 | 3.7105 | 3.4947 | 4.8579 | 4.7779 | 4.6958 | 4.5926 | 4.4611 | 4.3411 | 4.2253 | 4.1074 | 3.9926 | 3.8989 | 3.7126 | 3.4968
|  | LEAFIELD PRIMARY | FB |  |  |  |  | 4.9295 | 4.8716 | 4.8274 | 4.7821 | 4.7316 | 4.6832 | 4.6337 | 4.5895 | 4.5421 | 4.3537 | 4.1716 | 3.9895 | 4.9211 | 4.8579 | 4.8095 | 4.76 | 4.7063 | 4.6537 | 4.6 | 4.5516 | 4.5 | 4.2968 | 4.0916 | 3.8832 | 4.9211 | 4.8579 | 4.8105 | 4.76 | 4.7063 | 4.6537 | 4.6011 | 4.5526 | 4.5011 | 4.2979 | 4.0926 | 3.8853
WILLESDEN GSP | ACTON LANE BSP | LEAMINGTON PARK PRIMARY | MINIMUM HEADROOM | TQ 20539 81536 | NO | NO | 0 | 25.2453 | 22.6316 | 21.2411 | 19.5663 | 17.5337 | 15.6189 | 15.2 | 14.8042 | 14.3347 | 13.5716 | 13.1684 | 12.8042 | 24.2495 | 20.7537 | 19.0126 | 16.9158 | 14.3716 | 12.1221 | 11.6358 | 11.1905 | 10.6516 | 9.7905 | 9.3421 | 8.9358 | 24.9558 | 21.5158 | 19.7737 | 17.6758 | 15.1316 | 12.8811 | 12.3947 | 11.9495 | 11.4095 | 10.5495 | 10.1 | 9.6937
|  | LEAMINGTON PARK PRIMARY | EE |  |  |  |  | 25.2474 | 25.1821 | 22.0116 | 20.4895 | 18.8821 | 17.1358 | 15.2 | 14.9105 | 14.6611 | 14.0284 | 13.7432 | 13.5053 | 24.2495 | 24.1463 | 19.9832 | 18.0779 | 16.0705 | 13.9084 | 11.6358 | 11.3074 | 11.0263 | 10.2947 | 9.9716 | 9.7011 | 24.9568 | 24.8863 | 20.7453 | 18.8389 | 16.8316 | 14.6674 | 12.3947 | 12.0663 | 11.7853 | 11.0537 | 10.7284 | 10.4579
|  | LEAMINGTON PARK PRIMARY | HT |  |  |  |  | 25.2453 | 22.6316 | 21.2411 | 19.5663 | 17.5337 | 15.6189 | 15.2253 | 14.8042 | 14.3347 | 13.5716 | 13.1684 | 12.8042 | 24.2495 | 20.7537 | 19.0126 | 16.9158 | 14.3716 | 12.1221 | 11.6726 | 11.1905 | 10.6516 | 9.7905 | 9.3421 | 8.9358 | 24.9558 | 21.5158 | 19.7737 | 17.6758 | 15.1316 | 12.8811 | 12.4316 | 11.9495 | 11.4095 | 10.5495 | 10.1 | 9.6937
|  | LEAMINGTON PARK PRIMARY | HE |  |  |  |  | 25.2589 | 25.1958 | 22.6105 | 21.7253 | 20.8547 | 19.8611 | 18.8432 | 17.8263 | 17.0305 | 14.3726 | 14.0126 | 13.8968 | 24.2568 | 24.2179 | 20.7379 | 19.6358 | 18.5589 | 17.3253 | 16.06 | 14.7958 | 13.8232 | 10.6874 | 10.2684 | 10.1347 | 24.9684 | 24.9095 | 21.5 | 20.3968 | 19.32 | 18.0853 | 16.82 | 15.5558 | 14.5832 | 11.4463 | 11.0274 | 10.8937
|  | LEAMINGTON PARK PRIMARY | FB |  |  |  |  | 25.2874 | 25.2484 | 25.2168 | 24.2937 | 23.9411 | 23.5537 | 23.08 | 22.5684 | 22.0274 | 19.9537 | 19.5063 | 19.3516 | 24.2768 | 24.2505 | 24.2274 | 22.8547 | 22.4179 | 21.9368 | 21.3463 | 20.7074 | 20.0326 | 17.4432 | 16.8947 | 16.7095 | 24.9947 | 24.9579 | 24.9284 | 23.6179 | 23.18 | 22.7 | 22.1084 | 21.4695 | 20.7947 | 18.2032 | 17.6558 | 17.4695
MINETY GSP | STRATTON (RESERVE) BSP | LECHLADE PRIMARY | MINIMUM HEADROOM | SP 22074 00496 | NO | YES | 0.094737 | 7.5589 | 7.4526 | 7.3337 | 7.1505 | 6.9263 | 6.6768 | 6.4337 | 6.1789 | 5.9242 | 5.2579 | 4.7442 | 4.2074 | 8.6779 | 8.5632 | 8.4347 | 8.2358 | 7.9916 | 7.7211 | 7.4558 | 7.1768 | 6.8989 | 6.1642 | 5.5916 | 4.9874 | 7.4968 | 7.3821 | 7.2526 | 7.0526 | 6.8084 | 6.5368 | 6.2705 | 5.9916 | 5.7126 | 4.9758 | 4.4021 | 3.7958
|  | LECHLADE PRIMARY | EE |  |  |  |  | 7.5589 | 7.4526 | 7.3442 | 7.2221 | 7.0663 | 6.9095 | 6.7474 | 6.5926 | 6.4379 | 6.0874 | 5.7326 | 5.3579 | 8.6779 | 8.5632 | 8.4474 | 8.3179 | 8.1537 | 7.9874 | 7.8147 | 7.6484 | 7.4842 | 7.0916 | 6.6905 | 6.2632 | 7.4968 | 7.3821 | 7.2653 | 7.1347 | 6.9705 | 6.8042 | 6.6305 | 6.4642 | 6.3 | 5.9063 | 5.5042 | 5.0747
|  | LECHLADE PRIMARY | HT |  |  |  |  | 7.5758 | 7.4705 | 7.3337 | 7.1505 | 6.9263 | 6.6768 | 6.4337 | 6.1789 | 5.9242 | 5.2579 | 4.7442 | 4.2074 | 8.6968 | 8.5832 | 8.4347 | 8.2358 | 7.9916 | 7.7211 | 7.4558 | 7.1768 | 6.8989 | 6.1642 | 5.5916 | 4.9874 | 7.5147 | 7.4011 | 7.2526 | 7.0526 | 6.8084 | 6.5368 | 6.2705 | 5.9916 | 5.7126 | 4.9758 | 4.4021 | 3.7958
|  | LECHLADE PRIMARY | HE |  |  |  |  | 7.6442 | 7.5747 | 7.4926 | 7.3958 | 7.2632 | 7.1253 | 6.9905 | 6.8589 | 6.7295 | 6.5558 | 6.3189 | 6.0442 | 8.7747 | 8.7 | 8.6137 | 8.5126 | 8.3758 | 8.2305 | 8.0874 | 7.9505 | 7.8137 | 7.6168 | 7.3442 | 7.0274 | 7.5926 | 7.5189 | 7.4316 | 7.3316 | 7.1937 | 7.0474 | 6.9053 | 6.7674 | 6.6305 | 6.4337 | 6.16 | 5.8411
|  | LECHLADE PRIMARY | FB |  |  |  |  | 7.7011 | 7.6432 | 7.5979 | 7.5495 | 7.4958 | 7.4368 | 7.3779 | 7.3242 | 7.2674 | 7.0453 | 6.8274 | 6.5968 | 8.8358 | 8.7716 | 8.7232 | 8.6705 | 8.6126 | 8.5484 | 8.4842 | 8.4253 | 8.3642 | 8.1221 | 7.8768 | 7.6126 | 7.6547 | 7.5905 | 7.5411 | 7.4884 | 7.4316 | 7.3663 | 7.3021 | 7.2432 | 7.1811 | 6.9389 | 6.6937 | 6.4284
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LECKHAMPSTEAD PRIMARY | MINIMUM HEADROOM | SU 43962 77635 | NO | YES | 0 | 8.7253 | 8.6632 | 8.5853 | 8.4874 | 8.3684 | 8.2379 | 8.1116 | 7.9821 | 7.8505 | 7.5253 | 7.3053 | 7.1063 | 8.0937 | 8.0095 | 7.9253 | 7.8221 | 7.6958 | 7.5589 | 7.4253 | 7.2884 | 7.1474 | 6.7989 | 6.56 | 6.3432 | 6.2411 | 6.2 | 6.1526 | 6.0863 | 6.0084 | 5.9221 | 5.8358 | 5.7516 | 5.6684 | 5.48 | 5.3663 | 5.2674
|  | LECKHAMPSTEAD PRIMARY | EE |  |  |  |  | 8.7253 | 8.6632 | 8.5853 | 8.4947 | 8.3874 | 8.2853 | 8.1874 | 8.0842 | 7.9874 | 7.8305 | 7.6895 | 7.5747 | 8.0937 | 8.0095 | 7.9253 | 7.8295 | 7.7189 | 7.6126 | 7.5105 | 7.4032 | 7.3021 | 7.1263 | 6.9695 | 6.84 | 6.2411 | 6.2 | 6.1547 | 6.0926 | 6.0095 | 5.9295 | 5.8568 | 5.7789 | 5.7063 | 5.6558 | 5.6084 | 5.5726
|  | LECKHAMPSTEAD PRIMARY | HT |  |  |  |  | 8.7274 | 8.6863 | 8.5968 | 8.4874 | 8.3684 | 8.2379 | 8.1116 | 7.9821 | 7.8505 | 7.5253 | 7.3053 | 7.1063 | 8.1126 | 8.0358 | 7.94 | 7.8221 | 7.6958 | 7.5589 | 7.4253 | 7.2884 | 7.1474 | 6.7989 | 6.56 | 6.3432 | 6.2432 | 6.2042 | 6.1526 | 6.0863 | 6.0084 | 5.9221 | 5.8358 | 5.7516 | 5.6684 | 5.48 | 5.3663 | 5.2674
|  | LECKHAMPSTEAD PRIMARY | HE |  |  |  |  | 8.7379 | 8.7 | 8.6568 | 8.5979 | 8.5095 | 8.4221 | 8.3358 | 8.2495 | 8.1642 | 8.1158 | 8.0495 | 7.9926 | 8.1568 | 8.0979 | 8.0337 | 7.9558 | 7.8579 | 7.7684 | 7.68 | 7.5905 | 7.5032 | 7.4463 | 7.3705 | 7.3042 | 6.2537 | 6.2158 | 6.1726 | 6.1137 | 6.0326 | 5.9589 | 5.8863 | 5.8126 | 5.7389 | 5.7432 | 5.7316 | 5.7232
|  | LECKHAMPSTEAD PRIMARY | FB |  |  |  |  | 8.7663 | 8.7484 | 8.7326 | 8.7147 | 8.6947 | 8.6663 | 8.6316 | 8.5989 | 8.5653 | 8.4295 | 8.3189 | 8.2316 | 8.2084 | 8.1611 | 8.1274 | 8.0905 | 8.0526 | 8.0137 | 7.9768 | 7.9411 | 7.9063 | 7.7589 | 7.6368 | 7.5368 | 6.2821 | 6.2642 | 6.2484 | 6.2305 | 6.2105 | 6.1905 | 6.1705 | 6.1526 | 6.1337 | 6.0621 | 6.0232 | 5.9979
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | LEE-ON-SOLENT PRIMARY | MINIMUM HEADROOM | SU 56858 00293 | NO | YES | 0 | 26.5158 | 26.3316 | 25.5168 | 24.4389 | 23.3432 | 22.2032 | 21.1989 | 20.3326 | 19.42 | 17.4895 | 16.0442 | 14.7358 | 22.8463 | 22.0421 | 21.0653 | 19.8537 | 18.6316 | 17.3632 | 16.2526 | 15.3032 | 14.2989 | 12.1895 | 10.5905 | 9.14 | 24.7579 | 23.9389 | 22.9589 | 21.7432 | 20.5179 | 19.2453 | 18.1326 | 17.18 | 16.1726 | 14.0579 | 12.4537 | 10.9989
|  | LEE-ON-SOLENT PRIMARY | EE |  |  |  |  | 26.5158 | 26.3316 | 25.66 | 24.8158 | 23.9768 | 23.0926 | 22.2442 | 21.6116 | 21.0095 | 20.1105 | 19.1137 | 18.2516 | 22.8463 | 22.2579 | 21.2316 | 20.2905 | 19.3737 | 18.4 | 17.4642 | 16.7821 | 16.1347 | 15.1253 | 13.9937 | 13.0168 | 24.7579 | 24.1558 | 23.1253 | 22.1811 | 21.2611 | 20.2863 | 19.3474 | 18.6642 | 18.0158 | 17.0032 | 15.8684 | 14.8863
|  | LEE-ON-SOLENT PRIMARY | HT |  |  |  |  | 26.52 | 26.3463 | 25.5168 | 24.4389 | 23.3432 | 22.2032 | 21.1989 | 20.3326 | 19.42 | 17.4895 | 16.0442 | 14.7358 | 22.8547 | 22.0421 | 21.0653 | 19.8537 | 18.6316 | 17.3632 | 16.2526 | 15.3032 | 14.2989 | 12.1895 | 10.5905 | 9.14 | 24.8053 | 23.9389 | 22.9589 | 21.7432 | 20.5179 | 19.2453 | 18.1326 | 17.18 | 16.1726 | 14.0579 | 12.4537 | 10.9989
|  | LEE-ON-SOLENT PRIMARY | HE |  |  |  |  | 26.5547 | 26.3842 | 26.1368 | 25.4368 | 24.6495 | 24.0084 | 23.2189 | 22.5821 | 21.9758 | 21.56 | 21.06 | 20.5958 | 22.9042 | 22.6337 | 21.7779 | 21.0042 | 20.1453 | 19.4526 | 18.5842 | 17.8979 | 17.2442 | 16.7516 | 16.1758 | 15.6368 | 24.9621 | 24.5326 | 23.6747 | 22.8979 | 22.0368 | 21.3432 | 20.4726 | 19.7842 | 19.1295 | 18.6347 | 18.0558 | 17.5147
|  | LEE-ON-SOLENT PRIMARY | FB |  |  |  |  | 26.6874 | 26.6032 | 26.5274 | 26.4432 | 26.3484 | 26.1242 | 25.7705 | 25.4842 | 25.2 | 24.3842 | 23.7726 | 23.22 | 23.0453 | 22.9442 | 22.78 | 22.3821 | 22.0484 | 21.7526 | 21.3547 | 21.0347 | 20.7179 | 19.82 | 19.1379 | 18.5105 | 25.0947 | 24.9684 | 24.6789 | 24.28 | 23.9453 | 23.6484 | 23.2495 | 22.9284 | 22.6105 | 21.7105 | 21.0263 | 20.3968
LOVEDEAN GSP | HAVANT BSP | LEIGH PARK PRIMARY | MINIMUM HEADROOM | SU 72144 07875 | NO | YES | 0 | 36.2463 | 36.0842 | 35.9053 | 35.6463 | 35.2979 | 34.9168 | 34.1011 | 33.0832 | 32.0653 | 28.44 | 26.8074 | 24.9053 | 31.1242 | 30.6621 | 29.9726 | 29.1242 | 28.1516 | 27.0968 | 25.9968 | 24.8579 | 23.7179 | 19.5916 | 17.7579 | 15.6 | 35.1516 | 34.74 | 34.1263 | 33.3684 | 32.4989 | 31.5547 | 30.5726 | 29.5568 | 28.5411 | 24.4758 | 22.6442 | 20.4895
|  | LEIGH PARK PRIMARY | EE |  |  |  |  | 36.2463 | 36.0842 | 35.9053 | 35.6568 | 35.3084 | 34.9716 | 34.6505 | 34.3168 | 33.9884 | 31.8989 | 30.8179 | 29.4874 | 31.1242 | 30.68 | 30.0474 | 29.4821 | 28.94 | 28.4316 | 27.8379 | 27.2063 | 26.5758 | 23.5632 | 22.3337 | 20.7989 | 35.1516 | 34.7505 | 34.1863 | 33.6705 | 33.16 | 32.6789 | 32.1305 | 31.5474 | 30.9663 | 28.3726 | 27.2116 | 25.6811
|  | LEIGH PARK PRIMARY | HT |  |  |  |  | 36.2621 | 36.1147 | 35.9242 | 35.6463 | 35.2979 | 34.9168 | 34.1011 | 33.0832 | 32.0653 | 28.44 | 26.8074 | 24.9053 | 31.1989 | 30.6621 | 29.9726 | 29.1242 | 28.1516 | 27.0968 | 25.9968 | 24.8579 | 23.7179 | 19.5916 | 17.7579 | 15.6 | 35.2168 | 34.74 | 34.1263 | 33.3684 | 32.4989 | 31.5547 | 30.5726 | 29.5568 | 28.5411 | 24.4758 | 22.6442 | 20.4895
|  | LEIGH PARK PRIMARY | HE |  |  |  |  | 36.2716 | 36.1105 | 35.9295 | 35.68 | 35.3368 | 35.02 | 34.6979 | 34.3642 | 34.0337 | 33.1 | 32.3905 | 31.3832 | 31.3526 | 30.9926 | 30.4316 | 29.9232 | 29.4126 | 28.9537 | 28.4221 | 27.8537 | 27.2863 | 24.9295 | 24.1063 | 22.9274 | 35.3326 | 35.02 | 34.5158 | 34.0474 | 33.5621 | 33.1242 | 32.6274 | 32.0968 | 31.5684 | 29.5726 | 28.8653 | 27.8063
|  | LEIGH PARK PRIMARY | FB |  |  |  |  | 36.3863 | 36.3 | 36.2232 | 36.1358 | 36.0389 | 35.9421 | 35.8474 | 35.7589 | 35.6653 | 35.2768 | 34.9358 | 34.0916 | 31.5547 | 31.2989 | 31.0653 | 30.7947 | 30.5958 | 30.4189 | 30.2232 | 30.0063 | 29.7642 | 28.5989 | 26.9074 | 25.9368 | 35.5126 | 35.3011 | 35.0989 | 34.8558 | 34.6726 | 34.5074 | 34.3274 | 34.1295 | 33.9105 | 32.8695 | 31.4063 | 30.5642
BRAMLEY (BASI) GSP | READING BSP | LITTLE HUNGERFORD PRIMARY | MINIMUM HEADROOM | SU 75372 72019 | NO | YES | 0 | 37.5095 | 37.1137 | 36.6589 | 36.0232 | 35.2642 | 34.4211 | 33.5979 | 32.7547 | 31.2211 | 27.8137 | 25.4221 | 22.4747 | 36.0305 | 35.54 | 34.9811 | 34.1474 | 32.5695 | 30.6832 | 28.9768 | 27.2432 | 25.5705 | 21.8642 | 19.2358 | 15.9295 | 37.4884 | 36.7558 | 35.9358 | 34.6442 | 33.1305 | 31.3263 | 29.6884 | 28.0263 | 26.3968 | 22.6905 | 20.0621 | 16.7558
|  | LITTLE HUNGERFORD PRIMARY | EE |  |  |  |  | 37.5095 | 37.1137 | 36.6768 | 36.1032 | 35.3305 | 34.5853 | 33.8968 | 33.1916 | 32.5084 | 31.9716 | 31.48 | 29.7368 | 36.0305 | 35.54 | 35.0158 | 34.3611 | 33.5232 | 32.5737 | 31.4621 | 30.3474 | 29.4 | 27.72 | 26.1263 | 23.9842 | 37.4884 | 36.7558 | 36.0116 | 35.1558 | 34.1516 | 33.0811 | 32.0032 | 30.9189 | 29.9926 | 28.4021 | 26.8947 | 24.8105
|  | LITTLE HUNGERFORD PRIMARY | HT |  |  |  |  | 37.5295 | 37.1547 | 36.6589 | 36.0232 | 35.2642 | 34.4211 | 33.5979 | 32.7547 | 31.2211 | 27.8137 | 25.4221 | 22.4747 | 36.0547 | 35.6074 | 34.9811 | 34.1474 | 32.5695 | 30.6832 | 28.9768 | 27.2432 | 25.5705 | 21.8642 | 19.2358 | 15.9295 | 37.6284 | 36.8947 | 35.9358 | 34.6442 | 33.1305 | 31.3263 | 29.6884 | 28.0263 | 26.3968 | 22.6905 | 20.0621 | 16.7558
|  | LITTLE HUNGERFORD PRIMARY | HE |  |  |  |  | 37.6189 | 37.26 | 36.8674 | 36.3263 | 35.58 | 34.8926 | 34.2179 | 33.5305 | 32.8674 | 32.9053 | 32.76 | 32.6 | 36.1379 | 35.7842 | 35.3958 | 34.8116 | 34.0211 | 33.2621 | 32.5084 | 31.7432 | 31.0411 | 30.5463 | 29.6726 | 28.1368 | 37.9853 | 37.4474 | 36.8821 | 36.1768 | 35.2737 | 34.3379 | 33.3832 | 32.4232 | 31.6211 | 31.0811 | 30.2653 | 28.8358
|  | LITTLE HUNGERFORD PRIMARY | FB |  |  |  |  | 37.9158 | 37.7379 | 37.58 | 37.4074 | 37.2147 | 37.0179 | 36.8253 | 36.6432 | 36.4568 | 35.76 | 35.3484 | 35.0432 | 36.4295 | 36.2568 | 36.1032 | 35.9337 | 35.7179 | 35.4663 | 35.2126 | 34.9695 | 34.7421 | 33.7505 | 32.5926 | 31.2021 | 38.5 | 38.0979 | 37.7937 | 37.4705 | 37.1274 | 36.7379 | 36.3326 | 35.9358 | 35.6042 | 34.2579 | 33.1579 | 31.8537
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW PRIMARY | MINIMUM HEADROOM | SU 86037 87794 | NO | YES | 0 | 29.1971 | 28.9518 | 28.7003 | 28.3118 | 27.8308 | 27.3034 | 26.7708 | 26.2266 | 25.6845 | 24.3876 | 23.5529 | 22.8213 | 22.5171 | 22.1497 | 21.7908 | 21.2182 | 20.4866 | 19.6803 | 18.855 | 17.9908 | 17.1287 | 15.0508 | 13.6761 | 12.4687 | 17.6697 | 17.3034 | 16.9434 | 16.3718 | 15.6424 | 14.8382 | 14.0139 | 13.1508 | 12.2897 | 10.2161 | 8.8434 | 7.6392
|  | LITTLE MARLOW PRIMARY | EE |  |  |  |  | 29.1971 | 28.9518 | 28.7003 | 28.3897 | 27.9855 | 27.6108 | 27.2445 | 26.8624 | 26.4866 | 25.9087 | 25.3918 | 24.9645 | 22.5171 | 22.1497 | 21.7908 | 21.3845 | 20.9045 | 20.4529 | 19.975 | 19.475 | 18.9834 | 17.8666 | 16.8708 | 16.0318 | 17.6697 | 17.3034 | 16.9434 | 16.5392 | 16.0592 | 15.6076 | 15.1308 | 14.6297 | 14.1392 | 13.0266 | 12.0308 | 11.195
|  | LITTLE MARLOW PRIMARY | HT |  |  |  |  | 29.235 | 29.0087 | 28.7066 | 28.3118 | 27.8308 | 27.3034 | 26.7708 | 26.2266 | 25.6845 | 24.3876 | 23.5529 | 22.8213 | 22.5982 | 22.2666 | 21.8171 | 21.2182 | 20.4866 | 19.6803 | 18.855 | 17.9908 | 17.1287 | 15.0508 | 13.6761 | 12.4687 | 17.7497 | 17.4192 | 16.9708 | 16.3718 | 15.6424 | 14.8382 | 14.0139 | 13.1508 | 12.2897 | 10.2161 | 8.8434 | 7.6392
|  | LITTLE MARLOW PRIMARY | HE |  |  |  |  | 29.3371 | 29.1382 | 28.9266 | 28.6487 | 28.2666 | 27.9276 | 27.5908 | 27.2403 | 26.8961 | 26.7266 | 26.4603 | 26.2487 | 22.7961 | 22.5329 | 22.2634 | 21.9308 | 21.5003 | 21.1139 | 20.7182 | 20.3013 | 19.8918 | 19.4192 | 18.8255 | 18.335 | 17.9476 | 17.6855 | 17.4161 | 17.0834 | 16.6539 | 16.2676 | 15.8718 | 15.455 | 15.0455 | 14.575 | 13.9824 | 13.4939
|  | LITTLE MARLOW PRIMARY | FB |  |  |  |  | 29.4834 | 29.3529 | 29.2476 | 29.1339 | 29.0108 | 28.8876 | 28.7645 | 28.6455 | 28.5203 | 28.0203 | 27.6487 | 27.3592 | 23.0024 | 22.7918 | 22.635 | 22.4697 | 22.2939 | 22.1203 | 21.9413 | 21.7613 | 21.5782 | 20.7918 | 20.1024 | 19.5213 | 18.1539 | 17.9445 | 17.7876 | 17.6224 | 17.4466 | 17.2729 | 17.0939 | 16.915 | 16.7318 | 15.9466 | 15.2592 | 14.6792
NURSLING GSP | ROWNHAMS BSP | LORDSHILL PRIMARY | MINIMUM HEADROOM | SU 38746 16055 | NO | YES | 0 | 30.6895 | 30.5821 | 30.4663 | 30.1232 | 29.7263 | 29.4221 | 29.0905 | 28.7063 | 28.2842 | 25.7084 | 24.7674 | 23.8621 | 28.1095 | 28.0021 | 27.8863 | 27.7284 | 27.5032 | 27.2958 | 27.0958 | 26.8189 | 26.3611 | 23.4179 | 22.3653 | 21.3484 | 29.6926 | 29.4716 | 29.1126 | 28.6 | 28.1716 | 27.8526 | 27.5032 | 27.0916 | 26.6379 | 23.7326 | 22.6916 | 21.6832
|  | LORDSHILL PRIMARY | EE |  |  |  |  | 30.6895 | 30.5821 | 30.4663 | 30.2095 | 29.8926 | 29.5916 | 29.2926 | 29.0147 | 28.7411 | 26.9453 | 26.1021 | 25.4832 | 28.1095 | 28.0021 | 27.8863 | 27.7284 | 27.5032 | 27.2958 | 27.1074 | 26.9095 | 26.7137 | 24.8032 | 23.8379 | 23.1295 | 29.6926 | 29.4716 | 29.1147 | 28.6989 | 28.3684 | 28.0516 | 27.7358 | 27.4453 | 27.16 | 25.1021 | 24.1495 | 23.4505
|  | LORDSHILL PRIMARY | HT |  |  |  |  | 30.6989 | 30.6032 | 30.4747 | 30.1232 | 29.7263 | 29.4221 | 29.0905 | 28.7063 | 28.2842 | 25.7084 | 24.7674 | 23.8621 | 28.1189 | 28.0232 | 27.8947 | 27.7295 | 27.5316 | 27.3137 | 27.0958 | 26.8189 | 26.3611 | 23.4179 | 22.3653 | 21.3484 | 29.7326 | 29.5242 | 29.1126 | 28.6 | 28.1716 | 27.8526 | 27.5032 | 27.0916 | 26.6379 | 23.7326 | 22.6916 | 21.6832
|  | LORDSHILL PRIMARY | HE |  |  |  |  | 30.7147 | 30.6105 | 30.4989 | 30.3421 | 30.1168 | 29.9105 | 29.6411 | 29.3947 | 29.1589 | 27.7211 | 27.1242 | 26.6905 | 28.1347 | 28.0305 | 27.9189 | 27.7621 | 27.5368 | 27.3379 | 27.1453 | 26.9453 | 26.7516 | 25.6811 | 24.9863 | 24.48 | 29.8463 | 29.6821 | 29.3758 | 29 | 28.6958 | 28.4147 | 28.1337 | 27.88 | 27.6379 | 25.9695 | 25.2853 | 24.7863
|  | LORDSHILL PRIMARY | FB |  |  |  |  | 30.7874 | 30.7358 | 30.6884 | 30.6337 | 30.5758 | 30.5158 | 30.4579 | 30.4053 | 30.3474 | 29.9968 | 28.6937 | 28.2811 | 28.2074 | 28.1558 | 28.1084 | 28.0537 | 27.9958 | 27.9358 | 27.8779 | 27.8253 | 27.7674 | 27.5558 | 26.7074 | 26.2347 | 29.9737 | 29.8484 | 29.6916 | 29.5211 | 29.4032 | 29.2821 | 29.1579 | 29.0411 | 28.9326 | 28.4811 | 26.9905 | 26.5242
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LOVE LANE PRIMARY | MINIMUM HEADROOM | SU 47334 68495 | NO | YES | 0 | 45.0568 | 44.8632 | 44.62 | 44.3368 | 43.9768 | 43.2779 | 42.6074 | 41.8495 | 41.0537 | 39.3442 | 38.2084 | 37.0789 | 41.8832 | 41.7179 | 41.5242 | 41.2495 | 40.9053 | 39.8895 | 39.1242 | 38.2789 | 37.4011 | 35.5263 | 34.2747 | 33.02 | 43.2874 | 43.0526 | 42.3063 | 41.6821 | 40.6832 | 39.6284 | 38.8747 | 38.0453 | 37.1832 | 35.3389 | 34.1095 | 32.8768
|  | LOVE LANE PRIMARY | EE |  |  |  |  | 45.0568 | 44.8632 | 44.62 | 44.3558 | 43.9874 | 43.6347 | 43.3274 | 43.0105 | 42.6126 | 41.8926 | 41.1095 | 40.3537 | 41.8832 | 41.7179 | 41.5242 | 41.2674 | 40.9074 | 40.5632 | 40.1937 | 39.7389 | 39.2926 | 38.4316 | 37.5242 | 36.6642 | 43.2874 | 43.1221 | 42.3063 | 41.8326 | 41.0905 | 40.3653 | 39.9168 | 39.4663 | 39.0232 | 38.18 | 37.2937 | 36.4526
|  | LOVE LANE PRIMARY | HT |  |  |  |  | 45.0705 | 44.8632 | 44.6295 | 44.3368 | 43.9768 | 43.2779 | 42.6074 | 41.8495 | 41.0537 | 39.3442 | 38.2084 | 37.0789 | 41.8926 | 41.74 | 41.5326 | 41.2495 | 40.9053 | 39.8895 | 39.1242 | 38.2789 | 37.4011 | 35.5263 | 34.2747 | 33.02 | 43.2968 | 43.0526 | 42.4095 | 41.6821 | 40.6832 | 39.6284 | 38.8747 | 38.0453 | 37.1832 | 35.3389 | 34.1095 | 32.8768
|  | LOVE LANE PRIMARY | HE |  |  |  |  | 45.1032 | 44.9211 | 44.6853 | 44.4263 | 44.0579 | 43.7179 | 43.4116 | 43.0968 | 42.7895 | 42.7947 | 42.62 | 42.1968 | 41.9158 | 41.7558 | 41.5758 | 41.3284 | 40.9674 | 40.6358 | 40.3316 | 40.0179 | 39.7126 | 39.7232 | 39.3021 | 38.7695 | 43.32 | 43.16 | 42.6979 | 42.2832 | 41.5789 | 40.9063 | 40.5326 | 40.1547 | 39.7884 | 39.5442 | 39.0326 | 38.5137
|  | LOVE LANE PRIMARY | FB |  |  |  |  | 45.2474 | 45.1537 | 45.0737 | 44.9716 | 44.8695 | 44.7653 | 44.6737 | 44.5884 | 44.4979 | 44.1589 | 43.9516 | 43.8053 | 42.0389 | 41.96 | 41.8895 | 41.8105 | 41.7221 | 41.6326 | 41.5463 | 41.4663 | 41.3811 | 41.0611 | 40.8632 | 40.7284 | 43.4432 | 43.3642 | 43.2937 | 43.2147 | 43.1263 | 43.0316 | 42.9189 | 42.7653 | 42.6095 | 41.9705 | 41.3463 | 40.76
COWLEY GSP | YARNTON BSP | LOVELACE ROAD PRIMARY | MINIMUM HEADROOM | SP 50395 10376 | YES | YES | 1.0516 | 12.4095 | 30.3358 | 30.2547 | 29.8084 | 28.3895 | 26.9147 | 25.4263 | 23.9147 | 22.6411 | 20.6305 | 19.7 | 19.3442 | 11.4116 | 28.8495 | 28.1758 | 27.6379 | 25.9905 | 24.2811 | 22.5558 | 20.8021 | 19.3295 | 17.0253 | 15.9695 | 15.5853 | 11.5705 | 29.0095 | 28.3379 | 27.8011 | 26.1589 | 24.4547 | 22.7337 | 20.9853 | 19.5158 | 17.2168 | 16.1642 | 15.78
|  | LOVELACE ROAD PRIMARY | EE |  |  |  |  | 12.4095 | 30.3358 | 30.2558 | 29.9789 | 29.6211 | 28.3916 | 27.1211 | 25.8526 | 24.8084 | 22.3747 | 21.6347 | 21.42 | 11.4189 | 28.9137 | 28.2842 | 27.8358 | 27.4421 | 26.0189 | 24.5453 | 23.0747 | 21.8684 | 19.0221 | 18.1684 | 17.9305 | 11.5779 | 29.0747 | 28.4463 | 27.9989 | 27.6053 | 26.1863 | 24.7158 | 23.2505 | 22.0474 | 19.2095 | 18.3579 | 18.12
|  | LOVELACE ROAD PRIMARY | HT |  |  |  |  | 12.4158 | 30.3453 | 30.2547 | 29.8084 | 28.3895 | 26.9147 | 25.4263 | 23.9147 | 22.6411 | 20.6305 | 19.7 | 19.3442 | 11.4116 | 28.8495 | 28.1758 | 27.6379 | 25.9905 | 24.2811 | 22.5558 | 20.8021 | 19.3295 | 17.0253 | 15.9695 | 15.5853 | 11.5705 | 29.0095 | 28.3379 | 27.8011 | 26.1589 | 24.4547 | 22.7337 | 20.9853 | 19.5158 | 17.2168 | 16.1642 | 15.78
|  | LOVELACE ROAD PRIMARY | HE |  |  |  |  | 12.4305 | 30.3611 | 30.2832 | 30.1695 | 29.8274 | 28.5895 | 27.3116 | 26.0358 | 24.9947 | 22.8863 | 22.2947 | 22.2053 | 11.5337 | 29.0716 | 28.4758 | 28.0558 | 27.68 | 26.2463 | 24.7642 | 23.2863 | 22.0832 | 19.5989 | 18.9084 | 18.8063 | 11.6926 | 29.2316 | 28.6379 | 28.2189 | 27.8442 | 26.4137 | 24.9358 | 23.4611 | 22.2621 | 19.7853 | 19.0968 | 18.9947
|  | LOVELACE ROAD PRIMARY | FB |  |  |  |  | 12.4789 | 30.4411 | 30.4084 | 30.3705 | 30.3295 | 30.2874 | 30.0968 | 29.5221 | 29.0305 | 26.8832 | 26.3189 | 26.1537 | 11.7347 | 29.48 | 29.2179 | 29.0179 | 28.8726 | 28.5495 | 27.9589 | 27.2874 | 26.7158 | 24.2126 | 23.5632 | 23.3779 | 11.8926 | 29.6389 | 29.3779 | 29.1789 | 29.0337 | 28.7116 | 28.1221 | 27.4526 | 26.8821 | 24.3863 | 23.7379 | 23.5537
MANNINGTON GSP | ARNEWOOD BSP | LYMINGTON PRIMARY | MINIMUM HEADROOM | SZ 31720 96856 | NO | YES | 0 | 31.8205 | 31.2879 | 29.9395 | 29.0311 | 28.1121 | 27.0858 | 26.0605 | 25.0732 | 23.4553 | 21.1279 | 19.4205 | 17.9858 | 28.3705 | 27.6989 | 25.8968 | 24.7568 | 23.6326 | 22.3758 | 21.1158 | 19.9095 | 17.7989 | 14.9442 | 12.7926 | 10.9958 | 28.5453 | 27.8863 | 26.1274 | 25.0074 | 23.9032 | 22.6684 | 21.4305 | 20.2453 | 18.18 | 15.3747 | 13.2653 | 11.5021
|  | LYMINGTON PRIMARY | EE |  |  |  |  | 31.8205 | 31.4005 | 30.0353 | 29.3837 | 28.79 | 28.1732 | 27.5195 | 26.9342 | 26.0574 | 24.9942 | 23.8132 | 22.8974 | 28.3705 | 27.8705 | 26.0305 | 25.2484 | 24.6074 | 23.9189 | 23.1621 | 22.5084 | 21.4347 | 20.0484 | 18.48 | 17.2684 | 28.5453 | 28.0516 | 26.2558 | 25.4874 | 24.8505 | 24.1684 | 23.4211 | 22.7747 | 21.7189 | 20.3632 | 18.8305 | 17.6463
|  | LYMINGTON PRIMARY | HT |  |  |  |  | 31.8668 | 31.2879 | 29.9395 | 29.0311 | 28.1121 | 27.0858 | 26.0605 | 25.0732 | 23.4553 | 21.1279 | 19.4205 | 17.9858 | 28.4316 | 27.6989 | 25.8968 | 24.7568 | 23.6326 | 22.3758 | 21.1158 | 19.9095 | 17.7989 | 14.9442 | 12.7926 | 10.9958 | 28.6042 | 27.8863 | 26.1274 | 25.0074 | 23.9032 | 22.6684 | 21.4305 | 20.2453 | 18.18 | 15.3747 | 13.2653 | 11.5021
|  | LYMINGTON PRIMARY | HE |  |  |  |  | 32.0879 | 31.7668 | 30.4858 | 29.9058 | 29.3616 | 28.8121 | 28.25 | 27.7605 | 26.9774 | 26.6668 | 25.9353 | 25.4068 | 28.7242 | 28.3589 | 26.6358 | 25.9505 | 25.3758 | 24.7726 | 24.1474 | 23.6295 | 22.6895 | 22.2326 | 21.2221 | 20.4884 | 28.8905 | 28.5295 | 26.8474 | 26.1726 | 25.6 | 25.0021 | 24.3832 | 23.8674 | 22.9421 | 22.5 | 21.5147 | 20.8
|  | LYMINGTON PRIMARY | FB |  |  |  |  | 32.3384 | 32.1111 | 31.2047 | 30.8911 | 30.6963 | 30.4774 | 30.2479 | 30.0679 | 29.8805 | 29.1016 | 28.2974 | 27.6626 | 29.0147 | 28.7347 | 27.4811 | 27.0789 | 26.8526 | 26.5905 | 26.3137 | 26.1021 | 25.8842 | 24.9526 | 23.9063 | 23.0642 | 29.1768 | 28.9021 | 27.6811 | 27.2874 | 27.0632 | 26.8063 | 26.5326 | 26.3242 | 26.1095 | 25.1926 | 24.1684 | 23.3463
MELKSHAM GSP | CHIPPENHAM BSP | LYNEHAM PRIMARY | MINIMUM HEADROOM | ST 99348 80481 | NO | YES | 0.31579 | 13.7432 | 13.6453 | 31.2458 | 30.8879 | 30.4953 | 30.0395 | 29.7037 | 29.33 | 28.9384 | 27.8858 | 27.03 | 26.2689 | 11.1853 | 10.9463 | 26.8063 | 26.3884 | 25.9347 | 25.4032 | 25.0379 | 24.6253 | 24.1916 | 23.0105 | 22.0358 | 21.1695 | 11.5621 | 11.4747 | 28.48 | 28.3474 | 27.9621 | 27.4263 | 27.0589 | 26.6432 | 26.2063 | 25.0158 | 24.0337 | 23.1589
|  | LYNEHAM PRIMARY | EE |  |  |  |  | 13.7432 | 13.6453 | 31.2458 | 30.9132 | 30.5753 | 30.2226 | 30.0121 | 29.7974 | 29.59 | 29.0721 | 28.4553 | 27.9195 | 11.1853 | 10.9463 | 26.8063 | 26.4179 | 26.0368 | 25.6337 | 25.4053 | 25.1737 | 24.9516 | 24.3558 | 23.6411 | 23.0189 | 11.5621 | 11.4747 | 28.4832 | 28.3579 | 28.0663 | 27.66 | 27.4305 | 27.1968 | 26.9737 | 26.3737 | 25.6516 | 25.0232
|  | LYNEHAM PRIMARY | HT |  |  |  |  | 13.7505 | 13.66 | 31.2711 | 30.8879 | 30.4953 | 30.0395 | 29.7037 | 29.33 | 28.9384 | 27.8858 | 27.03 | 26.2689 | 11.2221 | 11.0011 | 26.84 | 26.3884 | 25.9347 | 25.4032 | 25.0379 | 24.6253 | 24.1916 | 23.0105 | 22.0358 | 21.1695 | 11.5674 | 11.4863 | 28.48 | 28.3474 | 27.9621 | 27.4263 | 27.0589 | 26.6432 | 26.2063 | 25.0158 | 24.0337 | 23.1589
|  | LYNEHAM PRIMARY | HE |  |  |  |  | 13.7768 | 13.6916 | 31.4289 | 31.1258 | 30.8089 | 30.4837 | 30.3068 | 30.13 | 29.9574 | 29.7416 | 29.2984 | 28.9068 | 11.3147 | 11.1274 | 27.0284 | 26.6758 | 26.32 | 25.9474 | 25.7621 | 25.5789 | 25.3989 | 25.1232 | 24.5958 | 24.1347 | 11.5884 | 11.5105 | 28.5242 | 28.4042 | 28.2337 | 27.9768 | 27.7916 | 27.6074 | 27.4274 | 27.1474 | 26.6147 | 26.1474
|  | LYNEHAM PRIMARY | FB |  |  |  |  | 13.8379 | 13.7958 | 31.6047 | 31.5584 | 31.4711 | 31.3353 | 31.2637 | 31.1974 | 31.1279 | 30.7995 | 30.4258 | 30.0984 | 11.4242 | 11.3 | 27.3558 | 27.2 | 27.0611 | 26.9 | 26.8211 | 26.7474 | 26.6695 | 26.2926 | 25.8411 | 25.4463 | 11.6463 | 11.6095 | 28.6768 | 28.6389 | 28.5979 | 28.5558 | 28.5158 | 28.4779 | 28.4368 | 28.2884 | 27.8674 | 27.4684
FLEET-BRAMLEY GSP | BRACKNELL BSP | MVEE PRIMARY | MINIMUM HEADROOM | SU 98120 65945 | NO | YES | 0 | 27.17 | 26.8153 | 26.4005 | 28.0132 | 27.6184 | 27.4068 | 27.1468 | 26.8532 | 26.6437 | 25.9226 | 25.3953 | 24.9911 | 25.3347 | 24.9442 | 24.4884 | 25.9905 | 25.5611 | 25.34 | 25.0684 | 24.7632 | 24.5442 | 23.7853 | 23.2274 | 22.7989 | 26.2168 | 25.82 | 25.3568 | 27.0053 | 26.5684 | 26.3432 | 26.0632 | 25.7484 | 25.5232 | 24.7389 | 24.1642 | 23.7232
|  | MVEE PRIMARY | EE |  |  |  |  | 27.17 | 26.8153 | 26.4005 | 28.0132 | 27.6184 | 27.4068 | 27.1468 | 26.8532 | 26.6437 | 25.9226 | 25.3953 | 24.9911 | 25.3347 | 24.9442 | 24.4884 | 25.9905 | 25.5611 | 25.34 | 25.0684 | 24.7632 | 24.5442 | 23.7853 | 23.2274 | 22.7989 | 26.2168 | 25.82 | 25.3568 | 27.0053 | 26.5684 | 26.3432 | 26.0632 | 25.7484 | 25.5232 | 24.7389 | 24.1642 | 23.7232
|  | MVEE PRIMARY | HT |  |  |  |  | 27.2605 | 26.9332 | 26.5742 | 28.1942 | 27.8553 | 27.7132 | 27.5616 | 27.4132 | 27.2826 | 26.8468 | 26.5142 | 26.2016 | 25.4295 | 25.0674 | 24.6705 | 26.1768 | 25.8 | 25.6463 | 25.4821 | 25.3211 | 25.1789 | 24.7116 | 24.3568 | 24.0242 | 26.3147 | 25.9484 | 25.5453 | 27.2011 | 26.8211 | 26.6663 | 26.5021 | 26.3389 | 26.1968 | 25.7232 | 25.3621 | 25.0211
|  | MVEE PRIMARY | HE |  |  |  |  | 27.4658 | 27.29 | 27.0837 | 28.8911 | 28.6774 | 28.6121 | 28.55 | 28.4868 | 28.4247 | 28.3616 | 28.2932 | 28.2353 | 25.6442 | 25.4411 | 25.2032 | 26.9074 | 26.6653 | 26.5968 | 26.5326 | 26.4663 | 26.4021 | 26.3274 | 26.2474 | 26.18 | 26.5379 | 26.3358 | 26.0979 | 27.9579 | 27.7158 | 27.6484 | 27.5832 | 27.5179 | 27.4526 | 27.3789 | 27.2989 | 27.2326
|  | MVEE PRIMARY | FB |  |  |  |  | 28.0384 | 27.9468 | 27.8553 | 29.8068 | 29.7216 | 29.6974 | 29.6711 | 29.6468 | 29.6216 | 29.5205 | 29.4395 | 29.3774 | 26.3168 | 26.2116 | 26.1042 | 27.9726 | 27.8758 | 27.8484 | 27.82 | 27.7926 | 27.7653 | 27.6547 | 27.5642 | 27.4926 | 27.2084 | 27.1032 | 26.9968 | 29.02 | 28.9232 | 28.8958 | 28.8674 | 28.8411 | 28.8137 | 28.7032 | 28.6126 | 28.5411
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON PRIMARY | MINIMUM HEADROOM | SY 59138 97747 | NO | YES | 0 | 11.3695 | 11.2547 | 11.1347 | 10.9705 | 10.7779 | 10.5684 | 10.3589 | 10.14 | 9.9221 | 6.8747 | 6.5811 | 6.3358 | 9.9811 | 9.8547 | 9.7253 | 9.5474 | 9.3389 | 9.1126 | 8.8874 | 8.6495 | 8.4137 | 4.8232 | 4.4895 | 4.2105 | 10.4874 | 10.3621 | 10.2316 | 10.0547 | 9.8463 | 9.62 | 9.3947 | 9.1568 | 8.92 | 5.3284 | 4.9947 | 4.7147
|  | MAIDEN NEWTON PRIMARY | EE |  |  |  |  | 11.3695 | 11.2547 | 11.1347 | 10.9958 | 10.8263 | 10.6705 | 10.5095 | 10.3453 | 10.1853 | 6.8747 | 6.5811 | 6.3358 | 9.9811 | 9.8547 | 9.7253 | 9.5779 | 9.3989 | 9.2358 | 9.0621 | 8.8874 | 8.7168 | 4.8232 | 4.4895 | 4.2105 | 10.4874 | 10.3621 | 10.2316 | 10.0832 | 9.9053 | 9.7411 | 9.5684 | 9.3937 | 9.2232 | 5.3284 | 4.9947 | 4.7147
|  | MAIDEN NEWTON PRIMARY | HT |  |  |  |  | 11.3874 | 11.2768 | 11.14 | 10.9705 | 10.7779 | 10.5684 | 10.3589 | 10.14 | 9.9221 | 7.7895 | 7.38 | 7.0274 | 10.0011 | 9.88 | 9.7305 | 9.5474 | 9.3389 | 9.1126 | 8.8874 | 8.6495 | 8.4137 | 5.9453 | 5.4905 | 5.1 | 10.5084 | 10.3874 | 10.2379 | 10.0547 | 9.8463 | 9.62 | 9.3947 | 9.1568 | 8.92 | 6.4505 | 5.9958 | 5.6053
|  | MAIDEN NEWTON PRIMARY | HE |  |  |  |  | 11.4432 | 11.3558 | 11.2642 | 11.1484 | 10.9937 | 10.8568 | 10.7253 | 10.5905 | 10.4579 | 7.3632 | 7.1968 | 7.0579 | 10.0642 | 9.9716 | 9.8726 | 9.7505 | 9.5895 | 9.4463 | 9.3095 | 9.1684 | 9.0295 | 5.3758 | 5.1832 | 5.0221 | 10.5716 | 10.4789 | 10.38 | 10.2579 | 10.0968 | 9.9537 | 9.8168 | 9.6747 | 9.5368 | 5.8821 | 5.6884 | 5.5274
|  | MAIDEN NEWTON PRIMARY | FB |  |  |  |  | 11.5095 | 11.4484 | 11.4011 | 11.3474 | 11.2916 | 11.2358 | 11.18 | 11.1253 | 11.0716 | 10.8411 | 10.6421 | 10.4758 | 10.1358 | 10.0684 | 10.0158 | 9.9579 | 9.8968 | 9.8358 | 9.7758 | 9.7158 | 9.6568 | 9.4032 | 9.1789 | 8.9895 | 10.6432 | 10.5758 | 10.5232 | 10.4653 | 10.4042 | 10.3432 | 10.2821 | 10.2221 | 10.1642 | 9.9095 | 9.6853 | 9.4958
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | MAIDENHEAD PRIMARY | MINIMUM HEADROOM | SU 86485 79800 | NO | YES | 0 | 42.8905 | 42.6232 | 61.9084 | 61.4789 | 60.9611 | 58.2621 | 55.2958 | 53.1158 | 51.2737 | 47.0684 | 44.8958 | 42.9347 | 40.5158 | 39.8674 | 55.0705 | 53.6621 | 52.0642 | 49.0358 | 45.6316 | 43.1537 | 41.0768 | 36.3484 | 33.9189 | 31.7221 | 43.9705 | 43.0853 | 59.6916 | 57.4474 | 54.9211 | 51.5084 | 48.1084 | 45.6347 | 43.56 | 38.8421 | 36.4168 | 34.2221
|  | MAIDENHEAD PRIMARY | EE |  |  |  |  | 42.8905 | 42.6232 | 61.9158 | 61.5084 | 60.9621 | 59.2084 | 57.1758 | 55.9895 | 54.8305 | 52.1442 | 50.7042 | 49.4242 | 40.5158 | 39.8674 | 55.0705 | 53.7379 | 52.1642 | 50.1474 | 47.8358 | 46.5253 | 45.2474 | 42.1347 | 40.5053 | 39.0358 | 43.9705 | 43.0853 | 59.6916 | 57.5642 | 55.1063 | 52.6179 | 50.3095 | 49.0011 | 47.7242 | 44.6168 | 42.9926 | 41.5263
|  | MAIDENHEAD PRIMARY | HT |  |  |  |  | 42.9032 | 42.6484 | 61.9084 | 61.4789 | 60.9611 | 58.2621 | 55.2958 | 53.1158 | 51.2737 | 47.0684 | 44.8958 | 42.9347 | 40.5842 | 39.9611 | 55.0779 | 53.6621 | 52.0642 | 49.0358 | 45.6316 | 43.1537 | 41.0768 | 36.3484 | 33.9189 | 31.7221 | 43.9832 | 43.2295 | 59.7116 | 57.4474 | 54.9211 | 51.5084 | 48.1084 | 45.6347 | 43.56 | 38.8421 | 36.4168 | 34.2221
|  | MAIDENHEAD PRIMARY | HE |  |  |  |  | 42.96 | 42.7063 | 62.0095 | 61.6074 | 61.0653 | 60.1653 | 58.2074 | 57.1347 | 56.2 | 53.9926 | 52.9874 | 52.1084 | 40.7663 | 40.2074 | 55.4842 | 54.2116 | 52.7621 | 51.2316 | 49.0337 | 47.8568 | 46.8421 | 44.2295 | 43.0558 | 42.0263 | 44.04 | 43.6105 | 60.38 | 58.3589 | 56.1295 | 53.7253 | 51.5053 | 50.3295 | 49.3158 | 46.7084 | 45.5368 | 44.5095
|  | MAIDENHEAD PRIMARY | FB |  |  |  |  | 43.1505 | 43.0274 | 62.5158 | 62.3905 | 62.2516 | 62.1116 | 61.9747 | 61.8484 | 61.7137 | 61.2158 | 59.8453 | 58.9705 | 41.0853 | 40.7663 | 56.4368 | 55.9137 | 55.3389 | 54.7211 | 54.1095 | 53.8758 | 53.5621 | 52.1421 | 50.8074 | 49.8042 | 44.2305 | 44.1074 | 61.6558 | 60.8453 | 59.9011 | 58.8726 | 57.8537 | 57.5274 | 57.0611 | 54.8463 | 53.2768 | 52.2768
MELKSHAM GSP | CHIPPENHAM BSP | MALMESBURY PRIMARY | MINIMUM HEADROOM | ST 92288 87493 | NO | YES | 0.063158 | 9.2284 | 8.9474 | 8.7105 | 8.4516 | 7.9937 | 7.4779 | 6.9684 | 4.1853 | 1.5221 | 0.25158 | -0.78105 | -1.7105 | 12.9368 | 12.6168 | 12.3547 | 12.0768 | 11.5663 | 10.9958 | 10.4263 | 7.1168 | 3.9505 | 2.5189 | 1.3358 | 0.26842 | 13.32 | 13 | 12.7379 | 12.4589 | 11.9495 | 11.3832 | 10.8137 | 7.5032 | 4.3347 | 2.9021 | 1.7189 | 0.65158
|  | MALMESBURY PRIMARY | EE |  |  |  |  | 9.2284 | 8.9474 | 8.7105 | 8.4789 | 8.0832 | 7.6653 | 7.2926 | 5.8726 | 4.5147 | 1.7211 | 0.97789 | 0.34 | 12.9368 | 12.6168 | 12.3547 | 12.1074 | 11.6747 | 11.2126 | 10.8021 | 9.1368 | 7.5379 | 4.2011 | 3.3326 | 2.5842 | 13.32 | 13 | 12.7379 | 12.4895 | 12.0568 | 11.5947 | 11.1842 | 9.5232 | 7.9242 | 4.5853 | 3.7168 | 2.9674
|  | MALMESBURY PRIMARY | HT |  |  |  |  | 9.2684 | 9.0074 | 8.7453 | 8.4516 | 7.9937 | 7.4779 | 6.9684 | 4.1853 | 1.5221 | 0.25158 | -0.78105 | -1.7105 | 12.9853 | 12.6863 | 12.3968 | 12.0768 | 11.5663 | 10.9958 | 10.4263 | 7.1168 | 3.9505 | 2.5189 | 1.3358 | 0.26842 | 13.3684 | 13.0695 | 12.78 | 12.4589 | 11.9495 | 11.3832 | 10.8137 | 7.5032 | 4.3347 | 2.9021 | 1.7189 | 0.65158
|  | MALMESBURY PRIMARY | HE |  |  |  |  | 9.3589 | 9.1316 | 8.9432 | 8.7442 | 8.3726 | 7.9874 | 7.6589 | 6.2863 | 4.9737 | 2.5495 | 2.0042 | 1.5516 | 13.0947 | 12.8337 | 12.6253 | 12.4179 | 12.0137 | 11.5884 | 11.2305 | 9.6232 | 8.0789 | 5.1547 | 4.4989 | 3.9589 | 13.4779 | 13.2168 | 13.0084 | 12.8011 | 12.3968 | 11.9716 | 11.6137 | 10.0095 | 8.4642 | 5.54 | 4.8789 | 4.3389
|  | MALMESBURY PRIMARY | FB |  |  |  |  | 9.5526 | 9.4084 | 9.3105 | 9.2232 | 9.0884 | 8.9263 | 8.7842 | 8.6968 | 8.6084 | 8.1832 | 7.7011 | 7.28 | 13.3189 | 13.1495 | 13.0379 | 12.94 | 12.7832 | 12.5979 | 12.4379 | 12.3421 | 12.2463 | 11.7726 | 11.2126 | 10.7189 | 13.6989 | 13.5316 | 13.4211 | 13.3232 | 13.1663 | 12.9811 | 12.8211 | 12.7253 | 12.6284 | 12.1547 | 11.5947 | 11.1011
MINETY GSP | SWINDON BSP | MANCHESTER ROAD PRIMARY | MINIMUM HEADROOM | SU 15254 85130 | NO | YES | 0.13158 | 43.2895 | 42.6621 | 41.5947 | 40.2326 | 38.2789 | 36.2232 | 34.0537 | 32.2558 | 30.4568 | 25.3726 | 22.6137 | 20.5242 | 47.9611 | 47.3421 | 46.2937 | 44.9547 | 43.0347 | 41.0147 | 38.8821 | 37.1147 | 35.3453 | 30.3495 | 27.6358 | 25.5789 | 50.7526 | 50.5863 | 50.3989 | 50.0916 | 47.9474 | 45.5884 | 43.0926 | 41.0368 | 38.9789 | 33.14 | 29.9884 | 27.6158
|  | MANCHESTER ROAD PRIMARY | EE |  |  |  |  | 43.2895 | 42.6621 | 41.5947 | 40.2326 | 38.3811 | 36.4168 | 34.2411 | 32.4789 | 30.7274 | 25.9358 | 23.7295 | 22.2 | 47.9611 | 47.3421 | 46.2937 | 44.9547 | 43.1347 | 41.2053 | 39.0684 | 37.3358 | 35.6147 | 30.9147 | 28.7484 | 27.2463 | 50.7526 | 50.5863 | 50.3989 | 50.0916 | 48.0663 | 45.8063 | 43.2937 | 41.2716 | 39.2611 | 33.6768 | 31.1305 | 29.3705
|  | MANCHESTER ROAD PRIMARY | HT |  |  |  |  | 43.3726 | 42.7758 | 41.7032 | 40.3221 | 38.2789 | 36.2232 | 34.0537 | 32.2558 | 30.4568 | 25.3726 | 22.6137 | 20.5242 | 48.0432 | 47.4547 | 46.4 | 45.0421 | 43.0347 | 41.0147 | 38.8821 | 37.1147 | 35.3453 | 30.3495 | 27.6358 | 25.5789 | 50.7789 | 50.6221 | 50.4116 | 50.14 | 47.9474 | 45.5884 | 43.0926 | 41.0368 | 38.9789 | 33.14 | 29.9884 | 27.6158
|  | MANCHESTER ROAD PRIMARY | HE |  |  |  |  | 43.5368 | 42.9979 | 41.9968 | 40.6842 | 38.8547 | 36.9232 | 34.8347 | 33.1674 | 31.5116 | 27.5063 | 25.7747 | 24.6632 | 48.2032 | 47.6726 | 46.6884 | 45.3979 | 43.6 | 41.7011 | 39.6505 | 38.0116 | 36.3832 | 32.4589 | 30.7611 | 29.6695 | 50.8158 | 50.6611 | 50.4716 | 50.2211 | 48.6116 | 46.3958 | 43.9895 | 42.0811 | 40.1842 | 35.48 | 33.4621 | 32.1653
|  | MANCHESTER ROAD PRIMARY | FB |  |  |  |  | 44.2758 | 43.9253 | 43.4463 | 42.8663 | 42.1642 | 41.3421 | 40.36 | 39.5168 | 38.62 | 35.46 | 34.0663 | 33.0947 | 48.9295 | 48.5842 | 48.1137 | 47.5432 | 46.8537 | 46.0463 | 45.0821 | 44.2547 | 43.3747 | 40.2726 | 38.9032 | 37.9484 | 50.9105 | 50.8105 | 50.7211 | 50.6211 | 50.5095 | 50.3979 | 50.22 | 49.3074 | 48.3032 | 44.6463 | 43.0411 | 41.9221
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON PRIMARY | MINIMUM HEADROOM | SU 07592 05256 | NO | YES | 0 | 15.8108 | 15.6624 | 15.4845 | 15.2403 | 14.9487 | 14.6318 | 14.3182 | 13.9971 | 13.6761 | 12.8603 | 12.2129 | 11.6382 | 13.9479 | 13.7595 | 13.5321 | 13.2163 | 12.8416 | 12.4342 | 12.03 | 11.6111 | 11.1921 | 10.1037 | 9.3742 | 8.7342 | 13.9411 | 13.8358 | 13.7074 | 13.5347 | 13.3284 | 13.1032 | 12.6979 | 12.28 | 11.86 | 10.7716 | 10.0421 | 9.4021
|  | MANNINGTON PRIMARY | EE |  |  |  |  | 15.8108 | 15.6624 | 15.5066 | 15.3182 | 15.0866 | 14.8687 | 14.6518 | 14.4318 | 14.2192 | 13.8097 | 13.4561 | 13.1571 | 13.9479 | 13.7595 | 13.5616 | 13.3321 | 13.0595 | 12.8037 | 12.5395 | 12.2732 | 12.0174 | 11.41 | 10.8911 | 10.4458 | 13.9411 | 13.8358 | 13.7211 | 13.5747 | 13.3842 | 13.2053 | 13.0368 | 12.8621 | 12.6842 | 12.0779 | 11.5589 | 11.1137
|  | MANNINGTON PRIMARY | HT |  |  |  |  | 15.8266 | 15.6761 | 15.4845 | 15.2403 | 14.9487 | 14.6318 | 14.3182 | 13.9971 | 13.6761 | 12.8603 | 12.2129 | 11.6382 | 13.9732 | 13.7784 | 13.5321 | 13.2163 | 12.8416 | 12.4342 | 12.03 | 11.6111 | 11.1921 | 10.1037 | 9.3742 | 8.7342 | 13.9484 | 13.8421 | 13.7074 | 13.5347 | 13.3284 | 13.1032 | 12.6979 | 12.28 | 11.86 | 10.7716 | 10.0421 | 9.4021
|  | MANNINGTON PRIMARY | HE |  |  |  |  | 15.8939 | 15.7813 | 15.655 | 15.4939 | 15.2813 | 15.0908 | 14.9024 | 14.7139 | 14.5297 | 14.3529 | 14.1371 | 13.9529 | 14.07 | 13.9332 | 13.7774 | 13.5868 | 13.3416 | 13.1205 | 12.9026 | 12.6847 | 12.4742 | 12.1742 | 11.8384 | 11.5458 | 13.9863 | 13.8989 | 13.8 | 13.6705 | 13.4905 | 13.3305 | 13.1726 | 13.0137 | 12.8579 | 12.8042 | 12.5074 | 12.2147
|  | MANNINGTON PRIMARY | FB |  |  |  |  | 15.9845 | 15.9108 | 15.8508 | 15.7845 | 15.7139 | 15.6424 | 15.5708 | 15.5024 | 15.4318 | 15.1382 | 14.895 | 14.6876 | 14.1795 | 14.0805 | 14.0016 | 13.9163 | 13.8247 | 13.7332 | 13.6395 | 13.55 | 13.4584 | 13.0658 | 12.7174 | 12.4111 | 14.0568 | 14.0095 | 13.9674 | 13.9211 | 13.8716 | 13.8211 | 13.7716 | 13.7242 | 13.6747 | 13.4821 | 13.3463 | 13.0789
LOVEDEAN GSP | CHICHESTER BSP | MARKET PRIMARY | MINIMUM HEADROOM | SU 86479 04732 | NO | YES | 0 | 30.9526 | 30.8147 | 30.6568 | 30.4337 | 30.1663 | 29.8726 | 29.5684 | 28.7347 | 27.9432 | 25.7358 | 24.1663 | 22.6895 | 26.8326 | 26.7105 | 26.5747 | 26.3905 | 26.1389 | 25.8968 | 25.6526 | 24.7358 | 23.8116 | 21.2084 | 19.3768 | 17.7116 | 28.5842 | 28.4484 | 28.2947 | 28.0211 | 27.4074 | 26.7516 | 25.9937 | 25.1779 | 24.4053 | 21.9 | 20.0695 | 18.4074
|  | MARKET PRIMARY | EE |  |  |  |  | 30.9526 | 30.8147 | 30.6621 | 30.4695 | 30.2095 | 29.9611 | 29.7095 | 29.4526 | 29.2053 | 28.7811 | 27.6347 | 26.6295 | 26.8326 | 26.7105 | 26.5747 | 26.3916 | 26.1389 | 25.8968 | 25.6695 | 25.4337 | 25.2011 | 24.8926 | 23.5053 | 22.2863 | 28.5842 | 28.4484 | 28.2989 | 28.1074 | 27.8495 | 27.6 | 27.2663 | 26.8221 | 26.4347 | 25.2074 | 24.0947 | 22.9758
|  | MARKET PRIMARY | HT |  |  |  |  | 30.9642 | 30.8305 | 30.6568 | 30.4337 | 30.1663 | 29.8726 | 29.5684 | 28.7347 | 27.9432 | 25.7358 | 24.1663 | 22.6895 | 26.8411 | 26.7284 | 26.5821 | 26.3905 | 26.1611 | 25.9074 | 25.6526 | 24.7358 | 23.8116 | 21.2084 | 19.3768 | 17.7116 | 28.5958 | 28.4653 | 28.2947 | 28.0211 | 27.4074 | 26.7516 | 25.9937 | 25.1779 | 24.4053 | 21.9 | 20.0695 | 18.4074
|  | MARKET PRIMARY | HE |  |  |  |  | 30.9821 | 30.8484 | 30.6979 | 30.5032 | 30.2368 | 29.9916 | 29.7379 | 29.4853 | 29.2411 | 29.1884 | 29.0684 | 28.3958 | 26.8505 | 26.7284 | 26.5905 | 26.4011 | 26.14 | 25.8989 | 25.6611 | 25.4211 | 25.1842 | 25.1968 | 25.1484 | 24.3842 | 28.6126 | 28.48 | 28.3316 | 28.1379 | 27.8726 | 27.6274 | 27.3758 | 27.1253 | 26.8821 | 26.3074 | 25.5295 | 24.8411
|  | MARKET PRIMARY | FB |  |  |  |  | 31.0779 | 31.0032 | 30.9358 | 30.8653 | 30.7874 | 30.7074 | 30.6242 | 30.5484 | 30.4716 | 30.1611 | 29.9568 | 29.8084 | 26.9368 | 26.8716 | 26.8116 | 26.7453 | 26.6716 | 26.5968 | 26.5242 | 26.4568 | 26.3853 | 26.1211 | 25.9716 | 25.8758 | 28.7074 | 28.6337 | 28.5674 | 28.4968 | 28.42 | 28.3411 | 28.2589 | 28.1853 | 28.1084 | 27.7242 | 27.0158 | 26.38
MELKSHAM GSP | WEST GRAFTON BSP | MARLBOROUGH SOUTH PRIMARY | MINIMUM HEADROOM | SU 19293 68264 | NO | YES | 0 | 18.5318 | 18.4045 | 18.2666 | 18.0687 | 17.8213 | 17.5676 | 17.3066 | 16.8434 | 16.2624 | 14.6476 | 13.335 | 12.1718 | 15.7753 | 15.5132 | 15.2521 | 14.8647 | 14.3153 | 13.8132 | 13.2879 | 12.6826 | 12.0437 | 10.2468 | 8.7658 | 7.4532 | 12.0284 | 11.7716 | 11.5147 | 11.1358 | 10.5958 | 10.1032 | 9.5884 | 8.9968 | 8.3726 | 6.6232 | 5.1853 | 3.9105
|  | MARLBOROUGH SOUTH PRIMARY | EE |  |  |  |  | 18.5318 | 18.4045 | 18.2666 | 18.0813 | 17.8213 | 17.5803 | 17.3603 | 17.1329 | 16.9087 | 16.2224 | 15.2476 | 14.4118 | 15.7753 | 15.5132 | 15.2521 | 14.8921 | 14.4289 | 14.0932 | 13.7258 | 13.3563 | 12.9932 | 12.0068 | 10.8911 | 9.93 | 12.0284 | 11.7716 | 11.5147 | 11.1611 | 10.7063 | 10.3737 | 10.0126 | 9.6484 | 9.2905 | 8.3358 | 7.2547 | 6.3274
|  | MARLBOROUGH SOUTH PRIMARY | HT |  |  |  |  | 18.5413 | 18.4234 | 18.2666 | 18.0687 | 17.8297 | 17.5676 | 17.3066 | 16.8434 | 16.2624 | 14.6476 | 13.335 | 12.1718 | 15.8321 | 15.5974 | 15.3079 | 14.8647 | 14.3153 | 13.8132 | 13.2879 | 12.6826 | 12.0437 | 10.2468 | 8.7658 | 7.4532 | 12.0832 | 11.8537 | 11.5684 | 11.1358 | 10.5958 | 10.1032 | 9.5884 | 8.9968 | 8.3726 | 6.6232 | 5.1853 | 3.9105
|  | MARLBOROUGH SOUTH PRIMARY | HE |  |  |  |  | 18.5708 | 18.4529 | 18.3213 | 18.1403 | 17.8813 | 17.6518 | 17.4297 | 17.2034 | 16.9803 | 16.9897 | 16.7139 | 16.1413 | 15.9679 | 15.7795 | 15.5795 | 15.2689 | 14.8384 | 14.5479 | 14.2711 | 13.9911 | 13.7174 | 13.3279 | 12.55 | 11.8826 | 12.2147 | 12.0295 | 11.8316 | 11.5263 | 11.1021 | 10.8137 | 10.5389 | 10.2621 | 9.9895 | 9.6158 | 8.8663 | 8.2221
|  | MARLBOROUGH SOUTH PRIMARY | FB |  |  |  |  | 18.6561 | 18.5982 | 18.5466 | 18.4887 | 18.4245 | 18.3592 | 18.2961 | 18.2382 | 18.175 | 17.9445 | 17.8171 | 17.3592 | 16.1205 | 15.9732 | 15.8626 | 15.7184 | 15.5532 | 15.4237 | 15.3037 | 15.1889 | 15.07 | 14.5037 | 13.7963 | 13.1689 | 12.3653 | 12.2211 | 12.1137 | 11.9726 | 11.8105 | 11.6842 | 11.5653 | 11.4526 | 11.3368 | 10.7832 | 10.0979 | 9.4916
NURSLING GSP | ROWNHAMS BSP | MAYBUSH PRIMARY | MINIMUM HEADROOM | SU 38426 14930 | NO | YES | 0 | 25.7179 | 25.3253 | 24.8958 | 24.2558 | 23.8474 | 23.2726 | 22.6853 | 22.2495 | 21.1621 | 21.3032 | 19.8347 | 18.5368 | 21.9253 | 21.5011 | 21.0305 | 20.3347 | 19.9337 | 19.3253 | 18.7 | 18.4232 | 17.0421 | 18.5326 | 16.9105 | 15.4789 | 24.0232 | 23.6053 | 23.1442 | 22.4611 | 22.0537 | 21.4526 | 20.8358 | 20.4 | 19.2074 | 20.9842 | 19.4 | 18
|  | MAYBUSH PRIMARY | EE |  |  |  |  | 25.7179 | 25.3253 | 24.9095 | 24.4389 | 23.8474 | 23.2726 | 22.6853 | 22.5116 | 21.1621 | 23.2189 | 22.12 | 21.2105 | 21.9253 | 21.5011 | 21.0547 | 20.5558 | 19.9337 | 19.3253 | 18.7 | 18.8579 | 17.0421 | 20.6958 | 19.4632 | 18.4411 | 24.0232 | 23.6053 | 23.1632 | 22.6695 | 22.0537 | 21.4526 | 20.8358 | 21.1263 | 19.2074 | 23.0695 | 21.8663 | 20.8695
|  | MAYBUSH PRIMARY | HT |  |  |  |  | 25.7874 | 25.4032 | 24.8958 | 24.2558 | 24.8842 | 24.0853 | 23.2253 | 22.2495 | 23.4832 | 21.3032 | 19.8347 | 18.5368 | 22.0021 | 21.5853 | 21.0305 | 20.3347 | 21.3147 | 20.4453 | 19.5032 | 18.4232 | 20.9326 | 18.5326 | 16.9105 | 15.4789 | 24.1 | 23.6895 | 23.1442 | 22.4611 | 23.2274 | 22.3758 | 21.4537 | 20.4 | 23.3305 | 20.9842 | 19.4 | 18
|  | MAYBUSH PRIMARY | HE |  |  |  |  | 26.0011 | 25.7263 | 25.4242 | 25.0463 | 24.5211 | 24.0221 | 23.5189 | 22.9337 | 22.3632 | 25.0147 | 24.4484 | 23.9368 | 22.2453 | 21.9558 | 21.6358 | 21.2411 | 20.6947 | 20.1716 | 19.6421 | 19.0158 | 18.4063 | 22.6895 | 22.0368 | 21.4463 | 24.3368 | 24.0505 | 23.7358 | 23.3453 | 22.8032 | 22.2863 | 21.7642 | 21.1484 | 20.5484 | 24.9011 | 24.4084 | 23.8379
|  | MAYBUSH PRIMARY | FB |  |  |  |  | 26.3011 | 26.0884 | 25.9189 | 25.7442 | 25.5432 | 25.34 | 25.1263 | 24.9211 | 24.6537 | 23.5284 | 24.2779 | 23.6884 | 22.5758 | 22.3432 | 22.1589 | 21.9716 | 21.7537 | 21.5337 | 21.3021 | 21.0779 | 20.7832 | 19.5274 | 20.6263 | 19.9568 | 24.6589 | 24.4316 | 24.2516 | 24.0663 | 23.8537 | 23.6379 | 23.4105 | 23.1916 | 22.9032 | 21.6811 | 22.5674 | 21.9189
MELKSHAM GSP | NORRINGTON BSP | MELKSHAM TOWN PRIMARY | MINIMUM HEADROOM | ST 90170 64096 | NO | YES | 0 | 41.7716 | 41.6495 | 41.5389 | 41.4147 | 41.2779 | 44.2642 | 42.7653 | 41.3863 | 40.0695 | 36.7221 | 35.9768 | 33.4368 | 30.9684 | 30.5263 | 30.0274 | 29.4568 | 28.7705 | 32.0726 | 30.4053 | 28.8779 | 27.4221 | 23.4811 | 23.9726 | 21.1053 | 35.2421 | 34.8463 | 34.4042 | 33.8979 | 33.2916 | 36.0305 | 34.5211 | 33.1337 | 31.8084 | 28.4253 | 29.1789 | 26.6295
|  | MELKSHAM TOWN PRIMARY | EE |  |  |  |  | 50.2358 | 49.9579 | 49.3063 | 47.8884 | 46.3568 | 44.88 | 43.7621 | 42.8842 | 40.3147 | 36.7221 | 36.8863 | 35.1053 | 39.7621 | 38.9242 | 37.7516 | 36.1495 | 34.4411 | 32.7926 | 31.5589 | 30.6116 | 27.6611 | 23.4811 | 24.76 | 22.7105 | 42.92 | 42.1589 | 41.1095 | 39.6811 | 38.1379 | 36.6516 | 35.5274 | 34.6453 | 32.0526 | 28.4253 | 30.0842 | 28.2937
|  | MELKSHAM TOWN PRIMARY | HT |  |  |  |  | 50.2537 | 49.9905 | 49.3989 | 47.7989 | 46.0874 | 44.2642 | 42.7653 | 41.3863 | 40.0695 | 38.8179 | 35.9768 | 33.4368 | 39.8853 | 39.0989 | 37.8621 | 36.0516 | 34.1242 | 32.0726 | 30.4053 | 28.8779 | 27.4221 | 27.1779 | 23.9726 | 21.1053 | 43.0284 | 42.3158 | 41.2021 | 39.5916 | 37.8674 | 36.0305 | 34.5211 | 33.1337 | 31.8084 | 32.0326 | 29.1789 | 26.6295
|  | MELKSHAM TOWN PRIMARY | HE |  |  |  |  | 50.3211 | 50.0632 | 49.7789 | 48.6147 | 47.1484 | 45.7663 | 44.7758 | 44.0263 | 41.5853 | 38.9884 | 39.7095 | 38.4274 | 40.1789 | 39.5032 | 38.4695 | 36.9832 | 35.3516 | 33.8084 | 32.7263 | 31.9295 | 29.1316 | 26.0547 | 27.9168 | 26.4211 | 43.2947 | 42.6737 | 41.7442 | 40.4137 | 38.9379 | 37.5463 | 36.5505 | 35.7979 | 33.3358 | 30.7105 | 32.8916 | 31.6032
|  | MELKSHAM TOWN PRIMARY | FB |  |  |  |  | 41.7716 | 41.6495 | 41.5389 | 41.4147 | 41.2779 | 49.2979 | 48.8505 | 48.5347 | 48.2811 | 47.1526 | 45.8379 | 44.6884 | 30.9684 | 30.5263 | 30.0274 | 29.4568 | 28.7705 | 37.7 | 37.1958 | 36.8453 | 36.5705 | 35.3253 | 33.82 | 32.4937 | 35.2421 | 34.8463 | 34.4042 | 33.8979 | 33.2916 | 41.0989 | 40.6484 | 40.3305 | 40.0758 | 38.94 | 37.6137 | 36.4547
NURSLING GSP |  | MARCHWOOD PRIMARY | MINIMUM HEADROOM | SU 39234 11008 | NO | YES | 0 | -0.63474 | -0.82526 | -1.0568 | -1.2968 | -1.6084 | -1.9368 | -2.1768 | -4.0758 | -4.2979 | -4.7558 | -5.1 | -5.3884 | -1.5926 | -1.8337 | -2.1263 | -2.4253 | -2.8063 | -3.2042 | -3.4874 | -5.8916 | -6.1537 | -6.6884 | -7.0979 | -7.4379 | -1.3568 | -1.4095 | -1.7084 | -2.0168 | -2.4 | -2.7947 | -3.0758 | -5.4579 | -5.7189 | -6.2495 | -6.6558 | -6.9937
|  | MARCHWOOD PRIMARY | EE |  |  |  |  | -0.63474 | -0.70421 | -0.95579 | -1.2358 | -1.4442 | -1.6558 | -1.7811 | -2.7232 | -2.8211 | -3.0042 | -3.2463 | -3.4326 | -1.5926 | -1.6716 | -1.9926 | -2.3463 | -2.5958 | -2.8442 | -2.9853 | -4.1695 | -4.2747 | -4.4947 | -4.7895 | -5.0168 | -1.3568 | -1.4 | -1.5705 | -1.9347 | -2.1905 | -2.4379 | -2.5789 | -3.7516 | -3.8568 | -4.0758 | -4.3674 | -4.5937
|  | MARCHWOOD PRIMARY | HT |  |  |  |  | -0.62842 | -0.82526 | -1.0568 | -1.2968 | -1.6084 | -1.9368 | -2.1768 | -4.0758 | -4.2979 | -4.7558 | -5.1 | -5.3884 | -1.5842 | -1.8337 | -2.1263 | -2.4253 | -2.8063 | -3.2042 | -3.4874 | -5.8916 | -6.1537 | -6.6884 | -7.0979 | -7.4379 | -1.3537 | -1.4095 | -1.7084 | -2.0168 | -2.4 | -2.7947 | -3.0758 | -5.4579 | -5.7189 | -6.2495 | -6.6558 | -6.9937
|  | MARCHWOOD PRIMARY | HE |  |  |  |  | -0.58947 | -0.64316 | -0.88105 | -1.1484 | -1.3474 | -1.5411 | -1.6537 | -2.5832 | -2.6653 | -2.7326 | -2.8989 | -3.02 | -1.5358 | -1.5937 | -1.8968 | -2.2347 | -2.4726 | -2.7042 | -2.8284 | -3.9968 | -4.0821 | -4.1695 | -4.3789 | -4.5316 | -1.3432 | -1.3821 | -1.4716 | -1.82 | -2.0632 | -2.2989 | -2.4232 | -3.5811 | -3.6663 | -3.7526 | -3.96 | -4.1105
|  | MARCHWOOD PRIMARY | FB |  |  |  |  | -0.54737 | -0.58632 | -0.63158 | -0.76105 | -0.88105 | -0.96105 | -1.0074 | -1.04 | -1.0726 | -1.2126 | -1.3642 | -1.48 | -1.4884 | -1.5337 | -1.5884 | -1.7547 | -1.9074 | -2.0074 | -2.0632 | -2.0989 | -2.1368 | -2.2979 | -2.4863 | -2.6316 | -1.3147 | -1.3358 | -1.3547 | -1.3863 | -1.4842 | -1.5863 | -1.6432 | -1.68 | -1.7179 | -1.8832 | -2.0768 | -2.2263
LOVEDEAN GSP | HAVANT BSP | MEYRICK ROAD PRIMARY | MINIMUM HEADROOM | SU 70849 06469 | NO | YES | 0 | 27.9453 | 27.2305 | 26.4295 | 25.4789 | 24.4411 | 23.3263 | 22.2168 | 21.0547 | 19.8684 | 16.7 | 13.9442 | 11.5432 | 23.7021 | 23.3874 | 23.0168 | 22.5358 | 21.9726 | 20.8116 | 19.5979 | 18.3211 | 17.0147 | 13.4989 | 10.3895 | 7.6789 | 27.4105 | 27.1579 | 26.2779 | 25.2305 | 24.0958 | 22.8779 | 21.6663 | 20.3905 | 19.0853 | 15.5737 | 12.4684 | 9.7621
|  | MEYRICK ROAD PRIMARY | EE |  |  |  |  | 27.9453 | 27.2779 | 26.4547 | 25.7726 | 25.0168 | 24.3495 | 23.6874 | 23 | 22.2895 | 20.7695 | 18.7747 | 17.1253 | 23.7021 | 23.3874 | 23.0221 | 22.5958 | 22.04 | 21.5179 | 21.0295 | 20.5242 | 19.8358 | 18.1084 | 15.8158 | 13.9179 | 27.4105 | 27.1579 | 26.3074 | 25.5705 | 24.7747 | 24.0768 | 23.3811 | 22.6537 | 21.9011 | 20.1768 | 17.8874 | 15.9926
|  | MEYRICK ROAD PRIMARY | HT |  |  |  |  | 28.04 | 27.2305 | 26.4295 | 25.4789 | 24.4411 | 23.3263 | 22.2168 | 21.0547 | 19.8684 | 16.7 | 13.9442 | 11.5432 | 23.7274 | 23.4032 | 23.0168 | 22.5358 | 21.9726 | 20.8116 | 19.5979 | 18.3211 | 17.0147 | 13.4989 | 10.3895 | 7.6789 | 27.4232 | 27.1632 | 26.2779 | 25.2305 | 24.0958 | 22.8779 | 21.6663 | 20.3905 | 19.0853 | 15.5737 | 12.4684 | 9.7621
|  | MEYRICK ROAD PRIMARY | HE |  |  |  |  | 28.2695 | 27.7295 | 27.0211 | 26.4284 | 25.7389 | 25.1568 | 24.5926 | 24.0063 | 23.3947 | 22.7305 | 21.3168 | 20.1168 | 23.7989 | 23.5158 | 23.1832 | 22.78 | 22.2442 | 21.7589 | 21.2853 | 20.8 | 20.3179 | 20.2558 | 18.6705 | 17.2642 | 27.4663 | 27.2284 | 26.9558 | 26.3242 | 25.6042 | 25.0021 | 24.42 | 23.8126 | 23.1737 | 22.3863 | 20.7389 | 19.3358
|  | MEYRICK ROAD PRIMARY | FB |  |  |  |  | 28.6211 | 28.2653 | 27.9958 | 27.6642 | 27.4074 | 27.1695 | 26.9389 | 26.7179 | 26.4684 | 25.4147 | 24.1463 | 23.0705 | 24.0074 | 23.8526 | 23.7211 | 23.5695 | 23.4179 | 23.2684 | 23.1232 | 22.9874 | 22.84 | 22.2768 | 21.6979 | 20.4611 | 27.6495 | 27.5305 | 27.4232 | 27.3042 | 27.1716 | 27.0379 | 26.8695 | 26.6316 | 26.3611 | 25.2074 | 23.7632 | 22.5295
MELKSHAM GSP | ANDOVER BSP | MIDDLE WALLOP PRIMARY | MINIMUM HEADROOM | SU 30984 40155 | YES | YES | 0 | 14.7737 | 14.7021 | 14.6295 | 14.5432 | 14.4411 | 14.3474 | 14.2442 | 14.1379 | 12.3295 | 8.9305 | 8.7158 | 8.46 | 14.6032 | 14.5242 | 14.4474 | 14.3547 | 14.2484 | 14.1505 | 14.0442 | 13.9326 | 11.8147 | 7.8116 | 7.5674 | 7.3211 | 14.6295 | 14.5516 | 14.4737 | 14.3811 | 14.2747 | 14.1768 | 14.0705 | 13.96 | 11.8484 | 7.8568 | 7.6137 | 7.3663
|  | MIDDLE WALLOP PRIMARY | EE |  |  |  |  | 14.7737 | 14.7021 | 14.6295 | 14.5432 | 14.4411 | 14.3474 | 14.2537 | 14.1579 | 13.2105 | 8.9305 | 8.7158 | 8.5011 | 14.6032 | 14.5242 | 14.4474 | 14.3547 | 14.2484 | 14.1505 | 14.0516 | 13.9505 | 12.8463 | 7.8116 | 7.5674 | 7.3211 | 14.6295 | 14.5516 | 14.4737 | 14.3811 | 14.2747 | 14.1768 | 14.0779 | 13.9768 | 12.8768 | 7.8568 | 7.6137 | 7.3674
|  | MIDDLE WALLOP PRIMARY | HT |  |  |  |  | 14.7884 | 14.7232 | 14.6474 | 14.5579 | 14.4621 | 14.3516 | 14.2442 | 14.1379 | 12.3295 | 9.0989 | 8.78 | 8.46 | 14.62 | 14.5495 | 14.4684 | 14.3737 | 14.2737 | 14.1568 | 14.0442 | 13.9326 | 11.8147 | 8.04 | 7.6832 | 7.3211 | 14.6453 | 14.5758 | 14.4958 | 14.4011 | 14.3 | 14.1842 | 14.0705 | 13.96 | 11.8484 | 8.0842 | 7.7274 | 7.3663
|  | MIDDLE WALLOP PRIMARY | HE |  |  |  |  | 14.8253 | 14.7747 | 14.7179 | 14.6463 | 14.5526 | 14.4716 | 14.3937 | 14.3126 | 13.3832 | 9.2211 | 9.0811 | 8.9284 | 14.6611 | 14.6074 | 14.5474 | 14.4726 | 14.3758 | 14.2905 | 14.2105 | 14.1274 | 13.0432 | 8.14 | 7.9768 | 7.7989 | 14.6874 | 14.6337 | 14.5737 | 14.4989 | 14.4021 | 14.3179 | 14.2368 | 14.1547 | 13.0726 | 8.1842 | 8.0221 | 7.8442
|  | MIDDLE WALLOP PRIMARY | FB |  |  |  |  | 14.8663 | 14.8284 | 14.8 | 14.7674 | 14.7337 | 14.7011 | 14.6684 | 14.6379 | 14.6053 | 14.4737 | 14.3326 | 14.1947 | 14.7053 | 14.6632 | 14.6316 | 14.5968 | 14.5611 | 14.5253 | 14.4905 | 14.4568 | 14.4221 | 14.2779 | 14.1179 | 13.9589 | 14.7316 | 14.6895 | 14.6579 | 14.6232 | 14.5874 | 14.5516 | 14.5168 | 14.4832 | 14.4484 | 14.3042 | 14.1442 | 13.9874
FLEET-BRAMLEY GSP | FERNHURST BSP | MIDHURST PRIMARY | MINIMUM HEADROOM | SU 88127 19555 | NO | YES | 2.1053 | 31.9837 | 31.7795 | 31.5479 | 31.2774 | 30.9521 | 30.4542 | 29.8605 | 29.2047 | 28.5321 | 28.3363 | 27.0953 | 25.9879 | 28.5042 | 28.2221 | 27.9084 | 27.5705 | 27.1926 | 26.7495 | 26.1326 | 25.3705 | 24.5842 | 24.6316 | 23.4832 | 22.1589 | 29.8274 | 29.5716 | 29.2589 | 28.9221 | 28.5453 | 28.1032 | 27.5358 | 26.7874 | 26.0158 | 25.9968 | 25.2021 | 23.8768
|  | MIDHURST PRIMARY | EE |  |  |  |  | 31.9837 | 31.7795 | 31.5479 | 31.2774 | 30.9521 | 30.5974 | 30.2458 | 29.8753 | 29.4911 | 28.7332 | 29.2542 | 28.4963 | 28.5042 | 28.2221 | 27.9084 | 27.5705 | 27.1926 | 26.7495 | 26.3579 | 25.9589 | 25.5411 | 24.6316 | 25.8621 | 24.9232 | 29.8274 | 29.5716 | 29.2589 | 28.9221 | 28.5453 | 28.1032 | 27.7116 | 27.3137 | 26.8968 | 25.9968 | 27.4284 | 26.5116
|  | MIDHURST PRIMARY | HT |  |  |  |  | 32.6753 | 32.5447 | 32.1721 | 31.6879 | 31.1174 | 30.4542 | 29.8605 | 29.2047 | 28.5321 | 28.3363 | 27.0953 | 25.9879 | 29.5568 | 29.2463 | 28.8053 | 28.2453 | 27.5863 | 26.8158 | 26.1326 | 25.3705 | 24.5842 | 24.9653 | 23.4832 | 22.1589 | 30.8526 | 30.5937 | 30.1611 | 29.6105 | 28.9632 | 28.2074 | 27.5358 | 26.7874 | 26.0158 | 26.6705 | 25.2021 | 23.8768
|  | MIDHURST PRIMARY | HE |  |  |  |  | 32.0984 | 31.9332 | 31.7363 | 31.4921 | 31.1826 | 30.8563 | 30.5721 | 30.2816 | 29.9847 | 29.7637 | 30.2858 | 29.7626 | 28.7063 | 28.5021 | 28.2547 | 27.9684 | 27.6253 | 27.2295 | 26.9137 | 26.5884 | 26.2463 | 25.8653 | 26.9916 | 26.3284 | 29.9758 | 29.7947 | 29.5789 | 29.3168 | 28.9747 | 28.58 | 28.2642 | 27.94 | 27.5979 | 27.2211 | 28.4768 | 27.8305
|  | MIDHURST PRIMARY | FB |  |  |  |  | 32.2321 | 32.1226 | 32.0321 | 31.9374 | 31.8363 | 31.7184 | 31.6195 | 31.5258 | 31.4216 | 31.0079 | 30.4395 | 29.93 | 28.8768 | 28.72 | 28.5916 | 28.4642 | 28.3284 | 28.16 | 28.0284 | 27.9032 | 27.7621 | 27.1705 | 26.4684 | 25.8474 | 30.1242 | 29.9958 | 29.8905 | 29.7832 | 29.6695 | 29.5095 | 29.3779 | 29.2526 | 29.1126 | 28.5242 | 27.8263 | 27.2116
AXMINSTER GSP | YEOVIL BSP | MILBORNE PORT PRIMARY | MINIMUM HEADROOM | ST 67929 19741 | YES | YES | 0 | 3.3684 | 3.2737 | 3.1779 | 3.0653 | 2.6737 | 2.3558 | 2.0421 | 1.9126 | 1.7768 | 1.3874 | 1.0968 | 0.80105 | 2.8474 | 2.7484 | 2.6474 | 2.5305 | 2.1053 | 1.7621 | 1.4158 | 1.28 | 1.1389 | 0.71895 | 0.40211 | 0.075789 | 2.9863 | 2.8884 | 2.7884 | 2.6726 | 2.2432 | 1.8874 | 1.5379 | 1.4021 | 1.26 | 0.84105 | 0.52526 | 0.19895
|  | MILBORNE PORT PRIMARY | EE |  |  |  |  | 3.3684 | 3.2737 | 3.1779 | 3.0653 | 2.7526 | 2.5158 | 2.3958 | 2.0905 | 1.7895 | 1.6053 | 1.4232 | 1.2379 | 2.8474 | 2.7484 | 2.6474 | 2.5305 | 2.1937 | 1.9411 | 1.8168 | 1.4863 | 1.1463 | 0.93895 | 0.73579 | 0.52526 | 2.9863 | 2.8884 | 2.7884 | 2.6726 | 2.3358 | 2.0758 | 1.9495 | 1.6063 | 1.2684 | 1.06 | 0.85684 | 0.64737
|  | MILBORNE PORT PRIMARY | HT |  |  |  |  | 3.3853 | 3.3011 | 3.1989 | 3.0884 | 2.6737 | 2.3558 | 2.0421 | 1.9126 | 1.7768 | 1.3874 | 1.0968 | 0.80105 | 2.8663 | 2.7779 | 2.6716 | 2.5568 | 2.1053 | 1.7621 | 1.4158 | 1.28 | 1.1389 | 0.71895 | 0.40211 | 0.075789 | 3.0053 | 2.9168 | 2.8116 | 2.6979 | 2.2432 | 1.8874 | 1.5379 | 1.4021 | 1.26 | 0.84105 | 0.52526 | 0.19895
|  | MILBORNE PORT PRIMARY | HE |  |  |  |  | 3.4263 | 3.3558 | 3.2821 | 3.1874 | 2.8863 | 2.72 | 2.56 | 2.2705 | 1.9832 | 1.9326 | 1.8421 | 1.7347 | 2.9116 | 2.8379 | 2.7621 | 2.6653 | 2.34 | 2.1653 | 1.9968 | 1.6832 | 1.3684 | 1.3063 | 1.2021 | 1.0779 | 3.0484 | 2.9758 | 2.9011 | 2.8042 | 2.4853 | 2.3095 | 2.1368 | 1.8126 | 1.4905 | 1.4284 | 1.3242 | 1.2
|  | MILBORNE PORT PRIMARY | FB |  |  |  |  | 3.4926 | 3.4442 | 3.4063 | 3.3674 | 3.2547 | 3.2126 | 3.1463 | 3.0779 | 2.9305 | 2.6568 | 2.5253 | 2.3958 | 2.98 | 2.9284 | 2.8884 | 2.8474 | 2.7232 | 2.68 | 2.6074 | 2.5337 | 2.3716 | 2.0758 | 1.9337 | 1.7926 | 3.1168 | 3.0663 | 3.0263 | 2.9853 | 2.8642 | 2.8211 | 2.7505 | 2.6779 | 2.5147 | 2.2074 | 2.06 | 1.9137
FLEET-BRAMLEY GSP | ALDERSHOT BSP | MILFORD PRIMARY | MINIMUM HEADROOM | SU 94719 43018 | NO | YES | 0 | 26.9034 | 26.7571 | 26.5834 | 26.3466 | 26.0624 | 25.7497 | 25.0413 | 24.2161 | 23.3697 | 21.6824 | 20.6961 | 19.8266 | 26.1603 | 26.0139 | 25.6076 | 24.6487 | 23.5445 | 22.5097 | 21.4771 | 20.5582 | 19.6161 | 17.7497 | 16.6624 | 15.7034 | 27.5003 | 27.1792 | 26.5308 | 25.6255 | 24.5813 | 23.6013 | 22.6161 | 21.6992 | 20.7571 | 18.8939 | 17.8087 | 16.8508
|  | MILFORD PRIMARY | EE |  |  |  |  | 26.9034 | 26.7571 | 26.5876 | 26.3655 | 26.0624 | 25.7708 | 25.4971 | 25.2171 | 24.9455 | 24.7582 | 24.2392 | 23.6708 | 26.1603 | 26.0139 | 25.7539 | 25.0382 | 24.2424 | 23.635 | 23.095 | 22.6908 | 22.2771 | 21.4445 | 20.6824 | 20.0339 | 27.5003 | 27.1876 | 26.6655 | 25.9866 | 25.2287 | 24.6445 | 24.1245 | 23.7297 | 23.3266 | 22.5413 | 21.8224 | 21.175
|  | MILFORD PRIMARY | HT |  |  |  |  | 26.9118 | 26.7708 | 26.5834 | 26.3466 | 26.0624 | 25.7497 | 25.0413 | 24.2161 | 23.3697 | 21.6824 | 20.6961 | 19.8266 | 26.1687 | 26.0276 | 25.6076 | 24.6487 | 23.5445 | 22.5097 | 21.4771 | 20.5582 | 19.6161 | 17.7497 | 16.6624 | 15.7034 | 27.5118 | 27.1792 | 26.5308 | 25.6255 | 24.5813 | 23.6013 | 22.6161 | 21.6992 | 20.7571 | 18.8939 | 17.8087 | 16.8508
|  | MILFORD PRIMARY | HE |  |  |  |  | 26.9445 | 26.8055 | 26.6466 | 26.4297 | 26.1329 | 25.8561 | 25.5855 | 25.3108 | 25.0382 | 25.0508 | 25.0108 | 24.9855 | 26.2013 | 26.0624 | 25.9034 | 25.4845 | 24.7308 | 24.1771 | 23.6992 | 23.3592 | 23.0024 | 22.635 | 22.1729 | 21.7782 | 27.5518 | 27.4024 | 27.0266 | 26.4045 | 25.6855 | 25.1518 | 24.6897 | 24.355 | 24.0045 | 23.6655 | 23.235 | 22.8676
|  | MILFORD PRIMARY | FB |  |  |  |  | 27.0508 | 26.9855 | 26.9255 | 26.8592 | 26.7855 | 26.7108 | 26.6382 | 26.5708 | 26.4982 | 26.2339 | 26.0866 | 25.995 | 26.3076 | 26.2424 | 26.1824 | 26.1161 | 26.0424 | 25.8739 | 25.6645 | 25.5308 | 25.3792 | 24.7497 | 24.2087 | 23.7508 | 27.6645 | 27.5897 | 27.5203 | 27.2929 | 27.0118 | 26.7866 | 26.5866 | 26.4582 | 26.3129 | 25.7108 | 25.1992 | 24.7687
MANNINGTON GSP | ARNEWOOD BSP | MILFORD-ON-SEA PRIMARY | MINIMUM HEADROOM | SZ 28252 93347 | NO | YES | 0 | 24.28 | 23.8684 | 23.3526 | 22.7084 | 21.8168 | 20.8505 | 19.9105 | 18.9442 | 18.1589 | 16.4221 | 15.1358 | 14.0642 | 22.4537 | 21.9368 | 21.2947 | 20.4958 | 19.3705 | 18.1547 | 16.9737 | 15.8621 | 14.9958 | 13.0884 | 11.6589 | 10.4695 | 23.5021 | 23.0116 | 22.3926 | 21.5926 | 20.4684 | 19.2516 | 18.0695 | 16.9579 | 16.0926 | 14.1842 | 12.7526 | 11.5632
|  | MILFORD-ON-SEA PRIMARY | EE |  |  |  |  | 24.28 | 23.8726 | 23.4589 | 23.0084 | 22.3642 | 21.7063 | 21.0589 | 20.4747 | 20.0926 | 19.4147 | 18.5916 | 17.9021 | 22.4537 | 21.9484 | 21.4411 | 20.9063 | 20.1379 | 19.3411 | 18.5495 | 17.8484 | 17.4295 | 16.5642 | 15.5484 | 14.7632 | 23.5021 | 23.0221 | 22.5389 | 22.0042 | 21.2358 | 20.4379 | 19.6453 | 18.9442 | 18.5263 | 17.6611 | 16.6453 | 15.8589
|  | MILFORD-ON-SEA PRIMARY | HT |  |  |  |  | 24.3116 | 23.8684 | 23.3526 | 22.7084 | 21.8168 | 20.8505 | 19.9105 | 18.9442 | 18.1589 | 16.4221 | 15.1358 | 14.0642 | 22.4937 | 21.9368 | 21.2947 | 20.4958 | 19.3705 | 18.1547 | 16.9737 | 15.8621 | 14.9958 | 13.0884 | 11.6589 | 10.4695 | 23.54 | 23.0116 | 22.3926 | 21.5926 | 20.4684 | 19.2516 | 18.0695 | 16.9579 | 16.0926 | 14.1842 | 12.7526 | 11.5632
|  | MILFORD-ON-SEA PRIMARY | HE |  |  |  |  | 24.4684 | 24.1305 | 23.7789 | 23.3789 | 22.7716 | 22.16 | 21.5653 | 21.0326 | 20.7021 | 20.4832 | 19.9863 | 19.6253 | 22.6989 | 22.2863 | 21.8611 | 21.3937 | 20.6726 | 19.9347 | 19.2158 | 18.5863 | 18.2389 | 17.9232 | 17.2495 | 16.7579 | 23.7326 | 23.3389 | 22.9337 | 22.4832 | 21.7705 | 21.0316 | 20.3126 | 19.6842 | 19.3358 | 19.02 | 18.3463 | 17.8547
|  | MILFORD-ON-SEA PRIMARY | FB |  |  |  |  | 24.6579 | 24.4474 | 24.2758 | 24.1032 | 23.8779 | 23.6242 | 23.3642 | 23.1358 | 23.0074 | 22.4695 | 21.9305 | 21.5211 | 22.92 | 22.6537 | 22.44 | 22.2274 | 21.9442 | 21.6211 | 21.2905 | 21 | 20.8516 | 20.2147 | 19.5253 | 18.9926 | 23.9453 | 23.6937 | 23.4905 | 23.2884 | 23.02 | 22.7147 | 22.3874 | 22.0968 | 21.9495 | 21.3116 | 20.6221 | 20.0895
MANNINGTON GSP | MANNINGTON BSP | MILL LANE PRIMARY | MINIMUM HEADROOM | SU 14691 05633 | NO | YES | 0 | 34.6479 | 34.2047 | 43.0811 | 42.1947 | 40.9863 | 39.5947 | 38.2168 | 36.7768 | 35.2926 | 30.5895 | 28.7042 | 27.1032 | 30.0768 | 29.5263 | 37.7621 | 36.7189 | 35.2811 | 33.6832 | 32.1105 | 30.4642 | 28.7926 | 23.4316 | 21.32 | 19.5284 | 30.1821 | 29.6579 | 38.2242 | 37.2337 | 35.8 | 34.2053 | 32.6368 | 30.9947 | 29.3263 | 23.9789 | 21.8716 | 20.0842
|  | MILL LANE PRIMARY | EE |  |  |  |  | 34.6479 | 34.2563 | 43.2063 | 42.5989 | 41.7411 | 40.8421 | 39.9158 | 38.9432 | 37.9874 | 34.6474 | 33.3011 | 32.2126 | 30.0768 | 29.6095 | 37.92 | 37.2305 | 36.2537 | 35.2147 | 34.1442 | 33.0505 | 31.9758 | 28.0463 | 26.5032 | 25.2558 | 30.1821 | 29.7326 | 38.3695 | 37.7084 | 36.7695 | 35.7337 | 34.6653 | 33.5726 | 32.4989 | 28.5821 | 27.0432 | 25.7979
|  | MILL LANE PRIMARY | HT |  |  |  |  | 34.69 | 34.2047 | 43.0811 | 42.1947 | 40.9863 | 39.5947 | 38.2168 | 36.7768 | 35.2926 | 30.5895 | 28.7042 | 27.1032 | 30.1326 | 29.5263 | 37.7621 | 36.7189 | 35.2811 | 33.6832 | 32.1105 | 30.4642 | 28.7926 | 23.4316 | 21.32 | 19.5284 | 30.2337 | 29.6579 | 38.2242 | 37.2337 | 35.8 | 34.2053 | 32.6368 | 30.9947 | 29.3263 | 23.9789 | 21.8716 | 20.0842
|  | MILL LANE PRIMARY | HE |  |  |  |  | 34.8963 | 34.5953 | 43.6484 | 43.1347 | 42.3295 | 41.5032 | 40.6884 | 39.8558 | 39.0074 | 36.4811 | 35.6053 | 34.9147 | 30.4053 | 30.0621 | 38.4884 | 37.8895 | 36.9768 | 36.0242 | 35.0842 | 34.1232 | 33.1758 | 30.1242 | 29.1042 | 28.2989 | 30.4905 | 30.1568 | 38.9032 | 38.3263 | 37.4505 | 36.54 | 35.6021 | 34.6432 | 33.6968 | 30.6547 | 29.6379 | 28.8347
|  | MILL LANE PRIMARY | FB |  |  |  |  | 35.0479 | 34.9279 | 44.2116 | 43.9632 | 43.6874 | 43.3453 | 42.9895 | 42.6189 | 42.2263 | 40.7042 | 39.2737 | 38.5589 | 30.6811 | 30.4263 | 39.1253 | 38.8126 | 38.4621 | 38.0484 | 37.62 | 37.1716 | 36.6947 | 34.8789 | 33.1926 | 32.3568 | 30.7558 | 30.5126 | 39.5211 | 39.2242 | 38.8926 | 38.5032 | 38.0989 | 37.6768 | 37.2126 | 35.4 | 33.7189 | 32.8842
COWLEY GSP | DRAYTON BSP | MILTON PRIMARY | MINIMUM HEADROOM | SU 49992 92060 | NO | YES | 0 | 55.28 | 54.6105 | 53.4558 | 60.4989 | 58.6516 | 55.3453 | 51.6042 | 50.74 | 48.1663 | 55.5474 | 53.1695 | 52.4684 | 50.6905 | 49.3053 | 47.1621 | 52.5579 | 50.4958 | 46.8189 | 42.5021 | 41.5937 | 38.6453 | 46.8495 | 44.14 | 43.3421 | 52.9832 | 51.6747 | 49.5842 | 55.6779 | 53.6158 | 49.6926 | 45.3863 | 44.4411 | 41.4937 | 49.8368 | 47.0432 | 46.2463
|  | MILTON PRIMARY | EE |  |  |  |  | 55.4042 | 54.6105 | 53.4558 | 61.4916 | 58.6516 | 57.3 | 53.9284 | 50.74 | 48.1663 | 65.5463 | 61.6558 | 60.4463 | 50.6905 | 49.3053 | 47.1621 | 53.6979 | 50.4958 | 49.1516 | 45.2632 | 41.5937 | 38.6453 | 70.3463 | 65.9158 | 64.5832 | 52.9832 | 51.6747 | 49.5842 | 56.8442 | 53.6158 | 51.9916 | 48.1063 | 44.4411 | 41.4937 | 78.7579 | 74.2526 | 72.88
|  | MILTON PRIMARY | HT |  |  |  |  | 56.0084 | 55.1316 | 53.8853 | 60.4989 | 58.9474 | 55.3453 | 51.6042 | 76.7779 | 73.8695 | 63.7568 | 59.0147 | 57.0579 | 51.2863 | 49.6853 | 47.3653 | 52.5579 | 50.9726 | 46.8189 | 42.5021 | 78.8779 | 78.3947 | 68.3526 | 62.9716 | 60.8095 | 53.5232 | 52.0232 | 49.7358 | 55.6779 | 53.8379 | 49.6926 | 45.3863 | 85.3895 | 84.9074 | 76.8116 | 71.3642 | 69.1747
|  | MILTON PRIMARY | HE |  |  |  |  | 55.6905 | 55.0179 | 53.9916 | 62.1947 | 60.7779 | 59.4663 | 55.9137 | 52.8684 | 50.3347 | 67.8926 | 64.5642 | 63.8642 | 51.1347 | 49.9326 | 47.9968 | 54.7253 | 52.9232 | 51.6116 | 47.5 | 43.9884 | 41.08 | 72.8716 | 69.0295 | 68.2347 | 53.4147 | 52.2853 | 50.4305 | 57.8853 | 56.04 | 54.4821 | 50.3811 | 46.8768 | 43.9747 | 81.3737 | 77.48 | 76.6705
|  | MILTON PRIMARY | FB |  |  |  |  | 55.28 | 54.9284 | 54.5126 | 63.4316 | 62.7 | 62.7274 | 61.4737 | 59.8495 | 58.5137 | 55.5474 | 53.1695 | 52.4684 | 50.8842 | 50.2516 | 49.4653 | 57.48 | 56.0389 | 55.4189 | 53.5579 | 51.6653 | 50.1126 | 46.8495 | 44.14 | 43.3421 | 53.2221 | 52.6284 | 51.8947 | 60.6916 | 59.2726 | 58.5789 | 56.7474 | 54.8853 | 53.3568 | 49.8368 | 47.0432 | 46.2463
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON PRIMARY | MINIMUM HEADROOM | ST 96164 14520 | YES | YES | 0 | 4.8084 | 4.7537 | 4.6968 | 4.6074 | 4.5074 | 4.3968 | 4.2853 | 4.1726 | 4.0589 | 3.7695 | 3.5716 | 3.3958 | 4.78 | 4.72 | 4.6579 | 4.56 | 4.4505 | 4.3295 | 4.2074 | 4.0842 | 3.9589 | 3.6379 | 3.4179 | 3.2211 | 4.7811 | 4.7211 | 4.6589 | 4.5611 | 4.4516 | 4.3305 | 4.2095 | 4.0853 | 3.9611 | 3.6411 | 3.4211 | 3.2253
|  | MINCHINGTON PRIMARY | EE |  |  |  |  | 4.8084 | 4.7537 | 4.6979 | 4.6326 | 4.5505 | 4.4747 | 4.3968 | 4.3232 | 4.2474 | 4.0926 | 3.9526 | 3.8347 | 4.78 | 4.72 | 4.6589 | 4.5895 | 4.5021 | 4.4221 | 4.3379 | 4.2589 | 4.1779 | 4.0011 | 3.8411 | 3.7053 | 4.7811 | 4.7211 | 4.66 | 4.5895 | 4.5032 | 4.4232 | 4.3389 | 4.26 | 4.18 | 4.0021 | 3.8432 | 3.7084
|  | MINCHINGTON PRIMARY | HT |  |  |  |  | 4.8179 | 4.7663 | 4.6968 | 4.6074 | 4.5074 | 4.3968 | 4.2853 | 4.1726 | 4.0589 | 3.7695 | 3.5716 | 3.3958 | 4.7905 | 4.7337 | 4.6579 | 4.56 | 4.4505 | 4.3295 | 4.2074 | 4.0842 | 3.9589 | 3.6379 | 3.4179 | 3.2211 | 4.7916 | 4.7347 | 4.6589 | 4.5611 | 4.4516 | 4.3305 | 4.2095 | 4.0853 | 3.9611 | 3.6411 | 3.4211 | 3.2253
|  | MINCHINGTON PRIMARY | HE |  |  |  |  | 4.8442 | 4.8032 | 4.7589 | 4.7032 | 4.6305 | 4.56 | 4.4937 | 4.4316 | 4.3674 | 4.2916 | 4.2042 | 4.1284 | 4.8211 | 4.7768 | 4.7295 | 4.6705 | 4.5926 | 4.5189 | 4.4495 | 4.3832 | 4.3168 | 4.2263 | 4.1242 | 4.0358 | 4.8211 | 4.7768 | 4.7295 | 4.6705 | 4.5937 | 4.52 | 4.4505 | 4.3842 | 4.3168 | 4.2274 | 4.1253 | 4.0368
|  | MINCHINGTON PRIMARY | FB |  |  |  |  | 4.8758 | 4.8463 | 4.8232 | 4.7989 | 4.7726 | 4.7453 | 4.7189 | 4.6926 | 4.6663 | 4.5516 | 4.4632 | 4.3874 | 4.8547 | 4.8221 | 4.7968 | 4.7705 | 4.7411 | 4.7116 | 4.6821 | 4.6537 | 4.6253 | 4.4968 | 4.3968 | 4.3105 | 4.8558 | 4.8232 | 4.7968 | 4.7705 | 4.7421 | 4.7126 | 4.6832 | 4.6547 | 4.6253 | 4.4979 | 4.3979 | 4.3126
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE PRIMARY | MINIMUM HEADROOM | SU 01647 91932 | NO | YES | 0 | 13.9411 | 13.8442 | 13.7453 | 13.6295 | 13.4789 | 13.3095 | 13.1368 | 12.94 | 12.7358 | 8.0495 | 6.4126 | 6.0074 | 12.1684 | 12.0684 | 11.9674 | 11.8495 | 11.6958 | 11.5221 | 11.3453 | 11.1432 | 10.9326 | 5.7916 | 3.9147 | 3.4653 | 12.5274 | 12.4263 | 12.3242 | 12.2063 | 12.0516 | 11.8768 | 11.6989 | 11.4947 | 11.2821 | 6.1611 | 4.2642 | 3.8105
|  | MINETY VILLAGE PRIMARY | EE |  |  |  |  | 13.9411 | 13.8442 | 13.7453 | 13.6358 | 13.5084 | 13.3832 | 13.2442 | 13.1063 | 12.9705 | 9.8126 | 8.2926 | 8.0032 | 12.1684 | 12.0684 | 11.9674 | 11.8547 | 11.7253 | 11.5979 | 11.4568 | 11.3147 | 11.1758 | 7.7989 | 6.0453 | 5.7179 | 12.5274 | 12.4263 | 12.3242 | 12.2105 | 12.0811 | 11.9537 | 11.8105 | 11.6684 | 11.5284 | 8.1263 | 6.4147 | 6.0853
|  | MINETY VILLAGE PRIMARY | HT |  |  |  |  | 13.9632 | 13.8716 | 13.7653 | 13.6295 | 13.4789 | 13.3095 | 13.1368 | 12.94 | 12.7358 | 8.0495 | 6.4126 | 6.0074 | 12.1905 | 12.0968 | 11.9874 | 11.8495 | 11.6958 | 11.5221 | 11.3453 | 11.1432 | 10.9326 | 5.7916 | 3.9147 | 3.4653 | 12.5495 | 12.4558 | 12.3453 | 12.2063 | 12.0516 | 11.8768 | 11.6989 | 11.4947 | 11.2821 | 6.1611 | 4.2642 | 3.8105
|  | MINETY VILLAGE PRIMARY | HE |  |  |  |  | 14.0189 | 13.9547 | 13.8821 | 13.7937 | 13.6811 | 13.5779 | 13.4758 | 13.3779 | 13.2779 | 10.3453 | 8.9537 | 8.7716 | 12.2495 | 12.1832 | 12.1095 | 12.0189 | 11.9053 | 11.8011 | 11.6979 | 11.5989 | 11.4979 | 8.3895 | 6.7853 | 6.5758 | 12.6095 | 12.5421 | 12.4684 | 12.3779 | 12.2642 | 12.1589 | 12.0558 | 11.9558 | 11.8547 | 8.6926 | 7.1632 | 6.9516
|  | MINETY VILLAGE PRIMARY | FB |  |  |  |  | 16.4 | 14.02 | 13.98 | 13.9368 | 13.8926 | 13.8463 | 13.8021 | 13.7621 | 13.72 | 13.2863 | 11.6305 | 11.4389 | 14.7716 | 12.2495 | 12.2095 | 12.1642 | 12.1179 | 12.0705 | 12.0253 | 11.9842 | 11.9411 | 11.4874 | 9.7337 | 9.5326 | 14.8337 | 12.6095 | 12.5684 | 12.5232 | 12.4768 | 12.4295 | 12.3832 | 12.3421 | 12.2979 | 11.8379 | 10.0547 | 9.8505
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | MORTIMER PRIMARY | MINIMUM HEADROOM | SU 62236 64103 | NO | YES | 0 | 16.8624 | 16.4708 | 16.0076 | 15.4897 | 14.9992 | 14.5624 | 14.2455 | 13.9161 | 13.5897 | 11.2571 | 10.615 | 9.9592 | 12.4184 | 11.9153 | 11.3468 | 10.7405 | 10.1774 | 9.6889 | 9.35 | 8.9942 | 8.6395 | 5.8563 | 5.1626 | 4.4468 | 15.1242 | 14.6242 | 14.06 | 13.4579 | 12.8979 | 12.4116 | 12.0726 | 11.7189 | 11.3663 | 8.6011 | 7.9116 | 7.1947
|  | MORTIMER PRIMARY | EE |  |  |  |  | 16.8624 | 16.4708 | 16.0076 | 15.5182 | 15.0771 | 14.7287 | 14.4508 | 14.1624 | 13.8803 | 12.6403 | 12.2687 | 11.8761 | 12.4184 | 11.9153 | 11.3468 | 10.7742 | 10.2763 | 9.8953 | 9.5984 | 9.2889 | 8.9879 | 7.4595 | 7.0216 | 6.5511 | 15.1242 | 14.6242 | 14.06 | 13.4905 | 12.9947 | 12.6147 | 12.3189 | 12.0116 | 11.7116 | 10.1958 | 9.7611 | 9.2926
|  | MORTIMER PRIMARY | HT |  |  |  |  | 16.8982 | 16.5224 | 16.0371 | 15.4897 | 14.9992 | 14.5624 | 14.2455 | 13.9161 | 13.5897 | 11.2571 | 10.615 | 9.9592 | 12.4668 | 11.9837 | 11.3847 | 10.7405 | 10.1774 | 9.6889 | 9.35 | 8.9942 | 8.6395 | 5.8563 | 5.1626 | 4.4468 | 15.1716 | 14.6916 | 14.0979 | 13.4579 | 12.8979 | 12.4116 | 12.0726 | 11.7189 | 11.3663 | 8.6011 | 7.9116 | 7.1947
|  | MORTIMER PRIMARY | HE |  |  |  |  | 16.9876 | 16.6445 | 16.2424 | 15.7929 | 15.3761 | 15.0624 | 14.8224 | 14.5782 | 14.3382 | 13.4171 | 13.2434 | 13.0971 | 12.5826 | 12.1437 | 11.6321 | 11.1068 | 10.6405 | 10.2995 | 10.0489 | 9.7953 | 9.5468 | 8.3805 | 8.17 | 7.99 | 15.2874 | 14.8516 | 14.3421 | 13.8211 | 13.3568 | 13.0168 | 12.7674 | 12.5137 | 12.2653 | 11.1105 | 10.9011 | 10.7232
|  | MORTIMER PRIMARY | FB |  |  |  |  | 17.0876 | 17.0392 | 16.8803 | 16.7213 | 16.5813 | 16.4666 | 16.3771 | 16.2929 | 16.2034 | 15.8318 | 15.4739 | 15.2382 | 12.8616 | 12.6447 | 12.4384 | 12.2342 | 12.0605 | 11.9226 | 11.8184 | 11.7205 | 11.6163 | 11.1932 | 10.77 | 10.4911 | 15.5642 | 15.3484 | 15.1432 | 14.9411 | 14.7684 | 14.6316 | 14.5274 | 14.4305 | 14.3263 | 13.9053 | 13.4853 | 13.2074
MANNINGTON GSP | SALISBURY BSP | NETHERHAMPTON PRIMARY | MINIMUM HEADROOM | SU 12478 29102 | NO | YES | 9.4737 | 10.7316 | 10.6495 | 10.5579 | 10.3547 | 9.7621 | 9.1505 | 8.4411 | 7.92 | 7.7168 | 5.4463 | 5.0179 | 4.6516 | 10.3274 | 9.9979 | 9.5737 | 8.8737 | 8.1979 | 7.4979 | 6.6842 | 6.0905 | 5.8726 | 3.2474 | 2.7726 | 2.3663 | 10.5463 | 10.3137 | 9.8916 | 9.1926 | 8.5179 | 7.82 | 7.0084 | 6.4168 | 6.1989 | 3.58 | 3.1063 | 2.7011
|  | NETHERHAMPTON PRIMARY | EE |  |  |  |  | 10.7316 | 10.6495 | 10.5579 | 10.3547 | 9.7621 | 9.18 | 8.5968 | 8.1221 | 7.8821 | 6.7295 | 6.4284 | 6.1758 | 10.3274 | 9.9979 | 9.5737 | 8.8737 | 8.1979 | 7.5316 | 6.8642 | 6.3232 | 6.0589 | 4.7147 | 4.3737 | 4.0853 | 10.5463 | 10.3137 | 9.8916 | 9.1926 | 8.5179 | 7.8537 | 7.1874 | 6.6474 | 6.3842 | 5.0442 | 4.7042 | 4.4168
|  | NETHERHAMPTON PRIMARY | HT |  |  |  |  | 10.7368 | 10.6611 | 10.5579 | 10.3653 | 9.7663 | 9.1505 | 8.4411 | 7.92 | 7.7168 | 5.4463 | 5.0179 | 4.6516 | 10.3547 | 10.0379 | 9.6042 | 8.8884 | 8.2011 | 7.4979 | 6.6842 | 6.0905 | 5.8726 | 3.2474 | 2.7726 | 2.3663 | 10.5505 | 10.3537 | 9.9211 | 9.2074 | 8.5221 | 7.82 | 7.0084 | 6.4168 | 6.1989 | 3.58 | 3.1063 | 2.7011
|  | NETHERHAMPTON PRIMARY | HE |  |  |  |  | 10.7537 | 10.6811 | 10.5937 | 10.4611 | 9.9347 | 9.3705 | 8.8137 | 8.3632 | 8.1495 | 7.1947 | 7.0137 | 6.8642 | 10.4179 | 10.1242 | 9.7284 | 9.0516 | 8.3958 | 7.7495 | 7.1116 | 6.6011 | 6.3674 | 5.2411 | 5.0316 | 4.8579 | 10.5632 | 10.44 | 10.0453 | 9.3705 | 8.7158 | 8.0716 | 7.4347 | 6.9253 | 6.6916 | 5.5695 | 5.3611 | 5.1874
|  | NETHERHAMPTON PRIMARY | FB |  |  |  |  | 10.8074 | 10.7695 | 10.7326 | 10.6884 | 10.6389 | 10.5874 | 10.5368 | 10.4253 | 10.3221 | 10.0463 | 9.8358 | 9.6621 | 10.6189 | 10.4547 | 10.2758 | 10.0253 | 9.74 | 9.4547 | 9.1484 | 8.9442 | 8.8274 | 8.5211 | 8.2842 | 8.0863 | 10.6032 | 10.5768 | 10.5526 | 10.3411 | 10.0568 | 9.7726 | 9.4663 | 9.2632 | 9.1463 | 8.8411 | 8.6042 | 8.4074
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON PRIMARY | MINIMUM HEADROOM | SU 47615 12025 | NO | YES | 0 | 46.9611 | 46.5621 | 46.0989 | 44.6989 | 42.4368 | 40.4242 | 38.7158 | 36.8747 | 34.9811 | 29.7589 | 26.2347 | 23.1053 | 42.3789 | 40.0063 | 38.5421 | 36.5474 | 34.0558 | 31.8632 | 30.02 | 28.0211 | 25.9621 | 20.2232 | 16.3347 | 12.8779 | 42.0011 | 40.9347 | 39.6074 | 37.7958 | 35.5389 | 33.5284 | 31.8221 | 29.9821 | 28.0905 | 22.8768 | 19.1926 | 15.6926
|  | NETLEY COMMON PRIMARY | EE |  |  |  |  | 46.9611 | 46.5621 | 46.1032 | 44.9537 | 43.0484 | 41.2663 | 39.9358 | 38.7568 | 37.6779 | 33.1747 | 30.7358 | 28.6558 | 42.3789 | 40.0063 | 38.5421 | 36.8368 | 34.7653 | 32.8326 | 31.4126 | 30.1705 | 29.0411 | 23.9263 | 21.1811 | 18.8358 | 42.0011 | 40.9347 | 39.6074 | 38.0495 | 36.1474 | 34.3674 | 33.0389 | 31.86 | 30.7821 | 26.2874 | 23.8537 | 21.7032
|  | NETLEY COMMON PRIMARY | HT |  |  |  |  | 46.9758 | 46.5989 | 46.0989 | 44.6989 | 42.4368 | 40.4242 | 38.7158 | 36.8747 | 34.9811 | 29.7589 | 26.2347 | 23.1053 | 42.5189 | 40.1242 | 38.6126 | 36.5474 | 34.0558 | 31.8632 | 30.02 | 28.0211 | 25.9621 | 20.2232 | 16.3347 | 12.8779 | 42.1263 | 41.0411 | 39.6674 | 37.7958 | 35.5389 | 33.5284 | 31.8221 | 29.9821 | 28.0905 | 22.8768 | 19.1926 | 15.6926
|  | NETLEY COMMON PRIMARY | HE |  |  |  |  | 47.0295 | 46.6432 | 46.1937 | 45.5842 | 44.0884 | 42.4168 | 41.2126 | 40.1674 | 39.2126 | 35.9537 | 34.3379 | 32.9032 | 42.9274 | 40.7663 | 39.4832 | 37.9263 | 35.9516 | 34.1421 | 32.8695 | 31.7811 | 30.7968 | 27.0274 | 25.18 | 23.5347 | 42.4863 | 41.6032 | 40.4326 | 39.0042 | 37.1863 | 35.5158 | 34.3137 | 33.2684 | 32.3147 | 29.0632 | 27.4505 | 26.02
|  | NETLEY COMMON PRIMARY | FB |  |  |  |  | 47.3379 | 47.1516 | 46.9811 | 46.7937 | 46.5832 | 46.3716 | 46.1653 | 45.8842 | 45.5032 | 43.6147 | 41.9989 | 40.5905 | 43.5126 | 41.6989 | 41.1147 | 40.4011 | 39.6242 | 38.86 | 38.3116 | 37.8368 | 37.4295 | 35.3653 | 33.5653 | 31.98 | 43.0484 | 42.4779 | 41.9505 | 41.3084 | 40.6074 | 39.9179 | 39.4168 | 38.98 | 38.6 | 36.7147 | 35.1011 | 33.6947
MANNINGTON GSP | ARNEWOOD BSP | NEW MILTON PRIMARY | MINIMUM HEADROOM | SZ 23049 94942 | NO | YES | 0 | 33.6016 | 33.1289 | 32.5216 | 31.69 | 30.6805 | 29.5384 | 27.9068 | 24.3911 | 23.1753 | 20.1784 | 18.1237 | 16.3963 | 28.1463 | 27.5958 | 26.8737 | 25.8863 | 24.6874 | 23.3221 | 21.2811 | 16.6316 | 15.1589 | 11.6737 | 9.4137 | 7.5168 | 30.32 | 29.7895 | 29.0947 | 28.1474 | 26.9968 | 25.6895 | 23.7526 | 19.3916 | 17.9842 | 14.6547 | 12.4979 | 10.6579
|  | NEW MILTON PRIMARY | EE |  |  |  |  | 33.6016 | 33.1289 | 32.6489 | 32.0868 | 31.4037 | 30.6942 | 29.7174 | 27.7921 | 27.0479 | 25.5911 | 24.3279 | 23.3437 | 28.1463 | 27.5958 | 27.0453 | 26.42 | 25.6874 | 24.9053 | 23.7347 | 21.2632 | 20.4179 | 18.5389 | 16.9189 | 15.6537 | 30.32 | 29.7895 | 29.2547 | 28.6474 | 27.9263 | 27.1632 | 26.0421 | 23.7084 | 22.8884 | 21.1179 | 19.5884 | 18.3947
|  | NEW MILTON PRIMARY | HT |  |  |  |  | 33.6563 | 33.1468 | 32.5216 | 31.69 | 30.6805 | 29.5384 | 27.9068 | 24.3911 | 23.1753 | 20.1784 | 18.1237 | 16.3963 | 28.2179 | 27.6095 | 26.8737 | 25.8863 | 24.6874 | 23.3221 | 21.2811 | 16.6316 | 15.1589 | 11.6737 | 9.4137 | 7.5168 | 30.3863 | 29.8032 | 29.0947 | 28.1474 | 26.9968 | 25.6895 | 23.7526 | 19.3916 | 17.9842 | 14.6547 | 12.4979 | 10.6579
|  | NEW MILTON PRIMARY | HE |  |  |  |  | 33.91 | 33.5521 | 33.1732 | 32.6921 | 32.0658 | 31.4363 | 30.5416 | 28.71 | 28.0563 | 27.3826 | 26.6111 | 26.0405 | 28.5453 | 28.1474 | 27.7295 | 27.2116 | 26.5537 | 25.8716 | 24.8179 | 22.4737 | 21.7505 | 20.8053 | 19.7747 | 19.0084 | 30.6958 | 30.3074 | 29.8989 | 29.3916 | 28.7411 | 28.0726 | 27.0589 | 24.8453 | 24.14 | 23.2642 | 22.2989 | 21.5832
|  | NEW MILTON PRIMARY | FB |  |  |  |  | 34.2005 | 33.9426 | 33.7447 | 33.5332 | 33.3079 | 33.0584 | 32.7868 | 32.5226 | 32.2447 | 31.2837 | 30.2774 | 29.5995 | 28.8747 | 28.5663 | 28.3326 | 28.0884 | 27.8284 | 27.5379 | 27.2126 | 26.8947 | 26.5621 | 25.4211 | 24.1337 | 23.2632 | 31.0147 | 30.7189 | 30.4947 | 30.2589 | 30.0074 | 29.7274 | 29.4158 | 29.1126 | 28.7937 | 27.6979 | 26.4821 | 25.6611
FAWLEY GSP | COWES BSP | NEWPORT PRIMARY | MINIMUM HEADROOM | SZ 50076 89544 | NO | YES | 0 | 62.2137 | 61.8684 | 61.4737 | 62.2337 | 61.8432 | 58.8968 | 56.8211 | 54.7537 | 52.7947 | 47.6021 | 44.1905 | 41.5621 | 55.5568 | 55.0442 | 54.3221 | 55.2905 | 53.3505 | 49.3147 | 47.1032 | 44.8989 | 42.8126 | 37.2737 | 33.6305 | 30.8337 | 56.5232 | 55.7347 | 54.8221 | 55.5442 | 53.6874 | 49.8568 | 47.7432 | 45.6368 | 43.4389 | 37.5695 | 33.7063 | 30.7474
|  | NEWPORT PRIMARY | EE |  |  |  |  | 62.2137 | 61.8684 | 61.4737 | 62.4621 | 61.8432 | 61.0316 | 59.3789 | 57.7663 | 56.3042 | 52.2242 | 49.4968 | 47.5779 | 55.5568 | 55.0442 | 54.3221 | 55.5021 | 54.2105 | 51.6474 | 49.8947 | 48.1874 | 46.64 | 42.2421 | 39.3095 | 37.2484 | 56.5232 | 55.7347 | 54.8221 | 55.7347 | 54.48 | 52.0316 | 50.3442 | 48.6979 | 47.2084 | 42.8926 | 39.7684 | 37.5747
|  | NEWPORT PRIMARY | HT |  |  |  |  | 62.2705 | 61.9537 | 61.5642 | 62.5589 | 62.0253 | 58.8968 | 56.8211 | 54.7537 | 52.7947 | 47.6021 | 44.1905 | 41.5621 | 55.6474 | 55.1632 | 54.3853 | 55.2905 | 53.3505 | 49.3147 | 47.1032 | 44.8989 | 42.8126 | 37.2737 | 33.6305 | 30.8337 | 56.6695 | 55.9053 | 54.8884 | 55.5442 | 53.6874 | 49.8568 | 47.7432 | 45.6368 | 43.4389 | 37.5695 | 33.7063 | 30.7474
|  | NEWPORT PRIMARY | HE |  |  |  |  | 62.3937 | 62.1411 | 61.8568 | 62.9421 | 62.4084 | 61.9116 | 60.8958 | 59.5053 | 58.2274 | 55.4379 | 53.4958 | 52.2189 | 55.8463 | 55.4747 | 55.0389 | 56.6063 | 55.4653 | 53.0453 | 51.5137 | 50.0442 | 48.6947 | 45.6547 | 43.5474 | 42.1621 | 56.9895 | 56.4137 | 55.7179 | 56.8168 | 55.7116 | 53.4053 | 51.9358 | 50.5242 | 49.2274 | 46.3695 | 44.1937 | 42.7042
|  | NEWPORT PRIMARY | FB |  |  |  |  | 62.5895 | 62.4674 | 62.3568 | 62.2337 | 62.0968 | 61.9589 | 61.8253 | 61.7011 | 61.5674 | 60.0863 | 60.2158 | 59.0695 | 56.1095 | 55.8947 | 55.7 | 55.4832 | 55.2032 | 54.8358 | 54.2011 | 53.5568 | 52.9284 | 50.1147 | 50.6968 | 49.4653 | 57.3663 | 56.9937 | 56.6526 | 56.2768 | 55.8316 | 55.3453 | 54.74 | 54.1263 | 53.5284 | 50.8516 | 51.2189 | 50.0495
FLEET-BRAMLEY GSP | ALDERSHOT BSP | NORMANDY PRIMARY | MINIMUM HEADROOM | SU 93221 52894 | YES | YES | 0 | 6.9768 | 6.9063 | 6.7863 | 6.6147 | 6.4158 | 6.1947 | 5.9674 | 5.7295 | 5.4926 | 5.1105 | 4.9105 | 4.7368 | 6.3 | 6.2137 | 6.0674 | 5.86 | 5.6168 | 5.3505 | 5.0853 | 4.8137 | 4.5421 | 4.1116 | 3.8884 | 3.6947 | 6.7453 | 6.6484 | 6.5021 | 6.2947 | 6.0526 | 5.7863 | 5.5221 | 5.2505 | 4.98 | 4.5505 | 4.3284 | 4.1347
|  | NORMANDY PRIMARY | EE |  |  |  |  | 6.9768 | 6.9411 | 6.8853 | 6.8221 | 6.7568 | 6.6895 | 6.6211 | 6.5537 | 6.4842 | 6.3632 | 6.2305 | 6.1242 | 6.3021 | 6.2537 | 6.1947 | 6.1253 | 6.0547 | 5.9842 | 5.9105 | 5.8368 | 5.7611 | 5.6147 | 5.4516 | 5.3211 | 6.7474 | 6.6916 | 6.6295 | 6.5589 | 6.4895 | 6.4189 | 6.3453 | 6.2705 | 6.1958 | 6.0495 | 5.8874 | 5.7568
|  | NORMANDY PRIMARY | HT |  |  |  |  | 6.9779 | 6.9063 | 6.7863 | 6.6147 | 6.4158 | 6.1947 | 5.9674 | 5.7295 | 5.4926 | 5.1105 | 4.9105 | 4.7368 | 6.3 | 6.2137 | 6.0674 | 5.86 | 5.6168 | 5.3505 | 5.0853 | 4.8137 | 4.5421 | 4.1116 | 3.8884 | 3.6947 | 6.7453 | 6.6484 | 6.5021 | 6.2947 | 6.0526 | 5.7863 | 5.5221 | 5.2505 | 4.98 | 4.5505 | 4.3284 | 4.1347
|  | NORMANDY PRIMARY | HE |  |  |  |  | 6.9863 | 6.9621 | 6.9337 | 6.8884 | 6.8284 | 6.7737 | 6.7179 | 6.6653 | 6.6116 | 6.5821 | 6.5042 | 6.4432 | 6.3358 | 6.2989 | 6.2537 | 6.2011 | 6.1411 | 6.0863 | 6.0295 | 5.9737 | 5.9179 | 5.8811 | 5.7811 | 5.7042 | 6.7905 | 6.7484 | 6.6979 | 6.6411 | 6.5779 | 6.5211 | 6.4632 | 6.4074 | 6.3526 | 6.3147 | 6.2158 | 6.1389
|  | NORMANDY PRIMARY | FB |  |  |  |  | 7.0042 | 6.9926 | 6.9832 | 6.9716 | 6.9589 | 6.94 | 6.9189 | 6.8989 | 6.8789 | 6.7979 | 6.7063 | 6.6295 | 6.3653 | 6.3389 | 6.3179 | 6.2947 | 6.2726 | 6.2526 | 6.2316 | 6.2116 | 6.1905 | 6.0979 | 5.9874 | 5.8926 | 6.8232 | 6.7916 | 6.7674 | 6.74 | 6.7158 | 6.6916 | 6.6684 | 6.6463 | 6.6242 | 6.5316 | 6.4221 | 6.3274
NURSLING GSP | ROWNHAMS BSP | NORTH BADDESLEY PRIMARY | MINIMUM HEADROOM | SU 38080 20568 | NO | YES | 0 | 30.0289 | 29.6553 | 28.9163 | 27.9395 | 26.7374 | 25.8826 | 25.2184 | 24.6068 | 23.9184 | 16.8384 | 15.25 | 13.7711 | 25.6389 | 25 | 23.9168 | 22.6137 | 21.1895 | 20.1979 | 19.4379 | 18.7747 | 17.9958 | 9.2442 | 7.3642 | 5.6053 | 26.5421 | 25.9042 | 24.8232 | 23.5221 | 22.1011 | 21.1126 | 20.3547 | 19.6916 | 18.9137 | 10.1863 | 8.3105 | 6.5558
|  | NORTH BADDESLEY PRIMARY | EE |  |  |  |  | 30.0289 | 29.6553 | 28.9163 | 27.9395 | 26.7374 | 25.8826 | 25.2184 | 24.6479 | 23.9974 | 18.4826 | 17.2416 | 16.2363 | 25.6389 | 25 | 23.9168 | 22.6137 | 21.1895 | 20.1979 | 19.4379 | 18.7989 | 18.0589 | 11.1347 | 9.6189 | 8.3895 | 26.5421 | 25.9042 | 24.8232 | 23.5221 | 22.1011 | 21.1126 | 20.3547 | 19.7168 | 18.9768 | 12.0726 | 10.5611 | 9.3358
|  | NORTH BADDESLEY PRIMARY | HT |  |  |  |  | 30.0384 | 29.6763 | 28.9974 | 28.0395 | 26.8732 | 25.9542 | 25.2226 | 24.6068 | 23.9184 | 16.8384 | 15.25 | 13.7711 | 25.7168 | 25.02 | 24.0526 | 22.7453 | 21.3568 | 20.2905 | 19.46 | 18.7747 | 17.9958 | 9.2442 | 7.3642 | 5.6053 | 26.6189 | 25.9242 | 24.9579 | 23.6547 | 22.2695 | 21.2042 | 20.3747 | 19.6916 | 18.9137 | 10.1863 | 8.3105 | 6.5558
|  | NORTH BADDESLEY PRIMARY | HE |  |  |  |  | 30.0784 | 29.9068 | 29.23 | 28.3816 | 27.2289 | 26.4363 | 25.8279 | 25.3142 | 24.7195 | 19.7026 | 18.7795 | 18.0458 | 25.9053 | 25.3705 | 24.3779 | 23.1505 | 21.7832 | 20.8621 | 20.1737 | 19.6074 | 18.9347 | 12.5737 | 11.4189 | 10.4979 | 26.8074 | 26.2737 | 25.2842 | 24.0589 | 22.6947 | 21.7758 | 21.0884 | 20.5221 | 19.8516 | 13.5095 | 12.3579 | 11.44
|  | NORTH BADDESLEY PRIMARY | FB |  |  |  |  | 30.1995 | 30.1216 | 30.0258 | 29.6395 | 29.2911 | 29.0005 | 28.77 | 28.5774 | 28.3121 | 26.47 | 24.4237 | 23.7753 | 26.2189 | 25.8895 | 25.4789 | 24.8989 | 24.3853 | 23.9674 | 23.6453 | 23.3821 | 23.0463 | 20.7979 | 18.2526 | 17.46 | 27.12 | 26.7916 | 26.3821 | 25.8032 | 25.2905 | 24.8747 | 24.5537 | 24.2905 | 23.9558 | 21.7126 | 19.1747 | 18.3842
LOVEDEAN GSP | FAREHAM (MAIN) BSP | NORTH FAREHAM PRIMARY | MINIMUM HEADROOM | SU 56427 07430 | NO | YES | 0 | 16.9537 | 16.7695 | 16.2411 | 38.5789 | 37.7463 | 35.5589 | 33.3 | 30.7642 | 27.9863 | 21.1126 | 19.6326 | 18.3105 | 15.1074 | 14.0958 | 12.7737 | 32.6989 | 31.7779 | 29.2621 | 26.6611 | 23.7316 | 20.5147 | 12.5463 | 10.8937 | 9.4158 | 15.6884 | 14.8053 | 13.6495 | 34.8253 | 33.92 | 31.4105 | 28.8137 | 25.8884 | 22.6779 | 14.7221 | 13.0716 | 11.5968
|  | NORTH FAREHAM PRIMARY | EE |  |  |  |  | 16.9537 | 16.7695 | 16.5663 | 39.4242 | 38.9189 | 36.9221 | 35.1937 | 33.3263 | 31.38 | 23.3779 | 22.3642 | 21.4926 | 15.1074 | 14.6958 | 13.4979 | 33.6926 | 33.1642 | 30.8684 | 28.8853 | 26.74 | 24.4989 | 15.0821 | 13.9232 | 12.9221 | 15.6884 | 15.3105 | 14.2653 | 35.7916 | 35.2684 | 33.0137 | 31.0337 | 28.8916 | 26.6547 | 17.2547 | 16.0968 | 15.0979
|  | NORTH FAREHAM PRIMARY | HT |  |  |  |  | 16.9589 | 16.7853 | 16.2411 | 38.5789 | 37.7463 | 35.5589 | 33.3 | 30.7642 | 27.9863 | 21.1126 | 19.6326 | 18.3105 | 15.1611 | 14.0958 | 12.7737 | 32.6989 | 31.7779 | 29.2621 | 26.6611 | 23.7316 | 20.5147 | 12.5463 | 10.8937 | 9.4158 | 15.7347 | 14.8053 | 13.6495 | 34.8253 | 33.92 | 31.4105 | 28.8137 | 25.8884 | 22.6779 | 14.7221 | 13.0716 | 11.5968
|  | NORTH FAREHAM PRIMARY | HE |  |  |  |  | 16.9979 | 16.8274 | 16.6368 | 40.1737 | 39.8095 | 39.4747 | 38.6042 | 37.4295 | 36.1621 | 30.2295 | 28.0505 | 25.8863 | 15.3842 | 15.0779 | 14.4863 | 35.3747 | 34.9053 | 34.0558 | 32.8958 | 31.5684 | 30.1284 | 23.1084 | 20.5411 | 17.9874 | 15.9295 | 15.6442 | 15.1137 | 37.2705 | 36.8158 | 36.0453 | 34.9905 | 33.6905 | 32.2737 | 25.2674 | 22.7042 | 20.1558
|  | NORTH FAREHAM PRIMARY | FB |  |  |  |  | 17.1284 | 17.0453 | 16.9705 | 40.6863 | 40.5926 | 40.5 | 40.4074 | 40.3232 | 40.1158 | 35.9926 | 33.7958 | 32.1874 | 15.6221 | 15.3947 | 15.2232 | 36.4989 | 36.3116 | 35.9379 | 35.5547 | 35.0411 | 34.4853 | 29.6705 | 27.1074 | 25.2274 | 16.1516 | 15.9453 | 15.7884 | 38.3011 | 38.1274 | 37.7968 | 37.4579 | 37.0095 | 36.5253 | 31.8189 | 29.26 | 27.3842
LALEHAM GSP | EAST BEDFONT BSP | NORTH FELTHAM PRIMARY | MINIMUM HEADROOM | TQ 10987 74875 | NO | YES | 0 | 27.6116 | 27.4874 | 27.34 | 27.1653 | 26.86 | 26.5105 | 26.1221 | 25.7411 | 25.3863 | 24.6168 | 24.1674 | 23.7474 | 29.3758 | 29.0589 | 28.7253 | 28.3958 | 27.3726 | 26.1726 | 24.7232 | 23.3042 | 22.0537 | 19.6937 | 18.4463 | 17.44 | 22.2905 | 22.0863 | 21.8611 | 21.6221 | 21.0337 | 20.3505 | 19.5463 | 18.7568 | 18.0495 | 16.6568 | 15.8947 | 15.2663
|  | NORTH FELTHAM PRIMARY | EE |  |  |  |  | 27.6221 | 27.5063 | 27.3674 | 27.2063 | 26.9674 | 26.7032 | 26.4116 | 26.1084 | 25.8316 | 25.3779 | 25.1442 | 24.9642 | 29.4463 | 29.1695 | 28.8253 | 28.5189 | 27.9674 | 27.2179 | 26.2295 | 25.1947 | 24.32 | 22.0853 | 21.2105 | 20.5558 | 22.3263 | 22.1432 | 21.9179 | 21.6958 | 21.3326 | 20.8789 | 20.3137 | 19.7232 | 19.2116 | 18.0579 | 17.5716 | 17.2063
|  | NORTH FELTHAM PRIMARY | HT |  |  |  |  | 27.6116 | 27.4874 | 27.34 | 27.1653 | 26.86 | 26.5105 | 26.1221 | 25.7411 | 25.3863 | 24.6168 | 24.1674 | 23.7474 | 29.3758 | 29.0589 | 28.7253 | 28.3958 | 27.3726 | 26.1726 | 24.7232 | 23.3042 | 22.0537 | 19.6937 | 18.4463 | 17.44 | 22.2905 | 22.0863 | 21.8611 | 21.6221 | 21.0337 | 20.3505 | 19.5463 | 18.7568 | 18.0495 | 16.6568 | 15.8947 | 15.2663
|  | NORTH FELTHAM PRIMARY | HE |  |  |  |  | 27.6526 | 27.54 | 27.4084 | 27.2505 | 27.0084 | 26.7474 | 26.4568 | 26.1568 | 25.8811 | 25.6179 | 25.4937 | 25.4063 | 29.5632 | 29.3274 | 29.0211 | 28.7453 | 28.2221 | 27.4884 | 26.5326 | 25.5305 | 24.6916 | 22.9316 | 22.3063 | 21.8674 | 22.3926 | 22.2284 | 22.0242 | 21.8168 | 21.4579 | 21.0116 | 20.46 | 19.8842 | 19.3874 | 18.5358 | 18.2158 | 17.9895
|  | NORTH FELTHAM PRIMARY | FB |  |  |  |  | 27.7337 | 27.6684 | 27.6105 | 27.5474 | 27.4695 | 27.3874 | 27.2916 | 27.1874 | 27.0832 | 26.6421 | 26.4568 | 26.3305 | 29.7337 | 29.5779 | 29.44 | 29.2968 | 29.0926 | 28.8674 | 28.5442 | 28.1295 | 27.7389 | 25.9358 | 25.3253 | 24.8853 | 22.5116 | 22.4084 | 22.3168 | 22.22 | 22.0895 | 21.9474 | 21.7568 | 21.5305 | 21.3137 | 20.3379 | 19.9863 | 19.7358
COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY PRIMARY | MINIMUM HEADROOM | SP 48645 04403 | NO | YES | 0 | 9.5958 | 9.4979 | 6.4821 | 6.2653 | 6.0032 | 5.7579 | 5.5263 | 5.2916 | 5.0611 | 4.6526 | 4.2526 | 3.7042 | 7.3474 | 7.2495 | 4.0232 | 3.7916 | 3.5168 | 3.2579 | 3.0126 | 2.7653 | 2.5211 | 2.0558 | 1.5989 | 0.95474 | 8.5737 | 8.4758 | 4.9589 | 4.7274 | 4.4516 | 4.1926 | 3.9484 | 3.7011 | 3.4579 | 2.9937 | 2.5358 | 1.8937
|  | NORTH HINKSEY PRIMARY | EE |  |  |  |  | 9.5958 | 9.4979 | 6.4821 | 6.2653 | 6.0032 | 5.7579 | 5.5263 | 5.2916 | 5.0611 | 4.6526 | 4.2526 | 3.7042 | 7.3474 | 7.2495 | 4.0232 | 3.7916 | 3.5168 | 3.2579 | 3.0126 | 2.7653 | 2.5211 | 2.0558 | 1.5989 | 0.95474 | 8.5737 | 8.4758 | 4.9589 | 4.7274 | 4.4516 | 4.1926 | 3.9484 | 3.7011 | 3.4579 | 2.9937 | 2.5358 | 1.8937
|  | NORTH HINKSEY PRIMARY | HT |  |  |  |  | 9.6021 | 9.5084 | 9.3884 | 9.2337 | 8.9484 | 8.6168 | 8.2853 | 7.9347 | 7.5726 | 6.6432 | 5.8958 | 4.9589 | 7.3537 | 7.26 | 7.14 | 6.9853 | 6.8 | 6.5958 | 6.3579 | 5.9747 | 5.5789 | 4.5505 | 3.7053 | 2.6242 | 8.58 | 8.4863 | 8.3663 | 8.2116 | 7.9737 | 7.6232 | 7.2695 | 6.8947 | 6.5053 | 5.4821 | 4.6368 | 3.5568
|  | NORTH HINKSEY PRIMARY | HE |  |  |  |  | 9.6305 | 9.5432 | 6.7168 | 6.5358 | 6.3021 | 6.0905 | 5.8863 | 5.6779 | 5.4747 | 5.3242 | 5.0937 | 4.6884 | 7.3821 | 7.2947 | 4.2968 | 4.1063 | 3.8632 | 3.6432 | 3.4305 | 3.2137 | 3.0032 | 2.8189 | 2.5484 | 2.0621 | 8.6084 | 8.5211 | 5.2316 | 5.0411 | 4.7989 | 4.5779 | 4.3653 | 4.1495 | 3.9389 | 3.7558 | 3.4842 | 3
|  | NORTH HINKSEY PRIMARY | FB |  |  |  |  | 9.6937 | 9.6505 | 9.6116 | 9.5674 | 9.5189 | 9.4705 | 9.4232 | 9.3789 | 9.3316 | 9.08 | 8.7968 | 8.4579 | 7.4453 | 7.4021 | 7.3632 | 7.3189 | 7.2705 | 7.2221 | 7.1747 | 7.1305 | 7.0832 | 6.9105 | 6.8147 | 6.4916 | 8.6716 | 8.6284 | 8.5895 | 8.5453 | 8.4968 | 8.4484 | 8.4011 | 8.3568 | 8.3095 | 8.1095 | 7.7958 | 7.4126
NORTH HYDE GSP |  | NORTH HYDE PRIMARY | MINIMUM HEADROOM | TQ 10367 79001 | NO | NO | 0 | 99.7632 | 99.36 | 143.2768 | 142.6463 | 141.6179 | 140.7358 | 139.76 | 138.7495 | 137.6821 | 134.8063 | 132.2463 | 129.7147 | 93.1042 | 92.3979 | 140.4011 | 139.3589 | 137.3768 | 135.8716 | 134.1168 | 132.2558 | 130.2389 | 124.6853 | 121.4021 | 118.5558 | 70.7621 | 70.2411 | 116.0358 | 115.2442 | 113.8442 | 112.72 | 111.44 | 110.0989 | 108.6611 | 104.54 | 101.4368 | 98.5905
|  | NORTH HYDE PRIMARY | EE |  |  |  |  | 99.8526 | 99.4884 | 143.4684 | 142.9758 | 142.3495 | 141.5547 | 140.9663 | 140.3663 | 139.7716 | 138.3842 | 137.3032 | 136.4158 | 93.3632 | 92.7958 | 140.9095 | 140.2011 | 139.3811 | 138.0474 | 137.2053 | 136.3505 | 135.5147 | 132.4011 | 130.0695 | 128.1463 | 70.9179 | 70.4737 | 116.3495 | 115.7737 | 115.0716 | 114.0663 | 113.38 | 112.68 | 111.9916 | 109.9316 | 108.3632 | 107.0726
|  | NORTH HYDE PRIMARY | HT |  |  |  |  | 99.7632 | 99.36 | 143.2768 | 142.6463 | 141.6179 | 140.7358 | 139.76 | 138.7495 | 137.6821 | 134.8063 | 132.2463 | 129.7147 | 93.1042 | 92.3979 | 140.4011 | 139.3589 | 137.3768 | 135.8716 | 134.1168 | 132.2558 | 130.2389 | 124.6853 | 121.4021 | 118.5558 | 70.7621 | 70.2411 | 116.0358 | 115.2442 | 113.8442 | 112.72 | 111.44 | 110.0989 | 108.6611 | 104.54 | 101.4368 | 98.5905
|  | NORTH HYDE PRIMARY | HE |  |  |  |  | 100.0179 | 99.7116 | 143.7453 | 143.2979 | 142.6958 | 141.9442 | 141.4137 | 140.8674 | 140.3316 | 139.6347 | 138.9747 | 138.4484 | 93.7253 | 93.3 | 141.5389 | 140.9379 | 140.1832 | 138.9358 | 138.2579 | 137.56 | 136.8832 | 134.9221 | 133.3032 | 131.9905 | 71.1589 | 70.8074 | 116.7653 | 116.2568 | 115.5958 | 114.6505 | 114.0632 | 113.4579 | 112.8674 | 111.6779 | 110.6442 | 109.8116
|  | NORTH HYDE PRIMARY | FB |  |  |  |  | 100.3842 | 100.1737 | 144.3937 | 144.1821 | 143.9674 | 143.7505 | 143.4463 | 143.2442 | 143.0295 | 141.9432 | 141.1821 | 140.5811 | 94.4442 | 94.1042 | 142.6284 | 142.2884 | 141.9695 | 141.6421 | 141.0747 | 140.7632 | 140.4347 | 138.4295 | 136.9 | 135.6179 | 71.6632 | 71.4021 | 117.5842 | 117.3232 | 117.0684 | 116.8084 | 116.4011 | 116.1568 | 115.8968 | 114.4526 | 113.3926 | 112.5263
MINETY GSP | CIRENCESTER BSP | NORTHLEACH PRIMARY | MINIMUM HEADROOM | SP 10557 14251 | NO | YES | 0 | 11.3063 | 11.1958 | 11.0821 | 10.8968 | 10.6389 | 10.34 | 10.04 | 9.7389 | 9.4389 | 8.6779 | 8.1221 | 7.5274 | 10.6853 | 10.5663 | 10.4432 | 10.2421 | 9.9579 | 9.6284 | 9.2958 | 8.9632 | 8.6305 | 7.7832 | 7.1579 | 6.4842 | 11.0874 | 10.9684 | 10.8474 | 10.6474 | 10.3663 | 10.0389 | 9.7105 | 9.3811 | 9.0516 | 8.2126 | 7.5958 | 6.9295
|  | NORTHLEACH PRIMARY | EE |  |  |  |  | 11.3063 | 11.1958 | 11.0821 | 10.9589 | 10.7916 | 10.6168 | 10.44 | 10.2695 | 10.1021 | 9.7021 | 9.3274 | 8.9179 | 10.6853 | 10.5663 | 10.4432 | 10.3126 | 10.1347 | 9.9484 | 9.7558 | 9.5726 | 9.3937 | 8.9421 | 8.5147 | 8.0442 | 11.0874 | 10.9684 | 10.8474 | 10.7168 | 10.54 | 10.3547 | 10.1642 | 9.9821 | 9.8032 | 9.3579 | 8.9368 | 8.4716
|  | NORTHLEACH PRIMARY | HT |  |  |  |  | 11.3316 | 11.2221 | 11.0884 | 10.8968 | 10.6389 | 10.34 | 10.04 | 9.7389 | 9.4389 | 8.6779 | 8.1221 | 7.5274 | 10.7147 | 10.5947 | 10.4516 | 10.2421 | 9.9579 | 9.6284 | 9.2958 | 8.9632 | 8.6305 | 7.7832 | 7.1579 | 6.4842 | 11.1158 | 10.9968 | 10.8547 | 10.6474 | 10.3663 | 10.0389 | 9.7105 | 9.3811 | 9.0516 | 8.2126 | 7.5958 | 6.9295
|  | NORTHLEACH PRIMARY | HE |  |  |  |  | 11.3958 | 11.3221 | 11.2389 | 11.1368 | 11.0053 | 10.8505 | 10.7 | 10.5568 | 10.4147 | 10.1979 | 9.9411 | 9.6305 | 10.7863 | 10.7074 | 10.6189 | 10.5137 | 10.3758 | 10.2116 | 10.0505 | 9.8989 | 9.7495 | 9.5 | 9.2032 | 8.84 | 11.1863 | 11.1084 | 11.0211 | 10.9158 | 10.7779 | 10.6147 | 10.4558 | 10.3042 | 10.1558 | 9.9095 | 9.6168 | 9.26
|  | NORTHLEACH PRIMARY | FB |  |  |  |  | 11.4558 | 11.3947 | 11.3474 | 11.2979 | 11.2453 | 11.1811 | 11.1158 | 11.0568 | 10.9968 | 10.7516 | 10.5168 | 10.2495 | 10.8516 | 10.7842 | 10.7326 | 10.6779 | 10.6211 | 10.5516 | 10.4789 | 10.4147 | 10.3495 | 10.0789 | 9.8126 | 9.5053 | 11.2516 | 11.1853 | 11.1337 | 11.08 | 11.0232 | 10.9547 | 10.8832 | 10.8189 | 10.7547 | 10.4853 | 10.2232 | 9.9189
IVER 66KV GSP |  | NORTHOLT PRIMARY | MINIMUM HEADROOM | TQ 11550 83230 | NO | NO | 0.56105 | 83.9337 | 83.1537 | 82.0789 | 81.0884 | 79.7421 | 78.5684 | 76.9737 | 75.2526 | 73.1516 | 68.7589 | 66.2368 | 63.9779 | 80.3747 | 79.4537 | 78.1863 | 77.0621 | 75.5116 | 74.2021 | 72.3526 | 70.3379 | 67.8326 | 62.6905 | 59.7716 | 57.1558 | 80.0253 | 79.1221 | 77.8821 | 76.7747 | 75.2505 | 73.96 | 72.1432 | 70.1663 | 67.7147 | 62.6695 | 59.8032 | 57.2347
|  | NORTHOLT PRIMARY | EE |  |  |  |  | 83.9337 | 83.16 | 82.2042 | 81.3674 | 80.3947 | 79.4316 | 78.4905 | 77.5158 | 76.5547 | 74.6053 | 72.9895 | 71.6126 | 80.3747 | 79.4726 | 78.3505 | 77.4189 | 76.3632 | 75.3179 | 74.2895 | 73.2211 | 72.1716 | 69.8347 | 67.9011 | 66.2453 | 80.0253 | 79.1411 | 78.0411 | 77.1211 | 76.0747 | 75.0421 | 74.0253 | 72.9684 | 71.9295 | 69.6453 | 67.7516 | 66.1326
|  | NORTHOLT PRIMARY | HT |  |  |  |  | 83.9432 | 83.1537 | 82.0789 | 81.0884 | 79.7421 | 78.5684 | 76.9737 | 75.2526 | 73.1516 | 68.7589 | 66.2368 | 63.9779 | 80.3821 | 79.4537 | 78.1863 | 77.0621 | 75.5116 | 74.2021 | 72.3526 | 70.3379 | 67.8326 | 62.6905 | 59.7716 | 57.1558 | 80.0337 | 79.1221 | 77.8821 | 76.7747 | 75.2505 | 73.96 | 72.1432 | 70.1663 | 67.7147 | 62.6695 | 59.8032 | 57.2347
|  | NORTHOLT PRIMARY | HE |  |  |  |  | 84.3242 | 83.6947 | 82.8653 | 82.1305 | 81.2137 | 80.3389 | 79.5053 | 78.6379 | 77.7937 | 77.0274 | 76.2284 | 75.5411 | 80.8663 | 80.1526 | 79.1937 | 78.3968 | 77.42 | 76.4863 | 75.6021 | 74.6768 | 73.7789 | 72.7832 | 71.7863 | 70.9232 | 80.1105 | 79.7547 | 78.86 | 78.0716 | 77.1021 | 76.1758 | 75.2989 | 74.3811 | 73.4905 | 72.5242 | 71.5537 | 70.7126
|  | NORTHOLT PRIMARY | FB |  |  |  |  | 84.6505 | 84.2463 | 83.8 | 83.4284 | 83.0358 | 82.6379 | 82.2579 | 81.8937 | 81.4989 | 79.8863 | 78.6663 | 77.6747 | 81.3147 | 80.76 | 80.2389 | 79.8189 | 79.3779 | 78.9316 | 78.5063 | 78.0958 | 77.6516 | 75.8095 | 74.3695 | 73.1789 | 80.3474 | 80.1253 | 79.8905 | 79.4768 | 79.0421 | 78.6021 | 78.1821 | 77.7779 | 77.3411 | 75.5284 | 74.1179 | 72.9537
BRAMLEY (BASI) GSP | READING BSP | NORTHUMBERLAND AVENUE PRIMARY | MINIMUM HEADROOM | SU 72207 71092 | NO | YES | 0.31579 | 24.6713 | 24.4008 | 24.0608 | 23.7334 | 23.2134 | 22.6713 | 21.8103 | 21.1892 | 20.5271 | 17.5703 | 15.8313 | 14.9871 | 22.5889 | 22.4868 | 22.2089 | 21.8374 | 21.21 | 20.5447 | 19.4395 | 18.6637 | 17.8847 | 14.7605 | 12.5858 | 11.6521 | 23.3495 | 22.8021 | 22.1737 | 21.7832 | 21.1389 | 20.4726 | 19.3642 | 18.5863 | 17.8053 | 14.6832 | 12.4884 | 11.5537
|  | NORTHUMBERLAND AVENUE PRIMARY | EE |  |  |  |  | 24.6713 | 24.4008 | 24.065 | 23.7724 | 23.2345 | 22.6976 | 21.8271 | 21.2134 | 20.5661 | 18.0924 | 16.9471 | 16.3576 | 22.5889 | 22.4868 | 22.2163 | 21.8879 | 21.2468 | 20.5847 | 19.4605 | 18.6889 | 17.9237 | 15.3047 | 14.0037 | 13.3405 | 23.3495 | 22.8021 | 22.1821 | 21.8389 | 21.1758 | 20.5126 | 19.3853 | 18.6116 | 17.8442 | 15.2284 | 13.9232 | 13.2579
|  | NORTHUMBERLAND AVENUE PRIMARY | HT |  |  |  |  | 24.6913 | 24.4113 | 24.0608 | 23.7334 | 23.2134 | 22.6713 | 21.8103 | 21.1892 | 20.5271 | 17.5703 | 15.8313 | 14.9871 | 22.5953 | 22.5016 | 22.2089 | 21.8374 | 21.21 | 20.5447 | 19.4395 | 18.6637 | 17.8847 | 14.7605 | 12.5858 | 11.6521 | 23.3947 | 22.8074 | 22.1737 | 21.7832 | 21.1389 | 20.4726 | 19.3642 | 18.5863 | 17.8053 | 14.6832 | 12.4884 | 11.5537
|  | NORTHUMBERLAND AVENUE PRIMARY | HE |  |  |  |  | 24.7355 | 24.4861 | 24.1997 | 23.9818 | 23.4597 | 22.9492 | 22.1218 | 21.5555 | 20.9955 | 18.6261 | 17.7334 | 17.3587 | 22.6068 | 22.5068 | 22.3942 | 22.1468 | 21.5426 | 20.9216 | 19.8563 | 19.1521 | 18.4532 | 15.6795 | 14.6542 | 14.2258 | 23.4926 | 22.9968 | 22.4242 | 22.1189 | 21.48 | 20.8505 | 19.7832 | 19.0768 | 18.3758 | 15.5916 | 14.5632 | 14.1326
|  | NORTHUMBERLAND AVENUE PRIMARY | FB |  |  |  |  | 24.8261 | 24.7292 | 24.6166 | 24.5461 | 24.405 | 24.2639 | 23.9513 | 23.6839 | 23.4008 | 21.8608 | 21.1576 | 20.7597 | 22.6837 | 22.6332 | 22.5889 | 22.5374 | 22.4816 | 22.4247 | 22.0732 | 21.7468 | 21.3784 | 19.3374 | 18.4942 | 18.0468 | 23.6621 | 23.4326 | 23.2063 | 23.1032 | 22.8232 | 22.5421 | 22.0263 | 21.6779 | 21.3074 | 19.2611 | 18.4147 | 17.9663
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD PRIMARY | MINIMUM HEADROOM | SU 68329 86784 | YES | YES | 0 | 6.7558 | 6.6884 | 6.6126 | 6.5263 | 6.4147 | 6.3042 | 6.2053 | 6.0979 | 5.9916 | 5.5947 | 5.3737 | 5.1558 | 6.7221 | 6.6484 | 6.5674 | 6.4758 | 6.3568 | 6.24 | 6.1368 | 6.0232 | 5.9105 | 5.4737 | 5.2316 | 4.9916 | 6.7221 | 6.6495 | 6.5684 | 6.4758 | 6.3579 | 6.2411 | 6.1379 | 6.0242 | 5.9116 | 5.4758 | 5.2326 | 4.9937
|  | NUFFIELD PRIMARY | EE |  |  |  |  | 6.76 | 6.6905 | 6.6179 | 6.5389 | 6.4411 | 6.3505 | 6.2579 | 6.1621 | 6.0716 | 5.8347 | 5.6916 | 5.5589 | 6.7263 | 6.6505 | 6.5737 | 6.4884 | 6.3874 | 6.2926 | 6.1947 | 6.0926 | 5.9968 | 5.7263 | 5.5663 | 5.4158 | 6.7274 | 6.6516 | 6.5737 | 6.4895 | 6.3874 | 6.2926 | 6.1958 | 6.0926 | 5.9979 | 5.7284 | 5.5674 | 5.4168
|  | NUFFIELD PRIMARY | HT |  |  |  |  | 6.7558 | 6.6884 | 6.6126 | 6.5263 | 6.4147 | 6.3042 | 6.2053 | 6.0979 | 5.9916 | 5.5947 | 5.3737 | 5.1558 | 6.7221 | 6.6484 | 6.5674 | 6.4758 | 6.3568 | 6.24 | 6.1368 | 6.0232 | 5.9105 | 5.4737 | 5.2316 | 4.9916 | 6.7221 | 6.6495 | 6.5684 | 6.4758 | 6.3579 | 6.2411 | 6.1379 | 6.0242 | 5.9116 | 5.4758 | 5.2326 | 4.9937
|  | NUFFIELD PRIMARY | HE |  |  |  |  | 6.8116 | 6.7621 | 6.7084 | 6.6432 | 6.5558 | 6.4779 | 6.4032 | 6.3284 | 6.2537 | 6.1379 | 6.0642 | 6.0042 | 6.7853 | 6.7326 | 6.6758 | 6.6074 | 6.5179 | 6.4368 | 6.36 | 6.2821 | 6.2042 | 6.0684 | 5.9842 | 5.9147 | 6.7853 | 6.7326 | 6.6758 | 6.6074 | 6.5179 | 6.4379 | 6.36 | 6.2832 | 6.2053 | 6.0684 | 5.9853 | 5.9158
|  | NUFFIELD PRIMARY | FB |  |  |  |  | 6.8516 | 6.8137 | 6.7842 | 6.7537 | 6.7211 | 6.6874 | 6.6558 | 6.6242 | 6.5937 | 6.4632 | 6.3221 | 6.2379 | 6.8284 | 6.7863 | 6.7547 | 6.7211 | 6.6853 | 6.6495 | 6.6147 | 6.5811 | 6.5474 | 6.4053 | 6.2463 | 6.1505 | 6.8284 | 6.7874 | 6.7547 | 6.7211 | 6.6863 | 6.6495 | 6.6158 | 6.5811 | 6.5484 | 6.4063 | 6.2474 | 6.1516
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | OAKRIDGE PRIMARY | MINIMUM HEADROOM | SU 63496 53664 | NO | YES | 0 | 30.4816 | 30.0247 | 29.4889 | 28.8763 | 28.3868 | 27.8258 | 27.0732 | 26.3142 | 25.5511 | 23.5468 | 22.6932 | 21.6405 | 28.8442 | 28.3095 | 27.6189 | 26.8389 | 26.2589 | 25.5874 | 24.6463 | 23.6968 | 22.74 | 20.1947 | 19.1642 | 17.8263 | 29.5484 | 29.3684 | 29.1674 | 28.4053 | 27.8221 | 27.1463 | 26.1979 | 25.24 | 24.2758 | 21.7074 | 20.6768 | 19.3411
|  | OAKRIDGE PRIMARY | EE |  |  |  |  | 30.4816 | 30.0247 | 29.4889 | 28.9847 | 28.6068 | 28.2426 | 27.8753 | 27.1332 | 26.3963 | 24.9163 | 24.4153 | 23.7111 | 28.8442 | 28.3095 | 27.6189 | 26.9968 | 26.5863 | 26.1895 | 25.7811 | 24.8474 | 23.9189 | 21.9242 | 21.3011 | 20.3737 | 29.5484 | 29.3684 | 29.1674 | 28.5663 | 28.1547 | 27.7558 | 27.3463 | 26.4032 | 25.4674 | 23.4526 | 22.8232 | 21.8863
|  | OAKRIDGE PRIMARY | HT |  |  |  |  | 30.5332 | 30.1037 | 29.5174 | 28.8763 | 28.3868 | 27.8258 | 27.0732 | 26.3142 | 25.5511 | 23.5468 | 22.6932 | 21.6405 | 28.8589 | 28.4095 | 27.6526 | 26.8389 | 26.2589 | 25.5874 | 24.6463 | 23.6968 | 22.74 | 20.1947 | 19.1642 | 17.8263 | 29.5653 | 29.4011 | 29.1842 | 28.4053 | 27.8221 | 27.1463 | 26.1979 | 25.24 | 24.2758 | 21.7074 | 20.6768 | 19.3411
|  | OAKRIDGE PRIMARY | HE |  |  |  |  | 30.6226 | 30.2174 | 29.7237 | 29.2511 | 28.8879 | 28.5521 | 28.2153 | 27.65 | 27.0942 | 25.7637 | 25.5226 | 25.2795 | 28.8695 | 28.5726 | 27.9421 | 27.3674 | 26.9821 | 26.6253 | 26.2621 | 25.58 | 24.9105 | 23.0263 | 22.7095 | 22.3842 | 29.58 | 29.4074 | 29.2095 | 28.94 | 28.5547 | 28.1968 | 27.8326 | 27.1463 | 26.4716 | 24.5653 | 24.2453 | 23.9158
|  | OAKRIDGE PRIMARY | FB |  |  |  |  | 30.8353 | 30.5942 | 30.3563 | 30.1521 | 30.0174 | 29.8826 | 29.75 | 29.6237 | 29.3595 | 28.2521 | 27.8563 | 27.53 | 28.9853 | 28.9 | 28.7221 | 28.4663 | 28.3095 | 28.1547 | 28.0011 | 27.8537 | 27.5158 | 26.0768 | 25.5884 | 25.1726 | 29.7011 | 29.6084 | 29.5211 | 29.4316 | 29.3432 | 29.2537 | 29.1663 | 29.0853 | 28.9832 | 27.6389 | 27.1463 | 26.7274
COWLEY GSP | HEADINGTON BSP | OLD ROAD PRIMARY | MINIMUM HEADROOM | SP 55274 06426 | NO | YES | 0.063158 | 33.6711 | 33.5626 | 33.4479 | 33.2868 | 33.0732 | 32.8647 | 32.6447 | 32.4279 | 32.2111 | 31.6879 | 31.3563 | 31.0647 | 26.4063 | 26.0989 | 25.8316 | 25.4853 | 25.0547 | 24.6842 | 24.1895 | 23.7074 | 23.2895 | 22.0832 | 21.3916 | 20.7958 | 30.9663 | 30.6895 | 30.1463 | 29.4453 | 28.5642 | 27.9042 | 26.8716 | 25.8716 | 25.06 | 23.5126 | 22.8484 | 22.2737
|  | OLD ROAD PRIMARY | EE |  |  |  |  | 33.6711 | 33.5626 | 33.4479 | 33.2921 | 33.0732 | 32.87 | 32.6816 | 32.4858 | 32.2932 | 32.1142 | 31.9489 | 31.8153 | 26.4063 | 26.0989 | 25.8684 | 25.5821 | 25.1589 | 24.8958 | 24.5537 | 24.2337 | 23.9842 | 23.5779 | 23.3137 | 23.0989 | 30.9663 | 30.72 | 30.2642 | 29.7221 | 28.9021 | 28.5168 | 27.8726 | 27.3105 | 26.9484 | 26.0979 | 25.64 | 25.2653
|  | OLD ROAD PRIMARY | HT |  |  |  |  | 33.6805 | 33.5816 | 33.4521 | 33.2868 | 33.0868 | 32.8647 | 32.6447 | 32.4279 | 32.2111 | 31.6879 | 31.3563 | 31.0647 | 26.4137 | 26.1011 | 25.8316 | 25.4853 | 25.0547 | 24.6842 | 24.1895 | 23.7074 | 23.2895 | 22.0832 | 21.3916 | 20.7958 | 30.9768 | 30.6895 | 30.1463 | 29.4453 | 28.5642 | 27.9042 | 26.8716 | 25.8716 | 25.06 | 23.5126 | 22.8484 | 22.2737
|  | OLD ROAD PRIMARY | HE |  |  |  |  | 33.7016 | 33.6005 | 33.4889 | 33.3342 | 33.1111 | 32.9142 | 32.7237 | 32.5258 | 32.3353 | 32.3384 | 32.2879 | 32.2521 | 26.4779 | 26.1958 | 25.9832 | 25.7116 | 25.2937 | 25.0421 | 24.7095 | 24.3989 | 24.1632 | 24.0063 | 23.9011 | 23.8221 | 30.9979 | 30.8968 | 30.5232 | 30.0221 | 29.2221 | 28.8642 | 28.2526 | 27.7221 | 27.3979 | 26.9263 | 26.7147 | 26.5526
|  | OLD ROAD PRIMARY | FB |  |  |  |  | 33.7711 | 33.7163 | 33.6668 | 33.6121 | 33.5521 | 33.49 | 33.43 | 33.3732 | 33.3153 | 33.0963 | 32.9732 | 32.8953 | 26.6053 | 26.4642 | 26.3621 | 26.2505 | 26.1063 | 25.9537 | 25.8358 | 25.7295 | 25.6537 | 25.3305 | 25.1358 | 24.9926 | 31.0674 | 31.0126 | 30.9632 | 30.9084 | 30.7642 | 30.4337 | 30.2011 | 30 | 29.8884 | 29.36 | 29.0263 | 28.7547
COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD PRIMARY | MINIMUM HEADROOM | SP 50148 05901 | NO | YES | 0 | 35.0889 | 35.0205 | 34.9458 | 34.8395 | 34.7005 | 32.4174 | 29.4995 | 26.4458 | 24.0311 | 18.9321 | 18.4574 | 18.0174 | 31.5611 | 31.4926 | 31.4179 | 31.3116 | 31.1716 | 29.0968 | 25.6547 | 22.0832 | 19.2632 | 13.2989 | 12.7589 | 12.2589 | 32.4568 | 32.3884 | 32.3137 | 32.2074 | 32.0674 | 30.4653 | 27.0821 | 23.5211 | 20.7084 | 14.7137 | 14.1758 | 13.6747
|  | OXFORD PRIMARY | EE |  |  |  |  | 35.0889 | 35.0205 | 34.9458 | 34.8447 | 34.7005 | 32.8395 | 29.4995 | 26.4711 | 24.0805 | 18.9321 | 18.4574 | 18.0174 | 31.5611 | 31.4926 | 31.4179 | 31.3158 | 31.1716 | 29.5684 | 25.6547 | 22.1105 | 19.3168 | 13.2989 | 12.7589 | 12.2589 | 32.4568 | 32.3884 | 32.3137 | 32.2116 | 32.0674 | 30.9832 | 27.0821 | 23.5484 | 20.7632 | 14.7137 | 14.1758 | 13.6747
|  | OXFORD PRIMARY | HT |  |  |  |  | 35.0963 | 35.0311 | 34.9479 | 34.8395 | 35.0047 | 32.4174 | 31.9521 | 28.4932 | 25.7384 | 23.6679 | 23.0058 | 22.3711 | 31.5684 | 31.5032 | 31.42 | 31.3116 | 31.5505 | 29.0968 | 28.5747 | 24.5253 | 21.3063 | 18.9295 | 18.1895 | 17.4789 | 32.4642 | 32.3989 | 32.3158 | 32.2074 | 32.4053 | 30.4653 | 29.9432 | 25.9053 | 22.6958 | 20.3253 | 19.5863 | 18.8779
|  | OXFORD PRIMARY | HE |  |  |  |  | 35.1047 | 35.0363 | 34.9595 | 34.8542 | 34.7016 | 32.9184 | 29.5195 | 26.4458 | 24.0311 | 19.7353 | 19.4953 | 19.2647 | 31.5768 | 31.5084 | 31.4316 | 31.3263 | 31.1737 | 29.6611 | 25.68 | 22.0832 | 19.2632 | 14.2274 | 13.9526 | 13.6853 | 32.4726 | 32.4042 | 32.3274 | 32.2221 | 32.0695 | 31.0768 | 27.1074 | 23.5211 | 20.7084 | 15.6389 | 15.3653 | 15.0979
|  | OXFORD PRIMARY | FB |  |  |  |  | 35.15 | 35.11 | 35.0753 | 35.0353 | 34.9921 | 34.9479 | 34.9047 | 33.7332 | 32.7247 | 27.0689 | 26.8742 | 26.5689 | 31.6221 | 31.5821 | 31.5474 | 31.5074 | 31.4642 | 31.42 | 31.3768 | 30.5663 | 29.3874 | 22.7526 | 22.5632 | 22.2147 | 32.5179 | 32.4779 | 32.4432 | 32.4032 | 32.36 | 32.3158 | 32.2726 | 31.98 | 30.8042 | 24.1895 | 23.9516 | 23.6042
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | OXFORD SCIENCE PARK PRIMARY | MINIMUM HEADROOM | TBC | NO | YES | 0 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | OXFORD SCIENCE PARK PRIMARY | EE |  |  |  |  | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | OXFORD SCIENCE PARK PRIMARY | HT |  |  |  |  | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | OXFORD SCIENCE PARK PRIMARY | HE |  |  |  |  | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | OXFORD SCIENCE PARK PRIMARY | FB |  |  |  |  | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 22.68 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | OVERTON PRIMARY | MINIMUM HEADROOM | SU 52061 50913 | NO | YES | 0 | 29.6621 | 29.4474 | 29.3179 | 29.1537 | 28.7968 | 28.4179 | 26.3937 | 24.5147 | 22.6379 | 15.6147 | 12.7358 | 11.4968 | 29.4126 | 29.1716 | 29.0305 | 28.8568 | 28.4568 | 28.0358 | 25.6663 | 23.4695 | 21.2747 | 13.0347 | 9.68 | 8.1232 | 29.4211 | 29.1874 | 29.0495 | 28.8779 | 28.4832 | 28.0611 | 25.6968 | 23.5042 | 21.3126 | 13.0874 | 9.7389 | 8.1863
|  | OVERTON PRIMARY | EE |  |  |  |  | 29.6621 | 29.4474 | 29.3179 | 29.1695 | 28.8358 | 28.5105 | 28.1842 | 26.3158 | 24.4505 | 16.8537 | 13.4989 | 13.2284 | 29.4126 | 29.1716 | 29.0305 | 28.8747 | 28.5042 | 28.1442 | 27.78 | 25.5937 | 23.4105 | 14.4442 | 10.5116 | 10.2042 | 29.4211 | 29.1874 | 29.0495 | 28.8947 | 28.5295 | 28.1695 | 27.8063 | 25.6232 | 23.4432 | 14.4947 | 10.5695 | 10.2621
|  | OVERTON PRIMARY | HT |  |  |  |  | 29.6853 | 29.4842 | 29.34 | 29.1537 | 28.7968 | 28.4179 | 26.3937 | 24.5147 | 22.6379 | 15.6147 | 12.7358 | 12.32 | 29.44 | 29.2137 | 29.0579 | 28.8568 | 28.4568 | 28.0358 | 25.6663 | 23.4695 | 21.2747 | 13.0347 | 9.68 | 9.22 | 29.4484 | 29.2274 | 29.0747 | 28.8779 | 28.4832 | 28.0611 | 25.6968 | 23.5042 | 21.3126 | 13.0874 | 9.7389 | 9.28
|  | OVERTON PRIMARY | HE |  |  |  |  | 29.7432 | 29.5632 | 29.4621 | 29.3368 | 29.02 | 28.7179 | 28.4189 | 27.3611 | 26.3084 | 17.7179 | 14.1053 | 11.4968 | 29.5063 | 29.3053 | 29.1979 | 29.0674 | 28.7179 | 28.3821 | 28.0516 | 26.8232 | 25.6 | 15.4411 | 11.1895 | 8.1232 | 29.5126 | 29.3168 | 29.2105 | 29.0811 | 28.74 | 28.4074 | 28.0768 | 26.8516 | 25.6295 | 15.4895 | 11.2463 | 8.1863
|  | OVERTON PRIMARY | FB |  |  |  |  | 29.8821 | 29.7726 | 29.7189 | 29.6621 | 29.5389 | 29.4105 | 29.2768 | 29.2211 | 28.6358 | 25.6905 | 20.9705 | 18.9463 | 29.6611 | 29.5368 | 29.4789 | 29.4168 | 29.2779 | 29.1316 | 28.98 | 28.92 | 28.2337 | 24.7737 | 19.2042 | 16.8189 | 29.6632 | 29.5432 | 29.4853 | 29.4242 | 29.2895 | 29.1484 | 29 | 28.9421 | 28.26 | 24.8053 | 19.2474 | 16.8663
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PADWORTH PRIMARY | MINIMUM HEADROOM | SU 62243 66052 | YES | YES | 0 | 9.9126 | 9.8832 | 9.8526 | 9.8021 | 9.7474 | 9.6853 | 9.6232 | 9.5568 | 9.4874 | 8.8589 | 8.7505 | 8.6474 | 9.4874 | 9.4537 | 9.42 | 9.3632 | 9.3011 | 9.2316 | 9.1632 | 9.0874 | 9.0074 | 8.2305 | 8.1053 | 7.9853 | 10.2379 | 10.2053 | 10.1716 | 10.1147 | 10.0526 | 9.9842 | 9.9147 | 9.8389 | 9.7589 | 8.9842 | 8.86 | 8.74
|  | PADWORTH PRIMARY | EE |  |  |  |  | 9.9126 | 9.8832 | 9.8526 | 9.8189 | 9.7758 | 9.7358 | 9.6916 | 9.6495 | 9.6095 | 9.0611 | 8.9916 | 8.9305 | 9.4874 | 9.4537 | 9.42 | 9.3832 | 9.3379 | 9.2968 | 9.2484 | 9.2032 | 9.16 | 8.4705 | 8.3863 | 8.3126 | 10.2379 | 10.2053 | 10.1716 | 10.1347 | 10.0895 | 10.0484 | 10 | 9.9547 | 9.9126 | 9.2242 | 9.1411 | 9.0674
|  | PADWORTH PRIMARY | HT |  |  |  |  | 9.9179 | 9.8905 | 9.8526 | 9.8021 | 9.7474 | 9.6853 | 9.6232 | 9.5568 | 9.4874 | 8.8589 | 8.7505 | 8.6474 | 9.4937 | 9.4632 | 9.42 | 9.3632 | 9.3011 | 9.2316 | 9.1632 | 9.0874 | 9.0074 | 8.2305 | 8.1053 | 7.9853 | 10.2442 | 10.2147 | 10.1716 | 10.1147 | 10.0526 | 9.9842 | 9.9147 | 9.8389 | 9.7589 | 8.9842 | 8.86 | 8.74
|  | PADWORTH PRIMARY | HE |  |  |  |  | 9.9295 | 9.9063 | 9.8821 | 9.8526 | 9.8158 | 9.7789 | 9.7442 | 9.7105 | 9.6726 | 9.1821 | 9.1453 | 9.1126 | 9.5074 | 9.4832 | 9.4568 | 9.4263 | 9.3874 | 9.3495 | 9.3137 | 9.2789 | 9.24 | 8.6158 | 8.5705 | 8.5295 | 10.2589 | 10.2347 | 10.2084 | 10.1779 | 10.1389 | 10.1011 | 10.0653 | 10.0305 | 9.9905 | 9.3695 | 9.3242 | 9.2832
|  | PADWORTH PRIMARY | FB |  |  |  |  | 9.9516 | 9.9358 | 9.9232 | 9.9084 | 9.8958 | 9.8821 | 9.8684 | 9.8568 | 9.8432 | 9.7905 | 9.4389 | 9.3937 | 9.5316 | 9.5137 | 9.5 | 9.4832 | 9.4684 | 9.4537 | 9.4389 | 9.4253 | 9.4105 | 9.3516 | 8.9116 | 8.8558 | 10.2832 | 10.2653 | 10.2516 | 10.2347 | 10.22 | 10.2053 | 10.1905 | 10.1768 | 10.1621 | 10.1032 | 9.6642 | 9.6095
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PANGBOURNE PRIMARY | MINIMUM HEADROOM | SU 62960 76144 | NO | YES | 0 | 27.3634 | 27.2855 | 27.1939 | 27.0687 | 26.9182 | 26.755 | 26.5918 | 26.2834 | 25.9592 | 25.0424 | 24.5476 | 24.0329 | 25.5403 | 25.3813 | 25.2129 | 24.9339 | 24.6139 | 24.2761 | 23.9508 | 23.5939 | 23.2234 | 22.1487 | 21.5939 | 21.0224 | 26.1255 | 26.0171 | 25.8487 | 25.5687 | 25.2497 | 24.9118 | 24.5866 | 24.2297 | 23.8582 | 22.7834 | 22.2287 | 21.6571
|  | PANGBOURNE PRIMARY | EE |  |  |  |  | 27.3634 | 27.2855 | 27.1971 | 27.0782 | 26.9192 | 26.7655 | 26.6203 | 26.4761 | 26.3318 | 26.0192 | 25.6961 | 25.3876 | 25.5403 | 25.3813 | 25.2129 | 25.0245 | 24.8066 | 24.5939 | 24.3708 | 24.1497 | 23.9318 | 23.3118 | 22.9213 | 22.5434 | 26.1255 | 26.0171 | 25.8487 | 25.6603 | 25.4413 | 25.2297 | 25.0066 | 24.7855 | 24.5666 | 23.9466 | 23.5561 | 23.1792
|  | PANGBOURNE PRIMARY | HT |  |  |  |  | 27.3676 | 27.2918 | 27.1939 | 27.0687 | 26.9182 | 26.755 | 26.5918 | 26.2834 | 25.9592 | 25.0424 | 24.5476 | 24.0329 | 25.5687 | 25.4234 | 25.2129 | 24.9339 | 24.6139 | 24.2761 | 23.9508 | 23.5939 | 23.2234 | 22.1487 | 21.5939 | 21.0224 | 26.1297 | 26.0539 | 25.8487 | 25.5687 | 25.2497 | 24.9118 | 24.5866 | 24.2297 | 23.8582 | 22.7834 | 22.2287 | 21.6571
|  | PANGBOURNE PRIMARY | HE |  |  |  |  | 27.3813 | 27.3108 | 27.2266 | 27.1118 | 26.955 | 26.8097 | 26.6666 | 26.5213 | 26.3803 | 26.3876 | 26.3666 | 26.2487 | 25.6392 | 25.5318 | 25.4097 | 25.2582 | 25.0655 | 24.8813 | 24.7013 | 24.5203 | 24.3445 | 24.015 | 23.7982 | 23.5729 | 26.1434 | 26.0729 | 25.9887 | 25.8739 | 25.7003 | 25.5171 | 25.3371 | 25.1561 | 24.9803 | 24.6508 | 24.4339 | 24.2076
|  | PANGBOURNE PRIMARY | FB |  |  |  |  | 27.4403 | 27.4055 | 27.3739 | 27.3382 | 27.3003 | 27.2613 | 27.2234 | 27.1876 | 27.1487 | 27.0097 | 26.9329 | 26.8487 | 25.7329 | 25.6529 | 25.5908 | 25.5234 | 25.4539 | 25.3761 | 25.3003 | 25.2287 | 25.1539 | 24.8592 | 24.4497 | 24.1918 | 26.2024 | 26.1676 | 26.1361 | 26.1003 | 26.0624 | 26.0118 | 25.9361 | 25.8645 | 25.7897 | 25.495 | 25.0845 | 24.8266
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE PRIMARY | MINIMUM HEADROOM | SU 51369 08259 | NO | YES | 0 | 31.4416 | 31.2721 | 31.1395 | 30.9658 | 42.3711 | 41.1384 | 40.2163 | 39.2584 | 38.2679 | 35.9774 | 34.4479 | 33.0784 | 28.7705 | 28.6568 | 28.5611 | 28.4453 | 42.3063 | 41.6347 | 40.6211 | 39.5642 | 38.4684 | 35.9284 | 34.2253 | 32.6968 | 30.0084 | 29.8463 | 29.7095 | 29.5316 | 41.8421 | 41.4474 | 40.5642 | 39.5074 | 38.4105 | 35.8705 | 34.1663 | 32.6379
|  | PARK GATE PRIMARY | EE |  |  |  |  | 43.5574 | 43.3679 | 43.1511 | 42.8626 | 42.4763 | 42.0984 | 41.6458 | 41.0089 | 40.3816 | 38.73 | 37.6247 | 36.7258 | 43.3874 | 43.1979 | 42.9811 | 42.6926 | 42.3063 | 41.9284 | 41.5758 | 41.22 | 40.8674 | 39.0284 | 37.7653 | 36.7368 | 42.9232 | 42.7337 | 42.5168 | 42.2284 | 41.8421 | 41.4642 | 41.1116 | 40.7558 | 40.4032 | 38.9705 | 37.7074 | 36.6779
|  | PARK GATE PRIMARY | HT |  |  |  |  | 43.5605 | 43.3816 | 43.1437 | 42.8426 | 42.3711 | 41.1384 | 40.2163 | 39.2584 | 38.2679 | 35.9774 | 34.4479 | 33.0784 | 43.3905 | 43.2116 | 42.9737 | 42.6726 | 42.3095 | 41.6347 | 40.6211 | 39.5642 | 38.4684 | 35.9284 | 34.2253 | 32.6968 | 42.9263 | 42.7474 | 42.5095 | 42.2084 | 41.8453 | 41.4474 | 40.5642 | 39.5074 | 38.4105 | 35.8705 | 34.1663 | 32.6379
|  | PARK GATE PRIMARY | HE |  |  |  |  | 43.59 | 43.41 | 43.2058 | 42.9247 | 42.5458 | 42.1879 | 41.8374 | 41.4847 | 41.1353 | 40.1395 | 39.7089 | 39.2889 | 43.42 | 43.24 | 43.0358 | 42.7547 | 42.3758 | 42.0179 | 41.6674 | 41.3147 | 40.9653 | 40.6211 | 40.1221 | 39.6337 | 42.9558 | 42.7758 | 42.5716 | 42.2905 | 41.9116 | 41.5537 | 41.2032 | 40.8505 | 40.5011 | 40.5379 | 40.0653 | 39.5768
|  | PARK GATE PRIMARY | FB |  |  |  |  | 31.4416 | 31.2721 | 31.1395 | 30.9658 | 43.4058 | 43.3121 | 43.2205 | 43.1363 | 43.0447 | 42.7121 | 42.0395 | 41.5353 | 28.7705 | 28.6568 | 28.5611 | 28.4453 | 43.2358 | 43.1421 | 43.0505 | 42.9663 | 42.8747 | 42.5421 | 42.3579 | 42.0442 | 30.0084 | 29.8463 | 29.7095 | 29.5316 | 42.7716 | 42.6779 | 42.5863 | 42.5021 | 42.4105 | 42.0779 | 41.8937 | 41.7779
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PARK HOUSE PRIMARY | MINIMUM HEADROOM | SU 23138 43780 | NO | YES | 0 | 4.5337 | 4.5137 | 4.4884 | 4.4495 | 4.3916 | 4.3358 | 4.2789 | 2.5347 | 2.4758 | 2.3147 | 2.1558 | 2.0032 | 3.8589 | 3.8158 | 3.7674 | 3.7158 | 3.6547 | 3.5958 | 3.5368 | 1.4895 | 1.4284 | 1.2558 | 1.0789 | 0.90842 | 3.8589 | 3.8158 | 3.7684 | 3.7168 | 3.6547 | 3.5968 | 3.5379 | 1.4968 | 1.4358 | 1.2632 | 1.0863 | 0.91579
|  | PARK HOUSE PRIMARY | EE |  |  |  |  | 4.5337 | 4.5137 | 4.4884 | 4.4495 | 4.3916 | 4.3358 | 4.2789 | 3.3779 | 3.3242 | 3.2326 | 3.1253 | 3.0232 | 3.8589 | 3.8158 | 3.7674 | 3.7158 | 3.6547 | 3.5958 | 3.5368 | 2.4821 | 2.4263 | 2.3232 | 2.2011 | 2.0842 | 3.8589 | 3.8158 | 3.7684 | 3.7168 | 3.6547 | 3.5968 | 3.5379 | 2.4863 | 2.4295 | 2.3274 | 2.2053 | 2.0884
|  | PARK HOUSE PRIMARY | HT |  |  |  |  | 4.5347 | 4.5158 | 4.4895 | 4.4568 | 4.4063 | 4.3463 | 4.2884 | 2.5347 | 2.4758 | 2.3147 | 2.1558 | 2.0032 | 3.8684 | 3.8295 | 3.7821 | 3.7305 | 3.6726 | 3.6095 | 3.5484 | 1.4895 | 1.4284 | 1.2558 | 1.0789 | 0.90842 | 3.8684 | 3.8305 | 3.7832 | 3.7316 | 3.6726 | 3.6095 | 3.5495 | 1.4968 | 1.4358 | 1.2632 | 1.0863 | 0.91579
|  | PARK HOUSE PRIMARY | HE |  |  |  |  | 4.5389 | 4.5189 | 4.4968 | 4.4653 | 4.4211 | 4.3821 | 4.3432 | 3.4579 | 3.4084 | 3.3789 | 3.3095 | 3.2411 | 3.8905 | 3.8589 | 3.8232 | 3.7789 | 3.7221 | 3.6716 | 3.6211 | 2.5737 | 2.5232 | 2.4884 | 2.4074 | 2.3274 | 3.8905 | 3.8589 | 3.8232 | 3.78 | 3.7232 | 3.6716 | 3.6211 | 2.5779 | 2.5263 | 2.4916 | 2.4116 | 2.3316
|  | PARK HOUSE PRIMARY | FB |  |  |  |  | 4.5547 | 4.5442 | 4.5368 | 4.5263 | 4.5158 | 4.5053 | 4.4947 | 4.4853 | 4.4747 | 4.4011 | 4.3263 | 4.2516 | 3.9168 | 3.8916 | 3.8747 | 3.8516 | 3.8305 | 3.8095 | 3.7863 | 3.7674 | 3.7453 | 3.6621 | 3.5779 | 3.4926 | 3.9179 | 3.8926 | 3.8747 | 3.8516 | 3.8316 | 3.8095 | 3.7874 | 3.7674 | 3.7463 | 3.6632 | 3.5789 | 3.4937
MINETY GSP | STRATTON (MAIN) BSP | PARK NORTH PRIMARY | MINIMUM HEADROOM | SU 18052 84542 | NO | YES | 0 | 34.2647 | 34.0079 | 33.6079 | 32.7237 | 32.1405 | 31.1805 | 30.2111 | 29.2437 | 28.3068 | 25.0363 | 22.4268 | 20.0826 | 29.9063 | 29.1263 | 27.9747 | 26.9453 | 26.3305 | 25.2558 | 24.1642 | 23.0789 | 22.0337 | 18.6474 | 15.6968 | 13.0463 | 32.34 | 31.5716 | 30.44 | 29.4263 | 28.8179 | 27.7611 | 26.6905 | 25.6242 | 24.5979 | 21.3179 | 18.4326 | 15.7863
|  | PARK NORTH PRIMARY | EE |  |  |  |  | 34.2647 | 34.0079 | 33.6079 | 32.7237 | 32.1405 | 31.1805 | 30.2111 | 29.2437 | 28.3068 | 25.4342 | 23.5416 | 22.3416 | 29.9063 | 29.1263 | 27.9747 | 26.9453 | 26.3305 | 25.2558 | 24.1642 | 23.0789 | 22.0337 | 18.7305 | 16.5653 | 15.4126 | 32.34 | 31.5716 | 30.44 | 29.4263 | 28.8179 | 27.7611 | 26.6905 | 25.6242 | 24.5979 | 21.3747 | 19.2589 | 18.1505
|  | PARK NORTH PRIMARY | HT |  |  |  |  | 34.6332 | 34.3711 | 34.0479 | 33.2953 | 32.5763 | 31.5447 | 30.5047 | 29.4795 | 28.4763 | 25.0363 | 22.4268 | 20.0826 | 30.7621 | 29.8126 | 28.9116 | 27.8547 | 27.0611 | 25.9137 | 24.7547 | 23.6126 | 22.5021 | 18.6474 | 15.6968 | 13.0463 | 32.8653 | 32.2842 | 31.4011 | 30.3632 | 29.5789 | 28.4505 | 27.3116 | 26.1884 | 25.0958 | 21.3179 | 18.4326 | 15.7863
|  | PARK NORTH PRIMARY | HE |  |  |  |  | 34.3858 | 34.1668 | 33.8805 | 33.3532 | 32.8311 | 31.9426 | 31.0289 | 30.1258 | 29.2542 | 27.0058 | 25.5321 | 24.2658 | 30.2916 | 29.6579 | 28.6232 | 27.6916 | 27.1421 | 26.1379 | 25.1147 | 24.1053 | 23.1337 | 20.4926 | 18.7842 | 17.3105 | 32.5432 | 32.0947 | 31.0779 | 30.1611 | 29.6137 | 28.6242 | 27.6189 | 26.6274 | 25.6716 | 23.1021 | 21.4368 | 20.0021
|  | PARK NORTH PRIMARY | FB |  |  |  |  | 34.5416 | 34.4121 | 34.2963 | 34.1637 | 34.0226 | 33.8784 | 33.7321 | 33.5942 | 33.21 | 31.1995 | 30.0121 | 28.9868 | 30.8632 | 30.4842 | 30.1368 | 29.7358 | 29.3695 | 28.9642 | 28.4958 | 28.0211 | 27.5316 | 25.18 | 23.7968 | 22.6147 | 32.6674 | 32.5568 | 32.4579 | 32.1716 | 31.8105 | 31.4105 | 30.9505 | 30.4832 | 30.0021 | 27.7021 | 26.3505 | 25.1968
WILLESDEN GSP | ACTON LANE BSP | PARK ROYAL PRIMARY | MINIMUM HEADROOM | TQ 20137 82215 | NO | NO | 0 | 11.1747 | 10.6295 | 39.0421 | 39.0253 | 39.0021 | 38.9642 | 38.9042 | 38.8442 | 38.7568 | 38.6105 | 38.4726 | 38.3505 | 13.5789 | 13.5726 | 42.0642 | 42.0537 | 42.0389 | 42.0253 | 41.9516 | 41.8726 | 41.7568 | 41.5653 | 41.3905 | 41.2284 | 12.8368 | 12.7853 | 41.2684 | 41.2589 | 41.2421 | 41.2263 | 41.2095 | 41.1916 | 41.1695 | 41.1495 | 41.16 | 41.1126
|  | PARK ROYAL PRIMARY | EE |  |  |  |  | 11.2 | 11.1863 | 39.0421 | 39.0253 | 39.0021 | 38.9642 | 38.9042 | 38.8442 | 38.7884 | 38.6179 | 38.5663 | 38.4695 | 13.5789 | 13.5726 | 42.0642 | 42.0547 | 42.0389 | 42.0253 | 41.9516 | 41.8726 | 41.7989 | 41.5653 | 41.5053 | 41.3737 | 12.8379 | 12.8305 | 41.2684 | 41.2589 | 41.2421 | 41.2263 | 41.2095 | 41.1937 | 41.1768 | 41.1495 | 41.2063 | 41.1884
|  | PARK ROYAL PRIMARY | HT |  |  |  |  | 11.1747 | 10.6295 | 39.1137 | 39.0947 | 39.0347 | 38.9947 | 38.9347 | 38.8526 | 38.7568 | 38.6105 | 38.4726 | 38.3505 | 13.58 | 13.5737 | 42.0653 | 42.0537 | 42.0411 | 42.0263 | 41.9947 | 41.8842 | 41.7568 | 41.5726 | 41.3905 | 41.2284 | 12.8368 | 12.7853 | 41.2758 | 41.2632 | 41.2474 | 41.2305 | 41.2116 | 41.1916 | 41.1695 | 41.1947 | 41.16 | 41.1126
|  | PARK ROYAL PRIMARY | HE |  |  |  |  | 11.2084 | 11.1979 | 39.0568 | 39.0411 | 39.0221 | 38.9853 | 38.9474 | 38.9095 | 38.8768 | 38.8316 | 38.7726 | 38.7263 | 13.58 | 13.5737 | 42.0663 | 42.0558 | 42.0411 | 42.0274 | 42.0105 | 41.9632 | 41.9221 | 41.8589 | 41.78 | 41.7147 | 12.8389 | 12.8326 | 41.2716 | 41.2611 | 41.2463 | 41.2305 | 41.2147 | 41.1989 | 41.1842 | 41.18 | 41.1705 | 41.1642
|  | PARK ROYAL PRIMARY | FB |  |  |  |  | 11.2147 | 11.2063 | 39.6989 | 39.4295 | 39.42 | 39.4116 | 39.3958 | 39.38 | 39.3663 | 39.2937 | 39.2253 | 39.1568 | 13.5842 | 13.58 | 42.0758 | 42.0716 | 42.0663 | 42.0611 | 42.0558 | 42.0505 | 42.0463 | 42.0274 | 42.0168 | 42.0105 | 12.8442 | 12.8389 | 41.3347 | 41.3084 | 41.3021 | 41.2968 | 41.2905 | 41.2853 | 41.28 | 41.2558 | 41.2411 | 41.2295
MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE NORTH PRIMARY | MINIMUM HEADROOM | SZ 03222 92233 | NO | YES | 0 | 24.2811 | 23.8653 | 22.9758 | 21.7874 | 20.4537 | 18.7284 | 17.0642 | 15.4832 | 13.92 | 10.0021 | 7.4695 | 5.1989 | 22.3558 | 22.0263 | 21.66 | 21.1421 | 20.5032 | 19.1053 | 17.2347 | 15.4632 | 13.7116 | 9.2989 | 6.4358 | 3.8663 | 22.3653 | 22.0358 | 21.6695 | 20.9389 | 19.6621 | 18.0179 | 16.4326 | 14.9242 | 13.4316 | 9.7011 | 7.1779 | 4.6126
|  | PARKSTONE NORTH PRIMARY | EE |  |  |  |  | 24.2811 | 23.8653 | 23.0853 | 22.1811 | 21.1242 | 20.0905 | 19.0811 | 18.2221 | 17.4021 | 15.3011 | 13.5284 | 12.0053 | 22.3558 | 22.0263 | 21.6653 | 21.1789 | 20.5032 | 19.8663 | 19.2842 | 18.6832 | 17.8663 | 15.4179 | 13.3568 | 11.5821 | 22.3653 | 22.0358 | 21.6747 | 21.1884 | 20.2789 | 19.2758 | 18.3 | 17.4621 | 16.6579 | 14.6905 | 13.0242 | 11.5958
|  | PARKSTONE NORTH PRIMARY | HT |  |  |  |  | 24.2989 | 23.8989 | 22.9758 | 21.7874 | 20.4537 | 18.7284 | 17.0642 | 15.4832 | 13.92 | 10.0021 | 7.4695 | 5.1989 | 22.3737 | 22.0642 | 21.66 | 21.1421 | 20.5189 | 19.1053 | 17.2347 | 15.4632 | 13.7116 | 9.2989 | 6.4358 | 3.8663 | 22.3832 | 22.0737 | 21.6695 | 20.9389 | 19.6621 | 18.0179 | 16.4326 | 14.9242 | 13.4316 | 9.7011 | 7.1779 | 4.6126
|  | PARKSTONE NORTH PRIMARY | HE |  |  |  |  | 24.3642 | 24.0526 | 23.7084 | 23.0032 | 22.0189 | 21.0874 | 20.2042 | 19.4747 | 18.7832 | 17.7547 | 16.6484 | 15.6895 | 22.4389 | 22.1274 | 21.7832 | 21.3053 | 20.6337 | 20.0284 | 19.44 | 18.8389 | 18.2495 | 18.2505 | 16.9368 | 15.7937 | 22.4484 | 22.1368 | 21.7926 | 21.3147 | 20.6432 | 20.0379 | 19.3474 | 18.6284 | 17.9453 | 17.0011 | 15.9726 | 15.0832
|  | PARKSTONE NORTH PRIMARY | FB |  |  |  |  | 24.5937 | 24.4411 | 24.3042 | 24.1505 | 23.9021 | 23.5211 | 23.1432 | 22.8674 | 22.5842 | 21.0789 | 19.8621 | 18.8158 | 22.6684 | 22.5158 | 22.3789 | 22.2253 | 22.0547 | 21.8821 | 21.7158 | 21.56 | 21.3937 | 20.7832 | 20.3495 | 19.1295 | 22.6779 | 22.5253 | 22.3884 | 22.2347 | 22.0642 | 21.8916 | 21.7253 | 21.5695 | 21.4032 | 20.2589 | 19.1116 | 18.1305
MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE SOUTH PRIMARY | MINIMUM HEADROOM | SZ 04762 89848 | NO | YES | 0 | 31.6679 | 31.4953 | 31.3026 | 31.0289 | 30.6111 | 29.91 | 29.2268 | 28.4753 | 27.73 | 26.0132 | 24.7721 | 23.6679 | 28.5495 | 28.3884 | 28.2074 | 27.8547 | 27.2579 | 26.46 | 25.6874 | 24.8684 | 24.0558 | 22.1895 | 20.8274 | 19.6147 | 30.2347 | 30.0632 | 29.8063 | 29.2747 | 28.6747 | 27.8705 | 27.0937 | 26.2684 | 25.4505 | 23.5716 | 22.1979 | 20.9758
|  | PARKSTONE SOUTH PRIMARY | EE |  |  |  |  | 31.6679 | 31.4953 | 31.3026 | 31.0511 | 30.7058 | 30.3784 | 30.0426 | 29.6258 | 29.2247 | 28.4216 | 27.55 | 26.8079 | 28.5495 | 28.3884 | 28.2074 | 27.9653 | 27.5789 | 27.1358 | 26.7063 | 26.2589 | 25.8305 | 24.8789 | 23.9032 | 23.0684 | 30.2347 | 30.0632 | 29.8421 | 29.4579 | 29 | 28.5537 | 28.1232 | 27.6747 | 27.2453 | 26.2853 | 25.3 | 24.4568
|  | PARKSTONE SOUTH PRIMARY | HT |  |  |  |  | 31.6847 | 31.5174 | 31.3037 | 31.0289 | 30.6111 | 29.91 | 29.2268 | 28.4753 | 27.73 | 26.0132 | 24.7721 | 23.6679 | 28.5632 | 28.4105 | 28.2116 | 27.8547 | 27.2579 | 26.46 | 25.6874 | 24.8684 | 24.0558 | 22.1895 | 20.8274 | 19.6147 | 30.2505 | 30.0863 | 29.8063 | 29.2747 | 28.6747 | 27.8705 | 27.0937 | 26.2684 | 25.4505 | 23.5716 | 22.1979 | 20.9758
|  | PARKSTONE SOUTH PRIMARY | HE |  |  |  |  | 31.7205 | 31.5553 | 31.3721 | 31.1237 | 30.7753 | 30.4605 | 30.1574 | 29.8437 | 29.5384 | 29.5153 | 29.0216 | 28.6016 | 28.5874 | 28.4284 | 28.2516 | 28.0095 | 27.6663 | 27.3568 | 27.0589 | 26.7505 | 26.4495 | 26.1853 | 25.5768 | 25.0611 | 30.2842 | 30.12 | 29.9379 | 29.6916 | 29.3432 | 29.0295 | 28.7274 | 28.3526 | 27.9895 | 27.6032 | 26.9884 | 26.4674
|  | PARKSTONE SOUTH PRIMARY | FB |  |  |  |  | 31.8395 | 31.7521 | 31.6742 | 31.5868 | 31.4921 | 31.3963 | 31.3026 | 31.2153 | 31.1237 | 30.7732 | 30.25 | 29.7689 | 28.7011 | 28.6211 | 28.5484 | 28.4674 | 28.3779 | 28.2874 | 28.1989 | 28.1168 | 28.0295 | 27.5063 | 26.8316 | 26.2526 | 30.4032 | 30.3158 | 30.2389 | 30.1537 | 30.0589 | 29.9642 | 29.8716 | 29.7853 | 29.64 | 28.9253 | 28.2453 | 27.6611
FLEET-BRAMLEY GSP | WOKINGHAM BSP | PEACOCK FARM PRIMARY | MINIMUM HEADROOM | SU 84770 68709 | NO | YES | 0.053684 | 16.8242 | 16.7716 | 16.6674 | 16.3495 | 16.1305 | 15.9 | 15.7147 | 15.5211 | 15.32 | 14.7874 | 14.38 | 13.9147 | 14.8695 | 14.8095 | 14.7305 | 14.4768 | 14.2253 | 13.9611 | 13.7537 | 13.5358 | 13.3084 | 12.6958 | 12.2158 | 11.6884 | 15.5326 | 15.3979 | 15.1326 | 14.7484 | 14.4958 | 14.2316 | 14.0242 | 13.8053 | 13.5768 | 12.9632 | 12.4821 | 11.9526
|  | PEACOCK FARM PRIMARY | EE |  |  |  |  | 16.8242 | 16.7716 | 16.6758 | 16.4221 | 16.2842 | 16.1474 | 16.0126 | 15.8768 | 15.7453 | 15.4968 | 15.2389 | 14.9442 | 14.8695 | 14.8095 | 14.7305 | 14.5695 | 14.4232 | 14.2779 | 14.1337 | 13.9874 | 13.8463 | 13.5495 | 13.2358 | 12.8716 | 15.5326 | 15.3979 | 15.1453 | 14.8421 | 14.6958 | 14.5495 | 14.4042 | 14.2589 | 14.1179 | 13.8179 | 13.5042 | 13.1389
|  | PEACOCK FARM PRIMARY | HT |  |  |  |  | 16.8274 | 16.7789 | 16.6674 | 16.3495 | 16.1305 | 15.9 | 15.7147 | 15.5211 | 15.32 | 14.7874 | 14.38 | 13.9147 | 14.8747 | 14.8189 | 14.7326 | 14.4768 | 14.2253 | 13.9611 | 13.7537 | 13.5358 | 13.3084 | 12.6958 | 12.2158 | 11.6884 | 15.5568 | 15.4263 | 15.1326 | 14.7484 | 14.4958 | 14.2316 | 14.0242 | 13.8053 | 13.5768 | 12.9632 | 12.4821 | 11.9526
|  | PEACOCK FARM PRIMARY | HE |  |  |  |  | 16.8368 | 16.7874 | 16.7284 | 16.5484 | 16.4211 | 16.2989 | 16.1758 | 16.0568 | 15.9368 | 15.8242 | 15.6558 | 15.4389 | 14.8874 | 14.8337 | 14.7589 | 14.6621 | 14.5526 | 14.4505 | 14.3347 | 14.2105 | 14.0853 | 13.94 | 13.7284 | 13.4547 | 15.6126 | 15.5074 | 15.28 | 14.9989 | 14.8653 | 14.7368 | 14.6074 | 14.4832 | 14.3568 | 14.2116 | 14 | 13.7242
|  | PEACOCK FARM PRIMARY | FB |  |  |  |  | 16.8747 | 16.8505 | 16.8274 | 16.8032 | 16.7758 | 16.7474 | 16.72 | 16.6863 | 16.6379 | 16.4316 | 16.2495 | 16.0621 | 14.9284 | 14.9 | 14.8684 | 14.8358 | 14.8063 | 14.7758 | 14.7453 | 14.7189 | 14.6895 | 14.5779 | 14.3811 | 14.1505 | 15.6779 | 15.6042 | 15.4947 | 15.3747 | 15.3221 | 15.2663 | 15.2126 | 15.1621 | 15.1074 | 14.8716 | 14.6537 | 14.4221
WILLESDEN GSP |  | PERIVALE PRIMARY | MINIMUM HEADROOM | TQ 17544 82947 | NO | NO | 0.19263 | 46.1158 | 45.9968 | 45.8705 | 45.6947 | 45.4611 | 45.2326 | 44.9789 | 44.7221 | 44.1789 | 42.7632 | 41.9537 | 41.2379 | 41.5116 | 41.3958 | 41.2737 | 41.1021 | 40.8705 | 40.6516 | 40.4074 | 40.1621 | 39.9095 | 39.2853 | 38.8905 | 38.0611 | 44.6 | 44.3589 | 44.0989 | 43.7916 | 43.2979 | 42.9263 | 42.34 | 41.6726 | 40.8211 | 39.1116 | 38.1484 | 37.2979
|  | PERIVALE PRIMARY | EE |  |  |  |  | 46.1158 | 45.9968 | 45.8705 | 45.7011 | 45.4611 | 45.2411 | 45.0411 | 44.8242 | 44.6147 | 44.3547 | 43.8505 | 43.3821 | 41.5116 | 41.3958 | 41.2737 | 41.1074 | 40.8705 | 40.6537 | 40.4568 | 40.2463 | 40.0411 | 39.7979 | 39.5905 | 39.4232 | 44.6053 | 44.3589 | 44.1084 | 43.8211 | 43.48 | 43.1379 | 42.78 | 42.4011 | 42.0411 | 41.1684 | 40.4874 | 39.9084
|  | PERIVALE PRIMARY | HT |  |  |  |  | 46.1263 | 46.0168 | 45.8758 | 45.6947 | 45.4695 | 45.2326 | 44.9789 | 44.7221 | 44.1789 | 42.7632 | 41.9537 | 41.2379 | 41.5232 | 41.4168 | 41.28 | 41.1021 | 40.8842 | 40.6516 | 40.4074 | 40.1621 | 39.9095 | 39.2853 | 38.8905 | 38.0611 | 44.6 | 44.3632 | 44.0989 | 43.7916 | 43.2979 | 42.9263 | 42.34 | 41.6726 | 40.8211 | 39.1116 | 38.1484 | 37.2979
|  | PERIVALE PRIMARY | HE |  |  |  |  | 46.1537 | 46.0453 | 45.9284 | 45.7653 | 45.5295 | 45.3221 | 45.12 | 44.9095 | 44.7053 | 44.6726 | 44.5947 | 44.5358 | 41.5463 | 41.44 | 41.3242 | 41.1642 | 40.9295 | 40.7253 | 40.5253 | 40.3179 | 40.1147 | 40.0916 | 40.02 | 39.9674 | 44.7811 | 44.6021 | 44.4126 | 44.1768 | 43.8716 | 43.5726 | 43.2863 | 42.9853 | 42.7011 | 42.3832 | 42.0537 | 41.7705
|  | PERIVALE PRIMARY | FB |  |  |  |  | 46.2253 | 46.1516 | 46.0874 | 46.0158 | 45.9358 | 45.8558 | 45.7779 | 45.7042 | 45.6263 | 45.3337 | 45.1589 | 45.0389 | 41.6126 | 41.5421 | 41.4789 | 41.4084 | 41.3305 | 41.2526 | 41.1768 | 41.1053 | 41.0284 | 40.7453 | 40.58 | 40.4684 | 44.9463 | 44.8453 | 44.7221 | 44.5905 | 44.4484 | 44.3095 | 44.1642 | 44.0274 | 43.8811 | 43.2632 | 42.7811 | 42.3737
FLEET-BRAMLEY GSP | FERNHURST BSP | PETERSFIELD PRIMARY | MINIMUM HEADROOM | SU 74173 23420 | NO | YES | 0.15474 | 35.0953 | 34.8637 | 34.5953 | 33.9184 | 32.8868 | 31.7837 | 30.6942 | 29.5205 | 28.2932 | 25.3416 | 23.3332 | 21.5163 | 28.2505 | 27.7989 | 27.2274 | 26.2147 | 25.0063 | 23.72 | 22.4495 | 21.0684 | 19.6189 | 16.1147 | 13.7116 | 11.5326 | 25.6611 | 25.2284 | 24.6832 | 23.7242 | 22.5811 | 21.3621 | 20.1579 | 18.8526 | 17.4842 | 14.1832 | 11.9242 | 9.8768
|  | PETERSFIELD PRIMARY | EE |  |  |  |  | 35.0953 | 34.8637 | 34.6016 | 34.2574 | 33.7658 | 33.2174 | 32.6353 | 32.0363 | 31.4037 | 29.8921 | 28.4595 | 27.2121 | 28.2505 | 27.7989 | 27.3347 | 26.7747 | 26.1379 | 25.5558 | 24.9232 | 24.2705 | 23.5726 | 21.7158 | 19.9474 | 18.4011 | 25.6611 | 25.2284 | 24.7821 | 24.2411 | 23.62 | 23.0505 | 22.4358 | 21.8021 | 21.1295 | 19.3979 | 17.7526 | 16.3168
|  | PETERSFIELD PRIMARY | HT |  |  |  |  | 35.1132 | 34.8921 | 34.5953 | 33.9184 | 32.8868 | 31.7837 | 30.6942 | 29.5205 | 28.2932 | 25.3416 | 23.3332 | 21.5163 | 28.3442 | 27.92 | 27.2274 | 26.2147 | 25.0063 | 23.72 | 22.4495 | 21.0684 | 19.6189 | 16.1147 | 13.7116 | 11.5326 | 25.7484 | 25.3421 | 24.6832 | 23.7242 | 22.5811 | 21.3621 | 20.1579 | 18.8526 | 17.4842 | 14.1832 | 11.9242 | 9.8768
|  | PETERSFIELD PRIMARY | HE |  |  |  |  | 35.1626 | 34.9479 | 34.7016 | 34.3647 | 33.9153 | 33.4942 | 33.0826 | 32.6658 | 32.2521 | 31.5974 | 30.6289 | 29.7774 | 28.5674 | 28.2368 | 27.8779 | 27.3989 | 26.8168 | 26.3084 | 25.8126 | 25.2947 | 24.7305 | 23.7926 | 22.5695 | 21.4874 | 25.9568 | 25.6358 | 25.2863 | 24.82 | 24.2505 | 23.7495 | 23.26 | 22.7516 | 22.2 | 21.34 | 20.2095 | 19.2126
|  | PETERSFIELD PRIMARY | FB |  |  |  |  | 35.3311 | 35.2195 | 35.1216 | 35.0111 | 34.89 | 34.7689 | 34.6521 | 34.5416 | 34.4237 | 33.6616 | 32.7089 | 31.8711 | 28.8474 | 28.5895 | 28.3947 | 28.1811 | 27.9558 | 27.7421 | 27.5337 | 27.3347 | 27.0979 | 25.9505 | 24.7916 | 23.7568 | 26.2263 | 25.9821 | 25.7958 | 25.5905 | 25.3747 | 25.1684 | 24.9684 | 24.7768 | 24.5505 | 23.4632 | 22.38 | 21.4168
IVER 132KV GSP | CHALVEY BSP | PETERSFIELD AVENUE PRIMARY | MINIMUM HEADROOM | SU 98108 80286 | NO | NO | 0.058947 | 57.3163 | 57.1584 | 56.9774 | 54.7574 | 52.4395 | 50.3542 | 49.1111 | 47.7826 | 46.5679 | 41.0721 | 39.6879 | 38.4637 | 50.2189 | 49.0158 | 47.7368 | 45.8316 | 43.9937 | 41.6863 | 40.2737 | 38.7653 | 37.3958 | 31.0642 | 29.5232 | 28.1611 | 54.9821 | 53.6221 | 51.8126 | 49.0905 | 46.5116 | 44.1937 | 42.8253 | 41.3632 | 40.0074 | 33.6926 | 32.1547 | 30.7958
|  | PETERSFIELD AVENUE PRIMARY | EE |  |  |  |  | 57.3163 | 57.1584 | 56.9774 | 54.7574 | 52.4395 | 50.3542 | 49.1111 | 47.7826 | 46.7742 | 41.8237 | 40.83 | 39.9816 | 50.2189 | 49.6032 | 47.7368 | 45.8316 | 43.9937 | 41.6863 | 40.2737 | 38.7653 | 37.6326 | 31.8463 | 30.7158 | 29.7474 | 54.9821 | 54.5084 | 51.8126 | 49.0905 | 46.5116 | 44.1937 | 42.8253 | 41.3632 | 40.2432 | 34.4737 | 33.3453 | 32.38
|  | PETERSFIELD AVENUE PRIMARY | HT |  |  |  |  | 57.3279 | 57.1816 | 56.9889 | 55.0995 | 53.0363 | 50.8237 | 49.4005 | 47.8163 | 46.5679 | 41.0721 | 39.6879 | 38.4637 | 50.2695 | 49.0158 | 48.0063 | 46.0926 | 44.4547 | 42.2358 | 40.6168 | 38.8084 | 37.3958 | 31.0642 | 29.5232 | 28.1611 | 55.0021 | 53.6221 | 52.2105 | 49.4758 | 47.1811 | 44.7232 | 43.1547 | 41.4053 | 40.0074 | 33.6926 | 32.1547 | 30.7958
|  | PETERSFIELD AVENUE PRIMARY | HE |  |  |  |  | 57.3416 | 57.1826 | 57.0026 | 55.1195 | 52.8321 | 50.7826 | 49.6089 | 48.3511 | 47.4174 | 43.1121 | 42.5163 | 42.0068 | 50.3695 | 49.8032 | 47.9832 | 46.1105 | 44.2958 | 42.1863 | 40.8589 | 39.4347 | 38.3895 | 33.3147 | 32.6221 | 32.0284 | 55.0326 | 54.7916 | 52.1695 | 49.4979 | 46.9537 | 44.6758 | 43.3884 | 42.0074 | 40.9916 | 35.9389 | 35.2484 | 34.6568
|  | PETERSFIELD AVENUE PRIMARY | FB |  |  |  |  | 57.4605 | 57.3805 | 57.3068 | 57.2247 | 57.1342 | 56.4468 | 55.9489 | 55.3774 | 54.9353 | 51.8679 | 51.1953 | 50.6205 | 50.5421 | 50.2263 | 49.7895 | 48.6979 | 48.0011 | 47.1874 | 46.7874 | 46.3347 | 45.9779 | 43.4032 | 42.6442 | 41.9863 | 55.1621 | 55.0347 | 54.7147 | 53.1263 | 52.1316 | 50.9621 | 50.4105 | 49.7747 | 49.2863 | 45.8579 | 45.1211 | 44.4853
MANNINGTON GSP | SALISBURY BSP | PETERSFINGER PRIMARY | MINIMUM HEADROOM | SU 15608 29334 | NO | YES | 0 | 26.4487 | 26.0845 | 25.6708 | 25.1919 | 24.575 | 23.8908 | 23.1824 | 22.475 | 21.794 | 19.9656 | 18.4877 | 17.1592 | 24.5245 | 24.1024 | 23.6235 | 23.0824 | 22.3782 | 21.5961 | 20.7824 | 19.9687 | 19.1877 | 17.0635 | 15.3087 | 13.7277 | 25.375 | 25.0456 | 24.6487 | 24.1119 | 23.4087 | 22.6277 | 21.8161 | 21.0045 | 20.2256 | 18.1045 | 16.354 | 14.7771
|  | PETERSFINGER PRIMARY | EE |  |  |  |  | 26.4487 | 26.0845 | 25.6708 | 25.2382 | 24.7192 | 24.2203 | 23.7287 | 23.2887 | 22.9203 | 22.0592 | 21.0266 | 20.1308 | 24.5245 | 24.1024 | 23.6235 | 23.135 | 22.5613 | 22.0087 | 21.4582 | 20.9729 | 20.5782 | 19.5435 | 18.2835 | 17.1866 | 25.375 | 25.0456 | 24.6487 | 24.1656 | 23.5929 | 23.0403 | 22.4908 | 22.0066 | 21.6119 | 20.5792 | 19.3235 | 18.2287
|  | PETERSFINGER PRIMARY | HT |  |  |  |  | 26.4835 | 26.1645 | 25.7182 | 25.1919 | 24.575 | 23.8908 | 23.1824 | 22.475 | 21.794 | 19.9656 | 18.4877 | 17.1592 | 24.5908 | 24.2003 | 23.6845 | 23.0824 | 22.3782 | 21.5961 | 20.7824 | 19.9687 | 19.1877 | 17.0635 | 15.3087 | 13.7277 | 25.4224 | 25.1161 | 24.7098 | 24.1119 | 23.4087 | 22.6277 | 21.8161 | 21.0045 | 20.2256 | 18.1045 | 16.354 | 14.7771
|  | PETERSFINGER PRIMARY | HE |  |  |  |  | 26.5603 | 26.3508 | 25.9971 | 25.615 | 25.1319 | 24.6792 | 24.2403 | 23.855 | 23.5392 | 23.1382 | 22.3908 | 21.735 | 24.7582 | 24.4256 | 24.0203 | 23.594 | 23.0645 | 22.5656 | 22.0813 | 21.6666 | 21.3382 | 20.8266 | 19.894 | 19.0729 | 25.5445 | 25.2771 | 24.9561 | 24.6003 | 24.0919 | 23.595 | 23.1119 | 22.6982 | 22.3698 | 21.8592 | 20.9298 | 20.1108
|  | PETERSFINGER PRIMARY | FB |  |  |  |  | 26.6845 | 26.5761 | 26.4508 | 26.2813 | 26.1024 | 25.9129 | 25.7245 | 25.5656 | 25.4382 | 24.8245 | 24.1445 | 23.5613 | 24.9529 | 24.7266 | 24.5224 | 24.3256 | 24.1203 | 23.9013 | 23.6824 | 23.5003 | 23.3592 | 22.655 | 21.8361 | 21.1224 | 25.7077 | 25.535 | 25.3792 | 25.2256 | 25.0645 | 24.894 | 24.7077 | 24.5277 | 24.3877 | 23.6866 | 22.8687 | 22.1582
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PEWSEY PRIMARY | MINIMUM HEADROOM | SU 14710 59252 | NO | YES | 0 | 14.2679 | 14.1026 | 13.9332 | 13.7153 | 13.43 | 13.1037 | 12.7658 | 12.3889 | 11.9942 | 10.9216 | 10.0511 | 9.2721 | 11.8484 | 11.6684 | 11.4863 | 11.2537 | 10.9463 | 10.5947 | 10.2284 | 9.8158 | 9.3821 | 8.1895 | 7.2084 | 6.3295 | 11.7189 | 11.5537 | 11.3842 | 11.1663 | 10.8811 | 10.5558 | 10.2168 | 9.8411 | 9.4474 | 8.3758 | 7.5074 | 6.7284
|  | PEWSEY PRIMARY | EE |  |  |  |  | 14.2679 | 14.1026 | 13.9332 | 13.7374 | 13.5068 | 13.2837 | 13.0553 | 12.8289 | 12.6058 | 12.0732 | 11.4479 | 10.9058 | 11.8484 | 11.6684 | 11.4863 | 11.2779 | 11.0379 | 10.8053 | 10.5642 | 10.3253 | 10.0895 | 9.4832 | 8.7653 | 8.1411 | 11.7189 | 11.5537 | 11.3842 | 11.1884 | 10.9579 | 10.7347 | 10.5063 | 10.28 | 10.0568 | 9.5263 | 8.9011 | 8.3611
|  | PEWSEY PRIMARY | HT |  |  |  |  | 14.3026 | 14.1511 | 13.9637 | 13.7153 | 13.43 | 13.1037 | 12.7658 | 12.3889 | 11.9942 | 10.9216 | 10.0511 | 9.2721 | 11.8874 | 11.7242 | 11.5221 | 11.2537 | 10.9463 | 10.5947 | 10.2284 | 9.8158 | 9.3821 | 8.1895 | 7.2084 | 6.3295 | 11.7526 | 11.6021 | 11.4147 | 11.1663 | 10.8811 | 10.5558 | 10.2168 | 9.8411 | 9.4474 | 8.3758 | 7.5074 | 6.7284
|  | PEWSEY PRIMARY | HE |  |  |  |  | 14.3826 | 14.2584 | 14.1268 | 13.9626 | 13.7511 | 13.5574 | 13.37 | 13.1826 | 13.0005 | 12.7721 | 12.3279 | 11.9395 | 11.9789 | 11.8463 | 11.7074 | 11.5368 | 11.3179 | 11.1189 | 10.9253 | 10.7326 | 10.5453 | 10.2747 | 9.7568 | 9.3032 | 11.8326 | 11.7084 | 11.5768 | 11.4137 | 11.2011 | 11.0074 | 10.8211 | 10.6337 | 10.4516 | 10.2232 | 9.78 | 9.3926
|  | PEWSEY PRIMARY | FB |  |  |  |  | 14.4847 | 14.3932 | 14.3237 | 14.2489 | 14.1711 | 14.0921 | 14.0142 | 13.9437 | 13.87 | 13.5163 | 13.11 | 12.7532 | 12.0874 | 11.9863 | 11.9105 | 11.8295 | 11.7453 | 11.66 | 11.5768 | 11.5 | 11.4211 | 11.0326 | 10.5695 | 10.1589 | 11.9347 | 11.8432 | 11.7737 | 11.6989 | 11.6211 | 11.5421 | 11.4653 | 11.3937 | 11.3211 | 10.9684 | 10.5621 | 10.2063
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE PRIMARY | MINIMUM HEADROOM | SY 70169 99809 | NO | YES | 0 | 6.74 | 6.6895 | 6.6242 | 6.5347 | 6.4284 | 6.3095 | 6.1937 | 6.0737 | 5.14 | 2.4747 | 2.2474 | 2.0453 | 6.3632 | 6.3021 | 6.2221 | 6.1137 | 5.9832 | 5.84 | 5.6979 | 5.5505 | 4.4505 | 1.3316 | 1.0758 | 0.84842 | 6.3632 | 6.3021 | 6.2221 | 6.1147 | 5.9842 | 5.8411 | 5.7 | 5.5526 | 4.4558 | 1.3453 | 1.0905 | 0.86421
|  | PIDDLETRENTHIDE PRIMARY | EE |  |  |  |  | 6.74 | 6.6895 | 6.6368 | 6.5726 | 6.4958 | 6.4211 | 6.3453 | 6.2705 | 5.8253 | 4.4768 | 4.3084 | 4.1642 | 6.3632 | 6.3021 | 6.2389 | 6.1642 | 6.0768 | 5.9916 | 5.9053 | 5.8168 | 5.2526 | 3.6695 | 3.4768 | 3.3105 | 6.3632 | 6.3021 | 6.2389 | 6.1653 | 6.0779 | 5.9926 | 5.9063 | 5.8179 | 5.2547 | 3.6768 | 3.4853 | 3.3189
|  | PIDDLETRENTHIDE PRIMARY | HT |  |  |  |  | 6.7463 | 6.6937 | 6.6242 | 6.5347 | 6.4284 | 6.3095 | 6.1937 | 6.0737 | 5.14 | 2.4747 | 2.2474 | 2.0453 | 6.3705 | 6.3063 | 6.2221 | 6.1137 | 5.9832 | 5.84 | 5.6979 | 5.5505 | 4.4505 | 1.3316 | 1.0758 | 0.84842 | 6.3705 | 6.3074 | 6.2221 | 6.1147 | 5.9842 | 5.8411 | 5.7 | 5.5526 | 4.4558 | 1.3453 | 1.0905 | 0.86421
|  | PIDDLETRENTHIDE PRIMARY | HE |  |  |  |  | 6.7705 | 6.7316 | 6.6874 | 6.6337 | 6.5621 | 6.4979 | 6.4358 | 6.3705 | 5.9547 | 4.7042 | 4.5947 | 4.4979 | 6.4021 | 6.3568 | 6.3053 | 6.2432 | 6.1642 | 6.0916 | 6.0211 | 5.9484 | 5.4011 | 3.9263 | 3.7989 | 3.6863 | 6.4021 | 6.3568 | 6.3053 | 6.2432 | 6.1653 | 6.0926 | 6.0221 | 5.9495 | 5.4032 | 3.9326 | 3.8063 | 3.6937
|  | PIDDLETRENTHIDE PRIMARY | FB |  |  |  |  | 6.7979 | 6.7737 | 6.7516 | 6.7295 | 6.7053 | 6.6789 | 6.6526 | 6.6284 | 6.6032 | 6.4947 | 6.4 | 6.3211 | 6.4337 | 6.4032 | 6.3768 | 6.3505 | 6.32 | 6.2884 | 6.2568 | 6.2274 | 6.1968 | 6.0621 | 5.94 | 5.8347 | 6.4337 | 6.4032 | 6.3768 | 6.3505 | 6.3211 | 6.2884 | 6.2568 | 6.2274 | 6.1979 | 6.0621 | 5.9411 | 5.8358
FLEET-BRAMLEY GSP | FERNHURST BSP | PLAISTOW PRIMARY | MINIMUM HEADROOM | TQ 02071 29626 | NO | YES | 0 | 14.7792 | 28.75 | 28.5205 | 28.2595 | 27.9479 | 27.6616 | 27.3742 | 27.0658 | 24.9216 | 16.9732 | 10.5889 | 7.53 | 13.7184 | 26.8505 | 26.6063 | 26.3126 | 25.9726 | 25.6579 | 25.3421 | 24.9989 | 22.4905 | 13.1726 | 5.6653 | 2.0832 | 14.0589 | 27.6411 | 27.3968 | 27.1189 | 26.7895 | 26.4874 | 26.1842 | 25.8568 | 23.5221 | 14.24 | 6.7432 | 3.1642
|  | PLAISTOW PRIMARY | EE |  |  |  |  | 14.7792 | 28.75 | 28.5205 | 28.2858 | 28.0405 | 27.8195 | 27.5668 | 27.2963 | 26.1458 | 22.2574 | 19.6816 | 16.3858 | 13.7184 | 26.8505 | 26.6063 | 26.3579 | 26.1042 | 25.8737 | 25.6084 | 25.3253 | 23.9989 | 19.4705 | 16.4747 | 12.6126 | 14.0589 | 27.6411 | 27.3968 | 27.1474 | 26.8926 | 26.66 | 26.3947 | 26.1095 | 24.8611 | 20.5074 | 17.5 | 13.6347
|  | PLAISTOW PRIMARY | HT |  |  |  |  | 14.8424 | 28.8163 | 28.5647 | 28.2595 | 27.9479 | 27.6616 | 27.3742 | 27.0658 | 24.9216 | 16.9732 | 10.5889 | 7.53 | 13.7858 | 26.9189 | 26.6453 | 26.3126 | 25.9726 | 25.6579 | 25.3421 | 24.9989 | 22.4905 | 13.1726 | 5.6653 | 2.0832 | 14.1263 | 27.7126 | 27.4453 | 27.1189 | 26.7895 | 26.4874 | 26.1842 | 25.8568 | 23.5221 | 14.24 | 6.7432 | 3.1642
|  | PLAISTOW PRIMARY | HE |  |  |  |  | 15.0055 | 29.1016 | 29.01 | 28.9037 | 28.7732 | 28.6532 | 28.5311 | 28.4079 | 27.3637 | 23.9763 | 21.7426 | 18.7047 | 13.9605 | 27.2263 | 27.1295 | 27.0168 | 26.8832 | 26.7589 | 26.6337 | 26.5063 | 25.2905 | 21.2937 | 18.6611 | 15.08 | 14.3032 | 28.0211 | 27.9274 | 27.8179 | 27.6853 | 27.5632 | 27.4389 | 27.3137 | 26.18 | 22.3884 | 19.7547 | 16.1716
|  | PLAISTOW PRIMARY | FB |  |  |  |  | 15.0676 | 29.1868 | 29.1405 | 29.0942 | 29.0458 | 28.9974 | 28.95 | 28.9047 | 28.8532 | 27.7942 | 25.5353 | 22.8795 | 14.0268 | 27.3147 | 27.2642 | 27.2137 | 27.1611 | 27.1095 | 27.0579 | 27.0095 | 26.9526 | 25.72 | 23.0653 | 19.9368 | 14.3674 | 28.1084 | 28.06 | 28.0116 | 27.9611 | 27.9105 | 27.8611 | 27.8137 | 27.76 | 26.6105 | 24.1453 | 21.0305
MINETY GSP | STRATTON (MAIN) BSP | PLESSEY PRIMARY | MINIMUM HEADROOM | SU 16381 86720 | NO | YES | 0 | 17.0958 | 16.8484 | 16.5432 | 16.3095 | 15.7947 | 15.0958 | 14.1116 | 13.1147 | 11.5189 | 9.7032 | 8.7368 | 7.7758 | 15.9526 | 15.66 | 15.3053 | 15.0484 | 14.4463 | 13.6116 | 12.4084 | 11.1905 | 9.1611 | 6.8874 | 5.6926 | 4.4937 | 16.5147 | 16.2432 | 15.8895 | 15.6326 | 15.0305 | 14.1979 | 12.9968 | 11.78 | 9.7537 | 7.4853 | 6.2916 | 5.0947
|  | PLESSEY PRIMARY | EE |  |  |  |  | 17.0958 | 16.8968 | 16.5432 | 16.3095 | 16.0337 | 15.5611 | 14.8379 | 13.9674 | 11.5189 | 9.7032 | 8.7368 | 7.7758 | 15.9526 | 15.7274 | 15.3053 | 15.0484 | 14.7516 | 14.1989 | 13.3211 | 12.2558 | 9.1611 | 6.8874 | 5.6926 | 4.4937 | 16.5147 | 16.3105 | 15.8895 | 15.6326 | 15.3358 | 14.7842 | 13.9074 | 12.8432 | 9.7537 | 7.4853 | 6.2916 | 5.0947
|  | PLESSEY PRIMARY | HT |  |  |  |  | 17.1442 | 16.8484 | 16.6379 | 16.3926 | 15.7947 | 15.0958 | 14.1116 | 13.1147 | 12.2853 | 11.0495 | 9.7126 | 8.3842 | 16.0105 | 15.66 | 15.4253 | 15.1589 | 14.4463 | 13.6116 | 12.4084 | 11.1905 | 10.1853 | 8.7432 | 7.1168 | 5.4895 | 16.5484 | 16.2432 | 16.0084 | 15.7421 | 15.0305 | 14.1979 | 12.9968 | 11.78 | 10.7758 | 9.3358 | 7.7126 | 6.0874
|  | PLESSEY PRIMARY | HE |  |  |  |  | 17.2463 | 17.1063 | 16.7979 | 16.6011 | 16.3495 | 15.8947 | 15.2084 | 14.3621 | 11.9389 | 10.6011 | 9.8768 | 9.1253 | 16.1347 | 15.9789 | 15.6137 | 15.4021 | 15.1347 | 14.6053 | 13.7747 | 12.74 | 9.6779 | 7.9768 | 7.0642 | 6.1105 | 16.62 | 16.5021 | 16.1968 | 15.9863 | 15.7189 | 15.1895 | 14.36 | 13.3263 | 10.2705 | 8.5716 | 7.6611 | 6.7095
|  | PLESSEY PRIMARY | FB |  |  |  |  | 17.4095 | 17.2358 | 17.1453 | 16.9863 | 16.8821 | 16.7758 | 16.5779 | 16.3158 | 16.0305 | 14.4042 | 13.7632 | 13.1695 | 17.5947 | 16.1189 | 16.0158 | 15.8263 | 15.7095 | 15.5905 | 15.3537 | 15.0305 | 14.6811 | 12.6495 | 11.86 | 11.1179 | 16.8558 | 16.6168 | 16.5442 | 16.4095 | 16.2926 | 16.1737 | 15.9368 | 15.6147 | 15.2663 | 13.2379 | 12.4495 | 11.7084
LOVEDEAN GSP | FAREHAM (MAIN) BSP | PLESSEY TITCHFIELD PRIMARY | MINIMUM HEADROOM | SU 53390 06922 | NO | YES | 0 | 34.7947 | 34.6021 | 34.3632 | 34.0884 | 33.7558 | 33.4611 | 33.1453 | 32.8284 | 32.5116 | 31.7158 | 30.9884 | 30.1021 | 33.3474 | 33.1674 | 32.9421 | 32.6211 | 32.2232 | 31.9105 | 31.5547 | 31.1947 | 30.8337 | 29.8958 | 29.2232 | 28.2684 | 33.7084 | 33.5242 | 33.2926 | 33.02 | 32.4074 | 31.8632 | 31.3779 | 30.8726 | 30.3632 | 28.9579 | 27.8611 | 26.8747
|  | PLESSEY TITCHFIELD PRIMARY | EE |  |  |  |  | 34.7947 | 34.6305 | 34.4084 | 34.1537 | 33.8737 | 33.6042 | 33.3516 | 33.1621 | 32.9147 | 32.6189 | 32.3253 | 32.0789 | 33.3474 | 33.1884 | 32.9811 | 32.7168 | 32.4189 | 32.1305 | 31.8589 | 31.7011 | 31.4368 | 31.0463 | 30.6453 | 30.3042 | 33.7084 | 33.5474 | 33.3347 | 33.0874 | 32.8095 | 32.5116 | 32.1737 | 31.9495 | 31.6295 | 30.9274 | 30.1705 | 29.5137
|  | PLESSEY TITCHFIELD PRIMARY | HT |  |  |  |  | 34.8042 | 34.6021 | 34.3632 | 34.0884 | 33.7558 | 33.4611 | 33.1453 | 32.8284 | 32.5116 | 31.7158 | 30.9884 | 30.1021 | 33.3547 | 33.1674 | 32.9421 | 32.6211 | 32.2232 | 31.9105 | 31.5547 | 31.1947 | 30.8337 | 29.8958 | 29.2232 | 28.2684 | 33.7168 | 33.5242 | 33.2926 | 33.02 | 32.4074 | 31.8632 | 31.3779 | 30.8726 | 30.3632 | 28.9579 | 27.8611 | 26.8747
|  | PLESSEY TITCHFIELD PRIMARY | HE |  |  |  |  | 34.8568 | 34.7232 | 34.5284 | 34.2947 | 34.0326 | 33.7884 | 33.5495 | 33.3147 | 33.0821 | 33.0568 | 32.9568 | 32.8663 | 33.4074 | 33.2726 | 33.0884 | 32.8653 | 32.6053 | 32.3642 | 32.1284 | 31.8884 | 31.6463 | 31.5863 | 31.4368 | 31.2937 | 33.7716 | 33.6358 | 33.4474 | 33.22 | 32.9589 | 32.7168 | 32.48 | 32.2463 | 32.0147 | 31.9747 | 31.6611 | 31.3453
|  | PLESSEY TITCHFIELD PRIMARY | FB |  |  |  |  | 34.9537 | 34.8916 | 34.8263 | 34.7337 | 34.6411 | 34.5642 | 34.4884 | 34.4158 | 34.3421 | 34.06 | 33.8705 | 33.7211 | 33.5147 | 33.4389 | 33.3758 | 33.2895 | 33.2011 | 33.1274 | 33.0547 | 32.9842 | 32.9126 | 32.6347 | 32.3989 | 32.1979 | 33.8789 | 33.8021 | 33.7379 | 33.6495 | 33.56 | 33.4842 | 33.4105 | 33.34 | 33.2674 | 32.9916 | 32.7832 | 32.4158
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | POOLE PRIMARY | MINIMUM HEADROOM | SZ 01091 90595 | NO | YES | 0 | 30.1537 | 41.8874 | 41.8095 | 41.6989 | 40.8589 | 40.2116 | 39.7284 | 39.1832 | 38.6284 | 35.5642 | 34.6 | 33.8989 | 29.3432 | 38.7274 | 38.3158 | 37.2958 | 36.2484 | 35.52 | 34.9832 | 34.3726 | 33.7526 | 30.2526 | 29.1705 | 28.3895 | 25.5989 | 36.0747 | 35.6884 | 34.7326 | 33.7495 | 33.0621 | 32.5516 | 31.9747 | 31.3874 | 28.1084 | 27.0863 | 26.3463
|  | POOLE PRIMARY | EE |  |  |  |  | 30.1537 | 41.8874 | 41.8158 | 41.7168 | 41.0189 | 40.5358 | 40.1621 | 39.7811 | 39.4053 | 36.7232 | 35.9263 | 35.4011 | 29.3432 | 38.7274 | 38.3537 | 37.4084 | 36.4347 | 35.8947 | 35.4821 | 35.0611 | 34.6453 | 31.5516 | 30.6453 | 30.0505 | 25.5989 | 36.0747 | 35.7221 | 34.8368 | 33.9221 | 33.4105 | 33.0179 | 32.6168 | 32.22 | 29.3368 | 28.4863 | 27.9274
|  | POOLE PRIMARY | HT |  |  |  |  | 30.1579 | 41.8958 | 41.8158 | 41.7095 | 40.8589 | 40.2116 | 39.7284 | 39.1832 | 38.6284 | 35.5642 | 34.6 | 33.8989 | 29.3484 | 38.7284 | 38.3158 | 37.2958 | 36.2484 | 35.52 | 34.9832 | 34.3726 | 33.7526 | 30.2526 | 29.1705 | 28.3895 | 25.6179 | 36.0768 | 35.6884 | 34.7326 | 33.7495 | 33.0621 | 32.5516 | 31.9747 | 31.3874 | 28.1084 | 27.0863 | 26.3463
|  | POOLE PRIMARY | HE |  |  |  |  | 30.16 | 41.8884 | 41.8095 | 41.6989 | 41.1495 | 40.6758 | 40.3653 | 40.0463 | 39.7337 | 37.5011 | 36.9495 | 36.6389 | 29.3537 | 38.8421 | 38.4905 | 37.5589 | 36.5916 | 36.0642 | 35.7253 | 35.3768 | 35.0358 | 32.4463 | 31.8126 | 31.4568 | 25.68 | 36.1821 | 35.8495 | 34.9758 | 34.0663 | 33.5653 | 33.24 | 32.9074 | 32.5811 | 30.1726 | 29.58 | 29.2474
|  | POOLE PRIMARY | FB |  |  |  |  | 30.2063 | 41.9653 | 41.9295 | 41.8884 | 41.8432 | 41.7979 | 41.7537 | 41.7116 | 41.6684 | 40.2947 | 39.7863 | 39.4284 | 29.4074 | 38.9589 | 38.9147 | 38.5789 | 38.1884 | 37.9526 | 37.7916 | 37.6253 | 37.4484 | 35.6063 | 35.0305 | 34.6253 | 25.8463 | 36.4705 | 36.3095 | 35.9368 | 35.5716 | 35.3484 | 35.1958 | 35.0379 | 34.8716 | 33.1463 | 32.6053 | 32.2232
LOVEDEAN GSP | PORTSMOUTH BSP | PORTCHESTER PRIMARY | MINIMUM HEADROOM | SU 62043 05575 | NO | YES | 0.042105 | 31.9732 | 31.5974 | 30.8005 | 29.8921 | 28.8195 | 27.6647 | 26.2205 | 24.7626 | 23.2984 | 19.7837 | 18.1174 | 16.6384 | 29.8147 | 29.3105 | 28.4979 | 27.5716 | 26.4789 | 25.3032 | 23.8168 | 22.0705 | 20.3168 | 16.0989 | 14.1442 | 12.4053 | 26.5137 | 25.9411 | 25.0063 | 23.9505 | 22.7074 | 21.3716 | 19.6674 | 17.9432 | 16.2105 | 12.0463 | 10.1126 | 8.3937
|  | PORTCHESTER PRIMARY | EE |  |  |  |  | 31.9732 | 31.6479 | 30.9847 | 30.3068 | 29.5005 | 28.7195 | 27.9574 | 26.7363 | 25.5268 | 22.5079 | 21.3942 | 20.45 | 29.8147 | 29.3642 | 28.6874 | 28 | 27.1821 | 26.3905 | 25.6168 | 24.3705 | 23.1368 | 19.3411 | 17.9842 | 16.8284 | 26.5137 | 26.0105 | 25.2379 | 24.4705 | 23.5726 | 22.7011 | 21.8453 | 20.4105 | 18.9895 | 15.2484 | 13.9105 | 12.7705
|  | PORTCHESTER PRIMARY | HT |  |  |  |  | 31.9995 | 31.5974 | 30.8005 | 29.8921 | 28.8195 | 27.6647 | 26.2205 | 24.7626 | 23.2984 | 19.7837 | 18.1174 | 16.6384 | 29.8758 | 29.3105 | 28.4979 | 27.5716 | 26.4789 | 25.3032 | 23.8168 | 22.0705 | 20.3168 | 16.0989 | 14.1442 | 12.4053 | 26.5853 | 25.9411 | 25.0063 | 23.9505 | 22.7074 | 21.3716 | 19.6674 | 17.9432 | 16.2105 | 12.0463 | 10.1126 | 8.3937
|  | PORTCHESTER PRIMARY | HE |  |  |  |  | 32.0974 | 31.8479 | 31.4595 | 30.8605 | 30.1121 | 29.4047 | 28.7111 | 27.8384 | 26.9816 | 24.8037 | 23.7268 | 23.2658 | 30.0947 | 29.7547 | 29.1747 | 28.5663 | 27.8095 | 27.0926 | 26.3905 | 25.5032 | 24.6326 | 22.1547 | 20.7853 | 20.2032 | 26.8453 | 26.4747 | 25.8168 | 25.1442 | 24.3179 | 23.5316 | 22.7621 | 21.7674 | 20.7905 | 18.0242 | 16.6768 | 16.1032
|  | PORTCHESTER PRIMARY | FB |  |  |  |  | 32.29 | 32.1416 | 32.0047 | 31.8489 | 31.6111 | 31.3237 | 31.0289 | 30.7289 | 30.3142 | 28.3458 | 27.11 | 26.5447 | 30.3589 | 30.1137 | 29.8811 | 29.6137 | 29.3242 | 29.0326 | 28.7316 | 28.4253 | 28.0011 | 25.9842 | 24.7032 | 24.0168 | 27.1337 | 26.8547 | 26.5916 | 26.2863 | 25.9589 | 25.6263 | 25.2832 | 24.9316 | 24.4368 | 22.0568 | 20.5547 | 19.8768
CHICKERELL GSP | CHICKERELL BSP | PORTLAND PRIMARY | MINIMUM HEADROOM | SY 68307 73941 | NO | YES | 0 | 21.8895 | 21.7516 | 21.5989 | 21.3611 | 20.7453 | 19.9663 | 19.1853 | 18.3768 | 17.5642 | 15.4958 | 14.0895 | 12.8126 | 19.4326 | 19.1021 | 18.6379 | 17.9853 | 17.1947 | 16.3295 | 15.4653 | 14.5653 | 13.6611 | 11.3495 | 9.7726 | 8.3411 | 21.0853 | 20.7484 | 20.2737 | 19.6063 | 18.7979 | 17.9147 | 17.0326 | 16.1126 | 15.1884 | 12.8242 | 11.2105 | 9.7432
|  | PORTLAND PRIMARY | EE |  |  |  |  | 21.8895 | 21.7516 | 21.5989 | 21.3789 | 21.0768 | 20.7968 | 20.3474 | 19.8726 | 19.4084 | 18.2189 | 17.1695 | 16.2484 | 19.4326 | 19.1021 | 18.7453 | 18.3242 | 17.8137 | 17.3316 | 16.8221 | 16.3095 | 15.8074 | 14.4537 | 13.2579 | 12.2084 | 21.0853 | 20.7484 | 20.3832 | 19.9568 | 19.4389 | 18.9505 | 18.4316 | 17.9116 | 17.4011 | 16.0116 | 14.7842 | 13.7053
|  | PORTLAND PRIMARY | HT |  |  |  |  | 21.9032 | 21.78 | 21.6032 | 21.3611 | 20.7453 | 19.9663 | 19.1853 | 18.3768 | 17.5642 | 15.4958 | 14.0895 | 12.8126 | 19.4789 | 19.1232 | 18.6379 | 17.9853 | 17.1947 | 16.3295 | 15.4653 | 14.5653 | 13.6611 | 11.3495 | 9.7726 | 8.3411 | 21.1326 | 20.7684 | 20.2737 | 19.6063 | 18.7979 | 17.9147 | 17.0326 | 16.1126 | 15.1884 | 12.8242 | 11.2105 | 9.7432
|  | PORTLAND PRIMARY | HE |  |  |  |  | 21.9189 | 21.7842 | 21.6421 | 21.44 | 21.1379 | 20.8684 | 20.6074 | 20.34 | 20.0011 | 19.38 | 18.6642 | 18.0305 | 19.6221 | 19.3611 | 19.0653 | 18.6937 | 18.2116 | 17.7737 | 17.3442 | 16.9158 | 16.4958 | 15.7663 | 14.9379 | 14.2053 | 21.1589 | 21.0147 | 20.7137 | 20.3368 | 19.8484 | 19.4053 | 18.9705 | 18.5358 | 18.1105 | 17.3568 | 16.5053 | 15.7495
|  | PORTLAND PRIMARY | FB |  |  |  |  | 22.0137 | 21.9463 | 21.8853 | 21.8179 | 21.7421 | 21.6663 | 21.5863 | 21.5074 | 21.4242 | 21.0337 | 20.3611 | 19.7653 | 19.7989 | 19.6168 | 19.4611 | 19.2937 | 19.1084 | 18.9232 | 18.7337 | 18.5484 | 18.3579 | 17.5284 | 16.7684 | 16.0884 | 21.2589 | 21.1842 | 21.1147 | 20.9442 | 20.7558 | 20.5663 | 20.3737 | 20.1842 | 19.9895 | 19.1432 | 18.3642 | 17.6653
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH PRIMARY | MINIMUM HEADROOM | SZ 63405 99685 | NO | YES | 0 | 37.5777 | 37.4693 | 37.0682 | 36.5493 | 35.964 | 35.7356 | 35.5029 | 35.2535 | 35.0008 | 34.2419 | 33.6535 | 33.1261 | 41.5798 | 41.5103 | 41.4082 | 41.0682 | 40.1587 | 39.8672 | 39.5703 | 39.2429 | 38.9135 | 37.8724 | 37.0398 | 36.2945 | 40.8629 | 40.7335 | 40.1851 | 39.4766 | 38.6798 | 38.4103 | 38.1366 | 37.8366 | 37.5345 | 36.5945 | 35.8482 | 35.1798
|  | PORTSMOUTH PRIMARY | EE |  |  |  |  | 37.5777 | 37.4693 | 37.0808 | 36.6114 | 36.0472 | 35.8945 | 35.7272 | 35.5577 | 35.3882 | 35.0187 | 34.5935 | 34.2303 | 41.5798 | 41.5166 | 41.4261 | 41.1587 | 40.2882 | 40.1156 | 39.9156 | 39.7135 | 39.5124 | 38.9766 | 38.3387 | 37.7872 | 40.8629 | 40.7335 | 40.1987 | 39.5556 | 38.7945 | 38.6282 | 38.4398 | 38.2493 | 38.0598 | 37.5819 | 37.0198 | 36.5345
|  | PORTSMOUTH PRIMARY | HT |  |  |  |  | 37.5893 | 37.484 | 37.0682 | 36.5493 | 35.964 | 35.7356 | 35.5029 | 35.2535 | 35.0008 | 34.2419 | 33.6535 | 33.1261 | 41.5798 | 41.5187 | 41.4145 | 41.0682 | 40.1587 | 39.8672 | 39.5703 | 39.2429 | 38.9135 | 37.8724 | 37.0398 | 36.2945 | 40.8819 | 40.7545 | 40.1851 | 39.4766 | 38.6798 | 38.4103 | 38.1366 | 37.8366 | 37.5345 | 36.5945 | 35.8482 | 35.1798
|  | PORTSMOUTH PRIMARY | HE |  |  |  |  | 37.6187 | 37.5208 | 37.1366 | 36.6672 | 36.0935 | 35.9408 | 35.7893 | 35.6356 | 35.4851 | 35.3998 | 36.0608 | 35.8377 | 41.5808 | 41.5103 | 41.4082 | 41.2756 | 40.4072 | 40.2419 | 40.0787 | 39.9124 | 39.7503 | 39.6072 | 40.6598 | 40.3008 | 40.924 | 40.8135 | 40.2903 | 39.6556 | 38.8872 | 38.7272 | 38.5672 | 38.4061 | 38.2482 | 38.1251 | 39.3251 | 39.0145
|  | PORTSMOUTH PRIMARY | FB |  |  |  |  | 37.6819 | 37.6093 | 37.4282 | 37.2261 | 36.9977 | 36.9261 | 36.8619 | 36.8008 | 36.7345 | 36.4724 | 36.2387 | 35.9987 | 41.6272 | 41.5819 | 41.5335 | 41.4798 | 41.4187 | 41.3682 | 41.3219 | 41.2766 | 41.2293 | 41.0524 | 40.7777 | 40.4135 | 40.9966 | 40.9093 | 40.664 | 40.3882 | 40.0777 | 39.9966 | 39.924 | 39.8535 | 39.7787 | 39.4735 | 39.1787 | 38.8577
MELKSHAM GSP | ANDOVER BSP | PORTWAY PRIMARY | MINIMUM HEADROOM | SU 34402 46001 | NO | YES | 8.4758 | 23.7237 | 23.5616 | 23.3974 | 23.2079 | 22.9774 | 22.7605 | 22.5247 | 20.9374 | 19.7616 | 20.1542 | 19.3574 | 18.5658 | 21.7916 | 21.6137 | 21.4347 | 21.2316 | 20.9895 | 20.7611 | 20.5074 | 18.6337 | 17.2674 | 18.0716 | 17.3695 | 16.4768 | 22.7305 | 22.5537 | 22.3758 | 22.1737 | 21.9316 | 21.7032 | 21.4495 | 19.5789 | 18.2147 | 19.0179 | 18.3579 | 17.6358
|  | PORTWAY PRIMARY | EE |  |  |  |  | 23.7237 | 23.5616 | 23.3974 | 23.2079 | 22.9774 | 22.7605 | 22.5247 | 21.6132 | 20.9268 | 20.4353 | 19.8605 | 20.4616 | 21.7916 | 21.6137 | 21.4347 | 21.2316 | 20.9895 | 20.7611 | 20.5074 | 19.4379 | 18.6411 | 18.0716 | 17.4105 | 18.5958 | 22.7305 | 22.5537 | 22.3758 | 22.1737 | 21.9316 | 21.7032 | 21.4495 | 20.3811 | 19.5853 | 19.0179 | 18.3579 | 19.7558
|  | PORTWAY PRIMARY | HT |  |  |  |  | 23.7553 | 23.6089 | 23.4405 | 23.2458 | 23.0289 | 22.7816 | 22.5405 | 20.9374 | 19.7616 | 20.1542 | 19.3574 | 18.5658 | 21.8284 | 21.6684 | 21.4863 | 21.28 | 21.0526 | 20.7895 | 20.5347 | 18.6337 | 17.2674 | 18.2621 | 17.3695 | 16.4768 | 22.7663 | 22.6074 | 22.4274 | 22.2221 | 21.9937 | 21.7316 | 21.4768 | 19.5789 | 18.2147 | 19.4221 | 18.5284 | 17.6358
|  | PORTWAY PRIMARY | HE |  |  |  |  | 23.8342 | 23.7153 | 23.5847 | 23.4247 | 23.2132 | 23.0216 | 22.8363 | 21.9763 | 21.3405 | 21.2047 | 20.8426 | 21.6321 | 21.92 | 21.7926 | 21.6526 | 21.4853 | 21.2663 | 21.0663 | 20.8747 | 19.8663 | 19.1295 | 18.9642 | 18.5347 | 19.9168 | 22.8568 | 22.7305 | 22.5916 | 22.4253 | 22.2063 | 22.0074 | 21.8158 | 20.8105 | 20.0737 | 19.9095 | 19.48 | 21.0768
|  | PORTWAY PRIMARY | FB |  |  |  |  | 23.93 | 23.8416 | 23.7721 | 23.6984 | 23.6195 | 23.5426 | 23.4658 | 23.3921 | 23.3163 | 23.0079 | 22.6426 | 22.2826 | 22.0232 | 21.9242 | 21.8484 | 21.7674 | 21.6821 | 21.5979 | 21.5137 | 21.4326 | 21.3495 | 21.0095 | 20.5853 | 20.1621 | 22.96 | 22.8621 | 22.7863 | 22.7063 | 22.6211 | 22.5368 | 22.4537 | 22.3737 | 22.2905 | 21.9516 | 21.5284 | 21.1053
IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY | MINIMUM HEADROOM | TQ 03425 75555 | NO | NO | 0 | 35.0563 | 34.9689 | 34.8616 | 34.7184 | 34.5447 | 34.3563 | 33.9195 | 33.4079 | 33.0342 | 27.1658 | 31.4468 | 31.13 | 31.0863 | 30.6232 | 30.4347 | 30.1263 | 29.76 | 29.3505 | 28.8379 | 28.2621 | 27.8505 | 20.8968 | 25.8 | 25.4316 | 33.6463 | 33.3895 | 33.2011 | 32.8916 | 32.5232 | 32.1137 | 31.6 | 31.0221 | 30.6095 | 23.6284 | 28.5474 | 28.1779
|  | POYLE PRIMARY | EE |  |  |  |  | 35.0563 | 34.9689 | 34.8658 | 34.7268 | 34.5458 | 34.3647 | 34.0668 | 33.6574 | 33.4058 | 31.6847 | 64.2395 | 63.8005 | 31.0863 | 30.6232 | 30.4347 | 30.1379 | 29.7968 | 29.4589 | 29.0074 | 28.5505 | 28.2821 | 26.2453 | 58.5958 | 58.0874 | 33.6463 | 33.3895 | 33.2011 | 32.9042 | 32.5621 | 32.2232 | 31.7705 | 31.3105 | 31.0421 | 28.9968 | 61.3432 | 60.8326
|  | POYLE PRIMARY | HT |  |  |  |  | 35.0584 | 34.9753 | 34.8616 | 34.7184 | 34.5447 | 34.3563 | 33.9195 | 33.4079 | 33.0342 | 27.1658 | 60.1016 | 59.4321 | 31.1189 | 30.6684 | 30.4463 | 30.1263 | 29.76 | 29.3505 | 28.8379 | 28.2621 | 27.8505 | 20.8968 | 53.74 | 52.9863 | 33.6484 | 33.4358 | 33.2126 | 32.8916 | 32.5232 | 32.1137 | 31.6 | 31.0221 | 30.6095 | 23.6284 | 56.4695 | 55.7126
|  | POYLE PRIMARY | HE |  |  |  |  | 35.0721 | 34.9868 | 34.8868 | 34.7511 | 34.5668 | 34.3953 | 34.2247 | 34.0195 | 33.8174 | 32.4647 | 65.2511 | 65.0068 | 31.2116 | 30.7937 | 30.6474 | 30.3884 | 30.0653 | 29.7611 | 29.3695 | 28.9789 | 28.7705 | 27.1463 | 59.7558 | 59.4674 | 33.6621 | 33.5611 | 33.4147 | 33.1547 | 32.8316 | 32.5263 | 32.1347 | 31.7432 | 31.5337 | 29.9021 | 62.5074 | 62.2168
|  | POYLE PRIMARY | FB |  |  |  |  | 35.1426 | 35.0995 | 35.0595 | 35.0163 | 34.9689 | 34.9195 | 34.8732 | 34.8289 | 34.7816 | 34.61 | 31.4468 | 31.13 | 31.3284 | 31.1326 | 31.0505 | 30.9326 | 30.8063 | 30.6737 | 30.5 | 30.3158 | 30.2253 | 29.8526 | 25.8 | 25.4316 | 33.7326 | 33.6895 | 33.6495 | 33.6063 | 33.5589 | 33.4411 | 33.2663 | 33.0821 | 32.9905 | 32.6179 | 28.5474 | 28.1779
MINETY GSP | STRATTON (MAIN) BSP | PRESSED STEEL SWINDON PRIMARY | MINIMUM HEADROOM | SU 16963 86368 | NO | YES | 0 | 42.6726 | 87.0463 | 86.8779 | 86.6768 | 86.4179 | 85.8579 | 84.9895 | 84.1011 | 83.3537 | 82.1926 | 81.1863 | 80.2379 | 40.7579 | 79.4674 | 79.0789 | 78.6568 | 78.2253 | 77.5253 | 76.5474 | 75.5421 | 74.7053 | 73.4411 | 72.3168 | 71.2526 | 40.7579 | 82.1747 | 81.7926 | 81.3779 | 80.9505 | 80.2621 | 79.3021 | 78.3179 | 77.4958 | 76.2495 | 75.1453 | 74.1
|  | PRESSED STEEL SWINDON PRIMARY | EE |  |  |  |  | 42.6726 | 87.0474 | 86.8895 | 86.7042 | 86.4716 | 86.1747 | 85.5674 | 84.8263 | 84.1558 | 82.6411 | 81.9474 | 81.3011 | 40.7579 | 79.6084 | 79.0789 | 78.6568 | 78.3389 | 77.8832 | 77.2021 | 76.3653 | 75.6116 | 73.8632 | 73.0747 | 72.3347 | 40.7579 | 82.3126 | 81.7926 | 81.3779 | 81.0621 | 80.6126 | 79.9442 | 79.1232 | 78.3832 | 76.6758 | 75.9032 | 75.1789
|  | PRESSED STEEL SWINDON PRIMARY | HT |  |  |  |  | 42.6874 | 87.0463 | 86.8779 | 86.6768 | 86.4179 | 85.8579 | 84.9895 | 84.1011 | 83.3537 | 82.1926 | 81.1863 | 80.2379 | 40.8168 | 79.4674 | 79.0905 | 78.7937 | 78.2253 | 77.5253 | 76.5474 | 75.5421 | 74.7053 | 73.4411 | 72.3168 | 71.2526 | 40.8158 | 82.1747 | 81.8042 | 81.5105 | 80.9505 | 80.2621 | 79.3021 | 78.3179 | 77.4958 | 76.2495 | 75.1453 | 74.1
|  | PRESSED STEEL SWINDON PRIMARY | HE |  |  |  |  | 42.7432 | 87.1432 | 87.0011 | 86.8326 | 86.6126 | 86.3968 | 86.0368 | 85.3137 | 84.6632 | 83.5295 | 83.0526 | 82.5926 | 40.9684 | 79.9053 | 79.4411 | 79.0779 | 78.8011 | 78.3811 | 77.7316 | 76.9147 | 76.1832 | 74.8579 | 74.3074 | 73.7705 | 40.9653 | 82.6042 | 82.1484 | 81.7905 | 81.5158 | 81.1011 | 80.4632 | 79.6632 | 78.9453 | 77.6526 | 77.1147 | 76.5905
|  | PRESSED STEEL SWINDON PRIMARY | FB |  |  |  |  | 42.8116 | 87.2537 | 87.2011 | 87.1337 | 87.0663 | 87.0011 | 86.9326 | 86.8632 | 86.7895 | 85.5558 | 85.0642 | 84.6505 | 41.1 | 80.06 | 79.9558 | 79.7253 | 79.5484 | 79.4274 | 79.2421 | 78.9874 | 78.7084 | 77.0968 | 76.5379 | 76.0632 | 41.0958 | 82.7579 | 82.6537 | 82.4284 | 82.2547 | 82.1347 | 81.9526 | 81.7042 | 81.4305 | 79.8547 | 79.3074 | 78.8432
FLEET-BRAMLEY GSP | ALTON BSP | PRESTON CANDOVER PRIMARY | MINIMUM HEADROOM | SU 60879 41131 | NO | YES | 0 | 16.7253 | 16.6389 | 16.5358 | 16.4347 | 16.2937 | 16.1221 | 15.9705 | 15.8105 | 15.6526 | 11.0347 | 10.9168 | 10.82 | 15.6358 | 15.5179 | 15.38 | 15.2568 | 15.0779 | 14.8779 | 14.7095 | 14.5305 | 14.3526 | 8.9326 | 8.7968 | 8.6842 | 15.8589 | 15.7411 | 15.6021 | 15.48 | 15.3 | 15.1 | 14.9305 | 14.7505 | 14.5737 | 9.1316 | 8.9958 | 8.8832
|  | PRESTON CANDOVER PRIMARY | EE |  |  |  |  | 16.7253 | 16.6537 | 16.5358 | 16.4453 | 16.3347 | 16.2284 | 16.12 | 16.0063 | 15.8926 | 13.8705 | 13.6716 | 13.4484 | 15.6358 | 15.5442 | 15.38 | 15.2737 | 15.1495 | 15.0295 | 14.9021 | 14.7747 | 14.6516 | 12.2663 | 12.0411 | 11.7863 | 15.8589 | 15.7674 | 15.6021 | 15.4958 | 15.3716 | 15.2516 | 15.1242 | 14.9968 | 14.8737 | 12.4779 | 12.2516 | 11.9968
|  | PRESTON CANDOVER PRIMARY | HT |  |  |  |  | 16.7368 | 16.6389 | 16.5516 | 16.4347 | 16.2937 | 16.1221 | 15.9705 | 15.8105 | 15.6526 | 12.2905 | 11.9779 | 11.6505 | 15.6537 | 15.5179 | 15.4074 | 15.2568 | 15.0779 | 14.8779 | 14.7095 | 14.5305 | 14.3526 | 10.4484 | 10.1032 | 9.7379 | 15.8768 | 15.7411 | 15.6305 | 15.48 | 15.3 | 15.1 | 14.9305 | 14.7505 | 14.5737 | 10.6526 | 10.3074 | 9.9411
|  | PRESTON CANDOVER PRIMARY | HE |  |  |  |  | 16.7674 | 16.7105 | 16.6074 | 16.5284 | 16.4305 | 16.3347 | 16.2411 | 16.1495 | 16.0568 | 11.0347 | 10.9168 | 10.82 | 15.7 | 15.6316 | 15.4905 | 15.4021 | 15.2958 | 15.1916 | 15.0884 | 14.9884 | 14.8884 | 8.9326 | 8.7968 | 8.6842 | 15.9242 | 15.8558 | 15.7137 | 15.6253 | 15.5179 | 15.4147 | 15.3116 | 15.2116 | 15.1105 | 9.1316 | 8.9958 | 8.8832
|  | PRESTON CANDOVER PRIMARY | FB |  |  |  |  | 16.8158 | 16.7779 | 16.7474 | 16.6989 | 16.6642 | 16.6305 | 16.5958 | 16.5642 | 16.5326 | 16.3884 | 14.0916 | 13.9663 | 15.7579 | 15.7074 | 15.6684 | 15.5989 | 15.5558 | 15.5137 | 15.4705 | 15.4305 | 15.3905 | 15.2011 | 12.4568 | 12.3147 | 15.9811 | 15.9305 | 15.8916 | 15.8232 | 15.7789 | 15.7368 | 15.6937 | 15.6537 | 15.6137 | 15.4232 | 12.6674 | 12.5253
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN PRIMARY | MINIMUM HEADROOM | SY 74226 95039 | NO | YES | 0 | 6.7463 | 6.6874 | 6.6126 | 6.5042 | 6.3737 | 6.2179 | 6.0674 | 5.9074 | 5.7495 | 5.3516 | 5.0863 | 4.8547 | 6.2863 | 6.2168 | 6.1253 | 5.9947 | 5.8432 | 5.6737 | 5.5084 | 5.3337 | 5.16 | 4.7211 | 4.4274 | 4.1705 | 6.3632 | 6.2989 | 6.2147 | 6.0926 | 5.9421 | 5.7737 | 5.6095 | 5.4358 | 5.2632 | 4.8274 | 4.5347 | 4.2789
|  | PUDDLETOWN PRIMARY | EE |  |  |  |  | 6.7463 | 6.6874 | 6.6263 | 6.5526 | 6.46 | 6.3747 | 6.2853 | 6.1916 | 6.1 | 5.88 | 5.6842 | 5.5147 | 6.2863 | 6.2168 | 6.1442 | 6.0589 | 5.9547 | 5.8589 | 5.7579 | 5.6579 | 5.56 | 5.3116 | 5.0916 | 4.9 | 6.3632 | 6.2989 | 6.2316 | 6.1516 | 6.0526 | 5.9568 | 5.8568 | 5.7579 | 5.66 | 5.4137 | 5.1947 | 5.0042
|  | PUDDLETOWN PRIMARY | HT |  |  |  |  | 6.7537 | 6.6916 | 6.6126 | 6.5042 | 6.3737 | 6.2179 | 6.0674 | 5.9074 | 5.7495 | 5.3516 | 5.0863 | 4.8547 | 6.2958 | 6.2221 | 6.1253 | 5.9947 | 5.8432 | 5.6737 | 5.5084 | 5.3337 | 5.16 | 4.7211 | 4.4274 | 4.1705 | 6.3716 | 6.3032 | 6.2147 | 6.0926 | 5.9421 | 5.7737 | 5.6095 | 5.4358 | 5.2632 | 4.8274 | 4.5347 | 4.2789
|  | PUDDLETOWN PRIMARY | HE |  |  |  |  | 6.78 | 6.7337 | 6.6853 | 6.62 | 6.5368 | 6.4611 | 6.3874 | 6.3126 | 6.24 | 6.1316 | 6 | 5.8842 | 6.3295 | 6.2768 | 6.22 | 6.1463 | 6.0526 | 5.9684 | 5.8853 | 5.8021 | 5.7221 | 5.5916 | 5.4421 | 5.3084 | 6.4011 | 6.3516 | 6.2989 | 6.2295 | 6.1411 | 6.0611 | 5.9821 | 5.9 | 5.82 | 5.6916 | 5.5421 | 5.4105
|  | PUDDLETOWN PRIMARY | FB |  |  |  |  | 6.8126 | 6.7832 | 6.7589 | 6.7316 | 6.7011 | 6.6705 | 6.64 | 6.6126 | 6.5821 | 6.4526 | 6.3305 | 6.2221 | 6.3674 | 6.3316 | 6.3021 | 6.2695 | 6.2326 | 6.1958 | 6.16 | 6.1263 | 6.0895 | 5.9305 | 5.7926 | 5.6695 | 6.4368 | 6.4032 | 6.3768 | 6.3474 | 6.3126 | 6.28 | 6.2463 | 6.2147 | 6.1821 | 6.0295 | 5.8916 | 5.7705
AXMINSTER GSP | YEOVIL BSP | PULHAM PRIMARY | MINIMUM HEADROOM | ST 71579 09451 | NO | YES | 0 | 8.1695 | 8.0695 | 7.96 | 7.8074 | 7.6316 | 7.4421 | 7.2547 | 7.0579 | 6.86 | 6.3358 | 5.9758 | 5.6642 | 5.1684 | 5.0579 | 4.9389 | 4.7716 | 4.58 | 4.3737 | 4.1684 | 3.9547 | 3.7432 | 3.1832 | 2.7968 | 2.4632 | 7.06 | 6.9737 | 6.8779 | 6.7442 | 6.5895 | 6.4232 | 6.2579 | 6.0884 | 5.8737 | 5.3021 | 4.9074 | 4.5653
|  | PULHAM PRIMARY | EE |  |  |  |  | 8.1695 | 8.0695 | 7.9611 | 7.8358 | 7.6853 | 7.5432 | 7.4011 | 7.2568 | 7.1168 | 6.8411 | 6.5874 | 6.3768 | 5.1684 | 5.0579 | 4.9389 | 4.8042 | 4.6453 | 4.4937 | 4.3411 | 4.1863 | 4.0358 | 3.7221 | 3.4453 | 3.2147 | 7.06 | 6.9737 | 6.8789 | 6.7663 | 6.6274 | 6.4968 | 6.3705 | 6.2411 | 6.1147 | 5.8526 | 5.5674 | 5.3295
|  | PULHAM PRIMARY | HT |  |  |  |  | 8.1832 | 8.0832 | 7.96 | 7.8074 | 7.6316 | 7.4421 | 7.2547 | 7.0579 | 6.86 | 6.3358 | 5.9758 | 5.6642 | 5.1842 | 5.0737 | 4.9389 | 4.7716 | 4.58 | 4.3737 | 4.1684 | 3.9547 | 3.7432 | 3.1832 | 2.7968 | 2.4632 | 7.0705 | 6.9842 | 6.8779 | 6.7442 | 6.5895 | 6.4232 | 6.2579 | 6.0884 | 5.8737 | 5.3021 | 4.9074 | 4.5653
|  | PULHAM PRIMARY | HE |  |  |  |  | 8.2305 | 8.1516 | 8.0684 | 7.96 | 7.8232 | 7.7 | 7.5789 | 7.46 | 7.34 | 7.2421 | 7.1053 | 6.9874 | 5.2389 | 5.1547 | 5.0642 | 4.9505 | 4.8063 | 4.6768 | 4.5505 | 4.4242 | 4.2979 | 4.1758 | 4.0116 | 3.8758 | 7.1063 | 7.0358 | 6.9611 | 6.8621 | 6.7337 | 6.62 | 6.5074 | 6.3968 | 6.2842 | 6.22 | 6.12 | 6.0084
|  | PULHAM PRIMARY | FB |  |  |  |  | 8.2958 | 8.2453 | 8.2074 | 8.1653 | 8.12 | 8.0737 | 8.0295 | 7.9863 | 7.9421 | 7.7558 | 7.6 | 7.4684 | 5.3095 | 5.2526 | 5.2095 | 5.1632 | 5.1126 | 5.0621 | 5.0137 | 4.9653 | 4.9158 | 4.7063 | 4.5274 | 4.3716 | 7.1653 | 7.1242 | 7.0916 | 7.0568 | 7.0168 | 6.9779 | 6.94 | 6.9042 | 6.8653 | 6.7095 | 6.5874 | 6.4863
LOVEDEAN GSP | FORT WIDLEY BSP | PURBROOK PRIMARY | MINIMUM HEADROOM | SU 67047 07819 | NO | YES | 0 | 16.0845 | 15.9613 | 15.6013 | 15.0171 | 14.3434 | 13.6361 | 12.9139 | 12.1739 | 11.4203 | 9.5245 | 8.5255 | 7.3929 | 14.0826 | 13.9458 | 13.61 | 13.0089 | 12.2532 | 11.4626 | 10.6532 | 9.8237 | 8.9763 | 6.8395 | 5.7226 | 4.4416 | 14.2368 | 13.9253 | 13.4989 | 12.8779 | 12.1621 | 11.4126 | 10.6463 | 9.8611 | 9.06 | 7.04 | 5.9811 | 4.7747
|  | PURBROOK PRIMARY | EE |  |  |  |  | 16.0845 | 15.9613 | 15.6487 | 15.2161 | 14.7339 | 14.2929 | 13.8645 | 13.4276 | 12.9782 | 11.8918 | 11.255 | 10.4855 | 14.0826 | 13.9458 | 13.6479 | 13.2395 | 12.7121 | 12.2311 | 11.7616 | 11.2837 | 10.79 | 9.5384 | 8.8142 | 7.9279 | 14.2368 | 13.9253 | 13.5505 | 13.0926 | 12.5863 | 12.1253 | 11.6768 | 11.2189 | 10.7474 | 9.5768 | 8.8958 | 8.0663
|  | PURBROOK PRIMARY | HT |  |  |  |  | 16.0908 | 15.9718 | 15.6013 | 15.0171 | 14.3434 | 13.6361 | 12.9139 | 12.1739 | 11.4203 | 9.5245 | 8.5255 | 7.3929 | 14.0889 | 13.9679 | 13.61 | 13.0089 | 12.2532 | 11.4626 | 10.6532 | 9.8237 | 8.9763 | 6.8395 | 5.7226 | 4.4416 | 14.2779 | 13.9547 | 13.4989 | 12.8779 | 12.1621 | 11.4126 | 10.6463 | 9.8611 | 9.06 | 7.04 | 5.9811 | 4.7747
|  | PURBROOK PRIMARY | HE |  |  |  |  | 16.1234 | 16.0097 | 15.8813 | 15.4992 | 15.0476 | 14.6424 | 14.2487 | 13.8445 | 13.4287 | 12.6455 | 12.2097 | 11.6076 | 14.1216 | 14.0079 | 13.8447 | 13.5068 | 13.07 | 12.6289 | 12.2005 | 11.7595 | 11.3047 | 10.3826 | 9.8763 | 9.1721 | 14.3905 | 14.1358 | 13.8137 | 13.3968 | 12.9242 | 12.5 | 12.0895 | 11.6663 | 11.2305 | 10.3768 | 9.9053 | 9.2516
|  | PURBROOK PRIMARY | FB |  |  |  |  | 16.2045 | 16.1466 | 16.0929 | 16.0339 | 15.9676 | 15.8003 | 15.6255 | 15.4497 | 15.255 | 14.5192 | 14.0961 | 13.6066 | 14.2047 | 14.1447 | 14.0911 | 14.0311 | 13.9226 | 13.7805 | 13.6353 | 13.49 | 13.2721 | 12.4426 | 11.9647 | 11.4026 | 14.5705 | 14.4042 | 14.2484 | 14.0695 | 13.8874 | 13.7074 | 13.5232 | 13.3368 | 13.1295 | 12.3453 | 11.8947 | 11.3684
FLEET-BRAMLEY GSP | PYESTOCK BSP | PYESTOCK PRIMARY | MINIMUM HEADROOM | SU 82940 54553 | NO | YES | 0 | 23.42 | 23.1179 | 22.9621 | 22.7611 | 22.5642 | 22.3674 | 22.1779 | 22.0032 | 21.8116 | 18.2611 | 18.2611 | 18.2611 | 21.1621 | 20.7737 | 20.5737 | 20.3147 | 20.0611 | 19.8074 | 19.5632 | 19.3389 | 19.0926 | 15.0189 | 15.0189 | 15.0189 | 22.82 | 22.3947 | 22.1768 | 21.8937 | 21.6168 | 21.34 | 21.0737 | 20.8284 | 20.5589 | 16.1095 | 16.1095 | 16.1095
|  | PYESTOCK PRIMARY | EE |  |  |  |  | 23.42 | 23.1179 | 22.9621 | 22.7611 | 22.5642 | 22.3674 | 22.1779 | 22.0032 | 21.8116 | 18.2611 | 18.2611 | 18.2611 | 21.1621 | 20.7737 | 20.5737 | 20.3147 | 20.0611 | 19.8074 | 19.5632 | 19.3389 | 19.0926 | 15.0189 | 15.0189 | 15.0189 | 22.82 | 22.3947 | 22.1768 | 21.8937 | 21.6168 | 21.34 | 21.0737 | 20.8284 | 20.5589 | 16.1095 | 16.1095 | 16.1095
|  | PYESTOCK PRIMARY | HT |  |  |  |  | 23.42 | 23.1179 | 22.9621 | 22.7611 | 22.5642 | 22.3674 | 22.1779 | 22.0042 | 21.8126 | 21.0768 | 21.0768 | 21.0768 | 21.1621 | 20.7737 | 20.5737 | 20.3147 | 20.0611 | 19.8074 | 19.5642 | 19.3411 | 19.0937 | 18.1463 | 18.1463 | 18.1463 | 22.82 | 22.3947 | 22.1768 | 21.8937 | 21.6168 | 21.34 | 21.0747 | 20.8305 | 20.5611 | 19.5253 | 19.5253 | 19.5253
|  | PYESTOCK PRIMARY | HE |  |  |  |  | 23.42 | 23.1179 | 22.9621 | 22.7611 | 22.5642 | 22.3674 | 22.1779 | 22.0042 | 21.8126 | 18.2621 | 18.2621 | 18.2621 | 21.1621 | 20.7737 | 20.5737 | 20.3147 | 20.0611 | 19.8074 | 19.5642 | 19.3411 | 19.0937 | 15.0211 | 15.0211 | 15.0211 | 22.82 | 22.3947 | 22.1768 | 21.8937 | 21.6168 | 21.34 | 21.0747 | 20.8305 | 20.5611 | 16.1116 | 16.1116 | 16.1116
|  | PYESTOCK PRIMARY | FB |  |  |  |  | 23.4947 | 23.3547 | 23.2874 | 23.2042 | 23.1263 | 23.0389 | 22.9463 | 22.8537 | 22.7421 | 22.2821 | 22.2821 | 22.2821 | 21.2589 | 21.0779 | 20.9916 | 20.8842 | 20.7842 | 20.6716 | 20.5526 | 20.4326 | 20.2895 | 19.6979 | 19.6979 | 19.6979 | 22.8958 | 22.7274 | 22.6337 | 22.5168 | 22.4074 | 22.2842 | 22.1537 | 22.0232 | 21.8674 | 21.22 | 21.22 | 21.22
MINETY GSP | TOOTHILL BSP | QUARRY ROAD PRIMARY | MINIMUM HEADROOM | SU 15334 83380 | NO | YES | 0 | 24.2937 | 24.1589 | 24.0063 | 23.7842 | 23.4695 | 23.1232 | 22.4916 | 21.6958 | 21.0916 | 19.6916 | 17.9442 | 16.2021 | 21.9568 | 21.8221 | 21.6695 | 21.3411 | 20.5663 | 19.76 | 19.0432 | 18.2895 | 17.7126 | 16.4032 | 14.5947 | 12.5853 | 19.6242 | 19.3832 | 19.0937 | 18.7537 | 18.1295 | 17.4853 | 16.9011 | 16.2937 | 15.8063 | 14.6916 | 13.4832 | 11.6989
|  | QUARRY ROAD PRIMARY | EE |  |  |  |  | 24.2937 | 24.1589 | 24.0063 | 23.8095 | 23.5116 | 23.2095 | 22.7874 | 22.0705 | 21.5221 | 20.2284 | 18.9737 | 17.7295 | 21.9568 | 21.8221 | 21.6695 | 21.3411 | 20.7284 | 19.9926 | 19.3253 | 18.6474 | 18.1232 | 16.9516 | 15.6642 | 14.2011 | 19.6242 | 19.3832 | 19.0937 | 18.7537 | 18.2505 | 17.6653 | 17.1326 | 16.5905 | 16.1537 | 15.2632 | 14.4326 | 13.3021
|  | QUARRY ROAD PRIMARY | HT |  |  |  |  | 24.3126 | 24.18 | 24.0063 | 23.7842 | 23.4695 | 23.1232 | 22.4916 | 21.6958 | 21.0916 | 19.6916 | 17.9442 | 16.2021 | 21.9758 | 21.8432 | 21.6695 | 21.3842 | 20.5663 | 19.76 | 19.0432 | 18.2895 | 17.7126 | 16.4032 | 14.5947 | 12.5853 | 19.6695 | 19.4411 | 19.1379 | 18.7768 | 18.1295 | 17.4853 | 16.9011 | 16.2937 | 15.8063 | 14.6916 | 13.4832 | 11.6989
|  | QUARRY ROAD PRIMARY | HE |  |  |  |  | 24.3537 | 24.2358 | 24.0895 | 23.8989 | 23.6284 | 23.3347 | 23.0537 | 22.6095 | 22.1179 | 21.3779 | 20.4537 | 19.4874 | 22.0168 | 21.8989 | 21.7526 | 21.5621 | 21.1053 | 20.3979 | 19.7747 | 19.1495 | 18.6779 | 17.9916 | 17.1716 | 16.2105 | 19.7705 | 19.5821 | 19.3305 | 19.0221 | 18.5358 | 17.9726 | 17.4705 | 16.9632 | 16.5632 | 16.0663 | 15.4758 | 14.8821
|  | QUARRY ROAD PRIMARY | FB |  |  |  |  | 24.4316 | 24.36 | 24.2958 | 24.2232 | 24.1432 | 24.0632 | 23.9821 | 23.8905 | 23.8011 | 23.4505 | 22.8032 | 22.0695 | 22.0947 | 22.0232 | 21.9589 | 21.8863 | 21.8063 | 21.7011 | 21.4737 | 21.2084 | 21.0147 | 20.0747 | 19.3684 | 18.6874 | 19.8863 | 19.7495 | 19.6232 | 19.4821 | 19.3 | 19.0989 | 18.8989 | 18.6947 | 18.5379 | 17.8042 | 17.2705 | 16.7716
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | QUEENSMEAD PRIMARY | MINIMUM HEADROOM | SU 87062 55683 | NO | YES | 0 | 12.6705 | 12.5337 | 12.2137 | 12.0442 | 11.4863 | 11.1989 | 10.8905 | 10.5779 | 10.2695 | 9.26 | 8.7937 | 8.3758 | 14.3811 | 14.2189 | 13.8011 | 13.6105 | 12.8842 | 12.5474 | 12.1789 | 11.8032 | 11.4305 | 10.1495 | 9.5811 | 9.0695 | 14.9895 | 14.9126 | 14.8211 | 14.6958 | 14.0695 | 13.7368 | 13.3726 | 13.0021 | 12.6347 | 11.3737 | 10.8126 | 10.3063
|  | QUEENSMEAD PRIMARY | EE |  |  |  |  | 12.6705 | 12.5337 | 12.2137 | 12.0442 | 11.4863 | 11.2821 | 11.0905 | 10.8968 | 10.7063 | 10.0758 | 9.7663 | 9.5063 | 14.3811 | 14.2189 | 13.8011 | 13.6105 | 12.8842 | 12.6589 | 12.4474 | 12.2337 | 12.0242 | 11.1726 | 10.7705 | 10.4316 | 14.9895 | 14.9126 | 14.8253 | 14.7084 | 14.0695 | 13.8463 | 13.6347 | 13.4232 | 13.2158 | 12.3811 | 11.9853 | 11.6526
|  | QUEENSMEAD PRIMARY | HT |  |  |  |  | 12.6958 | 12.5674 | 12.2432 | 12.0705 | 11.5021 | 11.1989 | 10.8905 | 10.5779 | 10.2695 | 9.26 | 8.7937 | 8.3758 | 14.4147 | 14.2653 | 13.8463 | 13.6526 | 12.9095 | 12.5474 | 12.1789 | 11.8032 | 11.4305 | 10.1495 | 9.5811 | 9.0695 | 14.9937 | 14.9189 | 14.8211 | 14.6958 | 14.0937 | 13.7368 | 13.3726 | 13.0021 | 12.6347 | 11.3737 | 10.8126 | 10.3063
|  | QUEENSMEAD PRIMARY | HE |  |  |  |  | 12.7547 | 12.6484 | 12.3547 | 12.2084 | 11.6642 | 11.4768 | 11.3105 | 11.1411 | 10.9758 | 10.5663 | 10.3947 | 10.2537 | 14.4937 | 14.3737 | 13.9926 | 13.8326 | 13.1263 | 12.9242 | 12.7474 | 12.5684 | 12.3937 | 11.8105 | 11.5768 | 11.3832 | 15.0074 | 14.9337 | 14.8484 | 14.7326 | 14.3074 | 14.1063 | 13.9305 | 13.7516 | 13.5779 | 13.0074 | 12.7789 | 12.5884
|  | QUEENSMEAD PRIMARY | FB |  |  |  |  | 12.8579 | 12.7821 | 12.6474 | 12.5821 | 12.3789 | 12.3063 | 12.2421 | 12.1811 | 12.1179 | 11.6611 | 11.4347 | 11.2411 | 14.6158 | 14.5242 | 14.3453 | 14.2684 | 13.9968 | 13.9105 | 13.8368 | 13.7653 | 13.6916 | 13.1053 | 12.8168 | 12.5632 | 15.0642 | 15.0284 | 14.9958 | 14.9589 | 14.9189 | 14.8779 | 14.8389 | 14.8021 | 14.7621 | 14.2874 | 14.0042 | 13.7547
MELKSHAM GSP | WEST GRAFTON BSP | RAMSBURY PRIMARY | MINIMUM HEADROOM | SU 27380 72108 | NO | YES | 0 | 8.7905 | 8.7316 | 8.6568 | 8.5495 | 8.4126 | 8.2579 | 8.0968 | 7.9242 | 7.7463 | 7.2779 | 6.8558 | 6.4326 | 8.2189 | 8.0705 | 7.9253 | 7.7979 | 7.6295 | 7.4389 | 7.2368 | 7.0137 | 6.7811 | 6.1526 | 5.6305 | 5.1537 | 7.8063 | 7.6621 | 7.52 | 7.3947 | 7.2284 | 7.0421 | 6.8442 | 6.6253 | 6.3989 | 5.7863 | 5.28 | 4.8158
|  | RAMSBURY PRIMARY | EE |  |  |  |  | 8.7905 | 8.7316 | 8.6568 | 8.5621 | 8.4453 | 8.3368 | 8.2274 | 8.1189 | 8.0147 | 7.7989 | 7.5442 | 7.3242 | 8.2189 | 8.0705 | 7.9253 | 7.8147 | 7.6853 | 7.5632 | 7.4379 | 7.3126 | 7.1947 | 6.88 | 6.5011 | 6.1705 | 7.8063 | 7.6621 | 7.52 | 7.4105 | 7.2821 | 7.1621 | 7.0379 | 6.9147 | 6.7979 | 6.4926 | 6.1253 | 5.8074
|  | RAMSBURY PRIMARY | HT |  |  |  |  | 8.7958 | 8.7411 | 8.6674 | 8.5495 | 8.4126 | 8.2579 | 8.0968 | 7.9242 | 7.7463 | 7.2779 | 6.8558 | 6.4326 | 8.2389 | 8.1011 | 7.9442 | 7.7979 | 7.6295 | 7.4389 | 7.2368 | 7.0137 | 6.7811 | 6.1526 | 5.6305 | 5.1537 | 7.8263 | 7.6905 | 7.5379 | 7.3947 | 7.2284 | 7.0421 | 6.8442 | 6.6253 | 6.3989 | 5.7863 | 5.28 | 4.8158
|  | RAMSBURY PRIMARY | HE |  |  |  |  | 8.8095 | 8.7568 | 8.7021 | 8.6337 | 8.5368 | 8.4505 | 8.3589 | 8.2642 | 8.1695 | 8.0811 | 7.9021 | 7.7484 | 8.2884 | 8.1663 | 8.0453 | 7.9558 | 7.8389 | 7.7337 | 7.6326 | 7.5295 | 7.4274 | 7.2779 | 6.9958 | 6.7516 | 7.8747 | 7.7547 | 7.6358 | 7.5474 | 7.4305 | 7.3263 | 7.2263 | 7.1242 | 7.0221 | 6.8789 | 6.6074 | 6.3716
|  | RAMSBURY PRIMARY | FB |  |  |  |  | 8.8453 | 8.82 | 8.7989 | 8.7747 | 8.7505 | 8.7253 | 8.7011 | 8.6789 | 8.6537 | 8.5095 | 8.3411 | 8.1968 | 8.3463 | 8.2789 | 8.2221 | 8.18 | 8.1358 | 8.0905 | 8.0474 | 8.0063 | 7.9621 | 7.7526 | 7.5063 | 7.2895 | 7.9316 | 7.8653 | 7.8095 | 7.7674 | 7.7242 | 7.68 | 7.6379 | 7.5979 | 7.5547 | 7.3495 | 7.1105 | 6.9011
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | RATFYN PRIMARY | MINIMUM HEADROOM | SU 16215 42533 | NO | YES | 0 | 26.8137 | 26.6568 | 26.4863 | 26.2463 | 25.7558 | 25.1747 | 24.5653 | 23.8832 | 23.1642 | 21.2389 | 19.6463 | 18.1968 | 22.7516 | 22.4663 | 22.1779 | 21.7863 | 21.2674 | 20.6716 | 20.0453 | 19.3442 | 18.6032 | 16.6126 | 14.9674 | 13.3842 | 24.6947 | 24.3905 | 24.0832 | 23.6674 | 23.1105 | 22.4716 | 21.7979 | 21.0368 | 20.2295 | 18.0463 | 16.2189 | 14.5789
|  | RATFYN PRIMARY | EE |  |  |  |  | 26.8137 | 26.6568 | 26.4863 | 26.2611 | 25.9284 | 25.5568 | 25.1768 | 24.7979 | 24.4274 | 23.5021 | 22.3684 | 21.3821 | 22.7516 | 22.4663 | 22.1779 | 21.8463 | 21.4495 | 21.0726 | 20.6863 | 20.3021 | 19.9263 | 18.9621 | 17.7789 | 16.7495 | 24.6947 | 24.3905 | 24.0832 | 23.7326 | 23.3221 | 22.9326 | 22.5274 | 22.1253 | 21.7326 | 20.6558 | 19.3242 | 18.1642
|  | RATFYN PRIMARY | HT |  |  |  |  | 26.8274 | 26.6821 | 26.4916 | 26.2463 | 25.7558 | 25.1747 | 24.5653 | 23.8832 | 23.1642 | 21.2389 | 19.6463 | 18.1968 | 22.8095 | 22.5537 | 22.2295 | 21.7863 | 21.2674 | 20.6716 | 20.0453 | 19.3442 | 18.6032 | 16.6126 | 14.9674 | 13.3842 | 24.7611 | 24.4874 | 24.1421 | 23.6674 | 23.1105 | 22.4716 | 21.7979 | 21.0368 | 20.2295 | 18.0463 | 16.2189 | 14.5789
|  | RATFYN PRIMARY | HE |  |  |  |  | 26.8632 | 26.7253 | 26.5653 | 26.3484 | 26.0484 | 25.7758 | 25.5116 | 25.2442 | 24.98 | 24.6232 | 23.7842 | 23.0484 | 22.9484 | 22.7389 | 22.5116 | 22.2305 | 21.8684 | 21.5347 | 21.2137 | 20.8947 | 20.5842 | 20.1263 | 19.2474 | 18.4747 | 24.8916 | 24.6947 | 24.4579 | 24.1663 | 23.7937 | 23.4505 | 23.1211 | 22.7937 | 22.4758 | 21.9484 | 20.9474 | 20.0663
|  | RATFYN PRIMARY | FB |  |  |  |  | 26.9642 | 26.8989 | 26.8368 | 26.7653 | 26.6874 | 26.6084 | 26.5316 | 26.46 | 26.3842 | 25.9105 | 25.18 | 24.54 | 23.1179 | 22.9611 | 22.8411 | 22.7137 | 22.5768 | 22.44 | 22.3074 | 22.1832 | 22.0558 | 21.4221 | 20.6621 | 19.9937 | 24.9926 | 24.9253 | 24.7958 | 24.6589 | 24.5137 | 24.3674 | 24.2263 | 24.0926 | 23.9568 | 23.2695 | 22.42 | 21.6663
BRAMLEY (BASI) GSP | READING BSP | READING PRIMARY | MINIMUM HEADROOM | SU 74591 73788 | NO | YES | 0 | 49.4805 | 49.1311 | 48.7279 | 48.1847 | 47.5416 | 46.6026 | 45.4784 | 44.31 | 43.0995 | 40.0784 | 37.8289 | 35.3111 | 44.8495 | 44.0937 | 43.1642 | 42.0895 | 40.88 | 39.5337 | 38.3274 | 37.0674 | 35.7579 | 32.4779 | 29.9958 | 27.1779 | 45.9179 | 45.6021 | 45.2421 | 44.7421 | 43.5358 | 42.1895 | 40.9821 | 39.7221 | 38.4116 | 35.1358 | 32.6526 | 29.8358
|  | READING PRIMARY | EE |  |  |  |  | 49.4805 | 49.1311 | 48.7416 | 48.2447 | 47.5784 | 46.9416 | 46.3479 | 45.7405 | 45.0974 | 43.65 | 42.2037 | 40.5605 | 44.8495 | 44.0937 | 43.2189 | 42.4589 | 41.5663 | 40.7042 | 39.8211 | 38.9326 | 38.0653 | 36.4474 | 34.8137 | 32.9347 | 45.9179 | 45.6021 | 45.2516 | 44.7768 | 44.1274 | 43.3589 | 42.4758 | 41.5874 | 40.7189 | 39.1063 | 37.4726 | 35.5926
|  | READING PRIMARY | HT |  |  |  |  | 49.5005 | 49.1679 | 48.7279 | 48.1847 | 47.5416 | 46.6026 | 45.4784 | 44.31 | 43.0995 | 40.0784 | 37.8289 | 35.3111 | 44.9726 | 44.1905 | 43.1642 | 42.0895 | 40.88 | 39.5337 | 38.3274 | 37.0674 | 35.7579 | 32.4779 | 29.9958 | 27.1779 | 45.9305 | 45.6326 | 45.2421 | 44.7421 | 43.5358 | 42.1895 | 40.9821 | 39.7221 | 38.4116 | 35.1358 | 32.6526 | 29.8358
|  | READING PRIMARY | HE |  |  |  |  | 49.5732 | 49.2511 | 48.8879 | 48.4132 | 47.7584 | 47.1637 | 46.5774 | 45.9858 | 45.3995 | 45.4174 | 45.1668 | 44.0668 | 45.1716 | 44.7189 | 43.9989 | 43.3663 | 42.56 | 41.8105 | 41.0716 | 40.3305 | 39.6032 | 39.0621 | 38.1316 | 36.8505 | 45.9821 | 45.6811 | 45.3474 | 44.8853 | 44.2432 | 43.6589 | 43.0863 | 42.5063 | 41.9326 | 41.7126 | 40.7789 | 39.4968
|  | READING PRIMARY | FB |  |  |  |  | 49.8258 | 49.6616 | 49.5142 | 49.3574 | 49.1837 | 49.0089 | 48.8405 | 48.6816 | 48.5132 | 47.8858 | 47.5026 | 46.5932 | 45.4505 | 45.2495 | 44.9526 | 44.6558 | 44.3368 | 44.0179 | 43.7032 | 43.3968 | 43.0863 | 41.8368 | 40.6884 | 39.4495 | 46.22 | 46.0758 | 45.9463 | 45.8011 | 45.6389 | 45.4768 | 45.32 | 45.1726 | 45.0158 | 44.4389 | 43.3442 | 42.1042
FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN PRIMARY | MINIMUM HEADROOM | SU 71540 74122 | NO | YES | 0 | 100.2305 | 100.0568 | 99.8568 | 99.6063 | 99.2737 | 97.1874 | 93.7832 | 90.7368 | 87.5832 | 82.0747 | 80.7768 | 79.5895 | 97.42 | 97.2453 | 97.0453 | 95.8179 | 93.9484 | 91.1474 | 87.2042 | 83.68 | 80.0305 | 73.6537 | 72.22 | 70.9063 | 98.3905 | 98.2116 | 98.0053 | 97.1589 | 95.2937 | 92.4263 | 88.4611 | 84.9168 | 81.2474 | 74.8747 | 73.4274 | 72.1021
|  | READING TOWN PRIMARY | EE |  |  |  |  | 100.2305 | 100.0568 | 99.8568 | 99.6063 | 99.2737 | 97.1874 | 93.7832 | 90.7368 | 87.5832 | 82.3305 | 81.2684 | 80.3474 | 97.42 | 97.2453 | 97.0453 | 95.8179 | 93.9484 | 91.1474 | 87.2042 | 83.68 | 80.0305 | 73.9411 | 72.7621 | 71.7421 | 98.3905 | 98.2116 | 98.0053 | 97.1589 | 95.2937 | 92.4263 | 88.4611 | 84.9168 | 81.2474 | 75.1042 | 73.8968 | 72.8484
|  | READING TOWN PRIMARY | HT |  |  |  |  | 100.2611 | 100.1 | 99.9021 | 99.6495 | 99.3579 | 97.2779 | 93.9526 | 90.9358 | 87.7937 | 82.0747 | 80.7768 | 79.5895 | 97.4474 | 97.2863 | 97.0863 | 95.8411 | 94.0095 | 91.2242 | 87.3695 | 83.88 | 80.24 | 73.6537 | 72.22 | 70.9063 | 98.4274 | 98.2632 | 98.0621 | 97.2021 | 95.3768 | 92.5263 | 88.6558 | 85.1495 | 81.4926 | 74.8747 | 73.4274 | 72.1021
|  | READING TOWN PRIMARY | HE |  |  |  |  | 100.3095 | 100.1663 | 100 | 99.7737 | 99.4695 | 97.7695 | 94.4968 | 91.5905 | 88.5579 | 84.1537 | 83.6158 | 83.1421 | 97.4979 | 97.3558 | 97.1884 | 96.3105 | 94.4937 | 91.7789 | 87.9842 | 84.6179 | 81.1042 | 75.9316 | 75.3147 | 74.7674 | 98.48 | 98.3379 | 98.1705 | 97.6789 | 95.88 | 93.0979 | 89.2884 | 85.9074 | 82.3811 | 77.1853 | 76.5632 | 76.0126
|  | READING TOWN PRIMARY | FB |  |  |  |  | 100.4084 | 100.3305 | 100.26 | 100.18 | 100.0916 | 100.0032 | 99.9168 | 99.1832 | 97.4747 | 94.3663 | 93.6547 | 93.0747 | 97.5968 | 97.5189 | 97.4484 | 97.3684 | 97.28 | 96.7021 | 95.0063 | 93.3242 | 91.3326 | 87.7337 | 86.9295 | 86.2684 | 98.58 | 98.5021 | 98.4316 | 98.3516 | 98.2632 | 98.0684 | 96.3937 | 94.6495 | 92.6495 | 89.0368 | 88.2305 | 87.5663
MANNINGTON GSP | REDHILL BSP | REDHILL PRIMARY | MINIMUM HEADROOM | SZ 08512 96149 | NO | YES | 0 | 41.7135 | 40.6914 | 39.5503 | 38.5535 | 37.3935 | 36.0029 | 34.6451 | 33.224 | 29.6924 | 26.3693 | 23.9198 | 21.6882 | 37.1682 | 36.0577 | 34.8198 | 33.7451 | 32.464 | 30.9293 | 29.4345 | 27.8619 | 23.7851 | 20.1335 | 17.424 | 14.9556 | 38.0482 | 36.9377 | 35.6998 | 34.6408 | 33.3745 | 31.864 | 30.3914 | 28.8451 | 24.7977 | 21.1366 | 18.4166 | 15.9366
|  | REDHILL PRIMARY | EE |  |  |  |  | 41.7135 | 40.6914 | 39.5503 | 38.5535 | 37.4619 | 36.4608 | 35.3851 | 34.2208 | 32.1766 | 27.3019 | 24.9966 | 23.1135 | 37.1682 | 36.0577 | 34.8198 | 33.7693 | 32.6293 | 31.5808 | 30.4524 | 29.2303 | 26.9387 | 21.4072 | 18.8566 | 16.7661 | 38.0482 | 36.9377 | 35.6998 | 34.6408 | 33.4945 | 32.4408 | 31.3051 | 30.0724 | 27.8145 | 22.2829 | 19.7008 | 17.5861
|  | REDHILL PRIMARY | HT |  |  |  |  | 41.9566 | 40.9229 | 39.7672 | 38.5777 | 37.3935 | 36.0029 | 34.6451 | 33.224 | 29.6924 | 26.3693 | 23.9198 | 21.6882 | 37.4282 | 36.2956 | 35.0303 | 33.7451 | 32.464 | 30.9293 | 29.4345 | 27.8619 | 23.7851 | 20.1335 | 17.424 | 14.9556 | 38.3124 | 37.1851 | 35.9272 | 34.6451 | 33.3745 | 31.864 | 30.3914 | 28.8451 | 24.7977 | 21.1366 | 18.4166 | 15.9366
|  | REDHILL PRIMARY | HE |  |  |  |  | 42.6208 | 42.0861 | 41.4724 | 40.9608 | 40.2998 | 39.6777 | 39.1008 | 38.4977 | 36.8472 | 34.004 | 33.0661 | 32.2598 | 38.1482 | 37.5608 | 36.8861 | 36.3503 | 35.6672 | 35.0208 | 34.424 | 33.7998 | 31.9324 | 28.5608 | 27.4672 | 26.5219 | 39.0398 | 38.4619 | 37.7987 | 37.2682 | 36.5882 | 35.9472 | 35.3535 | 34.7335 | 32.9072 | 29.6345 | 28.5472 | 27.6051
|  | REDHILL PRIMARY | FB |  |  |  |  | 43.0482 | 42.7156 | 41.4998 | 41.2693 | 41.0219 | 40.7745 | 40.5366 | 40.3093 | 40.0787 | 39.0282 | 38.0293 | 37.1703 | 38.6208 | 38.2493 | 36.4966 | 36.2461 | 35.9787 | 35.7103 | 35.4524 | 35.2061 | 34.9566 | 33.8019 | 32.6672 | 31.6808 | 39.504 | 39.1387 | 37.2482 | 37.0008 | 36.7366 | 36.4724 | 36.2187 | 35.9766 | 35.7303 | 34.5945 | 33.4861 | 32.5229
CHICKERELL GSP | CHICKERELL BSP | REDLANDS PRIMARY | MINIMUM HEADROOM | SY 67131 82321 | NO | YES | 0.031579 | 20.7221 | 22.2263 | 22.0337 | 21.7611 | 21.4253 | 21.0747 | 20.4705 | 19.5832 | 18.6989 | 16.5126 | 15.0705 | 13.7747 | 19.9779 | 19.9253 | 19.3821 | 18.6242 | 17.7189 | 16.7326 | 15.7537 | 14.7695 | 13.7895 | 11.3547 | 9.7432 | 8.2916 | 21.8137 | 22.4853 | 21.9484 | 21.1979 | 20.3021 | 19.3274 | 18.3589 | 17.3853 | 16.4158 | 14.0084 | 12.4158 | 10.9811
|  | REDLANDS PRIMARY | EE |  |  |  |  | 20.7221 | 22.2263 | 22.0411 | 21.7863 | 21.4253 | 21.0937 | 20.7958 | 20.4874 | 20.1832 | 19.5505 | 18.5421 | 17.6611 | 19.9779 | 19.9253 | 19.4884 | 18.98 | 18.3632 | 17.7863 | 17.2295 | 16.6705 | 16.1221 | 14.8063 | 13.6547 | 12.6495 | 21.8137 | 22.4853 | 22.0526 | 21.5484 | 20.9358 | 20.3642 | 19.8105 | 19.2547 | 18.7116 | 17.4147 | 16.2789 | 15.2863
|  | REDLANDS PRIMARY | HT |  |  |  |  | 20.7295 | 22.2463 | 22.0337 | 21.7611 | 21.4347 | 21.0747 | 20.4705 | 19.5832 | 18.6989 | 16.5126 | 15.0705 | 13.7747 | 20.0337 | 19.9579 | 19.3821 | 18.6242 | 17.7189 | 16.7326 | 15.7537 | 14.7695 | 13.7895 | 11.3547 | 9.7432 | 8.2916 | 21.8695 | 22.5179 | 21.9484 | 21.1979 | 20.3021 | 19.3274 | 18.3589 | 17.3853 | 16.4158 | 14.0084 | 12.4158 | 10.9811
|  | REDLANDS PRIMARY | HE |  |  |  |  | 20.7674 | 22.2853 | 22.1116 | 21.8684 | 21.5168 | 21.2105 | 20.9105 | 20.6021 | 20.3021 | 20.3432 | 20.0579 | 19.4537 | 20.2326 | 20.2811 | 19.9305 | 19.4958 | 18.9316 | 18.4221 | 17.9221 | 17.42 | 16.9326 | 16.1495 | 15.3453 | 14.64 | 22.0663 | 22.8368 | 22.4895 | 22.0579 | 21.4968 | 20.9905 | 20.4947 | 19.9958 | 19.5116 | 18.7421 | 17.9495 | 17.2558
|  | REDLANDS PRIMARY | FB |  |  |  |  | 20.8874 | 22.4905 | 22.4211 | 22.3432 | 22.2568 | 22.1695 | 22.0853 | 22.0063 | 21.9221 | 21.6137 | 21.4421 | 21.3337 | 20.4579 | 20.5989 | 20.4168 | 20.2211 | 20.0063 | 19.7905 | 19.5726 | 19.3611 | 19.1421 | 18.2011 | 17.4368 | 16.7821 | 22.2863 | 23.1526 | 22.9726 | 22.7789 | 22.5653 | 22.3526 | 22.1368 | 21.9274 | 21.7105 | 20.78 | 20.0263 | 19.38
MANNINGTON GSP | SALISBURY BSP | REDLYNCH PRIMARY | MINIMUM HEADROOM | SU 19073 20576 | NO | YES | 0 | 13.9529 | 13.8339 | 13.7013 | 13.5139 | 13.2929 | 13.0476 | 12.8066 | 10.8413 | 10.3634 | 9.1161 | 8.1308 | 7.2592 | 11.6374 | 11.4153 | 11.1584 | 10.8479 | 10.4532 | 10.01 | 9.5563 | 6.4521 | 5.9247 | 4.5395 | 3.4268 | 2.4426 | 11.7021 | 11.4842 | 11.2337 | 10.9274 | 10.54 | 10.1063 | 9.6621 | 6.6716 | 6.1568 | 4.8063 | 3.7263 | 2.7705
|  | REDLYNCH PRIMARY | EE |  |  |  |  | 13.9529 | 13.8339 | 13.7034 | 13.535 | 13.3066 | 13.095 | 12.8982 | 12.5118 | 12.2529 | 11.6908 | 10.9929 | 10.4013 | 11.6374 | 11.4153 | 11.1584 | 10.9068 | 10.6079 | 10.3279 | 10.0437 | 8.4563 | 8.1784 | 7.5016 | 6.6984 | 6.0142 | 11.7021 | 11.4842 | 11.2337 | 10.9853 | 10.6895 | 10.4116 | 10.1305 | 8.6 | 8.3253 | 7.6705 | 6.8926 | 6.2326
|  | REDLYNCH PRIMARY | HT |  |  |  |  | 13.9624 | 13.8497 | 13.7013 | 13.5139 | 13.2929 | 13.0476 | 12.8066 | 10.8413 | 10.3634 | 9.1161 | 8.1308 | 7.2592 | 11.6816 | 11.4721 | 11.1847 | 10.8479 | 10.4532 | 10.01 | 9.5563 | 6.4521 | 5.9247 | 4.5395 | 3.4268 | 2.4426 | 11.7453 | 11.54 | 11.2589 | 10.9274 | 10.54 | 10.1063 | 9.6621 | 6.6716 | 6.1568 | 4.8063 | 3.7263 | 2.7705
|  | REDLYNCH PRIMARY | HE |  |  |  |  | 13.9939 | 13.8887 | 13.7718 | 13.6171 | 13.3992 | 13.2034 | 13.0161 | 12.6887 | 12.4982 | 12.4813 | 12.0255 | 11.6097 | 11.7974 | 11.6384 | 11.4363 | 11.2311 | 10.9679 | 10.7279 | 10.4984 | 8.9637 | 8.7374 | 8.4405 | 7.8626 | 7.3732 | 11.8568 | 11.7 | 11.5021 | 11.2989 | 11.0379 | 10.8 | 10.5716 | 9.0905 | 8.8653 | 8.5811 | 8.0253 | 7.5537
|  | REDLYNCH PRIMARY | FB |  |  |  |  | 14.0792 | 14.0266 | 13.9782 | 13.9276 | 13.8708 | 13.8139 | 13.7592 | 13.7076 | 13.6518 | 13.4424 | 13.2971 | 13.1929 | 11.9342 | 11.8132 | 11.71 | 11.6142 | 11.5121 | 11.4089 | 11.3111 | 11.2184 | 11.1226 | 10.6658 | 10.1405 | 9.6858 | 11.9916 | 11.8726 | 11.7726 | 11.6789 | 11.5789 | 11.4779 | 11.3821 | 11.2905 | 11.1968 | 10.7505 | 10.2432 | 9.8032
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | REGENTS PARK PRIMARY | MINIMUM HEADROOM | SU 39267 13050 | NO | YES | 0.16842 | 32.4521 | 32.3668 | 32.2689 | 32.1332 | 31.9689 | 31.7879 | 31.6079 | 31.1584 | 30.6132 | 29.3689 | 28.5532 | 27.8311 | 28.8147 | 28.6389 | 28.3937 | 28.0568 | 27.5589 | 27.1842 | 26.6505 | 26.0189 | 25.3768 | 23.9442 | 23.0263 | 22.2137 | 26.7074 | 26.5347 | 26.2958 | 25.9663 | 25.4811 | 25.1137 | 24.5937 | 23.98 | 23.3547 | 21.9611 | 21.0674 | 20.2779
|  | REGENTS PARK PRIMARY | EE |  |  |  |  | 32.4521 | 32.3668 | 32.2732 | 32.1479 | 31.9711 | 31.8047 | 31.6542 | 31.4963 | 31.3395 | 30.5279 | 29.95 | 29.4374 | 28.8147 | 28.6389 | 28.4526 | 28.2432 | 27.9716 | 27.6568 | 27.2284 | 26.7663 | 26.3537 | 25.28 | 24.5821 | 23.9947 | 26.7074 | 26.5347 | 26.3516 | 26.1453 | 25.8789 | 25.5684 | 25.1495 | 24.7011 | 24.2979 | 23.2611 | 22.5853 | 22.0158
|  | REGENTS PARK PRIMARY | HT |  |  |  |  | 32.4553 | 32.3742 | 32.2689 | 32.1332 | 31.9689 | 31.7879 | 31.6079 | 31.1584 | 30.6132 | 29.3689 | 28.5532 | 27.8311 | 28.8368 | 28.6547 | 28.3937 | 28.0568 | 27.5589 | 27.1842 | 26.6505 | 26.0189 | 25.3768 | 23.9442 | 23.0263 | 22.2137 | 26.7284 | 26.5505 | 26.2958 | 25.9663 | 25.4811 | 25.1137 | 24.5937 | 23.98 | 23.3547 | 21.9611 | 21.0674 | 20.2779
|  | REGENTS PARK PRIMARY | HE |  |  |  |  | 32.47 | 32.3879 | 32.2963 | 32.17 | 31.99 | 31.8289 | 31.6732 | 31.5121 | 31.3563 | 31.3279 | 31.0016 | 30.7026 | 28.9368 | 28.8074 | 28.66 | 28.4811 | 28.2295 | 27.94 | 27.5663 | 27.1589 | 26.8011 | 26.2505 | 25.8474 | 25.4758 | 26.8253 | 26.6968 | 26.5526 | 26.3758 | 26.1263 | 25.8421 | 25.4768 | 25.0789 | 24.7295 | 24.2 | 23.8105 | 23.4516
|  | REGENTS PARK PRIMARY | FB |  |  |  |  | 32.5279 | 32.4858 | 32.4468 | 32.4037 | 32.3553 | 32.3068 | 32.2595 | 32.2153 | 32.1679 | 31.9963 | 31.8995 | 31.6679 | 29.04 | 28.9358 | 28.8537 | 28.7695 | 28.6716 | 28.5695 | 28.4432 | 28.2926 | 28.1432 | 27.3874 | 26.9589 | 26.5547 | 26.9263 | 26.8253 | 26.7453 | 26.6621 | 26.5653 | 26.4663 | 26.3421 | 26.1968 | 26.0505 | 25.3179 | 24.9011 | 24.5105
COWLEY GSP | WITNEY BSP | RISSINGTON PRIMARY | MINIMUM HEADROOM | SP 19225 19563 | YES | YES | 1.0842 | 12.6916 | 12.5463 | 12.4011 | 12.1537 | 11.8095 | 11.4074 | 11.0042 | 10.5832 | 10.1611 | 8.6347 | 7.8063 | 6.9379 | 14.4179 | 14.2621 | 14.1042 | 13.8337 | 13.4537 | 13.0063 | 12.5589 | 12.0895 | 11.6189 | 9.8832 | 8.9453 | 7.9568 | 12.5442 | 12.3905 | 12.2358 | 11.9716 | 11.6011 | 11.1653 | 10.7295 | 10.2726 | 9.8147 | 8.1337 | 7.2242 | 6.2674
|  | RISSINGTON PRIMARY | EE |  |  |  |  | 12.6916 | 12.5463 | 12.4011 | 12.2337 | 12.0053 | 11.7663 | 11.5084 | 11.2589 | 11.0168 | 10.0074 | 9.4189 | 8.7811 | 14.4179 | 14.2621 | 14.1042 | 13.9274 | 13.6842 | 13.4295 | 13.1474 | 12.8768 | 12.6147 | 11.4442 | 10.7695 | 10.0316 | 12.5442 | 12.3905 | 12.2358 | 12.0621 | 11.8221 | 11.5716 | 11.2958 | 11.0305 | 10.7726 | 9.6453 | 8.9937 | 8.2811
|  | RISSINGTON PRIMARY | HT |  |  |  |  | 12.7221 | 12.5821 | 12.4063 | 12.1537 | 11.8095 | 11.4074 | 11.0042 | 10.5832 | 10.1611 | 8.6347 | 7.8063 | 6.9379 | 14.4537 | 14.3021 | 14.1116 | 13.8337 | 13.4537 | 13.0063 | 12.5589 | 12.0895 | 11.6189 | 9.8832 | 8.9453 | 7.9568 | 12.5789 | 12.4295 | 12.2432 | 11.9716 | 11.6011 | 11.1653 | 10.7295 | 10.2726 | 9.8147 | 8.1337 | 7.2242 | 6.2674
|  | RISSINGTON PRIMARY | HE |  |  |  |  | 12.7979 | 12.6926 | 12.5811 | 12.4453 | 12.2579 | 12.0474 | 11.8411 | 11.6453 | 11.4579 | 10.7937 | 10.4021 | 9.9295 | 14.5368 | 14.4263 | 14.3084 | 14.1674 | 13.9737 | 13.7495 | 13.5295 | 13.3221 | 13.1242 | 12.3411 | 11.8853 | 11.3326 | 12.6611 | 12.5516 | 12.4347 | 12.2947 | 12.1021 | 11.8811 | 11.6653 | 11.46 | 11.2653 | 10.5137 | 10.0747 | 9.5432
|  | RISSINGTON PRIMARY | FB |  |  |  |  | 12.9547 | 12.8737 | 12.8105 | 12.7463 | 12.6768 | 12.5916 | 12.5042 | 12.4253 | 12.3453 | 12.0168 | 11.3989 | 10.9947 | 14.7126 | 14.6232 | 14.5558 | 14.4863 | 14.4126 | 14.3189 | 14.2232 | 14.1379 | 14.0495 | 13.6874 | 12.9726 | 12.5053 | 12.8326 | 12.7453 | 12.6789 | 12.6105 | 12.5368 | 12.4453 | 12.3516 | 12.2674 | 12.1811 | 11.8284 | 11.1379 | 10.6874
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | RIVERSIDE PRIMARY | MINIMUM HEADROOM | SU 47846 67187 | NO | YES | 0.025263 | 22.7505 | 22.6926 | 22.6284 | 22.3716 | 22.1653 | 21.9432 | 21.7242 | 21.4663 | 21.2011 | 20.4705 | 19.9895 | 19.5379 | 22.3337 | 21.9674 | 21.6958 | 21.3621 | 21.1411 | 20.9032 | 20.6684 | 20.3884 | 20.1 | 19.3305 | 18.8021 | 18.3063 | 20.4242 | 20.0526 | 19.7768 | 19.4389 | 19.2168 | 18.9758 | 18.7389 | 18.4568 | 18.1653 | 17.3853 | 16.8505 | 16.3474
|  | RIVERSIDE PRIMARY | EE |  |  |  |  | 22.7505 | 22.6926 | 22.6284 | 22.4168 | 22.2589 | 22.1053 | 21.9295 | 21.7495 | 21.5768 | 21.1347 | 20.7653 | 20.4316 | 22.3337 | 21.9674 | 21.6958 | 21.4158 | 21.2516 | 21.0916 | 20.9053 | 20.7137 | 20.5305 | 20.0663 | 19.6505 | 19.2747 | 20.4242 | 20.0526 | 19.7768 | 19.4937 | 19.3284 | 19.1684 | 18.9789 | 18.7863 | 18.6021 | 18.1295 | 17.7084 | 17.3274
|  | RIVERSIDE PRIMARY | HT |  |  |  |  | 22.7568 | 22.7011 | 22.6316 | 22.3716 | 22.1653 | 21.9432 | 21.7242 | 21.4663 | 21.2011 | 20.4705 | 19.9895 | 19.5379 | 22.3474 | 22.0053 | 21.7053 | 21.3621 | 21.1411 | 20.9032 | 20.6684 | 20.3884 | 20.1 | 19.3305 | 18.8021 | 18.3063 | 20.4526 | 20.0905 | 19.7863 | 19.4389 | 19.2168 | 18.9758 | 18.7389 | 18.4568 | 18.1653 | 17.3853 | 16.8505 | 16.3474
|  | RIVERSIDE PRIMARY | HE |  |  |  |  | 22.7621 | 22.7011 | 22.6358 | 22.5432 | 22.3958 | 22.2568 | 22.1221 | 21.9842 | 21.8537 | 21.6589 | 21.4611 | 21.2779 | 22.3589 | 22.0758 | 21.8295 | 21.5663 | 21.4105 | 21.2674 | 21.1295 | 20.9884 | 20.8547 | 20.6284 | 20.4042 | 20.1937 | 20.5084 | 20.1632 | 19.9126 | 19.6474 | 19.4905 | 19.3474 | 19.2084 | 19.0674 | 18.9326 | 18.7021 | 18.4747 | 18.2621
|  | RIVERSIDE PRIMARY | FB |  |  |  |  | 22.8021 | 22.7716 | 22.7432 | 22.7126 | 22.6768 | 22.6421 | 22.6084 | 22.5768 | 22.5421 | 22.4179 | 22.1695 | 21.94 | 22.4042 | 22.3074 | 22.1853 | 22.0684 | 22.0053 | 21.9421 | 21.8811 | 21.8211 | 21.7611 | 21.5189 | 21.1589 | 20.9 | 20.5863 | 20.3968 | 20.2737 | 20.1558 | 20.0916 | 20.0274 | 19.9653 | 19.9053 | 19.8453 | 19.6011 | 19.2358 | 18.9737
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE PRIMARY | MINIMUM HEADROOM | SU 11617 17810 | YES | YES | 0 | 3.9 | 3.8653 | 3.82 | 3.76 | 3.6874 | 3.6116 | 3.5347 | 3.4579 | 3.3768 | 3.1979 | 3.0632 | 2.9474 | 3.8863 | 3.8495 | 3.7989 | 3.7326 | 3.6526 | 3.5705 | 3.4863 | 3.4021 | 3.3126 | 3.1158 | 2.9663 | 2.8379 | 3.8863 | 3.8495 | 3.7989 | 3.7337 | 3.6537 | 3.5716 | 3.4874 | 3.4032 | 3.3137 | 3.1179 | 2.9684 | 2.84
|  | ROCKBOURNE PRIMARY | EE |  |  |  |  | 3.9 | 3.8653 | 3.8326 | 3.7958 | 3.7505 | 3.7084 | 3.6653 | 3.6189 | 3.5747 | 3.4968 | 3.4021 | 3.3316 | 3.8863 | 3.8495 | 3.8137 | 3.7747 | 3.7284 | 3.6832 | 3.6389 | 3.5895 | 3.5442 | 3.4558 | 3.3474 | 3.2663 | 3.8863 | 3.8495 | 3.8137 | 3.7747 | 3.7284 | 3.6842 | 3.6389 | 3.5905 | 3.5442 | 3.4568 | 3.3484 | 3.2674
|  | ROCKBOURNE PRIMARY | HT |  |  |  |  | 3.9032 | 3.8663 | 3.82 | 3.76 | 3.6874 | 3.6116 | 3.5347 | 3.4579 | 3.3768 | 3.1979 | 3.0632 | 2.9474 | 3.8895 | 3.8495 | 3.7989 | 3.7326 | 3.6526 | 3.5705 | 3.4863 | 3.4021 | 3.3126 | 3.1158 | 2.9663 | 2.8379 | 3.8905 | 3.8495 | 3.7989 | 3.7337 | 3.6537 | 3.5716 | 3.4874 | 3.4032 | 3.3137 | 3.1179 | 2.9684 | 2.84
|  | ROCKBOURNE PRIMARY | HE |  |  |  |  | 3.9242 | 3.8989 | 3.8747 | 3.8411 | 3.8021 | 3.7663 | 3.7305 | 3.6947 | 3.6611 | 3.6316 | 3.5726 | 3.5305 | 3.9137 | 3.8863 | 3.8621 | 3.8274 | 3.7874 | 3.7505 | 3.7137 | 3.6768 | 3.6411 | 3.6074 | 3.5389 | 3.4895 | 3.9137 | 3.8874 | 3.8621 | 3.8274 | 3.7874 | 3.7505 | 3.7137 | 3.6768 | 3.6421 | 3.6084 | 3.5389 | 3.4905
|  | ROCKBOURNE PRIMARY | FB |  |  |  |  | 3.9421 | 3.9253 | 3.9105 | 3.8979 | 3.8811 | 3.8674 | 3.8537 | 3.84 | 3.8242 | 3.7653 | 3.6968 | 3.6442 | 3.9337 | 3.9137 | 3.8979 | 3.8853 | 3.8674 | 3.8526 | 3.8368 | 3.8221 | 3.8053 | 3.7411 | 3.6642 | 3.6032 | 3.9337 | 3.9147 | 3.8989 | 3.8853 | 3.8674 | 3.8526 | 3.8368 | 3.8221 | 3.8053 | 3.7411 | 3.6642 | 3.6042
NURSLING GSP | ROWNHAMS BSP | ROMSEY PRIMARY | MINIMUM HEADROOM | SU 36092 21110 | NO | YES | 0 | 16.3842 | 44.0116 | 43.7895 | 43.5284 | 43.1642 | 42.3589 | 41.4084 | 40.5147 | 39.6579 | 34.9916 | 33.6568 | 32.3253 | 11.4432 | 36.4505 | 35.5505 | 34.74 | 33.6747 | 32.6379 | 31.5716 | 30.5726 | 29.6158 | 24.2916 | 22.8032 | 21.3095 | 9.7842 | 36.4347 | 36.2726 | 36.0411 | 35.7411 | 35.4547 | 34.4516 | 33.46 | 32.5095 | 27.2274 | 25.7495 | 24.2674
|  | ROMSEY PRIMARY | EE |  |  |  |  | 16.3842 | 44.0116 | 43.7895 | 43.5284 | 43.1642 | 42.3589 | 41.4084 | 40.5147 | 39.6579 | 36.2295 | 35.2832 | 34.3537 | 11.4432 | 36.5705 | 35.5505 | 34.74 | 33.6747 | 32.6379 | 31.5716 | 30.5726 | 29.6158 | 25.6389 | 24.5642 | 23.5021 | 9.7842 | 36.4347 | 36.2726 | 36.0526 | 35.7411 | 35.4547 | 34.4516 | 33.46 | 32.5095 | 28.5684 | 27.5021 | 26.4474
|  | ROMSEY PRIMARY | HT |  |  |  |  | 16.3968 | 44.0242 | 43.8032 | 43.5284 | 43.1979 | 42.4758 | 41.5053 | 40.5832 | 39.6979 | 34.9916 | 33.6568 | 32.3253 | 11.5095 | 36.4505 | 35.7105 | 34.8968 | 33.8663 | 32.7747 | 31.6926 | 30.6653 | 29.68 | 24.2916 | 22.8032 | 21.3095 | 9.7926 | 36.4568 | 36.2747 | 36.0411 | 35.7632 | 35.4547 | 34.5705 | 33.5505 | 32.5716 | 27.2274 | 25.7495 | 24.2674
|  | ROMSEY PRIMARY | HE |  |  |  |  | 16.4347 | 44.0758 | 43.8684 | 43.6168 | 43.2621 | 42.8253 | 41.9568 | 41.1442 | 40.3663 | 37.5253 | 36.9232 | 36.2916 | 11.6632 | 36.8726 | 35.9284 | 35.1758 | 34.1547 | 33.1695 | 32.1989 | 31.2937 | 30.4295 | 27.1021 | 26.4063 | 25.6726 | 9.8221 | 36.4811 | 36.3295 | 36.1147 | 35.8105 | 35.5379 | 35.0737 | 34.1758 | 33.3158 | 30.0211 | 29.3316 | 28.6042
|  | ROMSEY PRIMARY | FB |  |  |  |  | 16.5442 | 44.2621 | 44.1821 | 44.0863 | 43.9863 | 43.8821 | 43.78 | 43.6832 | 43.58 | 42.7747 | 41.5263 | 40.9084 | 11.8726 | 37.22 | 36.9032 | 36.4558 | 36.0537 | 35.62 | 35.1621 | 34.7147 | 34.26 | 33.0547 | 31.6211 | 30.9158 | 9.9242 | 36.6547 | 36.5926 | 36.5232 | 36.4463 | 36.3674 | 36.2916 | 36.2211 | 36.1453 | 35.8684 | 34.5053 | 33.8063
LOVEDEAN GSP | CHICHESTER BSP | ROSE GREEN PRIMARY | MINIMUM HEADROOM | SZ 89974 99335 | NO | YES | 1.0516 | 16.6874 | 15.8421 | 14.6274 | 13.5189 | 12.2189 | 11.1411 | 9.9474 | 8.7495 | 7.5632 | -1.66 | -3.9326 | -5.8842 | 14.6463 | 13.7263 | 12.3947 | 11.1905 | 9.7821 | 8.6095 | 7.3179 | 6.0189 | 4.7053 | -6.0632 | -8.6358 | -10.8432 | 14.6326 | 13.6705 | 12.2758 | 11.0168 | 9.5474 | 8.3274 | 6.9811 | 5.6274 | 4.2863 | -6.4295 | -9.0021 | -11.2074
|  | ROSE GREEN PRIMARY | EE |  |  |  |  | 16.6874 | 15.8421 | 14.6274 | 13.5189 | 12.2189 | 11.1779 | 10.14 | 9.0863 | 8.0768 | 1.9558 | 0.22 | -1.18 | 14.6463 | 13.7263 | 12.3947 | 11.1905 | 9.7821 | 8.6611 | 7.5421 | 6.4095 | 5.3211 | -1.8726 | -3.8568 | -5.4589 | 14.6326 | 13.6705 | 12.2758 | 11.0168 | 9.5474 | 8.3832 | 7.2189 | 6.04 | 4.9074 | -2.2674 | -4.2547 | -5.8589
|  | ROSE GREEN PRIMARY | HT |  |  |  |  | 16.7853 | 15.9811 | 14.7789 | 13.6263 | 12.3105 | 11.1411 | 9.9474 | 8.7495 | 7.5632 | -1.66 | -3.9326 | -5.8842 | 14.7526 | 13.8768 | 12.56 | 11.3063 | 9.8758 | 8.6095 | 7.3179 | 6.0189 | 4.7053 | -6.0632 | -8.6358 | -10.8432 | 14.7453 | 13.8284 | 12.4495 | 11.14 | 9.6453 | 8.3274 | 6.9811 | 5.6274 | 4.2863 | -6.4295 | -9.0021 | -11.2074
|  | ROSE GREEN PRIMARY | HE |  |  |  |  | 17.0337 | 16.3558 | 15.3063 | 14.3474 | 13.1726 | 12.2537 | 11.3474 | 10.4379 | 9.5358 | 4.14 | 2.8905 | 1.8874 | 15.02 | 14.2779 | 13.1232 | 12.0768 | 10.8011 | 9.8105 | 8.8316 | 7.8495 | 6.8758 | 0.49158 | -0.97053 | -2.1474 | 15.0242 | 14.2484 | 13.0358 | 11.9432 | 10.6126 | 9.5821 | 8.5653 | 7.5432 | 6.5316 | 0.13263 | -1.3274 | -2.5021
|  | ROSE GREEN PRIMARY | FB |  |  |  |  | 17.5474 | 17.1611 | 16.6789 | 16.2705 | 15.8316 | 15.4326 | 15.0189 | 14.5884 | 14.1316 | 11.66 | 10.6684 | 9.8747 | 15.58 | 15.1558 | 14.6242 | 14.1747 | 13.6937 | 13.2558 | 12.8021 | 12.3295 | 11.8263 | 9.0916 | 7.9989 | 7.1221 | 15.6105 | 15.1653 | 14.6074 | 14.1358 | 13.6305 | 13.1726 | 12.6979 | 12.2011 | 11.6737 | 8.7968 | 7.6495 | 6.7274
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | ROSE HILL PRIMARY | MINIMUM HEADROOM | SP 53637 03027 | NO | YES | 0 | 25.3305 | 45.1905 | 45.04 | 44.8316 | 43.3853 | 40.5137 | 37.1484 | 33.7547 | 30.6221 | 22.7663 | 20.0074 | 19.2253 | 23.0442 | 42.7242 | 42.2474 | 41.6326 | 39.2316 | 35.9389 | 32.0295 | 28.0874 | 24.4516 | 15.3284 | 12.1568 | 11.3042 | 24.0358 | 43.8705 | 43.7032 | 43.2453 | 40.9632 | 37.7211 | 33.9147 | 30.0747 | 26.5337 | 17.6474 | 14.5537 | 13.7137
|  | ROSE HILL PRIMARY | EE |  |  |  |  | 25.3305 | 45.1905 | 45.04 | 44.8337 | 44.5432 | 42.8537 | 40.0263 | 37.26 | 34.7905 | 26.8 | 24.4842 | 23.9779 | 23.0442 | 42.7242 | 42.3074 | 41.8537 | 41.3505 | 38.6632 | 35.4095 | 32.2 | 29.34 | 19.9779 | 17.2916 | 16.7253 | 24.0358 | 43.8705 | 43.7032 | 43.4547 | 42.9632 | 40.3989 | 37.2011 | 34.0737 | 31.2863 | 22.1821 | 19.5632 | 19.0084
|  | ROSE HILL PRIMARY | HT |  |  |  |  | 25.3442 | 45.2168 | 45.0495 | 44.8316 | 43.3853 | 40.5137 | 37.1484 | 33.7547 | 30.6221 | 22.7663 | 20.0074 | 19.2253 | 23.0632 | 42.7474 | 42.2474 | 41.6326 | 39.2316 | 35.9389 | 32.0295 | 28.0874 | 24.4516 | 15.3284 | 12.1568 | 11.3042 | 24.0505 | 43.8968 | 43.7095 | 43.2453 | 40.9632 | 37.7211 | 33.9147 | 30.0747 | 26.5337 | 17.6474 | 14.5537 | 13.7137
|  | ROSE HILL PRIMARY | HE |  |  |  |  | 25.3716 | 45.2379 | 45.0874 | 44.8811 | 44.5853 | 43.2411 | 40.42 | 37.6695 | 35.2189 | 27.8947 | 25.8968 | 25.6705 | 23.1232 | 42.9105 | 42.6642 | 42.2663 | 41.7937 | 39.1032 | 35.8663 | 32.6758 | 29.8379 | 21.22 | 18.8811 | 18.6232 | 24.0863 | 43.9316 | 43.7695 | 43.5526 | 43.2463 | 40.8316 | 37.6453 | 34.5368 | 31.7716 | 23.3958 | 21.1211 | 20.8695
|  | ROSE HILL PRIMARY | FB |  |  |  |  | 25.4589 | 45.3863 | 45.32 | 45.2474 | 45.1663 | 45.0842 | 44.7263 | 43.4379 | 42.2211 | 36.2758 | 34.6495 | 34.2811 | 23.2263 | 43.1032 | 43.0105 | 42.9137 | 42.8032 | 42.0705 | 40.7126 | 39.2379 | 37.8453 | 30.9042 | 29.0189 | 28.6042 | 24.1789 | 44.0926 | 44.0189 | 43.94 | 43.8516 | 43.6737 | 42.3884 | 40.9737 | 39.5937 | 32.8368 | 31 | 30.5937
MELKSHAM GSP | CHIPPENHAM BSP | ROWDEN PRIMARY | MINIMUM HEADROOM | ST 90805 72608 | NO | YES | 0.094737 | 22.8147 | 21.4874 | 20.5695 | 18.9337 | 15.9958 | 14.1811 | 21.0389 | 18.4684 | 15.6505 | 10.1432 | 8.2158 | 6.4895 | 22.7021 | 21.1947 | 20.1642 | 18.3168 | 14.9716 | 12.9263 | 19.5105 | 16.5937 | 13.3905 | 7.1474 | 4.9926 | 3.0653 | 23.8726 | 22.5326 | 21.5853 | 19.7105 | 16.3147 | 14.24 | 20.7884 | 17.8274 | 14.5747 | 8.2389 | 6.0663 | 4.1189
|  | ROWDEN PRIMARY | EE |  |  |  |  | 22.8147 | 21.4874 | 20.5695 | 18.9853 | 15.9958 | 14.1811 | 21.4147 | 19.6021 | 17.6674 | 12.7863 | 11.4105 | 10.2221 | 22.7021 | 21.1947 | 20.1642 | 18.3726 | 14.9716 | 12.9263 | 19.9337 | 17.8905 | 15.7021 | 10.0853 | 8.5305 | 7.1842 | 23.8726 | 22.5326 | 21.5853 | 19.7684 | 16.3147 | 14.24 | 21.2179 | 19.1432 | 16.9242 | 11.2137 | 9.6337 | 8.2695
|  | ROWDEN PRIMARY | HT |  |  |  |  | 22.8947 | 21.6011 | 20.6421 | 18.9337 | 16.7421 | 14.4021 | 21.0389 | 18.4684 | 15.6505 | 10.1432 | 8.2158 | 6.4895 | 22.7916 | 21.3211 | 20.2484 | 18.3168 | 15.8347 | 13.1874 | 19.5105 | 16.5937 | 13.3905 | 7.1474 | 4.9926 | 3.0653 | 23.9537 | 22.6484 | 21.6705 | 19.7105 | 17.1916 | 14.5042 | 20.7884 | 17.8274 | 14.5747 | 8.2389 | 6.0663 | 4.1189
|  | ROWDEN PRIMARY | HE |  |  |  |  | 23.0737 | 21.8411 | 21.0074 | 19.4874 | 16.54 | 14.7779 | 22.0684 | 20.3053 | 18.4105 | 14.22 | 13.2347 | 12.3821 | 22.9926 | 21.5937 | 20.6589 | 18.9421 | 15.5895 | 13.6042 | 20.6768 | 18.6905 | 16.5484 | 11.6842 | 10.5558 | 9.5747 | 24.1337 | 22.8905 | 22.0495 | 20.3453 | 16.9421 | 14.9274 | 21.9726 | 19.9579 | 17.7853 | 12.8347 | 11.6874 | 10.6905
|  | ROWDEN PRIMARY | FB |  |  |  |  | 23.4211 | 22.8632 | 22.4789 | 21.8716 | 20.7747 | 19.6947 | 27.9905 | 27.2495 | 26.3895 | 23.2947 | 22.3726 | 21.6032 | 23.3737 | 22.7411 | 22.3084 | 21.6179 | 20.3632 | 19.1274 | 27.3263 | 26.4821 | 25.5 | 21.9684 | 20.9316 | 20.06 | 24.4832 | 23.9211 | 23.5326 | 22.92 | 21.7842 | 20.5284 | 28.7147 | 27.8579 | 26.86 | 23.2726 | 22.2221 | 21.3368
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ROWNER PARK PRIMARY | MINIMUM HEADROOM | SU 58018 00782 | NO | YES | 0 | 23.6821 | 23.4905 | 23.2821 | 22.9642 | 22.6137 | 22.2179 | 21.8432 | 21.48 | 21.0632 | 20.0937 | 19.3916 | 18.7579 | 22.4958 | 22.2989 | 22.0737 | 21.7242 | 21.3411 | 20.9074 | 20.4989 | 20.1053 | 19.6453 | 18.58 | 17.8 | 17.0937 | 22.4158 | 22.2074 | 21.9811 | 21.6358 | 21.2558 | 20.8274 | 20.4242 | 20.0337 | 19.5789 | 18.5274 | 17.7579 | 17.0611
|  | ROWNER PARK PRIMARY | EE |  |  |  |  | 23.6821 | 23.4905 | 23.2968 | 23.0716 | 22.8032 | 22.5442 | 22.2884 | 22.0295 | 21.7789 | 21.3432 | 20.86 | 20.4358 | 22.4958 | 22.2989 | 22.0937 | 21.8537 | 21.5726 | 21.3021 | 21.0316 | 20.7611 | 20.4968 | 20.0053 | 19.4537 | 18.9674 | 22.4158 | 22.2074 | 22.0011 | 21.7611 | 21.4832 | 21.2137 | 20.9453 | 20.6758 | 20.4137 | 19.9295 | 19.3874 | 18.9095
|  | ROWNER PARK PRIMARY | HT |  |  |  |  | 23.7126 | 23.5179 | 23.2821 | 22.9642 | 22.6137 | 22.2179 | 21.8432 | 21.48 | 21.0632 | 20.0937 | 19.3916 | 18.7579 | 22.5263 | 22.3263 | 22.0737 | 21.7242 | 21.3411 | 20.9074 | 20.4989 | 20.1053 | 19.6453 | 18.58 | 17.8 | 17.0937 | 22.4495 | 22.2368 | 21.9811 | 21.6358 | 21.2558 | 20.8274 | 20.4242 | 20.0337 | 19.5789 | 18.5274 | 17.7579 | 17.0611
|  | ROWNER PARK PRIMARY | HE |  |  |  |  | 23.8063 | 23.66 | 23.5042 | 23.3095 | 23.0579 | 22.8253 | 22.5958 | 22.3611 | 22.1368 | 22.0042 | 21.7263 | 21.4779 | 22.6053 | 22.4768 | 22.3179 | 22.1211 | 21.8684 | 21.6337 | 21.3979 | 21.1558 | 20.9242 | 20.7632 | 20.4368 | 20.1442 | 22.5579 | 22.4042 | 22.24 | 22.0379 | 21.78 | 21.5411 | 21.3042 | 21.0632 | 20.8326 | 20.6747 | 20.3547 | 20.0684
|  | ROWNER PARK PRIMARY | FB |  |  |  |  | 23.9305 | 23.8168 | 23.7284 | 23.6358 | 23.5368 | 23.4379 | 23.3389 | 23.2463 | 23.1516 | 22.7695 | 22.42 | 22.1316 | 22.6821 | 22.6232 | 22.5442 | 22.4495 | 22.3484 | 22.2474 | 22.1474 | 22.0484 | 21.9463 | 21.5295 | 21.1337 | 20.8021 | 22.6916 | 22.5663 | 22.4716 | 22.3716 | 22.2663 | 22.16 | 22.0547 | 21.9547 | 21.8537 | 21.4411 | 21.0516 | 20.7263
FAWLEY GSP | COWES BSP | RYDE PRIMARY | MINIMUM HEADROOM | SZ 59554 91973 | NO | YES | 0 | 32.9311 | 32.2237 | 31.4532 | 30.0963 | 28.4805 | 26.8332 | 25.1205 | 23.4584 | 21.7195 | 16.8847 | 14.09 | 11.5237 | 28.7979 | 28.0158 | 27.1674 | 25.6516 | 23.8474 | 22.0158 | 20.1074 | 18.2558 | 16.3126 | 10.8737 | 7.7379 | 4.8547 | 31.9789 | 31.6 | 31.0442 | 29.74 | 27.9484 | 26.1284 | 24.2316 | 22.3926 | 20.4621 | 15.0621 | 11.9484 | 9.0832
|  | RYDE PRIMARY | EE |  |  |  |  | 32.9311 | 32.2237 | 31.4542 | 30.3468 | 29.0395 | 27.8384 | 26.5774 | 25.4111 | 22.4963 | 19.4142 | 17.4668 | 15.7142 | 28.7979 | 28.0158 | 27.1684 | 25.9432 | 24.5084 | 23.1947 | 21.8063 | 20.5305 | 17.1989 | 13.6453 | 11.4158 | 9.4053 | 31.9789 | 31.6 | 31.0463 | 30.0284 | 28.6021 | 27.2958 | 25.9147 | 24.6463 | 21.3411 | 17.8179 | 15.6063 | 13.6116
|  | RYDE PRIMARY | HT |  |  |  |  | 33.0363 | 32.3426 | 31.4532 | 30.0963 | 28.4805 | 26.8332 | 25.1205 | 23.4584 | 21.7195 | 16.8847 | 14.09 | 11.5237 | 28.9189 | 28.1505 | 27.1674 | 25.6516 | 23.8474 | 22.0158 | 20.1074 | 18.2558 | 16.3126 | 10.8737 | 7.7379 | 4.8547 | 31.9968 | 31.6758 | 31.0442 | 29.74 | 27.9484 | 26.1284 | 24.2316 | 22.3926 | 20.4621 | 15.0621 | 11.9484 | 9.0832
|  | RYDE PRIMARY | HE |  |  |  |  | 33.2753 | 32.6963 | 32.0416 | 31.0237 | 29.7711 | 28.6479 | 27.5142 | 26.4732 | 23.6868 | 21.6311 | 20.3079 | 19.0858 | 29.1937 | 28.5621 | 27.8484 | 26.7284 | 25.3589 | 24.1358 | 22.8979 | 21.7695 | 18.5884 | 16.1653 | 14.6253 | 13.1989 | 32.0432 | 31.7453 | 31.3779 | 30.6411 | 29.4463 | 28.2284 | 26.9968 | 25.8747 | 22.7179 | 20.3189 | 18.7926 | 17.38
|  | RYDE PRIMARY | FB |  |  |  |  | 33.6805 | 33.2953 | 32.9679 | 32.5247 | 32.0468 | 31.5721 | 31.0837 | 30.6384 | 30.1268 | 28.1142 | 26.8258 | 25.6616 | 29.6326 | 29.2032 | 28.8389 | 28.3432 | 27.8084 | 27.2768 | 26.7295 | 26.2295 | 25.6547 | 23.3853 | 21.9242 | 20.5895 | 32.2737 | 32.1232 | 31.9874 | 31.8295 | 31.5095 | 31.1884 | 30.8126 | 30.3158 | 29.7453 | 27.4926 | 26.0421 | 24.7179
MANNINGTON GSP | SALISBURY BSP | SALISBURY CENTRAL PRIMARY | MINIMUM HEADROOM | SU 14215 30481 | NO | YES | 0 | 47.8168 | 47.5537 | 47.2463 | 46.8263 | 46.2958 | 45.7747 | 44.3958 | 42.4895 | 40.52 | 35.1463 | 32.4768 | 30.0853 | 46.6695 | 46.4189 | 46.1411 | 45.5747 | 44.7526 | 43.5411 | 41.5011 | 39.2011 | 36.8411 | 30.7421 | 27.7379 | 25.0463 | 42.1242 | 41.5768 | 40.9421 | 40.1253 | 39.3474 | 38.26 | 36.4379 | 34.3937 | 32.2989 | 26.9011 | 24.22 | 21.6168
|  | SALISBURY CENTRAL PRIMARY | EE |  |  |  |  | 47.8168 | 47.5537 | 47.2463 | 46.8379 | 46.2958 | 45.7747 | 45.2042 | 43.8316 | 42.4947 | 38.4895 | 36.5516 | 34.8747 | 46.6695 | 46.4189 | 46.1411 | 45.6263 | 44.7526 | 43.8632 | 42.5358 | 40.9053 | 39.3221 | 34.4937 | 32.2747 | 30.3537 | 42.1242 | 41.5768 | 40.9421 | 40.1705 | 39.3474 | 38.5158 | 37.3137 | 35.8495 | 34.4263 | 30.2579 | 28.3084 | 26.6253
|  | SALISBURY CENTRAL PRIMARY | HT |  |  |  |  | 47.8368 | 47.6 | 47.2621 | 46.8263 | 46.5158 | 45.9432 | 44.3958 | 42.4895 | 40.52 | 35.1463 | 32.4768 | 30.0853 | 46.6895 | 46.4558 | 46.1495 | 45.5747 | 44.7979 | 43.5411 | 41.5011 | 39.2011 | 36.8411 | 30.7421 | 27.7379 | 25.0463 | 42.2263 | 41.7263 | 41.0463 | 40.1253 | 39.4116 | 38.26 | 36.4379 | 34.3937 | 32.2989 | 26.9011 | 24.22 | 21.6168
|  | SALISBURY CENTRAL PRIMARY | HE |  |  |  |  | 47.8811 | 47.6379 | 47.3632 | 46.9621 | 46.4168 | 45.9189 | 45.4042 | 44.7937 | 43.6274 | 40.5758 | 39.22 | 38.0421 | 46.7337 | 46.4905 | 46.2189 | 45.8442 | 45.3189 | 44.7263 | 43.5253 | 42.1189 | 40.7547 | 36.8642 | 35.2895 | 33.9179 | 42.4537 | 42.0253 | 41.4926 | 40.8011 | 40.0263 | 39.2684 | 38.1716 | 36.9011 | 35.6653 | 32.3547 | 30.9916 | 29.8063
|  | SALISBURY CENTRAL PRIMARY | FB |  |  |  |  | 48.0516 | 47.9284 | 47.8179 | 47.6937 | 47.5442 | 47.3842 | 47.2242 | 47.0705 | 46.9032 | 44.7484 | 43.7389 | 42.7137 | 46.9042 | 46.7811 | 46.6705 | 46.5463 | 46.4084 | 46.2695 | 46.1347 | 45.7137 | 45.0979 | 41.6453 | 40.4137 | 39.1484 | 42.7695 | 42.4611 | 42.1884 | 41.8747 | 41.5789 | 41.1811 | 40.7453 | 40.2811 | 39.7337 | 36.7053 | 35.6305 | 34.5211
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | SANDHURST PRIMARY | MINIMUM HEADROOM | SU 83597 60930 | NO | YES | 0 | 31.2847 | 30.7532 | 30.1374 | 29.1174 | 27.8784 | 26.5542 | 25.2963 | 24.01 | 22.7342 | 19.6858 | 17.4721 | 15.4858 | 30.3789 | 29.7579 | 29.04 | 27.8084 | 26.3053 | 24.7053 | 23.1958 | 21.6421 | 20.1011 | 16.3853 | 13.6253 | 11.1389 | 31.8053 | 31.5084 | 31.1621 | 29.9316 | 28.4284 | 26.8284 | 25.3189 | 23.7642 | 22.2232 | 18.5063 | 15.7453 | 13.2579
|  | SANDHURST PRIMARY | EE |  |  |  |  | 31.2847 | 30.7532 | 30.2005 | 29.5437 | 28.7426 | 27.9584 | 27.1984 | 26.4258 | 25.6763 | 24.2889 | 22.8163 | 21.5437 | 30.3789 | 29.7579 | 29.1242 | 28.3905 | 27.5158 | 26.6558 | 25.8137 | 24.9579 | 24.1305 | 22.3453 | 20.4158 | 18.74 | 31.8053 | 31.5084 | 31.1674 | 30.5168 | 29.64 | 28.78 | 27.9358 | 27.08 | 26.2526 | 24.4674 | 22.5379 | 20.8621
|  | SANDHURST PRIMARY | HT |  |  |  |  | 31.3858 | 30.8942 | 30.1374 | 29.1174 | 27.8784 | 26.5542 | 25.2963 | 24.01 | 22.7342 | 19.6858 | 17.4721 | 15.4858 | 30.5126 | 29.9421 | 29.04 | 27.8084 | 26.3053 | 24.7053 | 23.1958 | 21.6421 | 20.1011 | 16.3853 | 13.6253 | 11.1389 | 31.8232 | 31.5379 | 31.1621 | 29.9316 | 28.4284 | 26.8284 | 25.3189 | 23.7642 | 22.2232 | 18.5063 | 15.7453 | 13.2579
|  | SANDHURST PRIMARY | HE |  |  |  |  | 31.6342 | 31.2279 | 30.7858 | 30.2216 | 29.4826 | 28.7837 | 28.1016 | 27.4121 | 26.7437 | 26.1047 | 25.1237 | 24.2658 | 30.8305 | 30.3779 | 29.8905 | 29.2789 | 28.4874 | 27.7368 | 27.0063 | 26.2663 | 25.5516 | 24.6537 | 23.3158 | 22.1389 | 31.8863 | 31.6053 | 31.28 | 30.8379 | 30.2389 | 29.6747 | 29.1221 | 28.3926 | 27.6768 | 26.7768 | 25.4389 | 24.2611
|  | SANDHURST PRIMARY | FB |  |  |  |  | 31.9647 | 31.6753 | 31.4553 | 31.2163 | 30.9542 | 30.6879 | 30.4289 | 30.1805 | 29.9247 | 28.8121 | 27.7763 | 26.9089 | 31.2063 | 30.8579 | 30.6 | 30.3221 | 30.0168 | 29.7084 | 29.4074 | 29.1158 | 28.8189 | 27.4832 | 26.1547 | 25.02 | 32.1 | 31.9653 | 31.8442 | 31.7074 | 31.5568 | 31.4032 | 31.2558 | 31.1189 | 30.9474 | 29.6063 | 28.2779 | 27.1421
FAWLEY GSP | COWES BSP | SANDOWN PRIMARY | MINIMUM HEADROOM | SZ 59877 85052 | NO | YES | 0 | 17.8603 | 17.695 | 17.5087 | 17.2497 | 16.9182 | 16.2066 | 15.3939 | 14.5213 | 13.6782 | 11.4739 | 9.8361 | 8.3339 | 15.8353 | 15.5605 | 15.1342 | 14.5984 | 13.8416 | 13.05 | 12.2089 | 11.3037 | 10.3868 | 7.9353 | 6.0974 | 4.4079 | 15.9863 | 15.5768 | 15.1621 | 14.64 | 13.9053 | 13.1368 | 12.3221 | 11.4463 | 10.6 | 8.3874 | 6.5705 | 4.88
|  | SANDOWN PRIMARY | EE |  |  |  |  | 17.8603 | 17.695 | 17.5087 | 17.2571 | 16.9182 | 16.5918 | 16.2866 | 15.7666 | 15.2203 | 13.8992 | 12.7476 | 11.715 | 15.8353 | 15.5605 | 15.1353 | 14.7532 | 14.3079 | 13.7984 | 13.2216 | 12.6205 | 12.0595 | 10.6689 | 9.3511 | 8.1647 | 15.9863 | 15.5768 | 15.1632 | 14.7863 | 14.3484 | 13.8474 | 13.2853 | 12.7 | 12.1516 | 10.8232 | 9.6674 | 8.6295
|  | SANDOWN PRIMARY | HT |  |  |  |  | 17.8676 | 17.7129 | 17.5087 | 17.2497 | 16.9371 | 16.2066 | 15.3939 | 14.5213 | 13.6782 | 11.4739 | 9.8361 | 8.3339 | 15.8458 | 15.6374 | 15.1342 | 14.5984 | 13.8416 | 13.05 | 12.2089 | 11.3037 | 10.3868 | 7.9353 | 6.0974 | 4.4079 | 16.0484 | 15.6495 | 15.1621 | 14.64 | 13.9053 | 13.1368 | 12.3221 | 11.4463 | 10.6 | 8.3874 | 6.5705 | 4.88
|  | SANDOWN PRIMARY | HE |  |  |  |  | 17.8908 | 17.7308 | 17.5497 | 17.3024 | 16.9634 | 16.6487 | 16.3434 | 16.0308 | 15.7266 | 15.2687 | 14.4918 | 13.7729 | 15.8753 | 15.7058 | 15.5047 | 15.1826 | 14.7742 | 14.3121 | 13.8247 | 13.3068 | 12.8321 | 12.1068 | 11.2847 | 10.4805 | 16.1937 | 15.8621 | 15.5158 | 15.1968 | 14.7926 | 14.3379 | 13.86 | 13.3526 | 12.8874 | 12.2 | 11.4189 | 10.6958
|  | SANDOWN PRIMARY | FB |  |  |  |  | 18.0171 | 17.9403 | 17.8718 | 17.795 | 17.7097 | 17.6234 | 17.5403 | 17.4624 | 17.3782 | 17.0729 | 16.4329 | 15.7466 | 16.0079 | 15.9237 | 15.8489 | 15.7689 | 15.6795 | 15.5879 | 15.4026 | 15.2026 | 15.0121 | 14.0668 | 13.2711 | 12.55 | 16.4421 | 16.2211 | 16.0484 | 15.9032 | 15.7516 | 15.5989 | 15.4189 | 15.2242 | 15.04 | 14.1274 | 13.3642 | 12.6737
LOVEDEAN GSP | CHICHESTER BSP | SELSEY PRIMARY | MINIMUM HEADROOM | SZ 85667 94289 | NO | YES | 10.2632 | 16.6834 | 16.4792 | 16.195 | 15.815 | 15.3645 | 14.8792 | 14.4087 | 13.8971 | 13.3361 | 11.5782 | 10.195 | 8.9687 | 14.5037 | 14.2353 | 13.8311 | 13.2963 | 12.6637 | 11.99 | 11.3384 | 10.6026 | 9.8395 | 8.0132 | 6.5711 | 5.2911 | 15.4653 | 15.2032 | 14.8126 | 14.2937 | 13.6811 | 13.0274 | 12.3937 | 11.6821 | 10.9442 | 9.0516 | 7.4958 | 6.1158
|  | SELSEY PRIMARY | EE |  |  |  |  | 16.6834 | 16.4792 | 16.255 | 15.9939 | 15.6708 | 15.3624 | 15.0518 | 14.7339 | 14.4087 | 12.6318 | 11.6413 | 10.7961 | 14.5037 | 14.2353 | 13.9395 | 13.6226 | 13.2542 | 12.9037 | 12.5279 | 12.1447 | 11.7426 | 9.0953 | 8.0553 | 7.1647 | 15.4653 | 15.2032 | 14.9158 | 14.6042 | 14.2411 | 13.8947 | 13.5253 | 13.1484 | 12.7547 | 10.1874 | 9.0505 | 8.0779
|  | SELSEY PRIMARY | HT |  |  |  |  | 16.7076 | 16.4918 | 16.195 | 15.815 | 15.3645 | 14.8792 | 14.4087 | 13.8971 | 13.3361 | 11.5782 | 10.195 | 8.9687 | 14.5458 | 14.2511 | 13.8311 | 13.2963 | 12.6637 | 11.99 | 11.3384 | 10.6026 | 9.8395 | 8.0132 | 6.5711 | 5.2911 | 15.5053 | 15.2189 | 14.8126 | 14.2937 | 13.6811 | 13.0274 | 12.3937 | 11.6821 | 10.9442 | 9.0516 | 7.4958 | 6.1158
|  | SELSEY PRIMARY | HE |  |  |  |  | 16.7982 | 16.6413 | 16.4539 | 16.2255 | 15.9287 | 15.6561 | 15.3908 | 15.1161 | 14.8329 | 13.7676 | 13.175 | 12.5887 | 14.6932 | 14.5016 | 14.2711 | 14.0079 | 13.6816 | 13.3816 | 13.09 | 12.7879 | 12.4647 | 10.3679 | 9.6542 | 9.0342 | 15.6463 | 15.4589 | 15.2326 | 14.9737 | 14.6505 | 14.3526 | 14.0642 | 13.7642 | 13.4453 | 11.4589 | 10.7758 | 10.0905
|  | SELSEY PRIMARY | FB |  |  |  |  | 16.9266 | 16.8213 | 16.7339 | 16.6434 | 16.5466 | 16.4487 | 16.3539 | 16.2655 | 16.1655 | 15.7666 | 15.355 | 15.0097 | 14.8532 | 14.7058 | 14.5868 | 14.4689 | 14.3437 | 14.2174 | 14.0963 | 13.9805 | 13.85 | 13.3016 | 12.6258 | 12.0332 | 15.8032 | 15.6611 | 15.5442 | 15.4295 | 15.3074 | 15.1842 | 15.0663 | 14.9537 | 14.8253 | 14.2937 | 13.6453 | 13.0789
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY PRIMARY | MINIMUM HEADROOM | ST 85605 23325 | NO | YES | 0 | 26.7074 | 26.4147 | 26.0442 | 25.5053 | 24.86 | 24.1526 | 23.4411 | 22.6937 | 21.9389 | 14.3632 | 9.5337 | 6.8032 | 22.5463 | 22.2263 | 21.8158 | 21.2189 | 20.5042 | 19.7211 | 18.9316 | 18.1 | 17.2589 | 8.4474 | 2.8274 | -0.32842 | 24.0537 | 23.7389 | 23.3358 | 22.7505 | 22.0495 | 21.28 | 20.4947 | 19.6653 | 18.8263 | 10.0389 | 4.4347 | 1.2874
|  | SHAFTESBURY PRIMARY | EE |  |  |  |  | 26.7074 | 26.4147 | 26.0989 | 25.7295 | 25.2821 | 24.8568 | 24.4242 | 23.9874 | 23.5611 | 20.0832 | 17.9189 | 15.3863 | 22.5463 | 22.2263 | 21.88 | 21.48 | 21.0032 | 20.5495 | 20.0821 | 19.6126 | 19.1537 | 15.0874 | 12.5674 | 9.6063 | 24.0537 | 23.7389 | 23.3979 | 23.0042 | 22.5326 | 22.0853 | 21.6242 | 21.1611 | 20.7084 | 16.66 | 14.1474 | 11.1958
|  | SHAFTESBURY PRIMARY | HT |  |  |  |  | 26.7516 | 26.4484 | 26.0442 | 25.5053 | 24.86 | 24.1526 | 23.4411 | 22.6937 | 21.9389 | 14.3632 | 9.5337 | 6.8032 | 22.5968 | 22.2611 | 21.8158 | 21.2189 | 20.5042 | 19.7211 | 18.9316 | 18.1 | 17.2589 | 8.4474 | 2.8274 | -0.32842 | 24.1032 | 23.7737 | 23.3358 | 22.7505 | 22.0495 | 21.28 | 20.4947 | 19.6653 | 18.8263 | 10.0389 | 4.4347 | 1.2874
|  | SHAFTESBURY PRIMARY | HE |  |  |  |  | 26.8895 | 26.6642 | 26.4063 | 26.0842 | 25.6726 | 25.2937 | 24.9242 | 24.5537 | 24.1937 | 21.2021 | 19.3347 | 17.0495 | 22.7526 | 22.5105 | 22.2326 | 21.8874 | 21.4526 | 21.0505 | 20.6579 | 20.2653 | 19.8842 | 16.3568 | 14.1653 | 11.4789 | 24.2558 | 24.0168 | 23.7421 | 23.4011 | 22.9705 | 22.5737 | 22.1853 | 21.7979 | 21.42 | 17.9274 | 15.7421 | 13.0632
|  | SHAFTESBURY PRIMARY | FB |  |  |  |  | 27.0526 | 26.8947 | 26.7663 | 26.6242 | 26.4726 | 26.3189 | 26.1632 | 26.0126 | 25.8589 | 24.8853 | 23.0316 | 20.9937 | 22.9295 | 22.7547 | 22.6126 | 22.4568 | 22.2905 | 22.1211 | 21.9505 | 21.7842 | 21.6158 | 20.5126 | 18.3526 | 15.9674 | 24.4295 | 24.2579 | 24.1179 | 23.9653 | 23.8021 | 23.6358 | 23.4684 | 23.3042 | 23.1389 | 22.0611 | 19.92 | 17.5421
FAWLEY GSP | COWES BSP | SHALFLEET PRIMARY | MINIMUM HEADROOM | SZ 40828 88643 | NO | YES | 0 | 15.6592 | 15.5161 | 15.3708 | 15.1666 | 14.9192 | 14.6466 | 13.8097 | 11.6382 | 11.3118 | 7.4045 | 6.7308 | 6.1203 | 13.6468 | 13.4784 | 13.3089 | 13.0742 | 12.7868 | 12.4721 | 11.4953 | 8.9668 | 8.61 | 4.0763 | 3.3226 | 2.6384 | 13.6737 | 13.5926 | 13.4947 | 13.3663 | 13.2116 | 12.9874 | 12.0137 | 9.4926 | 9.1368 | 4.6158 | 3.8632 | 3.18
|  | SHALFLEET PRIMARY | EE |  |  |  |  | 15.6592 | 15.5161 | 15.3708 | 15.1982 | 14.9939 | 14.795 | 14.3392 | 13.8476 | 12.9582 | 10.9739 | 10.5097 | 10.1055 | 13.6468 | 13.4784 | 13.3089 | 13.1153 | 12.8932 | 12.6784 | 12.1132 | 11.8205 | 10.5384 | 8.2184 | 7.6858 | 7.2216 | 13.6747 | 13.5926 | 13.5021 | 13.3789 | 13.2137 | 13.0547 | 12.6295 | 12.4663 | 11.0589 | 8.7442 | 8.2137 | 7.7516
|  | SHALFLEET PRIMARY | HT |  |  |  |  | 15.6803 | 15.5476 | 15.3771 | 15.1666 | 14.9192 | 14.6466 | 13.8097 | 11.6382 | 11.3118 | 7.4045 | 6.7308 | 6.1203 | 13.6784 | 13.5195 | 13.3205 | 13.0742 | 12.7868 | 12.4721 | 11.4953 | 8.9668 | 8.61 | 4.0763 | 3.3226 | 2.6384 | 13.6737 | 13.5979 | 13.4947 | 13.3663 | 13.2116 | 12.9874 | 12.0137 | 9.4926 | 9.1368 | 4.6158 | 3.8632 | 3.18
|  | SHALFLEET PRIMARY | HE |  |  |  |  | 15.7424 | 15.6339 | 15.5192 | 15.375 | 15.1887 | 15.0171 | 14.615 | 13.5308 | 13.3476 | 11.6687 | 11.3803 | 11.1224 | 13.7616 | 13.6384 | 13.51 | 13.3532 | 13.1574 | 12.9742 | 12.4626 | 11.1784 | 10.9889 | 9.0058 | 8.67 | 8.3679 | 13.6874 | 13.6105 | 13.5263 | 13.4105 | 13.2505 | 13.1032 | 12.9579 | 11.6979 | 11.5074 | 9.5316 | 9.1958 | 8.8947
|  | SHALFLEET PRIMARY | FB |  |  |  |  | 15.8382 | 15.7645 | 15.7076 | 15.6466 | 15.5824 | 15.5182 | 15.4539 | 15.3908 | 15.3255 | 15.0403 | 14.7624 | 14.4824 | 13.8689 | 13.7784 | 13.7111 | 13.6374 | 13.5626 | 13.4868 | 13.4121 | 13.3363 | 13.2595 | 12.9111 | 12.5511 | 12.2289 | 13.7526 | 13.7189 | 13.6884 | 13.6537 | 13.6147 | 13.5768 | 13.5389 | 13.5042 | 13.4663 | 13.3295 | 13.0674 | 12.7463
FAWLEY GSP | COWES BSP | SHANKLIN PRIMARY | MINIMUM HEADROOM | SZ 57809 81912 | NO | YES | 0 | 30.5005 | 30.1668 | 29.8205 | 29.2974 | 28.6732 | 27.9784 | 27.2542 | 25.5216 | 24.7374 | 28.91 | 28.1605 | 27.4837 | 27.46 | 27.0832 | 26.6968 | 26.1095 | 25.4063 | 24.6232 | 23.8011 | 21.6832 | 20.7811 | 25.6642 | 24.7558 | 23.9211 | 28.2789 | 27.9316 | 27.5726 | 27.0295 | 26.38 | 25.6568 | 24.8442 | 22.7253 | 21.8232 | 26.6242 | 25.8 | 24.9642
|  | SHANKLIN PRIMARY | EE |  |  |  |  | 30.5005 | 30.1668 | 29.8205 | 29.4216 | 28.9479 | 28.4858 | 27.9826 | 26.9784 | 26.4679 | 34.5079 | 33.8795 | 32.8711 | 27.46 | 27.0832 | 26.6968 | 26.2632 | 25.7621 | 25.2716 | 24.72 | 23.5284 | 22.9684 | 30.8842 | 30.6758 | 30.5116 | 28.2789 | 27.9316 | 27.5726 | 27.1632 | 26.68 | 26.2084 | 25.6916 | 24.5716 | 24.0116 | 34.3832 | 34.1747 | 34.0095
|  | SHANKLIN PRIMARY | HT |  |  |  |  | 30.5605 | 30.2395 | 29.8289 | 29.2974 | 28.6732 | 27.9784 | 27.2542 | 25.5216 | 24.7374 | 32.2553 | 30.63 | 29.1521 | 27.5358 | 27.1716 | 26.7095 | 26.1095 | 25.4063 | 24.6232 | 23.8011 | 21.6832 | 20.7811 | 30.1326 | 29.5968 | 29.1263 | 28.3453 | 28.0095 | 27.5832 | 27.0295 | 26.38 | 25.6568 | 24.8442 | 22.7253 | 21.8232 | 33.6305 | 33.0947 | 32.6253
|  | SHANKLIN PRIMARY | HE |  |  |  |  | 30.7079 | 30.45 | 30.1763 | 29.8332 | 29.3953 | 28.9858 | 28.5711 | 27.6563 | 27.2321 | 34.8426 | 34.7921 | 34.7595 | 27.7168 | 27.4368 | 27.1421 | 26.7779 | 26.3221 | 25.8947 | 25.4579 | 24.3821 | 23.9316 | 31.2189 | 31.1684 | 31.1358 | 28.5021 | 28.2379 | 27.9579 | 27.6074 | 27.1632 | 26.7495 | 26.3274 | 25.3611 | 24.9284 | 34.7179 | 34.6674 | 34.6347
|  | SHANKLIN PRIMARY | FB |  |  |  |  | 30.9553 | 30.77 | 30.6289 | 30.4774 | 30.3163 | 30.1553 | 29.9974 | 29.8342 | 29.67 | 28.91 | 28.1605 | 27.4837 | 27.9947 | 27.7811 | 27.6211 | 27.4495 | 27.2705 | 27.0905 | 26.9147 | 26.7295 | 26.5442 | 25.6642 | 24.7558 | 23.9211 | 28.76 | 28.5653 | 28.4179 | 28.26 | 28.0937 | 27.9263 | 27.7632 | 27.5926 | 27.4221 | 26.6242 | 25.8 | 24.9642
AXMINSTER GSP | YEOVIL BSP | SHERBORNE PRIMARY | MINIMUM HEADROOM | ST 63978 18163 | NO | YES | 0 | 16.9961 | 16.8876 | 16.7592 | 16.5718 | 16.2161 | 15.5497 | 14.8834 | 14.1982 | 13.5224 | 11.9087 | 10.8308 | 9.8466 | 14.5132 | 14.3595 | 13.9742 | 13.4468 | 12.7416 | 11.9953 | 11.2479 | 10.4784 | 9.7205 | 7.9058 | 6.6911 | 5.5805 | 13.2221 | 12.9968 | 12.6526 | 12.18 | 11.5526 | 10.8863 | 10.2211 | 9.5368 | 8.8621 | 7.2516 | 6.1747 | 5.1926
|  | SHERBORNE PRIMARY | EE |  |  |  |  | 16.9961 | 16.8876 | 16.7634 | 16.5992 | 16.3771 | 16.1687 | 15.9729 | 15.5792 | 15.2024 | 14.2434 | 13.4571 | 12.7613 | 14.5132 | 14.3605 | 14.0868 | 13.7626 | 13.3721 | 12.9616 | 12.5247 | 12.0921 | 11.6816 | 10.5795 | 9.6784 | 8.8816 | 13.2221 | 12.9968 | 12.7474 | 12.4495 | 12.0842 | 11.7074 | 11.3084 | 10.9158 | 10.5389 | 9.5821 | 8.7958 | 8.1021
|  | SHERBORNE PRIMARY | HT |  |  |  |  | 17.0024 | 16.9024 | 16.7592 | 16.5718 | 16.2161 | 15.5497 | 14.8834 | 14.1982 | 13.5224 | 11.9087 | 10.8308 | 9.8466 | 14.5195 | 14.3595 | 13.9742 | 13.4468 | 12.7416 | 11.9953 | 11.2479 | 10.4784 | 9.7205 | 7.9058 | 6.6911 | 5.5805 | 13.2453 | 12.9989 | 12.6526 | 12.18 | 11.5526 | 10.8863 | 10.2211 | 9.5368 | 8.8621 | 7.2516 | 6.1747 | 5.1926
|  | SHERBORNE PRIMARY | HE |  |  |  |  | 17.0171 | 16.9171 | 16.8045 | 16.6413 | 16.4182 | 16.2171 | 16.0213 | 15.8203 | 15.6076 | 15.0329 | 14.4739 | 13.9718 | 14.5342 | 14.4342 | 14.3132 | 14.0226 | 13.6532 | 13.2711 | 12.8868 | 12.5079 | 12.1532 | 11.4763 | 10.8279 | 10.2426 | 13.3389 | 13.1568 | 12.9442 | 12.6737 | 12.3284 | 11.9758 | 11.6221 | 11.2716 | 10.9432 | 10.3705 | 9.8126 | 9.3116
|  | SHERBORNE PRIMARY | FB |  |  |  |  | 17.095 | 17.0497 | 17.0097 | 16.9645 | 16.9087 | 16.8518 | 16.7961 | 16.7424 | 16.6866 | 16.4697 | 16.0097 | 15.5676 | 14.6121 | 14.5668 | 14.5268 | 14.4816 | 14.3816 | 14.2458 | 14.09 | 13.9342 | 13.7795 | 13.0668 | 12.4984 | 11.99 | 13.4674 | 13.3516 | 13.2495 | 13.14 | 13.0179 | 12.8958 | 12.7558 | 12.6168 | 12.4779 | 11.8453 | 11.3463 | 10.9042
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE PRIMARY | MINIMUM HEADROOM | SP 03884 19102 | NO | YES | 0 | 4.1832 | 4.1368 | 4.0884 | 3.9516 | 3.7768 | 3.6611 | 3.5453 | 3.4274 | 3.3095 | 3.0042 | 2.7832 | 2.5589 | 3.8947 | 3.8421 | 3.7884 | 3.6263 | 3.4179 | 3.2853 | 3.1526 | 3.0179 | 2.8832 | 2.5284 | 2.2684 | 2.0021 | 3.7842 | 3.7316 | 3.6789 | 3.5168 | 3.3084 | 3.1768 | 3.0442 | 2.9095 | 2.7758 | 2.4211 | 2.1611 | 1.8958
|  | SHIPTON OLIFFE PRIMARY | EE |  |  |  |  | 4.1832 | 4.1368 | 4.0884 | 3.9716 | 3.8263 | 3.7558 | 3.68 | 3.6063 | 3.5368 | 3.3653 | 3.2137 | 3.0579 | 3.8947 | 3.8421 | 3.7884 | 3.6505 | 3.4789 | 3.4011 | 3.3168 | 3.2358 | 3.1589 | 2.9537 | 2.7716 | 2.5821 | 3.7842 | 3.7316 | 3.6789 | 3.5411 | 3.3695 | 3.2926 | 3.2084 | 3.1263 | 3.0495 | 2.8463 | 2.6632 | 2.4747
|  | SHIPTON OLIFFE PRIMARY | HT |  |  |  |  | 4.1947 | 4.1474 | 4.0916 | 3.9516 | 3.7768 | 3.6611 | 3.5453 | 3.4274 | 3.3095 | 3.0042 | 2.7832 | 2.5589 | 3.9074 | 3.8537 | 3.7926 | 3.6263 | 3.4179 | 3.2853 | 3.1526 | 3.0179 | 2.8832 | 2.5284 | 2.2684 | 2.0021 | 3.7979 | 3.7442 | 3.6832 | 3.5168 | 3.3084 | 3.1768 | 3.0442 | 2.9095 | 2.7758 | 2.4211 | 2.1611 | 1.8958
|  | SHIPTON OLIFFE PRIMARY | HE |  |  |  |  | 4.2211 | 4.1916 | 4.1537 | 4.0495 | 3.9158 | 3.8547 | 3.7926 | 3.7337 | 3.6768 | 3.5937 | 3.4947 | 3.3863 | 3.9389 | 3.9063 | 3.8663 | 3.7411 | 3.5853 | 3.5189 | 3.4516 | 3.3884 | 3.3274 | 3.2263 | 3.1042 | 2.9705 | 3.8284 | 3.7958 | 3.7558 | 3.6316 | 3.4758 | 3.4095 | 3.3432 | 3.28 | 3.2189 | 3.1168 | 2.9958 | 2.8621
|  | SHIPTON OLIFFE PRIMARY | FB |  |  |  |  | 4.2589 | 4.2326 | 4.2137 | 4.1663 | 4.1168 | 4.0884 | 4.0621 | 4.0389 | 4.0147 | 3.9147 | 3.8189 | 3.7126 | 3.9832 | 3.9526 | 3.9316 | 3.8747 | 3.8147 | 3.7821 | 3.7537 | 3.7274 | 3.7 | 3.5853 | 3.4705 | 3.34 | 3.8726 | 3.8432 | 3.8211 | 3.7642 | 3.7053 | 3.6726 | 3.6432 | 3.6179 | 3.5905 | 3.4758 | 3.3611 | 3.2316
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | SHIRLEY PRIMARY | MINIMUM HEADROOM | SU 39988 13808 | NO | YES | 0 | 33.6805 | 33.4637 | 33.2195 | 32.8668 | 32.4374 | 32.0068 | 31.3889 | 30.5047 | 29.4711 | 26.6584 | 24.8068 | 23.1532 | 30.3558 | 30.1368 | 29.8916 | 29.5368 | 28.9947 | 28.4053 | 27.6937 | 26.7274 | 25.5842 | 22.4474 | 20.3789 | 18.5316 | 26.8495 | 26.4495 | 25.8832 | 25.0768 | 24.0632 | 23.4853 | 22.7958 | 21.8695 | 20.7811 | 17.8032 | 15.84 | 14.0895
|  | SHIRLEY PRIMARY | EE |  |  |  |  | 33.6805 | 33.4637 | 33.23 | 32.9184 | 32.4816 | 32.0742 | 31.6942 | 31.3079 | 30.9279 | 29.8395 | 28.5037 | 27.3689 | 30.3558 | 30.1368 | 29.9032 | 29.5905 | 29.1526 | 28.7432 | 28.3621 | 27.9758 | 27.4642 | 26.0421 | 24.5232 | 23.2284 | 26.8495 | 26.4495 | 26.0242 | 25.5421 | 24.9042 | 24.28 | 23.6305 | 23.0747 | 22.5337 | 21.1937 | 19.7642 | 18.5484
|  | SHIRLEY PRIMARY | HT |  |  |  |  | 33.6953 | 33.4911 | 33.2195 | 32.8668 | 32.4374 | 32.0068 | 31.3889 | 30.5047 | 29.4711 | 26.6584 | 24.8068 | 23.1532 | 30.3705 | 30.1653 | 29.8916 | 29.5368 | 28.9947 | 28.4053 | 27.6937 | 26.7274 | 25.5842 | 22.4474 | 20.3789 | 18.5316 | 26.8989 | 26.4895 | 25.8832 | 25.0768 | 24.0632 | 23.4853 | 22.7958 | 21.8695 | 20.7811 | 17.8032 | 15.84 | 14.0895
|  | SHIRLEY PRIMARY | HE |  |  |  |  | 33.7374 | 33.5321 | 33.31 | 33.0016 | 32.5637 | 32.1711 | 31.7858 | 31.4026 | 31.0247 | 31.0195 | 30.6963 | 29.9437 | 30.4137 | 30.2074 | 29.9853 | 29.6758 | 29.2368 | 28.8432 | 28.4579 | 28.0737 | 27.6947 | 27.6884 | 27.0011 | 26.1274 | 27.1137 | 26.8105 | 26.4716 | 26.0547 | 25.4589 | 24.8947 | 24.3232 | 23.8579 | 23.4021 | 22.9505 | 22.1032 | 21.2884
|  | SHIRLEY PRIMARY | FB |  |  |  |  | 33.8858 | 33.7732 | 33.6742 | 33.5647 | 33.4416 | 33.3174 | 33.1963 | 33.0816 | 32.9626 | 32.5226 | 32.2447 | 31.7153 | 30.5621 | 30.4495 | 30.3495 | 30.24 | 30.1168 | 29.9916 | 29.8695 | 29.7547 | 29.6347 | 29.1926 | 28.8568 | 27.9905 | 27.3516 | 27.1158 | 26.9295 | 26.7368 | 26.5084 | 26.2716 | 26.0274 | 25.7905 | 25.5895 | 24.7632 | 23.9211 | 23.1074
MINETY GSP | STRATTON (RESERVE) BSP | SHRIVENHAM PRIMARY | MINIMUM HEADROOM | SU 23782 87902 | NO | YES | 0 | 16.7263 | 16.6316 | 16.5211 | 16.2716 | 15.9579 | 15.6379 | 15.3189 | 14.98 | 14.64 | 14.0442 | 13.6221 | 13.1347 | 14.1189 | 14.0126 | 13.8916 | 13.5979 | 13.2263 | 12.8505 | 12.4758 | 12.0747 | 11.6737 | 11 | 10.5347 | 9.9895 | 15.32 | 15.2147 | 15.0926 | 14.8 | 14.4295 | 14.0537 | 13.6789 | 13.28 | 12.8779 | 12.2063 | 11.7421 | 11.1968
|  | SHRIVENHAM PRIMARY | EE |  |  |  |  | 16.7337 | 16.6368 | 16.5326 | 16.4221 | 16.1526 | 15.8905 | 15.6242 | 15.3537 | 15.0863 | 14.6158 | 14.3768 | 14.0716 | 14.1295 | 14.02 | 13.9042 | 13.7842 | 13.4695 | 13.1621 | 12.8495 | 12.5305 | 12.2168 | 11.6453 | 11.3611 | 11.0126 | 15.3316 | 15.2221 | 15.1063 | 14.9863 | 14.6726 | 14.3653 | 14.0526 | 13.7347 | 13.4211 | 12.8505 | 12.5653 | 12.2179
|  | SHRIVENHAM PRIMARY | HT |  |  |  |  | 16.7263 | 16.6316 | 16.5211 | 16.2716 | 15.9579 | 15.6379 | 15.3189 | 14.98 | 14.64 | 14.0442 | 13.6221 | 13.1347 | 14.1189 | 14.0126 | 13.8916 | 13.5979 | 13.2263 | 12.8505 | 12.4758 | 12.0747 | 11.6737 | 11 | 10.5347 | 9.9895 | 15.32 | 15.2147 | 15.0926 | 14.8 | 14.4295 | 14.0537 | 13.6789 | 13.28 | 12.8779 | 12.2063 | 11.7421 | 11.1968
|  | SHRIVENHAM PRIMARY | HE |  |  |  |  | 16.8105 | 16.7442 | 16.6674 | 16.5758 | 16.4589 | 16.2147 | 15.9705 | 15.7253 | 15.4832 | 15.0358 | 14.8989 | 14.7 | 14.22 | 14.1474 | 14.0642 | 13.9674 | 13.8442 | 13.5589 | 13.2726 | 12.9853 | 12.7021 | 12.1421 | 11.9758 | 11.7284 | 15.4221 | 15.3495 | 15.2663 | 15.1695 | 15.0463 | 14.7611 | 14.4747 | 14.1884 | 13.9053 | 13.3463 | 13.18 | 12.9337
|  | SHRIVENHAM PRIMARY | FB |  |  |  |  | 16.9126 | 16.8579 | 16.8158 | 16.7716 | 16.6779 | 16.5768 | 16.4684 | 16.3547 | 16.2326 | 15.9484 | 15.7579 | 15.5789 | 14.3421 | 14.2789 | 14.2316 | 14.1821 | 14.0695 | 13.9484 | 13.8189 | 13.6811 | 13.5326 | 13.1989 | 12.9716 | 12.7526 | 15.5432 | 15.48 | 15.4337 | 15.3832 | 15.2716 | 15.1505 | 15.0211 | 14.8832 | 14.7347 | 14.4021 | 14.1747 | 13.9568
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON PRIMARY | MINIMUM HEADROOM | ST 85356 13659 | NO | YES | 0 | 22.96 | 22.6705 | 22.2621 | 21.7 | 21.0137 | 20.2653 | 19.5232 | 16.3453 | 15.5863 | 7.0926 | 0.065263 | -3.5495 | 20.5937 | 20.2726 | 19.8074 | 19.1747 | 18.4074 | 17.5716 | 16.7421 | 13.0284 | 12.1768 | 2.2568 | -5.9558 | -10.1568 | 20.6621 | 20.3432 | 19.8853 | 19.2589 | 18.5 | 17.6737 | 16.8537 | 13.1958 | 12.3547 | 2.4726 | -5.7168 | -9.9053
|  | SHROTON PRIMARY | EE |  |  |  |  | 22.96 | 22.6705 | 22.3558 | 21.9874 | 21.5358 | 21.1063 | 20.6726 | 19.0295 | 18.6074 | 14.9305 | 12.0905 | 8.5084 | 20.5937 | 20.2726 | 19.9221 | 19.5168 | 19.0284 | 18.5674 | 18.0958 | 16.1947 | 15.7389 | 11.4179 | 8.0863 | 3.8884 | 20.6621 | 20.3432 | 19.9958 | 19.5937 | 19.1074 | 18.6484 | 18.1832 | 16.3084 | 15.8558 | 11.6 | 8.2779 | 4.0874
|  | SHROTON PRIMARY | HT |  |  |  |  | 22.9926 | 22.6832 | 22.2621 | 21.7 | 21.0137 | 20.2653 | 19.5232 | 16.3453 | 15.5863 | 7.0926 | 0.065263 | -3.5495 | 20.6326 | 20.2842 | 19.8074 | 19.1747 | 18.4074 | 17.5716 | 16.7421 | 13.0284 | 12.1768 | 2.2568 | -5.9558 | -10.1568 | 20.7 | 20.3558 | 19.8853 | 19.2589 | 18.5 | 17.6737 | 16.8537 | 13.1958 | 12.3547 | 2.4726 | -5.7168 | -9.9053
|  | SHROTON PRIMARY | HE |  |  |  |  | 23.1242 | 22.9021 | 22.6453 | 22.3242 | 21.9074 | 21.5274 | 21.1526 | 19.5663 | 19.2032 | 15.9526 | 13.3758 | 10.0232 | 20.7853 | 20.5421 | 20.2579 | 19.9084 | 19.46 | 19.0495 | 18.6442 | 16.8095 | 16.4211 | 12.5674 | 9.5242 | 5.5695 | 20.8516 | 20.6105 | 20.3295 | 19.9832 | 19.5368 | 19.1295 | 18.7274 | 16.9189 | 16.5337 | 12.7442 | 9.7253 | 5.7821
|  | SHROTON PRIMARY | FB |  |  |  |  | 23.2905 | 23.14 | 23.0137 | 22.8779 | 22.7263 | 22.5758 | 22.4232 | 22.2726 | 22.1179 | 20.9611 | 18.3695 | 15.4158 | 20.9663 | 20.7958 | 20.6537 | 20.5011 | 20.3316 | 20.1632 | 19.9905 | 19.8221 | 19.6474 | 18.3158 | 15.2705 | 11.7895 | 21.0316 | 20.8632 | 20.7232 | 20.5716 | 20.4042 | 20.2368 | 20.0663 | 19.8989 | 19.7263 | 18.4126 | 15.4168 | 11.9853
LALEHAM GSP | STAINES BSP | SIDNEY ROAD PRIMARY | MINIMUM HEADROOM | TQ 04100 71760 | NO | YES | 0 | 32.55 | 31.9647 | 31.5763 | 30.9342 | 30.0258 | 29.0605 | 28.0068 | 26.9458 | 25.7142 | 21.2005 | 20.1079 | 19.1163 | 30.0432 | 29.8758 | 29.3442 | 28.4358 | 27.1263 | 25.74 | 24.2116 | 22.6663 | 20.8284 | 15.0705 | 13.8547 | 12.7495 | 31.3389 | 31.1642 | 30.6326 | 29.7337 | 28.44 | 27.0705 | 25.56 | 24.0337 | 22.2 | 16.4568 | 15.2442 | 14.14
|  | SIDNEY ROAD PRIMARY | EE |  |  |  |  | 32.55 | 31.9647 | 31.5763 | 30.9932 | 30.1374 | 29.2953 | 28.4553 | 27.4753 | 26.3679 | 22.6637 | 21.9142 | 21.2679 | 30.0432 | 29.8758 | 29.3484 | 28.5326 | 27.3253 | 26.1295 | 24.9295 | 23.5063 | 21.8705 | 16.7021 | 15.8463 | 15.1053 | 31.3389 | 31.1642 | 30.6368 | 29.8295 | 28.6358 | 27.4537 | 26.2663 | 24.8611 | 23.2389 | 18.0853 | 17.2326 | 16.4937
|  | SIDNEY ROAD PRIMARY | HT |  |  |  |  | 32.5921 | 32.0279 | 31.5774 | 30.9342 | 30.0258 | 29.0605 | 28.0068 | 26.9458 | 25.7142 | 21.2005 | 20.1079 | 19.1163 | 30.0558 | 29.9 | 29.3442 | 28.4358 | 27.1263 | 25.74 | 24.2116 | 22.6663 | 20.8284 | 15.0705 | 13.8547 | 12.7495 | 31.3495 | 31.2084 | 30.6326 | 29.7337 | 28.44 | 27.0705 | 25.56 | 24.0337 | 22.2 | 16.4568 | 15.2442 | 14.14
|  | SIDNEY ROAD PRIMARY | HE |  |  |  |  | 32.6774 | 32.1384 | 31.7932 | 31.2447 | 30.4121 | 29.6016 | 28.7974 | 27.9089 | 26.8942 | 23.6437 | 23.1637 | 22.7447 | 30.0758 | 29.9158 | 29.6747 | 28.9126 | 27.74 | 26.5905 | 25.4484 | 24.1716 | 22.6916 | 17.8137 | 17.2558 | 16.7663 | 31.3642 | 31.2263 | 30.9589 | 30.2053 | 29.0453 | 27.9095 | 26.78 | 25.5189 | 24.0568 | 19.1947 | 18.6379 | 18.1505
|  | SIDNEY ROAD PRIMARY | FB |  |  |  |  | 33.0447 | 32.8595 | 32.6932 | 32.4605 | 32.1574 | 31.8089 | 31.4395 | 31.0511 | 30.5153 | 28.4037 | 27.8142 | 27.4595 | 30.1842 | 30.1189 | 30.0526 | 29.9747 | 29.8842 | 29.6811 | 29.1316 | 28.5484 | 27.7295 | 24.4968 | 23.6368 | 23.1232 | 31.4611 | 31.3958 | 31.3379 | 31.2726 | 31.1958 | 30.9653 | 30.4221 | 29.8463 | 29.0389 | 25.8505 | 25.0011 | 24.4905
NURSLING GSP | ROWNHAMS BSP | SILKSTEAD PRIMARY | MINIMUM HEADROOM | SU 44578 24565 | NO | YES | 0 | 10.0147 | 9.8347 | 9.6558 | 9.3811 | 9.0179 | 8.6 | 8.1537 | 7.6958 | 7.2316 | 4.2253 | 3.4168 | 2.6758 | 8.9042 | 8.7126 | 8.5221 | 8.2295 | 7.8368 | 7.3853 | 6.8979 | 6.4 | 5.8926 | 2.4863 | 1.5979 | 0.78632 | 9.0926 | 8.9 | 8.7074 | 8.4126 | 8.0168 | 7.56 | 7.0684 | 6.5642 | 6.0505 | 2.6 | 1.7063 | 0.88737
|  | SILKSTEAD PRIMARY | EE |  |  |  |  | 10.0147 | 9.8347 | 9.6558 | 9.4516 | 9.2042 | 8.9737 | 8.7547 | 8.5337 | 8.3168 | 6.8189 | 6.2337 | 5.7032 | 8.9042 | 8.7126 | 8.5221 | 8.3084 | 8.0526 | 7.8147 | 7.5863 | 7.3568 | 7.1316 | 5.4284 | 4.7811 | 4.1926 | 9.0926 | 8.9 | 8.7074 | 8.4926 | 8.2368 | 7.9968 | 7.7674 | 7.5368 | 7.3105 | 5.5811 | 4.9242 | 4.3284
|  | SILKSTEAD PRIMARY | HT |  |  |  |  | 10.0432 | 9.8789 | 9.6695 | 9.3811 | 9.0179 | 8.6 | 8.1537 | 7.6958 | 7.2316 | 4.2253 | 3.4168 | 2.6758 | 8.9368 | 8.7632 | 8.54 | 8.2295 | 7.8368 | 7.3853 | 6.8979 | 6.4 | 5.8926 | 2.4863 | 1.5979 | 0.78632 | 9.1263 | 8.9505 | 8.7263 | 8.4126 | 8.0168 | 7.56 | 7.0684 | 6.5642 | 6.0505 | 2.6 | 1.7063 | 0.88737
|  | SILKSTEAD PRIMARY | HE |  |  |  |  | 10.1358 | 10.0074 | 9.8768 | 9.7116 | 9.4979 | 9.3042 | 9.1211 | 8.9316 | 8.7526 | 7.5305 | 7.1495 | 6.8137 | 9.04 | 8.9042 | 8.7674 | 8.5968 | 8.3779 | 8.1779 | 7.9905 | 7.7968 | 7.6126 | 6.2032 | 5.7716 | 5.3895 | 9.2305 | 9.0937 | 8.9558 | 8.7853 | 8.5653 | 8.3653 | 8.1768 | 7.9821 | 7.7979 | 6.3642 | 5.9253 | 5.5368
|  | SILKSTEAD PRIMARY | FB |  |  |  |  | 10.2242 | 10.1211 | 10.0379 | 9.9516 | 9.86 | 9.7684 | 9.6811 | 9.5968 | 9.5105 | 9.0537 | 8.6358 | 8.2695 | 9.1337 | 9.0221 | 8.9347 | 8.8421 | 8.7453 | 8.6484 | 8.5568 | 8.4674 | 8.3768 | 7.8842 | 7.4253 | 7.0221 | 9.3253 | 9.2126 | 9.1242 | 9.0316 | 8.9337 | 8.8368 | 8.7432 | 8.6537 | 8.5621 | 8.0653 | 7.6011 | 7.1926
BRAMLEY (BASI) GSP | READING BSP | SILVER STREET PRIMARY | MINIMUM HEADROOM | SU 71957 72821 | NO | YES | 0 | 33.3116 | 33.1695 | 33.0137 | 32.7968 | 32.4947 | 32.2189 | 31.7747 | 31.1516 | 30.5253 | 28.9126 | 27.6737 | 26.4947 | 31.5274 | 31.3842 | 31.2189 | 30.9916 | 30.4642 | 29.4884 | 28.5179 | 27.8779 | 27.2358 | 25.4432 | 24.0432 | 22.7242 | 31 | 30.8579 | 30.7021 | 30.4853 | 30.1832 | 29.4853 | 28.6547 | 28.0884 | 27.4347 | 25.5779 | 24.18 | 22.8632
|  | SILVER STREET PRIMARY | EE |  |  |  |  | 33.3116 | 33.1853 | 33.0442 | 32.8484 | 32.58 | 32.3179 | 31.8358 | 31.2305 | 30.6284 | 29.6295 | 28.7347 | 27.9042 | 31.5274 | 31.3895 | 31.2379 | 31.0284 | 30.5221 | 29.5579 | 28.5779 | 27.9568 | 27.3389 | 26.2042 | 25.1558 | 24.2063 | 31 | 30.8726 | 30.7326 | 30.5368 | 30.2684 | 29.5432 | 28.7126 | 28.1653 | 27.5389 | 26.34 | 25.2916 | 24.3453
|  | SILVER STREET PRIMARY | HT |  |  |  |  | 33.3168 | 33.1968 | 33.04 | 32.8337 | 32.5832 | 32.3053 | 31.7747 | 31.1516 | 30.5253 | 28.9126 | 27.6737 | 26.4947 | 31.5347 | 31.4011 | 31.2316 | 31 | 30.4642 | 29.4884 | 28.5179 | 27.8779 | 27.2358 | 25.4432 | 24.0432 | 22.7242 | 31.0053 | 30.8853 | 30.7274 | 30.5221 | 30.2716 | 29.4853 | 28.6547 | 28.0884 | 27.4347 | 25.5779 | 24.18 | 22.8632
|  | SILVER STREET PRIMARY | HE |  |  |  |  | 33.3116 | 33.1695 | 33.0137 | 32.7968 | 32.4947 | 32.2189 | 31.9505 | 31.5442 | 30.9947 | 30.5653 | 30.0379 | 29.5568 | 31.5347 | 31.3842 | 31.2189 | 30.9916 | 30.6758 | 29.7895 | 28.8611 | 28.2926 | 27.7295 | 27.28 | 26.7158 | 26.1221 | 31 | 30.8579 | 30.7021 | 30.4853 | 30.1832 | 29.7074 | 28.9137 | 28.4053 | 27.9021 | 27.4968 | 26.8495 | 26.2579
|  | SILVER STREET PRIMARY | FB |  |  |  |  | 33.4116 | 33.3326 | 33.2611 | 33.1811 | 33.0926 | 33.0021 | 32.9158 | 32.8347 | 32.7474 | 32.4295 | 32.2253 | 31.7032 | 31.64 | 31.5537 | 31.4768 | 31.3905 | 31.2958 | 31.1874 | 30.8779 | 30.6126 | 30.3305 | 29.6126 | 28.9968 | 28.4368 | 31.1 | 31.0211 | 30.9495 | 30.8695 | 30.7811 | 30.6905 | 30.6042 | 30.4884 | 30.2463 | 29.6095 | 29.0821 | 28.6126
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD PRIMARY | MINIMUM HEADROOM | SZ 18262 93590 | NO | YES | 0 | 30.9137 | 30.3558 | 29.6432 | 28.5105 | 27.1263 | 25.3095 | 23.5505 | 21.7221 | 19.9053 | 16.3347 | 14.0726 | 12.0684 | 31.1874 | 30.8842 | 30.0495 | 28.6484 | 26.9505 | 24.9074 | 22.9305 | 20.8695 | 18.8221 | 14.84 | 12.3126 | 10.0716 | 24.4758 | 23.8084 | 22.9368 | 21.5242 | 19.8126 | 17.7526 | 15.76 | 13.6821 | 11.6168 | 7.6053 | 5.0589 | 2.8
|  | SOMERFORD PRIMARY | EE |  |  |  |  | 30.9137 | 30.3558 | 29.7432 | 28.8516 | 27.7253 | 26.6358 | 25.4926 | 24.3179 | 23.1758 | 21.3032 | 19.7442 | 18.4368 | 31.1874 | 30.8842 | 30.1884 | 29.1168 | 27.7853 | 26.4916 | 25.2242 | 23.9316 | 22.6737 | 20.5189 | 18.7305 | 17.2295 | 24.4758 | 23.8084 | 23.0758 | 21.9979 | 20.6589 | 19.3558 | 18.08 | 16.7789 | 15.5116 | 13.3379 | 11.5326 | 10.0147
|  | SOMERFORD PRIMARY | HT |  |  |  |  | 30.9916 | 30.3895 | 29.6432 | 28.5105 | 27.1263 | 25.3095 | 23.5505 | 21.7221 | 19.9053 | 16.3347 | 14.0726 | 12.0684 | 31.2074 | 30.9232 | 30.0495 | 28.6484 | 26.9505 | 24.9074 | 22.9305 | 20.8695 | 18.8221 | 14.84 | 12.3126 | 10.0716 | 24.5768 | 23.8389 | 22.9368 | 21.5242 | 19.8126 | 17.7526 | 15.76 | 13.6821 | 11.6168 | 7.6053 | 5.0589 | 2.8
|  | SOMERFORD PRIMARY | HE |  |  |  |  | 31.2611 | 30.8326 | 30.3284 | 29.5295 | 28.4642 | 27.4611 | 26.4916 | 25.4726 | 24.4326 | 23.46 | 22.4758 | 21.6589 | 31.2705 | 30.9874 | 30.6695 | 30.0179 | 28.7695 | 27.5832 | 26.4379 | 25.2737 | 24.1379 | 22.9705 | 21.8179 | 20.8579 | 24.9347 | 24.4453 | 23.8611 | 22.9084 | 21.6526 | 20.4589 | 19.3063 | 18.1347 | 16.9916 | 15.8105 | 14.6453 | 13.6747
|  | SOMERFORD PRIMARY | FB |  |  |  |  | 31.5884 | 31.2863 | 31.0305 | 30.6842 | 30.2895 | 29.8821 | 29.4695 | 29.0516 | 28.6105 | 27.3221 | 26.2379 | 25.3347 | 31.4811 | 31.3432 | 31.2189 | 31.0779 | 30.8053 | 30.2958 | 29.7758 | 29.2463 | 28.6853 | 27.1316 | 25.8989 | 24.86 | 25.3105 | 24.9389 | 24.6284 | 24.1947 | 23.6979 | 23.1832 | 22.6589 | 22.1253 | 21.56 | 19.9937 | 18.7505 | 17.7011
LOVEDEAN GSP | CHICHESTER BSP | SOUTH BERSTED PRIMARY | MINIMUM HEADROOM | SU 94025 00705 | NO | YES | 0 | 33.3311 | 33.0953 | 32.8216 | 32.4468 | 31.9953 | 31.5005 | 31.0079 | 30.4626 | 29.5237 | 25.8289 | 22.7868 | 19.87 | 28.9989 | 28.4926 | 27.9779 | 27.3968 | 26.6411 | 25.6558 | 24.6347 | 23.5726 | 22.5126 | 18.1495 | 14.5453 | 11.2011 | 31.8568 | 31.5042 | 30.9842 | 30.4 | 29.64 | 28.6453 | 27.6158 | 26.5432 | 25.4726 | 21.0526 | 17.3979 | 14.0063
|  | SOUTH BERSTED PRIMARY | EE |  |  |  |  | 33.3311 | 33.0953 | 32.8321 | 32.4774 | 31.9953 | 31.5321 | 31.1037 | 30.6658 | 30.2342 | 29.1363 | 27.0247 | 25.1068 | 28.9989 | 28.4926 | 27.9779 | 27.3968 | 26.7179 | 26.0663 | 25.4168 | 24.7674 | 24.1295 | 22.0611 | 19.4716 | 17.1105 | 31.8568 | 31.5042 | 30.9842 | 30.4 | 29.7179 | 29.0621 | 28.4095 | 27.7558 | 27.1147 | 25.0158 | 22.3863 | 19.9874
|  | SOUTH BERSTED PRIMARY | HT |  |  |  |  | 33.3384 | 33.1163 | 32.8216 | 32.4468 | 31.9953 | 31.5005 | 31.0079 | 30.4626 | 29.5237 | 25.8289 | 22.7868 | 19.87 | 29.0968 | 28.6379 | 28.1147 | 27.4295 | 26.6411 | 25.6558 | 24.6347 | 23.5726 | 22.5126 | 18.1495 | 14.5453 | 11.2011 | 31.8789 | 31.5895 | 31.1242 | 30.4337 | 29.64 | 28.6453 | 27.6158 | 26.5432 | 25.4726 | 21.0526 | 17.3979 | 14.0063
|  | SOUTH BERSTED PRIMARY | HE |  |  |  |  | 33.3847 | 33.1637 | 32.9153 | 32.5732 | 32.0995 | 31.6626 | 31.2342 | 30.8005 | 30.3742 | 30.4121 | 29.1047 | 27.5637 | 29.3432 | 28.9726 | 28.5758 | 28.0937 | 27.4832 | 26.9168 | 26.3621 | 25.8095 | 25.2684 | 23.9821 | 21.9053 | 19.9726 | 31.9253 | 31.7042 | 31.4379 | 31.0453 | 30.4947 | 29.9253 | 29.3684 | 28.8147 | 28.2705 | 26.9611 | 24.8495 | 22.8842
|  | SOUTH BERSTED PRIMARY | FB |  |  |  |  | 33.5521 | 33.4426 | 33.3437 | 33.2321 | 33.1089 | 32.9847 | 32.8637 | 32.7521 | 32.6311 | 32.19 | 31.9268 | 30.7268 | 29.6453 | 29.36 | 29.1421 | 28.9105 | 28.6642 | 28.4189 | 28.1779 | 27.9474 | 27.7084 | 26.6653 | 25.0474 | 23.5758 | 32.0926 | 31.9832 | 31.8842 | 31.7611 | 31.5937 | 31.4263 | 31.1874 | 30.9558 | 30.7147 | 29.66 | 28.0189 | 26.5242
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE PRIMARY | MINIMUM HEADROOM | SZ 13563 92074 | NO | YES | 0 | 22.7632 | 22.5316 | 22.2768 | 21.7968 | 21.4905 | 20.9421 | 20.4095 | 19.4474 | 18.4095 | 16.06 | 14.2947 | 12.7 | 21.5 | 21.2726 | 20.7358 | 19.9789 | 19.7189 | 19.1232 | 18.5484 | 17.3684 | 16.1611 | 13.4811 | 11.5221 | 9.7463 | 21.2663 | 20.8326 | 20.2916 | 19.5516 | 19.2832 | 18.6947 | 18.0937 | 16.8968 | 15.7168 | 13.0979 | 11.1863 | 9.4568
|  | SOUTHBOURNE PRIMARY | EE |  |  |  |  | 22.7632 | 22.5316 | 22.2811 | 21.9463 | 21.4905 | 20.9421 | 20.4095 | 19.8568 | 19.3221 | 19.7021 | 18.5411 | 17.5337 | 21.5 | 21.2726 | 20.8411 | 20.3274 | 19.7189 | 19.1232 | 18.5484 | 17.9526 | 17.3779 | 17.8684 | 16.46 | 15.2326 | 21.2663 | 20.8326 | 20.3916 | 19.8842 | 19.2832 | 18.6947 | 18.1284 | 17.5389 | 16.9726 | 17.3558 | 15.9884 | 14.7989
|  | SOUTHBOURNE PRIMARY | HT |  |  |  |  | 22.7842 | 22.5621 | 22.2768 | 21.7968 | 22.5189 | 21.4884 | 20.4989 | 19.4474 | 18.4095 | 16.06 | 14.2947 | 12.7 | 21.52 | 21.3032 | 20.7358 | 19.9789 | 20.9326 | 19.7379 | 18.5937 | 17.3684 | 16.1611 | 13.4811 | 11.5221 | 9.7463 | 21.3368 | 20.8463 | 20.2916 | 19.5516 | 20.38 | 19.2126 | 18.0937 | 16.8968 | 15.7168 | 13.0979 | 11.1863 | 9.4568
|  | SOUTHBOURNE PRIMARY | HE |  |  |  |  | 22.8326 | 22.6137 | 22.3726 | 22.0421 | 21.58 | 21.1621 | 20.7579 | 20.3463 | 19.9421 | 21.1389 | 20.4042 | 19.7642 | 21.5642 | 21.3474 | 21.1084 | 20.78 | 20.32 | 19.8421 | 19.3516 | 18.8453 | 18.3621 | 19.6074 | 18.6895 | 17.8874 | 21.5716 | 21.2484 | 20.9011 | 20.4695 | 19.9116 | 19.3884 | 18.9011 | 18.3989 | 17.9189 | 19.0463 | 18.1589 | 17.3832
|  | SOUTHBOURNE PRIMARY | FB |  |  |  |  | 22.9895 | 22.8716 | 22.7663 | 22.6516 | 22.5242 | 22.3958 | 22.2716 | 22.1547 | 22.0305 | 21.4063 | 22.0821 | 21.3926 | 21.7189 | 21.6042 | 21.5011 | 21.3874 | 21.2632 | 21.1358 | 20.9716 | 20.7642 | 20.5516 | 19.5747 | 20.4242 | 19.5821 | 21.8305 | 21.5758 | 21.3779 | 21.1705 | 20.9495 | 20.7284 | 20.5168 | 20.3126 | 20.1042 | 19.1495 | 19.8842 | 19.0674
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | SOUTHCOTE PRIMARY | MINIMUM HEADROOM | SU 68199 71325 | NO | YES | 5.2632 | 21.5611 | 21.3621 | 21.1537 | 20.8379 | 20.3758 | 19.8032 | 19.2589 | 18.8137 | 18.3621 | 17.2684 | 16.4811 | 15.7337 | 21.0674 | 20.8158 | 20.5568 | 20.1495 | 19.5295 | 18.8789 | 18.2811 | 17.8 | 17.3105 | 16.12 | 15.2526 | 14.4242 | 21.4116 | 21.18 | 20.9389 | 20.5653 | 20.0053 | 19.4158 | 18.8705 | 18.4253 | 17.9726 | 16.8779 | 16.0895 | 15.3411
|  | SOUTHCOTE PRIMARY | EE |  |  |  |  | 21.5611 | 21.3621 | 21.1537 | 20.9053 | 20.4926 | 20.0737 | 19.6589 | 19.3421 | 19.0347 | 18.5495 | 18.0253 | 17.5463 | 21.0674 | 20.8158 | 20.5568 | 20.2632 | 19.7358 | 19.2168 | 18.7526 | 18.4189 | 18.0979 | 17.5537 | 16.9611 | 16.4158 | 21.4116 | 21.18 | 20.9389 | 20.6611 | 20.1779 | 19.7 | 19.2716 | 18.9537 | 18.6474 | 18.16 | 17.6347 | 17.1558
|  | SOUTHCOTE PRIMARY | HT |  |  |  |  | 21.5968 | 21.3989 | 21.1547 | 20.8379 | 20.3758 | 19.8032 | 19.2589 | 18.8137 | 18.3621 | 17.2684 | 16.4811 | 15.7337 | 21.1232 | 20.8674 | 20.5568 | 20.1495 | 19.5295 | 18.8789 | 18.2811 | 17.8 | 17.3105 | 16.12 | 15.2526 | 14.4242 | 21.46 | 21.2253 | 20.94 | 20.5653 | 20.0053 | 19.4158 | 18.8705 | 18.4253 | 17.9726 | 16.8779 | 16.0895 | 15.3411
|  | SOUTHCOTE PRIMARY | HE |  |  |  |  | 21.6726 | 21.5147 | 21.3421 | 21.12 | 20.7232 | 20.3421 | 19.9926 | 19.7263 | 19.4589 | 19.3063 | 19.0084 | 18.7168 | 21.2421 | 21.0558 | 20.8558 | 20.6063 | 20.1074 | 19.6253 | 19.1937 | 18.9011 | 18.6137 | 18.4179 | 18.0663 | 17.7263 | 21.5632 | 21.3874 | 21.1968 | 20.9579 | 20.4968 | 20.0516 | 19.6505 | 19.3674 | 19.0884 | 18.9242 | 18.6211 | 18.3284
|  | SOUTHCOTE PRIMARY | FB |  |  |  |  | 21.8021 | 21.6926 | 21.6063 | 21.5105 | 21.3684 | 21.22 | 21.0811 | 20.9853 | 20.8853 | 20.5095 | 20.1537 | 19.8158 | 21.3989 | 21.2537 | 21.1442 | 21.0232 | 20.8263 | 20.6189 | 20.4263 | 20.3063 | 20.1821 | 19.7053 | 19.2663 | 18.8747 | 21.7105 | 21.5779 | 21.4768 | 21.3653 | 21.1884 | 21.0032 | 20.8295 | 20.7189 | 20.6032 | 20.1642 | 19.7716 | 19.4274
EALING GSP |  | SOUTHFIELD ROAD PRIMARY | MINIMUM HEADROOM | TQ 20533 79746 | NO | YES | 0 | 45.4937 | 64.8389 | 63.9516 | 62.8979 | 61.5074 | 60.2284 | 59.0789 | 57.9895 | 56.6811 | 53.9232 | 52.22 | 50.6505 | 43.3305 | 62.6242 | 61.1179 | 59.3684 | 57.0274 | 54.96 | 53.1579 | 51.4758 | 49.3558 | 45.1274 | 42.5642 | 40.1905 | 39.1832 | 58.5358 | 57.66 | 56.62 | 55.2474 | 53.9842 | 52.8463 | 51.7674 | 50.4747 | 47.7442 | 46.0568 | 44.5021
|  | SOUTHFIELD ROAD PRIMARY | EE |  |  |  |  | 45.4937 | 64.8389 | 64.0084 | 63.02 | 61.8389 | 60.6684 | 59.8789 | 59.2189 | 58.5705 | 57.4421 | 56.4358 | 55.5505 | 43.3305 | 62.6484 | 61.2453 | 59.6221 | 57.7411 | 55.8789 | 54.76 | 53.9189 | 53.0968 | 51.2337 | 49.5568 | 48.0589 | 39.1832 | 58.5358 | 57.7168 | 56.74 | 55.5726 | 54.4147 | 53.6295 | 52.9747 | 52.3284 | 51.2137 | 50.22 | 49.3463
|  | SOUTHFIELD ROAD PRIMARY | HT |  |  |  |  | 45.5095 | 64.8432 | 63.9516 | 62.8979 | 61.5074 | 60.2284 | 59.0789 | 57.9895 | 56.6811 | 53.9232 | 52.22 | 50.6505 | 43.3453 | 62.6242 | 61.1179 | 59.3684 | 57.0274 | 54.96 | 53.1579 | 51.4758 | 49.3558 | 45.1274 | 42.5642 | 40.1905 | 39.1989 | 58.5411 | 57.66 | 56.62 | 55.2474 | 53.9842 | 52.8463 | 51.7674 | 50.4747 | 47.7442 | 46.0568 | 44.5021
|  | SOUTHFIELD ROAD PRIMARY | HE |  |  |  |  | 45.6611 | 65.0642 | 64.2863 | 63.3379 | 62.1747 | 61.0421 | 60.32 | 59.7347 | 59.1621 | 58.8337 | 58.3495 | 57.9063 | 43.4126 | 63.0242 | 61.7926 | 60.26 | 58.4316 | 56.6442 | 55.6821 | 55.0021 | 54.3411 | 53.6579 | 52.7621 | 51.9242 | 39.3474 | 58.7579 | 57.9895 | 57.0526 | 55.9021 | 54.7811 | 54.0632 | 53.48 | 52.9084 | 52.5863 | 52.1105 | 51.6747
|  | SOUTHFIELD ROAD PRIMARY | FB |  |  |  |  | 45.9842 | 65.6074 | 65.2232 | 64.8105 | 64.3379 | 63.8558 | 63.5463 | 63.3242 | 63.0863 | 62.1179 | 61.3526 | 60.7105 | 43.64 | 63.3958 | 63.1558 | 62.6137 | 61.8305 | 61.0316 | 60.5747 | 60.2821 | 59.9653 | 58.6221 | 57.4263 | 56.3568 | 39.6674 | 59.2958 | 58.9158 | 58.5084 | 58.0411 | 57.5653 | 57.2589 | 57.0379 | 56.8011 | 55.84 | 55.0821 | 54.4484
AXMINSTER GSP | YEOVIL BSP | SPARKFORD PRIMARY | MINIMUM HEADROOM | ST 60767 25496 | NO | YES | 0 | 6.1421 | 6.0695 | 5.9979 | 5.9105 | 5.7211 | 5.5147 | 5.3779 | 5.2442 | 5.1074 | 2.7147 | 2.4579 | 2.1684 | 5.7211 | 5.6621 | 5.6021 | 5.5263 | 5.3842 | 5.2316 | 5.0895 | 4.9453 | 4.7979 | 2.0126 | 1.7284 | 1.4042 | 5.3663 | 5.2884 | 5.2105 | 5.1189 | 4.9105 | 4.6821 | 4.5347 | 4.3905 | 4.2432 | 1.4632 | 1.18 | 0.85579
|  | SPARKFORD PRIMARY | EE |  |  |  |  | 6.1421 | 6.0695 | 5.9979 | 5.9105 | 5.7442 | 5.5516 | 5.42 | 5.2905 | 5.1726 | 3.9316 | 3.76 | 3.5632 | 5.7211 | 5.6621 | 5.6021 | 5.5263 | 5.3968 | 5.2547 | 5.1358 | 4.9958 | 4.8684 | 3.4158 | 3.2211 | 2.9958 | 5.3663 | 5.2884 | 5.2105 | 5.1189 | 4.9368 | 4.7232 | 4.5811 | 4.4411 | 4.3137 | 2.8642 | 2.6695 | 2.4442
|  | SPARKFORD PRIMARY | HT |  |  |  |  | 6.1547 | 6.0874 | 6.0116 | 5.9242 | 5.7211 | 5.5147 | 5.3779 | 5.2442 | 5.1074 | 2.7147 | 2.4579 | 2.1684 | 5.7284 | 5.6726 | 5.6084 | 5.5326 | 5.3842 | 5.2316 | 5.0895 | 4.9453 | 4.7979 | 2.0126 | 1.7284 | 1.4042 | 5.3811 | 5.3074 | 5.2274 | 5.1358 | 4.9105 | 4.6821 | 4.5347 | 4.3905 | 4.2432 | 1.4632 | 1.18 | 0.85579
|  | SPARKFORD PRIMARY | HE |  |  |  |  | 6.1905 | 6.1368 | 6.0789 | 6.0084 | 5.8495 | 5.6674 | 5.5547 | 5.4421 | 5.3389 | 4.22 | 4.1221 | 3.9863 | 5.7526 | 5.7063 | 5.6568 | 5.5926 | 5.4684 | 5.3337 | 5.2421 | 5.1484 | 5.0579 | 3.74 | 3.6274 | 3.4684 | 5.4211 | 5.3642 | 5.3042 | 5.2305 | 5.0579 | 4.8558 | 4.7337 | 4.6137 | 4.5032 | 3.1874 | 3.0747 | 2.9168
|  | SPARKFORD PRIMARY | FB |  |  |  |  | 6.2358 | 6.1979 | 6.1716 | 6.1411 | 6.0842 | 6.0211 | 5.98 | 5.9379 | 5.8968 | 5.7168 | 5.5979 | 5.4726 | 5.7916 | 5.7632 | 5.7421 | 5.7179 | 5.6779 | 5.6347 | 5.6042 | 5.5726 | 5.5432 | 5.4126 | 5.3137 | 5.1695 | 5.4695 | 5.4284 | 5.3989 | 5.3663 | 5.3021 | 5.2316 | 5.1853 | 5.1389 | 5.0937 | 4.8916 | 4.7589 | 4.6147
MELKSHAM GSP | NORRINGTON BSP | SPRING QUARRY WEST PRIMARY | MINIMUM HEADROOM | ST 84368 68717 | NO | YES | 0 | 29.9111 | 29.7163 | 26.9237 | 26.5605 | 26.3058 | 26.0279 | 25.7321 | 25.4016 | 25.0563 | 16.2342 | 10.9626 | 8.3237 | 26.6105 | 26.3937 | 23.1432 | 22.7379 | 22.4642 | 22.1653 | 21.8453 | 21.4832 | 21.1053 | 10.8453 | 4.7105 | 1.6337 | 27.7958 | 27.5811 | 24.3284 | 23.9221 | 23.6484 | 23.3495 | 23.0284 | 22.6653 | 22.2853 | 11.9842 | 5.8305 | 2.7621
|  | SPRING QUARRY WEST PRIMARY | EE |  |  |  |  | 29.9111 | 29.77 | 26.9921 | 26.6816 | 26.3058 | 26.1184 | 25.9247 | 25.7289 | 25.5395 | 21.6163 | 19.5226 | 16.8511 | 26.6105 | 26.4579 | 23.2232 | 22.8779 | 22.4642 | 22.2695 | 22.0642 | 21.8579 | 21.6589 | 17.0884 | 14.6558 | 11.5432 | 27.7958 | 27.6442 | 24.4095 | 24.0632 | 23.6484 | 23.4526 | 23.2484 | 23.04 | 22.8411 | 18.2516 | 15.8095 | 12.6842
|  | SPRING QUARRY WEST PRIMARY | HT |  |  |  |  | 29.9405 | 29.7163 | 26.9237 | 26.5605 | 26.3121 | 26.0279 | 25.7321 | 25.4016 | 25.0563 | 16.2342 | 10.9626 | 8.3237 | 26.6442 | 26.3937 | 23.1432 | 22.7379 | 22.4705 | 22.1653 | 21.8453 | 21.4832 | 21.1053 | 10.8453 | 4.7105 | 1.6337 | 27.8284 | 27.5811 | 24.3284 | 23.9221 | 23.6547 | 23.3495 | 23.0284 | 22.6653 | 22.2853 | 11.9842 | 5.8305 | 2.7621
|  | SPRING QUARRY WEST PRIMARY | HE |  |  |  |  | 30.01 | 29.9058 | 27.1911 | 26.9405 | 26.6311 | 26.3332 | 26.1742 | 26.0163 | 25.8616 | 22.2068 | 20.2742 | 17.7384 | 26.7221 | 26.6116 | 23.4495 | 23.1758 | 22.8389 | 22.5126 | 22.3495 | 22.1863 | 22.0284 | 17.7526 | 15.4968 | 12.5347 | 27.9063 | 27.7968 | 24.6368 | 24.3621 | 24.0242 | 23.6979 | 23.5337 | 23.3705 | 23.2126 | 18.9189 | 16.6537 | 13.6789
|  | SPRING QUARRY WEST PRIMARY | FB |  |  |  |  | 30.0963 | 30.0184 | 29.9584 | 29.85 | 29.7321 | 29.6068 | 29.4763 | 29.4142 | 29.3511 | 28.6668 | 26.7342 | 24.5058 | 26.8137 | 26.7284 | 26.6632 | 26.5432 | 26.4105 | 26.2716 | 26.1242 | 26.0579 | 25.9895 | 25.2126 | 22.9642 | 20.3674 | 27.9979 | 27.9126 | 27.8484 | 27.7284 | 27.5979 | 27.4589 | 27.3126 | 27.2463 | 27.1789 | 26.4074 | 24.1505 | 21.5421
NORTH HYDE GSP | NORTH HYDE BSP | SPRINGFIELD ROAD PRIMARY | MINIMUM HEADROOM | TQ 11409 80620 | NO | NO | 0.015789 | 27.5526 | 27.4305 | 27.3011 | 42.2326 | 40.6432 | 39.1274 | 36.5663 | 33.8716 | 31.7305 | 24.9884 | 19.7432 | 14.68 | 26.2463 | 25.5905 | 24.3011 | 37.1853 | 35.3958 | 33.6874 | 30.8368 | 27.8389 | 25.4179 | 17.7653 | 11.7368 | 5.9105 | 22.8716 | 22.7495 | 22.6189 | 38.5811 | 36.7653 | 35.0453 | 32.0905 | 28.9779 | 26.5189 | 18.7653 | 12.6979 | 6.8368
|  | SPRINGFIELD ROAD PRIMARY | EE |  |  |  |  | 27.5526 | 27.4305 | 27.3011 | 43.7537 | 42.4526 | 41.2758 | 39.2337 | 37.1684 | 35.8905 | 30.8358 | 26.1432 | 21.5926 | 26.2463 | 25.7663 | 24.7105 | 38.8768 | 37.44 | 36.1337 | 33.8989 | 31.6263 | 30.1884 | 24.3495 | 18.9316 | 13.6474 | 22.8716 | 22.7495 | 22.6189 | 43.7537 | 42.4526 | 41.2758 | 39.2337 | 37.1684 | 35.8905 | 30.8358 | 26.1432 | 21.5926
|  | SPRINGFIELD ROAD PRIMARY | HT |  |  |  |  | 27.5684 | 27.4621 | 27.3221 | 42.2326 | 40.6432 | 39.1274 | 36.5663 | 33.8716 | 31.7305 | 24.9884 | 19.7432 | 14.68 | 26.2526 | 25.5905 | 24.3011 | 37.1853 | 35.3958 | 33.6874 | 30.8368 | 27.8389 | 25.4179 | 17.7653 | 11.7368 | 5.9105 | 22.8874 | 22.7811 | 22.6411 | 38.5811 | 36.7653 | 35.0453 | 32.0905 | 28.9779 | 26.5189 | 18.7653 | 12.6979 | 6.8368
|  | SPRINGFIELD ROAD PRIMARY | HE |  |  |  |  | 27.5726 | 27.4547 | 27.3274 | 44.1684 | 42.8884 | 41.7568 | 39.8495 | 37.9147 | 36.7674 | 32.6421 | 28.4663 | 24.38 | 26.2863 | 25.9095 | 25.0126 | 39.3421 | 37.9316 | 36.6747 | 34.5916 | 32.4737 | 31.1832 | 26.3495 | 21.4695 | 16.6916 | 22.8916 | 22.7737 | 22.6463 | 40.0221 | 39.4189 | 38.1463 | 35.9558 | 33.7358 | 32.4421 | 27.5905 | 22.6979 | 17.9074
|  | SPRINGFIELD ROAD PRIMARY | FB |  |  |  |  | 27.6505 | 27.5821 | 27.52 | 49.5337 | 47.8084 | 46.2705 | 45.7642 | 45.1663 | 44.5526 | 41.4947 | 38.4979 | 35.5937 | 26.4158 | 26.2979 | 26.1389 | 46.8442 | 44.6147 | 42.5379 | 41.5263 | 40.4474 | 39.7568 | 36.3 | 32.8453 | 29.48 | 22.9695 | 22.9011 | 22.8389 | 45.3547 | 43.6411 | 41.8463 | 41.2684 | 40.6547 | 40.5179 | 37.8116 | 34.3284 | 30.9421
NURSLING GSP | WINCHESTER BSP | ST CROSS PRIMARY | MINIMUM HEADROOM | SU 47287 28156 | NO | YES | 0 | 17.6611 | 17.4368 | 17.2 | 16.8947 | 16.5147 | 16.0905 | 15.6579 | 14.6116 | 13.4474 | 14.1358 | 10.2253 | 7.6274 | 16.2516 | 15.4621 | 14.6842 | 14.0032 | 13.0589 | 11.9337 | 10.6916 | 9.4126 | 8.1084 | 9.2347 | 6.7937 | 3.8242 | 17.1537 | 16.4695 | 15.6905 | 15.0095 | 14.0653 | 12.94 | 11.6979 | 10.4179 | 9.1137 | 10.24 | 8.9663 | 5.9958
|  | ST CROSS PRIMARY | EE |  |  |  |  | 17.6611 | 17.4368 | 17.2 | 16.9221 | 16.5379 | 16.1811 | 15.8547 | 15.5158 | 15.1811 | 14.3884 | 18.1589 | 15.9832 | 16.2516 | 15.4621 | 14.6842 | 14.2505 | 13.74 | 13.2568 | 12.7916 | 12.3179 | 11.8484 | 9.2347 | 15.9368 | 13.4137 | 17.1537 | 16.4695 | 15.6905 | 15.2579 | 14.7463 | 14.2632 | 13.7979 | 13.3242 | 12.8547 | 10.24 | 18.1116 | 15.5884
|  | ST CROSS PRIMARY | HT |  |  |  |  | 17.6768 | 17.4695 | 17.2053 | 16.8947 | 16.5147 | 16.0905 | 15.6579 | 14.6116 | 13.4474 | 14.1358 | 10.2253 | 7.6274 | 16.3316 | 15.5811 | 14.7168 | 14.0032 | 13.0589 | 11.9337 | 10.6916 | 9.4126 | 8.1084 | 11.2947 | 6.7937 | 3.8242 | 17.1958 | 16.5884 | 15.7242 | 15.0095 | 14.0653 | 12.94 | 11.6979 | 10.4179 | 9.1137 | 13.4684 | 8.9663 | 5.9958
|  | ST CROSS PRIMARY | HE |  |  |  |  | 17.7189 | 17.5095 | 17.2874 | 17.0189 | 16.6411 | 16.3053 | 15.9768 | 15.6432 | 15.3126 | 15.1958 | 18.8884 | 17.8253 | 16.5126 | 15.8221 | 15.1316 | 14.7695 | 14.3053 | 13.8863 | 13.4842 | 13.0789 | 12.6768 | 10.6547 | 17.6242 | 15.4316 | 17.2926 | 16.8295 | 16.1379 | 15.7758 | 15.3116 | 14.8926 | 14.4905 | 14.0863 | 13.6832 | 11.6611 | 19.1674 | 17.5916
|  | ST CROSS PRIMARY | FB |  |  |  |  | 17.8821 | 17.7779 | 17.6832 | 17.5905 | 17.4884 | 17.3853 | 17.2842 | 17.1905 | 17.0916 | 16.6832 | 16.3705 | 15.6663 | 17.1347 | 16.8337 | 16.5337 | 16.3589 | 16.1747 | 15.9905 | 15.8116 | 15.6421 | 15.4695 | 14.2242 | 12.3926 | 10.4979 | 17.4484 | 17.3484 | 17.2579 | 17.1547 | 17.0189 | 16.8842 | 16.7526 | 16.6284 | 16.4758 | 15.2305 | 13.3989 | 11.5032
COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES PRIMARY | MINIMUM HEADROOM | SP 51259 05741 | NO | YES | 0 | 28.23 | 28.1605 | 28.0479 | 27.7226 | 27.3837 | 26.8584 | 26.2732 | 25.7311 | 25.23 | 24.55 | 24.2205 | 23.9247 | 32.0421 | 31.9895 | 31.9274 | 31.84 | 31.7126 | 31.0737 | 29.1295 | 27.3495 | 25.7358 | 23.9421 | 23.2232 | 22.5874 | 31.9989 | 31.9463 | 31.8842 | 31.7968 | 31.6695 | 31.0105 | 29.1947 | 27.5305 | 26.0221 | 24.3326 | 23.6495 | 23.0463
|  | ST EBBES PRIMARY | EE |  |  |  |  | 28.23 | 28.1605 | 28.0647 | 27.7995 | 27.5111 | 27.0963 | 26.6216 | 26.2132 | 25.8626 | 25.5437 | 25.3205 | 25.1342 | 32.0421 | 31.9895 | 31.9295 | 31.8484 | 31.7326 | 31.6242 | 31.3505 | 30.0611 | 28.9895 | 27.1211 | 26.5442 | 26.0579 | 31.9989 | 31.9463 | 31.8863 | 31.8053 | 31.6895 | 31.5811 | 31.2558 | 30.0516 | 29.0474 | 27.3063 | 26.7632 | 26.3042
|  | ST EBBES PRIMARY | HT |  |  |  |  | 28.2374 | 28.1689 | 28.0479 | 27.7226 | 27.3837 | 26.8584 | 26.2732 | 25.7311 | 25.23 | 24.55 | 24.2205 | 23.9247 | 32.0474 | 31.9958 | 31.9274 | 31.84 | 32.0989 | 31.0737 | 29.1295 | 27.3495 | 25.7358 | 23.9421 | 23.2232 | 22.5874 | 32.0042 | 31.9526 | 31.8842 | 31.7968 | 32.0147 | 31.0105 | 29.1947 | 27.5305 | 26.0221 | 24.3326 | 23.6495 | 23.0463
|  | ST EBBES PRIMARY | HE |  |  |  |  | 28.2584 | 28.1889 | 28.0974 | 27.8279 | 27.53 | 27.1058 | 26.6363 | 26.2374 | 25.8984 | 25.8332 | 25.73 | 25.6468 | 32.0526 | 31.9937 | 31.9305 | 31.84 | 31.7126 | 31.5989 | 31.4884 | 30.28 | 29.2674 | 28.08 | 27.7863 | 27.5463 | 32.0095 | 31.9505 | 31.8874 | 31.7968 | 31.6695 | 31.5558 | 31.4074 | 30.2516 | 29.3021 | 28.2021 | 27.9263 | 27.7011
|  | ST EBBES PRIMARY | FB |  |  |  |  | 28.3005 | 28.2542 | 28.2058 | 28.0942 | 27.9826 | 27.8942 | 27.7142 | 27.5521 | 27.4089 | 26.7847 | 26.9668 | 26.8395 | 32.0874 | 32.0526 | 32.0211 | 31.9863 | 31.9474 | 31.9084 | 31.8695 | 31.8337 | 31.7958 | 31.6063 | 31.6032 | 31.2568 | 32.0442 | 32.0095 | 31.9779 | 31.9432 | 31.9042 | 31.8653 | 31.8263 | 31.7905 | 31.7526 | 31.5053 | 31.5 | 31.1747
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | ST JOHNS PRIMARY | MINIMUM HEADROOM | SU 47113 66363 | NO | YES | 1.0516 | 16.7828 | 16.0038 | 15.1491 | 13.8807 | 12.4312 | 10.9164 | 9.4301 | 7.9733 | 6.6259 | 4.487 | 3.1364 | 1.8049 | 14.3301 | 13.4364 | 12.4585 | 11.0038 | 9.3449 | 7.6154 | 5.9185 | 4.2575 | 2.7259 | 0.35855 | -1.1383 | -2.6288 | 13.8743 | 13.2385 | 12.5428 | 11.5143 | 10.3333 | 9.0922 | 7.4722 | 5.8049 | 4.2701 | 1.8954 | 0.39539 | -1.0993
|  | ST JOHNS PRIMARY | EE |  |  |  |  | 16.7828 | 16.0038 | 15.1491 | 14.1133 | 12.887 | 11.6817 | 10.4838 | 9.368 | 8.3954 | 7.3501 | 6.4259 | 5.5438 | 14.3301 | 13.4364 | 12.4585 | 11.2785 | 9.8943 | 8.5301 | 7.167 | 5.907 | 4.8185 | 3.6207 | 2.5649 | 1.5491 | 13.8743 | 13.2385 | 12.5449 | 11.6922 | 10.6701 | 9.667 | 8.6775 | 7.4617 | 6.3701 | 5.168 | 4.1091 | 3.0891
|  | ST JOHNS PRIMARY | HT |  |  |  |  | 16.8617 | 16.1196 | 15.1501 | 13.8807 | 12.4312 | 10.9164 | 9.4301 | 7.9733 | 6.6259 | 4.487 | 3.1364 | 1.8049 | 14.4228 | 13.5722 | 12.4596 | 11.0038 | 9.3449 | 7.6154 | 5.9185 | 4.2575 | 2.7259 | 0.35855 | -1.1383 | -2.6288 | 13.9354 | 13.3322 | 12.5428 | 11.5143 | 10.3333 | 9.0922 | 7.4722 | 5.8049 | 4.2701 | 1.8954 | 0.39539 | -1.0993
|  | ST JOHNS PRIMARY | HE |  |  |  |  | 17.048 | 16.3659 | 15.5964 | 14.627 | 13.4385 | 12.2964 | 11.167 | 10.1259 | 9.228 | 8.8438 | 8.3375 | 7.8375 | 14.6385 | 13.8607 | 12.9828 | 11.8817 | 10.5438 | 9.2533 | 7.9743 | 6.8038 | 5.8049 | 5.3385 | 4.7459 | 4.1585 | 14.0828 | 13.5238 | 12.8933 | 12.0912 | 11.0954 | 10.1438 | 9.2038 | 8.3291 | 7.3607 | 6.8922 | 6.2975 | 5.707
|  | ST JOHNS PRIMARY | FB |  |  |  |  | 17.3385 | 16.9364 | 16.567 | 16.1491 | 15.6901 | 15.1985 | 14.6807 | 14.1943 | 13.7533 | 12.9249 | 12.2512 | 11.648 | 14.9564 | 14.4943 | 14.0701 | 13.588 | 13.0585 | 12.4922 | 11.8933 | 11.3291 | 10.8217 | 9.908 | 9.1449 | 8.4491 | 14.3385 | 14.0133 | 13.7164 | 13.3796 | 13.008 | 12.6143 | 12.2007 | 11.8133 | 11.4564 | 10.7364 | 10.1785 | 9.6933
COWLEY GSP | WITNEY BSP | STANDLAKE PRIMARY | MINIMUM HEADROOM | SP 38923 02349 | NO | YES | 0 | 14.0184 | 13.9647 | 13.8879 | 13.7932 | 13.6868 | 13.5753 | 13.4679 | 13.3563 | 13.2437 | 12.9553 | 12.7437 | 12.5405 | 12.4753 | 12.3837 | 12.2426 | 12.0711 | 11.9016 | 11.7342 | 11.5826 | 11.3995 | 11.2163 | 10.6742 | 10.1879 | 9.6795 | 12.9505 | 12.8579 | 12.7179 | 12.5463 | 12.3768 | 12.2095 | 12.0579 | 11.8758 | 11.6926 | 11.1516 | 10.6663 | 10.1589
|  | STANDLAKE PRIMARY | EE |  |  |  |  | 14.03 | 13.9721 | 13.9132 | 13.8384 | 13.7374 | 13.6447 | 13.5553 | 13.4658 | 13.3784 | 13.2711 | 13.1553 | 13.0447 | 12.5311 | 12.4342 | 12.3395 | 12.2332 | 12.1058 | 11.9837 | 11.8553 | 11.7311 | 11.61 | 11.3468 | 11.0321 | 10.7047 | 13.0053 | 12.9095 | 12.8137 | 12.7084 | 12.5811 | 12.4589 | 12.3305 | 12.2063 | 12.0853 | 11.8221 | 11.5084 | 11.1821
|  | STANDLAKE PRIMARY | HT |  |  |  |  | 14.0184 | 13.9647 | 13.8879 | 13.7932 | 13.6868 | 13.5753 | 13.4679 | 13.3563 | 13.2437 | 12.9553 | 12.7437 | 12.5405 | 12.4753 | 12.3837 | 12.2426 | 12.0711 | 11.9016 | 11.7342 | 11.5826 | 11.3995 | 11.2163 | 10.6742 | 10.1879 | 9.6795 | 12.9505 | 12.8579 | 12.7179 | 12.5463 | 12.3768 | 12.2095 | 12.0579 | 11.8758 | 11.6926 | 11.1516 | 10.6663 | 10.1589
|  | STANDLAKE PRIMARY | HE |  |  |  |  | 14.0595 | 14.0142 | 13.9626 | 13.8974 | 13.8037 | 13.7195 | 13.6363 | 13.5553 | 13.4732 | 13.4563 | 13.3963 | 13.3353 | 12.6047 | 12.5384 | 12.4668 | 12.3826 | 12.2721 | 12.1689 | 12.0658 | 11.9689 | 11.8721 | 11.7889 | 11.5816 | 11.35 | 13.0789 | 13.0126 | 12.9421 | 12.8568 | 12.7463 | 12.6432 | 12.5411 | 12.4442 | 12.3474 | 12.2642 | 12.0579 | 11.8263
|  | STANDLAKE PRIMARY | FB |  |  |  |  | 14.0974 | 14.07 | 14.0468 | 14.0216 | 13.9953 | 13.9668 | 13.9395 | 13.9153 | 13.8879 | 13.7879 | 13.7079 | 13.6363 | 12.6763 | 12.6226 | 12.5837 | 12.5416 | 12.4974 | 12.4511 | 12.4068 | 12.3658 | 12.3226 | 12.1532 | 11.95 | 11.7353 | 13.1505 | 13.0968 | 13.0579 | 13.0158 | 12.9716 | 12.9253 | 12.8811 | 12.84 | 12.7968 | 12.6274 | 12.4253 | 12.2116
MINETY GSP | STRATTON (RESERVE) BSP | STANTON FITZWARREN PRIMARY | MINIMUM HEADROOM | SU 17585 90987 | NO | YES | 0.21053 | 18.1579 | 17.8432 | 17.5968 | 17.32 | 16.9726 | 15.9432 | 14.3842 | 12.9495 | 11.2389 | 3.4568 | 1.8316 | 0.91474 | 12.6895 | 12.3305 | 12.0516 | 11.7379 | 11.3411 | 10.3021 | 8.5221 | 6.8874 | 4.9263 | -4.2063 | -6.0811 | -7.1316 | 14.3074 | 13.9526 | 13.6768 | 13.3663 | 12.9747 | 11.9305 | 10.1716 | 8.5537 | 6.6158 | -2.3947 | -4.2474 | -5.2863
|  | STANTON FITZWARREN PRIMARY | EE |  |  |  |  | 20.08 | 19.3537 | 18.5179 | 17.9358 | 17.2358 | 16.4021 | 15.1411 | 13.9084 | 12.4095 | 3.4568 | 1.8316 | 0.91474 | 14.9737 | 14.1442 | 13.1895 | 12.5379 | 11.7632 | 10.8274 | 9.3853 | 7.98 | 6.2611 | -4.2063 | -6.0811 | -7.1316 | 16.5547 | 15.7347 | 14.7895 | 14.1453 | 13.3758 | 12.4495 | 11.0242 | 9.6337 | 7.9347 | -2.3947 | -4.2474 | -5.2863
|  | STANTON FITZWARREN PRIMARY | HT |  |  |  |  | 20.1389 | 19.2674 | 18.6284 | 18.0105 | 17.0916 | 15.9432 | 14.3842 | 12.9495 | 11.2389 | 4.4937 | 2.4642 | 1.1589 | 15.0411 | 14.04 | 13.32 | 12.6326 | 11.6 | 10.3021 | 8.5221 | 6.8874 | 4.9263 | -2.8768 | -5.1905 | -6.6621 | 16.6211 | 15.6316 | 14.9189 | 14.2379 | 13.2147 | 11.9305 | 10.1716 | 8.5537 | 6.6158 | -1.0926 | -3.38 | -4.8368
|  | STANTON FITZWARREN PRIMARY | HE |  |  |  |  | 20.3074 | 19.6853 | 18.9411 | 18.4537 | 17.6432 | 16.8442 | 15.6189 | 14.4189 | 12.9516 | 4.5232 | 3.1705 | 2.4958 | 15.2295 | 14.5189 | 13.6684 | 13.1274 | 12.2189 | 11.3221 | 9.9221 | 8.5537 | 6.8705 | -3.0126 | -4.5863 | -5.3716 | 16.8074 | 16.1053 | 15.2632 | 14.7274 | 13.8284 | 12.94 | 11.5558 | 10.2021 | 8.5389 | -1.2126 | -2.7674 | -3.5421
|  | STANTON FITZWARREN PRIMARY | FB |  |  |  |  | 18.1579 | 17.8432 | 17.5968 | 17.32 | 16.9726 | 16.7242 | 16.2989 | 15.8505 | 15.1674 | 11.0474 | 9.9179 | 9.3389 | 12.6895 | 12.3305 | 12.0516 | 11.7379 | 11.3411 | 11.0653 | 10.5779 | 10.0632 | 9.2737 | 4.48 | 3.1779 | 2.5126 | 14.3074 | 13.9526 | 13.6768 | 13.3663 | 12.9747 | 12.6958 | 12.2137 | 11.7053 | 10.9253 | 6.1916 | 4.9063 | 4.2484
LALEHAM GSP | STAINES BSP | STANWELL PRIMARY | MINIMUM HEADROOM | TQ 06003 72766 | NO | YES | 0 | 23.4947 | 23.4 | 23.2947 | 23.0726 | 22.6316 | 22.1589 | 21.7105 | 21.2611 | 20.9926 | 14.7432 | 9.7768 | 2.9032 | 24.1168 | 24.0305 | 23.9358 | 23.7474 | 23.2274 | 22.6695 | 22.1442 | 21.6147 | 21.3147 | 13.4568 | 7.2063 | -1.4674 | 24.0926 | 24.0168 | 23.9337 | 23.7453 | 23.2389 | 22.6958 | 22.1842 | 21.6695 | 21.3747 | 13.6832 | 7.44 | -1.2168
|  | STANWELL PRIMARY | EE |  |  |  |  | 23.4947 | 23.4 | 23.2947 | 23.0989 | 22.6937 | 22.2937 | 21.9011 | 21.5 | 21.3095 | 14.7432 | 9.7768 | 2.9032 | 24.1168 | 24.0305 | 23.9358 | 23.7832 | 23.3137 | 22.8484 | 22.3884 | 21.9211 | 21.7158 | 13.4568 | 7.2063 | -1.4674 | 24.0926 | 24.0168 | 23.9337 | 23.78 | 23.3211 | 22.8674 | 22.4189 | 21.9632 | 21.7611 | 13.6832 | 7.44 | -1.2168
|  | STANWELL PRIMARY | HT |  |  |  |  | 23.5074 | 23.4189 | 23.3053 | 23.0726 | 22.6316 | 22.1589 | 21.7105 | 21.2611 | 20.9926 | 20.2663 | 10.12 | 3.8042 | 24.1274 | 24.0484 | 23.9463 | 23.7474 | 23.2274 | 22.6695 | 22.1442 | 21.6147 | 21.3147 | 20.4958 | 7.7453 | -0.18737 | 24.1021 | 24.0326 | 23.9442 | 23.7453 | 23.2389 | 22.6958 | 22.1842 | 21.6695 | 21.3747 | 20.5716 | 7.9768 | 0.058947
|  | STANWELL PRIMARY | HE |  |  |  |  | 23.5158 | 23.4253 | 23.3242 | 23.1768 | 22.8779 | 22.5021 | 22.1253 | 21.7495 | 21.5779 | 15.2305 | 10.4126 | 3.6674 | 24.1337 | 24.0516 | 23.9589 | 23.8253 | 23.5421 | 23.1053 | 22.6674 | 22.2305 | 22.0516 | 14.0389 | 7.9579 | -0.56737 | 24.1053 | 24.0316 | 23.9495 | 23.8347 | 23.5411 | 23.1158 | 22.6884 | 22.2621 | 22.0853 | 14.2663 | 8.1916 | -0.31895
|  | STANWELL PRIMARY | FB |  |  |  |  | 23.5737 | 23.5253 | 23.48 | 23.4253 | 23.3726 | 23.3168 | 23.26 | 23.1779 | 23.1042 | 21.6768 | 16.6968 | 10.7453 | 24.1905 | 24.1463 | 24.1053 | 24.0579 | 24.0105 | 23.96 | 23.9084 | 23.8621 | 23.7853 | 22.0253 | 15.7632 | 8.26 | 24.16 | 24.1221 | 24.0863 | 24.0474 | 24.0053 | 23.9621 | 23.9179 | 23.8632 | 23.7821 | 22.08 | 15.9905 | 8.4926
MANNINGTON GSP | SALISBURY BSP | STAPLEFORD PRIMARY | MINIMUM HEADROOM | SU 06871 37078 | NO | YES | 0.10526 | 15.1908 | 15.0866 | 14.9434 | 14.7971 | 14.6045 | 14.3845 | 14.1539 | 13.8971 | 13.6308 | 12.9097 | 12.315 | 11.7792 | 13.1974 | 13.0837 | 12.9258 | 12.7689 | 12.5605 | 12.3226 | 12.0711 | 11.7879 | 11.4921 | 10.6879 | 10.0153 | 9.4068 | 13.6347 | 13.5305 | 13.3874 | 13.24 | 13.0474 | 12.8274 | 12.5958 | 12.3379 | 12.0705 | 11.3463 | 10.7495 | 10.2105
|  | STAPLEFORD PRIMARY | EE |  |  |  |  | 15.1908 | 15.0866 | 14.9434 | 14.8192 | 14.6718 | 14.5287 | 14.3929 | 14.2529 | 14.1182 | 13.7834 | 13.3645 | 12.9982 | 13.1974 | 13.0837 | 12.9258 | 12.7942 | 12.6405 | 12.4911 | 12.3468 | 12.1995 | 12.0584 | 11.6763 | 11.1942 | 10.7711 | 13.6347 | 13.5305 | 13.3874 | 13.2621 | 13.1147 | 12.9716 | 12.8347 | 12.6947 | 12.56 | 12.2232 | 11.8032 | 11.4347
|  | STAPLEFORD PRIMARY | HT |  |  |  |  | 15.2129 | 15.1171 | 14.9603 | 14.7971 | 14.6045 | 14.3845 | 14.1539 | 13.8971 | 13.6308 | 12.9097 | 12.315 | 11.7792 | 13.2216 | 13.1184 | 12.9458 | 12.7689 | 12.5605 | 12.3226 | 12.0711 | 11.7879 | 11.4921 | 10.6879 | 10.0153 | 9.4068 | 13.6568 | 13.5611 | 13.4032 | 13.24 | 13.0474 | 12.8274 | 12.5958 | 12.3379 | 12.0705 | 11.3463 | 10.7495 | 10.2105
|  | STAPLEFORD PRIMARY | HE |  |  |  |  | 15.2655 | 15.1876 | 15.0697 | 14.9655 | 14.8329 | 14.7108 | 14.595 | 14.4792 | 14.3655 | 14.1982 | 13.8845 | 13.6066 | 13.2826 | 13.1995 | 13.0711 | 12.9616 | 12.8247 | 12.6984 | 12.5784 | 12.4595 | 12.3416 | 12.1437 | 11.7774 | 11.4521 | 13.7105 | 13.6326 | 13.5147 | 13.4105 | 13.2768 | 13.1547 | 13.0389 | 12.9232 | 12.8084 | 12.64 | 12.3253 | 12.0453
|  | STAPLEFORD PRIMARY | FB |  |  |  |  | 15.3276 | 15.2708 | 15.215 | 15.1676 | 15.1182 | 15.0687 | 15.0203 | 14.9761 | 14.9287 | 14.7003 | 14.4329 | 14.2003 | 13.3489 | 13.2858 | 13.2247 | 13.1732 | 13.1195 | 13.0658 | 13.0132 | 12.9647 | 12.9142 | 12.6616 | 12.3563 | 12.0889 | 13.7726 | 13.7158 | 13.66 | 13.6126 | 13.5621 | 13.5126 | 13.4642 | 13.4189 | 13.3726 | 13.1432 | 12.8747 | 12.6411
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH PRIMARY | MINIMUM HEADROOM | SU 77124 94355 | NO | YES | 0 | 17.3434 | 17.2508 | 17.1476 | 16.8455 | 16.4329 | 16.0613 | 15.6845 | 15.2939 | 14.9034 | 13.955 | 13.3287 | 12.7855 | 12.8479 | 12.6321 | 12.4047 | 12.0858 | 11.6858 | 11.3226 | 10.9553 | 10.5753 | 10.1953 | 9.2732 | 8.6658 | 8.1374 | 14.4663 | 14.22 | 13.9621 | 13.6011 | 13.1463 | 12.7411 | 12.3316 | 11.9042 | 11.4768 | 10.4368 | 9.7474 | 9.1474
|  | STOKENCHURCH PRIMARY | EE |  |  |  |  | 17.3434 | 17.2508 | 17.1497 | 16.9066 | 16.5866 | 16.3592 | 16.1255 | 15.8813 | 15.6413 | 15.1476 | 14.7118 | 14.3508 | 12.8479 | 12.6321 | 12.4047 | 12.1437 | 11.8311 | 11.6068 | 11.3763 | 11.1363 | 10.9005 | 10.4247 | 10.0037 | 9.6574 | 14.4663 | 14.22 | 13.9621 | 13.6705 | 13.3263 | 13.0895 | 12.8421 | 12.5842 | 12.3305 | 11.7726 | 11.2789 | 10.8705
|  | STOKENCHURCH PRIMARY | HT |  |  |  |  | 17.3508 | 17.2634 | 17.1476 | 16.8455 | 16.4329 | 16.0613 | 15.6845 | 15.2939 | 14.9034 | 13.955 | 13.3287 | 12.7855 | 12.8847 | 12.6847 | 12.4216 | 12.0858 | 11.6858 | 11.3226 | 10.9553 | 10.5753 | 10.1953 | 9.2732 | 8.6658 | 8.1374 | 14.5095 | 14.2832 | 13.9832 | 13.6011 | 13.1463 | 12.7411 | 12.3316 | 11.9042 | 11.4768 | 10.4368 | 9.7474 | 9.1474
|  | STOKENCHURCH PRIMARY | HE |  |  |  |  | 17.3771 | 17.2929 | 17.1982 | 17.0708 | 16.8729 | 16.6761 | 16.4771 | 16.2676 | 16.0624 | 15.8666 | 15.6182 | 15.4171 | 12.9763 | 12.8079 | 12.6205 | 12.3953 | 12.1047 | 11.91 | 11.7132 | 11.5068 | 11.3037 | 11.1174 | 10.8805 | 10.6879 | 14.6168 | 14.4284 | 14.2189 | 13.9695 | 13.6537 | 13.4516 | 13.2453 | 13.0274 | 12.8147 | 12.5832 | 12.2968 | 12.0632
|  | STOKENCHURCH PRIMARY | FB |  |  |  |  | 17.4339 | 17.3918 | 17.3529 | 17.3097 | 17.2613 | 17.2118 | 17.1655 | 17.1213 | 17.0739 | 16.7424 | 16.4382 | 16.1876 | 13.1037 | 12.9868 | 12.89 | 12.7868 | 12.6742 | 12.5911 | 12.5079 | 12.4258 | 12.3395 | 11.9826 | 11.6889 | 11.4479 | 14.7611 | 14.6274 | 14.5168 | 14.3989 | 14.2705 | 14.1789 | 14.0863 | 13.9947 | 13.8989 | 13.4968 | 13.1547 | 12.8695
MINETY GSP | STRATTON (RESERVE) BSP | STRATTON PRIMARY | MINIMUM HEADROOM | SU 16998 88837 | NO | YES | 0 | 35.0653 | 34.8158 | 34.3726 | 33.7484 | 32.84 | 31.4295 | 29.3842 | 27.3937 | 25.7411 | 22.4832 | 20.9642 | 19.4684 | 31.1095 | 30.8126 | 30.2463 | 29.44 | 28.2505 | 26.3653 | 23.9095 | 21.5642 | 19.6263 | 15.8316 | 14.0832 | 12.3516 | 31.0905 | 30.8474 | 30.4211 | 29.7821 | 28.5811 | 26.7 | 24.2516 | 21.9126 | 19.98 | 16.1947 | 14.4495 | 12.7221
|  | STRATTON PRIMARY | EE |  |  |  |  | 35.0653 | 34.8158 | 34.3726 | 33.7484 | 33.0105 | 31.9558 | 30.4916 | 28.7 | 27.1526 | 23.0484 | 21.9811 | 20.9263 | 31.1095 | 30.8126 | 30.2463 | 29.44 | 28.5011 | 27.1053 | 25.2168 | 23.1032 | 21.2842 | 16.3811 | 15.1347 | 13.8937 | 31.0905 | 30.8474 | 30.4211 | 29.7821 | 28.8453 | 27.4537 | 25.5695 | 23.4611 | 21.6474 | 16.7442 | 15.5011 | 14.2632
|  | STRATTON PRIMARY | HT |  |  |  |  | 35.1253 | 34.8895 | 34.4358 | 33.7916 | 32.84 | 31.4295 | 29.3842 | 27.3937 | 25.7411 | 22.4832 | 20.9642 | 19.4684 | 31.1874 | 30.9105 | 30.3379 | 29.5137 | 28.2505 | 26.3653 | 23.9095 | 21.5642 | 19.6263 | 15.8316 | 14.0832 | 12.3516 | 31.1484 | 30.9189 | 30.4811 | 29.8558 | 28.5811 | 26.7 | 24.2516 | 21.9126 | 19.98 | 16.1947 | 14.4495 | 12.7221
|  | STRATTON PRIMARY | HE |  |  |  |  | 35.2611 | 35.0842 | 34.6989 | 34.1232 | 33.4189 | 32.3947 | 31.0105 | 29.2242 | 27.6916 | 24.1295 | 23.3389 | 22.5232 | 31.36 | 31.1589 | 30.6695 | 29.9274 | 29.0326 | 27.6747 | 25.8147 | 23.7074 | 21.9042 | 17.6189 | 16.68 | 15.7042 | 31.2779 | 31.1063 | 30.7347 | 30.1821 | 29.3768 | 28.0211 | 26.1663 | 24.0653 | 22.2663 | 17.9789 | 17.0432 | 16.0705
|  | STRATTON PRIMARY | FB |  |  |  |  | 35.3968 | 35.2558 | 35.0653 | 34.8116 | 34.5305 | 34.1747 | 33.7084 | 33.1453 | 32.56 | 29.2558 | 28.6032 | 27.9442 | 31.5211 | 31.3474 | 31.1021 | 30.7684 | 30.3989 | 29.9221 | 29.2884 | 28.5126 | 27.7084 | 23.6011 | 22.8484 | 22.0705 | 31.4116 | 31.2737 | 31.0916 | 30.8495 | 30.58 | 30.2411 | 29.6326 | 28.8589 | 28.0558 | 23.9611 | 23.1947 | 22.42
LALEHAM GSP | STAINES BSP | SUNBURY CROSS PRIMARY | MINIMUM HEADROOM | TQ 10053 69996 | NO | YES | 0.052632 | 64.0084 | 63.1495 | 62.1737 | 58.9084 | 57.1032 | 55.0811 | 53.2853 | 51.62 | 50.0516 | 46.3137 | 43.4347 | 40.8126 | 58.9516 | 58.5611 | 58.14 | 54.6474 | 52.6442 | 50.3958 | 48.4126 | 46.5811 | 44.8632 | 40.7747 | 37.5842 | 34.6695 | 60.8168 | 60.4674 | 60.0789 | 58.8558 | 56.8705 | 54.6432 | 52.6768 | 50.8611 | 49.1558 | 45.0989 | 41.9347 | 39.0474
|  | SUNBURY CROSS PRIMARY | EE |  |  |  |  | 64.0084 | 63.1495 | 62.1832 | 60 | 58.5168 | 57.0147 | 55.7042 | 54.5042 | 53.4958 | 51.6379 | 49.7463 | 48.0874 | 58.9516 | 58.5611 | 58.1421 | 55.9263 | 54.3095 | 52.6663 | 51.2389 | 49.9453 | 48.8726 | 46.7674 | 44.6179 | 42.7232 | 60.8168 | 60.4674 | 60.08 | 59.5505 | 58.5137 | 56.8821 | 55.4653 | 54.1811 | 53.1137 | 51.0305 | 48.9042 | 47.0305
|  | SUNBURY CROSS PRIMARY | HT |  |  |  |  | 64.0232 | 63.3074 | 62.1737 | 58.9084 | 57.1032 | 55.0811 | 53.2853 | 51.62 | 50.0516 | 46.3137 | 43.4347 | 40.8126 | 58.9716 | 58.6095 | 58.14 | 54.6474 | 52.6442 | 50.3958 | 48.4126 | 46.5811 | 44.8632 | 40.7747 | 37.5842 | 34.6695 | 60.8316 | 60.5084 | 60.0789 | 58.8558 | 56.8705 | 54.6432 | 52.6768 | 50.8611 | 49.1558 | 45.0989 | 41.9347 | 39.0474
|  | SUNBURY CROSS PRIMARY | HE |  |  |  |  | 64.0674 | 63.7326 | 62.9337 | 60.8737 | 59.4705 | 58.0747 | 56.8779 | 55.7958 | 54.8979 | 54.1189 | 52.9179 | 51.8411 | 59.0316 | 58.6642 | 58.2684 | 56.9347 | 55.4116 | 53.8874 | 52.5947 | 51.4379 | 50.4979 | 49.5705 | 48.1768 | 46.9242 | 60.8758 | 60.5411 | 60.1695 | 59.6516 | 58.9347 | 58.0905 | 56.8063 | 55.6558 | 54.7189 | 53.8053 | 52.4295 | 51.1926
|  | SUNBURY CROSS PRIMARY | FB |  |  |  |  | 64.3274 | 64.1558 | 64.0042 | 63.6905 | 63.1537 | 62.5663 | 62.0589 | 61.6211 | 61.2484 | 59.6316 | 58.2726 | 57.1116 | 59.3074 | 59.1126 | 58.9463 | 58.7547 | 58.5442 | 58.3295 | 58.1242 | 57.7695 | 57.3653 | 55.5853 | 54.0558 | 52.7358 | 61.1358 | 60.9642 | 60.8126 | 60.64 | 60.4484 | 60.2558 | 60.0684 | 59.8947 | 59.7074 | 59.0253 | 58.2611 | 56.9547
FLEET-BRAMLEY GSP | BRACKNELL BSP | SUNNINGHILL PRIMARY | MINIMUM HEADROOM | SU 93757 67606 | NO | YES | 0 | 26.0874 | 25.7832 | 25.5053 | 25.2989 | 25.0558 | 24.7547 | 24.3737 | 23.9042 | 23.4032 | 21.9968 | 21.3358 | 20.7432 | 24.6316 | 24.2989 | 23.9705 | 23.7442 | 23.4842 | 23.1516 | 22.7147 | 22.1611 | 21.5674 | 19.8663 | 19.0537 | 18.3189 | 24.4442 | 24.3347 | 24.0789 | 23.8589 | 23.6042 | 23.2832 | 22.8653 | 22.3411 | 21.78 | 20.0842 | 19.2811 | 18.56
|  | SUNNINGHILL PRIMARY | EE |  |  |  |  | 26.0874 | 25.7832 | 25.5053 | 25.2989 | 25.0558 | 24.8179 | 24.5842 | 24.3505 | 24.1232 | 23.3168 | 22.8716 | 22.4958 | 24.6316 | 24.2989 | 23.9705 | 23.7442 | 23.4842 | 23.2305 | 22.9789 | 22.7284 | 22.4842 | 21.4716 | 20.9263 | 20.4621 | 24.4442 | 24.3347 | 24.0789 | 23.8589 | 23.6042 | 23.3568 | 23.1116 | 22.8663 | 22.6284 | 21.6863 | 21.1758 | 20.6979
|  | SUNNINGHILL PRIMARY | HT |  |  |  |  | 26.1189 | 25.8242 | 25.5168 | 25.3053 | 25.0674 | 24.7547 | 24.3737 | 23.9042 | 23.4032 | 21.9968 | 21.3358 | 20.7432 | 24.6368 | 24.3505 | 23.9853 | 23.7558 | 23.4989 | 23.1516 | 22.7147 | 22.1611 | 21.5674 | 19.8663 | 19.0537 | 18.3189 | 24.4516 | 24.3463 | 24.0916 | 23.8684 | 23.6189 | 23.2832 | 22.8653 | 22.3411 | 21.78 | 20.0842 | 19.2811 | 18.56
|  | SUNNINGHILL PRIMARY | HE |  |  |  |  | 26.2074 | 25.96 | 25.7411 | 25.4695 | 25.2411 | 25.0274 | 24.8211 | 24.6158 | 24.4126 | 23.8905 | 23.6137 | 23.3789 | 24.6537 | 24.5221 | 24.2684 | 23.9568 | 23.7168 | 23.4926 | 23.2779 | 23.0642 | 22.8505 | 22.1695 | 21.8168 | 21.5168 | 24.4747 | 24.3716 | 24.2579 | 24.0568 | 23.8211 | 23.6011 | 23.3884 | 23.1779 | 22.9684 | 22.3421 | 22.0158 | 21.7379
|  | SUNNINGHILL PRIMARY | FB |  |  |  |  | 26.3526 | 26.2053 | 26.1 | 25.9832 | 25.8989 | 25.8168 | 25.7379 | 25.6547 | 25.5768 | 25.2242 | 24.7053 | 24.4389 | 24.72 | 24.6768 | 24.6379 | 24.5432 | 24.4484 | 24.3558 | 24.2684 | 24.1737 | 24.0863 | 23.68 | 23.0337 | 22.7053 | 24.5474 | 24.4958 | 24.4516 | 24.4011 | 24.3495 | 24.2968 | 24.2484 | 24.2 | 24.1505 | 23.7916 | 23.1895 | 22.8821
MELKSHAM GSP | CHIPPENHAM BSP | SUTTON BENGER PRIMARY | MINIMUM HEADROOM | ST 93394 80051 | NO | YES | 0 | 15.8876 | 29.9047 | 28.9732 | 28.8732 | 28.7447 | 28.5974 | 28.4458 | 28.2711 | 25.5111 | 25.0342 | 24.6384 | 24.2858 | 13.5153 | 26.6863 | 25.5968 | 25.4884 | 25.3495 | 25.1895 | 25.0232 | 24.8305 | 21.5947 | 21.0611 | 20.6126 | 20.2116 | 14.3137 | 27.9463 | 26.9358 | 26.8316 | 26.6968 | 26.5432 | 26.3842 | 26.2011 | 23.1789 | 22.6558 | 22.2168 | 21.8253
|  | SUTTON BENGER PRIMARY | EE |  |  |  |  | 15.8876 | 29.9047 | 28.9732 | 28.8953 | 28.8016 | 28.7142 | 28.6258 | 28.5384 | 27.1637 | 26.9384 | 26.6511 | 26.4005 | 13.5153 | 26.6863 | 25.5968 | 25.5147 | 25.4158 | 25.3253 | 25.2316 | 25.14 | 23.5326 | 23.2747 | 22.9432 | 22.6537 | 14.3137 | 27.9463 | 26.9358 | 26.8547 | 26.7589 | 26.6705 | 26.5789 | 26.4895 | 24.9989 | 24.7568 | 24.4474 | 24.1768
|  | SUTTON BENGER PRIMARY | HT |  |  |  |  | 15.8982 | 29.9216 | 28.9826 | 28.8732 | 28.7447 | 28.5974 | 28.4458 | 28.2711 | 25.5111 | 25.0342 | 24.6384 | 24.2858 | 13.5279 | 26.7053 | 25.6074 | 25.4884 | 25.3495 | 25.1895 | 25.0232 | 24.8305 | 21.5947 | 21.0611 | 20.6126 | 20.2116 | 14.3253 | 27.9642 | 26.9453 | 26.8316 | 26.6968 | 26.5432 | 26.3842 | 26.2011 | 23.1789 | 22.6558 | 22.2168 | 21.8253
|  | SUTTON BENGER PRIMARY | HE |  |  |  |  | 15.9329 | 29.9668 | 29.0532 | 28.9879 | 28.9037 | 28.83 | 28.7563 | 28.6837 | 27.3226 | 27.21 | 26.99 | 26.7974 | 13.5668 | 26.7568 | 25.6874 | 25.6189 | 25.5326 | 25.4558 | 25.38 | 25.3053 | 23.7137 | 23.5811 | 23.3232 | 23.0979 | 14.3621 | 28.0126 | 27.0211 | 26.9537 | 26.8684 | 26.7926 | 26.7189 | 26.6442 | 25.1684 | 25.0453 | 24.8074 | 24.5968
|  | SUTTON BENGER PRIMARY | FB |  |  |  |  | 15.9992 | 30.0974 | 30.0647 | 30.0374 | 30.0058 | 29.9774 | 29.9468 | 29.9184 | 29.8889 | 29.7437 | 29.5626 | 29.4037 | 13.6405 | 26.9021 | 26.8663 | 26.8368 | 26.8021 | 26.7716 | 26.7389 | 26.7084 | 26.6768 | 26.5147 | 26.3084 | 26.1242 | 14.4326 | 28.1505 | 28.1158 | 28.0874 | 28.0547 | 28.0242 | 27.9937 | 27.9632 | 27.9337 | 27.7789 | 27.5853 | 27.4137
IVER 132KV GSP | UPTON BSP | SUTTON LANE PRIMARY | MINIMUM HEADROOM | TQ 02185 78595 | NO | NO | 0 | 22.3908 | 22.2666 | 22.0582 | 21.6582 | 21.1771 | 20.8024 | 20.5361 | 20.1718 | 19.8118 | 18.9592 | 18.2213 | 17.5561 | 22.9792 | 22.7939 | 22.4055 | 21.5613 | 20.5771 | 19.8866 | 19.5245 | 19.1108 | 18.7003 | 17.735 | 16.8676 | 16.0845 | 23.2508 | 23.0729 | 22.7087 | 21.9213 | 21.0013 | 20.3518 | 20.0045 | 19.6087 | 19.2161 | 18.2897 | 17.4224 | 16.6382
|  | SUTTON LANE PRIMARY | EE |  |  |  |  | 22.3908 | 22.2666 | 22.0582 | 21.6582 | 21.1771 | 20.8234 | 20.6213 | 20.4171 | 20.1845 | 19.7255 | 19.2276 | 18.7992 | 22.9792 | 22.7939 | 22.4055 | 21.5613 | 20.5771 | 19.9297 | 19.6708 | 19.4139 | 19.1624 | 18.615 | 18.0087 | 17.4866 | 23.2508 | 23.0729 | 22.7087 | 21.9213 | 21.0013 | 20.3908 | 20.1392 | 19.8908 | 19.6455 | 19.1308 | 18.5634 | 18.0413
|  | SUTTON LANE PRIMARY | HT |  |  |  |  | 22.4076 | 22.2897 | 22.0729 | 21.6603 | 21.1803 | 20.8024 | 20.5361 | 20.1718 | 19.8118 | 18.9592 | 18.2213 | 17.5561 | 23.0171 | 22.8466 | 22.4497 | 21.5813 | 20.5803 | 19.8866 | 19.5245 | 19.1108 | 18.7003 | 17.735 | 16.8676 | 16.0845 | 23.2866 | 23.1224 | 22.7487 | 21.9392 | 21.0055 | 20.3518 | 20.0045 | 19.6087 | 19.2161 | 18.2897 | 17.4224 | 16.6382
|  | SUTTON LANE PRIMARY | HE |  |  |  |  | 22.4445 | 22.3392 | 22.1466 | 21.7592 | 21.2845 | 20.9434 | 20.7529 | 20.5634 | 20.3739 | 20.2982 | 20.0108 | 19.7413 | 23.1003 | 22.9624 | 22.615 | 21.8024 | 20.8392 | 20.2171 | 19.9961 | 19.7761 | 19.5571 | 19.3371 | 18.9403 | 18.6003 | 23.3634 | 23.2297 | 22.9024 | 22.1445 | 21.2434 | 20.6582 | 20.4413 | 20.2255 | 20.0097 | 19.8087 | 19.4413 | 19.1276
|  | SUTTON LANE PRIMARY | FB |  |  |  |  | 22.5308 | 22.4624 | 22.3761 | 22.2171 | 22.0434 | 21.9097 | 21.8455 | 21.7824 | 21.7192 | 21.455 | 21.2403 | 21.0666 | 23.2171 | 23.1076 | 22.9403 | 22.5918 | 22.2076 | 21.935 | 21.8413 | 21.7497 | 21.6582 | 21.2497 | 20.8382 | 20.4792 | 23.4761 | 23.3718 | 23.215 | 22.8908 | 22.5339 | 22.2792 | 22.1897 | 22.1013 | 22.0129 | 21.6234 | 21.2371 | 20.9024
MANNINGTON GSP | WAREHAM BSP | SWANAGE PRIMARY | MINIMUM HEADROOM | SZ 02010 79296 | NO | YES | 0 | 15.4347 | 39.9221 | 39.5337 | 38.9874 | 38.3368 | 37.6242 | 36.9158 | 36.1758 | 35.4337 | 33.4989 | 32.1811 | 31.0084 | 14.3158 | 36.5758 | 36.1474 | 35.5474 | 34.8326 | 34.0516 | 33.2747 | 32.4579 | 31.5653 | 29.1495 | 27.4863 | 26.0042 | 14.6295 | 38.1263 | 37.7505 | 37.22 | 36.5905 | 35.9011 | 35.2158 | 34.3326 | 33.4126 | 30.9779 | 29.3 | 27.8063
|  | SWANAGE PRIMARY | EE |  |  |  |  | 15.4347 | 39.9221 | 39.5863 | 39.1853 | 38.6958 | 38.2295 | 37.7432 | 37.2547 | 36.7758 | 35.7011 | 34.7684 | 33.9716 | 14.3158 | 36.5758 | 36.2095 | 35.7789 | 35.2611 | 34.7663 | 34.2432 | 33.7189 | 33.2053 | 31.9768 | 30.7547 | 29.6979 | 14.6295 | 38.1263 | 37.7979 | 37.4074 | 36.9284 | 36.4716 | 35.9958 | 35.5189 | 35.0505 | 33.8411 | 32.5968 | 31.5284
|  | SWANAGE PRIMARY | HT |  |  |  |  | 15.4768 | 39.9558 | 39.5337 | 38.9874 | 38.3368 | 37.6242 | 36.9158 | 36.1758 | 35.4337 | 33.4989 | 32.1811 | 31.0084 | 14.3632 | 36.6105 | 36.1474 | 35.5474 | 34.8326 | 34.0516 | 33.2747 | 32.4579 | 31.5653 | 29.1495 | 27.4863 | 26.0042 | 14.6695 | 38.1589 | 37.7505 | 37.22 | 36.5905 | 35.9011 | 35.2158 | 34.3326 | 33.4126 | 30.9779 | 29.3 | 27.8063
|  | SWANAGE PRIMARY | HE |  |  |  |  | 15.6158 | 40.1695 | 39.8874 | 39.5316 | 39.0695 | 38.6495 | 38.2358 | 37.8221 | 37.4168 | 36.9253 | 36.3337 | 35.8284 | 14.5211 | 36.8579 | 36.5558 | 36.1779 | 35.6926 | 35.2495 | 34.8137 | 34.3779 | 33.9516 | 33.3674 | 32.6789 | 32.0811 | 14.8021 | 38.3611 | 38.0853 | 37.7368 | 37.2832 | 36.8695 | 36.4642 | 36.0568 | 35.6589 | 35.1968 | 34.6368 | 33.9337
|  | SWANAGE PRIMARY | FB |  |  |  |  | 15.7568 | 40.4232 | 40.2821 | 40.1305 | 39.9642 | 39.7958 | 39.6284 | 39.4674 | 39.2979 | 38.5926 | 37.9684 | 37.4305 | 14.7105 | 37.1242 | 36.9705 | 36.8053 | 36.6242 | 36.44 | 36.2568 | 36.0811 | 35.8958 | 35.1179 | 34.4095 | 33.7947 | 14.9747 | 38.6105 | 38.4747 | 38.3274 | 38.1663 | 38.0021 | 37.84 | 37.6832 | 37.52 | 36.8389 | 36.24 | 35.7284
MINETY GSP | SWINDON BSP | SWINDON PRIMARY | MINIMUM HEADROOM | SU 12449 86967 | NO | YES | 0 | 42.4926 | 41.6979 | 40.8716 | 39.9484 | 38.5811 | 36.8758 | 34.9716 | 33.0895 | 31.3568 | 27.5084 | 23.3884 | 19.3979 | 45.2674 | 44.5432 | 43.7821 | 42.9189 | 41.6347 | 40.0768 | 38.3579 | 36.66 | 35.0863 | 31.5642 | 27.0958 | 22.3411 | 48.3032 | 47.5326 | 46.7295 | 45.8274 | 44.4895 | 42.8358 | 40.9968 | 38.9832 | 37.0263 | 32.7116 | 27.8442 | 23.1021
|  | SWINDON PRIMARY | EE |  |  |  |  | 42.4926 | 41.6979 | 40.8716 | 39.9484 | 38.7695 | 37.4432 | 36.0242 | 34.4579 | 33 | 29.8737 | 27.0263 | 24.2905 | 45.2674 | 44.5432 | 43.7821 | 42.9189 | 41.8063 | 40.58 | 39.2905 | 37.8726 | 36.5463 | 33.8495 | 31.0137 | 27.6758 | 48.3032 | 47.5326 | 46.7295 | 45.8274 | 44.6716 | 43.38 | 42.0063 | 40.4937 | 38.9253 | 35.1905 | 31.7579 | 28.4295
|  | SWINDON PRIMARY | HT |  |  |  |  | 42.6779 | 41.94 | 41.0737 | 40.0558 | 38.5811 | 36.8758 | 34.9716 | 33.0895 | 31.3568 | 27.5084 | 23.3884 | 19.3979 | 45.4284 | 44.7516 | 43.9463 | 42.9895 | 41.6347 | 40.0768 | 38.3579 | 36.66 | 35.0863 | 31.5642 | 27.0958 | 22.3411 | 48.48 | 47.7632 | 46.9189 | 45.9221 | 44.4895 | 42.8358 | 40.9968 | 38.9832 | 37.0263 | 32.7116 | 27.8442 | 23.1021
|  | SWINDON PRIMARY | HE |  |  |  |  | 43.1232 | 42.5716 | 41.9389 | 41.1768 | 40.1084 | 38.9032 | 37.5884 | 36.1242 | 34.7674 | 32.7937 | 30.6947 | 28.6126 | 45.8189 | 45.3042 | 44.7084 | 43.9821 | 42.9653 | 41.8463 | 40.6411 | 39.3116 | 38.0716 | 36.4189 | 34.6621 | 32.6916 | 48.9063 | 48.3674 | 47.7474 | 46.9979 | 45.9474 | 44.7737 | 43.4968 | 42.08 | 40.7642 | 38.6095 | 36.0253 | 33.4368
|  | SWINDON PRIMARY | FB |  |  |  |  | 43.5589 | 43.1074 | 42.7558 | 42.38 | 41.9442 | 41.4874 | 41.0116 | 40.4947 | 39.94 | 37.2432 | 35.3726 | 33.6505 | 46.2189 | 45.8147 | 45.4937 | 45.1505 | 44.7526 | 44.3379 | 43.9095 | 43.4505 | 42.9568 | 40.6095 | 39.0011 | 37.5453 | 49.3295 | 48.8947 | 48.5537 | 48.1895 | 47.7663 | 47.3242 | 46.8653 | 46.3695 | 45.8358 | 43.2611 | 41.1821 | 39.0842
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | TADLEY PRIMARY | MINIMUM HEADROOM | SU 57753 62717 | NO | YES | 0 | 23.8211 | 23.7 | 23.5621 | 23.3684 | 23.1347 | 22.8853 | 22.6347 | 22.3884 | 22.1442 | 22.0653 | 23.1463 | 23.0695 | 25.2253 | 24.9895 | 23.8326 | 23.5053 | 23.1137 | 22.68 | 22.3495 | 22.0063 | 21.6547 | 19.6716 | 23.4421 | 23.1547 | 25.8884 | 25.6453 | 24.3537 | 24.0074 | 23.5926 | 23.1316 | 22.7895 | 22.4316 | 22.0768 | 20.0916 | 23.9663 | 23.6495
|  | TADLEY PRIMARY | EE |  |  |  |  | 23.8211 | 23.7 | 23.5653 | 23.3832 | 23.1347 | 22.9 | 22.6842 | 22.4611 | 22.24 | 22.0653 | 25.2768 | 25.1653 | 25.2253 | 24.9895 | 23.8326 | 23.5568 | 23.2326 | 22.9221 | 22.6126 | 22.2884 | 21.9705 | 19.6716 | 26.6411 | 26.5295 | 25.8884 | 25.6453 | 24.3537 | 24.0642 | 23.7274 | 23.4063 | 23.0842 | 22.7453 | 22.4126 | 20.0916 | 28.1642 | 28.0537
|  | TADLEY PRIMARY | HT |  |  |  |  | 23.8274 | 23.7126 | 23.5621 | 23.3684 | 23.1379 | 22.8853 | 22.6347 | 22.3884 | 22.1442 | 24.92 | 24.5768 | 24.2779 | 25.2737 | 25.0579 | 23.8674 | 23.5053 | 23.1137 | 22.68 | 22.3495 | 22.0063 | 21.6547 | 26.2842 | 25.9411 | 25.0853 | 25.9389 | 25.7179 | 24.3937 | 24.0074 | 23.5926 | 23.1316 | 22.7895 | 22.4316 | 22.0768 | 27.8074 | 27.4642 | 26.6326
|  | TADLEY PRIMARY | HE |  |  |  |  | 23.8537 | 23.7389 | 23.6116 | 23.4347 | 23.1895 | 22.9663 | 22.7495 | 22.5284 | 22.3126 | 22.3263 | 25.6211 | 25.5968 | 25.3642 | 25.2137 | 24.1116 | 23.88 | 23.5842 | 23.3126 | 23.0484 | 22.7758 | 22.5105 | 20.7011 | 26.9853 | 26.9611 | 26.04 | 25.8821 | 24.6663 | 24.4274 | 24.1242 | 23.8453 | 23.5747 | 23.2947 | 23.0221 | 21.1232 | 28.5095 | 28.4853
|  | TADLEY PRIMARY | FB |  |  |  |  | 23.94 | 23.8863 | 23.8358 | 23.7811 | 23.7211 | 23.6589 | 23.6 | 23.5442 | 23.4842 | 23.2663 | 23.1463 | 23.0695 | 25.4642 | 25.3926 | 25.3042 | 25.1989 | 25.0895 | 24.9758 | 24.8684 | 24.7653 | 24.6547 | 24.2095 | 23.4421 | 23.1547 | 26.1263 | 26.0726 | 25.9716 | 25.8632 | 25.7505 | 25.6337 | 25.5232 | 25.4168 | 25.3032 | 24.8305 | 23.9663 | 23.6495
IVER 132KV GSP | SLOUGH BSP | TAPLOW PRIMARY | MINIMUM HEADROOM | SU 91721 81234 | NO | NO | 0 | 32.89 | 32.7289 | 32.5395 | 32.2816 | 31.9647 | 31.6289 | 31.29 | 30.9553 | 30.6226 | 29.09 | 27.9637 | 26.97 | 25.5905 | 25.2642 | 24.9263 | 24.4905 | 23.92 | 23.2958 | 22.6389 | 21.9453 | 21.2537 | 19.5705 | 18.3568 | 17.2863 | 30.7032 | 30.52 | 30.3137 | 29.9421 | 29.3726 | 28.7516 | 28.0958 | 27.4053 | 26.7158 | 25.0379 | 23.8284 | 22.7621
|  | TAPLOW PRIMARY | EE |  |  |  |  | 32.89 | 32.7289 | 32.5447 | 32.2963 | 31.9647 | 31.6416 | 31.3353 | 31.0279 | 30.7205 | 30.4795 | 30.0658 | 29.4353 | 25.5905 | 25.2642 | 24.9263 | 24.54 | 24.0989 | 23.6674 | 23.2253 | 22.7758 | 22.3326 | 21.4453 | 20.6158 | 19.9211 | 30.7032 | 30.52 | 30.3137 | 29.9926 | 29.5526 | 29.1211 | 28.68 | 28.2305 | 27.7874 | 26.9053 | 26.08 | 25.3874
|  | TAPLOW PRIMARY | HT |  |  |  |  | 32.8942 | 32.7405 | 32.5395 | 32.2816 | 31.9711 | 31.6289 | 31.29 | 30.9553 | 30.6226 | 29.09 | 27.9637 | 26.97 | 25.6547 | 25.3558 | 24.9758 | 24.4905 | 23.92 | 23.2958 | 22.6389 | 21.9453 | 21.2537 | 19.5705 | 18.3568 | 17.2863 | 30.7158 | 30.5421 | 30.3158 | 29.9421 | 29.3726 | 28.7516 | 28.0958 | 27.4053 | 26.7158 | 25.0379 | 23.8284 | 22.7621
|  | TAPLOW PRIMARY | HE |  |  |  |  | 32.9205 | 32.7647 | 32.5868 | 32.3447 | 32.0184 | 31.7068 | 31.4037 | 31.0953 | 30.7911 | 30.8163 | 30.7753 | 30.75 | 25.8116 | 25.5684 | 25.3053 | 24.9842 | 24.5863 | 24.2053 | 23.8253 | 23.4347 | 23.0505 | 22.6937 | 22.2158 | 21.8179 | 30.7589 | 30.5916 | 30.4021 | 30.1495 | 29.8137 | 29.4926 | 29.1789 | 28.86 | 28.5032 | 28.1484 | 27.6726 | 27.2768
|  | TAPLOW PRIMARY | FB |  |  |  |  | 33.0437 | 32.9679 | 32.8995 | 32.8216 | 32.7384 | 32.6521 | 32.5679 | 32.4911 | 32.4079 | 32.1026 | 31.9332 | 31.8247 | 26.0189 | 25.8316 | 25.6895 | 25.5368 | 25.3811 | 25.2221 | 25.0642 | 24.9084 | 24.7484 | 24.0653 | 23.48 | 22.9905 | 30.8937 | 30.8032 | 30.7242 | 30.6368 | 30.5432 | 30.4474 | 30.3537 | 30.2663 | 30.1726 | 29.5189 | 28.9368 | 28.4495
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON PRIMARY | MINIMUM HEADROOM | ST 94510 07307 | NO | YES | 0 | 6.6979 | 6.6558 | 6.5895 | 6.5011 | 6.3905 | 6.2716 | 6.1526 | 6.0337 | 5.9116 | 5.5937 | 5.3832 | 5.1874 | 6.58 | 6.5274 | 6.4463 | 6.3379 | 6.2021 | 6.0568 | 5.9116 | 5.7642 | 5.6179 | 5.2516 | 5.0074 | 4.78 | 7.3863 | 7.3653 | 7.3411 | 7.2474 | 7.1168 | 6.9758 | 6.8347 | 6.6926 | 6.5505 | 6.1905 | 5.9421 | 5.7084
|  | TARRANT RUSHTON PRIMARY | EE |  |  |  |  | 6.6979 | 6.6558 | 6.6074 | 6.5484 | 6.4768 | 6.4074 | 6.3379 | 6.2705 | 6.2042 | 6.0516 | 5.9158 | 5.7842 | 6.58 | 6.5274 | 6.4705 | 6.4011 | 6.32 | 6.24 | 6.16 | 6.0821 | 6.0063 | 5.8084 | 5.6337 | 5.4758 | 7.3863 | 7.3653 | 7.3421 | 7.3084 | 7.2295 | 7.1505 | 7.0726 | 6.9968 | 6.9221 | 6.7316 | 6.5642 | 6.4116
|  | TARRANT RUSHTON PRIMARY | HT |  |  |  |  | 6.6989 | 6.6568 | 6.5895 | 6.5011 | 6.3905 | 6.2716 | 6.1526 | 6.0337 | 5.9116 | 5.5937 | 5.3832 | 5.1874 | 6.5863 | 6.5274 | 6.4463 | 6.3379 | 6.2021 | 6.0568 | 5.9116 | 5.7642 | 5.6179 | 5.2516 | 5.0074 | 4.78 | 7.3874 | 7.3674 | 7.3411 | 7.2474 | 7.1168 | 6.9758 | 6.8347 | 6.6926 | 6.5505 | 6.1905 | 5.9421 | 5.7084
|  | TARRANT RUSHTON PRIMARY | HE |  |  |  |  | 6.7053 | 6.6853 | 6.6495 | 6.5968 | 6.5316 | 6.4684 | 6.4053 | 6.3463 | 6.2874 | 6.1968 | 6.1011 | 6.0126 | 6.6105 | 6.5726 | 6.5232 | 6.4642 | 6.3895 | 6.3179 | 6.2463 | 6.18 | 6.1137 | 5.9895 | 5.8621 | 5.7453 | 7.3916 | 7.3737 | 7.3505 | 7.3189 | 7.2779 | 7.2253 | 7.1558 | 7.0905 | 7.0253 | 6.9074 | 6.7853 | 6.6726
|  | TARRANT RUSHTON PRIMARY | FB |  |  |  |  | 6.7211 | 6.7105 | 6.7011 | 6.6853 | 6.6611 | 6.6358 | 6.6116 | 6.5863 | 6.5621 | 6.4558 | 6.3663 | 6.2926 | 6.6389 | 6.6105 | 6.5884 | 6.5621 | 6.5337 | 6.5021 | 6.4737 | 6.4432 | 6.4147 | 6.2832 | 6.1705 | 6.0747 | 7.4063 | 7.3968 | 7.3884 | 7.3789 | 7.3684 | 7.3568 | 7.3463 | 7.3368 | 7.3221 | 7.1947 | 7.0853 | 6.9937
MANNINGTON GSP | SALISBURY BSP | TEFFONT PRIMARY | MINIMUM HEADROOM | ST 99837 30994 | NO | YES | 0 | 6.3958 | 6.3326 | 6.2674 | 6.1853 | 6.0758 | 5.9474 | 5.8168 | 5.6705 | 5.5168 | 5.0968 | 4.7589 | 4.4579 | 4.7558 | 4.6853 | 4.6126 | 4.5221 | 4.4021 | 4.2642 | 4.1232 | 3.9621 | 3.7937 | 3.3274 | 2.9474 | 2.6074 | 5.9053 | 5.8337 | 5.7611 | 5.6716 | 5.5516 | 5.4126 | 5.2726 | 5.1116 | 4.9432 | 4.4779 | 4.0989 | 3.7579
|  | TEFFONT PRIMARY | EE |  |  |  |  | 6.3958 | 6.3326 | 6.2674 | 6.1926 | 6.1021 | 6.0147 | 5.9253 | 5.8337 | 5.7474 | 5.5379 | 5.2989 | 5.0842 | 4.7558 | 4.6853 | 4.6126 | 4.5305 | 4.4337 | 4.3411 | 4.2474 | 4.1505 | 4.0589 | 3.8211 | 3.5453 | 3.2989 | 5.9053 | 5.8337 | 5.7611 | 5.6789 | 5.5832 | 5.4905 | 5.3958 | 5.2989 | 5.2084 | 4.9705 | 4.6958 | 4.4495
|  | TEFFONT PRIMARY | HT |  |  |  |  | 6.4063 | 6.3495 | 6.2789 | 6.1853 | 6.0758 | 5.9474 | 5.8168 | 5.6705 | 5.5168 | 5.0968 | 4.7589 | 4.4579 | 4.7705 | 4.7053 | 4.6274 | 4.5221 | 4.4021 | 4.2642 | 4.1232 | 3.9621 | 3.7937 | 3.3274 | 2.9474 | 2.6074 | 5.9189 | 5.8547 | 5.7758 | 5.6716 | 5.5516 | 5.4126 | 5.2726 | 5.1116 | 4.9432 | 4.4779 | 4.0989 | 3.7579
|  | TEFFONT PRIMARY | HE |  |  |  |  | 6.4389 | 6.3926 | 6.3421 | 6.28 | 6.1979 | 6.1242 | 6.0526 | 5.9789 | 5.9116 | 5.8263 | 5.66 | 5.5074 | 4.8084 | 4.7579 | 4.7032 | 4.6368 | 4.5516 | 4.4737 | 4.3979 | 4.3211 | 4.2505 | 4.1453 | 3.9526 | 3.7737 | 5.9579 | 5.9074 | 5.8526 | 5.7853 | 5.7 | 5.6221 | 5.5474 | 5.4695 | 5.4 | 5.2947 | 5.1021 | 4.9232
|  | TEFFONT PRIMARY | FB |  |  |  |  | 6.4758 | 6.4421 | 6.4158 | 6.3884 | 6.36 | 6.3295 | 6.3 | 6.2726 | 6.2463 | 6.1168 | 5.9611 | 5.8232 | 4.8505 | 4.8105 | 4.7811 | 4.7495 | 4.7168 | 4.6832 | 4.6505 | 4.62 | 4.5905 | 4.4432 | 4.2653 | 4.1063 | 5.9989 | 5.96 | 5.9295 | 5.8979 | 5.8663 | 5.8316 | 5.8 | 5.7684 | 5.7389 | 5.5916 | 5.4147 | 5.2558
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | TEMPLE FARM PRIMARY | MINIMUM HEADROOM | SU 84178 83872 | YES | YES | 0 | 4.6495 | 4.6379 | 4.6232 | 4.6053 | 4.5821 | 4.5568 | 4.5316 | 4.5074 | 4.4832 | 4.4284 | 4.3958 | 4.3663 | 3.98 | 3.9674 | 3.9526 | 3.9337 | 3.9105 | 3.8853 | 3.8589 | 3.8347 | 3.8095 | 3.7526 | 3.7179 | 3.6863 | 3.9253 | 3.9011 | 3.8737 | 3.8463 | 3.8147 | 3.7832 | 3.7516 | 3.7189 | 3.6863 | 3.5895 | 3.5221 | 3.4632
|  | TEMPLE FARM PRIMARY | EE |  |  |  |  | 4.6495 | 4.6379 | 4.6232 | 4.6053 | 4.5821 | 4.5579 | 4.5358 | 4.5137 | 4.4916 | 4.4747 | 4.4632 | 4.4516 | 3.98 | 3.9674 | 3.9526 | 3.9337 | 3.9105 | 3.8853 | 3.8632 | 3.84 | 3.8179 | 3.7979 | 3.7842 | 3.7716 | 3.9253 | 3.9011 | 3.8737 | 3.8463 | 3.8147 | 3.7832 | 3.7516 | 3.7189 | 3.6863 | 3.6253 | 3.5779 | 3.5389
|  | TEMPLE FARM PRIMARY | HT |  |  |  |  | 4.6505 | 4.6389 | 4.6242 | 4.6053 | 4.5821 | 4.5568 | 4.5316 | 4.5074 | 4.4832 | 4.4284 | 4.3958 | 4.3663 | 3.9811 | 3.9695 | 3.9537 | 3.9337 | 3.9105 | 3.8853 | 3.8589 | 3.8347 | 3.8095 | 3.7526 | 3.7179 | 3.6863 | 3.9305 | 3.9084 | 3.8832 | 3.8547 | 3.8242 | 3.7905 | 3.7579 | 3.7232 | 3.6905 | 3.5895 | 3.5221 | 3.4632
|  | TEMPLE FARM PRIMARY | HE |  |  |  |  | 4.6537 | 4.6421 | 4.6284 | 4.6105 | 4.5874 | 4.5653 | 4.5421 | 4.52 | 4.4989 | 4.4989 | 4.4958 | 4.4937 | 3.9853 | 3.9726 | 3.9589 | 3.9411 | 3.9168 | 3.8947 | 3.8716 | 3.8495 | 3.8274 | 3.8263 | 3.8232 | 3.82 | 3.9432 | 3.9253 | 3.9053 | 3.8821 | 3.8547 | 3.8274 | 3.7989 | 3.7726 | 3.7484 | 3.7295 | 3.7084 | 3.6926
|  | TEMPLE FARM PRIMARY | FB |  |  |  |  | 4.6611 | 4.6558 | 4.6505 | 4.6453 | 4.6389 | 4.6337 | 4.6274 | 4.6221 | 4.6158 | 4.5947 | 4.5832 | 4.5747 | 3.9926 | 3.9874 | 3.9811 | 3.9758 | 3.9695 | 3.9632 | 3.9568 | 3.9516 | 3.9453 | 3.9221 | 3.9095 | 3.9 | 3.9579 | 3.9442 | 3.9337 | 3.9221 | 3.9105 | 3.9 | 3.8884 | 3.8779 | 3.8663 | 3.8232 | 3.7853 | 3.7558
MELKSHAM GSP | CHIPPENHAM BSP | TETBURY PRIMARY | MINIMUM HEADROOM | ST 89708 93444 | NO | YES | 0.061053 | 9.1474 | 9.0589 | 8.9526 | 8.8105 | 8.6358 | 8.2547 | 7.8589 | 7.4442 | 7.0295 | 5.9495 | 5.1547 | 4.3305 | 8.1916 | 8.0232 | 7.6968 | 7.36 | 6.9147 | 6.4779 | 6.0442 | 5.5895 | 5.1337 | 3.94 | 3.0537 | 2.1295 | 8.6389 | 8.4758 | 8.1642 | 7.8411 | 7.3989 | 6.9579 | 6.5211 | 6.0632 | 5.6042 | 4.4011 | 3.5063 | 2.5737
|  | TETBURY PRIMARY | EE |  |  |  |  | 9.1474 | 9.0589 | 8.9537 | 8.8232 | 8.6474 | 8.4863 | 8.3032 | 8.0547 | 7.8116 | 7.2379 | 6.6716 | 6.0726 | 8.1916 | 8.0232 | 7.6968 | 7.4368 | 7.1137 | 6.8537 | 6.5695 | 6.2947 | 6.0295 | 5.3811 | 4.7411 | 4.0568 | 8.6389 | 8.4758 | 8.1642 | 7.9137 | 7.5989 | 7.3379 | 7.0516 | 6.7747 | 6.5084 | 5.8537 | 5.2084 | 4.5168
|  | TETBURY PRIMARY | HT |  |  |  |  | 9.1547 | 9.0726 | 8.9526 | 8.8105 | 8.6358 | 8.2547 | 7.8589 | 7.4442 | 7.0295 | 5.9495 | 5.1547 | 4.3305 | 8.2263 | 8.0653 | 7.7095 | 7.36 | 6.9147 | 6.4779 | 6.0442 | 5.5895 | 5.1337 | 3.94 | 3.0537 | 2.1295 | 8.6716 | 8.5158 | 8.1758 | 7.8411 | 7.3989 | 6.9579 | 6.5211 | 6.0632 | 5.6042 | 4.4011 | 3.5063 | 2.5737
|  | TETBURY PRIMARY | HE |  |  |  |  | 9.1789 | 9.1011 | 9.0021 | 8.8811 | 8.7074 | 8.5579 | 8.4095 | 8.26 | 8.1137 | 7.9937 | 7.6326 | 7.1947 | 8.3126 | 8.1926 | 7.9032 | 7.6811 | 7.3968 | 7.1684 | 6.94 | 6.7232 | 6.5147 | 6.24 | 5.8179 | 5.3126 | 8.7537 | 8.6368 | 8.36 | 8.1453 | 7.8684 | 7.6442 | 7.4211 | 7.2084 | 7 | 6.7221 | 6.2947 | 5.7842
|  | TETBURY PRIMARY | FB |  |  |  |  | 9.2389 | 9.1989 | 9.1589 | 9.1168 | 9.0716 | 9.0274 | 8.9832 | 8.9442 | 8.9 | 8.7411 | 8.6063 | 8.2379 | 8.4326 | 8.3411 | 8.2011 | 8.0989 | 7.9947 | 7.8989 | 7.8032 | 7.7179 | 7.6284 | 7.2674 | 6.8737 | 6.4379 | 8.8695 | 8.7811 | 8.6484 | 8.5495 | 8.4495 | 8.3568 | 8.2663 | 8.1832 | 8.0968 | 7.7495 | 7.3558 | 6.9158
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM PRIMARY | MINIMUM HEADROOM | SU 52758 66466 | NO | YES | 0.10526 | 35.6668 | 35.3574 | 35.0247 | 34.5426 | 33.9542 | 32.6974 | 30.8953 | 28.3742 | 26.5184 | 20.8216 | 17.9658 | 16.1595 | 30.6021 | 29.9011 | 29.3032 | 28.24 | 26.8737 | 25.1958 | 23.1811 | 20.3179 | 18.2368 | 11.78 | 8.5663 | 6.5642 | 32.8126 | 32.1411 | 31.5505 | 30.4895 | 29.1221 | 27.4442 | 25.4284 | 22.5653 | 20.4832 | 14.0316 | 10.8158 | 8.8126
|  | THATCHAM PRIMARY | EE |  |  |  |  | 35.6668 | 35.3574 | 35.03 | 34.5932 | 33.9932 | 33.41 | 32.4721 | 30.7595 | 29.4521 | 25.2311 | 22.9784 | 21.7774 | 30.6021 | 29.9011 | 29.3211 | 28.6632 | 27.7042 | 26.5642 | 25.0158 | 23.0947 | 21.6453 | 16.7526 | 14.1747 | 12.8084 | 32.8126 | 32.1411 | 31.5695 | 30.9116 | 29.9526 | 28.8116 | 27.2632 | 25.3421 | 23.8926 | 18.9979 | 16.4253 | 15.0579
|  | THATCHAM PRIMARY | HT |  |  |  |  | 35.6889 | 35.4016 | 35.0247 | 34.5426 | 33.9542 | 32.6974 | 30.8953 | 28.3742 | 26.5184 | 20.8216 | 17.9658 | 16.1595 | 30.7253 | 30.0811 | 29.3032 | 28.24 | 26.8737 | 25.1958 | 23.1811 | 20.3179 | 18.2368 | 11.78 | 8.5663 | 6.5642 | 32.9284 | 32.3116 | 31.5505 | 30.4895 | 29.1221 | 27.4442 | 25.4284 | 22.5653 | 20.4832 | 14.0316 | 10.8158 | 8.8126
|  | THATCHAM PRIMARY | HE |  |  |  |  | 35.7574 | 35.4753 | 35.1721 | 34.7563 | 34.1668 | 33.6153 | 33.0511 | 31.8468 | 30.6479 | 27.2963 | 25.5626 | 24.8574 | 31.0147 | 30.4716 | 30.0305 | 29.4895 | 28.6053 | 27.5611 | 26.14 | 24.3453 | 23.0242 | 19.0811 | 17.0611 | 16.2432 | 33.2 | 32.6779 | 32.2463 | 31.7147 | 30.8547 | 29.8095 | 28.3884 | 26.5937 | 25.2716 | 21.3274 | 19.3074 | 18.4884
|  | THATCHAM PRIMARY | FB |  |  |  |  | 35.99 | 35.8479 | 35.7268 | 35.5911 | 35.4363 | 35.2732 | 35.1005 | 34.9332 | 34.7595 | 32.6068 | 30.8332 | 30.0184 | 31.5884 | 31.2232 | 30.9811 | 30.7263 | 30.38 | 29.9316 | 29.2747 | 28.5958 | 27.9232 | 24.9389 | 22.9063 | 21.98 | 33.7463 | 33.3989 | 33.1663 | 32.9211 | 32.5895 | 32.1632 | 31.5242 | 30.8442 | 30.1716 | 27.1874 | 25.1526 | 24.2263
NORTH HYDE GSP | NORTH HYDE BSP | THE GREEN PRIMARY | MINIMUM HEADROOM | TQ 12414 79503 | NO | NO | 0 | Generation Headroom Winter (MVA) 2027: 14.3253; Generation Headroom Winter (MVA) 2028: 12.9632; Generation Headroom Winter (MVA) 2029: 10.3989 | 13.7821 | 12.3389 | 9.6095 | [9 empty] | 12.4368 | 12.3895 | 10.9432
|  | THE GREEN PRIMARY | EE |  |  |  |  | Generation Headroom Winter (MVA) 2027: 14.3863; Generation Headroom Winter (MVA) 2028: 13.1358; Generation Headroom Winter (MVA) 2029: 10.8011 | 13.8105 | 12.5242 | 10.0389 | [9 empty] | 12.4368 | 12.3895 | 11.4189
|  | THE GREEN PRIMARY | HT |  |  |  |  | Generation Headroom Winter (MVA) 2027: 14.3253; Generation Headroom Winter (MVA) 2028: 12.9632; Generation Headroom Winter (MVA) 2029: 10.3989 | 13.7821 | 12.3389 | 9.6095 | [9 empty] | 12.4411 | 12.3989 | 10.9432
|  | THE GREEN PRIMARY | HE |  |  |  |  | Generation Headroom Winter (MVA) 2027: 14.4411; Generation Headroom Winter (MVA) 2028: 13.2105; Generation Headroom Winter (MVA) 2029: 10.8937 | 13.8411 | 12.6032 | 10.1368 | [9 empty] | 12.4421 | 12.3926 | 11.5274
|  | THE GREEN PRIMARY | FB |  |  |  |  | Generation Headroom Winter (MVA) 2027: 14.8442; Generation Headroom Winter (MVA) 2028: 14.2611; Generation Headroom Winter (MVA) 2029: 13.2589 | 14.0421 | 13.72 | 12.6537 | [9 empty] | 12.4705 | 12.4411 | 12.4147
FLEET-BRAMLEY GSP | READING TOWN BSP | THE MALL PRIMARY | MINIMUM HEADROOM | SU 71319 73293 | NO | YES | 0 | 35.5748 | 35.5085 | 35.4232 | 33.5864 | 32.3232 | 31.539 | 30.8558 | 30.1421 | 29.4316 | 28.4958 | 27.8085 | 27.1716 | 34.3621 | 34.2937 | 34.1937 | 33.3411 | 32.1421 | 31.3927 | 30.74 | 29.9769 | 29.1758 | 28.1474 | 27.3874 | 26.6821 | 34.4937 | 34.4274 | 34.3421 | 34.0885 | 32.6632 | 31.7874 | 31.0274 | 30.2316 | 29.44 | 28.4211 | 27.6706 | 26.9727
|  | THE MALL PRIMARY | EE |  |  |  |  | 35.5748 | 35.5095 | 35.4327 | 33.6158 | 32.3464 | 31.5685 | 30.8632 | 30.1548 | 29.4537 | 28.8253 | 28.3064 | 27.8516 | 34.3621 | 34.2937 | 34.1969 | 33.3695 | 32.1632 | 31.4221 | 30.7485 | 29.9843 | 29.1937 | 28.4843 | 27.899 | 27.3864 | 34.4937 | 34.4285 | 34.3516 | 34.12 | 32.6874 | 31.819 | 31.0316 | 30.2411 | 29.459 | 28.7579 | 28.18 | 27.6748
|  | THE MALL PRIMARY | HT |  |  |  |  | 35.579 | 35.5148 | 35.4295 | 33.5864 | 32.3232 | 31.539 | 30.8558 | 30.1421 | 29.4316 | 28.4958 | 27.8085 | 27.1716 | 34.3674 | 34.299 | 34.1937 | 33.3411 | 32.1421 | 31.3927 | 30.74 | 29.9769 | 29.1758 | 28.1474 | 27.3874 | 26.6821 | 34.4979 | 34.4337 | 34.3485 | 34.0885 | 32.6632 | 31.7874 | 31.0274 | 30.2316 | 29.44 | 28.4211 | 27.6706 | 26.9727
|  | THE MALL PRIMARY | HE |  |  |  |  | 35.5811 | 35.5085 | 35.4232 | 33.7421 | 32.4716 | 31.7043 | 31.0421 | 30.3811 | 29.7274 | 29.4706 | 29.1674 | 28.9011 | 34.3716 | 34.2979 | 34.1937 | 33.4874 | 32.279 | 31.5474 | 30.9137 | 30.2579 | 29.5232 | 29.2264 | 28.88 | 28.5769 | 34.5 | 34.4274 | 34.3421 | 34.1464 | 32.8369 | 31.9811 | 31.2443 | 30.5095 | 29.7832 | 29.4906 | 29.1485 | 28.8495
|  | THE MALL PRIMARY | FB |  |  |  |  | 35.6306 | 35.5885 | 35.5516 | 35.5095 | 35.4632 | 35.2221 | 34.9032 | 34.5643 | 34.2053 | 33.8685 | 33.4706 | 33.1527 | 34.4379 | 34.3937 | 34.3474 | 34.259 | 34.1895 | 34.1274 | 34.0674 | 34.0095 | 33.9232 | 33.5969 | 33.2148 | 32.9116 | 34.5495 | 34.5074 | 34.4706 | 34.4285 | 34.3821 | 34.3348 | 34.2832 | 34.22 | 34.1537 | 33.9769 | 33.8611 | 33.6443
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | THEALE PRIMARY | MINIMUM HEADROOM | SU 64755 71015 | NO | YES | 2.1053 | 26.0487 | 25.8961 | 24.1182 | 23.9224 | 23.695 | 23.4592 | 23.2255 | 23.0045 | 22.8561 | 22.4529 | 22.2066 | 21.9761 | 25.6276 | 25.4066 | 23.3466 | 23.1361 | 22.8918 | 22.6392 | 22.3887 | 22.1529 | 21.9961 | 21.5571 | 21.2834 | 21.0255 | 25.2897 | 25.055 | 22.8455 | 22.6234 | 22.3666 | 22.0992 | 21.8361 | 21.5876 | 21.4234 | 20.9739 | 20.7003 | 20.4424
|  | THEALE PRIMARY | EE |  |  |  |  | 26.0487 | 25.8961 | 24.1182 | 23.9539 | 23.7613 | 23.5687 | 23.3666 | 23.1961 | 23.1034 | 22.8666 | 22.6834 | 22.5087 | 25.6276 | 25.4066 | 23.3466 | 23.1708 | 22.9645 | 22.7603 | 22.5445 | 22.3634 | 22.2666 | 22.0108 | 21.8129 | 21.615 | 25.2897 | 25.055 | 22.8455 | 22.6603 | 22.4445 | 22.2297 | 22.0024 | 21.8129 | 21.7129 | 21.4413 | 21.2308 | 21.0308
|  | THEALE PRIMARY | HT |  |  |  |  | 26.0571 | 25.9118 | 24.1213 | 23.9224 | 23.695 | 23.4592 | 23.2255 | 23.0045 | 22.8561 | 22.4529 | 22.2066 | 21.9761 | 25.6392 | 25.4276 | 23.3497 | 23.1361 | 22.8918 | 22.6392 | 22.3887 | 22.1529 | 21.9961 | 21.5571 | 21.2834 | 21.0255 | 25.3024 | 25.0771 | 22.8487 | 22.6234 | 22.3666 | 22.0992 | 21.8361 | 21.5876 | 21.4234 | 20.9739 | 20.7003 | 20.4424
|  | THEALE PRIMARY | HE |  |  |  |  | 26.075 | 25.935 | 24.1845 | 24.0297 | 23.8424 | 23.6613 | 23.4824 | 23.3339 | 23.2634 | 23.1803 | 23.0855 | 22.9824 | 25.6666 | 25.4645 | 23.4182 | 23.2529 | 23.0539 | 22.8613 | 22.6708 | 22.5139 | 22.4413 | 22.3497 | 22.2466 | 22.1339 | 25.3318 | 25.1171 | 22.9224 | 22.7487 | 22.5403 | 22.3382 | 22.1371 | 21.9739 | 21.9013 | 21.8013 | 21.6918 | 21.5718
|  | THEALE PRIMARY | FB |  |  |  |  | 26.155 | 26.0813 | 26.035 | 25.9845 | 25.9287 | 25.8708 | 25.8076 | 25.7571 | 25.7318 | 25.635 | 25.515 | 25.3992 | 25.7782 | 25.6697 | 25.6055 | 25.5339 | 25.4571 | 25.3739 | 25.2845 | 25.2129 | 25.1834 | 25.0645 | 24.8961 | 24.7687 | 25.4497 | 25.335 | 25.2666 | 25.1908 | 25.1087 | 25.0213 | 24.9266 | 24.8508 | 24.8203 | 24.6971 | 24.5192 | 24.3834
MELKSHAM GSP | ANDOVER BSP | THRUXTON PRIMARY | MINIMUM HEADROOM | SU 29134 45674 | NO | YES | 0 | 7.1642 | 7.1179 | 7.0632 | 6.8547 | 6.1842 | 5.5242 | 4.8547 | 4.1789 | 3.4884 | -8.3663 | -18.0284 | -22.4 | 6.5884 | 6.4916 | 6.2368 | 5.7495 | 4.9579 | 4.1779 | 3.3916 | 2.5968 | 1.8011 | -12.1263 | -23.4863 | -28.6158 | 6.5895 | 6.4926 | 6.2389 | 5.7526 | 4.9632 | 4.1853 | 3.4011 | 2.6084 | 1.8147 | -12.0716 | -23.3968 | -28.5105
|  | THRUXTON PRIMARY | EE |  |  |  |  | 7.1642 | 7.1179 | 7.0674 | 6.8547 | 6.1842 | 5.5242 | 4.8653 | 4.2011 | 3.5232 | -4.8295 | -8.5611 | -13.3295 | 6.5884 | 6.4916 | 6.2368 | 5.7495 | 4.9579 | 4.1779 | 3.3989 | 2.6168 | 1.8326 | -7.9958 | -12.3832 | -17.9926 | 6.5895 | 6.4926 | 6.2389 | 5.7526 | 4.9632 | 4.1853 | 3.4074 | 2.6274 | 1.8463 | -7.9526 | -12.3263 | -17.9189
|  | THRUXTON PRIMARY | HT |  |  |  |  | 7.1663 | 7.1221 | 7.0632 | 6.8737 | 6.2095 | 5.5326 | 4.8547 | 4.1789 | 3.4884 | -8.3663 | -18.0284 | -22.4 | 6.6074 | 6.52 | 6.2611 | 5.7726 | 4.9895 | 4.1905 | 3.3916 | 2.5968 | 1.8011 | -12.1263 | -23.4863 | -28.6158 | 6.6084 | 6.52 | 6.2632 | 5.7758 | 4.9937 | 4.1979 | 3.4011 | 2.6084 | 1.8147 | -12.0716 | -23.3968 | -28.5105
|  | THRUXTON PRIMARY | HE |  |  |  |  | 7.1779 | 7.1368 | 7.0895 | 6.98 | 6.3221 | 5.6789 | 5.0389 | 4.3958 | 3.7368 | -4.4663 | -8.1053 | -12.8 | 6.6589 | 6.5905 | 6.3589 | 5.8937 | 5.1179 | 4.3568 | 3.6 | 2.8389 | 2.0768 | -7.5874 | -11.8716 | -17.3989 | 6.6589 | 6.5916 | 6.36 | 5.8968 | 5.1221 | 4.3632 | 3.6084 | 2.8495 | 2.0905 | -7.5453 | -11.8158 | -17.3274
|  | THRUXTON PRIMARY | FB |  |  |  |  | 7.2116 | 7.1916 | 7.1747 | 7.1547 | 7.1326 | 6.8621 | 6.5537 | 6.2221 | 5.8632 | 4.3126 | -0.66842 | -4.7916 | 6.7168 | 6.6642 | 6.5579 | 6.3589 | 6.0726 | 5.7337 | 5.3653 | 4.9695 | 4.54 | 2.6916 | -3.1684 | -8.0211 | 6.7179 | 6.6642 | 6.5589 | 6.3611 | 6.0747 | 5.7368 | 5.3695 | 4.9747 | 4.5463 | 2.7042 | -3.1389 | -7.9768
MELKSHAM GSP | WEST GRAFTON BSP | TIDWORTH PRIMARY | MINIMUM HEADROOM | SU 24088 49593 | NO | YES | 0 | 17.4221 | 17.16 | 16.6295 | 15.5063 | 14.48 | 13.4021 | 12.2305 | 10.8116 | 9.2653 | 3.9684 | 1.6453 | 0.34105 | 14.9916 | 14.3895 | 13.5147 | 12.2863 | 11.1389 | 9.9358 | 8.6253 | 7.0263 | 5.2821 | -0.73895 | -3.3621 | -4.8179 | 13.2853 | 12.6516 | 11.7263 | 10.4811 | 9.3516 | 8.1663 | 6.8758 | 5.3042 | 3.5884 | -2.3253 | -4.9042 | -6.3379
|  | TIDWORTH PRIMARY | EE |  |  |  |  | 17.4221 | 17.16 | 16.6295 | 15.5579 | 14.6379 | 13.7484 | 12.8011 | 11.6579 | 10.4368 | 6.0211 | 4.0947 | 3.1853 | 14.9916 | 14.3895 | 13.5147 | 12.3453 | 11.3242 | 10.3358 | 9.2758 | 7.9926 | 6.6179 | 1.5526 | -0.64421 | -1.6747 | 13.2853 | 12.6516 | 11.7263 | 10.5379 | 9.5337 | 8.5589 | 7.5168 | 6.2537 | 4.9011 | -0.069474 | -2.2263 | -3.2379
|  | TIDWORTH PRIMARY | HT |  |  |  |  | 17.4442 | 17.1989 | 16.6737 | 15.5063 | 14.48 | 13.4021 | 12.2305 | 10.8116 | 9.2653 | 3.9684 | 1.6453 | 0.34105 | 15.0463 | 14.4705 | 13.5611 | 12.2863 | 11.1389 | 9.9358 | 8.6253 | 7.0263 | 5.2821 | -0.73895 | -3.3621 | -4.8179 | 13.3432 | 12.7368 | 11.7768 | 10.4811 | 9.3516 | 8.1663 | 6.8758 | 5.3042 | 3.5884 | -2.3253 | -4.9042 | -6.3379
|  | TIDWORTH PRIMARY | HE |  |  |  |  | 17.4979 | 17.2589 | 16.9095 | 15.88 | 14.9853 | 14.1316 | 13.2316 | 12.1389 | 10.9642 | 6.9853 | 5.3295 | 4.6474 | 15.1695 | 14.6326 | 13.8084 | 12.7095 | 11.7179 | 10.7695 | 9.7663 | 8.5421 | 7.2211 | 2.6274 | 0.72526 | -0.055789 | 13.4726 | 12.9074 | 12.0379 | 10.8968 | 9.92 | 8.9863 | 7.9979 | 6.7926 | 5.4926 | 0.99053 | -0.87579 | -1.6432
|  | TIDWORTH PRIMARY | FB |  |  |  |  | 17.6179 | 17.4884 | 17.3432 | 17.1705 | 16.9853 | 16.6095 | 16.1863 | 15.6411 | 15.0011 | 12.1947 | 10.9779 | 10.3979 | 15.3811 | 15.0747 | 14.6947 | 14.2337 | 13.8832 | 13.4884 | 13.0389 | 12.42 | 11.6916 | 8.4905 | 7.1074 | 6.4505 | 13.6926 | 13.3695 | 12.9684 | 12.48 | 12.1105 | 11.6937 | 11.2242 | 10.6158 | 9.9 | 6.7568 | 5.3979 | 4.7526
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY PRIMARY | MINIMUM HEADROOM | ST 93438 29127 | NO | YES | 0.21053 | 8.7811 | 8.6779 | 8.5747 | 8.4547 | 8.3042 | 8.1337 | 7.9589 | 7.7063 | 7.4484 | 6.8411 | 6.4211 | 6.0516 | 7.1937 | 7.0832 | 6.9705 | 6.8442 | 6.6863 | 6.5042 | 6.3179 | 6.04 | 5.7547 | 5.0853 | 4.6179 | 4.2053 | 7.6695 | 7.6105 | 7.5474 | 7.46 | 7.3326 | 7.1516 | 6.9653 | 6.6874 | 6.4021 | 5.7337 | 5.2663 | 4.8547
|  | TISBURY PRIMARY | EE |  |  |  |  | 8.7811 | 8.6779 | 8.5747 | 8.4547 | 8.3116 | 8.1737 | 8.0368 | 7.8389 | 7.6432 | 7.3032 | 7.0074 | 6.7611 | 7.1937 | 7.0832 | 6.9705 | 6.8442 | 6.6947 | 6.5505 | 6.4074 | 6.1905 | 5.9779 | 5.5895 | 5.2537 | 4.9716 | 7.6695 | 7.6105 | 7.5474 | 7.4642 | 7.3411 | 7.1979 | 7.0537 | 6.8379 | 6.6253 | 6.2358 | 5.9011 | 5.62
|  | TISBURY PRIMARY | HT |  |  |  |  | 8.8011 | 8.7095 | 8.5968 | 8.4589 | 8.3042 | 8.1337 | 7.9589 | 7.7063 | 7.4484 | 6.8411 | 6.4211 | 6.0516 | 7.2168 | 7.1179 | 6.9968 | 6.8505 | 6.6863 | 6.5042 | 6.3179 | 6.04 | 5.7547 | 5.0853 | 4.6179 | 4.2053 | 7.6737 | 7.6211 | 7.5495 | 7.46 | 7.3326 | 7.1516 | 6.9653 | 6.6874 | 6.4021 | 5.7337 | 5.2663 | 4.8547
|  | TISBURY PRIMARY | HE |  |  |  |  | 8.8516 | 8.7768 | 8.6979 | 8.5968 | 8.4674 | 8.3474 | 8.2326 | 8.0589 | 7.8863 | 7.7232 | 7.5389 | 7.3821 | 7.2747 | 7.1958 | 7.1116 | 7.0063 | 6.8737 | 6.7505 | 6.6316 | 6.4442 | 6.2579 | 6.0642 | 5.8505 | 5.6684 | 7.6884 | 7.6368 | 7.58 | 7.5 | 7.3905 | 7.2905 | 7.1947 | 7.0905 | 6.9042 | 6.7116 | 6.4979 | 6.3158
|  | TISBURY PRIMARY | FB |  |  |  |  | 8.9137 | 8.8568 | 8.8147 | 8.7684 | 8.72 | 8.6726 | 8.6242 | 8.5484 | 8.4674 | 8.2253 | 8.0242 | 7.8568 | 7.3411 | 7.2789 | 7.2326 | 7.1821 | 7.1305 | 7.0789 | 7.0263 | 6.9411 | 6.8516 | 6.5832 | 6.3568 | 6.1653 | 7.7284 | 7.7011 | 7.6779 | 7.6516 | 7.6232 | 7.5947 | 7.5663 | 7.5368 | 7.4979 | 7.2295 | 7.0042 | 6.8126
LOVEDEAN GSP | FAREHAM (MAIN) BSP | TITCHFIELD PRIMARY | MINIMUM HEADROOM | SU 54104 05695 | NO | YES | 1.0421 | 16.0063 | 15.7137 | 15.2958 | 14.7274 | 14.1347 | 28.4263 | 27.0474 | 25.6589 | 24.2758 | 21.2032 | 20.0432 | 19.0042 | 13.3979 | 13.1663 | 12.84 | 12.2179 | 11.5558 | 25.76 | 24.1516 | 22.5305 | 20.9158 | 17.3842 | 16.0895 | 14.9274 | 14.0084 | 13.6726 | 13.1926 | 12.5379 | 11.8874 | 26.1063 | 24.5368 | 22.9547 | 21.38 | 17.9379 | 16.6695 | 15.5305
|  | TITCHFIELD PRIMARY | EE |  |  |  |  | 16.0063 | 15.7389 | 15.3979 | 14.9905 | 14.5 | 29.1421 | 28.7284 | 27.5737 | 26.4368 | 23.3211 | 22.5674 | 21.8926 | 13.3979 | 13.1779 | 12.9063 | 12.5516 | 12 | 26.6211 | 26.1726 | 24.8295 | 23.5063 | 19.7779 | 18.9179 | 18.1453 | 14.0084 | 13.7074 | 13.32 | 12.8621 | 12.3189 | 26.9432 | 26.5011 | 25.1895 | 23.8979 | 20.2726 | 19.4389 | 18.6842
|  | TITCHFIELD PRIMARY | HT |  |  |  |  | 16.0421 | 15.7137 | 15.2958 | 14.7274 | 14.1347 | 28.4263 | 27.0474 | 25.6589 | 24.2758 | 21.2032 | 20.0432 | 19.0042 | 13.4211 | 13.1663 | 12.84 | 12.2179 | 11.5558 | 25.76 | 24.1516 | 22.5305 | 20.9158 | 17.3842 | 16.0895 | 14.9274 | 14.0516 | 13.6726 | 13.1926 | 12.5379 | 11.8874 | 26.1063 | 24.5368 | 22.9547 | 21.38 | 17.9379 | 16.6695 | 15.5305
|  | TITCHFIELD PRIMARY | HE |  |  |  |  | 16.1747 | 15.9726 | 15.6874 | 15.3295 | 14.8726 | 29.5632 | 29.2011 | 28.6537 | 28.1116 | 26.7168 | 25.2832 | 23.8789 | 13.5168 | 13.3421 | 13.1095 | 12.8116 | 12.4221 | 27.1337 | 26.7368 | 26.1158 | 25.5116 | 23.8211 | 22.0947 | 20.4 | 14.2095 | 13.9884 | 13.6684 | 13.2695 | 12.7674 | 27.4432 | 27.0516 | 26.4411 | 25.8474 | 24.2063 | 22.5295 | 20.8832
|  | TITCHFIELD PRIMARY | FB |  |  |  |  | 16.3326 | 16.1874 | 16.0768 | 15.92 | 15.7505 | 30.5747 | 30.4547 | 30.3179 | 30.0747 | 28.8042 | 27.6947 | 26.6379 | 13.6516 | 13.5368 | 13.4474 | 13.3242 | 13.1916 | 28.0537 | 27.9526 | 27.8432 | 27.6305 | 26.1295 | 24.8158 | 23.5579 | 14.3832 | 14.2179 | 14.0937 | 13.9137 | 13.7189 | 28.5168 | 28.3842 | 28.2284 | 27.9421 | 26.4768 | 25.1979 | 23.9737
FLEET-BRAMLEY GSP | ALDERSHOT BSP | TONGHAM PRIMARY | MINIMUM HEADROOM | SU 88310 49487 | NO | YES | 0.073684 | 32.9147 | 32.4484 | 31.7474 | 30.9716 | 29.9779 | 28.7074 | 27.5158 | 26.3053 | 25.0989 | 22.1221 | 20.76 | 19.5895 | 32.22 | 31.7032 | 30.9221 | 30.0653 | 28.9642 | 27.5442 | 26.2168 | 24.8642 | 23.5179 | 20.18 | 18.6789 | 17.3895 | 32.6284 | 32.1242 | 31.3621 | 30.5253 | 29.4516 | 28.0674 | 26.7726 | 25.4379 | 24.0905 | 20.7516 | 19.2505 | 17.96
|  | TONGHAM PRIMARY | EE |  |  |  |  | 32.9147 | 32.4684 | 31.9505 | 31.4768 | 30.8726 | 30.1789 | 29.5811 | 28.9821 | 28.3895 | 26.6653 | 25.7105 | 24.9579 | 32.22 | 31.7295 | 31.16 | 30.6568 | 30.0168 | 29.2716 | 28.6326 | 27.9958 | 27.3653 | 25.3863 | 24.3053 | 23.4526 | 32.6284 | 32.1484 | 31.5916 | 31.0958 | 30.4653 | 29.7326 | 29.1021 | 28.4747 | 27.8526 | 25.9358 | 24.8747 | 24.0221
|  | TONGHAM PRIMARY | HT |  |  |  |  | 32.96 | 32.4484 | 31.7474 | 30.9716 | 29.9779 | 28.7074 | 27.5158 | 26.3053 | 25.0989 | 22.1221 | 20.76 | 19.5895 | 32.2705 | 31.7032 | 30.9221 | 30.0653 | 28.9642 | 27.5442 | 26.2168 | 24.8642 | 23.5179 | 20.18 | 18.6789 | 17.3895 | 32.6789 | 32.1242 | 31.3621 | 30.5253 | 29.4516 | 28.0674 | 26.7726 | 25.4379 | 24.0905 | 20.7516 | 19.2505 | 17.96
|  | TONGHAM PRIMARY | HE |  |  |  |  | 33.1705 | 32.8168 | 32.3789 | 31.9737 | 31.4084 | 30.7758 | 30.2537 | 29.7305 | 29.2189 | 28.1221 | 27.5621 | 27.1442 | 32.5105 | 32.1284 | 31.6537 | 31.2284 | 30.6337 | 29.9568 | 29.4084 | 28.8589 | 28.3221 | 27.0316 | 26.3842 | 25.9011 | 32.9116 | 32.5368 | 32.0705 | 31.6505 | 31.0632 | 30.3968 | 29.8547 | 29.3126 | 28.7811 | 27.5379 | 26.9116 | 26.4453
|  | TONGHAM PRIMARY | FB |  |  |  |  | 33.4284 | 33.1863 | 32.9821 | 32.8021 | 32.5832 | 32.3242 | 32.1074 | 31.8968 | 31.6747 | 30.5895 | 29.76 | 29.2053 | 32.7895 | 32.52 | 32.2947 | 32.0989 | 31.8611 | 31.5747 | 31.3379 | 31.1063 | 30.8642 | 29.6537 | 28.7158 | 28.0874 | 33.1853 | 32.9232 | 32.7032 | 32.5105 | 32.2779 | 31.9979 | 31.7653 | 31.5389 | 31.3021 | 30.1221 | 29.2116 | 28.6011
MINETY GSP | TOOTHILL BSP | TOOTHILL PRIMARY | MINIMUM HEADROOM | SU 13215 83986 | NO | YES | 0 | 32.7079 | 32.1079 | 31.4258 | 30.6479 | 29.6216 | 28.2732 | 26.6416 | 24.9805 | 23.3447 | 21.9911 | 20.6153 | 19.3279 | 29.4389 | 28.6989 | 27.8579 | 26.9042 | 25.6558 | 24.0032 | 22.1263 | 20.2126 | 18.3537 | 16.8642 | 15.2842 | 13.8253 | 28.6053 | 27.8674 | 27.0284 | 26.0779 | 24.8316 | 23.1832 | 21.3116 | 19.4032 | 17.5589 | 16.0726 | 14.4863 | 13.0295
|  | TOOTHILL PRIMARY | EE |  |  |  |  | 32.7079 | 32.1079 | 31.4258 | 30.6479 | 29.7468 | 28.5795 | 27.2058 | 25.6974 | 24.0858 | 22.4563 | 21.5184 | 20.5984 | 29.4389 | 28.6989 | 27.8579 | 26.9042 | 25.8105 | 24.3695 | 22.7716 | 21.0316 | 19.1716 | 17.3179 | 16.2463 | 15.1884 | 28.6053 | 27.8674 | 27.0284 | 26.0779 | 24.9863 | 23.5484 | 21.9537 | 20.2189 | 18.3632 | 16.5274 | 15.4579 | 14.4032
|  | TOOTHILL PRIMARY | HT |  |  |  |  | 32.7616 | 32.1753 | 31.4858 | 30.6921 | 29.6216 | 28.2732 | 26.6416 | 24.9805 | 23.3447 | 21.9911 | 20.6153 | 19.3279 | 29.5032 | 28.7811 | 27.9358 | 26.9684 | 25.6558 | 24.0032 | 22.1263 | 20.2126 | 18.3537 | 16.8642 | 15.2842 | 13.8253 | 28.6695 | 27.9495 | 27.1053 | 26.1411 | 24.8316 | 23.1832 | 21.3116 | 19.4032 | 17.5589 | 16.0726 | 14.4863 | 13.0295
|  | TOOTHILL PRIMARY | HE |  |  |  |  | 32.8774 | 32.3384 | 31.7037 | 30.9658 | 30.0879 | 28.9468 | 27.6321 | 26.1479 | 24.5637 | 23.2921 | 22.6079 | 21.9079 | 29.6421 | 28.9768 | 28.1958 | 27.2916 | 26.2274 | 24.8189 | 23.26 | 21.5495 | 19.7189 | 18.2232 | 17.4305 | 16.6147 | 28.8084 | 28.1453 | 27.3653 | 26.4642 | 25.4021 | 23.9968 | 22.4421 | 20.7368 | 18.9116 | 17.4137 | 16.6242 | 15.8095
|  | TOOTHILL PRIMARY | FB |  |  |  |  | 33.5921 | 32.8489 | 32.5511 | 32.2289 | 31.8784 | 31.4205 | 30.9016 | 30.3132 | 29.5837 | 28.1732 | 27.5416 | 26.9616 | 31.1832 | 29.6032 | 29.2358 | 28.8368 | 28.4063 | 27.8358 | 27.1874 | 26.4484 | 25.5274 | 23.8347 | 23.1137 | 22.4453 | 30.3863 | 28.7695 | 28.4021 | 28.0053 | 27.5758 | 27.0074 | 26.36 | 25.6232 | 24.7042 | 23.0158 | 22.2979 | 21.6305
NURSLING GSP | ROWNHAMS BSP | TOTTON PRIMARY | MINIMUM HEADROOM | SU 35835 13428 | NO | YES | 0 | 24.2853 | 24.1126 | 23.9242 | 23.6547 | 23.3147 | 22.9421 | 22.4389 | 21.4947 | 23.7979 | 23.3863 | 29.5158 | 27.4905 | 22.8232 | 22.6505 | 22.4621 | 22.1926 | 21.6505 | 20.8411 | 19.8705 | 18.6863 | 22.3358 | 20.9137 | 25.8937 | 23.5758 | 23.2474 | 22.8863 | 22.4189 | 21.7937 | 21.0242 | 20.2147 | 19.2463 | 18.0632 | 21.9905 | 20.2905 | 25.2811 | 22.9663
|  | TOTTON PRIMARY | EE |  |  |  |  | 24.2853 | 24.1126 | 23.9263 | 23.6726 | 23.3147 | 22.9853 | 22.6842 | 22.3432 | 35.4221 | 33.4211 | 32.5042 | 30.8547 | 22.8232 | 22.6505 | 22.4642 | 22.2105 | 21.8526 | 21.5232 | 21.0989 | 20.2684 | 32.9179 | 30.3158 | 29.2495 | 27.3284 | 23.2474 | 23.0747 | 22.4421 | 22.04 | 21.5663 | 21.1168 | 20.4726 | 19.6432 | 32.2937 | 29.6958 | 28.6316 | 26.7147
|  | TOTTON PRIMARY | HT |  |  |  |  | 24.2958 | 24.1358 | 23.9242 | 23.6547 | 23.3295 | 22.9421 | 22.4389 | 21.4947 | 33.9411 | 30.8232 | 29.5158 | 27.4905 | 22.8337 | 22.6737 | 22.4621 | 22.1926 | 21.6505 | 20.8411 | 19.8705 | 18.6863 | 30.9516 | 27.3505 | 25.8937 | 23.5758 | 23.2579 | 22.8863 | 22.4189 | 21.7937 | 21.0242 | 20.2147 | 19.2463 | 18.0632 | 30.3295 | 26.7358 | 25.2811 | 22.9663
|  | TOTTON PRIMARY | HE |  |  |  |  | 24.3347 | 24.1747 | 24 | 23.7568 | 23.4095 | 23.1011 | 22.8011 | 22.4937 | 35.6526 | 34.7295 | 34.1884 | 32.8979 | 22.8726 | 22.7126 | 22.5379 | 22.2947 | 21.9474 | 21.6389 | 21.3389 | 21.0316 | 33.8242 | 31.8705 | 31.2021 | 29.6232 | 23.2968 | 23.1368 | 22.8884 | 22.5589 | 22.1379 | 21.7537 | 21.2 | 20.4579 | 33.1989 | 31.2495 | 30.5821 | 29.0063
|  | TOTTON PRIMARY | FB |  |  |  |  | 24.4505 | 24.3726 | 24.3021 | 24.2242 | 24.1368 | 24.0484 | 23.9632 | 23.8832 | 23.7979 | 23.3863 | 36.3758 | 35.3547 | 22.9884 | 22.9105 | 22.84 | 22.7621 | 22.6747 | 22.5863 | 22.5011 | 22.4211 | 22.3358 | 20.9137 | 33.6653 | 32.4021 | 23.4126 | 23.3347 | 23.2642 | 23.1863 | 23.0989 | 22.9632 | 22.7116 | 22.3611 | 21.9905 | 20.2905 | 33.0421 | 31.7821
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK PRIMARY | MINIMUM HEADROOM | SU 45156 14783 | NO | YES | 0.52632 | 33.7721 | 33.4426 | 33.0205 | 31.9974 | 31.4584 | 30.55 | 29.6374 | 28.8037 | 27.9647 | 31.3984 | 32.9311 | 30.6574 | 27.3789 | 26.7168 | 25.9653 | 24.8811 | 24.3505 | 23.4105 | 22.46 | 21.5979 | 20.7316 | 24.2505 | 27.8147 | 25.2832 | 30.8737 | 30.22 | 29.4589 | 28.3453 | 27.8189 | 26.8621 | 25.8958 | 25.02 | 24.1389 | 27.7 | 29.5211 | 26.9916
|  | TOWNHILL PARK PRIMARY | EE |  |  |  |  | 33.7721 | 33.4426 | 33.0553 | 32.3553 | 31.4584 | 30.55 | 29.6374 | 28.8037 | 27.9647 | 39.4668 | 37.7037 | 36.2058 | 27.3789 | 26.7168 | 26.0411 | 25.2768 | 24.3505 | 23.4105 | 22.46 | 21.5979 | 20.7316 | 35.1158 | 33.1063 | 31.3979 | 30.8737 | 30.22 | 29.5379 | 28.76 | 27.8189 | 26.8621 | 25.8958 | 25.02 | 24.1389 | 36.8242 | 34.8147 | 33.1053
|  | TOWNHILL PARK PRIMARY | HT |  |  |  |  | 33.7847 | 33.4732 | 33.0205 | 31.9974 | 42.7974 | 42.1321 | 41.4721 | 40.8142 | 39.3837 | 35.5026 | 32.9311 | 30.6574 | 27.4579 | 26.7989 | 25.9653 | 24.8811 | 40.0779 | 39.0663 | 37.9305 | 36.5453 | 34.9758 | 30.6758 | 27.8147 | 25.2832 | 30.9516 | 30.3011 | 29.4589 | 28.3453 | 41.7884 | 40.7768 | 39.6411 | 38.2547 | 36.6853 | 32.3832 | 29.5211 | 26.9916
|  | TOWNHILL PARK PRIMARY | HE |  |  |  |  | 33.8279 | 33.5237 | 33.1742 | 32.6932 | 32.0311 | 31.4016 | 30.6468 | 29.9184 | 29.1837 | 40.4995 | 40.4153 | 39.6247 | 27.8011 | 27.2989 | 26.7663 | 26.1168 | 25.2621 | 24.4189 | 23.5779 | 22.8337 | 22.0821 | 37.6474 | 36.3874 | 35.2295 | 31.2863 | 30.7895 | 30.2611 | 29.6168 | 28.7674 | 27.9179 | 27.0642 | 26.3126 | 25.5537 | 39.3579 | 38.0979 | 36.9389
|  | TOWNHILL PARK PRIMARY | FB |  |  |  |  | 34.07 | 33.9247 | 33.7932 | 33.6447 | 33.4816 | 33.3047 | 33.13 | 32.9647 | 32.73 | 31.3984 | 42.7447 | 42.5374 | 28.2474 | 27.8758 | 27.5989 | 27.3063 | 26.98 | 26.6432 | 26.3053 | 25.9789 | 25.6705 | 24.2505 | 39.4989 | 38.3326 | 31.6695 | 31.3621 | 31.0884 | 30.8 | 30.4779 | 30.1453 | 29.8116 | 29.4768 | 29.1611 | 27.7 | 41.2095 | 40.0432
MINETY GSP | SWINDON BSP | TRADING ESTATE PRIMARY | MINIMUM HEADROOM | SU 13490 85868 | NO | YES | 0 | 19.5218 | 19.4429 | 17.9166 | 17.8229 | 17.4724 | 16.9829 | 16.1997 | 15.2924 | 14.5439 | 12.8787 | 12.2471 | 11.6376 | 18.3153 | 18.2289 | 16.4037 | 16.3037 | 15.8984 | 15.3279 | 14.4047 | 13.3321 | 12.45 | 10.4911 | 9.7595 | 9.0511 | 18.9758 | 18.8947 | 17.2474 | 17.1516 | 16.7789 | 16.2568 | 15.4168 | 14.4432 | 13.6411 | 11.8568 | 11.1853 | 10.5368
|  | TRADING ESTATE PRIMARY | EE |  |  |  |  | 19.5218 | 19.4429 | 17.9166 | 17.8229 | 17.7124 | 17.4334 | 16.8903 | 16.1913 | 15.5303 | 13.3966 | 12.9039 | 12.4366 | 18.3153 | 18.2289 | 16.4037 | 16.3037 | 16.1868 | 15.8679 | 15.23 | 14.4068 | 13.6268 | 11.0816 | 10.5047 | 9.9553 | 18.9758 | 18.8947 | 17.2474 | 17.1516 | 17.0379 | 16.7432 | 16.1611 | 15.4126 | 14.7032 | 12.4042 | 11.8779 | 11.3758
|  | TRADING ESTATE PRIMARY | HT |  |  |  |  | 19.5439 | 19.4724 | 17.945 | 17.8492 | 17.4724 | 16.9829 | 16.1997 | 15.2924 | 14.5439 | 12.8787 | 12.2471 | 11.6376 | 18.3395 | 18.2626 | 16.4374 | 16.3342 | 15.8984 | 15.3279 | 14.4047 | 13.3321 | 12.45 | 10.4911 | 9.7595 | 9.0511 | 18.9989 | 18.9253 | 17.2779 | 17.1789 | 16.7789 | 16.2568 | 15.4168 | 14.4432 | 13.6411 | 11.8568 | 11.1853 | 10.5368
|  | TRADING ESTATE PRIMARY | HE |  |  |  |  | 19.5808 | 19.5229 | 18.0124 | 17.9334 | 17.8282 | 17.5524 | 17.0387 | 16.3597 | 15.7124 | 13.9492 | 13.6082 | 13.2745 | 18.3826 | 18.3205 | 16.5142 | 16.4311 | 16.3226 | 16.0068 | 15.4047 | 14.6047 | 13.8426 | 11.7311 | 11.3268 | 10.93 | 19.0389 | 18.9789 | 17.3495 | 17.2684 | 17.1621 | 16.8705 | 16.3211 | 15.5937 | 14.8989 | 12.9958 | 12.6295 | 12.2705
|  | TRADING ESTATE PRIMARY | FB |  |  |  |  | 19.6229 | 19.5745 | 19.5355 | 19.4945 | 19.4492 | 19.4039 | 19.2839 | 19.0924 | 18.8766 | 17.3861 | 17.0355 | 16.7387 | 18.4289 | 18.3742 | 18.3321 | 18.2879 | 18.2384 | 18.19 | 18.0511 | 17.8247 | 17.5711 | 15.7984 | 15.3879 | 15.0384 | 19.0821 | 19.0305 | 18.9916 | 18.9484 | 18.9021 | 18.8558 | 18.7284 | 18.5221 | 18.2905 | 16.6874 | 16.3126 | 15.9947
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | TRASH GREEN PRIMARY | MINIMUM HEADROOM | SU 66254 68745 | NO | YES | 0 | 16.0824 | 15.9066 | 15.7034 | 15.355 | 14.9655 | 14.5445 | 14.1329 | 13.6887 | 13.2245 | 10.6887 | 7.9318 | 7.3255 | 14.0689 | 13.8784 | 13.6574 | 13.2732 | 12.8458 | 12.3837 | 11.9332 | 11.4416 | 10.9289 | 7.9489 | 4.8121 | 4.1353 | 14.2495 | 14.0589 | 13.8389 | 13.4547 | 13.0274 | 12.5674 | 12.1168 | 11.6263 | 11.1147 | 8.1442 | 5.0147 | 4.3389
|  | TRASH GREEN PRIMARY | EE |  |  |  |  | 16.0824 | 15.9066 | 15.7266 | 15.5182 | 15.2761 | 15.0382 | 14.7982 | 14.5655 | 14.3329 | 10.6887 | 8.8118 | 8.4255 | 14.0689 | 13.8784 | 13.6837 | 13.4647 | 13.2111 | 12.9637 | 12.7121 | 12.4679 | 12.2237 | 7.9489 | 5.7553 | 5.3121 | 14.2495 | 14.0589 | 13.8642 | 13.6453 | 13.3926 | 13.1453 | 12.8926 | 12.6484 | 12.4053 | 8.1442 | 5.9558 | 5.5137
|  | TRASH GREEN PRIMARY | HT |  |  |  |  | 16.1161 | 15.9529 | 15.7034 | 15.355 | 14.9655 | 14.5445 | 14.1329 | 13.6887 | 13.2245 | 11.4792 | 7.9318 | 7.3255 | 14.1079 | 13.9321 | 13.6574 | 13.2732 | 12.8458 | 12.3837 | 11.9332 | 11.4416 | 10.9289 | 8.9458 | 4.8121 | 4.1353 | 14.2874 | 14.1116 | 13.8389 | 13.4547 | 13.0274 | 12.5674 | 12.1168 | 11.6263 | 11.1147 | 9.1358 | 5.0147 | 4.3389
|  | TRASH GREEN PRIMARY | HE |  |  |  |  | 16.1939 | 16.0634 | 15.9276 | 15.7508 | 15.5297 | 15.3224 | 15.1213 | 14.9224 | 14.7245 | 11.3508 | 9.6445 | 9.3961 | 14.1984 | 14.0584 | 13.9153 | 13.7321 | 13.5047 | 13.29 | 13.0837 | 12.8784 | 12.6753 | 8.6963 | 6.69 | 6.3995 | 14.3779 | 14.2389 | 14.0958 | 13.9126 | 13.6842 | 13.4705 | 13.2642 | 13.0589 | 12.8558 | 8.8895 | 6.8895 | 6.6
|  | TRASH GREEN PRIMARY | FB |  |  |  |  | 16.3582 | 16.2634 | 16.1918 | 16.115 | 16.0329 | 15.9508 | 15.8718 | 15.7982 | 15.7213 | 15.4087 | 14.9929 | 14.715 | 14.3774 | 14.2721 | 14.1942 | 14.1121 | 14.0226 | 13.9332 | 13.8479 | 13.7689 | 13.6858 | 13.3468 | 12.8721 | 12.5553 | 14.5568 | 14.4516 | 14.3747 | 14.2916 | 14.2021 | 14.1137 | 14.0284 | 13.9495 | 13.8663 | 13.5274 | 13.0537 | 12.7379
MELKSHAM GSP | NORRINGTON BSP | TROWBRIDGE TOWN PRIMARY | MINIMUM HEADROOM | ST 84668 58036 | NO | YES | 0.10526 | 30.5579 | 30.3811 | 30.1895 | 29.9074 | 29.2295 | 28.3716 | 27.56 | 26.6884 | 25.8232 | 16.7168 | 7.1874 | 2.1726 | 29.0126 | 28.6495 | 28.2253 | 27.6432 | 26.8411 | 25.8568 | 24.9274 | 23.9221 | 22.9232 | 11.8337 | 0.62947 | -5.22 | 29.5537 | 29.1905 | 28.7695 | 28.1916 | 27.3937 | 26.4137 | 25.4905 | 24.4905 | 23.4916 | 12.4189 | 1.2474 | -4.5874
|  | TROWBRIDGE TOWN PRIMARY | EE |  |  |  |  | 30.5579 | 30.3811 | 30.1895 | 29.9305 | 29.3547 | 28.7021 | 28.0979 | 27.5095 | 26.9789 | 20.4958 | 16.5537 | 11.6179 | 29.0126 | 28.6495 | 28.2253 | 27.6874 | 27.0116 | 26.2737 | 25.5895 | 24.9337 | 24.3474 | 16.2579 | 11.5463 | 5.7358 | 29.5537 | 29.1905 | 28.7695 | 28.2347 | 27.5611 | 26.8263 | 26.1453 | 25.4916 | 24.9084 | 16.8295 | 12.1274 | 6.3347
|  | TROWBRIDGE TOWN PRIMARY | HT |  |  |  |  | 30.5747 | 30.4105 | 30.1958 | 29.9074 | 29.2295 | 28.3716 | 27.56 | 26.6884 | 25.8232 | 16.7168 | 7.1874 | 2.1726 | 29.0958 | 28.7695 | 28.3032 | 27.6432 | 26.8411 | 25.8568 | 24.9274 | 23.9221 | 22.9232 | 11.8337 | 0.62947 | -5.22 | 29.6358 | 29.3105 | 28.8474 | 28.1916 | 27.3937 | 26.4137 | 25.4905 | 24.4905 | 23.4916 | 12.4189 | 1.2474 | -4.5874
|  | TROWBRIDGE TOWN PRIMARY | HE |  |  |  |  | 30.6095 | 30.4411 | 30.2526 | 29.9947 | 29.6253 | 29.18 | 28.6705 | 28.1716 | 27.7284 | 22.0147 | 18.4958 | 13.9579 | 29.2737 | 29.0074 | 28.66 | 28.1863 | 27.5537 | 26.8726 | 26.2958 | 25.7516 | 25.2758 | 18.0232 | 13.7842 | 8.3842 | 29.8137 | 29.5484 | 29.2021 | 28.7305 | 28.1 | 27.4232 | 26.8474 | 26.3063 | 25.8305 | 18.5958 | 14.3695 | 8.9853
|  | TROWBRIDGE TOWN PRIMARY | FB |  |  |  |  | 30.7274 | 30.6421 | 30.5663 | 30.4811 | 30.3853 | 30.2895 | 30.1968 | 30.0832 | 29.9 | 28.5979 | 25.2947 | 21.4316 | 29.4821 | 29.2737 | 29.0884 | 28.8695 | 28.6221 | 28.3221 | 28.0568 | 27.8126 | 27.5926 | 26.0211 | 21.8695 | 17.1032 | 29.9979 | 29.8137 | 29.6295 | 29.4116 | 29.1663 | 28.8674 | 28.6042 | 28.3611 | 28.1432 | 26.5821 | 22.4326 | 17.6811
BRAMLEY (BASI) GSP | READING BSP | TWYFORD PRIMARY | MINIMUM HEADROOM | SU 78430 76339 | NO | YES | 0 | 17.7034 | 17.5255 | 17.3045 | 17.0118 | 16.6718 | 15.9971 | 15.2539 | 14.4939 | 13.7076 | 12.095 | 11.0697 | 9.8676 | 15.6174 | 15.2237 | 14.5289 | 13.6784 | 12.8216 | 12.0016 | 11.1837 | 10.3458 | 9.4774 | 7.7079 | 6.5784 | 5.2321 | 16.2505 | 15.8916 | 15.2705 | 14.5074 | 13.7242 | 12.9053 | 12.0884 | 11.2526 | 10.3853 | 8.62 | 7.4926 | 6.1495
|  | TWYFORD PRIMARY | EE |  |  |  |  | 17.7034 | 17.5255 | 17.315 | 17.0445 | 16.6908 | 16.3645 | 16.0045 | 15.4424 | 14.8897 | 14.0624 | 13.4371 | 12.6708 | 15.6174 | 15.2237 | 14.5447 | 13.8647 | 13.2005 | 12.6679 | 12.0584 | 11.4479 | 10.8468 | 9.9079 | 9.2016 | 8.3226 | 16.2505 | 15.8916 | 15.2842 | 14.6705 | 14.0547 | 13.5547 | 12.9621 | 12.3526 | 11.7526 | 10.8158 | 10.1105 | 9.2337
|  | TWYFORD PRIMARY | HT |  |  |  |  | 17.7087 | 17.5424 | 17.3045 | 17.0118 | 16.6718 | 15.9971 | 15.2539 | 14.4939 | 13.7076 | 12.095 | 11.0697 | 9.8676 | 15.6784 | 15.29 | 14.5289 | 13.6784 | 12.8216 | 12.0016 | 11.1837 | 10.3458 | 9.4774 | 7.7079 | 6.5784 | 5.2321 | 16.3032 | 15.9495 | 15.2705 | 14.5074 | 13.7242 | 12.9053 | 12.0884 | 11.2526 | 10.3853 | 8.62 | 7.4926 | 6.1495
|  | TWYFORD PRIMARY | HE |  |  |  |  | 17.7413 | 17.5792 | 17.3834 | 17.1276 | 16.7887 | 16.4845 | 16.1824 | 15.8761 | 15.555 | 15.2087 | 14.8855 | 14.3718 | 15.8363 | 15.5332 | 14.9332 | 14.3226 | 13.7089 | 13.2342 | 12.6932 | 12.1489 | 11.6142 | 11.1995 | 10.8247 | 10.2237 | 16.4421 | 16.1611 | 15.6242 | 15.0695 | 14.4989 | 14.0505 | 13.5474 | 13.0411 | 12.5179 | 12.1042 | 11.7305 | 11.1316
|  | TWYFORD PRIMARY | FB |  |  |  |  | 17.8771 | 17.7971 | 17.7203 | 17.6339 | 17.5455 | 17.4592 | 17.3718 | 17.2876 | 17.2003 | 16.8908 | 16.7108 | 16.2824 | 16.0511 | 15.8395 | 15.5542 | 15.2837 | 15.0437 | 14.8426 | 14.6026 | 14.3605 | 14.1047 | 13.3889 | 12.8732 | 12.2889 | 16.6442 | 16.4537 | 16.2 | 15.9589 | 15.7432 | 15.56 | 15.3442 | 15.1263 | 14.8968 | 14.2453 | 13.7768 | 13.1937
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | UNION STREET PRIMARY | MINIMUM HEADROOM | SP 52865 05849 | NO | YES | 0 | 32.5242 | 32.4042 | 32.2747 | 32.0958 | 31.8389 | 31.5611 | 31.2589 | 30.9505 | 30.3632 | 28.3916 | 27.4737 | 26.6674 | 27.2674 | 27.0074 | 26.7158 | 26.2453 | 25.1632 | 24.0979 | 23.1568 | 22.0779 | 21.1116 | 18.9158 | 17.9084 | 17.0253 | 29.8747 | 29.7547 | 29.6242 | 29.4453 | 29.0295 | 27.9611 | 27.0168 | 25.9347 | 24.9642 | 22.7621 | 21.7537 | 20.8674
|  | UNION STREET PRIMARY | EE |  |  |  |  | 32.5242 | 32.4042 | 32.2747 | 32.0968 | 31.8463 | 31.6053 | 31.3621 | 31.1074 | 30.8663 | 30.5895 | 30.3621 | 29.9 | 27.2674 | 27.0074 | 26.7484 | 26.4537 | 25.5916 | 24.8011 | 24.2063 | 23.5905 | 23.1474 | 22.0063 | 21.2905 | 20.6747 | 29.8747 | 29.7547 | 29.6242 | 29.4474 | 29.1968 | 28.6663 | 28.0705 | 27.4526 | 27.0074 | 25.8642 | 25.1463 | 24.5274
|  | UNION STREET PRIMARY | HT |  |  |  |  | 32.5379 | 32.4263 | 32.2832 | 32.0958 | 31.8684 | 31.5611 | 31.2589 | 30.9505 | 30.3632 | 28.3916 | 27.4737 | 26.6674 | 27.3021 | 27.0547 | 26.7158 | 26.2453 | 25.1632 | 24.0979 | 23.1568 | 22.0779 | 21.1116 | 18.9158 | 17.9084 | 17.0253 | 29.8884 | 29.7768 | 29.6337 | 29.4453 | 29.0295 | 27.9611 | 27.0168 | 25.9347 | 24.9642 | 22.7621 | 21.7537 | 20.8674
|  | UNION STREET PRIMARY | HE |  |  |  |  | 32.5505 | 32.4295 | 32.2937 | 32.1074 | 31.8389 | 31.6011 | 31.3716 | 31.1158 | 30.8758 | 30.8305 | 30.7358 | 30.6684 | 27.4453 | 27.2474 | 27.0379 | 26.7811 | 25.9337 | 25.1758 | 24.6621 | 24.1253 | 23.7653 | 23.2189 | 22.8484 | 22.5611 | 29.9011 | 29.78 | 29.6442 | 29.4579 | 29.1895 | 28.9453 | 28.5274 | 27.9905 | 27.6295 | 27.0811 | 26.7084 | 26.42
|  | UNION STREET PRIMARY | FB |  |  |  |  | 32.6274 | 32.5579 | 32.4947 | 32.4253 | 32.3474 | 32.2684 | 32.1916 | 32.1211 | 32.0442 | 31.7653 | 31.5832 | 31.4547 | 27.5895 | 27.4242 | 27.2979 | 27.1653 | 26.8189 | 26.4758 | 26.2263 | 25.9663 | 25.7863 | 25.0432 | 24.5232 | 24.0674 | 29.9779 | 29.9084 | 29.8453 | 29.7758 | 29.6979 | 29.6189 | 29.5421 | 29.4716 | 29.3947 | 28.9084 | 28.3874 | 27.9305
COWLEY GSP | OXFORD (OSNEY) BSP | UNIVERSITY PARKS PRIMARY | MINIMUM HEADROOM | SP 51472 07052 | NO | YES | 0 | 39.98 | 39.8642 | 39.7589 | 39.6905 | 39.6147 | 39.5316 | 39.4295 | 39.2947 | 39.1495 | 38.8758 | 38.6705 | 38.4916 | 46.6979 | 46.6632 | 46.6263 | 46.5895 | 46.5474 | 46.5011 | 46.4516 | 46.3947 | 46.3368 | 46.2779 | 46.1905 | 46.1126 | 48.0211 | 48.0021 | 47.9821 | 47.9537 | 47.9147 | 47.8779 | 47.8432 | 47.8042 | 47.7653 | 47.7211 | 47.6589 | 47.6032
|  | UNIVERSITY PARKS PRIMARY | EE |  |  |  |  | 39.9905 | 39.88 | 39.7926 | 39.7526 | 39.7032 | 39.6547 | 39.5853 | 39.5147 | 39.4484 | 39.3347 | 39.1737 | 39.0389 | 46.6989 | 46.6632 | 46.6305 | 46.6021 | 46.5621 | 46.5253 | 46.4853 | 46.4442 | 46.4042 | 46.4221 | 46.3674 | 46.3211 | 48.0211 | 48.0021 | 47.9821 | 47.9558 | 47.9179 | 47.8832 | 47.8505 | 47.8158 | 47.7821 | 47.7958 | 47.7642 | 47.7379
|  | UNIVERSITY PARKS PRIMARY | HT |  |  |  |  | 39.98 | 39.8642 | 39.7589 | 39.6905 | 39.6147 | 39.5316 | 39.4295 | 39.2947 | 39.1495 | 38.8758 | 38.6705 | 38.4916 | 46.6979 | 46.6632 | 46.6263 | 46.5895 | 46.5474 | 46.5011 | 46.4516 | 46.3947 | 46.3368 | 46.2779 | 46.1905 | 46.1126 | 48.0232 | 48.0063 | 47.9842 | 47.9537 | 47.92 | 47.8811 | 47.8432 | 47.8042 | 47.7653 | 47.7211 | 47.6589 | 47.6032
|  | UNIVERSITY PARKS PRIMARY | HE |  |  |  |  | 40.0105 | 39.9063 | 39.8242 | 39.7884 | 39.7368 | 39.6916 | 39.6495 | 39.6053 | 39.5653 | 39.5368 | 39.4568 | 39.3937 | 46.7042 | 46.6705 | 46.6379 | 46.6095 | 46.5653 | 46.5274 | 46.4905 | 46.4526 | 46.4168 | 46.4105 | 46.3863 | 46.3684 | 48.0242 | 48.0053 | 47.9842 | 47.9568 | 47.9147 | 47.8779 | 47.8432 | 47.8063 | 47.7716 | 47.7695 | 47.7579 | 47.7495
|  | UNIVERSITY PARKS PRIMARY | FB |  |  |  |  | 40.0568 | 39.9989 | 39.9589 | 39.94 | 39.9211 | 39.9011 | 39.8821 | 39.8632 | 39.8453 | 39.7705 | 39.6684 | 39.5737 | 46.7221 | 46.7021 | 46.6874 | 46.6747 | 46.6621 | 46.6474 | 46.6347 | 46.6221 | 46.6095 | 46.5589 | 46.52 | 46.4905 | 48.0358 | 48.0242 | 48.0147 | 48.0032 | 47.9916 | 47.9789 | 47.9674 | 47.9558 | 47.9442 | 47.9 | 47.8747 | 47.8589
EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD PRIMARY | MINIMUM HEADROOM | SP 51750 25667 | NO | YES | 0.77895 | 14.3161 | 13.8508 | 12.3982 | 11.2066 | 7.3171 | 5.3182 | 3.3203 | 1.3192 | -0.68079 | -4.2703 | 6.2897 | 6.2003 | 11.8384 | 11.2921 | 9.5889 | 8.1953 | 3.6258 | 1.2826 | -1.0584 | -3.4026 | -5.7468 | -9.9458 | 2.4142 | 2.3121 | 12.7726 | 12.2411 | 10.5863 | 9.2305 | 4.6747 | 2.3379 | 0.0042105 | -2.3337 | -4.6705 | -8.8579 | 3.4663 | 3.3653
|  | UPPER HEYFORD PRIMARY | EE |  |  |  |  | 14.4013 | 13.9887 | 12.6655 | 11.5855 | 8.3561 | 6.5487 | 4.7382 | 2.9192 | 1.1055 | -2.3976 | 31.1013 | 30.9645 | 11.9616 | 11.4563 | 9.9047 | 8.6405 | 4.8468 | 2.7279 | 0.60474 | -1.5268 | -3.6532 | -7.77 | 25.7058 | 25.55 | 12.8905 | 12.4 | 10.8916 | 9.6632 | 5.8916 | 3.7789 | 1.6621 | -0.46316 | -2.5832 | -6.6874 | 26.7884 | 26.6337
|  | UPPER HEYFORD PRIMARY | HT |  |  |  |  | 14.3161 | 13.8508 | 12.3982 | 11.2066 | 7.3171 | 5.3182 | 3.3203 | 1.3192 | -0.68079 | -4.2703 | 29.1455 | 28.8739 | 11.8384 | 11.2921 | 9.5889 | 8.1953 | 3.6258 | 1.2826 | -1.0584 | -3.4026 | -5.7468 | -9.9458 | 23.4395 | 23.1342 | 12.7726 | 12.2411 | 10.5863 | 9.2305 | 4.6747 | 2.3379 | 0.0042105 | -2.3337 | -4.6705 | -8.8579 | 24.5284 | 24.2232
|  | UPPER HEYFORD PRIMARY | HE |  |  |  |  | 14.4476 | 14.0624 | 12.7582 | 11.6918 | 8.4729 | 6.7676 | 5.0687 | 3.3613 | 1.6592 | -2.0882 | 31.4824 | 31.4171 | 12.0205 | 11.5395 | 10.0079 | 8.7605 | 4.9784 | 2.9795 | 0.98684 | -1.0132 | -3.01 | -7.4205 | 26.1342 | 26.0584 | 12.9495 | 12.4811 | 10.9937 | 9.7811 | 6.0232 | 4.0305 | 2.0432 | 0.048421 | -1.9411 | -6.3389 | 27.2158 | 27.14
|  | UPPER HEYFORD PRIMARY | FB |  |  |  |  | 14.6413 | 14.4655 | 13.6003 | 13.155 | 11.9887 | 10.7192 | 9.8908 | 8.9897 | 8.0118 | 6.4161 | 6.2897 | 6.2003 | 12.2889 | 12.0458 | 10.9921 | 10.4711 | 9.0984 | 7.6058 | 6.6332 | 5.5753 | 4.4258 | 2.5574 | 2.4142 | 2.3121 | 13.2105 | 12.9737 | 11.9505 | 11.4432 | 10.1116 | 8.6432 | 7.6737 | 6.6179 | 5.4716 | 3.6095 | 3.4663 | 3.3653
IVER 132KV GSP | UPTON BSP | UPTON PRIMARY | MINIMUM HEADROOM | TQ 00800 79434 | NO | NO | 0 | 31.4537 | 31.3242 | 30.7779 | 30.3621 | 29.86 | 29.3695 | 28.5979 | 27.9368 | 27.1674 | 25.5442 | 24.1947 | 23.0011 | 29.5295 | 29.3358 | 27.3695 | 26.8811 | 26.3158 | 25.7642 | 24.7768 | 23.96 | 22.9621 | 20.9516 | 19.1526 | 17.5621 | 29.2958 | 29.1284 | 29.0189 | 28.5674 | 28.0263 | 27.4989 | 26.5947 | 25.8379 | 24.9274 | 23.0663 | 21.3947 | 19.7989
|  | UPTON PRIMARY | EE |  |  |  |  | 32.0821 | 31.8305 | 30.7779 | 30.3621 | 29.86 | 29.3695 | 28.6779 | 28.1832 | 27.5863 | 26.7263 | 25.8326 | 25.0789 | 30.3747 | 29.6484 | 27.3695 | 26.8811 | 26.3158 | 25.7642 | 24.8726 | 24.3074 | 23.5716 | 22.3779 | 21.0926 | 20.0042 | 30.0526 | 29.7316 | 29.0284 | 28.5674 | 28.0263 | 27.4989 | 26.6842 | 26.1442 | 25.4632 | 24.3968 | 23.2621 | 22.2453
|  | UPTON PRIMARY | HT |  |  |  |  | 32.0989 | 31.86 | 30.8453 | 30.4168 | 29.9274 | 29.3989 | 28.5979 | 27.9368 | 27.1674 | 25.5442 | 24.1947 | 23.0011 | 30.4063 | 29.7695 | 27.4779 | 26.9768 | 26.4168 | 25.8189 | 24.7768 | 23.96 | 22.9621 | 20.9516 | 19.1526 | 17.5621 | 30.0779 | 29.7758 | 29.0674 | 28.6474 | 28.1147 | 27.5442 | 26.5947 | 25.8379 | 24.9274 | 23.0663 | 21.3947 | 19.7989
|  | UPTON PRIMARY | HE |  |  |  |  | 32.1379 | 31.8989 | 31.0716 | 30.6989 | 30.22 | 29.7716 | 29.1263 | 28.6832 | 28.1347 | 27.8642 | 27.3432 | 26.9116 | 30.48 | 30.0168 | 27.8221 | 27.4042 | 26.8811 | 26.3916 | 25.5821 | 25.1021 | 24.4474 | 23.9968 | 23.1937 | 22.5189 | 30.1368 | 29.8432 | 29.1747 | 28.8495 | 28.4158 | 28.0084 | 27.2937 | 26.8274 | 26.2137 | 25.8326 | 25.1368 | 24.5568
|  | UPTON PRIMARY | FB |  |  |  |  | 31.4537 | 31.3242 | 31.2263 | 31.1168 | 30.9968 | 30.8758 | 30.7432 | 30.6326 | 30.5053 | 30.0653 | 30.3158 | 29.8 | 29.5295 | 29.3358 | 29.2179 | 29.0432 | 28.8316 | 28.6211 | 28.2579 | 28.0589 | 27.7526 | 26.8842 | 27.1368 | 26.3916 | 29.2958 | 29.1284 | 29.0189 | 28.8979 | 28.7642 | 28.6316 | 28.4674 | 28.3442 | 28.1916 | 27.6926 | 28.3463 | 28.0505
IVER 66KV GSP |  | UXBRIDGE PRIMARY | MINIMUM HEADROOM | TQ 04984 83484 | NO | NO | 0 | 66.1116 | 89.7958 | 89.4453 | 88.0758 | 86.1926 | 84.24 | 82.2874 | 80.2758 | 78.2632 | 74.8905 | 72.9274 | 71.1621 | 63.36 | 87.0453 | 85.2853 | 83.4358 | 81.2337 | 78.9558 | 76.6779 | 74.3263 | 71.9737 | 68.0958 | 65.8463 | 63.8221 | 65.0284 | 87.3189 | 85.7863 | 83.9853 | 81.8358 | 79.6105 | 77.3853 | 75.0905 | 72.7926 | 68.9979 | 66.7947 | 64.8116
|  | UXBRIDGE PRIMARY | EE |  |  |  |  | 66.1116 | 89.9095 | 89.5358 | 88.9842 | 87.5853 | 86.1695 | 84.7074 | 83.2432 | 81.7926 | 78.96 | 77.5305 | 76.3042 | 63.36 | 87.1579 | 86.3053 | 84.5274 | 82.9158 | 81.28 | 79.5853 | 77.8884 | 76.2084 | 72.8474 | 71.1695 | 69.7263 | 65.0284 | 88.6253 | 86.6537 | 85.0463 | 83.4695 | 81.8695 | 80.2126 | 78.5547 | 76.9126 | 73.6358 | 72 | 70.5926
|  | UXBRIDGE PRIMARY | HT |  |  |  |  | 66.1158 | 89.7958 | 89.4453 | 88.0758 | 86.1926 | 84.24 | 82.2874 | 80.2758 | 78.2632 | 74.8905 | 72.9274 | 71.1621 | 63.3642 | 87.0453 | 85.2853 | 83.4358 | 81.2337 | 78.9558 | 76.6779 | 74.3263 | 71.9737 | 68.0958 | 65.8463 | 63.8221 | 65.0547 | 87.3189 | 85.7863 | 83.9853 | 81.8358 | 79.6105 | 77.3853 | 75.0905 | 72.7926 | 68.9979 | 66.7947 | 64.8116
|  | UXBRIDGE PRIMARY | HE |  |  |  |  | 66.1632 | 89.9768 | 89.6232 | 89.24 | 88.2958 | 86.9442 | 85.6011 | 84.2537 | 82.9189 | 80.7558 | 79.8284 | 79.0253 | 63.4116 | 87.2253 | 86.7968 | 85.1011 | 83.76 | 82.2 | 80.6474 | 79.0916 | 77.5495 | 74.9305 | 73.82 | 72.8558 | 65.2716 | 88.9642 | 87.0789 | 85.5989 | 84.2926 | 82.7663 | 81.2484 | 79.7263 | 78.2179 | 75.6737 | 74.5937 | 73.6547
|  | UXBRIDGE PRIMARY | FB |  |  |  |  | 66.2947 | 90.1842 | 90.0863 | 89.9158 | 89.7495 | 89.5958 | 89.4411 | 89.2863 | 88.8284 | 86.66 | 85.7084 | 84.8737 | 63.5432 | 87.4326 | 87.3347 | 87.1653 | 87 | 86.6284 | 85.9232 | 85.1621 | 84.34 | 81.8021 | 80.6989 | 79.7189 | 65.4874 | 89.2526 | 89.0621 | 88.2053 | 87.5021 | 86.9337 | 86.3189 | 85.6589 | 84.8642 | 82.3874 | 81.3084 | 80.3526
NURSLING GSP | VELMORE BSP | VELMORE PRIMARY | MINIMUM HEADROOM | SU 42935 19205 | NO | YES | 0 | 36.9605 | 36.5974 | 36.3174 | 35.8984 | 35.3184 | 34.6626 | 33.99 | 33.2468 | 32.4847 | 30.0342 | 28.7605 | 27.2584 | 33.5053 | 32.9295 | 32.5526 | 31.9695 | 31.1274 | 30.1432 | 29.1189 | 27.9347 | 26.7021 | 22.3526 | 20.5232 | 18.7979 | 26.7432 | 26.1737 | 25.8 | 25.2232 | 24.3884 | 23.4147 | 22.4011 | 21.2305 | 20.0126 | 15.7211 | 13.9137 | 12.2105
|  | VELMORE PRIMARY | EE |  |  |  |  | 36.9605 | 36.5974 | 36.3174 | 35.9058 | 35.3363 | 34.7563 | 34.2005 | 33.59 | 32.9763 | 31.2795 | 30.5658 | 29.8532 | 33.5053 | 32.9295 | 32.5526 | 31.9695 | 31.1674 | 30.3158 | 29.4737 | 28.5295 | 27.5684 | 24.16 | 22.86 | 21.6568 | 26.7432 | 26.1737 | 25.8 | 25.2232 | 24.4263 | 23.5853 | 22.7516 | 21.8168 | 20.8674 | 17.5116 | 16.2284 | 15.0442
|  | VELMORE PRIMARY | HT |  |  |  |  | 36.9995 | 36.6605 | 36.3563 | 35.8984 | 35.3184 | 34.6626 | 33.99 | 33.2468 | 32.4847 | 30.0342 | 28.7605 | 27.2584 | 33.58 | 33.0421 | 32.6453 | 31.9842 | 31.1274 | 30.1432 | 29.1189 | 27.9347 | 26.7021 | 22.3526 | 20.5232 | 18.7979 | 26.8179 | 26.2853 | 25.8916 | 25.2368 | 24.3884 | 23.4147 | 22.4011 | 21.2305 | 20.0126 | 15.7211 | 13.9137 | 12.2105
|  | VELMORE PRIMARY | HE |  |  |  |  | 37.1142 | 36.8079 | 36.5805 | 36.2132 | 35.6742 | 35.1437 | 34.6258 | 34.0574 | 33.4837 | 32.2174 | 31.7668 | 31.3437 | 33.7779 | 33.3084 | 33.0263 | 32.5211 | 31.7726 | 30.9968 | 30.2358 | 29.3768 | 28.4979 | 25.7126 | 24.8032 | 23.9295 | 27.0126 | 26.5474 | 26.2674 | 25.7674 | 25.0253 | 24.2558 | 23.5032 | 22.6526 | 21.7832 | 19.0453 | 18.1495 | 17.2905
|  | VELMORE PRIMARY | FB |  |  |  |  | 37.3184 | 37.1395 | 37.0268 | 36.8774 | 36.6974 | 36.49 | 36.2805 | 36.0468 | 35.7932 | 34.6805 | 34.1026 | 33.6784 | 34.0789 | 33.7811 | 33.6211 | 33.3916 | 33.1063 | 32.7621 | 32.4095 | 31.9968 | 31.5495 | 29.5126 | 28.4684 | 27.6779 | 27.3105 | 27.0158 | 26.8579 | 26.6305 | 26.3484 | 26.0084 | 25.6611 | 25.2537 | 24.8126 | 22.8032 | 21.7737 | 20.9947
FAWLEY GSP | COWES BSP | VENTNOR PRIMARY | MINIMUM HEADROOM | SZ 56148 77857 | NO | YES | 0 | 19.8195 | 19.6037 | 19.3763 | 19.0489 | 18.6542 | 18.2174 | 17.7711 | 17.2974 | 16.8268 | 15.5626 | 14.6605 | 13.6079 | 20.0153 | 19.7532 | 19.4826 | 19.0942 | 18.6205 | 18.0858 | 17.49 | 16.8384 | 16.1911 | 14.3668 | 12.9995 | 11.7479 | 19.9521 | 19.6637 | 19.37 | 18.9468 | 18.43 | 17.8563 | 17.2595 | 16.6058 | 15.9574 | 14.1268 | 12.7553 | 11.5005
|  | VENTNOR PRIMARY | EE |  |  |  |  | 19.8195 | 19.6037 | 19.3763 | 19.1016 | 18.7626 | 18.4332 | 18.0974 | 17.7468 | 17.4058 | 16.8058 | 16.2332 | 15.7353 | 20.0153 | 19.7532 | 19.4826 | 19.1711 | 18.8016 | 18.4416 | 18.0595 | 17.6553 | 17.2437 | 16.2458 | 15.2805 | 14.43 | 19.9521 | 19.6637 | 19.37 | 19.0363 | 18.65 | 18.2721 | 17.8658 | 17.4321 | 17.0142 | 16.0132 | 15.0437 | 14.1889
|  | VENTNOR PRIMARY | HT |  |  |  |  | 19.85 | 19.6458 | 19.3837 | 19.0489 | 18.6542 | 18.2174 | 17.7711 | 17.2974 | 16.8268 | 15.5626 | 14.6605 | 13.6079 | 20.0626 | 19.8132 | 19.4974 | 19.0942 | 18.6205 | 18.0858 | 17.49 | 16.8384 | 16.1911 | 14.3668 | 12.9995 | 11.7479 | 20.0037 | 19.7332 | 19.3889 | 18.9468 | 18.43 | 17.8563 | 17.2595 | 16.6058 | 15.9574 | 14.1268 | 12.7553 | 11.5005
|  | VENTNOR PRIMARY | HE |  |  |  |  | 19.9268 | 19.7521 | 19.5616 | 19.3163 | 18.9953 | 18.6963 | 18.4005 | 18.09 | 17.7868 | 17.5742 | 17.2321 | 16.9279 | 20.1753 | 19.9774 | 19.7637 | 19.4963 | 19.1553 | 18.8374 | 18.5195 | 18.1795 | 17.85 | 17.4868 | 16.8626 | 16.2911 | 20.0626 | 19.8995 | 19.7037 | 19.4237 | 19.0721 | 18.7437 | 18.4132 | 18.0563 | 17.7121 | 17.2658 | 16.6311 | 16.0574
|  | VENTNOR PRIMARY | FB |  |  |  |  | 20.0784 | 19.9647 | 19.8742 | 19.7753 | 19.6711 | 19.5647 | 19.4616 | 19.3584 | 19.2532 | 18.7953 | 18.3942 | 18.0511 | 20.3511 | 20.2058 | 20.0953 | 19.9763 | 19.8511 | 19.7247 | 19.6026 | 19.4753 | 19.3479 | 18.7679 | 18.1637 | 17.5795 | 20.2037 | 20.1037 | 20.0226 | 19.9153 | 19.7795 | 19.6416 | 19.5089 | 19.3689 | 19.2289 | 18.5805 | 17.9332 | 17.3468
MANNINGTON GSP | MANNINGTON BSP | VERWOOD PRIMARY | MINIMUM HEADROOM | SU 07716 10226 | NO | YES | 0 | 10.4632 | 10.1295 | 9.68 | 9.0663 | 8.3284 | 7.5263 | 6.7305 | 5.9337 | 5.1442 | 2.1474 | 0.82 | -0.55263 | 10.5126 | 10.0821 | 9.4821 | 8.6611 | 7.6747 | 6.6021 | 5.5358 | 4.4653 | 3.4021 | -0.96421 | -2.6716 | -4.2116 | 11.1032 | 10.6789 | 10.0895 | 9.2811 | 8.3126 | 7.2442 | 6.18 | 5.1116 | 4.0505 | -0.30316 | -2.0074 | -3.5442
|  | VERWOOD PRIMARY | EE |  |  |  |  | 10.4632 | 10.1295 | 9.7705 | 9.3389 | 8.8032 | 8.3 | 7.8179 | 7.3326 | 6.8611 | 3.2684 | 2.4568 | 1.6495 | 10.5126 | 10.0821 | 9.62 | 9.0832 | 8.44 | 7.8347 | 7.2453 | 6.6558 | 6.0853 | 0.36526 | -0.83263 | -1.8632 | 11.1032 | 10.6789 | 10.2232 | 9.6937 | 9.0579 | 8.46 | 7.8779 | 7.2958 | 6.7284 | 1.0242 | -0.17053 | -1.1989
|  | VERWOOD PRIMARY | HT |  |  |  |  | 10.4968 | 10.1484 | 9.68 | 9.0663 | 8.3284 | 7.5263 | 6.7305 | 5.9337 | 5.1442 | 2.1474 | 0.82 | -0.55263 | 10.5642 | 10.1021 | 9.4821 | 8.6611 | 7.6747 | 6.6021 | 5.5358 | 4.4653 | 3.4021 | -0.96421 | -2.6716 | -4.2116 | 11.1537 | 10.6989 | 10.0895 | 9.2811 | 8.3126 | 7.2442 | 6.18 | 5.1116 | 4.0505 | -0.30316 | -2.0074 | -3.5442
|  | VERWOOD PRIMARY | HE |  |  |  |  | 10.6495 | 10.3884 | 10.0926 | 9.7158 | 9.2189 | 8.7674 | 8.3253 | 7.8821 | 7.4495 | 4.2611 | 3.7116 | 3.2389 | 10.7821 | 10.46 | 10.0895 | 9.6326 | 9.0453 | 8.5084 | 7.9821 | 7.4568 | 6.9463 | 1.7326 | 0.86947 | 0.12 | 11.3674 | 11.0495 | 10.6842 | 10.2326 | 9.6516 | 9.12 | 8.5989 | 8.08 | 7.5747 | 2.3884 | 1.5284 | 0.78105
|  | VERWOOD PRIMARY | FB |  |  |  |  | 10.8432 | 10.6737 | 10.5326 | 10.38 | 10.2105 | 10.0411 | 9.8705 | 9.7063 | 9.5326 | 8.8137 | 8.2589 | 7.7968 | 11.0189 | 10.7926 | 10.6053 | 10.4042 | 10.1832 | 9.96 | 9.7358 | 9.5168 | 9.2874 | 8.3084 | 7.5126 | 6.8263 | 11.6011 | 11.3789 | 11.1947 | 10.9968 | 10.7789 | 10.56 | 10.3389 | 10.1232 | 9.8979 | 8.9368 | 8.1547 | 7.4695
NORTH HYDE GSP |  | VICARAGE FARM ROAD PRIMARY | MINIMUM HEADROOM | TQ 12358 76435 | NO | NO | 0 | 47.1219 | 84.9579 | 84.5526 | 84.0442 | 82.8137 | 80.7232 | 78.2484 | 75.6358 | 72.9074 | 67.8979 | 64.7726 | 61.7821 | 44.7356 | 81.6916 | 80.3874 | 78.9211 | 76.6705 | 74.3232 | 71.5284 | 68.5716 | 65.4768 | 59.9189 | 56.4221 | 53.0642 | 37.7293 | 75.5695 | 75.2326 | 74.7968 | 73.0526 | 70.6979 | 67.8937 | 64.9253 | 61.8211 | 56.2505 | 52.7411 | 49.3726
|  | VICARAGE FARM ROAD PRIMARY | EE |  |  |  |  | 47.1314 | 84.9632 | 84.6221 | 84.1653 | 83.5453 | 82.5074 | 81.1558 | 79.7495 | 78.36 | 74.9095 | 73.0095 | 71.1179 | 44.7482 | 82.0726 | 80.6221 | 79.2716 | 77.7274 | 76.3863 | 74.8842 | 73.3232 | 71.7779 | 67.8095 | 65.7032 | 63.5411 | 37.7377 | 75.5705 | 75.2895 | 74.8989 | 74.1137 | 72.7684 | 71.2621 | 69.6947 | 68.1474 | 64.1632 | 62.0526 | 59.8832
|  | VICARAGE FARM ROAD PRIMARY | HT |  |  |  |  | 47.1219 | 84.9579 | 84.5526 | 84.0442 | 82.8137 | 80.7232 | 78.2484 | 75.6358 | 72.9074 | 67.8979 | 64.7726 | 61.7821 | 44.7356 | 81.6916 | 80.3874 | 78.9211 | 76.6705 | 74.3232 | 71.5284 | 68.5716 | 65.4768 | 59.9189 | 56.4221 | 53.0642 | 37.7293 | 75.5695 | 75.2326 | 74.7968 | 73.0526 | 70.6979 | 67.8937 | 64.9253 | 61.8211 | 56.2505 | 52.7411 | 49.3726
|  | VICARAGE FARM ROAD PRIMARY | HE |  |  |  |  | 47.1787 | 85.0211 | 84.7326 | 84.2874 | 83.6716 | 83.1284 | 82.0568 | 80.7432 | 79.4442 | 77.0168 | 75.6432 | 74.2926 | 44.8124 | 82.6053 | 81.2895 | 80.0505 | 78.5758 | 77.3211 | 75.9242 | 74.4726 | 73.0347 | 70.1874 | 68.5979 | 67.0295 | 37.7861 | 75.6284 | 75.3579 | 74.9726 | 74.4221 | 73.7063 | 72.3063 | 70.8505 | 69.4084 | 66.5495 | 64.9526 | 63.3779
|  | VICARAGE FARM ROAD PRIMARY | FB |  |  |  |  | 47.3461 | 85.2968 | 85.1653 | 85.0179 | 84.8537 | 84.6768 | 84.4874 | 84.3032 | 84.1084 | 82.5916 | 81.2074 | 79.96 | 45.0029 | 82.9347 | 82.7853 | 82.4179 | 81.8295 | 81.3116 | 80.7242 | 80.0789 | 79.4126 | 76.4168 | 74.8537 | 73.4316 | 37.9535 | 75.9042 | 75.7726 | 75.6253 | 75.4611 | 75.2968 | 75.1368 | 74.9874 | 74.8284 | 72.7979 | 71.2295 | 69.8011
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | WALLINGFORD PRIMARY | MINIMUM HEADROOM | SU 59847 89486 | NO | YES | 0.069474 | 22.7537 | 21.9958 | 21.1853 | 20.3853 | 19.6011 | 26.3658 | 25.7868 | 25.1668 | 24.6384 | 26.4605 | 25.3711 | 24.1826 | 20.2789 | 19.3979 | 18.4589 | 17.5379 | 16.6358 | 21.7442 | 21.1211 | 20.4611 | 19.8937 | 23.4253 | 22.1979 | 20.8337 | 20.8253 | 19.9716 | 19.06 | 18.1695 | 17.3095 | 23.2895 | 22.6684 | 22.0084 | 21.4453 | 25.7 | 24.5432 | 23.2221
|  | WALLINGFORD PRIMARY | EE |  |  |  |  | 22.7537 | 21.9958 | 21.1853 | 20.3853 | 19.6011 | 26.3658 | 25.7868 | 25.1668 | 24.6384 | 26.4605 | 25.5458 | 24.6668 | 20.2789 | 19.3979 | 18.4589 | 17.5463 | 16.6758 | 21.7442 | 21.1211 | 20.4611 | 19.8937 | 23.5274 | 22.5547 | 21.5558 | 20.8253 | 19.9716 | 19.06 | 18.1695 | 17.3147 | 23.2895 | 22.6684 | 22.0084 | 21.4453 | 25.7 | 24.7621 | 23.78
|  | WALLINGFORD PRIMARY | HT |  |  |  |  | 22.7853 | 22.0316 | 21.2232 | 20.4116 | 19.6242 | 29.9363 | 29.49 | 29.0237 | 28.5721 | 26.4616 | 25.3711 | 24.1826 | 20.2968 | 19.4105 | 18.4695 | 17.5379 | 16.6358 | 27.3074 | 26.8305 | 26.3253 | 25.8347 | 23.4253 | 22.1979 | 20.8337 | 20.8516 | 19.9968 | 19.0874 | 18.1821 | 17.3095 | 29.4758 | 29.0053 | 28.5105 | 28.0316 | 25.7389 | 24.5432 | 23.2221
|  | WALLINGFORD PRIMARY | HE |  |  |  |  | 23.2084 | 22.6895 | 22.1389 | 21.5758 | 21.0063 | 27.9595 | 27.6342 | 27.3016 | 26.9774 | 29.9121 | 29.5258 | 29.2468 | 20.78 | 20.1589 | 19.5011 | 18.8432 | 18.2011 | 23.4684 | 23.1253 | 22.7747 | 22.4326 | 27.2758 | 26.7842 | 26.44 | 21.3274 | 20.7358 | 20.1095 | 19.48 | 18.8589 | 25.0368 | 24.6989 | 24.3537 | 24.0168 | 29.4863 | 29.0074 | 28.6821
|  | WALLINGFORD PRIMARY | FB |  |  |  |  | 23.4537 | 23.2021 | 22.9389 | 22.6926 | 22.4726 | 29.6542 | 29.5153 | 29.3795 | 29.2416 | 28.6858 | 28.1647 | 27.7932 | 21.1274 | 20.7653 | 20.4484 | 20.1547 | 19.8968 | 25.4032 | 25.2474 | 25.0947 | 24.9411 | 24.3095 | 23.6905 | 23.2463 | 21.6589 | 21.3147 | 21.0137 | 20.7347 | 20.4874 | 26.9011 | 26.7505 | 26.6032 | 26.4537 | 25.8442 | 25.2547 | 24.8316
COWLEY GSP | DRAYTON BSP | WANTAGE PRIMARY | MINIMUM HEADROOM | SU 41290 88304 | NO | YES | 0.10526 | 26.0411 | 25.8842 | 25.4147 | 24.6705 | 24.0421 | 23.6158 | 23.1853 | 22.7168 | 22.2337 | 20.7958 | 19.7589 | 18.4916 | 23.0011 | 22.4589 | 21.8189 | 20.9874 | 20.2968 | 19.8442 | 19.3863 | 18.8842 | 18.3653 | 16.7947 | 15.6505 | 14.2232 | 24.3042 | 23.7579 | 23.1116 | 22.2726 | 21.5768 | 21.1221 | 20.6611 | 20.1558 | 19.6337 | 18.0505 | 16.8979 | 15.4674
|  | WANTAGE PRIMARY | EE |  |  |  |  | 26.0411 | 25.8842 | 25.5147 | 24.8979 | 24.2768 | 23.9505 | 23.6326 | 23.3063 | 22.9895 | 22.2463 | 21.6589 | 20.9011 | 23.0537 | 22.5232 | 21.9358 | 21.2495 | 20.5695 | 20.2305 | 19.8958 | 19.5537 | 19.2221 | 18.3874 | 17.7337 | 16.8758 | 24.3579 | 23.8221 | 23.2284 | 22.5358 | 21.8505 | 21.5116 | 21.1758 | 20.8316 | 20.4989 | 19.6568 | 18.9958 | 18.1305
|  | WANTAGE PRIMARY | HT |  |  |  |  | 26.0453 | 25.8947 | 25.4147 | 24.6705 | 24.0421 | 23.6158 | 23.1853 | 22.7168 | 22.2337 | 20.7958 | 19.7589 | 18.4916 | 23.0011 | 22.4589 | 21.8189 | 20.9874 | 20.2968 | 19.8442 | 19.3863 | 18.8842 | 18.3653 | 16.7947 | 15.6505 | 14.2232 | 24.3042 | 23.7579 | 23.1116 | 22.2726 | 21.5768 | 21.1221 | 20.6611 | 20.1558 | 19.6337 | 18.0505 | 16.8979 | 15.4674
|  | WANTAGE PRIMARY | HE |  |  |  |  | 26.0958 | 25.9558 | 25.7979 | 25.2516 | 24.7463 | 24.3832 | 24.1095 | 23.8316 | 23.5632 | 23.2232 | 22.8926 | 22.3526 | 23.2547 | 22.8021 | 22.28 | 21.6474 | 21.1021 | 20.7158 | 20.4337 | 20.1474 | 19.8716 | 19.4758 | 19.0989 | 18.4789 | 24.5611 | 24.1042 | 23.5768 | 22.94 | 22.3905 | 22.0021 | 21.72 | 21.4326 | 21.1558 | 20.7558 | 20.3747 | 19.7474
|  | WANTAGE PRIMARY | FB |  |  |  |  | 26.1937 | 26.1189 | 26.0505 | 25.9758 | 25.8958 | 25.8242 | 25.7558 | 25.6737 | 25.5579 | 25.0884 | 24.5947 | 24.1137 | 23.44 | 23.2895 | 23.0358 | 22.7547 | 22.5032 | 22.3737 | 22.2463 | 22.1253 | 22.0021 | 21.4937 | 20.9421 | 20.3968 | 24.8716 | 24.5958 | 24.3389 | 24.0558 | 23.8021 | 23.6716 | 23.5442 | 23.4221 | 23.2979 | 22.7863 | 22.2295 | 21.68
MANNINGTON GSP | WAREHAM BSP | WAREHAM TOWN PRIMARY | MINIMUM HEADROOM | SY 92036 87463 | NO | YES | 0 | 13.4658 | 39.7968 | 39.5063 | 39.1011 | 38.6189 | 38.0926 | 37.5674 | 35.1947 | 34.6432 | 31.6958 | 30.5947 | 29.6221 | 12.3163 | 36.4011 | 36.0389 | 35.5347 | 34.9337 | 34.2789 | 33.6242 | 30.3284 | 29.6347 | 26.1053 | 24.8653 | 23.7684 | 11.1142 | 36.5537 | 36.4305 | 36.2579 | 36.0421 | 35.8232 | 35.3126 | 32.0263 | 31.3337 | 27.8116 | 26.5747 | 25.48
|  | WAREHAM TOWN PRIMARY | EE |  |  |  |  | 13.4658 | 39.7968 | 39.5568 | 39.2768 | 38.9295 | 38.6011 | 38.2505 | 36.9895 | 35.2832 | 33.8737 | 33.0705 | 30.1653 | 12.3163 | 36.4011 | 36.1126 | 35.78 | 35.3821 | 35.0021 | 34.5863 | 32.8716 | 30.5147 | 28.5916 | 27.6695 | 24.2674 | 11.1142 | 36.5537 | 36.4305 | 36.2684 | 36.0421 | 35.8295 | 35.6337 | 34.5589 | 32.2084 | 30.2895 | 29.3684 | 25.9768
|  | WAREHAM TOWN PRIMARY | HT |  |  |  |  | 13.4932 | 39.8137 | 39.5063 | 39.1011 | 38.6189 | 38.0926 | 37.5674 | 35.1947 | 34.6432 | 31.6958 | 30.5947 | 29.6221 | 12.3532 | 36.42 | 36.0389 | 35.5347 | 34.9337 | 34.2789 | 33.6242 | 30.3284 | 29.6347 | 26.1053 | 24.8653 | 23.7684 | 11.1205 | 36.5674 | 36.4316 | 36.2579 | 36.0505 | 35.8232 | 35.3126 | 32.0263 | 31.3337 | 27.8116 | 26.5747 | 25.48
|  | WAREHAM TOWN PRIMARY | HE |  |  |  |  | 13.5932 | 39.9716 | 39.7747 | 39.5263 | 39.2053 | 38.9074 | 38.6179 | 37.4168 | 35.7663 | 34.7895 | 34.3453 | 31.7011 | 12.4837 | 36.6337 | 36.4011 | 36.1137 | 35.7495 | 35.4095 | 35.0789 | 33.4474 | 31.1726 | 29.7695 | 29.1495 | 26 | 11.1458 | 36.5937 | 36.4789 | 36.3211 | 36.1011 | 35.9 | 35.7063 | 35.1358 | 32.8663 | 31.4684 | 30.8495 | 27.7095
|  | WAREHAM TOWN PRIMARY | FB |  |  |  |  | 13.7174 | 40.1526 | 40.0558 | 39.9516 | 39.8379 | 39.7221 | 39.6053 | 39.4916 | 39.3758 | 38.8811 | 38.4337 | 38.0389 | 12.6289 | 36.8368 | 36.7179 | 36.5905 | 36.4505 | 36.3084 | 36.1653 | 36.0253 | 35.8821 | 35.2611 | 34.6684 | 34.1326 | 11.2216 | 36.7221 | 36.6768 | 36.6274 | 36.5726 | 36.5168 | 36.4621 | 36.4116 | 36.3579 | 36.16 | 36.0505 | 35.82
FLEET-BRAMLEY GSP | BRACKNELL BSP | WARFIELD PRIMARY | MINIMUM HEADROOM | SU 86960 71382 | NO | YES | 1.0516 | 28.1184 | 27.8574 | 27.5711 | 27.1016 | 26.4532 | 25.7216 | 24.8984 | 24.45 | 23.4447 | 26.2458 | 24.5668 | 23.0942 | 28.1547 | 27.7211 | 27.2874 | 26.3653 | 24.9011 | 23.2053 | 21.0979 | 20.2253 | 18.9495 | 23.6726 | 22.7389 | 21.0811 | 29.4137 | 28.9958 | 28.5747 | 27.6937 | 26.3053 | 24.6989 | 22.7084 | 21.8737 | 20.6253 | 25.18 | 24.3232 | 23.6126
|  | WARFIELD PRIMARY | EE |  |  |  |  | 28.1184 | 27.8574 | 27.5753 | 27.1711 | 26.5889 | 25.9384 | 25.17 | 24.45 | 23.4447 | 28.3868 | 27.2511 | 26.3016 | 28.1547 | 27.7211 | 27.2874 | 26.5937 | 25.4832 | 24.0611 | 22.0274 | 20.2253 | 18.9495 | 27.02 | 25.7105 | 24.6126 | 29.4137 | 28.9958 | 28.5747 | 27.9084 | 26.8474 | 25.4958 | 23.5779 | 21.8737 | 20.6253 | 30.4737 | 29.1663 | 28.0705
|  | WARFIELD PRIMARY | HT |  |  |  |  | 28.1458 | 27.9005 | 27.5711 | 27.1016 | 26.4532 | 25.7216 | 24.8984 | 29.6879 | 28.3942 | 26.2458 | 24.5668 | 23.0942 | 28.2421 | 27.8421 | 27.2947 | 26.3653 | 24.9011 | 23.2053 | 21.0979 | 28.4674 | 27.0063 | 24.6284 | 22.7389 | 21.0811 | 29.4958 | 29.1095 | 28.5811 | 27.6937 | 26.3053 | 24.6989 | 22.7084 | 31.92 | 30.4611 | 28.0863 | 26.1989 | 24.5432
|  | WARFIELD PRIMARY | HE |  |  |  |  | 28.2311 | 28.0068 | 27.7574 | 27.3795 | 26.8153 | 26.1995 | 25.4479 | 24.7479 | 24.1711 | 29.7247 | 28.9405 | 28.2889 | 28.4632 | 28.1484 | 27.8158 | 27.2063 | 26.1547 | 24.8042 | 22.8347 | 21.1011 | 19.8853 | 28.5358 | 27.6137 | 26.8432 | 29.7042 | 29.3979 | 29.0726 | 28.4842 | 27.4779 | 26.1947 | 24.3368 | 22.6968 | 21.5411 | 31.9779 | 31.0674 | 30.2989
|  | WARFIELD PRIMARY | FB |  |  |  |  | 28.4184 | 28.29 | 28.1847 | 28.0511 | 27.8742 | 27.6616 | 27.3679 | 27.0953 | 26.8721 | 26.3468 | 25.9774 | 25.7016 | 28.7663 | 28.5242 | 28.3463 | 28.08 | 27.6632 | 27.0979 | 26.1768 | 25.3189 | 24.6989 | 23.6726 | 22.7663 | 22.0126 | 29.9968 | 29.7653 | 29.5937 | 29.34 | 28.9453 | 28.4116 | 27.5484 | 26.7442 | 26.1611 | 25.18 | 24.3232 | 23.6126
MELKSHAM GSP | FROME BSP | WARMINSTER PRIMARY | MINIMUM HEADROOM | ST 84936 44551 | NO | YES | 0 | 14.0076 | 13.9024 | 13.7782 | 13.6192 | 13.4108 | 13.2066 | 12.5961 | 11.7476 | 10.9508 | 9.8276 | 9.1139 | 8.4782 | 14.2658 | 13.8395 | 13.2268 | 12.6132 | 11.7816 | 10.9321 | 10.0532 | 9.0616 | 8.1332 | 6.8511 | 6.0363 | 5.31 | 12.8747 | 12.4495 | 11.8379 | 11.2253 | 10.3947 | 9.5463 | 8.6695 | 7.68 | 6.7516 | 5.4726 | 4.6568 | 3.9316
|  | WARMINSTER PRIMARY | EE |  |  |  |  | 14.0076 | 13.9024 | 13.7782 | 13.6255 | 13.4108 | 13.215 | 12.8003 | 12.1634 | 11.5697 | 10.6666 | 10.155 | 9.7224 | 14.2658 | 13.8395 | 13.2268 | 12.6205 | 11.7816 | 11.0237 | 10.2953 | 9.5553 | 8.8679 | 7.8005 | 7.2037 | 6.6984 | 12.8747 | 12.4495 | 11.8379 | 11.2326 | 10.3947 | 9.6368 | 8.9095 | 8.1716 | 7.4853 | 6.42 | 5.8242 | 5.3189
|  | WARMINSTER PRIMARY | HT |  |  |  |  | 14.0171 | 13.9182 | 13.7813 | 13.6192 | 13.4234 | 13.2066 | 12.5961 | 11.7476 | 10.9508 | 9.8276 | 9.1139 | 8.4782 | 14.3037 | 13.8932 | 13.2647 | 12.6132 | 11.8258 | 10.9321 | 10.0532 | 9.0616 | 8.1332 | 6.8511 | 6.0363 | 5.31 | 12.9126 | 12.5032 | 11.8758 | 11.2253 | 10.44 | 9.5463 | 8.6695 | 7.68 | 6.7516 | 5.4726 | 4.6568 | 3.9316
|  | WARMINSTER PRIMARY | HE |  |  |  |  | 14.0371 | 13.9403 | 13.8213 | 13.675 | 13.4624 | 13.275 | 13.0718 | 12.4613 | 11.8929 | 11.3003 | 10.9582 | 10.6697 | 14.3868 | 14.0047 | 13.43 | 12.8563 | 12.0374 | 11.3026 | 10.6142 | 9.9068 | 9.25 | 8.5321 | 8.1258 | 7.7816 | 12.9958 | 12.6147 | 12.0411 | 11.4684 | 10.6495 | 9.9168 | 9.2295 | 8.5232 | 7.8674 | 7.1505 | 6.7453 | 6.4011
|  | WARMINSTER PRIMARY | FB |  |  |  |  | 14.1066 | 14.0571 | 14.0087 | 13.9561 | 13.895 | 13.8245 | 13.7687 | 13.7118 | 13.6539 | 13.4718 | 13.3676 | 13.295 | 14.6226 | 14.4132 | 14.1584 | 13.91 | 13.5942 | 13.15 | 12.8679 | 12.5774 | 12.2816 | 11.6321 | 11.23 | 10.8889 | 13.2316 | 13.0221 | 12.7684 | 12.52 | 12.2042 | 11.7621 | 11.48 | 11.1895 | 10.8947 | 10.2453 | 9.8442 | 9.5042
LOVEDEAN GSP | FORT WIDLEY BSP | WATERLOOVILLE PRIMARY | MINIMUM HEADROOM | SU 67988 09282 | NO | YES | 0 | 60.6911 | 59.7995 | 58.8732 | 57.3911 | 55.6732 | 53.8679 | 52.0626 | 50.3142 | 48.6068 | 43.6868 | 40.4816 | 37.7142 | 51.5021 | 50.4926 | 49.4526 | 47.7716 | 45.8274 | 43.7895 | 41.7495 | 39.7758 | 37.8505 | 32.2389 | 28.5695 | 25.4053 | 56.4758 | 55.5137 | 54.5211 | 52.9232 | 51.0737 | 49.1316 | 47.1895 | 45.3084 | 43.4737 | 38.1495 | 34.6726 | 31.6716
|  | WATERLOOVILLE PRIMARY | EE |  |  |  |  | 60.6911 | 59.7995 | 58.9321 | 57.7521 | 56.4195 | 55.1795 | 53.9584 | 52.8321 | 51.7689 | 48.7995 | 46.4816 | 44.5868 | 51.5021 | 50.4926 | 49.5189 | 48.1958 | 46.7211 | 45.3526 | 43.9968 | 42.7589 | 41.5937 | 38.1116 | 35.4 | 33.1832 | 56.4758 | 55.5137 | 54.5853 | 53.3221 | 51.9053 | 50.5905 | 49.2895 | 48.0989 | 46.9758 | 43.7063 | 41.1579 | 39.0747
|  | WATERLOOVILLE PRIMARY | HT |  |  |  |  | 60.7974 | 59.9016 | 58.8732 | 57.3911 | 55.6732 | 53.8679 | 52.0626 | 50.3142 | 48.6068 | 43.6868 | 40.4816 | 37.7142 | 51.6274 | 50.6105 | 49.4526 | 47.7716 | 45.8274 | 43.7895 | 41.7495 | 39.7758 | 37.8505 | 32.2389 | 28.5695 | 25.4053 | 56.5926 | 55.6263 | 54.5211 | 52.9232 | 51.0737 | 49.1316 | 47.1895 | 45.3084 | 43.4737 | 38.1495 | 34.6726 | 31.6716
|  | WATERLOOVILLE PRIMARY | HE |  |  |  |  | 61.0005 | 60.3405 | 59.6068 | 58.5447 | 57.2921 | 56.1563 | 55.0637 | 54.0689 | 53.1311 | 51.1816 | 49.4974 | 48.1374 | 51.9568 | 51.1242 | 50.3074 | 49.1189 | 47.7379 | 46.4863 | 45.2842 | 44.2021 | 43.1863 | 40.8358 | 38.8295 | 37.2063 | 56.9032 | 56.1084 | 55.3263 | 54.1905 | 52.8632 | 51.6589 | 50.5032 | 49.4558 | 48.4726 | 46.2895 | 44.4158 | 42.9021
|  | WATERLOOVILLE PRIMARY | FB |  |  |  |  | 61.2195 | 61.0805 | 60.9542 | 60.5321 | 60.0553 | 59.5805 | 59.1026 | 58.6837 | 58.2647 | 56.6079 | 54.7753 | 53.5426 | 52.7758 | 52.2621 | 51.8558 | 51.3347 | 50.7937 | 50.2558 | 49.7116 | 49.2379 | 48.7653 | 46.8884 | 44.7516 | 43.3116 | 57.6853 | 57.1937 | 56.8063 | 56.3116 | 55.7968 | 55.2853 | 54.7684 | 54.3179 | 53.8674 | 52.0811 | 50.0716 | 48.7168
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON PRIMARY | MINIMUM HEADROOM | SU 69106 94287 | NO | YES | 0 | 9.1495 | 9.0274 | 8.7789 | 8.5063 | 29.1521 | 28.9447 | 28.7574 | 28.5668 | 28.3742 | 27.7837 | 27.4026 | 27.0026 | 7.0611 | 6.9316 | 6.6632 | 6.3705 | 25.3568 | 25.1421 | 24.9495 | 24.7526 | 24.5537 | 23.9305 | 23.5274 | 23.0989 | 6.9842 | 6.8421 | 6.5379 | 6.2095 | 26.0789 | 25.8505 | 25.6484 | 25.44 | 25.2295 | 24.5389 | 24.0895 | 23.6021
|  | WATLINGTON PRIMARY | EE |  |  |  |  | 9.1526 | 9.0274 | 8.8 | 8.5495 | 29.2163 | 29.0447 | 28.8774 | 28.7068 | 28.5395 | 28.23 | 27.9847 | 27.7647 | 7.0653 | 6.9326 | 6.6863 | 6.4168 | 25.4284 | 25.2516 | 25.0789 | 24.9032 | 24.7295 | 24.3937 | 24.1295 | 23.8905 | 6.9905 | 6.8453 | 6.5642 | 6.2621 | 26.1642 | 25.9789 | 25.7947 | 25.6063 | 25.4232 | 25.0379 | 24.7326 | 24.4547
|  | WATLINGTON PRIMARY | HT |  |  |  |  | 9.1495 | 9.0274 | 8.7789 | 8.5063 | 29.1521 | 28.9447 | 28.7574 | 28.5668 | 28.3742 | 27.7837 | 27.4026 | 27.0026 | 7.0611 | 6.9316 | 6.6632 | 6.3705 | 25.3568 | 25.1421 | 24.9495 | 24.7526 | 24.5537 | 23.9305 | 23.5274 | 23.0989 | 6.9842 | 6.8421 | 6.5379 | 6.2095 | 26.0789 | 25.8505 | 25.6484 | 25.44 | 25.2295 | 24.5389 | 24.0895 | 23.6021
|  | WATLINGTON PRIMARY | HE |  |  |  |  | 9.2411 | 9.1495 | 8.9484 | 8.7232 | 29.41 | 29.2595 | 29.1163 | 28.9689 | 28.8247 | 28.7289 | 28.6079 | 28.5037 | 7.1611 | 7.0653 | 6.8495 | 6.6074 | 25.6411 | 25.4874 | 25.3411 | 25.1905 | 25.0432 | 24.9337 | 24.8021 | 24.6874 | 7.1011 | 6.9989 | 6.7526 | 6.4811 | 26.4095 | 26.2495 | 26.0968 | 25.9411 | 25.7874 | 25.6558 | 25.5032 | 25.3684
|  | WATLINGTON PRIMARY | FB |  |  |  |  | 9.3116 | 9.2453 | 9.1484 | 9.0505 | 29.8405 | 29.7784 | 29.7195 | 29.6637 | 29.6026 | 29.3689 | 29.1868 | 29.0437 | 7.2358 | 7.1642 | 7.0589 | 6.9526 | 26.0895 | 26.0253 | 25.9621 | 25.9032 | 25.84 | 25.5916 | 25.3968 | 25.24 | 7.1811 | 7.1011 | 6.9811 | 6.86 | 26.8916 | 26.8211 | 26.7526 | 26.6874 | 26.6189 | 26.3463 | 26.1263 | 25.9474
AMERSHAM GSP | LOUDWATER BSP | WELL END PRIMARY | MINIMUM HEADROOM | SU 88511 87957 | NO | YES | 1.0516 | 28.7361 | 28.594 | 27.6571 | 27.0635 | 26.4024 | 25.7182 | 24.9571 | 24.255 | 23.5287 | 21.714 | 20.6635 | 19.734 | 25.5613 | 25.0108 | 23.2087 | 22.5571 | 21.835 | 21.1024 | 20.3013 | 19.5624 | 18.7982 | 16.8835 | 15.7782 | 14.7992 | 27.4392 | 27.2382 | 25.3256 | 24.6287 | 23.8592 | 23.0792 | 22.2235 | 21.4371 | 20.6213 | 18.5761 | 17.3971 | 16.354
|  | WELL END PRIMARY | EE |  |  |  |  | 28.7361 | 28.594 | 27.6571 | 27.0908 | 26.5035 | 25.9908 | 25.4561 | 25.0687 | 24.6908 | 23.7677 | 23.0687 | 22.4698 | 25.5613 | 25.0108 | 23.2087 | 22.5866 | 21.9529 | 21.4056 | 20.8413 | 20.4445 | 20.0561 | 19.0677 | 18.3192 | 17.6782 | 27.4392 | 27.2382 | 25.3256 | 24.6592 | 23.9877 | 23.4129 | 22.8182 | 22.4087 | 22.0087 | 20.934 | 20.1203 | 19.4235
|  | WELL END PRIMARY | HT |  |  |  |  | 28.7413 | 28.6045 | 27.6835 | 27.0635 | 26.4024 | 25.7182 | 24.9571 | 24.255 | 23.5287 | 21.714 | 20.6635 | 19.734 | 25.6182 | 25.0866 | 23.2392 | 22.5571 | 21.835 | 21.1024 | 20.3013 | 19.5624 | 18.7982 | 16.8835 | 15.7782 | 14.7992 | 27.4445 | 27.294 | 25.3592 | 24.6287 | 23.8592 | 23.0792 | 22.2235 | 21.4371 | 20.6213 | 18.5761 | 17.3971 | 16.354
|  | WELL END PRIMARY | HE |  |  |  |  | 28.7624 | 28.6235 | 27.9456 | 27.4245 | 26.8656 | 26.3919 | 25.9182 | 25.5877 | 25.2603 | 24.8087 | 24.3856 | 24.0192 | 25.6603 | 25.2729 | 23.5371 | 22.9677 | 22.3656 | 21.8613 | 21.3561 | 21.0161 | 20.6803 | 20.1792 | 19.7213 | 19.3245 | 27.4656 | 27.3266 | 25.6845 | 25.0782 | 24.4424 | 23.914 | 23.3835 | 23.0371 | 22.694 | 22.1382 | 21.634 | 21.1971
|  | WELL END PRIMARY | FB |  |  |  |  | 28.875 | 28.8087 | 28.7487 | 28.6824 | 28.6087 | 28.534 | 28.4613 | 28.394 | 28.3213 | 28.054 | 27.4898 | 27.0929 | 25.7824 | 25.7045 | 25.5098 | 25.2645 | 25.0287 | 24.8192 | 24.6024 | 24.4635 | 24.3287 | 23.7266 | 23.0971 | 22.6508 | 27.5782 | 27.5119 | 27.4519 | 27.3856 | 27.255 | 27.0887 | 26.8645 | 26.7182 | 26.5771 | 25.9382 | 25.2561 | 24.7729
WILLESDEN GSP |  | WESLEY AVENUE PRIMARY | MINIMUM HEADROOM | TQ 20927 83082 | NO | NO | 0 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905
|  | WESLEY AVENUE PRIMARY | EE |  |  |  |  | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905
|  | WESLEY AVENUE PRIMARY | HT |  |  |  |  | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905
|  | WESLEY AVENUE PRIMARY | HE |  |  |  |  | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905
|  | WESLEY AVENUE PRIMARY | FB |  |  |  |  | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 65.6284 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 64.6547 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905 | 63.4905
LOVEDEAN GSP | FAREHAM (MAIN) BSP | WEST END PRIMARY | MINIMUM HEADROOM | SU 57216 06147 | NO | YES | 0 | 33.0142 | 32.8458 | 32.6489 | 32.3805 | 32.0563 | 31.7016 | 31.0889 | 30.3921 | 29.7468 | 27.9089 | 26.4216 | 25.0826 | 30.6568 | 30.4884 | 30.2074 | 29.5095 | 28.6505 | 27.5568 | 26.6989 | 25.9032 | 25.1716 | 23.0884 | 21.4274 | 19.9316 | 27.3095 | 27.1242 | 26.9053 | 26.6021 | 26.2368 | 25.8221 | 25.4284 | 25.0432 | 24.6674 | 23.7442 | 22.6779 | 21.2221
|  | WEST END PRIMARY | EE |  |  |  |  | 33.0142 | 32.8458 | 32.6563 | 32.4026 | 32.0563 | 31.7226 | 31.4153 | 31.0984 | 30.7879 | 30.3279 | 29.3542 | 28.4932 | 30.6568 | 30.4884 | 30.2989 | 29.9021 | 29.4084 | 28.7495 | 28.0747 | 27.5221 | 27.0558 | 25.9495 | 24.7579 | 23.7158 | 27.3095 | 27.1242 | 26.9211 | 26.6537 | 26.2958 | 25.9368 | 25.6 | 25.2642 | 24.9411 | 24.6305 | 24.3421 | 24.1063
|  | WEST END PRIMARY | HT |  |  |  |  | 33.0184 | 32.8595 | 32.6489 | 32.3805 | 32.0574 | 31.7016 | 31.0889 | 30.3921 | 29.7468 | 27.9089 | 26.4216 | 25.0826 | 30.6611 | 30.5021 | 30.2074 | 29.5095 | 28.6505 | 27.5568 | 26.6989 | 25.9032 | 25.1716 | 23.0884 | 21.4274 | 19.9316 | 27.3168 | 27.1389 | 26.9053 | 26.6021 | 26.2368 | 25.8221 | 25.4284 | 25.0432 | 24.6674 | 23.7442 | 22.6779 | 21.2221
|  | WEST END PRIMARY | HE |  |  |  |  | 33.0468 | 32.8858 | 32.7058 | 32.4574 | 32.1132 | 31.7942 | 31.4837 | 31.1689 | 30.8584 | 30.8858 | 30.8353 | 30.8026 | 30.6895 | 30.5284 | 30.3484 | 30.1 | 29.7558 | 29.3484 | 28.7558 | 28.2979 | 27.9189 | 27.6421 | 27.1316 | 26.6347 | 27.3589 | 27.1874 | 27.0011 | 26.7442 | 26.3916 | 26.0495 | 25.7168 | 25.3905 | 25.0747 | 25.0779 | 24.9905 | 24.9211
|  | WEST END PRIMARY | FB |  |  |  |  | 33.1689 | 33.0879 | 33.0142 | 32.9321 | 32.8405 | 32.7489 | 32.6595 | 32.5763 | 32.4868 | 32.1605 | 31.9784 | 31.8626 | 30.8116 | 30.7305 | 30.6568 | 30.5747 | 30.4832 | 30.3916 | 30.2916 | 30.0789 | 29.9137 | 29.2326 | 28.6179 | 28.0368 | 27.4895 | 27.3979 | 27.3168 | 27.2274 | 27.1295 | 27.0242 | 26.9211 | 26.8284 | 26.7326 | 26.3779 | 26.1611 | 26.0084
MELKSHAM GSP | WEST GRAFTON BSP | WEST GRAFTON VILLAGE PRIMARY | MINIMUM HEADROOM | SU 24639 60279 | NO | YES | 0.15684 | 10.7537 | 10.6211 | 10.5105 | 10.36 | 10.1611 | 9.9368 | 9.7021 | 9.4484 | 9.1789 | 8.4453 | 7.8453 | 7.3053 | 9.7526 | 9.6 | 9.4779 | 9.3116 | 9.0905 | 8.8389 | 8.5758 | 8.2853 | 7.9758 | 7.1579 | 6.4811 | 5.8705 | 9.0179 | 8.8663 | 8.7442 | 8.5779 | 8.3568 | 8.1063 | 7.8432 | 7.5526 | 7.2442 | 6.4284 | 5.7526 | 5.1442
|  | WEST GRAFTON VILLAGE PRIMARY | EE |  |  |  |  | 10.7537 | 10.6211 | 10.5105 | 10.3821 | 10.2242 | 10.0758 | 9.9379 | 9.7958 | 9.6568 | 9.3389 | 8.9316 | 8.5632 | 9.7526 | 9.6 | 9.4779 | 9.3379 | 9.1705 | 9.0126 | 8.8653 | 8.7137 | 8.5642 | 8.1821 | 7.6989 | 7.2737 | 9.0179 | 8.8663 | 8.7442 | 8.6042 | 8.4368 | 8.2789 | 8.1316 | 7.98 | 7.8316 | 7.4495 | 6.9684 | 6.5442
|  | WEST GRAFTON VILLAGE PRIMARY | HT |  |  |  |  | 10.7758 | 10.6516 | 10.5274 | 10.36 | 10.1611 | 9.9368 | 9.7021 | 9.4484 | 9.1789 | 8.4453 | 7.8453 | 7.3053 | 9.7789 | 9.6368 | 9.5 | 9.3116 | 9.0905 | 8.8389 | 8.5758 | 8.2853 | 7.9758 | 7.1579 | 6.4811 | 5.8705 | 9.0453 | 8.9032 | 8.7663 | 8.5779 | 8.3568 | 8.1063 | 7.8432 | 7.5526 | 7.2442 | 6.4284 | 5.7526 | 5.1442
|  | WEST GRAFTON VILLAGE PRIMARY | HE |  |  |  |  | 10.8316 | 10.7284 | 10.6432 | 10.5347 | 10.3937 | 10.2653 | 10.1432 | 10.02 | 9.9011 | 9.74 | 9.4442 | 9.18 | 9.8453 | 9.7295 | 9.6368 | 9.5211 | 9.3737 | 9.2389 | 9.1116 | 8.9842 | 8.8589 | 8.6537 | 8.2863 | 7.9611 | 9.1105 | 8.9958 | 8.9021 | 8.7874 | 8.64 | 8.5053 | 8.3779 | 8.2505 | 8.1253 | 7.9211 | 7.5537 | 7.2305
|  | WEST GRAFTON VILLAGE PRIMARY | FB |  |  |  |  | 10.9063 | 10.8421 | 10.7979 | 10.7495 | 10.6968 | 10.6463 | 10.5968 | 10.5516 | 10.5042 | 10.2705 | 10.0158 | 9.7979 | 9.9295 | 9.8547 | 9.8053 | 9.7505 | 9.6916 | 9.6347 | 9.58 | 9.5295 | 9.4758 | 9.2084 | 8.9 | 8.6337 | 9.1958 | 9.12 | 9.0705 | 9.0158 | 8.9579 | 8.9011 | 8.8463 | 8.7958 | 8.7421 | 8.4747 | 8.1674 | 7.9011
AXMINSTER GSP | YEOVIL BSP | WEST HENDFORD PRIMARY | MINIMUM HEADROOM | ST 55000 15442 | NO | YES | 0 | 62.7168 | 62.6126 | 62.4947 | 62.3274 | 62.1253 | 61.9179 | 61.7053 | 61.3358 | 60.7684 | 59.6358 | 58.7979 | 57.9253 | 56.0505 | 55.7274 | 55.4053 | 54.8832 | 54.1968 | 53.3937 | 52.7011 | 51.8937 | 51.1705 | 49.9137 | 48.9768 | 47.9926 | 60.2189 | 60.1147 | 59.9968 | 59.8295 | 59.6263 | 58.9274 | 58.2495 | 57.4621 | 56.7547 | 55.5168 | 54.5989 | 53.6263
|  | WEST HENDFORD PRIMARY | EE |  |  |  |  | 62.7168 | 62.6126 | 62.4947 | 62.3379 | 62.1253 | 61.9242 | 61.7432 | 61.3358 | 60.7747 | 60.0558 | 59.4326 | 58.7916 | 56.0505 | 55.7274 | 55.4053 | 54.8832 | 54.1968 | 53.5168 | 52.7937 | 51.8937 | 51.1705 | 50.3326 | 49.6211 | 48.8821 | 60.2189 | 60.1147 | 59.9968 | 59.84 | 59.6263 | 59.0474 | 58.3411 | 57.4621 | 56.7547 | 55.9368 | 55.2411 | 54.5147
|  | WEST HENDFORD PRIMARY | HT |  |  |  |  | 62.7232 | 62.6242 | 62.4947 | 62.3274 | 62.1337 | 61.9179 | 61.7053 | 61.3663 | 60.7684 | 59.6358 | 58.7979 | 57.9253 | 56.0937 | 55.7884 | 55.4642 | 54.9379 | 54.2568 | 53.3937 | 52.7011 | 51.9611 | 51.1958 | 49.9137 | 48.9768 | 47.9926 | 60.2253 | 60.1263 | 59.9968 | 59.8295 | 59.6358 | 58.9274 | 58.2495 | 57.5253 | 56.7758 | 55.5168 | 54.5989 | 53.6263
|  | WEST HENDFORD PRIMARY | HE |  |  |  |  | 62.74 | 62.6379 | 62.5263 | 62.3684 | 62.1537 | 61.96 | 61.7737 | 61.5842 | 61.2011 | 61.0137 | 60.7158 | 60.3116 | 56.1905 | 55.9189 | 55.6484 | 55.1589 | 54.4947 | 53.8484 | 53.2074 | 52.4832 | 51.7674 | 51.4916 | 51.0884 | 50.6158 | 60.2421 | 60.14 | 60.0284 | 59.8705 | 59.6558 | 59.3705 | 58.7442 | 58.0347 | 57.3337 | 57.0674 | 56.6747 | 56.2147
|  | WEST HENDFORD PRIMARY | FB |  |  |  |  | 62.82 | 62.7758 | 62.7347 | 62.6884 | 62.6379 | 62.5874 | 62.5368 | 62.4905 | 62.4421 | 62.2589 | 62.1579 | 62.0937 | 56.3632 | 56.1958 | 56.0642 | 55.8547 | 55.5989 | 55.3263 | 55.0316 | 54.7253 | 54.3505 | 53.8242 | 53.3653 | 52.8758 | 60.3221 | 60.2779 | 60.2368 | 60.1905 | 60.14 | 60.0895 | 60.0389 | 59.9926 | 59.8726 | 59.3568 | 58.9084 | 58.4305
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR PRIMARY | MINIMUM HEADROOM | ST 77699 22040 | NO | YES | 0.17895 | 6.8547 | 6.7274 | 6.5779 | 6.3642 | 6.1137 | 5.8432 | 5.5758 | 5.3 | 3.3695 | 2.6716 | 2.2116 | 1.8 | 6.9916 | 6.8537 | 6.6884 | 6.4537 | 6.18 | 5.8832 | 5.5895 | 5.2874 | 3.0368 | 2.2653 | 1.7537 | 1.2947 | 7.0684 | 6.9347 | 6.7779 | 6.5537 | 6.2853 | 5.9937 | 5.7053 | 5.4084 | 3.2168 | 2.4589 | 1.9558 | 1.5042
|  | WEST STOUR PRIMARY | EE |  |  |  |  | 6.8547 | 6.7274 | 6.5937 | 6.4389 | 6.2537 | 6.0737 | 5.8958 | 5.72 | 4.72 | 4.3558 | 4.0411 | 3.7758 | 6.9916 | 6.8537 | 6.7074 | 6.5421 | 6.3453 | 6.1537 | 5.9632 | 5.7758 | 4.6168 | 4.1989 | 3.8411 | 3.5379 | 7.0684 | 6.9347 | 6.7958 | 6.6347 | 6.4442 | 6.2547 | 6.0674 | 5.8821 | 4.7537 | 4.3463 | 3.9947 | 3.6989
|  | WEST STOUR PRIMARY | HT |  |  |  |  | 6.8716 | 6.7432 | 6.5779 | 6.3642 | 6.1137 | 5.8432 | 5.5758 | 5.3 | 3.3695 | 2.6716 | 2.2116 | 1.8 | 7.0116 | 6.8695 | 6.6884 | 6.4537 | 6.18 | 5.8832 | 5.5895 | 5.2874 | 3.0368 | 2.2653 | 1.7537 | 1.2947 | 7.0863 | 6.9516 | 6.7779 | 6.5537 | 6.2853 | 5.9937 | 5.7053 | 5.4084 | 3.2168 | 2.4589 | 1.9558 | 1.5042
|  | WEST STOUR PRIMARY | HE |  |  |  |  | 6.9326 | 6.8389 | 6.7316 | 6.6021 | 6.4337 | 6.2768 | 6.1242 | 5.9737 | 4.9958 | 4.8116 | 4.6105 | 4.4379 | 7.0811 | 6.98 | 6.8642 | 6.7263 | 6.5484 | 6.3832 | 6.2221 | 6.0621 | 4.9305 | 4.7105 | 4.4768 | 4.2758 | 7.1526 | 7.0547 | 6.9432 | 6.8095 | 6.6368 | 6.4758 | 6.3179 | 6.1632 | 5.0611 | 4.8474 | 4.62 | 4.4242
|  | WEST STOUR PRIMARY | FB |  |  |  |  | 7.0063 | 6.9411 | 6.8874 | 6.8316 | 6.7695 | 6.7084 | 6.6484 | 6.5874 | 6.5253 | 6.2653 | 6.0484 | 5.8684 | 7.16 | 7.0874 | 7.0284 | 6.9663 | 6.8989 | 6.8316 | 6.7653 | 6.6989 | 6.6305 | 6.3421 | 6.0968 | 5.8905 | 7.2284 | 7.1589 | 7.1032 | 7.0442 | 6.98 | 6.9158 | 6.8526 | 6.7884 | 6.7232 | 6.4453 | 6.2063 | 6.0042
MANNINGTON GSP | BOURNEMOUTH BSP | WESTBOURNE PRIMARY | MINIMUM HEADROOM | SZ 07642 91485 | NO | YES | 0.015789 | 34.0247 | 33.8847 | 33.7174 | 33.4837 | 33.1574 | 32.8637 | 32.5774 | 32.0058 | 31.0132 | 28.9511 | 27.5247 | 26.2111 | 30.0221 | 29.8789 | 29.7147 | 29.4779 | 29.1484 | 28.8516 | 28.2105 | 27.3389 | 26.2211 | 23.9232 | 22.3284 | 20.8589 | 30.5537 | 30.2621 | 29.8842 | 29.3632 | 28.7653 | 27.9179 | 27.0979 | 26.1947 | 25.0768 | 22.7779 | 21.1842 | 19.7147
|  | WESTBOURNE PRIMARY | EE |  |  |  |  | 34.0247 | 33.8889 | 33.7395 | 33.5332 | 33.2437 | 32.9668 | 32.7068 | 32.4342 | 32.1616 | 31.7626 | 30.7047 | 29.7742 | 30.0221 | 29.8789 | 29.7242 | 29.5105 | 29.2179 | 28.9347 | 28.6684 | 28.3884 | 28.0989 | 27.1337 | 25.9305 | 24.8674 | 30.5537 | 30.2695 | 29.98 | 29.6421 | 29.2453 | 28.8474 | 28.4274 | 27.9863 | 27.3432 | 25.9895 | 24.7863 | 23.7242
|  | WESTBOURNE PRIMARY | HT |  |  |  |  | 34.0332 | 33.9068 | 33.7374 | 33.5174 | 33.25 | 32.9532 | 32.65 | 32.0058 | 31.0132 | 28.9511 | 27.5247 | 26.2111 | 30.0316 | 29.8958 | 29.7179 | 29.4842 | 29.2011 | 28.88 | 28.2105 | 27.3389 | 26.2211 | 23.9232 | 22.3284 | 20.8589 | 30.5958 | 30.2621 | 29.8842 | 29.3632 | 28.7653 | 27.9179 | 27.0979 | 26.1947 | 25.0768 | 22.7779 | 21.1842 | 19.7147
|  | WESTBOURNE PRIMARY | HE |  |  |  |  | 34.0353 | 33.8847 | 33.7174 | 33.4837 | 33.1574 | 32.8637 | 32.5774 | 32.2847 | 31.9984 | 31.9911 | 31.8984 | 31.5753 | 30.04 | 29.8863 | 29.7147 | 29.4779 | 29.1484 | 28.8516 | 28.5621 | 28.2663 | 27.9674 | 27.9316 | 27.5621 | 26.9232 | 30.7326 | 30.5053 | 30.2589 | 29.9495 | 29.5516 | 29.1768 | 28.8263 | 28.4589 | 27.8958 | 27.2358 | 26.4621 | 25.78
|  | WESTBOURNE PRIMARY | FB |  |  |  |  | 34.1311 | 34.0437 | 33.9658 | 33.8784 | 33.7805 | 33.6826 | 33.5868 | 33.4984 | 33.4026 | 33.0542 | 32.8553 | 32.7247 | 30.1389 | 30.0463 | 29.9653 | 29.8747 | 29.7737 | 29.6726 | 29.5747 | 29.4832 | 29.3779 | 29.0063 | 28.78 | 28.1568 | 30.9011 | 30.7084 | 30.56 | 30.4011 | 30.2316 | 30.0632 | 29.8968 | 29.74 | 29.4495 | 28.5621 | 27.76 | 27.0316
MELKSHAM GSP | FROME BSP | WESTBURY PRIMARY | MINIMUM HEADROOM | ST 87654 51530 | NO | YES | 0 | 30.9026 | 30.3995 | 29.7521 | 28.9384 | 27.7005 | 26.7879 | 26.0163 | 24.9058 | 23.8068 | 25.0363 | 23.01 | 21.2005 | 26.9674 | 26.4137 | 25.6958 | 24.7979 | 23.4137 | 22.4095 | 21.5642 | 20.3968 | 19.1779 | 22.3189 | 20.0379 | 17.9979 | 26.9811 | 26.6474 | 26.2442 | 25.7095 | 24.6463 | 23.6442 | 22.7779 | 21.5442 | 20.3274 | 24.1758 | 21.8989 | 19.8642
|  | WESTBURY PRIMARY | EE |  |  |  |  | 30.9026 | 30.3995 | 29.7521 | 28.99 | 27.7005 | 26.7879 | 26.0163 | 25.3721 | 24.7658 | 25.57 | 24.1247 | 22.87 | 26.9674 | 26.4137 | 25.6958 | 24.8547 | 23.4137 | 22.4095 | 21.5642 | 20.8747 | 20.2263 | 22.7926 | 21.1368 | 19.6958 | 26.9811 | 26.6474 | 26.2442 | 25.7474 | 24.6463 | 23.6442 | 22.8 | 22.1105 | 21.4642 | 24.6495 | 22.9979 | 21.5611
|  | WESTBURY PRIMARY | HT |  |  |  |  | 30.9879 | 30.5195 | 29.8268 | 28.9384 | 28.4774 | 27.1984 | 26.0195 | 24.9058 | 23.8068 | 25.0363 | 23.01 | 21.2005 | 27.0642 | 26.5505 | 25.7842 | 24.7979 | 24.3737 | 22.9453 | 21.6326 | 20.3968 | 19.1779 | 22.3189 | 20.0379 | 17.9979 | 27.0263 | 26.7147 | 26.2737 | 25.7095 | 25.5126 | 24.0874 | 22.7779 | 21.5442 | 20.3274 | 24.1758 | 21.8989 | 19.8642
|  | WESTBURY PRIMARY | HE |  |  |  |  | 31.19 | 30.7921 | 30.2342 | 29.5479 | 28.3089 | 27.4584 | 26.7584 | 26.1921 | 25.6626 | 27.1574 | 26.1226 | 25.2226 | 27.2916 | 26.8589 | 26.2432 | 25.4916 | 24.1095 | 23.1747 | 22.4168 | 21.8158 | 21.2579 | 24.5832 | 23.3789 | 22.3284 | 27.14 | 26.86 | 26.5011 | 26.0411 | 25.2768 | 24.4084 | 23.6505 | 23.0505 | 22.4926 | 26.4368 | 25.2358 | 24.1884
|  | WESTBURY PRIMARY | FB |  |  |  |  | 31.3542 | 31.1784 | 30.9047 | 30.6026 | 30.1563 | 29.5795 | 29.3311 | 29.1553 | 28.9742 | 28.1237 | 27.8511 | 27.0353 | 27.5663 | 27.2705 | 26.9642 | 26.6263 | 26.1232 | 25.4642 | 25.1905 | 25.0011 | 24.8053 | 23.8705 | 23.6326 | 22.6958 | 27.3284 | 27.1632 | 27 | 26.8179 | 26.5716 | 26.2695 | 26.1063 | 25.9779 | 25.8421 | 25.1032 | 24.7737 | 23.8389
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WESTERN ESPLANADE PRIMARY | MINIMUM HEADROOM | SU 41618 12009 | NO | YES | 0.094737 | 64.1505 | 63.7726 | 63.3684 | 62.9274 | 60.9579 | 58.1642 | 55.3484 | 52.3295 | 49.7358 | 45.1021 | 43.8684 | 42.7684 | 51.6611 | 51.3063 | 50.9263 | 50.5063 | 48.3042 | 45.0653 | 41.8021 | 38.3 | 35.2958 | 29.9863 | 28.6042 | 27.3737 | 62.6442 | 62.5337 | 62.4063 | 61.6021 | 58.8937 | 55.6537 | 52.3905 | 48.8874 | 45.8821 | 40.5884 | 39.2053 | 37.9747
|  | WESTERN ESPLANADE PRIMARY | EE |  |  |  |  | 64.1674 | 63.8053 | 63.4632 | 63.1 | 62.6347 | 61.2653 | 59.1789 | 56.3168 | 54.3842 | 47.2084 | 46.2695 | 45.4589 | 51.6747 | 51.3347 | 51.0116 | 50.6663 | 50.2221 | 48.7063 | 46.2916 | 42.9684 | 40.7368 | 32.3716 | 31.3105 | 30.3874 | 62.6442 | 62.5337 | 62.4147 | 62.0853 | 61.18 | 59.2968 | 56.8811 | 53.5579 | 51.3242 | 42.9695 | 41.9126 | 40.9874
|  | WESTERN ESPLANADE PRIMARY | HT |  |  |  |  | 64.1505 | 63.7726 | 63.3684 | 62.9274 | 60.9579 | 58.1642 | 55.3484 | 52.3295 | 49.7358 | 45.1021 | 43.8684 | 42.7684 | 51.6611 | 51.3063 | 50.9263 | 50.5063 | 48.3042 | 45.0653 | 41.8021 | 38.3 | 35.2958 | 29.9863 | 28.6042 | 27.3737 | 62.6495 | 62.5484 | 62.4137 | 61.6021 | 58.8937 | 55.6537 | 52.3905 | 48.8874 | 45.8821 | 40.5884 | 39.2053 | 37.9747
|  | WESTERN ESPLANADE PRIMARY | HE |  |  |  |  | 64.2221 | 63.8716 | 63.5358 | 63.1726 | 62.6947 | 61.4642 | 59.4063 | 56.9063 | 54.9989 | 48.7789 | 47.8295 | 47.3421 | 51.7263 | 51.3968 | 51.0779 | 50.7305 | 50.2716 | 48.9495 | 46.5726 | 43.6768 | 41.4758 | 34.1726 | 33.0695 | 32.5063 | 62.6537 | 62.5358 | 62.4063 | 62.2263 | 61.4432 | 59.5411 | 57.1621 | 54.2663 | 52.0642 | 44.7589 | 43.6547 | 43.0916
|  | WESTERN ESPLANADE PRIMARY | FB |  |  |  |  | 64.4421 | 64.2484 | 64.0884 | 63.9358 | 63.7621 | 63.5779 | 63.2358 | 62.8547 | 62.3347 | 56.8337 | 55.5832 | 55.0211 | 51.9337 | 51.7505 | 51.6 | 51.4547 | 51.2895 | 51.1147 | 50.7958 | 50.4421 | 49.8968 | 43.4853 | 42.0442 | 41.4021 | 62.7305 | 62.6632 | 62.6021 | 62.5347 | 62.4589 | 62.3821 | 62.3084 | 61.3905 | 60.4874 | 54.0747 | 52.6326 | 51.9905
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON PRIMARY | MINIMUM HEADROOM | SU 45207 09912 | NO | YES | 0.084211 | 23.3295 | 23.1442 | 22.0158 | 22.2379 | 21.4632 | 20.8874 | 20.2379 | 19.4558 | 18.5747 | 16.1789 | 12.8789 | 11.4568 | 21.4084 | 21.0232 | 19.6547 | 19.7926 | 18.9432 | 18.3347 | 17.64 | 16.7884 | 15.8189 | 13.1547 | 9.3663 | 7.7768 | 19.1221 | 18.74 | 17.3905 | 17.5989 | 16.7579 | 16.1537 | 15.4632 | 14.6189 | 13.66 | 11.0253 | 7.2905 | 5.72
|  | WESTON PRIMARY | EE |  |  |  |  | 23.3295 | 23.1442 | 22.0495 | 22.4568 | 21.9147 | 21.3621 | 20.8011 | 20.2926 | 19.7811 | 18.6189 | 16.6568 | 15.7116 | 21.4084 | 21.0232 | 19.6947 | 20.0495 | 19.48 | 18.8947 | 18.2968 | 17.7642 | 17.2253 | 15.9032 | 13.6347 | 12.5526 | 19.1221 | 18.74 | 17.4305 | 17.8516 | 17.2853 | 16.7042 | 16.1095 | 15.5789 | 15.0432 | 13.7389 | 11.5042 | 10.4379
|  | WESTON PRIMARY | HT |  |  |  |  | 23.3389 | 23.1632 | 22.0158 | 22.2379 | 21.4632 | 20.8874 | 20.2379 | 19.4558 | 18.5747 | 16.1789 | 12.8789 | 11.4568 | 21.4695 | 21.0884 | 19.6547 | 19.7926 | 18.9432 | 18.3347 | 17.64 | 16.7884 | 15.8189 | 13.1547 | 9.3663 | 7.7768 | 19.1821 | 18.8042 | 17.3905 | 17.5989 | 16.7579 | 16.1537 | 15.4632 | 14.6189 | 13.66 | 11.0253 | 7.2905 | 5.72
|  | WESTON PRIMARY | HE |  |  |  |  | 23.3579 | 23.1705 | 22.4211 | 22.8832 | 22.3737 | 21.8642 | 21.3547 | 20.9 | 20.4442 | 19.9147 | 18.3821 | 17.7516 | 21.52 | 21.3284 | 20.1284 | 20.5474 | 20.0179 | 19.4842 | 18.9484 | 18.48 | 18.0074 | 17.38 | 15.5853 | 14.8505 | 19.3758 | 19.0863 | 17.8568 | 18.3421 | 17.8147 | 17.2832 | 16.7505 | 16.2832 | 15.8126 | 15.1968 | 13.4305 | 12.7074
|  | WESTON PRIMARY | FB |  |  |  |  | 23.5011 | 23.4084 | 22.9084 | 23.5863 | 23.3937 | 23.1947 | 22.9916 | 22.7958 | 22.6095 | 21.7768 | 21.0579 | 20.4042 | 21.6695 | 21.5705 | 20.6358 | 21.2747 | 21.0663 | 20.8505 | 20.6295 | 20.4147 | 20.2137 | 19.2989 | 18.4895 | 17.7432 | 19.66 | 19.4347 | 18.3621 | 19.0663 | 18.8589 | 18.6463 | 18.4263 | 18.2147 | 18.0147 | 17.1095 | 16.3095 | 15.5737
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH PRIMARY | MINIMUM HEADROOM | SY 67443 79096 | NO | YES | 0 | 35.8432 | 35.1253 | 34.1074 | 32.7042 | 31.0042 | 29.1463 | 27.2926 | 25.3947 | 23.4968 | 18.7579 | 15.5758 | 12.6768 | 34.2158 | 33.4063 | 32.2295 | 30.6116 | 28.6516 | 26.5095 | 24.3737 | 22.1811 | 19.9884 | 14.4779 | 10.7632 | 7.3747 | 33.2495 | 32.4958 | 31.4137 | 29.9221 | 28.1168 | 26.1432 | 24.1747 | 22.1568 | 20.1389 | 15.0884 | 11.3737 | 7.9053
|  | WEYMOUTH PRIMARY | EE |  |  |  |  | 35.8432 | 35.1253 | 34.3453 | 33.4179 | 32.2653 | 31.1874 | 30.1021 | 29.0053 | 27.9337 | 25.3453 | 23.0463 | 21.0316 | 34.2158 | 33.4063 | 32.5232 | 31.4905 | 30.2295 | 29.0442 | 27.8411 | 26.6253 | 25.44 | 22.3411 | 19.5979 | 17.1832 | 33.2495 | 32.4958 | 31.6737 | 30.7032 | 29.5063 | 28.3842 | 27.2505 | 26.1063 | 24.9884 | 22.1916 | 19.7116 | 17.5337
|  | WEYMOUTH PRIMARY | HT |  |  |  |  | 35.9274 | 35.1589 | 34.1074 | 32.7042 | 31.0042 | 29.1463 | 27.2926 | 25.3947 | 23.4968 | 18.7579 | 15.5758 | 12.6768 | 34.3147 | 33.4347 | 32.2295 | 30.6116 | 28.6516 | 26.5095 | 24.3737 | 22.1811 | 19.9884 | 14.4779 | 10.7632 | 7.3747 | 33.3411 | 32.5263 | 31.4137 | 29.9221 | 28.1168 | 26.1432 | 24.1747 | 22.1568 | 20.1389 | 15.0884 | 11.3737 | 7.9053
|  | WEYMOUTH PRIMARY | HE |  |  |  |  | 36.2263 | 35.6495 | 34.9958 | 34.1642 | 33.0674 | 32.0832 | 31.1168 | 30.1453 | 29.2011 | 27.7832 | 26.2105 | 24.8158 | 34.5842 | 34.0379 | 33.3105 | 32.3968 | 31.2063 | 30.1337 | 29.08 | 28.0232 | 26.9979 | 25.2168 | 23.2926 | 21.5811 | 33.6653 | 33.0642 | 32.38 | 31.5147 | 30.38 | 29.36 | 28.3589 | 27.3526 | 26.3747 | 24.8095 | 23.0937 | 21.5705
|  | WEYMOUTH PRIMARY | FB |  |  |  |  | 36.6284 | 36.2358 | 35.9021 | 35.54 | 35.14 | 34.7379 | 34.3316 | 33.9347 | 33.5221 | 31.7611 | 30.26 | 28.9558 | 34.9347 | 34.6137 | 34.2905 | 33.88 | 33.4284 | 32.9737 | 32.5116 | 32.0589 | 31.5895 | 29.5589 | 27.7832 | 26.2179 | 34.0832 | 33.6674 | 33.3168 | 32.9347 | 32.5137 | 32.0905 | 31.6611 | 31.2421 | 30.8063 | 28.9347 | 27.3232 | 25.9126
COWLEY GSP | HEADINGTON BSP | WHEATLEY PRIMARY | MINIMUM HEADROOM | SP 60777 05379 | NO | YES | 0.37579 | 36.0189 | 35.4579 | 34.6558 | 33.7032 | 32.7084 | 31.3979 | 30.2853 | 29.1484 | 28.1958 | 28.5389 | 28.8642 | 28.2495 | 34.4737 | 33.8263 | 32.9 | 31.8011 | 30.6579 | 29.1442 | 27.8642 | 26.5558 | 25.4632 | 25.8747 | 27.0905 | 26.4053 | 34.7895 | 34.1421 | 33.2147 | 32.1158 | 30.9726 | 29.4589 | 28.1779 | 26.8695 | 25.7768 | 26.1874 | 27.8126 | 27.1274
|  | WHEATLEY PRIMARY | EE |  |  |  |  | 36.0979 | 35.5695 | 34.8358 | 33.9642 | 33.0821 | 31.9189 | 30.9032 | 29.8684 | 29.0126 | 28.5389 | 32.3389 | 31.9947 | 34.5684 | 33.9611 | 33.1116 | 32.1063 | 31.0979 | 29.7568 | 28.5842 | 27.3926 | 26.4105 | 25.8747 | 31.8116 | 31.42 | 34.8832 | 34.2758 | 33.4263 | 32.4211 | 31.4116 | 30.0695 | 28.8968 | 27.7063 | 26.7242 | 26.1874 | 32.9463 | 32.5547
|  | WHEATLEY PRIMARY | HT |  |  |  |  | 36.0189 | 35.4579 | 34.6558 | 33.7032 | 32.7084 | 31.3979 | 30.2853 | 29.1484 | 28.1958 | 29.4211 | 28.8642 | 28.2495 | 34.4737 | 33.8263 | 32.9 | 31.8011 | 30.6579 | 29.1442 | 27.8642 | 26.5558 | 25.4632 | 27.7021 | 27.0905 | 26.4053 | 34.7895 | 34.1421 | 33.2147 | 32.1158 | 30.9726 | 29.4589 | 28.1779 | 26.8695 | 25.7768 | 28.4253 | 27.8126 | 27.1274
|  | WHEATLEY PRIMARY | HE |  |  |  |  | 36.2253 | 35.7442 | 35.0537 | 34.2158 | 33.3611 | 32.2347 | 31.2537 | 30.2632 | 29.4484 | 29.2811 | 33.2526 | 33.0863 | 34.7116 | 34.1589 | 33.36 | 32.3937 | 31.4168 | 30.1147 | 28.9853 | 27.8453 | 26.9105 | 26.7126 | 32.8389 | 32.6453 | 35.0274 | 34.4747 | 33.6758 | 32.7084 | 31.7305 | 30.4295 | 29.2989 | 28.1579 | 27.2242 | 27.0253 | 33.9737 | 33.7811
|  | WHEATLEY PRIMARY | FB |  |  |  |  | 36.34 | 36.08 | 35.7653 | 35.4095 | 35.0716 | 34.5758 | 34.1095 | 33.6042 | 33.1589 | 32.82 | 32.5432 | 32.3221 | 34.7958 | 34.5379 | 34.1726 | 33.7611 | 33.3695 | 32.7937 | 32.2505 | 31.6621 | 31.1453 | 30.7737 | 30.4621 | 30.2126 | 35.1526 | 34.8537 | 34.4874 | 34.0758 | 33.6842 | 33.1084 | 32.5653 | 31.9768 | 31.46 | 31.0884 | 30.7768 | 30.5263
MELKSHAM GSP | ANDOVER BSP | WHITCHURCH PRIMARY | MINIMUM HEADROOM | SU 45924 48466 | NO | YES | 0 | 8.02 | 7.9642 | 7.9053 | 7.8211 | 7.7137 | 7.6095 | 7.4979 | 7.32 | 7.1453 | 6.7021 | 6.3705 | 6.0042 | 6.1758 | 6.0621 | 5.9505 | 5.7916 | 5.6021 | 5.3526 | 5.1547 | 4.9547 | 4.7653 | 4.2811 | 3.9126 | 3.4979 | 6.2705 | 6.1789 | 6.0874 | 5.9579 | 5.8021 | 5.6063 | 5.4421 | 5.2768 | 5.1189 | 4.7263 | 4.4389 | 4.1337
|  | WHITCHURCH PRIMARY | EE |  |  |  |  | 8.02 | 7.9642 | 7.9053 | 7.8263 | 7.7137 | 7.6105 | 7.5179 | 7.4179 | 7.3221 | 7.0232 | 6.8179 | 6.5684 | 6.1758 | 6.0621 | 5.9505 | 5.8242 | 5.6737 | 5.5316 | 5.3505 | 5.1589 | 4.9842 | 4.6253 | 4.3895 | 4.1 | 6.2705 | 6.1789 | 6.0874 | 5.98 | 5.8432 | 5.7168 | 5.5695 | 5.4137 | 5.2674 | 5.02 | 4.8495 | 4.6505
|  | WHITCHURCH PRIMARY | HT |  |  |  |  | 8.0242 | 7.9726 | 7.9063 | 7.8211 | 7.7211 | 7.6095 | 7.4979 | 7.32 | 7.1453 | 6.7021 | 6.3705 | 6.0042 | 6.2011 | 6.0989 | 5.9663 | 5.7916 | 5.6021 | 5.3526 | 5.1547 | 4.9547 | 4.7653 | 4.2811 | 3.9126 | 3.4979 | 6.2874 | 6.2042 | 6.0979 | 5.9579 | 5.8021 | 5.6063 | 5.4421 | 5.2768 | 5.1189 | 4.7263 | 4.4389 | 4.1337
|  | WHITCHURCH PRIMARY | HE |  |  |  |  | 8.0337 | 7.9821 | 7.9263 | 7.8474 | 7.7358 | 7.6379 | 7.5442 | 7.4453 | 7.3516 | 7.3579 | 7.3284 | 7.2379 | 6.2558 | 6.1726 | 6.0884 | 5.9821 | 5.8432 | 5.7211 | 5.5632 | 5.4011 | 5.2537 | 5.0905 | 4.9747 | 4.8695 | 6.3242 | 6.2537 | 6.18 | 6.0842 | 5.9568 | 5.8432 | 5.7105 | 5.5726 | 5.4463 | 5.3474 | 5.2684 | 5.1979
|  | WHITCHURCH PRIMARY | FB |  |  |  |  | 8.0726 | 8.0484 | 8.0263 | 8.0011 | 7.9737 | 7.9453 | 7.9189 | 7.8937 | 7.8674 | 7.7695 | 7.7147 | 7.6284 | 6.3242 | 6.2611 | 6.2137 | 6.1632 | 6.1105 | 6.0558 | 6.0053 | 5.94 | 5.8768 | 5.5884 | 5.4116 | 5.2674 | 6.3811 | 6.3337 | 6.2958 | 6.2547 | 6.2126 | 6.1674 | 6.1263 | 6.0768 | 6.0274 | 5.8126 | 5.6821 | 5.58
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY PRIMARY | MINIMUM HEADROOM | SU 52936 08794 | NO | YES | 1.0516 | 31.2889 | 40.2758 | 39.6811 | 38.9737 | 38.2095 | 37.2821 | 36.4747 | 35.5789 | 34.6379 | 33.0674 | 32.1653 | 31.3558 | 27.0453 | 35.2811 | 34.4147 | 33.3221 | 32.1874 | 31.1137 | 30.1842 | 29.1484 | 28.0568 | 26.2589 | 25.2295 | 24.3032 | 27.2474 | 36.3137 | 36.1495 | 35.1232 | 33.9842 | 32.9074 | 31.9737 | 30.9337 | 29.8389 | 28.0358 | 27.0021 | 26.0737
|  | WHITELEY PRIMARY | EE |  |  |  |  | 31.2889 | 40.2758 | 39.7084 | 39.0968 | 38.48 | 37.9453 | 37.3737 | 36.7916 | 36.2063 | 34.7516 | 34.1105 | 33.5442 | 27.0453 | 35.2842 | 34.4621 | 33.5263 | 32.6179 | 31.9116 | 31.2611 | 30.5968 | 29.9305 | 28.2074 | 27.4579 | 26.7926 | 27.2474 | 36.3137 | 36.1537 | 35.3274 | 34.4168 | 33.7074 | 33.0547 | 32.3895 | 31.7211 | 29.9905 | 29.2379 | 28.5705
|  | WHITELEY PRIMARY | HT |  |  |  |  | 31.3068 | 40.2768 | 39.6811 | 38.9737 | 38.2095 | 37.2821 | 36.4747 | 35.5789 | 34.6379 | 33.0674 | 32.1653 | 31.3558 | 27.0695 | 35.2811 | 34.4147 | 33.3221 | 32.1874 | 31.1137 | 30.1842 | 29.1484 | 28.0568 | 26.2589 | 25.2295 | 24.3032 | 27.2526 | 36.32 | 36.1495 | 35.1232 | 33.9842 | 32.9074 | 31.9737 | 30.9337 | 29.8389 | 28.0358 | 27.0021 | 26.0737
|  | WHITELEY PRIMARY | HE |  |  |  |  | 31.3711 | 40.3863 | 39.8516 | 39.2642 | 38.6611 | 38.1905 | 37.6947 | 37.1568 | 36.6084 | 35.5968 | 35.2716 | 34.9537 | 27.1632 | 35.4474 | 34.6811 | 33.7916 | 32.9053 | 32.2347 | 31.6389 | 31.0295 | 30.4053 | 29.1874 | 28.8011 | 28.4221 | 27.2684 | 36.3389 | 36.1884 | 35.5937 | 34.7053 | 34.0326 | 33.4347 | 32.8232 | 32.1979 | 30.9747 | 30.5863 | 30.2053
|  | WHITELEY PRIMARY | FB |  |  |  |  | 33.7416 | 40.9063 | 40.6747 | 40.4253 | 40.2 | 40.0105 | 39.8589 | 39.6968 | 39.5347 | 38.7537 | 38.4632 | 38.2074 | 30.7579 | 36.1747 | 35.84 | 35.48 | 35.16 | 34.8947 | 34.6874 | 34.4505 | 34.2084 | 33.0053 | 32.5779 | 32.1958 | 27.5958 | 36.5095 | 36.4505 | 36.3853 | 36.3179 | 36.2547 | 36.1968 | 36.14 | 36.0126 | 34.8053 | 34.3758 | 33.9926
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WHITLEY WOOD PRIMARY | MINIMUM HEADROOM | SU 72812 69667 | NO | YES | 1.0526 | 30.7837 | 30.4826 | 30.1584 | 29.6079 | 28.7479 | 27.8458 | 26.9889 | 26.1353 | 25.3405 | 19.9879 | 14.0195 | 6.6384 | 28.1295 | 27.7653 | 27.38 | 26.7274 | 25.7211 | 24.6716 | 23.6768 | 22.6568 | 21.7105 | 14.4968 | 6.8389 | -1.7737 | 31.1337 | 30.7568 | 30.3568 | 29.6747 | 28.6168 | 27.5147 | 26.4726 | 25.4337 | 24.4737 | 16.9105 | 8.9274 | -0.097895
|  | WHITLEY WOOD PRIMARY | EE |  |  |  |  | 30.7837 | 30.4826 | 30.1668 | 29.7521 | 29.2047 | 28.53 | 27.8342 | 27.1468 | 26.5521 | 19.9879 | 15.19 | 7.5374 | 28.1295 | 27.7653 | 27.3916 | 26.9095 | 26.3116 | 25.5474 | 24.7495 | 23.9642 | 23.2968 | 14.4968 | 8.0611 | -0.92421 | 31.1337 | 30.7568 | 30.3684 | 29.8716 | 29.2558 | 28.4589 | 27.6253 | 26.8074 | 26.1137 | 16.9105 | 10.16 | 0.72737
|  | WHITLEY WOOD PRIMARY | HT |  |  |  |  | 30.8353 | 30.5332 | 30.1584 | 29.6079 | 28.7479 | 27.8458 | 26.9889 | 26.1353 | 25.3405 | 23.7626 | 14.0195 | 6.6384 | 28.2032 | 27.8337 | 27.38 | 26.7274 | 25.7211 | 24.6716 | 23.6768 | 22.6568 | 21.7105 | 19.8705 | 6.8389 | -1.7737 | 31.2126 | 30.8274 | 30.3568 | 29.6747 | 28.6168 | 27.5147 | 26.4726 | 25.4337 | 24.4737 | 22.5926 | 8.9274 | -0.097895
|  | WHITLEY WOOD PRIMARY | HE |  |  |  |  | 30.9658 | 30.7332 | 30.4711 | 30.1037 | 29.6163 | 29.01 | 28.3584 | 27.7174 | 27.1658 | 21.0889 | 16.5963 | 9.4163 | 28.3832 | 28.1179 | 27.8232 | 27.4053 | 26.8547 | 26.1389 | 25.3979 | 24.6716 | 24.0589 | 15.8653 | 9.7916 | 1.1042 | 31.4042 | 31.1316 | 30.8284 | 30.4 | 29.8347 | 29.0905 | 28.3179 | 27.5621 | 26.9274 | 18.3316 | 11.9526 | 2.8274
|  | WHITLEY WOOD PRIMARY | FB |  |  |  |  | 31.3911 | 31.2289 | 31.1016 | 30.9479 | 30.7784 | 30.5911 | 30.3616 | 30.1332 | 29.93 | 28.0468 | 23.29 | 17.6089 | 28.9653 | 28.7621 | 28.6074 | 28.4179 | 28.2063 | 27.9695 | 27.6674 | 27.3632 | 27.1 | 24.7705 | 18.3968 | 10.7326 | 32.0221 | 31.8095 | 31.6484 | 31.4505 | 31.2295 | 30.9821 | 30.6632 | 30.3421 | 30.0653 | 27.5789 | 20.9263 | 12.88
MINETY GSP | CIRENCESTER BSP | WHITEWAY PRIMARY | MINIMUM HEADROOM | SP 02076 03059 | NO | YES | 0 | 30.85 | 30.7921 | 30.7395 | 30.6816 | 30.2647 | 29.6437 | 29.0237 | 28.39 | 27.7553 | 26.1268 | 24.93 | 23.6616 | 25.4589 | 25.3137 | 25.2021 | 24.8863 | 24.2853 | 23.5768 | 22.8684 | 22.1432 | 21.4147 | 19.5358 | 18.1379 | 16.6421 | 28.9358 | 28.8779 | 28.8253 | 28.7674 | 28.3884 | 27.7063 | 27.0232 | 26.3242 | 25.6242 | 23.8189 | 22.4579 | 20.9726
|  | WHITEWAY PRIMARY | EE |  |  |  |  | 31.1658 | 31.0489 | 30.9174 | 30.7489 | 30.5205 | 30.2216 | 29.8426 | 29.4753 | 29.1216 | 28.2489 | 27.4247 | 26.5268 | 25.8221 | 25.5747 | 25.3211 | 25.0453 | 24.6747 | 24.2779 | 23.8568 | 23.4526 | 23.0642 | 22.0358 | 21.0579 | 19.9779 | 29.3232 | 29.2063 | 29.0747 | 28.9053 | 28.6779 | 28.3716 | 27.9632 | 27.5695 | 27.1916 | 26.2084 | 25.2758 | 24.2495
|  | WHITEWAY PRIMARY | HT |  |  |  |  | 31.1805 | 31.0658 | 30.9142 | 30.7216 | 30.2647 | 29.6437 | 29.0237 | 28.39 | 27.7553 | 26.1268 | 24.93 | 23.6616 | 25.8842 | 25.6347 | 25.3305 | 24.8863 | 24.2853 | 23.5768 | 22.8684 | 22.1432 | 21.4147 | 19.5358 | 18.1379 | 16.6421 | 29.3379 | 29.2232 | 29.0716 | 28.8789 | 28.3884 | 27.7063 | 27.0232 | 26.3242 | 25.6242 | 23.8189 | 22.4579 | 20.9726
|  | WHITEWAY PRIMARY | HE |  |  |  |  | 31.2226 | 31.1226 | 31.0005 | 30.8405 | 30.6174 | 30.4079 | 30.2058 | 29.9963 | 29.7395 | 29.2879 | 28.7247 | 28.0542 | 26.0295 | 25.86 | 25.6684 | 25.4463 | 25.1474 | 24.7937 | 24.4484 | 24.1189 | 23.8021 | 23.2579 | 22.5779 | 21.7568 | 29.38 | 29.28 | 29.1579 | 28.9979 | 28.7747 | 28.5653 | 28.3632 | 28.1537 | 27.8937 | 27.3768 | 26.7316 | 25.9547
|  | WHITEWAY PRIMARY | FB |  |  |  |  | 30.85 | 30.7921 | 30.7395 | 30.6816 | 30.6163 | 30.5511 | 30.4879 | 30.4279 | 30.3647 | 29.93 | 29.9342 | 29.3679 | 25.4589 | 25.3137 | 25.2021 | 25.0863 | 24.9632 | 24.8116 | 24.6589 | 24.5189 | 24.3758 | 23.7895 | 23.8874 | 23.2042 | 28.9358 | 28.8779 | 28.8253 | 28.7674 | 28.7021 | 28.6368 | 28.5737 | 28.5137 | 28.4505 | 28.0032 | 28.0116 | 27.3632
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WILSON ROAD PRIMARY | MINIMUM HEADROOM | SU 69235 73304 | NO | YES | 0 | 32.6953 | 32.5132 | 32.2984 | 31.8911 | 31.0774 | 30.1721 | 29.7426 | 29.2974 | 28.8553 | 27.4732 | 26.3405 | 25.2879 | 29.3326 | 29.1 | 28.6305 | 28.0074 | 26.9253 | 25.7179 | 25.2432 | 24.7411 | 24.2432 | 22.5453 | 21.0821 | 19.7095 | 30.6232 | 30.2558 | 29.7789 | 29.1463 | 28.0442 | 26.8137 | 26.3358 | 25.8295 | 25.3263 | 23.6053 | 22.1168 | 20.7211
|  | WILSON ROAD PRIMARY | EE |  |  |  |  | 32.6953 | 32.5132 | 32.2984 | 31.9437 | 31.1037 | 30.2089 | 29.7868 | 29.3563 | 28.9321 | 28.2374 | 27.4711 | 26.7816 | 29.3326 | 29.1 | 28.6421 | 28.0905 | 26.98 | 25.7832 | 25.3 | 24.8126 | 24.3326 | 23.4084 | 22.3568 | 21.3989 | 30.6232 | 30.2558 | 29.7916 | 29.2316 | 28.1011 | 26.8811 | 26.3937 | 25.9 | 25.4168 | 24.4758 | 23.4021 | 22.4253
|  | WILSON ROAD PRIMARY | HT |  |  |  |  | 32.7163 | 32.5363 | 32.3068 | 31.8911 | 31.0774 | 30.1721 | 29.7426 | 29.2974 | 28.8553 | 27.4732 | 26.3405 | 25.2879 | 29.3547 | 29.1084 | 28.6305 | 28.0074 | 26.9253 | 25.7179 | 25.2432 | 24.7411 | 24.2432 | 22.5453 | 21.0821 | 19.7095 | 30.6968 | 30.2653 | 29.7789 | 29.1463 | 28.0442 | 26.8137 | 26.3358 | 25.8295 | 25.3263 | 23.6053 | 22.1168 | 20.7211
|  | WILSON ROAD PRIMARY | HE |  |  |  |  | 32.7416 | 32.5595 | 32.3416 | 32.0511 | 31.3426 | 30.4668 | 30.0763 | 29.6847 | 29.3005 | 29.0921 | 28.6363 | 28.2153 | 29.3832 | 29.1979 | 28.9716 | 28.46 | 27.3653 | 26.2011 | 25.7768 | 25.3526 | 24.9368 | 24.6221 | 23.9611 | 23.3432 | 30.7242 | 30.5368 | 30.1295 | 29.6105 | 28.4968 | 27.3105 | 26.8842 | 26.4579 | 26.04 | 25.7168 | 25.0411 | 24.4084
|  | WILSON ROAD PRIMARY | FB |  |  |  |  | 32.8689 | 32.7658 | 32.6721 | 32.5647 | 32.4247 | 32.17 | 32.0163 | 31.8689 | 31.7142 | 31.1332 | 30.5868 | 30.1121 | 29.5137 | 29.4074 | 29.3095 | 29.1989 | 28.7989 | 28.2937 | 28.1105 | 27.9337 | 27.7495 | 27.0505 | 26.32 | 25.6621 | 30.8474 | 30.7495 | 30.6358 | 30.3968 | 29.9495 | 29.4337 | 29.2484 | 29.0684 | 28.8832 | 28.1747 | 27.4305 | 26.7579
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE PRIMARY | MINIMUM HEADROOM | SZ 02014 99989 | NO | YES | 0 | 22.1432 | 21.4337 | 38.5716 | 37.32 | 35.9442 | 34.6042 | 33.2821 | 31.9232 | 30.5705 | 27.2716 | 25.0463 | 23.0432 | 21.8558 | 21.0642 | 35.8474 | 34.4432 | 32.9084 | 31.4253 | 29.96 | 28.4505 | 26.9474 | 23.2716 | 20.7779 | 18.5316 | 22.3558 | 21.6095 | 37.6789 | 36.3579 | 34.9126 | 33.5095 | 32.1232 | 30.6979 | 29.2179 | 25.5505 | 23.0621 | 20.82
|  | WIMBORNE PRIMARY | EE |  |  |  |  | 22.1432 | 21.4337 | 38.7168 | 37.78 | 36.7653 | 35.9947 | 35.2221 | 34.4463 | 33.6947 | 31.9663 | 30.4084 | 29.0726 | 21.8558 | 21.0642 | 36.0168 | 34.9789 | 33.8768 | 33.0537 | 32.2242 | 31.3926 | 30.5863 | 28.6095 | 26.8263 | 25.2926 | 22.3558 | 21.6095 | 37.8347 | 36.8526 | 35.7989 | 35.0053 | 34.2074 | 33.4063 | 32.6305 | 30.7916 | 29.0958 | 27.5663
|  | WIMBORNE PRIMARY | HT |  |  |  |  | 22.2147 | 21.4611 | 38.5716 | 37.32 | 35.9442 | 34.6042 | 33.2821 | 31.9232 | 30.5705 | 27.2716 | 25.0463 | 23.0432 | 21.9379 | 21.0916 | 35.8474 | 34.4432 | 32.9084 | 31.4253 | 29.96 | 28.4505 | 26.9474 | 23.2716 | 20.7779 | 18.5316 | 22.4316 | 21.6368 | 37.6789 | 36.3579 | 34.9126 | 33.5095 | 32.1232 | 30.6979 | 29.2179 | 25.5505 | 23.0621 | 20.82
|  | WIMBORNE PRIMARY | HE |  |  |  |  | 22.4821 | 21.8979 | 39.2947 | 38.4474 | 37.5021 | 36.8105 | 36.1421 | 35.4674 | 34.8179 | 33.8916 | 32.8326 | 31.92 | 22.2421 | 21.5958 | 36.6779 | 35.7442 | 34.72 | 33.9874 | 33.28 | 32.5653 | 31.8789 | 30.7821 | 29.5495 | 28.4832 | 22.7158 | 22.1042 | 38.4495 | 37.5642 | 36.5832 | 35.8737 | 35.1884 | 34.4958 | 33.8295 | 32.8274 | 31.6905 | 30.7105
|  | WIMBORNE PRIMARY | FB |  |  |  |  | 22.8432 | 22.4747 | 40.3484 | 39.9853 | 39.6295 | 39.3495 | 39.0716 | 38.8011 | 38.5253 | 37.3221 | 36.2779 | 35.3737 | 22.6368 | 22.2221 | 37.8379 | 37.4305 | 37.0337 | 36.7274 | 36.4211 | 36.1242 | 35.82 | 34.4832 | 33.2979 | 32.2611 | 23.0916 | 22.7032 | 39.5505 | 39.1674 | 38.7937 | 38.5021 | 38.2116 | 37.9295 | 37.6411 | 36.3779 | 35.2716 | 34.3084
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES PRIMARY | MINIMUM HEADROOM | SU 03028 12678 | YES | YES | 0 | 5.0621 | 5.0442 | 5.0274 | 5.0084 | 4.9842 | 4.9621 | 4.9379 | 4.9147 | 4.8926 | 4.8284 | 4.7789 | 4.7337 | 4.9358 | 4.9179 | 4.8989 | 4.8789 | 4.8537 | 4.8305 | 4.8053 | 4.7811 | 4.7568 | 4.6905 | 4.6358 | 4.5863 | 4.9368 | 4.9179 | 4.8989 | 4.8789 | 4.8537 | 4.8305 | 4.8053 | 4.7811 | 4.7579 | 4.6905 | 4.6358 | 4.5874
|  | WIMBORNE ST GILES PRIMARY | EE |  |  |  |  | 5.0621 | 5.0442 | 5.0274 | 5.0084 | 4.9842 | 4.9621 | 4.9379 | 4.9147 | 4.8926 | 4.8495 | 4.8158 | 4.7863 | 4.9358 | 4.9179 | 4.8989 | 4.8789 | 4.8537 | 4.8305 | 4.8053 | 4.7811 | 4.7568 | 4.7084 | 4.6705 | 4.6389 | 4.9368 | 4.9179 | 4.8989 | 4.8789 | 4.8537 | 4.8305 | 4.8053 | 4.7811 | 4.7579 | 4.7095 | 4.6716 | 4.6389
|  | WIMBORNE ST GILES PRIMARY | HT |  |  |  |  | 5.0663 | 5.0495 | 5.0326 | 5.0137 | 4.9916 | 4.9695 | 4.9463 | 4.9211 | 4.8979 | 4.8284 | 4.7789 | 4.7337 | 4.9411 | 4.9232 | 4.9053 | 4.8853 | 4.8621 | 4.8389 | 4.8158 | 4.7895 | 4.7642 | 4.6905 | 4.6358 | 4.5863 | 4.9411 | 4.9232 | 4.9053 | 4.8853 | 4.8621 | 4.8389 | 4.8158 | 4.7895 | 4.7642 | 4.6905 | 4.6358 | 4.5874
|  | WIMBORNE ST GILES PRIMARY | HE |  |  |  |  | 5.0747 | 5.0621 | 5.0474 | 5.0305 | 5.0105 | 4.9895 | 4.9705 | 4.9516 | 4.9326 | 4.9211 | 4.9063 | 4.8937 | 4.9505 | 4.9368 | 4.9221 | 4.9042 | 4.8832 | 4.8621 | 4.8421 | 4.8242 | 4.8032 | 4.7905 | 4.7726 | 4.7589 | 4.9505 | 4.9379 | 4.9221 | 4.9042 | 4.8832 | 4.8621 | 4.8432 | 4.8242 | 4.8042 | 4.7916 | 4.7737 | 4.7589
|  | WIMBORNE ST GILES PRIMARY | FB |  |  |  |  | 5.0832 | 5.0737 | 5.0663 | 5.0579 | 5.0516 | 5.0432 | 5.0347 | 5.0274 | 5.02 | 4.9884 | 4.9632 | 4.9421 | 4.96 | 4.9495 | 4.9421 | 4.9326 | 4.9253 | 4.9158 | 4.9074 | 4.9 | 4.8916 | 4.8579 | 4.8295 | 4.8063 | 4.96 | 4.9495 | 4.9421 | 4.9326 | 4.9253 | 4.9158 | 4.9074 | 4.9 | 4.8916 | 4.8579 | 4.8295 | 4.8063
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON PRIMARY | MINIMUM HEADROOM | ST 71286 27802 | NO | YES | 0 | 12.5249 | 12.3333 | 12.1533 | 11.947 | 11.7028 | 11.3859 | 11.0133 | 8.9143 | 8.6364 | 5.3501 | 4.888 | 4.3743 | 8.9312 | 8.7217 | 8.5291 | 8.3101 | 8.0543 | 7.7154 | 7.3112 | 4.887 | 4.5922 | 0.75644 | 0.23329 | -0.35513 | 10.267 | 10.0585 | 9.8659 | 9.648 | 9.3933 | 9.0554 | 8.6533 | 6.2501 | 5.9564 | 2.1228 | 1.5975 | 1.007
|  | WINCANTON PRIMARY | EE |  |  |  |  | 12.5249 | 12.3333 | 12.1533 | 11.947 | 11.7028 | 11.4691 | 11.2312 | 9.9343 | 9.5712 | 5.3501 | 4.888 | 4.3743 | 8.9312 | 8.7217 | 8.5291 | 8.3101 | 8.0543 | 7.8112 | 7.5585 | 6.0712 | 5.6722 | 0.75644 | 0.23329 | -0.35513 | 10.267 | 10.0585 | 9.8659 | 9.648 | 9.3933 | 9.1491 | 8.8985 | 7.4238 | 7.028 | 2.1228 | 1.5975 | 1.007
|  | WINCANTON PRIMARY | HT |  |  |  |  | 12.5585 | 12.3817 | 12.1985 | 11.9901 | 11.7585 | 11.3859 | 11.0133 | 8.9143 | 8.6364 | 6.1112 | 5.4417 | 4.6964 | 8.9701 | 8.7764 | 8.5817 | 8.3617 | 8.1196 | 7.7154 | 7.3112 | 4.887 | 4.5922 | 1.7101 | 0.97013 | 0.13644 | 10.3049 | 10.1133 | 9.9185 | 9.6996 | 9.4585 | 9.0554 | 8.6533 | 6.2501 | 5.9564 | 3.0817 | 2.3385 | 1.5028
|  | WINCANTON PRIMARY | HE |  |  |  |  | 12.6438 | 12.4975 | 12.3596 | 12.1838 | 11.9607 | 11.7564 | 11.5607 | 10.3575 | 10.0807 | 6.0922 | 5.8249 | 5.4733 | 9.0659 | 8.908 | 8.7628 | 8.5796 | 8.3491 | 8.1364 | 7.9343 | 6.5554 | 6.2575 | 1.5922 | 1.2838 | 0.87644 | 10.4007 | 10.2438 | 10.0985 | 9.9154 | 9.6859 | 9.4743 | 9.2722 | 7.9049 | 7.608 | 2.9607 | 2.6512 | 2.2428
|  | WINCANTON PRIMARY | FB |  |  |  |  | 12.7964 | 12.6933 | 12.6196 | 12.5407 | 12.4554 | 12.3722 | 12.2922 | 12.2143 | 12.0859 | 11.6617 | 11.3417 | 11.0007 | 9.2333 | 9.1196 | 9.0396 | 8.9543 | 8.8617 | 8.7722 | 8.6859 | 8.6017 | 8.4585 | 7.9901 | 7.6312 | 7.2417 | 10.567 | 10.4543 | 10.3743 | 10.2891 | 10.1975 | 10.108 | 10.0217 | 9.9385 | 9.7964 | 9.3301 | 8.9743 | 8.587
COWLEY GSP | WITNEY BSP | WINDRUSH PARK PRIMARY | MINIMUM HEADROOM | SP 33366 09758 | NO | YES | 0 | 32.3116 | 32.1779 | 31.96 | 31.6779 | 31.4105 | 31.1358 | 30.8895 | 30.5821 | 30.2737 | 29.92 | 29.0937 | 27.6632 | 28.7516 | 28.6032 | 28.3537 | 28.0305 | 27.7305 | 27.4305 | 27.1663 | 26.8316 | 26.4958 | 26.3253 | 25.3958 | 23.5663 | 31.2474 | 31.0958 | 30.8411 | 30.5105 | 30.2053 | 29.9 | 29.6326 | 29.2916 | 28.9495 | 28.8821 | 27.9284 | 25.9495
|  | WINDRUSH PARK PRIMARY | EE |  |  |  |  | 32.3642 | 32.2305 | 32.0979 | 31.94 | 31.7474 | 31.5621 | 31.3726 | 31.1789 | 30.9905 | 30.6042 | 30.6011 | 30.0021 | 28.8211 | 28.6716 | 28.5242 | 28.3537 | 28.1505 | 27.9537 | 27.7474 | 27.5379 | 27.3337 | 26.8884 | 27.0884 | 26.4011 | 31.3179 | 31.1653 | 31.0179 | 30.8453 | 30.6389 | 30.44 | 30.2295 | 30.0179 | 29.8105 | 29.3547 | 29.66 | 28.9537
|  | WINDRUSH PARK PRIMARY | HT |  |  |  |  | 32.3116 | 32.1779 | 31.96 | 31.6779 | 31.4105 | 31.1358 | 30.8895 | 30.5821 | 30.2737 | 29.92 | 29.0937 | 27.6632 | 28.7516 | 28.6032 | 28.3537 | 28.0305 | 27.7305 | 27.4305 | 27.1663 | 26.8316 | 26.4958 | 26.3253 | 25.3958 | 23.5663 | 31.2474 | 31.0958 | 30.8411 | 30.5105 | 30.2053 | 29.9 | 29.6326 | 29.2916 | 28.9495 | 28.8821 | 27.9284 | 25.9495
|  | WINDRUSH PARK PRIMARY | HE |  |  |  |  | 32.4632 | 32.3632 | 32.26 | 32.1295 | 31.9547 | 31.7926 | 31.6379 | 31.4789 | 31.3253 | 31.2116 | 30.8621 | 30.3989 | 28.9358 | 28.8274 | 28.7179 | 28.5789 | 28.3958 | 28.2263 | 28.0632 | 27.8968 | 27.7347 | 27.5916 | 27.1642 | 26.6263 | 31.4368 | 31.3263 | 31.2158 | 31.0758 | 30.8916 | 30.72 | 30.5568 | 30.3884 | 30.2253 | 30.0768 | 29.6368 | 29.0832
|  | WINDRUSH PARK PRIMARY | FB |  |  |  |  | 32.5537 | 32.5211 | 32.4905 | 32.4579 | 32.4147 | 32.3463 | 32.2821 | 32.2179 | 32.1516 | 31.8989 | 31.5811 | 31.2221 | 29.1853 | 29.1 | 29.0368 | 28.9695 | 28.8968 | 28.8211 | 28.7495 | 28.6779 | 28.6053 | 28.3221 | 27.9453 | 27.5137 | 31.6916 | 31.6053 | 31.5411 | 31.4726 | 31.3989 | 31.3221 | 31.2495 | 31.1758 | 31.1021 | 30.8147 | 30.4284 | 29.9842
MANNINGTON GSP |  | WINFRITH HEATH PRIMARY | MINIMUM HEADROOM | SY 80748 86538 | NO | YES | 0 | 11.995 | 11.8539 | 11.655 | 11.3782 | 11.0455 | 10.6803 | 10.3192 | 8.0992 | 5.6592 | 4.7076 | 4.0739 | 3.5045 | 23.4792 | 23.3234 | 23.1013 | 22.7929 | 22.4213 | 22.0139 | 21.6097 | 19.0182 | 16.1655 | 15.0939 | 14.3792 | 13.735 | 8.4897 | 8.335 | 8.1139 | 7.8055 | 7.435 | 7.0287 | 6.6255 | 4.0413 | 1.1961 | 0.12763 | -0.58605 | -1.2282
|  | WINFRITH HEATH PRIMARY | EE |  |  |  |  | 11.995 | 11.8539 | 11.7034 | 11.5255 | 11.3087 | 11.1024 | 10.8887 | 9.7518 | 8.5108 | 5.4266 | 4.9676 | 4.5645 | 23.4792 | 23.3234 | 23.1582 | 22.9645 | 22.7329 | 22.5097 | 22.2782 | 20.9582 | 19.5161 | 15.895 | 15.3666 | 14.9024 | 8.4897 | 8.335 | 8.1697 | 7.9771 | 7.7445 | 7.5234 | 7.2908 | 5.975 | 4.5371 | 0.92553 | 0.40026 | -0.063947
|  | WINFRITH HEATH PRIMARY | HT |  |  |  |  | 12.0108 | 11.8613 | 11.655 | 11.3782 | 11.0455 | 10.6803 | 10.3192 | 8.0992 | 5.6592 | 4.7076 | 4.0739 | 3.5045 | 23.4961 | 23.3308 | 23.1013 | 22.7929 | 22.4213 | 22.0139 | 21.6097 | 19.0182 | 16.1655 | 15.0939 | 14.3792 | 13.735 | 8.5076 | 8.3424 | 8.1139 | 7.8055 | 7.435 | 7.0287 | 6.6255 | 4.0413 | 1.1961 | 0.12763 | -0.58605 | -1.2282
|  | WINFRITH HEATH PRIMARY | HE |  |  |  |  | 12.075 | 11.9666 | 11.8424 | 11.6855 | 11.4866 | 11.3034 | 11.1234 | 10.0213 | 8.8139 | 5.9655 | 5.6445 | 5.3582 | 23.5708 | 23.4518 | 23.3171 | 23.1487 | 22.9361 | 22.7392 | 22.5476 | 21.2676 | 19.8645 | 16.5076 | 16.1329 | 15.7971 | 8.5813 | 8.4634 | 8.3287 | 8.1603 | 7.9476 | 7.7518 | 7.5592 | 6.2834 | 4.8845 | 1.5371 | 1.1645 | 0.82868
|  | WINFRITH HEATH PRIMARY | FB |  |  |  |  | 12.1518 | 12.0803 | 12.0192 | 11.9518 | 11.8782 | 11.8055 | 11.7308 | 11.6571 | 11.5813 | 11.255 | 10.9603 | 10.7013 | 23.6529 | 23.5729 | 23.5055 | 23.4318 | 23.3497 | 23.2697 | 23.1866 | 23.1045 | 23.0203 | 22.6561 | 22.3192 | 22.0203 | 8.6634 | 8.5834 | 8.5171 | 8.4434 | 8.3613 | 8.2813 | 8.1982 | 8.1171 | 8.0329 | 7.6687 | 7.3329 | 7.035
COWLEY GSP | DRAYTON BSP | WINSMORE LANE PRIMARY | MINIMUM HEADROOM | SU 49513 96982 | NO | YES | 0.2 | 25.5884 | 25.4063 | 25.2105 | 24.9263 | 24.5842 | 24.2126 | 23.8411 | 23.46 | 22.76 | 20.3463 | 18.7853 | 16.8189 | 18.5874 | 18.2337 | 17.8621 | 17.3189 | 16.7 | 16.0663 | 15.4253 | 14.6968 | 13.9421 | 11.2832 | 9.56 | 7.36 | 23.0253 | 22.76 | 22.4853 | 22.0821 | 21.6126 | 21.1211 | 20.6263 | 20.0895 | 19.54 | 17.8042 | 16.4621 | 14.2316
|  | WINSMORE LANE PRIMARY | EE |  |  |  |  | 25.5884 | 25.4063 | 25.2105 | 24.9516 | 24.5842 | 24.2505 | 23.9432 | 23.6242 | 23.3084 | 22.2789 | 21.3768 | 20.18 | 18.5947 | 18.2337 | 17.8726 | 17.4621 | 16.8589 | 16.3958 | 15.9253 | 15.4484 | 14.9821 | 13.4032 | 12.4011 | 11.0474 | 23.0253 | 22.76 | 22.4895 | 22.1611 | 21.6863 | 21.2926 | 20.9105 | 20.5179 | 20.1347 | 19.2126 | 18.5905 | 17.8211
|  | WINSMORE LANE PRIMARY | HT |  |  |  |  | 25.6021 | 25.4316 | 25.2126 | 24.9263 | 24.5842 | 24.2126 | 23.8411 | 23.46 | 22.76 | 20.3463 | 18.7853 | 16.8189 | 18.5874 | 18.2442 | 17.8621 | 17.3189 | 16.7 | 16.0663 | 15.4253 | 14.6968 | 13.9421 | 11.2832 | 9.56 | 7.36 | 23.0295 | 22.78 | 22.4853 | 22.0821 | 21.6126 | 21.1211 | 20.6263 | 20.0895 | 19.54 | 17.8042 | 16.4621 | 14.2316
|  | WINSMORE LANE PRIMARY | HE |  |  |  |  | 25.6537 | 25.4884 | 25.3021 | 25.0505 | 24.6916 | 24.3611 | 24.0558 | 23.7368 | 23.4274 | 23.3642 | 23.1095 | 22.2358 | 18.8558 | 18.5926 | 18.3105 | 17.9653 | 17.52 | 16.9937 | 16.6063 | 16.2074 | 15.8263 | 14.9105 | 14.3232 | 13.3232 | 23.1811 | 22.9705 | 22.74 | 22.4453 | 22.0474 | 21.6274 | 21.2842 | 20.9284 | 20.5863 | 20.1326 | 19.8 | 19.2758
|  | WINSMORE LANE PRIMARY | FB |  |  |  |  | 25.7737 | 25.6789 | 25.5958 | 25.5032 | 25.3989 | 25.2968 | 25.1968 | 25.1032 | 25.0042 | 24.6347 | 24.3832 | 23.8537 | 19.1232 | 18.9116 | 18.7474 | 18.5737 | 18.3516 | 18.1674 | 17.9874 | 17.8147 | 17.6389 | 16.9105 | 15.8811 | 15.0305 | 23.3674 | 23.22 | 23.1 | 22.9695 | 22.8116 | 22.6716 | 22.5347 | 22.4053 | 22.2705 | 21.7368 | 21.1284 | 20.6442
MANNINGTON GSP | LYTCHETT BSP | WINTERBORNE KINGSTON PRIMARY | MINIMUM HEADROOM | SY 84631 98138 | NO | YES | 0 | 23.6221 | 23.4516 | 23.2474 | 22.9568 | 22.6147 | 22.2411 | 21.8705 | 21.4884 | 19.8074 | 18.7895 | 13.3832 | -1.7758 | 21.5779 | 21.3863 | 21.1526 | 20.8232 | 20.4347 | 20.0116 | 19.5905 | 19.1547 | 17.2189 | 16.0958 | 9.7021 | -8.1842 | 22.1663 | 21.9726 | 21.7389 | 21.4063 | 21.0158 | 20.5884 | 20.1653 | 19.7263 | 17.7684 | 16.6358 | 10.2105 | -7.6653
|  | WINTERBORNE KINGSTON PRIMARY | EE |  |  |  |  | 23.6221 | 23.4516 | 23.2716 | 23.0611 | 22.8042 | 22.56 | 22.3137 | 22.0684 | 21.2147 | 20.6621 | 13.3832 | -1.7758 | 21.5779 | 21.3863 | 21.1842 | 20.9516 | 20.6737 | 20.4084 | 20.1368 | 19.8674 | 18.8495 | 18.2211 | 9.7021 | -8.1842 | 22.1663 | 21.9726 | 21.7684 | 21.5347 | 21.2558 | 20.9895 | 20.7158 | 20.4442 | 19.4158 | 18.7842 | 10.2105 | -7.6653
|  | WINTERBORNE KINGSTON PRIMARY | HT |  |  |  |  | 23.6463 | 23.4737 | 23.2474 | 22.9568 | 22.6147 | 22.2411 | 21.8705 | 21.4884 | 19.8074 | 18.7895 | 18.1084 | 4.3979 | 21.6063 | 21.4105 | 21.1526 | 20.8232 | 20.4347 | 20.0116 | 19.5905 | 19.1547 | 17.2189 | 16.0958 | 15.34 | -0.77474 | 22.1958 | 21.9979 | 21.7389 | 21.4063 | 21.0158 | 20.5884 | 20.1653 | 19.7263 | 17.7684 | 16.6358 | 15.8737 | -0.26947
|  | WINTERBORNE KINGSTON PRIMARY | HE |  |  |  |  | 23.7263 | 23.5979 | 23.4505 | 23.2705 | 23.0347 | 22.8179 | 22.6063 | 22.3947 | 21.5853 | 21.32 | 14.2074 | -0.80842 | 21.7011 | 21.56 | 21.3968 | 21.2011 | 20.9474 | 20.7137 | 20.4863 | 20.2589 | 19.2842 | 18.9589 | 10.6274 | -7.0979 | 22.2905 | 22.1484 | 21.9853 | 21.7884 | 21.5337 | 21.2989 | 21.0705 | 20.8421 | 19.8579 | 19.5284 | 11.1379 | -6.58
|  | WINTERBORNE KINGSTON PRIMARY | FB |  |  |  |  | 23.8242 | 23.7347 | 23.6632 | 23.5842 | 23.4989 | 23.4126 | 23.3274 | 23.2442 | 23.1589 | 20.2863 | 13.9547 | 0.75579 | 21.8084 | 21.7063 | 21.6253 | 21.5358 | 21.4389 | 21.3421 | 21.2453 | 21.1505 | 21.0537 | 17.6495 | 10.2274 | -5.3432 | 22.3989 | 22.2958 | 22.2137 | 22.1232 | 22.0263 | 21.9284 | 21.8316 | 21.7358 | 21.6379 | 18.1958 | 10.7379 | -4.8295
MANNINGTON GSP | REDHILL BSP | WINTON PRIMARY | MINIMUM HEADROOM | SZ 09349 93822 | NO | YES | 0 | 32.3274 | 31.8316 | 38.0368 | 37.2168 | 36.2768 | 35.0211 | 33.8137 | 32.5389 | 31.2779 | 28.4642 | 26.4611 | 24.6642 | 32.3242 | 32.0274 | 38.5021 | 37.9095 | 36.7937 | 35.2505 | 33.7747 | 32.1989 | 30.6411 | 27.1916 | 24.6832 | 22.4242 | 32.5474 | 32.2642 | 38.7516 | 38.3137 | 37.2568 | 35.7168 | 34.2432 | 32.6705 | 31.1158 | 27.6737 | 25.1705 | 22.9158
|  | WINTON PRIMARY | EE |  |  |  |  | 32.3274 | 31.8316 | 38.1242 | 37.5253 | 36.7947 | 36.0853 | 35.4063 | 34.7032 | 34.0284 | 32.7158 | 31.3505 | 30.1863 | 32.3242 | 32.0274 | 38.5021 | 38.0705 | 37.48 | 36.7705 | 36.0158 | 35.2347 | 34.4905 | 32.7811 | 30.9821 | 29.4347 | 32.5474 | 32.2642 | 38.7516 | 38.3305 | 37.7495 | 37.1989 | 36.4789 | 35.6979 | 34.9547 | 33.2474 | 31.4547 | 29.9116
|  | WINTON PRIMARY | HT |  |  |  |  | 32.4011 | 31.8611 | 38.0368 | 37.2168 | 36.2768 | 35.0211 | 33.8137 | 32.5389 | 31.2779 | 28.4642 | 26.4611 | 24.6642 | 32.3474 | 32.0674 | 38.5021 | 37.9095 | 36.7937 | 35.2505 | 33.7747 | 32.1989 | 30.6411 | 27.1916 | 24.6832 | 22.4242 | 32.5674 | 32.3042 | 38.7568 | 38.3137 | 37.2568 | 35.7168 | 34.2432 | 32.6705 | 31.1158 | 27.6737 | 25.1705 | 22.9158
|  | WINTON PRIMARY | HE |  |  |  |  | 32.5726 | 32.2726 | 38.6642 | 38.1474 | 37.4674 | 36.8358 | 36.2411 | 35.6263 | 35.0411 | 34.5432 | 33.6958 | 32.9684 | 32.4168 | 32.1421 | 38.6358 | 38.2147 | 37.6284 | 37.0968 | 36.5811 | 36.0547 | 35.54 | 35.1568 | 33.9895 | 32.9789 | 32.6242 | 32.3568 | 38.8568 | 38.4432 | 37.8621 | 37.3379 | 36.8274 | 36.3074 | 35.7968 | 35.6189 | 34.4558 | 33.4474
|  | WINTON PRIMARY | FB |  |  |  |  | 32.7884 | 32.6242 | 39.2611 | 39.0316 | 38.7874 | 38.5421 | 38.3053 | 38.08 | 37.8505 | 36.8274 | 35.8821 | 35.0821 | 32.6158 | 32.4747 | 39.1484 | 39.0084 | 38.8537 | 38.6979 | 38.5463 | 38.4053 | 38.2547 | 37.4979 | 36.2747 | 35.2116 | 32.8168 | 32.6842 | 39.3642 | 39.2305 | 39.0821 | 38.9316 | 38.7863 | 38.6505 | 38.5053 | 37.96 | 36.74 | 35.68
COWLEY GSP | WITNEY BSP | WITNEY TOWN PRIMARY | MINIMUM HEADROOM | SP 35844 09625 | NO | YES | 0 | 44.8116 | 44.5821 | 44.3347 | 43.9737 | 42.9242 | 41.1979 | 39.6284 | 37.8579 | 36.0453 | 31.9832 | 29.7516 | 27.44 | 34.6968 | 34.3295 | 33.8084 | 32.9 | 31.6695 | 30.3295 | 29.1011 | 27.7863 | 26.4716 | 23.5 | 21.2284 | 18.62 | 42.1853 | 41.9547 | 41.7074 | 40.4263 | 38.5105 | 36.4295 | 34.5505 | 32.5084 | 30.46 | 25.88 | 23.3768 | 20.7674
|  | WITNEY TOWN PRIMARY | EE |  |  |  |  | 44.8116 | 44.5821 | 44.3347 | 43.9979 | 43.5253 | 42.16 | 40.7863 | 39.4021 | 37.9895 | 35.3716 | 33.9158 | 32.4095 | 34.6968 | 34.3295 | 33.9168 | 33.2253 | 32.1358 | 31.0011 | 29.9305 | 28.8474 | 27.7747 | 25.9947 | 24.9589 | 23.9168 | 42.1853 | 41.9547 | 41.7084 | 41.0105 | 39.3905 | 37.6558 | 36.0063 | 34.3474 | 32.7053 | 29.6916 | 28.0358 | 26.3084
|  | WITNEY TOWN PRIMARY | HT |  |  |  |  | 44.8316 | 44.6158 | 44.3347 | 43.9737 | 42.9242 | 41.1979 | 39.6284 | 37.8579 | 36.0453 | 31.9832 | 29.7516 | 27.44 | 34.7158 | 34.36 | 33.8084 | 32.9 | 31.6695 | 30.3295 | 29.1011 | 27.7863 | 26.4716 | 23.5 | 21.2284 | 18.62 | 42.2053 | 41.9895 | 41.7074 | 40.4263 | 38.5105 | 36.4295 | 34.5505 | 32.5084 | 30.46 | 25.88 | 23.3768 | 20.7674
|  | WITNEY TOWN PRIMARY | HE |  |  |  |  | 44.8863 | 44.6737 | 44.4379 | 44.1105 | 43.6432 | 42.8621 | 41.5842 | 40.3 | 39.0316 | 37.2916 | 36.3484 | 35.2832 | 34.9284 | 34.6432 | 34.2968 | 33.6621 | 32.6095 | 31.5305 | 30.5232 | 29.5095 | 28.5084 | 27.3916 | 26.7589 | 26.0632 | 42.26 | 42.0474 | 41.8116 | 41.4842 | 40.1695 | 38.5189 | 36.9926 | 35.4611 | 33.9474 | 31.86 | 30.7705 | 29.5305
|  | WITNEY TOWN PRIMARY | FB |  |  |  |  | 45.0326 | 44.9221 | 44.8232 | 44.7116 | 44.5884 | 44.4632 | 44.3421 | 44.1705 | 43.5053 | 41.8695 | 40.9832 | 40.0653 | 35.1442 | 34.9411 | 34.7653 | 34.4926 | 34.1116 | 33.6547 | 33.2063 | 32.7432 | 32.2474 | 30.9811 | 30.2926 | 29.6116 | 42.4063 | 42.2958 | 42.1968 | 42.0853 | 41.9621 | 41.4095 | 40.6789 | 39.9137 | 39.0958 | 37.1211 | 36.0526 | 34.92
FLEET-BRAMLEY GSP | WOKINGHAM BSP | WOKINGHAM PRIMARY | MINIMUM HEADROOM | SU 79589 67665 | NO | YES | 0 | 31.1921 | 31.0374 | 30.8511 | 30.6089 | 30.0984 | 29.3763 | 28.6911 | 27.9974 | 27.2911 | 25.57 | 24.7774 | 23.9426 | 28.2853 | 27.9905 | 27.5884 | 27.1789 | 26.4726 | 25.6379 | 24.8495 | 24.0484 | 23.2316 | 21.2232 | 20.3232 | 19.3579 | 29.5547 | 29.2642 | 28.8705 | 28.4653 | 27.7705 | 26.9379 | 26.1516 | 25.3516 | 24.5358 | 22.5316 | 21.6347 | 20.6705
|  | WOKINGHAM PRIMARY | EE |  |  |  |  | 31.1921 | 31.0374 | 30.8574 | 30.6321 | 30.2342 | 29.6426 | 29.0574 | 28.4721 | 27.8932 | 26.7742 | 26.2889 | 25.7732 | 28.2853 | 27.9905 | 27.5884 | 27.2505 | 26.6432 | 25.9695 | 25.2989 | 24.6284 | 23.9653 | 22.5916 | 22.0168 | 21.3937 | 29.5547 | 29.2642 | 28.8705 | 28.5347 | 27.9379 | 27.2695 | 26.6 | 25.9305 | 25.2684 | 23.8979 | 23.3253 | 22.7042
|  | WOKINGHAM PRIMARY | HT |  |  |  |  | 31.1984 | 31.0511 | 30.8511 | 30.6089 | 30.0984 | 29.3763 | 28.6911 | 27.9974 | 27.2911 | 25.57 | 24.7774 | 23.9426 | 28.3432 | 28.0611 | 27.6116 | 27.1789 | 26.4726 | 25.6379 | 24.8495 | 24.0484 | 23.2316 | 21.2232 | 20.3232 | 19.3579 | 29.6116 | 29.3337 | 28.8916 | 28.4653 | 27.7705 | 26.9379 | 26.1516 | 25.3516 | 24.5358 | 22.5316 | 21.6347 | 20.6705
|  | WOKINGHAM PRIMARY | HE |  |  |  |  | 31.2342 | 31.0942 | 30.93 | 30.7174 | 30.4132 | 30.0679 | 29.5311 | 28.9921 | 28.4584 | 27.7205 | 27.4837 | 27.1732 | 28.4916 | 28.2779 | 27.9495 | 27.6726 | 27.1084 | 26.4863 | 25.8747 | 25.2632 | 24.6558 | 23.7147 | 23.4232 | 23.0358 | 29.6632 | 29.5242 | 29.2221 | 28.9474 | 28.3905 | 27.78 | 27.1747 | 26.5642 | 25.9579 | 25.02 | 24.7284 | 24.3421
|  | WOKINGHAM PRIMARY | FB |  |  |  |  | 31.3542 | 31.2847 | 31.2216 | 31.1542 | 31.0732 | 30.9889 | 30.9047 | 30.7847 | 30.5332 | 29.7047 | 29.3342 | 28.9711 | 28.6884 | 28.5453 | 28.3789 | 28.2516 | 28.0284 | 27.7632 | 27.4874 | 27.2063 | 26.9063 | 25.9232 | 25.4916 | 25.0537 | 29.7811 | 29.7137 | 29.6463 | 29.5211 | 29.3032 | 29.0442 | 28.7737 | 28.4989 | 28.2063 | 27.2242 | 26.7937 | 26.3579
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | WOODCOTE PRIMARY | MINIMUM HEADROOM | SU 64425 81624 | YES | YES | 0.82105 | 8.8474 | 8.8116 | 8.7684 | 8.7095 | 8.64 | 8.5642 | 8.4895 | 8.4158 | 8.3432 | 8.0411 | 7.8505 | 7.6411 | 7.32 | 7.2453 | 7.1653 | 7.0695 | 6.9421 | 6.8179 | 6.7116 | 6.5989 | 6.4884 | 6.1232 | 5.8937 | 5.6305 | 7.7884 | 7.7137 | 7.6347 | 7.5411 | 7.4147 | 7.2926 | 7.1863 | 7.0758 | 6.9663 | 6.6063 | 6.3811 | 6.1232
|  | WOODCOTE PRIMARY | EE |  |  |  |  | 8.8474 | 8.8116 | 8.7705 | 8.7147 | 8.6432 | 8.5716 | 8.5053 | 8.4389 | 8.3726 | 8.2537 | 8.1411 | 8.0389 | 7.32 | 7.2453 | 7.1653 | 7.0737 | 6.9705 | 6.8695 | 6.7663 | 6.6642 | 6.5632 | 6.3621 | 6.2168 | 6.0832 | 7.7884 | 7.7137 | 7.6347 | 7.5442 | 7.4432 | 7.3421 | 7.24 | 7.1389 | 7.0389 | 6.8432 | 6.7011 | 6.5695
|  | WOODCOTE PRIMARY | HT |  |  |  |  | 8.8484 | 8.8137 | 8.7684 | 8.7095 | 8.64 | 8.5642 | 8.4895 | 8.4158 | 8.3432 | 8.0411 | 7.8505 | 7.6411 | 7.3253 | 7.2505 | 7.1663 | 7.0695 | 6.9421 | 6.8179 | 6.7116 | 6.5989 | 6.4884 | 6.1232 | 5.8937 | 5.6305 | 7.7926 | 7.7189 | 7.6358 | 7.5411 | 7.4147 | 7.2926 | 7.1863 | 7.0758 | 6.9663 | 6.6063 | 6.3811 | 6.1232
|  | WOODCOTE PRIMARY | HE |  |  |  |  | 8.8558 | 8.8211 | 8.7842 | 8.7326 | 8.6611 | 8.5947 | 8.5284 | 8.4632 | 8.3989 | 8.4063 | 8.3979 | 8.3884 | 7.3737 | 7.3179 | 7.2568 | 7.1832 | 7.0937 | 7.0053 | 6.9189 | 6.8326 | 6.7495 | 6.6779 | 6.5979 | 6.5295 | 7.84 | 7.7853 | 7.7253 | 7.6516 | 7.5632 | 7.4747 | 7.3895 | 7.3032 | 7.2211 | 7.1516 | 7.0737 | 7.0074
|  | WOODCOTE PRIMARY | FB |  |  |  |  | 8.8832 | 8.8684 | 8.8547 | 8.8389 | 8.8211 | 8.8042 | 8.7874 | 8.7716 | 8.7547 | 8.6926 | 8.6589 | 8.6379 | 7.4221 | 7.3811 | 7.3495 | 7.3158 | 7.2789 | 7.2442 | 7.2084 | 7.1737 | 7.1379 | 6.9937 | 6.8779 | 6.7842 | 7.8874 | 7.8474 | 7.8168 | 7.7832 | 7.7474 | 7.7126 | 7.6779 | 7.6442 | 7.6084 | 7.4663 | 7.3526 | 7.2621
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WOODMILL LANE PRIMARY | MINIMUM HEADROOM | SU 43733 15470 | NO | YES | 0 | 24.7866 | 24.6508 | 24.4824 | 24.234 | 23.9192 | 23.6698 | 23.3982 | 23.0877 | 22.6666 | 20.9887 | 19.8887 | 18.9035 | 24.2582 | 24.0761 | 23.8161 | 23.4403 | 22.9487 | 22.654 | 22.3066 | 21.8519 | 21.3245 | 19.795 | 18.5645 | 17.4529 | 23.1224 | 22.9161 | 22.6077 | 22.1645 | 21.5761 | 21.2582 | 20.8698 | 20.3382 | 19.7108 | 18.0213 | 16.9129 | 15.9203
|  | WOODMILL LANE PRIMARY | EE |  |  |  |  | 24.7866 | 24.6508 | 24.5035 | 24.3182 | 24.0582 | 23.8066 | 23.5635 | 23.3298 | 23.0982 | 22.7519 | 22.1182 | 21.4298 | 24.2582 | 24.0761 | 23.8792 | 23.6498 | 23.335 | 23.0192 | 22.6929 | 22.4066 | 22.1266 | 21.4971 | 20.8213 | 20.1982 | 23.1224 | 22.9161 | 22.6919 | 22.4392 | 22.0971 | 21.7456 | 21.375 | 21.0613 | 20.755 | 19.974 | 19.1603 | 18.4645
|  | WOODMILL LANE PRIMARY | HT |  |  |  |  | 24.8013 | 24.6708 | 24.4824 | 24.234 | 23.9192 | 23.6698 | 23.3982 | 23.0877 | 22.6666 | 20.9887 | 19.8887 | 18.9035 | 24.2803 | 24.0971 | 23.8161 | 23.4403 | 22.9487 | 22.654 | 22.3066 | 21.8519 | 21.3245 | 19.795 | 18.5645 | 17.4529 | 23.1498 | 22.9392 | 22.6077 | 22.1645 | 21.5761 | 21.2582 | 20.8698 | 20.3382 | 19.7108 | 18.0213 | 16.9129 | 15.9203
|  | WOODMILL LANE PRIMARY | HE |  |  |  |  | 24.8403 | 24.7182 | 24.5824 | 24.4024 | 24.1413 | 23.9024 | 23.6635 | 23.4413 | 23.2235 | 23.1529 | 22.974 | 22.8108 | 24.3613 | 24.215 | 24.0487 | 23.8403 | 23.5361 | 23.2435 | 22.9445 | 22.694 | 22.4519 | 22.2477 | 21.8645 | 21.4992 | 23.254 | 23.095 | 22.9108 | 22.6877 | 22.3603 | 22.0392 | 21.7087 | 21.4424 | 21.1866 | 20.9119 | 20.4203 | 19.9456
|  | WOODMILL LANE PRIMARY | FB |  |  |  |  | 24.9277 | 24.8519 | 24.7866 | 24.7161 | 24.635 | 24.5529 | 24.4687 | 24.3887 | 24.3119 | 24.014 | 23.7856 | 23.5919 | 24.4719 | 24.3656 | 24.2771 | 24.1856 | 24.0771 | 23.9656 | 23.8456 | 23.7287 | 23.6298 | 23.2192 | 22.834 | 22.4635 | 23.3761 | 23.254 | 23.154 | 23.0498 | 22.9277 | 22.7992 | 22.6603 | 22.5245 | 22.4129 | 21.9424 | 21.4729 | 21.0077
COWLEY GSP | YARNTON BSP | WOODSTOCK PRIMARY | MINIMUM HEADROOM | SP 44795 17462 | NO | YES | 0.012632 | 14.3066 | 14.1192 | 13.7382 | 13.2013 | 12.6097 | 11.6782 | 10.7992 | 10.0234 | 9.2466 | 7.7971 | 7.1434 | 6.455 | 13.8089 | 13.6089 | 13.1911 | 12.5732 | 11.8868 | 10.7911 | 9.7763 | 8.8837 | 7.9921 | 6.3458 | 5.6132 | 4.8342 | 13.2263 | 13.0147 | 12.5726 | 11.9484 | 11.2632 | 10.1695 | 9.1568 | 8.2663 | 7.3758 | 5.7316 | 4.9989 | 4.2221
|  | WOODSTOCK PRIMARY | EE |  |  |  |  | 14.3308 | 14.1434 | 13.8287 | 13.3929 | 12.8708 | 12.3634 | 11.9013 | 11.2466 | 10.5876 | 8.9455 | 8.5234 | 8.1034 | 13.8374 | 13.6363 | 13.2932 | 12.8037 | 12.2026 | 11.6184 | 11.0847 | 10.3258 | 9.5679 | 7.6479 | 7.1679 | 6.6879 | 13.2579 | 13.0463 | 12.6832 | 12.1789 | 11.5789 | 10.9958 | 10.4621 | 9.7032 | 8.9463 | 7.0295 | 6.5495 | 6.0695
|  | WOODSTOCK PRIMARY | HT |  |  |  |  | 14.3066 | 14.1192 | 13.7382 | 13.2013 | 12.6097 | 11.6782 | 10.7992 | 10.0234 | 9.2466 | 7.7971 | 7.1434 | 6.455 | 13.8089 | 13.6089 | 13.1911 | 12.5732 | 11.8868 | 10.7911 | 9.7763 | 8.8837 | 7.9921 | 6.3458 | 5.6132 | 4.8342 | 13.2263 | 13.0147 | 12.5726 | 11.9484 | 11.2632 | 10.1695 | 9.1568 | 8.2663 | 7.3758 | 5.7316 | 4.9989 | 4.2221
|  | WOODSTOCK PRIMARY | HE |  |  |  |  | 14.4255 | 14.2761 | 13.9897 | 13.5803 | 13.0771 | 12.5918 | 12.155 | 11.6203 | 11.0887 | 9.5192 | 9.2445 | 8.9571 | 13.9416 | 13.7816 | 13.4689 | 13.0216 | 12.4437 | 11.8837 | 11.3816 | 10.7616 | 10.1511 | 8.2932 | 7.9753 | 7.6405 | 13.3674 | 13.2011 | 12.8705 | 12.3979 | 11.82 | 11.2611 | 10.76 | 10.1411 | 9.5316 | 7.6768 | 7.3589 | 7.0242
|  | WOODSTOCK PRIMARY | FB |  |  |  |  | 14.5603 | 14.4624 | 14.3266 | 14.1476 | 13.955 | 13.7413 | 13.535 | 13.3855 | 13.0992 | 11.9497 | 11.5245 | 11.2497 | 14.0868 | 13.9805 | 13.8332 | 13.6363 | 13.4237 | 13.1879 | 12.9511 | 12.7774 | 12.4395 | 11.0795 | 10.5858 | 10.27 | 13.5211 | 13.4084 | 13.2516 | 13.0432 | 12.8179 | 12.5674 | 12.3274 | 12.1537 | 11.8158 | 10.4579 | 9.9653 | 9.6505
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON PRIMARY | MINIMUM HEADROOM | SU 44145 11242 | NO | YES | 0 | 32.9411 | 32.8684 | 32.7832 | 32.6632 | 32.42 | 32.1611 | 31.8716 | 31.5389 | 31.1947 | 30.2568 | 29.6484 | 29.1095 | 29.6874 | 29.5516 | 29.3589 | 29.0874 | 28.6379 | 28.3042 | 27.9179 | 27.4621 | 26.9874 | 25.9147 | 25.2337 | 24.6295 | 32.5347 | 32.4695 | 32.3789 | 32.1074 | 31.6589 | 31.3253 | 30.94 | 30.4853 | 30.0105 | 28.9411 | 28.26 | 27.6579
|  | WOOLSTON PRIMARY | EE |  |  |  |  | 32.9411 | 32.8684 | 32.7863 | 32.6779 | 32.5347 | 32.3863 | 32.1484 | 31.8958 | 31.6663 | 31.1853 | 30.7916 | 30.42 | 29.6874 | 29.5516 | 29.4021 | 29.2326 | 29.0211 | 28.74 | 28.3632 | 28.0326 | 27.7389 | 27.0147 | 26.5168 | 26.0895 | 32.5347 | 32.4695 | 32.3947 | 32.2526 | 32.04 | 31.7589 | 31.3832 | 31.0526 | 30.7611 | 30.0389 | 29.5421 | 29.1147
|  | WOOLSTON PRIMARY | HT |  |  |  |  | 32.9463 | 32.8768 | 32.7832 | 32.6632 | 32.42 | 32.1611 | 31.8716 | 31.5389 | 31.1947 | 30.2568 | 29.6484 | 29.1095 | 29.7063 | 29.5663 | 29.3589 | 29.0874 | 28.6379 | 28.3042 | 27.9179 | 27.4621 | 26.9874 | 25.9147 | 25.2337 | 24.6295 | 32.5389 | 32.4779 | 32.3789 | 32.1074 | 31.6589 | 31.3253 | 30.94 | 30.4853 | 30.0105 | 28.9411 | 28.26 | 27.6579
|  | WOOLSTON PRIMARY | HE |  |  |  |  | 32.9579 | 32.8895 | 32.8084 | 32.7 | 32.5558 | 32.4105 | 32.2579 | 32.0516 | 31.8432 | 31.6063 | 31.4168 | 31.2337 | 29.7768 | 29.6737 | 29.5526 | 29.4053 | 29.2074 | 28.9432 | 28.5895 | 28.2895 | 28.0295 | 27.6411 | 27.3453 | 27.0568 | 32.5442 | 32.4789 | 32.4032 | 32.2989 | 32.1611 | 31.9621 | 31.6095 | 31.3095 | 31.0505 | 30.6632 | 30.3674 | 30.08
|  | WOOLSTON PRIMARY | FB |  |  |  |  | 33.0126 | 32.9747 | 32.9421 | 32.9053 | 32.8642 | 32.8232 | 32.7779 | 32.7337 | 32.6905 | 32.3979 | 32.1832 | 31.9905 | 29.8632 | 29.7821 | 29.7189 | 29.6526 | 29.5747 | 29.4958 | 29.3832 | 29.2474 | 29.14 | 28.5916 | 28.2863 | 28.0032 | 32.5947 | 32.5621 | 32.5326 | 32.4989 | 32.4621 | 32.4253 | 32.3884 | 32.2674 | 32.1589 | 31.6116 | 31.3084 | 31.0253
MINETY GSP | SWINDON BSP | WOOTTON BASSETT PRIMARY | MINIMUM HEADROOM | SU 07587 81123 | NO | YES | 0.15789 | 22.7011 | 22.4147 | 21.1663 | 20.4147 | 19.5168 | 18.6242 | 17.7947 | 17.0726 | 20.8832 | 18.7874 | 18.9621 | 17.5726 | 22.6147 | 22.2926 | 20.7621 | 19.8811 | 18.8126 | 17.7579 | 16.7768 | 15.9337 | 20.4305 | 18.0937 | 19.1 | 17.4495 | 22.7263 | 22.4063 | 20.8926 | 20.0211 | 18.9653 | 17.9232 | 16.9537 | 16.1211 | 20.2116 | 17.5211 | 18.9663 | 17.3158
|  | WOOTTON BASSETT PRIMARY | EE |  |  |  |  | 22.7011 | 22.4147 | 21.1663 | 20.48 | 19.5168 | 18.6242 | 17.7947 | 17.0726 | 20.9758 | 18.7874 | 19.9684 | 19.0021 | 22.6147 | 22.2926 | 20.7621 | 19.9516 | 18.8126 | 17.7579 | 16.7768 | 15.9337 | 20.7832 | 18.0937 | 20.1189 | 18.9411 | 22.7263 | 22.4063 | 20.8926 | 20.0905 | 18.9653 | 17.9232 | 16.9537 | 16.1211 | 20.2116 | 17.5211 | 19.9853 | 18.8074
|  | WOOTTON BASSETT PRIMARY | HT |  |  |  |  | 22.7642 | 22.4979 | 21.2137 | 20.4147 | 26.0221 | 24.92 | 23.8663 | 22.8589 | 22.0074 | 20.5221 | 18.9621 | 17.5726 | 22.6905 | 22.3926 | 20.8242 | 19.8811 | 26.8811 | 25.5758 | 24.3316 | 23.1442 | 22.1526 | 20.9495 | 19.1 | 17.4495 | 22.8011 | 22.5053 | 20.9547 | 20.0211 | 26.3095 | 25.0053 | 23.76 | 22.5716 | 21.58 | 20.8168 | 18.9663 | 17.3158
|  | WOOTTON BASSETT PRIMARY | HE |  |  |  |  | 22.9295 | 22.7305 | 21.5537 | 20.9253 | 20.0063 | 19.1653 | 18.4105 | 17.7632 | 21.7411 | 20.0674 | 21.5663 | 20.8705 | 22.8832 | 22.6653 | 21.2211 | 20.4811 | 19.3958 | 18.4011 | 17.5126 | 16.7632 | 21.7021 | 19.6095 | 22 | 21.1347 | 22.9916 | 22.7747 | 21.3484 | 20.6158 | 19.5411 | 18.5579 | 17.6811 | 16.9389 | 21.1305 | 19.0379 | 21.8663 | 21.0011
|  | WOOTTON BASSETT PRIMARY | FB |  |  |  |  | 23.1105 | 22.9516 | 22.7674 | 22.4895 | 22.14 | 21.7621 | 21.4021 | 21.0958 | 20.8832 | 26.6463 | 25.9305 | 25.3105 | 23.0884 | 22.9063 | 22.6905 | 22.3568 | 21.9368 | 21.4821 | 21.0474 | 20.68 | 20.4305 | 27.6232 | 26.76 | 26.0042 | 23.1958 | 23.0147 | 22.8011 | 22.4716 | 22.0558 | 21.6053 | 21.1758 | 20.8126 | 20.5653 | 27.0526 | 26.1905 | 25.4337
COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD PRIMARY | MINIMUM HEADROOM | SU 49244 98269 | NO | YES | 0 | 17.7647 | 17.5163 | 16.8153 | 16.0005 | 15.3226 | 14.2921 | 13.0889 | 11.8384 | 10.5742 | 5.9616 | 1.8216 | -2.4668 | 10.9768 | 10.3674 | 9.5779 | 8.68 | 7.9537 | 6.8221 | 5.4884 | 4.0979 | 2.6916 | -2.5358 | -7.2737 | -12.2 | 14.1389 | 13.5442 | 12.7705 | 11.8905 | 11.1758 | 10.0674 | 8.7632 | 7.4032 | 6.0284 | 0.93895 | -3.7105 | -8.6558
|  | WOOTTON ROAD PRIMARY | EE |  |  |  |  | 17.7647 | 17.5163 | 16.8689 | 16.1142 | 15.5342 | 14.6911 | 13.7153 | 12.7342 | 11.7626 | 8.4626 | 5.2511 | 1.9479 | 10.9874 | 10.3726 | 9.6411 | 8.8063 | 8.2021 | 7.2821 | 6.2011 | 5.1168 | 4.0442 | 0.23368 | -3.4747 | -7.3021 | 14.1495 | 13.5484 | 12.8316 | 12.0158 | 11.4158 | 10.5137 | 9.4558 | 8.3947 | 7.3432 | 3.6484 | 0.050526 | -3.7442
|  | WOOTTON ROAD PRIMARY | HT |  |  |  |  | 17.7753 | 17.5163 | 16.8153 | 16.0005 | 15.3226 | 14.2921 | 13.0889 | 11.8384 | 10.5742 | 5.9616 | 1.8216 | -2.4668 | 10.9768 | 10.3674 | 9.5779 | 8.68 | 7.9537 | 6.8221 | 5.4884 | 4.0979 | 2.6916 | -2.5358 | -7.2737 | -12.2 | 14.1389 | 13.5442 | 12.7705 | 11.8905 | 11.1758 | 10.0674 | 8.7632 | 7.4032 | 6.0284 | 0.93895 | -3.7105 | -8.6558
|  | WOOTTON ROAD PRIMARY | HE |  |  |  |  | 17.85 | 17.6384 | 17.3595 | 16.6889 | 16.1679 | 15.3984 | 14.4868 | 13.5689 | 12.6647 | 9.9595 | 7.1384 | 4.1679 | 11.3168 | 10.8316 | 10.2095 | 9.4632 | 8.9232 | 8.0842 | 7.0789 | 6.0684 | 5.0716 | 1.9042 | -1.38 | -4.8463 | 14.4705 | 13.9947 | 13.3863 | 12.6547 | 12.1179 | 11.2947 | 10.3105 | 9.32 | 8.3442 | 5.28 | 2.0989 | -1.28
|  | WOOTTON ROAD PRIMARY | FB |  |  |  |  | 18.0047 | 17.8921 | 17.7889 | 17.6742 | 17.5595 | 17.27 | 16.8574 | 16.4289 | 15.9711 | 13.7521 | 11.6311 | 9.5563 | 11.6674 | 11.3389 | 11.0242 | 10.6842 | 10.4674 | 10.0937 | 9.62 | 9.1326 | 8.6147 | 6.0853 | 3.6411 | 1.2379 | 14.8147 | 14.4926 | 14.1853 | 13.8547 | 13.6411 | 13.2747 | 12.8137 | 12.3389 | 11.8347 | 9.3747 | 7.0032 | 4.6726
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | WRECCLESHAM PRIMARY | MINIMUM HEADROOM | SU 82093 44312 | NO | YES | 0 | 34.4347 | 34.2516 | 34.0221 | 33.7179 | 33.2832 | 32.4379 | 31.4916 | 30.5021 | 29.4832 | 25.7568 | 24.5495 | 23.4695 | 31.48 | 31.2147 | 30.6505 | 29.8958 | 29.0295 | 28.0337 | 26.9663 | 25.8463 | 24.6905 | 20.3695 | 19.0105 | 17.7958 | 29.0232 | 28.6716 | 28.0916 | 27.3347 | 26.4653 | 25.4663 | 24.3958 | 23.2726 | 22.1126 | 17.7779 | 16.4158 | 15.1968
|  | WRECCLESHAM PRIMARY | EE |  |  |  |  | 34.4347 | 34.2516 | 34.0463 | 33.78 | 33.4211 | 33.0832 | 32.7663 | 32.4368 | 32.0884 | 30.56 | 29.7347 | 29.0337 | 31.48 | 31.2147 | 30.8347 | 30.3947 | 29.8042 | 29.3611 | 28.9158 | 28.4568 | 27.9758 | 25.9968 | 25.0411 | 24.2253 | 29.0232 | 28.6768 | 28.2758 | 27.8337 | 27.2442 | 26.8011 | 26.3547 | 25.8958 | 25.4137 | 23.4253 | 22.4674 | 21.6484
|  | WRECCLESHAM PRIMARY | HT |  |  |  |  | 34.4421 | 34.2632 | 34.0221 | 33.7179 | 33.2832 | 32.4379 | 31.4916 | 30.5021 | 29.4832 | 25.7568 | 24.5495 | 23.4695 | 31.5105 | 31.2179 | 30.6505 | 29.8958 | 29.0295 | 28.0337 | 26.9663 | 25.8463 | 24.6905 | 20.3695 | 19.0105 | 17.7958 | 29.0789 | 28.6716 | 28.0916 | 27.3347 | 26.4653 | 25.4663 | 24.3958 | 23.2726 | 22.1126 | 17.7779 | 16.4158 | 15.1968
|  | WRECCLESHAM PRIMARY | HE |  |  |  |  | 34.4884 | 34.3274 | 34.1368 | 33.8863 | 33.5411 | 33.2253 | 32.92 | 32.6053 | 32.2979 | 31.7621 | 31.2474 | 30.8053 | 31.6295 | 31.4253 | 31.1695 | 30.86 | 30.3516 | 29.9684 | 29.6032 | 29.2158 | 28.8095 | 27.3737 | 26.7632 | 26.2368 | 29.2695 | 29.0221 | 28.7011 | 28.3316 | 27.7937 | 27.4095 | 27.0442 | 26.6568 | 26.2505 | 24.8074 | 24.1947 | 23.6663
|  | WRECCLESHAM PRIMARY | FB |  |  |  |  | 34.6211 | 34.5411 | 34.4684 | 34.3884 | 34.2958 | 34.2063 | 34.1221 | 34.0421 | 33.9568 | 33.6284 | 33.3853 | 33.0347 | 31.8032 | 31.6695 | 31.5505 | 31.4337 | 31.2789 | 31.1547 | 31.0063 | 30.8579 | 30.6853 | 29.9295 | 29.2611 | 28.6874 | 29.4842 | 29.2968 | 29.1316 | 28.9779 | 28.76 | 28.6011 | 28.4484 | 28.3 | 28.1274 | 27.3695 | 26.6979 | 26.1221
MINETY GSP | TOOTHILL BSP | WROUGHTON PRIMARY | MINIMUM HEADROOM | SU 14446 81504 | NO | YES | 0 | 25.414 | 24.2729 | 23.9645 | 23.5203 | 23.0856 | 22.6456 | 22.1192 | 21.5329 | 21.0003 | 18.034 | 17.4982 | 16.9813 | 22.494 | 21.2887 | 20.9677 | 20.5035 | 20.0529 | 19.5961 | 19.0487 | 18.4361 | 17.8813 | 14.7361 | 14.174 | 13.6319 | 23.7077 | 22.3813 | 22.035 | 21.5329 | 21.0529 | 20.5656 | 19.9771 | 19.3171 | 18.7203 | 15.2371 | 14.6266 | 14.034
|  | WROUGHTON PRIMARY | EE |  |  |  |  | 25.414 | 24.2729 | 23.9645 | 23.5203 | 23.1519 | 22.8213 | 22.4182 | 21.9835 | 21.5445 | 18.034 | 17.4982 | 16.9813 | 22.494 | 21.2887 | 20.9677 | 20.5035 | 20.1213 | 19.7803 | 19.3592 | 18.9077 | 18.4508 | 14.7361 | 14.174 | 13.6319 | 23.7077 | 22.3813 | 22.035 | 21.5329 | 21.1256 | 20.7635 | 20.3129 | 19.8266 | 19.335 | 15.2371 | 14.6266 | 14.034
|  | WROUGHTON PRIMARY | HT |  |  |  |  | 25.4487 | 24.3182 | 24.0024 | 23.5477 | 23.0856 | 22.6456 | 22.1192 | 21.5329 | 21.0003 | 18.6129 | 17.8435 | 17.0866 | 22.5308 | 21.3371 | 21.0077 | 20.5329 | 20.0529 | 19.5961 | 19.0487 | 18.4361 | 17.8813 | 15.3729 | 14.5708 | 13.7813 | 23.7477 | 22.4329 | 22.0803 | 21.5677 | 21.0529 | 20.5656 | 19.9771 | 19.3171 | 18.7203 | 15.9835 | 15.1203 | 14.2677
|  | WROUGHTON PRIMARY | HE |  |  |  |  | 25.5392 | 24.4477 | 24.1782 | 23.7677 | 23.4256 | 23.114 | 22.7329 | 22.315 | 21.8929 | 18.6456 | 18.2603 | 17.874 | 22.6256 | 21.4708 | 21.1908 | 20.7613 | 20.4077 | 20.0845 | 19.6877 | 19.2529 | 18.814 | 15.3719 | 14.9666 | 14.5582 | 23.8487 | 22.5782 | 22.2761 | 21.8108 | 21.435 | 21.0919 | 20.6666 | 20.1992 | 19.7277 | 15.9203 | 15.4761 | 15.0256
|  | WROUGHTON PRIMARY | FB |  |  |  |  | 26.2056 | 25.7971 | 25.6824 | 25.5782 | 25.3782 | 25.3045 | 25.1708 | 25.0235 | 24.8719 | 23.9119 | 23.535 | 23.2045 | 23.3287 | 22.8982 | 22.7782 | 22.6698 | 22.4603 | 22.3845 | 22.2456 | 22.0908 | 21.9329 | 20.9224 | 20.5287 | 20.1813 | 24.6235 | 24.1498 | 24.0203 | 23.9035 | 23.6771 | 23.5971 | 23.4477 | 23.2803 | 23.1098 | 22.0066 | 21.5782 | 21.1992
AMERSHAM GSP | LOUDWATER BSP | WYCOMBE MARSH PRIMARY | MINIMUM HEADROOM | SU 88582 91845 | NO | YES | 0 | 19.0779 | 18.9558 | 18.8147 | 18.6232 | 18.3768 | 18.1274 | 17.8747 | 17.6211 | 17.3695 | 16.7611 | 16.3842 | 15.7695 | 27.4758 | 27.0042 | 26.6768 | 26.2411 | 25.6863 | 25.0695 | 24.4337 | 23.7768 | 23.1221 | 21.5895 | 20.5895 | 19.7021 | -24.1811 | -24.6389 | -24.9589 | -25.3853 | -25.9284 | -26.5316 | -27.1516 | -27.7926 | -28.4316 | -29.9274 | -30.9021 | -31.7674
|  | WYCOMBE MARSH PRIMARY | EE |  |  |  |  | 19.0779 | 18.9558 | 18.8147 | 18.6263 | 18.3768 | 18.1274 | 17.8895 | 17.6484 | 17.4116 | 17.2368 | 17.0895 | 16.9737 | 27.4758 | 27.0042 | 26.6768 | 26.38 | 26.0432 | 25.7105 | 25.3505 | 24.9811 | 24.6179 | 23.8453 | 23.1505 | 22.56 | -24.1811 | -24.6389 | -24.9589 | -25.2526 | -25.5853 | -25.9147 | -26.2695 | -26.6347 | -26.9926 | -27.7421 | -28.4147 | -28.9863
|  | WYCOMBE MARSH PRIMARY | HT |  |  |  |  | 19.0842 | 18.9695 | 18.8168 | 18.6232 | 18.3895 | 18.1316 | 17.8747 | 17.6211 | 17.3695 | 16.7611 | 16.3842 | 15.7695 | 27.5305 | 27.0853 | 26.6916 | 26.2411 | 25.6863 | 25.0695 | 24.4337 | 23.7768 | 23.1221 | 21.5895 | 20.5895 | 19.7021 | -24.1284 | -24.5611 | -24.9442 | -25.3853 | -25.9284 | -26.5316 | -27.1516 | -27.7926 | -28.4316 | -29.9274 | -30.9021 | -31.7674
|  | WYCOMBE MARSH PRIMARY | HE |  |  |  |  | 19.0968 | 18.9737 | 18.8305 | 18.6358 | 18.38 | 18.1316 | 17.8884 | 17.6442 | 17.4053 | 17.4095 | 17.3716 | 17.3453 | 27.6495 | 27.2421 | 26.9674 | 26.7116 | 26.4 | 26.1011 | 25.7863 | 25.4621 | 25.1453 | 24.7737 | 24.3484 | 23.9863 | -24.0137 | -24.4095 | -24.6789 | -24.9326 | -25.2432 | -25.5389 | -25.8516 | -26.1726 | -26.4863 | -26.8421 | -27.2526 | -27.6021
|  | WYCOMBE MARSH PRIMARY | FB |  |  |  |  | 19.1905 | 19.1295 | 19.0737 | 19.0116 | 18.9421 | 18.8726 | 18.8053 | 18.7421 | 18.6747 | 18.4274 | 18.2895 | 18.2011 | 27.9305 | 27.6779 | 27.5358 | 27.4137 | 27.2853 | 27.1589 | 27.0274 | 26.8937 | 26.7568 | 26.1642 | 25.6653 | 25.2463 | -23.7411 | -23.9853 | -24.1242 | -24.2432 | -24.3695 | -24.4937 | -24.6232 | -24.7537 | -24.8884 | -25.4663 | -25.9516 | -26.3568
LOVEDEAN GSP | WYMERING BSP | WYMERING PRIMARY | MINIMUM HEADROOM | SU 64974 05375 | NO | YES | 0.063158 | 65.7637 | 65.6353 | 65.5226 | 65.4026 | 65.2584 | 74.4321 | 73.3142 | 72.1458 | 70.9784 | 66.3826 | 64.3574 | 62.6374 | 62.7389 | 62.5242 | 62.3526 | 62.1874 | 61.9537 | 73.7842 | 73.3632 | 72.4842 | 71.3168 | 66.8537 | 64.8284 | 62.9747 | 67.1558 | 67.0358 | 66.9305 | 66.8158 | 66.6811 | 75.8589 | 75.3505 | 74.0379 | 72.7189 | 67.4768 | 65.1716 | 63.2147
|  | WYMERING PRIMARY | EE |  |  |  |  | 76.4847 | 76.2374 | 75.9679 | 75.6142 | 75.1447 | 74.67 | 74.2174 | 73.3616 | 72.4879 | 68.9458 | 67.5911 | 66.4184 | 75.4126 | 75.2011 | 74.9642 | 74.6432 | 74.2053 | 73.7842 | 73.3916 | 72.9874 | 72.5884 | 69.3168 | 68.0611 | 66.8884 | 77.4874 | 77.2747 | 77.0389 | 76.7179 | 76.28 | 75.8589 | 75.4663 | 75.0621 | 74.5137 | 70.3379 | 68.8284 | 67.4621
|  | WYMERING PRIMARY | HT |  |  |  |  | 76.5079 | 76.2763 | 75.9795 | 75.5963 | 75.1258 | 74.4321 | 73.3142 | 72.1458 | 70.9784 | 66.3826 | 64.3574 | 62.6374 | 75.4284 | 75.2316 | 74.9747 | 74.6442 | 74.2432 | 73.8021 | 73.3632 | 72.4842 | 71.3168 | 66.8537 | 64.8284 | 62.9747 | 77.5032 | 77.3063 | 77.0484 | 76.7189 | 76.3179 | 75.8768 | 75.3505 | 74.0379 | 72.7189 | 67.4768 | 65.1716 | 63.2147
|  | WYMERING PRIMARY | HE |  |  |  |  | 76.5532 | 76.3216 | 76.0647 | 75.7205 | 75.25 | 74.8047 | 74.3658 | 73.9216 | 73.4858 | 70.7279 | 70.0153 | 69.2826 | 75.4537 | 75.2474 | 75.0126 | 74.6926 | 74.2484 | 73.84 | 73.4379 | 73.0295 | 72.6284 | 71.0663 | 70.3526 | 69.62 | 77.5284 | 77.3221 | 77.0874 | 76.7674 | 76.3232 | 75.9147 | 75.5126 | 75.1042 | 74.7032 | 72.3842 | 71.54 | 70.6674
|  | WYMERING PRIMARY | FB |  |  |  |  | 65.7637 | 65.6353 | 65.5226 | 65.4026 | 65.2584 | 76.0826 | 75.9405 | 75.8037 | 75.6605 | 75.1111 | 73.3321 | 72.5374 | 62.7389 | 62.5242 | 62.3526 | 62.1874 | 61.9537 | 75.0432 | 74.9242 | 74.8126 | 74.6947 | 74.2589 | 73.6705 | 72.8747 | 67.1558 | 67.0358 | 66.9305 | 66.8158 | 66.6811 | 77.1179 | 76.9989 | 76.8874 | 76.7695 | 76.3337 | 75.2442 | 74.3179
COWLEY GSP | YARNTON BSP | YARNTON PRIMARY | MINIMUM HEADROOM | SP 48277 12108 | NO | YES | 0 | 32.4147 | 30.0147 | 28.2526 | 26.1221 | 22.8116 | 20.1589 | 17.5253 | 15.3053 | 13.6895 | -1.6663 | -12.7168 | -18.6337 | 29.3126 | 26.5232 | 24.4958 | 22.0484 | 18.2232 | 15.18 | 12.1589 | 9.6221 | 7.7989 | -9.9832 | -22.8874 | -29.8789 | 30.5316 | 27.7484 | 25.7274 | 23.2853 | 19.4716 | 16.4358 | 13.4221 | 10.8926 | 9.0726 | -8.6 | -21.4663 | -28.4947
|  | YARNTON PRIMARY | EE |  |  |  |  | 32.7842 | 31.9916 | 28.4968 | 26.5389 | 23.7253 | 21.7263 | 19.7179 | 17.6989 | 16.0811 | 7.7853 | 3.8305 | -1.1305 | 29.7516 | 28.8579 | 24.7821 | 22.5326 | 19.2989 | 17.0189 | 14.7189 | 12.4126 | 10.5758 | 0.97895 | -3.6263 | -9.4337 | 30.9684 | 30.0758 | 26.0116 | 23.7695 | 20.5442 | 18.2695 | 15.9747 | 13.6737 | 11.8411 | 2.3305 | -2.2611 | -8.0495
|  | YARNTON PRIMARY | HT |  |  |  |  | 32.4147 | 30.0147 | 28.2526 | 26.1221 | 22.8116 | 20.1589 | 17.5253 | 15.3053 | 13.6895 | -1.6663 | -12.7168 | -18.6337 | 29.3126 | 26.5232 | 24.4958 | 22.0484 | 18.2232 | 15.18 | 12.1589 | 9.6221 | 7.7989 | -9.9832 | -22.8874 | -29.8789 | 30.5316 | 27.7484 | 25.7274 | 23.2853 | 19.4716 | 16.4358 | 13.4221 | 10.8926 | 9.0726 | -8.6 | -21.4663 | -28.4947
|  | YARNTON PRIMARY | HE |  |  |  |  | 33.0989 | 32.4274 | 29.0295 | 27.1589 | 24.4063 | 22.4758 | 20.5474 | 18.6305 | 17.1084 | 9.2821 | 5.7589 | 1.2095 | 30.1084 | 29.3526 | 25.3895 | 23.2411 | 20.0768 | 17.8716 | 15.6684 | 13.4789 | 11.7547 | 2.5316 | -1.6032 | -6.9526 | 31.3242 | 30.5705 | 26.6189 | 24.4758 | 21.32 | 19.12 | 16.9221 | 14.7379 | 13.0189 | 3.8232 | -0.29895 | -5.6326
|  | YARNTON PRIMARY | FB |  |  |  |  | 33.7211 | 33.3147 | 32.6189 | 31.0368 | 30.0011 | 29.2053 | 28.3179 | 27.58 | 26.7916 | 22.6432 | 18.8516 | 14.6284 | 30.8158 | 30.3547 | 29.5526 | 27.7063 | 26.5063 | 25.5895 | 24.5642 | 23.7126 | 22.8042 | 17.9895 | 13.5632 | 8.6126 | 32.0305 | 31.5705 | 30.7695 | 28.9295 | 27.7326 | 26.8189 | 25.7947 | 24.9463 | 24.04 | 19.2389 | 14.8253 | 9.8895
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | YATTENDON PRIMARY | MINIMUM HEADROOM | SU 53699 74307 | NO | YES | 0 | 14.3526 | 14.1884 | 13.9347 | 13.5253 | 13.0621 | 12.5695 | 12.0558 | 11.6316 | 11.1895 | 10.3042 | 9.7347 | 9.1558 | 14.2611 | 14.0832 | 13.8011 | 13.3421 | 12.8253 | 12.2758 | 11.7021 | 11.2326 | 10.7411 | 9.7663 | 9.1379 | 8.4905 | 14.2632 | 14.0853 | 13.8042 | 13.3463 | 12.8305 | 12.2821 | 11.7095 | 11.24 | 10.7505 | 9.7768 | 9.1495 | 8.5042
|  | YATTENDON PRIMARY | EE |  |  |  |  | 14.3526 | 14.1884 | 13.96 | 13.6958 | 13.3747 | 13.0684 | 12.7305 | 12.52 | 12.3116 | 11.9537 | 11.5653 | 11.1863 | 14.2611 | 14.0832 | 13.8305 | 13.5411 | 13.1947 | 12.8621 | 12.4905 | 12.2695 | 12.0516 | 11.6474 | 11.2063 | 10.7726 | 14.2632 | 14.0853 | 13.8337 | 13.5442 | 13.1989 | 12.8663 | 12.4958 | 12.2737 | 12.0558 | 11.6537 | 11.2137 | 10.7811
|  | YATTENDON PRIMARY | HT |  |  |  |  | 14.3821 | 14.2337 | 13.9347 | 13.5253 | 13.0621 | 12.5695 | 12.0558 | 11.6316 | 11.1895 | 10.3042 | 9.7347 | 9.1558 | 14.2958 | 14.1358 | 13.8011 | 13.3421 | 12.8253 | 12.2758 | 11.7021 | 11.2326 | 10.7411 | 9.7663 | 9.1379 | 8.4905 | 14.2979 | 14.1379 | 13.8042 | 13.3463 | 12.8305 | 12.2821 | 11.7095 | 11.24 | 10.7505 | 9.7768 | 9.1495 | 8.5042
|  | YATTENDON PRIMARY | HE |  |  |  |  | 14.4589 | 14.3379 | 14.1463 | 13.9116 | 13.6147 | 13.3337 | 13.0295 | 12.8484 | 12.6726 | 12.5705 | 12.3411 | 12.0958 | 14.3832 | 14.2547 | 14.0453 | 13.7895 | 13.4695 | 13.1663 | 12.8347 | 12.6484 | 12.4663 | 12.3432 | 12.0779 | 11.7916 | 14.3853 | 14.2568 | 14.0474 | 13.7926 | 13.4726 | 13.1695 | 12.8389 | 12.6526 | 12.4705 | 12.3474 | 12.0832 | 11.7979
|  | YATTENDON PRIMARY | FB |  |  |  |  | 14.5747 | 14.4863 | 14.3926 | 14.2895 | 14.1768 | 14.0611 | 13.9274 | 13.8579 | 13.7874 | 13.5 | 13.2221 | 12.9611 | 14.5084 | 14.4116 | 14.3063 | 14.1916 | 14.0663 | 13.9379 | 13.7874 | 13.7116 | 13.6358 | 13.3232 | 13.0105 | 12.7116 | 14.5095 | 14.4126 | 14.3084 | 14.1937 | 14.0684 | 13.94 | 13.7895 | 13.7147 | 13.6389 | 13.3274 | 13.0147 | 12.7158
MELKSHAM GSP | CHIPPENHAM BSP | YATTON KEYNELL PRIMARY | MINIMUM HEADROOM | ST 87300 75782 | YES | YES | 0 | 4.6695 | 4.5863 | 4.5021 | 4.4042 | 4.28 | 4.1389 | 3.9958 | 3.8379 | 3.6789 | 3.2284 | 2.8811 | 2.5747 | 4.6232 | 4.5326 | 4.4421 | 4.3389 | 4.2084 | 4.0589 | 3.9074 | 3.7368 | 3.5653 | 3.0705 | 2.6832 | 2.3421 | 4.6242 | 4.5337 | 4.4432 | 4.3411 | 4.2095 | 4.0611 | 3.9095 | 3.7389 | 3.5674 | 3.0737 | 2.6874 | 2.3463
|  | YATTON KEYNELL PRIMARY | EE |  |  |  |  | 4.6695 | 4.5863 | 4.5021 | 4.4042 | 4.2853 | 4.1726 | 4.06 | 3.9453 | 3.8305 | 3.5863 | 3.3368 | 3.1337 | 4.6232 | 4.5326 | 4.4421 | 4.3389 | 4.2147 | 4.0979 | 3.9779 | 3.8568 | 3.7368 | 3.4589 | 3.1747 | 2.9432 | 4.6242 | 4.5337 | 4.4432 | 4.3411 | 4.2158 | 4.0989 | 3.98 | 3.8589 | 3.7389 | 3.4611 | 3.1768 | 2.9453
|  | YATTON KEYNELL PRIMARY | HT |  |  |  |  | 4.6874 | 4.6116 | 4.5189 | 4.4063 | 4.28 | 4.1389 | 3.9958 | 3.8379 | 3.6789 | 3.2284 | 2.8811 | 2.5747 | 4.6432 | 4.5621 | 4.4632 | 4.3432 | 4.2084 | 4.0589 | 3.9074 | 3.7368 | 3.5653 | 3.0705 | 2.6832 | 2.3421 | 4.6442 | 4.5632 | 4.4642 | 4.3442 | 4.2095 | 4.0611 | 3.9095 | 3.7389 | 3.5674 | 3.0737 | 2.6874 | 2.3463
|  | YATTON KEYNELL PRIMARY | HE |  |  |  |  | 4.7316 | 4.6684 | 4.6053 | 4.5253 | 4.4168 | 4.32 | 4.2295 | 4.1358 | 4.0474 | 3.9653 | 3.8126 | 3.6916 | 4.6926 | 4.6263 | 4.56 | 4.4768 | 4.3653 | 4.2653 | 4.1726 | 4.0768 | 3.9853 | 3.8884 | 3.7105 | 3.5695 | 4.6937 | 4.6274 | 4.5611 | 4.4779 | 4.3663 | 4.2663 | 4.1737 | 4.0779 | 3.9863 | 3.8895 | 3.7126 | 3.5716
|  | YATTON KEYNELL PRIMARY | FB |  |  |  |  | 4.7811 | 4.7358 | 4.7021 | 4.6653 | 4.6274 | 4.5863 | 4.5495 | 4.5158 | 4.4789 | 4.3168 | 4.1484 | 4.0032 | 4.7463 | 4.6958 | 4.6589 | 4.62 | 4.5789 | 4.5347 | 4.4958 | 4.4589 | 4.4189 | 4.2421 | 4.0516 | 3.8853 | 4.7474 | 4.6968 | 4.66 | 4.6211 | 4.58 | 4.5358 | 4.4968 | 4.46 | 4.42 | 4.2432 | 4.0537 | 3.8874
AXMINSTER GSP | YEOVIL BSP | YEOVIL PRIMARY | MINIMUM HEADROOM | ST 57690 16833 | NO | YES | 0 | 27.2689 | 26.8553 | 26.4174 | 25.7616 | 24.9184 | 24.0153 | 23.0542 | 22.1984 | 21.2816 | 13.5289 | 12.1921 | 4.0921 | 25.4747 | 25.0232 | 24.5453 | 23.8242 | 22.9011 | 21.9011 | 20.8379 | 19.8979 | 18.8674 | 9.7811 | 10.0695 | 0.57579 | 26.3779 | 25.9263 | 25.4495 | 24.7295 | 23.8084 | 22.8105 | 21.7495 | 20.8105 | 19.7821 | 10.7232 | 11.8863 | 2.4084
|  | YEOVIL PRIMARY | EE |  |  |  |  | 27.2689 | 26.8553 | 26.4174 | 25.7616 | 24.9184 | 24.1089 | 23.2868 | 22.2405 | 21.2816 | 13.5289 | 12.1921 | 4.0921 | 25.4747 | 25.0232 | 24.5453 | 23.8242 | 22.9011 | 22.0147 | 21.1042 | 19.9347 | 18.8674 | 9.7811 | 10.0695 | 0.57579 | 26.3779 | 25.9263 | 25.4495 | 24.7295 | 23.8084 | 22.9232 | 22.0147 | 20.8474 | 19.7821 | 10.7232 | 11.8863 | 2.4084
|  | YEOVIL PRIMARY | HT |  |  |  |  | 27.3416 | 26.9605 | 26.5174 | 25.8616 | 25.0626 | 24.0153 | 23.0542 | 22.1984 | 21.2974 | 24.0058 | 12.3026 | 4.5184 | 25.5589 | 25.1411 | 24.6611 | 23.9421 | 23.0653 | 21.9011 | 20.8379 | 19.8979 | 18.9042 | 24.0168 | 10.3747 | 1.3095 | 26.4611 | 26.0442 | 25.5642 | 24.8463 | 23.9716 | 22.8105 | 21.7495 | 20.8105 | 19.82 | 25.8389 | 12.1926 | 3.1358
|  | YEOVIL PRIMARY | HE |  |  |  |  | 27.4932 | 27.1595 | 26.7921 | 26.1889 | 25.3742 | 24.6142 | 23.8721 | 22.9974 | 22.1289 | 14.9984 | 14.0932 | 6.3626 | 25.7326 | 25.3737 | 24.9779 | 24.3189 | 23.4316 | 22.6011 | 21.7884 | 20.8221 | 19.8611 | 11.4558 | 12.2137 | 3.1358 | 26.6347 | 26.2758 | 25.8811 | 25.2232 | 24.3379 | 23.5084 | 22.6979 | 21.7326 | 20.7737 | 12.3937 | 14.0316 | 4.9621
|  | YEOVIL PRIMARY | FB |  |  |  |  | 27.7574 | 27.5353 | 27.3553 | 27.0995 | 26.7963 | 26.4795 | 26.1553 | 25.8247 | 25.3984 | 23.3153 | 17.5847 | 10.7195 | 26.0179 | 25.7716 | 25.5726 | 25.2874 | 24.9474 | 24.5926 | 24.2274 | 23.8537 | 23.3684 | 20.9768 | 14.26 | 6.1937 | 26.92 | 26.6737 | 26.4758 | 26.1905 | 25.8516 | 25.4968 | 25.1326 | 24.76 | 24.2758 | 21.8905 | 15.1937 | 7.1526
AXMINSTER GSP | YEOVIL BSP | YETMINSTER PRIMARY | MINIMUM HEADROOM | ST 60294 10206 | NO | YES | 0.21053 | 11.1368 | 10.9326 | 10.6674 | 10.3 | 10.1 | 9.6284 | 9.1611 | 8.6863 | 8.2137 | -0.40211 | -6.8505 | -15.7463 | 11.0495 | 10.8263 | 10.5347 | 10.1295 | 9.9432 | 9.4242 | 8.9095 | 8.3842 | 7.8611 | -2.2863 | -9.8642 | -20.3284 | 11.0516 | 10.8284 | 10.5379 | 10.1337 | 9.9147 | 9.3968 | 8.8832 | 8.3589 | 7.8368 | -2.28 | -9.8347 | -20.2674
|  | YETMINSTER PRIMARY | EE |  |  |  |  | 11.1368 | 10.9326 | 10.7158 | 10.46 | 10.1463 | 9.8558 | 9.5663 | 9.2779 | 9 | -0.40211 | -6.8505 | -15.7463 | 11.0495 | 10.8263 | 10.5905 | 10.3147 | 9.9821 | 9.6716 | 9.36 | 9.0505 | 8.7526 | -2.2863 | -9.8642 | -20.3284 | 11.0516 | 10.8284 | 10.5926 | 10.3179 | 9.9853 | 9.6758 | 9.3642 | 9.0558 | 8.7568 | -2.28 | -9.8347 | -20.2674
|  | YETMINSTER PRIMARY | HT |  |  |  |  | 11.1621 | 10.9474 | 10.6674 | 10.3 | 10.1 | 9.6284 | 9.1611 | 8.6863 | 8.2137 | 7.0368 | 0.59579 | -7.5916 | 11.0789 | 10.8432 | 10.5347 | 10.1295 | 9.9432 | 9.4242 | 8.9095 | 8.3842 | 7.8611 | 6.5505 | -0.99053 | -10.5937 | 11.08 | 10.8453 | 10.5379 | 10.1337 | 9.9147 | 9.3968 | 8.8832 | 8.3589 | 7.8368 | 6.5284 | -0.98947 | -10.5642
|  | YETMINSTER PRIMARY | HE |  |  |  |  | 11.2505 | 11.0937 | 10.9179 | 10.6968 | 10.4105 | 10.1516 | 9.9011 | 9.6495 | 9.4074 | 0.29789 | -5.9747 | -14.7179 | 11.18 | 11.0116 | 10.8221 | 10.5863 | 10.2842 | 10.0095 | 9.7421 | 9.4768 | 9.22 | -1.4989 | -8.8832 | -19.1811 | 11.1811 | 11.0126 | 10.8242 | 10.5884 | 10.2863 | 10.0116 | 9.7453 | 9.48 | 9.2232 | -1.4947 | -8.8568 | -19.1221
|  | YETMINSTER PRIMARY | FB |  |  |  |  | 11.3789 | 11.28 | 11.1979 | 11.1084 | 11.0126 | 10.9147 | 10.8179 | 10.7221 | 10.6253 | 8.74 | 2.5537 | -5.1316 | 11.3168 | 11.2063 | 11.1158 | 11.0168 | 10.9116 | 10.8042 | 10.6968 | 10.5905 | 10.4842 | 8.2905 | 1.0337 | -8.0105 | 11.3179 | 11.2084 | 11.1168 | 11.0189 | 10.9137 | 10.8063 | 10.7 | 10.5937 | 10.4863 | 8.3 | 1.0326 | -7.9842
IVER 66KV GSP |  | YIEWSLEY PRIMARY | MINIMUM HEADROOM | TQ 05643 80961 | NO | NO | 0.36842 | 58.1968 | 57.4758 | 56.3989 | 54.8779 | 53.0684 | 51.1579 | 49.2463 | 47.2895 | 45.5147 | 40.8032 | 37.7232 | 34.9432 | 57.9474 | 57.1421 | 55.9337 | 54.22 | 52.1832 | 50.0368 | 47.8884 | 45.6853 | 43.7684 | 38.5105 | 35.0442 | 31.9126 | 57.9516 | 57.1495 | 55.9421 | 54.2326 | 52.2011 | 50.0589 | 47.9158 | 45.7168 | 43.8389 | 38.6063 | 35.1484 | 32.0253
|  | YIEWSLEY PRIMARY | EE |  |  |  |  | 58.1968 | 57.5695 | 56.8789 | 56.0347 | 55.08 | 54.0937 | 53.0874 | 52.0695 | 51.0779 | 48.7674 | 46.5684 | 44.66 | 57.9474 | 57.2579 | 56.5011 | 55.5821 | 54.5589 | 53.4979 | 52.4063 | 51.3021 | 50.2316 | 47.6968 | 45.1758 | 42.9842 | 57.9516 | 57.2632 | 56.5084 | 55.5905 | 54.5684 | 53.5095 | 52.42 | 51.3179 | 50.2474 | 47.7695 | 45.2547 | 43.0684
|  | YIEWSLEY PRIMARY | HT |  |  |  |  | 58.2484 | 57.4758 | 56.3989 | 54.8779 | 53.0684 | 51.1579 | 49.2463 | 47.2895 | 45.5147 | 40.8032 | 37.7232 | 34.9432 | 58.0053 | 57.1421 | 55.9337 | 54.22 | 52.1832 | 50.0368 | 47.8884 | 45.6853 | 43.7684 | 38.5105 | 35.0442 | 31.9126 | 58.0105 | 57.1495 | 55.9421 | 54.2326 | 52.2011 | 50.0589 | 47.9158 | 45.7168 | 43.8389 | 38.6063 | 35.1484 | 32.0253
|  | YIEWSLEY PRIMARY | HE |  |  |  |  | 58.5611 | 58.0747 | 57.5116 | 56.7705 | 55.8811 | 54.9842 | 54.1011 | 53.2126 | 52.3474 | 51.1505 | 49.3926 | 48.0874 | 58.3695 | 57.8453 | 57.2358 | 56.4389 | 55.4937 | 54.5337 | 53.5884 | 52.6389 | 51.7147 | 50.4011 | 48.24 | 46.7116 | 58.3737 | 57.8505 | 57.2411 | 56.4463 | 55.5021 | 54.5432 | 53.5989 | 52.6505 | 51.7274 | 50.4674 | 48.2632 | 46.7389
|  | YIEWSLEY PRIMARY | FB |  |  |  |  | 58.94 | 58.5632 | 58.2526 | 57.9011 | 57.5316 | 57.1358 | 56.74 | 56.3453 | 55.9389 | 54.1737 | 52.6895 | 51.4 | 58.7821 | 58.3663 | 58.0263 | 57.64 | 57.2358 | 56.8021 | 56.3663 | 55.9305 | 55.4821 | 53.5158 | 51.8316 | 50.3537 | 58.7853 | 58.3705 | 58.0305 | 57.6453 | 57.2421 | 56.8084 | 56.3737 | 55.9389 | 55.4916 | 53.5295 | 51.8495 | 50.3747
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ZETLAND ROAD PRIMARY | MINIMUM HEADROOM | SU 60592 00043 | NO | YES | 0 | 18.7379 | 18.1674 | 17.5516 | 16.6874 | 16.0811 | 15.0579 | 14.0421 | 13.0432 | 11.98 | 9.2337 | 7.3579 | 5.6453 | 18.5726 | 17.9411 | 17.2589 | 16.3042 | 15.6926 | 14.5716 | 13.4589 | 12.3663 | 11.1968 | 8.1663 | 6.0853 | 4.1821 | 18.5758 | 17.9453 | 17.2653 | 16.3126 | 15.6526 | 14.5337 | 13.4232 | 12.3326 | 11.1653 | 8.1389 | 6.0632 | 4.1642
|  | ZETLAND ROAD PRIMARY | EE |  |  |  |  | 18.7379 | 18.1674 | 17.6179 | 17.0042 | 16.1442 | 15.4789 | 14.7316 | 14.0063 | 13.3779 | 12.4074 | 11.0537 | 9.8842 | 18.5726 | 17.9411 | 17.34 | 16.6768 | 15.7505 | 15.0474 | 14.2432 | 13.4663 | 12.8053 | 11.7526 | 10.2158 | 8.8832 | 18.5758 | 17.9453 | 17.3453 | 16.6832 | 15.7568 | 15.0558 | 14.2537 | 13.4768 | 12.8158 | 11.7168 | 10.1853 | 8.8547
|  | ZETLAND ROAD PRIMARY | HT |  |  |  |  | 18.8021 | 18.2116 | 17.5516 | 16.6874 | 16.0811 | 15.0579 | 14.0421 | 13.0432 | 11.98 | 9.2337 | 7.3579 | 5.6453 | 18.6442 | 17.9863 | 17.2589 | 16.3042 | 15.6926 | 14.5716 | 13.4589 | 12.3663 | 11.1968 | 8.1663 | 6.0853 | 4.1821 | 18.6474 | 17.9905 | 17.2653 | 16.3126 | 15.6526 | 14.5337 | 13.4232 | 12.3326 | 11.1653 | 8.1389 | 6.0632 | 4.1642
|  | ZETLAND ROAD PRIMARY | HE |  |  |  |  | 19.0242 | 18.5579 | 18.0968 | 17.5516 | 16.7337 | 16.1295 | 15.4853 | 14.8663 | 14.3453 | 14.2853 | 13.4968 | 12.8158 | 18.9021 | 18.3937 | 17.8958 | 17.3168 | 16.4389 | 15.8084 | 15.1284 | 14.4779 | 13.9432 | 13.8937 | 12.98 | 12.1863 | 18.9042 | 18.3968 | 17.9 | 17.3211 | 16.4453 | 15.8147 | 15.1358 | 14.4853 | 13.9505 | 13.8537 | 12.9432 | 12.1516
|  | ZETLAND ROAD PRIMARY | FB |  |  |  |  | 19.3253 | 19.0126 | 18.7716 | 18.5158 | 18.2011 | 17.9053 | 17.62 | 17.3547 | 17.1326 | 16.2305 | 15.6495 | 14.8326 | 19.2274 | 18.8811 | 18.6158 | 18.3368 | 17.9905 | 17.6663 | 17.3537 | 17.0642 | 16.8253 | 15.8495 | 15.2379 | 14.3074 | 19.2284 | 18.8832 | 18.6189 | 18.3411 | 17.9947 | 17.6705 | 17.3589 | 17.0695 | 16.8316 | 15.8579 | 15.1979 | 14.2705

## BSP Headroom Demand
Grid Supply Point | Bulk Supply Point |  | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Demand (MVA) | Demand Headroom Winter (MVA) | [11 empty] | Demand Headroom Summer (MVA) | [11 empty] | Demand Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT BSP | MINIMUM HEADROOM | SU 85922 48779 | NO | NO | 36.106 | 75.0048 | 73.8813 | 71.6548 | 68.1629 | 64.4813 | 59.1823 | 53.0456 | 46.5874 | 40.5844 | 20.264 | 8.6476 | 5.4017 | 69.0311 | 67.6447 | 65.4258 | 62.2595 | 58.9237 | 54.4658 | 49.2942 | 43.8447 | 38.7574 | 21.1921 | 6.7195 | -21.8289 | 64.1311 | 63.0679 | 61.1005 | 57.7584 | 53.9953 | 48.9026 | 43.0847 | 36.9753 | 31.3511 | 21.9342 | 11.5415 | 7.2701
|  | ALDERSHOT BSP | EE |  |  |  |  | 75.1038 | 74.3558 | 72.614 | 69.8864 | 67.1252 | 62.9762 | 58.0782 | 52.8282 | 48.1691 | 28.7038 | 15.9017 | 10.6487 | 71.6946 | 70.5405 | 68.668 | 65.9905 | 63.1731 | 59.5027 | 55.2313 | 50.4415 | 46.2782 | 26.3262 | 13.2731 | 3.6793 | 67.5191 | 66.7385 | 65.1731 | 62.5558 | 59.6466 | 55.5895 | 50.9823 | 45.9925 | 41.6231 | 22.9721 | 11.5415 | 7.2701
|  | ALDERSHOT BSP | HT |  |  |  |  | 75.0048 | 73.8813 | 71.6548 | 68.1629 | 64.4813 | 59.1823 | 53.0456 | 46.5874 | 40.5844 | 20.264 | 8.6476 | 5.4017 | 69.0311 | 67.6447 | 65.4258 | 62.2595 | 58.9237 | 54.4658 | 49.2942 | 43.8447 | 38.7574 | 21.1921 | 12.7121 | 10.8911 | 64.1311 | 63.0679 | 61.1005 | 57.7584 | 53.9953 | 48.9026 | 43.0847 | 36.9753 | 31.3511 | 25.2995 | 21.6174 | 18.5542
|  | ALDERSHOT BSP | HE |  |  |  |  | 75.1385 | 74.4344 | 72.7099 | 69.9742 | 67.065 | 63.067 | 58.1007 | 52.9242 | 48.3007 | 32.5354 | 22.4946 | 18.6762 | 69.109 | 67.9395 | 65.9911 | 63.3026 | 60.2763 | 56.6111 | 52.0879 | 47.1711 | 42.8437 | 24.6942 | 12.7732 | 3.0153 | 64.2216 | 63.4574 | 61.8626 | 59.1753 | 55.9984 | 52.01 | 47.1479 | 42.0721 | 37.5774 | 21.9342 | 12.9395 | 9.8858
|  | ALDERSHOT BSP | FB |  |  |  |  | 76.8374 | 76.6231 | 75.9885 | 75.2405 | 74.1119 | 72.5303 | 71.0619 | 69.4129 | 67.5456 | 55.7446 | 40.4344 | 31.2323 | 70.1395 | 69.1163 | 67.8805 | 66.7205 | 64.769 | 62.0416 | 59.27 | 56.2837 | 53.0363 | 33.4005 | 6.7195 | -21.8289 | 65.9563 | 65.6753 | 65.0963 | 64.5932 | 63.6195 | 61.9532 | 60.2563 | 58.2826 | 56.0563 | 43.169 | 27.5784 | 18.21
FLEET-BRAMLEY GSP | ALTON BSP | ALTON BSP | MINIMUM HEADROOM | SU 72730 39772 | NO | NO | 47.692 | 21.1795 | 20.2815 | 18.1295 | 16.1162 | 13.5519 | 9.6132 | 5.1734 | 0.69989 | -3.5562 | -19.3215 | -28.392 | -32.7368 | 35.5378 | 34.3357 | 32.1504 | 30.4936 | 28.4041 | 25.6725 | 22.3694 | 18.9662 | 15.721 | 3.3431 | -1.6075 | -15.1032 | 26.9757 | 25.8525 | 23.4262 | 21.5062 | 19.0652 | 15.6652 | 11.7136 | 7.7052 | 3.8641 | -4.3769 | -10.7172 | -13.8182
|  | ALTON BSP | EE |  |  |  |  | 21.1815 | 20.3142 | 18.3795 | 16.9754 | 15.1887 | 11.9989 | 8.1866 | 4.4295 | 0.89172 | -13.9062 | -22.7083 | -27.142 | 37.194 | 36.1022 | 34.0685 | 32.7358 | 31.1246 | 28.8848 | 25.9971 | 23.096 | 20.3236 | 7.0675 | 0.063396 | -4.7193 | 28.9512 | 27.9226 | 25.7103 | 24.2899 | 22.5563 | 19.8256 | 16.4542 | 13.1185 | 9.9542 | -3.6417 | -10.7172 | -13.8182
|  | ALTON BSP | HT |  |  |  |  | 21.1927 | 20.2815 | 18.1295 | 16.1162 | 13.5519 | 9.6132 | 5.1734 | 0.69989 | -3.5562 | -19.3215 | -28.392 | -32.7368 | 35.5462 | 34.3357 | 32.1504 | 30.4936 | 28.4041 | 25.6725 | 22.3694 | 18.9662 | 15.721 | 3.3431 | -1.6075 | -2.7159 | 26.9841 | 25.8525 | 23.4262 | 21.5062 | 19.0652 | 15.6652 | 11.7136 | 7.7052 | 3.8641 | -0.042189 | -3.9527 | -6.3264
|  | ALTON BSP | HE |  |  |  |  | 21.1795 | 20.2948 | 18.3836 | 16.9621 | 15.1223 | 12.0642 | 8.2183 | 4.3132 | 0.80907 | -11.5726 | -19.0256 | -22.7205 | 35.5378 | 34.3883 | 32.3083 | 30.9547 | 29.2704 | 27.1325 | 24.182 | 21.0652 | 18.2673 | 6.1315 | -0.12535 | -5.2601 | 26.9757 | 25.8968 | 23.6336 | 22.1747 | 20.3452 | 17.6978 | 14.2336 | 10.6589 | 7.4389 | -4.3769 | -10.3485 | -13.1411
|  | ALTON BSP | FB |  |  |  |  | 21.9325 | 21.4672 | 20.5948 | 20.6478 | 20.1683 | 19.4019 | 18.3642 | 17.0591 | 16.0356 | 8.2244 | -3.0011 | -9.0022 | 36.0631 | 35.1368 | 33.9168 | 33.581 | 32.4789 | 31.1694 | 29.761 | 27.9778 | 26.441 | 15.4441 | -0.41482 | -15.1032 | 27.8147 | 27.1568 | 26.1104 | 26.0852 | 25.302 | 24.3736 | 23.3673 | 21.9831 | 20.9157 | 12.8325 | 1.6431 | -4.418
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | AMESBURY BSP | MINIMUM HEADROOM | SU 15842 42724 | NO | NO | 4.048 | 64.0774 | 64.1978 | 64.2203 | 63.5437 | 62.9213 | 61.4815 | 59.8448 | 58.1244 | 56.405 | 49.1723 | 43.7193 | 40.4866 | 71.2081 | 71.1544 | 71.0755 | 70.5133 | 70.0723 | 69.227 | 68.1976 | 67.1565 | 66.0965 | 61.6607 | 58.9018 | 52.8091 | 64.4365 | 64.466 | 64.447 | 63.7607 | 63.2039 | 61.9228 | 60.4323 | 58.8818 | 57.3491 | 53.2923 | 50.0418 | 48.4828
|  | AMESBURY BSP | EE |  |  |  |  | 64.0774 | 64.1978 | 64.2203 | 63.5733 | 63.0937 | 61.704 | 60.2244 | 58.756 | 57.2835 | 50.4662 | 45.5386 | 42.8866 | 72.3644 | 72.3246 | 72.2481 | 71.7552 | 71.4358 | 70.6542 | 69.7399 | 68.8756 | 67.9807 | 63.1379 | 60.2277 | 58.2583 | 65.8522 | 65.8766 | 65.8532 | 65.2348 | 64.8124 | 63.6175 | 62.2858 | 60.9644 | 59.6501 | 54.146 | 50.695 | 49.195
|  | AMESBURY BSP | HT |  |  |  |  | 64.0846 | 64.2111 | 64.2499 | 63.5437 | 62.9213 | 61.4815 | 59.8448 | 58.1244 | 56.405 | 49.1723 | 43.7193 | 40.4866 | 71.2081 | 71.1597 | 71.0755 | 70.5133 | 70.0723 | 69.227 | 68.1976 | 67.1565 | 66.0965 | 61.6607 | 59.5618 | 58.9818 | 64.4365 | 64.467 | 64.447 | 63.7607 | 63.2039 | 61.9228 | 60.4323 | 58.8818 | 57.3491 | 55.6923 | 54.6144 | 53.587
|  | AMESBURY BSP | HE |  |  |  |  | 64.0897 | 64.206 | 64.2427 | 63.5499 | 63.0274 | 61.6346 | 60.1458 | 58.6019 | 57.0866 | 51.6091 | 46.9815 | 44.4968 | 71.2091 | 71.1544 | 71.086 | 70.5723 | 70.2333 | 69.4533 | 68.5165 | 67.5923 | 66.6344 | 62.2712 | 59.4512 | 57.167 | 64.4428 | 64.466 | 64.4502 | 63.7828 | 63.3344 | 62.1039 | 60.7428 | 59.3155 | 57.9091 | 53.2923 | 50.0418 | 48.4828
|  | AMESBURY BSP | FB |  |  |  |  | 64.5591 | 64.8366 | 65.0774 | 65.1876 | 65.2886 | 65.1356 | 65.0376 | 64.6601 | 64.1142 | 60.358 | 56.2652 | 53.6733 | 71.4723 | 71.466 | 71.4386 | 71.347 | 71.2207 | 70.8355 | 70.4818 | 69.8639 | 69.0597 | 64.6586 | 58.9018 | 52.8091 | 64.927 | 65.127 | 65.2976 | 65.3586 | 65.447 | 65.2933 | 65.1933 | 64.7512 | 64.0891 | 60.306 | 56.3544 | 54.0144
MELKSHAM GSP | ANDOVER BSP | ANDOVER BSP | MINIMUM HEADROOM | SU 35334 46598 | NO | NO | 23.985 | 35.3291 | 34.473 | 147.6709 | 145.4638 | 142.526 | 138.7546 | 133.9342 | 127.7434 | 119.5413 | 102.8454 | 87.9607 | 78.8964 | 42.6889 | 42.1078 | 151.0941 | 150.031 | 148.6847 | 147.4289 | 144.8426 | 139.6626 | 131.5963 | 115.6689 | 104.0647 | 92.1236 | 37.192 | 36.6415 | 147.2405 | 145.8741 | 143.9184 | 141.2163 | 136.6068 | 130.4447 | 121.5457 | 104.672 | 92.971 | 83.1057
|  | ANDOVER BSP | EE |  |  |  |  | 35.3291 | 34.6791 | 147.8617 | 145.6281 | 142.626 | 138.7546 | 134.2832 | 129.375 | 124.1505 | 105.2301 | 88.9321 | 80.9087 | 44.4546 | 44.1852 | 153.1954 | 152.1781 | 150.8148 | 149.424 | 147.5679 | 143.9556 | 139.8597 | 123.6964 | 109.127 | 101.1505 | 39.1699 | 38.8658 | 149.4883 | 148.1628 | 146.1852 | 143.3934 | 139.5036 | 135.0576 | 130.1648 | 112.2689 | 96.927 | 90.2923
|  | ANDOVER BSP | HT |  |  |  |  | 35.3464 | 34.473 | 147.6709 | 145.4638 | 142.526 | 138.8821 | 134.0566 | 129.2311 | 123.3281 | 103.9076 | 87.9607 | 78.8964 | 42.7047 | 42.1078 | 151.0941 | 150.031 | 148.6847 | 147.4289 | 144.8426 | 140.9289 | 135.4963 | 119.8257 | 107.8152 | 101.7678 | 37.2057 | 36.6415 | 147.2405 | 145.8741 | 143.9184 | 141.2163 | 136.6068 | 131.972 | 125.8205 | 121.191 | 116.9573 | 113.7563
|  | ANDOVER BSP | HE |  |  |  |  | 35.3332 | 34.7148 | 147.925 | 145.7148 | 142.5923 | 138.8291 | 133.9342 | 127.7434 | 119.5413 | 102.8454 | 90.3576 | 80.5617 | 42.6889 | 42.4015 | 151.3973 | 150.3415 | 148.9015 | 147.4857 | 145.0889 | 139.6626 | 131.5963 | 115.6689 | 104.0647 | 92.1236 | 37.192 | 36.9005 | 147.5236 | 146.1363 | 144.0405 | 141.2626 | 136.6878 | 130.4447 | 121.5457 | 104.672 | 92.971 | 83.1057
|  | ANDOVER BSP | FB |  |  |  |  | 36.177 | 36.1607 | 150.3342 | 149.2117 | 147.8066 | 146.2321 | 144.0485 | 141.7995 | 139.4995 | 128.6638 | 115.7025 | 106.7189 | 43.1289 | 43.0278 | 152.511 | 151.8426 | 151.032 | 150.0531 | 148.672 | 146.9499 | 144.8457 | 132.8384 | 114.4763 | 96.3941 | 37.9847 | 38.0741 | 149.3584 | 148.7131 | 147.8584 | 146.6552 | 144.9194 | 143.3036 | 141.3247 | 130.6615 | 116.5815 | 106.8478
MANNINGTON GSP | ARNEWOOD BSP | ARNEWOOD BSP | MINIMUM HEADROOM | SZ 26094 97294 | NO | NO | 7.611 | 20.0004 | 19.6606 | 18.6289 | 85.6172 | 83.4141 | 79.5365 | 75.0539 | 70.4253 | 66.2774 | 51.457 | 40.4968 | 35.5774 | 32.9804 | 32.3236 | 31.2331 | 98.476 | 96.4392 | 93.9381 | 90.8392 | 87.4539 | 84.5013 | 74.0571 | 68.407 | 54.2897 | 23.2046 | 22.7941 | 21.7088 | 88.7287 | 86.3729 | 83.0887 | 79.2076 | 75.135 | 71.5108 | 64.0192 | 55.7825 | 51.9916
|  | ARNEWOOD BSP | EE |  |  |  |  | 20.131 | 20.0157 | 19.1922 | 86.608 | 85.0916 | 81.5784 | 77.358 | 73.1702 | 69.3692 | 55.7447 | 45.1488 | 39.8182 | 34.1432 | 33.5922 | 32.6371 | 100.061 | 98.4682 | 96.3427 | 93.4968 | 90.5855 | 87.8682 | 76.3059 | 68.407 | 62.811 | 24.6769 | 24.4167 | 23.5289 | 90.9161 | 89.1794 | 86.3519 | 82.8008 | 79.2355 | 75.9896 | 64.1365 | 55.7825 | 51.9916
|  | ARNEWOOD BSP | HT |  |  |  |  | 20.0004 | 19.6606 | 18.6289 | 85.6172 | 83.4141 | 79.5365 | 75.0539 | 70.4253 | 66.2774 | 51.457 | 40.4968 | 35.5774 | 32.9804 | 32.3236 | 31.2331 | 98.476 | 96.4392 | 93.9381 | 90.8392 | 87.4539 | 84.5013 | 74.0571 | 68.4476 | 67.1255 | 23.2046 | 22.7941 | 21.7088 | 88.7287 | 86.3729 | 83.0887 | 79.2076 | 75.135 | 71.5108 | 67.8718 | 65.2981 | 63.2813
|  | ARNEWOOD BSP | HE |  |  |  |  | 20.1116 | 20.0616 | 19.1993 | 86.5896 | 84.9141 | 81.2702 | 77.0161 | 72.7335 | 68.7845 | 57.9488 | 49.1733 | 45.6059 | 33.0331 | 32.5752 | 31.5204 | 98.9729 | 97.1771 | 94.9445 | 92.0739 | 89.0845 | 86.2339 | 76.035 | 69.1718 | 63.9308 | 23.2783 | 23.1099 | 22.1278 | 89.515 | 87.536 | 84.5392 | 80.8981 | 77.1824 | 73.7424 | 64.0192 | 57.1508 | 54.6118
|  | ARNEWOOD BSP | FB |  |  |  |  | 21.1891 | 21.5238 | 21.3514 | 89.6927 | 89.457 | 88.7508 | 87.911 | 86.9814 | 86.0437 | 78.8682 | 69.5692 | 64.0804 | 33.9299 | 33.6846 | 32.8909 | 100.8329 | 100.0445 | 98.7697 | 97.3897 | 95.7992 | 94.0297 | 83.2034 | 69.1287 | 54.2897 | 24.4731 | 24.6867 | 24.4004 | 92.6813 | 92.3413 | 91.516 | 90.6003 | 89.4687 | 88.2297 | 80.7424 | 71.6887 | 66.1739
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | BASINGSTOKE (T1A & T2A) BSP | MINIMUM HEADROOM | SU 65132 52710 | YES | NO | 19.406 | 67.0116 | 66.8943 | 66.779 | 66.3453 | 65.3014 | 63.9055 | 62.6677 | 61.3616 | 60.1677 | 55.1147 | 50.6351 | 48.2637 | 65.6412 | 65.4044 | 65.2981 | 65.0233 | 64.3012 | 63.4549 | 62.4139 | 61.2118 | 60.1707 | 56.2139 | 53.3781 | 47.1833 | 64.7069 | 64.5374 | 64.4111 | 63.9911 | 63.0195 | 61.8164 | 60.6522 | 59.3943 | 58.2701 | 54.4048 | 51.3218 | 49.6126
|  | BASINGSTOKE (T1A & T2A) BSP | EE |  |  |  |  | 67.0116 | 66.9422 | 66.779 | 66.43 | 65.5882 | 64.282 | 63.0851 | 61.7606 | 60.5484 | 55.1147 | 50.6351 | 48.2637 | 66.7935 | 66.6364 | 66.4731 | 66.2466 | 65.7476 | 64.9782 | 63.9986 | 62.821 | 61.818 | 57.0445 | 53.77 | 51.4017 | 65.9341 | 65.8218 | 65.6269 | 65.2892 | 64.5433 | 63.4535 | 62.3555 | 61.13 | 60.029 | 54.8647 | 51.3218 | 49.6126
|  | BASINGSTOKE (T1A & T2A) BSP | HT |  |  |  |  | 67.0228 | 66.8943 | 66.7922 | 66.3453 | 65.3014 | 63.9055 | 62.6677 | 61.3616 | 60.1677 | 55.2116 | 51.0269 | 49.3779 | 65.6454 | 65.4044 | 65.2981 | 65.0233 | 64.3012 | 63.4549 | 62.4139 | 61.2118 | 60.1707 | 56.2865 | 54.0328 | 53.4918 | 64.7164 | 64.5374 | 64.4143 | 63.9911 | 63.0195 | 61.8164 | 60.6522 | 59.3943 | 58.2701 | 57.229 | 56.3248 | 55.2974
|  | BASINGSTOKE (T1A & T2A) BSP | HE |  |  |  |  | 67.0147 | 66.9535 | 66.8024 | 66.4126 | 65.5484 | 64.2575 | 63.1035 | 61.7759 | 60.5739 | 56.4749 | 53.5086 | 52.1494 | 65.6412 | 65.4791 | 65.3044 | 65.0739 | 64.5549 | 63.7444 | 62.7591 | 61.5086 | 60.4718 | 56.2139 | 53.6633 | 51.6191 | 64.7069 | 64.6059 | 64.4111 | 64.0385 | 63.2427 | 62.1301 | 61.0301 | 59.7543 | 58.6353 | 54.4048 | 52.0385 | 51.0648
|  | BASINGSTOKE (T1A & T2A) BSP | FB |  |  |  |  | 67.2555 | 67.3759 | 67.4382 | 67.3382 | 66.9596 | 66.5606 | 66.2473 | 65.8575 | 65.3698 | 62.6402 | 60.4555 | 57.4728 | 65.8097 | 65.7854 | 65.717 | 65.5044 | 65.1749 | 64.7802 | 64.257 | 63.656 | 63.0202 | 58.8181 | 53.3781 | 47.1833 | 64.9417 | 65.0301 | 65.0659 | 64.9217 | 64.6448 | 64.3122 | 63.9522 | 63.508 | 62.9985 | 60.1301 | 57.3385 | 54.448
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BASINGSTOKE (T1B & T2B) BSP | MINIMUM HEADROOM | SU 65132 52711 | NO | NO | 11.527 | 54.4982 | 53.7788 | 52.5084 | 50.7278 | 48.6574 | 45.1747 | 40.0523 | 34.8961 | 29.942 | 12.1247 | 1.9574 | -2.9477 | 61.1881 | 60.705 | 60.0029 | 58.9281 | 57.8197 | 55.9965 | 53.2965 | 50.3302 | 47.6313 | 38.086 | 32.1208 | 19.766 | 56.7439 | 56.2987 | 55.525 | 54.0671 | 52.3976 | 49.5471 | 45.2397 | 40.6744 | 36.4618 | 24.977 | 17.3617 | 13.9015
|  | BASINGSTOKE (T1B & T2B) BSP | EE |  |  |  |  | 54.4982 | 53.7788 | 52.5084 | 50.7982 | 48.9706 | 45.7298 | 42.0502 | 36.6706 | 31.4859 | 13.0941 | 2.7645 | -2.5447 | 62.578 | 62.1076 | 61.4637 | 60.5576 | 59.6658 | 58.0964 | 56.1392 | 53.2892 | 50.6403 | 39.0852 | 33.129 | 28.5096 | 58.3025 | 57.8505 | 57.0872 | 55.9015 | 54.58 | 52.0454 | 49.0841 | 44.577 | 40.3484 | 24.977 | 17.3617 | 13.9015
|  | BASINGSTOKE (T1B & T2B) BSP | HT |  |  |  |  | 54.5155 | 53.8869 | 52.6553 | 50.7278 | 48.6574 | 45.1747 | 40.0523 | 34.8961 | 29.942 | 12.1247 | 1.9574 | -2.9477 | 61.1944 | 60.7197 | 60.0029 | 58.9281 | 57.8197 | 55.9965 | 53.2965 | 50.3302 | 47.6313 | 38.086 | 34.3481 | 33.0513 | 56.746 | 56.3334 | 55.525 | 54.0671 | 52.3976 | 49.5471 | 45.2397 | 40.6744 | 36.4618 | 32.5281 | 27.7892 | 25.745
|  | BASINGSTOKE (T1B & T2B) BSP | HE |  |  |  |  | 54.5094 | 53.839 | 52.5961 | 50.7829 | 48.8349 | 45.6135 | 41.9329 | 37.3737 | 32.9839 | 18.5461 | 9.1594 | 4.2818 | 61.1881 | 60.705 | 60.0418 | 59.0965 | 58.1734 | 56.5597 | 54.5176 | 51.9808 | 49.6608 | 39.1355 | 32.9229 | 27.6587 | 56.7439 | 56.2987 | 55.5281 | 54.245 | 52.8134 | 50.2313 | 47.1597 | 43.2618 | 39.6723 | 26.9271 | 19.5523 | 15.9944
|  | BASINGSTOKE (T1B & T2B) BSP | FB |  |  |  |  | 55.1716 | 54.9747 | 54.4349 | 53.8543 | 53.1533 | 52.1839 | 51.1594 | 50.1155 | 48.0655 | 38.34 | 28.3737 | 22.4227 | 61.7176 | 61.5113 | 61.1292 | 60.7302 | 60.2471 | 59.2765 | 58.085 | 56.9955 | 55.2387 | 45.5092 | 32.1208 | 19.766 | 57.5608 | 57.6208 | 57.3913 | 57.1565 | 56.9408 | 56.2776 | 55.3597 | 54.4955 | 52.5618 | 43.1555 | 32.8165 | 27.5123
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | BASINGSTOKE (T3 & T4) BSP | MINIMUM HEADROOM | SU 65132 52712 | NO | NO | 35.672 | 59.6642 | 59.5234 | 59.2907 | 58.5785 | 57.3509 | 55.6417 | 53.7315 | 51.5897 | 49.5958 | 40.9642 | 35.5846 | 32.6652 | 61.5218 | 61.3881 | 61.2344 | 60.8155 | 59.9849 | 58.7386 | 57.3628 | 55.6344 | 54.1344 | 48.3081 | 42.9176 | 33.8533 | 58.166 | 57.946 | 57.707 | 57.0607 | 56.1018 | 54.6555 | 52.8965 | 50.7765 | 48.887 | 42.6302 | 38.3958 | 36.1468
|  | BASINGSTOKE (T3 & T4) BSP | EE |  |  |  |  | 59.6642 | 59.5234 | 59.2907 | 58.6601 | 57.5642 | 55.9428 | 54.2285 | 52.0234 | 49.955 | 41.0183 | 35.5846 | 32.6652 | 62.4417 | 62.3162 | 62.1754 | 61.8407 | 61.1366 | 59.9611 | 58.7866 | 57.0917 | 55.5907 | 48.9458 | 44.7428 | 41.1836 | 59.2173 | 58.9846 | 58.7489 | 58.203 | 57.4111 | 56.0805 | 54.5917 | 52.4968 | 50.5979 | 42.803 | 38.3958 | 36.1468
|  | BASINGSTOKE (T3 & T4) BSP | HT |  |  |  |  | 59.6775 | 59.5591 | 59.3193 | 58.5785 | 57.3509 | 55.6417 | 53.7315 | 51.5897 | 49.5958 | 40.9642 | 35.8734 | 33.6907 | 61.527 | 61.4018 | 61.2344 | 60.8155 | 59.9849 | 58.7386 | 57.3628 | 55.6344 | 54.1344 | 48.6681 | 45.8618 | 44.9586 | 58.166 | 57.946 | 57.707 | 57.0607 | 56.1018 | 54.6555 | 52.8965 | 50.7765 | 48.887 | 47.2955 | 45.5123 | 44.1028
|  | BASINGSTOKE (T3 & T4) BSP | HE |  |  |  |  | 59.6795 | 59.553 | 59.3407 | 58.7224 | 57.6009 | 56.0387 | 54.3642 | 52.2703 | 50.2928 | 42.5989 | 38.7958 | 37.1183 | 61.5218 | 61.3881 | 61.2397 | 60.9144 | 60.1765 | 58.9807 | 57.7565 | 56.0491 | 54.5281 | 48.3081 | 44.6386 | 41.3228 | 58.1702 | 57.946 | 57.7355 | 57.1491 | 56.2986 | 54.9639 | 53.4449 | 51.3681 | 49.4744 | 42.6302 | 39.5112 | 38.2239
|  | BASINGSTOKE (T3 & T4) BSP | FB |  |  |  |  | 59.9234 | 59.9795 | 59.9479 | 59.7122 | 59.4509 | 59.0397 | 58.3142 | 57.5142 | 56.402 | 50.3224 | 45.7285 | 42.6724 | 61.707 | 61.6902 | 61.646 | 61.2744 | 60.8502 | 60.1818 | 59.3018 | 58.4155 | 57.3428 | 50.6744 | 42.9176 | 33.8533 | 58.5228 | 58.547 | 58.5133 | 58.2744 | 58.066 | 57.6691 | 57.1228 | 56.506 | 55.5565 | 49.6049 | 44.8912 | 41.5797
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH BSP | MINIMUM HEADROOM | SP5972023735 | NO | NO | 184.689 | -65.5886 | -67.1009 | -66.4404 | -70.1465 | -79.5965 | -89.9078 | -99.972 | -109.5292 | -118.4884 | -140.2037 | -152.8251 | -157.7516 | -55.003 | -55.7514 | -48.9861 | -50.5251 | -57.5282 | -63.6966 | -69.5451 | -75.2009 | -80.344 | -92.6735 | -98.3703 | -99.7861 | -62.884 | -63.5724 | -59.8503 | -62.4377 | -71.144 | -79.2893 | -87.1609 | -94.6745 | -101.704 | -114.0619 | -122.2251 | -125.1261
|  | BICESTER NORTH BSP | EE |  |  |  |  | -65.5886 | -67.1009 | -66.4404 | -70.1098 | -75.6251 | -85.5567 | -95.3516 | -104.9771 | -114.0343 | -137.571 | -148.5271 | -152.6578 | -53.8445 | -54.4312 | -47.3527 | -48.669 | -51.7261 | -57.0588 | -62.0445 | -67.118 | -71.771 | -86.7088 | -92.1547 | -94.571 | -61.5425 | -62.2241 | -58.2822 | -60.7598 | -65.3894 | -72.8894 | -80.171 | -87.4037 | -94.1741 | -113.3353 | -121.9078 | -124.919
|  | BICESTER NORTH BSP | HT |  |  |  |  | -65.5468 | -67.0345 | -66.3139 | -69.9261 | -79.5965 | -89.9078 | -99.972 | -109.5292 | -118.4884 | -140.2037 | -152.8251 | -157.7516 | -55.003 | -55.7514 | -48.9861 | -50.5251 | -57.5282 | -63.6966 | -69.5451 | -75.2009 | -80.344 | -92.6735 | -98.3703 | -99.7861 | -62.884 | -63.5566 | -59.8503 | -62.4377 | -71.144 | -79.2893 | -87.1609 | -94.6745 | -101.704 | -107.0524 | -110.5998 | -113.2893
|  | BICESTER NORTH BSP | HE |  |  |  |  | -65.5794 | -67.0784 | -66.3986 | -70.1465 | -75.718 | -85.7159 | -95.5751 | -105.1455 | -114.1241 | -134.8792 | -145.122 | -148.8884 | -54.884 | -55.4945 | -48.5156 | -49.8819 | -53.0493 | -58.6387 | -63.8682 | -69.0524 | -73.7987 | -87.2419 | -92.7366 | -95.6072 | -62.8724 | -63.5724 | -59.7482 | -62.3609 | -67.163 | -74.9893 | -82.5724 | -89.984 | -96.9061 | -114.0619 | -122.2251 | -125.1261
|  | BICESTER NORTH BSP | FB |  |  |  |  | -64.5723 | -65.5009 | -63.6527 | -65.9445 | -69.5863 | -74.5904 | -80.6802 | -86.3669 | -92.0527 | -117.4271 | -130.47 | -136.7108 | -54.343 | -55.0187 | -47.6293 | -48.4693 | -50.7535 | -53.884 | -57.9398 | -61.7261 | -65.1598 | -82.7903 | -91.9324 | -98.8419 | -62.2819 | -62.6556 | -57.7187 | -59.1345 | -62.3903 | -66.3114 | -71.2577 | -75.7766 | -80.1882 | -101.0977 | -112.0966 | -117.9219
BOTLEY WOOD GSP | BOTLEY WOOD BSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU 54073 09759 | NO | NO | 20.306 | 78.7912 | 78.4606 | 77.634 | 76.5259 | 75.3892 | 73.481 | 71.5596 | 69.5902 | 67.6412 | 61.1983 | 56.3943 | 54.7494 | 81.8575 | 81.5996 | 80.9533 | 80.1775 | 79.3954 | 78.2207 | 76.7891 | 75.3501 | 73.9017 | 69.6112 | 66.8588 | 60.8185 | 79.0417 | 78.8249 | 78.2617 | 77.4775 | 76.4501 | 74.8712 | 73.1554 | 71.4122 | 69.687 | 65.9028 | 62.5384 | 61.2445
|  | BOTLEY WOOD BSP | EE |  |  |  |  | 78.8126 | 78.6085 | 77.8749 | 76.9789 | 76.1065 | 74.4647 | 72.6157 | 70.7667 | 68.9514 | 62.6014 | 57.8943 | 55.8126 | 82.5016 | 82.3251 | 81.7169 | 81.021 | 80.3272 | 79.3261 | 77.9874 | 76.6792 | 75.4333 | 70.2986 | 66.8588 | 64.7904 | 79.8363 | 79.7078 | 79.2139 | 78.5782 | 77.7741 | 76.4312 | 74.8169 | 73.2251 | 71.6761 | 66.1986 | 62.5384 | 61.2445
|  | BOTLEY WOOD BSP | HT |  |  |  |  | 78.7912 | 78.4606 | 77.634 | 76.5259 | 75.3892 | 73.481 | 71.5596 | 69.5902 | 67.6412 | 61.1983 | 56.3943 | 54.7494 | 81.8575 | 81.5996 | 80.9533 | 80.1775 | 79.3954 | 78.2207 | 76.7891 | 75.3501 | 73.9017 | 69.6112 | 67.187 | 66.9038 | 79.0417 | 78.8249 | 78.2617 | 77.4775 | 76.4501 | 74.8712 | 73.1554 | 71.4122 | 69.687 | 67.9964 | 66.9901 | 66.0375
|  | BOTLEY WOOD BSP | HE |  |  |  |  | 78.8167 | 78.6126 | 77.9116 | 77.0024 | 76.0075 | 74.4534 | 72.632 | 70.784 | 68.9432 | 63.6892 | 60.2392 | 58.9994 | 81.8596 | 81.6796 | 81.0596 | 80.3849 | 79.607 | 78.6017 | 77.2091 | 75.8491 | 74.5217 | 69.8638 | 67.028 | 64.9722 | 79.0575 | 78.9301 | 78.4417 | 77.7933 | 76.8564 | 75.5417 | 73.8817 | 72.2428 | 70.6143 | 65.9028 | 63.2491 | 62.4733
|  | BOTLEY WOOD BSP | FB |  |  |  |  | 79.2647 | 79.1463 | 78.9861 | 78.7667 | 78.3422 | 77.9157 | 77.4238 | 76.8779 | 76.2851 | 72.5922 | 68.9616 | 66.8198 | 82.0838 | 81.8954 | 81.6617 | 81.4143 | 80.9501 | 80.3438 | 79.6849 | 78.9575 | 78.1575 | 73.0512 | 67.0522 | 60.8185 | 79.467 | 79.4217 | 79.3291 | 79.227 | 78.9101 | 78.6101 | 78.2238 | 77.688 | 77.0607 | 73.2375 | 69.5764 | 67.468
MANNINGTON GSP | BOURNEMOUTH BSP | BOURNEMOUTH BSP | MINIMUM HEADROOM | SZ 06265 92437 | NO | NO | 31.19 | 36.285 | 35.9248 | 34.132 | 30.5126 | 26.0279 | 19.1758 | 11.2473 | 3.7126 | -4.3364 | -33.5976 | -53.6782 | -60.467 | 62.8708 | 61.7087 | 59.7139 | 56.9181 | 53.3676 | 48.9855 | 43.4497 | 38.3676 | 32.8023 | 14.1497 | -13.0671 | -53.3692 | 44.4687 | 44.015 | 42.4939 | 39.6308 | 35.3602 | 29.4866 | 22.4223 | 15.9592 | 9.0518 | -6.3323 | -24.1252 | -30.9037
|  | BOURNEMOUTH BSP | EE |  |  |  |  | 36.3289 | 36.2636 | 34.9177 | 31.8473 | 27.9269 | 22.1299 | 15.3401 | 8.7432 | 2.0901 | -25.9915 | -46.719 | -55.8252 | 66.1554 | 65.1361 | 63.5105 | 60.8452 | 57.6126 | 53.8197 | 49.0973 | 44.5738 | 39.9361 | 15.9452 | -2.7078 | -17.1782 | 48.282 | 47.9626 | 46.7687 | 44.3881 | 40.731 | 35.7799 | 29.8279 | 24.281 | 18.6646 | -6.3323 | -24.1252 | -30.9037
|  | BOURNEMOUTH BSP | HT |  |  |  |  | 36.285 | 35.9248 | 34.132 | 30.5126 | 26.0279 | 19.1758 | 11.2473 | 3.7126 | -4.3364 | -33.5976 | -53.6782 | -60.467 | 62.8708 | 61.7087 | 59.7139 | 56.9181 | 53.3676 | 48.9855 | 43.4497 | 38.3676 | 32.8023 | 14.1497 | 3.2097 | -0.23134 | 44.4687 | 44.015 | 42.4939 | 39.6308 | 35.3602 | 29.4866 | 22.4223 | 15.9592 | 9.0518 | 2.156 | -3.0829 | -7.5619
|  | BOURNEMOUTH BSP | HE |  |  |  |  | 36.434 | 36.5289 | 35.1769 | 32.0667 | 27.9014 | 22.9412 | 16.5707 | 10.7758 | 4.8483 | -16.6905 | -32.4721 | -39.715 | 62.9708 | 62.0539 | 60.2918 | 57.7897 | 54.3371 | 50.6697 | 45.6076 | 41.2129 | 36.5992 | 15.2781 | -1.984 | -16.9871 | 44.5771 | 44.4213 | 43.1634 | 40.7297 | 36.7592 | 32.2802 | 26.2876 | 21.1845 | 15.9066 | -3.6303 | -17.2492 | -22.8482
|  | BOURNEMOUTH BSP | FB |  |  |  |  | 37.8361 | 38.8075 | 38.6912 | 37.8667 | 36.1707 | 35.2565 | 33.9095 | 32.6422 | 31.2391 | 18.5942 | -0.80272 | -14.3629 | 63.3402 | 62.7792 | 61.4487 | 59.8613 | 57.3371 | 54.6276 | 51.6666 | 48.3929 | 45.0445 | 21.5571 | -13.0671 | -53.3692 | 45.836 | 46.5139 | 46.5118 | 45.9402 | 44.6834 | 43.8002 | 42.3581 | 40.7308 | 39.036 | 25.2487 | 6.1518 | -7.1345
FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL BSP | MINIMUM HEADROOM | SU 86026 69422 | NO | NO | 75.816 | 49.4574 | 49.4136 | 48.6044 | 46.2095 | 42.6197 | 37.4207 | 31.1299 | 23.8595 | 16.8717 | -6.466 | -22.0864 | -28.9426 | 46.6391 | 46.1633 | 45.1307 | 43.2201 | 40.2128 | 36.5338 | 31.8359 | 26.2686 | 20.8307 | 3.7728 | -11.3999 | -39.1704 | 43.0296 | 42.9286 | 42.097 | 40.0601 | 36.7917 | 32.318 | 26.4054 | 19.8233 | 13.4443 | -2.516 | -16.0079 | -21.8946
|  | BRACKNELL BSP | EE |  |  |  |  | 49.4574 | 49.4136 | 48.7523 | 46.935 | 44.3248 | 39.4003 | 32.3391 | 24.9238 | 17.8717 | -4.8385 | -20.8579 | -28.763 | 49.4299 | 48.9605 | 48.1013 | 46.5391 | 44.3136 | 40.9993 | 35.9289 | 30.6187 | 25.4585 | 4.6574 | -9.1568 | -19.5354 | 46.4268 | 46.2901 | 45.6391 | 44.0585 | 41.7044 | 37.6054 | 31.3197 | 24.8676 | 18.6962 | -2.516 | -16.0079 | -21.8946
|  | BRACKNELL BSP | HT |  |  |  |  | 49.4768 | 49.4656 | 48.6044 | 46.2095 | 42.6197 | 37.4207 | 31.1299 | 23.8595 | 16.8717 | -6.466 | -22.0864 | -28.9426 | 46.6391 | 46.1633 | 45.1307 | 43.2201 | 40.2128 | 36.5338 | 31.8359 | 26.2686 | 20.8307 | 3.7728 | -4.9778 | -7.7104 | 43.0296 | 42.9286 | 42.097 | 40.0601 | 36.7917 | 32.318 | 26.4054 | 19.8233 | 13.4443 | 6.9622 | 2.8412 | -0.77039
|  | BRACKNELL BSP | HE |  |  |  |  | 49.5227 | 49.5381 | 48.9401 | 47.0299 | 44.3513 | 39.6503 | 33.3023 | 26.3819 | 19.8166 | 1.8115 | -10.7303 | -16.2222 | 46.6665 | 46.2086 | 45.3486 | 43.7107 | 41.4043 | 38.0191 | 33.4907 | 28.4833 | 23.5812 | 5.5622 | -6.8378 | -17.1135 | 43.0612 | 42.977 | 42.3559 | 40.6422 | 38.1475 | 34.0717 | 28.4022 | 22.3159 | 16.4717 | -0.59776 | -11.1841 | -15.3388
|  | BRACKNELL BSP | FB |  |  |  |  | 51.1452 | 51.6299 | 52.1697 | 51.9666 | 51.4187 | 50.2054 | 47.7483 | 45.2462 | 42.8381 | 30.9942 | 15.0676 | 5.9778 | 47.5612 | 47.0938 | 46.8075 | 45.9822 | 44.7043 | 42.6949 | 39.8065 | 36.7822 | 33.5991 | 14.6938 | -11.3999 | -39.1704 | 44.5496 | 44.9359 | 45.4654 | 45.438 | 45.0949 | 44.0749 | 41.9243 | 39.637 | 37.3886 | 24.3433 | 8.537 | -0.32723
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | BURGHFIELD (MAIN) BSP | MINIMUM HEADROOM | SU 69442 70509 | NO | NO | 44.59 | 23.977 | 23.8791 | 23.2995 | 22.376 | 21.076 | 16.9801 | 14.8525 | 12.3056 | 10.0668 | -2.0148 | -8.9158 | -12.1709 | 34.3335 | 33.8398 | 32.9293 | 31.9282 | 30.684 | 26.6914 | 24.7482 | 22.5608 | 20.6924 | 10.2419 | -5.6202 | -24.9297 | 26.7629 | 26.5124 | 25.8545 | 25.1482 | 24.0956 | 20.0208 | 17.9324 | 15.2272 | 12.9672 | 4.3545 | -1.4993 | -3.8523
|  | BURGHFIELD (MAIN) BSP | EE |  |  |  |  | 23.977 | 23.976 | 23.4148 | 22.675 | 21.3556 | 17.2076 | 14.976 | 12.4923 | 10.2097 | -1.4842 | -8.9158 | -12.1709 | 35.9701 | 35.5773 | 34.7487 | 33.8926 | 32.7201 | 28.9232 | 27.0467 | 25.012 | 23.2283 | 11.765 | 4.0079 | -3.2156 | 28.6691 | 28.4956 | 27.8671 | 27.3048 | 26.2997 | 22.3997 | 20.3589 | 17.8773 | 15.665 | 4.7426 | -1.4993 | -3.8523
|  | BURGHFIELD (MAIN) BSP | HT |  |  |  |  | 24.0025 | 23.8791 | 23.2995 | 22.376 | 21.076 | 16.9801 | 14.8525 | 12.3056 | 10.0668 | -2.0148 | -8.5873 | -11.0148 | 34.3335 | 33.8398 | 32.9293 | 31.9282 | 30.684 | 26.6914 | 24.7482 | 22.5608 | 20.6924 | 11.4903 | 7.3766 | 5.744 | 26.7629 | 26.5124 | 25.8545 | 25.1482 | 24.0956 | 20.0208 | 17.9324 | 15.2272 | 12.9672 | 10.6419 | 7.3408 | 5.3282
|  | BURGHFIELD (MAIN) BSP | HE |  |  |  |  | 24.0199 | 24.0607 | 23.5393 | 22.7933 | 21.474 | 17.474 | 15.3699 | 13.1046 | 10.9791 | 1.0801 | -4.4362 | -7.1097 | 34.3408 | 33.9408 | 33.0924 | 32.2187 | 31.0135 | 27.1251 | 25.1956 | 23.1945 | 21.4124 | 10.2419 | 2.8114 | -4.7886 | 26.7745 | 26.6356 | 26.0208 | 25.4314 | 24.3672 | 20.4587 | 18.4366 | 16.0766 | 13.9261 | 4.3545 | -0.38021 | -2.4707
|  | BURGHFIELD (MAIN) BSP | FB |  |  |  |  | 24.6127 | 24.8689 | 24.7587 | 24.9127 | 24.4199 | 21.5321 | 20.875 | 20.075 | 19.4219 | 15.1413 | 5.1831 | 0.31988 | 34.4756 | 34.0356 | 33.2608 | 32.8577 | 31.7987 | 27.9366 | 26.384 | 24.6945 | 23.0703 | 13.0051 | -5.6202 | -24.9297 | 27.3219 | 27.3882 | 27.0998 | 27.2598 | 26.8766 | 23.7851 | 23.1956 | 22.4945 | 21.8608 | 17.2229 | 7.1272 | 2.2303
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | BURGHFIELD (RESERVE) BSP | MINIMUM HEADROOM | SU 69442 70509 | NO | NO | 19.667 | 53.1193 | 52.8938 | 52.0397 | 51.1632 | 17.4183 | 14.805 | 12.5367 | 9.8469 | 7.2469 | -3.1368 | -8.7562 | -10.6623 | 62.9687 | 62.5161 | 61.2676 | 60.2192 | 19.3032 | 14.3592 | 12.1782 | 9.5308 | 7.1792 | -2.2303 | -6.4039 | -19.2081 | 53.7066 | 53.3961 | 52.675 | 51.7887 | 11.59 | 6.6971 | 4.274 | 1.3013 | -1.3524 | -8.8429 | -13.2366 | -14.6406
|  | BURGHFIELD (RESERVE) BSP | EE |  |  |  |  | 53.1193 | 52.9142 | 52.102 | 51.4183 | 17.4183 | 15.3438 | 13.0683 | 10.3632 | 7.801 | -2.4286 | -8.2266 | -10.6623 | 64.1849 | 63.7737 | 62.593 | 61.6818 | 19.3032 | 17.4808 | 15.3839 | 12.9318 | 10.7298 | 0.34917 | -5.1549 | -8.9957 | 55.2481 | 54.9492 | 54.2655 | 53.5032 | 11.59 | 10.1686 | 7.792 | 4.9716 | 2.4614 | -7.7876 | -12.8019 | -14.6406
|  | BURGHFIELD (RESERVE) BSP | HT |  |  |  |  | 53.1265 | 52.8938 | 52.0397 | 51.1632 | 49.6877 | 14.805 | 12.5367 | 9.8469 | 7.2469 | -3.1368 | -8.7562 | -10.5837 | 62.9687 | 62.5161 | 61.2676 | 60.2192 | 58.5276 | 14.3592 | 12.1782 | 9.5308 | 7.1792 | -2.2303 | -5.9871 | -6.6966 | 53.7119 | 53.4003 | 52.675 | 51.7887 | 50.555 | 6.6971 | 4.274 | 1.3013 | -1.3524 | -4.2513 | -6.1703 | -7.8239
|  | BURGHFIELD (RESERVE) BSP | HE |  |  |  |  | 53.1285 | 52.9101 | 52.1459 | 51.4295 | 50.0387 | 47.9377 | 13.0255 | 10.3785 | 7.6948 | -0.068424 | -4.9786 | -6.6154 | 62.9687 | 62.5255 | 61.3382 | 60.3803 | 58.7729 | 56.8508 | 12.6287 | 10.1676 | 7.7466 | -0.94709 | -6.2313 | -9.9597 | 53.7066 | 53.3961 | 52.7234 | 51.9003 | 50.734 | 49.254 | 4.7371 | 1.9003 | -0.82078 | -8.8429 | -13.2366 | -14.4755
|  | BURGHFIELD (RESERVE) BSP | FB |  |  |  |  | 53.8775 | 54.0112 | 54.0561 | 54.0438 | 53.9663 | 53.5234 | 52.6989 | 19.4581 | 18.5724 | 13.5714 | 6.2918 | 1.3214 | 63.375 | 63.0782 | 62.6834 | 62.2992 | 61.754 | 60.7413 | 59.2466 | 15.9676 | 14.3655 | 5.5813 | -6.4039 | -19.2081 | 54.2108 | 54.1234 | 53.9961 | 53.7392 | 53.4308 | 52.994 | 52.3782 | 9.7508 | 9.0508 | 3.8561 | -3.925 | -9.4134
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY (MAIN) BSP | MINIMUM HEADROOM | SU 86530 59483 | NO | NO | 18.185 | 33.9543 | 33.2533 | 32.2308 | 30.7941 | 28.4859 | 24.8002 | 20.639 | 15.9645 | 11.8839 | -2.361 | -11.1661 | -13.4498 | 59.7275 | 58.6643 | 57.3464 | 55.7159 | 53.1159 | 49.8548 | 46.0601 | 41.8748 | 38.2696 | 26.0306 | 15.0938 | -4.3999 | 37.6043 | 36.8485 | 35.8422 | 34.3738 | 31.8012 | 28.2664 | 24.2833 | 19.8927 | 16.1106 | 6.9496 | 0.46882 | -2.0291
|  | CAMBERLEY (MAIN) BSP | EE |  |  |  |  | 33.9543 | 33.2533 | 32.4155 | 31.4727 | 30.0206 | 26.9145 | 22.9655 | 18.5992 | 14.8349 | 1.1482 | -7.9682 | -11.2539 | 61.0596 | 60.0494 | 58.8892 | 57.5413 | 55.5137 | 52.728 | 49.2749 | 45.4525 | 42.1964 | 28.1841 | 18.8729 | 12.627 | 39.6545 | 38.927 | 38.0862 | 37.0311 | 35.2525 | 32.2862 | 28.6413 | 24.6341 | 21.2188 | 8.5566 | 0.46882 | -2.0291
|  | CAMBERLEY (MAIN) BSP | HT |  |  |  |  | 33.9655 | 33.2614 | 32.2308 | 30.7941 | 28.4859 | 24.8002 | 20.639 | 15.9645 | 11.8839 | -2.361 | -11.1661 | -13.4498 | 59.7327 | 58.6643 | 57.3464 | 55.7159 | 53.1159 | 49.8548 | 46.0601 | 41.8748 | 38.2696 | 26.0306 | 19.7833 | 18.6264 | 37.6043 | 36.8485 | 35.8422 | 34.3738 | 31.8012 | 28.2664 | 24.2833 | 19.8927 | 16.1106 | 12.0159 | 9.4169 | 7.038
|  | CAMBERLEY (MAIN) BSP | HE |  |  |  |  | 33.9665 | 33.2757 | 32.4553 | 31.5247 | 29.9563 | 26.8727 | 22.9135 | 18.7614 | 14.8135 | 2.6471 | -4.4161 | -6.8886 | 59.7275 | 58.6759 | 57.4896 | 56.1822 | 53.9833 | 51.1043 | 47.5243 | 43.8064 | 40.2212 | 26.7159 | 18.6075 | 12.1022 | 37.6054 | 36.858 | 36.0127 | 34.9622 | 32.9917 | 29.9401 | 26.1906 | 22.2769 | 18.5664 | 6.9496 | 0.82116 | -1.0831
|  | CAMBERLEY (MAIN) BSP | FB |  |  |  |  | 34.9727 | 34.8431 | 34.6002 | 34.4798 | 34.3196 | 33.5298 | 32.2584 | 30.8492 | 29.5206 | 19.9053 | 9.2369 | 3.3369 | 60.1654 | 59.5317 | 58.7496 | 57.9401 | 56.9296 | 55.3117 | 53.1422 | 50.8254 | 48.6327 | 33.658 | 15.0938 | -4.3999 | 38.6485 | 38.5622 | 38.2696 | 38.0854 | 37.8075 | 36.9264 | 35.5064 | 33.9085 | 32.4212 | 22.2927 | 11.8633 | 5.8517
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | CAMBERLEY (RESERVE) BSP | MINIMUM HEADROOM | SU 86530 59483 | NO | NO | 32.697 | 1.6553 | -35.7263 | -36.3202 | -37.2937 | -38.7957 | -41.3794 | -44.4804 | -47.8733 | -51.2049 | -63.0743 | -70.3957 | -72.4855 | -0.24904 | -48.4511 | -49.2596 | -50.3901 | -52.0406 | -54.1427 | -56.7322 | -59.7143 | -62.629 | -72.349 | -82.7975 | -98.9311 | -7.6617 | -55.6301 | -56.4059 | -57.5448 | -59.3469 | -61.8006 | -64.8143 | -68.168 | -71.4448 | -79.049 | -84.7175 | -86.0943
|  | CAMBERLEY (RESERVE) BSP | EE |  |  |  |  | 1.6635 | -35.7018 | -36.2171 | -37.0018 | -38.1753 | -40.3804 | -43.211 | -46.1294 | -49.0835 | -61.0222 | -68.9498 | -72.3365 | 2.728 | -43.972 | -44.7046 | -45.6995 | -47.1302 | -48.8944 | -51.3444 | -53.8659 | -56.4791 | -68.1546 | -75.9526 | -81.7893 | -4.4189 | -50.9067 | -51.5995 | -52.5383 | -54.0169 | -56.0791 | -58.8567 | -61.6904 | -64.6046 | -76.1404 | -83.1883 | -85.6934
|  | CAMBERLEY (RESERVE) BSP | HT |  |  |  |  | 1.6553 | -35.7263 | -36.3202 | -37.2937 | -38.7957 | -41.3794 | -44.4804 | -47.8733 | -51.2049 | -63.0743 | -70.3957 | -72.4855 | -0.24904 | -48.4511 | -49.2596 | -50.3901 | -52.0406 | -54.1427 | -56.7322 | -59.7143 | -62.629 | -72.349 | -77.2796 | -78.4027 | -7.6617 | -55.6301 | -56.4059 | -57.5448 | -59.3469 | -61.8006 | -64.8143 | -68.168 | -71.4448 | -74.7711 | -77.2522 | -79.1827
|  | CAMBERLEY (RESERVE) BSP | HE |  |  |  |  | 1.6788 | -35.6753 | -36.1712 | -37.0467 | -38.3243 | -40.4824 | -43.1049 | -45.8345 | -48.7488 | -58.612 | -64.9253 | -66.9253 | -0.24062 | -48.4238 | -49.168 | -50.2164 | -51.7238 | -53.5575 | -55.8796 | -58.2943 | -60.9754 | -71.5385 | -78.8227 | -84.3933 | -7.648 | -55.5975 | -56.2859 | -57.329 | -58.9448 | -61.0427 | -63.6754 | -66.3722 | -69.3438 | -79.049 | -84.7175 | -86.0943
|  | CAMBERLEY (RESERVE) BSP | FB |  |  |  |  | 2.6747 | -34.4998 | -34.5029 | -34.7396 | -35.0212 | -35.7978 | -36.3498 | -37.0335 | -37.8702 | -44.8702 | -53.0406 | -57.5692 | 0.57306 | -47.6469 | -48.0869 | -48.9343 | -49.8311 | -51.4101 | -52.8301 | -54.3248 | -56.0417 | -67.5975 | -82.7975 | -98.9311 | -6.7459 | -54.5017 | -54.4333 | -54.7111 | -55.169 | -56.0911 | -56.8501 | -57.7185 | -58.8164 | -66.5406 | -75.1922 | -79.9385
IVER 132KV GSP | CHALVEY BSP | CHALVEY BSP | MINIMUM HEADROOM | SU 96669 79364 | NO | YES | 45.189 | 38.7215 | 37.8296 | 36.9 | 35.1694 | 33.3602 | 146.1 | 143.447 | 140.3694 | 137.348 | 124.596 | 117.4582 | 114.447 | 50.051 | 48.8784 | 48.3837 | 46.7216 | 45.2331 | 153.3837 | 151.5931 | 148.5889 | 145.391 | 132.3378 | 123.6704 | 110.8068 | 39.4184 | 38.4616 | 37.61 | 35.7521 | 33.9784 | 143.6521 | 141.7152 | 138.4321 | 135.1447 | 123.0878 | 115.8102 | 112.8766
|  | CHALVEY BSP | EE |  |  |  |  | 38.7215 | 38.4153 | 36.9 | 35.1694 | 33.3602 | 146.1 | 143.447 | 140.3694 | 137.348 | 124.596 | 117.4582 | 114.447 | 51.1592 | 50.9725 | 49.5419 | 47.9296 | 46.4602 | 154.6102 | 152.0051 | 148.9245 | 145.8143 | 132.3378 | 123.6704 | 116.8388 | 40.8684 | 40.4551 | 39.0511 | 37.3021 | 35.5582 | 145.2225 | 142.4664 | 139.2919 | 136.1592 | 123.0878 | 115.8102 | 112.8766
|  | CHALVEY BSP | HT |  |  |  |  | 38.7664 | 37.8296 | 37.0031 | 35.2174 | 33.7011 | 146.4143 | 144.2817 | 141.0572 | 137.8776 | 126.6541 | 121.4868 | 120.4511 | 50.051 | 48.8784 | 48.3837 | 46.7216 | 45.6321 | 153.63 | 151.7047 | 148.5889 | 145.391 | 134.911 | 129.9489 | 128.3447 | 39.4184 | 38.4616 | 37.61 | 35.7521 | 34.231 | 143.8321 | 141.7152 | 138.4321 | 135.1447 | 132.1689 | 129.2173 | 127.1931
|  | CHALVEY BSP | HE |  |  |  |  | 38.7806 | 38.5164 | 37.0592 | 35.298 | 33.4633 | 146.2684 | 144.3776 | 141.8531 | 139.346 | 130.9204 | 126.6531 | 124.9786 | 50.0521 | 49.8647 | 48.3963 | 46.7352 | 45.2331 | 153.3837 | 151.5931 | 149.0426 | 146.4195 | 136.3826 | 129.2879 | 122.9742 | 39.4258 | 39.0395 | 37.6416 | 35.8026 | 33.9784 | 143.6521 | 141.7595 | 139.1721 | 136.5795 | 127.9795 | 123.55 | 121.9089
|  | CHALVEY BSP | FB |  |  |  |  | 39.3051 | 39.4562 | 38.9429 | 37.1286 | 35.8817 | 149.1225 | 148.4072 | 147.398 | 146.3653 | 140.0592 | 133.1939 | 128.1633 | 50.2752 | 50.2742 | 49.8247 | 47.6984 | 46.0531 | 153.9247 | 152.6584 | 151.1416 | 149.5995 | 139.8952 | 126.7321 | 110.8068 | 40.1458 | 40.3079 | 39.7889 | 38.1647 | 37.0037 | 147.1258 | 146.3763 | 145.3058 | 144.2142 | 137.5721 | 130.5047 | 125.3584
LOVEDEAN GSP | CHICHESTER BSP | CHICHESTER BSP | MINIMUM HEADROOM | SU 92281 07417 | NO | YES | 93.391 | -108.9142 | 3.545 | -0.21828 | -5.4479 | -12.0826 | -23.0356 | -35.304 | -47.953 | -60.2326 | -110.1224 | -143.1244 | -161.256 | -80.9842 | 30.4632 | 28.9821 | 26.7316 | 23.7347 | 19.4779 | 11.6558 | 3.4674 | -4.3863 | -31.9853 | -50.5831 | -92.1916 | -100.66 | 12.3211 | 9.8495 | 5.9421 | 0.97054 | -7.5789 | -18.1779 | -29.1021 | -39.6295 | -68.2168 | -88.7142 | -100.3326
|  | CHICHESTER BSP | EE |  |  |  |  | -108.9142 | 3.7542 | -0.21828 | -5.2173 | -11.4387 | -21.9305 | -33.7979 | -45.7122 | -57.1122 | -101.7122 | -132.1479 | -149.5213 | -76.7377 | 35.1205 | 33.5766 | 31.7205 | 29.2297 | 25.9409 | 18.9593 | 11.7736 | 5.0868 | -25.5132 | -45.9754 | -62.1009 | -95.7866 | 17.4521 | 14.7991 | 11.3593 | 6.9185 | -0.58563 | -10.3928 | -20.2295 | -29.4897 | -65.7489 | -88.7142 | -100.3326
|  | CHICHESTER BSP | HT |  |  |  |  | -108.9122 | 3.545 | -0.06318 | -5.4479 | -12.0826 | -22.9009 | -35.2448 | -47.953 | -60.2326 | -110.1224 | -143.1244 | -161.256 | -80.9842 | 30.4632 | 28.9821 | 26.7316 | 23.7347 | 19.4779 | 11.6558 | 3.4674 | -4.3863 | -31.9853 | -45.8863 | -51.1326 | -100.66 | 12.3211 | 9.8495 | 5.9421 | 0.97054 | -7.5789 | -18.1779 | -29.1021 | -39.6295 | -49.7231 | -57.86 | -64.5495
|  | CHICHESTER BSP | HE |  |  |  |  | -108.8611 | 3.8695 | -0.06522 | -5.4295 | -12.005 | -23.0356 | -35.304 | -47.8724 | -59.9081 | -96.1969 | -121.1366 | -134.6173 | -80.9747 | 30.8474 | 29.2316 | 27.2779 | 24.6684 | 21.2011 | 14.0726 | 6.539 | -0.44631 | -28.7074 | -47.361 | -64.1642 | -100.6284 | 12.6169 | 9.94 | 6.1337 | 1.3 | -6.761 | -17.0031 | -27.5231 | -37.4537 | -68.2168 | -87.0853 | -96.7453
|  | CHICHESTER BSP | FB |  |  |  |  | -106.2805 | 7.7756 | 6.148 | 4.347 | 2.1358 | -0.96012 | -4.552 | -8.2989 | -12.1091 | -37.4315 | -63.4305 | -80.8999 | -79.8368 | 32.3569 | 31.639 | 30.5347 | 29.2232 | 27.3937 | 24.7969 | 20.9926 | 17.0779 | -12.3242 | -50.5831 | -92.1916 | -98.3347 | 16.0811 | 15.1884 | 13.8432 | 12.2021 | 10.1369 | 7.7042 | 4.9179 | 1.879 | -22.6674 | -47.5 | -63.9158
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL BSP | MINIMUM HEADROOM | SY 65479 80511 | NO | NO | 20.316 | 16.2639 | 15.922 | 14.668 | 11.6945 | 7.6965 | 1.3129 | -5.8249 | -13.2076 | -20.1514 | -48.0137 | -70.6994 | -82.9984 | 25.9901 | 25.5659 | 24.6627 | 22.2154 | 18.9996 | 15.0512 | 10.1943 | 4.9627 | 0.25326 | -17.932 | -28.9183 | -53.1067 | 21.6975 | 21.1954 | 20.0154 | 17.4859 | 14.2754 | 9.4006 | 3.2364 | -3.4825 | -9.6562 | -24.6808 | -41.4869 | -50.1165
|  | CHICKERELL BSP | EE |  |  |  |  | 16.322 | 16.1741 | 15.1996 | 12.8669 | 9.5792 | 3.6833 | -2.9504 | -9.7147 | -16.1412 | -41.6678 | -63.1392 | -75.1994 | 28.4753 | 28.2121 | 27.5804 | 25.5274 | 22.8325 | 19.4335 | 15.0937 | 10.556 | 6.36 | -13.6012 | -28.4257 | -38.8144 | 24.3621 | 24.006 | 23.0794 | 21.057 | 18.456 | 14.0856 | 8.8621 | 2.9417 | -2.6134 | -24.6808 | -41.4869 | -50.1165
|  | CHICKERELL BSP | HT |  |  |  |  | 16.2639 | 15.922 | 14.668 | 11.6945 | 7.6965 | 1.3129 | -5.8249 | -13.2076 | -20.1514 | -48.0137 | -70.6994 | -82.9984 | 25.9901 | 25.5659 | 24.6627 | 22.2154 | 18.9996 | 15.0512 | 10.1943 | 4.9627 | 0.25326 | -17.932 | -28.9183 | -32.5867 | 21.6975 | 21.1954 | 20.0154 | 17.4859 | 14.2754 | 9.4006 | 3.2364 | -3.4825 | -9.6562 | -15.7362 | -20.2973 | -24.8562
|  | CHICKERELL BSP | HE |  |  |  |  | 16.3527 | 16.2292 | 15.2955 | 12.8057 | 9.3761 | 3.5588 | -3.0218 | -9.779 | -16.1555 | -35.4035 | -51.9239 | -61.0453 | 26.0554 | 25.7838 | 25.1396 | 23.0059 | 20.2027 | 16.7196 | 12.2954 | 7.6238 | 3.3133 | -13.7646 | -25.7152 | -36.0225 | 21.7617 | 21.4227 | 20.4975 | 18.3143 | 15.5354 | 11.0891 | 5.7775 | -0.31516 | -5.972 | -23.3615 | -36.1615 | -42.9773
|  | CHICKERELL BSP | FB |  |  |  |  | 17.6924 | 18.0751 | 18.2761 | 18.068 | 17.6118 | 16.6986 | 15.4231 | 13.8557 | 11.7751 | -0.71163 | -17.1933 | -30.0596 | 26.6775 | 26.3996 | 26.0196 | 25.4006 | 24.4112 | 22.6796 | 20.2869 | 17.8364 | 14.7617 | -3.1109 | -26.8709 | -53.1067 | 23.1185 | 23.4259 | 23.5554 | 23.3438 | 22.908 | 21.948 | 20.5891 | 19.1227 | 17.168 | 4.3659 | -11.9994 | -24.0931
MELKSHAM GSP | CHIPPENHAM BSP | CHIPPENHAM BSP | MINIMUM HEADROOM | ST 92629 74275 | NO | NO | 71.305 | -17.6872 | 95.0932 | 92.3442 | 88.7829 | 84.5319 | 78.3115 | 71.5993 | 64.5227 | 57.3125 | 34.7268 | 19.7023 | 11.3534 | 3.1369 | 111.6284 | 109.66 | 107.44 | 104.3653 | 100.7937 | 96.4621 | 91.7916 | 86.9021 | 71.6453 | 64.4748 | 46.4474 | -10.961 | 99.4758 | 97.3695 | 94.1569 | 90.1621 | 84.919 | 79.0305 | 72.8484 | 66.4263 | 52.8505 | 41.8273 | 36.3692
|  | CHIPPENHAM BSP | EE |  |  |  |  | -17.6872 | 95.0932 | 92.4268 | 89.2146 | 84.784 | 79.3258 | 73.2013 | 67.188 | 61.1013 | 39.6278 | 25.0789 | 16.8462 | 5.114 | 113.6732 | 111.7977 | 109.8069 | 106.6243 | 103.511 | 99.514 | 95.6263 | 91.4487 | 74.8089 | 65.11 | 58.664 | -8.5033 | 101.9794 | 99.9926 | 97.1375 | 93.0345 | 88.5712 | 83.1763 | 78.0069 | 72.6345 | 53.3304 | 41.8273 | 36.3692
|  | CHIPPENHAM BSP | HT |  |  |  |  | -17.6668 | 95.1095 | 92.3442 | 88.7829 | 84.5319 | 78.3115 | 71.5993 | 64.5227 | 57.3125 | 34.7268 | 19.7023 | 11.3534 | 3.1369 | 111.639 | 109.66 | 107.44 | 104.4937 | 100.7937 | 96.4621 | 91.7916 | 86.9021 | 71.6453 | 64.4748 | 62.6232 | -10.961 | 99.4769 | 97.3695 | 94.1569 | 90.1621 | 84.919 | 79.0305 | 72.8484 | 66.4263 | 60.679 | 56.4137 | 52.8895
|  | CHIPPENHAM BSP | HE |  |  |  |  | -17.6535 | 95.1054 | 92.4585 | 89.2738 | 84.7523 | 79.2921 | 73.2544 | 67.2687 | 61.2125 | 43.2146 | 30.2585 | 23.4809 | 3.1411 | 111.6284 | 109.7211 | 107.7327 | 104.3653 | 101.1095 | 97.0411 | 93.0358 | 88.7221 | 73.8548 | 65.0084 | 58.3242 | -10.9526 | 99.4758 | 97.4527 | 94.5727 | 90.24 | 85.5874 | 80.1158 | 74.8021 | 69.2863 | 52.8505 | 42.8232 | 38.2379
|  | CHIPPENHAM BSP | FB |  |  |  |  | -16.2525 | 97.0452 | 95.9452 | 94.7952 | 92.2993 | 89.5319 | 87.3799 | 84.884 | 82.3758 | 69.5911 | 56.5503 | 48.0207 | 4.0284 | 112.5748 | 111.68 | 110.98 | 108.78 | 106.2895 | 104.2211 | 101.6337 | 98.9474 | 83.6505 | 65.3305 | 46.4474 | -9.7621 | 101.0642 | 100.4369 | 99.8979 | 98.0042 | 95.4432 | 93.4337 | 90.9632 | 88.4653 | 75.2863 | 62.0253 | 53.0916
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ 15716 93165 | NO | NO | 25.573 | 45.8787 | 45.6655 | 44.8042 | 43.0593 | 40.8042 | 35.8848 | 30.5032 | 24.7155 | 19.0063 | -0.3325 | -14.0029 | -19.7652 | 58.0585 | 57.5322 | 56.7448 | 55.469 | 53.6038 | 50.9006 | 47.6511 | 43.9974 | 40.3417 | 29.009 | 15.9385 | -7.4531 | 50.2494 | 49.8484 | 48.9379 | 47.2063 | 44.9547 | 41.0242 | 36.5631 | 31.5789 | 26.6115 | 16.7848 | 6.4236 | 1.2002
|  | CHRISTCHURCH BSP | EE |  |  |  |  | 45.9532 | 45.9889 | 45.2665 | 43.945 | 42.1532 | 37.8287 | 33.0359 | 27.8471 | 22.7093 | 5.0338 | -8.1376 | -15.4039 | 59.4269 | 59.0973 | 58.3861 | 57.3453 | 55.7953 | 53.5739 | 50.8596 | 47.6953 | 44.4892 | 30.5739 | 20.6341 | 11.6973 | 51.895 | 51.7155 | 50.8522 | 49.5165 | 47.7226 | 44.3491 | 40.5226 | 36.2726 | 31.9093 | 16.7848 | 6.4236 | 1.2002
|  | CHRISTCHURCH BSP | HT |  |  |  |  | 45.8787 | 45.6655 | 44.8042 | 43.0593 | 40.8042 | 35.8848 | 30.5032 | 24.7155 | 19.0063 | -0.3325 | -14.0029 | -19.7652 | 58.0585 | 57.5322 | 56.7448 | 55.469 | 53.6038 | 50.9006 | 47.6511 | 43.9974 | 40.3417 | 29.009 | 23.0322 | 21.1553 | 50.2494 | 49.8484 | 48.9379 | 47.2063 | 44.9547 | 41.0242 | 36.5631 | 31.5789 | 26.6115 | 22.44 | 19.2484 | 16.1768
|  | CHRISTCHURCH BSP | HE |  |  |  |  | 45.9808 | 46.0236 | 45.3808 | 43.8971 | 41.8981 | 37.9104 | 33.4175 | 28.5746 | 23.7736 | 9.9899 | -0.94985 | -6.2917 | 58.1101 | 57.748 | 57.088 | 56.0143 | 54.3448 | 52.1038 | 49.3227 | 46.1564 | 42.9417 | 30.8774 | 21.0753 | 11.9985 | 50.3105 | 50.1031 | 49.3442 | 47.8505 | 45.8084 | 42.5494 | 38.7915 | 34.661 | 30.4105 | 18.4484 | 9.7158 | 5.6989
|  | CHRISTCHURCH BSP | FB |  |  |  |  | 46.9063 | 47.3573 | 47.691 | 47.8716 | 47.6257 | 46.9818 | 46.1593 | 45.1665 | 44.0134 | 36.5236 | 24.795 | 16.693 | 58.4259 | 58.0259 | 57.8048 | 57.488 | 56.629 | 55.1585 | 53.508 | 51.708 | 49.5869 | 36.1153 | 15.9385 | -7.4531 | 51.1431 | 51.4842 | 51.7168 | 51.8915 | 51.5915 | 50.8747 | 49.9705 | 48.8715 | 47.5463 | 39.3252 | 27.7694 | 19.8768
IVER 132KV GSP | CIPPENHAM BSP | CIPPENHAM BSP | MINIMUM HEADROOM | SU 96266 79634 | NO | YES | 22.271 | 76.441 | 76.5297 | 76.392 | 76.0655 | 75.6593 | 75.0144 | 74.0379 | 72.944 | 71.894 | 68.1481 | 65.7073 | 64.8165 | 77.9394 | 77.8573 | 77.6268 | 77.2931 | 76.8889 | 76.2089 | 75.1026 | 73.93 | 72.7847 | 68.6731 | 64.8447 | 57.8584 | 72.9352 | 72.8763 | 72.63 | 72.1973 | 71.6794 | 70.9258 | 69.8247 | 68.6615 | 67.5363 | 65.2584 | 62.4277 | 61.1736
|  | CIPPENHAM BSP | EE |  |  |  |  | 76.441 | 76.5297 | 76.442 | 76.2736 | 75.8797 | 75.3614 | 74.5144 | 73.7991 | 73.1277 | 69.3879 | 66.3236 | 64.8165 | 78.5716 | 78.494 | 78.3032 | 78.0389 | 77.644 | 77.1134 | 76.0899 | 75.1736 | 74.2777 | 69.544 | 66.0583 | 63.1757 | 73.7614 | 73.7012 | 73.5022 | 73.2022 | 72.6971 | 72.1012 | 71.0981 | 70.2522 | 69.4267 | 65.3287 | 62.4277 | 61.1736
|  | CIPPENHAM BSP | HT |  |  |  |  | 76.4481 | 76.5369 | 76.392 | 76.0655 | 75.6593 | 75.0144 | 74.0379 | 72.944 | 71.894 | 68.1481 | 65.7073 | 65.1532 | 77.9394 | 77.8573 | 77.6268 | 77.2931 | 76.8889 | 76.2089 | 75.1026 | 73.93 | 72.7847 | 68.6731 | 66.5384 | 65.8394 | 72.9352 | 72.8763 | 72.63 | 72.1973 | 71.6794 | 70.9258 | 69.8247 | 68.6615 | 67.5363 | 66.1489 | 65.3184 | 64.7763
|  | CIPPENHAM BSP | HE |  |  |  |  | 76.4553 | 76.5593 | 76.4869 | 76.294 | 76.0032 | 75.5134 | 74.6961 | 73.9308 | 73.2736 | 70.5114 | 68.3379 | 67.3257 | 77.9405 | 77.8605 | 77.6615 | 77.3826 | 77.0258 | 76.5079 | 75.4405 | 74.4342 | 73.5068 | 69.13 | 65.8984 | 63.0352 | 72.9394 | 72.8889 | 72.6973 | 72.3668 | 71.9068 | 71.3131 | 70.3037 | 69.3763 | 68.5394 | 65.2584 | 63.131 | 62.2342
|  | CIPPENHAM BSP | FB |  |  |  |  | 76.7481 | 77.0032 | 77.1726 | 77.2522 | 77.1797 | 77.0277 | 76.7604 | 76.5542 | 76.3144 | 74.6032 | 70.9471 | 68.5757 | 78.1342 | 78.1637 | 78.1279 | 77.9826 | 77.6458 | 77.1647 | 76.571 | 76.0226 | 75.4215 | 71.4237 | 64.8447 | 57.8584 | 73.2931 | 73.4279 | 73.5279 | 73.5352 | 73.4268 | 73.2131 | 72.8815 | 72.6047 | 72.2721 | 69.9689 | 66.0889 | 63.6994
IVER 132KV GSP | CIPPENHAM B BSP | CIPPENHAM B BSP | MINIMUM HEADROOM | SU 96266 79634 | NO | YES | 34.252 | Demand Headroom Winter (MVA) 2032: 96.214; Demand Headroom Winter (MVA) 2033: 96.214; Demand Headroom Winter (MVA) 2034: 96.214; Demand Headroom Winter (MVA) 2035: 96.214; Demand Headroom Winter (MVA) 2040: 96.214; Demand Headroom Winter (MVA) 2045: 96.214; Demand Headroom Winter (MVA) 2050: 96.214 | [5 empty] | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | [5 empty] | 92.614 | 92.614 | 92.614 | 92.614 | 92.614 | 92.614 | 92.614
|  | CIPPENHAM B BSP | EE |  |  |  |  | Demand Headroom Winter (MVA) 2032: 96.214; Demand Headroom Winter (MVA) 2033: 96.214; Demand Headroom Winter (MVA) 2034: 96.214; Demand Headroom Winter (MVA) 2035: 96.214; Demand Headroom Winter (MVA) 2040: 96.214; Demand Headroom Winter (MVA) 2045: 96.214; Demand Headroom Winter (MVA) 2050: 96.214 | [5 empty] | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | [5 empty] | 92.614 | 92.614 | 92.614 | 92.614 | 92.614 | 92.614 | 92.614
|  | CIPPENHAM B BSP | HT |  |  |  |  | Demand Headroom Winter (MVA) 2032: 96.214; Demand Headroom Winter (MVA) 2033: 96.214; Demand Headroom Winter (MVA) 2034: 96.214; Demand Headroom Winter (MVA) 2035: 96.214; Demand Headroom Winter (MVA) 2040: 96.214; Demand Headroom Winter (MVA) 2045: 96.214; Demand Headroom Winter (MVA) 2050: 96.214 | [5 empty] | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | [5 empty] | 92.614 | 92.614 | 92.614 | 92.614 | 92.614 | 92.614 | 92.614
|  | CIPPENHAM B BSP | HE |  |  |  |  | Demand Headroom Winter (MVA) 2032: 96.214; Demand Headroom Winter (MVA) 2033: 96.214; Demand Headroom Winter (MVA) 2034: 96.214; Demand Headroom Winter (MVA) 2035: 96.214; Demand Headroom Winter (MVA) 2040: 96.214; Demand Headroom Winter (MVA) 2045: 96.214; Demand Headroom Winter (MVA) 2050: 96.214 | [5 empty] | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | [5 empty] | 92.614 | 92.614 | 92.614 | 92.614 | 92.614 | 92.614 | 92.614
|  | CIPPENHAM B BSP | FB |  |  |  |  | Demand Headroom Winter (MVA) 2032: 96.214; Demand Headroom Winter (MVA) 2033: 96.214; Demand Headroom Winter (MVA) 2034: 96.214; Demand Headroom Winter (MVA) 2035: 96.214; Demand Headroom Winter (MVA) 2040: 96.214; Demand Headroom Winter (MVA) 2045: 96.214; Demand Headroom Winter (MVA) 2050: 96.214 | [5 empty] | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | 90.814 | [5 empty] | 92.614 | 92.614 | 92.614 | 92.614 | 92.614 | 92.614 | 92.614
MINETY GSP | CIRENCESTER BSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP 02701 00368 | NO | NO | 15.706 | 51.7181 | 51.5711 | 51.117 | 49.7538 | 48.114 | 45.3681 | 41.6374 | 37.3905 | 29.9191 | 14.816 | -1.3779 | -11.087 | 66.1067 | 65.5498 | 64.7814 | 63.2604 | 61.3846 | 59.0741 | 55.5046 | 50.9067 | 42.0877 | 28.5898 | 17.5046 | 5.6509 | 54.9246 | 54.8141 | 54.5288 | 53.5919 | 51.9614 | 49.2446 | 45.2783 | 40.8056 | 31.7172 | 18.0993 | 6.153 | -4.5228
|  | CIRENCESTER BSP | EE |  |  |  |  | 51.7181 | 51.5966 | 51.1813 | 50.213 | 48.9762 | 46.6946 | 43.9232 | 40.563 | 36.2466 | 20.4313 | 4.0548 | -2.7717 | 67.2714 | 66.7581 | 65.9663 | 64.7091 | 62.9816 | 60.9091 | 58.2734 | 55.1203 | 51.2336 | 37.6795 | 22.901 | 16.5224 | 56.4724 | 56.3938 | 56.1234 | 55.4499 | 54.1867 | 51.8663 | 48.9591 | 45.6122 | 41.5265 | 27.1346 | 11.4112 | 5.7652
|  | CIRENCESTER BSP | HT |  |  |  |  | 51.7354 | 51.5711 | 51.117 | 49.7538 | 48.114 | 45.3681 | 41.6374 | 37.3905 | 31.3854 | 14.816 | -1.3779 | -11.087 | 66.1067 | 65.5498 | 64.7814 | 63.2604 | 61.3846 | 59.0741 | 55.5046 | 51.6183 | 45.8614 | 32.193 | 19.2972 | 12.3772 | 54.9288 | 54.8141 | 54.5288 | 53.5919 | 51.9614 | 49.2446 | 45.2783 | 41.0541 | 34.8877 | 30.1362 | 27.6277 | 25.0814
|  | CIRENCESTER BSP | HE |  |  |  |  | 51.7283 | 51.6374 | 51.3099 | 50.2058 | 48.9344 | 46.517 | 43.1415 | 38.063 | 29.9191 | 15.9874 | 3.1793 | -7.0585 | 66.1067 | 65.5909 | 64.8741 | 63.4814 | 61.8267 | 59.6277 | 56.2404 | 50.9067 | 42.0877 | 28.5898 | 17.5046 | 5.6509 | 54.9246 | 54.8541 | 54.6425 | 53.8646 | 52.6214 | 50.1183 | 46.4341 | 40.8056 | 31.7172 | 18.0993 | 6.153 | -4.5228
|  | CIRENCESTER BSP | FB |  |  |  |  | 52.6323 | 52.9436 | 53.0477 | 52.864 | 52.6242 | 52.2385 | 51.4844 | 50.4691 | 48.9364 | 41.5589 | 30.2823 | 22.3007 | 66.7246 | 66.7709 | 66.5793 | 66.0635 | 65.3688 | 64.5467 | 63.3341 | 61.5741 | 59.1888 | 48.0162 | 33.0277 | 18.4109 | 55.7425 | 56.0077 | 56.1351 | 56.0625 | 55.8277 | 55.4035 | 54.6593 | 53.6362 | 52.0162 | 43.6467 | 31.8246 | 23.2888
FAWLEY GSP | COWES BSP | COWES BSP | MINIMUM HEADROOM | SZ 50486 94250 | NO | NO | 5.182 | 25.8908 | 25.849 | 25.1806 | 24.1602 | 22.7959 | 20.402 | 17.9316 | 15.3796 | 12.9031 | 3.1735 | -4.8653 | -8.949 | 31.6342 | 31.5563 | 31.0595 | 30.4826 | 29.4974 | 28.1142 | 26.5679 | 25.0153 | 23.5363 | 18.1426 | 14.9626 | 8.1468 | 29.4937 | 29.4916 | 28.8716 | 27.9642 | 26.5695 | 24.4411 | 22.2432 | 20.0663 | 17.9474 | 12.8806 | 7.2592 | 4.7582
|  | COWES BSP | EE |  |  |  |  | 25.8908 | 25.8531 | 25.2194 | 24.3245 | 23.1153 | 20.899 | 18.7 | 16.3245 | 14.0867 | 5.5194 | -1.9949 | -5.9898 | 32.3449 | 32.2837 | 31.851 | 31.3776 | 30.548 | 29.3153 | 27.9622 | 26.5224 | 25.198 | 19.3541 | 15.0071 | 12.2827 | 30.3286 | 30.3347 | 29.7755 | 29.0112 | 27.8224 | 25.8898 | 23.9561 | 21.9357 | 20.0643 | 12.8806 | 7.2592 | 4.7582
|  | COWES BSP | HT |  |  |  |  | 25.9 | 25.849 | 25.1806 | 24.1602 | 22.7959 | 20.402 | 17.9316 | 15.3796 | 12.9031 | 3.1735 | -4.8653 | -8.949 | 31.6342 | 31.5563 | 31.0595 | 30.4826 | 29.4974 | 28.1142 | 26.5679 | 25.0153 | 23.5363 | 18.1426 | 14.9626 | 14.4111 | 29.4937 | 29.4916 | 28.8716 | 27.9642 | 26.5695 | 24.4411 | 22.2432 | 20.0663 | 17.9474 | 15.6305 | 14.22 | 12.8021
|  | COWES BSP | HE |  |  |  |  | 25.9051 | 25.8765 | 25.2408 | 24.3143 | 23.0663 | 20.8755 | 18.652 | 16.2796 | 14.1102 | 7.3031 | 1.2112 | -2.1918 | 31.6405 | 31.5763 | 31.1163 | 30.6321 | 29.7763 | 28.5437 | 27.1068 | 25.6237 | 24.3289 | 19.0879 | 15.4942 | 12.4247 | 29.4989 | 29.5147 | 28.9326 | 28.1253 | 26.8695 | 24.9284 | 22.8895 | 20.8158 | 18.9705 | 13.0137 | 8.6042 | 6.2663
|  | COWES BSP | FB |  |  |  |  | 26.4306 | 26.6265 | 26.501 | 26.2633 | 25.8265 | 25.2847 | 25.0102 | 24.6571 | 24.2673 | 20.6847 | 15.0429 | 11.2867 | 31.99 | 31.9626 | 31.7458 | 31.5258 | 31.0658 | 30.4574 | 29.8837 | 29.2279 | 28.5121 | 23.1795 | 15.7668 | 8.1468 | 30.0126 | 30.1937 | 30.1505 | 30.0432 | 29.62 | 29.0505 | 28.7 | 28.2326 | 27.7316 | 23.5274 | 18.0684 | 14.4189
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | COWLEY LOCAL (RESERVE) BSP | MINIMUM HEADROOM | SP 56113 03074 | NO | NO | 32.929 | 68.8803 | 67.5966 | 66.3252 | 64.7109 | 62.7119 | 59.7956 | 54.5374 | 45.2833 | 26.1507 | 5.7017 | -16.8605 | -41.0871 | 71.3541 | 70.8457 | 70.3604 | 69.6794 | 68.3215 | 66.6551 | 61.9046 | 52.0646 | 29.5741 | 8.732 | -15.2227 | -44.8133 | 68.8394 | 67.912 | 66.9583 | 65.6215 | 63.8394 | 61.4741 | 56.0625 | 45.4088 | 22.1951 | 0.023568 | -25.1101 | -54.2606
|  | COWLEY LOCAL (RESERVE) BSP | EE |  |  |  |  | 69.0548 | 68.2395 | 67.016 | 65.3752 | 63.5262 | 60.4895 | 56.5313 | 51.2833 | 44.6374 | 25.4272 | -4.2779 | -16.3503 | 72.1231 | 71.8558 | 71.4833 | 70.9272 | 69.9517 | 68.414 | 65.6946 | 61.4058 | 55.2466 | 38.467 | 5.6262 | -7.4473 | 69.6935 | 69.2027 | 68.3323 | 67.1333 | 65.6405 | 63.3221 | 59.8497 | 54.7895 | 47.9191 | 29.1282 | -4.6462 | -17.5177
|  | COWLEY LOCAL (RESERVE) BSP | HT |  |  |  |  | 68.8803 | 67.5966 | 66.3252 | 64.7109 | 62.7119 | 59.7956 | 54.5374 | 48.7068 | 38.2497 | 15.9425 | -13.0024 | -33.1452 | 71.3541 | 70.8457 | 70.3604 | 69.6794 | 68.3215 | 66.6551 | 61.9046 | 56.4615 | 44.9678 | 25.3625 | -5.3891 | -26.8122 | 68.8394 | 67.912 | 66.9583 | 65.6215 | 63.8394 | 61.4741 | 56.0625 | 49.952 | 37.8109 | 32.0509 | 28.7867 | 24.5404
|  | COWLEY LOCAL (RESERVE) BSP | HE |  |  |  |  | 69.0548 | 68.2435 | 67.1976 | 65.6864 | 63.9231 | 61.0538 | 55.8068 | 45.2833 | 26.1507 | 5.7017 | -16.8605 | -41.0871 | 71.4888 | 71.213 | 70.8804 | 70.3562 | 69.4004 | 67.9278 | 63.373 | 52.0646 | 29.5741 | 8.732 | -15.2227 | -44.8133 | 68.932 | 68.4204 | 67.6478 | 66.4983 | 65.0257 | 62.7867 | 57.4836 | 45.4088 | 22.1951 | 0.023568 | -25.1101 | -54.2606
|  | COWLEY LOCAL (RESERVE) BSP | FB |  |  |  |  | 69.714 | 69.5619 | 68.7935 | 68.1129 | 67.3844 | 66.3231 | 64.6395 | 62.6731 | 59.1793 | 45.8303 | 30.117 | 17.1435 | 71.7236 | 71.6373 | 71.353 | 71.0825 | 70.7667 | 70.0657 | 68.412 | 66.3973 | 62.4183 | 48.3688 | 30.1204 | 12.1646 | 69.312 | 69.2257 | 68.8183 | 68.3562 | 67.8551 | 67.0236 | 65.3425 | 63.2909 | 59.2762 | 45.1783 | 28.0067 | 13.2036
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL (MAIN) BSP | MINIMUM HEADROOM | SP 56113 03074 | NO | NO | 70.432 | 5.779 | 5.1627 | 4.8168 | 118.3964 | 114.9913 | 110.3801 | 105.2668 | 99.6423 | 94.0535 | 77.7495 | 70.5576 | 67.8311 | 18.6034 | 17.8634 | 17.1803 | 126.0013 | 123.0961 | 119.6392 | 115.6498 | 111.0908 | 106.535 | 93.8855 | 84.8561 | 68.8845 | 7.6424 | 7.035 | 6.4592 | 116.8887 | 113.7592 | 109.6813 | 105.054 | 99.7655 | 94.435 | 84.2382 | 76.226 | 72.6331
|  | COWLEY LOCAL (MAIN) BSP | EE |  |  |  |  | 5.779 | 5.1627 | 4.8168 | 118.5658 | 116.8342 | 112.6729 | 108.2688 | 103.8372 | 99.4872 | 80.975 | 71.8658 | 67.8311 | 20.2944 | 19.6209 | 19.0301 | 128.0505 | 126.7862 | 123.8464 | 120.4903 | 116.9862 | 113.4913 | 97.1607 | 89.3148 | 82.7556 | 9.6586 | 9.0362 | 8.525 | 119.1658 | 117.626 | 114.0648 | 110.2199 | 106.2352 | 102.2178 | 84.2382 | 76.226 | 72.6331
|  | COWLEY LOCAL (MAIN) BSP | HT |  |  |  |  | 5.8607 | 5.2862 | 4.8403 | 118.3964 | 114.9913 | 110.3801 | 105.2668 | 99.6423 | 94.0535 | 77.7495 | 70.5576 | 68.626 | 18.6034 | 17.8634 | 17.1803 | 126.0013 | 123.0961 | 119.6392 | 115.6498 | 111.0908 | 106.535 | 93.8855 | 88.695 | 87.0087 | 7.6592 | 7.0624 | 6.4592 | 116.8887 | 113.7592 | 109.6813 | 105.054 | 99.7655 | 94.435 | 89.6434 | 86.7708 | 83.9719
|  | COWLEY LOCAL (MAIN) BSP | HE |  |  |  |  | 5.8239 | 5.2464 | 4.9433 | 118.676 | 116.926 | 112.8668 | 108.6403 | 104.2597 | 99.9413 | 84.4882 | 78.0974 | 75.6209 | 18.6319 | 17.9371 | 17.3466 | 126.3477 | 125.0455 | 121.9529 | 118.5224 | 114.8066 | 111.0813 | 96.0498 | 89.0255 | 83.2255 | 7.6424 | 7.035 | 6.5498 | 117.1434 | 115.5266 | 111.8866 | 108.0403 | 103.9077 | 99.7224 | 84.3108 | 78.6687 | 76.6982
|  | COWLEY LOCAL (MAIN) BSP | FB |  |  |  |  | 6.5352 | 6.1586 | 6.1148 | 120.725 | 120.0484 | 118.6066 | 116.2872 | 113.8444 | 111.5086 | 97.1311 | 87.7311 | 82.0137 | 19.0266 | 18.3034 | 17.7498 | 127.0708 | 126.0087 | 124.4971 | 122.0624 | 119.4371 | 116.8487 | 99.5203 | 84.8561 | 68.8845 | 8.4771 | 8.0119 | 7.854 | 119.2087 | 118.4224 | 117.1708 | 115.0845 | 112.7971 | 110.5319 | 95.5477 | 86.1645 | 80.2129
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU 78324 50817 | NO | YES | 23.249 | 42.8883 | 43.2312 | 42.4383 | 155.3177 | 153.4891 | 150.3228 | 146.5666 | 142.6075 | 138.6564 | 125.8962 | 117.6615 | 114.3972 | 57.8813 | 57.895 | 56.7813 | 165.0392 | 163.3097 | 160.9192 | 157.854 | 154.5782 | 151.5003 | 141.8276 | 133.8234 | 117.4392 | 46.274 | 46.575 | 45.6519 | 155.5582 | 153.6687 | 150.7687 | 147.175 | 143.3729 | 139.774 | 133.9908 | 127.7722 | 124.9794
|  | COXMOOR WOOD BSP | EE |  |  |  |  | 42.8883 | 43.2608 | 42.8067 | 156.2207 | 155.0717 | 152.4983 | 149.5248 | 146.1738 | 142.9228 | 131.0687 | 122.5962 | 118.5901 | 59.3151 | 59.3518 | 58.4375 | 166.9947 | 165.6488 | 163.5875 | 161.0906 | 158.2947 | 155.7202 | 144.7396 | 137.3375 | 131.6977 | 48.1039 | 48.409 | 47.7753 | 158.161 | 156.8161 | 154.4202 | 151.5722 | 148.3957 | 145.4732 | 134.6886 | 127.7722 | 124.9794
|  | COXMOOR WOOD BSP | HT |  |  |  |  | 42.8924 | 43.2312 | 42.4383 | 155.3177 | 153.4891 | 150.3228 | 146.5666 | 142.6075 | 138.6564 | 125.8962 | 117.6615 | 114.3972 | 57.8813 | 57.895 | 56.7813 | 165.0392 | 163.3097 | 160.9192 | 157.854 | 154.5782 | 151.5003 | 141.8276 | 137.1234 | 135.9424 | 46.274 | 46.575 | 45.6519 | 155.5582 | 153.6687 | 150.7687 | 147.175 | 143.3729 | 139.774 | 136.3424 | 133.9624 | 131.8613
|  | COXMOOR WOOD BSP | HE |  |  |  |  | 42.9046 | 43.2832 | 42.8455 | 156.1615 | 154.9034 | 152.4105 | 149.4911 | 146.1758 | 143.0207 | 133.1452 | 126.0891 | 123.0472 | 57.8897 | 57.9255 | 56.9845 | 165.4887 | 164.0624 | 162.0076 | 159.4361 | 156.5497 | 153.9666 | 143.6929 | 136.7634 | 130.8529 | 46.2824 | 46.6066 | 45.9729 | 156.2497 | 154.7645 | 152.3992 | 149.4876 | 146.2308 | 143.3245 | 133.9908 | 128.2182 | 125.9708
|  | COXMOOR WOOD BSP | FB |  |  |  |  | 43.8791 | 44.3883 | 44.8699 | 159.634 | 159.6024 | 159.1228 | 158.6309 | 157.9656 | 156.9819 | 150.2034 | 140.8636 | 135.3421 | 58.515 | 58.3929 | 58.2782 | 168.0224 | 167.2771 | 165.8529 | 164.4782 | 162.9476 | 161.0403 | 149.3529 | 133.8234 | 117.4392 | 47.2761 | 47.7171 | 48.1266 | 160.135 | 160.0413 | 159.2813 | 158.5866 | 157.6876 | 156.3761 | 148.5824 | 139.3192 | 133.8676
IVER 132KV GSP | DENHAM B BSP | DENHAM B BSP | MINIMUM HEADROOM | TQ 01785 87618 | NO | YES | 4.821 |  |  |  | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 |  |  |  | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 |  |  |  | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6
|  | DENHAM B BSP | EE | [7 empty] | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 |  |  |  | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 |  |  |  | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6
|  | DENHAM B BSP | HT | [7 empty] | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 |  |  |  | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 |  |  |  | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6
|  | DENHAM B BSP | HE | [7 empty] | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 |  |  |  | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 |  |  |  | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6
|  | DENHAM B BSP | FB | [7 empty] | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 | 114.2 |  |  |  | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 |  |  |  | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6 | 110.6
IVER 132KV GSP | DENHAM BSP | DENHAM BSP | MINIMUM HEADROOM | TQ 01785 87618 | NO | YES | 11.488 | 57.4768 | 57.634 | 76.5664 | 75.7807 | 74.8215 | 72.1348 | 69.094 | 65.6144 | 62.2736 | 50.3103 | 41.0736 | 36.246 | 68.4986 | 68.4438 | 86.6649 | 86.148 | 85.607 | 84.3512 | 82.7522 | 80.647 | 78.7754 | 72.6691 | 70.0386 | 66.9459 | 60.2291 | 60.2943 | 78.9175 | 78.2407 | 77.4228 | 75.2354 | 72.6501 | 69.7333 | 67.0733 | 61.4996 | 55.8712 | 53.4513
|  | DENHAM BSP | EE |  |  |  |  | 57.4768 | 57.6901 | 76.7491 | 76.3572 | 75.8093 | 73.5185 | 70.8011 | 67.5225 | 64.3725 | 53.2603 | 44.4378 | 39.643 | 69.7125 | 69.7176 | 87.9819 | 87.6881 | 87.2891 | 86.2921 | 84.9085 | 82.9523 | 81.3319 | 74.7697 | 71.1411 | 68.8299 | 61.7462 | 61.8738 | 80.5432 | 80.2023 | 79.6819 | 77.8972 | 75.6554 | 72.9493 | 70.5493 | 62.0217 | 56.186 | 53.4513
|  | DENHAM BSP | HT |  |  |  |  | 57.4778 | 57.634 | 76.5664 | 75.7807 | 74.8215 | 72.1348 | 69.094 | 65.6144 | 62.2736 | 50.3103 | 41.0736 | 36.246 | 68.4996 | 68.4438 | 86.6649 | 86.148 | 85.607 | 84.3512 | 82.7522 | 80.647 | 78.7754 | 72.6691 | 70.0386 | 69.5217 | 60.2291 | 60.2943 | 78.9175 | 78.2407 | 77.4228 | 75.2354 | 72.6501 | 69.7333 | 67.0733 | 64.2807 | 62.6543 | 61.0933
|  | DENHAM BSP | HE |  |  |  |  | 57.4778 | 57.7646 | 76.7521 | 76.2297 | 75.5725 | 73.1032 | 70.2072 | 66.947 | 63.7011 | 54.8695 | 46.8093 | 43.2848 | 68.4986 | 68.5891 | 86.7565 | 86.4333 | 86.048 | 84.9712 | 83.5091 | 81.7522 | 80.1354 | 74.3775 | 70.4965 | 67.7354 | 60.2291 | 60.4449 | 79.0059 | 78.5954 | 78.0259 | 76.0722 | 73.627 | 70.9965 | 68.5122 | 61.4996 | 55.8712 | 53.5859
|  | DENHAM BSP | FB |  |  |  |  | 58.3493 | 58.833 | 78.2827 | 78.6093 | 78.8144 | 78.7164 | 78.544 | 78.0562 | 77.6287 | 74.0736 | 68.6378 | 66.0981 | 69.1501 | 69.3122 | 87.6922 | 87.7638 | 87.6859 | 87.3196 | 86.8954 | 86.1438 | 85.4543 | 80.5554 | 73.4733 | 66.9459 | 61.1543 | 61.6059 | 80.5733 | 80.8575 | 81.0891 | 81.0154 | 80.8733 | 80.3691 | 79.8501 | 75.887 | 70.6522 | 68.3691
COWLEY GSP | DRAYTON BSP | DRAYTON BSP | MINIMUM HEADROOM | SU 46684 92706 | NO | NO | 76.875 | -27.396 | -29.8011 | -48.6797 | -53.1021 | -57.2746 | -62.899 | -69.847 | -78.0654 | -89.149 | -112.1695 | -134.2552 | -146.8848 | -6.016 | -7.917 | -27.4304 | -34.0339 | -37.1623 | -40.9939 | -46.4518 | -52.5907 | -62.797 | -83.3897 | -99.3918 | -115.6654 | -22.6065 | -24.397 | -43.7019 | -50.7623 | -54.3475 | -59.2423 | -65.7265 | -73.2254 | -85.1475 | -106.3623 | -122.4202 | -134.9497
|  | DRAYTON BSP | EE |  |  |  |  | -27.2644 | -29.3644 | -48.6797 | -52.1909 | -56.4072 | -62.3766 | -69.3797 | -76.9031 | -84.1746 | -109.4368 | -131.6878 | -141.1297 | -3.5519 | -5.1366 | -27.4304 | -29.5121 | -32.4008 | -36.0651 | -41.0559 | -46.7672 | -52.5927 | -74.3355 | -94.8713 | -105.6162 | -19.6549 | -21.21 | -43.7019 | -46.1253 | -49.4151 | -54.2906 | -60.4876 | -67.3447 | -74.1713 | -97.6519 | -119.0355 | -127.1855
|  | DRAYTON BSP | HT |  |  |  |  | -27.396 | -29.8011 | -32.7684 | -53.1021 | -57.2746 | -62.899 | -69.847 | -77.3521 | -85.8093 | -112.1695 | -134.2552 | -146.8848 | -6.016 | -7.917 | -10.0475 | -34.0339 | -37.1623 | -40.9939 | -46.4518 | -52.5907 | -60.2802 | -80.8349 | -98.0318 | -107.237 | -22.6065 | -24.397 | -26.5654 | -50.7623 | -54.3475 | -59.2423 | -65.7265 | -72.916 | -81.5718 | -88.7728 | -93.536 | -97.4802
|  | DRAYTON BSP | HE |  |  |  |  | -27.2582 | -29.3419 | -32.2582 | -35.7572 | -55.649 | -61.9297 | -69.1184 | -78.0654 | -89.149 | -110.895 | -127.947 | -139.8766 | -5.8086 | -7.4486 | -9.376 | -11.5202 | -34.9823 | -38.997 | -44.1897 | -51.9181 | -62.797 | -83.3897 | -99.3918 | -115.6654 | -22.4612 | -24.0644 | -26.1623 | -28.6697 | -52.5033 | -57.8286 | -64.317 | -73.2254 | -85.1475 | -106.3623 | -122.4202 | -134.9497
|  | DRAYTON BSP | FB |  |  |  |  | -25.8072 | -26.747 | -28.2317 | -29.7705 | -31.7174 | -50.8797 | -54.1827 | -57.3562 | -60.6001 | -75.5256 | -91.6307 | -101.348 | -5.1444 | -6.3075 | -7.7012 | -8.9897 | -10.9844 | -34.7202 | -38.0444 | -41.2823 | -44.9686 | -63.1044 | -85.7949 | -108.3612 | -21.2444 | -21.937 | -23.0454 | -24.1107 | -25.6823 | -49.0033 | -51.7297 | -54.4739 | -57.8328 | -73.236 | -89.8286 | -100.1539
EALING GSP | EALING BSP | EALING BSP | MINIMUM HEADROOM | TQ 18371 79475 | NO | NO | 20.869 | 33.5862 | 33.0964 | 32.7872 | 32.2189 | 30.7852 | 29.0107 | 27.0148 | 24.7474 | 22.6934 | 15.6944 | 9.274 | 5.8362 | 41.4056 | 40.8551 | 40.5361 | 39.9309 | 38.4561 | 36.8319 | 34.7972 | 32.4582 | 30.3835 | 22.4172 | 7.214 | -14.4733 | 36.0172 | 35.6056 | 35.4203 | 34.9445 | 33.4867 | 31.8435 | 29.8877 | 27.633 | 25.634 | 20.4158 | 14.4311 | 11.2352
|  | EALING BSP | EE |  |  |  |  | 33.5862 | 33.2393 | 32.7872 | 32.2189 | 31.2189 | 29.7372 | 28.0668 | 26.1556 | 24.5005 | 15.6944 | 9.274 | 5.8362 | 42.5342 | 42.1964 | 41.7689 | 41.1576 | 40.1872 | 38.8678 | 37.1372 | 35.1138 | 33.3842 | 23.6985 | 15.8076 | 7.1036 | 37.2832 | 37.0168 | 36.6536 | 36.1709 | 35.276 | 33.9546 | 32.326 | 30.4383 | 28.8372 | 20.4158 | 14.4311 | 11.2352
|  | EALING BSP | HT |  |  |  |  | 33.6474 | 33.0964 | 32.8372 | 32.3117 | 30.7852 | 29.0107 | 27.0148 | 24.7474 | 22.6934 | 16.0883 | 11.5536 | 10.0107 | 41.4056 | 40.8551 | 40.5361 | 39.9309 | 38.4561 | 36.8319 | 34.7972 | 32.4582 | 30.3835 | 24.5814 | 20.5814 | 18.2961 | 36.0509 | 35.6056 | 35.4203 | 34.9445 | 33.4867 | 31.8435 | 29.8877 | 27.633 | 25.634 | 23.7435 | 22.6909 | 21.3656
|  | EALING BSP | HE |  |  |  |  | 33.6138 | 33.2913 | 32.926 | 32.3729 | 31.3332 | 29.8383 | 28.2097 | 26.3464 | 24.7301 | 18.5015 | 14.3821 | 11.9403 | 41.4056 | 41.0603 | 40.653 | 40.0509 | 39.0456 | 37.6319 | 35.8551 | 33.7603 | 31.9519 | 23.0603 | 15.7961 | 7.3382 | 36.0172 | 35.7698 | 35.4667 | 34.9782 | 34.0098 | 32.6267 | 30.9909 | 29.0845 | 27.4603 | 21.2414 | 17.3172 | 15.1267
|  | EALING BSP | FB |  |  |  |  | 34.1189 | 34.0464 | 34.0015 | 33.676 | 33.1954 | 32.6352 | 32.0648 | 31.3066 | 30.7556 | 25.6811 | 19.9485 | 15.2117 | 41.4761 | 41.0993 | 40.6445 | 39.9835 | 39.0709 | 37.8993 | 36.4403 | 34.8003 | 33.3256 | 22.4172 | 7.214 | -14.4733 | 36.5782 | 36.5793 | 36.5667 | 36.3203 | 35.9435 | 35.4919 | 34.9488 | 34.1688 | 33.6172 | 28.4519 | 22.7635 | 18.1288
LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT BSP | MINIMUM HEADROOM | TQ 08394 73826 | NO | NO | 28.849 | -9.8512 | -9.8502 | -10.1257 | -10.689 | -11.6236 | -13.4104 | -15.6308 | -18.2869 | -20.9165 | -30.8063 | -38.0879 | -40.9471 | 1.4264 | 3.8969 | 3.5485 | 2.8643 | 1.7885 | 0.039021 | -2.181 | -4.861 | -7.5462 | -17.0725 | -30.8241 | -51.2252 | -5.962 | -4.4641 | -4.6936 | -5.3757 | -6.4168 | -8.2368 | -10.4883 | -13.1905 | -16.2073 | -24.9725 | -32.1704 | -34.8429
|  | EAST BEDFONT BSP | EE |  |  |  |  | -9.8512 | -9.789 | -10.1257 | -10.689 | -11.293 | -12.7094 | -14.8277 | -17.243 | -19.5512 | -30.8063 | -38.0879 | -40.9471 | 3.1786 | 5.8133 | 5.3296 | 4.6857 | 4.0367 | 2.6735 | 0.4755 | -1.9837 | -4.4572 | -17.0725 | -25.8837 | -33.7306 | -3.9816 | -2.3827 | -2.7674 | -3.4092 | -4.0214 | -5.4612 | -7.6755 | -10.1663 | -12.8123 | -24.9725 | -32.1704 | -34.8429
|  | EAST BEDFONT BSP | HT |  |  |  |  | -9.8032 | -9.8502 | -10.0114 | -10.6155 | -11.6236 | -13.4104 | -15.6308 | -18.2869 | -20.9165 | -30.2838 | -35.842 | -37.2022 | 1.4295 | 3.8969 | 3.5485 | 2.8643 | 1.7885 | 0.039021 | -2.181 | -4.861 | -7.5462 | -16.2978 | -21.1557 | -23.0483 | -5.9526 | -4.4641 | -4.6778 | -5.3715 | -6.4168 | -8.2368 | -10.4883 | -13.1905 | -16.2073 | -19.221 | -21.2483 | -22.9094
|  | EAST BEDFONT BSP | HE |  |  |  |  | -9.8114 | -9.7043 | -10.0083 | -10.5941 | -11.1614 | -12.492 | -14.3155 | -16.3951 | -18.4379 | -26.1583 | -30.4543 | -32.8196 | 1.4264 | 4.0559 | 3.5601 | 2.898 | 2.2611 | 0.89376 | -1.0494 | -3.2336 | -5.5083 | -16.0136 | -23.421 | -31.5168 | -5.962 | -4.3368 | -4.6936 | -5.3757 | -5.9852 | -7.3936 | -9.3262 | -11.4957 | -13.9041 | -22.4862 | -26.6915 | -28.9315
|  | EAST BEDFONT BSP | FB |  |  |  |  | -9.1849 | -8.8634 | -8.8053 | -8.8298 | -8.8155 | -9.1961 | -9.7492 | -10.693 | -11.6196 | -17.9716 | -24.4267 | -29.5502 | 1.5706 | 4.1432 | 3.7201 | 3.1801 | 2.5201 | 1.398 | 0.033758 | -1.621 | -3.3599 | -15.1778 | -30.8241 | -51.2252 | -5.2599 | -3.3926 | -3.3936 | -3.4231 | -3.4136 | -3.8241 | -4.3978 | -5.4126 | -6.3768 | -13.181 | -20.1336 | -26.1105
LOVEDEAN GSP | FAREHAM (MAIN) BSP | FAREHAM (MAIN) BSP | MINIMUM HEADROOM | SU 56534 04031 | NO | YES | 55.596 | 7.1448 | 6.4061 | 5.2826 | 2.8785 | 0.3683 | -4.4348 | -10.4929 | -16.9358 | -22.7837 | -44.2256 | -56.297 | -61.2235 | 19.2758 | 18.3295 | 17.2758 | 15.5274 | 13.2547 | 9.8431 | 5.5189 | 0.75051 | -3.4379 | -18.2569 | -29.719 | -54.1474 | 10.3189 | 9.6284 | 8.781 | 6.5326 | 4.0368 | -0.10107 | -5.2548 | -10.9242 | -16.0421 | -28.9835 | -39.211 | -44.2376
|  | FAREHAM (MAIN) BSP | EE |  |  |  |  | 7.2295 | 7.1132 | 6.2326 | 4.3112 | 2.3336 | -2.149 | -7.3888 | -13.6511 | -19.1899 | -41.0797 | -53.4572 | -59.9541 | 21.2053 | 20.691 | 19.7981 | 18.3247 | 16.4012 | 13.439 | 9.7624 | 5.4951 | 1.8634 | -16.1998 | -26.8019 | -36.0253 | 12.5604 | 12.3257 | 11.6502 | 9.8563 | 7.8685 | 4.1736 | -0.18146 | -5.3274 | -9.8335 | -28.9835 | -39.211 | -44.2376
|  | FAREHAM (MAIN) BSP | HT |  |  |  |  | 7.1448 | 6.4061 | 5.2826 | 2.8785 | 0.3683 | -4.4348 | -10.4929 | -16.9358 | -22.7837 | -44.2256 | -56.297 | -61.2235 | 19.2758 | 18.3295 | 17.2758 | 15.5274 | 13.2547 | 9.8431 | 5.5189 | 0.75051 | -3.4379 | -18.2569 | -24.9095 | -26.9526 | 10.3189 | 9.6284 | 8.781 | 6.5326 | 4.0368 | -0.10107 | -5.2548 | -10.9242 | -16.0421 | -21.6379 | -25.7242 | -29.1779
|  | FAREHAM (MAIN) BSP | HE |  |  |  |  | 7.2561 | 7.1479 | 6.5469 | 4.6989 | 2.5459 | -1.4164 | -6.3633 | -11.8164 | -16.7848 | -33.3388 | -43.6164 | -49.1807 | 19.3326 | 18.78 | 17.9937 | 16.5768 | 14.5305 | 11.7589 | 8.0884 | 3.9989 | 0.21367 | -15.7305 | -25.5716 | -35.159 | 10.401 | 10.161 | 9.6663 | 7.8705 | 5.6631 | 2.2674 | -2.0011 | -6.74 | -11.0316 | -26.2463 | -34.4505 | -38.6548
|  | FAREHAM (MAIN) BSP | FB |  |  |  |  | 8.6173 | 8.9612 | 9.0999 | 9.0479 | 8.8581 | 7.7601 | 6.6428 | 5.1765 | 3.5989 | -8.4235 | -21.9888 | -31.399 | 20.14 | 19.7263 | 19.1126 | 18.4421 | 17.4716 | 15.6095 | 13.6968 | 11.5074 | 9.1221 | -7.999 | -29.719 | -54.1474 | 11.7116 | 11.9537 | 11.9916 | 11.6084 | 10.9958 | 10.0547 | 9.121 | 7.8768 | 6.2852 | -5.5884 | -18.6463 | -27.9074
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | FAREHAM (RESERVE) BSP | MINIMUM HEADROOM | SU 56534 04031 | NO | YES | 39.545 | 18.2279 | 18.1228 | 17.734 | 16.8759 | 15.8361 | 14.1534 | 12.2024 | 9.8238 | 7.6769 | -1.6935 | -8.1598 | -10.5507 | 23.448 | 23.0585 | 22.4311 | 21.6269 | 20.5133 | 18.9985 | 17.2154 | 15.148 | 13.4375 | 6.5817 | -3.7899 | -19.3783 | 33.0154 | 32.7206 | 32.0585 | 31.0185 | 29.7017 | 27.8901 | 25.8269 | 23.5185 | 21.6048 | 15.9075 | 9.7014 | 6.7932
|  | FAREHAM (RESERVE) BSP | EE |  |  |  |  | 18.2728 | 18.4279 | 18.0453 | 17.4993 | 16.683 | 15.2167 | 13.4238 | 11.0646 | 9.184 | 0.41975 | -6.9823 | -10.5507 | 24.231 | 24.0616 | 23.4126 | 22.7851 | 21.7483 | 20.4279 | 18.7534 | 16.8157 | 15.3381 | 7.0412 | 0.11261 | -5.9996 | 33.533 | 33.4534 | 32.8024 | 32.0453 | 30.9289 | 29.381 | 27.4544 | 25.333 | 23.7014 | 15.9075 | 9.7014 | 6.7932
|  | FAREHAM (RESERVE) BSP | HT |  |  |  |  | 18.2279 | 18.1228 | 17.734 | 16.8759 | 15.8361 | 14.1534 | 12.2024 | 9.8238 | 7.6769 | -1.6935 | -8.1598 | -10.3231 | 23.448 | 23.0585 | 22.4311 | 21.6269 | 20.5133 | 18.9985 | 17.2154 | 15.148 | 13.4375 | 6.8038 | 2.7743 | 1.388 | 33.0154 | 32.7206 | 32.0585 | 31.0185 | 29.7017 | 27.8901 | 25.8269 | 23.5185 | 21.6048 | 19.3101 | 17.8217 | 16.0596
|  | FAREHAM (RESERVE) BSP | HE |  |  |  |  | 18.3208 | 18.5044 | 18.1861 | 17.63 | 16.7902 | 15.5075 | 13.8422 | 11.5442 | 9.731 | 2.9014 | -1.4813 | -3.9262 | 23.5038 | 23.3143 | 22.6733 | 22.0375 | 20.9775 | 19.6301 | 17.9322 | 15.9175 | 14.3701 | 6.5817 | 0.90799 | -5.2689 | 33.0901 | 33.0269 | 32.4111 | 31.6196 | 30.4427 | 28.9469 | 27.0627 | 24.9185 | 23.2806 | 16.6606 | 13.1448 | 11.1385
|  | FAREHAM (RESERVE) BSP | FB |  |  |  |  | 18.8493 | 19.0759 | 19.2412 | 19.2667 | 19.1259 | 18.8483 | 18.5565 | 18.134 | 17.7044 | 13.8973 | 7.1187 | 2.0075 | 23.7385 | 23.4038 | 23.029 | 22.5796 | 21.7954 | 20.7985 | 19.8154 | 18.6933 | 17.4764 | 8.9459 | -3.7899 | -19.3783 | 33.6122 | 33.6133 | 33.548 | 33.2448 | 32.8817 | 32.5227 | 32.1385 | 31.6343 | 30.9038 | 26.2059 | 19.6869 | 14.8248
FLEET-BRAMLEY GSP | FERNHURST BSP | FERNHURST BSP | MINIMUM HEADROOM | SU 72730 39772 | NO | NO | 41.363 | 24.0264 | 24.2661 | 23.1529 | 27.3868 | 25.0041 | 21.3746 | 17.1868 | 12.7919 | 8.2868 | -4.9356 | -14.4999 | -18.8826 | 43.4705 | 43.1084 | 41.54 | 50.3673 | 47.9536 | 45.0252 | 41.4831 | 37.8 | 34.0768 | 22.721 | 16.9968 | 3.9726 | 31.5021 | 31.5431 | 30.2663 | 37.3315 | 34.7379 | 31.3336 | 27.3989 | 23.2736 | 19.0568 | 13.3052 | 6.2113 | 3.4429
|  | FERNHURST BSP | EE |  |  |  |  | 24.057 | 24.4355 | 23.8121 | 28.7603 | 27.3246 | 24.3276 | 21.0215 | 17.4919 | 13.8725 | 1.047 | -8.3316 | -12.4969 | 45.0797 | 44.8041 | 43.4939 | 52.6735 | 50.9501 | 48.3378 | 45.3644 | 42.2317 | 39.0552 | 26.8725 | 19.0205 | 14.2235 | 33.5399 | 33.6899 | 32.7786 | 40.4113 | 38.6929 | 35.8307 | 32.6613 | 29.3011 | 25.8562 | 13.9164 | 6.2113 | 3.4429
|  | FERNHURST BSP | HT |  |  |  |  | 24.0264 | 24.2661 | 23.1529 | 27.3868 | 25.0041 | 21.3746 | 17.1868 | 12.7919 | 8.2868 | -4.9356 | -14.4999 | -18.8826 | 43.4705 | 43.1084 | 41.54 | 50.3673 | 47.9536 | 45.0252 | 41.4831 | 37.8 | 34.0768 | 22.721 | 16.9968 | 15.9894 | 31.5021 | 31.5431 | 30.2663 | 37.3315 | 34.7379 | 31.3336 | 27.3989 | 23.2736 | 19.0568 | 15.0621 | 12.7747 | 10.6179
|  | FERNHURST BSP | HE |  |  |  |  | 24.061 | 24.4488 | 23.8315 | 28.648 | 27.098 | 24.1399 | 20.7205 | 17.1052 | 13.4837 | 3.4429 | -4.7969 | -8.4408 | 43.4768 | 43.2031 | 41.8505 | 50.9789 | 49.1684 | 46.6168 | 43.521 | 40.3115 | 37.1221 | 26.041 | 19.1115 | 14.1021 | 31.52 | 31.6873 | 30.7305 | 38.2863 | 36.4336 | 33.5915 | 30.2431 | 26.7452 | 23.2579 | 13.3052 | 6.6726 | 4.1536
|  | FERNHURST BSP | FB |  |  |  |  | 25.261 | 26.059 | 26.5927 | 32.5092 | 32.6358 | 31.8786 | 31.0797 | 30.348 | 29.4246 | 21.1358 | 11.0123 | 4.8592 | 44.3715 | 44.3579 | 44.1126 | 53.9336 | 53.4031 | 51.8905 | 50.1389 | 48.5757 | 46.8715 | 34.6063 | 19.3136 | 3.9726 | 32.74 | 33.3652 | 33.7273 | 42.2505 | 42.2947 | 41.4336 | 40.3579 | 39.3884 | 38.2726 | 29.2357 | 19.0757 | 12.841
LOVEDEAN GSP | FORT WIDLEY BSP | FORT WIDLEY BSP | MINIMUM HEADROOM | SU 65875 07686 | NO | YES | 16.472 | 40.7152 | 79.2427 | 78.8192 | 78.1733 | 77.3294 | 76.0519 | 74.5958 | 72.9631 | 71.4794 | 66.0886 | 62.7662 | 61.4233 | 45.0319 | 81.3414 | 80.7783 | 80.153 | 79.3067 | 78.1183 | 76.7004 | 75.0972 | 73.7014 | 68.8277 | 62.7088 | 53.093 | 41.8761 | 78.8498 | 78.3172 | 77.6519 | 76.7446 | 75.4088 | 73.8677 | 72.2004 | 70.7446 | 67.4698 | 64.6284 | 63.2152
|  | FORT WIDLEY BSP | EE |  |  |  |  | 40.7162 | 79.2937 | 78.9519 | 78.4907 | 77.8672 | 76.8254 | 75.6172 | 74.3192 | 73.0948 | 68.0009 | 64.4427 | 62.5764 | 45.6427 | 82.0029 | 81.508 | 81.0101 | 80.3192 | 79.3427 | 78.1356 | 76.756 | 75.5509 | 69.6856 | 65.5641 | 61.8948 | 42.6162 | 79.6407 | 79.1825 | 78.6866 | 77.9764 | 76.8835 | 75.5886 | 74.1866 | 72.956 | 67.8172 | 64.6284 | 63.2152
|  | FORT WIDLEY BSP | HT |  |  |  |  | 40.7152 | 79.2427 | 78.8192 | 78.1733 | 77.3294 | 76.0519 | 74.5958 | 72.9631 | 71.4794 | 66.0886 | 62.7662 | 61.4233 | 45.0319 | 81.3414 | 80.7783 | 80.153 | 79.3067 | 78.1183 | 76.7004 | 75.0972 | 73.7014 | 68.8277 | 66.4277 | 65.5435 | 41.8761 | 78.8498 | 78.3172 | 77.6519 | 76.7446 | 75.4088 | 73.8677 | 72.2004 | 70.7446 | 69.0888 | 67.9109 | 66.9025
|  | FORT WIDLEY BSP | HE |  |  |  |  | 40.7254 | 79.3141 | 78.9876 | 78.5009 | 77.8621 | 76.8396 | 75.655 | 74.3621 | 73.1672 | 68.8131 | 65.8886 | 64.457 | 45.0372 | 81.3888 | 80.8793 | 80.3614 | 79.6604 | 78.6551 | 77.3972 | 75.9667 | 74.754 | 69.0646 | 65.0361 | 61.3319 | 41.8846 | 78.9098 | 78.4498 | 77.9183 | 77.1804 | 76.0646 | 74.7383 | 73.2983 | 72.0709 | 67.4698 | 64.7877 | 63.7361
|  | FORT WIDLEY BSP | FB |  |  |  |  | 41.0907 | 79.856 | 79.9437 | 79.8152 | 79.557 | 79.2948 | 78.9152 | 78.5213 | 78.0876 | 75.3529 | 70.9815 | 68.5376 | 45.1772 | 81.5793 | 81.4456 | 81.1404 | 80.5551 | 79.8888 | 79.0646 | 78.2183 | 77.3277 | 71.4772 | 62.7088 | 53.093 | 42.3183 | 79.5498 | 79.6446 | 79.5161 | 79.154 | 78.8593 | 78.4161 | 77.9319 | 77.4056 | 73.974 | 69.3583 | 66.8667
MELKSHAM GSP | FROME BSP | FROME BSP | MINIMUM HEADROOM | ST 78803 48019 | NO | NO | 28.094 | -0.46328 | -1.2725 | -2.4796 | 109.8569 | 107.412 | 103.1406 | 98.1691 | 93.1191 | 88.4783 | 70.6589 | 56.8508 | 49.7497 | 15.2362 | 14.5467 | 13.6835 | 122.1562 | 120.3593 | 117.2993 | 113.6025 | 109.4414 | 105.893 | 92.8141 | 85.2299 | 69.3572 | 5.7888 | 5.2783 | 4.2783 | 113.5267 | 110.7193 | 106.852 | 102.4551 | 97.7235 | 93.5551 | 81.1751 | 71.3635 | 66.691
|  | FROME BSP | EE |  |  |  |  | -0.46022 | -1.2694 | -2.4786 | 109.8987 | 107.5283 | 103.3252 | 98.3191 | 93.311 | 88.7314 | 70.6589 | 56.8508 | 49.965 | 17.8033 | 17.1359 | 16.3084 | 124.8635 | 123.0972 | 120.2951 | 116.741 | 113.0278 | 109.7237 | 95.1564 | 85.2839 | 79.3655 | 8.7033 | 8.2104 | 7.2421 | 116.6043 | 113.9155 | 110.291 | 106.0064 | 101.6441 | 97.7053 | 82.1747 | 71.3635 | 66.691
|  | FROME BSP | HT |  |  |  |  | -0.46022 | -1.2714 | -2.4786 | 109.8763 | 107.5487 | 103.2273 | 98.2538 | 93.1191 | 88.4783 | 70.7671 | 56.9528 | 49.7497 | 15.2393 | 14.5467 | 13.6835 | 122.1562 | 120.4035 | 117.2993 | 113.6025 | 109.4414 | 105.893 | 92.8141 | 85.2299 | 83.1172 | 5.7888 | 5.2783 | 4.2783 | 113.5267 | 110.772 | 106.852 | 102.4551 | 97.7235 | 93.5551 | 89.4983 | 86.4941 | 83.7267
|  | FROME BSP | HE |  |  |  |  | -0.46328 | -1.2725 | -2.4796 | 109.8569 | 107.412 | 103.1406 | 98.1691 | 93.1446 | 88.5467 | 74.0355 | 62.365 | 56.9793 | 15.2362 | 14.5499 | 13.6983 | 122.2277 | 120.3593 | 117.432 | 113.8393 | 110.0162 | 106.612 | 94.0688 | 85.9383 | 80.1625 | 5.792 | 5.2814 | 4.292 | 113.5941 | 110.7193 | 106.9299 | 102.5762 | 98.0762 | 94.0046 | 81.1751 | 72.1941 | 68.4299
|  | FROME BSP | FB |  |  |  |  | 0.36427 | 0.079576 | -0.50002 | 113.1906 | 112.0201 | 110.212 | 108.763 | 107.514 | 105.8834 | 95.7834 | 83.6844 | 76.2038 | 15.7699 | 15.5004 | 15.0941 | 124.4372 | 123.4425 | 121.993 | 120.1688 | 118.473 | 116.1477 | 103.0414 | 86.4172 | 69.3572 | 6.5467 | 6.4446 | 6.1751 | 117.4614 | 116.4246 | 114.6393 | 113.0256 | 111.6183 | 109.5151 | 99.1814 | 87.5077 | 80.0762
LOVEDEAN GSP | HAVANT BSP | HAVANT BSP | MINIMUM HEADROOM | SU 70625 05720 | NO | YES | 33.21 | 24.6357 | 24.1806 | 22.6439 | 20.4061 | 17.3694 | 12.7367 | 7.6541 | 2.151 | 111.3278 | 92.7349 | 80.0033 | 74.1451 | 37.4445 | 36.6487 | 35.0393 | 32.8803 | 30.074 | 26.475 | 22.2845 | 17.6456 | 128.6571 | 114.735 | 97.8045 | 70.035 | 27.954 | 27.4614 | 26.0624 | 23.9077 | 20.8108 | 16.5445 | 11.735 | 6.454 | 118.6445 | 109.0382 | 98.6084 | 93.2931
|  | HAVANT BSP | EE |  |  |  |  | 24.6357 | 24.9316 | 23.4837 | 21.9204 | 19.7306 | 15.8184 | 11.3357 | 6.6408 | 116.6196 | 98.8788 | 85.5676 | 78.5278 | 39.2594 | 39.1492 | 37.488 | 35.738 | 33.4655 | 30.4166 | 26.6849 | 22.6502 | 134.2635 | 117.138 | 104.6706 | 93.5972 | 30.09 | 30.2706 | 28.889 | 27.3482 | 25.0247 | 21.4604 | 17.2543 | 12.7706 | 125.7523 | 109.5135 | 98.6084 | 93.2931
|  | HAVANT BSP | HT |  |  |  |  | 24.6388 | 24.1806 | 22.6439 | 20.4061 | 17.3694 | 12.7367 | 7.6541 | 2.151 | 111.3278 | 92.7349 | 80.0033 | 74.1451 | 37.4445 | 36.6487 | 35.0393 | 32.8803 | 30.074 | 26.475 | 22.2845 | 17.6456 | 128.6571 | 114.735 | 107.2487 | 104.2624 | 27.954 | 27.4614 | 26.0624 | 23.9077 | 20.8108 | 16.5445 | 11.735 | 6.454 | 118.6445 | 114.0645 | 110.0214 | 107.0224
|  | HAVANT BSP | HE |  |  |  |  | 24.6602 | 24.9755 | 23.552 | 21.8816 | 19.5531 | 15.5918 | 11.1204 | 6.4306 | 116.2972 | 101.8706 | 91.2676 | 85.8104 | 37.454 | 37.3382 | 35.6214 | 33.8066 | 31.4119 | 28.2445 | 24.4214 | 20.354 | 131.8077 | 115.774 | 104.0824 | 92.5708 | 27.9635 | 28.174 | 26.7687 | 25.094 | 22.5866 | 18.874 | 14.575 | 10.034 | 122.8182 | 109.0382 | 100.2193 | 95.875
|  | HAVANT BSP | FB |  |  |  |  | 25.9857 | 26.7735 | 27.2194 | 26.9704 | 26.6694 | 25.4255 | 24.0622 | 22.6347 | 135.4013 | 126.0155 | 112.0268 | 103.8962 | 37.9982 | 37.954 | 37.595 | 36.5898 | 35.3919 | 33.1329 | 30.615 | 28.0203 | 140.4529 | 123.054 | 97.8045 | 70.035 | 29.1245 | 29.8003 | 30.1803 | 29.935 | 29.7119 | 28.5119 | 26.9656 | 25.4003 | 140.6698 | 130.0645 | 116.134 | 108.2098
COWLEY GSP | HEADINGTON BSP | HEADINGTON BSP | MINIMUM HEADROOM | SP 54454 08145 | NO | NO | 78.635 | 13.0318 | 11.5103 | 10.0359 | 8.4971 | 5.2716 | -0.31619 | -4.5846 | -8.8295 | -17.1948 | -27.208 | -37.2815 | -44.1305 | 17.4265 | 16.4896 | 15.8086 | 15.0644 | 12.377 | 7.4749 | 3.838 | -0.0072211 | -11.6672 | -23.0683 | -34.6493 | -48.4599 | 12.6149 | 11.4801 | 10.5001 | 9.277 | 6.3854 | 1.3012 | -2.662 | -6.7693 | -17.4272 | -28.4883 | -38.1914 | -48.3388
|  | HEADINGTON BSP | EE |  |  |  |  | 13.2644 | 11.9869 | 10.8869 | 9.7461 | 8.4746 | 2.8818 | -0.15496 | -3.7019 | -10.2182 | -21.1284 | -33.2723 | -37.559 | 18.8851 | 18.1085 | 17.6412 | 17.1116 | 16.2269 | 11.3657 | 9.0279 | 5.8606 | -0.94553 | -11.4915 | -26.0557 | -33.9843 | 14.2953 | 13.3636 | 12.6463 | 11.7851 | 10.6983 | 5.7626 | 2.9932 | -0.37309 | -6.6384 | -17.4333 | -30.9486 | -35.6466
|  | HEADINGTON BSP | HT |  |  |  |  | 13.0318 | 11.5103 | 10.0359 | 8.4971 | 5.2716 | -0.31619 | -4.5846 | -8.8295 | -17.1948 | -27.1019 | -37.2815 | -42.9264 | 17.4265 | 16.4896 | 15.8086 | 15.0644 | 12.377 | 7.4749 | 3.838 | -0.0072211 | -8.9651 | -18.3756 | -30.423 | -38.0956 | 12.6149 | 11.4801 | 10.5001 | 9.277 | 6.3854 | 1.3012 | -2.662 | -6.7693 | -15.4325 | -18.6388 | -19.9483 | -21.7314
|  | HEADINGTON BSP | HE |  |  |  |  | 13.2644 | 12.0236 | 10.9532 | 9.793 | 8.541 | 2.9746 | -0.61823 | -5.9468 | -16.6244 | -27.208 | -35.8213 | -44.1305 | 17.5454 | 16.7559 | 16.2759 | 15.7307 | 14.8801 | 9.7907 | 6.6696 | 1.0338 | -11.6672 | -23.0683 | -34.6493 | -48.4599 | 12.7686 | 11.8265 | 11.1096 | 10.2233 | 9.1244 | 3.9665 | 0.45909 | -5.3504 | -17.4272 | -28.4883 | -38.1914 | -48.3388
|  | HEADINGTON BSP | FB |  |  |  |  | 13.8083 | 12.9216 | 12.0787 | 11.2042 | 10.5726 | 6.694 | 4.3563 | 2.6787 | -2.1019 | -10.6192 | -18.7152 | -24.1815 | 17.7686 | 17.0801 | 16.6844 | 16.1317 | 15.3759 | 11.2528 | 8.678 | 6.6928 | 0.71278 | -10.4356 | -23.862 | -39.4925 | 13.1086 | 12.3328 | 11.797 | 11.2444 | 10.7075 | 6.5138 | 4.2907 | 2.6907 | -2.8514 | -10.803 | -18.343 | -24.6304
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU 84773 92191 | NO | NO | 26.979 | 13.0729 | 13.1127 | 12.6903 | 11.2801 | 9.1719 | 5.4984 | -0.014824 | -6.3556 | -16.1893 | -35.2026 | -55.7393 | -66.8965 | 60.626 | 60.2818 | 59.2302 | 57.6491 | 55.1344 | 52.147 | 47.3797 | 41.3544 | 30.8912 | 12.707 | -1.9688 | -17.6645 | 18.507 | 18.4702 | 18.067 | 16.8344 | 14.887 | 11.6344 | 6.3281 | -0.30876 | -11.2267 | -28.6172 | -43.1593 | -55.5393
|  | HIGH WYCOMBE BSP | EE |  |  |  |  | 13.0729 | 13.1127 | 12.6903 | 11.4178 | 9.7086 | 6.1188 | 1.4137 | -4.0475 | -9.924 | -30.3077 | -51.2618 | -60.8505 | 61.8405 | 61.5028 | 60.5762 | 59.1762 | 57.063 | 54.2568 | 50.4854 | 45.9334 | 40.7977 | 22.263 | 2.9732 | -7.638 | 21.0242 | 20.9793 | 20.5773 | 19.5742 | 18.0222 | 15.0007 | 10.7038 | 5.6415 | 0.0344 | -18.936 | -38.8003 | -47.0115
|  | HIGH WYCOMBE BSP | HT |  |  |  |  | 13.2607 | 13.4219 | 12.8168 | 11.2801 | 9.1719 | 5.4984 | -0.014824 | -5.9169 | -13.3077 | -35.2026 | -55.7393 | -66.8965 | 60.6418 | 60.3218 | 59.2302 | 57.6491 | 55.1344 | 52.147 | 47.3797 | 42.1681 | 34.9776 | 17.066 | 1.3712 | -6.7435 | 18.5986 | 18.6344 | 18.0807 | 16.8344 | 14.887 | 11.6344 | 6.3281 | 0.63019 | -7.0245 | -12.5709 | -15.8867 | -19.8235
|  | HIGH WYCOMBE BSP | HE |  |  |  |  | 13.1168 | 13.178 | 12.7648 | 11.2882 | 9.4056 | 5.8862 | 0.79844 | -6.3556 | -16.1893 | -33.4658 | -48.8077 | -60.6148 | 60.626 | 60.2818 | 59.3102 | 57.8797 | 55.6807 | 52.7144 | 48.2933 | 41.3544 | 30.8912 | 12.707 | -1.9688 | -17.6645 | 18.507 | 18.4702 | 18.067 | 16.8912 | 15.1881 | 12.0681 | 7.1281 | -0.30876 | -11.2267 | -28.6172 | -43.1593 | -55.5393
|  | HIGH WYCOMBE BSP | FB |  |  |  |  | 14.5046 | 14.8005 | 15.1658 | 15.3995 | 15.3801 | 15.0923 | 14.1607 | 12.727 | 11.0423 | 0.83416 | -13.524 | -24.7669 | 61.2902 | 61.1502 | 60.6849 | 60.3386 | 59.5565 | 58.4355 | 56.3881 | 53.5976 | 50.6155 | 33.9439 | 11.7818 | -12.4024 | 19.4407 | 19.7502 | 19.9849 | 20.067 | 19.8565 | 19.5386 | 18.6533 | 17.3176 | 15.3439 | 3.926 | -11.4172 | -23.5624
LOVEDEAN GSP | HUNSTON BSP | HUNSTON BSP | MINIMUM HEADROOM | SU 86946 02627 | NO | YES | 36.915 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064
|  | HUNSTON BSP | EE |  |  |  |  | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064
|  | HUNSTON BSP | HT |  |  |  |  | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064
|  | HUNSTON BSP | HE |  |  |  |  | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064
|  | HUNSTON BSP | FB |  |  |  |  | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 101.7184 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 97.2064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064 | 99.0064
FAWLEY GSP | LANGLEY BSP | LANGLEY BSP | MINIMUM HEADROOM | SU 45185 01376 | NO | NO | 10.167 | 31.6881 | 31.7116 | 31.332 | 30.4137 | 29.1739 | 27.1004 | 24.5677 | 21.9412 | 18.633 | 9.5473 | 1.1412 | -3.4221 | 33.7497 | 33.7434 | 33.4602 | 32.956 | 32.3086 | 31.3497 | 29.7665 | 28.0434 | 24.1886 | 17.5118 | 11.7307 | 5.7823 | 31.3286 | 31.3728 | 30.9781 | 30.1476 | 29.0802 | 27.4686 | 25.276 | 22.9686 | 19.5149 | 12.5255 | 6.4149 | 1.6665
|  | LANGLEY BSP | EE |  |  |  |  | 31.7412 | 31.9055 | 31.7279 | 31.1647 | 30.3953 | 28.6677 | 26.681 | 24.4555 | 21.9922 | 14.0881 | 5.7871 | 2.2239 | 34.2805 | 34.3397 | 34.1458 | 33.7836 | 33.3121 | 32.5458 | 31.4427 | 29.9805 | 28.2233 | 22.0264 | 15.008 | 11.5203 | 31.9723 | 32.0703 | 31.8478 | 31.2856 | 30.557 | 29.2295 | 27.605 | 25.6836 | 23.5274 | 16.6948 | 9.0652 | 6.2274
|  | LANGLEY BSP | HT |  |  |  |  | 31.6881 | 31.7116 | 31.332 | 30.4137 | 29.1739 | 27.1004 | 24.5677 | 21.9412 | 18.633 | 9.5473 | 1.1412 | -3.4221 | 33.7497 | 33.7434 | 33.4602 | 32.956 | 32.3086 | 31.3497 | 29.7665 | 28.0434 | 25.4413 | 19.3307 | 13.6202 | 10.6002 | 31.3286 | 31.3728 | 30.9781 | 30.1476 | 29.0802 | 27.4686 | 25.276 | 22.9686 | 19.8234 | 17.636 | 16.0897 | 14.8444
|  | LANGLEY BSP | HE |  |  |  |  | 31.7504 | 31.9188 | 31.7483 | 31.1432 | 30.3534 | 28.7147 | 26.6269 | 23.7943 | 19.7596 | 12.2494 | 5.5106 | 0.88814 | 33.7855 | 33.8413 | 33.6423 | 33.2655 | 32.7928 | 31.9781 | 30.5781 | 28.1507 | 24.1886 | 17.5118 | 11.7307 | 5.7823 | 31.3813 | 31.4876 | 31.2423 | 30.6528 | 29.8971 | 28.556 | 26.6739 | 23.836 | 19.5149 | 12.5255 | 6.4149 | 1.6665
|  | LANGLEY BSP | FB |  |  |  |  | 32.2096 | 32.4586 | 32.7279 | 32.8249 | 32.8963 | 32.6147 | 32.2677 | 31.7188 | 31.0116 | 27.1177 | 21.2351 | 17.6024 | 34.0276 | 34.0486 | 34.0823 | 33.9834 | 33.8476 | 33.3202 | 32.6992 | 31.8781 | 30.8613 | 25.4139 | 17.2907 | 9.1749 | 31.7634 | 31.9518 | 32.1518 | 32.2276 | 32.3055 | 32.0634 | 31.6413 | 30.9465 | 30.1034 | 25.8528 | 19.9665 | 16.056
IVER 132KV GSP | LONGFORD BSP | LONGFORD BSP | MINIMUM HEADROOM | TQ 03910 76751 | NO | YES | 19.067 | 72.657 | 78.0521 | 77.9327 | 77.695 | 77.3674 | 76.945 | 76.4246 | 75.8787 | 75.397 | 69.9358 | 68.4368 | 67.9562 | 59.4576 | 69.286 | 69.0871 | 68.8586 | 68.4702 | 67.9513 | 67.2892 | 66.6281 | 66.0365 | 60.2018 | 58.6618 | 55.0007 | 63.0018 | 71.1071 | 70.9923 | 70.8007 | 70.5113 | 70.1544 | 69.6839 | 69.2049 | 68.7955 | 64.7902 | 63.0419 | 62.5766
|  | LONGFORD BSP | EE |  |  |  |  | 72.657 | 78.0521 | 77.9501 | 77.7766 | 77.5103 | 77.1531 | 76.6746 | 76.1909 | 75.7674 | 70.9511 | 69.1572 | 68.7021 | 60.694 | 70.546 | 70.3684 | 70.1766 | 69.8399 | 69.3501 | 68.7215 | 68.1409 | 67.6093 | 61.896 | 59.2358 | 57.9031 | 64.1787 | 72.295 | 72.2042 | 72.0572 | 71.8246 | 71.5266 | 71.1144 | 70.7021 | 70.3623 | 65.7266 | 63.0419 | 62.5766
|  | LONGFORD BSP | HT |  |  |  |  | 72.66 | 78.0521 | 77.9327 | 77.695 | 77.3674 | 76.945 | 76.4246 | 75.8787 | 75.397 | 69.9358 | 68.4368 | 67.9562 | 59.4586 | 69.286 | 69.0871 | 68.8586 | 68.4702 | 67.9513 | 67.2892 | 66.6281 | 66.0365 | 60.2018 | 58.6618 | 58.3039 | 63.0018 | 71.1071 | 70.9923 | 70.8007 | 70.5113 | 70.1544 | 69.6839 | 69.2049 | 68.7955 | 66.2997 | 65.2502 | 64.5481
|  | LONGFORD BSP | HE |  |  |  |  | 72.66 | 78.0623 | 77.9674 | 77.7878 | 77.5093 | 77.1593 | 76.7052 | 76.2429 | 75.8297 | 71.4419 | 70.147 | 69.796 | 59.4576 | 69.2965 | 69.1165 | 68.9218 | 68.5628 | 68.0776 | 67.4197 | 66.8334 | 66.2702 | 60.9334 | 59.0018 | 57.7649 | 63.0018 | 71.1144 | 71.0281 | 70.8671 | 70.6165 | 70.326 | 69.9018 | 69.4944 | 69.146 | 64.7902 | 63.606 | 63.2786
|  | LONGFORD BSP | FB |  |  |  |  | 72.8682 | 78.3715 | 78.4093 | 78.2664 | 78.1725 | 78.0705 | 77.948 | 77.7776 | 77.6491 | 76.6817 | 72.097 | 71.2603 | 59.7628 | 69.7397 | 69.7197 | 69.3302 | 69.1081 | 68.8207 | 68.5681 | 68.2197 | 67.8702 | 65.6302 | 58.8039 | 55.0007 | 63.2007 | 71.4028 | 71.4407 | 71.3081 | 71.2249 | 71.126 | 71.0207 | 70.8618 | 70.7492 | 69.8418 | 65.1628 | 64.3692
AMERSHAM GSP | LOUDWATER BSP | LOUDWATER BSP | MINIMUM HEADROOM | SU 90644 91247 | NO | YES | 15.511 | 56.6401 | 56.2105 | 55.432 | 53.3646 | 51.1911 | 26.8779 | 22.6126 | 18.2554 | 13.9809 | -0.79865 | -10.5252 | -14.0895 | 69.5815 | 69.0141 | 68.2941 | 66.6583 | 65.032 | 36.3646 | 33.5278 | 30.5194 | 27.5667 | 18.0478 | 12.3004 | -2.1754 | 60.0594 | 59.5141 | 58.7267 | 56.7394 | 54.7583 | 25.1931 | 21.5267 | 17.7257 | 13.9994 | 5.7446 | -0.45326 | -2.5501
|  | LOUDWATER BSP | EE |  |  |  |  | 56.6401 | 56.2105 | 55.5228 | 53.736 | 51.8636 | 48.2952 | 44.2422 | 40.1289 | 36.0411 | 22.3799 | 12.7922 | 8.5738 | 70.6618 | 70.1138 | 69.4914 | 68.0536 | 66.6149 | 64.623 | 62.0444 | 59.3434 | 56.5761 | 45.8781 | 39.1628 | 34.4975 | 61.471 | 60.9271 | 60.2434 | 58.5587 | 56.874 | 54.0404 | 50.672 | 47.2251 | 43.7669 | 32.0669 | 24.6924 | 22.0138
|  | LOUDWATER BSP | HT |  |  |  |  | 56.6513 | 56.2371 | 55.432 | 53.3646 | 51.1911 | 26.8779 | 22.6126 | 18.2554 | 13.9809 | -0.79865 | -10.5252 | -14.0895 | 69.5815 | 69.0141 | 68.2941 | 66.6583 | 65.032 | 36.3646 | 33.5278 | 30.5194 | 27.5667 | 18.0478 | 13.7646 | 13.3204 | 60.0594 | 59.5141 | 58.7267 | 56.7394 | 54.7583 | 25.1931 | 21.5267 | 17.7257 | 13.9994 | 10.5299 | 7.9952 | 5.5425
|  | LOUDWATER BSP | HE |  |  |  |  | 56.6626 | 56.2564 | 55.5962 | 53.7258 | 51.784 | 27.8228 | 23.9442 | 19.8605 | 15.8289 | 4.7473 | -3.2527 | -6.414 | 69.5825 | 69.0236 | 68.3888 | 66.892 | 65.4078 | 36.9699 | 34.4499 | 31.6299 | 28.7888 | 18.9383 | 12.5762 | 7.5183 | 60.0667 | 59.5278 | 58.8425 | 57.0499 | 55.2636 | 26.0015 | 22.7131 | 19.1594 | 15.6383 | 5.7446 | -0.45326 | -2.5501
|  | LOUDWATER BSP | FB |  |  |  |  | 57.686 | 57.832 | 57.8503 | 57.7646 | 57.6799 | 36.7381 | 35.9146 | 34.9371 | 33.9391 | 27.1809 | 18.2044 | 13.0279 | 70.3015 | 70.032 | 69.6583 | 69.2046 | 68.6478 | 41.192 | 39.7141 | 38.1352 | 36.5036 | 26.2331 | 12.3004 | -2.1754 | 61.2299 | 61.2794 | 61.2573 | 61.0467 | 60.912 | 33.9436 | 32.9857 | 31.9173 | 30.8278 | 23.7699 | 14.9804 | 9.8499
MANNINGTON GSP | LYTCHETT BSP | LYTCHETT BSP | MINIMUM HEADROOM | SY 97796 94214 | NO | NO | 13.96 | 52.6601 | 57.9491 | 57.0338 | 55.4052 | 53.2542 | 49.6532 | 45.6164 | 40.9848 | 36.4532 | 20.796 | 9.693 | 4.6613 | 60.5218 | 70.5986 | 69.806 | 68.3923 | 66.2281 | 63.8397 | 60.3849 | 57.0828 | 54.0186 | 43.3323 | 38.1386 | 25.1881 | 53.186 | 61.2744 | 60.487 | 59.1839 | 57.4397 | 54.8197 | 50.8312 | 46.7123 | 42.8186 | 34.887 | 26.9715 | 23.1624
|  | LYTCHETT BSP | EE |  |  |  |  | 52.6815 | 58.0256 | 57.2562 | 55.9715 | 54.1103 | 50.7032 | 46.9613 | 43.193 | 39.546 | 25.3583 | 14.9277 | 9.4266 | 61.9481 | 72.0756 | 71.3287 | 70.2736 | 68.4838 | 66.2654 | 63.343 | 60.5573 | 57.8032 | 46.0501 | 38.5011 | 33.196 | 54.8879 | 63.0297 | 62.3654 | 61.3715 | 59.8981 | 57.5338 | 54.6246 | 51.0766 | 47.6042 | 35.0848 | 26.9715 | 23.1624
|  | LYTCHETT BSP | HT |  |  |  |  | 52.6601 | 57.9491 | 57.0338 | 55.4052 | 53.2542 | 49.6532 | 45.6164 | 40.9848 | 36.4532 | 20.796 | 9.693 | 4.6613 | 60.5218 | 70.5986 | 69.806 | 68.3923 | 66.2281 | 63.8397 | 60.3849 | 57.0828 | 54.0186 | 43.3323 | 38.1386 | 36.9576 | 53.186 | 61.2744 | 60.487 | 59.1839 | 57.4397 | 54.8197 | 50.8312 | 46.7123 | 42.8186 | 38.4997 | 36.6439 | 33.8323
|  | LYTCHETT BSP | HE |  |  |  |  | 52.6846 | 58.0613 | 57.3113 | 55.8746 | 53.8899 | 50.5471 | 46.8154 | 43.0838 | 39.4511 | 27.9664 | 19.3981 | 15.4062 | 60.5407 | 70.6839 | 70.0176 | 68.7776 | 66.8733 | 64.6723 | 61.6102 | 58.7786 | 55.9333 | 45.6407 | 39.3165 | 34.1681 | 53.2144 | 61.3523 | 60.7123 | 59.5755 | 57.9733 | 55.5839 | 52.5565 | 48.9681 | 45.3986 | 34.887 | 28.3533 | 25.5049
|  | LYTCHETT BSP | FB |  |  |  |  | 53.3407 | 59.1481 | 59.0685 | 58.9124 | 58.3073 | 57.6797 | 56.9634 | 56.1205 | 55.2195 | 49.0022 | 40.7358 | 34.3052 | 61.0291 | 71.246 | 71.1755 | 71.0576 | 69.9997 | 68.686 | 67.3586 | 65.8818 | 64.2197 | 53.4333 | 40.047 | 25.1881 | 53.8523 | 62.326 | 62.2818 | 62.1944 | 61.6481 | 61.1144 | 60.486 | 59.7576 | 58.9344 | 52.3123 | 43.5828 | 37.1933
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | MAIDENHEAD BSP | MINIMUM HEADROOM | SU 86592 79883 | NO | NO | 37.466 | 36.8259 | 36.6045 | 35.9514 | 34.3004 | 32.1187 | 28.88 | 25.7453 | 22.2759 | 19.3157 | 4.9677 | -1.7731 | -3.7925 | 45.9756 | 45.5819 | 44.7714 | 43.3672 | 41.383 | 38.8966 | 36.4651 | 33.5924 | 31.2366 | 19.7787 | 12.9598 | 0.22191 | 36.8114 | 36.5272 | 35.824 | 34.3745 | 32.2945 | 29.4503 | 26.6566 | 23.5156 | 20.9145 | 11.1335 | 5.6996 | 3.5251
|  | MAIDENHEAD BSP | EE |  |  |  |  | 36.8259 | 36.6045 | 36.0014 | 34.3728 | 32.3055 | 29.1871 | 26.4371 | 23.5371 | 21.0381 | 7.5004 | 0.19017 | -2.8006 | 47.3925 | 47.0231 | 46.2925 | 44.9751 | 43.22 | 40.8914 | 38.8169 | 36.4761 | 34.5139 | 22.4159 | 16.2516 | 11.9282 | 38.5414 | 38.2578 | 37.622 | 36.269 | 34.4149 | 31.6986 | 29.3037 | 26.7292 | 24.5741 | 11.8965 | 5.6996 | 3.5251
|  | MAIDENHEAD BSP | HT |  |  |  |  | 36.8351 | 36.6289 | 35.9514 | 34.3004 | 32.1187 | 28.88 | 25.7453 | 22.2759 | 19.3157 | 4.9677 | -1.7731 | -3.7925 | 45.9756 | 45.5819 | 44.7714 | 43.3672 | 41.383 | 38.8966 | 36.4651 | 33.5924 | 31.2366 | 19.7787 | 15.9524 | 15.243 | 36.8114 | 36.5272 | 35.824 | 34.3745 | 32.2945 | 29.4503 | 26.6566 | 23.5156 | 20.9145 | 15.1503 | 12.8124 | 10.8945
|  | MAIDENHEAD BSP | HE |  |  |  |  | 36.8575 | 36.6718 | 36.1238 | 34.4136 | 32.3136 | 29.2626 | 26.5187 | 23.6759 | 21.3279 | 9.5555 | 4.0442 | 1.7596 | 45.984 | 45.6124 | 44.8819 | 43.5093 | 41.7103 | 39.3524 | 37.1493 | 34.7051 | 32.7503 | 21.0787 | 15.5587 | 11.0356 | 36.8261 | 36.5524 | 35.9472 | 34.484 | 32.5366 | 29.823 | 27.3324 | 24.7293 | 22.6082 | 11.1335 | 6.5272 | 4.8114
|  | MAIDENHEAD BSP | FB |  |  |  |  | 37.7994 | 37.7677 | 37.6575 | 36.7473 | 35.682 | 34.2432 | 33.0861 | 32.4177 | 31.5861 | 25.5422 | 14.7932 | 10.3126 | 46.3861 | 46.1387 | 45.704 | 44.7598 | 43.6587 | 42.1324 | 40.604 | 39.323 | 37.8566 | 28.3051 | 12.9598 | 0.22191 | 37.7703 | 37.7524 | 37.723 | 36.8724 | 36.0198 | 34.7766 | 33.6556 | 32.8966 | 31.9619 | 25.5714 | 14.6093 | 10.2882
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON BSP | MINIMUM HEADROOM | SU 07523 05221 | NO | NO | 24.193 | 65.7934 | 65.1281 | 63.2689 | 61.0903 | 57.422 | 52.0414 | 43.9261 | 35.2924 | 17.1995 | -6.3617 | -31.9127 | -48.6566 | 78.4521 | 77.5648 | 75.9216 | 74.1321 | 70.9111 | 66.7416 | 59.2195 | 48.7606 | 27.9479 | 0.90583 | -24.491 | -52.6152 | 66.3911 | 65.4237 | 63.0921 | 60.5627 | 56.7079 | 51.8027 | 43.4953 | 32.9721 | 11.5479 | -14.3015 | -38.5047 | -62.3542
|  | MANNINGTON BSP | EE |  |  |  |  | 65.9067 | 65.5332 | 63.8761 | 62.3148 | 59.5067 | 54.6516 | 48.7108 | 41.3475 | 33.3873 | 9.6567 | -19.7403 | -30.7311 | 80.3669 | 79.7138 | 78.2556 | 76.9189 | 74.171 | 70.3475 | 65.274 | 58.5363 | 50.8505 | 25.8169 | -7.3127 | -21.9311 | 68.7516 | 68.0434 | 66.0077 | 64.0791 | 60.9189 | 56.4985 | 50.8434 | 43.4883 | 35.275 | 10.7985 | -21.4362 | -32.5852
|  | MANNINGTON BSP | HT |  |  |  |  | 65.7934 | 65.1281 | 63.2689 | 61.0903 | 57.422 | 52.0414 | 43.9261 | 35.4689 | 23.3424 | -3.5586 | -31.9127 | -48.1117 | 78.4521 | 77.5648 | 75.9216 | 74.1321 | 70.9111 | 66.7416 | 59.2195 | 51.27 | 38.5364 | 12.4774 | -16.51 | -33.4889 | 66.3911 | 65.4237 | 63.0921 | 60.5627 | 56.7079 | 51.8027 | 43.4953 | 34.8069 | 21.3416 | 13.5079 | 9.3132 | 4.2532
|  | MANNINGTON BSP | HE |  |  |  |  | 65.8883 | 65.5414 | 63.8495 | 62.2587 | 59.5159 | 54.5791 | 47.2659 | 35.2924 | 17.1995 | -6.3617 | -28.5433 | -48.6566 | 78.5174 | 77.8753 | 76.3311 | 74.9437 | 72.2216 | 68.3269 | 61.4921 | 48.7606 | 27.9479 | 0.90583 | -24.491 | -52.6152 | 66.4595 | 65.7732 | 63.6037 | 61.5869 | 58.4469 | 53.8943 | 46.3932 | 32.9721 | 11.5479 | -14.3015 | -38.5047 | -62.3542
|  | MANNINGTON BSP | FB |  |  |  |  | 67.1842 | 67.5097 | 67.3424 | 66.8128 | 66.172 | 65.1801 | 63.5648 | 61.5771 | 57.7577 | 41.4546 | 22.2526 | 7.6373 | 79.3469 | 78.989 | 78.5216 | 77.5016 | 76.2437 | 74.4353 | 71.7743 | 68.7827 | 63.6616 | 40.8543 | 12.089 | -17.7247 | 67.85 | 68.109 | 67.9079 | 66.9121 | 65.8785 | 64.4648 | 62.1995 | 59.6469 | 55.1321 | 36.6311 | 15.3206 | -1.8163
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU 47559 12003 | NO | NO | 16.767 | 60.6842 | 61.0291 | 60.5261 | 58.6689 | 56.1373 | 52.1985 | 46.9506 | 40.8944 | 35.0801 | 14.0495 | 0.59137 | -4.3505 | 87.2125 | 86.5946 | 85.4409 | 83.2735 | 80.5009 | 76.803 | 72.0325 | 66.8641 | 61.9641 | 44.5967 | 18.4241 | -21.0296 | 67.7735 | 67.8198 | 67.1367 | 65.1988 | 62.2883 | 58.0325 | 52.8746 | 47.2925 | 42.0325 | 29.6241 | 17.2046 | 11.871
|  | NETLEY COMMON BSP | EE |  |  |  |  | 60.6842 | 61.1271 | 60.6046 | 59.1883 | 57.2128 | 53.323 | 48.5026 | 42.9363 | 37.8342 | 17.975 | 3.4026 | -3.4892 | 89.4842 | 89.0638 | 87.9148 | 86.0791 | 83.7689 | 80.1699 | 75.9526 | 71.2148 | 66.9261 | 46.1863 | 30.0312 | 15.3087 | 70.6148 | 70.8148 | 70.072 | 68.5465 | 66.2699 | 62.1016 | 57.5944 | 52.5597 | 48.0046 | 29.7046 | 17.2046 | 11.871
|  | NETLEY COMMON BSP | HT |  |  |  |  | 60.7087 | 61.0291 | 60.5261 | 58.6689 | 56.1373 | 52.1985 | 46.9506 | 40.8944 | 35.0801 | 14.0495 | 0.59137 | -4.3505 | 87.2125 | 86.5946 | 85.4409 | 83.2735 | 80.5009 | 76.803 | 72.0325 | 66.8641 | 61.9641 | 45.5251 | 36.7714 | 33.3577 | 67.7735 | 67.8198 | 67.1367 | 65.1988 | 62.2883 | 58.0325 | 52.8746 | 47.2925 | 42.0325 | 36.4862 | 32.9798 | 29.2925
|  | NETLEY COMMON BSP | HE |  |  |  |  | 60.7352 | 61.1495 | 60.8199 | 59.2679 | 57.124 | 53.3781 | 48.7301 | 43.2914 | 38.3332 | 22.4169 | 11.3148 | 6.4454 | 87.2198 | 86.6998 | 85.6935 | 83.8167 | 81.3335 | 77.6114 | 73.3367 | 68.4504 | 64.0335 | 44.5967 | 29.4472 | 14.3956 | 67.7914 | 67.943 | 67.3956 | 65.743 | 63.2293 | 59.0041 | 54.5272 | 49.4325 | 44.8335 | 29.6241 | 20.0967 | 16.2304
|  | NETLEY COMMON BSP | FB |  |  |  |  | 62.0924 | 63.2516 | 63.9424 | 64.2169 | 64.2434 | 63.5914 | 62.9179 | 61.8995 | 61.0934 | 50.7199 | 34.9516 | 25.2077 | 87.9135 | 87.6872 | 87.2114 | 86.323 | 84.9535 | 82.4525 | 79.6651 | 76.4019 | 73.3493 | 51.283 | 18.4241 | -21.0296 | 69.3819 | 70.3504 | 70.9819 | 71.1819 | 71.1904 | 70.4377 | 69.5398 | 67.9241 | 66.5083 | 54.2683 | 38.6335 | 28.9167
MELKSHAM GSP | NORRINGTON BSP | NORRINGTON BSP | MINIMUM HEADROOM | ST 88273 64983 | NO | YES | 44.934 | -39.5159 | 49.5369 | 14.7838 | 11.2808 | 6.4532 | -1.1437 | -9.6049 | -18.7264 | -27.3651 | -60.2896 | -85.2039 | -98.4794 | -2.686 | 74.7793 | 30.5582 | 27.6414 | 23.4466 | 18.5361 | 12.4487 | 5.6435 | -0.59969 | -22.7955 | -34.9923 | -60.6523 | -29.0576 | 50.3887 | 6.6308 | 3.8066 | -0.57127 | -7.0513 | -14.5997 | -22.8702 | -30.5934 | -49.3902 | -67.6065 | -76.0728
|  | NORRINGTON BSP | EE |  |  |  |  | -39.5159 | 49.6032 | 14.9685 | 11.844 | 7.1716 | 0.011384 | -8.2254 | -16.4988 | -24.5498 | -57.159 | -81.7723 | -94.5866 | 0.23024 | 78.7088 | 35.9272 | 33.2884 | 29.1517 | 24.6792 | 18.669 | 12.5639 | 6.718 | -17.4228 | -33.3259 | -44.0045 | -25.28 | 55.1925 | 12.8568 | 10.4058 | 6.2394 | 0.30269 | -7.0249 | -14.4085 | -21.4881 | -48.7238 | -67.6065 | -76.0728
|  | NORRINGTON BSP | HT |  |  |  |  | -39.5108 | 49.5369 | 14.7838 | 11.2808 | 6.4532 | -1.1437 | -9.6049 | -18.7264 | -27.3651 | -60.2896 | -85.2039 | -98.4794 | -2.686 | 74.7793 | 30.5582 | 27.6414 | 23.4466 | 18.5361 | 12.4487 | 5.6435 | -0.59969 | -22.7955 | -34.9923 | -37.5376 | -29.0565 | 50.3887 | 6.6308 | 3.8066 | -0.57127 | -7.0513 | -14.5997 | -22.8702 | -30.5934 | -38.3976 | -43.4523 | -48.7586
|  | NORRINGTON BSP | HE |  |  |  |  | -39.5098 | 49.6073 | 15.0053 | 11.7828 | 7.0114 | -0.23453 | -8.0896 | -16.0182 | -23.8141 | -49.8009 | -70.2611 | -80.3631 | -2.685 | 74.8056 | 30.674 | 27.9266 | 23.6414 | 18.994 | 13.3929 | 7.6393 | 2.0445 | -18.0797 | -31.0776 | -41.8102 | -29.0576 | 50.4319 | 6.7729 | 4.1656 | -0.18706 | -6.3607 | -13.3471 | -20.4744 | -27.3534 | -49.3902 | -64.7418 | -71.706
|  | NORRINGTON BSP | FB |  |  |  |  | -37.4547 | 52.5053 | 19.3236 | 18.4502 | 16.3604 | 13.6736 | 11.2226 | 8.7389 | 6.0838 | -9.8029 | -29.3121 | -41.6774 | -1.8271 | 75.9319 | 33.1361 | 32.4393 | 30.3003 | 27.3077 | 24.394 | 21.294 | 17.8003 | -3.7692 | -31.6007 | -60.6523 | -27.0565 | 53.1656 | 10.6666 | 10.0677 | 8.6087 | 6.5603 | 4.3719 | 1.8898 | -0.90496 | -17.545 | -35.9313 | -47.3839
MELKSHAM GSP | NORRINGTON B BSP | NORRINGTON B BSP | MINIMUM HEADROOM | ST 88273 64983 | NO | YES | 5.868 |  | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 |  | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 |  | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012
|  | NORRINGTON B BSP | EE | [5 empty] | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 |  | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 |  | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012
|  | NORRINGTON B BSP | HT | [5 empty] | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 |  | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 |  | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012
|  | NORRINGTON B BSP | HE | [5 empty] | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 |  | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 |  | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012
|  | NORRINGTON B BSP | FB | [5 empty] | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 | 113.612 |  | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 | 108.212 |  | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012 | 110.012
NORTH HYDE GSP | NORTH HYDE BSP | NORTH HYDE BSP | MINIMUM HEADROOM | TQ 10367 79001 | NO | YES | 10.339 | 50.9342 | 49.4638 | 47.1393 | 43.9546 | 41.1158 | 38.3791 | 36.2087 | 33.7485 | 31.673 | 23.4291 | 16.6189 | 12.5015 | 57.8611 | 56.6569 | 55.2622 | 53.3137 | 51.5485 | 49.8822 | 48.6022 | 46.6737 | 44.9959 | 36.6985 | 29.2148 | 14.8243 | 51.4916 | 50.2137 | 48.4432 | 45.8632 | 43.5085 | 41.2674 | 39.7832 | 37.5748 | 35.7022 | 28.023 | 21.5862 | 17.9026
|  | NORTH HYDE BSP | EE |  |  |  |  | 50.9342 | 49.6464 | 47.1393 | 43.9546 | 41.1158 | 38.3791 | 36.2087 | 33.7485 | 31.673 | 23.4291 | 16.6189 | 12.5015 | 58.576 | 57.6811 | 56.1077 | 54.2699 | 52.6046 | 50.9872 | 49.3066 | 47.3413 | 45.5934 | 36.6985 | 29.3505 | 22.775 | 52.3811 | 51.3444 | 49.3821 | 46.9148 | 44.6393 | 42.4719 | 40.4995 | 38.2475 | 36.3087 | 28.023 | 21.5862 | 17.9026
|  | NORTH HYDE BSP | HT |  |  |  |  | 50.976 | 49.4638 | 47.2658 | 44.125 | 41.2832 | 38.6536 | 36.8648 | 34.4975 | 32.5097 | 23.8056 | 17.6393 | 14.325 | 57.8643 | 56.6569 | 55.2622 | 53.3137 | 51.5485 | 49.8822 | 48.6022 | 46.6737 | 44.9959 | 38.3201 | 33.8169 | 31.2664 | 51.5064 | 50.2137 | 48.4622 | 45.8864 | 43.5085 | 41.3306 | 39.7832 | 37.5748 | 35.7022 | 33.5716 | 31.8022 | 30.2653
|  | NORTH HYDE BSP | HE |  |  |  |  | 50.9556 | 49.6903 | 47.2056 | 43.9791 | 41.1424 | 38.3791 | 36.6954 | 34.6311 | 33.0403 | 27.8536 | 23.4556 | 20.6036 | 57.8611 | 56.9422 | 55.3222 | 53.4211 | 51.7411 | 50.0474 | 48.9264 | 47.3927 | 46.1559 | 39.5316 | 33.6759 | 27.7674 | 51.4916 | 50.4485 | 48.4432 | 45.8632 | 43.5264 | 41.2674 | 39.8685 | 38.0506 | 36.6422 | 31.4369 | 27.3453 | 24.8285
|  | NORTH HYDE BSP | FB |  |  |  |  | 51.5852 | 50.473 | 48.7362 | 45.9209 | 43.7566 | 41.7117 | 40.8077 | 39.8189 | 39.1301 | 35.0413 | 29.027 | 24.0485 | 58.139 | 57.0716 | 55.7969 | 53.6959 | 51.9843 | 50.2643 | 49.1327 | 47.9537 | 46.9116 | 40.1937 | 29.2148 | 14.8243 | 52.0759 | 51.1622 | 49.8043 | 47.558 | 45.7516 | 44.0264 | 43.2485 | 42.399 | 41.7716 | 37.9337 | 32.2801 | 27.639
COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD (OSNEY) BSP | MINIMUM HEADROOM | SP 50054 05983 | NO | NO | 48.255 | -37.4903 | -37.4383 | -37.8689 | -38.9709 | 28.9016 | 24.9914 | 20.5557 | 16.0098 | 11.9935 | -1.7004 | -11.1535 | -16.2841 | -16.7621 | -16.7126 | -17.0031 | -17.5558 | 50.8724 | 48.2745 | 45.2482 | 42.205 | 39.645 | 30.2903 | 22.704 | 6.2671 | -31.2337 | -31.1053 | -31.4453 | -32.1663 | 36.1176 | 32.7924 | 28.9755 | 24.784 | 20.8482 | 12.6619 | 4.7006 | 0.81794
|  | OXFORD (OSNEY) BSP | EE |  |  |  |  | -37.4903 | -37.4383 | -37.8689 | -38.8862 | 31.3649 | 27.6465 | 23.272 | 18.922 | 14.8149 | -0.46675 | -10.7096 | -16.2841 | -14.7801 | -14.7199 | -14.9342 | -15.3515 | 55.4343 | 53.2343 | 50.5057 | 47.772 | 45.0945 | 32.9016 | 25.1302 | 19.321 | -28.8689 | -28.7811 | -29.1342 | -29.7771 | 40.6404 | 37.7006 | 34.1557 | 29.9567 | 26.171 | 12.9526 | 4.7006 | 0.81794
|  | OXFORD (OSNEY) BSP | HT |  |  |  |  | -37.4199 | -37.3015 | -37.7128 | -38.7607 | 28.9016 | 24.9914 | 20.5557 | 16.0098 | 11.9935 | -1.7004 | -11.1535 | -16.0331 | -16.7621 | -16.7126 | -17.0031 | -17.5558 | 50.8724 | 48.2745 | 45.2482 | 42.205 | 39.645 | 30.2903 | 24.7061 | 22.6871 | -31.2337 | -31.0663 | -31.4263 | -32.1305 | 36.1176 | 32.7924 | 28.9755 | 24.784 | 20.8482 | 16.9808 | 14.9555 | 13.0797
|  | OXFORD (OSNEY) BSP | HE |  |  |  |  | -37.4771 | -37.4128 | -37.8403 | -38.9709 | 31.1761 | 27.4945 | 23.1812 | 18.8455 | 15.0098 | 2.8251 | -5.0708 | -9.3219 | -16.7221 | -16.6621 | -16.8863 | -17.3274 | 53.4334 | 51.0934 | 48.2345 | 45.3513 | 42.6482 | 31.9576 | 24.9376 | 19.3713 | -31.2253 | -31.1053 | -31.4453 | -32.1663 | 38.1208 | 35.1208 | 31.5482 | 27.1976 | 23.3661 | 12.6619 | 6.2829 | 3.3903
|  | OXFORD (OSNEY) BSP | FB |  |  |  |  | -36.975 | -36.6607 | -36.5811 | -36.9413 | 34.07 | 33.3792 | 31.1771 | 29.0332 | 27.2986 | 17.4455 | 10.0384 | 2.3547 | -16.4558 | -16.3147 | -16.2674 | -16.4516 | 54.645 | 54.0461 | 52.1408 | 50.264 | 48.3134 | 36.4082 | 22.704 | 6.2671 | -30.6926 | -30.3779 | -30.2084 | -30.3621 | 40.884 | 40.3513 | 38.3766 | 36.3692 | 34.7808 | 25.8334 | 17.4703 | 10.3566
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | POOLE (HAMWORTHY) BSP | MINIMUM HEADROOM | SZ 00203 90789 | NO | NO | 7 | 46.5826 | 46.399 | 45.7347 | 44.7806 | 43.502 | 41.6775 | 39.8143 | 37.4296 | 34.9765 | 27.4173 | 23.5387 | 21.8928 | 48.0372 | 47.8551 | 47.4856 | 46.9898 | 46.4151 | 45.7856 | 45.0214 | 43.7498 | 42.3477 | 37.0898 | 31.374 | 21.8172 | 46.3246 | 46.1109 | 45.5803 | 44.8035 | 43.8003 | 42.5203 | 41.1635 | 39.4382 | 37.4982 | 32.8561 | 29.2041 | 27.3255
|  | POOLE (HAMWORTHY) BSP | EE |  |  |  |  | 46.5918 | 46.4541 | 45.8224 | 44.9438 | 43.7265 | 42.0969 | 40.3714 | 38.1255 | 35.7755 | 28.7908 | 24.7836 | 22.601 | 48.7357 | 48.5826 | 48.2683 | 47.8398 | 47.3102 | 46.803 | 46.201 | 45.1449 | 43.851 | 37.4908 | 33.4153 | 29.7806 | 47.1132 | 46.95 | 46.4592 | 45.7836 | 44.8183 | 43.7071 | 42.4673 | 40.8898 | 39.1643 | 32.8561 | 29.2041 | 27.3255
|  | POOLE (HAMWORTHY) BSP | HT |  |  |  |  | 46.5826 | 46.399 | 45.7347 | 44.7806 | 43.502 | 41.6775 | 39.8143 | 37.4296 | 34.9765 | 27.4173 | 23.5387 | 21.8928 | 48.0372 | 47.8551 | 47.4856 | 46.9898 | 46.4151 | 45.7856 | 45.0214 | 43.7498 | 42.3477 | 37.0898 | 34.5698 | 33.5961 | 46.3246 | 46.1109 | 45.5803 | 44.8035 | 43.8003 | 42.5203 | 41.1635 | 39.4382 | 37.4982 | 35.5551 | 34.2161 | 33.1403
|  | POOLE (HAMWORTHY) BSP | HE |  |  |  |  | 46.599 | 46.4632 | 45.8234 | 44.9663 | 43.8285 | 42.2581 | 40.5673 | 38.3551 | 36.0724 | 30.5969 | 27.5847 | 25.9898 | 48.0425 | 47.8909 | 47.5498 | 47.1098 | 46.5698 | 46.053 | 45.4288 | 44.4067 | 43.1119 | 37.8109 | 33.9467 | 30.2709 | 46.333 | 46.1719 | 45.6582 | 44.9677 | 44.0319 | 42.934 | 41.694 | 40.0877 | 38.3582 | 33.414 | 30.694 | 29.3646
|  | POOLE (HAMWORTHY) BSP | FB |  |  |  |  | 46.8806 | 46.8581 | 46.5061 | 46.0336 | 45.3643 | 44.7969 | 44.2428 | 43.4234 | 42.4306 | 37.8581 | 33.752 | 30.6 | 48.254 | 48.1477 | 47.9425 | 47.693 | 47.3288 | 46.8761 | 46.114 | 45.2288 | 44.3372 | 38.9898 | 31.374 | 21.8172 | 46.614 | 46.5488 | 46.2646 | 45.8825 | 45.3456 | 44.8993 | 44.453 | 43.8214 | 43.1846 | 39.6856 | 35.6614 | 32.3225
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ 63405 99685 | NO | YES | 14.162 | -14.49 | -14.0471 | -14.9471 | 72.9651 | 69.66 | 64.4794 | 58.0468 | 51.16 | 44.6325 | 13.2376 | -8.3298 | -19.6369 | 4.6088 | 4.2299 | 2.932 | 90.8499 | 87.433 | 83.5193 | 78.6677 | 73.2993 | 68.2835 | 47.0406 | 5.6277 | -50.9617 | -14.5691 | -14.2323 | -15.1301 | 73.0825 | 69.3899 | 64.7183 | 59.0435 | 52.8741 | 47.1246 | 28.1151 | 6.8641 | -3.4941
|  | PORTSMOUTH BSP | EE |  |  |  |  | -14.49 | -13.839 | -14.5094 | 73.857 | 71.311 | 66.4141 | 60.7396 | 54.2049 | 47.8988 | 18.1723 | -6.8981 | -19.6369 | 7.7743 | 7.6366 | 6.5366 | 94.6906 | 91.7315 | 88.1192 | 83.9141 | 78.9529 | 74.2723 | 47.0406 | 23.1294 | 0.2988 | -10.9471 | -10.4828 | -11.1583 | 77.4896 | 74.5815 | 70.309 | 65.4468 | 59.759 | 54.4345 | 28.1151 | 6.8641 | -3.4941
|  | PORTSMOUTH BSP | HT |  |  |  |  | -14.3992 | -14.0471 | -14.9471 | 72.9651 | 69.66 | 64.4794 | 58.0468 | 51.16 | 44.6325 | 13.2376 | -8.3298 | -17.9512 | 4.6846 | 4.2877 | 2.932 | 90.8499 | 87.433 | 83.5193 | 78.6677 | 73.2993 | 68.2835 | 48.5172 | 35.4025 | 28.6688 | -14.5691 | -14.2323 | -15.1301 | 73.0825 | 69.3899 | 64.7183 | 59.0435 | 52.8741 | 47.1246 | 41.0046 | 34.9046 | 29.6962
|  | PORTSMOUTH BSP | HE |  |  |  |  | -14.3543 | -13.59 | -14.1196 | 74.308 | 71.8315 | 67.759 | 62.6937 | 57.2764 | 51.9141 | 29.9366 | 13.5906 | 4.1947 | 4.7151 | 4.5951 | 3.4551 | 91.6456 | 88.7783 | 85.2509 | 80.8888 | 76.2109 | 71.712 | 47.2299 | 26.0677 | 3.4362 | -14.5428 | -13.9386 | -14.527 | 74.0941 | 71.1899 | 67.3583 | 62.6646 | 57.6835 | 52.9014 | 33.1972 | 19.1983 | 11.4593
|  | PORTSMOUTH BSP | FB |  |  |  |  | -13.3879 | -12.2594 | -11.5226 | 78.4478 | 78.2019 | 77.2651 | 76.1223 | 74.7019 | 72.9692 | 59.0212 | 36.5641 | 19.958 | 4.6088 | 4.2299 | 3.5162 | 92.233 | 90.2341 | 87.0941 | 83.5593 | 79.9141 | 76.052 | 49.0604 | 5.6277 | -50.9617 | -13.4501 | -12.4375 | -11.728 | 78.3625 | 78.2256 | 77.4077 | 76.1593 | 74.2614 | 72.1962 | 58.2141 | 36.8425 | 20.9414
FLEET-BRAMLEY GSP | PYESTOCK BSP | PYESTOCK BSP | MINIMUM HEADROOM | SU 82940 54553 | YES | NO | 77.45 | 48.3175 | 48.1206 | 47.64 | 46.9553 | 46.1328 | 44.744 | 43.2747 | 41.593 | 40.0369 | 35.0971 | 31.6236 | 29.9573 | -10.1342 | -10.2574 | -10.59 | -10.9647 | -11.4089 | -12.0774 | -12.8247 | -13.7384 | -14.5142 | -17.0447 | -18.3068 | -22.2974 | 44.5626 | 44.4511 | 44.1416 | 43.69 | 43.1395 | 42.2111 | 41.2174 | 40.09 | 38.9532 | 36.8784 | 34.9437 | 34.2657
|  | PYESTOCK BSP | EE |  |  |  |  | 48.3175 | 48.1206 | 47.7716 | 47.3165 | 46.7604 | 45.6053 | 44.3451 | 42.942 | 41.691 | 37.4604 | 34.3349 | 32.7685 | -9.5649 | -9.6822 | -9.9445 | -10.2139 | -10.5486 | -11.0639 | -11.6955 | -12.4445 | -13.0373 | -15.8353 | -17.6935 | -19.0057 | 45.1922 | 45.0851 | 44.8667 | 44.5586 | 44.1739 | 43.4055 | 42.5514 | 41.5973 | 40.7545 | 37.3514 | 35.1473 | 34.2657
|  | PYESTOCK BSP | HT |  |  |  |  | 48.3206 | 48.1359 | 47.64 | 46.9553 | 46.1328 | 44.744 | 43.2747 | 41.593 | 40.0369 | 35.0971 | 31.6236 | 29.9573 | -10.1332 | -10.2574 | -10.59 | -10.9647 | -11.4089 | -12.0774 | -12.8247 | -13.7384 | -14.5142 | -17.0447 | -18.2953 | -18.6458 | 44.5626 | 44.4616 | 44.1416 | 43.69 | 43.1395 | 42.2111 | 41.2174 | 40.09 | 38.9532 | 37.6479 | 36.7942 | 36.1826
|  | PYESTOCK BSP | HE |  |  |  |  | 48.3216 | 48.1267 | 47.7828 | 47.291 | 46.7032 | 45.5349 | 44.2614 | 42.9012 | 41.6144 | 37.8553 | 35.1522 | 33.9747 | -10.1342 | -10.2563 | -10.5289 | -10.8132 | -11.17 | -11.6889 | -12.3605 | -13.0921 | -13.7216 | -16.3742 | -18.1353 | -19.5121 | 44.5637 | 44.4511 | 44.2268 | 43.8889 | 43.4721 | 42.6858 | 41.7889 | 40.81 | 39.9332 | 36.8784 | 34.9437 | 34.2974
|  | PYESTOCK BSP | FB |  |  |  |  | 48.5838 | 48.4328 | 48.4573 | 48.3359 | 48.1798 | 47.8185 | 47.4859 | 47.1716 | 46.7869 | 44.5685 | 42.2685 | 40.9032 | -10.0005 | -10.1626 | -10.2089 | -10.3521 | -10.5489 | -10.9658 | -11.3626 | -11.7437 | -12.1942 | -14.8816 | -18.3068 | -22.2974 | 44.8005 | 44.7237 | 44.7679 | 44.7184 | 44.6279 | 44.3605 | 44.1142 | 43.8721 | 43.5447 | 41.6016 | 39.9416 | 38.6047
BRAMLEY (BASI) GSP | READING BSP | READING BSP | MINIMUM HEADROOM | SU 74642 73856 | NO | NO | 66.733 | 56.7132 | 55.9163 | 54.0153 | 51.2183 | 47.5122 | 41.3316 | 34.3173 | 26.9224 | 19.9041 | -5.2643 | -20.2112 | -26.2215 | 91.7575 | 90.2091 | 87.8859 | 85.227 | 81.8259 | 76.9901 | 71.3691 | 65.1417 | 59.2775 | 39.5849 | 20.9596 | -13.8393 | 67.1754 | 66.1859 | 64.0796 | 61.2649 | 57.6154 | 51.9775 | 45.5154 | 38.5523 | 31.9544 | 16.1112 | 2.8826 | -2.9082
|  | READING BSP | EE |  |  |  |  | 56.7132 | 56.1204 | 54.5153 | 52.303 | 49.3306 | 43.6469 | 36.6806 | 29.7745 | 23.3 | -1.4592 | -17.6449 | -25.199 | 94.9245 | 93.5663 | 91.4541 | 89.1214 | 86.2275 | 81.8122 | 76.4581 | 70.6377 | 65.1745 | 41.9469 | 26.4836 | 13.6449 | 71.0653 | 70.2714 | 68.4306 | 66.1561 | 63.2265 | 58.1275 | 51.9479 | 45.5285 | 39.4949 | 16.6469 | 2.8826 | -2.9082
|  | READING BSP | HT |  |  |  |  | 56.7214 | 55.9163 | 54.0153 | 51.2183 | 47.5122 | 41.3316 | 34.3173 | 26.9224 | 19.9041 | -5.2643 | -20.2112 | -26.2215 | 91.7575 | 90.2091 | 87.8859 | 85.227 | 81.8259 | 76.9901 | 71.3691 | 65.1417 | 59.2775 | 39.5849 | 30.007 | 26.7575 | 67.1754 | 66.1859 | 64.0796 | 61.2649 | 57.6154 | 51.9775 | 45.5154 | 38.5523 | 31.9544 | 25.6933 | 21.1059 | 16.7196
|  | READING BSP | HE |  |  |  |  | 56.7581 | 56.2143 | 54.6469 | 52.353 | 49.2551 | 43.8724 | 37.0755 | 30.2388 | 23.8826 | 3.9275 | -8.5082 | -14.8898 | 91.7786 | 90.3765 | 88.2038 | 85.7933 | 82.7586 | 78.3238 | 72.7912 | 66.8238 | 61.2575 | 40.2017 | 25.8828 | 12.2238 | 67.208 | 66.4301 | 64.5765 | 62.1544 | 59.0186 | 54.007 | 47.7259 | 41.187 | 35.1059 | 16.1112 | 5.4544 | 0.27541
|  | READING BSP | FB |  |  |  |  | 58.6388 | 59.4388 | 59.4183 | 59.1469 | 58.2724 | 56.4918 | 54.1632 | 51.7653 | 49.2796 | 34.8296 | 17.6234 | 6.2439 | 92.8533 | 92.2923 | 91.0912 | 89.8259 | 87.8165 | 84.8912 | 81.5796 | 78.0912 | 74.4249 | 51.6112 | 20.9596 | -13.8393 | 69.0786 | 69.6144 | 69.4891 | 69.0038 | 68.0007 | 66.1933 | 63.967 | 61.5575 | 59.0407 | 44.0354 | 26.8891 | 15.5144
FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN BSP | MINIMUM HEADROOM | SU 71580 74111 | NO | NO | 19.646 | 54.175 | 54.1107 | 53.7015 | 51.6199 | 50.0637 | 47.5719 | 44.6117 | 41.6229 | 38.6066 | 30.4841 | 24.9586 | 22.1464 | 62.2622 | 62.0032 | 61.7527 | 59.8137 | 59.1443 | 58.059 | 56.2474 | 54.618 | 52.9043 | 45.6264 | 35.058 | 21.5516 | 55.698 | 55.5137 | 55.198 | 53.4116 | 52.3337 | 50.6611 | 48.4737 | 46.3369 | 44.0737 | 38.2569 | 34.0691 | 32.0752
|  | READING TOWN BSP | EE |  |  |  |  | 54.175 | 54.177 | 53.7066 | 51.6199 | 50.0637 | 47.5719 | 44.6117 | 41.6229 | 38.6066 | 30.4841 | 24.9586 | 22.1464 | 63.5068 | 63.3007 | 63.064 | 61.1997 | 60.5252 | 59.4956 | 57.7038 | 56.0048 | 54.316 | 47.4079 | 42.2599 | 36.9885 | 57.1762 | 57.0538 | 56.7028 | 54.9864 | 53.8711 | 52.1456 | 49.9405 | 47.7875 | 45.5772 | 38.4221 | 34.0691 | 32.0752
|  | READING TOWN BSP | HT |  |  |  |  | 54.2015 | 54.1107 | 53.7015 | 51.625 | 50.2413 | 47.9923 | 45.2495 | 42.6341 | 39.8811 | 31.4331 | 26.4617 | 24.3729 | 62.2622 | 62.0032 | 61.7527 | 59.8137 | 59.1443 | 58.1106 | 56.2474 | 54.618 | 52.9043 | 47.9159 | 45.4685 | 44.1769 | 55.698 | 55.5137 | 55.198 | 53.4116 | 52.3674 | 50.7306 | 48.5727 | 46.619 | 44.4548 | 42.5464 | 40.4295 | 39.1832
|  | READING TOWN BSP | HE |  |  |  |  | 54.2199 | 54.2546 | 53.8168 | 51.7046 | 50.1433 | 47.7882 | 44.9413 | 42.0546 | 39.1076 | 32.7148 | 28.7525 | 26.7964 | 62.2716 | 62.0685 | 61.8295 | 59.9137 | 59.2327 | 58.2106 | 56.3811 | 54.6516 | 52.9232 | 46.4874 | 41.6453 | 36.4032 | 55.7074 | 55.6159 | 55.2864 | 53.4916 | 52.3337 | 50.6611 | 48.4737 | 46.3369 | 44.0737 | 38.2569 | 35.0474 | 33.6695
|  | READING TOWN BSP | FB |  |  |  |  | 54.5321 | 54.6995 | 54.6148 | 53.0046 | 52.0892 | 50.9209 | 49.2576 | 47.6484 | 46.0382 | 41.6892 | 36.9923 | 33.7188 | 62.2874 | 62.0622 | 61.8664 | 59.9853 | 59.2232 | 58.059 | 56.319 | 54.8127 | 53.298 | 45.6264 | 35.058 | 21.5516 | 56.0916 | 56.1885 | 56.1674 | 54.7527 | 54.0316 | 53.199 | 51.8969 | 50.7316 | 49.5853 | 45.4948 | 40.8327 | 37.7316
MANNINGTON GSP | REDHILL BSP | REDHILL BSP | MINIMUM HEADROOM | SZ 08581 96162 | NO | NO | 16.422 | 53.0284 | 52.2703 | 51.1509 | 49.4845 | 47.5111 | 42.7264 | 37.6386 | 32.1274 | 26.8764 | 9.5141 | -3.1757 | -9.0961 | 61.0326 | 60.2652 | 59.3694 | 58.3757 | 57.0663 | 54.6568 | 51.7231 | 48.6147 | 45.7273 | 36.6315 | 28.3041 | 11.5705 | 51.9505 | 51.0726 | 49.9768 | 48.4757 | 46.6326 | 42.8915 | 38.6873 | 34.281 | 30.122 | 23.4326 | 15.1001 | 11.0042
|  | REDHILL BSP | EE |  |  |  |  | 53.0937 | 52.5723 | 51.6743 | 50.5519 | 49.1927 | 45.1805 | 40.8764 | 36.3274 | 31.9294 | 16.6458 | 4.9611 | -1.494 | 62.3491 | 61.7348 | 60.9593 | 60.2093 | 59.1603 | 57.2389 | 54.8062 | 52.2215 | 49.8062 | 39.0695 | 31.6685 | 25.495 | 53.6032 | 52.8991 | 51.9644 | 50.8838 | 49.5879 | 46.5011 | 42.997 | 39.3287 | 35.8766 | 23.5185 | 15.1001 | 11.0042
|  | REDHILL BSP | HT |  |  |  |  | 53.0284 | 52.2703 | 51.1509 | 49.4845 | 47.5111 | 42.7264 | 37.6386 | 32.1274 | 26.8764 | 9.5141 | -3.1757 | -9.0961 | 61.0326 | 60.2652 | 59.3694 | 58.3757 | 57.0663 | 54.6568 | 51.7231 | 48.6147 | 45.7273 | 36.6315 | 32.2147 | 30.9799 | 51.9505 | 51.0726 | 49.9768 | 48.4757 | 46.6326 | 42.8915 | 38.6873 | 34.281 | 30.122 | 26.2168 | 23.6863 | 21.0557
|  | REDHILL BSP | HE |  |  |  |  | 53.1131 | 52.6192 | 51.7641 | 50.4948 | 48.9478 | 45.2162 | 41.0999 | 36.7733 | 32.5896 | 19.7682 | 9.605 | 4.6345 | 61.082 | 60.4578 | 59.6947 | 58.9105 | 57.7715 | 55.8652 | 53.3189 | 50.7168 | 48.2715 | 38.242 | 30.942 | 24.3041 | 52.0094 | 51.3115 | 50.4168 | 49.2073 | 47.7031 | 44.7178 | 41.182 | 37.5789 | 34.1663 | 23.4326 | 16.0241 | 12.6547
|  | REDHILL BSP | FB |  |  |  |  | 53.9325 | 54.1845 | 54.4223 | 54.3111 | 54.1529 | 53.6886 | 53.0182 | 52.3172 | 51.4917 | 45.0203 | 35.3396 | 29.5917 | 61.3431 | 61.0652 | 60.881 | 60.3157 | 59.6463 | 58.5326 | 57.2041 | 55.8515 | 54.3568 | 43.6126 | 28.3041 | 11.5705 | 52.8473 | 52.9936 | 53.2368 | 52.942 | 52.722 | 52.1547 | 51.3305 | 50.522 | 49.5347 | 42.561 | 33.4947 | 28.1999
NURSLING GSP | ROWNHAMS BSP | ROWNHAMS BSP | MINIMUM HEADROOM | SU 37168 16854 | NO | NO | 53.076 | -0.23234 | -1.1609 | -2.1834 | 109.799 | 106.6052 | 101.5837 | 95.0174 | 88.045 | 77.7225 | 49.5001 | 26.9195 | 14.4337 | 23.8017 | 22.1691 | 21.0323 | 128.7439 | 125.6744 | 122.1333 | 116.7239 | 110.3775 | 98.7986 | 74.1596 | 55.6817 | 35.9228 | -0.12983 | -1.1235 | -1.8772 | 107.6123 | 104.2744 | 99.9081 | 93.6039 | 86.7702 | 74.3702 | 49.627 | 32.727 | 18.8449
|  | ROWNHAMS BSP | EE |  |  |  |  | -0.20479 | -0.5354 | -1.7354 | 110.7133 | 108.1878 | 103.3133 | 97.5062 | 91.2368 | 84.297 | 56.2705 | 32.346 | 21.1848 | 25.7608 | 24.6383 | 23.2669 | 131.2444 | 128.6444 | 125.3148 | 121.0138 | 116.0006 | 110.2393 | 86.0965 | 63.273 | 49.571 | 2.6057 | 2.1771 | 1.1373 | 111.072 | 108.3791 | 104.2067 | 99.0699 | 93.1873 | 86.4944 | 60.7914 | 38.0414 | 28.5852
|  | ROWNHAMS BSP | HT |  |  |  |  | -0.23234 | -1.1609 | -2.1834 | 109.799 | 106.6052 | 101.5837 | 95.0174 | 88.045 | 79.4623 | 49.5001 | 26.9195 | 14.4337 | 23.8017 | 22.1691 | 21.0323 | 128.7439 | 125.6744 | 122.1333 | 116.7239 | 110.927 | 103.0081 | 80.1007 | 62.607 | 52.8291 | -0.12983 | -1.1235 | -1.8772 | 107.6123 | 104.2744 | 99.9081 | 93.6039 | 86.7702 | 77.8554 | 71.6323 | 64.1796 | 59.3723
|  | ROWNHAMS BSP | HE |  |  |  |  | -0.17214 | -0.43336 | -1.6058 | 110.7215 | 108.0797 | 103.4082 | 97.0817 | 88.9766 | 77.7225 | 52.4205 | 34.6592 | 21.3235 | 23.8407 | 22.6902 | 21.2733 | 129.1639 | 126.4786 | 123.1702 | 117.926 | 110.3775 | 98.7986 | 74.1596 | 55.6817 | 36.1365 | -0.064568 | -0.46352 | -1.4877 | 108.2723 | 105.4007 | 101.3007 | 95.2639 | 86.8344 | 74.3702 | 49.627 | 32.727 | 18.8449
|  | ROWNHAMS BSP | FB |  |  |  |  | 0.70541 | 1.1819 | 1.2105 | 114.8858 | 114.4154 | 113.4358 | 111.8225 | 109.7766 | 107.0429 | 92.5337 | 72.1092 | 59.0501 | 24.8386 | 24.1596 | 23.1228 | 131.5796 | 130.2081 | 128.266 | 125.6333 | 122.5291 | 118.5817 | 97.5017 | 66.5691 | 35.9228 | 1.3175 | 1.5449 | 1.4091 | 112.3744 | 112.067 | 111.1502 | 109.407 | 107.1428 | 104.0365 | 88.2112 | 66.6428 | 53.2439
MANNINGTON GSP | SALISBURY BSP | SALISBURY BSP | MINIMUM HEADROOM | SU 11049 31395 | NO | NO | 31.786 | 50.4543 | 49.9278 | 48.7513 | 46.7798 | 44.1237 | 40.1451 | 35.5207 | 30.2543 | 25.4605 | 7.9931 | -4.6181 | -9.6753 | 66.3557 | 65.5546 | 64.1494 | 62.0304 | 59.602 | 56.7736 | 53.081 | 48.9873 | 45.2852 | 31.7999 | 24.289 | 8.2241 | 51.8867 | 51.4331 | 50.2289 | 48.2625 | 45.5373 | 42.0562 | 37.7331 | 32.8952 | 28.5299 | 17.0394 | 7.3074 | 3.6921
|  | SALISBURY BSP | EE |  |  |  |  | 50.4543 | 49.9278 | 48.7513 | 46.7798 | 44.1758 | 40.2094 | 35.6064 | 30.8064 | 26.4105 | 9.9502 | -2.2018 | -7.4773 | 67.9074 | 67.0217 | 65.6992 | 63.8594 | 61.4921 | 58.8043 | 55.5584 | 52.0931 | 48.8656 | 33.9339 | 24.289 | 18.7074 | 53.9625 | 53.3992 | 52.2502 | 50.4472 | 47.9064 | 44.5329 | 40.5809 | 36.4084 | 32.5564 | 17.2166 | 7.3074 | 3.6921
|  | SALISBURY BSP | HT |  |  |  |  | 50.486 | 50.1002 | 48.9849 | 46.9237 | 44.4441 | 40.5074 | 35.5207 | 30.2543 | 25.4605 | 7.9931 | -4.6181 | -9.6753 | 66.3567 | 65.5546 | 64.1494 | 62.0304 | 59.602 | 56.7736 | 53.081 | 48.9873 | 45.2852 | 31.7999 | 24.5178 | 23.3946 | 51.8952 | 51.4636 | 50.3089 | 48.2762 | 45.6625 | 42.1931 | 37.7331 | 32.8952 | 28.5299 | 23.671 | 20.552 | 17.9678
|  | SALISBURY BSP | HE |  |  |  |  | 50.4686 | 50.039 | 48.8482 | 46.8033 | 44.1237 | 40.1451 | 35.688 | 30.7982 | 26.5186 | 13.4268 | 4.2819 | -0.27628 | 66.3557 | 65.5736 | 64.1704 | 62.1641 | 59.6346 | 56.8483 | 53.642 | 49.9083 | 46.6462 | 33.3304 | 25.7104 | 19.582 | 51.8867 | 51.4331 | 50.2289 | 48.2625 | 45.5373 | 42.0562 | 38.1436 | 33.7131 | 29.8478 | 17.0394 | 9.6973 | 6.4078
|  | SALISBURY BSP | FB |  |  |  |  | 51.4513 | 51.5992 | 51.2319 | 50.9258 | 49.94 | 48.7737 | 47.6002 | 46.3002 | 44.8421 | 34.8217 | 23.5411 | 15.9309 | 67.0441 | 66.6778 | 65.9546 | 65.382 | 63.7462 | 61.9041 | 60.0578 | 58.0946 | 55.9052 | 42.1515 | 25.6767 | 8.2241 | 53.0267 | 53.1204 | 52.8625 | 52.672 | 51.6478 | 50.3794 | 49.0362 | 47.552 | 45.8678 | 35.2299 | 24.1931 | 16.7783
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST 85442 23791 | NO | NO | 41.856 | 33.9602 | 33.9398 | 33.4939 | 31.8582 | 29.4184 | 25.601 | 21.2337 | 16.8796 | 12.4368 | -1.3102 | -11.6581 | -17.6418 | 49.7092 | 49.4071 | 49.0219 | 47.7008 | 45.7692 | 43.4313 | 40.4587 | 37.4924 | 34.4419 | 25.1292 | 20.7082 | 9.6313 | 39.2033 | 38.9254 | 38.4528 | 36.7697 | 34.5286 | 31.3539 | 27.5781 | 23.8139 | 19.936 | 13.356 | 6.551 | 3.3623
|  | SHAFTESBURY BSP | EE |  |  |  |  | 33.9919 | 34.0449 | 33.7806 | 32.7102 | 30.5225 | 27.1337 | 23.2123 | 19.1684 | 15.2521 | 2.4643 | -6.8806 | -12.0704 | 50.9482 | 50.7135 | 50.4125 | 49.5064 | 47.6217 | 45.5829 | 43.0064 | 40.3125 | 37.7727 | 27.4707 | 21.2115 | 16.9135 | 40.8317 | 40.6143 | 40.2694 | 39.1133 | 37.0266 | 34.3704 | 31.0908 | 27.6806 | 24.4194 | 13.3959 | 6.551 | 3.3623
|  | SHAFTESBURY BSP | HT |  |  |  |  | 33.9602 | 33.9398 | 33.4939 | 31.8582 | 29.4184 | 25.601 | 21.2337 | 16.8796 | 12.4368 | -1.3102 | -11.6581 | -17.6418 | 49.7092 | 49.4071 | 49.0219 | 47.7008 | 45.7692 | 43.4313 | 40.4587 | 37.4924 | 34.4419 | 25.1292 | 20.7082 | 19.7292 | 39.2033 | 38.9254 | 38.4528 | 36.7697 | 34.5286 | 31.3539 | 27.5781 | 23.8139 | 19.936 | 16.5949 | 14.497 | 12.5275
|  | SHAFTESBURY BSP | HE |  |  |  |  | 33.9898 | 34.0643 | 33.8286 | 32.551 | 30.4521 | 26.8623 | 22.8551 | 18.7357 | 14.6215 | 5.151 | -3.1306 | -7.403 | 49.7219 | 49.4871 | 49.205 | 48.0682 | 46.3113 | 44.1345 | 41.5145 | 38.7871 | 36.0587 | 27.3892 | 21.9524 | 17.5303 | 39.2265 | 39.0265 | 38.7065 | 37.2886 | 35.2812 | 32.3981 | 28.9833 | 25.4697 | 21.937 | 13.356 | 7.3307 | 4.516
|  | SHAFTESBURY BSP | FB |  |  |  |  | 35.0072 | 35.5745 | 35.8786 | 35.9235 | 36.0633 | 35.5337 | 34.9092 | 34.2 | 33.3602 | 25.149 | 16.6541 | 11.201 | 50.4598 | 50.5734 | 50.4787 | 50.1787 | 49.9861 | 48.9734 | 47.8145 | 46.5882 | 45.2608 | 34.9787 | 22.6766 | 9.6313 | 40.3507 | 40.7718 | 40.9581 | 40.8718 | 41.0191 | 40.3265 | 39.5275 | 38.6507 | 37.7223 | 29.456 | 21.3633 | 16.1265
IVER 132KV GSP | SLOUGH BSP | SLOUGH BSP | MINIMUM HEADROOM | SU 95574 81752 | NO | YES | 94.823 | -25.4156 | 87.716 | 60.2293 | 60.5069 | 60.5834 | 60.4732 | 60.1885 | 59.8834 | 59.5018 | 54.9722 | 48.2201 | 43.8803 | -27.0423 | 80.9619 | 44.5135 | 44.4745 | 44.2556 | 43.6903 | 42.7724 | 41.8261 | 40.8251 | 32.9987 | 21.2124 | 7.6366 | -24.5676 | 86.1029 | 50.0808 | 50.0672 | 49.9272 | 49.7008 | 49.3219 | 48.9082 | 48.4472 | 44.6819 | 39.6577 | 35.4756
|  | SLOUGH BSP | EE |  |  |  |  | -25.4156 | 87.716 | 87.6732 | 87.3844 | 86.6916 | 84.9252 | 81.2742 | 77.7905 | 74.4201 | 60.6395 | 51.114 | 46.965 | -25.1033 | 82.9007 | 82.7222 | 82.3691 | 81.815 | 81.0242 | 77.8864 | 74.7273 | 71.666 | 57.5354 | 48.0242 | 41.5589 | -22.6533 | 87.9854 | 87.7354 | 87.3058 | 86.5936 | 85.4467 | 82.2395 | 79.066 | 76.0569 | 62.4742 | 53.3109 | 49.615
|  | SLOUGH BSP | HT |  |  |  |  | -25.3931 | 87.763 | 87.6905 | 87.2701 | 86.2773 | 84.4569 | 81.9895 | 78.9364 | 75.7864 | 63.8436 | 56.1854 | 53.8109 | -27.0423 | 80.9619 | 80.7577 | 80.3598 | 79.7114 | 78.8651 | 77.1293 | 74.3924 | 71.5998 | 61.1756 | 55.5019 | 53.8703 | -24.5665 | 86.1145 | 85.8777 | 85.3051 | 84.3956 | 83.1398 | 81.4345 | 78.6829 | 75.9956 | 73.4145 | 70.8924 | 68.5314
|  | SLOUGH BSP | HE |  |  |  |  | -25.3799 | 87.7803 | 87.766 | 87.3977 | 86.6018 | 84.9467 | 82.7028 | 80.2711 | 77.9324 | 69.9732 | 64.5905 | 61.9201 | -27.0413 | 80.9629 | 80.7798 | 80.4177 | 79.844 | 79.0429 | 77.5187 | 75.5082 | 73.5566 | 64.6735 | 58.2998 | 52.3682 | -24.5676 | 86.1029 | 85.8766 | 85.3545 | 84.5419 | 83.4166 | 81.8356 | 79.8608 | 77.9787 | 70.7651 | 65.9198 | 63.6251
|  | SLOUGH BSP | FB |  |  |  |  | -24.835 | 88.5028 | 60.2293 | 60.5069 | 60.5834 | 60.4732 | 60.1885 | 59.8834 | 59.5018 | 54.9722 | 48.2201 | 43.8803 | -26.7539 | 81.3461 | 44.5135 | 44.4745 | 44.2556 | 43.6903 | 42.7724 | 41.8261 | 40.8251 | 32.9987 | 21.2124 | 7.6366 | -24.0823 | 86.8051 | 50.0808 | 50.0672 | 49.9272 | 49.7008 | 49.3219 | 48.9082 | 48.4472 | 44.6819 | 39.6577 | 35.4756
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | SOUTHAMPTON (RESERVE) BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | NO | 29.698 | -5.7487 | -5.6089 | -5.6079 | -5.7896 | -6.1559 | -7.3314 | -9.4151 | -11.2916 | -18.3661 | -25.6314 | -34.0232 | -42.1212 | 6.0829 | 5.9535 | 5.7577 | 5.5187 | 5.1598 | 4.445 | 2.3566 | -1.0865 | -9.9171 | -21.0897 | -33.0402 | -48.4686 | -5.8644 | -5.7655 | -5.8265 | -6.0286 | -6.4718 | -7.6129 | -10.0655 | -13.5444 | -22.6497 | -32.1129 | -41.2318 | -52.2444
|  | SOUTHAMPTON (RESERVE) BSP | EE |  |  |  |  | -5.7487 | -5.6089 | -5.5794 | -5.6508 | -5.7406 | -6.162 | -6.9304 | -9.1008 | -11.6457 | -18.8753 | -31.8324 | -36.3212 | 7.6023 | 7.5625 | 7.4288 | 7.2574 | 7.0411 | 6.5982 | 5.7074 | 3.7737 | 1.0431 | -8.7263 | -24.8661 | -33.9528 | -4.0855 | -3.9977 | -4.0283 | -4.1273 | -4.314 | -4.914 | -5.9794 | -8.2773 | -11.513 | -19.9589 | -34.2049 | -39.1661
|  | SOUTHAMPTON (RESERVE) BSP | HT |  |  |  |  | -5.7324 | -5.5916 | -5.6079 | -5.7896 | -6.1559 | -7.3314 | -9.4151 | -11.2916 | -14.8365 | -22.5028 | -34.0232 | -40.6957 | 6.2198 | 6.1777 | 6.0103 | 5.7745 | 5.2882 | 4.445 | 2.3566 | 0.25452 | -4.3602 | -13.7686 | -27.276 | -35.9129 | -5.8644 | -5.7655 | -5.8265 | -6.0286 | -6.4718 | -7.6129 | -10.0655 | -12.636 | -17.5497 | -19.8739 | -21.0539 | -22.7865
|  | SOUTHAMPTON (RESERVE) BSP | HE |  |  |  |  | -5.7089 | -5.5396 | -5.4804 | -5.5528 | -5.6242 | -5.9712 | -7.2753 | -11.2304 | -18.3661 | -25.6314 | -33.3059 | -42.1212 | 6.2187 | 6.1829 | 6.0461 | 5.8535 | 5.6314 | 5.1945 | 3.505 | -1.0865 | -9.9171 | -21.0897 | -33.0402 | -48.4686 | -5.8518 | -5.7318 | -5.7339 | -5.8539 | -6.216 | -6.8076 | -8.6602 | -13.5444 | -22.6497 | -32.1129 | -41.2318 | -52.2444
|  | SOUTHAMPTON (RESERVE) BSP | FB |  |  |  |  | -5.6314 | -5.4385 | -5.311 | -5.2263 | -5.1467 | -5.163 | -5.4804 | -5.96 | -7.4783 | -12.2273 | -17.86 | -24.7151 | 6.0829 | 5.9535 | 5.7577 | 5.5187 | 5.1598 | 4.6766 | 3.7671 | 2.6577 | 0.64504 | -8.8171 | -23.3655 | -41.7981 | -5.7665 | -5.6234 | -5.5455 | -5.4739 | -5.4139 | -5.4465 | -5.8897 | -6.6929 | -8.4729 | -14.5129 | -22.316 | -30.0076
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | SOUTHAMPTON (MAIN) BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | NO | 37.202 | 22.1553 | 21.8695 | 21.3542 | 20.6206 | 18.6604 | 15.9114 | 10.7379 | 3.6502 | -11.9733 | -31.857 | -50.1907 | -69.4264 | 30.2299 | 29.5099 | 28.2446 | 27.072 | 24.9288 | 22.5583 | 17.0762 | 7.8941 | -11.1733 | -33.948 | -56.8943 | -84.2585 | 26.6878 | 26.0888 | 24.9804 | 23.833 | 21.6509 | 19.0793 | 13.4604 | 4.4499 | -14.7491 | -36.3543 | -57.3901 | -80.6901
|  | SOUTHAMPTON (MAIN) BSP | EE |  |  |  |  | 22.1553 | 21.8695 | 21.4308 | 20.9471 | 20.0665 | 17.3246 | 13.6022 | 8.6665 | 2.8981 | -17.3162 | -44.01 | -54.5284 | 32.0137 | 31.3188 | 30.1759 | 29.1657 | 27.8208 | 25.4769 | 22.0535 | 17.2137 | 11.1504 | -8.8965 | -39.5567 | -54.4516 | 28.6014 | 28.0004 | 27.0075 | 26.1443 | 24.9239 | 22.4086 | 18.7708 | 13.6667 | 7.4198 | -12.622 | -42.4904 | -53.7843
|  | SOUTHAMPTON (MAIN) BSP | HT |  |  |  |  | 22.1665 | 21.8818 | 21.3542 | 20.6206 | 18.6604 | 15.9114 | 10.7379 | 5.1144 | -4.1539 | -25.3009 | -49.7754 | -64.7641 | 30.2299 | 29.5099 | 28.2446 | 27.072 | 24.9288 | 22.5583 | 17.0762 | 11.2151 | 0.59935 | -18.8754 | -45.2764 | -62.8375 | 26.6878 | 26.0888 | 24.9804 | 23.833 | 21.6509 | 19.0793 | 13.4604 | 7.3015 | -3.5891 | -9.308 | -12.5712 | -16.5785
|  | SOUTHAMPTON (MAIN) BSP | HE |  |  |  |  | 22.1981 | 21.9777 | 21.59 | 21.0644 | 20.091 | 17.5297 | 12.6787 | 3.6502 | -11.9733 | -31.857 | -50.1907 | -69.4264 | 30.2404 | 29.5488 | 28.3783 | 27.3436 | 25.9383 | 23.592 | 18.4162 | 7.8941 | -11.1733 | -33.948 | -56.8943 | -84.2585 | 26.6972 | 26.1288 | 25.1436 | 24.2046 | 22.872 | 20.4215 | 15.1267 | 4.4499 | -14.7491 | -36.3543 | -57.3901 | -80.6901
|  | SOUTHAMPTON (MAIN) BSP | FB |  |  |  |  | 22.5165 | 22.392 | 22.2614 | 22.193 | 21.9889 | 21.5359 | 20.2104 | 18.5124 | 15.3685 | 2.1277 | -12.7335 | -26.5213 | 30.4151 | 29.7004 | 28.9762 | 28.2867 | 27.4046 | 25.7983 | 23.2741 | 20.6867 | 16.293 | -2.6891 | -26.1754 | -53.6249 | 27.2615 | 26.9078 | 26.5657 | 26.253 | 25.8678 | 24.9351 | 23.0762 | 21.0383 | 17.312 | 2.4036 | -14.4385 | -29.9228
NURSLING GSP | SOUTHAMPTON C BSP | SOUTHAMPTON C BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | NO | 5.698 |  |  |  | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 |  |  |  | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 |  |  |  | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482
|  | SOUTHAMPTON C BSP | EE | [7 empty] | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 |  |  |  | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 |  |  |  | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482
|  | SOUTHAMPTON C BSP | HT | [7 empty] | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 |  |  |  | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 |  |  |  | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482
|  | SOUTHAMPTON C BSP | HE | [7 empty] | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 |  |  |  | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 |  |  |  | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482
|  | SOUTHAMPTON C BSP | FB | [7 empty] | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 | 225.5482 |  |  |  | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 | 217.1482 |  |  |  | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482 | 220.7482
LALEHAM GSP | STAINES BSP | STAINES BSP | MINIMUM HEADROOM | TQ 04585 72135 | NO | NO | 35.415 | 2.705 | 2.3458 | 1.9692 | 0.5917 | -1.2491 | 81.309 | 77.6692 | 73.2356 | 68.8876 | 52.4417 | 43.3386 | 38.8152 | 13.0442 | 12.7779 | 12.3557 | 11.46 | 10.2273 | 85.2568 | 82.9326 | 78.8231 | 74.8 | 60.8 | 47.9042 | 23.4947 | 1.8463 | 1.6126 | 1.2084 | -0.054779 | -2.3053 | 74.8726 | 71.181 | 66.7789 | 62.4831 | 51.1611 | 41.3652 | 37.3774
|  | STAINES BSP | EE |  |  |  |  | 2.705 | 2.3458 | 1.9692 | 0.98762 | -0.31136 | 82.6641 | 79.0141 | 74.8499 | 70.8448 | 53.756 | 43.3386 | 38.8152 | 16.6407 | 16.3907 | 16.0264 | 15.2927 | 14.3182 | 89.606 | 87.2978 | 83.3825 | 79.6233 | 62.2244 | 50.8264 | 41.4917 | 5.7448 | 5.4764 | 5.1131 | 4.2468 | 2.5254 | 80.0764 | 76.3192 | 72.205 | 68.2539 | 51.1611 | 41.3652 | 37.3774
|  | STAINES BSP | HT |  |  |  |  | 2.7448 | 2.4244 | 1.9713 | 0.5917 | -1.2491 | 81.309 | 77.6692 | 73.2356 | 68.8876 | 52.4417 | 43.8346 | 41.509 | 13.0515 | 12.7926 | 12.3557 | 11.46 | 10.2273 | 85.2568 | 82.9326 | 78.8231 | 74.8 | 60.8 | 54.3357 | 52.3263 | 1.8526 | 1.6168 | 1.2084 | -0.054779 | -2.3053 | 74.8726 | 71.181 | 66.7789 | 62.4831 | 58.3115 | 54.7736 | 51.5621
|  | STAINES BSP | HE |  |  |  |  | 2.7407 | 2.4305 | 2.0978 | 1.0448 | -0.34402 | 82.7203 | 79.5968 | 75.8703 | 72.2907 | 60.0529 | 52.8866 | 49.7631 | 13.0442 | 12.7779 | 12.3979 | 11.6326 | 10.6052 | 85.8484 | 84.0768 | 80.5042 | 77.0631 | 62.6863 | 52.7084 | 43.6063 | 1.8463 | 1.6126 | 1.2821 | 0.30733 | -1.5727 | 75.9768 | 72.7579 | 69.0379 | 65.4621 | 52.9242 | 46.1368 | 43.3947
|  | STAINES BSP | FB |  |  |  |  | 3.806 | 4.0152 | 4.0172 | 4.0703 | 3.9703 | 89.008 | 88.2499 | 87.3784 | 86.0897 | 77.6795 | 65.9131 | 57.857 | 13.5515 | 13.5389 | 13.3463 | 13.0873 | 12.6431 | 88.4842 | 87.4652 | 85.8926 | 83.7263 | 69.4547 | 47.9042 | 23.4947 | 2.9263 | 3.2284 | 3.2357 | 3.2915 | 3.2389 | 83.0021 | 82.1852 | 81.0547 | 79.3189 | 69.8842 | 57.6684 | 49.4294
MINETY GSP | STRATTON (RESERVE) BSP | STRATTON (RESERVE) BSP | MINIMUM HEADROOM | SU 17028 88748 | NO | NO | 45.49 | 42.1195 | 41.3236 | 40.7757 | 39.4104 | 37.5022 | 34.0175 | 29.8032 | 25.444 | 21.4471 | 8.1104 | -0.25291 | -3.9968 | 48.4403 | 47.2256 | 46.4498 | 45.1213 | 43.3235 | 40.5077 | 37.0529 | 33.3603 | 30.0835 | 20.4129 | 15.242 | 4.0666 | 42.6445 | 41.6245 | 41.0687 | 39.714 | 37.8403 | 34.6235 | 30.7277 | 26.6571 | 22.9866 | 13.3708 | 7.2328 | 4.4297
|  | STRATTON (RESERVE) BSP | EE |  |  |  |  | 42.2267 | 41.6471 | 40.9583 | 39.742 | 38.3206 | 35.3195 | 31.4961 | 27.3206 | 23.4736 | 8.6563 | 0.28281 | -3.7733 | 49.7297 | 48.7267 | 47.8542 | 46.6532 | 45.3236 | 43.0542 | 40.0124 | 36.5971 | 33.6267 | 21.7053 | 15.242 | 10.9471 | 44.1685 | 43.3716 | 42.692 | 41.5073 | 40.1359 | 37.4971 | 34.0359 | 30.2308 | 26.8818 | 13.9338 | 7.2328 | 4.4297
|  | STRATTON (RESERVE) BSP | HT |  |  |  |  | 42.1195 | 41.3236 | 40.7757 | 39.4104 | 37.5022 | 34.0175 | 29.8032 | 25.444 | 21.4471 | 8.1104 | -0.25291 | -3.9968 | 48.4403 | 47.2256 | 46.4498 | 45.1213 | 43.3235 | 40.5077 | 37.0529 | 33.3603 | 30.0835 | 20.4129 | 15.7087 | 14.4877 | 42.6445 | 41.6245 | 41.0687 | 39.714 | 37.8403 | 34.6235 | 30.7277 | 26.6571 | 22.9866 | 19.7256 | 17.3245 | 15.035
|  | STRATTON (RESERVE) BSP | HE |  |  |  |  | 42.241 | 41.6828 | 41.0206 | 39.7206 | 38.244 | 35.2032 | 31.3573 | 27.1308 | 23.243 | 10.7124 | 4.1573 | 0.89607 | 48.5119 | 47.4835 | 46.5898 | 45.3298 | 43.9677 | 41.5824 | 38.4308 | 34.8603 | 31.7761 | 20.8508 | 15.3898 | 10.9319 | 42.7277 | 41.9224 | 41.2403 | 39.955 | 38.5119 | 35.755 | 32.1719 | 28.1824 | 24.7182 | 13.3708 | 8.2213 | 5.8635
|  | STRATTON (RESERVE) BSP | FB |  |  |  |  | 43.1512 | 43.1379 | 43.0624 | 42.5195 | 42.0022 | 41.1002 | 39.8277 | 38.4185 | 36.6451 | 26.0675 | 18.3777 | 13.3675 | 49.2192 | 48.7698 | 48.3508 | 47.4603 | 46.6413 | 45.394 | 43.8708 | 42.2382 | 40.2277 | 27.8971 | 16.0656 | 4.0666 | 43.6982 | 43.534 | 43.4592 | 42.8845 | 42.4519 | 41.5256 | 40.3129 | 38.9982 | 37.3066 | 26.9971 | 19.1571 | 14.1866
MINETY GSP | STRATTON (MAIN) BSP | STRATTON (MAIN) BSP | MINIMUM HEADROOM | SU 17028 88748 | NO | NO | 15.693 | 54.0107 | 53.2515 | 52.8015 | 51.9025 | 50.5729 | 48.3454 | 45.4831 | 42.376 | 39.4495 | 29.325 | 21.8893 | 17.6546 | 54.7972 | 53.9424 | 53.5561 | 53.0708 | 51.7898 | 50.1603 | 47.8014 | 45.2329 | 43.0087 | 36.8151 | 27.1035 | 12.6645 | 48.0845 | 47.4266 | 47.1182 | 46.6098 | 45.3414 | 43.5087 | 40.9708 | 38.3161 | 36.0793 | 29.6558 | 23.3099 | 19.8518
|  | STRATTON (MAIN) BSP | EE |  |  |  |  | 54.0107 | 53.8556 | 52.8015 | 51.9025 | 51.1229 | 49.1882 | 46.728 | 43.7617 | 40.828 | 29.6076 | 22.2413 | 17.6546 | 56.2834 | 56.1987 | 55.1599 | 54.5967 | 54.1048 | 52.864 | 50.912 | 48.5732 | 46.4671 | 37.6487 | 31.2885 | 25.1732 | 49.8201 | 49.8089 | 48.912 | 48.3416 | 47.8181 | 46.3742 | 44.3558 | 41.9558 | 39.6671 | 29.6558 | 23.3099 | 19.8518
|  | STRATTON (MAIN) BSP | HT |  |  |  |  | 54.0495 | 53.2515 | 52.827 | 52.0097 | 50.5729 | 48.3454 | 45.4831 | 42.376 | 39.4495 | 29.325 | 21.8893 | 18.0852 | 54.7982 | 53.9424 | 53.5561 | 53.0793 | 51.7898 | 50.1603 | 47.8014 | 45.2329 | 43.0087 | 38.014 | 34.4172 | 32.4887 | 48.0845 | 47.4266 | 47.1182 | 46.6098 | 45.3414 | 43.5087 | 40.9708 | 38.3161 | 36.0793 | 34.2119 | 32.6266 | 31.2003
|  | STRATTON (MAIN) BSP | HE |  |  |  |  | 54.0372 | 53.9189 | 52.8995 | 51.9933 | 51.2127 | 49.4138 | 47.0454 | 44.2546 | 41.426 | 32.1648 | 26.9627 | 23.9505 | 54.7972 | 54.7151 | 53.6466 | 53.0708 | 52.5677 | 51.3161 | 49.2835 | 46.8445 | 44.6498 | 36.8151 | 31.2456 | 25.2677 | 48.0908 | 48.1087 | 47.2119 | 46.6108 | 46.0635 | 44.6435 | 42.5866 | 40.1256 | 37.9393 | 29.9319 | 25.4761 | 22.8782
|  | STRATTON (MAIN) BSP | FB |  |  |  |  | 54.4505 | 54.4709 | 54.3974 | 53.6423 | 53.2719 | 52.9046 | 52.0831 | 50.9607 | 49.8505 | 42.5168 | 37.2525 | 32.5117 | 55.0814 | 55.0298 | 54.9035 | 53.9666 | 53.3403 | 52.6172 | 51.374 | 49.8087 | 48.2435 | 37.9235 | 27.1035 | 12.6645 | 48.4993 | 48.6214 | 48.6635 | 48.0256 | 47.7856 | 47.5866 | 46.8719 | 45.8266 | 44.7845 | 38.0203 | 33.0308 | 28.3687
MINETY GSP | SWINDON BSP | SWINDON BSP | MINIMUM HEADROOM | SU 12447 87062 | NO | NO | 21.663 | 39.2068 | 39.0609 | 38.1272 | 36.613 | 34.0436 | 26.4997 | 21.7385 | 16.7538 | 12.1385 | -3.8258 | -17.2024 | -24.6687 | 51.0439 | 50.4808 | 49.3145 | 47.8892 | 45.1997 | 37.0218 | 33.0787 | 28.7176 | 24.7166 | 10.3081 | 0.87551 | -18.5371 | 38.5029 | 38.4439 | 37.4323 | 35.925 | 33.106 | 24.3576 | 19.7881 | 14.9102 | 10.4039 | -3.8277 | -12.2319 | -16.6571
|  | SWINDON BSP | EE |  |  |  |  | 39.2068 | 39.0609 | 38.1272 | 36.613 | 34.4446 | 30.3691 | 25.4119 | 20.2844 | 15.516 | -3.8258 | -17.2024 | -24.6687 | 52.6326 | 52.0795 | 50.9561 | 49.5989 | 47.351 | 44.1214 | 40.2765 | 36.0938 | 32.2652 | 15.8203 | 5.4428 | -3.2276 | 40.501 | 40.4122 | 39.3887 | 37.9938 | 35.702 | 31.7938 | 27.2387 | 22.4387 | 18.004 | 0.46932 | -10.5052 | -16.3368
|  | SWINDON BSP | HT |  |  |  |  | 39.2517 | 39.1425 | 38.2405 | 36.6711 | 34.0436 | 29.8078 | 24.5354 | 19.2038 | 14.3303 | -3.7411 | -16.1717 | -22.1779 | 51.0439 | 50.4808 | 49.3145 | 47.8892 | 45.1997 | 41.6745 | 37.3913 | 32.8597 | 28.7513 | 15.7323 | 8.7997 | 5.846 | 38.5029 | 38.4439 | 37.4323 | 35.925 | 33.106 | 28.8808 | 23.8766 | 18.7018 | 13.9955 | 9.7629 | 6.2481 | 3.5345
|  | SWINDON BSP | HE |  |  |  |  | 39.2466 | 39.1446 | 38.2446 | 36.6793 | 34.4507 | 26.4997 | 21.7385 | 16.7538 | 12.1385 | -3.2177 | -13.3309 | -18.8922 | 51.046 | 50.485 | 49.3218 | 47.9502 | 45.6039 | 37.0218 | 33.0787 | 28.7176 | 24.7166 | 10.3081 | 0.87551 | -7.6098 | 38.5081 | 38.4545 | 37.446 | 35.9702 | 33.5239 | 24.3576 | 19.7881 | 14.9102 | 10.4039 | -3.8277 | -12.2319 | -16.6571
|  | SWINDON BSP | FB |  |  |  |  | 40.0711 | 40.4762 | 40.215 | 39.5732 | 38.7456 | 37.2446 | 35.4783 | 33.6783 | 31.816 | 20.3323 | 8.4752 | -1.2085 | 51.4776 | 51.2334 | 50.5113 | 49.5313 | 48.3366 | 46.2587 | 43.9618 | 41.5745 | 38.9966 | 22.9166 | 3.7692 | -18.5371 | 39.266 | 39.6123 | 39.525 | 39.1534 | 38.4787 | 37.0239 | 35.1839 | 33.245 | 31.1302 | 18.7787 | 6.806 | -2.5761
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM BSP | MINIMUM HEADROOM | SU 52824 66435 | NO | NO | 54.972 | -83.4429 | 31.0734 | 30.2591 | 28.1489 | 25.3407 | 21.1907 | 14.4295 | 6.8499 | -5.1195 | -27.6399 | -50.0419 | -61.4001 | -49.6504 | 59.158 | 57.4759 | 55.1233 | 52.0422 | 48.0591 | 41.6685 | 33.7791 | 20.3517 | -4.2788 | -22.8904 | -42.3873 | -76.1483 | 34.4654 | 32.5233 | 29.9896 | 26.6359 | 21.9496 | 14.9749 | 6.918 | -6.9883 | -29.6883 | -46.8346 | -61.2988
|  | THATCHAM BSP | EE |  |  |  |  | -83.4429 | 31.3887 | 30.3173 | 28.4826 | 25.9693 | 22.0469 | 17.0785 | 10.1683 | 3.0989 | -21.8419 | -45.1889 | -54.5062 | -46.5848 | 62.606 | 60.7836 | 58.8275 | 56.254 | 52.6316 | 47.5091 | 41.3111 | 34.7387 | 9.456 | -14.6001 | -26.797 | -72.245 | 38.6887 | 36.6856 | 34.6581 | 31.9458 | 27.6877 | 22.0652 | 15.3897 | 8.3611 | -16.1521 | -39.2991 | -47.5042
|  | THATCHAM BSP | HT |  |  |  |  | -83.4399 | 31.0734 | 30.2591 | 28.1489 | 25.3407 | 21.1907 | 14.4295 | 6.8499 | -2.195 | -27.6399 | -50.0419 | -61.4001 | -49.6504 | 59.158 | 57.4759 | 55.1233 | 52.0422 | 48.0591 | 41.6685 | 34.5412 | 25.397 | 1.0496 | -18.9146 | -28.2125 | -76.1483 | 34.4654 | 32.5233 | 29.9896 | 26.6359 | 21.9496 | 14.9749 | 7.3096 | -2.3567 | -10.602 | -14.7378 | -19.1399
|  | THATCHAM BSP | HE |  |  |  |  | -83.4011 | 31.4489 | 30.3714 | 28.3969 | 25.8254 | 21.8683 | 16.355 | 7.1091 | -5.1195 | -26.4184 | -43.9144 | -57.2929 | -49.6251 | 59.5338 | 57.6591 | 55.6254 | 53.0875 | 49.3085 | 43.1959 | 33.7791 | 20.3517 | -4.2788 | -22.8904 | -42.3873 | -76.1146 | 34.8075 | 32.7738 | 30.6464 | 27.8896 | 23.4496 | 16.817 | 6.918 | -6.9883 | -29.6883 | -46.8346 | -61.2988
|  | THATCHAM BSP | FB |  |  |  |  | -82.0521 | 33.3918 | 33.6693 | 33.2377 | 32.7091 | 31.5662 | 30.0224 | 28.3765 | 25.955 | 13.8377 | -6.2827 | -19.646 | -48.8304 | 60.697 | 60.2812 | 59.5306 | 58.4527 | 56.0191 | 53.0159 | 50.1412 | 46.0001 | 23.7359 | -7.1273 | -37.8273 | -74.7809 | 37.3685 | 37.6433 | 37.4675 | 36.8696 | 35.0927 | 32.957 | 31.0054 | 27.7127 | 11.0022 | -10.6178 | -24.9736
MINETY GSP | TOOTHILL BSP | TOOTHILL BSP | MINIMUM HEADROOM | SU 13191 83945 | NO | NO | 40.257 | 154.6955 | 152.8149 | 151.1547 | 148.6761 | 145.8812 | 141.8067 | 136.9231 | 131.7506 | 126.7812 | 110.8618 | 101.6608 | 97.272 | 153.7717 | 151.8549 | 151.0096 | 149.6317 | 147.7107 | 145.2001 | 142.0528 | 138.4043 | 135.0864 | 124.8159 | 117.4914 | 109.1454 | 152.5917 | 150.5128 | 149.2275 | 147.1917 | 144.7233 | 141.3075 | 137.1033 | 132.4307 | 128.1128 | 116.0414 | 108.1537 | 104.7986
|  | TOOTHILL BSP | EE |  |  |  |  | 154.6955 | 152.8149 | 151.1547 | 148.6761 | 146.168 | 142.3557 | 137.0639 | 131.8792 | 126.7812 | 110.8618 | 101.6608 | 97.272 | 154.9823 | 153.118 | 152.2945 | 150.9578 | 149.568 | 147.4965 | 144.0251 | 140.5863 | 137.1986 | 124.8159 | 117.4914 | 112.5925 | 153.9261 | 151.8874 | 150.6149 | 148.6782 | 146.6761 | 143.6516 | 139.0506 | 134.5741 | 130.1823 | 116.0414 | 108.1537 | 104.7986
|  | TOOTHILL BSP | HT |  |  |  |  | 154.7404 | 152.8904 | 151.2955 | 148.8629 | 145.8812 | 141.8067 | 136.9231 | 131.7506 | 126.8843 | 112.9078 | 104.2588 | 100.569 | 153.7917 | 151.858 | 151.0096 | 149.6317 | 147.7107 | 145.2001 | 142.0528 | 138.4043 | 135.0864 | 126.1054 | 121.0559 | 119.5654 | 152.6212 | 150.5285 | 149.2601 | 147.2707 | 144.7233 | 141.3075 | 137.1033 | 132.4307 | 128.1128 | 124.5475 | 122.3054 | 120.0222
|  | TOOTHILL BSP | HE |  |  |  |  | 154.7149 | 152.8731 | 151.221 | 148.7098 | 146.2292 | 142.3557 | 137.5802 | 132.7302 | 127.9027 | 115.6455 | 109.7312 | 106.4833 | 153.7717 | 151.8549 | 151.0128 | 149.6317 | 148.2454 | 146.0338 | 143.1054 | 139.9791 | 136.8464 | 127.1728 | 122.0654 | 117.2296 | 152.5917 | 150.5128 | 149.2275 | 147.1917 | 145.1538 | 141.9643 | 137.9001 | 133.718 | 129.5591 | 118.8538 | 114.1159 | 111.6064
|  | TOOTHILL BSP | FB |  |  |  |  | 155.5935 | 154.1506 | 152.8323 | 151.3925 | 149.7537 | 148.0741 | 145.6659 | 143.1874 | 140.3588 | 129.8935 | 123.3394 | 118.4884 | 154.2401 | 152.338 | 151.4243 | 150.5896 | 149.4885 | 148.3096 | 146.5191 | 144.6201 | 142.4359 | 131.5064 | 121.3117 | 109.1454 | 153.5001 | 151.818 | 150.7401 | 149.6991 | 148.4528 | 147.2233 | 145.3254 | 143.2707 | 140.7854 | 130.9812 | 124.6054 | 119.6685
IVER 132KV GSP | UPTON BSP | UPTON BSP | MINIMUM HEADROOM | TQ 00838 79445 | NO | YES | 6.347 | 37.0943 | 37.0096 | 36.7198 | 36.3035 | 35.579 | 34.4004 | 32.9923 | 31.5219 | 29.9402 | 23.9015 | 19.4943 | 17.4504 | 44.8895 | 44.7284 | 44.3326 | 43.88 | 43.1968 | 42.2074 | 40.9642 | 39.5884 | 38.1337 | 32.8251 | 28.2642 | 19.18 | 39.0364 | 38.9838 | 38.6733 | 38.2501 | 37.5575 | 36.4059 | 35.0596 | 33.6069 | 32.0438 | 27.3249 | 23.3729 | 21.6974
|  | UPTON BSP | EE |  |  |  |  | 37.0943 | 37.0096 | 36.7198 | 36.3311 | 35.7729 | 34.678 | 33.1025 | 31.576 | 30.0586 | 23.9015 | 19.4943 | 17.4504 | 45.7608 | 45.6067 | 45.2251 | 44.8057 | 44.2435 | 43.3496 | 41.9424 | 40.5067 | 39.1282 | 32.8251 | 28.4976 | 24.8098 | 40.1045 | 40.0382 | 39.7249 | 39.3688 | 38.8729 | 37.8209 | 36.3015 | 34.8025 | 33.326 | 27.3249 | 23.3729 | 21.6974
|  | UPTON BSP | HT |  |  |  |  | 37.1219 | 37.0515 | 36.7637 | 36.3035 | 35.579 | 34.4004 | 32.9923 | 31.5219 | 29.9402 | 24.2811 | 20.6402 | 19.577 | 44.8895 | 44.7284 | 44.3326 | 43.88 | 43.1968 | 42.2074 | 40.9642 | 39.5884 | 38.1337 | 33.2958 | 30.8842 | 30.1137 | 39.0364 | 38.9838 | 38.6733 | 38.2501 | 37.5575 | 36.4059 | 35.0596 | 33.6069 | 32.0438 | 30.7396 | 29.6048 | 28.5438
|  | UPTON BSP | HE |  |  |  |  | 37.1249 | 37.0576 | 36.7953 | 36.3556 | 35.7382 | 34.7045 | 33.2841 | 31.8984 | 30.4984 | 26.2607 | 23.2127 | 21.83 | 44.8937 | 44.7368 | 44.3505 | 43.9147 | 43.3284 | 42.4516 | 41.2095 | 39.8979 | 38.6137 | 33.4863 | 29.6137 | 25.8905 | 39.0427 | 38.9922 | 38.6954 | 38.2869 | 37.728 | 36.7185 | 35.3427 | 34.0038 | 32.6322 | 28.4469 | 25.7048 | 24.5154
|  | UPTON BSP | FB |  |  |  |  | 37.629 | 37.6321 | 37.7045 | 37.6351 | 37.4392 | 37.1362 | 36.8545 | 36.6433 | 36.2249 | 33.5994 | 29.3647 | 26.5249 | 45.1463 | 44.9232 | 44.7242 | 44.46 | 44.0137 | 43.3147 | 42.6358 | 42.0042 | 41.1737 | 36.0632 | 28.2642 | 19.18 | 39.5217 | 39.5312 | 39.5806 | 39.548 | 39.3985 | 39.1048 | 38.8248 | 38.6038 | 38.1375 | 35.2343 | 30.9659 | 28.1354
NURSLING GSP | VELMORE BSP | VELMORE BSP | MINIMUM HEADROOM | SU 42855 19215 | NO | NO | 51.14 | 2.0117 | 115.6668 | 114.5719 | 112.9821 | 110.2811 | 105.7209 | 100.3045 | 94.6668 | 89.1331 | 68.4484 | 54.8607 | 49.477 | 18.4655 | 127.6044 | 126.776 | 125.6065 | 123.1486 | 120.2865 | 116.6728 | 112.7065 | 109.056 | 96.5371 | 82.2539 | 59.4623 | 4.5076 | 115.6402 | 114.7076 | 113.1023 | 110.0297 | 105.9318 | 101.0634 | 96.0286 | 91.3476 | 78.7086 | 69.5854 | 65.2599
|  | VELMORE BSP | EE |  |  |  |  | 2.0117 | 115.7362 | 114.5719 | 113.0219 | 110.6015 | 105.7811 | 100.3045 | 95.1525 | 90.1015 | 71.2453 | 57.8831 | 51.327 | 20.4344 | 129.7813 | 128.8395 | 127.8272 | 125.768 | 123.065 | 119.6803 | 116.1323 | 112.8782 | 98.4221 | 88.515 | 80.4558 | 6.9344 | 118.217 | 117.1262 | 115.7201 | 113.1691 | 109.065 | 104.3211 | 99.8405 | 95.6844 | 79.815 | 69.5854 | 65.2599
|  | VELMORE BSP | HT |  |  |  |  | 2.0372 | 115.6668 | 114.726 | 112.9862 | 110.2811 | 105.7209 | 100.328 | 94.6668 | 89.1331 | 68.4484 | 54.8607 | 49.477 | 18.4655 | 127.6044 | 126.776 | 125.6065 | 123.1486 | 120.2865 | 116.6728 | 112.7065 | 109.056 | 96.7455 | 90.616 | 89.0928 | 4.5076 | 115.6402 | 114.7423 | 113.1023 | 110.0297 | 105.9318 | 101.0634 | 96.0286 | 91.3476 | 86.4097 | 83.2086 | 79.9623
|  | VELMORE BSP | HE |  |  |  |  | 2.0464 | 115.7984 | 114.6637 | 112.9821 | 110.4168 | 105.7362 | 100.3902 | 95.279 | 90.2556 | 74.3209 | 63.676 | 58.4556 | 18.4655 | 127.776 | 126.8013 | 125.7349 | 123.5834 | 120.8097 | 117.3139 | 113.7318 | 110.3286 | 96.5371 | 87.3602 | 78.6739 | 4.516 | 115.8034 | 114.7076 | 113.1423 | 110.3918 | 106.2571 | 101.4528 | 96.9023 | 92.6234 | 78.7086 | 70.6055 | 66.8907
|  | VELMORE BSP | FB |  |  |  |  | 3.0392 | 117.3178 | 117.2158 | 116.7872 | 116.0994 | 114.7127 | 113.2668 | 111.7872 | 110.3841 | 100.6402 | 88.13 | 80.5698 | 18.8928 | 128.2349 | 127.7413 | 126.9613 | 125.8476 | 124.0528 | 122.1339 | 120.0286 | 117.7781 | 102.6465 | 82.2539 | 59.4623 | 5.5213 | 117.2571 | 117.2907 | 117.0349 | 116.4834 | 115.156 | 113.7918 | 112.1476 | 110.5528 | 99.5634 | 87.5034 | 80.3076
MANNINGTON GSP | WAREHAM BSP | WAREHAM BSP | MINIMUM HEADROOM | SY 91548 88451 | NO | NO | 2.913 | -2.3276 | 11.6699 | 11.0974 | 10.1505 | 8.7556 | 6.5985 | 4.1658 | 1.676 | -0.87806 | -9.6974 | -16.1872 | -20.1005 | 0.58105 | 13.8363 | 13.6237 | 13.2437 | 12.6879 | 11.9668 | 10.4995 | 8.9479 | 7.2742 | 1.8416 | -0.77737 | -4.69 | -0.94632 | 12.7316 | 12.4432 | 11.8747 | 11.0768 | 9.4442 | 7.3842 | 5.2705 | 3.1042 | -1.3959 | -5.848 | -8.3184
|  | WAREHAM BSP | EE |  |  |  |  | -2.2929 | 11.7658 | 11.326 | 10.5821 | 9.5403 | 7.6179 | 5.3219 | 2.8781 | 0.54745 | -7.6107 | -13.6291 | -17.2383 | 1.3969 | 14.6827 | 14.5194 | 14.2265 | 13.8041 | 13.2378 | 12.1337 | 10.6327 | 9.1827 | 3.2816 | -0.17245 | -2.6347 | -0.056122 | 13.6653 | 13.4622 | 13.0286 | 12.4286 | 11.2582 | 9.3898 | 7.3806 | 5.4673 | -1.3959 | -5.848 | -8.3184
|  | WAREHAM BSP | HT |  |  |  |  | -2.3276 | 11.6699 | 11.0974 | 10.1505 | 8.7556 | 6.5985 | 4.1658 | 1.676 | -0.87806 | -9.6974 | -16.1872 | -20.1005 | 0.58105 | 13.8363 | 13.6237 | 13.2437 | 12.6879 | 11.9668 | 10.4995 | 8.9479 | 7.2742 | 1.8416 | -0.77737 | -1.8016 | -0.94632 | 12.7316 | 12.4432 | 11.8747 | 11.0768 | 9.4442 | 7.3842 | 5.2705 | 3.1042 | 1.1747 | -0.081053 | -1.4421
|  | WAREHAM BSP | HE |  |  |  |  | -2.3041 | 11.7474 | 11.325 | 10.5505 | 9.4597 | 7.474 | 5.1342 | 2.7128 | 0.27602 | -5.7821 | -10.8964 | -13.6393 | 0.59263 | 13.8721 | 13.7132 | 13.41 | 12.9679 | 12.3647 | 11.1963 | 9.7258 | 8.17 | 3.5405 | 0.56158 | -1.8247 | -0.93368 | 12.7821 | 12.5811 | 12.12 | 11.4811 | 10.1968 | 8.2684 | 6.2411 | 4.1842 | -0.97474 | -4.7537 | -6.7211
|  | WAREHAM BSP | FB |  |  |  |  | -1.9653 | 12.3311 | 12.3974 | 12.2872 | 12.0189 | 11.6689 | 11.123 | 10.6281 | 10.0158 | 6.1872 | 1.2566 | -2.4179 | 0.82105 | 14.2026 | 14.19 | 14.1174 | 13.9774 | 13.8142 | 13.5489 | 13.1816 | 12.4647 | 8.0132 | 1.9058 | -4.69 | -0.66526 | 13.1926 | 13.18 | 13.1105 | 12.94 | 12.7274 | 12.4337 | 12.1126 | 11.76 | 8.3979 | 3.7442 | 0.14632
MELKSHAM GSP | WEST GRAFTON BSP | WEST GRAFTON BSP | MINIMUM HEADROOM | SU 24302 59215 | NO | NO | 7.68 | 25.1841 | 25.0637 | 24.6953 | 23.9392 | 23.082 | 21.7902 | 20.1137 | 18.0453 | 16.2606 | 9.4688 | 5.5525 | 4.1004 | 33.4301 | 33.1469 | 32.6311 | 31.929 | 31.0174 | 29.8648 | 28.3553 | 26.4101 | 24.8911 | 19.1248 | 16.5553 | 9.2669 | 27.648 | 27.5185 | 27.1974 | 26.509 | 25.5932 | 24.3385 | 22.6995 | 20.6637 | 19.0027 | 14.1448 | 11.205 | 9.9672
|  | WEST GRAFTON BSP | EE |  |  |  |  | 25.1861 | 25.0667 | 24.7249 | 24.0382 | 23.3484 | 22.1494 | 20.4994 | 18.679 | 17.0851 | 10.3392 | 6.2912 | 4.5616 | 34.0254 | 33.7519 | 33.2693 | 32.6315 | 31.8968 | 30.8203 | 29.3132 | 27.6917 | 26.357 | 20.2846 | 16.6611 | 14.2968 | 28.4479 | 28.3254 | 28.0315 | 27.4244 | 26.7019 | 25.553 | 23.9448 | 22.2091 | 20.757 | 14.6009 | 11.205 | 9.9672
|  | WEST GRAFTON BSP | HT |  |  |  |  | 25.1841 | 25.0667 | 24.6953 | 23.9392 | 23.082 | 21.7902 | 20.1137 | 18.0453 | 16.2606 | 9.4688 | 5.5525 | 4.1004 | 33.4301 | 33.1511 | 32.6311 | 31.929 | 31.0174 | 29.8648 | 28.3553 | 26.4101 | 24.8911 | 19.1248 | 16.5553 | 16.1164 | 27.648 | 27.5206 | 27.1974 | 26.509 | 25.5932 | 24.3385 | 22.6995 | 20.6637 | 19.0027 | 17.2459 | 16.0627 | 14.7743
|  | WEST GRAFTON BSP | HE |  |  |  |  | 25.1974 | 25.0637 | 24.7239 | 24.0606 | 23.3116 | 22.2045 | 20.5402 | 18.7841 | 16.9892 | 11.1045 | 7.63 | 6.33 | 33.4427 | 33.1469 | 32.6522 | 32.0385 | 31.2374 | 30.2659 | 28.7101 | 27.1511 | 25.5459 | 19.869 | 16.7353 | 14.4353 | 27.6616 | 27.5185 | 27.2164 | 26.6311 | 25.8322 | 24.7732 | 23.109 | 21.4143 | 19.6901 | 14.1448 | 11.3101 | 10.3574
|  | WEST GRAFTON BSP | FB |  |  |  |  | 25.8759 | 25.8147 | 25.6616 | 25.4576 | 25.4453 | 25.1096 | 24.4035 | 23.8035 | 22.9922 | 18.4555 | 13.7127 | 11.0065 | 34.0259 | 33.6701 | 33.3406 | 32.9943 | 32.7501 | 32.1437 | 31.1764 | 30.4111 | 29.4416 | 23.8322 | 16.6332 | 9.2669 | 28.3532 | 28.2753 | 28.149 | 28.0122 | 28.0532 | 27.6764 | 26.8985 | 26.3164 | 25.5037 | 21.0753 | 16.2985 | 13.3911
NURSLING GSP | WINCHESTER BSP | WINCHESTER BSP | MINIMUM HEADROOM | SU 44965 26671 | NO | NO | 15.502 | 35.9027 | 35.4619 | 34.6548 | 33.5354 | 146.2464 | 143.0698 | 136.4188 | 125.776 | 104.8402 | 81.8402 | 56.4311 | 29.8678 | 46.2682 | 45.4545 | 43.9345 | 42.8345 | 150.6714 | 148.4429 | 142.2408 | 130.2661 | 105.2608 | 80.6798 | 53.4314 | 20.744 | 31.6766 | 31.0756 | 29.7987 | 28.6019 | 138.2029 | 135.3893 | 128.5303 | 116.1082 | 90.5819 | 65.3787 | 37.1398 | 5.3924
|  | WINCHESTER BSP | EE |  |  |  |  | 35.9027 | 35.5354 | 34.6548 | 33.6609 | 146.6556 | 143.8392 | 139.0964 | 133.6076 | 126.2045 | 104.2372 | 68.5341 | 54.9627 | 48.106 | 47.4081 | 45.8846 | 44.9499 | 153.2009 | 151.2336 | 147.4795 | 142.5326 | 135.2346 | 115.104 | 77.3703 | 63.1805 | 33.9856 | 33.4764 | 32.1407 | 31.1928 | 141.2254 | 138.6601 | 134.3887 | 128.9509 | 121.1346 | 99.4132 | 60.0387 | 46.0673
|  | WINCHESTER BSP | HT |  |  |  |  | 35.9231 | 35.4619 | 34.6742 | 33.5354 | 146.2464 | 143.0698 | 136.4188 | 129.5566 | 117.2015 | 92.2943 | 58.4066 | 36.9413 | 46.2682 | 45.4545 | 43.9345 | 42.8345 | 150.6714 | 148.4429 | 142.2408 | 135.7429 | 122.1261 | 99.5335 | 64.8787 | 42.5524 | 31.6766 | 31.0756 | 29.7987 | 28.6019 | 138.2029 | 135.3893 | 128.5303 | 121.4093 | 107.1829 | 100.5577 | 96.9135 | 92.2524
|  | WINCHESTER BSP | HE |  |  |  |  | 35.9119 | 35.5578 | 34.6936 | 33.5752 | 146.4617 | 143.6382 | 137.2902 | 125.776 | 104.8402 | 81.8402 | 56.4311 | 29.8678 | 46.2724 | 45.5503 | 43.9945 | 42.9924 | 151.2314 | 149.0945 | 143.084 | 130.2661 | 105.2608 | 80.6798 | 53.4314 | 20.744 | 31.6766 | 31.1703 | 29.8261 | 28.7387 | 138.6714 | 135.9608 | 129.4472 | 116.1082 | 90.5819 | 65.3787 | 37.1398 | 5.3924
|  | WINCHESTER BSP | FB |  |  |  |  | 36.4772 | 36.4303 | 36.1803 | 35.8415 | 149.7709 | 149.2209 | 147.8964 | 146.3504 | 143.18 | 130.0076 | 111.3096 | 95.7566 | 46.864 | 46.6293 | 45.9124 | 45.6051 | 154.8324 | 153.8019 | 151.2103 | 148.8082 | 144.1766 | 126.7145 | 102.9208 | 79.4945 | 32.5703 | 32.6629 | 32.2735 | 32.0356 | 143.2629 | 142.6829 | 140.6472 | 138.5987 | 134.3451 | 118.7714 | 97.7977 | 80.0051
COWLEY GSP | WITNEY BSP | WITNEY BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | NO | 34.335 | 24.0516 | 23.4159 | 136.4789 | 134.1861 | 131.6524 | 127.3269 | 122.7922 | 117.88 | 113.2453 | 96.6198 | 84.8636 | 77.8106 | 43.6476 | 43.055 | 151.4002 | 149.716 | 147.8265 | 145.0539 | 141.8781 | 138.3729 | 135.1571 | 123.9423 | 118.5139 | 101.7097 | 29.7592 | 29.2202 | 139.1497 | 136.9529 | 134.4329 | 130.6076 | 126.5434 | 122.1234 | 118.0044 | 108.475 | 100.6305 | 96.3896
|  | WITNEY BSP | EE |  |  |  |  | 24.0516 | 23.4159 | 136.5881 | 134.7187 | 132.4657 | 128.2596 | 123.6238 | 118.6024 | 114.1014 | 98.9045 | 87.9187 | 81.4851 | 45.4233 | 44.908 | 153.5621 | 152.2468 | 150.756 | 148.3907 | 145.4162 | 141.9968 | 139.1274 | 126.91 | 119.2315 | 113.3366 | 31.8937 | 31.358 | 141.5682 | 139.7641 | 137.7396 | 134.3039 | 130.2988 | 125.9162 | 122.1172 | 108.9366 | 100.6305 | 96.3896
|  | WITNEY BSP | HT |  |  |  |  | 24.1333 | 23.6363 | 136.4789 | 134.1861 | 131.6524 | 127.3269 | 122.7922 | 117.88 | 113.2453 | 96.6198 | 84.8636 | 77.8106 | 43.6476 | 43.055 | 151.4002 | 149.716 | 147.8265 | 145.0539 | 141.8781 | 138.3729 | 135.1571 | 123.9423 | 118.5234 | 116.5339 | 29.7687 | 29.2318 | 139.1497 | 136.9529 | 134.4329 | 130.6076 | 126.5434 | 122.1234 | 118.0044 | 113.3434 | 111.0234 | 108.5192
|  | WITNEY BSP | HE |  |  |  |  | 24.071 | 23.4445 | 136.6136 | 134.5779 | 132.2371 | 127.9687 | 123.2994 | 118.334 | 113.783 | 102.033 | 92.4351 | 87.0687 | 43.756 | 43.2276 | 151.8329 | 150.4602 | 148.9308 | 146.4729 | 143.3823 | 139.9792 | 137.0402 | 126.1297 | 118.8918 | 112.5665 | 29.7592 | 29.2202 | 139.375 | 137.4339 | 135.2623 | 131.6876 | 127.5634 | 123.1423 | 119.2044 | 108.475 | 101.1897 | 97.3634
|  | WITNEY BSP | FB |  |  |  |  | 25.4516 | 25.4506 | 139.7494 | 139.4698 | 138.8585 | 137.5249 | 136.4126 | 135.1902 | 134.0494 | 126.5647 | 116.3545 | 109.0177 | 44.5971 | 44.1023 | 153.555 | 153.1444 | 152.3697 | 150.7076 | 149.0139 | 147.2308 | 145.5518 | 134.0918 | 118.5139 | 101.7097 | 31.1971 | 31.0476 | 142.6234 | 142.4592 | 141.9876 | 140.5939 | 139.2729 | 137.8371 | 136.5181 | 127.9876 | 117.8444 | 110.7655
FLEET-BRAMLEY GSP | WOKINGHAM BSP | WOKINGHAM BSP | MINIMUM HEADROOM | SU 79589 67665 | NO | NO | 12.124 | 80.4762 | 80.3711 | 79.868 | 78.8721 | 77.565 | 75.1456 | 72.5007 | 69.5884 | 66.6384 | 57.319 | 51.4619 | 48.7384 | 80.2634 | 79.8866 | 79.4445 | 78.6687 | 77.5813 | 76.1718 | 74.4718 | 72.4634 | 70.3971 | 63.904 | 59.154 | 51.8855 | 79.0824 | 78.8813 | 78.4918 | 77.6466 | 76.4192 | 74.4108 | 72.1887 | 69.6445 | 67.0529 | 60.3081 | 55.4377 | 53.0377
|  | WOKINGHAM BSP | EE |  |  |  |  | 80.4762 | 80.4027 | 80.0078 | 79.2701 | 78.2323 | 76.0762 | 73.1711 | 70.117 | 67.1333 | 58.1782 | 52.415 | 49.1588 | 81.0581 | 80.7132 | 80.3377 | 79.6805 | 78.704 | 77.5826 | 75.6468 | 73.5887 | 71.5468 | 63.904 | 59.154 | 55.6407 | 79.9601 | 79.7887 | 79.4764 | 78.8468 | 77.8479 | 76.1723 | 73.6958 | 71.0928 | 68.5264 | 60.3081 | 55.4377 | 53.0377
|  | WOKINGHAM BSP | HT |  |  |  |  | 80.4854 | 80.3711 | 79.868 | 78.8721 | 77.565 | 75.1456 | 72.5007 | 69.5884 | 66.6384 | 57.319 | 51.4619 | 48.7384 | 80.2634 | 79.8866 | 79.4445 | 78.6687 | 77.5813 | 76.1718 | 74.4718 | 72.4634 | 70.3971 | 64.0034 | 60.8918 | 59.9076 | 79.0845 | 78.8813 | 78.4918 | 77.6466 | 76.4192 | 74.4108 | 72.1887 | 69.6445 | 67.0529 | 64.6813 | 63.0982 | 61.4887
|  | WOKINGHAM BSP | HE |  |  |  |  | 80.4843 | 80.4109 | 80.0354 | 79.2129 | 78.0925 | 76.0374 | 73.5843 | 70.9088 | 68.2823 | 61.4078 | 57.3139 | 54.965 | 80.2634 | 79.8982 | 79.5139 | 78.8266 | 77.7982 | 76.6266 | 75.0687 | 73.2887 | 71.5024 | 65.4213 | 61.8203 | 58.4024 | 79.0824 | 78.9055 | 78.6003 | 77.8908 | 76.7918 | 75.1182 | 73.0655 | 70.7845 | 68.5213 | 62.2792 | 59.0297 | 57.2603
|  | WOKINGHAM BSP | FB |  |  |  |  | 81.1548 | 81.4119 | 81.2721 | 81.166 | 80.8997 | 80.315 | 79.6272 | 78.7772 | 78.0262 | 73.6997 | 68.8323 | 65.116 | 80.6929 | 80.6066 | 80.1645 | 79.8192 | 79.2918 | 78.4939 | 77.6066 | 76.5866 | 75.6687 | 69.4497 | 61.3382 | 51.8855 | 79.7603 | 79.9424 | 79.7361 | 79.6813 | 79.4413 | 78.9255 | 78.2876 | 77.4697 | 76.7382 | 72.2929 | 67.5161 | 63.8803
FAWLEY GSP | WOOTTON COMMON BSP | WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ52785 90310 | NO | NO | 20.412 | 30.3079 | 30.5855 | 29.9038 | 27.8498 | 24.8232 | 19.5304 | 13.4824 | 7.1038 | 1.2008 | -23.7696 | -43.4717 | -54.5931 | 45.9711 | 45.8068 | 45.0026 | 43.4753 | 40.8795 | 37.8437 | 34.0068 | 29.6521 | 26.0868 | 12.6153 | 1.53 | -20.4626 | 33.3005 | 33.5416 | 32.7668 | 30.7911 | 27.6963 | 23.25 | 17.9437 | 12.1858 | 7.2353 | -5.8721 | -19.1633 | -26.2112
|  | WOOTTON COMMON BSP | EE |  |  |  |  | 30.313 | 30.6181 | 30.1273 | 28.4855 | 26.1783 | 21.16 | 15.5447 | 9.6702 | 4.061 | -18.9013 | -37.4023 | -47.986 | 47.6827 | 47.5663 | 46.9082 | 45.6653 | 43.6459 | 40.9571 | 37.6327 | 33.9143 | 30.6031 | 14.8367 | 3.3602 | -5.6653 | 35.4378 | 35.6949 | 35.098 | 33.4949 | 31.1041 | 27.0194 | 22.2673 | 17.1806 | 12.5327 | -5.6347 | -19.1633 | -26.2112
|  | WOOTTON COMMON BSP | HT |  |  |  |  | 30.313 | 30.5855 | 29.9038 | 27.8498 | 24.8232 | 19.5304 | 13.4824 | 7.1038 | 1.2008 | -23.7696 | -43.4717 | -54.5931 | 45.9784 | 45.8068 | 45.0026 | 43.4753 | 40.8795 | 37.8437 | 34.0068 | 29.6521 | 26.0868 | 12.6153 | 4.7689 | 2.0226 | 33.3068 | 33.5416 | 32.7668 | 30.7911 | 27.6963 | 23.25 | 17.9437 | 12.1858 | 7.2353 | 1.9974 | -1.6742 | -5.4311
|  | WOOTTON COMMON BSP | HE |  |  |  |  | 30.3079 | 30.6416 | 30.1722 | 28.3579 | 25.8671 | 20.8753 | 15.1906 | 9.3732 | 3.6457 | -15.0635 | -30.2676 | -38.3033 | 45.9711 | 45.8542 | 45.1753 | 43.8732 | 41.7521 | 39.0226 | 35.5111 | 31.8121 | 28.3184 | 13.9289 | 4.0132 | -5.0121 | 33.3005 | 33.5826 | 32.9816 | 31.2153 | 28.6226 | 24.4437 | 19.4689 | 14.3511 | 9.4689 | -5.8721 | -16.7679 | -22.2163
|  | WOOTTON COMMON BSP | FB |  |  |  |  | 31.5283 | 32.3702 | 32.7375 | 32.8324 | 32.6487 | 31.9079 | 30.7059 | 29.2844 | 27.6702 | 17.861 | 4.0089 | -5.0207 | 46.7521 | 46.7553 | 46.3932 | 45.8763 | 45.0742 | 43.5763 | 41.6247 | 39.3921 | 36.8216 | 21.9774 | 1.53 | -20.4626 | 34.45 | 35.0995 | 35.4258 | 35.5595 | 35.4111 | 34.5174 | 33.1626 | 31.5679 | 29.6774 | 18.9868 | 5.8868 | -2.4132
LOVEDEAN GSP | WYMERING BSP | WYMERING BSP | MINIMUM HEADROOM | SU 64948 05441 | NO | YES | 79.287 | 24.4473 | 24.3371 | 24.1769 | 23.8361 | 23.382 | 22.8371 | 22.131 | 21.5146 | 20.8983 | 16.1289 | 12.334 | 10.4524 | 20.0111 | 19.97 | 19.8321 | 19.609 | 19.3343 | 18.9227 | 18.4048 | 17.8732 | 17.1448 | 13.3027 | 10.71 | 5.6564 | 20.2111 | 20.23 | 20.1521 | 19.9343 | 19.6416 | 19.169 | 18.5911 | 18.0058 | 17.4343 | 14.11 | 10.5595 | 9.1769
|  | WYMERING BSP | EE |  |  |  |  | 24.4473 | 24.3371 | 24.1769 | 23.8361 | 23.382 | 22.8371 | 22.131 | 21.5146 | 20.8983 | 16.1289 | 12.334 | 10.4524 | 21.1738 | 21.1412 | 21.0208 | 20.8371 | 20.5687 | 20.2208 | 19.7299 | 19.2422 | 18.6269 | 14.2687 | 11.2575 | 9.3095 | 21.4136 | 21.4228 | 21.3544 | 21.1626 | 20.8881 | 20.4554 | 19.8901 | 19.333 | 18.7881 | 14.1289 | 10.5595 | 9.1769
|  | WYMERING BSP | HT |  |  |  |  | 24.4677 | 24.381 | 24.2463 | 23.9116 | 23.5003 | 22.9595 | 22.333 | 21.7626 | 21.1861 | 16.5034 | 13.2748 | 11.8983 | 20.0143 | 19.97 | 19.8321 | 19.609 | 19.3343 | 18.9227 | 18.4048 | 17.8732 | 17.1448 | 13.3027 | 11.2479 | 10.8416 | 20.2164 | 20.2374 | 20.1521 | 19.9343 | 19.6416 | 19.169 | 18.5911 | 18.0058 | 17.4343 | 16.4637 | 15.0837 | 14.189
|  | WYMERING BSP | HE |  |  |  |  | 24.4616 | 24.3636 | 24.2187 | 23.8993 | 23.4656 | 22.9922 | 22.3473 | 21.8014 | 21.2442 | 17.6799 | 15.5136 | 14.0259 | 20.0111 | 19.9774 | 19.8532 | 19.6669 | 19.3974 | 19.0743 | 18.5911 | 18.1258 | 17.5195 | 13.5816 | 11.3869 | 9.3153 | 20.2111 | 20.23 | 20.169 | 19.9816 | 19.709 | 19.3248 | 18.7953 | 18.2816 | 17.7732 | 14.11 | 12.0985 | 10.8543
|  | WYMERING BSP | FB |  |  |  |  | 24.5963 | 24.6238 | 24.481 | 24.4524 | 24.2554 | 24.0901 | 23.9156 | 23.733 | 23.4952 | 22.1452 | 18.8136 | 16.7136 | 20.1153 | 20.1006 | 19.9648 | 19.9753 | 19.7174 | 19.4448 | 19.1553 | 18.8479 | 18.4964 | 16.0385 | 10.71 | 5.6564 | 20.4079 | 20.5037 | 20.4827 | 20.5932 | 20.4711 | 20.3553 | 20.2143 | 20.0532 | 19.8479 | 18.5006 | 14.9164 | 12.5848
COWLEY GSP | YARNTON BSP | YARNTON BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | NO | 141.954 | -31.5001 | 86.6295 | 84.4335 | 82.0499 | 77.9162 | 72.5019 | 66.6417 | 61.107 | 55.9692 | 39.0662 | 30.1937 | 25.9641 | -8.639 | 109.3747 | 108.2526 | 106.6526 | 103.64 | 100.0347 | 95.6915 | 91.6936 | 87.7979 | 75.1652 | 69.78 | 55.1926 | -23.1958 | 94.9273 | 92.9231 | 90.9536 | 87.2589 | 82.6421 | 77.2884 | 72.3368 | 67.6294 | 57.361 | 51.8421 | 49.4152
|  | YARNTON BSP | EE |  |  |  |  | -31.4185 | 88.0437 | 84.9019 | 82.8305 | 79.8141 | 75.3723 | 70.2029 | 64.7366 | 59.4468 | 42.4835 | 34.0886 | 30.3764 | -6.8889 | 112.8397 | 110.4978 | 109.2499 | 107.3988 | 104.5988 | 100.9111 | 97.1539 | 93.4437 | 79.2652 | 71.705 | 66.4784 | -20.9828 | 98.4682 | 95.5692 | 93.955 | 91.455 | 87.7611 | 83.2652 | 78.5825 | 73.9346 | 58.909 | 51.8652 | 49.4152
|  | YARNTON BSP | HT |  |  |  |  | -31.5001 | 86.6295 | 84.4335 | 82.0499 | 77.9162 | 72.5019 | 66.6417 | 61.107 | 55.9692 | 39.0662 | 30.1937 | 25.9641 | -8.639 | 109.3747 | 108.2526 | 106.6526 | 103.64 | 100.0347 | 95.6915 | 91.6936 | 87.7979 | 75.1652 | 69.78 | 68.3484 | -23.1958 | 94.9273 | 92.9231 | 90.9536 | 87.2589 | 82.6421 | 77.2884 | 72.3368 | 67.6294 | 63.2579 | 59.3842 | 56.7957
|  | YARNTON BSP | HE |  |  |  |  | -31.4114 | 88.057 | 84.9101 | 82.7478 | 79.6519 | 75.1611 | 69.9448 | 64.3927 | 59.2907 | 44.3172 | 37.3815 | 34.4386 | -8.5643 | 111.16 | 108.7379 | 107.4431 | 105.5147 | 102.6084 | 98.8221 | 94.8652 | 91.3 | 77.8084 | 71.2652 | 65.7926 | -23.0958 | 96.3484 | 93.3652 | 91.6294 | 88.9894 | 85.1484 | 80.5052 | 75.5726 | 71.0579 | 57.361 | 51.8421 | 49.7557
|  | YARNTON BSP | FB |  |  |  |  | -30.3705 | 89.6233 | 88.5631 | 86.3641 | 84.8315 | 82.9764 | 80.4692 | 78.2407 | 75.7284 | 64.3325 | 54.0529 | 49.209 | -8.0664 | 111.8126 | 111.2494 | 109.2073 | 107.9484 | 106.1431 | 103.7357 | 101.481 | 99.061 | 85.9336 | 70.2736 | 55.1926 | -22 | 97.9979 | 97.1157 | 95.1694 | 94.0284 | 92.4463 | 90.2347 | 88.221 | 85.9757 | 74.6979 | 64.5031 | 59.3979
AXMINSTER GSP | YEOVIL BSP | YEOVIL BSP | MINIMUM HEADROOM | ST 57586 16894 | NO | NO | 64.506 | 18.787 | 18.3748 | 17.3901 | 15.8207 | 13.0901 | 8.4574 | 80.9074 | 75.4727 | 70.8227 | 54.2217 | 41.9054 | 36.6217 | 34.1059 | 33.6838 | 32.8111 | 31.6059 | 29.7311 | 27.5364 | 98.0385 | 93.5901 | 89.789 | 76.0943 | 67.4185 | 46.8069 | 19.5553 | 19.108 | 18.089 | 16.6017 | 14.3943 | 11.4575 | 82.709 | 78.0206 | 73.9122 | 62.3964 | 52.7023 | 48.934
|  | YEOVIL BSP | EE |  |  |  |  | 18.8095 | 18.6717 | 17.7584 | 16.2972 | 13.8329 | 9.7472 | 82.7625 | 77.434 | 72.8248 | 55.3135 | 42.5686 | 36.8176 | 36.5207 | 36.2493 | 35.4319 | 34.2921 | 32.6482 | 30.736 | 101.734 | 97.3646 | 93.6748 | 78.2544 | 68.1676 | 61.4503 | 22.4748 | 22.2064 | 21.2646 | 19.9115 | 17.9686 | 15.4493 | 87.1401 | 82.8115 | 78.8493 | 63.2676 | 52.7023 | 48.934
|  | YEOVIL BSP | HT |  |  |  |  | 18.787 | 18.3748 | 17.3901 | 15.8207 | 13.0901 | 8.4574 | 80.9074 | 75.4727 | 70.8227 | 54.2217 | 41.9054 | 36.6217 | 34.1059 | 33.6838 | 32.8111 | 31.6059 | 29.7311 | 27.5364 | 98.0385 | 93.5901 | 89.789 | 76.0943 | 68.7617 | 67.9975 | 19.5553 | 19.108 | 18.089 | 16.6017 | 14.3943 | 11.4575 | 82.709 | 78.0206 | 73.9122 | 69.3869 | 66.6164 | 63.9396
|  | YEOVIL BSP | HE |  |  |  |  | 18.8186 | 18.6931 | 17.9003 | 16.4299 | 13.8758 | 9.7186 | 82.5921 | 77.3625 | 72.7584 | 58.7329 | 48.8513 | 43.8819 | 34.1248 | 33.8427 | 33.0396 | 31.8711 | 30.1648 | 28.1796 | 99.0722 | 94.6532 | 90.8385 | 77.0543 | 68.6248 | 61.1764 | 19.5859 | 19.328 | 18.4522 | 17.0269 | 14.9743 | 12.3027 | 83.8332 | 79.4596 | 75.3732 | 62.3964 | 54.5164 | 50.9596
|  | YEOVIL BSP | FB |  |  |  |  | 19.6635 | 19.9809 | 20.0993 | 19.6717 | 18.8084 | 17.8493 | 94.3197 | 93.2115 | 91.7309 | 81.5737 | 69.8482 | 61.836 | 34.9038 | 34.949 | 34.8364 | 34.5006 | 33.8217 | 32.9596 | 104.868 | 102.8775 | 100.6775 | 86.2827 | 67.4185 | 46.8069 | 20.4353 | 20.6017 | 20.5827 | 20.1459 | 19.3164 | 18.3543 | 91.8269 | 90.789 | 89.5196 | 81.9932 | 70.509 | 62.4838

## BSP Headroom Generation
Grid Supply Point | Bulk Supply Point |  | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Generation (MVA) | Generation Headroom Winter (MVA) | [11 empty] | Generation Headroom Summer (MVA) | [11 empty] | Generation Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT BSP | MINIMUM HEADROOM | SU 85922 48779 | NO | YES | 0.42526 | 209.7947 | 208.3674 | 206.6021 | 204.2063 | 197.6558 | 189.5484 | 181.7579 | 173.88 | 166.0211 | 150.5274 | 141.5463 | 133.6389 | 184.2537 | 183.0116 | 181.5747 | 177.4221 | 168.8168 | 159.8337 | 151.2116 | 142.4779 | 133.7653 | 116.5463 | 106.6958 | 98.0211 | 192.3147 | 191.0695 | 189.6316 | 183.9084 | 175.2295 | 166.1684 | 157.4789 | 148.6726 | 139.8863 | 122.5874 | 112.6653 | 103.92
|  | ALDERSHOT BSP | EE |  |  |  |  | 209.7947 | 208.3674 | 206.6874 | 204.5126 | 201.7095 | 197.4937 | 193.3421 | 189.2768 | 185.2884 | 177.94 | 171.6663 | 166.4558 | 184.2537 | 183.0116 | 181.5842 | 179.4253 | 174.2705 | 169.0358 | 164.5916 | 160.2526 | 156.0011 | 147.5768 | 140.5242 | 134.6579 | 192.3147 | 191.0695 | 189.6421 | 186.9242 | 180.7526 | 175.4832 | 171.0105 | 166.6505 | 162.3716 | 153.9242 | 146.8084 | 140.8811
|  | ALDERSHOT BSP | HT |  |  |  |  | 209.8884 | 208.4832 | 206.6021 | 204.2063 | 197.6558 | 189.5484 | 181.7579 | 173.88 | 166.0211 | 150.5274 | 141.5463 | 133.6389 | 184.3221 | 183.1347 | 181.5747 | 177.4221 | 168.8168 | 159.8337 | 151.2116 | 142.4779 | 133.7653 | 116.5463 | 106.6958 | 98.0211 | 192.3842 | 191.1958 | 189.6316 | 183.9084 | 175.2295 | 166.1684 | 157.4789 | 148.6726 | 139.8863 | 122.5874 | 112.6653 | 103.92
|  | ALDERSHOT BSP | HE |  |  |  |  | 210.2084 | 208.8726 | 207.2789 | 205.1642 | 202.3884 | 199.8284 | 197.3779 | 194.0884 | 190.5926 | 187.2379 | 183.4779 | 180.4011 | 184.5568 | 183.3632 | 181.9832 | 180.1105 | 177.2747 | 173.3811 | 169.5063 | 165.7537 | 162.0737 | 158.0011 | 153.6926 | 150.1653 | 192.6189 | 191.4253 | 190.0453 | 188.1726 | 184.72 | 179.8758 | 175.9821 | 172.2147 | 168.5158 | 164.4516 | 160.0989 | 156.5295
|  | ALDERSHOT BSP | FB |  |  |  |  | 211.1737 | 210.5105 | 209.8758 | 209.1663 | 208.3958 | 207.6389 | 206.9242 | 206.2589 | 205.5474 | 203.7842 | 200.9011 | 197.1611 | 185.4663 | 184.8821 | 184.36 | 183.7716 | 183.12 | 182.4621 | 181.8221 | 181.2284 | 180.5905 | 177.6789 | 172.4547 | 168.2453 | 193.5284 | 192.9442 | 192.4221 | 191.8337 | 191.1821 | 190.5242 | 189.8842 | 189.2905 | 188.6526 | 184.2432 | 178.9726 | 174.7242
FLEET-BRAMLEY GSP | ALTON BSP | ALTON BSP | MINIMUM HEADROOM | SU 72730 39772 | NO | YES | 89.5653 | 99.0011 | 95.9421 | 92.2579 | 88.5495 | 45.5221 | 0.21263 | -4.3663 | -8.9589 | -17.1642 | -92.3537 | -141.2042 | -165.7663 | 84.7747 | 81.4232 | 77.3811 | 73.3284 | 23.1968 | -29.8832 | -34.9832 | -40.1084 | -49.4937 | -137.3789 | -194.5032 | -223.0642 | 82.9063 | 81.8695 | 78.9411 | 74.8179 | 24.5589 | -28.3674 | -33.46 | -38.5747 | -47.9379 | -135.5674 | -192.5368 | -221.0274
|  | ALTON BSP | EE |  |  |  |  | 99.0011 | 95.9421 | 92.2579 | 89.6221 | 47.9874 | 5.3937 | 2.4474 | -0.38316 | -4.8326 | -40.8147 | -60.5137 | -85.5147 | 84.7747 | 81.4232 | 77.3811 | 74.5705 | 26.1663 | -23.7042 | -26.88 | -29.9126 | -34.8663 | -76.9337 | -99.8989 | -129.1684 | 82.9063 | 81.8695 | 78.9411 | 76.0958 | 27.4968 | -22.2368 | -25.42 | -28.4611 | -33.4137 | -75.3895 | -98.3158 | -127.5168
|  | ALTON BSP | HT |  |  |  |  | 99.4179 | 96.4674 | 92.3389 | 88.5495 | 45.5221 | 0.21263 | -4.3663 | -8.9589 | -17.1642 | -92.3537 | -141.2042 | -165.7663 | 85.2305 | 81.9937 | 77.4537 | 73.3284 | 23.1968 | -29.8832 | -34.9832 | -40.1084 | -49.4937 | -137.3789 | -194.5032 | -223.0642 | 83.0758 | 82.1063 | 79.02 | 74.8179 | 24.5589 | -28.3674 | -33.46 | -38.5747 | -47.9379 | -135.5674 | -192.5368 | -221.0274
|  | ALTON BSP | HE |  |  |  |  | 100.3421 | 97.9516 | 94.8947 | 92.8021 | 51.6126 | 9.4653 | 7.1526 | 4.9958 | 1.1021 | -31.4674 | -48.9653 | -72.1053 | 86.2884 | 83.6168 | 80.2526 | 78.0295 | 30.1737 | -19.2158 | -21.6863 | -23.9674 | -28.2989 | -66.6832 | -87.2579 | -114.4926 | 83.5011 | 82.7674 | 81.8558 | 79.6263 | 31.5621 | -17.6811 | -20.1484 | -22.4263 | -26.7505 | -65.0158 | -85.5274 | -112.68
|  | ALTON BSP | FB |  |  |  |  | 101.4695 | 100.52 | 99.2705 | 98.4189 | 81.9063 | 80.9032 | 79.9232 | 79.0632 | 78.2084 | 70.7411 | 50.5463 | 29.9453 | 87.6168 | 86.4326 | 85.0295 | 84.1063 | 65.2484 | 64.1347 | 63.0484 | 62.1 | 61.1621 | 52.6158 | 28.9653 | 4.78 | 84.0789 | 83.7284 | 83.4105 | 83.0558 | 66.5421 | 65.4295 | 64.3453 | 63.4 | 62.4632 | 53.9379 | 30.3558 | 6.2463
BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | AMESBURY BSP | MINIMUM HEADROOM | SU 15842 42724 | NO | YES | 0.22737 | 53.3579 | 52.2242 | 51.5095 | 19.5684 | 18.3495 | 16.9632 | 15.5232 | 12.2347 | 10.5632 | -0.57684 | -4.2716 | -7.5926 | 33.7484 | 32.4811 | 31.7126 | -5.6895 | -7.0021 | -8.4958 | -10.0589 | -13.7916 | -15.6274 | -28.4179 | -32.5768 | -36.3211 | 36.7989 | 35.5442 | 34.7789 | -2.1284 | -3.4347 | -4.9189 | -6.4716 | -10.1632 | -11.9842 | -24.6242 | -28.7432 | -32.4484
|  | AMESBURY BSP | EE |  |  |  |  | 53.3579 | 52.2242 | 51.5095 | 19.6621 | 18.6884 | 17.7537 | 16.8095 | 15.0263 | 14.1053 | 8.1295 | 5.5042 | 3.2189 | 33.7484 | 32.4811 | 31.7126 | -5.5842 | -6.6011 | -7.5747 | -8.5695 | -10.5474 | -11.5147 | -18.4495 | -21.46 | -24.0832 | 36.7989 | 35.5442 | 34.7789 | -2.0263 | -3.0379 | -4.0074 | -4.9989 | -6.9621 | -7.9232 | -14.7705 | -17.7463 | -20.34
|  | AMESBURY BSP | HT |  |  |  |  | 53.4979 | 52.4295 | 51.6411 | 19.5684 | 18.3495 | 16.9632 | 15.5232 | 12.2347 | 10.5632 | -0.57684 | -4.2716 | -7.5926 | 33.9084 | 32.7158 | 31.8663 | -5.6895 | -7.0021 | -8.4958 | -10.0589 | -13.7916 | -15.6274 | -28.4179 | -32.5768 | -36.3211 | 36.9568 | 35.7747 | 34.9316 | -2.1284 | -3.4347 | -4.9189 | -6.4716 | -10.1632 | -11.9842 | -24.6242 | -28.7432 | -32.4484
|  | AMESBURY BSP | HE |  |  |  |  | 53.8411 | 52.8874 | 52.3295 | 20.6137 | 19.72 | 18.9021 | 18.1105 | 16.4737 | 15.7032 | 10.9221 | 9.0168 | 7.3505 | 34.2979 | 33.2389 | 32.6505 | -4.4937 | -5.4168 | -6.2621 | -7.0779 | -8.8863 | -9.6779 | -15.2979 | -17.5126 | -19.4579 | 37.3411 | 36.2916 | 35.7053 | -0.94842 | -1.8674 | -2.7105 | -3.5242 | -5.3158 | -6.1063 | -11.6526 | -13.8379 | -15.7589
|  | AMESBURY BSP | FB |  |  |  |  | 55.5547 | 53.4463 | 53.1526 | 52.8379 | 52.5074 | 52.1726 | 20.8221 | 20.5211 | 20.2084 | 18.1295 | 16.4221 | 14.9221 | 36.2653 | 33.8179 | 33.4989 | 33.1579 | 32.8011 | 32.44 | -4.3358 | -4.6621 | -4.9968 | -7.3232 | -9.2674 | -10.9895 | 39.2863 | 36.8684 | 36.5526 | 36.2126 | 35.86 | 35.5011 | -0.78526 | -1.1095 | -1.4421 | -3.7463 | -5.6684 | -7.3684
MELKSHAM GSP | ANDOVER BSP | ANDOVER BSP | MINIMUM HEADROOM | SU 35334 46598 | NO | YES | 43.0747 | 64.46 | 29.6611 | 91.7737 | 88.4895 | 84.3189 | 61.1789 | 57.5495 | 51.2305 | 45.3 | -1.6726 | -20.2347 | -31.4832 | 43.1779 | 2.0947 | 59.4147 | 55.7389 | 51.0968 | 24.0842 | 20.0368 | 12.8347 | 6.3453 | -47.9179 | -69.8789 | -82.8105 | 46.6979 | 5.7032 | 63.0937 | 59.4232 | 54.7842 | 27.8474 | 23.8032 | 16.6147 | 9.7432 | -44.1411 | -66.2653 | -79.1642
|  | ANDOVER BSP | EE |  |  |  |  | 64.46 | 29.6611 | 91.7737 | 88.4895 | 84.3189 | 61.1789 | 57.5495 | 51.2305 | 46.3074 | 22.2095 | 13.4189 | 3.5011 | 43.1779 | 2.0947 | 59.4147 | 55.7389 | 51.0968 | 24.0842 | 20.0368 | 12.8347 | 7.2653 | -20.6832 | -30.8537 | -42.3884 | 46.6979 | 5.7032 | 63.0937 | 59.4232 | 54.7842 | 27.8474 | 23.8032 | 16.6147 | 11.0579 | -17.2263 | -27.3737 | -38.8832
|  | ANDOVER BSP | HT |  |  |  |  | 64.7663 | 29.8484 | 91.9189 | 88.5516 | 87.6389 | 64.4979 | 60.6611 | 51.6863 | 45.3 | -1.6726 | -20.2347 | -31.4832 | 43.5337 | 2.2916 | 59.5758 | 55.8147 | 55.1926 | 28.1947 | 23.9316 | 13.6147 | 6.3453 | -47.9179 | -69.8789 | -82.8105 | 47.0474 | 5.9011 | 63.2611 | 59.5032 | 58.46 | 31.5432 | 27.2884 | 16.9958 | 9.7432 | -44.1411 | -66.2653 | -79.1642
|  | ANDOVER BSP | HE |  |  |  |  | 65.4853 | 31.1358 | 93.6274 | 90.6611 | 86.7189 | 63.8621 | 60.5947 | 54.6632 | 50.1011 | 28.5695 | 21.4168 | 12.9716 | 44.3537 | 3.7589 | 61.5053 | 58.1905 | 53.8053 | 27.1053 | 23.4758 | 16.7158 | 11.5611 | -13.6021 | -21.98 | -31.8916 | 47.8642 | 7.3695 | 65.1916 | 61.8853 | 57.5074 | 30.8842 | 27.2621 | 20.5232 | 15.38 | -10.1242 | -18.4737 | -28.3579
|  | ANDOVER BSP | FB |  |  |  |  | 95.2684 | 94.3568 | 144.7326 | 105.24 | 103.8063 | 102.2558 | 100.6074 | 93.4232 | 91.7821 | 85.2368 | 79.7989 | 72.3274 | 80.1821 | 79.1537 | 121.4316 | 75.02 | 73.3958 | 71.6305 | 69.7526 | 61.3484 | 59.4758 | 51.9926 | 45.9263 | 37.2074 | 84.4421 | 83.3705 | 124.9958 | 78.6695 | 77.0474 | 75.2874 | 73.4137 | 65.0358 | 63.1674 | 55.7032 | 49.2379 | 40.5432
MANNINGTON GSP | ARNEWOOD BSP | ARNEWOOD BSP | MINIMUM HEADROOM | SZ 26094 97294 | NO | YES | 13 | 75.3053 | 68.1853 | 63.1095 | 104.7021 | 101.2474 | 97.4221 | 93.0537 | 86.5389 | 82.1937 | 73.8853 | 68.0263 | 63.1189 | 66.5137 | 56.3305 | 49.9842 | 87.9821 | 84.1642 | 79.9326 | 75.0589 | 67.6505 | 62.7968 | 53.6253 | 47.1 | 41.6463 | 68.6084 | 58.7979 | 52.5137 | 91.0958 | 87.3495 | 83.1979 | 78.4211 | 71.1863 | 66.4295 | 57.4263 | 50.9926 | 45.5505
|  | ARNEWOOD BSP | EE |  |  |  |  | 75.3053 | 73.8811 | 63.4758 | 106.0895 | 103.8611 | 101.5442 | 98.8568 | 95.2032 | 92.8411 | 88.8168 | 84.6989 | 81.5063 | 66.5137 | 64.8084 | 50.4884 | 89.6 | 87.2442 | 84.7705 | 81.8347 | 77.7716 | 75.2253 | 70.6537 | 65.96 | 62.3147 | 68.6084 | 67.1347 | 53.0105 | 92.6716 | 90.34 | 87.8947 | 85.0053 | 81.0232 | 78.5126 | 74.0463 | 69.4663 | 65.9074
|  | ARNEWOOD BSP | HT |  |  |  |  | 75.4516 | 73.7853 | 63.1095 | 104.7021 | 101.2474 | 97.4221 | 93.0537 | 86.5389 | 82.1937 | 73.8853 | 68.0263 | 63.1189 | 66.7053 | 64.6442 | 49.9842 | 87.9821 | 84.1642 | 79.9326 | 75.0589 | 67.6505 | 62.7968 | 53.6253 | 47.1 | 41.6463 | 68.6453 | 66.9726 | 52.5137 | 91.0958 | 87.3495 | 83.1979 | 78.4211 | 71.1863 | 66.4295 | 57.4263 | 50.9926 | 45.5505
|  | ARNEWOOD BSP | HE |  |  |  |  | 76.1505 | 75.0442 | 64.9168 | 108.0389 | 105.9937 | 103.9253 | 101.5432 | 98.2116 | 96.1684 | 94.5916 | 91.9811 | 90.0674 | 67.6221 | 66.3421 | 52.3937 | 91.8368 | 89.6916 | 87.4937 | 84.9221 | 81.2337 | 79.0589 | 77.1832 | 74.1526 | 71.9253 | 68.8116 | 68.1274 | 54.8937 | 94.8526 | 92.7274 | 90.5526 | 88.0189 | 84.3989 | 82.2484 | 80.4316 | 77.4821 | 75.3158
|  | ARNEWOOD BSP | FB |  |  |  |  | 76.9621 | 68.1853 | 66.8589 | 126.1074 | 110.2011 | 109.3368 | 108.4274 | 107.62 | 106.9105 | 104.1516 | 101.1895 | 98.9895 | 68.1768 | 56.3305 | 54.5832 | 113.6621 | 94.0821 | 93.1316 | 92.1253 | 91.2337 | 90.4642 | 87.4505 | 84.0937 | 81.5842 | 69.3232 | 58.7979 | 57.0716 | 116.1589 | 97.0811 | 96.1484 | 95.1589 | 94.2853 | 93.5263 | 90.5611 | 87.2821 | 84.8337
BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | BASINGSTOKE (T1A & T2A) BSP | MINIMUM HEADROOM | SU 65132 52710 | YES | YES | 29.4737 | 102.1558 | 101.7389 | 101.2674 | 100.7158 | 99.1716 | 97.4789 | 96.1768 | 95.6474 | 94.4105 | 91.6589 | 89.4263 | 87.3874 | 95.6032 | 95.2 | 94.7484 | 94.2063 | 93.5253 | 92.8926 | 92.2653 | 91.6074 | 91.0053 | 87.4453 | 85.9832 | 83.68 | 99.1842 | 98.7789 | 98.3263 | 97.6484 | 95.7442 | 93.7884 | 92.3158 | 91.84 | 90.4453 | 86.7526 | 84.9568 | 82.6579
|  | BASINGSTOKE (T1A & T2A) BSP | EE |  |  |  |  | 102.1558 | 101.7389 | 101.2674 | 100.7158 | 99.5642 | 98.1547 | 97.0137 | 95.6474 | 94.4105 | 96.4084 | 95.2432 | 93.7189 | 95.6032 | 95.2 | 94.7484 | 94.2063 | 93.5253 | 92.8926 | 92.2653 | 91.6074 | 91.0053 | 92.8105 | 92.1884 | 91.5526 | 99.1842 | 98.7789 | 98.3263 | 97.6484 | 96.2611 | 94.66 | 93.3874 | 91.84 | 90.4453 | 96.1842 | 95.0926 | 93.3547
|  | BASINGSTOKE (T1A & T2A) BSP | HT |  |  |  |  | 102.2211 | 101.8326 | 101.3716 | 100.8063 | 99.1716 | 97.4789 | 96.1768 | 99.5947 | 98.3863 | 95.9589 | 89.4263 | 87.3874 | 95.6632 | 95.2937 | 94.8505 | 94.3095 | 93.7326 | 93.1442 | 92.5558 | 94.6684 | 94.1053 | 92.7453 | 85.9832 | 83.68 | 99.2442 | 98.8737 | 98.4295 | 97.6621 | 95.7442 | 93.7884 | 92.3158 | 99.4432 | 98.3042 | 95.9116 | 84.9568 | 82.6579
|  | BASINGSTOKE (T1A & T2A) BSP | HE |  |  |  |  | 102.4189 | 102.1389 | 101.8316 | 101.42 | 100.8242 | 99.6663 | 98.7411 | 97.6611 | 96.6705 | 91.6589 | 91.5221 | 91.4253 | 95.8505 | 95.5811 | 95.2916 | 94.8895 | 94.3411 | 93.8368 | 93.3474 | 92.8463 | 92.3589 | 87.4453 | 86.9126 | 86.4305 | 99.4337 | 99.1642 | 98.8747 | 98.4726 | 97.78 | 96.3716 | 95.3442 | 94.1253 | 93.0168 | 86.7526 | 86.1547 | 85.6095
|  | BASINGSTOKE (T1A & T2A) BSP | FB |  |  |  |  | 102.5937 | 102.4284 | 102.2779 | 102.1105 | 101.9189 | 101.7242 | 101.5411 | 101.1989 | 100.7411 | 98.6158 | 97.7 | 96.9274 | 96.0158 | 95.8632 | 95.7211 | 95.5663 | 95.3989 | 95.2295 | 95.0632 | 94.9074 | 94.7421 | 94.0958 | 93.6642 | 93.3305 | 99.5989 | 99.4463 | 99.3042 | 99.1495 | 98.9821 | 98.8063 | 98.4379 | 98.0137 | 97.4863 | 95.0116 | 93.98 | 93.1053
BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BASINGSTOKE (T1B & T2B) BSP | MINIMUM HEADROOM | SU 65132 52711 | NO | YES | 0.94737 | 103.86 | 87.8937 | 86.0611 | 83.8158 | 81.1737 | 77.9979 | 72.8021 | 67.72 | 62.7074 | 45.8 | 39.8684 | 35.8547 | 99.1042 | 78.9421 | 76.8653 | 74.3411 | 71.3758 | 67.7905 | 61.8337 | 56.0579 | 50.3632 | 30.9305 | 24.2421 | 19.7789 | 96.3579 | 76.7347 | 74.6632 | 72.1421 | 69.1863 | 65.6032 | 59.6621 | 53.9011 | 48.22 | 28.8389 | 22.1674 | 17.7116
|  | BASINGSTOKE (T1B & T2B) BSP | EE |  |  |  |  | 103.86 | 87.8937 | 86.0611 | 84.18 | 81.9389 | 79.6632 | 77.3547 | 72.4674 | 67.6042 | 50.8695 | 45.7168 | 43.0832 | 99.1042 | 78.9421 | 76.8653 | 74.7737 | 72.3179 | 69.8063 | 67.2389 | 61.6116 | 56.0737 | 36.5 | 30.5558 | 27.5495 | 96.3579 | 76.7347 | 74.6632 | 72.5726 | 70.1211 | 67.6158 | 65.0516 | 59.4389 | 53.9147 | 34.3947 | 28.4653 | 25.4684
|  | BASINGSTOKE (T1B & T2B) BSP | HT |  |  |  |  | 103.8884 | 88.2232 | 86.1958 | 83.8158 | 81.1737 | 77.9979 | 72.8021 | 67.72 | 62.7074 | 45.8 | 39.8684 | 35.8547 | 99.3568 | 79.3242 | 77.0263 | 74.3411 | 71.3758 | 67.7905 | 61.8337 | 56.0579 | 50.3632 | 30.9305 | 24.2421 | 19.7789 | 96.5747 | 77.1158 | 74.8232 | 72.1421 | 69.1863 | 65.6032 | 59.6621 | 53.9011 | 48.22 | 28.8389 | 22.1674 | 17.7116
|  | BASINGSTOKE (T1B & T2B) BSP | HE |  |  |  |  | 103.9832 | 88.8947 | 87.3137 | 85.6263 | 83.5189 | 81.4295 | 79.2811 | 75.8516 | 72.4789 | 60.0421 | 54.4884 | 50.8232 | 99.9495 | 80.12 | 78.3379 | 76.4789 | 74.1811 | 71.8832 | 69.5084 | 65.5905 | 61.7653 | 47.0979 | 40.5832 | 36.2842 | 96.6695 | 77.9095 | 76.1316 | 74.2758 | 71.9811 | 69.6874 | 67.3158 | 63.4084 | 59.5895 | 44.9653 | 38.4716 | 34.1863
|  | BASINGSTOKE (T1B & T2B) BSP | FB |  |  |  |  | 104.4147 | 104.1453 | 103.9021 | 88.8284 | 88.02 | 87.1453 | 86.3116 | 85.4747 | 83.7832 | 76.7337 | 69.8758 | 66.4042 | 100.8947 | 99.9916 | 99.1074 | 79.9958 | 79.0832 | 78.0874 | 77.1421 | 76.1874 | 74.2032 | 65.9484 | 57.9768 | 53.9558 | 97.1011 | 96.8316 | 96.3663 | 77.7874 | 76.8758 | 75.8821 | 74.9379 | 73.9863 | 72.0074 | 63.7747 | 55.8263 | 51.8168
BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | BASINGSTOKE (T3 & T4) BSP | MINIMUM HEADROOM | SU 65132 52712 | NO | YES | 73.3811 | 98.4705 | 97.8432 | 88.8105 | 87.4147 | 85.6242 | 83.7337 | 81.5705 | 79.3747 | 25.3653 | 16.5979 | 13.6579 | 11.2305 | 101.7295 | 101.4105 | 86.2337 | 84.42 | 82.0905 | 79.64 | 76.8021 | 73.9158 | 7.4621 | -2.6053 | -5.9147 | -8.6368 | 102.3463 | 102.0611 | 88.3516 | 86.56 | 84.2632 | 81.8432 | 79.0432 | 76.1947 | 9.9579 | -0.078947 | -3.38 | -6.0968
|  | BASINGSTOKE (T3 & T4) BSP | EE |  |  |  |  | 98.4705 | 97.8432 | 88.8105 | 87.6084 | 86.0958 | 84.56 | 82.9874 | 80.8263 | 27.1621 | 19.0463 | 16.8411 | 15.1516 | 101.7295 | 101.4105 | 86.2337 | 84.7021 | 82.7926 | 80.8411 | 78.8211 | 75.9642 | 9.5621 | 0.092632 | -2.4358 | -4.3674 | 102.3463 | 102.0611 | 88.3516 | 86.8368 | 84.9495 | 83.0189 | 81.0263 | 78.2074 | 12.0505 | 2.6158 | 0.092632 | -1.8358
|  | BASINGSTOKE (T3 & T4) BSP | HT |  |  |  |  | 98.5442 | 97.9558 | 88.8674 | 87.4147 | 85.6242 | 83.7337 | 81.5705 | 79.3747 | 25.3653 | 16.5979 | 13.6579 | 11.2305 | 101.7547 | 101.46 | 86.3063 | 84.42 | 82.0905 | 79.64 | 76.8021 | 73.9158 | 7.4621 | -2.6053 | -5.9147 | -8.6368 | 102.3684 | 102.1042 | 88.4242 | 86.56 | 84.2632 | 81.8432 | 79.0432 | 76.1947 | 9.9579 | -0.078947 | -3.38 | -6.0968
|  | BASINGSTOKE (T3 & T4) BSP | HE |  |  |  |  | 98.6705 | 98.1105 | 89.2842 | 88.1484 | 86.6632 | 85.1842 | 83.7053 | 81.8232 | 28.7284 | 21.2768 | 19.7116 | 19.0905 | 101.7821 | 101.4695 | 86.8937 | 85.4589 | 83.6 | 81.7284 | 79.8463 | 77.3968 | 11.4095 | 2.6263 | 0.80105 | 0.082105 | 102.3853 | 102.0989 | 89.0021 | 87.5832 | 85.7463 | 83.8947 | 82.0358 | 79.6179 | 13.8937 | 5.1368 | 3.3168 | 2.6011
|  | BASINGSTOKE (T3 & T4) BSP | FB |  |  |  |  | 99.0032 | 98.6684 | 98.3684 | 89.8547 | 89.2821 | 88.6758 | 88.0211 | 87.34 | 86.3874 | 81.7189 | 80.3842 | 79.6663 | 102.0084 | 101.8442 | 101.6947 | 87.54 | 86.7937 | 85.9989 | 85.1316 | 84.2242 | 82.9316 | 76.5126 | 74.7474 | 73.8137 | 102.6 | 102.4537 | 102.32 | 89.6442 | 88.9074 | 88.1221 | 87.2684 | 86.3726 | 85.0989 | 78.7768 | 77.0358 | 76.1126
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH BSP | MINIMUM HEADROOM | SP5972023735 | NO | YES | 62.4832 | 100.5516 | 98.3263 | 109.2832 | 105.0032 | 82.3768 | 54.1895 | 40.3821 | 25.5242 | -6.4789 | -33.2474 | -14.5453 | -20.9705 | 91.3968 | 88.8389 | 96.4916 | 91.5579 | 65.0337 | 31.9705 | 15.8453 | -1.5168 | -39.08 | -70.2789 | -54.04 | -61.4316 | 84.36 | 81.8663 | 90.1579 | 85.3505 | 59.58 | 27.46 | 11.7832 | -5.0947 | -42.2389 | -73.3505 | -57.0611 | -64.4337
|  | BICESTER NORTH BSP | EE |  |  |  |  | 100.7084 | 98.88 | 111.5421 | 107.6547 | 94.2895 | 70.1242 | 59.1568 | 46.4874 | 17.2874 | -15.6295 | 4.5726 | -0.070526 | 91.9232 | 89.5 | 99.1526 | 94.6684 | 79.0495 | 50.7021 | 37.8979 | 23.0926 | -11.1874 | -49.8263 | -31.9211 | -37.3137 | 84.8674 | 82.5074 | 92.7389 | 88.3705 | 73.1895 | 45.6526 | 33.2021 | 18.8095 | -14.4884 | -52.9558 | -35.0032 | -40.3811
|  | BICESTER NORTH BSP | HT |  |  |  |  | 100.5516 | 98.3263 | 109.2832 | 105.0032 | 82.3768 | 54.1895 | 40.3821 | 25.5242 | -6.4789 | -33.2474 | -14.5453 | -20.9705 | 91.3968 | 88.8389 | 96.4916 | 91.5579 | 65.0337 | 31.9705 | 15.8453 | -1.5168 | -39.08 | -70.2789 | -54.04 | -61.4316 | 84.36 | 81.8663 | 90.1579 | 85.3505 | 59.58 | 27.46 | 11.7832 | -5.0947 | -42.2389 | -73.3505 | -57.0611 | -64.4337
|  | BICESTER NORTH BSP | HE |  |  |  |  | 100.8916 | 99.7189 | 112.5737 | 108.84 | 95.5821 | 71.4347 | 60.5347 | 48.5611 | 20.0968 | -10.0811 | 9.8947 | 4.9126 | 92.6063 | 90.4474 | 100.3179 | 96.0084 | 80.5137 | 52.1842 | 39.4558 | 25.4684 | -7.9516 | -43.4526 | -25.8747 | -31.72 | 85.5379 | 83.4326 | 93.8811 | 89.6821 | 74.62 | 47.1021 | 34.7253 | 21.1263 | -11.3337 | -46.5979 | -28.9716 | -34.8
|  | BICESTER NORTH BSP | FB |  |  |  |  | 101.0947 | 100.9084 | 128.8537 | 127.2411 | 106.1305 | 102.2242 | 97.6611 | 93.0326 | 88.08 | 64.4968 | 54.7074 | 50.5811 | 93.6589 | 92.4284 | 119.4 | 117.5347 | 92.7032 | 88.1379 | 82.7989 | 77.3811 | 71.5842 | 43.9347 | 32.4779 | 27.6632 | 86.5663 | 85.3663 | 112.4211 | 110.6042 | 86.4926 | 82.0547 | 76.8663 | 71.6 | 65.9653 | 39.1053 | 27.9684 | 23.2874
BOTLEY WOOD GSP | BOTLEY WOOD BSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU 54073 09759 | NO | YES | 82.0937 | 98.6589 | 96.2042 | 95.84 | 95.4168 | 105.3347 | 103.1958 | 101.48 | 99.6421 | 97.7147 | 93.8242 | 91.3758 | 89.1811 | 96.8053 | 93.62 | 93.08 | 92.4484 | 103.2568 | 100.8021 | 98.8558 | 96.7589 | 94.5684 | 90.2253 | 87.4895 | 85.0326 | 92.6253 | 92.2463 | 92.1063 | 91.9474 | 102.7168 | 100.2611 | 98.3137 | 96.2168 | 94.0253 | 89.6821 | 86.9442 | 84.4874
|  | BOTLEY WOOD BSP | EE |  |  |  |  | 110.2242 | 109.4326 | 108.4379 | 107.3021 | 106.2042 | 105 | 103.7737 | 102.5621 | 101.3568 | 98.2863 | 96.5347 | 95.0558 | 110.3653 | 109.2179 | 107.7579 | 106.1305 | 104.6726 | 103.0242 | 101.6042 | 100.2526 | 98.9095 | 95.2789 | 93.2642 | 91.5684 | 105.4884 | 105.2053 | 104.8779 | 104.4442 | 103.8642 | 102.4832 | 101.0642 | 99.7116 | 98.3684 | 94.7368 | 92.7211 | 91.0242
|  | BOTLEY WOOD BSP | HT |  |  |  |  | 110.2705 | 109.3758 | 108.2432 | 106.8326 | 105.3347 | 103.1958 | 101.48 | 99.6421 | 97.7147 | 93.8242 | 91.3758 | 89.1811 | 110.4379 | 109.1053 | 107.4326 | 105.3516 | 103.2568 | 100.8021 | 98.8558 | 96.7589 | 94.5684 | 90.2253 | 87.4895 | 85.0326 | 105.4947 | 105.2263 | 104.8695 | 104.42 | 102.7168 | 100.2611 | 98.3137 | 96.2168 | 94.0253 | 89.6821 | 86.9442 | 84.4874
|  | BOTLEY WOOD BSP | HE |  |  |  |  | 110.4758 | 109.7779 | 108.9116 | 107.8895 | 106.8411 | 105.7863 | 104.8126 | 103.7505 | 102.54 | 100.5147 | 99.7684 | 99.0411 | 110.7579 | 109.7653 | 108.5063 | 107.0653 | 105.6853 | 104.2705 | 102.9863 | 101.6589 | 100.3084 | 97.8558 | 96.9684 | 96.1 | 105.5347 | 105.2621 | 104.9547 | 104.5326 | 103.96 | 103.4221 | 102.4463 | 101.1189 | 99.7674 | 97.3147 | 96.4274 | 95.5579
|  | BOTLEY WOOD BSP | FB |  |  |  |  | 98.6589 | 96.2042 | 95.84 | 95.4168 | 109.4453 | 109.0621 | 108.6905 | 108.3284 | 107.96 | 106.2326 | 105.3379 | 104.5168 | 96.8053 | 93.62 | 93.08 | 92.4484 | 109.2011 | 108.6505 | 108.1158 | 107.5916 | 107.0611 | 104.48 | 103.2505 | 102.2968 | 92.6253 | 92.2463 | 92.1063 | 91.9474 | 105.2579 | 105.1158 | 104.9779 | 104.8495 | 104.7116 | 103.9389 | 102.7095 | 101.7547
MANNINGTON GSP | BOURNEMOUTH BSP | BOURNEMOUTH BSP | MINIMUM HEADROOM | SZ 06265 92437 | NO | YES | 0.078947 | 221.6726 | 220.3537 | 196.1074 | 189.9442 | 181.7968 | 174.3884 | 166.3611 | 158.9 | 151.2705 | 133.0011 | 121.2716 | 110.5916 | 201.2758 | 199.9568 | 175.7105 | 173.42 | 164.0989 | 155.7232 | 146.6011 | 138.1589 | 129.5095 | 108.7937 | 95.48 | 83.3421 | 202.2895 | 200.9705 | 176.7242 | 174.6263 | 165.9337 | 157.5758 | 148.4758 | 140.0505 | 131.4168 | 110.7453 | 97.4621 | 85.3474
|  | BOURNEMOUTH BSP | EE |  |  |  |  | 221.6726 | 220.3537 | 196.1263 | 192.0905 | 185.2663 | 181.3747 | 176.6705 | 172.9179 | 169.1168 | 158.72 | 150.3411 | 143.0179 | 201.2758 | 199.9568 | 175.7295 | 173.7568 | 168.3105 | 164.1453 | 158.9611 | 154.9432 | 150.8642 | 138.7221 | 128.9832 | 120.4442 | 202.2895 | 200.9705 | 176.74 | 174.7695 | 170.1347 | 165.9747 | 160.8 | 156.7863 | 152.7074 | 140.5979 | 130.8832 | 122.3663
|  | BOURNEMOUTH BSP | HT |  |  |  |  | 221.7526 | 220.5116 | 196.1074 | 189.9442 | 181.7968 | 174.3884 | 166.3611 | 158.9 | 151.2705 | 133.0011 | 121.2716 | 110.5916 | 201.3558 | 200.1147 | 175.7105 | 173.42 | 164.0989 | 155.7232 | 146.6011 | 138.1589 | 129.5095 | 108.7937 | 95.48 | 83.3421 | 202.3695 | 201.1284 | 176.7242 | 174.6263 | 165.9337 | 157.5758 | 148.4758 | 140.0505 | 131.4168 | 110.7453 | 97.4621 | 85.3474
|  | BOURNEMOUTH BSP | HE |  |  |  |  | 221.9358 | 220.6147 | 196.3663 | 194.3326 | 188.4337 | 184.8632 | 180.6442 | 177.3884 | 174.1053 | 168.5126 | 163.1221 | 158.3874 | 201.5389 | 200.2179 | 175.9695 | 173.9358 | 171.0758 | 168.3463 | 163.7663 | 160.3695 | 156.9253 | 150.1421 | 143.7537 | 138.1189 | 202.5526 | 201.2316 | 176.9832 | 174.9495 | 172.0895 | 169.5126 | 165.5916 | 162.1958 | 158.7537 | 151.9937 | 145.6242 | 140.0032
|  | BOURNEMOUTH BSP | FB |  |  |  |  | 222.8505 | 222.1579 | 198.7579 | 198.06 | 197.2842 | 196.5032 | 195.7432 | 194.6589 | 193.2663 | 185.9905 | 180.3053 | 175.3305 | 202.4537 | 201.7611 | 178.3611 | 177.6632 | 176.8874 | 176.1063 | 175.3463 | 174.64 | 173.8832 | 169.1642 | 162.6168 | 156.8095 | 203.4674 | 202.7747 | 179.3747 | 178.6768 | 177.9011 | 177.12 | 176.36 | 175.6537 | 174.8968 | 170.9884 | 164.4547 | 158.6632
FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL BSP | MINIMUM HEADROOM | SU 86026 69422 | NO | YES | 1.2179 | 227.3653 | 226.7863 | 226.2684 | 227.7084 | 223.5779 | 216.7589 | 209.4737 | 207.9968 | 200.5495 | 183.0253 | 166.7221 | 157.6242 | 209.6979 | 209.1189 | 208.6011 | 208.78 | 202.2 | 194.5653 | 186.3726 | 185.1611 | 178.7232 | 159.0474 | 138.1863 | 127.9579 | 206.0095 | 205.4305 | 204.9126 | 206.4642 | 203.0232 | 195.3989 | 187.2158 | 186.0463 | 179.6095 | 161.0284 | 138.7926 | 128.4695
|  | BRACKNELL BSP | EE |  |  |  |  | 237.72 | 236.3421 | 232.5105 | 230.34 | 225.4179 | 220.4105 | 214.0463 | 208.0463 | 202.2547 | 197.1737 | 189.7695 | 183.5453 | 222.9684 | 221.58 | 212.4758 | 209.7884 | 204.4263 | 198.9495 | 191.8326 | 185.1611 | 178.7232 | 175.2453 | 166.7684 | 159.6126 | 217.6411 | 216.2495 | 213.2105 | 210.6811 | 205.3158 | 199.8379 | 192.7221 | 186.0463 | 179.6095 | 177.3221 | 168.7453 | 161.5095
|  | BRACKNELL BSP | HT |  |  |  |  | 237.8779 | 236.5926 | 232.8105 | 229.5147 | 223.5779 | 216.7589 | 209.4737 | 207.9968 | 200.5495 | 183.0253 | 166.7221 | 157.6242 | 223.1305 | 221.8368 | 212.8 | 208.78 | 202.2 | 194.5653 | 186.3726 | 187.2274 | 178.8253 | 159.0474 | 138.1863 | 127.9579 | 217.8042 | 216.5074 | 213.5432 | 209.6842 | 203.0232 | 195.3989 | 187.2158 | 189.4516 | 180.98 | 161.0284 | 138.7926 | 128.4695
|  | BRACKNELL BSP | HE |  |  |  |  | 238.2442 | 237.0695 | 235.7168 | 234.1495 | 229.6168 | 225.0705 | 219.26 | 213.7274 | 208.4232 | 198.5653 | 193.8853 | 189.9326 | 223.5084 | 222.3337 | 216.2579 | 214.1295 | 209.2063 | 204.2389 | 197.7537 | 191.6084 | 185.7221 | 172.9295 | 167.4284 | 162.7663 | 218.1842 | 217.0095 | 215.6568 | 215.0526 | 210.1358 | 205.1737 | 198.7 | 192.5568 | 186.6821 | 173.0347 | 167.5432 | 162.8905
|  | BRACKNELL BSP | FB |  |  |  |  | 227.3653 | 226.7863 | 226.2684 | 227.7084 | 227.0611 | 237.5579 | 235.0853 | 232.6947 | 230.2168 | 222.1347 | 217.6084 | 213.5432 | 209.6979 | 209.1189 | 208.6011 | 210.0063 | 209.3589 | 217.7537 | 214.9274 | 212.1916 | 209.3611 | 200.1758 | 195.0621 | 190.3779 | 206.0095 | 205.4305 | 204.9126 | 206.4642 | 205.8168 | 218.2326 | 215.8547 | 213.1221 | 210.2958 | 201.1253 | 195.9358 | 191.2568
FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | BURGHFIELD (MAIN) BSP | MINIMUM HEADROOM | SU 69442 70509 | NO | YES | 3.1579 | 108.7916 | 107.9411 | 106.2505 | 103.9937 | 101 | 95.3842 | 53.6737 | 50.4137 | 47.5505 | 18.2937 | -2.3147 | -13.8032 | 103.5537 | 101.7232 | 99.2158 | 96.3737 | 92.5274 | 85.1726 | 39.8663 | 36.2832 | 33.1674 | -0.83895 | -24.8484 | -38.1074 | 105.8042 | 104.7968 | 102.2453 | 99.3589 | 95.4474 | 87.9389 | 39.6811 | 36.1053 | 32.9926 | -0.92105 | -24.8611 | -38.0874
|  | BURGHFIELD (MAIN) BSP | EE |  |  |  |  | 108.7916 | 107.9411 | 106.2758 | 104.4095 | 101.4832 | 96.6189 | 55.5463 | 52.8937 | 50.7263 | 35.2474 | 26.0337 | 15.5116 | 103.5537 | 101.7232 | 99.2579 | 96.9832 | 93.2895 | 86.6084 | 42.0453 | 39.16 | 36.8453 | 18.7116 | 7.9611 | -4.3705 | 105.8042 | 104.7968 | 102.2895 | 99.9842 | 96.2316 | 89.4147 | 41.8537 | 38.9726 | 36.6621 | 18.5811 | 7.8579 | -4.4368
|  | BURGHFIELD (MAIN) BSP | HT |  |  |  |  | 108.8642 | 108.0379 | 106.2505 | 103.9937 | 101 | 95.3842 | 53.6737 | 50.4137 | 47.5505 | 18.2937 | -2.3147 | -13.8032 | 103.8516 | 101.9337 | 99.2158 | 96.3737 | 92.5274 | 85.1726 | 39.8663 | 36.2832 | 33.1674 | -0.83895 | -24.8484 | -38.1074 | 105.8484 | 105.0095 | 102.2453 | 99.3589 | 95.4474 | 87.9389 | 39.6811 | 36.1053 | 32.9926 | -0.92105 | -24.8611 | -38.0874
|  | BURGHFIELD (MAIN) BSP | HE |  |  |  |  | 109.0579 | 108.2695 | 107.3042 | 105.7326 | 102.9063 | 98.1916 | 57.9295 | 55.5179 | 53.5789 | 40.2895 | 32.4821 | 23.1547 | 104.5474 | 103.0811 | 100.9305 | 98.9 | 95.3653 | 88.8884 | 44.8253 | 42.2253 | 40.1832 | 24.4453 | 15.2484 | 4.2379 | 105.9768 | 105.2758 | 103.9989 | 101.9442 | 98.3558 | 91.7463 | 44.6274 | 42.0316 | 39.9916 | 24.3021 | 15.1316 | 4.1547
|  | BURGHFIELD (MAIN) BSP | FB |  |  |  |  | 109.6789 | 109.2632 | 108.8737 | 108.4579 | 107.9568 | 106.2337 | 105.3979 | 104.58 | 67.2053 | 62.9537 | 51.9242 | 43.3495 | 105.7274 | 104.9947 | 104.0168 | 103.1074 | 101.7442 | 98.9484 | 97.8726 | 96.8063 | 54.9179 | 50.1989 | 37.2863 | 27.2274 | 106.4989 | 106.1516 | 105.8358 | 105.4853 | 104.8179 | 101.9611 | 100.8663 | 99.7811 | 54.7589 | 49.9947 | 37.1189 | 27.0884
FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | BURGHFIELD (RESERVE) BSP | MINIMUM HEADROOM | SU 69442 70509 | NO | YES | 41.8737 | 75.44 | 74.0316 | 70.8505 | 68.82 | 66.4884 | 64.1221 | 61.9789 | 59.8621 | 57.7747 | 44.1042 | 37.7589 | 34.3421 | 65.5642 | 64.02 | 60.4432 | 58.2326 | 55.7 | 53.1453 | 50.8411 | 48.5653 | 46.3253 | 30.9232 | 23.8316 | 20.0863 | 64.1084 | 62.5474 | 58.9179 | 56.6842 | 54.1263 | 51.5432 | 49.22 | 46.9242 | 44.6621 | 29.0316 | 21.8432 | 18.0558
|  | BURGHFIELD (RESERVE) BSP | EE |  |  |  |  | 75.44 | 74.0316 | 70.8505 | 69.2653 | 67.4011 | 65.6632 | 64.0221 | 62.5221 | 61.1232 | 53.8884 | 50.1779 | 48.0347 | 65.5642 | 64.02 | 60.4432 | 58.7421 | 56.7558 | 54.9147 | 53.1737 | 51.6 | 50.14 | 41.8916 | 37.6979 | 35.2926 | 64.1084 | 62.5474 | 58.9179 | 57.2 | 55.1989 | 53.3442 | 51.5895 | 50.0053 | 48.5368 | 40.1568 | 35.9 | 33.4611
|  | BURGHFIELD (RESERVE) BSP | HT |  |  |  |  | 75.6189 | 74.2589 | 70.8589 | 68.82 | 66.4884 | 64.1221 | 61.9789 | 59.8621 | 57.7747 | 44.1042 | 37.7589 | 34.3421 | 65.7663 | 64.2779 | 60.4547 | 58.2326 | 55.7 | 53.1453 | 50.8411 | 48.5653 | 46.3253 | 30.9232 | 23.8316 | 20.0863 | 64.3147 | 62.8084 | 58.9295 | 56.6842 | 54.1263 | 51.5432 | 49.22 | 46.9242 | 44.6621 | 29.0316 | 21.8432 | 18.0558
|  | BURGHFIELD (RESERVE) BSP | HE |  |  |  |  | 76.1189 | 74.9737 | 72.0284 | 70.6379 | 68.9011 | 67.3263 | 65.8979 | 64.6116 | 63.4221 | 57.8484 | 55.1621 | 53.9916 | 66.3295 | 65.0842 | 61.7789 | 60.2947 | 58.4579 | 56.7989 | 55.2989 | 53.9695 | 52.7505 | 46.3053 | 43.2263 | 41.8905 | 64.8874 | 63.6295 | 60.2747 | 58.7789 | 56.9274 | 55.2568 | 53.7505 | 52.4158 | 51.1905 | 44.6316 | 41.5021 | 40.1421
|  | BURGHFIELD (RESERVE) BSP | FB |  |  |  |  | 85.5189 | 76.2989 | 75.7379 | 75.1389 | 74.4916 | 73.8547 | 73.26 | 72.7632 | 72.2853 | 70.3916 | 68.0547 | 66.5863 | 78.4842 | 66.5116 | 65.8979 | 65.2463 | 64.5379 | 63.8453 | 63.2 | 62.6642 | 62.1547 | 60.1168 | 57.5042 | 55.8611 | 77.2463 | 65.0684 | 64.4453 | 63.7874 | 63.0726 | 62.3726 | 61.7211 | 61.18 | 60.6653 | 58.6074 | 55.96 | 54.2947
FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY (MAIN) BSP | MINIMUM HEADROOM | SU 86530 59483 | NO | YES | 0.24211 | 104.4221 | 101.6484 | 98.7842 | 94.9621 | 89.8642 | 84.4568 | 79.1611 | 73.8505 | 68.6305 | 54.9463 | 46.5042 | 40.0663 | 85.5295 | 82.3947 | 79.1832 | 74.9032 | 69.1589 | 63.0779 | 57.1295 | 51.1516 | 45.2821 | 29.7674 | 20.0832 | 12.76 | 91.5905 | 88.4263 | 85.1905 | 80.8768 | 75.0853 | 68.9537 | 62.9568 | 56.9305 | 51.0137 | 35.3758 | 25.7126 | 18.4021
|  | CAMBERLEY (MAIN) BSP | EE |  |  |  |  | 104.4221 | 101.6484 | 98.8326 | 95.9547 | 92.5674 | 88.9537 | 85.0505 | 81.2737 | 77.6453 | 68.4916 | 62.3 | 58.0726 | 85.5295 | 82.3947 | 79.2337 | 76.0653 | 72.3758 | 68.4116 | 64.0758 | 59.8979 | 55.8937 | 45.2053 | 38.0242 | 33.1316 | 91.5905 | 88.4263 | 85.2411 | 82.0516 | 78.3421 | 74.3495 | 69.98 | 65.7737 | 61.7421 | 50.9389 | 43.6895 | 38.7505
|  | CAMBERLEY (MAIN) BSP | HT |  |  |  |  | 104.7495 | 102.0726 | 98.7842 | 94.9621 | 89.8642 | 84.4568 | 79.1611 | 73.8505 | 68.6305 | 54.9463 | 46.5042 | 40.0663 | 85.9126 | 82.8863 | 79.1832 | 74.9032 | 69.1589 | 63.0779 | 57.1295 | 51.1516 | 45.2821 | 29.7674 | 20.0832 | 12.76 | 91.9768 | 88.9263 | 85.1905 | 80.8768 | 75.0853 | 68.9537 | 62.9568 | 56.9305 | 51.0137 | 35.3758 | 25.7126 | 18.4021
|  | CAMBERLEY (MAIN) BSP | HE |  |  |  |  | 105.5716 | 103.22 | 100.7758 | 98.2126 | 95.0305 | 91.6779 | 88.0905 | 84.6337 | 81.3389 | 74.8958 | 70.3811 | 67.5853 | 86.8547 | 84.2158 | 81.4895 | 78.6884 | 75.24 | 71.5695 | 67.6116 | 63.8137 | 60.2011 | 52.5116 | 47.18 | 43.8789 | 92.9274 | 90.2695 | 87.5211 | 84.7021 | 81.2337 | 77.5389 | 73.5558 | 69.7305 | 66.0958 | 58.3137 | 52.9232 | 49.5853
|  | CAMBERLEY (MAIN) BSP | FB |  |  |  |  | 119.5989 | 119.1937 | 118.8316 | 118.1779 | 116.9779 | 115.7 | 114.1905 | 112.7011 | 111.1863 | 89.8768 | 85.6168 | 82.7274 | 106.0979 | 104.4958 | 103.2 | 101.96 | 100.6168 | 99.1811 | 97.4663 | 95.7726 | 94.0526 | 68.9895 | 64.0884 | 60.7537 | 108.8979 | 108.4926 | 108.1305 | 107.2495 | 106.1084 | 104.8958 | 103.4705 | 101.9158 | 100.2 | 74.9032 | 69.9537 | 66.5884
FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | CAMBERLEY (RESERVE) BSP | MINIMUM HEADROOM | SU 86530 59483 | NO | YES | 0.26421 | 99.8242 | 97.8621 | 96.0453 | 93.8632 | 91.3316 | 88.1832 | 88.4042 | 86.4179 | 84.4337 | 78.0368 | 64.0011 | 60.5126 | 102.6937 | 100.5074 | 98.2516 | 95.6032 | 92.6358 | 88.7589 | 89.5337 | 87.24 | 84.9379 | 79.2947 | 58.2295 | 53.9747 | 102.7147 | 102.0674 | 101.3179 | 98.7663 | 95.8558 | 91.9495 | 92.7453 | 90.4411 | 88.1263 | 84.3242 | 61.0853 | 56.7947
|  | CAMBERLEY (RESERVE) BSP | EE |  |  |  |  | 99.8242 | 97.8621 | 96.0453 | 94.1516 | 91.8211 | 89.9316 | 88.4042 | 86.4179 | 84.4337 | 87.6158 | 84.5274 | 82.3442 | 102.6937 | 100.5074 | 98.2516 | 95.9884 | 93.2432 | 91.1095 | 89.5337 | 87.24 | 84.9379 | 91.7358 | 87.6842 | 84.8484 | 102.7147 | 102.0674 | 101.3284 | 99.1526 | 96.3916 | 94.2484 | 92.7453 | 90.4411 | 88.1263 | 96.8789 | 92.7905 | 89.9274
|  | CAMBERLEY (RESERVE) BSP | HT |  |  |  |  | 100.0232 | 98.1042 | 96.0989 | 93.8632 | 91.3316 | 88.1832 | 94.1221 | 90.7211 | 87.2611 | 78.0368 | 64.0011 | 60.5126 | 102.7316 | 100.8242 | 98.3326 | 95.6032 | 92.6358 | 88.7589 | 99.6432 | 95.3968 | 91.0621 | 79.2947 | 58.2295 | 53.9747 | 102.7526 | 102.1337 | 101.3179 | 98.7663 | 95.8558 | 91.9495 | 104.4116 | 100.5642 | 96.1926 | 84.3242 | 61.0853 | 56.7947
|  | CAMBERLEY (RESERVE) BSP | HE |  |  |  |  | 100.5568 | 98.8579 | 97.2695 | 95.5632 | 93.3558 | 91.6305 | 90.2895 | 88.4884 | 86.6811 | 91.2337 | 89.2611 | 88.0316 | 102.8589 | 101.8326 | 99.8874 | 97.8758 | 95.3042 | 93.3821 | 92.0695 | 90.0305 | 87.9758 | 96.2526 | 93.5526 | 91.8705 | 102.88 | 102.2642 | 101.5505 | 100.5842 | 98.4747 | 96.5442 | 95.3095 | 93.2632 | 91.1968 | 101.3589 | 98.6284 | 96.9284
|  | CAMBERLEY (RESERVE) BSP | FB |  |  |  |  | 101.5958 | 100.6379 | 99.8853 | 99.1568 | 98.34 | 97.4863 | 96.8232 | 96.1537 | 95.4474 | 91.3326 | 89.0484 | 87.4726 | 103.3263 | 103.0274 | 102.7589 | 102.1674 | 101.1516 | 100.0905 | 99.2884 | 98.4716 | 97.6084 | 92.3053 | 89.3579 | 87.3116 | 103.3474 | 103.0484 | 102.78 | 102.4779 | 102.1421 | 101.8032 | 101.4758 | 101.1695 | 100.7884 | 95.4358 | 92.4611 | 90.3958
IVER 132KV GSP | CHALVEY BSP | CHALVEY BSP | MINIMUM HEADROOM | SU 96669 79364 | NO | YES | 4.1684 | 107.3158 | 106.7505 | 104.8263 | 100.6158 | 95.7621 | 181.9189 | 178.8063 | 174.4758 | 169.9337 | 157.5674 | 153.0516 | 149.0253 | 97.6179 | 97.08 | 95.6779 | 90.5 | 84.5747 | 169.9474 | 166.2368 | 161.0021 | 155.4789 | 140.3579 | 135.0442 | 130.3042 | 103.0232 | 102.4863 | 100.0484 | 95.0368 | 89.2989 | 174.7653 | 171.0611 | 165.8326 | 160.3189 | 145.2221 | 139.9147 | 135.18
|  | CHALVEY BSP | EE |  |  |  |  | 107.3158 | 106.7505 | 104.8263 | 100.6158 | 95.7621 | 181.9189 | 178.8063 | 175.1389 | 171.7453 | 161.8263 | 158.66 | 155.9621 | 97.6179 | 97.08 | 95.6779 | 90.5 | 84.5747 | 169.9474 | 166.2368 | 161.82 | 157.7558 | 145.2516 | 141.3958 | 138.0947 | 103.0232 | 102.4863 | 100.0484 | 95.0368 | 89.2989 | 174.7653 | 171.0611 | 166.6505 | 162.5905 | 150.1095 | 146.2579 | 142.9621
|  | CHALVEY BSP | HT |  |  |  |  | 107.3474 | 106.7663 | 105.3021 | 101.0821 | 97.0505 | 182.9716 | 179.3189 | 174.4758 | 169.9337 | 157.5674 | 153.0516 | 149.0253 | 97.6495 | 97.1495 | 96.1937 | 91.0989 | 86.2063 | 171.2853 | 166.9116 | 161.0021 | 155.4789 | 140.3579 | 135.0442 | 130.3042 | 103.0558 | 102.5558 | 100.6326 | 95.6126 | 90.8695 | 176.0947 | 171.7347 | 165.8326 | 160.3189 | 145.2221 | 139.9147 | 135.18
|  | CHALVEY BSP | HE |  |  |  |  | 107.3895 | 106.8537 | 105.8095 | 101.7358 | 96.9705 | 183.2505 | 180.3316 | 176.8368 | 173.6179 | 165.7389 | 163.7947 | 162.1379 | 97.6916 | 97.1558 | 96.5453 | 91.9211 | 86.1179 | 171.6411 | 168.1884 | 164 | 160.1611 | 150.0126 | 147.5621 | 145.4663 | 103.0979 | 102.5621 | 101.2474 | 96.4074 | 90.7832 | 176.4379 | 173.0095 | 168.8263 | 164.9926 | 154.8642 | 152.4189 | 150.3253
|  | CHALVEY BSP | FB |  |  |  |  | 107.8032 | 107.5305 | 107.2832 | 106.8695 | 106.4221 | 195.1474 | 193.8674 | 192.3242 | 190.8032 | 184.6337 | 182.3895 | 180.5589 | 98.1053 | 97.8326 | 97.5853 | 97.3074 | 97.0011 | 186.0274 | 184.4684 | 182.5621 | 180.6947 | 173.0758 | 170.3674 | 168.1274 | 103.5116 | 103.2389 | 102.9916 | 102.7137 | 102.4074 | 190.3947 | 188.8832 | 187.04 | 185.2326 | 177.8632 | 175.1874 | 172.9495
LOVEDEAN GSP | CHICHESTER BSP | CHICHESTER BSP | MINIMUM HEADROOM | SU 92281 07417 | NO | YES | 81.5337 | 101.6695 | 184.1874 | 162.2053 | 130.0379 | 120.7421 | 108.34 | 89.1158 | 79.4463 | 61.1379 | -31.9768 | -68.7389 | -95.9905 | 61.7653 | 142.6705 | 117.24 | 79.9705 | 70.0937 | 57.4568 | 35.56 | 26.1021 | 5.2821 | -103.6189 | -145.8053 | -176.94 | 67.1832 | 147.7211 | 122.5905 | 85.4842 | 75.5947 | 63.8337 | 41.9305 | 33.1116 | 12.2905 | -97.2526 | -139.4642 | -170.6221
|  | CHICHESTER BSP | EE |  |  |  |  | 101.6695 | 184.1874 | 162.2053 | 130.0379 | 121.0442 | 112.1684 | 97.4811 | 88.8484 | 77.7074 | 29.6684 | 5.0421 | -16.4705 | 61.7653 | 142.6705 | 117.24 | 79.9705 | 70.0937 | 60.3147 | 43.6758 | 34.1589 | 21.6821 | -32.9611 | -62.5874 | -87.4968 | 67.1832 | 147.7211 | 122.5905 | 85.4842 | 75.5947 | 65.8063 | 49.1526 | 39.6274 | 27.14 | -26.9032 | -57.1716 | -82.1168
|  | CHICHESTER BSP | HT |  |  |  |  | 104.9095 | 188.8274 | 166.2337 | 132.1105 | 120.7421 | 108.34 | 89.1158 | 79.4463 | 61.1379 | -31.9768 | -68.7389 | -95.9905 | 66.5326 | 149.7095 | 123.5989 | 84.0568 | 71.3337 | 57.4568 | 35.56 | 26.1021 | 5.2821 | -103.6189 | -145.8053 | -176.94 | 72.5979 | 155.8368 | 130.0032 | 90.4442 | 77.7147 | 63.8337 | 41.9305 | 33.1116 | 12.2905 | -97.2526 | -139.4642 | -170.6221
|  | CHICHESTER BSP | HE |  |  |  |  | 104.2063 | 187.7432 | 166.6695 | 135.2642 | 126.8274 | 118.6337 | 104.8589 | 97.1589 | 86.8989 | 40.8632 | 23.4821 | 5.5537 | 64.6432 | 146.7084 | 122.3084 | 85.9063 | 76.6484 | 67.6316 | 52.0442 | 43.5958 | 32.1389 | -22.5747 | -42.8916 | -63.8853 | 70.0484 | 151.7337 | 127.6379 | 91.4589 | 82.2 | 73.18 | 57.5884 | 49.1411 | 37.6811 | -17.3737 | -37.6968 | -58.6989
|  | CHICHESTER BSP | FB |  |  |  |  | 110.46 | 193.0537 | 190.3 | 187.2916 | 184.0221 | 180.5179 | 176.8347 | 173.3474 | 169.7884 | 151.8621 | 135.2253 | 120.16 | 71.7579 | 152.5642 | 149.4684 | 146.0905 | 142.42 | 138.48 | 134.32 | 130.3768 | 126.3642 | 105.9263 | 86.7295 | 69.2558 | 77.0811 | 157.5411 | 154.4779 | 151.1326 | 147.4989 | 143.5979 | 139.4811 | 135.5811 | 131.6063 | 111.3968 | 92.2842 | 74.8021
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL BSP | MINIMUM HEADROOM | SY 65479 80511 | NO | YES | 131.7158 | 114.7021 | 125.5926 | 107.6705 | 102.7505 | 96.8358 | 90.3705 | 83.9337 | 75.4653 | 68.0274 | 41.1758 | 29.9 | 19.7326 | 94.1326 | 107.7526 | 85.6168 | 80.1589 | 73.6 | 66.4305 | 59.2979 | 49.7695 | 41.4526 | 10.8853 | -1.76 | -13.1747 | 101.7453 | 113.6137 | 91.7053 | 86.2495 | 79.6863 | 72.5168 | 65.3842 | 55.8537 | 47.5316 | 16.9632 | 4.3147 | -7.1032
|  | CHICKERELL BSP | EE |  |  |  |  | 128.0747 | 125.5926 | 108.4105 | 105.1042 | 101.0432 | 97.2421 | 93.3758 | 88.5547 | 84.3379 | 69.9737 | 61.7589 | 54.5937 | 110.6 | 107.7526 | 86.4832 | 82.9074 | 78.5674 | 74.4989 | 70.3179 | 65.0316 | 60.4474 | 43.8853 | 34.5116 | 26.3179 | 116.4179 | 113.6137 | 92.5705 | 88.9947 | 84.6568 | 80.5853 | 76.4011 | 71.1147 | 66.5295 | 49.9674 | 40.5895 | 32.3895
|  | CHICKERELL BSP | HT |  |  |  |  | 128.3863 | 125.7684 | 107.6705 | 102.7505 | 96.8358 | 90.3705 | 83.9337 | 75.4653 | 68.0274 | 41.1758 | 29.9 | 19.7326 | 110.9789 | 107.9295 | 85.6168 | 80.1589 | 73.6 | 66.4305 | 59.2979 | 49.7695 | 41.4526 | 10.8853 | -1.76 | -13.1747 | 116.7905 | 113.7916 | 91.7053 | 86.2495 | 79.6863 | 72.5168 | 65.3842 | 55.8537 | 47.5316 | 16.9632 | 4.3147 | -7.1032
|  | CHICKERELL BSP | HE |  |  |  |  | 129.4526 | 127.4884 | 110.9474 | 108.0463 | 104.2463 | 100.8253 | 97.4768 | 93.1821 | 89.4926 | 79.5042 | 73.9042 | 69.0084 | 112.2895 | 110.0905 | 89.3937 | 86.2821 | 82.2505 | 78.6074 | 75.0368 | 70.3726 | 66.4063 | 54.6421 | 48.1347 | 42.4347 | 118.0747 | 115.9053 | 95.4895 | 92.3768 | 88.3442 | 84.7011 | 81.1316 | 76.4653 | 72.4979 | 60.7358 | 54.2189 | 48.5179
|  | CHICKERELL BSP | FB |  |  |  |  | 114.7021 | 129.52 | 128.4 | 127.1832 | 125.8463 | 110.0611 | 108.6389 | 107.2484 | 105.8137 | 99.6463 | 94.2947 | 89.6358 | 94.1326 | 112.2947 | 110.9989 | 109.5989 | 108.06 | 88.2989 | 86.7326 | 85.1989 | 83.6179 | 76.7653 | 70.6989 | 65.3663 | 101.7453 | 118.0884 | 116.8147 | 115.4337 | 113.9189 | 94.3926 | 92.8263 | 91.2905 | 89.7105 | 82.8558 | 76.7895 | 71.4526
MELKSHAM GSP | CHIPPENHAM BSP | CHIPPENHAM BSP | MINIMUM HEADROOM | ST 92629 74275 | NO | YES | 219.2884 | 63.3274 | 91.4853 | 79.6432 | 75.5389 | 69.6674 | -5.3832 | -8.0442 | -12.1474 | -65.1105 | -91.04 | -101.2263 | -109.9737 | 53.0737 | 66.8789 | 52.8768 | 48.2347 | 41.5884 | -36.2916 | -39.5916 | -46.2389 | -108.3758 | -137.1495 | -151.1537 | -161.0432 | 58.1853 | 70.9811 | 56.9189 | 52.2674 | 45.5958 | -38.8032 | -41.9737 | -46.9368 | -109.0937 | -137.2958 | -151.9074 | -161.8011
|  | CHIPPENHAM BSP | EE |  |  |  |  | 63.3274 | 91.4853 | 79.6432 | 75.5389 | 69.6674 | -5.3832 | -8.0442 | -11.7884 | -56.4516 | -73.7189 | -73.6158 | -79.7379 | 53.0737 | 66.8789 | 52.8768 | 48.2347 | 41.5884 | -36.2916 | -39.5916 | -44.1789 | -96.3053 | -116.4326 | -115.9495 | -122.9958 | 58.1853 | 70.9811 | 56.9189 | 52.2674 | 45.5958 | -38.8032 | -41.9737 | -46.4284 | -98.2379 | -118.3705 | -116.9979 | -124.0526
|  | CHIPPENHAM BSP | HT |  |  |  |  | 63.6884 | 92.0211 | 79.9632 | 76.9 | 71.3547 | -0.75474 | -5.0789 | -12.1474 | -65.1105 | -91.04 | -101.2263 | -109.9737 | 53.5063 | 67.4947 | 53.2589 | 50.7305 | 44.4411 | -32.4537 | -37.7 | -46.2389 | -108.3758 | -137.1495 | -151.1537 | -161.0432 | 58.6232 | 71.6011 | 57.3074 | 54.8421 | 48.5326 | -33.4168 | -38.5284 | -46.9368 | -109.0937 | -137.2958 | -151.9074 | -161.8011
|  | CHIPPENHAM BSP | HE |  |  |  |  | 64.5589 | 93.2474 | 81.8211 | 78.06 | 72.4316 | 13.3284 | 11.0137 | 7.5979 | -36.9389 | -50.7042 | -55.56 | -59.9432 | 54.3179 | 68.9158 | 55.3968 | 51.1579 | 44.7979 | -20.8505 | -23.6579 | -27.7474 | -79.4032 | -95.6632 | -103.8632 | -109.0021 | 59.6474 | 73.0284 | 59.4547 | 55.2042 | 48.8221 | -19.7242 | -22.3989 | -26.3516 | -77.6884 | -93.9558 | -102.3663 | -107.4979
|  | CHIPPENHAM BSP | FB |  |  |  |  | 65.9232 | 95.9937 | 94.5484 | 93.0042 | 83.3263 | 75.9474 | 76.0389 | 76.1663 | 74.4663 | 67.6653 | 67.3863 | 63.5042 | 54.9853 | 71.9842 | 70.3274 | 68.56 | 57.0432 | 50.8421 | 50.6158 | 50.4211 | 48.4747 | 40.66 | 39.5095 | 34.9747 | 61.1316 | 76.1053 | 74.4411 | 72.6684 | 61.1053 | 53.4474 | 53.3505 | 53.2905 | 51.3347 | 43.4937 | 42.6453 | 38.0916
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ 15716 93165 | NO | YES | 93.6832 | 109.2842 | 107.2958 | 104.5979 | 101.2547 | 99.5863 | 94.5895 | 59.4716 | 54.2789 | 46.0926 | 13.0074 | -8.1768 | -20.8926 | 102.2684 | 100.0821 | 97.0674 | 93.3737 | 91.7484 | 86.2547 | 44.7926 | 38.9779 | 29.6158 | -8.9326 | -33.6326 | -48.3084 | 99.7558 | 97.5537 | 94.5179 | 90.7968 | 89.0221 | 83.3021 | 41.3747 | 35.5137 | 26.0737 | -12.8758 | -37.8347 | -52.6558
|  | CHRISTCHURCH BSP | EE |  |  |  |  | 109.2842 | 107.2958 | 104.9916 | 102.5632 | 99.5863 | 96.6905 | 63.6305 | 60.7074 | 55.6347 | 42.0716 | 32.0789 | 20.8863 | 102.2684 | 100.0821 | 97.5379 | 94.9179 | 91.7484 | 88.6537 | 49.5916 | 46.4484 | 40.7726 | 24.9442 | 13.2695 | 0.11684 | 99.7558 | 97.5537 | 94.9905 | 92.3547 | 89.1747 | 86.0632 | 46.56 | 43.4021 | 37.5558 | 21.3589 | 9.5611 | -3.7389
|  | CHRISTCHURCH BSP | HT |  |  |  |  | 109.5589 | 107.3663 | 104.5979 | 101.2547 | 99.6716 | 94.5895 | 59.4716 | 54.2789 | 46.0926 | 13.0074 | -8.1768 | -20.8926 | 102.5832 | 100.1411 | 97.0674 | 93.3737 | 91.9295 | 86.2547 | 44.7926 | 38.9779 | 29.6158 | -8.9326 | -33.6326 | -48.3084 | 100.0705 | 97.6116 | 94.5179 | 90.7968 | 89.0221 | 83.3021 | 41.3747 | 35.5137 | 26.0737 | -12.8758 | -37.8347 | -52.6558
|  | CHRISTCHURCH BSP | HE |  |  |  |  | 110.5074 | 108.9684 | 107.0495 | 104.9284 | 102.1453 | 99.5337 | 66.8337 | 64.2916 | 59.5926 | 49.1347 | 41.1158 | 31.6105 | 103.6779 | 102.02 | 99.9284 | 97.6705 | 94.7347 | 91.9632 | 53.3379 | 50.6474 | 45.4179 | 32.9958 | 23.5095 | 12.2316 | 101.1789 | 99.5137 | 97.4084 | 95.14 | 92.1916 | 89.4105 | 50.3463 | 47.6453 | 42.2516 | 29.4705 | 19.8789 | 8.4684
|  | CHRISTCHURCH BSP | FB |  |  |  |  | 111.6137 | 110.5105 | 109.5211 | 108.5579 | 107.4979 | 106.4263 | 105.3695 | 74.1095 | 73.0337 | 68.7053 | 61.7589 | 52.8379 | 104.5 | 103.6442 | 102.5411 | 101.4832 | 100.3168 | 99.1379 | 97.9747 | 60.8221 | 59.6316 | 54.86 | 46.84 | 36.3337 | 102.0295 | 101.1411 | 100.0316 | 98.9653 | 97.7916 | 96.6053 | 95.4326 | 57.8474 | 56.6505 | 51.7211 | 43.4084 | 32.7832
IVER 132KV GSP | CIPPENHAM BSP | CIPPENHAM BSP | MINIMUM HEADROOM | SU 96266 79634 | NO | YES | 0 | 100.8168 | 100.5116 | 100.16 | 99.6716 | 99.0632 | 98.4326 | 97.7842 | 97.1474 | 95.2032 | 90.3789 | 87.6 | 85.0705 | 98.5326 | 98.2274 | 97.8716 | 97.34 | 96.7053 | 96.0105 | 94.5905 | 92.1695 | 89.8 | 84.3526 | 81.2484 | 78.4168 | 98.9358 | 98.6305 | 98.2789 | 97.7895 | 97.1821 | 96.5516 | 95.3558 | 92.9758 | 90.6053 | 85.1568 | 82.0516 | 79.2189
|  | CIPPENHAM BSP | EE |  |  |  |  | 100.8168 | 100.5116 | 100.1632 | 99.6937 | 99.0632 | 98.4453 | 97.8663 | 97.2737 | 96.6853 | 96.0747 | 94.2726 | 92.5895 | 98.5326 | 98.2274 | 97.8726 | 97.3768 | 96.7053 | 96.0568 | 95.4358 | 94.8189 | 93.7379 | 91.0421 | 88.8147 | 86.8674 | 98.9358 | 98.6305 | 98.2811 | 97.8126 | 97.1821 | 96.5642 | 95.9853 | 95.3916 | 94.4968 | 91.8474 | 89.6189 | 87.6705
|  | CIPPENHAM BSP | HT |  |  |  |  | 100.8295 | 100.54 | 100.16 | 99.6716 | 99.0821 | 98.4326 | 97.7842 | 97.1474 | 95.2032 | 90.3789 | 87.6 | 85.0705 | 98.5453 | 98.2558 | 97.8716 | 97.34 | 96.7084 | 96.0105 | 94.5905 | 92.1695 | 89.8 | 84.3526 | 81.2484 | 78.4168 | 98.9484 | 98.6589 | 98.2789 | 97.7895 | 97.2011 | 96.5516 | 95.3558 | 92.9758 | 90.6053 | 85.1568 | 82.0516 | 79.2189
|  | CIPPENHAM BSP | HE |  |  |  |  | 100.8695 | 100.5695 | 100.2263 | 99.7579 | 99.1211 | 98.5189 | 97.9316 | 97.3326 | 96.7453 | 96.7779 | 96.6863 | 96.1884 | 98.5853 | 98.2853 | 97.9421 | 97.4737 | 96.8232 | 96.1937 | 95.5726 | 94.9484 | 94.3432 | 93.8032 | 92.3337 | 91.0326 | 98.9884 | 98.6884 | 98.3453 | 97.8768 | 97.24 | 96.6379 | 96.0505 | 95.4516 | 94.8642 | 94.5632 | 93.1295 | 91.8389
|  | CIPPENHAM BSP | FB |  |  |  |  | 101.1 | 100.9495 | 100.8137 | 100.6611 | 100.4916 | 100.3211 | 100.1547 | 100 | 99.8347 | 99.2284 | 98.8884 | 98.6705 | 98.8158 | 98.6653 | 98.5295 | 98.3768 | 98.2074 | 98.0368 | 97.8526 | 97.6832 | 97.5042 | 96.8558 | 96.4516 | 95.4895 | 99.2189 | 99.0684 | 98.9326 | 98.78 | 98.6105 | 98.44 | 98.2737 | 98.1189 | 97.9537 | 97.3474 | 97.0074 | 96.2547
IVER 132KV GSP | CIPPENHAM B BSP | CIPPENHAM B BSP | MINIMUM HEADROOM | SU 96266 79634 | NO | YES | TBC | Generation Headroom Winter (MVA) 2032: 115.2; Generation Headroom Winter (MVA) 2033: 115.2; Generation Headroom Winter (MVA) 2034: 115.2; Generation Headroom Winter (MVA) 2035: 115.2; Generation Headroom Winter (MVA) 2040: 115.2; Generation Headroom Winter (MVA) 2045: 115.2; Generation Headroom Winter (MVA) 2050: 115.2 | [5 empty] | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | [5 empty] | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6
|  | CIPPENHAM B BSP | EE |  |  |  |  | Generation Headroom Winter (MVA) 2032: 115.2; Generation Headroom Winter (MVA) 2033: 115.2; Generation Headroom Winter (MVA) 2034: 115.2; Generation Headroom Winter (MVA) 2035: 115.2; Generation Headroom Winter (MVA) 2040: 115.2; Generation Headroom Winter (MVA) 2045: 115.2; Generation Headroom Winter (MVA) 2050: 115.2 | [5 empty] | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | [5 empty] | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6
|  | CIPPENHAM B BSP | HT |  |  |  |  | Generation Headroom Winter (MVA) 2032: 115.2; Generation Headroom Winter (MVA) 2033: 115.2; Generation Headroom Winter (MVA) 2034: 115.2; Generation Headroom Winter (MVA) 2035: 115.2; Generation Headroom Winter (MVA) 2040: 115.2; Generation Headroom Winter (MVA) 2045: 115.2; Generation Headroom Winter (MVA) 2050: 115.2 | [5 empty] | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | [5 empty] | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6
|  | CIPPENHAM B BSP | HE |  |  |  |  | Generation Headroom Winter (MVA) 2032: 115.2; Generation Headroom Winter (MVA) 2033: 115.2; Generation Headroom Winter (MVA) 2034: 115.2; Generation Headroom Winter (MVA) 2035: 115.2; Generation Headroom Winter (MVA) 2040: 115.2; Generation Headroom Winter (MVA) 2045: 115.2; Generation Headroom Winter (MVA) 2050: 115.2 | [5 empty] | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | [5 empty] | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6
|  | CIPPENHAM B BSP | FB |  |  |  |  | Generation Headroom Winter (MVA) 2032: 115.2; Generation Headroom Winter (MVA) 2033: 115.2; Generation Headroom Winter (MVA) 2034: 115.2; Generation Headroom Winter (MVA) 2035: 115.2; Generation Headroom Winter (MVA) 2040: 115.2; Generation Headroom Winter (MVA) 2045: 115.2; Generation Headroom Winter (MVA) 2050: 115.2 | [5 empty] | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | 109.8 | [5 empty] | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6
MINETY GSP | CIRENCESTER BSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP 02701 00368 | NO | YES | 127.2632 | 97.7537 | 89.5316 | 70.3116 | 29.8484 | 7.5979 | -12.0789 | -15.2168 | -18.5158 | -21.8347 | -45.3242 | -61.8442 | -67.7653 | 80.8579 | 71.2168 | 49.3632 | 2.7989 | -22.7337 | -45.6895 | -49.1779 | -52.8611 | -56.5726 | -83.7705 | -102.9411 | -109.6621 | 86.0642 | 76.3895 | 54.0358 | 6.6737 | -19.2768 | -42.1832 | -45.6653 | -49.3411 | -53.0453 | -80.1684 | -99.2842 | -105.9905
|  | CIRENCESTER BSP | EE |  |  |  |  | 97.7537 | 96.3126 | 70.3116 | 30.3968 | 8.9674 | -9.5642 | -11.6379 | -13.7253 | -15.7589 | -30.1116 | -40.1474 | -44.3789 | 80.8579 | 79.2779 | 49.3632 | 3.4084 | -21.1663 | -42.7842 | -45.06 | -47.3474 | -49.5705 | -66.2937 | -77.9789 | -82.8537 | 86.0642 | 84.4663 | 54.0358 | 7.2916 | -17.6958 | -39.2842 | -41.5579 | -43.8411 | -46.0632 | -62.7389 | -74.3895 | -79.2516
|  | CIRENCESTER BSP | HT |  |  |  |  | 98.0053 | 96.5747 | 70.3853 | 29.8484 | 7.5979 | -12.0789 | -15.2168 | -18.5158 | -21.8347 | -45.3242 | -61.8442 | -67.7653 | 81.1379 | 79.5663 | 49.4474 | 2.7989 | -22.7337 | -45.6895 | -49.1779 | -52.8611 | -56.5726 | -83.7705 | -102.9411 | -109.6621 | 86.3484 | 84.7589 | 54.1253 | 6.6737 | -19.2768 | -42.1832 | -45.6653 | -49.3411 | -53.0453 | -80.1684 | -99.2842 | -105.9905
|  | CIRENCESTER BSP | HE |  |  |  |  | 98.6274 | 97.5495 | 71.8453 | 32.1853 | 10.8568 | -7.4832 | -9.2368 | -10.9874 | -12.6968 | -24.9358 | -33.6905 | -36.8253 | 81.8253 | 80.6484 | 51.0674 | 5.4063 | -19.0579 | -40.4284 | -42.3295 | -44.2242 | -46.0747 | -60.4368 | -70.6937 | -74.3526 | 87.0453 | 85.8568 | 55.7642 | 9.3147 | -15.5579 | -36.9347 | -38.8316 | -40.7242 | -42.5716 | -56.8926 | -67.1168 | -70.7663
|  | CIRENCESTER BSP | FB |  |  |  |  | 110.6863 | 89.5316 | 74.1232 | 73.3789 | 72.5874 | 71.8189 | 71.0495 | 70.2789 | 69.48 | 65.8537 | 61.5316 | 58.8421 | 96.2316 | 71.2168 | 53.4695 | 52.6484 | 51.7789 | 50.9389 | 50.0926 | 49.2442 | 48.3684 | 44.3389 | 39.54 | 36.4895 | 101.8316 | 76.3895 | 58.3316 | 57.5032 | 56.6242 | 55.7737 | 54.9168 | 54.06 | 53.1716 | 49.0895 | 44.0789 | 40.9832
FAWLEY GSP | COWES BSP | COWES BSP | MINIMUM HEADROOM | SZ 50486 94250 | NO | YES | 15.7895 | 39.2232 | 38.1095 | 35.74 | 33.9168 | 32.4379 | 30.7432 | 29.0611 | 25.4621 | 23.4432 | 15.3579 | 26.3211 | 18.9705 | 29.2242 | 27.9989 | 25.3042 | 23.2958 | 21.7221 | 19.8958 | 18.0726 | 14.3189 | 11.7768 | 2.2126 | 14.5232 | 5.9274 | 30.4726 | 29.2495 | 26.5579 | 24.5516 | 22.9789 | 21.1558 | 19.3337 | 15.6495 | 13.0453 | 3.5011 | 15.7947 | 7.2147
|  | COWES BSP | EE |  |  |  |  | 39.2232 | 38.1095 | 35.74 | 34.2463 | 32.4379 | 30.7432 | 29.0611 | 25.4621 | 23.4432 | 105.1063 | 97.6642 | 88.6653 | 29.2242 | 27.9989 | 25.3042 | 23.6768 | 21.7221 | 19.8958 | 18.0726 | 14.3189 | 11.7768 | 113.1895 | 104.5442 | 94.0526 | 30.4726 | 29.2495 | 26.5579 | 24.9326 | 22.9789 | 21.1558 | 19.3337 | 15.6495 | 13.0453 | 102.7895 | 94.1421 | 83.6474
|  | COWES BSP | HT |  |  |  |  | 39.3979 | 38.3232 | 35.7705 | 33.9168 | 125.2263 | 122.8832 | 120.2832 | 112.4379 | 110.3274 | 84.0305 | 66.6684 | 57.0916 | 29.4263 | 28.2432 | 25.3432 | 23.2958 | 136.0695 | 133.4916 | 130.6105 | 121.5695 | 119.2579 | 88.7842 | 68.6453 | 57.6126 | 30.6758 | 29.4926 | 26.5979 | 24.5516 | 125.6747 | 123.0968 | 120.2147 | 111.1726 | 108.8611 | 78.3779 | 58.2316 | 47.1968
|  | COWES BSP | HE |  |  |  |  | 39.8147 | 38.9284 | 36.7621 | 35.4368 | 33.7379 | 32.1916 | 30.7316 | 26.6916 | 25.5505 | 15.3579 | 102.4895 | 94.3463 | 29.9042 | 28.9432 | 26.4853 | 25.0537 | 23.2263 | 21.5674 | 20.0063 | 15.4095 | 14.2221 | 2.2126 | 109.9811 | 100.4347 | 31.1505 | 30.1916 | 27.7379 | 26.3074 | 24.4821 | 22.8242 | 21.2632 | 16.6747 | 15.4874 | 3.5011 | 99.58 | 90.0305
|  | COWES BSP | FB |  |  |  |  | 44.0232 | 39.8263 | 39.2905 | 38.7116 | 38.0611 | 37.4242 | 36.9579 | 36.5126 | 36.0663 | 32.8916 | 26.3211 | 18.9705 | 35.1189 | 29.8916 | 29.2947 | 28.6526 | 27.9295 | 27.2232 | 26.7179 | 26.2337 | 25.7495 | 22.1695 | 14.5232 | 5.9274 | 36.3579 | 31.1379 | 30.5442 | 29.9032 | 29.1811 | 28.4747 | 27.9705 | 27.4853 | 27.0021 | 23.4274 | 15.7947 | 7.2147
COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | COWLEY LOCAL (RESERVE) BSP | MINIMUM HEADROOM | SP 56113 03074 | NO | YES | 68.2842 | 92.4568 | 90.6716 | 78.4547 | 75.9547 | 72.9863 | 68.54 | 54.6895 | 51.7211 | 47.9074 | 33.1947 | 23.2642 | 17.9947 | 83.4358 | 81.3663 | 66.7053 | 63.8158 | 60.3726 | 55.2695 | 39.6242 | 36.4389 | 32.7242 | 15.7421 | 2.7421 | -3.2926 | 85.8811 | 83.8116 | 69.1874 | 66.2968 | 62.8589 | 57.7484 | 42.1411 | 38.9516 | 35.4137 | 19.0432 | 5.3684 | -0.65684
|  | COWLEY LOCAL (RESERVE) BSP | EE |  |  |  |  | 92.6821 | 91.3716 | 80.1821 | 77.8316 | 75.1221 | 68.54 | 55.1495 | 52.3305 | 49.2211 | 40.4411 | 35.2747 | 31.1811 | 83.7284 | 82.2421 | 68.8211 | 66.1116 | 63.0063 | 55.2695 | 39.6242 | 36.4389 | 32.8958 | 24.1621 | 18.2558 | 13.5358 | 86.1705 | 84.68 | 71.2884 | 68.5768 | 65.4705 | 57.7484 | 42.1411 | 38.9516 | 35.4137 | 27.3579 | 21.4726 | 16.7516
|  | COWLEY LOCAL (RESERVE) BSP | HT |  |  |  |  | 92.4568 | 90.6716 | 78.4547 | 75.9547 | 72.9863 | 69.2726 | 54.6895 | 51.7211 | 47.9074 | 33.1947 | 23.2642 | 17.9947 | 83.4358 | 81.3663 | 66.7053 | 63.8158 | 60.3726 | 57.5305 | 40.4747 | 37.1 | 32.7242 | 15.7421 | 2.7421 | -3.2926 | 85.8811 | 83.8116 | 69.1874 | 66.2968 | 62.8589 | 60.7063 | 43.6979 | 40.3305 | 35.9663 | 19.0432 | 5.3684 | -0.65684
|  | COWLEY LOCAL (RESERVE) BSP | HE |  |  |  |  | 93.3695 | 92.4242 | 81.7821 | 79.9853 | 77.8242 | 71.8211 | 59.0495 | 56.8853 | 54.3463 | 43.2989 | 36.5779 | 32.3947 | 84.5211 | 83.4074 | 70.6063 | 68.5295 | 66.0526 | 58.9316 | 43.9863 | 41.5379 | 38.6484 | 24.9074 | 16.9884 | 12.0747 | 86.9726 | 85.8611 | 73.1 | 71.0274 | 68.5558 | 61.4537 | 46.5537 | 44.1105 | 41.2284 | 27.1874 | 19.2811 | 14.3821
|  | COWLEY LOCAL (RESERVE) BSP | FB |  |  |  |  | 94.0484 | 93.5211 | 92.9684 | 92.1947 | 91.3484 | 90.38 | 89.3874 | 88.3411 | 87.2274 | 81.62 | 76.7768 | 73.5274 | 85.3863 | 84.7063 | 84.0189 | 83.1137 | 82.1253 | 80.9895 | 79.8232 | 78.5916 | 77.2768 | 70.6211 | 64.8347 | 60.9484 | 87.8242 | 87.1579 | 86.4726 | 85.5684 | 84.5832 | 83.4505 | 82.2874 | 81.0579 | 79.7484 | 73.1105 | 67.3411 | 63.4653
COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL (MAIN) BSP | MINIMUM HEADROOM | SP 56113 03074 | NO | YES | 44.2105 | 65.5105 | 65.0242 | 64.4968 | 152.7495 | 145.9916 | 138.3916 | 129.7789 | 120.9021 | 112.3221 | 95.9589 | 88.74 | 82.8316 | 61.6295 | 61.1432 | 53.5 | 141.1053 | 133.4084 | 124.6947 | 114.7926 | 104.5821 | 94.7179 | 77.4505 | 69.2684 | 61.1495 | 61.8663 | 61.3789 | 57.3326 | 144.9747 | 137.3674 | 128.8232 | 119.12 | 109.1116 | 99.4432 | 82.6147 | 74.4032 | 66.1463
|  | COWLEY LOCAL (MAIN) BSP | EE |  |  |  |  | 65.5105 | 65.0242 | 64.4968 | 153.7768 | 151.4958 | 145.6558 | 139.0084 | 132.5537 | 126.7463 | 109.72 | 103.8495 | 101.6526 | 61.6295 | 61.1432 | 54.3421 | 142.6168 | 139.8063 | 133.1368 | 125.5084 | 118.1116 | 111.4768 | 93.2063 | 86.48 | 84.0137 | 61.8663 | 61.3789 | 58.1179 | 146.4537 | 143.6853 | 137.14 | 129.6632 | 122.4095 | 115.8979 | 98.12 | 91.5242 | 89.0989
|  | COWLEY LOCAL (MAIN) BSP | HT |  |  |  |  | 65.5632 | 65.1147 | 64.5295 | 152.7495 | 145.9916 | 138.3916 | 129.7789 | 120.9021 | 112.3221 | 95.9589 | 88.74 | 82.8316 | 61.6821 | 61.2337 | 53.5 | 141.1053 | 133.4084 | 124.6947 | 114.7926 | 104.5821 | 94.7179 | 77.4505 | 69.2684 | 61.1495 | 61.9189 | 61.4705 | 57.3326 | 144.9747 | 137.3674 | 128.8232 | 119.12 | 109.1116 | 99.4432 | 82.6147 | 74.4032 | 66.1463
|  | COWLEY LOCAL (MAIN) BSP | HE |  |  |  |  | 65.6463 | 65.1726 | 64.6432 | 153.9147 | 152.8095 | 146.9916 | 140.4158 | 134.0516 | 128.3411 | 111.0842 | 106.3884 | 105.2368 | 61.7653 | 61.2916 | 55.5874 | 144.0411 | 141.3274 | 134.6789 | 127.1432 | 119.8558 | 113.3316 | 93.2032 | 87.7568 | 86.44 | 62.0021 | 61.5284 | 59.2895 | 147.7979 | 145.1737 | 138.6516 | 131.2621 | 124.1158 | 117.7147 | 97.9705 | 92.6368 | 91.3474
|  | COWLEY LOCAL (MAIN) BSP | FB |  |  |  |  | 65.9537 | 65.6926 | 65.4568 | 155.1937 | 154.9021 | 154.6074 | 154.32 | 154.0537 | 152.2463 | 137.0516 | 133.0284 | 131.4579 | 62.0726 | 61.8116 | 61.5758 | 151.3126 | 151.0211 | 149.4979 | 146.5516 | 143.4232 | 140.5158 | 122.9263 | 118.3705 | 116.5968 | 62.3095 | 62.0484 | 61.8126 | 151.5495 | 151.2579 | 150.9632 | 150.1642 | 147.2326 | 144.4011 | 127.1768 | 122.6474 | 120.9042
FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU 78324 50817 | NO | YES | 0 | 112.1326 | 107.5874 | 105.9137 | 176.4221 | 173.0768 | 169.0853 | 164.9453 | 160.6937 | 156.4389 | 141.2832 | 134.9632 | 109.9074 | 90.9295 | 84.3232 | 82.1989 | 149.2821 | 145.6168 | 141.2032 | 136.68 | 132.0242 | 127.3632 | 110.4411 | 103.4916 | 74.8621 | 99.0474 | 89.9758 | 87.9211 | 155.5253 | 151.7937 | 147.3347 | 142.7589 | 138.0516 | 133.3368 | 116.1832 | 109.1505 | 80.0663
|  | COXMOOR WOOD BSP | EE |  |  |  |  | 112.1326 | 107.5874 | 106.0916 | 177.6537 | 175.3505 | 173.2179 | 171.0863 | 168.9274 | 166.7905 | 159.6179 | 155.26 | 141.7916 | 90.9295 | 84.3232 | 82.4768 | 150.7263 | 148.2968 | 146.06 | 143.8084 | 141.5253 | 139.2684 | 131.1042 | 126.2232 | 110.7863 | 99.0474 | 89.9758 | 88.1821 | 156.9947 | 154.5516 | 152.3032 | 150.0368 | 147.7411 | 145.4695 | 137.1526 | 132.1989 | 116.5032
|  | COXMOOR WOOD BSP | HT |  |  |  |  | 112.1705 | 107.8558 | 105.9137 | 176.4221 | 173.0768 | 169.0853 | 164.9453 | 160.6937 | 156.4389 | 141.2832 | 134.9632 | 109.9074 | 90.9674 | 84.7084 | 82.1989 | 149.2821 | 145.6168 | 141.2032 | 136.68 | 132.0242 | 127.3632 | 110.4411 | 103.4916 | 74.8621 | 99.0853 | 90.3442 | 87.9211 | 155.5253 | 151.7937 | 147.3347 | 142.7589 | 138.0516 | 133.3368 | 116.1832 | 109.1505 | 80.0663
|  | COXMOOR WOOD BSP | HE |  |  |  |  | 112.32 | 108.6811 | 107.4347 | 179.6337 | 177.5147 | 175.6147 | 173.7811 | 171.9074 | 170.0611 | 165.3758 | 162.5411 | 150.3811 | 91.1168 | 85.9316 | 84.4621 | 153.02 | 150.8053 | 148.8326 | 146.9326 | 144.9895 | 143.0726 | 137.5284 | 134.2905 | 120.2789 | 99.2347 | 91.5042 | 90.0705 | 159.3232 | 157.1 | 155.1189 | 153.2105 | 151.2611 | 149.3358 | 143.6621 | 140.3737 | 126.1179
|  | COXMOOR WOOD BSP | FB |  |  |  |  | 112.9021 | 110.0695 | 109.4684 | 198.8389 | 198.1379 | 197.4768 | 180.5105 | 179.8063 | 179.0663 | 175.8968 | 172.8211 | 170.2537 | 91.6989 | 87.5716 | 86.8063 | 176.02 | 175.1453 | 174.3347 | 153.8526 | 153.0853 | 152.2821 | 148.7979 | 145.3232 | 142.38 | 99.8168 | 93.1063 | 92.3663 | 181.6042 | 180.7558 | 179.9695 | 160.1537 | 159.38 | 158.5705 | 155.0495 | 151.4958 | 148.5116
IVER 132KV GSP | DENHAM B BSP | DENHAM B BSP | MINIMUM HEADROOM | TQ 01785 87618 | NO | YES | 0 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | DENHAM B BSP | EE | [7 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | DENHAM B BSP | HT | [7 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | DENHAM B BSP | HE | [7 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | DENHAM B BSP | FB | [7 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
IVER 132KV GSP | DENHAM BSP | DENHAM BSP | MINIMUM HEADROOM | TQ 01785 87618 | NO | YES | 40.0432 | 109.2747 | 108.7453 | 123.1189 | 122.2726 | 119.0242 | 110.3726 | 108.2095 | 105.9737 | 103.7463 | 85.4789 | 70.6147 | 62.4632 | 105.9053 | 105.3758 | 117.6189 | 115.6368 | 110.3189 | 98.7168 | 96.1432 | 93.46 | 90.7821 | 69.5611 | 52.3421 | 42.9884 | 102.8653 | 102.3358 | 115.4095 | 113.4537 | 108.2295 | 96.8611 | 94.3179 | 91.6684 | 89.0274 | 68.2168 | 51.4453 | 42.3263
|  | DENHAM BSP | EE |  |  |  |  | 109.2747 | 108.7453 | 123.1389 | 122.3284 | 121.1632 | 113.3011 | 111.8979 | 110.4632 | 109.0589 | 102.1221 | 95.78 | 88.2389 | 105.9053 | 105.3758 | 117.6653 | 116.3705 | 113.3032 | 102.7747 | 101.2095 | 99.6074 | 98.0432 | 88.6811 | 81.3379 | 72.6021 | 102.8653 | 102.3358 | 115.4558 | 114.1705 | 111.1463 | 100.8295 | 99.2768 | 97.6884 | 96.1368 | 86.9632 | 79.7674 | 71.2147
|  | DENHAM BSP | HT |  |  |  |  | 109.2884 | 108.7832 | 123.1189 | 122.2726 | 119.0242 | 110.3726 | 108.2095 | 105.9737 | 103.7463 | 85.4789 | 70.6147 | 62.4632 | 105.9189 | 105.4137 | 117.6189 | 115.6368 | 110.3189 | 98.7168 | 96.1432 | 93.46 | 90.7821 | 69.5611 | 52.3421 | 42.9884 | 102.8789 | 102.3737 | 115.4095 | 113.4537 | 108.2295 | 96.8611 | 94.3179 | 91.6684 | 89.0274 | 68.2168 | 51.4453 | 42.3263
|  | DENHAM BSP | HE |  |  |  |  | 109.3747 | 108.8705 | 123.3032 | 122.5179 | 121.46 | 114.7221 | 113.5042 | 112.2642 | 111.0474 | 105.7453 | 100.9937 | 94.3937 | 106.0053 | 105.5011 | 118.9653 | 117.8895 | 115.06 | 104.6453 | 103.3368 | 101.9968 | 100.6863 | 93.2705 | 87.1537 | 79.4484 | 102.9653 | 102.4611 | 116.7316 | 115.6611 | 112.8716 | 102.6653 | 101.3642 | 100.0326 | 98.7295 | 91.4779 | 85.4937 | 77.9568
|  | DENHAM BSP | FB |  |  |  |  | 109.7926 | 109.5537 | 124.3358 | 124.0947 | 123.8242 | 123.5526 | 123.2884 | 123.0421 | 122.78 | 121.8147 | 119.4705 | 114.1758 | 106.4232 | 106.1842 | 120.9663 | 120.7253 | 120.4547 | 120.1832 | 119.9189 | 119.6726 | 119.4105 | 117.4916 | 110.9295 | 103.6937 | 103.3832 | 103.1442 | 117.9263 | 117.6853 | 117.4147 | 117.1432 | 116.8789 | 116.6326 | 116.3705 | 115.2568 | 108.8284 | 101.7453
COWLEY GSP | DRAYTON BSP | DRAYTON BSP | MINIMUM HEADROOM | SU 46684 92706 | NO | YES | 88.4842 | 86.2905 | 82.1074 | 77.0158 | 79.7432 | 74.8568 | 67.9926 | 27.7137 | 21.6958 | 14.7516 | 14.9179 | 6.6958 | 1.6042 | 58.7663 | 54.0568 | 48.3368 | 49.9516 | 44.7379 | 37.0789 | -9.3821 | -16.0884 | -23.8758 | -12.3084 | -21.6105 | -27.3274 | 71.2011 | 66.4453 | 60.6674 | 62.9211 | 57.3442 | 49.6158 | 2.5863 | -4.1895 | -12.0558 | 5.1779 | -4.2495 | -10.0505
|  | DRAYTON BSP | EE |  |  |  |  | 86.8758 | 83.0305 | 78.3295 | 82.6779 | 76.5221 | 72.5168 | 27.7137 | 21.6958 | 14.7516 | 14.9179 | 6.6958 | 1.6042 | 59.4168 | 55.1168 | 49.8337 | 53.3179 | 46.5368 | 42.3484 | -9.3821 | -16.0884 | -23.8758 | -12.3084 | -21.6105 | -27.3274 | 71.9495 | 67.5989 | 62.2579 | 66.4021 | 59.4611 | 54.9211 | 2.5863 | -4.1895 | -12.0558 | 5.1779 | -4.2495 | -10.0505
|  | DRAYTON BSP | HT |  |  |  |  | 86.2905 | 82.1074 | 77.0158 | 79.7432 | 74.8568 | 67.9926 | 60.9842 | 82.6242 | 72.3463 | 23.9947 | 12.6695 | 4.2 | 58.7663 | 54.0568 | 48.3368 | 49.9516 | 44.7379 | 37.0789 | 29.2547 | 65.7811 | 54.1537 | -1.2421 | -13.9411 | -23.3737 | 71.2011 | 66.4453 | 60.6674 | 62.9211 | 57.3442 | 49.6158 | 41.7179 | 84.2411 | 72.4968 | 16.4853 | 3.66 | -5.8674
|  | DRAYTON BSP | HE |  |  |  |  | 88.2747 | 84.9821 | 80.8305 | 85.6663 | 81.2411 | 77.1053 | 32.4189 | 26.8474 | 20.2411 | 22.9495 | 16.7642 | 13.4874 | 60.9726 | 57.2863 | 52.62 | 56.6495 | 51.8663 | 47.5 | -4.1095 | -10.3116 | -17.72 | -3.4674 | -10.58 | -14.3347 | 73.5274 | 69.8095 | 65.0979 | 69.7989 | 64.8811 | 60.1642 | 7.9621 | 1.7042 | -5.7758 | 14.1811 | 6.9789 | 3.1768
|  | DRAYTON BSP | FB |  |  |  |  | 92.2916 | 87.4053 | 85.5937 | 92.9253 | 90.4979 | 88.9 | 86.1232 | 83.3389 | 80.9221 | 73.74 | 67.9779 | 64.8495 | 73.2032 | 59.8642 | 57.8274 | 64.6147 | 61.8747 | 60.1674 | 57.0211 | 53.8589 | 51.1305 | 43.24 | 36.7568 | 33.2253 | 83.7284 | 72.5347 | 70.4842 | 77.9674 | 75.2021 | 73.3453 | 70.1663 | 66.9737 | 64.2179 | 55.9368 | 49.2937 | 45.7284
EALING GSP | EALING BSP | EALING BSP | MINIMUM HEADROOM | TQ 18371 79475 | NO | YES | 0.014737 | 95.7232 | 95.3737 | 94.9211 | 94.3274 | 92.0137 | 87.8263 | 83.82 | 80.2474 | 76.2253 | 68.68 | 64.2937 | 60.7695 | 90.5211 | 90.1716 | 88.6021 | 86.2516 | 81.5853 | 76.8053 | 72.24 | 68.4274 | 63.8421 | 55.34 | 50.1789 | 46.2537 | 87.4684 | 86.4116 | 85.3042 | 84.0874 | 81.9611 | 79.7474 | 77.6011 | 74.4063 | 69.9442 | 61.6505 | 56.5126 | 52.6726
|  | EALING BSP | EE |  |  |  |  | 95.7263 | 95.3737 | 94.9663 | 94.4105 | 93.6126 | 90.9263 | 88.2779 | 85.6179 | 83.14 | 76.56 | 74.0558 | 71.8979 | 90.5242 | 90.1716 | 89.2337 | 86.8968 | 83.88 | 80.4253 | 77.44 | 74.4421 | 71.6558 | 64.2758 | 61.4221 | 58.9611 | 87.52 | 86.6463 | 85.5589 | 84.3695 | 82.8147 | 81.1063 | 79.5874 | 78.0537 | 76.5916 | 70.3526 | 67.5779 | 65.18
|  | EALING BSP | HT |  |  |  |  | 95.7232 | 95.3768 | 94.9211 | 94.3274 | 92.0137 | 87.8263 | 83.82 | 80.2474 | 76.2253 | 68.68 | 64.2937 | 60.7695 | 90.5211 | 90.1747 | 88.6021 | 86.2516 | 81.5853 | 76.8053 | 72.24 | 68.4274 | 63.8421 | 55.34 | 50.1789 | 46.2537 | 87.4684 | 86.4116 | 85.3042 | 84.0874 | 81.9611 | 79.7474 | 77.6011 | 74.4063 | 69.9442 | 61.6505 | 56.5126 | 52.6726
|  | EALING BSP | HE |  |  |  |  | 95.7579 | 95.3989 | 94.9895 | 94.4274 | 93.6621 | 91.9547 | 89.2968 | 86.7484 | 84.3768 | 79.5084 | 77.2463 | 75.9347 | 90.5558 | 90.1968 | 89.7874 | 88.1168 | 85.1611 | 81.6347 | 78.6411 | 75.7768 | 73.1189 | 67.6347 | 64.6274 | 63.1011 | 87.7116 | 86.9021 | 85.9105 | 84.8147 | 83.2705 | 81.5411 | 80.0053 | 78.5074 | 77.0863 | 73.6274 | 70.5642 | 69.0842
|  | EALING BSP | FB |  |  |  |  | 96.0042 | 95.7789 | 95.5789 | 95.3537 | 95.1032 | 94.8516 | 94.6063 | 94.3779 | 94.1326 | 90.3379 | 88.3716 | 86.8547 | 90.8021 | 90.5768 | 90.3768 | 90.1516 | 89.9011 | 89.6295 | 88.6663 | 87.4863 | 86.3884 | 79.6811 | 77.4579 | 75.7326 | 88.3179 | 87.8179 | 87.3958 | 86.8811 | 86.2916 | 85.6674 | 85.1253 | 84.5589 | 84.0105 | 81.0495 | 79.9295 | 79.1032
LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT BSP | MINIMUM HEADROOM | TQ 08394 73826 | NO | YES | 1.7895 | 96.3663 | 95.6463 | 93.9695 | 92.8832 | 91.4021 | 89.0537 | 85.1295 | 80.9558 | 76.7895 | 66.2126 | 60.7474 | 55.9905 | 94.1611 | 95.2211 | 88.2011 | 86.0884 | 82.4074 | 78.0737 | 73.0484 | 67.6674 | 62.2926 | 50.0432 | 43.9263 | 38.6032 | 83.2295 | 84.28 | 83.6095 | 82.4453 | 80.0989 | 77.3811 | 74.3263 | 70.0737 | 64.7674 | 52.6768 | 46.6326 | 41.3726
|  | EAST BEDFONT BSP | EE |  |  |  |  | 96.3758 | 95.6674 | 94.0705 | 93.0684 | 91.7337 | 90.3737 | 88.9305 | 86.0768 | 83.3674 | 76.1684 | 72.7432 | 69.7758 | 94.2611 | 95.4853 | 88.5737 | 86.6695 | 84.2653 | 81.4926 | 78.2537 | 74.6768 | 71.2926 | 61.4895 | 57.3747 | 53.9726 | 83.2295 | 84.28 | 83.6611 | 82.7874 | 81.0305 | 79.1168 | 77.0158 | 74.7358 | 72.5547 | 63.9758 | 59.9179 | 56.5653
|  | EAST BEDFONT BSP | HT |  |  |  |  | 96.3663 | 95.6463 | 93.9695 | 92.8832 | 91.4021 | 89.0537 | 85.1295 | 80.9558 | 76.7895 | 66.2126 | 60.7474 | 55.9905 | 94.1611 | 95.2211 | 88.2011 | 86.0884 | 82.4074 | 78.0737 | 73.0484 | 67.6674 | 62.2926 | 50.0432 | 43.9263 | 38.6032 | 83.2368 | 84.3042 | 83.6095 | 82.4453 | 80.0989 | 77.3811 | 74.3263 | 70.0737 | 64.7674 | 52.6768 | 46.6326 | 41.3726
|  | EAST BEDFONT BSP | HE |  |  |  |  | 96.5768 | 95.9232 | 94.3884 | 93.4232 | 92.1021 | 90.8 | 89.4547 | 87.7726 | 85.2032 | 79.8011 | 77.7505 | 76.0853 | 95.0516 | 96.5768 | 89.9358 | 88.2505 | 85.9821 | 83.3716 | 80.3516 | 76.9947 | 73.8137 | 66.2042 | 63.3947 | 61.1116 | 83.3232 | 84.3832 | 83.7863 | 82.9547 | 81.8074 | 80.1137 | 78.1105 | 75.9389 | 73.8547 | 68.6305 | 65.8653 | 63.6158
|  | EAST BEDFONT BSP | FB |  |  |  |  | 97.4863 | 96.7221 | 96.3937 | 96.02 | 95.6179 | 95.2021 | 94.76 | 94.3053 | 93.8232 | 91.7389 | 90.7421 | 89.0747 | 95.9663 | 98.0989 | 97.3558 | 96.4821 | 95.5863 | 94.6232 | 93.4474 | 92.0463 | 90.6105 | 83.2705 | 80.2674 | 77.9411 | 83.7274 | 85.0484 | 84.7979 | 84.5147 | 84.2053 | 83.8895 | 83.5821 | 83.3 | 82.9947 | 80.6463 | 78.8621 | 77.5211
LOVEDEAN GSP | FAREHAM (MAIN) BSP | FAREHAM (MAIN) BSP | MINIMUM HEADROOM | SU 56534 04031 | NO | YES | 33.7726 | 114.1611 | 113.1326 | 62.6495 | 59.4137 | 55.4042 | 49.2821 | 42.8611 | 35.9021 | 28.9295 | -3.9147 | -18.4284 | -28.1968 | 102.4442 | 101.52 | 36.6568 | 32.8884 | 28.9558 | 22.1126 | 14.8884 | 7.0295 | -0.84947 | -38.7389 | -55.3484 | -66.4274 | 105.1284 | 104.2042 | 38.3295 | 34.5684 | 31.0179 | 24.2021 | 16.9958 | 9.1537 | 1.2926 | -36.4905 | -53.0579 | -64.1074
|  | FAREHAM (MAIN) BSP | EE |  |  |  |  | 114.1611 | 113.1326 | 62.6495 | 59.4137 | 56.4158 | 52.0947 | 47.8305 | 42.5674 | 37.5979 | 14.8937 | 7.3074 | -0.54 | 102.4442 | 101.52 | 36.6568 | 32.8884 | 29.5737 | 24.5863 | 19.8632 | 13.9947 | 8.4411 | -18.0737 | -26.8021 | -35.8916 | 105.1284 | 104.2042 | 38.3295 | 34.5684 | 31.2558 | 26.28 | 21.5663 | 15.7189 | 10.1789 | -16.2589 | -24.9579 | -34.0232
|  | FAREHAM (MAIN) BSP | HT |  |  |  |  | 115.8368 | 114.7926 | 63.6379 | 59.4684 | 55.4042 | 49.2821 | 42.8611 | 35.9021 | 28.9295 | -3.9147 | -18.4284 | -28.1968 | 103.5926 | 102.7232 | 38.5768 | 33.6337 | 28.9558 | 22.1126 | 14.8884 | 7.0295 | -0.84947 | -38.7389 | -55.3484 | -66.4274 | 106.7747 | 105.9053 | 40.6221 | 35.6884 | 31.0179 | 24.2021 | 16.9958 | 9.1537 | 1.2926 | -36.4905 | -53.0579 | -64.1074
|  | FAREHAM (MAIN) BSP | HE |  |  |  |  | 114.4505 | 113.5105 | 64.9663 | 62.52 | 59.7358 | 56.8158 | 53.6684 | 50.0937 | 46.7105 | 30.2221 | 21.4484 | 12.9663 | 102.6495 | 101.7789 | 39.5463 | 36.7832 | 33.7337 | 30.4695 | 26.9011 | 22.7884 | 19.0558 | -0.39158 | -11.1116 | -21.0758 | 105.3337 | 104.4632 | 41.2116 | 38.4526 | 35.4063 | 32.1463 | 28.5863 | 24.4789 | 20.7526 | 1.3653 | -9.5263 | -19.4589
|  | FAREHAM (MAIN) BSP | FB |  |  |  |  | 115.1526 | 114.6579 | 114.2232 | 113.7253 | 113.1779 | 78.5537 | 77.3484 | 75.9347 | 74.5589 | 66.2347 | 58.6253 | 51.5705 | 103.3105 | 102.8758 | 102.4863 | 102.0484 | 101.5589 | 56.9589 | 55.5453 | 53.8516 | 52.2179 | 42.0042 | 32.4863 | 23.7968 | 105.9947 | 105.56 | 105.1705 | 104.7326 | 104.2432 | 58.5726 | 57.1611 | 55.4716 | 53.84 | 43.6526 | 34.1611 | 25.4958
LOVEDEAN GSP | FAREHAM (RESERVE) BSP | FAREHAM (RESERVE) BSP | MINIMUM HEADROOM | SU 56534 04031 | NO | YES | 52.5263 | 13.3716 | 11.9832 | 10.2442 | 8.0168 | 5.9989 | 3.4726 | 1.1063 | -1.0958 | -3.4589 | -9.0347 | -13.0453 | -16.7095 | 9.0653 | 7.4863 | 5.5263 | 3.0147 | 0.82 | -1.9989 | -4.6253 | -7.0568 | -9.6853 | -15.8779 | -20.3274 | -24.3779 | 10.2747 | 8.72 | 6.7895 | 4.3158 | 2.0916 | -0.68842 | -3.2789 | -5.68 | -8.2747 | -14.3863 | -18.7705 | -22.7632
|  | FAREHAM (RESERVE) BSP | EE |  |  |  |  | 13.3716 | 12.0874 | 10.4621 | 8.7989 | 6.8558 | 5.0653 | 3.2358 | 1.6337 | 0.16421 | -2.0989 | -4.8863 | -7.3011 | 9.0653 | 7.6263 | 5.7916 | 3.9505 | 1.8295 | -0.11579 | -2.1232 | -3.8505 | -5.4211 | -7.9495 | -11.1611 | -13.9484 | 10.2747 | 8.8558 | 7.0495 | 5.2295 | 3.1316 | 1.2074 | -0.77579 | -2.4863 | -4.0453 | -6.5895 | -9.7421 | -12.4832
|  | FAREHAM (RESERVE) BSP | HT |  |  |  |  | 13.5053 | 11.9832 | 10.2442 | 8.0168 | 5.9989 | 3.4726 | 1.1063 | -1.0958 | -3.4589 | -9.0347 | -13.0453 | -16.7095 | 9.2189 | 7.4863 | 5.5263 | 3.0147 | 0.82 | -1.9989 | -4.6253 | -7.0568 | -9.6853 | -15.8779 | -20.3274 | -24.3779 | 10.4253 | 8.72 | 6.7895 | 4.3158 | 2.0916 | -0.68842 | -3.2789 | -5.68 | -8.2747 | -14.3863 | -18.7705 | -22.7632
|  | FAREHAM (RESERVE) BSP | HE |  |  |  |  | 13.9389 | 12.96 | 11.6042 | 10.18 | 8.3411 | 6.8768 | 5.2305 | 3.7516 | 2.4084 | 1.8242 | 0.28947 | -1.0789 | 9.8042 | 8.6516 | 7.1347 | 5.5811 | 3.5884 | 2.0263 | 0.24105 | -1.3358 | -2.7558 | -3.4368 | -5.2463 | -6.8663 | 11 | 9.8621 | 8.3663 | 6.8284 | 4.8558 | 3.3074 | 1.5411 | -0.023158 | -1.4326 | -2.1526 | -3.9274 | -5.5126
|  | FAREHAM (RESERVE) BSP | FB |  |  |  |  | 14.3074 | 13.9653 | 13.3863 | 12.6968 | 11.9926 | 11.34 | 10.6137 | 9.9779 | 9.3832 | 7.3074 | 5.7937 | 4.1642 | 10.5053 | 9.7368 | 9.0874 | 8.3116 | 7.5253 | 6.8 | 5.9853 | 5.2747 | 4.6179 | 2.3316 | 0.66526 | -1.2189 | 11.6926 | 10.9347 | 10.2958 | 9.5316 | 8.7558 | 8.04 | 7.2368 | 6.5368 | 5.8874 | 3.6295 | 1.9316 | 0.083158
FLEET-BRAMLEY GSP | FERNHURST BSP | FERNHURST BSP | MINIMUM HEADROOM | SU 72730 39772 | NO | YES |  | 113.3821 | 111.4968 | 111.1453 | 137.4621 | 118.6137 | 113.7 | 109.1653 | 104.3411 | 69.8 | 48.8105 | 32.5316 | 22.2453 | 94.3421 | 92.1874 | 92.6074 | 118.4495 | 94.7463 | 88.9558 | 83.6505 | 77.9621 | 37.0368 | 12.9968 | -6.4032 | -18.1442 | 94.3905 | 93.4305 | 93.7989 | 122.3832 | 101.0526 | 95.5832 | 90.5579 | 85.1863 | 45.1221 | 21.0726 | 1.2937 | -10.4589
|  | FERNHURST BSP | EE |  |  |  |  | 113.3821 | 111.4968 | 111.1453 | 138.5084 | 121.1158 | 118.1116 | 115.5084 | 112.8716 | 82.4916 | 72.0263 | 63.7295 | 55.4526 | 94.3421 | 92.1874 | 92.6074 | 119.62 | 97.8253 | 94.4747 | 91.6116 | 88.7211 | 51.7768 | 39.6768 | 30.0947 | 20.4895 | 94.3905 | 93.4305 | 93.7989 | 122.3832 | 103.6284 | 100.4 | 97.6232 | 94.8189 | 59.7242 | 47.6053 | 38.0053 | 28.3884
|  | FERNHURST BSP | HT |  |  |  |  | 114.2568 | 114.1179 | 111.3211 | 137.4621 | 118.6137 | 113.7 | 109.1653 | 104.3411 | 69.8 | 48.8105 | 32.5316 | 22.2453 | 95.6147 | 96.2484 | 92.9853 | 118.4495 | 94.7463 | 88.9558 | 83.6505 | 77.9621 | 37.0368 | 12.9968 | -6.4032 | -18.1442 | 94.9442 | 95.5074 | 94.3474 | 122.8779 | 101.0526 | 95.5832 | 90.5579 | 85.1863 | 45.1221 | 21.0726 | 1.2937 | -10.4589
|  | FERNHURST BSP | HE |  |  |  |  | 114.5842 | 113.1874 | 113.2916 | 141.0432 | 123.9326 | 121.2705 | 119.1516 | 117.0232 | 87.3684 | 80.2179 | 70.1305 | 63.5558 | 95.7811 | 94.2189 | 95.1811 | 122.6547 | 101.1926 | 98.2347 | 95.9663 | 93.6916 | 57.3063 | 48.8558 | 35.6832 | 27.9537 | 94.7695 | 93.9611 | 94.5021 | 123.2305 | 106.8305 | 103.98 | 101.7653 | 99.5453 | 65.3053 | 56.8526 | 42.92 | 35.1895
|  | FERNHURST BSP | FB |  |  |  |  | 115.68 | 114.7253 | 113.9053 | 142.9632 | 141.8905 | 140.7895 | 125.7442 | 124.9505 | 123.9989 | 119.4105 | 115.5642 | 110.0253 | 97.0147 | 95.8958 | 94.9453 | 123.8474 | 122.5937 | 121.3074 | 102.1274 | 101.2221 | 100.1221 | 94.6737 | 90.5495 | 83.5979 | 95.3916 | 95.0042 | 94.6526 | 124.2589 | 123.8221 | 123.3789 | 107.1853 | 106.32 | 105.2747 | 100.1421 | 97.02 | 90.5853
LOVEDEAN GSP | FORT WIDLEY BSP | FORT WIDLEY BSP | MINIMUM HEADROOM | SU 65875 07686 | NO | YES | 0 | 68.0726 | 97.0737 | 95.7526 | 93.6968 | 91.3168 | 88.8168 | 86.3021 | 83.8274 | 81.38 | 60.2421 | 56.0558 | 52.1789 | 61.2063 | 89.8705 | 88.3821 | 86.0463 | 83.3484 | 80.5221 | 77.6758 | 74.8737 | 72.1042 | 47.1284 | 42.3453 | 37.9042 | 63.5526 | 92.2789 | 90.86 | 88.6411 | 86.0758 | 83.3842 | 80.6758 | 78.0095 | 75.3737 | 51.9895 | 47.2916 | 42.8347
|  | FORT WIDLEY BSP | EE |  |  |  |  | 68.0726 | 97.0737 | 95.8579 | 94.2516 | 92.4442 | 90.7695 | 89.1253 | 87.5684 | 86.0632 | 74.8516 | 71.9116 | 69.2642 | 61.2063 | 89.8705 | 88.5032 | 86.7 | 84.6989 | 82.8505 | 81.0274 | 79.3116 | 77.6547 | 64.3084 | 60.8747 | 57.7747 | 63.5526 | 92.2789 | 90.9758 | 89.2547 | 87.3316 | 85.5558 | 83.8063 | 82.1579 | 80.5632 | 68.1032 | 64.8737 | 61.9611
|  | FORT WIDLEY BSP | HT |  |  |  |  | 68.0853 | 97.2032 | 95.7526 | 93.6968 | 91.3168 | 88.8168 | 86.3021 | 83.8274 | 81.38 | 60.2421 | 56.0558 | 52.1789 | 61.3758 | 90.0189 | 88.3821 | 86.0463 | 83.3484 | 80.5221 | 77.6758 | 74.8737 | 72.1042 | 47.1284 | 42.3453 | 37.9042 | 63.7105 | 92.4211 | 90.86 | 88.6411 | 86.0758 | 83.3842 | 80.6758 | 78.0095 | 75.3737 | 51.9895 | 47.2916 | 42.8347
|  | FORT WIDLEY BSP | HE |  |  |  |  | 68.1747 | 97.7895 | 96.7726 | 95.3211 | 93.6232 | 92.0874 | 90.6074 | 89.2126 | 87.8653 | 77.9747 | 75.8653 | 73.9179 | 61.8253 | 90.7263 | 89.5705 | 87.9463 | 86.0737 | 84.3811 | 82.7516 | 81.2295 | 79.7611 | 67.8747 | 65.3632 | 63.0389 | 64.1337 | 93.0842 | 91.98 | 90.4274 | 88.6274 | 86.9989 | 85.4326 | 83.9621 | 82.5432 | 71.4863 | 69.1411 | 66.9737
|  | FORT WIDLEY BSP | FB |  |  |  |  | 68.4674 | 98.2789 | 98.1084 | 97.9168 | 97.2968 | 96.6547 | 96.0063 | 95.4147 | 94.8042 | 92.4253 | 90.1779 | 88.4663 | 62.7526 | 92.1421 | 91.5726 | 90.8632 | 90.1305 | 89.4032 | 88.6642 | 87.9947 | 87.3032 | 84.5989 | 81.9853 | 79.9853 | 65.0958 | 94.4379 | 93.8947 | 93.2211 | 92.5242 | 91.8326 | 91.1316 | 90.4947 | 89.8368 | 87.2663 | 84.8063 | 82.9253
MELKSHAM GSP | FROME BSP | FROME BSP | MINIMUM HEADROOM | ST 78803 48019 | NO | YES | 9.4737 | 79.6916 | 67.4968 | 26.4063 | 112.6558 | 107.7832 | 103.2842 | 98.8663 | 92.3316 | 69.7926 | 52.2379 | 33.6021 | 26.3432 | 55.9537 | 41.7095 | -1.2284 | 84.5979 | 79.1926 | 74.1937 | 69.2726 | 61.9042 | 35.5411 | 17.8853 | -5.3505 | -13.5211 | 59.0474 | 44.8337 | 1.92 | 87.74 | 82.3316 | 77.3337 | 72.4084 | 64.9168 | 38.6305 | 21.4179 | -2.6253 | -10.7947
|  | FROME BSP | EE |  |  |  |  | 79.6916 | 67.4968 | 26.4063 | 112.6558 | 107.7832 | 103.2842 | 98.8663 | 93.5968 | 75.3084 | 64.9821 | 55.7884 | 50.4411 | 55.9537 | 41.7095 | -1.2284 | 84.5979 | 79.1926 | 74.1937 | 69.2726 | 63.3695 | 42.0263 | 32.52 | 22.1916 | 16.0905 | 59.0474 | 44.8337 | 1.92 | 87.74 | 82.3316 | 77.3337 | 72.4084 | 66.5 | 45.2074 | 35.6653 | 25.4642 | 19.3474
|  | FROME BSP | HT |  |  |  |  | 80.1474 | 68.1379 | 27.0084 | 113.0179 | 109.5326 | 104.4305 | 99.4295 | 92.3316 | 69.7926 | 52.2379 | 33.6021 | 26.3432 | 56.4579 | 42.4211 | -0.55368 | 84.9989 | 81.2853 | 75.5747 | 69.9842 | 61.9042 | 35.5411 | 17.8853 | -5.3505 | -13.5211 | 59.5653 | 45.5537 | 2.6053 | 88.1589 | 84.2621 | 78.56 | 72.9821 | 64.9168 | 38.6305 | 21.4179 | -2.6253 | -10.7947
|  | FROME BSP | HE |  |  |  |  | 81.1842 | 69.6453 | 29.1832 | 115.9779 | 111.5305 | 107.4874 | 103.6884 | 99.1021 | 81.3747 | 76.2137 | 64.3958 | 61.0453 | 57.6179 | 44.1042 | 1.8589 | 88.2895 | 83.3505 | 78.8474 | 74.6263 | 69.4811 | 48.7726 | 44.4916 | 29.0379 | 25.1137 | 60.7316 | 47.2579 | 5.0484 | 91.4842 | 86.5537 | 82.06 | 77.8484 | 72.7116 | 52.0642 | 48.1147 | 31.9179 | 28.0021
|  | FROME BSP | FB |  |  |  |  | 110.1474 | 104.9368 | 47.6758 | 127.0137 | 125.3442 | 123.3547 | 121.7516 | 120.3484 | 118.8811 | 113.0811 | 109.7716 | 106.5379 | 97.9011 | 83.8011 | 22.6726 | 100.1253 | 98.2274 | 95.9537 | 94.1326 | 92.5442 | 90.8842 | 84.3032 | 80.6442 | 76.9158 | 100.9 | 87.6147 | 25.3937 | 102.8821 | 100.9884 | 98.7189 | 96.9042 | 95.3189 | 93.6611 | 87.0989 | 83.2621 | 79.5442
LOVEDEAN GSP | HAVANT BSP | HAVANT BSP | MINIMUM HEADROOM | SU 70625 05720 | NO | YES | 22.1063 | 119.0189 | 118.4611 | 117.8979 | 116.9326 | 113.2547 | 106.1674 | 99.2632 | 90.64 | 173.6547 | 154.9095 | 142.5811 | 131.7042 | 89.1284 | 88.4253 | 87.8063 | 87.0905 | 86.3253 | 82.6053 | 74.9084 | 65.18 | 147.3758 | 126.3063 | 112.4095 | 100.1411 | 101.5189 | 100.9726 | 100.48 | 99.9274 | 95.8589 | 87.96 | 80.2737 | 70.5568 | 152.7653 | 131.7242 | 117.8463 | 105.5958
|  | HAVANT BSP | EE |  |  |  |  | 129.72 | 128.5547 | 125.5979 | 121.7579 | 117.0389 | 112.3179 | 107.5926 | 102.2011 | 187.7379 | 176.1653 | 167.2968 | 159.8558 | 102.98 | 101.8147 | 100.5137 | 98.7642 | 94.9758 | 89.8232 | 84.6358 | 78.6758 | 163.8021 | 150.4674 | 140.2895 | 131.7274 | 113.4916 | 112.3263 | 109.6442 | 105.4347 | 100.3116 | 95.1632 | 89.9832 | 84.0253 | 169.1611 | 155.8495 | 145.6842 | 137.1379
|  | HAVANT BSP | HT |  |  |  |  | 129.7684 | 128.6705 | 125.0274 | 119.7621 | 113.2547 | 106.1674 | 99.2632 | 90.64 | 173.6547 | 154.9095 | 142.5811 | 131.7042 | 103.0284 | 101.9305 | 100.4863 | 97.78 | 90.5158 | 82.6053 | 74.9084 | 65.18 | 147.3758 | 126.3063 | 112.4095 | 100.1411 | 113.54 | 112.44 | 108.9789 | 103.1137 | 95.8589 | 87.96 | 80.2737 | 70.5568 | 152.7653 | 131.7242 | 117.8463 | 105.5958
|  | HAVANT BSP | HE |  |  |  |  | 129.9874 | 128.8947 | 127.6705 | 124.7947 | 120.3779 | 116.04 | 111.7537 | 106.8105 | 192.7968 | 185.0537 | 178.6442 | 173.2432 | 103.2474 | 102.1547 | 100.9305 | 99.2368 | 96.9021 | 94.0895 | 89.4211 | 83.9853 | 169.6337 | 160.4895 | 153.0053 | 146.6832 | 113.7589 | 112.6663 | 111.4421 | 108.9211 | 104.1453 | 99.4253 | 94.76 | 89.3295 | 174.9821 | 165.8558 | 158.3853 | 152.0768
|  | HAVANT BSP | FB |  |  |  |  | 119.0189 | 118.4611 | 117.8979 | 116.9326 | 115.2884 | 127.5863 | 125.7316 | 123.8453 | 212.0274 | 204.7821 | 198.1495 | 193.3011 | 89.1284 | 88.4253 | 87.8063 | 87.0905 | 86.3253 | 101.26 | 100.6611 | 100.1042 | 189.5084 | 182.1558 | 174.5663 | 168.9968 | 101.5189 | 100.9726 | 100.48 | 99.9274 | 98.2421 | 111.7716 | 109.7747 | 107.6568 | 195.6253 | 187.5 | 179.9211 | 174.3632
COWLEY GSP | HEADINGTON BSP | HEADINGTON BSP | MINIMUM HEADROOM | SP 54454 08145 | NO | YES | 19.9463 | 101.6589 | 98.9042 | 80.6126 | 77.0189 | 70.3979 | 34.4158 | 28.3074 | 23.0432 | 10.3705 | -9.0158 | -18.8874 | -25.3663 | 83.1916 | 81.9042 | 65.14 | 61.3863 | 53.7021 | 11.3189 | 4.2568 | -1.5358 | -16.3663 | -37.7232 | -49.1747 | -58.0832 | 89.4137 | 86.4421 | 66.9863 | 63.6726 | 56.4979 | 14.1916 | 7.1368 | 1.4158 | -13.3874 | -34.06 | -45.4832 | -55.1011
|  | HEADINGTON BSP | EE |  |  |  |  | 101.6589 | 98.9042 | 81.0789 | 77.9968 | 74.7684 | 42.1179 | 37.6642 | 32.9358 | 22.0916 | 8.5642 | 6.7621 | 5.3147 | 83.1916 | 81.9042 | 65.14 | 61.6095 | 57.9537 | 19.4947 | 14.36 | 8.9116 | -3.7737 | -18.7853 | -19.2463 | -20.8726 | 89.4137 | 86.4421 | 66.9863 | 63.6726 | 60.2263 | 22.1432 | 17.0158 | 11.5758 | -1.0874 | -15.8895 | -15.6537 | -17.28
|  | HEADINGTON BSP | HT |  |  |  |  | 103.2116 | 100.3032 | 80.6126 | 77.0189 | 70.3979 | 34.4158 | 28.3074 | 23.0432 | 10.3705 | -9.0158 | -18.8874 | -25.3663 | 86.6179 | 85.2926 | 65.5158 | 61.3863 | 53.7021 | 11.3189 | 4.2568 | -1.5358 | -16.3663 | -37.7232 | -49.1747 | -58.0832 | 92.3126 | 89.1705 | 67.6811 | 63.8116 | 56.4979 | 14.1916 | 7.1368 | 1.4158 | -13.3874 | -34.06 | -45.4832 | -55.1011
|  | HEADINGTON BSP | HE |  |  |  |  | 102.2432 | 99.7126 | 82.0653 | 79.1305 | 76.0021 | 43.4232 | 39.0516 | 34.5937 | 24.0347 | 10.3316 | 2.7211 | 2.0737 | 83.4916 | 82.3095 | 66.2705 | 62.9095 | 59.3674 | 20.9884 | 15.9547 | 10.8253 | -1.5232 | -17.7305 | -27.6168 | -28.36 | 90.0421 | 87.3105 | 68.0505 | 64.8968 | 61.5558 | 23.6432 | 18.6179 | 13.4958 | 1.1695 | -15.0063 | -25.0811 | -25.8221
|  | HEADINGTON BSP | FB |  |  |  |  | 103.5105 | 102.2137 | 100.9179 | 85.7716 | 84.5368 | 80.96 | 78.7916 | 77.0347 | 71.4442 | 64.6495 | 61.7053 | 60.6747 | 84.6758 | 83.5221 | 82.9253 | 70.5632 | 69.1432 | 64.9568 | 62.4337 | 60.3947 | 53.8274 | 45.9442 | 42.5463 | 41.3821 | 93.0053 | 90.0042 | 88.6042 | 72.0568 | 70.7284 | 66.8389 | 64.4884 | 62.5863 | 56.4253 | 48.5547 | 45.1621 | 43.9989
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU 84773 92191 | NO | YES | 0 | 114.9042 | 113.3779 | 111.2053 | 108.3821 | 105.0895 | 101.5568 | 97.9811 | 73.3642 | 61.6084 | 53.4295 | 48.9726 | 45.2084 | 80.2937 | 78.6505 | 76.2947 | 73.2337 | 69.6684 | 65.8474 | 61.9779 | 32.3316 | 20.3305 | 11.0579 | 6.0695 | 1.8453 | 78.3063 | 76.6505 | 74.2684 | 71.1779 | 67.5768 | 63.7211 | 59.8137 | 29.7179 | 17.3 | 7.8874 | 2.8305 | -1.4526
|  | HIGH WYCOMBE BSP | EE |  |  |  |  | 116.16 | 114.4979 | 112.7147 | 110.6884 | 108.3874 | 106.2979 | 104.7411 | 102.4105 | 61.6084 | 53.4295 | 48.9726 | 45.2084 | 81.7579 | 79.9653 | 78.0411 | 75.8842 | 73.4895 | 71.32 | 69.8789 | 67.4116 | 20.3305 | 11.0579 | 6.0695 | 1.8453 | 79.8011 | 77.9884 | 76.0463 | 73.8716 | 71.4653 | 69.2863 | 67.6653 | 65.1821 | 17.3 | 7.8874 | 2.8305 | -1.4526
|  | HIGH WYCOMBE BSP | HT |  |  |  |  | 114.9042 | 113.3779 | 111.2053 | 108.3821 | 105.0895 | 101.5568 | 97.9811 | 94.2032 | 90.4232 | 74.1589 | 67.9463 | 62.3579 | 80.2937 | 78.6505 | 76.2947 | 73.2337 | 69.6684 | 65.8474 | 61.9779 | 57.8695 | 53.7568 | 35.5505 | 28.7421 | 22.6084 | 78.3063 | 76.6505 | 74.2684 | 71.1779 | 67.5768 | 63.7211 | 59.8137 | 55.6621 | 51.5053 | 33.0505 | 26.1674 | 19.9642
|  | HIGH WYCOMBE BSP | HE |  |  |  |  | 116.5568 | 115.4316 | 114.0137 | 112.2947 | 110.1968 | 108.38 | 107.2105 | 105.2758 | 64.8695 | 59.7663 | 57.1768 | 55.0389 | 82.1621 | 80.8621 | 79.3547 | 77.5463 | 75.3863 | 73.52 | 72.5284 | 70.5253 | 23.9 | 17.9747 | 15.0295 | 12.5853 | 80.3821 | 79.0716 | 77.5537 | 75.7358 | 73.5674 | 71.6958 | 70.5326 | 68.5232 | 21.1011 | 15.0737 | 12.0821 | 9.5979
|  | HIGH WYCOMBE BSP | FB |  |  |  |  | 117.3147 | 116.6221 | 115.8926 | 115.0768 | 114.26 | 113.4737 | 112.6768 | 73.3642 | 72.5432 | 69.0853 | 66.6674 | 64.08 | 83.1779 | 82.1526 | 81.3126 | 80.4305 | 79.5505 | 78.7105 | 77.8558 | 32.3316 | 31.4505 | 27.6937 | 25.1663 | 22.2547 | 81.4063 | 80.3705 | 79.5211 | 78.6305 | 77.7463 | 76.8989 | 76.0368 | 29.7179 | 28.8305 | 25.0368 | 22.3011 | 19.3495
LOVEDEAN GSP | HUNSTON BSP | HUNSTON BSP | MINIMUM HEADROOM | SU 86946 02627 | NO | YES | 45.0053 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832
|  | HUNSTON BSP | EE |  |  |  |  | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832
|  | HUNSTON BSP | HT |  |  |  |  | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832
|  | HUNSTON BSP | HE |  |  |  |  | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832
|  | HUNSTON BSP | FB |  |  |  |  | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832 | 89.7832
FAWLEY GSP | LANGLEY BSP | LANGLEY BSP | MINIMUM HEADROOM | SU 45185 01376 | NO | YES | 0 | 47.4147 | 46.7105 | 46.0011 | 45.1432 | 43.54 | 41.8453 | 38.3632 | 36.6874 | 33.8726 | 29.4979 | 26.6821 | 24.3368 | 41.8579 | 41.0874 | 40.3284 | 39.4579 | 37.7032 | 35.8358 | 31.8516 | 30.0053 | 26.8084 | 21.9495 | 18.8105 | 16.2032 | 41.8242 | 41.0705 | 40.3242 | 39.4358 | 37.7084 | 35.8853 | 32.0295 | 30.2263 | 27.1274 | 22.3905 | 19.3326 | 16.7916
|  | LANGLEY BSP | EE |  |  |  |  | 47.4147 | 46.7168 | 46.0011 | 45.1789 | 44.9147 | 43.9747 | 42.1316 | 41.2 | 39.7411 | 37.5663 | 35.6663 | 34.2074 | 41.8579 | 41.1 | 40.3284 | 39.4579 | 39.3326 | 38.3526 | 36.2937 | 35.3179 | 33.7126 | 31.2242 | 29.0484 | 27.3811 | 41.8242 | 41.0811 | 40.3242 | 39.4663 | 39.2737 | 38.3032 | 36.2979 | 35.3337 | 33.7663 | 31.3589 | 29.2526 | 27.6358
|  | LANGLEY BSP | HT |  |  |  |  | 47.4895 | 46.7105 | 46.4474 | 45.1432 | 43.54 | 41.8453 | 38.3632 | 36.6874 | 33.8726 | 29.4979 | 26.6821 | 24.3368 | 41.9442 | 41.0874 | 40.9105 | 39.4726 | 37.7032 | 35.8358 | 31.8516 | 30.0053 | 26.8084 | 21.9495 | 18.8105 | 16.2032 | 41.9084 | 41.0705 | 40.84 | 39.4358 | 37.7084 | 35.8853 | 32.0295 | 30.2263 | 27.1274 | 22.3905 | 19.3326 | 16.7916
|  | LANGLEY BSP | HE |  |  |  |  | 47.8653 | 47.3421 | 46.7842 | 46.0895 | 45.9074 | 45.0832 | 43.3589 | 42.5495 | 41.2147 | 40.1074 | 38.8916 | 38.0053 | 42.38 | 41.8253 | 41.2368 | 40.5126 | 40.4863 | 39.6358 | 37.7179 | 36.8853 | 35.4274 | 34.1032 | 32.6811 | 31.6432 | 42.2568 | 41.7821 | 41.2011 | 40.4842 | 40.3853 | 39.5432 | 37.6747 | 36.8474 | 35.42 | 34.1516 | 32.7821 | 31.7821
|  | LANGLEY BSP | FB |  |  |  |  | 48.32 | 47.9347 | 47.6432 | 47.3326 | 47.0063 | 46.6747 | 46.3537 | 46.0463 | 46.4284 | 45.1 | 43.4368 | 42.4211 | 42.8653 | 42.4411 | 42.1221 | 41.7853 | 41.4326 | 41.0737 | 40.7274 | 40.3937 | 40.9305 | 39.4811 | 37.5779 | 36.4179 | 42.54 | 42.3758 | 42.08 | 41.7495 | 41.4032 | 41.0526 | 40.7116 | 40.3842 | 40.8505 | 39.4305 | 37.5884 | 36.4663
IVER 132KV GSP | LONGFORD BSP | LONGFORD BSP | MINIMUM HEADROOM | TQ 03910 76751 | NO | YES | 2 | 44.58 | 74.5232 | 74.4705 | 74.4137 | 74.3516 | 74.2863 | 74.2253 | 74.1674 | 74.1053 | 73.8789 | 73.7589 | 73.6789 | 45.98 | 75.8358 | 75.7526 | 75.6463 | 75.5326 | 75.4126 | 75.2737 | 75.1326 | 75.0337 | 74.6316 | 70.7989 | 70.2358 | 34.9547 | 64.8379 | 64.7632 | 64.6726 | 64.5747 | 64.4716 | 64.3558 | 64.24 | 64.1526 | 63.8042 | 62.2611 | 62.0158
|  | LONGFORD BSP | EE |  |  |  |  | 70.2053 | 100.0905 | 99.9547 | 99.7737 | 99.5358 | 99.3011 | 99.0811 | 98.8558 | 98.6326 | 98.2021 | 130.4253 | 129.7042 | 62.4874 | 92.3726 | 92.2368 | 92.0558 | 91.8179 | 91.5832 | 91.2337 | 90.6442 | 90.2432 | 84.1537 | 116.1537 | 115.3305 | 61.0189 | 90.9042 | 90.7684 | 90.5874 | 90.3495 | 90.1147 | 89.5884 | 89.0505 | 88.6758 | 83.2095 | 115.3295 | 114.56
|  | LONGFORD BSP | HT |  |  |  |  | 70.2084 | 100.0989 | 99.9516 | 99.7642 | 99.5379 | 99.2916 | 99.0432 | 98.8 | 98.5579 | 95.6558 | 128.1832 | 127.1432 | 62.4905 | 92.3811 | 92.2337 | 92.0463 | 91.8211 | 91.2179 | 90.4389 | 89.5789 | 88.88 | 81.26 | 113.6516 | 112.4926 | 61.0221 | 90.9126 | 90.7653 | 90.5779 | 90.2179 | 89.6053 | 88.9042 | 88.1347 | 87.5032 | 80.5021 | 112.9653 | 111.8695
|  | LONGFORD BSP | HE |  |  |  |  | 70.2232 | 100.1126 | 99.9811 | 99.8042 | 99.5621 | 99.3358 | 99.1126 | 98.8863 | 98.6632 | 98.6968 | 131.8789 | 131.4284 | 62.5053 | 92.3947 | 92.2632 | 92.0863 | 91.8442 | 91.6179 | 91.3947 | 91.1684 | 90.9095 | 85.4568 | 117.7832 | 117.2611 | 61.0368 | 90.9263 | 90.7947 | 90.6179 | 90.3758 | 90.1495 | 89.9263 | 89.5484 | 89.2505 | 84.4305 | 116.8547 | 116.3705
|  | LONGFORD BSP | FB |  |  |  |  | 44.58 | 74.5232 | 74.4705 | 74.4137 | 74.3516 | 74.2863 | 74.2253 | 74.1674 | 74.1053 | 73.8789 | 73.7589 | 73.6789 | 45.98 | 75.8358 | 75.7526 | 75.6463 | 75.5326 | 75.4126 | 75.2737 | 75.1326 | 75.0337 | 74.6316 | 70.7989 | 70.2358 | 34.9547 | 64.8379 | 64.7632 | 64.6726 | 64.5747 | 64.4716 | 64.3558 | 64.24 | 64.1526 | 63.8042 | 62.2611 | 62.0158
AMERSHAM GSP | LOUDWATER BSP | LOUDWATER BSP | MINIMUM HEADROOM | SU 90644 91247 | NO | YES | 1.0516 | 100.5221 | 98.2284 | 94.9853 | 92.1811 | 89.0063 | 85.6316 | 82.4189 | 79.2042 | 75.9768 | 68.22 | 63.3221 | 59.0158 | 96.9084 | 94.3695 | 90.7484 | 87.6895 | 84.24 | 80.58 | 77.1063 | 73.6221 | 70.1263 | 61.7116 | 56.3863 | 51.7042 | 51.9326 | 49.4032 | 45.5968 | 42.4158 | 38.8305 | 35.0295 | 31.4274 | 27.8137 | 24.1853 | 15.4526 | 9.9168 | 5.0537
|  | LOUDWATER BSP | EE |  |  |  |  | 100.5221 | 98.2284 | 94.9853 | 92.6053 | 90.1526 | 87.8347 | 85.7221 | 83.7168 | 81.7516 | 78.0242 | 74.8663 | 72.2221 | 96.9084 | 94.3695 | 90.7484 | 88.1716 | 85.5726 | 83.1274 | 80.9053 | 78.8074 | 76.7558 | 72.5895 | 69.0537 | 66.0832 | 51.9326 | 49.4032 | 45.5968 | 42.9242 | 40.2526 | 37.7442 | 35.4705 | 33.3305 | 31.2368 | 26.8526 | 23.1347 | 20.0105
|  | LOUDWATER BSP | HT |  |  |  |  | 100.7779 | 98.5979 | 95.0947 | 92.1811 | 89.0063 | 85.6316 | 82.4189 | 79.2042 | 75.9768 | 68.22 | 63.3221 | 59.0158 | 97.1989 | 94.7863 | 90.8779 | 87.6895 | 84.24 | 80.58 | 77.1063 | 73.6221 | 70.1263 | 61.7116 | 56.3863 | 51.7042 | 51.9568 | 49.8442 | 45.7368 | 42.4158 | 38.8305 | 35.0295 | 31.4274 | 27.8137 | 24.1853 | 15.4526 | 9.9168 | 5.0537
|  | LOUDWATER BSP | HE |  |  |  |  | 101.3968 | 99.4295 | 96.4726 | 94.3242 | 92.0253 | 89.9063 | 88.0253 | 86.2516 | 84.5147 | 82.8737 | 81.0516 | 79.5284 | 97.8989 | 95.7358 | 92.4421 | 90.1347 | 87.7095 | 85.4863 | 83.5337 | 81.7063 | 79.9179 | 78.0063 | 75.9232 | 74.1747 | 52.0674 | 50.8505 | 47.3947 | 45.0074 | 42.5211 | 40.2495 | 38.26 | 36.4063 | 34.5937 | 32.5495 | 30.3379 | 28.48
|  | LOUDWATER BSP | FB |  |  |  |  | 102.7 | 101.5074 | 100.6011 | 99.68 | 98.8063 | 97.9663 | 97.2274 | 96.5611 | 95.88 | 92.9926 | 90.5568 | 88.6337 | 99.3168 | 97.9905 | 96.9874 | 95.9779 | 95.0284 | 94.1147 | 93.3211 | 92.6032 | 91.8726 | 88.7484 | 86.0495 | 83.8958 | 52.6537 | 52.3074 | 51.9947 | 51.0895 | 50.1021 | 49.1537 | 48.3316 | 47.5895 | 46.8368 | 43.5958 | 40.7663 | 38.5021
MANNINGTON GSP | LYTCHETT BSP | LYTCHETT BSP | MINIMUM HEADROOM | SY 97796 94214 | NO | YES | 84.42 | 49.2053 | 77.7389 | 75.8368 | 73.2316 | 70.8074 | 67.1926 | 63.6389 | 59.9337 | 54.9695 | -2.6947 | -39.2147 | -63.1074 | 35.1842 | 63.5947 | 61.5116 | 58.6642 | 56.1147 | 52.1505 | 48.2558 | 44.1821 | 38.6432 | -28.6326 | -71.2505 | -99.0853 | 34.8347 | 63.2589 | 61.1968 | 58.3737 | 55.7726 | 51.8453 | 47.9884 | 43.9526 | 38.4737 | -27.0032 | -69.0695 | -96.8316
|  | LYTCHETT BSP | EE |  |  |  |  | 49.2053 | 77.7389 | 76.1768 | 74.3726 | 72.0147 | 69.9568 | 67.8937 | 65.8116 | 63.1389 | 38.0979 | 23.4516 | 2.3063 | 35.1842 | 63.5947 | 61.9074 | 59.9768 | 57.4684 | 55.2979 | 53.1 | 50.8853 | 47.9832 | 18.8442 | 1.7537 | -23.0137 | 34.8347 | 63.2589 | 61.5832 | 59.6674 | 57.1768 | 55.0158 | 52.8326 | 50.6305 | 47.7516 | 19.2232 | 2.5905 | -21.4979
|  | LYTCHETT BSP | HT |  |  |  |  | 49.4042 | 77.8284 | 75.8368 | 73.2316 | 70.8074 | 67.1926 | 63.6389 | 59.9337 | 54.9695 | -2.6947 | -39.2147 | -63.1074 | 35.4074 | 63.6832 | 61.5116 | 58.6642 | 56.1147 | 52.1505 | 48.2558 | 44.1821 | 38.6432 | -28.6326 | -71.2505 | -99.0853 | 35.0568 | 63.3484 | 61.1968 | 58.3737 | 55.7726 | 51.8453 | 47.9884 | 43.9526 | 38.4737 | -27.0032 | -69.0695 | -96.8316
|  | LYTCHETT BSP | HE |  |  |  |  | 50.1358 | 79.0305 | 77.7726 | 76.2284 | 74.0463 | 72.2232 | 70.4737 | 68.7063 | 66.3474 | 43.6547 | 30.4453 | 10.5189 | 36.2305 | 65.0516 | 63.7084 | 62.0737 | 59.7663 | 57.8537 | 56.0211 | 54.1674 | 51.6274 | 25.1253 | 9.62 | -13.8021 | 35.8716 | 64.7011 | 63.3653 | 61.7411 | 59.4463 | 57.5432 | 55.7189 | 53.8747 | 51.3526 | 25.3705 | 10.2958 | -12.4705
|  | LYTCHETT BSP | FB |  |  |  |  | 59.9137 | 80.2505 | 79.6168 | 78.9368 | 78.1295 | 77.3947 | 76.6747 | 75.9737 | 75.2516 | 69.5232 | 56.6747 | 41.2168 | 47.9989 | 66.3368 | 65.6453 | 64.9074 | 64.0253 | 63.2295 | 62.4495 | 61.6853 | 60.9021 | 54.4526 | 39.6368 | 21.5242 | 47.4726 | 65.9779 | 65.2947 | 64.56 | 63.6874 | 62.8979 | 62.1232 | 61.3663 | 60.5895 | 54.2179 | 39.6032 | 21.9863
FLEET-BRAMLEY GSP | MAIDENHEAD BSP | MAIDENHEAD BSP | MINIMUM HEADROOM | SU 86592 79883 | NO | YES | 19.4737 | 111.0642 | 101.5337 | 99.2832 | 95.2611 | 90.4232 | 84.9253 | 79.9316 | 75.6253 | 71.4895 | 55.8021 | 50.7053 | 46.1011 | 103.14 | 90.1674 | 87.6 | 82.9516 | 77.3579 | 70.9937 | 65.2379 | 60.3032 | 55.5758 | 37.2516 | 31.4684 | 26.2379 | 106.2063 | 91.6 | 89.0326 | 84.3947 | 78.8084 | 72.4526 | 66.7053 | 61.7779 | 57.0558 | 38.7632 | 32.9905 | 27.7642
|  | MAIDENHEAD BSP | EE |  |  |  |  | 111.0642 | 101.5337 | 99.2832 | 95.3389 | 90.5589 | 86.2084 | 82.8737 | 80.76 | 78.6905 | 67.3305 | 63.7263 | 60.6874 | 103.14 | 90.1674 | 87.6 | 83.0337 | 77.5263 | 72.5305 | 68.7463 | 66.4379 | 64.1842 | 50.6379 | 46.4526 | 42.8989 | 106.2063 | 91.6 | 89.0326 | 84.4737 | 78.9716 | 73.9863 | 70.2063 | 67.9 | 65.6495 | 52.1263 | 47.9516 | 44.4042
|  | MAIDENHEAD BSP | HT |  |  |  |  | 111.0958 | 101.8432 | 99.3389 | 95.2611 | 90.4232 | 84.9253 | 79.9316 | 75.6253 | 71.4895 | 55.8021 | 50.7053 | 46.1011 | 103.1716 | 90.5305 | 87.6695 | 82.9516 | 77.3579 | 70.9937 | 65.2379 | 60.3032 | 55.5758 | 37.2516 | 31.4684 | 26.2379 | 106.2379 | 91.9621 | 89.1021 | 84.3947 | 78.8084 | 72.4526 | 66.7053 | 61.7779 | 57.0558 | 38.7632 | 32.9905 | 27.7642
|  | MAIDENHEAD BSP | HE |  |  |  |  | 111.2095 | 102.6632 | 100.6905 | 96.9863 | 92.5263 | 88.1179 | 84.9832 | 83.0947 | 81.3432 | 71.7 | 69.2316 | 67.1863 | 103.2853 | 91.4979 | 89.2621 | 84.9811 | 79.8611 | 74.7884 | 71.2453 | 69.2116 | 67.3389 | 55.6853 | 52.7432 | 50.2979 | 106.3516 | 92.9253 | 90.6926 | 86.42 | 81.3053 | 76.2411 | 72.7021 | 70.6695 | 68.8 | 57.1684 | 54.2305 | 51.7905
|  | MAIDENHEAD BSP | FB |  |  |  |  | 111.6642 | 111.3716 | 103.3189 | 101.7432 | 99.94 | 98.0737 | 96.6832 | 96.0295 | 95.2905 | 91.8284 | 84.9063 | 82.8179 | 103.74 | 103.4474 | 92.1874 | 90.3453 | 88.2337 | 86.0495 | 84.4379 | 83.7126 | 82.8863 | 78.9495 | 70.7253 | 68.2916 | 106.8063 | 106.5137 | 93.6168 | 91.7768 | 89.6684 | 87.4895 | 85.8779 | 85.1537 | 84.3295 | 80.3968 | 72.1874 | 69.7589
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON BSP | MINIMUM HEADROOM | SU 07523 05221 | NO | YES | 0 | 141.1905 | 138.4347 | 130.6589 | 125.4589 | 119.1937 | 112.4884 | 105.9063 | 99.2147 | 92.54 | 45.6221 | 0.098947 | -13.7337 | 127.0074 | 123.9495 | 115.0726 | 109.2821 | 102.3074 | 94.8537 | 87.54 | 80.0905 | 72.6484 | 19.0747 | -34.3642 | -50.1105 | 129.0421 | 125.9853 | 117.1042 | 111.3137 | 104.3368 | 96.8811 | 89.5642 | 82.1147 | 74.6716 | 21.3853 | -32.3642 | -48.1126
|  | MANNINGTON BSP | EE |  |  |  |  | 141.1905 | 138.4358 | 131.3326 | 127.6284 | 123.1579 | 118.9347 | 114.7347 | 110.5663 | 106.5232 | 82.1168 | 61.3947 | 48.3968 | 127.0074 | 123.9705 | 115.8526 | 111.7979 | 106.9579 | 102.3821 | 97.8042 | 93.2716 | 88.8789 | 60.4779 | 36.9495 | 21.3095 | 129.0421 | 126.0063 | 117.8821 | 113.8295 | 108.9884 | 104.4126 | 99.8337 | 95.2979 | 90.9053 | 62.4968 | 39.2621 | 23.3253
|  | MANNINGTON BSP | HT |  |  |  |  | 141.4926 | 138.4347 | 130.6589 | 125.4589 | 119.1937 | 112.4884 | 105.9063 | 99.2147 | 92.54 | 45.6221 | 0.098947 | -13.7337 | 127.3505 | 123.9495 | 115.0726 | 109.2821 | 102.3074 | 94.8537 | 87.54 | 80.0905 | 72.6484 | 19.0747 | -34.3642 | -50.1105 | 129.3874 | 125.9853 | 117.1042 | 111.3137 | 104.3368 | 96.8811 | 89.5642 | 82.1147 | 74.6716 | 21.3853 | -32.3642 | -48.1126
|  | MANNINGTON BSP | HE |  |  |  |  | 142.7284 | 140.5611 | 133.9768 | 130.6926 | 126.5347 | 122.7021 | 119.0042 | 115.3389 | 111.7895 | 91.1242 | 70.4768 | 60.8832 | 128.7516 | 126.3947 | 118.8674 | 115.2958 | 110.8116 | 106.6705 | 102.6789 | 98.7347 | 94.9116 | 70.6232 | 46.1611 | 34.9379 | 130.7895 | 128.4305 | 120.9021 | 117.3305 | 112.8432 | 108.7042 | 104.7105 | 100.7663 | 96.9421 | 72.6442 | 48.0316 | 36.8042
|  | MANNINGTON BSP | FB |  |  |  |  | 144.2084 | 142.7705 | 141.3389 | 139.8642 | 138.3074 | 136.7274 | 135.1474 | 133.5905 | 131.98 | 124.8895 | 115.4989 | 106.5874 | 130.3547 | 128.7526 | 127.1516 | 125.5063 | 123.7779 | 122.0242 | 120.26 | 118.5242 | 116.7274 | 108.7526 | 97.9274 | 87.5863 | 132.3232 | 130.7895 | 129.1895 | 127.5432 | 125.8137 | 124.06 | 122.2947 | 120.5589 | 118.7611 | 110.7853 | 99.9526 | 89.6105
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU 47559 12003 | NO | YES | 40.4368 | 197.6663 | 194.5011 | 190.1 | 185.5726 | 181.9474 | 169.3432 | 164.8347 | 159.7779 | 155.7663 | 130.3874 | 116.2568 | 105.2463 | 172.0442 | 168.5853 | 163.7105 | 158.6263 | 154.8747 | 140.5895 | 135.7758 | 130.3253 | 126.1021 | 98.36 | 82.5042 | 70.2168 | 181.7011 | 178.2684 | 173.4379 | 168.4653 | 164.7242 | 150.5895 | 145.8042 | 140.3874 | 136.1811 | 107.4011 | 91.54 | 79.2516
|  | NETLEY COMMON BSP | EE |  |  |  |  | 197.6663 | 194.5011 | 190.1232 | 186.86 | 181.9474 | 169.3432 | 164.8347 | 159.7779 | 155.7663 | 155.2284 | 145.7842 | 138.4853 | 172.0442 | 168.5853 | 163.7358 | 160.12 | 154.8747 | 140.5895 | 135.7758 | 130.3253 | 126.1021 | 126.5358 | 115.7379 | 107.3937 | 181.7011 | 178.2684 | 173.46 | 169.9411 | 164.7242 | 150.5895 | 145.8042 | 140.3874 | 136.1811 | 135.4821 | 124.7821 | 116.4347
|  | NETLEY COMMON BSP | HT |  |  |  |  | 198.0874 | 194.9674 | 190.1 | 185.5726 | 192.3989 | 179.0074 | 173.2926 | 164.9789 | 158.04 | 130.3874 | 116.2568 | 105.2463 | 172.5295 | 169.1084 | 163.7105 | 158.6263 | 167.8642 | 152.6768 | 146.5021 | 137.2663 | 129.6389 | 98.36 | 82.5042 | 70.2168 | 182.1811 | 178.7853 | 173.4379 | 168.4653 | 176.4337 | 161.4126 | 155.2768 | 146.1232 | 138.56 | 107.4011 | 91.54 | 79.2516
|  | NETLEY COMMON BSP | HE |  |  |  |  | 199.4442 | 196.9516 | 193.1621 | 190.3779 | 185.7768 | 173.5842 | 169.5632 | 165.0295 | 161.5232 | 165.8 | 159.4979 | 154.5979 | 174.0884 | 171.4105 | 167.2463 | 164.1884 | 159.3084 | 145.4874 | 141.2537 | 136.4168 | 132.7821 | 138.5021 | 131.1726 | 125.4663 | 183.2168 | 181.0589 | 176.9305 | 173.9611 | 169.1063 | 155.4295 | 151.2158 | 146.4074 | 142.7842 | 147.3242 | 140.0874 | 134.4526
|  | NETLEY COMMON BSP | FB |  |  |  |  | 201.3947 | 199.6611 | 197.4253 | 196.6674 | 194.9284 | 193.1832 | 174.5358 | 173.04 | 171.6432 | 164.9768 | 172.6842 | 167.6884 | 176.1821 | 174.2632 | 171.7453 | 170.7979 | 168.8916 | 166.9768 | 145.2116 | 143.5758 | 142.0684 | 134.7168 | 144.7653 | 139.0674 | 184.3505 | 183.6747 | 181.4084 | 180.5411 | 178.6484 | 176.7495 | 155.2674 | 153.6442 | 152.1442 | 144.8568 | 153.6421 | 148.0074
MELKSHAM GSP | NORRINGTON BSP | NORRINGTON BSP | MINIMUM HEADROOM | ST 88273 64983 | NO | YES | 0 | 115.5379 | 201.4979 | 186.9968 | 146.8 | 139.2021 | 120.9347 | 113.0737 | 104.7874 | 93.8126 | 20.2695 | -10.3674 | -28.7842 | 78.8716 | 164.3168 | 147.1463 | 99.5126 | 91.0547 | 70.0284 | 61.3 | 52.0674 | 40.3516 | -44.2368 | -81.3589 | -102.4442 | 88.7926 | 174.2337 | 157.0989 | 109.5495 | 101.1021 | 80.1074 | 71.3937 | 62.1653 | 50.6232 | -33.5779 | -71.0095 | -92.0642
|  | NORRINGTON BSP | EE |  |  |  |  | 115.5379 | 201.4979 | 186.9968 | 147.1926 | 139.9411 | 124.2242 | 118.3589 | 112.7421 | 105.4253 | 68.1221 | 55.7653 | 40.6442 | 78.8716 | 164.3168 | 147.1463 | 99.9495 | 91.9432 | 73.8937 | 67.4421 | 61.3021 | 53.14 | 10.1389 | -3.0011 | -20.5989 | 88.7926 | 174.2337 | 157.0989 | 109.9821 | 101.9853 | 83.9568 | 77.5084 | 71.3758 | 63.2232 | 20.4421 | 7.5547 | -10.0147
|  | NORRINGTON BSP | HT |  |  |  |  | 116.1368 | 202.2674 | 187.4684 | 146.8 | 139.2021 | 120.9347 | 113.0737 | 104.7874 | 93.8126 | 20.2695 | -10.3674 | -28.7842 | 79.5716 | 165.1979 | 147.7147 | 99.5126 | 91.0547 | 70.0284 | 61.3 | 52.0674 | 40.3516 | -44.2368 | -81.3589 | -102.4442 | 89.4926 | 175.1211 | 157.6632 | 109.5495 | 101.1021 | 80.1074 | 71.3937 | 62.1653 | 50.6232 | -33.5779 | -71.0095 | -92.0642
|  | NORRINGTON BSP | HE |  |  |  |  | 117.5663 | 204.2884 | 190.4874 | 151.3284 | 144.5095 | 129.2179 | 123.9968 | 119.0895 | 112.4505 | 80.6189 | 66.3421 | 53.9895 | 81.2158 | 167.5484 | 151.2021 | 104.6863 | 97.1853 | 79.6011 | 73.9116 | 68.5979 | 61.2358 | 24.2779 | 6.3105 | -8.2211 | 91.1368 | 177.4737 | 161.1537 | 114.7242 | 107.2284 | 89.6737 | 83.9884 | 78.6832 | 71.3284 | 34.5947 | 16.3958 | 1.8895
|  | NORRINGTON BSP | FB |  |  |  |  | 134.7621 | 222.7168 | 205.8526 | 181.1884 | 144.3042 | 141.2768 | 138.9305 | 136.8253 | 134.8305 | 125.4832 | 114.3432 | 103.1968 | 101.0958 | 188.7695 | 168.5253 | 138.88 | 94.8 | 92.3147 | 89.6747 | 87.3137 | 85.0905 | 74.5305 | 61.6347 | 48.6305 | 111.1737 | 199.0853 | 179.8726 | 150.28 | 106.2821 | 102.38 | 99.7421 | 97.3853 | 95.1653 | 84.6232 | 71.7442 | 58.7653
MELKSHAM GSP | NORRINGTON B BSP | NORRINGTON B BSP | MINIMUM HEADROOM | ST 88273 64983 | NO | YES | 0 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | NORRINGTON B BSP | EE | [5 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | NORRINGTON B BSP | HT | [5 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | NORRINGTON B BSP | HE | [5 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | NORRINGTON B BSP | FB | [5 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
NORTH HYDE GSP | NORTH HYDE BSP | NORTH HYDE BSP | MINIMUM HEADROOM | TQ 10367 79001 | NO | NO | 0.015789 | 95.2189 | 95.0074 | 91.5716 | 85.1053 | 79.0274 | 74.1726 | 71.3579 | 68.3926 | 65.9789 | 58.6379 | 52.9105 | 47.3874 | 91.5895 | 90.8179 | 86.7747 | 79.4821 | 72.3663 | 66.7021 | 63.4505 | 60.0221 | 57.2432 | 48.7937 | 42.1484 | 35.7316 | 84.7516 | 84.54 | 84.3126 | 78.4779 | 71.5516 | 66.0347 | 62.8632 | 59.52 | 56.8074 | 48.5737 | 42.0968 | 35.8421
|  | NORTH HYDE BSP | EE |  |  |  |  | 95.2189 | 95.0074 | 92.3253 | 86.6632 | 81.3989 | 77.0032 | 74.8337 | 72.6389 | 71.2316 | 65.8695 | 60.8895 | 56.0442 | 91.5895 | 91.3779 | 87.5789 | 81.3284 | 75.1842 | 70.0621 | 67.5642 | 65.0421 | 63.4495 | 57.1695 | 51.3684 | 45.6853 | 84.7516 | 84.54 | 84.3126 | 80.2716 | 74.2905 | 69.3 | 66.8621 | 64.3979 | 62.84 | 56.7253 | 51.0884 | 45.5579
|  | NORTH HYDE BSP | HT |  |  |  |  | 95.2421 | 95.0547 | 91.5716 | 85.1053 | 79.0274 | 74.1726 | 71.3579 | 68.3926 | 65.9789 | 58.6379 | 52.9105 | 47.3874 | 91.6126 | 90.8179 | 86.7747 | 79.4821 | 72.3663 | 66.7021 | 63.4505 | 60.0221 | 57.2432 | 48.7937 | 42.1484 | 35.7316 | 84.7747 | 84.5874 | 84.3432 | 78.4779 | 71.5516 | 66.0347 | 62.8632 | 59.52 | 56.8074 | 48.5737 | 42.0968 | 35.8421
|  | NORTH HYDE BSP | HE |  |  |  |  | 95.2505 | 95.0421 | 92.7747 | 87.18 | 81.9558 | 77.6274 | 75.6158 | 73.5758 | 72.3232 | 68.0779 | 63.6895 | 59.4095 | 91.6211 | 91.4126 | 88.0558 | 81.9305 | 75.8389 | 70.7947 | 68.4863 | 66.1474 | 64.7379 | 59.7137 | 54.5389 | 49.4905 | 84.7832 | 84.5747 | 84.3537 | 80.86 | 74.9263 | 70.0116 | 67.7579 | 65.4747 | 64.0926 | 59.2095 | 54.1789 | 49.2705
|  | NORTH HYDE BSP | FB |  |  |  |  | 95.3842 | 95.2621 | 95.1516 | 94.4611 | 92.34 | 90.3663 | 89.3979 | 88.3695 | 87.7084 | 84.4495 | 81.2284 | 78.1168 | 91.7547 | 91.6326 | 91.5221 | 89.8389 | 87.5884 | 85.4937 | 84.4705 | 83.3411 | 82.5842 | 78.8189 | 75.0611 | 71.4168 | 84.9168 | 84.7947 | 84.6842 | 84.5611 | 84.4242 | 84.2863 | 83.3937 | 82.2295 | 81.4895 | 77.8168 | 74.1579 | 70.6095
COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD (OSNEY) BSP | MINIMUM HEADROOM | SP 50054 05983 | NO | YES | 66.2105 | 99.9408 | 98.785 | 94.4092 | 92.1029 | 199.7824 | 178.7455 | 172.3266 | 166.0918 | 137.1666 | 126.0539 | 120.8887 | 115.6908 | 89.9376 | 89.4134 | 88.8376 | 88.0039 | 190.7966 | 161.9513 | 153.4482 | 145.1945 | 108.3324 | 95.6071 | 89.6955 | 83.7197 | 91.8545 | 91.3303 | 90.7534 | 89.9197 | 194.0703 | 165.1061 | 156.5713 | 148.2882 | 111.4092 | 98.4976 | 92.5608 | 86.5597
|  | OXFORD (OSNEY) BSP | EE |  |  |  |  | 99.9408 | 98.785 | 94.8376 | 92.9218 | 204.8571 | 186.4024 | 181.0413 | 176.1297 | 137.1666 | 126.0539 | 120.8887 | 115.6908 | 89.9376 | 89.4134 | 88.845 | 88.0797 | 196.7966 | 172.6271 | 165.5261 | 159.0629 | 108.3324 | 95.6071 | 89.6955 | 83.7197 | 91.8545 | 91.3303 | 90.7608 | 89.9955 | 200.5092 | 175.965 | 168.8387 | 162.3534 | 111.4092 | 98.4976 | 92.5608 | 86.5597
|  | OXFORD (OSNEY) BSP | HT |  |  |  |  | 99.9587 | 98.8303 | 94.4092 | 92.1029 | 199.7824 | 178.7455 | 172.3266 | 166.0918 | 160.5118 | 151.2245 | 144.6876 | 137.5539 | 89.9787 | 89.4818 | 88.8376 | 88.0039 | 190.7966 | 161.9513 | 153.4482 | 145.1945 | 137.8492 | 125.9524 | 118.0587 | 109.9587 | 91.8955 | 91.3987 | 90.7534 | 89.9197 | 194.0703 | 165.1061 | 156.5713 | 148.2882 | 140.9155 | 128.9787 | 121.0555 | 112.9292
|  | OXFORD (OSNEY) BSP | HE |  |  |  |  | 100.5682 | 99.6355 | 95.8745 | 94.1008 | 206.1182 | 187.6845 | 182.4413 | 177.6634 | 139.1508 | 130.7918 | 126.9624 | 122.9276 | 90.0882 | 89.5903 | 89.0397 | 88.2734 | 196.9766 | 174.3292 | 167.3997 | 161.1282 | 110.6261 | 100.9376 | 96.5039 | 91.8113 | 92.005 | 91.5071 | 90.9566 | 90.1903 | 200.6934 | 177.6766 | 170.7218 | 164.4261 | 113.7092 | 103.8429 | 99.3903 | 94.6787
|  | OXFORD (OSNEY) BSP | FB |  |  |  |  | 101.2239 | 100.5776 | 99.9861 | 99.1976 | 212.6203 | 211.7297 | 196.0434 | 194.0297 | 159.7466 | 150.0097 | 146.9845 | 143.6161 | 90.4303 | 90.1629 | 89.925 | 89.6555 | 199.1587 | 198.8587 | 184.9587 | 182.2597 | 134.6608 | 122.6808 | 119.3366 | 115.4629 | 92.3471 | 92.0797 | 91.8418 | 91.5724 | 202.8755 | 202.5755 | 188.3376 | 185.6303 | 137.8271 | 125.805 | 122.3061 | 118.4197
MANNINGTON GSP | POOLE (HAMWORTHY) BSP | POOLE (HAMWORTHY) BSP | MINIMUM HEADROOM | SZ 00203 90789 | NO | YES | 0.39368 | 66.8726 | 66.5989 | 66.2979 | 65.7789 | 64.2211 | 62.4232 | 60.3295 | 57.6895 | 52.3989 | 19.44 | -1.8811 | -12.2432 | 65.6579 | 64.7863 | 63.26 | 61.0116 | 59.26 | 57.2747 | 54.8916 | 51.9179 | 45.8684 | 7.4516 | -17.4347 | -29.4716 | 62.6663 | 61.8347 | 60.3968 | 58.2758 | 56.6084 | 54.74 | 52.4832 | 49.68 | 44.0137 | 8.5505 | -15.3368 | -27.3779
|  | POOLE (HAMWORTHY) BSP | EE |  |  |  |  | 66.8726 | 66.5989 | 66.2979 | 65.8895 | 64.2211 | 62.6053 | 61.0989 | 59.1937 | 57.2221 | 40.9074 | 32.4842 | 21.8095 | 65.6579 | 64.7863 | 63.4305 | 61.54 | 59.26 | 57.4379 | 55.7379 | 53.5674 | 51.4347 | 32.4611 | 22.6368 | 10.1547 | 62.6663 | 61.8347 | 60.5526 | 58.7674 | 56.6084 | 54.8758 | 53.2611 | 51.2053 | 49.2021 | 31.6295 | 22.5705 | 11.0737
|  | POOLE (HAMWORTHY) BSP | HT |  |  |  |  | 66.8937 | 66.6358 | 66.3011 | 65.7789 | 64.7011 | 62.4232 | 60.3295 | 57.6895 | 52.3989 | 19.44 | -1.8811 | -12.2432 | 65.7516 | 64.8032 | 63.26 | 61.0116 | 59.88 | 57.2747 | 54.8916 | 51.9179 | 45.8684 | 7.4516 | -17.4347 | -29.4716 | 62.7537 | 61.8547 | 60.3968 | 58.2758 | 57.2021 | 54.74 | 52.4832 | 49.68 | 44.0137 | 8.5505 | -15.3368 | -27.3779
|  | POOLE (HAMWORTHY) BSP | HE |  |  |  |  | 66.9379 | 66.6684 | 66.3684 | 65.9537 | 64.9147 | 63.3726 | 62.0147 | 60.2558 | 58.4632 | 43.3147 | 35.5779 | 25.4947 | 65.8221 | 65.3295 | 64.0947 | 62.3011 | 60.0779 | 58.3411 | 56.82 | 54.8242 | 52.8695 | 35.2074 | 26.1453 | 14.3211 | 63.0432 | 62.3463 | 61.1768 | 59.48 | 57.3726 | 55.72 | 54.2695 | 52.3779 | 50.5411 | 34.1926 | 25.8526 | 14.9768
|  | POOLE (HAMWORTHY) BSP | FB |  |  |  |  | 67.1242 | 66.9853 | 66.8611 | 66.7211 | 66.5663 | 66.4105 | 66.2589 | 66.1179 | 65.2347 | 61.6621 | 53.7947 | 44.7863 | 66.0253 | 65.8695 | 65.4968 | 64.7453 | 63.8379 | 63.08 | 62.3695 | 61.3926 | 60.3453 | 56.2474 | 47.1621 | 36.66 | 63.5116 | 63.0684 | 62.5158 | 61.8053 | 60.9526 | 60.2358 | 59.5642 | 58.6463 | 57.6632 | 53.8284 | 45.3611 | 35.6547
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ 63405 99685 | NO | YES | 5.2 | 105.1274 | 103.6979 | 102.0211 | 189.6442 | 193.0758 | 192.1484 | 191.2389 | 190.3758 | 188.2632 | 167.4926 | 155.44 | 144.6989 | 111.2179 | 109.9695 | 108.5747 | 196.6537 | 199.4032 | 198.5958 | 192.8421 | 184.38 | 175.88 | 151.3053 | 137.1537 | 124.5484 | 114.3905 | 113.1432 | 111.7474 | 199.8274 | 202.5768 | 201.7695 | 194.7389 | 186.3726 | 177.9611 | 153.6684 | 139.6747 | 127.2074
|  | PORTSMOUTH BSP | EE |  |  |  |  | 105.1274 | 103.6979 | 102.0211 | 189.8274 | 203.7642 | 200.9368 | 198.2221 | 195.3853 | 192.5726 | 183.8484 | 175.1263 | 167.7189 | 111.2179 | 109.9695 | 108.5747 | 196.6779 | 210.9158 | 206.8632 | 201.1611 | 194.9032 | 188.6842 | 170.7505 | 160.2337 | 151.2758 | 114.3905 | 113.1432 | 111.7474 | 199.8495 | 214.0863 | 208.6232 | 202.9526 | 196.7316 | 190.5705 | 172.8811 | 162.4989 | 153.6547
|  | PORTSMOUTH BSP | HT |  |  |  |  | 105.2695 | 103.8905 | 102.0389 | 189.6442 | 203.6147 | 200.4611 | 197.2516 | 194.0379 | 188.2632 | 167.4926 | 155.44 | 144.6989 | 111.3126 | 110.1684 | 108.6568 | 196.6979 | 208.7432 | 201 | 192.8421 | 184.38 | 175.88 | 151.3053 | 137.1537 | 124.5484 | 114.4863 | 113.3389 | 111.8305 | 199.8705 | 210.5105 | 202.8168 | 194.7389 | 186.3726 | 177.9611 | 153.6684 | 139.6747 | 127.2074
|  | PORTSMOUTH BSP | HE |  |  |  |  | 105.4421 | 104.0463 | 102.3874 | 190.1589 | 203.9979 | 201.2411 | 198.5547 | 195.8 | 193.0979 | 191.9463 | 189.4337 | 184.8253 | 111.3695 | 110.0905 | 108.6432 | 196.6537 | 210.7421 | 208.2011 | 205.7189 | 202.42 | 197.8347 | 185.9263 | 177.3463 | 171.62 | 114.5432 | 113.2642 | 111.8168 | 199.8274 | 213.9158 | 211.3747 | 208.8105 | 204.1726 | 199.6074 | 187.8537 | 179.3253 | 173.6821
|  | PORTSMOUTH BSP | FB |  |  |  |  | 106.4253 | 105.6011 | 104.8611 | 194.0126 | 193.0758 | 192.1484 | 191.2389 | 190.3758 | 189.4432 | 202.6168 | 200.2411 | 198.6905 | 112.2653 | 111.5558 | 110.9147 | 200.1979 | 199.4032 | 198.5958 | 197.8189 | 197.0937 | 196.3147 | 206.5726 | 197.5326 | 191.5716 | 115.4389 | 114.7295 | 114.0884 | 203.3716 | 202.5768 | 201.7695 | 200.9926 | 200.2674 | 199.4884 | 208.3547 | 199.4042 | 193.5179
FLEET-BRAMLEY GSP | PYESTOCK BSP | PYESTOCK BSP | MINIMUM HEADROOM | SU 82940 54553 | YES | YES | 0 | 96.7474 | 96.3947 | 95.9863 | 94.9463 | 93.7074 | 92.34 | 90.9832 | 89.6242 | 88.2547 | 78.9926 | 77.2442 | 75.6589 | 92.1705 | 91.38 | 90.6695 | 89.5884 | 88.2947 | 86.8716 | 85.4579 | 84.0432 | 82.6158 | 72.7484 | 70.7989 | 69.0284 | 93.0937 | 92.2474 | 91.4958 | 90.3432 | 88.9695 | 87.4526 | 85.9495 | 84.4421 | 82.9211 | 72.3389 | 70.4021 | 68.6432
|  | PYESTOCK BSP | EE |  |  |  |  | 96.7474 | 96.3947 | 96.0674 | 95.3716 | 94.5568 | 93.7537 | 92.9663 | 92.1937 | 91.4147 | 86.4768 | 85.2705 | 84.2211 | 92.1705 | 91.38 | 90.7674 | 90.0358 | 89.1947 | 88.3663 | 87.5558 | 86.76 | 85.9558 | 80.7326 | 79.4663 | 78.3642 | 93.0937 | 92.2474 | 91.6 | 90.8295 | 89.9495 | 89.0821 | 88.2305 | 87.3958 | 86.5516 | 80.8695 | 79.5063 | 78.3179
|  | PYESTOCK BSP | HT |  |  |  |  | 96.7695 | 96.4284 | 95.9863 | 94.9463 | 93.7074 | 92.34 | 90.9832 | 89.6242 | 88.2547 | 78.9926 | 77.2442 | 75.6589 | 92.2463 | 91.4842 | 90.6695 | 89.5884 | 88.2947 | 86.8716 | 85.4579 | 84.0432 | 82.6158 | 72.7484 | 70.7989 | 69.0284 | 93.1768 | 92.3611 | 91.4958 | 90.3432 | 88.9695 | 87.4526 | 85.9495 | 84.4421 | 82.9211 | 72.3389 | 70.4021 | 68.6432
|  | PYESTOCK BSP | HE |  |  |  |  | 96.8547 | 96.54 | 96.2453 | 95.8568 | 95.1379 | 94.3989 | 93.6916 | 92.9947 | 92.2895 | 87.9379 | 87.1063 | 86.3716 | 92.4484 | 91.7642 | 91.2432 | 90.5895 | 89.8053 | 89.0453 | 88.3168 | 87.6021 | 86.8747 | 82.26 | 81.3821 | 80.6042 | 93.3926 | 92.6611 | 92.1137 | 91.4274 | 90.6063 | 89.8116 | 89.0516 | 88.3032 | 87.5442 | 82.5011 | 81.5453 | 80.7
|  | PYESTOCK BSP | FB |  |  |  |  | 97.0558 | 96.8874 | 96.7642 | 96.6253 | 96.4747 | 96.3189 | 96.1684 | 95.9516 | 95.6316 | 94.2568 | 93.4337 | 92.7253 | 92.7968 | 92.3947 | 92.1442 | 91.8621 | 91.5642 | 91.2495 | 90.94 | 90.6316 | 90.2989 | 88.8632 | 88.0011 | 87.2579 | 93.7589 | 93.3284 | 93.0632 | 92.7621 | 92.4453 | 92.1116 | 91.7821 | 91.4547 | 91.0989 | 89.5632 | 88.64 | 87.8389
BRAMLEY (BASI) GSP | READING BSP | READING BSP | MINIMUM HEADROOM | SU 74642 73856 | NO | YES | 54.5263 | 226.2105 | 224.5895 | 213.9842 | 208.3053 | 201.6211 | 172.1632 | 148.8874 | 141.5811 | 134.2189 | 104.4747 | 80.3316 | 65.3253 | 214.4358 | 210.7 | 187.3663 | 181.0968 | 173.7274 | 139.6674 | 112.8642 | 104.8021 | 96.6695 | 63.0779 | 35.3274 | 18.3505 | 212.0874 | 210.6347 | 190.4947 | 184.2747 | 176.9695 | 143.3211 | 116.8347 | 108.8411 | 100.7779 | 67.6432 | 40.1116 | 23.3126
|  | READING BSP | EE |  |  |  |  | 226.2105 | 224.5895 | 214.2716 | 209.6221 | 203.9663 | 176.1295 | 153.9411 | 147.88 | 142.0021 | 124.0074 | 109.6116 | 98.3053 | 214.4358 | 210.7 | 187.6989 | 182.62 | 176.4979 | 144.3126 | 118.72 | 112.0737 | 105.6389 | 84.9937 | 68.3989 | 55.3716 | 212.0874 | 210.6347 | 190.8189 | 185.7779 | 179.6958 | 147.9 | 122.6116 | 116.0137 | 109.6305 | 89.3326 | 72.9263 | 60.0463
|  | READING BSP | HT |  |  |  |  | 226.2895 | 224.7474 | 213.9842 | 208.3053 | 201.6211 | 172.1632 | 148.8874 | 141.5811 | 134.2189 | 104.4747 | 80.3316 | 65.3253 | 214.4853 | 211.0684 | 187.3663 | 181.0968 | 173.7274 | 139.6674 | 112.8642 | 104.8021 | 96.6695 | 63.0779 | 35.3274 | 18.3505 | 212.1411 | 210.7779 | 190.4947 | 184.2747 | 176.9695 | 143.3211 | 116.8347 | 108.8411 | 100.7779 | 67.6432 | 40.1116 | 23.3126
|  | READING BSP | HE |  |  |  |  | 226.6032 | 225.0947 | 217.3453 | 213.1968 | 207.8737 | 180.4926 | 158.8642 | 153.3832 | 148.0789 | 134.4979 | 123.0768 | 114.3568 | 214.7053 | 213.3147 | 191.2326 | 186.7347 | 180.9989 | 149.3221 | 124.3905 | 118.4221 | 112.6568 | 96.6579 | 83.3295 | 73.14 | 212.3611 | 210.9705 | 194.3168 | 189.8495 | 184.1505 | 152.8611 | 128.2284 | 122.3021 | 116.5747 | 100.7968 | 87.6358 | 77.5768
|  | READING BSP | FB |  |  |  |  | 227.7768 | 227.0095 | 226.3116 | 220.3674 | 218.3021 | 216.0126 | 213.2695 | 210.8095 | 208.2779 | 197.7716 | 188.3 | 180.2347 | 215.8042 | 215.1337 | 214.5305 | 194.4179 | 192.1253 | 189.5705 | 186.4758 | 183.7063 | 180.8621 | 168.9937 | 158.1337 | 148.8305 | 213.4611 | 212.7905 | 212.1874 | 197.4884 | 195.2158 | 192.6863 | 189.62 | 186.8811 | 184.0632 | 172.32 | 161.5832 | 152.3937
FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN BSP | MINIMUM HEADROOM | SU 71580 74111 | NO | YES | 0 | 109.3684 | 108.9137 | 108.3663 | 107.36 | 103.8642 | 100.0295 | 95.3579 | 91.0368 | 86.6295 | 77.8737 | 74.4379 | 71.3042 | 103.8621 | 103.4063 | 102.8821 | 99.7653 | 95.7653 | 91.3842 | 86.0537 | 81.1126 | 76.0684 | 66.1168 | 62.3105 | 58.8358 | 102.0874 | 101.6263 | 101.0968 | 98.4937 | 94.5853 | 90.3453 | 85.1421 | 80.3411 | 75.4421 | 65.8053 | 62.0779 | 58.6737
|  | READING TOWN BSP | EE |  |  |  |  | 109.3684 | 108.9137 | 108.3663 | 107.36 | 103.8642 | 100.0326 | 95.3579 | 91.0368 | 86.6295 | 79.5663 | 77.0274 | 74.8095 | 103.8621 | 103.4063 | 102.8821 | 99.8421 | 95.7737 | 91.4126 | 86.0537 | 81.1126 | 76.0684 | 67.8968 | 65.0421 | 62.5411 | 102.0874 | 101.6263 | 101.0968 | 98.5474 | 94.5853 | 90.3453 | 85.1421 | 80.3411 | 75.4421 | 67.5053 | 64.6989 | 62.2411
|  | READING TOWN BSP | HT |  |  |  |  | 109.4158 | 108.9832 | 108.4084 | 107.3684 | 103.8842 | 100.0295 | 95.4211 | 91.0916 | 86.6463 | 77.8737 | 74.4379 | 71.3042 | 103.9074 | 103.4726 | 102.9147 | 99.7653 | 95.7653 | 91.3842 | 86.1126 | 81.1663 | 76.0821 | 66.1168 | 62.3105 | 58.8358 | 102.1411 | 101.7042 | 101.1442 | 98.4937 | 94.6053 | 90.3474 | 85.2295 | 80.4274 | 75.4958 | 65.8053 | 62.0779 | 58.6737
|  | READING TOWN BSP | HE |  |  |  |  | 109.5126 | 109.0916 | 108.6021 | 107.6716 | 105.1221 | 101.4211 | 96.9821 | 92.9084 | 88.7316 | 83.4505 | 82.0326 | 80.7768 | 104.0042 | 103.5842 | 103.0937 | 101.1179 | 97.1979 | 92.9821 | 87.8968 | 83.2421 | 78.4642 | 72.2358 | 70.5968 | 69.1389 | 102.2411 | 101.8211 | 101.3305 | 99.8526 | 96.0063 | 91.9126 | 86.9811 | 82.4632 | 77.8274 | 71.8253 | 70.2358 | 68.8253
|  | READING TOWN BSP | FB |  |  |  |  | 109.8158 | 109.5947 | 109.3979 | 109.1747 | 108.8947 | 108.5316 | 108.1379 | 106.6526 | 104.3863 | 99.98 | 98.1663 | 96.6758 | 104.3074 | 104.0863 | 103.8895 | 103.6663 | 103.42 | 103.1705 | 101.1463 | 98.7905 | 96.16 | 91.12 | 89.0716 | 87.3684 | 102.5453 | 102.3242 | 102.1274 | 101.9042 | 101.6579 | 101.4084 | 99.8842 | 97.5863 | 95.0421 | 90.1526 | 88.16 | 86.5063
MANNINGTON GSP | REDHILL BSP | REDHILL BSP | MINIMUM HEADROOM | SZ 08581 96162 | NO | YES | 105.3274 | 98.1011 | 95.9263 | 93.5768 | 90.6705 | 87.5347 | 83.5611 | 79.7179 | 75.6958 | 69.9705 | 39.8158 | 32.6421 | 26.1716 | 89.9358 | 87.3463 | 84.4674 | 81.0032 | 77.3063 | 72.4263 | 67.7379 | 62.7737 | 55.3537 | 19.5137 | 11.5589 | 4.3758 | 92.3211 | 89.7211 | 86.8442 | 83.3705 | 79.6726 | 74.8 | 70.1147 | 65.1589 | 57.7547 | 21.9968 | 14.0421 | 6.8568
|  | REDHILL BSP | EE |  |  |  |  | 98.1011 | 95.9263 | 93.5768 | 91.2937 | 88.6326 | 86.1547 | 83.6926 | 81.0853 | 77.8484 | 63.9979 | 58.8368 | 54.1505 | 89.9358 | 87.3463 | 84.5642 | 82.0158 | 79.1274 | 76.4263 | 73.7295 | 70.8726 | 67.0347 | 48.2211 | 41.9558 | 36.6695 | 92.3211 | 89.7211 | 86.9242 | 84.3579 | 81.4632 | 78.7495 | 76.0379 | 73.1632 | 69.3189 | 50.4989 | 44.2137 | 38.9116
|  | REDHILL BSP | HT |  |  |  |  | 98.4842 | 96.2063 | 93.5979 | 90.6705 | 87.5347 | 83.5611 | 79.7179 | 75.6958 | 69.9705 | 39.8158 | 32.6421 | 26.1716 | 90.3937 | 87.6126 | 84.4674 | 81.0032 | 77.3063 | 72.4263 | 67.7379 | 62.7737 | 55.3537 | 19.5137 | 11.5589 | 4.3758 | 92.7874 | 89.9989 | 86.8442 | 83.3705 | 79.6726 | 74.8 | 70.1147 | 65.1589 | 57.7547 | 21.9968 | 14.0421 | 6.8568
|  | REDHILL BSP | HE |  |  |  |  | 99.6579 | 98.2137 | 96.5968 | 94.9695 | 92.8568 | 90.9242 | 89.1168 | 87.2358 | 84.5558 | 74.3095 | 71.7484 | 69.5505 | 91.8347 | 90.1189 | 88.1979 | 86.4084 | 84.1474 | 82.0674 | 80.1453 | 78.1368 | 74.9684 | 60.2811 | 56.7453 | 53.6842 | 94.2411 | 92.5274 | 90.6105 | 88.8242 | 86.5632 | 84.4842 | 82.5642 | 80.5568 | 77.3947 | 62.7505 | 59.2253 | 56.1737
|  | REDHILL BSP | FB |  |  |  |  | 106.3895 | 99.8937 | 98.2389 | 97.5421 | 96.7737 | 96.0347 | 95.3211 | 94.6442 | 93.9505 | 90.8568 | 88.0242 | 85.6389 | 101.2 | 92.0842 | 89.6789 | 88.8537 | 87.9453 | 87.0789 | 86.2474 | 85.4516 | 84.6453 | 80.9011 | 77.2284 | 74.0568 | 103.4158 | 94.4905 | 91.92 | 91.0958 | 90.1895 | 89.3253 | 88.4947 | 87.7 | 86.8937 | 83.1558 | 79.4937 | 76.3295
NURSLING GSP | ROWNHAMS BSP | ROWNHAMS BSP | MINIMUM HEADROOM | SU 37168 16854 | NO | YES | 57.8421 | 95.5968 | 92.8221 | 67.6874 | 152.7389 | 148.4463 | 95.7905 | 86.1747 | 80.16 | 87.6589 | 60.0758 | 50.5621 | 41.0368 | 66.4232 | 63.3368 | 34.0179 | 118.5095 | 114.0137 | 52.4716 | 41.5684 | 34.8968 | 41.7411 | 10.22 | -0.38947 | -11.0779 | 70.2421 | 67.1589 | 37.8863 | 122.3874 | 117.6232 | 56.1926 | 45.3063 | 38.6432 | 45.4958 | 14.0221 | 3.4263 | -7.2484
|  | ROWNHAMS BSP | EE |  |  |  |  | 95.5968 | 92.9368 | 67.6874 | 153.6463 | 148.9916 | 97.7737 | 89.6316 | 85.7305 | 94.1053 | 76.3989 | 69.2905 | 62.5137 | 66.4232 | 63.5 | 34.0179 | 119.5653 | 114.5105 | 54.6326 | 45.4116 | 41.4832 | 49.0274 | 28.6568 | 20.5705 | 12.8168 | 70.2421 | 67.3211 | 37.8863 | 123.4368 | 118.3874 | 58.6189 | 49.4105 | 45.5432 | 53.0337 | 32.4242 | 24.3442 | 16.5989
|  | ROWNHAMS BSP | HT |  |  |  |  | 95.9463 | 92.8221 | 67.7011 | 152.7389 | 148.4463 | 95.7905 | 86.1747 | 80.16 | 87.6589 | 60.0758 | 50.5621 | 41.0368 | 66.8211 | 63.3368 | 34.0295 | 118.5095 | 114.0137 | 52.4716 | 41.5684 | 34.8968 | 41.7411 | 10.22 | -0.38947 | -11.0779 | 70.6411 | 67.1589 | 37.9011 | 122.3874 | 117.6232 | 56.1926 | 45.3063 | 38.6432 | 45.4958 | 14.0221 | 3.4263 | -7.2484
|  | ROWNHAMS BSP | HE |  |  |  |  | 97.1253 | 95.0621 | 70.3589 | 156.7632 | 152.44 | 101.6274 | 93.9474 | 90.0084 | 99.5495 | 84.4937 | 78.2432 | 73.5347 | 68.1632 | 65.9253 | 37.06 | 123.1179 | 118.4389 | 59.0105 | 50.3284 | 46.0526 | 55.2526 | 37.1863 | 29.1053 | 23.6116 | 71.9811 | 69.7442 | 40.9326 | 126.9947 | 122.3189 | 62.9989 | 54.3295 | 50.0589 | 59.2642 | 40.8589 | 32.6326 | 27.1495
|  | ROWNHAMS BSP | FB |  |  |  |  | 98.5979 | 97.1705 | 79.5147 | 167.6642 | 166.0221 | 159.36 | 157.6621 | 155.92 | 154.0137 | 142.2253 | 149.1389 | 144.6537 | 69.76 | 68.1758 | 47.4884 | 135.4042 | 133.5768 | 125.8442 | 123.9516 | 121.9979 | 119.86 | 106.3695 | 112.5221 | 107.3863 | 73.5747 | 71.9947 | 51.3453 | 139.2621 | 137.4379 | 129.72 | 127.8295 | 125.8789 | 123.7421 | 110.2758 | 116.1663 | 111.0411
MANNINGTON GSP | SALISBURY BSP | SALISBURY BSP | MINIMUM HEADROOM | SU 11049 31395 | NO | YES | 71.1053 | 118.5032 | 117.5505 | 109.5179 | 106.7779 | 103.7305 | 89.8863 | 47.8084 | 41.2674 | 36.0358 | 18.22 | 9.8284 | 2.3189 | 105.4726 | 103.0558 | 90.9589 | 87.6411 | 84.0284 | 67.3663 | 18.1453 | 11.0905 | 5.2253 | -15.0684 | -24.5316 | -33.0095 | 102.4926 | 101.6674 | 91.4168 | 88.3905 | 85.0621 | 69.1947 | 20.6863 | 13.3011 | 7.5021 | -12.5168 | -21.8621 | -30.2326
|  | SALISBURY BSP | EE |  |  |  |  | 118.5032 | 117.5505 | 109.5179 | 106.9505 | 103.7305 | 89.8863 | 47.8084 | 43.3032 | 40.1453 | 33.1474 | 27.1505 | 21.9484 | 105.4726 | 103.0558 | 90.9589 | 87.8537 | 84.0284 | 67.3663 | 18.1453 | 13.1095 | 9.6537 | 1.9158 | -4.9716 | -10.9558 | 102.4926 | 101.6674 | 91.4168 | 88.5842 | 85.0621 | 69.1947 | 20.6863 | 15.7053 | 12.28 | 4.2358 | -2.5516 | -8.4526
|  | SALISBURY BSP | HT |  |  |  |  | 118.5832 | 117.6905 | 109.7232 | 106.7779 | 107.3568 | 92.3253 | 48.5947 | 41.2674 | 36.0358 | 18.22 | 9.8284 | 2.3189 | 105.7295 | 103.5337 | 91.2442 | 87.6411 | 88.4589 | 70.4537 | 19.4084 | 11.0905 | 5.2253 | -15.0684 | -24.5316 | -33.0095 | 102.5474 | 101.7758 | 91.6621 | 88.3905 | 89.2074 | 71.9168 | 21.5295 | 13.3011 | 7.5021 | -12.5168 | -21.8621 | -30.2326
|  | SALISBURY BSP | HE |  |  |  |  | 118.8105 | 117.94 | 111.1179 | 108.7937 | 105.7389 | 92.4663 | 50.7263 | 46.6526 | 43.8958 | 39.6663 | 35.4011 | 31.6747 | 105.8989 | 104.7653 | 93.0684 | 90.2937 | 86.6916 | 70.3189 | 21.5021 | 16.9726 | 13.9895 | 9.3 | 4.3263 | -0.028421 | 102.7168 | 101.9421 | 93.2705 | 90.7242 | 87.3979 | 72.1158 | 24 | 19.5179 | 16.5579 | 11.5284 | 6.6358 | 2.3484
|  | SALISBURY BSP | FB |  |  |  |  | 119.4305 | 118.9768 | 118.5632 | 112.9295 | 111.7505 | 110.5284 | 109.4095 | 108.4158 | 107.3968 | 102.3558 | 102.4526 | 99.0505 | 106.4632 | 106.0842 | 105.4495 | 95.1621 | 93.6853 | 92.1484 | 90.7495 | 89.5116 | 88.2547 | 81.8147 | 82.0779 | 78.1779 | 103.2811 | 102.9021 | 102.5589 | 95.2242 | 93.8968 | 92.5189 | 91.26 | 90.1453 | 89.0084 | 83.2726 | 83.4074 | 79.5505
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST 85442 23791 | NO | YES | 96.7379 | 87.2895 | 85.7411 | 83.8189 | 81.14 | 78.3558 | 43.94 | 40.3179 | 31.9316 | 26.6611 | -2.3442 | -17.9779 | -27.8726 | 72.1874 | 70.4895 | 68.36 | 65.3989 | 62.38 | 21.9158 | 17.9021 | 8.2432 | 2.2674 | -31.4495 | -49.5779 | -60.96 | 75.6968 | 74.0011 | 71.8768 | 68.92 | 65.8579 | 25.5105 | 21.5032 | 11.8663 | 5.9074 | -27.72 | -45.8032 | -57.1558
|  | SHAFTESBURY BSP | EE |  |  |  |  | 87.2895 | 85.7411 | 84.0021 | 82.0516 | 79.6895 | 46.6168 | 44.3284 | 39.5337 | 36.3726 | 22.9632 | 15.2937 | 6.7863 | 72.1874 | 70.4895 | 68.5758 | 66.4653 | 63.9432 | 25.0526 | 22.5768 | 17.1463 | 13.6432 | -2.0347 | -10.9516 | -20.9 | 75.6968 | 74.0011 | 72.0895 | 69.9779 | 67.4589 | 28.6811 | 26.2084 | 20.7916 | 17.2947 | 1.6 | -7.2926 | -17.2179
|  | SHAFTESBURY BSP | HT |  |  |  |  | 87.5189 | 85.9516 | 83.8189 | 81.14 | 78.3558 | 43.94 | 40.3179 | 31.9316 | 26.6611 | -2.3442 | -17.9779 | -27.8726 | 72.4505 | 70.72 | 68.36 | 65.3989 | 62.38 | 21.9158 | 17.9021 | 8.2432 | 2.2674 | -31.4495 | -49.5779 | -60.96 | 75.9611 | 74.2326 | 71.8768 | 68.92 | 65.8579 | 25.5105 | 21.5032 | 11.8663 | 5.9074 | -27.72 | -45.8032 | -57.1558
|  | SHAFTESBURY BSP | HE |  |  |  |  | 88.24 | 87.0653 | 85.6463 | 83.9568 | 81.7863 | 48.9589 | 46.9811 | 42.5558 | 39.7568 | 28.6442 | 22.46 | 15.1968 | 73.2737 | 72.0053 | 70.4621 | 68.6547 | 66.3484 | 27.7316 | 25.6242 | 20.6253 | 17.5463 | 4.3968 | -2.88 | -11.4547 | 76.7842 | 75.5168 | 73.9747 | 72.1684 | 69.8642 | 31.3642 | 29.2579 | 24.2695 | 21.1947 | 8.0358 | 0.77895 | -7.7695
|  | SHAFTESBURY BSP | FB |  |  |  |  | 96.8842 | 96.0621 | 95.3663 | 94.6442 | 93.8295 | 93.0074 | 92.1874 | 91.4 | 90.5453 | 78.56 | 72.6926 | 66.1 | 82.1874 | 81.8674 | 81.5053 | 80.7937 | 79.9895 | 79.1295 | 78.2221 | 77.3516 | 76.4 | 62.4495 | 55.6611 | 47.9432 | 86.8453 | 85.9421 | 85.1747 | 84.3895 | 83.5 | 82.6042 | 81.7053 | 80.84 | 79.8905 | 65.98 | 59.16 | 51.4632
IVER 132KV GSP | SLOUGH BSP | SLOUGH BSP | MINIMUM HEADROOM | SU 95574 81752 | NO | YES | 0 | 105.1684 | 194.6326 | 194.02 | 193.1737 | 192.0989 | 191.0232 | 189.9284 | 188.8253 | 187.7305 | 185.0737 | 181.6379 | 178.1274 | 104.3389 | 193.8032 | 193.1905 | 192.3442 | 191.2695 | 190.1926 | 189.0968 | 187.2105 | 184.8989 | 179.2126 | 171.3484 | 167.4726 | 108.1811 | 197.6463 | 197.0326 | 196.1863 | 195.1126 | 194.0358 | 192.9 | 190.6716 | 188.4526 | 182.9979 | 175.3989 | 171.5295
|  | SLOUGH BSP | EE |  |  |  |  | 105.1684 | 194.6326 | 194.02 | 193.1989 | 192.0989 | 191.0232 | 190.0126 | 188.9842 | 187.9916 | 187.1821 | 186.5126 | 185.9811 | 104.3389 | 193.8032 | 193.1905 | 192.3695 | 191.2695 | 190.1926 | 189.1821 | 188.1537 | 187.16 | 184.74 | 179.9242 | 177.3474 | 108.1811 | 197.6463 | 197.0326 | 196.2116 | 195.1126 | 194.0358 | 193.0253 | 191.9968 | 191.0116 | 188.2632 | 183.7621 | 181.2863
|  | SLOUGH BSP | HT |  |  |  |  | 105.1916 | 194.6874 | 194.0232 | 193.1737 | 192.1495 | 191.0242 | 189.9284 | 188.8253 | 187.7305 | 185.0737 | 181.6379 | 178.1274 | 104.3621 | 193.8579 | 193.1937 | 192.3442 | 191.3189 | 190.1937 | 189.0968 | 187.2105 | 184.8989 | 179.2126 | 171.3484 | 167.4726 | 108.2053 | 197.7 | 197.0358 | 196.1863 | 195.1611 | 194.0368 | 192.9 | 190.6716 | 188.4526 | 182.9979 | 175.3989 | 171.5295
|  | SLOUGH BSP | HE |  |  |  |  | 105.2684 | 194.7516 | 194.1621 | 193.3589 | 192.2684 | 191.2347 | 190.2242 | 189.1989 | 188.2105 | 188.2663 | 188.1284 | 188.04 | 104.4389 | 193.9221 | 193.3326 | 192.5295 | 191.4389 | 190.4053 | 189.3947 | 188.3695 | 187.38 | 187.4368 | 185.5958 | 184.0768 | 108.2821 | 197.7653 | 197.1758 | 196.3726 | 195.2821 | 194.2484 | 193.2379 | 192.2126 | 191.2326 | 191.28 | 189.1189 | 187.7095
|  | SLOUGH BSP | FB |  |  |  |  | 105.6779 | 195.4253 | 195.1958 | 194.9389 | 194.6568 | 194.3695 | 194.0905 | 193.8316 | 193.5547 | 192.5368 | 191.9705 | 191.6084 | 104.8484 | 194.5958 | 194.3663 | 194.1095 | 193.8274 | 193.54 | 193.2611 | 193.0021 | 192.7253 | 191.7074 | 191.1411 | 190.0432 | 108.6916 | 198.4389 | 198.2095 | 197.9526 | 197.6705 | 197.3832 | 197.1042 | 196.8453 | 196.5684 | 195.5505 | 194.9842 | 193.4926
NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | SOUTHAMPTON (RESERVE) BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | YES | 3.7905 | 77.1179 | 76.9137 | 77.0453 | 76.9074 | 76.7632 | 71.5305 | 68.0168 | 65.6505 | 63.6411 | 59.7253 | 57.3758 | 55.2463 | 66.0747 | 65.6232 | 65.9842 | 65.8695 | 65.0221 | 57.4389 | 53.3579 | 50.6305 | 48.3505 | 43.8968 | 41.2347 | 38.8253 | 63.8389 | 63.6505 | 63.7484 | 63.6337 | 63.5053 | 59.8274 | 55.8863 | 53.2474 | 51.0558 | 46.7347 | 44.1516 | 41.8116
|  | SOUTHAMPTON (RESERVE) BSP | EE |  |  |  |  | 77.1179 | 76.9137 | 78.7411 | 78.4305 | 78.0253 | 77.6232 | 76.7116 | 73.2705 | 68.2158 | 64.0074 | 62.1863 | 60.6179 | 66.0747 | 65.6232 | 66.8326 | 66.5716 | 66.2011 | 65.6295 | 64.3979 | 60.3863 | 53.6947 | 48.8074 | 46.7147 | 44.9095 | 63.8389 | 63.6663 | 65.0937 | 64.8337 | 64.4621 | 64.1137 | 63.7821 | 63.1895 | 56.1895 | 51.4895 | 49.4663 | 47.7189
|  | SOUTHAMPTON (RESERVE) BSP | HT |  |  |  |  | 77.12 | 78.9621 | 78.7011 | 78.3305 | 77.3421 | 71.5305 | 68.0168 | 65.6505 | 63.6411 | 59.7253 | 57.3758 | 55.2463 | 66.08 | 67.0326 | 66.8147 | 66.5295 | 65.0221 | 57.4389 | 53.3579 | 50.6305 | 48.3505 | 43.8968 | 41.2347 | 38.8253 | 63.8442 | 65.2947 | 65.0768 | 64.7905 | 64.4432 | 59.8274 | 55.8863 | 53.2474 | 51.0558 | 46.7347 | 44.1516 | 41.8116
|  | SOUTHAMPTON (RESERVE) BSP | HE |  |  |  |  | 77.1411 | 76.9221 | 78.7326 | 78.3895 | 77.94 | 75.4716 | 74.8789 | 72.5368 | 70.0653 | 66.3684 | 64.8705 | 63.8484 | 66.0811 | 65.8863 | 66.7937 | 66.4958 | 66.0758 | 62.7737 | 61.6926 | 58.7695 | 55.9263 | 51.5547 | 49.8063 | 48.6147 | 63.8453 | 63.6505 | 65.0558 | 64.7579 | 64.3379 | 62.3474 | 61.9832 | 61.0863 | 58.3274 | 54.1232 | 52.4379 | 51.2874
|  | SOUTHAMPTON (RESERVE) BSP | FB |  |  |  |  | 77.2947 | 77.16 | 77.0453 | 76.9074 | 76.7632 | 76.6189 | 76.4674 | 76.3263 | 75.9747 | 72.1147 | 72.7032 | 71.6558 | 66.2032 | 66.0884 | 65.9842 | 65.8695 | 65.6042 | 65.2621 | 64.8432 | 64.4347 | 62.9074 | 58.1095 | 59.6295 | 58.4232 | 63.9674 | 63.8526 | 63.7484 | 63.6337 | 63.5053 | 63.3768 | 63.2495 | 63.1326 | 63.0084 | 60.4768 | 62.5263 | 61.3989
NURSLING GSP | SOUTHAMPTON (MAIN) BSP | SOUTHAMPTON (MAIN) BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | YES | 0 | 113.8211 | 113.0274 | 111.9863 | 109.7211 | 105.3895 | 101.3674 | 97.0168 | 92.02 | 87.1947 | 76.7853 | 71.7779 | 67.3105 | 97.9253 | 97.4221 | 96.8779 | 96.0874 | 94.3042 | 89.7663 | 84.8442 | 79.1611 | 73.6768 | 61.9126 | 56.3074 | 51.3095 | 97.5747 | 97.0705 | 96.5263 | 95.7358 | 93.2526 | 88.8411 | 84.0589 | 78.5432 | 73.22 | 61.8242 | 56.3632 | 51.4937
|  | SOUTHAMPTON (MAIN) BSP | EE |  |  |  |  | 113.8211 | 113.0274 | 112.2074 | 110.9305 | 108.9726 | 106.0884 | 102.6189 | 98.4863 | 95.3495 | 85.2084 | 81.5137 | 78.3632 | 97.9253 | 97.4221 | 96.8789 | 96.1337 | 95.0779 | 94.0916 | 91.3905 | 86.7021 | 83.18 | 71.4379 | 67.2379 | 63.6411 | 97.5747 | 97.0705 | 96.5263 | 95.7821 | 94.7274 | 93.74 | 90.3726 | 85.8232 | 82.3947 | 71.0705 | 67.0011 | 63.5116
|  | SOUTHAMPTON (MAIN) BSP | HT |  |  |  |  | 113.8537 | 113.0663 | 111.9863 | 109.7211 | 105.3895 | 101.3674 | 97.0168 | 92.02 | 87.1947 | 76.7853 | 71.7779 | 67.3105 | 97.9537 | 97.4895 | 96.8779 | 96.0874 | 94.3042 | 89.7663 | 84.8442 | 79.1611 | 73.6768 | 61.9126 | 56.3074 | 51.3095 | 97.6032 | 97.1389 | 96.5263 | 95.7358 | 93.2526 | 88.8411 | 84.0589 | 78.5432 | 73.22 | 61.8242 | 56.3632 | 51.4937
|  | SOUTHAMPTON (MAIN) BSP | HE |  |  |  |  | 114.0621 | 113.3316 | 112.5632 | 111.5979 | 110.1032 | 107.3916 | 104.1074 | 100.5137 | 97.5747 | 90.2021 | 87.6305 | 85.5979 | 98.0116 | 97.5084 | 96.96 | 96.1926 | 95.0979 | 94.1253 | 93.14 | 89.0895 | 85.8053 | 77.1379 | 74.16 | 71.8032 | 97.6611 | 97.1579 | 96.6095 | 95.8421 | 94.7474 | 93.7747 | 92.0621 | 88.1221 | 84.9232 | 76.5716 | 73.6916 | 71.4147
|  | SOUTHAMPTON (MAIN) BSP | FB |  |  |  |  | 114.5653 | 114.1358 | 113.7684 | 113.3884 | 112.9537 | 112.5074 | 111.9379 | 110.7495 | 109.5632 | 102.1337 | 99.2421 | 97.1063 | 98.36 | 98.0937 | 97.8505 | 97.5811 | 97.28 | 96.9768 | 96.6832 | 96.4105 | 96.1158 | 90.4979 | 87.2105 | 84.7695 | 98.0095 | 97.7432 | 97.5 | 97.2305 | 96.9295 | 96.6263 | 96.3326 | 96.06 | 95.7653 | 89.5832 | 86.3916 | 84.0263
NURSLING GSP | SOUTHAMPTON C BSP | SOUTHAMPTON C BSP | MINIMUM HEADROOM | SU 41425 11999 | NO | YES | 0 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | SOUTHAMPTON C BSP | EE | [7 empty] | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | SOUTHAMPTON C BSP | HT | [7 empty] | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | SOUTHAMPTON C BSP | HE | [7 empty] | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | SOUTHAMPTON C BSP | FB | [7 empty] | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
LALEHAM GSP | STAINES BSP | STAINES BSP | MINIMUM HEADROOM | TQ 04585 72135 | NO | YES | 105.3158 | 190.84 | 188.2463 | 180.1347 | 174.6032 | 169.8284 | 201.5495 | 196.2842 | 190.9221 | 185.4926 | 154.3126 | 133.8537 | 121.2842 | 176.3158 | 175.44 | 173.4253 | 166.8021 | 161.2053 | 191.9832 | 185.8095 | 179.5011 | 173.1084 | 134.8895 | 109.7779 | 95.1063 | 177.3411 | 176.4611 | 175.4863 | 174.16 | 170.1547 | 200.9305 | 194.7526 | 188.4421 | 182.0474 | 143.8116 | 118.6853 | 104.0021
|  | STAINES BSP | EE |  |  |  |  | 190.84 | 188.2463 | 180.1779 | 176.2453 | 172.5505 | 205.8547 | 202.2295 | 198.3716 | 194.6568 | 178.1389 | 168.8379 | 158.2242 | 176.3158 | 175.44 | 173.5021 | 168.8895 | 164.7032 | 197.4684 | 193.3168 | 188.8863 | 184.6263 | 164.0842 | 152.6358 | 139.4684 | 177.3411 | 176.4611 | 175.4863 | 174.16 | 172.3537 | 206.4011 | 202.2432 | 197.8116 | 193.5474 | 172.9821 | 161.5137 | 148.3274
|  | STAINES BSP | HT |  |  |  |  | 190.9053 | 188.7147 | 180.1347 | 174.6032 | 169.8284 | 201.5495 | 196.2842 | 190.9221 | 185.4926 | 154.3126 | 133.8537 | 121.2842 | 176.3789 | 175.5737 | 173.4253 | 166.8021 | 161.2053 | 191.9832 | 185.8095 | 179.5011 | 173.1084 | 134.8895 | 109.7779 | 95.1063 | 177.4084 | 176.6032 | 175.5453 | 174.1947 | 170.1547 | 200.9305 | 194.7526 | 188.4421 | 182.0474 | 143.8116 | 118.6853 | 104.0021
|  | STAINES BSP | HE |  |  |  |  | 191.0032 | 189.6821 | 181.9653 | 178.3189 | 174.8179 | 208.3863 | 205.0642 | 201.6011 | 198.2684 | 184.3558 | 176.8032 | 167.6674 | 176.4758 | 175.6379 | 174.7042 | 171.4253 | 167.4789 | 200.5537 | 196.7853 | 192.8463 | 189.0674 | 171.4747 | 162.0168 | 150.5379 | 177.5074 | 176.6684 | 175.7337 | 174.4358 | 172.6453 | 208.0968 | 205.7358 | 201.7947 | 198.0147 | 180.4116 | 170.9442 | 159.4568
|  | STAINES BSP | FB |  |  |  |  | 191.6453 | 191.2168 | 190.8337 | 190.4011 | 189.9221 | 225.9432 | 224.4874 | 223.0053 | 221.4284 | 213.9032 | 205.1316 | 196.5653 | 177.1179 | 176.6895 | 176.3063 | 175.8737 | 175.3947 | 212.0126 | 211.54 | 211.1053 | 210.6379 | 207.0253 | 196.2053 | 185.5568 | 178.1505 | 177.7221 | 177.3389 | 176.9063 | 176.4274 | 213.0453 | 212.5726 | 212.1379 | 211.6705 | 209.9579 | 205.1611 | 194.5084
MINETY GSP | STRATTON (RESERVE) BSP | STRATTON (RESERVE) BSP | MINIMUM HEADROOM | SU 17028 88748 | NO | YES | 109.7789 | 61.8611 | 60.8432 | 21.5853 | 20.7611 | 14.2021 | 10.1884 | 5.3021 | -12.4811 | -17.2053 | -116.3811 | -145.8032 | -161.6568 | 41.9958 | 40.9874 | -5.3621 | -6.2884 | -13.4674 | -17.98 | -23.5274 | -38.7042 | -44.0653 | -160.4084 | -194.7695 | -213.1895 | 44.0937 | 43.0758 | -3.1221 | -4.0463 | -11.2358 | -15.74 | -21.2737 | -39.7484 | -45.0979 | -161.0958 | -195.3558 | -213.7232
|  | STRATTON (RESERVE) BSP | EE |  |  |  |  | 62.5326 | 60.8484 | 54.9989 | 53.0716 | 18.4716 | 15.5316 | 11.7316 | -7.0116 | -10.9811 | -62.3526 | -73.8642 | -88.0432 | 42.8937 | 41.0084 | 34.2295 | 32.0989 | -8.4684 | -11.7484 | -16.0558 | -31.6358 | -36.1358 | -96.46 | -109.8758 | -126.4695 | 44.9789 | 43.0989 | 36.3358 | 34.2063 | -6.24 | -9.5095 | -13.8084 | -33.1432 | -37.6337 | -97.7895 | -111.1663 | -127.7095
|  | STRATTON (RESERVE) BSP | HT |  |  |  |  | 62.6526 | 60.8432 | 55.0737 | 52.7316 | 14.2021 | 10.1884 | 5.3021 | -12.4811 | -17.2053 | -116.3811 | -145.8032 | -161.6568 | 43.0263 | 40.9874 | 34.3211 | 31.7211 | -13.4674 | -17.98 | -23.5274 | -38.7042 | -44.0653 | -160.4084 | -194.7695 | -213.1895 | 45.1095 | 43.0758 | 36.4263 | 33.8326 | -11.2358 | -15.74 | -21.2737 | -39.7484 | -45.0979 | -161.0958 | -195.3558 | -213.7232
|  | STRATTON (RESERVE) BSP | HE |  |  |  |  | 63.4253 | 62.1084 | 56.5579 | 54.9011 | 20.5168 | 17.6958 | 14.0821 | 4.3737 | 0.58316 | -48.9611 | -59.3295 | -72.5179 | 43.8989 | 42.4305 | 35.9895 | 34.1705 | -6.1495 | -9.3 | -13.3905 | -22.1242 | -26.4221 | -84.7221 | -96.8811 | -112.3832 | 45.9821 | 44.5147 | 38.0926 | 36.2779 | -3.9211 | -7.0695 | -11.1484 | -21.3779 | -25.6663 | -83.8011 | -95.9232 | -111.3779
|  | STRATTON (RESERVE) BSP | FB |  |  |  |  | 61.8611 | 61.0189 | 21.5853 | 20.7611 | 19.7463 | 18.7442 | 17.4274 | 15.9737 | 14.2432 | 3.6126 | -6.6505 | -18.0832 | 41.9958 | 41.0484 | -5.3621 | -6.2884 | -7.4316 | -8.5547 | -10.0547 | -11.7189 | -13.7063 | -26.0421 | -38.0189 | -51.4253 | 44.0937 | 43.1463 | -3.1221 | -4.0463 | -5.1853 | -6.3158 | -7.8126 | -9.4705 | -11.4547 | -23.7558 | -35.7126 | -49.0758
MINETY GSP | STRATTON (MAIN) BSP | STRATTON (MAIN) BSP | MINIMUM HEADROOM | SU 17028 88748 | NO | YES | 50.8421 | 103.3179 | 102.7926 | 101.5621 | 100.0274 | 98.5821 | 95.8305 | 92.3316 | 88.7989 | 82.1937 | 75.7358 | 70.3253 | 65.2537 | 96.4263 | 95.1074 | 92.7547 | 90.9758 | 89.5421 | 86.2989 | 82.0958 | 77.8421 | 69.8695 | 62.6947 | 56.5926 | 50.8621 | 97.6158 | 96.3189 | 94.0137 | 92.2632 | 90.9368 | 87.7516 | 83.6305 | 79.4632 | 71.6716 | 64.62 | 58.6421 | 53.0263
|  | STRATTON (MAIN) BSP | EE |  |  |  |  | 103.3179 | 102.7926 | 101.5621 | 100.0274 | 98.8032 | 96.7074 | 93.9874 | 90.8842 | 86.3863 | 78.8147 | 74.9168 | 71.7758 | 96.4263 | 95.1074 | 92.7547 | 90.9758 | 89.6632 | 87.2221 | 83.9632 | 80.2242 | 74.6895 | 65.7716 | 61.3189 | 57.8958 | 97.6158 | 96.3189 | 94.0137 | 92.2632 | 90.9621 | 88.5611 | 85.3653 | 81.7 | 76.2874 | 67.5768 | 63.2232 | 59.9695
|  | STRATTON (MAIN) BSP | HT |  |  |  |  | 103.7253 | 103.1653 | 102.3011 | 100.8137 | 98.5821 | 95.8305 | 92.3316 | 88.7989 | 82.1937 | 75.7358 | 70.3253 | 65.2537 | 97.3558 | 95.4126 | 93.8358 | 92.1453 | 89.5421 | 86.2989 | 82.0958 | 77.8421 | 69.8695 | 62.6947 | 56.5926 | 50.8621 | 98.6189 | 96.7137 | 95.1632 | 93.4968 | 90.9368 | 87.7516 | 83.6305 | 79.4632 | 71.6716 | 64.62 | 58.6421 | 53.0263
|  | STRATTON (MAIN) BSP | HE |  |  |  |  | 103.5821 | 103.1421 | 102.5421 | 101.3674 | 100.2621 | 98.2695 | 95.6642 | 92.6611 | 88.2589 | 82.5411 | 79.6158 | 76.8874 | 97.2558 | 96.2579 | 94.16 | 92.5947 | 91.4274 | 89.1084 | 85.9968 | 82.3789 | 76.9674 | 69.9547 | 66.5726 | 63.4011 | 98.4316 | 97.4495 | 95.3916 | 93.8516 | 92.6916 | 90.4095 | 87.3579 | 83.8137 | 78.5189 | 71.6832 | 68.3811 | 65.2863
|  | STRATTON (MAIN) BSP | FB |  |  |  |  | 103.9874 | 103.6232 | 103.3884 | 103.1032 | 102.8137 | 102.5221 | 102.1368 | 101.0874 | 99.9737 | 93.8926 | 91.4558 | 89.3705 | 99.52 | 97.4211 | 96.8358 | 95.9084 | 95.2147 | 94.5347 | 93.4874 | 92.2063 | 90.8505 | 83.3126 | 80.3347 | 77.7516 | 99.2432 | 98.5926 | 98.0168 | 97.1074 | 96.4253 | 95.7547 | 94.7284 | 93.4747 | 92.1484 | 84.7811 | 81.8663 | 79.3432
MINETY GSP | SWINDON BSP | SWINDON BSP | MINIMUM HEADROOM | SU 12447 87062 | NO | YES | 3.3684 | 81.1716 | 79.4137 | 74.8032 | 71.8105 | 67.8042 | 63.4495 | 58.6042 | 53.9484 | 47.6632 | 35.8537 | 24.6137 | 16.6368 | 92.6884 | 91.9158 | 90.8737 | 87.5042 | 82.9968 | 78.0589 | 72.5126 | 67.2074 | 60.8968 | 47.4968 | 33.4747 | 23.9716 | 97.4758 | 96.7032 | 92.8789 | 89.7337 | 85.5274 | 80.7495 | 74.9926 | 69.4895 | 61.2495 | 48.2853 | 33.8211 | 24.3179
|  | SWINDON BSP | EE |  |  |  |  | 81.1716 | 79.4137 | 74.8032 | 71.8105 | 67.8042 | 63.4495 | 58.6042 | 53.9484 | 54.0747 | 42.1211 | 37.8789 | 32.2632 | 92.6884 | 91.9158 | 90.8737 | 87.5042 | 82.9968 | 78.0589 | 72.5126 | 67.2074 | 68.5695 | 54.0074 | 49.4537 | 42.6126 | 97.4758 | 96.7032 | 92.8789 | 89.7337 | 85.5274 | 80.7495 | 74.9926 | 69.4895 | 69.0358 | 54.3579 | 50.24 | 43.3979
|  | SWINDON BSP | HT |  |  |  |  | 81.5211 | 79.8779 | 75.1821 | 71.9611 | 73.7853 | 68.5432 | 62.7495 | 57.2484 | 47.6632 | 35.8537 | 24.6137 | 16.6368 | 92.7895 | 92.0389 | 91.0421 | 87.7147 | 91.1453 | 85.1884 | 78.5653 | 72.2895 | 60.8968 | 47.4968 | 33.4747 | 23.9716 | 97.5768 | 96.8263 | 93.2905 | 89.9105 | 92.4579 | 86.3021 | 79.4284 | 72.9168 | 61.2495 | 48.2853 | 33.8211 | 24.3179
|  | SWINDON BSP | HE |  |  |  |  | 82.3242 | 81.0011 | 76.7337 | 74.0211 | 70.1947 | 66.0453 | 61.4895 | 57.1189 | 57.5242 | 48.36 | 42.3232 | 38.1653 | 93.0411 | 92.3705 | 91.5505 | 90.0474 | 85.7558 | 81.0547 | 75.8547 | 70.8884 | 72.5821 | 61.42 | 53.6947 | 48.5295 | 97.8284 | 97.1579 | 94.9253 | 92.0811 | 88.0674 | 83.6958 | 78.4716 | 73.3253 | 73.2189 | 61.7737 | 53.8253 | 48.66
|  | SWINDON BSP | FB |  |  |  |  | 83.68 | 82.6863 | 81.6589 | 80.4147 | 78.9211 | 77.2653 | 75.3842 | 73.5747 | 71.7453 | 70.3411 | 66.0863 | 62.5305 | 93.4937 | 93.1011 | 92.7453 | 92.3484 | 91.9063 | 91.46 | 91.0284 | 89.4811 | 87.3684 | 86.9305 | 81.9968 | 77.8389 | 98.2811 | 97.8884 | 97.5326 | 97.1358 | 96.6937 | 95.5084 | 93.5105 | 91.5874 | 89.6421 | 88.0305 | 82.8905 | 78.5516
BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM BSP | MINIMUM HEADROOM | SU 52824 66435 | NO | YES | 24.2105 | 106.1305 | 194.6705 | 191.4211 | 169.0611 | 163.1463 | 141.5389 | 122.4568 | 115.2221 | 108.6842 | 89.8411 | 74.7189 | 66.2453 | 78.8116 | 165.1505 | 159.0242 | 132.6505 | 126.0263 | 100.5442 | 78.2632 | 70.2274 | 63.0105 | 44.1179 | 24.8705 | 15.4905 | 84.9042 | 171.1295 | 164.7684 | 138.2421 | 131.62 | 106.1284 | 83.8368 | 75.7989 | 68.5811 | 50.8274 | 30.4463 | 21.06
|  | THATCHAM BSP | EE |  |  |  |  | 106.1305 | 194.6705 | 191.4211 | 170.3063 | 165.6674 | 145.9011 | 128.4716 | 123.4705 | 119.0695 | 104.4632 | 103.1989 | 97.5463 | 78.8116 | 165.1505 | 159.0242 | 134.1253 | 129.0926 | 105.7926 | 85.2642 | 79.7958 | 75.0432 | 58.2211 | 59.1705 | 52.7547 | 84.9042 | 171.1295 | 164.7684 | 139.7158 | 134.6832 | 111.3737 | 90.8379 | 85.3695 | 80.6116 | 63.7926 | 65.8747 | 59.4547
|  | THATCHAM BSP | HT |  |  |  |  | 106.2053 | 194.8737 | 191.5737 | 169.0611 | 163.1463 | 141.5389 | 122.4568 | 115.2221 | 108.6842 | 89.8411 | 74.7189 | 66.2453 | 79.3674 | 165.5737 | 159.1968 | 132.6505 | 126.0263 | 100.5442 | 78.2632 | 70.2274 | 63.0105 | 44.1179 | 24.8705 | 15.4905 | 84.9789 | 171.5726 | 164.9526 | 138.2421 | 131.62 | 106.1284 | 83.8368 | 75.7989 | 68.5811 | 50.8274 | 30.4463 | 21.06
|  | THATCHAM BSP | HE |  |  |  |  | 106.4505 | 195.2063 | 193.3916 | 173.5937 | 169.2568 | 149.8874 | 132.9842 | 128.5821 | 124.7642 | 114.4811 | 107.4989 | 104.4074 | 80.6642 | 167.7179 | 162.2137 | 137.9832 | 133.3042 | 110.4611 | 90.5695 | 85.76 | 81.6421 | 69.5053 | 60.3126 | 56.7379 | 85.2253 | 173.8116 | 168.1 | 143.58 | 138.9011 | 116.0495 | 96.1537 | 91.3432 | 87.2211 | 75.08 | 65.3263 | 61.7495
|  | THATCHAM BSP | FB |  |  |  |  | 107.4084 | 196.8147 | 196.2716 | 195.6116 | 194.7737 | 177.4695 | 175.6105 | 173.8537 | 172.1305 | 165.9021 | 159.5979 | 155.9074 | 82.7863 | 170.8653 | 168.32 | 166.54 | 164.7526 | 142.1568 | 140.0526 | 138.0589 | 136.1137 | 129.1021 | 121.78 | 117.5032 | 86.1832 | 175.5895 | 174.3895 | 172.5537 | 170.7105 | 147.7537 | 145.6495 | 143.6547 | 141.7105 | 134.6979 | 127.3716 | 123.0937
MINETY GSP | TOOTHILL BSP | TOOTHILL BSP | MINIMUM HEADROOM | SU 13191 83945 | NO | YES | 41.0526 | 197.0274 | 194.6021 | 192.2074 | 150.4579 | 146.0674 | 141.2758 | 135.5253 | 129.8516 | 124.6084 | 92.0842 | 86.5242 | 81.9137 | 190.9821 | 187.9768 | 185.2095 | 136.1368 | 131.1242 | 125.6411 | 119.0274 | 112.4968 | 106.4989 | 68.6716 | 62.2105 | 56.9821 | 189.5832 | 186.5853 | 183.8274 | 134.9011 | 129.9011 | 124.4305 | 117.8347 | 111.3221 | 105.3505 | 67.6853 | 61.1758 | 55.9579
|  | TOOTHILL BSP | EE |  |  |  |  | 197.0274 | 194.6021 | 192.2074 | 150.4579 | 146.9463 | 142.8232 | 137.8126 | 132.6632 | 127.6674 | 105.3168 | 101.7442 | 98.4863 | 190.9821 | 187.9768 | 185.2095 | 136.1368 | 132.1432 | 127.4242 | 121.6495 | 115.7147 | 109.9632 | 83.8021 | 79.8242 | 76.0716 | 189.5832 | 186.5853 | 183.8274 | 134.9011 | 130.9168 | 126.2074 | 120.4474 | 114.5316 | 108.7937 | 82.7253 | 78.8074 | 75.0663
|  | TOOTHILL BSP | HT |  |  |  |  | 197.2126 | 194.8368 | 192.4316 | 150.6305 | 146.0674 | 141.2758 | 135.5253 | 129.8516 | 124.6084 | 92.0842 | 86.5242 | 81.9137 | 191.2032 | 188.2642 | 185.4768 | 136.3516 | 131.1242 | 125.6411 | 119.0274 | 112.4968 | 106.4989 | 68.6716 | 62.2105 | 56.9821 | 189.6526 | 186.8726 | 184.0895 | 135.1147 | 129.9011 | 124.4305 | 117.8347 | 111.3221 | 105.3505 | 67.6853 | 61.1758 | 55.9579
|  | TOOTHILL BSP | HE |  |  |  |  | 197.4463 | 195.4379 | 193.2884 | 151.7053 | 148.3021 | 144.2695 | 139.3695 | 134.3137 | 129.4147 | 108.5895 | 105.62 | 103.1295 | 191.7095 | 188.9789 | 186.4358 | 137.5505 | 133.6832 | 129.0653 | 123.4221 | 117.5979 | 111.9568 | 87.4547 | 84.0032 | 81.0979 | 189.7895 | 187.5884 | 185.0484 | 136.3116 | 132.4526 | 127.8453 | 122.2168 | 116.4095 | 110.7842 | 86.3516 | 82.9105 | 80.0105
|  | TOOTHILL BSP | FB |  |  |  |  | 197.7432 | 197.4853 | 196.7979 | 195.6968 | 194.3747 | 192.9179 | 152.2179 | 150.0474 | 147.6821 | 139.4453 | 136.8537 | 134.7979 | 192.2989 | 191.8611 | 190.6758 | 189.3168 | 187.6832 | 186.0063 | 138.1021 | 135.5832 | 132.8358 | 123.2811 | 120.3105 | 117.9411 | 190.0295 | 189.8221 | 189.2768 | 187.9232 | 186.2937 | 184.6211 | 136.8632 | 134.3495 | 131.6105 | 122.0811 | 119.1189 | 116.7558
IVER 132KV GSP | UPTON BSP | UPTON BSP | MINIMUM HEADROOM | TQ 00838 79445 | NO | YES | 0 | 70.4179 | 69.7811 | 67.9084 | 66.8011 | 65.48 | 64.26 | 62.9684 | 61.7821 | 60.4926 | 57.6253 | 55.3295 | 53.2947 | 64.9589 | 64.0716 | 61.2853 | 59.8158 | 58.1116 | 56.5884 | 54.9453 | 53.4705 | 51.8189 | 48.2537 | 45.2053 | 42.5 | 67.0642 | 66.8968 | 64.9137 | 63.5105 | 61.8737 | 60.4084 | 58.8274 | 57.3789 | 55.7242 | 52.1505 | 49.0937 | 46.38
|  | UPTON BSP | EE |  |  |  |  | 70.5632 | 69.7811 | 67.9084 | 66.8011 | 65.48 | 64.3811 | 63.3253 | 62.4653 | 61.5126 | 60.0453 | 58.5558 | 57.3 | 65.1253 | 64.0716 | 61.2853 | 59.8158 | 58.1116 | 56.76 | 55.4526 | 54.4705 | 53.3295 | 51.2905 | 49.1505 | 47.3389 | 67.5505 | 67.2084 | 64.9137 | 63.5105 | 61.8737 | 60.5684 | 59.3074 | 58.3474 | 57.24 | 55.1937 | 53.0474 | 51.2274
|  | UPTON BSP | HT |  |  |  |  | 70.6558 | 69.9189 | 68.0032 | 66.8368 | 65.4853 | 64.26 | 62.9684 | 61.7821 | 60.4926 | 57.6253 | 55.3295 | 53.2947 | 65.2674 | 64.2779 | 61.4432 | 59.8947 | 58.1179 | 56.5884 | 54.9453 | 53.4705 | 51.8189 | 48.2537 | 45.2053 | 42.5 | 67.5642 | 67.2368 | 65.06 | 63.5821 | 61.8821 | 60.4084 | 58.8274 | 57.3789 | 55.7242 | 52.1505 | 49.0937 | 46.38
|  | UPTON BSP | HE |  |  |  |  | 70.8789 | 70.2147 | 68.4421 | 67.4158 | 66.1442 | 65.1232 | 64.1516 | 63.3811 | 62.5084 | 62.0326 | 61.1684 | 60.4495 | 65.6 | 64.7295 | 62.0979 | 60.7589 | 59.1368 | 57.8968 | 56.7305 | 55.8937 | 54.8863 | 54.0905 | 52.7547 | 51.6305 | 67.6105 | 67.2789 | 65.6758 | 64.3937 | 62.8347 | 61.6337 | 60.5053 | 59.6789 | 58.6958 | 57.9589 | 56.6611 | 55.5337
|  | UPTON BSP | FB |  |  |  |  | 70.4179 | 69.9989 | 69.6947 | 69.26 | 68.7884 | 68.3842 | 68 | 67.7211 | 67.3726 | 66.1884 | 65.9968 | 65.1284 | 64.9589 | 64.3842 | 63.9842 | 63.3842 | 62.7368 | 62.2021 | 61.6905 | 61.3474 | 60.8958 | 59.3905 | 59.0453 | 57.7895 | 67.0642 | 66.8968 | 66.7484 | 66.5789 | 66.3674 | 65.8558 | 65.3674 | 65.0358 | 64.6021 | 63.1558 | 62.7337 | 61.5484
NURSLING GSP | VELMORE BSP | VELMORE BSP | MINIMUM HEADROOM | SU 42855 19215 | NO | YES | 60 | 60.8779 | 149.8663 | 148.7453 | 126.2979 | 121.4642 | 116.2158 | 110.6716 | 104.9863 | 99.1853 | 83.8221 | 74.4874 | 66.0842 | 50.3011 | 139.2895 | 137.9105 | 109.3147 | 103.9442 | 98.1147 | 91.9337 | 85.5768 | 79.0811 | 61.7811 | 51.2579 | 41.7663 | 39.7705 | 128.7589 | 127.6379 | 102.9695 | 97.6568 | 91.8916 | 85.7779 | 79.4947 | 73.0747 | 56.0084 | 45.6137 | 36.2411
|  | VELMORE BSP | EE |  |  |  |  | 60.8779 | 149.8663 | 148.7758 | 126.6389 | 122.4411 | 117.9358 | 113.5042 | 109.4779 | 105.6495 | 96.2611 | 89.7105 | 83.9568 | 50.3011 | 139.2895 | 137.9105 | 109.6979 | 105.1116 | 100.1337 | 95.2074 | 90.7779 | 86.5737 | 75.7295 | 68.2074 | 61.5737 | 39.7705 | 128.7589 | 127.6663 | 103.3484 | 98.8021 | 93.8758 | 89.0042 | 84.6158 | 80.4526 | 69.7884 | 62.3768 | 55.8368
|  | VELMORE BSP | HT |  |  |  |  | 60.9263 | 149.9874 | 148.7453 | 126.2979 | 121.4642 | 116.2158 | 110.6716 | 104.9863 | 99.1853 | 83.8221 | 74.4874 | 66.0842 | 50.3495 | 139.4105 | 138.1684 | 109.3147 | 103.9442 | 98.1147 | 91.9337 | 85.5768 | 79.0811 | 61.7811 | 51.2579 | 41.7663 | 39.8189 | 128.88 | 127.6379 | 102.9695 | 97.6568 | 91.8916 | 85.7779 | 79.4947 | 73.0747 | 56.0084 | 45.6137 | 36.2411
|  | VELMORE BSP | HE |  |  |  |  | 61.1453 | 150.2126 | 149.1979 | 129.1284 | 125.3274 | 121.1695 | 117.0968 | 113.4484 | 109.9905 | 103.7242 | 99.1926 | 95.1211 | 50.5684 | 139.6358 | 138.6211 | 112.72 | 108.4274 | 103.8389 | 99.3389 | 95.3516 | 91.5811 | 84.1316 | 78.8263 | 74.0432 | 40.0379 | 129.1053 | 128.0905 | 106.3295 | 102.0747 | 97.5316 | 93.0789 | 89.1263 | 85.3895 | 78.0674 | 72.8453 | 68.14
|  | VELMORE BSP | FB |  |  |  |  | 61.8316 | 151.3789 | 149.5347 | 149.0768 | 148.5653 | 148.0484 | 146.3832 | 125.5084 | 123.8916 | 117.5842 | 113.1242 | 109.3537 | 51.2547 | 140.8021 | 139.1779 | 138.72 | 137.9526 | 135.9442 | 133.8832 | 107.3358 | 105.5168 | 98.3842 | 93.2926 | 88.9453 | 40.7242 | 130.2716 | 128.1074 | 127.6495 | 127.1379 | 126.6211 | 126.1232 | 100.4832 | 98.6874 | 91.6432 | 86.6189 | 82.3337
MANNINGTON GSP | WAREHAM BSP | WAREHAM BSP | MINIMUM HEADROOM | SY 91548 88451 | NO | YES | 0 | 28.9353 | 42.4492 | 41.6124 | 40.4355 | 39.0345 | 37.5029 | 35.9776 | 32.5661 | 26.5808 | 20.4639 | 17.2892 | 10.0524 | 24.0232 | 36.5816 | 35.5521 | 33.8079 | 32.3911 | 30.5174 | 28.6521 | 24.1226 | 15.9984 | 9.0911 | 5.5342 | -2.8163 | 23.9516 | 37.4137 | 37.0411 | 34.94 | 34.6042 | 32.7263 | 30.8474 | 26.2726 | 18.1179 | 11.2074 | 7.6484 | -0.70421
|  | WAREHAM BSP | EE |  |  |  |  | 28.9353 | 42.4492 | 41.7345 | 40.8903 | 39.8545 | 38.8682 | 37.8429 | 35.9008 | 32.7282 | 29.8587 | 27.885 | 24.0313 | 24.0232 | 36.5816 | 35.7268 | 34.7395 | 33.5637 | 32.4395 | 31.2384 | 28.7563 | 24.5311 | 20.6753 | 18.0374 | 13.1753 | 23.9516 | 37.4137 | 37.0411 | 36.5442 | 35.8011 | 34.6705 | 33.4611 | 30.9547 | 26.6863 | 22.7905 | 20.1526 | 15.2884
|  | WAREHAM BSP | HT |  |  |  |  | 29.0237 | 42.5166 | 41.6124 | 40.4355 | 39.0345 | 37.5029 | 35.9776 | 32.5661 | 26.5808 | 20.4639 | 17.2892 | 10.0524 | 24.1379 | 36.6563 | 35.5521 | 34.1089 | 32.3911 | 30.5174 | 28.6521 | 24.1226 | 15.9984 | 9.0911 | 5.5342 | -2.8163 | 23.9726 | 37.4589 | 37.0463 | 36.3432 | 34.6126 | 32.7263 | 30.8474 | 26.2726 | 18.1179 | 11.2074 | 7.6484 | -0.70421
|  | WAREHAM BSP | HE |  |  |  |  | 29.3163 | 42.9734 | 42.3808 | 41.6324 | 40.6618 | 39.7734 | 38.9018 | 37.1197 | 34.0997 | 32.4303 | 31.1629 | 28.2492 | 24.5221 | 37.2711 | 36.5805 | 35.7258 | 34.6405 | 33.6384 | 32.6574 | 30.3953 | 26.3911 | 24.0226 | 22.2847 | 18.1763 | 24.04 | 37.5253 | 37.1716 | 36.6842 | 36.0021 | 35.3853 | 34.7832 | 32.6168 | 28.5695 | 26.1726 | 24.4158 | 20.2958
|  | WAREHAM BSP | FB |  |  |  |  | 29.6911 | 43.5134 | 43.2197 | 40.8513 | 40.505 | 40.1534 | 39.8018 | 39.4629 | 39.1092 | 37.6261 | 36.3176 | 35.1766 | 24.9568 | 37.8732 | 37.5174 | 33.8079 | 33.3911 | 32.9658 | 32.5416 | 32.1289 | 31.7005 | 29.8658 | 28.1626 | 26.6447 | 24.2716 | 37.9158 | 37.7758 | 34.94 | 34.6042 | 34.2632 | 33.9211 | 33.5926 | 33.2516 | 31.6411 | 29.92 | 28.3884
MELKSHAM GSP | WEST GRAFTON BSP | WEST GRAFTON BSP | MINIMUM HEADROOM | SU 24302 59215 | NO | YES | 15 | 56.6474 | 55.68 | 54.3611 | 52.6042 | 50.7137 | 48.7611 | 46.6747 | 44.2358 | 41.6168 | 33.4042 | 28.7063 | 25.2758 | 49.3674 | 48.16 | 46.6768 | 44.7084 | 42.6042 | 40.4389 | 38.1168 | 35.3737 | 32.42 | 23.0516 | 17.7032 | 13.8263 | 41.5579 | 40.3747 | 38.9305 | 37.0179 | 34.9642 | 32.8547 | 30.5926 | 27.9274 | 25.0589 | 15.9874 | 10.8074 | 7.0432
|  | WEST GRAFTON BSP | EE |  |  |  |  | 56.6474 | 55.68 | 54.3611 | 52.7189 | 51.08 | 49.6021 | 48.0505 | 46.2947 | 44.4768 | 38.5863 | 34.9337 | 32.5326 | 49.3674 | 48.16 | 46.6768 | 44.8389 | 43.0421 | 41.4242 | 39.7084 | 37.7589 | 35.7305 | 28.8884 | 24.6737 | 21.9116 | 41.5579 | 40.3747 | 38.9305 | 37.1411 | 35.3874 | 33.8042 | 32.1316 | 30.2305 | 28.2568 | 21.6547 | 17.5842 | 14.9168
|  | WEST GRAFTON BSP | HT |  |  |  |  | 56.6874 | 55.8916 | 54.4853 | 52.6042 | 50.7137 | 48.7611 | 46.6747 | 44.2358 | 41.6168 | 33.4042 | 28.7063 | 25.2758 | 49.5284 | 48.4 | 46.8242 | 44.7084 | 42.6042 | 40.4389 | 38.1168 | 35.3737 | 32.42 | 23.0516 | 17.7032 | 13.8263 | 41.7168 | 40.6063 | 39.0737 | 37.0179 | 34.9642 | 32.8547 | 30.5926 | 27.9274 | 25.0589 | 15.9874 | 10.8074 | 7.0432
|  | WEST GRAFTON BSP | HE |  |  |  |  | 56.8 | 56.3432 | 55.1716 | 53.6547 | 52.0979 | 50.7305 | 49.34 | 47.7516 | 46.0905 | 41.4842 | 38.6021 | 36.86 | 49.9084 | 48.9095 | 47.6032 | 45.9095 | 44.2095 | 42.7168 | 41.1937 | 39.4379 | 37.5958 | 32.1705 | 28.8032 | 26.7716 | 42.0905 | 41.1063 | 39.8284 | 38.18 | 36.5158 | 35.0558 | 33.5663 | 31.8547 | 30.0568 | 24.8411 | 21.5989 | 19.6389
|  | WEST GRAFTON BSP | FB |  |  |  |  | 57.0726 | 56.86 | 56.6179 | 55.9579 | 55.3779 | 54.7895 | 54.1632 | 53.4274 | 52.5863 | 48.8305 | 46.5074 | 44.9611 | 50.4242 | 49.8084 | 49.1853 | 48.4442 | 47.7947 | 47.1337 | 46.4295 | 45.5926 | 44.6347 | 40.3326 | 37.6621 | 35.8842 | 42.6 | 41.9926 | 41.38 | 40.6558 | 40.0232 | 39.38 | 38.6958 | 37.8853 | 36.9589 | 32.7947 | 30.2137 | 28.4947
NURSLING GSP | WINCHESTER BSP | WINCHESTER BSP | MINIMUM HEADROOM | SU 44965 26671 | NO | YES | 75.8074 | 112.7663 | 111.8537 | 108.7453 | 106.3442 | 193.0926 | 178.6011 | 140.9737 | 137.2284 | 133.4411 | 69.0389 | 19.3263 | -0.37474 | 105.0368 | 104.7305 | 104.2295 | 101.6274 | 187.8495 | 170.0021 | 124.9316 | 120.6916 | 116.4 | 40.7958 | -17.6989 | -40.7168 | 102.2526 | 101.9463 | 101.6705 | 100.7147 | 186.9653 | 169.1126 | 124.0284 | 119.7884 | 115.4958 | 39.9 | -18.4263 | -41.3779
|  | WINCHESTER BSP | EE |  |  |  |  | 113.7095 | 111.8842 | 108.7453 | 106.7211 | 194.2495 | 181.1274 | 145.1432 | 143.1032 | 141.0821 | 112.3474 | 91.4 | 71.7242 | 107.5463 | 106.8832 | 104.2295 | 102.0579 | 189.3253 | 173.1011 | 129.9147 | 127.7 | 125.5053 | 91.4011 | 66.8653 | 43.7653 | 104.4126 | 103.7495 | 103.0368 | 101.1632 | 188.4379 | 172.2137 | 129.0105 | 126.7937 | 124.6011 | 90.4821 | 65.9547 | 42.8526
|  | WINCHESTER BSP | HT |  |  |  |  | 113.9432 | 112.1326 | 108.9337 | 106.3442 | 193.0926 | 178.6011 | 140.9737 | 137.2284 | 133.4411 | 69.0389 | 19.3263 | -0.37474 | 107.5789 | 106.9684 | 104.4463 | 101.6274 | 187.8495 | 170.0021 | 124.9316 | 120.6916 | 116.4 | 40.7958 | -17.6989 | -40.7168 | 104.4474 | 103.8358 | 103.0284 | 100.7147 | 186.9653 | 169.1126 | 124.0284 | 119.7884 | 115.4958 | 39.9 | -18.4263 | -41.3779
|  | WINCHESTER BSP | HE |  |  |  |  | 114.5 | 112.9737 | 110.1074 | 108.3021 | 195.9832 | 183.0695 | 147.4263 | 145.6589 | 143.9095 | 117.4905 | 94.9326 | 76.4411 | 107.6979 | 107.0716 | 105.7474 | 103.8221 | 191.3674 | 175.4547 | 132.5895 | 130.7042 | 128.8379 | 97.2189 | 69.6389 | 47.8126 | 104.5663 | 103.94 | 103.2695 | 102.3263 | 190.5042 | 174.5684 | 131.6895 | 129.8063 | 127.9368 | 96.3084 | 68.1442 | 46.3505
|  | WINCHESTER BSP | FB |  |  |  |  | 112.7663 | 111.8537 | 111.0484 | 110.1916 | 199.3137 | 201.4095 | 200.6421 | 199.92 | 199.1642 | 193.4158 | 179.9674 | 163.9137 | 105.0368 | 104.7305 | 104.4547 | 104.1474 | 193.8032 | 196.5842 | 196.2484 | 195.6 | 194.7853 | 188.1263 | 171.4084 | 152.1505 | 102.2526 | 101.9463 | 101.6705 | 101.3632 | 191.0189 | 193.4526 | 193.1168 | 192.8042 | 192.4695 | 187.2442 | 170.5211 | 151.2568
COWLEY GSP | WITNEY BSP | WITNEY BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | YES | 95.7895 | 78.6474 | 61.0989 | 148.2863 | 144.5821 | 140.2747 | 135.8158 | 132.0853 | 126.8979 | 123.8189 | 103.7295 | 95.9853 | 87.2326 | 53.9 | 33.3326 | 120.1979 | 116.0568 | 111.2474 | 106.2905 | 102.1895 | 95.0053 | 93.0253 | 70.1968 | 61.4895 | 51.3642 | 61.64 | 41.7905 | 128.7305 | 124.6926 | 120.0032 | 115.1663 | 111.1537 | 104.18 | 102.2021 | 79.4737 | 70.7589 | 60.5263
|  | WITNEY BSP | EE |  |  |  |  | 81.8905 | 65.7579 | 153.6042 | 150.9316 | 147.3968 | 143.9105 | 140.8716 | 137.8295 | 134.8432 | 124.3274 | 119.8779 | 114.4958 | 57.7368 | 38.8463 | 126.4653 | 123.5253 | 119.6505 | 115.8168 | 112.4779 | 109.1505 | 105.8821 | 93.6937 | 88.8168 | 82.6211 | 65.3347 | 47.0989 | 134.7726 | 131.8937 | 128.1011 | 124.3505 | 121.0811 | 117.8221 | 114.6189 | 102.8274 | 98.0926 | 91.8937
|  | WITNEY BSP | HT |  |  |  |  | 78.6474 | 61.0989 | 148.2863 | 144.5821 | 140.2747 | 135.8158 | 132.0853 | 127.9621 | 123.8189 | 103.7295 | 95.9853 | 87.2326 | 53.9 | 33.3326 | 120.1979 | 116.0568 | 111.2474 | 106.2905 | 102.1895 | 97.6189 | 93.0253 | 70.1968 | 61.4895 | 51.3642 | 61.64 | 41.7905 | 128.7305 | 124.6926 | 120.0032 | 115.1663 | 111.1537 | 106.6895 | 102.2021 | 79.4737 | 70.7589 | 60.5263
|  | WITNEY BSP | HE |  |  |  |  | 83.0411 | 67.3389 | 155.5505 | 153.1884 | 149.8937 | 146.6863 | 144.0084 | 141.3558 | 138.7474 | 131.1168 | 127.8842 | 124 | 59.0421 | 40.6495 | 128.6874 | 126.1021 | 122.5084 | 118.9832 | 116.0758 | 113.2011 | 110.3758 | 101.3653 | 97.6105 | 93.0684 | 66.6063 | 48.8526 | 136.9316 | 134.3989 | 130.8726 | 127.4263 | 124.5737 | 121.7516 | 118.9758 | 110.2968 | 106.6663 | 102.2453
|  | WITNEY BSP | FB |  |  |  |  | 111.0758 | 96.4368 | 185.5147 | 184.4432 | 183.1758 | 154.7663 | 153.5568 | 126.8979 | 125.6442 | 121.7526 | 118.26 | 114.7874 | 92.8537 | 74.8221 | 163.7958 | 162.5979 | 161.1768 | 127.7368 | 126.3884 | 95.0053 | 93.5958 | 89.2747 | 85.3084 | 81.3053 | 102.3347 | 81.8168 | 170.8158 | 169.6484 | 168.2653 | 136.0189 | 134.7063 | 104.18 | 102.7716 | 98.4505 | 94.4811 | 90.4758
FLEET-BRAMLEY GSP | WOKINGHAM BSP | WOKINGHAM BSP | MINIMUM HEADROOM | SU 79589 67665 | NO | YES | 0.13789 | 100.9032 | 100.48 | 99.98 | 99.2916 | 98.4632 | 97.5347 | 95.6779 | 93.7432 | 91.7958 | 87.3642 | 84.6874 | 81.5874 | 96.1884 | 95.3516 | 94.2337 | 92.6611 | 90.7737 | 88.4789 | 86.3526 | 84.1274 | 81.8821 | 76.8947 | 73.9011 | 70.3726 | 98.0653 | 97.2389 | 96.1179 | 94.5432 | 92.6484 | 90.3484 | 88.2179 | 85.9853 | 83.7337 | 78.7326 | 75.7326 | 72.1916
|  | WOKINGHAM BSP | EE |  |  |  |  | 100.9032 | 100.48 | 99.9905 | 99.36 | 98.5263 | 97.6968 | 96.9084 | 96.0937 | 94.6884 | 92.2389 | 90.6179 | 88.6021 | 96.1884 | 95.3516 | 94.2832 | 93.1663 | 91.8663 | 90.3253 | 88.6958 | 87.0337 | 85.4547 | 82.5011 | 80.5779 | 78.2232 | 98.0653 | 97.2389 | 96.1695 | 95.0495 | 93.7484 | 92.2042 | 90.5695 | 88.9032 | 87.3211 | 84.3547 | 82.4253 | 80.0642
|  | WOKINGHAM BSP | HT |  |  |  |  | 100.9211 | 100.5263 | 99.98 | 99.2916 | 98.4632 | 97.5347 | 95.6779 | 93.7432 | 91.7958 | 87.3642 | 84.6874 | 81.5874 | 96.3558 | 95.5242 | 94.2337 | 92.6611 | 90.7737 | 88.4789 | 86.3526 | 84.1274 | 81.8821 | 76.8947 | 73.9011 | 70.3726 | 98.2284 | 97.4095 | 96.1179 | 94.5432 | 92.6484 | 90.3484 | 88.2179 | 85.9853 | 83.7337 | 78.7326 | 75.7326 | 72.1916
|  | WOKINGHAM BSP | HE |  |  |  |  | 100.9905 | 100.6189 | 100.1747 | 99.5674 | 98.7484 | 97.9611 | 97.1842 | 96.4 | 95.6295 | 94.9516 | 94.0663 | 92.7432 | 96.6 | 96.14 | 95.2611 | 94.3032 | 93.1084 | 91.7011 | 90.2463 | 88.7621 | 87.3547 | 85.7263 | 84.6379 | 82.9958 | 98.4484 | 98.0105 | 97.1421 | 96.1916 | 94.9947 | 93.5842 | 92.1274 | 90.64 | 89.2284 | 87.5937 | 86.5021 | 84.8505
|  | WOKINGHAM BSP | FB |  |  |  |  | 101.2863 | 101.1095 | 100.9484 | 100.7568 | 100.5389 | 100.3105 | 100.0821 | 99.8684 | 99.64 | 98.8253 | 98.3621 | 97.1221 | 96.8958 | 96.7189 | 96.3716 | 95.9379 | 95.4632 | 94.8747 | 94.2316 | 93.5642 | 92.8947 | 90.7453 | 89.3684 | 87.8147 | 98.7442 | 98.5674 | 98.2453 | 97.8168 | 97.3484 | 96.7611 | 96.1168 | 95.4474 | 94.7758 | 92.62 | 91.24 | 89.6811
FAWLEY GSP | WOOTTON COMMON BSP | WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ52785 90310 | NO | YES | 50.88 | 93.3611 | 90.6558 | 87.7411 | 85.0453 | 62.6463 | 54.7463 | 48.3779 | 40.8368 | 31.0284 | 11.6947 | -0.058947 | -10.3 | 78.6253 | 75.6568 | 72.4674 | 69.8474 | 46.8326 | 37.9663 | 30.8958 | 22.44 | 11.3147 | -10.4411 | -23.6568 | -35.1611 | 77.4137 | 74.4779 | 71.3263 | 68.4526 | 45.5232 | 36.8021 | 29.8326 | 21.5116 | 10.5832 | -10.8179 | -23.8189 | -35.1421
|  | WOOTTON COMMON BSP | EE |  |  |  |  | 93.3611 | 90.6558 | 87.7411 | 85.9368 | 65.1158 | 59.8832 | 55.2105 | 50.0653 | 43.9221 | 31.7105 | 23.1674 | 16.0653 | 78.6253 | 75.6568 | 72.4674 | 70.8968 | 49.7716 | 44.0242 | 38.9137 | 33.2568 | 26.4168 | 12.3653 | 2.5874 | -5.5537 | 77.4137 | 74.4779 | 71.3263 | 69.4684 | 48.3863 | 42.7116 | 37.6642 | 32.0789 | 25.34 | 11.5474 | 1.9442 | -6.0516
|  | WOOTTON COMMON BSP | HT |  |  |  |  | 93.8211 | 91.1958 | 87.8253 | 85.0453 | 62.6463 | 54.7463 | 48.3779 | 40.8368 | 31.0284 | 11.6947 | -0.058947 | -10.3 | 79.1505 | 76.2611 | 72.5547 | 69.8474 | 46.8326 | 37.9663 | 30.8958 | 22.44 | 11.3147 | -10.4411 | -23.6568 | -35.1611 | 77.9326 | 75.0768 | 71.4179 | 68.4526 | 45.5232 | 36.8021 | 29.8326 | 21.5116 | 10.5832 | -10.8179 | -23.8189 | -35.1421
|  | WOOTTON COMMON BSP | HE |  |  |  |  | 94.8821 | 92.7874 | 90.4411 | 89.1021 | 85.3116 | 63.7684 | 59.7189 | 55.2053 | 49.6558 | 41.9326 | 36.0926 | 31.2537 | 80.3579 | 78.0905 | 75.5526 | 74.5116 | 70.4642 | 48.4537 | 44.0642 | 39.1337 | 32.9811 | 23.8695 | 17.0632 | 11.4126 | 79.1211 | 76.88 | 74.3705 | 73.0368 | 69.0326 | 47.0895 | 42.7495 | 37.8811 | 31.8168 | 22.9126 | 16.2474 | 10.7168
|  | WOOTTON COMMON BSP | FB |  |  |  |  | 114.6842 | 114.1589 | 112.8958 | 91.1926 | 89.7358 | 88.2368 | 86.5895 | 84.9474 | 83.26 | 75.8453 | 72.0989 | 67.4779 | 101.4221 | 100.8968 | 99.6884 | 75.4695 | 73.86 | 72.2021 | 70.3695 | 68.5305 | 66.6495 | 58.3063 | 54.3432 | 49.0421 | 102.4316 | 101.9063 | 100.3705 | 74.2432 | 72.6568 | 71.0232 | 69.2179 | 67.4084 | 65.5558 | 57.3516 | 53.1737 | 47.9726
LOVEDEAN GSP | WYMERING BSP | WYMERING BSP | MINIMUM HEADROOM | SU 64948 05441 | NO | YES | 5.8305 | 91.0747 | 90.8021 | 90.5905 | 90.3947 | 90.1011 | 97.9211 | 96.8032 | 95.6347 | 94.4674 | 89.8716 | 87.8463 | 86.1263 | 90.5653 | 90.2937 | 90.0821 | 89.8863 | 89.5926 | 101.2768 | 100.1589 | 98.9905 | 97.8232 | 93.0789 | 90.7737 | 88.8189 | 89.7347 | 89.4337 | 89.2032 | 88.9926 | 88.6684 | 97.2979 | 96.0411 | 94.7221 | 93.4032 | 88.1611 | 85.8558 | 83.8989
|  | WYMERING BSP | EE |  |  |  |  | 101.7495 | 101.2484 | 100.7516 | 100.1663 | 99.4747 | 98.6158 | 97.7358 | 96.8505 | 95.9768 | 92.4347 | 91.08 | 89.9074 | 104.4947 | 104.2832 | 104.0463 | 103.5232 | 102.8305 | 101.9716 | 101.0905 | 100.2063 | 99.3326 | 95.8232 | 94.4295 | 93.0653 | 101.5821 | 101.02 | 100.4716 | 99.8326 | 99.0884 | 98.1389 | 97.1579 | 96.1747 | 95.2032 | 91.0221 | 89.5126 | 88.1463
|  | WYMERING BSP | HT |  |  |  |  | 101.8316 | 101.3484 | 100.7695 | 100.0137 | 99.0547 | 97.9211 | 96.8032 | 95.6347 | 94.4674 | 89.8716 | 87.8463 | 86.1263 | 104.5105 | 104.3137 | 104.0568 | 103.3695 | 102.4105 | 101.2768 | 100.1589 | 98.9905 | 97.8232 | 93.0789 | 90.7737 | 88.8189 | 101.6779 | 101.1368 | 100.4895 | 99.6474 | 98.5737 | 97.2979 | 96.0411 | 94.7221 | 93.4032 | 88.1611 | 85.8558 | 83.8989
|  | WYMERING BSP | HE |  |  |  |  | 102.0105 | 101.6063 | 101.1905 | 100.6747 | 100.0221 | 99.3137 | 98.6147 | 97.9179 | 97.2316 | 94.2168 | 93.5042 | 92.7716 | 104.5358 | 104.3295 | 104.0947 | 103.7747 | 103.3305 | 102.6705 | 101.9716 | 101.2747 | 100.5874 | 97.5726 | 96.8589 | 96.1263 | 101.8863 | 101.4442 | 100.9916 | 100.4347 | 99.7389 | 98.9695 | 98.2095 | 97.4537 | 96.7084 | 93.0684 | 92.2242 | 91.3516
|  | WYMERING BSP | FB |  |  |  |  | 91.0747 | 90.8021 | 90.5905 | 90.3947 | 90.1011 | 101.1168 | 100.8095 | 100.5 | 100.1768 | 98.8232 | 96.8211 | 96.0263 | 90.5653 | 90.2937 | 90.0821 | 89.8863 | 89.5926 | 104.1253 | 104.0063 | 103.8558 | 103.5337 | 102.1789 | 100.1768 | 99.3811 | 89.7347 | 89.4337 | 89.2032 | 88.9926 | 88.6684 | 100.8958 | 100.5495 | 100.1989 | 99.8347 | 98.2916 | 95.9284 | 95.0021
COWLEY GSP | YARNTON BSP | YARNTON BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | YES | 123.6726 | 95.4 | 211.5116 | 205.0558 | 200.3579 | 175.0189 | 158.1453 | 141.1632 | 133.5495 | 122.7537 | 79.2042 | 52.7137 | 42.2758 | 80.9621 | 196.4158 | 188.8063 | 183.3726 | 153.1695 | 134.1916 | 114.4758 | 105.7979 | 93.36 | 42.8811 | 12.0853 | -0.010526 | 82.3989 | 197.8558 | 190.2611 | 184.8347 | 154.6958 | 135.7421 | 116.0611 | 107.4021 | 94.9821 | 44.6189 | 13.8779 | 1.7737
|  | YARNTON BSP | EE |  |  |  |  | 98.0011 | 215.7295 | 208.2116 | 204.3053 | 198.7642 | 168.8674 | 154.3295 | 147.6105 | 139.7726 | 111.6779 | 99.0158 | 91.2379 | 84.1211 | 201.5284 | 192.6168 | 188.1189 | 181.7411 | 146.7916 | 129.9021 | 122.2347 | 113.2389 | 80.5358 | 65.8053 | 56.7853 | 85.5495 | 202.9611 | 194.0632 | 189.5726 | 183.2021 | 148.3147 | 131.4558 | 123.8011 | 114.82 | 82.2063 | 67.5053 | 58.4989
|  | YARNTON BSP | HT |  |  |  |  | 95.4 | 211.5116 | 205.0558 | 200.3579 | 192.3853 | 158.1453 | 141.1632 | 133.5495 | 122.7537 | 79.2042 | 52.7137 | 42.2758 | 80.9621 | 196.4158 | 188.8063 | 183.3726 | 174.2116 | 134.1916 | 114.4758 | 105.7979 | 93.36 | 42.8811 | 12.0853 | -0.010526 | 82.3989 | 197.8558 | 190.2611 | 184.8347 | 175.6895 | 135.7421 | 116.0611 | 107.4021 | 94.9821 | 44.6189 | 13.8779 | 1.7737
|  | YARNTON BSP | HE |  |  |  |  | 99.02 | 217.1347 | 209.9379 | 206.3 | 200.9537 | 171.3537 | 157.1179 | 150.7411 | 143.3295 | 117.2747 | 106.1137 | 99.6726 | 85.3 | 203.16 | 194.6242 | 190.4453 | 184.2937 | 149.6242 | 133.0958 | 125.82 | 117.3274 | 86.6568 | 73.58 | 66.0337 | 86.7274 | 204.5916 | 196.0695 | 191.8968 | 185.7558 | 151.1484 | 134.6484 | 127.3821 | 118.9053 | 88.2937 | 75.2379 | 67.7053
|  | YARNTON BSP | FB |  |  |  |  | 100.4295 | 219.2463 | 217.7842 | 215.4263 | 175.0189 | 162.9916 | 160.0695 | 157.3684 | 154.4432 | 142.6905 | 133.6716 | 127.5642 | 86.9053 | 205.5442 | 203.8432 | 201.0663 | 153.1695 | 139.0874 | 135.7158 | 132.5979 | 129.2221 | 115.6347 | 105.2379 | 98.1358 | 88.3295 | 206.9695 | 205.2726 | 202.5032 | 154.6958 | 140.6389 | 137.2716 | 134.16 | 130.7874 | 117.2263 | 106.72 | 99.6347
AXMINSTER GSP | YEOVIL BSP | YEOVIL BSP | MINIMUM HEADROOM | ST 57586 16894 | NO | YES | 90.5053 | 65.5716 | 63.1547 | 59.8874 | 56.0463 | 51.0432 | 34.2326 | 87.0158 | 81.8842 | 77.1863 | 21.2526 | -25.3074 | -47.9105 | 35.5463 | 32.8832 | 29.2474 | 25.0189 | 19.4916 | 0.067368 | 51.9442 | 46.2695 | 41.1042 | -22.1274 | -78.2789 | -104.4484 | 41.0979 | 38.44 | 34.8137 | 30.5863 | 25.0411 | 5.6737 | 57.5674 | 51.9011 | 46.7442 | -15.4463 | -72.2989 | -98.3968
|  | YEOVIL BSP | EE |  |  |  |  | 65.5716 | 63.1547 | 60.0589 | 56.3568 | 51.4232 | 36.5137 | 91.9821 | 86.8779 | 82.1663 | 54.2789 | 41.7642 | 19.7274 | 35.5463 | 32.8853 | 29.4453 | 25.3684 | 19.9379 | 2.7326 | 57.7126 | 52.0347 | 46.8074 | 14.2084 | 1.5253 | -24.2537 | 41.0979 | 38.4432 | 35.0084 | 30.9379 | 25.5168 | 8.3558 | 63.3463 | 57.68 | 52.4653 | 19.9253 | 8.1389 | -17.5663
|  | YEOVIL BSP | HT |  |  |  |  | 65.9126 | 63.1705 | 59.8874 | 56.0463 | 51.0432 | 34.2326 | 87.0158 | 81.8842 | 77.1863 | 21.2526 | -25.3074 | -47.9105 | 35.94 | 32.8832 | 29.2474 | 25.0189 | 19.4916 | 0.067368 | 51.9442 | 46.2695 | 41.1042 | -22.1274 | -78.2789 | -104.4484 | 41.4884 | 38.44 | 34.8137 | 30.5863 | 25.0411 | 5.6737 | 57.5674 | 51.9011 | 46.7442 | -15.4463 | -72.2989 | -98.3968
|  | YEOVIL BSP | HE |  |  |  |  | 66.8126 | 64.8653 | 62.3379 | 59.0705 | 54.3947 | 39.6832 | 95.34 | 91.1211 | 86.9821 | 62.2621 | 45.0747 | 24.9158 | 36.9611 | 34.8463 | 32.0663 | 28.4926 | 23.3653 | 6.3726 | 61.5789 | 56.9453 | 52.3937 | 23.2537 | 2.1589 | -21.5432 | 42.5126 | 40.3989 | 37.6242 | 34.0568 | 28.9389 | 11.9926 | 67.2095 | 62.5811 | 58.0379 | 28.9558 | 7.4926 | -16.1411
|  | YEOVIL BSP | FB |  |  |  |  | 74.0495 | 68.0305 | 67.0063 | 64.6411 | 62.8379 | 61.3358 | 119.8495 | 118.4189 | 116.4642 | 107.8421 | 92.4737 | 74.3411 | 45.3442 | 38.3305 | 37.1937 | 34.4874 | 32.4505 | 30.7716 | 89.1042 | 87.4947 | 85.2789 | 75.4316 | 57.5189 | 36.2663 | 50.8716 | 43.8779 | 42.7421 | 40.0411 | 38.0116 | 36.3347 | 94.6726 | 93.0674 | 90.8537 | 81.0347 | 63.14 | 41.9505

## LEP Reference
Local Authority | Grid Supply Point | Bulk Supply Point | Primary Substation
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ARGYLE ROAD PRIMARY
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BILSHAM PRIMARY
Arun | LOVEDEAN GSP |  | CHALCRAFT LANE PRIMARY
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | CHICHESTER PRIMARY
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ROSE GREEN PRIMARY
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | SOUTH BERSTED PRIMARY
Basingstoke and Deane | MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST PRIMARY
Basingstoke and Deane | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BALL HILL PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | BASINGSTOKE PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BRAMLEY GREEN PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | BROOK STREET PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | CHINEHAM PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | DOWN GRANGE PRIMARY
Basingstoke and Deane | FLEET-BRAMLEY GSP | ALTON BSP | HERRIARD PRIMARY
Basingstoke and Deane | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HOOK PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | HOUNDMILLS PRIMARY
Basingstoke and Deane | MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1A & T2A) BSP | JAYS CLOSE PRIMARY
Basingstoke and Deane | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINGSCLERE PRIMARY
Basingstoke and Deane | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | MORTIMER PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T3 & T4) BSP | OAKRIDGE PRIMARY
Basingstoke and Deane | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | OVERTON PRIMARY
Basingstoke and Deane | FLEET-BRAMLEY GSP | ALTON BSP | PRESTON CANDOVER PRIMARY
Basingstoke and Deane | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | ST JOHNS PRIMARY
Basingstoke and Deane | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | TADLEY PRIMARY
Basingstoke and Deane | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM PRIMARY
Basingstoke and Deane | MELKSHAM GSP | ANDOVER BSP | WHITCHURCH PRIMARY
Bath and North East Somerset | MELKSHAM GSP | NORRINGTON BSP | BRADFORD-ON-AVON PRIMARY
Bath and North East Somerset | MELKSHAM GSP | NORRINGTON BSP | SPRING QUARRY WEST PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | ALDERNEY PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | BOURNE VALLEY PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | CENTRAL PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | LYTCHETT BSP | CORFE MULLEN PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | LYTCHETT BSP | CREEKMOOR PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | REDHILL BSP | EAST HOWE PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | ELECTRIC HOUSE PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | POOLE (HAMWORTHY) BSP | HAMWORTHY PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | LYTCHETT BSP | HOLES BAY PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE NORTH PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE SOUTH PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | REDHILL BSP | REDHILL PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | BOURNEMOUTH BSP | WESTBOURNE PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | REDHILL BSP | WINTON PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | ASCOT PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | BAGSHOT PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CROWTHORNE PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | EASTHAMPSTEAD PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | KINGS RIDE PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | KNOWL HILL PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | WOKINGHAM BSP | PEACOCK FARM PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | SANDHURST PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | SUNNINGHILL PRIMARY
Bracknell Forest | FLEET-BRAMLEY GSP | BRACKNELL BSP | WARFIELD PRIMARY
Buckinghamshire | IVER 132KV GSP | UPTON BSP | BEACONSFIELD (END BUSBARS) PRIMARY
Buckinghamshire | IVER 132KV GSP | DENHAM BSP | BEACONSFIELD (MIDDLE BUSBARS) PRIMARY
Buckinghamshire | AMERSHAM GSP | LOUDWATER BSP | BOWERDEAN PRIMARY
Buckinghamshire | IVER 132KV GSP | CHALVEY BSP | CHALVEY PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE PRIMARY
Buckinghamshire | IVER 132KV GSP | DENHAM BSP | COKES LANE PRIMARY
Buckinghamshire | IVER 132KV GSP | DENHAM BSP | DENHAM AVENUE PRIMARY
Buckinghamshire | IVER 132KV GSP | SLOUGH BSP | FARNHAM ROYAL PRIMARY
Buckinghamshire | AMERSHAM GSP | LOUDWATER BSP | FLACKWELL HEATH PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE PRIMARY
Buckinghamshire | IVER 132KV GSP | DENHAM BSP | GERRARDS CROSS PRIMARY
Buckinghamshire | IVER 132KV GSP | DENHAM BSP | GRASSINGHAM ROAD PRIMARY
Buckinghamshire | BRAMLEY (BASI) GSP | READING BSP | HENLEY PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW PRIMARY
Buckinghamshire | IVER 132KV GSP | CHALVEY BSP | PETERSFIELD AVENUE PRIMARY
Buckinghamshire | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH PRIMARY
Buckinghamshire | IVER 132KV GSP | UPTON BSP | SUTTON LANE PRIMARY
Buckinghamshire | IVER 132KV GSP | SLOUGH BSP | TAPLOW PRIMARY
Buckinghamshire | IVER 132KV GSP | UPTON BSP | UPTON PRIMARY
Buckinghamshire | IVER 66KV GSP |  | UXBRIDGE PRIMARY
Buckinghamshire | AMERSHAM GSP | LOUDWATER BSP | WELL END PRIMARY
Buckinghamshire | AMERSHAM GSP | LOUDWATER BSP | WYCOMBE MARSH PRIMARY
Buckinghamshire | IVER 66KV GSP |  | YIEWSLEY PRIMARY
Cherwell | COWLEY GSP | HEADINGTON BSP | ARNCOTT PRIMARY
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH PRIMARY
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER PRIMARY
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD PRIMARY
Cherwell | COWLEY GSP | YARNTON BSP | DEDDINGTON PRIMARY
Cherwell | COWLEY GSP | HEADINGTON BSP | HEADINGTON PRIMARY
Cherwell | COWLEY GSP | YARNTON BSP | KIDDINGTON PRIMARY
Cherwell | COWLEY GSP | YARNTON BSP | LOVELACE ROAD PRIMARY
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD PRIMARY
Cherwell | COWLEY GSP | YARNTON BSP | WOODSTOCK PRIMARY
Cherwell | COWLEY GSP | YARNTON BSP | YARNTON PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ASHLING ROAD PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BILLINGSHURST PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BIRDHAM PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | CHICHESTER PRIMARY
Chichester | LOVEDEAN GSP | HAVANT BSP | EMSWORTH PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | FIVE OAKS PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | HASLEMERE PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | HASLINGBOURNE PRIMARY
Chichester | LOVEDEAN GSP | HAVANT BSP | HORNDEAN PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | HUNSTON PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | LANGLEY COURT PRIMARY
Chichester | LOVEDEAN GSP | HAVANT BSP | LEIGH PARK PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | MARKET PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | MIDHURST PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | PETERSFIELD PRIMARY
Chichester | FLEET-BRAMLEY GSP | FERNHURST BSP | PLAISTOW PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | ROSE GREEN PRIMARY
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | SELSEY PRIMARY
Cotswold | MELKSHAM GSP | CHIPPENHAM BSP | ALDERTON PRIMARY
Cotswold | COWLEY GSP | WITNEY BSP | BLEDINGTON PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | CRICKLADE PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | FAIRFORD PRIMARY
Cotswold | MINETY GSP | STRATTON (RESERVE) BSP | LECHLADE PRIMARY
Cotswold | MELKSHAM GSP | CHIPPENHAM BSP | MALMESBURY PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | NORTHLEACH PRIMARY
Cotswold | COWLEY GSP | WITNEY BSP | RISSINGTON PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE PRIMARY
Cotswold | MINETY GSP | STRATTON (RESERVE) BSP | STANTON FITZWARREN PRIMARY
Cotswold | MELKSHAM GSP | CHIPPENHAM BSP | TETBURY PRIMARY
Cotswold | MINETY GSP | CIRENCESTER BSP | WHITEWAY PRIMARY
Cotswold | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WHITLEY WOOD PRIMARY
Dorset | MANNINGTON GSP | LYTCHETT BSP | BLANDFORD PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | CHICKERELL PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | CHILTON CANTELO PRIMARY
Dorset | MANNINGTON GSP | LYTCHETT BSP | CORFE MULLEN PRIMARY
Dorset | MANNINGTON GSP | LYTCHETT BSP | CREEKMOOR PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | DORCHESTER PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL PRIMARY
Dorset | MANNINGTON GSP | POOLE (HAMWORTHY) BSP | HAMWORTHY PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | HENSTRIDGE PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | MANNINGTON PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | Mill Lane PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON PRIMARY
Dorset | MANNINGTON GSP | BOURNEMOUTH BSP | PARKSTONE SOUTH PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | PORTLAND PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | PULHAM PRIMARY
Dorset | MANNINGTON GSP | REDHILL BSP | REDHILL PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | REDLANDS PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | SHERBORNE PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON PRIMARY
Dorset | MANNINGTON GSP | WAREHAM BSP | SWANAGE PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | VERWOOD PRIMARY
Dorset | MANNINGTON GSP | WAREHAM BSP | WAREHAM TOWN PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | WEST HENDFORD PRIMARY
Dorset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR PRIMARY
Dorset | CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE PRIMARY
Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES PRIMARY
Dorset | MANNINGTON GSP |  | WINFRITH HEATH PRIMARY
Dorset | MANNINGTON GSP | LYTCHETT BSP | WINTERBORNE KINGSTON PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | YEOVIL PRIMARY
Dorset | AXMINSTER GSP | YEOVIL BSP | YETMINSTER PRIMARY
Ealing | EALING GSP |  | BOSTON MANOR PRIMARY
Ealing | EALING GSP | EALING BSP | BRENTFORD PRIMARY
Ealing | WILLESDEN GSP |  | CANAL BANK 11kV PRIMARY
Ealing | EALING GSP |  | COPLEY DENE PRIMARY
Ealing | EALING GSP | EALING BSP | DEAN GARDENS PRIMARY
Ealing | EALING GSP |  | EALING PRIMARY
Ealing | WILLESDEN GSP | ACTON LANE BSP | GOLDSMITHS PRIMARY
Ealing | WILLESDEN GSP |  | GREENFORD PRIMARY
Ealing | EALING GSP |  | IRONBRIDGE PRIMARY
Ealing | WILLESDEN GSP | ACTON LANE BSP | LEAMINGTON PARK PRIMARY
Ealing | NORTH HYDE GSP |  | NORTH HYDE PRIMARY
Ealing | IVER 66KV GSP |  | NORTHOLT PRIMARY
Ealing | WILLESDEN GSP | ACTON LANE BSP | PARK ROYAL PRIMARY
Ealing | WILLESDEN GSP |  | PERIVALE PRIMARY
Ealing | EALING GSP |  | SOUTHFIELD ROAD PRIMARY
Ealing | NORTH HYDE GSP | NORTH HYDE BSP | SPRINGFIELD ROAD PRIMARY
Ealing | NORTH HYDE GSP | NORTH HYDE BSP | THE GREEN PRIMARY
Ealing | WILLESDEN GSP |  | WESLEY AVENUE PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALTON BSP | ALRESFORD PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALTON BSP | ALTON LOCAL PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALTON BSP | BORDON PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALTON BSP | HERRIARD PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALDERSHOT BSP | HINDHEAD PRIMARY
East Hampshire | LOVEDEAN GSP | HAVANT BSP | HORNDEAN PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | FERNHURST BSP | LANGLEY COURT PRIMARY
East Hampshire | LOVEDEAN GSP | HAVANT BSP | LEIGH PARK PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | FERNHURST BSP | PETERSFIELD PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | ALTON BSP | PRESTON CANDOVER PRIMARY
East Hampshire | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | WRECCLESHAM PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | BASSETT PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | BISHOPSTOKE PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | CHANDLERS FORD PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | HEDGE END PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK PRIMARY
Eastleigh | NURSLING GSP | VELMORE BSP | VELMORE PRIMARY
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | BROCKHURST PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | HOEFORD PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (RESERVE) BSP | LEE-ON-SOLENT PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | NORTH FAREHAM PRIMARY
Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | PLESSEY TITCHFIELD PRIMARY
Fareham | LOVEDEAN GSP | PORTSMOUTH BSP | PORTCHESTER PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | TITCHFIELD PRIMARY
Fareham | LOVEDEAN GSP | FAREHAM (MAIN) BSP | WEST END PRIMARY
Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY PRIMARY
Fareham | LOVEDEAN GSP | WYMERING BSP | WYMERING PRIMARY
Gosport | LOVEDEAN GSP | FAREHAM (MAIN) BSP | BROCKHURST PRIMARY
Gosport | LOVEDEAN GSP | FAREHAM (MAIN) BSP | HOEFORD PRIMARY
Gosport | LOVEDEAN GSP | FAREHAM (RESERVE) BSP | LEE-ON-SOLENT PRIMARY
Gosport | LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ROWNER PARK PRIMARY
Gosport | LOVEDEAN GSP | FAREHAM (RESERVE) BSP | ZETLAND ROAD PRIMARY
Guildford | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FARNBOROUGH PRIMARY
Guildford | FLEET-BRAMLEY GSP | ALDERSHOT BSP | GODALMING PRIMARY
Guildford | FLEET-BRAMLEY GSP | ALDERSHOT BSP | MILFORD PRIMARY
Guildford | FLEET-BRAMLEY GSP | ALDERSHOT BSP | NORMANDY PRIMARY
Guildford | FLEET-BRAMLEY GSP | ALDERSHOT BSP | TONGHAM PRIMARY
Hammersmith and Fulham | WILLESDEN GSP |  | CANAL BANK 11kV PRIMARY
Hart | FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT PRIMARY
Hart | BRAMLEY (BASI) GSP | READING BSP | ARBORFIELD PRIMARY
Hart | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | BRAMLEY GREEN PRIMARY
Hart | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | COVE PRIMARY
Hart | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | COXMOOR WOOD PRIMARY
Hart | FLEET-BRAMLEY GSP | PYESTOCK BSP | Crookham PRIMARY
Hart | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | HAWLEY PRIMARY
Hart | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HITCHES LANE PRIMARY
Hart | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | HOOK PRIMARY
Hart | FLEET-BRAMLEY GSP | PYESTOCK BSP | PYESTOCK PRIMARY
Hart | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | SANDHURST PRIMARY
Havant | LOVEDEAN GSP | HAVANT BSP | BROCKHAMPTON PRIMARY
Havant | LOVEDEAN GSP | HAVANT BSP | EMSWORTH PRIMARY
Havant | LOVEDEAN GSP | PORTSMOUTH BSP | FARLINGTON PRIMARY
Havant | LOVEDEAN GSP | HAVANT BSP | GABLE HEAD PRIMARY
Havant | LOVEDEAN GSP | HAVANT BSP | LEIGH PARK PRIMARY
Havant | LOVEDEAN GSP | HAVANT BSP | MEYRICK ROAD PRIMARY
Havant | LOVEDEAN GSP | FORT WIDLEY BSP | PURBROOK PRIMARY
Havant | LOVEDEAN GSP | FORT WIDLEY BSP | WATERLOOVILLE PRIMARY
Hillingdon | NORTH HYDE GSP | NORTH HYDE BSP | BATH ROAD EAST PRIMARY
Hillingdon | IVER 132KV GSP | LONGFORD BSP | BATH ROAD WEST PRIMARY
Hillingdon | IVER 132KV GSP | DENHAM BSP | DENHAM AVENUE PRIMARY
Hillingdon | LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT PRIMARY
Hillingdon | IVER 132KV GSP | DENHAM BSP | HAREFIELD PRIMARY
Hillingdon | NORTH HYDE GSP |  | HAYES PRIMARY
Hillingdon | IVER 66KV GSP |  | HILLINGDON PRIMARY
Hillingdon | LALEHAM GSP | EAST BEDFONT BSP | NORTH FELTHAM PRIMARY
Hillingdon | NORTH HYDE GSP |  | NORTH HYDE PRIMARY
Hillingdon | IVER 66KV GSP |  | NORTHOLT PRIMARY
Hillingdon | IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY
Hillingdon | NORTH HYDE GSP | NORTH HYDE BSP | SPRINGFIELD ROAD PRIMARY
Hillingdon | IVER 66KV GSP |  | UXBRIDGE PRIMARY
Hillingdon | IVER 66KV GSP |  | YIEWSLEY PRIMARY
Horsham | LOVEDEAN GSP | CHICHESTER & HUNSTON BSP | BILLINGSHURST PRIMARY
Horsham | FLEET-BRAMLEY GSP | FERNHURST BSP | FIVE OAKS PRIMARY
Horsham | FLEET-BRAMLEY GSP | FERNHURST BSP | PLAISTOW PRIMARY
Hounslow | NORTH HYDE GSP | NORTH HYDE BSP | BATH ROAD EAST PRIMARY
Hounslow | EALING GSP |  | BOSTON MANOR PRIMARY
Hounslow | EALING GSP | EALING BSP | BRENTFORD PRIMARY
Hounslow | EALING GSP |  | BRIDGE ROAD PRIMARY
Hounslow | LALEHAM GSP | EAST BEDFONT BSP | CHURCH ROAD PRIMARY
Hounslow | EALING GSP |  | EALING PRIMARY
Hounslow | LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT PRIMARY
Hounslow | LALEHAM GSP | EAST BEDFONT BSP | FELTHAM PRIMARY
Hounslow | EALING GSP | EALING BSP | HARVARD LANE PRIMARY
Hounslow | LALEHAM GSP | EAST BEDFONT BSP | HOPE AND ANCHOR PRIMARY
Hounslow | EALING GSP |  | IRONBRIDGE PRIMARY
Hounslow | LALEHAM GSP | EAST BEDFONT BSP | NORTH FELTHAM PRIMARY
Hounslow | NORTH HYDE GSP |  | NORTH HYDE PRIMARY
Hounslow | EALING GSP |  | SOUTHFIELD ROAD PRIMARY
Hounslow | LALEHAM GSP | STAINES BSP | STANWELL PRIMARY
Hounslow | LALEHAM GSP | STAINES BSP | SUNBURY CROSS PRIMARY
Hounslow | NORTH HYDE GSP |  | VICARAGE FARM ROAD PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN PRIMARY
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR PRIMARY
Mendip | MELKSHAM GSP | NORRINGTON BSP | BRADFORD-ON-AVON PRIMARY
Mendip | MELKSHAM GSP | FROME BSP | BRUTON PRIMARY
Mendip | MELKSHAM GSP | FROME BSP | FROME PRIMARY
Mendip | MELKSHAM GSP | FROME BSP | HOLWELL PRIMARY
Mendip | MELKSHAM GSP | NORRINGTON BSP | TROWBRIDGE TOWN PRIMARY
New Forest | FAWLEY GSP | LANGLEY BSP | BUTTS ASH PRIMARY
New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH PRIMARY
New Forest | NURSLING GSP | ROWNHAMS BSP | FLETCHWOOD PRIMARY
New Forest | MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE PRIMARY
New Forest | MANNINGTON GSP | ARNEWOOD BSP | HINCHESLEA PRIMARY
New Forest | MANNINGTON GSP | SALISBURY BSP | HOMINGTON PRIMARY
New Forest | FAWLEY GSP | LANGLEY BSP | LANGLEY PRIMARY
New Forest | MANNINGTON GSP | ARNEWOOD BSP | LYMINGTON PRIMARY
New Forest | NURSLING GSP |  | MARCHWOOD PRIMARY
New Forest | MANNINGTON GSP | ARNEWOOD BSP | MILFORD-ON-SEA PRIMARY
New Forest | MANNINGTON GSP | MANNINGTON BSP | Mill Lane PRIMARY
New Forest | MANNINGTON GSP | ARNEWOOD BSP | NEW MILTON PRIMARY
New Forest | MANNINGTON GSP | SALISBURY BSP | REDLYNCH PRIMARY
New Forest | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE PRIMARY
New Forest | NURSLING GSP | ROWNHAMS BSP | ROMSEY PRIMARY
New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD PRIMARY
New Forest | NURSLING GSP | ROWNHAMS BSP | TOTTON PRIMARY
New Forest | MANNINGTON GSP | MANNINGTON BSP | VERWOOD PRIMARY
Oxford | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL PRIMARY
Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD PRIMARY
Oxford | COWLEY GSP | HEADINGTON BSP | HEADINGTON PRIMARY
Oxford | COWLEY GSP | YARNTON BSP | LOVELACE ROAD PRIMARY
Oxford | COWLEY GSP | HEADINGTON BSP | OLD ROAD PRIMARY
Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD PRIMARY
Oxford | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | OXFORD SCIENCE PARK PRIMARY
Oxford | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | ROSE HILL PRIMARY
Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES PRIMARY
Oxford | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | UNION STREET PRIMARY
Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | UNIVERSITY PARKS PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | COLLEGE PARK PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | FARLINGTON PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | GAMBLE ROAD PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | HILSEA PRIMARY
Portsmouth | LOVEDEAN GSP | HAVANT BSP | MEYRICK ROAD PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | PORTCHESTER PRIMARY
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH PRIMARY
Portsmouth | LOVEDEAN GSP | WYMERING BSP | WYMERING PRIMARY
Purbeck | MANNINGTON GSP | WAREHAM BSP | BOVINGTON PRIMARY
Purbeck | MANNINGTON GSP | WAREHAM BSP | BUSHEY PRIMARY
Reading | FLEET-BRAMLEY GSP | READING TOWN BSP | CAVERSHAM PRIMARY
Reading | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | COURAGES PRIMARY
Reading | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | GREEN PARK PRIMARY
Reading | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | KENTWOOD HILL PRIMARY
Reading | BRAMLEY (BASI) GSP | READING BSP | NORTHUMBERLAND AVENUE PRIMARY
Reading | BRAMLEY (BASI) GSP | READING BSP | READING PRIMARY
Reading | FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN PRIMARY
Reading | BRAMLEY (BASI) GSP | READING BSP | SILVER STREET PRIMARY
Reading | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | SOUTHCOTE PRIMARY
Reading | FLEET-BRAMLEY GSP | READING TOWN BSP | THE MALL PRIMARY
Reading | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WILSON ROAD PRIMARY
Richmond upon Thames | EALING GSP |  | BRIDGE ROAD PRIMARY
Richmond upon Thames | LALEHAM GSP | EAST BEDFONT BSP | HOPE AND ANCHOR PRIMARY
Runnymede | LALEHAM GSP | STAINES BSP | CAUSEWAY PRIMARY
Runnymede | LALEHAM GSP | STAINES BSP | EGHAM PRIMARY
Runnymede | FLEET-BRAMLEY GSP | BRACKNELL BSP | MVEE PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | COVE PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | PYESTOCK BSP | Crookham PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | PYESTOCK BSP | FARNBORO AIRFIELD PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FARNBOROUGH PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | HAWLEY PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | ALDERSHOT BSP | LABURNUM ROAD PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | QUEENSMEAD PRIMARY
Rushmoor | FLEET-BRAMLEY GSP | ALDERSHOT BSP | TONGHAM PRIMARY
Slough | IVER 132KV GSP | CHALVEY BSP | CHALVEY PRIMARY
Slough | IVER 132KV GSP | SLOUGH BSP | FARNHAM ROYAL PRIMARY
Slough | IVER 132KV GSP | CHALVEY BSP | PETERSFIELD AVENUE PRIMARY
Slough | IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY
Slough | IVER 132KV GSP | UPTON BSP | SUTTON LANE PRIMARY
Slough | IVER 132KV GSP | UPTON BSP | UPTON PRIMARY
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | BERINSFIELD PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | READING TOWN BSP | CAVERSHAM PRIMARY
South Oxfordshire | COWLEY GSP | DRAYTON BSP | CHOLSEY PRIMARY
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | COWLEY LOCAL PRIMARY
South Oxfordshire | COWLEY GSP |  | CULHAM PRIMARY
South Oxfordshire | COWLEY GSP | DRAYTON BSP | FULSCOT PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | GORING PRIMARY
South Oxfordshire | COWLEY GSP | HEADINGTON BSP | HEADINGTON PRIMARY
South Oxfordshire | BRAMLEY (BASI) GSP | READING BSP | HENLEY PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | KENTWOOD HILL PRIMARY
South Oxfordshire | BRAMLEY (BASI) GSP | READING BSP | KIDMORE END PRIMARY
South Oxfordshire | COWLEY GSP | DRAYTON BSP | MILTON PRIMARY
South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD PRIMARY
South Oxfordshire | COWLEY GSP | HEADINGTON BSP | OLD ROAD PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PANGBOURNE PRIMARY
South Oxfordshire | BRAMLEY (BASI) GSP | READING BSP | READING PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | READING TOWN BSP | READING TOWN PRIMARY
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (MAIN) BSP | ROSE HILL PRIMARY
South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH PRIMARY
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | WALLINGFORD PRIMARY
South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON PRIMARY
South Oxfordshire | COWLEY GSP | HEADINGTON BSP | WHEATLEY PRIMARY
South Oxfordshire | COWLEY GSP | DRAYTON BSP | WINSMORE LANE PRIMARY
South Oxfordshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | WOODCOTE PRIMARY
South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON PRIMARY
South Somerset | MELKSHAM GSP | FROME BSP | BRUTON PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | CASTLE CARY PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | CHILTON CANTELO PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | HENSTRIDGE PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | LARKHILL PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | MILBORNE PORT PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | SHERBORNE PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | SPARKFORD PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | WEST HENDFORD PRIMARY
South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR PRIMARY
South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON PRIMARY
South Somerset | AXMINSTER GSP | YEOVIL BSP | YEOVIL PRIMARY
Southampton | NURSLING GSP | VELMORE BSP | BASSETT PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | BEVOIS VALLEY PRIMARY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CENTRAL BRIDGE PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (RESERVE) BSP | CHAPEL PRIMARY
Southampton | NURSLING GSP | ROWNHAMS BSP | LORDSHILL PRIMARY
Southampton | NURSLING GSP | ROWNHAMS BSP | MAYBUSH PRIMARY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (MAIN) BSP | REGENTS PARK PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (MAIN) BSP | SHIRLEY PRIMARY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WESTERN ESPLANADE PRIMARY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON PRIMARY
Southampton | NURSLING GSP | SOUTHAMPTON (MAIN) BSP | WOODMILL LANE PRIMARY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON PRIMARY
Spelthorne | LALEHAM GSP | STAINES BSP | CAUSEWAY PRIMARY
Spelthorne | LALEHAM GSP | EAST BEDFONT BSP | CHURCH ROAD PRIMARY
Spelthorne | LALEHAM GSP | EAST BEDFONT BSP | EAST BEDFONT PRIMARY
Spelthorne | IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY
Spelthorne | LALEHAM GSP | STAINES BSP | SIDNEY ROAD PRIMARY
Spelthorne | LALEHAM GSP | STAINES BSP | STANWELL PRIMARY
Spelthorne | LALEHAM GSP | STAINES BSP | SUNBURY CROSS PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | BRACKNELL BSP | BAGSHOT PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CAMBERLEY PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | BRACKNELL BSP | CHOBHAM PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FARNBOROUGH PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | CAMBERLEY (RESERVE) BSP | FRIMLEY PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | KINGS RIDE PRIMARY
Surrey Heath | FLEET-BRAMLEY GSP | BRACKNELL BSP | MVEE PRIMARY
Swindon | MINETY GSP | TOOTHILL BSP | CHISLEDON PRIMARY
Swindon | MINETY GSP | TOOTHILL BSP | DORCAN SOUTH PRIMARY
Swindon | MINETY GSP | STRATTON (MAIN) BSP | DRAKES WAY PRIMARY
Swindon | MINETY GSP |  | GALILEO PRIMARY
Swindon | MINETY GSP | SWINDON BSP | MANCHESTER ROAD PRIMARY
Swindon | MINETY GSP | STRATTON (MAIN) BSP | PARK NORTH PRIMARY
Swindon | MINETY GSP | STRATTON (MAIN) BSP | PLESSEY PRIMARY
Swindon | MINETY GSP | STRATTON (MAIN) BSP | PRESSED STEEL SWINDON PRIMARY
Swindon | MINETY GSP | TOOTHILL BSP | QUARRY ROAD PRIMARY
Swindon | MINETY GSP | STRATTON (RESERVE) BSP | SHRIVENHAM PRIMARY
Swindon | MINETY GSP | STRATTON (RESERVE) BSP | STANTON FITZWARREN PRIMARY
Swindon | MINETY GSP | STRATTON (RESERVE) BSP | STRATTON PRIMARY
Swindon | MINETY GSP | SWINDON BSP | SWINDON PRIMARY
Swindon | MINETY GSP | TOOTHILL BSP | TOOTHILL PRIMARY
Swindon | MINETY GSP | SWINDON BSP | TRADING ESTATE PRIMARY
Swindon | MINETY GSP | SWINDON BSP | WOOTTON BASSETT PRIMARY
Swindon | MINETY GSP | TOOTHILL BSP | WROUGHTON PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | ANDOVER PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | ANDOVER TOWN PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | BARTON STACEY PRIMARY
Test Valley | NURSLING GSP | VELMORE BSP | BASSETT PRIMARY
Test Valley | NURSLING GSP | VELMORE BSP | CHANDLERS FORD PRIMARY
Test Valley | NURSLING GSP | WINCHESTER BSP | DUNBRIDGE PRIMARY
Test Valley | NURSLING GSP | WINCHESTER BSP | HOUGHTON PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT PRIMARY
Test Valley | NURSLING GSP | ROWNHAMS BSP | LORDSHILL PRIMARY
Test Valley | NURSLING GSP | ROWNHAMS BSP | MAYBUSH PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | MIDDLE WALLOP PRIMARY
Test Valley | NURSLING GSP | ROWNHAMS BSP | NORTH BADDESLEY PRIMARY
Test Valley | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PARK HOUSE PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | PORTWAY PRIMARY
Test Valley | NURSLING GSP | ROWNHAMS BSP | ROMSEY PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | THRUXTON PRIMARY
Test Valley | MELKSHAM GSP | WEST GRAFTON BSP | TIDWORTH PRIMARY
Test Valley | NURSLING GSP | VELMORE BSP | VELMORE PRIMARY
Test Valley | MELKSHAM GSP | ANDOVER BSP | WHITCHURCH PRIMARY
Three Rivers | IVER 132KV GSP | DENHAM BSP | COKES LANE PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | CHOLSEY PRIMARY
Vale of White Horse | COWLEY GSP | YARNTON BSP | EYNSHAM PRIMARY
Vale of White Horse | MINETY GSP | STRATTON (RESERVE) BSP | FARINGDON PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | FULSCOT PRIMARY
Vale of White Horse | COWLEY GSP | WITNEY BSP | FYFIELD PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | GROVE PRIMARY
Vale of White Horse | COWLEY GSP |  | HARWELL PRIMARY
Vale of White Horse | COWLEY GSP | COWLEY LOCAL (RESERVE) BSP | KENNINGTON PRIMARY
Vale of White Horse | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LAMBOURN PRIMARY
Vale of White Horse | MINETY GSP | STRATTON (RESERVE) BSP | LECHLADE PRIMARY
Vale of White Horse | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LECKHAMPSTEAD PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | MILTON PRIMARY
Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY PRIMARY
Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD PRIMARY
Vale of White Horse | MINETY GSP | STRATTON (RESERVE) BSP | SHRIVENHAM PRIMARY
Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES PRIMARY
Vale of White Horse | COWLEY GSP | WITNEY BSP | STANDLAKE PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | WANTAGE PRIMARY
Vale of White Horse | COWLEY GSP | DRAYTON BSP | WINSMORE LANE PRIMARY
Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD PRIMARY
Vale of White Horse | COWLEY GSP | YARNTON BSP | YARNTON PRIMARY
Waverley | FLEET-BRAMLEY GSP | ALDERSHOT BSP | ALDERSHOT PRIMARY
Waverley | FLEET-BRAMLEY GSP | ALDERSHOT BSP | FARNHAM PRIMARY
Waverley | FLEET-BRAMLEY GSP | ALDERSHOT BSP | GODALMING PRIMARY
Waverley | FLEET-BRAMLEY GSP | FERNHURST BSP | HASLEMERE PRIMARY
Waverley | FLEET-BRAMLEY GSP | ALDERSHOT BSP | HINDHEAD PRIMARY
Waverley | FLEET-BRAMLEY GSP | ALDERSHOT BSP | MILFORD PRIMARY
Waverley | FLEET-BRAMLEY GSP | FERNHURST BSP | PLAISTOW PRIMARY
Waverley | FLEET-BRAMLEY GSP | COXMOOR WOOD BSP | WRECCLESHAM PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BALL HILL PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | BEENHAM PRIMARY
West Berkshire | COWLEY GSP | DRAYTON BSP | CHOLSEY PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | GORING PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | HUNGERFORD PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | KENTWOOD HILL PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINTBURY PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LAMBOURN PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LECKHAMPSTEAD PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LOVE LANE PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | MORTIMER PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PADWORTH PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | PANGBOURNE PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | RIVERSIDE PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | ST JOHNS PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | TADLEY PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | THATCHAM PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | THEALE PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (RESERVE) BSP | TRASH GREEN PRIMARY
West Berkshire | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WHITLEY WOOD PRIMARY
West Berkshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | YATTENDON PRIMARY
West Dorset | MANNINGTON GSP | WAREHAM BSP | BOVINGTON PRIMARY
West Dorset | AXMINSTER GSP | YEOVIL BSP | MILBORNE PORT PRIMARY
West Oxfordshire | MINETY GSP | STRATTON (RESERVE) BSP | BLACK BOURTON PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | BLEDINGTON PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | BURFORD PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | CARTERTON PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | CHARLBURY PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | CHIPPING NORTON PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | DEDDINGTON PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | EYNSHAM PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | KIDDINGTON PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | LEAFIELD PRIMARY
West Oxfordshire | MINETY GSP | STRATTON (RESERVE) BSP | LECHLADE PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | RISSINGTON PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | STANDLAKE PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | WINDRUSH PARK PRIMARY
West Oxfordshire | COWLEY GSP | WITNEY BSP | WITNEY TOWN PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | WOODSTOCK PRIMARY
West Oxfordshire | COWLEY GSP | YARNTON BSP | YARNTON PRIMARY
Bournemouth, Christchurch and Poole | MANNINGTON GSP | POOLE (HAMWORTHY) BSP | POOLE PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | ALDERTON PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | ASHTON PARK PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | BEMERTON PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | BOSCOMBE DOWN PRIMARY
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | BRADFORD-ON-AVON PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | BROMHAM PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | CALNE PRIMARY
Wiltshire | MINETY GSP | TOOTHILL BSP | CHISLEDON PRIMARY
Wiltshire | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | COCKLEBURY PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | CODFORD PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | CORSHAM PRIMARY
Wiltshire | MINETY GSP | CIRENCESTER BSP | CRICKLADE PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | CROCKERTON PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | DEVIZES PRIMARY
Wiltshire | NURSLING GSP | WINCHESTER BSP | DUNBRIDGE PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | EASTERTON PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | ENFORD PRIMARY
Wiltshire | MINETY GSP | CIRENCESTER BSP | FAIRFORD PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | FROME PRIMARY
Wiltshire | MINETY GSP |  | GALILEO PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | HAWKERIDGE PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | HOMINGTON PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | HUNGERFORD PRIMARY
Wiltshire | MINETY GSP | CIRENCESTER BSP | KEMBLE RAF PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | KINTBURY PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | THATCHAM BSP | LAMBOURN PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | LYNEHAM PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | MALMESBURY PRIMARY
Wiltshire | MELKSHAM GSP | WEST GRAFTON BSP | MARLBOROUGH SOUTH PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | MELKSHAM TOWN PRIMARY
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON PRIMARY
Wiltshire | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | NETHERHAMPTON PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PARK HOUSE PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | PETERSFINGER PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | PEWSEY PRIMARY
Wiltshire | MELKSHAM GSP | WEST GRAFTON BSP | RAMSBURY PRIMARY
Wiltshire | BRAMLEY (AMES-THAT) GSP | AMESBURY BSP | RATFYN PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | REDLYNCH PRIMARY
Wiltshire | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | ROWDEN PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | SALISBURY CENTRAL PRIMARY
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY PRIMARY
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | SPRING QUARRY WEST PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | STAPLEFORD PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | SUTTON BENGER PRIMARY
Wiltshire | MINETY GSP | SWINDON BSP | SWINDON PRIMARY
Wiltshire | MANNINGTON GSP | SALISBURY BSP | TEFFONT PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | TETBURY PRIMARY
Wiltshire | MELKSHAM GSP | ANDOVER BSP | THRUXTON PRIMARY
Wiltshire | MELKSHAM GSP | WEST GRAFTON BSP | TIDWORTH PRIMARY
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | TISBURY PRIMARY
Wiltshire | MELKSHAM GSP | NORRINGTON BSP | TROWBRIDGE TOWN PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | WARMINSTER PRIMARY
Wiltshire | MELKSHAM GSP | WEST GRAFTON BSP | WEST GRAFTON VILLAGE PRIMARY
Wiltshire | MELKSHAM GSP | FROME BSP | WESTBURY PRIMARY
Wiltshire | MINETY GSP | SWINDON BSP | WOOTTON BASSETT PRIMARY
Wiltshire | MINETY GSP | TOOTHILL BSP | WROUGHTON PRIMARY
Wiltshire | MELKSHAM GSP | CHIPPENHAM BSP | YATTON KEYNELL PRIMARY
Winchester | FLEET-BRAMLEY GSP | ALTON BSP | ALRESFORD PRIMARY
Winchester | MELKSHAM GSP | ANDOVER BSP | BARTON STACEY PRIMARY
Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM PRIMARY
Winchester | NURSLING GSP | VELMORE BSP | CHANDLERS FORD PRIMARY
Winchester | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH PRIMARY
Winchester | NURSLING GSP | WINCHESTER BSP | GORDON ROAD PRIMARY
Winchester | NURSLING GSP | WINCHESTER BSP | HARESTOCK PRIMARY
Winchester | NURSLING GSP | VELMORE BSP | HEDGE END PRIMARY
Winchester | LOVEDEAN GSP | HAVANT BSP | HORNDEAN PRIMARY
Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON PRIMARY
Winchester | NURSLING GSP | ROWNHAMS BSP | NORTH BADDESLEY PRIMARY
Winchester | LOVEDEAN GSP | FAREHAM (MAIN) BSP | NORTH FAREHAM PRIMARY
Winchester | BRAMLEY (BASI) GSP | BASINGSTOKE (T1B & T2B) BSP | OVERTON PRIMARY
Winchester | LOVEDEAN GSP | PORTSMOUTH BSP | PORTCHESTER PRIMARY
Winchester | FLEET-BRAMLEY GSP | ALTON BSP | PRESTON CANDOVER PRIMARY
Winchester | LOVEDEAN GSP | FORT WIDLEY BSP | PURBROOK PRIMARY
Winchester | NURSLING GSP | ROWNHAMS BSP | SILKSTEAD PRIMARY
Winchester | NURSLING GSP | WINCHESTER BSP | ST CROSS PRIMARY
Winchester | LOVEDEAN GSP | FAREHAM (MAIN) BSP | TITCHFIELD PRIMARY
Winchester | LOVEDEAN GSP | FORT WIDLEY BSP | WATERLOOVILLE PRIMARY
Winchester | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY PRIMARY
Winchester | LOVEDEAN GSP | WYMERING BSP | WYMERING PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | BRACKNELL BSP | ASCOT PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | BRACKNELL BSP | BAGSHOT PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | BRAYWICK ROAD PRIMARY
Windsor and Maidenhead | LALEHAM GSP | STAINES BSP | CAUSEWAY PRIMARY
Windsor and Maidenhead | IVER 132KV GSP | CHALVEY BSP | CHALVEY PRIMARY
Windsor and Maidenhead | IVER 132KV GSP | CIPPENHAM BSP | CLARENCE ROAD PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | CORDWALLIS PRIMARY
Windsor and Maidenhead | LALEHAM GSP | STAINES BSP | EGHAM PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | KNOWL HILL PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | MAIDENHEAD PRIMARY
Windsor and Maidenhead | IVER 132KV GSP | LONGFORD BSP | POYLE PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | BRACKNELL BSP | SUNNINGHILL PRIMARY
Windsor and Maidenhead | IVER 132KV GSP | UPTON BSP | SUTTON LANE PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | TEMPLE FARM PRIMARY
Windsor and Maidenhead | IVER 132KV GSP | UPTON BSP | UPTON PRIMARY
Windsor and Maidenhead | FLEET-BRAMLEY GSP | BRACKNELL BSP | WARFIELD PRIMARY
Windsor and Maidenhead | AMERSHAM GSP | LOUDWATER BSP | WELL END PRIMARY
Wokingham | BRAMLEY (BASI) GSP | READING BSP | ARBORFIELD PRIMARY
Wokingham | FLEET-BRAMLEY GSP | BRACKNELL BSP | BRACKNELL PRIMARY
Wokingham | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | COURAGES PRIMARY
Wokingham | FLEET-BRAMLEY GSP | CAMBERLEY (MAIN) BSP | CROWTHORNE PRIMARY
Wokingham | FLEET-BRAMLEY GSP | WOKINGHAM BSP | ELMS ROAD PRIMARY
Wokingham | BRAMLEY (BASI) GSP | READING BSP | HENLEY PRIMARY
Wokingham | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | KNOWL HILL PRIMARY
Wokingham | BRAMLEY (BASI) GSP | READING BSP | LITTLE HUNGERFORD PRIMARY
Wokingham | BRAMLEY (BASI) GSP | READING BSP | READING PRIMARY
Wokingham | FLEET-BRAMLEY GSP | MAIDENHEAD BSP | TEMPLE FARM PRIMARY
Wokingham | BRAMLEY (BASI) GSP | READING BSP | TWYFORD PRIMARY
Wokingham | FLEET-BRAMLEY GSP | BURGHFIELD (MAIN) BSP | WHITLEY WOOD PRIMARY
Wokingham | FLEET-BRAMLEY GSP | WOKINGHAM BSP | WOKINGHAM PRIMARY

## EISD
| GSPs in November 2025 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Amersham | 2037 | Pending review | 2037 | Under active review
| Axminster | 2036 | Pending review | 2036 | Under active review
| Botley Wood | 2036 | Pending review | 2036 | Under active review
| Bramley (BASI) | 2036 | Pending review | 2036 | Under active review
| Bramley (THAT-AMES) | 2036 | Pending review | 2036 | Under active review
| Bramley (FLEE) | 2036 | Pending review | 2036 | Under active review
| Chickerell | 2036 | Pending review | 2036 | Under active review
| Cowley | 2029 | Pending review | 2029 | Under active review
| Ealing | 2037 | Pending review | 2037 | Under active review
| East Claydon | 2034 | Pending review | 2034 | Under active review
| Fawley | 2036 | Pending review | 2036 | Under active review
| Iver | 2037 | Pending review | 2037 | Under active review
| Laleham | 2037 | Pending review | 2037 | Under active review
| Lovedean | 2036 | Pending review | 2036 | Under active review
| Mannington | 2036 | Pending review | 2036 | Under active review
| Melksham | 2036 | Pending review | 2036 | Under active review
| Minety | 2036 | Pending review | 2036 | Under active review
| North Hyde | 2037 | Pending review | 2037 | Under active review
| Nursling | 2036 | Pending review | 2036 | Under active review
| Tynemouth | 2032 | Pending review | 2032 | Under active review
| Willesden | 2037 | Pending review | 2037 | Under active review
Southern Electric Power Distribution | DNO Licence area
National Energy System Operator | Transmission System Operator
2026-03-31 | Last update
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for new applications for demand and generation of significant size (>1MW).
2 Approved by Ofgem in April 2025, the connection reform aim to remove unviable projects from the queue and prioritise projects meeting specific readiness and strategic alignment criteria. A revised timeline has been published on 13 February 2026 to illustrate the issue of modification offers by NESO.
https://www.neso.energy/industry-information/connections-reform/connections-reform-timeline
3 Connections Network Design Methodology (CNDM) defines the queue formation process undertaken during application windows, including allocation of new capacity and reallocation of released capacity when projects exit the queue.
https://www.neso.energy/industry-information/connections-reform/connections-reform-design-documents-and-methodologies
Gate 2 Criteria Methodology sets out the benchmark used to assess whether a project is sufficiently ready and strategically aligned to progress within the reformed connections process. SSEN provides detailed evidence requirements for meeting Gate 2 criteria.
https://www.ssen.co.uk/globalassets/our-services/large-new-connections-300kva/connections-reform/sse-connections-reform-gate-2-criteria_2025-05-19.pdf
4 Where the transmission owner is actively reviewing projects as part of the connection reform process, this is shown as "under active review". Projects that have not yet entered the review process are shown as “Pending review”.
5 The EISDs reflect both works at a Grid Supply Point and in wider transmission network.
6 Where an EISD has not been established for a GSP, this is shown as N/A.
Connection headroom is likely to be available because no constraints or construction works impacting connection have been defined at this stage. This is represented as “No date restriction identified”.
7 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
8 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.