## Content and User Guide
TG-NET-ENG-005 | SSEN Standard Design Matrix for POC Assessment |  |  |  | Applies to
[5 empty] | Distribution  |  | Transmission
Revision: 3.00 | Classification: Public |  | Issue Date: August 2025 |  |  | Review Date: August 2030
Description: |  | The Standard Design Matrix shall be used as the guidance for determining a point of connection. The matrix details where generic design is acceptable and where more detailed analysis (as detailed in PR-NET-NPL-001 Section 11) is required. The matrix is designed to be a 'quick guide' to reference the process. Process maps have been included as tabs in this spreadsheet and these provided a more detailed view of the requirements for each design. Reference must be made to the SSEN 'G81' documents. Basic Assessments are also provided in this spreadsheet to determine if a more detailed analysis is required
Owner: |  | John R. Baker
Developer: |  | John R. Baker, Mark Trueman, James McNeish
Structure: |  | Definitions |  | General Definition and Abbreviations
|  | Def_Abnormal Load |  | Definition of Abnormal Load
|  | Design Matrix |  | Standard Design Matrix for Single POC Assessment
|  | Whole Current |  | Process Map for Whole Current Metered Connection(s), including Unmetered Connection > 2 kVA
|  | Non-Whole Current |  | Process Map for Non-Whole Current Metered Connection(s)
|  | Abnormal Load |  | Process Map for Abnormal Load in addition to "Whole Current" or "Non-Whole Current" Process
|  | Unmetered |  | Process Map for Unmetered Connection ≤ 2 kVA
|  | Transformer Assessment (2) |  | Transformer Assessment Approach (2) , as describe in definition
|  | Basic Assessment |  | Basic Transformer Assessment
Data derivation: |  | not applicable
Significant named ranges: |  | not applicable
Housekeeping requirements: |  | review when new 'G81' documents are added or withdrawn
Inveralmond House, 200 Dunkeld Road, Perth PH1 3AQ ssen.co.uk
Scottish and Southern Electricity Networks is a trading name of: Scottish and Southern Energy Power Distribution Limited Registered in Scotland No. SC213459;
Scottish Hydro Electric Transmission plc Registered in Scotland No. SC213461; Scottish Hydro Electric Power Distribution plc Registered in Scotland No. SC213460;
(all having their Registered Offices at Inveralmond House 200 Dunkeld Road Perth PH1 3AQ); and Southern Electric Power Distribution plc Registered in England & Wales No. 04094290
having its Registered Office at One Forbury Place, 43 Forbury Road, Reading, RG1 3JHwhich are members of the SSE Group www.ssen.co.uk

## Definitions
Definitions and Abbreviations
Abnormal Load | Equipment that is likely to cause a disturbance to the electricity supply to other customers on the Network. See "Def_Abnormal Load" Tab.
EHV Assessment | An assessment of the EHV Distribution Network by SSEN System Planning
HV Assessment | An assessment of the HV Distribution Network by SSEN Network Planning
Network Assessment | A network study carried out using approved methods as outlined in PR-NET-NPL-001. SSEN's preferred method is WinDEBUT software. This will include assessment for the transformer, distributor and service.
Whole Current Metered | Used to measure AC current in which the whole current to be measured flows directly through the meter
Non-whole Current Metered | Where the current is converted to an indirect variable which is measured by a meter that is not directly measuring the actual current
Point of Common Coupling | The point of a power supply network at which other loads are, or may be, connected
Point of Supply | The physical exit point (or points) from our Distribution Network
Transformer Assessment | An assessment of the Loading of a Transformer, based on approved methods
Transformer Rating | The rating, (in kVA) is the load carrying capability of the Transformer.
Unmetered | A Connection to allow a supply of electricity to a particular piece of electrical equipment that draws a current that is connected to the distribution network without a meter.
WinDEBUT | A load flow software package used for designing and / or checking the capability of LV networks.
EHV | Extra High Voltage
HV | High Voltage
LV | Low Voltage
TX | Transformer

## Def_Abnormal Load
Definition of Abnormal Load

## Design Matrix
Standard Design Matrix for Single POC Assessment
Please also refer to the 'Contents and User Guide' tab
Type of Connection | kVA/phase per Connection | Total Site Demand | Method of Calculation and Output Requirements
|  |  | 2 kV to 4kV Networks | LV Service |  | LV Distributor |  | 6.6 kV or 11 kV Secondary Substation Transformer |  |  |  | 6.6 kV or 11 kV Circuits | EHV (including Primary Substations) and Above
|  |  |  | Length > 30 m | Length ≤ 30 m | Cable < 95mm2 | Cable ≥ 95mm2 | up to 50 kVA | 100 kVA | > 100 kVA to 315 kVA | > 315 kVA
Unmetered | up to 2 kVA/phase |  | SSEN will provide POC |  | Not Required if length of service and distributor extension is less than 30 m
Whole Current Metered (Single Customer) | up to 23 kVA/phase | [6 empty] | Basic Transformer Assessment
Whole Current Metered (Multiple Customers) | up to 23 kVA/phase | < 250 kVA |  | Network Assessment Required
|  | ≥ 250 kVA | [10 empty] | If ≥ 500 kVA
Non-Whole Current Metered |  | < 250 kVA
≥ 250 kVA & < 500 kVA
≥ 500 kVA
Generation & Abnormal Load |  |  | SSEN will provide POC
Key
Assessment not required
Assessment may be required
Assessment required
SSEN will provide POC

## Transformer Assessment (2)
Transformer Assessment Approach (2)
1Basic Transformer Assessment can be found in "Basic Assessment" Tab

## Basic Assessment
EXAMPLE ONLY

## Version Control
Version | Date | Notes | Author | Checked | Approved
1 | 2017-12-05 | Document updated into new format. Single customer and multi customer split into different tabs | John R. Baker | Stephen Booth | Matt Thomas
2 | 2020-02-01 | Added definition of Abnormal Load Combined single- and multi-customer design Matrix Updated the process maps and created new Abnormal Load process map Included Transformer Basic Assessment | Hui Yi Heng | John R. Baker | Peter Williams
2.01 | 2025-01-17 | Reviewed only. New review date only 12 months to permit major overhaul to take place by new author and review team | John R. Baker | Elina Bezusko | Shirley Robertson
3 | 2025-07-04 | Whole current, non-whole current, abnormal load and unmetered flow charts updated | John R. Baker | Elina Bezusko | Shirley Robertson