## Content and User Guide
TG-NET-ENG-005 | SSEN Standard Design Matrices for POC Assessment |  |  | Applies to
|  |  |  | Distribution  |  | Transmission 
Revision: 1.00 | Classification: Public |  | Issue Date: November 2017 |  | Review Date: November 2022
Description: |  | Document to be use in conjunction with SSEN 'G81' documents
Owner: |  | John R. Baker
Developer: |  | John R. Baker
Structure: |  | not applicable
Data derivation: |  | not applicable
Significant named ranges: |  | not applicable
Housekeeping requirements: |  | review when new 'G81' documents are added or withdrawn
Inveralmond House, 200 Dunkeld Road, Perth PH1 3AQ ssen.co.uk
Scottish and Southern Electricity Networks is a trading name of: Scottish and Southern Energy Power Distribution Limited Registered in Scotland No. SC213459;
Scottish Hydro Electric Transmission plc Registered in Scotland No. SC213461; Scottish Hydro Electric Power Distribution plc Registered in Scotland No. SC213460;
(all having their Registered Offices at Inveralmond House 200 Dunkeld Road Perth PH1 3AQ); and Southern Electric Power Distribution plc Registered in England & Wales No. 04094290
having its Registered Office at One Forbury Place, 43 Forbury Road, Reading, RG1 3JHwhich are members of the SSE Group www.ssen.co.uk

## Supporting Notes
Standard Design Matrices
The Standard Design Matrices shall be used as the guidance for determinining a point of connection. The matrices detail where generic design is acceptable and where more detailed analysis is required.
There are two matricies, on for a single customer point load and one for multiple customers where an A.D.M.D. can be applied.
The matrices are designed to be a 'quick guide' to reference the process. Process maps have been included as tabs in this spreadsheet and these provided a more detailed view of the requirements for each design. Reference must me made to the SSEN 'G81' documents. The process maps are shown on the following tabs;
(a) Unmetered ADMD limited to 8kVA and single customer load to 2kVA
(b) Domestic (excluding loads with motor starting). ADMD limited to 8kVA and single customer load to 23kVA per phase
(c) Light Industrial, commercial ( including domestic and all loads with motor starting). ADMD limited to 23kVA per phase and single customer load to 23kVA per phase
(d) Heavy industrial and commercial (includes domestic estates). Any ADMD not exceeding 1000kVA. Single customer loads up to 1500kVA.
The following notes refer to the standard design matrices
1 | Maximum Capacities | these may well be subject to other design constraints such a volt drop, earth fault loop impedance etc.
2 | New unloaded LV cables | winter cyclic ratings will be used unless load is predominantly in summer in which case the summer sustained rating shall be used
3 | Existing loaded LV cables | winter cyclic rating less ADMD applicable to existing installed load
4 | New transformers | nameplate rating
5 | Existing transformers | nameplate rating less ADMD applicable to existing installed load
6 | Volt Drop | Volt drop on distributor not to exceed 5% and that on service 2%
7 | Overhead Circuit | defined by any OH line section between the primary substation and the POC
8 | Windebut | an EA Technology design product - other software or a manual method of calculation can be used
9 | SinCal | a Siemens design product - other software or a manual method of calculation can be used

## Standard Design - Single Custom
Standard Design Matrix for Single Customer for Single POC Assessment - Single point demand (no diversity)
Please also refer to the 'Supporting Notes' tab
Number of Phases | Maximum Demand | Demand Type | Method of Calculation and Output Requirements
|  |  | LV Service | LV Distributor |  | 6.6kV or 11kV Secondary Substation Transformer |  |  |  |  | 2kV up to 4kV Networks | 6.6 and 11kV Circuits |  | 22kV and 33kV Substations | 22 and 33kV Circuits |  | 66kV up to and incl. 400kV Substations | 66kV up to and incl. 400kV Circuits
|  |  |  | up to 10 metre branch ('T') on to existing distributor | >10 metre branch and any extension to distributor | up to 50kVA | >50kVA to 100kVA | >100 kVA to 500kVA | >500 kVA | Upgraded or New Tx |  | Overhead | Under- ground |  | Overhead | Under- ground |  | Overhead | Under- ground
Single phase | up to 2kVA | Street Lighting | Service 'T' + standard service (max service length 20m (35mm2 concentric), otherwise service design assessment required) | Use same LV cable CSA or equivalent | [6 empty] | SSEN will provide POC
Single phase | up to 8kVA
Single phase | up to 23kVA |  |  |  |  | Transformer loading assessment only
Two phases | up to 46kVA
Three phase | up to 69kVA
Single phase | up to 23kVA | Industrial and Commercial or Domestic including any load with motor starting (e.g. heat pumps) etc | Design assessment using a suitable analysis method / tool (e.g. Windebut). |  |  | Transformer loading assessment. Design assessment using suitable analysis method / tool (e.g. SinCal) |  |  |  |  | SSEN will provide POC
Two phases | up to 46kVA
Three Phase | up to 69kVA
Three Phase | up to 250kVA | Commercial / Industrial (LV only)
Three Phase | up to 414kVA | [10 empty] | Design assessment using suitable analysis method / tool (e.g. SinCal)
Three Phase | up to and including 1,500kVA | Industrial / Commercial (LV from dedicated transformer) | Most likely singles | No distributer (dedicated feed from transformer)
Three Phase | up to 50,000kVA | Industrial / Commercial or Distributed Generation | SSEN will provide POC
Key
| Design assessment not essential |  |  | Design assessment necessary |  |  | SSEN will provide POC |  |  | Transformer upgrade essential |  |  |  | Awaiting requirements. SSEN will provide POC meantime
The completed network must comply with the Supply Characteristics of the Design and Planning Guidance applicable to the voltage

## Standard Design - Multi Cust
Standard Design Matrix for Multiple Customer (2 or more) for Single POC Assessment - Applies ADMD (After Diversity Maximum Demand)
Please also refer to the 'Supporting Notes' tab
Number of Phases | Aggregated ADMD Limit | Demand Type | Method of Calculation and Output Requirements
|  |  | LV Service | LV Distributor |  | 6.6kV or 11kV Secondary Substation Transformer |  |  |  |  | 2kV up to 4kV Networks | 6.6 and 11kV Circuits |  | 22kV and 33kV Substations | 22kV and 33kV circuits |  | 66kV up to and incl. 400kV Substations | 66kV up to and incl. 400kV Circuits
|  |  |  | up to 10 metre branch ('T') on to existing Distributor | >10 metre branch and any extension to distributor | up to 50kVA | >50kVA to 100kVA | >100 kVA to 500kVA | >500kVA | Upgraded or New Tx |  | Overhead | Under- ground |  | Overhead | Under- ground |  | Overhead | Under- ground
Single phase | up to 8kVA | Street Lighting | Service 'T' + standard service (max service length 20m (35mm2 concentric), otherwise service design assessment required) | Use same LV Distributor cable CSA or equivalent |  | Transformer loading assessment only |  |  |  |  | SSEN provide POC
Single phase | Max ADMD of 8kVA / phase | Domestic only (with no motor starting e.g. heat pumps) Maximum 9 properties (maximum 3 per phase) |  | Use same LV Distributor cable CSA or equivalent | Design assessment or use simplistic approach in TG-PS-886 (Appendix 1) for 'T'
Two phases
Three Phase
Single phase | Max ADMD of 23kVA / phase | Industrial/commercial or domestic including any load with motor starting (e.g. heat pumps) | Service 'T' + standard service (max service length 20m (35mm2 concentric), otherwise service design assessment required) | Design assessment using suitable analysis method / tool (e.g. Windebut). |  |  |  | Transformer loading assessment. Include design assessment for any non domestic load using suitable analysis method / tool (e.g. SinCal). |  |  | SSEN will provide POC
Two phases
Three phase
Three phase | 69kVA and up to 150kVA | Any demand type | Design assessment using suitable analysis method / tool (e.g. Windebut).
Three phase | up to 250kVA
Three phase | up to 500kVA |  |  |  |  | Upgrade transformer capacity. Design assessment for any non domestic load using suitable analysis method / tool (e.g. SinCal). | [5 empty] | Design assessment using suitable analysis method / tool (e.g. Sincal)
Three phase | over 500kVA and up to 1000kVA | [12 empty] | SSEN will provide POC
Key
| Design assessment not essential |  |  | Design assessment necessary |  |  | SSEN will provide POC |  |  | Transformer upgrade essential |  |  |  | Awaiting requirements. SSEN will provide POC meantime
The completed network must comply with the Supply Characteristics of the Design and Planning Guidance applicable to the voltage

## Version Control
Version | Date | Notes | Author | Checked | Approved
1 | 2017-12-05 | Document updated into new format. Single customer and multi customer split into different tabs | John R. Baker | Stephen Booth | Matt Thomas