## Contents
SEPD Network Scenario Headroom Report 2023 Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations and Bulk Supply Points (BSP) up to 2050. SSEN have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN best view of the future demand and generation needs on our network is aligned to the Customer Transformation scenario. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Dem | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Gen | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
LEP Reference | This tab provides information on the LEPs, local authorities and the connected GSPs, BSPs and Primaries that support those areas
ESID | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
May 2023 Version 1.1

## Key Information
SEPD Network Scenario Headroom Report 2023 Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our other documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation or BSP as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. Where the capacity is shown as 0 MVA, this signifies that there may be no alternative supplies to restore power to these sites. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SEPD.
May 2023
Version 1.1

## Primary Headroom Dem
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Demand Headroom Winter MVA | [13 empty] | Demand Headroom Summer MVA | [13 empty] | Demand Headroom Spring/Autumn MVA
[6 empty] | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH | ALDERNEY | MINIMUM HEADROOM | SZ 04270 95141 | YES | 5.9917 | 5.8492 | 5.7152 | 5.5434 | 5.3029 | 4.9787 | 4.4824 | 3.8941 | 3.2273 | 2.4756 | 0.54534 | -3.0425 | -4.8924 | -6.0452 | 8.0317 | 7.9451 | 7.8503 | 7.7526 | 7.6201 | 7.4553 | 7.2039 | 6.9137 | 6.5092 | 5.8378 | 4.3754 | 0.18391 | -4.6552 | -9.5009 | 6.0717 | 5.9757 | 5.8788 | 5.7475 | 5.4875 | 5.1048 | 4.4987 | 3.7341 | 2.7503 | 1.6693 | -0.59384 | -4.5469 | -9.7758 | -12.3603
|  | ALDERNEY | CT |  |  | 5.9917 | 5.8647 | 5.7234 | 5.5672 | 5.3826 | 5.0946 | 4.6987 | 4.1487 | 3.4615 | 2.7392 | 1.3094 | -2.5343 | -4.8924 | -6.0452 | 8.0317 | 7.9451 | 7.8503 | 7.7526 | 7.6371 | 7.4653 | 7.2642 | 6.9895 | 6.6537 | 6.2088 | 4.9132 | 1.2142 | -1.548 | -4.6577 | 6.0717 | 5.9806 | 5.8788 | 5.769 | 5.6385 | 5.361 | 4.9324 | 4.354 | 3.5608 | 2.5273 | 0.56777 | -4.0309 | -6.3656 | -7.5373
|  | ALDERNEY | LW |  |  | 5.9942 | 5.8492 | 5.7152 | 5.5434 | 5.3029 | 4.9787 | 4.4824 | 3.8941 | 3.2273 | 2.4756 | 0.54534 | -3.0425 | -4.5946 | -5.5197 | 8.0429 | 7.9583 | 7.8786 | 7.7662 | 7.6201 | 7.4553 | 7.2039 | 6.9137 | 6.5092 | 5.8378 | 4.3754 | 2.0525 | 0.73851 | -0.24652 | 6.0758 | 5.9757 | 5.8802 | 5.7475 | 5.4875 | 5.1048 | 4.4987 | 3.7341 | 2.7503 | 1.6693 | -0.59384 | -4.5469 | -6.1526 | -6.4074
|  | ALDERNEY | ST |  |  | 6.0819 | 6.0301 | 5.9656 | 5.8608 | 5.7373 | 5.5848 | 5.388 | 5.1641 | 4.8812 | 4.5446 | 3.5927 | 0.89672 | -2.3916 | -4.2301 | 8.0765 | 8.029 | 7.9745 | 7.8858 | 7.7901 | 7.6761 | 7.5275 | 7.369 | 7.1604 | 6.9195 | 6.3096 | 2.5118 | -1.2447 | -4.7131 | 6.1269 | 6.0839 | 6.0319 | 5.94 | 5.8376 | 5.714 | 5.5523 | 5.3765 | 5.1501 | 4.8857 | 3.9438 | -0.64056 | -3.9355 | -5.7217
|  | ALDERNEY | FS |  |  | 5.9917 | 5.8647 | 5.7234 | 5.5672 | 5.3826 | 5.0946 | 4.6987 | 4.1487 | 3.4615 | 2.7392 | 1.3094 | -2.5343 | -4.8924 | -6.0452 | 9.6013 | 8.025 | 7.9674 | 7.8944 | 7.8033 | 7.6899 | 7.5488 | 7.3761 | 7.1535 | 6.8836 | 5.7761 | 0.18391 | -4.6552 | -9.5009 | 7.6503 | 6.0794 | 6.0256 | 5.9501 | 5.8531 | 5.7304 | 5.5766 | 5.2339 | 4.7564 | 4.1623 | 2.4722 | -4.0822 | -9.7758 | -12.3603
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT | MINIMUM HEADROOM | SU 85976 48834 | YES | 2.4815 | 1.9621 | 1.401 | 0.59939 | -0.40071 | -1.4383 | -3.0116 | -4.8952 | -7.0769 | -9.494 | -14.7071 | -23.8518 | -26.4648 | -27.9073 | 4.1672 | 3.8187 | 3.4308 | 2.9436 | 2.3039 | 1.6343 | 0.53284 | -0.81626 | -2.3334 | -4.0434 | -7.7893 | -14.1047 | -18.4038 | -26.4445 | 2.3961 | 1.8994 | 1.3644 | 0.61008 | -0.33747 | -1.323 | -2.8418 | -4.6686 | -6.7686 | -9.1007 | -14.1441 | -22.9205 | -25.3092 | -27.9866
|  | ALDERSHOT | CT |  |  | 2.7 | 2.3492 | 1.8401 | 1.17 | 0.43674 | -0.59672 | -1.7139 | -3.3221 | -5.5608 | -7.7229 | -11.7512 | -21.5922 | -26.2011 | -27.9073 | 4.1918 | 3.8864 | 3.4422 | 2.9732 | 2.4549 | 1.6811 | 0.83503 | -0.42462 | -2.0201 | -3.5586 | -6.4187 | -13.4219 | -17.0674 | -19.7989 | 2.5735 | 2.2214 | 1.72 | 1.0907 | 0.40119 | -0.59735 | -1.6799 | -3.2676 | -5.4049 | -7.4747 | -11.3292 | -20.6918 | -24.9673 | -26.5107
|  | ALDERSHOT | LW |  |  | 2.4815 | 1.9621 | 1.401 | 0.59939 | -0.40071 | -1.4383 | -3.0116 | -4.8952 | -7.0769 | -9.494 | -14.7071 | -23.8518 | -26.4648 | -24.8155 | 4.1672 | 3.8187 | 3.4308 | 2.9436 | 2.3039 | 1.6343 | 0.53284 | -0.81626 | -2.3334 | -4.0434 | -7.7893 | -14.1047 | -15.5159 | -13.9772 | 2.3961 | 1.8994 | 1.3644 | 0.61008 | -0.33747 | -1.323 | -2.8418 | -4.6686 | -6.7686 | -9.1007 | -14.1441 | -22.9205 | -25.3092 | -23.5785
|  | ALDERSHOT | ST |  |  | 2.9323 | 2.8051 | 2.5346 | 2.2685 | 1.9201 | 1.4646 | 0.84094 | 0.071056 | -0.85109 | -2.0059 | -5.1068 | -15.1925 | -22.0772 | -24.9245 | 4.3614 | 4.2282 | 3.9703 | 3.7166 | 3.3924 | 2.9733 | 2.4179 | 1.7314 | 0.91988 | -0.090588 | -2.7891 | -11.2451 | -17.1008 | -20.3186 | 2.7999 | 2.6702 | 2.4076 | 2.1335 | 1.777 | 1.31 | 0.67419 | -0.11455 | -1.0538 | -2.2311 | -5.3964 | -15.5632 | -22.246 | -24.7682
|  | ALDERSHOT | FS |  |  | 2.7 | 2.3492 | 1.8401 | 1.17 | 0.43674 | -0.59672 | -1.7139 | -3.3221 | -5.5608 | -7.7229 | -11.7512 | -21.5922 | -26.2011 | -27.9073 | 4.3524 | 4.2154 | 4.0137 | 3.7854 | 3.4942 | 3.1295 | 2.6637 | 2.0694 | 1.3427 | 0.13262 | -2.9774 | -10.2665 | -18.4038 | -26.4445 | 2.79 | 2.6651 | 2.4733 | 2.2204 | 1.8959 | 1.4858 | 0.95904 | 0.2799 | -0.55789 | -1.5404 | -4.4945 | -13.9857 | -22.1008 | -27.9866
MELKSHAM GSP | CHIPPENHAM | ALDERTON | MINIMUM HEADROOM | ST 84609 84059 | YES | -0.21856 | -0.45927 | 2.4083 | 2.1868 | 1.903 | 1.5919 | 1.0822 | 0.44944 | -0.28844 | -1.12 | -2.9543 | -7.7072 | -11.0432 | -11.9126 | 0.42752 | 0.29086 | 3.0349 | 2.8879 | 2.6871 | 2.426 | 2.0868 | 1.6072 | 1.0355 | 0.38728 | -1.5825 | -7.2949 | -9.7871 | -10.5989 | -0.2709 | -0.49748 | 2.1586 | 1.9463 | 1.6718 | 1.371 | 0.87274 | 0.2519 | -0.4783 | -1.3019 | -4.1264 | -11.2382 | -14.3423 | -15.3274
|  | ALDERTON | CT |  |  | -0.20514 | -0.33564 | 2.5635 | 2.3335 | 2.0784 | 1.7045 | 1.2812 | 0.69141 | -0.023815 | -0.75975 | -2.1345 | -5.1943 | -6.6478 | -7.3163 | 0.44658 | 0.32942 | 3.072 | 2.9044 | 2.7129 | 2.426 | 2.0944 | 1.6308 | 1.0697 | 0.47417 | -0.63775 | -3.2083 | -4.4728 | -5.3068 | -0.20964 | -0.38907 | 2.2936 | 2.0702 | 1.8204 | 1.4523 | 1.0324 | 0.44906 | -0.26077 | -1.0009 | -2.3812 | -5.4711 | -6.9523 | -7.6891
|  | ALDERTON | LW |  |  | -0.21856 | -0.45927 | 2.4083 | 2.1868 | 1.903 | 1.5919 | 1.0822 | 0.44944 | -0.28844 | -1.12 | -2.9543 | -6.1568 | -7.4518 | -8.3109 | 0.42752 | 0.29086 | 3.0349 | 2.8879 | 2.6871 | 2.4668 | 2.0868 | 1.6072 | 1.0355 | 0.38728 | -1.0416 | -3.5154 | -4.6677 | -5.5794 | -0.2709 | -0.49748 | 2.1586 | 1.9463 | 1.6718 | 1.371 | 0.87274 | 0.2519 | -0.4783 | -1.3019 | -3.1163 | -6.275 | -7.642 | -8.9575
|  | ALDERTON | ST |  |  | -0.18731 | -0.20504 | 2.7826 | 2.5354 | 2.261 | 1.9307 | 1.5056 | 1.0113 | 0.38485 | -0.35814 | -2.3048 | -7.7072 | -11.0432 | -11.9126 | 0.48763 | 0.4174 | 3.2077 | 3.0105 | 2.7927 | 2.5302 | 2.1822 | 1.7927 | 1.279 | 0.67445 | -0.91568 | -5.4746 | -8.4245 | -9.4921 | -0.14148 | -0.24626 | 2.5021 | 2.2491 | 1.9737 | 1.6436 | 1.2146 | 0.72459 | 0.0918 | -0.65474 | -2.6085 | -8.0869 | -11.5227 | -12.5109
|  | ALDERTON | FS |  |  | -0.20514 | -0.33564 | 2.5635 | 2.3335 | 2.0784 | 1.7045 | 1.2812 | 0.69141 | -0.023815 | -0.75975 | -2.1345 | -5.1943 | -6.6478 | -7.3163 | 0.49277 | 0.42076 | 3.2126 | 3.0801 | 2.92 | 2.7071 | 2.4332 | 2.0852 | 1.6367 | 0.7234 | -1.5825 | -7.2949 | -9.7871 | -10.5989 | -0.12178 | -0.21865 | 2.5445 | 2.3591 | 2.1463 | 1.8739 | 1.4681 | 0.7613 | -0.15228 | -1.2817 | -4.1264 | -11.2382 | -14.3423 | -15.3274
BRAMLEY (FLEE) | ALTON | ALRESFORD | MINIMUM HEADROOM | SU 59684 32511 | YES | -1.8072 | -2.218 | 7.7035 | 7.2455 | 6.7629 | 6.2569 | 5.6914 | 5.0782 | 4.4398 | 3.7706 | 2.3898 | -1.5152 | -4.113 | -5.6197 | 1.0452 | 0.8462 | 10.2438 | 10.0285 | 9.7989 | 9.5568 | 9.2719 | 8.9555 | 8.5549 | 8.0102 | 6.7703 | 0.94371 | -3.4927 | -6.4866 | -3.2189 | -3.6018 | 5.6056 | 5.1877 | 4.7473 | 4.2853 | 3.767 | 3.2048 | 2.5997 | 1.9651 | 0.25533 | -7.2541 | -12.9456 | -16.7868
|  | ALRESFORD | CT |  |  | -1.489 | -1.699 | 8.4139 | 8.0422 | 7.6335 | 7.176 | 6.6539 | 6.0861 | 5.3465 | 4.5474 | 2.8262 | -1.5152 | -4.113 | -5.6197 | 1.1501 | 1.0252 | 10.4789 | 10.2687 | 10.0278 | 9.7416 | 9.3937 | 9.0184 | 8.5549 | 8.0102 | 6.9553 | 4.2136 | 1.7536 | -0.79022 | -2.9184 | -3.1116 | 6.275 | 5.9336 | 5.5541 | 5.1264 | 4.6299 | 4.0959 | 3.3838 | 2.596 | 1.0067 | -3.1807 | -5.3987 | -6.9272
|  | ALRESFORD | LW |  |  | -1.8072 | -2.218 | 7.7035 | 7.2455 | 6.7629 | 6.2569 | 5.6914 | 5.0782 | 4.4398 | 3.7706 | 2.3898 | -0.44913 | -2.49 | -3.9618 | 1.0452 | 0.8462 | 10.2438 | 10.0285 | 9.7989 | 9.5568 | 9.2719 | 8.9555 | 8.5986 | 8.2154 | 7.4175 | 5.8534 | 4.4418 | 3.0713 | -3.2189 | -3.6018 | 5.6056 | 5.1877 | 4.7473 | 4.2853 | 3.767 | 3.2048 | 2.5997 | 1.9651 | 0.66108 | -2.0071 | -4.0806 | -5.6978
|  | ALRESFORD | ST |  |  | -1.3807 | -1.524 | 8.6465 | 8.3222 | 8.0141 | 7.6875 | 7.2999 | 6.9394 | 6.5374 | 6.1323 | 5.2738 | 2.8193 | 0.37744 | -1.9382 | 1.2001 | 1.1082 | 10.5923 | 10.3396 | 10.1101 | 9.8631 | 9.5496 | 9.2721 | 8.9258 | 8.5765 | 7.8173 | 5.5793 | 2.9959 | -0.071711 | -2.8133 | -2.9416 | 6.5013 | 6.1825 | 5.8884 | 5.5789 | 5.2025 | 4.8672 | 4.4659 | 4.0645 | 3.2101 | 0.7712 | -1.7237 | -4.1192
|  | ALRESFORD | FS |  |  | -1.489 | -1.699 | 8.4139 | 8.0422 | 7.6335 | 7.176 | 6.6539 | 6.0861 | 5.3465 | 4.5474 | 2.8262 | -1.5152 | -4.113 | -5.6197 | 1.2372 | 1.1144 | 10.576 | 10.3869 | 10.1758 | 9.9343 | 9.6553 | 9.3433 | 8.9886 | 8.5885 | 6.7703 | 0.94371 | -3.4927 | -6.4866 | -2.7384 | -2.8756 | 6.573 | 6.3241 | 6.0553 | 5.7553 | 5.4176 | 5.0438 | 4.461 | 3.2773 | 0.25533 | -7.2541 | -12.9456 | -16.7868
BRAMLEY (FLEE) | ALTON | ALTON LOCAL | MINIMUM HEADROOM | SU 72434 39606 | YES | 8.8626 | 7.4903 | 6.2073 | 4.7733 | 3.1782 | 1.5504 | -0.84316 | -3.6932 | -7.0002 | -10.5975 | -18.3096 | -32.9151 | -41.865 | -46.0964 | 17.1991 | 26.8356 | 26.0358 | 25.2016 | 24.2194 | 23.2184 | 21.5789 | 19.5695 | 17.087 | 14.3293 | 9.2096 | -3.2517 | -10.5465 | -19.4825 | 20.6447 | 19.4189 | 18.2674 | 16.9575 | 15.4669 | 13.9369 | 11.6422 | 8.8949 | 5.7085 | 2.2308 | -5.2282 | -19.5466 | -28.0392 | -32.1081
|  | ALTON LOCAL | CT |  |  | 9.4472 | 8.577 | 7.6281 | 6.3896 | 5.1013 | 3.3025 | 1.2754 | -1.4978 | -5.257 | -8.9923 | -15.9445 | -32.9151 | -41.865 | -46.0964 | 17.334 | 27.2166 | 26.523 | 25.6964 | 24.8022 | 23.4755 | 21.9455 | 19.8075 | 17.087 | 14.3293 | 9.2308 | -3.2517 | -10.5465 | -16.5829 | 21.1502 | 20.3849 | 19.5129 | 18.3539 | 17.1297 | 15.3993 | 13.4406 | 10.7475 | 7.1302 | 3.5085 | -3.2173 | -19.5466 | -28.0392 | -32.1081
|  | ALTON LOCAL | LW |  |  | 8.8626 | 7.4903 | 6.2073 | 4.7733 | 3.1782 | 1.5504 | -0.84316 | -3.6932 | -7.0002 | -10.5975 | -18.3096 | -31.9838 | -37.4327 | -37.309 | 17.1991 | 26.8356 | 26.0358 | 25.2016 | 24.2194 | 23.2184 | 21.5789 | 19.5695 | 17.2663 | 14.7156 | 9.2096 | -0.10104 | -3.7485 | -3.7609 | 20.6447 | 19.4189 | 18.2674 | 16.9575 | 15.4669 | 13.9369 | 11.6422 | 8.8949 | 5.7085 | 2.2308 | -5.2282 | -18.3046 | -23.5974 | -23.658
|  | ALTON LOCAL | ST |  |  | 9.9353 | 9.4837 | 8.9928 | 8.3218 | 7.6322 | 6.7655 | 5.6092 | 4.2988 | 2.6793 | 0.7918 | -3.9952 | -19.4079 | -30.827 | -37.2375 | 17.6581 | 27.8367 | 27.4716 | 26.8757 | 26.264 | 25.5034 | 24.4725 | 23.3416 | 21.8986 | 20.2261 | 16.0027 | 2.7321 | -7.7901 | -15.034 | 21.6112 | 21.2343 | 20.8245 | 20.1557 | 19.4661 | 18.6064 | 17.4515 | 16.1629 | 14.5448 | 12.6614 | 7.8733 | -7.5341 | -18.9029 | -24.9279
|  | ALTON LOCAL | FS |  |  | 9.4472 | 8.577 | 7.6281 | 6.3896 | 5.1013 | 3.3025 | 1.2754 | -1.4978 | -5.257 | -8.9923 | -15.9445 | -32.9151 | -41.865 | -46.0964 | 17.8233 | 27.9213 | 27.5066 | 27.0407 | 26.5212 | 25.888 | 25.1155 | 24.1971 | 23.0835 | 21.7781 | 18.4127 | 6.9794 | -6.4969 | -19.4825 | 21.8209 | 21.3796 | 20.935 | 20.3955 | 19.803 | 19.0721 | 18.1863 | 17.137 | 15.835 | 14.3233 | 8.3361 | -6.4625 | -16.1177 | -25.3457
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER | MINIMUM HEADROOM | SU 35240 46643 | YES | 19.5993 | 19.3819 | 19.1298 | 18.7396 | 18.2736 | 17.7782 | 17.1456 | 16.4353 | 15.589 | 14.0427 | 10.2592 | 3.633 | 1.5263 | 0.30305 | 20.1162 | 20.0022 | 19.8718 | 19.6776 | 19.4349 | 19.1689 | 18.8044 | 18.3799 | 17.0901 | 15.1834 | 10.2594 | 1.6847 | -1.1922 | -3.4293 | 18.5592 | 18.3597 | 18.1343 | 17.776 | 17.3515 | 16.8959 | 16.3158 | 15.6615 | 14.0343 | 11.7258 | 5.6643 | -5.0094 | -8.7625 | -11.7827
|  | ANDOVER | CT |  |  | 19.8167 | 19.7194 | 19.5853 | 19.3212 | 19.0092 | 18.6437 | 18.2308 | 17.7328 | 16.9798 | 16.2319 | 14.7233 | 10.5421 | 7.875 | 6.6189 | 20.186 | 20.1118 | 20.0135 | 19.8618 | 19.6846 | 19.4629 | 19.2083 | 18.8875 | 18.4535 | 18.0181 | 17.13 | 14.6295 | 12.8844 | 11.4863 | 18.7572 | 18.668 | 18.5499 | 18.3075 | 18.0286 | 17.6975 | 17.3242 | 16.8676 | 16.1826 | 15.5012 | 14.129 | 10.3534 | 8.0074 | 6.9457
|  | ANDOVER | LW |  |  | 19.5993 | 19.3819 | 19.1298 | 18.7396 | 18.2736 | 17.7782 | 17.1456 | 16.4353 | 15.589 | 14.0427 | 10.2592 | 3.633 | 1.5263 | 0.30305 | 20.1162 | 20.0022 | 19.8718 | 19.6776 | 19.4349 | 19.1689 | 18.8044 | 18.3799 | 17.8874 | 17.2149 | 14.4446 | 9.7063 | 8.3407 | 7.4925 | 18.5592 | 18.3597 | 18.1343 | 17.776 | 17.3515 | 16.8959 | 16.3158 | 15.6615 | 14.8803 | 13.5838 | 9.9923 | 3.7318 | 1.7826 | 0.64985
|  | ANDOVER | ST |  |  | 19.9311 | 19.9114 | 19.8602 | 19.7818 | 19.6775 | 19.5565 | 19.3987 | 19.2183 | 19.0252 | 18.8036 | 18.2399 | 16.0067 | 14.0496 | 12.2555 | 20.249 | 20.2195 | 20.1695 | 20.0991 | 20.0128 | 19.9117 | 19.7807 | 19.6348 | 19.4789 | 19.2978 | 18.8369 | 17.1458 | 15.5795 | 13.8956 | 18.8656 | 18.849 | 18.8081 | 18.7376 | 18.6478 | 18.5429 | 18.4061 | 18.2501 | 18.0823 | 17.8881 | 17.393 | 15.4112 | 13.6733 | 12.0483
|  | ANDOVER | FS |  |  | 19.8167 | 19.7194 | 19.5853 | 19.3212 | 19.0092 | 18.6437 | 18.2308 | 17.7328 | 16.9798 | 16.2319 | 14.7233 | 10.5421 | 7.875 | 6.6189 | 20.2316 | 20.1781 | 20.1002 | 19.9981 | 19.855 | 19.6748 | 19.4345 | 18.5685 | 17.0901 | 15.1834 | 10.2594 | 1.6847 | -1.1922 | -3.4293 | 18.8446 | 18.803 | 18.7316 | 18.602 | 18.4172 | 18.184 | 17.183 | 15.7883 | 14.0343 | 11.7258 | 5.6643 | -5.0094 | -8.7625 | -11.7827
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST | MINIMUM HEADROOM | SU 37953 46433 | YES | 9.4877 | 8.4366 | 7.3099 | 5.8356 | 3.7528 | 1.471 | -2.3321 | -6.642 | -11.512 | -16.6232 | -27.6706 | -45.8052 | -54.5366 | -58.0184 | 10.6814 | 9.9672 | 9.2243 | 8.2958 | 6.9106 | 4.9274 | 2.69 | -0.26419 | -4.0554 | -7.8389 | -16.4795 | -31.4283 | -38.248 | -48.5835 | 8.3731 | 7.3744 | 6.388 | 5.1185 | 3.1189 | 0.82618 | -2.7653 | -6.9869 | -11.7423 | -16.7597 | -27.6124 | -45.7218 | -53.9428 | -58.295
|  | ANDOVER EAST | CT |  |  | 9.7222 | 8.922 | 7.742 | 6.2427 | 4.3254 | 1.4779 | -1.5723 | -5.7518 | -11.0341 | -15.9139 | -24.9691 | -45.8052 | -54.5366 | -58.0184 | 10.7019 | 10.106 | 9.3057 | 8.3086 | 6.963 | 4.9274 | 2.7496 | -0.17769 | -4.0554 | -7.8389 | -14.9981 | -31.4283 | -38.248 | -41.922 | 8.5614 | 7.7897 | 6.8746 | 5.4248 | 3.5846 | 0.82618 | -2.1378 | -6.2433 | -11.4027 | -16.183 | -25.0392 | -45.7218 | -53.9428 | -56.9971
|  | ANDOVER EAST | LW |  |  | 9.4877 | 8.4366 | 7.3099 | 5.8356 | 3.7528 | 1.471 | -2.3321 | -6.642 | -11.512 | -16.6232 | -27.6706 | -45.5349 | -49.3427 | -44.9379 | 10.6814 | 9.9672 | 9.2243 | 8.2958 | 6.9106 | 5.3506 | 2.69 | -0.26419 | -3.7242 | -7.6353 | -16.4795 | -30.3682 | -32.929 | -28.7823 | 8.3731 | 7.3744 | 6.388 | 5.1185 | 3.1189 | 0.92893 | -2.7653 | -6.9869 | -11.7423 | -16.7597 | -27.6124 | -45.6325 | -49.2244 | -44.2766
|  | ANDOVER EAST | ST |  |  | 10.2552 | 9.9485 | 9.5558 | 8.9358 | 7.8075 | 6.2848 | 4.4664 | 2.5169 | 0.19594 | -2.3899 | -9.422 | -33.1106 | -48.8754 | -53.6459 | 11.0807 | 10.8553 | 10.5606 | 10.0812 | 9.2254 | 8.0616 | 6.6912 | 5.2799 | 3.5577 | 1.7023 | -3.5655 | -23.1938 | -36.3295 | -41.0648 | 9.078 | 8.79 | 8.4189 | 7.8187 | 6.8378 | 5.5086 | 3.7438 | 1.8343 | -0.43954 | -2.9949 | -9.962 | -33.8129 | -49.3877 | -53.936
|  | ANDOVER EAST | FS |  |  | 9.7222 | 8.922 | 7.742 | 6.2427 | 4.3254 | 1.4779 | -1.5723 | -5.7518 | -11.0341 | -15.9139 | -24.9691 | -45.8052 | -54.5366 | -58.0184 | 11.1682 | 10.9359 | 10.6562 | 10.2633 | 9.7019 | 8.9191 | 7.9478 | 6.8417 | 5.5519 | 4.1268 | 0.30253 | -15.5229 | -34.8562 | -48.5835 | 9.1971 | 8.9273 | 8.6022 | 8.0911 | 7.3939 | 6.5011 | 5.3309 | 3.8621 | 2.2004 | 0.33908 | -4.6903 | -23.8933 | -45.7166 | -58.295
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER TOWN | MINIMUM HEADROOM | SU 36207 45078 | YES | 1.5324 | 1.3136 | 1.0666 | 0.60485 | 0.053186 | -0.53827 | -1.2115 | -1.9619 | -2.8255 | -3.7415 | -5.7026 | -9.7058 | -12.8752 | -14.5291 | 3.5931 | 3.4735 | 3.3404 | 3.1109 | 2.8262 | 2.5189 | 2.1302 | 1.0252 | -0.51784 | -2.4247 | -6.9704 | -15.5769 | -18.5766 | -20.8403 | 1.346 | 1.1442 | 0.92293 | 0.51402 | 0.025254 | -0.49824 | -1.1151 | -1.8075 | -2.7853 | -5.1353 | -10.7268 | -21.4122 | -25.2987 | -28.3158
|  | ANDOVER TOWN | CT |  |  | 1.7178 | 1.6103 | 1.4572 | 1.0915 | 0.67687 | 0.16137 | -0.35115 | -1.015 | -1.9837 | -2.9309 | -4.7748 | -9.7058 | -12.8752 | -14.5291 | 3.6235 | 3.5167 | 3.3765 | 3.1447 | 2.8806 | 2.5376 | 2.1875 | 1.7293 | 1.123 | 0.5225 | -0.67158 | -4.0572 | -6.9485 | -9.9613 | 1.506 | 1.4021 | 1.2605 | 0.93513 | 0.56813 | 0.10505 | -0.35477 | -0.94492 | -1.8183 | -2.6739 | -4.3642 | -8.8784 | -11.7265 | -13.1741
|  | ANDOVER TOWN | LW |  |  | 1.5324 | 1.3136 | 1.0666 | 0.60485 | 0.053186 | -0.53827 | -1.2115 | -1.9619 | -2.8255 | -3.7415 | -5.7026 | -9.5553 | -11.3359 | -11.6629 | 3.5931 | 3.4735 | 3.3404 | 3.1109 | 2.8262 | 2.5189 | 2.1302 | 1.6844 | 1.1913 | 0.66183 | -0.46145 | -2.5373 | -3.3657 | -3.3499 | 1.346 | 1.1442 | 0.92293 | 0.51402 | 0.025254 | -0.49824 | -1.1151 | -1.8075 | -2.6001 | -3.4373 | -5.1943 | -8.7037 | -10.2351 | -10.4363
|  | ANDOVER TOWN | ST |  |  | 1.8513 | 1.8332 | 1.7764 | 1.662 | 1.5069 | 1.3132 | 1.1114 | 0.87472 | 0.60757 | 0.28936 | -0.55221 | -3.7393 | -6.4127 | -8.4468 | 3.6985 | 3.6495 | 3.5727 | 3.4518 | 3.3033 | 3.1264 | 2.9333 | 2.7125 | 2.4679 | 2.1783 | 1.4246 | -1.3405 | -4.1819 | -7.231 | 1.6299 | 1.611 | 1.5612 | 1.4597 | 1.3249 | 1.1624 | 0.99124 | 0.79131 | 0.56498 | 0.29339 | -0.5136 | -3.532 | -5.99 | -7.7533
|  | ANDOVER TOWN | FS |  |  | 1.7178 | 1.6103 | 1.4572 | 1.0915 | 0.67687 | 0.16137 | -0.35115 | -1.015 | -1.9837 | -2.9309 | -4.7748 | -9.7058 | -12.8752 | -14.5291 | 3.673 | 3.601 | 3.494 | 3.3359 | 3.1276 | 2.8641 | 2.2263 | 1.0252 | -0.51784 | -2.4247 | -6.9704 | -15.5769 | -18.5766 | -20.8403 | 1.5971 | 1.5585 | 1.4807 | 1.3341 | 1.1314 | 0.8685 | 0.22232 | -1.0697 | -2.7853 | -5.1353 | -10.7268 | -21.4122 | -25.2987 | -28.3158
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD | MINIMUM HEADROOM | SU 75949 65766 | YES | 7.1692 | 6.7904 | 6.4125 | 5.9327 | 5.3047 | 4.6224 | 3.5463 | 2.2219 | 0.68717 | -1.0317 | -4.8259 | -15.0567 | -22.0587 | -26.2869 | 10.5574 | 10.3062 | 10.0542 | 9.744 | 9.3212 | 8.7977 | 8.0807 | 7.1071 | 5.977 | 4.6981 | 1.8567 | -15.1254 | -29.5262 | -34.5833 | 7.7163 | 7.3731 | 7.0299 | 6.5901 | 6.0188 | 5.3952 | 4.3975 | 3.1119 | 1.6183 | -0.058126 | -3.7612 | -25.2759 | -43.0375 | -49.3695
|  | ARBORFIELD | CT |  |  | 7.2902 | 7.0264 | 6.7153 | 6.2838 | 5.805 | 5.1098 | 4.3404 | 3.2467 | 1.8327 | 0.42486 | -2.1733 | -8.3881 | -11.4279 | -12.8868 | 10.5739 | 10.3595 | 10.1046 | 9.7863 | 9.4271 | 8.8918 | 8.2898 | 7.4286 | 6.3611 | 5.2744 | 3.2722 | -1.5769 | -4.133 | -6.0465 | 7.8359 | 7.6022 | 7.3274 | 6.9384 | 6.5069 | 5.8522 | 5.0985 | 4.0251 | 2.6455 | 1.2612 | -1.2883 | -7.3725 | -10.3272 | -11.7839
|  | ARBORFIELD | LW |  |  | 7.1692 | 6.7904 | 6.4125 | 5.9327 | 5.3047 | 4.6224 | 3.5463 | 2.2219 | 0.68717 | -1.0317 | -4.8259 | -15.0567 | -22.0587 | -26.2869 | 10.5584 | 10.3062 | 10.0542 | 9.744 | 9.3212 | 8.8583 | 8.0807 | 7.1071 | 5.977 | 4.6981 | 1.8567 | -5.0777 | -10.6635 | -14.2855 | 7.7163 | 7.3731 | 7.0299 | 6.5901 | 6.0188 | 5.3952 | 4.3975 | 3.1119 | 1.6183 | -0.058126 | -3.7612 | -13.615 | -20.4565 | -24.7171
|  | ARBORFIELD | ST |  |  | 7.4765 | 7.3741 | 7.2465 | 6.9904 | 6.6942 | 6.3332 | 5.8683 | 5.3351 | 4.6891 | 3.9214 | 1.8732 | -4.7723 | -9.5225 | -11.7955 | 10.7057 | 10.614 | 10.4973 | 10.2567 | 9.995 | 9.6812 | 9.2701 | 8.8173 | 8.2562 | 7.5974 | 5.8243 | 0.11619 | -4.2028 | -6.7114 | 8.0033 | 7.9124 | 7.7995 | 7.547 | 7.2695 | 6.9371 | 6.506 | 6.0043 | 5.3516 | 4.58 | 2.5234 | -4.2924 | -9.1826 | -11.3865
|  | ARBORFIELD | FS |  |  | 7.2902 | 7.0264 | 6.7153 | 6.2838 | 5.805 | 5.1098 | 4.3404 | 3.2467 | 1.8327 | 0.42486 | -2.1733 | -8.3881 | -11.4279 | -12.8868 | 10.5574 | 10.3386 | 10.0783 | 9.7489 | 9.333 | 8.7977 | 8.0871 | 7.1548 | 6.0711 | 4.8511 | 1.872 | -15.1254 | -29.5262 | -34.5833 | 7.8505 | 7.6286 | 7.364 | 6.9988 | 6.5379 | 5.902 | 5.0483 | 3.9257 | 2.6064 | 1.129 | -3.6302 | -25.2759 | -43.0375 | -49.3695
LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD | MINIMUM HEADROOM | SZ 93193 99152 | YES | 13.5143 | 12.887 | 12.2638 | 11.3573 | 10.2294 | 9.0107 | 7.0437 | 4.6418 | 1.9119 | -1.1127 | -7.6501 | -19.2979 | -24.0009 | -27.3019 | 14.9791 | 14.5006 | 13.9275 | 13.1937 | 12.3908 | 11.2203 | 9.9471 | 8.0725 | 5.7471 | 3.4667 | -0.86203 | -12.3762 | -28.7152 | -55.1703 | 12.3872 | 11.7885 | 11.1957 | 10.349 | 9.2971 | 8.2109 | 6.4051 | 4.0658 | 1.4047 | -1.5497 | -7.9426 | -19.188 | -23.5174 | -27.0138
|  | ARGYLE ROAD | CT |  |  | 13.7276 | 13.2818 | 12.7463 | 11.8845 | 10.9183 | 9.5213 | 8.0216 | 5.7976 | 2.9426 | 0.18283 | -4.8941 | -17.4407 | -24.0009 | -27.3019 | 14.9791 | 14.5006 | 13.9275 | 13.1937 | 12.3908 | 11.2203 | 9.9471 | 8.0725 | 5.7471 | 3.4667 | -0.86203 | -12.3762 | -21.698 | -33.1031 | 12.5648 | 12.1287 | 11.6048 | 10.8127 | 9.9608 | 8.7054 | 7.2484 | 5.0706 | 2.2948 | -0.38234 | -5.3092 | -17.4086 | -23.5174 | -26.5161
|  | ARGYLE ROAD | LW |  |  | 13.5143 | 12.887 | 12.2638 | 11.3573 | 10.2294 | 9.0107 | 7.0437 | 4.6418 | 1.9119 | -1.1127 | -7.6501 | -19.2979 | -23.5594 | -22.4482 | 15.0358 | 14.5642 | 14.1002 | 13.5111 | 12.7341 | 11.9273 | 10.5176 | 8.7589 | 6.7644 | 4.5324 | -0.32407 | -8.714 | -11.2352 | -10.0127 | 12.3872 | 11.7885 | 11.1957 | 10.349 | 9.2971 | 8.2109 | 6.4051 | 4.0658 | 1.4047 | -1.5497 | -7.9426 | -19.188 | -23.1118 | -21.8521
|  | ARGYLE ROAD | ST |  |  | 14.1751 | 14.0937 | 13.9471 | 13.7357 | 13.4317 | 12.9374 | 12.258 | 11.3642 | 10.2887 | 8.9284 | 5.1575 | -7.7237 | -17.0578 | -21.0865 | 15.2809 | 15.0818 | 14.8163 | 14.462 | 14.0076 | 13.428 | 12.6958 | 11.7778 | 10.6569 | 9.2857 | 5.6056 | -7.1887 | -19.1841 | -31.3171 | 12.9879 | 12.9029 | 12.7557 | 12.5439 | 12.2407 | 11.8247 | 11.2686 | 10.4661 | 9.425 | 8.1103 | 4.4651 | -8.4583 | -17.6543 | -21.4754
|  | ARGYLE ROAD | FS |  |  | 13.7276 | 13.2818 | 12.7463 | 11.8845 | 10.9183 | 9.5213 | 8.0216 | 5.7976 | 2.9426 | 0.18283 | -4.8941 | -17.4407 | -24.0009 | -27.3019 | 15.2359 | 15.009 | 14.719 | 14.2942 | 13.7725 | 13.1419 | 12.3644 | 11.4238 | 10.2782 | 8.9271 | 5.3307 | -8.5674 | -28.7152 | -55.1703 | 12.9248 | 12.8215 | 12.6669 | 12.4019 | 12.0604 | 11.6331 | 11.0917 | 10.4148 | 9.5218 | 8.437 | 5.4471 | -6.0928 | -19.1505 | -27.0138
COWLEY GSP | HEADINGTON BSP | ARNCOTT | MINIMUM HEADROOM | SP 60730 18095 | NO | 5.9865 | 5.4174 | 4.5162 | 3.5875 | 2.4048 | 1.419 | -0.24778 | -2.2002 | -4.5264 | -7.2596 | -13.7982 | -24.8454 | -28.6742 | -31.9962 | 6.9707 | 6.612 | 6.0274 | 5.352 | 4.2723 | 3.1469 | 1.5141 | -0.034265 | -1.8544 | -4.0081 | -9.1488 | -17.8918 | -21.2977 | -24.5551 | 6.5544 | 6.0763 | 5.3416 | 4.5091 | 3.271 | 1.938 | 0.048385 | -1.8478 | -4.0963 | -6.7431 | -13.0607 | -23.7855 | -27.7518 | -31.3577
|  | ARNCOTT | CT |  |  | 6.2037 | 5.8143 | 5.0038 | 4.3381 | 3.3864 | 2.7176 | 1.7942 | 1.092 | 0.18387 | -0.67688 | -2.1608 | -5.3772 | -7.3813 | -8.6582 | 7.095 | 6.8837 | 6.3088 | 5.8891 | 5.2205 | 4.7432 | 4.0015 | 3.492 | 2.8651 | 2.2021 | 1.0202 | -1.6418 | -3.4729 | -5.1061 | 6.7233 | 6.503 | 5.8319 | 5.2598 | 4.4145 | 3.7924 | 2.9094 | 2.2299 | 1.3809 | 0.53918 | -0.9097 | -4.1624 | -6.2287 | -7.6375
|  | ARNCOTT | LW |  |  | 5.9865 | 5.4174 | 4.5162 | 3.5875 | 2.4048 | 1.419 | -0.24778 | -2.2002 | -4.5264 | -7.2596 | -13.7982 | -24.8454 | -28.6742 | -31.9962 | 6.9707 | 6.612 | 6.0274 | 5.352 | 4.2723 | 3.1469 | 1.5141 | -0.034265 | -1.8544 | -4.0081 | -9.1488 | -17.8918 | -21.2977 | -24.5551 | 6.5544 | 6.0763 | 5.3416 | 4.5091 | 3.271 | 1.938 | 0.048385 | -1.8478 | -4.0963 | -6.7431 | -13.0607 | -23.7855 | -27.7518 | -31.3577
|  | ARNCOTT | ST |  |  | 6.2873 | 5.9586 | 5.2173 | 4.5082 | 3.6175 | 3.0571 | 2.211 | 1.7319 | 1.1211 | 0.53825 | -0.73469 | -4.2372 | -7.1078 | -9.009 | 7.125 | 6.9541 | 6.4507 | 5.904 | 5.207 | 4.7562 | 4.01 | 3.629 | 3.1145 | 2.6186 | 1.5398 | -1.5295 | -4.3847 | -6.6504 | 6.7566 | 6.5645 | 6.0434 | 5.3846 | 4.5678 | 4.0329 | 3.2008 | 2.7341 | 2.1221 | 1.5374 | 0.28106 | -3.3059 | -6.3828 | -8.5066
|  | ARNCOTT | FS |  |  | 6.2037 | 5.8143 | 5.0038 | 4.3381 | 3.3864 | 2.7176 | 1.7942 | 1.092 | 0.18387 | -0.67688 | -2.1608 | -5.3772 | -7.3813 | -8.6582 | 7.1845 | 6.8634 | 6.3877 | 5.8852 | 5.2657 | 4.6601 | 3.8808 | 3.0255 | 2.0768 | 1.1035 | -0.99572 | -6.1164 | -9.8334 | -12.1414 | 6.8286 | 6.5705 | 6.01 | 5.376 | 4.6163 | 3.8671 | 2.922 | 1.8469 | 0.64314 | -0.58357 | -3.2306 | -9.6607 | -14.1403 | -16.4115
BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT | MINIMUM HEADROOM | SU 91615 68855 | YES | 12.8267 | 12.2351 | 11.6473 | 10.5718 | 9.2949 | 8.0952 | 6.4685 | 4.4251 | 2.1558 | -0.38386 | -7.1841 | -26.7943 | -37.4883 | -41.241 | 14.0856 | 13.6768 | 13.2729 | 12.4719 | 11.4847 | 10.5789 | 9.3271 | 7.8069 | 6.1693 | 4.3204 | -1.0787 | -16.0016 | -24.0994 | -26.9489 | 11.7868 | 11.2829 | 10.7796 | 9.7094 | 8.4026 | 7.2066 | 5.5885 | 3.5848 | 1.3883 | -1.0716 | -7.6182 | -26.3794 | -36.5815 | -40.1453
|  | ASCOT | CT |  |  | 13.0527 | 12.649 | 12.1897 | 11.151 | 10.0603 | 9.03 | 7.891 | 6.2633 | 4.1328 | 2.0779 | -1.7284 | -10.8755 | -15.1522 | -16.8559 | 14.1171 | 13.7701 | 13.366 | 12.4719 | 11.5049 | 10.7266 | 9.8602 | 8.5979 | 7.0437 | 5.5391 | 2.7208 | -4.1029 | -7.713 | -10.5141 | 12.0045 | 11.6752 | 11.2571 | 10.1698 | 9.0028 | 8.0048 | 6.9018 | 5.3143 | 3.2603 | 1.2796 | -2.3963 | -11.1626 | -15.1326 | -16.6608
|  | ASCOT | LW |  |  | 12.8267 | 12.2351 | 11.6473 | 10.5718 | 9.2949 | 8.0952 | 6.4685 | 4.4251 | 2.1558 | -0.38386 | -7.1841 | -26.7943 | -37.4883 | -41.241 | 14.0856 | 13.6768 | 13.2729 | 12.486 | 11.4847 | 10.5789 | 9.3271 | 7.8069 | 6.1693 | 4.3204 | -1.0787 | -16.0016 | -24.0994 | -26.9489 | 11.7868 | 11.2829 | 10.7796 | 9.7094 | 8.4026 | 7.2066 | 5.5885 | 3.5848 | 1.3883 | -1.0716 | -7.6182 | -26.3794 | -36.5815 | -40.1453
|  | ASCOT | ST |  |  | 13.2966 | 13.1136 | 12.8938 | 12.249 | 11.551 | 11.1724 | 10.6374 | 9.9263 | 9.1254 | 8.1295 | 5.4262 | -3.8712 | -10.2842 | -12.7617 | 14.3002 | 14.1327 | 13.9278 | 13.2521 | 12.5028 | 12.1109 | 11.5951 | 10.973 | 10.2767 | 9.4145 | 7.0752 | -0.58271 | -6.2311 | -9.492 | 12.2187 | 12.0809 | 11.9102 | 11.2078 | 10.4076 | 10.0328 | 9.4965 | 8.7943 | 8.006 | 7.0222 | 4.332 | -4.738 | -10.9755 | -13.2465
|  | ASCOT | FS |  |  | 13.0527 | 12.649 | 12.1897 | 11.151 | 10.0603 | 9.03 | 7.891 | 6.2633 | 4.1328 | 2.0779 | -1.7284 | -10.8755 | -15.1522 | -16.8559 | 14.2836 | 14.1033 | 13.8861 | 13.4699 | 12.9663 | 12.4961 | 11.9496 | 11.321 | 10.5864 | 9.7112 | 7.3844 | -0.75765 | -9.6492 | -17.2564 | 12.2015 | 12.0571 | 11.881 | 11.4528 | 10.9212 | 10.4264 | 9.8569 | 9.1582 | 8.3204 | 7.3249 | 4.6792 | -4.4987 | -13.628 | -19.0363
LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD | MINIMUM HEADROOM | SU 84085 06737 | YES | -2.5709 | -3.4744 | -4.4122 | 11.3387 | 9.7012 | 8.0576 | 6.247 | 4.2661 | 1.9491 | -0.69231 | -8.6075 | -21.0666 | -25.3434 | -28.1592 | 1.2193 | 0.79649 | 0.36839 | 18.4773 | 17.7378 | 16.9953 | 16.1474 | 15.1563 | 13.1546 | 10.7783 | 5.2153 | -3.3285 | -6.1146 | -9.1192 | -2.6369 | -3.3683 | -4.1139 | 13.4575 | 12.1444 | 10.8239 | 9.3616 | 7.7238 | 5.7467 | 3.5634 | -2.8288 | -14.5093 | -18.5298 | -21.2785
|  | ASHLING ROAD | CT |  |  | -2.0198 | -2.5572 | -3.1237 | 13.0329 | 11.8153 | 10.5636 | 9.2945 | 7.8206 | 5.6491 | 3.3219 | -1.2668 | -10.5969 | -16.8888 | -20.3147 | 1.3524 | 1.0243 | 0.65779 | 18.8446 | 18.2093 | 17.5304 | 16.8285 | 15.9951 | 14.8747 | 13.6678 | 11.2709 | 5.73 | 0.41401 | -6.0216 | -2.1548 | -2.5846 | -3.041 | 14.823 | 13.8533 | 12.8365 | 11.7971 | 10.5737 | 8.7729 | 6.8565 | 3.0256 | -4.9832 | -10.3674 | -13.3586
|  | ASHLING ROAD | LW |  |  | -2.5709 | -3.4744 | -4.4122 | 11.3387 | 9.7012 | 8.0576 | 6.247 | 4.2661 | 1.9491 | -0.69231 | -8.6075 | -21.0666 | -25.3434 | -28.1592 | 1.2193 | 0.79649 | 0.36839 | 18.4773 | 17.7378 | 16.9953 | 16.1474 | 15.1563 | 13.1546 | 10.7783 | 5.2153 | -3.3285 | -6.1146 | -8.2757 | -2.6369 | -3.3683 | -4.1139 | 13.4575 | 12.1444 | 10.8239 | 9.3616 | 7.7238 | 5.7467 | 3.5634 | -2.8288 | -14.5093 | -18.5298 | -21.2785
|  | ASHLING ROAD | ST |  |  | -1.8047 | -2.2133 | -2.6475 | 13.9595 | 13.2873 | 12.6634 | 12.0504 | 11.3737 | 10.6036 | 9.7104 | 7.8165 | 3.1606 | -1.2988 | -6.2166 | 1.447 | 1.1861 | 0.89768 | 19.2595 | 18.8208 | 18.3882 | 17.938 | 17.4405 | 16.8661 | 16.2051 | 14.7236 | 10.5196 | 5.4957 | -1.4186 | -1.9606 | -2.2725 | -2.6074 | 15.652 | 15.1245 | 14.6278 | 14.131 | 13.5827 | 12.9495 | 12.2166 | 10.6299 | 6.4966 | 2.5676 | -1.5791
|  | ASHLING ROAD | FS |  |  | -2.0198 | -2.5572 | -3.1237 | 13.0329 | 11.8153 | 10.5636 | 9.2945 | 7.8206 | 5.6491 | 3.3219 | -1.2668 | -10.5969 | -16.8888 | -20.3147 | 1.4589 | 1.2024 | 0.92204 | 19.2931 | 18.848 | 18.3992 | 17.9213 | 17.395 | 16.7613 | 16.0504 | 14.4603 | 9.4174 | 2.3026 | -9.1192 | -1.9151 | -2.1783 | -2.4576 | 15.8377 | 15.3336 | 14.8455 | 14.3497 | 13.8153 | 13.1429 | 12.4082 | 10.8668 | 6.525 | 2.3291 | -1.6329
MELKSHAM GSP | NORRINGTON | ASHTON PARK | MINIMUM HEADROOM | ST 87141 57741 | YES | 2.433 | 1.5478 | 0.75341 | -0.83134 | -2.7241 | -4.658 | -6.5835 | -8.5359 | -10.6158 | -12.745 | -17.104 | -27.2247 | -33.3641 | -37.5329 | 7.5123 | 7.0347 | 6.6132 | 5.8012 | 4.7784 | 3.7267 | 2.7232 | 1.7365 | 0.74314 | -0.28912 | -2.4156 | -7.4711 | -12.966 | -20.2925 | 3.5161 | 2.7777 | 2.1115 | 0.77856 | -0.83346 | -2.5202 | -4.1977 | -5.8941 | -7.7001 | -9.5543 | -13.3522 | -22.1517 | -29.382 | -34.6017
|  | ASHTON PARK | CT |  |  | 3.0362 | 2.3672 | 1.869 | 0.76454 | -0.70844 | -2.1023 | -3.3933 | -4.7617 | -6.8142 | -8.9678 | -13.207 | -22.4289 | -28.3976 | -31.6853 | 7.6868 | 7.1802 | 6.8002 | 6.2067 | 5.3238 | 4.5174 | 3.8129 | 3.0829 | 2.0755 | 0.96385 | -1.2445 | -6.5674 | -11.4575 | -17.1502 | 4.0238 | 3.4548 | 3.0383 | 2.1354 | 0.90137 | -0.25885 | -1.3394 | -2.4948 | -4.2533 | -6.1171 | -9.7754 | -17.8692 | -23.1323 | -26.0542
|  | ASHTON PARK | LW |  |  | 2.433 | 1.5478 | 0.75341 | -0.83134 | -2.7241 | -4.658 | -6.5835 | -8.5359 | -10.6158 | -12.745 | -17.104 | -27.2247 | -33.3641 | -37.5329 | 7.5123 | 7.0347 | 6.6132 | 5.8012 | 4.7784 | 3.7267 | 2.7232 | 1.7365 | 0.74314 | -0.28912 | -2.4156 | -7.4711 | -12.966 | -17.5841 | 3.5161 | 2.7777 | 2.1115 | 0.77856 | -0.83346 | -2.5202 | -4.1977 | -5.8941 | -7.7001 | -9.5543 | -13.3522 | -22.1517 | -29.382 | -34.6017
|  | ASHTON PARK | ST |  |  | 3.2106 | 2.6328 | 2.2357 | 1.4981 | 0.51799 | -0.2914 | -0.96373 | -1.5794 | -2.2577 | -2.9875 | -4.467 | -8.566 | -12.8657 | -18.0532 | 7.7566 | 7.289 | 6.9512 | 6.381 | 5.619 | 4.9857 | 4.4529 | 3.9885 | 3.44 | 2.8538 | 1.6035 | -2.0603 | -6.6429 | -13.2187 | 4.1701 | 3.6781 | 3.3469 | 2.7003 | 1.8525 | 1.163 | 0.57806 | 0.068582 | -0.50746 | -1.1203 | -2.3805 | -5.9901 | -9.8194 | -14.428
|  | ASHTON PARK | FS |  |  | 3.0362 | 2.3672 | 1.869 | 0.76454 | -0.70844 | -2.1023 | -3.3933 | -4.7617 | -6.8142 | -8.9678 | -13.207 | -22.4289 | -28.3976 | -31.6853 | 7.7798 | 7.4949 | 7.2324 | 6.7923 | 6.2582 | 5.7339 | 5.2256 | 4.718 | 4.1094 | 3.4561 | 1.9784 | -2.7798 | -9.3894 | -20.2925 | 4.2155 | 3.9407 | 3.7103 | 3.2121 | 2.6246 | 2.0607 | 1.524 | 1.0022 | 0.37049 | -0.28118 | -1.6713 | -5.8632 | -9.6839 | -13.552
BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT | MINIMUM HEADROOM | SU 91122 63523 | YES | 8.7169 | 8.2307 | 7.7372 | 6.9252 | 5.9419 | 4.8895 | 3.3372 | 1.487 | -0.65144 | -3.0389 | -8.3243 | -26.0434 | -33.2829 | -34.1447 | 11.206 | 10.8924 | 10.5081 | 9.9909 | 9.3968 | 8.5233 | 7.5124 | 6.0748 | 4.2739 | 2.4203 | -1.2578 | -14.4787 | -19.8743 | -20.5871 | 8.4061 | 7.943 | 7.4734 | 6.7037 | 5.7633 | 4.751 | 3.2413 | 1.4392 | -0.62265 | -2.9303 | -8.4032 | -25.4219 | -32.3511 | -33.2242
|  | BAGSHOT | CT |  |  | 8.9194 | 8.5693 | 8.1414 | 7.4299 | 6.6236 | 5.4874 | 4.1987 | 2.3975 | -0.088623 | -2.6334 | -7.6847 | -18.8316 | -23.4623 | -25.2385 | 11.206 | 10.8924 | 10.5081 | 9.9909 | 9.3968 | 8.5233 | 7.5124 | 6.0748 | 4.2739 | 2.4203 | -1.2578 | -9.349 | -13.0907 | -16.014 | 8.5691 | 8.2183 | 7.7884 | 7.1181 | 6.3518 | 5.2481 | 3.9891 | 2.2254 | -0.17294 | -2.632 | -7.508 | -18.179 | -22.4935 | -24.1343
|  | BAGSHOT | LW |  |  | 8.7169 | 8.2307 | 7.7372 | 6.9252 | 5.9419 | 4.8895 | 3.3372 | 1.487 | -0.65144 | -3.0389 | -8.3243 | -26.0434 | -33.2829 | -34.1447 | 11.2138 | 10.8945 | 10.5729 | 10.085 | 9.4581 | 8.77 | 7.6721 | 6.3365 | 4.8516 | 3.1688 | -1.067 | -14.4787 | -19.8743 | -20.5871 | 8.4061 | 7.943 | 7.4734 | 6.7037 | 5.7633 | 4.751 | 3.2413 | 1.4392 | -0.62265 | -2.9303 | -8.4032 | -25.4219 | -32.3511 | -33.2242
|  | BAGSHOT | ST |  |  | 9.2035 | 9.1075 | 8.9796 | 8.7184 | 8.4227 | 8.048 | 7.5473 | 6.9536 | 6.2741 | 5.4108 | 3.0112 | -5.3731 | -11.5583 | -14.6018 | 11.4148 | 11.2994 | 11.1505 | 10.87 | 10.562 | 10.1853 | 9.6881 | 9.1236 | 8.493 | 7.7176 | 5.6066 | -1.5202 | -7.0584 | -10.6278 | 8.8468 | 8.7499 | 8.6195 | 8.3399 | 8.0289 | 7.6384 | 7.1137 | 6.5021 | 5.8034 | 4.933 | 2.5325 | -5.7565 | -11.7952 | -14.6394
|  | BAGSHOT | FS |  |  | 8.9194 | 8.5693 | 8.1414 | 7.4299 | 6.6236 | 5.4874 | 4.1987 | 2.3975 | -0.088623 | -2.6334 | -7.6847 | -18.8316 | -23.4623 | -25.2385 | 11.3955 | 11.265 | 11.0975 | 10.8699 | 10.5844 | 10.2224 | 9.7643 | 9.194 | 8.5277 | 7.0719 | 2.4883 | -7.7349 | -14.2521 | -18.5015 | 8.8289 | 8.7278 | 8.5899 | 8.36 | 8.0622 | 7.6786 | 7.1873 | 6.5636 | 4.9624 | 2.7304 | -2.9324 | -15.7019 | -24.0444 | -29.6687
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL | MINIMUM HEADROOM | SU 42417 63142 | YES | 6.9781 | 6.4916 | 6.0108 | 5.4545 | 4.7854 | 3.7827 | 2.6467 | 0.95423 | -1.0734 | -3.9905 | -12.122 | -33.9571 | -47.4128 | -52.1333 | 8.4879 | 8.1633 | 7.7684 | 7.3167 | 6.8021 | 6.0083 | 5.105 | 3.7456 | 2.1343 | 0.50693 | -5.6055 | -22.6322 | -33.0548 | -36.7264 | 6.537 | 6.0716 | 5.6122 | 5.0428 | 4.3896 | 3.4051 | 2.2872 | 0.62011 | -1.3777 | -3.8857 | -11.6952 | -32.6691 | -45.5715 | -50.0963
|  | BALL HILL | CT |  |  | 6.9983 | 6.563 | 6.0474 | 5.4545 | 4.7854 | 3.7827 | 2.6467 | 0.95423 | -1.0734 | -3.9905 | -12.122 | -33.9571 | -47.4128 | -52.1333 | 8.4879 | 8.1633 | 7.7684 | 7.3167 | 6.8021 | 6.0083 | 5.105 | 3.7456 | 2.1343 | 0.50693 | -5.6055 | -22.6322 | -33.0548 | -36.7264 | 6.5424 | 6.121 | 5.6201 | 5.0428 | 4.3896 | 3.4051 | 2.2872 | 0.62011 | -1.3777 | -3.8857 | -11.6952 | -32.6691 | -45.5715 | -50.0963
|  | BALL HILL | LW |  |  | 6.9781 | 6.4916 | 6.0108 | 5.5218 | 4.8761 | 4.1867 | 3.0102 | 1.5458 | -0.052926 | -1.9027 | -5.9611 | -12.7672 | -14.3834 | -12.6493 | 8.5414 | 8.2186 | 7.9012 | 7.5374 | 7.0338 | 6.4942 | 5.5315 | 4.3306 | 3.0432 | 1.5904 | -1.6014 | -6.8977 | -8.075 | -6.546 | 6.537 | 6.0716 | 5.6122 | 5.1314 | 4.4937 | 3.8111 | 2.6413 | 1.1652 | -0.43315 | -2.2306 | -6.1782 | -12.8478 | -14.4779 | -12.7191
|  | BALL HILL | ST |  |  | 7.2853 | 7.1142 | 6.8987 | 6.5766 | 6.1988 | 5.7312 | 5.1412 | 4.4232 | 3.6196 | 2.6336 | -0.12672 | -8.7627 | -14.1439 | -15.3536 | 8.7006 | 8.5783 | 8.4205 | 8.1757 | 7.886 | 7.5152 | 7.0334 | 6.4484 | 5.7976 | 4.9863 | 2.7726 | -4.1959 | -8.6605 | -9.9937 | 6.8222 | 6.66 | 6.4542 | 6.1375 | 5.7673 | 5.3085 | 4.7253 | 4.0178 | 3.2145 | 2.2226 | -0.46236 | -8.8226 | -14.1425 | -15.3137
|  | BALL HILL | FS |  |  | 6.9983 | 6.563 | 6.0474 | 5.4545 | 4.7854 | 3.7827 | 2.6467 | 0.95423 | -1.0734 | -3.9905 | -12.122 | -33.9571 | -47.4128 | -52.1333 | 8.7178 | 8.6084 | 8.4705 | 8.2855 | 8.0603 | 7.7773 | 7.4268 | 6.9891 | 6.5073 | 5.933 | 4.3453 | -1.7511 | -8.2663 | -12.0341 | 6.8657 | 6.7323 | 6.5667 | 6.3209 | 6.0309 | 5.6701 | 5.2299 | 4.6949 | 4.0844 | 3.3661 | 1.4174 | -6.0483 | -13.7287 | -17.7677
BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY | MINIMUM HEADROOM | SU 42075 42720 | YES | -0.62845 | -1.1424 | -1.6445 | -2.2509 | -2.9618 | -4.042 | -5.2762 | -7.1134 | -9.4584 | -12.7741 | -20.8927 | -37.7886 | -47.0641 | -52.5325 | 1.5756 | 1.2273 | 0.80555 | 0.32347 | -0.22718 | -1.0888 | -2.0718 | -3.5532 | -5.3729 | -7.9681 | -14.3226 | -27.5716 | -34.8058 | -39.1442 | 0.0091362 | -0.47424 | -0.97702 | -1.5878 | -2.2838 | -3.3542 | -4.5746 | -6.4016 | -8.5775 | -11.4992 | -19.316 | -35.599 | -44.536 | -49.8308
|  | BARTON STACEY | CT |  |  | -0.61576 | -1.0768 | -1.6279 | -2.2509 | -2.9618 | -4.042 | -5.2762 | -7.1134 | -9.4584 | -12.7741 | -20.8927 | -37.7886 | -47.0641 | -52.5325 | 1.5756 | 1.2273 | 0.80555 | 0.32347 | -0.22718 | -1.0888 | -2.0718 | -3.5532 | -5.3729 | -7.9681 | -14.3226 | -27.5716 | -34.8058 | -39.1442 | 0.0091362 | -0.4393 | -0.97702 | -1.5878 | -2.2838 | -3.3542 | -4.5746 | -6.4016 | -8.5775 | -11.4992 | -19.316 | -35.599 | -44.536 | -49.8308
|  | BARTON STACEY | LW |  |  | -0.62845 | -1.1424 | -1.6445 | -2.1655 | -2.8645 | -3.6015 | -4.9045 | -6.5452 | -8.3493 | -10.3796 | -14.887 | -22.1063 | -23.6272 | -21.6159 | 1.6284 | 1.2666 | 0.91418 | 0.50723 | -0.053442 | -0.64822 | -1.7312 | -3.0836 | -4.5443 | -6.1872 | -9.7654 | -15.4605 | -16.6888 | -15.1748 | 0.019337 | -0.47424 | -0.9557 | -1.4751 | -2.1781 | -2.9212 | -4.2478 | -5.9014 | -7.692 | -9.7188 | -14.1985 | -21.3671 | -22.9109 | -20.9766
|  | BARTON STACEY | ST |  |  | -0.30245 | -0.47709 | -0.69682 | -1.0504 | -1.4675 | -1.9843 | -2.6448 | -3.4315 | -4.3415 | -5.4779 | -8.5762 | -18.5431 | -24.8886 | -26.4476 | 1.805 | 1.6809 | 1.5175 | 1.2253 | 0.88791 | 0.46708 | -0.087854 | -0.74052 | -1.496 | -2.4283 | -4.974 | -13.0527 | -18.3028 | -19.8135 | 0.31149 | 0.1463 | -0.064863 | -0.42337 | -0.84159 | -1.3608 | -2.033 | -2.8284 | -3.7518 | -4.8878 | -7.971 | -17.9147 | -24.2716 | -25.8662
|  | BARTON STACEY | FS |  |  | -0.61576 | -1.0768 | -1.6279 | -2.2509 | -2.9618 | -4.042 | -5.2762 | -7.1134 | -9.4584 | -12.7741 | -20.8927 | -37.7886 | -47.0641 | -52.5325 | 1.8195 | 1.7101 | 1.5704 | 1.3724 | 1.1231 | 0.80884 | 0.41586 | -0.065968 | -0.60118 | -1.235 | -2.9768 | -9.4227 | -16.4892 | -20.5376 | 0.34404 | 0.20399 | 0.030531 | -0.22599 | -0.54488 | -0.94185 | -1.4305 | -2.0238 | -2.6973 | -3.4864 | -5.6342 | -13.5838 | -22.3024 | -27.1418
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE | MINIMUM HEADROOM | SU 65155 52705 | YES | 18.85 | 18.5333 | 18.1497 | 17.5505 | 16.8528 | 16.0523 | 14.8679 | 13.2075 | 11.1233 | 7.97 | 1.0905 | -10.0253 | -12.8008 | -14.3676 | 17.1911 | 17.0061 | 16.7981 | 16.3514 | 15.9492 | 15.5009 | 14.8843 | 13.9166 | 11.931 | 9.5979 | 4.6284 | -3.631 | -5.6099 | -6.7807 | 16.7975 | 16.441 | 15.9896 | 15.1845 | 14.3385 | 13.5446 | 12.4076 | 10.9354 | 9.3076 | 6.7289 | 0.13568 | -10.4947 | -13.117 | -14.5972
|  | BASINGSTOKE | CT |  |  | 18.9211 | 18.7323 | 18.4505 | 17.9682 | 17.589 | 17.098 | 16.4888 | 15.4882 | 14.315 | 13.0539 | 10.2166 | 0.17726 | -4.235 | -4.3812 | 17.2384 | 17.1326 | 16.9683 | 16.518 | 16.2973 | 16.0137 | 15.6508 | 14.977 | 13.9233 | 12.7517 | 10.7051 | 4.4274 | 1.4001 | -0.57536 | 16.9383 | 16.7102 | 16.3436 | 15.5924 | 14.9998 | 14.3262 | 13.5498 | 12.3331 | 10.7856 | 9.2534 | 6.55 | -0.60004 | -4.7656 | -4.866
|  | BASINGSTOKE | LW |  |  | 18.85 | 18.5333 | 18.1497 | 17.5505 | 16.8528 | 16.0523 | 14.8679 | 13.2075 | 11.1233 | 7.97 | 1.0905 | -10.0253 | -12.8008 | -14.3676 | 17.1911 | 17.0061 | 16.7981 | 16.3514 | 15.9492 | 15.5009 | 14.8843 | 13.9166 | 11.931 | 9.5979 | 4.6284 | -3.631 | -5.6099 | -6.7807 | 16.7975 | 16.441 | 15.9896 | 15.1845 | 14.3385 | 13.5446 | 12.4076 | 10.9354 | 9.3076 | 6.7289 | 0.13568 | -10.4947 | -13.117 | -14.5972
|  | BASINGSTOKE | ST |  |  | 19.0934 | 19.0456 | 18.9155 | 18.5494 | 18.3224 | 18.1107 | 17.8155 | 17.3364 | 16.8208 | 16.2289 | 15.091 | 11.3203 | 7.6378 | 5.9896 | 17.3192 | 17.283 | 17.1946 | 16.7707 | 16.6069 | 16.449 | 16.2204 | 15.7989 | 15.3757 | 14.9106 | 14.2313 | 9.8489 | 6.1164 | 2.8091 | 17.1442 | 17.0928 | 16.922 | 16.4331 | 16.1437 | 15.8898 | 15.5325 | 14.9955 | 14.4237 | 13.7433 | 12.2147 | 7.02 | 3.4987 | 1.9366
|  | BASINGSTOKE | FS |  |  | 18.9211 | 18.7323 | 18.4505 | 17.9682 | 17.589 | 17.098 | 16.4888 | 15.4882 | 14.315 | 13.0539 | 10.2166 | 0.17726 | -4.235 | -4.3812 | 17.3297 | 17.2541 | 17.1428 | 16.9068 | 16.7134 | 16.5271 | 16.312 | 16.001 | 15.6325 | 15.2072 | 14.0154 | 9.0363 | 2.8312 | -4.4595 | 17.1047 | 17.0021 | 16.8074 | 16.4645 | 16.1358 | 15.81 | 15.4289 | 14.9062 | 14.2811 | 13.5948 | 12.0231 | 6.8263 | 1.6011 | -1.6883
NURSLING GSP | VELMORE BSP | BASSETT | MINIMUM HEADROOM | SU 42193 15958 | YES | 13.816 | 13.4816 | 13.1093 | 12.2299 | 10.0087 | 6.4985 | 1.5755 | -5.1339 | -13.7325 | -24.3904 | -50.4748 | -95.5128 | -107.7385 | -116.728 | 15.2007 | 14.9631 | 14.6357 | 14.0935 | 13.3555 | 11.5328 | 7.699 | 2.4731 | -4.1768 | -12.4616 | -32.7673 | -67.6768 | -77.1475 | -84.3335 | 13.1207 | 12.8075 | 12.4986 | 11.3633 | 9.0695 | 5.7011 | 0.96643 | -5.4773 | -13.7211 | -23.9523 | -48.9902 | -92.2056 | -103.9859 | -112.7096
|  | BASSETT | CT |  |  | 13.9695 | 13.6939 | 13.1093 | 12.2299 | 10.0087 | 6.4985 | 1.5755 | -5.1339 | -13.7325 | -24.3904 | -50.4748 | -95.5128 | -107.7385 | -116.728 | 15.2007 | 14.9631 | 14.6357 | 14.0935 | 13.3555 | 11.5328 | 7.699 | 2.4731 | -4.1768 | -12.4616 | -32.7673 | -67.6768 | -77.1475 | -84.3335 | 13.2505 | 12.988 | 12.6445 | 11.3633 | 9.0695 | 5.7011 | 0.96643 | -5.4773 | -13.7211 | -23.9523 | -48.9902 | -92.2056 | -103.9859 | -112.7096
|  | BASSETT | LW |  |  | 13.816 | 13.4816 | 13.149 | 12.4174 | 11.5822 | 10.6568 | 9.4774 | 8.1517 | 5.8709 | 2.823 | -4.9266 | -22.2137 | -34.3193 | -41.5886 | 15.2613 | 15.108 | 14.9542 | 14.557 | 14.0851 | 13.5027 | 12.7608 | 11.9281 | 11.0404 | 8.8674 | 2.9175 | -10.4146 | -20.0548 | -26.176 | 13.1207 | 12.8075 | 12.4986 | 11.7921 | 10.9815 | 10.0701 | 8.8795 | 7.3872 | 4.9707 | 2.0328 | -5.4221 | -22.0687 | -33.8546 | -41.0946
|  | BASSETT | ST |  |  | 14.2917 | 14.2824 | 14.2612 | 14.0981 | 13.9538 | 13.7918 | 13.5321 | 13.2525 | 12.9351 | 12.5521 | 11.4213 | 6.8904 | 2.9706 | 0.33022 | 15.4102 | 15.3685 | 15.3157 | 15.089 | 14.8991 | 14.6957 | 14.4056 | 14.1692 | 13.8966 | 13.4564 | 11.9771 | 6.4165 | -0.41008 | -9.0966 | 13.5516 | 13.5274 | 13.4821 | 13.2543 | 13.0484 | 12.814 | 12.4628 | 12.1278 | 11.7505 | 11.2999 | 10.0918 | 5.6102 | 1.68 | -0.94756
|  | BASSETT | FS |  |  | 13.9695 | 13.6939 | 13.1093 | 12.2299 | 10.0087 | 6.4985 | 1.5755 | -5.1339 | -13.7325 | -24.3904 | -50.4748 | -95.5128 | -107.7385 | -116.728 | 15.3816 | 15.2953 | 15.1995 | 15.042 | 14.8537 | 14.6347 | 14.3605 | 13.9477 | 13.1907 | 12.2951 | 9.9714 | 1.7856 | -10.0892 | -27.3176 | 13.4688 | 13.3651 | 13.2435 | 13.0291 | 12.7574 | 12.434 | 11.9889 | 11.4555 | 10.8335 | 10.109 | 8.2714 | 2.2635 | -3.8479 | -7.6973
NORTH HYDE GSP | NORTH HYDE (D) | BATH ROAD EAST | MINIMUM HEADROOM | TQ 09097 76885 | YES | 1.4758 | 1.0299 | 0.73246 | 0.21889 | -0.43687 | -1.2555 | -3.1428 | -5.6631 | -8.8774 | -12.9555 | -24.5804 | -70.1006 | -106.2312 | -117.332 | 2.5733 | 2.3858 | 2.1963 | 1.8607 | 1.1035 | 0.0012733 | -1.4794 | -3.4507 | -5.9451 | -9.1304 | -18.224 | -53.8942 | -82.2715 | -91.0711 | 1.4466 | 1.0558 | 0.77373 | 0.26634 | -0.38309 | -1.133 | -2.6277 | -5.0551 | -8.1429 | -12.0682 | -23.2469 | -67.0032 | -101.7406 | -112.4535
|  | BATH ROAD EAST | CT |  |  | 1.4984 | 1.1162 | 0.81571 | 0.37139 | -0.16127 | -1.2555 | -3.1428 | -5.6631 | -8.8774 | -12.9555 | -24.5804 | -70.1006 | -106.2312 | -117.332 | 2.5733 | 2.3858 | 2.1963 | 1.8607 | 1.1035 | 0.0012733 | -1.4794 | -3.4507 | -5.9451 | -9.1304 | -18.224 | -53.8942 | -82.2715 | -91.0711 | 1.4537 | 1.1144 | 0.82213 | 0.40282 | -0.099613 | -0.82805 | -2.6277 | -5.0551 | -8.1429 | -12.0682 | -23.2469 | -67.0032 | -101.7406 | -112.4535
|  | BATH ROAD EAST | LW |  |  | 1.4758 | 1.0299 | 0.73246 | 0.21889 | -0.43687 | -1.187 | -2.299 | -3.6254 | -5.6804 | -8.4721 | -15.466 | -33.1217 | -40.3333 | -41.2373 | 2.6559 | 2.503 | 2.3813 | 2.0177 | 1.5434 | 0.89667 | -0.31166 | -1.8246 | -3.6102 | -5.8072 | -11.3011 | -25.2056 | -30.9792 | -31.878 | 1.4466 | 1.0558 | 0.77373 | 0.26634 | -0.38309 | -1.133 | -2.2485 | -3.5669 | -5.225 | -7.9282 | -14.6838 | -31.7412 | -38.7638 | -39.7533
|  | BATH ROAD EAST | ST |  |  | 1.7093 | 1.5095 | 1.4236 | 1.2067 | 0.9763 | 0.68935 | 0.30866 | -0.085838 | -0.54156 | -1.0946 | -2.5997 | -7.7207 | -11.3198 | -12.7914 | 2.7273 | 2.6606 | 2.6271 | 2.4513 | 2.2979 | 2.0482 | 1.7152 | 1.4026 | 0.95446 | 0.42387 | -0.98904 | -5.8215 | -9.97 | -13.3264 | 1.6516 | 1.488 | 1.4023 | 1.1573 | 0.90895 | 0.60804 | 0.20271 | -0.20788 | -0.68045 | -1.2513 | -2.8017 | -7.9763 | -11.6617 | -13.1361
|  | BATH ROAD EAST | FS |  |  | 1.4984 | 1.1162 | 0.81571 | 0.37139 | -0.16127 | -1.2555 | -3.1428 | -5.6631 | -8.8774 | -12.9555 | -24.5804 | -70.1006 | -106.2312 | -117.332 | 2.7329 | 2.6628 | 2.6235 | 2.5459 | 2.3926 | 2.1781 | 1.9153 | 1.5816 | 1.1194 | 0.59429 | -0.7207 | -5.3224 | -11.4915 | -18.9243 | 1.6549 | 1.4902 | 1.3783 | 1.2108 | 1.0014 | 0.74376 | 0.4165 | 0.012385 | -0.43982 | -0.95365 | -2.2404 | -6.5927 | -11.2833 | -14.1032
IVER 132KV | LONGFORD | BATH ROAD WEST | MINIMUM HEADROOM | TQ 05814 76820 | YES | 14.1611 | 13.969 | 13.7136 | 13.3711 | 12.8732 | 12.1926 | 11.0892 | 9.6699 | 7.9673 | 5.9369 | 1.0799 | -5.9031 | -7.6895 | -9.2006 | 11.7959 | 11.7105 | 11.6247 | 11.4937 | 11.3091 | 11.074 | 10.5375 | 9.4311 | 8.1016 | 6.5137 | 2.7176 | -2.7382 | -4.2456 | -5.64 | 12.4194 | 12.3211 | 12.2251 | 12.0486 | 11.826 | 11.5596 | 10.8081 | 9.4417 | 7.8017 | 5.8464 | 1.1738 | -5.5582 | -7.3622 | -8.9487
|  | BATH ROAD WEST | CT |  |  | 14.2068 | 14.1226 | 13.9505 | 13.7482 | 13.5137 | 13.1538 | 12.7421 | 12.1136 | 11.2959 | 10.4176 | 8.7256 | 6.1441 | 5.4709 | 4.9341 | 11.809 | 11.7527 | 11.6906 | 11.6178 | 11.531 | 11.398 | 11.2425 | 11.0275 | 10.7047 | 10.0449 | 8.75 | 6.8117 | 6.2826 | 5.7986 | 12.4645 | 12.408 | 12.3466 | 12.2354 | 12.1076 | 11.934 | 11.7437 | 11.4903 | 11.0201 | 10.1747 | 8.5475 | 6.0613 | 5.3743 | 4.7986
|  | BATH ROAD WEST | LW |  |  | 14.1611 | 13.969 | 13.7136 | 13.3711 | 12.8732 | 12.1926 | 11.0892 | 9.6699 | 7.9673 | 5.9369 | 1.0799 | -5.9031 | -7.6895 | -9.2006 | 11.7959 | 11.7105 | 11.6247 | 11.4937 | 11.3091 | 11.074 | 10.5375 | 9.4311 | 8.1016 | 6.5137 | 2.7176 | -2.7382 | -4.2456 | -5.64 | 12.4194 | 12.3211 | 12.2251 | 12.0486 | 11.826 | 11.5596 | 10.8081 | 9.4417 | 7.8017 | 5.8464 | 1.1738 | -5.5582 | -7.3622 | -8.9487
|  | BATH ROAD WEST | ST |  |  | 14.2776 | 14.2718 | 14.2552 | 14.1964 | 14.0506 | 13.8693 | 13.6372 | 13.3639 | 13.0139 | 12.5919 | 11.472 | 8.2262 | 6.8375 | 6.1865 | 11.8596 | 11.8433 | 11.8201 | 11.7575 | 11.6904 | 11.6111 | 11.5067 | 11.3958 | 11.2439 | 11.0674 | 10.6078 | 8.0883 | 6.8734 | 6.2531 | 12.5321 | 12.5254 | 12.5084 | 12.4559 | 12.3929 | 12.3191 | 12.2181 | 12.1087 | 11.9506 | 11.7666 | 11.237 | 7.9762 | 6.5487 | 5.8256
|  | BATH ROAD WEST | FS |  |  | 14.2068 | 14.1226 | 13.9505 | 13.7482 | 13.5137 | 13.1538 | 12.7421 | 12.1136 | 11.2959 | 10.4176 | 8.7256 | 6.1441 | 5.4709 | 4.9341 | 11.8615 | 11.8493 | 11.8316 | 11.8016 | 11.7631 | 11.715 | 11.6569 | 11.5891 | 11.5053 | 11.4088 | 11.1507 | 10.0004 | 8.3384 | 7.1668 | 12.521 | 12.5143 | 12.4995 | 12.4617 | 12.4151 | 12.3587 | 12.2864 | 12.2043 | 12.097 | 11.9777 | 11.6589 | 10.2437 | 8.1114 | 6.6353
IVER 132KV | UPTON BSP | BEACONSFIELD (END B/B) | MINIMUM HEADROOM | SU 93668 91219 | YES | -0.11714 | -0.25817 | -0.48445 | -0.72323 | -1.0053 | -1.3301 | -1.7097 | -2.0485 | -2.8347 | -3.856 | -4.3651 | -3.856 | -4.3742 | -4.7615 | 1.0262 | 0.98319 | 0.93071 | 0.87365 | 0.80687 | 0.72975 | 0.62491 | 0.50148 | 0.21943 | -0.36853 | -1.5044 | -0.583 | -0.93806 | -1.5044 | 0.17614 | 0.038656 | -0.18232 | -0.4155 | -0.68844 | -1.0026 | -1.3695 | -1.6971 | -2.4478 | -3.3703 | -4.1531 | -3.3703 | -3.8093 | -4.1531
|  | BEACONSFIELD (END B/B) | CT |  |  | 1.4012 | 1.3582 | 1.3057 | 1.2487 | 1.1819 | 1.108 | 1.0284 | 0.9134 | 0.59443 | 0.0064679 | -1.1294 | -3.5255 | -4.3742 | -4.7615 | 1.0262 | 0.98319 | 0.93071 | 0.87365 | 0.80687 | 0.733 | 0.65337 | 0.5384 | 0.21943 | -0.36853 | -1.5044 | -0.36853 | -0.93806 | -1.5044 | 0.24594 | 0.14013 | -0.0033507 | -0.15645 | -0.33598 | -0.53943 | -0.76048 | -1.1127 | -1.8741 | -3.0635 | -4.1531 | -3.0635 | -3.8093 | -4.1531
|  | BEACONSFIELD (END B/B) | LW |  |  | -0.11714 | -0.25817 | -0.48445 | -0.72323 | -1.0053 | -1.3301 | -1.7097 | -2.0485 | -2.8347 | -3.856 | -4.3651 | -3.856 | -4.1883 | -4.3651 | 1.0578 | 1.0154 | 0.96569 | 0.89791 | 0.82194 | 0.72975 | 0.62491 | 0.50148 | 0.3656 | -0.070126 | -0.66924 | -0.583 | -0.66924 | -0.71801 | 0.17614 | 0.038656 | -0.18232 | -0.4155 | -0.68844 | -1.0026 | -1.3695 | -1.6971 | -2.4478 | -3.3703 | -3.8134 | -3.3703 | -3.6611 | -3.8134
|  | BEACONSFIELD (END B/B) | ST |  |  | 0.19489 | 0.13406 | 0.069427 | -0.0027079 | -0.095091 | -0.2008 | -0.32309 | -0.44959 | -1.084 | -2.0465 | -2.7815 | -2.0465 | -2.4983 | -2.7815 | 1.1069 | 1.0882 | 1.0648 | 1.037 | 1.0008 | 0.9594 | 0.9076 | 0.84267 | 0.57472 | -0.021972 | -0.74874 | -0.021972 | -0.27936 | -0.74874 | 0.48146 | 0.42263 | 0.35992 | 0.2899 | 0.20258 | 0.10247 | -0.013694 | -0.13392 | -0.73936 | -1.6585 | -2.3485 | -1.6585 | -2.0869 | -2.3485
|  | BEACONSFIELD (END B/B) | FS |  |  | 1.4012 | 1.3582 | 1.3057 | 1.2487 | 1.1819 | 1.108 | 1.0284 | 0.9134 | 0.59443 | 0.0064679 | -1.1294 | -3.5255 | -4.3742 | -4.7615 | 1.1128 | 1.0977 | 1.0766 | 1.054 | 1.0252 | 0.99136 | 0.95317 | 0.90472 | 0.73121 | 0.18161 | -1.3721 | 0.18161 | -0.5369 | -1.3721 | 0.50967 | 0.4708 | 0.41048 | 0.34856 | 0.27777 | 0.18827 | 0.090666 | -0.025306 | -0.47405 | -1.5611 | -2.2555 | -1.5611 | -2.0561 | -2.2555
IVER 132KV | DENHAM | BEACONSFIELD (MIDDLE B/B) | MINIMUM HEADROOM | SU 93668 91219 | YES | -1.7914 | -2.3566 | 0.51257 | -0.49315 | -1.673 | -3.0214 | -4.574 | -5.9731 | -9.2561 | -13.3415 | -15.3777 | -13.3415 | -15.4802 | -17.1394 | 0.24904 | -0.10176 | 3.2374 | 2.7934 | 2.2537 | 1.6355 | 0.95466 | -0.042616 | -2.0966 | -5.2323 | -9.8387 | -5.2323 | -7.5732 | -9.8387 | -1.2372 | -1.7871 | 1.079 | 0.14626 | -0.94548 | -2.2022 | -3.6697 | -4.9801 | -7.9829 | -11.6728 | -14.7767 | -11.6728 | -13.4291 | -14.7767
|  | BEACONSFIELD (MIDDLE B/B) | CT |  |  | 0.99904 | 0.64824 | 4.0624 | 3.6184 | 3.0787 | 2.4605 | 1.7797 | 0.78238 | -1.2716 | -4.4073 | -9.0137 | -12.0196 | -15.4802 | -17.1394 | 0.24904 | -0.10176 | 3.2374 | 2.7934 | 2.2537 | 1.6355 | 0.95466 | -0.042616 | -2.0966 | -5.2323 | -9.8387 | -5.2323 | -7.5732 | -9.8387 | -0.95798 | -1.3812 | 1.7949 | 1.1825 | 0.46434 | -0.34946 | -1.2337 | -2.6427 | -5.688 | -10.4456 | -14.7767 | -10.4456 | -13.4291 | -14.7767
|  | BEACONSFIELD (MIDDLE B/B) | LW |  |  | -1.7914 | -2.3566 | 0.51257 | -0.49315 | -1.673 | -3.0214 | -4.574 | -5.9731 | -9.2561 | -13.3415 | -15.3777 | -13.3415 | -14.6707 | -15.3777 | 0.62079 | 0.29948 | 3.6809 | 3.1537 | 2.5893 | 1.9044 | 1.0919 | 0.084688 | -0.78532 | -2.6257 | -5.3308 | -4.7704 | -5.3308 | -5.6243 | -1.2372 | -1.7871 | 1.079 | 0.14626 | -0.94548 | -2.2022 | -3.6697 | -4.9801 | -7.9829 | -11.6728 | -13.4452 | -11.6728 | -12.8363 | -13.4452
|  | BEACONSFIELD (MIDDLE B/B) | ST |  |  | -0.52481 | -0.7245 | 2.857 | 2.5656 | 2.1924 | 1.7665 | 1.2751 | 0.76132 | -1.7759 | -5.7006 | -8.8093 | -5.7006 | -7.6039 | -8.8093 | 0.95733 | 0.74323 | 4.2761 | 4.0321 | 3.7285 | 3.3789 | 2.9701 | 2.5725 | 0.55458 | -2.6055 | -6.6804 | -2.6055 | -4.5468 | -6.6804 | -0.015902 | -0.2512 | 3.248 | 2.9679 | 2.6186 | 2.2182 | 1.7535 | 1.2726 | -1.1492 | -4.8257 | -7.5856 | -4.8257 | -6.5394 | -7.5856
|  | BEACONSFIELD (MIDDLE B/B) | FS |  |  | 0.99904 | 0.64824 | 4.0624 | 3.6184 | 3.0787 | 2.4605 | 1.7797 | 0.78238 | -1.2716 | -4.4073 | -9.0137 | -12.0196 | -15.4802 | -17.1394 | 1.0086 | 0.84289 | 4.3961 | 4.1855 | 3.9378 | 3.6226 | 3.2708 | 2.868 | 1.2636 | -2.8182 | -9.2405 | -2.8182 | -5.7757 | -9.2405 | 0.096968 | -0.058524 | 3.4502 | 3.2025 | 2.9194 | 2.5614 | 2.1709 | 1.707 | -0.087908 | -4.4361 | -7.2136 | -4.4361 | -6.4162 | -7.2136
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM | MINIMUM HEADROOM | SU 58204 69025 | YES | 3.155 | 2.9824 | 2.8045 | 2.6483 | 2.4777 | 2.279 | 2.043 | 1.6767 | 0.73845 | -0.40814 | -3.249 | -7.7618 | -8.8984 | -9.6485 | 4.7337 | 4.6202 | 4.4937 | 4.3301 | 4.1039 | 3.7704 | 3.2993 | 2.6945 | 1.9795 | 1.1014 | -1.0848 | -6.5864 | -16.1357 | -21.2967 | 3.4702 | 3.3423 | 3.2098 | 3.0735 | 2.9197 | 2.7385 | 2.2519 | 1.4938 | 0.59481 | -0.50425 | -3.228 | -10.0279 | -21.7809 | -28.1392
|  | BEENHAM | CT |  |  | 3.2853 | 3.1769 | 3.0679 | 2.9472 | 2.8134 | 2.6696 | 2.4999 | 2.3126 | 2.0401 | 1.2784 | -0.41876 | -3.3805 | -4.3333 | -4.862 | 4.7877 | 4.7133 | 4.6271 | 4.5174 | 4.3776 | 4.1598 | 3.8678 | 3.4779 | 2.9929 | 2.4243 | 1.1503 | -1.0527 | -1.665 | -2.0424 | 3.5668 | 3.4869 | 3.4064 | 3.3154 | 3.2133 | 3.0947 | 2.9483 | 2.4895 | 1.865 | 1.1386 | -0.48102 | -3.3044 | -4.1919 | -4.6904
|  | BEENHAM | LW |  |  | 3.155 | 2.9824 | 2.8045 | 2.6483 | 2.4777 | 2.279 | 2.043 | 1.6767 | 0.73845 | -0.40814 | -3.249 | -7.7618 | -8.8984 | -9.6485 | 4.7337 | 4.6202 | 4.4937 | 4.3301 | 4.1039 | 3.7704 | 3.2993 | 2.6945 | 1.9795 | 1.1014 | -1.0848 | -4.5333 | -5.3566 | -5.9235 | 3.4702 | 3.3423 | 3.2098 | 3.0735 | 2.9197 | 2.7385 | 2.2519 | 1.4938 | 0.59481 | -0.50425 | -3.228 | -7.5545 | -8.6339 | -9.3484
|  | BEENHAM | ST |  |  | 3.3469 | 3.2801 | 3.2095 | 3.0947 | 2.9839 | 2.8683 | 2.745 | 2.6245 | 2.5077 | 2.3814 | 2.1131 | 1.4639 | 1.0415 | 0.75283 | 4.8453 | 4.8167 | 4.7843 | 4.7138 | 4.6467 | 4.5743 | 4.487 | 4.4033 | 4.3182 | 4.2202 | 3.9806 | 3.2468 | 2.9703 | 2.8824 | 3.6121 | 3.5628 | 3.5105 | 3.4144 | 3.3244 | 3.231 | 3.1277 | 3.0277 | 2.9268 | 2.8175 | 2.5831 | 2.0128 | 1.6226 | 1.3846
|  | BEENHAM | FS |  |  | 3.2853 | 3.1769 | 3.0679 | 2.9472 | 2.8134 | 2.6696 | 2.4999 | 2.3126 | 2.0401 | 1.2784 | -0.41876 | -3.3805 | -4.3333 | -4.862 | 4.794 | 4.7326 | 4.6545 | 4.5299 | 4.3618 | 4.1462 | 3.8687 | 3.5159 | 3.0862 | 2.5433 | 0.92969 | -6.5864 | -16.1357 | -21.2967 | 3.6301 | 3.5892 | 3.5437 | 3.4607 | 3.3732 | 3.2787 | 3.054 | 2.6028 | 2.0518 | 1.3615 | -0.66357 | -10.0279 | -21.7809 | -28.1392
MANNINGTON GSP | SALISBURY | BEMERTON | MINIMUM HEADROOM | SU 11583 31233 | YES | 17.1326 | 16.4403 | 15.8943 | 15.2018 | 14.3185 | 13.3798 | 12.5874 | 11.7634 | 10.6173 | 9.6031 | 7.4366 | 2.6339 | -0.27996 | -2.0601 | 17.9061 | 17.423 | 17.0948 | 16.7076 | 16.192 | 15.5891 | 15.1109 | 14.6316 | 13.9213 | 13.317 | 11.9375 | 0.19644 | -6.1245 | -6.4907 | 16.6387 | 16.0296 | 15.5596 | 14.9537 | 14.1756 | 13.3322 | 12.5996 | 11.8343 | 10.7697 | 9.8283 | 7.797 | -6.457 | -14.4231 | -15.1293
|  | BEMERTON | CT |  |  | 17.4681 | 16.9426 | 16.6346 | 16.1515 | 15.3803 | 14.4145 | 13.7717 | 12.9919 | 11.6769 | 10.5211 | 8.3768 | 3.0809 | -0.24895 | -2.0601 | 18.0765 | 17.6521 | 17.4611 | 17.1936 | 16.6956 | 15.9851 | 15.5522 | 15.029 | 14.1464 | 13.3821 | 11.9764 | 8.4542 | 5.8928 | 3.3669 | 16.9345 | 16.4689 | 16.2096 | 15.7897 | 15.1069 | 14.2301 | 13.6339 | 12.9077 | 11.6893 | 10.6137 | 8.6185 | 3.7224 | 0.69837 | -0.95511
|  | BEMERTON | LW |  |  | 17.1326 | 16.4403 | 15.8943 | 15.2018 | 14.3185 | 13.3798 | 12.5874 | 11.7634 | 10.6173 | 9.6031 | 7.4366 | 2.6339 | -0.27996 | -1.5355 | 17.9061 | 17.423 | 17.0948 | 16.7076 | 16.192 | 15.5891 | 15.1109 | 14.6316 | 13.9213 | 13.317 | 11.9375 | 8.9986 | 7.2413 | 5.4415 | 16.6387 | 16.0296 | 15.5596 | 14.9537 | 14.1756 | 13.3322 | 12.5996 | 11.8343 | 10.7697 | 9.8283 | 7.797 | 3.3305 | 0.65625 | -1.4836
|  | BEMERTON | ST |  |  | 17.6118 | 17.1819 | 16.9842 | 16.7194 | 16.2275 | 15.5939 | 15.2754 | 14.9361 | 14.3401 | 13.8835 | 12.8991 | 9.5007 | 6.4601 | 3.9716 | 18.1514 | 17.7827 | 17.6562 | 17.4542 | 17.0669 | 16.5124 | 16.2313 | 15.9556 | 15.4389 | 15.0666 | 14.2248 | 11.3017 | 8.4149 | 5.5392 | 17.0668 | 16.6915 | 16.5363 | 16.2972 | 15.8572 | 15.2785 | 14.9715 | 14.6618 | 14.1038 | 13.6664 | 12.7049 | 9.4223 | 6.5085 | 4.1974
|  | BEMERTON | FS |  |  | 17.4681 | 16.9426 | 16.6346 | 16.1515 | 15.3803 | 14.4145 | 13.7717 | 12.9919 | 11.6769 | 10.5211 | 8.3768 | 3.0809 | -0.24895 | -2.0601 | 18.2295 | 17.9448 | 17.7357 | 17.5083 | 17.1923 | 16.8119 | 16.484 | 16.1289 | 15.6146 | 15.0733 | 12.1781 | 0.19644 | -6.1245 | -6.4907 | 17.1546 | 16.8682 | 16.6486 | 16.381 | 16.02 | 15.6034 | 15.2453 | 14.8507 | 14.0196 | 12.5473 | 8.4151 | -6.457 | -14.4231 | -15.1293
COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD | MINIMUM HEADROOM | SU 58382 95467 | NO | 9.2007 | 8.2151 | 7.0653 | 5.3276 | 2.8515 | -0.22214 | -4.2718 | -8.8742 | -13.8315 | -19.0441 | -30.2467 | -48.5457 | -52.2264 | -53.714 | 13.1434 | 12.4353 | 11.6542 | 10.5799 | 9.0794 | 7.0608 | 4.2013 | 0.95551 | -2.3645 | -5.8851 | -13.3894 | -25.5159 | -34.841 | -41.9352 | 13.5479 | 12.5726 | 11.4944 | 9.9454 | 7.7529 | 4.9257 | 1.0293 | -3.3994 | -7.9909 | -12.8298 | -23.1867 | -40.0998 | -46.8336 | -54.3893
|  | BERINSFIELD | CT |  |  | 9.4276 | 8.7245 | 7.7586 | 6.0977 | 3.9149 | 0.83433 | -2.5361 | -7.0345 | -12.2551 | -17.495 | -27.7274 | -45.1683 | -51.5115 | -53.714 | 13.1934 | 12.62 | 11.874 | 10.7489 | 9.3704 | 7.1355 | 4.6504 | 1.437 | -2.1558 | -5.6908 | -12.3423 | -24.9086 | -29.799 | -32.176 | 13.6921 | 12.9517 | 11.9663 | 10.4367 | 8.5003 | 5.5254 | 2.2451 | -2.0144 | -6.8957 | -11.7383 | -21.0089 | -37.5934 | -43.6938 | -45.8121
|  | BERINSFIELD | LW |  |  | 9.2007 | 8.2151 | 7.0653 | 5.3276 | 2.8515 | -0.22214 | -4.2718 | -8.8742 | -13.8315 | -19.0441 | -30.2467 | -48.5457 | -52.2264 | -49.7009 | 13.1434 | 12.4353 | 11.6542 | 10.5799 | 9.0794 | 7.0608 | 4.2013 | 0.95551 | -2.3645 | -5.8851 | -13.3894 | -25.5159 | -27.9953 | -25.8608 | 13.5479 | 12.5726 | 11.4944 | 9.9454 | 7.7529 | 4.9257 | 1.0293 | -3.3994 | -7.9909 | -12.8298 | -23.1867 | -40.0998 | -43.612 | -41.1186
|  | BERINSFIELD | ST |  |  | 9.8224 | 9.483 | 8.9231 | 7.8251 | 6.3463 | 4.4789 | 2.3971 | 0.055522 | -2.4526 | -5.4034 | -12.6083 | -29.2352 | -39.4381 | -42.7545 | 13.3348 | 13.205 | 12.8829 | 12.1333 | 11.1699 | 9.7537 | 8.0896 | 6.2268 | 4.2712 | 2.0727 | -3.1962 | -16.4748 | -24.9203 | -28.0577 | 14.1252 | 13.8034 | 13.2901 | 12.31 | 11.0076 | 9.2037 | 7.1217 | 4.7814 | 2.2691 | -0.5831 | -7.4724 | -24.3374 | -34.6587 | -37.835
|  | BERINSFIELD | FS |  |  | 9.4276 | 8.7245 | 7.7586 | 6.0977 | 3.9149 | 0.83433 | -2.5361 | -7.0345 | -12.2551 | -17.495 | -27.7274 | -45.1683 | -51.5115 | -53.714 | 13.4302 | 12.9593 | 12.3622 | 11.5339 | 10.4501 | 8.8095 | 6.7959 | 4.4118 | 1.8787 | -0.80539 | -6.8497 | -22.2633 | -34.841 | -41.9352 | 14.0319 | 13.439 | 12.679 | 11.5884 | 10.1505 | 8.0865 | 5.5643 | 2.5761 | -0.63799 | -4.0482 | -11.7385 | -31.3517 | -46.8336 | -54.3893
NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY | MINIMUM HEADROOM | SU 42648 13187 | YES | 15.4381 | 15.0195 | 14.4244 | 13.8098 | 13.4943 | 13.1838 | 12.8405 | 12.4178 | 11.9816 | 11.5264 | 10.6077 | 8.2359 | 6.6209 | 5.7163 | 17.3617 | 17.0944 | 16.7242 | 16.2787 | 15.8781 | 15.3512 | 14.7315 | 14.0115 | 13.1594 | 12.1233 | 9.5358 | -1.7343 | -23.0711 | -61.7256 | 14.3807 | 14.029 | 13.5322 | 13.0082 | 12.7266 | 12.4487 | 12.1386 | 11.7531 | 11.3489 | 10.9263 | 10.0733 | 7.8866 | 5.4783 | 2.3129
|  | BEVOIS VALLEY | CT |  |  | 15.5888 | 15.2973 | 14.8251 | 14.3221 | 14.0919 | 13.8111 | 13.4643 | 12.9834 | 12.4256 | 11.8822 | 10.8351 | 8.2359 | 6.6209 | 5.7163 | 17.3617 | 17.0944 | 16.7242 | 16.2787 | 15.9189 | 15.4914 | 14.9932 | 14.3571 | 13.6606 | 12.9108 | 11.2186 | 4.8441 | -5.7164 | -24.1525 | 14.5145 | 14.2724 | 13.8804 | 13.4507 | 13.2431 | 12.9902 | 12.6811 | 12.2483 | 11.7441 | 11.2453 | 10.2819 | 7.8866 | 6.3526 | 5.4537
|  | BEVOIS VALLEY | LW |  |  | 15.4381 | 15.0195 | 14.4244 | 13.8098 | 13.4943 | 13.1838 | 12.8405 | 12.4178 | 11.9816 | 11.5264 | 10.6077 | 8.7775 | 7.7603 | 6.9874 | 17.4225 | 17.2203 | 16.94 | 16.6649 | 16.5253 | 16.3852 | 16.2164 | 15.976 | 15.7346 | 15.4786 | 14.9604 | 13.9863 | 13.2532 | 12.5192 | 14.3807 | 14.029 | 13.5322 | 13.0082 | 12.7266 | 12.4487 | 12.1386 | 11.7531 | 11.3489 | 10.9263 | 10.0733 | 8.3637 | 7.316 | 6.4609
|  | BEVOIS VALLEY | ST |  |  | 15.8127 | 15.6388 | 15.297 | 15.0857 | 15.1185 | 15.1294 | 15.1011 | 14.9895 | 14.9135 | 14.8421 | 14.665 | 12.9899 | 12.0474 | 11.1894 | 17.4578 | 17.2445 | 16.9338 | 16.6013 | 16.3486 | 16.047 | 15.6862 | 15.2193 | 14.73 | 14.1958 | 12.8627 | 7.1178 | -3.3972 | -22.1037 | 14.713 | 14.5756 | 14.2998 | 14.1292 | 14.1553 | 14.1625 | 14.1371 | 14.0347 | 13.9566 | 13.8803 | 13.6899 | 12.5589 | 11.5573 | 10.24
|  | BEVOIS VALLEY | FS |  |  | 15.5888 | 15.2973 | 14.8251 | 14.3221 | 14.0919 | 13.8111 | 13.4643 | 12.9834 | 12.4256 | 11.8822 | 10.8351 | 8.2359 | 6.6209 | 5.7163 | 17.4055 | 17.1684 | 16.8306 | 16.3374 | 15.8781 | 15.3512 | 14.7315 | 14.0115 | 13.1594 | 12.1233 | 9.5358 | -1.7343 | -23.0711 | -61.7256 | 14.6429 | 14.5238 | 14.3121 | 14.1092 | 14.0244 | 13.9177 | 13.7891 | 13.624 | 13.4569 | 13.2616 | 12.7407 | 10.013 | 5.4783 | 2.3129
EAST CLAYDON GSP | BICESTER NORTH | BICESTER | MINIMUM HEADROOM | SP 58381 21988 | NO | 38.3027 | 38.3004 | 38.2967 | 38.2913 | 38.2833 | 38.2715 | 38.2545 | 38.231 | 38.2007 | 38.163 | 38.0735 | 37.891 | 37.8374 | 37.7995 | 39.0658 | 39.0308 | 38.9969 | 38.9593 | 38.9055 | 38.8497 | 38.7409 | 38.6019 | 38.4493 | 38.2772 | 37.9023 | 37.3281 | 37.2485 | 37.4668 | 34.7757 | 34.7382 | 34.7018 | 34.6615 | 34.6038 | 34.544 | 34.4273 | 34.2783 | 34.1148 | 33.916 | 33.4522 | 32.7418 | 32.6433 | 32.9134
|  | BICESTER | CT |  |  | 38.3035 | 38.3022 | 38.3004 | 38.2979 | 38.2943 | 38.2893 | 38.2823 | 38.2725 | 38.2598 | 38.243 | 38.1937 | 38.0103 | 37.8992 | 37.9117 | 39.0963 | 39.0952 | 39.0936 | 39.0914 | 39.0882 | 39.0838 | 39.0776 | 39.069 | 39.0577 | 39.043 | 38.9994 | 38.8375 | 38.7587 | 38.7672 | 34.8076 | 34.8057 | 34.8032 | 34.7997 | 34.7947 | 34.7875 | 34.7776 | 34.7638 | 34.7458 | 34.7222 | 34.6524 | 34.3932 | 34.2669 | 34.2806
|  | BICESTER | LW |  |  | 38.3027 | 38.3004 | 38.2967 | 38.2913 | 38.2833 | 38.2715 | 38.2545 | 38.231 | 38.2007 | 38.163 | 38.0735 | 37.891 | 37.8374 | 37.7995 | 39.0957 | 39.0936 | 39.0904 | 39.0856 | 39.0785 | 39.0681 | 39.0531 | 39.0324 | 39.0056 | 38.9723 | 38.8934 | 38.7528 | 38.7162 | 38.6903 | 34.8065 | 34.8032 | 34.7981 | 34.7905 | 34.7791 | 34.7624 | 34.7385 | 34.7052 | 34.6624 | 34.6092 | 34.4828 | 34.2583 | 34.2 | 34.097
|  | BICESTER | ST |  |  | 38.3045 | 38.304 | 38.3034 | 38.3026 | 38.3015 | 38.3 | 38.2979 | 38.2952 | 38.2915 | 38.2868 | 38.2734 | 38.2298 | 38.218 | 38.2296 | 39.0973 | 39.0969 | 39.0965 | 39.0958 | 39.0949 | 39.0937 | 39.0921 | 39.09 | 39.0871 | 39.0834 | 39.0729 | 39.0387 | 39.0295 | 39.0386 | 34.8094 | 34.809 | 34.8085 | 34.8078 | 34.8068 | 34.8055 | 34.8037 | 34.8014 | 34.7983 | 34.7942 | 34.7827 | 34.7456 | 34.7356 | 34.7453
|  | BICESTER | FS |  |  | 38.3035 | 38.3022 | 38.3004 | 38.2979 | 38.2943 | 38.2893 | 38.2823 | 38.2725 | 38.2598 | 38.243 | 38.1937 | 38.0103 | 37.8992 | 37.9117 | 39.0658 | 39.0308 | 38.9969 | 38.9593 | 38.9055 | 38.8497 | 38.7409 | 38.6019 | 38.4493 | 38.2772 | 37.9023 | 37.3281 | 37.2485 | 37.4668 | 34.7757 | 34.7382 | 34.7018 | 34.6615 | 34.6038 | 34.544 | 34.4273 | 34.2783 | 34.1148 | 33.916 | 33.4522 | 32.7418 | 32.6433 | 32.9134
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST | MINIMUM HEADROOM | TQ 08305 26315 | YES | 2.3306 | 2.0377 | 1.7189 | 1.269 | 0.76946 | 0.30625 | -0.43968 | -2.0466 | -4.1504 | -6.7162 | -12.9013 | -23.8842 | -27.4421 | -29.9213 | 4.0592 | 3.8949 | 3.7155 | 3.4492 | 3.1478 | 2.7764 | 2.1904 | 0.96396 | -0.61069 | -2.5408 | -7.2159 | -15.3464 | -17.7332 | -19.455 | 2.7046 | 2.442 | 2.1611 | 1.7591 | 1.309 | 0.88235 | 0.34159 | -1.1492 | -3.1554 | -5.6019 | -11.5005 | -21.9331 | -25.2449 | -27.5548
|  | BILLINGSHURST | CT |  |  | 2.4545 | 2.2319 | 1.9507 | 1.5247 | 1.0676 | 0.53622 | -0.43968 | -2.0466 | -4.1504 | -6.7162 | -12.9013 | -23.8842 | -27.4421 | -29.9213 | 4.0823 | 3.9216 | 3.7208 | 3.4492 | 3.1478 | 2.7764 | 2.1904 | 0.96396 | -0.61069 | -2.5408 | -7.2159 | -15.3464 | -17.7332 | -19.455 | 2.8192 | 2.6185 | 2.368 | 1.9844 | 1.5647 | 1.0686 | 0.38868 | -1.1492 | -3.1554 | -5.6019 | -11.5005 | -21.9331 | -25.2449 | -27.5548
|  | BILLINGSHURST | LW |  |  | 2.3306 | 2.0377 | 1.7189 | 1.269 | 0.76946 | 0.30625 | -0.28405 | -0.9661 | -1.7418 | -2.6863 | -4.8819 | -9.0199 | -11.0072 | -11.4926 | 4.0592 | 3.8949 | 3.7155 | 3.4644 | 3.1756 | 2.8978 | 2.5171 | 2.0491 | 1.5352 | 0.92142 | -0.48876 | -3.0138 | -4.0255 | -4.4409 | 2.7046 | 2.442 | 2.1611 | 1.7591 | 1.309 | 0.88235 | 0.34159 | -0.27887 | -0.98278 | -1.8314 | -3.8139 | -7.5985 | -9.3087 | -9.7079
|  | BILLINGSHURST | ST |  |  | 2.5736 | 2.4446 | 2.2685 | 2.0071 | 1.7247 | 1.4357 | 1.1098 | 0.70116 | 0.21019 | -0.41695 | -2.0687 | -6.3146 | -8.8994 | -10.4357 | 4.1512 | 4.0518 | 3.9212 | 3.7366 | 3.5328 | 3.3027 | 3.0302 | 2.6934 | 2.2918 | 1.7857 | 0.46981 | -2.881 | -4.9764 | -6.4371 | 2.9334 | 2.8219 | 2.6733 | 2.448 | 2.2037 | 1.9498 | 1.6622 | 1.3048 | 0.86402 | 0.25463 | -1.3408 | -5.455 | -7.8331 | -9.0677
|  | BILLINGSHURST | FS |  |  | 2.4545 | 2.2319 | 1.9507 | 1.5247 | 1.0676 | 0.53622 | -0.43968 | -2.0466 | -4.1504 | -6.7162 | -12.9013 | -23.8842 | -27.4421 | -29.9213 | 4.1441 | 4.0657 | 3.9553 | 3.8039 | 3.6373 | 3.4517 | 3.2308 | 2.9596 | 2.6456 | 2.2617 | 1.2013 | -2.6718 | -6.9035 | -10.3175 | 2.9307 | 2.852 | 2.7331 | 2.5429 | 2.339 | 2.1234 | 1.8862 | 1.5937 | 1.2482 | 0.82418 | -0.44279 | -5.0432 | -9.731 | -12.5248
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM | MINIMUM HEADROOM | SU 97366 01594 | YES | 13.3383 | 12.3529 | 11.0515 | 9.2423 | 7.134 | 5.1519 | 2.6503 | -0.20432 | -3.2575 | -6.4961 | -12.9693 | -25.6016 | -28.808 | -29.6828 | 15.2872 | 14.7324 | 14.0238 | 13.0741 | 11.9494 | 10.878 | 9.4294 | 7.7459 | 5.9291 | 3.9657 | -0.051392 | -7.4354 | -11.086 | -19.1547 | 13.1399 | 12.4578 | 11.4135 | 9.9164 | 8.1512 | 6.4622 | 4.3105 | 1.8459 | -0.80479 | -3.6336 | -9.5152 | -20.7622 | -23.6866 | -24.8604
|  | BILSHAM | CT |  |  | 13.5958 | 12.8562 | 11.7688 | 10.2172 | 8.4969 | 6.6578 | 4.6641 | 2.0592 | -1.1033 | -4.3093 | -10.2223 | -21.3039 | -26.8918 | -29.6828 | 15.332 | 14.8568 | 14.188 | 13.3119 | 12.3472 | 11.2482 | 10.0531 | 8.4461 | 6.5325 | 4.5992 | 0.99796 | -6.4916 | -11.086 | -15.0212 | 13.4101 | 12.9149 | 12.0537 | 10.7789 | 9.3502 | 7.7911 | 6.0882 | 3.8529 | 1.1087 | -1.7222 | -6.9853 | -17.1679 | -22.3121 | -24.8604
|  | BILSHAM | LW |  |  | 13.3383 | 12.3529 | 11.0515 | 9.2423 | 7.134 | 5.1519 | 2.6503 | -0.20432 | -3.2575 | -6.4961 | -12.9693 | -25.6016 | -28.808 | -28.8007 | 15.2872 | 14.7324 | 14.0238 | 13.0741 | 11.9494 | 10.878 | 9.4294 | 7.7459 | 5.9291 | 3.9657 | -0.051392 | -7.4354 | -9.3006 | -9.0734 | 13.1399 | 12.4578 | 11.4135 | 9.9164 | 8.1512 | 6.4622 | 4.3105 | 1.8459 | -0.80479 | -3.6336 | -9.5152 | -20.7622 | -23.6866 | -23.5765
|  | BILSHAM | ST |  |  | 13.807 | 13.2823 | 12.4241 | 11.3676 | 10.238 | 9.2055 | 8.0657 | 6.7451 | 5.2949 | 3.6376 | -0.083746 | -9.3483 | -15.8959 | -19.4689 | 15.4685 | 15.1472 | 14.6471 | 14.0158 | 13.3317 | 12.6688 | 11.9123 | 11.0338 | 10.051 | 8.9137 | 6.2265 | -1.1611 | -7.1065 | -11.4822 | 13.5475 | 13.2157 | 12.6417 | 11.8175 | 10.9347 | 10.1149 | 9.1986 | 8.1391 | 6.9645 | 5.6099 | 2.2944 | -6.627 | -13.032 | -16.1372
|  | BILSHAM | FS |  |  | 13.5958 | 12.8562 | 11.7688 | 10.2172 | 8.4969 | 6.6578 | 4.6641 | 2.0592 | -1.1033 | -4.3093 | -10.2223 | -21.3039 | -26.8918 | -29.6828 | 15.4537 | 15.1272 | 14.6428 | 14.0314 | 13.342 | 12.6221 | 11.7965 | 10.8204 | 9.3406 | 7.2939 | 2.5533 | -6.9527 | -10.8775 | -19.1547 | 13.5396 | 13.2284 | 12.7367 | 11.9735 | 11.1216 | 10.2555 | 9.2726 | 8.1228 | 6.5221 | 4.0468 | -1.7435 | -13.5386 | -18.6446 | -22.4814
FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD | MINIMUM HEADROOM | SZ 56409 91399 | YES | 7.8242 | 7.6032 | 7.3816 | 7.0013 | 6.5616 | 6.0998 | 5.4691 | 4.7326 | 3.8152 | 2.8107 | 0.63403 | -4.0291 | -8.2762 | -8.9634 | 9.2454 | 9.1062 | 8.9677 | 8.7632 | 8.5075 | 8.2351 | 7.8098 | 7.0761 | 5.7361 | 4.0595 | -0.25161 | -7.5846 | -10.0111 | -12.1103 | 7.7199 | 7.536 | 7.3504 | 7.0171 | 6.6357 | 6.2163 | 5.6473 | 4.9497 | 3.998 | 1.9354 | -3.3585 | -12.472 | -15.6427 | -18.4004
|  | BINSTEAD | CT |  |  | 7.9766 | 7.8469 | 7.6971 | 7.387 | 7.0483 | 6.6089 | 6.1283 | 5.4896 | 4.5048 | 3.4742 | 1.4418 | -4.0291 | -8.2762 | -8.9634 | 9.2761 | 9.162 | 9.0266 | 8.8231 | 8.5947 | 8.2726 | 7.9095 | 7.4048 | 6.7164 | 5.9861 | 4.5456 | 0.070062 | -3.0915 | -3.6788 | 7.8626 | 7.7615 | 7.6457 | 7.3828 | 7.0877 | 6.6744 | 6.1889 | 5.5281 | 4.5665 | 3.5687 | 1.6073 | -3.9196 | -8.0339 | -8.7823
|  | BINSTEAD | LW |  |  | 7.8242 | 7.6032 | 7.3816 | 7.0013 | 6.5616 | 6.0998 | 5.4691 | 4.7326 | 3.8152 | 2.8107 | 0.63403 | -3.5205 | -5.677 | -6.503 | 9.2454 | 9.1062 | 8.9677 | 8.7632 | 8.5075 | 8.2351 | 7.8098 | 7.2917 | 6.648 | 5.9315 | 4.3907 | 1.3678 | -0.36666 | -2.0043 | 7.7199 | 7.536 | 7.3504 | 7.0171 | 6.6357 | 6.2163 | 5.6473 | 4.9497 | 4.0397 | 3.0391 | 0.90117 | -3.0699 | -5.2175 | -6.3513
|  | BINSTEAD | ST |  |  | 8.0897 | 8.0541 | 8.0045 | 7.8867 | 7.7611 | 7.608 | 7.3983 | 7.1616 | 6.8276 | 6.3887 | 5.2139 | 0.91596 | -2.5683 | -4.7431 | 9.3505 | 9.3061 | 9.2472 | 9.1207 | 8.9867 | 8.8255 | 8.609 | 8.3698 | 8.0288 | 7.6315 | 6.5789 | 2.9712 | -0.14079 | -2.4047 | 7.9601 | 7.9365 | 7.9028 | 7.7975 | 7.6942 | 7.5724 | 7.3542 | 7.0842 | 6.706 | 6.2577 | 5.0615 | 0.79204 | -2.7007 | -4.8669
|  | BINSTEAD | FS |  |  | 7.9766 | 7.8469 | 7.6971 | 7.387 | 7.0483 | 6.6089 | 6.1283 | 5.4896 | 4.5048 | 3.4742 | 1.4418 | -4.0291 | -8.2762 | -8.9634 | 9.3224 | 9.2457 | 9.1514 | 9.0191 | 8.8454 | 8.6253 | 8.1234 | 7.0761 | 5.7361 | 4.0595 | -0.25161 | -7.5846 | -10.0111 | -12.1103 | 7.9236 | 7.8612 | 7.7779 | 7.6356 | 7.4482 | 7.1976 | 6.8528 | 5.6477 | 3.998 | 1.9354 | -3.3585 | -12.472 | -15.6427 | -18.4004
LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM | MINIMUM HEADROOM | SZ 81965 99422 | YES | -1.1212 | -1.3394 | 8.7691 | 8.3765 | 7.9666 | 7.5344 | 7.0559 | 6.4227 | 5.6092 | 4.7358 | 1.8948 | -3.2663 | -5.3222 | -6.8005 | -0.17358 | -0.24836 | 9.2743 | 9.1521 | 9.0222 | 8.8719 | 8.6946 | 8.4441 | 8.1079 | 7.4852 | 5.2869 | 1.7199 | -6.1567 | -10.7798 | -0.5308 | -0.71155 | 8.703 | 8.4039 | 8.095 | 7.773 | 7.4232 | 6.955 | 6.3177 | 5.1391 | 2.2084 | -2.6562 | -11.3777 | -17.3297
|  | BIRDHAM | CT |  |  | -0.91726 | -0.9823 | 9.2897 | 9.0851 | 8.8165 | 8.5321 | 8.2405 | 7.8232 | 7.0889 | 6.3237 | 4.74 | 0.9266 | -1.7426 | -3.2248 | -0.10156 | -0.14287 | 9.4091 | 9.3142 | 9.2141 | 9.1047 | 8.9893 | 8.8126 | 8.5072 | 8.1743 | 7.4754 | 5.7071 | 4.1291 | 2.6567 | -0.31029 | -0.37509 | 9.1498 | 8.9494 | 8.7428 | 8.5267 | 8.3065 | 7.9878 | 7.4204 | 6.8245 | 5.5089 | 2.1516 | -0.28024 | -1.6668
|  | BIRDHAM | LW |  |  | -1.1212 | -1.3394 | 8.7691 | 8.3765 | 7.9666 | 7.5344 | 7.0559 | 6.4227 | 5.6092 | 4.7358 | 1.8948 | -3.2663 | -5.3222 | -6.8005 | -0.17358 | -0.24836 | 9.2743 | 9.1521 | 9.0222 | 8.8719 | 8.6946 | 8.4441 | 8.1079 | 7.4852 | 5.2869 | 1.7199 | 0.27266 | -1.0084 | -0.5308 | -0.71155 | 8.703 | 8.4039 | 8.095 | 7.773 | 7.4232 | 6.955 | 6.3177 | 5.1391 | 2.2084 | -2.6562 | -4.6494 | -6.174
|  | BIRDHAM | ST |  |  | -0.81157 | -0.82308 | 9.5128 | 9.487 | 9.4542 | 9.4181 | 9.3793 | 9.2639 | 9.1079 | 8.9377 | 8.5462 | 6.9942 | 5.0119 | 2.5638 | -0.065794 | -0.089286 | 9.4835 | 9.4505 | 9.4122 | 9.3691 | 9.3208 | 9.2342 | 9.1118 | 8.9819 | 8.6798 | 7.7073 | 6.3095 | 4.4488 | -0.22365 | -0.24707 | 9.3276 | 9.2877 | 9.2421 | 9.1938 | 9.1426 | 9.035 | 8.8892 | 8.7326 | 8.3759 | 7.142 | 5.514 | 3.491
|  | BIRDHAM | FS |  |  | -0.91726 | -0.9823 | 9.2897 | 9.0851 | 8.8165 | 8.5321 | 8.2405 | 7.8232 | 7.0889 | 6.3237 | 4.74 | 0.9266 | -1.7426 | -3.2248 | -0.084002 | -0.11839 | 9.4393 | 9.3804 | 9.3126 | 9.2327 | 9.1378 | 8.9981 | 8.8119 | 8.6032 | 8.0086 | 1.7362 | -6.1567 | -10.7798 | -0.24261 | -0.27324 | 9.2884 | 9.2027 | 9.1087 | 9.001 | 8.878 | 8.696 | 8.4392 | 8.1598 | 6.4666 | -1.4525 | -11.3777 | -17.3297
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM | MINIMUM HEADROOM | SU 56691 16683 | YES | 5.2409 | 4.6665 | 4.0947 | 3.4228 | 2.7285 | 2.0203 | 1.2669 | 0.45947 | -0.53639 | -1.6216 | -3.9739 | -9.4587 | -15.2626 | -17.663 | 9.428 | 9.1487 | 8.8911 | 8.5906 | 8.2714 | 7.9401 | 7.5411 | 6.0277 | 3.7993 | 1.0207 | -6.0335 | -23.7634 | -31.3971 | -33.6237 | 4.9231 | 4.4238 | 3.9342 | 3.3564 | 2.7513 | 2.1318 | 1.4466 | 0.66806 | -2.1137 | -5.5691 | -14.3047 | -36.4539 | -46.1981 | -49.3337
|  | BISHOPS WALTHAM | CT |  |  | 5.6649 | 5.2607 | 4.9391 | 4.4179 | 3.8839 | 3.2719 | 2.6703 | 1.9695 | 0.84255 | -0.32202 | -2.6263 | -8.3055 | -12.1752 | -14.0488 | 9.5298 | 9.2511 | 9.0446 | 8.7645 | 8.4639 | 8.0901 | 7.6937 | 7.2018 | 6.528 | 5.8074 | 4.3681 | 0.82821 | -1.6578 | -3.8005 | 5.2746 | 4.913 | 4.6298 | 4.1731 | 3.6986 | 3.1425 | 2.5812 | 1.9148 | 0.87221 | -0.21306 | -2.3574 | -7.569 | -10.962 | -12.605
|  | BISHOPS WALTHAM | LW |  |  | 5.2409 | 4.6665 | 4.0947 | 3.4228 | 2.7285 | 2.0203 | 1.2669 | 0.45947 | -0.53639 | -1.6216 | -3.9739 | -9.4587 | -15.2626 | -17.663 | 9.428 | 9.1487 | 8.8911 | 8.5906 | 8.2714 | 7.9401 | 7.5411 | 7.0874 | 6.5349 | 5.915 | 4.5302 | -1.8172 | -6.8124 | -8.778 | 4.9231 | 4.4238 | 3.9342 | 3.3564 | 2.7513 | 2.1318 | 1.4466 | 0.70153 | -0.21525 | -1.2178 | -3.4007 | -10.8832 | -17.29 | -19.6833
|  | BISHOPS WALTHAM | ST |  |  | 5.8206 | 5.5271 | 5.3169 | 5.0043 | 4.7037 | 4.3922 | 4.0787 | 3.7506 | 3.3798 | 2.9701 | 2.0022 | -1.3735 | -4.5392 | -7.4552 | 9.6097 | 9.396 | 9.2595 | 9.0492 | 8.8446 | 8.622 | 8.3731 | 8.1156 | 7.8135 | 7.4797 | 6.661 | 3.929 | 1.2884 | -1.3977 | 5.415 | 5.1568 | 4.9795 | 4.6959 | 4.4232 | 4.1382 | 3.8371 | 3.5258 | 3.1628 | 2.7697 | 1.8299 | -1.4434 | -4.4093 | -7.0148
|  | BISHOPS WALTHAM | FS |  |  | 5.6649 | 5.2607 | 4.9391 | 4.4179 | 3.8839 | 3.2719 | 2.6703 | 1.9695 | 0.84255 | -0.32202 | -2.6263 | -8.3055 | -12.1752 | -14.0488 | 9.5656 | 9.3568 | 9.1299 | 8.848 | 8.531 | 8.1204 | 7.6412 | 6.0277 | 3.7993 | 1.0207 | -6.0335 | -23.7634 | -31.3971 | -33.6237 | 5.4055 | 5.1706 | 4.9186 | 4.543 | 4.1286 | 3.6055 | 2.8047 | 0.66806 | -2.1137 | -5.5691 | -14.3047 | -36.4539 | -46.1981 | -49.3337
NURSLING GSP | VELMORE BSP | BISHOPSTOKE | MINIMUM HEADROOM | SU 46463 18472 | YES | 4.5908 | 4.5431 | 4.4949 | 4.4349 | 4.3475 | 4.2376 | 4.0642 | 3.8385 | 3.5372 | 3.1339 | 2.104 | 0.47391 | -0.18191 | -0.88396 | 3.9911 | 3.8798 | 3.7165 | 3.4737 | 3.1133 | 2.5889 | 1.8349 | 0.67545 | -0.79777 | -2.6512 | -7.4353 | -15.3697 | -17.5547 | -19.2668 | 2.6868 | 2.5367 | 2.3144 | 1.9826 | 1.4887 | 0.76601 | -0.26916 | -1.6897 | -3.4876 | -5.75 | -11.5914 | -21.2868 | -23.9568 | -26.02
|  | BISHOPSTOKE | CT |  |  | 4.5924 | 4.5559 | 4.5142 | 4.4655 | 4.4074 | 4.3187 | 4.2128 | 4.061 | 3.8616 | 3.6288 | 3.082 | 1.3949 | 0.55949 | 0.36226 | 4.0604 | 4.0269 | 3.9884 | 3.9435 | 3.8896 | 3.8078 | 3.71 | 3.5698 | 3.3817 | 3.1581 | 2.6547 | 1.3635 | 0.68058 | 0.41159 | 2.7831 | 2.7397 | 2.6912 | 2.6329 | 2.5603 | 2.4557 | 2.3294 | 2.1469 | 1.9052 | 1.6232 | 0.97884 | -0.71856 | -1.5801 | -1.8412
|  | BISHOPSTOKE | LW |  |  | 4.5908 | 4.5431 | 4.4949 | 4.4349 | 4.3475 | 4.2376 | 4.0642 | 3.8385 | 3.5372 | 3.1339 | 2.104 | 0.47391 | -0.18191 | -0.88396 | 4.0585 | 4.014 | 3.969 | 3.9126 | 3.8305 | 3.727 | 3.5639 | 3.3516 | 3.0596 | 2.7167 | 1.953 | 0.71262 | 0.04001 | -0.73764 | 2.778 | 2.7182 | 2.6591 | 2.5834 | 2.4722 | 2.3319 | 2.1126 | 1.8279 | 1.4476 | 0.99742 | -0.0067896 | -1.6112 | -2.3407 | -3.1563
|  | BISHOPSTOKE | ST |  |  | 4.6271 | 4.6177 | 4.6047 | 4.5851 | 4.5592 | 4.5258 | 4.483 | 4.4296 | 4.3406 | 4.2395 | 3.9766 | 3.2333 | 2.6841 | 2.2636 | 4.081 | 4.0764 | 4.0702 | 4.0543 | 4.0307 | 4.0001 | 3.9611 | 3.9124 | 3.8232 | 3.7242 | 3.4695 | 2.7499 | 2.1322 | 1.6136 | 2.8248 | 2.8141 | 2.7998 | 2.7774 | 2.7478 | 2.7094 | 2.66 | 2.5989 | 2.4945 | 2.3767 | 2.0722 | 1.2086 | 0.54451 | 0.012991
|  | BISHOPSTOKE | FS |  |  | 4.5924 | 4.5559 | 4.5142 | 4.4655 | 4.4074 | 4.3187 | 4.2128 | 4.061 | 3.8616 | 3.6288 | 3.082 | 1.3949 | 0.55949 | 0.36226 | 3.9911 | 3.8798 | 3.7165 | 3.4737 | 3.1133 | 2.5889 | 1.8349 | 0.67545 | -0.79777 | -2.6512 | -7.4353 | -15.3697 | -17.5547 | -19.2668 | 2.6868 | 2.5367 | 2.3144 | 1.9826 | 1.4887 | 0.76601 | -0.26916 | -1.6897 | -3.4876 | -5.75 | -11.5914 | -21.2868 | -23.9568 | -26.02
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE | MINIMUM HEADROOM | SU 45116 13082 | YES | 0.081244 | -0.082193 | -0.24916 | -0.62582 | -1.02 | -1.5956 | -3.245 | -7.017 | -11.9112 | -17.9564 | -32.7392 | -58.394 | -65.4695 | -70.6012 | 1.6406 | 1.5315 | 1.388 | 1.1256 | 0.8053 | 0.035445 | -2.073 | -4.9795 | -8.7255 | -13.3842 | -24.8164 | -44.502 | -49.8685 | -53.898 | 0.05027 | -0.095859 | -0.24519 | -0.58025 | -0.93543 | -1.5189 | -3.7165 | -7.3278 | -12.0106 | -17.8031 | -31.9726 | -56.5364 | -63.3228 | -68.2816
|  | BITTERNE | CT |  |  | 0.21477 | 0.087019 | -0.07381 | -0.4906 | -0.97005 | -1.5956 | -3.245 | -7.017 | -11.9112 | -17.9564 | -32.7392 | -58.394 | -65.4695 | -70.6012 | 1.6429 | 1.5315 | 1.388 | 1.1256 | 0.8053 | 0.035445 | -2.073 | -4.9795 | -8.7255 | -13.3842 | -24.8164 | -44.502 | -49.8685 | -53.898 | 0.1616 | 0.041989 | -0.1101 | -0.49217 | -0.93543 | -1.5189 | -3.7165 | -7.3278 | -12.0106 | -17.8031 | -31.9726 | -56.5364 | -63.3228 | -68.2816
|  | BITTERNE | LW |  |  | 0.081244 | -0.082193 | -0.24916 | -0.62582 | -1.02 | -1.4236 | -1.8901 | -2.4066 | -3.0246 | -3.6799 | -5.1228 | -8.362 | -10.2378 | -11.0116 | 1.6406 | 1.5592 | 1.4759 | 1.3132 | 1.1345 | 0.94792 | 0.71112 | 0.43724 | 0.089553 | -0.28913 | -1.1357 | -3.0352 | -4.3305 | -5.0636 | 0.05027 | -0.095859 | -0.24519 | -0.58025 | -0.93301 | -1.2954 | -1.7198 | -2.1924 | -2.7673 | -3.3792 | -4.7228 | -7.7192 | -9.5301 | -10.3564
|  | BITTERNE | ST |  |  | 0.36723 | 0.3609 | 0.35396 | 0.34512 | 0.32099 | 0.29868 | 0.2607 | 0.20548 | 0.11197 | 0.0081574 | -0.29019 | -1.8682 | -3.688 | -5.4323 | 1.7362 | 1.7058 | 1.6698 | 1.6277 | 1.5729 | 1.5105 | 1.4326 | 1.3375 | 1.1634 | 0.9701 | 0.47691 | -1.5197 | -4.4888 | -8.7022 | 0.30363 | 0.29856 | 0.29254 | 0.28318 | 0.25977 | 0.2367 | 0.19867 | 0.14425 | 0.046096 | -0.062005 | -0.36634 | -1.8693 | -3.6265 | -5.29
|  | BITTERNE | FS |  |  | 0.21477 | 0.087019 | -0.07381 | -0.4906 | -0.97005 | -1.5956 | -3.245 | -7.017 | -11.9112 | -17.9564 | -32.7392 | -58.394 | -65.4695 | -70.6012 | 1.6699 | 1.5961 | 1.504 | 1.3775 | 1.2153 | 1.0127 | 0.7535 | 0.42198 | -0.08337 | -0.87295 | -4.89 | -21.213 | -34.6913 | -39.3469 | 0.21925 | 0.16509 | 0.096862 | -0.025251 | -0.18673 | -0.38966 | -0.65235 | -0.99799 | -1.4577 | -2.2451 | -6.9827 | -27.0532 | -43.7251 | -49.5647
MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON | MINIMUM HEADROOM | SP 28349 03818 | YES | 4.8979 | 4.7509 | 4.6296 | 4.4305 | 4.1786 | 3.8244 | 3.3721 | 2.7145 | 1.9844 | 1.1023 | -1.343 | -12.4241 | -25.7693 | -33.0744 | 5.4782 | 5.189 | 4.9113 | 4.5855 | 4.1859 | 3.669 | 2.9475 | 1.936 | 0.75835 | -0.50965 | -3.0915 | -8.2815 | -18.3703 | -24.1425 | 4.1964 | 4.0711 | 3.9674 | 3.6259 | 3.1422 | 2.5106 | 1.622 | 0.36762 | -1.0826 | -2.5938 | -5.6408 | -12.6236 | -25.4571 | -32.5162
|  | BLACK BOURTON | CT |  |  | 4.8979 | 4.7589 | 4.6296 | 4.4305 | 4.1786 | 3.8244 | 3.3721 | 2.7145 | 1.9844 | 1.1023 | -1.343 | -12.4241 | -25.7693 | -33.0744 | 5.6576 | 5.5651 | 5.5014 | 5.4031 | 5.2829 | 5.1299 | 4.8231 | 4.2075 | 3.5297 | 2.7062 | 0.57639 | -7.9769 | -18.3703 | -24.1425 | 4.2047 | 4.1155 | 4.0508 | 3.9648 | 3.8518 | 3.6897 | 3.3555 | 2.616 | 1.7479 | 0.70774 | -1.9698 | -12.6236 | -25.4571 | -32.5162
|  | BLACK BOURTON | LW |  |  | 4.956 | 4.7509 | 4.6379 | 4.4952 | 4.3446 | 4.1906 | 4.0198 | 3.7777 | 3.5062 | 3.1233 | 2.2003 | -0.27844 | -1.7439 | -2.4037 | 5.6414 | 5.5373 | 5.4844 | 5.4206 | 5.3523 | 5.2817 | 5.197 | 5.0487 | 4.864 | 4.4994 | 3.6298 | 1.7502 | 0.57977 | -0.10654 | 4.2267 | 4.1325 | 4.0927 | 4.0521 | 4.001 | 3.9464 | 3.8576 | 3.6015 | 3.2639 | 2.7808 | 1.6344 | -0.85215 | -2.3198 | -3.0741
|  | BLACK BOURTON | ST |  |  | 5.0093 | 4.9547 | 4.9325 | 4.8597 | 4.7892 | 4.7034 | 4.5834 | 4.3892 | 4.2073 | 4.0072 | 3.5096 | 2.0847 | 1.2752 | 0.71768 | 5.6878 | 5.6192 | 5.5849 | 5.4936 | 5.4138 | 5.3259 | 5.2085 | 5.0609 | 4.9245 | 4.7901 | 4.4867 | 3.408 | 1.9357 | -0.063982 | 4.2594 | 4.2137 | 4.201 | 4.1322 | 4.0737 | 4.0061 | 3.9076 | 3.7552 | 3.6326 | 3.5093 | 3.22 | 1.8291 | 0.70195 | -0.20218
|  | BLACK BOURTON | FS |  |  | 4.8979 | 4.7589 | 4.6296 | 4.4305 | 4.1786 | 3.8244 | 3.3721 | 2.7145 | 1.9844 | 1.1023 | -1.343 | -12.4241 | -25.7693 | -33.0744 | 5.4782 | 5.189 | 4.9113 | 4.5855 | 4.1859 | 3.669 | 2.9475 | 1.936 | 0.75835 | -0.50965 | -3.0915 | -8.2815 | -10.82 | -13.2673 | 4.1964 | 4.0711 | 3.9674 | 3.6259 | 3.1422 | 2.5106 | 1.622 | 0.36762 | -1.0826 | -2.5938 | -5.6408 | -11.5128 | -13.3865 | -13.4611
MANNINGTON GSP | LYTCHETT | BLANDFORD | MINIMUM HEADROOM | ST 88810 05536 | YES | 15.0955 | 14.047 | 13.0705 | 11.7198 | 10.0207 | 8.455 | 6.025 | 2.7437 | -0.83519 | -4.8025 | -13.1121 | -27.1389 | -35.2264 | -38.1005 | 18.7115 | 18.2632 | 17.9083 | 17.1248 | 15.9617 | 14.8647 | 13.0334 | 10.5383 | 7.9706 | 5.0911 | -1.0617 | -12.9139 | -26.1032 | -38.6132 | 16.5532 | 15.5807 | 14.6783 | 13.4507 | 11.8885 | 10.4218 | 8.1158 | 4.961 | 1.516 | -2.3142 | -10.3976 | -24.166 | -35.5939 | -46.3298
|  | BLANDFORD | CT |  |  | 15.354 | 14.6205 | 13.8531 | 12.6544 | 11.2209 | 9.5723 | 7.6084 | 4.4233 | 0.6454 | -3.114 | -10.0219 | -27.1389 | -35.2264 | -38.1005 | 18.7681 | 18.3798 | 18.1538 | 17.3322 | 16.261 | 14.9271 | 13.375 | 10.9153 | 8.1389 | 5.3443 | 0.14463 | -12.9139 | -19.6926 | -23.9341 | 16.8142 | 16.0794 | 15.3554 | 14.2489 | 12.9218 | 11.3422 | 9.4358 | 6.3346 | 2.6899 | -0.93273 | -7.5754 | -24.166 | -31.9149 | -34.6846
|  | BLANDFORD | LW |  |  | 15.0955 | 14.047 | 13.0705 | 11.7198 | 10.0207 | 8.455 | 6.025 | 2.7437 | -0.83519 | -4.8025 | -13.1121 | -26.967 | -31.1721 | -29.8647 | 18.7115 | 18.2632 | 17.9083 | 17.1248 | 15.9617 | 14.8647 | 13.0334 | 10.5383 | 7.9706 | 5.0911 | -1.0617 | -11.0329 | -13.9736 | -13.8402 | 16.5532 | 15.5807 | 14.6783 | 13.4507 | 11.8885 | 10.4218 | 8.1158 | 4.961 | 1.516 | -2.3142 | -10.3976 | -23.7945 | -27.8842 | -26.6819
|  | BLANDFORD | ST |  |  | 15.5102 | 15.2353 | 15.0784 | 14.4301 | 13.5973 | 12.8575 | 11.8327 | 10.3894 | 8.9332 | 7.0478 | 2.2566 | -13.1412 | -23.9468 | -28.5222 | 18.8905 | 18.6116 | 18.5138 | 18.1959 | 17.7411 | 17.2453 | 16.3129 | 15.0166 | 13.7021 | 12.1457 | 8.1784 | -4.9566 | -14.6909 | -19.9458 | 17.2284 | 16.8594 | 16.5479 | 15.9363 | 15.1596 | 14.442 | 13.4503 | 12.0616 | 10.4638 | 8.5527 | 3.6633 | -11.9857 | -22.8742 | -27.2872
|  | BLANDFORD | FS |  |  | 15.354 | 14.6205 | 13.8531 | 12.6544 | 11.2209 | 9.5723 | 7.6084 | 4.4233 | 0.6454 | -3.114 | -10.0219 | -27.1389 | -35.2264 | -38.1005 | 18.9541 | 18.6976 | 18.4872 | 18.2025 | 17.7518 | 16.9601 | 15.9555 | 14.6621 | 13.22 | 11.5209 | 7.1083 | -8.7958 | -26.1032 | -38.6132 | 17.2084 | 16.8209 | 16.4029 | 15.7761 | 14.9915 | 14.1411 | 13.0601 | 11.5713 | 9.835 | 7.79 | 2.4503 | -16.38 | -35.5939 | -46.3298
COWLEY GSP | WITNEY BSP | BLEDDINGTON | MINIMUM HEADROOM | SP 25641 22580 | NO | -0.10339 | -0.34194 | -0.58567 | -0.81552 | -1.1106 | -1.4269 | -1.9166 | -2.5102 | -3.2011 | -3.9856 | -6.2409 | -16.29 | -24.0317 | -26.2896 | 1.2838 | 1.1463 | 1.0053 | 0.85891 | 0.66429 | 0.45108 | 0.013085 | -0.89576 | -2.0673 | -3.5314 | -7.1739 | -15.4581 | -18.6416 | -19.7165 | 0.12865 | -0.094621 | -0.32249 | -0.54391 | -0.82615 | -1.1283 | -1.6281 | -2.7569 | -4.2141 | -6.0272 | -10.5287 | -20.8247 | -24.8134 | -26.1997
|  | BLEDDINGTON | CT |  |  | 0.010218 | -0.1551 | -0.33701 | -0.55493 | -0.78379 | -1.0993 | -1.4442 | -1.9329 | -2.5295 | -3.1166 | -4.2513 | -6.8751 | -8.1659 | -8.5219 | 1.3152 | 1.2072 | 1.0835 | 0.94112 | 0.78704 | 0.56214 | 0.31413 | -0.05265 | -0.49342 | -0.9263 | -1.7594 | -3.709 | -4.6048 | -4.9991 | 0.2194 | 0.063709 | -0.1089 | -0.31476 | -0.53188 | -0.83526 | -1.1675 | -1.6428 | -2.2219 | -2.7913 | -3.8897 | -6.422 | -7.6282 | -7.9479
|  | BLEDDINGTON | LW |  |  | -0.10339 | -0.34194 | -0.58567 | -0.81552 | -1.1106 | -1.4269 | -1.9166 | -2.5102 | -3.2011 | -3.9856 | -6.2409 | -16.29 | -24.0317 | -26.2896 | 1.2838 | 1.1463 | 1.0053 | 0.85891 | 0.66429 | 0.45108 | 0.1015 | -0.33507 | -0.84032 | -1.4223 | -3.3034 | -11.0637 | -17.0625 | -18.8033 | 0.12865 | -0.094621 | -0.32249 | -0.54391 | -0.82615 | -1.1283 | -1.6018 | -2.1793 | -2.8505 | -3.6146 | -5.9764 | -15.6052 | -23.0212 | -25.1774
|  | BLEDDINGTON | ST |  |  | 0.1058 | 0.020281 | -0.079565 | -0.21538 | -0.37241 | -0.55954 | -0.7775 | -1.0456 | -1.3492 | -1.7056 | -2.6369 | -5.4106 | -7.1759 | -7.7506 | 1.3769 | 1.3244 | 1.2601 | 1.1764 | 1.0744 | 0.94788 | 0.79323 | 0.60008 | 0.38198 | 0.11784 | -0.59679 | -2.7786 | -4.1656 | -4.676 | 0.31136 | 0.23251 | 0.13898 | 0.012857 | -0.13431 | -0.31122 | -0.51943 | -0.77685 | -1.0695 | -1.4154 | -2.3233 | -5.0299 | -6.73 | -7.2531
|  | BLEDDINGTON | FS |  |  | 0.010218 | -0.1551 | -0.33701 | -0.55493 | -0.78379 | -1.0993 | -1.4442 | -1.9329 | -2.5295 | -3.1166 | -4.2513 | -6.8751 | -8.1659 | -8.5219 | 1.3697 | 1.3053 | 1.225 | 1.1187 | 0.98235 | 0.67661 | 0.013085 | -0.89576 | -2.0673 | -3.5314 | -7.1739 | -15.4581 | -18.6416 | -19.7165 | 0.31915 | 0.23396 | 0.13027 | -0.019328 | -0.20464 | -0.79738 | -1.6281 | -2.7569 | -4.2141 | -6.0272 | -10.5287 | -20.8247 | -24.8134 | -26.1997
BRAMLEY (FLEE) | ALTON | BORDON | MINIMUM HEADROOM | SU 82256 35269 | YES | 0.15368 | -0.833 | -1.7674 | -2.9407 | -4.2126 | -5.5272 | -7.0089 | -8.5671 | -10.3618 | -12.1273 | -15.5395 | -21.844 | -26.9205 | -29.9701 | 4.001 | 3.4382 | 2.8892 | 2.3138 | 1.7198 | 1.1174 | 0.41731 | -0.33255 | -1.1792 | -2.0376 | -5.716 | -16.4906 | -24.7 | -30.0666 | -0.50068 | -1.3561 | -2.1833 | -3.202 | -4.2777 | -5.3901 | -6.6557 | -8.003 | -9.5656 | -11.1142 | -14.1362 | -22.1401 | -32.739 | -39.9518
|  | BORDON | CT |  |  | 0.68413 | 0.080217 | -0.53515 | -1.2895 | -2.1069 | -3.074 | -4.2254 | -5.4941 | -7.4659 | -9.4376 | -13.0703 | -21.3406 | -26.9205 | -29.9701 | 4.1968 | 3.7973 | 3.362 | 2.9278 | 2.496 | 1.9656 | 1.3441 | 0.64198 | -0.35729 | -1.3846 | -3.2691 | -7.6415 | -11.1754 | -14.8194 | -0.0020941 | -0.50601 | -1.0391 | -1.738 | -2.4628 | -3.3168 | -4.2951 | -5.3835 | -7.075 | -8.7917 | -12.0105 | -19.3669 | -24.2921 | -26.9896
|  | BORDON | LW |  |  | 0.15368 | -0.833 | -1.7674 | -2.9407 | -4.2126 | -5.5272 | -7.0089 | -8.5671 | -10.3618 | -12.1273 | -15.5395 | -21.844 | -25.4164 | -27.1199 | 4.001 | 3.4382 | 2.8892 | 2.3138 | 1.7198 | 1.1174 | 0.41731 | -0.33255 | -1.1792 | -2.0376 | -3.7428 | -6.6685 | -8.2956 | -9.2355 | -0.50068 | -1.3561 | -2.1833 | -3.202 | -4.2777 | -5.3901 | -6.6557 | -8.003 | -9.5656 | -11.1142 | -14.1362 | -19.7176 | -22.8908 | -24.4484
|  | BORDON | ST |  |  | 0.81838 | 0.30114 | -0.21939 | -0.63299 | -1.0409 | -1.5059 | -2.059 | -2.6143 | -3.2558 | -3.914 | -5.1705 | -9.0413 | -13.0455 | -17.6104 | 4.2648 | 3.9154 | 3.535 | 3.2035 | 2.9193 | 2.5902 | 2.1802 | 1.7763 | 1.2731 | 0.74766 | -0.31007 | -3.4514 | -6.9078 | -11.1376 | 0.12691 | -0.29418 | -0.73668 | -1.1265 | -1.4691 | -1.8601 | -2.3361 | -2.8054 | -3.3671 | -3.9461 | -5.0664 | -8.6382 | -12.366 | -16.4542
|  | BORDON | FS |  |  | 0.68413 | 0.080217 | -0.53515 | -1.2895 | -2.1069 | -3.074 | -4.2254 | -5.4941 | -7.4659 | -9.4376 | -13.0703 | -21.3406 | -26.9205 | -29.9701 | 4.3914 | 4.0114 | 3.6332 | 3.2787 | 2.9108 | 2.4945 | 2.0084 | 1.4453 | 0.71403 | -1.0986 | -5.716 | -16.4906 | -24.7 | -30.0666 | 0.28962 | -0.1363 | -0.54485 | -0.97922 | -1.4289 | -1.9332 | -2.518 | -3.1859 | -4.0438 | -4.9702 | -8.5208 | -22.1401 | -32.739 | -39.9518
MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN | MINIMUM HEADROOM | SU 17186 41044 | YES | 11.5113 | 11.3125 | 11.1733 | 11.0047 | 10.6297 | 9.9317 | 8.7483 | 7.2867 | 5.591 | 3.6877 | -0.47751 | -7.6052 | -10.7378 | -12.4743 | 10.5044 | 10.3847 | 10.2666 | 10.1278 | 9.9607 | 9.7016 | 9.3953 | 8.7513 | 7.3807 | 6.0193 | 2.9569 | -2.5841 | -5.6573 | -10.4874 | 8.6251 | 8.4762 | 8.3397 | 8.1792 | 7.9843 | 7.6789 | 7.3183 | 6.7972 | 6.151 | 5.4486 | 4.0109 | -2.4914 | -7.5131 | -8.8249
|  | BOSCOMBE DOWN | CT |  |  | 11.5224 | 11.3526 | 11.2038 | 11.0128 | 10.787 | 10.0444 | 9.085 | 7.6588 | 5.8458 | 4.0715 | 0.74913 | -7.063 | -10.7378 | -12.4743 | 10.5044 | 10.3847 | 10.2666 | 10.1278 | 9.9607 | 9.7016 | 9.3953 | 8.7513 | 7.3807 | 6.0193 | 3.4669 | -2.5841 | -5.6573 | -7.729 | 8.6251 | 8.4762 | 8.3397 | 8.1792 | 7.9843 | 7.6789 | 7.3183 | 6.7972 | 6.151 | 5.4486 | 4.0109 | -1.857 | -5.3339 | -7.0426
|  | BOSCOMBE DOWN | LW |  |  | 11.5113 | 11.3125 | 11.1733 | 11.0047 | 10.6297 | 9.9317 | 8.7483 | 7.2867 | 5.591 | 3.6877 | -0.47751 | -7.6052 | -9.7687 | -8.8024 | 10.5271 | 10.4061 | 10.3156 | 10.2153 | 10.0716 | 9.9177 | 9.6365 | 8.7942 | 7.518 | 6.0856 | 2.9569 | -2.364 | -4.1036 | -3.6022 | 8.6461 | 8.4879 | 8.3778 | 8.2567 | 8.0822 | 7.8948 | 7.5534 | 7.1238 | 6.5968 | 6.0032 | 4.3119 | -2.4914 | -4.6739 | -3.7511
|  | BOSCOMBE DOWN | ST |  |  | 11.6219 | 11.5371 | 11.4847 | 11.3878 | 11.2672 | 11.1174 | 10.9206 | 10.5061 | 9.7083 | 8.7313 | 6.0919 | -2.3409 | -8.142 | -10.4831 | 10.5769 | 10.523 | 10.4794 | 10.3916 | 10.2912 | 10.1671 | 10.0026 | 9.8191 | 9.554 | 9.2496 | 7.2191 | 0.4176 | -4.614 | -7.1451 | 8.7122 | 8.6424 | 8.5954 | 8.5012 | 8.3894 | 8.2482 | 8.0607 | 7.8492 | 7.5507 | 7.205 | 6.2913 | 2.3404 | -3.6069 | -5.9557
|  | BOSCOMBE DOWN | FS |  |  | 11.5224 | 11.3526 | 11.2038 | 11.0128 | 10.787 | 10.0444 | 9.085 | 7.6588 | 5.8458 | 4.0715 | 0.74913 | -7.063 | -10.7378 | -12.4743 | 10.5622 | 10.4944 | 10.4302 | 10.3396 | 10.2207 | 10.0626 | 9.8559 | 9.588 | 9.2404 | 8.8104 | 7.6145 | 0.12113 | -5.4669 | -10.4874 | 8.6977 | 8.6128 | 8.5421 | 8.4386 | 8.302 | 8.119 | 7.8786 | 7.5653 | 7.1647 | 6.6672 | 5.2751 | -1.9132 | -7.5131 | -8.8249
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST | MINIMUM HEADROOM | SZ 11636 92447 | YES | 12.7136 | 12.3242 | 11.9366 | 11.2674 | 10.4807 | 9.6615 | 8.5215 | 7.1976 | 5.7013 | 4.0847 | 0.71439 | -6.6221 | -10.603 | -12.3887 | 15.9023 | 15.5815 | 15.2001 | 14.6539 | 14.0447 | 13.2363 | 12.3446 | 11.1628 | 9.6551 | 8.0364 | 4.776 | -4.4367 | -21.0099 | -52.0752 | 13.1016 | 12.9989 | 12.8769 | 12.7289 | 12.5537 | 12.288 | 11.5643 | 10.2205 | 8.7031 | 7.0498 | 3.5739 | -3.6602 | -7.392 | -9.0704
|  | BOSCOMBE EAST | CT |  |  | 12.9325 | 12.6835 | 12.3861 | 11.7904 | 11.1414 | 10.2734 | 9.3402 | 8.0828 | 6.3861 | 4.6958 | 1.4641 | -6.6221 | -10.603 | -12.3887 | 15.9023 | 15.5815 | 15.2001 | 14.6539 | 14.0447 | 13.2363 | 12.3446 | 11.1628 | 9.6551 | 8.0364 | 4.776 | -4.4367 | -14.0187 | -28.1589 | 13.1016 | 12.9989 | 12.8769 | 12.7289 | 12.5537 | 12.288 | 11.9842 | 10.8494 | 9.1235 | 7.4059 | 4.1397 | -3.6602 | -7.392 | -9.0704
|  | BOSCOMBE EAST | LW |  |  | 12.7136 | 12.3242 | 11.9366 | 11.2674 | 10.4807 | 9.6615 | 8.5215 | 7.1976 | 5.7013 | 4.0847 | 0.71439 | -5.2698 | -7.4186 | -7.0971 | 15.9744 | 15.7345 | 15.4981 | 15.139 | 14.6923 | 14.2221 | 13.4946 | 12.6251 | 11.633 | 10.4489 | 7.9396 | 3.8249 | 2.4788 | 2.8026 | 13.12 | 13.0098 | 12.9077 | 12.7772 | 12.5949 | 12.397 | 11.5643 | 10.2205 | 8.7031 | 7.0498 | 3.5739 | -2.3338 | -4.3889 | -3.9998
|  | BOSCOMBE EAST | ST |  |  | 13.1862 | 13.1353 | 13.0483 | 12.903 | 12.7059 | 12.4448 | 12.1078 | 11.695 | 11.1968 | 10.5823 | 8.9278 | 2.5507 | -2.5392 | -5.5523 | 16.0586 | 15.8739 | 15.642 | 15.3259 | 14.9482 | 14.4916 | 13.943 | 13.3035 | 12.5289 | 11.6193 | 9.2892 | 0.35979 | -10.5953 | -25.3132 | 13.1862 | 13.1551 | 13.1099 | 13.0293 | 12.9273 | 12.7992 | 12.6372 | 12.4462 | 12.1967 | 11.901 | 11.1275 | 4.6406 | -0.40233 | -3.1375
|  | BOSCOMBE EAST | FS |  |  | 12.9325 | 12.6835 | 12.3861 | 11.7904 | 11.1414 | 10.2734 | 9.3402 | 8.0828 | 6.3861 | 4.6958 | 1.4641 | -6.6221 | -10.603 | -12.3887 | 16.0355 | 15.817 | 15.5511 | 15.1527 | 14.6809 | 14.1304 | 13.4754 | 12.7154 | 11.7768 | 10.7005 | 7.9959 | -2.6048 | -21.0099 | -52.0752 | 13.1848 | 13.1552 | 13.112 | 13.0456 | 12.9562 | 12.8408 | 12.6973 | 12.5197 | 12.3035 | 12.0493 | 11.3886 | 6.5545 | 0.27073 | -4.1805
MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY | MINIMUM HEADROOM | SZ 06207 92415 | YES | 4.9824 | 4.5046 | 3.9349 | 2.8081 | 1.5587 | 0.2311 | -1.27 | -2.7408 | -4.3947 | -6.0932 | -9.5458 | -17.8838 | -29.0151 | -33.0562 | 11.7812 | 11.5302 | 11.1999 | 10.5824 | 9.8975 | 9.1148 | 7.0718 | 3.2239 | -1.6564 | -7.7171 | -22.6775 | -49.0281 | -57.1931 | -63.5414 | 4.622 | 4.2069 | 3.7093 | 2.7428 | 1.6244 | 0.43258 | -0.92635 | -3.8716 | -9.8256 | -17.2188 | -35.461 | -67.8691 | -78.3336 | -86.6146
|  | BOURNE VALLEY | CT |  |  | 5.4837 | 5.2434 | 4.8572 | 3.9807 | 3.0104 | 1.9251 | 0.79745 | -0.38273 | -2.1888 | -4.0377 | -7.7966 | -17.8838 | -29.0151 | -33.0562 | 11.878 | 11.6121 | 11.1999 | 10.5824 | 9.8975 | 9.1148 | 8.2916 | 7.4241 | 6.2237 | 4.9634 | 2.2635 | -5.7909 | -14.2548 | -24.9341 | 5.0402 | 4.8218 | 4.4634 | 3.6882 | 2.8497 | 1.8989 | 0.8807 | -0.18459 | -1.8051 | -3.4656 | -6.854 | -17.1617 | -27.671 | -31.4154
|  | BOURNE VALLEY | LW |  |  | 4.9824 | 4.5046 | 3.9349 | 2.8081 | 1.5587 | 0.2311 | -1.27 | -2.7408 | -4.3947 | -6.0932 | -9.5458 | -16.128 | -19.3691 | -20.2192 | 11.7812 | 11.5302 | 11.202 | 10.6356 | 9.9796 | 9.2639 | 8.4123 | 7.6133 | 6.7495 | 5.8549 | 4.0083 | 0.79101 | -0.63251 | -0.88468 | 4.622 | 4.2069 | 3.7093 | 2.7428 | 1.6244 | 0.43258 | -0.92635 | -2.2503 | -3.7322 | -5.2576 | -8.3727 | -14.261 | -17.085 | -17.7355
|  | BOURNE VALLEY | ST |  |  | 5.6649 | 5.5625 | 5.3202 | 5.044 | 4.7085 | 4.3348 | 3.948 | 3.6121 | 3.2423 | 2.8158 | 1.8484 | -1.8632 | -5.594 | -9.6739 | 11.9655 | 11.7779 | 11.4501 | 11.0845 | 10.6643 | 10.201 | 9.7134 | 9.2666 | 8.733 | 8.1309 | 6.7221 | 1.7347 | -5.3712 | -16.4665 | 5.2037 | 5.113 | 4.8888 | 4.6325 | 4.3264 | 3.9865 | 3.6349 | 3.3375 | 3.011 | 2.6301 | 1.7455 | -1.6547 | -4.9906 | -8.4631
|  | BOURNE VALLEY | FS |  |  | 5.4837 | 5.2434 | 4.8572 | 3.9807 | 3.0104 | 1.9251 | 0.79745 | -0.38273 | -2.1888 | -4.0377 | -7.7966 | -17.8838 | -29.0151 | -33.0562 | 11.8551 | 11.5919 | 11.2107 | 10.6928 | 10.0436 | 9.2162 | 7.0718 | 3.2239 | -1.6564 | -7.7171 | -22.6775 | -49.0281 | -57.1931 | -63.5414 | 5.0718 | 4.9068 | 4.6282 | 4.1954 | 3.6388 | 2.8988 | 0.79036 | -3.8716 | -9.8256 | -17.2188 | -35.461 | -67.8691 | -78.3336 | -86.6146
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON | MINIMUM HEADROOM | ST 77363 30262 | YES | 0.41169 | 0.14957 | -0.11781 | -0.48621 | -0.90202 | -1.344 | -1.85 | -2.3948 | -3.0484 | -3.7435 | -6.5926 | -14.3733 | -18.8101 | -21.3117 | 2.7087 | 2.5912 | 2.4619 | 2.2609 | 1.9966 | 1.674 | 1.2032 | 0.48769 | -1.1944 | -3.3727 | -9.814 | -35.8552 | -56.9643 | -63.63 | 0.98043 | 0.74224 | 0.50098 | 0.17508 | -0.1899 | -0.57783 | -1.1017 | -2.7333 | -4.8274 | -7.5268 | -15.4732 | -47.5795 | -73.627 | -82.0378
|  | BOURTON | CT |  |  | 0.65668 | 0.51283 | 0.35148 | 0.044767 | -0.29692 | -0.70866 | -1.1662 | -1.7014 | -2.5355 | -3.4031 | -6.5926 | -14.3733 | -18.8101 | -21.3117 | 2.7879 | 2.7026 | 2.6027 | 2.4409 | 2.2537 | 2.0186 | 1.7504 | 1.4184 | 0.94708 | 0.44307 | -2.1348 | -7.6344 | -10.6588 | -12.434 | 1.2032 | 1.0719 | 0.92528 | 0.64571 | 0.33518 | -0.037749 | -0.44973 | -0.93807 | -1.6946 | -3.1529 | -6.6501 | -13.9915 | -18.1491 | -20.5011
|  | BOURTON | LW |  |  | 0.41169 | 0.14957 | -0.11781 | -0.48621 | -0.90202 | -1.344 | -1.85 | -2.3948 | -3.0484 | -3.7435 | -5.2352 | -8.5909 | -10.5606 | -11.1501 | 2.7087 | 2.5912 | 2.4705 | 2.3096 | 2.1212 | 1.9174 | 1.6671 | 1.3869 | 1.054 | 0.69023 | -0.11837 | -1.9389 | -3.2334 | -3.8374 | 0.98043 | 0.74224 | 0.50098 | 0.17508 | -0.1899 | -0.57783 | -1.0272 | -1.5148 | -2.1006 | -2.7266 | -4.0774 | -7.1131 | -8.9008 | -9.7183
|  | BOURTON | ST |  |  | 0.75888 | 0.68915 | 0.60843 | 0.48738 | 0.35359 | 0.20266 | 0.0407 | -0.13364 | -0.32342 | -0.52814 | -1.013 | -2.7669 | -4.456 | -6.0795 | 2.8425 | 2.8001 | 2.7494 | 2.6816 | 2.6034 | 2.513 | 2.4126 | 2.3017 | 2.1787 | 2.0416 | 1.7061 | 0.50415 | -0.68915 | -1.9474 | 1.2938 | 1.2343 | 1.1656 | 1.0624 | 0.94825 | 0.81961 | 0.67911 | 0.52419 | 0.35418 | 0.16709 | -0.28615 | -1.8899 | -3.3812 | -4.7562
|  | BOURTON | FS |  |  | 0.65668 | 0.51283 | 0.35148 | 0.044767 | -0.29692 | -0.70866 | -1.1662 | -1.7014 | -2.5355 | -3.4031 | -6.5926 | -14.3733 | -18.8101 | -21.3117 | 2.741 | 2.6122 | 2.4619 | 2.2609 | 1.9966 | 1.674 | 1.2032 | 0.48769 | -1.1944 | -3.3727 | -9.814 | -35.8552 | -56.9643 | -63.63 | 1.1649 | 0.98951 | 0.79431 | 0.51133 | 0.14381 | -0.29188 | -1.1017 | -2.7333 | -4.8274 | -7.5268 | -15.4732 | -47.5795 | -73.627 | -82.0378
MANNINGTON GSP | WAREHAM | BOVINGTON | MINIMUM HEADROOM | SY 83933 87831 | YES | 3.8767 | 3.6804 | 3.4731 | 3.1888 | 2.642 | 2.0549 | 1.2687 | 0.28676 | -0.67401 | -1.6235 | -3.8065 | -8.1872 | -10.3434 | -11.2072 | 3.4265 | 3.3183 | 3.1972 | 3.0103 | 2.6506 | 2.2177 | 1.7763 | 1.1298 | 0.40452 | -0.32618 | -2.0646 | -5.3934 | -7.1473 | -7.5931 | 2.6633 | 2.4671 | 2.2636 | 1.9941 | 1.4994 | 0.97399 | 0.25368 | -0.65007 | -1.5572 | -2.4735 | -4.5616 | -8.8688 | -10.952 | -11.8079
|  | BOVINGTON | CT |  |  | 3.9491 | 3.8022 | 3.6198 | 3.3345 | 2.8077 | 2.1659 | 1.5218 | 0.60432 | -0.43047 | -1.4367 | -3.4984 | -8.1872 | -10.3434 | -11.2072 | 3.4458 | 3.3581 | 3.2077 | 3.0103 | 2.6506 | 2.2177 | 1.7763 | 1.1298 | 0.40452 | -0.32618 | -1.794 | -5.3934 | -7.1473 | -7.5931 | 2.7136 | 2.5585 | 2.3698 | 2.0987 | 1.6218 | 1.036 | 0.43608 | -0.42203 | -1.407 | -2.3793 | -4.3516 | -8.8688 | -10.952 | -11.8079
|  | BOVINGTON | LW |  |  | 3.8767 | 3.6804 | 3.4731 | 3.1888 | 2.642 | 2.0549 | 1.2687 | 0.28676 | -0.67401 | -1.6235 | -3.8065 | -7.9769 | -9.3158 | -9.3031 | 3.4265 | 3.3183 | 3.1972 | 3.0203 | 2.6743 | 2.313 | 1.8031 | 1.1506 | 0.49196 | -0.24667 | -2.0646 | -5.0824 | -6.123 | -7.0074 | 2.6633 | 2.4671 | 2.2636 | 1.9941 | 1.4994 | 0.97399 | 0.25368 | -0.65007 | -1.5572 | -2.4735 | -4.5616 | -8.4627 | -9.792 | -9.9818
|  | BOVINGTON | ST |  |  | 4.0668 | 4.0159 | 3.9437 | 3.8077 | 3.4598 | 3.092 | 2.7362 | 2.2737 | 1.8241 | 1.3302 | -0.002333 | -3.9309 | -6.6061 | -7.9168 | 3.4952 | 3.4803 | 3.4566 | 3.3273 | 3.0583 | 2.796 | 2.5252 | 2.1851 | 1.8293 | 1.4309 | 0.369 | -2.7765 | -4.9808 | -6.1137 | 2.8321 | 2.7784 | 2.7034 | 2.5546 | 2.2318 | 1.9027 | 1.5701 | 1.1469 | 0.71249 | 0.2274 | -1.073 | -4.9463 | -7.6141 | -8.9291
|  | BOVINGTON | FS |  |  | 3.9491 | 3.8022 | 3.6198 | 3.3345 | 2.8077 | 2.1659 | 1.5218 | 0.60432 | -0.43047 | -1.4367 | -3.4984 | -8.1872 | -10.3434 | -11.2072 | 3.4957 | 3.482 | 3.4589 | 3.3718 | 3.1976 | 3.0023 | 2.7817 | 2.5164 | 2.2425 | 1.9526 | 1.1905 | -1.4458 | -4.1944 | -6.0853 | 2.8314 | 2.7775 | 2.7123 | 2.603 | 2.3866 | 2.1396 | 1.8631 | 1.5327 | 1.1855 | 0.82288 | -0.1223 | -3.4326 | -6.7983 | -8.9174
AMERSHAM | LOUDWATER BSP | BOWERDEAN | MINIMUM HEADROOM | SU 87718 93880 | YES | -1.2293 | -2.157 | -2.9213 | -4.0629 | -5.3241 | -6.5932 | -8.1392 | -9.865 | -11.9304 | -14.1417 | -18.9946 | -28.5149 | -34.2074 | -36.3736 | 3.0646 | 2.5475 | 2.1175 | 1.562 | 0.90384 | 0.23533 | -0.72409 | -1.8591 | -3.4661 | -5.0528 | -8.1321 | -16.0334 | -21.1843 | -30.1401 | -1.2215 | -2.0172 | -2.6934 | -3.6937 | -4.8273 | -5.973 | -7.4636 | -9.1677 | -11.1761 | -13.3437 | -17.941 | -26.9018 | -32.0878 | -34.0175
|  | BOWERDEAN | CT |  |  | -0.73705 | -1.3342 | -1.8479 | -2.743 | -3.6996 | -4.8949 | -6.1214 | -7.7158 | -10.1651 | -12.5574 | -17.1506 | -28.5149 | -34.2074 | -36.3736 | 3.1473 | 2.6971 | 2.2595 | 1.6933 | 1.0754 | 0.23939 | -0.64766 | -1.8543 | -3.4661 | -5.0528 | -8.1321 | -16.0334 | -21.1843 | -26.1231 | -0.83921 | -1.3681 | -1.8582 | -2.6786 | -3.5594 | -4.7026 | -5.8926 | -7.4563 | -9.7567 | -12.0031 | -16.3093 | -26.9018 | -32.0878 | -34.0175
|  | BOWERDEAN | LW |  |  | -1.2293 | -2.157 | -2.9213 | -4.0629 | -5.3241 | -6.5932 | -8.1392 | -9.865 | -11.9304 | -14.1417 | -18.9946 | -27.8756 | -31.2727 | -30.3842 | 3.0646 | 2.5475 | 2.1175 | 1.562 | 0.90384 | 0.23533 | -0.72409 | -1.8591 | -3.1674 | -4.6033 | -7.6876 | -13.0603 | -14.7709 | -13.8164 | -1.2215 | -2.0172 | -2.6934 | -3.6937 | -4.8273 | -5.973 | -7.4636 | -9.1677 | -11.1761 | -13.3437 | -17.941 | -26.2688 | -29.3365 | -28.3557
|  | BOWERDEAN | ST |  |  | -0.46313 | -0.84422 | -1.1264 | -1.3518 | -1.6298 | -1.9938 | -2.4086 | -2.9227 | -3.5564 | -4.3526 | -6.5056 | -14.5441 | -21.0937 | -25.4742 | 3.3249 | 3.0348 | 2.7741 | 2.5307 | 2.2293 | 1.8476 | 1.3936 | 0.84769 | 0.22256 | -0.54565 | -2.5956 | -9.7681 | -16.1727 | -22.0575 | -0.5721 | -0.8784 | -1.1268 | -1.3518 | -1.6357 | -2.0103 | -2.4568 | -3.002 | -3.625 | -4.4105 | -6.5446 | -14.3614 | -20.5594 | -24.4686
|  | BOWERDEAN | FS |  |  | -0.73705 | -1.3342 | -1.8479 | -2.743 | -3.6996 | -4.8949 | -6.1214 | -7.7158 | -10.1651 | -12.5574 | -17.1506 | -28.5149 | -34.2074 | -36.3736 | 3.326 | 3.0285 | 2.7536 | 2.4888 | 2.1816 | 1.8103 | 1.3948 | 0.88891 | 0.23401 | -0.50211 | -2.3619 | -9.4389 | -18.9357 | -30.1401 | -0.55876 | -0.84665 | -1.0829 | -1.3536 | -1.6638 | -2.0409 | -2.4505 | -2.9548 | -3.6371 | -4.3862 | -6.2535 | -13.2882 | -21.371 | -27.2776
BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL | MINIMUM HEADROOM | SU 86075 69397 | YES | 31.8777 | 31.0839 | 30.1165 | 28.3268 | 26.6292 | 24.366 | 21.4104 | 18.1894 | 14.9385 | 11.6638 | 4.6953 | -5.9566 | -10.6772 | -13.1212 | 34.1115 | 33.6228 | 33.0136 | 31.9426 | 30.9271 | 29.0386 | 26.5785 | 24.1159 | 21.7109 | 19.23 | 14.6173 | 4.7677 | -2.4289 | -18.0623 | 27.2641 | 26.5004 | 25.5984 | 24.0665 | 22.5659 | 20.2545 | 17.2262 | 14.0347 | 10.903 | 7.8254 | 1.4038 | -8.8243 | -13.1082 | -15.298
|  | BRACKNELL | CT |  |  | 32.2487 | 31.7354 | 30.9041 | 29.2208 | 27.8277 | 25.6288 | 23.1158 | 20.0228 | 16.5262 | 13.2914 | 7.0576 | -5.0834 | -10.6772 | -13.1212 | 34.205 | 33.8101 | 33.1515 | 31.9779 | 31.0327 | 29.0574 | 26.7921 | 24.3187 | 21.7109 | 19.23 | 14.6173 | 4.7677 | -1.6448 | -8.4614 | 27.5703 | 27.0596 | 26.2773 | 24.8262 | 23.5975 | 21.3273 | 18.739 | 15.7374 | 12.4366 | 9.4037 | 3.6648 | -7.9035 | -13.1082 | -15.298
|  | BRACKNELL | LW |  |  | 31.8777 | 31.0839 | 30.1165 | 28.3268 | 26.6292 | 24.366 | 21.4104 | 18.1894 | 14.9385 | 11.6638 | 4.6953 | -5.9566 | -9.1389 | -8.5897 | 34.1115 | 33.6228 | 33.0136 | 31.9426 | 30.9271 | 29.0386 | 26.5785 | 24.1159 | 21.8605 | 19.5556 | 14.6904 | 7.1799 | 5.1999 | 5.9331 | 27.2641 | 26.5004 | 25.5984 | 24.0665 | 22.5659 | 20.2545 | 17.2262 | 14.0347 | 10.903 | 7.8254 | 1.4038 | -8.8243 | -11.8106 | -11.1843
|  | BRACKNELL | ST |  |  | 32.6588 | 32.4305 | 31.935 | 30.8547 | 30.0626 | 28.7045 | 27.0558 | 25.2091 | 23.422 | 21.6002 | 17.3252 | 6.8153 | 0.45909 | -2.8959 | 34.4314 | 34.2112 | 33.7653 | 32.8589 | 32.2095 | 30.7433 | 29.0045 | 27.2253 | 25.6156 | 24.0213 | 20.2804 | 10.4121 | 2.6374 | -4.5925 | 27.9634 | 27.7468 | 27.2643 | 26.3443 | 25.6595 | 24.1961 | 22.4369 | 20.5852 | 18.8549 | 17.1222 | 13.178 | 2.91 | -3.2551 | -6.256
|  | BRACKNELL | FS |  |  | 32.2487 | 31.7354 | 30.9041 | 29.2208 | 27.8277 | 25.6288 | 23.1158 | 20.0228 | 16.5262 | 13.2914 | 7.0576 | -5.0834 | -10.6772 | -13.1212 | 34.4538 | 34.1814 | 33.7909 | 33.0926 | 32.4528 | 31.0655 | 29.4445 | 27.725 | 26.0887 | 24.4946 | 20.7564 | 10.3697 | -2.4289 | -18.0623 | 27.9859 | 27.7267 | 27.3337 | 26.5979 | 25.9372 | 24.5519 | 22.9222 | 21.1672 | 19.5161 | 17.9151 | 14.3493 | 4.7952 | -4.3441 | -10.1436
MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON | MINIMUM HEADROOM | ST 81260 60564 | YES | 8.2232 | 7.0788 | 5.9642 | 4.5529 | 2.6757 | 0.55594 | -2.8135 | -7.2013 | -12.2327 | -17.7542 | -29.7296 | -48.9152 | -57.0699 | -60.4651 | 11.567 | 10.7731 | 9.8178 | 8.6888 | 7.4303 | 5.4473 | 3.249 | -0.11403 | -4.2653 | -8.2193 | -17.3707 | -32.528 | -39.7634 | -48.286 | 9.272 | 8.154 | 7.0464 | 5.6858 | 3.8401 | 1.666 | -1.5509 | -5.8804 | -10.8396 | -16.2881 | -28.1093 | -46.9694 | -55.101 | -61.0768
|  | BRADFORD-ON-AVON | CT |  |  | 8.3016 | 7.3281 | 6.1611 | 4.697 | 3.0731 | 0.55594 | -2.219 | -6.4487 | -11.7823 | -16.8502 | -26.1586 | -48.0949 | -57.0699 | -60.4651 | 11.567 | 10.7731 | 9.8178 | 8.6888 | 7.4303 | 5.4473 | 3.249 | -0.11403 | -4.2653 | -8.2193 | -15.4599 | -32.528 | -39.7634 | -43.5452 | 9.3103 | 8.3455 | 7.1875 | 5.7491 | 4.1525 | 1.666 | -1.0801 | -5.2701 | -10.5297 | -15.5397 | -24.7267 | -46.3291 | -55.101 | -58.4497
|  | BRADFORD-ON-AVON | LW |  |  | 8.2232 | 7.0788 | 5.9642 | 4.5529 | 2.6757 | 0.69559 | -2.8135 | -7.2013 | -12.2327 | -17.7542 | -29.7296 | -48.9152 | -53.3899 | -48.9074 | 11.6549 | 10.7843 | 9.9399 | 8.9383 | 7.5487 | 6.0903 | 3.4058 | 0.018809 | -3.8579 | -8.1148 | -17.3707 | -31.9265 | -35.1899 | -31.7308 | 9.272 | 8.154 | 7.0464 | 5.6858 | 3.8401 | 1.9054 | -1.5509 | -5.8804 | -10.8396 | -16.2881 | -28.1093 | -46.9694 | -51.39 | -47.0607
|  | BRADFORD-ON-AVON | ST |  |  | 8.9644 | 8.6515 | 8.2206 | 7.5301 | 6.646 | 5.4893 | 3.9516 | 2.0416 | -0.32513 | -3.1413 | -10.8781 | -36.0889 | -52.902 | -58.3342 | 12.0709 | 11.7909 | 11.4124 | 10.7899 | 10.0257 | 9.0423 | 7.7352 | 6.1446 | 4.1599 | 1.8244 | -4.5565 | -25.1518 | -39.1736 | -44.3897 | 9.9624 | 9.6508 | 9.2218 | 8.5117 | 7.6189 | 6.4574 | 4.9098 | 3.0032 | 0.63176 | -2.1864 | -9.9203 | -35.0333 | -51.7848 | -57.1446
|  | BRADFORD-ON-AVON | FS |  |  | 8.3016 | 7.3281 | 6.1611 | 4.697 | 3.0731 | 0.55594 | -2.219 | -6.4487 | -11.7823 | -16.8502 | -26.1586 | -48.0949 | -57.0699 | -60.4651 | 12.0824 | 11.82 | 11.478 | 11.0141 | 10.415 | 9.6483 | 8.6722 | 7.4554 | 6.0188 | 4.3352 | -0.26138 | -17.0393 | -35.9784 | -48.286 | 9.9797 | 9.6988 | 9.3251 | 8.7794 | 8.0685 | 7.1567 | 5.9937 | 4.5406 | 2.8026 | 0.76487 | -4.7961 | -25.1543 | -47.7674 | -61.0768
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN | MINIMUM HEADROOM | SU 67431 58511 | YES | 8.844 | 8.4472 | 8.0551 | 7.5791 | 6.9678 | 6.3039 | 5.2489 | 3.8581 | 2.2673 | 0.48446 | -3.4004 | -10.1157 | -13.3924 | -14.9727 | 9.9712 | 9.707 | 9.39 | 9.0083 | 8.5775 | 7.9149 | 7.1658 | 6.0598 | 4.7106 | 3.3361 | 0.64718 | -5.2487 | -8.4547 | -10.8886 | 8.4941 | 8.1108 | 7.7326 | 7.2768 | 6.6855 | 5.9714 | 4.9874 | 3.6124 | 1.9747 | 0.25606 | -3.5779 | -10.3958 | -13.6951 | -15.7563
|  | BRAMLEY GREEN | CT |  |  | 8.9015 | 8.572 | 8.1803 | 7.6855 | 7.1351 | 6.3039 | 5.3768 | 4.0003 | 2.2797 | 0.55884 | -2.6258 | -10.1157 | -13.3924 | -14.8492 | 9.9712 | 9.707 | 9.39 | 9.0083 | 8.5775 | 7.9149 | 7.1658 | 6.0598 | 4.7106 | 3.3361 | 0.79329 | -5.2487 | -8.0801 | -9.8073 | 8.5352 | 8.211 | 7.8248 | 7.3388 | 6.7957 | 5.9714 | 5.0472 | 3.6796 | 1.9747 | 0.25606 | -2.9202 | -10.3958 | -13.6951 | -15.2336
|  | BRAMLEY GREEN | LW |  |  | 8.844 | 8.4472 | 8.0551 | 7.5791 | 6.9678 | 6.3368 | 5.2489 | 3.8581 | 2.2673 | 0.48446 | -3.4004 | -9.8562 | -11.8186 | -10.9961 | 9.9948 | 9.712 | 9.4327 | 9.109 | 8.667 | 8.2064 | 7.3586 | 6.2877 | 5.056 | 3.6702 | 0.64718 | -4.3354 | -6.0635 | -5.7933 | 8.4941 | 8.1108 | 7.7326 | 7.2768 | 6.6855 | 6.0743 | 4.9874 | 3.6124 | 2.037 | 0.2704 | -3.5779 | -9.9651 | -12.0457 | -11.4624
|  | BRAMLEY GREEN | ST |  |  | 9.1119 | 8.9925 | 8.8309 | 8.5183 | 8.1661 | 7.7277 | 7.1529 | 6.4766 | 5.6399 | 4.6319 | 1.9135 | -6.6883 | -12.658 | -14.9727 | 10.13 | 10.0273 | 9.8903 | 9.6017 | 9.2907 | 8.9117 | 8.4066 | 7.8388 | 7.1173 | 6.2617 | 3.9707 | -3.216 | -8.4547 | -10.8886 | 8.7423 | 8.6247 | 8.4662 | 8.1372 | 7.7756 | 7.3297 | 6.7404 | 6.0615 | 5.2066 | 4.1845 | 1.4364 | -7.2228 | -13.3163 | -15.7563
|  | BRAMLEY GREEN | FS |  |  | 8.9015 | 8.572 | 8.1803 | 7.6855 | 7.1351 | 6.3039 | 5.3768 | 4.0003 | 2.2797 | 0.55884 | -2.6258 | -10.1157 | -13.3924 | -14.8492 | 10.1329 | 10.0325 | 9.9021 | 9.7146 | 9.4838 | 9.1858 | 8.816 | 8.3561 | 7.8137 | 7.1641 | 4.7194 | -1.8729 | -6.4237 | -10.3149 | 8.755 | 8.6457 | 8.5019 | 8.2776 | 8.0021 | 7.6459 | 7.2041 | 6.6558 | 5.9914 | 5.2146 | 2.5628 | -5.6271 | -11.2926 | -15.6567
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD | MINIMUM HEADROOM | SZ 64712 98665 | YES | 2.8419 | 2.1744 | 1.5289 | 0.50296 | -0.69814 | -1.9336 | -3.722 | -5.7796 | -7.9859 | -10.4193 | -15.6367 | -24.2275 | -27.8381 | -29.19 | 6.1655 | 5.3487 | 4.3962 | 3.1528 | 1.7812 | 0.035312 | -1.8882 | -4.3288 | -7.1722 | -10.1181 | -16.7169 | -46.2922 | -101.34 | -202.5647 | 2.2332 | 1.6318 | 1.0494 | 0.14612 | -0.96557 | -2.1113 | -3.8062 | -5.7815 | -7.9156 | -10.2752 | -15.3403 | -23.6483 | -27.01 | -28.3311
|  | BRANDON ROAD | CT |  |  | 3.1277 | 2.6814 | 2.1635 | 1.255 | 0.29462 | -0.98893 | -2.3579 | -4.1961 | -6.4933 | -8.7302 | -12.9118 | -23.3161 | -27.8381 | -29.19 | 6.1655 | 5.3487 | 4.3962 | 3.1528 | 1.7812 | 0.035312 | -1.8882 | -4.3288 | -7.1722 | -10.1181 | -16.3146 | -36.8696 | -65.57 | -113.7286 | 2.4317 | 2.0008 | 1.4975 | 0.69879 | -0.16698 | -1.3617 | -2.6419 | -4.4177 | -6.6201 | -8.7657 | -12.7881 | -22.7282 | -27.01 | -28.3311
|  | BRANDON ROAD | LW |  |  | 2.8419 | 2.1744 | 1.5289 | 0.50296 | -0.69814 | -1.9336 | -3.722 | -5.7796 | -7.9859 | -10.4193 | -15.6367 | -24.2275 | -26.2309 | -25.1411 | 6.5733 | 6.1546 | 5.7496 | 5.2023 | 4.5195 | 3.8025 | 2.632 | 1.2263 | -0.33972 | -2.09 | -5.8668 | -11.9422 | -13.4245 | -12.5357 | 2.2332 | 1.6318 | 1.0494 | 0.14612 | -0.96557 | -2.1113 | -3.8062 | -5.7815 | -7.9156 | -10.2752 | -15.3403 | -23.6483 | -25.611 | -24.5636
|  | BRANDON ROAD | ST |  |  | 3.5237 | 3.3878 | 3.2173 | 3.0183 | 2.7442 | 2.3695 | 1.8682 | 1.2471 | 0.4872 | -0.47895 | -3.1698 | -12.942 | -19.9098 | -22.9071 | 6.4058 | 5.8024 | 5.0892 | 4.2012 | 3.1632 | 1.9334 | 0.4919 | -1.1642 | -3.0517 | -5.2497 | -10.809 | -31.8705 | -62.6916 | -111.3752 | 2.8003 | 2.6718 | 2.5062 | 2.3059 | 2.0284 | 1.6484 | 1.1387 | 0.49875 | -0.28742 | -1.284 | -4.0601 | -13.906 | -20.8467 | -23.6226
|  | BRANDON ROAD | FS |  |  | 3.1277 | 2.6814 | 2.1635 | 1.255 | 0.29462 | -0.98893 | -2.3579 | -4.1961 | -6.4933 | -8.7302 | -12.9118 | -23.3161 | -27.8381 | -29.19 | 6.331 | 5.6028 | 4.7502 | 3.4768 | 1.9966 | 0.30243 | -1.7129 | -4.0133 | -6.5247 | -9.4225 | -16.7169 | -46.2922 | -101.34 | -202.5647 | 2.7721 | 2.6422 | 2.4822 | 2.2394 | 1.935 | 1.5582 | 1.0745 | 0.49592 | -0.18998 | -0.99744 | -3.1688 | -11.173 | -20.4955 | -26.7358
BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD | MINIMUM HEADROOM | SU 88887 80726 | YES | 8.3806 | 7.88 | 7.2671 | 6.4042 | 5.458 | 4.3698 | 3.0993 | 1.8142 | 0.31414 | -1.2941 | -6.6857 | -14.3324 | -16.3847 | -17.663 | 12.5936 | 12.4052 | 12.1745 | 11.9091 | 11.6006 | 11.035 | 10.0755 | 8.8796 | 7.4216 | 5.7327 | 1.8517 | -3.6113 | -4.9317 | -16.9474 | 8.9132 | 8.4874 | 7.9861 | 7.2557 | 6.4515 | 5.5216 | 4.4344 | 3.3326 | 2.0637 | -0.057083 | -5.1316 | -12.3517 | -14.2545 | -15.4467
|  | BRAYWICK ROAD | CT |  |  | 8.4194 | 8.2144 | 7.9081 | 7.3286 | 6.6732 | 5.8468 | 4.9376 | 4.0021 | 2.6778 | 1.3128 | -1.2141 | -5.6088 | -8.1671 | -9.5785 | 12.6121 | 12.4783 | 12.2706 | 12.1014 | 11.9191 | 11.6063 | 11.2589 | 10.7776 | 9.9856 | 9.1532 | 7.5248 | 3.7822 | -0.5651 | -7.2129 | 9.1643 | 8.9212 | 8.5863 | 8.0918 | 7.5498 | 6.862 | 6.0963 | 5.3088 | 4.1901 | 3.0376 | 0.90197 | -2.8689 | -5.0786 | -6.2797
|  | BRAYWICK ROAD | LW |  |  | 8.3806 | 7.88 | 7.2671 | 6.4042 | 5.458 | 4.3698 | 3.0993 | 1.8142 | 0.31414 | -1.2941 | -6.6857 | -14.3324 | -16.3847 | -17.663 | 12.5936 | 12.4052 | 12.1745 | 11.9091 | 11.6006 | 11.035 | 10.0755 | 8.8796 | 7.4216 | 5.7327 | 1.8517 | -3.6113 | -4.9317 | -5.8253 | 8.9132 | 8.4874 | 7.9861 | 7.2557 | 6.4515 | 5.5216 | 4.4344 | 3.3326 | 2.0637 | -0.057083 | -5.1316 | -12.3517 | -14.2545 | -15.4467
|  | BRAYWICK ROAD | ST |  |  | 8.4643 | 8.2931 | 8.0182 | 7.7548 | 7.4518 | 6.9731 | 6.4629 | 6.0069 | 5.4964 | 4.9394 | 3.899 | 2.004 | 0.57302 | -1.5094 | 12.6476 | 12.5406 | 12.3579 | 12.1623 | 11.9739 | 11.6806 | 11.3458 | 11.0986 | 10.8246 | 10.4863 | 9.4186 | 6.4819 | 2.4444 | -4.436 | 9.2789 | 9.1036 | 8.8288 | 8.523 | 8.2339 | 7.8553 | 7.4415 | 7.0861 | 6.6958 | 6.2662 | 5.4511 | 3.4828 | 2.4665 | 0.77698
|  | BRAYWICK ROAD | FS |  |  | 8.4194 | 8.2144 | 7.9081 | 7.3286 | 6.6732 | 5.8468 | 4.9376 | 4.0021 | 2.6778 | 1.3128 | -1.2141 | -5.6088 | -8.1671 | -9.5785 | 12.6677 | 12.5417 | 12.3762 | 12.2039 | 12.0167 | 11.7797 | 11.5124 | 11.2438 | 10.7893 | 10.1578 | 8.7542 | 4.1624 | -3.4789 | -16.9474 | 9.2994 | 9.132 | 8.9119 | 8.6362 | 8.3551 | 8.0252 | 7.6716 | 7.3155 | 6.8923 | 6.4484 | 5.5648 | 2.4172 | -2.4094 | -5.6045
EALING GSP | EALING (D) | BRENTFORD | MINIMUM HEADROOM | TQ 17659 78277 | YES | 7.3839 | 5.0619 | 3.3222 | 1.5493 | -0.060296 | -1.6893 | -4.1362 | -7.0555 | -10.1672 | -13.4974 | -20.71 | -33.0852 | -37.06 | -38.8792 | 14.1441 | 12.8385 | 11.8546 | 10.7865 | 9.6311 | 7.9261 | 5.9329 | 3.2438 | 0.13501 | -2.8703 | -8.5062 | -23.7974 | -50.7613 | -98.368 | 9.1952 | 7.2441 | 5.7741 | 4.2203 | 2.7153 | 1.1882 | -1.1532 | -3.9604 | -6.9494 | -10.1775 | -17.1889 | -29.1386 | -33.0319 | -34.6282
|  | BRENTFORD | CT |  |  | 7.9239 | 6.246 | 4.8181 | 3.3027 | 1.996 | 0.057095 | -2.2203 | -5.2533 | -8.8037 | -12.0845 | -17.911 | -31.4077 | -37.06 | -38.8792 | 14.1907 | 13.0716 | 11.9653 | 10.7865 | 9.6311 | 7.9261 | 5.9329 | 3.2438 | 0.13501 | -2.8703 | -8.5062 | -23.7974 | -38.2708 | -60.0451 | 9.6017 | 8.1862 | 6.9319 | 5.6065 | 4.4139 | 2.5875 | 0.44867 | -2.4957 | -5.9326 | -9.1327 | -14.8048 | -27.8498 | -33.0319 | -34.6282
|  | BRENTFORD | LW |  |  | 7.3839 | 5.0619 | 3.3222 | 1.5493 | -0.060296 | -1.6893 | -4.1362 | -7.0555 | -10.1672 | -13.4974 | -20.71 | -33.0852 | -36.2896 | -33.969 | 14.1441 | 12.8385 | 11.8546 | 10.8571 | 9.8431 | 8.8112 | 7.0842 | 4.9678 | 2.6977 | 0.20125 | -5.2423 | -14.276 | -16.3185 | -13.9943 | 9.1952 | 7.2441 | 5.7741 | 4.2203 | 2.7153 | 1.1882 | -1.1532 | -3.9604 | -6.9494 | -10.1775 | -17.1889 | -29.1386 | -32.1363 | -29.6986
|  | BRENTFORD | ST |  |  | 8.4053 | 7.1367 | 6.1637 | 5.3539 | 4.719 | 3.8103 | 2.5431 | 1.0973 | -0.42914 | -2.1552 | -6.4274 | -20.9942 | -30.4684 | -33.6554 | 14.5061 | 13.6923 | 12.9433 | 12.1454 | 11.3522 | 10.3023 | 8.9185 | 7.3322 | 5.5906 | 3.5821 | -1.3735 | -18.3594 | -36.004 | -58.2483 | 10.0571 | 9.0484 | 8.2489 | 7.5301 | 6.914 | 6.0345 | 4.8032 | 3.3766 | 1.8507 | 0.084441 | -4.3552 | -18.7756 | -28.0433 | -31.0018
|  | BRENTFORD | FS |  |  | 7.9239 | 6.246 | 4.8181 | 3.3027 | 1.996 | 0.057095 | -2.2203 | -5.2533 | -8.8037 | -12.0845 | -17.911 | -31.4077 | -37.06 | -38.8792 | 14.6535 | 13.761 | 12.9727 | 12.0952 | 11.1743 | 10.1267 | 8.8615 | 7.4273 | 5.7437 | 3.8216 | -1.0176 | -19.8141 | -50.7613 | -98.368 | 10.3041 | 9.3439 | 8.63 | 7.9445 | 7.3235 | 6.6088 | 5.7429 | 4.7584 | 3.6454 | 2.4019 | -0.7812 | -12.4579 | -25.7592 | -33.8694
LOVEDEAN GSP | HAVANT | BROCKHAMPTON | MINIMUM HEADROOM | SU 70868 05828 | YES | 14.3389 | 14.1463 | 13.9506 | 13.7124 | 13.4285 | 13.2163 | 12.9947 | 12.7695 | 12.5264 | 12.2697 | 11.5886 | 9.9112 | 8.8793 | 7.8031 | 14.3865 | 14.1422 | 13.8933 | 13.6184 | 13.2859 | 13.0234 | 12.7442 | 12.412 | 12.0566 | 11.6732 | 10.8869 | 9.7081 | 8.3384 | 5.0854 | 13.7909 | 13.5845 | 13.3744 | 13.1178 | 12.8006 | 12.5608 | 12.3246 | 12.0827 | 11.8276 | 11.5547 | 10.9991 | 9.9599 | 8.763 | 7.5777
|  | BROCKHAMPTON | CT |  |  | 14.3389 | 14.1463 | 13.9506 | 13.7124 | 13.4411 | 13.3377 | 13.2089 | 13.0523 | 12.8186 | 12.5256 | 11.9372 | 10.0587 | 9.0711 | 8.3035 | 14.3865 | 14.1422 | 13.8933 | 13.6184 | 13.3054 | 13.1546 | 12.9711 | 12.7081 | 12.3245 | 11.895 | 11.1071 | 9.909 | 9.2529 | 7.5436 | 13.7909 | 13.5845 | 13.3744 | 13.1178 | 12.8251 | 12.6988 | 12.5421 | 12.3523 | 12.0767 | 11.7532 | 11.157 | 10.133 | 9.1132 | 8.2433
|  | BROCKHAMPTON | LW |  |  | 14.3413 | 14.171 | 13.9743 | 13.7243 | 13.4285 | 13.2163 | 12.9947 | 12.7695 | 12.5264 | 12.2697 | 11.5886 | 9.9112 | 8.8793 | 7.8031 | 14.3911 | 14.1738 | 13.9302 | 13.6358 | 13.2859 | 13.0234 | 12.7442 | 12.412 | 12.0566 | 11.6732 | 10.8869 | 9.9155 | 9.0334 | 7.8374 | 13.7926 | 13.6062 | 13.395 | 13.1234 | 12.8006 | 12.5608 | 12.3246 | 12.0827 | 11.8276 | 11.5547 | 10.9991 | 10.0101 | 8.8635 | 7.5777
|  | BROCKHAMPTON | ST |  |  | 14.3765 | 14.2127 | 14.0435 | 13.7724 | 13.4927 | 13.4086 | 13.29 | 13.1913 | 13.0015 | 12.7964 | 12.3029 | 10.7803 | 9.4978 | 8.3337 | 14.4412 | 14.2392 | 14.0298 | 13.7163 | 13.3953 | 13.2761 | 13.112 | 12.9683 | 12.7117 | 12.4324 | 11.6798 | 9.7081 | 8.3384 | 7.2132 | 13.8344 | 13.658 | 13.4765 | 13.1839 | 12.8789 | 12.774 | 12.6277 | 12.5059 | 12.2795 | 12.0365 | 11.4506 | 9.9599 | 8.763 | 7.7765
|  | BROCKHAMPTON | FS |  |  | 14.3389 | 14.1463 | 13.9506 | 13.7124 | 13.4411 | 13.3377 | 13.2089 | 13.0523 | 12.8186 | 12.5256 | 11.9372 | 10.0587 | 9.0711 | 8.3035 | 14.5131 | 14.4 | 14.263 | 14.0877 | 13.9007 | 13.7594 | 13.624 | 13.4853 | 13.3254 | 13.143 | 12.6917 | 11.4549 | 10.3653 | 5.0854 | 13.9007 | 13.8017 | 13.6827 | 13.5249 | 13.3532 | 13.2269 | 13.1077 | 12.9879 | 12.8501 | 12.6938 | 12.3111 | 11.4485 | 10.778 | 10.1257
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST | MINIMUM HEADROOM | SU 59381 02061 | YES | 8.9591 | 8.1521 | 7.227 | 5.9185 | 4.3446 | 2.6945 | 0.44463 | -1.9907 | -4.8385 | -7.872 | -14.3287 | -24.8436 | -29.8018 | -31.7221 | 11.3276 | 10.6287 | 9.8293 | 8.9033 | 7.8615 | 6.4821 | 5.0179 | 3.078 | 0.66388 | -1.6536 | -5.9766 | -16.0738 | -23.8916 | -42.0149 | 8.8395 | 7.9871 | 7.0856 | 5.8599 | 4.3782 | 2.8562 | 0.71359 | -1.5769 | -4.2079 | -7.1403 | -13.3864 | -23.4973 | -28.2991 | -30.1425
|  | BROCKHURST | CT |  |  | 9.2267 | 8.5395 | 7.6876 | 6.4741 | 5.1079 | 3.3903 | 1.6473 | -0.7568 | -3.8516 | -6.8236 | -12.3164 | -24.5334 | -29.8018 | -31.7221 | 11.3276 | 10.6287 | 9.8293 | 8.9033 | 7.8615 | 6.4821 | 5.0179 | 3.078 | 0.66388 | -1.6536 | -5.9766 | -16.0738 | -22.472 | -29.1562 | 9.0378 | 8.2905 | 7.4316 | 6.2863 | 5.0205 | 3.407 | 1.7427 | -0.48198 | -3.4586 | -6.3131 | -11.5679 | -23.2947 | -28.2991 | -30.1425
|  | BROCKHURST | LW |  |  | 8.9591 | 8.1521 | 7.227 | 5.9185 | 4.3446 | 2.6945 | 0.44463 | -1.9907 | -4.8385 | -7.872 | -14.3287 | -24.8436 | -27.3442 | -25.4571 | 11.3329 | 10.6522 | 9.9392 | 9.0767 | 7.9847 | 6.8522 | 5.1037 | 3.1892 | 1.0839 | -1.1598 | -5.9572 | -13.3981 | -15.0964 | -13.5475 | 8.8395 | 7.9871 | 7.0856 | 5.8599 | 4.3782 | 2.8562 | 0.71359 | -1.5769 | -4.2079 | -7.1403 | -13.3864 | -23.4973 | -25.8917 | -24.0585
|  | BROCKHURST | ST |  |  | 9.5304 | 9.0868 | 8.5643 | 8.0021 | 7.2662 | 6.4631 | 5.5019 | 4.4862 | 3.2624 | 1.7206 | -2.2501 | -14.2273 | -22.6058 | -25.8871 | 11.5948 | 11.1519 | 10.6378 | 10.0726 | 9.3625 | 8.5573 | 7.6087 | 6.5839 | 5.3255 | 3.8885 | 0.21684 | -10.9196 | -20.2506 | -27.6466 | 9.3831 | 8.9363 | 8.4063 | 7.8319 | 7.1096 | 6.3105 | 5.3826 | 4.3954 | 3.2135 | 1.6974 | -2.2956 | -14.3974 | -22.6725 | -25.8322
|  | BROCKHURST | FS |  |  | 9.2267 | 8.5395 | 7.6876 | 6.4741 | 5.1079 | 3.3903 | 1.6473 | -0.7568 | -3.8516 | -6.8236 | -12.3164 | -24.5334 | -29.8018 | -31.7221 | 11.6591 | 11.3431 | 10.9528 | 10.4776 | 9.9125 | 9.2629 | 8.5203 | 7.6826 | 6.6265 | 5.4277 | 2.346 | -8.7081 | -23.8916 | -42.0149 | 9.4539 | 9.164 | 8.7961 | 8.3238 | 7.7655 | 7.1336 | 6.4284 | 5.6437 | 4.7186 | 3.6805 | 0.80104 | -9.6147 | -21.1502 | -28.2572
MELKSHAM GSP | NORRINGTON | BROMHAM | MINIMUM HEADROOM | ST 98670 65994 | YES | 1.0372 | 0.77376 | 0.51963 | 0.23354 | -0.14123 | -0.70874 | -1.3486 | -2.2906 | -3.466 | -4.6557 | -6.9431 | -11.969 | -13.9555 | -14.782 | 2.0317 | 1.9567 | 1.8033 | 1.5569 | 1.2743 | 0.83855 | 0.33988 | -0.39909 | -1.3027 | -2.2263 | -4.5111 | -9.1403 | -10.5699 | -11.5774 | 1.2883 | 1.0353 | 0.79123 | 0.49718 | 0.13054 | -0.42634 | -1.0564 | -1.9848 | -3.1393 | -4.3116 | -6.5605 | -12.2137 | -14.0542 | -15.2976
|  | BROMHAM | CT |  |  | 1.0602 | 0.83442 | 0.56684 | 0.23425 | -0.14123 | -0.70874 | -1.3486 | -2.2906 | -3.466 | -4.6557 | -6.9431 | -11.969 | -13.9555 | -14.782 | 2.0317 | 1.9567 | 1.8033 | 1.5569 | 1.2743 | 0.83855 | 0.33988 | -0.39909 | -1.3027 | -2.2263 | -4.5111 | -9.1403 | -10.5699 | -11.5774 | 1.3026 | 1.0827 | 0.82111 | 0.49718 | 0.13054 | -0.42634 | -1.0564 | -1.9848 | -3.1393 | -4.3116 | -6.5605 | -12.2137 | -14.0542 | -15.2976
|  | BROMHAM | LW |  |  | 1.0372 | 0.77376 | 0.51963 | 0.23354 | -0.14106 | -0.53258 | -1.2016 | -2.0348 | -2.9672 | -4.0031 | -6.2696 | -9.9517 | -10.871 | -10.0974 | 2.0696 | 2.0176 | 1.8457 | 1.6496 | 1.3827 | 1.1028 | 0.59815 | -0.035819 | -0.7436 | -1.5488 | -3.3474 | -6.1722 | -6.9049 | -6.3777 | 1.2883 | 1.0353 | 0.79123 | 0.5152 | 0.15153 | -0.22871 | -0.88565 | -1.7051 | -2.6221 | -3.6423 | -5.8462 | -9.3603 | -10.3136 | -9.6987
|  | BROMHAM | ST |  |  | 1.215 | 1.1284 | 1.0276 | 0.85097 | 0.64689 | 0.39216 | 0.066967 | -0.32186 | -0.77758 | -1.335 | -2.8429 | -7.9465 | -11.4103 | -12.5591 | 2.0886 | 2.0768 | 2.0608 | 1.9995 | 1.8424 | 1.64 | 1.3748 | 1.0659 | 0.69516 | 0.24514 | -0.98119 | -5.1269 | -8.0121 | -9.0816 | 1.453 | 1.3702 | 1.2724 | 1.0931 | 0.88928 | 0.6361 | 0.3101 | -0.074913 | -0.53122 | -1.0874 | -2.5874 | -7.503 | -10.9832 | -12.1518
|  | BROMHAM | FS |  |  | 1.0602 | 0.83442 | 0.56684 | 0.23425 | -0.14123 | -0.70874 | -1.3486 | -2.2906 | -3.466 | -4.6557 | -6.9431 | -11.969 | -13.9555 | -14.782 | 2.089 | 2.0785 | 2.0645 | 2.0377 | 1.9506 | 1.7959 | 1.6076 | 1.375 | 1.1099 | 0.80061 | -0.026274 | -3.1944 | -6.7964 | -9.0469 | 1.4672 | 1.3985 | 1.3146 | 1.1833 | 1.0289 | 0.83097 | 0.59413 | 0.30232 | -0.032915 | -0.42376 | -1.4565 | -5.2958 | -9.6113 | -12.1953
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET | MINIMUM HEADROOM | SU 63480 52228 | YES | 15.8256 | 15.6617 | 15.4602 | 15.2186 | 14.9279 | 13.7715 | 12.1894 | 9.8255 | 6.9903 | 4.3051 | -0.76661 | -11.4399 | -15.3469 | -16.6346 | 17.2712 | 17.0228 | 16.5266 | 15.8944 | 15.1893 | 14.1023 | 12.8122 | 10.8904 | 8.6049 | 6.396 | 2.2541 | -7.5632 | -13.2422 | -28.1597 | 15.1699 | 14.713 | 14.1986 | 13.5589 | 12.8475 | 11.6829 | 10.1567 | 7.8563 | 5.0976 | 2.4735 | -2.4944 | -12.9266 | -16.6902 | -17.9739
|  | BROOK STREET | CT |  |  | 15.8256 | 15.6617 | 15.4602 | 15.2186 | 14.9279 | 13.7715 | 12.1894 | 9.8255 | 6.9903 | 4.3051 | -0.56112 | -11.4399 | -15.3469 | -16.6346 | 17.2712 | 17.0228 | 16.5266 | 15.8944 | 15.1893 | 14.1023 | 12.8122 | 10.8904 | 8.6049 | 6.396 | 2.2541 | -7.5632 | -13.1619 | -19.0186 | 15.1699 | 14.7295 | 14.1986 | 13.5589 | 12.8475 | 11.6829 | 10.1567 | 7.8563 | 5.0976 | 2.4735 | -2.3099 | -12.9266 | -16.6902 | -17.9739
|  | BROOK STREET | LW |  |  | 15.8736 | 15.7224 | 15.5821 | 15.4233 | 15.1172 | 14.2239 | 12.3629 | 10.0487 | 7.5132 | 4.8098 | -0.76661 | -9.8909 | -11.3967 | -8.3704 | 17.3388 | 17.1251 | 16.8035 | 16.3327 | 15.6762 | 14.9951 | 13.6115 | 11.8772 | 9.9796 | 7.9088 | 3.5439 | -3.2132 | -4.2756 | -1.9593 | 15.2004 | 14.713 | 14.2392 | 13.6818 | 12.9223 | 12.138 | 10.3581 | 8.1155 | 5.6582 | 3.0116 | -2.4944 | -11.3197 | -12.7781 | -9.7634
|  | BROOK STREET | ST |  |  | 15.9498 | 15.9045 | 15.8421 | 15.7493 | 15.6286 | 15.471 | 15.1968 | 14.8614 | 13.7104 | 12.3302 | 8.6547 | -3.8667 | -11.6098 | -13.4392 | 17.3792 | 17.3217 | 17.2455 | 17.0706 | 16.7138 | 16.1986 | 15.4732 | 14.5725 | 13.5354 | 12.2819 | 8.9407 | -2.1324 | -10.7507 | -16.9663 | 15.5482 | 15.4442 | 15.2888 | 15.0593 | 14.7381 | 14.3071 | 13.6365 | 12.7589 | 11.6444 | 10.2894 | 6.6368 | -5.5593 | -13.2616 | -15.0311
|  | BROOK STREET | FS |  |  | 15.8256 | 15.6617 | 15.4602 | 15.2186 | 14.9279 | 13.7715 | 12.1894 | 9.8255 | 6.9903 | 4.3051 | -0.56112 | -11.4399 | -15.3469 | -16.6346 | 17.3777 | 17.3199 | 17.2241 | 17.0312 | 16.7371 | 16.2725 | 15.6365 | 14.8711 | 14.0195 | 13.0393 | 10.4553 | 0.39959 | -13.2422 | -28.1597 | 15.5305 | 15.4355 | 15.2993 | 15.0883 | 14.8169 | 14.4646 | 13.9369 | 13.2939 | 12.5901 | 11.6848 | 9.257 | -0.094776 | -11.2834 | -17.5468
MELKSHAM GSP | FROME BSP | BRUTON | MINIMUM HEADROOM | ST 69094 35148 | YES | 1.603 | 1.0307 | 0.45943 | -0.22045 | -1.1482 | -2.1621 | -3.9324 | -6.1562 | -8.6591 | -11.4978 | -17.8536 | -27.9877 | -31.0241 | -32.4841 | 2.5756 | 2.1793 | 1.7012 | 1.1514 | 0.46316 | -0.44328 | -1.8142 | -3.6498 | -5.691 | -8.0092 | -13.0848 | -21.1248 | -23.7409 | -28.3862 | 1.6258 | 1.076 | 0.51781 | -0.15628 | -1.0777 | -2.0867 | -3.8492 | -6.0599 | -8.5583 | -11.4414 | -17.767 | -27.8198 | -30.839 | -36.1606
|  | BRUTON | CT |  |  | 1.603 | 1.1179 | 0.53751 | -0.14041 | -0.89442 | -2.0728 | -3.3799 | -5.3767 | -7.864 | -10.3162 | -14.9177 | -26.1997 | -31.0241 | -32.4841 | 2.5756 | 2.1793 | 1.7012 | 1.1514 | 0.53548 | -0.44328 | -1.5363 | -3.2112 | -5.206 | -7.1664 | -10.84 | -19.8659 | -23.7409 | -25.1075 | 1.6258 | 1.1478 | 0.57499 | -0.094206 | -0.8405 | -2.0098 | -3.3106 | -5.3589 | -7.8509 | -10.2918 | -14.8663 | -26.0691 | -30.839 | -32.309
|  | BRUTON | LW |  |  | 1.603 | 1.0307 | 0.45943 | -0.22045 | -1.1482 | -2.1621 | -3.9324 | -6.1562 | -8.6591 | -11.4978 | -17.8536 | -27.9877 | -29.9364 | -31.0682 | 2.6269 | 2.187 | 1.7495 | 1.211 | 0.46316 | -0.35488 | -1.8142 | -3.6498 | -5.691 | -8.0092 | -13.0848 | -21.1248 | -22.7075 | -23.324 | 1.6355 | 1.076 | 0.51781 | -0.15628 | -1.0777 | -2.0867 | -3.8492 | -6.0599 | -8.5583 | -11.4414 | -17.767 | -27.8198 | -29.7912 | -30.4086
|  | BRUTON | ST |  |  | 1.9319 | 1.7626 | 1.5441 | 1.1772 | 0.73407 | 0.1773 | -0.55867 | -1.4447 | -2.4771 | -3.7635 | -7.4459 | -19.4539 | -27.1973 | -29.1986 | 2.8381 | 2.7034 | 2.5239 | 2.1989 | 1.818 | 1.3388 | 0.69898 | -0.060585 | -0.9525 | -2.057 | -5.0891 | -14.8447 | -21.2121 | -23.0063 | 1.9494 | 1.7842 | 1.5695 | 1.1919 | 0.74412 | 0.18387 | -0.5597 | -1.4452 | -2.4812 | -3.8045 | -7.533 | -19.5323 | -27.2924 | -29.3222
|  | BRUTON | FS |  |  | 1.603 | 1.1179 | 0.53751 | -0.14041 | -0.89442 | -2.0728 | -3.3799 | -5.3767 | -7.864 | -10.3162 | -14.9177 | -26.1997 | -31.0241 | -32.4841 | 2.7829 | 2.6075 | 2.3832 | 2.0822 | 1.7093 | 1.2046 | 0.58246 | -0.23739 | -1.1803 | -2.2446 | -4.9448 | -14.0493 | -23.1943 | -28.3862 | 1.8944 | 1.683 | 1.4173 | 1.0514 | 0.5993 | -0.0056845 | -0.75602 | -1.7352 | -2.8782 | -4.1662 | -7.4389 | -18.7012 | -29.9552 | -36.1606
COWLEY GSP | WITNEY BSP | BURFORD | MINIMUM HEADROOM | SP 25671 12529 | NO | 0.83158 | 0.65191 | 0.49653 | 0.31286 | -0.057267 | -0.844 | -1.9807 | -3.5189 | -5.4229 | -7.7977 | -13.843 | -23.569 | -25.9098 | -27.4896 | 1.8097 | 1.6167 | 1.4503 | 1.2608 | 0.9993 | 0.65972 | -0.047399 | -1.2501 | -2.7366 | -4.5935 | -9.3261 | -16.9214 | -18.7228 | -19.9457 | 0.66476 | 0.35872 | 0.097793 | -0.18401 | -0.57016 | -1 | -1.7491 | -2.7054 | -4.01 | -6.2932 | -12.1044 | -21.4491 | -23.6902 | -25.1975
|  | BURFORD | CT |  |  | 0.88569 | 0.76704 | 0.66907 | 0.56092 | 0.4287 | 0.12494 | -0.40505 | -1.2007 | -2.144 | -3.0572 | -4.7625 | -8.5704 | -10.0217 | -10.4795 | 1.8275 | 1.6735 | 1.5242 | 1.3412 | 1.1005 | 0.71982 | 0.29681 | -0.35358 | -1.1206 | -1.86 | -3.2283 | -6.3203 | -7.451 | -7.8648 | 0.68248 | 0.43162 | 0.18167 | -0.093109 | -0.40233 | -0.88316 | -1.4166 | -2.2299 | -3.1922 | -4.119 | -5.8346 | -9.6941 | -11.1148 | -11.5453
|  | BURFORD | LW |  |  | 0.83158 | 0.65191 | 0.49653 | 0.31286 | -0.057267 | -0.844 | -1.9807 | -3.5189 | -5.4229 | -7.7977 | -13.843 | -23.569 | -25.9098 | -27.4896 | 1.8097 | 1.6167 | 1.4503 | 1.2608 | 0.9993 | 0.65972 | -0.047399 | -1.2501 | -2.7366 | -4.5935 | -9.3261 | -16.9214 | -18.7228 | -19.9457 | 0.66476 | 0.35872 | 0.097793 | -0.18401 | -0.57016 | -1 | -1.7491 | -2.7054 | -4.01 | -6.2932 | -12.1044 | -21.4491 | -23.6902 | -25.1975
|  | BURFORD | ST |  |  | 0.94745 | 0.87731 | 0.83824 | 0.78179 | 0.71147 | 0.6299 | 0.52475 | 0.36631 | -0.044922 | -0.55224 | -1.9348 | -6.3556 | -9.2415 | -9.8727 | 1.9088 | 1.83 | 1.7674 | 1.678 | 1.566 | 1.4267 | 1.2013 | 0.90819 | 0.57592 | 0.16002 | -0.98785 | -4.6645 | -6.9864 | -7.5389 | 0.8203 | 0.69812 | 0.59497 | 0.45068 | 0.26514 | 0.031986 | -0.27157 | -0.64014 | -1.0614 | -1.5851 | -3.0223 | -7.588 | -10.4466 | -11.0609
|  | BURFORD | FS |  |  | 0.88569 | 0.76704 | 0.66907 | 0.56092 | 0.4287 | 0.12494 | -0.40505 | -1.2007 | -2.144 | -3.0572 | -4.7625 | -8.5704 | -10.0217 | -10.4795 | 1.8876 | 1.7785 | 1.6874 | 1.5732 | 1.4075 | 1.1806 | 0.83682 | 0.40402 | -0.072071 | -0.62307 | -2.0006 | -6.0046 | -9.6406 | -11.2682 | 0.78327 | 0.60928 | 0.45921 | 0.26875 | 0.016817 | -0.27108 | -0.70267 | -1.2438 | -1.8446 | -2.5356 | -4.2578 | -9.2679 | -13.7609 | -15.7136
MANNINGTON GSP | WAREHAM | BUSHEY | MINIMUM HEADROOM | SY 97671 83532 | YES | 1.2234 | 0.74805 | 0.16759 | -0.4876 | -1.2102 | -2.38 | -3.6698 | -5.7512 | -8.106 | -10.7107 | -16.4981 | -25.955 | -28.5447 | -29.7503 | 1.5891 | 1.2034 | 0.73963 | 0.22003 | -0.35375 | -1.2871 | -2.3118 | -3.9449 | -5.8709 | -7.9351 | -12.587 | -20.1837 | -22.6977 | -28.0955 | 1.3364 | 0.86535 | 0.30389 | -0.32943 | -1.0282 | -2.1593 | -3.4103 | -5.4645 | -7.8176 | -10.4093 | -16.1748 | -25.5854 | -28.6517 | -35.2951
|  | BUSHEY | CT |  |  | 1.2234 | 0.74805 | 0.16759 | -0.4876 | -1.2102 | -2.38 | -3.6648 | -5.6904 | -8.106 | -10.4335 | -14.6888 | -24.3881 | -27.9325 | -29.1376 | 1.5891 | 1.2034 | 0.73963 | 0.22003 | -0.35375 | -1.2871 | -2.3118 | -3.934 | -5.8709 | -7.7409 | -11.1569 | -18.9531 | -21.8484 | -22.9295 | 1.3364 | 0.86535 | 0.30389 | -0.32943 | -1.0282 | -2.1593 | -3.4022 | -5.4131 | -7.8176 | -10.1367 | -14.3745 | -24.0416 | -27.606 | -28.8613
|  | BUSHEY | LW |  |  | 1.2768 | 0.75469 | 0.2356 | -0.3469 | -1.1702 | -2.0371 | -3.6698 | -5.7512 | -8.0783 | -10.7107 | -16.4981 | -25.955 | -28.5447 | -28.2902 | 1.6497 | 1.2305 | 0.81859 | 0.36021 | -0.29185 | -0.97774 | -2.281 | -3.9449 | -5.8172 | -7.9351 | -12.587 | -20.1837 | -22.3645 | -22.1422 | 1.3934 | 0.87676 | 0.36687 | -0.19658 | -0.9929 | -1.8318 | -3.4103 | -5.4645 | -7.785 | -10.4093 | -16.1748 | -25.5854 | -28.2044 | -27.4348
|  | BUSHEY | ST |  |  | 1.5205 | 1.3592 | 1.1397 | 0.83683 | 0.42893 | -0.12451 | -0.8474 | -1.7851 | -2.893 | -4.2824 | -8.0984 | -20.1729 | -27.893 | -29.7503 | 1.8323 | 1.7019 | 1.5235 | 1.279 | 0.95076 | 0.51105 | -0.067009 | -0.81649 | -1.7145 | -2.8372 | -5.9211 | -15.6739 | -22.0209 | -23.6723 | 1.6315 | 1.472 | 1.2546 | 0.95499 | 0.55706 | 0.023155 | -0.67432 | -1.5789 | -2.6546 | -4.0282 | -7.8385 | -19.8918 | -27.662 | -29.5999
|  | BUSHEY | FS |  |  | 1.2234 | 0.74805 | 0.16759 | -0.4876 | -1.2102 | -2.38 | -3.6648 | -5.6904 | -8.106 | -10.4335 | -14.6888 | -24.3881 | -27.9325 | -29.1376 | 1.8193 | 1.6955 | 1.5313 | 1.3127 | 1.0299 | 0.66455 | 0.19534 | -0.39677 | -1.0681 | -1.8751 | -4.1495 | -12.899 | -22.6977 | -28.0955 | 1.6184 | 1.4678 | 1.2692 | 0.99987 | 0.65537 | 0.21113 | -0.35934 | -1.0754 | -1.8895 | -2.8672 | -5.6593 | -16.5174 | -28.6517 | -35.2951
FAWLEY GSP | LANGLEY BSP | BUTTS ASH | MINIMUM HEADROOM | SU 41923 05772 | YES | 6.2643 | 5.9709 | 5.6816 | 4.6463 | 3.5416 | 2.2742 | 0.8732 | -0.49192 | -1.8739 | -3.3215 | -6.3498 | -21.2197 | -29.0004 | -29.4485 | 10.0649 | 9.9358 | 9.8095 | 9.0681 | 8.2534 | 7.2415 | 6.1222 | 5.0951 | 4.2716 | 3.3952 | 0.73957 | -11.5124 | -17.3274 | -17.7492 | 7.6296 | 7.3559 | 7.0863 | 6.0032 | 4.8392 | 3.4744 | 1.9873 | 0.57895 | -0.75443 | -2.154 | -6.4099 | -21.9602 | -29.4731 | -29.9931
|  | BUTTS ASH | CT |  |  | 6.7147 | 6.6606 | 6.6009 | 6.1449 | 5.6436 | 5.0981 | 4.4555 | 3.8554 | 2.7207 | 1.4755 | -1.022 | -8.2092 | -13.3788 | -16.015 | 10.215 | 10.1593 | 10.0959 | 9.8424 | 9.5322 | 9.1764 | 8.7003 | 8.2894 | 7.7124 | 7.0337 | 5.6901 | 1.7171 | -1.5403 | -4.4737 | 8.0446 | 7.9931 | 7.9366 | 7.4989 | 7.0064 | 6.4659 | 5.8069 | 5.2097 | 4.138 | 2.9689 | 0.66619 | -5.9212 | -10.5565 | -12.9235
|  | BUTTS ASH | LW |  |  | 6.2643 | 5.9709 | 5.6816 | 4.6463 | 3.5416 | 2.2742 | 0.8732 | -0.49192 | -1.8739 | -3.3215 | -6.3498 | -21.2197 | -29.0004 | -29.4485 | 10.0649 | 9.9358 | 9.8095 | 9.0681 | 8.2534 | 7.2415 | 6.1222 | 5.0951 | 4.2716 | 3.3952 | 0.73957 | -11.5124 | -17.3274 | -17.7492 | 7.6296 | 7.3559 | 7.0863 | 6.0032 | 4.8392 | 3.4744 | 1.9873 | 0.57895 | -0.75443 | -2.154 | -6.4099 | -21.9602 | -29.4731 | -29.9931
|  | BUTTS ASH | ST |  |  | 6.8123 | 6.8138 | 6.8044 | 6.4037 | 6.1164 | 5.839 | 5.429 | 5.1891 | 4.959 | 4.7268 | 4.1786 | 1.3791 | -2.007 | -6.2545 | 10.2594 | 10.2306 | 10.1917 | 9.6733 | 9.298 | 8.9389 | 8.4139 | 8.1079 | 7.8147 | 7.5227 | 6.8395 | 4.3144 | 1.5618 | -2.0203 | 8.1382 | 8.1402 | 8.1325 | 7.6397 | 7.2918 | 6.9613 | 6.469 | 6.1955 | 5.9411 | 5.6907 | 5.1037 | 2.3128 | -0.88758 | -4.7773
|  | BUTTS ASH | FS |  |  | 6.7147 | 6.6606 | 6.6009 | 6.1449 | 5.6436 | 5.0981 | 4.4555 | 3.8554 | 2.7207 | 1.4755 | -1.022 | -8.2092 | -13.3788 | -16.015 | 10.2336 | 10.1799 | 10.1135 | 9.9227 | 9.7128 | 9.4553 | 9.166 | 8.8598 | 8.4806 | 8.0512 | 7.0156 | 3.8178 | -0.15064 | -5.8271 | 8.1081 | 8.0854 | 8.0535 | 7.8574 | 7.6461 | 7.3843 | 7.0943 | 6.7846 | 6.3565 | 5.8838 | 4.7732 | 1.3025 | -2.0586 | -5.2854
MELKSHAM GSP | CHIPPENHAM | CALNE | MINIMUM HEADROOM | SU 00521 72497 | YES | -3.6147 | -4.3239 | -5.0206 | -5.9557 | -7.1213 | -8.3612 | -10.3436 | -12.7861 | -15.584 | -18.6633 | -25.2915 | -36.5873 | -42.7831 | -45.3034 | 3.1354 | 2.6563 | 2.1882 | 1.5998 | 0.82038 | -0.17107 | -1.4192 | -3.1628 | -5.3489 | -7.5167 | -12.0791 | -21.35 | -26.1747 | -35.5379 | -2.7585 | -3.383 | -3.9974 | -4.8431 | -5.9402 | -7.106 | -8.9287 | -11.288 | -13.9753 | -16.941 | -23.3332 | -34.1 | -39.8741 | -42.1003
|  | CALNE | CT |  |  | -3.3187 | -3.808 | -4.3829 | -5.2365 | -6.2172 | -7.661 | -9.2424 | -11.5282 | -14.5462 | -17.4891 | -23.0855 | -36.4789 | -42.7831 | -45.3034 | 3.1591 | 2.7376 | 2.2341 | 1.5998 | 0.89012 | -0.17107 | -1.3432 | -3.1224 | -5.3489 | -7.5167 | -11.6074 | -21.35 | -26.1747 | -29.8756 | -2.4805 | -2.9031 | -3.4247 | -4.2357 | -5.1302 | -6.4606 | -7.9859 | -10.2101 | -13.1171 | -15.9489 | -21.3163 | -34.067 | -39.8741 | -42.1003
|  | CALNE | LW |  |  | -3.6147 | -4.3239 | -5.0206 | -5.9557 | -7.1213 | -8.3612 | -10.3436 | -12.7861 | -15.584 | -18.6633 | -25.2915 | -36.5873 | -39.92 | -38.3734 | 3.1354 | 2.6563 | 2.1882 | 1.6017 | 0.82038 | -0.010979 | -1.4192 | -3.1628 | -5.1162 | -7.295 | -12.0791 | -19.8566 | -21.5711 | -19.882 | -2.7585 | -3.383 | -3.9974 | -4.8431 | -5.9402 | -7.106 | -8.9287 | -11.288 | -13.9753 | -16.941 | -23.3332 | -34.1 | -37.0848 | -35.3344
|  | CALNE | ST |  |  | -2.9316 | -3.09 | -3.2921 | -3.5994 | -4.0121 | -4.5391 | -5.2585 | -6.1967 | -7.2704 | -8.6034 | -12.2364 | -24.6994 | -33.4952 | -37.2863 | 3.4323 | 3.2752 | 3.0718 | 2.7831 | 2.4064 | 1.923 | 1.2991 | 0.52596 | -0.36666 | -1.5181 | -4.6693 | -15.1894 | -22.8971 | -27.1023 | -2.1398 | -2.2749 | -2.4472 | -2.7158 | -3.0731 | -3.5827 | -4.24 | -5.0933 | -6.1404 | -7.4453 | -11.0134 | -23.2863 | -31.9068 | -35.2369
|  | CALNE | FS |  |  | -3.3187 | -3.808 | -4.3829 | -5.2365 | -6.2172 | -7.661 | -9.2424 | -11.5282 | -14.5462 | -17.4891 | -23.0855 | -36.4789 | -42.7831 | -45.3034 | 3.3944 | 3.2087 | 2.9754 | 2.6661 | 2.2861 | 1.7888 | 1.1834 | 0.40157 | -0.54255 | -1.608 | -4.3194 | -14.2123 | -25.6412 | -35.5379 | -2.1656 | -2.3166 | -2.5061 | -2.8225 | -3.2113 | -3.7547 | -4.4101 | -5.2649 | -6.3733 | -7.6109 | -10.7281 | -21.787 | -33.3541 | -40.6103
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY | MINIMUM HEADROOM | SU 86584 59452 | YES | 57.1867 | 56.9218 | 56.6484 | 56.2786 | 55.2326 | 53.8436 | 51.625 | 48.9264 | 45.8775 | 42.4838 | 35.0557 | 21.8671 | 12.8419 | 10.1127 | 58.4916 | 58.2955 | 58.0108 | 57.2831 | 56.4749 | 55.27 | 53.9049 | 51.9106 | 49.4897 | 47.0147 | 41.7678 | 30.701 | 18.8707 | 4.3516 | 55.1419 | 54.4984 | 53.8604 | 52.8752 | 51.6478 | 50.3604 | 48.2922 | 45.6544 | 42.6938 | 39.3916 | 32.1562 | 19.4442 | 14.0015 | 5.6006
|  | CAMBERLEY | CT |  |  | 57.2342 | 57.0503 | 56.8366 | 56.5857 | 56.0639 | 54.5119 | 52.8091 | 50.3263 | 47.0487 | 43.8419 | 37.714 | 22.9251 | 16.2549 | 14.0139 | 58.5068 | 58.3424 | 58.0108 | 57.2831 | 56.4749 | 55.27 | 53.9329 | 51.9613 | 49.4897 | 47.0147 | 42.2646 | 30.701 | 24.6175 | 19.6415 | 55.3485 | 54.8782 | 54.3176 | 53.4425 | 52.4854 | 51.0049 | 49.3407 | 46.9015 | 43.7195 | 40.6079 | 34.6696 | 20.4261 | 14.1654 | 12.1413
|  | CAMBERLEY | LW |  |  | 57.1867 | 56.9218 | 56.6484 | 56.2786 | 55.2326 | 53.8436 | 51.625 | 48.9264 | 45.8775 | 42.4838 | 35.0557 | 21.8671 | 12.8419 | 10.1127 | 58.4916 | 58.2955 | 58.0522 | 57.377 | 56.477 | 55.5201 | 53.9049 | 51.9106 | 49.7098 | 47.2328 | 41.7678 | 32.382 | 27.0325 | 25.0144 | 55.1419 | 54.4984 | 53.8604 | 52.8752 | 51.6478 | 50.3604 | 48.2922 | 45.6544 | 42.6938 | 39.3916 | 32.1562 | 19.4442 | 14.4275 | 11.8567
|  | CAMBERLEY | ST |  |  | 57.3749 | 57.3148 | 57.2317 | 57.0743 | 56.8886 | 56.6547 | 56.3469 | 55.9735 | 54.7548 | 53.2137 | 48.7703 | 34.3367 | 24.8696 | 21.2853 | 58.619 | 58.5544 | 58.4686 | 58.3087 | 58.0803 | 57.4918 | 56.7221 | 55.776 | 54.6801 | 53.3128 | 49.4702 | 37.0856 | 28.1187 | 22.6381 | 55.7168 | 55.5788 | 55.3794 | 55.0513 | 54.6339 | 54.0851 | 53.3499 | 52.3124 | 51.1002 | 49.5674 | 45.2934 | 31.026 | 21.7915 | 18.4991
|  | CAMBERLEY | FS |  |  | 57.2342 | 57.0503 | 56.8366 | 56.5857 | 56.0639 | 54.5119 | 52.8091 | 50.3263 | 47.0487 | 43.8419 | 37.714 | 22.9251 | 16.2549 | 14.0139 | 58.5667 | 58.4587 | 58.315 | 58.1179 | 57.7895 | 57.1471 | 56.2868 | 55.2073 | 53.9136 | 52.3774 | 48.3463 | 34.6105 | 18.8707 | 4.3516 | 55.6189 | 55.423 | 55.1668 | 54.782 | 54.2789 | 53.6403 | 52.7756 | 51.6155 | 50.187 | 48.492 | 44.0324 | 29.1293 | 14.0015 | 5.6006
WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 25.069 | 25.0086 | 24.8487 | 24.6406 | 24.4248 | 24.1962 | 23.9764 | 23.7422 | 22.9432 | 21.606 | 19.7115 | 21.606 | 20.6125 | 19.7115 | 14.5579 | 14.4966 | 14.4153 | 14.3276 | 14.2409 | 14.145 | 14.037 | 13.9028 | 13.4306 | 12.3299 | 6.2551 | 12.3299 | 10.398 | 6.2551 | 17.8566 | 17.7696 | 17.6497 | 17.4815 | 17.2883 | 17.0831 | 16.8832 | 16.6682 | 15.9358 | 14.7678 | 13.3905 | 14.7678 | 14.0316 | 13.3905
|  | CANAL BANK 11kV | CT |  |  | 25.0692 | 25.0112 | 24.9468 | 24.8763 | 24.8011 | 24.7179 | 24.587 | 24.3873 | 23.7062 | 22.1406 | 19.7115 | 22.1406 | 20.7469 | 19.7115 | 14.5579 | 14.4966 | 14.4153 | 14.3276 | 14.2409 | 14.145 | 14.037 | 13.9028 | 13.4306 | 12.3299 | 8.9721 | 12.3299 | 11.0668 | 8.9721 | 17.9353 | 17.8697 | 17.7798 | 17.6834 | 17.5938 | 17.4958 | 17.3861 | 17.2407 | 16.6227 | 15.2628 | 13.3905 | 15.2628 | 14.1685 | 13.3905
|  | CANAL BANK 11kV | LW |  |  | 25.069 | 25.0086 | 24.8487 | 24.6406 | 24.4248 | 24.1962 | 23.9764 | 23.7422 | 22.9432 | 21.606 | 19.7619 | 21.606 | 20.6125 | 19.7619 | 14.5956 | 14.5409 | 14.4793 | 14.3959 | 14.3057 | 14.2079 | 14.1018 | 13.9863 | 13.8571 | 13.4102 | 12.3402 | 12.7358 | 12.3402 | 11.9912 | 17.8566 | 17.7696 | 17.6497 | 17.4815 | 17.2883 | 17.0831 | 16.8832 | 16.6682 | 15.9358 | 14.7678 | 13.4205 | 14.7678 | 14.0316 | 13.4205
|  | CANAL BANK 11kV | ST |  |  | 25.1426 | 25.1123 | 25.0746 | 25.0315 | 24.9839 | 24.9295 | 24.8606 | 24.7765 | 24.4304 | 23.4257 | 21.8409 | 23.4257 | 22.5557 | 21.8409 | 14.6313 | 14.5969 | 14.5508 | 14.4994 | 14.4421 | 14.3773 | 14.2992 | 14.2071 | 13.847 | 12.81 | 9.7613 | 12.81 | 11.6939 | 9.7613 | 18.0379 | 18.0095 | 17.9706 | 17.9266 | 17.8787 | 17.8244 | 17.7568 | 17.6725 | 17.3374 | 16.3875 | 15.1527 | 16.3875 | 15.6742 | 15.1527
|  | CANAL BANK 11kV | FS |  |  | 25.0692 | 25.0112 | 24.9468 | 24.8763 | 24.8011 | 24.7179 | 24.587 | 24.3873 | 23.7062 | 22.1406 | 19.7115 | 22.1406 | 20.7469 | 19.7115 | 14.636 | 14.6017 | 14.5501 | 14.4944 | 14.4322 | 14.3627 | 14.2825 | 14.1833 | 13.8113 | 12.7004 | 6.2551 | 12.7004 | 10.398 | 6.2551 | 18.0543 | 18.0312 | 17.9942 | 17.957 | 17.9172 | 17.8733 | 17.8235 | 17.7619 | 17.5413 | 16.8365 | 15.5325 | 16.8365 | 16.0461 | 15.5325
WILLESDEN GSP | ACTON LANE | CANAL BANK 6.6kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 10.967 | 34.8598 | 34.8495 | 34.8336 | 34.8167 | 34.7984 | 34.7793 | 34.758 | 34.6847 | 34.5697 | 34.4423 | 34.5697 | 34.5003 | 34.4423 | 11.4121 | 33.3062 | 33.2994 | 33.292 | 33.284 | 33.2751 | 33.2647 | 33.252 | 33.2073 | 33.1141 | 32.7152 | 33.1141 | 32.9705 | 32.7152 | 11.1037 | 32.9973 | 32.9898 | 32.9814 | 32.9715 | 32.9605 | 32.9465 | 32.93 | 32.8718 | 32.7879 | 32.7133 | 32.7879 | 32.7471 | 32.7133
|  | CANAL BANK 6.6kV | CT |  |  | 10.9672 | 34.8604 | 34.8528 | 34.8445 | 34.8356 | 34.8257 | 34.8143 | 34.8004 | 34.7408 | 34.6119 | 34.4451 | 34.6119 | 34.5157 | 34.4451 | 11.4121 | 33.3062 | 33.2994 | 33.292 | 33.284 | 33.2751 | 33.2647 | 33.252 | 33.2073 | 33.1141 | 32.868 | 33.1141 | 33.0058 | 32.868 | 11.1037 | 32.9975 | 32.9907 | 32.9832 | 32.9751 | 32.9661 | 32.9556 | 32.943 | 32.8979 | 32.8105 | 32.7234 | 32.8105 | 32.7614 | 32.7234
|  | CANAL BANK 6.6kV | LW |  |  | 10.967 | 34.8598 | 34.8495 | 34.8336 | 34.8167 | 34.7984 | 34.7793 | 34.758 | 34.6847 | 34.5697 | 34.4423 | 34.5697 | 34.5003 | 34.4423 | 11.4178 | 33.3129 | 33.307 | 33.3001 | 33.2922 | 33.283 | 33.2726 | 33.2594 | 33.2438 | 33.1891 | 33.0836 | 33.1145 | 33.0836 | 33.0588 | 11.1037 | 32.9973 | 32.9898 | 32.9814 | 32.9715 | 32.9605 | 32.9465 | 32.93 | 32.8718 | 32.7879 | 32.7133 | 32.7879 | 32.7471 | 32.7133
|  | CANAL BANK 6.6kV | ST |  |  | 10.976 | 34.8726 | 34.8682 | 34.8632 | 34.8577 | 34.8513 | 34.8432 | 34.8333 | 34.7923 | 34.675 | 34.548 | 34.675 | 34.5941 | 34.548 | 11.42 | 33.317 | 33.3131 | 33.3086 | 33.3035 | 33.2976 | 33.2901 | 33.2808 | 33.2432 | 33.138 | 32.9073 | 33.138 | 33.0395 | 32.9073 | 11.1118 | 33.0087 | 33.0048 | 33.0003 | 32.9953 | 32.9895 | 32.9821 | 32.973 | 32.9355 | 32.8289 | 32.7179 | 32.8289 | 32.7572 | 32.7179
|  | CANAL BANK 6.6kV | FS |  |  | 10.9672 | 34.8604 | 34.8528 | 34.8445 | 34.8356 | 34.8257 | 34.8143 | 34.8004 | 34.7408 | 34.6119 | 34.4451 | 34.6119 | 34.5157 | 34.4451 | 11.421 | 33.3183 | 33.3148 | 33.3112 | 33.307 | 33.3024 | 33.2968 | 33.2902 | 33.2608 | 33.1483 | 32.7152 | 33.1483 | 32.9705 | 32.7152 | 11.1131 | 33.0104 | 33.0072 | 33.0039 | 33.0002 | 32.996 | 32.9911 | 32.9854 | 32.964 | 32.8879 | 32.7611 | 32.8879 | 32.8038 | 32.7611
COWLEY GSP | WITNEY BSP | CARTERTON | MINIMUM HEADROOM | SP 28261 07823 | NO | 11.7683 | 11.5326 | 11.2952 | 10.9573 | 10.551 | 10.3359 | 10.1462 | 9.9545 | 9.7567 | 9.544 | 8.9694 | 7.7059 | 6.9635 | 6.402 | 11.7341 | 11.6172 | 11.499 | 11.3118 | 11.0894 | 10.9421 | 10.7963 | 10.6519 | 10.5196 | 10.3731 | 9.5313 | 3.2453 | 0.0096604 | 0.05206 | 11.4027 | 11.2238 | 11.0424 | 10.7593 | 10.418 | 10.213 | 10.0223 | 9.8313 | 9.6425 | 9.4383 | 8.9076 | 1.4845 | -2.4973 | -2.4775
|  | CARTERTON | CT |  |  | 11.8268 | 11.6456 | 11.4565 | 11.2147 | 10.9054 | 10.774 | 10.6357 | 10.4822 | 10.261 | 10.0431 | 9.6176 | 8.3198 | 7.3753 | 6.7711 | 11.7435 | 11.6383 | 11.5272 | 11.3944 | 11.2274 | 11.1369 | 11.0336 | 10.9238 | 10.7861 | 10.6379 | 10.3231 | 9.2961 | 8.3583 | 7.2513 | 11.4528 | 11.3176 | 11.1754 | 10.9843 | 10.7368 | 10.6226 | 10.4972 | 10.3608 | 10.1672 | 9.9723 | 9.5858 | 8.4197 | 7.6173 | 7.1377
|  | CARTERTON | LW |  |  | 11.7683 | 11.5326 | 11.2952 | 10.9573 | 10.551 | 10.3359 | 10.1462 | 9.9545 | 9.7567 | 9.544 | 8.9694 | 7.7059 | 6.9635 | 6.402 | 11.7341 | 11.6172 | 11.499 | 11.3118 | 11.0894 | 10.9421 | 10.7963 | 10.6519 | 10.5196 | 10.3731 | 10.0031 | 9.2653 | 8.9489 | 8.7316 | 11.4027 | 11.2238 | 11.0424 | 10.7593 | 10.418 | 10.213 | 10.0223 | 9.8313 | 9.6425 | 9.4383 | 8.9076 | 7.7715 | 7.1607 | 6.7214
|  | CARTERTON | ST |  |  | 11.8467 | 11.6808 | 11.5047 | 11.2931 | 11.059 | 10.9724 | 10.8799 | 10.7896 | 10.6919 | 10.5925 | 10.395 | 9.7865 | 9.2691 | 8.6769 | 11.7523 | 11.6534 | 11.5476 | 11.3981 | 11.2428 | 11.1579 | 11.057 | 10.9662 | 10.8675 | 10.7627 | 10.5307 | 9.8312 | 9.0749 | 7.9356 | 11.4707 | 11.3492 | 11.2186 | 11.0428 | 10.8555 | 10.7765 | 10.6859 | 10.6037 | 10.5168 | 10.4269 | 10.2414 | 9.6983 | 9.2768 | 8.8004
|  | CARTERTON | FS |  |  | 11.8268 | 11.6456 | 11.4565 | 11.2147 | 10.9054 | 10.774 | 10.6357 | 10.4822 | 10.261 | 10.0431 | 9.6176 | 8.3198 | 7.3753 | 6.7711 | 11.751 | 11.6487 | 11.5371 | 11.4096 | 11.2603 | 11.1549 | 11.0422 | 10.9091 | 10.7473 | 10.5563 | 9.5313 | 3.2453 | 0.0096604 | 0.05206 | 11.4747 | 11.3597 | 11.2352 | 11.0828 | 10.9044 | 10.7903 | 10.6732 | 10.5331 | 10.3689 | 10.1751 | 9.1897 | 1.4845 | -2.4973 | -2.4775
AXMINSTER | YEOVIL BSP | CASTLE CARY | MINIMUM HEADROOM | ST 64534 31039 | YES | 5.3817 | 4.9777 | 4.582 | 4.1649 | 3.5509 | 2.9229 | 1.8782 | 0.58812 | -0.76337 | -2.2764 | -5.543 | -11.2369 | -13.8047 | -14.7395 | 7.1427 | 6.878 | 6.624 | 6.3611 | 5.978 | 5.5357 | 4.9092 | 4.0625 | 2.8546 | 1.6557 | -0.72856 | -5.4632 | -7.4676 | -9.4382 | 5.9328 | 5.5474 | 5.172 | 4.773 | 4.188 | 3.5394 | 2.5501 | 1.2548 | -0.19762 | -1.7155 | -4.9545 | -10.7338 | -13.2519 | -14.9348
|  | CASTLE CARY | CT |  |  | 5.4491 | 5.1457 | 4.7885 | 4.3527 | 3.8095 | 3.0046 | 2.115 | 0.80907 | -0.73685 | -2.2492 | -4.9866 | -11.2369 | -13.8047 | -14.7395 | 7.1582 | 6.9532 | 6.7095 | 6.4212 | 6.0695 | 5.5357 | 4.9393 | 4.0634 | 2.8546 | 1.6557 | -0.5111 | -5.4632 | -7.4676 | -8.3838 | 5.9611 | 5.6557 | 5.2931 | 4.8605 | 4.335 | 3.5394 | 2.659 | 1.3525 | -0.19762 | -1.7155 | -4.4623 | -10.7338 | -13.2519 | -14.1764
|  | CASTLE CARY | LW |  |  | 5.3817 | 4.9777 | 4.582 | 4.1649 | 3.5509 | 2.9229 | 1.8782 | 0.58812 | -0.76337 | -2.2764 | -5.543 | -10.8118 | -12.0772 | -10.8432 | 7.1427 | 6.878 | 6.624 | 6.3611 | 5.978 | 5.5879 | 4.9092 | 4.0625 | 3.071 | 1.8704 | -0.72856 | -4.8202 | -5.7736 | -4.8141 | 5.9328 | 5.5474 | 5.172 | 4.773 | 4.188 | 3.5889 | 2.5501 | 1.2548 | -0.12487 | -1.6533 | -4.9545 | -10.2313 | -11.4866 | -10.2516
|  | CASTLE CARY | ST |  |  | 5.6495 | 5.5416 | 5.3958 | 5.1734 | 4.8508 | 4.447 | 3.9411 | 3.3283 | 2.6318 | 1.7792 | -0.48522 | -7.7219 | -12.6143 | -14.191 | 7.289 | 7.2145 | 7.1145 | 6.9481 | 6.7253 | 6.4453 | 6.0833 | 5.6577 | 5.1597 | 4.5581 | 2.8037 | -3.2025 | -7.305 | -8.6989 | 6.1619 | 6.0564 | 5.9131 | 5.6855 | 5.3694 | 4.9704 | 4.4607 | 3.8467 | 3.139 | 2.2727 | -0.040119 | -7.4359 | -12.4293 | -13.9944
|  | CASTLE CARY | FS |  |  | 5.4491 | 5.1457 | 4.7885 | 4.3527 | 3.8095 | 3.0046 | 2.115 | 0.80907 | -0.73685 | -2.2492 | -4.9866 | -11.2369 | -13.8047 | -14.7395 | 7.3265 | 7.232 | 7.1216 | 6.9824 | 6.7844 | 6.5423 | 6.2431 | 5.8761 | 5.4682 | 4.9889 | 3.7368 | -0.88199 | -6.1805 | -9.4382 | 6.206 | 6.091 | 5.9511 | 5.7633 | 5.4927 | 5.1638 | 4.7589 | 4.2621 | 3.7138 | 3.0719 | 1.3662 | -4.6709 | -11.1581 | -14.9348
LALEHAM | STAINES | CAUSEWAY | MINIMUM HEADROOM | TQ 02763 71680 | YES | 25.3348 | 24.6564 | 24.2255 | 23.4824 | 22.4263 | 21.1263 | 19.3836 | 16.4925 | 12.6611 | 8.12 | -2.4863 | -21.0083 | -26.2654 | -29.6912 | 28.1184 | 27.887 | 27.6662 | 27.3008 | 26.7633 | 25.928 | 24.1304 | 21.8323 | 18.9425 | 15.4993 | 7.4277 | -6.4156 | -10.0806 | -12.5786 | 25.8431 | 25.3764 | 25.0788 | 24.46 | 23.6256 | 22.1909 | 19.9123 | 17.059 | 13.4006 | 9.0628 | -1.0752 | -18.7302 | -23.6779 | -26.9113
|  | CAUSEWAY | CT |  |  | 25.5345 | 25.0373 | 24.672 | 24.0401 | 23.1524 | 21.6606 | 19.4587 | 16.4925 | 12.6611 | 8.12 | -2.4863 | -21.0083 | -26.2654 | -29.6912 | 28.1184 | 27.887 | 27.6662 | 27.3008 | 26.7633 | 25.928 | 24.1304 | 21.8323 | 18.9425 | 15.4993 | 7.4277 | -6.4156 | -10.0806 | -12.5786 | 26.0279 | 25.704 | 25.415 | 24.8743 | 23.926 | 22.1909 | 19.9123 | 17.059 | 13.4006 | 9.0628 | -1.0752 | -18.7302 | -23.6779 | -26.9113
|  | CAUSEWAY | LW |  |  | 25.3348 | 24.6564 | 24.2255 | 23.4824 | 22.4263 | 21.1263 | 19.3836 | 17.8178 | 16.0633 | 14.1405 | 9.9922 | 2.6255 | 0.45885 | -0.25707 | 28.1489 | 27.9084 | 27.767 | 27.5122 | 27.1158 | 26.5969 | 25.8737 | 24.9381 | 23.787 | 22.3719 | 19.1156 | 13.5579 | 11.1684 | 9.998 | 25.8431 | 25.3764 | 25.0788 | 24.46 | 23.6256 | 22.5902 | 21.2703 | 20.1227 | 18.8561 | 17.3084 | 13.0532 | 5.8211 | 2.6246 | 1.1254
|  | CAUSEWAY | ST |  |  | 25.7921 | 25.5091 | 25.391 | 25.1242 | 24.6956 | 24.0747 | 23.3195 | 22.7106 | 22.0305 | 21.1696 | 18.9152 | 11.0684 | 6.0481 | 3.85 | 28.2505 | 28.1415 | 28.0783 | 27.8823 | 27.6594 | 27.3669 | 26.9866 | 26.6826 | 26.3843 | 25.9895 | 23.8251 | 16.7304 | 11.565 | 7.6866 | 26.2391 | 26.0794 | 26.0302 | 25.8335 | 25.5544 | 25.1451 | 24.6344 | 24.2608 | 23.8742 | 23.3896 | 21.0717 | 13.1244 | 8.2334 | 6.3758
|  | CAUSEWAY | FS |  |  | 25.5345 | 25.0373 | 24.672 | 24.0401 | 23.1524 | 21.6606 | 19.4587 | 16.4925 | 12.6611 | 8.12 | -2.4863 | -21.0083 | -26.2654 | -29.6912 | 28.2493 | 28.1006 | 27.9981 | 27.851 | 27.6235 | 27.3204 | 26.934 | 26.4789 | 25.9446 | 25.1179 | 22.2623 | 13.7316 | 7.5567 | -0.084308 | 26.2355 | 26.0631 | 25.9782 | 25.8231 | 25.539 | 25.066 | 24.4673 | 23.8091 | 22.8634 | 21.5247 | 17.9048 | 7.2905 | -0.51685 | -4.4436
BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM | MINIMUM HEADROOM | SU 71512 75747 | YES | 15.3228 | 14.6867 | 14.0555 | 13.0329 | 11.7961 | 10.4585 | 8.4128 | 5.9625 | 3.2271 | 0.20245 | -6.3392 | -17.8101 | -29.1352 | -34.0548 | 16.6883 | 16.2762 | 15.7803 | 15.1261 | 14.4112 | 13.2941 | 12.0731 | 10.3007 | 8.1747 | 6.0648 | 1.4989 | -8.8325 | -15.7605 | -25.5116 | 14.1769 | 13.5683 | 12.9645 | 12.0108 | 10.8437 | 9.5658 | 7.571 | 5.1774 | 2.5249 | -0.41329 | -6.7746 | -17.7955 | -25.9142 | -30.636
|  | CAVERSHAM | CT |  |  | 15.5409 | 15.0883 | 14.5415 | 13.6336 | 12.6463 | 11.1937 | 9.6226 | 7.3954 | 4.5361 | 1.7118 | -3.7533 | -17.8101 | -29.1352 | -34.0548 | 16.6883 | 16.2763 | 15.7803 | 15.1261 | 14.4112 | 13.2941 | 12.0731 | 10.3007 | 8.1747 | 6.0648 | 1.9694 | -8.8325 | -15.7605 | -21.5037 | 14.3723 | 13.9352 | 13.3955 | 12.5217 | 11.5755 | 10.1558 | 8.619 | 6.4298 | 3.6686 | 0.94047 | -4.3263 | -17.7955 | -25.9142 | -30.636
|  | CAVERSHAM | LW |  |  | 15.3228 | 14.6867 | 14.0555 | 13.0329 | 11.7961 | 10.4585 | 8.4128 | 5.9625 | 3.2271 | 0.20245 | -6.3392 | -17.7964 | -21.0623 | -19.645 | 16.7091 | 16.2762 | 15.8479 | 15.2625 | 14.4998 | 13.6498 | 12.202 | 10.4259 | 8.4685 | 6.276 | 1.4989 | -6.4475 | -8.4768 | -7.2157 | 14.1769 | 13.5683 | 12.9645 | 12.0108 | 10.8437 | 9.5658 | 7.571 | 5.1774 | 2.5249 | -0.41329 | -6.7746 | -17.7756 | -20.8607 | -19.4525
|  | CAVERSHAM | ST |  |  | 15.8945 | 15.759 | 15.5736 | 15.3191 | 14.9685 | 14.4338 | 13.7492 | 12.8825 | 11.9036 | 10.6751 | 7.2592 | -4.9576 | -13.8463 | -17.3645 | 16.9391 | 16.7683 | 16.5472 | 16.2723 | 15.9133 | 15.3793 | 14.7132 | 13.8885 | 12.9736 | 11.8444 | 8.7616 | -1.853 | -10.5213 | -16.5331 | 14.7172 | 14.5882 | 14.4044 | 14.1506 | 13.8014 | 13.2474 | 12.5435 | 11.6576 | 10.6772 | 9.4487 | 6.0354 | -5.9135 | -14.5374 | -17.9855
|  | CAVERSHAM | FS |  |  | 15.5409 | 15.0883 | 14.5415 | 13.6336 | 12.6463 | 11.1937 | 9.6226 | 7.3954 | 4.5361 | 1.7118 | -3.7533 | -17.8101 | -29.1352 | -34.0548 | 16.8886 | 16.6693 | 16.405 | 16.098 | 15.7157 | 15.2127 | 14.5654 | 13.7408 | 12.7625 | 11.656 | 8.8683 | -0.99258 | -13.1564 | -25.5116 | 14.6575 | 14.4848 | 14.2669 | 13.957 | 13.566 | 13.0371 | 12.3494 | 11.4574 | 10.4127 | 9.2393 | 6.2914 | -3.9325 | -14.9755 | -21.8068
MANNINGTON GSP | BOURNEMOUTH | CENTRAL | MINIMUM HEADROOM | SZ 10293 91931 | YES | 3.651 | 3.1445 | 2.6197 | 1.7443 | 0.76791 | -0.24162 | -1.4531 | -2.7808 | -4.2539 | -5.7536 | -8.8428 | -18.8397 | -23.3365 | -26.4151 | 9.1471 | 8.7841 | 8.3626 | 7.7599 | 7.0799 | 6.2359 | 5.2956 | 4.1304 | 2.6501 | 1.0888 | -2.2355 | -11.7717 | -28.9419 | -63.8519 | 4.1932 | 3.7431 | 3.281 | 2.527 | 1.6748 | 0.79137 | -0.31308 | -1.5425 | -2.9098 | -4.3224 | -8.0222 | -18.7004 | -22.8642 | -25.7603
|  | CENTRAL | CT |  |  | 4.0631 | 3.756 | 3.4042 | 2.6832 | 1.8859 | 0.91764 | -0.12506 | -1.4132 | -3.1709 | -4.9405 | -8.4764 | -18.8397 | -23.3365 | -26.4151 | 9.1471 | 8.7841 | 8.3626 | 7.7599 | 7.0799 | 6.2359 | 5.2956 | 4.1304 | 2.6501 | 1.0888 | -2.2355 | -11.7717 | -23.1551 | -40.5031 | 4.5236 | 4.242 | 3.9189 | 3.2789 | 2.5737 | 1.6946 | 0.74198 | -0.46669 | -2.0919 | -3.7308 | -8.0222 | -18.7004 | -22.8642 | -25.7603
|  | CENTRAL | LW |  |  | 3.651 | 3.1445 | 2.6197 | 1.7443 | 0.76791 | -0.24162 | -1.4531 | -2.7808 | -4.2539 | -5.7536 | -8.8428 | -15.1273 | -18.7907 | -20.1387 | 9.1695 | 8.9013 | 8.6229 | 8.2023 | 7.7165 | 7.2088 | 6.5424 | 5.7913 | 4.9489 | 4.0655 | 2.215 | -1.3993 | -4.3526 | -7.4275 | 4.1932 | 3.7431 | 3.281 | 2.527 | 1.6748 | 0.79137 | -0.31308 | -1.5425 | -2.9098 | -4.3224 | -7.253 | -13.0338 | -16.3453 | -19.8183
|  | CENTRAL | ST |  |  | 4.5252 | 4.4957 | 4.4341 | 4.3491 | 4.218 | 4.0418 | 3.8133 | 3.5348 | 3.1604 | 2.7273 | 1.5911 | -2.9094 | -6.6732 | -10.6392 | 9.3693 | 9.1592 | 8.9023 | 8.5863 | 8.2148 | 7.776 | 7.2601 | 6.6764 | 5.9522 | 5.1312 | 3.0948 | -4.6721 | -15.9467 | -33.835 | 4.9312 | 4.9053 | 4.8477 | 4.7587 | 4.6304 | 4.4589 | 4.233 | 3.9583 | 3.5905 | 3.1591 | 2.0144 | -2.3855 | -6.0315 | -9.5343
|  | CENTRAL | FS |  |  | 4.0631 | 3.756 | 3.4042 | 2.6832 | 1.8859 | 0.91764 | -0.12506 | -1.4132 | -3.1709 | -4.9405 | -8.4764 | -18.8397 | -23.3365 | -26.4151 | 9.3334 | 9.0896 | 8.7925 | 8.337 | 7.8123 | 7.2166 | 6.5264 | 5.7388 | 4.7801 | 3.7001 | 1.033 | -9.5797 | -28.9419 | -63.8519 | 4.8796 | 4.8552 | 4.8049 | 4.618 | 4.4005 | 4.1525 | 3.8738 | 3.5483 | 3.1708 | 2.7677 | 1.7767 | -2.103 | -6.8189 | -11.0423
NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE | MINIMUM HEADROOM | SU 42591 11255 | YES | 20.4731 | 19.2486 | 18.3989 | 17.7213 | 17.0538 | 16.2345 | 15.0891 | 13.043 | 11.5253 | 9.9564 | 6.847 | -0.72603 | -3.0998 | -4.8228 | 24.5675 | 24.0023 | 23.37 | 22.6661 | 21.9974 | 20.9824 | 19.9125 | 17.9965 | 16.3829 | 14.7681 | 11.5289 | 1.4964 | -18.6146 | -51.9757 | 19.6681 | 18.651 | 17.9125 | 17.2913 | 16.6654 | 15.889 | 14.817 | 12.8431 | 11.4169 | 9.9287 | 6.9187 | -1.1312 | -3.456 | -5.1686
|  | CENTRAL BRIDGE | CT |  |  | 20.5126 | 19.4248 | 18.6161 | 17.9774 | 17.4082 | 16.4282 | 15.3843 | 13.3905 | 11.7404 | 10.1712 | 7.3486 | -0.72603 | -3.0998 | -4.8228 | 24.5675 | 24.0023 | 23.37 | 22.6661 | 21.9974 | 20.9824 | 19.9125 | 17.9965 | 16.3829 | 14.7681 | 11.5289 | 2.604 | -7.58 | -23.6214 | 19.6992 | 18.7882 | 18.0764 | 17.4842 | 16.9539 | 16.0218 | 15.0516 | 13.1113 | 11.5668 | 10.0869 | 7.1122 | -1.1312 | -3.456 | -5.1686
|  | CENTRAL BRIDGE | LW |  |  | 20.4731 | 19.2486 | 18.3989 | 17.7213 | 17.0538 | 16.2345 | 15.0891 | 13.043 | 11.5253 | 9.9564 | 6.847 | 2.2988 | 0.7896 | -0.58142 | 24.632 | 24.14 | 23.7489 | 23.3787 | 22.9127 | 22.3348 | 21.5283 | 19.9917 | 18.8915 | 17.7436 | 14.5243 | 9.296 | 7.7745 | 6.5002 | 19.6681 | 18.651 | 17.9125 | 17.2913 | 16.6654 | 15.889 | 14.817 | 12.8431 | 11.4169 | 9.9287 | 6.9187 | 2.0202 | 0.20295 | -1.2416
|  | CENTRAL BRIDGE | ST |  |  | 20.806 | 19.935 | 19.37 | 19.0038 | 18.7202 | 18.2173 | 17.6778 | 16.5858 | 15.8623 | 15.0941 | 13.2503 | 8.1622 | 5.1229 | 4.0321 | 24.6431 | 24.1474 | 23.7443 | 23.3187 | 22.8278 | 22.1277 | 21.3851 | 20.0463 | 19.0627 | 17.9963 | 15.3981 | 6.6304 | -4.5667 | -20.799 | 19.9872 | 19.2888 | 18.8163 | 18.4902 | 18.242 | 17.7809 | 17.3114 | 16.23 | 15.5725 | 14.8657 | 13.1205 | 8.0562 | 4.8328 | 3.6844
|  | CENTRAL BRIDGE | FS |  |  | 20.5126 | 19.4248 | 18.6161 | 17.9774 | 17.4082 | 16.4282 | 15.3843 | 13.3905 | 11.7404 | 10.1712 | 7.3486 | -0.72603 | -3.0998 | -4.8228 | 24.6984 | 24.2928 | 23.9473 | 23.2775 | 22.5756 | 21.7213 | 20.7618 | 19.4243 | 18.2287 | 16.8911 | 13.6592 | 1.4964 | -18.6146 | -51.9757 | 20.0659 | 19.5153 | 19.1325 | 18.7858 | 18.4685 | 18.0278 | 17.5601 | 16.7344 | 16.1152 | 15.4403 | 13.8463 | 8.3055 | 2.4789 | -0.76166
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS | MINIMUM HEADROOM | ST 66140 01039 | YES | 0.3098 | 0.25377 | 0.19546 | 0.13365 | 0.047297 | -0.095911 | -0.37433 | -0.75063 | -1.2334 | -1.8622 | -3.6873 | -10.3055 | -15.1228 | -18.9231 | 0.63863 | 0.60368 | 0.55202 | 0.46266 | 0.33303 | 0.077379 | -0.36656 | -0.97976 | -1.7699 | -2.7504 | -5.0812 | -9.2922 | -11.2697 | -14.2453 | 0.36349 | 0.30008 | 0.22354 | 0.075048 | -0.18862 | -0.57332 | -1.1203 | -1.8732 | -2.8437 | -4.0459 | -6.9024 | -12.079 | -14.5569 | -18.2036
|  | CERNE ABBAS | CT |  |  | 0.31543 | 0.26594 | 0.20819 | 0.13365 | 0.047297 | -0.073248 | -0.21321 | -0.48866 | -0.82869 | -1.2523 | -2.4791 | -8.0179 | -15.1228 | -18.9231 | 0.64203 | 0.61283 | 0.57719 | 0.52914 | 0.46889 | 0.38995 | 0.29004 | 0.12436 | -0.11108 | -0.43664 | -1.3867 | -5.7135 | -11.2697 | -14.2453 | 0.37413 | 0.32291 | 0.26179 | 0.17873 | 0.075775 | -0.057696 | -0.24995 | -0.5149 | -0.84055 | -1.2465 | -2.423 | -7.7391 | -14.5569 | -18.2036
|  | CERNE ABBAS | LW |  |  | 0.3098 | 0.25377 | 0.19546 | 0.14008 | 0.065264 | -0.095911 | -0.37433 | -0.75063 | -1.2334 | -1.8622 | -3.6873 | -10.3055 | -13.5285 | -13.1967 | 0.63863 | 0.60368 | 0.5606 | 0.50937 | 0.43844 | 0.34419 | 0.19908 | -0.042805 | -0.41582 | -0.90327 | -2.325 | -7.5004 | -10.015 | -9.7454 | 0.36349 | 0.30008 | 0.22354 | 0.13587 | 0.015653 | -0.14302 | -0.40248 | -0.76279 | -1.2253 | -1.8281 | -3.579 | -9.9306 | -13.0216 | -12.6996
|  | CERNE ABBAS | ST |  |  | 0.36109 | 0.34346 | 0.32365 | 0.29575 | 0.26199 | 0.21936 | 0.16927 | 0.1059 | 0.035177 | -0.050512 | -0.2747 | -0.9629 | -1.3795 | -1.4873 | 0.68198 | 0.67671 | 0.67142 | 0.66377 | 0.65516 | 0.64486 | 0.63407 | 0.62082 | 0.60703 | 0.59128 | 0.55411 | 0.035497 | -0.2998 | -0.39775 | 0.44206 | 0.43096 | 0.42038 | 0.40512 | 0.389 | 0.36944 | 0.34949 | 0.30886 | 0.24148 | 0.15954 | -0.055377 | -0.71765 | -1.1179 | -1.2201
|  | CERNE ABBAS | FS |  |  | 0.31543 | 0.26594 | 0.20819 | 0.13365 | 0.047297 | -0.073248 | -0.21321 | -0.48866 | -0.82869 | -1.2523 | -2.4791 | -8.0179 | -15.1228 | -18.9231 | 0.64854 | 0.60872 | 0.55202 | 0.46266 | 0.33303 | 0.077379 | -0.36656 | -0.97976 | -1.7699 | -2.7504 | -5.0812 | -9.2922 | -10.4531 | -11.2648 | 0.38794 | 0.32004 | 0.22546 | 0.075048 | -0.18862 | -0.57332 | -1.1203 | -1.8732 | -2.8437 | -4.0459 | -6.9024 | -12.079 | -13.5131 | -14.5148
IVER 132KV | CHALVEY BSP | CHALVEY | MINIMUM HEADROOM | SU 96669 79364 | YES | 38.3516 | 36.9576 | 35.5724 | 33.3739 | 31.1946 | 28.2262 | 24.4541 | 20.8243 | 16.0613 | 8.7744 | -8.0757 | -40.3437 | -56.5321 | -65.7406 | 44.6606 | 43.9856 | 43.3377 | 42.3218 | 41.258 | 39.0462 | 35.5328 | 30.763 | 25.7679 | 20.1465 | 7.1972 | -17.4587 | -29.7948 | -76.2559 | 35.623 | 34.4638 | 33.3146 | 31.39 | 29.4811 | 26.5415 | 22.7814 | 17.7874 | 11.5117 | 4.4519 | -11.7978 | -42.8906 | -58.4319 | -67.27
|  | CHALVEY | CT |  |  | 39.1237 | 38.4159 | 37.6604 | 36.0949 | 34.6403 | 32.3444 | 29.3341 | 26.5216 | 23.4011 | 20.6181 | 15.6398 | 2.1991 | -5.5982 | -7.0344 | 44.7465 | 44.1593 | 43.5123 | 42.4476 | 41.4686 | 39.4113 | 36.6519 | 34.1603 | 31.5205 | 29.0412 | 24.33 | 10.6088 | -6.2317 | -32.0121 | 36.2879 | 35.737 | 35.1416 | 33.8426 | 32.6401 | 30.3968 | 27.4216 | 24.7107 | 21.7738 | 19.1386 | 14.4578 | -1.6937 | -9.0081 | -10.2823
|  | CHALVEY | LW |  |  | 38.3516 | 36.9576 | 35.5724 | 33.3739 | 31.1946 | 28.2262 | 24.4541 | 20.8243 | 16.0613 | 8.7744 | -8.0757 | -40.3437 | -56.5321 | -65.7406 | 44.6606 | 43.9856 | 43.3377 | 42.3218 | 41.258 | 39.0462 | 35.5328 | 30.763 | 25.7679 | 20.1465 | 7.1972 | -17.4587 | -29.7948 | -36.948 | 35.623 | 34.4638 | 33.3146 | 31.39 | 29.4811 | 26.5415 | 22.7814 | 17.7874 | 11.5117 | 4.4519 | -11.7978 | -42.8906 | -58.4319 | -67.27
|  | CHALVEY | ST |  |  | 39.4879 | 38.981 | 38.4321 | 37.633 | 37.0475 | 35.8248 | 33.9859 | 32.46 | 31.2539 | 30.2776 | 28.742 | 24.4926 | 20.672 | 16.0585 | 44.8993 | 44.4038 | 43.8532 | 42.9604 | 42.2233 | 40.5855 | 38.2905 | 36.2953 | 34.5482 | 32.9089 | 29.7622 | 19.614 | 3.7978 | -22.6564 | 36.6109 | 36.2369 | 35.8286 | 35.1524 | 34.6739 | 33.3717 | 31.4562 | 29.8926 | 28.6722 | 27.6633 | 26.0648 | 20.1283 | 17.1904 | 14.2875
|  | CHALVEY | FS |  |  | 39.1237 | 38.4159 | 37.6604 | 36.0949 | 34.6403 | 32.3444 | 29.3341 | 26.5216 | 23.4011 | 20.6181 | 15.6398 | 2.1991 | -5.5982 | -7.0344 | 44.9857 | 44.3507 | 43.6799 | 42.7732 | 41.8196 | 40.0104 | 37.8024 | 35.5146 | 33.194 | 30.7944 | 25.2574 | 7.7591 | -22.1236 | -76.2559 | 36.7301 | 36.3022 | 35.8783 | 35.2942 | 34.7159 | 33.3543 | 31.6767 | 29.9627 | 27.5615 | 24.6176 | 16.9913 | -4.2126 | -19.3032 | -27.2306
NURSLING GSP | VELMORE BSP | CHANDLERSFORD | MINIMUM HEADROOM | SU 43494 21552 | YES | 13.6829 | 13.2421 | 12.771 | 11.9467 | 10.9572 | 9.9552 | 8.6541 | 7.0438 | 5.1623 | 3.1135 | -1.2934 | -12.464 | -19.6911 | -19.6564 | 16.7346 | 16.4679 | 16.1866 | 15.7633 | 15.2338 | 14.6906 | 13.3407 | 9.9913 | 5.7246 | 0.38101 | -13.1852 | -42.2001 | -59.1996 | -69.8182 | 13.0006 | 12.5989 | 12.1733 | 11.4177 | 10.5257 | 9.6175 | 8.414 | 5.3347 | 0.08593 | -6.4749 | -23.1142 | -58.8844 | -80.1299 | -93.657
|  | CHANDLERSFORD | CT |  |  | 14.0045 | 13.7698 | 13.4744 | 12.821 | 12.096 | 11.1931 | 10.2603 | 8.9534 | 7.0105 | 5.0856 | 1.3216 | -8.0248 | -13.045 | -15.4184 | 16.8018 | 16.586 | 16.3199 | 15.9113 | 15.4533 | 14.8424 | 14.1926 | 13.2586 | 12.0037 | 10.7572 | 8.3195 | 2.1729 | -1.727 | -5.2704 | 13.3081 | 13.1013 | 12.8447 | 12.2531 | 11.6001 | 10.7873 | 9.9424 | 8.7708 | 7.0064 | 5.2553 | 1.8227 | -6.6911 | -11.2603 | -13.3917
|  | CHANDLERSFORD | LW |  |  | 13.6829 | 13.2421 | 12.771 | 11.9467 | 10.9572 | 9.9552 | 8.6541 | 7.0438 | 5.1623 | 3.1135 | -1.2934 | -12.464 | -19.6911 | -19.6564 | 16.7346 | 16.4679 | 16.1866 | 15.7633 | 15.2338 | 14.6906 | 13.8837 | 12.8801 | 11.7334 | 10.4595 | 7.6601 | -0.13155 | -5.2634 | -5.0537 | 13.0006 | 12.5989 | 12.1733 | 11.4177 | 10.5257 | 9.6175 | 8.414 | 6.954 | 5.2441 | 3.3796 | -0.65146 | -9.7658 | -16.5694 | -16.466
|  | CHANDLERSFORD | ST |  |  | 14.2062 | 14.1448 | 14.0332 | 13.8666 | 13.6308 | 13.358 | 13.0348 | 12.588 | 12.0643 | 11.4086 | 9.6498 | 3.1803 | -2.1195 | -5.8272 | 16.9357 | 16.8432 | 16.7119 | 16.5442 | 16.3247 | 16.0631 | 15.7478 | 15.3408 | 14.8645 | 14.2785 | 12.7211 | 7.3081 | 2.6294 | -1.4865 | 13.4929 | 13.4426 | 13.3516 | 13.2118 | 13.0156 | 12.7852 | 12.5066 | 12.1252 | 11.676 | 11.1117 | 9.594 | 3.6084 | -1.3069 | -4.5518
|  | CHANDLERSFORD | FS |  |  | 14.0045 | 13.7698 | 13.4744 | 12.821 | 12.096 | 11.1931 | 10.2603 | 8.9534 | 7.0105 | 5.0856 | 1.3216 | -8.0248 | -13.045 | -15.4184 | 16.8785 | 16.7125 | 16.4828 | 16.1952 | 15.8081 | 15.2997 | 13.3407 | 9.9913 | 5.7246 | 0.38101 | -13.1852 | -42.2001 | -59.1996 | -69.8182 | 13.4128 | 13.2796 | 13.0739 | 12.7611 | 12.3323 | 11.7605 | 9.4309 | 5.3347 | 0.08593 | -6.4749 | -23.1142 | -58.8844 | -80.1299 | -93.657
NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL | MINIMUM HEADROOM | SU 42849 11983 | YES | 1.575 | 1.3727 | 1.0942 | 0.83862 | 0.67367 | 0.50099 | 0.30123 | 0.086352 | -0.26478 | -0.62881 | -1.5843 | -4.6069 | -5.6335 | -6.4204 | 4.4605 | 4.3236 | 4.1513 | 3.8802 | 3.7265 | 3.5 | 3.1822 | 2.7904 | 2.3051 | 1.7213 | -0.83409 | -13.9647 | -20.7985 | -25.1551 | 1.9919 | 1.8321 | 1.6389 | 1.439 | 1.317 | 1.1854 | 1.0306 | 0.86097 | 0.51714 | -0.9334 | -5.2709 | -21.2723 | -29.554 | -29.5925
|  | CHAPEL | CT |  |  | 1.6115 | 1.4597 | 1.2584 | 1.0066 | 0.87176 | 0.70313 | 0.48583 | 0.21709 | -0.18939 | -0.62881 | -1.5843 | -4.6069 | -5.6335 | -6.4204 | 4.4605 | 4.3236 | 4.1513 | 3.8802 | 3.7265 | 3.5354 | 3.3031 | 3.0226 | 2.6532 | 2.2205 | 1.2512 | -1.3471 | -5.091 | -11.2032 | 2.0226 | 1.8955 | 1.7269 | 1.5067 | 1.4052 | 1.27 | 1.0907 | 0.86097 | 0.51714 | 0.13283 | -1.1593 | -4.3266 | -5.349 | -6.166
|  | CHAPEL | LW |  |  | 1.575 | 1.3727 | 1.0942 | 0.83862 | 0.67367 | 0.50099 | 0.30123 | 0.086352 | -0.26478 | -0.62813 | -1.3861 | -2.4564 | -2.9945 | -3.5215 | 4.4833 | 4.3697 | 4.2345 | 4.0629 | 3.9635 | 3.8514 | 3.7229 | 3.5851 | 3.3682 | 3.1408 | 2.6678 | 1.9757 | 1.4564 | 0.84933 | 1.9919 | 1.8321 | 1.6389 | 1.439 | 1.317 | 1.1854 | 1.0306 | 0.86269 | 0.58693 | 0.29961 | -0.2959 | -1.2462 | -1.8469 | -2.482
|  | CHAPEL | ST |  |  | 1.7343 | 1.6532 | 1.5244 | 1.3977 | 1.3962 | 1.3806 | 1.3401 | 1.2893 | 1.1638 | 1.0331 | 0.70174 | -0.10526 | -0.69455 | -1.4694 | 4.5211 | 4.4212 | 4.2876 | 4.0657 | 3.968 | 3.8501 | 3.7043 | 3.5412 | 3.2926 | 3.022 | 2.3626 | 0.045584 | -3.7501 | -10.0373 | 2.1326 | 2.0694 | 1.9667 | 1.8338 | 1.8281 | 1.81 | 1.7707 | 1.7297 | 1.622 | 1.5085 | 1.2158 | 0.50689 | -0.075848 | -0.79564
|  | CHAPEL | FS |  |  | 1.6115 | 1.4597 | 1.2584 | 1.0066 | 0.87176 | 0.70313 | 0.48583 | 0.21709 | -0.18939 | -0.62881 | -1.5843 | -4.6069 | -5.6335 | -6.4204 | 4.4939 | 4.3688 | 4.2107 | 3.9803 | 3.7625 | 3.5 | 3.1822 | 2.7904 | 2.3051 | 1.7213 | -0.83409 | -13.9647 | -20.7985 | -25.1551 | 2.0967 | 2.0122 | 1.8951 | 1.7564 | 1.6417 | 1.4866 | 1.2822 | 1.0198 | 0.5468 | -0.9334 | -5.2709 | -21.2723 | -29.554 | -29.5925
COWLEY GSP | YARNTON BSP | CHARLBURY | MINIMUM HEADROOM | SP 36034 18376 | NO | 7.9841 | 7.7649 | 7.5422 | 7.252 | 6.919 | 6.5746 | 6.0879 | 5.5172 | 4.8254 | 4.0806 | 2.4347 | -0.70055 | -2.8306 | -4.026 | 9.188 | 9.0695 | 8.9512 | 8.8066 | 8.6242 | 8.4163 | 8.1221 | 7.7385 | 7.2699 | 6.7528 | 5.6162 | 3.358 | 1.6118 | 0.28332 | 7.9212 | 7.7221 | 7.5195 | 7.2539 | 6.9512 | 6.6382 | 6.2014 | 5.6915 | 5.062 | 4.3863 | 2.8415 | -0.1442 | -2.146 | -3.3022
|  | CHARLBURY | CT |  |  | 8.1183 | 7.9776 | 7.8204 | 7.5688 | 7.3004 | 6.9483 | 6.5763 | 6.0642 | 5.3301 | 4.5998 | 3.1864 | -0.48365 | -2.8306 | -4.026 | 9.2058 | 9.1016 | 8.9801 | 8.8258 | 8.6578 | 8.4163 | 8.1554 | 7.7734 | 7.2808 | 6.7854 | 5.8434 | 3.358 | 1.6118 | 0.28332 | 8.0484 | 7.9223 | 7.782 | 7.5535 | 7.3098 | 6.9929 | 6.6582 | 6.2012 | 5.5356 | 4.8669 | 3.5406 | 0.067355 | -2.146 | -3.3022
|  | CHARLBURY | LW |  |  | 7.9841 | 7.7649 | 7.5422 | 7.252 | 6.919 | 6.5746 | 6.0879 | 5.5172 | 4.8254 | 4.0806 | 2.4347 | -0.70055 | -2.1312 | -2.3544 | 9.188 | 9.0695 | 8.9512 | 8.8066 | 8.6242 | 8.4344 | 8.1221 | 7.7385 | 7.2699 | 6.7528 | 5.6162 | 3.5565 | 2.6229 | 2.3909 | 7.9212 | 7.7221 | 7.5195 | 7.2539 | 6.9512 | 6.6382 | 6.2014 | 5.6915 | 5.062 | 4.3863 | 2.8415 | -0.1442 | -1.5387 | -1.8202
|  | CHARLBURY | ST |  |  | 8.2114 | 8.1508 | 8.0753 | 7.9683 | 7.8345 | 7.6769 | 7.4781 | 7.2365 | 6.931 | 6.567 | 5.6038 | 2.5182 | 0.0048048 | -1.6369 | 9.2637 | 9.2145 | 9.1517 | 9.0714 | 8.9684 | 8.8398 | 8.6756 | 8.4711 | 8.2085 | 7.8957 | 7.066 | 4.5056 | 2.373 | 0.88462 | 8.1338 | 8.08 | 8.0131 | 7.9179 | 7.7992 | 7.6601 | 7.485 | 7.2728 | 6.9956 | 6.6688 | 5.7689 | 2.7485 | 0.27207 | -1.3236
|  | CHARLBURY | FS |  |  | 8.1183 | 7.9776 | 7.8204 | 7.5688 | 7.3004 | 6.9483 | 6.5763 | 6.0642 | 5.3301 | 4.5998 | 3.1864 | -0.48365 | -2.8306 | -4.026 | 9.2701 | 9.2257 | 9.1695 | 9.1015 | 9.0188 | 8.9185 | 8.7961 | 8.646 | 8.4642 | 8.2542 | 7.6962 | 5.6047 | 3.2629 | 1.3787 | 8.1526 | 8.1124 | 8.0596 | 7.9723 | 7.8724 | 7.7558 | 7.6207 | 7.4571 | 7.2339 | 6.9855 | 6.3575 | 3.8525 | 1.0929 | -0.88404
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER | MINIMUM HEADROOM | SY 67309 93186 | YES | 2.8014 | 2.0804 | 1.3409 | 0.61179 | -0.25481 | -1.2843 | -2.8376 | -4.6361 | -6.6192 | -9.1034 | -14.6118 | -24.7677 | -27.281 | -28.574 | 5.2082 | 4.7756 | 4.2761 | 3.7424 | 3.1628 | 2.2519 | 1.2737 | -0.15187 | -1.847 | -3.6557 | -7.1641 | -14.4803 | -17.5807 | -22.2605 | 3.7947 | 3.1265 | 2.4477 | 1.7563 | 0.90258 | -0.06966 | -1.544 | -3.277 | -5.1858 | -7.5487 | -12.7322 | -22.0923 | -24.8371 | -26.0128
|  | CHARMINSTER | CT |  |  | 2.9229 | 2.337 | 1.6567 | 0.93651 | 0.1496 | -1.1181 | -2.4496 | -4.2811 | -6.4976 | -8.9324 | -13.7046 | -23.523 | -27.281 | -28.574 | 5.2082 | 4.7809 | 4.2761 | 3.7424 | 3.1628 | 2.2519 | 1.2737 | -0.15187 | -1.847 | -3.6557 | -7.013 | -14.4803 | -17.5807 | -19.4661 | 3.8709 | 3.3142 | 2.6609 | 1.9529 | 1.19 | 0.0055544 | -1.2509 | -3.0155 | -5.1506 | -7.4627 | -11.922 | -21.2908 | -24.8371 | -26.0128
|  | CHARMINSTER | LW |  |  | 2.8014 | 2.0804 | 1.3409 | 0.61179 | -0.25481 | -1.2843 | -2.8376 | -4.6361 | -6.6192 | -9.1034 | -14.6118 | -24.7677 | -26.9818 | -25.203 | 5.2387 | 4.7756 | 4.3119 | 3.8367 | 3.2245 | 2.5447 | 1.4234 | 0.066632 | -1.4189 | -3.2501 | -7.1641 | -13.9449 | -15.1549 | -13.4005 | 3.7947 | 3.1265 | 2.4477 | 1.7563 | 0.90258 | -0.06966 | -1.544 | -3.277 | -5.1858 | -7.5487 | -12.7322 | -22.0923 | -24.0552 | -22.2021
|  | CHARMINSTER | ST |  |  | 3.2066 | 2.867 | 2.4613 | 2.0599 | 1.6062 | 0.99757 | 0.31385 | -0.52968 | -1.4767 | -2.8457 | -6.3465 | -16.5587 | -22.7955 | -24.7437 | 5.4249 | 5.2086 | 4.9427 | 4.6499 | 4.2993 | 3.831 | 3.2678 | 2.5976 | 1.8407 | 0.76055 | -1.965 | -10.3675 | -15.889 | -18.2582 | 4.1645 | 3.8739 | 3.5192 | 3.1413 | 2.6992 | 2.1105 | 1.4217 | 0.62035 | -0.28155 | -1.5707 | -4.8569 | -14.8125 | -20.9931 | -22.7865
|  | CHARMINSTER | FS |  |  | 2.9229 | 2.337 | 1.6567 | 0.93651 | 0.1496 | -1.1181 | -2.4496 | -4.2811 | -6.4976 | -8.9324 | -13.7046 | -23.523 | -27.281 | -28.574 | 5.4385 | 5.2349 | 4.9909 | 4.7218 | 4.411 | 4.0046 | 3.5387 | 2.9886 | 2.376 | 1.5956 | -0.44426 | -7.9269 | -16.1847 | -22.2605 | 4.202 | 3.9474 | 3.6472 | 3.3028 | 2.9162 | 2.4157 | 1.8558 | 1.2099 | 0.48725 | -0.43562 | -2.8317 | -11.5862 | -20.6088 | -25.6833
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER | MINIMUM HEADROOM | SU 92198 07420 | YES | 4.5356 | 3.596 | 2.4932 | 0.98417 | -0.92656 | -2.9769 | -5.6006 | -8.6011 | -11.9258 | -15.5408 | -22.6846 | -34.8721 | -40.9344 | -43.6722 | 8.837 | 8.269 | 7.6152 | 6.76 | 5.6468 | 4.4754 | 2.8357 | 0.90832 | -1.1657 | -3.6085 | -8.2868 | -17.1722 | -21.27 | -23.7718 | 7.8265 | 6.9863 | 6.0221 | 4.7094 | 3.0293 | 1.2284 | -1.1959 | -4.0156 | -7.083 | -10.3804 | -16.9754 | -28.5583 | -34.1127 | -36.5395
|  | CHICHESTER | CT |  |  | 4.8438 | 4.1716 | 3.2759 | 1.9155 | 0.25024 | -1.779 | -3.9867 | -6.888 | -10.6596 | -14.5338 | -21.8538 | -34.8721 | -40.9344 | -43.6722 | 8.8848 | 8.4101 | 7.7931 | 6.9426 | 5.9161 | 4.6237 | 3.203 | 1.2457 | -1.1572 | -3.6085 | -8.2868 | -17.1722 | -21.27 | -23.7718 | 8.06 | 7.436 | 6.6209 | 5.4111 | 3.9465 | 2.101 | 0.079813 | -2.651 | -6.0965 | -9.6216 | -16.3054 | -28.5583 | -34.1127 | -36.5395
|  | CHICHESTER | LW |  |  | 4.5356 | 3.596 | 2.4932 | 0.98417 | -0.92656 | -2.9769 | -5.6006 | -8.6011 | -11.9258 | -15.5408 | -22.6846 | -31.9936 | -34.8708 | -33.8108 | 8.837 | 8.269 | 7.6152 | 6.76 | 5.6468 | 4.4754 | 2.8357 | 0.90832 | -1.1657 | -3.4221 | -8.0164 | -14.2356 | -15.7059 | -14.4189 | 7.8265 | 6.9863 | 6.0221 | 4.7094 | 3.0293 | 1.2284 | -1.1959 | -4.0156 | -7.083 | -10.3804 | -16.9754 | -25.8289 | -28.3661 | -27.0946
|  | CHICHESTER | ST |  |  | 5.182 | 4.7923 | 4.2096 | 3.3982 | 2.3919 | 1.3437 | 0.19372 | -1.1214 | -2.593 | -4.4201 | -8.6529 | -19.3573 | -26.6984 | -30.2547 | 9.1195 | 8.8732 | 8.5114 | 7.9736 | 7.3051 | 6.6126 | 5.8135 | 4.8833 | 3.8346 | 2.5795 | -0.46435 | -8.7729 | -14.5147 | -17.2559 | 8.3995 | 8.0714 | 7.5865 | 6.8858 | 6.019 | 5.1005 | 4.058 | 2.8484 | 1.4908 | -0.12851 | -3.9927 | -14.3137 | -21.3014 | -24.4613
|  | CHICHESTER | FS |  |  | 4.8438 | 4.1716 | 3.2759 | 1.9155 | 0.25024 | -1.779 | -3.9867 | -6.888 | -10.6596 | -14.5338 | -21.8538 | -34.8721 | -40.9344 | -43.6722 | 9.2033 | 8.9409 | 8.5893 | 8.1375 | 7.5819 | 6.9573 | 6.242 | 5.4233 | 4.5302 | 3.5248 | 1.1504 | -6.0173 | -14.0365 | -19.9273 | 8.5096 | 8.1962 | 7.769 | 7.1753 | 6.451 | 5.6397 | 4.7181 | 3.6731 | 2.5043 | 1.203 | -1.8028 | -10.7162 | -20.2317 | -26.4222
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL | MINIMUM HEADROOM | SY 65479 80511 | YES | 6.0948 | 5.343 | 4.5477 | 3.654 | 2.5186 | 1.226 | -0.83455 | -3.2702 | -6.0202 | -9.1012 | -15.7719 | -26.4419 | -32.0271 | -34.0878 | -5.184 | -5.5219 | -6.0511 | -6.6721 | -7.425 | -8.4389 | -9.7394 | -11.612 | -13.7587 | -16.1876 | -21.4762 | -29.9264 | -34.4848 | -39.5233 | -6.5277 | -7.2929 | -8.0775 | -8.9474 | -10.0918 | -11.3218 | -13.3376 | -15.784 | -18.5447 | -21.6453 | -28.374 | -39.0161 | -44.0882 | -45.9621
|  | CHICKERELL | CT |  |  | 6.1895 | 5.5573 | 4.802 | 3.9419 | 2.9422 | 1.4291 | -0.2101 | -2.5257 | -5.3916 | -8.185 | -13.4139 | -26.1959 | -32.0271 | -34.0878 | -5.1718 | -5.489 | -6.0435 | -6.6721 | -7.3686 | -8.4389 | -9.6146 | -11.4523 | -13.7005 | -15.8904 | -19.9774 | -29.9264 | -34.4848 | -36.7182 | -6.5117 | -7.1804 | -7.9742 | -8.8611 | -9.8399 | -11.3218 | -12.9315 | -15.2784 | -18.1513 | -20.9429 | -26.1347 | -38.6677 | -44.0882 | -45.9621
|  | CHICKERELL | LW |  |  | 6.0948 | 5.343 | 4.5477 | 3.654 | 2.5186 | 1.226 | -0.83455 | -3.2702 | -6.0202 | -9.1012 | -15.7719 | -26.4419 | -28.9488 | -26.9218 | -5.184 | -5.5219 | -6.0511 | -6.6293 | -7.425 | -8.2696 | -9.7394 | -11.612 | -13.7587 | -16.1876 | -21.4762 | -29.7536 | -31.531 | -29.7251 | -6.5277 | -7.2929 | -8.0775 | -8.9474 | -10.0918 | -11.3105 | -13.3376 | -15.784 | -18.5447 | -21.6453 | -28.374 | -39.0161 | -41.3883 | -39.1315
|  | CHICKERELL | ST |  |  | 6.445 | 6.1596 | 5.7702 | 5.3552 | 4.8519 | 4.213 | 3.4165 | 2.4185 | 1.2567 | -0.17034 | -4.0246 | -16.9091 | -25.7021 | -28.5143 | -5.0537 | -5.1725 | -5.3163 | -5.5608 | -5.9371 | -6.4225 | -7.0572 | -7.8277 | -8.7455 | -9.9035 | -13.211 | -23.8986 | -31.3106 | -34.1935 | -6.1514 | -6.4641 | -6.858 | -7.2832 | -7.8165 | -8.5041 | -9.3598 | -10.3831 | -11.5846 | -13.0688 | -17.1068 | -30.1731 | -38.9276 | -41.7066
|  | CHICKERELL | FS |  |  | 6.1895 | 5.5573 | 4.802 | 3.9419 | 2.9422 | 1.4291 | -0.2101 | -2.5257 | -5.3916 | -8.185 | -13.4139 | -26.1959 | -32.0271 | -34.0878 | -5.0523 | -5.1711 | -5.3112 | -5.5509 | -5.9022 | -6.3508 | -6.9089 | -7.5901 | -8.3875 | -9.3387 | -11.9315 | -21.3838 | -32.0252 | -39.5233 | -6.1519 | -6.459 | -6.8297 | -7.2485 | -7.7449 | -8.3793 | -9.1286 | -10.0336 | -11.0751 | -12.2754 | -15.423 | -26.7491 | -38.8682 | -45.8324
AXMINSTER | YEOVIL BSP | CHILTON CANTELLO | MINIMUM HEADROOM | ST 57910 21616 | YES | 0.37908 | -0.37565 | -1.2275 | -2.1767 | -3.3945 | -4.6992 | -6.8229 | -9.4084 | -12.1449 | -15.0462 | -21.4186 | -31.2426 | -35.6933 | -39.5748 | 2.2568 | 1.9766 | 1.4228 | 0.76369 | -0.096099 | -1.0245 | -2.5765 | -4.4733 | -6.4863 | -8.6808 | -13.5109 | -21.1775 | -25.341 | -28.483 | 0.68093 | -0.086323 | -0.85496 | -1.7342 | -2.8773 | -4.1084 | -6.1387 | -8.6159 | -11.2425 | -14.0596 | -20.2625 | -30.051 | -33.6474 | -37.433
|  | CHILTON CANTELLO | CT |  |  | 0.41654 | -0.14834 | -0.96329 | -1.8974 | -2.9398 | -4.4661 | -6.2155 | -8.7289 | -11.616 | -14.3806 | -19.6069 | -30.0773 | -33.9207 | -35.2033 | 2.2827 | 2.061 | 1.4921 | 0.84232 | 0.11254 | -0.99018 | -2.2566 | -4.1019 | -6.2327 | -8.3039 | -12.1918 | -20.3551 | -23.3524 | -24.5836 | 0.73649 | 0.10389 | -0.64471 | -1.5097 | -2.4801 | -3.9245 | -5.5809 | -7.9804 | -10.7501 | -13.4191 | -18.4498 | -28.9133 | -32.7107 | -33.9653
|  | CHILTON CANTELLO | LW |  |  | 0.37908 | -0.37565 | -1.2275 | -2.1767 | -3.3945 | -4.6992 | -6.8229 | -9.4084 | -12.1449 | -15.0462 | -21.4186 | -31.2426 | -35.6933 | -39.5748 | 2.2568 | 1.9766 | 1.4228 | 0.76369 | -0.096099 | -1.0245 | -2.5765 | -4.4733 | -6.4863 | -8.6808 | -13.5109 | -21.1775 | -25.341 | -28.483 | 0.68093 | -0.086323 | -0.85496 | -1.7342 | -2.8773 | -4.1084 | -6.1387 | -8.6159 | -11.2425 | -14.0596 | -20.2625 | -30.051 | -33.6474 | -37.433
|  | CHILTON CANTELLO | ST |  |  | 0.59348 | 0.46208 | 0.065502 | -0.54833 | -1.2338 | -2.0571 | -3.0985 | -4.3189 | -5.6483 | -7.178 | -11.1773 | -23.0386 | -30.5968 | -32.4428 | 2.3832 | 2.2926 | 2.1816 | 1.8389 | 1.3511 | 0.75759 | -0.015674 | -0.90705 | -1.8925 | -3.0495 | -6.1009 | -15.3717 | -21.5332 | -23.1958 | 1.0659 | 0.75437 | 0.36699 | -0.20199 | -0.83514 | -1.6003 | -2.5797 | -3.7205 | -4.9766 | -6.4432 | -10.44 | -22.4411 | -29.9832 | -31.8385
|  | CHILTON CANTELLO | FS |  |  | 0.41654 | -0.14834 | -0.96329 | -1.8974 | -2.9398 | -4.4661 | -6.2155 | -8.7289 | -11.616 | -14.3806 | -19.6069 | -30.0773 | -33.9207 | -35.2033 | 2.3954 | 2.2813 | 2.1591 | 1.9269 | 1.5008 | 0.99621 | 0.34807 | -0.42688 | -1.2577 | -2.1904 | -4.6264 | -12.7989 | -21.7443 | -26.6421 | 1.0915 | 0.78631 | 0.42682 | -0.040292 | -0.59323 | -1.243 | -2.0707 | -3.0584 | -4.1247 | -5.3126 | -8.5043 | -19.2214 | -30.4249 | -36.3774
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM | MINIMUM HEADROOM | SU 65105 55805 | YES | 13.9256 | 13.4246 | 12.8755 | 12.1931 | 11.4296 | 10.6173 | 9.9814 | 9.3626 | 8.7408 | 8.0833 | 5.6783 | -3.004 | -6.9576 | -6.9016 | 16.2772 | 16.0538 | 15.8472 | 15.5077 | 15.0711 | 14.606 | 14.1477 | 13.7054 | 13.1858 | 11.2249 | 6.5869 | -2.0872 | -5.0136 | -7.1682 | 14.8103 | 14.5055 | 14.1992 | 13.7555 | 13.1925 | 12.4561 | 11.4401 | 10.0909 | 8.3916 | 6.0962 | 0.4061 | -10.3815 | -14.2215 | -17.1882
|  | CHINEHAM | CT |  |  | 14.1625 | 13.8084 | 13.4075 | 13.0195 | 12.5068 | 12.0028 | 11.5784 | 11.1388 | 10.4641 | 9.756 | 8.4179 | 4.7375 | 0.058549 | -2.4419 | 16.3231 | 16.1183 | 15.9426 | 15.8125 | 15.5377 | 15.3321 | 15.0927 | 14.8559 | 14.6108 | 14.2852 | 13.5759 | 11.5098 | 8.3507 | 6.6139 | 14.8779 | 14.6286 | 14.385 | 14.1859 | 13.8629 | 13.5436 | 13.1865 | 12.7798 | 12.3199 | 11.6138 | 10.0342 | 5.2937 | 0.89044 | -1.4535
|  | CHINEHAM | LW |  |  | 13.9256 | 13.4246 | 12.8755 | 12.1931 | 11.4296 | 10.6173 | 9.9814 | 9.3626 | 8.7408 | 8.0833 | 5.6783 | -3.004 | -6.9576 | -6.9016 | 16.2772 | 16.0538 | 15.8472 | 15.5077 | 15.0711 | 14.606 | 14.1477 | 13.7054 | 13.3208 | 12.8753 | 11.5097 | 4.9181 | 2.0028 | 2.1308 | 14.8103 | 14.5055 | 14.1992 | 13.7555 | 13.1925 | 12.468 | 11.7884 | 10.8863 | 9.896 | 8.7375 | 5.8828 | -2.494 | -6.2633 | -6.1835
|  | CHINEHAM | ST |  |  | 14.2365 | 13.9282 | 13.5779 | 13.2648 | 12.9153 | 12.6288 | 12.3841 | 12.2018 | 12.0478 | 11.8982 | 11.6451 | 10.3892 | 9.0851 | 7.3705 | 16.3559 | 16.1738 | 16.0227 | 15.7766 | 15.4674 | 15.2645 | 15.0137 | 14.8422 | 14.6944 | 14.5457 | 14.2516 | 13.3152 | 12.5422 | 11.3798 | 14.9587 | 14.7651 | 14.5837 | 14.3163 | 14.003 | 13.7587 | 13.4705 | 13.2497 | 13.0359 | 12.8039 | 12.2786 | 10.8206 | 10.1867 | 9.2597
|  | CHINEHAM | FS |  |  | 14.1625 | 13.8084 | 13.4075 | 13.0195 | 12.5068 | 12.0028 | 11.5784 | 11.1388 | 10.4641 | 9.756 | 8.4179 | 4.7375 | 0.058549 | -2.4419 | 16.3384 | 16.1562 | 15.9501 | 15.7312 | 15.4214 | 15.0673 | 14.6513 | 14.1365 | 13.1858 | 11.2249 | 6.5869 | -2.0872 | -5.0136 | -7.1682 | 14.8645 | 14.6016 | 14.2592 | 13.8378 | 13.2411 | 12.4561 | 11.4401 | 10.0909 | 8.3916 | 6.0962 | 0.4061 | -10.3815 | -14.2215 | -17.1882
COWLEY GSP | YARNTON BSP | CHIPPING NORTON | MINIMUM HEADROOM | SP 31382 26792 | NO | 2.6688 | 1.867 | 1.0823 | 0.19233 | -1.007 | -2.2145 | -4.1304 | -6.4234 | -8.8592 | -11.5785 | -17.303 | -28.4708 | -33.2747 | -34.7024 | 4.6859 | 4.1031 | 3.5284 | 2.8941 | 2.052 | 1.0472 | -0.1577 | -1.9529 | -4.1351 | -6.2899 | -15.2615 | -40.157 | -56.3999 | -62.7109 | 2.4775 | 1.7106 | 0.96129 | 0.11055 | -0.98916 | -2.0938 | -3.9271 | -6.1433 | -8.6365 | -11.7254 | -22.7265 | -53.3495 | -73.3833 | -81.2966
|  | CHIPPING NORTON | CT |  |  | 2.8099 | 2.2046 | 1.5106 | 0.61252 | -0.5023 | -2.0173 | -3.6594 | -6.0096 | -8.8592 | -11.5785 | -16.652 | -28.4708 | -33.2747 | -34.7024 | 4.6859 | 4.1865 | 3.6014 | 2.9277 | 2.1412 | 1.0472 | -0.15453 | -1.9529 | -4.1351 | -6.2276 | -10.1366 | -19.2828 | -23.0469 | -24.611 | 2.5707 | 1.9732 | 1.2779 | 0.43446 | -0.56639 | -2.003 | -3.5691 | -5.8758 | -8.6365 | -11.2657 | -16.1808 | -27.6675 | -32.2955 | -33.6449
|  | CHIPPING NORTON | LW |  |  | 2.6688 | 1.867 | 1.0823 | 0.19233 | -1.007 | -2.2145 | -4.1304 | -6.4234 | -8.8538 | -11.4503 | -17.303 | -26.8301 | -28.8235 | -26.2036 | 4.6971 | 4.1031 | 3.5284 | 2.8941 | 2.052 | 1.2202 | -0.1577 | -1.8449 | -3.6926 | -5.7614 | -10.2946 | -17.493 | -18.7916 | -16.5184 | 2.4775 | 1.7106 | 0.96129 | 0.11055 | -0.98916 | -2.0938 | -3.9271 | -6.1433 | -8.5072 | -11.1012 | -16.7883 | -26.0458 | -27.9284 | -25.3326
|  | CHIPPING NORTON | ST |  |  | 3.1051 | 2.7589 | 2.3572 | 1.869 | 1.2316 | 0.55739 | -0.33512 | -1.4796 | -2.759 | -4.3399 | -8.501 | -21.176 | -29.0165 | -31.2262 | 4.9431 | 4.6941 | 4.392 | 4.0097 | 3.5016 | 2.9304 | 2.2102 | 1.3321 | 0.33217 | -0.90302 | -4.2528 | -14.4536 | -20.8799 | -22.9661 | 2.8867 | 2.5777 | 2.2079 | 1.7418 | 1.1321 | 0.47309 | -0.34853 | -1.4625 | -2.7269 | -4.2486 | -8.2586 | -20.7139 | -28.4338 | -30.5145
|  | CHIPPING NORTON | FS |  |  | 2.8099 | 2.2046 | 1.5106 | 0.61252 | -0.5023 | -2.0173 | -3.6594 | -6.0096 | -8.8592 | -11.5785 | -16.652 | -28.4708 | -33.2747 | -34.7024 | 4.9629 | 4.6798 | 4.3494 | 3.9478 | 3.4373 | 2.834 | 1.6559 | -0.42254 | -3.0123 | -6.2899 | -15.2615 | -40.157 | -56.3999 | -62.7109 | 2.9128 | 2.5777 | 2.1866 | 1.6832 | 1.0505 | -0.067647 | -1.978 | -4.5236 | -7.704 | -11.7254 | -22.7265 | -53.3495 | -73.3833 | -81.2966
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE | MINIMUM HEADROOM | SU 80226 89155 | YES | 1.5648 | 1.4263 | 1.2919 | 1.1692 | 1.0205 | 0.86946 | 0.62884 | 0.33863 | 0.014339 | -0.34765 | -1.1416 | -2.6031 | -3.6467 | -3.9324 | 2.1258 | 2.0778 | 2.0321 | 1.9905 | 1.9005 | 1.761 | 1.5709 | 1.314 | 0.97647 | 0.47803 | -0.71115 | -3.0322 | -3.8752 | -4.4347 | 1.1773 | 1.0489 | 0.92428 | 0.80903 | 0.66783 | 0.52392 | 0.2912 | 0.0089919 | -0.30614 | -0.65852 | -1.8375 | -4.783 | -5.8736 | -6.5997
|  | CHISBRIDGE | CT |  |  | 1.6202 | 1.5224 | 1.4134 | 1.2913 | 1.1589 | 0.97667 | 0.7853 | 0.51154 | 0.17557 | -0.14846 | -0.75046 | -2.1246 | -2.8212 | -3.0287 | 2.1476 | 2.1158 | 2.0818 | 2.0436 | 2.0018 | 1.9468 | 1.8884 | 1.8105 | 1.7135 | 1.6159 | 1.4225 | 0.48974 | -0.0064967 | -0.27289 | 1.2251 | 1.133 | 1.0299 | 0.91446 | 0.78909 | 0.61417 | 0.42979 | 0.16338 | -0.16243 | -0.4763 | -1.0582 | -2.3867 | -3.0413 | -3.2358
|  | CHISBRIDGE | LW |  |  | 1.5648 | 1.4263 | 1.2919 | 1.1692 | 1.0205 | 0.86946 | 0.62884 | 0.33863 | 0.014339 | -0.34765 | -1.1416 | -2.6031 | -3.1463 | -2.9152 | 2.1258 | 2.0778 | 2.0321 | 1.9905 | 1.9404 | 1.8869 | 1.8083 | 1.7145 | 1.6058 | 1.4812 | 1.1913 | 0.25532 | -0.10777 | 0.11931 | 1.1773 | 1.0489 | 0.92428 | 0.80903 | 0.66783 | 0.52392 | 0.2912 | 0.0089919 | -0.30614 | -0.65852 | -1.4328 | -2.8521 | -3.3715 | -3.1347
|  | CHISBRIDGE | ST |  |  | 1.6662 | 1.6071 | 1.5427 | 1.4523 | 1.3439 | 1.2207 | 1.0722 | 0.89486 | 0.68737 | 0.43793 | -0.21448 | -2.307 | -3.6467 | -3.9324 | 2.1678 | 2.1498 | 2.1308 | 2.1033 | 2.0713 | 2.0362 | 1.9956 | 1.9488 | 1.8946 | 1.8315 | 1.6736 | 0.19406 | -0.90452 | -1.2072 | 1.2684 | 1.2139 | 1.1539 | 1.0695 | 0.96773 | 0.8507 | 0.70854 | 0.53755 | 0.33698 | 0.094614 | -0.54374 | -2.585 | -3.8804 | -4.1581
|  | CHISBRIDGE | FS |  |  | 1.6202 | 1.5224 | 1.4134 | 1.2913 | 1.1589 | 0.97667 | 0.7853 | 0.51154 | 0.17557 | -0.14846 | -0.75046 | -2.1246 | -2.8212 | -3.0287 | 2.1549 | 2.1203 | 2.0739 | 1.9996 | 1.9005 | 1.761 | 1.5709 | 1.314 | 0.97647 | 0.47803 | -0.71115 | -3.0322 | -3.8752 | -4.4347 | 1.2899 | 1.2445 | 1.1954 | 1.114 | 1.0247 | 0.91031 | 0.77259 | 0.6011 | 0.27127 | -0.3539 | -1.8375 | -4.783 | -5.8736 | -6.5997
MINETY GSP | TOOTHILL BSP | CHISLEDON | MINIMUM HEADROOM | SU 18894 79934 | YES | 1.0616 | -3.9689 | -9.1052 | -10.4329 | -12.1287 | -14.7706 | -18.1262 | -21.6877 | -25.3238 | -29.087 | -36.7592 | -46.2533 | -49.3867 | -51.9617 | -0.56511 | -6.0211 | -11.562 | -12.3205 | -13.2939 | -15.2863 | -17.8657 | -20.464 | -23.0453 | -25.6758 | -31.9914 | -41.9105 | -45.2029 | -47.7305 | -1.4698 | -7.3226 | -13.2728 | -14.3701 | -15.7904 | -18.3221 | -21.5863 | -24.9851 | -28.4157 | -31.9412 | -39.0715 | -48.9579 | -52.7521 | -55.5412
|  | CHISLEDON | CT |  |  | 1.1336 | -3.7197 | -8.7371 | -9.8677 | -11.2284 | -13.7011 | -16.4725 | -19.6045 | -22.9624 | -26.2984 | -32.5722 | -41.5311 | -44.5802 | -45.9351 | -0.52271 | -5.8996 | -11.4336 | -12.0872 | -12.8573 | -14.7731 | -16.9474 | -19.2579 | -21.6131 | -23.8751 | -27.9406 | -34.5433 | -37.2026 | -38.7994 | -1.3985 | -7.1029 | -12.9671 | -13.9059 | -15.0383 | -17.4304 | -20.1431 | -23.1383 | -26.2933 | -29.3831 | -35.0885 | -43.6926 | -46.7911 | -48.2493
|  | CHISLEDON | LW |  |  | 1.0616 | -3.9689 | -9.1052 | -10.4329 | -12.1287 | -14.7706 | -18.1262 | -21.6877 | -25.3238 | -29.087 | -36.7592 | -46.2533 | -49.3867 | -51.9617 | -0.56511 | -6.0211 | -11.562 | -12.3205 | -13.2939 | -15.2863 | -17.8657 | -20.464 | -23.0453 | -25.6758 | -31.9914 | -41.9105 | -45.2029 | -47.7305 | -1.4698 | -7.3226 | -13.2728 | -14.3701 | -15.7904 | -18.3221 | -21.5863 | -24.9851 | -28.4157 | -31.9412 | -39.0715 | -48.9579 | -52.7521 | -55.5412
|  | CHISLEDON | ST |  |  | 1.3066 | -3.3793 | -8.2084 | -9.0471 | -10.0201 | -11.7497 | -13.6764 | -15.6444 | -17.6509 | -19.7629 | -24.3162 | -32.7956 | -37.9302 | -39.9956 | -0.46918 | -5.7969 | -11.2073 | -11.5563 | -12.087 | -13.5301 | -15.1862 | -16.8063 | -18.3966 | -20.0028 | -23.3632 | -30.1269 | -34.7779 | -36.9386 | -1.2458 | -6.8034 | -12.4964 | -13.1582 | -13.9204 | -15.5738 | -17.4775 | -19.3783 | -21.2802 | -23.2426 | -27.428 | -35.7724 | -41.1459 | -43.3346
|  | CHISLEDON | FS |  |  | 1.1336 | -3.7197 | -8.7371 | -9.8677 | -11.2284 | -13.7011 | -16.4725 | -19.6045 | -22.9624 | -26.2984 | -32.5722 | -41.5311 | -44.5802 | -45.9351 | -0.4861 | -5.8193 | -11.2089 | -11.6846 | -12.3163 | -13.7876 | -15.516 | -17.3814 | -19.1969 | -20.9887 | -24.6945 | -31.9044 | -37.5647 | -40.8042 | -1.3042 | -6.881 | -12.5555 | -13.2315 | -14.0573 | -15.7512 | -17.7354 | -19.8969 | -22.0471 | -24.1991 | -28.7461 | -37.6402 | -44.4234 | -47.9593
BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM | MINIMUM HEADROOM | SU 97173 63223 | YES | -0.55098 | -1.2158 | 10.4037 | 9.4813 | 8.3861 | 7.1966 | 5.17 | 2.5874 | -0.3883 | -3.7539 | -12.3327 | -40.4062 | -57.4135 | -63.254 | 13.2608 | 12.7836 | 12.2175 | 11.527 | 10.7761 | 9.6106 | 8.2949 | 6.3039 | 3.8715 | 1.4498 | -6.0519 | -27.7649 | -41.0149 | -45.7296 | 11.1135 | 10.4319 | 9.753 | 8.8473 | 7.7266 | 6.5174 | 4.4934 | 1.962 | -0.94919 | -4.2461 | -13.4513 | -40.3916 | -56.7578 | -62.4522
|  | CHOBHAM | CT |  |  | -0.41638 | -0.92421 | 10.7477 | 9.8849 | 8.9832 | 7.5343 | 5.8886 | 3.4389 | 0.29861 | -2.829 | -8.8581 | -22.6685 | -28.4407 | -30.5823 | 13.2608 | 12.7889 | 12.2175 | 11.527 | 10.7761 | 9.6106 | 8.2949 | 6.3039 | 3.8715 | 1.4498 | -3.177 | -13.7086 | -18.0735 | -20.2343 | 11.1935 | 10.6458 | 9.9824 | 9.0929 | 8.1435 | 6.7111 | 5.095 | 2.6824 | -0.40196 | -3.4726 | -9.3563 | -22.8238 | -28.3905 | -30.4657
|  | CHOBHAM | LW |  |  | -0.55098 | -1.2158 | 10.4037 | 9.4813 | 8.3861 | 7.1966 | 5.17 | 2.5874 | -0.3883 | -3.7539 | -12.3327 | -40.4062 | -57.4135 | -63.254 | 13.3005 | 12.7836 | 12.2701 | 11.6404 | 10.8175 | 9.9317 | 8.356 | 6.3584 | 4.091 | 1.5103 | -6.0519 | -27.7649 | -41.0149 | -45.7296 | 11.1135 | 10.4319 | 9.753 | 8.8473 | 7.7266 | 6.5174 | 4.4934 | 1.962 | -0.94919 | -4.2461 | -13.4513 | -40.3916 | -56.7578 | -62.4522
|  | CHOBHAM | ST |  |  | -0.11261 | -0.31254 | 11.697 | 11.3074 | 10.8737 | 10.3084 | 9.5325 | 8.4562 | 7.1724 | 5.5843 | 1.1604 | -12.9589 | -22.2993 | -25.2249 | 13.5312 | 13.3396 | 13.0832 | 12.7069 | 12.2634 | 11.6874 | 10.9238 | 9.9755 | 8.8462 | 7.4506 | 3.6644 | -8.1208 | -15.793 | -18.4759 | 11.5247 | 11.316 | 11.0274 | 10.6039 | 10.1111 | 9.4682 | 8.6128 | 7.524 | 6.2021 | 4.5657 | 0.011054 | -14.3861 | -23.6508 | -26.4888
|  | CHOBHAM | FS |  |  | -0.41638 | -0.92421 | 10.7477 | 9.8849 | 8.9832 | 7.5343 | 5.8886 | 3.4389 | 0.29861 | -2.829 | -8.8581 | -22.6685 | -28.4407 | -30.5823 | 13.5143 | 13.3268 | 13.0867 | 12.7786 | 12.4077 | 11.9339 | 11.331 | 10.5772 | 9.7186 | 8.6872 | 5.8162 | -5.0334 | -16.8275 | -23.8216 | 11.5101 | 11.3096 | 11.0524 | 10.6978 | 10.2777 | 9.7425 | 9.0586 | 8.2016 | 7.1816 | 5.9441 | 2.509 | -10.6932 | -25.0274 | -32.9917
COWLEY GSP | DRAYTON BSP | CHOLSEY | MINIMUM HEADROOM | SU 58223 84685 | NO | 7.0537 | 5.7143 | 4.2649 | 2.5 | 0.43131 | -2.6197 | -6.4771 | -12.2207 | -18.6212 | -25.8879 | -41.924 | -68.2192 | -85.7231 | -94.9505 | 7.2528 | 6.2092 | 4.9595 | 3.5506 | 1.9941 | -0.51901 | -3.3419 | -7.9058 | -12.9804 | -18.749 | -31.4877 | -51.7853 | -63.6961 | -70.8809 | 5.9626 | 4.6636 | 3.1998 | 1.4767 | -0.54097 | -3.469 | -7.2984 | -12.8922 | -19.1333 | -26.3084 | -42.1895 | -67.5624 | -82.0592 | -90.8686
|  | CHOLSEY | CT |  |  | 7.0537 | 5.7778 | 4.2649 | 2.5 | 0.53379 | -2.6197 | -6.0721 | -11.4945 | -18.0072 | -24.2459 | -35.7198 | -62.447 | -72.1817 | -74.7893 | 7.2528 | 6.2092 | 4.9595 | 3.5506 | 1.9941 | -0.51901 | -3.2752 | -7.6202 | -12.7978 | -17.7572 | -26.8713 | -48.109 | -55.825 | -58.1521 | 5.9626 | 4.7015 | 3.1998 | 1.4767 | -0.42302 | -3.469 | -6.8048 | -12.1333 | -18.5986 | -24.7906 | -36.1717 | -62.661 | -72.2457 | -74.7859
|  | CHOLSEY | LW |  |  | 7.1161 | 5.7143 | 4.3044 | 2.6874 | 0.43131 | -1.9773 | -6.4771 | -12.2207 | -18.6212 | -25.8879 | -41.924 | -68.2192 | -85.7231 | -94.9505 | 7.4164 | 6.279 | 5.1679 | 3.9083 | 2.1228 | 0.22477 | -3.3419 | -7.9058 | -12.9804 | -18.749 | -31.4877 | -51.7853 | -63.6961 | -70.8809 | 6.0836 | 4.6636 | 3.2744 | 1.6844 | -0.54097 | -2.9146 | -7.2984 | -12.8922 | -19.1333 | -26.3084 | -42.1895 | -67.5624 | -82.0592 | -90.8686
|  | CHOLSEY | ST |  |  | 7.7473 | 7.4129 | 6.8507 | 6.0639 | 5.0091 | 3.6078 | 1.7113 | -0.7325 | -3.5692 | -7.15 | -17.0602 | -48.8139 | -68.7706 | -73.1384 | 7.9144 | 7.5516 | 7.0727 | 6.4242 | 5.5514 | 4.3894 | 2.8585 | 0.88405 | -1.4006 | -4.2869 | -12.2805 | -37.8558 | -53.9388 | -57.5601 | 6.7722 | 6.3364 | 5.7673 | 4.9879 | 3.9418 | 2.5509 | 0.71809 | -1.6403 | -4.3772 | -7.8445 | -17.7119 | -49.3095 | -69.1269 | -73.3871
|  | CHOLSEY | FS |  |  | 7.0537 | 5.7778 | 4.2649 | 2.5 | 0.53379 | -2.6197 | -6.0721 | -11.4945 | -18.0072 | -24.2459 | -35.7198 | -62.447 | -72.1817 | -74.7893 | 7.9293 | 7.5971 | 7.1737 | 6.6291 | 5.9293 | 5.0206 | 3.8677 | 2.3981 | 0.75971 | -1.1771 | -6.5259 | -26.985 | -49.9568 | -62.8156 | 6.8019 | 6.4088 | 5.9122 | 5.2556 | 4.4123 | 3.3226 | 1.9388 | 0.1842 | -1.792 | -4.1219 | -10.6164 | -35.8963 | -64.2041 | -79.791
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH | MINIMUM HEADROOM | SZ 15698 93141 | YES | 8.8515 | 8.0667 | 7.2456 | 5.9517 | 4.4384 | 2.8142 | 0.54728 | -2.1362 | -5.3112 | -8.8044 | -16.3674 | -30.4833 | -35.4059 | -36.9449 | -15.6432 | -16.1907 | -16.7537 | -17.5091 | -18.4635 | -19.4737 | -21.0297 | -22.9093 | -25.0467 | -27.4363 | -32.6914 | -42.2215 | -57.1738 | -72.782 | -20.9939 | -21.7631 | -22.5603 | -23.7721 | -25.2188 | -26.7327 | -28.8618 | -31.4822 | -34.5051 | -37.8408 | -45.0895 | -58.5039 | -63.1166 | -71.686
|  | CHRISTCHURCH | CT |  |  | 9.3264 | 8.8486 | 8.2698 | 7.1839 | 5.9807 | 4.4204 | 2.6551 | 0.23102 | -3.0006 | -6.1756 | -12.2038 | -26.655 | -33.7737 | -36.9449 | -15.5668 | -16.0406 | -16.608 | -17.3637 | -18.1995 | -19.3636 | -20.6211 | -22.3978 | -24.6574 | -26.8946 | -31.1751 | -41.7572 | -48.3483 | -54.4622 | -20.6118 | -21.1199 | -21.7316 | -22.7576 | -23.8767 | -25.3757 | -27.0578 | -29.3748 | -32.4455 | -35.4638 | -41.1852 | -54.8398 | -61.4311 | -64.3122
|  | CHRISTCHURCH | LW |  |  | 8.8515 | 8.0667 | 7.2456 | 5.9517 | 4.4384 | 2.8142 | 0.54728 | -2.1362 | -5.3112 | -8.8044 | -16.3674 | -30.4833 | -35.4059 | -34.3355 | -15.6432 | -16.1907 | -16.7537 | -17.5091 | -18.4635 | -19.4737 | -21.0297 | -22.9093 | -25.0467 | -27.4363 | -32.6914 | -42.2215 | -45.8365 | -45.9828 | -20.9939 | -21.7631 | -22.5603 | -23.7721 | -25.2188 | -26.7327 | -28.8618 | -31.4822 | -34.5051 | -37.8408 | -45.0895 | -58.5039 | -63.0612 | -61.891
|  | CHRISTCHURCH | ST |  |  | 9.7197 | 9.5397 | 9.2826 | 8.9832 | 8.594 | 8.078 | 7.408 | 6.5385 | 5.4712 | 4.1765 | 0.71938 | -11.2743 | -20.2939 | -25.1759 | -15.2882 | -15.5114 | -15.7992 | -16.1456 | -16.5808 | -17.1169 | -17.7674 | -18.5589 | -19.5115 | -20.6638 | -23.7241 | -34.2064 | -43.0284 | -49.9381 | -20.2199 | -20.4135 | -20.6811 | -21.0052 | -21.4243 | -21.941 | -22.5748 | -23.4376 | -24.4744 | -25.7378 | -29.1328 | -40.8218 | -49.5158 | -54.0015
|  | CHRISTCHURCH | FS |  |  | 9.3264 | 8.8486 | 8.2698 | 7.1839 | 5.9807 | 4.4204 | 2.6551 | 0.23102 | -3.0006 | -6.1756 | -12.2038 | -26.655 | -33.7737 | -36.9449 | -15.451 | -15.8035 | -16.2387 | -16.7647 | -17.4033 | -18.2345 | -19.2521 | -20.5883 | -22.2279 | -24.0414 | -28.3534 | -42.053 | -57.1738 | -72.782 | -20.3988 | -20.7253 | -21.1353 | -21.6854 | -22.354 | -23.2414 | -24.4058 | -25.9459 | -27.8029 | -29.8383 | -34.6233 | -49.4021 | -63.1166 | -71.686
LALEHAM | EAST BEDFONT A | CHURCH ROAD | MINIMUM HEADROOM | TQ 06820 71722 | YES | 0.55952 | 0.33803 | -0.029845 | -0.67898 | -1.1947 | -1.6995 | -2.2862 | -2.9069 | -3.6436 | -4.4086 | -5.9827 | -9.9852 | -12.9292 | -14.4658 | 3.5175 | 3.3301 | 3.068 | 2.7564 | 2.4134 | 2.0195 | 1.4075 | 0.64146 | -0.30445 | -1.3945 | -4.0197 | -11.2481 | -19.0963 | -28.2539 | 0.87665 | 0.69358 | 0.40329 | -0.10707 | -0.52494 | -0.93497 | -1.4257 | -2.2737 | -3.3144 | -4.505 | -7.3504 | -14.6091 | -20.354 | -23.2248
|  | CHURCH ROAD | CT |  |  | 0.82199 | 0.73538 | 0.51145 | 0.00090668 | -0.37313 | -0.79397 | -1.2521 | -1.8153 | -2.7203 | -3.6105 | -5.375 | -9.9852 | -12.9292 | -14.4658 | 3.6441 | 3.5582 | 3.3946 | 3.1197 | 2.9028 | 2.641 | 2.3504 | 1.9784 | 1.4292 | 0.87453 | -0.26765 | -3.4773 | -6.4931 | -10.293 | 1.0768 | 0.99804 | 0.81534 | 0.40757 | 0.098135 | -0.25892 | -0.64872 | -1.1377 | -1.9037 | -2.6814 | -4.2911 | -8.4547 | -10.9547 | -12.1729
|  | CHURCH ROAD | LW |  |  | 0.55952 | 0.33803 | -0.029845 | -0.67898 | -1.1947 | -1.6995 | -2.2862 | -2.9069 | -3.6436 | -4.4086 | -5.9827 | -9.3387 | -10.9925 | -11.4109 | 3.5829 | 3.4777 | 3.3004 | 3.0169 | 2.7917 | 2.569 | 2.2848 | 1.9708 | 1.6049 | 1.2163 | 0.40371 | -1.2186 | -1.9262 | -1.9709 | 0.87665 | 0.69358 | 0.40329 | -0.10707 | -0.52494 | -0.93497 | -1.4257 | -1.9833 | -2.6527 | -3.35 | -4.7889 | -7.7973 | -9.2148 | -9.4315
|  | CHURCH ROAD | ST |  |  | 0.90356 | 0.89917 | 0.75002 | 0.59031 | 0.54863 | 0.48663 | 0.40171 | 0.26993 | 0.12896 | -0.036118 | -0.46512 | -2.6228 | -4.7779 | -6.9906 | 3.6767 | 3.6366 | 3.518 | 3.3896 | 3.3121 | 3.2145 | 3.0932 | 2.9366 | 2.7377 | 2.507 | 1.9237 | -0.39413 | -3.219 | -7.1599 | 1.1439 | 1.137 | 1.0215 | 0.89572 | 0.85343 | 0.79184 | 0.7082 | 0.58327 | 0.44655 | 0.28333 | -0.14535 | -2.1532 | -4.0427 | -5.8297
|  | CHURCH ROAD | FS |  |  | 0.82199 | 0.73538 | 0.51145 | 0.00090668 | -0.37313 | -0.79397 | -1.2521 | -1.8153 | -2.7203 | -3.6105 | -5.375 | -9.9852 | -12.9292 | -14.4658 | 3.5175 | 3.3301 | 3.068 | 2.7564 | 2.4134 | 2.0195 | 1.4075 | 0.64146 | -0.30445 | -1.3945 | -4.0197 | -11.2481 | -19.0963 | -28.2539 | 0.94391 | 0.7572 | 0.47601 | 0.11961 | -0.26044 | -0.69518 | -1.3941 | -2.2737 | -3.3144 | -4.505 | -7.3504 | -14.6091 | -20.354 | -23.2248
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN | MINIMUM HEADROOM | SP 02761 00827 | YES | 2.8886 | 2.5205 | 1.9555 | 1.2057 | 0.045022 | -1.4874 | -4.0842 | -7.269 | -11.0776 | -15.169 | -23.5156 | -40.8771 | -48.5253 | -51.7924 | 7.0008 | 6.4642 | 5.9413 | 5.2053 | 4.2851 | 2.8708 | 1.2528 | -1.1227 | -4.1081 | -7.314 | -13.3408 | -27.5043 | -35.9367 | -49.4326 | 2.1862 | 1.6298 | 1.0937 | 0.38624 | -0.53169 | -1.5001 | -3.5016 | -6.6761 | -10.5534 | -14.5516 | -22.8645 | -39.4497 | -46.6626 | -54.1569
|  | CIRENCESTER TOWN | CT |  |  | 2.8886 | 2.6213 | 2.2843 | 1.6266 | 0.52668 | -1.4461 | -3.6771 | -6.9548 | -11.0776 | -15.169 | -22.8575 | -40.8771 | -48.5253 | -51.7924 | 7.0008 | 6.5361 | 5.9738 | 5.2053 | 4.2851 | 2.8708 | 1.2528 | -1.1227 | -4.1081 | -7.314 | -13.3408 | -27.5043 | -34.2408 | -39.309 | 2.3259 | 1.9268 | 1.4419 | 0.71998 | -0.13743 | -1.3991 | -3.2564 | -6.5092 | -10.5534 | -14.5516 | -22.0308 | -39.4497 | -46.6626 | -49.6893
|  | CIRENCESTER TOWN | LW |  |  | 2.9375 | 2.5205 | 1.9555 | 1.2057 | 0.045022 | -1.4874 | -4.0842 | -7.269 | -10.8423 | -14.8514 | -23.5156 | -38.0706 | -41.911 | -39.2101 | 7.0107 | 6.4642 | 5.9413 | 5.3013 | 4.3599 | 3.3719 | 1.6404 | -0.50744 | -3.0986 | -6.1958 | -13.0488 | -24.0911 | -26.4828 | -23.7623 | 2.1862 | 1.6298 | 1.0937 | 0.38624 | -0.53169 | -1.5001 | -3.5016 | -6.6761 | -10.227 | -14.2173 | -22.8645 | -37.2197 | -40.6748 | -37.6222
|  | CIRENCESTER TOWN | ST |  |  | 3.0957 | 3.0287 | 2.941 | 2.7704 | 2.5482 | 2.256 | 1.6452 | 0.32961 | -1.2261 | -3.1632 | -8.3888 | -26.1794 | -38.373 | -42.4672 | 7.3226 | 7.1648 | 6.9579 | 6.6185 | 6.1865 | 5.5913 | 4.7461 | 3.7334 | 2.5253 | 1.0426 | -3.277 | -18.5453 | -29.5512 | -35.0378 | 2.6866 | 2.6 | 2.4798 | 2.236 | 1.9137 | 1.4824 | 0.89792 | 0.2095 | -1.0927 | -3.0672 | -8.4232 | -26.4021 | -38.4507 | -42.3744
|  | CIRENCESTER TOWN | FS |  |  | 2.8886 | 2.6213 | 2.2843 | 1.6266 | 0.52668 | -1.4461 | -3.6771 | -6.9548 | -11.0776 | -15.169 | -22.8575 | -40.8771 | -48.5253 | -51.7924 | 7.3307 | 7.102 | 6.8286 | 6.4734 | 6.0125 | 5.4125 | 4.5977 | 3.5885 | 2.4143 | 0.99812 | -2.8213 | -18.3309 | -35.9367 | -49.4326 | 2.6844 | 2.5276 | 2.3378 | 2.0574 | 1.6837 | 1.2038 | 0.60195 | -0.15262 | -1.0499 | -2.7625 | -7.6138 | -25.3109 | -43.9477 | -54.1569
IVER 132KV | CIPPENHAM | CLARENCE ROAD | MINIMUM HEADROOM | SU 95654 76652 | YES | 13.0886 | 12.5553 | 12.0128 | 10.9652 | 9.7642 | 8.4811 | 6.9693 | 5.3226 | 2.4762 | -2.988 | -16.1012 | -45.9248 | -66.486 | -78.3426 | 18.8816 | 18.6073 | 18.2779 | 17.7127 | 17.0443 | 16.1852 | 15.2008 | 13.9297 | 12.2233 | 8.8258 | -0.8862 | -22.5758 | -37.4524 | -46.2433 | 10.6535 | 10.1741 | 9.6907 | 8.7546 | 7.6867 | 6.5467 | 5.1859 | 3.6975 | 0.45 | -4.733 | -17.2147 | -45.5184 | -64.996 | -76.2506
|  | CLARENCE ROAD | CT |  |  | 13.6266 | 13.375 | 13.0703 | 12.226 | 11.2385 | 10.0232 | 8.6613 | 6.9955 | 2.4762 | -2.988 | -16.1012 | -45.9248 | -66.486 | -78.3426 | 18.9285 | 18.6327 | 18.2779 | 17.7127 | 17.0443 | 16.1852 | 15.2008 | 13.9297 | 12.2233 | 8.8258 | -0.8862 | -22.5758 | -37.4524 | -46.2433 | 11.1228 | 10.891 | 10.6099 | 9.8485 | 8.9627 | 7.8625 | 6.6171 | 4.8559 | 0.45 | -4.733 | -17.2147 | -45.5184 | -64.996 | -76.2506
|  | CLARENCE ROAD | LW |  |  | 13.0886 | 12.5553 | 12.0128 | 10.9652 | 9.7642 | 8.4811 | 6.9693 | 5.3226 | 3.3563 | 1.3003 | -2.6074 | -11.5007 | -16.2953 | -17.6714 | 18.8816 | 18.6073 | 18.3323 | 17.8629 | 17.292 | 16.6687 | 15.8465 | 14.9119 | 13.8369 | 12.6739 | 10.3393 | 5.4416 | 3.135 | 2.7792 | 10.6535 | 10.1741 | 9.6907 | 8.7546 | 7.6867 | 6.5467 | 5.1859 | 3.6975 | 1.9256 | 0.064775 | -3.534 | -11.636 | -15.8566 | -17.0051
|  | CLARENCE ROAD | ST |  |  | 13.9731 | 13.9513 | 13.8991 | 13.7724 | 13.5799 | 13.3261 | 13.02 | 12.6754 | 12.2701 | 11.7827 | 10.6656 | 5.4733 | 0.30264 | -5.2011 | 19.1049 | 18.9445 | 18.7436 | 18.4509 | 18.1065 | 17.695 | 17.2012 | 16.6607 | 16.0459 | 15.3312 | 13.6355 | 7.15 | -0.85679 | -12.2708 | 11.4405 | 11.4227 | 11.3782 | 11.2474 | 11.0708 | 10.8414 | 10.5541 | 10.2382 | 9.8635 | 9.3988 | 8.2812 | 3.3708 | -1.3666 | -6.2346
|  | CLARENCE ROAD | FS |  |  | 13.6266 | 13.375 | 13.0703 | 12.226 | 11.2385 | 10.0232 | 8.6613 | 6.9955 | 2.4762 | -2.988 | -16.1012 | -45.9248 | -66.486 | -78.3426 | 18.969 | 18.6793 | 18.3303 | 17.8954 | 17.3731 | 16.6982 | 15.9182 | 14.9165 | 13.6969 | 12.3918 | 9.5296 | -0.30652 | -13.4279 | -33.6704 | 11.3069 | 11.1871 | 11.0316 | 10.7529 | 10.4045 | 9.9321 | 9.3488 | 8.5497 | 7.5063 | 6.4239 | 4.2135 | -3.1473 | -9.7529 | -15.0056
MELKSHAM GSP | CHIPPENHAM | COCKLEBURY | MINIMUM HEADROOM | ST 92447 73890 | YES | 19.8534 | 19.4534 | 19.1092 | 18.3725 | 17.5866 | 16.6355 | 15.5711 | 14.4309 | 13.1085 | 11.7398 | 5.3273 | -14.815 | -24.9461 | -25.4134 | 24.3732 | 24.133 | 23.9399 | 23.5008 | 23.1399 | 22.66 | 22.1113 | 21.4634 | 19.9933 | 18.1528 | 13.4825 | -1.4627 | -8.826 | -8.9708 | 21.433 | 21.0796 | 20.7776 | 20.1415 | 19.4608 | 18.647 | 17.7293 | 16.745 | 15.6037 | 13.5864 | 7.5071 | -11.6723 | -21.2936 | -21.7083
|  | COCKLEBURY | CT |  |  | 20.1486 | 19.8269 | 19.6275 | 19.0095 | 18.4137 | 17.6253 | 16.7554 | 15.7379 | 14.2143 | 11.7398 | 5.3273 | -14.815 | -24.9461 | -25.4134 | 24.4289 | 24.133 | 23.9399 | 23.5008 | 23.1399 | 22.66 | 22.1113 | 21.4634 | 19.9933 | 18.1528 | 13.4825 | -1.4627 | -8.826 | -8.9708 | 21.6792 | 21.3867 | 21.2064 | 20.6758 | 20.1701 | 19.4924 | 18.7325 | 17.8026 | 16.005 | 13.5864 | 7.5071 | -11.6723 | -21.2936 | -21.7083
|  | COCKLEBURY | LW |  |  | 19.8534 | 19.4534 | 19.1092 | 18.3725 | 17.5866 | 16.6355 | 15.5711 | 14.4309 | 13.1085 | 11.7497 | 9.2706 | 5.0999 | 2.5503 | 1.1838 | 24.3732 | 24.1386 | 23.9494 | 23.5369 | 23.1428 | 22.6675 | 22.1321 | 21.5523 | 20.9002 | 20.2227 | 18.9689 | 16.944 | 15.6291 | 14.7466 | 21.433 | 21.0796 | 20.7776 | 20.1415 | 19.4608 | 18.647 | 17.7293 | 16.745 | 15.6037 | 14.4285 | 12.2578 | 8.5718 | 6.2999 | 5.0455
|  | COCKLEBURY | ST |  |  | 20.3172 | 20.1071 | 20.0288 | 19.7038 | 19.4566 | 19.1206 | 18.7614 | 18.394 | 17.9517 | 17.4607 | 16.4667 | 13.6069 | 10.831 | 7.7926 | 24.5092 | 24.2822 | 24.1616 | 23.8184 | 23.6041 | 23.3377 | 23.0276 | 22.7184 | 22.3328 | 21.9056 | 20.9663 | 18.0535 | 14.5394 | 9.6908 | 21.8243 | 21.6304 | 21.559 | 21.2594 | 21.0448 | 20.7631 | 20.4516 | 20.1431 | 19.7637 | 19.34 | 18.4459 | 15.7902 | 13.2589 | 10.5397
|  | COCKLEBURY | FS |  |  | 20.1486 | 19.8269 | 19.6275 | 19.0095 | 18.4137 | 17.6253 | 16.7554 | 15.7379 | 14.2143 | 11.7398 | 5.3273 | -14.815 | -24.9461 | -25.4134 | 24.4316 | 24.2058 | 23.9957 | 23.6698 | 23.2995 | 22.8741 | 22.275 | 21.568 | 20.7304 | 19.8008 | 17.7538 | 12.9735 | 7.8083 | 0.24177 | 21.7289 | 21.523 | 21.342 | 21.0047 | 20.6097 | 20.1536 | 19.4835 | 18.6831 | 17.752 | 16.7284 | 14.5594 | 10.313 | 7.5796 | 5.85
MELKSHAM GSP | FROME BSP | CODFORD | MINIMUM HEADROOM | ST 97372 39559 | YES | 1.7345 | 1.5508 | 1.3676 | 1.2003 | 0.97243 | 0.69093 | 0.31068 | -0.21467 | -0.84838 | -1.4701 | -2.8629 | -5.2234 | -6.6064 | -7.0137 | 1.3128 | 1.257 | 1.1893 | 1.1139 | 1.0269 | 0.77898 | 0.50611 | 0.082188 | -0.42831 | -0.92846 | -2.0099 | -5.122 | -9.641 | -12.1213 | 1.3901 | 1.3247 | 1.2347 | 1.108 | 0.96039 | 0.68529 | 0.32325 | -0.20975 | -0.85454 | -1.4777 | -2.9073 | -6.7068 | -12.3168 | -15.3751
|  | CODFORD | CT |  |  | 1.7588 | 1.6029 | 1.4271 | 1.23 | 1.0149 | 0.69093 | 0.33403 | -0.2054 | -0.84838 | -1.4701 | -2.6171 | -5.2234 | -6.2598 | -6.5663 | 1.3128 | 1.257 | 1.1893 | 1.1139 | 1.0269 | 0.77898 | 0.50611 | 0.082188 | -0.42831 | -0.92846 | -1.8467 | -3.9436 | -4.7376 | -5.0238 | 1.4317 | 1.3626 | 1.2425 | 1.108 | 0.96039 | 0.68529 | 0.33204 | -0.20975 | -0.85454 | -1.4777 | -2.6367 | -5.2685 | -6.2783 | -6.5712
|  | CODFORD | LW |  |  | 1.7345 | 1.5508 | 1.3676 | 1.2003 | 0.97243 | 0.73309 | 0.31068 | -0.21467 | -0.7971 | -1.4469 | -2.8629 | -5.1324 | -5.547 | -4.8294 | 1.3253 | 1.2667 | 1.21 | 1.147 | 1.0447 | 0.87701 | 0.54995 | 0.13631 | -0.32192 | -0.85254 | -2.0099 | -3.8039 | -4.0876 | -3.4626 | 1.3901 | 1.3247 | 1.2347 | 1.1206 | 0.96171 | 0.73875 | 0.32325 | -0.20218 | -0.78842 | -1.4457 | -2.9073 | -5.1936 | -5.588 | -4.8317
|  | CODFORD | ST |  |  | 1.8472 | 1.777 | 1.6886 | 1.5698 | 1.4144 | 1.2235 | 0.97608 | 0.67291 | 0.30924 | -0.12824 | -1.2838 | -4.6542 | -6.6064 | -7.0137 | 1.3452 | 1.3234 | 1.2933 | 1.2521 | 1.1956 | 1.1197 | 0.99964 | 0.76317 | 0.48177 | 0.13487 | -0.80813 | -3.5699 | -5.1645 | -5.5197 | 1.4403 | 1.4337 | 1.4061 | 1.343 | 1.239 | 1.1061 | 0.93191 | 0.66789 | 0.3037 | -0.13835 | -1.3199 | -4.7599 | -6.731 | -7.1225
|  | CODFORD | FS |  |  | 1.7588 | 1.6029 | 1.4271 | 1.23 | 1.0149 | 0.69093 | 0.33403 | -0.2054 | -0.84838 | -1.4701 | -2.6171 | -5.2234 | -6.2598 | -6.5663 | 1.3222 | 1.2911 | 1.2497 | 1.1956 | 1.125 | 1.0337 | 0.83505 | 0.56815 | 0.27143 | -0.082842 | -1.1109 | -5.122 | -9.641 | -12.1213 | 1.4374 | 1.4316 | 1.3651 | 1.2658 | 1.1412 | 0.98213 | 0.78457 | 0.4464 | 0.06172 | -0.39267 | -1.6799 | -6.7068 | -12.3168 | -15.3751
IVER 132KV | DENHAM | COKES LANE | MINIMUM HEADROOM | SU 99240 97483 | YES | 5.5474 | 5.4291 | 5.3061 | 5.1193 | 4.8874 | 4.6283 | 4.4436 | 4.258 | 4.0306 | 3.7845 | 3.2306 | 1.4635 | -0.033933 | -0.83679 | 7.2183 | 7.1405 | 7.049 | 6.9413 | 6.7917 | 6.6206 | 6.4303 | 6.1975 | 5.9194 | 5.5753 | 4.6562 | 1.7232 | -0.34819 | -1.5356 | 5.383 | 5.2826 | 5.1774 | 5.0091 | 4.7891 | 4.5732 | 4.4124 | 4.2388 | 3.9047 | 3.4928 | 2.3971 | -1.0412 | -3.2761 | -4.0569
|  | COKES LANE | CT |  |  | 5.6249 | 5.55 | 5.4777 | 5.3441 | 5.1624 | 5 | 4.8763 | 4.7323 | 4.477 | 4.2136 | 3.6693 | 1.4635 | -0.033933 | -0.83679 | 7.2605 | 7.2089 | 7.1559 | 7.0784 | 6.9484 | 6.8514 | 6.7784 | 6.6977 | 6.5706 | 6.4337 | 5.811 | 4.4252 | 3.5179 | 2.9935 | 5.4582 | 5.3979 | 5.3401 | 5.2212 | 5.0414 | 4.8947 | 4.7921 | 4.6815 | 4.4855 | 4.2835 | 3.8079 | 1.7178 | 0.31408 | -0.44227
|  | COKES LANE | LW |  |  | 5.5474 | 5.4291 | 5.3061 | 5.1193 | 4.8874 | 4.6283 | 4.4436 | 4.258 | 4.0306 | 3.7845 | 3.2306 | 1.9916 | 1.3994 | 1.3819 | 7.2358 | 7.1737 | 7.109 | 7.0161 | 6.8838 | 6.7592 | 6.6675 | 6.5701 | 6.4516 | 6.3168 | 5.9952 | 5.2502 | 4.9652 | 5.0199 | 5.383 | 5.2826 | 5.1774 | 5.0091 | 4.7891 | 4.5732 | 4.4124 | 4.2467 | 4.0434 | 3.8197 | 3.3055 | 2.1395 | 1.6288 | 1.6587
|  | COKES LANE | ST |  |  | 5.6202 | 5.5454 | 5.463 | 5.3768 | 5.2352 | 5.1238 | 5.0462 | 4.954 | 4.8425 | 4.707 | 4.3877 | 3.5937 | 2.9481 | 2.3745 | 7.2563 | 7.2031 | 7.1433 | 7.0812 | 6.9619 | 6.8784 | 6.8073 | 6.7231 | 6.625 | 6.5072 | 6.223 | 5.5146 | 4.893 | 4.19 | 5.4543 | 5.3948 | 5.3277 | 5.2565 | 5.1174 | 5.023 | 4.952 | 4.8658 | 4.7612 | 4.6333 | 4.3278 | 3.5702 | 2.9595 | 2.4131
|  | COKES LANE | FS |  |  | 5.6249 | 5.55 | 5.4777 | 5.3441 | 5.1624 | 5 | 4.8763 | 4.7323 | 4.477 | 4.2136 | 3.6693 | 1.4635 | -0.033933 | -0.83679 | 7.2183 | 7.1405 | 7.049 | 6.9413 | 6.7917 | 6.6206 | 6.4303 | 6.1975 | 5.9194 | 5.5753 | 4.6562 | 1.7232 | -0.34819 | -1.5356 | 5.4113 | 5.3265 | 5.2296 | 5.1028 | 4.9268 | 4.7254 | 4.5059 | 4.2388 | 3.9047 | 3.4928 | 2.3971 | -1.0412 | -3.2761 | -4.0569
LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK | MINIMUM HEADROOM | SU 65893 02686 | YES | 0.98399 | 0.80054 | 0.59575 | 0.12314 | -0.37364 | -0.89183 | -1.4584 | -2.0806 | -3.1401 | -5.0891 | -9.5619 | -17.4228 | -19.7525 | -21.6003 | 2.12 | 1.9498 | 1.761 | 1.4933 | 1.2049 | 0.88347 | 0.49385 | 0.051281 | -0.78123 | -2.2245 | -5.5619 | -11.3919 | -24.3219 | -51.9767 | -0.10695 | -0.2787 | -0.46575 | -0.88437 | -1.3261 | -1.7892 | -2.2988 | -2.8619 | -3.5166 | -5.3588 | -9.6281 | -17.133 | -19.4417 | -21.3414
|  | COLLEGE PARK | CT |  |  | 1.2164 | 1.135 | 1.0537 | 0.76269 | 0.46347 | 0.14851 | -0.1644 | -0.49227 | -0.99197 | -1.5117 | -2.5591 | -5.5568 | -7.2482 | -7.9086 | 2.12 | 1.9498 | 1.761 | 1.4933 | 1.2049 | 0.88547 | 0.54037 | 0.16242 | -0.3521 | -0.92568 | -2.2785 | -7.2254 | -15.0829 | -28.1718 | 0.10808 | 0.031225 | -0.04548 | -0.31276 | -0.57907 | -0.8561 | -1.1317 | -1.4212 | -1.866 | -2.3338 | -3.2756 | -5.9603 | -7.5042 | -8.1515
|  | COLLEGE PARK | LW |  |  | 0.98399 | 0.80054 | 0.59575 | 0.12314 | -0.37364 | -0.89183 | -1.4584 | -2.0806 | -3.1401 | -5.0891 | -9.5619 | -17.4228 | -19.7525 | -21.6003 | 2.1403 | 2.0508 | 1.9495 | 1.7683 | 1.5743 | 1.3663 | 1.1223 | 0.41319 | -0.78123 | -2.2245 | -5.5619 | -11.3919 | -13.2833 | -14.9234 | -0.10695 | -0.2787 | -0.46575 | -0.88437 | -1.3261 | -1.7892 | -2.2988 | -2.8619 | -3.5166 | -5.3588 | -9.6281 | -17.133 | -19.4417 | -21.3414
|  | COLLEGE PARK | ST |  |  | 1.2807 | 1.2321 | 1.1848 | 1.1752 | 1.1707 | 1.161 | 1.1429 | 1.1191 | 1.0635 | 0.99637 | 0.81661 | -0.53014 | -2.1128 | -3.582 | 2.1413 | 1.982 | 1.8039 | 1.6302 | 1.4359 | 1.212 | 0.95705 | 0.67142 | 0.28016 | -0.15649 | -1.2149 | -5.6354 | -13.619 | -27.1004 | 0.16571 | 0.11917 | 0.073514 | 0.064753 | 0.060022 | 0.050089 | 0.0322 | 0.0085111 | -0.052864 | -0.1242 | -0.32624 | -1.5882 | -3.091 | -4.4987
|  | COLLEGE PARK | FS |  |  | 1.2164 | 1.135 | 1.0537 | 0.76269 | 0.46347 | 0.14851 | -0.1644 | -0.49227 | -0.99197 | -1.5117 | -2.5591 | -5.5568 | -7.2482 | -7.9086 | 2.1269 | 1.9678 | 1.7803 | 1.5164 | 1.2177 | 0.88347 | 0.49385 | 0.051281 | -0.57283 | -1.2869 | -3.0829 | -10.156 | -24.3219 | -51.9767 | 0.16045 | 0.14078 | 0.11553 | 0.069449 | 0.021209 | -0.033969 | -0.094153 | -0.16851 | -0.30573 | -0.46195 | -0.80731 | -1.8787 | -3.4198 | -5.2255
BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS | MINIMUM HEADROOM | SU 88285 81857 | YES | 9.9898 | 9.5039 | 9.0155 | 8.2971 | 7.4973 | 6.7459 | 5.782 | 4.6755 | 3.3743 | 1.124 | -5.5893 | -17.4812 | -21.5907 | -24.2734 | 12.4582 | 12.1997 | 11.9414 | 11.6092 | 11.2136 | 10.6966 | 10.107 | 9.2919 | 8.2321 | 6.2063 | 1.274 | -7.0774 | -9.5808 | -11.351 | 9.247 | 8.8374 | 8.4143 | 7.779 | 7.0653 | 6.385 | 5.4964 | 4.4724 | 3.2742 | 1.0263 | -5.3508 | -16.5701 | -20.3539 | -22.8375
|  | CORDWALLIS | CT |  |  | 10.2895 | 9.9833 | 9.6384 | 9.0448 | 8.3919 | 7.633 | 6.7754 | 5.6435 | 3.9693 | 1.124 | -5.5893 | -17.4812 | -21.5907 | -24.2734 | 12.4911 | 12.2525 | 11.9756 | 11.6163 | 11.2136 | 10.6966 | 10.107 | 9.2919 | 8.2321 | 6.2063 | 1.274 | -7.0774 | -9.5808 | -11.351 | 9.5182 | 9.2525 | 8.9499 | 8.4186 | 7.8319 | 7.1307 | 6.3371 | 5.2793 | 3.7186 | 1.0263 | -5.3508 | -16.5701 | -20.3539 | -22.8375
|  | CORDWALLIS | LW |  |  | 9.9898 | 9.5039 | 9.0155 | 8.2971 | 7.4973 | 6.7459 | 5.782 | 4.6755 | 3.3743 | 1.992 | -0.75826 | -6.7002 | -11.8804 | -15.8591 | 12.4582 | 12.1997 | 11.9414 | 11.6092 | 11.2149 | 10.8354 | 10.2698 | 9.5901 | 8.8208 | 7.9786 | 6.2299 | 2.8114 | -2.2658 | -5.2555 | 9.247 | 8.8374 | 8.4143 | 7.779 | 7.0653 | 6.385 | 5.4964 | 4.4724 | 3.2742 | 1.9957 | -0.58275 | -6.0614 | -11.1009 | -14.8733
|  | CORDWALLIS | ST |  |  | 10.4806 | 10.3242 | 10.1445 | 9.9742 | 9.7745 | 9.5801 | 9.3263 | 9.0158 | 8.6602 | 8.2403 | 7.1638 | 2.7267 | -0.99909 | -3.9394 | 12.6042 | 12.4676 | 12.3072 | 12.1395 | 11.942 | 11.7245 | 11.4508 | 11.1208 | 10.7432 | 10.2918 | 9.1596 | 5.0574 | 1.0725 | -3.0987 | 9.6962 | 9.5735 | 9.4288 | 9.2805 | 9.1049 | 8.9249 | 8.6886 | 8.4002 | 8.0673 | 7.6696 | 6.6827 | 2.4065 | -1.0776 | -3.5782
|  | CORDWALLIS | FS |  |  | 10.2895 | 9.9833 | 9.6384 | 9.0448 | 8.3919 | 7.633 | 6.7754 | 5.6435 | 3.9693 | 1.124 | -5.5893 | -17.4812 | -21.5907 | -24.2734 | 12.5558 | 12.3587 | 12.134 | 11.8995 | 11.6234 | 11.306 | 10.8987 | 10.374 | 9.7358 | 9.0344 | 7.4261 | 2.2358 | -3.8895 | -11.2737 | 9.6557 | 9.4864 | 9.2938 | 9.0568 | 8.7835 | 8.4816 | 8.0949 | 7.5908 | 6.9634 | 6.2889 | 4.6485 | -0.39085 | -5.1645 | -8.4685
MANNINGTON GSP | LYTCHETT | CORFE MULLEN | MINIMUM HEADROOM | SY 98583 96071 | YES | 19.9668 | 19.777 | 19.5872 | 19.3436 | 18.7348 | 17.5089 | 15.5457 | 13.2114 | 10.7536 | 8.0713 | 2.2312 | -14.5912 | -31.0657 | -36.4586 | 18.4543 | 18.0714 | 17.7123 | 17.1896 | 16.4762 | 15.687 | 14.3984 | 12.8249 | 11.13 | 9.242 | 5.0843 | -5.3294 | -17.7305 | -21.7851 | 16.9152 | 16.3214 | 15.7791 | 14.956 | 13.8785 | 12.6908 | 10.856 | 8.656 | 6.3043 | 3.7239 | -1.9091 | -14.6621 | -30.4026 | -35.5665
|  | CORFE MULLEN | CT |  |  | 19.9668 | 19.777 | 19.5872 | 19.3436 | 19.0101 | 18.3396 | 16.8307 | 14.77 | 12.2294 | 9.6941 | 4.7249 | -14.5912 | -31.0657 | -36.4586 | 18.4925 | 18.1675 | 17.7867 | 17.2509 | 16.6217 | 15.6978 | 14.6424 | 13.1523 | 11.3668 | 9.5712 | 6.0389 | -5.3294 | -17.7305 | -21.7851 | 17.1004 | 16.6796 | 16.2251 | 15.4842 | 14.6199 | 13.3821 | 11.9701 | 10.0133 | 7.5867 | 5.1619 | 0.41904 | -14.6621 | -30.4026 | -35.5665
|  | CORFE MULLEN | LW |  |  | 20.0083 | 19.816 | 19.6593 | 19.393 | 18.7348 | 17.5089 | 15.5457 | 13.2114 | 10.7536 | 8.0713 | 2.2312 | -8.3039 | -11.7204 | -10.5275 | 18.4543 | 18.0714 | 17.7123 | 17.1896 | 16.4762 | 15.687 | 14.3984 | 12.8249 | 11.13 | 9.242 | 5.0843 | -2.1477 | -4.234 | -3.1796 | 16.9152 | 16.3214 | 15.7791 | 14.956 | 13.8785 | 12.6908 | 10.856 | 8.656 | 6.3043 | 3.7239 | -1.9091 | -11.9493 | -15.1197 | -13.9025
|  | CORFE MULLEN | ST |  |  | 20.0979 | 20.0158 | 19.9591 | 19.8403 | 19.6754 | 19.4646 | 19.1814 | 18.8812 | 18.5094 | 17.4693 | 14.6932 | 5.0272 | -2.1159 | -5.4236 | 18.6767 | 18.5258 | 18.3701 | 18.123 | 17.7941 | 17.3569 | 16.7832 | 16.1196 | 15.3991 | 14.5261 | 12.1892 | 4.4202 | -1.5897 | -5.3018 | 17.3642 | 17.1902 | 17.0136 | 16.7236 | 16.3301 | 15.8222 | 15.1481 | 14.366 | 13.532 | 12.5145 | 9.7818 | 0.33851 | -6.626 | -9.763
|  | CORFE MULLEN | FS |  |  | 19.9668 | 19.777 | 19.5872 | 19.3436 | 19.0101 | 18.3396 | 16.8307 | 14.77 | 12.2294 | 9.6941 | 4.7249 | -14.5912 | -31.0657 | -36.4586 | 18.6213 | 18.4323 | 18.2297 | 17.9524 | 17.5763 | 17.0815 | 16.4715 | 15.6993 | 14.8397 | 13.8781 | 11.4729 | 2.9469 | -6.6164 | -14.6635 | 17.2926 | 17.077 | 16.8492 | 16.5228 | 16.0882 | 15.5131 | 14.803 | 13.8977 | 12.8754 | 11.7388 | 8.9226 | -1.1404 | -11.7034 | -18.0211
MELKSHAM GSP | NORRINGTON | CORSHAM | MINIMUM HEADROOM | ST 86766 69583 | YES | -1.1544 | -1.6883 | -2.2103 | -2.9133 | -3.8373 | -5.2659 | -7.4392 | -9.8765 | -12.5057 | -15.3194 | -21.1892 | -31.0377 | -35.9454 | -38.1163 | 1.6942 | 1.3749 | 1.0009 | 0.46076 | -0.14097 | -1.579 | -3.2055 | -5.2081 | -7.4518 | -9.573 | -13.9122 | -22.2271 | -26.4819 | -33.293 | -0.78256 | -1.3394 | -1.8828 | -2.5855 | -3.5065 | -4.9923 | -7.2399 | -9.7194 | -12.3543 | -15.1555 | -20.9731 | -30.7045 | -35.3196 | -37.659
|  | CORSHAM | CT |  |  | -0.99758 | -1.3941 | -1.8597 | -2.5649 | -3.377 | -4.9944 | -6.8019 | -9.137 | -11.9482 | -14.6096 | -19.4571 | -30.8052 | -35.9454 | -38.1163 | 1.7074 | 1.4221 | 1.0009 | 0.46076 | -0.14097 | -1.579 | -3.2055 | -5.2081 | -7.4518 | -9.573 | -13.3934 | -22.2271 | -26.4819 | -29.4007 | -0.67933 | -1.1174 | -1.636 | -2.344 | -3.1263 | -4.8148 | -6.7105 | -9.1022 | -11.9305 | -14.6005 | -19.4079 | -30.4878 | -35.3196 | -37.3425
|  | CORSHAM | LW |  |  | -1.1544 | -1.6883 | -2.2103 | -2.9133 | -3.8373 | -5.2659 | -7.4392 | -9.8765 | -12.5057 | -15.3194 | -21.1892 | -31.0377 | -33.957 | -32.5328 | 1.6942 | 1.3749 | 1.0303 | 0.55713 | -0.087853 | -1.287 | -3.1213 | -5.1125 | -7.175 | -9.3545 | -13.9122 | -21.3481 | -23.2698 | -21.9121 | -0.78256 | -1.3394 | -1.8828 | -2.5855 | -3.5065 | -4.9923 | -7.2399 | -9.7194 | -12.3543 | -15.1555 | -20.9731 | -30.7045 | -33.4262 | -31.9584
|  | CORSHAM | ST |  |  | -0.68933 | -0.81319 | -0.97597 | -1.2332 | -1.5804 | -2.4095 | -3.5068 | -4.7105 | -5.9863 | -7.4359 | -11.0956 | -22.6675 | -30.7245 | -33.853 | 1.8963 | 1.7876 | 1.6469 | 1.4315 | 1.1206 | 0.22045 | -0.89066 | -2.0595 | -3.2627 | -4.5852 | -7.822 | -17.7081 | -24.8373 | -28.3418 | -0.35661 | -0.49424 | -0.6791 | -0.97022 | -1.3546 | -2.3163 | -3.5133 | -4.7976 | -6.1521 | -7.6838 | -11.4938 | -23.341 | -31.4208 | -34.3287
|  | CORSHAM | FS |  |  | -0.99758 | -1.3941 | -1.8597 | -2.5649 | -3.377 | -4.9944 | -6.8019 | -9.137 | -11.9482 | -14.6096 | -19.4571 | -30.8052 | -35.9454 | -38.1163 | 1.8719 | 1.7386 | 1.5784 | 1.3639 | 1.0376 | 0.2016 | -0.8505 | -2.0142 | -3.1811 | -4.4094 | -7.3177 | -16.1124 | -25.7979 | -33.293 | -0.39044 | -0.55991 | -0.7655 | -1.0626 | -1.4509 | -2.3453 | -3.4812 | -4.7546 | -6.0597 | -7.4621 | -10.837 | -20.999 | -31.6288 | -37.659
EAST CLAYDON GSP | BICESTER NORTH | COTTISFORD | MINIMUM HEADROOM | SP 59021 31128 | NO | -1.7025 | -2.5061 | -3.4755 | -4.5662 | -5.7739 | -7.7215 | -9.8673 | -13.2206 | -17.2193 | -21.2948 | -30.6925 | -45.3543 | -51.9935 | -55.0533 | -0.37897 | -1.0187 | -1.7919 | -2.6657 | -3.6379 | -5.2076 | -6.946 | -9.6506 | -12.871 | -16.0405 | -24.6879 | -43.0969 | -49.4834 | -54.0356 | -1.7076 | -2.4836 | -3.4195 | -4.4755 | -5.6471 | -7.5337 | -9.6483 | -12.9925 | -16.9809 | -21.0055 | -31.9844 | -54.5626 | -62.4235 | -67.8978
|  | COTTISFORD | CT |  |  | -1.7025 | -2.5061 | -3.4755 | -4.5662 | -5.7739 | -7.7215 | -9.8673 | -13.2206 | -17.2193 | -21.0729 | -28.0857 | -44.2077 | -50.0554 | -51.9197 | -0.37897 | -1.0187 | -1.7919 | -2.6657 | -3.6379 | -5.2076 | -6.946 | -9.6506 | -12.871 | -16 | -21.6924 | -34.8265 | -39.6968 | -41.4727 | -1.7076 | -2.4836 | -3.4195 | -4.4755 | -5.6471 | -7.5337 | -9.6483 | -12.9925 | -16.9809 | -20.8377 | -27.8552 | -44.0056 | -49.9118 | -51.8715
|  | COTTISFORD | LW |  |  | -1.5856 | -2.4667 | -3.3311 | -4.2865 | -5.6399 | -7.0597 | -9.7493 | -13.1766 | -16.9878 | -21.2948 | -30.6925 | -45.3543 | -48.2028 | -44.0432 | -0.26572 | -0.95655 | -1.6328 | -2.3914 | -3.4704 | -4.6046 | -6.7617 | -9.5115 | -12.5763 | -16.0405 | -23.5961 | -35.39 | -37.8938 | -34.9001 | -1.5962 | -2.4478 | -3.2835 | -4.2096 | -5.5208 | -6.8979 | -9.5032 | -12.9153 | -16.7136 | -21.0055 | -30.3671 | -44.9809 | -47.9491 | -44.0098
|  | COTTISFORD | ST |  |  | -1.238 | -1.5205 | -1.9101 | -2.521 | -3.2911 | -4.2873 | -5.6067 | -7.249 | -9.205 | -11.6418 | -18.2837 | -38.9546 | -51.9935 | -55.0533 | -0.0046655 | -0.23188 | -0.541 | -1.0606 | -1.6958 | -2.5124 | -3.601 | -4.9327 | -6.5365 | -8.5201 | -13.9249 | -30.7525 | -41.5565 | -44.3844 | -1.256 | -1.5341 | -1.9106 | -2.5231 | -3.2819 | -4.2576 | -5.5522 | -7.1473 | -9.0584 | -11.497 | -18.1476 | -38.8396 | -51.9846 | -55.1928
|  | COTTISFORD | FS |  |  | -1.7025 | -2.5061 | -3.4755 | -4.5662 | -5.7739 | -7.7215 | -9.8673 | -13.2206 | -17.2193 | -21.0729 | -28.0857 | -44.2077 | -50.0554 | -51.9197 | -0.039387 | -0.27424 | -0.59143 | -1.0383 | -1.623 | -2.6861 | -4.5673 | -7.1422 | -10.4178 | -14.5042 | -24.6879 | -43.0969 | -49.4834 | -54.0356 | -1.2945 | -1.5828 | -1.9726 | -2.525 | -3.4462 | -5.0805 | -7.3815 | -10.5328 | -14.5381 | -19.5334 | -31.9844 | -54.5626 | -62.4235 | -67.8978
BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES | MINIMUM HEADROOM | SU 70990 69570 | YES | 13.383 | 12.532 | 11.3603 | 10.2765 | 9.2882 | 7.7931 | 6.0697 | 3.556 | 0.92934 | -2.0327 | -8.3214 | -18.0157 | -21.9671 | -23.3281 | 14.0129 | 13.3298 | 12.3618 | 11.5628 | 10.9283 | 9.7459 | 8.4334 | 6.3996 | 4.1699 | 1.7302 | -3.2285 | -17.0911 | -32.6343 | -37.8471 | 14.0281 | 13.1553 | 12.0071 | 11.0165 | 10.1075 | 8.7139 | 7.0572 | 4.5872 | 1.8685 | -1.073 | -7.3052 | -24.0312 | -42.9871 | -49.3609
|  | COURAGES | CT |  |  | 13.4288 | 12.5781 | 11.3603 | 10.2765 | 9.3865 | 7.7931 | 6.2568 | 3.7275 | 0.92934 | -2.0327 | -7.3155 | -18.0157 | -21.9671 | -23.3281 | 14.0513 | 13.3485 | 12.3618 | 11.5628 | 11.0369 | 9.7459 | 8.5009 | 6.4403 | 4.1699 | 1.7302 | -2.5969 | -11.3574 | -14.8549 | -16.5616 | 14.0473 | 13.1771 | 12.0071 | 11.0165 | 10.2226 | 8.7139 | 7.1953 | 4.6792 | 1.8685 | -1.073 | -6.3096 | -17.031 | -20.9949 | -22.3974
|  | COURAGES | LW |  |  | 13.383 | 12.532 | 11.5151 | 10.4449 | 9.2882 | 8.0044 | 6.0697 | 3.556 | 1.0435 | -1.9614 | -8.3214 | -17.8991 | -20.1672 | -17.8889 | 14.0129 | 13.3298 | 12.4926 | 11.6869 | 10.9283 | 9.9899 | 8.4334 | 6.3996 | 4.3797 | 1.9364 | -3.2285 | -10.9661 | -12.901 | -11.2141 | 14.0281 | 13.1553 | 12.1423 | 11.1547 | 10.1075 | 8.9379 | 7.0572 | 4.5872 | 2.0511 | -0.95856 | -7.3052 | -16.9105 | -19.2191 | -16.9929
|  | COURAGES | ST |  |  | 13.6986 | 13.1122 | 12.2528 | 11.5899 | 11.1462 | 10.2569 | 9.3464 | 8.0006 | 6.6403 | 4.7739 | 0.27412 | -12.6602 | -20.9452 | -22.8642 | 14.2284 | 13.7021 | 12.9158 | 12.3156 | 11.9824 | 11.3361 | 10.7829 | 9.814 | 8.6794 | 7.1184 | 3.3982 | -7.2461 | -14.3457 | -16.5465 | 14.3479 | 13.7767 | 12.944 | 12.2822 | 11.7999 | 10.9641 | 10.1547 | 8.9436 | 7.6076 | 5.7731 | 1.2357 | -11.7856 | -20.1184 | -22.1104
|  | COURAGES | FS |  |  | 13.4288 | 12.5781 | 11.3603 | 10.2765 | 9.3865 | 7.7931 | 6.2568 | 3.7275 | 0.92934 | -2.0327 | -7.3155 | -18.0157 | -21.9671 | -23.3281 | 14.3572 | 13.9988 | 13.5064 | 13.0059 | 12.5563 | 11.9878 | 11.1568 | 10.0117 | 8.6919 | 6.9572 | 1.983 | -17.0911 | -32.6343 | -37.8471 | 14.486 | 14.062 | 13.464 | 12.8318 | 12.1903 | 11.3447 | 10.3701 | 9.0387 | 7.4854 | 5.3011 | -0.87038 | -24.0312 | -42.9871 | -49.3609
BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE | MINIMUM HEADROOM | SU 85415 55937 | YES | 12.2008 | 11.3089 | 10.5581 | 9.636 | 8.5527 | 7.0954 | 4.9562 | 2.5737 | 0.016912 | -2.7511 | -8.6085 | -18.9652 | -21.8849 | -23.1472 | 13.2816 | 12.5624 | 11.8806 | 11.3566 | 10.6832 | 9.4517 | 7.6853 | 5.7494 | 3.7499 | 1.6077 | -2.8994 | -10.6491 | -14.6804 | -21.4589 | 11.2671 | 10.4615 | 9.7707 | 8.9212 | 7.9309 | 6.4705 | 4.382 | 2.033 | -0.526 | -3.2795 | -9.0776 | -19.2579 | -22.0654 | -23.1332
|  | COVE | CT |  |  | 12.487 | 11.5158 | 10.7444 | 10.017 | 9.2276 | 7.7141 | 6.0293 | 3.8666 | 1.2507 | -1.2445 | -5.8216 | -16.7413 | -21.5362 | -23.1472 | 13.3867 | 12.5624 | 11.8806 | 11.3566 | 10.7808 | 9.4517 | 7.9493 | 6.0771 | 3.9677 | 1.9793 | -1.6336 | -10.2544 | -14.6804 | -17.9908 | 11.5458 | 10.6548 | 9.9483 | 9.2982 | 8.5932 | 7.1157 | 5.4169 | 3.1572 | 0.52251 | -1.9677 | -6.4786 | -17.0519 | -21.6321 | -23.1332
|  | COVE | LW |  |  | 12.2008 | 11.3089 | 10.5581 | 9.636 | 8.5527 | 7.0954 | 4.9562 | 2.5737 | 0.016912 | -2.7511 | -8.6085 | -18.9652 | -21.8849 | -20.2005 | 13.2816 | 12.617 | 12.0399 | 11.4252 | 10.6832 | 9.4738 | 7.6853 | 5.7494 | 3.7499 | 1.6077 | -2.8994 | -10.6491 | -12.6541 | -11.3685 | 11.2671 | 10.4615 | 9.7707 | 8.9212 | 7.9309 | 6.4705 | 4.382 | 2.033 | -0.526 | -3.2795 | -9.0776 | -19.2579 | -22.0654 | -20.3325
|  | COVE | ST |  |  | 12.689 | 11.9847 | 11.5109 | 11.253 | 10.9169 | 10.1426 | 9.1721 | 8.095 | 6.9645 | 5.6634 | 2.3627 | -8.1261 | -15.3844 | -17.8487 | 13.5374 | 12.9199 | 12.4701 | 12.2285 | 11.9206 | 11.1081 | 10.1065 | 9.0347 | 7.9222 | 6.681 | 3.6429 | -5.5217 | -12.1661 | -15.8628 | 11.7202 | 11.064 | 10.6194 | 10.3921 | 10.0988 | 9.2989 | 8.3069 | 7.2197 | 5.9823 | 4.5746 | 1.047 | -9.7943 | -16.9353 | -19.2376
|  | COVE | FS |  |  | 12.487 | 11.5158 | 10.7444 | 10.017 | 9.2276 | 7.7141 | 6.0293 | 3.8666 | 1.2507 | -1.2445 | -5.8216 | -16.7413 | -21.5362 | -23.1472 | 13.6329 | 13.3235 | 13.0255 | 12.7565 | 12.4589 | 11.7501 | 10.8981 | 9.9804 | 9.0227 | 8.0232 | 5.6053 | -2.2185 | -12.0896 | -21.4589 | 11.8399 | 11.5346 | 11.2572 | 10.9921 | 10.6991 | 10.0024 | 9.1608 | 8.2547 | 7.3163 | 6.2673 | 3.6619 | -4.8671 | -14.4883 | -20.3151
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL | MINIMUM HEADROOM | SP 56113 03074 | YES | 4.6149 | 3.562 | 2.5122 | 0.76418 | -1.3401 | -3.7034 | -6.5825 | -10.0233 | -13.5809 | -17.1043 | -30.1358 | -63.8107 | -83.4717 | -90.8655 | 8.4904 | 7.7544 | 6.9515 | 5.6112 | 4.1812 | 2.3833 | 0.5102 | -2.2273 | -5.4352 | -8.703 | -18.783 | -44.3326 | -59.2893 | -65.1546 | 3.4126 | 2.4338 | 1.4708 | -0.19749 | -2.1888 | -4.4117 | -7.1999 | -10.545 | -13.9898 | -17.4277 | -29.9063 | -62.2147 | -81.0804 | -88.2498
|  | COWLEY LOCAL | CT |  |  | 4.9594 | 4.1243 | 3.1942 | 1.5148 | -0.3085 | -2.6549 | -4.9869 | -8.3164 | -12.394 | -16.8773 | -30.1358 | -63.8107 | -83.4717 | -90.8655 | 8.4974 | 7.7544 | 6.9515 | 5.6112 | 4.1812 | 2.3833 | 0.5102 | -2.2273 | -5.4352 | -8.703 | -18.783 | -44.3326 | -59.2893 | -65.1546 | 3.703 | 2.9141 | 2.0412 | 0.4339 | -1.2738 | -3.4754 | -5.717 | -8.9361 | -12.8562 | -17.187 | -29.9063 | -62.2147 | -81.0804 | -88.2498
|  | COWLEY LOCAL | LW |  |  | 4.6149 | 3.562 | 2.5122 | 0.76418 | -1.3401 | -3.7034 | -6.5825 | -10.0233 | -13.5809 | -17.1043 | -24.6998 | -38.3646 | -42.9251 | -43.5819 | 8.4904 | 7.7678 | 7.0737 | 5.8711 | 4.4155 | 2.7977 | 0.70285 | -1.8917 | -4.4953 | -7.0509 | -12.5897 | -22.3674 | -26.0114 | -28.8475 | 3.4126 | 2.4338 | 1.4708 | -0.19749 | -2.1888 | -4.4117 | -7.1999 | -10.545 | -13.9898 | -17.4277 | -24.8403 | -38.1325 | -42.626 | -43.2749
|  | COWLEY LOCAL | ST |  |  | 5.4073 | 4.9913 | 4.5276 | 3.5191 | 2.4539 | 1.3072 | 0.1121 | -1.4465 | -3.1002 | -4.7354 | -9.0385 | -23.5196 | -33.7097 | -38.1391 | 8.8043 | 8.3692 | 7.9139 | 6.8454 | 5.7886 | 4.7 | 3.4933 | 1.9699 | 0.30691 | -1.3337 | -5.5802 | -19.6455 | -32.5353 | -45.0862 | 4.1329 | 3.7516 | 3.3335 | 2.2957 | 1.2631 | 0.17226 | -1.0234 | -2.5499 | -4.1885 | -5.8237 | -10.1394 | -24.561 | -34.6953 | -38.946
|  | COWLEY LOCAL | FS |  |  | 4.9594 | 4.1243 | 3.1942 | 1.5148 | -0.3085 | -2.6549 | -4.9869 | -8.3164 | -12.394 | -16.8773 | -30.1358 | -63.8107 | -83.4717 | -90.8655 | 8.821 | 8.4505 | 8.0188 | 7.3266 | 6.5176 | 5.5653 | 4.5549 | 3.3439 | 1.8718 | 0.28426 | -3.6424 | -17.7096 | -37.5352 | -63.7771 | 4.1594 | 3.8691 | 3.5181 | 2.8944 | 2.1548 | 1.2569 | 0.33821 | -0.77018 | -2.0727 | -3.46 | -6.883 | -18.7021 | -31.4875 | -39.9537
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD | MINIMUM HEADROOM | SU 78275 50779 | YES | 2.9338 | 2.7954 | 2.6434 | 2.4607 | 2.3236 | 2.0733 | 1.3416 | 0.36641 | -0.97076 | -2.5515 | -6.1203 | -12.8306 | -15.1729 | -16.7098 | 3.8818 | 3.8136 | 3.6918 | 3.5957 | 3.4862 | 3.3275 | 2.8036 | 2.0673 | 1.0912 | -0.08885 | -2.7643 | -7.673 | -9.2811 | -10.4566 | 3.0768 | 2.9085 | 2.7259 | 2.466 | 2.1487 | 1.6254 | 0.92538 | -0.0061536 | -1.2783 | -2.7922 | -6.2082 | -12.6178 | -14.855 | -16.3607
|  | COXMOOR WOOD | CT |  |  | 2.9901 | 2.8832 | 2.7291 | 2.5424 | 2.3696 | 2.0733 | 1.3416 | 0.36641 | -0.97076 | -2.5515 | -6.1203 | -12.8306 | -15.1729 | -16.7098 | 3.8818 | 3.8136 | 3.6918 | 3.5957 | 3.4862 | 3.3275 | 2.8036 | 2.0673 | 1.0912 | -0.08885 | -2.7643 | -7.673 | -9.2811 | -10.4566 | 3.1977 | 3.0626 | 2.8326 | 2.5195 | 2.1487 | 1.6254 | 0.92538 | -0.0061536 | -1.2783 | -2.7922 | -6.2082 | -12.6178 | -14.855 | -16.3607
|  | COXMOOR WOOD | LW |  |  | 2.9338 | 2.7954 | 2.6434 | 2.4607 | 2.3236 | 2.1828 | 2.0254 | 1.8602 | 1.5504 | 1.1967 | 0.45524 | -1.1902 | -2.4286 | -3.1974 | 3.9071 | 3.8576 | 3.7894 | 3.7453 | 3.7146 | 3.6852 | 3.6416 | 3.592 | 3.5194 | 3.3106 | 2.8413 | 2.1589 | 1.5786 | 0.95033 | 3.0768 | 2.9085 | 2.7259 | 2.466 | 2.2598 | 2.0476 | 1.8186 | 1.5828 | 1.2529 | 0.92287 | 0.23991 | -1.2378 | -2.4267 | -3.254
|  | COXMOOR WOOD | ST |  |  | 3.0354 | 2.9641 | 2.8588 | 2.7612 | 2.7133 | 2.6568 | 2.5795 | 2.5149 | 2.4207 | 2.3305 | 2.1097 | 1.0884 | 0.017915 | -1.4866 | 3.914 | 3.8748 | 3.7923 | 3.7117 | 3.6592 | 3.6021 | 3.5231 | 3.4608 | 3.3617 | 3.2643 | 3.0273 | 2.3061 | 1.2942 | -0.31062 | 3.2253 | 3.1467 | 3.043 | 2.9293 | 2.8718 | 2.8054 | 2.7156 | 2.6432 | 2.5168 | 2.3485 | 1.9232 | 0.55139 | -0.53233 | -1.9079
|  | COXMOOR WOOD | FS |  |  | 2.9901 | 2.8832 | 2.7291 | 2.5424 | 2.3696 | 2.0733 | 1.3416 | 0.36641 | -0.97076 | -2.5515 | -6.1203 | -12.8306 | -15.1729 | -16.7098 | 3.9101 | 3.8653 | 3.8025 | 3.7455 | 3.7004 | 3.6476 | 3.5849 | 3.5139 | 3.4254 | 3.3247 | 3.07 | 1.7853 | -0.098266 | -1.3843 | 3.2195 | 3.1318 | 3.0326 | 2.9308 | 2.8558 | 2.7701 | 2.6567 | 2.5288 | 2.3505 | 2.1483 | 1.6853 | -0.38275 | -2.8584 | -4.618
MANNINGTON GSP | LYTCHETT | CREEKMOOR | MINIMUM HEADROOM | SZ 00552 94121 | YES | 2.9624 | 2.3896 | 1.8647 | 0.95808 | -0.14508 | -1.3013 | -2.9745 | -5.0067 | -7.2209 | -9.6349 | -15.0168 | -25.8247 | -31.5579 | -34.9687 | 8.1877 | 7.8535 | 7.5469 | 7.0527 | 6.4296 | 5.7631 | 4.6429 | 3.1085 | 1.3323 | -0.55339 | -4.3715 | -12.8976 | -17.5904 | -23.5644 | 4.1231 | 3.6356 | 3.1833 | 2.3753 | 1.3953 | 0.31044 | -1.2876 | -3.3384 | -5.6287 | -8.1458 | -13.5032 | -23.8108 | -29.2227 | -31.6853
|  | CREEKMOOR | CT |  |  | 3.1847 | 2.7815 | 2.3408 | 1.5301 | 0.63018 | -0.60738 | -1.9741 | -3.9181 | -6.4242 | -8.9321 | -13.8336 | -25.8247 | -31.5579 | -34.9687 | 8.2251 | 7.9342 | 7.6073 | 7.1149 | 6.5571 | 5.7631 | 4.7651 | 3.2197 | 1.3323 | -0.55339 | -4.2101 | -12.8976 | -17.5904 | -21.0494 | 4.3258 | 3.9873 | 3.61 | 2.8946 | 2.0674 | 0.89416 | -0.40902 | -2.4082 | -4.9503 | -7.4792 | -12.3629 | -23.8108 | -29.2227 | -31.6853
|  | CREEKMOOR | LW |  |  | 2.9624 | 2.3896 | 1.8647 | 0.95808 | -0.14508 | -1.3013 | -2.9745 | -5.0067 | -7.2209 | -9.6349 | -15.0168 | -24.2935 | -27.0216 | -25.854 | 8.1877 | 7.8535 | 7.5469 | 7.0527 | 6.4296 | 5.7659 | 4.6429 | 3.1085 | 1.4508 | -0.38967 | -4.3715 | -10.7971 | -12.4634 | -11.435 | 4.1231 | 3.6356 | 3.1833 | 2.3753 | 1.3953 | 0.31044 | -1.2876 | -3.3384 | -5.6287 | -8.1458 | -13.5032 | -22.4048 | -24.98 | -23.8264
|  | CREEKMOOR | ST |  |  | 3.4615 | 3.3078 | 3.1552 | 2.8983 | 2.5645 | 2.1376 | 1.5903 | 0.86245 | 0.094056 | -0.84672 | -3.3966 | -13.2491 | -20.6121 | -24.1427 | 8.4047 | 8.2822 | 8.1499 | 7.9307 | 7.6656 | 7.3353 | 6.9114 | 6.3694 | 5.69 | 4.7643 | 2.2547 | -6.1158 | -12.5645 | -16.361 | 4.5716 | 4.4521 | 4.3285 | 4.1025 | 3.8186 | 3.4578 | 2.9382 | 2.242 | 1.4379 | 0.39272 | -2.4605 | -12.2834 | -19.56 | -22.7822
|  | CREEKMOOR | FS |  |  | 3.1847 | 2.7815 | 2.3408 | 1.5301 | 0.63018 | -0.60738 | -1.9741 | -3.9181 | -6.4242 | -8.9321 | -13.8336 | -25.8247 | -31.5579 | -34.9687 | 8.3823 | 8.2373 | 8.0752 | 7.8652 | 7.597 | 7.2619 | 6.8393 | 6.2977 | 5.5861 | 4.6701 | 2.3338 | -5.8511 | -15.2944 | -23.5644 | 4.5448 | 4.4082 | 4.2513 | 4.0189 | 3.7146 | 3.3341 | 2.8119 | 2.1163 | 1.2528 | 0.18914 | -2.5031 | -11.7722 | -21.5149 | -27.5968
MINETY GSP | CIRENCESTER BSP | CRICKLADE | MINIMUM HEADROOM | SU 09400 93270 | YES | 4.8576 | 4.7821 | 4.5987 | 4.2732 | 3.8846 | 3.4482 | 2.6846 | 1.455 | -0.1031 | -1.9662 | -6.3863 | -13.8381 | -16.5567 | -18.7793 | 6.2895 | 6.128 | 5.9413 | 5.6751 | 5.3051 | 4.8136 | 4.1116 | 3.1928 | 2.0149 | 0.59454 | -2.7832 | -8.4502 | -10.7318 | -12.8847 | 4.6073 | 4.3603 | 4.1149 | 3.7969 | 3.4119 | 2.9847 | 2.409 | 1.6996 | 0.22187 | -1.5692 | -5.814 | -12.9801 | -15.7529 | -18.1572
|  | CRICKLADE | CT |  |  | 4.8628 | 4.8071 | 4.7379 | 4.6448 | 4.4516 | 4.0711 | 3.561 | 2.8928 | 1.9764 | 0.9882 | -1.5194 | -10.095 | -14.5721 | -15.2224 | 6.3493 | 6.2515 | 6.1321 | 5.9592 | 5.7379 | 5.4331 | 5.0394 | 4.5268 | 3.8424 | 2.9892 | 0.88463 | -5.6301 | -9.0448 | -9.6626 | 4.76 | 4.6141 | 4.4406 | 4.1604 | 3.8383 | 3.4133 | 2.9206 | 2.2744 | 1.3923 | 0.42993 | -1.5137 | -9.4559 | -13.8199 | -14.5601
|  | CRICKLADE | LW |  |  | 4.8576 | 4.7821 | 4.5987 | 4.2732 | 3.8846 | 3.4482 | 2.6846 | 1.455 | -0.1031 | -1.9662 | -6.3863 | -13.8381 | -16.5567 | -18.7793 | 6.2895 | 6.128 | 5.9413 | 5.6751 | 5.3051 | 4.8136 | 4.1116 | 3.1928 | 2.0149 | 0.59454 | -2.7832 | -8.4502 | -10.7318 | -12.8847 | 4.6073 | 4.3603 | 4.1149 | 3.7969 | 3.4119 | 2.9847 | 2.409 | 1.6996 | 0.22187 | -1.5692 | -5.814 | -12.9801 | -15.7529 | -18.1572
|  | CRICKLADE | ST |  |  | 4.9116 | 4.8965 | 4.8759 | 4.7895 | 4.707 | 4.614 | 4.4852 | 4.1645 | 3.7253 | 3.2237 | 1.9669 | -1.7189 | -4.7001 | -6.7069 | 6.4158 | 6.4019 | 6.3832 | 6.2667 | 6.1572 | 6.0387 | 5.8813 | 5.7399 | 5.5183 | 5.284 | 4.7072 | 1.9148 | -0.73526 | -2.7046 | 4.8752 | 4.801 | 4.7166 | 4.5326 | 4.329 | 4.0862 | 3.7752 | 3.4409 | 2.9965 | 2.4928 | 1.2252 | -2.517 | -5.557 | -7.561
|  | CRICKLADE | FS |  |  | 4.8628 | 4.8071 | 4.7379 | 4.6448 | 4.4516 | 4.0711 | 3.561 | 2.8928 | 1.9764 | 0.9882 | -1.5194 | -10.095 | -14.5721 | -15.2224 | 6.3967 | 6.368 | 6.3 | 6.1827 | 6.0295 | 5.823 | 5.5555 | 5.2107 | 4.7639 | 4.2251 | 2.8285 | -0.62665 | -3.3264 | -5.2451 | 4.8689 | 4.7891 | 4.6927 | 4.5203 | 4.3164 | 4.051 | 3.7435 | 3.3497 | 2.8542 | 2.3103 | 1.0005 | -3.1316 | -6.87 | -9.3947
MELKSHAM GSP | FROME BSP | CROCKERTON | MINIMUM HEADROOM | ST 87736 43371 | YES | -0.13701 | -0.3512 | -0.55448 | -0.89664 | -1.3061 | -1.7518 | -2.3307 | -2.9909 | -3.767 | -4.6173 | -6.537 | -11.1118 | -15.2129 | -17.3411 | 3.2638 | 3.2212 | 3.1818 | 3.1241 | 3.0421 | 2.902 | 2.5341 | 2.1065 | 1.6181 | 1.0712 | -0.19047 | -3.2324 | -6.0985 | -7.6365 | 1.2693 | 1.0149 | 0.75778 | 0.40516 | 0.0089408 | -0.41856 | -0.89904 | -1.4215 | -2.0609 | -2.7338 | -4.1604 | -7.2829 | -9.5194 | -11.5171
|  | CROCKERTON | CT |  |  | -0.0055874 | -0.12899 | -0.26151 | -0.465 | -0.69468 | -1.0544 | -1.4668 | -1.982 | -2.7192 | -3.4691 | -4.9684 | -8.1917 | -11.0071 | -12.3837 | 3.2674 | 3.2318 | 3.1922 | 3.1444 | 3.0833 | 2.9945 | 2.8554 | 2.6375 | 2.2015 | 1.75 | 0.84934 | -0.82728 | -2.9337 | -5.0971 | 1.5233 | 1.4109 | 1.2885 | 1.0242 | 0.73331 | 0.40678 | 0.052168 | -0.34562 | -1.0001 | -1.6758 | -3.0854 | -6.5859 | -9.0745 | -10.2533
|  | CROCKERTON | LW |  |  | -0.13701 | -0.3512 | -0.55448 | -0.89664 | -1.3061 | -1.7518 | -2.3307 | -2.9909 | -3.767 | -4.6173 | -6.537 | -11.1118 | -15.2129 | -17.3411 | 3.2638 | 3.2212 | 3.1818 | 3.1241 | 3.0421 | 2.902 | 2.5341 | 2.1065 | 1.6181 | 1.0712 | -0.19047 | -3.2324 | -6.0985 | -7.6365 | 1.2693 | 1.0149 | 0.75778 | 0.40516 | 0.0089408 | -0.41856 | -0.89904 | -1.4215 | -2.0609 | -2.7338 | -4.1604 | -7.2829 | -9.5194 | -11.5171
|  | CROCKERTON | ST |  |  | 0.10408 | 0.051615 | -0.0089561 | -0.11088 | -0.23499 | -0.38394 | -0.56769 | -0.77644 | -1.0182 | -1.3024 | -2.0342 | -4.4337 | -5.8048 | -6.954 | 3.2942 | 3.2787 | 3.2586 | 3.2163 | 3.1656 | 3.1043 | 3.025 | 2.9395 | 2.843 | 2.6951 | 2.2454 | 0.72654 | -0.31976 | -2.6527 | 1.6558 | 1.6018 | 1.5481 | 1.4527 | 1.3429 | 1.2179 | 1.0651 | 0.90254 | 0.71128 | 0.5022 | -0.00026227 | -1.7002 | -3.1926 | -4.8315
|  | CROCKERTON | FS |  |  | -0.0055874 | -0.12899 | -0.26151 | -0.465 | -0.69468 | -1.0544 | -1.4668 | -1.982 | -2.7192 | -3.4691 | -4.9684 | -8.1917 | -11.0071 | -12.3837 | 3.2858 | 3.2638 | 3.2363 | 3.1972 | 3.1448 | 3.0789 | 2.9913 | 2.8829 | 2.7311 | 2.5088 | 1.7776 | -1.24 | -3.3563 | -7.5482 | 1.6467 | 1.5857 | 1.5256 | 1.3988 | 1.2494 | 1.0862 | 0.88015 | 0.64704 | 0.33044 | -0.017003 | -0.81011 | -3.4139 | -5.5733 | -7.2113
BRAMLEY (FLEE) | PYESTOCK BSP | Crookham (Church) | MINIMUM HEADROOM | SU 81702 53403 | YES | 10.4005 | 10.0148 | 9.5691 | 8.7918 | 8.0444 | 6.8552 | 5.5367 | 4.2664 | 2.8789 | 1.5234 | -0.9542 | -5.7304 | -8.5636 | -10.155 | 12.2578 | 12.0738 | 11.8648 | 11.5216 | 11.2062 | 10.4073 | 9.4884 | 8.6647 | 7.8597 | 7.0659 | 5.4749 | 1.6069 | -1.7806 | -8.8882 | 8.4497 | 8.1529 | 7.8121 | 7.2055 | 6.6159 | 5.4881 | 4.2204 | 3.0299 | 1.7713 | 0.55829 | -1.6451 | -5.8863 | -8.3545 | -9.6684
|  | Crookham (Church) | CT |  |  | 10.7559 | 10.5786 | 10.3355 | 9.7789 | 9.2654 | 8.3102 | 7.2514 | 6.2184 | 4.7733 | 3.362 | 0.8096 | -4.9718 | -8.5318 | -10.155 | 12.3434 | 12.1971 | 12.0078 | 11.6774 | 11.3851 | 10.5985 | 9.6984 | 8.867 | 7.946 | 7.0659 | 5.4749 | 1.6069 | -1.7806 | -5.7074 | 8.7264 | 8.5916 | 8.4074 | 7.9571 | 7.5551 | 6.6422 | 5.6131 | 4.6392 | 3.3267 | 2.061 | -0.21262 | -5.322 | -8.3545 | -9.6684
|  | Crookham (Church) | LW |  |  | 10.4005 | 10.0148 | 9.5691 | 8.7918 | 8.0444 | 6.8552 | 5.5367 | 4.2664 | 2.8789 | 1.5234 | -0.9542 | -5.7304 | -8.5636 | -9.5844 | 12.2578 | 12.0738 | 11.8648 | 11.5216 | 11.2062 | 10.4073 | 9.4884 | 8.6647 | 7.8597 | 7.1031 | 5.7583 | 3.1709 | 1.8074 | 1.3281 | 8.4497 | 8.1529 | 7.8121 | 7.2055 | 6.6159 | 5.4881 | 4.2204 | 3.0299 | 1.7713 | 0.55829 | -1.6451 | -5.8863 | -8.3064 | -9.149
|  | Crookham (Church) | ST |  |  | 10.8328 | 10.7004 | 10.4998 | 10.2525 | 10.0694 | 9.5214 | 8.9081 | 8.3213 | 7.7689 | 7.2391 | 6.3448 | 4.2567 | 1.8776 | -1.0716 | 12.3758 | 12.2494 | 12.0789 | 11.8631 | 11.6918 | 11.0904 | 10.4008 | 9.7491 | 9.1548 | 8.5925 | 7.5915 | 5.1612 | 2.1353 | -2.3154 | 8.7889 | 8.692 | 8.5431 | 8.3402 | 8.2002 | 7.6277 | 6.9767 | 6.367 | 5.8093 | 5.288 | 4.4153 | 2.475 | 0.45089 | -2.0053
|  | Crookham (Church) | FS |  |  | 10.7559 | 10.5786 | 10.3355 | 9.7789 | 9.2654 | 8.3102 | 7.2514 | 6.2184 | 4.7733 | 3.362 | 0.8096 | -4.9718 | -8.5318 | -10.155 | 12.3517 | 12.1808 | 11.9691 | 11.7259 | 11.4919 | 10.8493 | 10.1129 | 9.3296 | 8.5459 | 7.7949 | 6.3375 | 2.7326 | -1.6681 | -8.8882 | 8.7583 | 8.6255 | 8.4479 | 8.212 | 8 | 7.3735 | 6.6701 | 5.9182 | 5.1328 | 4.3991 | 3.0599 | 0.19015 | -2.1084 | -4.2029
BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE | MINIMUM HEADROOM | SU 84470 64352 | YES | 5.1784 | 3.677 | 2.1847 | 0.31934 | -2.0108 | -4.5716 | -7.9746 | -11.8787 | -16.1452 | -20.7984 | -30.7274 | -47.9402 | -56.7709 | -60.3048 | 9.4766 | 8.5381 | 7.6153 | 6.5107 | 5.146 | 3.3186 | 1.3183 | -1.5171 | -4.9261 | -8.2836 | -14.8852 | -29.1749 | -36.354 | -47.0893 | 5.1607 | 3.8307 | 2.5163 | 0.84902 | -1.255 | -3.5544 | -6.7449 | -10.4591 | -14.5385 | -19.006 | -28.5647 | -45.1582 | -53.4461 | -56.7015
|  | CROWTHORNE | CT |  |  | 5.5023 | 4.3541 | 3.0336 | 1.34 | -0.59132 | -3.3469 | -6.132 | -9.8963 | -14.6508 | -19.3408 | -28.0829 | -47.9402 | -56.7709 | -60.3048 | 9.4766 | 8.6317 | 7.648 | 6.5107 | 5.2229 | 3.3186 | 1.3183 | -1.5171 | -4.9261 | -8.2836 | -14.5441 | -29.1749 | -36.354 | -41.4247 | 5.4328 | 4.4146 | 3.2303 | 1.6902 | -0.062133 | -2.601 | -5.2153 | -8.8169 | -13.3581 | -17.8342 | -26.1628 | -45.1582 | -53.4461 | -56.7015
|  | CROWTHORNE | LW |  |  | 5.1784 | 3.677 | 2.1847 | 0.31934 | -2.0108 | -4.5716 | -7.9746 | -11.8787 | -16.1452 | -20.7984 | -30.7274 | -46.889 | -51.8303 | -49.3595 | 9.4841 | 8.5381 | 7.6153 | 6.5424 | 5.146 | 3.6356 | 1.3485 | -1.3896 | -4.3867 | -7.7111 | -14.8852 | -26.3446 | -29.2321 | -26.7671 | 5.1607 | 3.8307 | 2.5163 | 0.84902 | -1.255 | -3.5544 | -6.7449 | -10.4591 | -14.5385 | -19.006 | -28.5647 | -44.0659 | -48.6466 | -46.07
|  | CROWTHORNE | ST |  |  | 5.9783 | 5.2997 | 4.5017 | 3.6302 | 2.5392 | 1.1489 | -0.36688 | -2.1159 | -4.071 | -6.4555 | -12.727 | -32.4221 | -45.6642 | -51.1525 | 9.8349 | 9.3593 | 8.7885 | 8.1123 | 7.2799 | 6.2196 | 4.9807 | 3.5275 | 1.887 | -0.11311 | -5.3703 | -21.8895 | -33.5079 | -39.5047 | 5.8981 | 5.3425 | 4.6735 | 3.8932 | 2.9171 | 1.6667 | 0.24379 | -1.421 | -3.3102 | -5.6722 | -11.9103 | -31.3471 | -44.4782 | -49.445
|  | CROWTHORNE | FS |  |  | 5.5023 | 4.3541 | 3.0336 | 1.34 | -0.59132 | -3.3469 | -6.132 | -9.8963 | -14.6508 | -19.3408 | -28.0829 | -47.9402 | -56.7709 | -60.3048 | 9.8414 | 9.348 | 8.7832 | 8.1748 | 7.4218 | 6.5029 | 5.438 | 4.1953 | 2.8216 | 1.2242 | -2.949 | -17.6527 | -34.4793 | -47.0893 | 5.9321 | 5.3934 | 4.7798 | 4.0791 | 3.2101 | 2.1466 | 0.942 | -0.45294 | -2.0578 | -3.9106 | -8.802 | -25.7905 | -44.3295 | -55.3187
EALING GSP | EALING (D) | DEAN GARDENS | MINIMUM HEADROOM | TQ 16546 80368 | YES | 1.3113 | 1.1095 | 0.94838 | 0.73564 | 0.46966 | 0.19308 | -0.27365 | -0.84555 | -1.4726 | -2.1718 | -3.6863 | -6.1014 | -7.3775 | -7.7962 | 3.4755 | 3.3635 | 3.2201 | 3.0101 | 2.473 | 1.6267 | 0.42211 | -1.3066 | -3.586 | -6.4164 | -13.1513 | -25.4026 | -28.9875 | -31.6234 | 1.7016 | 1.5212 | 1.3734 | 1.1801 | 0.93519 | -0.084407 | -1.6446 | -3.8053 | -6.5916 | -10.0493 | -18.276 | -33.2485 | -37.6138 | -40.7382
|  | DEAN GARDENS | CT |  |  | 1.345 | 1.186 | 1.0294 | 0.81644 | 0.58373 | 0.2386 | -0.13118 | -0.6807 | -1.3509 | -1.9914 | -3.1896 | -6.1014 | -7.3775 | -7.7962 | 3.5141 | 3.4527 | 3.3913 | 3.2116 | 2.9776 | 2.6444 | 2.2799 | 1.7607 | 1.1507 | 0.5491 | -0.63313 | -4.1239 | -7.7113 | -12.7973 | 1.7257 | 1.5815 | 1.4348 | 1.2394 | 1.0261 | 0.70571 | 0.36173 | -0.15481 | -0.78282 | -1.3819 | -2.5351 | -5.375 | -6.5722 | -6.9538
|  | DEAN GARDENS | LW |  |  | 1.3113 | 1.1095 | 0.94838 | 0.73564 | 0.46966 | 0.19308 | -0.27365 | -0.84555 | -1.4726 | -2.1718 | -3.6863 | -6.0496 | -6.4182 | -5.7172 | 3.5441 | 3.5049 | 3.4782 | 3.4276 | 3.2499 | 3.0634 | 2.7261 | 2.3038 | 1.8378 | 1.3138 | 0.17266 | -1.5808 | -1.8302 | -1.2436 | 1.7016 | 1.5212 | 1.3734 | 1.1801 | 0.93519 | 0.68011 | 0.24321 | -0.29485 | -0.88468 | -1.5439 | -3.0202 | -5.3716 | -5.7228 | -4.9863
|  | DEAN GARDENS | ST |  |  | 1.4533 | 1.3843 | 1.3336 | 1.2633 | 1.1645 | 1.027 | 0.85003 | 0.62128 | 0.35337 | 0.011932 | -0.93774 | -4.2156 | -6.4536 | -7.1352 | 3.5365 | 3.4954 | 3.4568 | 3.4093 | 3.35 | 3.1538 | 2.914 | 2.6222 | 2.2909 | 1.8879 | 0.81493 | -3.0602 | -7.3765 | -12.589 | 1.8259 | 1.7667 | 1.7194 | 1.6534 | 1.5607 | 1.4315 | 1.2641 | 1.0468 | 0.79228 | 0.46747 | -0.44121 | -3.7371 | -5.9952 | -6.6323
|  | DEAN GARDENS | FS |  |  | 1.345 | 1.186 | 1.0294 | 0.81644 | 0.58373 | 0.2386 | -0.13118 | -0.6807 | -1.3509 | -1.9914 | -3.1896 | -6.1014 | -7.3775 | -7.7962 | 3.4755 | 3.3635 | 3.2201 | 3.0101 | 2.473 | 1.6267 | 0.42211 | -1.3066 | -3.586 | -6.4164 | -13.1513 | -25.4026 | -28.9875 | -31.6234 | 1.817 | 1.7313 | 1.6472 | 1.5182 | 1.0127 | -0.084407 | -1.6446 | -3.8053 | -6.5916 | -10.0493 | -18.276 | -33.2485 | -37.6138 | -40.7382
COWLEY GSP | YARNTON BSP | DEDDINGTON | MINIMUM HEADROOM | SP 46729 30325 | NO | -1.1096 | -1.8086 | -2.5032 | -3.2797 | -4.3534 | -5.5773 | -7.5742 | -10.2301 | -13.1699 | -16.5186 | -23.9236 | -36.1431 | -38.8683 | -38.5243 | 0.88422 | 0.409 | -0.12062 | -0.73868 | -1.5022 | -2.5974 | -4.7362 | -7.7529 | -11.5656 | -16.4462 | -29.8929 | -67.1497 | -91.0783 | -99.9674 | -0.23283 | -0.89753 | -1.5717 | -2.3302 | -3.378 | -4.4987 | -7.1839 | -10.8844 | -15.5639 | -21.5495 | -38.0225 | -83.7018 | -113.0478 | -123.9953
|  | DEDDINGTON | CT |  |  | -1.1044 | -1.7064 | -2.4196 | -3.233 | -4.1312 | -5.5773 | -7.1627 | -9.6297 | -12.5712 | -15.3834 | -20.5354 | -32.4771 | -36.8855 | -38.1109 | 0.88422 | 0.42668 | -0.12062 | -0.73868 | -1.4496 | -2.5974 | -3.8593 | -5.8317 | -8.1649 | -10.3947 | -14.4767 | -23.9606 | -27.478 | -28.7008 | -0.21156 | -0.79292 | -1.4818 | -2.2686 | -3.1327 | -4.4987 | -6.0344 | -8.4851 | -11.4024 | -14.1905 | -19.2943 | -31.1129 | -35.4372 | -36.6295
|  | DEDDINGTON | LW |  |  | -1.1096 | -1.8086 | -2.5032 | -3.2797 | -4.3534 | -5.4941 | -7.5742 | -10.2301 | -13.1699 | -16.5186 | -23.9236 | -36.1431 | -38.8683 | -36.7228 | 0.92057 | 0.409 | -0.098994 | -0.68422 | -1.5022 | -2.393 | -4.06 | -6.1726 | -8.4993 | -11.1497 | -17.0158 | -26.6364 | -28.6865 | -26.808 | -0.23283 | -0.89753 | -1.5717 | -2.3302 | -3.378 | -4.4948 | -6.5061 | -9.065 | -11.9785 | -15.2959 | -22.6307 | -34.7103 | -37.3624 | -34.7226
|  | DEDDINGTON | ST |  |  | -0.74466 | -0.96941 | -1.2659 | -1.6823 | -2.2185 | -2.9071 | -3.8064 | -4.9557 | -6.2837 | -7.9529 | -12.5722 | -27.4227 | -36.646 | -38.5243 | 1.1583 | 0.98988 | 0.76573 | 0.44295 | 0.030286 | -0.50297 | -1.2098 | -2.1375 | -3.1959 | -4.5307 | -8.233 | -20.1666 | -27.6273 | -29.3173 | 0.10455 | -0.09224 | -0.36757 | -0.77492 | -1.2963 | -1.9641 | -2.8368 | -3.9292 | -5.1877 | -6.8288 | -11.4185 | -26.174 | -35.3184 | -37.1454
|  | DEDDINGTON | FS |  |  | -1.1044 | -1.7064 | -2.4196 | -3.233 | -4.1312 | -5.5773 | -7.1627 | -9.6297 | -12.5712 | -15.3834 | -20.5354 | -32.4771 | -36.8855 | -38.1109 | 1.1045 | 0.89945 | 0.62821 | 0.11276 | -0.94887 | -2.527 | -4.7362 | -7.7529 | -11.5656 | -16.4462 | -29.8929 | -67.1497 | -91.0783 | -99.9674 | 0.043372 | -0.19734 | -0.5166 | -1.1624 | -2.5287 | -4.4707 | -7.1839 | -10.8844 | -15.5639 | -21.5495 | -38.0225 | -83.7018 | -113.0478 | -123.9953
IVER 132KV | DENHAM | DENHAM AVENUE | MINIMUM HEADROOM | TQ 03761 86587 | YES | 0.16815 | -0.050971 | -0.2751 | -0.66647 | -1.1591 | -1.6973 | -2.4911 | -3.4321 | -4.4685 | -5.6212 | -8.1295 | -12.7631 | -14.7951 | -14.671 | 1.4154 | 1.2875 | 1.1634 | 0.91962 | 0.61094 | 0.25796 | -0.28082 | -1.0398 | -1.8012 | -2.6564 | -4.5303 | -8.1047 | -10.1823 | -12.2137 | 0.013477 | -0.21091 | -0.42826 | -0.81274 | -1.3084 | -1.8598 | -2.6948 | -3.6674 | -4.6719 | -5.7917 | -8.2309 | -12.7093 | -14.514 | -14.8669
|  | DENHAM AVENUE | CT |  |  | 0.26383 | 0.10548 | -0.089483 | -0.40064 | -0.75767 | -1.25 | -1.8047 | -2.6308 | -3.6722 | -4.6762 | -6.5601 | -11.0508 | -13.0943 | -13.9238 | 1.438 | 1.3327 | 1.21 | 1.031 | 0.82049 | 0.51237 | 0.049914 | -0.61134 | -1.389 | -2.1381 | -3.5329 | -6.8454 | -8.3805 | -9.3295 | 0.085923 | -0.078033 | -0.27404 | -0.59158 | -0.95451 | -1.4716 | -2.0497 | -2.86 | -3.8662 | -4.8352 | -6.6482 | -10.9504 | -12.8577 | -13.6041
|  | DENHAM AVENUE | LW |  |  | 0.16815 | -0.050971 | -0.2751 | -0.66647 | -1.1591 | -1.6973 | -2.4911 | -3.4321 | -4.4685 | -5.6212 | -8.1295 | -12.7631 | -14.7951 | -14.671 | 1.4154 | 1.2875 | 1.1634 | 0.91962 | 0.61094 | 0.25796 | -0.28082 | -1.0398 | -1.8012 | -2.6564 | -4.5303 | -8.1047 | -10.1823 | -10.0356 | 0.013477 | -0.21091 | -0.42826 | -0.81274 | -1.3084 | -1.8598 | -2.6948 | -3.6674 | -4.6719 | -5.7917 | -8.2309 | -12.7093 | -14.514 | -14.3744
|  | DENHAM AVENUE | ST |  |  | 0.36823 | 0.31723 | 0.24205 | 0.053205 | -0.16246 | -0.42363 | -0.76037 | -1.1432 | -1.5974 | -2.1755 | -3.7358 | -8.5838 | -11.6235 | -12.7524 | 1.5026 | 1.4596 | 1.4006 | 1.2369 | 1.0718 | 0.88177 | 0.63075 | 0.32768 | -0.070474 | -0.56589 | -1.885 | -5.8908 | -8.4622 | -9.5881 | 0.19606 | 0.13879 | 0.055732 | -0.14785 | -0.37235 | -0.66084 | -1.04 | -1.4654 | -1.9211 | -2.4893 | -4.0228 | -8.7876 | -11.7394 | -12.7681
|  | DENHAM AVENUE | FS |  |  | 0.26383 | 0.10548 | -0.089483 | -0.40064 | -0.75767 | -1.25 | -1.8047 | -2.6308 | -3.6722 | -4.6762 | -6.5601 | -11.0508 | -13.0943 | -13.9238 | 1.4954 | 1.4422 | 1.3772 | 1.2814 | 1.1578 | 1.0068 | 0.82081 | 0.54074 | 0.17045 | -0.25191 | -1.3295 | -5.0597 | -9.1732 | -12.2137 | 0.18506 | 0.11491 | 0.025328 | -0.11207 | -0.30471 | -0.55029 | -0.86023 | -1.2513 | -1.6821 | -2.1706 | -3.4042 | -7.7333 | -12.2424 | -14.8669
MELKSHAM GSP | NORRINGTON | DEVIZES | MINIMUM HEADROOM | SU 00106 60986 | YES | -2.7034 | -3.1904 | -3.6862 | -4.3312 | -5.0464 | -5.7908 | -6.7882 | -7.8579 | -8.9975 | -10.1846 | -12.6386 | -19.0153 | -22.9991 | -25.7947 | 1.8767 | 1.6361 | 1.3842 | 1.0766 | 0.73586 | 0.37872 | -0.22828 | -0.87108 | -1.4195 | -2.0492 | -4.5673 | -9.2164 | -11.2897 | -16.1205 | -3.2033 | -3.6508 | -4.1065 | -4.7055 | -5.3627 | -6.046 | -6.971 | -7.9585 | -8.9943 | -10.0731 | -12.2992 | -18.3804 | -21.772 | -24.2593
|  | DEVIZES | CT |  |  | -2.2844 | -2.4989 | -2.73 | -3.2009 | -3.7304 | -4.3558 | -5.1775 | -6.0989 | -7.4154 | -8.7766 | -11.7918 | -19.0153 | -22.9991 | -25.7947 | 2.0042 | 1.871 | 1.7229 | 1.4683 | 1.1719 | 0.80778 | 0.20356 | -0.46523 | -1.2233 | -2.0492 | -4.5673 | -9.2164 | -11.2897 | -15.4847 | -2.8215 | -3.0185 | -3.2311 | -3.6663 | -4.1531 | -4.7282 | -5.4999 | -6.3599 | -7.5761 | -8.8474 | -11.6191 | -18.3804 | -21.772 | -24.2593
|  | DEVIZES | LW |  |  | -2.7034 | -3.1904 | -3.6862 | -4.3312 | -5.0464 | -5.7908 | -6.7882 | -7.8579 | -8.9975 | -10.1846 | -12.6386 | -17.5944 | -20.6517 | -22.3702 | 1.8767 | 1.6361 | 1.3842 | 1.0766 | 0.73586 | 0.37872 | -0.22828 | -0.87108 | -1.4195 | -1.9978 | -3.1953 | -5.4533 | -7.0123 | -8.166 | -3.2033 | -3.6508 | -4.1065 | -4.7055 | -5.3627 | -6.046 | -6.971 | -7.9585 | -8.9943 | -10.0731 | -12.2992 | -16.7469 | -19.5279 | -21.1178
|  | DEVIZES | ST |  |  | -1.9881 | -2.0406 | -2.103 | -2.2854 | -2.4965 | -2.7422 | -3.1848 | -3.6348 | -4.0752 | -4.5607 | -5.7301 | -9.3906 | -12.6766 | -16.3119 | 2.1434 | 2.0921 | 2.03 | 1.8545 | 1.679 | 1.4841 | 1.0524 | 0.63705 | 0.28856 | -0.094935 | -1.0328 | -4.045 | -7.6674 | -12.2959 | -2.5436 | -2.5881 | -2.6419 | -2.8287 | -3.0279 | -3.2542 | -3.6766 | -4.0927 | -4.4966 | -4.9383 | -5.9996 | -9.3217 | -12.3728 | -15.6659
|  | DEVIZES | FS |  |  | -2.2844 | -2.4989 | -2.73 | -3.2009 | -3.7304 | -4.3558 | -5.1775 | -6.0989 | -7.4154 | -8.7766 | -11.7918 | -19.0153 | -22.9991 | -25.7947 | 2.2185 | 2.1285 | 2.027 | 1.8775 | 1.7184 | 1.5304 | 1.2639 | 0.95445 | 0.623 | 0.25225 | -0.60756 | -3.5953 | -8.6012 | -16.1205 | -2.4719 | -2.5407 | -2.6193 | -2.8115 | -3.0174 | -3.2505 | -3.5476 | -3.8788 | -4.2568 | -4.6505 | -5.5476 | -8.6489 | -11.8231 | -14.9711
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH | MINIMUM HEADROOM | SU 19288 83540 | YES | 12.4882 | 12.4209 | 12.3358 | 12.1174 | 11.7975 | 11.4551 | 10.9064 | 10.2307 | 9.3478 | 8.4107 | 6.5779 | 2.5137 | 0.80233 | -0.035716 | 13.2511 | 13.1885 | 13.1093 | 13.0081 | 12.8768 | 12.5878 | 12.216 | 11.6616 | 10.9535 | 10.2251 | 8.8045 | 5.6717 | 4.1806 | 3.0269 | 12.1893 | 12.0473 | 11.9067 | 11.6962 | 11.4354 | 11.1583 | 10.7249 | 10.1926 | 9.2864 | 8.3645 | 6.5261 | 2.658 | 1.0266 | 0.18727
|  | DORCAN SOUTH | CT |  |  | 12.4882 | 12.4209 | 12.3358 | 12.1709 | 11.8817 | 11.4551 | 10.97 | 10.268 | 9.3478 | 8.4107 | 6.5779 | 2.5137 | 0.80233 | -0.035716 | 13.2511 | 13.1885 | 13.1093 | 13.0081 | 12.8768 | 12.5878 | 12.216 | 11.6616 | 10.9535 | 10.2251 | 8.8045 | 5.6717 | 4.1806 | 3.0269 | 12.2234 | 12.1096 | 11.9723 | 11.7585 | 11.5196 | 11.1736 | 10.7769 | 10.1926 | 9.2864 | 8.3645 | 6.5802 | 2.658 | 1.0266 | 0.18727
|  | DORCAN SOUTH | LW |  |  | 12.5116 | 12.4567 | 12.3697 | 12.1174 | 11.7975 | 11.457 | 10.9064 | 10.2307 | 9.4274 | 8.534 | 6.5969 | 3.2653 | 2.1863 | 2.2828 | 13.2748 | 13.2261 | 13.1817 | 13.1319 | 12.9546 | 12.7192 | 12.3088 | 11.7932 | 11.1745 | 10.48 | 8.9812 | 6.5053 | 5.6491 | 5.6262 | 12.1893 | 12.0473 | 11.9067 | 11.6962 | 11.4354 | 11.1583 | 10.7249 | 10.1991 | 9.3917 | 8.4844 | 6.5261 | 3.2324 | 2.1611 | 2.2572
|  | DORCAN SOUTH | ST |  |  | 12.5434 | 12.5283 | 12.5078 | 12.4788 | 12.4404 | 12.39 | 12.2428 | 11.9845 | 11.6629 | 11.2608 | 10.1584 | 6.3235 | 3.2976 | 2.0064 | 13.3033 | 13.29 | 13.2718 | 13.2458 | 13.2115 | 13.1666 | 13.1086 | 12.8944 | 12.6089 | 12.2603 | 11.3121 | 8.0996 | 5.4001 | 3.8349 | 12.3113 | 12.2834 | 12.2418 | 12.1818 | 12.1038 | 11.9966 | 11.8583 | 11.671 | 11.4264 | 11.0902 | 9.9521 | 6.0454 | 2.9866 | 1.6564
|  | DORCAN SOUTH | FS |  |  | 12.4882 | 12.4209 | 12.3358 | 12.1709 | 11.8817 | 11.4551 | 10.97 | 10.268 | 9.3478 | 8.4107 | 6.5779 | 2.5137 | 0.80233 | -0.035716 | 13.3051 | 13.2942 | 13.2795 | 13.2598 | 13.2347 | 13.2026 | 13.1626 | 13.0374 | 12.8209 | 12.5725 | 11.9121 | 9.4283 | 6.277 | 3.3581 | 12.3097 | 12.2807 | 12.2457 | 12.1897 | 12.1165 | 12.0278 | 11.9105 | 11.7705 | 11.5796 | 11.367 | 10.7284 | 7.873 | 4.6091 | 2.5144
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER TOWN | MINIMUM HEADROOM | SY 69113 90401 | YES | 9.806 | 9.1521 | 8.4224 | 7.3179 | 6.0424 | 4.6618 | 2.8974 | 1.0172 | -1.1463 | -3.5263 | -8.4647 | -18.2556 | -25.5286 | -29.2819 | 12.3897 | 12.2254 | 11.9455 | 11.7075 | 11.436 | 10.7642 | 9.7601 | 8.4667 | 6.7855 | 5.0831 | 1.7231 | -6.9372 | -13.5125 | -23.2769 | 11.3795 | 10.7842 | 10.1116 | 9.1352 | 7.9859 | 6.747 | 5.0964 | 3.2318 | 1.1014 | -1.1922 | -6.0038 | -15.3075 | -21.7283 | -24.9044
|  | DORCHESTER TOWN | CT |  |  | 10.1958 | 9.7833 | 9.2305 | 8.3213 | 7.3125 | 6.0265 | 4.6052 | 2.9125 | 0.50723 | -1.9022 | -6.5863 | -18.2556 | -25.5286 | -29.2819 | 12.3897 | 12.2254 | 11.9455 | 11.7075 | 11.436 | 10.7642 | 9.7601 | 8.4667 | 6.7855 | 5.0831 | 1.7231 | -6.9372 | -13.5125 | -20.1721 | 11.6267 | 11.3014 | 10.7481 | 9.9243 | 8.9954 | 7.7598 | 6.3889 | 4.6618 | 2.367 | 0.06969 | -4.3807 | -15.3075 | -21.7283 | -24.9044
|  | DORCHESTER TOWN | LW |  |  | 9.806 | 9.1521 | 8.4224 | 7.3179 | 6.0424 | 4.6618 | 2.8974 | 1.0172 | -1.1463 | -3.5263 | -8.4647 | -17.7828 | -21.8096 | -22.7319 | 12.4213 | 12.2541 | 12.0402 | 11.8232 | 11.5458 | 10.8584 | 9.7846 | 8.5817 | 7.1572 | 5.5963 | 2.2807 | -3.4019 | -5.3681 | -5.3256 | 11.3795 | 10.7842 | 10.1116 | 9.1352 | 7.9859 | 6.747 | 5.0964 | 3.2318 | 1.1014 | -1.1922 | -6.0038 | -14.7376 | -18.1589 | -18.5169
|  | DORCHESTER TOWN | ST |  |  | 10.5027 | 10.3129 | 9.997 | 9.586 | 9.118 | 8.5668 | 7.8994 | 7.2039 | 6.411 | 5.4142 | 2.9153 | -5.6985 | -12.1491 | -16.4842 | 12.4882 | 12.4041 | 12.2083 | 12.0153 | 11.806 | 11.5596 | 11.2566 | 10.8709 | 10.1016 | 9.1664 | 6.7242 | -1.2294 | -8.2291 | -15.1959 | 11.7441 | 11.6372 | 11.4168 | 11.1262 | 10.6886 | 10.1384 | 9.4545 | 8.7071 | 7.8447 | 6.8264 | 4.2151 | -4.2608 | -10.32 | -14.1549
|  | DORCHESTER TOWN | FS |  |  | 10.1958 | 9.7833 | 9.2305 | 8.3213 | 7.3125 | 6.0265 | 4.6052 | 2.9125 | 0.50723 | -1.9022 | -6.5863 | -18.2556 | -25.5286 | -29.2819 | 12.4951 | 12.4195 | 12.2897 | 12.1407 | 11.9684 | 11.7699 | 11.5422 | 11.1933 | 10.5155 | 9.7477 | 7.8396 | 0.47199 | -9.8481 | -23.2769 | 11.7558 | 11.6643 | 11.513 | 11.3059 | 10.9324 | 10.498 | 9.9724 | 9.4054 | 8.7345 | 7.9832 | 6.1244 | -0.60719 | -8.0446 | -13.5572
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE | MINIMUM HEADROOM | SU 61604 50238 | YES | 9.2251 | 9.0935 | 8.9631 | 8.5661 | 8.0215 | 7.2534 | 6.1968 | 4.9072 | 3.287 | 1.6594 | -1.2113 | -8.2186 | -14.3595 | -17.4396 | 11.5267 | 11.2859 | 11.0418 | 10.5655 | 9.9747 | 9.4189 | 8.8271 | 8.2581 | 7.5877 | 6.8987 | 5.148 | -0.29509 | -5.4536 | -15.1048 | 7.9882 | 7.5204 | 7.0428 | 6.0266 | 4.8575 | 3.7275 | 2.5522 | 1.3838 | -0.05277 | -1.4987 | -4.0634 | -10.6018 | -16.3612 | -19.0139
|  | DOWN GRANGE | CT |  |  | 9.2358 | 9.1282 | 9.0144 | 8.8527 | 8.4804 | 8.1456 | 7.7828 | 7.4184 | 6.2346 | 4.5204 | 1.2928 | -7.9541 | -14.3595 | -17.4396 | 11.6972 | 11.5242 | 11.3299 | 10.9022 | 10.3042 | 9.8055 | 9.2782 | 8.7315 | 7.8277 | 6.8987 | 5.148 | -0.29509 | -5.4536 | -11.236 | 8.573 | 8.4175 | 8.2452 | 7.5374 | 6.6152 | 5.8309 | 5.0115 | 4.1643 | 2.5371 | 0.89831 | -2.0739 | -10.6018 | -16.3612 | -19.0139
|  | DOWN GRANGE | LW |  |  | 9.2251 | 9.0935 | 8.9631 | 8.5661 | 8.0215 | 7.2534 | 6.1968 | 4.9072 | 3.287 | 1.6594 | -1.2113 | -8.2186 | -12.1275 | -13.4805 | 11.5267 | 11.2859 | 11.0418 | 10.5655 | 9.9747 | 9.4189 | 8.8271 | 8.2581 | 7.5877 | 6.909 | 5.7341 | 2.9576 | 1.4944 | 1.0067 | 7.9882 | 7.5204 | 7.0428 | 6.0266 | 4.8575 | 3.7275 | 2.5522 | 1.3838 | -0.05277 | -1.4987 | -4.0634 | -10.2274 | -13.5648 | -14.6411
|  | DOWN GRANGE | ST |  |  | 9.2656 | 9.1791 | 9.0856 | 8.946 | 8.5951 | 8.4338 | 8.2552 | 8.1012 | 7.9303 | 7.7371 | 7.4277 | 6.1274 | 2.4308 | -3.482 | 11.7448 | 11.598 | 11.4333 | 11.2167 | 10.8379 | 10.5754 | 10.2874 | 10.0108 | 9.6879 | 9.321 | 8.5778 | 5.3621 | 0.92613 | -5.7911 | 8.6693 | 8.5598 | 8.4415 | 8.2541 | 7.8736 | 7.6562 | 7.4184 | 7.2005 | 6.9681 | 6.7027 | 6.2338 | 3.2389 | -0.67229 | -5.6537
|  | DOWN GRANGE | FS |  |  | 9.2358 | 9.1282 | 9.0144 | 8.8527 | 8.4804 | 8.1456 | 7.7828 | 7.4184 | 6.2346 | 4.5204 | 1.2928 | -7.9541 | -14.3595 | -17.4396 | 11.7519 | 11.6031 | 11.4359 | 11.2394 | 10.9749 | 10.7233 | 10.4462 | 10.1681 | 9.7225 | 9.2389 | 8.2212 | 4.1232 | -2.9335 | -15.1048 | 8.6898 | 8.6057 | 8.5153 | 8.3306 | 8.074 | 7.8487 | 7.6117 | 7.3872 | 6.9681 | 6.544 | 5.7784 | 2.6256 | -1.3428 | -5.8436
MINETY GSP | STRATTON (2 X 90) | DRAKES WAY | MINIMUM HEADROOM | SU 16899 85647 | YES | 7.3771 | 7.3425 | 7.3091 | 7.2679 | 7.2186 | 7.1509 | 7.0674 | 6.8686 | 6.5581 | 6.2264 | 5.55 | 4.4414 | 3.7651 | 3.1178 | 8.2242 | 8.1965 | 8.1659 | 8.1276 | 8.0365 | 7.9392 | 7.7847 | 7.6059 | 7.3823 | 7.139 | 6.6413 | 5.9607 | 3.8293 | -0.81606 | 7.2914 | 7.2533 | 7.2163 | 7.1713 | 7.1006 | 6.9894 | 6.7617 | 6.5008 | 6.1832 | 5.8407 | 5.1394 | 4.1119 | 3.449 | 2.7204
|  | DRAKES WAY | CT |  |  | 7.3771 | 7.3446 | 7.3091 | 7.2679 | 7.2217 | 7.1509 | 7.0707 | 6.9583 | 6.7539 | 6.4764 | 5.8207 | 4.5627 | 3.8247 | 3.2919 | 8.2242 | 8.1965 | 8.1659 | 8.1303 | 8.0726 | 7.9622 | 7.8393 | 7.6691 | 7.4455 | 7.2072 | 6.7659 | 6.0153 | 4.5198 | 2.2732 | 7.2914 | 7.2555 | 7.2163 | 7.1713 | 7.1092 | 7.0048 | 6.8874 | 6.6971 | 6.3723 | 6.0341 | 5.4018 | 4.2365 | 3.6302 | 3.1324
|  | DRAKES WAY | LW |  |  | 7.3799 | 7.3425 | 7.3118 | 7.2719 | 7.2186 | 7.1614 | 7.0674 | 6.8686 | 6.5581 | 6.2264 | 5.55 | 4.4414 | 3.7651 | 3.1178 | 8.2299 | 8.2013 | 8.178 | 8.1276 | 8.0365 | 7.9392 | 7.7847 | 7.6059 | 7.3823 | 7.139 | 6.6413 | 5.9607 | 5.4278 | 4.7532 | 7.2948 | 7.2533 | 7.2194 | 7.1747 | 7.1006 | 6.9894 | 6.7617 | 6.5008 | 6.1832 | 5.8407 | 5.1394 | 4.1119 | 3.449 | 2.7204
|  | DRAKES WAY | ST |  |  | 7.4039 | 7.3922 | 7.3764 | 7.3456 | 7.3102 | 7.2665 | 7.2103 | 7.1457 | 7.0474 | 6.9353 | 6.5603 | 5.1272 | 4.3013 | 3.6287 | 8.2443 | 8.2324 | 8.2168 | 8.1854 | 8.1509 | 8.1098 | 8.0572 | 7.9884 | 7.8487 | 7.6888 | 7.2701 | 6.0526 | 4.9737 | 2.3986 | 7.3216 | 7.3091 | 7.2919 | 7.2571 | 7.2173 | 7.1685 | 7.0994 | 7.0032 | 6.861 | 6.6968 | 6.2671 | 4.8541 | 3.8397 | 3.0441
|  | DRAKES WAY | FS |  |  | 7.3771 | 7.3446 | 7.3091 | 7.2679 | 7.2217 | 7.1509 | 7.0707 | 6.9583 | 6.7539 | 6.4764 | 5.8207 | 4.5627 | 3.8247 | 3.2919 | 8.2437 | 8.2315 | 8.216 | 8.1928 | 8.165 | 8.1303 | 8.0891 | 8.0391 | 7.9653 | 7.8834 | 7.6265 | 6.4139 | 3.8293 | -0.81606 | 7.322 | 7.3108 | 7.2959 | 7.2731 | 7.2451 | 7.2091 | 7.1658 | 7.1121 | 7.0224 | 6.9201 | 6.6542 | 5.5878 | 4.5232 | 3.6723
NURSLING GSP | WINCHESTER | DUNBRIDGE | MINIMUM HEADROOM | SU 31520 26244 | YES | -2.1778 | 4.0121 | 3.7846 | 3.5206 | 3.2684 | 2.9912 | 2.6583 | 2.2931 | 1.8538 | 0.99275 | -1.0245 | -4.6011 | -7.0347 | -8.5128 | 1.9662 | 7.9466 | 7.776 | 7.5372 | 7.053 | 5.5668 | 3.4798 | 0.6394 | -3.0009 | -7.533 | -18.7366 | -38.1149 | -43.5953 | -47.8963 | -0.45208 | 5.3981 | 5.0951 | 4.2944 | 3.014 | 1.1809 | -1.3859 | -4.8767 | -9.3441 | -14.904 | -28.6349 | -52.558 | -59.3829 | -64.6436
|  | DUNBRIDGE | CT |  |  | -2.0465 | 4.2261 | 4.0803 | 3.8238 | 3.6129 | 3.3465 | 3.0271 | 2.6652 | 2.2097 | 1.4834 | -0.34354 | -4.6011 | -7.0347 | -8.1172 | 2.0094 | 8.0239 | 7.8659 | 7.5909 | 7.3486 | 7.0148 | 6.6018 | 6.0909 | 5.462 | 4.7171 | 3.2431 | -0.32337 | -2.4534 | -3.9362 | -0.30127 | 5.643 | 5.4132 | 5.0592 | 4.7266 | 4.2889 | 3.7661 | 3.1172 | 2.3055 | 1.3753 | -0.4642 | -4.7833 | -7.2758 | -8.5026
|  | DUNBRIDGE | LW |  |  | -2.1778 | 4.0121 | 3.7846 | 3.5206 | 3.2684 | 2.9912 | 2.6583 | 2.2931 | 1.8538 | 0.99275 | -1.0245 | -4.4862 | -6.195 | -7.1184 | 1.9662 | 7.9466 | 7.776 | 7.5372 | 7.2822 | 6.9878 | 6.5613 | 6.0482 | 5.4192 | 4.712 | 3.1722 | 0.56165 | -1.0359 | -2.3208 | -0.45208 | 5.3981 | 5.0951 | 4.7554 | 4.3874 | 3.9714 | 3.3964 | 2.7134 | 1.8909 | 0.97558 | -1.0149 | -4.4369 | -6.3269 | -7.5837
|  | DUNBRIDGE | ST |  |  | -1.9623 | 4.3711 | 4.2786 | 3.9485 | 3.7161 | 3.47 | 3.1594 | 2.8879 | 2.5123 | 2.1273 | 0.94746 | -3.4642 | -6.6959 | -8.5128 | 2.0764 | 8.1497 | 8.0537 | 7.6855 | 7.4169 | 7.1199 | 6.7219 | 6.3541 | 5.8384 | 5.2786 | 3.903 | 0.065729 | -3.0499 | -5.2081 | -0.19214 | 5.84 | 5.6986 | 5.2744 | 4.9359 | 4.5614 | 4.0846 | 3.6239 | 3.0029 | 2.3238 | 0.67187 | -3.8363 | -7.2676 | -9.3064
|  | DUNBRIDGE | FS |  |  | -2.0465 | 4.2261 | 4.0803 | 3.8238 | 3.6129 | 3.3465 | 3.0271 | 2.6652 | 2.2097 | 1.4834 | -0.34354 | -4.6011 | -7.0347 | -8.1172 | 2.0617 | 8.102 | 7.9643 | 7.7124 | 7.053 | 5.5668 | 3.4798 | 0.6394 | -3.0009 | -7.533 | -18.7366 | -38.1149 | -43.5953 | -47.8963 | -0.18905 | 5.7709 | 5.2086 | 4.2944 | 3.014 | 1.1809 | -1.3859 | -4.8767 | -9.3441 | -14.904 | -28.6349 | -52.558 | -59.3829 | -64.6436
MANNINGTON GSP | REDHILL BSP | EAST HOWE | MINIMUM HEADROOM | SZ 06789 95116 | YES | 7.8453 | 6.7479 | 5.6516 | 3.8953 | 1.8516 | -0.30655 | -3.2626 | -6.9938 | -10.9628 | -15.1608 | -24.2121 | -41.272 | -54.4288 | -59.8986 | 11.0032 | 10.3096 | 9.633 | 8.6591 | 7.5155 | 6.3029 | 4.5505 | 2.1774 | -0.29269 | -2.9673 | -9.0753 | -20.8231 | -32.5558 | -42.1216 | 7.5233 | 6.504 | 5.4921 | 3.8964 | 2.0303 | 0.060634 | -2.6919 | -6.1473 | -9.9114 | -13.9308 | -22.6324 | -38.9375 | -52.1026 | -57.4305
|  | EAST HOWE | CT |  |  | 8.3548 | 7.5776 | 6.7473 | 5.2614 | 3.6669 | 1.4774 | -0.8902 | -4.2489 | -8.4292 | -12.4289 | -19.9134 | -37.4082 | -45.6553 | -49.298 | 11.1725 | 10.5785 | 9.9736 | 9.0857 | 8.1588 | 6.8868 | 5.3842 | 3.1485 | 0.48432 | -2.102 | -7.2181 | -19.6545 | -26.5551 | -32.1644 | 7.9622 | 7.221 | 6.4317 | 5.0711 | 3.6293 | 1.6806 | -0.54015 | -3.7325 | -7.6944 | -11.4999 | -18.6151 | -35.216 | -42.9131 | -46.2761
|  | EAST HOWE | LW |  |  | 7.8453 | 6.7479 | 5.6516 | 3.8953 | 1.8516 | -0.30655 | -3.2626 | -6.9938 | -10.9628 | -15.1608 | -24.2121 | -41.272 | -54.4288 | -59.8986 | 11.0032 | 10.3096 | 9.633 | 8.6591 | 7.5155 | 6.3029 | 4.5505 | 2.1774 | -0.29269 | -2.9673 | -9.0753 | -20.8231 | -32.5558 | -36.9263 | 7.5233 | 6.504 | 5.4921 | 3.8964 | 2.0303 | 0.060634 | -2.6919 | -6.1473 | -9.9114 | -13.9308 | -22.6324 | -38.9375 | -52.1026 | -57.4305
|  | EAST HOWE | ST |  |  | 8.7528 | 8.3352 | 7.8907 | 7.2846 | 6.5857 | 5.7074 | 4.5236 | 2.9661 | 1.3413 | -0.56873 | -5.5236 | -21.5234 | -33.0789 | -38.6667 | 11.4148 | 11.0523 | 10.7005 | 10.2383 | 9.7345 | 9.1084 | 8.3284 | 7.2714 | 6.0473 | 4.6017 | 0.86286 | -12.2979 | -22.4689 | -29.0464 | 8.3441 | 7.9532 | 7.5413 | 6.9831 | 6.3431 | 5.5394 | 4.527 | 3.0524 | 1.4859 | -0.37947 | -5.2578 | -21.2005 | -32.5819 | -37.4415
|  | EAST HOWE | FS |  |  | 8.3548 | 7.5776 | 6.7473 | 5.2614 | 3.6669 | 1.4774 | -0.8902 | -4.2489 | -8.4292 | -12.4289 | -19.9134 | -37.4082 | -45.6553 | -49.298 | 11.466 | 11.1782 | 10.8532 | 10.4347 | 9.9577 | 9.391 | 8.7147 | 7.8718 | 6.8351 | 5.609 | 2.3317 | -10.1196 | -26.3331 | -42.1216 | 8.4011 | 8.1005 | 7.7441 | 7.229 | 6.6323 | 5.918 | 5.0634 | 4.0038 | 2.7038 | 1.1963 | -2.7335 | -17.174 | -32.9961 | -43.0298
MELKSHAM GSP | NORRINGTON | EASTERTON | MINIMUM HEADROOM | SU 01568 54730 | YES | 5.4451 | 5.1414 | 4.8268 | 4.6121 | 4.3691 | 4.098 | 3.7192 | 2.7805 | 1.4784 | -0.21334 | -4.1295 | -11.0099 | -13.408 | -15.3639 | 7.3288 | 7.2333 | 7.1329 | 7.0579 | 6.9685 | 6.8582 | 6.6742 | 6.1812 | 5.1218 | 3.8333 | 0.8393 | -4.3966 | -6.3668 | -8.1876 | 5.2942 | 5.0261 | 4.7477 | 4.5559 | 4.3381 | 4.0939 | 3.8001 | 3.4594 | 2.3397 | 0.71906 | -3.0322 | -9.6251 | -12.0375 | -14.1091
|  | EASTERTON | CT |  |  | 5.6739 | 5.4923 | 5.3024 | 5.094 | 4.8626 | 4.6161 | 4.336 | 4.0431 | 3.6769 | 3.2461 | 2.1934 | -2.2679 | -4.9256 | -5.3492 | 7.3832 | 7.3118 | 7.2337 | 7.1404 | 7.0278 | 6.8986 | 6.7367 | 6.5694 | 6.3597 | 6.0744 | 5.4346 | 2.1728 | 0.17557 | -0.24676 | 5.495 | 5.3344 | 5.1661 | 4.978 | 4.7672 | 4.5409 | 4.2789 | 4.0078 | 3.6649 | 3.2484 | 2.3602 | -1.3862 | -3.9828 | -4.4749
|  | EASTERTON | LW |  |  | 5.4451 | 5.1414 | 4.8268 | 4.6121 | 4.3691 | 4.098 | 3.7192 | 2.7805 | 1.4784 | -0.21334 | -4.1295 | -11.0099 | -13.408 | -15.3639 | 7.3288 | 7.2333 | 7.1329 | 7.0579 | 6.9685 | 6.8582 | 6.6742 | 6.1812 | 5.1218 | 3.8333 | 0.8393 | -4.3966 | -6.3668 | -8.1876 | 5.2942 | 5.0261 | 4.7477 | 4.5559 | 4.3381 | 4.0939 | 3.8001 | 3.4594 | 2.3397 | 0.71906 | -3.0322 | -9.6251 | -12.0375 | -14.1091
|  | EASTERTON | ST |  |  | 5.8149 | 5.7019 | 5.5886 | 5.377 | 5.1758 | 4.9708 | 4.7355 | 4.5219 | 4.2481 | 3.968 | 3.3538 | 1.7542 | 0.4464 | -0.53348 | 7.4257 | 7.3768 | 7.3246 | 7.1861 | 7.0641 | 6.9394 | 6.7814 | 6.6508 | 6.4576 | 6.2621 | 5.8049 | 4.4637 | 3.2063 | 1.9958 | 5.6195 | 5.5199 | 5.4198 | 5.2111 | 5.0188 | 4.8244 | 4.596 | 4.3968 | 4.1277 | 3.8555 | 3.2545 | 1.679 | 0.32253 | -0.741
|  | EASTERTON | FS |  |  | 5.6739 | 5.4923 | 5.3024 | 5.094 | 4.8626 | 4.6161 | 4.336 | 4.0431 | 3.6769 | 3.2461 | 2.1934 | -2.2679 | -4.9256 | -5.3492 | 7.4473 | 7.4082 | 7.3651 | 7.2886 | 7.2083 | 7.1178 | 7.0201 | 6.9186 | 6.7923 | 6.6584 | 6.3293 | 5.4136 | 4.7475 | 4.0324 | 5.6757 | 5.6064 | 5.5336 | 5.3811 | 5.2264 | 5.0577 | 4.8813 | 4.7002 | 4.4693 | 4.228 | 3.7123 | 2.2977 | 1.4304 | 0.59733
BRAMLEY (FLEE) | BRACKNELL RESERVE | EASTHAMPSTEAD | MINIMUM HEADROOM | SU 86148 67194 | YES | 9.634 | 9.2201 | 8.8222 | 7.9831 | 7.0791 | 5.6081 | 3.9362 | 2.3035 | 0.57838 | -1.1785 | -4.7804 | -13.6707 | -17.1369 | -19.0116 | 12.6496 | 12.4247 | 12.2249 | 11.8538 | 11.4356 | 10.4189 | 9.2238 | 8.1038 | 7.0218 | 5.9489 | 3.7932 | -2.8483 | -5.1843 | -13.5831 | 8.7192 | 8.3394 | 7.9788 | 7.2307 | 6.4239 | 4.9758 | 3.3183 | 1.7231 | 0.078953 | -1.5674 | -4.9049 | -13.5961 | -16.8298 | -18.5828
|  | EASTHAMPSTEAD | CT |  |  | 10.1676 | 10.063 | 9.9333 | 9.3778 | 8.8024 | 7.6075 | 6.3796 | 5.1659 | 3.4992 | 1.8821 | -1.1307 | -9.3479 | -15.6246 | -18.8105 | 12.8196 | 12.7027 | 12.5634 | 12.2544 | 11.9366 | 10.9622 | 9.9363 | 8.9419 | 7.8244 | 6.7688 | 4.8658 | -0.33946 | -5.1843 | -10.3114 | 9.194 | 9.0992 | 8.9841 | 8.4832 | 7.9731 | 6.7584 | 5.5095 | 4.2942 | 2.6984 | 1.1702 | -1.6291 | -9.1118 | -14.54 | -17.2312
|  | EASTHAMPSTEAD | LW |  |  | 9.634 | 9.2201 | 8.8222 | 7.9831 | 7.0791 | 5.6081 | 3.9362 | 2.3035 | 0.57838 | -1.1785 | -4.7804 | -13.6707 | -17.1369 | -19.0116 | 12.6496 | 12.4247 | 12.2249 | 11.8538 | 11.4356 | 10.4189 | 9.2238 | 8.1038 | 7.0218 | 5.9489 | 3.7932 | -2.8483 | -5.0256 | -6.3241 | 8.7192 | 8.3394 | 7.9788 | 7.2307 | 6.4239 | 4.9758 | 3.3183 | 1.7231 | 0.078953 | -1.5674 | -4.9049 | -13.5961 | -16.8298 | -18.5828
|  | EASTHAMPSTEAD | ST |  |  | 10.3483 | 10.3523 | 10.3432 | 10.2513 | 10.162 | 9.5767 | 8.9623 | 8.3968 | 7.9312 | 7.4656 | 6.5428 | 2.8766 | -1.1124 | -5.39 | 12.9082 | 12.8537 | 12.7827 | 12.6536 | 12.5226 | 11.8382 | 11.1109 | 10.4334 | 9.8258 | 9.2308 | 8.0707 | 4.4457 | 0.25269 | -5.219 | 9.363 | 9.3715 | 9.3686 | 9.2919 | 9.2196 | 8.5712 | 7.899 | 7.2883 | 6.7807 | 6.293 | 5.3764 | 1.9622 | -1.6902 | -5.5818
|  | EASTHAMPSTEAD | FS |  |  | 10.1676 | 10.063 | 9.9333 | 9.3778 | 8.8024 | 7.6075 | 6.3796 | 5.1659 | 3.4992 | 1.8821 | -1.1307 | -9.3479 | -15.6246 | -18.8105 | 12.9143 | 12.8155 | 12.7134 | 12.5825 | 12.4226 | 11.821 | 11.1452 | 10.4798 | 9.7974 | 9.1322 | 7.7422 | 3.5797 | -3.0467 | -13.5831 | 9.3554 | 9.3242 | 9.2925 | 9.1786 | 9.04 | 8.4476 | 7.7946 | 7.1639 | 6.5314 | 5.9383 | 4.7709 | 1.3598 | -2.7377 | -6.8352
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH | MINIMUM HEADROOM | SU 45426 18958 | YES | 7.6171 | 5.3958 | 3.5991 | 1.4621 | -0.79332 | -3.0208 | -5.8618 | -9.2151 | -13.0951 | -17.2805 | -26.6687 | -43.794 | -50.2329 | -54.195 | 12.9876 | 11.425 | 10.2274 | 8.9575 | 7.6154 | 6.312 | 4.4771 | 2.2594 | -0.29513 | -3.2942 | -9.8004 | -23.1302 | -33.0187 | -55.4796 | 7.1957 | 5.218 | 3.6158 | 1.7077 | -0.33289 | -2.3547 | -5.0226 | -8.1908 | -12.0399 | -16.2248 | -25.2194 | -41.4809 | -47.4468 | -50.9806
|  | EASTLEIGH NORTH | CT |  |  | 8.3587 | 6.6757 | 5.6036 | 4.045 | 2.3997 | 0.19829 | -2.0846 | -5.1773 | -9.6786 | -14.0746 | -22.0494 | -40.6624 | -50.0212 | -54.195 | 13.2506 | 11.8887 | 11.0828 | 10.0637 | 8.9714 | 7.4208 | 5.7391 | 3.408 | 0.10205 | -3.1168 | -8.9713 | -23.1302 | -32.5459 | -42.0562 | 7.8424 | 6.337 | 5.3774 | 3.9764 | 2.4877 | 0.45278 | -1.7181 | -4.9005 | -9.2354 | -13.4063 | -20.9632 | -38.559 | -47.201 | -50.9806
|  | EASTLEIGH NORTH | LW |  |  | 7.6171 | 5.3958 | 3.5991 | 1.4621 | -0.79332 | -3.0208 | -5.8618 | -9.2151 | -13.0951 | -17.2805 | -26.6687 | -43.794 | -50.2329 | -49.1165 | 12.9876 | 11.425 | 10.2274 | 8.9575 | 7.6154 | 6.312 | 4.4771 | 2.2594 | -0.29513 | -3.2942 | -9.8004 | -21.2976 | -25.2743 | -24.7038 | 7.1957 | 5.218 | 3.6158 | 1.7077 | -0.33289 | -2.3547 | -5.0226 | -8.1908 | -12.0399 | -16.2248 | -25.2194 | -41.4809 | -47.4468 | -46.1682
|  | EASTLEIGH NORTH | ST |  |  | 8.8904 | 7.6343 | 7.0378 | 6.3482 | 5.5689 | 4.5962 | 3.463 | 2.1101 | 0.42219 | -1.5232 | -6.5929 | -23.2315 | -35.3296 | -41.8824 | 13.5894 | 12.53 | 12.0622 | 11.51 | 10.8699 | 10.0475 | 9.0361 | 7.836 | 6.298 | 4.52 | 0.071525 | -14.6666 | -27.3543 | -38.1796 | 8.3469 | 7.2551 | 6.7566 | 6.156 | 5.4621 | 4.5787 | 3.5125 | 2.232 | 0.57835 | -1.4666 | -6.5043 | -22.7195 | -34.3985 | -40.4023
|  | EASTLEIGH NORTH | FS |  |  | 8.3587 | 6.6757 | 5.6036 | 4.045 | 2.3997 | 0.19829 | -2.0846 | -5.1773 | -9.6786 | -14.0746 | -22.0494 | -40.6624 | -50.0212 | -54.195 | 13.9681 | 13.0725 | 12.3547 | 11.6244 | 10.8498 | 9.9654 | 8.9722 | 7.7932 | 6.3359 | 4.6585 | 0.48889 | -13.7753 | -33.0187 | -55.4796 | 8.7582 | 7.8756 | 7.1826 | 6.4158 | 5.611 | 4.6946 | 3.6929 | 2.4952 | 1.032 | -0.63698 | -4.7999 | -19.1817 | -34.7029 | -45.2226
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY | MINIMUM HEADROOM | SZ 66357 99040 | YES | 12.1527 | 12.0654 | 11.9814 | 11.7274 | 11.476 | 11.2272 | 10.954 | 10.6615 | 10.3353 | 10.0012 | 9.3378 | 7.9459 | 6.802 | 6.3898 | 13.8369 | 13.7842 | 13.7125 | 13.6065 | 13.4616 | 13.2631 | 12.9921 | 12.633 | 12.1752 | 11.1288 | 7.8918 | 2.4514 | -4.6812 | -22.7647 | 12.9984 | 12.939 | 12.8818 | 12.7051 | 12.5301 | 12.357 | 12.174 | 11.99 | 11.005 | 9.4669 | 5.5112 | -1.194 | -3.4146 | -5.4863
|  | EASTNEY | CT |  |  | 12.2955 | 12.2767 | 12.2637 | 12.0837 | 11.9045 | 11.7246 | 11.5429 | 11.3571 | 11.0688 | 10.7416 | 10.0791 | 8.0222 | 6.802 | 6.3898 | 13.864 | 13.8421 | 13.817 | 13.7855 | 13.7505 | 13.709 | 13.6629 | 13.5258 | 13.1613 | 12.7528 | 11.8421 | 8.4049 | 2.9741 | -5.9873 | 13.0963 | 13.0838 | 13.0753 | 12.9509 | 12.8271 | 12.7024 | 12.5762 | 12.4464 | 12.2383 | 12.0134 | 11.5018 | 9.7263 | 8.6235 | 8.1785
|  | EASTNEY | LW |  |  | 12.1527 | 12.0654 | 11.9814 | 11.7274 | 11.476 | 11.2272 | 10.954 | 10.6615 | 10.3353 | 10.0012 | 9.3378 | 7.9459 | 7.2185 | 6.4691 | 13.8786 | 13.8715 | 13.8649 | 13.8559 | 13.8448 | 13.8324 | 13.8141 | 13.792 | 13.7331 | 13.6695 | 13.5454 | 13.0588 | 12.4587 | 11.734 | 12.9984 | 12.939 | 12.8818 | 12.7051 | 12.5301 | 12.357 | 12.174 | 11.99 | 11.7419 | 11.4481 | 10.8664 | 9.633 | 8.8855 | 8.0684
|  | EASTNEY | ST |  |  | 12.3527 | 12.368 | 12.3784 | 12.383 | 12.3892 | 12.3888 | 12.3813 | 12.3722 | 12.3239 | 12.2729 | 12.1496 | 11.4278 | 10.415 | 9.2821 | 13.867 | 13.8469 | 13.823 | 13.7928 | 13.7578 | 13.7171 | 13.6703 | 13.6168 | 13.5255 | 13.3383 | 12.5805 | 9.5275 | 4.0085 | -5.3577 | 13.1404 | 13.1537 | 13.1627 | 13.1668 | 13.1718 | 13.1703 | 13.1619 | 13.1511 | 13.0963 | 13.0395 | 12.9037 | 12.2352 | 11.2707 | 10.229
|  | EASTNEY | FS |  |  | 12.2955 | 12.2767 | 12.2637 | 12.0837 | 11.9045 | 11.7246 | 11.5429 | 11.3571 | 11.0688 | 10.7416 | 10.0791 | 8.0222 | 6.802 | 6.3898 | 13.8369 | 13.7842 | 13.7125 | 13.6065 | 13.4616 | 13.2631 | 12.9921 | 12.633 | 12.1752 | 11.1288 | 7.8918 | 2.4514 | -4.6812 | -22.7647 | 13.1232 | 13.1182 | 13.1134 | 13.0771 | 13.0297 | 12.9662 | 12.8761 | 12.2309 | 11.005 | 9.4669 | 5.5112 | -1.194 | -3.4146 | -5.4863
LALEHAM | STAINES | EGHAM | MINIMUM HEADROOM | TQ 01030 71404 | YES | 1.1712 | 0.22797 | -0.62653 | 26.1464 | 24.805 | 23.4077 | 22.0756 | 20.5077 | 18.6993 | 16.7341 | 12.5727 | 5.1947 | 1.3807 | -0.45268 | 8.0607 | 7.5233 | 7.0331 | 35.6986 | 34.966 | 34.1406 | 33.2612 | 32.0539 | 30.5595 | 29.0755 | 26.242 | 17.2295 | 6.1258 | -5.5276 | 0.72097 | -0.087489 | -0.83896 | 27.3988 | 26.2055 | 24.9523 | 23.6349 | 22.1187 | 20.4028 | 18.5311 | 14.5535 | 6.8681 | -7.0312 | -12.8008
|  | EGHAM | CT |  |  | 1.5066 | 0.85794 | 0.17357 | 27.1784 | 26.1133 | 24.7438 | 23.622 | 22.1147 | 20.0558 | 18.0322 | 14.2782 | 5.5866 | 1.3807 | -0.45268 | 8.0609 | 7.5831 | 7.0803 | 35.7518 | 35.0655 | 34.1406 | 33.2612 | 32.0539 | 30.5595 | 29.0755 | 26.242 | 19.2968 | 14.2818 | 7.8197 | 0.97091 | 0.39806 | -0.18845 | 28.2434 | 27.305 | 26.0724 | 25.0089 | 23.5664 | 21.6212 | 19.7098 | 16.1577 | 7.9931 | 4.17 | 2.5571
|  | EGHAM | LW |  |  | 1.1712 | 0.22797 | -0.62653 | 26.1464 | 24.805 | 23.4077 | 22.0756 | 20.5077 | 18.6993 | 16.7341 | 12.5727 | 5.1947 | 2.6278 | 3.3058 | 8.0607 | 7.5233 | 7.0331 | 35.6986 | 34.966 | 34.1937 | 33.2667 | 32.1725 | 30.9838 | 29.6646 | 26.82 | 22.0533 | 20.776 | 21.7197 | 0.72097 | -0.087489 | -0.83896 | 27.3988 | 26.2055 | 24.9523 | 23.6349 | 22.1187 | 20.4028 | 18.5311 | 14.5535 | 7.5695 | 5.2553 | 6.055
|  | EGHAM | ST |  |  | 1.7666 | 1.3228 | 0.90801 | 28.3808 | 27.8206 | 27.1764 | 26.6675 | 26.0697 | 25.3706 | 24.5265 | 22.3596 | 14.9779 | 9.6909 | 6.7269 | 8.2321 | 7.9098 | 7.5811 | 36.4461 | 35.9783 | 35.4321 | 34.8819 | 34.2568 | 33.5516 | 32.7032 | 30.5175 | 23.2215 | 16.6201 | 10.0797 | 1.2314 | 0.86974 | 0.51585 | 29.3617 | 28.8767 | 28.3121 | 27.8137 | 27.2342 | 26.564 | 25.7478 | 23.6247 | 16.5074 | 11.4807 | 8.7733
|  | EGHAM | FS |  |  | 1.5066 | 0.85794 | 0.17357 | 27.1784 | 26.1133 | 24.7438 | 23.622 | 22.1147 | 20.0558 | 18.0322 | 14.2782 | 5.5866 | 1.3807 | -0.45268 | 8.254 | 7.8617 | 7.4628 | 36.2908 | 35.7659 | 35.1467 | 34.5107 | 33.73 | 32.8517 | 31.8492 | 29.343 | 17.2295 | 6.1258 | -5.5276 | 1.2703 | 0.862 | 0.46536 | 29.2768 | 28.7481 | 28.1231 | 27.5359 | 26.8019 | 25.9354 | 24.9537 | 22.5086 | 6.8681 | -7.0312 | -12.8008
MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE | MINIMUM HEADROOM | SZ 08757 91379 | YES | 4.4471 | 4.1563 | 3.8445 | 3.3898 | 2.559 | 1.5614 | -0.057147 | -2.0228 | -4.0129 | -6.254 | -11.1016 | -18.816 | -20.634 | -22.1075 | 5.8006 | 5.4166 | 4.9691 | 4.3305 | 3.6107 | 2.6838 | 1.6401 | 0.10827 | -1.5319 | -3.1399 | -6.6493 | -13.949 | -23.5772 | -40.2268 | 4.0368 | 3.5227 | 2.9711 | 2.2213 | 1.2932 | 0.2969 | -1.3657 | -3.3618 | -5.3335 | -7.5512 | -12.3553 | -19.963 | -21.7443 | -23.0126
|  | ELECTRIC HOUSE | CT |  |  | 4.4972 | 4.2973 | 4.0746 | 3.7015 | 2.9522 | 1.8642 | 0.65826 | -1.0871 | -2.9979 | -4.8373 | -8.1935 | -15.9719 | -19.3689 | -20.7762 | 5.8006 | 5.4166 | 4.9691 | 4.3305 | 3.6107 | 2.6838 | 1.6401 | 0.10827 | -1.5319 | -3.1399 | -6.1705 | -13.949 | -19.9978 | -27.418 | 4.0868 | 3.6724 | 3.1502 | 2.4087 | 1.5806 | 0.45934 | -0.79607 | -2.5983 | -4.4994 | -6.3226 | -9.6298 | -17.2973 | -20.6373 | -22.0369
|  | ELECTRIC HOUSE | LW |  |  | 4.4471 | 4.1563 | 3.8445 | 3.3898 | 2.559 | 1.5614 | -0.057147 | -2.0228 | -4.0129 | -6.254 | -11.1016 | -18.816 | -20.634 | -22.1075 | 5.8671 | 5.4755 | 5.0716 | 4.5398 | 3.8712 | 3.146 | 1.9303 | 0.41796 | -1.1274 | -2.8674 | -6.6493 | -12.6147 | -14.0352 | -14.1395 | 4.0368 | 3.5227 | 2.9711 | 2.2213 | 1.2932 | 0.2969 | -1.3657 | -3.3618 | -5.3335 | -7.5512 | -12.3553 | -19.963 | -21.7443 | -20.5761
|  | ELECTRIC HOUSE | ST |  |  | 4.6247 | 4.5295 | 4.4185 | 4.1939 | 3.9025 | 3.6136 | 3.2432 | 2.732 | 1.9026 | 0.88135 | -1.8777 | -10.659 | -16.3783 | -18.3184 | 6.0121 | 5.8131 | 5.5698 | 5.1606 | 4.6495 | 4.0914 | 3.3901 | 2.5678 | 1.79 | 0.85017 | -1.8313 | -10.6902 | -18.8292 | -26.7194 | 4.4096 | 4.2678 | 4.0701 | 3.6928 | 3.1985 | 2.647 | 1.9251 | 1.0517 | 0.22974 | -0.78432 | -3.5336 | -12.2986 | -18.167 | -20.1328
|  | ELECTRIC HOUSE | FS |  |  | 4.4972 | 4.2973 | 4.0746 | 3.7015 | 2.9522 | 1.8642 | 0.65826 | -1.0871 | -2.9979 | -4.8373 | -8.1935 | -15.9719 | -19.3689 | -20.7762 | 6.0317 | 5.802 | 5.5292 | 5.1111 | 4.641 | 4.0902 | 3.4231 | 2.6392 | 1.875 | 0.99388 | -1.3208 | -10.5206 | -23.5772 | -40.2268 | 4.4186 | 4.2685 | 4.0807 | 3.742 | 3.3638 | 2.9087 | 2.342 | 1.6566 | 1.0073 | 0.24963 | -1.7883 | -9.383 | -17.9175 | -23.0126
BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD | MINIMUM HEADROOM | SU 81057 68532 | YES | 3.5848 | 2.8268 | 1.9774 | 0.55862 | -1.1744 | -3.0106 | -5.6387 | -8.7396 | -11.9278 | -15.4276 | -22.8325 | -36.0272 | -44.4942 | -50.5399 | 7.8831 | 7.3651 | 6.8098 | 5.969 | 4.8942 | 3.7397 | 1.9688 | -0.15536 | -2.3652 | -4.8287 | -10.1453 | -19.5161 | -27.8144 | -37.5406 | 3.8276 | 3.0885 | 2.3047 | 1.0256 | -0.55461 | -2.2408 | -4.7082 | -7.6355 | -10.6769 | -14.0295 | -21.1694 | -33.8033 | -41.861 | -47.7302
|  | ELMS ROAD | CT |  |  | 3.8874 | 3.3262 | 2.5978 | 1.3798 | 0.030025 | -1.7515 | -3.6889 | -6.3708 | -9.6295 | -12.818 | -18.6834 | -32.5307 | -39.2485 | -42.3069 | 7.8858 | 7.4072 | 6.8098 | 5.9762 | 5.0474 | 3.7653 | 2.3529 | 0.36135 | -1.9863 | -4.3018 | -8.6443 | -19.3084 | -25.8573 | -32.078 | 4.0484 | 3.5112 | 2.8308 | 1.7309 | 0.50783 | -1.1466 | -2.9568 | -5.4937 | -8.5904 | -11.6206 | -17.2087 | -30.3815 | -36.6278 | -39.4191
|  | ELMS ROAD | LW |  |  | 3.5848 | 2.8268 | 1.9774 | 0.55862 | -1.1744 | -3.0106 | -5.6387 | -8.7396 | -11.9278 | -15.4276 | -22.8325 | -36.0272 | -44.4942 | -50.5399 | 7.8831 | 7.3651 | 6.818 | 5.969 | 4.8942 | 3.7397 | 1.9688 | -0.15536 | -2.3652 | -4.8287 | -10.1453 | -19.5161 | -27.8144 | -32.5976 | 3.8276 | 3.0885 | 2.3047 | 1.0256 | -0.55461 | -2.2408 | -4.7082 | -7.6355 | -10.6769 | -14.0295 | -21.1694 | -33.8033 | -41.861 | -47.7302
|  | ELMS ROAD | ST |  |  | 4.2626 | 4.0704 | 3.742 | 3.1159 | 2.3925 | 1.5736 | 0.58675 | -0.58273 | -1.7706 | -3.2144 | -6.9354 | -19.3225 | -28.3835 | -32.9838 | 8.1597 | 7.9421 | 7.6357 | 7.1161 | 6.5249 | 5.8389 | 4.995 | 4.014 | 2.9757 | 1.7187 | -1.5632 | -12.4877 | -21.5927 | -28.7566 | 4.432 | 4.2416 | 3.943 | 3.3808 | 2.7319 | 1.9837 | 1.0602 | -0.052075 | -1.2139 | -2.636 | -6.3687 | -18.7687 | -27.7402 | -31.775
|  | ELMS ROAD | FS |  |  | 3.8874 | 3.3262 | 2.5978 | 1.3798 | 0.030025 | -1.7515 | -3.6889 | -6.3708 | -9.6295 | -12.818 | -18.6834 | -32.5307 | -39.2485 | -42.3069 | 8.1527 | 7.9298 | 7.6331 | 7.1945 | 6.6767 | 6.0763 | 5.3589 | 4.5132 | 3.6145 | 2.5718 | -0.1489 | -10.4739 | -23.6984 | -37.5406 | 4.433 | 4.2562 | 4.003 | 3.5431 | 2.9997 | 2.3745 | 1.6292 | 0.74184 | -0.20144 | -1.2914 | -4.1431 | -14.8188 | -26.6968 | -34.2429
LOVEDEAN GSP | HAVANT | EMSWORTH | MINIMUM HEADROOM | SU 74861 05807 | YES | -0.33311 | -0.98177 | -1.6256 | -2.5116 | -3.5338 | -4.593 | -6.0848 | -7.8794 | -9.9888 | -12.3257 | -17.4303 | -27.2479 | -31.5124 | -33.1645 | 2.1342 | 1.7271 | 1.3263 | 0.81476 | 0.18164 | -0.4839 | -1.5387 | -2.8375 | -4.3487 | -6.0437 | -9.7703 | -16.5404 | -21.4279 | -25.6116 | -0.25975 | -0.84529 | -1.4261 | -2.2364 | -3.1908 | -4.1858 | -5.6293 | -7.3723 | -9.4212 | -11.6948 | -16.6571 | -26.077 | -29.8885 | -31.6187
|  | EMSWORTH | CT |  |  | -0.1286 | -0.59685 | -1.1372 | -1.8992 | -2.6823 | -3.7665 | -4.8847 | -6.487 | -8.6627 | -10.8018 | -14.8177 | -25.0496 | -30.5111 | -33.1645 | 2.1497 | 1.7944 | 1.3782 | 0.87772 | 0.34565 | -0.44163 | -1.2825 | -2.5346 | -4.1099 | -5.6675 | -8.5774 | -15.8531 | -20.0393 | -23.2362 | -0.088114 | -0.51592 | -1.0145 | -1.7189 | -2.4518 | -3.484 | -4.5618 | -6.12 | -8.2159 | -10.283 | -14.156 | -23.9269 | -29.086 | -31.6187
|  | EMSWORTH | LW |  |  | -0.33311 | -0.98177 | -1.6256 | -2.5116 | -3.5338 | -4.593 | -6.0848 | -7.8794 | -9.9888 | -12.3257 | -17.4303 | -27.2479 | -31.5124 | -32.5177 | 2.1342 | 1.7271 | 1.3263 | 0.81476 | 0.18164 | -0.4839 | -1.5387 | -2.8375 | -4.3487 | -6.0437 | -9.7703 | -16.5404 | -21.4279 | -22.5303 | -0.25975 | -0.84529 | -1.4261 | -2.2364 | -3.1908 | -4.1858 | -5.6293 | -7.3723 | -9.4212 | -11.6948 | -16.6571 | -26.077 | -29.8885 | -31.08
|  | EMSWORTH | ST |  |  | 0.12149 | -0.11602 | -0.41449 | -0.7628 | -1.1652 | -1.6586 | -2.2607 | -3.017 | -3.9368 | -5.0629 | -8.0611 | -17.6612 | -24.6703 | -28.5458 | 2.3275 | 2.1465 | 1.9191 | 1.6313 | 1.292 | 0.86304 | 0.32229 | -0.34737 | -1.1784 | -2.188 | -4.8648 | -13.0922 | -19.3267 | -23.18 | 0.15349 | -0.049058 | -0.31025 | -0.63609 | -1.0201 | -1.4965 | -2.0917 | -2.8376 | -3.7569 | -4.8808 | -8.0307 | -17.89 | -24.9395 | -28.4556
|  | EMSWORTH | FS |  |  | -0.1286 | -0.59685 | -1.1372 | -1.8992 | -2.6823 | -3.7665 | -4.8847 | -6.487 | -8.6627 | -10.8018 | -14.8177 | -25.0496 | -30.5111 | -33.1645 | 2.3413 | 2.1753 | 1.9715 | 1.7353 | 1.4547 | 1.109 | 0.69903 | 0.18843 | -0.77433 | -2.1078 | -5.6068 | -13.7884 | -19.2807 | -25.6116 | 0.17376 | -0.0032816 | -0.22431 | -0.50278 | -0.8324 | -1.2373 | -1.7105 | -2.3032 | -3.0536 | -4.3315 | -8.7483 | -18.9989 | -26.0442 | -31.0725
MELKSHAM GSP | AMESBURY | ENFORD | MINIMUM HEADROOM | SU 13728 51712 | YES | 3.6918 | 3.6871 | 3.6816 | 3.6645 | 3.6454 | 3.6256 | 3.5972 | 3.5755 | 3.5371 | 3.498 | 3.3886 | 2.7254 | 2.1031 | 1.4906 | 4.1959 | 4.1454 | 4.0936 | 4.0548 | 4.0099 | 3.9611 | 3.8939 | 3.8024 | 3.6869 | 3.5579 | 3.3084 | 0.69766 | -1.0023 | -1.0953 | 3.8668 | 3.8566 | 3.8463 | 3.8385 | 3.8154 | 3.7929 | 3.7619 | 3.7416 | 3.7028 | 3.5023 | 2.3832 | -1.6961 | -3.8274 | -3.9637
|  | ENFORD | CT |  |  | 3.6918 | 3.6872 | 3.6816 | 3.6729 | 3.661 | 3.6437 | 3.6207 | 3.5944 | 3.56 | 3.5137 | 3.3886 | 2.8054 | 2.2215 | 1.9186 | 4.2238 | 4.1841 | 4.1422 | 4.0954 | 4.0396 | 3.9726 | 3.8952 | 3.8024 | 3.6869 | 3.5579 | 3.3084 | 2.7067 | 2.2452 | 1.842 | 3.8738 | 3.867 | 3.8601 | 3.849 | 3.8342 | 3.8168 | 3.7932 | 3.7711 | 3.7403 | 3.6942 | 3.6079 | 2.8708 | 2.3672 | 2.0592
|  | ENFORD | LW |  |  | 3.6923 | 3.6871 | 3.6821 | 3.6765 | 3.6679 | 3.6585 | 3.6415 | 3.6202 | 3.5888 | 3.5541 | 3.4032 | 2.7254 | 2.1031 | 1.4906 | 4.1959 | 4.1454 | 4.0936 | 4.0548 | 4.0099 | 3.9611 | 3.8939 | 3.8148 | 3.7151 | 3.604 | 3.3681 | 2.8885 | 2.4594 | 2.1466 | 3.8668 | 3.8566 | 3.8463 | 3.8385 | 3.8294 | 3.8195 | 3.8063 | 3.7913 | 3.7649 | 3.7368 | 3.5867 | 2.747 | 1.8234 | 1.1759
|  | ENFORD | ST |  |  | 3.6933 | 3.6909 | 3.6878 | 3.6645 | 3.6454 | 3.6256 | 3.5972 | 3.5755 | 3.5371 | 3.498 | 3.3997 | 3.0785 | 2.3013 | 1.7775 | 4.2483 | 4.2241 | 4.1991 | 4.1427 | 4.088 | 4.0281 | 3.9539 | 3.8833 | 3.7877 | 3.684 | 3.4257 | 2.5875 | 1.7689 | 1.1909 | 3.8771 | 3.8727 | 3.8683 | 3.8385 | 3.8154 | 3.7929 | 3.7619 | 3.7416 | 3.7028 | 3.6664 | 3.5823 | 3.3258 | 2.471 | 1.9635
|  | ENFORD | FS |  |  | 3.6918 | 3.6872 | 3.6816 | 3.6729 | 3.661 | 3.6437 | 3.6207 | 3.5944 | 3.56 | 3.5137 | 3.3886 | 2.8054 | 2.2215 | 1.9186 | 4.2498 | 4.2244 | 4.1961 | 4.1512 | 4.0983 | 4.0351 | 3.9641 | 3.8757 | 3.7691 | 3.6482 | 3.3408 | 0.69766 | -1.0023 | -1.0953 | 3.8779 | 3.8736 | 3.8691 | 3.8566 | 3.8427 | 3.8264 | 3.809 | 3.7898 | 3.763 | 3.5023 | 2.3832 | -1.6961 | -3.8274 | -3.9637
COWLEY GSP | YARNTON BSP | EYNSHAM | MINIMUM HEADROOM | SP 42236 10266 | NO | 8.8955 | 8.04 | 7.0023 | 5.5097 | 3.6358 | 1.454 | -1.2309 | -4.0649 | -7.035 | -9.8108 | -14.9666 | -24.5979 | -28.131 | -30.0917 | 11.3452 | 10.6652 | 9.8954 | 8.9462 | 7.7762 | 6.3606 | 4.5 | 2.0437 | -1.4456 | -5.5667 | -15.45 | -32.8294 | -38.1767 | -42.0424 | 8.4182 | 7.6071 | 6.6659 | 5.3505 | 3.6833 | 1.7605 | -0.76123 | -3.4979 | -6.3013 | -11.1301 | -23.101 | -44.2592 | -50.9369 | -55.8785
|  | EYNSHAM | CT |  |  | 9.0684 | 8.2101 | 7.2441 | 5.9085 | 4.3734 | 2.4143 | 0.456 | -1.9876 | -4.7928 | -7.2822 | -11.4709 | -20.0973 | -23.8595 | -25.488 | 11.3752 | 10.6652 | 9.8954 | 8.9462 | 7.8931 | 6.5237 | 5.167 | 3.4515 | 1.5796 | -0.028486 | -2.9061 | -9.2016 | -12.1328 | -13.9936 | 8.5247 | 7.7004 | 6.782 | 5.556 | 4.1674 | 2.3204 | 0.47614 | -1.8746 | -4.564 | -6.973 | -10.935 | -19.2089 | -22.7821 | -24.3173
|  | EYNSHAM | LW |  |  | 8.8955 | 8.04 | 7.0023 | 5.5097 | 3.6358 | 1.454 | -1.2309 | -4.0649 | -7.035 | -9.8108 | -14.9666 | -24.5979 | -28.131 | -30.0917 | 11.3452 | 10.7194 | 9.9902 | 9.0042 | 7.7762 | 6.3606 | 4.5 | 2.4946 | 0.49894 | -1.4592 | -6.452 | -15.1694 | -17.8695 | -19.4983 | 8.4182 | 7.6071 | 6.6659 | 5.3505 | 3.6833 | 1.7605 | -0.76123 | -3.4979 | -6.3013 | -8.9928 | -14.182 | -24.1359 | -27.5556 | -29.5087
|  | EYNSHAM | ST |  |  | 9.2533 | 8.5712 | 7.7869 | 6.7517 | 5.5963 | 4.262 | 2.9641 | 1.568 | 0.11364 | -1.2905 | -4.3165 | -13.6515 | -19.6859 | -22.0136 | 11.5222 | 10.9603 | 10.3508 | 9.5676 | 8.7096 | 7.7098 | 6.698 | 5.5826 | 4.4696 | 3.4582 | 1.1454 | -6.2938 | -11.3628 | -13.6607 | 8.7447 | 8.1388 | 7.4531 | 6.53 | 5.5003 | 4.2848 | 3.0497 | 1.6732 | 0.26064 | -1.1205 | -4.2693 | -13.4273 | -19.5274 | -21.637
|  | EYNSHAM | FS |  |  | 9.0684 | 8.2101 | 7.2441 | 5.9085 | 4.3734 | 2.4143 | 0.456 | -1.9876 | -4.7928 | -7.2822 | -11.4709 | -20.0973 | -23.8595 | -25.488 | 11.5392 | 11.1882 | 10.7175 | 10.0712 | 8.8225 | 7.1152 | 4.9021 | 2.0437 | -1.4456 | -5.5667 | -15.45 | -32.8294 | -38.1767 | -42.0424 | 8.7764 | 8.389 | 7.8597 | 7.0998 | 5.9255 | 3.9496 | 1.3657 | -2.0122 | -6.1652 | -11.1301 | -23.101 | -44.2592 | -50.9369 | -55.8785
MINETY GSP | CIRENCESTER BSP | FAIRFORD | MINIMUM HEADROOM | SP 14418 00559 | YES | 4.8222 | 4.4602 | 4.0888 | 3.6836 | 3.0914 | 2.0175 | 0.53012 | -1.4181 | -3.869 | -6.8836 | -14.6313 | -31.8332 | -44.1659 | -51.5984 | 6.3185 | 6.1116 | 5.8963 | 5.6516 | 5.3204 | 4.9283 | 4.3349 | 3.0998 | 1.2204 | -1.1036 | -7.0987 | -20.4154 | -32.1565 | -36.8418 | 4.5646 | 4.2316 | 3.8856 | 3.5075 | 3.0218 | 2.4595 | 1.6528 | -0.10831 | -2.4624 | -5.3588 | -12.8005 | -29.3229 | -43.4051 | -49.2375
|  | FAIRFORD | CT |  |  | 5.051 | 4.8413 | 4.6053 | 4.2904 | 3.9443 | 3.4654 | 2.964 | 2.2655 | 1.3366 | 0.38647 | -1.4003 | -5.6459 | -8.071 | -9.2874 | 6.3891 | 6.2422 | 6.0712 | 5.8617 | 5.6249 | 5.2708 | 4.8932 | 4.3732 | 3.7144 | 3.0236 | 1.7246 | -1.3751 | -3.2386 | -4.6697 | 4.7608 | 4.5564 | 4.3231 | 4.0182 | 3.6822 | 3.2045 | 2.6974 | 2.0175 | 1.1201 | 0.1938 | -1.5456 | -5.6516 | -7.9875 | -9.2184
|  | FAIRFORD | LW |  |  | 4.8222 | 4.4602 | 4.0888 | 3.6836 | 3.0914 | 2.0175 | 0.53012 | -1.4181 | -3.869 | -6.8836 | -14.6313 | -31.8332 | -44.1659 | -51.5984 | 6.3185 | 6.1116 | 5.8963 | 5.6516 | 5.3204 | 4.9283 | 4.3349 | 3.0998 | 1.2204 | -1.1036 | -7.0987 | -20.4154 | -30.1981 | -36.3721 | 4.5646 | 4.2316 | 3.8856 | 3.5075 | 3.0218 | 2.4595 | 1.6528 | -0.10831 | -2.4624 | -5.3588 | -12.8005 | -29.3229 | -41.296 | -48.6573
|  | FAIRFORD | ST |  |  | 5.1827 | 5.0695 | 4.9461 | 4.7451 | 4.5131 | 4.2233 | 3.8958 | 3.5423 | 3.091 | 2.5366 | 1.1255 | -3.2859 | -6.7192 | -8.6281 | 6.4696 | 6.3941 | 6.3046 | 6.1505 | 5.9757 | 5.7505 | 5.4855 | 5.1936 | 4.8093 | 4.3647 | 3.2167 | -0.36304 | -3.347 | -5.3061 | 4.8865 | 4.7814 | 4.663 | 4.4617 | 4.2321 | 3.9443 | 3.6088 | 3.2411 | 2.7667 | 2.2161 | 0.80959 | -3.5555 | -7.0129 | -8.9588
|  | FAIRFORD | FS |  |  | 5.051 | 4.8413 | 4.6053 | 4.2904 | 3.9443 | 3.4654 | 2.964 | 2.2655 | 1.3366 | 0.38647 | -1.4003 | -5.6459 | -8.071 | -9.2874 | 6.4543 | 6.3631 | 6.2534 | 6.1063 | 5.9196 | 5.6828 | 5.3887 | 5.0214 | 4.0859 | 2.6557 | -1.5435 | -18.4057 | -32.1565 | -36.8418 | 4.8867 | 4.775 | 4.6445 | 4.4475 | 4.2 | 3.8961 | 3.5232 | 2.774 | 1.3835 | -0.39418 | -5.5851 | -26.4349 | -43.4051 | -49.2375
MINETY GSP | STRATTON (2 X 60) | FARINGDON | MINIMUM HEADROOM | SU 28819 94924 | YES | -1.9953 | -2.4115 | 7.9993 | 7.5363 | 7.0442 | 6.5123 | 5.9216 | 5.3598 | 4.675 | 3.5953 | -0.52659 | -13.4037 | -20.22 | -21.0153 | 0.075791 | -0.12452 | 9.5576 | 9.326 | 9.0872 | 8.8234 | 8.5208 | 8.2201 | 7.8395 | 7.3862 | 4.6067 | -5.0961 | -10.4296 | -11.3224 | -1.7654 | 14.5605 | 14.2658 | 13.8855 | 13.4868 | 13.0594 | 12.5828 | 12.1239 | 11.5537 | 10.2264 | 6.3025 | -5.9947 | -12.633 | -13.5998
|  | FARINGDON | CT |  |  | -1.6961 | -1.929 | 8.6534 | 8.3087 | 7.9692 | 7.5899 | 7.1751 | 6.8091 | 6.2102 | 5.5666 | 4.2689 | 0.63742 | -2.3445 | -4.2168 | 0.17437 | 0.029422 | 9.7546 | 9.5403 | 9.3341 | 9.0969 | 8.8204 | 8.5736 | 8.2312 | 7.823 | 6.991 | 4.4901 | 1.8853 | -1.0847 | -1.5198 | 14.9558 | 14.8027 | 14.5193 | 14.238 | 13.9227 | 13.5697 | 13.2655 | 12.7766 | 12.2284 | 11.1249 | 8.0305 | 5.4876 | 3.8397
|  | FARINGDON | LW |  |  | -1.9953 | -2.4115 | 7.9993 | 7.5363 | 7.0442 | 6.5123 | 5.9216 | 5.3598 | 4.675 | 3.5953 | -0.52659 | -13.4037 | -20.22 | -21.0153 | 0.075791 | -0.12452 | 9.5576 | 9.326 | 9.0872 | 8.8234 | 8.5208 | 8.2201 | 7.8395 | 7.3862 | 4.6067 | -5.0961 | -10.4296 | -11.3224 | -1.7654 | 14.5605 | 14.2658 | 13.8855 | 13.4868 | 13.0594 | 12.5828 | 12.1239 | 11.5537 | 10.2264 | 6.3025 | -5.9947 | -12.633 | -13.5998
|  | FARINGDON | ST |  |  | -1.5997 | -1.7756 | 8.8622 | 8.5953 | 8.3664 | 8.1212 | 7.8323 | 7.606 | 7.3215 | 7.0318 | 6.3687 | 4.244 | 2.0338 | -0.45346 | 0.2084 | 0.087372 | 9.8348 | 9.588 | 9.3903 | 9.179 | 8.9156 | 8.7059 | 8.429 | 8.1472 | 7.497 | 5.4181 | 2.8332 | -0.6297 | -1.4473 | 15.072 | 14.9605 | 14.7048 | 14.4913 | 14.2647 | 13.9873 | 13.7713 | 13.4802 | 13.1848 | 12.5121 | 10.4816 | 8.3822 | 6.0879
|  | FARINGDON | FS |  |  | -1.6961 | -1.929 | 8.6534 | 8.3087 | 7.9692 | 7.5899 | 7.1751 | 6.8091 | 6.2102 | 5.5666 | 4.2689 | 0.63742 | -2.3445 | -4.2168 | 0.23058 | 0.10972 | 9.8577 | 9.6979 | 9.5377 | 9.3596 | 9.1696 | 8.9902 | 8.7695 | 8.5362 | 7.9995 | 6.1673 | 3.6607 | -0.55899 | -1.4037 | 15.1365 | 15.0472 | 14.8733 | 14.7041 | 14.5181 | 14.3287 | 14.161 | 13.9373 | 13.7113 | 13.2173 | 11.6004 | 10.0506 | 8.3429
LOVEDEAN GSP | WYMERING BSP | FARLINGTON | MINIMUM HEADROOM | SU 67400 04843 | YES | 12.3165 | 11.9289 | 11.381 | 10.6588 | 9.7548 | 8.4685 | 6.5758 | 4.153 | 1.1711 | -2.4742 | -11.2905 | -25.8477 | -29.9376 | -33.1422 | 12.3686 | 12.1571 | 11.6944 | 11.0907 | 10.3159 | 9.2623 | 7.7777 | 5.8776 | 3.5427 | 0.68497 | -6.2218 | -17.6429 | -21.0825 | -23.9718 | 11.5905 | 11.2393 | 10.6866 | 9.9289 | 8.9825 | 7.7562 | 5.969 | 3.6303 | 0.75561 | -2.7573 | -11.2449 | -25.2812 | -29.3673 | -32.6737
|  | FARLINGTON | CT |  |  | 12.491 | 12.2379 | 11.8259 | 11.5042 | 11.2739 | 10.943 | 10.5441 | 10.0363 | 9.4175 | 8.744 | 7.1697 | 2.8764 | 0.9392 | -0.097277 | 12.4255 | 12.2235 | 11.8708 | 11.6342 | 11.5014 | 11.2869 | 10.9592 | 10.5483 | 10.0515 | 9.4851 | 8.3684 | 4.9202 | 2.5405 | -0.038361 | 11.7229 | 11.4844 | 11.0854 | 10.7955 | 10.6001 | 10.2513 | 9.8304 | 9.2472 | 8.403 | 7.4308 | 5.5627 | 1.2625 | -0.68706 | -1.7764
|  | FARLINGTON | LW |  |  | 12.3165 | 11.9289 | 11.381 | 10.6588 | 9.7548 | 8.4685 | 6.5758 | 4.153 | 1.1711 | -2.4742 | -11.2905 | -25.8477 | -29.9376 | -33.1422 | 12.3686 | 12.1571 | 11.6944 | 11.0907 | 10.3159 | 9.2623 | 7.7777 | 5.8776 | 3.5427 | 0.68497 | -6.2218 | -17.6429 | -21.0825 | -23.9718 | 11.5905 | 11.2393 | 10.6866 | 9.9289 | 8.9825 | 7.7562 | 5.969 | 3.6303 | 0.75561 | -2.7573 | -11.2449 | -25.2812 | -29.3673 | -32.6737
|  | FARLINGTON | ST |  |  | 12.5829 | 12.4092 | 12.0792 | 11.7871 | 11.622 | 11.434 | 11.1857 | 10.9566 | 10.6625 | 10.324 | 9.4666 | 5.0795 | 1.4511 | 0.0037074 | 12.4666 | 12.3021 | 11.9899 | 11.7125 | 11.5774 | 11.4301 | 11.2271 | 11.0603 | 10.838 | 10.5942 | 9.8807 | 5.9233 | 2.0224 | -0.79555 | 11.7981 | 11.6246 | 11.2946 | 10.9934 | 10.8318 | 10.6518 | 10.4082 | 10.1955 | 9.9183 | 9.6052 | 8.3682 | 3.4108 | -0.29625 | -1.8625
|  | FARLINGTON | FS |  |  | 12.491 | 12.2379 | 11.8259 | 11.5042 | 11.2739 | 10.943 | 10.5441 | 10.0363 | 9.4175 | 8.744 | 7.1697 | 2.8764 | 0.9392 | -0.097277 | 12.4777 | 12.3969 | 12.2506 | 12.0879 | 11.9533 | 11.8267 | 11.6939 | 11.567 | 11.4102 | 11.2335 | 10.8029 | 7.9595 | 3.1696 | -2.7474 | 11.812 | 11.7287 | 11.5749 | 11.3982 | 11.2471 | 11.1021 | 10.9475 | 10.7998 | 10.6261 | 10.4292 | 9.8887 | 6.6093 | 2.5808 | -0.10753
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH | MINIMUM HEADROOM | SU 88404 53930 | YES | 12.0602 | 10.8627 | 9.839 | 8.538 | 6.8206 | 4.9515 | 2.2007 | -0.94651 | -4.3154 | -8.886 | -21.7288 | -51.3047 | -66.4525 | -71.8841 | 15.2267 | 14.4767 | 13.8173 | 13.0251 | 11.9478 | 10.764 | 8.8942 | 6.7175 | 4.3675 | 1.267 | -8.5082 | -31.0311 | -42.5334 | -46.6968 | 12.4823 | 11.427 | 10.4977 | 9.3017 | 7.7157 | 5.9867 | 3.3584 | 0.3766 | -2.8368 | -6.9823 | -19.2755 | -47.5688 | -62.0337 | -67.2103
|  | FARNBOROUGH | CT |  |  | 12.4172 | 11.53 | 10.735 | 9.7369 | 8.4625 | 6.7203 | 4.6866 | 2.1481 | -0.93731 | -3.8205 | -9.1935 | -21.6442 | -27.2479 | -29.3396 | 15.2864 | 14.6269 | 13.9903 | 13.2836 | 12.4324 | 11.2284 | 9.8427 | 8.0029 | 5.8231 | 3.7463 | -0.171 | -9.5179 | -14.744 | -19.3035 | 12.7527 | 11.9527 | 11.1918 | 10.2358 | 9.0754 | 7.4683 | 5.6034 | 3.2066 | 0.28041 | -2.4716 | -7.604 | -19.4734 | -24.686 | -26.5826
|  | FARNBOROUGH | LW |  |  | 12.0602 | 10.8627 | 9.839 | 8.538 | 6.8206 | 4.9515 | 2.2007 | -0.94651 | -4.3154 | -8.886 | -21.7288 | -51.3047 | -66.4525 | -71.8841 | 15.2267 | 14.4767 | 13.8173 | 13.0251 | 11.9478 | 10.764 | 8.8942 | 6.7175 | 4.3675 | 1.267 | -8.5082 | -31.0311 | -42.5334 | -46.6968 | 12.4823 | 11.427 | 10.4977 | 9.3017 | 7.7157 | 5.9867 | 3.3584 | 0.3766 | -2.8368 | -6.9823 | -19.2755 | -47.5688 | -62.0337 | -67.2103
|  | FARNBOROUGH | ST |  |  | 12.7549 | 12.1638 | 11.6866 | 11.2735 | 10.6599 | 9.9144 | 8.8616 | 7.7517 | 6.6174 | 5.3053 | 1.8273 | -9.7341 | -17.7095 | -21.3695 | 15.5359 | 15.1149 | 14.742 | 14.3588 | 13.8429 | 13.211 | 12.3896 | 11.4872 | 10.5273 | 9.3909 | 6.3631 | -3.7932 | -11.4795 | -16.5403 | 13.0985 | 12.6138 | 12.1962 | 11.7851 | 11.201 | 10.4793 | 9.5266 | 8.4928 | 7.4124 | 6.1349 | 2.6652 | -8.979 | -16.8902 | -19.9386
|  | FARNBOROUGH | FS |  |  | 12.4172 | 11.53 | 10.735 | 9.7369 | 8.4625 | 6.7203 | 4.6866 | 2.1481 | -0.93731 | -3.8205 | -9.1935 | -21.6442 | -27.2479 | -29.3396 | 15.5171 | 15.1126 | 14.7203 | 14.3066 | 13.7581 | 13.0877 | 12.2267 | 11.2223 | 10.0728 | 8.7882 | 3.0394 | -8.5998 | -16.6948 | -28.6252 | 13.0874 | 12.6426 | 12.2316 | 11.7733 | 11.1533 | 10.391 | 9.4072 | 8.2659 | 6.7978 | 3.853 | -3.5229 | -18.0689 | -24.7058 | -29.6265
BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM | MINIMUM HEADROOM | SU 84517 47217 | YES | 2.3271 | 1.3436 | 0.2847 | -1.1238 | -2.9215 | -4.887 | -7.9219 | -12.7734 | -19.8255 | -28.4974 | -50.1434 | -94.5443 | -109.4963 | -113.1493 | 6.4351 | 5.9994 | 5.3686 | 4.3651 | 2.7899 | 0.6103 | -2.5304 | -6.7086 | -12.0433 | -18.7274 | -35.4812 | -69.7999 | -81.161 | -83.9152 | 2.1549 | 1.257 | 0.26374 | -1.0337 | -2.6757 | -4.4979 | -8.1685 | -13.6551 | -20.4125 | -28.73 | -49.5001 | -92.082 | -106.3653 | -109.8242
|  | FARNHAM | CT |  |  | 2.5736 | 1.8861 | 0.99267 | -0.19079 | -1.5287 | -3.463 | -5.6118 | -8.733 | -12.7406 | -16.6969 | -24.6129 | -42.7392 | -50.1279 | -52.8943 | 6.477 | 6.2195 | 5.5096 | 4.5592 | 3.4828 | 1.8662 | 0.057425 | -2.6226 | -5.9269 | -9.1873 | -15.3931 | -29.4973 | -36.2084 | -41.2707 | 2.395 | 1.8091 | 1.0324 | -0.0006746 | -1.2773 | -3.296 | -5.5388 | -8.8564 | -13.0744 | -17.2147 | -25.047 | -42.5807 | -49.5826 | -52.1456
|  | FARNHAM | LW |  |  | 2.3271 | 1.3436 | 0.2847 | -1.1238 | -2.9215 | -4.887 | -7.9219 | -12.7734 | -19.8255 | -28.4974 | -50.1434 | -94.5443 | -109.4963 | -113.1493 | 6.4351 | 5.9994 | 5.3686 | 4.3651 | 2.7899 | 0.6103 | -2.5304 | -6.7086 | -12.0433 | -18.7274 | -35.4812 | -69.7999 | -81.161 | -83.9152 | 2.1549 | 1.257 | 0.26374 | -1.0337 | -2.6757 | -4.4979 | -8.1685 | -13.6551 | -20.4125 | -28.73 | -49.5001 | -92.082 | -106.3653 | -109.8242
|  | FARNHAM | ST |  |  | 3.0436 | 2.7906 | 2.3939 | 1.8798 | 1.2362 | 0.41761 | -0.62822 | -1.915 | -3.4059 | -5.242 | -10.6067 | -28.7717 | -40.6174 | -44.5078 | 6.6457 | 6.5505 | 6.3177 | 6.0947 | 5.5295 | 4.7299 | 3.7019 | 2.4512 | 0.98566 | -0.81947 | -5.6533 | -21.0638 | -31.8502 | -37.2259 | 2.8109 | 2.6059 | 2.267 | 1.8204 | 1.2734 | 0.5791 | -0.50771 | -1.9358 | -3.6268 | -5.7201 | -11.3964 | -29.7871 | -41.4996 | -45.126
|  | FARNHAM | FS |  |  | 2.5736 | 1.8861 | 0.99267 | -0.19079 | -1.5287 | -3.463 | -5.6118 | -8.733 | -12.7406 | -16.6969 | -24.6129 | -42.7392 | -50.1279 | -52.8943 | 6.7337 | 6.4792 | 6.1278 | 5.7439 | 5.2661 | 4.0329 | 2.3386 | 0.038985 | -2.7998 | -6.3439 | -15.6738 | -36.6453 | -49.7383 | -57.8342 | 2.9323 | 2.6361 | 2.2475 | 1.7479 | 1.1396 | 0.069462 | -1.8746 | -4.503 | -7.9386 | -12.5016 | -24.1122 | -50.0132 | -66.3598 | -76.6376
IVER 132KV | SLOUGH | FARNHAM ROYAL | MINIMUM HEADROOM | SU 95597 82844 | YES | 12.6373 | 11.9719 | 11.2173 | 1.6513 | -8.1437 | -12.714 | -18.3126 | -23.404 | -28.1396 | -32.7434 | -47.476 | -78.5655 | -97.7225 | -108.1055 | 17.1711 | 16.7799 | 16.3402 | 5.3898 | -5.7108 | -10.2892 | -16.0079 | -20.969 | -25.2778 | -29.271 | -41.1824 | -66.6254 | -82.0563 | -90.5592 | 10.6746 | 10.0701 | 9.3913 | -2.1409 | -13.8515 | -19.0397 | -25.3785 | -30.991 | -36.0643 | -40.8793 | -55.3429 | -86.3439 | -105.1904 | -115.4068
|  | FARNHAM ROYAL | CT |  |  | 13.1715 | 12.8518 | 12.418 | 3.202 | -6.085 | -10.261 | -15.0222 | -19.4397 | -23.9626 | -28.0132 | -34.8538 | -50.215 | -57.8212 | -61.054 | 17.2862 | 16.9784 | 16.5852 | 5.7228 | -5.2048 | -9.7086 | -14.9513 | -19.5894 | -23.8505 | -27.5692 | -33.6126 | -46.8249 | -55.6038 | -64.6165 | 11.2262 | 10.9668 | 10.5624 | -0.59344 | -11.8161 | -16.6265 | -22.1653 | -27.1657 | -32.0496 | -36.3577 | -43.4528 | -58.7968 | -66.1389 | -69.2175
|  | FARNHAM ROYAL | LW |  |  | 12.6373 | 11.9719 | 11.2173 | 1.6513 | -8.1437 | -12.714 | -18.3126 | -23.404 | -28.1396 | -32.7434 | -47.476 | -78.5655 | -97.7225 | -108.1055 | 17.1711 | 16.7799 | 16.3402 | 5.3898 | -5.7108 | -10.2892 | -16.0079 | -20.969 | -25.2778 | -29.271 | -41.1824 | -66.6254 | -82.0563 | -90.5592 | 10.6746 | 10.0701 | 9.3913 | -2.1409 | -13.8515 | -19.0397 | -25.3785 | -30.991 | -36.0643 | -40.8793 | -55.3429 | -86.3439 | -105.1904 | -115.4068
|  | FARNHAM ROYAL | ST |  |  | 13.466 | 13.3812 | 13.1913 | 4.6695 | -3.9036 | -6.8821 | -10.4026 | -13.6045 | -16.4378 | -19.0332 | -23.8309 | -35.1943 | -43.414 | -48.3783 | 17.4657 | 17.3164 | 17.0913 | 6.4888 | -4.1489 | -7.8222 | -12.1534 | -16.0361 | -19.4455 | -22.5044 | -27.9563 | -39.6003 | -49.6218 | -59.3171 | 11.4878 | 11.4356 | 11.3013 | 0.74487 | -9.8503 | -13.4622 | -17.7318 | -21.5628 | -24.9021 | -27.8987 | -33.2415 | -44.9086 | -53.1126 | -57.7919
|  | FARNHAM ROYAL | FS |  |  | 13.1715 | 12.8518 | 12.418 | 3.202 | -6.085 | -10.261 | -15.0222 | -19.4397 | -23.9626 | -28.0132 | -34.8538 | -50.215 | -57.8212 | -61.054 | 17.4639 | 17.2746 | 17.019 | 6.4601 | -4.1658 | -7.5819 | -11.5522 | -15.4665 | -18.9041 | -21.9951 | -28.0251 | -40.8788 | -56.4615 | -76.2132 | 11.4828 | 11.3953 | 11.2513 | 0.75222 | -9.8325 | -13.191 | -17.0907 | -20.9329 | -24.2757 | -27.2454 | -32.9737 | -46.7495 | -60.7161 | -67.4721
LALEHAM | EAST BEDFONT A | FELTHAM | MINIMUM HEADROOM | TQ 10628 72811 | YES | 13.2698 | 12.6926 | 12.1677 | 11.4967 | 10.7545 | 9.9635 | 8.7438 | 6.5625 | 3.178 | -0.85453 | -10.5494 | -26.0272 | -30.018 | -32.8298 | 14.1105 | 13.6606 | 13.3486 | 13.0583 | 12.7689 | 12.3827 | 11.4766 | 9.5405 | 6.9219 | 3.7972 | -3.6583 | -15.4825 | -18.4827 | -34.5497 | 12.7481 | 12.1296 | 11.6134 | 10.9787 | 10.2417 | 9.4248 | 8.1862 | 6.1116 | 2.8927 | -0.94768 | -10.1945 | -24.9913 | -28.7808 | -31.456
|  | FELTHAM | CT |  |  | 13.4934 | 13.1314 | 12.733 | 12.133 | 11.4466 | 10.435 | 9.1682 | 6.5625 | 3.178 | -0.85453 | -10.5494 | -26.0272 | -30.018 | -32.8298 | 14.2526 | 13.9583 | 13.7248 | 13.4217 | 13.0233 | 12.3827 | 11.4766 | 9.5405 | 6.9219 | 3.7972 | -3.6583 | -15.4825 | -18.4827 | -21.4485 | 12.9897 | 12.6074 | 12.245 | 11.6986 | 10.9814 | 9.9194 | 8.6519 | 6.1116 | 2.8927 | -0.94768 | -10.1945 | -24.9913 | -28.7808 | -31.456
|  | FELTHAM | LW |  |  | 13.2698 | 12.6926 | 12.1677 | 11.4967 | 10.7545 | 9.9635 | 8.7438 | 7.036 | 5.1422 | 3.0663 | -1.4728 | -8.8824 | -21.9108 | -28.9258 | 14.1105 | 13.6606 | 13.3486 | 13.0583 | 12.7689 | 12.4865 | 12.086 | 10.878 | 9.5754 | 8.126 | 4.9211 | -1.4829 | -12.1212 | -17.6053 | 12.7481 | 12.1296 | 11.6134 | 10.9787 | 10.2417 | 9.4248 | 8.1862 | 6.5317 | 4.7601 | 2.8088 | -1.469 | -8.6316 | -21.0359 | -27.7517
|  | FELTHAM | ST |  |  | 13.7375 | 13.5792 | 13.4128 | 13.2165 | 12.9895 | 12.6727 | 12.1889 | 11.4352 | 10.52 | 9.4335 | 6.7508 | -0.72571 | -5.6723 | -7.0454 | 14.3703 | 14.1935 | 14.1169 | 14.0061 | 13.8851 | 13.6827 | 13.3639 | 12.7442 | 11.8067 | 10.715 | 8.0963 | -0.034764 | -8.0008 | -16.6427 | 13.2194 | 13.0319 | 12.8927 | 12.7172 | 12.5123 | 12.1286 | 11.5335 | 10.752 | 9.8628 | 8.8141 | 6.2522 | -1.2471 | -6.0121 | -7.3184
|  | FELTHAM | FS |  |  | 13.4934 | 13.1314 | 12.733 | 12.133 | 11.4466 | 10.435 | 9.1682 | 6.5625 | 3.178 | -0.85453 | -10.5494 | -26.0272 | -30.018 | -32.8298 | 14.4977 | 14.2252 | 14.0124 | 13.8123 | 13.5632 | 13.286 | 12.916 | 12.4505 | 11.6366 | 10.5636 | 7.8581 | -1.5846 | -15.3192 | -34.5497 | 13.342 | 13.0847 | 12.8648 | 12.6363 | 12.355 | 12.0423 | 11.6375 | 11.0127 | 10.2889 | 9.4264 | 6.2662 | -5.2017 | -11.9242 | -12.7701
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN | MINIMUM HEADROOM | SU 06593 00685 | YES | 6.4708 | 5.0265 | 3.6554 | 1.5493 | -0.9676 | -3.7595 | -8.3446 | -13.8439 | -19.7995 | -26.3921 | -40.7142 | -66.5473 | -76.0683 | -81.4856 | 12.0651 | 11.4509 | 11.0031 | 9.6759 | 8.0212 | 5.5765 | 2.2864 | -1.8843 | -6.2713 | -11.1723 | -21.8961 | -40.4068 | -49.5118 | -57.7984 | 7.8402 | 6.4546 | 5.1462 | 3.1615 | 0.77841 | -1.8701 | -6.3595 | -11.717 | -17.4833 | -23.8801 | -37.7996 | -62.5937 | -71.8233 | -76.9381
|  | FERNDOWN | CT |  |  | 6.7224 | 5.5669 | 4.3338 | 2.3515 | 0.3541 | -2.6977 | -6.4503 | -11.5572 | -17.8033 | -23.9093 | -35.3951 | -62.8884 | -76.0683 | -81.4856 | 12.0651 | 11.4509 | 11.0031 | 9.6759 | 8.1073 | 5.5765 | 2.5929 | -1.4325 | -6.0849 | -10.6283 | -19.12 | -39.4628 | -49.5118 | -55.382 | 8.1224 | 6.9066 | 5.7025 | 3.8141 | 1.9146 | -1.0458 | -4.7253 | -9.7011 | -15.749 | -21.6593 | -32.7494 | -59.278 | -71.8233 | -76.9381
|  | FERNDOWN | LW |  |  | 6.4708 | 5.0265 | 3.6554 | 1.5493 | -0.9676 | -3.7595 | -8.3446 | -13.8439 | -19.7995 | -26.3921 | -40.7142 | -66.5473 | -74.1017 | -69.6359 | 12.1003 | 11.5918 | 11.164 | 9.8515 | 8.0212 | 5.9612 | 2.2864 | -1.8843 | -6.2713 | -11.1723 | -21.8961 | -40.4068 | -45.1512 | -41.2054 | 7.8402 | 6.4546 | 5.1462 | 3.1615 | 0.77841 | -1.8701 | -6.3595 | -11.717 | -17.4833 | -23.8801 | -37.7996 | -62.5937 | -69.6846 | -65.197
|  | FERNDOWN | ST |  |  | 7.0513 | 6.5997 | 6.3283 | 5.4297 | 4.466 | 3.0483 | 1.0474 | -1.0236 | -3.243 | -6.1786 | -14.1562 | -40.4063 | -59.0327 | -66.1986 | 12.2547 | 11.8188 | 11.5739 | 11.0047 | 10.5933 | 9.8879 | 8.0486 | 6.1018 | 4.1068 | 1.6363 | -5.0862 | -26.9093 | -42.5747 | -49.3763 | 8.7864 | 8.203 | 7.704 | 6.7812 | 5.8462 | 4.4716 | 2.5364 | 0.51367 | -1.7271 | -4.6116 | -12.4803 | -38.8711 | -57.4926 | -64.2266
|  | FERNDOWN | FS |  |  | 6.7224 | 5.5669 | 4.3338 | 2.3515 | 0.3541 | -2.6977 | -6.4503 | -11.5572 | -17.8033 | -23.9093 | -35.3951 | -62.8884 | -76.0683 | -81.4856 | 12.2819 | 12.0461 | 11.8286 | 11.4735 | 11.1281 | 10.6472 | 9.4637 | 7.9248 | 6.216 | 4.2701 | -0.85252 | -19.7066 | -41.5065 | -57.7984 | 8.7945 | 8.4021 | 7.9617 | 7.2565 | 6.4508 | 5.3948 | 4.0179 | 2.4195 | 0.59457 | -1.6444 | -7.598 | -29.5085 | -54.2663 | -69.175
BRAMLEY (FLEE) | FERNHURST | FIVE OAKS | MINIMUM HEADROOM | TQ 10647 29057 | YES | 4.9423 | 4.098 | 3.2457 | 2.2941 | 0.95843 | -0.76452 | -3.1537 | -6.4659 | -10.0983 | -13.7475 | -21.4759 | -35.673 | -42.2601 | -44.0993 | 7.2735 | 6.6946 | 6.0084 | 5.2251 | 4.3189 | 2.9255 | 1.3311 | -1.0681 | -3.9512 | -6.7242 | -12.7152 | -24.3408 | -29.4406 | -31.2312 | 4.5187 | 3.7673 | 3.0081 | 2.0841 | 0.84619 | -0.86087 | -3.072 | -6.2344 | -9.7119 | -13.2795 | -21.1037 | -35.2175 | -41.5179 | -43.365
|  | FIVE OAKS | CT |  |  | 4.9724 | 4.2168 | 3.328 | 2.2947 | 1.0872 | -0.76452 | -2.9051 | -6.0854 | -9.8753 | -13.3686 | -19.9224 | -35.673 | -42.2601 | -44.0993 | 7.2735 | 6.6946 | 6.0084 | 5.2251 | 4.3189 | 2.9255 | 1.3311 | -1.0681 | -3.9512 | -6.7242 | -11.9086 | -24.3408 | -29.4406 | -31.2312 | 4.5552 | 3.8837 | 3.0865 | 2.0841 | 0.92368 | -0.86087 | -2.9139 | -5.9737 | -9.6649 | -13.165 | -19.6846 | -35.2175 | -41.5179 | -43.365
|  | FIVE OAKS | LW |  |  | 4.9423 | 4.098 | 3.2457 | 2.2941 | 0.95843 | -0.53391 | -3.1537 | -6.4659 | -10.0983 | -13.7475 | -21.4759 | -33.8143 | -36.6962 | -34.2654 | 7.3294 | 6.7256 | 6.1175 | 5.4252 | 4.4491 | 3.3771 | 1.4596 | -0.95558 | -3.6297 | -6.5031 | -12.7152 | -22.4747 | -24.746 | -22.704 | 4.5187 | 3.7673 | 3.0081 | 2.1252 | 0.84619 | -0.56964 | -3.072 | -6.2344 | -9.7119 | -13.2795 | -21.1037 | -33.4703 | -36.3491 | -33.7258
|  | FIVE OAKS | ST |  |  | 5.4217 | 5.0934 | 4.6843 | 4.0795 | 3.3004 | 2.3211 | 1.0408 | -0.52183 | -2.3308 | -4.306 | -9.4935 | -25.8738 | -36.4398 | -39.4373 | 7.6053 | 7.3558 | 7.0423 | 6.5521 | 5.9519 | 5.2057 | 4.2254 | 3.0519 | 1.6723 | 0.091139 | -4.2023 | -17.516 | -26.2567 | -29.0217 | 4.9557 | 4.6613 | 4.2982 | 3.7374 | 3.0411 | 2.1351 | 0.91091 | -0.56886 | -2.2991 | -4.2522 | -9.5972 | -26.0154 | -36.6105 | -39.6599
|  | FIVE OAKS | FS |  |  | 4.9724 | 4.2168 | 3.328 | 2.2947 | 1.0872 | -0.76452 | -2.9051 | -6.0854 | -9.8753 | -13.3686 | -19.9224 | -35.673 | -42.2601 | -44.0993 | 7.6273 | 7.433 | 7.1775 | 6.8271 | 6.3739 | 5.7955 | 5.0602 | 4.1474 | 3.1293 | 2.0348 | -0.89436 | -11.8307 | -23.8047 | -30.7594 | 4.9997 | 4.7818 | 4.4943 | 4.0791 | 3.5452 | 2.863 | 1.9371 | 0.78705 | -0.50475 | -1.8756 | -5.5288 | -19.1735 | -33.9235 | -42.236
AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH | MINIMUM HEADROOM | SU 90667 89318 | YES | 14.086 | 13.5577 | 13.0368 | 12.2383 | 11.263 | 10.2522 | 8.7041 | 6.8369 | 4.6185 | 1.758 | -4.4934 | -15.5492 | -18.7196 | -20.2726 | 16.2771 | 16.1116 | 15.9509 | 15.7545 | 15.4788 | 15.1631 | 14.2643 | 12.5891 | 10.6569 | 8.5825 | 3.8927 | -4.1408 | -7.8093 | -13.1426 | 13.0256 | 12.4703 | 11.9238 | 11.1299 | 10.075 | 8.9752 | 7.1675 | 4.946 | 2.4454 | -0.34258 | -6.443 | -17.1596 | -20.1283 | -21.5358
|  | FLACKWELL HEATH | CT |  |  | 14.2605 | 13.949 | 13.529 | 12.8264 | 12.0649 | 11.0067 | 9.8618 | 8.2098 | 5.5954 | 2.9682 | -1.9358 | -13.6415 | -18.6027 | -20.2726 | 16.2974 | 16.1735 | 16.0324 | 15.8745 | 15.6976 | 15.4168 | 14.3646 | 12.6997 | 10.6569 | 8.6864 | 5.0167 | -3.8192 | -7.8093 | -10.2728 | 13.1905 | 12.7831 | 12.2885 | 11.4966 | 10.6332 | 9.3678 | 7.9909 | 5.9365 | 3.2916 | 0.73947 | -4.0144 | -15.3078 | -19.9975 | -21.5358
|  | FLACKWELL HEATH | LW |  |  | 14.086 | 13.5577 | 13.0368 | 12.2383 | 11.263 | 10.2522 | 8.7041 | 6.8369 | 4.6185 | 1.758 | -4.4934 | -15.5492 | -18.7196 | -16.3504 | 16.2771 | 16.1116 | 15.9509 | 15.7545 | 15.4788 | 15.1631 | 14.2643 | 12.5891 | 10.7136 | 8.5825 | 3.8927 | -4.1408 | -6.0701 | -3.9378 | 13.0256 | 12.4703 | 11.9238 | 11.1299 | 10.075 | 8.9752 | 7.1675 | 4.946 | 2.4454 | -0.34258 | -6.443 | -17.1596 | -20.1283 | -17.703
|  | FLACKWELL HEATH | ST |  |  | 14.3677 | 14.3246 | 14.266 | 14.1303 | 13.8431 | 13.4592 | 12.9499 | 12.2928 | 11.5236 | 10.5608 | 7.2109 | -5.1688 | -13.3996 | -16.2047 | 16.3884 | 16.3456 | 16.2884 | 16.1968 | 16.0801 | 15.9305 | 15.7358 | 15.4965 | 15.114 | 13.9898 | 10.8986 | 0.69392 | -6.2935 | -9.3711 | 13.4971 | 13.3714 | 13.2015 | 12.949 | 12.6135 | 12.1017 | 11.4222 | 10.5468 | 9.5263 | 8.2436 | 4.6264 | -7.5093 | -15.569 | -18.1736
|  | FLACKWELL HEATH | FS |  |  | 14.2605 | 13.949 | 13.529 | 12.8264 | 12.0649 | 11.0067 | 9.8618 | 8.2098 | 5.5954 | 2.9682 | -1.9358 | -13.6415 | -18.6027 | -20.2726 | 16.3873 | 16.3478 | 16.2954 | 16.2226 | 16.1269 | 16.004 | 15.847 | 15.65 | 15.4219 | 15.1441 | 12.9777 | 4.555 | -5.5456 | -13.1426 | 13.4972 | 13.3877 | 13.2404 | 13.02 | 12.7364 | 12.3655 | 11.8515 | 11.2129 | 10.4445 | 9.5305 | 7.043 | -2.651 | -13.787 | -20.4868
NURSLING GSP | ROWNHAMS | FLETCHWOOD | MINIMUM HEADROOM | SU 33800 12142 | YES | 10.5736 | 9.9672 | 9.3795 | 8.3205 | 7.0791 | 5.6807 | 3.6446 | 1.4535 | -1.4278 | -5.4402 | -14.5581 | -29.9774 | -34.8148 | -37.6888 | 12.6206 | 12.2734 | 11.9402 | 11.3382 | 10.6015 | 9.749 | 8.3456 | 6.8299 | 5.366 | 3.2571 | -3.4969 | -14.8307 | -18.2605 | -20.6098 | 9.8858 | 9.3364 | 8.7968 | 7.8257 | 6.676 | 5.3789 | 3.4413 | 1.3493 | -0.82719 | -3.206 | -11.4971 | -26.199 | -30.8292 | -33.6841
|  | FLETCHWOOD | CT |  |  | 11.0581 | 10.7561 | 10.4258 | 9.6996 | 8.8838 | 7.8381 | 6.4198 | 4.8205 | 2.6811 | 0.47293 | -3.9682 | -13.551 | -18.4815 | -20.5494 | 12.7588 | 12.5123 | 12.2315 | 11.7807 | 11.2616 | 10.5525 | 9.504 | 8.292 | 6.9436 | 5.5707 | 2.8815 | -3.2717 | -6.9289 | -9.9766 | 10.2867 | 9.9886 | 9.654 | 8.9774 | 8.2145 | 7.2113 | 5.8447 | 4.2683 | 2.2523 | 0.2139 | -3.7791 | -12.4928 | -17.0747 | -19.0356
|  | FLETCHWOOD | LW |  |  | 10.5736 | 9.9672 | 9.3795 | 8.3205 | 7.0791 | 5.6807 | 3.6446 | 1.4535 | -1.4278 | -5.4402 | -14.5581 | -29.9774 | -34.8148 | -37.6888 | 12.6206 | 12.2734 | 11.9402 | 11.3382 | 10.6015 | 9.749 | 8.3456 | 6.8299 | 5.366 | 3.2571 | -3.4969 | -14.8307 | -18.2605 | -20.6098 | 9.8858 | 9.3364 | 8.7968 | 7.8257 | 6.676 | 5.3789 | 3.4413 | 1.3493 | -0.82719 | -3.206 | -11.4971 | -26.199 | -30.8292 | -33.6841
|  | FLETCHWOOD | ST |  |  | 11.2619 | 11.1216 | 10.9718 | 10.6344 | 10.2582 | 9.8136 | 8.9968 | 8.2393 | 7.6223 | 6.8991 | 4.8834 | -2.0604 | -7.87 | -11.8954 | 12.8952 | 12.7708 | 12.6282 | 12.3116 | 11.9809 | 11.5918 | 10.8532 | 10.1699 | 9.6286 | 8.9895 | 7.3567 | 1.9827 | -2.9393 | -6.9685 | 10.4897 | 10.3608 | 10.2168 | 9.8701 | 9.4966 | 9.0573 | 8.2503 | 7.5055 | 6.8844 | 6.1486 | 4.2646 | -2.0972 | -7.6533 | -11.3582
|  | FLETCHWOOD | FS |  |  | 11.0581 | 10.7561 | 10.4258 | 9.6996 | 8.8838 | 7.8381 | 6.4198 | 4.8205 | 2.6811 | 0.47293 | -3.9682 | -13.551 | -18.4815 | -20.5494 | 12.9177 | 12.7883 | 12.6485 | 12.4429 | 12.1936 | 11.8977 | 11.4686 | 10.9939 | 10.4799 | 9.9172 | 8.5678 | 3.8319 | -2.3736 | -9.2655 | 10.5303 | 10.4155 | 10.295 | 10.0546 | 9.7649 | 9.426 | 8.9488 | 8.4239 | 7.8148 | 7.1563 | 5.6126 | 0.27662 | -5.8398 | -10.5628
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE | MINIMUM HEADROOM | SU 14069 15523 | YES | 7.1052 | 6.8203 | 6.484 | 6.1002 | 5.4053 | 4.2829 | 2.7066 | 0.54914 | -2.1063 | -5.263 | -13.1496 | -25.6221 | -28.7858 | -30.9977 | 8.0214 | 7.867 | 7.6835 | 7.4759 | 7.2201 | 6.8885 | 5.8508 | 4.2329 | 2.237 | -0.15504 | -6.1807 | -15.6835 | -17.9964 | -19.6846 | 6.7282 | 6.4736 | 6.1777 | 5.8189 | 5.1538 | 4.0931 | 2.5988 | 0.55187 | -1.972 | -4.9808 | -12.5123 | -24.427 | -27.4261 | -29.5338
|  | FORDINGBRIDGE | CT |  |  | 7.286 | 7.1339 | 6.9306 | 6.6849 | 6.42 | 6.0563 | 5.6335 | 5.0202 | 4.2241 | 3.5082 | 2.052 | -1.0835 | -2.8658 | -3.4152 | 8.0919 | 7.9978 | 7.8744 | 7.7394 | 7.5919 | 7.383 | 7.1397 | 6.7778 | 6.3253 | 5.9181 | 5.0793 | 3.1032 | 1.8457 | 1.065 | 6.9111 | 6.7831 | 6.6148 | 6.3974 | 6.1625 | 5.8437 | 5.4743 | 4.939 | 4.2322 | 3.5964 | 2.3049 | -0.51397 | -2.1288 | -2.6268
|  | FORDINGBRIDGE | LW |  |  | 7.1052 | 6.8203 | 6.484 | 6.1002 | 5.4053 | 4.2829 | 2.7066 | 0.54914 | -2.1063 | -5.263 | -13.1496 | -25.6221 | -28.7858 | -30.9977 | 8.0214 | 7.867 | 7.6835 | 7.4759 | 7.2201 | 6.8885 | 5.8508 | 4.2329 | 2.237 | -0.15504 | -6.1807 | -15.6835 | -17.9964 | -19.6846 | 6.7282 | 6.4736 | 6.1777 | 5.8189 | 5.1538 | 4.0931 | 2.5988 | 0.55187 | -1.972 | -4.9808 | -12.5123 | -24.427 | -27.4261 | -29.5338
|  | FORDINGBRIDGE | ST |  |  | 7.3752 | 7.2786 | 7.1376 | 7.0277 | 6.9062 | 6.7368 | 6.5274 | 6.223 | 5.8988 | 5.6145 | 4.966 | 3.3562 | 2.1062 | 1.0544 | 8.1413 | 8.0816 | 7.9971 | 7.9282 | 7.85 | 7.7418 | 7.6068 | 7.4093 | 7.1941 | 7.0023 | 6.5496 | 5.3227 | 4.2993 | 3.2969 | 6.9944 | 6.9177 | 6.8064 | 6.7153 | 6.6136 | 6.4747 | 6.3028 | 6.0525 | 5.7825 | 5.5458 | 5.0006 | 3.5761 | 2.4519 | 1.484
|  | FORDINGBRIDGE | FS |  |  | 7.286 | 7.1339 | 6.9306 | 6.6849 | 6.42 | 6.0563 | 5.6335 | 5.0202 | 4.2241 | 3.5082 | 2.052 | -1.0835 | -2.8658 | -3.4152 | 8.1484 | 8.0906 | 8.014 | 7.9457 | 7.8689 | 7.769 | 7.651 | 7.4933 | 7.3067 | 7.1296 | 6.7327 | 5.521 | 4.079 | 2.3994 | 7.01 | 6.9443 | 6.8556 | 6.7607 | 6.658 | 6.5259 | 6.376 | 6.1772 | 5.9347 | 5.7103 | 5.2304 | 3.8263 | 2.4706 | 1.3554
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK | MINIMUM HEADROOM | SU 66139 00180 | YES | 0.92878 | 0.27409 | -0.38507 | -1.6196 | -2.9085 | -4.2066 | -5.5909 | -7.0518 | -8.5901 | -10.1963 | -13.5853 | -20.3991 | -33.0759 | -40.3807 | 7.6308 | 7.1483 | 6.6012 | 5.7843 | 4.8912 | 3.8711 | 2.6748 | 1.2964 | -0.31606 | -2.1395 | -6.5608 | -23.7327 | -56.7153 | -119.3222 | 2.3066 | 1.7593 | 1.2062 | 0.13286 | -0.99405 | -2.1394 | -3.3804 | -4.6931 | -6.0773 | -7.5282 | -10.5966 | -17.5142 | -30.0047 | -37.1173
|  | FRATTON PARK | CT |  |  | 1.4662 | 1.1224 | 0.75139 | -0.13555 | -1.0699 | -2.0633 | -3.0586 | -4.1676 | -5.6798 | -7.2006 | -10.1852 | -17.5726 | -21.1783 | -22.0137 | 7.6308 | 7.1483 | 6.6012 | 5.7843 | 4.8912 | 3.8711 | 2.7473 | 1.464 | -0.10009 | -1.7743 | -5.4273 | -17.6428 | -35.6839 | -65.5518 | 2.7779 | 2.5046 | 2.2058 | 1.4295 | 0.62355 | -0.24392 | -1.1226 | -2.1084 | -3.4537 | -4.8111 | -7.4692 | -14.0961 | -17.3105 | -18.0848
|  | FRATTON PARK | LW |  |  | 0.92878 | 0.27409 | -0.38507 | -1.6196 | -2.9085 | -4.2066 | -5.5909 | -7.0518 | -8.5901 | -10.1963 | -13.5853 | -20.3991 | -33.0759 | -40.3807 | 7.7336 | 7.4255 | 7.1192 | 6.5905 | 6.0127 | 5.3895 | 4.6855 | 3.9329 | 3.1291 | 2.2706 | 0.42003 | -6.6241 | -16.8027 | -22.6604 | 2.3066 | 1.7593 | 1.2062 | 0.13286 | -0.99405 | -2.1394 | -3.3804 | -4.6931 | -6.0773 | -7.5282 | -10.5966 | -17.5142 | -30.0047 | -37.1173
|  | FRATTON PARK | ST |  |  | 1.703 | 1.4984 | 1.2734 | 1.007 | 0.72843 | 0.4521 | 0.17419 | -0.12052 | -0.45601 | -0.83644 | -1.7544 | -5.5765 | -9.2917 | -12.3393 | 7.7402 | 7.3332 | 6.8671 | 6.264 | 5.6039 | 4.8706 | 4.0506 | 3.1575 | 2.1096 | 0.93022 | -1.9143 | -13.0424 | -31.5443 | -62.3897 | 2.997 | 2.8515 | 2.6862 | 2.4676 | 2.2434 | 2.0199 | 1.7858 | 1.5448 | 1.2633 | 0.94383 | 0.16184 | -3.3765 | -6.8205 | -9.4947
|  | FRATTON PARK | FS |  |  | 1.4662 | 1.1224 | 0.75139 | -0.13555 | -1.0699 | -2.0633 | -3.0586 | -4.1676 | -5.6798 | -7.2006 | -10.1852 | -17.5726 | -21.1783 | -22.0137 | 7.7068 | 7.219 | 6.6669 | 5.8489 | 4.9194 | 3.8823 | 2.6748 | 1.2964 | -0.31606 | -2.1395 | -6.5608 | -23.7327 | -56.7153 | -119.3222 | 3.0172 | 2.8823 | 2.745 | 2.4875 | 2.2051 | 1.9119 | 1.604 | 1.2623 | 0.82463 | 0.35948 | -0.65927 | -4.1395 | -8.4567 | -12.6643
COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD | MINIMUM HEADROOM | SP 50426 08256 | YES | 5.3152 | 4.9848 | 4.5442 | 3.9933 | 3.3395 | 2.6493 | 1.3918 | -0.26858 | -2.1818 | -4.2067 | -8.6265 | -22.7705 | -30.4933 | -30.0765 | 7.1466 | 6.761 | 6.3277 | 5.8366 | 5.3072 | 4.5308 | 3.6729 | 2.3823 | 0.82576 | -0.67118 | -3.4992 | -12.4373 | -21.7186 | -39.2736 | 5.1045 | 4.6109 | 4.1473 | 3.5815 | 2.8749 | 2.1355 | 0.9129 | -0.68771 | -2.5344 | -4.5136 | -8.8497 | -21.2657 | -28.7599 | -28.4844
|  | FRENCHAY ROAD | CT |  |  | 5.4412 | 5.2503 | 4.8916 | 4.417 | 3.9067 | 3.0463 | 2.106 | 0.63573 | -1.2099 | -2.9009 | -5.9646 | -13.3206 | -16.5312 | -17.8183 | 7.1466 | 6.761 | 6.3277 | 5.8366 | 5.3072 | 4.5308 | 3.6729 | 2.3823 | 0.82576 | -0.67118 | -3.4992 | -10.9921 | -17.0979 | -25.1803 | 5.1631 | 4.7612 | 4.3199 | 3.7934 | 3.2393 | 2.3891 | 1.4594 | -0.0057183 | -1.8208 | -3.5063 | -6.5578 | -13.8135 | -16.8881 | -18.1163
|  | FRENCHAY ROAD | LW |  |  | 5.3152 | 4.9848 | 4.5442 | 3.9933 | 3.3395 | 2.6493 | 1.3918 | -0.26858 | -2.1818 | -4.2067 | -8.6265 | -22.7705 | -30.4933 | -30.0765 | 7.2159 | 6.8552 | 6.5173 | 6.1337 | 5.6359 | 5.1092 | 4.1837 | 2.9591 | 1.5476 | -0.00029385 | -3.4053 | -12.4373 | -18.5376 | -18.3934 | 5.1045 | 4.6109 | 4.1473 | 3.5815 | 2.8749 | 2.1355 | 0.9129 | -0.68771 | -2.5344 | -4.5136 | -8.8497 | -21.2657 | -28.7599 | -28.4844
|  | FRENCHAY ROAD | ST |  |  | 5.5279 | 5.4281 | 5.3405 | 5.2772 | 5.1658 | 4.9242 | 4.5444 | 3.9194 | 3.1637 | 2.2995 | -0.084853 | -8.2527 | -13.8029 | -15.8383 | 7.3199 | 7.1004 | 6.8539 | 6.5854 | 6.2569 | 5.8372 | 5.3052 | 4.6262 | 3.8155 | 2.8703 | 0.34808 | -8.1756 | -16.2715 | -24.7602 | 5.4039 | 5.2268 | 5.0356 | 4.8392 | 4.5841 | 4.2359 | 3.7653 | 3.1231 | 2.3428 | 1.4288 | -1.0528 | -9.1816 | -14.7411 | -16.7775
|  | FRENCHAY ROAD | FS |  |  | 5.4412 | 5.2503 | 4.8916 | 4.417 | 3.9067 | 3.0463 | 2.106 | 0.63573 | -1.2099 | -2.9009 | -5.9646 | -13.3206 | -16.5312 | -17.8183 | 7.3019 | 7.0686 | 6.8043 | 6.4967 | 6.1259 | 5.674 | 5.1175 | 4.4211 | 3.5902 | 2.6423 | 0.19624 | -8.8092 | -21.7186 | -39.2736 | 5.395 | 5.2326 | 5.0569 | 4.8623 | 4.6184 | 4.3008 | 3.8388 | 3.1039 | 2.1508 | 1.0066 | -1.7369 | -7.4231 | -14.7277 | -19.4765
FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER | MINIMUM HEADROOM | SZ 34325 86965 | YES | 6.7757 | 6.3969 | 6.0153 | 5.4496 | 4.8125 | 4.1333 | 3.119 | 1.8807 | 0.40331 | -1.2549 | -4.8857 | -12.9463 | -15.8016 | -17.6272 | 8.0053 | 7.7654 | 7.5226 | 7.1961 | 6.799 | 6.3676 | 5.6671 | 4.7886 | 3.7386 | 2.5457 | -0.47919 | -6.9457 | -9.1006 | -10.9251 | 7.2699 | 6.9186 | 6.5644 | 6.0449 | 5.4447 | 4.8029 | 3.8283 | 2.6323 | 1.2022 | -0.40602 | -3.9302 | -12.2135 | -14.9985 | -16.8627
|  | FRESHWATER | CT |  |  | 6.9447 | 6.6989 | 6.4101 | 5.9495 | 5.496 | 4.8611 | 4.1804 | 3.2028 | 1.8548 | 0.53565 | -1.9414 | -8.1418 | -11.2567 | -12.6765 | 8.0502 | 7.8631 | 7.6406 | 7.3489 | 7.0492 | 6.6002 | 6.1109 | 5.3766 | 4.4336 | 3.5045 | 1.7709 | -2.4571 | -4.6056 | -6.0234 | 7.4152 | 7.1829 | 6.9081 | 6.4795 | 6.0492 | 5.4394 | 4.7841 | 3.8341 | 2.5371 | 1.264 | -1.122 | -7.0323 | -9.9616 | -11.3091
|  | FRESHWATER | LW |  |  | 6.7757 | 6.3969 | 6.0153 | 5.4496 | 4.8125 | 4.1333 | 3.119 | 1.8807 | 0.40331 | -1.2549 | -4.8857 | -12.9463 | -15.8016 | -17.6272 | 8.0053 | 7.7654 | 7.5226 | 7.1961 | 6.799 | 6.3676 | 5.6671 | 4.7886 | 3.7386 | 2.5457 | -0.47919 | -6.9457 | -9.1006 | -10.6849 | 7.2699 | 6.9186 | 6.5644 | 6.0449 | 5.4447 | 4.8029 | 3.8283 | 2.6323 | 1.2022 | -0.40602 | -3.9302 | -12.2135 | -14.9985 | -16.8627
|  | FRESHWATER | ST |  |  | 7.1163 | 7.0211 | 6.8989 | 6.737 | 6.5685 | 6.3394 | 6.0384 | 5.6469 | 5.1748 | 4.5959 | 3.0171 | -2.5003 | -6.8083 | -9.2281 | 8.1657 | 8.0893 | 7.9907 | 7.8635 | 7.7164 | 7.5201 | 7.2633 | 6.9329 | 6.5212 | 6.0189 | 4.6553 | 0.14255 | -3.3869 | -5.3744 | 7.5796 | 7.4939 | 7.3816 | 7.2306 | 7.0643 | 6.8385 | 6.5418 | 6.1558 | 5.6827 | 5.103 | 3.5225 | -2.0628 | -6.3763 | -8.5349
|  | FRESHWATER | FS |  |  | 6.9447 | 6.6989 | 6.4101 | 5.9495 | 5.496 | 4.8611 | 4.1804 | 3.2028 | 1.8548 | 0.53565 | -1.9414 | -8.1418 | -11.2567 | -12.6765 | 8.0983 | 7.9678 | 7.8049 | 7.6021 | 7.3713 | 7.0455 | 6.6535 | 6.1094 | 5.4465 | 4.7206 | 3.0013 | -2.2418 | -7.1746 | -10.9251 | 7.4992 | 7.3505 | 7.1645 | 6.9118 | 6.6289 | 6.2312 | 5.7558 | 5.0965 | 4.2817 | 3.3913 | 1.2971 | -5.0522 | -10.7567 | -14.4712
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY | MINIMUM HEADROOM | SU 87745 57942 | YES | 8.8405 | 8.5113 | 8.1348 | 7.3207 | 6.4334 | 5.4917 | 4.4001 | 3.2075 | 1.0117 | -2.2284 | -10.1028 | -25.9589 | -36.0678 | -41.4742 | 12.1828 | 12.0182 | 11.8131 | 11.418 | 10.9685 | 10.4752 | 9.866 | 9.1845 | 8.4476 | 6.3681 | 0.57062 | -11.0111 | -18.4183 | -22.5429 | 8.9073 | 8.6264 | 8.3051 | 7.6202 | 6.8674 | 6.0636 | 5.1162 | 4.078 | 2.8854 | 0.512 | -6.9775 | -22.034 | -31.6248 | -36.7797
|  | FRIMLEY | CT |  |  | 9.2547 | 9.1503 | 8.9581 | 8.4222 | 7.8503 | 7.1923 | 6.484 | 5.6398 | 4.2428 | 2.7408 | -2.3018 | -11.6496 | -15.1766 | -17.0785 | 12.2804 | 12.1485 | 11.9279 | 11.6018 | 11.2407 | 10.8034 | 10.3124 | 9.7158 | 8.89 | 8.0217 | 6.1913 | 0.4023 | -2.4948 | -6.9331 | 9.2199 | 9.1258 | 8.9569 | 8.5134 | 8.0277 | 7.4583 | 6.8389 | 6.0917 | 4.8844 | 3.6441 | 0.49562 | -8.2094 | -11.3963 | -13.1291
|  | FRIMLEY | LW |  |  | 8.8405 | 8.5113 | 8.1348 | 7.3207 | 6.4334 | 5.4917 | 4.4001 | 3.2075 | 1.0117 | -2.2284 | -10.1028 | -25.9589 | -36.0678 | -41.4742 | 12.1828 | 12.0182 | 11.8131 | 11.418 | 10.9685 | 10.4752 | 9.866 | 9.1845 | 8.4476 | 6.3681 | 0.57062 | -11.0111 | -18.4183 | -22.5429 | 8.9073 | 8.6264 | 8.3051 | 7.6202 | 6.8674 | 6.0636 | 5.1162 | 4.078 | 2.8854 | 0.512 | -6.9775 | -22.034 | -31.6248 | -36.7797
|  | FRIMLEY | ST |  |  | 9.3751 | 9.3543 | 9.2554 | 9.1136 | 8.9728 | 8.8128 | 8.6213 | 8.4164 | 8.2407 | 8.0275 | 7.4613 | 4.5251 | 1.2861 | -2.3687 | 12.3523 | 12.2758 | 12.1174 | 11.9385 | 11.7555 | 11.5491 | 11.3013 | 11.0416 | 10.796 | 10.5061 | 9.7657 | 6.7743 | 3.182 | -1.8501 | 9.3194 | 9.298 | 9.2107 | 9.0771 | 8.9462 | 8.7976 | 8.6136 | 8.4214 | 8.2522 | 8.0447 | 7.4855 | 4.7688 | 1.9736 | -0.99214
|  | FRIMLEY | FS |  |  | 9.2547 | 9.1503 | 8.9581 | 8.4222 | 7.8503 | 7.1923 | 6.484 | 5.6398 | 4.2428 | 2.7408 | -2.3018 | -11.6496 | -15.1766 | -17.0785 | 12.2427 | 12.0713 | 11.8488 | 11.5725 | 11.2324 | 10.8391 | 10.3069 | 9.6331 | 8.8388 | 7.9084 | 5.571 | -1.9589 | -10.0318 | -18.8283 | 9.1732 | 9.0372 | 8.86 | 8.5861 | 8.24 | 7.8369 | 7.2614 | 6.5422 | 5.6883 | 4.6938 | 2.2172 | -5.9964 | -17.0232 | -22.0944
MELKSHAM GSP | FROME BSP | FROME | MINIMUM HEADROOM | ST 78850 48051 | YES | 26.482 | 25.0199 | 23.3433 | 21.264 | 19.002 | 16.766 | 13.7446 | 10.3584 | 6.5512 | 2.5321 | -6.1203 | -22.3531 | -29.3758 | -34.5009 | 30.6064 | 29.7378 | 28.7045 | 27.5272 | 26.2348 | 24.9167 | 22.8652 | 20.3977 | 17.6919 | 14.8451 | 8.6559 | -3.3103 | -11.8491 | -23.585 | 25.426 | 24.1728 | 22.7268 | 20.9264 | 18.9591 | 16.9786 | 14.1664 | 10.7655 | 6.961 | 2.9711 | -5.6362 | -21.3555 | -28.4321 | -33.1736
|  | FROME | CT |  |  | 27.0771 | 26.0606 | 24.6825 | 22.9425 | 21.1944 | 19.0353 | 16.6476 | 13.6156 | 9.6007 | 5.6659 | -1.7612 | -19.2018 | -29.3758 | -34.5009 | 30.7897 | 30.0792 | 29.0691 | 28.0029 | 26.9403 | 25.3751 | 23.5169 | 21.1105 | 18.1534 | 15.269 | 9.8554 | -3.3103 | -11.8491 | -19.3434 | 25.9804 | 25.1224 | 23.9337 | 22.4558 | 20.961 | 18.8769 | 16.4774 | 13.3689 | 9.3463 | 5.4502 | -1.8408 | -18.9649 | -28.4321 | -33.1736
|  | FROME | LW |  |  | 26.482 | 25.0199 | 23.3433 | 21.264 | 19.002 | 16.766 | 13.7446 | 10.3584 | 6.5512 | 2.5321 | -6.1203 | -22.3531 | -29.2197 | -30.1301 | 30.6064 | 29.7378 | 28.7045 | 27.5272 | 26.2348 | 24.9167 | 22.8652 | 20.3977 | 17.6919 | 14.8451 | 8.6559 | -2.3689 | -6.8235 | -7.242 | 25.426 | 24.1728 | 22.7268 | 20.9264 | 18.9591 | 16.9786 | 14.1664 | 10.7655 | 6.961 | 2.9711 | -5.6362 | -21.3555 | -27.7555 | -28.2677
|  | FROME | ST |  |  | 27.5587 | 26.9156 | 25.9583 | 24.8346 | 23.7961 | 22.656 | 21.2395 | 19.7621 | 18.0946 | 16.284 | 11.784 | -2.9799 | -14.8791 | -21.8513 | 31.0675 | 30.5909 | 29.8435 | 28.9777 | 28.2083 | 27.3024 | 26.0868 | 24.8621 | 23.3027 | 21.651 | 17.4683 | 4.2619 | -7.0211 | -15.9455 | 26.4104 | 25.8797 | 25.0596 | 24.0793 | 23.1959 | 22.197 | 20.8358 | 19.2776 | 17.4752 | 15.5512 | 10.6572 | -4.7783 | -16.5383 | -23.2099
|  | FROME | FS |  |  | 27.0771 | 26.0606 | 24.6825 | 22.9425 | 21.1944 | 19.0353 | 16.6476 | 13.6156 | 9.6007 | 5.6659 | -1.7612 | -19.2018 | -29.3758 | -34.5009 | 31.1636 | 30.7229 | 30.1236 | 29.4267 | 28.7033 | 27.8987 | 26.9501 | 25.8528 | 24.5395 | 23.0716 | 19.318 | 7.0796 | -7.6877 | -23.585 | 26.5386 | 26.0843 | 25.4622 | 24.6618 | 23.8405 | 22.9433 | 21.8991 | 20.6855 | 19.1098 | 17.4034 | 13.2306 | -0.13002 | -13.7748 | -23.3585
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE | MINIMUM HEADROOM | SU 84935 93873 | YES | 6.3216 | 5.7914 | 5.4638 | 4.8462 | 4.1926 | 3.5164 | 2.7164 | 1.8377 | 0.75341 | -0.4063 | -2.8883 | -9.5013 | -11.6218 | -12.6417 | 8.7428 | 8.4824 | 8.3084 | 7.9835 | 7.6294 | 7.1973 | 6.7214 | 6.1573 | 5.3824 | 4.594 | 2.0151 | -2.5354 | -13.6582 | -33.4768 | 5.2687 | 4.8572 | 4.5937 | 4.0621 | 3.4584 | 2.8302 | 2.088 | 1.2719 | 0.26802 | -0.80888 | -3.3978 | -9.7348 | -11.6849 | -12.639
|  | FRYERS LANE | CT |  |  | 6.6924 | 6.3953 | 6.2668 | 5.8483 | 5.4111 | 4.9056 | 4.3641 | 3.7619 | 2.7104 | 1.6809 | -0.33569 | -5.7306 | -9.1104 | -10.6335 | 8.7756 | 8.5101 | 8.3084 | 7.9835 | 7.6294 | 7.1973 | 6.7214 | 6.1573 | 5.3824 | 4.594 | 2.9511 | -2.2156 | -8.5008 | -17.8643 | 5.5335 | 5.2932 | 5.1707 | 4.8347 | 4.4816 | 4.0562 | 3.5982 | 3.0535 | 2.1112 | 1.1906 | -0.61425 | -5.5019 | -8.563 | -9.933
|  | FRYERS LANE | LW |  |  | 6.3216 | 5.7914 | 5.4638 | 4.8462 | 4.1926 | 3.5164 | 2.7164 | 1.8377 | 0.75341 | -0.4063 | -2.8883 | -9.5013 | -11.6218 | -12.6417 | 8.7428 | 8.4824 | 8.3248 | 8.0556 | 7.7545 | 7.4334 | 7.0077 | 6.5181 | 5.9386 | 4.875 | 2.0151 | -2.5354 | -3.7866 | -4.4938 | 5.2687 | 4.8572 | 4.5937 | 4.0621 | 3.4584 | 2.8302 | 2.088 | 1.2719 | 0.26802 | -0.80888 | -3.3978 | -9.7348 | -11.6849 | -12.639
|  | FRYERS LANE | ST |  |  | 6.865 | 6.6677 | 6.6408 | 6.5886 | 6.516 | 6.4141 | 6.2695 | 6.1164 | 5.9352 | 5.7126 | 5.1038 | 2.3597 | -0.25142 | -2.9038 | 8.8557 | 8.6459 | 8.5044 | 8.3211 | 8.1081 | 7.8527 | 7.5453 | 7.2059 | 6.8137 | 6.3582 | 5.2091 | 0.72807 | -5.5868 | -15.4214 | 5.6717 | 5.5187 | 5.4907 | 5.4356 | 5.3622 | 5.2617 | 5.1205 | 4.9661 | 4.7852 | 4.5614 | 3.9508 | 1.351 | -0.98101 | -3.1953
|  | FRYERS LANE | FS |  |  | 6.6924 | 6.3953 | 6.2668 | 5.8483 | 5.4111 | 4.9056 | 4.3641 | 3.7619 | 2.7104 | 1.6809 | -0.33569 | -5.7306 | -9.1104 | -10.6335 | 8.844 | 8.6194 | 8.4437 | 8.1965 | 7.912 | 7.5869 | 7.2081 | 6.7766 | 6.2312 | 5.6097 | 4.0548 | -2.3006 | -13.6582 | -33.4768 | 5.6711 | 5.5355 | 5.4983 | 5.4089 | 5.3069 | 5.1875 | 5.0522 | 4.8963 | 4.662 | 4.4055 | 3.7629 | 1.0293 | -2.8734 | -6.2267
COWLEY GSP | DRAYTON BSP | FULSCOT | MINIMUM HEADROOM | SU 54413 89511 | NO | 5.9213 | 5.0388 | 4.1436 | 3.0272 | 1.6571 | 0.17471 | -1.5307 | -3.2029 | -4.9905 | -6.842 | -10.1643 | -16.7035 | -23.2319 | -25.8013 | 10.1426 | 9.6552 | 9.1668 | 8.5914 | 7.8766 | 7.1077 | 6.1411 | 5.1174 | 4.0291 | 2.8624 | 0.61682 | -4.8245 | -11.0069 | -12.8751 | 5.3949 | 4.6939 | 3.9803 | 3.0554 | 1.9209 | 0.68441 | -0.76119 | -2.2646 | -3.8807 | -5.5696 | -8.7814 | -14.9666 | -21.867 | -24.2756
|  | FULSCOT | CT |  |  | 6.2464 | 5.6185 | 4.9183 | 4.0123 | 2.9145 | 1.5691 | 0.20246 | -1.2819 | -3.2403 | -5.1707 | -8.2128 | -15.0154 | -18.8644 | -20.731 | 10.2199 | 9.8052 | 9.3488 | 8.8235 | 8.2014 | 7.4022 | 6.5756 | 5.5868 | 4.3795 | 3.1901 | 1.2012 | -3.5035 | -6.6178 | -9.5266 | 5.6734 | 5.1836 | 4.6495 | 3.9159 | 3.0253 | 1.9014 | 0.71767 | -0.64718 | -2.4203 | -4.1641 | -6.9753 | -13.3048 | -16.756 | -18.3679
|  | FULSCOT | LW |  |  | 5.9213 | 5.0388 | 4.1436 | 3.0272 | 1.6571 | 0.17471 | -1.5307 | -3.2029 | -4.9905 | -6.842 | -10.1643 | -16.7035 | -23.2319 | -25.8013 | 10.1426 | 9.6552 | 9.1668 | 8.5914 | 7.8766 | 7.1077 | 6.1411 | 5.1174 | 4.0291 | 2.8624 | 0.61682 | -4.8245 | -11.0069 | -12.8751 | 5.3949 | 4.6939 | 3.9803 | 3.0554 | 1.9209 | 0.68441 | -0.76119 | -2.2646 | -3.8807 | -5.5696 | -8.7814 | -14.9666 | -21.867 | -24.2756
|  | FULSCOT | ST |  |  | 6.4951 | 6.038 | 5.5373 | 5.048 | 4.442 | 3.7607 | 3.0781 | 2.3988 | 1.6616 | 0.81291 | -0.86481 | -6.1529 | -10.3494 | -13.1043 | 10.3559 | 10.0578 | 9.7295 | 9.4014 | 8.9979 | 8.5314 | 8.0317 | 7.5214 | 6.9671 | 6.3173 | 4.8802 | 0.28527 | -3.6289 | -6.9476 | 5.9014 | 5.5716 | 5.2044 | 4.8441 | 4.3985 | 3.893 | 3.3285 | 2.7321 | 2.0846 | 1.3273 | -0.27492 | -5.3977 | -9.3377 | -11.7513
|  | FULSCOT | FS |  |  | 6.2464 | 5.6185 | 4.9183 | 4.0123 | 2.9145 | 1.5691 | 0.20246 | -1.2819 | -3.2403 | -5.1707 | -8.2128 | -15.0154 | -18.8644 | -20.731 | 10.3748 | 10.0853 | 9.7697 | 9.4425 | 9.0541 | 8.6154 | 8.1478 | 7.6734 | 7.1355 | 6.5423 | 5.2247 | 0.43601 | -5.4196 | -11.7789 | 5.9272 | 5.6282 | 5.3062 | 4.9325 | 4.4897 | 3.9961 | 3.4807 | 2.9541 | 2.3358 | 1.6656 | 0.24868 | -4.8014 | -10.0639 | -13.7194
COWLEY GSP | WITNEY BSP | FYFIELD | MINIMUM HEADROOM | SU 42256 99551 | NO | 4.0127 | 3.402 | 2.7182 | 1.9383 | 0.94568 | -0.13663 | -1.8036 | -3.7292 | -5.7862 | -8.1227 | -13.2711 | -23.1464 | -26.6006 | -29.0906 | 6.7138 | 6.3188 | 5.8865 | 5.3818 | 4.7164 | 3.9868 | 2.7949 | 1.3653 | -0.20221 | -1.9905 | -5.9382 | -14.6539 | -17.4825 | -19.7492 | 4.0488 | 3.5114 | 2.9176 | 2.2299 | 1.3503 | 0.38124 | -1.1075 | -2.9141 | -4.9322 | -7.2242 | -12.9423 | -24.0145 | -27.4603 | -30.0558
|  | FYFIELD | CT |  |  | 4.1277 | 3.6577 | 3.0485 | 2.3222 | 1.5218 | 0.3916 | -0.85836 | -2.5322 | -4.4854 | -6.4251 | -9.9955 | -18.1686 | -21.8234 | -23.38 | 6.7227 | 6.3854 | 5.9561 | 5.4558 | 4.8982 | 4.0803 | 3.1649 | 1.8916 | 0.40638 | -1.0867 | -3.8384 | -10.2578 | -13.2602 | -15.0708 | 4.1649 | 3.7588 | 3.2398 | 2.6102 | 1.911 | 0.9227 | -0.22753 | -1.8762 | -3.8122 | -5.7404 | -9.2834 | -17.4204 | -20.9844 | -22.5306
|  | FYFIELD | LW |  |  | 4.0127 | 3.402 | 2.7182 | 1.9383 | 0.94568 | -0.13663 | -1.8036 | -3.7292 | -5.7862 | -8.1227 | -13.2711 | -23.1464 | -26.6006 | -29.0906 | 6.7138 | 6.3188 | 5.8865 | 5.3818 | 4.7164 | 3.9868 | 2.7949 | 1.3653 | -0.20221 | -1.9905 | -5.9382 | -14.6539 | -17.4825 | -19.7492 | 4.0488 | 3.5114 | 2.9176 | 2.2299 | 1.3503 | 0.38124 | -1.1075 | -2.9141 | -4.9322 | -7.2242 | -12.9423 | -24.0145 | -27.4603 | -30.0558
|  | FYFIELD | ST |  |  | 4.3997 | 4.177 | 3.8457 | 3.3545 | 2.8143 | 2.1899 | 1.4184 | 0.59559 | -0.3123 | -1.4072 | -4.2853 | -13.4326 | -19.8456 | -22.1123 | 6.9143 | 6.7621 | 6.5417 | 6.1677 | 5.7665 | 5.2965 | 4.6962 | 4.0555 | 3.315 | 2.4292 | 0.078119 | -7.4052 | -12.8099 | -15.2128 | 4.4075 | 4.2197 | 3.9456 | 3.4991 | 3.02 | 2.471 | 1.784 | 1.0629 | 0.21075 | -0.89702 | -3.8316 | -13.1847 | -19.6618 | -21.9987
|  | FYFIELD | FS |  |  | 4.1277 | 3.6577 | 3.0485 | 2.3222 | 1.5218 | 0.3916 | -0.85836 | -2.5322 | -4.4854 | -6.4251 | -9.9955 | -18.1686 | -21.8234 | -23.38 | 6.9273 | 6.7916 | 6.5983 | 6.3399 | 6.0366 | 5.6723 | 5.2346 | 4.7468 | 4.2279 | 3.6244 | 2.0192 | -3.7894 | -10.2573 | -14.6088 | 4.4419 | 4.2901 | 4.0677 | 3.7463 | 3.3803 | 2.9474 | 2.439 | 1.8867 | 1.2943 | 0.58848 | -1.4264 | -8.7406 | -16.8265 | -21.6803
LOVEDEAN GSP | HAVANT | GABLE HEAD | MINIMUM HEADROOM | SZ 72204 99904 | YES | 16.3167 | 15.9237 | 15.4492 | 14.664 | 13.7573 | 12.958 | 11.9541 | 10.8367 | 9.487 | 8.0525 | 5.0238 | -0.96684 | -4.6313 | -6.642 | 18.1432 | 17.9249 | 17.669 | 17.2962 | 16.8434 | 16.438 | 15.8548 | 15.1714 | 14.3536 | 13.4629 | 11.5566 | 7.5431 | 4.6948 | 0.079457 | 15.0543 | 14.714 | 14.3173 | 13.6396 | 12.8604 | 12.1567 | 11.2764 | 10.2966 | 9.0982 | 7.8258 | 5.0563 | -0.47499 | -3.838 | -5.5914
|  | GABLE HEAD | CT |  |  | 16.623 | 16.413 | 16.0993 | 15.484 | 14.7876 | 14.094 | 13.3425 | 12.3833 | 10.92 | 9.4538 | 6.629 | -0.34937 | -4.4797 | -6.642 | 18.2153 | 18.0461 | 17.8127 | 17.4657 | 17.0738 | 16.63 | 16.1442 | 15.4774 | 14.57 | 13.6567 | 11.9053 | 7.5431 | 4.6948 | 2.2742 | 15.3356 | 15.1621 | 14.9108 | 14.3868 | 13.7948 | 13.1913 | 12.5379 | 11.7059 | 10.4137 | 9.0625 | 6.4365 | -0.0026442 | -3.6743 | -5.5914
|  | GABLE HEAD | LW |  |  | 16.3167 | 15.9237 | 15.4492 | 14.664 | 13.7573 | 12.958 | 11.9541 | 10.8367 | 9.487 | 8.0525 | 5.0238 | -0.96684 | -4.6313 | -5.8606 | 18.1432 | 17.9249 | 17.669 | 17.2962 | 16.8434 | 16.438 | 15.8548 | 15.1714 | 14.3536 | 13.4629 | 11.5566 | 7.9712 | 5.8872 | 2.9448 | 15.0543 | 14.714 | 14.3173 | 13.6396 | 12.8604 | 12.1567 | 11.2764 | 10.2966 | 9.0982 | 7.8258 | 5.0563 | -0.47499 | -3.838 | -5.0859
|  | GABLE HEAD | ST |  |  | 16.8333 | 16.764 | 16.6098 | 16.408 | 16.1538 | 15.9577 | 15.7107 | 15.4067 | 14.9788 | 14.4683 | 13.1516 | 8.471 | 4.3894 | 1.1657 | 18.3295 | 18.2528 | 18.1239 | 17.966 | 17.7678 | 17.5809 | 17.3465 | 17.0582 | 16.6939 | 16.2628 | 15.1463 | 11.367 | 7.8696 | 4.8088 | 15.5264 | 15.4787 | 15.3696 | 15.2212 | 15.0322 | 14.8782 | 14.6824 | 14.439 | 14.1151 | 13.6721 | 12.4194 | 7.9648 | 4.0358 | 1.0093
|  | GABLE HEAD | FS |  |  | 16.623 | 16.413 | 16.0993 | 15.484 | 14.7876 | 14.094 | 13.3425 | 12.3833 | 10.92 | 9.4538 | 6.629 | -0.34937 | -4.4797 | -6.642 | 18.2715 | 18.1536 | 17.981 | 17.768 | 17.5177 | 17.2385 | 16.9156 | 16.4904 | 15.9586 | 15.396 | 14.1103 | 9.8772 | 5.1049 | 0.079457 | 15.4603 | 15.3792 | 15.2396 | 15.0188 | 14.7658 | 14.5012 | 14.1996 | 13.7925 | 13.159 | 12.499 | 11.0182 | 6.1913 | 1.333 | -2.3754
LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD | MINIMUM HEADROOM | SU 64771 01769 | YES | 9.2252 | 8.6595 | 7.9568 | 6.6734 | 5.3343 | 3.9389 | 2.3891 | 0.69116 | -0.9822 | -2.6867 | -6.1702 | -11.7288 | -14.9436 | -15.5248 | 12.8878 | 12.3675 | 11.727 | 10.738 | 9.7059 | 8.5313 | 7.1651 | 5.5699 | 3.7893 | 1.7632 | -3.2143 | -22.0224 | -56.0234 | -118.0088 | 9.14 | 8.6568 | 8.069 | 6.9682 | 5.8078 | 4.5856 | 3.2154 | 1.7257 | 0.25953 | -1.2373 | -4.2941 | -9.2694 | -14.6112 | -21.9573
|  | GAMBLE ROAD | CT |  |  | 9.6749 | 9.3452 | 8.8798 | 7.855 | 6.809 | 5.6687 | 4.4736 | 3.0442 | 1.2755 | -0.54684 | -4.1935 | -11.7288 | -14.9436 | -15.5248 | 12.8878 | 12.3675 | 11.727 | 10.738 | 9.7059 | 8.5313 | 7.2451 | 5.7464 | 4.0023 | 2.1293 | -1.9497 | -14.3136 | -31.9228 | -61.1267 | 9.5176 | 9.2322 | 8.8404 | 7.9459 | 7.0549 | 6.0699 | 5.0311 | 3.7832 | 2.2409 | 0.6519 | -2.5379 | -9.2694 | -12.1693 | -12.7536
|  | GAMBLE ROAD | LW |  |  | 9.2252 | 8.6595 | 7.9568 | 6.6734 | 5.3343 | 3.9389 | 2.3891 | 0.69116 | -0.9822 | -2.6867 | -6.1702 | -11.268 | -12.5041 | -13.261 | 13.0158 | 12.7115 | 12.3404 | 11.6983 | 11.0281 | 10.3075 | 9.4607 | 8.5453 | 7.6333 | 6.6934 | 4.7583 | 1.9772 | 1.0794 | 0.47987 | 9.14 | 8.6568 | 8.069 | 6.9682 | 5.8078 | 4.5856 | 3.2154 | 1.7257 | 0.25953 | -1.2373 | -4.2941 | -8.8688 | -10.0593 | -10.8322
|  | GAMBLE ROAD | ST |  |  | 9.8675 | 9.6651 | 9.3339 | 8.8976 | 8.4927 | 8.0697 | 7.6165 | 7.0895 | 6.5058 | 5.8683 | 4.4033 | 0.42592 | -2.883 | -5.5548 | 12.9782 | 12.5285 | 11.9638 | 11.1839 | 10.3916 | 9.5135 | 8.5308 | 7.4459 | 6.2296 | 4.8818 | 1.6959 | -9.4738 | -27.471 | -57.5636 | 9.6913 | 9.5233 | 9.2557 | 8.8615 | 8.5142 | 8.1504 | 7.7518 | 7.304 | 6.803 | 6.2541 | 4.9784 | 1.3163 | -1.7849 | -4.2616
|  | GAMBLE ROAD | FS |  |  | 9.6749 | 9.3452 | 8.8798 | 7.855 | 6.809 | 5.6687 | 4.4736 | 3.0442 | 1.2755 | -0.54684 | -4.1935 | -11.7288 | -14.9436 | -15.5248 | 12.9324 | 12.4295 | 11.806 | 10.8471 | 9.7728 | 8.5636 | 7.1651 | 5.5699 | 3.7893 | 1.7632 | -3.2143 | -22.0224 | -56.0234 | -118.0088 | 9.6734 | 9.5339 | 9.319 | 8.9576 | 8.5742 | 8.1481 | 7.6718 | 7.1123 | 6.4369 | 5.6871 | 3.8863 | -2.9158 | -14.6112 | -21.9573
IVER 132KV | DENHAM | GERRARDS CROSS | MINIMUM HEADROOM | SU 99973 87964 | YES | -0.44666 | -1.5479 | -2.6832 | -4.314 | -6.1291 | -8.9763 | -12.094 | -16.769 | -22.332 | -27.7734 | -40.1998 | -60.6022 | -69.1685 | -71.9803 | 1.9093 | 1.0514 | 0.0041601 | -1.3364 | -2.8316 | -5.2081 | -7.7267 | -11.5471 | -16.0094 | -20.323 | -29.5256 | -46.3236 | -53.4346 | -64.4267 | -0.92241 | -1.9826 | -3.1627 | -4.812 | -6.6475 | -9.5397 | -12.633 | -17.3763 | -22.95 | -28.3524 | -40.6422 | -60.801 | -69.1999 | -79.1986
|  | GERRARDS CROSS | CT |  |  | -0.44666 | -1.447 | -2.6832 | -4.314 | -6.1291 | -8.9763 | -12.0105 | -16.6907 | -22.332 | -27.7734 | -37.7687 | -60.6022 | -69.1685 | -71.9803 | 1.9093 | 1.0514 | 0.0041601 | -1.3364 | -2.8316 | -5.2081 | -7.7267 | -11.5471 | -16.0094 | -20.323 | -28.2334 | -46.3236 | -53.4346 | -56.7209 | -0.92241 | -1.9341 | -3.1627 | -4.812 | -6.6475 | -9.5397 | -12.633 | -17.352 | -22.95 | -28.3524 | -38.254 | -60.801 | -69.1999 | -71.949
|  | GERRARDS CROSS | LW |  |  | -0.40915 | -1.5479 | -2.6472 | -4.1123 | -6.1187 | -8.2956 | -12.094 | -16.769 | -21.9481 | -27.7246 | -40.1998 | -59.693 | -63.3029 | -57.2221 | 2.0563 | 1.1601 | 0.27716 | -0.85745 | -2.4404 | -4.1871 | -7.2824 | -11.09 | -15.1601 | -19.7071 | -29.5256 | -44.6858 | -47.3301 | -42.4399 | -0.84047 | -1.9826 | -3.0866 | -4.5534 | -6.5632 | -8.7745 | -12.6053 | -17.3763 | -22.5246 | -28.2635 | -40.6422 | -59.9148 | -63.4532 | -57.4228
|  | GERRARDS CROSS | ST |  |  | 0.21442 | -0.10989 | -0.54702 | -1.3256 | -2.3441 | -3.7101 | -5.3703 | -7.4331 | -9.7226 | -12.6456 | -20.7409 | -47.0095 | -64.019 | -68.4979 | 2.4448 | 2.1512 | 1.7579 | 1.0302 | 0.11598 | -1.1117 | -2.5756 | -4.366 | -6.326 | -8.7687 | -15.4185 | -36.8279 | -50.9422 | -55.361 | -0.25032 | -0.5813 | -1.029 | -1.8705 | -2.9356 | -4.3747 | -6.083 | -8.1847 | -10.5168 | -13.4786 | -21.5676 | -47.7046 | -64.5968 | -68.9682
|  | GERRARDS CROSS | FS |  |  | -0.44666 | -1.447 | -2.6832 | -4.314 | -6.1291 | -8.9763 | -12.0105 | -16.6907 | -22.332 | -27.7734 | -37.7687 | -60.6022 | -69.1685 | -71.9803 | 2.3884 | 2.0591 | 1.6432 | 1.0576 | 0.29576 | -0.70956 | -1.9679 | -3.5535 | -5.3035 | -7.3324 | -12.7084 | -31.9853 | -52.4297 | -64.4267 | -0.31444 | -0.67884 | -1.1417 | -1.8305 | -2.7195 | -3.8986 | -5.375 | -7.2387 | -9.3281 | -11.767 | -18.2879 | -41.6416 | -66.1198 | -79.1986
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM | MINIMUM HEADROOM | ST 80185 25765 | YES | 22.2687 | 21.8626 | 21.5168 | 21.0642 | 20.4122 | 19.552 | 18.7583 | 17.9953 | 17.0781 | 16.0594 | 14.2468 | 10.0027 | 7.5183 | 7.2921 | 21.5344 | 21.1287 | 20.8396 | 20.5744 | 20.3382 | 19.8061 | 19.3547 | 18.8344 | 18.2088 | 17.5103 | 16.0644 | 12.4616 | 10.7831 | 10.7362 | 20.9704 | 20.5245 | 20.1561 | 19.665 | 19.1342 | 18.3672 | 17.6935 | 17.0526 | 16.2799 | 15.4314 | 13.8981 | 9.3385 | 7.0154 | 6.8328
|  | GILLINGHAM | CT |  |  | 22.3051 | 21.8969 | 21.7934 | 21.5888 | 21.2489 | 20.3632 | 19.7927 | 19.1393 | 18.134 | 17.0095 | 15.0014 | 10.0027 | 7.5183 | 7.2921 | 21.587 | 21.1984 | 21.1301 | 21.0162 | 20.8791 | 20.1839 | 19.9755 | 19.571 | 18.9155 | 18.1663 | 16.617 | 12.4616 | 10.7831 | 10.7362 | 21.1071 | 20.7136 | 20.5876 | 20.2844 | 19.9126 | 19.0881 | 18.6167 | 18.07 | 17.2119 | 16.2569 | 14.5396 | 9.3385 | 7.0154 | 6.8328
|  | GILLINGHAM | LW |  |  | 22.2687 | 21.8626 | 21.5168 | 21.0642 | 20.4122 | 19.552 | 18.7583 | 17.9953 | 17.0781 | 16.0594 | 14.2468 | 10.3248 | 9.3569 | 9.0306 | 21.5344 | 21.1287 | 20.8396 | 20.5744 | 20.3382 | 19.8061 | 19.3547 | 18.8344 | 18.2088 | 17.5103 | 16.0644 | 13.1797 | 12.6218 | 12.2809 | 20.9704 | 20.5245 | 20.1561 | 19.665 | 19.1342 | 18.3672 | 17.6935 | 17.0526 | 16.2799 | 15.4314 | 13.8981 | 10.1431 | 9.3015 | 8.8351
|  | GILLINGHAM | ST |  |  | 22.3361 | 21.952 | 21.8747 | 21.7343 | 21.5648 | 20.9767 | 20.7418 | 20.3962 | 19.8875 | 19.281 | 18.1307 | 15.8188 | 14.7068 | 13.6938 | 21.6143 | 21.2462 | 21.1995 | 21.1173 | 21.0175 | 20.3778 | 20.2318 | 20.0758 | 19.7939 | 19.4734 | 18.7847 | 17.0783 | 16.2295 | 15.3914 | 21.1623 | 20.8085 | 20.7178 | 20.5467 | 20.34 | 19.7216 | 19.4741 | 19.2067 | 18.7959 | 18.3004 | 17.3708 | 15.3848 | 14.4229 | 13.5273
|  | GILLINGHAM | FS |  |  | 22.3051 | 21.8969 | 21.7934 | 21.5888 | 21.2489 | 20.3632 | 19.7927 | 19.1393 | 18.134 | 17.0095 | 15.0014 | 10.0027 | 7.5183 | 7.2921 | 21.8072 | 21.5437 | 21.3645 | 21.204 | 21.0567 | 20.7192 | 20.5004 | 20.2632 | 20.0295 | 19.7721 | 19.1543 | 17.0354 | 15.058 | 13.1839 | 21.3192 | 21.072 | 20.8816 | 20.6598 | 20.4282 | 20.0542 | 19.7616 | 19.4465 | 19.095 | 18.7012 | 17.8612 | 15.4545 | 13.4091 | 11.8408
BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING | MINIMUM HEADROOM | SU 96743 44375 | YES | 9.4911 | 9.0468 | 8.6059 | 7.9162 | 7.1237 | 6.2921 | 5.2125 | 4.003 | 2.5465 | -0.21663 | -7.7569 | -21.5199 | -26.2461 | -29.0911 | 13.6321 | 13.3976 | 13.1675 | 12.8238 | 12.4116 | 11.8495 | 11.1978 | 10.3072 | 9.1188 | 7.4694 | 1.9742 | -7.6077 | -10.4296 | -12.2831 | 8.8157 | 8.4221 | 8.0306 | 7.3747 | 6.6344 | 5.8542 | 4.8734 | 3.7501 | 2.3944 | -0.57306 | -7.7305 | -20.7026 | -25.051 | -27.6875
|  | GODALMING | CT |  |  | 9.8159 | 9.5527 | 9.2501 | 8.6926 | 8.0617 | 7.2499 | 6.349 | 5.1691 | 3.0829 | -0.21663 | -7.7569 | -21.5199 | -26.2461 | -29.0911 | 13.6698 | 13.4449 | 13.1801 | 12.8238 | 12.4116 | 11.8495 | 11.1978 | 10.3072 | 9.1188 | 7.4694 | 1.9742 | -7.6077 | -10.4296 | -12.2831 | 9.1171 | 8.8739 | 8.5918 | 8.0745 | 7.4897 | 6.7273 | 5.8765 | 4.7514 | 2.5535 | -0.57306 | -7.7305 | -20.7026 | -25.051 | -27.6875
|  | GODALMING | LW |  |  | 9.4911 | 9.0468 | 8.6059 | 7.9162 | 7.1237 | 6.2921 | 5.2125 | 4.003 | 2.5465 | 0.98286 | -2.3108 | -8.6127 | -11.5838 | -11.9111 | 13.6321 | 13.3976 | 13.1675 | 12.8322 | 12.4212 | 11.9635 | 11.3047 | 10.5442 | 9.681 | 8.7342 | 6.7037 | 3.0489 | 1.5828 | 1.7569 | 8.8157 | 8.4221 | 8.0306 | 7.3747 | 6.6344 | 5.8542 | 4.8734 | 3.7501 | 2.3944 | 0.93413 | -2.1531 | -7.9936 | -10.6612 | -10.8524
|  | GODALMING | ST |  |  | 10.0288 | 9.9358 | 9.8118 | 9.6715 | 9.4752 | 9.227 | 8.8997 | 8.5118 | 8.05 | 7.4746 | 5.9389 | 0.55431 | -3.8213 | -7.3182 | 13.7912 | 13.6744 | 13.5281 | 13.3466 | 13.1255 | 12.8543 | 12.5075 | 12.1069 | 11.6595 | 11.1109 | 9.6633 | 4.9003 | 0.76003 | -3.3246 | 9.3158 | 9.234 | 9.1225 | 8.9761 | 8.7815 | 8.5364 | 8.2113 | 7.8281 | 7.3781 | 6.8166 | 5.3103 | 0.13686 | -3.9604 | -7.0452
|  | GODALMING | FS |  |  | 9.8159 | 9.5527 | 9.2501 | 8.6926 | 8.0617 | 7.2499 | 6.349 | 5.1691 | 3.0829 | -0.21663 | -7.7569 | -21.5199 | -26.2461 | -29.0911 | 13.7853 | 13.6613 | 13.5105 | 13.3552 | 13.1617 | 12.9302 | 12.647 | 12.3085 | 11.8971 | 11.4135 | 10.1478 | 5.3276 | -0.65579 | -7.4406 | 9.3137 | 9.2377 | 9.1392 | 8.997 | 8.8129 | 8.5966 | 8.3304 | 8.0063 | 7.5657 | 7.0555 | 5.7422 | 0.75115 | -4.5841 | -8.4877
WILLESDEN GSP | ACTON LANE | GOLDSMITHS | MINIMUM HEADROOM | TQ 21089 80758 | YES | 11.9025 | 11.9025 | 11.9025 | 11.8722 | 11.8471 | 11.8077 | 11.7649 | 11.729 | 11.7211 | 11.7129 | 11.6985 | 11.6585 | 11.6502 | 11.6502 | 11.04 | 11.04 | 11.04 | 11.0022 | 10.9707 | 10.9215 | 10.868 | 10.8231 | 10.8132 | 10.803 | 10.785 | 10.7349 | 10.7246 | 10.7246 | 11.04 | 11.04 | 11.04 | 11.0022 | 10.9707 | 10.9215 | 10.868 | 10.8231 | 10.8132 | 10.803 | 10.785 | 10.7349 | 10.7246 | 10.7246
|  | GOLDSMITHS | CT |  |  | 11.9025 | 11.9025 | 11.9025 | 11.8984 | 11.8912 | 11.8826 | 11.8671 | 11.8577 | 11.8577 | 11.8577 | 11.8577 | 11.8577 | 11.8577 | 11.8577 | 11.04 | 11.04 | 11.04 | 11.0349 | 11.0258 | 11.0151 | 10.9957 | 10.9839 | 10.9839 | 10.9839 | 10.9839 | 10.9839 | 10.9839 | 10.9839 | 11.04 | 11.04 | 11.04 | 11.0349 | 11.0258 | 11.0151 | 10.9957 | 10.9839 | 10.9839 | 10.9839 | 10.9839 | 10.9839 | 10.9839 | 10.9839
|  | GOLDSMITHS | LW |  |  | 11.9025 | 11.9025 | 11.9025 | 11.8763 | 11.8471 | 11.8077 | 11.7649 | 11.729 | 11.7211 | 11.7129 | 11.6985 | 11.6585 | 11.6502 | 11.6502 | 11.04 | 11.04 | 11.04 | 11.0073 | 10.9707 | 10.9215 | 10.868 | 10.8231 | 10.8132 | 10.803 | 10.785 | 10.7349 | 10.7246 | 10.7246 | 11.04 | 11.04 | 11.04 | 11.0073 | 10.9707 | 10.9215 | 10.868 | 10.8231 | 10.8132 | 10.803 | 10.785 | 10.7349 | 10.7246 | 10.7246
|  | GOLDSMITHS | ST |  |  | 11.9025 | 11.9025 | 11.9025 | 11.8722 | 11.8518 | 11.8333 | 11.8053 | 11.7924 | 11.7924 | 11.7924 | 11.7924 | 11.7924 | 11.7924 | 11.7924 | 11.04 | 11.04 | 11.04 | 11.0022 | 10.9766 | 10.9536 | 10.9185 | 10.9024 | 10.9024 | 10.9024 | 10.9024 | 10.9024 | 10.9024 | 10.9024 | 11.04 | 11.04 | 11.04 | 11.0022 | 10.9766 | 10.9536 | 10.9185 | 10.9024 | 10.9024 | 10.9024 | 10.9024 | 10.9024 | 10.9024 | 10.9024
|  | GOLDSMITHS | FS |  |  | 11.9025 | 11.9025 | 11.9025 | 11.8984 | 11.8912 | 11.8826 | 11.8671 | 11.8577 | 11.8577 | 11.8577 | 11.8577 | 11.8577 | 11.8577 | 11.8577 | 11.04 | 11.04 | 11.04 | 11.0317 | 11.0235 | 11.0135 | 11.0036 | 10.9953 | 10.9953 | 10.9953 | 10.9953 | 10.9953 | 10.9953 | 10.9953 | 11.04 | 11.04 | 11.04 | 11.0317 | 11.0235 | 11.0135 | 11.0036 | 10.9953 | 10.9953 | 10.9953 | 10.9953 | 10.9953 | 10.9953 | 10.9953
NURSLING GSP | WINCHESTER | GORDON ROAD | MINIMUM HEADROOM | SU 48217 29991 | YES | 7.9392 | 7.8163 | 7.6675 | 7.1716 | 6.4803 | 5.6325 | 4.6556 | 3.6604 | 1.7078 | -0.90725 | -7.0809 | -17.5412 | -20.6356 | -22.5069 | 11.9026 | 11.7952 | 11.6417 | 11.3808 | 11.0321 | 10.5622 | 9.8697 | 8.3667 | 6.6 | 4.0346 | -2.6056 | -14.4897 | -18.884 | -32.4482 | 7.8802 | 7.6803 | 7.4561 | 6.926 | 6.2642 | 5.37 | 4.3498 | 2.8857 | 0.7687 | -1.9741 | -9.9205 | -24.6042 | -30.1097 | -34.4313
|  | GORDON ROAD | CT |  |  | 7.957 | 7.8736 | 7.7626 | 7.5845 | 7.3534 | 6.8777 | 6.3269 | 5.7741 | 5.0202 | 4.1708 | 1.6983 | -7.5783 | -12.31 | -13.1179 | 11.9114 | 11.8148 | 11.6956 | 11.5221 | 11.3034 | 11.0079 | 10.6663 | 10.2821 | 9.8748 | 9.1872 | 6.8703 | 0.36032 | -4.8904 | -14.6016 | 7.906 | 7.8077 | 7.6842 | 7.4958 | 7.17 | 6.6801 | 6.17 | 5.6021 | 4.8025 | 3.7714 | 0.81685 | -7.932 | -12.3192 | -12.9987
|  | GORDON ROAD | LW |  |  | 7.9392 | 7.8163 | 7.6675 | 7.1716 | 6.4803 | 5.6325 | 4.6556 | 3.6604 | 1.7078 | -0.90725 | -7.0809 | -17.5412 | -20.6356 | -22.5069 | 11.9285 | 11.8334 | 11.7228 | 11.4589 | 11.1112 | 10.6555 | 9.8697 | 8.3667 | 6.6658 | 4.6347 | 0.0076085 | -7.642 | -9.7022 | -11.0263 | 7.8802 | 7.6803 | 7.4561 | 6.926 | 6.2642 | 5.37 | 4.3498 | 2.8857 | 0.7687 | -1.8316 | -7.7238 | -17.6699 | -20.555 | -22.3035
|  | GORDON ROAD | ST |  |  | 8.0143 | 7.9898 | 7.9405 | 7.7422 | 7.5364 | 7.2953 | 7.0324 | 6.8303 | 6.6599 | 6.4451 | 5.9 | 3.7037 | 2.5636 | 0.36764 | 11.9549 | 11.9036 | 11.832 | 11.6035 | 11.3841 | 11.1395 | 10.8493 | 10.6117 | 10.4041 | 10.1547 | 9.527 | 5.4028 | -0.76091 | -11.0728 | 7.9757 | 7.948 | 7.8987 | 7.6843 | 7.474 | 7.2334 | 6.9515 | 6.7271 | 6.5338 | 6.2833 | 5.5731 | 2.844 | 1.759 | 0.5413
|  | GORDON ROAD | FS |  |  | 7.957 | 7.8736 | 7.7626 | 7.5845 | 7.3534 | 6.8777 | 6.3269 | 5.7741 | 5.0202 | 4.1708 | 1.6983 | -7.5783 | -12.31 | -13.1179 | 11.9026 | 11.7952 | 11.6417 | 11.3808 | 11.0321 | 10.5622 | 9.903 | 8.4648 | 6.6 | 4.0346 | -2.6056 | -14.4897 | -18.884 | -32.4482 | 7.8984 | 7.7942 | 7.6292 | 7.335 | 6.8903 | 6.2182 | 4.9325 | 3.1476 | 0.96167 | -1.9741 | -9.9205 | -24.6042 | -30.1097 | -34.4313
BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING | MINIMUM HEADROOM | SU 60305 82895 | YES | 7.9261 | 7.6716 | 7.421 | 7.0736 | 6.6235 | 6.1236 | 5.3258 | 4.1533 | 1.8079 | -1.0721 | -8.0722 | -20.2698 | -29.7611 | -35.2248 | 8.2055 | 8.0636 | 7.8673 | 7.565 | 7.1007 | 6.4145 | 5.4577 | 4.125 | 2.4233 | 0.22767 | -5.1906 | -23.9926 | -41.1494 | -46.5005 | 7.6894 | 7.4438 | 7.2014 | 6.8705 | 6.4381 | 5.9577 | 5.1814 | 3.9313 | 1.6839 | -1.0765 | -7.7881 | -30.6043 | -51.6704 | -58.3353
|  | GORING | CT |  |  | 7.9738 | 7.7777 | 7.5377 | 7.2072 | 6.825 | 6.2489 | 5.5899 | 4.1533 | 1.8079 | -1.0721 | -8.0722 | -20.2698 | -23.6583 | -25.9979 | 8.2545 | 8.1056 | 7.8884 | 7.565 | 7.1007 | 6.4145 | 5.4577 | 4.125 | 2.4233 | 0.22767 | -5.1906 | -14.5443 | -17.031 | -18.7893 | 7.7269 | 7.5334 | 7.2964 | 6.9797 | 6.6115 | 6.0514 | 5.41 | 3.9313 | 1.6839 | -1.0765 | -7.7881 | -19.4685 | -22.6879 | -24.9151
|  | GORING | LW |  |  | 7.9261 | 7.6716 | 7.421 | 7.0736 | 6.6235 | 6.1236 | 5.3258 | 4.3193 | 2.7982 | 0.41355 | -5.8215 | -19.9023 | -29.7611 | -35.2248 | 8.2357 | 8.0836 | 7.8821 | 7.5918 | 7.1772 | 6.6014 | 5.7743 | 4.6574 | 3.269 | 1.4814 | -3.35 | -14.2673 | -21.9151 | -26.1768 | 7.6894 | 7.4438 | 7.2014 | 6.8705 | 6.4381 | 5.9577 | 5.1814 | 4.1994 | 2.6532 | 0.36656 | -5.616 | -19.1233 | -28.5703 | -33.8019
|  | GORING | ST |  |  | 8.1134 | 8.0475 | 7.9651 | 7.8452 | 7.6879 | 7.478 | 7.2046 | 6.8507 | 6.4408 | 5.9224 | 4.4913 | -0.16558 | -3.2167 | -4.2004 | 8.3887 | 8.375 | 8.3568 | 8.3329 | 8.3011 | 8.2595 | 8.2058 | 8.1373 | 8.0586 | 7.96 | 6.8757 | 3.0921 | 0.60798 | -0.28488 | 7.8634 | 7.7987 | 7.7168 | 7.5986 | 7.4429 | 7.2351 | 6.9637 | 6.6123 | 6.2047 | 5.6893 | 4.2662 | -0.34775 | -3.3382 | -4.2505
|  | GORING | FS |  |  | 7.9738 | 7.7777 | 7.5377 | 7.2072 | 6.825 | 6.2489 | 5.5899 | 4.1533 | 1.8079 | -1.0721 | -8.0722 | -20.2698 | -23.6583 | -25.9979 | 8.2055 | 8.0636 | 7.8673 | 7.594 | 7.2163 | 6.6966 | 5.9846 | 5.017 | 3.7791 | 2.1463 | -2.9868 | -23.9926 | -41.1494 | -46.5005 | 7.8404 | 7.7688 | 7.6725 | 7.5359 | 7.3531 | 7.1195 | 6.4132 | 5.1555 | 3.5401 | 1.4302 | -4.8605 | -30.6043 | -51.6704 | -58.3353
IVER 132KV | DENHAM | GRASSINGHAM ROAD | MINIMUM HEADROOM | TQ 00165 90988 | YES | 6.0626 | 5.5198 | 4.9665 | 4.1267 | 3.081 | 1.9615 | 0.19177 | -1.9732 | -4.4658 | -7.2591 | -13.3933 | -26.5471 | -33.5719 | -34.191 | 7.9232 | 7.5467 | 7.1666 | 6.6358 | 5.9345 | 5.1682 | 3.8916 | 2.3076 | 0.51941 | -1.5083 | -5.9984 | -15.6691 | -22.267 | -27.2541 | 5.2256 | 4.7386 | 4.2401 | 3.4636 | 2.5025 | 1.4452 | -0.27385 | -2.3802 | -4.7917 | -7.4996 | -13.4549 | -26.2361 | -32.9574 | -35.6243
|  | GRASSINGHAM ROAD | CT |  |  | 6.265 | 5.8915 | 5.4436 | 4.744 | 3.9813 | 2.8758 | 1.6404 | -0.14705 | -2.5682 | -4.9552 | -9.5639 | -21.4758 | -29.205 | -32.8801 | 7.9328 | 7.602 | 7.2042 | 6.6953 | 6.1295 | 5.277 | 4.3173 | 2.9039 | 1.1545 | -0.57325 | -3.8855 | -12.4254 | -17.1277 | -19.8495 | 5.4223 | 5.0939 | 4.6449 | 3.9804 | 3.2518 | 2.1737 | 0.9687 | -0.79623 | -3.1205 | -5.4072 | -9.7835 | -21.1892 | -28.6746 | -32.1884
|  | GRASSINGHAM ROAD | LW |  |  | 6.0626 | 5.5198 | 4.9665 | 4.1267 | 3.081 | 1.9615 | 0.19177 | -1.9732 | -4.4658 | -7.2591 | -13.3933 | -26.5471 | -33.5719 | -34.191 | 7.9232 | 7.5467 | 7.1666 | 6.6358 | 5.9345 | 5.1682 | 3.8916 | 2.3076 | 0.51941 | -1.5083 | -5.9984 | -15.6691 | -20.902 | -21.4207 | 5.2256 | 4.7386 | 4.2401 | 3.4636 | 2.5025 | 1.4452 | -0.27385 | -2.3802 | -4.7917 | -7.4996 | -13.4549 | -26.2361 | -32.9574 | -33.5922
|  | GRASSINGHAM ROAD | ST |  |  | 6.5281 | 6.4124 | 6.2502 | 5.9694 | 5.63 | 5.1988 | 4.5981 | 3.874 | 3.0389 | 1.9949 | -0.88351 | -11.1609 | -18.4742 | -21.631 | 8.1351 | 8.0073 | 7.8376 | 7.5533 | 7.2229 | 6.8107 | 6.2555 | 5.602 | 4.8642 | 3.951 | 1.4523 | -6.946 | -13.0022 | -15.9763 | 5.6582 | 5.5585 | 5.4182 | 5.1522 | 4.7976 | 4.3487 | 3.7288 | 2.9873 | 2.1305 | 1.0609 | -1.8875 | -11.8786 | -19.0435 | -22.0079
|  | GRASSINGHAM ROAD | FS |  |  | 6.265 | 5.8915 | 5.4436 | 4.744 | 3.9813 | 2.8758 | 1.6404 | -0.14705 | -2.5682 | -4.9552 | -9.5639 | -21.4758 | -29.205 | -32.8801 | 7.9356 | 7.6177 | 7.2503 | 6.8168 | 6.277 | 5.5791 | 4.6254 | 3.3493 | 1.8991 | 0.31627 | -3.3801 | -13.6676 | -22.267 | -27.2541 | 5.4561 | 5.1472 | 4.7488 | 4.2465 | 3.6203 | 2.8037 | 1.6769 | 0.15909 | -1.6169 | -3.5412 | -7.9193 | -20.3172 | -30.5204 | -35.6243
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET | MINIMUM HEADROOM | SU 64445 00178 | YES | 14.8947 | 14.7185 | 14.4816 | 14.1236 | 13.6852 | 13.2511 | 12.4566 | 11.4719 | 10.3948 | 9.2012 | 6.5968 | 1.8744 | -0.4153 | -3.4444 | 16.987 | 16.6678 | 16.2724 | 15.7694 | 15.2042 | 14.474 | 13.669 | 12.6253 | 11.4011 | 10.1378 | 7.5587 | -3.3469 | -21.3739 | -51.1662 | 13.7949 | 13.6818 | 13.5013 | 13.1088 | 12.5707 | 12.0284 | 11.1907 | 10.2339 | 9.1774 | 8.0044 | 5.4445 | 0.80391 | -1.4566 | -4.4964
|  | GREETHAM STREET | CT |  |  | 14.9658 | 14.8464 | 14.6766 | 14.3841 | 14.0253 | 13.5719 | 12.8802 | 11.9515 | 10.8046 | 9.675 | 7.554 | 2.6913 | 0.76604 | 0.060575 | 16.987 | 16.6678 | 16.2724 | 15.7694 | 15.2042 | 14.474 | 13.669 | 12.6253 | 11.4011 | 10.1378 | 7.5587 | -0.085548 | -9.0266 | -23.1113 | 13.7949 | 13.6818 | 13.5333 | 13.2769 | 12.8282 | 12.2191 | 11.5597 | 10.656 | 9.5407 | 8.4397 | 6.3735 | 1.6456 | -0.24671 | -0.98764
|  | GREETHAM STREET | LW |  |  | 14.8947 | 14.7185 | 14.4816 | 14.1236 | 13.6852 | 13.2511 | 12.4566 | 11.4719 | 10.3948 | 9.2012 | 6.5968 | 1.8744 | -0.4153 | -3.4444 | 17.1115 | 16.9119 | 16.6889 | 16.4059 | 16.0338 | 15.6515 | 15.0304 | 14.3075 | 13.4908 | 12.5787 | 10.5862 | 6.9382 | 4.9806 | 2.3824 | 13.8065 | 13.6883 | 13.5013 | 13.1088 | 12.5707 | 12.0284 | 11.1907 | 10.2339 | 9.1774 | 8.0044 | 5.4445 | 0.80391 | -1.4566 | -4.4964
|  | GREETHAM STREET | ST |  |  | 15.1214 | 15.1028 | 15.0499 | 14.97 | 14.8621 | 14.7452 | 14.5977 | 14.3729 | 13.9193 | 13.351 | 11.8321 | 6.6428 | 3.2335 | 1.9261 | 17.1154 | 16.9067 | 16.6379 | 16.288 | 15.8712 | 15.3874 | 14.8147 | 14.1617 | 13.4023 | 12.5107 | 10.2488 | 2.0849 | -8.1504 | -22.6348 | 13.8792 | 13.8305 | 13.7504 | 13.6487 | 13.5193 | 13.3757 | 13.2019 | 12.9258 | 12.4627 | 11.886 | 10.3379 | 5.1874 | 1.7527 | 0.41237
|  | GREETHAM STREET | FS |  |  | 14.9658 | 14.8464 | 14.6766 | 14.3841 | 14.0253 | 13.5719 | 12.8802 | 11.9515 | 10.8046 | 9.675 | 7.554 | 2.6913 | 0.76604 | 0.060575 | 17.0533 | 16.7814 | 16.4462 | 15.944 | 15.3428 | 14.6606 | 13.8127 | 12.8381 | 11.8075 | 10.6192 | 7.6404 | -3.3469 | -21.3739 | -51.1662 | 13.8706 | 13.8326 | 13.7617 | 13.6737 | 13.559 | 13.3136 | 12.8974 | 12.4061 | 11.8579 | 11.2195 | 9.5786 | 4.3046 | -1.063 | -4.1308
COWLEY GSP | DRAYTON BSP | GROVE | MINIMUM HEADROOM | SU 39515 89611 | NO | -1.3931 | -2.0413 | -2.7 | -3.4407 | -4.2387 | -5.1428 | -6.1426 | -7.5746 | -8.6804 | -9.7696 | -12.1574 | -17.7654 | -21.6431 | -22.4336 | 1.352 | 1.0269 | 0.70303 | 0.3553 | -0.018808 | -0.44261 | -0.92065 | -1.6508 | -2.2004 | -3.1534 | -7.4215 | -15.6063 | -18.5674 | -20.7814 | -0.71443 | -1.2296 | -1.7552 | -2.3619 | -3.0214 | -3.7693 | -4.6052 | -5.8081 | -6.7572 | -8.3353 | -13.241 | -23.3659 | -27.2176 | -30.1768
|  | GROVE | CT |  |  | -1.0961 | -1.5236 | -1.978 | -2.5448 | -3.1593 | -3.9183 | -4.7393 | -5.9482 | -7.0668 | -8.1253 | -10.307 | -14.9185 | -18.1004 | -19.9926 | 1.4538 | 1.2116 | 0.95317 | 0.65468 | 0.32908 | -0.074937 | -0.52044 | -1.1957 | -1.7833 | -2.365 | -3.5722 | -6.4575 | -9.1662 | -12.1039 | -0.45574 | -0.7842 | -1.1366 | -1.5983 | -2.1025 | -2.7282 | -3.4108 | -4.4215 | -5.375 | -6.289 | -8.1648 | -12.2059 | -15.0211 | -16.6941
|  | GROVE | LW |  |  | -1.3931 | -2.0413 | -2.7 | -3.4407 | -4.2387 | -5.1428 | -6.1426 | -7.5746 | -8.6804 | -9.7696 | -12.1574 | -17.7654 | -21.6431 | -22.4336 | 1.352 | 1.0269 | 0.70303 | 0.3553 | -0.018808 | -0.44261 | -0.92065 | -1.6508 | -2.2004 | -2.7579 | -4.0163 | -8.8503 | -11.946 | -12.3906 | -0.71443 | -1.2296 | -1.7552 | -2.3619 | -3.0214 | -3.7693 | -4.6052 | -5.8081 | -6.7572 | -7.7004 | -9.7703 | -16.8998 | -20.959 | -21.5425
|  | GROVE | ST |  |  | -0.99132 | -1.3646 | -1.7588 | -2.1459 | -2.5352 | -2.9913 | -3.4687 | -4.1735 | -4.6493 | -5.0858 | -6.057 | -8.4014 | -10.4506 | -12.7297 | 1.5033 | 1.2887 | 1.0604 | 0.81802 | 0.57559 | 0.29224 | -0.018718 | -0.48327 | -0.81444 | -1.1322 | -1.8445 | -3.7965 | -6.0124 | -9.0913 | -0.3621 | -0.64164 | -0.93961 | -1.2509 | -1.5607 | -1.9215 | -2.3047 | -2.8703 | -3.2612 | -3.624 | -4.4356 | -6.4869 | -8.3321 | -10.3665
|  | GROVE | FS |  |  | -1.0961 | -1.5236 | -1.978 | -2.5448 | -3.1593 | -3.9183 | -4.7393 | -5.9482 | -7.0668 | -8.1253 | -10.307 | -14.9185 | -18.1004 | -19.9926 | 1.5212 | 1.2837 | 1.0267 | 0.74317 | 0.42667 | 0.037067 | -0.41819 | -1.0382 | -1.6751 | -3.1534 | -7.4215 | -15.6063 | -18.5674 | -20.7814 | -0.32088 | -0.5944 | -0.88626 | -1.2337 | -1.6071 | -2.0642 | -3.0757 | -4.5271 | -6.2565 | -8.3353 | -13.241 | -23.3659 | -27.2176 | -30.1768
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL | MINIMUM HEADROOM | ST 98638 11417 | YES | 1.7154 | 1.6966 | 1.6721 | 1.6412 | 1.6014 | 1.5423 | 1.4673 | 1.2277 | 0.8999 | 0.56827 | -0.10626 | -2.2382 | -3.4073 | -3.3117 | 1.6325 | 1.5853 | 1.5261 | 1.4266 | 1.1013 | 0.61627 | -0.10951 | -1.1097 | -2.3693 | -3.9607 | -8.0733 | -14.8244 | -16.5596 | -17.8618 | 1.502 | 1.3956 | 1.2411 | 1.0076 | 0.66023 | 0.062224 | -0.82795 | -2.0543 | -3.5974 | -5.5469 | -10.581 | -18.8626 | -21.0008 | -22.6036
|  | GUSSAGE ST MICHAEL | CT |  |  | 1.7154 | 1.6966 | 1.6721 | 1.6412 | 1.6014 | 1.5423 | 1.4673 | 1.2277 | 0.8999 | 0.56827 | -0.10626 | -2.2382 | -3.4073 | -3.3117 | 1.6325 | 1.5853 | 1.5261 | 1.4595 | 1.3811 | 1.2606 | 1.1225 | 0.91643 | 0.66528 | 0.41042 | -0.10306 | -1.3545 | -2.3177 | -2.2331 | 1.5621 | 1.5331 | 1.494 | 1.4494 | 1.363 | 1.2041 | 1.0226 | 0.75537 | 0.42691 | 0.094997 | -0.57521 | -2.4175 | -3.6215 | -3.5262
|  | GUSSAGE ST MICHAEL | LW |  |  | 1.7205 | 1.7021 | 1.6804 | 1.6523 | 1.6115 | 1.5588 | 1.4755 | 1.2901 | 1.0114 | 0.69539 | -0.016351 | -1.2402 | -1.4795 | -1.2487 | 1.6382 | 1.5885 | 1.538 | 1.4842 | 1.4095 | 1.327 | 1.1812 | 0.99447 | 0.78213 | 0.54031 | -0.0043717 | -0.93357 | -1.0972 | -0.8225 | 1.5513 | 1.514 | 1.4689 | 1.4238 | 1.3643 | 1.2677 | 1.076 | 0.83091 | 0.55122 | 0.23512 | -0.47665 | -1.6963 | -1.9247 | -1.5805
|  | GUSSAGE ST MICHAEL | ST |  |  | 1.7324 | 1.7282 | 1.7225 | 1.7145 | 1.7036 | 1.6892 | 1.6705 | 1.6464 | 1.6183 | 1.5388 | 1.1317 | -0.16172 | -0.977 | -1.1512 | 1.6661 | 1.6479 | 1.6264 | 1.598 | 1.56 | 1.5116 | 1.4481 | 1.3686 | 1.2769 | 1.1625 | 0.84498 | -0.17376 | -0.81815 | -0.96524 | 1.5922 | 1.5758 | 1.5635 | 1.5482 | 1.5291 | 1.51 | 1.4476 | 1.3429 | 1.2216 | 1.0719 | 0.65741 | -0.65575 | -1.4795 | -1.6472
|  | GUSSAGE ST MICHAEL | FS |  |  | 1.7154 | 1.6966 | 1.6721 | 1.6412 | 1.6014 | 1.5423 | 1.4673 | 1.2277 | 0.8999 | 0.56827 | -0.10626 | -2.2382 | -3.4073 | -3.3117 | 1.6526 | 1.622 | 1.5826 | 1.4266 | 1.1013 | 0.61627 | -0.10951 | -1.1097 | -2.3693 | -3.9607 | -8.0733 | -14.8244 | -16.5596 | -17.8618 | 1.502 | 1.3956 | 1.2411 | 1.0076 | 0.66023 | 0.062224 | -0.82795 | -2.0543 | -3.5974 | -5.5469 | -10.581 | -18.8626 | -21.0008 | -22.6036
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE | MINIMUM HEADROOM | SU 47370 08794 | YES | 12.9933 | 12.8338 | 12.6696 | 12.3421 | 11.9946 | 11.6386 | 11.1954 | 10.6831 | 9.7235 | 8.3258 | 5.3077 | -0.38585 | -2.6 | -4.0378 | 14.5804 | 14.5005 | 14.3785 | 14.1962 | 13.9675 | 13.6335 | 13.1758 | 12.5288 | 11.6601 | 10.6657 | 8.507 | 4.5814 | -3.6723 | -8.5249 | 11.9309 | 11.7838 | 11.6325 | 11.3308 | 11.0099 | 10.6806 | 10.2745 | 9.8079 | 9.1937 | 7.8687 | 5.0077 | -0.35681 | -9.6429 | -15.7896
|  | HAMBLE | CT |  |  | 13.187 | 13.1256 | 13.0565 | 12.8204 | 12.5713 | 12.2825 | 11.8583 | 10.9694 | 9.7235 | 8.3258 | 5.3077 | -0.38585 | -2.6 | -4.0378 | 14.5804 | 14.5071 | 14.3785 | 14.1962 | 13.9675 | 13.6335 | 13.1758 | 12.5288 | 11.6601 | 10.6657 | 8.507 | 4.6167 | 3.2091 | 2.1466 | 12.1078 | 12.0499 | 11.9842 | 11.7641 | 11.5304 | 11.2574 | 10.9486 | 10.369 | 9.1937 | 7.8687 | 5.0077 | -0.35681 | -2.4448 | -3.8451
|  | HAMBLE | LW |  |  | 12.9933 | 12.8338 | 12.6696 | 12.3421 | 11.9946 | 11.6386 | 11.1954 | 10.6831 | 10.0223 | 9.3261 | 7.5711 | 4.5418 | 3.2604 | 2.3227 | 14.596 | 14.5005 | 14.3979 | 14.2618 | 14.0797 | 13.8434 | 13.4818 | 13.0375 | 12.4814 | 11.8559 | 10.4785 | 8.4946 | 7.577 | 6.6902 | 11.9309 | 11.7838 | 11.6325 | 11.3308 | 11.0099 | 10.6806 | 10.2745 | 9.8079 | 9.196 | 8.5508 | 7.2156 | 4.3733 | 3.065 | 2.0721
|  | HAMBLE | ST |  |  | 13.2477 | 13.2212 | 13.1868 | 13.1293 | 13.0504 | 12.9479 | 12.8035 | 12.6082 | 12.3422 | 12.0303 | 11.2714 | 9.1358 | 7.3953 | 5.4034 | 14.6262 | 14.6068 | 14.5813 | 14.5449 | 14.4973 | 14.4326 | 14.3139 | 14.1621 | 13.9474 | 13.696 | 13.047 | 11.2843 | 9.0173 | 5.8195 | 12.1678 | 12.1457 | 12.1163 | 12.066 | 11.9967 | 11.9067 | 11.7817 | 11.6145 | 11.3766 | 11.1 | 10.4266 | 8.5183 | 6.8186 | 4.8964
|  | HAMBLE | FS |  |  | 13.187 | 13.1256 | 13.0565 | 12.8204 | 12.5713 | 12.2825 | 11.8583 | 10.9694 | 9.7235 | 8.3258 | 5.3077 | -0.38585 | -2.6 | -4.0378 | 14.6008 | 14.5677 | 14.524 | 14.4187 | 14.2798 | 14.1001 | 13.8671 | 13.5643 | 13.1772 | 12.6879 | 11.1978 | 4.5814 | -3.6723 | -8.5249 | 12.1636 | 12.1456 | 12.1251 | 12.0643 | 11.9945 | 11.9116 | 11.8079 | 11.6772 | 11.4036 | 10.7592 | 8.9053 | 0.65769 | -9.6429 | -15.7896
MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY | MINIMUM HEADROOM | SZ 00104 90800 | YES | 5.4174 | 4.4088 | 3.6328 | 2.1622 | 0.46045 | -1.3293 | -3.3538 | -5.5285 | -7.947 | -10.6111 | -14.7013 | -23.2122 | -29.2177 | -32.6193 | 10.4304 | 9.8805 | 9.4474 | 8.6917 | 7.8006 | 6.864 | 5.7416 | 4.4975 | 2.8808 | 1.0921 | -1.9465 | -9.5483 | -16.0103 | -30.3184 | 5.9076 | 5.0705 | 4.3995 | 3.1644 | 1.7151 | 0.18371 | -1.625 | -3.5967 | -5.8178 | -8.2658 | -12.2977 | -20.2083 | -25.7381 | -28.9197
|  | HAMWORTHY | CT |  |  | 5.8105 | 5.0824 | 4.4857 | 3.2491 | 1.8325 | 0.18558 | -1.4933 | -3.4427 | -6.048 | -8.8506 | -13.212 | -23.2122 | -29.2177 | -32.6193 | 10.5108 | 10.0208 | 9.5632 | 8.8076 | 7.9465 | 6.9158 | 5.8317 | 4.5346 | 2.8808 | 1.0921 | -1.9465 | -9.5483 | -16.0103 | -23.4856 | 6.2253 | 5.6176 | 5.0833 | 4.0287 | 2.82 | 1.3753 | -0.11499 | -1.8947 | -4.2656 | -6.8023 | -10.8547 | -20.2083 | -25.7381 | -28.9197
|  | HAMWORTHY | LW |  |  | 5.4174 | 4.4088 | 3.6328 | 2.1622 | 0.46045 | -1.3293 | -3.3538 | -5.5285 | -7.947 | -10.6111 | -14.7013 | -22.1028 | -25.9527 | -27.5907 | 10.4304 | 9.8805 | 9.4474 | 8.6917 | 7.8006 | 6.864 | 5.7416 | 4.4975 | 3.0754 | 1.499 | -1.1624 | -5.9611 | -8.4899 | -9.7298 | 5.9076 | 5.0705 | 4.3995 | 3.1644 | 1.7151 | 0.18371 | -1.625 | -3.5967 | -5.8178 | -8.2658 | -12.2977 | -19.5469 | -23.1301 | -24.6051
|  | HAMWORTHY | ST |  |  | 6.0202 | 5.4591 | 5.0353 | 4.2868 | 3.4524 | 2.5843 | 1.7138 | 0.84315 | -0.18514 | -1.3961 | -3.4943 | -11.3757 | -17.7832 | -22.2002 | 10.6341 | 10.2521 | 9.9105 | 9.356 | 8.7428 | 8.0874 | 7.4028 | 6.6886 | 5.7963 | 4.7618 | 2.6284 | -4.6832 | -12.2871 | -20.2695 | 6.426 | 5.986 | 5.6275 | 4.9957 | 4.2905 | 3.5437 | 2.7666 | 1.9794 | 0.99381 | -0.20138 | -2.5703 | -10.2314 | -16.5476 | -20.8305
|  | HAMWORTHY | FS |  |  | 5.8105 | 5.0824 | 4.4857 | 3.2491 | 1.8325 | 0.18558 | -1.4933 | -3.4427 | -6.048 | -8.8506 | -13.212 | -23.2122 | -29.2177 | -32.6193 | 10.6646 | 10.2977 | 9.9883 | 9.4734 | 8.8884 | 8.2507 | 7.5627 | 6.8031 | 5.8766 | 4.8073 | 2.5136 | -7.0149 | -15.958 | -30.3184 | 6.4914 | 6.1039 | 5.8132 | 5.2626 | 4.6409 | 3.9732 | 3.266 | 2.4877 | 1.5511 | 0.48682 | -1.6468 | -13.3459 | -21.3508 | -23.6576
IVER 132KV | DENHAM | HAREFIELD | MINIMUM HEADROOM | TQ 04001 91227 | YES | 5.0799 | 5.0074 | 4.9408 | 4.8097 | 4.6237 | 4.3817 | 4.0952 | 3.7125 | 3.1892 | 2.5835 | 1.0502 | -3.822 | -6.1934 | -6.24 | 5.7914 | 5.7671 | 5.7423 | 5.685 | 5.614 | 5.5296 | 5.4373 | 5.3273 | 5.1685 | 4.8057 | 3.7071 | 0.15004 | -1.5407 | -1.5045 | 4.677 | 4.6288 | 4.5786 | 4.4533 | 4.3056 | 4.1526 | 3.9866 | 3.8132 | 3.6145 | 3.2023 | 1.7521 | -2.8664 | -5.103 | -5.1256
|  | HAREFIELD | CT |  |  | 5.1018 | 5.0379 | 4.9589 | 4.8097 | 4.6237 | 4.3817 | 4.0952 | 3.7125 | 3.1892 | 2.5835 | 1.0502 | -3.822 | -6.1934 | -6.24 | 5.8097 | 5.7863 | 5.758 | 5.6944 | 5.6166 | 5.5296 | 5.4373 | 5.3273 | 5.1685 | 4.8057 | 3.7071 | 0.15004 | -1.5407 | -1.5045 | 4.7525 | 4.7378 | 4.718 | 4.6227 | 4.5073 | 4.3834 | 4.2576 | 4.1101 | 3.7731 | 3.2023 | 1.7521 | -2.8664 | -5.103 | -5.1256
|  | HAREFIELD | LW |  |  | 5.0799 | 5.0074 | 4.9408 | 4.8196 | 4.6694 | 4.5106 | 4.2947 | 4.0635 | 3.8014 | 3.5318 | 2.967 | 1.9817 | 1.5213 | 1.3594 | 5.7914 | 5.7671 | 5.7423 | 5.685 | 5.614 | 5.5393 | 5.4558 | 5.3678 | 5.2674 | 5.1643 | 4.9484 | 4.4719 | 4.1775 | 4.0644 | 4.677 | 4.6288 | 4.5786 | 4.4533 | 4.3056 | 4.1526 | 3.9866 | 3.8132 | 3.6145 | 3.413 | 2.9969 | 2.0695 | 1.5254 | 1.3303
|  | HAREFIELD | ST |  |  | 5.17 | 5.1589 | 5.1437 | 5.117 | 5.0794 | 5.0321 | 4.9776 | 4.9101 | 4.8268 | 4.7219 | 4.4515 | 3.5813 | 3.1063 | 2.7227 | 5.8203 | 5.8062 | 5.7897 | 5.7667 | 5.7359 | 5.7015 | 5.6666 | 5.6263 | 5.579 | 5.5227 | 5.39 | 4.835 | 4.0606 | 2.851 | 4.7715 | 4.7706 | 4.7689 | 4.7597 | 4.7434 | 4.7256 | 4.7113 | 4.6928 | 4.6698 | 4.637 | 4.565 | 4.0561 | 3.6497 | 3.0768
|  | HAREFIELD | FS |  |  | 5.1018 | 5.0379 | 4.9589 | 4.8097 | 4.6237 | 4.3817 | 4.0952 | 3.7125 | 3.1892 | 2.5835 | 1.0502 | -3.822 | -6.1934 | -6.24 | 5.8166 | 5.797 | 5.774 | 5.7475 | 5.7076 | 5.6645 | 5.6118 | 5.5543 | 5.4744 | 5.3885 | 5.1787 | 4.3762 | 3.0686 | 0.84268 | 4.7695 | 4.7645 | 4.7583 | 4.7505 | 4.7255 | 4.7036 | 4.6734 | 4.6452 | 4.5809 | 4.5202 | 4.3775 | 3.8489 | 3.235 | 2.6262
NURSLING GSP | WINCHESTER | HARESTOCK | MINIMUM HEADROOM | SU 45908 31300 | YES | 7.3603 | 6.825 | 6.2838 | 5.4383 | 4.5172 | 3.5435 | 2.4657 | 1.3149 | -0.025296 | -1.4173 | -4.3148 | -9.7278 | -13.6507 | -16.0448 | 11.2429 | 10.9875 | 10.7315 | 10.3528 | 9.9396 | 9.4978 | 8.9882 | 8.4399 | 7.8052 | 7.122 | 5.4453 | 1.5642 | -1.4327 | -4.4204 | 7.8892 | 7.4386 | 6.9819 | 6.2562 | 5.472 | 4.6387 | 3.7071 | 2.7096 | 1.5403 | 0.32315 | -2.2121 | -7.0105 | -10.7248 | -12.8772
|  | HARESTOCK | CT |  |  | 7.6469 | 7.3248 | 6.9825 | 6.3737 | 5.7073 | 4.9237 | 4.0581 | 3.0948 | 1.6339 | 0.11927 | -2.9241 | -9.4991 | -13.6507 | -16.0448 | 11.2898 | 11.0826 | 10.8576 | 10.5264 | 10.1564 | 9.7238 | 9.2334 | 8.6895 | 7.9578 | 7.1277 | 5.4453 | 1.5642 | -1.4327 | -4.4204 | 8.1559 | 7.8977 | 7.6206 | 7.086 | 6.4949 | 5.8176 | 5.0652 | 4.2295 | 2.9522 | 1.6103 | -1.0779 | -6.9824 | -10.7248 | -12.8772
|  | HARESTOCK | LW |  |  | 7.3603 | 6.825 | 6.2838 | 5.4383 | 4.5172 | 3.5435 | 2.4657 | 1.3149 | -0.025296 | -1.4173 | -4.3148 | -9.7278 | -12.8458 | -14.4855 | 11.2429 | 10.9875 | 10.7315 | 10.3528 | 9.9396 | 9.4978 | 8.9882 | 8.4399 | 7.8052 | 7.122 | 5.6771 | 2.9628 | 1.145 | -0.14897 | 7.8892 | 7.4386 | 6.9819 | 6.2562 | 5.472 | 4.6387 | 3.7071 | 2.7096 | 1.5403 | 0.32315 | -2.2121 | -7.0105 | -9.9154 | -11.5665
|  | HARESTOCK | ST |  |  | 7.8635 | 7.6022 | 7.318 | 6.9241 | 6.5471 | 6.142 | 5.6969 | 5.2641 | 4.7612 | 4.2419 | 3.078 | -0.20948 | -3.5997 | -7.3022 | 11.4354 | 11.2633 | 11.0734 | 10.7656 | 10.4801 | 10.1761 | 9.8196 | 9.4917 | 9.1027 | 8.701 | 7.7753 | 5.0644 | 2.0677 | -1.6333 | 8.3644 | 8.1648 | 7.9437 | 7.59 | 7.2628 | 6.9137 | 6.5185 | 6.1513 | 5.7075 | 5.2519 | 4.2206 | 1.1429 | -2.0578 | -5.5037
|  | HARESTOCK | FS |  |  | 7.6469 | 7.3248 | 6.9825 | 6.3737 | 5.7073 | 4.9237 | 4.0581 | 3.0948 | 1.6339 | 0.11927 | -2.9241 | -9.4991 | -13.6507 | -16.0448 | 11.4318 | 11.2652 | 11.0864 | 10.8743 | 10.6496 | 10.4034 | 10.1371 | 9.8592 | 9.5255 | 9.1798 | 8.4078 | 6.178 | 3.5044 | -0.22978 | 8.381 | 8.2129 | 8.0397 | 7.7844 | 7.5208 | 7.2406 | 6.9442 | 6.644 | 6.221 | 5.7968 | 4.8908 | 2.3565 | -0.31114 | -3.1631
EALING GSP | EALING (D) | HARVARD LANE | MINIMUM HEADROOM | TQ 20021 78030 | YES | -1.2648 | -1.8574 | 8.3517 | 7.363 | 6.2231 | 5.0153 | 3.293 | 1.3813 | -0.59621 | -2.7667 | -7.4008 | -15.2475 | -18.7773 | -20.5659 | 2.4511 | 1.8593 | 11.3456 | 10.3889 | 9.2641 | 7.9509 | 6.3367 | 4.4384 | 2.3032 | -0.10517 | -5.9254 | -26.8837 | -60.5635 | -118.1424 | -0.61893 | -1.2001 | 8.4169 | 7.4636 | 6.3642 | 5.2147 | 3.5843 | 1.7503 | -0.14139 | -2.225 | -6.6835 | -14.1645 | -21.1343 | -26.9789
|  | HARVARD LANE | CT |  |  | -1.0009 | -1.3797 | 8.9652 | 8.1174 | 7.216 | 6.0147 | 4.7013 | 2.9841 | 0.89052 | -1.1586 | -5.0183 | -14.2355 | -18.7773 | -20.5659 | 2.4511 | 1.8602 | 11.3629 | 10.4263 | 9.394 | 8.0502 | 6.5438 | 4.6356 | 2.4446 | 0.2144 | -4.3223 | -18.2508 | -35.7639 | -64.6536 | -0.34997 | -0.71678 | 9.0231 | 8.2513 | 7.3921 | 6.2375 | 4.9628 | 3.2932 | 1.2632 | -0.71258 | -4.3654 | -13.0987 | -17.2732 | -18.8615
|  | HARVARD LANE | LW |  |  | -1.2648 | -1.8574 | 8.3517 | 7.363 | 6.2231 | 5.0153 | 3.293 | 1.3813 | -0.59621 | -2.7667 | -7.4008 | -15.2475 | -17.1415 | -15.8745 | 2.6435 | 2.2354 | 12.0501 | 11.4602 | 10.7537 | 10.0019 | 8.8522 | 7.5269 | 6.1439 | 4.597 | 1.2201 | -4.26 | -5.3052 | -3.9171 | -0.61893 | -1.2001 | 8.4169 | 7.4636 | 6.3642 | 5.2147 | 3.5843 | 1.7503 | -0.14139 | -2.225 | -6.6835 | -14.1645 | -15.8499 | -14.4474
|  | HARVARD LANE | ST |  |  | -0.75475 | -0.91043 | 9.6797 | 9.3078 | 8.8951 | 8.3817 | 7.7264 | 7.0031 | 6.1963 | 5.2037 | 2.6173 | -6.0285 | -12.1841 | -15.012 | 2.6239 | 2.1997 | 11.8876 | 11.1795 | 10.3875 | 9.4454 | 8.3087 | 7.0488 | 5.6766 | 4.0707 | 0.065893 | -14.4157 | -33.2828 | -62.1378 | -0.11107 | -0.25624 | 9.7283 | 9.3693 | 8.9696 | 8.465 | 7.8062 | 7.0733 | 6.2631 | 5.2649 | 2.6633 | -5.949 | -11.9121 | -14.3704
|  | HARVARD LANE | FS |  |  | -1.0009 | -1.3797 | 8.9652 | 8.1174 | 7.216 | 6.0147 | 4.7013 | 2.9841 | 0.89052 | -1.1586 | -5.0183 | -14.2355 | -18.7773 | -20.5659 | 2.4911 | 1.8593 | 11.3456 | 10.3889 | 9.2641 | 7.9509 | 6.3367 | 4.4384 | 2.3032 | -0.10517 | -5.9254 | -26.8837 | -60.5635 | -118.1424 | -0.23097 | -0.531 | 9.3256 | 8.8538 | 8.2798 | 7.5754 | 6.6533 | 5.5197 | 4.2088 | 2.7601 | -0.64657 | -11.0308 | -21.1343 | -26.9789
BRAMLEY (FLEE) | FERNHURST | HASLEMERE | MINIMUM HEADROOM | SU 89300 31710 | YES | 2.0593 | 1.1961 | 0.29671 | -0.80449 | -2.2191 | -3.7587 | -6.5462 | -11.2201 | -17.0945 | -24.3061 | -42.1523 | -78.5094 | -98.3792 | -109.7873 | 5.753 | 5.2152 | 4.6544 | 3.9748 | 3.0674 | 2.0222 | -0.63483 | -4.2002 | -8.6769 | -14.2064 | -27.9577 | -55.8959 | -71.2123 | -80.2548 | 2.4137 | 1.6377 | 0.82526 | -0.19692 | -1.5361 | -3.0079 | -5.3433 | -8.6543 | -14.2796 | -21.1906 | -38.3021 | -73.1344 | -92.2094 | -103.2417
|  | HASLEMERE | CT |  |  | 2.378 | 1.7806 | 1.0711 | 0.14882 | -0.85738 | -2.3227 | -3.9129 | -6.228 | -9.2617 | -12.2082 | -17.6793 | -31.0834 | -37.4388 | -39.906 | 5.8449 | 5.4141 | 4.8997 | 4.285 | 3.556 | 2.441 | 1.2125 | -0.60293 | -2.8405 | -5.0474 | -9.1954 | -19.2999 | -24.2944 | -27.8712 | 2.7318 | 2.2123 | 1.5345 | 0.64855 | -0.31898 | -1.7425 | -3.2923 | -5.562 | -8.507 | -11.3715 | -16.6795 | -29.6038 | -35.5988 | -37.9104
|  | HASLEMERE | LW |  |  | 2.0593 | 1.1961 | 0.29671 | -0.80449 | -2.2191 | -3.7587 | -6.5462 | -11.2201 | -17.0945 | -24.3061 | -42.1523 | -78.5094 | -98.3792 | -109.7873 | 5.753 | 5.2152 | 4.6544 | 3.9748 | 3.0674 | 2.0222 | -0.63483 | -4.2002 | -8.6769 | -14.2064 | -27.9577 | -55.8959 | -71.2123 | -80.2548 | 2.4137 | 1.6377 | 0.82526 | -0.19692 | -1.5361 | -3.0079 | -5.3433 | -8.6543 | -14.2796 | -21.1906 | -38.3021 | -73.1344 | -92.2094 | -103.2417
|  | HASLEMERE | ST |  |  | 2.7607 | 2.522 | 2.2022 | 1.7891 | 1.2737 | 0.61996 | -0.235 | -1.282 | -2.5094 | -4.0391 | -8.2584 | -22.2742 | -32.0885 | -35.9454 | 6.089 | 5.8954 | 5.6422 | 5.2947 | 4.8795 | 4.3604 | 3.6506 | 2.753 | 1.7085 | 0.42814 | -3.1164 | -14.9471 | -23.4568 | -27.7694 | 3.0733 | 2.8704 | 2.5986 | 2.2186 | 1.7121 | 1.0644 | 0.21384 | -0.82209 | -2.0428 | -3.5476 | -7.6375 | -21.6927 | -31.361 | -35.0329
|  | HASLEMERE | FS |  |  | 2.378 | 1.7806 | 1.0711 | 0.14882 | -0.85738 | -2.3227 | -3.9129 | -6.228 | -9.2617 | -12.2082 | -17.6793 | -31.0834 | -37.4388 | -39.906 | 5.9372 | 5.595 | 5.1875 | 4.719 | 4.1085 | 3.2815 | 2.1853 | 0.75238 | -0.91312 | -2.8249 | -7.3999 | -21.2424 | -33.9039 | -42.2024 | 2.9009 | 2.5367 | 2.0504 | 1.442 | 0.68447 | -0.28655 | -1.5754 | -3.2675 | -5.2583 | -7.4634 | -12.8834 | -29.3581 | -43.6354 | -50.8386
BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE | MINIMUM HEADROOM | SU 98188 20276 | YES | 2.2003 | 14.0986 | 13.6659 | 13.1904 | 12.5773 | 11.92 | 10.8487 | 9.5195 | 8.0195 | 6.3157 | 2.4286 | -11.836 | -19.5865 | -18.7565 | 4.4954 | 15.9763 | 15.6967 | 15.3735 | 14.9398 | 14.4688 | 13.664 | 12.6544 | 11.527 | 10.2349 | 7.2705 | -4.8495 | -10.7943 | -10.8536 | 3.0246 | 14.3833 | 13.972 | 13.5143 | 12.9199 | 12.2808 | 11.2296 | 9.9237 | 8.4558 | 6.7862 | 2.9763 | -11.5425 | -18.955 | -18.1643
|  | HASLINGBOURNE | CT |  |  | 2.3175 | 14.3301 | 13.9646 | 13.5261 | 13.0472 | 12.3392 | 11.5775 | 10.4303 | 9.0251 | 7.6686 | 5.1665 | -0.7201 | -3.2615 | -4.1052 | 4.5256 | 16.0548 | 15.7839 | 15.4695 | 15.1235 | 14.5963 | 14.0221 | 13.149 | 12.1038 | 11.1023 | 9.2274 | 4.7994 | 2.8464 | 1.8455 | 3.1237 | 14.5764 | 14.2208 | 13.7967 | 13.3325 | 12.6397 | 11.8921 | 10.7617 | 9.3842 | 8.0672 | 5.6436 | -0.098263 | -2.5249 | -3.3127
|  | HASLINGBOURNE | LW |  |  | 2.2003 | 14.0986 | 13.6659 | 13.1904 | 12.5773 | 11.92 | 10.8487 | 9.5195 | 8.0195 | 6.3157 | 2.4286 | -11.836 | -19.5865 | -18.7565 | 4.4954 | 15.9763 | 15.6967 | 15.3735 | 14.9398 | 14.4688 | 13.664 | 12.6544 | 11.527 | 10.2349 | 7.2705 | -4.8495 | -10.7943 | -10.0824 | 3.0246 | 14.3833 | 13.972 | 13.5143 | 12.9199 | 12.2808 | 11.2296 | 9.9237 | 8.4558 | 6.7862 | 2.9763 | -11.5425 | -18.955 | -18.1325
|  | HASLINGBOURNE | ST |  |  | 2.5284 | 14.7316 | 14.5719 | 14.3375 | 14.0488 | 13.689 | 13.2289 | 12.659 | 12.0096 | 11.2075 | 9.0163 | 2.0593 | -2.4086 | -3.7426 | 4.6696 | 16.3362 | 16.216 | 16.0379 | 15.8187 | 15.5423 | 15.1846 | 14.7438 | 14.2457 | 13.6262 | 11.944 | 6.4999 | 2.8944 | 1.6148 | 3.3269 | 14.9657 | 14.8119 | 14.5823 | 14.2999 | 13.9467 | 13.4928 | 12.9315 | 12.2927 | 11.5017 | 9.3606 | 2.5193 | -1.8662 | -3.118
|  | HASLINGBOURNE | FS |  |  | 2.3175 | 14.3301 | 13.9646 | 13.5261 | 13.0472 | 12.3392 | 11.5775 | 10.4303 | 9.0251 | 7.6686 | 5.1665 | -0.7201 | -3.2615 | -4.1052 | 4.6009 | 16.2319 | 16.0664 | 15.839 | 15.5513 | 15.1864 | 14.7246 | 14.1469 | 13.4967 | 12.7085 | 10.495 | 2.2192 | -6.213 | -10.8536 | 3.2497 | 14.8495 | 14.6461 | 14.3483 | 13.9759 | 13.5073 | 12.918 | 12.1826 | 11.3476 | 10.3386 | 7.5601 | -2.8296 | -13.0321 | -18.1643
MELKSHAM GSP | FROME BSP | HAWKERIDGE | MINIMUM HEADROOM | ST 86422 53026 | YES | 1.4679 | 1.2712 | 1.0369 | 0.69918 | -0.20427 | -1.6687 | -3.4248 | -6.0668 | -8.9154 | -12.1238 | -19.1222 | -30.3583 | -33.5491 | -35.3797 | 1.5236 | 1.4191 | 1.2946 | 1.059 | 0.5922 | -0.088572 | -1.5453 | -3.7119 | -6.0194 | -8.6189 | -14.4189 | -23.6717 | -26.1283 | -29.318 | 0.78955 | 0.66051 | 0.50675 | 0.28626 | -0.20819 | -1.6717 | -3.5017 | -6.1579 | -9.006 | -12.2134 | -19.3223 | -30.7254 | -33.8113 | -37.8464
|  | HAWKERIDGE | CT |  |  | 1.4679 | 1.2712 | 1.0369 | 0.69918 | -0.20427 | -1.6687 | -3.2836 | -5.816 | -8.8031 | -11.6604 | -16.8205 | -28.8497 | -33.0269 | -34.1614 | 1.5236 | 1.4191 | 1.2946 | 1.059 | 0.69451 | -0.088572 | -1.3187 | -3.3655 | -5.7692 | -8.0714 | -12.331 | -22.2001 | -25.5582 | -26.4797 | 0.78955 | 0.66051 | 0.50675 | 0.32373 | -0.20819 | -1.6717 | -3.2893 | -5.8173 | -8.7943 | -11.6443 | -16.8608 | -29.0673 | -33.2275 | -34.3542
|  | HAWKERIDGE | LW |  |  | 1.4938 | 1.2799 | 1.067 | 0.75592 | -0.16955 | -1.3139 | -3.4248 | -6.0668 | -8.9154 | -12.1238 | -19.1222 | -30.3583 | -32.0303 | -27.8792 | 1.541 | 1.4253 | 1.3144 | 1.0798 | 0.5922 | 0.035053 | -1.5453 | -3.7119 | -6.0194 | -8.6189 | -14.4189 | -23.6717 | -25.0223 | -21.6722 | 0.811 | 0.66806 | 0.53112 | 0.28626 | -0.20297 | -1.3695 | -3.5017 | -6.1579 | -9.006 | -12.2134 | -19.3223 | -30.7254 | -32.3985 | -28.2591
|  | HAWKERIDGE | ST |  |  | 1.5954 | 1.53 | 1.4393 | 1.2454 | 1.0329 | 0.77102 | 0.10062 | -1.0693 | -2.4072 | -4.0938 | -8.7793 | -23.9107 | -33.5491 | -35.3797 | 1.5944 | 1.5604 | 1.5137 | 1.3579 | 1.2088 | 1.0369 | 0.6327 | 0.15385 | -0.73071 | -2.0793 | -5.8712 | -18.3609 | -26.1283 | -27.5971 | 0.87703 | 0.83503 | 0.77735 | 0.60635 | 0.43677 | 0.23747 | -0.036127 | -1.131 | -2.4691 | -4.1539 | -8.8321 | -24.205 | -33.8113 | -35.6281
|  | HAWKERIDGE | FS |  |  | 1.4679 | 1.2712 | 1.0369 | 0.69918 | -0.20427 | -1.6687 | -3.2836 | -5.816 | -8.8031 | -11.6604 | -16.8205 | -28.8497 | -33.0269 | -34.1614 | 1.5957 | 1.5655 | 1.5244 | 1.4493 | 1.3564 | 1.2369 | 1.0892 | 0.76452 | 0.40325 | -0.24334 | -2.6271 | -12.1742 | -23.2718 | -29.318 | 0.87871 | 0.84141 | 0.79077 | 0.70279 | 0.59284 | 0.45104 | 0.27447 | 0.060027 | -0.76815 | -1.8443 | -4.8892 | -16.6484 | -30.3772 | -37.8464
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY | MINIMUM HEADROOM | SU 85973 57691 | YES | 11.5629 | 11.1506 | 10.7983 | 10.0812 | 9.1527 | 8.2671 | 7.0861 | 5.7189 | 4.2001 | 2.545 | -0.97013 | -7.2433 | -9.581 | -10.957 | 14.7313 | 14.4754 | 14.2498 | 13.8505 | 13.264 | 12.7041 | 11.9086 | 10.9781 | 9.9881 | 8.8894 | 6.5214 | 1.5466 | -6.1274 | -15.1318 | 12.1312 | 11.7439 | 11.4002 | 10.7364 | 9.8618 | 9.0135 | 7.865 | 6.5473 | 5.0997 | 3.5163 | 0.14299 | -5.7834 | -7.7767 | -10.9536
|  | HAWLEY | CT |  |  | 11.8424 | 11.6127 | 11.3668 | 10.8134 | 10.0371 | 9.2547 | 8.4029 | 7.278 | 5.6858 | 4.126 | 1.1494 | -6.0684 | -9.581 | -10.957 | 14.7806 | 14.5658 | 14.3368 | 13.9736 | 13.4107 | 12.8542 | 12.2339 | 11.3875 | 10.2905 | 9.2073 | 7.1132 | 1.8664 | -1.6484 | -5.3254 | 12.3492 | 12.1152 | 11.8736 | 11.3573 | 10.6326 | 9.8891 | 9.0753 | 7.9897 | 6.4811 | 5.0037 | 2.1884 | -4.5803 | -7.7767 | -8.9938
|  | HAWLEY | LW |  |  | 11.5629 | 11.1506 | 10.7983 | 10.0812 | 9.1527 | 8.2671 | 7.0861 | 5.7189 | 4.2001 | 2.545 | -0.97013 | -7.2433 | -9.0468 | -8.2664 | 14.7313 | 14.4754 | 14.2498 | 13.8505 | 13.264 | 12.7041 | 11.9086 | 10.9781 | 9.9881 | 8.8894 | 6.5214 | 2.5778 | 1.7007 | 2.4894 | 12.1312 | 11.7439 | 11.4002 | 10.7364 | 9.8618 | 9.0135 | 7.865 | 6.5473 | 5.0997 | 3.5163 | 0.14299 | -5.7834 | -7.392 | -6.5388
|  | HAWLEY | ST |  |  | 12.0102 | 11.9179 | 11.8585 | 11.7161 | 11.3498 | 11.1215 | 10.8078 | 10.4428 | 10.038 | 9.5297 | 8.1274 | 2.72 | -1.6298 | -4.2406 | 14.9012 | 14.7975 | 14.6966 | 14.5106 | 14.1411 | 13.8908 | 13.5619 | 13.1936 | 12.7809 | 12.2737 | 10.9079 | 6.0013 | 1.4794 | -2.7601 | 12.5198 | 12.4324 | 12.3609 | 12.199 | 11.8428 | 11.6108 | 11.2917 | 10.9255 | 10.5249 | 10.0207 | 8.6258 | 3.3563 | -0.76463 | -3.0936
|  | HAWLEY | FS |  |  | 11.8424 | 11.6127 | 11.3668 | 10.8134 | 10.0371 | 9.2547 | 8.4029 | 7.278 | 5.6858 | 4.126 | 1.1494 | -6.0684 | -9.581 | -10.957 | 14.8028 | 14.6039 | 14.3989 | 14.1358 | 13.7602 | 13.3436 | 12.7968 | 12.0962 | 11.248 | 10.3159 | 8.1635 | 1.5466 | -6.1274 | -15.1318 | 12.3992 | 12.2041 | 12.0137 | 11.7395 | 11.348 | 10.9073 | 10.318 | 9.5471 | 8.6227 | 7.6202 | 5.3505 | -1.2877 | -7.289 | -10.9536
COWLEY GSP | HEADINGTON BSP | HEADINGTON | MINIMUM HEADROOM | SP 54440 08085 | NO | 19.7696 | 19.4919 | 19.1597 | 18.5315 | 17.9157 | 17.2742 | 15.4752 | 13.3851 | 11.1181 | 8.6672 | 4.4183 | -3.2207 | -5.8757 | -6.9589 | 19.3669 | 19.098 | 18.8216 | 18.2698 | 17.7299 | 16.8919 | 15.6725 | 14.2801 | 12.8207 | 11.0706 | 7.9823 | 0.69144 | -8.1307 | -22.0958 | 18.5007 | 17.9682 | 17.3276 | 16.1313 | 14.8335 | 13.4708 | 11.7165 | 9.7232 | 7.6065 | 5.3315 | 1.237 | -6.1306 | -8.4367 | -9.7664
|  | HEADINGTON | CT |  |  | 19.7922 | 19.5334 | 19.271 | 18.7389 | 18.329 | 17.8583 | 17.136 | 15.1822 | 12.6917 | 10.1854 | 6.1436 | -2.5197 | -5.8757 | -6.9589 | 19.3842 | 19.1243 | 18.9161 | 18.4603 | 17.9208 | 16.9753 | 15.9341 | 14.5406 | 12.8207 | 11.0706 | 7.9823 | 0.69144 | -4.2283 | -10.107 | 18.6753 | 18.2546 | 17.7294 | 16.685 | 15.6635 | 14.4437 | 13.1186 | 11.3332 | 9.0541 | 6.7425 | 2.9103 | -5.3161 | -8.4367 | -9.4146
|  | HEADINGTON | LW |  |  | 19.7696 | 19.4919 | 19.1597 | 18.5315 | 17.9157 | 17.2742 | 15.4752 | 13.3851 | 11.1181 | 8.6672 | 4.4183 | -3.2207 | -5.6358 | -4.6675 | 19.3669 | 19.098 | 18.8216 | 18.2698 | 17.7299 | 16.8919 | 15.6725 | 14.2801 | 12.8264 | 11.2425 | 8.2618 | 2.9754 | 1.4136 | 0.74546 | 18.5007 | 17.9682 | 17.3276 | 16.1313 | 14.8335 | 13.4708 | 11.7165 | 9.7232 | 7.6065 | 5.3315 | 1.237 | -6.1306 | -8.4252 | -7.4294
|  | HEADINGTON | ST |  |  | 19.8808 | 19.7023 | 19.5269 | 19.0219 | 18.6758 | 18.3507 | 17.9827 | 17.591 | 17.14 | 16.6327 | 15.4648 | 8.5732 | 3.8114 | 1.5298 | 19.4649 | 19.2797 | 19.1642 | 18.7164 | 18.4493 | 18.1797 | 17.744 | 17.0555 | 16.265 | 15.344 | 13.2949 | 6.4624 | 0.15873 | -6.3274 | 18.9102 | 18.7009 | 18.412 | 17.7481 | 17.193 | 16.6345 | 15.9803 | 15.2392 | 14.3996 | 13.4145 | 11.3251 | 4.4852 | -0.14583 | -2.1248
|  | HEADINGTON | FS |  |  | 19.7922 | 19.5334 | 19.271 | 18.7389 | 18.329 | 17.8583 | 17.136 | 15.1822 | 12.6917 | 10.1854 | 6.1436 | -2.5197 | -5.8757 | -6.9589 | 19.4901 | 19.3583 | 19.2065 | 18.9153 | 18.6585 | 18.1476 | 17.4153 | 16.5426 | 15.5114 | 14.3604 | 11.7593 | 2.9841 | -8.1307 | -22.0958 | 18.8664 | 18.6391 | 18.2968 | 17.7144 | 17.1162 | 16.4613 | 15.6933 | 14.7674 | 13.706 | 12.5352 | 10.0066 | 1.9956 | -5.5736 | -9.7664
NURSLING GSP | VELMORE BSP | HEDGE END | MINIMUM HEADROOM | SU 49035 15685 | YES | 3.7566 | 2.0618 | 0.32192 | -1.7067 | -4.2774 | -6.914 | -11.0163 | -15.9 | -21.2917 | -27.4331 | -40.8053 | -62.1853 | -70.6612 | -73.5194 | 6.0133 | 4.9082 | 3.573 | 2.0747 | 0.443 | -2.0075 | -4.6655 | -8.6538 | -13.4123 | -17.9777 | -28.6199 | -45.7416 | -53.6504 | -66.4443 | 4.1722 | 2.6523 | 1.0484 | -0.83321 | -3.2211 | -6.004 | -9.7573 | -14.6682 | -20.0992 | -26.2852 | -39.7999 | -60.9594 | -69.3623 | -79.1485
|  | HEDGE END | CT |  |  | 3.7566 | 2.2499 | 0.49404 | -1.5493 | -3.7718 | -6.914 | -10.2948 | -15.1555 | -21.0855 | -26.7647 | -37.125 | -61.4374 | -70.6612 | -73.5194 | 6.0133 | 4.9082 | 3.573 | 2.0747 | 0.443 | -2.0075 | -4.6655 | -8.6538 | -13.4123 | -17.9777 | -26.282 | -45.7416 | -53.6504 | -57.3054 | 4.1722 | 2.7565 | 1.0918 | -0.83321 | -2.9349 | -6.004 | -9.3212 | -14.1777 | -20.0992 | -25.8307 | -36.2086 | -60.2604 | -69.3623 | -72.1912
|  | HEDGE END | LW |  |  | 3.7905 | 2.0618 | 0.32192 | -1.7067 | -4.2774 | -6.8182 | -11.0163 | -15.9 | -21.2917 | -27.4331 | -40.8053 | -62.1853 | -66.123 | -59.7009 | 6.1451 | 4.9283 | 3.7282 | 2.3564 | 0.53931 | -1.2887 | -4.5474 | -8.5225 | -12.9204 | -17.8634 | -28.6199 | -45.3858 | -48.4072 | -43.3135 | 4.2722 | 2.6523 | 1.0484 | -0.80951 | -3.2211 | -5.6317 | -9.7573 | -14.6682 | -20.0935 | -26.2852 | -39.7999 | -60.9594 | -64.8651 | -58.5334
|  | HEDGE END | ST |  |  | 4.3906 | 3.633 | 2.7021 | 1.577 | 0.24239 | -1.3062 | -3.2091 | -5.4253 | -7.9807 | -11.1897 | -19.9766 | -48.5608 | -66.932 | -71.547 | 6.5649 | 6.0327 | 5.3826 | 4.5947 | 3.6284 | 2.4376 | 0.90214 | -0.96718 | -3.1488 | -5.8648 | -13.239 | -36.7101 | -52.196 | -57.169 | 4.885 | 4.1954 | 3.3535 | 2.3338 | 1.0918 | -0.3959 | -2.2571 | -4.4849 | -7.0708 | -10.2902 | -19.207 | -47.8016 | -66.0978 | -70.6708
|  | HEDGE END | FS |  |  | 3.7566 | 2.2499 | 0.49404 | -1.5493 | -3.7718 | -6.914 | -10.2948 | -15.1555 | -21.0855 | -26.7647 | -37.125 | -61.4374 | -70.6612 | -73.5194 | 6.6064 | 6.1038 | 5.5058 | 4.7881 | 3.9329 | 2.9265 | 1.7046 | 0.22724 | -1.4324 | -3.4127 | -8.8598 | -28.9563 | -51.7402 | -66.4443 | 4.9473 | 4.3225 | 3.5816 | 2.6746 | 1.6022 | 0.35102 | -1.1594 | -2.9139 | -4.8854 | -7.2319 | -13.6707 | -37.6898 | -64.2928 | -79.1485
BRAMLEY (FLEE) | READING BSP | HENLEY | MINIMUM HEADROOM | SU 76070 82422 | YES | 11.5551 | 11.023 | 10.4187 | 9.3855 | 8.042 | 6.583 | 4.5744 | 2.1863 | -0.49001 | -3.4145 | -9.8153 | -22.6387 | -31.9676 | -35.1591 | 14.3336 | 13.9905 | 13.6123 | 13.0321 | 12.2536 | 11.4059 | 10.1241 | 8.5656 | 6.837 | 4.9098 | 0.64847 | -10.0462 | -16.9717 | -22.6316 | 11.1928 | 10.6921 | 10.1352 | 9.2134 | 8.0116 | 6.702 | 4.8509 | 2.6322 | 0.14645 | -2.5841 | -8.5758 | -21.3679 | -30.2307 | -33.2353
|  | HENLEY | CT |  |  | 11.8019 | 11.458 | 10.9851 | 10.1212 | 9.0956 | 7.7583 | 6.344 | 4.4125 | 1.8865 | -0.62272 | -5.463 | -14.8369 | -19.6356 | -21.761 | 14.3475 | 14.0351 | 13.631 | 13.0563 | 12.3859 | 11.4658 | 10.4763 | 9.0802 | 7.3723 | 5.6861 | 2.4467 | -4.6626 | -9.236 | -13.7657 | 11.4088 | 11.0738 | 10.6285 | 9.8543 | 8.9429 | 7.7258 | 6.4287 | 4.6295 | 2.2887 | -0.024858 | -4.4602 | -13.3038 | -17.6851 | -19.5548
|  | HENLEY | LW |  |  | 11.5551 | 11.023 | 10.4187 | 9.3855 | 8.042 | 6.583 | 4.5744 | 2.1863 | -0.49001 | -3.4145 | -9.8153 | -22.6387 | -31.9676 | -35.1591 | 14.3336 | 13.9905 | 13.6123 | 13.0321 | 12.2536 | 11.4059 | 10.1241 | 8.5656 | 6.837 | 4.9098 | 0.64847 | -10.0462 | -16.9717 | -19.3242 | 11.1928 | 10.6921 | 10.1352 | 9.2134 | 8.0116 | 6.702 | 4.8509 | 2.6322 | 0.14645 | -2.5841 | -8.5758 | -21.3679 | -30.2307 | -33.2353
|  | HENLEY | ST |  |  | 12.0697 | 11.9554 | 11.7409 | 11.3053 | 10.7378 | 10.084 | 9.3243 | 8.4184 | 7.3835 | 6.1256 | 2.8885 | -6.0416 | -12.334 | -15.3377 | 14.5274 | 14.3864 | 14.1748 | 13.8244 | 13.3835 | 12.8616 | 12.2377 | 11.4928 | 10.6534 | 9.6322 | 6.9661 | -1.0155 | -7.3948 | -12.3905 | 11.6654 | 11.5543 | 11.3606 | 10.98 | 10.4879 | 9.9104 | 9.2218 | 8.3962 | 7.4527 | 6.2967 | 3.279 | -5.6085 | -11.7142 | -14.3034
|  | HENLEY | FS |  |  | 11.8019 | 11.458 | 10.9851 | 10.1212 | 9.0956 | 7.7583 | 6.344 | 4.4125 | 1.8865 | -0.62272 | -5.463 | -14.8369 | -19.6356 | -21.761 | 14.4912 | 14.3181 | 14.0789 | 13.7222 | 13.2675 | 12.7272 | 12.0681 | 11.2754 | 10.3704 | 9.3375 | 6.7152 | -1.934 | -12.1856 | -22.6316 | 11.6287 | 11.494 | 11.288 | 10.9129 | 10.4226 | 9.842 | 9.1342 | 8.2859 | 7.2791 | 6.1453 | 3.2865 | -5.6763 | -14.6986 | -20.2212
AXMINSTER | YEOVIL BSP | HENSTRIDGE | MINIMUM HEADROOM | ST 72676 19263 | YES | 13.1597 | 12.6155 | 12.0273 | 11.4362 | 10.7514 | 10.0041 | 8.4376 | 6.4899 | 4.3839 | 2.0472 | -2.885 | -10.7323 | -14.2525 | -15.3968 | 13.9117 | 13.7533 | 13.5885 | 13.4201 | 13.196 | 12.6495 | 11.6708 | 10.1453 | 8.3737 | 6.6712 | 2.8545 | -3.4049 | -6.0199 | -9.8368 | 11.7338 | 11.1745 | 10.5869 | 9.9483 | 9.1563 | 8.3086 | 6.8523 | 4.9674 | 2.926 | 0.65509 | -4.1706 | -11.8504 | -15.2277 | -18.6433
|  | HENSTRIDGE | CT |  |  | 13.2823 | 12.8482 | 12.3086 | 11.696 | 11.0801 | 10.0128 | 8.7058 | 6.7475 | 4.4441 | 2.2217 | -1.8393 | -10.7323 | -14.2525 | -15.3968 | 13.9388 | 13.7987 | 13.6263 | 13.4201 | 13.196 | 12.6495 | 11.6708 | 10.1453 | 8.3737 | 6.6712 | 3.5607 | -3.4049 | -6.0199 | -7.0065 | 11.8197 | 11.3572 | 10.7628 | 10.0781 | 9.368 | 8.3086 | 7.0559 | 5.1594 | 2.926 | 0.77255 | -3.1694 | -11.8504 | -15.2277 | -16.3048
|  | HENSTRIDGE | LW |  |  | 13.1597 | 12.6155 | 12.0273 | 11.4362 | 10.7514 | 10.0041 | 8.4376 | 6.4899 | 4.3839 | 2.0472 | -2.885 | -10.7059 | -12.2901 | -9.978 | 13.9117 | 13.7533 | 13.5885 | 13.4303 | 13.2621 | 12.9146 | 11.734 | 10.2272 | 8.6021 | 6.7795 | 2.8545 | -3.3388 | -4.3827 | -2.2692 | 11.7338 | 11.1745 | 10.5869 | 9.9483 | 9.1563 | 8.3591 | 6.8523 | 4.9674 | 2.9261 | 0.65509 | -4.1706 | -11.8328 | -13.3278 | -10.9813
|  | HENSTRIDGE | ST |  |  | 13.5395 | 13.3469 | 13.0898 | 12.7636 | 12.416 | 12.0067 | 11.4007 | 10.4631 | 9.4182 | 8.1344 | 4.7904 | -5.6167 | -12.2905 | -13.9549 | 14.0343 | 13.9704 | 13.8877 | 13.7954 | 13.7073 | 13.6102 | 13.458 | 12.9413 | 12.1134 | 11.0838 | 8.3283 | -0.20662 | -5.5308 | -6.8854 | 12.0622 | 11.9084 | 11.6408 | 11.3142 | 10.9169 | 10.4126 | 9.699 | 8.78 | 7.7728 | 6.5279 | 3.2489 | -6.813 | -13.3674 | -14.9569
|  | HENSTRIDGE | FS |  |  | 13.2823 | 12.8482 | 12.3086 | 11.696 | 11.0801 | 10.0128 | 8.7058 | 6.7475 | 4.4441 | 2.2217 | -1.8393 | -10.7323 | -14.2525 | -15.3968 | 14.0137 | 13.9328 | 13.8223 | 13.6778 | 13.5123 | 13.3001 | 13.001 | 12.6039 | 12.1359 | 11.5636 | 9.9009 | 2.5243 | -5.3834 | -9.8368 | 12.0306 | 11.9142 | 11.7145 | 11.4082 | 11.0647 | 10.6148 | 10.0167 | 9.2698 | 8.4362 | 7.4655 | 4.9371 | -4.0789 | -13.4736 | -18.6433
BRAMLEY (FLEE) | ALTON | HERRIARD | MINIMUM HEADROOM | SU 66770 44972 | YES | 5.6214 | 5.5094 | 5.4027 | 5.2679 | 5.1142 | 4.8858 | 4.6249 | 4.24 | 3.7743 | 3.3028 | 2.3711 | 0.28196 | -1.9318 | -2.613 | 5.9088 | 5.7241 | 5.3656 | 4.8253 | 4.0229 | 2.8432 | 1.1613 | -1.1644 | -4.1319 | -7.8458 | -17.0546 | -32.8916 | -37.0802 | -40.1124 | 5.5961 | 5.3212 | 4.8825 | 4.2162 | 3.2291 | 1.7807 | -0.27993 | -3.1263 | -6.7607 | -11.3058 | -22.5712 | -41.9746 | -47.122 | -50.8433
|  | HERRIARD | CT |  |  | 5.6244 | 5.5213 | 5.4038 | 5.2679 | 5.1142 | 4.8858 | 4.6249 | 4.24 | 3.7743 | 3.3028 | 2.3711 | 0.28196 | -1.9318 | -2.613 | 5.9154 | 5.8402 | 5.7507 | 5.6479 | 5.5304 | 5.3501 | 5.1442 | 4.835 | 4.4625 | 4.086 | 3.3475 | 1.6908 | 0.23598 | -0.28948 | 5.7811 | 5.7098 | 5.605 | 5.4838 | 5.347 | 5.1465 | 4.9055 | 4.5316 | 4.0791 | 3.6151 | 2.6907 | 0.6328 | -1.5571 | -2.2093
|  | HERRIARD | LW |  |  | 5.6214 | 5.5094 | 5.4027 | 5.3012 | 5.1683 | 5.0237 | 4.7748 | 4.4568 | 4.1183 | 3.7316 | 2.8917 | 1.562 | 1.3269 | 1.7661 | 5.9292 | 5.8555 | 5.7848 | 5.7119 | 5.6117 | 5.5054 | 5.3095 | 5.0593 | 4.7882 | 4.4807 | 3.8147 | 2.7872 | 2.6265 | 2.9902 | 5.7793 | 5.6921 | 5.5943 | 5.5039 | 5.3876 | 5.2597 | 5.0452 | 4.746 | 4.4185 | 4.0444 | 3.2089 | 1.8964 | 1.6702 | 2.1109
|  | HERRIARD | ST |  |  | 5.6736 | 5.6253 | 5.5695 | 5.4869 | 5.3864 | 5.2559 | 5.0959 | 4.895 | 4.655 | 4.3628 | 3.5786 | 1.3204 | -0.041317 | -0.33113 | 5.9531 | 5.9201 | 5.8786 | 5.8207 | 5.7463 | 5.6482 | 5.523 | 5.3635 | 5.1742 | 4.9399 | 4.3076 | 2.5038 | 1.4043 | 1.1298 | 5.8025 | 5.7837 | 5.7521 | 5.6771 | 5.5875 | 5.4721 | 5.3329 | 5.1594 | 4.9394 | 4.6573 | 3.8854 | 1.6475 | 0.30127 | 0.020421
|  | HERRIARD | FS |  |  | 5.6244 | 5.5213 | 5.4038 | 5.2679 | 5.1142 | 4.8858 | 4.6249 | 4.24 | 3.7743 | 3.3028 | 2.3711 | 0.28196 | -1.9318 | -2.613 | 5.9088 | 5.7241 | 5.3656 | 4.8253 | 4.0229 | 2.8432 | 1.1613 | -1.1644 | -4.1319 | -7.8458 | -17.0546 | -32.8916 | -37.0802 | -40.1124 | 5.5961 | 5.3212 | 4.8825 | 4.2162 | 3.2291 | 1.7807 | -0.27993 | -3.1263 | -6.7607 | -11.3058 | -22.5712 | -41.9746 | -47.122 | -50.8433
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE | MINIMUM HEADROOM | SU 84733 92200 | YES | 8.1091 | 8.0039 | 7.9276 | 7.7051 | 7.3986 | 6.9944 | 6.5486 | 6.058 | 4.852 | 3.5711 | 0.8988 | -3.6878 | -5.1949 | -6.0083 | 10.3711 | 10.2273 | 10.1244 | 10.0109 | 9.7467 | 9.4811 | 9.149 | 8.6907 | 8.1429 | 7.2533 | 4.4165 | -7.1874 | -13.6981 | -14.4091 | 7.3646 | 7.1986 | 7.0765 | 6.9384 | 6.6075 | 6.2004 | 5.7037 | 5.018 | 4.1708 | 3.1398 | -0.20687 | -13.9093 | -22.1197 | -23.2838
|  | HIGH WYCOMBE | CT |  |  | 8.1262 | 8.0576 | 7.9815 | 7.8911 | 7.6757 | 7.4563 | 6.9502 | 6.058 | 4.852 | 3.5711 | 0.8988 | -3.6878 | -5.1949 | -6.0083 | 10.3834 | 10.2797 | 10.1631 | 10.025 | 9.7467 | 9.4811 | 9.149 | 8.6907 | 8.1429 | 7.4147 | 5.5806 | 2.6014 | 1.8294 | 1.358 | 7.3729 | 7.2474 | 7.1065 | 6.9384 | 6.6075 | 6.2004 | 5.7037 | 5.018 | 4.1708 | 3.2611 | 1.2683 | -3.0095 | -4.3701 | -5.1107
|  | HIGH WYCOMBE | LW |  |  | 8.1091 | 8.0039 | 7.9276 | 7.7051 | 7.3986 | 6.9944 | 6.5486 | 6.0849 | 5.3271 | 4.4479 | 2.6293 | 0.35447 | -0.26305 | -0.41251 | 10.3711 | 10.2273 | 10.1244 | 10.0109 | 9.7929 | 9.6145 | 9.3459 | 9.0306 | 8.6965 | 8.3266 | 7.1103 | 5.7451 | 5.4891 | 5.4159 | 7.3646 | 7.1986 | 7.0765 | 6.9407 | 6.6447 | 6.3675 | 5.9462 | 5.4547 | 4.9209 | 4.3333 | 2.9562 | 0.85573 | 0.311 | 0.17913
|  | HIGH WYCOMBE | ST |  |  | 8.1801 | 8.1603 | 8.1346 | 8.0886 | 7.9267 | 7.8483 | 7.7371 | 7.6102 | 7.4668 | 7.1953 | 6.2798 | 3.3844 | 1.9709 | 1.0347 | 10.469 | 10.4406 | 10.4022 | 10.3345 | 10.1401 | 10.0263 | 9.869 | 9.6868 | 9.477 | 9.2255 | 8.6005 | 6.6906 | 6.0394 | 5.6674 | 7.4775 | 7.4443 | 7.3991 | 7.3203 | 7.1108 | 6.9783 | 6.7979 | 6.5863 | 6.3272 | 5.9675 | 5.0453 | 2.4983 | 1.7244 | 1.4049
|  | HIGH WYCOMBE | FS |  |  | 8.1262 | 8.0576 | 7.9815 | 7.8911 | 7.6757 | 7.4563 | 6.9502 | 6.058 | 4.852 | 3.5711 | 0.8988 | -3.6878 | -5.1949 | -6.0083 | 10.4274 | 10.3402 | 10.2363 | 10.0965 | 9.8621 | 9.5925 | 9.2277 | 8.7562 | 8.1576 | 7.2533 | 4.4165 | -7.1874 | -13.6981 | -14.4091 | 7.4226 | 7.3242 | 7.2026 | 7.0354 | 6.7632 | 6.4098 | 5.8784 | 5.1821 | 4.2915 | 3.1398 | -0.20687 | -13.9093 | -22.1197 | -23.2838
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN | MINIMUM HEADROOM | SU 86304 92972 | YES | 25.4421 | 25.3484 | 25.2696 | 25.1702 | 24.8481 | 24.5032 | 24.1096 | 23.6884 | 23.1879 | 22.5647 | 20.6842 | 16.9562 | 15.4612 | 14.5579 | 30.386 | 30.2979 | 30.2108 | 30.1084 | 29.9852 | 29.8092 | 29.598 | 29.3174 | 28.9852 | 28.6253 | 27.3427 | 20.9694 | 11.4774 | 5.9085 | 26.3515 | 26.1655 | 26.0134 | 25.7291 | 25.4275 | 25.1129 | 24.75 | 24.3611 | 23.9065 | 23.4332 | 22.2978 | 14.6378 | 2.8104 | -4.1265
|  | HIGH WYCOMBE TOWN | CT |  |  | 25.4421 | 25.3484 | 25.2696 | 25.1702 | 25.0057 | 24.7537 | 24.4491 | 24.0227 | 23.4767 | 22.5647 | 20.6842 | 16.9562 | 15.4612 | 14.5579 | 30.386 | 30.2979 | 30.2108 | 30.1084 | 29.9852 | 29.8092 | 29.598 | 29.3174 | 28.9852 | 28.6253 | 27.3427 | 24.6229 | 21.3563 | 16.5044 | 26.5058 | 26.4011 | 26.3172 | 26.0947 | 25.8517 | 25.5591 | 25.2366 | 24.8532 | 24.2639 | 23.6562 | 22.2978 | 18.6634 | 17.3136 | 16.4955
|  | HIGH WYCOMBE TOWN | LW |  |  | 25.4541 | 25.3542 | 25.2949 | 25.1806 | 24.8481 | 24.5032 | 24.1096 | 23.6884 | 23.1879 | 22.6682 | 21.6108 | 19.583 | 18.5869 | 18.3426 | 30.4174 | 30.3476 | 30.3018 | 30.2397 | 30.1569 | 30.065 | 29.9162 | 29.7452 | 29.5692 | 29.3741 | 28.8371 | 27.9157 | 27.8272 | 27.7613 | 26.3515 | 26.1655 | 26.0134 | 25.7291 | 25.4275 | 25.1129 | 24.75 | 24.3611 | 23.9065 | 23.4332 | 22.4692 | 20.6483 | 19.7805 | 19.5868
|  | HIGH WYCOMBE TOWN | ST |  |  | 25.5026 | 25.4575 | 25.4299 | 25.3778 | 25.3155 | 25.2371 | 25.1359 | 24.978 | 24.7877 | 24.5534 | 23.9206 | 21.694 | 20.8635 | 20.6675 | 30.433 | 30.3828 | 30.3358 | 30.2595 | 30.174 | 30.0721 | 29.9458 | 29.8074 | 29.6535 | 29.4692 | 28.9876 | 27.0988 | 23.9912 | 18.9906 | 26.6529 | 26.6387 | 26.6443 | 26.625 | 26.5966 | 26.559 | 26.4989 | 26.4035 | 26.2202 | 25.9943 | 25.2852 | 23.1692 | 22.4402 | 22.2593
|  | HIGH WYCOMBE TOWN | FS |  |  | 25.4421 | 25.3484 | 25.2696 | 25.1702 | 25.0057 | 24.7537 | 24.4491 | 24.0227 | 23.4767 | 22.5647 | 20.6842 | 16.9562 | 15.4612 | 14.5579 | 30.4057 | 30.3299 | 30.2527 | 30.1499 | 30.0228 | 29.8687 | 29.6713 | 29.4299 | 29.152 | 28.8157 | 27.8864 | 20.9694 | 11.4774 | 5.9085 | 26.6073 | 26.5512 | 26.5157 | 26.4282 | 26.3154 | 26.1907 | 26.0101 | 25.7871 | 25.4583 | 24.9079 | 23.3019 | 14.6378 | 2.8104 | -4.1265
LOVEDEAN GSP | WYMERING BSP | HILSEA | MINIMUM HEADROOM | SU 66394 03806 | YES | 13.1241 | 12.8797 | 12.5984 | 11.9173 | 11.0382 | 9.8478 | 8.2602 | 6.3723 | 4.2896 | 1.7847 | -3.9249 | -13.9034 | -16.5995 | -18.5994 | 17.3085 | 17.2205 | 17.1283 | 16.6447 | 16.022 | 14.9211 | 13.5071 | 11.9101 | 10.2642 | 8.2618 | 3.6015 | -4.7287 | -7.0913 | -8.8878 | 14.0153 | 13.9145 | 13.8075 | 13.2989 | 12.6944 | 11.8831 | 10.5458 | 8.6159 | 6.5528 | 4.082 | -1.5158 | -11.4162 | -14.161 | -16.2216
|  | HILSEA | CT |  |  | 13.2453 | 13.1524 | 13.0481 | 12.8793 | 12.6548 | 12.338 | 11.9073 | 11.424 | 10.8828 | 10.2371 | 8.8567 | 5.3078 | 3.8626 | 3.6856 | 17.3487 | 17.318 | 17.2832 | 17.1927 | 17.0565 | 16.8752 | 16.591 | 16.3463 | 15.9912 | 15.4589 | 14.343 | 11.4631 | 10.2564 | 9.9889 | 14.0646 | 14.0318 | 13.9948 | 13.9004 | 13.7589 | 13.5682 | 13.2737 | 13.0119 | 12.7634 | 12.4231 | 11.3405 | 7.7735 | 6.305 | 6.0653
|  | HILSEA | LW |  |  | 13.1241 | 12.8797 | 12.5984 | 11.9173 | 11.0382 | 9.8478 | 8.2602 | 6.3723 | 4.2896 | 1.7847 | -3.9249 | -13.9034 | -16.5995 | -18.5994 | 17.3085 | 17.2205 | 17.1283 | 16.6447 | 16.022 | 14.9211 | 13.5071 | 11.9101 | 10.2642 | 8.2618 | 3.6015 | -4.7287 | -7.0913 | -8.8878 | 14.0153 | 13.9145 | 13.8075 | 13.2989 | 12.6944 | 11.8831 | 10.5458 | 8.6159 | 6.5528 | 4.082 | -1.5158 | -11.4162 | -14.161 | -16.2216
|  | HILSEA | ST |  |  | 13.3403 | 13.3191 | 13.2888 | 12.948 | 12.6869 | 12.4188 | 12.0298 | 11.7592 | 11.4702 | 11.159 | 10.3996 | 8.2847 | 7.3491 | 6.8846 | 17.376 | 17.3659 | 17.3523 | 16.9664 | 16.6937 | 16.4329 | 16.0403 | 15.8218 | 15.6099 | 15.4053 | 14.9483 | 13.1789 | 12.2425 | 11.6924 | 14.1001 | 14.0934 | 14.0831 | 13.7008 | 13.4308 | 13.1721 | 12.7816 | 12.564 | 12.3507 | 12.143 | 11.6717 | 10.3481 | 9.3849 | 8.8279
|  | HILSEA | FS |  |  | 13.2453 | 13.1524 | 13.0481 | 12.8793 | 12.6548 | 12.338 | 11.9073 | 11.424 | 10.8828 | 10.2371 | 8.8567 | 5.3078 | 3.8626 | 3.6856 | 17.3959 | 17.3687 | 17.3445 | 17.241 | 17.1317 | 17.0022 | 16.8639 | 16.7364 | 16.6311 | 16.5187 | 16.2674 | 15.728 | 15.0288 | 14.2702 | 14.119 | 14.0967 | 14.0777 | 13.9805 | 13.8778 | 13.7553 | 13.6242 | 13.5047 | 13.4047 | 13.299 | 13.0602 | 12.5811 | 12.1583 | 11.5273
MANNINGTON GSP | ARNEWOOD | HINCHELSEA | MINIMUM HEADROOM | SU 27805 00447 | YES | 7.1065 | 6.95 | 6.7467 | 6.3728 | 5.7918 | 5.0063 | 3.9152 | 2.4714 | 0.67184 | -1.5459 | -7.1172 | -16.0921 | -18.4572 | -20.0418 | 7.8777 | 7.8184 | 7.7538 | 7.6409 | 7.5053 | 7.2166 | 6.4018 | 5.3112 | 3.9562 | 2.2734 | -1.9865 | -8.7909 | -10.4934 | -11.706 | 6.5643 | 6.4451 | 6.3162 | 6.0689 | 5.791 | 5.4687 | 5.0407 | 3.6614 | 1.9443 | -0.17432 | -5.5027 | -14.0744 | -16.313 | -17.8247
|  | HINCHELSEA | CT |  |  | 7.1451 | 7.0303 | 6.8686 | 6.6279 | 6.2898 | 5.6894 | 4.863 | 3.7374 | 2.2131 | 0.39725 | -3.7714 | -11.428 | -13.7421 | -15.1895 | 7.907 | 7.8629 | 7.8068 | 7.7132 | 7.6026 | 7.4577 | 6.9973 | 6.1581 | 5.0325 | 3.6776 | 0.54552 | -5.0757 | -6.6363 | -7.6793 | 6.6853 | 6.6378 | 6.5731 | 6.4072 | 6.2142 | 5.9779 | 5.6994 | 4.8521 | 3.4024 | 1.6726 | -2.3026 | -9.5763 | -11.744 | -13.1108
|  | HINCHELSEA | LW |  |  | 7.1065 | 6.95 | 6.7467 | 6.3728 | 5.7918 | 5.0063 | 3.9152 | 2.4714 | 0.67184 | -1.5459 | -7.1172 | -16.0921 | -18.4572 | -20.0418 | 7.8777 | 7.8184 | 7.7538 | 7.6409 | 7.5053 | 7.2166 | 6.4018 | 5.3112 | 3.9562 | 2.2734 | -1.9865 | -8.7909 | -10.4934 | -11.706 | 6.5643 | 6.4451 | 6.3162 | 6.0689 | 5.791 | 5.4687 | 5.0407 | 3.6614 | 1.9443 | -0.17432 | -5.5027 | -14.0744 | -16.313 | -17.8247
|  | HINCHELSEA | ST |  |  | 7.2571 | 7.245 | 7.2289 | 7.1994 | 7.1646 | 7.1207 | 7.065 | 6.9993 | 6.9227 | 6.8284 | 6.576 | 5.8007 | 4.7994 | 3.7885 | 7.937 | 7.9165 | 7.8916 | 7.8569 | 7.8192 | 7.7732 | 7.7168 | 7.6525 | 7.5884 | 7.5106 | 7.3036 | 6.5036 | 5.6986 | 4.8307 | 6.7391 | 6.7259 | 6.7105 | 6.6812 | 6.6528 | 6.6153 | 6.5706 | 6.5184 | 6.4643 | 6.3984 | 6.2054 | 5.278 | 4.3374 | 3.4451
|  | HINCHELSEA | FS |  |  | 7.1451 | 7.0303 | 6.8686 | 6.6279 | 6.2898 | 5.6894 | 4.863 | 3.7374 | 2.2131 | 0.39725 | -3.7714 | -11.428 | -13.7421 | -15.1895 | 7.9354 | 7.9135 | 7.8855 | 7.8566 | 7.8212 | 7.7781 | 7.7291 | 7.6705 | 7.599 | 7.5179 | 7.3112 | 6.4983 | 5.4559 | 4.2671 | 6.7403 | 6.7315 | 6.7155 | 6.6913 | 6.6599 | 6.6195 | 6.5801 | 6.5306 | 6.4429 | 6.3486 | 6.1243 | 5.2149 | 4.0875 | 3.0898
BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD | MINIMUM HEADROOM | SU 88631 36479 | YES | 8.3498 | 7.5234 | 6.7134 | 5.6867 | 4.3399 | 2.9248 | 0.5326 | -2.4254 | -5.7971 | -9.5771 | -17.8841 | -32.7221 | -39.8798 | -43.9178 | 11.3146 | 10.7528 | 10.074 | 9.2646 | 8.3554 | 6.9398 | 5.359 | 2.9579 | 0.045209 | -2.8248 | -8.7423 | -20.7742 | -26.1297 | -28.7453 | 9.1589 | 8.3583 | 7.5737 | 6.5848 | 5.2801 | 3.8658 | 1.5628 | -1.3445 | -4.6687 | -8.3218 | -16.5581 | -31.158 | -37.9539 | -40.6457
|  | HINDHEAD | CT |  |  | 8.4516 | 7.7686 | 6.9497 | 5.8909 | 4.7119 | 2.9252 | 0.94369 | -2.0298 | -5.7733 | -9.4579 | -16.4528 | -32.7221 | -39.8798 | -42.6772 | 11.3146 | 10.7528 | 10.074 | 9.2646 | 8.3554 | 6.9398 | 5.359 | 2.9579 | 0.045209 | -2.8248 | -8.2394 | -20.7742 | -26.1297 | -28.7453 | 9.2398 | 8.5782 | 7.7846 | 6.7533 | 5.6045 | 3.8658 | 1.932 | -0.96005 | -4.6687 | -8.3218 | -15.2122 | -31.158 | -37.9539 | -40.6457
|  | HINDHEAD | LW |  |  | 8.3498 | 7.5234 | 6.7134 | 5.6867 | 4.3399 | 2.9248 | 0.5326 | -2.4254 | -5.7971 | -9.5771 | -17.8841 | -32.4741 | -39.7337 | -43.9178 | 11.3768 | 10.7737 | 10.1841 | 9.4756 | 8.5006 | 7.4721 | 5.6115 | 3.2726 | 0.66561 | -2.2731 | -8.7423 | -19.7757 | -23.7321 | -27.1311 | 9.1589 | 8.3583 | 7.5737 | 6.5848 | 5.2801 | 3.9077 | 1.5628 | -1.3445 | -4.6248 | -8.2981 | -16.5581 | -30.7922 | -36.2241 | -40.3245
|  | HINDHEAD | ST |  |  | 8.9243 | 8.6989 | 8.401 | 7.9371 | 7.3516 | 6.5967 | 5.6114 | 4.3841 | 2.9519 | 1.1708 | -3.7685 | -20.4041 | -31.5459 | -35.2119 | 11.6804 | 11.4843 | 11.224 | 10.8143 | 10.3095 | 9.6633 | 8.8138 | 7.7723 | 6.5615 | 5.0582 | 0.92073 | -12.5759 | -21.6963 | -24.9555 | 9.6993 | 9.4818 | 9.194 | 8.7309 | 8.157 | 7.4204 | 6.4565 | 5.2664 | 3.8745 | 2.049 | -2.9874 | -19.5268 | -30.5773 | -34.1328
|  | HINDHEAD | FS |  |  | 8.4516 | 7.7686 | 6.9497 | 5.8909 | 4.7119 | 2.9252 | 0.94369 | -2.0298 | -5.7733 | -9.4579 | -16.4528 | -32.7221 | -39.8798 | -42.6772 | 11.6937 | 11.5192 | 11.2929 | 10.9924 | 10.6116 | 10.1278 | 9.5216 | 8.7698 | 7.9243 | 6.9195 | 4.1321 | -6.5656 | -18.7623 | -26.2875 | 9.726 | 9.5444 | 9.3077 | 8.9559 | 8.5154 | 7.9558 | 7.2628 | 6.4037 | 5.3918 | 4.2004 | 0.84574 | -12.2976 | -27.1964 | -35.9156
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL | MINIMUM HEADROOM | SU 00702 06030 | YES | 2.0888 | 2.0149 | 1.9288 | 1.8642 | 1.7798 | 1.6835 | 1.5379 | 1.0469 | 0.33212 | -0.54294 | -2.6022 | -10.9553 | -15.0898 | -14.8285 | 2.6663 | 2.6342 | 2.596 | 2.5436 | 2.4744 | 2.3842 | 2.163 | 1.7361 | 1.1819 | 0.50167 | -1.1605 | -7.7339 | -10.9843 | -10.8218 | 2.3549 | 2.286 | 2.2052 | 2.134 | 1.9375 | 1.6622 | 1.2675 | 0.73637 | 0.049726 | -0.79093 | -2.7981 | -10.8477 | -14.8409 | -14.622
|  | HINTON MARTELL | CT |  |  | 2.1288 | 2.0681 | 2.0007 | 1.9191 | 1.8179 | 1.6928 | 1.5379 | 1.2162 | 0.57609 | -0.25589 | -2.6022 | -10.9553 | -15.0898 | -14.8285 | 2.6716 | 2.6374 | 2.5965 | 2.5436 | 2.4744 | 2.3842 | 2.2125 | 1.8308 | 1.3343 | 0.68163 | -1.1605 | -7.7339 | -10.9843 | -10.8218 | 2.3915 | 2.3349 | 2.2719 | 2.1655 | 1.9746 | 1.7129 | 1.3609 | 0.88474 | 0.26874 | -0.53529 | -2.7981 | -10.8477 | -14.8409 | -14.622
|  | HINTON MARTELL | LW |  |  | 2.0888 | 2.0149 | 1.9288 | 1.8642 | 1.7798 | 1.6835 | 1.555 | 1.0469 | 0.33212 | -0.54294 | -2.5853 | -6.1644 | -7.2592 | -8.1294 | 2.6663 | 2.6342 | 2.596 | 2.5617 | 2.515 | 2.458 | 2.163 | 1.7361 | 1.1819 | 0.50167 | -1.0899 | -3.8741 | -4.7811 | -5.5675 | 2.3549 | 2.286 | 2.2052 | 2.134 | 1.9375 | 1.6622 | 1.2675 | 0.73637 | 0.049726 | -0.79093 | -2.7529 | -6.1927 | -7.2857 | -8.1889
|  | HINTON MARTELL | ST |  |  | 2.1689 | 2.1353 | 2.1042 | 2.0396 | 1.9837 | 1.9238 | 1.8558 | 1.799 | 1.7282 | 1.6493 | 1.4852 | 1.0606 | 0.66356 | 0.35147 | 2.6961 | 2.6805 | 2.6648 | 2.6193 | 2.5816 | 2.5425 | 2.4935 | 2.4558 | 2.4008 | 2.3442 | 2.2182 | 1.8566 | 1.4564 | 1.0618 | 2.4298 | 2.3992 | 2.3707 | 2.3051 | 2.2496 | 2.1908 | 2.1225 | 2.0677 | 1.9953 | 1.9165 | 1.7514 | 1.321 | 0.89776 | 0.54882
|  | HINTON MARTELL | FS |  |  | 2.1288 | 2.0681 | 2.0007 | 1.9191 | 1.8179 | 1.6928 | 1.5379 | 1.2162 | 0.57609 | -0.25589 | -2.6022 | -10.9553 | -15.0898 | -14.8285 | 2.7018 | 2.6897 | 2.6759 | 2.6535 | 2.6297 | 2.6021 | 2.5744 | 2.5443 | 2.5066 | 2.4684 | 2.3824 | 2.1448 | 1.9624 | 1.7598 | 2.4461 | 2.4268 | 2.4054 | 2.3677 | 2.3288 | 2.2843 | 2.2433 | 2.1973 | 2.1364 | 2.0772 | 1.9478 | 1.5725 | 1.3371 | 1.1334
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE | MINIMUM HEADROOM | SU 79461 54769 | YES | 13.9355 | 13.2249 | 12.5096 | 11.4691 | 10.2552 | 9.0674 | 7.4171 | 5.5064 | 3.1649 | 0.58648 | -5.0375 | -15.3033 | -21.5633 | -24.5876 | 19.2589 | 18.8324 | 18.3966 | 17.8014 | 17.0634 | 16.3182 | 15.1559 | 13.7585 | 12.1557 | 10.3767 | 6.4749 | -1.8816 | -7.0149 | -10.8196 | 12.7648 | 12.1002 | 11.4328 | 10.4812 | 9.3443 | 8.2121 | 6.563 | 4.623 | 2.3561 | -0.12531 | -5.5328 | -15.2945 | -21.3805 | -24.2255
|  | HITCHES LANE | CT |  |  | 14.2975 | 13.8625 | 13.3621 | 12.5227 | 11.6021 | 10.4762 | 9.1815 | 7.3962 | 4.8604 | 2.3219 | -2.5746 | -14.8981 | -21.5633 | -24.5876 | 19.32 | 18.959 | 18.5179 | 17.9293 | 17.2687 | 16.3814 | 15.3809 | 14.0034 | 12.2262 | 10.4104 | 6.9166 | -1.8816 | -7.0149 | -10.8196 | 13.0385 | 12.6026 | 12.0943 | 11.2892 | 10.3994 | 9.2516 | 7.9788 | 6.2425 | 3.8115 | 1.3616 | -3.347 | -15.1205 | -21.3805 | -24.2255
|  | HITCHES LANE | LW |  |  | 13.9355 | 13.2249 | 12.5096 | 11.4691 | 10.2552 | 9.0674 | 7.4171 | 5.5064 | 3.1649 | 0.58648 | -5.0375 | -15.3033 | -19.773 | -20.1736 | 19.2589 | 18.8324 | 18.3966 | 17.8014 | 17.0634 | 16.3182 | 15.1559 | 13.7585 | 12.1557 | 10.3767 | 6.4749 | -0.34871 | -3.2561 | -3.6107 | 12.7648 | 12.1002 | 11.4328 | 10.4812 | 9.3443 | 8.2121 | 6.563 | 4.623 | 2.3561 | -0.12531 | -5.5328 | -15.2945 | -19.5582 | -20.0136
|  | HITCHES LANE | ST |  |  | 14.6307 | 14.4495 | 14.2246 | 13.8159 | 13.365 | 12.8798 | 12.2494 | 11.4817 | 10.4913 | 9.3107 | 6.1745 | -4.0937 | -11.8286 | -16.7813 | 19.5261 | 19.3493 | 19.1305 | 18.7179 | 18.2684 | 17.7624 | 17.1002 | 16.3752 | 15.4826 | 14.4318 | 11.6789 | 2.9967 | -3.8654 | -8.7993 | 13.3644 | 13.191 | 12.9698 | 12.5325 | 12.0555 | 11.5206 | 10.8158 | 10.0259 | 9.0285 | 7.8434 | 4.7039 | -5.4374 | -13.033 | -17.7258
|  | HITCHES LANE | FS |  |  | 14.2975 | 13.8625 | 13.3621 | 12.5227 | 11.6021 | 10.4762 | 9.1815 | 7.3962 | 4.8604 | 2.3219 | -2.5746 | -14.8981 | -21.5633 | -24.5876 | 19.5727 | 19.382 | 19.1593 | 18.8809 | 18.5604 | 18.1859 | 17.7455 | 17.2176 | 16.6142 | 15.9271 | 14.13 | 7.5394 | -0.20187 | -7.0316 | 13.4234 | 13.2576 | 13.0625 | 12.7416 | 12.3866 | 11.9851 | 11.5157 | 10.9488 | 10.2442 | 9.4508 | 7.3921 | -0.2301 | -8.9077 | -15.2271
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD | MINIMUM HEADROOM | SU 57855 04433 | YES | 0.70145 | 0.39782 | 0.078813 | -0.48446 | -1.1146 | -2.3504 | -4.219 | -6.6258 | -9.6649 | -13.3141 | -21.9167 | -38.8332 | -44.8074 | -47.5588 | 6.1954 | 6.0338 | 5.8228 | 5.5414 | 5.0828 | 4.0765 | 2.6895 | 0.88367 | -1.4169 | -4.1974 | -10.7777 | -23.7011 | -28.4932 | -31.0661 | 4.1601 | 3.8137 | 3.4508 | 2.8368 | 1.9691 | 0.6614 | -1.1214 | -3.4204 | -6.3348 | -9.8363 | -18.0878 | -34.3225 | -40.2091 | -43.1159
|  | HOEFORD | CT |  |  | 0.87684 | 0.71307 | 0.49805 | 0.18086 | -0.066756 | -0.55318 | -1.0759 | -1.7068 | -2.6728 | -3.6673 | -5.6564 | -10.5948 | -13.4223 | -14.8918 | 6.2409 | 6.1394 | 5.9489 | 5.7478 | 5.6304 | 5.47 | 5.3162 | 4.9782 | 4.3615 | 3.6831 | 2.2999 | -1.2964 | -4.224 | -7.3747 | 4.2729 | 4.1389 | 3.9408 | 3.5804 | 3.2169 | 2.7962 | 2.3678 | 1.8714 | 1.0262 | 0.093217 | -1.7674 | -6.3747 | -9.0955 | -10.554
|  | HOEFORD | LW |  |  | 0.70145 | 0.39782 | 0.078813 | -0.48446 | -1.1146 | -2.3504 | -4.219 | -6.6258 | -9.6649 | -13.3141 | -21.9167 | -38.8332 | -44.8074 | -47.5588 | 6.1954 | 6.0338 | 5.8228 | 5.5414 | 5.0828 | 4.0765 | 2.6895 | 0.88367 | -1.4169 | -4.1974 | -10.7777 | -23.7011 | -28.4932 | -31.0661 | 4.1601 | 3.8137 | 3.4508 | 2.8368 | 1.9691 | 0.6614 | -1.1214 | -3.4204 | -6.3348 | -9.8363 | -18.0878 | -34.3225 | -40.2091 | -43.1159
|  | HOEFORD | ST |  |  | 0.92225 | 0.82083 | 0.66357 | 0.50158 | 0.41503 | 0.30677 | 0.19797 | 0.07713 | -0.11621 | -0.48039 | -1.4592 | -4.8159 | -7.7481 | -10.1385 | 6.2427 | 6.1725 | 6.0122 | 5.8212 | 5.7168 | 5.5954 | 5.4828 | 5.3597 | 5.1542 | 4.9284 | 4.1678 | 0.97496 | -2.4048 | -6.1684 | 4.2742 | 4.1786 | 4.0177 | 3.8379 | 3.7337 | 3.6089 | 3.4848 | 3.3479 | 3.1173 | 2.7344 | 1.7344 | -1.2014 | -4.1347 | -6.5082
|  | HOEFORD | FS |  |  | 0.87684 | 0.71307 | 0.49805 | 0.18086 | -0.066756 | -0.55318 | -1.0759 | -1.7068 | -2.6728 | -3.6673 | -5.6564 | -10.5948 | -13.4223 | -14.8918 | 6.2338 | 6.1471 | 6.0278 | 5.8744 | 5.7186 | 5.5222 | 5.2893 | 4.9237 | 4.1279 | 3.0425 | 0.3366 | -5.0805 | -7.7124 | -11.8442 | 4.2675 | 4.154 | 4.0217 | 3.8627 | 3.6967 | 3.3124 | 2.7516 | 2.0092 | 1.0591 | -0.23036 | -3.5637 | -10.3657 | -13.8739 | -16.8371
MANNINGTON GSP | LYTCHETT | HOLES BAY | MINIMUM HEADROOM | SZ 00725 91955 | YES | 3.0522 | 2.7869 | 2.4763 | 2.0952 | 1.5673 | 0.865 | -0.1436 | -1.5163 | -3.8375 | -6.6862 | -13.7951 | -24.9316 | -27.903 | -30.3296 | 5.5562 | 5.4028 | 5.2333 | 5.0311 | 4.7882 | 4.4982 | 4.1216 | 3.6859 | 3.1174 | 2.3993 | -2.1439 | -10.8243 | -13.2441 | -15.3568 | 4.383 | 4.2027 | 4.003 | 3.7257 | 3.3916 | 2.9925 | 2.4761 | 1.8697 | 1.1127 | -0.3293 | -7.1574 | -17.8656 | -20.8015 | -23.2659
|  | HOLES BAY | CT |  |  | 3.1603 | 2.9921 | 2.8201 | 2.7015 | 2.5604 | 2.3537 | 2.1125 | 1.8046 | 1.4168 | 0.99567 | 0.17787 | -1.4822 | -2.235 | -2.8254 | 5.6168 | 5.4843 | 5.3536 | 5.2691 | 5.17 | 5.0464 | 4.9076 | 4.7619 | 4.5522 | 4.3188 | 3.8745 | 2.9584 | 2.2157 | 1.3547 | 4.4881 | 4.3613 | 4.2343 | 4.1145 | 3.9745 | 3.806 | 3.6205 | 3.4156 | 3.1091 | 2.7784 | 2.1416 | 0.84181 | 0.038071 | -0.58477
|  | HOLES BAY | LW |  |  | 3.0522 | 2.7869 | 2.4763 | 2.0952 | 1.5673 | 0.865 | -0.1436 | -1.5163 | -3.8375 | -6.6862 | -13.7951 | -24.9316 | -27.903 | -30.3296 | 5.5562 | 5.4028 | 5.2333 | 5.0311 | 4.7882 | 4.4982 | 4.1216 | 3.6859 | 3.1174 | 2.3993 | -2.1439 | -10.8243 | -13.2441 | -15.3568 | 4.383 | 4.2027 | 4.003 | 3.7257 | 3.3916 | 2.9925 | 2.4761 | 1.8697 | 1.1127 | -0.3293 | -7.1574 | -17.8656 | -20.8015 | -23.2659
|  | HOLES BAY | ST |  |  | 3.2254 | 3.1089 | 2.9895 | 2.9069 | 2.8121 | 2.6972 | 2.5563 | 2.4182 | 2.228 | 2.0086 | 1.4702 | 0.028273 | -0.74555 | -1.2151 | 5.6534 | 5.5461 | 5.4412 | 5.3825 | 5.3235 | 5.2552 | 5.1701 | 5.1066 | 4.9974 | 4.8816 | 4.6251 | 3.837 | 2.8891 | 1.7784 | 4.5567 | 4.4744 | 4.3939 | 4.3459 | 4.2988 | 4.2433 | 4.1674 | 4.1121 | 4.0058 | 3.8922 | 3.6325 | 2.7645 | 1.8483 | 0.87726
|  | HOLES BAY | FS |  |  | 3.1603 | 2.9921 | 2.8201 | 2.7015 | 2.5604 | 2.3537 | 2.1125 | 1.8046 | 1.4168 | 0.99567 | 0.17787 | -1.4822 | -2.235 | -2.8254 | 5.6709 | 5.6048 | 5.531 | 5.4653 | 5.3965 | 5.3261 | 5.2465 | 5.1652 | 5.0568 | 4.9349 | 4.6398 | 3.6629 | 2.3554 | 0.79021 | 4.5637 | 4.5131 | 4.4554 | 4.391 | 4.3225 | 4.2531 | 4.1721 | 4.0898 | 3.9781 | 3.8535 | 3.5508 | 2.4953 | 1.2136 | -0.037427
MELKSHAM GSP | FROME BSP | HOLWELL | MINIMUM HEADROOM | ST 72191 44633 | YES | -3.0799 | -3.2286 | -3.398 | -3.5817 | -3.8258 | -4.1155 | -4.6497 | -5.8643 | -7.3166 | -8.9589 | -12.6032 | -18.9947 | -28.3494 | -34.6815 | -2.5213 | -2.6262 | -2.7462 | -2.8746 | -3.045 | -3.244 | -3.591 | -4.5766 | -5.7715 | -7.0625 | -9.9845 | -15.1065 | -22.3287 | -27.6927 | -3.1238 | -3.294 | -3.4875 | -3.6822 | -4.0516 | -4.6773 | -5.573 | -6.819 | -8.236 | -9.8382 | -13.3961 | -19.7221 | -28.837 | -35.1584
|  | HOLWELL | CT |  |  | -3.0062 | -3.0846 | -3.1788 | -3.2986 | -3.4453 | -3.8258 | -4.5582 | -5.7129 | -7.2099 | -8.6894 | -11.3821 | -17.5449 | -20.0334 | -21.0614 | -2.4811 | -2.5367 | -2.6047 | -2.6957 | -2.8097 | -2.9824 | -3.591 | -4.562 | -5.7715 | -6.9887 | -9.2022 | -14.3136 | -16.4649 | -17.5483 | -3.0144 | -3.0994 | -3.1963 | -3.5038 | -3.9609 | -4.6773 | -5.4798 | -6.6864 | -8.1461 | -9.6031 | -12.2568 | -18.358 | -20.9176 | -22.0463
|  | HOLWELL | LW |  |  | -3.0799 | -3.2286 | -3.398 | -3.5817 | -3.8258 | -4.1155 | -4.6497 | -5.8643 | -7.3166 | -8.9589 | -12.6032 | -18.9947 | -28.3494 | -34.6815 | -2.5213 | -2.6262 | -2.7462 | -2.8746 | -3.045 | -3.244 | -3.5801 | -4.5766 | -5.7426 | -7.0625 | -9.9845 | -15.1065 | -22.3287 | -27.6927 | -3.1238 | -3.294 | -3.4875 | -3.6822 | -4.0516 | -4.5905 | -5.573 | -6.819 | -8.236 | -9.8382 | -13.3961 | -19.7221 | -28.837 | -35.1584
|  | HOLWELL | ST |  |  | -2.9516 | -2.9772 | -3.0102 | -3.1279 | -3.2363 | -3.3575 | -3.5231 | -3.7496 | -4.4359 | -5.2589 | -7.6998 | -15.5025 | -20.6994 | -22.2581 | -2.4418 | -2.4585 | -2.4813 | -2.6029 | -2.7063 | -2.8175 | -2.9748 | -3.1086 | -3.5803 | -4.3207 | -6.3518 | -12.8058 | -17.289 | -18.8972 | -2.9581 | -2.9934 | -3.033 | -3.1782 | -3.306 | -3.5107 | -4.0288 | -4.6259 | -5.3857 | -6.2936 | -8.7355 | -16.3995 | -21.726 | -23.4442
|  | HOLWELL | FS |  |  | -3.0062 | -3.0846 | -3.1788 | -3.2986 | -3.4453 | -3.8258 | -4.5582 | -5.7129 | -7.2099 | -8.6894 | -11.3821 | -17.5449 | -20.0334 | -21.0614 | -2.4288 | -2.4661 | -2.5126 | -2.585 | -2.6708 | -2.7857 | -2.9272 | -3.1058 | -3.3361 | -3.6184 | -4.5984 | -9.5138 | -14.8476 | -17.911 | -2.9454 | -3.0019 | -3.0708 | -3.18 | -3.3107 | -3.4763 | -3.6825 | -3.9622 | -4.4759 | -5.0806 | -6.7353 | -12.7638 | -19.2005 | -22.8825
MANNINGTON GSP | SALISBURY | HOMINGTON | MINIMUM HEADROOM | SU 11742 26037 | YES | 8.1842 | 7.7605 | 7.3275 | 6.8542 | 6.0462 | 4.6079 | 2.544 | -0.25142 | -3.7921 | -8.2128 | -19.2924 | -45.3837 | -54.9957 | -56.436 | 9.1465 | 8.8574 | 8.5636 | 7.7812 | 6.5404 | 4.7272 | 2.1444 | -1.4133 | -5.9412 | -11.6121 | -25.696 | -50.1667 | -57.0206 | -61.9252 | 8.1676 | 7.7672 | 7.36 | 6.4913 | 4.9582 | 2.7274 | -0.44484 | -4.8073 | -10.3597 | -17.309 | -34.5558 | -64.6033 | -73.0618 | -79.108
|  | HOMINGTON | CT |  |  | 8.2634 | 7.9453 | 7.5661 | 7.1505 | 6.6906 | 5.9879 | 5.2167 | 4.0537 | 2.6756 | 1.3456 | -1.1148 | -6.7671 | -9.0814 | -9.7394 | 9.148 | 8.9056 | 8.6141 | 8.2905 | 7.9303 | 7.3621 | 6.734 | 5.7706 | 4.6381 | 3.5469 | 1.5385 | -3.1105 | -4.9197 | -5.5851 | 8.2199 | 7.9088 | 7.5336 | 7.1196 | 6.6603 | 5.9447 | 5.157 | 3.955 | 2.5335 | 1.1646 | -1.3551 | -7.1371 | -9.3771 | -9.9992
|  | HOMINGTON | LW |  |  | 8.1842 | 7.7605 | 7.3275 | 6.8542 | 6.0462 | 4.6079 | 2.544 | -0.25142 | -3.7921 | -8.2128 | -19.2924 | -45.3837 | -54.9957 | -56.436 | 9.1465 | 8.8574 | 8.5636 | 8.2105 | 7.5322 | 6.4066 | 4.7865 | 2.593 | -0.17634 | -3.6389 | -12.3217 | -32.7758 | -40.2738 | -41.3773 | 8.1676 | 7.7672 | 7.36 | 6.9007 | 6.0796 | 4.6909 | 2.6983 | 0.0037211 | -3.402 | -7.654 | -18.3076 | -43.3889 | -52.6134 | -53.9823
|  | HOMINGTON | ST |  |  | 8.4733 | 8.3383 | 8.1757 | 7.9359 | 7.6436 | 7.281 | 6.8207 | 6.2613 | 5.6273 | 4.8424 | 2.7164 | -3.9546 | -8.267 | -9.2446 | 9.3033 | 9.2109 | 9.0922 | 8.9068 | 8.6809 | 8.3948 | 8.0214 | 7.5665 | 7.0519 | 6.4092 | 4.6462 | -0.97078 | -4.5119 | -5.4173 | 8.4242 | 8.2985 | 8.1437 | 7.9076 | 7.6205 | 7.2618 | 6.8002 | 6.231 | 5.5825 | 4.7753 | 2.5733 | -4.3727 | -8.6992 | -9.648
|  | HOMINGTON | FS |  |  | 8.2634 | 7.9453 | 7.5661 | 7.1505 | 6.6906 | 5.9879 | 5.2167 | 4.0537 | 2.6756 | 1.3456 | -1.1148 | -6.7671 | -9.0814 | -9.7394 | 9.2778 | 9.1626 | 8.6206 | 7.7812 | 6.5404 | 4.7272 | 2.1444 | -1.4133 | -5.9412 | -11.6121 | -25.696 | -50.1667 | -57.0206 | -61.9252 | 8.3981 | 8.2172 | 7.5332 | 6.4913 | 4.9582 | 2.7274 | -0.44484 | -4.8073 | -10.3597 | -17.309 | -34.5558 | -64.6033 | -73.0618 | -79.108
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK | MINIMUM HEADROOM | SU 72602 53780 | YES | 13.1931 | 12.3785 | 11.5652 | 10.4942 | 9.1248 | 7.6346 | 5.2252 | 2.2283 | -2.1684 | -8.3161 | -24.4669 | -65.3558 | -90.1397 | -99.1346 | 16.3524 | 15.7682 | 15.1933 | 14.4519 | 13.4872 | 12.316 | 10.6306 | 7.6272 | 3.8208 | -0.91529 | -13.4142 | -45.1391 | -64.5889 | -71.9518 | 12.7723 | 12.0192 | 11.2722 | 10.2684 | 9.0053 | 7.6224 | 5.4193 | 1.8214 | -2.9446 | -8.8473 | -24.3546 | -63.6044 | -87.5108 | -96.349
|  | HOOK | CT |  |  | 13.3904 | 12.7815 | 12.0502 | 11.0157 | 9.9139 | 8.2656 | 6.4062 | 3.6947 | 0.2074 | -3.3133 | -11.9129 | -33.8364 | -45.6038 | -52.5451 | 16.3755 | 15.8761 | 15.2708 | 14.4699 | 13.6223 | 12.316 | 10.8277 | 8.6268 | 5.9428 | 3.2303 | -3.868 | -20.5697 | -29.4704 | -34.9087 | 12.9844 | 12.4416 | 11.7892 | 10.8298 | 9.8241 | 8.3261 | 6.6157 | 3.9145 | 0.5072 | -2.9139 | -12.3961 | -33.4629 | -44.7756 | -51.5127
|  | HOOK | LW |  |  | 13.1931 | 12.3785 | 11.5652 | 10.4942 | 9.1248 | 7.6346 | 5.2252 | 2.2283 | -2.1684 | -8.3161 | -24.4669 | -65.3558 | -90.1397 | -99.1346 | 16.3524 | 15.7682 | 15.1933 | 14.4519 | 13.4872 | 12.4258 | 10.6306 | 7.6272 | 3.8208 | -0.91529 | -13.4142 | -45.1391 | -64.5889 | -71.9518 | 12.7723 | 12.0192 | 11.2722 | 10.2684 | 9.0053 | 7.6224 | 5.4193 | 1.8214 | -2.9446 | -8.8473 | -24.3546 | -63.6044 | -87.5108 | -96.349
|  | HOOK | ST |  |  | 13.8143 | 13.6051 | 13.3347 | 12.8282 | 12.284 | 11.5884 | 10.671 | 9.566 | 8.2654 | 6.6648 | 2.3101 | -12.0813 | -22.0094 | -25.8962 | 16.6935 | 16.5054 | 16.2616 | 15.7852 | 15.3027 | 14.6903 | 13.8678 | 12.9019 | 11.7602 | 10.3716 | 6.6192 | -5.6355 | -14.4696 | -18.7829 | 13.3675 | 13.1829 | 12.9448 | 12.4463 | 11.9477 | 11.3193 | 10.4904 | 9.5179 | 8.1961 | 6.5503 | 2.0882 | -12.5569 | -22.614 | -26.3705
|  | HOOK | FS |  |  | 13.3904 | 12.7815 | 12.0502 | 11.0157 | 9.9139 | 8.2656 | 6.4062 | 3.6947 | 0.2074 | -3.3133 | -11.9129 | -33.8364 | -45.6038 | -52.5451 | 16.6252 | 16.3479 | 16.0216 | 15.5767 | 15.037 | 14.3518 | 13.4682 | 12.343 | 10.2979 | 7.5617 | -0.21428 | -29.0854 | -51.9764 | -60.1845 | 13.3013 | 13.0278 | 12.7084 | 12.2239 | 11.6381 | 10.8925 | 9.9315 | 8.246 | 5.5983 | 2.2346 | -7.3161 | -42.8746 | -71.1474 | -81.4749
LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR | MINIMUM HEADROOM | TQ 12710 72057 | YES | 4.0765 | 3.7936 | 3.4693 | 3.049 | 2.4816 | 1.8159 | 0.82735 | -0.50724 | -1.9806 | -3.6426 | -7.3302 | -13.4905 | -15.9173 | -16.477 | 4.8499 | 4.6117 | 4.3217 | 3.9794 | 3.5987 | 2.9986 | 2.3349 | 1.2844 | 0.087624 | -1.1764 | -4.0795 | -9.1065 | -13.9745 | -19.6517 | 4.0748 | 3.8212 | 3.5175 | 3.1076 | 2.5518 | 1.9118 | 0.93638 | -0.36305 | -1.7942 | -3.4097 | -6.9958 | -13.0769 | -16.6485 | -21.0055
|  | HOPE AND ANCHOR | CT |  |  | 4.105 | 3.8457 | 3.4961 | 3.0577 | 2.5729 | 1.8159 | 0.98551 | -0.2883 | -1.8259 | -3.3178 | -6.1507 | -13.1789 | -15.9173 | -16.477 | 4.8499 | 4.6117 | 4.3217 | 3.9794 | 3.5987 | 2.9986 | 2.335 | 1.3134 | 0.087624 | -1.1052 | -3.3803 | -9.1065 | -11.7313 | -13.1281 | 4.0906 | 3.8717 | 3.5403 | 3.1188 | 2.647 | 1.9118 | 1.1038 | -0.13288 | -1.6248 | -3.0753 | -5.84 | -12.7347 | -15.4259 | -15.9539
|  | HOPE AND ANCHOR | LW |  |  | 4.0765 | 3.7936 | 3.4693 | 3.049 | 2.4816 | 1.8867 | 0.82735 | -0.50724 | -1.9806 | -3.6426 | -7.3302 | -13.4905 | -14.5658 | -12.6931 | 4.8853 | 4.6293 | 4.3756 | 4.0634 | 3.6304 | 3.1698 | 2.3349 | 1.2844 | 0.13123 | -1.1764 | -4.0795 | -8.8951 | -9.7026 | -8.1689 | 4.0748 | 3.8212 | 3.5175 | 3.1076 | 2.5518 | 1.967 | 0.93638 | -0.36305 | -1.7942 | -3.4097 | -6.9958 | -13.0769 | -14.1248 | -12.2441
|  | HOPE AND ANCHOR | ST |  |  | 4.2423 | 4.1837 | 4.0759 | 3.8694 | 3.5904 | 3.213 | 2.7099 | 2.0655 | 1.3106 | 0.36034 | -2.2008 | -9.7803 | -14.2321 | -15.2154 | 4.996 | 4.9035 | 4.7778 | 4.5883 | 4.3459 | 4.0247 | 3.599 | 3.0613 | 2.4267 | 1.6322 | -0.50197 | -6.8273 | -10.8722 | -12.5475 | 4.2401 | 4.1697 | 4.0731 | 3.8957 | 3.6302 | 3.2635 | 2.7742 | 2.1506 | 1.4219 | 0.50473 | -1.9835 | -9.5188 | -13.926 | -14.8706
|  | HOPE AND ANCHOR | FS |  |  | 4.105 | 3.8457 | 3.4961 | 3.0577 | 2.5729 | 1.8159 | 0.98551 | -0.2883 | -1.8259 | -3.3178 | -6.1507 | -13.1789 | -15.9173 | -16.477 | 4.9776 | 4.8842 | 4.7584 | 4.5887 | 4.369 | 4.086 | 3.723 | 3.2638 | 2.7274 | 2.0772 | 0.27573 | -6.3714 | -13.9745 | -19.6517 | 4.2193 | 4.1451 | 4.0379 | 3.879 | 3.6383 | 3.3179 | 2.9012 | 2.3658 | 1.7618 | 1.026 | -1.0192 | -8.5424 | -16.6485 | -21.0055
LOVEDEAN GSP | HAVANT | HORNDEAN | MINIMUM HEADROOM | SU 70271 12802 | YES | 5.9514 | 4.2682 | 2.66 | 0.48571 | -2.2439 | -5.1419 | -9.5988 | -15.2385 | -21.9005 | -29.3229 | -45.6319 | -73.4579 | -83.2377 | -88.7144 | 10.3524 | 9.2407 | 8.1691 | 6.8324 | 5.0741 | 3.1899 | 0.069269 | -3.8075 | -8.274 | -13.7488 | -27.755 | -66.8712 | -90.4959 | -104.496 | 5.3169 | 3.6569 | 2.0594 | -0.042142 | -2.7382 | -5.593 | -10.187 | -15.8234 | -22.258 | -29.4437 | -45.2352 | -89.5278 | -119.1408 | -137.0678
|  | HORNDEAN | CT |  |  | 6.4359 | 5.2193 | 3.8523 | 1.9065 | -0.26013 | -3.3592 | -6.9146 | -12.2837 | -19.2719 | -26.1449 | -39.2899 | -69.83 | -83.2377 | -88.7144 | 10.4142 | 9.478 | 8.399 | 7.0498 | 5.5337 | 3.2751 | 0.76087 | -3.0421 | -8.26 | -13.3715 | -23.0307 | -45.5231 | -55.7886 | -62.3597 | 5.6499 | 4.3868 | 2.9324 | 0.96001 | -1.2322 | -4.462 | -8.0222 | -13.2501 | -20.0022 | -26.6385 | -39.2846 | -68.5733 | -81.1541 | -86.1765
|  | HORNDEAN | LW |  |  | 5.9514 | 4.2682 | 2.66 | 0.48571 | -2.2439 | -5.1419 | -9.5988 | -15.2385 | -21.9005 | -29.3229 | -45.6319 | -73.4579 | -82.105 | -78.9989 | 10.3524 | 9.2407 | 8.1691 | 6.8324 | 5.0741 | 3.1899 | 0.069269 | -3.8075 | -8.274 | -13.7488 | -25.8063 | -45.6706 | -50.8711 | -53.2636 | 5.3169 | 3.6569 | 2.0594 | -0.042142 | -2.7382 | -5.593 | -10.187 | -15.8234 | -22.258 | -29.4437 | -45.2352 | -71.9987 | -80.0484 | -77.1059
|  | HORNDEAN | ST |  |  | 7.1375 | 6.5915 | 6.0037 | 5.2665 | 4.2996 | 3.074 | 1.4973 | -0.4499 | -2.9216 | -6.1141 | -14.832 | -43.8144 | -64.5138 | -72.2323 | 10.9287 | 10.5087 | 10.0267 | 9.4162 | 8.6273 | 7.6206 | 6.3235 | 4.7179 | 2.8197 | 0.38459 | -7.1809 | -31.7854 | -49.2038 | -57.2672 | 6.4048 | 5.882 | 5.2822 | 4.4973 | 3.4659 | 2.1394 | 0.41618 | -1.7942 | -4.388 | -7.6155 | -16.4529 | -45.8426 | -66.1216 | -73.3671
|  | HORNDEAN | FS |  |  | 6.4359 | 5.2193 | 3.8523 | 1.9065 | -0.26013 | -3.3592 | -6.9146 | -12.2837 | -19.2719 | -26.1449 | -39.2899 | -69.83 | -83.2377 | -88.7144 | 10.794 | 10.2134 | 9.5355 | 8.7064 | 7.6445 | 6.2684 | 4.4702 | 2.1455 | -3.3086 | -10.1991 | -27.755 | -66.8712 | -90.4959 | -104.496 | 6.2381 | 5.5491 | 4.746 | 3.7009 | 2.3646 | 0.63406 | -1.6275 | -4.5532 | -11.1017 | -19.58 | -41.1471 | -89.5278 | -119.1408 | -137.0678
NURSLING GSP | WINCHESTER | HOUGHTON | MINIMUM HEADROOM | SU 33784 31741 | YES | 0.46145 | 0.20351 | -0.15684 | -0.68875 | -1.459 | -2.5707 | -4.1381 | -6.3829 | -9.2334 | -12.8551 | -21.9446 | -37.027 | -41.4821 | -45.0127 | 2.4752 | 2.2674 | 1.9741 | 1.5305 | 0.88146 | -0.056442 | -1.3901 | -3.1556 | -5.3986 | -8.2903 | -15.5123 | -27.6249 | -31.3518 | -34.4813 | 0.66051 | 0.49504 | 0.23252 | -0.25262 | -1.004 | -2.1668 | -3.8024 | -5.9764 | -8.7293 | -12.2498 | -21.0551 | -35.7578 | -40.237 | -43.8664
|  | HOUGHTON | CT |  |  | 0.46145 | 0.20351 | -0.15684 | -0.68875 | -1.459 | -2.5707 | -4.1381 | -6.3829 | -9.2334 | -12.8551 | -21.9446 | -37.027 | -41.4821 | -45.0127 | 2.4752 | 2.2674 | 1.9741 | 1.5305 | 0.88146 | -0.056442 | -1.3901 | -3.1556 | -5.3986 | -8.2903 | -15.5123 | -27.6249 | -31.3518 | -34.4813 | 0.7484 | 0.57152 | 0.23252 | -0.25262 | -1.004 | -2.1668 | -3.8024 | -5.9764 | -8.7293 | -12.2498 | -21.0551 | -35.7578 | -40.237 | -43.8664
|  | HOUGHTON | LW |  |  | 0.50517 | 0.34697 | 0.17249 | -0.012439 | -0.24884 | -0.53906 | -0.93093 | -1.4219 | -2.0605 | -2.863 | -5.1496 | -14.41 | -26.7461 | -34.387 | 2.5245 | 2.4066 | 2.2754 | 2.1285 | 1.9384 | 1.7029 | 1.3822 | 0.97896 | 0.4329 | -0.22652 | -2.0104 | -9.2882 | -19.4381 | -26.1958 | 0.66051 | 0.49504 | 0.32093 | 0.18479 | -0.049256 | -0.3348 | -0.70233 | -1.1515 | -1.7457 | -2.5486 | -4.7617 | -13.7101 | -25.8739 | -33.6912
|  | HOUGHTON | ST |  |  | 0.69682 | 0.66036 | 0.61758 | 0.41498 | 0.25126 | 0.089219 | -0.12982 | -0.28771 | -0.55691 | -0.81968 | -1.4331 | -3.1618 | -4.8372 | -6.4703 | 2.6695 | 2.6461 | 2.6176 | 2.3944 | 2.2243 | 2.0611 | 1.8335 | 1.6888 | 1.409 | 1.1422 | 0.52468 | -1.2176 | -3.1125 | -4.9022 | 0.87121 | 0.81593 | 0.75341 | 0.4892 | 0.28007 | 0.08011 | -0.18162 | -0.35733 | -0.67077 | -0.9624 | -1.6011 | -3.5078 | -5.5797 | -7.5201
|  | HOUGHTON | FS |  |  | 0.46145 | 0.20351 | -0.15684 | -0.68875 | -1.459 | -2.5707 | -4.1381 | -6.3829 | -9.2334 | -12.8551 | -21.9446 | -37.027 | -41.4821 | -45.0127 | 2.5399 | 2.4129 | 2.2424 | 1.9603 | 1.5884 | 1.0823 | 0.40193 | -0.50345 | -1.6987 | -3.2209 | -7.5814 | -23.1702 | -30.9394 | -30.8873 | 0.82323 | 0.7078 | 0.56463 | 0.28077 | -0.12601 | -0.70898 | -1.5533 | -2.6739 | -4.1459 | -6.0164 | -11.3648 | -30.5742 | -40.1291 | -40.007
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS | MINIMUM HEADROOM | SU 62187 52886 | YES | 21.1351 | 20.6047 | 19.8775 | 18.7543 | 17.7615 | 16.5546 | 15.2005 | 13.7365 | 12.1607 | 10.5174 | 5.7523 | -9.1577 | -19.8047 | -28.1392 | 21.7988 | 21.5481 | 21.207 | 20.6635 | 20.1528 | 19.5174 | 18.8031 | 17.8823 | 16.5105 | 14.8333 | 10.8376 | -0.54576 | -8.3971 | -14.7667 | 20.0617 | 19.7556 | 19.2814 | 18.3491 | 17.4996 | 16.4624 | 15.3025 | 14.0559 | 12.7174 | 11.1248 | 5.9566 | -8.2984 | -18.3662 | -26.3221
|  | HOUNDMILLS | CT |  |  | 21.1506 | 20.8891 | 20.374 | 19.4453 | 18.667 | 17.6337 | 16.5793 | 15.3285 | 13.7971 | 12.1988 | 9.1261 | -4.2945 | -19.8047 | -28.1392 | 21.8024 | 21.6483 | 21.3581 | 20.8914 | 20.4636 | 19.902 | 19.3449 | 18.6899 | 17.6386 | 16.3693 | 13.41 | 3.4185 | -8.3971 | -14.7667 | 20.0954 | 19.8506 | 19.4911 | 18.9397 | 18.2817 | 17.4078 | 16.516 | 15.4587 | 14.1653 | 12.8186 | 9.2 | -3.5563 | -18.3662 | -26.3221
|  | HOUNDMILLS | LW |  |  | 21.1351 | 20.6047 | 19.8775 | 18.7543 | 17.7615 | 16.5546 | 15.2005 | 13.7365 | 12.1607 | 10.5174 | 5.7523 | -9.1577 | -16.0831 | -15.6255 | 21.7988 | 21.5481 | 21.207 | 20.6635 | 20.1528 | 19.5174 | 18.8031 | 17.8823 | 16.5105 | 14.8333 | 10.8376 | -0.54576 | -5.8227 | -5.3912 | 20.0617 | 19.7556 | 19.2814 | 18.3491 | 17.4996 | 16.4624 | 15.3025 | 14.0559 | 12.7174 | 11.1248 | 5.9566 | -8.2984 | -14.9117 | -14.4494
|  | HOUNDMILLS | ST |  |  | 21.2287 | 21.0203 | 20.6227 | 19.9126 | 19.4044 | 18.7477 | 18.141 | 17.4742 | 16.7854 | 16.0671 | 14.9087 | 13.3248 | 12.1964 | 10.7652 | 21.8659 | 21.7549 | 21.5104 | 21.1247 | 20.8126 | 20.4216 | 20.0704 | 19.7065 | 19.3274 | 18.9275 | 18.2613 | 17.0066 | 15.8232 | 13.7271 | 20.1825 | 19.9932 | 19.6979 | 19.2241 | 18.8861 | 18.3697 | 17.8726 | 17.3504 | 16.8154 | 16.2554 | 15.3543 | 13.993 | 13.006 | 11.7305
|  | HOUNDMILLS | FS |  |  | 21.1506 | 20.8891 | 20.374 | 19.4453 | 18.667 | 17.6337 | 16.5793 | 15.3285 | 13.7971 | 12.1988 | 9.1261 | -4.2945 | -19.8047 | -28.1392 | 21.8638 | 21.7591 | 21.5572 | 21.2508 | 20.9901 | 20.6754 | 20.3567 | 20.0206 | 19.6482 | 19.2517 | 18.4813 | 16.1576 | 12.7986 | 8.1597 | 20.1848 | 20.0136 | 19.7461 | 19.3639 | 19.0628 | 18.678 | 18.2937 | 17.8126 | 17.2973 | 16.7555 | 15.7463 | 13.5709 | 11.2888 | 9.473
BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD | MINIMUM HEADROOM | SU 34066 68957 | YES | 1.6325 | 5.0902 | 4.4477 | 3.3262 | 1.6487 | -0.7277 | -4.1188 | -8.7253 | -14.5424 | -21.7691 | -39.5345 | -69.541 | -77.1437 | -82.4729 | 9.6 | 13.35 | 13.35 | 13.3203 | 13.2956 | 13.257 | 13.2149 | 13.1797 | 13.1719 | 13.1638 | 13.1497 | 13.1104 | 13.1023 | 13.1023 | 1.2993 | 4.5573 | 3.8746 | 2.8526 | 1.3638 | -0.80971 | -4.0697 | -8.4962 | -14.0768 | -21.0119 | -38.0631 | -66.8501 | -74.1229 | -79.2267
|  | HUNGERFORD | CT |  |  | 1.8218 | 5.5095 | 5.3311 | 5.0934 | 4.7741 | 4.1533 | 3.3076 | 2.1111 | 0.52832 | -1.4264 | -6.8049 | -25.6401 | -34.8681 | -34.2867 | 9.6 | 13.35 | 13.35 | 13.346 | 13.3389 | 13.3304 | 13.3152 | 13.306 | 13.306 | 13.306 | 13.306 | 13.306 | 13.306 | 13.306 | 1.5871 | 5.1591 | 4.93 | 4.6048 | 4.1818 | 3.5859 | 2.8038 | 1.7295 | 0.33428 | -1.4628 | -6.6079 | -24.6404 | -33.4518 | -32.8678
|  | HUNGERFORD | LW |  |  | 1.6325 | 5.0902 | 4.4477 | 3.3262 | 1.6487 | -0.7277 | -4.1188 | -8.7253 | -14.5424 | -21.7691 | -39.5345 | -69.541 | -77.1437 | -82.4729 | 9.6 | 13.35 | 13.35 | 13.3243 | 13.2956 | 13.257 | 13.2149 | 13.1797 | 13.1719 | 13.1638 | 13.1497 | 13.1104 | 13.1023 | 13.1023 | 1.2993 | 4.5573 | 3.8746 | 2.8526 | 1.3638 | -0.80971 | -4.0697 | -8.4962 | -14.0768 | -21.0119 | -38.0631 | -66.8501 | -74.1229 | -79.2267
|  | HUNGERFORD | ST |  |  | 1.9588 | 5.7649 | 5.7389 | 5.6761 | 5.6082 | 5.5261 | 5.4177 | 5.2987 | 5.109 | 4.7617 | 3.746 | 0.30358 | -2.1137 | -3.2463 | 9.6 | 13.35 | 13.35 | 13.3203 | 13.3002 | 13.2821 | 13.2546 | 13.2419 | 13.2419 | 13.2419 | 13.2419 | 13.2419 | 13.2419 | 13.2419 | 1.7628 | 5.4883 | 5.4554 | 5.3699 | 5.2828 | 5.1788 | 5.0474 | 4.9048 | 4.7523 | 4.5677 | 4.0755 | 1.5415 | -0.78885 | -1.8146
|  | HUNGERFORD | FS |  |  | 1.8218 | 5.5095 | 5.3311 | 5.0934 | 4.7741 | 4.1533 | 3.3076 | 2.1111 | 0.52832 | -1.4264 | -6.8049 | -25.6401 | -34.8681 | -34.2867 | 9.6 | 13.35 | 13.35 | 13.3435 | 13.337 | 13.3292 | 13.3214 | 13.3149 | 13.3149 | 13.3149 | 13.3149 | 13.3149 | 13.3149 | 13.3149 | 1.7592 | 5.4853 | 5.4543 | 5.3964 | 5.3237 | 5.2342 | 5.1294 | 5.0074 | 4.8685 | 4.7084 | 4.0678 | -0.49668 | -4.6745 | -6.8952
LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON | MINIMUM HEADROOM | SU 86949 02632 | YES | 9.709 | 9.516 | 9.3398 | 9.1412 | 8.6971 | 8.3621 | 7.8788 | 7.423 | 6.7046 | 6.1248 | 2.7936 | -10.6875 | -26.7891 | -35.7127 | 14.1243 | 13.8888 | 13.6656 | 13.3985 | 12.8481 | 12.3848 | 11.6948 | 11.0099 | 9.9586 | 8.9439 | 6.0823 | -4.2263 | -16.8482 | -24.0119 | 8.2662 | 8.086 | 7.9218 | 7.7304 | 7.2944 | 6.663 | 5.7655 | 4.7053 | 3.3829 | 1.9467 | -1.762 | -14.6687 | -30.1828 | -38.8671
|  | HUNSTON | CT |  |  | 9.8023 | 9.7193 | 9.6337 | 9.542 | 9.0952 | 8.9538 | 8.6586 | 8.4255 | 7.931 | 7.6447 | 6.8721 | 4.2261 | 2.3886 | 1.2329 | 14.2667 | 14.1772 | 14.083 | 13.9743 | 13.4944 | 13.3117 | 12.9513 | 12.6551 | 12.0415 | 11.6655 | 10.9938 | 9.6083 | 7.9552 | 5.9624 | 8.3564 | 8.2829 | 8.2069 | 8.1241 | 7.6868 | 7.5553 | 7.2624 | 7.046 | 6.4424 | 5.7626 | 4.4916 | 2.3888 | 0.90552 | -0.19521
|  | HUNSTON | LW |  |  | 9.709 | 9.516 | 9.3398 | 9.1412 | 8.6971 | 8.3621 | 7.8788 | 7.423 | 6.7046 | 6.1248 | 2.7936 | -10.6875 | -26.7891 | -35.7127 | 14.1243 | 13.8888 | 13.6656 | 13.3985 | 12.8481 | 12.3848 | 11.6948 | 11.0099 | 9.9586 | 8.9439 | 6.0823 | -4.2263 | -16.8482 | -24.0119 | 8.2662 | 8.086 | 7.9218 | 7.7304 | 7.2944 | 6.663 | 5.7655 | 4.7053 | 3.3829 | 1.9467 | -1.762 | -14.6687 | -30.1828 | -38.8671
|  | HUNSTON | ST |  |  | 9.8231 | 9.7625 | 9.6973 | 9.5993 | 9.1536 | 9.0315 | 8.7489 | 8.5573 | 8.1019 | 7.8507 | 7.3172 | 6.2542 | 5.5479 | 4.926 | 14.3129 | 14.2663 | 14.2118 | 14.1112 | 13.6479 | 13.5156 | 13.1967 | 12.9938 | 12.4842 | 12.1971 | 11.5507 | 10.0283 | 9.1213 | 6.9418 | 8.377 | 8.3254 | 8.2692 | 8.1742 | 7.7347 | 7.6195 | 7.3358 | 7.1585 | 6.7032 | 6.4658 | 5.9631 | 4.332 | 3.0037 | 1.8478
|  | HUNSTON | FS |  |  | 9.8023 | 9.7193 | 9.6337 | 9.542 | 9.0952 | 8.9538 | 8.6586 | 8.4255 | 7.931 | 7.6447 | 6.8721 | 4.2261 | 2.3886 | 1.2329 | 14.3651 | 14.2842 | 14.2106 | 14.1321 | 13.916 | 13.7797 | 13.5768 | 13.401 | 13.1242 | 12.8879 | 12.3203 | 10.6919 | 8.4618 | 4.8065 | 8.4254 | 8.3384 | 8.2608 | 8.1823 | 7.9736 | 7.8447 | 7.6552 | 7.485 | 7.2256 | 7.0076 | 6.561 | 5.61 | 4.0854 | 2.7872
BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT | MINIMUM HEADROOM | SU 39384 52476 | YES | 0.63354 | 0.12667 | -0.38066 | -0.89837 | -1.6064 | -2.5651 | -3.7157 | -5.4402 | -7.5741 | -9.6843 | -14.5982 | -32.5579 | -42.0187 | -41.1708 | 1.7255 | 1.3794 | 0.96177 | 0.49013 | -0.039916 | -0.87787 | -1.8132 | -3.2482 | -4.9615 | -6.6509 | -10.3821 | -24.7275 | -32.1807 | -31.5939 | 0.72687 | 0.31761 | -0.096278 | -0.51109 | -1.1033 | -2.1536 | -3.3202 | -5.1066 | -7.2425 | -9.3432 | -14.153 | -31.508 | -40.6318 | -39.8679
|  | HURSTBOURNE TARRANT | CT |  |  | 0.65429 | 0.21182 | -0.31116 | -0.89837 | -1.5514 | -2.5651 | -3.686 | -5.4252 | -7.5741 | -9.6843 | -13.666 | -22.4529 | -25.6786 | -26.5492 | 1.7255 | 1.3794 | 0.96177 | 0.49013 | -0.039916 | -0.87787 | -1.8132 | -3.2482 | -4.9615 | -6.6509 | -9.8351 | -16.9101 | -19.5316 | -20.4413 | 0.77796 | 0.43567 | 0.035492 | -0.4346 | -1.1033 | -2.1536 | -3.3202 | -5.1066 | -7.2425 | -9.3432 | -13.3046 | -22.053 | -25.255 | -26.139
|  | HURSTBOURNE TARRANT | LW |  |  | 0.63354 | 0.12667 | -0.38066 | -0.89642 | -1.6064 | -2.3642 | -3.7157 | -5.4402 | -7.3732 | -9.5788 | -14.5982 | -32.5579 | -42.0187 | -41.1708 | 1.7732 | 1.4058 | 1.0417 | 0.64797 | 0.092438 | -0.4981 | -1.5949 | -2.999 | -4.5719 | -6.3654 | -10.3821 | -24.7275 | -32.1807 | -31.5939 | 0.72687 | 0.31761 | -0.096278 | -0.51109 | -1.0769 | -1.7974 | -3.1761 | -4.9365 | -6.9039 | -9.143 | -14.153 | -31.508 | -40.6318 | -39.8679
|  | HURSTBOURNE TARRANT | ST |  |  | 0.93421 | 0.76188 | 0.53465 | 0.21716 | -0.18317 | -0.69255 | -1.3471 | -2.1588 | -3.114 | -4.2884 | -7.5948 | -17.9459 | -24.3511 | -25.7564 | 1.9436 | 1.8164 | 1.6453 | 1.3944 | 1.0765 | 0.66536 | 0.12626 | -0.54589 | -1.3427 | -2.33 | -5.0234 | -13.3841 | -18.65 | -19.9924 | 0.99476 | 0.85722 | 0.67731 | 0.41976 | 0.10344 | -0.29259 | -0.87522 | -1.7142 | -2.7088 | -3.9374 | -7.282 | -17.5959 | -23.9984 | -25.4247
|  | HURSTBOURNE TARRANT | FS |  |  | 0.65429 | 0.21182 | -0.31116 | -0.89837 | -1.5514 | -2.5651 | -3.686 | -5.4252 | -7.5741 | -9.6843 | -13.666 | -22.4529 | -25.6786 | -26.5492 | 1.9662 | 1.8628 | 1.7266 | 1.5458 | 1.3165 | 1.0256 | 0.65997 | 0.2071 | -0.29903 | -0.90167 | -2.5772 | -8.9639 | -16.024 | -19.9505 | 1.036 | 0.9313 | 0.79434 | 0.60226 | 0.3684 | 0.079944 | -0.27057 | -0.75884 | -1.4005 | -2.1601 | -4.2555 | -12.2369 | -20.9764 | -25.7524
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE | MINIMUM HEADROOM | SU 63055 50105 | YES | 17.8855 | 17.6068 | 17.3413 | 16.8485 | 16.1699 | 15.4844 | 14.8 | 14.0942 | 13.2566 | 12.394 | 9.8986 | -0.87226 | -11.9328 | -17.8223 | 18.7505 | 18.6165 | 18.4921 | 18.2783 | 17.8969 | 17.4606 | 17.0835 | 16.7109 | 16.286 | 15.7272 | 14.0416 | 6.4498 | -1.6121 | -5.9545 | 16.6871 | 16.4355 | 16.1969 | 15.7561 | 15.1407 | 14.5125 | 13.8837 | 13.2337 | 12.4684 | 11.6786 | 9.4408 | -0.72395 | -11.2092 | -16.7931
|  | JAYS CLOSE | CT |  |  | 18.168 | 18.0569 | 17.9301 | 17.5589 | 16.9377 | 16.3195 | 15.8407 | 15.2595 | 14.2914 | 13.2446 | 9.8986 | -0.87226 | -11.9328 | -17.8223 | 18.8027 | 18.716 | 18.6163 | 18.4399 | 17.9954 | 17.4966 | 17.1968 | 16.8233 | 16.286 | 15.7272 | 14.0416 | 6.4498 | -1.6121 | -5.9545 | 16.9333 | 16.8293 | 16.7108 | 16.3762 | 15.8077 | 15.2315 | 14.7907 | 14.2507 | 13.3666 | 12.4732 | 9.4408 | -0.72395 | -11.2092 | -16.7931
|  | JAYS CLOSE | LW |  |  | 17.8855 | 17.6068 | 17.3413 | 16.8485 | 16.1699 | 15.4844 | 14.8 | 14.0942 | 13.2566 | 12.394 | 10.6039 | 6.7165 | 4.7859 | 4.3617 | 18.7505 | 18.6165 | 18.4921 | 18.2783 | 17.8969 | 17.4606 | 17.0835 | 16.7109 | 16.2911 | 15.8629 | 14.9627 | 13.075 | 12.2258 | 12.0963 | 16.6871 | 16.4355 | 16.1969 | 15.7561 | 15.1407 | 14.5125 | 13.8837 | 13.2337 | 12.4684 | 11.6786 | 10.036 | 6.5445 | 4.859 | 4.5477
|  | JAYS CLOSE | ST |  |  | 18.2994 | 18.2711 | 18.2335 | 18.1643 | 17.8572 | 17.5995 | 17.4641 | 17.2995 | 17.1155 | 16.8829 | 16.2863 | 13.209 | 11.2289 | 8.9477 | 18.887 | 18.8561 | 18.8164 | 18.755 | 18.4385 | 18.1156 | 17.9995 | 17.8656 | 17.7189 | 17.5163 | 16.9814 | 14.8501 | 12.7547 | 10.1609 | 17.064 | 17.0418 | 17.0119 | 16.9499 | 16.6558 | 16.3997 | 16.279 | 16.1341 | 15.9732 | 15.764 | 15.2114 | 12.6431 | 10.5786 | 8.5017
|  | JAYS CLOSE | FS |  |  | 18.168 | 18.0569 | 17.9301 | 17.5589 | 16.9377 | 16.3195 | 15.8407 | 15.2595 | 14.2914 | 13.2446 | 9.8986 | -0.87226 | -11.9328 | -17.8223 | 18.8877 | 18.8425 | 18.7956 | 18.7313 | 18.5698 | 18.3772 | 18.1863 | 17.9731 | 17.7292 | 17.4567 | 16.8061 | 14.4821 | 11.564 | 7.5818 | 17.0583 | 17.0162 | 16.9794 | 16.8894 | 16.7107 | 16.5164 | 16.3277 | 16.1103 | 15.8212 | 15.5037 | 14.7692 | 12.2518 | 9.6447 | 7.3776
COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON | MINIMUM HEADROOM | SP 52881 01094 | NO | 0.68211 | 0.45888 | 0.24824 | 0.027191 | -0.18199 | -0.40706 | -0.66096 | -1.3676 | -2.7854 | -4.48 | -8.4086 | -15.766 | -18.1369 | -19.6991 | 2.5007 | 2.3792 | 2.2645 | 2.1413 | 2.0192 | 1.8471 | 1.5013 | 0.69714 | -0.34714 | -1.6101 | -4.5579 | -9.9333 | -11.509 | -12.5985 | 1.3182 | 1.1299 | 0.94319 | 0.70412 | 0.46587 | 0.20197 | -0.097101 | -0.55904 | -1.9066 | -3.5206 | -7.2658 | -14.2423 | -16.4489 | -17.9079
|  | KENNINGTON | CT |  |  | 0.77577 | 0.60871 | 0.44155 | 0.25629 | 0.058552 | -0.19077 | -0.50311 | -1.3676 | -2.7854 | -4.48 | -8.4086 | -15.766 | -18.1369 | -19.6991 | 2.5252 | 2.4138 | 2.2969 | 2.1726 | 2.0312 | 1.8471 | 1.5013 | 0.69714 | -0.34714 | -1.6101 | -4.5579 | -9.9333 | -11.509 | -12.5985 | 1.4248 | 1.2935 | 1.1546 | 0.96044 | 0.74412 | 0.47358 | 0.13025 | -0.55904 | -1.9066 | -3.5206 | -7.2658 | -14.2423 | -16.4489 | -17.9079
|  | KENNINGTON | LW |  |  | 0.68211 | 0.45888 | 0.24824 | 0.027191 | -0.18199 | -0.40706 | -0.66096 | -0.94235 | -1.2718 | -2.168 | -4.5863 | -8.6107 | -9.914 | -10.759 | 2.5007 | 2.3792 | 2.2645 | 2.1413 | 2.0192 | 1.8805 | 1.7157 | 1.5294 | 1.0127 | 0.30404 | -1.4686 | -4.3556 | -5.1963 | -5.7878 | 1.3182 | 1.1299 | 0.94319 | 0.70412 | 0.46587 | 0.20197 | -0.097101 | -0.43376 | -0.83438 | -1.3063 | -3.5849 | -7.3878 | -8.5906 | -9.3741
|  | KENNINGTON | ST |  |  | 0.81777 | 0.68789 | 0.57178 | 0.51421 | 0.4729 | 0.42227 | 0.35146 | 0.29197 | 0.23888 | 0.18406 | 0.033213 | -0.83504 | -1.815 | -2.8109 | 2.5555 | 2.4717 | 2.3933 | 2.3388 | 2.294 | 2.2419 | 2.1731 | 2.1116 | 2.0579 | 1.9995 | 1.8459 | 1.1371 | 0.28698 | -0.79389 | 1.4702 | 1.3792 | 1.2962 | 1.2437 | 1.2051 | 1.161 | 1.0998 | 1.0533 | 1.0126 | 0.97097 | 0.86107 | 0.10022 | -0.83444 | -1.8836
|  | KENNINGTON | FS |  |  | 0.77577 | 0.60871 | 0.44155 | 0.25629 | 0.058552 | -0.19077 | -0.50311 | -1.3676 | -2.7854 | -4.48 | -8.4086 | -15.766 | -18.1369 | -19.6991 | 2.5687 | 2.4871 | 2.4118 | 2.3646 | 2.3241 | 2.2758 | 2.2243 | 2.1693 | 2.0991 | 2.024 | 1.8487 | 1.1518 | 0.12028 | -1.4254 | 1.4946 | 1.4147 | 1.3469 | 1.2996 | 1.2641 | 1.2202 | 1.1773 | 1.1341 | 1.0593 | 0.98374 | 0.82468 | 0.17476 | -0.64943 | -1.5666
BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL | MINIMUM HEADROOM | SU 67102 74048 | YES | 2.0305 | 1.7907 | 1.5262 | 1.1014 | 0.6768 | 0.073215 | -1.6962 | -4.7881 | -8.3764 | -12.2996 | -20.7213 | -38.4021 | -48.1921 | -52.472 | 6.2753 | 5.7636 | 5.2448 | 4.412 | 3.4444 | 2.2574 | 0.79268 | -1.4285 | -4.3236 | -7.2205 | -12.8557 | -26.9652 | -35.4295 | -46.3266 | 2.7249 | 1.9576 | 1.1802 | -0.21326 | -1.7842 | -3.4001 | -5.7277 | -8.5709 | -12.0304 | -15.8212 | -23.9666 | -40.9117 | -50.1295 | -54.1705
|  | KENTWOOD HILL | CT |  |  | 2.0305 | 1.7907 | 1.5262 | 1.1014 | 0.71633 | 0.073215 | -0.76914 | -2.9896 | -7.0744 | -11.1306 | -18.9818 | -38.4021 | -48.1921 | -52.472 | 6.3696 | 5.9059 | 5.3481 | 4.4258 | 3.533 | 2.2574 | 0.79268 | -1.4285 | -4.3236 | -7.2205 | -12.8557 | -26.9652 | -35.4295 | -42.3182 | 3.1572 | 2.6287 | 2.0008 | 0.70635 | -0.56166 | -2.2932 | -4.1999 | -7.0643 | -10.9856 | -14.8833 | -22.4141 | -40.9117 | -50.1295 | -54.1705
|  | KENTWOOD HILL | LW |  |  | 2.0897 | 1.8591 | 1.6641 | 1.2227 | 0.6768 | 0.098041 | -1.6962 | -4.7881 | -8.3764 | -12.2996 | -20.7213 | -36.288 | -42.0258 | -40.8465 | 6.2753 | 5.7636 | 5.2448 | 4.412 | 3.4444 | 2.44 | 0.85484 | -1.2703 | -3.7257 | -6.4477 | -12.3426 | -22.7746 | -26.4312 | -25.505 | 2.7249 | 1.9576 | 1.1802 | -0.21326 | -1.7842 | -3.4001 | -5.7277 | -8.5709 | -12.0304 | -15.8212 | -23.9666 | -38.8296 | -44.2661 | -43.1368
|  | KENTWOOD HILL | ST |  |  | 2.2051 | 2.1255 | 2.0524 | 1.8518 | 1.7244 | 1.5509 | 1.3174 | 1.0165 | 0.61773 | 0.13668 | -2.0601 | -17.7288 | -29.8531 | -35.8882 | 6.6398 | 6.4611 | 6.2578 | 5.8648 | 5.4878 | 4.9972 | 4.3608 | 3.5588 | 2.4757 | 1.0846 | -2.6939 | -15.6748 | -26.6429 | -34.6039 | 3.5384 | 3.3923 | 3.2235 | 2.8297 | 2.4526 | 1.9479 | 1.2705 | 0.40269 | -0.80395 | -2.335 | -6.5571 | -21.549 | -33.2316 | -39.3228
|  | KENTWOOD HILL | FS |  |  | 2.0305 | 1.7907 | 1.5262 | 1.1014 | 0.71633 | 0.073215 | -0.76914 | -2.9896 | -7.0744 | -11.1306 | -18.9818 | -38.4021 | -48.1921 | -52.472 | 6.6069 | 6.4026 | 6.1643 | 5.8117 | 5.4203 | 4.9203 | 4.3226 | 3.5583 | 2.512 | 1.2462 | -1.9823 | -14.0441 | -29.7632 | -46.3266 | 3.4963 | 3.3328 | 3.1321 | 2.758 | 2.3408 | 1.8002 | 1.1552 | 0.31455 | -0.85391 | -2.2301 | -5.7201 | -18.6907 | -33.4581 | -43.5596
COWLEY GSP | YARNTON BSP | KIDDINGTON | MINIMUM HEADROOM | SP 43362 24301 | NO | 11.2901 | 10.927 | 10.5769 | 10.1989 | 9.7122 | 9.0988 | 8.0951 | 6.3539 | 4.2532 | 2.205 | -1.8934 | -10.8641 | -14.4709 | -15.3709 | 12.5834 | 12.4579 | 12.2988 | 12.0959 | 11.8382 | 11.4574 | 10.9763 | 9.8467 | 8.2388 | 6.6347 | 3.6016 | -3.5964 | -7.3128 | -11.5353 | 11.4234 | 10.9613 | 10.4919 | 9.9076 | 9.2589 | 8.2452 | 7.1336 | 5.4102 | 3.3342 | 1.312 | -2.7261 | -11.5532 | -15.8801 | -20.9826
|  | KIDDINGTON | CT |  |  | 11.3494 | 11.051 | 10.6966 | 10.273 | 9.7989 | 9.0988 | 8.0951 | 6.3539 | 4.2532 | 2.205 | -1.6736 | -10.8641 | -14.4709 | -15.3709 | 12.5834 | 12.4579 | 12.2988 | 12.0959 | 11.8382 | 11.4574 | 10.9763 | 9.8467 | 8.2388 | 6.6347 | 3.6016 | -3.5964 | -6.404 | -7.2884 | 11.4234 | 11.0002 | 10.4919 | 9.9076 | 9.2589 | 8.2452 | 7.1336 | 5.4102 | 3.3342 | 1.312 | -2.5114 | -11.5532 | -15.0618 | -15.928
|  | KIDDINGTON | LW |  |  | 11.2901 | 10.927 | 10.5769 | 10.1989 | 9.7122 | 9.2138 | 8.214 | 6.5467 | 4.7023 | 2.6295 | -1.8934 | -9.1008 | -10.5309 | -8.2913 | 12.6341 | 12.5364 | 12.4436 | 12.3412 | 12.2014 | 12.0505 | 11.2703 | 10.1862 | 8.783 | 7.1617 | 3.6209 | -1.9473 | -2.9478 | -1.0827 | 11.4382 | 10.9613 | 10.4999 | 9.9942 | 9.3041 | 8.5923 | 7.277 | 5.6264 | 3.8018 | 1.7503 | -2.7261 | -9.8366 | -11.2147 | -8.9606
|  | KIDDINGTON | ST |  |  | 11.5425 | 11.4213 | 11.2731 | 11.0716 | 10.8224 | 10.5137 | 10.1181 | 9.6345 | 9.0217 | 7.9265 | 4.8993 | -4.8567 | -11.066 | -12.563 | 12.6825 | 12.6577 | 12.6238 | 12.5764 | 12.5091 | 12.4225 | 12.3117 | 12.1734 | 11.6686 | 10.9446 | 8.6805 | 0.87292 | -4.1069 | -5.3901 | 11.697 | 11.5435 | 11.3445 | 11.0731 | 10.7205 | 10.2642 | 9.6687 | 8.9149 | 8.0471 | 6.9615 | 3.9586 | -5.7173 | -11.8534 | -13.2912
|  | KIDDINGTON | FS |  |  | 11.3494 | 11.051 | 10.6966 | 10.273 | 9.7989 | 9.0988 | 8.0951 | 6.3539 | 4.2532 | 2.205 | -1.6736 | -10.8641 | -14.4709 | -15.3709 | 12.6741 | 12.6435 | 12.6056 | 12.5567 | 12.4922 | 12.413 | 12.3035 | 12.0145 | 11.4017 | 10.6799 | 8.4684 | 0.71514 | -7.3128 | -11.5353 | 11.653 | 11.4575 | 11.2253 | 10.9207 | 10.5281 | 10.0559 | 9.3963 | 8.5713 | 7.6485 | 6.5617 | 3.7097 | -5.9514 | -15.8801 | -20.9826
BRAMLEY (FLEE) | READING BSP | KIDMORE END | MINIMUM HEADROOM | SU 69953 78205 | YES | 4.7394 | 4.2796 | 3.8291 | 3.2428 | 2.5024 | 1.7401 | 0.50795 | -0.99597 | -2.7221 | -4.6329 | -8.7356 | -15.6484 | -19.474 | -21.0123 | 6.0311 | 5.753 | 5.4811 | 5.1015 | 4.6546 | 3.9824 | 3.2457 | 2.1345 | 0.75743 | -0.59624 | -3.5522 | -9.2367 | -12.2874 | -16.1762 | 4.6142 | 4.1786 | 3.7523 | 3.2112 | 2.5134 | 1.793 | 0.58893 | -0.89476 | -2.5983 | -4.4914 | -8.5652 | -15.2668 | -18.8497 | -21.5674
|  | KIDMORE END | CT |  |  | 4.8651 | 4.5195 | 4.1076 | 3.5393 | 2.9197 | 2.0274 | 1.056 | -0.37848 | -2.2467 | -4.074 | -7.4988 | -15.6484 | -19.474 | -21.0123 | 6.0404 | 5.791 | 5.4924 | 5.1015 | 4.6546 | 3.9824 | 3.2457 | 2.1345 | 0.75743 | -0.59624 | -3.1359 | -9.2367 | -12.2874 | -14.2057 | 4.6968 | 4.355 | 3.9463 | 3.4056 | 2.8148 | 1.9427 | 0.99169 | -0.43178 | -2.2553 | -4.0405 | -7.376 | -15.2668 | -18.8497 | -20.286
|  | KIDMORE END | LW |  |  | 4.7394 | 4.2796 | 3.8291 | 3.2428 | 2.5024 | 1.7401 | 0.50795 | -0.99597 | -2.7221 | -4.6329 | -8.7356 | -15.4697 | -17.4493 | -16.4208 | 6.0311 | 5.753 | 5.4811 | 5.1442 | 4.6617 | 4.1572 | 3.2743 | 2.1727 | 0.90873 | -0.50326 | -3.5522 | -8.4797 | -9.8407 | -9.0378 | 4.6142 | 4.1786 | 3.7523 | 3.2112 | 2.5134 | 1.793 | 0.58893 | -0.89476 | -2.5983 | -4.4914 | -8.5652 | -15.157 | -17.0667 | -16.0131
|  | KIDMORE END | ST |  |  | 5.0895 | 4.9541 | 4.7906 | 4.5574 | 4.2621 | 3.8837 | 3.4052 | 2.7897 | 2.062 | 1.1603 | -1.2997 | -9.6036 | -15.6281 | -18.0006 | 6.1893 | 6.0842 | 5.9537 | 5.7834 | 5.5664 | 5.2882 | 4.8982 | 4.3977 | 3.8065 | 3.0783 | 1.0954 | -5.5349 | -10.6098 | -13.032 | 4.9191 | 4.79 | 4.6305 | 4.4047 | 4.1148 | 3.7401 | 3.2615 | 2.6513 | 1.9268 | 1.03 | -1.4189 | -9.5537 | -15.5321 | -17.8614
|  | KIDMORE END | FS |  |  | 4.8651 | 4.5195 | 4.1076 | 3.5393 | 2.9197 | 2.0274 | 1.056 | -0.37848 | -2.2467 | -4.074 | -7.4988 | -15.6484 | -19.474 | -21.0123 | 6.1812 | 6.0753 | 5.9403 | 5.7763 | 5.5685 | 5.311 | 4.9594 | 4.5126 | 3.992 | 3.3755 | 1.6911 | -4.6167 | -11.5906 | -16.1762 | 4.9154 | 4.7962 | 4.6406 | 4.4241 | 4.1468 | 3.8018 | 3.372 | 2.8325 | 2.1793 | 1.4115 | -0.67942 | -8.4503 | -16.7552 | -21.5674
BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE | MINIMUM HEADROOM | SU 87551 61530 | YES | 10.6607 | 10.4002 | 10.1328 | 9.4443 | 8.6506 | 7.7735 | 6.6766 | 5.4153 | 3.9951 | 2.1235 | -4.6285 | -17.4842 | -21.6907 | -23.7705 | 14.1889 | 14.0231 | 13.8537 | 13.4873 | 13.043 | 12.5467 | 11.8556 | 11.0366 | 9.7503 | 7.716 | 2.7203 | -6.6344 | -9.4603 | -10.9031 | 11.0448 | 10.7955 | 10.5406 | 9.9366 | 9.2288 | 8.4448 | 7.4293 | 6.2502 | 4.9272 | 2.8227 | -3.5874 | -15.7792 | -19.7184 | -21.6683
|  | KINGS RIDE | CT |  |  | 10.8765 | 10.7414 | 10.5735 | 10.0207 | 9.406 | 8.6433 | 7.7977 | 6.7122 | 5.092 | 2.1235 | -4.6285 | -17.4842 | -21.6907 | -23.7705 | 14.2222 | 14.0764 | 13.8984 | 13.554 | 13.1671 | 12.6542 | 12.0777 | 11.2996 | 9.7503 | 7.716 | 2.7203 | -6.6344 | -9.4603 | -10.9031 | 11.222 | 11.0812 | 10.9072 | 10.4196 | 9.8753 | 9.1808 | 8.4069 | 7.3918 | 5.6376 | 2.8227 | -3.5874 | -15.7792 | -19.7184 | -21.6683
|  | KINGS RIDE | LW |  |  | 10.6607 | 10.4002 | 10.1328 | 9.4443 | 8.6506 | 7.7735 | 6.6766 | 5.4153 | 3.9951 | 2.4514 | -2.5085 | -11.5665 | -14.0494 | -15.3851 | 14.1889 | 14.0231 | 13.8537 | 13.4873 | 13.043 | 12.5467 | 11.8556 | 11.0366 | 10.1342 | 8.7715 | 4.5443 | -2.097 | -3.765 | -4.7519 | 11.0448 | 10.7955 | 10.5406 | 9.9366 | 9.2288 | 8.4448 | 7.4293 | 6.2502 | 4.9272 | 3.4802 | -1.5438 | -10.1552 | -12.4819 | -13.7444
|  | KINGS RIDE | ST |  |  | 11.0363 | 11.0156 | 10.9867 | 10.7672 | 10.5312 | 10.2652 | 9.96 | 9.6072 | 9.211 | 8.7049 | 7.3031 | 3.2292 | 0.38807 | -1.601 | 14.3201 | 14.2586 | 14.18 | 13.9827 | 13.7646 | 13.5102 | 13.2059 | 12.8534 | 12.4609 | 11.9889 | 10.7869 | 7.2632 | 4.4925 | 1.972 | 11.3711 | 11.3428 | 11.3036 | 11.1045 | 10.887 | 10.6354 | 10.3351 | 9.9858 | 9.5901 | 9.1099 | 7.8863 | 4.1039 | 1.4213 | -0.23038
|  | KINGS RIDE | FS |  |  | 10.8765 | 10.7414 | 10.5735 | 10.0207 | 9.406 | 8.6433 | 7.7977 | 6.7122 | 5.092 | 2.1235 | -4.6285 | -17.4842 | -21.6907 | -23.7705 | 14.3195 | 14.2608 | 14.1853 | 14.0268 | 13.8486 | 13.6411 | 13.4005 | 13.1218 | 12.8123 | 12.4611 | 11.5725 | 8.4849 | 4.4624 | -0.13059 | 11.3665 | 11.3498 | 11.3184 | 11.1602 | 10.9888 | 10.7867 | 10.5587 | 10.2937 | 9.9755 | 9.6211 | 8.7464 | 5.8471 | 2.5219 | -0.06913
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE | MINIMUM HEADROOM | SU 51982 59358 | YES | 1.3018 | 0.65876 | 0.033064 | -0.73523 | -1.6219 | -2.993 | -4.5348 | -6.8699 | -9.696 | -12.5065 | -18.0658 | -34.1262 | -46.0932 | -52.9194 | 2.3876 | 1.9415 | 1.4023 | 0.78238 | 0.086361 | -1.0109 | -2.245 | -4.133 | -6.3918 | -8.6366 | -12.924 | -25.3181 | -34.6366 | -40.0363 | 1.2639 | 0.65813 | 0.01186 | -0.78198 | -1.6653 | -3.053 | -4.6061 | -6.9847 | -9.8478 | -12.6737 | -18.1821 | -33.316 | -44.841 | -51.4456
|  | KINGSCLERE | CT |  |  | 1.3033 | 0.73826 | 0.061492 | -0.73523 | -1.6219 | -2.993 | -4.5348 | -6.8699 | -9.696 | -12.5065 | -17.9121 | -34.1262 | -46.0932 | -52.9194 | 2.3876 | 1.9415 | 1.4023 | 0.78238 | 0.086361 | -1.0109 | -2.245 | -4.133 | -6.3918 | -8.6366 | -12.924 | -25.3181 | -34.6366 | -40.0363 | 1.2639 | 0.69535 | 0.01186 | -0.78198 | -1.6653 | -3.053 | -4.6061 | -6.9847 | -9.8478 | -12.6737 | -18.0261 | -33.316 | -44.841 | -51.4456
|  | KINGSCLERE | LW |  |  | 1.3018 | 0.65876 | 0.033064 | -0.64717 | -1.5706 | -2.53 | -4.2637 | -6.4499 | -8.9111 | -11.7751 | -18.0658 | -28.6754 | -31.5236 | -28.9911 | 2.453 | 1.9825 | 1.5244 | 1.0193 | 0.31344 | -0.42248 | -1.8024 | -3.5564 | -5.5117 | -7.7462 | -12.7244 | -21.046 | -23.3042 | -21.3874 | 1.2831 | 0.65813 | 0.049774 | -0.62548 | -1.5569 | -2.5249 | -4.3135 | -6.5785 | -9.0992 | -11.9411 | -18.1821 | -28.6743 | -31.5166 | -29.0703
|  | KINGSCLERE | ST |  |  | 1.6761 | 1.4701 | 1.2069 | 0.80722 | 0.30856 | -0.32956 | -1.1592 | -2.1914 | -3.4098 | -4.9217 | -9.257 | -22.9494 | -31.7367 | -33.9987 | 2.6705 | 2.5084 | 2.295 | 1.9649 | 1.5558 | 1.0297 | 0.33792 | -0.51696 | -1.5313 | -2.7876 | -6.2309 | -17.3523 | -24.6244 | -26.7815 | 1.6348 | 1.4321 | 1.1676 | 0.75831 | 0.24621 | -0.41359 | -1.2789 | -2.356 | -3.6361 | -5.226 | -9.5655 | -23.2206 | -32.0105 | -34.296
|  | KINGSCLERE | FS |  |  | 1.3033 | 0.73826 | 0.061492 | -0.73523 | -1.6219 | -2.993 | -4.5348 | -6.8699 | -9.696 | -12.5065 | -17.9121 | -34.1262 | -46.0932 | -52.9194 | 2.6922 | 2.5552 | 2.3758 | 2.1385 | 1.8378 | 1.4568 | 0.98031 | 0.38528 | -0.28159 | -1.0712 | -3.2422 | -11.6469 | -21.2016 | -26.8047 | 1.6716 | 1.5089 | 1.2931 | 0.99402 | 0.61413 | 0.13482 | -0.46267 | -1.2103 | -2.0591 | -3.0635 | -5.815 | -16.3081 | -28.0111 | -34.5875
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY | MINIMUM HEADROOM | SU 37657 67143 | YES | 2.9506 | 2.6578 | 2.2671 | 1.8681 | 1.4548 | 1.0153 | 0.4996 | 0.030098 | -1.0421 | -2.15 | -2.284 | -2.15 | -2.258 | -2.284 | 4.287 | 3.5204 | 2.5876 | 1.5319 | 0.39071 | -1.4528 | -3.4758 | -6.7028 | -10.5943 | -14.3203 | -22.7559 | 2.7694 | 2.7238 | 2.4138 | 3.0573 | 2.1093 | 0.96116 | -0.32911 | -1.7333 | -4.0317 | -6.5698 | -10.6432 | -15.4774 | -20.1062 | -30.7531 | -1.0825 | -1.1768 | -1.1985
|  | KINTBURY | CT |  |  | 3.5486 | 3.3933 | 3.172 | 2.9419 | 2.6908 | 2.4143 | 2.1125 | 1.7072 | 0.87769 | -0.39653 | -0.78035 | -0.39653 | -0.69487 | -0.78035 | 4.287 | 3.5204 | 2.5876 | 1.5319 | 0.39071 | -1.4528 | -3.4758 | -6.7028 | -10.5943 | -14.3203 | -21.1736 | 3.3127 | 3.1076 | 2.9327 | 3.0573 | 2.1093 | 0.96116 | -0.32911 | -1.7333 | -4.0317 | -6.5698 | -10.6432 | -15.4774 | -20.1062 | -28.6161 | 0.41907 | 0.17277 | 0.10358
|  | KINTBURY | LW |  |  | 2.9506 | 2.6578 | 2.2671 | 1.8681 | 1.4548 | 1.0153 | 0.4996 | 0.030098 | -1.0421 | -2.15 | -2.284 | -2.15 | -2.258 | -2.284 | 4.3915 | 3.6019 | 2.7981 | 1.9103 | 0.6682 | -0.6275 | -3.1081 | -6.3029 | -9.8852 | -13.9286 | -22.7559 | 2.7694 | 2.7238 | 2.7118 | 3.1633 | 2.1216 | 1.0978 | -0.0017326 | -1.5244 | -3.138 | -6.2345 | -10.2901 | -14.7475 | -19.777 | -30.7531 | -1.0825 | -1.1768 | -1.1985
|  | KINTBURY | ST |  |  | 3.7289 | 3.6382 | 3.4969 | 3.3509 | 3.2016 | 3.0412 | 2.8674 | 2.6842 | 1.9289 | 0.91494 | 0.044702 | 0.91494 | 0.38385 | 0.044702 | 4.7128 | 4.4801 | 4.1607 | 3.6539 | 3.0045 | 2.1474 | 1.0246 | -0.4244 | -2.0945 | -4.2063 | -10.2273 | 3.8407 | 3.5357 | 3.268 | 3.6761 | 3.3373 | 2.8957 | 2.2682 | 1.464 | 0.41466 | -0.94977 | -2.7454 | -4.8273 | -7.5155 | -15.013 | 1.5154 | 1.074 | 0.79926
|  | KINTBURY | FS |  |  | 3.5486 | 3.3933 | 3.172 | 2.9419 | 2.6908 | 2.4143 | 2.1125 | 1.7072 | 0.87769 | -0.39653 | -0.78035 | -0.39653 | -0.69487 | -0.78035 | 4.7369 | 4.5369 | 4.279 | 3.876 | 3.3636 | 2.713 | 1.8832 | 0.83717 | -0.3174 | -1.7021 | -5.6082 | 3.3503 | 2.8146 | 2.4138 | 3.7212 | 3.4365 | 3.0726 | 2.5674 | 1.9308 | 1.1325 | 0.1224 | -1.1485 | -2.5918 | -4.3215 | -9.2656 | 0.4665 | -0.45559 | -1.0736
BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL | MINIMUM HEADROOM | SU 82849 79105 | YES | 0.99704 | 0.23605 | -0.68586 | -1.7238 | -2.8794 | -4.7352 | -6.7782 | -9.9774 | -13.7689 | -17.4095 | -25.5474 | -39.2302 | -44.4809 | -45.9267 | 1.6063 | 1.231 | 0.53652 | -0.24764 | -1.1238 | -2.5896 | -4.235 | -6.8061 | -9.8399 | -12.7535 | -19.2632 | -30.2236 | -34.4261 | -39.7219 | 0.43224 | -0.30355 | -1.1948 | -2.2007 | -3.322 | -5.1211 | -7.1053 | -10.2046 | -13.9446 | -17.5628 | -25.7024 | -39.2396 | -44.4382 | -50.8398
|  | KNOWL HILL | CT |  |  | 0.99704 | 0.23605 | -0.68586 | -1.7238 | -2.8794 | -4.7352 | -6.7782 | -9.9774 | -13.7689 | -17.4095 | -24.107 | -39.2302 | -44.4809 | -45.9267 | 1.6063 | 1.231 | 0.53652 | -0.24764 | -1.1238 | -2.5896 | -4.235 | -6.8061 | -9.8399 | -12.7535 | -18.1081 | -30.2236 | -34.4261 | -35.6975 | 0.43224 | -0.30355 | -1.1948 | -2.2007 | -3.322 | -5.1211 | -7.1053 | -10.2046 | -13.9446 | -17.5628 | -24.2151 | -39.2396 | -44.4382 | -45.8663
|  | KNOWL HILL | LW |  |  | 1.1141 | 0.29031 | -0.51069 | -1.4209 | -2.7012 | -4.0416 | -6.5536 | -9.7306 | -13.1746 | -17.0666 | -25.5474 | -38.7183 | -40.7149 | -36.0199 | 1.6437 | 1.3025 | 0.7116 | 0.016504 | -0.95947 | -2.0022 | -4.0326 | -6.5925 | -9.3517 | -12.4682 | -19.2632 | -29.7918 | -31.3417 | -27.54 | 0.54435 | -0.25215 | -1.0268 | -1.9172 | -3.1667 | -4.4788 | -6.924 | -10.0095 | -13.3906 | -17.2634 | -25.7024 | -38.8017 | -40.7723 | -36.0857
|  | KNOWL HILL | ST |  |  | 1.4961 | 1.2326 | 0.88029 | 0.36041 | -0.30804 | -1.1779 | -2.3249 | -3.7689 | -5.4189 | -7.4986 | -13.2469 | -31.6015 | -43.0111 | -45.2765 | 1.72 | 1.6706 | 1.6031 | 1.3042 | 0.78921 | 0.12237 | -0.76071 | -1.8807 | -3.2007 | -4.868 | -9.485 | -24.2531 | -33.4517 | -35.3505 | 0.91443 | 0.65954 | 0.31882 | -0.19536 | -0.84918 | -1.6965 | -2.8154 | -4.2149 | -5.8077 | -7.8153 | -13.4565 | -31.7263 | -43.0752 | -45.3133
|  | KNOWL HILL | FS |  |  | 0.99704 | 0.23605 | -0.68586 | -1.7238 | -2.8794 | -4.7352 | -6.7782 | -9.9774 | -13.7689 | -17.4095 | -24.107 | -39.2302 | -44.4809 | -45.9267 | 1.7173 | 1.6692 | 1.6068 | 1.4034 | 0.98545 | 0.44971 | -0.24053 | -1.1086 | -2.1093 | -3.3063 | -6.5903 | -18.8657 | -32.406 | -39.7219 | 0.9114 | 0.66642 | 0.35782 | -0.064601 | -0.59876 | -1.2818 | -2.164 | -3.2688 | -4.4988 | -5.9451 | -9.9026 | -25.1177 | -41.8608 | -50.8398
BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD | MINIMUM HEADROOM | SU 86017 50475 | YES | 13.1058 | 12.7306 | 12.121 | 10.5835 | 8.8444 | 7.76 | 6.4502 | 5.0311 | 3.4749 | 2.0181 | -0.68526 | -7.7078 | -10.3003 | -11.8717 | 19.7815 | 19.3849 | 19.035 | 18.2735 | 17.3524 | 16.7178 | 16.0074 | 15.1586 | 14.0416 | 12.9387 | 11.16 | 5.4008 | -5.8907 | -27.0806 | 14.259 | 13.675 | 13.148 | 11.8562 | 10.364 | 9.4139 | 8.2798 | 7.051 | 5.7067 | 4.4514 | 3.0095 | -1.8778 | -4.2287 | -5.6555
|  | LABURNAM ROAD | CT |  |  | 13.1058 | 12.7306 | 12.4383 | 11.5617 | 10.0724 | 9.138 | 8.0237 | 6.6653 | 4.7825 | 2.9519 | -0.68526 | -7.7078 | -10.3003 | -11.8717 | 19.7946 | 19.3849 | 19.035 | 18.2735 | 17.3524 | 16.7178 | 16.0074 | 15.1586 | 14.0416 | 12.9387 | 11.16 | 5.9487 | -0.56674 | -10.7925 | 14.5468 | 14.1166 | 13.7703 | 12.7086 | 11.4183 | 10.6099 | 9.6582 | 8.497 | 6.8752 | 5.3055 | 3.1746 | -1.8778 | -4.2287 | -5.6555
|  | LABURNAM ROAD | LW |  |  | 13.1136 | 12.7327 | 12.121 | 10.5835 | 8.8444 | 7.76 | 6.4502 | 5.0311 | 3.4749 | 2.0181 | 0.38666 | -2.9849 | -4.722 | -5.3284 | 19.7815 | 19.4125 | 19.097 | 18.3571 | 17.5086 | 17.0027 | 16.407 | 15.7704 | 15.0704 | 14.4348 | 13.7437 | 12.3997 | 11.7515 | 11.5069 | 14.259 | 13.675 | 13.148 | 11.8562 | 10.364 | 9.4139 | 8.2798 | 7.051 | 5.7067 | 4.4514 | 3.0095 | 0.051689 | -1.4198 | -1.8925
|  | LABURNAM ROAD | ST |  |  | 13.1576 | 12.8265 | 12.5843 | 12.0285 | 11.3668 | 11.0306 | 10.6843 | 10.2773 | 9.7536 | 9.2763 | 8.6923 | 6.2668 | 5.1261 | 2.7154 | 19.8791 | 19.5186 | 19.2204 | 18.6336 | 17.9292 | 17.4932 | 17.0253 | 16.4883 | 15.8149 | 15.1464 | 14.0319 | 10.0422 | 4.0123 | -6.2502 | 14.7563 | 14.4399 | 14.2124 | 13.6133 | 12.8944 | 12.5845 | 12.2476 | 11.8457 | 11.3165 | 10.8091 | 10.3088 | 8.5921 | 7.1426 | 5.1506
|  | LABURNAM ROAD | FS |  |  | 13.1058 | 12.7306 | 12.4383 | 11.5617 | 10.0724 | 9.138 | 8.0237 | 6.6653 | 4.7825 | 2.9519 | -0.68526 | -7.7078 | -10.3003 | -11.8717 | 19.8414 | 19.4903 | 19.14 | 18.4792 | 17.7417 | 17.1663 | 16.4899 | 15.7057 | 14.8069 | 13.8687 | 12.0203 | 5.4008 | -5.8907 | -27.0806 | 14.718 | 14.4578 | 14.2228 | 13.6251 | 12.9712 | 12.5805 | 12.1196 | 11.552 | 10.9122 | 10.2828 | 9.376 | 6.7728 | 4.4702 | 2.3136
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN | MINIMUM HEADROOM | SU 33280 78217 | YES | -2.7166 | -3.1937 | -3.8505 | -4.778 | -5.9898 | -7.8203 | -10.2379 | -13.641 | -18.0654 | -23.6698 | -37.5856 | -66.293 | -78.164 | -83.6481 | 0.14779 | -0.31461 | -1.0085 | -1.8242 | -2.7174 | -4.1651 | -5.775 | -8.4513 | -11.8402 | -16.243 | -27.0848 | -49.3999 | -58.5204 | -62.7551 | -3.0648 | -3.5266 | -4.162 | -5.0567 | -6.2257 | -7.9938 | -10.3898 | -13.7953 | -18.1754 | -23.6161 | -36.9871 | -64.5644 | -75.9403 | -81.1935
|  | LAMBOURN | CT |  |  | -2.7166 | -3.1937 | -3.8505 | -4.778 | -5.9898 | -7.8203 | -10.2379 | -13.641 | -18.0654 | -23.6698 | -37.5856 | -66.293 | -78.164 | -83.6481 | 0.14779 | -0.31461 | -1.0085 | -1.8242 | -2.7174 | -4.1651 | -5.775 | -8.4513 | -11.8402 | -16.243 | -27.0848 | -49.3999 | -58.5204 | -62.7551 | -3.0648 | -3.5266 | -4.162 | -5.0567 | -6.2257 | -7.9938 | -10.3898 | -13.7953 | -18.1754 | -23.6161 | -36.9871 | -64.5644 | -75.9403 | -81.1935
|  | LAMBOURN | LW |  |  | -2.517 | -2.8505 | -3.4291 | -4.252 | -5.3619 | -6.661 | -8.9392 | -11.8199 | -15.0403 | -18.6841 | -26.7733 | -39.9347 | -42.6931 | -40.6918 | 0.31296 | -0.25304 | -0.84461 | -1.5257 | -2.4702 | -3.4847 | -5.3301 | -7.6752 | -10.2839 | -13.2387 | -19.7419 | -30.1103 | -32.081 | -29.0852 | -2.8705 | -3.1941 | -3.5567 | -4.0516 | -4.8838 | -6.1534 | -8.4784 | -11.4246 | -14.7062 | -18.4173 | -26.5705 | -39.6568 | -42.2473 | -39.9282
|  | LAMBOURN | ST |  |  | -1.832 | -1.9065 | -2.0169 | -2.3151 | -2.8413 | -3.5474 | -4.4357 | -5.6946 | -7.149 | -8.9766 | -14.0629 | -30.6552 | -41.068 | -43.364 | 0.76281 | 0.5688 | 0.30659 | -0.073378 | -0.54743 | -1.2017 | -2.0162 | -3.0663 | -4.2822 | -5.8153 | -10.0445 | -23.5546 | -31.9174 | -33.8552 | -2.2135 | -2.2822 | -2.3898 | -2.5729 | -2.7647 | -3.1537 | -4.0901 | -5.394 | -6.9049 | -8.8079 | -14.0453 | -30.7773 | -41.0908 | -43.315
|  | LAMBOURN | FS |  |  | -2.7166 | -3.1937 | -3.8505 | -4.778 | -5.9898 | -7.8203 | -10.2379 | -13.641 | -18.0654 | -23.6698 | -37.5856 | -66.293 | -78.164 | -83.6481 | 1.0688 | 0.83574 | 0.54254 | 0.16261 | -0.31789 | -0.94647 | -1.7509 | -2.7889 | -3.954 | -5.3094 | -8.8915 | -21.5731 | -34.7715 | -41.9568 | -1.1815 | -1.2444 | -1.3264 | -1.4976 | -2.012 | -2.7307 | -3.7282 | -5.0136 | -6.4674 | -8.1559 | -12.6036 | -28.3371 | -44.5757 | -53.1454
FAWLEY GSP | LANGLEY BSP | LANGLEY | MINIMUM HEADROOM | SU 45158 01418 | YES | 2.8773 | 1.2839 | -1.3101 | -11.0352 | -22.0125 | -36.7569 | -52.8961 | -67.5393 | -75.5855 | -84.0128 | -99.1993 | -136.241 | -144.3113 | -143.9768 | -0.31452 | -2.2882 | -5.5086 | -17.6447 | -31.2642 | -49.5741 | -69.5758 | -86.8707 | -95.5428 | -104.6234 | -120.5729 | -162.1298 | -170.8512 | -170.9637 | 0.22138 | -1.7885 | -5.0452 | -17.2397 | -30.9646 | -49.3898 | -69.5428 | -87.0609 | -96.0171 | -105.3841 | -122.508 | -166.1459 | -175.7559 | -176.0577
|  | LANGLEY | CT |  |  | 3.8153 | 3.5298 | 3.073 | 1.6924 | -0.78554 | -3.7603 | -8.9385 | -12.6558 | -15.3937 | -20.1158 | -28.7358 | -49.4086 | -54.9628 | -56.133 | 0.87324 | 0.53385 | -0.012695 | -1.718 | -4.7307 | -8.3372 | -14.685 | -19.1493 | -21.5956 | -26.0688 | -34.114 | -54.4649 | -58.8445 | -59.581 | 1.4446 | 1.0913 | 0.52939 | -1.2136 | -4.3015 | -7.9959 | -14.4388 | -18.9828 | -21.5759 | -26.3335 | -35.1627 | -57.961 | -63.6357 | -64.6581
|  | LANGLEY | LW |  |  | 2.8773 | 1.2839 | -1.3101 | -11.0352 | -22.0125 | -36.7569 | -52.8961 | -67.5393 | -75.5855 | -84.0128 | -99.1993 | -136.241 | -144.3113 | -143.9768 | -0.31452 | -2.2882 | -5.5086 | -17.6447 | -31.2642 | -49.5741 | -69.5758 | -86.8707 | -95.5428 | -104.6234 | -120.5729 | -162.1298 | -170.8512 | -170.9637 | 0.22138 | -1.7885 | -5.0452 | -17.2397 | -30.9646 | -49.3898 | -69.5428 | -87.0609 | -96.0171 | -105.3841 | -122.508 | -166.1459 | -175.7559 | -176.0577
|  | LANGLEY | ST |  |  | 3.0535 | 2.1599 | 0.23605 | -9.3262 | -15.891 | -21.8304 | -30.8039 | -35.3838 | -38.6925 | -41.6469 | -47.8159 | -67.0471 | -73.9842 | -75.9814 | -0.095817 | -1.2128 | -3.6154 | -15.5632 | -23.7022 | -31.0554 | -42.1991 | -47.8289 | -51.8072 | -55.3129 | -62.6307 | -82.4803 | -88.0177 | -88.8485 | 0.49203 | -0.62632 | -3.0304 | -14.985 | -23.1597 | -30.5519 | -41.7331 | -47.3637 | -51.3614 | -54.9012 | -62.3534 | -82.5565 | -88.8223 | -90.525
|  | LANGLEY | FS |  |  | 3.8153 | 3.5298 | 3.073 | 1.6924 | -0.78554 | -3.7603 | -8.9385 | -12.6558 | -15.3937 | -20.1158 | -28.7358 | -49.4086 | -54.9628 | -56.133 | 1.0198 | 0.98266 | 0.92275 | -1.7109 | -4.3885 | -7.6168 | -10.858 | -13.7342 | -15.3931 | -17.0671 | -20.4062 | -23.6388 | -25.8739 | -28.2909 | 1.6109 | 1.5749 | 1.5162 | -1.1239 | -3.8343 | -7.0974 | -10.3754 | -13.2864 | -14.9882 | -16.7071 | -20.1582 | -23.6706 | -27.7585 | -30.5403
BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT | MINIMUM HEADROOM | SU 80847 29056 | YES | 12.6886 | 12.1811 | 11.6922 | 11.1918 | 10.554 | 9.8793 | 8.822 | 7.5268 | 6.0641 | 4.4267 | 0.8373 | -19.6079 | -35.6797 | -40.6115 | 14.6123 | 14.3029 | 14.007 | 13.685 | 13.2701 | 12.7113 | 12.0587 | 11.1061 | 9.9443 | 8.7835 | 6.2077 | -9.4956 | -21.795 | -25.5393 | 12.4283 | 12.0011 | 11.5836 | 11.1411 | 10.5338 | 9.8897 | 8.8653 | 7.6057 | 6.1881 | 4.5982 | 1.1097 | -18.1911 | -33.559 | -38.2621
|  | LANGLEY COURT | CT |  |  | 12.8274 | 12.4341 | 12.0041 | 11.5106 | 10.9555 | 10.169 | 9.2976 | 8.0499 | 6.4703 | 4.8933 | 0.97129 | -19.6079 | -35.6797 | -40.6115 | 14.6215 | 14.3447 | 14.0319 | 13.685 | 13.2923 | 12.7113 | 12.0616 | 11.1061 | 9.9443 | 8.7835 | 6.2666 | -9.4956 | -21.795 | -25.5393 | 12.5691 | 12.2492 | 11.8742 | 11.4027 | 10.8735 | 10.1151 | 9.2738 | 8.0583 | 6.5287 | 5.0034 | 1.504 | -18.1911 | -33.559 | -38.2621
|  | LANGLEY COURT | LW |  |  | 12.6886 | 12.1811 | 11.6922 | 11.1918 | 10.554 | 9.8793 | 8.822 | 7.5268 | 6.0641 | 4.4267 | 0.8373 | -7.0035 | -10.5948 | -11.1226 | 14.6123 | 14.3029 | 14.007 | 13.6916 | 13.2701 | 12.8189 | 12.0587 | 11.1104 | 10.0512 | 8.8533 | 6.2077 | 0.42182 | -2.2083 | -2.5564 | 12.4283 | 12.0011 | 11.5836 | 11.1411 | 10.5338 | 9.8897 | 8.8653 | 7.6057 | 6.1881 | 4.5982 | 1.1097 | -6.0921 | -9.4981 | -9.9782
|  | LANGLEY COURT | ST |  |  | 13.0576 | 12.8516 | 12.6418 | 12.4084 | 12.1092 | 11.7494 | 11.2931 | 10.7555 | 10.1477 | 9.4122 | 7.4199 | 0.9225 | -3.4419 | -5.098 | 14.7824 | 14.6473 | 14.4993 | 14.3257 | 14.1048 | 13.8309 | 13.4802 | 13.0573 | 12.5775 | 11.9852 | 10.3666 | 5.0036 | 1.3579 | -0.16582 | 12.7704 | 12.6049 | 12.435 | 12.2374 | 11.9845 | 11.6387 | 11.198 | 10.6751 | 10.0831 | 9.3582 | 7.364 | 0.87803 | -3.3985 | -4.8534
|  | LANGLEY COURT | FS |  |  | 12.8274 | 12.4341 | 12.0041 | 11.5106 | 10.9555 | 10.169 | 9.2976 | 8.0499 | 6.4703 | 4.8933 | 0.97129 | -19.6079 | -35.6797 | -40.6115 | 14.768 | 14.6139 | 14.4491 | 14.2626 | 14.0285 | 13.7501 | 13.3731 | 12.9092 | 12.3931 | 11.7905 | 10.2242 | 4.8016 | -0.88821 | -4.4527 | 12.7897 | 12.6278 | 12.4646 | 12.2433 | 11.9442 | 11.5934 | 11.1321 | 10.5641 | 9.912 | 9.1559 | 7.2139 | 0.62248 | -6.0269 | -9.6967
AXMINSTER | YEOVIL BSP | LARKHILL | MINIMUM HEADROOM | ST 53677 16914 | YES | 12.0248 | 11.4564 | 10.9371 | 10.1746 | 9.2499 | 8.306 | 6.8247 | 5.0311 | 2.676 | 0.1935 | -5.1744 | -14.9472 | -19.7883 | -21.6394 | 14.2801 | 13.9422 | 13.651 | 13.2591 | 12.7606 | 11.9498 | 10.9076 | 9.352 | 7.2906 | 5.4036 | 1.864 | -6.5424 | -10.9673 | -21.2603 | 12.5867 | 12.0427 | 11.5453 | 10.8286 | 9.9504 | 8.9934 | 7.4239 | 5.5005 | 3.1842 | 0.76596 | -4.4701 | -13.8758 | -18.3905 | -20.0645
|  | LARKHILL | CT |  |  | 12.2555 | 11.8983 | 11.4639 | 10.781 | 10.0339 | 8.9443 | 7.7311 | 5.9127 | 3.2149 | 0.7253 | -3.9219 | -14.9472 | -19.7883 | -21.6394 | 14.3684 | 14.1324 | 13.8469 | 13.4488 | 12.8771 | 11.9498 | 10.9076 | 9.352 | 7.2906 | 5.4036 | 1.8818 | -6.5424 | -10.9673 | -14.7873 | 12.784 | 12.4312 | 12.0022 | 11.3303 | 10.5581 | 9.4022 | 8.1164 | 6.2184 | 3.6091 | 1.1973 | -3.2981 | -13.8758 | -18.3905 | -20.0645
|  | LARKHILL | LW |  |  | 12.0248 | 11.4564 | 10.9371 | 10.1746 | 9.2499 | 8.306 | 6.8247 | 5.0311 | 2.676 | 0.1935 | -5.1744 | -14.6139 | -17.5618 | -15.9804 | 14.2801 | 13.9422 | 13.651 | 13.2591 | 12.7606 | 12.1175 | 10.9478 | 9.4761 | 7.7065 | 5.8683 | 1.864 | -4.8235 | -6.4452 | -4.8365 | 12.5867 | 12.0427 | 11.5453 | 10.8286 | 9.9504 | 8.9934 | 7.4239 | 5.5005 | 3.1842 | 0.76596 | -4.4701 | -13.5402 | -16.2399 | -14.5481
|  | LARKHILL | ST |  |  | 12.5342 | 12.4278 | 12.2882 | 12.082 | 11.8064 | 11.4187 | 10.8843 | 10.2145 | 9.2984 | 8.3454 | 5.405 | -5.139 | -12.596 | -15.4659 | 14.526 | 14.4365 | 14.3219 | 14.1616 | 13.9576 | 13.6743 | 13.22 | 12.5281 | 11.6007 | 10.6097 | 7.9597 | -1.116 | -8.0441 | -12.2669 | 13.055 | 12.9496 | 12.8104 | 12.6041 | 12.3292 | 11.9421 | 11.3435 | 10.5891 | 9.5954 | 8.4993 | 5.395 | -5.2059 | -12.473 | -15.1181
|  | LARKHILL | FS |  |  | 12.2555 | 11.8983 | 11.4639 | 10.781 | 10.0339 | 8.9443 | 7.7311 | 5.9127 | 3.2149 | 0.7253 | -3.9219 | -14.9472 | -19.7883 | -21.6394 | 14.536 | 14.3988 | 14.2549 | 14.0772 | 13.8523 | 13.5814 | 13.2326 | 12.6305 | 11.8425 | 10.9749 | 8.7532 | 0.4025 | -10.4154 | -21.2603 | 13.0515 | 12.9085 | 12.7471 | 12.5268 | 12.2453 | 11.8897 | 11.3993 | 10.7593 | 9.9318 | 9.0262 | 6.6843 | -2.3219 | -12.3589 | -18.4176
COWLEY GSP | WITNEY BSP | LEAFIELD | MINIMUM HEADROOM | SP 30282 15270 | NO | 1.0677 | 1.0334 | 0.95017 | 0.82117 | 0.68762 | 0.55331 | 0.38664 | 0.19886 | -0.052743 | -0.54798 | -2.1139 | -7.6365 | -10.4777 | -10.5953 | 1.7558 | 1.7154 | 1.675 | 1.6168 | 1.5541 | 1.4881 | 1.4056 | 1.2992 | 1.1055 | 0.64965 | -0.61127 | -4.7929 | -6.9992 | -7.1732 | 0.86808 | 0.7889 | 0.71085 | 0.59689 | 0.47853 | 0.35894 | 0.22185 | -0.026159 | -0.46602 | -1.0117 | -2.6304 | -7.9069 | -10.6601 | -10.8347
|  | LEAFIELD | CT |  |  | 1.0755 | 1.0516 | 1.0232 | 0.98479 | 0.90146 | 0.77478 | 0.62934 | 0.47439 | 0.2079 | -0.086119 | -0.73117 | -3.4931 | -7.0934 | -9.0562 | 1.7826 | 1.7507 | 1.7164 | 1.6561 | 1.5851 | 1.5038 | 1.4056 | 1.2992 | 1.1408 | 0.95238 | 0.53183 | -1.6203 | -4.3212 | -5.8477 | 0.94588 | 0.90308 | 0.86067 | 0.76611 | 0.65861 | 0.5413 | 0.40442 | 0.25887 | 0.011672 | -0.26679 | -0.92466 | -3.9809 | -7.4325 | -9.3352
|  | LEAFIELD | LW |  |  | 1.0677 | 1.0334 | 0.95017 | 0.82117 | 0.68762 | 0.55331 | 0.38664 | 0.19886 | -0.052743 | -0.54798 | -2.1139 | -7.6365 | -10.4777 | -10.5953 | 1.7558 | 1.7154 | 1.675 | 1.6168 | 1.5541 | 1.4881 | 1.4086 | 1.3201 | 1.1055 | 0.64965 | -0.61127 | -4.7929 | -6.9992 | -7.1732 | 0.86808 | 0.7889 | 0.71085 | 0.59689 | 0.47853 | 0.35894 | 0.22185 | -0.026159 | -0.46602 | -1.0117 | -2.6304 | -7.9069 | -10.6601 | -10.8347
|  | LEAFIELD | ST |  |  | 1.1028 | 1.0978 | 1.0912 | 1.0605 | 1.0335 | 1.005 | 0.96607 | 0.92993 | 0.86546 | 0.79934 | 0.65106 | 0.066064 | -0.69681 | -1.5718 | 1.8013 | 1.7824 | 1.7616 | 1.7116 | 1.6674 | 1.6234 | 1.5695 | 1.524 | 1.4635 | 1.4032 | 1.264 | 0.76681 | 0.13038 | -0.6516 | 0.97615 | 0.95407 | 0.9311 | 0.87378 | 0.82232 | 0.77312 | 0.71589 | 0.66567 | 0.59948 | 0.53294 | 0.38436 | -0.17751 | -0.87495 | -1.6479
|  | LEAFIELD | FS |  |  | 1.0755 | 1.0516 | 1.0232 | 0.98479 | 0.90146 | 0.77478 | 0.62934 | 0.47439 | 0.2079 | -0.086119 | -0.73117 | -3.4931 | -7.0934 | -9.0562 | 1.7887 | 1.7512 | 1.7112 | 1.6617 | 1.6003 | 1.5355 | 1.4352 | 1.318 | 1.1798 | 1.0275 | 0.69599 | 0.0011205 | -0.4093 | -0.78448 | 0.96602 | 0.92567 | 0.8827 | 0.81975 | 0.74286 | 0.66402 | 0.54146 | 0.40206 | 0.22177 | 0.024579 | -0.39512 | -1.302 | -1.8331 | -2.2185
WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK | MINIMUM HEADROOM | TQ 20539 81536 | YES | 10.35 | 23.28 | 23.28 | 23.2335 | 23.1948 | 23.1343 | 23.0685 | 23.0134 | 23.0012 | 22.9886 | 22.9665 | 22.905 | 22.8922 | 22.8922 | 9.6 | 22.08 | 22.08 | 22.0219 | 21.9735 | 21.8979 | 21.8156 | 21.7467 | 21.7315 | 21.7157 | 21.6881 | 21.6112 | 21.5953 | 21.5953 | 9.6 | 22.08 | 22.08 | 22.0219 | 21.9735 | 21.8979 | 21.8156 | 21.7467 | 21.7315 | 21.7157 | 21.6881 | 21.6112 | 21.5953 | 21.5953
|  | LEAMINGTON PARK | CT |  |  | 10.35 | 23.28 | 23.28 | 23.2737 | 23.2626 | 23.2494 | 23.2255 | 23.2111 | 23.2111 | 23.2111 | 23.2111 | 23.2111 | 23.2111 | 23.2111 | 9.6 | 22.08 | 22.08 | 22.0722 | 22.0582 | 22.0417 | 22.0119 | 21.9938 | 21.9938 | 21.9938 | 21.9938 | 21.9938 | 21.9938 | 21.9938 | 9.6 | 22.08 | 22.08 | 22.0722 | 22.0582 | 22.0417 | 22.0119 | 21.9938 | 21.9938 | 21.9938 | 21.9938 | 21.9938 | 21.9938 | 21.9938
|  | LEAMINGTON PARK | LW |  |  | 10.35 | 23.28 | 23.28 | 23.2398 | 23.1948 | 23.1343 | 23.0685 | 23.0134 | 23.0012 | 22.9886 | 22.9665 | 22.905 | 22.8922 | 22.8922 | 9.6 | 22.08 | 22.08 | 22.0297 | 21.9735 | 21.8979 | 21.8156 | 21.7467 | 21.7315 | 21.7157 | 21.6881 | 21.6112 | 21.5953 | 21.5953 | 9.6 | 22.08 | 22.08 | 22.0297 | 21.9735 | 21.8979 | 21.8156 | 21.7467 | 21.7315 | 21.7157 | 21.6881 | 21.6112 | 21.5953 | 21.5953
|  | LEAMINGTON PARK | ST |  |  | 10.35 | 23.28 | 23.28 | 23.2335 | 23.2021 | 23.1737 | 23.1306 | 23.1108 | 23.1108 | 23.1108 | 23.1108 | 23.1108 | 23.1108 | 23.1108 | 9.6 | 22.08 | 22.08 | 22.0219 | 21.9826 | 21.9472 | 21.8933 | 21.8685 | 21.8685 | 21.8685 | 21.8685 | 21.8685 | 21.8685 | 21.8685 | 9.6 | 22.08 | 22.08 | 22.0219 | 21.9826 | 21.9472 | 21.8933 | 21.8685 | 21.8685 | 21.8685 | 21.8685 | 21.8685 | 21.8685 | 21.8685
|  | LEAMINGTON PARK | FS |  |  | 10.35 | 23.28 | 23.28 | 23.2737 | 23.2626 | 23.2494 | 23.2255 | 23.2111 | 23.2111 | 23.2111 | 23.2111 | 23.2111 | 23.2111 | 23.2111 | 9.6 | 22.08 | 22.08 | 22.0673 | 22.0546 | 22.0393 | 22.024 | 22.0113 | 22.0113 | 22.0113 | 22.0113 | 22.0113 | 22.0113 | 22.0113 | 9.6 | 22.08 | 22.08 | 22.0673 | 22.0546 | 22.0393 | 22.024 | 22.0113 | 22.0113 | 22.0113 | 22.0113 | 22.0113 | 22.0113 | 22.0113
MINETY GSP | STRATTON (2 X 60) | LECHLADE | MINIMUM HEADROOM | SP 22074 00496 | YES | 1.8587 | 1.5037 | 1.6792 | 1.2684 | 0.69967 | 0.075831 | -0.93374 | -2.1929 | -3.7018 | -5.5794 | -11.9336 | -28.4981 | -39.6204 | -44.9162 | 1.9495 | 1.7875 | 2.1 | 1.8517 | 1.4665 | 0.89173 | 0.21314 | -0.73472 | -1.9171 | -3.3626 | -8.3413 | -21.3478 | -30.5962 | -35.6185 | 1.9146 | 1.578 | 1.732 | 1.3428 | 0.79895 | 0.1977 | -0.78605 | -2.0168 | -3.5937 | -5.9384 | -12.0749 | -28.0674 | -39.1135 | -44.7458
|  | LECHLADE | CT |  |  | 1.9564 | 1.6954 | 1.8884 | 1.4626 | 0.95618 | 0.22472 | -0.62145 | -1.8082 | -3.3103 | -4.912 | -8.0318 | -15.8595 | -21.206 | -24.753 | 1.9495 | 1.8007 | 2.1008 | 1.8517 | 1.4665 | 0.89173 | 0.21314 | -0.73472 | -1.9171 | -3.2171 | -5.7267 | -11.8538 | -16.2632 | -19.4245 | 1.9967 | 1.7448 | 1.9204 | 1.5037 | 1.0074 | 0.28626 | -0.55489 | -1.7284 | -3.2167 | -4.8265 | -7.952 | -16.1984 | -21.5545 | -25.2296
|  | LECHLADE | LW |  |  | 1.8587 | 1.5037 | 1.6792 | 1.2684 | 0.69967 | 0.075831 | -0.93374 | -2.1929 | -3.7018 | -5.5794 | -11.9336 | -28.4981 | -39.6204 | -44.9162 | 1.9564 | 1.7875 | 2.1 | 1.8681 | 1.4681 | 1.0262 | 0.26968 | -0.68733 | -1.8621 | -3.3626 | -8.3413 | -21.3478 | -30.5962 | -35.6185 | 1.9146 | 1.578 | 1.732 | 1.3428 | 0.79895 | 0.1977 | -0.78605 | -2.0168 | -3.5937 | -5.9384 | -12.0749 | -28.0674 | -39.1135 | -44.7458
|  | LECHLADE | ST |  |  | 2.115 | 2.008 | 2.3908 | 2.0868 | 1.7538 | 1.3579 | 0.83678 | 0.27599 | -0.466 | -1.3176 | -3.6268 | -11.2864 | -17.1748 | -19.9333 | 2.0387 | 1.9827 | 2.3889 | 2.1306 | 1.8881 | 1.6158 | 1.1643 | 0.69404 | 0.027739 | -0.72298 | -2.7277 | -9.2222 | -14.5834 | -17.5356 | 2.1504 | 2.049 | 2.4004 | 2.0716 | 1.7374 | 1.3338 | 0.79438 | 0.23151 | -0.5411 | -1.417 | -3.7796 | -11.5813 | -17.7647 | -20.8423
|  | LECHLADE | FS |  |  | 1.9564 | 1.6954 | 1.8884 | 1.4626 | 0.95618 | 0.22472 | -0.62145 | -1.8082 | -3.3103 | -4.912 | -8.0318 | -15.8595 | -21.206 | -24.753 | 2.0538 | 2.0105 | 2.4345 | 2.3265 | 2.1949 | 2.0322 | 1.8382 | 1.5458 | 1.1739 | 0.74711 | -0.36472 | -4.2523 | -8.6541 | -11.8153 | 2.1888 | 2.1157 | 2.5027 | 2.3377 | 2.1301 | 1.8869 | 1.5732 | 1.2124 | 0.75931 | 0.23742 | -1.1048 | -5.9081 | -11.3325 | -14.9978
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD | MINIMUM HEADROOM | SU 43962 77635 | YES | -0.14836 | -0.88212 | -1.6153 | -2.4077 | -3.5097 | -4.7692 | -6.8929 | -9.6785 | -13.3253 | -18.1297 | -29.8621 | -49.4903 | -54.2745 | -57.1416 | 0.28482 | -0.21486 | -0.81734 | -1.4902 | -2.2555 | -3.4359 | -4.9606 | -7.2017 | -9.6964 | -13.2771 | -22.4759 | -37.8408 | -41.5458 | -43.7728 | -0.42831 | -1.1266 | -1.8419 | -2.6265 | -3.7234 | -4.9985 | -7.0735 | -9.8326 | -12.9123 | -17.0918 | -28.3831 | -47.2659 | -51.8554 | -54.5878
|  | LECKHAMPSTEAD | CT |  |  | -0.14386 | -0.77626 | -1.5312 | -2.3713 | -3.3009 | -4.7692 | -6.3916 | -8.9702 | -12.0369 | -14.9942 | -20.4753 | -32.7634 | -37.0027 | -38.0161 | 0.28482 | -0.21486 | -0.81734 | -1.4902 | -2.2386 | -3.4359 | -4.7598 | -6.8243 | -9.2711 | -11.632 | -16.0062 | -25.8542 | -29.2554 | -30.2634 | -0.42831 | -1.0504 | -1.7946 | -2.624 | -3.5428 | -4.9985 | -6.6044 | -9.0976 | -12.062 | -14.9217 | -20.2651 | -32.4616 | -36.6402 | -37.6392
|  | LECKHAMPSTEAD | LW |  |  | -0.14836 | -0.88212 | -1.6153 | -2.4077 | -3.5097 | -4.715 | -6.8929 | -9.6785 | -13.3253 | -18.1297 | -29.8621 | -49.4903 | -54.2745 | -57.1416 | 0.34597 | -0.20606 | -0.75519 | -1.3766 | -2.2555 | -3.2095 | -4.9606 | -7.2017 | -9.6964 | -13.2771 | -22.4759 | -37.8408 | -41.5458 | -43.7728 | -0.40834 | -1.1266 | -1.8419 | -2.6265 | -3.7234 | -4.9157 | -7.0735 | -9.8326 | -12.9123 | -17.0918 | -28.3831 | -47.2659 | -51.8554 | -54.5878
|  | LECKHAMPSTEAD | ST |  |  | 0.25516 | 0.021962 | -0.27673 | -0.69176 | -1.2242 | -1.9111 | -2.8 | -3.9236 | -5.2103 | -6.82 | -11.3729 | -25.9093 | -34.9985 | -36.8408 | 0.60448 | 0.42984 | 0.19822 | -0.12686 | -0.54791 | -1.0978 | -1.8179 | -2.7318 | -3.7746 | -5.0872 | -8.7226 | -20.4026 | -27.7594 | -29.4016 | -0.031665 | -0.25725 | -0.5501 | -0.96009 | -1.4846 | -2.1628 | -3.0429 | -4.1557 | -5.4292 | -7.0229 | -11.4185 | -25.6685 | -34.6983 | -36.5137
|  | LECKHAMPSTEAD | FS |  |  | -0.14386 | -0.77626 | -1.5312 | -2.3713 | -3.3009 | -4.7692 | -6.3916 | -8.9702 | -12.0369 | -14.9942 | -20.4753 | -32.7634 | -37.0027 | -38.0161 | 0.57963 | 0.38652 | 0.14635 | -0.16032 | -0.55134 | -1.0494 | -1.6976 | -2.5302 | -3.4517 | -4.5207 | -7.3483 | -17.4403 | -28.0806 | -33.7223 | -0.044911 | -0.28311 | -0.57469 | -0.9601 | -1.4468 | -2.0577 | -2.8488 | -3.8598 | -4.9902 | -6.2956 | -9.7285 | -22.0538 | -35.2177 | -42.1148
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT | MINIMUM HEADROOM | SU 56858 00293 | YES | 9.8669 | 9.3788 | 8.861 | 8.0004 | 6.9912 | 5.9272 | 4.34 | 2.3951 | 0.0032004 | -2.6966 | -8.5364 | -23.3962 | -39.9873 | -45.3956 | 12.1742 | 11.8335 | 11.4788 | 10.982 | 10.3519 | 9.6801 | 8.5544 | 7.1017 | 5.3855 | 3.4564 | -0.78121 | -12.3866 | -25.4506 | -30.0894 | 9.3919 | 8.9743 | 8.51 | 7.6958 | 6.7163 | 5.6844 | 4.1515 | 2.2951 | 0.093917 | -2.3508 | -7.8888 | -22.4014 | -38.4725 | -43.9187
|  | LEE-ON-SOLENT | CT |  |  | 10.1657 | 9.8773 | 9.5117 | 8.8266 | 8.0848 | 7.019 | 5.8888 | 4.1449 | 1.7601 | -0.58918 | -4.9372 | -15.4606 | -20.4723 | -22.5853 | 12.2347 | 11.9549 | 11.6088 | 11.1309 | 10.6087 | 9.8193 | 8.9288 | 7.6026 | 5.8997 | 4.2078 | 1.0495 | -6.8175 | -11.4346 | -15.2184 | 9.6605 | 9.4207 | 9.0339 | 8.3521 | 7.6158 | 6.6042 | 5.5276 | 3.9758 | 1.8618 | -0.28858 | -4.472 | -14.5977 | -19.4208 | -21.5029
|  | LEE-ON-SOLENT | LW |  |  | 9.8669 | 9.3788 | 8.861 | 8.0004 | 6.9912 | 5.9272 | 4.34 | 2.3951 | 0.0032004 | -2.6966 | -8.5364 | -23.3962 | -39.9873 | -45.3956 | 12.1742 | 11.8335 | 11.4788 | 10.982 | 10.3519 | 9.6801 | 8.5544 | 7.1017 | 5.3855 | 3.4564 | -0.78121 | -12.3866 | -25.4506 | -30.0894 | 9.3919 | 8.9743 | 8.51 | 7.6958 | 6.7163 | 5.6844 | 4.1515 | 2.2951 | 0.093917 | -2.3508 | -7.8888 | -22.4014 | -38.4725 | -43.9187
|  | LEE-ON-SOLENT | ST |  |  | 10.4433 | 10.3756 | 10.2572 | 10.0998 | 9.8812 | 9.5924 | 9.2017 | 8.6223 | 7.8812 | 6.8615 | 4.1536 | -5.1842 | -12.3729 | -16.0718 | 12.4291 | 12.3252 | 12.1774 | 11.9927 | 11.7496 | 11.4346 | 11.0326 | 10.4981 | 9.7581 | 8.8596 | 6.4744 | -1.5231 | -8.3161 | -13.1137 | 9.8997 | 9.8478 | 9.7568 | 9.6324 | 9.3991 | 9.0699 | 8.6398 | 8.0753 | 7.3532 | 6.466 | 4.064 | -5.1764 | -12.3722 | -15.9486
|  | LEE-ON-SOLENT | FS |  |  | 10.1657 | 9.8773 | 9.5117 | 8.8266 | 8.0848 | 7.019 | 5.8888 | 4.1449 | 1.7601 | -0.58918 | -4.9372 | -15.4606 | -20.4723 | -22.5853 | 12.4045 | 12.2915 | 12.1388 | 11.9452 | 11.7006 | 11.3962 | 11.0182 | 10.5527 | 9.9062 | 9.1318 | 7.089 | -0.58626 | -10.3239 | -19.6563 | 9.8661 | 9.8081 | 9.7186 | 9.5611 | 9.3144 | 8.9798 | 8.5624 | 8.0482 | 7.3867 | 6.6195 | 4.6188 | -3.6356 | -13.3281 | -19.6942
LOVEDEAN GSP | HAVANT | LEIGH PARK | MINIMUM HEADROOM | SU 72144 07875 | YES | 13.9378 | 12.8402 | 11.7175 | 10.3139 | 8.6214 | 6.2891 | 3.6034 | -0.32381 | -5.1998 | -10.0077 | -22.1996 | -48.2338 | -55.9293 | -61.0432 | 14.5327 | 13.6545 | 12.6307 | 11.5265 | 10.1674 | 8.2997 | 6.1324 | 2.9567 | -0.92589 | -4.7632 | -15.0165 | -34.7777 | -40.2667 | -48.9849 | 11.9721 | 10.9087 | 9.7538 | 8.3968 | 6.7608 | 4.4829 | 1.8432 | -2.0311 | -6.817 | -11.5338 | -22.8766 | -47.7795 | -55.0516 | -59.8868
|  | LEIGH PARK | CT |  |  | 13.9775 | 12.9346 | 11.7175 | 10.3139 | 8.6214 | 6.2891 | 3.6034 | -0.32381 | -5.1998 | -10.0077 | -22.1996 | -48.2338 | -55.9293 | -61.0432 | 14.5327 | 13.6545 | 12.6307 | 11.5265 | 10.1674 | 8.2997 | 6.1324 | 2.9567 | -0.92589 | -4.7632 | -15.0165 | -34.7777 | -40.2667 | -44.0434 | 11.9867 | 10.9566 | 9.7538 | 8.3968 | 6.7608 | 4.4829 | 1.8432 | -2.0311 | -6.817 | -11.5338 | -22.8766 | -47.7795 | -55.0516 | -59.8868
|  | LEIGH PARK | LW |  |  | 13.9378 | 12.8402 | 11.7301 | 10.413 | 8.6427 | 6.8177 | 3.6916 | -0.097444 | -4.3559 | -9.0502 | -19.3223 | -35.9923 | -40.2041 | -36.8394 | 14.6274 | 13.8051 | 12.9704 | 12.0264 | 10.7001 | 9.3373 | 6.9119 | 3.9554 | 0.6683 | -2.964 | -10.9225 | -23.2823 | -26.0296 | -23.0044 | 11.9721 | 10.9087 | 9.8319 | 8.5658 | 6.8516 | 5.0864 | 2.014 | -1.7196 | -5.9037 | -10.5229 | -20.6268 | -36.8188 | -40.7323 | -37.2012
|  | LEIGH PARK | ST |  |  | 14.5316 | 14.0412 | 13.4516 | 12.8353 | 11.9167 | 10.8936 | 9.5229 | 7.8327 | 5.8715 | 3.5121 | -2.8269 | -22.6239 | -35.6856 | -39.5257 | 14.9549 | 14.5059 | 13.9748 | 13.4248 | 12.608 | 11.7135 | 10.5169 | 9.0523 | 7.3235 | 5.2616 | -0.21531 | -17.1376 | -29.3957 | -35.8163 | 12.5306 | 12.0453 | 11.4621 | 10.8643 | 9.9725 | 8.9696 | 7.6059 | 5.9217 | 3.969 | 1.6156 | -4.759 | -24.8189 | -37.6687 | -41.2786
|  | LEIGH PARK | FS |  |  | 13.9775 | 12.9346 | 11.7175 | 10.3139 | 8.6214 | 6.2891 | 3.6034 | -0.32381 | -5.1998 | -10.0077 | -22.1996 | -48.2338 | -55.9293 | -61.0432 | 14.9479 | 14.627 | 14.2238 | 13.7401 | 13.111 | 12.3795 | 11.446 | 10.3037 | 8.9291 | 7.3401 | 3.1404 | -12.0198 | -31.3271 | -48.9849 | 12.5275 | 12.1915 | 11.7665 | 11.25 | 10.5743 | 9.7803 | 8.7574 | 7.4916 | 6.0325 | 4.3462 | -0.15452 | -16.7308 | -35.383 | -45.9109
BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD | MINIMUM HEADROOM | SU 75372 72019 | YES | 11.8473 | 10.8496 | 9.8697 | 8.2885 | 6.2733 | 4.1428 | 0.94151 | -2.8467 | -7.1652 | -11.8461 | -21.8131 | -42.3506 | -59.1599 | -67.056 | 16.9371 | 16.2737 | 15.5823 | 14.5858 | 13.4444 | 11.7809 | 9.9416 | 7.2839 | 3.9151 | 0.5952 | -5.8505 | -23.1635 | -34.0822 | -42.8142 | 12.2722 | 11.3817 | 10.5068 | 9.0593 | 7.2428 | 5.3214 | 2.4679 | -1.0912 | -5.2179 | -9.7107 | -19.306 | -38.8353 | -55.4387 | -62.9163
|  | LITTLE HUNGERFORD | CT |  |  | 12.2628 | 11.5743 | 10.7449 | 9.3498 | 7.7489 | 5.499 | 3.038 | -0.4297 | -5.1669 | -9.8013 | -18.7372 | -42.3506 | -59.1599 | -67.056 | 16.9464 | 16.3271 | 15.5823 | 14.5858 | 13.4444 | 11.7809 | 9.9416 | 7.2839 | 3.9151 | 0.5952 | -5.8505 | -23.1635 | -34.0822 | -42.4915 | 12.6705 | 12.0661 | 11.3375 | 10.08 | 8.6462 | 6.6437 | 4.3648 | 1.0131 | -3.514 | -7.9448 | -16.4706 | -38.8353 | -55.4387 | -62.9163
|  | LITTLE HUNGERFORD | LW |  |  | 11.8473 | 10.8496 | 9.8697 | 8.2885 | 6.2733 | 4.1428 | 0.94151 | -2.8467 | -7.1652 | -11.8461 | -21.8131 | -40.0604 | -47.0083 | -45.5869 | 16.9371 | 16.2737 | 15.6257 | 14.6926 | 13.4483 | 12.1252 | 9.9609 | 7.3363 | 4.4057 | 1.1729 | -5.7932 | -17.982 | -21.9864 | -20.2981 | 12.2722 | 11.3817 | 10.5068 | 9.0593 | 7.2428 | 5.3214 | 2.4679 | -1.0912 | -5.2179 | -9.7107 | -19.306 | -36.6377 | -42.9877 | -41.3184
|  | LITTLE HUNGERFORD | ST |  |  | 12.7488 | 12.5349 | 12.2358 | 11.763 | 11.0777 | 10.193 | 9.0409 | 7.6241 | 5.9997 | 3.9981 | -1.524 | -20.6603 | -34.9059 | -42.0523 | 17.2991 | 17.0405 | 16.7016 | 16.2183 | 15.5824 | 14.7766 | 13.7408 | 12.4849 | 11.0372 | 9.2643 | 4.4922 | -11.8908 | -24.9454 | -33.7889 | 13.1072 | 12.9247 | 12.6681 | 12.2468 | 11.6555 | 10.8948 | 9.8986 | 8.6566 | 7.0623 | 5.09 | -0.34768 | -19.3101 | -33.2288 | -39.5715
|  | LITTLE HUNGERFORD | FS |  |  | 12.2628 | 11.5743 | 10.7449 | 9.3498 | 7.7489 | 5.499 | 3.038 | -0.4297 | -5.1669 | -9.8013 | -18.7372 | -42.3506 | -59.1599 | -67.056 | 17.3012 | 17.0453 | 16.7228 | 16.3289 | 15.8153 | 15.1764 | 14.3866 | 13.4245 | 12.2558 | 10.904 | 7.3243 | -6.5823 | -24.5905 | -42.8142 | 13.1188 | 12.9593 | 12.7464 | 12.3987 | 11.9297 | 11.3394 | 10.6075 | 9.7105 | 8.5622 | 7.1491 | 3.33 | -11.5104 | -28.8534 | -40.1731
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW | MINIMUM HEADROOM | SU 86037 87794 | YES | 9.4959 | 9.3219 | 9.1564 | 8.7658 | 8.3536 | 7.9023 | 7.3959 | 6.8497 | 6.1484 | 5.4354 | 3.9751 | 0.83719 | -1.8494 | -3.15 | 12.8669 | 12.792 | 12.6966 | 12.5185 | 12.3174 | 12.0939 | 11.85 | 11.5808 | 11.1881 | 10.7827 | 9.9077 | 6.9304 | 1.9835 | -7.4666 | 9.448 | 9.2637 | 9.0882 | 8.6701 | 8.2395 | 7.8061 | 7.3393 | 6.8425 | 6.2201 | 5.5868 | 4.2889 | 1.5178 | -0.80138 | -1.9285
|  | LITTLE MARLOW | CT |  |  | 9.7464 | 9.7011 | 9.6591 | 9.405 | 9.1413 | 8.8683 | 8.5854 | 8.2712 | 7.5552 | 6.792 | 5.2247 | 0.97613 | -1.8494 | -3.15 | 12.8961 | 12.8049 | 12.7038 | 12.5185 | 12.3174 | 12.0939 | 11.85 | 11.5808 | 11.1881 | 10.7827 | 9.9077 | 6.9304 | 3.3637 | -1.6996 | 9.7142 | 9.6672 | 9.6226 | 9.3512 | 9.0693 | 8.7765 | 8.4723 | 8.1486 | 7.4776 | 6.7924 | 5.4037 | 1.665 | -0.80138 | -1.9285
|  | LITTLE MARLOW | LW |  |  | 9.4959 | 9.3219 | 9.1564 | 8.7658 | 8.3536 | 7.9023 | 7.3959 | 6.8497 | 6.1484 | 5.4354 | 3.9751 | 0.83719 | -0.87086 | -1.3209 | 12.8669 | 12.792 | 12.7219 | 12.5601 | 12.3907 | 12.2158 | 12.023 | 11.8225 | 11.5817 | 11.3329 | 10.5856 | 9.2997 | 8.9217 | 8.8105 | 9.448 | 9.2637 | 9.0882 | 8.6701 | 8.2395 | 7.8061 | 7.3393 | 6.8425 | 6.2201 | 5.5868 | 4.2889 | 1.5178 | 0.025341 | -0.35368
|  | LITTLE MARLOW | ST |  |  | 9.7964 | 9.7795 | 9.7574 | 9.7126 | 9.6548 | 9.5786 | 9.4818 | 9.3576 | 9.2011 | 9.0069 | 8.5045 | 6.4752 | 4.7544 | 2.7217 | 12.9136 | 12.8323 | 12.7354 | 12.6115 | 12.4697 | 12.3013 | 12.0996 | 11.8685 | 11.6087 | 11.303 | 10.5452 | 7.8353 | 4.5597 | -0.73098 | 9.7735 | 9.7609 | 9.7429 | 9.6998 | 9.6454 | 9.5745 | 9.4845 | 9.3706 | 9.2298 | 9.0544 | 8.5985 | 6.6813 | 4.9794 | 3.0492
|  | LITTLE MARLOW | FS |  |  | 9.7464 | 9.7011 | 9.6591 | 9.405 | 9.1413 | 8.8683 | 8.5854 | 8.2712 | 7.5552 | 6.792 | 5.2247 | 0.97613 | -1.8494 | -3.15 | 12.9067 | 12.8084 | 12.6966 | 12.5622 | 12.4061 | 12.2314 | 12.0191 | 11.7761 | 11.4842 | 11.1535 | 10.3565 | 7.303 | 1.9835 | -7.4666 | 9.7713 | 9.756 | 9.7408 | 9.6874 | 9.6251 | 9.5587 | 9.4758 | 9.3789 | 9.2011 | 9.0085 | 8.5852 | 6.9941 | 5.0577 | 2.9921
NURSLING GSP | ROWNHAMS | LORDSHILL | MINIMUM HEADROOM | SU 38746 16055 | YES | 16.8985 | 16.7523 | 16.5319 | 16.1313 | 15.6683 | 15.1929 | 14.5668 | 13.8526 | 12.5059 | 10.8288 | 7.2253 | 1.0924 | -2.0431 | -3.3912 | 17.0368 | 16.9636 | 16.8755 | 16.7782 | 16.6665 | 16.4952 | 16.2548 | 15.2838 | 14.0952 | 12.8869 | 10.3322 | 5.1386 | 2.1872 | -3.2117 | 15.3791 | 15.0198 | 14.6649 | 14.158 | 13.5121 | 12.8414 | 11.7636 | 10.4513 | 8.968 | 7.3242 | 3.7888 | -2.1261 | -5.0659 | -6.318
|  | LORDSHILL | CT |  |  | 16.9554 | 16.8665 | 16.7571 | 16.5445 | 16.202 | 15.7667 | 15.3011 | 14.6434 | 12.9968 | 11.3821 | 8.3313 | 1.1286 | -2.0431 | -3.3912 | 17.0368 | 16.9636 | 16.8755 | 16.7782 | 16.6665 | 16.4952 | 16.2881 | 15.3164 | 14.0952 | 12.8869 | 10.599 | 5.1386 | 2.1872 | -0.29887 | 15.4515 | 15.1721 | 14.8333 | 14.3433 | 13.8053 | 13.0217 | 12.1636 | 10.9085 | 9.3075 | 7.7352 | 4.7778 | -2.1169 | -5.0659 | -6.318
|  | LORDSHILL | LW |  |  | 16.8985 | 16.7523 | 16.5319 | 16.1313 | 15.6683 | 15.1929 | 14.5668 | 13.8526 | 12.5059 | 10.8288 | 7.2253 | 1.0924 | -0.68293 | -0.043994 | 17.0533 | 16.9787 | 16.9059 | 16.8124 | 16.6827 | 16.5406 | 16.2548 | 15.2838 | 14.1875 | 12.9661 | 10.3322 | 6.0143 | 4.7749 | 5.231 | 15.3791 | 15.0198 | 14.6649 | 14.158 | 13.5121 | 12.8414 | 11.7636 | 10.4513 | 8.968 | 7.3242 | 3.7888 | -2.1261 | -3.8114 | -3.1433
|  | LORDSHILL | ST |  |  | 17.1047 | 17.1159 | 17.1122 | 17.0876 | 17.0388 | 16.9672 | 16.854 | 16.7122 | 16.5159 | 16.2666 | 13.9884 | 6.3117 | 1.1191 | -0.99567 | 17.0809 | 17.0498 | 17.0068 | 16.936 | 16.8523 | 16.7493 | 16.6134 | 16.455 | 16.2429 | 15.9401 | 13.9438 | 7.4116 | 2.4523 | -0.39862 | 15.7041 | 15.636 | 15.5285 | 15.3603 | 15.1238 | 14.807 | 14.3726 | 13.8212 | 13.1399 | 12.2849 | 9.9285 | 2.3204 | -2.8398 | -4.8967
|  | LORDSHILL | FS |  |  | 16.9554 | 16.8665 | 16.7571 | 16.5445 | 16.202 | 15.7667 | 15.3011 | 14.6434 | 12.9968 | 11.3821 | 8.3313 | 1.1286 | -2.0431 | -3.3912 | 17.0854 | 17.0587 | 17.023 | 16.979 | 16.9226 | 16.8534 | 16.7678 | 16.6647 | 16.5285 | 16.3703 | 15.5319 | 10.4663 | 3.7057 | -3.2117 | 15.6999 | 15.6431 | 15.5594 | 15.4116 | 15.2244 | 14.9847 | 14.686 | 14.3155 | 13.8867 | 13.3798 | 11.9766 | 6.5025 | 0.13137 | -3.9726
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE | MINIMUM HEADROOM | SU 47334 68495 | YES | 16.7676 | 16.4123 | 16.0592 | 15.1795 | 14.2384 | 13.3386 | 12.4262 | 11.7207 | 10.9827 | 9.3861 | 4.7308 | -3.6546 | -6.5519 | -8.2899 | 20.0025 | 19.814 | 19.6301 | 18.8631 | 18.3229 | 17.8322 | 17.2143 | 16.2357 | 15.0372 | 13.6236 | 10.2325 | 4.3855 | 2.6552 | -9.8154 | 15.0939 | 14.7812 | 14.4708 | 13.6338 | 12.8023 | 11.9764 | 11.1437 | 10.4727 | 9.6646 | 7.6578 | 3.2433 | -4.6487 | -7.2986 | -8.8892
|  | LOVE LANE | CT |  |  | 17.0933 | 16.8756 | 16.6462 | 15.8054 | 15.0593 | 14.4066 | 13.7174 | 13.1149 | 11.5809 | 9.3861 | 4.7308 | -3.6546 | -6.5519 | -8.2899 | 20.0854 | 19.8855 | 19.6638 | 18.8631 | 18.3229 | 17.8322 | 17.2143 | 16.2357 | 15.0372 | 13.6236 | 10.2325 | 4.3855 | 2.6552 | -2.2015 | 15.3905 | 15.1979 | 14.9871 | 14.1465 | 13.5003 | 12.9102 | 12.2865 | 11.2596 | 9.6646 | 7.6578 | 3.2433 | -4.6487 | -7.2986 | -8.8892
|  | LOVE LANE | LW |  |  | 16.7676 | 16.4123 | 16.0592 | 15.1795 | 14.2384 | 13.3386 | 12.4262 | 11.7207 | 10.9827 | 10.2298 | 8.6547 | 5.374 | 3.6019 | 2.8287 | 20.0025 | 19.814 | 19.6301 | 18.9948 | 18.4264 | 17.8548 | 17.3039 | 16.8459 | 16.2917 | 15.5908 | 13.8836 | 11.5658 | 10.9662 | 10.7045 | 15.0939 | 14.7812 | 14.4708 | 13.6338 | 12.8023 | 11.9764 | 11.1437 | 10.4727 | 9.7899 | 9.0935 | 7.5434 | 4.1504 | 3.0744 | 2.5317
|  | LOVE LANE | ST |  |  | 17.3385 | 17.2403 | 17.1277 | 16.5331 | 16.1153 | 15.8457 | 15.5715 | 15.4104 | 15.2357 | 15.0205 | 14.5296 | 10.6005 | 8.6935 | 7.4219 | 20.2315 | 20.1062 | 19.9611 | 19.2419 | 18.8388 | 18.5369 | 18.2264 | 17.9663 | 17.6937 | 17.374 | 16.4794 | 13.2387 | 8.9923 | 1.654 | 15.6257 | 15.5509 | 15.4621 | 14.8532 | 14.4986 | 14.2556 | 14.0098 | 13.8545 | 13.6714 | 13.132 | 11.7232 | 7.8406 | 6.5776 | 5.799
|  | LOVE LANE | FS |  |  | 17.0933 | 16.8756 | 16.6462 | 15.8054 | 15.0593 | 14.4066 | 13.7174 | 13.1149 | 11.5809 | 9.3861 | 4.7308 | -3.6546 | -6.5519 | -8.2899 | 20.226 | 20.1 | 19.9618 | 19.5652 | 19.2145 | 18.8767 | 18.5473 | 18.253 | 17.8846 | 17.4366 | 16.3411 | 11.9636 | 4.2921 | -9.8154 | 15.6199 | 15.5545 | 15.4934 | 15.1638 | 14.8652 | 14.5991 | 14.3571 | 14.1906 | 13.9922 | 13.7916 | 13.3289 | 10.7176 | 7.9907 | 5.6814
COWLEY GSP | YARNTON BSP | LOVELACE ROAD | MINIMUM HEADROOM | SP 50395 10376 | NO | 6.5057 | 6.2655 | 6.012 | 5.5005 | 5.0104 | 4.585 | 4.0215 | 3.3792 | 2.6181 | 1.6914 | -1.3038 | -7.2452 | -9.1936 | -10.5524 | 8.1007 | 7.9529 | 7.7732 | 7.4888 | 7.2061 | 6.8612 | 6.4681 | 5.9237 | 5.2332 | 4.5106 | 2.8131 | -1.5428 | -2.9523 | -5.0337 | 7.1018 | 6.8876 | 6.664 | 6.2167 | 5.7711 | 5.3683 | 4.8228 | 4.2 | 3.4717 | 2.5778 | -0.1426 | -5.8158 | -7.703 | -9.0592
|  | LOVELACE ROAD | CT |  |  | 6.6001 | 6.4241 | 6.2092 | 5.7542 | 5.3313 | 4.8728 | 4.3636 | 3.6638 | 2.6919 | 1.6914 | -1.3038 | -7.2452 | -9.1936 | -10.5524 | 8.1007 | 7.9529 | 7.7732 | 7.4888 | 7.2061 | 6.8612 | 6.4681 | 5.9237 | 5.2332 | 4.5106 | 2.8131 | -1.5428 | -2.9523 | -5.0337 | 7.1808 | 7.0211 | 6.8263 | 6.4284 | 6.0451 | 5.6094 | 5.1213 | 4.4486 | 3.5289 | 2.5778 | -0.1426 | -5.8158 | -7.703 | -9.0592
|  | LOVELACE ROAD | LW |  |  | 6.5057 | 6.2655 | 6.012 | 5.5005 | 5.0104 | 4.585 | 4.0215 | 3.3792 | 2.6181 | 1.7884 | -0.040672 | -2.9423 | -4.0315 | -4.013 | 8.1127 | 7.9728 | 7.8284 | 7.5578 | 7.2792 | 7.0199 | 6.6373 | 6.1914 | 5.6799 | 5.1145 | 3.8805 | 1.8839 | 1.0369 | 0.88828 | 7.1018 | 6.8876 | 6.664 | 6.2167 | 5.7711 | 5.3683 | 4.8228 | 4.2 | 3.4717 | 2.677 | 0.93756 | -1.877 | -3.0014 | -3.0964
|  | LOVELACE ROAD | ST |  |  | 6.706 | 6.6203 | 6.5136 | 6.2709 | 6.0819 | 5.9228 | 5.7239 | 5.4801 | 5.1612 | 4.7836 | 3.7598 | 0.58573 | -1.9045 | -3.3432 | 8.1705 | 8.0883 | 7.986 | 7.7919 | 7.618 | 7.4438 | 7.2245 | 6.9735 | 6.6653 | 6.3033 | 5.3429 | 2.2808 | -0.65215 | -3.3943 | 7.2819 | 7.2099 | 7.1197 | 6.909 | 6.7364 | 6.5788 | 6.375 | 6.13 | 5.8132 | 5.4366 | 4.4159 | 1.2159 | -1.3029 | -2.6954
|  | LOVELACE ROAD | FS |  |  | 6.6001 | 6.4241 | 6.2092 | 5.7542 | 5.3313 | 4.8728 | 4.3636 | 3.6638 | 2.6919 | 1.6914 | -1.3038 | -7.2452 | -9.1936 | -10.5524 | 8.1709 | 8.0914 | 7.9929 | 7.8375 | 7.6906 | 7.5425 | 7.3702 | 7.1677 | 6.9246 | 6.6446 | 5.9126 | 3.2948 | -0.27742 | -4.6419 | 7.285 | 7.2296 | 7.1574 | 6.9946 | 6.8569 | 6.7285 | 6.5838 | 6.4109 | 6.1812 | 5.9191 | 5.2297 | 2.8701 | 0.094227 | -1.9461
MANNINGTON GSP | ARNEWOOD | LYMINGTON | MINIMUM HEADROOM | SZ 31720 96856 | YES | 10.0117 | 9.5935 | 9.1675 | 8.4208 | 7.6285 | 6.766 | 5.7153 | 4.6737 | 3.4873 | 2.2505 | -0.3283 | -5.7104 | -11.0616 | -14.9353 | 13.3099 | 13.1099 | 12.9036 | 12.5777 | 12.2113 | 11.8089 | 11.2564 | 10.6708 | 10 | 9.2763 | 7.7485 | 3.793 | -0.057223 | -3.7606 | 9.2442 | 8.8694 | 8.4922 | 7.8453 | 7.1495 | 6.3945 | 5.4521 | 4.4918 | 3.3843 | 2.219 | -0.19863 | -4.9681 | -10.9439 | -14.6989
|  | LYMINGTON | CT |  |  | 10.4086 | 10.243 | 10.0277 | 9.5117 | 8.9711 | 8.2928 | 7.5301 | 6.6903 | 5.3885 | 4.056 | 1.4495 | -5.7104 | -11.0616 | -14.9353 | 13.4159 | 13.2869 | 13.1236 | 12.8516 | 12.5443 | 12.1357 | 11.6705 | 11.1178 | 10.356 | 9.5745 | 8.0544 | 3.793 | -0.057223 | -3.7606 | 9.6181 | 9.4657 | 9.2725 | 8.801 | 8.3062 | 7.6902 | 6.999 | 6.2326 | 5.0306 | 3.8102 | 1.4467 | -4.9681 | -10.9439 | -14.6989
|  | LYMINGTON | LW |  |  | 10.0117 | 9.5935 | 9.1675 | 8.4208 | 7.6285 | 6.766 | 5.7153 | 4.6737 | 3.4873 | 2.2505 | -0.3283 | -5.4133 | -8.2102 | -9.1797 | 13.3099 | 13.1099 | 12.9036 | 12.5777 | 12.2113 | 11.8089 | 11.2564 | 10.6708 | 10 | 9.2763 | 7.7485 | 5.0075 | 3.6117 | 3.0986 | 9.2442 | 8.8694 | 8.4922 | 7.8453 | 7.1495 | 6.3945 | 5.4521 | 4.4918 | 3.3843 | 2.219 | -0.19863 | -4.8675 | -7.4178 | -8.2712
|  | LYMINGTON | ST |  |  | 10.5776 | 10.52 | 10.4209 | 10.2559 | 10.0682 | 9.8144 | 9.4873 | 9.1613 | 8.8244 | 8.4197 | 7.4404 | 3.6652 | -0.076622 | -3.7168 | 13.5019 | 13.4375 | 13.3443 | 13.2119 | 13.0582 | 12.8559 | 12.5954 | 12.318 | 11.9975 | 11.6207 | 10.6938 | 7.4443 | 3.9443 | -0.046555 | 9.7787 | 9.7274 | 9.6428 | 9.5008 | 9.339 | 9.1216 | 8.8411 | 8.5557 | 8.2463 | 7.8783 | 6.9893 | 3.4037 | -0.12365 | -3.4807
|  | LYMINGTON | FS |  |  | 10.4086 | 10.243 | 10.0277 | 9.5117 | 8.9711 | 8.2928 | 7.5301 | 6.6903 | 5.3885 | 4.056 | 1.4495 | -5.7104 | -11.0616 | -14.9353 | 13.5149 | 13.4395 | 13.3461 | 13.2206 | 13.0752 | 12.9009 | 12.6839 | 12.4582 | 12.1576 | 11.8185 | 10.9974 | 7.8781 | 3.3778 | -2.8641 | 9.8021 | 9.7498 | 9.6808 | 9.5278 | 9.3587 | 9.1588 | 8.9174 | 8.6837 | 8.3578 | 8.0029 | 7.1952 | 4.128 | 0.565 | -2.8228
MELKSHAM GSP | CHIPPENHAM | LYNEHAM | MINIMUM HEADROOM | ST 99348 80481 | YES | -1.6545 | -2.0823 | -2.5765 | -3.119 | -3.8119 | -4.549 | -5.5767 | -6.8261 | -8.2492 | -9.8257 | -13.1992 | -20.3685 | -24.1552 | -25.732 | 0.97168 | 0.69547 | 0.3894 | 0.025499 | -0.42062 | -1.0663 | -1.765 | -2.7467 | -3.9494 | -5.2219 | -7.6158 | -13.5762 | -16.6782 | -18.6964 | -1.4868 | -1.8658 | -2.2902 | -2.7544 | -3.3616 | -4.0532 | -5.0564 | -6.2786 | -7.6763 | -9.259 | -12.5419 | -19.8018 | -23.5844 | -25.2758
|  | LYNEHAM | CT |  |  | -1.5127 | -1.8345 | -2.2907 | -2.8563 | -3.4888 | -4.3693 | -5.2606 | -6.5249 | -8.1167 | -9.7501 | -12.8295 | -20.3685 | -24.1552 | -25.732 | 0.98116 | 0.73605 | 0.41598 | 0.025499 | -0.42062 | -1.0663 | -1.765 | -2.7467 | -3.9494 | -5.2219 | -7.6158 | -13.5762 | -16.6782 | -18.5032 | -1.3545 | -1.6369 | -2.0018 | -2.502 | -3.1017 | -3.9481 | -4.8313 | -6.0752 | -7.6368 | -9.259 | -12.3116 | -19.8018 | -23.5844 | -25.2758
|  | LYNEHAM | LW |  |  | -1.6545 | -2.0823 | -2.5765 | -3.119 | -3.8119 | -4.549 | -5.5767 | -6.8261 | -8.2492 | -9.8257 | -13.1992 | -18.8393 | -21.1759 | -21.4258 | 0.97168 | 0.69547 | 0.3894 | 0.040491 | -0.41552 | -0.90196 | -1.6567 | -2.5863 | -3.6524 | -4.8412 | -7.3902 | -11.5761 | -13.601 | -14.3263 | -1.4868 | -1.8658 | -2.2902 | -2.7544 | -3.3616 | -4.0532 | -5.0564 | -6.2786 | -7.6763 | -9.2262 | -12.5419 | -18.0735 | -20.5515 | -21.1143
|  | LYNEHAM | ST |  |  | -1.3251 | -1.4791 | -1.7238 | -2.1723 | -2.6305 | -3.1642 | -3.775 | -4.4349 | -5.2552 | -6.2008 | -8.647 | -16.1612 | -21.716 | -24.3505 | 1.1248 | 1.0184 | 0.85342 | 0.47359 | 0.10342 | -0.31534 | -0.8346 | -1.3615 | -2.0467 | -2.8263 | -4.8501 | -11.0959 | -16.0145 | -18.6964 | -1.1885 | -1.3248 | -1.5285 | -1.963 | -2.3811 | -2.8427 | -3.4652 | -4.1192 | -4.9523 | -5.9048 | -8.3707 | -15.944 | -21.6539 | -24.4652
|  | LYNEHAM | FS |  |  | -1.5127 | -1.8345 | -2.2907 | -2.8563 | -3.4888 | -4.3693 | -5.2606 | -6.5249 | -8.1167 | -9.7501 | -12.8295 | -20.3685 | -24.1552 | -25.732 | 1.1484 | 1.0606 | 0.92388 | 0.71848 | 0.48059 | 0.19401 | -0.11272 | -0.47043 | -0.89685 | -1.3781 | -2.6387 | -7.0448 | -11.8802 | -15.2564 | -1.1345 | -1.2333 | -1.3876 | -1.6365 | -1.9144 | -2.2383 | -2.58 | -3.0258 | -3.5765 | -4.1894 | -5.7795 | -11.3985 | -17.3907 | -21.2672
BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E | MINIMUM HEADROOM | SU 98120 65945 | YES | 23.4955 | 23.3075 | 22.7488 | 21.9607 | 21.7178 | 21.1923 | 20.208 | 19.1053 | 18.0261 | 16.8263 | 14.0647 | 9.8975 | 1.3319 | -3.5962 | 23.3224 | 23.2359 | 22.8328 | 22.1209 | 21.8042 | 21.2836 | 20.5425 | 19.69 | 18.814 | 17.8216 | 15.6424 | 10.9039 | 6.14 | 2.2819 | 22.0786 | 21.9118 | 21.4284 | 20.6423 | 20.1466 | 19.4628 | 18.5202 | 17.4501 | 16.3862 | 15.2002 | 12.595 | 7.061 | 0.51876 | -4.22
|  | M V E E | CT |  |  | 23.4955 | 23.3075 | 22.7488 | 21.9607 | 21.7178 | 21.357 | 20.6327 | 19.644 | 18.5584 | 17.4865 | 15.4468 | 10.0521 | 1.3319 | -3.5962 | 23.3305 | 23.2471 | 22.8328 | 22.1209 | 21.8042 | 21.3328 | 20.8067 | 20.0559 | 19.2075 | 18.3696 | 16.7616 | 12.8829 | 6.14 | 2.2819 | 22.0786 | 21.9118 | 21.4284 | 20.6423 | 20.2236 | 19.6113 | 18.9286 | 17.9778 | 16.9145 | 15.8664 | 13.8692 | 8.9804 | 0.51876 | -4.22
|  | M V E E | LW |  |  | 23.5382 | 23.3697 | 23.0163 | 22.455 | 21.9182 | 21.1923 | 20.208 | 19.1053 | 18.0261 | 16.8263 | 14.0647 | 9.8975 | 9.3712 | 10.6659 | 23.3224 | 23.2359 | 22.9462 | 22.3303 | 21.8201 | 21.2836 | 20.5425 | 19.69 | 18.814 | 17.8216 | 15.6424 | 12.371 | 12.001 | 13.063 | 22.1047 | 21.9493 | 21.5343 | 20.7951 | 20.1466 | 19.4628 | 18.5202 | 17.4501 | 16.3862 | 15.2002 | 12.595 | 8.4643 | 7.9555 | 9.2526
|  | M V E E | ST |  |  | 23.5857 | 23.47 | 23.0079 | 22.3241 | 22.217 | 22.0917 | 21.9371 | 21.4789 | 20.9962 | 20.3938 | 18.7418 | 13.5234 | 10.3202 | 9.6134 | 23.3453 | 23.2806 | 22.9263 | 22.3961 | 22.3321 | 22.0743 | 21.7491 | 21.3747 | 20.9791 | 20.4849 | 19.1175 | 14.9098 | 12.3214 | 11.7119 | 22.1679 | 22.0639 | 21.6533 | 21.0354 | 20.9198 | 20.6004 | 20.2046 | 19.7492 | 19.2748 | 18.6816 | 17.0815 | 12.013 | 8.84 | 8.1603
|  | M V E E | FS |  |  | 23.4955 | 23.3075 | 22.7488 | 21.9607 | 21.7178 | 21.357 | 20.6327 | 19.644 | 18.5584 | 17.4865 | 15.4468 | 10.0521 | 1.3319 | -3.5962 | 23.3618 | 23.3057 | 23.0542 | 22.5674 | 22.1481 | 21.6557 | 21.0417 | 20.2463 | 19.3819 | 18.4502 | 16.3486 | 10.9039 | 6.8821 | 5.2206 | 22.1904 | 22.0939 | 21.7374 | 21.1758 | 20.6779 | 20.0921 | 19.3652 | 18.4368 | 17.4297 | 16.3412 | 13.7549 | 7.061 | 2.0791 | 0.032085
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON | MINIMUM HEADROOM | SY 59138 97747 | YES | 1.6799 | 1.4215 | 1.1605 | 0.93258 | 0.61027 | 0.11156 | -0.47716 | -1.3018 | -3.3903 | -6.4837 | -13.6931 | -26.5371 | -30.1085 | -32.5012 | 2.2234 | 2.0891 | 1.9389 | 1.7582 | 1.5459 | 1.2336 | 0.86888 | 0.33656 | -1.0561 | -3.4519 | -9.0493 | -19.0041 | -21.6608 | -23.4838 | -0.14903 | -0.37968 | -0.61101 | -0.81948 | -1.1437 | -1.6058 | -2.1491 | -2.9229 | -3.866 | -6.7011 | -13.614 | -25.9272 | -29.3266 | -31.6102
|  | MAIDEN NEWTON | CT |  |  | 1.7535 | 1.533 | 1.2758 | 0.97037 | 0.61027 | 0.11156 | -0.47716 | -1.3018 | -3.3903 | -6.4837 | -13.6931 | -26.5371 | -30.1085 | -32.5012 | 2.2234 | 2.0942 | 1.9389 | 1.7582 | 1.5459 | 1.2336 | 0.86888 | 0.33656 | -1.0561 | -3.4519 | -9.0493 | -19.0041 | -21.6608 | -23.4838 | -0.10553 | -0.30551 | -0.54013 | -0.81756 | -1.1437 | -1.6058 | -2.1491 | -2.9229 | -3.866 | -6.7011 | -13.614 | -25.9272 | -29.3266 | -31.6102
|  | MAIDEN NEWTON | LW |  |  | 1.6799 | 1.4215 | 1.1605 | 0.93258 | 0.64067 | 0.33592 | -0.1484 | -0.73242 | -1.3746 | -2.0868 | -3.6305 | -6.1325 | -6.773 | -6.3226 | 2.2241 | 2.0891 | 1.9543 | 1.8232 | 1.6467 | 1.462 | 1.1397 | 0.73928 | 0.29848 | -0.19559 | -1.2724 | -2.9621 | -3.2931 | -2.8392 | -0.14903 | -0.37968 | -0.61101 | -0.81948 | -1.0888 | -1.3702 | -1.8328 | -2.3971 | -3.0176 | -3.7086 | -5.2097 | -7.6119 | -8.1693 | -7.6496
|  | MAIDEN NEWTON | ST |  |  | 1.9248 | 1.8409 | 1.7378 | 1.5974 | 1.4258 | 1.2217 | 0.98223 | 0.69528 | 0.37133 | -0.013738 | -1.0241 | -4.0904 | -6.0934 | -6.7236 | 2.3159 | 2.269 | 2.2088 | 2.1287 | 2.0266 | 1.8992 | 1.7417 | 1.5465 | 1.3261 | 1.0558 | 0.32506 | -1.9854 | -3.5173 | -4.0162 | 0.04643 | -0.027235 | -0.11888 | -0.24408 | -0.39911 | -0.58666 | -0.81109 | -1.0839 | -1.3948 | -1.7687 | -2.7616 | -5.8109 | -7.7887 | -8.3573
|  | MAIDEN NEWTON | FS |  |  | 1.7535 | 1.533 | 1.2758 | 0.97037 | 0.61027 | 0.11156 | -0.47716 | -1.3018 | -3.3903 | -6.4837 | -13.6931 | -26.5371 | -30.1085 | -32.5012 | 2.3226 | 2.2808 | 2.228 | 2.1537 | 2.065 | 1.9575 | 1.828 | 1.6702 | 1.4969 | 1.2993 | 0.78337 | -1.148 | -3.1604 | -4.3278 | 0.066015 | 0.0059494 | -0.067979 | -0.18877 | -0.32673 | -0.48762 | -0.67684 | -0.90104 | -1.1531 | -1.4351 | -2.1514 | -4.8055 | -7.4525 | -8.9393
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD | MINIMUM HEADROOM | SU 86485 79800 | YES | 14.9668 | 14.4417 | 13.9177 | 12.958 | 11.7606 | 10.4806 | 8.727 | 6.6484 | 3.2092 | -1.665 | -13.3223 | -39.8722 | -58.1203 | -68.5186 | 19.0257 | 18.7219 | 18.4156 | 17.9065 | 17.2739 | 16.4109 | 15.3717 | 13.2984 | 10.322 | 6.7618 | -1.9228 | -21.4841 | -34.9566 | -42.8214 | 13.724 | 13.2356 | 12.7493 | 11.8763 | 10.7873 | 9.6201 | 7.9848 | 6.0939 | 2.5359 | -2.0904 | -13.2029 | -38.4775 | -55.8497 | -65.79
|  | MAIDENHEAD | CT |  |  | 15.3604 | 15.0493 | 14.6801 | 13.864 | 12.8427 | 11.5531 | 9.9778 | 7.358 | 3.2092 | -1.665 | -13.3223 | -39.8722 | -58.1203 | -68.5186 | 19.054 | 18.7637 | 18.4156 | 17.9065 | 17.2739 | 16.4109 | 15.3717 | 13.2984 | 10.322 | 6.7618 | -1.9228 | -21.4841 | -34.9566 | -42.8214 | 14.0417 | 13.7343 | 13.3673 | 12.6145 | 11.6877 | 10.4877 | 9.0349 | 6.4577 | 2.5359 | -2.0904 | -13.2029 | -38.4775 | -55.8497 | -65.79
|  | MAIDENHEAD | LW |  |  | 14.9668 | 14.4417 | 13.9177 | 12.958 | 11.7606 | 10.4806 | 8.727 | 6.6484 | 4.3564 | 2.0288 | -2.2809 | -10.4608 | -14.0284 | -14.3419 | 19.0257 | 18.7219 | 18.4219 | 17.9421 | 17.3025 | 16.6086 | 15.5428 | 14.2826 | 12.9299 | 11.4976 | 8.7265 | 3.8566 | 2.0072 | 2.1578 | 13.724 | 13.2356 | 12.7493 | 11.8763 | 10.7873 | 9.6201 | 7.9848 | 6.0939 | 4.012 | 1.8766 | -2.1434 | -9.7813 | -13.0367 | -13.2426
|  | MAIDENHEAD | ST |  |  | 15.5972 | 15.4765 | 15.3339 | 15.0658 | 14.6886 | 14.2426 | 13.6072 | 12.858 | 12.0208 | 11.0732 | 9.0155 | 1.6388 | -4.5024 | -8.789 | 19.2208 | 19.0839 | 18.9161 | 18.618 | 18.2585 | 17.839 | 17.2783 | 16.6603 | 15.9785 | 15.1932 | 13.3343 | 6.9811 | 1.4179 | -3.3622 | 14.2725 | 14.1585 | 14.02 | 13.7348 | 13.367 | 12.9399 | 12.3561 | 11.7062 | 10.9901 | 10.1532 | 8.1454 | 1.0039 | -4.8304 | -8.7247
|  | MAIDENHEAD | FS |  |  | 15.3604 | 15.0493 | 14.6801 | 13.864 | 12.8427 | 11.5531 | 9.9778 | 7.358 | 3.2092 | -1.665 | -13.3223 | -39.8722 | -58.1203 | -68.5186 | 19.2239 | 19.0858 | 18.9188 | 18.7112 | 18.4269 | 18.0904 | 17.6552 | 17.1434 | 16.5463 | 15.8939 | 14.3958 | 8.8539 | 1.7257 | -6.0128 | 14.2904 | 14.1965 | 14.0794 | 13.8733 | 13.578 | 13.2339 | 12.7824 | 12.2536 | 11.5777 | 10.868 | 9.3205 | 3.3804 | -3.4747 | -8.6575
MELKSHAM GSP | CHIPPENHAM | MALMESBURY | MINIMUM HEADROOM | ST 92288 87493 | YES | -1.203 | -1.747 | -2.4674 | -3.3188 | -4.3755 | -5.4933 | -7.4073 | -9.7868 | -12.5092 | -15.5104 | -22.1269 | -35.5834 | -44.976 | -45.3416 | 0.59288 | 0.10658 | -0.43819 | -1.1247 | -1.847 | -2.9647 | -4.2188 | -6.1021 | -8.3841 | -10.6569 | -15.0742 | -25.9443 | -32.696 | -33.151 | -1.2336 | -2.0062 | -2.7699 | -3.6177 | -4.6514 | -5.8297 | -7.6023 | -9.9737 | -12.7813 | -15.6899 | -22.181 | -35.3154 | -44.3493 | -44.7556
|  | MALMESBURY | CT |  |  | -1.0265 | -1.4455 | -2.1365 | -3.0673 | -4.0299 | -5.4879 | -7.1123 | -9.5256 | -12.5092 | -15.4581 | -21.0988 | -35.5834 | -44.976 | -45.3416 | 0.59288 | 0.13834 | -0.43819 | -1.1247 | -1.847 | -2.9647 | -4.2188 | -6.1021 | -8.3841 | -10.6569 | -15.0159 | -25.9443 | -32.696 | -33.151 | -1.1502 | -1.793 | -2.5477 | -3.4556 | -4.3921 | -5.8297 | -7.4313 | -9.8332 | -12.7813 | -15.6899 | -21.2262 | -35.3154 | -44.3493 | -44.7556
|  | MALMESBURY | LW |  |  | -1.203 | -1.747 | -2.4674 | -3.3188 | -4.3755 | -5.4933 | -7.4073 | -9.7868 | -12.4778 | -15.5104 | -22.1269 | -32.6621 | -35.1732 | -32.9581 | 0.6063 | 0.10658 | -0.41013 | -1.0061 | -1.7607 | -2.5524 | -3.982 | -5.7837 | -7.8179 | -10.1023 | -15.0742 | -23.1302 | -24.9704 | -23.2082 | -1.2336 | -2.0062 | -2.7699 | -3.6177 | -4.6514 | -5.731 | -7.6023 | -9.9737 | -12.6579 | -15.6603 | -22.181 | -32.5143 | -34.999 | -32.8846
|  | MALMESBURY | ST |  |  | -0.81937 | -0.98717 | -1.2219 | -1.5813 | -2.0504 | -2.6786 | -3.5701 | -4.6444 | -5.906 | -7.4577 | -11.6798 | -25.284 | -34.5274 | -37.5473 | 0.85655 | 0.65792 | 0.41427 | 0.037038 | -0.3752 | -0.92103 | -1.6387 | -2.4954 | -3.5166 | -4.7542 | -8.1075 | -19.11 | -26.9617 | -30.0559 | -0.76471 | -1.038 | -1.371 | -1.8777 | -2.4175 | -3.0983 | -3.9919 | -5.0675 | -6.3449 | -7.8962 | -12.0996 | -25.622 | -34.8267 | -37.8408
|  | MALMESBURY | FS |  |  | -1.0265 | -1.4455 | -2.1365 | -3.0673 | -4.0299 | -5.4879 | -7.1123 | -9.5256 | -12.5092 | -15.4581 | -21.0988 | -35.5834 | -44.976 | -45.3416 | 0.87184 | 0.6884 | 0.46819 | 0.17736 | -0.14227 | -0.58004 | -1.1182 | -1.7844 | -2.5485 | -3.4348 | -5.803 | -14.6069 | -24.8274 | -31.5715 | -0.72488 | -0.96215 | -1.2465 | -1.6499 | -2.0869 | -2.6368 | -3.31 | -4.1432 | -5.1083 | -6.2233 | -9.1901 | -20.2183 | -32.2088 | -39.324
MINETY GSP | SWINDON BSP | MANCHESTER ROAD | MINIMUM HEADROOM | SU 15254 85130 | YES | 11.2995 | 10.5029 | 9.7929 | 9.0003 | 8.21 | 7.3634 | 6.4664 | 5.5843 | 4.3529 | 3.0296 | 0.83529 | -4.1487 | -7.6728 | -10.0373 | 18.2311 | 17.6793 | 17.1906 | 16.7627 | 16.3222 | 15.57 | 14.8351 | 14.0178 | 12.8572 | 11.6084 | 9.2982 | 0.059291 | -18.3799 | -52.9969 | 14.2585 | 13.5435 | 12.8968 | 12.1855 | 11.4789 | 10.7333 | 9.9391 | 9.1444 | 8.0482 | 6.8736 | 4.8688 | 0.43133 | -2.6546 | -4.7586
|  | MANCHESTER ROAD | CT |  |  | 11.7272 | 11.2179 | 10.7485 | 10.2331 | 9.7061 | 8.9365 | 8.1946 | 7.4027 | 6.0552 | 4.6436 | 2.4114 | -3.5268 | -7.6728 | -10.0373 | 18.3107 | 17.7972 | 17.2805 | 16.8192 | 16.3222 | 15.57 | 14.8351 | 14.0178 | 12.8572 | 11.6084 | 9.2982 | 1.9996 | -8.2723 | -24.8739 | 14.6494 | 14.2212 | 13.8101 | 13.3687 | 12.914 | 12.2326 | 11.5642 | 10.8388 | 9.6123 | 8.3278 | 6.2733 | 1.0071 | -2.6546 | -4.7586
|  | MANCHESTER ROAD | LW |  |  | 11.2995 | 10.5029 | 9.7929 | 9.0003 | 8.21 | 7.3634 | 6.4664 | 5.5843 | 4.3529 | 3.0296 | 0.83529 | -4.1487 | -6.7246 | -8.2733 | 18.2311 | 17.6793 | 17.1906 | 16.7627 | 16.35 | 15.8874 | 15.411 | 14.9434 | 14.2981 | 13.6008 | 12.4066 | 9.9449 | 8.5509 | 7.5243 | 14.2585 | 13.5435 | 12.8968 | 12.1855 | 11.4789 | 10.7333 | 9.9391 | 9.1444 | 8.0482 | 6.8736 | 4.8688 | 0.43133 | -1.882 | -3.3222
|  | MANCHESTER ROAD | ST |  |  | 11.947 | 11.5707 | 11.2318 | 11.1213 | 11.007 | 10.7063 | 10.4463 | 10.19 | 9.668 | 9.0414 | 7.6478 | 2.8564 | 0.93436 | -0.49612 | 18.4114 | 17.9649 | 17.5139 | 17.2095 | 16.8723 | 16.3165 | 15.7797 | 15.2064 | 14.4403 | 13.5803 | 11.8265 | 5.2956 | -4.9434 | -22.1093 | 14.8361 | 14.533 | 14.2535 | 14.1569 | 14.0549 | 13.7774 | 13.5275 | 13.2748 | 12.8783 | 12.4195 | 11.6752 | 7.6359 | 5.7138 | 3.2825
|  | MANCHESTER ROAD | FS |  |  | 11.7272 | 11.2179 | 10.7485 | 10.2331 | 9.7061 | 8.9365 | 8.1946 | 7.4027 | 6.0552 | 4.6436 | 2.4114 | -3.5268 | -7.6728 | -10.0373 | 18.5254 | 18.0392 | 17.5577 | 17.0581 | 16.5086 | 15.8687 | 15.1563 | 14.3741 | 13.3821 | 12.2456 | 9.6819 | 0.059291 | -18.3799 | -52.9969 | 14.9605 | 14.6446 | 14.3713 | 14.1539 | 13.9294 | 13.664 | 13.3823 | 13.0886 | 12.6695 | 12.1941 | 11.3234 | 8.6377 | 5.6488 | 2.6357
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON | MINIMUM HEADROOM | SU 07592 05256 | YES | 7.2824 | 6.8986 | 6.3896 | 5.7566 | 5.1703 | 4.1529 | 2.8177 | 1.1762 | -0.73008 | -2.6499 | -7.2265 | -14.5888 | -17.9166 | -19.5104 | 7.9732 | 7.8446 | 7.3348 | 6.7255 | 6.2308 | 5.3692 | 4.2982 | 2.9212 | 1.2585 | -0.35047 | -3.9163 | -9.9379 | -12.9418 | -15.9903 | 6.7334 | 6.2968 | 5.6747 | 4.9504 | 4.3595 | 3.3451 | 2.0696 | 0.41022 | -1.5958 | -3.5421 | -7.969 | -15.2616 | -18.6976 | -22.554
|  | MANNINGTON | CT |  |  | 7.2851 | 6.9902 | 6.3896 | 5.7566 | 5.181 | 4.1529 | 2.8732 | 1.2496 | -0.73008 | -2.6402 | -6.262 | -14.5888 | -17.7353 | -18.7767 | 7.9732 | 7.8884 | 7.3348 | 6.7255 | 6.2308 | 5.3692 | 4.2982 | 2.9212 | 1.2585 | -0.35047 | -3.2633 | -9.9379 | -12.4883 | -13.4478 | 6.7334 | 6.3498 | 5.6747 | 4.9504 | 4.3595 | 3.3451 | 2.0794 | 0.41913 | -1.5958 | -3.5421 | -7.071 | -15.2616 | -18.4029 | -19.4684
|  | MANNINGTON | LW |  |  | 7.2824 | 6.8986 | 6.3926 | 5.8336 | 5.1703 | 4.3754 | 2.8177 | 1.1762 | -0.63126 | -2.6499 | -7.2265 | -14.4232 | -15.7707 | -13.5452 | 7.9794 | 7.8446 | 7.424 | 6.9062 | 6.304 | 5.657 | 4.3648 | 2.987 | 1.4699 | -0.22782 | -3.9163 | -9.6309 | -10.7487 | -9.0803 | 6.7496 | 6.2968 | 5.7274 | 5.0977 | 4.369 | 3.5928 | 2.0696 | 0.41022 | -1.4329 | -3.4946 | -7.969 | -15.0401 | -16.4187 | -14.2759
|  | MANNINGTON | ST |  |  | 7.3653 | 7.3329 | 6.9705 | 6.529 | 6.2517 | 5.8052 | 5.042 | 4.261 | 3.3089 | 2.1328 | -1.0395 | -11.3569 | -17.9166 | -19.5104 | 8.0301 | 8.0011 | 7.6407 | 7.3289 | 7.2321 | 6.7966 | 6.0782 | 5.4102 | 4.5913 | 3.581 | 0.85196 | -7.5705 | -12.9418 | -14.3445 | 6.9308 | 6.8244 | 6.4361 | 5.9662 | 5.6059 | 5.0608 | 4.2248 | 3.4475 | 2.4958 | 1.2907 | -1.9675 | -12.1187 | -18.6976 | -20.3277
|  | MANNINGTON | FS |  |  | 7.2851 | 6.9902 | 6.3896 | 5.7566 | 5.181 | 4.1529 | 2.8732 | 1.2496 | -0.73008 | -2.6402 | -6.262 | -14.5888 | -17.7353 | -18.7767 | 8.0861 | 8.0279 | 7.8528 | 7.6676 | 7.535 | 7.2204 | 6.7489 | 6.2156 | 5.6246 | 4.9327 | 3.0308 | -3.9907 | -11.6972 | -15.9903 | 6.9864 | 6.8714 | 6.6302 | 6.3066 | 5.9772 | 5.5504 | 4.9955 | 4.3753 | 3.6803 | 2.8685 | 0.59229 | -7.8487 | -17.3178 | -22.554
LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET | MINIMUM HEADROOM | SU 86479 04732 | YES | 5.3085 | 4.9608 | 4.5689 | 4.042 | 3.548 | 3.0134 | 2.4175 | 1.7577 | 0.97391 | -0.60836 | -5.1245 | -12.2683 | -14.7894 | -16.6774 | 7.7523 | 7.644 | 7.5197 | 7.3388 | 7.129 | 6.7948 | 6.1026 | 5.2483 | 4.2588 | 2.9356 | -0.41088 | -5.5733 | -7.3658 | -8.9227 | 5.2478 | 5.0511 | 4.7299 | 4.2494 | 3.7808 | 3.2578 | 2.6472 | 1.9686 | 0.58392 | -1.0616 | -4.9456 | -11.5857 | -14.0196 | -15.9226
|  | MARKET | CT |  |  | 5.5511 | 5.3559 | 5.1118 | 4.7605 | 4.4464 | 4.0868 | 3.6731 | 3.1947 | 2.4533 | 1.6879 | -0.45596 | -5.7869 | -8.2874 | -10.0422 | 7.7534 | 7.6609 | 7.5472 | 7.4362 | 7.3164 | 7.1493 | 6.9347 | 6.3849 | 5.7078 | 4.9441 | 3.1981 | -0.31938 | -1.7691 | -3.4454 | 5.2934 | 5.1738 | 5.0242 | 4.8639 | 4.6208 | 4.2871 | 3.8875 | 3.4156 | 2.5644 | 1.5276 | -0.81319 | -5.248 | -7.5658 | -9.2287
|  | MARKET | LW |  |  | 5.3085 | 4.9608 | 4.5689 | 4.042 | 3.548 | 3.0134 | 2.4175 | 1.7577 | 0.97391 | -0.60836 | -5.1245 | -12.2683 | -14.7894 | -16.6774 | 7.7523 | 7.644 | 7.5197 | 7.3388 | 7.129 | 6.7948 | 6.1026 | 5.2483 | 4.2588 | 2.9356 | -0.41088 | -5.5733 | -7.3658 | -8.9227 | 5.2478 | 5.0511 | 4.7299 | 4.2494 | 3.7808 | 3.2578 | 2.6472 | 1.9686 | 0.58392 | -1.0616 | -4.9456 | -11.5857 | -14.0196 | -15.9226
|  | MARKET | ST |  |  | 5.7299 | 5.6315 | 5.4859 | 5.3493 | 5.2745 | 5.188 | 5.0667 | 4.9456 | 4.7937 | 4.6445 | 4.281 | 2.4173 | 1.1068 | -1.3973 | 7.7941 | 7.7338 | 7.6554 | 7.5258 | 7.4227 | 7.3108 | 7.1625 | 7.0269 | 6.8668 | 6.6927 | 6.2637 | 4.3481 | 2.8949 | -0.55467 | 5.3478 | 5.2709 | 5.1691 | 5.0291 | 4.9244 | 4.8096 | 4.6561 | 4.5112 | 4.3418 | 4.1445 | 3.425 | 1.1228 | -0.080995 | -1.2222
|  | MARKET | FS |  |  | 5.5511 | 5.3559 | 5.1118 | 4.7605 | 4.4464 | 4.0868 | 3.6731 | 3.1947 | 2.4533 | 1.6879 | -0.45596 | -5.7869 | -8.2874 | -10.0422 | 7.7901 | 7.7199 | 7.6334 | 7.5445 | 7.4574 | 7.3578 | 7.2311 | 6.9415 | 6.547 | 6.1107 | 5.1329 | 2.74 | -0.026197 | -4.6111 | 5.3471 | 5.2621 | 5.1554 | 5.0561 | 4.9672 | 4.8424 | 4.5641 | 4.2383 | 3.8613 | 3.4542 | 2.5736 | 0.64748 | -0.83459 | -2.3116
MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH | MINIMUM HEADROOM | SU 19293 68264 | YES | 1.7334 | 1.6423 | 1.5551 | 1.3418 | 0.87135 | 0.37225 | -0.36228 | -1.2315 | -2.2241 | -3.3159 | -5.6716 | -10.0849 | -14.0588 | -16.8204 | 3.5242 | 3.3438 | 3.1673 | 2.9452 | 2.6553 | 2.2983 | 1.8457 | 1.2443 | 0.50787 | -0.2357 | -1.7915 | -5.2295 | -8.7056 | -13.6978 | 1.5193 | 1.2363 | 0.95947 | 0.60996 | 0.17899 | -0.27871 | -0.94422 | -1.7272 | -2.6183 | -3.5981 | -5.7643 | -9.9306 | -13.3937 | -16.0127
|  | MARLBOROUGH SOUTH | CT |  |  | 1.7363 | 1.6547 | 1.5563 | 1.4334 | 1.2744 | 0.81271 | 0.23911 | -0.55082 | -1.6023 | -2.6384 | -4.6499 | -9.3919 | -11.8745 | -13.0111 | 3.5466 | 3.3844 | 3.1945 | 2.9547 | 2.6828 | 2.2983 | 1.8669 | 1.2586 | 0.50787 | -0.2357 | -1.6894 | -5.2295 | -7.4808 | -9.6468 | 1.6664 | 1.4814 | 1.2705 | 0.96054 | 0.61344 | 0.14758 | -0.37305 | -1.0848 | -2.0372 | -2.9799 | -4.8217 | -9.2549 | -11.509 | -12.5084
|  | MARLBOROUGH SOUTH | LW |  |  | 1.7334 | 1.6423 | 1.5551 | 1.3418 | 0.87135 | 0.37225 | -0.36228 | -1.2315 | -2.2241 | -3.3159 | -5.6716 | -10.0849 | -14.0588 | -16.8204 | 3.5242 | 3.3438 | 3.1673 | 2.9452 | 2.6553 | 2.343 | 1.8457 | 1.2443 | 0.57703 | -0.16745 | -1.7915 | -4.714 | -6.2167 | -8.299 | 1.5193 | 1.2363 | 0.95947 | 0.60996 | 0.17899 | -0.27871 | -0.94422 | -1.7272 | -2.6183 | -3.5981 | -5.7643 | -9.9306 | -13.3937 | -16.0127
|  | MARLBOROUGH SOUTH | ST |  |  | 1.8039 | 1.7816 | 1.7511 | 1.6922 | 1.6165 | 1.5207 | 1.3956 | 1.2501 | 0.82528 | 0.31091 | -1.0586 | -5.3456 | -8.2226 | -9.6849 | 3.649 | 3.573 | 3.4781 | 3.3396 | 3.1682 | 2.9544 | 2.6858 | 2.3641 | 2.0005 | 1.5597 | 0.40216 | -3.2589 | -6.1197 | -8.4488 | 1.8297 | 1.7634 | 1.6819 | 1.5473 | 1.3767 | 1.1631 | 0.89876 | 0.57806 | 0.20432 | -0.24549 | -1.482 | -5.6483 | -8.3928 | -9.6686
|  | MARLBOROUGH SOUTH | FS |  |  | 1.7363 | 1.6547 | 1.5563 | 1.4334 | 1.2744 | 0.81271 | 0.23911 | -0.55082 | -1.6023 | -2.6384 | -4.6499 | -9.3919 | -11.8745 | -13.0111 | 3.6328 | 3.5501 | 3.4464 | 3.3076 | 3.1372 | 2.9305 | 2.6796 | 2.3777 | 2.0387 | 1.6403 | 0.57989 | -3.55 | -8.7056 | -13.6978 | 1.8201 | 1.7577 | 1.6767 | 1.5343 | 1.3616 | 1.1549 | 0.90977 | 0.61503 | 0.26928 | -0.1337 | -1.1827 | -5.6499 | -10.6409 | -13.7574
NURSLING GSP | ROWNHAMS | MAYBUSH | MINIMUM HEADROOM | SU 38426 14930 | YES | 4.5299 | 4.1183 | 3.7146 | 2.8886 | 1.9713 | 0.96203 | -0.27003 | -1.5599 | -2.9974 | -4.4637 | -7.4777 | -14.314 | -17.4277 | -18.2361 | 6.0573 | 5.7989 | 5.5503 | 5.0116 | 4.3848 | 3.6572 | 2.7141 | 1.7396 | 0.65635 | -0.41835 | -2.9012 | -9.9682 | -22.3143 | -42.6498 | 5.009 | 4.6285 | 4.2551 | 3.4599 | 2.5693 | 1.5745 | 0.35125 | -0.99191 | -2.5123 | -4.0601 | -7.2271 | -13.6493 | -16.8208 | -17.8518
|  | MAYBUSH | CT |  |  | 4.8627 | 4.6936 | 4.5026 | 3.8634 | 3.1722 | 2.3759 | 1.5038 | 0.49784 | -0.93855 | -2.3561 | -5.0053 | -12.125 | -16.1437 | -18.0809 | 6.1352 | 5.9569 | 5.7505 | 5.2398 | 4.669 | 3.9865 | 3.2181 | 2.3247 | 1.0948 | -0.19503 | -2.8034 | -9.9682 | -16.9572 | -26.4552 | 5.302 | 5.1435 | 4.9638 | 4.3542 | 3.6902 | 2.921 | 2.0724 | 1.0204 | -0.48318 | -1.9541 | -4.6588 | -11.3239 | -15.1474 | -17.0447
|  | MAYBUSH | LW |  |  | 4.5299 | 4.1183 | 3.7146 | 2.8886 | 1.9713 | 0.96203 | -0.27003 | -1.5599 | -2.9974 | -4.4637 | -7.4777 | -14.314 | -17.4277 | -18.2361 | 6.0573 | 5.7989 | 5.5503 | 5.0116 | 4.3848 | 3.6572 | 2.7141 | 1.7396 | 0.65635 | -0.41835 | -2.9012 | -8.9041 | -12.4136 | -13.4498 | 5.009 | 4.6285 | 4.2551 | 3.4599 | 2.5693 | 1.5745 | 0.35125 | -0.99191 | -2.5123 | -4.0601 | -7.2271 | -13.6493 | -16.8208 | -17.8518
|  | MAYBUSH | ST |  |  | 5.2061 | 5.2495 | 5.2643 | 5.0423 | 4.8027 | 4.5336 | 4.1842 | 3.8319 | 3.3146 | 2.8076 | 1.7454 | -3.8514 | -8.3892 | -11.2615 | 6.3003 | 6.2365 | 6.1455 | 5.7498 | 5.3406 | 4.8908 | 4.3416 | 3.7971 | 3.0347 | 2.2846 | 0.46233 | -6.4147 | -14.348 | -24.2932 | 5.6113 | 5.6468 | 5.6558 | 5.3882 | 5.1112 | 4.8066 | 4.4146 | 4.0336 | 3.4689 | 2.8814 | 1.5372 | -4.1675 | -8.7286 | -11.5786
|  | MAYBUSH | FS |  |  | 4.8627 | 4.6936 | 4.5026 | 3.8634 | 3.1722 | 2.3759 | 1.5038 | 0.49784 | -0.93855 | -2.3561 | -5.0053 | -12.125 | -16.1437 | -18.0809 | 6.3242 | 6.1839 | 6.0275 | 5.7221 | 5.3661 | 4.9397 | 4.4517 | 3.8954 | 3.174 | 2.2876 | -0.11133 | -8.9409 | -22.3143 | -42.6498 | 5.6131 | 5.5714 | 5.5213 | 5.3192 | 5.087 | 4.7978 | 4.4766 | 4.1047 | 3.6014 | 3.0287 | 1.6884 | -4.2934 | -10.519 | -14.6459
MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN | MINIMUM HEADROOM | ST 90170 64096 | YES | 15.4128 | 14.8246 | 14.3332 | 13.4341 | 12.4431 | 11.3797 | 10.2202 | 9.0627 | 7.6488 | 4.7696 | -1.705 | -14.9488 | -21.1785 | -25.0796 | 9.9286 | 9.6606 | 9.4459 | 9.0154 | 8.523 | 7.9746 | 6.9517 | 5.5683 | 3.6163 | 1.2982 | -3.7918 | -13.3259 | -16.8769 | -19.5017 | 6.1146 | 5.6673 | 5.296 | 4.5979 | 3.8148 | 2.9621 | 1.994 | 1.0134 | -0.14443 | -1.3479 | -3.9923 | -16.9677 | -22.2352 | -25.782
|  | MELKSHAM TOWN | CT |  |  | 15.9181 | 15.5993 | 15.318 | 14.6554 | 13.8795 | 12.9739 | 11.9565 | 10.4219 | 7.772 | 4.7696 | -1.705 | -14.9488 | -21.1785 | -25.0796 | 10.0676 | 9.8629 | 9.6692 | 9.3131 | 8.8271 | 8.0168 | 6.9517 | 5.5683 | 3.6163 | 1.2982 | -3.7918 | -13.3259 | -16.8769 | -19.5017 | 6.4635 | 6.2091 | 5.9843 | 5.4758 | 4.8754 | 4.1577 | 3.3407 | 2.4584 | 1.061 | -0.45707 | -3.9923 | -16.9677 | -22.2352 | -25.782
|  | MELKSHAM TOWN | LW |  |  | 15.4128 | 14.8246 | 14.3332 | 13.4341 | 12.4431 | 11.3797 | 10.2202 | 9.0627 | 7.6488 | 6.1976 | 3.2311 | -2.876 | -7.0236 | -9.5592 | 9.9286 | 9.6606 | 9.4459 | 9.0154 | 8.523 | 7.9746 | 7.3383 | 6.6982 | 5.9744 | 5.2157 | 3.6624 | 0.59007 | -1.7577 | -3.6234 | 6.1146 | 5.6673 | 5.296 | 4.5979 | 3.8148 | 2.9621 | 1.994 | 1.0134 | -0.14443 | -1.3479 | -3.8182 | -8.7988 | -12.2315 | -14.5806
|  | MELKSHAM TOWN | ST |  |  | 16.1436 | 15.982 | 15.875 | 15.5333 | 15.2064 | 14.85 | 14.4226 | 14.0908 | 13.662 | 13.2171 | 12.1497 | 7.8003 | 3.1918 | -1.9595 | 10.1573 | 10.0331 | 9.9304 | 9.5889 | 9.2826 | 8.957 | 8.5418 | 8.2209 | 7.7948 | 7.349 | 6.2647 | 2.4251 | -1.8177 | -6.8484 | 6.6179 | 6.4833 | 6.3905 | 6.0309 | 5.7016 | 5.3475 | 4.9031 | 4.5595 | 4.1106 | 3.6399 | 2.4872 | -1.8161 | -6.0469 | -10.1918
|  | MELKSHAM TOWN | FS |  |  | 15.9181 | 15.5993 | 15.318 | 14.6554 | 13.8795 | 12.9739 | 11.9565 | 10.4219 | 7.772 | 4.7696 | -1.705 | -14.9488 | -21.1785 | -25.0796 | 10.1675 | 10.0428 | 9.944 | 9.7456 | 9.5227 | 9.2712 | 8.9923 | 8.7045 | 8.3054 | 7.8715 | 6.8658 | 3.5754 | -1.0338 | -8.0307 | 6.6423 | 6.5196 | 6.4429 | 6.2094 | 5.949 | 5.6604 | 5.3441 | 5.0209 | 4.5834 | 4.1177 | 3.0746 | -0.20004 | -3.6401 | -7.0856
LOVEDEAN GSP | HAVANT | MEYRICK ROAD | MINIMUM HEADROOM | SU 70849 06469 | YES | 5.0854 | 4.3137 | 3.5053 | 1.9788 | 0.13835 | -1.7195 | -4.3935 | -7.497 | -10.8828 | -14.4925 | -21.9161 | -36.7292 | -50.0466 | -57.7875 | 8.1829 | 7.6901 | 7.1835 | 6.32 | 5.239 | 4.1295 | 2.4128 | 0.37887 | -1.8626 | -4.3781 | -9.2452 | -21.7686 | -31.4112 | -37.1381 | 4.5763 | 3.8974 | 3.1925 | 1.8474 | 0.22811 | -1.4241 | -3.7864 | -6.6572 | -9.8219 | -13.2174 | -20.2521 | -34.7155 | -47.3575 | -54.7365
|  | MEYRICK ROAD | CT |  |  | 5.3763 | 4.8261 | 4.1384 | 2.771 | 1.2441 | -0.67141 | -2.8267 | -5.7502 | -9.4995 | -13.2478 | -20.4068 | -36.7292 | -50.0466 | -57.7875 | 8.2138 | 7.7773 | 7.2376 | 6.3849 | 5.4253 | 4.1404 | 2.6863 | 0.64638 | -1.8626 | -4.3781 | -9.2279 | -21.7686 | -31.4112 | -37.1381 | 4.8513 | 4.3729 | 3.7777 | 2.5822 | 1.2416 | -0.45684 | -2.4044 | -5.1459 | -8.6512 | -12.1548 | -18.8566 | -34.7155 | -47.3575 | -54.7365
|  | MEYRICK ROAD | LW |  |  | 5.0854 | 4.3137 | 3.5053 | 1.9788 | 0.13835 | -1.7195 | -4.3935 | -7.497 | -10.8828 | -14.4925 | -21.9161 | -34.4814 | -38.4273 | -37.4582 | 8.1829 | 7.6901 | 7.1835 | 6.32 | 5.239 | 4.1295 | 2.4128 | 0.37887 | -1.8225 | -4.2195 | -9.2452 | -17.4757 | -19.7816 | -18.7536 | 4.5763 | 3.8974 | 3.1925 | 1.8474 | 0.22811 | -1.4241 | -3.7864 | -6.6572 | -9.8219 | -13.2174 | -20.2521 | -32.1052 | -35.7172 | -34.6264
|  | MEYRICK ROAD | ST |  |  | 5.7846 | 5.5844 | 5.2987 | 4.6624 | 3.9218 | 3.129 | 2.1375 | 0.96816 | -0.33661 | -1.8948 | -5.7895 | -18.2969 | -27.4207 | -32.2142 | 8.4947 | 8.3186 | 8.0782 | 7.608 | 7.0656 | 6.4592 | 5.6903 | 4.7914 | 3.7799 | 2.5642 | -0.56398 | -10.631 | -18.3759 | -23.0525 | 5.2247 | 5.0616 | 4.8297 | 4.2986 | 3.6873 | 3.0228 | 2.1846 | 1.1638 | -0.045266 | -1.5037 | -5.2278 | -17.3483 | -26.3396 | -30.5265
|  | MEYRICK ROAD | FS |  |  | 5.3763 | 4.8261 | 4.1384 | 2.771 | 1.2441 | -0.67141 | -2.8267 | -5.7502 | -9.4995 | -13.2478 | -20.4068 | -36.7292 | -50.0466 | -57.7875 | 8.4321 | 8.2117 | 7.9247 | 7.4689 | 6.9343 | 6.2982 | 5.5309 | 4.5717 | 3.4744 | 2.2731 | -0.60716 | -10.5208 | -21.6756 | -31.015 | 5.1597 | 4.9625 | 4.6969 | 4.1717 | 3.5675 | 2.8637 | 2.0194 | 0.87709 | -0.45526 | -1.9015 | -5.3167 | -16.9619 | -29.3055 | -37.2397
BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP | MINIMUM HEADROOM | SU 30984 40155 | YES | 1.384 | 1.2752 | 1.1585 | 1.0589 | 0.949 | 0.7093 | 0.20113 | -0.47383 | -1.3498 | -2.4728 | -5.557 | -16.3235 | -21.746 | -21.6321 | 2.8501 | 2.7738 | 2.6918 | 2.5806 | 2.4364 | 2.2804 | 2.0399 | 1.6475 | 0.97362 | 0.090936 | -2.3288 | -10.8072 | -15.0832 | -15.0898 | 1.8413 | 1.7414 | 1.637 | 1.5476 | 1.34 | 1.0045 | 0.55273 | -0.050998 | -0.89421 | -1.9838 | -4.965 | -15.3633 | -20.6249 | -20.5894
|  | MIDDLE WALLOP | CT |  |  | 1.4635 | 1.3862 | 1.3042 | 1.1946 | 1.0684 | 0.7093 | 0.20113 | -0.47383 | -1.3498 | -2.4728 | -5.557 | -16.3235 | -21.746 | -21.6321 | 2.8748 | 2.831 | 2.7813 | 2.7121 | 2.6255 | 2.5183 | 2.1655 | 1.6475 | 0.97362 | 0.090936 | -2.3288 | -10.8072 | -15.0832 | -15.0898 | 1.9041 | 1.8255 | 1.7414 | 1.5824 | 1.34 | 1.0045 | 0.55273 | -0.050998 | -0.89421 | -1.9838 | -4.965 | -15.3633 | -20.6249 | -20.5894
|  | MIDDLE WALLOP | LW |  |  | 1.384 | 1.2752 | 1.1585 | 1.0589 | 0.949 | 0.82841 | 0.68659 | 0.53065 | 0.33858 | 0.12877 | -0.31859 | -1.1452 | -1.8413 | -2.5079 | 2.8553 | 2.8084 | 2.7576 | 2.7085 | 2.6518 | 2.5871 | 2.5076 | 2.4183 | 2.295 | 2.1578 | 1.8621 | 1.3385 | 0.72825 | -0.0078433 | 1.8413 | 1.7414 | 1.637 | 1.5476 | 1.4506 | 1.3462 | 1.2235 | 1.0918 | 0.92807 | 0.75267 | 0.35824 | -0.41112 | -1.1682 | -1.9605
|  | MIDDLE WALLOP | ST |  |  | 1.5108 | 1.4661 | 1.4074 | 1.2867 | 1.1715 | 1.0518 | 0.89856 | 0.76606 | 0.58218 | 0.3891 | -0.043758 | -0.98852 | -1.7417 | -2.453 | 2.9015 | 2.8761 | 2.8426 | 2.7391 | 2.6487 | 2.5553 | 2.4292 | 2.3275 | 2.1739 | 2.0174 | 1.6677 | 0.83832 | 0.031237 | -0.82811 | 1.9596 | 1.9209 | 1.8707 | 1.747 | 1.6363 | 1.5249 | 1.3811 | 1.2689 | 1.1018 | 0.93435 | 0.53457 | -0.41133 | -1.2623 | -2.0602
|  | MIDDLE WALLOP | FS |  |  | 1.4635 | 1.3862 | 1.3042 | 1.1946 | 1.0684 | 0.7093 | 0.20113 | -0.47383 | -1.3498 | -2.4728 | -5.557 | -16.3235 | -21.746 | -21.6321 | 2.8501 | 2.7738 | 2.6918 | 2.5806 | 2.4364 | 2.2804 | 2.0399 | 1.7485 | 1.418 | 1.0458 | 0.18952 | -2.018 | -3.6218 | -4.3635 | 1.9475 | 1.8885 | 1.825 | 1.6907 | 1.5174 | 1.3375 | 1.0133 | 0.60381 | 0.13709 | -0.38921 | -1.5921 | -4.3982 | -6.3067 | -7.0473
BRAMLEY (FLEE) | FERNHURST | MIDHURST | MINIMUM HEADROOM | SU 88127 19555 | YES | 16.1137 | 15.7888 | 15.461 | 15.0706 | 14.6471 | 14.2161 | 13.6842 | 13.106 | 12.4214 | 10.8425 | 7.2814 | 0.51669 | -2.1448 | -3.7131 | 17.9094 | 17.7701 | 17.6311 | 17.4623 | 17.2647 | 17.059 | 16.7648 | 16.3976 | 15.399 | 14.2482 | 11.6855 | 7.0252 | 5.4892 | 4.5057 | 15.1758 | 14.8809 | 14.584 | 14.2277 | 13.8418 | 13.4484 | 12.9655 | 12.4421 | 11.4679 | 9.9419 | 6.5677 | 0.20779 | -2.2225 | -3.6619
|  | MIDHURST | CT |  |  | 16.3821 | 16.1964 | 15.993 | 15.6463 | 15.2843 | 14.8469 | 14.3679 | 13.7715 | 12.4548 | 10.8425 | 7.2814 | 0.51669 | -2.1448 | -3.7131 | 17.9675 | 17.8556 | 17.7268 | 17.5476 | 17.3524 | 17.0934 | 16.8024 | 16.3976 | 15.399 | 14.2482 | 11.6855 | 7.0252 | 5.4892 | 4.5057 | 15.4199 | 15.2505 | 15.0648 | 14.7467 | 14.4126 | 14.0081 | 13.5614 | 12.8089 | 11.4679 | 9.9419 | 6.5677 | 0.20779 | -2.2225 | -3.6619
|  | MIDHURST | LW |  |  | 16.1137 | 15.7888 | 15.461 | 15.0706 | 14.6471 | 14.2161 | 13.6842 | 13.106 | 12.4214 | 11.701 | 10.1837 | 6.7739 | 4.9879 | 4.5974 | 17.9094 | 17.7701 | 17.6311 | 17.4623 | 17.2647 | 17.059 | 16.7648 | 16.4248 | 16.0404 | 15.6211 | 14.7154 | 12.8909 | 12.1656 | 12.2396 | 15.1758 | 14.8809 | 14.584 | 14.2277 | 13.8418 | 13.4484 | 12.9655 | 12.4421 | 11.8093 | 11.1406 | 9.7278 | 6.6138 | 5.0987 | 4.8498
|  | MIDHURST | ST |  |  | 16.5418 | 16.4546 | 16.3559 | 16.2101 | 16.0419 | 15.8485 | 15.6246 | 15.3601 | 15.0513 | 14.6934 | 13.795 | 10.9409 | 8.6799 | 6.8945 | 18.0393 | 17.9802 | 17.9091 | 17.8093 | 17.6921 | 17.5515 | 17.3796 | 17.1753 | 16.9418 | 16.6627 | 15.9454 | 13.7709 | 12.0566 | 10.5404 | 15.5671 | 15.4877 | 15.3967 | 15.2604 | 15.1029 | 14.9204 | 14.7063 | 14.4535 | 14.1588 | 13.8149 | 12.9461 | 10.2545 | 8.2062 | 6.6669
|  | MIDHURST | FS |  |  | 16.3821 | 16.1964 | 15.993 | 15.6463 | 15.2843 | 14.8469 | 14.3679 | 13.7715 | 12.4548 | 10.8425 | 7.2814 | 0.51669 | -2.1448 | -3.7131 | 18.027 | 17.9604 | 17.8798 | 17.7684 | 17.6348 | 17.4759 | 17.2804 | 17.0453 | 16.7638 | 16.4307 | 15.5548 | 12.3748 | 9.2624 | 6.6227 | 15.5688 | 15.4921 | 15.4039 | 15.2429 | 15.0579 | 14.8481 | 14.5959 | 14.3008 | 13.9279 | 13.4988 | 12.4117 | 8.4632 | 5.0408 | 2.9387
AXMINSTER | YEOVIL BSP | MILBORNE PORT | MINIMUM HEADROOM | ST 67929 19741 | YES | 0.4841 | 0.33827 | 0.18737 | 0.00072247 | -0.23648 | -0.62453 | -1.3002 | -2.2139 | -3.3951 | -4.839 | -8.5586 | -17.0809 | -23.0891 | -26.5014 | 0.22039 | 0.17321 | 0.10955 | 0.023557 | -0.08915 | -0.25572 | -0.60429 | -1.2276 | -2.0273 | -3.0582 | -5.741 | -12.2416 | -16.8089 | -19.4256 | 0.58171 | 0.43311 | 0.27898 | 0.090559 | -0.14201 | -0.39306 | -0.89656 | -1.7718 | -2.9003 | -4.2813 | -7.8419 | -15.9927 | -21.7315 | -24.9934
|  | MILBORNE PORT | CT |  |  | 0.55472 | 0.44756 | 0.3105 | 0.11423 | -0.12049 | -0.62453 | -1.3002 | -2.2139 | -3.3951 | -4.839 | -8.5586 | -17.0809 | -23.0891 | -26.5014 | 0.22039 | 0.17321 | 0.10955 | 0.023557 | -0.08915 | -0.25572 | -0.60429 | -1.2276 | -2.0273 | -3.0582 | -5.741 | -12.2416 | -16.8089 | -19.4256 | 0.63383 | 0.51976 | 0.37551 | 0.17961 | -0.03902 | -0.35299 | -0.89656 | -1.7718 | -2.9003 | -4.2813 | -7.8419 | -15.9927 | -21.7315 | -24.9934
|  | MILBORNE PORT | LW |  |  | 0.4841 | 0.33827 | 0.18737 | 0.00072247 | -0.23648 | -0.5002 | -0.88778 | -1.3644 | -1.9198 | -2.5473 | -3.9221 | -6.1294 | -6.6001 | -6.22 | 0.24401 | 0.21593 | 0.17159 | 0.094969 | 0.002944 | -0.095034 | -0.23553 | -0.407 | -0.60731 | -0.91969 | -1.9411 | -3.4925 | -3.7129 | -3.3357 | 0.58171 | 0.43311 | 0.27898 | 0.090559 | -0.14201 | -0.39306 | -0.76782 | -1.2306 | -1.7694 | -2.3794 | -3.7197 | -5.8426 | -6.262 | -5.8605
|  | MILBORNE PORT | ST |  |  | 0.63291 | 0.58992 | 0.53434 | 0.46289 | 0.37618 | 0.25962 | 0.10465 | -0.088349 | -0.30959 | -0.58884 | -1.3609 | -4.0101 | -5.7922 | -6.3684 | 0.26337 | 0.25306 | 0.23983 | 0.22267 | 0.20051 | 0.17303 | 0.1172 | 0.042503 | -0.041663 | -0.14584 | -0.41981 | -2.3512 | -3.7208 | -4.1886 | 0.71082 | 0.66555 | 0.60608 | 0.52853 | 0.43162 | 0.314 | 0.16357 | -0.024569 | -0.24161 | -0.51806 | -1.2649 | -3.8204 | -5.534 | -6.0834
|  | MILBORNE PORT | FS |  |  | 0.55472 | 0.44756 | 0.3105 | 0.11423 | -0.12049 | -0.62453 | -1.3002 | -2.2139 | -3.3951 | -4.839 | -8.5586 | -17.0809 | -23.0891 | -26.5014 | 0.26689 | 0.25823 | 0.24857 | 0.23662 | 0.22082 | 0.20054 | 0.17776 | 0.13052 | 0.067095 | -0.0033729 | -0.18126 | -1.0086 | -2.4973 | -3.5327 | 0.73386 | 0.69819 | 0.66152 | 0.60419 | 0.53116 | 0.43875 | 0.34074 | 0.22267 | 0.072949 | -0.095251 | -0.53026 | -2.2008 | -4.0207 | -5.1742
BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD | MINIMUM HEADROOM | SU 94719 43018 | YES | 10.4405 | 10.05 | 9.6527 | 9.1658 | 8.7093 | 6.7207 | 3.9559 | 0.19907 | -4.7277 | -10.7439 | -25.3244 | -50.721 | -57.9288 | -62.7872 | 11.9645 | 11.8044 | 11.6173 | 11.4418 | 11.0404 | 9.6405 | 7.6732 | 4.8796 | 1.1582 | -3.4211 | -14.5876 | -33.7218 | -38.7917 | -42.3738 | 10.3365 | 10.0317 | 9.7197 | 9.3127 | 8.4014 | 6.6561 | 4.0138 | 0.41738 | -4.2829 | -10.0302 | -23.9739 | -48.1963 | -54.9931 | -59.6035
|  | MILFORD | CT |  |  | 10.6858 | 10.4159 | 10.1132 | 9.6776 | 8.7194 | 6.7207 | 3.9559 | 0.19907 | -4.7277 | -10.7439 | -25.3244 | -50.721 | -57.9288 | -62.7872 | 12.0008 | 11.8427 | 11.6613 | 11.4427 | 11.0404 | 9.6405 | 7.6732 | 4.8796 | 1.1582 | -3.4211 | -14.5876 | -33.7218 | -38.7917 | -42.3738 | 10.5347 | 10.3252 | 10.0873 | 9.6027 | 8.4014 | 6.6561 | 4.0138 | 0.41738 | -4.2829 | -10.0302 | -23.9739 | -48.1963 | -54.9931 | -59.6035
|  | MILFORD | LW |  |  | 10.4405 | 10.05 | 9.6527 | 9.1658 | 8.7093 | 8.2287 | 7.7105 | 7.1791 | 6.5162 | 5.8309 | 4.4281 | 1.4713 | -0.26979 | -0.75921 | 11.9645 | 11.8044 | 11.6434 | 11.4474 | 11.2588 | 11.0486 | 10.8104 | 10.565 | 10.2927 | 10.0022 | 9.3922 | 8.1317 | 7.4302 | 7.2413 | 10.3365 | 10.0317 | 9.7197 | 9.3127 | 8.9233 | 8.5081 | 8.0564 | 7.5927 | 7.0308 | 6.4466 | 5.2433 | 2.5786 | 0.97273 | 0.51416
|  | MILFORD | ST |  |  | 10.7828 | 10.5909 | 10.3911 | 10.2409 | 10.1168 | 9.9705 | 9.7813 | 9.589 | 9.3853 | 9.1504 | 8.5972 | 6.728 | 4.8218 | 2.5782 | 12.0452 | 11.9258 | 11.7975 | 11.672 | 11.5586 | 11.4255 | 11.2532 | 11.0795 | 10.9102 | 10.7122 | 10.2292 | 8.7953 | 7.4149 | 5.7815 | 10.6122 | 10.4653 | 10.3099 | 10.1697 | 10.0494 | 9.9085 | 9.7246 | 9.542 | 9.3517 | 9.1294 | 8.599 | 6.8659 | 5.1686 | 3.3465
|  | MILFORD | FS |  |  | 10.6858 | 10.4159 | 10.1132 | 9.6776 | 8.7194 | 6.7207 | 3.9559 | 0.19907 | -4.7277 | -10.7439 | -25.3244 | -50.721 | -57.9288 | -62.7872 | 11.9892 | 11.8139 | 11.6173 | 11.4418 | 11.2674 | 11.0147 | 10.7404 | 10.3516 | 9.8956 | 9.4483 | 8.5927 | 6.2459 | 4.6396 | 2.975 | 10.5546 | 10.3514 | 10.1265 | 9.9173 | 9.719 | 9.4234 | 9.1087 | 8.6539 | 8.0744 | 7.5127 | 6.4709 | 3.6095 | 1.6443 | -0.042837
MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA | MINIMUM HEADROOM | SZ 28252 93347 | YES | 0.44028 | -0.27651 | 11.2708 | 10.0689 | 8.5397 | 7.0012 | 4.6217 | 1.8153 | -1.3753 | -4.9349 | -12.6253 | -26.1662 | -33.0257 | -35.4673 | 2.1102 | 1.5776 | 12.7095 | 11.8754 | 10.9439 | 9.6181 | 8.1777 | 6.0343 | 3.3712 | 0.78423 | -4.9119 | -15.5 | -20.6204 | -23.899 | -0.022342 | -0.71173 | 10.2994 | 9.1516 | 7.6798 | 6.2359 | 3.9346 | 1.1868 | -1.9398 | -5.4563 | -13.0223 | -26.2453 | -32.7642 | -35.0653
|  | MILFORD-ON-SEA | CT |  |  | 0.61176 | 0.066644 | 11.6662 | 10.4689 | 9.1432 | 7.3347 | 5.452 | 2.6759 | -0.89167 | -4.3499 | -10.7264 | -26.1662 | -33.0257 | -35.4673 | 2.1102 | 1.6 | 12.7095 | 11.8754 | 10.9548 | 9.6181 | 8.1978 | 6.0403 | 3.3712 | 0.78423 | -3.9857 | -15.5 | -20.6204 | -23.0697 | 0.11429 | -0.42167 | 10.5632 | 9.4329 | 8.1846 | 6.4481 | 4.6137 | 1.8806 | -1.6048 | -4.9827 | -11.2097 | -26.2453 | -32.7642 | -35.0653
|  | MILFORD-ON-SEA | LW |  |  | 0.44028 | -0.27651 | 11.2708 | 10.0689 | 8.5397 | 7.0012 | 4.6217 | 1.8153 | -1.3753 | -4.9349 | -12.6253 | -25.1152 | -28.2642 | -25.3852 | 2.1447 | 1.5776 | 12.7474 | 11.9737 | 10.9439 | 9.9259 | 8.1777 | 6.0343 | 3.6193 | 0.91968 | -4.9119 | -14.1537 | -16.2634 | -13.9528 | -0.022342 | -0.71173 | 10.2994 | 9.1516 | 7.6798 | 6.2359 | 3.9346 | 1.1868 | -1.9398 | -5.4563 | -13.0223 | -25.2444 | -28.2915 | -25.4503
|  | MILFORD-ON-SEA | ST |  |  | 0.9831 | 0.79648 | 12.8083 | 12.2886 | 11.641 | 10.8695 | 9.8825 | 8.6519 | 7.1802 | 5.3427 | 0.37926 | -16.1289 | -27.2865 | -31.2695 | 2.4256 | 2.2399 | 13.7175 | 13.3009 | 12.7654 | 12.1228 | 11.3255 | 10.3207 | 9.1142 | 7.6116 | 3.5433 | -9.4452 | -18.3354 | -21.8001 | 0.47698 | 0.29489 | 11.7604 | 11.2932 | 10.6556 | 9.8748 | 8.9052 | 7.6859 | 6.224 | 4.3991 | -0.54469 | -16.6732 | -27.7151 | -31.5553
|  | MILFORD-ON-SEA | FS |  |  | 0.61176 | 0.066644 | 11.6662 | 10.4689 | 9.1432 | 7.3347 | 5.452 | 2.6759 | -0.89167 | -4.3499 | -10.7264 | -26.1662 | -33.0257 | -35.4673 | 2.4438 | 2.2859 | 13.8125 | 13.4766 | 13.0555 | 12.5734 | 11.9966 | 11.3022 | 10.49 | 9.5288 | 6.877 | -3.3401 | -15.477 | -23.899 | 0.49635 | 0.34664 | 11.8728 | 11.4911 | 11.0158 | 10.4333 | 9.7363 | 8.8937 | 7.896 | 6.7214 | 3.4973 | -8.935 | -23.429 | -32.2399
MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood | MINIMUM HEADROOM | SU 14691 05633 | YES | 3.9082 | 18.8439 | 17.89 | 16.5688 | 14.8674 | 12.8257 | 9.3791 | 5.0606 | 0.33237 | -4.7737 | -15.7669 | -33.0457 | -54.6658 | -61.7493 | 9.9699 | 9.7362 | 23.1494 | 22.203 | 20.9529 | 19.4286 | 17.0243 | 13.8251 | 10.3419 | 6.6041 | -1.5237 | -16.3884 | -33.0198 | -38.7956 | 5.5485 | 4.7032 | 17.7669 | 16.5562 | 14.9355 | 13.0863 | 9.9222 | 5.7559 | 1.1921 | -3.7444 | -14.4066 | -31.1671 | -52.0071 | -58.8086
|  | Mill Lane, Ringwood | CT |  |  | 4.1614 | 19.3487 | 18.4956 | 17.2692 | 15.8314 | 13.5882 | 10.9374 | 7.0161 | 2.1892 | -2.4429 | -11.328 | -32.914 | -54.6658 | -61.7493 | 9.9699 | 9.7362 | 23.1661 | 22.203 | 21.1247 | 19.4286 | 17.4259 | 14.402 | 10.7941 | 7.3776 | 0.82647 | -16.3884 | -33.0198 | -38.4125 | 5.6363 | 5.1689 | 18.3309 | 17.1697 | 15.8763 | 13.8826 | 11.3331 | 7.5389 | 2.8788 | -1.5881 | -10.137 | -31.013 | -52.0071 | -58.8086
|  | Mill Lane, Ringwood | LW |  |  | 3.9082 | 18.8439 | 17.89 | 16.5688 | 14.8674 | 12.8257 | 9.3791 | 5.0606 | 0.33237 | -4.7737 | -15.7669 | -33.0457 | -37.3166 | -34.3184 | 10.0125 | 9.7543 | 23.1494 | 22.21 | 20.9529 | 19.5308 | 17.0243 | 13.8251 | 10.3419 | 6.6041 | -1.5237 | -14.1529 | -16.9277 | -14.422 | 5.5485 | 4.7032 | 17.7669 | 16.5562 | 14.9355 | 13.0863 | 9.9222 | 5.7559 | 1.1921 | -3.7444 | -14.4066 | -31.1671 | -35.2215 | -32.2076
|  | Mill Lane, Ringwood | ST |  |  | 4.6257 | 20.3707 | 20.0582 | 19.5114 | 18.8616 | 17.9163 | 16.4675 | 14.6044 | 12.5363 | 10.192 | 3.9417 | -15.9381 | -29.4312 | -33.9836 | 10.1629 | 10.0907 | 23.8926 | 23.6366 | 23.2639 | 22.4032 | 21.1948 | 19.6599 | 17.942 | 16.0395 | 10.9409 | -5.6938 | -17.2402 | -22.262 | 5.9235 | 5.85 | 19.6468 | 19.2002 | 18.6222 | 17.7364 | 16.4549 | 14.8172 | 12.8044 | 10.5192 | 4.3875 | -15.6381 | -28.9685 | -33.3322
|  | Mill Lane, Ringwood | FS |  |  | 4.1614 | 19.3487 | 18.4956 | 17.2692 | 15.8314 | 13.5882 | 10.9374 | 7.0161 | 2.1892 | -2.4429 | -11.328 | -32.914 | -54.6658 | -61.7493 | 10.1472 | 10.0462 | 23.8284 | 23.6326 | 22.9424 | 22.0607 | 20.8337 | 19.2848 | 17.5438 | 15.5449 | 10.4085 | -7.2768 | -26.1512 | -38.7956 | 5.9072 | 5.8097 | 19.4732 | 18.9874 | 18.3121 | 17.3801 | 16.0824 | 14.3037 | 12.2253 | 9.8317 | 3.6957 | -17.2726 | -38.6287 | -49.936
COWLEY GSP | DRAYTON BSP | MILTON | MINIMUM HEADROOM | SU 49992 92060 | NO | 8.4639 | 2.1612 | -4.2169 | -7.0378 | -10.3153 | -15.26 | -20.8667 | -26.0666 | -30.7826 | -34.5001 | -41.0483 | -52.0538 | -56.7794 | -59.8754 | 13.4945 | 6.6845 | -0.09589 | -2.0864 | -4.2701 | -8.2352 | -12.5568 | -16.2507 | -19.446 | -22.0067 | -26.7512 | -37.217 | -45.0488 | -47.4356 | 8.2514 | 1.1722 | -5.9261 | -8.4254 | -11.2823 | -16.0604 | -21.4405 | -26.3025 | -30.6975 | -34.2369 | -40.4811 | -51.4338 | -59.2193 | -62.2072
|  | MILTON | CT |  |  | 8.9461 | 2.7678 | -3.2896 | -5.7673 | -8.4445 | -13.0898 | -17.6637 | -22.3349 | -27.24 | -31.2563 | -37.4926 | -49.0127 | -54.4437 | -57.0701 | 13.7916 | 6.8886 | 0.26121 | -1.4988 | -3.3022 | -7.0619 | -10.6757 | -14.0491 | -17.494 | -20.3595 | -24.7531 | -32.9718 | -36.9663 | -39.5983 | 8.7536 | 1.7693 | -5.0266 | -7.1848 | -9.485 | -13.9386 | -18.366 | -22.7674 | -27.3873 | -31.1733 | -37.0568 | -48.2274 | -53.3342 | -55.7156
|  | MILTON | LW |  |  | 8.4639 | 2.1612 | -4.2169 | -7.0378 | -10.3153 | -15.26 | -20.8667 | -26.0666 | -30.7826 | -34.5001 | -41.0483 | -52.0538 | -56.7794 | -59.8754 | 13.4945 | 6.6845 | -0.09589 | -2.0864 | -4.2701 | -8.2352 | -12.5568 | -16.2507 | -19.446 | -22.0067 | -26.7512 | -37.217 | -45.0488 | -47.4356 | 8.2514 | 1.1722 | -5.9261 | -8.4254 | -11.2823 | -16.0604 | -21.4405 | -26.3025 | -30.6975 | -34.2369 | -40.4811 | -51.4338 | -59.2193 | -62.2072
|  | MILTON | ST |  |  | 9.2404 | 3.3327 | -2.4344 | -4.4369 | -6.503 | -10.0446 | -13.3945 | -16.4892 | -19.4354 | -21.9662 | -26.5147 | -36.9675 | -43.7527 | -47.3138 | 13.9346 | 7.1724 | 0.69518 | -0.85999 | -2.3953 | -5.5477 | -8.4767 | -11.0827 | -13.5176 | -15.5222 | -19.0227 | -27.2479 | -32.9249 | -35.9552 | 9.0089 | 2.2505 | -4.3063 | -6.0463 | -7.7846 | -11.1968 | -14.4445 | -17.3721 | -20.1256 | -22.5518 | -26.917 | -37.2562 | -43.8745 | -47.0783
|  | MILTON | FS |  |  | 8.9461 | 2.7678 | -3.2896 | -5.7673 | -8.4445 | -13.0898 | -17.6637 | -22.3349 | -27.24 | -31.2563 | -37.4926 | -49.0127 | -54.4437 | -57.0701 | 14.303 | 8.1631 | 1.9968 | 0.79128 | -0.49313 | -3.1218 | -5.8685 | -8.5158 | -10.8545 | -12.8228 | -16.6039 | -24.4393 | -31.7536 | -37.4273 | 9.3992 | 3.2363 | -2.9783 | -4.3285 | -5.7841 | -8.6199 | -11.6066 | -14.5005 | -17.1572 | -19.4279 | -23.7908 | -33.4925 | -41.929 | -47.5597
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON | MINIMUM HEADROOM | ST 96164 14520 | YES | 1.8449 | 1.2674 | 0.55417 | -0.25686 | -1.1865 | -2.651 | -4.5746 | -8.1624 | -12.7146 | -18.3055 | -31.9237 | -55.4944 | -61.6684 | -65.8538 | 2.4613 | 2.0094 | 1.4466 | 0.80322 | 0.068748 | -1.1044 | -2.8119 | -5.6252 | -9.1942 | -13.5791 | -24.2645 | -42.758 | -47.5475 | -50.8185 | 2.0174 | 1.4477 | 0.74454 | -0.058188 | -0.97763 | -2.4363 | -4.5051 | -7.9583 | -12.3389 | -17.7165 | -30.81 | -53.4822 | -59.4125 | -63.4314
|  | MINCHINGTON | CT |  |  | 1.8449 | 1.2674 | 0.55417 | -0.25686 | -1.1865 | -2.651 | -4.5746 | -8.1624 | -12.7146 | -18.3055 | -31.9237 | -55.4944 | -61.6684 | -65.8538 | 2.4613 | 2.0094 | 1.4466 | 0.80322 | 0.068748 | -1.1044 | -2.8119 | -5.6252 | -9.1942 | -13.5791 | -24.2645 | -42.758 | -47.5475 | -50.8185 | 2.0174 | 1.4477 | 0.74454 | -0.058188 | -0.97763 | -2.4363 | -4.5051 | -7.9583 | -12.3389 | -17.7165 | -30.81 | -53.4822 | -59.4125 | -63.4314
|  | MINCHINGTON | LW |  |  | 1.911 | 1.283 | 0.66129 | -0.01688 | -0.96857 | -1.9824 | -3.8532 | -6.2396 | -8.9085 | -11.9433 | -18.6287 | -29.3389 | -31.2787 | -28.1218 | 2.5376 | 2.0613 | 1.5797 | 1.041 | 0.27614 | -0.54072 | -2.0652 | -4.0153 | -6.1945 | -8.6738 | -14.1363 | -22.7143 | -24.2202 | -21.628 | 2.0881 | 1.4707 | 0.85949 | 0.18213 | -0.77992 | -1.8043 | -3.7056 | -6.1332 | -8.8453 | -11.9284 | -18.7146 | -29.395 | -31.2998 | -28.1066
|  | MINCHINGTON | ST |  |  | 2.2397 | 2.0506 | 1.7977 | 1.4548 | 1.0018 | 0.4052 | -0.37051 | -1.3556 | -2.5064 | -3.9444 | -7.9187 | -20.7853 | -28.9666 | -30.5961 | 2.7637 | 2.6213 | 2.4264 | 2.1626 | 1.8019 | 1.3221 | 0.69297 | -0.11512 | -1.052 | -2.2319 | -5.506 | -16.0269 | -22.6136 | -23.9668 | 2.4059 | 2.2204 | 1.9719 | 1.6346 | 1.1879 | 0.5859 | -0.20195 | -1.2073 | -2.3801 | -3.8499 | -7.9197 | -20.9529 | -29.0907 | -30.7013
|  | MINCHINGTON | FS |  |  | 1.8449 | 1.2674 | 0.55417 | -0.25686 | -1.1865 | -2.651 | -4.5746 | -8.1624 | -12.7146 | -18.3055 | -31.9237 | -55.4944 | -61.6684 | -65.8538 | 2.7536 | 2.6095 | 2.4228 | 2.1796 | 1.8591 | 1.4472 | 0.91536 | 0.24033 | -0.51266 | -1.4023 | -3.8338 | -12.8589 | -22.6715 | -27.8931 | 2.3987 | 2.2166 | 1.9831 | 1.6716 | 1.2743 | 0.75637 | 0.089395 | -0.75073 | -1.6959 | -2.8086 | -5.8385 | -17.0718 | -29.2333 | -35.6768
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE | MINIMUM HEADROOM | SU 01647 91932 | YES | 8.887 | 8.0195 | 7.0714 | 5.9848 | 4.4602 | 2.6042 | 0.42324 | -2.6506 | -6.4076 | -10.1695 | -17.3025 | -35.2481 | -55.0203 | -61.4791 | 9.4032 | 8.8398 | 8.192 | 7.3055 | 6.2067 | 4.7691 | 3.1792 | 0.82167 | -2.0603 | -4.9691 | -10.2504 | -26.8524 | -42.6015 | -48.0089 | 7.6285 | 6.8271 | 5.957 | 4.9568 | 3.5565 | 1.7295 | -0.31349 | -3.2848 | -6.9365 | -10.6168 | -17.687 | -35.8981 | -55.0847 | -61.5109
|  | MINETY VILLAGE | CT |  |  | 8.887 | 8.1761 | 7.2588 | 6.0377 | 4.5341 | 2.6042 | 0.45371 | -2.6506 | -6.4076 | -10.1695 | -17.152 | -35.2481 | -55.0203 | -61.4791 | 9.4032 | 8.8794 | 8.2041 | 7.3055 | 6.2067 | 4.7691 | 3.1792 | 0.82167 | -2.0603 | -4.9691 | -10.2504 | -26.8524 | -42.6015 | -48.0089 | 7.6285 | 6.9532 | 6.0958 | 4.9568 | 3.5565 | 1.7295 | -0.31349 | -3.2848 | -6.9365 | -10.6168 | -17.3795 | -35.8981 | -55.0847 | -61.5109
|  | MINETY VILLAGE | LW |  |  | 8.8887 | 8.0195 | 7.0714 | 5.9848 | 4.4602 | 2.8883 | 0.42324 | -2.6107 | -6.0173 | -9.6582 | -17.3025 | -29.0014 | -31.9099 | -29.6584 | 9.4544 | 8.8398 | 8.192 | 7.4337 | 6.3494 | 5.2554 | 3.4486 | 1.1759 | -1.4196 | -4.2581 | -10.1696 | -19.3614 | -22.0671 | -20.8966 | 7.6443 | 6.8271 | 5.957 | 4.9635 | 3.5579 | 2.1122 | -0.20979 | -3.0945 | -6.4461 | -10.0761 | -17.687 | -29.2739 | -32.4025 | -30.5339
|  | MINETY VILLAGE | ST |  |  | 9.2823 | 8.9502 | 8.4593 | 7.5566 | 6.4313 | 5.2903 | 3.9094 | 2.2806 | 0.24243 | -2.0983 | -7.7411 | -23.7149 | -33.9093 | -36.9453 | 9.6795 | 9.4844 | 9.1618 | 8.4631 | 7.6067 | 6.7614 | 5.7144 | 4.4747 | 2.8548 | 0.97996 | -3.5778 | -16.6444 | -25.3737 | -28.4789 | 8.017 | 7.7166 | 7.2815 | 6.4275 | 5.3801 | 4.3132 | 3.0013 | 1.4668 | -0.48398 | -2.8085 | -8.5293 | -24.5867 | -35.006 | -38.3159
|  | MINETY VILLAGE | FS |  |  | 8.887 | 8.1761 | 7.2588 | 6.0377 | 4.5341 | 2.6042 | 0.45371 | -2.6506 | -6.4076 | -10.1695 | -17.152 | -35.2481 | -55.0203 | -61.4791 | 9.7596 | 9.57 | 9.2718 | 8.8302 | 8.2673 | 7.629 | 6.8821 | 5.9972 | 4.964 | 3.7851 | 0.78964 | -9.2557 | -20.0978 | -26.367 | 8.1371 | 7.8523 | 7.4731 | 6.9121 | 6.209 | 5.4073 | 4.4657 | 3.3615 | 2.0851 | 0.61243 | -3.1719 | -15.7626 | -29.1877 | -36.783
BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER | MINIMUM HEADROOM | SU 62236 64103 | YES | 4.8249 | 4.4629 | 4.1602 | 3.6929 | 3.1802 | 1.8837 | -0.32529 | -3.2677 | -7.0861 | -11.7882 | -23.0126 | -42.5157 | -48.2282 | -52.2971 | 6.8976 | 6.6999 | 6.5315 | 6.2152 | 5.845 | 5.1886 | 3.4505 | 1.1528 | -1.7969 | -5.4753 | -14.2372 | -29.3896 | -33.7613 | -37.0693 | 4.9755 | 4.6546 | 4.3799 | 3.9242 | 3.375 | 1.8482 | -0.29114 | -3.125 | -6.7933 | -11.331 | -22.1455 | -40.9682 | -46.5243 | -50.547
|  | MORTIMER | CT |  |  | 5.0311 | 4.8252 | 4.6222 | 4.2071 | 3.4676 | 1.8837 | -0.32529 | -3.2677 | -7.0861 | -11.7882 | -23.0126 | -42.5157 | -48.2282 | -52.2971 | 6.9464 | 6.8164 | 6.6717 | 6.3792 | 5.9741 | 5.1886 | 3.4505 | 1.1528 | -1.7969 | -5.4753 | -14.2372 | -29.3896 | -33.7613 | -37.0693 | 5.1545 | 4.972 | 4.783 | 4.3916 | 3.375 | 1.8482 | -0.29114 | -3.125 | -6.7933 | -11.331 | -22.1455 | -40.9682 | -46.5243 | -50.547
|  | MORTIMER | LW |  |  | 4.8249 | 4.4629 | 4.1602 | 3.6929 | 3.1802 | 2.6727 | 2.0954 | 1.5061 | 0.866 | 0.1938 | -1.2163 | -4.2874 | -6.1549 | -7.1304 | 6.8976 | 6.6999 | 6.5315 | 6.2152 | 5.845 | 5.4706 | 5.0436 | 4.6166 | 4.1957 | 3.7457 | 2.7807 | 0.65757 | -0.79134 | -1.8433 | 4.9755 | 4.6546 | 4.3799 | 3.9242 | 3.4056 | 2.8897 | 2.3051 | 1.7144 | 1.0919 | 0.43607 | -0.93232 | -3.9245 | -5.8393 | -7.0085
|  | MORTIMER | ST |  |  | 5.1602 | 5.0491 | 4.9715 | 4.6348 | 4.3194 | 4.0512 | 3.6901 | 3.3895 | 2.9837 | 2.5609 | 1.6073 | -1.4624 | -4.1376 | -6.1283 | 7.0105 | 6.936 | 6.8706 | 6.5272 | 6.2042 | 5.9407 | 5.5691 | 5.2791 | 4.8831 | 4.471 | 3.5248 | 0.65402 | -2.0211 | -4.5057 | 5.2737 | 5.1805 | 5.1097 | 4.7402 | 4.3833 | 4.0995 | 3.7093 | 3.4011 | 2.9779 | 2.5257 | 1.4864 | -1.6907 | -4.4384 | -6.4789
|  | MORTIMER | FS |  |  | 5.0311 | 4.8252 | 4.6222 | 4.2071 | 3.4676 | 1.8837 | -0.32529 | -3.2677 | -7.0861 | -11.7882 | -23.0126 | -42.5157 | -48.2282 | -52.2971 | 7.0836 | 6.9755 | 6.8867 | 6.7367 | 6.5634 | 6.3853 | 6.188 | 5.9892 | 5.75 | 5.4861 | 4.8971 | 3.1825 | 1.0618 | -1.7192 | 5.3772 | 5.2593 | 5.1746 | 4.9945 | 4.7919 | 4.5908 | 4.3766 | 4.1641 | 3.8917 | 3.5954 | 2.9548 | 1.082 | -0.80904 | -2.4942
MANNINGTON GSP | SALISBURY | NETHERHAMPTON | MINIMUM HEADROOM | SU 12478 29102 | YES | 5.952 | 5.588 | 5.24 | 4.8018 | 4.1995 | 3.594 | 2.8324 | 1.7798 | 0.8122 | -0.17826 | -2.5353 | -14.4258 | -20.5741 | -20.5073 | 6.532 | 6.3068 | 6.0926 | 5.839 | 5.4384 | 5.0352 | 4.5636 | 3.8019 | 3.0884 | 2.3616 | 0.19168 | -8.9712 | -13.6195 | -13.5286 | 5.4785 | 5.155 | 4.844 | 4.4539 | 3.9103 | 3.3629 | 2.6204 | 1.596 | 0.66898 | -0.28114 | -2.3421 | -12.7198 | -18.6041 | -18.5457
|  | NETHERHAMPTON | CT |  |  | 6.0508 | 5.777 | 5.4984 | 5.1321 | 4.5684 | 4.0296 | 3.413 | 2.4095 | 1.3758 | 0.39604 | -2.2219 | -14.4258 | -20.5741 | -20.5073 | 6.534 | 6.3287 | 6.1083 | 5.847 | 5.4384 | 5.0352 | 4.5752 | 3.8212 | 3.0884 | 2.3616 | 0.32664 | -8.9712 | -13.6195 | -13.5286 | 5.5476 | 5.2968 | 5.0316 | 4.6899 | 4.183 | 3.6566 | 3.058 | 2.1158 | 1.1459 | 0.21217 | -1.663 | -12.7198 | -18.6041 | -18.5457
|  | NETHERHAMPTON | LW |  |  | 5.952 | 5.588 | 5.24 | 4.8018 | 4.1995 | 3.594 | 2.8324 | 1.7798 | 0.8122 | -0.17826 | -2.5353 | -8.076 | -9.8979 | -11.0541 | 6.532 | 6.3068 | 6.0926 | 5.839 | 5.4553 | 5.0842 | 4.5636 | 3.8019 | 3.1395 | 2.4405 | 0.19168 | -3.9385 | -5.2958 | -6.2646 | 5.4785 | 5.155 | 4.844 | 4.4539 | 3.9103 | 3.3629 | 2.6204 | 1.596 | 0.66898 | -0.28114 | -2.3421 | -6.5922 | -8.3548 | -9.5146
|  | NETHERHAMPTON | ST |  |  | 6.1397 | 5.9458 | 5.7577 | 5.5594 | 5.2029 | 4.9626 | 4.676 | 4.2039 | 3.839 | 3.4539 | 2.4497 | -0.89024 | -3.439 | -4.8328 | 6.6077 | 6.4734 | 6.3344 | 6.1587 | 5.8571 | 5.6384 | 5.3686 | 4.9385 | 4.6141 | 4.2604 | 3.3391 | 0.19234 | -2.5585 | -4.9601 | 5.6454 | 5.4868 | 5.326 | 5.1361 | 4.8124 | 4.5716 | 4.2747 | 3.805 | 3.4542 | 3.0804 | 2.095 | -1.2376 | -3.7766 | -5.0074
|  | NETHERHAMPTON | FS |  |  | 6.0508 | 5.777 | 5.4984 | 5.1321 | 4.5684 | 4.0296 | 3.413 | 2.4095 | 1.3758 | 0.39604 | -2.2219 | -14.4258 | -20.5741 | -20.5073 | 6.5852 | 6.4441 | 6.2944 | 6.1208 | 5.8777 | 5.6259 | 5.3301 | 4.9473 | 4.5725 | 4.1616 | 3.1003 | -0.94197 | -6.221 | -11.7074 | 5.6235 | 5.4685 | 5.3106 | 5.13 | 4.8773 | 4.6146 | 4.3059 | 3.9065 | 3.5143 | 3.0938 | 2.0075 | -2.1145 | -6.8506 | -9.7627
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV | MINIMUM HEADROOM | SU 47615 12025 | YES | 28.35 | 28.35 | 28.35 | 28.3038 | 28.2654 | 28.2053 | 28.1399 | 28.0852 | 28.0198 | 27.952 | 27.8334 | 27.5032 | 26.7958 | 25.8143 | 26.7 | 26.7 | 26.7 | 26.6423 | 26.5943 | 26.5192 | 26.4374 | 26.369 | 26.2873 | 26.2025 | 26.0543 | 25.6415 | 24.7573 | 23.5304 | 26.7 | 26.7 | 26.7 | 26.6423 | 26.5943 | 26.5192 | 26.4374 | 26.369 | 26.2873 | 26.2025 | 26.0543 | 25.6415 | 24.7573 | 23.5304
|  | NETLEY COMMON 11kV | CT |  |  | 28.35 | 28.35 | 28.35 | 28.3438 | 28.3327 | 28.3196 | 28.2959 | 28.2816 | 28.2594 | 28.2102 | 28.121 | 27.8727 | 27.4508 | 26.9452 | 26.7 | 26.7 | 26.7 | 26.6922 | 26.6784 | 26.662 | 26.6324 | 26.6144 | 26.5868 | 26.5253 | 26.4137 | 26.1034 | 25.576 | 24.944 | 26.7 | 26.7 | 26.7 | 26.6922 | 26.6784 | 26.662 | 26.6324 | 26.6144 | 26.5868 | 26.5253 | 26.4137 | 26.1034 | 25.576 | 24.944
|  | NETLEY COMMON 11kV | LW |  |  | 28.35 | 28.35 | 28.35 | 28.31 | 28.2654 | 28.2053 | 28.1399 | 28.0852 | 28.0198 | 27.952 | 27.8334 | 27.5032 | 26.7958 | 25.8143 | 26.7 | 26.7 | 26.7 | 26.65 | 26.5943 | 26.5192 | 26.4374 | 26.369 | 26.2873 | 26.2025 | 26.0543 | 25.6415 | 24.7573 | 23.5304 | 26.7 | 26.7 | 26.7 | 26.65 | 26.5943 | 26.5192 | 26.4374 | 26.369 | 26.2873 | 26.2025 | 26.0543 | 25.6415 | 24.7573 | 23.5304
|  | NETLEY COMMON 11kV | ST |  |  | 28.35 | 28.35 | 28.35 | 28.3038 | 28.2726 | 28.2445 | 28.2017 | 28.182 | 28.135 | 28.0949 | 28.0069 | 27.753 | 27.0512 | 26.2581 | 26.7 | 26.7 | 26.7 | 26.6423 | 26.6032 | 26.5681 | 26.5146 | 26.4899 | 26.4312 | 26.3812 | 26.2711 | 25.9538 | 25.0765 | 24.0851 | 26.7 | 26.7 | 26.7 | 26.6423 | 26.6032 | 26.5681 | 26.5146 | 26.4899 | 26.4312 | 26.3812 | 26.2711 | 25.9538 | 25.0765 | 24.0851
|  | NETLEY COMMON 11kV | FS |  |  | 28.35 | 28.35 | 28.35 | 28.3438 | 28.3327 | 28.3196 | 28.2959 | 28.2816 | 28.2594 | 28.2102 | 28.121 | 27.8727 | 27.4508 | 26.9452 | 26.7 | 26.7 | 26.7 | 26.6874 | 26.6748 | 26.6596 | 26.6444 | 26.6318 | 26.6091 | 26.5872 | 26.5434 | 26.5168 | 26.4616 | 26.163 | 26.7 | 26.7 | 26.7 | 26.6874 | 26.6748 | 26.6596 | 26.6444 | 26.6318 | 26.6091 | 26.5872 | 26.5434 | 26.5168 | 26.4616 | 26.163
MANNINGTON GSP | ARNEWOOD | NEW MILTON | MINIMUM HEADROOM | SZ 23049 94942 | YES | 4.9954 | 4.1533 | 3.3063 | 2.0307 | 0.45962 | -1.2447 | -3.8953 | -7.0669 | -10.7568 | -14.7886 | -24.5937 | -44.2312 | -50.2887 | -53.8042 | 10.0708 | 9.5563 | 9.0374 | 8.3135 | 7.3781 | 6.3472 | 4.5618 | 2.3278 | -0.24386 | -3.11 | -9.375 | -23.6457 | -27.9185 | -32.2506 | 7.3813 | 6.6218 | 5.8549 | 4.681 | 3.2412 | 1.6765 | -0.72861 | -3.6276 | -7.1708 | -11.0632 | -21.276 | -40.0026 | -45.778 | -49.2227
|  | NEW MILTON | CT |  |  | 5.3735 | 4.8155 | 4.1495 | 3.0646 | 1.8917 | 0.19759 | -1.6945 | -4.3573 | -7.9821 | -11.4871 | -18.065 | -34.3832 | -42.4234 | -45.7269 | 10.1712 | 9.7607 | 9.2689 | 8.5849 | 7.8358 | 6.6172 | 5.2394 | 3.2431 | 0.68797 | -1.7988 | -6.4718 | -18.0392 | -24.3209 | -28.9463 | 7.7497 | 7.2607 | 6.6781 | 5.7046 | 4.6528 | 3.1507 | 1.3719 | -1.2104 | -4.6873 | -8.0556 | -14.3686 | -29.916 | -37.4041 | -40.4412
|  | NEW MILTON | LW |  |  | 4.9954 | 4.1533 | 3.3063 | 2.0307 | 0.45962 | -1.2447 | -3.8953 | -7.0669 | -10.7568 | -14.7886 | -24.5937 | -44.2312 | -50.2887 | -53.8042 | 10.0708 | 9.5563 | 9.0374 | 8.3135 | 7.3781 | 6.3472 | 4.5618 | 2.3278 | -0.24386 | -3.11 | -9.375 | -23.6457 | -27.9185 | -30.7152 | 7.3813 | 6.6218 | 5.8549 | 4.681 | 3.2412 | 1.6765 | -0.72861 | -3.6276 | -7.1708 | -11.0632 | -21.276 | -40.0026 | -45.778 | -49.2227
|  | NEW MILTON | ST |  |  | 5.8039 | 5.6344 | 5.4009 | 5.0612 | 4.6033 | 3.9669 | 3.093 | 2.0312 | 0.77659 | -0.75674 | -4.9228 | -19.3488 | -30.1914 | -35.9412 | 10.4449 | 10.2931 | 10.091 | 9.8125 | 9.4485 | 8.9591 | 8.289 | 7.4052 | 6.3299 | 5.0152 | 1.4546 | -10.4401 | -19.7521 | -25.6781 | 8.1355 | 7.9902 | 7.7897 | 7.4941 | 7.0966 | 6.5486 | 5.7919 | 4.8776 | 3.6409 | 2.1213 | -2.0218 | -16.2881 | -26.9835 | -32.033
|  | NEW MILTON | FS |  |  | 5.3735 | 4.8155 | 4.1495 | 3.0646 | 1.8917 | 0.19759 | -1.6945 | -4.3573 | -7.9821 | -11.4871 | -18.065 | -34.3832 | -42.4234 | -45.7269 | 10.4501 | 10.3081 | 10.1249 | 9.8744 | 9.5596 | 9.1565 | 8.6376 | 8.018 | 7.1793 | 6.1927 | 3.5524 | -6.6753 | -19.8043 | -32.2506 | 8.1443 | 8.0188 | 7.8511 | 7.5754 | 7.2267 | 6.7764 | 6.1974 | 5.5051 | 4.6078 | 3.539 | 0.56101 | -10.975 | -24.3138 | -33.215
FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT | MINIMUM HEADROOM | SZ 50076 89544 | YES | 9.92 | 9.3255 | 8.7035 | 7.6972 | 6.4612 | 5.0375 | 3.2311 | 1.2353 | -0.97318 | -3.3355 | -8.717 | -19.4111 | -24.9411 | -28.1159 | 17.9147 | 17.7283 | 17.5451 | 17.2737 | 16.9191 | 16.3854 | 15.1849 | 13.8078 | 11.978 | 10.0069 | 6.3049 | -3.068 | -9.6685 | -23.8876 | 13.0944 | 12.5196 | 11.9142 | 10.957 | 9.7789 | 8.4289 | 6.6456 | 4.6405 | 2.4184 | 0.1364 | -4.7669 | -14.8311 | -19.9216 | -23.6843
|  | NEWPORT | CT |  |  | 10.322 | 9.974 | 9.5425 | 8.7044 | 7.7569 | 6.3756 | 5.0467 | 3.34 | 1.012 | -1.4201 | -6.3905 | -18.5523 | -24.9411 | -28.1159 | 17.9273 | 17.7784 | 17.5965 | 17.3368 | 17.0639 | 16.3854 | 15.3692 | 13.9326 | 11.978 | 10.0069 | 6.3049 | -3.068 | -9.6685 | -16.7315 | 13.4432 | 13.0833 | 12.6334 | 11.8136 | 10.8995 | 9.5428 | 8.2158 | 6.4612 | 4.1157 | 1.8401 | -2.5531 | -14.0166 | -19.9216 | -22.8396
|  | NEWPORT | LW |  |  | 9.92 | 9.3255 | 8.7035 | 7.6972 | 6.4612 | 5.0375 | 3.2311 | 1.2353 | -0.97318 | -3.3355 | -8.717 | -19.4111 | -24.3823 | -26.3025 | 17.9147 | 17.7283 | 17.5451 | 17.2737 | 16.9191 | 16.3933 | 15.1849 | 13.8078 | 12.1823 | 10.3107 | 6.3424 | -0.79366 | -5.5868 | -10.0481 | 13.0944 | 12.5196 | 11.9142 | 10.957 | 9.7789 | 8.4289 | 6.6456 | 4.6405 | 2.4184 | 0.1364 | -4.7669 | -14.8311 | -19.4863 | -23.6843
|  | NEWPORT | ST |  |  | 10.7112 | 10.6488 | 10.5091 | 10.2043 | 9.8243 | 9.2072 | 8.6401 | 7.9952 | 7.2619 | 6.4312 | 4.1024 | -6.635 | -14.6227 | -19.2166 | 18.0381 | 17.9844 | 17.9009 | 17.6779 | 17.4637 | 17.0376 | 16.7152 | 16.3722 | 15.9292 | 14.9901 | 12.233 | 2.47 | -6.2697 | -14.1908 | 13.8029 | 13.7421 | 13.6045 | 13.2811 | 12.8965 | 12.2857 | 11.6931 | 11.0132 | 10.2225 | 9.3056 | 6.9285 | -3.2787 | -11.0351 | -15.3175
|  | NEWPORT | FS |  |  | 10.322 | 9.974 | 9.5425 | 8.7044 | 7.7569 | 6.3756 | 5.0467 | 3.34 | 1.012 | -1.4201 | -6.3905 | -18.5523 | -24.9411 | -28.1159 | 18.0476 | 17.9995 | 17.9286 | 17.8026 | 17.6448 | 17.3964 | 17.1578 | 16.8945 | 16.2645 | 15.4774 | 13.3908 | 4.5986 | -8.0669 | -23.8876 | 13.7907 | 13.7269 | 13.6152 | 13.3388 | 12.9859 | 12.5177 | 12.0145 | 11.4425 | 10.7805 | 10.082 | 8.332 | 1.033 | -8.4306 | -15.1274
BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY | MINIMUM HEADROOM | SU 93221 52894 | YES | 0.13044 | -0.0011456 | -0.16891 | -0.40629 | -0.70938 | -1.1005 | -1.615 | -2.2841 | -3.1192 | -4.1673 | -7.0348 | -16.839 | -21.6041 | -21.1231 | 1.1907 | 1.1322 | 1.059 | 0.96324 | 0.85655 | 0.58949 | 0.21819 | -0.27031 | -0.88522 | -1.668 | -3.8544 | -11.4874 | -15.1943 | -14.8092 | 0.76991 | 0.6753 | 0.55932 | 0.39236 | 0.1763 | -0.18779 | -0.66953 | -1.299 | -2.0869 | -3.0795 | -5.8117 | -15.2121 | -19.7807 | -19.3169
|  | NORMANDY | CT |  |  | 0.22781 | 0.16263 | 0.055635 | -0.086026 | -0.2484 | -0.43118 | -0.63421 | -0.87188 | -1.1704 | -1.4821 | -2.0342 | -2.9052 | -3.9393 | -4.5269 | 1.2071 | 1.1645 | 1.105 | 1.0341 | 0.9553 | 0.86686 | 0.77 | 0.65796 | 0.52488 | 0.38384 | 0.12561 | -0.41015 | -1.252 | -1.6892 | 0.81528 | 0.75891 | 0.67417 | 0.56016 | 0.42866 | 0.2801 | 0.11439 | -0.080028 | -0.32575 | -0.58275 | -1.0428 | -1.8022 | -2.8038 | -3.3625
|  | NORMANDY | LW |  |  | 0.13044 | -0.0011456 | -0.16891 | -0.40629 | -0.70938 | -1.1005 | -1.615 | -2.2841 | -3.1192 | -4.1673 | -7.0348 | -16.839 | -21.6041 | -21.1231 | 1.1907 | 1.1322 | 1.059 | 0.96324 | 0.85655 | 0.58949 | 0.21819 | -0.27031 | -0.88522 | -1.668 | -3.8544 | -11.4874 | -15.1943 | -14.8092 | 0.76991 | 0.6753 | 0.55932 | 0.39236 | 0.1763 | -0.18779 | -0.66953 | -1.299 | -2.0869 | -3.0795 | -5.8117 | -15.2121 | -19.7807 | -19.3169
|  | NORMANDY | ST |  |  | 0.24507 | 0.17583 | 0.079656 | -0.020909 | -0.11812 | -0.22401 | -0.33267 | -0.45178 | -0.57554 | -0.70872 | -0.92798 | -1.2196 | -1.4752 | -1.7695 | 1.2131 | 1.1727 | 1.118 | 1.0623 | 1.0068 | 0.94624 | 0.88365 | 0.81481 | 0.74469 | 0.66894 | 0.54006 | 0.35713 | 0.19015 | -0.039624 | 0.82507 | 0.77103 | 0.69535 | 0.61606 | 0.53949 | 0.45562 | 0.36955 | 0.27477 | 0.17627 | 0.070031 | -0.10604 | -0.34138 | -0.54601 | -0.78451
|  | NORMANDY | FS |  |  | 0.22781 | 0.16263 | 0.055635 | -0.086026 | -0.2484 | -0.43118 | -0.63421 | -0.87188 | -1.1704 | -1.4821 | -2.0342 | -2.9052 | -3.9393 | -4.5269 | 1.2135 | 1.1784 | 1.1301 | 1.0812 | 1.0277 | 0.97186 | 0.91379 | 0.85175 | 0.78667 | 0.71802 | 0.60297 | 0.41162 | 0.22018 | -0.044091 | 0.82711 | 0.78567 | 0.72557 | 0.66054 | 0.58841 | 0.51592 | 0.44171 | 0.36121 | 0.27095 | 0.17559 | 0.020981 | -0.21907 | -0.43379 | -0.65417
NURSLING GSP | ROWNHAMS | NORTH BADDESLEY | MINIMUM HEADROOM | SU 38080 20568 | YES | -1.1329 | -1.5832 | -1.8843 | -2.3879 | -2.9534 | -3.538 | -4.2123 | -6.3557 | -9.6939 | -13.7532 | -23.4101 | -41.2681 | -47.2392 | -50.9143 | 2.9785 | 2.7231 | 2.5664 | 2.3113 | 1.8356 | 0.77554 | -0.68687 | -2.6407 | -5.1663 | -8.2538 | -15.6218 | -29.0226 | -33.349 | -36.2051 | 1.2908 | 0.91418 | 0.65827 | 0.22595 | -0.26279 | -0.85274 | -2.5455 | -4.9382 | -8.1539 | -12.0449 | -21.2991 | -38.3813 | -44.1092 | -47.7066
|  | NORTH BADDESLEY | CT |  |  | -0.80543 | -1.1282 | -1.3077 | -1.7041 | -2.2102 | -2.8136 | -3.9944 | -6.3557 | -9.6939 | -13.7532 | -23.4101 | -41.2681 | -47.2392 | -50.9143 | 3.103 | 2.8624 | 2.7288 | 2.501 | 1.8356 | 0.77554 | -0.68687 | -2.6407 | -5.1663 | -8.2538 | -15.6218 | -29.0226 | -33.349 | -36.2051 | 1.5655 | 1.2839 | 1.1375 | 0.81745 | 0.38184 | -0.85274 | -2.5455 | -4.9382 | -8.1539 | -12.0449 | -21.2991 | -38.3813 | -44.1092 | -47.7066
|  | NORTH BADDESLEY | LW |  |  | -1.1329 | -1.5832 | -1.8843 | -2.3879 | -2.9534 | -3.538 | -4.2123 | -4.9253 | -5.8022 | -6.7207 | -8.6553 | -12.9015 | -15.7354 | -17.405 | 2.9785 | 2.7231 | 2.5664 | 2.3113 | 2.0144 | 1.7023 | 1.3268 | 0.9228 | 0.42626 | -0.1099 | -1.26 | -3.7532 | -5.6264 | -7.04 | 1.2908 | 0.91418 | 0.65827 | 0.22595 | -0.26279 | -0.79016 | -1.4057 | -2.0568 | -2.8621 | -3.7101 | -5.5062 | -9.5004 | -12.1877 | -13.8509
|  | NORTH BADDESLEY | ST |  |  | -0.64516 | -0.88683 | -0.97343 | -1.1315 | -1.3271 | -1.5359 | -1.8017 | -2.0438 | -2.3511 | -2.6626 | -3.39 | -5.9807 | -8.7277 | -11.701 | 3.2029 | 3.0116 | 2.937 | 2.775 | 2.594 | 2.4091 | 2.1638 | 1.9444 | 1.6495 | 1.3436 | 0.63588 | -1.6031 | -4.1491 | -7.2006 | 1.7008 | 1.483 | 1.4083 | 1.2413 | 1.0503 | 0.84805 | 0.58418 | 0.34553 | 0.027443 | -0.30047 | -1.0673 | -3.5624 | -6.1249 | -8.7812
|  | NORTH BADDESLEY | FS |  |  | -0.80543 | -1.1282 | -1.3077 | -1.7041 | -2.2102 | -2.8136 | -3.9944 | -6.3557 | -9.6939 | -13.7532 | -23.4101 | -41.2681 | -47.2392 | -50.9143 | 3.1508 | 2.9256 | 2.7584 | 2.5611 | 2.32 | 2.039 | 1.6722 | 1.2141 | 0.64777 | 0.026305 | -1.4019 | -5.1625 | -8.7347 | -12.7084 | 1.6288 | 1.3657 | 1.1786 | 0.93126 | 0.62996 | 0.27594 | -0.19129 | -0.78421 | -1.5212 | -2.2918 | -3.9555 | -8.2438 | -11.6547 | -14.1597
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM | MINIMUM HEADROOM | SU 56427 07430 | YES | 1.8173 | 1.37 | 0.90182 | 0.15953 | -0.68065 | -1.6193 | -2.9133 | -4.3709 | -6.0638 | -7.8486 | -11.754 | -25.6464 | -38.898 | -43.4047 | 4.2516 | 3.9785 | 3.6992 | 3.2847 | 2.7817 | 2.1896 | 1.3058 | 0.29698 | -0.83378 | -2.0273 | -5.0316 | -15.9495 | -25.7712 | -29.149 | 1.6086 | 1.2065 | 0.79437 | 0.1136 | -0.65996 | -1.533 | -2.7248 | -4.0788 | -5.6899 | -7.3925 | -11.0558 | -24.5943 | -37.2301 | -41.5531
|  | NORTH FAREHAM | CT |  |  | 2.115 | 1.8281 | 1.5016 | 0.93352 | 0.31519 | -0.53819 | -1.4595 | -2.6692 | -4.4325 | -6.1408 | -9.5422 | -25.6464 | -38.898 | -43.4047 | 4.3088 | 4.0677 | 3.7897 | 3.411 | 2.9797 | 2.3466 | 1.65 | 0.73165 | -0.45613 | -1.619 | -4.0019 | -15.9495 | -25.7712 | -29.149 | 1.8671 | 1.6215 | 1.3406 | 0.82888 | 0.26562 | -0.50922 | -1.3656 | -2.5134 | -4.1384 | -5.7237 | -8.9338 | -24.5943 | -37.2301 | -41.5531
|  | NORTH FAREHAM | LW |  |  | 1.8173 | 1.37 | 0.90182 | 0.15953 | -0.68065 | -1.6193 | -2.9133 | -4.3709 | -6.0638 | -7.8486 | -11.754 | -19.8021 | -22.9725 | -24.8509 | 4.2516 | 3.9785 | 3.6992 | 3.2847 | 2.7817 | 2.1896 | 1.3058 | 0.29698 | -0.83378 | -2.0273 | -5.0316 | -11.4814 | -13.719 | -15.3041 | 1.6086 | 1.2065 | 0.79437 | 0.1136 | -0.65996 | -1.533 | -2.7248 | -4.0788 | -5.6899 | -7.3925 | -11.0558 | -19.0578 | -22.1084 | -24.0103
|  | NORTH FAREHAM | ST |  |  | 2.2949 | 2.1561 | 1.9897 | 1.7868 | 1.543 | 1.1788 | 0.73944 | 0.21682 | -0.39951 | -1.0789 | -2.8794 | -9.0309 | -14.1629 | -17.5909 | 4.4274 | 4.2891 | 4.1267 | 3.9133 | 3.6595 | 3.2981 | 2.8634 | 2.3772 | 1.8255 | 1.234 | -0.30873 | -5.7969 | -10.9392 | -15.6906 | 2.0351 | 1.9188 | 1.7819 | 1.5953 | 1.3735 | 1.043 | 0.64537 | 0.1578 | -0.39746 | -1.0201 | -2.8125 | -8.8244 | -13.7707 | -16.9497
|  | NORTH FAREHAM | FS |  |  | 2.115 | 1.8281 | 1.5016 | 0.93352 | 0.31519 | -0.53819 | -1.4595 | -2.6692 | -4.4325 | -6.1408 | -9.5422 | -25.6464 | -38.898 | -43.4047 | 4.4204 | 4.2919 | 4.1378 | 3.9496 | 3.7257 | 3.4346 | 3.0821 | 2.6622 | 2.1208 | 1.5202 | -0.0044496 | -5.9402 | -13.6911 | -22.8284 | 2.0331 | 1.9389 | 1.8262 | 1.6561 | 1.4579 | 1.1982 | 0.88529 | 0.48859 | -0.056786 | -0.65302 | -2.2725 | -8.267 | -14.5503 | -18.8113
LALEHAM | EAST BEDFONT A | NORTH FELTHAM | MINIMUM HEADROOM | TQ 10987 74875 | YES | 4.8728 | 3.7616 | 2.6843 | 1.3546 | -0.2161 | -1.9027 | -4.3665 | -6.9975 | -10.0492 | -13.4169 | -21.9282 | -43.3393 | -55.4091 | -59.2907 | 5.5788 | 4.8088 | 4.0635 | 3.2519 | 2.2848 | 0.86776 | -1.1656 | -3.0653 | -5.2491 | -7.9462 | -14.9284 | -31.4733 | -40.8627 | -47.2216 | 4.8659 | 3.8742 | 2.8975 | 1.6907 | 0.26348 | -1.338 | -3.7531 | -6.2986 | -9.0929 | -12.3604 | -20.7421 | -41.2782 | -52.847 | -56.5455
|  | NORTH FELTHAM | CT |  |  | 5.1619 | 4.2889 | 3.2906 | 2.1028 | 0.80472 | -0.90973 | -2.877 | -5.4607 | -8.608 | -11.6571 | -17.217 | -29.1326 | -33.7676 | -35.3735 | 5.7745 | 5.084 | 4.3591 | 3.6502 | 2.8505 | 1.6769 | -0.0061592 | -1.9117 | -4.1861 | -6.4666 | -11.0198 | -21.6627 | -28.157 | -35.175 | 5.1856 | 4.3656 | 3.4671 | 2.4052 | 1.1887 | -0.46013 | -2.4351 | -4.7357 | -7.7812 | -10.7283 | -16.0879 | -27.689 | -32.1342 | -33.6356
|  | NORTH FELTHAM | LW |  |  | 4.8728 | 3.7616 | 2.6843 | 1.3546 | -0.2161 | -1.9027 | -4.3665 | -6.9975 | -10.0492 | -13.4169 | -21.9282 | -43.3393 | -55.4091 | -59.2907 | 5.5788 | 4.8088 | 4.0635 | 3.2519 | 2.2848 | 0.86776 | -1.1656 | -3.0653 | -5.2491 | -7.9462 | -14.9284 | -31.4733 | -40.8627 | -43.8831 | 4.8659 | 3.8742 | 2.8975 | 1.6907 | 0.26348 | -1.338 | -3.7531 | -6.2986 | -9.0929 | -12.3604 | -20.7421 | -41.2782 | -52.847 | -56.5455
|  | NORTH FELTHAM | ST |  |  | 5.3018 | 4.7341 | 4.1454 | 3.487 | 2.6519 | 1.6482 | 0.42976 | -0.53895 | -1.6794 | -3.3277 | -7.6039 | -20.7732 | -29.2162 | -31.4711 | 5.8855 | 5.2991 | 4.6922 | 4.0911 | 3.4117 | 2.6282 | 1.7003 | 1.2066 | 0.31926 | -1.0372 | -4.4417 | -16.8635 | -26.6512 | -33.7243 | 5.3226 | 4.7687 | 4.1942 | 3.5985 | 2.8377 | 1.9284 | 0.82411 | -0.10096 | -1.2918 | -2.7553 | -6.8446 | -20.204 | -28.7716 | -30.8922
|  | NORTH FELTHAM | FS |  |  | 5.1619 | 4.2889 | 3.2906 | 2.1028 | 0.80472 | -0.90973 | -2.877 | -5.4607 | -8.608 | -11.6571 | -17.217 | -29.1326 | -33.7676 | -35.3735 | 6.0795 | 5.6524 | 5.2196 | 4.757 | 4.2241 | 3.6595 | 3.001 | 2.388 | 1.4974 | 0.43098 | -2.3594 | -14.0801 | -29.6115 | -47.2216 | 5.513 | 5.1199 | 4.7222 | 4.2673 | 3.6752 | 3.0181 | 2.2425 | 1.4384 | 0.50997 | -0.60995 | -3.5343 | -14.4731 | -26.5379 | -33.6343
COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY | MINIMUM HEADROOM | SP 48645 04403 | YES | 0.14493 | -0.62383 | -1.3963 | -2.4012 | -3.7387 | -5.1856 | -7.6485 | -10.7564 | -14.3186 | -18.4008 | -27.3824 | -43.1937 | -48.6265 | -52.1408 | 1.6394 | 1.1026 | 0.49738 | -0.24098 | -1.1819 | -2.3935 | -4.1741 | -6.6305 | -9.4257 | -12.621 | -19.6351 | -32.0254 | -36.3111 | -42.8691 | -0.062428 | -0.81227 | -1.5651 | -2.5375 | -3.8404 | -5.2513 | -7.6725 | -10.7282 | -14.2713 | -18.3215 | -27.2131 | -42.1284 | -47.4488 | -53.2377
|  | NORTH HINKSEY | CT |  |  | 0.20009 | -0.43249 | -1.1935 | -2.1547 | -3.2108 | -4.8453 | -6.636 | -9.3716 | -12.7734 | -16.097 | -22.3677 | -37.1199 | -43.098 | -45.4447 | 1.6394 | 1.1218 | 0.49738 | -0.24098 | -1.0755 | -2.3935 | -3.8496 | -6.0886 | -8.7969 | -11.4433 | -16.3499 | -27.8404 | -32.6429 | -35.0935 | -0.011128 | -0.62028 | -1.3574 | -2.3137 | -3.3681 | -5.0166 | -6.8282 | -9.6084 | -13.036 | -16.3729 | -22.5721 | -37.0984 | -42.9546 | -45.2775
|  | NORTH HINKSEY | LW |  |  | 0.14493 | -0.62383 | -1.3963 | -2.4012 | -3.7387 | -5.1856 | -7.6485 | -10.7564 | -14.3186 | -18.4008 | -27.3824 | -43.1937 | -48.6265 | -52.1408 | 1.6827 | 1.1026 | 0.52163 | -0.19374 | -1.1819 | -2.2553 | -4.1741 | -6.6305 | -9.4257 | -12.621 | -19.6351 | -32.0254 | -36.3111 | -39.337 | -0.062428 | -0.81227 | -1.5651 | -2.5375 | -3.8404 | -5.2513 | -7.6725 | -10.7282 | -14.2713 | -18.3215 | -27.2131 | -42.1284 | -47.4488 | -51.0018
|  | NORTH HINKSEY | ST |  |  | 0.62328 | 0.4164 | 0.13449 | -0.29283 | -0.83851 | -1.5467 | -2.4804 | -3.6521 | -5.0319 | -6.7522 | -11.5564 | -27.894 | -39.0517 | -42.7808 | 1.9681 | 1.7861 | 1.5417 | 1.1662 | 0.70015 | 0.10095 | -0.69521 | -1.6967 | -2.8841 | -4.3544 | -8.413 | -21.7068 | -30.9802 | -34.489 | 0.39802 | 0.19984 | -0.070595 | -0.49375 | -1.0269 | -1.7383 | -2.7012 | -3.9043 | -5.3308 | -7.1059 | -12.0289 | -28.2863 | -39.4209 | -43.1375
|  | NORTH HINKSEY | FS |  |  | 0.20009 | -0.43249 | -1.1935 | -2.1547 | -3.2108 | -4.8453 | -6.636 | -9.3716 | -12.7734 | -16.097 | -22.3677 | -37.1199 | -43.098 | -45.4447 | 1.8386 | 1.5388 | 1.179 | 0.73781 | 0.17915 | -0.54833 | -1.5326 | -2.826 | -4.2964 | -5.9437 | -9.9947 | -22.8638 | -35.4947 | -42.8691 | 0.25052 | -0.082896 | -0.48248 | -0.99764 | -1.682 | -2.57 | -3.7613 | -5.3298 | -7.1298 | -9.1446 | -14.0901 | -29.8065 | -45.0592 | -53.2377
MINETY GSP | CIRENCESTER BSP | NORTHLEACH | MINIMUM HEADROOM | SP 10557 14251 | YES | 4.2625 | 4.0549 | 3.8346 | 3.6785 | 3.4907 | 3.276 | 3.005 | 2.6767 | 2.266 | 1.7746 | 0.53655 | -1.9686 | -3.1839 | -3.6904 | 5.1308 | 5.0499 | 4.969 | 4.913 | 4.8457 | 4.7746 | 4.6744 | 4.5592 | 4.4294 | 4.0783 | 3.1478 | 1.2946 | 0.21773 | -0.92606 | 3.8686 | 3.6974 | 3.5114 | 3.3679 | 3.1894 | 2.9746 | 2.7016 | 2.3704 | 1.9744 | 1.5014 | 0.26976 | -2.1407 | -3.2975 | -4.4935
|  | NORTHLEACH | CT |  |  | 4.4062 | 4.2657 | 4.1209 | 3.9531 | 3.7593 | 3.5117 | 3.2122 | 2.8335 | 2.3597 | 1.8068 | 0.53655 | -1.9686 | -3.1839 | -3.6904 | 5.1823 | 5.1282 | 5.0745 | 5.0152 | 4.948 | 4.862 | 4.7688 | 4.6541 | 4.4724 | 4.0783 | 3.1478 | 1.2946 | 0.47561 | -0.081638 | 3.9782 | 3.8577 | 3.7277 | 3.5709 | 3.3827 | 3.1436 | 2.8533 | 2.4911 | 2.036 | 1.5021 | 0.26976 | -2.1407 | -3.2584 | -3.7205
|  | NORTHLEACH | LW |  |  | 4.2625 | 4.0549 | 3.8346 | 3.6785 | 3.4907 | 3.276 | 3.005 | 2.6767 | 2.266 | 1.7746 | 0.59029 | -1.5275 | -2.3048 | -2.7928 | 5.1308 | 5.0499 | 4.969 | 4.913 | 4.8457 | 4.7746 | 4.6744 | 4.5592 | 4.4294 | 4.2695 | 3.4245 | 1.9967 | 1.5677 | 1.2615 | 3.8686 | 3.6974 | 3.5114 | 3.3679 | 3.1894 | 2.9746 | 2.7016 | 2.3704 | 1.9744 | 1.5014 | 0.35371 | -1.6701 | -2.3814 | -2.8292
|  | NORTHLEACH | ST |  |  | 4.4828 | 4.3888 | 4.2949 | 4.1582 | 4.0104 | 3.8417 | 3.647 | 3.426 | 3.1533 | 2.8328 | 1.9783 | -0.85599 | -2.3173 | -2.4571 | 5.2162 | 5.1831 | 5.1501 | 5.1019 | 5.0499 | 4.992 | 4.925 | 4.8507 | 4.7668 | 4.6725 | 4.178 | 2.0014 | 0.82968 | 0.63669 | 4.0389 | 3.9581 | 3.8744 | 3.7533 | 3.6182 | 3.4603 | 3.276 | 3.0605 | 2.8013 | 2.4948 | 1.6698 | -1.0843 | -2.4782 | -2.5646
|  | NORTHLEACH | FS |  |  | 4.4062 | 4.2657 | 4.1209 | 3.9531 | 3.7593 | 3.5117 | 3.2122 | 2.8335 | 2.3597 | 1.8068 | 0.53655 | -1.9686 | -3.1839 | -3.6904 | 5.233 | 5.2092 | 5.1833 | 5.1417 | 5.0959 | 5.0441 | 4.988 | 4.9276 | 4.8542 | 4.7551 | 4.211 | 2.2438 | 0.21773 | -0.92606 | 4.0619 | 3.989 | 3.9092 | 3.7895 | 3.6504 | 3.4927 | 3.3023 | 3.0819 | 2.8165 | 2.5173 | 1.7743 | -0.8798 | -3.2975 | -4.4935
BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE | MINIMUM HEADROOM | SU 72207 71092 | YES | 5.1698 | 4.8704 | 4.6183 | 4.0487 | 3.3973 | 2.7039 | 1.9118 | 1.0121 | -0.041263 | -1.0813 | -3.3289 | -9.1252 | -17.3448 | -21.8545 | 6.9418 | 6.7453 | 6.6007 | 6.3278 | 6.0182 | 5.6907 | 5.2989 | 4.836 | 4.1258 | 3.3587 | 1.6883 | -3.2535 | -9.7782 | -19.4492 | 5.0266 | 4.7564 | 4.534 | 4.0489 | 3.4969 | 2.9077 | 2.2272 | 1.4481 | 0.51442 | -0.41239 | -2.4793 | -9.4229 | -17.2944 | -21.6575
|  | NORTHUMBERLAND AVENUE | CT |  |  | 5.4472 | 5.3429 | 5.2283 | 4.7892 | 4.2653 | 3.6574 | 2.9447 | 2.086 | 0.89755 | -0.31166 | -2.8467 | -9.1252 | -17.3448 | -21.8545 | 7.0681 | 6.9784 | 6.8756 | 6.6274 | 6.3284 | 5.9563 | 5.4926 | 4.9273 | 4.1529 | 3.3587 | 1.6883 | -2.576 | -8.6102 | -12.1502 | 5.2798 | 5.1918 | 5.0931 | 4.7218 | 4.2782 | 3.7531 | 3.125 | 2.3641 | 1.2992 | 0.20324 | -2.0971 | -9.4229 | -17.2944 | -21.6575
|  | NORTHUMBERLAND AVENUE | LW |  |  | 5.1698 | 4.8704 | 4.6183 | 4.0487 | 3.3973 | 2.7039 | 1.9118 | 1.0121 | -0.041263 | -1.0813 | -3.3289 | -6.9223 | -8.534 | -9.5406 | 6.9418 | 6.7453 | 6.6007 | 6.3278 | 6.0182 | 5.6907 | 5.2989 | 4.836 | 4.2537 | 3.6876 | 2.4351 | 0.44208 | -0.61183 | -1.5207 | 5.0266 | 4.7564 | 4.534 | 4.0489 | 3.4969 | 2.9077 | 2.2272 | 1.4481 | 0.51442 | -0.41239 | -2.4793 | -5.8504 | -7.4296 | -8.5262
|  | NORTHUMBERLAND AVENUE | ST |  |  | 5.5258 | 5.4778 | 5.4292 | 5.2819 | 5.0937 | 4.8707 | 4.583 | 4.2282 | 3.7942 | 3.3877 | 2.4869 | -0.25035 | -2.4355 | -4.2353 | 7.1051 | 7.0474 | 6.983 | 6.8596 | 6.7072 | 6.5123 | 6.2515 | 5.938 | 5.5134 | 5.1127 | 4.236 | 1.3766 | -1.9623 | -6.395 | 5.348 | 5.3088 | 5.2676 | 5.1497 | 4.9978 | 4.8094 | 4.5569 | 4.2462 | 3.8459 | 3.469 | 2.6216 | -0.10152 | -2.2663 | -3.9074
|  | NORTHUMBERLAND AVENUE | FS |  |  | 5.4472 | 5.3429 | 5.2283 | 4.7892 | 4.2653 | 3.6574 | 2.9447 | 2.086 | 0.89755 | -0.31166 | -2.8467 | -9.1252 | -17.3448 | -21.8545 | 7.059 | 6.8776 | 6.6985 | 6.4616 | 6.176 | 5.8215 | 5.4077 | 4.8658 | 4.1258 | 3.3721 | 1.8021 | -3.2535 | -9.7782 | -19.4492 | 5.2632 | 5.0828 | 4.8983 | 4.6295 | 4.3097 | 3.8943 | 3.4181 | 2.7658 | 1.9424 | 1.1309 | -0.55113 | -5.2052 | -8.7674 | -11.1849
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD | MINIMUM HEADROOM | SU 68329 86784 | YES | 2.6298 | 2.5012 | 2.3559 | 2.2259 | 1.8097 | 1.0567 | -0.01503 | -1.4715 | -3.31 | -5.5915 | -11.2031 | -20.6084 | -22.9983 | -24.7162 | -3.2715 | -3.42 | -3.5756 | -3.7691 | -4.1707 | -4.7452 | -5.5706 | -6.6984 | -8.1255 | -9.9016 | -14.2759 | -21.5903 | -23.4163 | -24.7494 | -4.1109 | -4.322 | -4.5962 | -4.9485 | -5.4566 | -6.1766 | -7.2027 | -8.5986 | -10.3613 | -12.5497 | -17.9338 | -26.9541 | -29.2385 | -30.8843
|  | NUFFIELD | CT |  |  | 2.7165 | 2.636 | 2.5431 | 2.4381 | 2.3117 | 2.1528 | 1.8456 | 1.2389 | 0.461 | -0.51617 | -3.2218 | -12.3536 | -16.7794 | -16.4938 | -3.1646 | -3.2071 | -3.2618 | -3.3944 | -3.5714 | -3.8206 | -4.1524 | -4.6111 | -5.2014 | -5.9488 | -8.0334 | -15.1274 | -18.5112 | -18.2593 | -4.0106 | -4.124 | -4.2652 | -4.4446 | -4.6788 | -5.0017 | -5.4245 | -6.0039 | -6.7473 | -7.6823 | -10.2741 | -19.0307 | -23.262 | -22.9811
|  | NUFFIELD | LW |  |  | 2.6298 | 2.5012 | 2.3559 | 2.2259 | 1.8097 | 1.0567 | -0.01503 | -1.4715 | -3.31 | -5.5915 | -11.2031 | -20.6084 | -22.9983 | -24.7162 | -3.1893 | -3.2936 | -3.4948 | -3.7691 | -4.1707 | -4.7452 | -5.5706 | -6.6984 | -8.1255 | -9.9016 | -14.2759 | -21.5903 | -23.4163 | -24.7494 | -4.1109 | -4.322 | -4.5962 | -4.9485 | -5.4566 | -6.1766 | -7.2027 | -8.5986 | -10.3613 | -12.5497 | -17.9338 | -26.9541 | -29.2385 | -30.8843
|  | NUFFIELD | ST |  |  | 2.7671 | 2.7147 | 2.6645 | 2.5906 | 2.5162 | 2.4296 | 2.334 | 2.2278 | 2.1075 | 1.9678 | 1.6203 | 0.54152 | -0.077027 | -0.22778 | -3.1399 | -3.1663 | -3.1942 | -3.2311 | -3.2715 | -3.3202 | -3.3775 | -3.4454 | -3.5221 | -3.6151 | -3.8616 | -4.6914 | -5.196 | -5.4377 | -3.9005 | -3.9359 | -3.9718 | -4.0241 | -4.0789 | -4.143 | -4.2142 | -4.2932 | -4.3813 | -4.4827 | -4.7319 | -5.4232 | -5.7433 | -5.8589
|  | NUFFIELD | FS |  |  | 2.7165 | 2.636 | 2.5431 | 2.4381 | 2.3117 | 2.1528 | 1.8456 | 1.2389 | 0.461 | -0.51617 | -3.2218 | -12.3536 | -16.7794 | -16.4938 | -3.2715 | -3.42 | -3.5756 | -3.7611 | -4.0104 | -4.2867 | -4.7462 | -5.3264 | -5.9643 | -6.6978 | -8.4309 | -12.6394 | -15.7096 | -16.6784 | -3.9063 | -3.9505 | -3.9952 | -4.0639 | -4.1896 | -4.5388 | -5.1142 | -5.837 | -6.6395 | -7.5616 | -9.7289 | -15.0015 | -18.8003 | -19.9332
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE | MINIMUM HEADROOM | SU 63496 53664 | YES | 17.2444 | 16.8342 | 16.4156 | 15.7523 | 15.0944 | 14.421 | 13.803 | 13.1387 | 12.3062 | 11.4255 | 9.4822 | 5.0302 | 2.3393 | -0.76356 | 18.5704 | 18.3874 | 18.1991 | 17.8909 | 17.5567 | 17.2211 | 16.902 | 16.548 | 16.1197 | 15.6485 | 14.5683 | 10.3351 | 5.3544 | -0.19677 | 16.4924 | 16.1387 | 15.7779 | 15.1901 | 14.5849 | 13.9709 | 13.3951 | 12.778 | 12.0092 | 11.1967 | 9.4071 | 5.2859 | 2.1399 | -1.0198
|  | OAKRIDGE | CT |  |  | 17.5889 | 17.3728 | 17.1411 | 16.6146 | 16.1082 | 15.6251 | 15.1573 | 14.6382 | 13.7346 | 12.7775 | 10.813 | 5.8504 | 2.4098 | 0.41612 | 18.6762 | 18.5455 | 18.401 | 18.1171 | 17.7991 | 17.5221 | 17.2298 | 16.8976 | 16.3877 | 15.8175 | 14.6022 | 11.4899 | 8.8443 | 5.9177 | 16.8086 | 16.6304 | 16.4388 | 15.9773 | 15.5064 | 15.0732 | 14.643 | 14.1694 | 13.3431 | 12.4642 | 10.6649 | 6.1281 | 2.9715 | 1.1362
|  | OAKRIDGE | LW |  |  | 17.2444 | 16.8342 | 16.4156 | 15.7523 | 15.0944 | 14.421 | 13.803 | 13.1387 | 12.3062 | 11.4255 | 9.4822 | 5.0302 | 2.3393 | -0.76356 | 18.5704 | 18.3874 | 18.1991 | 17.8909 | 17.5567 | 17.2211 | 16.902 | 16.548 | 16.1197 | 15.6485 | 14.5683 | 12.1602 | 7.9709 | 5.403 | 16.4924 | 16.1387 | 15.7779 | 15.1901 | 14.5849 | 13.9709 | 13.3951 | 12.778 | 12.0092 | 11.1967 | 9.4071 | 5.2859 | 2.1399 | -1.0198
|  | OAKRIDGE | ST |  |  | 17.7072 | 17.5543 | 17.3906 | 17.066 | 16.7837 | 16.5657 | 16.3642 | 16.1539 | 15.9224 | 15.6739 | 15.0469 | 12.1673 | 9.7307 | 7.105 | 18.7271 | 18.6265 | 18.5155 | 18.2861 | 18.0495 | 17.8818 | 17.7038 | 17.5259 | 17.3064 | 17.0643 | 16.451 | 13.9573 | 11.4543 | 8.3379 | 16.9159 | 16.7951 | 16.6646 | 16.3843 | 16.1129 | 15.9172 | 15.723 | 15.5266 | 15.3045 | 15.0646 | 14.4594 | 11.7857 | 9.4833 | 7.0984
|  | OAKRIDGE | FS |  |  | 17.5889 | 17.3728 | 17.1411 | 16.6146 | 16.1082 | 15.6251 | 15.1573 | 14.6382 | 13.7346 | 12.7775 | 10.813 | 5.8504 | 2.4098 | 0.41612 | 18.7005 | 18.5819 | 18.4418 | 18.2293 | 17.9912 | 17.7341 | 17.4554 | 17.1323 | 16.7148 | 16.2213 | 14.9382 | 10.3351 | 5.3544 | -0.19677 | 16.9065 | 16.7855 | 16.6435 | 16.3697 | 16.0796 | 15.7745 | 15.4601 | 15.106 | 14.6531 | 14.1326 | 12.8211 | 8.1135 | 3.7566 | 0.89685
COWLEY GSP | HEADINGTON BSP | OLD ROAD | MINIMUM HEADROOM | SP 55274 06426 | NO | 10.4983 | 9.9873 | 9.3946 | 8.5539 | 7.7129 | 6.9458 | 6.107 | 5.0601 | 3.6438 | 2.2081 | -1.2756 | -8.0171 | -11.3913 | -11.8517 | 11.3648 | 11.0381 | 10.6355 | 10.2237 | 9.7363 | 9.2804 | 8.7801 | 8.1148 | 7.1233 | 6.082 | 3.6869 | -2.8801 | -9.9906 | -18.0424 | 10.1528 | 9.7091 | 9.1857 | 8.4354 | 7.6535 | 6.9377 | 6.1711 | 5.1629 | 3.784 | 2.3884 | -1.0102 | -7.5688 | -11.6581 | -14.2439
|  | OLD ROAD | CT |  |  | 10.7443 | 10.3769 | 9.9334 | 9.2819 | 8.6024 | 8.0863 | 7.3996 | 6.4622 | 5.0007 | 3.5846 | 0.48599 | -5.5003 | -7.8481 | -9.2371 | 11.4127 | 11.1188 | 10.7627 | 10.4534 | 10.019 | 9.6802 | 9.2338 | 8.5666 | 7.5004 | 6.5536 | 4.339 | -0.44757 | -3.7897 | -8.1732 | 10.3711 | 10.0545 | 9.6673 | 9.0941 | 8.4711 | 8.0022 | 7.3387 | 6.446 | 5.0618 | 3.6977 | 0.69632 | -5.0605 | -7.3028 | -8.6801
|  | OLD ROAD | LW |  |  | 10.4983 | 9.9873 | 9.3946 | 8.5539 | 7.7129 | 6.9458 | 6.107 | 5.0601 | 3.6438 | 2.2081 | -1.2756 | -8.0171 | -11.3913 | -11.8517 | 11.3648 | 11.0381 | 10.6355 | 10.2237 | 9.7363 | 9.2804 | 8.7801 | 8.1148 | 7.1233 | 6.2056 | 3.8709 | -2.4898 | -5.5176 | -6.0805 | 10.1528 | 9.7091 | 9.1857 | 8.4354 | 7.6535 | 6.9377 | 6.1711 | 5.1629 | 3.784 | 2.3884 | -1.0102 | -7.5688 | -10.4776 | -11.0577
|  | OLD ROAD | ST |  |  | 10.8494 | 10.5555 | 10.2 | 9.8488 | 9.5067 | 9.3765 | 9.1621 | 8.8164 | 8.2036 | 7.7214 | 6.4414 | 1.4548 | -1.7807 | -3.001 | 11.4336 | 11.1575 | 10.8222 | 10.5147 | 10.1288 | 10.0506 | 9.9329 | 9.6837 | 9.0389 | 8.6175 | 7.5204 | 3.1565 | -0.99141 | -5.2329 | 10.4682 | 10.2185 | 9.9102 | 9.6024 | 9.2794 | 9.1662 | 8.9576 | 8.6254 | 8.0347 | 7.5563 | 6.2495 | 1.2704 | -1.9536 | -3.1432
|  | OLD ROAD | FS |  |  | 10.7443 | 10.3769 | 9.9334 | 9.2819 | 8.6024 | 8.0863 | 7.3996 | 6.4622 | 5.0007 | 3.5846 | 0.48599 | -5.5003 | -7.8481 | -9.2371 | 11.5359 | 11.2937 | 11.0123 | 10.6537 | 10.1695 | 9.6875 | 9.0886 | 8.2505 | 7.1817 | 6.082 | 3.6869 | -2.8801 | -9.9906 | -18.0424 | 10.3672 | 9.9774 | 9.5417 | 9.0475 | 8.5171 | 7.9393 | 7.1719 | 6.1189 | 4.8411 | 3.5253 | 0.71525 | -6.309 | -11.6581 | -14.2439
COWLEY GSP | OXFORD (OSNEY) BSP | OSNEY | MINIMUM HEADROOM | SP 50148 05901 | YES | 8.409 | 8.3059 | 8.1673 | 7.9154 | 7.5389 | 6.9659 | 5.5605 | 3.6599 | 0.87382 | -2.4713 | -10.379 | -24.0013 | -28.0416 | -31.018 | 13.7948 | 13.6628 | 13.4983 | 13.1984 | 12.7951 | 12.279 | 11.6509 | 10.1995 | 8.3515 | 5.7743 | -0.33902 | -10.7906 | -13.9585 | -29.2028 | 8.0141 | 7.9146 | 7.7809 | 7.5444 | 7.1931 | 6.7076 | 5.9045 | 3.7509 | 1.0845 | -2.1242 | -9.7103 | -22.7793 | -26.7225 | -29.6965
|  | OSNEY | CT |  |  | 8.409 | 8.3059 | 8.1673 | 7.9154 | 7.5389 | 6.9659 | 5.5605 | 3.6599 | 0.87382 | -2.4713 | -10.379 | -24.0013 | -28.0416 | -31.018 | 13.7948 | 13.6628 | 13.4983 | 13.1984 | 12.7951 | 12.279 | 11.6509 | 10.1995 | 8.3515 | 5.7743 | -0.33902 | -10.7906 | -13.9585 | -16.5384 | 8.0141 | 7.9146 | 7.7809 | 7.5444 | 7.1931 | 6.7076 | 5.9045 | 3.7509 | 1.0845 | -2.1242 | -9.7103 | -22.7793 | -26.7225 | -29.6965
|  | OSNEY | LW |  |  | 8.4658 | 8.4089 | 8.3578 | 8.2141 | 7.9887 | 7.7312 | 7.1311 | 6.4234 | 5.8573 | 5.3344 | 4.2373 | 1.1697 | -0.93639 | -2.6948 | 13.8433 | 13.7801 | 13.7196 | 13.5388 | 13.2908 | 13.0011 | 12.6479 | 12.2841 | 11.9473 | 11.6177 | 10.9296 | 8.9858 | 7.145 | 5.3611 | 8.0697 | 8.0156 | 7.9669 | 7.8324 | 7.6257 | 7.3876 | 7.079 | 6.5448 | 6.0177 | 5.5218 | 4.449 | 1.3423 | -0.85086 | -2.8087
|  | OSNEY | ST |  |  | 8.5063 | 8.491 | 8.47 | 8.3589 | 8.1975 | 8.0174 | 7.8204 | 7.6266 | 7.4404 | 7.2503 | 6.7945 | 5.4194 | 4.1131 | 3.147 | 13.8772 | 13.8097 | 13.7261 | 13.5564 | 13.3467 | 13.1118 | 12.8495 | 12.5807 | 12.2876 | 11.9802 | 11.1496 | 7.7279 | 1.9248 | -7.7678 | 8.1088 | 8.0947 | 8.0753 | 7.9705 | 7.8257 | 7.6645 | 7.4847 | 7.31 | 7.1238 | 6.9344 | 6.4789 | 5.2676 | 4.0921 | 2.9394
|  | OSNEY | FS |  |  | 8.409 | 8.3059 | 8.1673 | 7.9154 | 7.5389 | 6.9659 | 5.5605 | 3.6599 | 0.87382 | -2.4713 | -10.379 | -24.0013 | -28.0416 | -31.018 | 13.8403 | 13.7384 | 13.6202 | 13.4031 | 13.1271 | 12.8097 | 12.3421 | 11.6855 | 11.0238 | 10.2726 | 8.2377 | 0.25184 | -11.2873 | -29.2028 | 8.0895 | 8.0635 | 8.0308 | 7.9352 | 7.7879 | 7.6131 | 7.4075 | 7.1859 | 6.9897 | 6.7841 | 5.8029 | 0.81557 | -3.6955 | -6.3521
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON | MINIMUM HEADROOM | SU 52061 50913 | YES | 7.6809 | 7.5883 | 7.4613 | 7.1591 | 6.7561 | 6.1262 | 5.2776 | 4.2194 | 3.0093 | 1.5181 | -5.5653 | -17.6457 | -20.7498 | -22.8438 | 11.9541 | 11.8334 | 11.6676 | 11.2793 | 10.7573 | 10.0241 | 9.0398 | 7.8201 | 6.4378 | 4.7353 | 0.056919 | -8.3829 | -10.4411 | -11.8714 | 6.7078 | 6.5291 | 6.3219 | 5.8686 | 5.327 | 4.6208 | 3.7454 | 2.731 | 0.64206 | -2.1789 | -9.0159 | -20.6958 | -23.6765 | -25.6812
|  | OVERTON | CT |  |  | 7.7184 | 7.6706 | 7.6067 | 7.5031 | 7.3569 | 7.1527 | 6.8624 | 6.5058 | 6.0324 | 5.4291 | 3.8716 | -2.5058 | -6.8252 | -6.8162 | 12.0037 | 11.9455 | 11.8689 | 11.7469 | 11.5748 | 11.3343 | 10.993 | 10.5758 | 10.0797 | 9.4441 | 7.783 | 2.5622 | -0.1491 | -0.045315 | 6.8492 | 6.7521 | 6.6378 | 6.4044 | 6.1103 | 5.7375 | 5.2392 | 4.6471 | 3.7928 | 2.7456 | -0.062704 | -6.0455 | -9.9827 | -9.952
|  | OVERTON | LW |  |  | 7.6809 | 7.5883 | 7.4613 | 7.1591 | 6.7561 | 6.1262 | 5.2776 | 4.2194 | 3.0093 | 1.5181 | -5.5653 | -17.6457 | -20.7498 | -22.8438 | 11.9541 | 11.8334 | 11.6676 | 11.2793 | 10.7573 | 10.0241 | 9.0398 | 7.8201 | 6.4378 | 4.7353 | 0.056919 | -8.3829 | -10.4411 | -11.8714 | 6.7078 | 6.5291 | 6.3219 | 5.8686 | 5.327 | 4.6208 | 3.7454 | 2.731 | 0.64206 | -2.1789 | -9.0159 | -20.6958 | -23.6765 | -25.6812
|  | OVERTON | ST |  |  | 7.7686 | 7.7557 | 7.7371 | 7.5932 | 7.4788 | 7.3604 | 7.1895 | 7.0567 | 6.9194 | 6.7569 | 6.3118 | 4.0457 | 1.2152 | 0.82999 | 12.0688 | 12.0558 | 12.0371 | 11.8642 | 11.7301 | 11.5944 | 11.3978 | 11.2555 | 11.115 | 10.9531 | 10.5188 | 8.121 | 5.7866 | 5.1282 | 6.9177 | 6.8773 | 6.8246 | 6.5979 | 6.4071 | 6.2031 | 5.9169 | 5.6629 | 5.3899 | 5.0568 | 4.0332 | -1.2173 | -3.988 | -4.2941
|  | OVERTON | FS |  |  | 7.7184 | 7.6706 | 7.6067 | 7.5031 | 7.3569 | 7.1527 | 6.8624 | 6.5058 | 6.0324 | 5.4291 | 3.8716 | -2.5058 | -6.8252 | -6.8162 | 12.0715 | 12.0615 | 12.0479 | 11.9976 | 11.9422 | 11.874 | 11.798 | 11.719 | 11.6473 | 11.5643 | 11.3414 | 10.5245 | 7.1843 | 4.6376 | 6.9342 | 6.9054 | 6.8645 | 6.7602 | 6.6476 | 6.5146 | 6.3679 | 6.202 | 6.0058 | 5.7854 | 5.2056 | 2.1376 | -2.2352 | -4.8213
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH | MINIMUM HEADROOM | SU 62243 66052 | YES | 1.4063 | 1.3495 | 1.2778 | 1.1627 | 0.99146 | 0.76018 | 0.43304 | -0.0071231 | -0.57396 | -1.303 | -3.6203 | -14.712 | -23.6314 | -26.5372 | 3.0338 | 2.999 | 2.9552 | 2.9002 | 2.8266 | 2.7258 | 2.5873 | 2.4005 | 1.7954 | 1.0066 | -1.2686 | -9.9724 | -17.0557 | -19.4683 | 1.8642 | 1.8096 | 1.7283 | 1.5506 | 1.3106 | 0.99122 | 0.54734 | -0.043875 | -0.80406 | -1.7753 | -4.5702 | -15.2336 | -23.8544 | -26.7284
|  | PADWORTH | CT |  |  | 1.4639 | 1.4502 | 1.4342 | 1.4116 | 1.3819 | 1.3387 | 1.2816 | 1.2109 | 1.119 | 1.0022 | 0.73898 | -0.25906 | -0.93805 | -1.2932 | 3.0545 | 3.0306 | 3.0007 | 2.955 | 2.8941 | 2.811 | 2.6969 | 2.5552 | 2.3651 | 2.1148 | 1.5388 | 0.29366 | -0.31151 | -0.73662 | 1.9034 | 1.8706 | 1.8317 | 1.7699 | 1.6919 | 1.5859 | 1.4447 | 1.2678 | 1.0317 | 0.7273 | 0.035527 | -1.4394 | -2.1366 | -2.5224
|  | PADWORTH | LW |  |  | 1.4063 | 1.3495 | 1.2778 | 1.1627 | 0.99146 | 0.76018 | 0.43304 | -0.0071231 | -0.57396 | -1.303 | -3.6203 | -14.712 | -23.6314 | -26.5372 | 3.0338 | 2.999 | 2.9552 | 2.9002 | 2.8266 | 2.7258 | 2.5873 | 2.4005 | 1.7954 | 1.0066 | -1.2686 | -9.9724 | -17.0557 | -19.4683 | 1.8642 | 1.8096 | 1.7283 | 1.5506 | 1.3106 | 0.99122 | 0.54734 | -0.043875 | -0.80406 | -1.7753 | -4.5702 | -15.2336 | -23.8544 | -26.7284
|  | PADWORTH | ST |  |  | 1.4731 | 1.4665 | 1.4571 | 1.4189 | 1.3833 | 1.3427 | 1.2861 | 1.2314 | 1.1468 | 1.0522 | 0.81273 | -0.36223 | -1.18 | -1.4025 | 3.0598 | 3.0389 | 3.0117 | 2.9435 | 2.873 | 2.787 | 2.6674 | 2.5331 | 2.3439 | 2.1196 | 1.5491 | 0.058529 | -0.73042 | -1.0589 | 1.9168 | 1.891 | 1.8588 | 1.7794 | 1.6965 | 1.5963 | 1.46 | 1.3029 | 1.0853 | 0.82389 | 0.16408 | -1.5599 | -2.4212 | -2.6891
|  | PADWORTH | FS |  |  | 1.4639 | 1.4502 | 1.4342 | 1.4116 | 1.3819 | 1.3387 | 1.2816 | 1.2109 | 1.119 | 1.0022 | 0.73898 | -0.25906 | -0.93805 | -1.2932 | 3.0695 | 3.0568 | 3.0423 | 3.0175 | 2.9881 | 2.9516 | 2.911 | 2.8631 | 2.803 | 2.7321 | 2.5433 | 1.7897 | 0.88223 | 0.27893 | 1.9315 | 1.9175 | 1.9031 | 1.8722 | 1.8358 | 1.79 | 1.7428 | 1.6856 | 1.6112 | 1.5232 | 1.2919 | 0.3742 | -0.69756 | -1.3803
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE | MINIMUM HEADROOM | SU 62960 76144 | YES | 16.9204 | 16.7131 | 16.4903 | 16.2134 | 15.8847 | 15.4201 | 14.9006 | 14.2879 | 13.4991 | 12.5827 | 10.3169 | 6.0052 | 4.1137 | 2.9223 | 19.5011 | 19.3958 | 19.2615 | 19.1073 | 18.9192 | 18.5953 | 18.2209 | 17.7613 | 17.1588 | 16.4389 | 14.6658 | 11.4667 | 8.8373 | 7.0285 | 17.0505 | 16.8646 | 16.6599 | 16.399 | 16.0879 | 15.6475 | 15.1508 | 14.561 | 13.7961 | 12.9036 | 10.6548 | 6.4438 | 4.547 | 2.7918
|  | PANGBOURNE | CT |  |  | 17.0945 | 16.9819 | 16.8528 | 16.6364 | 16.3721 | 15.9472 | 15.5485 | 15.0452 | 14.3247 | 13.4784 | 11.5828 | 7.6261 | 5.7685 | 4.6345 | 19.5503 | 19.4723 | 19.3745 | 19.2338 | 19.0518 | 18.7252 | 18.4146 | 18.01 | 17.4724 | 16.8161 | 15.3137 | 12.324 | 10.7982 | 9.3349 | 17.2007 | 17.0974 | 16.9757 | 16.7754 | 16.5289 | 16.127 | 15.7464 | 15.2626 | 14.5731 | 13.7556 | 11.9208 | 8.0696 | 6.2885 | 5.1497
|  | PANGBOURNE | LW |  |  | 16.9204 | 16.7131 | 16.4903 | 16.2134 | 15.8847 | 15.4201 | 14.9006 | 14.2879 | 13.4991 | 12.5827 | 10.3169 | 6.0052 | 4.1137 | 2.9223 | 19.5011 | 19.402 | 19.2848 | 19.1247 | 18.9193 | 18.5953 | 18.2209 | 17.7613 | 17.1588 | 16.4389 | 14.6658 | 11.4667 | 10.0254 | 8.9101 | 17.0505 | 16.8646 | 16.6599 | 16.399 | 16.0879 | 15.6475 | 15.1508 | 14.561 | 13.7961 | 12.9036 | 10.6548 | 6.4438 | 4.547 | 3.2653
|  | PANGBOURNE | ST |  |  | 17.163 | 17.0922 | 17.007 | 16.8839 | 16.7499 | 16.4814 | 16.2853 | 16.0434 | 15.7281 | 15.3397 | 14.2978 | 10.158 | 7.4164 | 6.4556 | 19.5771 | 19.5216 | 19.4527 | 19.3596 | 19.2517 | 19.0268 | 18.8561 | 18.6436 | 18.3642 | 18.0202 | 17.0689 | 13.481 | 11.0064 | 9.88 | 17.2592 | 17.1945 | 17.116 | 17.0004 | 16.8738 | 16.6189 | 16.4302 | 16.1971 | 15.8856 | 15.5031 | 14.4715 | 10.3611 | 7.6207 | 6.6585
|  | PANGBOURNE | FS |  |  | 17.0945 | 16.9819 | 16.8528 | 16.6364 | 16.3721 | 15.9472 | 15.5485 | 15.0452 | 14.3247 | 13.4784 | 11.5828 | 7.6261 | 5.7685 | 4.6345 | 19.5162 | 19.3958 | 19.2615 | 19.1073 | 18.9192 | 18.6502 | 18.3221 | 17.8766 | 17.3542 | 16.7904 | 15.5248 | 11.8965 | 8.8373 | 7.0285 | 17.2102 | 17.0885 | 16.9566 | 16.7776 | 16.5637 | 16.2637 | 15.9068 | 15.432 | 14.8645 | 14.2237 | 12.7168 | 8.3124 | 4.6552 | 2.7918
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE | MINIMUM HEADROOM | SU 51369 08259 | NO | 13.7024 | 13.4735 | 13.2457 | 12.7578 | 12.25 | 11.6513 | 10.9771 | 10.253 | 9.3143 | 8.3417 | 6.2946 | 2.3564 | -0.85917 | -2.7107 | 15.7689 | 15.6802 | 15.5885 | 15.4066 | 15.2085 | 14.9582 | 14.6607 | 14.3258 | 13.8733 | 13.384 | 12.3181 | 9.3491 | 4.9267 | -1.0545 | 13.0619 | 12.8598 | 12.6581 | 12.2272 | 11.777 | 11.2545 | 10.6655 | 10.0295 | 9.1919 | 8.3204 | 6.4827 | 2.9491 | 0.095918 | -1.5957
|  | PARK GATE | CT |  |  | 14.0189 | 13.9584 | 13.8937 | 13.5847 | 13.2559 | 12.8338 | 12.3651 | 11.8431 | 10.8573 | 9.8142 | 7.6209 | 2.4756 | -0.85917 | -2.7107 | 15.8501 | 15.7899 | 15.7203 | 15.568 | 15.4007 | 15.1781 | 14.921 | 14.623 | 14.1354 | 13.5736 | 12.3541 | 9.3491 | 6.7059 | 3.6933 | 13.3385 | 13.2844 | 13.2258 | 12.9535 | 12.6612 | 12.2933 | 11.8838 | 11.4243 | 10.5511 | 9.6206 | 7.6653 | 3.0769 | 0.095918 | -1.5957
|  | PARK GATE | LW |  |  | 13.7024 | 13.4735 | 13.2457 | 12.7578 | 12.25 | 11.6513 | 10.9771 | 10.253 | 9.3143 | 8.3417 | 6.2946 | 2.3564 | -0.066722 | -1.3816 | 15.7689 | 15.6802 | 15.5885 | 15.4066 | 15.2085 | 14.9582 | 14.6607 | 14.3258 | 13.8733 | 13.384 | 12.3181 | 10.3717 | 9.0997 | 8.1112 | 13.0619 | 12.8598 | 12.6581 | 12.2272 | 11.777 | 11.2545 | 10.6655 | 10.0295 | 9.1919 | 8.3204 | 6.4827 | 2.9491 | 0.72309 | -0.57728
|  | PARK GATE | ST |  |  | 14.1116 | 14.104 | 14.0905 | 14.0637 | 14.0272 | 13.9217 | 13.7938 | 13.6376 | 13.4345 | 13.1945 | 12.591 | 10.3897 | 8.0098 | 5.1161 | 15.8839 | 15.844 | 15.7949 | 15.7406 | 15.6754 | 15.5674 | 15.4378 | 15.2837 | 15.071 | 14.8272 | 14.2202 | 12.1592 | 9.663 | 6.2643 | 13.4205 | 13.4134 | 13.4005 | 13.3754 | 13.3439 | 13.258 | 13.1539 | 13.0242 | 12.8446 | 12.6339 | 12.1037 | 10.0807 | 7.7951 | 5.1322
|  | PARK GATE | FS |  |  | 14.0189 | 13.9584 | 13.8937 | 13.5847 | 13.2559 | 12.8338 | 12.3651 | 11.8431 | 10.8573 | 9.8142 | 7.6209 | 2.4756 | -0.85917 | -2.7107 | 15.8449 | 15.7788 | 15.6992 | 15.6014 | 15.4834 | 15.3211 | 15.1187 | 14.8794 | 14.5436 | 14.1543 | 13.1631 | 9.5948 | 4.9267 | -1.0545 | 13.3789 | 13.3493 | 13.3143 | 13.2211 | 13.1112 | 12.9542 | 12.7584 | 12.5303 | 12.1909 | 11.8067 | 10.7926 | 7.2194 | 3.4774 | 0.55274
MELKSHAM GSP | AMESBURY | PARK HOUSE | MINIMUM HEADROOM | SU 23138 43780 | YES | 1.9318 | 1.8324 | 1.7192 | 1.6197 | 1.4911 | 1.3364 | 1.1218 | 0.80646 | 0.34169 | -0.2179 | -1.5963 | -3.8929 | -6.5512 | -7.7685 | 2.3768 | 2.3241 | 2.2573 | 2.1762 | 2.0643 | 1.9132 | 1.7059 | 1.4412 | 1.0781 | 0.63749 | -0.44113 | -2.3855 | -4.7565 | -5.8987 | 1.9871 | 1.8937 | 1.783 | 1.673 | 1.5179 | 1.3157 | 1.0403 | 0.69745 | 0.23438 | -0.32359 | -1.684 | -3.9505 | -6.6827 | -7.9773
|  | PARK HOUSE | CT |  |  | 1.9921 | 1.9289 | 1.8567 | 1.7598 | 1.6302 | 1.4742 | 1.2721 | 1.0393 | 0.68502 | 0.18173 | -0.98041 | -3.6902 | -6.5512 | -7.7685 | 2.4008 | 2.364 | 2.3167 | 2.2418 | 2.1333 | 1.9917 | 1.7896 | 1.555 | 1.2447 | 0.81476 | -0.14806 | -2.3855 | -4.7565 | -5.8987 | 2.0428 | 1.9837 | 1.9144 | 1.8131 | 1.6729 | 1.4897 | 1.2396 | 0.94421 | 0.55289 | 0.026993 | -1.1526 | -3.828 | -6.6827 | -7.9773
|  | PARK HOUSE | LW |  |  | 1.9318 | 1.8324 | 1.7192 | 1.6197 | 1.4911 | 1.3364 | 1.1218 | 0.80646 | 0.34169 | -0.2179 | -1.5963 | -3.8929 | -4.978 | -6.109 | 2.3768 | 2.3241 | 2.2573 | 2.1762 | 2.0643 | 1.9132 | 1.7059 | 1.4412 | 1.0781 | 0.63749 | -0.44113 | -2.2291 | -3.3092 | -4.5788 | 1.9871 | 1.8937 | 1.783 | 1.673 | 1.5179 | 1.3157 | 1.0403 | 0.69745 | 0.23438 | -0.32359 | -1.684 | -3.9505 | -5.1709 | -6.5077
|  | PARK HOUSE | ST |  |  | 2.0236 | 1.9905 | 1.9403 | 1.8002 | 1.6782 | 1.5513 | 1.3861 | 1.2405 | 1.0252 | 0.78184 | 0.037505 | -2.6011 | -4.4456 | -5.1894 | 2.4135 | 2.3916 | 2.36 | 2.2221 | 2.1065 | 1.9843 | 1.8134 | 1.6679 | 1.4352 | 1.1822 | 0.51937 | -1.7374 | -3.4993 | -4.4675 | 2.0705 | 2.0377 | 1.9891 | 1.83 | 1.6929 | 1.5448 | 1.344 | 1.1625 | 0.88764 | 0.58356 | -0.21251 | -2.8996 | -4.8728 | -5.7911
|  | PARK HOUSE | FS |  |  | 1.9921 | 1.9289 | 1.8567 | 1.7598 | 1.6302 | 1.4742 | 1.2721 | 1.0393 | 0.68502 | 0.18173 | -0.98041 | -3.6902 | -6.5512 | -7.7685 | 2.4238 | 2.4074 | 2.386 | 2.3345 | 2.2799 | 2.2144 | 2.1406 | 2.0598 | 1.9499 | 1.825 | 1.5107 | 0.38345 | -0.99293 | -2.0704 | 2.0918 | 2.0694 | 2.0396 | 1.9675 | 1.8956 | 1.8122 | 1.7199 | 1.6145 | 1.4755 | 1.3163 | 0.92372 | -0.53489 | -2.2103 | -3.374
MINETY GSP | STRATTON (2 X 90) | PARK NORTH | MINIMUM HEADROOM | SU 18052 84542 | YES | 10.5205 | 10.2017 | 9.8881 | 9.1602 | 8.4136 | 7.6464 | 6.8394 | 6.0053 | 4.9848 | 3.3564 | -3.3486 | -16.6116 | -21.7387 | -25.1277 | 11.7685 | 11.6355 | 11.5048 | 11.2047 | 10.8899 | 10.5563 | 10.1902 | 9.6801 | 8.845 | 7.0076 | 2.1755 | -6.9614 | -10.1741 | -12.5242 | 10.2264 | 9.9565 | 9.6898 | 9.0686 | 8.4085 | 7.7226 | 6.9973 | 6.2465 | 5.3258 | 2.7129 | -3.6483 | -16.1282 | -20.8911 | -24.0889
|  | PARK NORTH | CT |  |  | 10.945 | 10.8362 | 10.7069 | 10.1547 | 9.5576 | 8.8932 | 8.1554 | 7.3115 | 5.8836 | 3.3564 | -3.3486 | -16.6116 | -21.7387 | -25.1277 | 11.8845 | 11.7893 | 11.6738 | 11.3862 | 11.0593 | 10.6733 | 10.2204 | 9.6801 | 8.845 | 7.0076 | 2.1755 | -6.9614 | -10.1741 | -12.5242 | 10.5815 | 10.4874 | 10.3746 | 9.9045 | 9.3931 | 8.8009 | 8.1284 | 7.3545 | 5.5366 | 2.7129 | -3.6483 | -16.1282 | -20.8911 | -24.0889
|  | PARK NORTH | LW |  |  | 10.5205 | 10.2017 | 9.8881 | 9.1602 | 8.4136 | 7.6464 | 6.8394 | 6.0053 | 4.9848 | 3.94 | 1.7594 | -3.8698 | -7.2432 | -9.3436 | 11.7685 | 11.6355 | 11.5048 | 11.2047 | 10.8899 | 10.5563 | 10.1902 | 9.8059 | 9.3339 | 8.8388 | 7.7888 | 5.182 | 3.4486 | 2.0761 | 10.2264 | 9.9565 | 9.6898 | 9.0686 | 8.4085 | 7.7226 | 6.9973 | 6.2465 | 5.3258 | 4.3799 | 2.4044 | -2.5369 | -5.511 | -7.4241
|  | PARK NORTH | ST |  |  | 11.1068 | 11.0914 | 11.0777 | 11.0215 | 10.9585 | 10.882 | 10.7802 | 10.6588 | 10.4818 | 10.2746 | 9.7489 | 6.5299 | 2.9947 | -0.81569 | 11.9572 | 11.911 | 11.8577 | 11.7648 | 11.6646 | 11.5479 | 11.4026 | 11.2461 | 11.0134 | 10.7489 | 10.0934 | 7.1993 | 3.3836 | -1.9101 | 10.7152 | 10.6995 | 10.6837 | 10.6218 | 10.5543 | 10.4725 | 10.362 | 10.2421 | 10.0647 | 9.8583 | 9.3011 | 6.3238 | 3.2053 | -0.18324
|  | PARK NORTH | FS |  |  | 10.945 | 10.8362 | 10.7069 | 10.1547 | 9.5576 | 8.8932 | 8.1554 | 7.3115 | 5.8836 | 3.3564 | -3.3486 | -16.6116 | -21.7387 | -25.1277 | 11.9609 | 11.9072 | 11.8476 | 11.7508 | 11.6446 | 11.5255 | 11.39 | 11.242 | 10.963 | 10.6551 | 9.9165 | 6.7725 | 0.9522 | -9 | 10.7204 | 10.7061 | 10.6911 | 10.6073 | 10.5201 | 10.4251 | 10.322 | 10.216 | 9.999 | 9.7751 | 9.2759 | 6.972 | 3.7395 | 0.24078
WILLESDEN GSP | ACTON LANE | PARK ROYAL | MINIMUM HEADROOM | TQ 20137 82215 | YES | -7.9596 | -7.9945 | -8.0364 | -8.0854 | -8.1436 | -8.2101 | -8.2866 | -8.3831 | -8.7233 | -9.2413 | -10.2071 | -9.2413 | -9.7093 | -10.2071 | -6.5071 | -6.5313 | -6.5636 | -6.6002 | -6.6417 | -6.6882 | -6.742 | -6.8066 | -7.0312 | -7.3796 | -7.9042 | -7.3796 | -7.6338 | -7.9042 | -6.6098 | -6.6373 | -6.6701 | -6.7085 | -6.7539 | -6.8058 | -6.8656 | -6.9862 | -7.4248 | -8.0426 | -8.7889 | -8.0426 | -8.3589 | -8.7889
|  | PARK ROYAL | CT |  |  | -7.9575 | -7.9898 | -8.0262 | -8.0681 | -8.1148 | -8.1671 | -8.223 | -8.2972 | -8.5634 | -9.1282 | -10.2071 | -9.1282 | -9.7093 | -10.2071 | -6.4982 | -6.5194 | -6.5455 | -6.575 | -6.6074 | -6.6434 | -6.6819 | -6.7345 | -6.9193 | -7.3203 | -7.9042 | -7.3203 | -7.6338 | -7.9042 | -6.6089 | -6.6347 | -6.6635 | -6.6966 | -6.7334 | -6.7748 | -6.8192 | -6.8774 | -7.1986 | -7.869 | -8.7889 | -7.869 | -8.3589 | -8.7889
|  | PARK ROYAL | LW |  |  | -7.9596 | -7.9945 | -8.0364 | -8.0854 | -8.1436 | -8.2101 | -8.2866 | -8.3831 | -8.7233 | -9.2413 | -9.9733 | -9.2413 | -9.6016 | -9.9733 | -6.5071 | -6.5313 | -6.5636 | -6.6002 | -6.6417 | -6.6882 | -6.742 | -6.8066 | -7.0312 | -7.3796 | -7.7681 | -7.3796 | -7.5858 | -7.7681 | -6.6098 | -6.6373 | -6.6701 | -6.7085 | -6.7539 | -6.8058 | -6.8656 | -6.9862 | -7.4248 | -8.0426 | -8.5841 | -8.0426 | -8.3554 | -8.5841
|  | PARK ROYAL | ST |  |  | -7.9153 | -7.9315 | -7.9519 | -7.9757 | -8.003 | -8.0347 | -8.0728 | -8.1223 | -8.3214 | -8.9039 | -9.6254 | -8.9039 | -9.3364 | -9.6254 | -6.4699 | -6.4802 | -6.4935 | -6.5089 | -6.5263 | -6.5463 | -6.5704 | -6.6012 | -6.723 | -7.0981 | -7.5617 | -7.0981 | -7.3762 | -7.5617 | -6.5762 | -6.5894 | -6.606 | -6.6253 | -6.6473 | -6.6727 | -6.703 | -6.7419 | -6.8992 | -7.5992 | -8.3658 | -7.5992 | -8.0793 | -8.3658
|  | PARK ROYAL | FS |  |  | -7.9575 | -7.9898 | -8.0262 | -8.0681 | -8.1148 | -8.1671 | -8.223 | -8.2972 | -8.5634 | -9.1282 | -10.2071 | -9.1282 | -9.7093 | -10.2071 | -6.4664 | -6.4748 | -6.486 | -6.4981 | -6.5109 | -6.5254 | -6.5406 | -6.5605 | -6.6316 | -6.8796 | -7.3294 | -6.8796 | -7.1586 | -7.3294 | -6.5724 | -6.5832 | -6.5959 | -6.6101 | -6.6254 | -6.6422 | -6.6604 | -6.6835 | -6.7683 | -7.1505 | -7.958 | -7.1505 | -7.6887 | -7.958
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH | MINIMUM HEADROOM | SZ 03222 92233 | YES | 4.2749 | 3.6094 | 3.109 | 1.9153 | 0.60301 | -0.79752 | -2.3062 | -3.8605 | -5.6011 | -7.3723 | -9.9803 | -17.0947 | -29.452 | -36.3237 | 10.5581 | 10.2433 | 10.0109 | 9.482 | 8.898 | 8.2348 | 7.4878 | 6.69 | 5.6056 | 4.436 | 2.3029 | -4.416 | -13.3962 | -33.0099 | 3.9769 | 3.4351 | 3.0097 | 2.0048 | 0.89988 | -0.2811 | -1.5582 | -2.874 | -4.3566 | -5.8654 | -8.1427 | -15.7111 | -27.4041 | -33.939
|  | PARKSTONE NORTH | CT |  |  | 4.7658 | 4.3958 | 4.1492 | 3.2285 | 2.2036 | 1.0652 | -0.14379 | -1.4218 | -3.2903 | -5.2453 | -8.415 | -17.0947 | -29.452 | -36.3237 | 10.6388 | 10.344 | 10.0903 | 9.5426 | 8.9281 | 8.2348 | 7.4878 | 6.69 | 5.6056 | 4.436 | 2.3029 | -4.416 | -12.5782 | -23.0976 | 4.4034 | 4.1165 | 3.9135 | 3.1451 | 2.2891 | 1.335 | 0.31627 | -0.76437 | -2.3663 | -4.048 | -6.8332 | -15.7111 | -27.4041 | -33.939
|  | PARKSTONE NORTH | LW |  |  | 4.2749 | 3.6094 | 3.109 | 1.9153 | 0.60301 | -0.79752 | -2.3062 | -3.8605 | -5.6011 | -7.3723 | -9.9803 | -15.3792 | -18.6846 | -20.4799 | 10.5581 | 10.2433 | 10.0109 | 9.482 | 8.898 | 8.2708 | 7.5882 | 6.8984 | 6.1249 | 5.3254 | 4.1145 | 1.7192 | 0.093806 | -1.089 | 3.9769 | 3.4351 | 3.0097 | 2.0048 | 0.89988 | -0.2811 | -1.5582 | -2.874 | -4.3566 | -5.8654 | -8.1427 | -12.9045 | -15.8435 | -17.5113
|  | PARKSTONE NORTH | ST |  |  | 5.0335 | 4.8032 | 4.698 | 4.3735 | 4.0005 | 3.5894 | 3.1712 | 2.7586 | 2.2564 | 1.7059 | 1.0064 | -1.927 | -5.094 | -9.2434 | 10.7516 | 10.5184 | 10.3272 | 9.996 | 9.6254 | 9.2131 | 8.7711 | 8.3214 | 7.7661 | 7.1542 | 6.0028 | 1.662 | -4.8776 | -15.5182 | 4.6408 | 4.4785 | 4.4014 | 4.1521 | 3.8668 | 3.5515 | 3.2272 | 2.9104 | 2.5085 | 2.0666 | 1.4598 | -1.1378 | -3.9956 | -7.7067
|  | PARKSTONE NORTH | FS |  |  | 4.7658 | 4.3958 | 4.1492 | 3.2285 | 2.2036 | 1.0652 | -0.14379 | -1.4218 | -3.2903 | -5.2453 | -8.415 | -17.0947 | -29.452 | -36.3237 | 10.7188 | 10.4278 | 10.175 | 9.765 | 9.2902 | 8.7735 | 8.1504 | 7.4552 | 6.5996 | 5.6545 | 3.7053 | -2.689 | -13.3962 | -33.0099 | 4.6 | 4.3978 | 4.2755 | 3.9468 | 3.5658 | 3.1651 | 2.6782 | 2.1424 | 1.4816 | 0.78077 | -0.41346 | -3.4701 | -6.4736 | -9.6715
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH | MINIMUM HEADROOM | SZ 04762 89848 | YES | 18.87 | 18.6027 | 18.28 | 17.6199 | 16.846 | 15.9174 | 13.8594 | 10.7154 | 6.7462 | 1.9001 | -9.7292 | -29.4606 | -35.3956 | -40.0166 | 19.6847 | 19.5559 | 19.3895 | 19.0696 | 18.4947 | 17.2429 | 15.4878 | 13.1366 | 10.1341 | 6.4409 | -2.4868 | -17.5782 | -22.2908 | -26.3174 | 17.6042 | 17.3515 | 17.0475 | 16.4347 | 15.7126 | 14.8411 | 12.7238 | 9.7305 | 5.9359 | 1.298 | -9.847 | -28.7604 | -34.6059 | -39.3205
|  | PARKSTONE SOUTH | CT |  |  | 19.1433 | 19.0215 | 18.8569 | 18.3666 | 17.7843 | 17.0846 | 16.242 | 15.2162 | 13.0874 | 10.1891 | 3.0925 | -16.0743 | -24.7791 | -26.4713 | 19.755 | 19.6568 | 19.5242 | 19.2518 | 18.9095 | 18.4764 | 17.8349 | 16.5304 | 14.8052 | 12.6437 | 7.2852 | -7.191 | -13.7139 | -15.0055 | 17.8629 | 17.7494 | 17.5972 | 17.1483 | 16.612 | 15.9646 | 15.1788 | 14.2053 | 11.9537 | 9.1803 | 2.3795 | -15.9897 | -24.372 | -26.0853
|  | PARKSTONE SOUTH | LW |  |  | 18.87 | 18.6027 | 18.28 | 17.6199 | 16.846 | 15.9174 | 13.8594 | 10.7154 | 6.7462 | 1.9001 | -9.7292 | -29.4606 | -35.3956 | -40.0166 | 19.6847 | 19.5559 | 19.3895 | 19.0696 | 18.4947 | 17.2429 | 15.4878 | 13.1366 | 10.1341 | 6.4409 | -2.4868 | -17.5782 | -22.2908 | -26.3174 | 17.6042 | 17.3515 | 17.0475 | 16.4347 | 15.7126 | 14.8411 | 12.7238 | 9.7305 | 5.9359 | 1.298 | -9.847 | -28.7604 | -34.6059 | -39.3205
|  | PARKSTONE SOUTH | ST |  |  | 19.2894 | 19.2626 | 19.215 | 19.0315 | 18.8317 | 18.6075 | 18.3299 | 18.0207 | 17.588 | 17.0868 | 15.8486 | 10.9301 | 7.2611 | 4.7558 | 19.8211 | 19.7726 | 19.7065 | 19.5346 | 19.359 | 19.1597 | 18.9048 | 18.6329 | 18.2491 | 17.8097 | 16.6882 | 12.515 | 9.1418 | 6.5959 | 17.9983 | 17.9729 | 17.9288 | 17.7526 | 17.5681 | 17.3598 | 17.0928 | 16.8009 | 16.3737 | 15.8798 | 14.6265 | 9.7541 | 6.0564 | 3.6683
|  | PARKSTONE SOUTH | FS |  |  | 19.1433 | 19.0215 | 18.8569 | 18.3666 | 17.7843 | 17.0846 | 16.242 | 15.2162 | 13.0874 | 10.1891 | 3.0925 | -16.0743 | -24.7791 | -26.4713 | 19.7707 | 19.6938 | 19.5926 | 19.427 | 19.2288 | 18.9892 | 18.7015 | 18.3571 | 17.9391 | 17.4491 | 16.1845 | 11.3759 | 5.977 | 1.8638 | 17.9369 | 17.8845 | 17.8076 | 17.6126 | 17.3809 | 17.1031 | 16.7744 | 16.3788 | 15.8731 | 15.2874 | 13.7962 | 8.136 | 1.8809 | -2.2586
BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM | MINIMUM HEADROOM | SU 84770 68709 | YES | 8.8847 | 7.9795 | 6.0829 | 5.7982 | 5.2133 | 4.0446 | 2.5757 | 1.0499 | -0.56816 | -2.3201 | -6.2295 | -12.5128 | -21.4739 | -26.6503 | 8.3279 | 7.2581 | 4.9524 | 4.5371 | 4.0232 | 2.7902 | 1.2621 | -0.22985 | -1.7123 | -3.2501 | -6.5331 | -11.7499 | -19.1883 | -23.3187 | 7.8719 | 6.778 | 4.4301 | 4.0333 | 3.4965 | 2.1733 | 0.52415 | -1.1286 | -2.8238 | -4.6168 | -8.5209 | -14.7752 | -23.6423 | -28.6588
|  | PEACOCK FARM | CT |  |  | 8.9341 | 8.0543 | 6.1767 | 5.7982 | 5.2133 | 4.0446 | 2.5757 | 1.0499 | -0.56816 | -2.3201 | -6.2295 | -12.5128 | -14.2073 | -15.384 | 8.3417 | 7.2765 | 4.9537 | 4.5371 | 4.0232 | 2.7902 | 1.2621 | -0.22985 | -1.7123 | -3.2501 | -6.5331 | -11.7499 | -13.1358 | -14.0641 | 7.8814 | 6.7824 | 4.4301 | 4.0333 | 3.4965 | 2.1733 | 0.52415 | -1.1286 | -2.8238 | -4.6168 | -8.5209 | -14.7752 | -16.4713 | -17.625
|  | PEACOCK FARM | LW |  |  | 8.8847 | 7.9795 | 6.0829 | 5.8071 | 5.4441 | 4.3791 | 3.0829 | 1.8825 | 0.7651 | -0.37718 | -2.9823 | -11.7603 | -21.4739 | -26.6503 | 8.3279 | 7.2581 | 4.9524 | 4.6774 | 4.301 | 3.0952 | 1.6815 | 0.43248 | -0.66677 | -1.7351 | -4.0247 | -11.3852 | -19.1883 | -23.3187 | 7.8719 | 6.778 | 4.4505 | 4.1841 | 3.7614 | 2.4975 | 1.0036 | -0.34336 | -1.5625 | -2.7755 | -5.4474 | -14.1968 | -23.6423 | -28.6588
|  | PEACOCK FARM | ST |  |  | 8.981 | 8.1326 | 6.3054 | 6.0228 | 5.702 | 5.0027 | 4.1722 | 3.4173 | 2.7456 | 2.1178 | 0.88506 | -2.1189 | -3.6547 | -3.9013 | 8.3671 | 7.3237 | 5.0521 | 4.8122 | 4.5411 | 3.6996 | 2.7043 | 1.8105 | 1.0436 | 0.35649 | -0.89722 | -3.6686 | -5.1191 | -5.3738 | 7.9536 | 6.9228 | 4.6631 | 4.3882 | 4.081 | 3.2355 | 2.2266 | 1.3188 | 0.53659 | -0.17547 | -1.5446 | -4.6683 | -6.2525 | -6.4761
|  | PEACOCK FARM | FS |  |  | 8.9341 | 8.0543 | 6.1767 | 5.7982 | 5.2133 | 4.0446 | 2.5757 | 1.0499 | -0.56816 | -2.3201 | -6.2295 | -12.5128 | -14.2073 | -15.384 | 8.3706 | 7.3309 | 5.0636 | 4.9561 | 4.8186 | 4.0167 | 3.1025 | 2.2294 | 1.5103 | 0.89051 | -0.2562 | -2.2812 | -4.2426 | -5.5142 | 7.9556 | 6.9276 | 4.6722 | 4.5599 | 4.404 | 3.5861 | 2.6581 | 1.7714 | 1.0371 | 0.40327 | -0.78867 | -3.0901 | -5.292 | -6.6072
BRAMLEY (FLEE) | FERNHURST | PETERSFIELD | MINIMUM HEADROOM | SU 74173 23420 | YES | 7.2934 | 6.8167 | 6.3284 | 5.6301 | 4.6465 | 2.9457 | 0.64958 | -2.2697 | -5.8857 | -10.3655 | -22.6221 | -65.4337 | -97.9545 | -108.0327 | 11.3118 | 11.1068 | 10.8911 | 10.5625 | 10.1455 | 9.6402 | 7.9535 | 5.7807 | 3.1094 | -0.24133 | -9.5313 | -42.3969 | -67.4752 | -75.2268 | 8.0164 | 7.592 | 7.1553 | 6.5201 | 5.785 | 4.8215 | 2.6324 | -0.15323 | -3.592 | -7.8608 | -19.5634 | -60.5149 | -91.6341 | -101.2581
|  | PETERSFIELD | CT |  |  | 7.7779 | 7.5621 | 7.3331 | 6.8484 | 6.295 | 5.6817 | 5.0034 | 3.5826 | 1.6042 | -0.64185 | -5.9899 | -19.2716 | -27.3296 | -30.5616 | 11.4355 | 11.2713 | 11.0851 | 10.7904 | 10.4388 | 10.0277 | 9.5488 | 8.991 | 8.2301 | 7.085 | 3.2728 | -6.0962 | -11.5999 | -13.7826 | 8.4369 | 8.2493 | 8.0431 | 7.6073 | 7.1115 | 6.5552 | 5.9321 | 5.2221 | 3.5585 | 1.4406 | -3.6166 | -16.1442 | -23.6926 | -26.692
|  | PETERSFIELD | LW |  |  | 7.2934 | 6.8167 | 6.3284 | 5.6301 | 4.6465 | 2.9457 | 0.64958 | -2.2697 | -5.8857 | -10.3655 | -22.6221 | -65.4337 | -97.9545 | -108.0327 | 11.3118 | 11.1068 | 10.8911 | 10.5625 | 10.1455 | 9.6402 | 7.9535 | 5.7807 | 3.1094 | -0.24133 | -9.5313 | -42.3969 | -67.4752 | -75.2268 | 8.0164 | 7.592 | 7.1553 | 6.5201 | 5.785 | 4.8215 | 2.6324 | -0.15323 | -3.592 | -7.8608 | -19.5634 | -60.5149 | -91.6341 | -101.2581
|  | PETERSFIELD | ST |  |  | 8.0294 | 7.9462 | 7.8608 | 7.7008 | 7.5072 | 7.3062 | 7.0801 | 6.8424 | 6.5799 | 6.279 | 5.5533 | 2.154 | 0.16358 | -2.4516 | 11.5467 | 11.4464 | 11.3322 | 11.1524 | 10.9498 | 10.7278 | 10.4661 | 10.1914 | 9.9007 | 9.565 | 8.7417 | 5.8855 | 2.5102 | -2.6471 | 8.6509 | 8.5772 | 8.5002 | 8.344 | 8.1643 | 7.9749 | 7.7549 | 7.5263 | 7.2763 | 6.9867 | 6.2851 | 3.8586 | 1.7994 | -0.61535
|  | PETERSFIELD | FS |  |  | 7.7779 | 7.5621 | 7.3331 | 6.8484 | 6.295 | 5.6817 | 5.0034 | 3.5826 | 1.6042 | -0.64185 | -5.9899 | -19.2716 | -27.3296 | -30.5616 | 11.5175 | 11.3852 | 11.2352 | 11.0285 | 10.7847 | 10.5132 | 10.1754 | 9.7826 | 9.3266 | 8.8099 | 7.5485 | 3.0758 | -2.835 | -11.697 | 8.6344 | 8.5483 | 8.4556 | 8.2605 | 8.0365 | 7.7948 | 7.4977 | 7.15 | 6.7083 | 6.2044 | 5.0126 | 1.1092 | -2.2702 | -4.7616
IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE | MINIMUM HEADROOM | SU 98108 80286 | YES | 20.3492 | 19.1594 | 17.7477 | 15.8245 | 13.6621 | 9.5635 | 2.5935 | -5.5444 | -14.5289 | -24.9089 | -49.5494 | -90.7208 | -101.1902 | -108.4731 | 25.8438 | 25.3724 | 24.629 | 23.2464 | 21.0099 | 16.6841 | 10.7264 | 3.8542 | -3.4915 | -11.8125 | -31.3564 | -63.9833 | -72.2986 | -78.0854 | 21.58 | 20.9111 | 19.8004 | 18.2212 | 16.3691 | 11.6737 | 5.357 | -2.5962 | -11.4185 | -21.5406 | -45.4169 | -85.3429 | -95.5342 | -102.5829
|  | PETERSFIELD AVENUE | CT |  |  | 20.7159 | 19.8839 | 18.7671 | 17.2811 | 15.6266 | 12.8156 | 9.7722 | 6.9902 | 4.6206 | 2.6551 | -1.9053 | -15.6454 | -21.0502 | -22.0895 | 25.9497 | 25.6352 | 25.0874 | 24.5148 | 23.7086 | 21.4753 | 18.7046 | 15.7629 | 13.2054 | 10.8772 | 5.9815 | -4.6359 | -8.676 | -10.441 | 21.7416 | 21.3055 | 20.6428 | 19.4741 | 18.1065 | 15.311 | 12.2235 | 9.393 | 7.0095 | 5.0412 | -0.30906 | -13.02 | -18.2371 | -19.2356
|  | PETERSFIELD AVENUE | LW |  |  | 20.3492 | 19.1594 | 17.7477 | 15.8245 | 13.6621 | 9.5635 | 2.5935 | -5.5444 | -14.5289 | -24.9089 | -49.5494 | -90.7208 | -101.1902 | -108.4731 | 25.8438 | 25.3724 | 24.629 | 23.2464 | 21.0099 | 16.6841 | 10.7264 | 3.8542 | -3.4915 | -11.8125 | -31.3564 | -63.9833 | -72.2986 | -78.0854 | 21.58 | 20.9111 | 19.8004 | 18.2212 | 16.3691 | 11.6737 | 5.357 | -2.5962 | -11.4185 | -21.5406 | -45.4169 | -85.3429 | -95.5342 | -102.5829
|  | PETERSFIELD AVENUE | ST |  |  | 20.9048 | 20.1908 | 19.1902 | 18.1617 | 17.0692 | 15.0499 | 12.936 | 11.0556 | 9.7521 | 8.8069 | 7.336 | 4.4857 | 2.5474 | 0.72266 | 26.0213 | 25.7633 | 25.2814 | 24.7774 | 24.0641 | 22.134 | 19.9927 | 17.9297 | 16.4605 | 15.3692 | 13.5448 | 9.2935 | 4.2071 | -3.5092 | 21.828 | 21.46 | 20.8767 | 20.2637 | 19.4272 | 17.384 | 15.1878 | 13.2234 | 11.8205 | 10.7737 | 8.9926 | 6.219 | 4.2741 | 2.6032
|  | PETERSFIELD AVENUE | FS |  |  | 20.7159 | 19.8839 | 18.7671 | 17.2811 | 15.6266 | 12.8156 | 9.7722 | 6.9902 | 4.6206 | 2.6551 | -1.9053 | -15.6454 | -21.0502 | -22.0895 | 26.0332 | 25.7807 | 25.436 | 25.0226 | 24.5173 | 22.8609 | 20.9966 | 19.1417 | 17.5074 | 16.0272 | 13.2326 | 6.9036 | -2.0835 | -17.8194 | 21.8542 | 21.5066 | 21.0691 | 20.5585 | 19.9833 | 18.2683 | 16.3596 | 14.4429 | 12.9065 | 11.6713 | 9.5386 | 6.0897 | 3.5528 | 1.326
MANNINGTON GSP | SALISBURY | PETERSFINGER | MINIMUM HEADROOM | SU 15608 29334 | YES | 1.0758 | 0.77037 | 0.46718 | 0.056329 | -0.38368 | -0.86426 | -1.3988 | -1.9636 | -2.6607 | -3.4916 | -5.8533 | -9.7878 | -11.6929 | -12.9635 | 5.5089 | 5.3892 | 5.2702 | 5.092 | 4.8874 | 4.6015 | 4.2594 | 3.8849 | 3.3682 | 2.772 | 1.4902 | -1.6782 | -4.7137 | -9.8939 | 2.129 | 1.8717 | 1.6157 | 1.2606 | 0.88034 | 0.46203 | -0.0042626 | -0.49598 | -1.1613 | -2.2207 | -4.5934 | -8.2526 | -9.8803 | -11.1655
|  | PETERSFINGER | CT |  |  | 1.3755 | 1.2243 | 1.0614 | 0.74289 | 0.38111 | -0.029651 | -0.49025 | -0.98851 | -1.7954 | -2.6658 | -4.4711 | -8.6507 | -11.4399 | -12.9273 | 5.5679 | 5.4566 | 5.3297 | 5.1282 | 4.8874 | 4.6015 | 4.2594 | 3.8849 | 3.3682 | 2.772 | 1.4902 | -1.6782 | -4.7137 | -8.6595 | 2.3767 | 2.2452 | 2.1018 | 1.821 | 1.498 | 1.1273 | 0.70156 | 0.24118 | -0.48969 | -1.2965 | -2.979 | -6.7558 | -9.1702 | -10.4926
|  | PETERSFINGER | LW |  |  | 1.0758 | 0.77037 | 0.46718 | 0.056329 | -0.38368 | -0.86426 | -1.3988 | -1.9636 | -2.6607 | -3.4916 | -5.8533 | -9.7878 | -11.6929 | -12.9635 | 5.5089 | 5.3892 | 5.2702 | 5.092 | 4.8931 | 4.6655 | 4.4012 | 4.1192 | 3.7814 | 3.4176 | 2.3528 | -0.23257 | -1.3909 | -2.4826 | 2.129 | 1.8717 | 1.6157 | 1.2606 | 0.88034 | 0.46203 | -0.0042626 | -0.49598 | -1.1613 | -2.2207 | -4.5934 | -8.2526 | -9.8803 | -11.1655
|  | PETERSFINGER | ST |  |  | 1.5014 | 1.421 | 1.3357 | 1.1483 | 0.96084 | 0.76293 | 0.53114 | 0.32124 | 0.069366 | -0.19356 | -0.80743 | -3.2529 | -5.3086 | -7.6415 | 5.6227 | 5.5469 | 5.4608 | 5.2695 | 5.0863 | 4.8905 | 4.6494 | 4.4328 | 4.1685 | 3.8878 | 3.213 | 0.76195 | -2.3992 | -6.7991 | 2.4842 | 2.4151 | 2.3413 | 2.153 | 1.974 | 1.7876 | 1.5627 | 1.3684 | 1.1273 | 0.87702 | 0.28764 | -2.423 | -4.2438 | -6.0655
|  | PETERSFINGER | FS |  |  | 1.3755 | 1.2243 | 1.0614 | 0.74289 | 0.38111 | -0.029651 | -0.49025 | -0.98851 | -1.7954 | -2.6658 | -4.4711 | -8.6507 | -11.4399 | -12.9273 | 5.6366 | 5.5609 | 5.473 | 5.3338 | 5.1788 | 5.0044 | 4.809 | 4.598 | 4.3362 | 4.0478 | 3.3786 | 0.90425 | -2.9975 | -9.8939 | 2.5275 | 2.4794 | 2.4268 | 2.3037 | 2.1739 | 2.0332 | 1.8859 | 1.7348 | 1.5132 | 1.2806 | 0.79538 | -0.88545 | -2.6513 | -4.2961
MELKSHAM GSP | AMESBURY | PEWSEY | MINIMUM HEADROOM | SU 14710 59252 | YES | 7.1743 | 7.1665 | 7.1558 | 7.1225 | 7.0853 | 7.0434 | 6.9833 | 6.6272 | 6.1608 | 5.6226 | 4.3385 | 1.6973 | 0.27426 | -0.57796 | 10.3871 | 10.2907 | 10.1859 | 10.0904 | 9.9708 | 9.8191 | 9.6257 | 9.3857 | 9.0869 | 8.7021 | 7.8135 | 5.8834 | 4.6207 | 3.6029 | 6.9553 | 6.948 | 6.9374 | 6.8966 | 6.8546 | 6.8085 | 6.6662 | 6.3662 | 6.0182 | 5.6364 | 4.5454 | 2.0298 | 0.38918 | -1.0283
|  | PEWSEY | CT |  |  | 7.1743 | 7.167 | 7.1566 | 7.1375 | 7.1072 | 7.065 | 7.0028 | 6.9297 | 6.5298 | 5.975 | 4.73 | 2.1269 | 0.41115 | -0.45131 | 10.4375 | 10.3615 | 10.2765 | 10.1715 | 10.0395 | 9.8738 | 9.6621 | 9.4083 | 9.0911 | 8.7021 | 7.8135 | 5.8834 | 4.6207 | 3.6029 | 6.9558 | 6.9486 | 6.9382 | 6.9183 | 6.8866 | 6.8427 | 6.7773 | 6.636 | 6.2391 | 5.7994 | 4.8657 | 2.3696 | 0.75523 | -0.079499
|  | PEWSEY | LW |  |  | 7.1744 | 7.1665 | 7.1558 | 7.1362 | 7.1071 | 7.0658 | 7.0093 | 6.6272 | 6.1608 | 5.6226 | 4.3385 | 1.6973 | 0.27426 | -0.57796 | 10.3871 | 10.2907 | 10.1859 | 10.0904 | 9.9708 | 9.8191 | 9.6257 | 9.3857 | 9.0869 | 8.7296 | 7.8473 | 6.0779 | 5.1254 | 4.4012 | 6.9553 | 6.948 | 6.9374 | 6.9169 | 6.887 | 6.8448 | 6.6662 | 6.3662 | 6.0182 | 5.6364 | 4.5454 | 2.0298 | 0.38918 | -1.0283
|  | PEWSEY | ST |  |  | 7.1761 | 7.1709 | 7.1634 | 7.1225 | 7.0853 | 7.0434 | 6.9833 | 6.9278 | 6.8431 | 6.7485 | 5.9936 | 3.4543 | 1.9906 | 1.3644 | 10.4815 | 10.4314 | 10.3739 | 10.2607 | 10.1432 | 10.0072 | 9.8348 | 9.6502 | 9.4096 | 9.1319 | 8.4358 | 6.3927 | 5.0774 | 4.2638 | 6.9575 | 6.9523 | 6.9449 | 6.8966 | 6.8546 | 6.8085 | 6.742 | 6.6838 | 6.5925 | 6.4924 | 6.0198 | 3.5399 | 2.1001 | 1.4887
|  | PEWSEY | FS |  |  | 7.1743 | 7.167 | 7.1566 | 7.1375 | 7.1072 | 7.065 | 7.0028 | 6.9297 | 6.5298 | 5.975 | 4.73 | 2.1269 | 0.41115 | -0.45131 | 10.5004 | 10.4627 | 10.4205 | 10.3509 | 10.2755 | 10.1902 | 10.0951 | 9.9905 | 9.8656 | 9.7274 | 9.3789 | 8.0072 | 6.4671 | 5.1458 | 6.9601 | 6.9577 | 6.9544 | 6.9418 | 6.927 | 6.9082 | 6.8865 | 6.8632 | 6.8304 | 6.7933 | 6.6972 | 5.2499 | 3.5072 | 2.3863
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE | MINIMUM HEADROOM | SY 70169 99809 | YES | 2.1349 | 2.0043 | 1.8527 | 1.7032 | 1.3849 | 0.92966 | 0.27626 | -0.73734 | -2.0408 | -3.6585 | -7.5938 | -15.5439 | -18.0807 | -19.0572 | 2.285 | 2.2288 | 2.1575 | 2.0743 | 1.9543 | 1.7892 | 1.4438 | 0.65479 | -0.35609 | -1.6146 | -4.6819 | -10.8731 | -12.8265 | -13.582 | 2.9284 | 2.8916 | 2.8459 | 2.6809 | 2.3202 | 1.8158 | 1.0968 | 0.11832 | -1.1325 | -2.6857 | -6.4656 | -14.0981 | -16.5275 | -17.4635
|  | PIDDLETRENTHIDE | CT |  |  | 2.2201 | 2.145 | 2.0564 | 1.9502 | 1.8225 | 1.6546 | 1.4458 | 1.175 | 0.83333 | 0.42896 | -0.93872 | -3.842 | -4.8352 | -5.1936 | 2.3206 | 2.2928 | 2.2589 | 2.2182 | 2.1675 | 2.099 | 2.0122 | 1.8972 | 1.7535 | 1.3107 | 0.22056 | -2.0339 | -2.7867 | -3.1332 | 2.9523 | 2.9317 | 2.9005 | 2.8541 | 2.7858 | 2.6866 | 2.5462 | 2.2879 | 1.8596 | 1.3028 | -0.08963 | -2.9091 | -3.8813 | -4.2313
|  | PIDDLETRENTHIDE | LW |  |  | 2.1349 | 2.0043 | 1.8527 | 1.7032 | 1.3849 | 0.92966 | 0.27626 | -0.73734 | -2.0408 | -3.6585 | -7.5938 | -15.5439 | -18.0807 | -19.0572 | 2.285 | 2.2288 | 2.1575 | 2.0743 | 1.9543 | 1.7892 | 1.4438 | 0.65479 | -0.35609 | -1.6146 | -4.6819 | -10.8731 | -12.8265 | -13.582 | 2.9472 | 2.9201 | 2.8795 | 2.6809 | 2.3202 | 1.8158 | 1.0968 | 0.11832 | -1.1325 | -2.6857 | -6.4656 | -14.0981 | -16.5275 | -17.4635
|  | PIDDLETRENTHIDE | ST |  |  | 2.2523 | 2.2001 | 2.1405 | 2.0539 | 1.955 | 1.8381 | 1.6965 | 1.5241 | 1.3143 | 1.0591 | 0.33378 | -2.99 | -4.6576 | -4.6522 | 2.3342 | 2.3161 | 2.2948 | 2.2645 | 2.2287 | 2.1851 | 2.1311 | 2.0643 | 1.9824 | 1.8819 | 1.1832 | -1.4032 | -2.7369 | -2.7739 | 2.9544 | 2.9389 | 2.9168 | 2.8853 | 2.8409 | 2.7791 | 2.6943 | 2.5799 | 2.4307 | 2.116 | 1.1492 | -2.0611 | -3.6958 | -3.6766
|  | PIDDLETRENTHIDE | FS |  |  | 2.2201 | 2.145 | 2.0564 | 1.9502 | 1.8225 | 1.6546 | 1.4458 | 1.175 | 0.83333 | 0.42896 | -0.93872 | -3.842 | -4.8352 | -5.1936 | 2.3312 | 2.3061 | 2.2783 | 2.2433 | 2.2041 | 2.1495 | 2.0893 | 2.0056 | 1.9065 | 1.6101 | 0.94793 | -1.3614 | -3.5177 | -4.6323 | 2.9284 | 2.8916 | 2.8459 | 2.7926 | 2.7306 | 2.6352 | 2.5253 | 2.3596 | 2.0807 | 1.7014 | 0.87221 | -2.045 | -4.7203 | -6.0823
BRAMLEY (FLEE) | FERNHURST | PLAISTOW | MINIMUM HEADROOM | TQ 02071 29626 | YES | 8.8578 | 8.6359 | 8.3924 | 8.1845 | 7.9184 | 7.3735 | 6.2503 | 4.7429 | 2.8398 | 0.42993 | -6.0761 | -23.3998 | -34.2885 | -38.5076 | 9.5456 | 9.4528 | 9.3401 | 9.1892 | 8.9966 | 8.7111 | 7.883 | 6.7249 | 5.2504 | 3.3787 | -1.6906 | -15.2087 | -23.8155 | -27.2941 | 8.8063 | 8.618 | 8.4084 | 8.2221 | 7.9803 | 7.4046 | 6.3307 | 4.8873 | 3.0598 | 0.74553 | -5.5031 | -22.141 | -32.664 | -36.8284
|  | PLAISTOW | CT |  |  | 9.0295 | 8.9096 | 8.7717 | 8.6154 | 8.4356 | 8.2267 | 7.9671 | 7.658 | 7.248 | 6.7459 | 5.6286 | 3.4251 | 2.2229 | 1.5165 | 9.6037 | 9.5459 | 9.4751 | 9.3864 | 9.2732 | 9.1293 | 8.9365 | 8.7024 | 8.4055 | 8.0241 | 7.1657 | 5.4286 | 4.4879 | 3.6325 | 8.9494 | 8.8464 | 8.7258 | 8.5835 | 8.4142 | 8.2114 | 7.9515 | 7.6424 | 7.2442 | 6.7491 | 5.6485 | 3.4766 | 2.3112 | 1.5877
|  | PLAISTOW | LW |  |  | 8.8578 | 8.6359 | 8.3924 | 8.1845 | 7.9184 | 7.3735 | 6.2503 | 4.7429 | 2.8398 | 0.42993 | -6.0761 | -23.3998 | -34.2885 | -38.5076 | 9.5456 | 9.4543 | 9.3461 | 9.233 | 9.0795 | 8.7111 | 7.883 | 6.7249 | 5.2504 | 3.3787 | -1.6906 | -15.2087 | -23.8155 | -27.2941 | 8.8063 | 8.618 | 8.4084 | 8.2221 | 7.9803 | 7.4046 | 6.3307 | 4.8873 | 3.0598 | 0.74553 | -5.5031 | -22.141 | -32.664 | -36.8284
|  | PLAISTOW | ST |  |  | 9.0735 | 8.9786 | 8.8804 | 8.7042 | 8.529 | 8.3422 | 8.1212 | 7.8842 | 7.5815 | 7.2259 | 6.3207 | 3.4663 | 1.8129 | 1.3451 | 9.6166 | 9.5687 | 9.5142 | 9.3981 | 9.2837 | 9.1556 | 8.9904 | 8.816 | 8.581 | 8.3083 | 7.5921 | 5.2587 | 3.7841 | 3.1258 | 8.9839 | 8.9018 | 8.8149 | 8.6465 | 8.4798 | 8.299 | 8.078 | 7.8421 | 7.5375 | 7.1867 | 6.2896 | 3.4555 | 1.7833 | 1.2782
|  | PLAISTOW | FS |  |  | 9.0295 | 8.9096 | 8.7717 | 8.6154 | 8.4356 | 8.2267 | 7.9671 | 7.658 | 7.248 | 6.7459 | 5.6286 | 3.4251 | 2.2229 | 1.5165 | 9.5569 | 9.4528 | 9.3401 | 9.1892 | 8.9966 | 8.7771 | 8.457 | 8.0615 | 7.6089 | 7.0821 | 5.7664 | 1.9414 | -1.165 | -2.5399 | 8.9365 | 8.7993 | 8.6587 | 8.4501 | 8.1915 | 7.9071 | 7.5027 | 7.0101 | 6.4325 | 5.7626 | 4.0962 | -0.77073 | -4.6148 | -6.1846
MINETY GSP | STRATTON (2 X 90) | PLESSEY Swindon | MINIMUM HEADROOM | SU 16381 86720 | YES | 15.525 | 15.525 | 15.525 | 15.4532 | 15.3747 | 15.2679 | 15.1517 | 15.0544 | 14.9848 | 14.9127 | 14.7865 | 14.435 | 14.0427 | 13.552 | 14.4 | 14.4 | 14.4 | 14.3102 | 14.2121 | 14.0786 | 13.9333 | 13.8117 | 13.7248 | 13.6346 | 13.4768 | 13.0375 | 12.5472 | 11.9337 | 14.4 | 14.4 | 14.4 | 14.3102 | 14.2121 | 14.0786 | 13.9333 | 13.8117 | 13.7248 | 13.6346 | 13.4768 | 13.0375 | 12.5472 | 11.9337
|  | PLESSEY Swindon | CT |  |  | 15.525 | 15.525 | 15.525 | 15.5153 | 15.4981 | 15.4777 | 15.4409 | 15.4185 | 15.3991 | 15.356 | 15.2776 | 15.0599 | 14.8314 | 14.5786 | 14.4 | 14.4 | 14.4 | 14.3879 | 14.3664 | 14.3408 | 14.2948 | 14.2669 | 14.2426 | 14.1887 | 14.0908 | 13.8186 | 13.533 | 13.217 | 14.4 | 14.4 | 14.4 | 14.3879 | 14.3664 | 14.3408 | 14.2948 | 14.2669 | 14.2426 | 14.1887 | 14.0908 | 13.8186 | 13.533 | 13.217
|  | PLESSEY Swindon | LW |  |  | 15.525 | 15.525 | 15.525 | 15.454 | 15.3747 | 15.2679 | 15.1517 | 15.0544 | 14.9848 | 14.9127 | 14.7865 | 14.435 | 14.0427 | 13.552 | 14.4 | 14.4 | 14.4 | 14.3112 | 14.2121 | 14.0786 | 13.9333 | 13.8117 | 13.7248 | 13.6346 | 13.4768 | 13.0375 | 12.5472 | 11.9337 | 14.4 | 14.4 | 14.4 | 14.3112 | 14.2121 | 14.0786 | 13.9333 | 13.8117 | 13.7248 | 13.6346 | 13.4768 | 13.0375 | 12.5472 | 11.9337
|  | PLESSEY Swindon | ST |  |  | 15.525 | 15.525 | 15.525 | 15.4532 | 15.4046 | 15.3608 | 15.2943 | 15.2636 | 15.2224 | 15.1873 | 15.11 | 14.8873 | 14.5128 | 14.1162 | 14.4 | 14.4 | 14.4 | 14.3102 | 14.2495 | 14.1948 | 14.1116 | 14.0732 | 14.0217 | 13.9778 | 13.8813 | 13.6029 | 13.1347 | 12.639 | 14.4 | 14.4 | 14.4 | 14.3102 | 14.2495 | 14.1948 | 14.1116 | 14.0732 | 14.0217 | 13.9778 | 13.8813 | 13.6029 | 13.1347 | 12.639
|  | PLESSEY Swindon | FS |  |  | 15.525 | 15.525 | 15.525 | 15.5153 | 15.4981 | 15.4777 | 15.4409 | 15.4185 | 15.3991 | 15.356 | 15.2776 | 15.0599 | 14.8314 | 14.5786 | 14.4 | 14.4 | 14.4 | 14.3804 | 14.3608 | 14.3371 | 14.3135 | 14.2939 | 14.274 | 14.2548 | 14.2163 | 14.1931 | 14.1627 | 14.0134 | 14.4 | 14.4 | 14.4 | 14.3804 | 14.3608 | 14.3371 | 14.3135 | 14.2939 | 14.274 | 14.2548 | 14.2163 | 14.1931 | 14.1627 | 14.0134
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSY TITCHFIELD | MINIMUM HEADROOM | SU 53390 06922 | YES | 13.359 | 13.2131 | 13.0862 | 12.7011 | 12.33 | 11.944 | 11.5307 | 11.0994 | 10.3868 | 9.5858 | 7.9422 | 5.2039 | 3.5751 | 2.3819 | 13.0525 | 12.9406 | 12.8358 | 12.6702 | 12.5023 | 12.3243 | 12.1148 | 11.8897 | 11.58 | 11.2523 | 10.3818 | 9.0248 | 7.5934 | 5.9616 | 12.357 | 12.1583 | 11.9654 | 11.627 | 11.2962 | 10.9486 | 10.5712 | 10.1761 | 9.5805 | 8.8328 | 7.2988 | 4.7691 | 3.3182 | 2.2756
|  | PLESSY TITCHFIELD | CT |  |  | 13.3624 | 13.244 | 13.1234 | 13.0169 | 12.9043 | 12.7285 | 12.4922 | 12.1327 | 11.3734 | 10.5816 | 9.0451 | 5.5804 | 3.5751 | 2.3819 | 13.1042 | 13.0393 | 12.972 | 12.8474 | 12.7191 | 12.5682 | 12.3999 | 12.2047 | 11.8677 | 11.5131 | 10.8072 | 9.0248 | 7.5934 | 5.9616 | 12.5447 | 12.4554 | 12.3645 | 12.1541 | 11.9351 | 11.694 | 11.4274 | 11.1019 | 10.4005 | 9.6882 | 8.3207 | 5.1617 | 3.3182 | 2.2756
|  | PLESSY TITCHFIELD | LW |  |  | 13.359 | 13.2131 | 13.0862 | 12.7011 | 12.33 | 11.944 | 11.5307 | 11.0994 | 10.3868 | 9.5858 | 7.9422 | 5.2039 | 3.7085 | 2.8052 | 13.0525 | 12.9406 | 12.8358 | 12.6702 | 12.5023 | 12.3243 | 12.1148 | 11.8897 | 11.58 | 11.2523 | 10.3818 | 9.0531 | 8.2692 | 7.4408 | 12.357 | 12.1583 | 11.9654 | 11.627 | 11.2962 | 10.9486 | 10.5712 | 10.1761 | 9.5805 | 8.8328 | 7.2988 | 4.7691 | 3.3241 | 2.3467
|  | PLESSY TITCHFIELD | ST |  |  | 13.4352 | 13.3728 | 13.3049 | 13.2383 | 13.1633 | 13.0665 | 12.9411 | 12.7927 | 12.5936 | 12.3595 | 11.6496 | 9.5287 | 7.8472 | 6.3649 | 13.1356 | 13.0944 | 13.0505 | 13.0076 | 12.9631 | 12.9076 | 12.8364 | 12.757 | 12.6394 | 12.508 | 12.1541 | 10.3253 | 9.2294 | 7.3616 | 12.5951 | 12.5316 | 12.4719 | 12.4357 | 12.4025 | 12.3591 | 12.3018 | 12.2427 | 12.0841 | 11.7865 | 11.0006 | 8.5127 | 6.8585 | 5.4106
|  | PLESSY TITCHFIELD | FS |  |  | 13.3624 | 13.244 | 13.1234 | 13.0169 | 12.9043 | 12.7285 | 12.4922 | 12.1327 | 11.3734 | 10.5816 | 9.0451 | 5.5804 | 3.5751 | 2.3819 | 13.1372 | 13.0919 | 13.0444 | 12.9948 | 12.9447 | 12.8843 | 12.8122 | 12.7265 | 12.5939 | 12.4511 | 12.1258 | 10.7868 | 9.1073 | 6.5885 | 12.5867 | 12.5122 | 12.4403 | 12.3681 | 12.3006 | 12.2167 | 12.1117 | 11.979 | 11.7626 | 11.5367 | 11.0607 | 9.5984 | 7.7454 | 6.0577
LOVEDEAN GSP | WYMERING BSP | PORTCHESTER | MINIMUM HEADROOM | SU 62043 05575 | YES | 0.28891 | -0.056904 | -0.36016 | -1.0444 | -1.7809 | -2.5907 | -3.5 | -4.4949 | -5.7599 | -7.1451 | -10.2117 | -16.508 | -20.1826 | -22.7077 | 2.6808 | 2.5165 | 2.3723 | 2.037 | 1.6615 | 1.2239 | 0.70912 | 0.13436 | -0.59763 | -1.4386 | -3.3461 | -7.4471 | -11.2556 | -17.8069 | -2.5893 | -2.8921 | -3.1675 | -3.8082 | -4.499 | -5.2617 | -6.1189 | -7.0507 | -8.2359 | -9.5309 | -12.3798 | -18.4114 | -21.9075 | -24.5953
|  | PORTCHESTER | CT |  |  | 0.68459 | 0.54704 | 0.44559 | 0.00026536 | -0.49552 | -1.0506 | -1.678 | -2.3794 | -3.6237 | -4.9887 | -7.8704 | -14.8998 | -19.2417 | -21.7966 | 2.8112 | 2.7057 | 2.6096 | 2.3685 | 2.0833 | 1.7445 | 1.3341 | 0.8651 | 0.12143 | -0.74884 | -2.7013 | -7.4471 | -11.2556 | -15.6511 | -2.2282 | -2.3429 | -2.436 | -2.8376 | -3.2902 | -3.7988 | -4.3857 | -5.0431 | -6.191 | -7.4703 | -10.176 | -16.6884 | -20.7071 | -23.1725
|  | PORTCHESTER | LW |  |  | 0.28891 | -0.056904 | -0.36016 | -1.0444 | -1.7809 | -2.5907 | -3.5 | -4.4949 | -5.7599 | -7.1451 | -10.2117 | -16.508 | -20.1826 | -22.7077 | 2.6808 | 2.5165 | 2.3723 | 2.037 | 1.6615 | 1.2239 | 0.70912 | 0.13436 | -0.59763 | -1.4386 | -3.3461 | -7.138 | -9.5826 | -11.8509 | -2.5893 | -2.8921 | -3.1675 | -3.8082 | -4.499 | -5.2617 | -6.1189 | -7.0507 | -8.2359 | -9.5309 | -12.3798 | -18.4114 | -21.9075 | -24.5953
|  | PORTCHESTER | ST |  |  | 0.7828 | 0.69953 | 0.65558 | 0.52323 | 0.38326 | 0.21254 | -0.0135 | -0.26044 | -0.60964 | -1.0288 | -2.2729 | -7.4261 | -12.0159 | -15.5492 | 2.8533 | 2.7705 | 2.6994 | 2.5292 | 2.3601 | 2.1638 | 1.9053 | 1.6411 | 1.2253 | 0.73922 | -0.5502 | -5.2353 | -9.9742 | -14.7722 | -2.141 | -2.2081 | -2.2495 | -2.3968 | -2.5444 | -2.7204 | -2.9584 | -3.2334 | -3.6323 | -4.108 | -5.4069 | -10.472 | -14.9772 | -18.3733
|  | PORTCHESTER | FS |  |  | 0.68459 | 0.54704 | 0.44559 | 0.00026536 | -0.49552 | -1.0506 | -1.678 | -2.3794 | -3.6237 | -4.9887 | -7.8704 | -14.8998 | -19.2417 | -21.7966 | 2.876 | 2.7929 | 2.7237 | 2.615 | 2.5017 | 2.3645 | 2.207 | 2.0313 | 1.716 | 1.3586 | 0.4665 | -3.1882 | -9.1605 | -17.8069 | -2.1059 | -2.1631 | -2.1913 | -2.2971 | -2.3957 | -2.521 | -2.6604 | -2.8116 | -3.0968 | -3.4123 | -4.1859 | -7.48 | -11.7584 | -15.5745
CHICKERELL GSP | CHICKERELL BSP | PORTLAND | MINIMUM HEADROOM | SY 68307 73941 | YES | 6.9453 | 6.7197 | 6.4667 | 5.9908 | 5.4464 | 4.8402 | 4.1556 | 3.3928 | 2.4061 | 1.3344 | -0.99013 | -5.8941 | -8.0672 | -9.5215 | 9.6885 | 9.587 | 9.4682 | 9.2513 | 8.9919 | 8.6892 | 8.3306 | 7.9139 | 7.3684 | 6.7553 | 4.7862 | 1.0415 | -0.40646 | -1.7357 | 8.069 | 7.8704 | 7.6494 | 7.2314 | 6.7534 | 6.2175 | 5.6056 | 4.9192 | 4.0211 | 3.0393 | 0.89586 | -3.7347 | -5.7417 | -7.2794
|  | PORTLAND | CT |  |  | 7.227 | 7.1568 | 7.0572 | 6.7434 | 6.3823 | 5.9719 | 5.5183 | 5.005 | 4.1123 | 3.1558 | 1.1659 | -3.7466 | -7.2151 | -9.3056 | 9.7836 | 9.7312 | 9.6591 | 9.5015 | 9.3122 | 9.0857 | 8.8223 | 8.51 | 8.0149 | 7.4517 | 6.234 | 3.3271 | 0.99934 | -1.4778 | 8.3164 | 8.2549 | 8.1672 | 7.8959 | 7.5821 | 7.223 | 6.8166 | 6.3485 | 5.5444 | 4.6722 | 2.8512 | -1.6001 | -4.6564 | -6.5667
|  | PORTLAND | LW |  |  | 6.9453 | 6.7197 | 6.4667 | 5.9908 | 5.4464 | 4.8402 | 4.1556 | 3.3928 | 2.4061 | 1.3344 | -0.99013 | -5.8941 | -8.0672 | -9.5215 | 9.6885 | 9.587 | 9.4682 | 9.2513 | 8.9919 | 8.6892 | 8.3306 | 7.9139 | 7.3684 | 6.7553 | 4.7862 | 1.0415 | -0.40646 | -1.6866 | 8.069 | 7.8704 | 7.6494 | 7.2314 | 6.7534 | 6.2175 | 5.6056 | 4.9192 | 4.0211 | 3.0393 | 0.89586 | -3.7347 | -5.7417 | -7.2794
|  | PORTLAND | ST |  |  | 7.3064 | 7.2788 | 7.2289 | 7.1413 | 7.0285 | 6.8888 | 6.7373 | 6.5555 | 6.3332 | 6.0759 | 5.4184 | 2.5985 | 0.022291 | -2.4404 | 9.818 | 9.787 | 9.7412 | 9.6699 | 9.5824 | 9.4757 | 9.3525 | 9.207 | 9.004 | 8.7705 | 8.1677 | 5.8367 | 3.4588 | 0.87405 | 8.3894 | 8.3675 | 8.3277 | 8.2535 | 8.1601 | 8.0439 | 7.9161 | 7.7632 | 7.5665 | 7.3397 | 6.7572 | 4.211 | 1.7676 | -0.64921
|  | PORTLAND | FS |  |  | 7.227 | 7.1568 | 7.0572 | 6.7434 | 6.3823 | 5.9719 | 5.5183 | 5.005 | 4.1123 | 3.1558 | 1.1659 | -3.7466 | -7.2151 | -9.3056 | 9.8191 | 9.7895 | 9.7474 | 9.6821 | 9.6006 | 9.5084 | 9.4079 | 9.292 | 9.1022 | 8.8907 | 8.3749 | 6.3015 | 3.0019 | -1.7357 | 8.3924 | 8.3774 | 8.3482 | 8.2695 | 8.1722 | 8.0653 | 7.9542 | 7.8252 | 7.6262 | 7.4111 | 6.9115 | 4.8875 | 2.3725 | -0.089248
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH | MINIMUM HEADROOM | SZ 63405 99685 | YES | 24.1496 | 23.7047 | 23.1318 | 22.0206 | 20.8071 | 19.7694 | 18.6803 | 17.2426 | 15.9213 | 14.5808 | 11.9977 | 7.0248 | 5.4204 | 3.6273 | 26.2817 | 26.0407 | 25.7241 | 25.1903 | 24.4549 | 23.76 | 23.0159 | 22.1358 | 21.3639 | 20.5696 | 18.8922 | 14.5956 | 5.9827 | -10.1992 | 22.4896 | 22.1493 | 21.7114 | 20.7761 | 19.747 | 18.8105 | 17.8156 | 16.5689 | 15.4532 | 14.3183 | 12.1363 | 7.8469 | 4.6268 | 1.9315
|  | PORTSMOUTH | CT |  |  | 24.2943 | 23.9664 | 23.5166 | 22.6999 | 21.7918 | 21.0761 | 20.3143 | 19.2071 | 18.0044 | 16.727 | 14.275 | 11.0771 | 9.9717 | 9.4351 | 26.2817 | 26.0407 | 25.7241 | 25.2004 | 24.5775 | 24.0214 | 23.3919 | 22.5999 | 21.7612 | 20.8169 | 18.8922 | 14.6551 | 9.5814 | 1.1897 | 22.615 | 22.3715 | 22.0347 | 21.3932 | 20.6705 | 20.082 | 19.4339 | 18.5336 | 17.5599 | 16.5043 | 14.4861 | 11.6598 | 10.5763 | 9.9785
|  | PORTSMOUTH | LW |  |  | 24.1496 | 23.7047 | 23.1318 | 22.0206 | 20.8071 | 19.7694 | 18.6803 | 17.2426 | 15.9213 | 14.5808 | 11.9977 | 7.0248 | 5.4204 | 3.6273 | 26.3131 | 26.1109 | 25.8426 | 25.1903 | 24.4549 | 23.76 | 23.0159 | 22.1358 | 21.3639 | 20.5696 | 19.0324 | 15.8492 | 12.3337 | 9.9751 | 22.4896 | 22.1493 | 21.7114 | 20.7761 | 19.747 | 18.8105 | 17.8156 | 16.5689 | 15.4532 | 14.3183 | 12.1363 | 7.8469 | 4.6268 | 1.9315
|  | PORTSMOUTH | ST |  |  | 24.4348 | 24.207 | 23.8655 | 23.1373 | 22.4585 | 21.9972 | 21.5107 | 20.9094 | 20.2477 | 19.565 | 18.1812 | 16.3529 | 15.5412 | 14.5067 | 26.3383 | 26.1287 | 25.851 | 25.2203 | 24.635 | 24.143 | 23.5701 | 22.9692 | 22.3094 | 21.6201 | 20.1139 | 16.2763 | 10.9814 | 2.2222 | 22.7783 | 22.6231 | 22.371 | 21.7551 | 21.2148 | 20.8356 | 20.4096 | 19.9592 | 19.4561 | 18.9423 | 17.8825 | 16.235 | 15.3136 | 14.1988
|  | PORTSMOUTH | FS |  |  | 24.2943 | 23.9664 | 23.5166 | 22.6999 | 21.7918 | 21.0761 | 20.3143 | 19.2071 | 18.0044 | 16.727 | 14.275 | 11.0771 | 9.9717 | 9.4351 | 26.3553 | 26.1334 | 25.8555 | 25.3573 | 24.8163 | 24.3081 | 23.7492 | 23.0485 | 22.3618 | 21.618 | 19.9498 | 14.5956 | 5.9827 | -10.1992 | 22.8184 | 22.6856 | 22.5031 | 22.1096 | 21.713 | 21.3978 | 21.0799 | 20.646 | 20.2374 | 19.8147 | 18.9775 | 17.1346 | 16.0445 | 15.0446
BRAMLEY (ANDO-THAT) | ANDOVER BSP | PORTWAY | MINIMUM HEADROOM | SU 34402 46001 | YES | 11.6991 | 11.3227 | 10.9276 | 10.4012 | 9.9769 | 9.5494 | 9.0142 | 8.392 | 7.684 | 6.8545 | 4.7989 | -0.2354 | -2.678 | -2.9336 | 14.9238 | 14.532 | 14.1082 | 13.6869 | 13.4088 | 13.1543 | 12.8975 | 12.6229 | 12.0222 | 11.2877 | 9.4825 | 5.1329 | 3.2747 | 3.2402 | 13.4414 | 13.0472 | 12.6125 | 12.0048 | 11.5277 | 11.0479 | 10.5369 | 9.9909 | 9.3424 | 8.6282 | 6.9654 | 3.4115 | 1.6009 | 1.1499
|  | PORTWAY | CT |  |  | 11.7584 | 11.3256 | 10.9276 | 10.5534 | 10.3888 | 10.1157 | 9.7777 | 9.3283 | 8.7472 | 8.1393 | 6.499 | 2.9533 | 0.94873 | -0.15563 | 14.9842 | 14.532 | 14.1082 | 13.7134 | 13.6354 | 13.5034 | 13.3194 | 13.0866 | 12.7818 | 12.4599 | 11.5863 | 9.36 | 8.0446 | 6.936 | 13.5054 | 13.0593 | 12.6503 | 12.2632 | 12.1512 | 11.8461 | 11.4602 | 11.0022 | 10.2956 | 9.546 | 8.0107 | 4.766 | 2.9927 | 2.0226
|  | PORTWAY | LW |  |  | 11.6991 | 11.3227 | 10.9324 | 10.4012 | 9.9769 | 9.5494 | 9.0142 | 8.392 | 7.684 | 6.8545 | 4.7989 | -0.2354 | -2.678 | -2.9336 | 14.9238 | 14.5346 | 14.1307 | 13.6869 | 13.4088 | 13.1543 | 12.8975 | 12.6229 | 12.0222 | 11.2877 | 9.4825 | 5.1329 | 3.2747 | 3.2402 | 13.4414 | 13.0472 | 12.6125 | 12.0048 | 11.5277 | 11.0479 | 10.5369 | 9.9909 | 9.3424 | 8.6282 | 6.9654 | 3.4115 | 1.6009 | 1.1499
|  | PORTWAY | ST |  |  | 11.7995 | 11.3996 | 11.0353 | 10.6853 | 10.6174 | 10.519 | 10.3698 | 10.1276 | 9.8049 | 9.4264 | 8.5179 | 6.0656 | 5.1499 | 3.8228 | 15.0175 | 14.5917 | 14.1949 | 13.8155 | 13.7592 | 13.6728 | 13.5385 | 13.3917 | 13.194 | 12.9695 | 12.485 | 11.003 | 9.9124 | 9.045 | 13.5556 | 13.1489 | 12.7793 | 12.4194 | 12.3466 | 12.2411 | 12.0834 | 11.9067 | 11.6743 | 11.4055 | 10.7894 | 8.4483 | 6.7586 | 5.5729
|  | PORTWAY | FS |  |  | 11.7584 | 11.3256 | 10.9276 | 10.5534 | 10.3888 | 10.1157 | 9.7777 | 9.3283 | 8.7472 | 8.1393 | 6.499 | 2.9533 | 0.94873 | -0.15563 | 15.1141 | 14.8789 | 14.6262 | 14.3585 | 14.1936 | 14.0439 | 13.8969 | 13.7382 | 13.5567 | 13.3581 | 12.8985 | 11.8089 | 9.2841 | 7.3053 | 13.644 | 13.4224 | 13.1852 | 12.9302 | 12.7647 | 12.6097 | 12.4522 | 12.2792 | 12.0078 | 11.6831 | 10.9577 | 8.7364 | 6.3468 | 4.3096
IVER 132KV | LONGFORD | POYLE | MINIMUM HEADROOM | TQ 03425 75555 | YES | 7.0179 | 6.7994 | 6.4975 | 5.5048 | 4.0529 | 2.0109 | -0.87446 | -4.5517 | -8.9411 | -14.3159 | -27.8899 | -57.2223 | -72.0085 | -78.2737 | 9.9058 | 9.6563 | 9.3207 | 8.6823 | 7.5012 | 5.9324 | 3.7274 | 0.91406 | -2.5106 | -6.7133 | -17.2973 | -40.2578 | -51.9059 | -57.0196 | 9.4497 | 9.2207 | 8.9041 | 7.8552 | 6.3184 | 4.3009 | 1.467 | -2.1172 | -6.3484 | -11.5282 | -24.5833 | -52.8363 | -67.123 | -73.2734
|  | POYLE | CT |  |  | 7.1109 | 6.997 | 6.7806 | 6.5893 | 6.3352 | 5.8232 | 4.921 | 3.7304 | 2.2137 | 0.50088 | -3.2367 | -11.5322 | -14.7029 | -16.4961 | 10.0124 | 9.8927 | 9.6665 | 9.4618 | 9.1931 | 8.8013 | 8.2044 | 7.2657 | 6.1568 | 4.9252 | 2.245 | -4.0401 | -6.6741 | -8.8294 | 9.6175 | 9.5006 | 9.2648 | 8.9046 | 8.4403 | 7.7951 | 6.9305 | 5.8624 | 4.4663 | 2.8036 | -1.1501 | -8.8716 | -11.8534 | -13.5989
|  | POYLE | LW |  |  | 7.0179 | 6.7994 | 6.4975 | 5.5048 | 4.0529 | 2.0109 | -0.87446 | -4.5517 | -8.9411 | -14.3159 | -27.8899 | -57.2223 | -72.0085 | -78.2737 | 9.9058 | 9.6563 | 9.3207 | 8.6823 | 7.5012 | 5.9324 | 3.7274 | 0.91406 | -2.5106 | -6.7133 | -17.2973 | -40.2578 | -51.9059 | -57.0196 | 9.4497 | 9.2207 | 8.9041 | 7.8552 | 6.3184 | 4.3009 | 1.467 | -2.1172 | -6.3484 | -11.5282 | -24.5833 | -52.8363 | -67.123 | -73.2734
|  | POYLE | ST |  |  | 7.181 | 7.1237 | 6.9685 | 6.6939 | 6.4393 | 6.1509 | 5.7476 | 5.3519 | 4.5948 | 3.4458 | 0.2647 | -9.9848 | -15.8548 | -17.2674 | 10.0663 | 10.0172 | 9.8722 | 9.5735 | 9.2573 | 8.8935 | 8.3791 | 7.8569 | 7.2447 | 6.3757 | 3.9871 | -4.7877 | -10.0067 | -11.6115 | 9.671 | 9.5826 | 9.3933 | 9.0037 | 8.6106 | 8.1368 | 7.4635 | 6.7099 | 5.8536 | 4.833 | 1.9133 | -8.7066 | -14.7423 | -15.9958
|  | POYLE | FS |  |  | 7.1109 | 6.997 | 6.7806 | 6.5893 | 6.3352 | 5.8232 | 4.921 | 3.7304 | 2.2137 | 0.50088 | -3.2367 | -11.5322 | -14.7029 | -16.4961 | 10.0778 | 10.0411 | 9.9659 | 9.8513 | 9.6775 | 9.4565 | 9.1763 | 8.8416 | 8.4721 | 8.0363 | 6.5992 | 0.99541 | -5.7917 | -10.4259 | 9.686 | 9.6228 | 9.5162 | 9.3418 | 9.1009 | 8.8096 | 8.4237 | 7.9456 | 7.3987 | 6.7518 | 4.9984 | -1.6382 | -9.3529 | -13.568
MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON SE | MINIMUM HEADROOM | SU 16963 86368 | YES | 2.3437 | 1.8368 | 1.3975 | 0.57616 | -0.25805 | -1.2668 | -2.3052 | -3.4955 | -4.5562 | -5.9348 | -8.3115 | -12.6093 | -14.6541 | -16.1812 | 2.5424 | 2.1695 | 1.8684 | 1.29 | 0.63685 | -0.11257 | -0.88265 | -1.7263 | -2.4013 | -3.3571 | -4.9195 | -7.7528 | -9.5235 | -11.3588 | 1.8896 | 1.3575 | 0.99018 | 0.36839 | -0.26605 | -0.92732 | -1.71 | -2.744 | -3.7316 | -5.0252 | -7.3508 | -11.5067 | -13.4378 | -14.8953
|  | PRESSED STEEL SWINDON SE | CT |  |  | 2.5905 | 2.0527 | 1.7179 | 0.97377 | 0.26708 | -0.58819 | -1.3372 | -2.3313 | -3.3974 | -4.84 | -7.1748 | -11.9481 | -14.5148 | -16.1812 | 2.6566 | 2.2075 | 1.9464 | 1.3583 | 0.70789 | 0.062388 | -0.50624 | -1.2381 | -1.9191 | -2.9377 | -4.4692 | -7.6449 | -9.5235 | -11.3588 | 1.9469 | 1.3575 | 0.99018 | 0.36839 | -0.26605 | -0.92732 | -1.4159 | -2.1578 | -2.8024 | -4.013 | -6.2458 | -10.7626 | -13.079 | -14.6317
|  | PRESSED STEEL SWINDON SE | LW |  |  | 2.3437 | 1.8368 | 1.3975 | 0.57616 | -0.25805 | -1.2668 | -2.3052 | -3.4955 | -4.5562 | -5.9348 | -8.3115 | -12.6093 | -14.6541 | -16.1146 | 2.5424 | 2.1695 | 1.8684 | 1.29 | 0.63685 | -0.11257 | -0.88265 | -1.7263 | -2.4013 | -3.3571 | -4.9195 | -7.7528 | -9.0673 | -10.2298 | 1.8896 | 1.4525 | 1.0917 | 0.50099 | -0.12354 | -0.89958 | -1.71 | -2.744 | -3.7316 | -5.0252 | -7.3508 | -11.5067 | -13.4378 | -14.8953
|  | PRESSED STEEL SWINDON SE | ST |  |  | 2.65 | 2.1521 | 1.8647 | 1.3397 | 0.86893 | 0.2827 | -0.15743 | -0.80128 | -1.2702 | -2.0643 | -3.1514 | -6.6775 | -9.4387 | -11.1254 | 2.6848 | 2.2566 | 2.0218 | 1.5227 | 0.97635 | 0.45765 | 0.040773 | -0.50611 | -0.90264 | -1.592 | -2.5012 | -5.2702 | -7.6491 | -9.3987 | 1.962 | 1.3853 | 1.033 | 0.41976 | -0.19611 | -0.82304 | -1.267 | -1.9164 | -2.3571 | -3.109 | -3.9365 | -6.1065 | -8.7705 | -10.3407
|  | PRESSED STEEL SWINDON SE | FS |  |  | 2.5905 | 2.0527 | 1.7179 | 0.97377 | 0.26708 | -0.58819 | -1.3372 | -2.3313 | -3.3974 | -4.84 | -7.1748 | -11.9481 | -14.5148 | -16.1812 | 2.7383 | 2.5219 | 2.349 | 2.0528 | 1.7189 | 1.3687 | 1.0295 | 0.65051 | 0.26205 | -0.23818 | -1.1968 | -3.9415 | -7.5146 | -11.0569 | 2.0433 | 1.772 | 1.5402 | 1.1831 | 0.80589 | 0.4023 | 0.03523 | -0.39429 | -0.78353 | -1.2905 | -2.1823 | -4.4449 | -8.1309 | -10.7738
BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER | MINIMUM HEADROOM | SU 60879 41131 | YES | 8.3689 | 8.007 | 7.6321 | 7.2013 | 6.7494 | 6.3811 | 5.9213 | 4.9745 | 3.3551 | 1.4252 | -3.0637 | -11.6493 | -15.5905 | -17.8863 | 9.055 | 8.8758 | 8.6841 | 8.421 | 8.1154 | 7.8265 | 7.4662 | 6.6841 | 5.5408 | 3.9503 | 0.26773 | -6.6814 | -9.6565 | -11.4244 | 8.3053 | 8.0208 | 7.7211 | 7.35 | 6.9324 | 6.5594 | 6.0961 | 5.181 | 3.699 | 1.8354 | -2.5 | -10.7774 | -14.5388 | -16.7359
|  | PRESTON CANDOVER | CT |  |  | 8.466 | 8.1837 | 7.8665 | 7.4844 | 7.0439 | 6.684 | 6.1836 | 5.0406 | 3.3551 | 1.4252 | -3.0637 | -11.6493 | -15.5905 | -17.8863 | 9.0801 | 8.9217 | 8.7376 | 8.5096 | 8.2072 | 7.9392 | 7.562 | 6.7238 | 5.5408 | 3.9503 | 0.26773 | -6.6814 | -9.6565 | -11.4244 | 8.3809 | 8.1572 | 7.901 | 7.5829 | 7.1827 | 6.8431 | 6.3603 | 5.3258 | 3.699 | 1.8354 | -2.5 | -10.7774 | -14.5388 | -16.7359
|  | PRESTON CANDOVER | LW |  |  | 8.3689 | 8.007 | 7.6321 | 7.2013 | 6.7494 | 6.3811 | 5.9213 | 4.9745 | 3.9687 | 2.8344 | 0.22164 | -4.2619 | -5.3269 | -5.7464 | 9.055 | 8.8758 | 8.6841 | 8.421 | 8.1154 | 7.8265 | 7.4662 | 6.6841 | 5.8778 | 4.9683 | 2.8682 | -0.69511 | -1.4488 | -1.7433 | 8.3053 | 8.0208 | 7.7211 | 7.35 | 6.9324 | 6.5594 | 6.0961 | 5.181 | 4.2188 | 3.1287 | 0.60413 | -3.7368 | -4.7666 | -5.1688
|  | PRESTON CANDOVER | ST |  |  | 8.5424 | 8.3177 | 8.0719 | 7.7524 | 7.4406 | 7.2452 | 6.9946 | 6.3137 | 5.6113 | 4.87 | 3.1871 | -1.0137 | -2.6006 | -2.7191 | 9.1227 | 9.0007 | 8.8659 | 8.6574 | 8.4342 | 8.2883 | 8.092 | 7.5318 | 6.9691 | 6.3667 | 4.9862 | 1.5339 | 0.20452 | -0.098592 | 8.4428 | 8.2704 | 8.0806 | 7.808 | 7.5203 | 7.3365 | 7.0958 | 6.48 | 5.8298 | 5.1367 | 3.5424 | -0.50702 | -2.0484 | -2.1341
|  | PRESTON CANDOVER | FS |  |  | 8.466 | 8.1837 | 7.8665 | 7.4844 | 7.0439 | 6.684 | 6.1836 | 5.0406 | 3.3551 | 1.4252 | -3.0637 | -11.6493 | -15.5905 | -17.8863 | 9.1471 | 9.0354 | 8.9144 | 8.7655 | 8.615 | 8.4998 | 8.3671 | 8.0929 | 7.7855 | 7.4201 | 6.5279 | 3.5652 | 0.85348 | -0.56583 | 8.4886 | 8.339 | 8.1784 | 7.9726 | 7.7759 | 7.6323 | 7.4683 | 7.157 | 6.796 | 6.3715 | 5.3178 | 1.769 | -1.4564 | -3.0537
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN | MINIMUM HEADROOM | SY 74226 95039 | YES | 2.7845 | 2.6865 | 2.5718 | 2.4406 | 2.2726 | 2.0545 | 1.7732 | 1.4031 | 0.8408 | 0.12563 | -1.5208 | -5.0894 | -6.7562 | -7.6584 | 3.9289 | 3.8794 | 3.8175 | 3.7044 | 3.5599 | 3.3941 | 3.1211 | 2.7929 | 2.3569 | 1.775 | 0.4435 | -2.488 | -3.9295 | -4.9128 | 3.1473 | 3.0695 | 2.9735 | 2.8532 | 2.6924 | 2.4655 | 2.122 | 1.7012 | 1.14 | 0.40918 | -1.2689 | -4.8629 | -6.5194 | -7.5095
|  | PUDDLETOWN | CT |  |  | 2.8345 | 2.7649 | 2.6778 | 2.5366 | 2.3537 | 2.1128 | 1.7924 | 1.4031 | 0.8408 | 0.12563 | -1.5208 | -5.0894 | -6.7562 | -7.6584 | 3.9405 | 3.8957 | 3.834 | 3.7315 | 3.5879 | 3.3941 | 3.1211 | 2.7929 | 2.3569 | 1.775 | 0.4435 | -2.488 | -3.9295 | -4.9128 | 3.1756 | 3.1144 | 3.033 | 2.8983 | 2.7141 | 2.4655 | 2.122 | 1.7012 | 1.14 | 0.40918 | -1.2689 | -4.8629 | -6.5194 | -7.5095
|  | PUDDLETOWN | LW |  |  | 2.7845 | 2.6865 | 2.5718 | 2.4406 | 2.2726 | 2.0545 | 1.7732 | 1.4193 | 0.94597 | 0.35242 | -1.0914 | -3.5883 | -4.9099 | -6.2621 | 3.9289 | 3.8794 | 3.8175 | 3.7326 | 3.6169 | 3.4584 | 3.2443 | 2.9656 | 2.589 | 2.1326 | 1.0158 | -0.90912 | -2.1483 | -3.5882 | 3.1473 | 3.0695 | 2.9735 | 2.8532 | 2.6924 | 2.4755 | 2.1869 | 1.8138 | 1.3206 | 0.72472 | -0.73627 | -3.2516 | -4.6802 | -6.2394
|  | PUDDLETOWN | ST |  |  | 2.8623 | 2.8108 | 2.7467 | 2.5842 | 2.4281 | 2.2517 | 2.0133 | 1.7679 | 1.4129 | 0.99584 | -0.058116 | -3.4831 | -5.7665 | -6.6692 | 3.9503 | 3.9117 | 3.8635 | 3.7044 | 3.5599 | 3.3986 | 3.1719 | 2.9498 | 2.6262 | 2.2706 | 1.3705 | -1.5534 | -3.6789 | -4.7446 | 3.1915 | 3.1414 | 3.0786 | 2.8988 | 2.7286 | 2.5346 | 2.2651 | 1.9872 | 1.5942 | 1.1533 | 0.033143 | -3.6107 | -6.0872 | -7.0951
|  | PUDDLETOWN | FS |  |  | 2.8345 | 2.7649 | 2.6778 | 2.5366 | 2.3537 | 2.1128 | 1.7924 | 1.4031 | 0.8408 | 0.12563 | -1.5208 | -5.0894 | -6.7562 | -7.6584 | 3.9558 | 3.9205 | 3.8771 | 3.8021 | 3.7167 | 3.6047 | 3.4791 | 3.3204 | 3.1145 | 2.8954 | 2.3824 | 0.65363 | -1.2284 | -2.5782 | 3.2027 | 3.1587 | 3.105 | 3.0119 | 2.9049 | 2.7653 | 2.6091 | 2.4082 | 2.1477 | 1.8706 | 1.2219 | -1.0289 | -3.4359 | -4.9924
AXMINSTER | YEOVIL BSP | PULHAM | MINIMUM HEADROOM | ST 71579 09451 | YES | -0.081387 | -0.2902 | -0.49846 | -0.62786 | -0.77029 | -0.91102 | -1.1239 | -1.3812 | -2.0995 | -3.1758 | -5.5921 | -9.9626 | -11.8645 | -13.4002 | 1.3426 | 1.2393 | 1.1364 | 1.0362 | 0.83802 | 0.62638 | 0.34506 | 0.11038 | -0.55257 | -1.4586 | -3.4535 | -7.1648 | -8.9034 | -10.4799 | 0.26111 | 0.077657 | -0.10536 | -0.21793 | -0.34539 | -0.61502 | -0.95256 | -1.3453 | -2.1695 | -3.2475 | -5.6469 | -10.0694 | -12.1037 | -13.8237
|  | PULHAM | CT |  |  | 0.050464 | -0.069031 | -0.18917 | -0.34433 | -0.53428 | -0.75975 | -1.0576 | -1.3741 | -2.0995 | -3.1758 | -5.5921 | -9.9626 | -11.8645 | -13.4002 | 1.3932 | 1.3383 | 1.2795 | 1.1877 | 1.0641 | 0.90979 | 0.5404 | 0.11038 | -0.55257 | -1.4586 | -3.4535 | -7.1648 | -8.9034 | -10.4799 | 0.37682 | 0.27343 | 0.16926 | 0.027455 | -0.14979 | -0.36007 | -0.71765 | -1.3453 | -2.1695 | -3.2475 | -5.6469 | -10.0694 | -12.1037 | -13.8237
|  | PULHAM | LW |  |  | -0.081387 | -0.2902 | -0.49846 | -0.62786 | -0.77029 | -0.91102 | -1.0814 | -1.2596 | -1.5075 | -1.7819 | -2.4035 | -4.6781 | -7.1011 | -9.4946 | 1.3426 | 1.2393 | 1.1364 | 1.0716 | 1.0027 | 0.93484 | 0.85252 | 0.74438 | 0.46058 | 0.13416 | -0.64207 | -2.4418 | -4.8158 | -7.4641 | 0.26111 | 0.077657 | -0.10536 | -0.21793 | -0.34131 | -0.46331 | -0.61028 | -0.76526 | -1.0044 | -1.3269 | -2.4134 | -4.6548 | -7.3044 | -10.0908
|  | PULHAM | ST |  |  | 0.094042 | 0.0014136 | -0.093584 | -0.3654 | -0.59264 | -0.83173 | -1.1239 | -1.3812 | -1.7609 | -2.127 | -2.875 | -5.0993 | -7.2158 | -8.916 | 1.3988 | 1.3455 | 1.2867 | 1.0362 | 0.83802 | 0.62638 | 0.34506 | 0.11575 | -0.2682 | -0.62844 | -1.3716 | -3.354 | -5.5526 | -7.5779 | 0.40064 | 0.30842 | 0.2114 | -0.093753 | -0.34539 | -0.61502 | -0.95256 | -1.2512 | -1.7025 | -2.1332 | -3.0184 | -5.3977 | -7.7921 | -9.8012
|  | PULHAM | FS |  |  | 0.050464 | -0.069031 | -0.18917 | -0.34433 | -0.53428 | -0.75975 | -1.0576 | -1.3741 | -2.0995 | -3.1758 | -5.5921 | -9.9626 | -11.8645 | -13.4002 | 1.4583 | 1.3912 | 1.3261 | 1.2218 | 1.1066 | 0.97845 | 0.82621 | 0.66406 | 0.45133 | 0.22012 | -0.26823 | -1.2453 | -1.9986 | -2.8412 | 0.48378 | 0.39265 | 0.30378 | 0.15985 | -0.00019516 | -0.17112 | -0.37245 | -0.586 | -0.86422 | -1.1693 | -1.8005 | -3.2704 | -4.293 | -5.2141
LOVEDEAN GSP | FORT WIDLEY | PURBROOK | MINIMUM HEADROOM | SU 67047 07819 | YES | 3.3206 | 3.1511 | 2.9688 | 2.5748 | 2.0786 | 1.5403 | 0.92135 | 0.22542 | -0.71876 | -1.7731 | -4.1811 | -9.1887 | -12.7433 | -15.0645 | 4.1092 | 4.0334 | 3.948 | 3.7717 | 3.5374 | 3.2647 | 2.932 | 2.5221 | 1.926 | 1.239 | -0.50228 | -4.7439 | -9.2367 | -12.8867 | 3.0946 | 2.9513 | 2.7923 | 2.4619 | 2.0412 | 1.5687 | 1.0088 | 0.35728 | -0.53624 | -1.5457 | -3.8574 | -8.7167 | -12.0912 | -14.6742
|  | PURBROOK | CT |  |  | 3.5352 | 3.4715 | 3.3911 | 3.1014 | 2.7201 | 2.2874 | 1.7743 | 1.1645 | 0.20282 | -0.92389 | -3.4217 | -9.1887 | -12.7433 | -15.0645 | 4.1709 | 4.1174 | 4.0478 | 3.8843 | 3.6605 | 3.3894 | 3.0468 | 2.6367 | 2.0169 | 1.239 | -0.50228 | -4.6202 | -7.6904 | -10.8167 | 3.2607 | 3.2006 | 3.124 | 2.8681 | 2.5315 | 2.139 | 1.6588 | 1.0897 | 0.19367 | -0.87777 | -3.2477 | -8.7167 | -12.0912 | -14.3851
|  | PURBROOK | LW |  |  | 3.3206 | 3.1511 | 2.9688 | 2.5748 | 2.0786 | 1.5403 | 0.92135 | 0.22542 | -0.71876 | -1.7731 | -4.1811 | -8.8799 | -11.7721 | -14.2336 | 4.1092 | 4.0334 | 3.948 | 3.7717 | 3.5374 | 3.2647 | 2.932 | 2.5221 | 1.926 | 1.239 | -0.35996 | -3.3927 | -5.661 | -8.0782 | 3.0946 | 2.9513 | 2.7923 | 2.4619 | 2.0412 | 1.5687 | 1.0088 | 0.35728 | -0.53624 | -1.5457 | -3.8574 | -8.2942 | -11.2416 | -13.9608
|  | PURBROOK | ST |  |  | 3.5349 | 3.4637 | 3.3815 | 3.1925 | 2.9454 | 2.6612 | 2.2865 | 1.8452 | 1.2603 | 0.58306 | -1.1527 | -6.7908 | -11.4046 | -14.3935 | 4.1529 | 4.084 | 4.0034 | 3.8328 | 3.629 | 3.3965 | 3.0779 | 2.716 | 2.1911 | 1.5976 | 0.086022 | -4.7439 | -9.2367 | -12.8867 | 3.2542 | 3.1845 | 3.1038 | 2.9149 | 2.6814 | 2.4124 | 2.0484 | 1.6243 | 1.0387 | 0.3677 | -1.3511 | -6.929 | -11.6224 | -14.6742
|  | PURBROOK | FS |  |  | 3.5352 | 3.4715 | 3.3911 | 3.1014 | 2.7201 | 2.2874 | 1.7743 | 1.1645 | 0.20282 | -0.92389 | -3.4217 | -9.1887 | -12.7433 | -15.0645 | 4.1616 | 4.0968 | 4.0194 | 3.9013 | 3.7442 | 3.5536 | 3.3167 | 3.0219 | 2.6045 | 2.1445 | 1.0616 | -2.324 | -6.4639 | -11.5296 | 3.2701 | 3.2122 | 3.1406 | 3.0046 | 2.8202 | 2.5971 | 2.3233 | 1.982 | 1.5162 | 1.0074 | -0.16987 | -3.7605 | -7.3009 | -10.0193
MINETY GSP | TOOTHILL BSP | QUARRY ROAD | MINIMUM HEADROOM | SU 15334 83380 | YES | 6.6102 | 6.1923 | 5.6929 | 4.9702 | 4.2043 | 3.3579 | 2.34 | 1.3396 | 0.34659 | -0.69894 | -3.11 | -8.1684 | -10.5311 | -12.6471 | 10.1051 | 9.847 | 9.4983 | 9.0462 | 8.616 | 8.0815 | 7.4734 | 6.8404 | 6.1103 | 5.2879 | 3.423 | -1.2033 | -5.9336 | -16.7284 | 5.8504 | 5.4562 | 4.9947 | 4.3257 | 3.6285 | 2.8481 | 1.9276 | 1.0319 | 0.11607 | -0.86995 | -3.1136 | -7.7764 | -9.9746 | -11.8652
|  | QUARRY ROAD | CT |  |  | 6.8623 | 6.5617 | 6.1443 | 5.5731 | 5.0094 | 4.3278 | 3.5299 | 2.7014 | 1.6628 | 0.53459 | -1.8644 | -7.3719 | -10.5251 | -12.6471 | 10.1495 | 9.8619 | 9.4983 | 9.0462 | 8.616 | 8.0815 | 7.4734 | 6.8404 | 6.1103 | 5.2879 | 3.423 | -1.2033 | -5.4195 | -11.3429 | 6.0926 | 5.8042 | 5.4316 | 4.8832 | 4.3624 | 3.7263 | 3.0086 | 2.2598 | 1.3047 | 0.26478 | -1.9461 | -7.0377 | -9.8943 | -11.8652
|  | QUARRY ROAD | LW |  |  | 6.6102 | 6.1923 | 5.6929 | 4.9702 | 4.2043 | 3.3579 | 2.34 | 1.3396 | 0.34659 | -0.69894 | -3.11 | -8.1684 | -10.5311 | -12.3214 | 10.1051 | 9.847 | 9.5345 | 9.1137 | 8.6778 | 8.1681 | 7.543 | 6.9446 | 6.3508 | 5.7045 | 4.1009 | 1.0262 | -0.43648 | -1.757 | 5.8504 | 5.4562 | 4.9947 | 4.3257 | 3.6285 | 2.8481 | 1.9276 | 1.0319 | 0.11607 | -0.86995 | -3.1136 | -7.7764 | -9.9746 | -11.7125
|  | QUARRY ROAD | ST |  |  | 7.0117 | 6.7946 | 6.4729 | 6.1781 | 5.9203 | 5.5989 | 5.2063 | 4.8521 | 4.5408 | 4.1792 | 3.2147 | -0.81387 | -3.7674 | -5.8889 | 10.2135 | 9.9717 | 9.6571 | 9.3282 | 9.0383 | 8.6771 | 8.2713 | 7.8893 | 7.5153 | 7.0878 | 5.9626 | 1.573 | -3.0505 | -8.7497 | 6.2368 | 6.0285 | 5.7502 | 5.464 | 5.2311 | 4.9234 | 4.5797 | 4.2731 | 3.9899 | 3.6436 | 2.6845 | -1.1917 | -4.0206 | -5.9603
|  | QUARRY ROAD | FS |  |  | 6.8623 | 6.5617 | 6.1443 | 5.5731 | 5.0094 | 4.3278 | 3.5299 | 2.7014 | 1.6628 | 0.53459 | -1.8644 | -7.3719 | -10.5251 | -12.6471 | 10.2366 | 10.0431 | 9.7984 | 9.5027 | 9.202 | 8.8598 | 8.4771 | 8.0703 | 7.6381 | 7.1655 | 5.9954 | 1.329 | -5.9336 | -16.7284 | 6.2712 | 6.136 | 5.9604 | 5.7069 | 5.464 | 5.1879 | 4.8903 | 4.5833 | 4.2783 | 3.9585 | 3.1561 | -0.15677 | -4.2089 | -7.4668
BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD | MINIMUM HEADROOM | SU 87062 55683 | YES | 2.8553 | 2.4908 | 2.2895 | 2.0273 | 1.7503 | 1.1619 | 0.37319 | -0.47781 | -1.3558 | -2.2002 | -3.0695 | -4.6669 | -5.56 | -6.1549 | 4.0348 | 3.8618 | 3.6824 | 3.5857 | 3.4403 | 3.1576 | 2.7672 | 2.3443 | 1.9256 | 1.5175 | 0.99976 | -0.4259 | -1.6745 | -4.5369 | 2.9359 | 2.6572 | 2.4493 | 2.2058 | 1.9439 | 1.4477 | 0.78938 | 0.079347 | -0.64881 | -1.3542 | -2.1311 | -3.5679 | -4.4439 | -4.9812
|  | QUEENSMEAD | CT |  |  | 2.9903 | 2.7344 | 2.5448 | 2.3779 | 2.2037 | 1.7121 | 1.0698 | 0.39213 | -0.43666 | -1.2747 | -2.3249 | -4.4451 | -5.56 | -6.1549 | 4.0581 | 3.9065 | 3.6824 | 3.5857 | 3.4778 | 3.218 | 2.8837 | 2.5133 | 2.0777 | 1.63 | 0.99976 | -0.4259 | -1.6745 | -3.3461 | 3.0539 | 2.8591 | 2.638 | 2.4905 | 2.334 | 1.9315 | 1.405 | 0.84458 | 0.15181 | -0.55092 | -1.4689 | -3.3313 | -4.3003 | -4.8141
|  | QUEENSMEAD | LW |  |  | 2.8553 | 2.4908 | 2.2895 | 2.0273 | 1.7503 | 1.1619 | 0.37319 | -0.47781 | -1.3558 | -2.2002 | -3.0695 | -4.6669 | -5.4831 | -5.8254 | 4.0348 | 3.8618 | 3.716 | 3.5862 | 3.4403 | 3.1576 | 2.7672 | 2.3443 | 1.9256 | 1.5175 | 1.0691 | 0.25845 | -0.16174 | -0.47343 | 2.9359 | 2.6572 | 2.4493 | 2.2058 | 1.9439 | 1.4477 | 0.78938 | 0.079347 | -0.64881 | -1.3542 | -2.1311 | -3.5679 | -4.4439 | -4.9812
|  | QUEENSMEAD | ST |  |  | 3.0713 | 2.8587 | 2.7156 | 2.6677 | 2.6226 | 2.3632 | 2.0302 | 1.7068 | 1.3854 | 1.0506 | 0.72028 | -0.28483 | -1.0221 | -1.9589 | 4.0901 | 3.9572 | 3.7537 | 3.6859 | 3.6193 | 3.4412 | 3.2149 | 2.9952 | 2.7811 | 2.5534 | 2.2352 | 1.1931 | 0.019489 | -1.8105 | 3.1213 | 2.9638 | 2.7826 | 2.7333 | 2.6886 | 2.4844 | 2.2206 | 1.9668 | 1.7171 | 1.4543 | 1.1739 | -0.035527 | -0.68475 | -1.1732
|  | QUEENSMEAD | FS |  |  | 2.9903 | 2.7344 | 2.5448 | 2.3779 | 2.2037 | 1.7121 | 1.0698 | 0.39213 | -0.43666 | -1.2747 | -2.3249 | -4.4451 | -5.56 | -6.1549 | 4.082 | 3.9552 | 3.8468 | 3.7593 | 3.659 | 3.4744 | 3.2461 | 2.996 | 2.734 | 2.4509 | 1.9866 | 0.42536 | -1.5409 | -4.5369 | 3.1148 | 2.9813 | 2.9003 | 2.8252 | 2.7399 | 2.5437 | 2.2949 | 2.0285 | 1.7415 | 1.4411 | 1.0326 | -0.22333 | -1.3498 | -2.2777
MELKSHAM GSP | WEST GRAFTON | RAMSBURY | MINIMUM HEADROOM | SU 27380 72108 | YES | 3.1994 | 3.0617 | 2.897 | 2.6452 | 2.3066 | 1.8622 | 1.2814 | 0.53437 | -0.38951 | -1.5161 | -4.3721 | -9.2948 | -10.8354 | -11.8187 | 4.2072 | 4.1278 | 4.025 | 3.8543 | 3.6188 | 3.2948 | 2.8593 | 2.2936 | 1.6075 | 0.75774 | -1.399 | -5.0643 | -6.4079 | -7.3599 | 3.0617 | 2.9335 | 2.7778 | 2.5337 | 2.2051 | 1.7697 | 1.1981 | 0.46276 | -0.43975 | -1.5487 | -4.3732 | -9.2025 | -10.6445 | -11.5864
|  | RAMSBURY | CT |  |  | 3.2781 | 3.1854 | 3.0622 | 2.8482 | 2.5555 | 2.1653 | 1.6394 | 0.93977 | -0.011704 | -1.1528 | -3.8423 | -9.0218 | -10.8354 | -11.8187 | 4.2275 | 4.157 | 4.0596 | 3.9071 | 3.6925 | 3.3967 | 2.9885 | 2.4462 | 1.7438 | 0.8896 | -1.1364 | -5.0261 | -6.4079 | -7.3599 | 3.1306 | 3.0418 | 2.9225 | 2.717 | 2.434 | 2.0537 | 1.5363 | 0.84188 | -0.08823 | -1.2081 | -3.8517 | -8.9311 | -10.6445 | -11.5864
|  | RAMSBURY | LW |  |  | 3.1994 | 3.0617 | 2.897 | 2.6452 | 2.3066 | 1.8622 | 1.2814 | 0.53437 | -0.38951 | -1.5161 | -4.3721 | -9.2948 | -10.7222 | -11.552 | 4.2072 | 4.1278 | 4.025 | 3.8543 | 3.6188 | 3.2948 | 2.8593 | 2.2936 | 1.6075 | 0.75774 | -1.399 | -5.0643 | -6.0537 | -6.6481 | 3.0617 | 2.9335 | 2.7778 | 2.5337 | 2.2051 | 1.7697 | 1.1981 | 0.46276 | -0.43975 | -1.5487 | -4.3732 | -9.2025 | -10.5708 | -11.377
|  | RAMSBURY | ST |  |  | 3.3175 | 3.2579 | 3.1854 | 3.0617 | 2.9123 | 2.7126 | 2.4403 | 2.0903 | 1.6532 | 1.1079 | -0.42917 | -5.9957 | -8.9174 | -9.0463 | 4.2466 | 4.1959 | 4.1326 | 4.0247 | 3.8981 | 3.7336 | 3.5077 | 3.2237 | 2.8827 | 2.4545 | 1.2492 | -3.0684 | -5.3658 | -5.5747 | 3.1662 | 3.1085 | 3.0376 | 2.9114 | 2.7615 | 2.5628 | 2.2904 | 1.9428 | 1.5116 | 0.97209 | -0.55026 | -6.0978 | -8.9645 | -9.0383
|  | RAMSBURY | FS |  |  | 3.2781 | 3.1854 | 3.0622 | 2.8482 | 2.5555 | 2.1653 | 1.6394 | 0.93977 | -0.011704 | -1.1528 | -3.8423 | -9.0218 | -10.8354 | -11.8187 | 4.2627 | 4.229 | 4.1863 | 4.1289 | 4.055 | 3.9646 | 3.851 | 3.7126 | 3.548 | 3.346 | 2.7535 | 0.00020293 | -3.5164 | -5.6285 | 3.1897 | 3.1573 | 3.1153 | 3.0465 | 2.9556 | 2.8481 | 2.7137 | 2.5527 | 2.3408 | 2.0852 | 1.3348 | -2.147 | -6.6376 | -9.2376
BRAMLEY (FLEE) | READING BSP | READING | MINIMUM HEADROOM | SU 74591 73788 | YES | 11.0742 | 10.7063 | 10.3167 | 9.4434 | 8.4208 | 7.2941 | 6.0212 | 2.5583 | -2.5309 | -8.5273 | -22.6028 | -49.3928 | -58.7107 | -63.7879 | 15.5664 | 15.3342 | 15.0445 | 14.5394 | 13.8909 | 13.0893 | 11.2744 | 8.4335 | 4.7379 | 0.31943 | -10.1605 | -29.5513 | -35.8321 | -43.8531 | 10.9708 | 10.6427 | 10.2939 | 9.5047 | 8.5862 | 7.5668 | 5.6406 | 2.0341 | -2.7924 | -8.4965 | -21.906 | -47.3052 | -56.035 | -60.8347
|  | READING | CT |  |  | 11.5279 | 11.3813 | 11.1825 | 10.4965 | 9.6596 | 8.6473 | 6.2938 | 2.5583 | -2.5309 | -8.5273 | -22.6028 | -49.3928 | -58.7107 | -63.7879 | 15.5664 | 15.3342 | 15.0445 | 14.5394 | 13.8909 | 13.0893 | 11.2744 | 8.4335 | 4.7379 | 0.31943 | -10.1605 | -29.5513 | -35.8321 | -39.5557 | 11.3645 | 11.2272 | 11.0399 | 10.4189 | 9.6626 | 8.3269 | 5.6406 | 2.0341 | -2.7924 | -8.4965 | -21.906 | -47.3052 | -56.035 | -60.8347
|  | READING | LW |  |  | 11.0742 | 10.7063 | 10.3167 | 9.4434 | 8.4208 | 7.2941 | 6.0212 | 4.6284 | 2.9234 | 1.1086 | -2.8031 | -10.8229 | -15.1635 | -17.6946 | 15.5889 | 15.448 | 15.2925 | 14.9366 | 14.4755 | 13.9323 | 13.2834 | 12.5528 | 11.6721 | 10.6931 | 8.4936 | 4.2825 | 2.0412 | 0.39714 | 10.9708 | 10.6427 | 10.2939 | 9.5047 | 8.5862 | 7.5668 | 6.4076 | 5.1344 | 3.5767 | 1.9058 | -1.7212 | -9.0373 | -12.9418 | -15.2931
|  | READING | ST |  |  | 11.6751 | 11.6242 | 11.5509 | 11.395 | 11.1759 | 10.8924 | 10.5401 | 10.1153 | 9.5996 | 9.0259 | 7.5652 | 1.1905 | -4.4004 | -9.1793 | 15.6206 | 15.4309 | 15.2013 | 14.873 | 14.4915 | 14.031 | 13.4662 | 12.8202 | 12.0661 | 11.219 | 9.1158 | 0.89535 | -9.2484 | -24.0962 | 11.4958 | 11.4457 | 11.3739 | 11.2132 | 11.005 | 10.7375 | 10.4 | 9.9937 | 9.4918 | 8.9293 | 7.4886 | 1.4229 | -3.7191 | -7.9671
|  | READING | FS |  |  | 11.5279 | 11.3813 | 11.1825 | 10.4965 | 9.6596 | 8.6473 | 6.2938 | 2.5583 | -2.5309 | -8.5273 | -22.6028 | -49.3928 | -58.7107 | -63.7879 | 15.6308 | 15.4294 | 15.1891 | 14.8634 | 14.4665 | 13.9924 | 13.4371 | 12.8122 | 12.0519 | 11.1896 | 9.0534 | 0.21107 | -15.8972 | -43.8531 | 11.5289 | 11.5083 | 11.4725 | 11.3647 | 11.2231 | 11.0486 | 10.8494 | 10.6326 | 10.2537 | 9.8469 | 8.8799 | 4.6849 | -0.80581 | -5.7969
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN | MINIMUM HEADROOM | SU 71540 74122 | YES | 54.3603 | 53.1751 | 51.9952 | 50.2694 | 48.5079 | 46.7421 | 44.8036 | 43.1493 | 41.3 | 39.1032 | 35.1257 | 27.8342 | 23.3856 | 20.7336 | 54.6408 | 53.4222 | 52.1007 | 51.0292 | 49.9164 | 48.7597 | 47.2772 | 46.1076 | 44.4697 | 42.3495 | 39.183 | 32.223 | 13.5346 | -18.1752 | 53.8785 | 52.5036 | 51.1011 | 49.6045 | 48.0699 | 46.4799 | 44.5848 | 43.173 | 41.5559 | 39.5471 | 35.7378 | 29.4378 | 26.2655 | 23.7678
|  | READING TOWN | CT |  |  | 54.4839 | 53.3099 | 52.1334 | 51.3827 | 50.0266 | 48.441 | 46.6731 | 45.0216 | 42.8349 | 40.2373 | 35.8212 | 27.8342 | 23.3856 | 20.7336 | 54.7817 | 53.4681 | 52.1007 | 51.1577 | 50.1854 | 48.8736 | 47.2772 | 46.1076 | 44.4697 | 42.3495 | 39.183 | 32.223 | 23.2709 | 7.0653 | 54.2307 | 53.0016 | 51.7256 | 50.6317 | 49.4803 | 48.0202 | 46.2911 | 44.8673 | 42.913 | 40.5334 | 36.3938 | 29.4378 | 26.2655 | 23.7678
|  | READING TOWN | LW |  |  | 54.3603 | 53.1751 | 51.9952 | 50.2694 | 48.5079 | 46.7421 | 44.8036 | 43.1493 | 41.3 | 39.1032 | 35.1257 | 29.5173 | 27.4997 | 26.0304 | 54.6408 | 53.4222 | 52.1652 | 51.0292 | 49.9164 | 48.7597 | 47.2863 | 46.446 | 45.4113 | 43.9967 | 42.0628 | 39.2926 | 38.0716 | 37.0331 | 53.8785 | 52.5036 | 51.1011 | 49.6045 | 48.0699 | 46.4799 | 44.5848 | 43.173 | 41.5559 | 39.5471 | 35.7378 | 30.1635 | 28.1315 | 26.5396
|  | READING TOWN | ST |  |  | 54.5904 | 53.4971 | 52.3827 | 51.6915 | 51.0361 | 50.1877 | 49.1816 | 48.5216 | 47.4431 | 46.002 | 43.7656 | 37.8333 | 34.2892 | 32.698 | 54.8951 | 53.6548 | 52.3659 | 51.5806 | 50.8125 | 49.7736 | 48.4916 | 47.7331 | 46.6198 | 45.062 | 42.9445 | 36.7375 | 26.8437 | 11.0546 | 54.4277 | 53.3286 | 52.1821 | 51.4329 | 50.7106 | 49.7876 | 48.6724 | 48.0046 | 47.0009 | 45.6471 | 43.4641 | 37.3032 | 33.8056 | 32.3041
|  | READING TOWN | FS |  |  | 54.4839 | 53.3099 | 52.1334 | 51.3827 | 50.0266 | 48.441 | 46.6731 | 45.0216 | 42.8349 | 40.2373 | 35.8212 | 27.8342 | 23.3856 | 20.7336 | 55.1693 | 54.2637 | 53.3001 | 52.3832 | 51.4527 | 50.4573 | 49.3157 | 48.2424 | 47.0621 | 45.6372 | 42.6991 | 32.8081 | 13.5346 | -18.1752 | 54.6355 | 53.8524 | 53.0536 | 52.2403 | 51.4254 | 50.5783 | 49.6254 | 48.7079 | 47.7191 | 46.5578 | 44.093 | 37.2799 | 30.8169 | 26.9459
MANNINGTON GSP | REDHILL BSP | REDHILL | MINIMUM HEADROOM | SZ 08512 96149 | YES | 13.2097 | 12.6577 | 11.9532 | 10.6819 | 9.2218 | 7.6304 | 6.0311 | 4.3149 | 0.84193 | -3.7185 | -14.9315 | -45.6444 | -64.5448 | -71.6065 | 16.0891 | 15.7477 | 15.3153 | 14.6285 | 13.8274 | 12.9224 | 12.026 | 11.0145 | 8.6578 | 5.3269 | -2.9826 | -25.797 | -39.838 | -45.0318 | 11.8671 | 11.3742 | 10.7568 | 9.6439 | 8.3681 | 6.9505 | 5.4996 | 3.9128 | 1.1485 | -3.1777 | -13.8458 | -43.0786 | -61.0526 | -67.7416
|  | REDHILL | CT |  |  | 13.6286 | 13.246 | 12.7294 | 11.6848 | 10.4564 | 9.0616 | 7.5031 | 4.6509 | 0.84193 | -3.7185 | -14.9315 | -45.6444 | -64.5448 | -71.6065 | 16.2134 | 15.8759 | 15.4497 | 14.7956 | 14.0112 | 13.0943 | 12.1853 | 11.0539 | 8.6578 | 5.3269 | -2.9826 | -25.797 | -39.838 | -45.0318 | 12.2329 | 11.8829 | 11.4228 | 10.4979 | 9.4034 | 8.1432 | 6.8544 | 4.7518 | 1.1485 | -3.1777 | -13.8458 | -43.0786 | -61.0526 | -67.7416
|  | REDHILL | LW |  |  | 13.2097 | 12.6577 | 11.9532 | 10.6819 | 9.2218 | 7.6304 | 6.0311 | 4.3149 | 2.3661 | 0.19444 | -4.6844 | -13.6736 | -17.1114 | -18.8265 | 16.0891 | 15.7477 | 15.3153 | 14.6285 | 13.8274 | 12.9224 | 12.026 | 11.0145 | 9.8667 | 8.5447 | 5.4364 | 0.048247 | -1.7813 | -2.8149 | 11.8671 | 11.3742 | 10.7568 | 9.6439 | 8.3681 | 6.9505 | 5.4996 | 3.9128 | 2.1152 | 0.096654 | -4.4894 | -12.7348 | -15.8707 | -17.3883
|  | REDHILL | ST |  |  | 13.7448 | 13.4454 | 13.0362 | 12.5546 | 11.9809 | 11.3581 | 10.8046 | 10.1548 | 9.4164 | 8.5113 | 6.2072 | -2.3272 | -8.2964 | -11.2366 | 16.2776 | 15.9922 | 15.6401 | 15.2438 | 14.7789 | 14.2672 | 13.8322 | 13.3216 | 12.7163 | 11.9841 | 10.124 | 3.4812 | -2.028 | -6.3896 | 12.3474 | 12.0788 | 11.7254 | 11.3101 | 10.8178 | 10.2793 | 9.8156 | 9.2691 | 8.6388 | 7.8631 | 5.8759 | -2.3562 | -7.9842 | -10.5109
|  | REDHILL | FS |  |  | 13.6286 | 13.246 | 12.7294 | 11.6848 | 10.4564 | 9.0616 | 7.5031 | 4.6509 | 0.84193 | -3.7185 | -14.9315 | -45.6444 | -64.5448 | -71.6065 | 16.325 | 16.1195 | 15.8518 | 15.5312 | 15.1592 | 14.7524 | 14.351 | 13.9067 | 13.3519 | 12.7282 | 11.23 | 5.7227 | -2.3268 | -12.5613 | 12.3942 | 12.2194 | 11.9762 | 11.6425 | 11.2531 | 10.8312 | 10.4231 | 9.9714 | 9.4087 | 8.7867 | 7.3332 | 2.0101 | -4.8702 | -9.8331
CHICKERELL GSP | CHICKERELL BSP | REDLANDS | MINIMUM HEADROOM | SY 67131 82321 | YES | 5.0196 | 4.7777 | 12.7881 | 12.2423 | 11.6248 | 10.9572 | 10.237 | 9.4487 | 7.9296 | 4.8776 | -2.8133 | -20.5649 | -33.0373 | -40.1426 | 6.4409 | 6.3395 | 13.9009 | 13.6715 | 13.4015 | 13.0961 | 12.7505 | 11.8309 | 10.1545 | 7.9371 | 2.2511 | -10.7225 | -19.841 | -25.1151 | 5.6658 | 5.4608 | 12.9125 | 12.4502 | 11.9257 | 11.353 | 10.7267 | 10.0333 | 8.3617 | 5.4699 | -1.8396 | -18.6799 | -30.507 | -37.2528
|  | REDLANDS | CT |  |  | 5.3128 | 5.2046 | 13.3408 | 12.9132 | 12.3974 | 11.7968 | 11.1005 | 10.2665 | 7.9296 | 4.8776 | -2.8133 | -20.5649 | -33.0373 | -40.1426 | 6.5173 | 6.4373 | 14.0099 | 13.7873 | 13.5083 | 13.1661 | 12.7507 | 11.8309 | 10.1545 | 7.9371 | 2.2511 | -10.7225 | -19.841 | -25.1151 | 5.9105 | 5.817 | 13.3731 | 13.0095 | 12.5692 | 12.0518 | 11.4443 | 10.7105 | 8.3617 | 5.4699 | -1.8396 | -18.6799 | -30.507 | -37.2528
|  | REDLANDS | LW |  |  | 5.0196 | 4.7777 | 12.7881 | 12.2423 | 11.6248 | 10.9572 | 10.237 | 9.4487 | 8.466 | 7.4248 | 5.1576 | 0.021126 | -5.4913 | -7.3611 | 6.4409 | 6.3395 | 13.9009 | 13.6715 | 13.4015 | 13.0961 | 12.7505 | 12.3559 | 11.8733 | 11.3387 | 10.1103 | 5.7516 | 1.4925 | 0.13809 | 5.6658 | 5.4608 | 12.9125 | 12.4502 | 11.9257 | 11.353 | 10.7267 | 10.0333 | 9.1681 | 8.2405 | 6.1919 | 1.4707 | -4.1153 | -5.8743
|  | REDLANDS | ST |  |  | 5.4246 | 5.3951 | 13.6212 | 13.5343 | 13.4142 | 13.2704 | 13.1215 | 12.9424 | 12.7468 | 12.5198 | 11.9432 | 9.3517 | 6.9679 | 4.6135 | 6.5753 | 6.5395 | 14.1677 | 14.0953 | 14.003 | 13.8927 | 13.7695 | 13.6245 | 13.4591 | 13.2636 | 12.7568 | 10.7186 | 8.7983 | 6.6894 | 6.0104 | 5.9872 | 13.6248 | 13.5534 | 13.4558 | 13.3385 | 13.216 | 13.068 | 12.9055 | 12.7151 | 12.2245 | 9.9318 | 7.779 | 5.6313
|  | REDLANDS | FS |  |  | 5.3128 | 5.2046 | 13.3408 | 12.9132 | 12.3974 | 11.7968 | 11.1005 | 10.2665 | 7.9296 | 4.8776 | -2.8133 | -20.5649 | -33.0373 | -40.1426 | 6.5619 | 6.5192 | 14.1397 | 14.0569 | 13.9556 | 13.8376 | 13.7001 | 13.5426 | 13.3222 | 13.0734 | 12.4472 | 9.9893 | 6.5747 | 2.3566 | 5.9974 | 5.9742 | 13.6128 | 13.5164 | 13.4023 | 13.2731 | 13.1232 | 12.9582 | 12.7061 | 12.4349 | 11.7816 | 9.2263 | 6.2293 | 3.6264
MANNINGTON GSP | SALISBURY | REDLYNCH | MINIMUM HEADROOM | SU 19073 20576 | YES | 1.8254 | 1.6536 | 1.4788 | 1.2312 | 0.96789 | 0.6983 | 0.20152 | -0.62781 | -1.7754 | -3.1806 | -6.8965 | -19.2779 | -25.5185 | -25.6538 | 3.9705 | 3.8688 | 3.7396 | 3.5439 | 3.2867 | 2.935 | 2.4674 | 1.8542 | 1.034 | -0.0034951 | -2.7829 | -12.1579 | -16.8317 | -16.9169 | 2.3956 | 2.255 | 2.1118 | 1.9061 | 1.6874 | 1.462 | 1.2159 | 0.59981 | -0.48945 | -1.8343 | -5.3902 | -17.2514 | -23.2363 | -23.4026
|  | REDLYNCH | CT |  |  | 2.0058 | 1.9213 | 1.8228 | 1.6218 | 1.3344 | 0.83931 | 0.20152 | -0.62781 | -1.7754 | -3.1806 | -6.8965 | -19.2779 | -25.5185 | -25.6538 | 3.9705 | 3.8688 | 3.7396 | 3.5439 | 3.2867 | 2.935 | 2.4674 | 1.8542 | 1.034 | -0.0034951 | -2.7829 | -12.1579 | -16.8317 | -16.9169 | 2.5425 | 2.4728 | 2.3917 | 2.2237 | 2.0329 | 1.8195 | 1.3909 | 0.59981 | -0.48945 | -1.8343 | -5.3902 | -17.2514 | -23.2363 | -23.4026
|  | REDLYNCH | LW |  |  | 1.8254 | 1.6536 | 1.4788 | 1.2312 | 0.96789 | 0.6983 | 0.4045 | 0.096171 | -0.28598 | -0.6886 | -1.685 | -3.6002 | -4.7747 | -5.572 | 3.9934 | 3.9126 | 3.835 | 3.7274 | 3.5958 | 3.4484 | 3.2479 | 3.0152 | 2.7325 | 2.4158 | 1.7293 | 0.65195 | -0.080784 | -0.83756 | 2.3956 | 2.255 | 2.1118 | 1.9061 | 1.6874 | 1.462 | 1.2159 | 0.94998 | 0.6064 | 0.24385 | -0.50103 | -2.0726 | -3.3384 | -4.2449
|  | REDLYNCH | ST |  |  | 2.0821 | 2.0395 | 1.9989 | 1.8897 | 1.7874 | 1.6797 | 1.5586 | 1.4519 | 1.3157 | 1.1791 | 0.87086 | -0.42888 | -1.6747 | -3.213 | 4.0834 | 4.0629 | 4.0393 | 3.9448 | 3.8608 | 3.7717 | 3.6549 | 3.5559 | 3.4139 | 3.2646 | 2.8977 | 1.8137 | 0.95272 | -0.32751 | 2.6085 | 2.5711 | 2.5352 | 2.424 | 2.3257 | 2.2244 | 2.1053 | 2.0079 | 1.8753 | 1.7447 | 1.4489 | 0.37748 | -0.93471 | -2.4095
|  | REDLYNCH | FS |  |  | 2.0058 | 1.9213 | 1.8228 | 1.6218 | 1.3344 | 0.83931 | 0.20152 | -0.62781 | -1.7754 | -3.1806 | -6.8965 | -19.2779 | -25.5185 | -25.6538 | 4.0855 | 4.0672 | 4.0442 | 3.9717 | 3.8658 | 3.736 | 3.5729 | 3.3636 | 3.1171 | 2.8604 | 2.3302 | 1.082 | 0.25487 | -0.61526 | 2.5813 | 2.5173 | 2.4426 | 2.3287 | 2.1947 | 2.0339 | 1.8401 | 1.5894 | 1.2676 | 0.93517 | 0.26283 | -1.3944 | -2.4685 | -3.3883
NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK | MINIMUM HEADROOM | SU 39267 13050 | YES | 15.73 | 15.4591 | 15.1531 | 14.7848 | 14.3758 | 13.9201 | 13.0722 | 12.0425 | 10.6604 | 8.8289 | 4.2706 | -5.1179 | -10.6509 | -10.9658 | 15.4177 | 15.0513 | 14.6474 | 14.4143 | 14.1355 | 13.7687 | 13.248 | 12.4465 | 11.2776 | 9.9368 | 6.6377 | -3.5634 | -10.1734 | -19.0391 | 15.1633 | 14.7976 | 14.4161 | 14.1436 | 13.6444 | 12.9561 | 11.9888 | 10.7773 | 9.3043 | 7.5193 | 3.0911 | -5.4615 | -10.9681 | -11.2936
|  | REGENTS PARK | CT |  |  | 15.8144 | 15.4969 | 15.1628 | 14.9539 | 14.6962 | 14.3692 | 13.8317 | 12.9398 | 11.5213 | 9.7531 | 5.6814 | -2.0821 | -4.755 | -6.5791 | 15.4408 | 15.1013 | 14.7188 | 14.4744 | 14.1687 | 13.7687 | 13.2524 | 12.5961 | 11.5678 | 10.1089 | 6.7127 | -0.24577 | -4.4489 | -10.0445 | 15.1633 | 14.7976 | 14.4161 | 14.2784 | 14.0541 | 13.507 | 12.6877 | 11.6183 | 10.1848 | 8.4616 | 4.5018 | -3.0512 | -5.693 | -7.5165
|  | REGENTS PARK | LW |  |  | 15.73 | 15.4591 | 15.1531 | 14.7848 | 14.3758 | 13.9201 | 13.0722 | 12.0425 | 10.6604 | 8.8289 | 4.2706 | -3.4159 | -5.7185 | -7.484 | 15.4177 | 15.187 | 14.9016 | 14.5842 | 14.2133 | 13.7876 | 13.248 | 12.5928 | 11.6043 | 10.2037 | 6.6932 | 0.87641 | -0.94525 | -2.5091 | 15.1651 | 14.9036 | 14.5839 | 14.1436 | 13.6444 | 12.9561 | 11.9888 | 10.7773 | 9.3043 | 7.5193 | 3.0911 | -4.3467 | -6.6513 | -8.4504
|  | REGENTS PARK | ST |  |  | 15.8578 | 15.5576 | 15.2461 | 15.1436 | 15.0152 | 14.849 | 14.1586 | 13.0938 | 11.7708 | 10.2355 | 6.4424 | -5.1179 | -10.6509 | -10.9658 | 15.4316 | 15.0513 | 14.6474 | 14.4143 | 14.1355 | 13.7839 | 13.3024 | 12.4465 | 11.2776 | 9.9368 | 6.6377 | -3.5634 | -10.1734 | -14.499 | 15.2068 | 14.8727 | 14.5234 | 14.3849 | 14.0368 | 13.5128 | 12.7609 | 11.7292 | 10.4727 | 9.0238 | 5.445 | -5.4615 | -10.9681 | -11.2936
|  | REGENTS PARK | FS |  |  | 15.8144 | 15.4969 | 15.1628 | 14.9539 | 14.6962 | 14.3692 | 13.8317 | 12.9398 | 11.5213 | 9.7531 | 5.6814 | -2.0821 | -4.755 | -6.5791 | 15.4816 | 15.3333 | 15.1322 | 14.9387 | 14.7267 | 14.5009 | 14.2296 | 13.9071 | 13.4892 | 12.9916 | 11.6085 | 4.4321 | -6.3106 | -19.0391 | 15.2397 | 15.1182 | 14.9597 | 14.8483 | 14.7356 | 14.6246 | 14.4926 | 14.3063 | 13.8963 | 13.3867 | 11.9349 | 5.6503 | -2.186 | -6.9011
COWLEY GSP | WITNEY BSP | RISSINGTON | MINIMUM HEADROOM | SP 19225 19563 | NO | 4.1158 | 3.9588 | 3.7972 | 3.5115 | 3.2768 | 3.0066 | 2.7396 | 2.4008 | 1.9494 | 1.5945 | 0.83646 | -3.1575 | -6.7706 | -8.7092 | 5.7277 | 5.6681 | 5.5934 | 5.3594 | 5.2306 | 5.0698 | 4.8694 | 4.5753 | 4.2104 | 3.8803 | 2.976 | -0.21372 | -2.9866 | -4.4758 | 4.4121 | 4.2678 | 4.1191 | 3.839 | 3.6256 | 3.3821 | 3.143 | 2.8343 | 2.4078 | 2.0883 | 1.1547 | -2.8914 | -6.4364 | -8.227
|  | RISSINGTON | CT |  |  | 4.2774 | 4.2029 | 4.1149 | 3.8105 | 3.6509 | 3.4786 | 3.282 | 3.0123 | 2.5665 | 2.2194 | 1.495 | -0.51515 | -1.7312 | -2.3846 | 5.7796 | 5.7438 | 5.7015 | 5.4974 | 5.4248 | 5.3423 | 5.2479 | 5.092 | 4.8479 | 4.6858 | 4.0356 | 2.6603 | 2.0755 | 1.8128 | 4.5585 | 4.4896 | 4.4075 | 4.0991 | 3.9539 | 3.7967 | 3.6227 | 3.3772 | 2.9576 | 2.6469 | 1.9941 | 0.040864 | -1.0608 | -1.5829
|  | RISSINGTON | LW |  |  | 4.1158 | 3.9588 | 3.7972 | 3.5115 | 3.2768 | 3.0066 | 2.7396 | 2.4008 | 1.9494 | 1.5945 | 0.83646 | -0.95708 | -1.9225 | -2.362 | 5.7277 | 5.6681 | 5.6061 | 5.4459 | 5.3401 | 5.2136 | 5.0898 | 4.9061 | 4.6533 | 4.415 | 3.6383 | 2.3377 | 1.9069 | 1.6452 | 4.4121 | 4.2678 | 4.1191 | 3.839 | 3.6256 | 3.3821 | 3.143 | 2.8343 | 2.4078 | 2.0883 | 1.4009 | -0.37783 | -1.0625 | -1.4366
|  | RISSINGTON | ST |  |  | 4.2655 | 4.1733 | 4.0711 | 3.764 | 3.585 | 3.3706 | 3.1136 | 2.7561 | 2.3187 | 1.9252 | 0.88139 | -3.1575 | -6.7706 | -8.7092 | 5.7389 | 5.6767 | 5.6018 | 5.3594 | 5.2306 | 5.0698 | 4.8694 | 4.5753 | 4.2104 | 3.8803 | 2.976 | -0.21372 | -2.9866 | -4.4758 | 4.5647 | 4.4814 | 4.3854 | 4.0983 | 3.9315 | 3.7302 | 3.4872 | 3.145 | 2.7152 | 2.2928 | 1.1547 | -2.8914 | -6.4364 | -8.227
|  | RISSINGTON | FS |  |  | 4.2774 | 4.2029 | 4.1149 | 3.8105 | 3.6509 | 3.4786 | 3.282 | 3.0123 | 2.5665 | 2.2194 | 1.495 | -0.51515 | -1.7312 | -2.3846 | 5.753 | 5.6766 | 5.5934 | 5.4387 | 5.3016 | 5.1352 | 4.9261 | 4.6341 | 4.2732 | 3.9253 | 3.2178 | 1.592 | 0.678 | 0.015687 | 4.5954 | 4.5077 | 4.4113 | 4.2183 | 4.0443 | 3.8396 | 3.5922 | 3.2493 | 2.7878 | 2.3382 | 1.43 | -0.70468 | -1.796 | -2.3436
BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE | MINIMUM HEADROOM | SU 47846 67187 | YES | 8.6952 | 8.4924 | 8.3587 | 8.2394 | 8.0856 | 7.7872 | 7.5087 | 7.1354 | 6.683 | 6.2083 | 5.0798 | 3.0777 | 2.4065 | 1.9762 | 10.5107 | 10.3945 | 10.3332 | 10.2876 | 10.2306 | 9.9753 | 9.8621 | 9.7191 | 9.5555 | 9.1758 | 8.1285 | 6.5834 | 6.2346 | 3.5536 | 8.6231 | 8.4616 | 8.3748 | 8.3156 | 8.2419 | 8.0567 | 7.9109 | 7.7028 | 7.2705 | 6.8163 | 5.7525 | 3.7328 | 3.1301 | 2.7423
|  | RIVERSIDE | CT |  |  | 8.7089 | 8.5414 | 8.4271 | 8.3036 | 8.1529 | 7.7872 | 7.5087 | 7.1354 | 6.683 | 6.2083 | 5.0798 | 3.0777 | 2.4065 | 1.9762 | 10.515 | 10.4171 | 10.3519 | 10.3072 | 10.25 | 9.9753 | 9.8621 | 9.7191 | 9.5555 | 9.1758 | 8.1285 | 6.5834 | 6.2346 | 5.7402 | 8.6385 | 8.5084 | 8.4278 | 8.3761 | 8.3091 | 8.0567 | 7.9244 | 7.7028 | 7.2705 | 6.8163 | 5.7525 | 3.7328 | 3.1301 | 2.7423
|  | RIVERSIDE | LW |  |  | 8.6952 | 8.4924 | 8.3587 | 8.2394 | 8.0856 | 7.8378 | 7.5431 | 7.2217 | 6.8678 | 6.4841 | 5.4732 | 3.7134 | 2.8798 | 2.4581 | 10.5107 | 10.3945 | 10.3332 | 10.2876 | 10.2306 | 10.0518 | 9.9111 | 9.783 | 9.6503 | 9.3957 | 8.4653 | 7.1068 | 6.5544 | 6.2612 | 8.6231 | 8.4616 | 8.3748 | 8.3156 | 8.2419 | 8.0699 | 7.9109 | 7.7538 | 7.4378 | 7.0696 | 6.1191 | 4.3459 | 3.5696 | 3.1765
|  | RIVERSIDE | ST |  |  | 8.744 | 8.6167 | 8.5489 | 8.5063 | 8.45 | 8.2404 | 8.0995 | 7.9438 | 7.7642 | 7.5486 | 6.8524 | 5.1228 | 4.6228 | 4.5048 | 10.5353 | 10.4598 | 10.4169 | 10.3826 | 10.3421 | 10.1033 | 10.0294 | 9.9549 | 9.8756 | 9.7833 | 9.4752 | 8.3772 | 7.9023 | 6.9465 | 8.6607 | 8.5576 | 8.5041 | 8.4689 | 8.4249 | 8.2197 | 8.1391 | 8.0585 | 7.9725 | 7.8716 | 7.4344 | 5.7914 | 5.3165 | 5.2122
|  | RIVERSIDE | FS |  |  | 8.7089 | 8.5414 | 8.4271 | 8.3036 | 8.1529 | 7.7872 | 7.5087 | 7.1354 | 6.683 | 6.2083 | 5.0798 | 3.0777 | 2.4065 | 1.9762 | 10.5553 | 10.4671 | 10.4165 | 10.3834 | 10.3459 | 10.2381 | 10.1684 | 10.0934 | 10.0172 | 9.9355 | 9.6511 | 8.3184 | 6.2513 | 3.5536 | 8.6912 | 8.5783 | 8.5203 | 8.484 | 8.4449 | 8.3484 | 8.2822 | 8.2107 | 8.1407 | 8.066 | 7.7651 | 6.5758 | 5.4215 | 4.7287
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE | MINIMUM HEADROOM | SU 11617 17810 | YES | 0.11896 | 0.0020627 | -0.18604 | -0.6227 | -1.2641 | -2.1905 | -3.5156 | -5.3425 | -7.6911 | -10.6087 | -17.5723 | -30.2571 | -33.7066 | -35.8535 | 0.47568 | 0.40785 | 0.31965 | 0.049131 | -0.44683 | -1.1674 | -2.2008 | -3.6295 | -5.468 | -7.7542 | -13.2141 | -23.1549 | -25.844 | -27.5275 | 0.11689 | 0.0098503 | -0.12215 | -0.54021 | -1.155 | -2.0439 | -3.3159 | -5.0704 | -7.3263 | -10.1292 | -16.82 | -29.0067 | -32.3176 | -34.3797
|  | ROCKBOURNE | CT |  |  | 0.17386 | 0.095353 | 0.0076194 | -0.11429 | -0.28106 | -0.50683 | -0.81091 | -1.2177 | -1.7402 | -2.3876 | -3.9213 | -6.5777 | -7.2866 | -7.5969 | 0.50126 | 0.45199 | 0.38988 | 0.30252 | 0.17978 | 0.0081173 | -0.23673 | -0.56757 | -0.9939 | -1.5173 | -2.7588 | -4.8988 | -5.4301 | -5.724 | 0.16634 | 0.092598 | 0.0082985 | -0.10948 | -0.27166 | -0.4927 | -0.79174 | -1.1927 | -1.7164 | -2.3578 | -3.8766 | -6.5377 | -7.203 | -7.5033
|  | ROCKBOURNE | LW |  |  | 0.11896 | 0.0020627 | -0.18604 | -0.6227 | -1.2641 | -2.1905 | -3.5156 | -5.3425 | -7.6911 | -10.6087 | -17.5723 | -30.2571 | -33.7066 | -35.8535 | 0.47568 | 0.40785 | 0.31965 | 0.049131 | -0.44683 | -1.1674 | -2.2008 | -3.6295 | -5.468 | -7.7542 | -13.2141 | -23.1549 | -25.844 | -27.5275 | 0.11689 | 0.0098503 | -0.12215 | -0.54021 | -1.155 | -2.0439 | -3.3159 | -5.0704 | -7.3263 | -10.1292 | -16.82 | -29.0067 | -32.3176 | -34.3797
|  | ROCKBOURNE | ST |  |  | 0.21761 | 0.18487 | 0.13946 | 0.077206 | 0.0082006 | -0.077849 | -0.18787 | -0.33654 | -0.51972 | -0.74852 | -1.3983 | -3.7769 | -4.991 | -4.9554 | 0.52808 | 0.50712 | 0.47846 | 0.43992 | 0.39302 | 0.33191 | 0.25075 | 0.14081 | 0.0038042 | -0.17879 | -0.71166 | -2.6601 | -3.6549 | -3.6499 | 0.20753 | 0.17698 | 0.13459 | 0.076371 | 0.010702 | -0.071979 | -0.17865 | -0.32308 | -0.50196 | -0.72664 | -1.3709 | -3.7321 | -4.9525 | -4.8964
|  | ROCKBOURNE | FS |  |  | 0.17386 | 0.095353 | 0.0076194 | -0.11429 | -0.28106 | -0.50683 | -0.81091 | -1.2177 | -1.7402 | -2.3876 | -3.9213 | -6.5777 | -7.2866 | -7.5969 | 0.50058 | 0.45666 | 0.40082 | 0.33449 | 0.2509 | 0.13827 | -0.012869 | -0.21392 | -0.44831 | -0.72227 | -1.417 | -3.7744 | -5.9074 | -6.8203 | 0.17927 | 0.12313 | 0.0486 | -0.04095 | -0.15151 | -0.29486 | -0.48087 | -0.72363 | -1.0145 | -1.3545 | -2.2074 | -5.1347 | -7.7854 | -8.8967
NURSLING GSP | ROWNHAMS | ROMSEY | MINIMUM HEADROOM | SU 36092 21110 | YES | 3.8071 | 3.2558 | 2.6242 | 1.5767 | 0.34279 | -1.4472 | -4.5704 | -8.7652 | -14.2257 | -20.8225 | -36.4443 | -63.3989 | -71.7297 | -77.6258 | 7.5466 | 7.1856 | 6.8354 | 6.2771 | 5.6008 | 4.859 | 2.8289 | -0.34064 | -4.4154 | -9.3992 | -21.2845 | -41.5561 | -47.5057 | -52.7087 | 3.174 | 2.5169 | 1.8504 | 0.84423 | -0.73207 | -2.93 | -5.9005 | -9.8934 | -15.0851 | -21.378 | -36.3006 | -62.0424 | -69.9766 | -75.916
|  | ROMSEY | CT |  |  | 4.1785 | 3.6721 | 3.2277 | 2.4463 | 0.87287 | -1.4472 | -4.5704 | -8.7652 | -14.2257 | -20.8225 | -36.4443 | -63.3989 | -71.7297 | -77.6258 | 7.6381 | 7.1856 | 6.8387 | 6.3783 | 5.7437 | 5.0187 | 2.8289 | -0.34064 | -4.4154 | -9.3992 | -21.2845 | -41.5561 | -47.5057 | -51.9865 | 3.174 | 2.5169 | 1.8504 | 0.84423 | -0.73207 | -2.93 | -5.9005 | -9.8934 | -15.0851 | -21.378 | -36.3006 | -62.0424 | -69.9766 | -75.6671
|  | ROMSEY | LW |  |  | 3.8071 | 3.2558 | 2.6242 | 1.5767 | 0.34279 | -1.0039 | -3.2732 | -6.4058 | -10.231 | -14.8174 | -26.1992 | -50.4266 | -67.3759 | -77.5934 | 7.5466 | 7.2001 | 6.8354 | 6.2771 | 5.6008 | 4.859 | 3.9787 | 1.8881 | -0.92067 | -4.3312 | -12.9081 | -31.2638 | -44.429 | -52.7087 | 3.1963 | 2.694 | 2.0128 | 0.95634 | -0.4763 | -2.2387 | -4.5876 | -7.5524 | -11.1808 | -15.5419 | -26.394 | -49.5485 | -65.8983 | -75.916
|  | ROMSEY | ST |  |  | 4.4115 | 4.0596 | 3.8078 | 3.4582 | 3.0212 | 2.6396 | 2.2208 | 1.7982 | 1.2814 | 0.73172 | -0.37406 | -3.4284 | -6.567 | -10.1951 | 7.7568 | 7.3913 | 7.159 | 6.8695 | 6.5103 | 6.2011 | 5.8442 | 5.4928 | 5.0492 | 4.5757 | 3.5417 | 0.38907 | -3.6409 | -9.2137 | 3.4126 | 3.0359 | 2.8432 | 2.6211 | 2.3445 | 2.1104 | 1.8277 | 1.5259 | 1.126 | 0.63137 | -0.56227 | -3.8015 | -6.2604 | -8.6344
|  | ROMSEY | FS |  |  | 4.1785 | 3.6721 | 3.2277 | 2.4463 | 0.87287 | -1.4472 | -4.5704 | -8.7652 | -14.2257 | -20.8225 | -36.4443 | -63.3989 | -71.7297 | -77.6258 | 7.6873 | 7.4385 | 7.1579 | 6.7893 | 6.3708 | 5.8989 | 5.366 | 4.7164 | 3.9337 | 3.098 | 1.358 | -3.6207 | -9.3392 | -17.7821 | 3.4099 | 3.2449 | 3.0791 | 2.8657 | 2.6268 | 2.3816 | 2.104 | 1.7072 | 0.81746 | -0.071555 | -1.8281 | -6.4073 | -9.9526 | -12.9554
LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN | MINIMUM HEADROOM | SZ 89974 99335 | YES | 5.1542 | 4.7268 | 4.2204 | 3.394 | 2.4774 | 1.5152 | 0.5912 | -0.52186 | -1.9734 | -3.674 | -11.2939 | -36.7208 | -58.2147 | -65.6597 | 8.9987 | 8.796 | 8.4547 | 8.0441 | 7.4183 | 6.6549 | 5.7075 | 4.4452 | 2.8057 | 0.74807 | -4.9538 | -24.2597 | -40.5253 | -46.091 | 5.1784 | 4.6911 | 4.1215 | 3.2493 | 2.2768 | 1.2412 | 0.22612 | -0.99045 | -2.5763 | -4.4242 | -8.8851 | -33.0903 | -53.6162 | -60.7203
|  | ROSE GREEN | CT |  |  | 5.2949 | 4.9825 | 4.5609 | 4.0003 | 3.3179 | 2.5174 | 1.726 | 0.72429 | -0.77192 | -2.5068 | -9.554 | -36.7208 | -58.2147 | -65.6597 | 8.9987 | 8.796 | 8.4547 | 8.0809 | 7.57 | 6.8784 | 6.0399 | 4.9084 | 3.4195 | 1.5412 | -3.7905 | -24.2597 | -40.5253 | -46.091 | 5.4415 | 5.1291 | 4.6856 | 3.9897 | 3.2214 | 2.3641 | 1.4959 | 0.39975 | -1.2567 | -3.17 | -7.6127 | -33.0903 | -53.6162 | -60.7203
|  | ROSE GREEN | LW |  |  | 5.1542 | 4.7268 | 4.2204 | 3.394 | 2.4774 | 1.5152 | 0.5912 | -0.52186 | -1.9734 | -3.674 | -11.2939 | -32.719 | -43.0105 | -44.545 | 9.0156 | 8.7975 | 8.4861 | 8.0441 | 7.4183 | 6.6549 | 5.7075 | 4.4452 | 2.8057 | 0.74807 | -4.9538 | -21.1946 | -28.9418 | -30.1441 | 5.1784 | 4.6911 | 4.1215 | 3.2493 | 2.2768 | 1.2412 | 0.22612 | -0.99045 | -2.5763 | -4.4242 | -8.8851 | -29.2668 | -39.11 | -40.6363
|  | ROSE GREEN | ST |  |  | 5.4121 | 5.1776 | 4.8616 | 4.5936 | 4.3476 | 4.1102 | 3.9389 | 3.7047 | 3.3957 | 3.0118 | 2.0461 | -8.3849 | -15.4154 | -17.999 | 9.1109 | 8.9901 | 8.7862 | 8.6139 | 8.4775 | 8.3384 | 8.2189 | 8.0599 | 7.8358 | 7.5809 | 6.1551 | -2.5209 | -8.0134 | -10.1208 | 5.5542 | 5.3156 | 4.973 | 4.677 | 4.399 | 4.1112 | 3.8778 | 3.552 | 3.1238 | 2.6222 | 1.3618 | -8.3225 | -15.1599 | -17.3216
|  | ROSE GREEN | FS |  |  | 5.2949 | 4.9825 | 4.5609 | 4.0003 | 3.3179 | 2.5174 | 1.726 | 0.72429 | -0.77192 | -2.5068 | -9.554 | -36.7208 | -58.2147 | -65.6597 | 9.1132 | 8.9898 | 8.831 | 8.6739 | 8.5154 | 8.3666 | 8.2301 | 8.0645 | 7.866 | 7.6403 | 5.6778 | -2.3847 | -11.7952 | -18.5768 | 5.5533 | 5.3202 | 5.0463 | 4.7469 | 4.4224 | 4.1104 | 3.802 | 3.427 | 2.9132 | 2.3414 | 0.96123 | -7.9466 | -19.0249 | -25.4748
COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL | MINIMUM HEADROOM | SP 53637 03027 | YES | 3.574 | 3.0768 | 2.4348 | 1.3571 | 0.015115 | -1.7873 | -3.8985 | -6.6952 | -11.7457 | -18.0166 | -33.0504 | -57.9916 | -64.5885 | -69.0743 | 7.2035 | 6.9108 | 6.3866 | 5.6757 | 4.9191 | 3.7718 | 2.2303 | -0.35905 | -4.2245 | -8.9394 | -20.2956 | -38.9894 | -43.7413 | -47.1302 | 4.7595 | 4.3172 | 3.7192 | 2.7518 | 1.5674 | -0.019726 | -1.9266 | -5.6315 | -10.5503 | -16.5162 | -30.8311 | -54.5886 | -60.8366 | -65.1101
|  | ROSE HILL | CT |  |  | 3.8254 | 3.4791 | 2.916 | 1.9118 | 0.7117 | -1.0519 | -3.1498 | -6.5673 | -11.7457 | -18.0166 | -33.0504 | -57.9916 | -64.5885 | -69.0743 | 7.2364 | 6.957 | 6.3866 | 5.6757 | 4.9191 | 3.7718 | 2.2303 | -0.35905 | -4.2245 | -8.9394 | -20.2956 | -38.9894 | -43.7413 | -47.1302 | 4.9738 | 4.6585 | 4.117 | 3.2073 | 2.1416 | 0.5694 | -1.6891 | -5.6315 | -10.5503 | -16.5162 | -30.8311 | -54.5886 | -60.8366 | -65.1101
|  | ROSE HILL | LW |  |  | 3.574 | 3.0768 | 2.4348 | 1.3571 | 0.015115 | -1.7873 | -3.8985 | -6.6952 | -9.7358 | -13.1959 | -21.9193 | -35.4275 | -39.0671 | -41.2977 | 7.2035 | 6.9108 | 6.4286 | 5.7653 | 5.0037 | 3.9747 | 2.6185 | 1.0185 | -0.79764 | -3.1597 | -9.1871 | -18.678 | -21.2625 | -22.9794 | 4.7595 | 4.3172 | 3.7192 | 2.7518 | 1.5674 | -0.019726 | -1.9266 | -4.4364 | -7.3625 | -10.7612 | -19.0118 | -31.8863 | -35.3939 | -37.5777
|  | ROSE HILL | ST |  |  | 3.9298 | 3.6791 | 3.2637 | 2.7213 | 2.1407 | 1.2433 | 0.10551 | -1.3245 | -2.8981 | -4.9303 | -10.4606 | -26.6734 | -35.3129 | -36.6035 | 7.3192 | 7.0838 | 6.6271 | 6.1504 | 5.7432 | 5.1242 | 4.2431 | 3.2683 | 2.129 | 0.56213 | -3.7938 | -17.335 | -25.8726 | -29.9821 | 5.0664 | 4.8389 | 4.4363 | 3.943 | 3.4444 | 2.7046 | 1.6327 | 0.22513 | -1.3644 | -3.3457 | -8.6542 | -24.8699 | -33.68 | -34.5605
|  | ROSE HILL | FS |  |  | 3.8254 | 3.4791 | 2.916 | 1.9118 | 0.7117 | -1.0519 | -3.1498 | -6.5673 | -11.7457 | -18.0166 | -33.0504 | -57.9916 | -64.5885 | -69.0743 | 7.4436 | 7.1899 | 6.8503 | 6.4318 | 5.984 | 5.3928 | 4.7042 | 3.8173 | 2.7549 | 1.4622 | -1.9468 | -13.5715 | -27.0799 | -39.3858 | 5.2032 | 4.9618 | 4.6578 | 4.2229 | 3.7248 | 3.0571 | 2.2254 | 1.018 | -0.349 | -1.9168 | -5.8161 | -18.5719 | -31.5076 | -38.2853
MELKSHAM GSP | CHIPPENHAM | ROWDEN | MINIMUM HEADROOM | ST 90805 72608 | YES | 6.4074 | 5.7627 | 5.0057 | 3.9577 | 2.9321 | 1.8675 | 0.7294 | -0.48299 | -1.8417 | -3.23 | -6.0856 | -16.8743 | -30.2765 | -37.6131 | 7.0681 | 6.7768 | 6.3996 | 5.9731 | 5.5811 | 5.1829 | 4.7435 | 4.1387 | 3.4856 | 2.8066 | 1.294 | -6.3063 | -16.0453 | -21.4899 | 5.8702 | 5.336 | 4.6922 | 3.8054 | 2.9415 | 2.0443 | 1.0839 | 0.060826 | -1.0876 | -2.2675 | -4.7082 | -15.7951 | -28.5088 | -35.4925
|  | ROWDEN | CT |  |  | 6.8347 | 6.4737 | 5.8393 | 5.0487 | 4.389 | 3.6096 | 2.7116 | 1.7177 | 0.23199 | -1.3095 | -4.3985 | -16.8743 | -30.2765 | -37.6131 | 7.19 | 6.982 | 6.5763 | 6.2362 | 5.9908 | 5.6918 | 5.326 | 4.7446 | 3.9363 | 3.067 | 1.294 | -6.3063 | -16.0453 | -21.4899 | 6.2429 | 5.9436 | 5.3877 | 4.7234 | 4.1784 | 3.5304 | 2.7745 | 1.9398 | 0.68717 | -0.62491 | -3.7688 | -15.7951 | -28.5088 | -35.4925
|  | ROWDEN | LW |  |  | 6.4074 | 5.7627 | 5.0057 | 3.9577 | 2.9321 | 1.8675 | 0.7294 | -0.48299 | -1.8417 | -3.23 | -6.0856 | -12.323 | -16.4508 | -17.4117 | 7.0681 | 6.7768 | 6.3996 | 5.9731 | 5.5811 | 5.1829 | 4.7435 | 4.1387 | 3.4856 | 2.8066 | 1.3754 | -2.687 | -5.5277 | -6.2285 | 5.8702 | 5.336 | 4.6922 | 3.8054 | 2.9415 | 2.0443 | 1.0839 | 0.060826 | -1.0876 | -2.2675 | -4.7082 | -11.3905 | -15.2939 | -16.2094
|  | ROWDEN | ST |  |  | 6.9319 | 6.6278 | 6.0598 | 5.5818 | 5.2834 | 4.915 | 4.4682 | 3.9801 | 3.4344 | 2.8846 | 1.8185 | -1.432 | -4.5953 | -8.2155 | 7.1932 | 6.9853 | 6.578 | 6.2388 | 6.0311 | 5.7764 | 5.4588 | 5.1281 | 4.7524 | 4.3787 | 3.6388 | 0.7286 | -2.4877 | -6.8254 | 6.3241 | 6.0737 | 5.5687 | 5.1398 | 4.8853 | 4.569 | 4.1762 | 3.7529 | 3.2668 | 2.7777 | 1.8243 | -1.1437 | -3.9953 | -7.2076
|  | ROWDEN | FS |  |  | 6.8347 | 6.4737 | 5.8393 | 5.0487 | 4.389 | 3.6096 | 2.7116 | 1.7177 | 0.23199 | -1.3095 | -4.3985 | -16.8743 | -30.2765 | -37.6131 | 7.2611 | 7.0822 | 6.8434 | 6.5949 | 6.3744 | 6.1497 | 5.9157 | 5.667 | 5.3879 | 5.0861 | 4.1989 | 1.2334 | -3.2275 | -10.0705 | 6.4068 | 6.1965 | 5.9149 | 5.578 | 5.2864 | 4.9848 | 4.6795 | 4.3537 | 3.9443 | 3.5115 | 2.5965 | -0.070696 | -3.1373 | -6.2399
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK | MINIMUM HEADROOM | SU 58018 00782 | YES | 19.5505 | 19.4084 | 19.2896 | 19.0321 | 18.7604 | 18.4698 | 18.148 | 17.7981 | 17.1757 | 15.6161 | 11.3963 | -3.1128 | -10.3133 | -10.2395 | 19.5165 | 19.4217 | 19.3555 | 19.2102 | 19.0571 | 18.8875 | 18.6682 | 18.3925 | 17.8863 | 16.7294 | 13.5541 | 2.5054 | -3.0037 | -2.9613 | 18.502 | 18.351 | 18.2284 | 17.9523 | 17.6643 | 17.3611 | 17.0305 | 16.6797 | 15.689 | 14.1985 | 10.1622 | -3.7298 | -10.6512 | -10.6238
|  | ROWNER PARK | CT |  |  | 19.6674 | 19.55 | 19.4939 | 19.2931 | 19.0711 | 18.817 | 18.5163 | 18.1599 | 17.1757 | 15.6161 | 11.3963 | -3.1128 | -10.3133 | -10.2395 | 19.5468 | 19.4238 | 19.3657 | 19.2335 | 19.0801 | 18.8951 | 18.6682 | 18.3925 | 17.8863 | 16.7294 | 13.5541 | 2.5054 | -3.0037 | -2.9613 | 18.6245 | 18.4964 | 18.4371 | 18.2193 | 17.9794 | 17.7056 | 17.3828 | 16.8899 | 15.689 | 14.1985 | 10.1622 | -3.7298 | -10.6512 | -10.6238
|  | ROWNER PARK | LW |  |  | 19.5505 | 19.4084 | 19.2896 | 19.0321 | 18.7604 | 18.4698 | 18.148 | 17.7981 | 17.373 | 16.9071 | 15.8776 | 13.8807 | 12.814 | 12.049 | 19.5165 | 19.4217 | 19.3555 | 19.2102 | 19.0571 | 18.8875 | 18.6939 | 18.4836 | 18.2195 | 17.9266 | 17.2803 | 16.0356 | 15.2126 | 14.444 | 18.502 | 18.351 | 18.2284 | 17.9523 | 17.6643 | 17.3611 | 17.0305 | 16.6797 | 16.2566 | 15.8015 | 14.8244 | 12.8981 | 11.8074 | 10.9698
|  | ROWNER PARK | ST |  |  | 19.7526 | 19.6626 | 19.6414 | 19.5949 | 19.5254 | 19.4419 | 19.2822 | 19.0826 | 18.8159 | 18.5053 | 17.7317 | 15.3018 | 13.2928 | 11.9713 | 19.587 | 19.4765 | 19.437 | 19.3688 | 19.2855 | 19.19 | 19.0369 | 18.8568 | 18.5969 | 18.2834 | 17.514 | 15.1572 | 12.7029 | 10.1674 | 18.7457 | 18.669 | 18.6701 | 18.6461 | 18.6071 | 18.5578 | 18.4499 | 18.276 | 18.0096 | 17.7015 | 16.9359 | 14.5625 | 12.5549 | 11.1877
|  | ROWNER PARK | FS |  |  | 19.6674 | 19.55 | 19.4939 | 19.2931 | 19.0711 | 18.817 | 18.5163 | 18.1599 | 17.1757 | 15.6161 | 11.3963 | -3.1128 | -10.3133 | -10.2395 | 19.592 | 19.5461 | 19.5112 | 19.4503 | 19.3842 | 19.3054 | 19.211 | 19.0993 | 18.9221 | 18.7163 | 18.1856 | 16.1645 | 13.1131 | 8.4936 | 18.7301 | 18.7173 | 18.7178 | 18.6691 | 18.6196 | 18.5572 | 18.4857 | 18.3979 | 18.2806 | 18.1438 | 17.7683 | 16.1489 | 14.3917 | 12.9764
FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE | MINIMUM HEADROOM | SZ 59554 91973 | YES | 9.772 | 9.226 | 8.6375 | 7.656 | 6.5835 | 5.5269 | 4.459 | 3.4536 | 2.1813 | 0.88006 | -1.7701 | -7.9613 | -12.8472 | -15.9849 | 13.1103 | 12.8746 | 12.6106 | 12.2245 | 11.7964 | 11.3756 | 10.9441 | 10.5354 | 10.0024 | 9.3315 | 7.6953 | 3.2129 | -1.4606 | -10.7221 | 9.28 | 8.8394 | 8.3601 | 7.5512 | 6.6676 | 5.791 | 4.8987 | 4.0449 | 2.9323 | 1.7924 | -0.53239 | -5.905 | -10.2542 | -13.0124
|  | RYDE | CT |  |  | 10.2528 | 9.9947 | 9.6493 | 8.9556 | 8.1786 | 7.3766 | 6.5642 | 5.7613 | 4.3342 | 2.8513 | -0.058401 | -7.5689 | -12.8472 | -15.9849 | 13.2257 | 13.0516 | 12.8166 | 12.4779 | 12.0919 | 11.6818 | 11.2509 | 10.8055 | 10.0986 | 9.3315 | 7.6953 | 3.2129 | -1.4606 | -7.3633 | 9.683 | 9.4816 | 9.2031 | 8.6332 | 7.9945 | 7.3292 | 6.6487 | 5.968 | 4.7574 | 3.4901 | 0.94163 | -5.6378 | -10.2542 | -13.0124
|  | RYDE | LW |  |  | 9.772 | 9.226 | 8.6375 | 7.656 | 6.5835 | 5.5269 | 4.459 | 3.4536 | 2.1813 | 0.88006 | -1.7701 | -7.9613 | -11.9198 | -13.998 | 13.1103 | 12.8746 | 12.6106 | 12.2245 | 11.7964 | 11.3756 | 10.9441 | 10.5354 | 10.0024 | 9.4261 | 8.2362 | 5.5017 | 3.6129 | 2.3307 | 9.28 | 8.8394 | 8.3601 | 7.5512 | 6.6676 | 5.791 | 4.8987 | 4.0449 | 2.9323 | 1.7924 | -0.53239 | -5.905 | -9.3918 | -11.2919
|  | RYDE | ST |  |  | 10.4672 | 10.3247 | 10.1029 | 9.9201 | 9.6917 | 9.4752 | 9.2592 | 9.0668 | 8.7845 | 8.4651 | 7.7424 | 4.5288 | 0.91512 | -3.5461 | 13.2902 | 13.1567 | 12.963 | 12.7861 | 12.5766 | 12.3584 | 12.1225 | 11.8829 | 11.55 | 11.1743 | 10.2833 | 6.9329 | 2.4897 | -3.9263 | 9.8682 | 9.7693 | 9.5972 | 9.458 | 9.2838 | 9.1148 | 8.9401 | 8.7791 | 8.5317 | 8.2509 | 7.5947 | 4.6533 | 1.3821 | -2.6049
|  | RYDE | FS |  |  | 10.2528 | 9.9947 | 9.6493 | 8.9556 | 8.1786 | 7.3766 | 6.5642 | 5.7613 | 4.3342 | 2.8513 | -0.058401 | -7.5689 | -12.8472 | -15.9849 | 13.3072 | 13.1691 | 12.9984 | 12.7988 | 12.5706 | 12.34 | 12.0987 | 11.8577 | 11.5002 | 11.1078 | 10.2025 | 6.7336 | 0.44079 | -10.7221 | 9.8715 | 9.78 | 9.6533 | 9.4682 | 9.2571 | 9.0611 | 8.8709 | 8.7038 | 8.4327 | 8.1549 | 7.5768 | 5.4146 | 2.5579 | -0.81969
MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL | MINIMUM HEADROOM | SU 14215 30481 | YES | 14.8565 | 14.3351 | 13.8972 | 13.0595 | 12.0452 | 10.7618 | 8.964 | 7.3563 | 5.8254 | 4.1975 | 0.66602 | -6.5037 | -12.06 | -15.556 | 19.8065 | 19.3324 | 19.2452 | 19.0203 | 18.472 | 18.0456 | 17.0105 | 16.0842 | 15.2947 | 14.3399 | 11.9835 | 6.0197 | 0.69695 | -9.1327 | 14.0247 | 13.4612 | 13.0451 | 12.2356 | 11.2093 | 10.0464 | 8.4765 | 7.03 | 5.654 | 4.183 | 0.97132 | -5.4458 | -10.2912 | -13.3028
|  | SALISBURY CENTRAL | CT |  |  | 15.183 | 14.8171 | 14.6762 | 14.2495 | 13.4351 | 12.4555 | 11.0709 | 9.8202 | 8.2137 | 6.488 | 2.8313 | -6.1524 | -12.06 | -15.556 | 19.8065 | 19.3324 | 19.2452 | 19.0203 | 18.472 | 18.1395 | 17.2605 | 16.3808 | 15.4118 | 14.3399 | 11.9835 | 6.0197 | 0.69695 | -5.8039 | 14.4448 | 13.964 | 13.8182 | 13.2507 | 12.3621 | 11.5232 | 10.3354 | 9.2253 | 7.7721 | 6.2064 | 2.8806 | -5.1442 | -10.2912 | -13.3028
|  | SALISBURY CENTRAL | LW |  |  | 14.8565 | 14.3351 | 13.8972 | 13.0595 | 12.0452 | 10.7618 | 8.964 | 7.3563 | 5.8254 | 4.1975 | 0.66602 | -6.5037 | -10.2647 | -12.2873 | 19.8304 | 19.5288 | 19.3978 | 19.1534 | 18.7092 | 18.0456 | 17.0105 | 16.0842 | 15.2947 | 14.4306 | 12.4875 | 8.8255 | 7.1292 | 6.127 | 14.0247 | 13.4612 | 13.0451 | 12.2356 | 11.2093 | 10.0464 | 8.4765 | 7.03 | 5.654 | 4.183 | 0.97132 | -5.4458 | -8.6825 | -10.3825
|  | SALISBURY CENTRAL | ST |  |  | 15.2883 | 15.0033 | 14.9409 | 14.7525 | 14.3397 | 13.9612 | 13.3701 | 12.8682 | 12.4331 | 11.9061 | 10.5335 | 5.034 | 0.71392 | -3.3285 | 19.845 | 19.401 | 19.3433 | 19.1214 | 18.5898 | 18.3038 | 17.8069 | 17.3823 | 17.1232 | 16.6358 | 15.2714 | 10.2325 | 5.0544 | -1.608 | 14.6483 | 14.2715 | 14.2349 | 14.031 | 13.5275 | 13.17 | 12.5479 | 12.0172 | 11.6095 | 11.1302 | 9.9058 | 4.8724 | 0.98607 | -2.4614
|  | SALISBURY CENTRAL | FS |  |  | 15.183 | 14.8171 | 14.6762 | 14.2495 | 13.4351 | 12.4555 | 11.0709 | 9.8202 | 8.2137 | 6.488 | 2.8313 | -6.1524 | -12.06 | -15.556 | 19.879 | 19.6862 | 19.5833 | 19.4226 | 19.1569 | 18.9114 | 18.5483 | 18.2265 | 17.8321 | 17.286 | 15.9643 | 10.8422 | 3.0813 | -9.1327 | 14.6785 | 14.5333 | 14.4739 | 14.2718 | 13.9758 | 13.656 | 13.1892 | 12.8008 | 12.4065 | 11.9824 | 10.9743 | 7.0158 | 2.3954 | -1.9124
BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST | MINIMUM HEADROOM | SU 83597 60930 | YES | 6.9355 | 6.5937 | 6.2445 | 5.4536 | 4.5985 | 3.6059 | 2.5029 | 1.3137 | -0.28559 | -1.9894 | -5.7262 | -15.422 | -19.1913 | -21.2486 | 6.4826 | 6.3789 | 6.2664 | 6.1101 | 5.8826 | 5.5781 | 5.1256 | 4.5381 | 3.8125 | 2.9423 | 0.91691 | -2.4565 | -4.5822 | -6.3385 | 6.4696 | 6.1654 | 5.8536 | 5.1503 | 4.3879 | 3.4829 | 2.4616 | 1.3553 | -0.102 | -1.6514 | -5.0551 | -14.078 | -17.57 | -19.5444
|  | SANDHURST | CT |  |  | 7.4548 | 7.3847 | 7.2992 | 6.8062 | 6.2659 | 5.6542 | 4.9969 | 4.287 | 2.8194 | 1.2499 | -2.1349 | -11.2818 | -17.4487 | -20.5119 | 6.5362 | 6.4783 | 6.4131 | 6.3327 | 6.2333 | 6.0854 | 5.9108 | 5.6841 | 5.4047 | 5.092 | 4.4179 | 1.9534 | -2.1002 | -6.3385 | 6.927 | 6.8625 | 6.7831 | 6.3434 | 5.8602 | 5.3111 | 4.7135 | 4.062 | 2.7365 | 1.3375 | -1.7173 | -9.9753 | -15.3946 | -18.0663
|  | SANDHURST | LW |  |  | 6.9355 | 6.5937 | 6.2445 | 5.4536 | 4.5985 | 3.6059 | 2.5029 | 1.3137 | -0.28559 | -1.9894 | -5.7262 | -15.422 | -19.1913 | -21.2486 | 6.4826 | 6.3789 | 6.2664 | 6.1101 | 5.8826 | 5.5781 | 5.1256 | 4.5381 | 3.8125 | 2.9423 | 0.91691 | -2.4565 | -4.5822 | -6.1019 | 6.4696 | 6.1654 | 5.8536 | 5.1503 | 4.3879 | 3.4829 | 2.4616 | 1.3553 | -0.102 | -1.6514 | -5.0551 | -14.078 | -17.57 | -19.5444
|  | SANDHURST | ST |  |  | 7.4833 | 7.4276 | 7.3576 | 7.2321 | 7.0725 | 6.8586 | 6.5668 | 6.2122 | 5.8021 | 5.3052 | 3.9601 | -1.6594 | -7.0366 | -11.8089 | 6.5525 | 6.5219 | 6.4829 | 6.3994 | 6.3061 | 6.1927 | 6.0438 | 5.8845 | 5.6853 | 5.4533 | 4.8366 | 3.0026 | -0.59733 | -5.4638 | 6.9462 | 6.8909 | 6.8218 | 6.6927 | 6.5341 | 6.327 | 6.0378 | 5.6881 | 5.2783 | 4.7832 | 3.4556 | -1.8928 | -6.8433 | -11.0477
|  | SANDHURST | FS |  |  | 7.4548 | 7.3847 | 7.2992 | 6.8062 | 6.2659 | 5.6542 | 4.9969 | 4.287 | 2.8194 | 1.2499 | -2.1349 | -11.2818 | -17.4487 | -20.5119 | 6.5648 | 6.5454 | 6.5201 | 6.4817 | 6.436 | 6.3765 | 6.3073 | 6.2298 | 6.1355 | 6.0287 | 5.733 | 4.6683 | 2.3868 | -4.6545 | 6.9991 | 6.9868 | 6.9716 | 6.8973 | 6.8208 | 6.7181 | 6.6095 | 6.4903 | 6.2183 | 5.93 | 5.2314 | 2.1987 | -1.8329 | -5.8774
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN | MINIMUM HEADROOM | SZ 59877 85052 | YES | 1.8864 | 1.6041 | 1.3498 | 0.83428 | 0.29562 | -0.26634 | -1.0729 | -1.9479 | -2.825 | -4.3076 | -9.0934 | -17.0017 | -19.5006 | -21.0502 | 4.2068 | 4.0603 | 3.9394 | 3.7339 | 3.5159 | 3.2847 | 2.8183 | 2.2924 | 1.6465 | 0.23249 | -3.2508 | -8.8291 | -10.3988 | -11.4882 | 1.4824 | 1.2109 | 0.97578 | 0.51323 | 0.030948 | -0.47171 | -1.2046 | -2.0031 | -2.7982 | -3.6666 | -7.9779 | -15.4336 | -17.7357 | -19.1794
|  | SANDOWN | CT |  |  | 2.2592 | 2.2112 | 2.1533 | 1.8563 | 1.5491 | 1.2145 | 0.66324 | 0.10114 | -0.63662 | -1.3749 | -2.7842 | -6.9943 | -9.9932 | -11.6178 | 4.3443 | 4.3076 | 4.2644 | 4.1498 | 4.0185 | 3.8556 | 3.5053 | 3.1412 | 2.8019 | 2.4297 | 1.7318 | -0.43538 | -2.5137 | -4.7927 | 1.8298 | 1.787 | 1.7356 | 1.4745 | 1.2044 | 0.90297 | 0.39269 | -0.12877 | -0.79297 | -1.4566 | -2.7029 | -6.3693 | -8.946 | -10.3188
|  | SANDOWN | LW |  |  | 1.8864 | 1.6041 | 1.3498 | 0.83428 | 0.29562 | -0.26634 | -1.0729 | -1.9479 | -2.825 | -4.3076 | -9.0934 | -17.0017 | -19.5006 | -21.0502 | 4.2068 | 4.0603 | 3.9394 | 3.7339 | 3.5159 | 3.2847 | 2.8183 | 2.2924 | 1.6465 | 0.23249 | -3.2508 | -8.8291 | -10.3988 | -11.4882 | 1.4824 | 1.2109 | 0.97578 | 0.51323 | 0.030948 | -0.47171 | -1.2046 | -2.0031 | -2.7982 | -3.6666 | -7.9779 | -15.4336 | -17.7357 | -19.1794
|  | SANDOWN | ST |  |  | 2.3626 | 2.3664 | 2.366 | 2.3564 | 2.3406 | 2.3023 | 2.0654 | 1.8075 | 1.7314 | 1.6537 | 1.5149 | 0.034374 | -1.894 | -4.4587 | 4.3781 | 4.3596 | 4.3364 | 4.3075 | 4.2723 | 4.2136 | 3.9816 | 3.7278 | 3.6139 | 3.4924 | 3.2629 | 2.0609 | 0.33799 | -2.3028 | 1.9216 | 1.9257 | 1.9268 | 1.9194 | 1.9061 | 1.866 | 1.628 | 1.3751 | 1.2932 | 1.2103 | 1.077 | -0.21593 | -1.8645 | -4.0611
|  | SANDOWN | FS |  |  | 2.2592 | 2.2112 | 2.1533 | 1.8563 | 1.5491 | 1.2145 | 0.66324 | 0.10114 | -0.63662 | -1.3749 | -2.7842 | -6.9943 | -9.9932 | -11.6178 | 4.3963 | 4.3421 | 4.2979 | 4.2499 | 4.1879 | 4.1274 | 3.9997 | 3.8506 | 3.6678 | 3.476 | 3.0845 | 1.5301 | -1.2306 | -5.908 | 1.9386 | 1.903 | 1.8807 | 1.8321 | 1.7689 | 1.711 | 1.5797 | 1.4365 | 1.2548 | 1.0753 | 0.7468 | -0.57449 | -2.3414 | -4.3854
LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY | MINIMUM HEADROOM | SZ 85667 94289 | YES | 1.5593 | 1.3027 | 1.1251 | 0.70248 | 0.24825 | -0.22836 | -0.74788 | -1.3187 | -2.0487 | -2.7732 | -4.2403 | -8.1416 | -14.6726 | -19.0126 | 3.7508 | 3.6123 | 3.5229 | 3.336 | 3.1319 | 2.9149 | 2.6677 | 2.3874 | 2.0103 | 1.621 | 0.79738 | -3.6953 | -9.4386 | -12.9357 | 3.1849 | 2.9597 | 2.797 | 2.4188 | 2.0148 | 1.5912 | 1.1274 | 0.61667 | -0.048687 | -0.71592 | -2.0825 | -6.3893 | -13.6546 | -17.9109
|  | SELSEY | CT |  |  | 1.8355 | 1.7551 | 1.7145 | 1.4554 | 1.1615 | 0.83519 | 0.4764 | 0.091278 | -0.61647 | -1.3241 | -2.6186 | -6.358 | -9.1955 | -10.9896 | 3.8733 | 3.8229 | 3.7915 | 3.6726 | 3.535 | 3.3718 | 3.1814 | 2.9717 | 2.617 | 2.2448 | 1.5572 | -0.41945 | -2.2329 | -4.0506 | 3.4412 | 3.3798 | 3.3444 | 3.1169 | 2.8612 | 2.5753 | 2.258 | 1.9169 | 1.2784 | 0.63278 | -0.55139 | -3.9377 | -6.5105 | -8.1403
|  | SELSEY | LW |  |  | 1.5593 | 1.3027 | 1.1251 | 0.70248 | 0.24825 | -0.22836 | -0.74788 | -1.3187 | -2.0487 | -2.7732 | -4.2403 | -8.1416 | -14.6726 | -19.0126 | 3.7508 | 3.6123 | 3.5229 | 3.336 | 3.1319 | 2.9149 | 2.6677 | 2.3874 | 2.0103 | 1.621 | 0.79738 | -3.6953 | -9.4386 | -12.9357 | 3.1849 | 2.9597 | 2.797 | 2.4188 | 2.0148 | 1.5912 | 1.1274 | 0.61667 | -0.048687 | -0.71592 | -2.0825 | -6.3893 | -13.6546 | -17.9109
|  | SELSEY | ST |  |  | 1.8953 | 1.8457 | 1.8414 | 1.7909 | 1.7219 | 1.6315 | 1.5232 | 1.4053 | 1.2468 | 1.098 | 0.8406 | -0.77615 | -2.9211 | -5.4181 | 3.8975 | 3.8604 | 3.8448 | 3.8062 | 3.7559 | 3.6869 | 3.598 | 3.5007 | 3.3553 | 3.2126 | 2.9418 | 1.6792 | -0.075381 | -2.245 | 3.4972 | 3.4616 | 3.4583 | 3.4208 | 3.3694 | 3.2982 | 3.2088 | 3.1109 | 2.9695 | 2.8351 | 2.5958 | 1.1257 | -0.88111 | -3.1509
|  | SELSEY | FS |  |  | 1.8355 | 1.7551 | 1.7145 | 1.4554 | 1.1615 | 0.83519 | 0.4764 | 0.091278 | -0.61647 | -1.3241 | -2.6186 | -6.358 | -9.1955 | -10.9896 | 3.9155 | 3.8558 | 3.8248 | 3.773 | 3.7075 | 3.6434 | 3.5669 | 3.4879 | 3.3401 | 3.191 | 2.8898 | 1.7352 | -0.31554 | -3.5994 | 3.5138 | 3.4591 | 3.4401 | 3.3785 | 3.302 | 3.2292 | 3.1447 | 3.0584 | 2.894 | 2.7372 | 2.4452 | 1.282 | -0.36541 | -2.2518
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY | MINIMUM HEADROOM | ST 85605 23325 | YES | 9.79 | 9.3867 | 8.8662 | 8.4043 | 7.809 | 7.1979 | 6.5318 | 5.714 | 4.7997 | 3.0371 | -1.1774 | -12.1776 | -17.1683 | -17.6876 | 12.5294 | 12.2974 | 11.9472 | 11.6917 | 11.3603 | 11.033 | 10.6643 | 10.2139 | 9.7393 | 8.5466 | 5.4413 | -2.7714 | -6.5091 | -6.9412 | 10.1682 | 9.7956 | 9.3022 | 8.8693 | 8.3276 | 7.7725 | 7.159 | 6.4128 | 5.1583 | 3.4926 | -0.51407 | -10.9958 | -15.7783 | -16.3217
|  | SHAFTESBURY | CT |  |  | 10.1443 | 9.9659 | 9.4536 | 9.1508 | 8.7391 | 8.2568 | 7.6888 | 6.9995 | 6.1128 | 5.1618 | 3.4552 | -0.18647 | -2.4132 | -3.5879 | 12.6942 | 12.592 | 12.1714 | 12.0109 | 11.7877 | 11.5071 | 11.155 | 10.7357 | 10.2258 | 9.6591 | 8.6175 | 6.3789 | 4.7376 | 2.9831 | 10.5083 | 10.3586 | 9.8751 | 9.6079 | 9.2585 | 8.8424 | 8.3373 | 7.7326 | 6.9406 | 6.0913 | 4.5275 | 1.2221 | -0.78256 | -1.8672
|  | SHAFTESBURY | LW |  |  | 9.79 | 9.3867 | 8.8662 | 8.4043 | 7.809 | 7.1979 | 6.5318 | 5.714 | 4.7997 | 3.0371 | -1.1774 | -12.1776 | -17.1683 | -17.6876 | 12.5294 | 12.2974 | 11.9472 | 11.6917 | 11.3603 | 11.033 | 10.6643 | 10.2139 | 9.7393 | 8.5466 | 5.4413 | -2.7714 | -6.5091 | -6.9412 | 10.1682 | 9.7956 | 9.3022 | 8.8693 | 8.3276 | 7.7725 | 7.159 | 6.4128 | 5.1583 | 3.4926 | -0.51407 | -10.9958 | -15.7783 | -16.3217
|  | SHAFTESBURY | ST |  |  | 10.2569 | 10.1571 | 9.7267 | 9.5869 | 9.3798 | 9.1326 | 8.8481 | 8.5294 | 8.2328 | 7.9176 | 7.4189 | 5.7188 | 4.1098 | 2.2809 | 12.7423 | 12.6788 | 12.301 | 12.1912 | 12.0523 | 11.8812 | 11.6611 | 11.4264 | 11.1931 | 10.9475 | 10.5361 | 9.1469 | 7.5785 | 5.5033 | 10.6132 | 10.5362 | 10.1266 | 9.9949 | 9.8207 | 9.6083 | 9.3518 | 9.0792 | 8.8144 | 8.5373 | 8.0877 | 6.5241 | 5.016 | 3.283
|  | SHAFTESBURY | FS |  |  | 10.1443 | 9.9659 | 9.4536 | 9.1508 | 8.7391 | 8.2568 | 7.6888 | 6.9995 | 6.1128 | 5.1618 | 3.4552 | -0.18647 | -2.4132 | -3.5879 | 12.7247 | 12.5643 | 12.3179 | 12.1195 | 11.8635 | 11.5914 | 11.2553 | 10.8063 | 10.2806 | 9.7169 | 8.6242 | 5.9884 | 3.7681 | 0.95271 | 10.6267 | 10.4406 | 10.1762 | 9.9196 | 9.5946 | 9.2401 | 8.8029 | 8.2357 | 7.5958 | 6.9208 | 5.6457 | 2.6682 | 0.89757 | -0.33278
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET | MINIMUM HEADROOM | SZ 40828 88643 | YES | 7.2463 | 7.0533 | 6.8588 | 6.6955 | 6.5043 | 6.2885 | 6.0167 | 5.5783 | 4.2561 | 2.6497 | -0.99416 | -7.5515 | -9.833 | -11.4388 | 8.0551 | 7.9851 | 7.9135 | 7.8494 | 7.7688 | 7.6373 | 7.4557 | 7.0215 | 6.0249 | 4.792 | 1.9869 | -3.0753 | -4.8376 | -6.2159 | 6.8989 | 6.7283 | 6.5563 | 6.411 | 6.2426 | 6.0528 | 5.8141 | 5.2287 | 3.9641 | 2.4183 | -1.0867 | -7.4179 | -9.6702 | -11.3125
|  | SHALFLEET | CT |  |  | 7.3867 | 7.2631 | 7.1288 | 6.953 | 6.7355 | 6.4743 | 6.1498 | 5.5783 | 4.2561 | 2.6497 | -0.99416 | -7.5515 | -9.833 | -11.4388 | 8.0912 | 8.0358 | 7.9723 | 7.8877 | 7.7768 | 7.6373 | 7.4557 | 7.0215 | 6.0249 | 4.792 | 1.9869 | -3.0753 | -4.8376 | -6.2159 | 7.0208 | 6.9104 | 6.7897 | 6.6302 | 6.4334 | 6.1962 | 5.8996 | 5.2287 | 3.9641 | 2.4183 | -1.0867 | -7.4179 | -9.6702 | -11.3125
|  | SHALFLEET | LW |  |  | 7.2463 | 7.0533 | 6.8588 | 6.6955 | 6.5043 | 6.2885 | 6.0167 | 5.7181 | 5.3358 | 4.9264 | 3.9584 | 1.304 | 0.051162 | -1.156 | 8.0551 | 7.9851 | 7.9135 | 7.8494 | 7.7688 | 7.6735 | 7.5474 | 7.4024 | 7.1868 | 6.9494 | 5.9919 | 4.0021 | 2.8733 | 1.5968 | 6.8989 | 6.7283 | 6.5563 | 6.411 | 6.2426 | 6.0528 | 5.8141 | 5.5497 | 5.1966 | 4.8168 | 3.7075 | 1.1427 | -0.19438 | -1.5703
|  | SHALFLEET | ST |  |  | 7.4831 | 7.4073 | 7.3338 | 7.2052 | 7.0636 | 6.906 | 6.716 | 6.5125 | 6.2432 | 5.973 | 5.4334 | 4.0749 | 2.8329 | 1.7167 | 8.1189 | 8.0758 | 8.0301 | 7.9424 | 7.8521 | 7.7457 | 7.6149 | 7.4722 | 7.2627 | 7.0569 | 6.6326 | 5.4892 | 4.2892 | 3.126 | 7.1056 | 7.0368 | 6.9698 | 6.845 | 6.7132 | 6.5668 | 6.3899 | 6.2022 | 5.9398 | 5.6797 | 5.1524 | 3.7963 | 2.472 | 1.2619
|  | SHALFLEET | FS |  |  | 7.3867 | 7.2631 | 7.1288 | 6.953 | 6.7355 | 6.4743 | 6.1498 | 5.5783 | 4.2561 | 2.6497 | -0.99416 | -7.5515 | -9.833 | -11.4388 | 8.1295 | 8.0967 | 8.0608 | 8.0004 | 7.928 | 7.8429 | 7.7412 | 7.6273 | 7.487 | 7.3307 | 6.9673 | 5.7728 | 4.5514 | 3.5487 | 7.1333 | 7.0855 | 7.0384 | 6.9394 | 6.8269 | 6.7003 | 6.5551 | 6.3968 | 6.2003 | 5.9836 | 5.5055 | 3.9193 | 2.4548 | 1.3201
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN | MINIMUM HEADROOM | SZ 57809 81912 | YES | 16.522 | 16.2296 | 15.9292 | 15.3951 | 14.8112 | 14.1825 | 13.4715 | 12.6698 | 11.6637 | 10.5465 | 7.8137 | -0.19408 | -3.4883 | -5.5854 | 17.3905 | 17.2526 | 17.105 | 16.8618 | 16.5782 | 16.2464 | 15.827 | 15.2337 | 14.3951 | 13.4093 | 10.771 | 4.9797 | 2.4798 | -3.5116 | 15.2778 | 15.0266 | 14.7655 | 14.2866 | 13.7592 | 13.1851 | 12.5293 | 11.7841 | 10.8536 | 9.8137 | 6.1172 | -1.9037 | -4.8048 | -6.6673
|  | SHANKLIN | CT |  |  | 16.827 | 16.6865 | 16.5278 | 16.1225 | 15.6542 | 15.0991 | 14.4412 | 13.6449 | 12.3778 | 10.9651 | 7.8137 | -0.19408 | -3.4883 | -5.5854 | 17.4682 | 17.3533 | 17.2153 | 16.9726 | 16.6746 | 16.2989 | 15.827 | 15.2337 | 14.3951 | 13.4093 | 10.771 | 4.9797 | 2.4798 | -1.1363 | 15.5439 | 15.4235 | 15.2837 | 14.9165 | 14.4886 | 13.9764 | 13.363 | 12.6141 | 11.4382 | 10.1185 | 6.1172 | -1.9037 | -4.8048 | -6.6673
|  | SHANKLIN | LW |  |  | 16.522 | 16.2296 | 15.9292 | 15.3951 | 14.8112 | 14.1825 | 13.4715 | 12.6698 | 11.6637 | 10.5465 | 7.9368 | 2.5047 | -0.33625 | -1.817 | 17.3905 | 17.2526 | 17.105 | 16.8618 | 16.5782 | 16.2464 | 15.8401 | 15.3525 | 14.7418 | 13.9889 | 12.1639 | 8.7843 | 7.3269 | 6.4605 | 15.2778 | 15.0266 | 14.7655 | 14.2866 | 13.7592 | 13.1851 | 12.5293 | 11.7841 | 10.8536 | 9.8137 | 7.1362 | 1.9502 | -0.51726 | -1.8314
|  | SHANKLIN | ST |  |  | 16.9654 | 16.9126 | 16.852 | 16.8029 | 16.732 | 16.6389 | 16.4881 | 16.2918 | 16.0466 | 15.7146 | 14.6294 | 9.8191 | 6.4786 | 4.4305 | 17.5213 | 17.4449 | 17.3574 | 17.2599 | 17.139 | 16.9912 | 16.784 | 16.5201 | 16.1804 | 15.7606 | 14.6297 | 10.3235 | 6.8639 | 3.5939 | 15.6665 | 15.625 | 15.5748 | 15.523 | 15.451 | 15.3576 | 15.2071 | 14.9496 | 14.6229 | 14.2072 | 13.0575 | 8.4238 | 5.3382 | 3.6253
|  | SHANKLIN | FS |  |  | 16.827 | 16.6865 | 16.5278 | 16.1225 | 15.6542 | 15.0991 | 14.4412 | 13.6449 | 12.3778 | 10.9651 | 7.8137 | -0.19408 | -3.4883 | -5.5854 | 17.5119 | 17.4358 | 17.345 | 17.2315 | 17.0962 | 16.9344 | 16.7375 | 16.5033 | 16.1882 | 15.8038 | 14.753 | 10.3738 | 4.1322 | -3.5116 | 15.6492 | 15.613 | 15.5646 | 15.4828 | 15.386 | 15.2692 | 15.1258 | 14.9547 | 14.6723 | 14.3111 | 13.3379 | 9.2008 | 4.3315 | 0.93179
AXMINSTER | YEOVIL BSP | SHERBORNE | MINIMUM HEADROOM | ST 63978 18163 | YES | 1.2362 | 1.0319 | 0.78174 | 0.34454 | -0.18927 | -0.81477 | -1.5631 | -2.4358 | -3.6395 | -4.9816 | -8.4776 | -14.569 | -17.5584 | -21.4906 | 3.0464 | 3.0035 | 2.9437 | 2.8541 | 2.5693 | 2.2142 | 1.7653 | 1.2224 | 0.50213 | -0.33106 | -2.4936 | -6.5183 | -10.1277 | -14.985 | 1.3894 | 1.2104 | 0.99656 | 0.61709 | 0.15853 | -0.39046 | -1.064 | -1.8443 | -2.9043 | -4.086 | -7.1386 | -12.5774 | -16.3772 | -20.0807
|  | SHERBORNE | CT |  |  | 1.4216 | 1.3196 | 1.167 | 0.83712 | 0.4154 | -0.10217 | -0.72171 | -1.4743 | -2.6398 | -3.9336 | -7.1973 | -13.5237 | -17.5584 | -21.4906 | 3.0464 | 3.0035 | 2.9437 | 2.8647 | 2.7009 | 2.3696 | 1.9571 | 1.443 | 0.7105 | -0.13005 | -2.2288 | -6.5183 | -10.0915 | -12.9318 | 1.5561 | 1.4708 | 1.3477 | 1.0624 | 0.69952 | 0.24435 | -0.30029 | -0.9648 | -1.9992 | -3.1465 | -6.0192 | -11.7564 | -16.3772 | -20.0807
|  | SHERBORNE | LW |  |  | 1.2362 | 1.0319 | 0.78174 | 0.34454 | -0.18927 | -0.81477 | -1.5631 | -2.4358 | -3.6395 | -4.9816 | -8.4776 | -14.569 | -16.7682 | -17.9783 | 3.0574 | 3.0189 | 2.969 | 2.8541 | 2.5693 | 2.2142 | 1.7653 | 1.2224 | 0.50213 | -0.33106 | -2.4936 | -6.198 | -7.3786 | -8.0254 | 1.3894 | 1.2104 | 0.99656 | 0.61709 | 0.15853 | -0.39046 | -1.064 | -1.8443 | -2.9043 | -4.086 | -7.1386 | -12.5774 | -14.5196 | -15.5554
|  | SHERBORNE | ST |  |  | 1.434 | 1.3246 | 1.1705 | 0.9527 | 0.67685 | 0.31629 | -0.10897 | -0.66588 | -1.3897 | -2.1803 | -4.2915 | -10.2871 | -13.9502 | -15.8026 | 3.0591 | 3.0242 | 2.9745 | 2.904 | 2.7175 | 2.4303 | 2.0894 | 1.6381 | 1.0703 | 0.44331 | -1.176 | -6.0382 | -9.3426 | -11.6434 | 1.5901 | 1.5085 | 1.3828 | 1.2016 | 0.97448 | 0.67481 | 0.31897 | -0.1503 | -0.75711 | -1.4221 | -3.3611 | -9.0885 | -12.5334 | -14.1285
|  | SHERBORNE | FS |  |  | 1.4216 | 1.3196 | 1.167 | 0.83712 | 0.4154 | -0.10217 | -0.72171 | -1.4743 | -2.6398 | -3.9336 | -7.1973 | -13.5237 | -17.5584 | -21.4906 | 3.0612 | 3.0239 | 2.9762 | 2.9155 | 2.7113 | 2.45 | 2.1119 | 1.6818 | 1.1443 | 0.55641 | -0.89365 | -5.2832 | -10.1277 | -14.985 | 1.5891 | 1.5029 | 1.3829 | 1.2036 | 0.97725 | 0.70722 | 0.35816 | -0.083739 | -0.65186 | -1.2652 | -2.8759 | -7.7021 | -12.1642 | -14.8589
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE | MINIMUM HEADROOM | SP 03884 19102 | YES | 0.027314 | -0.091959 | -0.23088 | -0.4211 | -0.66384 | -0.94966 | -1.3755 | -1.9417 | -2.5292 | -3.2285 | -5.0289 | -12.0833 | -15.6205 | -15.3371 | 1.1098 | 1.0159 | 0.90976 | 0.76624 | 0.58014 | 0.36092 | 0.028061 | -0.41778 | -0.88841 | -1.4538 | -2.8914 | -8.2686 | -10.9754 | -10.7288 | -0.72993 | -0.84927 | -0.98997 | -1.1768 | -1.4147 | -1.6944 | -2.108 | -2.6508 | -3.2172 | -3.8943 | -5.6921 | -12.0123 | -15.3947 | -15.1165
|  | SHIPTON OLIFFE | CT |  |  | 0.091559 | 0.0075931 | -0.098861 | -0.2296 | -0.40508 | -0.63009 | -0.92803 | -1.3426 | -1.8441 | -2.6133 | -4.7571 | -12.0833 | -15.6205 | -15.3371 | 1.1599 | 1.1082 | 1.0398 | 0.95058 | 0.82744 | 0.66241 | 0.43902 | 0.11913 | -0.33176 | -0.92146 | -2.576 | -8.2686 | -10.9754 | -10.7288 | -0.67309 | -0.75112 | -0.85097 | -0.97555 | -1.1437 | -1.3613 | -1.6512 | -2.0499 | -2.5212 | -3.0909 | -4.9828 | -12.0123 | -15.3947 | -15.1165
|  | SHIPTON OLIFFE | LW |  |  | 0.027314 | -0.091959 | -0.22287 | -0.36559 | -0.54524 | -0.78061 | -1.0851 | -1.5125 | -1.9969 | -2.7603 | -4.6091 | -7.7239 | -8.5607 | -9.0754 | 1.1377 | 1.0755 | 1.0019 | 0.90524 | 0.77773 | 0.60481 | 0.3753 | 0.03683 | -0.44046 | -1.0277 | -2.457 | -4.8481 | -5.4657 | -5.8555 | -0.72993 | -0.83915 | -0.96051 | -1.0983 | -1.2728 | -1.5031 | -1.8022 | -2.215 | -2.676 | -3.2423 | -4.8507 | -7.8417 | -8.6398 | -9.1303
|  | SHIPTON OLIFFE | ST |  |  | 0.043565 | -0.085551 | -0.23088 | -0.4211 | -0.66384 | -0.94966 | -1.3755 | -1.9417 | -2.5292 | -3.2285 | -5.0289 | -10.055 | -13.1447 | -13.6825 | 1.1098 | 1.0159 | 0.90976 | 0.76624 | 0.58014 | 0.36092 | 0.028061 | -0.41778 | -0.88841 | -1.4538 | -2.8914 | -6.9065 | -9.3923 | -9.8772 | -0.7244 | -0.84927 | -0.98997 | -1.1768 | -1.4147 | -1.6944 | -2.108 | -2.6508 | -3.2172 | -3.8943 | -5.6921 | -10.6786 | -13.7391 | -14.2603
|  | SHIPTON OLIFFE | FS |  |  | 0.091559 | 0.0075931 | -0.098861 | -0.2296 | -0.40508 | -0.63009 | -0.92803 | -1.3426 | -1.8441 | -2.6133 | -4.7571 | -12.0833 | -15.6205 | -15.3371 | 1.1919 | 1.1651 | 1.1333 | 1.0867 | 1.0328 | 0.96303 | 0.87909 | 0.7666 | 0.64974 | 0.50655 | 0.11846 | -1.3713 | -2.7644 | -3.4136 | -0.61323 | -0.65118 | -0.69397 | -0.7642 | -0.84006 | -0.93891 | -1.0531 | -1.1983 | -1.3573 | -1.5489 | -2.0583 | -3.9607 | -5.6312 | -6.3688
NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY | MINIMUM HEADROOM | SU 39988 13808 | YES | 14.0194 | 13.7597 | 13.4943 | 12.9377 | 12.3439 | 11.7103 | 11.0271 | 10.286 | 9.4062 | 8.4608 | 6.3464 | 1.9931 | -0.6678 | -2.4459 | 16.2765 | 16.1178 | 15.9097 | 15.5593 | 15.1666 | 14.6794 | 14.1559 | 13.5492 | 12.7387 | 11.8172 | 9.7214 | 3.4433 | -9.7803 | -35.3456 | 12.7761 | 12.5436 | 12.3072 | 11.7999 | 11.2592 | 10.6759 | 10.0516 | 9.379 | 8.5743 | 7.713 | 5.7636 | 1.7749 | -0.68198 | -2.3376
|  | SHIRLEY | CT |  |  | 14.3707 | 14.2759 | 14.1647 | 13.7449 | 13.3024 | 12.7884 | 12.2559 | 11.6579 | 10.7278 | 9.7213 | 7.5781 | 2.3582 | -0.6678 | -2.4459 | 16.294 | 16.1178 | 15.9097 | 15.5593 | 15.1666 | 14.6794 | 14.1559 | 13.5492 | 12.7387 | 11.8172 | 9.7214 | 3.4433 | -4.5555 | -17.1505 | 13.0953 | 13.0108 | 12.9107 | 12.5381 | 12.1406 | 11.6655 | 11.1811 | 10.6318 | 9.7801 | 8.8492 | 6.8509 | 2.0685 | -0.68198 | -2.3376
|  | SHIRLEY | LW |  |  | 14.0194 | 13.7597 | 13.4943 | 12.9377 | 12.3439 | 11.7103 | 11.0271 | 10.286 | 9.4062 | 8.4608 | 6.3464 | 1.9931 | -0.14683 | -1.4813 | 16.2765 | 16.1641 | 16.0458 | 15.8177 | 15.5635 | 15.2615 | 14.9211 | 14.5343 | 14.0485 | 13.5032 | 12.2341 | 9.764 | 8.4244 | 7.3079 | 12.7761 | 12.5436 | 12.3072 | 11.7999 | 11.2592 | 10.6759 | 10.0516 | 9.379 | 8.5743 | 7.713 | 5.7636 | 1.7749 | -0.24377 | -1.5961
|  | SHIRLEY | ST |  |  | 14.5625 | 14.5886 | 14.6108 | 14.6213 | 14.6224 | 14.5785 | 14.5383 | 14.4684 | 14.3359 | 14.1614 | 13.6193 | 10.7878 | 8.4538 | 6.4337 | 16.3619 | 16.2402 | 16.0939 | 15.9092 | 15.6955 | 15.4094 | 15.1095 | 14.7614 | 14.311 | 13.7914 | 12.461 | 6.9649 | -1.0473 | -13.6124 | 13.261 | 13.2839 | 13.3026 | 13.3072 | 13.303 | 13.2441 | 13.1984 | 13.1244 | 12.9833 | 12.8015 | 12.2472 | 9.4995 | 7.2325 | 5.3927
|  | SHIRLEY | FS |  |  | 14.3707 | 14.2759 | 14.1647 | 13.7449 | 13.3024 | 12.7884 | 12.2559 | 11.6579 | 10.7278 | 9.7213 | 7.5781 | 2.3582 | -0.6678 | -2.4459 | 16.3296 | 16.1697 | 15.9832 | 15.7087 | 15.3943 | 15.029 | 14.6108 | 14.1362 | 13.5299 | 12.8377 | 11.109 | 3.8967 | -9.7803 | -35.3456 | 13.2242 | 13.2308 | 13.2381 | 13.1825 | 13.1208 | 13.0369 | 12.9495 | 12.8488 | 12.7001 | 12.5383 | 12.1185 | 10.0752 | 7.0271 | 4.1682
MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM | MINIMUM HEADROOM | SU 23782 87902 | YES | 6.4781 | 6.2662 | 6.0504 | 5.9078 | 5.7524 | 5.5808 | 5.3837 | 5.1355 | 4.693 | 4.1789 | 3.0361 | 0.65638 | -0.46612 | -0.981 | 8.0176 | 7.9269 | 7.8414 | 7.7776 | 7.6905 | 7.5165 | 7.1313 | 6.5907 | 5.968 | 5.3178 | 3.9979 | 1.2889 | 0.13842 | -0.36196 | 6.2651 | 6.0835 | 5.8982 | 5.7187 | 5.4836 | 5.1784 | 4.7704 | 4.1338 | 3.3799 | 2.5903 | 0.99993 | -2.2832 | -3.6353 | -4.0418
|  | SHRIVENHAM | CT |  |  | 6.5608 | 6.403 | 6.2307 | 6.0841 | 5.9159 | 5.705 | 5.4472 | 5.1355 | 4.693 | 4.1789 | 3.0361 | 0.65638 | -0.46612 | -0.981 | 8.0346 | 7.9694 | 7.9003 | 7.8519 | 7.7954 | 7.71 | 7.6101 | 7.4732 | 7.2931 | 7.0008 | 6.1751 | 4.4657 | 3.5784 | 2.8544 | 6.3517 | 6.2253 | 6.0871 | 5.9538 | 5.8037 | 5.6129 | 5.3819 | 5.1019 | 4.6973 | 4.2247 | 3.1843 | 1.0074 | -0.087792 | -0.64558
|  | SHRIVENHAM | LW |  |  | 6.4781 | 6.2662 | 6.0504 | 5.9078 | 5.7524 | 5.5808 | 5.3837 | 5.1764 | 4.8868 | 4.5591 | 3.8507 | 1.324 | -0.15685 | -0.76548 | 8.0176 | 7.9269 | 7.8414 | 7.7776 | 7.6905 | 7.5896 | 7.4295 | 7.2286 | 6.9561 | 6.6346 | 5.7453 | 3.6898 | 2.4695 | 1.8078 | 6.2651 | 6.0835 | 5.8982 | 5.7585 | 5.6105 | 5.4572 | 5.2793 | 5.0906 | 4.8182 | 4.5116 | 3.3457 | 0.69565 | -0.80049 | -1.5125
|  | SHRIVENHAM | ST |  |  | 6.6229 | 6.5044 | 6.3813 | 6.3305 | 6.2723 | 6.2062 | 6.1229 | 6.0404 | 5.9374 | 5.8282 | 5.5695 | 4.6026 | 3.5816 | 2.5226 | 8.0672 | 8.0267 | 7.9818 | 7.957 | 7.924 | 7.881 | 7.8253 | 7.7592 | 7.6534 | 7.5359 | 7.2335 | 6.3659 | 5.6779 | 4.9117 | 6.4086 | 6.3168 | 6.2208 | 6.1715 | 6.1161 | 6.0545 | 5.9782 | 5.9025 | 5.7985 | 5.6889 | 5.4335 | 4.5095 | 3.4668 | 2.3981
|  | SHRIVENHAM | FS |  |  | 6.5608 | 6.403 | 6.2307 | 6.0841 | 5.9159 | 5.705 | 5.4472 | 5.1355 | 4.693 | 4.1789 | 3.0361 | 0.65638 | -0.46612 | -0.981 | 8.0533 | 7.9944 | 7.9313 | 7.8833 | 7.7881 | 7.5165 | 7.1313 | 6.5907 | 5.968 | 5.3178 | 3.9979 | 1.2889 | 0.13842 | -0.36196 | 6.331 | 6.1302 | 5.9202 | 5.7187 | 5.4836 | 5.1784 | 4.7704 | 4.1338 | 3.3799 | 2.5903 | 0.99993 | -2.2832 | -3.6353 | -4.0418
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON | MINIMUM HEADROOM | ST 85356 13659 | YES | 12.0389 | 11.7598 | 11.4597 | 11.1038 | 10.6309 | 10.1222 | 8.7006 | 6.5917 | 3.8402 | 0.47869 | -7.532 | -21.5869 | -26.0241 | -29.0478 | 13.465 | 13.3521 | 13.228 | 13.0773 | 12.7976 | 12.4343 | 11.3116 | 9.7088 | 7.6401 | 5.0752 | -1.0627 | -11.7309 | -14.9486 | -17.3276 | 8.4879 | 8.2503 | 7.9943 | 7.6896 | 7.2892 | 6.8533 | 6.1083 | 4.0914 | 1.4624 | -1.7636 | -9.4498 | -22.9418 | -27.2105 | -30.1785
|  | SHROTON | CT |  |  | 12.2741 | 12.0963 | 11.8795 | 11.5107 | 10.9996 | 10.3115 | 8.7006 | 6.5917 | 3.8402 | 0.47869 | -7.532 | -21.5869 | -26.0241 | -29.0478 | 13.5215 | 13.4209 | 13.293 | 13.0898 | 12.7976 | 12.4343 | 11.3116 | 9.7088 | 7.6401 | 5.0752 | -1.0627 | -11.7309 | -14.9486 | -17.3276 | 8.6827 | 8.5291 | 8.3411 | 8.0194 | 7.5769 | 7.0459 | 6.1083 | 4.0914 | 1.4624 | -1.7636 | -9.4498 | -22.9418 | -27.2105 | -30.1785
|  | SHROTON | LW |  |  | 12.0389 | 11.7598 | 11.4597 | 11.1038 | 10.6309 | 10.1222 | 9.5645 | 9.0462 | 8.4015 | 7.7239 | 6.2549 | 3.4361 | 1.5977 | 0.28703 | 13.465 | 13.3521 | 13.228 | 13.0773 | 12.864 | 12.6257 | 12.3512 | 12.0788 | 11.7215 | 11.3282 | 10.4451 | 8.8393 | 7.6218 | 6.4209 | 8.4879 | 8.2503 | 7.9943 | 7.6896 | 7.2892 | 6.8533 | 6.3669 | 5.8981 | 5.3035 | 4.6683 | 3.2718 | 0.63352 | -1.1438 | -2.5565
|  | SHROTON | ST |  |  | 12.3919 | 12.2846 | 12.1595 | 11.9343 | 11.6502 | 11.3529 | 11.0168 | 10.7038 | 10.3091 | 9.8886 | 8.9423 | 6.08 | 3.7564 | 1.918 | 13.5723 | 13.5042 | 13.4236 | 13.2507 | 13.0552 | 12.8457 | 12.5895 | 12.3542 | 12.0426 | 11.7141 | 10.9561 | 8.6701 | 6.6927 | 4.9357 | 8.7784 | 8.6809 | 8.5678 | 8.3453 | 8.0837 | 7.8079 | 7.4821 | 7.1794 | 6.792 | 6.3831 | 5.4406 | 2.4983 | 0.18284 | -1.5165
|  | SHROTON | FS |  |  | 12.2741 | 12.0963 | 11.8795 | 11.5107 | 10.9996 | 10.3115 | 8.7006 | 6.5917 | 3.8402 | 0.47869 | -7.532 | -21.5869 | -26.0241 | -29.0478 | 13.5556 | 13.4832 | 13.3912 | 13.2504 | 13.0605 | 12.8362 | 12.5775 | 12.2972 | 11.952 | 11.5539 | 10.5269 | 6.9636 | 3.499 | 0.89417 | 8.778 | 8.689 | 8.5774 | 8.3808 | 8.1235 | 7.8267 | 7.4908 | 7.1148 | 6.6334 | 6.0791 | 4.6525 | -0.34533 | -4.9218 | -7.5981
LALEHAM | STAINES | SIDNEY ROAD | MINIMUM HEADROOM | TQ 04100 71760 | YES | 7.8653 | 7.596 | 7.2789 | 6.7204 | 6.1091 | 5.5503 | 4.9797 | 4.0212 | 2.794 | 1.3652 | -2.3573 | -17.3333 | -28.3531 | -31.9515 | 11.5395 | 11.4089 | 11.2522 | 10.9931 | 10.6977 | 10.3597 | 9.9625 | 9.2958 | 8.2907 | 7.047 | 3.277 | -7.7755 | -15.9784 | -18.6024 | 8.8181 | 8.5921 | 8.3283 | 7.8481 | 7.319 | 6.8139 | 6.2799 | 5.3892 | 4.2055 | 2.9193 | -0.51992 | -14.7495 | -25.2295 | -28.6299
|  | SIDNEY ROAD | CT |  |  | 8.0893 | 7.9358 | 7.72 | 7.2689 | 6.7434 | 6.2291 | 5.6879 | 4.7446 | 3.31 | 1.6901 | -2.3573 | -17.3333 | -28.3531 | -31.9515 | 11.5806 | 11.4548 | 11.2869 | 11.0231 | 10.7042 | 10.3597 | 9.9625 | 9.2958 | 8.2907 | 7.047 | 3.277 | -7.7755 | -15.9784 | -18.6024 | 9.0088 | 8.8813 | 8.7017 | 8.3101 | 7.85 | 7.3826 | 6.8768 | 5.9971 | 4.6197 | 3.1431 | -0.51992 | -14.7495 | -25.2295 | -28.6299
|  | SIDNEY ROAD | LW |  |  | 7.8653 | 7.596 | 7.2789 | 6.7204 | 6.1091 | 5.5503 | 4.9797 | 4.0212 | 2.794 | 1.3652 | -1.8951 | -5.7673 | -7.3964 | -8.1142 | 11.5395 | 11.4089 | 11.2522 | 10.9931 | 10.6977 | 10.4046 | 10.0732 | 9.4967 | 8.6961 | 7.8691 | 5.8903 | 3.5695 | 2.7433 | 2.3212 | 8.8181 | 8.5921 | 8.3283 | 7.8481 | 7.319 | 6.8139 | 6.2799 | 5.3892 | 4.2055 | 2.9193 | -0.049741 | -3.6622 | -5.1081 | -5.7628
|  | SIDNEY ROAD | ST |  |  | 8.2163 | 8.1421 | 8.0177 | 7.8766 | 7.7122 | 7.5892 | 7.4708 | 7.1171 | 6.5699 | 5.9812 | 4.4139 | 0.69695 | -1.924 | -3.5862 | 11.6356 | 11.5499 | 11.4315 | 11.2859 | 11.1208 | 10.9624 | 10.7831 | 10.4289 | 9.8745 | 9.3569 | 7.9642 | 4.5215 | 1.51 | -1.5442 | 9.1137 | 9.0536 | 8.9531 | 8.8265 | 8.6797 | 8.5546 | 8.4189 | 8.0624 | 7.4755 | 6.9144 | 5.3827 | 1.8284 | -0.62658 | -2.0714
|  | SIDNEY ROAD | FS |  |  | 8.0893 | 7.9358 | 7.72 | 7.2689 | 6.7434 | 6.2291 | 5.6879 | 4.7446 | 3.31 | 1.6901 | -2.3573 | -17.3333 | -28.3531 | -31.9515 | 11.6683 | 11.5733 | 11.4575 | 11.3194 | 11.1751 | 11.042 | 10.8991 | 10.6535 | 10.2927 | 9.8746 | 8.828 | 5.8704 | 1.3835 | -4.5717 | 9.1604 | 9.095 | 9.0122 | 8.8839 | 8.7572 | 8.6574 | 8.5582 | 8.3386 | 7.9925 | 7.5813 | 6.5704 | 4.1061 | 0.97652 | -1.3375
NURSLING GSP | ROWNHAMS | SILKSTEAD | MINIMUM HEADROOM | SU 44578 24565 | YES | 2.6723 | 2.5368 | 2.402 | 2.1519 | 1.8812 | 1.5976 | 1.2682 | 0.92529 | 0.49001 | 0.0034728 | -1.1791 | -4.338 | -6.4524 | -8.3425 | 3.6907 | 3.6025 | 3.5027 | 3.295 | 3.0926 | 2.8581 | 2.5325 | 2.1722 | 1.7424 | 1.2963 | 0.31368 | -2.3359 | -4.5307 | -6.3336 | 2.5849 | 2.4749 | 2.365 | 2.1542 | 1.9233 | 1.6762 | 1.3861 | 0.98544 | 0.49581 | -0.013645 | -1.1298 | -4.3554 | -6.6499 | -8.4342
|  | SILKSTEAD | CT |  |  | 2.8071 | 2.7388 | 2.6614 | 2.4716 | 2.2487 | 1.9959 | 1.6877 | 1.3478 | 0.78576 | 0.1519 | -1.1791 | -4.338 | -6.2647 | -7.3245 | 3.7275 | 3.6755 | 3.6132 | 3.5042 | 3.367 | 3.1996 | 2.9816 | 2.7429 | 2.4121 | 1.8988 | 0.59166 | -1.8626 | -2.8694 | -3.7925 | 2.6876 | 2.6287 | 2.5608 | 2.398 | 2.2021 | 1.9753 | 1.691 | 1.3801 | 0.88293 | 0.30502 | -0.98678 | -4.3554 | -5.8239 | -6.8301
|  | SILKSTEAD | LW |  |  | 2.6723 | 2.5368 | 2.402 | 2.1519 | 1.8812 | 1.5976 | 1.2682 | 0.92529 | 0.49001 | 0.0034728 | -1.0083 | -3.001 | -4.453 | -5.4749 | 3.7082 | 3.6546 | 3.6005 | 3.4896 | 3.3632 | 3.2193 | 3.0437 | 2.8572 | 2.6305 | 2.3711 | 1.7832 | 0.67876 | -0.2934 | -1.2373 | 2.5849 | 2.4749 | 2.365 | 2.1542 | 1.9233 | 1.6762 | 1.3861 | 1.083 | 0.70492 | 0.28854 | -0.59265 | -2.3054 | -3.6318 | -4.7038
|  | SILKSTEAD | ST |  |  | 2.7849 | 2.6883 | 2.5799 | 2.3697 | 2.1565 | 1.9045 | 1.5607 | 1.1594 | 0.68535 | 0.18904 | -0.89977 | -3.9867 | -6.4524 | -8.3425 | 3.6907 | 3.6025 | 3.5027 | 3.295 | 3.0926 | 2.8581 | 2.5325 | 2.1722 | 1.7424 | 1.2963 | 0.31368 | -2.3359 | -4.5307 | -6.3336 | 2.6558 | 2.5617 | 2.4562 | 2.2324 | 2.0113 | 1.7524 | 1.3937 | 0.98544 | 0.49581 | -0.013645 | -1.1298 | -4.2093 | -6.6499 | -8.4342
|  | SILKSTEAD | FS |  |  | 2.8071 | 2.7388 | 2.6614 | 2.4716 | 2.2487 | 1.9959 | 1.6877 | 1.3478 | 0.78576 | 0.1519 | -1.1791 | -4.338 | -6.2647 | -7.3245 | 3.7492 | 3.7089 | 3.6625 | 3.5919 | 3.5161 | 3.4211 | 3.3155 | 3.1908 | 3.0385 | 2.8842 | 2.5574 | 1.608 | 0.57141 | -0.84093 | 2.7337 | 2.7036 | 2.6714 | 2.5939 | 2.5135 | 2.4146 | 2.3045 | 2.1759 | 1.9925 | 1.8104 | 1.4363 | 0.33124 | -0.71285 | -1.8459
BRAMLEY (FLEE) | READING BSP | SILVER STREET | MINIMUM HEADROOM | SU 71957 72821 | YES | 8.817 | 8.6926 | 8.5737 | 8.2952 | 7.9793 | 7.6248 | 7.1871 | 6.7138 | 6.1992 | 5.2665 | 2.7878 | -2.9002 | -5.938 | -7.6057 | 10.445 | 10.3439 | 10.2242 | 10.0726 | 9.8831 | 9.6284 | 9.306 | 8.8573 | 7.8882 | 6.7435 | 4.0626 | -2.8977 | -13.76 | -35.6677 | 8.612 | 8.4324 | 8.2378 | 7.8165 | 7.3341 | 6.7646 | 6.0794 | 5.2996 | 4.4144 | 3.3837 | 0.97801 | -4.4033 | -7.2501 | -8.8479
|  | SILVER STREET | CT |  |  | 8.9067 | 8.834 | 8.7482 | 8.5545 | 8.3304 | 8.0439 | 7.6955 | 7.2727 | 6.6857 | 5.8389 | 3.0762 | -2.9002 | -5.938 | -7.6057 | 10.445 | 10.3439 | 10.2242 | 10.0726 | 9.8831 | 9.6284 | 9.306 | 8.8573 | 7.8882 | 6.7435 | 4.0626 | -2.8977 | -10.3322 | -21.547 | 8.7622 | 8.6571 | 8.524 | 8.2089 | 7.8307 | 7.3592 | 6.7642 | 6.0421 | 5.0509 | 3.8888 | 1.2637 | -4.4033 | -7.2501 | -8.8479
|  | SILVER STREET | LW |  |  | 8.817 | 8.6926 | 8.5737 | 8.2952 | 7.9793 | 7.6248 | 7.1871 | 6.7138 | 6.1992 | 5.2665 | 2.7878 | -1.9563 | -3.7946 | -5.0888 | 10.507 | 10.455 | 10.4094 | 10.2767 | 10.1103 | 9.8993 | 9.6138 | 9.3084 | 8.8774 | 8.2413 | 6.7429 | 3.5683 | 2.2918 | 1.2112 | 8.612 | 8.4324 | 8.2378 | 7.8165 | 7.3341 | 6.7646 | 6.0794 | 5.2996 | 4.4144 | 3.3837 | 0.97801 | -3.5851 | -5.3887 | -6.7307
|  | SILVER STREET | ST |  |  | 9.0731 | 9.1021 | 9.1203 | 9.059 | 9.0027 | 8.9357 | 8.8221 | 8.714 | 8.567 | 8.3878 | 7.8466 | 3.9499 | 0.8794 | -0.84729 | 10.4945 | 10.4326 | 10.3556 | 10.1757 | 10.0016 | 9.8068 | 9.5554 | 9.3108 | 9.0235 | 8.6931 | 6.9599 | 0.24727 | -7.7093 | -18.8137 | 8.925 | 8.9225 | 8.9021 | 8.7731 | 8.6411 | 8.4823 | 8.2463 | 7.9897 | 7.66 | 7.2502 | 6.0539 | 1.3539 | -1.7072 | -3.2747
|  | SILVER STREET | FS |  |  | 8.9067 | 8.834 | 8.7482 | 8.5545 | 8.3304 | 8.0439 | 7.6955 | 7.2727 | 6.6857 | 5.8389 | 3.0762 | -2.9002 | -5.938 | -7.6057 | 10.4871 | 10.4132 | 10.3246 | 10.1921 | 10.0378 | 9.8578 | 9.6432 | 9.4005 | 8.9871 | 8.2612 | 6.4297 | -1.0157 | -13.76 | -35.6677 | 8.8991 | 8.8809 | 8.8556 | 8.7486 | 8.6226 | 8.4731 | 8.2838 | 8.0539 | 7.7906 | 7.4826 | 6.6753 | 3.4836 | -0.41656 | -3.2654
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD | MINIMUM HEADROOM | SZ 18262 93590 | YES | 1.203 | 0.61868 | -0.080271 | -1.3543 | -2.7628 | -4.2396 | -5.9115 | -7.388 | -9.1694 | -11.0779 | -16.8656 | -27.8589 | -32.1706 | -35.2556 | 5.9599 | 5.686 | 5.3537 | 4.7943 | 4.1615 | 3.4815 | 2.6844 | 1.9459 | 1.0161 | -0.89711 | -5.3166 | -12.9819 | -16.0796 | -18.7527 | 0.99422 | 0.51386 | -0.051771 | -1.1227 | -2.3117 | -3.573 | -5.0106 | -6.32 | -7.9247 | -9.653 | -15.3791 | -25.7695 | -29.9566 | -33.1282
|  | SOMERFORD | CT |  |  | 1.7377 | 1.4451 | 1.0464 | 0.12251 | -0.90787 | -2.0133 | -3.2714 | -4.4125 | -6.2023 | -8.1278 | -12.03 | -21.4713 | -27.4027 | -30.7672 | 6.1446 | 5.9566 | 5.7062 | 5.2499 | 4.7308 | 4.1573 | 3.4891 | 2.8436 | 1.8906 | 0.81606 | -1.4488 | -6.9767 | -11.0068 | -14.7785 | 1.4863 | 1.2631 | 0.95984 | 0.1793 | -0.69228 | -1.6366 | -2.7122 | -3.7107 | -5.3086 | -7.0456 | -10.5969 | -19.1386 | -24.4193 | -27.469
|  | SOMERFORD | LW |  |  | 1.203 | 0.61868 | -0.080271 | -1.3543 | -2.7628 | -4.2396 | -5.9115 | -7.388 | -9.1694 | -11.0779 | -16.8656 | -27.8589 | -32.1706 | -35.2556 | 5.9599 | 5.686 | 5.3537 | 4.7943 | 4.1615 | 3.4815 | 2.6844 | 1.9459 | 1.0161 | -0.89711 | -5.3166 | -12.9819 | -16.0796 | -18.7527 | 0.99422 | 0.51386 | -0.051771 | -1.1227 | -2.3117 | -3.573 | -5.0106 | -6.32 | -7.9247 | -9.653 | -15.3791 | -25.7695 | -29.9566 | -33.1282
|  | SOMERFORD | ST |  |  | 1.8793 | 1.6951 | 1.4126 | 1.0816 | 0.71427 | 0.35646 | -0.053837 | -0.33346 | -0.69925 | -1.1049 | -2.0138 | -6.0721 | -10.4218 | -15.0902 | 6.2001 | 6.0668 | 5.879 | 5.6593 | 5.4166 | 5.1694 | 4.8823 | 4.6536 | 4.3333 | 3.9798 | 3.1612 | -0.011925 | -3.8105 | -8.2893 | 1.6176 | 1.4954 | 1.2994 | 1.0528 | 0.77175 | 0.49467 | 0.1726 | -0.057851 | -0.3829 | -0.74366 | -1.5561 | -5.2463 | -9.3974 | -13.7103
|  | SOMERFORD | FS |  |  | 1.7377 | 1.4451 | 1.0464 | 0.12251 | -0.90787 | -2.0133 | -3.2714 | -4.4125 | -6.2023 | -8.1278 | -12.03 | -21.4713 | -27.4027 | -30.7672 | 6.1857 | 6.0448 | 5.8565 | 5.6288 | 5.3727 | 5.1077 | 4.8024 | 4.5455 | 4.1686 | 3.7585 | 2.8248 | -0.43966 | -5.2389 | -12.1104 | 1.5992 | 1.4794 | 1.3058 | 1.0289 | 0.71756 | 0.40428 | 0.047374 | -0.23283 | -0.66489 | -1.1203 | -2.1062 | -5.54 | -9.7901 | -14.0492
LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTEAD | MINIMUM HEADROOM | SU 94025 00705 | YES | 3.964 | 3.454 | 2.9404 | 2.0172 | 0.98429 | -0.14913 | -1.4727 | -3.3871 | -5.7629 | -8.4363 | -14.1114 | -24.758 | -30.2575 | -34.1829 | 6.9968 | 6.7174 | 6.4309 | 5.9903 | 5.4356 | 4.7673 | 3.9201 | 2.5879 | 0.93874 | -0.97334 | -5.1845 | -12.7784 | -16.081 | -21.6944 | 2.8478 | 2.3905 | 1.9247 | 1.1004 | 0.15996 | -0.89787 | -2.1598 | -3.9565 | -6.1976 | -8.7335 | -13.9433 | -23.8167 | -28.7711 | -32.3606
|  | SOUTH BERSTEAD | CT |  |  | 4.5262 | 4.3232 | 4.0728 | 3.4642 | 2.7334 | 1.8736 | 0.78734 | -0.84483 | -3.2237 | -5.8712 | -10.8896 | -21.9852 | -28.5372 | -32.9756 | 7.1926 | 7.0207 | 6.8031 | 6.4619 | 6.0106 | 5.44 | 4.6847 | 3.4593 | 1.8304 | -0.056384 | -3.5699 | -11.1769 | -16.081 | -21.1422 | 3.3304 | 3.143 | 2.9105 | 2.3611 | 1.6929 | 0.90401 | -0.074327 | -1.5611 | -3.7385 | -6.1518 | -10.7469 | -21.1611 | -27.0368 | -31.0036
|  | SOUTH BERSTEAD | LW |  |  | 3.964 | 3.454 | 2.9404 | 2.0172 | 0.98429 | -0.14913 | -1.4727 | -3.3871 | -5.7629 | -8.4363 | -14.1114 | -24.758 | -30.2575 | -34.1829 | 6.9968 | 6.7174 | 6.4309 | 5.9903 | 5.4356 | 4.7673 | 3.9201 | 2.5879 | 0.93874 | -0.97334 | -5.1845 | -12.7784 | -15.6694 | -18.0847 | 2.8478 | 2.3905 | 1.9247 | 1.1004 | 0.15996 | -0.89787 | -2.1598 | -3.9565 | -6.1976 | -8.7335 | -13.9433 | -23.8167 | -28.7711 | -32.3606
|  | SOUTH BERSTEAD | ST |  |  | 4.6238 | 4.5002 | 4.3503 | 4.1836 | 3.94 | 3.6391 | 3.2168 | 2.3771 | 1.3528 | 0.1796 | -2.0268 | -11.163 | -17.9971 | -21.8848 | 7.2156 | 7.0832 | 6.9236 | 6.7571 | 6.5297 | 6.2448 | 5.854 | 5.0955 | 4.1689 | 3.1122 | 1.1018 | -6.64 | -12.5938 | -16.7611 | 3.4147 | 3.2999 | 3.1609 | 3.0148 | 2.8029 | 2.541 | 2.1672 | 1.3999 | 0.46122 | -0.60516 | -2.568 | -11.4618 | -17.8674 | -21.2369
|  | SOUTH BERSTEAD | FS |  |  | 4.5262 | 4.3232 | 4.0728 | 3.4642 | 2.7334 | 1.8736 | 0.78734 | -0.84483 | -3.2237 | -5.8712 | -10.8896 | -21.9852 | -28.5372 | -32.9756 | 7.2591 | 7.126 | 6.9887 | 6.8344 | 6.6377 | 6.4272 | 6.1641 | 5.7681 | 5.2052 | 4.5312 | 3.0615 | -2.8763 | -11.7858 | -21.6944 | 3.4593 | 3.3497 | 3.242 | 3.0859 | 2.8882 | 2.6843 | 2.4319 | 2.0443 | 1.4632 | 0.77849 | -0.63949 | -6.516 | -14.8141 | -21.0719
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE | MINIMUM HEADROOM | SZ 13563 92074 | YES | 4.3707 | 4.0429 | 3.6683 | 2.896 | 1.9904 | 0.93598 | -0.31422 | -1.7821 | -3.5689 | -5.6329 | -10.6704 | -23.3051 | -36.2827 | -40.6885 | 5.5784 | 5.4139 | 5.2106 | 4.825 | 4.3393 | 3.727 | 2.9488 | 1.9807 | 0.77134 | -0.68079 | -4.2537 | -13.6674 | -23.6192 | -27.191 | 3.4387 | 3.1476 | 2.8082 | 2.125 | 1.3091 | 0.3337 | -0.85195 | -2.276 | -4.0266 | -6.0792 | -10.9967 | -21.3912 | -33.8691 | -38.2112
|  | SOUTHBOURNE | CT |  |  | 4.7436 | 4.6181 | 4.4454 | 3.87 | 3.1801 | 2.3541 | 1.3689 | 0.18173 | -1.6087 | -3.7096 | -8.3537 | -18.1943 | -22.6916 | -25.406 | 5.6692 | 5.536 | 5.3552 | 4.9977 | 4.543 | 3.9636 | 3.2292 | 2.3028 | 1.0366 | -0.46656 | -3.8891 | -11.2716 | -15.7935 | -21.0372 | 3.742 | 3.6159 | 3.4396 | 2.9176 | 2.277 | 1.4879 | 0.51702 | -0.68345 | -2.4126 | -4.4143 | -8.867 | -18.1985 | -22.3605 | -24.9063
|  | SOUTHBOURNE | LW |  |  | 4.3707 | 4.0429 | 3.6683 | 2.896 | 1.9904 | 0.93598 | -0.31422 | -1.7821 | -3.5689 | -5.6329 | -10.6704 | -23.3051 | -36.2827 | -40.6885 | 5.5784 | 5.4139 | 5.2106 | 4.825 | 4.3393 | 3.727 | 2.9488 | 1.9807 | 0.77134 | -0.68079 | -4.2537 | -13.6674 | -23.6192 | -27.191 | 3.4387 | 3.1476 | 2.8082 | 2.125 | 1.3091 | 0.3337 | -0.85195 | -2.276 | -4.0266 | -6.0792 | -10.9967 | -21.3912 | -33.8691 | -38.2112
|  | SOUTHBOURNE | ST |  |  | 4.9017 | 4.8665 | 4.8065 | 4.6808 | 4.5009 | 4.2645 | 3.9346 | 3.486 | 2.8508 | 2.0554 | -0.15329 | -8.7298 | -14.3764 | -16.8602 | 5.7266 | 5.6346 | 5.5151 | 5.3418 | 5.119 | 4.8387 | 4.4625 | 3.9948 | 3.384 | 2.6341 | 0.5858 | -7.0386 | -13.035 | -17.7278 | 3.8636 | 3.8119 | 3.7345 | 3.5911 | 3.3921 | 3.1305 | 2.7602 | 2.288 | 1.6606 | 0.87465 | -1.3191 | -9.7544 | -15.2584 | -17.5315
|  | SOUTHBOURNE | FS |  |  | 4.7436 | 4.6181 | 4.4454 | 3.87 | 3.1801 | 2.3541 | 1.3689 | 0.18173 | -1.6087 | -3.7096 | -8.3537 | -18.1943 | -22.6916 | -25.406 | 5.6986 | 5.5897 | 5.4504 | 5.264 | 5.0387 | 4.7539 | 4.417 | 3.9891 | 3.4156 | 2.7725 | 1.1863 | -5.2149 | -14.2118 | -24.7337 | 3.8248 | 3.764 | 3.6738 | 3.5017 | 3.2923 | 3.0199 | 2.6967 | 2.2734 | 1.7068 | 1.0812 | -0.44402 | -6.6291 | -14.1228 | -19.2711
BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE | MINIMUM HEADROOM | SU 68199 71325 | YES | 7.9749 | 7.7676 | 7.5434 | 7.0728 | 6.5299 | 5.8343 | 5.0451 | 4.1139 | 2.9564 | 1.594 | -2.1246 | -10.5796 | -13.4642 | -15.2271 | 7.9915 | 7.8501 | 7.6831 | 7.4709 | 7.2072 | 6.7357 | 6.1929 | 5.4501 | 4.572 | 3.4147 | 0.66989 | -6.0757 | -10.1854 | -15.2809 | 6.5408 | 6.3523 | 6.1458 | 5.7151 | 5.2133 | 4.5422 | 3.7887 | 2.8991 | 1.7975 | 0.44373 | -3.0391 | -11.0377 | -13.8916 | -15.3572
|  | SOUTHCOTE | CT |  |  | 8.1826 | 8.0888 | 7.9554 | 7.5738 | 7.1162 | 6.4521 | 5.7357 | 4.8359 | 3.4668 | 1.8513 | -2.1246 | -10.5796 | -13.4642 | -15.2271 | 8.0373 | 7.9442 | 7.8168 | 7.5729 | 7.2634 | 6.7486 | 6.2213 | 5.5414 | 4.5907 | 3.4147 | 0.66989 | -5.0445 | -7.9676 | -10.9442 | 6.7213 | 6.6313 | 6.5026 | 6.1499 | 5.7221 | 5.0627 | 4.3783 | 3.4985 | 2.1717 | 0.62162 | -3.0391 | -11.0377 | -13.7119 | -15.3572
|  | SOUTHCOTE | LW |  |  | 7.9749 | 7.7676 | 7.5434 | 7.0728 | 6.5299 | 5.8343 | 5.0451 | 4.1139 | 2.9564 | 1.594 | -1.8007 | -7.9829 | -10.0675 | -11.2036 | 7.9915 | 7.8856 | 7.762 | 7.5209 | 7.2233 | 6.7789 | 6.2719 | 5.6576 | 4.9019 | 3.9389 | 1.5424 | -2.6181 | -3.8528 | -4.6205 | 6.5408 | 6.3523 | 6.1458 | 5.7151 | 5.2133 | 4.5422 | 3.7887 | 2.8991 | 1.7975 | 0.44373 | -2.8338 | -8.7297 | -10.6539 | -11.7156
|  | SOUTHCOTE | ST |  |  | 8.1743 | 8.0407 | 7.8825 | 7.6702 | 7.3612 | 6.8407 | 6.2353 | 5.3794 | 4.368 | 3.2139 | 0.36259 | -8.3761 | -12.6915 | -13.4591 | 7.9935 | 7.8501 | 7.6831 | 7.4709 | 7.2072 | 6.7357 | 6.1929 | 5.4501 | 4.572 | 3.5744 | 1.1903 | -6.0757 | -10.1854 | -12.1549 | 6.7023 | 6.567 | 6.4074 | 6.1794 | 5.8615 | 5.3136 | 4.7067 | 3.8526 | 2.8423 | 1.6549 | -1.1826 | -9.7119 | -13.8916 | -14.4906
|  | SOUTHCOTE | FS |  |  | 8.1826 | 8.0888 | 7.9554 | 7.5738 | 7.1162 | 6.4521 | 5.7357 | 4.8359 | 3.4668 | 1.8513 | -2.1246 | -10.5796 | -13.4642 | -15.2271 | 8.0483 | 7.961 | 7.8592 | 7.723 | 7.5493 | 7.3046 | 7.0098 | 6.6476 | 6.1607 | 5.5823 | 4.0656 | -1.49 | -8.433 | -15.2809 | 6.7683 | 6.7053 | 6.6314 | 6.4996 | 6.3276 | 6.0799 | 5.7404 | 5.3137 | 4.787 | 4.1713 | 2.5503 | -3.3577 | -9.7589 | -13.3609
AXMINSTER | YEOVIL BSP | SPARKFORD | MINIMUM HEADROOM | ST 60767 25496 | YES | 1.1228 | 0.99548 | 0.87031 | 0.77702 | 0.67435 | 0.56628 | 0.44106 | 0.24078 | -0.12488 | -0.59159 | -1.8528 | -7.0083 | -13.452 | -16.8446 | 1.9776 | 1.9091 | 1.8413 | 1.7834 | 1.7209 | 1.6521 | 1.5367 | 1.384 | 1.2178 | 1.0165 | 0.29865 | -3.5961 | -8.5794 | -11.2234 | 1.057 | 0.93566 | 0.81648 | 0.7263 | 0.62918 | 0.52545 | 0.40477 | 0.27036 | -0.030669 | -0.48295 | -1.6879 | -6.6256 | -12.7982 | -16.0511
|  | SPARKFORD | CT |  |  | 1.1977 | 1.1319 | 1.0606 | 0.98691 | 0.90449 | 0.76151 | 0.5342 | 0.24078 | -0.12488 | -0.59159 | -1.8528 | -7.0083 | -13.452 | -16.8446 | 2.0069 | 1.9717 | 1.9323 | 1.8894 | 1.8391 | 1.7767 | 1.6979 | 1.6072 | 1.4953 | 1.1935 | 0.29865 | -3.5961 | -8.5794 | -11.2234 | 1.1271 | 1.064 | 0.99551 | 0.92432 | 0.84411 | 0.75042 | 0.63797 | 0.35175 | -0.030669 | -0.48295 | -1.6879 | -6.6256 | -12.7982 | -16.0511
|  | SPARKFORD | LW |  |  | 1.1228 | 0.99548 | 0.87031 | 0.77702 | 0.67435 | 0.56628 | 0.44106 | 0.27815 | 0.025222 | -0.27897 | -1.1467 | -3.836 | -5.075 | -4.9922 | 1.9776 | 1.9091 | 1.8413 | 1.7834 | 1.7209 | 1.6521 | 1.5703 | 1.4786 | 1.3851 | 1.275 | 0.81512 | -1.1063 | -2.0363 | -1.9565 | 1.057 | 0.93566 | 0.81648 | 0.7263 | 0.62918 | 0.52545 | 0.40477 | 0.27036 | 0.1309 | -0.15283 | -1.0215 | -3.5939 | -4.775 | -4.6919
|  | SPARKFORD | ST |  |  | 1.2418 | 1.201 | 1.1594 | 1.0938 | 1.0266 | 0.96151 | 0.88561 | 0.80752 | 0.71915 | 0.6293 | 0.44947 | -0.040998 | -0.33873 | -0.49078 | 2.0317 | 2.0112 | 1.9896 | 1.9492 | 1.9101 | 1.8698 | 1.8189 | 1.7706 | 1.7181 | 1.6629 | 1.5552 | 1.3165 | 1.1349 | 0.95666 | 1.1704 | 1.132 | 1.0929 | 1.0277 | 0.96189 | 0.89827 | 0.82311 | 0.74836 | 0.66834 | 0.58668 | 0.42346 | 0.081294 | -0.14604 | -0.28834
|  | SPARKFORD | FS |  |  | 1.1977 | 1.1319 | 1.0606 | 0.98691 | 0.90449 | 0.76151 | 0.5342 | 0.24078 | -0.12488 | -0.59159 | -1.8528 | -7.0083 | -13.452 | -16.8446 | 2.0283 | 1.9756 | 1.9178 | 1.8466 | 1.7623 | 1.6613 | 1.5367 | 1.384 | 1.2178 | 1.0165 | 0.42913 | -1.6482 | -3.3792 | -4.1367 | 1.1727 | 1.1036 | 1.0293 | 0.9267 | 0.80764 | 0.672 | 0.50554 | 0.30506 | 0.07962 | -0.18809 | -0.88398 | -3.5018 | -5.6276 | -6.5301
MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST | MINIMUM HEADROOM | ST 84368 68717 | YES | 12.9686 | 8.7212 | 4.4183 | -4.0843 | -4.4642 | -5.5305 | -6.8861 | -8.5846 | -10.3807 | -12.3128 | -16.3904 | -23.4882 | -28.3036 | -28.5518 | 12.6632 | 7.4716 | 2.2478 | -8.1292 | -8.3047 | -9.3114 | -10.8459 | -12.456 | -14.0556 | -15.711 | -19.0835 | -24.9381 | -28.4796 | -28.6795 | 10.0424 | 4.7976 | -0.48756 | -10.9779 | -11.3017 | -12.5142 | -14.1918 | -16.0154 | -17.884 | -19.8518 | -23.9263 | -31.0336 | -35.62 | -35.9027
|  | SPRING QUARRY WEST | CT |  |  | 13.0977 | 8.9372 | 4.7244 | -3.6797 | -3.9637 | -4.9385 | -6.0957 | -7.2368 | -8.6771 | -10.1798 | -13.5286 | -23.4582 | -28.3036 | -28.5518 | 12.6941 | 7.5337 | 2.3428 | -7.9962 | -8.1561 | -9.2224 | -10.5004 | -11.5928 | -12.8289 | -14.1361 | -16.8996 | -24.7559 | -28.4796 | -28.6795 | 10.1643 | 4.9922 | -0.22149 | -10.6412 | -10.8867 | -12.0208 | -13.3711 | -14.7376 | -16.2583 | -17.8111 | -21.1707 | -30.9049 | -35.62 | -35.9027
|  | SPRING QUARRY WEST | LW |  |  | 12.9686 | 8.7212 | 4.4183 | -4.0843 | -4.4642 | -5.5305 | -6.8861 | -8.5846 | -10.3807 | -12.3128 | -16.3904 | -23.4882 | -25.7958 | -27.2681 | 12.6674 | 7.4955 | 2.2961 | -8.0535 | -8.224 | -9.3036 | -10.8459 | -12.456 | -14.0556 | -15.711 | -19.0835 | -24.9381 | -26.8711 | -28.1838 | 10.0424 | 4.7976 | -0.48756 | -10.9779 | -11.3017 | -12.5142 | -14.1918 | -16.0154 | -17.884 | -19.8518 | -23.9263 | -31.0336 | -33.39 | -34.9156
|  | SPRING QUARRY WEST | ST |  |  | 13.0826 | 8.8929 | 4.6554 | -3.7182 | -3.9339 | -4.7965 | -5.8115 | -6.8212 | -7.788 | -8.6526 | -10.1633 | -13.5613 | -15.6619 | -16.9791 | 12.6632 | 7.4716 | 2.2478 | -8.1292 | -8.3047 | -9.3114 | -10.4922 | -11.6213 | -12.6617 | -13.5792 | -15.1463 | -18.3638 | -20.5029 | -22.1707 | 10.1583 | 4.9649 | -0.26463 | -10.6555 | -10.8438 | -11.846 | -13.0247 | -14.1533 | -15.2023 | -16.1242 | -17.6919 | -21.2028 | -23.3073 | -24.5269
|  | SPRING QUARRY WEST | FS |  |  | 13.0977 | 8.9372 | 4.7244 | -3.6797 | -3.9637 | -4.9385 | -6.0957 | -7.2368 | -8.6771 | -10.1798 | -13.5286 | -23.4582 | -28.3036 | -28.5518 | 12.6844 | 7.5102 | 2.312 | -8.0118 | -8.1494 | -9.0294 | -10.0676 | -11.1126 | -12.022 | -12.8299 | -14.3313 | -16.9258 | -19.2303 | -21.6105 | 10.1848 | 5.0195 | -0.17228 | -10.5037 | -10.6469 | -11.5197 | -12.5484 | -13.5815 | -14.5057 | -15.323 | -16.8324 | -19.4132 | -21.5118 | -22.921
NORTH HYDE GSP | NORTH HYDE (D) | SPRINGFIELD ROAD | MINIMUM HEADROOM | TQ 11409 80620 | YES | 10.4334 | 10.2341 | 9.9928 | 9.4588 | -23.8356 | -25.6427 | -27.7965 | -29.774 | -31.6538 | -33.4943 | -38.1529 | -50.278 | -57.6569 | -61.764 | 12.3302 | 12.2419 | 12.0467 | 11.6877 | -29.591 | -31.3012 | -33.2791 | -35.391 | -37.3976 | -39.2963 | -43.5591 | -53.3274 | -67.2438 | -90.9286 | 9.5279 | 9.3468 | 9.1269 | 8.6397 | -32.7629 | -34.7881 | -37.2113 | -39.3746 | -41.3629 | -43.2635 | -48.4677 | -60.4978 | -67.7143 | -71.7032
|  | SPRINGFIELD ROAD | CT |  |  | 10.6985 | 10.6497 | 10.5397 | 10.1661 | -22.9209 | -24.495 | -26.3181 | -27.956 | -29.6838 | -31.3443 | -34.4286 | -41.0892 | -44.2855 | -45.773 | 12.351 | 12.286 | 12.157 | 11.9099 | -29.278 | -31.0666 | -33.1756 | -35.042 | -36.8274 | -38.5114 | -41.6444 | -49.255 | -56.9822 | -68.4329 | 9.7782 | 9.7422 | 9.6495 | 9.3128 | -31.8895 | -33.6825 | -35.7696 | -37.5883 | -39.4022 | -41.0913 | -44.1489 | -50.6786 | -53.6277 | -54.9993
|  | SPRINGFIELD ROAD | LW |  |  | 10.4334 | 10.2341 | 9.9928 | 9.4588 | -23.8356 | -25.6427 | -27.7965 | -29.774 | -31.6538 | -33.4943 | -38.1529 | -50.278 | -57.6569 | -61.764 | 12.3604 | 12.3066 | 12.2127 | 12.0593 | -29.0819 | -30.8334 | -32.9566 | -34.7875 | -36.7219 | -38.8943 | -43.5591 | -53.3274 | -59.1917 | -62.4477 | 9.5279 | 9.3468 | 9.1269 | 8.6397 | -32.7629 | -34.7881 | -37.2113 | -39.3746 | -41.3629 | -43.2635 | -48.4677 | -60.4978 | -67.7143 | -71.7032
|  | SPRINGFIELD ROAD | ST |  |  | 10.6716 | 10.5859 | 10.4364 | 10.2873 | -22.5807 | -23.7857 | -25.2729 | -26.6889 | -28.0504 | -29.4196 | -32.1768 | -39.0972 | -43.7611 | -45.6127 | 12.3479 | 12.2788 | 12.1465 | 11.9171 | -29.2014 | -30.7892 | -32.7234 | -34.5543 | -36.234 | -37.8402 | -40.9803 | -49.4253 | -58.3794 | -69.734 | 9.7729 | 9.702 | 9.5707 | 9.4402 | -31.5574 | -32.9673 | -34.7355 | -36.4751 | -38.061 | -39.5785 | -42.5385 | -49.5409 | -54.1356 | -55.8117
|  | SPRINGFIELD ROAD | FS |  |  | 10.6985 | 10.6497 | 10.5397 | 10.1661 | -22.9209 | -24.495 | -26.3181 | -27.956 | -29.6838 | -31.3443 | -34.4286 | -41.0892 | -44.2855 | -45.773 | 12.3302 | 12.2419 | 12.0467 | 11.6877 | -29.591 | -31.3012 | -33.2791 | -35.391 | -37.3976 | -39.2963 | -43.0762 | -53.1367 | -67.2438 | -90.9286 | 9.7279 | 9.6257 | 9.4817 | 9.2984 | -31.7321 | -33.2071 | -34.9664 | -36.8878 | -38.7232 | -40.385 | -43.4492 | -49.8699 | -54.6491 | -57.6242
NURSLING GSP | WINCHESTER | ST CROSS | MINIMUM HEADROOM | SU 47287 28156 | YES | 3.3148 | 2.9933 | 2.4427 | 1.5181 | 0.55126 | -0.44973 | -1.3345 | -2.2365 | -3.326 | -4.5177 | -7.3002 | -16.5363 | -21.0043 | -21.6332 | 6.6947 | 6.4883 | 5.966 | 5.3682 | 4.8337 | 4.304 | 3.9042 | 3.3898 | 2.6755 | 1.7922 | -0.53251 | -7.0236 | -11.1465 | -18.183 | 2.9146 | 2.6086 | 2.0765 | 1.2014 | 0.27567 | -0.68125 | -1.5027 | -2.331 | -3.3236 | -4.3996 | -7.1473 | -15.8607 | -20.0749 | -20.6849
|  | ST CROSS | CT |  |  | 3.6273 | 3.4145 | 2.8181 | 2.0558 | 1.3416 | 0.63527 | 0.10978 | -0.49139 | -1.5881 | -2.7498 | -5.1969 | -11.5961 | -15.8736 | -18.362 | 6.7611 | 6.5409 | 5.966 | 5.3682 | 4.8337 | 4.304 | 3.9042 | 3.426 | 2.7349 | 1.954 | 0.21777 | -4.1735 | -7.8295 | -12.3335 | 3.2109 | 3.007 | 2.4219 | 1.6303 | 0.92381 | 0.24725 | -0.22094 | -0.7569 | -1.73 | -2.762 | -5.0704 | -10.884 | -14.5644 | -16.7223
|  | ST CROSS | LW |  |  | 3.3148 | 2.9933 | 2.4427 | 1.5181 | 0.55126 | -0.44973 | -1.3345 | -2.2365 | -3.326 | -4.5177 | -7.3002 | -16.5363 | -21.0043 | -21.6332 | 6.6947 | 6.512 | 6.1254 | 5.5916 | 5.0208 | 4.4179 | 3.9122 | 3.3898 | 2.7857 | 2.0813 | -0.53251 | -7.0236 | -10.1186 | -10.5398 | 2.9146 | 2.6086 | 2.0765 | 1.2014 | 0.27567 | -0.68125 | -1.5027 | -2.331 | -3.3236 | -4.3996 | -7.1473 | -15.8607 | -20.0749 | -20.6849
|  | ST CROSS | ST |  |  | 3.6966 | 3.5293 | 2.9785 | 2.4664 | 2.045 | 1.6599 | 1.4254 | 1.1428 | 0.79247 | 0.35363 | -0.88943 | -6.1865 | -10.4228 | -13.553 | 6.7858 | 6.5861 | 6.0318 | 5.5104 | 5.067 | 4.6508 | 4.3683 | 4.0423 | 3.6545 | 3.1857 | 1.9033 | -3.0104 | -7.5283 | -12.2035 | 3.2822 | 3.1244 | 2.5923 | 2.0749 | 1.6278 | 1.2427 | 1.0627 | 0.84982 | 0.53009 | 0.10609 | -1.1325 | -6.2375 | -10.1951 | -12.9549
|  | ST CROSS | FS |  |  | 3.6273 | 3.4145 | 2.8181 | 2.0558 | 1.3416 | 0.63527 | 0.10978 | -0.49139 | -1.5881 | -2.7498 | -5.1969 | -11.5961 | -15.8736 | -18.362 | 6.7134 | 6.4883 | 6.1233 | 5.6971 | 5.2189 | 4.7366 | 4.1471 | 3.4578 | 2.6755 | 1.7922 | -0.24667 | -5.5971 | -11.1465 | -18.183 | 3.2088 | 3.0403 | 2.7299 | 2.3275 | 1.8691 | 1.4108 | 0.82134 | 0.12294 | -0.71036 | -1.6426 | -3.7482 | -8.817 | -12.6657 | -15.0326
COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES | MINIMUM HEADROOM | SP 51259 05741 | YES | 8.0715 | 7.8632 | 7.571 | 7.3716 | 7.0805 | 6.8302 | 6.3821 | 5.9869 | 5.5376 | 5.0543 | 4.0018 | 2.0426 | 1.1188 | 0.37884 | 12.5725 | 12.362 | 12.0432 | 11.8283 | 11.4965 | 11.2282 | 10.7707 | 10.5331 | 10.2846 | 10.004 | 9.1171 | 2.5095 | -4.773 | -11.4938 | 9.2045 | 8.9819 | 8.6615 | 8.3101 | 7.8732 | 7.4797 | 6.9221 | 6.541 | 6.1128 | 5.6509 | 4.4364 | -2.6553 | -9.2713 | -12.5593
|  | ST EBBES | CT |  |  | 8.1385 | 7.9843 | 7.6411 | 7.5363 | 7.3111 | 7.1592 | 6.8447 | 6.676 | 6.4562 | 6.0282 | 5.2208 | 2.9062 | 1.4899 | 0.73095 | 12.637 | 12.4644 | 12.0459 | 11.923 | 11.6369 | 11.4562 | 11.0718 | 10.8899 | 10.6823 | 10.4482 | 10.0372 | 8.2097 | 5.8844 | 2.7988 | 9.3074 | 9.1489 | 8.7825 | 8.6398 | 8.3508 | 8.0911 | 7.6606 | 7.3803 | 7.0033 | 6.595 | 5.488 | 2.9166 | 1.5329 | 0.74239
|  | ST EBBES | LW |  |  | 8.0715 | 7.8632 | 7.571 | 7.3716 | 7.0805 | 6.8302 | 6.3821 | 5.9869 | 5.5376 | 5.0543 | 4.0018 | 2.0426 | 1.1188 | 0.37884 | 12.5725 | 12.362 | 12.0432 | 11.8283 | 11.4965 | 11.2282 | 10.7707 | 10.5331 | 10.2846 | 10.004 | 9.1171 | 7.5641 | 6.7301 | 5.8595 | 9.2045 | 8.9819 | 8.6615 | 8.3101 | 7.8732 | 7.4797 | 6.9221 | 6.541 | 6.1128 | 5.6509 | 4.6449 | 2.3879 | 1.3342 | 0.40666
|  | ST EBBES | ST |  |  | 8.1594 | 8.0212 | 7.694 | 7.5814 | 7.3602 | 7.2289 | 6.9359 | 6.8165 | 6.673 | 6.5199 | 6.2034 | 5.2786 | 4.6279 | 4.2285 | 12.6534 | 12.4933 | 12.0876 | 11.9483 | 11.6607 | 11.493 | 11.1217 | 10.9788 | 10.8083 | 10.6288 | 10.2769 | 9.1831 | 7.3526 | 4.2064 | 9.3861 | 9.273 | 8.9533 | 8.8696 | 8.6741 | 8.5752 | 8.306 | 8.2231 | 8.1105 | 7.9883 | 7.7414 | 6.1874 | 4.7917 | 3.8551
|  | ST EBBES | FS |  |  | 8.1385 | 7.9843 | 7.6411 | 7.5363 | 7.3111 | 7.1592 | 6.8447 | 6.676 | 6.4562 | 6.0282 | 5.2208 | 2.9062 | 1.4899 | 0.73095 | 12.6757 | 12.527 | 12.2913 | 12.1311 | 11.899 | 11.7048 | 11.4269 | 11.1948 | 10.9398 | 10.6471 | 9.1996 | 2.5095 | -4.773 | -11.4938 | 9.3754 | 9.2661 | 9.0762 | 8.9472 | 8.7636 | 8.5705 | 8.1478 | 7.648 | 7.0669 | 6.3555 | 4.4364 | -2.6553 | -9.2713 | -12.5593
BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS | MINIMUM HEADROOM | SU 47113 66363 | YES | 6.8729 | 6.8453 | 6.8112 | 6.728 | 6.4797 | 6.1193 | 5.7482 | 5.3067 | 4.7758 | 4.1447 | 2.6992 | 0.32335 | -0.64548 | -1.3206 | 11.6824 | 11.6133 | 11.5376 | 11.449 | 11.2923 | 11.0855 | 10.833 | 10.4952 | 10.1274 | 9.7441 | 8.9454 | 7.3748 | 6.5954 | 6.0914 | 7.7568 | 7.6939 | 7.6278 | 7.5387 | 7.3584 | 7.1208 | 6.8072 | 6.4225 | 5.9563 | 5.4008 | 4.1234 | 2.0398 | 1.1223 | 0.48275
|  | ST JOHNS | CT |  |  | 6.8729 | 6.8453 | 6.8112 | 6.728 | 6.4797 | 6.1193 | 5.7482 | 5.3067 | 4.7758 | 4.1447 | 2.6992 | 0.32335 | -0.64548 | -1.3206 | 11.716 | 11.6814 | 11.6375 | 11.55 | 11.3923 | 11.1497 | 10.9111 | 10.6242 | 10.2855 | 9.8807 | 8.9454 | 7.5184 | 6.9811 | 6.3188 | 7.7945 | 7.7682 | 7.735 | 7.6468 | 7.4411 | 7.1261 | 6.8072 | 6.4225 | 5.9563 | 5.4008 | 4.1234 | 2.0398 | 1.1223 | 0.48275
|  | ST JOHNS | LW |  |  | 6.8735 | 6.8572 | 6.8373 | 6.7845 | 6.5479 | 6.2091 | 5.8347 | 5.4221 | 4.9891 | 4.5352 | 3.5115 | 2.4667 | 2.1812 | 1.9469 | 11.7367 | 11.7263 | 11.7135 | 11.6676 | 11.5373 | 11.3391 | 11.1323 | 10.9088 | 10.6741 | 10.4246 | 9.8523 | 9.2151 | 9.0484 | 8.9118 | 7.7966 | 7.7815 | 7.7631 | 7.7074 | 7.5161 | 7.2307 | 6.9186 | 6.574 | 6.2122 | 5.8315 | 4.9671 | 4.0516 | 3.8031 | 3.6025
|  | ST JOHNS | ST |  |  | 6.8985 | 6.8954 | 6.8912 | 6.8494 | 6.7026 | 6.4968 | 6.3333 | 6.165 | 5.9762 | 5.7515 | 5.2285 | 4.4916 | 4.229 | 4.1039 | 11.7342 | 11.7168 | 11.6961 | 11.6378 | 11.5405 | 11.3873 | 11.2744 | 11.1577 | 11.0371 | 10.8947 | 10.5595 | 9.9075 | 9.4289 | 8.8341 | 7.8191 | 7.8162 | 7.8123 | 7.763 | 7.6517 | 7.4808 | 7.3555 | 7.2272 | 7.083 | 6.9108 | 6.5039 | 5.8872 | 5.6564 | 5.5585
|  | ST JOHNS | FS |  |  | 6.8729 | 6.8453 | 6.8112 | 6.728 | 6.4797 | 6.1193 | 5.7482 | 5.3067 | 4.7758 | 4.1447 | 2.6992 | 0.32335 | -0.64548 | -1.3206 | 11.6824 | 11.6133 | 11.5376 | 11.449 | 11.2923 | 11.0855 | 10.833 | 10.4952 | 10.1274 | 9.7441 | 8.9474 | 7.3748 | 6.5954 | 6.0914 | 7.7568 | 7.6939 | 7.6278 | 7.5387 | 7.3584 | 7.1208 | 6.8385 | 6.4775 | 6.076 | 5.6428 | 4.6955 | 2.9796 | 2.3215 | 2.2617
COWLEY GSP | WITNEY BSP | STANDLAKE | MINIMUM HEADROOM | SP 38923 02349 | NO | -1.2827 | -1.4084 | 7.4609 | 7.3398 | 7.197 | 7.0345 | 6.6857 | 6.0695 | 5.285 | 4.3296 | 1.9866 | -1.9328 | -3.1494 | -3.9754 | -0.26049 | -0.32109 | 8.1534 | 8.0398 | 7.8722 | 7.6155 | 7.2669 | 6.7978 | 6.2029 | 5.4681 | 3.6617 | 0.65496 | -0.23492 | -0.89681 | -0.88225 | -0.98499 | 7.4561 | 7.3362 | 7.0999 | 6.7685 | 6.3264 | 5.7362 | 4.9847 | 4.0654 | 1.8129 | -1.9606 | -3.1354 | -3.9506
|  | STANDLAKE | CT |  |  | -1.1933 | -1.2727 | 7.6389 | 7.5207 | 7.3798 | 7.1468 | 6.6857 | 6.0695 | 5.285 | 4.3296 | 1.9866 | -1.9328 | -3.1494 | -3.9754 | -0.25123 | -0.31568 | 8.1534 | 8.0398 | 7.8722 | 7.6155 | 7.2669 | 6.7978 | 6.2029 | 5.4681 | 3.6617 | 0.65496 | -0.23492 | -0.89681 | -0.88225 | -0.95245 | 7.5047 | 7.3362 | 7.0999 | 6.7685 | 6.3264 | 5.7362 | 4.9847 | 4.0654 | 1.8129 | -1.9606 | -3.1354 | -3.9506
|  | STANDLAKE | LW |  |  | -1.2827 | -1.4084 | 7.4609 | 7.3398 | 7.197 | 7.0345 | 6.8395 | 6.6064 | 6.3131 | 5.9817 | 5.1374 | 3.516 | 2.0275 | 0.85567 | -0.26049 | -0.32109 | 8.1697 | 8.1122 | 8.0408 | 7.9614 | 7.8524 | 7.7215 | 7.5518 | 7.3376 | 6.8118 | 5.4109 | 3.8574 | 2.8583 | -0.87419 | -0.98499 | 7.4561 | 7.3603 | 7.2319 | 7.0805 | 6.8968 | 6.6754 | 6.394 | 6.074 | 5.282 | 3.7822 | 1.8597 | 0.67813
|  | STANDLAKE | ST |  |  | -1.1958 | -1.2992 | 7.591 | 7.4404 | 7.2728 | 7.0743 | 6.8155 | 6.4238 | 5.9435 | 5.4387 | 4.3568 | 1.8812 | 0.75676 | 0.50164 | -0.20335 | -0.22908 | 8.2927 | 8.2332 | 8.1746 | 8.1098 | 7.9774 | 7.6497 | 7.2628 | 6.8562 | 5.9757 | 3.896 | 2.9013 | 2.5505 | -0.83373 | -0.87243 | 7.5734 | 7.4256 | 7.2628 | 7.0694 | 6.8142 | 6.4748 | 6.0464 | 5.5784 | 4.5047 | 1.9987 | 0.88326 | 0.67234
|  | STANDLAKE | FS |  |  | -1.1933 | -1.2727 | 7.6389 | 7.5207 | 7.3798 | 7.1468 | 6.6857 | 6.0695 | 5.285 | 4.3296 | 1.9866 | -1.9328 | -3.1494 | -3.9754 | -0.19044 | -0.20592 | 8.327 | 8.2955 | 8.2592 | 8.2196 | 8.1745 | 8.1258 | 8.0618 | 7.9916 | 7.5163 | 5.6742 | 3.9362 | 2.9483 | -0.82101 | -0.83415 | 7.6993 | 7.6577 | 7.562 | 7.4566 | 7.3308 | 7.1866 | 7.0062 | 6.7995 | 6.2562 | 4.0318 | 1.9675 | 0.89323
MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN | MINIMUM HEADROOM | SU 17585 90987 | YES | 8.7297 | 8.1977 | 7.5859 | 6.7958 | 5.9758 | 5.0375 | 3.1999 | 0.033025 | -3.8848 | -8.6346 | -19.961 | -43.136 | -56.0856 | -63.7502 | 6.3 | 5.8874 | 5.437 | 4.7927 | 4.1745 | 3.4838 | 1.7853 | -0.56924 | -3.5108 | -7.1024 | -15.7837 | -33.6764 | -43.9958 | -50.4631 | 2.1041 | 1.4521 | 1.633 | -0.2942 | -1.2781 | -2.6388 | -4.974 | -7.9778 | -11.7089 | -16.2367 | -27.0743 | -49.3096 | -61.9183 | -69.5774
|  | STANTON FITZWARREN | CT |  |  | 8.7924 | 8.3751 | 7.8208 | 7.1886 | 6.6799 | 5.96 | 5.1632 | 3.9258 | 1.1379 | -2.1865 | -9.8552 | -26.737 | -35.5254 | -39.6813 | 6.3646 | 6.0363 | 5.6323 | 5.0956 | 4.5875 | 3.9914 | 3.3155 | 2.2363 | 0.21638 | -2.2476 | -8.034 | -20.8739 | -27.6248 | -30.9646 | 2.3083 | 1.8282 | 2.1475 | 0.4121 | -0.36572 | -1.2418 | -2.2667 | -4.3112 | -6.9441 | -10.1062 | -17.4359 | -33.6372 | -42.1341 | -46.2398
|  | STANTON FITZWARREN | LW |  |  | 8.7297 | 8.1977 | 7.5859 | 6.7958 | 5.9758 | 5.0375 | 3.1999 | 0.033025 | -3.8848 | -8.6346 | -19.961 | -43.136 | -56.0856 | -63.7502 | 6.3 | 5.8874 | 5.437 | 4.7927 | 4.1745 | 3.4838 | 1.7853 | -0.56924 | -3.5108 | -7.1024 | -15.7837 | -33.6764 | -43.9958 | -50.4631 | 2.1041 | 1.4521 | 1.633 | -0.2942 | -1.2781 | -2.6388 | -4.974 | -7.9778 | -11.7089 | -16.2367 | -27.0743 | -49.3096 | -61.9183 | -69.5774
|  | STANTON FITZWARREN | ST |  |  | 8.8722 | 8.5244 | 8.0643 | 7.5036 | 7.1491 | 6.7492 | 6.3923 | 6.0274 | 5.5707 | 5.0864 | 4.1589 | -1.0831 | -5.455 | -8.2035 | 6.3989 | 6.088 | 5.7175 | 5.2198 | 4.8415 | 4.4334 | 3.9933 | 3.5261 | 2.9304 | 2.2703 | 0.79656 | -3.803 | -7.8764 | -10.8801 | 2.3819 | 1.955 | 2.339 | 0.7888 | 0.29937 | -0.22009 | -0.76357 | -1.3475 | -2.0742 | -2.8823 | -4.6146 | -9.9815 | -14.4189 | -17.1192
|  | STANTON FITZWARREN | FS |  |  | 8.7924 | 8.3751 | 7.8208 | 7.1886 | 6.6799 | 5.96 | 5.1632 | 3.9258 | 1.1379 | -2.1865 | -9.8552 | -26.737 | -35.5254 | -39.6813 | 6.3978 | 6.0815 | 5.7349 | 5.3104 | 4.9272 | 4.5176 | 4.0762 | 3.5529 | 2.9441 | 2.2792 | 0.88542 | -2.9222 | -6.7721 | -10.4767 | 2.3926 | 1.9885 | 2.4393 | 0.98637 | 0.48611 | -0.035982 | -0.58354 | -1.2305 | -1.9742 | -2.7814 | -4.4223 | -8.8019 | -12.7621 | -15.462
LALEHAM | STAINES | STANWELL | MINIMUM HEADROOM | TQ 06003 72766 | YES | 10.6704 | 10.5252 | 10.3702 | 10.0747 | 9.7339 | 8.2865 | 6.4787 | 3.7212 | 0.7786 | -2.4444 | -9.7475 | -26.0701 | -32.7535 | -34.0386 | 12.7326 | 12.6494 | 12.5579 | 12.4012 | 12.2075 | 10.3411 | 7.8734 | 5.3354 | 2.7575 | 0.030528 | -5.9481 | -19.3182 | -24.8852 | -26.2018 | 11.038 | 10.9055 | 10.7633 | 10.4954 | 10.1835 | 8.3479 | 5.6323 | 2.7278 | -0.29249 | -3.5371 | -10.7517 | -26.8896 | -33.5599 | -34.9978
|  | STANWELL | CT |  |  | 10.8129 | 10.754 | 10.6813 | 10.473 | 10.236 | 8.9066 | 7.3372 | 5.5974 | 3.8527 | 2.1793 | -1.4942 | -12.3614 | -19.846 | -22.4688 | 12.7845 | 12.7348 | 12.6741 | 12.5549 | 12.4151 | 10.9297 | 9.1686 | 7.4122 | 5.6383 | 3.933 | 0.51292 | -8.2102 | -14.1185 | -16.2625 | 11.1635 | 11.1078 | 11.0387 | 10.8487 | 10.6308 | 9.0593 | 7.2003 | 5.3198 | 3.3564 | 1.3466 | -2.7932 | -13.5179 | -20.8334 | -23.4479
|  | STANWELL | LW |  |  | 10.6704 | 10.5252 | 10.3702 | 10.0747 | 9.7339 | 8.2865 | 6.4787 | 3.7212 | 0.7786 | -2.4444 | -9.7475 | -26.0701 | -32.7535 | -34.0386 | 12.7326 | 12.6494 | 12.5579 | 12.4012 | 12.2075 | 10.3411 | 7.8734 | 5.3354 | 2.7575 | 0.030528 | -5.9481 | -19.3182 | -24.8852 | -26.2018 | 11.038 | 10.9055 | 10.7633 | 10.4954 | 10.1835 | 8.3479 | 5.6323 | 2.7278 | -0.29249 | -3.5371 | -10.7517 | -26.8896 | -33.5599 | -34.9978
|  | STANWELL | ST |  |  | 10.8921 | 10.8769 | 10.8592 | 10.8313 | 10.784 | 9.7969 | 8.6295 | 7.3599 | 6.2178 | 5.1739 | 3.1744 | -0.30578 | -2.6327 | -4.0432 | 12.8329 | 12.8141 | 12.7915 | 12.7615 | 12.7188 | 11.5042 | 10.0785 | 8.6998 | 7.4915 | 6.4355 | 4.5597 | 1.2432 | -1.2447 | -3.1281 | 11.2365 | 11.2231 | 11.206 | 11.1784 | 11.1315 | 9.9124 | 8.4742 | 7.0261 | 5.7473 | 4.6061 | 2.5259 | -1.085 | -3.5306 | -4.94
|  | STANWELL | FS |  |  | 10.8129 | 10.754 | 10.6813 | 10.473 | 10.236 | 8.9066 | 7.3372 | 5.5974 | 3.8527 | 2.1793 | -1.4942 | -12.3614 | -19.846 | -22.4688 | 12.8318 | 12.8131 | 12.7927 | 12.7605 | 12.7198 | 11.6059 | 10.3131 | 8.9524 | 7.789 | 6.7775 | 4.9464 | 2.4183 | -0.32437 | -3.5823 | 11.2348 | 11.2244 | 11.2163 | 11.182 | 11.1365 | 10.018 | 8.7208 | 7.3098 | 6.1 | 5.0349 | 3.083 | 0.4737 | -1.8602 | -3.645
MANNINGTON GSP | SALISBURY | STAPLEFORD | MINIMUM HEADROOM | SU 06871 37078 | YES | 3.8609 | 3.6387 | 3.4076 | 3.1991 | 2.9703 | 2.6977 | 2.3788 | 1.5235 | 0.2222 | -1.346 | -4.9057 | -11.2987 | -13.4292 | -14.8365 | 4.5488 | 4.463 | 4.3739 | 4.2729 | 4.1553 | 4.0078 | 3.8273 | 3.1281 | 2.144 | 0.93878 | -1.8018 | -6.7191 | -8.2841 | -9.4317 | 2.5556 | 2.3592 | 2.158 | 1.9448 | 1.635 | 1.2439 | 0.73713 | 0.11559 | -0.8817 | -2.3914 | -5.8152 | -11.9783 | -14.0432 | -15.4468
|  | STAPLEFORD | CT |  |  | 4.0225 | 3.887 | 3.7385 | 3.5556 | 3.3323 | 3.071 | 2.5399 | 1.5235 | 0.2222 | -1.346 | -4.9057 | -11.2987 | -13.4292 | -14.8365 | 4.5962 | 4.5332 | 4.4608 | 4.3653 | 4.2453 | 4.0977 | 3.8999 | 3.1281 | 2.144 | 0.93878 | -1.8018 | -6.7191 | -8.2841 | -9.4317 | 2.6875 | 2.5757 | 2.4439 | 2.2242 | 1.9105 | 1.5044 | 0.97906 | 0.32339 | -0.8817 | -2.3914 | -5.8152 | -11.9783 | -14.0432 | -15.4468
|  | STAPLEFORD | LW |  |  | 3.8609 | 3.6387 | 3.4076 | 3.1991 | 2.9703 | 2.6977 | 2.3788 | 1.5249 | 0.38923 | -0.98983 | -4.3771 | -9.7703 | -11.4941 | -12.9122 | 4.5488 | 4.463 | 4.3739 | 4.2729 | 4.1553 | 4.0078 | 3.8273 | 3.2121 | 2.3523 | 1.3022 | -1.2922 | -5.386 | -6.7705 | -8.0603 | 2.5556 | 2.3592 | 2.158 | 1.9448 | 1.635 | 1.2439 | 0.73713 | 0.11559 | -0.71232 | -2.0341 | -5.2808 | -10.4501 | -12.1724 | -13.6579
|  | STAPLEFORD | ST |  |  | 4.1035 | 4.0077 | 3.9121 | 3.7226 | 3.5446 | 3.3584 | 3.1468 | 2.9477 | 2.7182 | 2.4806 | 1.974 | 0.58591 | -0.56321 | -1.4394 | 4.6278 | 4.5814 | 4.5322 | 4.3959 | 4.2776 | 4.1534 | 3.9986 | 3.8651 | 3.7012 | 3.5356 | 3.167 | 2.0847 | 1.0891 | 0.18366 | 2.7515 | 2.6704 | 2.5888 | 2.4039 | 2.2363 | 2.0569 | 1.8476 | 1.6586 | 1.4346 | 1.2051 | 0.71284 | -0.64436 | -1.8022 | -2.7025
|  | STAPLEFORD | FS |  |  | 4.0225 | 3.887 | 3.7385 | 3.5556 | 3.3323 | 3.071 | 2.5399 | 1.5235 | 0.2222 | -1.346 | -4.9057 | -11.2987 | -13.4292 | -14.8365 | 4.6514 | 4.6183 | 4.5841 | 4.5198 | 4.4524 | 4.3781 | 4.3 | 4.2192 | 4.1256 | 4.0264 | 3.8056 | 3.0985 | 2.4925 | 1.8829 | 2.802 | 2.7501 | 2.7003 | 2.5945 | 2.4865 | 2.3691 | 2.2475 | 2.1213 | 1.963 | 1.7977 | 1.4473 | 0.28205 | -0.53875 | -1.2174
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH | MINIMUM HEADROOM | SU 77124 94355 | YES | -1.8361 | -2.0883 | 4.0688 | 3.763 | 3.4389 | 3.0828 | 2.6938 | 2.2771 | 1.366 | -0.49399 | -5.1714 | -15.7002 | -23.124 | -27.274 | 0.4925 | 0.37006 | 6.3967 | 6.2178 | 6.0234 | 5.7961 | 5.5381 | 5.2654 | 4.469 | 3.0743 | -0.46176 | -8.3614 | -13.8942 | -17.0516 | -1.4573 | -1.696 | 4.2131 | 3.9098 | 3.5864 | 3.2267 | 2.8304 | 2.348 | 0.8849 | -0.88761 | -5.3521 | -15.3895 | -22.4571 | -26.4191
|  | STOKENCHURCH | CT |  |  | -1.631 | -1.7572 | 4.5233 | 4.2924 | 4.0324 | 3.7294 | 3.3626 | 2.9035 | 1.366 | -0.49399 | -5.1714 | -15.7002 | -23.124 | -27.274 | 0.56131 | 0.48833 | 6.5563 | 6.4264 | 6.269 | 6.0728 | 5.8173 | 5.5235 | 4.469 | 3.0743 | -0.46176 | -8.3614 | -13.8942 | -17.0516 | -1.2682 | -1.3894 | 4.6321 | 4.4075 | 4.15 | 3.8442 | 3.4662 | 2.348 | 0.8849 | -0.88761 | -5.3521 | -15.3895 | -22.4571 | -26.4191
|  | STOKENCHURCH | LW |  |  | -1.8361 | -2.0883 | 4.0688 | 3.763 | 3.4389 | 3.0828 | 2.6938 | 2.2771 | 1.8261 | 1.3258 | -1.2506 | -11.5534 | -19.391 | -21.7209 | 0.4925 | 0.37006 | 6.3967 | 6.2178 | 6.0234 | 5.7961 | 5.5381 | 5.2654 | 5.0081 | 4.7117 | 2.6112 | -5.2257 | -11.2353 | -13.0285 | -1.4573 | -1.696 | 4.2131 | 3.9098 | 3.5864 | 3.2267 | 2.8304 | 2.4085 | 1.9674 | 1.1704 | -1.6451 | -11.5027 | -19.0019 | -21.2308
|  | STOKENCHURCH | ST |  |  | -1.5529 | -1.6312 | 4.701 | 4.5374 | 4.3859 | 4.225 | 4.0212 | 3.8377 | 3.6455 | 3.4337 | 2.9614 | 1.5409 | 0.36509 | -0.51562 | 0.59815 | 0.5495 | 6.647 | 6.516 | 6.3998 | 6.2756 | 6.1069 | 5.9607 | 5.8231 | 5.6682 | 5.3185 | 4.2237 | 3.3069 | 2.495 | -1.1859 | -1.2545 | 4.825 | 4.6592 | 4.5093 | 4.3518 | 4.1494 | 3.9754 | 3.8008 | 3.6025 | 3.1575 | 1.8278 | 0.75449 | -0.015349
|  | STOKENCHURCH | FS |  |  | -1.631 | -1.7572 | 4.5233 | 4.2924 | 4.0324 | 3.7294 | 3.3626 | 2.9035 | 1.366 | -0.49399 | -5.1714 | -15.7002 | -23.124 | -27.274 | 0.60393 | 0.50719 | 6.5539 | 6.4288 | 6.2935 | 6.1051 | 5.9014 | 5.622 | 5.3087 | 4.9957 | 4.3815 | 2.6324 | 1.3827 | 0.2944 | -1.1542 | -1.267 | 4.7653 | 4.5971 | 4.4182 | 4.1929 | 3.9547 | 3.6228 | 3.2084 | 2.7986 | 2.0067 | -0.27479 | -1.754 | -2.7225
MINETY GSP | STRATTON (2 X 60) | STRATTON | MINIMUM HEADROOM | SU 16998 88837 | YES | 10.7516 | 8.7187 | 5.6912 | 4.8725 | 3.9869 | 3.0358 | 1.8699 | 0.51601 | -0.72283 | -1.8478 | -4.1626 | -8.2846 | -12.946 | -13.9758 | 14.581 | 12.4567 | 9.0897 | 8.7457 | 8.3545 | 7.9103 | 7.3564 | 6.7153 | 6.1112 | 5.533 | 4.3025 | 1.3202 | -2.3205 | -3.0178 | 9.0957 | 6.7898 | 3.2391 | 2.5535 | 1.8062 | 0.99657 | 0.0055564 | -1.1415 | -2.2183 | -3.2144 | -5.2715 | -8.9607 | -12.6585 | -13.6766
|  | STRATTON | CT |  |  | 11.9907 | 11.4438 | 10.7269 | 10.1037 | 9.4151 | 8.6235 | 7.6451 | 6.4644 | 5.0922 | 3.733 | 0.91549 | -7.7839 | -12.946 | -13.9758 | 15.8247 | 15.3647 | 14.697 | 14.4101 | 14.0837 | 13.6905 | 13.1747 | 12.5585 | 11.8562 | 11.1072 | 8.5454 | 1.3202 | -2.3205 | -3.0178 | 10.5302 | 10.005 | 9.2719 | 8.7574 | 8.1827 | 7.5153 | 6.6857 | 5.687 | 4.4931 | 3.2853 | 0.77062 | -7.7416 | -12.6585 | -13.6766
|  | STRATTON | LW |  |  | 10.7516 | 8.7187 | 5.6912 | 4.8725 | 3.9869 | 3.0358 | 1.8699 | 0.51601 | -0.72283 | -1.8478 | -4.1626 | -8.2846 | -10.7884 | -12.6758 | 14.581 | 12.4567 | 9.0897 | 8.7457 | 8.3545 | 7.9103 | 7.3564 | 6.7153 | 6.1112 | 5.533 | 4.3025 | 2.1528 | 0.63728 | -0.8497 | 9.0957 | 6.7898 | 3.2391 | 2.5535 | 1.8062 | 0.99657 | 0.0055564 | -1.1415 | -2.2183 | -3.2144 | -5.2715 | -8.9607 | -11.2931 | -13.1669
|  | STRATTON | ST |  |  | 11.2604 | 10.1204 | 7.9353 | 7.5829 | 7.2253 | 6.8466 | 6.3677 | 5.8323 | 5.3588 | 4.9148 | 3.9327 | 0.87599 | -2.0333 | -4.8761 | 14.8365 | 13.5838 | 11.038 | 10.7959 | 10.5589 | 10.3038 | 9.9764 | 9.6296 | 9.2743 | 8.9203 | 8.0717 | 5.3917 | 2.5562 | -0.60008 | 9.5887 | 8.3017 | 5.7157 | 5.4239 | 5.1344 | 4.8286 | 4.4301 | 3.9912 | 3.5767 | 3.1777 | 2.27 | -0.65763 | -3.4415 | -6.03
|  | STRATTON | FS |  |  | 11.9907 | 11.4438 | 10.7269 | 10.1037 | 9.4151 | 8.6235 | 7.6451 | 6.4644 | 5.0922 | 3.733 | 0.91549 | -7.7839 | -12.946 | -13.9758 | 15.9372 | 15.7213 | 15.4818 | 15.2445 | 14.9766 | 14.6872 | 14.282 | 13.7996 | 13.2906 | 12.7651 | 11.5882 | 8.7199 | 5.4215 | 1.025 | 10.7175 | 10.4952 | 10.252 | 9.9633 | 9.6391 | 9.2929 | 8.8188 | 8.2567 | 7.6752 | 7.0998 | 5.8478 | 2.9595 | 0.3036 | -1.9883
LALEHAM | STAINES | SUNBURY CROSS | MINIMUM HEADROOM | TQ 10053 69996 | YES | 15.6567 | 15.0847 | 14.3829 | 13.1036 | 11.7282 | 10.308 | 8.7774 | 7.195 | 2.5377 | -3.6579 | -18.2054 | -47.543 | -63.1105 | -72.2299 | 28.5199 | 28.1705 | 27.7133 | 26.9604 | 25.968 | 24.4038 | 22.339 | 19.4683 | 15.5884 | 11.0086 | 0.17339 | -21.2213 | -32.4177 | -39.1573 | 26.4922 | 25.9353 | 25.2686 | 24.1262 | 22.943 | 21.717 | 19.5573 | 15.7182 | 10.7075 | 4.8494 | -8.9446 | -36.7736 | -51.4856 | -60.1162
|  | SUNBURY CROSS | CT |  |  | 16.1475 | 15.8763 | 15.4395 | 14.4571 | 13.3438 | 11.9955 | 10.4668 | 7.85 | 2.5377 | -3.6579 | -18.2054 | -47.543 | -63.1105 | -72.2299 | 28.6309 | 28.2717 | 27.7133 | 26.9604 | 25.968 | 24.4038 | 22.339 | 19.4683 | 15.5884 | 11.0086 | 0.17339 | -21.2213 | -32.4177 | -39.1573 | 26.9479 | 26.7016 | 26.3182 | 25.412 | 24.4137 | 22.4502 | 19.5573 | 15.7182 | 10.7075 | 4.8494 | -8.9446 | -36.7736 | -51.4856 | -60.1162
|  | SUNBURY CROSS | LW |  |  | 15.6567 | 15.0847 | 14.3829 | 13.1036 | 11.7282 | 10.308 | 8.7774 | 7.195 | 5.4491 | 3.6562 | -0.036928 | -6.6197 | -9.5724 | -10.787 | 28.5199 | 28.1705 | 27.7428 | 27.1005 | 26.4333 | 25.7369 | 24.9651 | 24.1632 | 23.3238 | 22.4439 | 20.353 | 17.4409 | 16.2904 | 15.7077 | 26.4922 | 25.9353 | 25.2686 | 24.1262 | 22.943 | 21.717 | 20.3916 | 19.0182 | 17.4867 | 15.9091 | 12.6549 | 6.8188 | 4.285 | 3.286
|  | SUNBURY CROSS | ST |  |  | 16.4228 | 16.3279 | 16.0926 | 15.7812 | 15.4763 | 15.1549 | 14.7919 | 14.417 | 13.9825 | 13.4807 | 12.2979 | 8.3223 | 4.7397 | 0.66559 | 28.8003 | 28.6667 | 28.4458 | 28.1348 | 27.8237 | 27.4824 | 27.081 | 26.6697 | 26.1567 | 25.5724 | 24.2219 | 19.8955 | 14.6579 | 6.8021 | 27.221 | 27.1512 | 26.9705 | 26.6992 | 26.439 | 26.165 | 25.8452 | 25.5267 | 25.1271 | 24.6642 | 23.5887 | 18.3802 | 15.5887 | 13.1571
|  | SUNBURY CROSS | FS |  |  | 16.1475 | 15.8763 | 15.4395 | 14.4571 | 13.3438 | 11.9955 | 10.4668 | 7.85 | 2.5377 | -3.6579 | -18.2054 | -47.543 | -63.1105 | -72.2299 | 28.7713 | 28.4335 | 28.0173 | 27.5392 | 27.0062 | 26.3456 | 25.4807 | 24.3834 | 23.0817 | 21.6502 | 18.2695 | 8.5791 | -2.636 | -18.008 | 27.1297 | 26.8232 | 26.431 | 25.9215 | 25.3562 | 24.6071 | 23.6335 | 22.356 | 20.8624 | 19.2456 | 15.6988 | 6.8482 | -0.064772 | -4.6373
BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL | MINIMUM HEADROOM | SU 93757 67606 | YES | 11.177 | 11.0056 | 10.8316 | 10.5058 | 10.1231 | 9.5724 | 7.8012 | 5.4373 | 2.4627 | -1.1892 | -10.0522 | -24.8711 | -28.7582 | -31.4134 | 13.5515 | 13.4693 | 13.3762 | 13.2257 | 12.9228 | 11.9876 | 10.6446 | 8.8366 | 6.565 | 3.7609 | -3.0765 | -14.4242 | -17.2936 | -19.3263 | 11.0365 | 10.8758 | 10.707 | 10.3903 | 10.0153 | 9.0729 | 7.3795 | 5.1171 | 2.2722 | -1.2235 | -9.7136 | -23.8884 | -27.5805 | -30.1142
|  | SUNNINGHILL | CT |  |  | 11.3496 | 11.2821 | 11.2251 | 11.0443 | 10.8384 | 10.6 | 10.3239 | 9.6114 | 8.1283 | 6.3327 | 1.7165 | -12.1449 | -18.5258 | -18.7649 | 13.5992 | 13.545 | 13.4897 | 13.3944 | 13.2804 | 13.1406 | 12.7939 | 11.9632 | 10.8713 | 9.537 | 6.0616 | -4.3895 | -9.0902 | -9.1259 | 11.199 | 11.137 | 11.0805 | 10.9051 | 10.7045 | 10.4701 | 10.1568 | 9.1072 | 7.6931 | 5.9838 | 1.5803 | -11.6432 | -17.7036 | -17.8947
|  | SUNNINGHILL | LW |  |  | 11.177 | 11.0056 | 10.8316 | 10.5058 | 10.1231 | 9.5724 | 7.8012 | 5.4373 | 2.4627 | -1.1892 | -10.0522 | -24.8711 | -28.7582 | -31.4134 | 13.5515 | 13.4693 | 13.38 | 13.2257 | 12.9228 | 11.9876 | 10.6446 | 8.8366 | 6.565 | 3.7609 | -3.0765 | -14.4242 | -17.2936 | -19.3263 | 11.0365 | 10.8758 | 10.707 | 10.3903 | 10.0153 | 9.0729 | 7.3795 | 5.1171 | 2.2722 | -1.2235 | -9.7136 | -23.8884 | -27.5805 | -30.1142
|  | SUNNINGHILL | ST |  |  | 11.4169 | 11.3924 | 11.3816 | 11.361 | 11.3332 | 11.3018 | 11.2597 | 11.2095 | 11.1564 | 11.0913 | 10.9319 | 10.0461 | 9.1069 | 7.9734 | 13.6309 | 13.5976 | 13.5672 | 13.5296 | 13.4868 | 13.4374 | 13.3761 | 13.3075 | 13.2406 | 13.1626 | 12.9696 | 12.1727 | 11.3011 | 10.1273 | 11.2653 | 11.2462 | 11.2363 | 11.215 | 11.1879 | 11.1573 | 11.1157 | 11.0669 | 11.0154 | 10.9523 | 10.7963 | 9.9769 | 9.1165 | 8.0627
|  | SUNNINGHILL | FS |  |  | 11.3496 | 11.2821 | 11.2251 | 11.0443 | 10.8384 | 10.6 | 10.3239 | 9.6114 | 8.1283 | 6.3327 | 1.7165 | -12.1449 | -18.5258 | -18.7649 | 13.5559 | 13.4721 | 13.3762 | 13.2591 | 13.1099 | 12.9205 | 12.6803 | 12.377 | 12.0296 | 11.6093 | 10.459 | 6.3304 | 2.4286 | -0.17407 | 11.184 | 11.1103 | 11.0323 | 10.9099 | 10.7519 | 10.5518 | 10.2984 | 9.9736 | 9.5742 | 9.0985 | 7.8054 | 3.0977 | -1.2285 | -3.5011
MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER | MINIMUM HEADROOM | ST 93394 80051 | YES | 3.0522 | 2.9426 | 2.8179 | 2.7129 | 2.5823 | 2.4378 | 2.2566 | 2.044 | 1.7391 | 1.19 | -0.28125 | -6.2398 | -13.7278 | -17.9137 | 4.0874 | 4.0408 | 3.9858 | 3.9314 | 3.8599 | 3.7725 | 3.6568 | 3.5116 | 3.3174 | 3.0032 | 1.8676 | -2.6584 | -8.5948 | -12.0239 | 3.0428 | 2.9476 | 2.8385 | 2.7437 | 2.6247 | 2.4899 | 2.3187 | 2.1143 | 1.8515 | 1.5329 | 0.1605 | -5.5241 | -12.7709 | -16.8837
|  | SUTTON BENGER | CT |  |  | 3.1476 | 3.0844 | 3.0064 | 2.9111 | 2.7954 | 2.6639 | 2.4919 | 2.2947 | 1.8019 | 1.19 | -0.28125 | -2.7906 | -3.6868 | -4.3166 | 4.1187 | 4.0847 | 4.0417 | 3.9859 | 3.9129 | 3.8225 | 3.6992 | 3.555 | 3.3672 | 3.0032 | 1.8676 | -0.070337 | -0.74484 | -1.2879 | 3.1247 | 3.0698 | 3.0014 | 2.9155 | 2.8091 | 2.6859 | 2.5219 | 2.3338 | 2.0777 | 1.5329 | 0.1605 | -2.2767 | -3.1616 | -3.8084
|  | SUTTON BENGER | LW |  |  | 3.0522 | 2.9426 | 2.8179 | 2.7129 | 2.5823 | 2.4378 | 2.2566 | 2.044 | 1.7391 | 1.2031 | -0.27246 | -6.2398 | -13.7278 | -17.9137 | 4.0874 | 4.0408 | 3.9858 | 3.9314 | 3.8599 | 3.7725 | 3.6568 | 3.5116 | 3.3174 | 3.0814 | 1.9641 | -2.6584 | -8.5948 | -12.0239 | 3.0428 | 2.9476 | 2.8385 | 2.7437 | 2.6247 | 2.4899 | 2.3187 | 2.1143 | 1.8515 | 1.5386 | 0.20704 | -5.5241 | -12.7709 | -16.8837
|  | SUTTON BENGER | ST |  |  | 3.1839 | 3.1346 | 3.091 | 2.9989 | 2.9134 | 2.821 | 2.7142 | 2.6129 | 2.4777 | 2.3345 | 1.981 | 0.8542 | -0.049708 | -0.55536 | 4.1338 | 4.1081 | 4.0818 | 4.0127 | 3.9506 | 3.8836 | 3.7979 | 3.7201 | 3.6085 | 3.4902 | 3.1907 | 2.1916 | 1.3359 | 0.68552 | 3.1554 | 3.1129 | 3.0746 | 2.9833 | 2.9006 | 2.8116 | 2.705 | 2.6064 | 2.4684 | 2.3252 | 1.9733 | 0.85476 | -0.047494 | -0.60435
|  | SUTTON BENGER | FS |  |  | 3.1476 | 3.0844 | 3.0064 | 2.9111 | 2.7954 | 2.6639 | 2.4919 | 2.2947 | 1.8019 | 1.19 | -0.28125 | -2.7906 | -3.6868 | -4.3166 | 4.142 | 4.1191 | 4.0958 | 4.0607 | 4.0213 | 3.9757 | 3.9236 | 3.8682 | 3.7986 | 3.72 | 3.5353 | 2.8935 | 2.2077 | 1.5943 | 3.1778 | 3.1464 | 3.1187 | 3.0674 | 3.0112 | 2.9476 | 2.8776 | 2.8071 | 2.711 | 2.603 | 2.3666 | 1.5463 | 0.78285 | 0.2188
IVER 132KV | UPTON BSP | SUTTON LANE | MINIMUM HEADROOM | TQ 02185 78595 | YES | 12.306 | 12.114 | 11.8805 | 11.4173 | 10.8546 | 10.1728 | 9.3 | 7.5517 | 4.9655 | 1.7694 | -6.156 | -24.3052 | -30.9626 | -32.1723 | 12.9499 | 12.8383 | 12.6944 | 12.4269 | 12.0746 | 11.6073 | 10.9803 | 9.5167 | 7.547 | 5.0978 | -1.0048 | -15.0002 | -20.1127 | -21.0367 | 11.6763 | 11.5103 | 11.3004 | 10.8952 | 10.3852 | 9.7391 | 8.8936 | 7.2442 | 4.7683 | 1.7062 | -5.8917 | -23.287 | -29.6567 | -30.8101
|  | SUTTON LANE | CT |  |  | 12.5015 | 12.4231 | 12.3281 | 12.0335 | 11.6838 | 11.2606 | 10.7322 | 10.0773 | 9.1688 | 8.1299 | 5.5497 | -0.30068 | -2.7061 | -3.978 | 12.9853 | 12.8858 | 12.7569 | 12.5314 | 12.2417 | 11.8648 | 11.3698 | 10.7383 | 9.918 | 8.9416 | 6.6458 | 1.4972 | -2.1338 | -6.8828 | 11.8169 | 11.735 | 11.6266 | 11.3573 | 11.017 | 10.581 | 10.0091 | 9.2762 | 8.293 | 7.1337 | 4.4434 | -1.0569 | -3.1876 | -4.3412
|  | SUTTON LANE | LW |  |  | 12.306 | 12.114 | 11.8805 | 11.4173 | 10.8546 | 10.1728 | 9.3 | 7.5517 | 4.9655 | 1.7694 | -6.156 | -24.3052 | -30.9626 | -32.1723 | 12.9499 | 12.8394 | 12.6956 | 12.4269 | 12.0746 | 11.6073 | 10.9803 | 9.5167 | 7.547 | 5.0978 | -1.0048 | -15.0002 | -20.1127 | -21.0367 | 11.6763 | 11.5103 | 11.3004 | 10.8952 | 10.3852 | 9.7391 | 8.8936 | 7.2442 | 4.7683 | 1.7062 | -5.8917 | -23.287 | -29.6567 | -30.8101
|  | SUTTON LANE | ST |  |  | 12.5759 | 12.554 | 12.5195 | 12.4405 | 12.3509 | 12.2308 | 12.0611 | 11.8568 | 11.6158 | 11.2878 | 10.3169 | 5.0451 | 2.0827 | 1.5197 | 13.0215 | 12.9565 | 12.8737 | 12.7294 | 12.5679 | 12.3691 | 12.1086 | 11.8032 | 11.4306 | 10.9586 | 9.6347 | 4.4633 | 0.19319 | -3.9104 | 11.8753 | 11.844 | 11.7976 | 11.6947 | 11.5759 | 11.4187 | 11.1964 | 10.9231 | 10.5926 | 10.1496 | 8.843 | 3.6525 | 0.78361 | 0.32329
|  | SUTTON LANE | FS |  |  | 12.5015 | 12.4231 | 12.3281 | 12.0335 | 11.6838 | 11.2606 | 10.7322 | 10.0773 | 9.1688 | 8.1299 | 5.5497 | -0.30068 | -2.7061 | -3.978 | 12.9589 | 12.8383 | 12.6944 | 12.5005 | 12.2771 | 11.9799 | 11.634 | 11.1714 | 10.5854 | 9.9489 | 8.4491 | 2.7486 | -5.3226 | -15.9661 | 11.8001 | 11.7083 | 11.5987 | 11.4417 | 11.2612 | 11.0019 | 10.6998 | 10.2669 | 9.735 | 9.1721 | 7.8787 | 3.1004 | -1.952 | -4.952
MANNINGTON GSP | WAREHAM | SWANAGE | MINIMUM HEADROOM | SZ 02010 79296 | YES | -1.2654 | -1.5193 | -1.8227 | -2.3564 | -2.9924 | -3.7329 | -5.3363 | -8.698 | -13.1561 | -18.5877 | -31.2603 | -54.5982 | -61.8758 | -66.8589 | 1.8567 | 1.6019 | 1.2179 | 0.62357 | -0.23773 | -1.4802 | -3.22 | -5.6198 | -8.9744 | -13.1014 | -22.7778 | -40.3099 | -45.4803 | -49.2114 | -0.016104 | -0.25516 | -0.53432 | -1.0346 | -1.624 | -2.3073 | -3.1109 | -6.2572 | -10.5093 | -15.701 | -27.8227 | -50.0921 | -56.9989 | -61.7802
|  | SWANAGE | CT |  |  | -1.022 | -1.1599 | -1.3604 | -1.8271 | -2.4184 | -3.153 | -5.3363 | -8.698 | -13.1561 | -18.5877 | -31.2603 | -54.5982 | -61.8758 | -66.8589 | 1.8567 | 1.6019 | 1.2179 | 0.62357 | -0.23773 | -1.4802 | -3.22 | -5.6198 | -8.9744 | -13.1014 | -22.7778 | -40.3099 | -45.4803 | -49.2114 | 0.21407 | 0.080991 | -0.11 | -0.56151 | -1.1331 | -1.8491 | -3.0466 | -6.2572 | -10.5093 | -15.701 | -27.8227 | -50.0921 | -56.9989 | -61.7802
|  | SWANAGE | LW |  |  | -1.2654 | -1.5193 | -1.8227 | -2.3564 | -2.9924 | -3.7329 | -4.6052 | -5.6352 | -6.9298 | -8.4049 | -14.3671 | -24.4939 | -27.9366 | -30.3236 | 1.9439 | 1.7868 | 1.5828 | 1.2779 | 0.84903 | 0.26799 | -0.54235 | -1.6144 | -2.9765 | -4.7398 | -9.2324 | -16.6258 | -19.0865 | -21.0706 | -0.016104 | -0.25516 | -0.53432 | -1.0346 | -1.624 | -2.3073 | -3.1109 | -4.0584 | -5.2629 | -6.632 | -11.5465 | -21.1794 | -24.489 | -26.8877
|  | SWANAGE | ST |  |  | -0.86668 | -0.89273 | -0.9485 | -1.0409 | -1.1705 | -1.328 | -1.5219 | -1.7574 | -2.0701 | -2.4484 | -3.4671 | -7.6368 | -10.9098 | -13.3476 | 2.1055 | 2.0876 | 2.059 | 2.0164 | 1.9595 | 1.8922 | 1.8129 | 1.721 | 1.4377 | 1.0819 | 0.12244 | -3.5849 | -6.9038 | -10.1803 | 0.36311 | 0.33899 | 0.2904 | 0.21082 | 0.098862 | -0.040492 | -0.21627 | -0.43553 | -0.73851 | -1.1074 | -2.1178 | -6.2043 | -9.3233 | -11.4655
|  | SWANAGE | FS |  |  | -1.022 | -1.1599 | -1.3604 | -1.8271 | -2.4184 | -3.153 | -5.3363 | -8.698 | -13.1561 | -18.5877 | -31.2603 | -54.5982 | -61.8758 | -66.8589 | 2.1001 | 2.0767 | 2.045 | 1.9964 | 1.9332 | 1.7517 | 1.4251 | 1.0288 | 0.54518 | -0.0065199 | -1.3149 | -5.2751 | -10.1999 | -16.0993 | 0.30085 | 0.21185 | 0.10646 | -0.051103 | -0.26426 | -0.49711 | -0.84716 | -1.2709 | -1.801 | -2.4 | -3.7897 | -7.7933 | -11.7086 | -14.3253
MINETY GSP | SWINDON BSP | SWINDON | MINIMUM HEADROOM | SU 12449 86967 | YES | 26.4214 | 25.8164 | 25.1977 | 23.9256 | 22.5968 | 21.2075 | 19.7089 | 18.0888 | 12.9834 | 5.6045 | -13.0636 | -56.7446 | -87.6604 | -105.789 | 29.7203 | 29.4515 | 29.1745 | 28.6345 | 28.0535 | 27.3826 | 26.4183 | 25.2334 | 23.4865 | 18.1955 | 4.3317 | -27.7078 | -50.5191 | -64.0812 | 24.7704 | 24.2369 | 23.6782 | 22.5102 | 21.2891 | 20.0122 | 18.6306 | 17.1347 | 12.2631 | 5.2527 | -12.5237 | -53.9985 | -83.3683 | -100.6181
|  | SWINDON | CT |  |  | 27.1539 | 26.898 | 26.5951 | 25.5901 | 24.4821 | 23.2189 | 21.7735 | 19.1008 | 12.9834 | 5.6045 | -13.0636 | -56.7446 | -87.6604 | -105.789 | 29.9139 | 29.6893 | 29.4146 | 28.8453 | 28.1833 | 27.3826 | 26.4183 | 25.2334 | 23.4865 | 18.1955 | 4.3317 | -27.7078 | -50.5191 | -64.0812 | 25.4092 | 25.178 | 24.9012 | 23.987 | 22.9408 | 21.7367 | 20.3465 | 18.0572 | 12.2631 | 5.2527 | -12.5237 | -53.9985 | -83.3683 | -100.6181
|  | SWINDON | LW |  |  | 26.4214 | 25.8164 | 25.1977 | 23.9256 | 22.5968 | 21.2075 | 19.7089 | 18.0888 | 16.072 | 13.9182 | 9.1682 | -7.9177 | -24.2424 | -30.1886 | 29.7203 | 29.4515 | 29.1745 | 28.6345 | 28.0535 | 27.4282 | 26.7185 | 25.9219 | 24.9095 | 23.7924 | 21.2216 | 10.7555 | -1.3013 | -5.8267 | 24.7704 | 24.2369 | 23.6782 | 22.5102 | 21.2891 | 20.0122 | 18.6306 | 17.1347 | 15.2626 | 13.2599 | 8.8324 | -7.0805 | -22.6043 | -28.3167
|  | SWINDON | ST |  |  | 27.435 | 27.358 | 27.2734 | 27.1313 | 26.964 | 26.7695 | 26.538 | 26.2569 | 25.9148 | 25.5286 | 24.5522 | 18.5187 | 12.3474 | 5.9074 | 30.0664 | 29.9524 | 29.8207 | 29.6675 | 29.4879 | 29.2768 | 29.0271 | 28.7308 | 28.3458 | 27.9073 | 26.7465 | 21.5246 | 15.3827 | 7.4416 | 25.6623 | 25.5947 | 25.5194 | 25.3921 | 25.2412 | 25.0638 | 24.8502 | 24.5878 | 24.2579 | 23.8847 | 22.9345 | 17.5134 | 11.9487 | 6.3341
|  | SWINDON | FS |  |  | 27.1539 | 26.898 | 26.5951 | 25.5901 | 24.4821 | 23.2189 | 21.7735 | 19.1008 | 12.9834 | 5.6045 | -13.0636 | -56.7446 | -87.6604 | -105.789 | 30.0381 | 29.9004 | 29.7399 | 29.5331 | 29.2929 | 29.02 | 28.6963 | 28.3196 | 27.7135 | 27.0188 | 25.2667 | 18.1797 | 7.6294 | -6.9994 | 25.6398 | 25.567 | 25.4857 | 25.2543 | 24.9904 | 24.6994 | 24.3583 | 23.9627 | 23.3533 | 22.6784 | 21.03 | 14.0505 | 5.76 | -1.2165
BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY | MINIMUM HEADROOM | SU 57753 62717 | YES | 14.2865 | 14.04 | 13.7536 | 13.2504 | 12.6407 | 11.9049 | 10.6202 | 8.1563 | 4.8491 | 0.73039 | -10.1721 | -43.3371 | -58.376 | -58.5754 | 15.3508 | 15.2147 | 15.0429 | 14.7522 | 14.3371 | 13.7696 | 13.0035 | 11.7042 | 9.2188 | 6.0946 | -2.254 | -27.695 | -39.0743 | -39.0434 | 13.3287 | 13.1037 | 12.8412 | 12.3784 | 11.8108 | 11.1017 | 9.9679 | 7.6077 | 4.4498 | 0.51108 | -9.9293 | -41.6747 | -56.0272 | -56.1746
|  | TADLEY | CT |  |  | 14.4631 | 14.3009 | 14.0836 | 13.6242 | 13.0389 | 12.2772 | 10.6202 | 8.1563 | 4.8491 | 0.73039 | -10.1721 | -43.3371 | -58.376 | -58.5754 | 15.3796 | 15.2458 | 15.0605 | 14.7522 | 14.3371 | 13.7696 | 13.0035 | 11.7042 | 9.2188 | 6.0946 | -2.254 | -27.695 | -39.0743 | -39.0434 | 13.4834 | 13.3255 | 13.109 | 12.6758 | 12.1113 | 11.3624 | 9.9679 | 7.6077 | 4.4498 | 0.51108 | -9.9293 | -41.6747 | -56.0272 | -56.1746
|  | TADLEY | LW |  |  | 14.2865 | 14.04 | 13.7536 | 13.2504 | 12.6407 | 11.9049 | 10.9686 | 9.7878 | 8.2946 | 6.5206 | 0.90467 | -8.5233 | -11.143 | -12.8135 | 15.3508 | 15.2147 | 15.0429 | 14.7623 | 14.3928 | 13.9064 | 13.2476 | 12.3792 | 11.2834 | 9.9405 | 6.5735 | -0.31523 | -2.1194 | -3.3671 | 13.3287 | 13.1037 | 12.8412 | 12.3784 | 11.8108 | 11.1017 | 10.174 | 8.9846 | 7.4815 | 5.6737 | 0.74859 | -8.2296 | -10.6915 | -12.2782
|  | TADLEY | ST |  |  | 14.5885 | 14.5398 | 14.4599 | 14.354 | 14.2144 | 14.0247 | 13.7628 | 13.4102 | 12.9644 | 12.3772 | 10.4791 | 2.5115 | -2.2035 | -3.2285 | 15.4545 | 15.395 | 15.3115 | 15.2057 | 15.0648 | 14.8745 | 14.6165 | 14.2705 | 13.8341 | 13.2647 | 11.608 | 5.2426 | 1.4763 | 0.36863 | 13.5932 | 13.5395 | 13.455 | 13.341 | 13.188 | 12.9785 | 12.6883 | 12.2955 | 11.7954 | 11.1366 | 9.2127 | 1.6248 | -2.8442 | -3.9154
|  | TADLEY | FS |  |  | 14.4631 | 14.3009 | 14.0836 | 13.6242 | 13.0389 | 12.2772 | 10.6202 | 8.1563 | 4.8491 | 0.73039 | -10.1721 | -43.3371 | -58.376 | -58.5754 | 15.3901 | 15.2676 | 15.1212 | 14.9535 | 14.7455 | 14.4792 | 14.1142 | 13.6213 | 13.0258 | 12.3591 | 10.752 | 5.214 | -0.81248 | -4.9261 | 13.5211 | 13.3984 | 13.2449 | 13.046 | 12.8025 | 12.4937 | 12.0687 | 11.4942 | 10.7748 | 9.9758 | 8.069 | 1.4933 | -5.4073 | -9.3421
IVER 132KV | SLOUGH | TAPLOW | MINIMUM HEADROOM | SU 91721 81234 | YES | 8.3772 | 7.8768 | 7.5912 | 7.0079 | 6.3083 | 5.4715 | 4.4726 | 2.231 | -1.0898 | -5.1378 | -14.9242 | -36.1932 | -45.9683 | -50.2104 | 12.6175 | 12.3885 | 12.2503 | 11.9533 | 11.5778 | 10.969 | 9.4033 | 7.3588 | 4.8654 | 1.8 | -5.6573 | -21.8626 | -29.2654 | -32.5207 | 10.2021 | 9.7809 | 9.5034 | 8.9197 | 8.2251 | 7.3929 | 6.217 | 3.6268 | 0.45731 | -3.4111 | -12.7712 | -33.1099 | -42.4358 | -46.484
|  | TAPLOW | CT |  |  | 8.6331 | 8.3202 | 8.184 | 7.7839 | 7.2975 | 6.6959 | 5.9477 | 5.0773 | 3.8036 | 1.1947 | -5.4569 | -22.8121 | -33.2965 | -37.3052 | 12.6734 | 12.49 | 12.3767 | 12.161 | 11.8799 | 11.5138 | 11.0332 | 10.1325 | 8.5561 | 6.6446 | 1.6961 | -11.182 | -18.9152 | -21.8247 | 10.456 | 10.2107 | 10.0818 | 9.6946 | 9.2307 | 8.6606 | 7.9542 | 7.1349 | 5.1763 | 2.6974 | -3.6376 | -20.1533 | -30.1113 | -33.8993
|  | TAPLOW | LW |  |  | 8.3772 | 7.8768 | 7.5912 | 7.0079 | 6.3083 | 5.4715 | 4.4726 | 2.231 | -1.0898 | -5.1378 | -14.9242 | -36.1932 | -45.9683 | -50.2104 | 12.6175 | 12.3885 | 12.2503 | 11.9533 | 11.5778 | 10.969 | 9.4033 | 7.3588 | 4.8654 | 1.8 | -5.6573 | -21.8626 | -29.2654 | -32.5207 | 10.2021 | 9.7809 | 9.5034 | 8.9197 | 8.2251 | 7.3929 | 6.217 | 3.6268 | 0.45731 | -3.4111 | -12.7712 | -33.1099 | -42.4358 | -46.484
|  | TAPLOW | ST |  |  | 8.7564 | 8.518 | 8.4795 | 8.3576 | 8.2116 | 8.0297 | 7.7754 | 7.5121 | 7.2114 | 6.8545 | 5.8488 | 1.7392 | -1.0807 | -2.7374 | 12.7259 | 12.5793 | 12.5179 | 12.371 | 12.2164 | 12.033 | 11.7827 | 11.5257 | 11.2512 | 10.918 | 9.9971 | 6.5103 | 4.0009 | 2.1763 | 10.5875 | 10.4214 | 10.3948 | 10.2753 | 10.1463 | 9.9925 | 9.7495 | 9.4909 | 9.2022 | 8.8551 | 7.8742 | 3.9211 | 1.2955 | -0.11637
|  | TAPLOW | FS |  |  | 8.6331 | 8.3202 | 8.184 | 7.7839 | 7.2975 | 6.6959 | 5.9477 | 5.0773 | 3.8036 | 1.1947 | -5.4569 | -22.8121 | -33.2965 | -37.3052 | 12.6885 | 12.5342 | 12.4443 | 12.3197 | 12.1586 | 11.9574 | 11.7179 | 11.427 | 11.0908 | 10.6882 | 9.6088 | 5.3632 | 0.35792 | -3.9915 | 10.5493 | 10.3973 | 10.35 | 10.2345 | 10.0845 | 9.8673 | 9.6137 | 9.3024 | 8.9177 | 8.4621 | 7.2683 | 2.5492 | -2.6845 | -6.0753
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON | MINIMUM HEADROOM | ST 94510 07307 | YES | 1.5236 | 1.4665 | 1.3898 | 1.2309 | 1.0199 | 0.024185 | -1.391 | -3.2998 | -5.6741 | -8.6318 | -16.1572 | -28.297 | -31.2261 | -33.3736 | 1.8627 | 1.6941 | 1.458 | 1.0903 | 0.55287 | -0.21054 | -1.2957 | -2.7649 | -4.5973 | -6.8871 | -12.7324 | -22.1225 | -24.3641 | -26.0404 | 1.9024 | 1.8146 | 1.6544 | 1.1909 | 0.51742 | -0.43621 | -1.7859 | -3.6088 | -5.8784 | -8.708 | -15.9134 | -27.5258 | -30.322 | -32.3807
|  | TARRANT RUSHTON | CT |  |  | 1.5713 | 1.5509 | 1.5166 | 1.4129 | 1.2799 | 1.1241 | 0.83805 | -0.079678 | -1.2663 | -2.6949 | -5.9991 | -11.7359 | -13.2829 | -14.3158 | 1.947 | 1.8668 | 1.7499 | 1.5614 | 1.2965 | 0.92 | 0.41183 | -0.28581 | -1.1817 | -2.2658 | -4.7816 | -9.1392 | -10.2656 | -11.045 | 1.9542 | 1.9094 | 1.8415 | 1.7259 | 1.4581 | 0.98273 | 0.34415 | -0.52887 | -1.6571 | -3.017 | -6.1647 | -11.6352 | -13.1009 | -14.0846
|  | TARRANT RUSHTON | LW |  |  | 1.5236 | 1.4676 | 1.3924 | 1.2309 | 1.0199 | 0.024185 | -1.391 | -3.2998 | -5.6741 | -8.6318 | -16.1572 | -28.297 | -31.2261 | -33.3736 | 1.8627 | 1.6941 | 1.458 | 1.0903 | 0.55287 | -0.21054 | -1.2957 | -2.7649 | -4.5973 | -6.8871 | -12.7324 | -22.1225 | -24.3641 | -26.0404 | 1.9024 | 1.8146 | 1.6544 | 1.1909 | 0.51742 | -0.43621 | -1.7859 | -3.6088 | -5.8784 | -8.708 | -15.9134 | -27.5258 | -30.322 | -32.3807
|  | TARRANT RUSHTON | ST |  |  | 1.5262 | 1.4665 | 1.3898 | 1.2615 | 1.1056 | 0.91955 | 0.69207 | 0.39083 | 0.052084 | -0.30589 | -1.0421 | -2.3635 | -2.8257 | -2.9227 | 2.0174 | 2.004 | 1.9833 | 1.9387 | 1.8837 | 1.8202 | 1.7201 | 1.4967 | 1.2443 | 0.97862 | 0.43304 | -0.59053 | -0.98753 | -1.1625 | 1.9356 | 1.8836 | 1.8165 | 1.7056 | 1.5712 | 1.4106 | 1.2153 | 0.95696 | 0.66737 | 0.36012 | -0.2768 | -1.5974 | -2.0487 | -2.1188
|  | TARRANT RUSHTON | FS |  |  | 1.5713 | 1.5509 | 1.5166 | 1.4129 | 1.2799 | 1.1241 | 0.83805 | -0.079678 | -1.2663 | -2.6949 | -5.9991 | -11.7359 | -13.2829 | -14.3158 | 2.0253 | 2.0206 | 2.0089 | 1.9779 | 1.9409 | 1.8992 | 1.8533 | 1.803 | 1.7447 | 1.6813 | 1.5298 | 1.0838 | 0.73594 | 0.52289 | 1.9869 | 1.9825 | 1.9652 | 1.9147 | 1.8586 | 1.7954 | 1.7299 | 1.6621 | 1.5761 | 1.4863 | 1.2897 | 0.73767 | 0.3149 | 0.018109
MANNINGTON GSP | SALISBURY | TEFFONT | MINIMUM HEADROOM | ST 99837 30994 | YES | -1.6041 | -1.7568 | -1.938 | -2.111 | -2.3374 | -2.6764 | -3.3132 | -4.215 | -5.3492 | -6.7446 | -10.255 | -17.362 | -29.6932 | -36.3047 | -0.64485 | -0.72064 | -0.81687 | -0.9277 | -1.0816 | -1.2962 | -1.5948 | -2.0274 | -2.7271 | -3.8042 | -6.5236 | -11.9959 | -21.6405 | -26.8228 | -1.5202 | -1.6504 | -1.8082 | -1.9678 | -2.1808 | -2.4698 | -2.8774 | -3.7415 | -4.8286 | -6.1674 | -9.5371 | -16.3519 | -28.188 | -34.5363
|  | TEFFONT | CT |  |  | -1.519 | -1.6294 | -1.7663 | -1.9461 | -2.2296 | -2.6764 | -3.3132 | -4.215 | -5.3492 | -6.7446 | -10.255 | -15.9809 | -17.5222 | -18.5976 | -0.61696 | -0.68096 | -0.76679 | -0.8846 | -1.0485 | -1.2782 | -1.5948 | -2.0274 | -2.7271 | -3.8042 | -6.5236 | -10.9397 | -12.0547 | -12.8719 | -1.4529 | -1.5495 | -1.6722 | -1.8368 | -2.0576 | -2.3584 | -2.8774 | -3.7415 | -4.8286 | -6.1674 | -9.5371 | -15.0298 | -16.4927 | -17.5207
|  | TEFFONT | LW |  |  | -1.6041 | -1.7568 | -1.938 | -2.111 | -2.3374 | -2.6398 | -3.0436 | -3.5666 | -4.2172 | -5.024 | -7.4148 | -17.362 | -29.6932 | -36.3047 | -0.64485 | -0.72064 | -0.81687 | -0.9277 | -1.0816 | -1.2962 | -1.5932 | -1.9897 | -2.486 | -3.1082 | -4.7273 | -11.9959 | -21.6405 | -26.8228 | -1.5202 | -1.6504 | -1.8082 | -1.9678 | -2.1808 | -2.4698 | -2.8608 | -3.373 | -4.0116 | -4.8067 | -6.8575 | -16.3519 | -28.188 | -34.5363
|  | TEFFONT | ST |  |  | -1.4768 | -1.5482 | -1.6371 | -1.751 | -1.8952 | -2.0681 | -2.2849 | -2.5531 | -2.8831 | -3.2968 | -4.4564 | -8.6103 | -11.0589 | -11.3757 | -0.59996 | -0.64182 | -0.69601 | -0.76633 | -0.85874 | -0.97688 | -1.1314 | -1.3315 | -1.5796 | -1.8968 | -2.8097 | -6.2088 | -8.2402 | -8.5223 | -1.4199 | -1.4827 | -1.5622 | -1.6654 | -1.798 | -1.9605 | -2.1678 | -2.4291 | -2.7536 | -3.1638 | -4.3257 | -8.5259 | -10.9838 | -11.2625
|  | TEFFONT | FS |  |  | -1.519 | -1.6294 | -1.7663 | -1.9461 | -2.2296 | -2.6764 | -3.3132 | -4.215 | -5.3492 | -6.7446 | -10.255 | -15.9809 | -17.5222 | -18.5976 | -0.59212 | -0.63244 | -0.68183 | -0.74336 | -0.81617 | -0.91263 | -1.0273 | -1.1811 | -1.3631 | -1.5717 | -2.1072 | -4.3386 | -6.9172 | -8.3386 | -1.3991 | -1.4543 | -1.521 | -1.6113 | -1.7157 | -1.8491 | -2.0043 | -2.2074 | -2.4513 | -2.7294 | -3.4281 | -6.3065 | -9.4775 | -11.1774
BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM | MINIMUM HEADROOM | SU 84178 83872 | YES | 0.97556 | 0.8487 | 0.6136 | 0.25801 | -0.24617 | -0.95805 | -2.0017 | -3.4161 | -5.2002 | -7.4915 | -13.7183 | -32.2763 | -40.3915 | -40.3411 | 1.4975 | 1.3765 | 1.207 | 0.9151 | 0.49022 | -0.10876 | -0.94454 | -2.0685 | -3.4716 | -5.2736 | -10.1712 | -24.7662 | -31.1357 | -31.092 | 1.0139 | 0.86158 | 0.63571 | 0.28636 | -0.20701 | -0.91027 | -1.9264 | -3.2975 | -5.0166 | -7.2241 | -13.2211 | -31.0754 | -38.8741 | -38.8279
|  | TEMPLE FARM | CT |  |  | 1.0392 | 0.96587 | 0.86501 | 0.70129 | 0.4519 | 0.054199 | -0.53532 | -1.3377 | -2.3573 | -3.6246 | -6.6955 | -17.0432 | -25.6987 | -28.3524 | 1.5577 | 1.4883 | 1.3937 | 1.2579 | 1.068 | 0.80196 | 0.41507 | -0.16711 | -0.99478 | -2.0256 | -4.5176 | -12.7013 | -19.4783 | -21.5585 | 1.0896 | 1.0036 | 0.88699 | 0.717 | 0.47477 | 0.078477 | -0.50013 | -1.2842 | -2.2772 | -3.5257 | -6.5684 | -16.3829 | -24.6955 | -27.2463
|  | TEMPLE FARM | LW |  |  | 0.97556 | 0.8487 | 0.6136 | 0.25801 | -0.24617 | -0.95805 | -2.0017 | -3.4161 | -5.2002 | -7.4915 | -13.7183 | -32.2763 | -40.3915 | -40.3411 | 1.4975 | 1.3765 | 1.207 | 0.9151 | 0.49022 | -0.10876 | -0.94454 | -2.0685 | -3.4716 | -5.2736 | -10.1712 | -24.7662 | -31.1357 | -31.092 | 1.0139 | 0.86158 | 0.63571 | 0.28636 | -0.20701 | -0.91027 | -1.9264 | -3.2975 | -5.0166 | -7.2241 | -13.2211 | -31.0754 | -38.8741 | -38.8279
|  | TEMPLE FARM | ST |  |  | 1.0901 | 0.9732 | 0.79054 | 0.53563 | 0.22442 | -0.1843 | -0.76203 | -1.5336 | -2.4502 | -3.5266 | -6.2702 | -14.9172 | -18.863 | -18.4453 | 1.612 | 1.5876 | 1.5341 | 1.3201 | 1.0641 | 0.72711 | 0.24063 | -0.40199 | -1.1583 | -2.0496 | -4.3215 | -11.3188 | -14.5156 | -14.2368 | 1.133 | 0.9852 | 0.80882 | 0.55418 | 0.24801 | -0.15151 | -0.71674 | -1.482 | -2.3932 | -3.4641 | -6.1937 | -14.8017 | -18.7257 | -18.3026
|  | TEMPLE FARM | FS |  |  | 1.0392 | 0.96587 | 0.86501 | 0.70129 | 0.4519 | 0.054199 | -0.53532 | -1.3377 | -2.3573 | -3.6246 | -6.6955 | -17.0432 | -25.6987 | -28.3524 | 1.6257 | 1.6152 | 1.6019 | 1.5761 | 1.5446 | 1.4224 | 1.2306 | 0.9893 | 0.71217 | 0.36007 | -0.62935 | -4.6808 | -9.4228 | -11.8357 | 1.1732 | 1.1598 | 1.088 | 0.98216 | 0.84637 | 0.67758 | 0.44548 | 0.1565 | -0.18003 | -0.59779 | -1.7801 | -6.6635 | -12.4856 | -15.4412
MELKSHAM GSP | CHIPPENHAM | TETBURY | MINIMUM HEADROOM | ST 89708 93444 | YES | 0.75697 | 0.55655 | 0.33772 | 0.00879 | -0.42384 | -0.9755 | -1.6831 | -2.5622 | -3.6522 | -4.9796 | -8.225 | -15.144 | -20.102 | -22.9799 | 2.0298 | 1.9229 | 1.7962 | 1.6069 | 1.3435 | 0.98988 | 0.51446 | -0.1005 | -0.86684 | -1.8158 | -4.1984 | -8.9572 | -12.6451 | -14.814 | 1.2345 | 1.063 | 0.86988 | 0.57941 | 0.18834 | -0.32819 | -0.99761 | -1.8389 | -2.8853 | -4.1636 | -7.3106 | -13.7521 | -18.4591 | -21.1907
|  | TETBURY | CT |  |  | 0.90687 | 0.78881 | 0.64152 | 0.36624 | -0.00078843 | -0.48947 | -1.1238 | -1.9252 | -3.0282 | -4.3338 | -7.2961 | -13.2015 | -15.6424 | -17.1606 | 2.0782 | 1.9923 | 1.879 | 1.6982 | 1.4477 | 1.1042 | 0.64534 | 0.047284 | -0.74283 | -1.6953 | -3.8987 | -8.1382 | -9.8423 | -11.3367 | 1.3509 | 1.2429 | 1.1036 | 0.85237 | 0.51299 | 0.053803 | -0.55239 | -1.3324 | -2.3936 | -3.6612 | -6.5632 | -12.1797 | -14.3341 | -15.6993
|  | TETBURY | LW |  |  | 0.75697 | 0.55655 | 0.33772 | 0.00879 | -0.42384 | -0.9755 | -1.6831 | -2.5622 | -3.6522 | -4.9796 | -8.225 | -15.144 | -20.102 | -22.9799 | 2.0298 | 1.9229 | 1.7962 | 1.6069 | 1.3435 | 0.98988 | 0.51446 | -0.1005 | -0.86684 | -1.8158 | -4.1984 | -8.9572 | -12.6451 | -14.814 | 1.2345 | 1.063 | 0.86988 | 0.57941 | 0.18834 | -0.32819 | -0.99761 | -1.8389 | -2.8853 | -4.1636 | -7.3106 | -13.7521 | -18.4591 | -21.1907
|  | TETBURY | ST |  |  | 0.92848 | 0.84394 | 0.73584 | 0.5836 | 0.37019 | 0.084824 | -0.28237 | -0.73717 | -1.2779 | -1.9644 | -3.9043 | -11.2834 | -16.1388 | -17.6886 | 2.0768 | 2.0078 | 1.9186 | 1.8002 | 1.636 | 1.4173 | 1.1321 | 0.77054 | 0.33637 | -0.21693 | -1.7912 | -7.7873 | -11.8305 | -13.1466 | 1.362 | 1.2821 | 1.1781 | 1.0319 | 0.82841 | 0.55483 | 0.19853 | -0.25139 | -0.79261 | -1.4828 | -3.4484 | -10.8658 | -15.6642 | -16.9582
|  | TETBURY | FS |  |  | 0.90687 | 0.78881 | 0.64152 | 0.36624 | -0.00078843 | -0.48947 | -1.1238 | -1.9252 | -3.0282 | -4.3338 | -7.2961 | -13.2015 | -15.6424 | -17.1606 | 2.1234 | 2.0815 | 2.0306 | 1.9663 | 1.8829 | 1.7782 | 1.6508 | 1.5002 | 1.3089 | 1.0731 | 0.41556 | -2.6446 | -6.725 | -9.9259 | 1.4294 | 1.3896 | 1.3411 | 1.2615 | 1.1604 | 1.0319 | 0.87821 | 0.69967 | 0.46676 | 0.18088 | -0.60968 | -4.3184 | -9.0012 | -11.9057
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM | MINIMUM HEADROOM | SU 52758 66466 | YES | 4.9483 | 4.5074 | 4.1075 | 3.4075 | 2.5585 | 1.3497 | 0.19162 | -0.92837 | -2.3241 | -3.5945 | -6.3219 | -12.4639 | -17.0388 | -19.5171 | 9.4718 | 9.2373 | 9.0467 | 8.7414 | 8.3448 | 7.6809 | 7.06 | 6.4293 | 5.6302 | 4.9988 | 3.0475 | -2.164 | -5.1716 | -9.3956 | 5.5662 | 5.1539 | 4.7896 | 4.1617 | 3.4353 | 2.3987 | 1.3785 | 0.38793 | -0.84773 | -1.9778 | -4.431 | -9.9753 | -14.2309 | -16.5037
|  | THATCHAM | CT |  |  | 5.4871 | 5.3618 | 5.2273 | 4.7589 | 4.1152 | 3.007 | 2.2304 | 1.4034 | -0.10404 | -1.5353 | -4.3672 | -11.9314 | -17.0388 | -19.5171 | 9.6702 | 9.5598 | 9.4339 | 9.1763 | 8.7586 | 7.9171 | 7.3529 | 6.7509 | 5.896 | 5.0698 | 3.3945 | -1.2035 | -5.1716 | -9.3956 | 6.0578 | 5.9449 | 5.8226 | 5.4031 | 4.8193 | 3.7987 | 3.0684 | 2.2997 | 0.98014 | -0.32105 | -2.8965 | -9.6769 | -14.2309 | -16.5037
|  | THATCHAM | LW |  |  | 4.9483 | 4.5074 | 4.1075 | 3.4075 | 2.5585 | 1.3497 | 0.19162 | -0.92837 | -2.3241 | -3.5945 | -6.3219 | -12.4639 | -16.3931 | -17.8395 | 9.4718 | 9.2373 | 9.0467 | 8.7414 | 8.3448 | 7.6809 | 7.06 | 6.4293 | 5.6302 | 4.9988 | 3.0475 | -2.164 | -4.9522 | -5.8866 | 5.5662 | 5.1539 | 4.7896 | 4.1617 | 3.4353 | 2.3987 | 1.3785 | 0.38793 | -0.84773 | -1.9778 | -4.431 | -9.9753 | -13.4841 | -15.0756
|  | THATCHAM | ST |  |  | 5.6362 | 5.5977 | 5.5497 | 5.4169 | 5.1364 | 4.4333 | 4.0708 | 3.714 | 3.3022 | 3.0017 | 2.3381 | -1.0106 | -4.665 | -8.8464 | 9.7368 | 9.6678 | 9.585 | 9.4161 | 9.1252 | 8.4428 | 8.044 | 7.6579 | 7.2052 | 6.852 | 6.0705 | 2.8862 | -0.85586 | -5.6728 | 6.1912 | 6.1566 | 6.1128 | 5.9704 | 5.6992 | 5.0331 | 4.6654 | 4.3118 | 3.8955 | 3.5842 | 2.9106 | -0.29584 | -3.7342 | -7.4662
|  | THATCHAM | FS |  |  | 5.4871 | 5.3618 | 5.2273 | 4.7589 | 4.1152 | 3.007 | 2.2304 | 1.4034 | -0.10404 | -1.5353 | -4.3672 | -11.9314 | -17.0388 | -19.5171 | 9.7677 | 9.6444 | 9.5305 | 9.4007 | 9.2022 | 8.8553 | 8.5567 | 8.2482 | 7.8443 | 7.451 | 6.5892 | 3.3946 | -1.2005 | -8.4312 | 6.2364 | 6.1574 | 6.0982 | 5.9698 | 5.7771 | 5.4347 | 5.1546 | 4.8744 | 4.4679 | 4.0847 | 3.2984 | 0.37867 | -2.9361 | -6.3897
NORTH HYDE GSP | NORTH HYDE (D) | THE GREEN | MINIMUM HEADROOM | TQ 12414 79503 | YES | 2.5442 | 2.2879 | 2.0239 | 1.6131 | 1.1807 | 0.70745 | 0.27 | -0.13354 | -0.5656 | -1.0449 | -2.5884 | -5.8026 | -6.9397 | -7.4646 | 4.5154 | 4.443 | 4.3622 | 4.2682 | 4.1483 | 3.9681 | 3.7826 | 3.5754 | 3.1528 | 2.5209 | 1.1236 | -2.9215 | -7.7268 | -14.3113 | 2.9756 | 2.7774 | 2.5727 | 2.2409 | 1.8907 | 1.5066 | 1.1437 | 0.80268 | 0.43694 | 0.022097 | -1.448 | -4.4749 | -7.0128 | -8.3319
|  | THE GREEN | CT |  |  | 2.6653 | 2.4929 | 2.2948 | 1.9494 | 1.5727 | 1.1337 | 0.71462 | 0.28692 | -0.27704 | -0.94591 | -2.5884 | -5.8026 | -6.9397 | -7.4646 | 4.5154 | 4.443 | 4.3631 | 4.2735 | 4.1483 | 3.9681 | 3.7826 | 3.5754 | 3.3166 | 2.9896 | 1.6513 | -1.2744 | -3.4903 | -6.6832 | 3.079 | 2.9501 | 2.799 | 2.5194 | 2.214 | 1.8556 | 1.5066 | 1.1436 | 0.66314 | 0.022097 | -1.448 | -4.4749 | -5.503 | -5.9781
|  | THE GREEN | LW |  |  | 2.5442 | 2.2879 | 2.0239 | 1.6131 | 1.1807 | 0.70745 | 0.27 | -0.13354 | -0.5656 | -1.0449 | -2.3249 | -4.7185 | -5.4081 | -5.8545 | 4.5256 | 4.4557 | 4.3884 | 4.3134 | 4.1871 | 4.0491 | 3.9123 | 3.781 | 3.635 | 3.47 | 2.8067 | 1.2316 | 0.79803 | 0.49996 | 2.9756 | 2.7774 | 2.5727 | 2.2409 | 1.8907 | 1.5066 | 1.1437 | 0.80268 | 0.43694 | 0.022838 | -1.2001 | -3.3987 | -4.0303 | -4.4374
|  | THE GREEN | ST |  |  | 2.706 | 2.5615 | 2.4045 | 2.2459 | 2.0781 | 1.9015 | 1.7626 | 1.6483 | 1.5135 | 1.3383 | 0.85996 | -1.5954 | -3.1269 | -3.6747 | 4.5315 | 4.4734 | 4.4113 | 4.344 | 4.2689 | 4.1835 | 4.1055 | 4.0265 | 3.9223 | 3.7967 | 3.4866 | 1.0724 | -1.5277 | -4.578 | 3.1159 | 3.0121 | 2.8974 | 2.7806 | 2.6566 | 2.5265 | 2.421 | 2.3309 | 2.2238 | 2.083 | 1.7245 | -0.57807 | -2.0176 | -2.4721
|  | THE GREEN | FS |  |  | 2.6653 | 2.4929 | 2.2948 | 1.9494 | 1.5727 | 1.1337 | 0.71462 | 0.28692 | -0.27704 | -0.94591 | -2.5884 | -5.8026 | -6.9397 | -7.4646 | 4.5213 | 4.4438 | 4.3622 | 4.2682 | 4.163 | 4.0406 | 3.8841 | 3.7032 | 3.1528 | 2.5209 | 1.1236 | -2.9215 | -7.7268 | -14.3113 | 3.1004 | 2.9714 | 2.8379 | 2.6783 | 2.5025 | 2.2934 | 2.0313 | 1.5882 | 1.0143 | 0.40501 | -0.89583 | -4.3467 | -7.0128 | -8.3319
BRAMLEY (FLEE) | READING TOWN BSP | THE MALL | MINIMUM HEADROOM | SU 71319 73293 | YES | 10.0143 | 9.8947 | 9.7928 | 9.6551 | 9.4736 | 9.225 | 8.974 | 8.7247 | 8.4637 | 8.1939 | 7.0398 | 4.6602 | 3.7676 | 3.0747 | 14.3822 | 14.2864 | 14.2027 | 14.0307 | 13.8049 | 13.4916 | 13.2028 | 12.9268 | 12.6374 | 12.2974 | 11.5141 | 9.6458 | 7.0171 | 1.9159 | 11.3306 | 11.1512 | 10.9786 | 10.6755 | 10.3119 | 9.8493 | 9.3997 | 8.9494 | 8.4715 | 7.9872 | 7.0047 | 5.4735 | 4.1442 | 3.2877
|  | THE MALL | CT |  |  | 10.0291 | 9.9401 | 9.8461 | 9.7341 | 9.5686 | 9.2873 | 9.0885 | 8.8428 | 8.5542 | 8.2322 | 7.0398 | 4.6602 | 3.7676 | 3.0747 | 14.4042 | 14.3271 | 14.2433 | 14.1025 | 13.8797 | 13.5299 | 13.2852 | 13.0103 | 12.6734 | 12.2974 | 11.5141 | 9.6458 | 7.5489 | 4.6715 | 11.4539 | 11.3569 | 11.2548 | 11.0321 | 10.7426 | 10.3194 | 9.9959 | 9.6287 | 9.1373 | 8.6029 | 7.5226 | 5.4735 | 4.1442 | 3.2877
|  | THE MALL | LW |  |  | 10.0143 | 9.8947 | 9.7928 | 9.6551 | 9.4736 | 9.225 | 8.974 | 8.7247 | 8.4637 | 8.1939 | 7.2507 | 5.6685 | 4.7512 | 4.0159 | 14.3822 | 14.2864 | 14.2027 | 14.0307 | 13.8049 | 13.4916 | 13.2028 | 12.9268 | 12.6374 | 12.3468 | 11.7628 | 10.9178 | 10.2581 | 9.5492 | 11.3306 | 11.1512 | 10.9786 | 10.6755 | 10.3119 | 9.8493 | 9.3997 | 8.9494 | 8.4715 | 7.9872 | 7.0047 | 5.5508 | 4.621 | 3.8015
|  | THE MALL | ST |  |  | 10.0652 | 10.0039 | 9.9379 | 9.8283 | 9.6814 | 9.446 | 9.2984 | 9.1483 | 8.9695 | 8.7733 | 8.3156 | 7.3299 | 6.7026 | 6.2236 | 14.4712 | 14.435 | 14.3916 | 14.3031 | 14.1593 | 13.9044 | 13.7563 | 13.5905 | 13.3908 | 13.1797 | 12.7016 | 11.3214 | 9.3681 | 6.2496 | 11.5138 | 11.4753 | 11.4329 | 11.3441 | 11.2167 | 10.9713 | 10.8291 | 10.69 | 10.5219 | 10.3398 | 9.9191 | 8.9723 | 8.1711 | 7.402
|  | THE MALL | FS |  |  | 10.0291 | 9.9401 | 9.8461 | 9.7341 | 9.5686 | 9.2873 | 9.0885 | 8.8428 | 8.5542 | 8.2322 | 7.0398 | 4.6602 | 3.7676 | 3.0747 | 14.4642 | 14.4137 | 14.357 | 14.2596 | 14.1221 | 13.9271 | 13.729 | 13.5137 | 13.2822 | 13.0244 | 12.4023 | 10.3112 | 7.0171 | 1.9159 | 11.5162 | 11.4717 | 11.4254 | 11.3669 | 11.2844 | 11.122 | 10.9674 | 10.799 | 10.638 | 10.4594 | 10.0305 | 8.5381 | 6.8192 | 5.3158
BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE | MINIMUM HEADROOM | SU 64755 71015 | YES | 13.8044 | 13.5202 | 13.4007 | 13.2691 | 13.0888 | 12.8669 | 12.5128 | 12.1439 | 11.7249 | 11.2335 | 10.1656 | 8.0549 | 6.4112 | 5.415 | 14.5571 | 14.3237 | 14.233 | 14.1186 | 13.9795 | 13.7987 | 13.5806 | 13.3906 | 13.1616 | 12.9036 | 12.4675 | 11.1243 | 9.8554 | 7.5307 | 12.8446 | 12.5771 | 12.4174 | 12.2467 | 12.014 | 11.7275 | 11.3273 | 10.9262 | 10.4667 | 9.9677 | 9.0289 | 7.2404 | 5.8099 | 4.8852
|  | THEALE | CT |  |  | 13.8216 | 13.5202 | 13.4113 | 13.3232 | 13.1848 | 12.9501 | 12.6552 | 12.281 | 11.8323 | 11.3527 | 10.3301 | 8.0549 | 6.4112 | 5.415 | 14.5947 | 14.3237 | 14.2623 | 14.2056 | 14.1076 | 13.9405 | 13.7435 | 13.5505 | 13.3115 | 13.037 | 12.5518 | 11.1243 | 9.8669 | 9.0186 | 12.8772 | 12.5948 | 12.4686 | 12.3426 | 12.1622 | 11.8634 | 11.5222 | 11.1249 | 10.6371 | 10.1137 | 9.1741 | 7.2404 | 5.8099 | 4.8852
|  | THEALE | LW |  |  | 13.8044 | 13.5417 | 13.4007 | 13.2691 | 13.0888 | 12.8669 | 12.5128 | 12.1439 | 11.7249 | 11.2335 | 10.1656 | 8.8922 | 8.3334 | 7.7713 | 14.5571 | 14.3364 | 14.233 | 14.1186 | 13.9795 | 13.7987 | 13.5806 | 13.3906 | 13.1616 | 12.9036 | 12.4675 | 11.6975 | 11.1712 | 10.4963 | 12.8446 | 12.5771 | 12.4174 | 12.2467 | 12.014 | 11.7275 | 11.3273 | 10.9262 | 10.4667 | 9.9677 | 9.0289 | 7.9325 | 7.3749 | 6.7156
|  | THEALE | ST |  |  | 13.8867 | 13.6344 | 13.5732 | 13.5134 | 13.4084 | 13.2467 | 13.0502 | 12.8665 | 12.641 | 12.3776 | 11.7114 | 9.9094 | 9.0558 | 8.4571 | 14.6189 | 14.3659 | 14.3227 | 14.2762 | 14.2016 | 14.088 | 13.9445 | 13.8226 | 13.6709 | 13.5025 | 13.1849 | 11.9939 | 11.125 | 9.7221 | 12.9618 | 12.7443 | 12.6805 | 12.6048 | 12.4856 | 12.3119 | 12.0963 | 11.888 | 11.6266 | 11.3207 | 10.6315 | 8.7434 | 7.7387 | 7.0947
|  | THEALE | FS |  |  | 13.8216 | 13.5202 | 13.4113 | 13.3232 | 13.1848 | 12.9501 | 12.6552 | 12.281 | 11.8323 | 11.3527 | 10.3301 | 8.0549 | 6.4112 | 5.415 | 14.6321 | 14.4974 | 14.4237 | 14.3607 | 14.2739 | 14.1664 | 14.0356 | 13.9213 | 13.7755 | 13.6149 | 13.2754 | 11.8644 | 9.8554 | 7.5307 | 12.9796 | 12.8603 | 12.7847 | 12.7143 | 12.6112 | 12.4783 | 12.3189 | 12.1697 | 11.9837 | 11.7751 | 11.3016 | 9.8502 | 8.5916 | 7.7024
BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON | MINIMUM HEADROOM | SU 29134 45674 | YES | -0.32934 | -0.45678 | -0.58861 | -0.68331 | -0.82112 | -0.94598 | -1.0657 | -1.1998 | -1.4169 | -1.7111 | -2.34 | -4.4976 | -5.8627 | -6.3482 | 1.133 | 1.0635 | 0.99668 | 0.94037 | 0.82513 | 0.70996 | 0.55761 | 0.39534 | 0.18469 | -0.10393 | -0.71952 | -2.5823 | -3.7131 | -4.2625 | -0.04194 | -0.15455 | -0.27081 | -0.35657 | -0.48398 | -0.59898 | -0.73136 | -0.87577 | -1.1411 | -1.4146 | -2.0055 | -4.2807 | -5.6821 | -6.2668
|  | THRUXTON | CT |  |  | -0.23521 | -0.31643 | -0.41059 | -0.51468 | -0.70903 | -0.84551 | -1.019 | -1.1947 | -1.4169 | -1.7111 | -2.34 | -4.4976 | -5.8627 | -6.3482 | 1.1652 | 1.1147 | 1.0576 | 0.98401 | 0.82513 | 0.70996 | 0.55761 | 0.39534 | 0.18469 | -0.10393 | -0.71952 | -2.5823 | -3.7131 | -4.2625 | 0.040344 | -0.031988 | -0.11588 | -0.21299 | -0.39826 | -0.53005 | -0.70212 | -0.87235 | -1.0913 | -1.3902 | -2.0055 | -4.2807 | -5.6821 | -6.2668
|  | THRUXTON | LW |  |  | -0.32934 | -0.45678 | -0.58861 | -0.68331 | -0.82112 | -0.94598 | -1.0657 | -1.1998 | -1.3737 | -1.5583 | -1.9547 | -2.8899 | -3.927 | -4.8985 | 1.133 | 1.0635 | 0.99668 | 0.94037 | 0.83565 | 0.75045 | 0.65356 | 0.54505 | 0.40386 | 0.2534 | -0.047288 | -0.55409 | -1.4095 | -2.5255 | -0.04194 | -0.15455 | -0.27081 | -0.35657 | -0.48398 | -0.59898 | -0.70989 | -0.83373 | -0.99194 | -1.1611 | -1.5233 | -2.4024 | -3.5265 | -4.6853
|  | THRUXTON | ST |  |  | -0.19316 | -0.25281 | -0.31664 | -0.4761 | -0.6876 | -0.82578 | -0.99543 | -1.1412 | -1.3399 | -1.5379 | -1.9853 | -3.271 | -4.5903 | -5.6377 | 1.2014 | 1.1743 | 1.1441 | 1.0081 | 0.8319 | 0.72479 | 0.58136 | 0.47694 | 0.30569 | 0.13977 | -0.24216 | -1.3062 | -2.4068 | -3.6521 | 0.077474 | 0.024531 | -0.032113 | -0.20163 | -0.41313 | -0.55363 | -0.73136 | -0.87478 | -1.0838 | -1.2888 | -1.7536 | -3.0752 | -4.4918 | -5.6576
|  | THRUXTON | FS |  |  | -0.23521 | -0.31643 | -0.41059 | -0.51468 | -0.70903 | -0.84551 | -1.019 | -1.1947 | -1.4169 | -1.7111 | -2.34 | -4.4976 | -5.8627 | -6.3482 | 1.2121 | 1.1913 | 1.1675 | 1.1097 | 1.0261 | 0.95077 | 0.86909 | 0.78887 | 0.59957 | 0.38945 | -0.03918 | -0.93584 | -1.3792 | -1.8263 | 0.0798 | 0.016938 | -0.052041 | -0.16946 | -0.31941 | -0.47347 | -0.6591 | -0.87577 | -1.1411 | -1.4146 | -1.9659 | -3.1916 | -3.7484 | -4.1631
MELKSHAM GSP | WEST GRAFTON | TIDWORTH | MINIMUM HEADROOM | SU 24088 49593 | YES | 3.4749 | 3.0098 | 2.553 | 1.9237 | 1.2821 | 0.58961 | -0.29681 | -1.3882 | -2.7336 | -4.2389 | -7.8047 | -14.1534 | -17.4956 | -19.6397 | 4.9387 | 4.7092 | 4.4769 | 4.146 | 3.7777 | 3.34 | 2.7692 | 2.0446 | 1.1387 | -0.013774 | -2.642 | -8.0519 | -10.8386 | -14.4653 | 3.2378 | 2.8504 | 2.4547 | 1.9133 | 1.3429 | 0.69498 | -0.13394 | -1.1615 | -2.4356 | -3.8821 | -7.3381 | -13.5788 | -16.7302 | -18.7838
|  | TIDWORTH | CT |  |  | 3.7189 | 3.3988 | 3.0733 | 2.5316 | 1.9579 | 1.3054 | 0.4621 | -0.58683 | -2.0095 | -3.5932 | -7.0925 | -14.1534 | -17.4956 | -19.6397 | 5.011 | 4.8232 | 4.6181 | 4.2953 | 3.9285 | 3.4826 | 2.8867 | 2.1372 | 1.1504 | -0.013774 | -2.642 | -8.0519 | -10.8386 | -13.6226 | 3.4474 | 3.1818 | 2.9007 | 2.4274 | 1.9082 | 1.3013 | 0.50698 | -0.485 | -1.8297 | -3.3583 | -6.7575 | -13.5788 | -16.7302 | -18.7838
|  | TIDWORTH | LW |  |  | 3.4749 | 3.0098 | 2.553 | 1.9237 | 1.2821 | 0.58961 | -0.29681 | -1.3882 | -2.7336 | -4.2389 | -7.8047 | -14.022 | -16.5535 | -18.5348 | 4.9387 | 4.7092 | 4.4769 | 4.146 | 3.7777 | 3.34 | 2.7692 | 2.0446 | 1.1387 | 0.081328 | -2.4953 | -6.9417 | -8.6991 | -10.3293 | 3.2378 | 2.8504 | 2.4547 | 1.9133 | 1.3429 | 0.69498 | -0.13394 | -1.1615 | -2.4356 | -3.8821 | -7.3381 | -13.3194 | -15.7738 | -17.7846
|  | TIDWORTH | ST |  |  | 3.8778 | 3.6411 | 3.4176 | 3.0314 | 2.6798 | 2.3024 | 1.8157 | 1.2327 | 0.49021 | -0.33201 | -2.4422 | -9.7671 | -13.9395 | -15.2363 | 5.0686 | 4.9146 | 4.7588 | 4.4724 | 4.2023 | 3.9015 | 3.5019 | 3.0375 | 2.4344 | 1.7449 | -0.065982 | -6.3337 | -10.3214 | -12.2858 | 3.5852 | 3.3923 | 3.204 | 2.8563 | 2.5325 | 2.176 | 1.7056 | 1.1446 | 0.41025 | -0.42045 | -2.5816 | -9.9698 | -14.1548 | -15.3045
|  | TIDWORTH | FS |  |  | 3.7189 | 3.3988 | 3.0733 | 2.5316 | 1.9579 | 1.3054 | 0.4621 | -0.58683 | -2.0095 | -3.5932 | -7.0925 | -14.1534 | -17.4956 | -19.6397 | 5.0892 | 4.9641 | 4.8359 | 4.6241 | 4.4172 | 4.1936 | 3.9314 | 3.6264 | 3.2544 | 2.8352 | 1.726 | -2.8593 | -8.9345 | -14.4653 | 3.6166 | 3.4727 | 3.3306 | 3.0571 | 2.7999 | 2.5292 | 2.219 | 1.861 | 1.4326 | 0.95969 | -0.27899 | -5.4834 | -11.6991 | -15.5564
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY | MINIMUM HEADROOM | ST 93438 29127 | YES | 2.8126 | 2.616 | 2.4031 | 2.2087 | 1.9626 | 1.6469 | 1.2189 | 0.62048 | -0.1755 | -1.14 | -3.3989 | -7.3023 | -8.4155 | -9.1461 | 3.7624 | 3.6737 | 3.5665 | 3.4463 | 3.2806 | 3.0499 | 2.7293 | 2.3012 | 1.7295 | 1.0301 | -0.60207 | -3.5064 | -4.379 | -5.0123 | 2.6392 | 2.4635 | 2.2654 | 2.0771 | 1.8338 | 1.5094 | 1.0727 | 0.50616 | -0.19152 | -1.0485 | -3.1851 | -6.8115 | -7.9007 | -8.6275
|  | TISBURY | CT |  |  | 2.9585 | 2.8553 | 2.7215 | 2.525 | 2.263 | 1.9233 | 1.4789 | 0.89859 | 0.16289 | -0.72339 | -2.7686 | -6.4667 | -7.6948 | -8.3644 | 3.7931 | 3.7176 | 3.6211 | 3.4932 | 3.3167 | 3.0747 | 2.7461 | 2.3012 | 1.7295 | 1.0301 | -0.60207 | -3.5064 | -4.379 | -5.0123 | 2.7365 | 2.6102 | 2.4618 | 2.2734 | 2.0242 | 1.6978 | 1.2675 | 0.70241 | -0.015773 | -0.88345 | -2.884 | -6.567 | -7.7058 | -8.3424
|  | TISBURY | LW |  |  | 2.8126 | 2.616 | 2.4031 | 2.2087 | 1.9626 | 1.6469 | 1.2189 | 0.62048 | -0.1755 | -1.14 | -3.3989 | -7.3023 | -8.4155 | -9.1461 | 3.7624 | 3.6737 | 3.5665 | 3.4463 | 3.2806 | 3.0499 | 2.7293 | 2.3016 | 1.7686 | 1.1058 | -0.56784 | -3.3746 | -4.1457 | -4.6949 | 2.6392 | 2.4635 | 2.2654 | 2.0771 | 1.8338 | 1.5094 | 1.0727 | 0.50616 | -0.19152 | -1.0485 | -3.1851 | -6.8115 | -7.9007 | -8.6275
|  | TISBURY | ST |  |  | 3.0281 | 2.968 | 2.9041 | 2.8046 | 2.6492 | 2.4676 | 2.2434 | 1.9608 | 1.6184 | 1.1918 | 0.0083157 | -4.2263 | -6.595 | -6.8316 | 3.8257 | 3.781 | 3.7259 | 3.6528 | 3.5571 | 3.4365 | 3.2802 | 3.0762 | 2.8244 | 2.5031 | 1.568 | -1.8641 | -3.7878 | -4.0286 | 2.806 | 2.7335 | 2.6489 | 2.5347 | 2.3898 | 2.2185 | 2.0051 | 1.734 | 1.4035 | 0.98948 | -0.16719 | -4.3606 | -6.7134 | -6.8875
|  | TISBURY | FS |  |  | 2.9585 | 2.8553 | 2.7215 | 2.525 | 2.263 | 1.9233 | 1.4789 | 0.89859 | 0.16289 | -0.72339 | -2.7686 | -6.4667 | -7.6948 | -8.3644 | 3.843 | 3.8103 | 3.7716 | 3.7161 | 3.6517 | 3.5735 | 3.4796 | 3.365 | 3.227 | 3.0588 | 2.584 | 0.39855 | -2.3314 | -3.95 | 2.841 | 2.7917 | 2.7364 | 2.6405 | 2.5363 | 2.4146 | 2.277 | 2.1158 | 1.9169 | 1.6825 | 1.0524 | -1.7491 | -4.975 | -6.8266
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD | MINIMUM HEADROOM | SU 54104 05695 | YES | 4.2282 | 3.6452 | 3.0446 | 2.2197 | 1.3232 | 0.32891 | -0.86327 | -4.6555 | -9.5621 | -15.5187 | -29.8412 | -54.0664 | -60.9465 | -65.7574 | 6.1081 | 5.8333 | 5.5522 | 5.1849 | 4.708 | 4.1197 | 2.2149 | -0.63483 | -4.285 | -8.7616 | -19.5981 | -37.819 | -42.8057 | -46.4832 | 4.2335 | 3.778 | 3.3051 | 2.6344 | 1.8988 | 1.0832 | -1.0381 | -4.635 | -9.2885 | -14.9524 | -28.5898 | -51.6766 | -58.2303 | -62.8675
|  | TITCHFIELD | CT |  |  | 4.4463 | 4.0004 | 3.505 | 2.7632 | 1.8857 | 0.79309 | -0.86327 | -4.6555 | -9.5621 | -15.5187 | -29.8412 | -54.0664 | -60.9465 | -65.7574 | 6.1407 | 5.8788 | 5.5821 | 5.1849 | 4.708 | 4.1197 | 2.2149 | -0.63483 | -4.285 | -8.7616 | -19.5981 | -37.819 | -42.8057 | -46.4832 | 4.4174 | 4.0694 | 3.6749 | 3.0582 | 2.3175 | 1.4108 | -1.0381 | -4.635 | -9.2885 | -14.9524 | -28.5898 | -51.6766 | -58.2303 | -62.8675
|  | TITCHFIELD | LW |  |  | 4.2282 | 3.6452 | 3.0446 | 2.2197 | 1.3232 | 0.32891 | -0.78856 | -2.0179 | -3.4391 | -4.9301 | -8.1264 | -13.0177 | -18.0274 | -21.0482 | 6.1081 | 5.8333 | 5.5522 | 5.1894 | 4.793 | 4.3547 | 3.86 | 3.3084 | 2.6494 | 1.9086 | -0.07662 | -5.6155 | -9.4257 | -11.9462 | 4.2335 | 3.778 | 3.3051 | 2.6344 | 1.8988 | 1.0832 | 0.17126 | -0.83902 | -2.0256 | -3.2967 | -6.0437 | -12.2648 | -17.1104 | -20.1288
|  | TITCHFIELD | ST |  |  | 4.5653 | 4.2047 | 3.8187 | 3.4242 | 3.0093 | 2.5546 | 2.086 | 1.5676 | 0.98564 | 0.36366 | -1.0131 | -3.8284 | -6.0609 | -8.389 | 6.2001 | 5.9862 | 5.7562 | 5.5221 | 5.2713 | 4.9893 | 4.6902 | 4.3508 | 3.9591 | 3.5383 | 2.5832 | 0.30293 | -1.893 | -4.5003 | 4.5265 | 4.2579 | 3.9665 | 3.6651 | 3.3466 | 2.9942 | 2.6284 | 2.2189 | 1.7455 | 1.2391 | 0.10568 | -2.408 | -4.5248 | -6.6947
|  | TITCHFIELD | FS |  |  | 4.4463 | 4.0004 | 3.505 | 2.7632 | 1.8857 | 0.79309 | -0.86327 | -4.6555 | -9.5621 | -15.5187 | -29.8412 | -54.0664 | -60.9465 | -65.7574 | 6.244 | 6.0496 | 5.8466 | 5.6312 | 5.4043 | 5.1624 | 4.9023 | 4.6268 | 4.3128 | 3.9839 | 3.2602 | 1.5129 | -0.59344 | -3.8131 | 4.5977 | 4.3747 | 4.1465 | 3.8819 | 3.6064 | 3.3209 | 3.0191 | 2.7065 | 2.3142 | 1.9152 | 1.0729 | -0.72839 | -2.4362 | -4.2434
BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM | MINIMUM HEADROOM | SU 88310 49487 | YES | 12.6657 | 12.2168 | 11.7646 | 10.9134 | 10.0253 | 9.0651 | 8.0673 | 6.9889 | 5.6837 | 4.2443 | -2.7969 | -28.527 | -48.1729 | -54.368 | 15.0647 | 14.8222 | 14.5342 | 14.1975 | 13.7839 | 13.2591 | 12.6585 | 11.8807 | 10.881 | 8.994 | 3.7746 | -15.3298 | -30.0091 | -34.5639 | 11.3659 | 10.9904 | 10.6073 | 9.858 | 9.0645 | 8.1939 | 7.2676 | 6.2502 | 4.1382 | 1.5679 | -5.2223 | -29.7211 | -48.4313 | -54.3074
|  | TONGHAM | CT |  |  | 13.0719 | 12.8316 | 12.5526 | 11.902 | 11.187 | 10.3621 | 9.4598 | 8.409 | 6.7496 | 4.3486 | -2.7969 | -28.527 | -48.1729 | -54.368 | 15.1786 | 15.0081 | 14.804 | 14.4502 | 14.0329 | 13.5161 | 12.8967 | 12.1343 | 10.9255 | 8.994 | 3.7746 | -15.3298 | -30.0091 | -34.5639 | 11.532 | 11.263 | 10.9374 | 10.4897 | 9.9286 | 9.0831 | 7.8634 | 6.2882 | 4.1382 | 1.5679 | -5.2223 | -29.7211 | -48.4313 | -54.3074
|  | TONGHAM | LW |  |  | 12.6657 | 12.2168 | 11.7646 | 10.9134 | 10.0253 | 9.0651 | 8.0673 | 6.9889 | 5.6837 | 4.2443 | 0.9186 | -5.9761 | -8.725 | -9.6853 | 15.0647 | 14.8535 | 14.6327 | 14.2307 | 13.7839 | 13.2591 | 12.6585 | 11.9642 | 11.152 | 10.2005 | 7.9095 | 3.6011 | 2.1104 | 1.4983 | 11.3659 | 10.9904 | 10.6073 | 9.858 | 9.0645 | 8.1939 | 7.2676 | 6.2502 | 5.0027 | 3.603 | 0.3764 | -6.0346 | -8.5614 | -9.4171
|  | TONGHAM | ST |  |  | 13.1723 | 13.0106 | 12.8418 | 12.6077 | 12.374 | 12.1264 | 11.8487 | 11.5495 | 11.1874 | 10.6611 | 9.217 | 3.2617 | -1.0051 | -3.5498 | 15.2146 | 15.0873 | 14.9478 | 14.7427 | 14.5303 | 14.29 | 13.9953 | 13.666 | 13.2836 | 12.8124 | 11.5253 | 6.6305 | 2.9777 | 0.25304 | 11.7218 | 11.636 | 11.542 | 11.3245 | 11.1002 | 10.8559 | 10.5614 | 10.2374 | 9.8629 | 9.4026 | 8.1017 | 2.3274 | -1.6763 | -3.8748
|  | TONGHAM | FS |  |  | 13.0719 | 12.8316 | 12.5526 | 11.902 | 11.187 | 10.3621 | 9.4598 | 8.409 | 6.7496 | 4.3486 | -2.7969 | -28.527 | -48.1729 | -54.368 | 15.0912 | 14.8222 | 14.5342 | 14.1975 | 13.8115 | 13.3331 | 12.7105 | 11.8807 | 10.881 | 9.8149 | 7.4888 | 1.0835 | -4.951 | -10.6538 | 11.7084 | 11.4355 | 11.1472 | 10.7698 | 10.3487 | 9.8361 | 9.1796 | 8.2174 | 7.0126 | 5.7422 | 3.0067 | -4.3852 | -10.257 | -13.7139
MINETY GSP | TOOTHILL BSP | TOOTHILL | MINIMUM HEADROOM | SU 13215 83986 | YES | 43.8988 | 43.5752 | 43.2528 | 42.6874 | 42.0799 | 41.4425 | 40.7327 | 39.9782 | 38.4718 | 36.4147 | 31.8608 | 23.2693 | 20.1875 | 18.1005 | 43.2705 | 43.1091 | 42.9499 | 42.6926 | 42.4124 | 42.1141 | 41.7717 | 41.2692 | 39.9845 | 38.4853 | 35.1377 | 29.0415 | 27.0068 | 25.4852 | 41.5709 | 41.311 | 41.0517 | 40.5761 | 40.0617 | 39.519 | 38.9091 | 38.2582 | 36.6805 | 34.7258 | 30.3929 | 22.2617 | 19.3548 | 17.3433
|  | TOOTHILL | CT |  |  | 44.124 | 43.9371 | 43.7321 | 43.294 | 42.8071 | 42.2471 | 41.6192 | 40.2711 | 38.4718 | 36.4147 | 31.8608 | 23.2693 | 20.1875 | 18.1005 | 43.3355 | 43.2111 | 43.0728 | 42.8433 | 42.5834 | 42.2746 | 41.9212 | 41.2692 | 39.9845 | 38.4853 | 35.1377 | 29.0415 | 27.0068 | 25.4852 | 41.7666 | 41.6227 | 41.4619 | 41.0945 | 40.6829 | 40.205 | 39.6676 | 38.3813 | 36.6805 | 34.7258 | 30.3929 | 22.2617 | 19.3548 | 17.3433
|  | TOOTHILL | LW |  |  | 43.8988 | 43.5752 | 43.2528 | 42.6874 | 42.0799 | 41.4425 | 40.7327 | 39.9782 | 39.2746 | 38.6134 | 37.2637 | 34.1512 | 32.3777 | 31.1871 | 43.2705 | 43.1091 | 42.9499 | 42.6926 | 42.4124 | 42.1141 | 41.7717 | 41.4035 | 41.043 | 40.6931 | 39.9738 | 38.4463 | 37.4357 | 36.5269 | 41.5709 | 41.311 | 41.0517 | 40.5761 | 40.0617 | 39.519 | 38.9091 | 38.2582 | 37.624 | 37.0175 | 35.778 | 33.003 | 31.3778 | 30.2109
|  | TOOTHILL | ST |  |  | 44.2175 | 44.0843 | 43.9417 | 43.7813 | 43.6182 | 43.4372 | 43.238 | 43.0216 | 42.855 | 42.7018 | 42.379 | 40.8301 | 38.9494 | 36.7022 | 43.382 | 43.2879 | 43.187 | 43.0718 | 42.9522 | 42.8187 | 42.6685 | 42.5055 | 42.3465 | 42.1904 | 41.8389 | 40.4903 | 38.7114 | 36.3242 | 41.8477 | 41.7479 | 41.6416 | 41.5157 | 41.3883 | 41.2458 | 41.0853 | 40.9108 | 40.7604 | 40.6194 | 40.3119 | 38.8902 | 37.1764 | 35.1536
|  | TOOTHILL | FS |  |  | 44.124 | 43.9371 | 43.7321 | 43.294 | 42.8071 | 42.2471 | 41.6192 | 40.2711 | 38.4718 | 36.4147 | 31.8608 | 23.2693 | 20.1875 | 18.1005 | 43.3359 | 43.2075 | 43.0617 | 42.8834 | 42.6754 | 42.4279 | 42.1331 | 41.7819 | 41.393 | 40.9499 | 39.7809 | 35.2495 | 30.498 | 26.2559 | 41.7809 | 41.6453 | 41.4949 | 41.2823 | 41.0366 | 40.7464 | 40.4032 | 39.9937 | 39.5433 | 39.0372 | 37.6637 | 32.3919 | 27.4552 | 24.4604
NURSLING GSP | ROWNHAMS | TOTTON | MINIMUM HEADROOM | SU 35835 13428 | YES | 5.1348 | 4.8954 | 4.6722 | 4.1873 | 3.6878 | 3.1764 | 2.5802 | 1.6924 | -0.29223 | -2.6284 | -8.1161 | -17.6162 | -21.0315 | -23.2564 | 7.8952 | 7.8258 | 7.7501 | 7.6385 | 7.485 | 6.9521 | 6.2342 | 5.2536 | 3.9938 | 2.4512 | -1.4828 | -7.9886 | -10.077 | -11.6342 | 5.3666 | 5.1611 | 4.9698 | 4.5532 | 4.1223 | 3.6773 | 3.1599 | 2.1515 | 0.27968 | -1.929 | -7.1193 | -16.0589 | -19.2467 | -21.3783
|  | TOTTON | CT |  |  | 5.4526 | 5.3726 | 5.2815 | 4.9222 | 4.5271 | 4.0651 | 3.1333 | 1.6924 | -0.29223 | -2.6284 | -8.1161 | -17.6162 | -21.0315 | -23.2564 | 7.8952 | 7.8316 | 7.7501 | 7.6385 | 7.485 | 6.9521 | 6.2342 | 5.2536 | 3.9938 | 2.4512 | -1.4828 | -7.9886 | -10.077 | -11.6342 | 5.632 | 5.5593 | 5.4751 | 5.162 | 4.8138 | 4.3225 | 3.4103 | 2.1515 | 0.27968 | -1.929 | -7.1193 | -16.0589 | -19.2467 | -21.3783
|  | TOTTON | LW |  |  | 5.1348 | 4.8954 | 4.6722 | 4.1873 | 3.6878 | 3.1764 | 2.5802 | 1.9113 | 1.0499 | 0.059967 | -2.1072 | -6.8046 | -9.5328 | -10.7417 | 7.8972 | 7.8258 | 7.7777 | 7.7108 | 7.63 | 7.4868 | 7.2036 | 6.8839 | 6.4736 | 5.998 | 4.8695 | 2.6806 | 1.1976 | 0.27261 | 5.3666 | 5.1611 | 4.9698 | 4.5532 | 4.1223 | 3.6773 | 3.1599 | 2.5824 | 1.8348 | 0.97973 | -0.89264 | -4.9877 | -7.4587 | -8.6515
|  | TOTTON | ST |  |  | 5.5812 | 5.5873 | 5.5915 | 5.5623 | 5.5368 | 5.4959 | 5.4065 | 5.2887 | 5.1371 | 4.9216 | 4.3514 | 1.724 | -0.16397 | -3.2738 | 7.9517 | 7.9384 | 7.9202 | 7.8736 | 7.8261 | 7.7628 | 7.664 | 7.5561 | 7.4149 | 7.2469 | 6.7452 | 4.8913 | 3.4345 | 0.51154 | 5.7431 | 5.7463 | 5.7476 | 5.7133 | 5.6836 | 5.6401 | 5.5539 | 5.448 | 5.3059 | 5.0497 | 4.2511 | 1.9398 | 0.28435 | -2.4345
|  | TOTTON | FS |  |  | 5.4526 | 5.3726 | 5.2815 | 4.9222 | 4.5271 | 4.0651 | 3.1333 | 1.6924 | -0.29223 | -2.6284 | -8.1161 | -17.6162 | -21.0315 | -23.2564 | 7.9634 | 7.9347 | 7.91 | 7.8804 | 7.8413 | 7.7984 | 7.7358 | 7.6615 | 7.5639 | 7.4417 | 7.0023 | 5.1532 | 2.5171 | -1.6257 | 5.7354 | 5.7135 | 5.6975 | 5.6396 | 5.5692 | 5.4951 | 5.3887 | 5.2499 | 5.0257 | 4.755 | 4.1593 | 2.2887 | 0.25326 | -1.9525
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK | MINIMUM HEADROOM | SU 45156 14783 | YES | 9.3024 | 8.7963 | 8.2883 | 7.3193 | 6.3464 | 5.3735 | 4.2905 | 3.1218 | 1.7584 | 0.30027 | -2.939 | -14.0323 | -26.7023 | -31.493 | 12.3371 | 12.0726 | 11.8112 | 11.3496 | 10.8776 | 10.3809 | 9.8029 | 9.1666 | 8.4387 | 7.2829 | 4.6391 | -3.9719 | -13.2805 | -16.851 | 9.4479 | 9.0986 | 8.7391 | 8.0594 | 7.2379 | 6.3627 | 5.3654 | 4.2644 | 2.9837 | 1.5939 | -1.5087 | -13.4953 | -25.5844 | -30.2003
|  | TOWNHILL PARK | CT |  |  | 9.785 | 9.5762 | 9.3411 | 8.6275 | 7.8906 | 7.0962 | 6.1732 | 5.1336 | 3.4783 | 1.6849 | -2.2962 | -14.0323 | -26.7023 | -31.493 | 12.4787 | 12.3092 | 12.1137 | 11.7239 | 11.2962 | 10.8023 | 10.1887 | 9.485 | 8.4595 | 7.2829 | 4.6391 | -3.9719 | -13.2805 | -16.851 | 9.7409 | 9.5799 | 9.3924 | 8.8965 | 8.3619 | 7.7611 | 6.9094 | 5.9245 | 4.4149 | 2.7304 | -0.98622 | -13.4953 | -25.5844 | -30.2003
|  | TOWNHILL PARK | LW |  |  | 9.3024 | 8.7963 | 8.2883 | 7.3193 | 6.3464 | 5.3735 | 4.2905 | 3.1218 | 1.7584 | 0.30027 | -2.939 | -9.6661 | -13.166 | -15.365 | 12.3371 | 12.0726 | 11.8112 | 11.3496 | 10.8776 | 10.3809 | 9.8029 | 9.1666 | 8.4387 | 7.6422 | 5.8607 | 2.2576 | 0.14575 | -1.6625 | 9.4479 | 9.0986 | 8.7391 | 8.0594 | 7.2379 | 6.3627 | 5.3654 | 4.2644 | 2.9837 | 1.5939 | -1.5087 | -7.6506 | -10.8683 | -13.1004
|  | TOWNHILL PARK | ST |  |  | 10.0596 | 9.9866 | 9.8952 | 9.7402 | 9.6124 | 9.4546 | 9.1468 | 8.7745 | 8.2939 | 7.7624 | 6.4808 | 1.3116 | -3.0984 | -6.8046 | 12.5815 | 12.461 | 12.3219 | 12.0807 | 11.8601 | 11.6099 | 11.2534 | 10.8721 | 10.3543 | 9.7542 | 8.3328 | 3.1324 | -2.1216 | -8.1839 | 9.8887 | 9.7906 | 9.675 | 9.4611 | 9.2675 | 9.0414 | 8.6907 | 8.2791 | 7.7488 | 7.1616 | 5.7384 | 0.60355 | -3.5864 | -6.7335
|  | TOWNHILL PARK | FS |  |  | 9.785 | 9.5762 | 9.3411 | 8.6275 | 7.8906 | 7.0962 | 6.1732 | 5.1336 | 3.4783 | 1.6849 | -2.2962 | -14.0323 | -26.7023 | -31.493 | 12.6417 | 12.5041 | 12.3602 | 12.1906 | 12.0184 | 11.83 | 11.6151 | 11.3705 | 10.9846 | 10.5448 | 9.4864 | 5.1247 | -2.4633 | -14.2544 | 9.9521 | 9.8771 | 9.7998 | 9.6673 | 9.5427 | 9.4079 | 9.2543 | 9.0714 | 8.8015 | 8.4923 | 7.738 | 4.3952 | -0.46521 | -4.8975
MINETY GSP | SWINDON BSP | TRADING ESTATE | MINIMUM HEADROOM | SU 13490 85868 | YES | 13.343 | 13.2897 | 13.2296 | 13.162 | 13.0666 | 12.944 | 12.784 | 12.5656 | 12.288 | 11.9771 | 11.2997 | 8.9177 | 7.5335 | 6.6269 | 14.6713 | 14.6357 | 14.6041 | 14.5599 | 14.5033 | 14.4236 | 14.3272 | 14.1939 | 14.0065 | 13.7866 | 13.3333 | 11.5797 | 10.4084 | 9.0502 | 14.1478 | 14.0996 | 14.0571 | 13.9932 | 13.9101 | 13.8038 | 13.5954 | 13.3436 | 13.0219 | 12.6626 | 11.8901 | 9.0228 | 7.6944 | 6.7721
|  | TRADING ESTATE | CT |  |  | 13.343 | 13.3014 | 13.2364 | 13.162 | 13.0764 | 12.944 | 12.7907 | 12.5703 | 12.288 | 11.98 | 11.3727 | 8.9177 | 7.5335 | 6.6269 | 14.6726 | 14.6422 | 14.6066 | 14.5599 | 14.5042 | 14.4236 | 14.3272 | 14.1939 | 14.0065 | 13.7866 | 13.3333 | 11.5797 | 10.4084 | 9.1829 | 14.1581 | 14.1223 | 14.0808 | 14.0229 | 13.9517 | 13.8121 | 13.6363 | 13.3865 | 13.0593 | 12.7038 | 11.8965 | 9.0228 | 7.6944 | 6.7721
|  | TRADING ESTATE | LW |  |  | 13.3445 | 13.2897 | 13.2296 | 13.1621 | 13.0666 | 12.9623 | 12.784 | 12.5656 | 12.2889 | 11.9771 | 11.2997 | 9.1593 | 8.0188 | 7.0333 | 14.6713 | 14.6357 | 14.6041 | 14.5612 | 14.5033 | 14.4371 | 14.3348 | 14.2086 | 14.0254 | 13.8183 | 13.3616 | 12.1781 | 11.2762 | 10.3427 | 14.1478 | 14.0996 | 14.0571 | 13.9932 | 13.9101 | 13.8038 | 13.5954 | 13.3436 | 13.0219 | 12.6626 | 11.8901 | 9.4307 | 8.2228 | 7.1093
|  | TRADING ESTATE | ST |  |  | 13.3688 | 13.3532 | 13.3321 | 13.3016 | 13.2535 | 13.1787 | 13.0825 | 12.9608 | 12.7876 | 12.5808 | 12.0246 | 10.3132 | 8.8085 | 7.6761 | 14.6944 | 14.681 | 14.663 | 14.638 | 14.6047 | 14.5612 | 14.5048 | 14.4327 | 14.3135 | 14.1757 | 13.8084 | 12.5659 | 10.5345 | 9.0807 | 14.1831 | 14.1682 | 14.1479 | 14.1186 | 14.0797 | 14.0288 | 13.9625 | 13.8611 | 13.6676 | 13.4381 | 12.8241 | 10.921 | 8.5432 | 7.3537
|  | TRADING ESTATE | FS |  |  | 13.343 | 13.3014 | 13.2364 | 13.162 | 13.0764 | 12.944 | 12.7907 | 12.5703 | 12.288 | 11.98 | 11.3727 | 8.9177 | 7.5335 | 6.6269 | 14.694 | 14.6808 | 14.664 | 14.6437 | 14.6185 | 14.5848 | 14.5441 | 14.4904 | 14.4101 | 14.3208 | 14.0994 | 13.3087 | 11.3198 | 9.0502 | 14.1836 | 14.17 | 14.1524 | 14.1294 | 14.1009 | 14.0628 | 14.0168 | 13.9561 | 13.8729 | 13.7611 | 13.4213 | 12.2368 | 9.9843 | 8.3454
BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN | MINIMUM HEADROOM | SU 66254 68745 | YES | 4.2991 | 3.906 | 3.4807 | 2.8573 | 2.1013 | 1.2869 | 0.401 | -1.192 | -3.6106 | -6.5267 | -13.2933 | -25.2454 | -29.3492 | -32.4462 | 7.234 | 7.017 | 6.7757 | 6.3986 | 5.9289 | 5.391 | 4.7471 | 3.9196 | 2.2687 | 0.024603 | -5.2076 | -14.4464 | -17.879 | -20.8201 | 4.6092 | 4.2705 | 3.9016 | 3.3343 | 2.6425 | 1.7762 | 0.3445 | -1.5711 | -3.9035 | -6.7149 | -13.2335 | -24.7667 | -28.9166 | -32.2227
|  | TRASH GREEN | CT |  |  | 4.6022 | 4.3457 | 4.0426 | 3.5883 | 3.0308 | 2.4228 | 1.766 | 0.90251 | -0.24324 | -1.6049 | -4.5862 | -10.8225 | -13.7379 | -15.3328 | 7.391 | 7.2266 | 7.0276 | 6.7446 | 6.3869 | 5.9673 | 5.4668 | 4.8229 | 4.0054 | 2.9881 | 0.72181 | -4.0486 | -6.4983 | -8.4861 | 4.8981 | 4.6864 | 4.4326 | 4.0341 | 3.5415 | 2.9949 | 2.39 | 1.6122 | 0.56866 | -0.68366 | -3.5972 | -9.7184 | -12.6006 | -14.268
|  | TRASH GREEN | LW |  |  | 4.2991 | 3.906 | 3.4807 | 2.8573 | 2.1013 | 1.2869 | 0.401 | -1.192 | -3.6106 | -6.5267 | -13.2933 | -25.2454 | -29.3492 | -32.4462 | 7.234 | 7.017 | 6.7757 | 6.3986 | 5.9289 | 5.391 | 4.7471 | 3.9196 | 2.2687 | 0.024603 | -5.2076 | -14.4464 | -17.879 | -20.8201 | 4.6092 | 4.2705 | 3.9016 | 3.3343 | 2.6425 | 1.7762 | 0.3445 | -1.5711 | -3.9035 | -6.7149 | -13.2335 | -24.7667 | -28.9166 | -32.2227
|  | TRASH GREEN | ST |  |  | 4.7713 | 4.5681 | 4.3332 | 3.9645 | 3.5849 | 3.2175 | 2.8231 | 2.3486 | 1.7757 | 1.1099 | -0.63454 | -6.7977 | -10.947 | -12.838 | 7.5083 | 7.3792 | 7.2263 | 6.9275 | 6.6364 | 6.3396 | 5.9856 | 5.5967 | 5.1046 | 4.5394 | 3.0486 | -2.1285 | -5.902 | -8.0423 | 5.0602 | 4.8985 | 4.7076 | 4.3608 | 4.0174 | 3.68 | 3.2973 | 2.8656 | 2.3241 | 1.7052 | 0.067845 | -6.0999 | -10.343 | -12.3337
|  | TRASH GREEN | FS |  |  | 4.6022 | 4.3457 | 4.0426 | 3.5883 | 3.0308 | 2.4228 | 1.766 | 0.90251 | -0.24324 | -1.6049 | -4.5862 | -10.8225 | -13.7379 | -15.3328 | 7.5234 | 7.3635 | 7.1874 | 6.9599 | 6.6941 | 6.4052 | 6.068 | 5.6404 | 5.1373 | 4.5728 | 3.2095 | -1.1363 | -5.5438 | -8.6377 | 5.101 | 4.9234 | 4.7298 | 4.4582 | 4.1458 | 3.8195 | 3.4528 | 2.9886 | 2.4219 | 1.7883 | 0.15451 | -5.0453 | -10.1817 | -13.3657
MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN | MINIMUM HEADROOM | ST 84668 58036 | YES | 7.7208 | 7.5374 | 7.3305 | 7.0394 | 6.5527 | 5.1371 | 3.1747 | 0.67457 | -2.4113 | -6.1209 | -15.4053 | -35.1008 | -48.5375 | -56.4422 | 10.4977 | 10.228 | 9.9224 | 9.4947 | 8.8804 | 8.062 | 6.8674 | 5.3073 | 3.2358 | 0.5593 | -6.4208 | -21.1702 | -31.3698 | -37.5424 | 7.5614 | 7.2851 | 7.0011 | 6.4872 | 5.8867 | 5.1958 | 3.3599 | 0.98162 | -1.9496 | -5.4799 | -14.3298 | -33.0877 | -45.936 | -53.5553
|  | TROWBRIDGE TOWN | CT |  |  | 7.7958 | 7.69 | 7.5598 | 7.3829 | 7.1345 | 6.7665 | 6.0884 | 4.6231 | 2.5741 | 0.25139 | -4.9342 | -14.4684 | -18.1718 | -20.6504 | 10.5995 | 10.4559 | 10.2635 | 10.0001 | 9.6461 | 9.1232 | 8.4411 | 7.5146 | 6.3485 | 4.9827 | 1.4957 | -5.0508 | -7.2481 | -8.8675 | 7.8782 | 7.7793 | 7.6698 | 7.3421 | 6.9508 | 6.4912 | 5.8821 | 4.7074 | 2.7742 | 0.57297 | -4.3452 | -13.3184 | -16.7327 | -19.0477
|  | TROWBRIDGE TOWN | LW |  |  | 7.7208 | 7.5374 | 7.3305 | 7.0394 | 6.5527 | 5.1371 | 3.1747 | 0.67457 | -2.4113 | -6.1209 | -15.4053 | -35.1008 | -48.5375 | -56.4422 | 10.4977 | 10.228 | 9.9224 | 9.4947 | 8.8804 | 8.062 | 6.8674 | 5.3073 | 3.2358 | 0.5593 | -6.4208 | -21.1702 | -31.3698 | -37.5424 | 7.5614 | 7.2851 | 7.0011 | 6.4872 | 5.8867 | 5.1958 | 3.3599 | 0.98162 | -1.9496 | -5.4799 | -14.3298 | -33.0877 | -45.936 | -53.5553
|  | TROWBRIDGE TOWN | ST |  |  | 7.8906 | 7.8644 | 7.8298 | 7.7359 | 7.6248 | 7.491 | 7.3124 | 7.1238 | 6.8872 | 6.6184 | 5.9357 | 3.1284 | 1.2412 | -0.65685 | 10.7119 | 10.6817 | 10.6415 | 10.5294 | 10.4075 | 10.2431 | 10.0255 | 9.7956 | 9.5052 | 9.1698 | 8.3055 | 5.8803 | 4.4617 | 0.70356 | 8.058 | 8.0572 | 8.0476 | 7.9783 | 7.8856 | 7.7739 | 7.6115 | 7.4444 | 7.2236 | 6.8887 | 5.8501 | 2.9409 | 1.3567 | -0.97999
|  | TROWBRIDGE TOWN | FS |  |  | 7.7958 | 7.69 | 7.5598 | 7.3829 | 7.1345 | 6.7665 | 6.0884 | 4.6231 | 2.5741 | 0.25139 | -4.9342 | -14.4684 | -18.1718 | -20.6504 | 10.7174 | 10.696 | 10.6664 | 10.6124 | 10.5426 | 10.4467 | 10.3227 | 10.1804 | 10.0084 | 9.8122 | 9.2958 | 6.9164 | 2.7135 | -3.6378 | 8.0395 | 8.0397 | 8.0297 | 7.9483 | 7.8466 | 7.7319 | 7.5916 | 7.4422 | 7.2115 | 6.9645 | 6.3752 | 4.0811 | 1.4884 | -1.1529
BRAMLEY (FLEE) | READING BSP | TWYFORD | MINIMUM HEADROOM | SU 78430 76339 | YES | 0.87963 | 0.68868 | 0.49595 | 0.074026 | -0.41593 | -0.96191 | -1.5729 | -2.241 | -3.1317 | -4.2271 | -8.5483 | -22.289 | -29.3646 | -29.6818 | 4.8439 | 4.7659 | 4.6511 | 4.4531 | 4.2367 | 3.9802 | 3.635 | 3.24 | 2.7404 | 1.5708 | -1.5677 | -11.7978 | -17.1305 | -17.4845 | 1.8423 | 1.672 | 1.4997 | 1.1208 | 0.6843 | 0.19594 | -0.35353 | -0.95639 | -1.7075 | -2.5129 | -6.2095 | -19.2976 | -26.0956 | -26.4985
|  | TWYFORD | CT |  |  | 1.1478 | 1.1037 | 1.0533 | 0.79178 | 0.47646 | 0.13274 | -0.25442 | -0.66029 | -1.4037 | -2.1872 | -3.8241 | -8.7469 | -12.4249 | -15.0251 | 4.9031 | 4.844 | 4.7745 | 4.6298 | 4.4491 | 4.2425 | 3.9963 | 3.7374 | 3.3615 | 2.9322 | 2.0184 | -0.66325 | -3.1888 | -5.8506 | 2.0788 | 2.039 | 1.9931 | 1.7594 | 1.4797 | 1.1734 | 0.8232 | 0.4578 | -0.2085 | -0.92287 | -2.3917 | -6.5491 | -9.7601 | -12.0767
|  | TWYFORD | LW |  |  | 0.87963 | 0.68868 | 0.49595 | 0.074026 | -0.41593 | -0.96191 | -1.5729 | -2.241 | -3.1317 | -4.2271 | -8.5483 | -22.289 | -29.3646 | -29.6818 | 4.8439 | 4.7659 | 4.6851 | 4.5103 | 4.2969 | 4.0477 | 3.754 | 3.4246 | 2.7404 | 1.5708 | -1.5677 | -11.7978 | -17.1305 | -17.4845 | 1.8423 | 1.672 | 1.4997 | 1.1208 | 0.6843 | 0.19594 | -0.35353 | -0.95639 | -1.7075 | -2.5129 | -6.2095 | -19.2976 | -26.0956 | -26.4985
|  | TWYFORD | ST |  |  | 1.1463 | 1.0645 | 0.97434 | 0.8028 | 0.59406 | 0.33715 | -0.010775 | -0.42438 | -0.91271 | -1.4193 | -2.5025 | -5.757 | -8.4248 | -10.8627 | 4.8714 | 4.768 | 4.6511 | 4.4531 | 4.2367 | 3.9802 | 3.635 | 3.24 | 2.7826 | 2.304 | 1.259 | -1.6591 | -4.1976 | -6.9382 | 2.0701 | 1.9895 | 1.9006 | 1.7187 | 1.5119 | 1.2602 | 0.91426 | 0.50927 | 0.023555 | -0.47962 | -1.559 | -4.7036 | -7.218 | -9.4405
|  | TWYFORD | FS |  |  | 1.1478 | 1.1037 | 1.0533 | 0.79178 | 0.47646 | 0.13274 | -0.25442 | -0.66029 | -1.4037 | -2.1872 | -3.8241 | -8.7469 | -12.4249 | -15.0251 | 4.9248 | 4.8692 | 4.8046 | 4.7272 | 4.63 | 4.5193 | 4.3867 | 4.2424 | 4.0652 | 3.872 | 3.4225 | 1.8253 | -0.28587 | -3.3973 | 2.1366 | 2.125 | 2.1124 | 2.0522 | 1.9725 | 1.8852 | 1.778 | 1.6654 | 1.4776 | 1.2802 | 0.84983 | -0.67846 | -2.5007 | -4.4589
COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET | MINIMUM HEADROOM | SP 52865 05849 | NO | 10.7075 | 10.5623 | 10.1556 | 9.6986 | 9.3224 | 8.9307 | 8.5078 | 8.035 | 7.415 | 6.7434 | 5.3673 | 1.3803 | -1.711 | -2.316 | 16.0171 | 15.8186 | 15.4555 | 15.063 | 14.6566 | 14.1704 | 13.6077 | 12.9318 | 12.1679 | 11.3389 | 9.4318 | 2.2778 | -10.0939 | -32.9458 | 9.67 | 9.5388 | 9.185 | 8.7309 | 8.3399 | 7.9341 | 7.4968 | 7.0299 | 6.4535 | 5.8414 | 4.5694 | 1.1748 | -1.7576 | -2.3686
|  | UNION STREET | CT |  |  | 10.8854 | 10.8505 | 10.5768 | 10.2336 | 9.9672 | 9.6736 | 9.3321 | 8.9199 | 8.2939 | 7.6015 | 6.0494 | 1.3803 | -1.711 | -2.316 | 16.0491 | 15.8885 | 15.5606 | 15.1884 | 14.8288 | 14.4171 | 13.9433 | 13.3925 | 12.7131 | 11.9576 | 10.2589 | 4.5971 | -3.0518 | -15.0627 | 9.8379 | 9.8024 | 9.5762 | 9.2802 | 9.0046 | 8.6993 | 8.35 | 7.934 | 7.2872 | 6.6013 | 5.183 | 1.1748 | -1.7576 | -2.3686
|  | UNION STREET | LW |  |  | 10.7075 | 10.5623 | 10.1556 | 9.6986 | 9.3224 | 8.9307 | 8.5078 | 8.035 | 7.415 | 6.7434 | 5.3673 | 2.4469 | 1.0326 | 0.16 | 16.0781 | 16.0188 | 15.8165 | 15.5848 | 15.394 | 15.1893 | 14.9584 | 14.7071 | 14.3825 | 14.0304 | 13.2839 | 11.7808 | 10.8565 | 10.0432 | 9.67 | 9.5388 | 9.185 | 8.7309 | 8.3399 | 7.9341 | 7.4968 | 7.0299 | 6.4535 | 5.8414 | 4.5694 | 1.8941 | 0.50321 | -0.46409
|  | UNION STREET | ST |  |  | 10.9489 | 10.942 | 10.7085 | 10.6042 | 10.564 | 10.512 | 10.4238 | 10.2969 | 10.1377 | 9.9618 | 9.4865 | 7.1038 | 4.5631 | 2.4191 | 16.0711 | 15.9415 | 15.6361 | 15.3692 | 15.1136 | 14.8184 | 14.4685 | 14.0662 | 13.6146 | 13.1119 | 11.8708 | 6.7735 | -1.2781 | -13.9693 | 9.8986 | 9.8904 | 9.6956 | 9.6024 | 9.5609 | 9.5074 | 9.4199 | 9.2993 | 9.1392 | 8.9607 | 8.4746 | 6.1527 | 3.6514 | 1.5785
|  | UNION STREET | FS |  |  | 10.8854 | 10.8505 | 10.5768 | 10.2336 | 9.9672 | 9.6736 | 9.3321 | 8.9199 | 8.2939 | 7.6015 | 6.0494 | 1.3803 | -1.711 | -2.316 | 16.0171 | 15.8186 | 15.4555 | 15.063 | 14.6566 | 14.1704 | 13.6077 | 12.9318 | 12.1679 | 11.3389 | 9.4318 | 2.2778 | -10.0939 | -32.9458 | 9.8393 | 9.7854 | 9.5656 | 9.4015 | 9.2759 | 9.0918 | 8.8845 | 8.5906 | 8.2042 | 7.824 | 7.0728 | 4.7738 | 2.6331 | 0.57403
EAST CLAYDON GSP | BICESTER NORTH | UPPER HEYFORD | MINIMUM HEADROOM | SP 51750 25667 | NO | 7.0657 | 6.6173 | 6.135 | 5.103 | 4.0253 | 2.7028 | 1.3453 | 0.04789 | -0.98807 | -1.7309 | -3.2555 | -6.203 | -6.8457 | -7.0186 | 8.2569 | 7.9555 | 7.6158 | 6.6296 | 5.7396 | 4.4854 | 3.2289 | 2.1047 | 1.349 | 0.73124 | -0.53544 | -3.352 | -3.8974 | -3.9777 | 6.7825 | 6.4106 | 6.0065 | 4.9464 | 3.8308 | 2.4356 | 1.0061 | -0.32071 | -1.2959 | -2.0872 | -3.6956 | -6.9225 | -7.5985 | -7.7448
|  | UPPER HEYFORD | CT |  |  | 7.1683 | 6.7297 | 6.2737 | 5.6429 | 5.064 | 4.401 | 3.7108 | 3.0223 | 2.3229 | 1.7919 | 0.73625 | -1.3148 | -2.0957 | -2.4716 | 8.2964 | 7.9849 | 7.6635 | 7.1518 | 6.6949 | 6.178 | 5.6488 | 5.1787 | 4.7587 | 4.3009 | 3.2431 | 1.2516 | 0.7767 | 0.5604 | 6.8761 | 6.5002 | 6.108 | 5.5195 | 4.9726 | 4.3426 | 3.6733 | 3.035 | 2.4128 | 1.8975 | 0.87903 | -1.1756 | -1.9349 | -2.273
|  | UPPER HEYFORD | LW |  |  | 7.0657 | 6.6173 | 6.135 | 5.103 | 4.0253 | 2.7028 | 1.3453 | 0.04789 | -0.98807 | -1.7309 | -3.2555 | -6.203 | -6.8457 | -7.0186 | 8.2569 | 7.9831 | 7.6835 | 6.731 | 5.7396 | 4.4854 | 3.2289 | 2.1047 | 1.349 | 0.73124 | -0.53544 | -3.352 | -3.8974 | -3.9777 | 6.7825 | 6.4106 | 6.0065 | 4.9464 | 3.8308 | 2.4356 | 1.0061 | -0.32071 | -1.2959 | -2.0872 | -3.6956 | -6.9225 | -7.5985 | -7.7448
|  | UPPER HEYFORD | ST |  |  | 7.1493 | 6.6844 | 6.1983 | 5.1761 | 4.4118 | 3.6265 | 2.7666 | 2.0261 | 1.2925 | 0.71651 | -0.51027 | -3.4128 | -4.4688 | -4.611 | 8.2836 | 7.9555 | 7.6158 | 6.6296 | 5.9344 | 5.2453 | 4.4882 | 3.9406 | 3.4236 | 2.955 | 1.9246 | -0.63138 | -1.5741 | -1.7838 | 6.8683 | 6.475 | 6.0623 | 5.0149 | 4.2496 | 3.4743 | 2.5823 | 1.8665 | 1.175 | 0.60108 | -0.63401 | -3.6207 | -4.6736 | -4.7718
|  | UPPER HEYFORD | FS |  |  | 7.1683 | 6.7297 | 6.2737 | 5.6429 | 5.064 | 4.401 | 3.7108 | 3.0223 | 2.3229 | 1.7919 | 0.73625 | -1.3148 | -2.0957 | -2.4716 | 8.3147 | 8.1195 | 7.8986 | 7.4767 | 7.0751 | 6.6255 | 6.1984 | 5.7792 | 5.39 | 5.0268 | 4.0816 | 1.2585 | -1.1157 | -2.297 | 6.9225 | 6.683 | 6.4144 | 5.9321 | 5.4628 | 4.9371 | 4.4111 | 3.8746 | 3.3555 | 2.8984 | 1.7418 | -1.7801 | -4.693 | -6.0856
IVER 132KV | UPTON BSP | UPTON | MINIMUM HEADROOM | TQ 00800 79434 | YES | 0.044965 | -0.33215 | -0.75076 | -2.3453 | -4.1282 | -7.1426 | -10.7386 | -14.4376 | -18.9238 | -24.1237 | -36.0377 | -59.6804 | -70.7304 | -76.819 | 4.3592 | 4.1462 | 3.8973 | 2.5335 | 0.97924 | -2.0066 | -5.7821 | -10.0633 | -13.9764 | -18.3317 | -28.0725 | -47.6163 | -56.4517 | -61.2531 | -1.3265 | -1.6717 | -2.0585 | -3.7693 | -5.7058 | -9.1235 | -13.1529 | -17.1202 | -21.3196 | -26.5496 | -38.367 | -61.961 | -72.7773 | -78.6548
|  | UPTON | CT |  |  | 0.4153 | 0.25959 | 0.055198 | -0.73553 | -1.6164 | -3.4645 | -5.8756 | -8.417 | -11.2716 | -14.3913 | -21.3327 | -35.5046 | -40.6481 | -43.3997 | 4.4732 | 4.3204 | 4.1215 | 3.5628 | 2.8825 | 1.095 | -1.2263 | -3.625 | -6.0755 | -8.8222 | -14.6251 | -26.308 | -31.4763 | -36.7729 | -0.99811 | -1.1448 | -1.3394 | -2.1072 | -3.0152 | -5.0705 | -7.7098 | -10.3678 | -13.267 | -16.5944 | -23.6463 | -37.7392 | -42.671 | -45.2665
|  | UPTON | LW |  |  | 0.044965 | -0.33215 | -0.75076 | -2.3453 | -4.1282 | -7.1426 | -10.7386 | -14.4376 | -18.9238 | -24.1237 | -36.0377 | -59.6804 | -70.7304 | -76.819 | 4.3592 | 4.1462 | 3.8973 | 2.5335 | 0.97924 | -2.0066 | -5.7821 | -10.0633 | -13.9764 | -18.3317 | -28.0725 | -47.6163 | -56.4517 | -61.2531 | -1.3265 | -1.6717 | -2.0585 | -3.7693 | -5.7058 | -9.1235 | -13.1529 | -17.1202 | -21.3196 | -26.5496 | -38.367 | -61.961 | -72.7773 | -78.6548
|  | UPTON | ST |  |  | 0.63553 | 0.62495 | 0.58613 | -0.27368 | -0.87214 | -2.1398 | -3.9134 | -5.427 | -6.8492 | -8.2862 | -12.068 | -25.1876 | -32.6419 | -34.5191 | 4.5761 | 4.5022 | 4.401 | 3.3269 | 2.5542 | 0.96166 | -1.2044 | -2.9847 | -4.6136 | -6.2865 | -10.2044 | -22.6137 | -30.3382 | -34.3048 | -0.80053 | -0.81416 | -0.85598 | -1.9014 | -2.6473 | -4.2245 | -6.3127 | -8.0228 | -9.6203 | -11.3241 | -15.3938 | -28.9105 | -36.4474 | -37.8886
|  | UPTON | FS |  |  | 0.4153 | 0.25959 | 0.055198 | -0.73553 | -1.6164 | -3.4645 | -5.8756 | -8.417 | -11.2716 | -14.3913 | -21.3327 | -35.5046 | -40.6481 | -43.3997 | 4.5401 | 4.4283 | 4.2955 | 3.9116 | 3.5068 | 2.2495 | 0.69986 | -0.92041 | -2.4146 | -3.9064 | -7.2236 | -16.8552 | -28.4681 | -39.3372 | -0.85389 | -0.91043 | -0.99411 | -1.3844 | -1.7979 | -3.0694 | -4.5401 | -6.1251 | -7.5958 | -9.0929 | -12.4264 | -22.1541 | -32.7956 | -39.1463
NURSLING GSP | VELMORE BSP | VELMORE | MINIMUM HEADROOM | SU 42935 19205 | YES | 4.6929 | 4.0753 | 3.4705 | 2.6194 | 1.4747 | -0.33538 | -3.052 | -6.3069 | -10.2333 | -14.9948 | -27.1701 | -56.709 | -74.5105 | -81.7828 | 10.0015 | 9.6436 | 9.1577 | 8.4545 | 7.5187 | 6.1965 | 4.0527 | 1.5601 | -1.3973 | -5.015 | -14.3236 | -37.0169 | -50.9336 | -56.9618 | 5.9585 | 5.4418 | 4.995 | 4.0779 | 2.7995 | 1.1202 | -1.5158 | -4.6555 | -8.4163 | -12.9813 | -24.6538 | -52.9935 | -70.1976 | -77.4163
|  | VELMORE | CT |  |  | 4.9838 | 4.7128 | 4.4981 | 4.2222 | 3.8924 | 3.4109 | 2.6805 | 1.9292 | 0.61946 | -1.0702 | -4.7248 | -13.0277 | -17.4402 | -20.2778 | 10.1069 | 9.9585 | 9.8508 | 9.7137 | 9.4928 | 9.1134 | 8.473 | 7.753 | 6.7116 | 5.5148 | 2.8887 | -2.7575 | -6.5467 | -10.7166 | 6.3161 | 6.0802 | 5.9274 | 5.5098 | 5.0168 | 4.4177 | 3.5002 | 2.5916 | 1.145 | -0.44375 | -3.8919 | -11.5603 | -15.6707 | -18.3546
|  | VELMORE | LW |  |  | 4.6929 | 4.0753 | 3.4705 | 2.6194 | 1.4747 | -0.33538 | -3.052 | -6.3069 | -10.2333 | -14.9948 | -27.1701 | -56.709 | -74.5105 | -81.7828 | 10.0015 | 9.6436 | 9.1577 | 8.4545 | 7.5187 | 6.1965 | 4.0527 | 1.5601 | -1.3973 | -5.015 | -14.3236 | -37.0169 | -50.9336 | -56.9618 | 5.9585 | 5.4418 | 4.995 | 4.0779 | 2.7995 | 1.1202 | -1.5158 | -4.6555 | -8.4163 | -12.9813 | -24.6538 | -52.9935 | -70.1976 | -77.4163
|  | VELMORE | ST |  |  | 5.0454 | 4.8773 | 4.7857 | 4.5549 | 4.2628 | 3.9164 | 3.2921 | 2.7876 | 2.1554 | 1.3017 | -1.5421 | -10.7698 | -17.1872 | -20.6637 | 10.1542 | 10.0419 | 9.9673 | 9.7238 | 9.4989 | 9.1659 | 8.4136 | 7.717 | 6.8916 | 5.9606 | 3.6789 | -4.1018 | -10.0939 | -14.462 | 6.3544 | 6.1244 | 5.9884 | 5.6729 | 5.3139 | 4.8937 | 4.1546 | 3.4773 | 2.6463 | 1.607 | -1.1408 | -10.1573 | -16.4312 | -19.7263
|  | VELMORE | FS |  |  | 4.9838 | 4.7128 | 4.4981 | 4.2222 | 3.8924 | 3.4109 | 2.6805 | 1.9292 | 0.61946 | -1.0702 | -4.7248 | -13.0277 | -17.4402 | -20.2778 | 10.2704 | 10.1312 | 10.0288 | 9.9082 | 9.7807 | 9.6163 | 9.3428 | 8.8975 | 8.3865 | 7.7988 | 6.2793 | 0.44253 | -7.0857 | -14.3919 | 6.4984 | 6.2983 | 6.1745 | 5.9837 | 5.7766 | 5.5124 | 5.1532 | 4.7487 | 4.2289 | 3.6449 | 2.1593 | -4.338 | -11.9067 | -17.0939
FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR | MINIMUM HEADROOM | SZ 56148 77857 | YES | 18.1305 | 17.8683 | 17.5971 | 17.2286 | 16.8255 | 16.3783 | 15.8604 | 15.2676 | 14.5271 | 13.658 | 11.6391 | 7.7279 | 5.8939 | 4.5393 | 19.4638 | 19.3536 | 19.2319 | 19.0643 | 18.863 | 18.6169 | 18.3031 | 17.9128 | 17.4253 | 16.8447 | 15.4314 | 12.525 | 10.3633 | 7.9612 | 17.0884 | 16.8595 | 16.6193 | 16.2919 | 15.9265 | 15.5115 | 15.0194 | 14.443 | 13.7273 | 12.908 | 10.9922 | 7.2911 | 5.6548 | 4.4553
|  | VENTNOR | CT |  |  | 18.3917 | 18.2669 | 18.132 | 17.8422 | 17.5221 | 17.159 | 16.7488 | 16.2323 | 15.4523 | 14.5846 | 12.6931 | 8.3552 | 5.8939 | 4.5393 | 19.5313 | 19.4556 | 19.36 | 19.1976 | 19.0018 | 18.7577 | 18.455 | 18.0715 | 17.5467 | 16.9363 | 15.5485 | 12.525 | 10.6713 | 8.7343 | 17.3083 | 17.1953 | 17.0696 | 16.8073 | 16.5107 | 16.1651 | 15.7625 | 15.2744 | 14.5458 | 13.7299 | 11.9412 | 7.8027 | 5.6548 | 4.4553
|  | VENTNOR | LW |  |  | 18.1305 | 17.8683 | 17.5971 | 17.2286 | 16.8255 | 16.3783 | 15.8604 | 15.2676 | 14.5271 | 13.658 | 11.6391 | 7.7279 | 5.9692 | 5.0361 | 19.4638 | 19.3536 | 19.2319 | 19.0643 | 18.863 | 18.6169 | 18.3031 | 17.9128 | 17.4253 | 16.8447 | 15.4314 | 12.9102 | 11.9985 | 11.44 | 17.0884 | 16.8595 | 16.6193 | 16.2919 | 15.9265 | 15.5115 | 15.0194 | 14.443 | 13.7273 | 12.908 | 10.9922 | 7.2911 | 5.7294 | 4.8782
|  | VENTNOR | ST |  |  | 18.5276 | 18.4774 | 18.4148 | 18.3211 | 18.2048 | 18.0511 | 17.8534 | 17.6014 | 17.2982 | 16.9115 | 15.8488 | 11.2465 | 8.2254 | 6.8141 | 19.5626 | 19.5095 | 19.4417 | 19.3516 | 19.2366 | 19.0907 | 18.9025 | 18.661 | 18.3689 | 17.9981 | 16.9617 | 13.091 | 10.3633 | 8.6591 | 17.4172 | 17.366 | 17.3013 | 17.2057 | 17.0852 | 16.9373 | 16.7466 | 16.502 | 16.2066 | 15.8288 | 14.7104 | 10.2322 | 7.3665 | 6.1572
|  | VENTNOR | FS |  |  | 18.3917 | 18.2669 | 18.132 | 17.8422 | 17.5221 | 17.159 | 16.7488 | 16.2323 | 15.4523 | 14.5846 | 12.6931 | 8.3552 | 5.8939 | 4.5393 | 19.5788 | 19.531 | 19.4773 | 19.3964 | 19.3008 | 19.1892 | 19.0501 | 18.8848 | 18.679 | 18.4396 | 17.8233 | 15.2805 | 11.7953 | 7.9612 | 17.4399 | 17.3992 | 17.3588 | 17.2582 | 17.1478 | 17.027 | 16.8837 | 16.7177 | 16.495 | 16.2443 | 15.6262 | 13.0012 | 9.8288 | 7.628
MANNINGTON GSP | MANNINGTON BSP | VERWOOD | MINIMUM HEADROOM | SU 07716 10226 | YES | -1.1399 | -1.4768 | -1.8642 | -2.5349 | -3.2467 | -4.0665 | -5.0235 | -6.1349 | -7.6683 | -9.4307 | -13.3161 | -20.2691 | -23.4783 | -25.5446 | 1.6135 | 1.4495 | 1.2537 | 0.93282 | 0.57301 | 0.13391 | -0.41157 | -1.0791 | -1.9922 | -3.0917 | -5.7016 | -10.572 | -14.1498 | -16.2094 | -1.7982 | -2.0898 | -2.4268 | -3.0149 | -3.6509 | -4.3915 | -5.2669 | -6.2962 | -7.7092 | -9.3755 | -13.0773 | -19.6546 | -22.6913 | -24.7337
|  | VERWOOD | CT |  |  | -0.80918 | -0.97089 | -1.1744 | -1.6732 | -2.2082 | -2.838 | -3.615 | -4.5649 | -6.1433 | -7.9247 | -11.6105 | -19.5243 | -23.3624 | -25.5446 | 1.7203 | 1.6047 | 1.4566 | 1.1787 | 0.85968 | 0.46337 | -0.047567 | -0.66379 | -1.5922 | -2.7527 | -5.2646 | -10.572 | -13.3357 | -15.81 | -1.5077 | -1.6463 | -1.8227 | -2.2631 | -2.7473 | -3.3243 | -4.0458 | -4.938 | -6.4007 | -8.0744 | -11.5845 | -19.0551 | -22.6068 | -24.6718
|  | VERWOOD | LW |  |  | -1.1399 | -1.4768 | -1.8642 | -2.5349 | -3.2467 | -4.0665 | -5.0235 | -6.1349 | -7.6683 | -9.4307 | -13.3161 | -20.2691 | -23.4783 | -25.5178 | 1.6135 | 1.4495 | 1.2537 | 0.93282 | 0.57301 | 0.13391 | -0.41157 | -1.0791 | -1.9922 | -3.0917 | -5.7016 | -10.2196 | -12.2524 | -13.8748 | -1.7982 | -2.0898 | -2.4268 | -3.0149 | -3.6509 | -4.3915 | -5.2669 | -6.2962 | -7.7092 | -9.3755 | -13.0773 | -19.6546 | -22.6913 | -24.7337
|  | VERWOOD | ST |  |  | -0.80509 | -0.97972 | -1.1866 | -1.4952 | -1.8261 | -2.2346 | -2.7828 | -3.4694 | -4.3574 | -5.3619 | -7.6692 | -15.2623 | -20.0823 | -22.3807 | 1.6985 | 1.5611 | 1.3985 | 1.1478 | 0.89246 | 0.58179 | 0.16291 | -0.34964 | -1.0844 | -1.9134 | -3.8859 | -10.1683 | -14.1498 | -16.2094 | -1.5106 | -1.6653 | -1.8484 | -2.1391 | -2.4413 | -2.8331 | -3.3657 | -4.0307 | -4.8912 | -5.8652 | -8.1462 | -15.6019 | -20.2691 | -22.3643
|  | VERWOOD | FS |  |  | -0.80918 | -0.97089 | -1.1744 | -1.6732 | -2.2082 | -2.838 | -3.615 | -4.5649 | -6.1433 | -7.9247 | -11.6105 | -19.5243 | -23.3624 | -25.5446 | 1.7563 | 1.673 | 1.5709 | 1.4388 | 1.3016 | 1.1383 | 0.94816 | 0.73345 | 0.41285 | 0.044666 | -0.83397 | -4.6425 | -9.7263 | -14.3219 | -1.4294 | -1.5043 | -1.599 | -1.7543 | -1.9113 | -2.0982 | -2.3114 | -2.548 | -2.9469 | -3.4193 | -4.5328 | -9.1144 | -14.807 | -18.8738
COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD | MINIMUM HEADROOM | SU 59847 89486 | NO | 2.6596 | 2.3653 | 2.1186 | 1.851 | 1.5509 | 1.2817 | 0.64412 | -0.11122 | -0.96724 | -1.823 | -3.6995 | -7.0059 | -8.8893 | -10.4087 | 6.5384 | 6.3353 | 6.183 | 5.8737 | 5.5507 | 5.2701 | 4.9165 | 4.2994 | 3.6568 | 2.9884 | 1.6734 | -1.6987 | -4.0369 | -6.3536 | 2.6722 | 2.2486 | 1.8491 | 1.2686 | 0.66682 | 0.13808 | -0.45509 | -1.1309 | -1.8907 | -2.6548 | -4.1472 | -6.8953 | -8.8823 | -10.1779
|  | WALLINGFORD | CT |  |  | 2.7608 | 2.6105 | 2.44 | 2.2544 | 2.0603 | 1.824 | 1.5257 | 1.1091 | 0.51009 | -0.4295 | -2.0875 | -6.0347 | -8.8893 | -10.4087 | 6.6212 | 6.5313 | 6.4275 | 6.2316 | 5.9573 | 5.6826 | 5.3374 | 4.9121 | 4.3922 | 3.8603 | 2.8637 | 0.38 | -1.8004 | -4.1916 | 3.0023 | 2.8157 | 2.6022 | 2.2014 | 1.7705 | 1.3649 | 0.87666 | 0.29262 | -0.54672 | -1.3678 | -2.8492 | -6.3916 | -8.8823 | -10.1779
|  | WALLINGFORD | LW |  |  | 2.6596 | 2.3653 | 2.1186 | 1.851 | 1.5509 | 1.2817 | 0.64412 | -0.11122 | -0.96724 | -1.823 | -3.6995 | -7.0059 | -8.3375 | -9.2538 | 6.5384 | 6.3353 | 6.183 | 5.8737 | 5.5507 | 5.2701 | 4.9429 | 4.5495 | 4.1043 | 3.3799 | 1.8611 | -0.23908 | -0.88683 | -1.2835 | 2.6722 | 2.2486 | 1.8491 | 1.2686 | 0.66682 | 0.13808 | -0.45509 | -1.1309 | -1.8907 | -2.6548 | -4.1472 | -6.8953 | -8.4539 | -9.2157
|  | WALLINGFORD | ST |  |  | 2.8078 | 2.689 | 2.5445 | 2.3634 | 2.1688 | 1.961 | 1.667 | 1.0611 | 0.29505 | -0.48927 | -1.9863 | -5.7093 | -7.8302 | -9.4418 | 6.6297 | 6.5417 | 6.3125 | 6.0319 | 5.7245 | 5.3866 | 4.9165 | 4.2994 | 3.6568 | 2.9884 | 1.6734 | -1.6987 | -4.0369 | -6.3536 | 3.0288 | 2.8353 | 2.6039 | 2.3148 | 1.991 | 1.6106 | 1.0772 | 0.37242 | -0.37357 | -1.1428 | -2.6237 | -6.3681 | -8.5158 | -9.9139
|  | WALLINGFORD | FS |  |  | 2.7608 | 2.6105 | 2.44 | 2.2544 | 2.0603 | 1.824 | 1.5257 | 1.1091 | 0.51009 | -0.4295 | -2.0875 | -6.0347 | -8.8893 | -10.4087 | 6.7044 | 6.5786 | 6.4667 | 6.3608 | 6.1967 | 6.0337 | 5.8429 | 5.6318 | 5.3911 | 5.1369 | 4.6041 | 2.6493 | -0.17173 | -4.3021 | 3.1667 | 3.0072 | 2.8515 | 2.6534 | 2.44 | 2.2759 | 2.0902 | 1.8884 | 1.6284 | 1.367 | 0.87335 | -0.86893 | -2.8507 | -4.8402
COWLEY GSP | DRAYTON BSP | WANTAGE | MINIMUM HEADROOM | SU 41290 88304 | NO | 10.1788 | 8.996 | 7.6641 | 5.9239 | 4.0139 | 2.136 | 0.61879 | -0.99268 | -2.6509 | -4.2634 | -8.4712 | -15.8006 | -18.7424 | -20.8606 | 9.8096 | 8.995 | 8.0163 | 6.6634 | 5.128 | 3.6385 | 2.4049 | 1.2094 | 0.10082 | -0.86008 | -3.867 | -9.3398 | -14.4552 | -16.7246 | 9.5817 | 8.5882 | 7.4519 | 5.9512 | 4.2209 | 2.4996 | 1.06 | -0.49287 | -2.1315 | -3.7631 | -7.8173 | -14.8127 | -18.37 | -20.0679
|  | WANTAGE | CT |  |  | 10.5412 | 9.4178 | 8.1364 | 6.4769 | 4.7688 | 3.295 | 2.1126 | 0.6331 | -1.2437 | -3.1328 | -7.2208 | -15.0809 | -18.524 | -20.8329 | 9.9677 | 9.1013 | 8.0686 | 6.6945 | 5.2317 | 4.0532 | 3.1259 | 2.0471 | 0.75904 | -0.58285 | -3.6216 | -9.3398 | -11.9773 | -14.5855 | 9.8735 | 8.9158 | 7.8071 | 6.3614 | 4.8504 | 3.4922 | 2.3259 | 0.864 | -0.94857 | -2.7538 | -6.6887 | -14.1553 | -17.2669 | -19.3392
|  | WANTAGE | LW |  |  | 10.1788 | 8.996 | 7.6641 | 5.9239 | 4.0139 | 2.136 | 0.61879 | -0.99268 | -2.6509 | -4.2634 | -8.4712 | -15.8006 | -18.5707 | -20.4887 | 9.8096 | 8.995 | 8.0163 | 6.6634 | 5.128 | 3.6385 | 2.4049 | 1.2094 | 0.10082 | -0.86008 | -3.867 | -8.9466 | -10.5966 | -11.7811 | 9.5817 | 8.5882 | 7.4519 | 5.9512 | 4.2209 | 2.4996 | 1.06 | -0.49287 | -2.1315 | -3.7631 | -7.8173 | -14.8127 | -17.3258 | -19.0493
|  | WANTAGE | ST |  |  | 10.6337 | 9.5712 | 8.3633 | 6.9128 | 5.479 | 4.3327 | 3.4706 | 2.4242 | 1.2893 | 0.20467 | -2.591 | -12.431 | -18.7424 | -20.8606 | 9.9828 | 9.139 | 8.1504 | 6.8361 | 5.4513 | 4.4616 | 3.7226 | 2.8607 | 1.9421 | 1.2536 | -1.0194 | -9.0284 | -14.4552 | -16.7246 | 9.9313 | 9.0193 | 7.9731 | 6.6997 | 5.4283 | 4.3708 | 3.5326 | 2.5013 | 1.393 | 0.34502 | -2.3887 | -12.0496 | -18.37 | -20.0679
|  | WANTAGE | FS |  |  | 10.5412 | 9.4178 | 8.1364 | 6.4769 | 4.7688 | 3.295 | 2.1126 | 0.6331 | -1.2437 | -3.1328 | -7.2208 | -15.0809 | -18.524 | -20.8329 | 10.175 | 9.6095 | 8.9594 | 8.1566 | 7.2813 | 6.4432 | 5.6938 | 4.8664 | 4.0052 | 3.1471 | 1.152 | -4.9425 | -11.1442 | -15.9911 | 10.1488 | 9.5412 | 8.8466 | 7.9599 | 7.024 | 6.1248 | 5.3197 | 4.4037 | 3.4168 | 2.4228 | 0.17409 | -6.7661 | -13.5056 | -17.5112
MANNINGTON GSP | WAREHAM | WAREHAM TOWN | MINIMUM HEADROOM | SY 92036 87463 | YES | 2.3585 | 2.0346 | 1.5392 | 0.91295 | 0.14508 | -0.72457 | -1.8173 | -3.0546 | -4.5926 | -6.269 | -10.0115 | -16.6726 | -19.7267 | -22.0845 | 0.71705 | 0.45223 | -0.047109 | -0.33672 | -0.69183 | -1.0739 | -1.5935 | -2.2379 | -3.0261 | -3.8225 | -5.872 | -10.7459 | -13.4012 | -15.8566 | 2.2729 | 1.9746 | 1.5204 | 0.94881 | 0.24031 | -0.56409 | -1.5838 | -2.7528 | -4.2228 | -5.8373 | -9.4683 | -15.9002 | -18.9568 | -21.4882
|  | WAREHAM TOWN | CT |  |  | 2.5709 | 2.2742 | 1.7389 | 1.2538 | 0.62254 | -0.10137 | -1.0182 | -2.0812 | -3.5989 | -5.2819 | -8.8155 | -16.0741 | -19.4716 | -21.6729 | 0.75424 | 0.45223 | -0.047109 | -0.33672 | -0.69183 | -1.0739 | -1.5183 | -1.9922 | -2.7061 | -3.5389 | -5.5038 | -10.7459 | -13.4012 | -15.8566 | 2.4573 | 2.1772 | 1.6716 | 1.2324 | 0.64696 | -0.022709 | -0.89228 | -1.9071 | -3.3523 | -4.9794 | -8.4125 | -15.4235 | -18.6954 | -20.9006
|  | WAREHAM TOWN | LW |  |  | 2.3585 | 2.0346 | 1.5392 | 0.91295 | 0.14508 | -0.72457 | -1.8173 | -3.0546 | -4.5926 | -6.269 | -10.0115 | -16.6726 | -19.7267 | -22.0845 | 0.71705 | 0.50985 | 0.16064 | -0.17535 | -0.58735 | -1.0304 | -1.5935 | -2.2379 | -3.0261 | -3.8225 | -5.872 | -10.5579 | -12.867 | -15.059 | 2.2729 | 1.9746 | 1.5204 | 0.94881 | 0.24031 | -0.56409 | -1.5838 | -2.7528 | -4.2228 | -5.8373 | -9.4683 | -15.9002 | -18.9568 | -21.4882
|  | WAREHAM TOWN | ST |  |  | 2.6299 | 2.3895 | 1.9228 | 1.6119 | 1.2226 | 0.81431 | 0.30354 | -0.24124 | -0.96346 | -1.7176 | -3.5334 | -10.4494 | -15.0658 | -16.9793 | 0.78125 | 0.50158 | 0.026645 | -0.26612 | -0.58665 | -0.90681 | -1.2766 | -1.6266 | -2.085 | -2.4962 | -3.1825 | -8.0773 | -12.1379 | -14.2629 | 2.5113 | 2.2856 | 1.8439 | 1.5412 | 1.1797 | 0.80159 | 0.31016 | -0.21111 | -0.92126 | -1.666 | -3.5103 | -10.5311 | -15.2065 | -17.0667
|  | WAREHAM TOWN | FS |  |  | 2.5709 | 2.2742 | 1.7389 | 1.2538 | 0.62254 | -0.10137 | -1.0182 | -2.0812 | -3.5989 | -5.2819 | -8.8155 | -16.0741 | -19.4716 | -21.6729 | 0.78119 | 0.67023 | 0.45996 | 0.26359 | 0.044656 | -0.17595 | -0.41793 | -0.67809 | -1.0017 | -1.334 | -1.9864 | -5.1161 | -10.6877 | -15.2385 | 2.5107 | 2.4052 | 2.1998 | 1.9759 | 1.71 | 1.4257 | 1.0934 | 0.71727 | 0.2197 | -0.32609 | -1.6454 | -6.8296 | -13.2046 | -17.3582
BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD | MINIMUM HEADROOM | SU 86960 71382 | YES | 1.7901 | 1.4587 | 1.0894 | 0.23578 | -1.0189 | -2.6927 | -4.6912 | -6.6734 | -8.9379 | -11.2247 | -15.8963 | -23.389 | -26.3315 | -27.8057 | 6.3167 | 6.1651 | 5.99 | 5.5855 | 4.9838 | 4.1701 | 3.1838 | 2.1791 | 1.0631 | -0.083477 | -2.5718 | -6.8469 | -9.7099 | -12.612 | 2.3041 | 1.9963 | 1.6569 | 0.86634 | -0.26617 | -1.769 | -3.574 | -5.3883 | -7.4158 | -9.4159 | -13.5617 | -20.3129 | -23.0101 | -24.4131
|  | WARFIELD | CT |  |  | 2.101 | 1.9424 | 1.7419 | 1.1118 | 0.13274 | -1.2146 | -2.7445 | -4.3127 | -6.4313 | -8.6641 | -13.4402 | -21.6555 | -25.48 | -27.5125 | 6.3885 | 6.2641 | 6.1066 | 5.7701 | 5.2544 | 4.5508 | 3.7287 | 2.86 | 1.758 | 0.54223 | -2.0174 | -6.8469 | -9.7099 | -12.612 | 2.6104 | 2.4709 | 2.2953 | 1.7244 | 0.8566 | -0.33602 | -1.708 | -3.1314 | -5.0849 | -7.1558 | -11.3742 | -18.7656 | -22.1896 | -24.0289
|  | WARFIELD | LW |  |  | 1.7901 | 1.4587 | 1.0894 | 0.23578 | -1.0189 | -2.6927 | -4.6912 | -6.6734 | -8.9379 | -11.2247 | -15.8963 | -23.389 | -26.3315 | -27.8057 | 6.3167 | 6.1651 | 5.99 | 5.5855 | 4.9838 | 4.1701 | 3.1838 | 2.1791 | 1.0631 | -0.083477 | -2.5718 | -6.6691 | -8.2755 | -9.2925 | 2.3041 | 1.9963 | 1.6569 | 0.86634 | -0.26617 | -1.769 | -3.574 | -5.3883 | -7.4158 | -9.4159 | -13.5617 | -20.3129 | -23.0101 | -24.4131
|  | WARFIELD | ST |  |  | 2.1604 | 2.0432 | 1.8911 | 1.5135 | 0.91295 | 0.1085 | -0.77279 | -1.5889 | -2.5161 | -3.5042 | -5.6863 | -11.0512 | -14.7418 | -17.3282 | 6.4155 | 6.3132 | 6.1852 | 5.9049 | 5.5205 | 5.0267 | 4.4625 | 3.93 | 3.3284 | 2.6718 | 1.1408 | -3.1069 | -6.3171 | -9.1475 | 2.6684 | 2.5707 | 2.4433 | 2.1074 | 1.6051 | 0.94194 | 0.20134 | -0.48467 | -1.2704 | -2.1183 | -4.0384 | -9.0655 | -12.5676 | -15.0671
|  | WARFIELD | FS |  |  | 2.101 | 1.9424 | 1.7419 | 1.1118 | 0.13274 | -1.2146 | -2.7445 | -4.3127 | -6.4313 | -8.6641 | -13.4402 | -21.6555 | -25.48 | -27.5125 | 6.4149 | 6.3087 | 6.1771 | 5.9628 | 5.6413 | 5.2121 | 4.7126 | 4.2231 | 3.6675 | 3.0937 | 1.8051 | -2.148 | -6.4804 | -10.9147 | 2.681 | 2.5978 | 2.4895 | 2.2244 | 1.8123 | 1.2495 | 0.59756 | -0.018258 | -0.76062 | -1.5059 | -3.1022 | -7.7179 | -12.3323 | -15.801
MELKSHAM GSP | FROME BSP | WARMINSTER | MINIMUM HEADROOM | ST 84936 44551 | YES | 5.4483 | 5.1409 | 4.8613 | 4.3394 | 3.7739 | 3.1628 | 2.495 | 1.9327 | 1.3021 | 0.66028 | -0.57051 | -2.3699 | -3.8576 | -4.7059 | 5.1096 | 4.8688 | 4.7097 | 4.4298 | 4.1483 | 3.8507 | 3.5295 | 3.2615 | 2.9716 | 2.6743 | 2.1001 | 1.0371 | 0.1692 | -0.63109 | 4.8971 | 4.6187 | 4.398 | 3.988 | 3.5441 | 3.0627 | 2.5338 | 2.0833 | 1.5622 | 1.0129 | -0.045204 | -1.6162 | -2.8814 | -3.596
|  | WARMINSTER | CT |  |  | 5.5483 | 5.3009 | 5.1846 | 4.8307 | 4.404 | 3.9137 | 3.3742 | 2.8862 | 2.1845 | 1.4437 | 0.068462 | -2.322 | -3.8576 | -4.7059 | 5.1883 | 4.9435 | 4.8513 | 4.6456 | 4.4359 | 4.1886 | 3.9079 | 3.6477 | 3.2946 | 2.9199 | 2.2287 | 1.0371 | 0.1692 | -0.63109 | 5.0431 | 4.8209 | 4.6992 | 4.3955 | 4.0646 | 3.6807 | 3.2532 | 2.8621 | 2.2992 | 1.6965 | 0.503 | -1.5668 | -2.8814 | -3.596
|  | WARMINSTER | LW |  |  | 5.4483 | 5.1409 | 4.8613 | 4.3394 | 3.7739 | 3.1628 | 2.495 | 1.9327 | 1.3021 | 0.66028 | -0.57051 | -2.3699 | -3.3782 | -3.8269 | 5.1096 | 4.8688 | 4.7097 | 4.4298 | 4.1483 | 3.8507 | 3.5295 | 3.2615 | 2.9716 | 2.6743 | 2.1001 | 1.2899 | 0.86196 | 0.67564 | 4.8971 | 4.6187 | 4.398 | 3.988 | 3.5441 | 3.0627 | 2.5338 | 2.0833 | 1.5622 | 1.0129 | -0.045204 | -1.6162 | -2.4727 | -2.8265
|  | WARMINSTER | ST |  |  | 5.5907 | 5.3697 | 5.2805 | 5.0785 | 4.821 | 4.5383 | 4.2428 | 3.9993 | 3.7325 | 3.4404 | 2.9304 | 1.9701 | 1.0369 | -0.12232 | 5.2142 | 4.9853 | 4.9099 | 4.7495 | 4.6066 | 4.4452 | 4.2659 | 4.1151 | 3.95 | 3.7703 | 3.4553 | 2.8069 | 2.1277 | 1.1925 | 5.0883 | 4.8924 | 4.7985 | 4.594 | 4.3994 | 4.1842 | 3.9553 | 3.7654 | 3.56 | 3.335 | 2.941 | 2.153 | 1.3922 | 0.46109
|  | WARMINSTER | FS |  |  | 5.5483 | 5.3009 | 5.1846 | 4.8307 | 4.404 | 3.9137 | 3.3742 | 2.8862 | 2.1845 | 1.4437 | 0.068462 | -2.322 | -3.8576 | -4.7059 | 5.2421 | 5.1048 | 5.0113 | 4.8636 | 4.712 | 4.5589 | 4.392 | 4.2565 | 4.0902 | 3.9177 | 3.5835 | 2.886 | 1.9899 | 0.54867 | 5.1162 | 4.99 | 4.8949 | 4.7154 | 4.523 | 4.3266 | 4.1191 | 3.9522 | 3.7499 | 3.5429 | 3.162 | 2.4094 | 1.6881 | 0.82779
LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE | MINIMUM HEADROOM | SU 67988 09282 | YES | 22.4445 | 21.4864 | 20.4447 | 19.0199 | 17.4456 | 15.6487 | 13.4091 | 11.0161 | 7.9441 | 3.0958 | -7.3996 | -25.7272 | -31.8033 | -35.5887 | 28.0147 | 27.4101 | 26.7532 | 26.0088 | 25.1831 | 24.2355 | 22.9853 | 21.3655 | 18.0528 | 14.2562 | 6.5449 | -6.7335 | -10.8792 | -13.7138 | 23.2398 | 22.4131 | 21.504 | 20.2652 | 18.895 | 17.3313 | 15.348 | 13.1979 | 10.2739 | 5.5201 | -4.4448 | -21.8071 | -27.5079 | -31.1208
|  | WATERLOOVILLE | CT |  |  | 23.0566 | 22.4055 | 21.7409 | 20.8604 | 19.8293 | 18.5457 | 16.9156 | 15.1496 | 12.2477 | 9.3247 | 4.069 | -7.394 | -13.7728 | -17.319 | 28.2334 | 27.699 | 27.1722 | 26.6988 | 26.1247 | 25.3816 | 24.3629 | 23.2182 | 21.3831 | 19.446 | 16.1287 | 9.0408 | 4.5576 | 0.24238 | 23.7551 | 23.1819 | 22.5982 | 21.8457 | 20.9522 | 19.8276 | 18.3517 | 16.7181 | 14.067 | 11.3379 | 6.4729 | -3.9726 | -9.6249 | -12.7477
|  | WATERLOOVILLE | LW |  |  | 22.4445 | 21.4864 | 20.4447 | 19.0199 | 17.4456 | 15.6487 | 13.4091 | 11.0161 | 7.9441 | 3.0958 | -7.3996 | -25.7272 | -31.8033 | -35.5887 | 28.0147 | 27.4101 | 26.7532 | 26.0088 | 25.1831 | 24.2355 | 22.9853 | 21.3655 | 18.0528 | 14.2562 | 6.5449 | -6.7335 | -10.8792 | -13.7138 | 23.2398 | 22.4131 | 21.504 | 20.2652 | 18.895 | 17.3313 | 15.348 | 13.1979 | 10.2739 | 5.5201 | -4.4448 | -21.8071 | -27.5079 | -31.1208
|  | WATERLOOVILLE | ST |  |  | 23.2028 | 22.635 | 22.0641 | 21.6797 | 21.2324 | 20.6446 | 19.818 | 18.9248 | 17.5568 | 16.1595 | 13.7244 | 5.2461 | -0.95653 | -5.0764 | 28.2774 | 27.7717 | 27.2835 | 26.9722 | 26.6161 | 26.1553 | 25.4717 | 24.7335 | 23.5804 | 22.3714 | 20.3974 | 13.655 | 8.4001 | 4.2195 | 23.868 | 23.3599 | 22.8535 | 22.5079 | 22.1073 | 21.5798 | 20.7993 | 19.9596 | 18.6976 | 17.386 | 15.182 | 7.1614 | 1.4047 | -2.1632
|  | WATERLOOVILLE | FS |  |  | 23.0566 | 22.4055 | 21.7409 | 20.8604 | 19.8293 | 18.5457 | 16.9156 | 15.1496 | 12.2477 | 9.3247 | 4.069 | -7.394 | -13.7728 | -17.319 | 28.3694 | 27.9528 | 27.4904 | 27.0734 | 26.6314 | 26.0775 | 25.4193 | 24.6159 | 23.5592 | 22.4722 | 20.393 | 13.839 | 6.2323 | -1.9076 | 23.9583 | 23.5455 | 23.0797 | 22.6049 | 22.0983 | 21.4523 | 20.6951 | 19.767 | 18.5453 | 17.3218 | 15.0207 | 7.6938 | 0.29698 | -5.1443
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON | MINIMUM HEADROOM | SU 69106 94287 | YES | 1.4462 | 1.1852 | 0.94531 | 0.67117 | -0.15533 | -1.3138 | -2.9381 | -5.1119 | -7.8323 | -11.2151 | -19.8099 | -33.6918 | -37.6138 | -40.7989 | 2.897 | 2.7478 | 2.5444 | 2.184 | 1.6586 | 0.90335 | -0.17722 | -1.6451 | -3.7488 | -6.3744 | -13.0599 | -23.8369 | -26.9914 | -29.7438 | 1.2481 | 1.0632 | 0.83214 | 0.26757 | -0.52352 | -1.6349 | -3.1945 | -5.2809 | -7.8918 | -11.1395 | -19.3897 | -32.7214 | -36.5842 | -39.8121
|  | WATLINGTON | CT |  |  | 1.6147 | 1.4939 | 1.39 | 1.2292 | 1.0508 | 0.85217 | 0.62051 | 0.39185 | 0.05147 | -0.32996 | -1.1289 | -2.9252 | -4.3636 | -5.1255 | 3.0046 | 2.9706 | 2.9442 | 2.8835 | 2.776 | 2.6493 | 2.4874 | 2.3276 | 2.1166 | 1.8469 | 1.2689 | -0.10338 | -1.2929 | -2.4043 | 1.3783 | 1.2748 | 1.193 | 1.0666 | 0.92009 | 0.75282 | 0.54747 | 0.34506 | 0.052385 | -0.29776 | -1.0439 | -2.7067 | -4.0112 | -4.767
|  | WATLINGTON | LW |  |  | 1.4462 | 1.1852 | 0.94531 | 0.67117 | -0.15533 | -1.3138 | -2.9381 | -5.1119 | -7.8323 | -11.2151 | -19.8099 | -33.6918 | -37.6138 | -40.7989 | 2.897 | 2.7478 | 2.5444 | 2.184 | 1.6586 | 0.90335 | -0.17722 | -1.6451 | -3.7488 | -6.3744 | -13.0599 | -23.8369 | -26.9914 | -29.7438 | 1.2481 | 1.0632 | 0.83214 | 0.26757 | -0.52352 | -1.6349 | -3.1945 | -5.2809 | -7.8918 | -11.1395 | -19.3897 | -32.7214 | -36.5842 | -39.8121
|  | WATLINGTON | ST |  |  | 1.6137 | 1.4781 | 1.3574 | 1.1439 | 0.93432 | 0.68029 | 0.37983 | 0.031297 | -0.39348 | -0.81475 | -1.6785 | -3.9936 | -5.6987 | -6.9507 | 3.0146 | 2.9841 | 2.8963 | 2.7092 | 2.5356 | 2.3236 | 2.0642 | 1.7797 | 1.4207 | 1.0678 | 0.33174 | -1.6917 | -3.329 | -4.8344 | 1.3711 | 1.2495 | 1.136 | 0.91346 | 0.70169 | 0.4468 | 0.1405 | -0.20531 | -0.63456 | -1.0579 | -1.9286 | -4.2656 | -5.9985 | -7.2512
|  | WATLINGTON | FS |  |  | 1.6147 | 1.4939 | 1.39 | 1.2292 | 1.0508 | 0.85217 | 0.62051 | 0.39185 | 0.05147 | -0.32996 | -1.1289 | -2.9252 | -4.3636 | -5.1255 | 3.0055 | 2.8512 | 2.6971 | 2.497 | 2.2387 | 1.9528 | 1.5011 | 0.94586 | 0.32468 | -0.37701 | -2.0074 | -5.7907 | -8.5302 | -9.9481 | 1.3137 | 1.1183 | 0.9375 | 0.68391 | 0.3629 | 0.012447 | -0.53472 | -1.2027 | -1.9632 | -2.8164 | -4.7835 | -9.4306 | -12.6058 | -13.799
AMERSHAM | LOUDWATER BSP | WELL END | MINIMUM HEADROOM | SU 88511 87957 | YES | 7.217 | 6.7398 | 6.2253 | 5.5472 | 4.8013 | 3.9374 | 2.9057 | 1.7687 | -0.44134 | -3.354 | -11.4552 | -40.8645 | -63.6548 | -70.4699 | 11.368 | 11.1993 | 11.013 | 10.806 | 10.3378 | 9.5854 | 8.5499 | 7.1981 | 5.4688 | 3.2924 | -2.8534 | -25.4847 | -43.1214 | -48.4176 | 7.1427 | 6.753 | 6.3285 | 5.7237 | 5.0507 | 4.2665 | 3.3245 | 1.6864 | -0.54761 | -3.3261 | -11.0718 | -39.2353 | -61.0679 | -67.5976
|  | WELL END | CT |  |  | 7.5253 | 7.2475 | 6.9345 | 6.4861 | 5.9846 | 5.3811 | 4.6412 | 3.8102 | 2.641 | 1.3435 | -1.4839 | -7.5708 | -10.3194 | -11.6365 | 11.4404 | 11.3334 | 11.2171 | 11.1206 | 11.009 | 10.8578 | 10.6701 | 10.3885 | 9.6286 | 8.7551 | 6.7803 | 2.5178 | 0.19136 | -2.129 | 7.4082 | 7.1848 | 6.9284 | 6.5673 | 6.1401 | 5.6114 | 4.9542 | 4.1941 | 3.138 | 1.9465 | -0.68968 | -6.2322 | -8.7169 | -9.9079
|  | WELL END | LW |  |  | 7.217 | 6.7398 | 6.2253 | 5.5472 | 4.8013 | 3.9374 | 2.9057 | 1.7687 | -0.44134 | -3.354 | -11.4552 | -40.8645 | -63.6548 | -70.4699 | 11.368 | 11.1993 | 11.013 | 10.806 | 10.3378 | 9.5854 | 8.5499 | 7.1981 | 5.4688 | 3.2924 | -2.8534 | -25.4847 | -43.1214 | -48.4176 | 7.1427 | 6.753 | 6.3285 | 5.7237 | 5.0507 | 4.2665 | 3.3245 | 1.6864 | -0.54761 | -3.3261 | -11.0718 | -39.2353 | -61.0679 | -67.5976
|  | WELL END | ST |  |  | 7.5068 | 7.2081 | 6.8768 | 6.5964 | 6.2688 | 5.8764 | 5.3235 | 4.6882 | 3.9987 | 3.1679 | 0.99427 | -6.2522 | -11.1249 | -13.0473 | 11.446 | 11.3456 | 11.2365 | 11.1283 | 11.0113 | 10.874 | 10.6906 | 10.4936 | 9.9063 | 9.1789 | 7.2719 | 1.072 | -3.2551 | -5.6106 | 7.3698 | 7.1138 | 6.8284 | 6.5648 | 6.2498 | 5.8711 | 5.3261 | 4.6845 | 3.9761 | 3.1166 | 0.85282 | -6.5717 | -11.3235 | -12.824
|  | WELL END | FS |  |  | 7.5253 | 7.2475 | 6.9345 | 6.4861 | 5.9846 | 5.3811 | 4.6412 | 3.8102 | 2.641 | 1.3435 | -1.4839 | -7.5708 | -10.3194 | -11.6365 | 11.461 | 11.3724 | 11.2738 | 11.1926 | 11.1039 | 10.9982 | 10.8753 | 10.7451 | 10.6112 | 10.2693 | 8.9281 | 3.795 | -1.7029 | -6.2357 | 7.4322 | 7.2464 | 7.0299 | 6.8251 | 6.5947 | 6.3052 | 5.9589 | 5.5649 | 5.0946 | 4.5261 | 2.9847 | -2.8473 | -8.5824 | -11.6713
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END | MINIMUM HEADROOM | SU 57216 06147 | YES | 13.9647 | 13.6709 | 13.365 | 12.8371 | 12.2463 | 11.5874 | 10.9627 | 10.2865 | 9.386 | 8.5017 | 6.8403 | 3.142 | 0.28509 | -1.7425 | 17.6172 | 17.49 | 17.357 | 17.1383 | 16.8843 | 16.5916 | 16.3042 | 15.9858 | 15.5454 | 15.0967 | 14.2534 | 11.8264 | 8.9702 | 5.5614 | 14.3722 | 14.1228 | 13.8657 | 13.398 | 12.8795 | 12.3031 | 11.7444 | 11.1387 | 10.3203 | 9.5104 | 7.9779 | 4.6855 | 2.2337 | 0.41022
|  | WEST END | CT |  |  | 14.3048 | 14.1958 | 14.0736 | 13.7434 | 13.368 | 12.9211 | 12.5231 | 12.0776 | 11.1674 | 10.2619 | 8.5569 | 3.89 | 0.28509 | -1.7425 | 17.7098 | 17.6229 | 17.523 | 17.3546 | 17.1568 | 16.9174 | 16.6907 | 16.4298 | 15.969 | 15.4863 | 14.5226 | 11.8264 | 8.9702 | 5.7226 | 14.6709 | 14.5831 | 14.4861 | 14.1971 | 13.873 | 13.49 | 13.1407 | 12.7477 | 11.9332 | 11.1158 | 9.5682 | 5.4259 | 2.2337 | 0.41022
|  | WEST END | LW |  |  | 13.9647 | 13.6709 | 13.365 | 12.8371 | 12.2463 | 11.5874 | 10.9627 | 10.2865 | 9.386 | 8.5017 | 6.8403 | 3.142 | 0.71383 | -0.63389 | 17.6172 | 17.49 | 17.357 | 17.1383 | 16.8843 | 16.5916 | 16.3042 | 15.9858 | 15.5454 | 15.0967 | 14.2534 | 12.5644 | 11.3052 | 10.3291 | 14.3722 | 14.1228 | 13.8657 | 13.398 | 12.8795 | 12.3031 | 11.7444 | 11.1387 | 10.3203 | 9.5104 | 7.9779 | 4.6855 | 2.4737 | 1.1536
|  | WEST END | ST |  |  | 14.4316 | 14.3833 | 14.3127 | 14.26 | 14.1556 | 14.002 | 13.8585 | 13.658 | 13.3841 | 13.1145 | 12.5981 | 10.6554 | 8.3497 | 5.293 | 17.7432 | 17.6659 | 17.5707 | 17.4689 | 17.3412 | 17.1777 | 16.9987 | 16.7747 | 16.4733 | 16.1642 | 15.5224 | 13.5459 | 10.9422 | 7.1417 | 14.7802 | 14.7434 | 14.6891 | 14.6343 | 14.5492 | 14.4266 | 14.3034 | 14.1322 | 13.8798 | 13.6293 | 13.1348 | 11.358 | 9.1964 | 6.3213
|  | WEST END | FS |  |  | 14.3048 | 14.1958 | 14.0736 | 13.7434 | 13.368 | 12.9211 | 12.5231 | 12.0776 | 11.1674 | 10.2619 | 8.5569 | 3.89 | 0.28509 | -1.7425 | 17.7555 | 17.6941 | 17.6182 | 17.5375 | 17.4328 | 17.3054 | 17.1859 | 17.0474 | 16.8346 | 16.6117 | 16.1181 | 14.2752 | 11.1295 | 5.5614 | 14.7816 | 14.7655 | 14.74 | 14.6811 | 14.5998 | 14.4985 | 14.4194 | 14.327 | 14.1403 | 13.9624 | 13.6109 | 12.2718 | 10.4654 | 8.1385
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE | MINIMUM HEADROOM | SU 24639 60279 | YES | 1.8621 | 1.6612 | 1.4483 | 1.2955 | 1.1078 | 0.8856 | 0.21445 | -0.82834 | -2.1519 | -3.7661 | -7.6749 | -14.3342 | -16.2837 | -17.5796 | 3.4149 | 3.3304 | 3.2365 | 3.1552 | 3.0179 | 2.8206 | 2.5633 | 1.9658 | 0.96261 | -0.26993 | -3.2694 | -8.3553 | -9.7263 | -10.6919 | 1.8208 | 1.6526 | 1.4696 | 1.3254 | 1.1134 | 0.64444 | 0.024131 | -0.82903 | -2.0936 | -3.6378 | -7.3801 | -13.7495 | -15.5875 | -16.8187
|  | WEST GRAFTON VILLAGE | CT |  |  | 1.9904 | 1.8495 | 1.6886 | 1.4975 | 1.2663 | 0.97354 | 0.21445 | -0.82834 | -2.1519 | -3.7661 | -7.6749 | -14.3342 | -16.2837 | -17.5796 | 3.4485 | 3.3728 | 3.2801 | 3.1658 | 3.0179 | 2.8206 | 2.5633 | 1.9658 | 0.96261 | -0.26993 | -3.2694 | -8.3553 | -9.7263 | -10.6919 | 1.925 | 1.8064 | 1.6674 | 1.4564 | 1.1134 | 0.64444 | 0.024131 | -0.82903 | -2.0936 | -3.6378 | -7.3801 | -13.7495 | -15.5875 | -16.8187
|  | WEST GRAFTON VILLAGE | LW |  |  | 1.8621 | 1.6612 | 1.4483 | 1.2955 | 1.1078 | 0.8856 | 0.62382 | 0.30367 | -0.077986 | -0.52223 | -1.7619 | -4.1812 | -5.1197 | -5.5928 | 3.4149 | 3.3304 | 3.2365 | 3.1552 | 3.048 | 2.9106 | 2.7335 | 2.5053 | 2.2254 | 1.857 | 0.89814 | -0.83331 | -1.4258 | -1.734 | 1.8208 | 1.6526 | 1.4696 | 1.3254 | 1.1426 | 0.91636 | 0.63688 | 0.28398 | -0.14446 | -0.65635 | -1.9305 | -4.2618 | -5.1397 | -5.5785
|  | WEST GRAFTON VILLAGE | ST |  |  | 2.0878 | 1.9993 | 1.9116 | 1.7841 | 1.6441 | 1.4788 | 1.2935 | 1.0737 | 0.82085 | 0.52034 | -0.32191 | -3.5303 | -5.532 | -6.0174 | 3.4835 | 3.4319 | 3.3749 | 3.2993 | 3.2097 | 3.0989 | 2.9653 | 2.7997 | 2.6094 | 2.3699 | 1.6443 | -0.92084 | -2.5695 | -3.1023 | 1.9909 | 1.9126 | 1.8293 | 1.7094 | 1.5726 | 1.4063 | 1.2114 | 0.97229 | 0.69146 | 0.34889 | -0.57407 | -3.7339 | -5.6938 | -6.108
|  | WEST GRAFTON VILLAGE | FS |  |  | 1.9904 | 1.8495 | 1.6886 | 1.4975 | 1.2663 | 0.97354 | 0.21445 | -0.82834 | -2.1519 | -3.7661 | -7.6749 | -14.3342 | -16.2837 | -17.5796 | 3.4832 | 3.4212 | 3.354 | 3.2681 | 3.1702 | 3.0513 | 2.9005 | 2.7077 | 2.4783 | 2.2132 | 1.6025 | -0.35799 | -2.1125 | -3.0713 | 1.9992 | 1.9167 | 1.8291 | 1.6936 | 1.5448 | 1.3672 | 1.1472 | 0.86996 | 0.54647 | 0.19387 | -0.59907 | -3.1502 | -5.2739 | -6.3107
AXMINSTER | YEOVIL BSP | WEST HENDFORD | MINIMUM HEADROOM | ST 55000 15442 | YES | 27.9341 | 27.8078 | 27.6501 | 27.4693 | 27.2614 | 26.99 | 26.5927 | 25.8324 | 24.8723 | 23.7813 | 21.1743 | 13.6579 | 7.7296 | 5.6406 | 30.284 | 30.2039 | 30.1048 | 29.987 | 29.8482 | 29.6659 | 29.4433 | 29.1648 | 28.8306 | 28.1145 | 26.3551 | 20.7211 | 16.3133 | 14.7476 | 28.1399 | 27.9993 | 27.8268 | 27.6243 | 27.3466 | 26.9499 | 26.4691 | 25.8372 | 25.057 | 24.1549 | 21.9729 | 14.1418 | 8.4871 | 6.4853
|  | WEST HENDFORD | CT |  |  | 27.9341 | 27.8078 | 27.6501 | 27.4693 | 27.2614 | 26.99 | 26.5927 | 25.8324 | 24.8723 | 23.7813 | 21.1743 | 13.6579 | 7.7296 | 5.6406 | 30.284 | 30.2039 | 30.1048 | 29.987 | 29.8482 | 29.6659 | 29.4433 | 29.1648 | 28.8306 | 28.1145 | 26.3551 | 20.7211 | 16.3133 | 14.7476 | 28.1399 | 27.9993 | 27.8268 | 27.6243 | 27.3466 | 26.9499 | 26.4691 | 25.8372 | 25.057 | 24.1549 | 21.9729 | 14.1418 | 8.4871 | 6.4853
|  | WEST HENDFORD | LW |  |  | 27.957 | 27.8226 | 27.6786 | 27.5129 | 27.3196 | 27.1122 | 26.8346 | 26.3205 | 25.7087 | 25.0493 | 23.6485 | 21.9676 | 21.2668 | 20.4965 | 30.3038 | 30.2244 | 30.1413 | 30.037 | 29.9135 | 29.7774 | 29.5937 | 29.3893 | 29.1718 | 28.9325 | 28.2993 | 27.2871 | 26.88 | 26.4989 | 28.1768 | 28.0344 | 27.8919 | 27.7243 | 27.4854 | 27.2181 | 26.8355 | 26.3993 | 25.9227 | 25.4009 | 24.2821 | 22.6352 | 21.8219 | 21.3057
|  | WEST HENDFORD | ST |  |  | 27.9925 | 27.9067 | 27.7943 | 27.6348 | 27.4715 | 27.2877 | 27.0638 | 26.817 | 26.5278 | 26.2062 | 25.4462 | 23.2819 | 22.0563 | 21.1374 | 30.3192 | 30.263 | 30.1909 | 30.0662 | 29.9439 | 29.8077 | 29.6358 | 29.4556 | 29.2401 | 29.0036 | 28.444 | 26.167 | 23.7604 | 20.9642 | 28.2292 | 28.1521 | 28.0505 | 27.8892 | 27.7232 | 27.5338 | 27.2974 | 27.0383 | 26.7287 | 26.3529 | 25.4086 | 23.1505 | 22.2199 | 21.6143
|  | WEST HENDFORD | FS |  |  | 27.9341 | 27.8078 | 27.6501 | 27.4693 | 27.2614 | 26.99 | 26.5927 | 25.8324 | 24.8723 | 23.7813 | 21.1743 | 13.6579 | 7.7296 | 5.6406 | 30.3279 | 30.2846 | 30.2264 | 30.1501 | 30.0646 | 29.9671 | 29.8582 | 29.7395 | 29.6064 | 29.4589 | 29.0992 | 27.4165 | 23.5061 | 17.8554 | 28.2416 | 28.1841 | 28.1046 | 28.0031 | 27.8881 | 27.7559 | 27.6076 | 27.4441 | 27.2626 | 27.0609 | 26.5269 | 24.9792 | 23.5893 | 22.6865
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR | MINIMUM HEADROOM | ST 77699 22040 | YES | 2.1841 | 1.9122 | 1.5464 | 1.0216 | 0.29246 | -0.90281 | -2.6401 | -4.9963 | -8.0099 | -11.7711 | -20.9125 | -36.5917 | -41.0151 | -44.2556 | 3.4239 | 3.3497 | 3.2535 | 3.1023 | 2.685 | 1.7261 | 0.37253 | -1.4618 | -3.8108 | -6.767 | -13.9478 | -26.2983 | -29.7961 | -32.4902 | 2.2637 | 2.1095 | 1.9489 | 1.8196 | 1.3344 | 0.13902 | -1.534 | -3.7977 | -6.6958 | -10.3246 | -19.1339 | -34.2808 | -38.6086 | -41.8312
|  | WEST STOUR | CT |  |  | 2.1841 | 1.9122 | 1.5464 | 1.0216 | 0.29246 | -0.90281 | -2.6401 | -4.9963 | -8.0099 | -11.7711 | -20.9125 | -36.5917 | -41.0151 | -44.2556 | 3.438 | 3.3572 | 3.2535 | 3.1023 | 2.685 | 1.7261 | 0.37253 | -1.4618 | -3.8108 | -6.767 | -13.9478 | -26.2983 | -29.7961 | -32.4902 | 2.3417 | 2.2167 | 2.0649 | 1.8528 | 1.3344 | 0.13902 | -1.534 | -3.7977 | -6.6958 | -10.3246 | -19.1339 | -34.2808 | -38.6086 | -41.8312
|  | WEST STOUR | LW |  |  | 2.2211 | 2.0417 | 1.8638 | 1.7296 | 1.5838 | 1.4325 | 1.2542 | 1.0584 | 0.81349 | 0.53236 | -0.035587 | -0.97213 | -1.8597 | -2.7842 | 3.4239 | 3.3497 | 3.2718 | 3.2054 | 3.1273 | 3.0361 | 2.9183 | 2.77 | 2.5528 | 2.2978 | 1.709 | 0.65811 | -0.31728 | -1.4932 | 2.2637 | 2.1095 | 1.9489 | 1.8196 | 1.674 | 1.5088 | 1.3133 | 1.0829 | 0.783 | 0.43808 | -0.3677 | -1.8468 | -3.0215 | -4.2764
|  | WEST STOUR | ST |  |  | 2.4069 | 2.3301 | 2.2516 | 2.0819 | 1.9204 | 1.7589 | 1.5735 | 1.4053 | 1.1816 | 0.9439 | 0.38865 | -2.2889 | -4.9023 | -6.2677 | 3.4735 | 3.4249 | 3.3682 | 3.2109 | 3.0633 | 2.9032 | 2.6947 | 2.4958 | 2.2154 | 1.9078 | 1.1132 | -1.5218 | -3.8112 | -5.1884 | 2.3977 | 2.3145 | 2.224 | 2.0209 | 1.8226 | 1.6095 | 1.3435 | 1.0777 | 0.72517 | 0.33525 | -0.65962 | -3.9041 | -6.6152 | -8.0964
|  | WEST STOUR | FS |  |  | 2.1841 | 1.9122 | 1.5464 | 1.0216 | 0.29246 | -0.90281 | -2.6401 | -4.9963 | -8.0099 | -11.7711 | -20.9125 | -36.5917 | -41.0151 | -44.2556 | 3.4553 | 3.3743 | 3.2877 | 3.1634 | 3.0175 | 2.8368 | 2.6047 | 2.3037 | 1.9409 | 1.5589 | 0.75533 | -1.145 | -2.3637 | -3.0576 | 2.3948 | 2.2823 | 2.1659 | 1.9911 | 1.7891 | 1.5453 | 1.2414 | 0.85129 | 0.37618 | -0.12479 | -1.1666 | -3.7282 | -5.328 | -6.1571
MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE | MINIMUM HEADROOM | SZ 07642 91485 | YES | 13.3395 | 13.0977 | 12.8423 | 12.3062 | 11.6872 | 10.9704 | 10.0373 | 8.9656 | 7.3166 | 4.4211 | -2.0599 | -13.8753 | -27.9261 | -33.0066 | 15.585 | 15.4537 | 15.2739 | 14.9422 | 14.5522 | 14.0803 | 13.3707 | 12.5552 | 11.4617 | 9.2796 | 4.3456 | -4.6261 | -15.3582 | -23.8898 | 12.4835 | 12.2577 | 12.0204 | 11.5311 | 10.9647 | 10.3044 | 9.3503 | 8.2612 | 6.7808 | 4.0122 | -2.1998 | -13.4992 | -26.9938 | -31.9422
|  | WESTBOURNE | CT |  |  | 13.5793 | 13.486 | 13.3663 | 12.9458 | 12.4609 | 11.8893 | 11.1375 | 10.2656 | 9.237 | 8.0594 | 3.8305 | -13.8753 | -27.9261 | -33.0066 | 15.5939 | 15.4537 | 15.2739 | 14.9422 | 14.5522 | 14.0803 | 13.3707 | 12.5552 | 11.7167 | 10.7254 | 8.542 | -4.6261 | -15.3582 | -19.3609 | 12.7059 | 12.6192 | 12.5092 | 12.1316 | 11.6959 | 11.1786 | 10.4049 | 9.5185 | 8.5654 | 7.4639 | 3.4369 | -13.4992 | -26.9938 | -31.9422
|  | WESTBOURNE | LW |  |  | 13.3395 | 13.0977 | 12.8423 | 12.3062 | 11.6872 | 10.9704 | 10.0373 | 8.9656 | 7.3166 | 4.4211 | -2.0599 | -13.4193 | -17.3446 | -20.4146 | 15.585 | 15.4547 | 15.3186 | 15.0478 | 14.7238 | 14.3313 | 13.6975 | 12.9633 | 11.4617 | 9.2796 | 4.3456 | -4.2341 | -7.333 | -10.0784 | 12.4835 | 12.2577 | 12.0204 | 11.5311 | 10.9647 | 10.3044 | 9.3503 | 8.2612 | 6.7808 | 4.0122 | -2.1998 | -13.0927 | -16.9953 | -20.196
|  | WESTBOURNE | ST |  |  | 13.8359 | 13.8803 | 13.9101 | 13.8356 | 13.7435 | 13.6178 | 13.3676 | 13.0903 | 12.7997 | 12.4657 | 11.7463 | 8.8196 | 6.4446 | 4.0203 | 15.6922 | 15.6105 | 15.5052 | 15.3221 | 15.1126 | 14.8602 | 14.4062 | 13.9116 | 13.4544 | 12.9406 | 11.7411 | 7.1248 | 0.93893 | -8.2527 | 12.9566 | 13.0046 | 13.0408 | 12.9916 | 12.925 | 12.8204 | 12.5117 | 12.1778 | 11.9038 | 11.5896 | 10.8718 | 7.9832 | 5.537 | 3.1522
|  | WESTBOURNE | FS |  |  | 13.5793 | 13.486 | 13.3663 | 12.9458 | 12.4609 | 11.8893 | 11.1375 | 10.2656 | 9.237 | 8.0594 | 3.8305 | -13.8753 | -27.9261 | -33.0066 | 15.6453 | 15.5078 | 15.346 | 15.0753 | 14.7461 | 14.3686 | 13.8713 | 13.2958 | 12.6794 | 11.9792 | 10.3182 | 3.8112 | -6.7175 | -23.8898 | 12.8841 | 12.8825 | 12.8716 | 12.7405 | 12.5745 | 12.3731 | 12.0785 | 11.7286 | 11.3664 | 10.9587 | 10.0457 | 6.4829 | 2.5021 | -0.53402
MELKSHAM GSP | FROME BSP | WESTBURY | MINIMUM HEADROOM | ST 87654 51530 | YES | 9.52 | 8.9289 | 8.295 | 7.4785 | 6.5499 | 5.5994 | 4.5316 | 3.3174 | 1.7881 | -1.2352 | -10.0066 | -29.1519 | -42.6079 | -50.6708 | 15.5695 | 15.2377 | 14.8643 | 14.4271 | 13.9155 | 13.4016 | 12.8185 | 12.1386 | 10.3 | 7.7381 | 1.1805 | -13.1602 | -23.4873 | -29.9445 | 10.9168 | 10.3874 | 9.8141 | 9.0835 | 8.2535 | 7.4057 | 6.4558 | 5.3768 | 4.0261 | 1.3992 | -6.9628 | -25.2171 | -38.1533 | -46.0217
|  | WESTBURY | CT |  |  | 10.017 | 9.6465 | 9.2289 | 8.7058 | 8.1145 | 7.5702 | 6.9418 | 6.255 | 5.0677 | 3.8035 | 1.2008 | -5.1994 | -9.5052 | -12.0659 | 15.7507 | 15.4615 | 15.1159 | 14.794 | 14.408 | 14.0606 | 13.6198 | 13.1196 | 12.3733 | 11.515 | 9.6894 | 5.4782 | 2.409 | -0.78273 | 11.3484 | 11.0032 | 10.602 | 10.1166 | 9.559 | 9.0341 | 8.4097 | 7.7176 | 6.559 | 5.2927 | 2.6513 | -3.4699 | -7.3272 | -9.6531
|  | WESTBURY | LW |  |  | 9.52 | 8.9289 | 8.295 | 7.4785 | 6.5499 | 5.5994 | 4.5316 | 3.3174 | 1.7881 | -1.2352 | -10.0066 | -29.1519 | -42.6079 | -50.6708 | 15.5695 | 15.2377 | 14.8643 | 14.4271 | 13.9155 | 13.4016 | 12.8185 | 12.1386 | 10.3 | 7.7381 | 1.1805 | -13.1602 | -23.4873 | -29.9445 | 10.9168 | 10.3874 | 9.8141 | 9.0835 | 8.2535 | 7.4057 | 6.4558 | 5.3768 | 4.0261 | 1.3992 | -6.9628 | -25.2171 | -38.1533 | -46.0217
|  | WESTBURY | ST |  |  | 10.2082 | 9.9482 | 9.6424 | 9.3624 | 9.0579 | 8.8543 | 8.5877 | 8.3393 | 8.0135 | 7.6728 | 6.9072 | 3.3042 | -0.15053 | -3.2012 | 15.8267 | 15.5869 | 15.2961 | 15.0288 | 14.7505 | 14.5543 | 14.2876 | 14.0359 | 13.6957 | 13.326 | 12.4418 | 9.0774 | 5.8781 | 2.5557 | 11.5152 | 11.2687 | 10.9702 | 10.6847 | 10.383 | 10.1707 | 9.8863 | 9.6208 | 9.2683 | 8.8912 | 8.0035 | 4.3916 | 1.1416 | -1.8212
|  | WESTBURY | FS |  |  | 10.017 | 9.6465 | 9.2289 | 8.7058 | 8.1145 | 7.5702 | 6.9418 | 6.255 | 5.0677 | 3.8035 | 1.2008 | -5.1994 | -9.5052 | -12.0659 | 15.8743 | 15.7132 | 15.5263 | 15.3179 | 15.0909 | 14.8873 | 14.6634 | 14.4263 | 14.101 | 13.7396 | 12.8986 | 10.0153 | 5.9862 | 0.57298 | 11.5835 | 11.429 | 11.257 | 11.0073 | 10.7422 | 10.5039 | 10.2498 | 9.9859 | 9.6211 | 9.2299 | 8.3605 | 5.3978 | 2.0714 | -1.0592
NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE | MINIMUM HEADROOM | SU 41618 12009 | YES | 29.9396 | 29.2379 | 28.1171 | 26.8677 | 24.6351 | 22.6938 | 20.4431 | 18.1517 | 16.2217 | 14.518 | 11.7187 | -2.1375 | -8.5954 | -8.739 | 32.1654 | 31.5975 | 30.5792 | 29.5557 | 27.9615 | 26.5461 | 24.6165 | 22.6525 | 21.1871 | 20.098 | 17.3734 | 6.8013 | 1.7078 | 1.4295 | 27.9952 | 27.2372 | 26.0452 | 24.8859 | 22.8692 | 21.0185 | 18.8 | 16.5603 | 14.7737 | 13.2529 | 10.5469 | -3.2029 | -9.4782 | -9.7396
|  | WESTERN ESPLANADE | CT |  |  | 30.065 | 29.372 | 28.2656 | 27.3029 | 25.4258 | 23.8203 | 22.1218 | 20.2184 | 18.4915 | 16.8868 | 14.5754 | 10.3573 | 8.1241 | 6.7785 | 32.2349 | 31.5975 | 30.5792 | 29.5557 | 27.9615 | 26.6284 | 25.1793 | 23.5663 | 22.2981 | 21.2464 | 19.6754 | 16.3232 | 13.2881 | 9.217 | 28.2062 | 27.5193 | 26.375 | 25.2509 | 23.4037 | 21.9096 | 20.2903 | 18.4823 | 16.9405 | 15.5719 | 13.5824 | 9.8233 | 7.7549 | 6.4531
|  | WESTERN ESPLANADE | LW |  |  | 29.9396 | 29.2379 | 28.1171 | 26.8677 | 24.6351 | 22.6938 | 20.4431 | 18.1517 | 16.2217 | 14.518 | 11.7187 | -2.1375 | -8.5954 | -8.739 | 32.1654 | 31.6097 | 30.7001 | 29.7223 | 28.1066 | 26.5461 | 24.6165 | 22.6525 | 21.1871 | 20.098 | 17.3734 | 6.8013 | 1.7078 | 1.4295 | 27.9952 | 27.2372 | 26.0452 | 24.8859 | 22.8692 | 21.0185 | 18.8 | 16.5603 | 14.7737 | 13.2529 | 10.5469 | -3.2029 | -9.4782 | -9.7396
|  | WESTERN ESPLANADE | ST |  |  | 30.2502 | 29.6562 | 28.6512 | 27.8055 | 26.3987 | 25.3193 | 24.0539 | 22.6641 | 21.5653 | 20.6509 | 19.333 | 15.4372 | 13.3077 | 11.8705 | 32.337 | 31.7499 | 30.7694 | 29.7867 | 28.3236 | 27.1268 | 25.825 | 24.4122 | 23.3807 | 22.6115 | 21.4178 | 17.959 | 14.7242 | 10.4447 | 28.3901 | 27.7878 | 26.7482 | 25.858 | 24.3782 | 23.2314 | 21.9875 | 20.6401 | 19.6556 | 18.9039 | 17.6634 | 13.8861 | 11.7478 | 10.3598
|  | WESTERN ESPLANADE | FS |  |  | 30.065 | 29.372 | 28.2656 | 27.3029 | 25.4258 | 23.8203 | 22.1218 | 20.2184 | 18.4915 | 16.8868 | 14.5754 | 10.3573 | 8.1241 | 6.7785 | 32.3705 | 32.0419 | 31.4421 | 30.8536 | 29.9203 | 29.0795 | 28.1873 | 27.2139 | 26.2968 | 25.4609 | 24.0156 | 19.7597 | 14.8507 | 7.4986 | 28.4593 | 28.12 | 27.5077 | 26.9665 | 26.0348 | 25.2503 | 24.4415 | 23.5282 | 22.7066 | 21.9752 | 20.8283 | 17.7352 | 14.8479 | 12.568
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON | MINIMUM HEADROOM | SU 45207 09912 | YES | 9.6575 | 9.4202 | 9.1414 | 8.6243 | 8.0125 | 7.2603 | 6.2709 | 5.0362 | 3.4622 | 1.6182 | -2.8132 | -10.8266 | -14.0745 | -16.5601 | 10.9986 | 10.8725 | 10.7228 | 10.4529 | 10.125 | 9.7188 | 9.1854 | 8.4797 | 7.3956 | 6.0934 | 2.9071 | -2.8611 | -6.6971 | -14.3702 | 9.2164 | 8.9579 | 8.6641 | 8.1429 | 7.5193 | 6.7654 | 5.7846 | 4.5537 | 2.9734 | 1.1217 | -3.2133 | -10.9082 | -14.002 | -16.5388
|  | WESTON | CT |  |  | 9.8859 | 9.7745 | 9.6234 | 9.2313 | 8.7569 | 8.1715 | 7.4265 | 6.463 | 5.0721 | 3.4366 | -0.29817 | -8.2877 | -11.9737 | -14.3277 | 11.0904 | 11.0101 | 10.9063 | 10.6859 | 10.421 | 10.0944 | 9.6578 | 8.9426 | 7.9323 | 6.7083 | 3.8911 | -2.196 | -5.9968 | -10.3512 | 9.4906 | 9.4122 | 9.323 | 9.0393 | 8.7351 | 8.351 | 7.6385 | 6.7115 | 5.3772 | 3.7921 | 0.16506 | -7.4624 | -10.9617 | -13.2718
|  | WESTON | LW |  |  | 9.6575 | 9.4202 | 9.1414 | 8.6243 | 8.0125 | 7.2603 | 6.2709 | 5.0362 | 3.4622 | 1.6182 | -2.8132 | -10.8266 | -14.0745 | -16.5601 | 10.9986 | 10.8725 | 10.7228 | 10.4529 | 10.125 | 9.7188 | 9.1854 | 8.4797 | 7.3956 | 6.0934 | 2.9071 | -2.8611 | -5.4403 | -7.8467 | 9.2164 | 8.9579 | 8.6641 | 8.1429 | 7.5193 | 6.7654 | 5.7846 | 4.5537 | 2.9734 | 1.1217 | -3.2133 | -10.9082 | -14.002 | -16.5388
|  | WESTON | ST |  |  | 9.9779 | 9.907 | 9.8143 | 9.6945 | 9.5063 | 9.2712 | 8.8858 | 8.358 | 7.6552 | 6.7956 | 4.4316 | -3.9621 | -9.6208 | -11.9199 | 11.1409 | 11.0844 | 11.0133 | 10.9253 | 10.8 | 10.6466 | 10.3402 | 9.8705 | 9.2229 | 8.446 | 6.3595 | -0.85421 | -6.6971 | -10.9639 | 9.6307 | 9.6295 | 9.62 | 9.6024 | 9.5617 | 9.3247 | 8.94 | 8.4152 | 7.7055 | 6.8412 | 4.4725 | -3.882 | -9.6056 | -11.7802
|  | WESTON | FS |  |  | 9.8859 | 9.7745 | 9.6234 | 9.2313 | 8.7569 | 8.1715 | 7.4265 | 6.463 | 5.0721 | 3.4366 | -0.29817 | -8.2877 | -11.9737 | -14.3277 | 11.136 | 11.0844 | 11.0177 | 10.9179 | 10.8023 | 10.6529 | 10.478 | 10.2405 | 9.7696 | 9.2421 | 7.9299 | 2.6424 | -5.0769 | -14.3702 | 9.6109 | 9.6078 | 9.5976 | 9.5357 | 9.4704 | 9.3914 | 9.2103 | 8.8725 | 8.4145 | 7.9088 | 6.6545 | 1.5135 | -4.73 | -9.0507
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH | MINIMUM HEADROOM | SY 67443 79096 | YES | 3.7121 | 3.2737 | 32.6299 | 31.6213 | 30.4889 | 29.252 | 27.9208 | 26.4625 | 24.6624 | 22.7752 | 18.7919 | 9.6285 | 3.7303 | 0.56056 | 5.0244 | 4.843 | 33.1315 | 32.7197 | 32.2374 | 31.6876 | 31.0641 | 30.3592 | 29.3064 | 28.1122 | 25.5348 | 18.3026 | 6.2625 | -16.1663 | 3.7348 | 3.362 | 31.4449 | 30.5909 | 29.6215 | 28.547 | 27.3796 | 26.0964 | 24.4906 | 22.7983 | 19.2052 | 10.9421 | 5.5068 | 2.4212
|  | WEYMOUTH | CT |  |  | 4.3098 | 4.1718 | 33.8392 | 33.1566 | 32.3739 | 31.4926 | 30.554 | 29.5073 | 27.7345 | 25.888 | 22.1405 | 12.3954 | 5.3368 | 1.1373 | 5.1354 | 4.9657 | 33.2516 | 32.8342 | 32.3427 | 31.7684 | 31.124 | 30.3831 | 29.3064 | 28.1122 | 25.5348 | 18.3026 | 9.9511 | -1.7835 | 4.237 | 4.1174 | 32.4612 | 31.8838 | 31.2204 | 30.4663 | 29.65 | 28.7294 | 27.1776 | 25.5361 | 22.1772 | 13.5504 | 7.2636 | 3.4591
|  | WEYMOUTH | LW |  |  | 3.7121 | 3.2737 | 32.6299 | 31.6213 | 30.4889 | 29.252 | 27.9208 | 26.4625 | 24.6624 | 22.7752 | 18.7919 | 9.6285 | 3.7303 | 0.56056 | 5.0244 | 4.843 | 33.1315 | 32.7197 | 32.2374 | 31.6876 | 31.0641 | 30.3592 | 29.4692 | 28.4978 | 26.3594 | 21.6874 | 18.0394 | 15.051 | 3.7348 | 3.362 | 31.4449 | 30.5909 | 29.6215 | 28.547 | 27.3796 | 26.0964 | 24.4906 | 22.7983 | 19.2052 | 10.9421 | 5.5068 | 2.4212
|  | WEYMOUTH | ST |  |  | 4.5526 | 4.5472 | 34.3398 | 34.2082 | 34.014 | 33.7702 | 33.502 | 33.183 | 32.7465 | 32.2609 | 31.021 | 25.7376 | 20.4374 | 14.685 | 5.21 | 5.085 | 33.4136 | 33.1632 | 32.8602 | 32.5007 | 32.0863 | 31.6134 | 31.0056 | 30.3202 | 28.5985 | 22.0315 | 13.481 | 1.4225 | 4.4345 | 4.4242 | 32.8712 | 32.7475 | 32.5733 | 32.353 | 32.1 | 31.7981 | 31.3959 | 30.9456 | 29.7739 | 24.8114 | 19.7911 | 14.555
|  | WEYMOUTH | FS |  |  | 4.3098 | 4.1718 | 33.8392 | 33.1566 | 32.3739 | 31.4926 | 30.554 | 29.5073 | 27.7345 | 25.888 | 22.1405 | 12.3954 | 5.3368 | 1.1373 | 5.1681 | 4.9967 | 33.283 | 32.9653 | 32.5786 | 32.1436 | 31.6119 | 31.0016 | 30.2052 | 29.3068 | 27.1529 | 19.3159 | 6.2625 | -16.1663 | 4.3797 | 4.3382 | 32.7651 | 32.5768 | 32.3357 | 32.0697 | 31.7386 | 31.3615 | 30.8351 | 30.2592 | 28.9608 | 24.5645 | 19.5893 | 14.8341
COWLEY GSP | HEADINGTON BSP | WHEATLEY | MINIMUM HEADROOM | SP 60777 05379 | NO | 4.7066 | 4.3277 | 3.9192 | 3.3101 | 2.5968 | 1.9248 | 0.75702 | -1.0858 | -3.4093 | -6.2679 | -13.6982 | -27.397 | -31.8906 | -34.9582 | 6.5569 | 6.3702 | 6.159 | 5.8097 | 5.3805 | 4.8264 | 3.7035 | 2.0624 | -0.00066889 | -2.5465 | -8.3299 | -18.9724 | -22.4652 | -25.0495 | 4.4268 | 4.1086 | 3.7593 | 3.2109 | 2.557 | 1.9007 | 1.0718 | 0.030884 | -2.307 | -5.4295 | -12.611 | -25.8911 | -30.3198 | -33.427
|  | WHEATLEY | CT |  |  | 4.9819 | 4.7114 | 4.3582 | 3.8186 | 3.0899 | 2.1116 | 0.75702 | -1.0858 | -3.4093 | -6.2679 | -13.6982 | -27.397 | -31.8906 | -34.9582 | 6.666 | 6.4976 | 6.2885 | 5.9676 | 5.5483 | 4.9212 | 3.7035 | 2.0624 | -0.00066889 | -2.5465 | -8.3299 | -18.9724 | -22.4652 | -25.0495 | 4.6731 | 4.4445 | 4.1653 | 3.7004 | 3.1153 | 2.4774 | 1.6091 | 0.11551 | -2.307 | -5.4295 | -12.611 | -25.8911 | -30.3198 | -33.427
|  | WHEATLEY | LW |  |  | 4.7066 | 4.3277 | 3.9192 | 3.3101 | 2.5968 | 1.9248 | 0.79321 | -0.83629 | -2.7964 | -5.2375 | -11.7684 | -22.5718 | -26.3314 | -29.5345 | 6.5569 | 6.3702 | 6.159 | 5.8097 | 5.3805 | 4.8264 | 3.7134 | 2.2488 | 0.51167 | -1.5974 | -6.6386 | -14.9668 | -18.1505 | -21.2154 | 4.4268 | 4.1086 | 3.7593 | 3.2109 | 2.557 | 1.9007 | 1.0718 | 0.030884 | -1.7779 | -4.4167 | -10.7017 | -21.1194 | -24.9528 | -28.3911
|  | WHEATLEY | ST |  |  | 5.0051 | 4.8168 | 4.6128 | 4.2026 | 3.8284 | 3.5303 | 3.1172 | 2.6909 | 2.166 | 1.5718 | 0.028315 | -5.9197 | -10.0545 | -12.031 | 6.6626 | 6.5477 | 6.4168 | 6.0536 | 5.736 | 5.4453 | 5.0349 | 4.6327 | 4.1335 | 3.5722 | 2.0923 | -3.0935 | -6.8634 | -8.9465 | 4.6858 | 4.5336 | 4.3647 | 3.9483 | 3.5773 | 3.2527 | 2.7974 | 2.3285 | 1.755 | 1.1042 | -0.6101 | -6.7342 | -10.998 | -13.0114
|  | WHEATLEY | FS |  |  | 4.9819 | 4.7114 | 4.3582 | 3.8186 | 3.0899 | 2.1116 | 0.75702 | -1.0858 | -3.4093 | -6.2679 | -13.6982 | -27.397 | -31.8906 | -34.9582 | 6.8428 | 6.6612 | 6.4551 | 6.1743 | 5.8487 | 5.4927 | 5.0394 | 4.4545 | 3.7701 | 3.0085 | 1.1962 | -4.3729 | -9.6873 | -13.0594 | 4.9507 | 4.734 | 4.4888 | 4.1416 | 3.7397 | 3.3148 | 2.775 | 2.071 | 1.2389 | 0.31823 | -1.8527 | -8.5719 | -14.8801 | -18.5064
BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH | MINIMUM HEADROOM | SU 45924 48466 | YES | 0.10273 | -0.12114 | -0.48719 | -1.0799 | -1.9137 | -3.0324 | -4.577 | -6.6664 | -9.332 | -12.661 | -21.3476 | -41.2078 | -55.1903 | -63.3241 | 0.10179 | -0.098772 | -0.38129 | -0.84024 | -1.4903 | -2.3539 | -3.5574 | -5.1839 | -7.2386 | -9.8223 | -16.5837 | -32.0022 | -42.8687 | -49.2491 | 0.15974 | 0.042466 | -0.20148 | -0.76909 | -1.5707 | -2.6451 | -4.1318 | -6.1397 | -8.6964 | -11.8951 | -20.241 | -39.3134 | -52.7406 | -60.5711
|  | WHITCHURCH | CT |  |  | 0.14091 | -0.12114 | -0.48719 | -1.0799 | -1.9137 | -3.0324 | -4.577 | -6.6664 | -9.332 | -12.661 | -21.3476 | -41.2078 | -55.1903 | -63.3241 | 0.10179 | -0.098772 | -0.38129 | -0.84024 | -1.4903 | -2.3539 | -3.5574 | -5.1839 | -7.2386 | -9.8223 | -16.5837 | -32.0022 | -42.8687 | -49.2491 | 0.21577 | 0.11797 | -0.20148 | -0.76909 | -1.5707 | -2.6451 | -4.1318 | -6.1397 | -8.6964 | -11.8951 | -20.241 | -39.3134 | -52.7406 | -60.5711
|  | WHITCHURCH | LW |  |  | 0.10273 | -0.024212 | -0.17329 | -0.44921 | -0.7971 | -1.2238 | -1.7632 | -2.4419 | -3.2829 | -4.2956 | -7.1344 | -17.108 | -24.7819 | -27.3314 | 0.20607 | 0.10836 | -0.004692 | -0.2041 | -0.46978 | -0.78566 | -1.1991 | -1.7213 | -2.3516 | -3.1394 | -5.3285 | -13.0187 | -19.0336 | -21.1267 | 0.15974 | 0.042466 | -0.096719 | -0.35828 | -0.68856 | -1.0871 | -1.5872 | -2.2103 | -3.0111 | -4.0011 | -6.5786 | -16.1514 | -23.5535 | -26.0687
|  | WHITCHURCH | ST |  |  | 0.24461 | 0.20898 | 0.15827 | 0.023322 | -0.14664 | -0.2958 | -0.50845 | -0.76835 | -1.0991 | -1.5125 | -2.7029 | -7.27 | -10.0063 | -10.5777 | 0.32275 | 0.31094 | 0.29452 | 0.18574 | 0.072348 | 0.0027227 | -0.094546 | -0.18212 | -0.29302 | -0.41867 | -1.2067 | -5.2426 | -7.9479 | -9.3661 | 0.29075 | 0.25989 | 0.21566 | 0.079951 | -0.083681 | -0.2229 | -0.42246 | -0.65579 | -0.96717 | -1.3826 | -2.5766 | -7.2653 | -9.9915 | -10.5252
|  | WHITCHURCH | FS |  |  | 0.14091 | -0.12114 | -0.48719 | -1.0799 | -1.9137 | -3.0324 | -4.577 | -6.6664 | -9.332 | -12.661 | -21.3476 | -41.2078 | -55.1903 | -63.3241 | 0.31815 | 0.30214 | 0.28271 | 0.22854 | 0.16132 | 0.095237 | 0.018235 | -0.067571 | -0.4254 | -0.95618 | -2.2666 | -6.6783 | -11.3173 | -14.9452 | 0.23699 | 0.15726 | 0.064969 | -0.08444 | -0.27252 | -0.49687 | -0.81798 | -1.2509 | -1.7757 | -2.3629 | -3.8273 | -8.8348 | -13.5364 | -15.8671
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY | MINIMUM HEADROOM | SU 52936 08794 | NO | 7.1978 | 6.2 | 5.0583 | 3.8601 | 2.6059 | 1.2463 | -0.25194 | -1.5857 | -4.4948 | -7.7676 | -9.5562 | -7.7676 | -8.6979 | -9.5562 | 9.4869 | 9.034 | 8.5743 | 8.0882 | 7.5407 | 6.9121 | 6.0614 | 5.287 | 3.5788 | 1.6846 | -0.2912 | 1.6846 | 0.6579 | -0.2912 | 5.6388 | 4.8197 | 3.8573 | 2.8323 | 1.7389 | 0.55011 | -0.76351 | -1.9476 | -4.5801 | -7.561 | -8.7987 | -7.561 | -8.3921 | -9.1614
|  | WHITELEY | CT |  |  | 7.3529 | 6.4641 | 5.4987 | 4.4858 | 3.4694 | 2.3705 | 1.2127 | -0.12638 | -2.947 | -6.7617 | -9.5562 | -6.7617 | -8.663 | -9.5562 | 9.5363 | 9.1013 | 8.6968 | 8.2725 | 7.8479 | 7.3093 | 6.6295 | 5.8531 | 4.1954 | 1.8786 | -0.2912 | 1.8786 | 0.6579 | -0.2912 | 17.0577 | 16.5944 | 15.9389 | 15.2322 | 14.4791 | 13.6647 | 12.7709 | 11.3664 | 7.9542 | 2.1203 | -5.1802 | -6.596 | -8.3488 | -9.1614
|  | WHITELEY | LW |  |  | 7.1978 | 6.2 | 5.0583 | 3.8601 | 2.6059 | 1.2463 | -0.25194 | -1.5857 | -4.4948 | -7.7676 | -9.1628 | -7.7676 | -8.6979 | -9.1628 | 9.4869 | 9.034 | 8.5743 | 8.0882 | 7.5407 | 6.9121 | 6.0614 | 5.287 | 3.5788 | 1.6846 | 1.0014 | 1.6846 | 1.2324 | 1.0014 | 5.6388 | 4.8197 | 3.8573 | 2.8323 | 1.7389 | 0.55011 | -0.76351 | -1.9476 | -4.5801 | -7.561 | -8.7987 | -7.561 | -8.3921 | -8.7987
|  | WHITELEY | ST |  |  | 7.82 | 7.42 | 7.0543 | 6.666 | 6.1076 | 5.4485 | 4.7722 | 4.1463 | 2.0008 | -1.5023 | -3.6663 | -1.5023 | -3.4195 | -3.6663 | 9.9251 | 9.6232 | 9.3662 | 9.097 | 8.8247 | 8.5328 | 8.2206 | 7.9063 | 6.6792 | 4.0771 | 2.2533 | 4.0771 | 2.5876 | 2.2533 | 6.1166 | 5.7562 | 5.4417 | 5.1145 | 4.7867 | 4.4383 | 3.9069 | 3.3779 | 1.5219 | -2.3363 | -4.4969 | -2.3363 | -4.1702 | -4.4969
|  | WHITELEY | FS |  |  | 7.3529 | 6.4641 | 5.4987 | 4.4858 | 3.4694 | 2.3705 | 1.2127 | -0.12638 | -2.947 | -6.7617 | -9.5562 | -6.7617 | -8.663 | -9.5562 | 9.9615 | 9.6804 | 9.4561 | 9.2273 | 8.9932 | 8.7441 | 8.4888 | 8.2374 | 7.5183 | 5.1729 | 2.4396 | 5.1729 | 3.5796 | 2.4396 | 6.1418 | 5.7988 | 5.513 | 5.2215 | 4.9282 | 4.6178 | 4.3032 | 4.0012 | 2.8767 | 0.0225 | -3.4321 | 0.0225 | -2.7952 | -3.4321
BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITELEY WOOD | MINIMUM HEADROOM | SU 72812 69667 | YES | 5.0009 | 3.6963 | 2.3962 | 0.46541 | -1.7054 | -5.0777 | -11.077 | -19.092 | -29.3652 | -41.7603 | -71.7327 | -94.0838 | -105.8623 | -114.1106 | 10.1224 | 9.3837 | 8.572 | 6.6741 | 4.1611 | 0.77289 | -3.8196 | -9.9804 | -17.7686 | -27.2471 | -50.2653 | -67.5225 | -76.2084 | -82.4979 | 6.6526 | 5.5632 | 4.4657 | 2.7543 | 0.75481 | -3.5234 | -9.2528 | -16.9147 | -26.7174 | -38.5725 | -67.2701 | -88.9401 | -100.1685 | -108.0854
|  | WHITELEY WOOD | CT |  |  | 5.4913 | 4.4173 | 3.3003 | 1.6462 | -0.57495 | -5.0777 | -11.077 | -19.092 | -29.3652 | -41.7603 | -71.7327 | -94.0838 | -105.8623 | -114.1106 | 10.248 | 9.5098 | 8.572 | 6.6741 | 4.1611 | 0.77289 | -3.8196 | -9.9804 | -17.7686 | -27.2471 | -50.2653 | -67.5225 | -76.2084 | -82.4979 | 7.0748 | 6.1717 | 5.2146 | 3.7553 | 0.75481 | -3.5234 | -9.2528 | -16.9147 | -26.7174 | -38.5725 | -67.2701 | -88.9401 | -100.1685 | -108.0854
|  | WHITELEY WOOD | LW |  |  | 5.0009 | 3.6963 | 2.3962 | 0.46541 | -1.7054 | -4.1697 | -6.9315 | -9.9922 | -13.4427 | -17.3039 | -26.3016 | -26.5189 | -31.2234 | -34.3848 | 10.1224 | 9.3837 | 8.647 | 7.5329 | 6.2523 | 4.7521 | 2.9953 | 0.9761 | -1.2938 | -3.9454 | -10.3389 | -12.4714 | -15.617 | -18.0553 | 6.6526 | 5.5632 | 4.4657 | 2.7543 | 0.80542 | -1.4409 | -4.0066 | -6.8873 | -10.1448 | -13.8342 | -22.4996 | -24.0052 | -28.4925 | -31.6023
|  | WHITELEY WOOD | ST |  |  | 5.67 | 4.7469 | 3.8441 | 2.7739 | 1.6831 | 0.50901 | -0.87945 | -2.4316 | -4.1602 | -6.1338 | -11.0408 | -14.6209 | -22.307 | -24.6523 | 10.3242 | 9.6653 | 9.02 | 8.1863 | 7.3456 | 6.455 | 5.3315 | 4.0721 | 2.6591 | 1.0226 | -3.1188 | -7.5609 | -14.3241 | -16.8754 | 7.235 | 6.4707 | 5.7154 | 4.7508 | 3.7757 | 2.7234 | 1.4314 | -0.02209 | -1.6641 | -3.5602 | -8.3458 | -13.2574 | -20.9105 | -22.7748
|  | WHITELEY WOOD | FS |  |  | 5.4913 | 4.4173 | 3.3003 | 1.6462 | -0.57495 | -5.0777 | -11.077 | -19.092 | -29.3652 | -41.7603 | -71.7327 | -94.0838 | -105.8623 | -114.1106 | 10.4077 | 9.8672 | 9.3103 | 8.6733 | 7.9867 | 7.2163 | 6.3661 | 5.396 | 4.2942 | 3.0795 | 0.086201 | -3.1522 | -13.3415 | -21.0052 | 7.3649 | 6.7699 | 6.1698 | 5.4082 | 4.6035 | 3.6978 | 2.7169 | 1.6123 | 0.29995 | -1.1244 | -4.5817 | -7.9123 | -19.3915 | -26.5014
MINETY GSP | CIRENCESTER BSP | WHITEWAY | MINIMUM HEADROOM | SP 02076 03059 | YES | 17.9423 | 17.7039 | 17.4073 | 16.9421 | 16.4689 | 15.9048 | 15.2044 | 14.5626 | 13.799 | 12.9472 | 11.0661 | 7.0202 | 4.8529 | 2.9991 | 19.9259 | 19.8124 | 19.671 | 19.4448 | 19.2061 | 18.8789 | 18.442 | 18.0683 | 17.6383 | 17.1241 | 15.9188 | 13.471 | 11.6215 | 9.7857 | 17.3668 | 17.15 | 16.8922 | 16.4835 | 16.0617 | 15.5497 | 14.9091 | 14.3175 | 13.6171 | 12.8326 | 11.0814 | 7.4074 | 5.5405 | 3.9677
|  | WHITEWAY | CT |  |  | 18.1973 | 18.0947 | 17.9272 | 17.5875 | 17.2365 | 16.7683 | 16.2076 | 15.6858 | 14.8933 | 14.0396 | 12.2679 | 7.81 | 4.8529 | 2.9991 | 20.0156 | 19.9466 | 19.8388 | 19.657 | 19.4597 | 19.1371 | 18.7542 | 18.4094 | 17.931 | 17.3919 | 16.2218 | 13.471 | 11.6215 | 9.8046 | 17.5952 | 17.503 | 17.3598 | 17.0657 | 16.7554 | 16.3292 | 15.8155 | 15.3326 | 14.6061 | 13.8185 | 12.1745 | 8.1457 | 5.5667 | 3.9677
|  | WHITEWAY | LW |  |  | 17.9423 | 17.7039 | 17.4073 | 16.9421 | 16.4689 | 15.9048 | 15.2044 | 14.5626 | 13.799 | 12.9472 | 11.0661 | 7.0202 | 4.8635 | 3.6221 | 19.9259 | 19.8124 | 19.671 | 19.4448 | 19.2061 | 18.8789 | 18.442 | 18.0683 | 17.6383 | 17.1241 | 15.9188 | 13.5514 | 12.5145 | 11.8852 | 17.3668 | 17.15 | 16.8922 | 16.4835 | 16.0617 | 15.5497 | 14.9091 | 14.3175 | 13.6171 | 12.8326 | 11.0814 | 7.4074 | 5.5405 | 4.4933
|  | WHITEWAY | ST |  |  | 18.3125 | 18.2778 | 18.1811 | 18.0146 | 17.8619 | 17.6142 | 17.3032 | 17.0673 | 16.8052 | 16.4849 | 15.669 | 11.9305 | 9.2523 | 7.4214 | 20.0563 | 20.0144 | 19.9362 | 19.8099 | 19.6851 | 19.4529 | 19.181 | 18.9686 | 18.7328 | 18.4427 | 17.6791 | 14.7119 | 12.5046 | 10.8249 | 17.6956 | 17.6637 | 17.5837 | 17.4376 | 17.3008 | 17.0704 | 16.7793 | 16.556 | 16.3072 | 16.001 | 15.1422 | 11.5917 | 9.1288 | 7.5849
|  | WHITEWAY | FS |  |  | 18.1973 | 18.0947 | 17.9272 | 17.5875 | 17.2365 | 16.7683 | 16.2076 | 15.6858 | 14.8933 | 14.0396 | 12.2679 | 7.81 | 4.8529 | 2.9991 | 20.0604 | 20.0047 | 19.9243 | 19.8127 | 19.6959 | 19.5424 | 19.3466 | 19.149 | 18.9248 | 18.6697 | 18.0568 | 15.7629 | 12.8899 | 9.7857 | 17.7027 | 17.6597 | 17.5869 | 17.4424 | 17.2983 | 17.1246 | 16.9066 | 16.6877 | 16.4374 | 16.1548 | 15.5057 | 12.9211 | 10.0985 | 7.9661
BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD | MINIMUM HEADROOM | SU 69235 73304 | YES | 11.8893 | 11.5763 | 11.241 | 10.7088 | 10.1352 | 9.416 | 8.6321 | 7.744 | 6.6305 | 5.3759 | 2.457 | -14.4376 | -35.7102 | -47.2446 | 15.1655 | 15.0229 | 14.8421 | 14.5598 | 14.23 | 13.7496 | 13.2349 | 12.5867 | 11.7115 | 10.6799 | 8.259 | -4.4829 | -20.7716 | -29.7656 | 11.8662 | 11.5894 | 11.2931 | 10.8029 | 10.2732 | 9.6211 | 8.9058 | 8.0974 | 7.0755 | 5.9047 | 3.1038 | -13.7314 | -34.1025 | -45.1919
|  | WILSON ROAD | CT |  |  | 12.1531 | 11.9834 | 11.7857 | 11.3643 | 10.9025 | 10.2339 | 9.5737 | 8.779 | 7.611 | 6.2788 | 3.2549 | -14.4376 | -35.7102 | -47.2446 | 15.1873 | 15.0307 | 14.8421 | 14.5598 | 14.23 | 13.7496 | 13.2349 | 12.5867 | 11.7115 | 10.6799 | 8.259 | -4.4829 | -20.7716 | -29.7656 | 12.1079 | 11.9605 | 11.7873 | 11.3961 | 10.9659 | 10.3596 | 9.7492 | 9.0151 | 7.9285 | 6.6865 | 3.3563 | -13.7314 | -34.1025 | -45.1919
|  | WILSON ROAD | LW |  |  | 11.8893 | 11.5763 | 11.241 | 10.7088 | 10.1352 | 9.416 | 8.6321 | 7.744 | 6.6305 | 5.3759 | 2.457 | -3.2284 | -5.4567 | -6.8425 | 15.1655 | 15.0229 | 14.863 | 14.6281 | 14.3557 | 13.9792 | 13.5334 | 12.9933 | 12.2912 | 11.4723 | 9.5111 | 5.8629 | 4.3699 | 3.2243 | 11.8662 | 11.5894 | 11.2931 | 10.8029 | 10.2732 | 9.6211 | 8.9058 | 8.0974 | 7.0755 | 5.9047 | 3.1038 | -2.2817 | -4.4291 | -5.8557
|  | WILSON ROAD | ST |  |  | 12.3651 | 12.3131 | 12.2523 | 12.2048 | 12.1482 | 11.9287 | 11.7822 | 11.5774 | 11.2847 | 10.9144 | 9.8595 | 5.2696 | 2.0523 | 0.016428 | 15.2686 | 15.163 | 15.0381 | 14.9062 | 14.7512 | 14.4809 | 14.2308 | 13.918 | 13.5047 | 13.0111 | 11.6907 | 6.4963 | 1.1335 | -5.4795 | 12.3168 | 12.2852 | 12.2458 | 12.2053 | 12.1467 | 11.9577 | 11.8122 | 11.6082 | 11.3102 | 10.9356 | 9.8585 | 5.2616 | 2.0867 | 0.31165
|  | WILSON ROAD | FS |  |  | 12.1531 | 11.9834 | 11.7857 | 11.3643 | 10.9025 | 10.2339 | 9.5737 | 8.779 | 7.611 | 6.2788 | 3.2549 | -14.4376 | -35.7102 | -47.2446 | 15.2175 | 15.0612 | 14.8845 | 14.6687 | 14.4149 | 14.0999 | 13.7039 | 13.2305 | 12.6529 | 11.9858 | 10.3177 | 4.2507 | -4.885 | -18.0031 | 12.2535 | 12.181 | 12.0952 | 11.9376 | 11.7574 | 11.5196 | 11.2136 | 10.841 | 10.3943 | 9.8806 | 8.6045 | 4.1511 | -0.89526 | -4.4303
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE | MINIMUM HEADROOM | SZ 02014 99989 | YES | -1.9256 | -2.809 | 11.7475 | 10.5223 | 9.2279 | 7.7129 | 5.8884 | 2.6528 | -3.1859 | -10.219 | -27.0914 | -56.5534 | -65.3304 | -71.3768 | 1.7207 | 1.2409 | 15.1119 | 14.46 | 13.7457 | 12.8794 | 11.6814 | 8.4772 | 4.1341 | -1.1609 | -13.9358 | -35.8567 | -41.9313 | -46.3363 | -1.8926 | -2.6261 | 10.9628 | 9.89 | 8.7283 | 7.3512 | 5.6721 | 1.7111 | -3.8481 | -10.5626 | -26.6805 | -54.7644 | -63.0456 | -68.7967
|  | WIMBORNE | CT |  |  | -1.5269 | -2.1653 | 12.6057 | 11.5793 | 10.4281 | 8.9501 | 7.0588 | 2.6528 | -3.1859 | -10.219 | -27.0914 | -56.5534 | -65.3304 | -71.3768 | 1.8359 | 1.41 | 15.3054 | 14.6819 | 13.9436 | 12.9666 | 11.6814 | 8.4772 | 4.1341 | -1.1609 | -13.9358 | -35.8567 | -41.9313 | -46.3363 | -1.5463 | -2.0787 | 11.6852 | 10.7822 | 9.7399 | 8.3866 | 6.0329 | 1.7111 | -3.8481 | -10.5626 | -26.6805 | -54.7644 | -63.0456 | -68.7967
|  | WIMBORNE | LW |  |  | -1.9256 | -2.809 | 11.7475 | 10.5223 | 9.2279 | 7.7129 | 5.8884 | 3.7562 | 1.3428 | -1.4495 | -8.2982 | -20.9924 | -27.427 | -32.6895 | 1.7207 | 1.2409 | 15.1119 | 14.46 | 13.7457 | 12.8794 | 11.7949 | 10.4657 | 8.8967 | 7.0218 | 2.3279 | -6.1189 | -12.4796 | -16.6117 | -1.8926 | -2.6261 | 10.9628 | 9.89 | 8.7283 | 7.3512 | 5.6721 | 3.6871 | 1.4112 | -1.2405 | -7.7572 | -19.7391 | -26.699 | -31.8021
|  | WIMBORNE | ST |  |  | -1.4026 | -1.9641 | 12.934 | 12.3564 | 11.7801 | 11.0678 | 10.118 | 8.9633 | 7.7009 | 6.2423 | 2.4932 | -9.6998 | -16.7533 | -19.5935 | 1.8978 | 1.519 | 15.5007 | 15.0781 | 14.6334 | 14.0697 | 13.3128 | 12.3947 | 11.353 | 10.1463 | 7.0578 | -2.9286 | -9.0023 | -12.0702 | -1.4404 | -1.9063 | 11.9727 | 11.4558 | 10.9275 | 10.2711 | 9.3822 | 8.2935 | 7.0686 | 5.6473 | 1.9962 | -9.9145 | -16.6887 | -19.1542
|  | WIMBORNE | FS |  |  | -1.5269 | -2.1653 | 12.6057 | 11.5793 | 10.4281 | 8.9501 | 7.0588 | 2.6528 | -3.1859 | -10.219 | -27.0914 | -56.5534 | -65.3304 | -71.3768 | 2.0032 | 1.7271 | 15.8228 | 15.5375 | 15.2596 | 14.9417 | 14.582 | 14.1856 | 13.7267 | 13.1785 | 11.6624 | 5.3518 | -3.2306 | -11.3191 | -1.286 | -1.5909 | 12.4766 | 12.1274 | 11.7944 | 11.4162 | 10.9925 | 10.526 | 9.9721 | 9.3361 | 7.6218 | 0.45523 | -8.5624 | -14.8292
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES | MINIMUM HEADROOM | SU 03028 12678 | YES | 0.36168 | 0.1926 | -0.040342 | -0.37174 | -0.83645 | -1.4853 | -2.3907 | -3.6348 | -5.2619 | -7.4126 | -13.7469 | -37.2977 | -48.8896 | -47.8042 | 0.47238 | 0.44354 | 0.32118 | 0.083073 | -0.25775 | -0.76489 | -1.4753 | -2.4503 | -3.7269 | -5.4215 | -10.4069 | -28.9484 | -38.0799 | -37.2678 | 0.27671 | 0.11536 | -0.10737 | -0.42511 | -0.8714 | -1.4951 | -2.3662 | -3.5617 | -5.126 | -7.1969 | -13.2903 | -35.9381 | -47.0962 | -46.0842
|  | WIMBORNE ST GILES | CT |  |  | 0.36168 | 0.1926 | -0.040342 | -0.37174 | -0.83645 | -1.4853 | -2.3907 | -3.6348 | -5.2619 | -7.4126 | -13.7469 | -37.2977 | -48.8896 | -47.8042 | 0.47507 | 0.44704 | 0.32118 | 0.083073 | -0.25775 | -0.76489 | -1.4753 | -2.4503 | -3.7269 | -5.4215 | -10.4069 | -28.9484 | -38.0799 | -37.2678 | 0.27671 | 0.11536 | -0.10737 | -0.42511 | -0.8714 | -1.4951 | -2.3662 | -3.5617 | -5.126 | -7.1969 | -13.2903 | -35.9381 | -47.0962 | -46.0842
|  | WIMBORNE ST GILES | LW |  |  | 0.45977 | 0.34932 | 0.19455 | -0.016311 | -0.32712 | -0.76957 | -1.4037 | -2.2715 | -3.3982 | -4.7867 | -8.0765 | -13.9257 | -15.612 | -16.8989 | 0.47238 | 0.44354 | 0.40612 | 0.36226 | 0.14061 | -0.1819 | -0.67399 | -1.3513 | -2.2331 | -3.3229 | -5.9025 | -10.49 | -11.8687 | -12.9771 | 0.37238 | 0.26802 | 0.12121 | -0.080264 | -0.37751 | -0.80148 | -1.4094 | -2.2422 | -3.3252 | -4.6604 | -7.8223 | -13.4472 | -15.1082 | -16.4075
|  | WIMBORNE ST GILES | ST |  |  | 0.56871 | 0.55892 | 0.53833 | 0.49021 | 0.44566 | 0.40113 | 0.34695 | 0.29225 | 0.22083 | 0.14752 | -0.023108 | -0.44263 | -0.82874 | -1.1088 | 0.49835 | 0.48645 | 0.47383 | 0.43433 | 0.39935 | 0.36436 | 0.31522 | 0.2719 | 0.21011 | 0.14771 | 0.0028989 | -0.37481 | -0.7594 | -1.0769 | 0.47745 | 0.46649 | 0.45481 | 0.4143 | 0.37971 | 0.33967 | 0.27845 | 0.22121 | 0.14498 | 0.067128 | -0.11381 | -0.56613 | -0.9936 | -1.3078
|  | WIMBORNE ST GILES | FS |  |  | 0.36168 | 0.1926 | -0.040342 | -0.37174 | -0.83645 | -1.4853 | -2.3907 | -3.6348 | -5.2619 | -7.4126 | -13.7469 | -37.2977 | -48.8896 | -47.8042 | 0.4895 | 0.47334 | 0.45298 | 0.41884 | 0.37788 | 0.32646 | 0.26371 | 0.18688 | 0.093564 | -0.017115 | -0.321 | -1.2772 | -1.8942 | -2.119 | 0.48104 | 0.4718 | 0.46187 | 0.4181 | 0.36309 | 0.29562 | 0.21525 | 0.11679 | -0.0044458 | -0.14513 | -0.52197 | -1.6985 | -2.4425 | -2.699
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON | MINIMUM HEADROOM | ST 71286 27802 | YES | 5.2122 | 4.9681 | 4.624 | 4.0929 | 3.3928 | 2.4854 | 1.2528 | -0.4319 | -2.6462 | -5.368 | -12.1067 | -38.0361 | -58.976 | -65.4031 | 6.6512 | 6.4643 | 6.27 | 6.0677 | 5.8182 | 5.4446 | 4.6967 | 3.362 | 1.6824 | -0.39818 | -5.5763 | -25.6916 | -41.8666 | -46.7951 | 6.2925 | 5.9633 | 5.6127 | 5.2068 | 4.7275 | 4.1592 | 3.0785 | 1.3979 | -0.71929 | -3.325 | -9.7818 | -34.6327 | -54.6852 | -60.8293
|  | WINCANTON | CT |  |  | 5.2634 | 5.1266 | 4.8554 | 4.3713 | 3.7471 | 2.8835 | 1.7676 | 0.28214 | -1.7122 | -4.3001 | -11.3998 | -38.0361 | -58.976 | -65.4031 | 6.6747 | 6.5822 | 6.46 | 6.3016 | 6.0855 | 5.7231 | 5.1113 | 3.918 | 2.3294 | 0.3501 | -5.107 | -25.6916 | -41.8666 | -46.7951 | 6.4631 | 6.2881 | 6.0674 | 5.7346 | 5.3253 | 4.7957 | 3.6833 | 2.1596 | 0.16326 | -2.3118 | -9.1106 | -34.6327 | -54.6852 | -60.8293
|  | WINCANTON | LW |  |  | 5.2122 | 4.9681 | 4.624 | 4.0929 | 3.3928 | 2.4854 | 1.2528 | -0.4319 | -2.6462 | -5.368 | -12.1067 | -27.4913 | -33.2284 | -34.3425 | 6.6512 | 6.4643 | 6.27 | 6.0677 | 5.8182 | 5.4446 | 4.6967 | 3.362 | 1.6824 | -0.39818 | -5.5763 | -17.4078 | -21.7567 | -22.5826 | 6.2925 | 5.9633 | 5.6127 | 5.2068 | 4.7275 | 4.1592 | 3.0785 | 1.3979 | -0.71929 | -3.325 | -9.7818 | -24.5154 | -29.9917 | -31.0491
|  | WINCANTON | ST |  |  | 5.3868 | 5.3345 | 5.2653 | 5.1725 | 5.0664 | 4.9276 | 4.7631 | 4.49 | 3.9262 | 3.2433 | 1.4273 | -5.1136 | -9.416 | -10.6977 | 6.7558 | 6.7236 | 6.6804 | 6.6152 | 6.5425 | 6.4388 | 6.3017 | 6.1502 | 5.9481 | 5.7127 | 4.3883 | -0.65412 | -4.1596 | -5.3628 | 6.5506 | 6.4357 | 6.2922 | 6.0899 | 5.8464 | 5.541 | 5.1706 | 4.7299 | 4.1851 | 3.5253 | 1.7451 | -4.5967 | -8.746 | -9.9743
|  | WINCANTON | FS |  |  | 5.2634 | 5.1266 | 4.8554 | 4.3713 | 3.7471 | 2.8835 | 1.7676 | 0.28214 | -1.7122 | -4.3001 | -11.3998 | -38.0361 | -58.976 | -65.4031 | 6.8229 | 6.7058 | 6.5944 | 6.4968 | 6.3841 | 6.248 | 6.0866 | 5.6273 | 4.8513 | 4.0144 | 2.2106 | -2.617 | -6.494 | -8.7708 | 6.5331 | 6.2645 | 5.9772 | 5.6438 | 5.2479 | 4.7538 | 4.1186 | 3.2703 | 2.2872 | 1.2312 | -1.0311 | -6.9175 | -11.26 | -13.1464
COWLEY GSP | WITNEY BSP | WINDRUSH PARK | MINIMUM HEADROOM | SP 33366 09758 | NO | 17.0328 | 16.7919 | 16.5736 | 16.2545 | 15.8987 | 15.4803 | 14.6128 | 13.3323 | 11.5708 | 9.4489 | 4.4951 | -3.5452 | -5.7454 | -7.3318 | 17.6435 | 17.4979 | 17.3679 | 17.194 | 16.9918 | 16.7442 | 16.2401 | 15.3328 | 13.9413 | 12.2664 | 8.5043 | 2.4756 | 0.91847 | -4.2601 | 15.8518 | 15.6328 | 15.4343 | 15.1441 | 14.8176 | 14.4298 | 13.8511 | 12.6297 | 10.9441 | 8.9117 | 4.1781 | -3.4821 | -5.5502 | -7.0477
|  | WINDRUSH PARK | CT |  |  | 17.2698 | 17.2005 | 17.1182 | 16.9289 | 16.7105 | 16.4265 | 16.0643 | 15.6349 | 14.8191 | 13.9475 | 12.27 | 8.4712 | 6.5427 | 5.3508 | 17.7361 | 17.6847 | 17.5978 | 17.4587 | 17.2915 | 17.0636 | 16.7626 | 16.4003 | 15.744 | 15.0298 | 13.8005 | 10.6514 | 8.0032 | 4.3699 | 16.0634 | 16.0008 | 15.9253 | 15.7534 | 15.5538 | 15.2906 | 14.9346 | 14.4678 | 13.654 | 12.7569 | 11.0927 | 7.5293 | 5.7934 | 4.7321
|  | WINDRUSH PARK | LW |  |  | 17.0328 | 16.7919 | 16.5736 | 16.2545 | 15.8987 | 15.4803 | 14.6128 | 13.3323 | 11.5708 | 9.4489 | 4.4951 | -3.5452 | -5.7454 | -7.3318 | 17.6435 | 17.4979 | 17.3679 | 17.194 | 16.9918 | 16.7442 | 16.2401 | 15.3328 | 13.9413 | 12.2664 | 8.5043 | 2.4756 | 0.91847 | -0.2536 | 15.8518 | 15.6328 | 15.4343 | 15.1441 | 14.8176 | 14.4298 | 13.8511 | 12.6297 | 10.9441 | 8.9117 | 4.1781 | -3.4821 | -5.5502 | -7.0477
|  | WINDRUSH PARK | ST |  |  | 17.3308 | 17.2992 | 17.2627 | 17.206 | 17.1302 | 17.0187 | 16.8524 | 16.6559 | 16.281 | 15.8655 | 15.2381 | 12.0235 | 9.9865 | 9.0299 | 17.7482 | 17.7264 | 17.6707 | 17.5926 | 17.496 | 17.3597 | 17.1706 | 16.9502 | 16.5276 | 16.0637 | 15.3667 | 12.277 | 9.3482 | 6.067 | 16.1181 | 16.09 | 16.0568 | 16.0044 | 15.9346 | 15.8301 | 15.6724 | 15.4614 | 15.0765 | 14.6372 | 13.8656 | 10.7548 | 8.8473 | 8.055
|  | WINDRUSH PARK | FS |  |  | 17.2698 | 17.2005 | 17.1182 | 16.9289 | 16.7105 | 16.4265 | 16.0643 | 15.6349 | 14.8191 | 13.9475 | 12.27 | 8.4712 | 6.5427 | 5.3508 | 17.7814 | 17.6931 | 17.5888 | 17.4639 | 17.3107 | 17.1417 | 16.9294 | 16.6907 | 16.3236 | 15.8907 | 14.9314 | 10.6972 | 4.0785 | -4.2601 | 16.1483 | 16.0666 | 15.9956 | 15.904 | 15.7896 | 15.6568 | 15.4666 | 15.2457 | 14.9154 | 14.5256 | 13.6091 | 9.8992 | 5.3539 | 2.4737
COWLEY GSP | DRAYTON BSP | WINSMORE LANE | MINIMUM HEADROOM | SU 49513 96982 | NO | 3.5705 | 3.2877 | 2.9935 | 2.4285 | 1.8084 | 1.1337 | 0.35429 | -0.51239 | -1.5963 | -2.8972 | -5.9268 | -12.2251 | -16.1246 | -18.9537 | 6.2407 | 6.1074 | 5.9628 | 5.7004 | 5.3931 | 5.0323 | 4.5684 | 3.9757 | 3.1316 | 2.1657 | -0.062644 | -5.5467 | -10.1777 | -21.2764 | 2.5958 | 2.3552 | 2.097 | 1.6116 | 1.0623 | 0.44008 | -0.30375 | -1.1635 | -2.2349 | -3.5314 | -6.6157 | -12.4655 | -15.7134 | -18.1082
|  | WINSMORE LANE | CT |  |  | 3.909 | 3.8032 | 3.6793 | 3.2787 | 2.8306 | 2.3097 | 1.7158 | 1.0091 | -0.17589 | -1.4619 | -4.315 | -11.6492 | -16.1246 | -18.9537 | 6.311 | 6.1892 | 6.0411 | 5.7734 | 5.4567 | 5.0632 | 4.5783 | 3.9757 | 3.1316 | 2.1657 | -0.062644 | -5.5467 | -10.0166 | -15.7304 | 2.8647 | 2.7655 | 2.6432 | 2.2913 | 1.883 | 1.391 | 0.80409 | 0.083366 | -1.0561 | -2.3276 | -5.1901 | -11.926 | -15.7134 | -18.1082
|  | WINSMORE LANE | LW |  |  | 3.5705 | 3.2877 | 2.9935 | 2.4285 | 1.8084 | 1.1337 | 0.35429 | -0.51239 | -1.5963 | -2.8972 | -5.9268 | -12.2251 | -15.3092 | -17.2391 | 6.2407 | 6.1074 | 5.9628 | 5.7004 | 5.3931 | 5.0323 | 4.5684 | 4.0082 | 3.3208 | 2.4712 | 0.3999 | -3.3234 | -4.8388 | -5.8598 | 2.5958 | 2.3552 | 2.097 | 1.6116 | 1.0623 | 0.44008 | -0.30375 | -1.1635 | -2.2349 | -3.5314 | -6.6157 | -12.4655 | -15.1398 | -16.7856
|  | WINSMORE LANE | ST |  |  | 4.0653 | 4.0577 | 4.0347 | 3.98 | 3.9073 | 3.8034 | 3.6623 | 3.4763 | 3.2369 | 2.9392 | 1.8544 | -3.3976 | -7.1911 | -9.8299 | 6.3671 | 6.2873 | 6.1863 | 6.0494 | 5.8879 | 5.6854 | 5.4332 | 5.1241 | 4.7494 | 4.2952 | 3.0353 | -2.0564 | -6.8053 | -12.1723 | 2.9817 | 2.9605 | 2.9228 | 2.8481 | 2.7525 | 2.6187 | 2.4376 | 2.1982 | 1.8941 | 1.5122 | 0.37156 | -4.616 | -8.0676 | -10.2721
|  | WINSMORE LANE | FS |  |  | 3.909 | 3.8032 | 3.6793 | 3.2787 | 2.8306 | 2.3097 | 1.7158 | 1.0091 | -0.17589 | -1.4619 | -4.315 | -11.6492 | -16.1246 | -18.9537 | 6.3468 | 6.2463 | 6.1275 | 5.9656 | 5.775 | 5.5536 | 5.2781 | 4.9531 | 4.5405 | 4.0619 | 2.8244 | -2.2553 | -10.1777 | -21.2764 | 2.9554 | 2.9213 | 2.8782 | 2.7673 | 2.6381 | 2.4844 | 2.2881 | 2.051 | 1.7355 | 1.3733 | 0.42687 | -3.5493 | -8.4931 | -12.237
MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON | MINIMUM HEADROOM | SY 84631 98138 | YES | 0.71121 | 0.3482 | -0.10062 | -0.67244 | -1.9995 | -4.74 | -8.6319 | -13.9431 | -20.7799 | -29.2748 | -50.1641 | -85.7794 | -96.8822 | -106.3617 | 2.3492 | 2.1548 | 1.8927 | 1.5208 | 0.45249 | -1.6574 | -4.6722 | -8.8032 | -14.1675 | -20.8386 | -37.2355 | -65.2253 | -74.7694 | -83.5941 | 0.49449 | 0.20342 | -0.16701 | -0.68747 | -2.5208 | -5.1472 | -8.8798 | -13.9763 | -20.5643 | -28.7473 | -48.8547 | -83.1806 | -94.4206 | -104.3993
|  | WINTERBOURNE KINGSTON | CT |  |  | 0.96407 | 0.75828 | 0.49155 | 0.053884 | -0.54027 | -1.3231 | -2.3895 | -3.7113 | -5.5939 | -8.7874 | -16.2586 | -31.6363 | -38.5641 | -42.8779 | 2.4364 | 2.3005 | 2.114 | 1.7998 | 1.3507 | 0.74482 | -0.11818 | -1.1597 | -2.553 | -5.1217 | -11.1212 | -23.6002 | -29.4451 | -33.4717 | 0.66437 | 0.47941 | 0.23235 | -0.17926 | -0.75049 | -1.5112 | -2.5699 | -3.8669 | -6.1163 | -9.2634 | -16.5858 | -31.7573 | -38.7791 | -43.3577
|  | WINTERBOURNE KINGSTON | LW |  |  | 0.71121 | 0.3482 | -0.10062 | -0.67244 | -1.9995 | -4.74 | -8.6319 | -13.9431 | -20.7799 | -29.2748 | -50.1641 | -85.7794 | -96.8822 | -106.3617 | 2.3492 | 2.1548 | 1.8927 | 1.5208 | 0.45249 | -1.6574 | -4.6722 | -8.8032 | -14.1675 | -20.8386 | -37.2355 | -65.2253 | -74.7694 | -83.5941 | 0.49449 | 0.20342 | -0.16701 | -0.68747 | -2.5208 | -5.1472 | -8.8798 | -13.9763 | -20.5643 | -28.7473 | -48.8547 | -83.1806 | -94.4206 | -104.3993
|  | WINTERBOURNE KINGSTON | ST |  |  | 0.97723 | 0.7773 | 0.53605 | -0.036592 | -0.58512 | -1.2395 | -2.0849 | -3.0265 | -4.3401 | -5.7575 | -9.2031 | -20.2575 | -27.4417 | -30.4337 | 2.4194 | 2.2769 | 2.101 | 1.5577 | 1.0717 | 0.5034 | -0.25473 | -1.0359 | -2.1791 | -3.3826 | -6.2958 | -15.8992 | -22.7709 | -26.3464 | 0.65322 | 0.46438 | 0.23449 | -0.38566 | -0.96072 | -1.6425 | -2.5375 | -3.5031 | -4.8732 | -6.3349 | -9.8794 | -21.2154 | -28.9411 | -32.4072
|  | WINTERBOURNE KINGSTON | FS |  |  | 0.96407 | 0.75828 | 0.49155 | 0.053884 | -0.54027 | -1.3231 | -2.3895 | -3.7113 | -5.5939 | -8.7874 | -16.2586 | -31.6363 | -38.5641 | -42.8779 | 2.5129 | 2.4446 | 2.3643 | 2.1869 | 1.9852 | 1.7401 | 1.4566 | 1.1413 | 0.69963 | 0.19841 | -1.0807 | -5.6181 | -11.1052 | -15.2769 | 0.78819 | 0.70175 | 0.60483 | 0.38595 | 0.13718 | -0.16048 | -0.50415 | -0.88776 | -1.431 | -2.0501 | -3.6261 | -9.4131 | -16.1673 | -20.7228
MANNINGTON GSP | REDHILL BSP | WINTON | MINIMUM HEADROOM | SZ 09349 93822 | YES | -2.6531 | -3.1417 | -3.6539 | -4.7261 | -6.0166 | -7.4286 | -9.0356 | -10.8721 | -13.4376 | -18.8951 | -33.2066 | -77.7107 | -108.7188 | -118.7681 | 2.2079 | 1.9366 | 1.6486 | 1.1078 | 0.40088 | -0.39602 | -2.0946 | -4.7559 | -8.0171 | -12.0835 | -22.8978 | -56.9658 | -80.8162 | -88.5717 | -1.9629 | -2.3486 | -2.759 | -3.6765 | -4.8849 | -6.2112 | -7.7289 | -10.6697 | -14.8846 | -20.0843 | -33.7517 | -76.333 | -106.0022 | -115.6123
|  | WINTON | CT |  |  | -2.1862 | -2.432 | -2.6452 | -3.3939 | -4.4178 | -5.4737 | -6.7369 | -8.2339 | -10.512 | -13.0663 | -23.9903 | -52.7144 | -70.0839 | -76.7681 | 2.3165 | 2.075 | 1.8597 | 1.4144 | 0.74035 | 0.041153 | -0.83813 | -1.9157 | -4.5246 | -7.7274 | -15.944 | -37.143 | -49.9059 | -54.7482 | -1.6312 | -1.8453 | -2.0394 | -2.6428 | -3.4929 | -4.3897 | -5.4947 | -6.8781 | -10.2127 | -14.3716 | -24.9046 | -52.2215 | -68.708 | -75.0179
|  | WINTON | LW |  |  | -2.6531 | -3.1417 | -3.6539 | -4.7261 | -6.0166 | -7.4286 | -9.0356 | -10.8721 | -13.4376 | -18.8951 | -33.2066 | -77.7107 | -108.7188 | -118.7681 | 2.2079 | 1.9366 | 1.6486 | 1.1078 | 0.40088 | -0.39602 | -2.0946 | -4.7559 | -8.0171 | -12.0835 | -22.8978 | -56.9658 | -80.8162 | -88.5717 | -1.9629 | -2.3486 | -2.759 | -3.6765 | -4.8849 | -6.2112 | -7.7289 | -10.6697 | -14.8846 | -20.0843 | -33.7517 | -76.333 | -106.0022 | -115.6123
|  | WINTON | ST |  |  | -2.1601 | -2.4058 | -2.6059 | -2.9403 | -3.5063 | -4.0267 | -4.7839 | -5.7104 | -6.7997 | -8.1128 | -11.4348 | -22.3727 | -30.1352 | -33.8928 | 2.2867 | 2.0188 | 1.7923 | 1.4406 | 0.9014 | 0.39596 | -0.32361 | -1.1828 | -2.1893 | -3.393 | -6.4463 | -16.1818 | -23.9631 | -29.9259 | -1.6493 | -1.8889 | -2.0899 | -2.4303 | -2.978 | -3.4945 | -4.2579 | -5.1895 | -6.2781 | -7.5943 | -10.9541 | -21.8567 | -29.3107 | -32.413
|  | WINTON | FS |  |  | -2.1862 | -2.432 | -2.6452 | -3.3939 | -4.4178 | -5.4737 | -6.7369 | -8.2339 | -10.512 | -13.0663 | -23.9903 | -52.7144 | -70.0839 | -76.7681 | 2.4117 | 2.2158 | 2.0131 | 1.761 | 1.4296 | 1.0652 | 0.62455 | 0.087281 | -0.58696 | -1.3389 | -3.1158 | -9.3415 | -18.0659 | -29.6486 | -1.5019 | -1.6417 | -1.7813 | -1.9985 | -2.2933 | -2.6205 | -3.0214 | -3.5259 | -4.1795 | -4.8906 | -6.5218 | -11.9741 | -18.0818 | -22.4863
COWLEY GSP | WITNEY BSP | WITNEY TOWN | MINIMUM HEADROOM | SP 35844 09625 | NO | 0.13729 | -0.29695 | -0.81298 | -1.7575 | -2.8881 | -4.1187 | -5.5313 | -7.0922 | -8.8929 | -11.7227 | -19.8262 | -35.2441 | -41.0117 | -44.853 | 7.0574 | 6.8551 | 6.6183 | 6.1967 | 5.6794 | 5.0997 | 4.124 | 2.6461 | 0.53027 | -2.1613 | -8.0888 | -19.0019 | -22.6959 | -25.3829 | -0.26813 | -0.64873 | -1.0864 | -1.9043 | -2.8785 | -3.9468 | -5.161 | -6.5147 | -8.1046 | -11.0166 | -18.7253 | -33.3271 | -38.7252 | -42.3751
|  | WITNEY TOWN | CT |  |  | 0.55458 | 0.35068 | 0.052632 | -0.67701 | -1.5794 | -2.6088 | -3.7615 | -5.1285 | -7.992 | -11.7227 | -19.8262 | -35.2441 | -41.0117 | -44.853 | 7.1839 | 7.0406 | 6.843 | 6.4559 | 5.9664 | 5.2269 | 4.124 | 2.6461 | 0.53027 | -2.1613 | -8.0888 | -19.0019 | -22.6959 | -25.3829 | 0.10275 | -0.07377 | -0.32268 | -0.95513 | -1.7372 | -2.6503 | -3.6983 | -4.9364 | -7.4789 | -11.0166 | -18.7253 | -33.3271 | -38.7252 | -42.3751
|  | WITNEY TOWN | LW |  |  | 0.13729 | -0.29695 | -0.81298 | -1.7575 | -2.8881 | -4.1187 | -5.5313 | -7.0922 | -8.8929 | -10.6106 | -15.5828 | -25.7115 | -29.4567 | -32.1869 | 7.0574 | 6.8551 | 6.6183 | 6.1967 | 5.6794 | 5.0997 | 4.4131 | 3.6287 | 2.0202 | 0.13884 | -4.2814 | -11.3028 | -13.8622 | -16.082 | -0.26813 | -0.64873 | -1.0864 | -1.9043 | -2.8785 | -3.9468 | -5.161 | -6.5147 | -8.1046 | -9.6543 | -14.5141 | -24.0447 | -27.6174 | -30.3465
|  | WITNEY TOWN | ST |  |  | 0.76251 | 0.68348 | 0.5254 | 0.21172 | -0.16497 | -0.55363 | -0.96688 | -1.4049 | -1.9073 | -2.3793 | -3.2584 | -7.0818 | -10.872 | -14.9531 | 7.2989 | 7.2349 | 7.1326 | 6.9137 | 6.6795 | 6.4087 | 6.069 | 5.7266 | 5.312 | 4.9003 | 4.0245 | 0.67738 | -2.9242 | -7.3127 | 0.31265 | 0.26453 | 0.1584 | -0.094969 | -0.38254 | -0.67816 | -1.0046 | -1.3361 | -1.7386 | -2.1223 | -2.8712 | -6.3057 | -9.8123 | -13.532
|  | WITNEY TOWN | FS |  |  | 0.55458 | 0.35068 | 0.052632 | -0.67701 | -1.5794 | -2.6088 | -3.7615 | -5.1285 | -7.992 | -11.7227 | -19.8262 | -35.2441 | -41.0117 | -44.853 | 7.2889 | 7.2203 | 7.1167 | 6.9504 | 6.7479 | 6.4727 | 6.1631 | 5.8277 | 5.4143 | 5.0101 | 4.1512 | 0.86444 | -3.8484 | -10.3233 | 0.29674 | 0.24979 | 0.15494 | -0.065848 | -0.33719 | -0.62615 | -0.93628 | -1.2655 | -1.7 | -2.0983 | -2.8699 | -6.0057 | -10.0131 | -13.8685
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM | MINIMUM HEADROOM | SU 79589 67665 | YES | 17.9534 | 17.5985 | 17.1723 | 16.4754 | 15.6665 | 14.752 | 13.6985 | 12.5035 | 10.016 | 6.6333 | -1.5627 | -15.4016 | -19.8279 | -22.9027 | 19.5765 | 19.3961 | 19.1764 | 18.8389 | 18.4392 | 17.9436 | 17.2977 | 16.5016 | 14.8078 | 12.3308 | 6.2606 | -3.7822 | -6.8293 | -9.1708 | 17.6125 | 17.3146 | 16.9648 | 16.3544 | 15.6498 | 14.8563 | 13.9419 | 12.4604 | 9.7928 | 6.5835 | -1.2059 | -14.3504 | -18.5625 | -21.5564
|  | WOKINGHAM | CT |  |  | 18.1712 | 17.9515 | 17.6429 | 17.0726 | 16.3805 | 15.5434 | 14.5443 | 12.842 | 10.016 | 6.6333 | -1.5627 | -15.4016 | -19.8279 | -22.9027 | 19.6224 | 19.4573 | 19.2339 | 18.8923 | 18.469 | 17.9436 | 17.2977 | 16.5016 | 14.8078 | 12.3308 | 6.2606 | -3.7822 | -6.8293 | -9.1708 | 17.8258 | 17.6505 | 17.4025 | 16.8975 | 16.2812 | 15.5275 | 14.4835 | 12.4604 | 9.7928 | 6.5835 | -1.2059 | -14.3504 | -18.5625 | -21.5564
|  | WOKINGHAM | LW |  |  | 17.9534 | 17.5985 | 17.1723 | 16.4754 | 15.6665 | 14.752 | 13.6985 | 12.5035 | 11.0671 | 9.5117 | 6.0487 | 0.094086 | -5.3267 | -10.0384 | 19.5765 | 19.3961 | 19.1764 | 18.8389 | 18.4392 | 17.9775 | 17.4306 | 16.7956 | 16.0049 | 15.1274 | 13.0596 | 9.396 | 4.2584 | 0.32457 | 17.6125 | 17.3146 | 16.9648 | 16.3544 | 15.6498 | 14.8563 | 13.9419 | 12.9052 | 11.6178 | 10.2234 | 7.1221 | 1.6018 | -4.704 | -9.4023
|  | WOKINGHAM | ST |  |  | 18.2425 | 18.075 | 17.8419 | 17.568 | 17.2621 | 16.9101 | 16.5217 | 16.0835 | 15.5586 | 14.9663 | 13.5047 | 9.0636 | 5.6109 | 3.0481 | 19.6688 | 19.5432 | 19.3769 | 19.1788 | 18.9605 | 18.7104 | 18.4249 | 18.1063 | 17.7084 | 17.2587 | 16.1239 | 12.5028 | 9.413 | 6.7025 | 17.9014 | 17.7813 | 17.6116 | 17.3987 | 17.1558 | 16.8742 | 16.56 | 16.2074 | 15.7659 | 15.2688 | 13.9726 | 9.7237 | 6.426 | 4.0487
|  | WOKINGHAM | FS |  |  | 18.1712 | 17.9515 | 17.6429 | 17.0726 | 16.3805 | 15.5434 | 14.5443 | 12.842 | 10.016 | 6.6333 | -1.5627 | -15.4016 | -19.8279 | -22.9027 | 19.6554 | 19.5301 | 19.3681 | 19.195 | 18.9928 | 18.7616 | 18.4969 | 18.1986 | 17.8418 | 17.4429 | 16.4635 | 13.2673 | 9.6786 | 6.3267 | 17.895 | 17.7919 | 17.6557 | 17.4676 | 17.2456 | 16.9921 | 16.709 | 16.397 | 15.9706 | 15.506 | 14.3842 | 10.7134 | 6.6944 | 3.6542
BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE | MINIMUM HEADROOM | SU 64425 81624 | YES | 1.2606 | 1.1921 | 1.1167 | 0.99062 | 0.84506 | 0.61139 | 0.19888 | -0.33999 | -1.0292 | -1.9033 | -4.355 | -12.7593 | -23.6068 | -29.6024 | 1.922 | 1.8887 | 1.8445 | 1.7941 | 1.7316 | 1.5938 | 1.3181 | 0.91692 | 0.40354 | -0.25492 | -2.1267 | -8.6219 | -17.016 | -21.6794 | 1.3239 | 1.263 | 1.1955 | 1.0832 | 0.95281 | 0.80863 | 0.47261 | -0.040602 | -0.69709 | -1.5311 | -3.8757 | -11.9272 | -22.315 | -28.0605
|  | WOODCOTE | CT |  |  | 1.3243 | 1.2897 | 1.2503 | 1.1532 | 0.97606 | 0.69626 | 0.34636 | -0.11128 | -0.71455 | -1.4437 | -3.4852 | -12.4035 | -23.6068 | -29.6024 | 1.9386 | 1.9157 | 1.8876 | 1.8375 | 1.7664 | 1.5938 | 1.3692 | 1.0238 | 0.58337 | 0.04323 | -1.4956 | -8.3311 | -17.016 | -21.6794 | 1.3805 | 1.3496 | 1.3141 | 1.2276 | 1.1281 | 0.93467 | 0.60145 | 0.16472 | -0.40802 | -1.1019 | -3.0499 | -11.5814 | -22.315 | -28.0605
|  | WOODCOTE | LW |  |  | 1.2606 | 1.1921 | 1.1167 | 0.99062 | 0.84506 | 0.61139 | 0.19888 | -0.33999 | -1.0292 | -1.9033 | -4.355 | -12.7593 | -16.8584 | -16.5267 | 1.922 | 1.8916 | 1.8564 | 1.8005 | 1.7316 | 1.6148 | 1.3181 | 0.91692 | 0.40354 | -0.25492 | -2.1267 | -8.6219 | -11.7696 | -11.4868 | 1.3239 | 1.263 | 1.1955 | 1.0832 | 0.95281 | 0.80863 | 0.47261 | -0.040602 | -0.69709 | -1.5311 | -3.8757 | -11.9272 | -15.8473 | -15.5216
|  | WOODCOTE | ST |  |  | 1.36 | 1.3463 | 1.3309 | 1.3123 | 1.2853 | 1.257 | 1.2277 | 1.1864 | 1.1445 | 1.0876 | 0.94518 | 0.32161 | -0.24577 | -0.74182 | 1.9562 | 1.9448 | 1.9312 | 1.9158 | 1.8952 | 1.8712 | 1.8431 | 1.8062 | 1.7653 | 1.7126 | 1.5706 | 1.0145 | 0.57406 | 0.21375 | 1.4119 | 1.3998 | 1.386 | 1.3693 | 1.3451 | 1.3193 | 1.2921 | 1.2538 | 1.2142 | 1.1604 | 1.0236 | 0.43275 | -0.078273 | -0.50283
|  | WOODCOTE | FS |  |  | 1.3243 | 1.2897 | 1.2503 | 1.1532 | 0.97606 | 0.69626 | 0.34636 | -0.11128 | -0.71455 | -1.4437 | -3.4852 | -12.4035 | -23.6068 | -29.6024 | 1.9272 | 1.8887 | 1.8445 | 1.7941 | 1.7337 | 1.6565 | 1.5492 | 1.4041 | 1.2332 | 1.0513 | 0.66529 | -0.30627 | -1.0251 | -1.5624 | 1.3886 | 1.3573 | 1.3194 | 1.267 | 1.2082 | 1.1344 | 1.0319 | 0.89772 | 0.729 | 0.54889 | 0.12488 | -1.0699 | -1.8813 | -2.3254
NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE | MINIMUM HEADROOM | SU 43733 15470 | YES | 13.3963 | 13.2171 | 13.0526 | 12.7128 | 12.3589 | 11.9851 | 11.5683 | 11.1087 | 10.5501 | 9.0496 | 5.2032 | -9.3456 | -16.786 | -16.8525 | 14.7974 | 14.6947 | 14.6087 | 14.4494 | 14.2799 | 14.0925 | 13.8722 | 13.4489 | 12.4911 | 11.26 | 8.3864 | -2.7187 | -8.3501 | -8.3707 | 12.6979 | 12.5297 | 12.3749 | 12.0493 | 11.7082 | 11.3446 | 10.9354 | 10.4819 | 9.9238 | 9.1075 | 5.4341 | -8.4745 | -15.6075 | -15.7009
|  | WOODMILL LANE | CT |  |  | 13.5651 | 13.4619 | 13.4052 | 13.1675 | 12.9182 | 12.6469 | 12.3482 | 12.0115 | 11.4739 | 9.9291 | 5.5626 | -9.3456 | -16.786 | -16.8525 | 14.8381 | 14.7317 | 14.6713 | 14.5395 | 14.3938 | 14.2262 | 14.0326 | 13.783 | 12.9035 | 11.7962 | 8.5333 | -2.7187 | -8.3501 | -8.3707 | 12.8548 | 12.7576 | 12.7033 | 12.4754 | 12.2349 | 11.9701 | 11.6758 | 11.3409 | 10.8077 | 9.9337 | 5.7669 | -8.4745 | -15.6075 | -15.7009
|  | WOODMILL LANE | LW |  |  | 13.3963 | 13.2171 | 13.0526 | 12.7128 | 12.3589 | 11.9851 | 11.5683 | 11.1087 | 10.5501 | 9.0496 | 5.2032 | -1.5182 | -3.6798 | -5.3046 | 14.7974 | 14.6947 | 14.6087 | 14.4494 | 14.2799 | 14.0925 | 13.8722 | 13.4489 | 12.4911 | 11.26 | 8.3864 | 3.4194 | 1.7267 | 0.26847 | 12.6979 | 12.5297 | 12.3749 | 12.0493 | 11.7082 | 11.3446 | 10.9354 | 10.4819 | 9.9238 | 9.1075 | 5.4341 | -0.9769 | -3.1111 | -4.7958
|  | WOODMILL LANE | ST |  |  | 13.6758 | 13.6358 | 13.6407 | 13.6475 | 13.6483 | 13.649 | 13.6434 | 13.6337 | 13.5935 | 13.5457 | 13.4176 | 12.4854 | 11.2457 | 9.7169 | 14.8887 | 14.813 | 14.7849 | 14.7493 | 14.709 | 14.6638 | 14.6082 | 14.5481 | 14.4448 | 14.3325 | 14.0593 | 12.9033 | 11.0504 | 8.2955 | 12.9646 | 12.9307 | 12.9387 | 12.945 | 12.9465 | 12.9475 | 12.9416 | 12.9332 | 12.8887 | 12.8378 | 12.704 | 11.8066 | 10.564 | 9.0307
|  | WOODMILL LANE | FS |  |  | 13.5651 | 13.4619 | 13.4052 | 13.1675 | 12.9182 | 12.6469 | 12.3482 | 12.0115 | 11.4739 | 9.9291 | 5.5626 | -9.3456 | -16.786 | -16.8525 | 14.8822 | 14.8245 | 14.7734 | 14.7132 | 14.6472 | 14.575 | 14.4898 | 14.3927 | 14.2456 | 14.0799 | 13.6728 | 12.0931 | 9.4504 | 5.1387 | 12.949 | 12.929 | 12.918 | 12.877 | 12.8306 | 12.7848 | 12.7299 | 12.6675 | 12.5686 | 12.4591 | 12.2033 | 11.1581 | 9.6238 | 7.957
COWLEY GSP | YARNTON BSP | WOODSTOCK | MINIMUM HEADROOM | SP 44795 17462 | NO | 5.7807 | 5.4644 | 5.137 | 4.756 | 4.3215 | 3.9042 | 3.4244 | 2.3677 | 0.81229 | -1.0881 | -5.9482 | -16.4974 | -23.9187 | -28.4554 | 7.3417 | 7.2384 | 7.1242 | 7.0015 | 6.8374 | 6.6384 | 6.2135 | 5.3466 | 4.1714 | 2.7252 | -0.99085 | -9.0723 | -14.9097 | -18.6461 | 5.3229 | 5.0671 | 4.7988 | 4.4724 | 4.0919 | 3.7093 | 3.2604 | 2.7267 | 1.493 | -0.32962 | -4.9886 | -15.106 | -22.298 | -26.7799
|  | WOODSTOCK | CT |  |  | 5.9486 | 5.748 | 5.528 | 5.2665 | 4.9591 | 4.657 | 4.3032 | 3.8699 | 3.2144 | 2.4813 | 0.47422 | -3.7277 | -5.3865 | -6.5569 | 7.3672 | 7.2924 | 7.2079 | 7.1315 | 7.0336 | 6.9138 | 6.7584 | 6.5494 | 6.2804 | 5.6217 | 3.9727 | 1.0031 | -0.10632 | -1.0017 | 5.4671 | 5.3082 | 5.1307 | 4.9042 | 4.6351 | 4.3597 | 4.0318 | 3.6267 | 3.0145 | 2.3202 | 0.8044 | -2.8201 | -4.4099 | -5.5714
|  | WOODSTOCK | LW |  |  | 5.7807 | 5.4644 | 5.137 | 4.756 | 4.3215 | 3.9042 | 3.4244 | 2.3677 | 0.81229 | -1.0881 | -5.9482 | -16.4974 | -23.9187 | -28.4554 | 7.3417 | 7.2384 | 7.1242 | 7.0015 | 6.8374 | 6.6384 | 6.2135 | 5.3466 | 4.1714 | 2.7252 | -0.99085 | -9.0723 | -14.9097 | -18.6461 | 5.3229 | 5.0671 | 4.7988 | 4.4724 | 4.0919 | 3.7093 | 3.2604 | 2.7267 | 1.493 | -0.32962 | -4.9886 | -15.106 | -22.298 | -26.7799
|  | WOODSTOCK | ST |  |  | 6.0112 | 5.8545 | 5.6865 | 5.5653 | 5.4306 | 5.3198 | 5.196 | 5.0484 | 4.8584 | 4.6374 | 4.0511 | 1.7025 | -0.1611 | -1.4674 | 7.3921 | 7.3388 | 7.282 | 7.2354 | 7.1839 | 7.1386 | 7.0843 | 7.0231 | 6.9268 | 6.8217 | 6.5537 | 4.7117 | 2.9676 | 1.4935 | 5.524 | 5.4055 | 5.2766 | 5.1757 | 5.0633 | 4.967 | 4.8579 | 4.7288 | 4.5538 | 4.3516 | 3.8168 | 1.688 | -0.09887 | -1.4384
|  | WOODSTOCK | FS |  |  | 5.9486 | 5.748 | 5.528 | 5.2665 | 4.9591 | 4.657 | 4.3032 | 3.8699 | 3.2144 | 2.4813 | 0.47422 | -3.7277 | -5.3865 | -6.5569 | 7.3987 | 7.3457 | 7.2892 | 7.2463 | 7.1998 | 7.16 | 7.1187 | 7.0713 | 7.0083 | 6.9377 | 6.7551 | 5.0045 | 2.849 | 0.75892 | 5.5464 | 5.4407 | 5.331 | 5.2191 | 5.1009 | 4.9992 | 4.8905 | 4.7706 | 4.5949 | 4.4009 | 3.9143 | 2.004 | -0.13761 | -1.7964
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON | MINIMUM HEADROOM | SU 44145 11242 | YES | 6.8289 | 6.377 | 6.0689 | 5.2289 | 4.4952 | 3.6368 | 2.6705 | 1.4792 | 0.014815 | -1.6896 | -5.8704 | -13.9824 | -17.0013 | -18.6388 | 8.8129 | 8.5827 | 8.421 | 7.9073 | 7.5026 | 6.9798 | 6.3544 | 5.5714 | 4.5842 | 3.3651 | 0.42543 | -5.8833 | -9.9644 | -18.9019 | 7.7105 | 7.3359 | 7.058 | 6.2884 | 5.6156 | 4.8191 | 3.9135 | 2.8327 | 1.5001 | -0.044269 | -3.8128 | -11.5674 | -14.4809 | -16.1566
|  | WOOLSTON | CT |  |  | 7.1213 | 6.838 | 6.6701 | 5.8331 | 5.2776 | 4.5874 | 3.7439 | 2.7093 | 1.2358 | -0.46883 | -4.3336 | -12.3293 | -15.7387 | -17.9222 | 8.8981 | 8.7039 | 8.5503 | 7.9134 | 7.5497 | 7.0727 | 6.4647 | 5.6923 | 4.6312 | 3.3651 | 0.42543 | -5.8833 | -9.9644 | -15.0368 | 7.968 | 7.7417 | 7.5965 | 6.8104 | 6.3085 | 5.689 | 4.9372 | 4.0169 | 2.6938 | 1.1647 | -2.3948 | -10.0067 | -13.2015 | -15.2885
|  | WOOLSTON | LW |  |  | 6.8289 | 6.377 | 6.0689 | 5.2289 | 4.4952 | 3.6368 | 2.6705 | 1.4792 | 0.014815 | -1.6896 | -5.8704 | -13.9824 | -17.0013 | -18.6388 | 8.8129 | 8.5827 | 8.421 | 7.9073 | 7.5026 | 6.9798 | 6.3544 | 5.5714 | 4.5842 | 3.4034 | 0.44068 | -5.1645 | -7.3001 | -8.6944 | 7.7105 | 7.3359 | 7.058 | 6.2884 | 5.6156 | 4.8191 | 3.9135 | 2.8327 | 1.5001 | -0.044269 | -3.8128 | -11.5674 | -14.4809 | -16.1566
|  | WOOLSTON | ST |  |  | 7.2692 | 7.0864 | 7.0374 | 6.6095 | 6.5114 | 6.3608 | 6.141 | 5.8496 | 5.4308 | 4.8761 | 3.161 | -3.931 | -8.3556 | -9.7888 | 8.9676 | 8.8257 | 8.7391 | 8.2924 | 8.1555 | 7.9673 | 7.7183 | 7.4001 | 6.9485 | 6.3827 | 4.7391 | -1.7439 | -6.8818 | -11.2405 | 8.1094 | 7.9775 | 7.9422 | 7.5376 | 7.4588 | 7.3357 | 7.152 | 6.9049 | 6.5412 | 6.0727 | 4.6521 | -2.026 | -6.39 | -7.8583
|  | WOOLSTON | FS |  |  | 7.1213 | 6.838 | 6.6701 | 5.8331 | 5.2776 | 4.5874 | 3.7439 | 2.7093 | 1.2358 | -0.46883 | -4.3336 | -12.3293 | -15.7387 | -17.9222 | 8.983 | 8.8416 | 8.7521 | 8.4945 | 8.3174 | 8.1111 | 7.8887 | 7.633 | 7.2416 | 6.7902 | 5.5714 | 0.24428 | -8.2056 | -18.9019 | 8.1331 | 8.0153 | 7.9813 | 7.7522 | 7.6135 | 7.4537 | 7.2897 | 7.1016 | 6.8147 | 6.4894 | 5.5892 | 1.305 | -4.9423 | -9.3529
MINETY GSP | SWINDON BSP | WOOTTON BASSETT | MINIMUM HEADROOM | SU 07587 81123 | YES | 9.4493 | 9.1675 | 8.8642 | 8.3851 | 7.8258 | 7.175 | 6.1241 | 4.0718 | 1.472 | -1.6563 | -9.1307 | -21.7544 | -25.9148 | -29.1084 | 12.3758 | 12.2401 | 12.0888 | 11.8518 | 11.5578 | 11.1966 | 10.7385 | 9.3004 | 7.377 | 5.0372 | -0.59247 | -9.9895 | -13.1637 | -15.9252 | 8.6502 | 8.4124 | 8.1541 | 7.7467 | 7.2684 | 6.706 | 5.5015 | 3.5514 | 1.0748 | -1.9098 | -9.0459 | -21.0782 | -25.1451 | -28.4033
|  | WOOTTON BASSETT | CT |  |  | 9.7691 | 9.6694 | 9.5587 | 9.259 | 8.9101 | 8.5155 | 8.054 | 7.5568 | 6.6887 | 5.7357 | 3.7113 | -1.5069 | -5.0125 | -6.9664 | 12.4858 | 12.4077 | 12.3179 | 12.1431 | 11.9304 | 11.6798 | 11.3726 | 11.0409 | 10.532 | 9.9305 | 8.6352 | 5.1241 | 2.1574 | -0.92141 | 8.9143 | 8.8285 | 8.7316 | 8.4736 | 8.1696 | 7.8212 | 7.4038 | 6.9528 | 6.183 | 5.3122 | 3.4554 | -1.2464 | -4.3366 | -6.1198
|  | WOOTTON BASSETT | LW |  |  | 9.4493 | 9.1675 | 8.8642 | 8.3851 | 7.8258 | 7.175 | 6.1241 | 4.0718 | 1.472 | -1.6563 | -9.1307 | -21.7544 | -25.9148 | -29.1084 | 12.3758 | 12.2401 | 12.0888 | 11.8518 | 11.5578 | 11.1966 | 10.7385 | 9.3004 | 7.377 | 5.0372 | -0.59247 | -9.9895 | -13.1637 | -15.9252 | 8.6502 | 8.4124 | 8.1541 | 7.7467 | 7.2684 | 6.706 | 5.5015 | 3.5514 | 1.0748 | -1.9098 | -9.0459 | -21.0782 | -25.1451 | -28.4033
|  | WOOTTON BASSETT | ST |  |  | 9.8574 | 9.7952 | 9.7258 | 9.5582 | 9.3757 | 9.1764 | 8.9046 | 8.6215 | 8.2505 | 7.8589 | 6.9503 | 3.7296 | 0.87005 | -1.8214 | 12.5205 | 12.4569 | 12.3837 | 12.2071 | 12.0332 | 11.8436 | 11.589 | 11.3413 | 11.0032 | 10.6503 | 9.8237 | 7.0618 | 4.0961 | 0.57254 | 8.9786 | 8.9169 | 8.8477 | 8.6647 | 8.4772 | 8.2724 | 7.9888 | 7.6974 | 7.3051 | 6.8929 | 5.9353 | 2.75 | -0.022059 | -2.4596
|  | WOOTTON BASSETT | FS |  |  | 9.7691 | 9.6694 | 9.5587 | 9.259 | 8.9101 | 8.5155 | 8.054 | 7.5568 | 6.6887 | 5.7357 | 3.7113 | -1.5069 | -5.0125 | -6.9664 | 12.5398 | 12.4895 | 12.433 | 12.3338 | 12.2242 | 12.0956 | 11.9519 | 11.7976 | 11.5743 | 11.33 | 10.7531 | 8.6647 | 5.5185 | 0.58028 | 9.0194 | 8.9932 | 8.9678 | 8.8694 | 8.7667 | 8.6457 | 8.5158 | 8.3798 | 8.159 | 7.9235 | 7.3875 | 5.4479 | 3.2009 | 0.96469
COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD | MINIMUM HEADROOM | SU 49244 98269 | YES | -2.4616 | -3.0521 | -3.673 | -4.8206 | -6.0776 | -7.4537 | -8.9657 | -10.4326 | -11.5497 | -12.8702 | -15.8976 | -22.6483 | -27.5097 | -30.496 | 1.8364 | 1.5468 | 1.2415 | 0.70625 | 0.11573 | -0.53997 | -1.276 | -2.0056 | -2.5815 | -3.3357 | -5.2638 | -10.0204 | -13.6875 | -17.7465 | -1.1495 | -1.62 | -2.1162 | -3.0639 | -4.1107 | -5.2669 | -6.5498 | -7.8149 | -8.8282 | -10.0188 | -12.7509 | -18.799 | -23.1242 | -25.9045
|  | WOOTTON ROAD | CT |  |  | -2.0827 | -2.4253 | -2.8259 | -3.7033 | -4.6849 | -5.8002 | -7.0342 | -8.2977 | -9.6992 | -11.2157 | -14.3521 | -22.1053 | -27.0115 | -30.0595 | 1.9363 | 1.7027 | 1.4304 | 0.95781 | 0.42196 | -0.19774 | -0.90082 | -1.6427 | -2.4386 | -3.3357 | -5.2638 | -10.0204 | -13.6875 | -17.7465 | -0.82041 | -1.082 | -1.3929 | -2.1124 | -2.9268 | -3.862 | -4.9124 | -6.0039 | -7.262 | -8.6341 | -11.4853 | -18.4168 | -22.6805 | -25.3071
|  | WOOTTON ROAD | LW |  |  | -2.4616 | -3.0521 | -3.673 | -4.8206 | -6.0776 | -7.4537 | -8.9657 | -10.4326 | -11.5497 | -12.8702 | -15.8976 | -22.6483 | -27.5097 | -30.496 | 1.8364 | 1.5468 | 1.2415 | 0.70625 | 0.11573 | -0.53997 | -1.276 | -2.0056 | -2.5815 | -3.2778 | -4.9254 | -8.5387 | -13.1948 | -16.4434 | -1.1495 | -1.62 | -2.1162 | -3.0639 | -4.1107 | -5.2669 | -6.5498 | -7.8149 | -8.8282 | -10.0188 | -12.7509 | -18.799 | -23.1242 | -25.9045
|  | WOOTTON ROAD | ST |  |  | -1.9923 | -2.2827 | -2.6163 | -3.1 | -3.5953 | -4.1324 | -4.699 | -5.2255 | -5.5517 | -5.945 | -6.9198 | -11.2577 | -15.4226 | -19.1248 | 1.9798 | 1.7755 | 1.5412 | 1.2019 | 0.85597 | 0.47846 | 0.062748 | -0.33253 | -0.64075 | -0.99986 | -1.9253 | -5.6549 | -9.4918 | -13.7207 | -0.73998 | -0.95419 | -1.2041 | -1.5876 | -1.9768 | -2.4011 | -2.8602 | -3.2895 | -3.5866 | -3.9451 | -4.8549 | -8.8672 | -12.6281 | -15.8479
|  | WOOTTON ROAD | FS |  |  | -2.0827 | -2.4253 | -2.8259 | -3.7033 | -4.6849 | -5.8002 | -7.0342 | -8.2977 | -9.6992 | -11.2157 | -14.3521 | -22.1053 | -27.0115 | -30.0595 | 2.0001 | 1.7988 | 1.5725 | 1.2803 | 0.96968 | 0.63008 | 0.26251 | -0.087245 | -0.38096 | -0.69988 | -1.4673 | -4.4791 | -9.0548 | -15.5774 | -0.705 | -0.89165 | -1.1017 | -1.4252 | -1.7619 | -2.1274 | -2.5136 | -2.8612 | -3.1506 | -3.4517 | -4.1536 | -6.9406 | -10.6156 | -14.0641
BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM | MINIMUM HEADROOM | SU 82093 44312 | YES | 14.2053 | 13.9183 | 13.5779 | 12.9456 | 12.2151 | 11.3222 | 9.1522 | 6.067 | 2.1384 | -2.702 | -14.7146 | -38.4726 | -46.7463 | -50.107 | 16.5787 | 16.4191 | 16.2197 | 15.8678 | 15.4432 | 14.89 | 13.5704 | 11.2336 | 8.2585 | 4.5683 | -4.6469 | -22.8444 | -29.23 | -32.1077 | 13.8109 | 13.5705 | 13.282 | 12.7573 | 12.1377 | 11.3609 | 10.3447 | 8.2061 | 4.4485 | -0.1853 | -11.6941 | -34.452 | -42.4622 | -45.8637
|  | WRECCLESHAM | CT |  |  | 14.4925 | 14.3719 | 14.1904 | 13.7053 | 13.174 | 12.4961 | 11.6406 | 10.0904 | 7.3596 | 4.0855 | -3.3978 | -17.6965 | -22.6963 | -25.7371 | 16.6589 | 16.5419 | 16.3672 | 16.0361 | 15.6612 | 15.1608 | 14.4934 | 13.6509 | 12.0427 | 9.5819 | 3.9331 | -6.6426 | -10.1594 | -12.4919 | 14.0208 | 13.9064 | 13.732 | 13.3102 | 12.8297 | 12.2 | 11.3785 | 10.344 | 8.7966 | 6.2509 | -0.92149 | -14.6007 | -19.3801 | -22.3489
|  | WRECCLESHAM | LW |  |  | 14.2053 | 13.9183 | 13.5779 | 12.9456 | 12.2151 | 11.3222 | 9.1522 | 6.067 | 2.1384 | -2.702 | -14.7146 | -38.4726 | -46.7463 | -50.107 | 16.5787 | 16.4191 | 16.2197 | 15.8678 | 15.4432 | 14.89 | 13.5704 | 11.2336 | 8.2585 | 4.5683 | -4.6469 | -22.8444 | -29.23 | -32.1077 | 13.8109 | 13.5705 | 13.282 | 12.7573 | 12.1377 | 11.3609 | 10.3447 | 8.2061 | 4.4485 | -0.1853 | -11.6941 | -34.452 | -42.4622 | -45.8637
|  | WRECCLESHAM | ST |  |  | 14.4757 | 14.3227 | 14.1305 | 13.7847 | 13.4214 | 12.9579 | 12.2995 | 11.451 | 10.4125 | 9.2519 | 6.507 | -1.8553 | -6.6525 | -8.4529 | 16.6147 | 16.448 | 16.2398 | 15.8943 | 15.5544 | 15.1276 | 14.526 | 13.7744 | 12.8611 | 11.8488 | 9.4575 | 2.4638 | -1.6956 | -3.6623 | 13.9689 | 13.7952 | 13.5809 | 13.2136 | 12.8447 | 12.3757 | 11.7059 | 10.8544 | 9.8064 | 8.6404 | 5.8884 | -2.3061 | -7.0529 | -8.8528
|  | WRECCLESHAM | FS |  |  | 14.4925 | 14.3719 | 14.1904 | 13.7053 | 13.174 | 12.4961 | 11.6406 | 10.0904 | 7.3596 | 4.0855 | -3.3978 | -17.6965 | -22.6963 | -25.7371 | 16.7327 | 16.6638 | 16.5816 | 16.4648 | 16.3412 | 16.1969 | 16.0282 | 15.8334 | 15.578 | 15.2781 | 14.4986 | 11.2925 | 7.1513 | 3.4911 | 14.1269 | 14.0852 | 14.0369 | 13.9283 | 13.8126 | 13.6764 | 13.5186 | 13.3316 | 13.0388 | 12.6948 | 11.8092 | 8.0905 | 3.3464 | -0.081072
MINETY GSP | TOOTHILL BSP | WROUGHTON | MINIMUM HEADROOM | SU 14446 81504 | YES | 15.965 | 15.6238 | 11.1845 | 10.6326 | 7.9626 | 6.8634 | 5.6158 | 4.4533 | 1.4245 | -2.2732 | -11.463 | -32.1641 | -46.6698 | -55.3182 | 16.4055 | 16.2274 | 10.9354 | 10.6441 | 7.7517 | 6.8793 | 5.8461 | 4.8984 | 3.0497 | 0.096269 | -7.1617 | -23.4017 | -34.8228 | -41.7535 | 14.8953 | 14.6181 | 9.2206 | 8.7495 | 5.6539 | 4.5508 | 3.2727 | 2.0865 | -0.50268 | -4.1173 | -13.0323 | -33.0636 | -47.1099 | -55.546
|  | WROUGHTON | CT |  |  | 16.1062 | 15.8544 | 15.5708 | 15.0897 | 14.5147 | 13.3417 | 7.094 | 4.5056 | 1.4245 | -2.2732 | -11.463 | -32.1641 | -46.6698 | -55.3182 | 16.4448 | 16.2885 | 16.107 | 15.8267 | 15.4778 | 14.5772 | 7.6676 | 5.5244 | 3.0497 | 0.096269 | -7.1617 | -23.4017 | -34.8228 | -41.7535 | 15.0181 | 14.8144 | 14.5788 | 14.1655 | 13.6616 | 12.3946 | 5.0974 | 2.5237 | -0.50268 | -4.1173 | -13.0323 | -33.0636 | -47.1099 | -55.546
|  | WROUGHTON | LW |  |  | 15.965 | 15.6238 | 11.1845 | 10.6326 | 7.9626 | 6.8634 | 5.6158 | 4.4533 | 3.3249 | 1.7343 | -3.3178 | -20.9047 | -34.748 | -39.79 | 16.4055 | 16.2274 | 10.9354 | 10.6441 | 7.7517 | 6.8793 | 5.8461 | 4.8984 | 3.9764 | 2.4142 | -1.6126 | -15.5326 | -26.686 | -31.0927 | 14.8953 | 14.6181 | 9.2206 | 8.7495 | 5.6539 | 4.5508 | 3.2727 | 2.0865 | 0.92722 | -0.84314 | -5.7889 | -22.8604 | -36.3823 | -41.5163
|  | WROUGHTON | ST |  |  | 16.1363 | 15.9237 | 15.6931 | 15.3505 | 10.9055 | 10.1745 | 7.3041 | 6.525 | 5.7675 | 4.9489 | 2.9404 | -3.5762 | -8.7514 | -11.3375 | 16.4534 | 16.3189 | 16.1689 | 15.9143 | 10.5506 | 9.8486 | 6.4727 | 5.7118 | 4.9561 | 4.1805 | 2.3545 | -3.2693 | -7.9668 | -10.5264 | 15.0424 | 14.8738 | 14.6864 | 14.3784 | 8.9537 | 8.1853 | 4.7415 | 3.9085 | 3.0858 | 2.1824 | 0.094039 | -6.5108 | -11.939 | -14.5324
|  | WROUGHTON | FS |  |  | 16.1062 | 15.8544 | 15.5708 | 15.0897 | 14.5147 | 13.3417 | 7.094 | 4.5056 | 1.4245 | -2.2732 | -11.463 | -32.1641 | -46.6698 | -55.3182 | 16.5078 | 16.4095 | 16.3067 | 16.1678 | 16.0174 | 15.4798 | 14.8788 | 14.3119 | 13.813 | 13.3613 | 12.4645 | 10.3929 | 7.7291 | 5.0987 | 15.1169 | 15.0038 | 14.8889 | 14.7136 | 14.5245 | 13.9505 | 13.3135 | 12.7202 | 12.1882 | 11.7073 | 10.7433 | 8.3604 | 5.4421 | 3.1593
AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH | MINIMUM HEADROOM | SU 88582 91845 | YES | 5.6849 | 5.3402 | 4.9969 | 4.4776 | 3.9555 | 3.4619 | 2.9037 | 2.2779 | 1.5223 | 0.67837 | -2.8443 | -17.7951 | -25.2165 | -25.1604 | 9.4276 | 9.2733 | 9.1169 | 8.8854 | 8.6375 | 8.3728 | 8.0467 | 7.6591 | 7.1984 | 6.212 | 2.9416 | -8.1882 | -13.5894 | -13.3457 | 7.1158 | 6.8262 | 6.5383 | 6.0774 | 5.6081 | 5.152 | 4.6373 | 4.0662 | 3.3895 | 2.604 | -0.94968 | -15.188 | -22.2247 | -22.1233
|  | WYCOMBE MARSH | CT |  |  | 5.9281 | 5.7437 | 5.5368 | 5.1468 | 4.7361 | 4.315 | 3.7934 | 3.1728 | 2.2247 | 1.1699 | -2.8443 | -17.7951 | -25.2165 | -25.1604 | 9.4839 | 9.3717 | 9.24 | 9.0453 | 8.8214 | 8.5631 | 8.2199 | 7.7956 | 7.1984 | 6.212 | 2.9416 | -8.1882 | -13.5894 | -13.3457 | 7.3342 | 7.187 | 7.0186 | 6.6757 | 6.3078 | 5.9185 | 5.4357 | 4.8625 | 3.9887 | 3.0128 | -0.94968 | -15.188 | -22.2247 | -22.1233
|  | WYCOMBE MARSH | LW |  |  | 5.6849 | 5.3402 | 4.9969 | 4.4776 | 3.9555 | 3.4619 | 2.9037 | 2.2779 | 1.5223 | 0.67837 | -1.2902 | -4.8694 | -6.2063 | -6.7859 | 9.4276 | 9.2733 | 9.1169 | 8.8854 | 8.6375 | 8.3728 | 8.0467 | 7.6591 | 7.2101 | 6.6754 | 5.387 | 3.1839 | 2.4902 | 2.1296 | 7.1158 | 6.8262 | 6.5383 | 6.0774 | 5.6081 | 5.152 | 4.6373 | 4.0662 | 3.3895 | 2.604 | 0.70715 | -2.6661 | -3.8819 | -4.4181
|  | WYCOMBE MARSH | ST |  |  | 6.0784 | 5.9803 | 5.8602 | 5.7261 | 5.6023 | 5.4917 | 5.3323 | 5.1374 | 4.9017 | 4.621 | 3.9 | 0.90162 | -1.0593 | -2.4081 | 9.5284 | 9.4466 | 9.3519 | 9.226 | 9.1038 | 8.9729 | 8.7946 | 8.5886 | 8.3462 | 8.0588 | 7.3219 | 4.5222 | 2.372 | 0.32468 | 7.4779 | 7.4138 | 7.322 | 7.1982 | 7.0821 | 6.968 | 6.8047 | 6.6087 | 6.3747 | 6.0933 | 5.36 | 2.3851 | 0.53318 | -0.51701
|  | WYCOMBE MARSH | FS |  |  | 5.9281 | 5.7437 | 5.5368 | 5.1468 | 4.7361 | 4.315 | 3.7934 | 3.1728 | 2.2247 | 1.1699 | -2.8443 | -17.7951 | -25.2165 | -25.1604 | 9.5592 | 9.4657 | 9.3712 | 9.2668 | 9.1629 | 9.0638 | 8.947 | 8.8154 | 8.6447 | 8.4439 | 7.921 | 5.6514 | 2.0426 | -2.6161 | 7.5085 | 7.4302 | 7.3587 | 7.2403 | 7.1319 | 7.0358 | 6.9254 | 6.8052 | 6.6522 | 6.4765 | 6.0218 | 3.9493 | 1.1796 | -0.98407
LOVEDEAN GSP | WYMERING BSP | WYMERING | MINIMUM HEADROOM | SU 64974 05375 | YES | 25.494 | 25.1207 | 24.7328 | 23.9274 | 22.7032 | 21.4396 | 19.699 | 17.9478 | 16.1311 | 14.1178 | 9.5711 | 1.6434 | -1.1312 | -2.9844 | 21.7083 | 21.2779 | 20.9249 | 20.466 | 19.8988 | 19.2678 | 18.2027 | 17.0528 | 15.9322 | 14.6105 | 11.6217 | 4.906 | -6.5946 | -21.8962 | 20.5453 | 20.0298 | 19.521 | 18.658 | 17.7029 | 16.6756 | 15.4222 | 14.1463 | 12.9322 | 11.6049 | 8.795 | 2.5351 | -0.11099 | -4.277
|  | WYMERING | CT |  |  | 25.5274 | 25.1207 | 24.7549 | 24.3938 | 23.9969 | 23.1298 | 22.1131 | 20.6396 | 18.72 | 16.5377 | 11.9744 | 2.9906 | -0.64033 | -2.7003 | 21.7269 | 21.2779 | 20.9249 | 20.6199 | 20.2691 | 19.8534 | 19.1678 | 18.1054 | 16.7779 | 15.2606 | 12.0022 | 4.906 | -0.40763 | -7.5332 | 20.7023 | 20.2365 | 19.8107 | 19.2408 | 18.6196 | 17.8774 | 17.0492 | 16.1004 | 14.9657 | 13.7793 | 11.5417 | 4.1756 | 0.83563 | -1.0866
|  | WYMERING | LW |  |  | 25.494 | 25.121 | 24.7328 | 23.9274 | 22.7032 | 21.4396 | 19.699 | 17.9478 | 16.1311 | 14.1178 | 9.5711 | 1.6434 | -1.1312 | -2.9844 | 21.7083 | 21.3431 | 20.9963 | 20.466 | 19.8988 | 19.2678 | 18.2027 | 17.0528 | 15.9322 | 14.6105 | 11.6217 | 6.4797 | 4.5771 | 3.1317 | 20.5453 | 20.0298 | 19.521 | 18.658 | 17.7029 | 16.6756 | 15.4222 | 14.1463 | 12.9322 | 11.6049 | 8.795 | 2.5351 | -0.11099 | -1.9302
|  | WYMERING | ST |  |  | 25.5879 | 25.2281 | 24.9093 | 24.4537 | 24.0326 | 23.612 | 23.1183 | 22.6762 | 22.1898 | 21.642 | 19.8142 | 11.584 | 6.1946 | 4.0236 | 21.7722 | 21.3587 | 21.0415 | 20.5962 | 20.1932 | 19.7813 | 19.2723 | 18.8324 | 18.3574 | 17.7748 | 15.6596 | 8.2877 | 1.5526 | -5.4829 | 20.8559 | 20.5026 | 20.1835 | 19.6751 | 19.2027 | 18.7132 | 18.1161 | 17.5677 | 16.9661 | 16.2739 | 14.6109 | 9.8913 | 6.2244 | 4.4397
|  | WYMERING | FS |  |  | 25.5274 | 25.1207 | 24.7549 | 24.3938 | 23.9969 | 23.1298 | 22.1131 | 20.6396 | 18.72 | 16.5377 | 11.9744 | 2.9906 | -0.64033 | -2.7003 | 21.8109 | 21.5565 | 21.2874 | 20.9631 | 20.6295 | 20.2775 | 19.8835 | 19.037 | 17.9809 | 16.8188 | 14.1314 | 5.4466 | -6.5946 | -21.8962 | 20.8991 | 20.6814 | 20.4311 | 20.093 | 19.734 | 19.3512 | 18.9277 | 18.4752 | 17.9685 | 17.4134 | 16.1118 | 9.3741 | 0.9132 | -4.277
COWLEY GSP | YARNTON BSP | YARNTON | MINIMUM HEADROOM | SP 48277 12108 | NO | 16.5327 | 16.0001 | 15.4258 | 14.4302 | 13.3126 | 12.0907 | 10.8143 | 9.433 | 5.9692 | 1.5888 | -8.5315 | -29.4966 | -41.1112 | -48.176 | 19.4173 | 19.1006 | 18.7986 | 18.4154 | 17.9706 | 17.4596 | 16.6158 | 14.6501 | 11.8856 | 8.6065 | 1.0171 | -14.3624 | -22.7853 | -28.1176 | 15.6164 | 15.1358 | 14.6198 | 13.7352 | 12.742 | 11.6494 | 10.4752 | 8.873 | 5.3881 | 1.208 | -8.4559 | -28.4128 | -39.4648 | -46.2508
|  | YARNTON | CT |  |  | 16.9975 | 16.792 | 16.5118 | 15.7795 | 14.9209 | 13.9006 | 12.4971 | 9.7149 | 5.9692 | 1.5888 | -8.5315 | -29.4966 | -41.1112 | -48.176 | 19.5213 | 19.3757 | 19.1809 | 18.8759 | 18.4824 | 17.9211 | 16.7663 | 14.6501 | 11.8856 | 8.6065 | 1.0171 | -14.3624 | -22.7853 | -28.1176 | 16.0298 | 15.8465 | 15.6008 | 14.9603 | 14.2011 | 13.218 | 11.4952 | 8.9483 | 5.3881 | 1.208 | -8.4559 | -28.4128 | -39.4648 | -46.2508
|  | YARNTON | LW |  |  | 16.5327 | 16.0001 | 15.4258 | 14.4302 | 13.3126 | 12.0907 | 10.8143 | 9.433 | 6.6317 | 3.0152 | -5.6157 | -23.8535 | -33.5938 | -38.3056 | 19.4173 | 19.1006 | 18.7986 | 18.4154 | 17.9706 | 17.4596 | 16.6158 | 14.8437 | 12.685 | 10.035 | 3.6336 | -9.8947 | -17.2639 | -21.138 | 15.6164 | 15.1358 | 14.6198 | 13.7352 | 12.742 | 11.6494 | 10.4752 | 8.873 | 6.0548 | 2.6157 | -5.606 | -22.9821 | -32.36 | -37.0481
|  | YARNTON | ST |  |  | 17.1254 | 16.9766 | 16.7772 | 16.3863 | 15.9603 | 15.4364 | 14.8342 | 14.1542 | 13.2903 | 12.3443 | 10.0612 | 2.6441 | -2.8458 | -6.5092 | 19.6331 | 19.5671 | 19.4758 | 19.2487 | 19.0271 | 18.7509 | 18.3837 | 18.0189 | 17.5101 | 16.6763 | 14.7903 | 8.5914 | 3.6129 | -0.62374 | 16.1429 | 16.0091 | 15.8357 | 15.4729 | 15.0955 | 14.6432 | 14.0966 | 13.4964 | 12.6956 | 11.702 | 9.434 | 2.2769 | -2.9429 | -6.2914
|  | YARNTON | FS |  |  | 16.9975 | 16.792 | 16.5118 | 15.7795 | 14.9209 | 13.9006 | 12.4971 | 9.7149 | 5.9692 | 1.5888 | -8.5315 | -29.4966 | -41.1112 | -48.176 | 19.7282 | 19.5245 | 19.3227 | 19.0996 | 18.8362 | 18.4755 | 17.642 | 16.5391 | 15.1478 | 13.5979 | 10.0068 | -0.54711 | -9.9574 | -17.6999 | 16.093 | 15.7835 | 15.4376 | 14.9653 | 14.4 | 13.6219 | 12.5526 | 11.1831 | 9.5242 | 7.6878 | 3.4697 | -8.7407 | -18.4669 | -23.6462
BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON | MINIMUM HEADROOM | SU 53699 74307 | YES | 2.3865 | 2.1013 | 1.8462 | 1.5613 | 1.2065 | 0.86134 | 0.13069 | -0.99703 | -2.4479 | -4.1905 | -8.5003 | -19.7264 | -24.5871 | -25.0114 | 5.0692 | 5.0103 | 4.9434 | 4.8352 | 4.5726 | 4.3259 | 3.9559 | 3.1117 | 2.0347 | 0.72818 | -2.5342 | -11.0842 | -14.6406 | -14.8939 | 3.178 | 2.9024 | 2.65 | 2.3844 | 2.0334 | 1.6902 | 1.4276 | 1.1632 | 0.37511 | -1.2853 | -5.3994 | -16.1255 | -20.7381 | -21.1257
|  | YATTENDON | CT |  |  | 2.5748 | 2.3868 | 2.2112 | 1.9282 | 1.5348 | 0.97431 | 0.13069 | -0.99703 | -2.4479 | -4.1905 | -8.5003 | -19.7264 | -24.5871 | -25.0114 | 5.0692 | 5.0103 | 4.9434 | 4.8352 | 4.5726 | 4.3259 | 3.9559 | 3.1117 | 2.0347 | 0.72818 | -2.5342 | -11.0842 | -14.6406 | -14.8939 | 3.359 | 3.1762 | 2.9979 | 2.7296 | 2.3246 | 1.9446 | 1.6164 | 1.2334 | 0.37511 | -1.2853 | -5.3994 | -16.1255 | -20.7381 | -21.1257
|  | YATTENDON | LW |  |  | 2.3865 | 2.1013 | 1.8462 | 1.5613 | 1.2065 | 0.86134 | 0.60799 | 0.35086 | 0.08698 | -0.18216 | -0.74146 | -1.9294 | -2.5838 | -2.7786 | 5.0973 | 5.0564 | 5.0324 | 4.9662 | 4.8146 | 4.6716 | 4.5592 | 4.4493 | 4.3608 | 4.2674 | 3.8099 | 3.1351 | 2.9683 | 2.9084 | 3.178 | 2.9024 | 2.65 | 2.3844 | 2.0334 | 1.6902 | 1.4276 | 1.1632 | 0.89861 | 0.63021 | 0.077065 | -1.0591 | -1.6695 | -1.8529
|  | YATTENDON | ST |  |  | 2.6391 | 2.4903 | 2.3562 | 2.0909 | 1.7392 | 1.4241 | 1.1658 | 0.892 | 0.59912 | 0.26904 | -0.50525 | -2.848 | -4.7722 | -5.8385 | 5.1094 | 5.085 | 5.0631 | 4.9943 | 4.803 | 4.673 | 4.5942 | 4.5143 | 4.4349 | 4.3398 | 3.9282 | 2.1192 | 0.50089 | -0.69505 | 3.4373 | 3.3026 | 3.1775 | 2.9375 | 2.5917 | 2.2964 | 2.0565 | 1.8094 | 1.5503 | 1.2612 | 0.59364 | -1.375 | -3.0746 | -4.0613
|  | YATTENDON | FS |  |  | 2.5748 | 2.3868 | 2.2112 | 1.9282 | 1.5348 | 0.97431 | 0.13069 | -0.99703 | -2.4479 | -4.1905 | -8.5003 | -19.7264 | -24.5871 | -25.0114 | 5.1215 | 5.0966 | 5.0773 | 5.0363 | 4.9482 | 4.8702 | 4.8139 | 4.76 | 4.7165 | 4.6668 | 4.5462 | 4.1368 | 3.5671 | 2.958 | 3.5347 | 3.4419 | 3.3664 | 3.1957 | 2.9883 | 2.7899 | 2.6306 | 2.4738 | 2.2821 | 2.0886 | 1.6896 | 0.32276 | -0.48253 | -1.0618
MELKSHAM GSP | CHIPPENHAM | YATTON KEYNALL | MINIMUM HEADROOM | ST 87300 75782 | YES | 0.60949 | 0.46908 | 0.30772 | 0.098706 | -0.18471 | -0.59704 | -1.0933 | -1.741 | -2.5517 | -3.6055 | -6.3848 | -11.4905 | -14.719 | -15.6369 | 1.4495 | 1.3719 | 1.2834 | 1.0704 | 0.81727 | 0.48006 | 0.064979 | -0.45347 | -1.1095 | -1.8087 | -3.5455 | -8.5709 | -11.4266 | -12.4855 | 0.59094 | 0.54913 | 0.44935 | 0.30589 | 0.13091 | -0.23798 | -0.77354 | -1.5007 | -2.4316 | -3.5701 | -6.2669 | -11.1458 | -14.4758 | -15.4479
|  | YATTON KEYNALL | CT |  |  | 0.71177 | 0.60853 | 0.47851 | 0.27834 | 0.012731 | -0.3359 | -0.80789 | -1.4706 | -2.436 | -3.6055 | -6.3848 | -11.2642 | -12.9573 | -14.0922 | 1.4941 | 1.4225 | 1.3315 | 1.1939 | 1.0093 | 0.76419 | 0.3875 | -0.084807 | -0.69321 | -1.4626 | -3.5455 | -7.348 | -8.6704 | -9.6691 | 0.61353 | 0.56143 | 0.49109 | 0.38415 | 0.21038 | -0.21055 | -0.77354 | -1.5007 | -2.4316 | -3.5701 | -6.2669 | -11.0261 | -12.7148 | -13.8925
|  | YATTON KEYNALL | LW |  |  | 0.60949 | 0.46908 | 0.30772 | 0.098706 | -0.16802 | -0.50363 | -0.94715 | -1.5042 | -2.1952 | -3.0269 | -5.0605 | -8.5518 | -10.0585 | -11.3547 | 1.4495 | 1.3719 | 1.2834 | 1.1555 | 0.99123 | 0.77454 | 0.44767 | 0.03459 | -0.47921 | -1.1025 | -2.6352 | -5.2543 | -6.5299 | -7.8236 | 0.59094 | 0.54913 | 0.44935 | 0.30589 | 0.13091 | -0.18389 | -0.59447 | -1.1195 | -1.7981 | -2.6131 | -4.5987 | -8.016 | -9.5981 | -11.0287
|  | YATTON KEYNALL | ST |  |  | 0.73158 | 0.58665 | 0.40736 | 0.11726 | -0.18471 | -0.59704 | -1.0933 | -1.741 | -2.5517 | -3.417 | -5.3998 | -11.4905 | -14.719 | -15.6369 | 1.528 | 1.4381 | 1.325 | 1.0704 | 0.81727 | 0.48006 | 0.064979 | -0.45347 | -1.1095 | -1.8087 | -3.4676 | -8.5709 | -11.4266 | -12.4855 | 0.73046 | 0.69482 | 0.64573 | 0.46215 | 0.17372 | -0.23798 | -0.73737 | -1.3727 | -2.1745 | -3.0268 | -4.9799 | -11.1458 | -14.4758 | -15.4479
|  | YATTON KEYNALL | FS |  |  | 0.71177 | 0.60853 | 0.47851 | 0.27834 | 0.012731 | -0.3359 | -0.80789 | -1.4706 | -2.436 | -3.6055 | -6.3848 | -11.2642 | -12.9573 | -14.0922 | 1.5761 | 1.5425 | 1.5027 | 1.4327 | 1.3537 | 1.2593 | 1.1503 | 1.0288 | 0.87287 | 0.67287 | 0.13338 | -2.0618 | -4.7463 | -6.5824 | 0.72041 | 0.71091 | 0.69778 | 0.65805 | 0.61212 | 0.5547 | 0.48854 | 0.39111 | 0.20207 | -0.039984 | -0.69046 | -3.4714 | -6.8222 | -8.9981
AXMINSTER | YEOVIL BSP | YEOVIL | MINIMUM HEADROOM | ST 57690 16833 | YES | 7.6923 | 7.3016 | 6.8826 | 6.21 | 5.4447 | 4.582 | 3.5874 | 2.4108 | 0.6968 | -2.2005 | -8.9111 | -21.114 | -24.813 | -27.0987 | 9.3188 | 9.1011 | 8.8664 | 8.5336 | 8.1385 | 7.6586 | 6.9656 | 5.5935 | 3.8445 | 1.7208 | -3.2485 | -12.0752 | -14.5625 | -16.2205 | 6.9983 | 6.6532 | 6.2794 | 5.6839 | 4.995 | 4.2014 | 3.2632 | 2.1315 | 0.017713 | -2.7378 | -9.1313 | -20.6987 | -24.1544 | -26.3092
|  | YEOVIL | CT |  |  | 8.089 | 7.9496 | 7.7742 | 7.3211 | 6.8003 | 6.1626 | 5.4165 | 4.5092 | 3.0264 | 1.36 | -2.3032 | -11.0744 | -16.1856 | -18.888 | 9.4744 | 9.382 | 9.2585 | 9.0026 | 8.6817 | 8.259 | 7.7219 | 7.0358 | 6.0333 | 4.8608 | 2.1954 | -3.846 | -7.4995 | -10.7784 | 7.334 | 7.2059 | 7.0461 | 6.6377 | 6.1626 | 5.5736 | 4.8717 | 4.0089 | 2.6216 | 1.0526 | -2.417 | -10.667 | -15.2127 | -17.6336
|  | YEOVIL | LW |  |  | 7.6923 | 7.3016 | 6.8826 | 6.21 | 5.4447 | 4.582 | 3.5874 | 2.4108 | 0.6968 | -2.2005 | -8.9111 | -21.114 | -24.813 | -27.0987 | 9.3188 | 9.1011 | 8.8664 | 8.5336 | 8.1385 | 7.6586 | 6.9656 | 5.5935 | 3.8445 | 1.7208 | -3.2485 | -12.0752 | -14.5625 | -16.2205 | 6.9983 | 6.6532 | 6.2794 | 5.6839 | 4.995 | 4.2014 | 3.2632 | 2.1315 | 0.017713 | -2.7378 | -9.1313 | -20.6987 | -24.1544 | -26.3092
|  | YEOVIL | ST |  |  | 8.1614 | 8.0318 | 7.8819 | 7.6803 | 7.4043 | 7.0639 | 6.5455 | 5.881 | 5.0905 | 4.0595 | 1.2915 | -7.9185 | -14.0938 | -16.6723 | 9.4796 | 9.3391 | 9.1745 | 8.9705 | 8.6946 | 8.356 | 7.8376 | 7.1745 | 6.3759 | 5.4183 | 2.9868 | -4.67 | -10.0193 | -12.9154 | 7.3855 | 7.2606 | 7.1169 | 6.9238 | 6.6569 | 6.3268 | 5.8154 | 5.1574 | 4.2845 | 3.1781 | 0.34426 | -8.8574 | -14.8417 | -16.965
|  | YEOVIL | FS |  |  | 8.089 | 7.9496 | 7.7742 | 7.3211 | 6.8003 | 6.1626 | 5.4165 | 4.5092 | 3.0264 | 1.36 | -2.3032 | -11.0744 | -16.1856 | -18.888 | 9.5762 | 9.4631 | 9.3399 | 9.1915 | 9.0203 | 8.7986 | 8.5484 | 8.2201 | 7.7715 | 7.2745 | 6.0866 | 1.3874 | -5.0147 | -12.132 | 7.482 | 7.3863 | 7.2842 | 7.1189 | 6.9317 | 6.6928 | 6.4311 | 6.0923 | 5.6423 | 5.1539 | 4.015 | -0.87199 | -6.6987 | -10.8618
AXMINSTER | YEOVIL BSP | YETMINSTER | MINIMUM HEADROOM | ST 60294 10206 | YES | 2.9906 | 2.5576 | 2.0512 | 1.5213 | 0.75214 | -0.32978 | -1.8378 | -3.8326 | -6.3616 | -9.492 | -17.59 | -36.0605 | -49.9191 | -58.9733 | 4.7083 | 4.4513 | 4.1234 | 3.7095 | 3.1254 | 2.3213 | 1.1837 | -0.33706 | -2.3027 | -4.7424 | -11.0612 | -25.4782 | -36.8111 | -44.7765 | 3.4459 | 3.0496 | 2.5835 | 2.0877 | 1.3332 | 0.30394 | -1.1344 | -3.0409 | -5.4782 | -8.4941 | -16.2876 | -34.0553 | -47.7027 | -56.9459
|  | YETMINSTER | CT |  |  | 3.3559 | 3.1769 | 2.9802 | 2.7486 | 2.4812 | 2.1681 | 1.7917 | 1.3959 | 0.88886 | 0.26093 | -1.3994 | -5.4261 | -7.8237 | -9.483 | 4.9159 | 4.8324 | 4.739 | 4.6095 | 4.4462 | 4.2444 | 3.978 | 3.711 | 3.3382 | 2.8069 | 1.7674 | -1.2767 | -3.3732 | -5.2956 | 3.7611 | 3.5962 | 3.4153 | 3.1998 | 2.9476 | 2.6581 | 2.3017 | 1.9215 | 1.4253 | 0.59069 | -1.3343 | -5.4601 | -7.9573 | -9.812
|  | YETMINSTER | LW |  |  | 2.9906 | 2.5576 | 2.0512 | 1.5213 | 0.75214 | -0.32978 | -1.8378 | -3.8326 | -6.3616 | -9.492 | -17.59 | -36.0605 | -49.9191 | -58.9733 | 4.7083 | 4.4513 | 4.1234 | 3.7095 | 3.1254 | 2.3213 | 1.1837 | -0.33706 | -2.3027 | -4.7424 | -11.0612 | -25.4782 | -36.8111 | -44.7765 | 3.4459 | 3.0496 | 2.5835 | 2.0877 | 1.3332 | 0.30394 | -1.1344 | -3.0409 | -5.4782 | -8.4941 | -16.2876 | -34.0553 | -47.7027 | -56.9459
|  | YETMINSTER | ST |  |  | 3.4607 | 3.3384 | 3.2039 | 2.87 | 2.5686 | 2.2625 | 1.8911 | 1.5502 | 0.73229 | -0.16524 | -2.3763 | -9.1475 | -13.8285 | -15.9044 | 4.9657 | 4.9123 | 4.8511 | 4.5698 | 4.3405 | 4.1128 | 3.8081 | 3.5841 | 3.1991 | 2.7753 | 0.95065 | -4.754 | -9.0781 | -11.5563 | 3.8619 | 3.7491 | 3.6262 | 3.2674 | 2.9578 | 2.6498 | 2.1407 | 1.5245 | 0.68535 | -0.22597 | -2.4717 | -9.4588 | -14.4444 | -16.8053
|  | YETMINSTER | FS |  |  | 3.3559 | 3.1769 | 2.9802 | 2.7486 | 2.4812 | 2.1681 | 1.7917 | 1.3959 | 0.88886 | 0.26093 | -1.3994 | -5.4261 | -7.8237 | -9.483 | 4.9893 | 4.9485 | 4.9033 | 4.7883 | 4.6644 | 4.5255 | 4.3725 | 4.2186 | 3.9993 | 3.7702 | 2.4264 | -1.5311 | -4.9394 | -6.9926 | 3.9223 | 3.8396 | 3.7533 | 3.5662 | 3.3703 | 3.1601 | 2.8038 | 2.2815 | 1.636 | 0.91189 | -0.8156 | -6.0311 | -10.4637 | -12.8643
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD | MINIMUM HEADROOM | SU 60592 00043 | YES | 3.432 | 3.0675 | 2.6424 | 1.5117 | 0.39877 | -0.64897 | -1.6971 | -2.8641 | -4.1566 | -5.473 | -8.3523 | -13.7512 | -15.9624 | -17.7522 | 7.0546 | 6.8758 | 6.6517 | 6.1197 | 5.5902 | 5.0844 | 4.5469 | 3.8939 | 3.005 | 2.0353 | -0.074621 | -5.7075 | -13.6224 | -31.6639 | 2.6789 | 2.3577 | 1.9832 | 1.0265 | 0.073714 | -0.83885 | -1.7687 | -2.8091 | -3.9846 | -5.2011 | -7.8808 | -12.9399 | -15.0132 | -16.5572
|  | ZETLAND ROAD | CT |  |  | 3.8467 | 3.6797 | 3.4414 | 2.5422 | 1.7062 | 0.94728 | 0.20546 | -0.67543 | -1.975 | -3.3058 | -6.0073 | -12.4377 | -15.9624 | -17.7522 | 7.1309 | 6.9387 | 6.6759 | 6.1223 | 5.5943 | 5.0862 | 4.5469 | 3.8939 | 3.005 | 2.0353 | -0.074621 | -5.7075 | -11.6951 | -20.4486 | 3.0431 | 2.8944 | 2.681 | 1.9219 | 1.2099 | 0.5511 | -0.10722 | -0.89238 | -2.0674 | -3.2999 | -5.8427 | -11.7388 | -14.8803 | -16.5572
|  | ZETLAND ROAD | LW |  |  | 3.432 | 3.0675 | 2.6424 | 1.5117 | 0.39877 | -0.64897 | -1.6971 | -2.8641 | -4.1566 | -5.473 | -8.3523 | -13.7512 | -15.9408 | -17.2784 | 7.0546 | 6.8758 | 6.6517 | 6.1197 | 5.5902 | 5.0844 | 4.5542 | 3.9383 | 3.2221 | 2.4541 | 0.69956 | -2.4116 | -3.7752 | -4.9244 | 2.6789 | 2.3577 | 1.9832 | 1.0265 | 0.073714 | -0.83885 | -1.7687 | -2.8091 | -3.9846 | -5.2011 | -7.8808 | -12.9399 | -15.0132 | -16.4008
|  | ZETLAND ROAD | ST |  |  | 4.1015 | 4.0774 | 3.9803 | 3.6501 | 3.4132 | 3.2825 | 3.1779 | 3.0147 | 2.7887 | 2.5529 | 1.8664 | -1.871 | -4.9269 | -7.4078 | 7.2284 | 7.0953 | 6.8944 | 6.5574 | 6.264 | 6.0157 | 5.7543 | 5.4317 | 5.0084 | 4.5397 | 3.3265 | -1.6201 | -7.7876 | -16.6983 | 3.2685 | 3.2427 | 3.1499 | 2.8798 | 2.6838 | 2.5668 | 2.4597 | 2.2975 | 2.0627 | 1.8036 | 1.0948 | -2.3074 | -5.1613 | -7.5887
|  | ZETLAND ROAD | FS |  |  | 3.8467 | 3.6797 | 3.4414 | 2.5422 | 1.7062 | 0.94728 | 0.20546 | -0.67543 | -1.975 | -3.3058 | -6.0073 | -12.4377 | -15.9624 | -17.7522 | 7.2038 | 7.0792 | 6.9078 | 6.5631 | 6.2203 | 5.8915 | 5.5374 | 5.1357 | 4.6129 | 4.0414 | 2.6219 | -3.1339 | -13.6224 | -31.6639 | 3.2254 | 3.2227 | 3.1798 | 2.9197 | 2.6914 | 2.5059 | 2.3277 | 2.1275 | 1.8678 | 1.6119 | 0.98382 | -1.7081 | -5.5291 | -9.1255

## BSP Headroom Dem
Grid Supply Point | Bulk Supply Point |  | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Demand Headroom Winter MVA | [13 empty] | Demand Headroom Summer MVA | [13 empty] | Demand Headroom Spring/Autumn MVA
[6 empty] | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050
WILLESDEN GSP | ACTON LANE | ACTON LANE | MINIMUM HEADROOM | TQ 20805 83142 | YES | 124.2 | 124.2 | 124.2 | 124.1232 | 124.0594 | 123.9595 | 123.8508 | 123.7599 | 123.7398 | 123.7189 | 123.6825 | 123.5809 | 123.5599 | 123.5599 | 115.2 | 115.2 | 115.2 | 115.104 | 115.0243 | 114.8994 | 114.7635 | 114.6498 | 114.6247 | 114.5986 | 114.5531 | 114.4261 | 114.3998 | 114.3998 | 115.2 | 115.2 | 115.2 | 115.104 | 115.0243 | 114.8994 | 114.7635 | 114.6498 | 114.6247 | 114.5986 | 114.5531 | 114.4261 | 114.3998 | 114.3998
|  |  | CT |  |  | 124.2 | 124.2 | 124.2 | 124.1896 | 124.1713 | 124.1494 | 124.1101 | 124.0862 | 124.0862 | 124.0862 | 124.0862 | 124.0862 | 124.0862 | 124.0862 | 115.2 | 115.2 | 115.2 | 115.1871 | 115.1641 | 115.1368 | 115.0876 | 115.0578 | 115.0578 | 115.0578 | 115.0578 | 115.0578 | 115.0578 | 115.0578 | 115.2 | 115.2 | 115.2 | 115.1871 | 115.1641 | 115.1368 | 115.0876 | 115.0578 | 115.0578 | 115.0578 | 115.0578 | 115.0578 | 115.0578 | 115.0578
|  |  | LW |  |  | 124.2 | 124.2 | 124.2 | 124.1336 | 124.0594 | 123.9595 | 123.8508 | 123.7599 | 123.7398 | 123.7189 | 123.6825 | 123.5809 | 123.5599 | 123.5599 | 115.2 | 115.2 | 115.2 | 115.117 | 115.0243 | 114.8994 | 114.7635 | 114.6498 | 114.6247 | 114.5986 | 114.5531 | 114.4261 | 114.3998 | 114.3998 | 115.2 | 115.2 | 115.2 | 115.117 | 115.0243 | 114.8994 | 114.7635 | 114.6498 | 114.6247 | 114.5986 | 114.5531 | 114.4261 | 114.3998 | 114.3998
|  |  | ST |  |  | 124.2 | 124.2 | 124.2 | 124.1232 | 124.0713 | 124.0246 | 123.9535 | 123.9207 | 123.9207 | 123.9207 | 123.9207 | 123.9207 | 123.9207 | 123.9207 | 115.2 | 115.2 | 115.2 | 115.104 | 115.0392 | 114.9807 | 114.8918 | 114.8508 | 114.8508 | 114.8508 | 114.8508 | 114.8508 | 114.8508 | 114.8508 | 115.2 | 115.2 | 115.2 | 115.104 | 115.0392 | 114.9807 | 114.8918 | 114.8508 | 114.8508 | 114.8508 | 114.8508 | 114.8508 | 114.8508 | 114.8508
|  |  | FS |  |  | 124.2 | 124.2 | 124.2 | 124.1896 | 124.1713 | 124.1494 | 124.1101 | 124.0862 | 124.0862 | 124.0862 | 124.0862 | 124.0862 | 124.0862 | 124.0862 | 115.2 | 115.2 | 115.2 | 115.1791 | 115.1581 | 115.1328 | 115.1075 | 115.0866 | 115.0866 | 115.0866 | 115.0866 | 115.0866 | 115.0866 | 115.0866 | 115.2 | 115.2 | 115.2 | 115.1791 | 115.1581 | 115.1328 | 115.1075 | 115.0866 | 115.0866 | 115.0866 | 115.0866 | 115.0866 | 115.0866 | 115.0866
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT BSP | MINIMUM HEADROOM | SU 85922 48779 | YES | 63.4716 | 59.1714 | 54.8168 | 48.1905 | 40.135 | 32.1938 | 21.2746 | 8.4879 | -6.357 | -23.0019 | -63.7516 | -175.5003 | -229.4855 | -255.7577 | 81.6855 | 78.9788 | 76.2146 | 72.3527 | 67.535 | 62.0753 | 55.2527 | 46.056 | 34.2209 | 22.2016 | -14.6642 | -95.799 | -133.6026 | -152.4661 | 54.0923 | 50.3334 | 46.4673 | 40.2932 | 33.0427 | 25.8917 | 16.15 | 4.6029 | -9.7994 | -25.6283 | -59.2291 | -149.5859 | -200.5085 | -225.3174
|  |  | CT |  |  | 65.018 | 61.9197 | 58.2438 | 52.4606 | 45.9902 | 38.0701 | 29.1638 | 16.834 | 0.27733 | -16.4022 | -63.7516 | -175.5003 | -229.4855 | -255.7577 | 81.8094 | 79.3335 | 76.352 | 72.4337 | 67.9398 | 62.0753 | 55.4246 | 46.056 | 34.2209 | 22.2016 | -14.6642 | -95.799 | -133.6026 | -152.4661 | 55.9349 | 53.4343 | 50.4473 | 45.3194 | 39.4651 | 32.4836 | 24.5583 | 12.7339 | -3.4258 | -19.7635 | -51.2103 | -149.5859 | -200.5085 | -225.3174
|  |  | LW |  |  | 63.4716 | 59.1714 | 54.8168 | 48.1905 | 40.135 | 32.1938 | 21.2746 | 8.4879 | -6.357 | -23.0019 | -57.9679 | -147.8523 | -194.6636 | -205.736 | 81.6855 | 78.9788 | 76.2146 | 72.3527 | 67.535 | 62.697 | 55.2527 | 46.2296 | 36.1565 | 24.9138 | -0.15488 | -74.5949 | -108.8357 | -117.0402 | 54.0923 | 50.3334 | 46.4673 | 40.2932 | 33.0427 | 25.8917 | 16.15 | 4.6029 | -9.7994 | -25.6283 | -59.2291 | -123.3321 | -167.814 | -178.3306
|  |  | ST |  |  | 66.7637 | 65.2189 | 63.3096 | 60.5552 | 57.3341 | 54.013 | 49.7878 | 44.6756 | 38.6762 | 31.4598 | 13.2391 | -46.6583 | -88.197 | -108.5346 | 82.9956 | 81.6597 | 79.9862 | 77.6788 | 74.9486 | 71.9619 | 68.2023 | 63.732 | 58.532 | 52.2787 | 36.207 | -15.8895 | -56.479 | -86.8073 | 57.5269 | 56.3609 | 54.9025 | 52.7343 | 50.1964 | 47.6428 | 44.4049 | 40.1529 | 34.4517 | 27.566 | 9.9694 | -47.6115 | -87.3726 | -106.8487
|  |  | FS |  |  | 65.018 | 61.9197 | 58.2438 | 52.4606 | 45.9902 | 38.0701 | 29.1638 | 16.834 | 0.27733 | -16.4022 | -63.7516 | -175.5003 | -229.4855 | -255.7577 | 82.8741 | 81.2902 | 79.4167 | 77.0337 | 74.2371 | 71.034 | 67.0969 | 62.1355 | 56.3796 | 49.8964 | 34.1395 | -19.096 | -81.1907 | -145.1121 | 57.498 | 56.1965 | 54.6549 | 52.3486 | 49.6839 | 46.7544 | 43.1882 | 38.5833 | 32.1417 | 24.9684 | 7.8434 | -48.3337 | -104.803 | -140.949
BRAMLEY (FLEE) | ALTON | ALTON | MINIMUM HEADROOM | SU 72730 39772 | YES | 93.15 | 93.15 | 93.15 | 92.8466 | 92.6414 | 92.4566 | 92.1755 | 92.0459 | 91.7435 | 91.4859 | 90.9193 | 93.15 | 93.15 | 84.2719 | 86.4 | 86.4 | 86.4 | 86.0207 | 85.7643 | 85.5332 | 85.1819 | 85.0199 | 84.6419 | 84.3199 | 83.6116 | 86.4 | 86.4 | 75.3024 | 86.4 | 86.4 | 86.4 | 86.0207 | 85.7643 | 85.5332 | 85.1819 | 85.0199 | 84.6419 | 84.3199 | 83.6116 | 86.4 | 86.4 | 75.3024
|  |  | CT |  |  | 93.15 | 93.15 | 93.15 | 93.1091 | 93.0365 | 92.9501 | 92.7947 | 92.7003 | 92.5579 | 92.2413 | 91.6666 | 93.15 | 93.15 | 86.9345 | 86.4 | 86.4 | 86.4 | 86.3489 | 86.2581 | 86.1501 | 85.9559 | 85.8378 | 85.6599 | 85.2642 | 84.5457 | 86.4 | 86.4 | 78.6306 | 86.4 | 86.4 | 86.4 | 86.3489 | 86.2581 | 86.1501 | 85.9559 | 85.8378 | 85.6599 | 85.2642 | 84.5457 | 86.4 | 86.4 | 78.6306
|  |  | LW |  |  | 93.15 | 93.15 | 93.15 | 93.1141 | 93.074 | 93.02 | 92.9613 | 92.9121 | 92.7984 | 92.6804 | 92.474 | 93.15 | 93.15 | 86.5654 | 86.4 | 86.4 | 86.4 | 86.3551 | 86.305 | 86.2376 | 86.1641 | 86.1027 | 85.9605 | 85.813 | 85.5551 | 86.4 | 86.4 | 78.1693 | 86.4 | 86.4 | 86.4 | 86.3551 | 86.305 | 86.2376 | 86.1641 | 86.1027 | 85.9605 | 85.813 | 85.5551 | 86.4 | 86.4 | 78.1693
|  |  | ST |  |  | 93.15 | 93.15 | 93.15 | 92.8466 | 92.6414 | 92.4566 | 92.1755 | 92.0459 | 91.7435 | 91.4859 | 90.9193 | 93.15 | 93.15 | 84.2719 | 86.4 | 86.4 | 86.4 | 86.0207 | 85.7643 | 85.5332 | 85.1819 | 85.0199 | 84.6419 | 84.3199 | 83.6116 | 86.4 | 86.4 | 75.3024 | 86.4 | 86.4 | 86.4 | 86.0207 | 85.7643 | 85.5332 | 85.1819 | 85.0199 | 84.6419 | 84.3199 | 83.6116 | 86.4 | 86.4 | 75.3024
|  |  | FS |  |  | 93.15 | 93.15 | 93.15 | 93.1091 | 93.0365 | 92.9501 | 92.7947 | 92.7003 | 92.5579 | 92.2413 | 91.6666 | 93.15 | 93.15 | 86.9345 | 86.4 | 86.4 | 86.4 | 86.3172 | 86.2345 | 86.1345 | 86.0345 | 85.9518 | 85.8057 | 85.6648 | 85.3829 | 86.4 | 86.4 | 84.05 | 86.4 | 86.4 | 86.4 | 86.3172 | 86.2345 | 86.1345 | 86.0345 | 85.9518 | 85.8057 | 85.6648 | 85.3829 | 86.4 | 86.4 | 84.05
MELKSHAM GSP | AMESBURY | AMESBURY | MINIMUM HEADROOM | SU 15842 42724 | YES | 39.9564 | 38.8317 | 37.766 | 36.583 | 35.1212 | 33.5269 | 31.3297 | 28.6872 | 25.3674 | 21.6537 | 13.3941 | -1.9183 | -11.2109 | -16.6271 | 47.0067 | 46.4355 | 45.896 | 45.27 | 44.4761 | 43.5916 | 42.2957 | 40.7333 | 38.709 | 36.3257 | 31.4664 | 19.8471 | 12.0079 | 5.7062 | 46.3862 | 45.634 | 44.941 | 44.1701 | 43.2295 | 42.2045 | 40.4761 | 37.8852 | 34.6945 | 31.1139 | 23.1372 | 7.9619 | -2.083 | -7.9689
|  |  | CT |  |  | 40.6491 | 39.9247 | 39.1676 | 38.0695 | 36.7945 | 35.1409 | 33.2489 | 30.7059 | 27.2377 | 23.5535 | 16.1008 | -1.2381 | -11.2109 | -16.6271 | 47.1993 | 46.7417 | 46.2564 | 45.5964 | 44.8057 | 43.7389 | 42.4707 | 40.8431 | 38.709 | 36.3257 | 31.4664 | 19.8471 | 12.0079 | 5.7062 | 46.5332 | 46.1506 | 45.5513 | 44.6818 | 43.6209 | 42.2077 | 40.4761 | 38.2796 | 35.3371 | 31.9401 | 24.4705 | 7.9619 | -2.083 | -7.9689
|  |  | LW |  |  | 39.9564 | 38.8317 | 37.766 | 36.583 | 35.1212 | 33.5269 | 31.3297 | 28.6872 | 25.3674 | 21.6537 | 13.3941 | -1.9183 | -9.2381 | -12.0828 | 47.0067 | 46.4355 | 45.896 | 45.27 | 44.4761 | 43.5916 | 42.2957 | 40.7333 | 38.8049 | 36.6333 | 31.7928 | 21.821 | 16.3991 | 13.5112 | 46.3862 | 45.634 | 44.941 | 44.1701 | 43.2295 | 42.2045 | 40.5154 | 37.8852 | 34.6945 | 31.1139 | 23.1372 | 8.4502 | 1.1806 | -2.0468
|  |  | ST |  |  | 41.1718 | 40.8036 | 40.4526 | 39.731 | 38.9475 | 38.0451 | 36.9047 | 35.6535 | 33.9937 | 32.0658 | 27.0932 | 11.0531 | -0.92564 | -7.579 | 47.4728 | 47.2286 | 46.9782 | 46.3893 | 45.7963 | 45.1231 | 44.243 | 43.3615 | 42.1686 | 40.8276 | 37.4012 | 25.3906 | 14.6465 | 7.742 | 46.7115 | 46.6177 | 46.531 | 46.1297 | 45.5513 | 44.9174 | 44.1107 | 43.3446 | 42.2855 | 40.5543 | 35.6027 | 19.622 | 7.5709 | 1.008
|  |  | FS |  |  | 40.6491 | 39.9247 | 39.1676 | 38.0695 | 36.7945 | 35.1409 | 33.2489 | 30.7059 | 27.2377 | 23.5535 | 16.1008 | -1.2381 | -11.2109 | -16.6271 | 47.4876 | 47.239 | 46.9803 | 46.5708 | 46.0975 | 45.5161 | 44.8374 | 44.0175 | 42.9808 | 41.8097 | 38.8763 | 26.9699 | 17.2717 | 6.955 | 46.6767 | 46.5547 | 46.4266 | 46.0741 | 45.4315 | 44.6344 | 43.6577 | 42.4464 | 40.8686 | 38.9653 | 33.8657 | 16.363 | 5.401 | 1.2332
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER BSP | MINIMUM HEADROOM | SU 35334 46598 | YES | 29.1001 | 26.3306 | 23.4565 | 106.6897 | 101.8882 | 95.987 | 86.8192 | 76.0452 | 63.7592 | 50.3238 | 20.5127 | -38.7626 | -73.5476 | -93.0865 | 32.7432 | 30.4166 | 28.0299 | 111.3847 | 107.6729 | 102.4256 | 96.4347 | 88.0732 | 77.6441 | 67.1469 | 46.4533 | -1.0485 | -25.2477 | -50.2788 | 23.3456 | 20.1656 | 16.9029 | 99.3138 | 94.131 | 88.5117 | 79.6426 | 69.0511 | 57.0459 | 43.7942 | 14.3367 | -42.1252 | -72.971 | -91.7719
|  |  | CT |  |  | 30.241 | 28.3544 | 25.9996 | 108.8545 | 104.0121 | 97.1492 | 89.431 | 78.6438 | 64.9948 | 51.3388 | 24.2547 | -38.7626 | -73.5476 | -93.0865 | 32.8535 | 30.6986 | 28.1415 | 111.3847 | 107.6913 | 102.4256 | 96.4347 | 88.0732 | 77.6441 | 67.1469 | 46.4533 | -1.0485 | -25.2477 | -40.7933 | 23.9024 | 21.2426 | 18.0788 | 100.4361 | 95.7523 | 89.0601 | 81.5031 | 70.9077 | 57.5614 | 44.1725 | 17.8394 | -42.1252 | -72.971 | -91.7719
|  |  | LW |  |  | 29.1001 | 26.3306 | 23.4565 | 106.6897 | 101.8882 | 95.987 | 86.8192 | 76.0452 | 63.7592 | 50.3238 | 20.5127 | -32.6388 | -50.0505 | -46.1658 | 32.7432 | 30.4166 | 28.0299 | 111.5137 | 107.6729 | 103.4797 | 96.7764 | 88.8231 | 79.7394 | 69.5841 | 46.9049 | 8.2901 | -2.9951 | 0.99083 | 23.3456 | 20.1656 | 16.9029 | 99.3138 | 94.131 | 88.5117 | 79.6426 | 69.0511 | 57.0459 | 43.7942 | 14.3367 | -36.7076 | -52.2996 | -48.0678
|  |  | ST |  |  | 30.8927 | 30.2845 | 29.5419 | 114.5308 | 112.3958 | 109.4396 | 105.17 | 100.3041 | 94.4845 | 87.6349 | 69.1837 | 8.7225 | -31.1389 | -45.3318 | 34.0381 | 33.0033 | 31.7296 | 116.1147 | 113.744 | 110.9314 | 107.3949 | 103.4979 | 98.6615 | 93.0095 | 77.7851 | 28.199 | -6.2054 | -22.1531 | 25.5325 | 24.3756 | 22.917 | 106.9914 | 104.1939 | 100.835 | 96.5893 | 91.7848 | 86.0053 | 79.2025 | 60.8553 | 0.93735 | -38.5162 | -52.2254
|  |  | FS |  |  | 30.241 | 28.3544 | 25.9996 | 108.8545 | 104.0121 | 97.1492 | 89.431 | 78.6438 | 64.9948 | 51.3388 | 24.2547 | -38.7626 | -73.5476 | -93.0865 | 34.0497 | 33.0124 | 31.7406 | 116.4375 | 114.3147 | 111.7229 | 108.4867 | 104.5784 | 100.0193 | 94.8122 | 81.4314 | 35.9266 | -13.5881 | -50.2788 | 25.5763 | 24.4492 | 23.0488 | 107.4378 | 104.922 | 101.8503 | 98.0054 | 93.3305 | 87.878 | 81.6578 | 65.646 | 11.2038 | -44.1061 | -76.1441
MANNINGTON GSP | ARNEWOOD | ARNEWOOD | MINIMUM HEADROOM | SZ 26094 97294 | YES | 8.2068 | 6.0586 | 3.8253 | 0.34971 | -3.8387 | -8.2164 | -14.6687 | -22.1514 | -30.7798 | -40.2326 | -60.5825 | -95.7214 | -113.0492 | -121.8847 | 17.4348 | 16.0569 | 14.6522 | 12.7233 | 10.2398 | 7.6218 | 3.3069 | -1.9021 | -7.8485 | -14.4823 | -28.9268 | -53.3493 | -69.4995 | -82.381 | 6.8131 | 4.874 | 2.8726 | -0.27571 | -4.0568 | -8.0294 | -13.8383 | -20.854 | -29.1478 | -38.2699 | -57.9522 | -91.635 | -107.5831 | -115.783
|  |  | CT |  |  | 9.238 | 7.8479 | 6.084 | 3.1046 | -0.13715 | -4.5406 | -9.3284 | -15.8974 | -24.9075 | -33.7464 | -50.4388 | -91.8462 | -113.0492 | -121.8847 | 17.5871 | 16.4363 | 15.0047 | 13.067 | 10.9342 | 7.8292 | 4.403 | -0.54413 | -6.8282 | -13.0029 | -24.6322 | -53.3493 | -69.4995 | -81.0004 | 7.8072 | 6.5826 | 5.043 | 2.3894 | -0.50073 | -4.4434 | -9.0024 | -15.3572 | -23.9819 | -32.4469 | -48.4147 | -87.7983 | -107.5831 | -115.783
|  |  | LW |  |  | 8.2068 | 6.0586 | 3.8253 | 0.34971 | -3.8387 | -8.2164 | -14.6687 | -22.1514 | -30.7798 | -40.2326 | -60.5825 | -95.7214 | -107.8752 | -105.0977 | 17.4348 | 16.0569 | 14.6522 | 12.7233 | 10.2398 | 7.6218 | 3.3069 | -1.9021 | -7.8485 | -14.4823 | -28.9268 | -52.7964 | -60.0584 | -57.4306 | 6.8131 | 4.874 | 2.8726 | -0.27571 | -4.0568 | -8.0294 | -13.8383 | -20.854 | -29.1478 | -38.2699 | -57.9522 | -91.635 | -103.0109 | -100.1372
|  |  | ST |  |  | 10.3021 | 9.8468 | 9.1423 | 8.04 | 6.6507 | 4.9132 | 2.7001 | 0.056627 | -3.0297 | -6.8309 | -17.0043 | -51.8547 | -78.2358 | -92.8563 | 18.3225 | 17.8803 | 17.2503 | 16.3507 | 15.2089 | 13.7607 | 11.8898 | 9.6263 | 6.9363 | 3.6334 | -5.2175 | -34.389 | -56.8977 | -70.8197 | 8.7679 | 8.3755 | 7.7796 | 6.8446 | 5.6644 | 4.1783 | 2.2697 | -0.20861 | -3.2552 | -7.0139 | -17.1181 | -51.9785 | -77.7904 | -90.7371
|  |  | FS |  |  | 9.238 | 7.8479 | 6.084 | 3.1046 | -0.13715 | -4.5406 | -9.3284 | -15.8974 | -24.9075 | -33.7464 | -50.4388 | -91.8462 | -113.0492 | -121.8847 | 18.3602 | 17.9475 | 17.3885 | 16.6228 | 15.6725 | 14.5251 | 13.106 | 11.4358 | 9.4005 | 7.0341 | 0.69907 | -23.728 | -54.4978 | -82.381 | 8.8203 | 8.4834 | 7.9962 | 7.1606 | 6.1349 | 4.9211 | 3.4497 | 1.7504 | -0.48569 | -3.2121 | -10.4068 | -38.1668 | -70.3065 | -92.1777
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE T1A & T2A | MINIMUM HEADROOM | SU 65132 52710 | YES | 24.1726 | 23.8478 | 23.2824 | 21.9854 | 20.4304 | 18.9744 | 17.1882 | 14.5179 | 10.8175 | 6.5746 | -2.6262 | -17.5746 | -31.6917 | -37.7274 | 20.7379 | 20.3796 | 19.9975 | 19.2314 | 18.3331 | 17.383 | 16.32 | 14.9596 | 13.4664 | 11.8362 | 6.2419 | -3.9362 | -13.9131 | -18.2372 | 21.5255 | 21.1338 | 20.7129 | 20.0745 | 19.1736 | 18.1702 | 16.8527 | 14.16 | 10.6367 | 6.5902 | -2.1831 | -16.3636 | -29.606 | -35.2904
|  |  | CT |  |  | 24.2103 | 23.9905 | 23.6251 | 22.7843 | 21.7377 | 20.4598 | 19.1453 | 17.1747 | 14.778 | 11.6167 | 4.5913 | -16.2189 | -31.6917 | -37.7274 | 20.9025 | 20.6763 | 20.3607 | 19.6062 | 18.8166 | 17.942 | 17.178 | 16.0157 | 14.5338 | 13.0134 | 10.217 | -2.7159 | -13.9131 | -18.2372 | 21.5554 | 21.2809 | 20.9076 | 20.3228 | 19.5654 | 18.6862 | 17.8329 | 16.5041 | 14.5078 | 11.4135 | 4.7578 | -14.9552 | -29.606 | -35.2904
|  |  | LW |  |  | 24.1726 | 23.8478 | 23.2824 | 21.9854 | 20.4304 | 18.9744 | 17.1882 | 14.5179 | 10.8175 | 6.5746 | -2.6262 | -17.5746 | -21.7454 | -23.5763 | 20.7379 | 20.3796 | 19.9975 | 19.2314 | 18.3331 | 17.383 | 16.32 | 14.9596 | 13.4664 | 11.8362 | 6.2419 | -3.9362 | -6.6609 | -7.9376 | 21.5255 | 21.1338 | 20.7129 | 20.0745 | 19.1736 | 18.1702 | 16.8527 | 14.16 | 10.6367 | 6.5902 | -2.1831 | -16.3636 | -20.2461 | -21.9473
|  |  | ST |  |  | 24.4123 | 24.3527 | 24.1957 | 23.752 | 23.242 | 22.8056 | 22.4145 | 21.6056 | 20.6945 | 19.6179 | 17.2051 | 10.3316 | 5.7774 | 1.6426 | 21.0928 | 21.0137 | 20.8536 | 20.3329 | 19.8192 | 19.3149 | 18.9323 | 18.3383 | 17.7267 | 17.0307 | 15.7289 | 10.5091 | 4.5367 | -1.4391 | 21.8177 | 21.7477 | 21.5938 | 21.1779 | 20.638 | 20.1509 | 19.7318 | 19.1175 | 18.4507 | 17.6736 | 16.0493 | 10.7911 | 7.789 | 5.3011
|  |  | FS |  |  | 24.2103 | 23.9905 | 23.6251 | 22.7843 | 21.7377 | 20.4598 | 19.1453 | 17.1747 | 14.778 | 11.6167 | 4.5913 | -16.2189 | -31.6917 | -37.7274 | 21.0909 | 20.9443 | 20.7495 | 20.3969 | 19.9857 | 19.5516 | 19.1128 | 18.5631 | 17.9072 | 17.1702 | 15.4455 | 9.1782 | -0.18451 | -11.6789 | 21.83 | 21.7263 | 21.559 | 21.2853 | 20.9136 | 20.5337 | 20.1275 | 19.6104 | 19.0261 | 18.3417 | 16.7318 | 11.4896 | 5.4583 | 0.46984
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BASINGSTOKE T1B & T2B | MINIMUM HEADROOM | SU 65132 52711 | YES | 29.2266 | 27.3639 | 25.3653 | 22.1731 | 18.4464 | 14.4697 | 9.788 | 4.5582 | -1.5106 | -8.2666 | -23.4233 | -52.4796 | -67.5046 | -75.6519 | 34.1352 | 33.0092 | 31.8426 | 30 | 27.6716 | 25.111 | 21.7373 | 17.8805 | 13.6281 | 8.8403 | -1.6373 | -24.393 | -46.0093 | -64.4904 | 23.2158 | 21.4631 | 19.6407 | 16.7343 | 13.2352 | 9.4508 | 4.6969 | -0.69259 | -6.8194 | -13.6041 | -28.2043 | -55.887 | -74.9199 | -89.6725
|  |  | CT |  |  | 30.2732 | 29.0736 | 27.6694 | 25.5409 | 22.9601 | 19.8485 | 16.4338 | 12.0124 | 5.873 | -0.7282 | -13.7628 | -45.8106 | -62.9 | -70.8839 | 34.399 | 33.443 | 32.3368 | 30.8309 | 28.8984 | 26.5893 | 23.9541 | 20.5907 | 16.2328 | 11.5772 | 2.4001 | -20.4066 | -34.3161 | -46.357 | 24.1918 | 23.0718 | 21.7697 | 19.6323 | 17.0082 | 13.9105 | 10.4801 | 6.1331 | 0.0011888 | -6.424 | -18.8854 | -49.2721 | -65.1109 | -72.5179
|  |  | LW |  |  | 29.2266 | 27.3639 | 25.3653 | 22.1731 | 18.4464 | 14.4697 | 9.788 | 4.5582 | -1.5106 | -8.2666 | -23.4233 | -52.4796 | -67.5046 | -75.6519 | 34.1352 | 33.0092 | 31.8426 | 30 | 27.6716 | 25.111 | 21.7373 | 17.8805 | 13.6281 | 8.8403 | -1.6373 | -24.393 | -37.9358 | -44.7519 | 23.2158 | 21.4631 | 19.6407 | 16.7343 | 13.2352 | 9.4508 | 4.6969 | -0.69259 | -6.8194 | -13.6041 | -28.2043 | -55.887 | -69.9385 | -78.1386
|  |  | ST |  |  | 30.8739 | 30.1874 | 29.3647 | 28.0821 | 26.5662 | 25.0267 | 23.1667 | 21.187 | 18.8779 | 16.1302 | 9.1382 | -15.77 | -34.1103 | -44.5912 | 34.807 | 34.2166 | 33.5283 | 32.2787 | 30.8458 | 29.4426 | 27.6829 | 25.9303 | 23.8789 | 21.4837 | 15.3747 | -5.5787 | -22.6551 | -36.41 | 24.7907 | 24.1714 | 23.435 | 22.095 | 20.5372 | 19.0063 | 17.1184 | 15.1951 | 12.9441 | 10.2906 | 3.5228 | -20.4738 | -38.4208 | -49.3449
|  |  | FS |  |  | 30.2732 | 29.0736 | 27.6694 | 25.5409 | 22.9601 | 19.8485 | 16.4338 | 12.0124 | 5.873 | -0.7282 | -13.7628 | -45.8106 | -62.9 | -70.8839 | 34.6572 | 33.9447 | 33.0963 | 32.0641 | 30.7688 | 29.2379 | 27.4099 | 25.1857 | 22.4914 | 19.4282 | 11.9708 | -22.7019 | -46.0093 | -64.4904 | 24.6589 | 23.9507 | 23.0992 | 21.912 | 20.4342 | 18.6862 | 16.6217 | 14.0949 | 10.9462 | 7.4045 | -1.1036 | -44.9306 | -74.9199 | -89.6725
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BASINGSTOKE T3 & T4 | MINIMUM HEADROOM | SU 65132 52712 | YES | 57.3828 | 55.9058 | 54.207 | 51.8057 | 49.3386 | 46.6391 | 42.91 | 38.5987 | 33.8158 | 28.7608 | 18.5754 | 1.5482 | -13.616 | -24.5223 | 59.8133 | 58.95 | 57.9872 | 56.6409 | 55.1781 | 53.3229 | 51.2125 | 48.3456 | 44.8359 | 41.3011 | 34.5332 | 18.7149 | 5.4835 | -19.5446 | 52.1068 | 50.8132 | 49.3618 | 47.2992 | 45.0777 | 42.6658 | 39.2682 | 35.3022 | 30.9053 | 26.2141 | 16.6073 | 0.36586 | -14.7452 | -25.1046
|  |  | CT |  |  | 57.8467 | 56.7423 | 55.3109 | 53.1414 | 51.0832 | 48.3649 | 45.3241 | 41.2738 | 36.149 | 31.0669 | 21.6596 | 1.7359 | -13.616 | -24.5223 | 59.8384 | 59.0409 | 58.0306 | 56.6409 | 55.2085 | 53.3229 | 51.2125 | 48.3456 | 44.8359 | 41.3011 | 34.5332 | 18.7149 | 7.3815 | -4.1521 | 52.4922 | 51.5243 | 50.2829 | 48.4125 | 46.5386 | 44.084 | 41.3212 | 37.5887 | 32.8671 | 28.1715 | 19.4016 | 0.52941 | -14.7452 | -25.1046
|  |  | LW |  |  | 57.3828 | 55.9058 | 54.207 | 51.8057 | 49.3386 | 46.6391 | 42.91 | 38.5987 | 33.8158 | 28.7608 | 18.5754 | 1.5482 | -5.6595 | -8.3452 | 59.8133 | 58.95 | 57.9872 | 56.6557 | 55.1781 | 53.571 | 51.2154 | 48.4375 | 45.3943 | 42.0912 | 35.1971 | 23.5367 | 15.2907 | 13.2724 | 52.1068 | 50.8132 | 49.3618 | 47.2992 | 45.0777 | 42.6658 | 39.2682 | 35.3022 | 30.9053 | 26.2141 | 16.6073 | 0.36586 | -7.2974 | -9.8831
|  |  | ST |  |  | 58.4626 | 57.8426 | 56.9519 | 55.6079 | 54.4171 | 53.027 | 51.407 | 49.5267 | 47.4466 | 45.0906 | 39.6123 | 23.3929 | 12.5218 | 7.1507 | 60.224 | 59.7631 | 59.1334 | 58.1741 | 57.211 | 56.1307 | 54.8514 | 53.3793 | 51.7095 | 49.7788 | 45.0769 | 30.1858 | 17.7448 | 6.448 | 53.0699 | 52.5651 | 51.8422 | 50.7192 | 49.6391 | 48.4219 | 46.9699 | 45.2786 | 43.3904 | 41.2105 | 35.944 | 19.9196 | 9.4198 | 4.5993
|  |  | FS |  |  | 57.8467 | 56.7423 | 55.3109 | 53.1414 | 51.0832 | 48.3649 | 45.3241 | 41.2738 | 36.149 | 31.0669 | 21.6596 | 1.7359 | -13.616 | -24.5223 | 60.1674 | 59.6909 | 59.0544 | 58.1655 | 57.2348 | 56.1422 | 54.8395 | 53.3368 | 51.6064 | 49.6359 | 44.7578 | 27.5089 | 5.4835 | -19.5446 | 53.0228 | 52.5477 | 51.8819 | 50.8692 | 49.8558 | 48.6593 | 47.2354 | 45.5948 | 43.7645 | 41.6988 | 36.6524 | 19.5376 | 1.9905 | -8.5582
EAST CLAYDON GSP | BICESTER NORTH | BICESTER NORTH | MINIMUM HEADROOM | SP5972023735 | YES | 31.05 | 31.05 | 31.05 | 30.5471 | 30.1284 | 29.4736 | 28.761 | 28.1647 | 27.8572 | 27.5384 | 26.9806 | 31.05 | 31.05 | 23.7055 | 28.8 | 28.8 | 28.8 | 28.1714 | 27.648 | 26.8295 | 25.9388 | 25.1933 | 24.809 | 24.4104 | 23.7133 | 28.8 | 28.8 | 19.6194 | 28.8 | 28.8 | 28.8 | 28.1714 | 27.648 | 26.8295 | 25.9388 | 25.1933 | 24.809 | 24.4104 | 23.7133 | 28.8 | 28.8 | 19.6194
|  |  | CT |  |  | 31.05 | 31.05 | 31.05 | 30.9822 | 30.8618 | 30.7187 | 30.4612 | 30.3046 | 30.2088 | 29.9957 | 29.6088 | 31.05 | 31.05 | 27.5707 | 28.8 | 28.8 | 28.8 | 28.7152 | 28.5648 | 28.3858 | 28.0639 | 27.8683 | 27.7485 | 27.4821 | 26.9984 | 28.8 | 28.8 | 24.4509 | 28.8 | 28.8 | 28.8 | 28.7152 | 28.5648 | 28.3858 | 28.0639 | 27.8683 | 27.7485 | 27.4821 | 26.9984 | 28.8 | 28.8 | 24.4509
|  |  | LW |  |  | 31.05 | 31.05 | 31.05 | 30.6145 | 30.1284 | 29.4736 | 28.761 | 28.1647 | 27.8572 | 27.5384 | 26.9806 | 31.05 | 31.05 | 23.7055 | 28.8 | 28.8 | 28.8 | 28.2556 | 27.648 | 26.8295 | 25.9388 | 25.1933 | 24.809 | 24.4104 | 23.7133 | 28.8 | 28.8 | 19.6194 | 28.8 | 28.8 | 28.8 | 28.2556 | 27.648 | 26.8295 | 25.9388 | 25.1933 | 24.809 | 24.4104 | 23.7133 | 28.8 | 28.8 | 19.6194
|  |  | ST |  |  | 31.05 | 31.05 | 31.05 | 30.5471 | 30.2071 | 29.9008 | 29.4349 | 29.2201 | 29.0165 | 28.8431 | 28.4617 | 31.05 | 31.05 | 25.8521 | 28.8 | 28.8 | 28.8 | 28.1714 | 27.7464 | 27.3635 | 26.7811 | 26.5127 | 26.2582 | 26.0414 | 25.5646 | 28.8 | 28.8 | 22.3026 | 28.8 | 28.8 | 28.8 | 28.1714 | 27.7464 | 27.3635 | 26.7811 | 26.5127 | 26.2582 | 26.0414 | 25.5646 | 28.8 | 28.8 | 22.3026
|  |  | FS |  |  | 31.05 | 31.05 | 31.05 | 30.9822 | 30.8618 | 30.7187 | 30.4612 | 30.3046 | 30.2088 | 29.9957 | 29.6088 | 31.05 | 31.05 | 27.5707 | 28.8 | 28.8 | 28.8 | 28.6628 | 28.5256 | 28.36 | 28.1943 | 28.0571 | 27.9588 | 27.8639 | 27.6741 | 28.8 | 28.8 | 27.2283 | 28.8 | 28.8 | 28.8 | 28.6628 | 28.5256 | 28.36 | 28.1943 | 28.0571 | 27.9588 | 27.8639 | 27.6741 | 28.8 | 28.8 | 27.2283
EALING GSP | BOSTON MANOR ROAD | BOSTON MANOR ROAD | MINIMUM HEADROOM | TQ 17043 78092 | YES | 13.8327 | 13.6001 | 13.2932 | 13.0017 | 12.6998 | 12.2769 | 11.5854 | 10.8105 | 9.7985 | 8.6821 | 6.2938 | 9.8242 | 9.1559 | 8.7461 | 8.9814 | 8.7575 | 8.5194 | 8.3186 | 8.0727 | 7.8096 | 7.5169 | 7.1512 | 6.7614 | 6.3559 | 5.8962 | 6.3559 | 5.8962 | 5.6246 | 13.2246 | 12.6226 | 12.1686 | 11.6517 | 11.3025 | 10.9789 | 10.4263 | 9.509 | 8.5251 | 7.4373 | 5.1056 | 10.416 | 9.7696 | 9.4052
|  |  | CT |  |  | 13.8327 | 13.6001 | 13.2932 | 13.0017 | 12.6998 | 12.399 | 12.0213 | 11.5722 | 11.0731 | 10.4704 | 9.7844 | 10.4704 | 9.7844 | 9.4227 | 8.9814 | 8.7575 | 8.5194 | 8.3186 | 8.0727 | 7.8096 | 7.5169 | 7.1512 | 6.7614 | 6.3559 | 5.8962 | 6.3559 | 5.8962 | 5.6246 | 14.0308 | 13.7957 | 13.5388 | 13.3284 | 13.1157 | 12.8732 | 12.539 | 12.0541 | 11.5391 | 10.9541 | 10.3021 | 10.9541 | 10.3021 | 9.9785
|  |  | LW |  |  | 15.0152 | 14.4957 | 14.0093 | 13.277 | 12.767 | 12.2769 | 11.5854 | 10.8105 | 9.7985 | 8.6821 | 6.2938 | 9.8242 | 9.1559 | 8.7461 | 12.2919 | 11.7247 | 11.3387 | 10.9268 | 10.6345 | 10.3719 | 9.9958 | 9.5452 | 8.9816 | 8.257 | 6.7002 | 6.5717 | 6.2086 | 5.9612 | 13.2246 | 12.6226 | 12.1686 | 11.6517 | 11.3025 | 10.9789 | 10.4263 | 9.509 | 8.5251 | 7.4373 | 5.1056 | 10.416 | 9.7696 | 9.4052
|  |  | ST |  |  | 15.2497 | 14.9685 | 14.8019 | 14.6088 | 14.4934 | 14.2216 | 13.8075 | 13.3638 | 12.8991 | 12.3777 | 10.9345 | 11.7945 | 11.4548 | 11.2212 | 12.5557 | 12.2276 | 12.0291 | 11.7889 | 11.6151 | 11.3199 | 10.8811 | 10.4119 | 9.9009 | 9.3364 | 7.8489 | 7.1542 | 6.8265 | 6.6262 | 13.5522 | 13.244 | 13.0392 | 12.8075 | 12.6967 | 12.5002 | 12.175 | 11.8402 | 11.4991 | 10.9795 | 9.5232 | 12.4428 | 12.1286 | 11.9452
|  |  | FS |  |  | 13.8327 | 13.6001 | 13.2932 | 13.0017 | 12.6998 | 12.399 | 12.0213 | 11.5722 | 11.0731 | 10.4704 | 9.7844 | 10.4704 | 9.7844 | 9.4227 | 12.696 | 12.3316 | 12.047 | 11.7531 | 11.4753 | 11.1648 | 10.769 | 10.36 | 9.8435 | 9.2485 | 7.571 | 6.7258 | 6.4456 | 6.2159 | 13.6946 | 13.3761 | 13.1268 | 12.8818 | 12.6974 | 12.5151 | 12.2766 | 12.0504 | 11.7751 | 11.4593 | 10.3863 | 12.3069 | 12.2077 | 12.0302
BOTLEY WOOD GSP | BOTLEY WOOD BSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU 54073 09759 | YES | 60.4198 | 60.1987 | 59.9773 | 59.5066 | 59.0147 | 58.4293 | 57.7671 | 57.0519 | 56.1246 | 55.1583 | 53.1123 | 49.2079 | 46.278 | 44.4712 | 67.0953 | 66.9861 | 66.8824 | 66.6984 | 66.4935 | 66.2423 | 65.9365 | 65.5987 | 65.1387 | 64.4844 | 63.0487 | 60.4456 | 56.2738 | 50.2927 | 55.7849 | 55.5828 | 55.3811 | 54.9502 | 54.5 | 53.9775 | 53.3885 | 52.7524 | 51.9149 | 51.0434 | 49.2057 | 45.6721 | 42.8189 | 41.1273
|  |  | CT |  |  | 60.7333 | 60.6729 | 60.6081 | 60.3049 | 59.9876 | 59.5773 | 59.1199 | 58.6092 | 57.6528 | 56.6375 | 54.4973 | 49.5019 | 46.278 | 44.4712 | 67.1814 | 67.1095 | 67.0267 | 66.8741 | 66.6974 | 66.4374 | 66.1259 | 65.7211 | 65.1387 | 64.4844 | 63.0487 | 60.4456 | 57.9202 | 54.9581 | 56.0711 | 56.0154 | 55.9556 | 55.6764 | 55.3842 | 55.0163 | 54.6068 | 54.1473 | 53.274 | 52.3436 | 50.3883 | 45.7998 | 42.8189 | 41.1273
|  |  | LW |  |  | 60.4198 | 60.1987 | 59.9773 | 59.5066 | 59.0147 | 58.4293 | 57.7671 | 57.0519 | 56.1246 | 55.1583 | 53.1123 | 49.2079 | 46.85 | 45.5504 | 67.0953 | 66.9861 | 66.8824 | 66.6984 | 66.4935 | 66.2423 | 65.9365 | 65.5987 | 65.1438 | 64.6601 | 63.6169 | 61.6638 | 60.3769 | 59.3787 | 55.7849 | 55.5828 | 55.3811 | 54.9502 | 54.5 | 53.9775 | 53.3885 | 52.7524 | 51.9149 | 51.0434 | 49.2057 | 45.6721 | 43.4461 | 42.1457
|  |  | ST |  |  | 60.826 | 60.8185 | 60.805 | 60.7787 | 60.7462 | 60.6446 | 60.5226 | 60.3734 | 60.1799 | 59.9515 | 59.3788 | 57.2037 | 54.7452 | 51.8306 | 67.231 | 67.1911 | 67.142 | 67.0877 | 67.0225 | 66.9146 | 66.785 | 66.6308 | 66.4181 | 66.1744 | 65.5673 | 63.5064 | 61.0102 | 57.5414 | 56.1592 | 56.1543 | 56.1438 | 56.1215 | 56.0937 | 56.0137 | 55.9176 | 55.7976 | 55.6302 | 55.4342 | 54.9421 | 52.9243 | 50.6883 | 47.93
|  |  | FS |  |  | 60.7333 | 60.6729 | 60.6081 | 60.3049 | 59.9876 | 59.5773 | 59.1199 | 58.6092 | 57.6528 | 56.6375 | 54.4973 | 49.5019 | 46.278 | 44.4712 | 67.192 | 67.1259 | 67.0464 | 66.9486 | 66.8305 | 66.6682 | 66.4658 | 66.2265 | 65.8907 | 65.5015 | 64.5102 | 60.9419 | 56.2738 | 50.2927 | 56.1226 | 56.0977 | 56.0689 | 55.9817 | 55.8803 | 55.7363 | 55.5579 | 55.352 | 55.0341 | 54.6515 | 53.6362 | 50.0631 | 46.321 | 43.3964
MANNINGTON GSP | BOURNEMOUTH | BOURNEMOUTH | MINIMUM HEADROOM | SZ 06265 92437 | YES | 8.4958 | 3.0125 | -2.3977 | -11.7526 | -23.2138 | -35.4937 | -52.6663 | -72.7263 | -95.7907 | -121.1241 | -174.7104 | -132.3083 | -185.6545 | -348.4456 | 33.2029 | 29.3523 | 25.1271 | 18.8119 | 11.5284 | 1.6828 | -9.3578 | -24.4198 | -42.7915 | -61.438 | -97.8685 | -72.9967 | -141.6911 | -438.0239 | 10.0904 | 4.7627 | -0.5227 | -9.2439 | -19.8802 | -31.3486 | -47.7628 | -68.0044 | -90.4346 | -115.0793 | -167.3901 | -128.355 | -179.0531 | -332.7272
|  |  | CT |  |  | 11.3966 | 7.2285 | 2.3681 | -5.9073 | -15.2172 | -27.6763 | -41.4009 | -60.1909 | -84.2436 | -108.2798 | -153.8534 | -132.3083 | -185.6545 | -348.4456 | 33.2391 | 29.5361 | 25.1271 | 18.8119 | 11.5284 | 1.6828 | -9.3578 | -24.4198 | -42.7915 | -61.438 | -97.8685 | -72.9967 | -119.2726 | -330.4809 | 12.4365 | 8.8144 | 4.549 | -3.1808 | -11.9614 | -23.7268 | -37.2173 | -55.5992 | -78.9794 | -102.4269 | -147.1066 | -128.355 | -179.0531 | -332.7272
|  |  | LW |  |  | 8.4958 | 3.0125 | -2.3977 | -11.7526 | -23.2138 | -35.4937 | -52.6663 | -72.7263 | -95.7907 | -121.1241 | -174.7104 | -130.0165 | -155.4993 | -297.0899 | 33.2029 | 29.3523 | 25.5249 | 19.8607 | 12.5586 | 4.6092 | -7.7485 | -22.459 | -38.6685 | -56.6522 | -95.3305 | -67.7934 | -86.4602 | -185.0335 | 10.0904 | 4.7627 | -0.5227 | -9.2439 | -19.8802 | -31.3486 | -47.7628 | -68.0044 | -90.4346 | -115.0793 | -167.3901 | -126.2507 | -150.9301 | -284.5931
|  |  | ST |  |  | 14.6708 | 13.2533 | 11.4431 | 8.1821 | 3.9976 | -1.0115 | -7.3197 | -14.819 | -23.5439 | -34.0747 | -61.5087 | -44.4027 | -69.7124 | -254.2069 | 35.3748 | 33.5991 | 31.3665 | 27.8078 | 23.4151 | 18.2581 | 11.8409 | 4.4572 | -4.0169 | -14.0461 | -39.9756 | -37.6192 | -83.5209 | -284.5651 | 15.564 | 14.4437 | 12.9582 | 10.0672 | 6.327 | 1.8911 | -3.967 | -11.3679 | -19.9488 | -30.315 | -57.5535 | -39.381 | -64.0767 | -245.9578
|  |  | FS |  |  | 11.3966 | 7.2285 | 2.3681 | -5.9073 | -15.2172 | -27.6763 | -41.4009 | -60.1909 | -84.2436 | -108.2798 | -153.8534 | -132.3083 | -185.6545 | -348.4456 | 36.4533 | 32.7141 | 30.0682 | 26.2586 | 21.5662 | 15.8824 | 8.8292 | 0.24574 | -9.8648 | -21.4685 | -50.4732 | -63.7586 | -141.6911 | -438.0239 | 16.5307 | 13.5471 | 11.7585 | 8.5299 | 4.4664 | -0.53029 | -6.7979 | -14.9228 | -24.7103 | -35.8922 | -69.0661 | -79.8473 | -109.4337 | -311.809
BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL MAIN | MINIMUM HEADROOM | SU 86026 69422 | YES | 15.6887 | 13.8649 | 11.8385 | 8.0172 | 3.6541 | -1.6503 | -8.4078 | -15.7162 | -23.4961 | -31.3993 | -48.4643 | -76.8088 | -86.4295 | -89.1776 | 21.3512 | 20.2315 | 19.0024 | 16.732 | 14.0457 | 10.3471 | 5.4735 | 0.27585 | -4.9923 | -10.4479 | -22.0059 | -41.0322 | -53.5909 | -80.5825 | 14.1218 | 12.4647 | 10.6455 | 7.253 | 3.2809 | -1.7644 | -8.3105 | -15.3886 | -22.8216 | -30.4579 | -46.6126 | -73.4723 | -82.3913 | -87.7947
|  |  | CT |  |  | 16.6372 | 15.4839 | 13.9497 | 10.5302 | 6.9748 | 2.3519 | -2.8475 | -9.0625 | -16.9561 | -24.6221 | -39.4638 | -68.9671 | -82.6621 | -88.8423 | 21.5309 | 20.588 | 19.3276 | 16.9264 | 14.4351 | 10.8415 | 6.7401 | 1.9231 | -3.5261 | -8.8218 | -18.984 | -40.6839 | -53.5909 | -66.1107 | 14.8729 | 13.7859 | 12.3167 | 9.1885 | 5.8789 | 1.3749 | -3.7366 | -9.8367 | -17.2379 | -24.4112 | -38.181 | -65.907 | -78.5057 | -84.0629
|  |  | LW |  |  | 15.6887 | 13.8649 | 11.8385 | 8.0172 | 3.6541 | -1.6503 | -8.4078 | -15.7162 | -23.4961 | -31.3993 | -48.4643 | -76.8088 | -86.4295 | -89.1776 | 21.3512 | 20.2315 | 19.0024 | 16.732 | 14.0457 | 10.3471 | 5.4735 | 0.27585 | -4.9923 | -10.4479 | -22.0059 | -41.0322 | -51.6328 | -55.9029 | 14.1218 | 12.4647 | 10.6455 | 7.253 | 3.2809 | -1.7644 | -8.3105 | -15.3886 | -22.8216 | -30.4579 | -46.6126 | -73.4723 | -82.3913 | -87.7947
|  |  | ST |  |  | 17.3743 | 16.7986 | 15.8692 | 13.735 | 11.6183 | 9.0425 | 5.9947 | 2.7395 | -0.76085 | -4.5972 | -13.8105 | -38.7848 | -55.1739 | -64.0504 | 21.9957 | 21.4675 | 20.6596 | 18.8482 | 17.0246 | 14.6146 | 11.7222 | 8.7001 | 5.662 | 2.3865 | -5.3827 | -27.2014 | -43.9148 | -57.5247 | 15.5538 | 15.0413 | 14.19 | 12.1756 | 10.1173 | 7.5223 | 4.3928 | 1.0699 | -2.3418 | -6.0413 | -14.9236 | -39.4764 | -55.3139 | -62.8325
|  |  | FS |  |  | 16.6372 | 15.4839 | 13.9497 | 10.5302 | 6.9748 | 2.3519 | -2.8475 | -9.0625 | -16.9561 | -24.6221 | -39.4638 | -68.9671 | -82.6621 | -88.8423 | 21.9924 | 21.3948 | 20.6161 | 19.2864 | 17.7913 | 15.4525 | 12.7097 | 9.781 | 6.7419 | 3.5649 | -3.9226 | -26.5224 | -52.6886 | -80.5825 | 15.5717 | 15.0257 | 14.2768 | 12.7875 | 11.1212 | 8.6133 | 5.6685 | 2.5187 | -0.77739 | -4.2014 | -12.2571 | -35.773 | -58.7161 | -73.0802
BRAMLEY (FLEE) | BRACKNELL RESERVE | BRACKNELL RESERVE | MINIMUM HEADROOM | SU 86026 69422 | YES | 35.6413 | 33.476 | 31.1531 | 27.4644 | 23.3913 | 18.4803 | 11.6753 | 3.8519 | -4.8795 | -14.5356 | -45.7561 | -117.5232 | -149.2821 | -160.3769 | 44.1861 | 42.7907 | 41.2634 | 39.0785 | 36.5751 | 33.2965 | 28.4323 | 22.7745 | 16.6293 | 7.7527 | -17.8415 | -72.0148 | -95.7985 | -104.4368 | 31.7561 | 29.8112 | 27.6808 | 24.256 | 20.4343 | 15.6921 | 9.0566 | 1.4305 | -7.0446 | -16.4197 | -46.0439 | -114.7373 | -145.1057 | -155.8193
|  |  | CT |  |  | 36.6333 | 35.2089 | 33.2503 | 29.9761 | 26.979 | 22.3153 | 17.1678 | 10.3922 | 1.5095 | -7.4119 | -24.8651 | -66.9366 | -95.1802 | -108.8303 | 44.2996 | 43.0961 | 41.402 | 39.1315 | 37.0718 | 33.4885 | 29.4772 | 24.1225 | 17.6932 | 11.2601 | -1.2202 | -30.8539 | -51.7311 | -61.4662 | 32.7156 | 31.4067 | 29.4908 | 26.4408 | 23.6145 | 19.045 | 13.9926 | 7.3445 | -1.2554 | -9.8807 | -26.6974 | -66.88 | -92.7159 | -105.6469
|  |  | LW |  |  | 35.6413 | 33.476 | 31.1531 | 27.4644 | 23.3913 | 18.4803 | 11.6753 | 3.8519 | -4.8795 | -14.5356 | -45.7561 | -117.5232 | -149.2821 | -160.3769 | 44.1861 | 42.7907 | 41.2634 | 39.0785 | 36.5751 | 33.2965 | 28.4323 | 22.7745 | 16.6293 | 7.7527 | -17.8415 | -72.0148 | -95.7985 | -104.4368 | 31.7561 | 29.8112 | 27.6808 | 24.256 | 20.4343 | 15.6921 | 9.0566 | 1.4305 | -7.0446 | -16.4197 | -46.0439 | -114.7373 | -145.1057 | -155.8193
|  |  | ST |  |  | 37.6264 | 37.0758 | 36.0952 | 34.5653 | 33.3816 | 31.4078 | 28.9847 | 26.2342 | 23.2867 | 19.7396 | 10.442 | -21.287 | -44.4719 | -56.377 | 44.9951 | 44.4553 | 43.5184 | 42.1126 | 40.9825 | 39.0507 | 36.6818 | 34.0503 | 31.2191 | 27.8768 | 19.2625 | -8.1618 | -28.7587 | -41.6538 | 33.6212 | 33.1623 | 32.256 | 30.7925 | 29.6312 | 27.6047 | 25.1229 | 22.3365 | 19.3355 | 15.7539 | 6.3043 | -25.2476 | -47.8901 | -58.4605
|  |  | FS |  |  | 36.6333 | 35.2089 | 33.2503 | 29.9761 | 26.979 | 22.3153 | 17.1678 | 10.3922 | 1.5095 | -7.4119 | -24.8651 | -66.9366 | -95.1802 | -108.8303 | 44.8056 | 44.068 | 43.1069 | 41.8577 | 40.4886 | 38.3878 | 35.8188 | 32.7592 | 29.3886 | 25.6009 | 16.1173 | -15.1601 | -48.9077 | -76.5408 | 33.434 | 32.7904 | 31.8566 | 30.4697 | 28.9543 | 26.6537 | 23.8397 | 20.4673 | 16.6305 | 12.3314 | 1.6216 | -33.5339 | -68.925 | -90.3685
EALING GSP | BRIDGE ROAD | BRIDGE ROAD | MINIMUM HEADROOM | TQ 14778 75741 | YES | 38.5292 | 37.6133 | 36.6364 | 35.0562 | 33.3915 | 31.6036 | 29.4774 | 27.4379 | 25.3156 | 23.0915 | 18.4584 | 10.0229 | 5.2279 | 2.7892 | 44.4534 | 43.874 | 43.2422 | 42.1948 | 41.0635 | 39.6261 | 37.9935 | 36.1779 | 33.9924 | 31.7326 | 27.1664 | 10.1335 | -26.6699 | -93.648 | 35.6228 | 34.7754 | 33.9208 | 32.5279 | 31.0536 | 29.4826 | 27.5782 | 25.7046 | 23.7611 | 21.7143 | 17.4389 | 9.7337 | 5.4554 | 3.3803
|  |  | CT |  |  | 39.215 | 38.7931 | 38.1802 | 36.9317 | 35.6386 | 34.0087 | 32.2427 | 30.3546 | 27.9078 | 25.4835 | 20.9827 | 10.6458 | 5.2279 | 2.7892 | 44.5206 | 43.9587 | 43.2422 | 42.1948 | 41.0635 | 39.6261 | 37.9935 | 36.1779 | 33.9924 | 31.7326 | 27.1664 | 12.8648 | -7.0341 | -39.0852 | 36.2587 | 35.8874 | 35.3617 | 34.2713 | 33.1357 | 31.6805 | 30.078 | 28.3165 | 26.0577 | 23.8279 | 19.7347 | 10.2631 | 5.4554 | 3.3803
|  |  | LW |  |  | 38.5292 | 37.6133 | 36.6364 | 35.0562 | 33.3915 | 31.6036 | 29.4774 | 27.4379 | 25.3156 | 23.0915 | 18.4584 | 10.0229 | 7.0987 | 7.0384 | 44.4534 | 43.874 | 43.3305 | 42.5393 | 41.7055 | 40.8126 | 39.6884 | 38.5828 | 37.4443 | 36.2308 | 33.5784 | 28.6963 | 27.278 | 27.8998 | 35.6228 | 34.7754 | 33.9208 | 32.5279 | 31.0536 | 29.4826 | 27.5782 | 25.7046 | 23.7611 | 21.7143 | 17.4389 | 9.7337 | 7.2015 | 7.3855
|  |  | ST |  |  | 39.684 | 39.5599 | 39.2595 | 38.9091 | 38.5306 | 37.9861 | 37.3042 | 36.6869 | 36.0074 | 35.1039 | 32.9478 | 25.5354 | 19.7767 | 15.8748 | 44.7438 | 44.3386 | 43.7881 | 43.1008 | 42.3437 | 41.3885 | 40.2261 | 39.0266 | 37.6795 | 36.1457 | 32.4936 | 18.831 | -1.5545 | -34.352 | 36.6841 | 36.5886 | 36.3532 | 36.0533 | 35.7264 | 35.2456 | 34.6117 | 34.0111 | 33.3613 | 32.5811 | 30.5717 | 23.3772 | 17.9679 | 14.6483
|  |  | FS |  |  | 39.215 | 38.7931 | 38.1802 | 36.9317 | 35.6386 | 34.0087 | 32.2427 | 30.3546 | 27.9078 | 25.4835 | 20.9827 | 10.6458 | 5.2279 | 2.7892 | 44.7683 | 44.1813 | 43.514 | 42.6353 | 41.6213 | 40.4729 | 39.1153 | 37.6967 | 35.9374 | 33.9364 | 29.1152 | 10.1335 | -26.6699 | -93.648 | 36.7215 | 36.5288 | 36.2942 | 35.9402 | 35.5363 | 35.0647 | 34.502 | 34.0032 | 33.384 | 32.7043 | 31.1409 | 25.5926 | 17.9928 | 11.7996
BRAMLEY (FLEE) | BURGHFIELD MAIN | BURGHFIELD MAIN | MINIMUM HEADROOM | SU 69442 70509 | YES | 13.1846 | 9.7386 | 6.202 | 1.1773 | -4.3636 | -10.4814 | -18.2713 | -27.8257 | -38.4905 | -56.2287 | -102.3838 | -203.0218 | -257.3255 | -285.1829 | 25.1487 | 22.8965 | 20.4472 | 17.2907 | 13.9637 | 9.3289 | 4.0041 | -3.4533 | -12.6728 | -25.2354 | -60.2422 | -135.5075 | -176.0266 | -197.4573 | 14.8121 | 11.8174 | 8.6179 | 4.0036 | -1.1114 | -6.7866 | -14.0786 | -23.13 | -33.39 | -45.0321 | -87.0659 | -183.1732 | -235.1097 | -261.9915
|  |  | CT |  |  | 14.4749 | 11.7349 | 8.548 | 4.0639 | -0.56601 | -6.9458 | -14.1125 | -23.8788 | -36.8078 | -56.2287 | -102.3838 | -203.0218 | -257.3255 | -285.1829 | 25.3038 | 23.0883 | 20.4472 | 17.2907 | 14.0492 | 9.3289 | 4.0041 | -3.4533 | -12.6728 | -25.2354 | -60.2422 | -135.5075 | -176.0266 | -197.4573 | 15.9855 | 13.5156 | 10.5692 | 6.3942 | 2.1135 | -3.8393 | -10.4199 | -19.7944 | -31.883 | -44.948 | -87.0659 | -183.1732 | -235.1097 | -261.9915
|  |  | LW |  |  | 13.1846 | 9.7386 | 6.202 | 1.1773 | -4.3636 | -10.4814 | -18.2713 | -27.8257 | -38.4905 | -50.5344 | -77.1822 | -123.6831 | -140.2686 | -142.6221 | 25.1487 | 22.8965 | 20.5485 | 17.4932 | 13.9637 | 9.921 | 4.3885 | -2.3571 | -9.8276 | -18.462 | -37.8638 | -70.5349 | -81.8018 | -83.9024 | 14.8121 | 11.8174 | 8.6179 | 4.0036 | -1.1114 | -6.7866 | -14.0786 | -23.13 | -33.39 | -45.0321 | -70.8823 | -115.6809 | -131.6734 | -134.2291
|  |  | ST |  |  | 15.6633 | 13.9195 | 11.9041 | 9.7765 | 7.8018 | 5.0454 | 1.8137 | -2.2943 | -6.8964 | -12.6353 | -27.3126 | -76.6961 | -110.5531 | -124.4987 | 26.0623 | 24.5747 | 22.8094 | 20.8299 | 18.957 | 16.4694 | 13.6057 | 9.9854 | 5.8515 | 0.72532 | -12.3928 | -55.4607 | -88.0245 | -108.9939 | 17.0854 | 15.594 | 13.7775 | 11.7406 | 9.894 | 7.3765 | 4.5034 | 0.53644 | -3.9716 | -9.6026 | -24.1209 | -72.9019 | -106.6404 | -119.47
|  |  | FS |  |  | 14.4749 | 11.7349 | 8.548 | 4.0639 | -0.56601 | -6.9458 | -14.1125 | -23.8788 | -36.8078 | -56.2287 | -102.3838 | -203.0218 | -257.3255 | -285.1829 | 26.1746 | 24.8836 | 23.3877 | 21.6647 | 19.8097 | 17.552 | 14.9609 | 11.7659 | 8.0058 | 3.6582 | -7.3864 | -47.634 | -96.8552 | -143.3794 | 17.2524 | 16.0538 | 14.6277 | 12.7996 | 10.8901 | 8.5664 | 5.9593 | 2.5701 | -1.5412 | -6.2513 | -18.1749 | -61.4491 | -109.0407 | -138.8145
BRAMLEY (FLEE) | BURGHFIELD RESERVE | BURGHFIELD RESERVE | MINIMUM HEADROOM | SU 69442 70509 | YES | 37.8898 | 37.1457 | 36.5092 | 35.2045 | 32.7004 | 29.6783 | 26.2257 | 22.2656 | 17.3032 | 9.0609 | -10.7423 | -92.3978 | -120.6944 | -70.6248 | 39.1819 | 38.2894 | 37.4925 | 36.2413 | 34.6989 | 32.7524 | 30.5281 | 27.981 | 23.5899 | 16.8053 | 1.4097 | -60.4414 | -81.5847 | -43.6569 | 38.2632 | 36.9164 | 35.6425 | 33.6853 | 31.324 | 28.4588 | 25.1967 | 21.4732 | 16.8343 | 9.0365 | -10.4601 | -88.7967 | -116.0568 | -68.5415
|  |  | CT |  |  | 38.1278 | 37.4485 | 36.8727 | 36.0682 | 34.9364 | 32.8937 | 29.5404 | 24.186 | 17.3032 | 9.0609 | -10.7423 | -92.3978 | -120.6944 | -70.6248 | 39.5664 | 38.7876 | 38.1336 | 37.0916 | 35.6962 | 33.7897 | 31.6569 | 28.8349 | 23.5899 | 16.8053 | 1.4097 | -60.4414 | -81.5847 | -43.6569 | 39.1831 | 38.2887 | 37.4756 | 35.992 | 34.0673 | 31.5281 | 28.6521 | 24.8726 | 17.6608 | 9.0365 | -10.4601 | -88.7967 | -116.0568 | -68.5415
|  |  | LW |  |  | 37.8898 | 37.1457 | 36.5092 | 35.2045 | 32.7004 | 29.6783 | 26.2257 | 22.2656 | 17.4596 | 11.9006 | -3.7562 | -82.5012 | -114.1503 | -65.306 | 39.1819 | 38.2894 | 37.4925 | 36.2413 | 34.6989 | 32.7524 | 30.5281 | 27.981 | 24.9259 | 19.8848 | 7.3317 | -52.6726 | -77.6524 | -41.6893 | 38.2632 | 36.9164 | 35.6425 | 33.6853 | 31.324 | 28.4588 | 25.1967 | 21.4732 | 16.8343 | 11.45 | -3.7663 | -79.3314 | -110.2292 | -64.4288
|  |  | ST |  |  | 38.5322 | 38.0783 | 37.7995 | 37.1092 | 36.3856 | 35.4324 | 33.7113 | 31.4715 | 28.7018 | 25.5103 | 17.7751 | -16.3367 | -35.494 | -29.5098 | 39.792 | 39.117 | 38.6136 | 37.5892 | 36.4917 | 35.108 | 33.5942 | 31.9839 | 29.9525 | 27.6724 | 22.184 | -3.0068 | -20.9268 | -20.4973 | 39.5231 | 38.754 | 38.122 | 36.9102 | 35.5633 | 33.8559 | 31.9122 | 29.7129 | 26.941 | 23.7659 | 16.0131 | -17.6251 | -36.8736 | -31.2673
|  |  | FS |  |  | 38.1278 | 37.4485 | 36.8727 | 36.0682 | 34.9364 | 32.8937 | 29.5404 | 24.186 | 17.3032 | 9.0609 | -10.7423 | -92.3978 | -120.6944 | -70.6248 | 39.9179 | 39.3115 | 38.7497 | 38.0289 | 37.1507 | 36.0784 | 34.8591 | 33.4383 | 31.7327 | 29.8237 | 25.3108 | -2.1852 | -25.9548 | -25.2471 | 39.6899 | 39.0126 | 38.3801 | 37.4714 | 36.352 | 34.9867 | 33.3773 | 31.4462 | 29.0847 | 26.4355 | 20.1762 | -14.0212 | -44.1556 | -31.5113
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY MAIN | MINIMUM HEADROOM | SU 86530 59483 | YES | 10.8445 | 8.0109 | 5.1816 | 0.78084 | -4.5316 | -10.2971 | -18.0787 | -27.1053 | -37.3491 | -48.55 | -72.8471 | -115.0347 | -137.2741 | -147.1316 | 26.9198 | 25.149 | 23.3978 | 20.9194 | 17.7839 | 14.3612 | 9.2611 | 3.1496 | -3.6796 | -11.2877 | -27.9824 | -61.9007 | -82.0987 | -115.1731 | 10.1349 | 7.5531 | 4.9826 | 0.99852 | -3.8575 | -9.1229 | -16.4416 | -25.0148 | -34.7377 | -45.4146 | -68.6215 | -108.6397 | -129.1782 | -138.0665
|  |  | CT |  |  | 12.0811 | 10.1708 | 7.9328 | 4.2158 | 0.065313 | -5.6218 | -11.6092 | -19.6715 | -30.6896 | -41.7006 | -63.0618 | -113.1346 | -137.2741 | -147.1316 | 27.1029 | 25.5525 | 23.7195 | 21.2343 | 18.4338 | 14.4447 | 10.1184 | 4.0918 | -3.5321 | -11.1892 | -26.1103 | -61.9007 | -82.0987 | -98.8058 | 11.1617 | 9.3713 | 7.2557 | 3.9312 | 0.1296 | -5.1662 | -10.8132 | -18.5293 | -28.9772 | -39.4157 | -59.6174 | -106.9173 | -129.1782 | -138.0665
|  |  | LW |  |  | 10.8445 | 8.0109 | 5.1816 | 0.78084 | -4.5316 | -10.2971 | -18.0787 | -27.1053 | -37.3491 | -48.55 | -72.8471 | -115.0347 | -130.1213 | -127.3375 | 26.9198 | 25.149 | 23.3978 | 20.9194 | 17.7839 | 14.3612 | 9.2611 | 3.1496 | -3.6796 | -11.2877 | -27.9824 | -55.9301 | -64.4521 | -61.1439 | 10.1349 | 7.5531 | 4.9826 | 0.99852 | -3.8575 | -9.1229 | -16.4416 | -25.0148 | -34.7377 | -45.4146 | -68.6215 | -108.6397 | -122.4299 | -119.1729
|  |  | ST |  |  | 13.1548 | 12.2242 | 11.0768 | 9.4735 | 7.4806 | 4.9346 | 1.9009 | -1.7315 | -5.8657 | -10.9599 | -24.4666 | -68.011 | -98.6597 | -114.1572 | 27.8399 | 27.0137 | 25.9947 | 24.5858 | 22.8836 | 20.7467 | 18.1286 | 15.0283 | 11.502 | 7.1985 | -4.1564 | -40.356 | -68.04 | -87.7194 | 12.1841 | 11.3549 | 10.313 | 8.7957 | 6.9172 | 4.5145 | 1.5754 | -1.9546 | -5.9988 | -10.9892 | -24.2669 | -66.9378 | -96.4896 | -110.5786
|  |  | FS |  |  | 12.0811 | 10.1708 | 7.9328 | 4.2158 | 0.065313 | -5.6218 | -11.6092 | -19.6715 | -30.6896 | -41.7006 | -63.0618 | -113.1346 | -137.2741 | -147.1316 | 27.8045 | 26.9281 | 25.8895 | 24.6213 | 23.0632 | 21.1595 | 18.8476 | 16.0887 | 12.8556 | 9.0898 | -0.69533 | -35.1346 | -76.1604 | -115.1731 | 12.1688 | 11.35 | 10.3709 | 8.9962 | 7.2974 | 5.1936 | 2.6525 | -0.39539 | -4.0403 | -8.2653 | -19.2343 | -57.2335 | -97.9052 | -123.4616
BRAMLEY (FLEE) | CAMBERLEY RESERVE | CAMBERLEY RESERVE | MINIMUM HEADROOM | SU 86530 59483 | YES | 37.4963 | 34.8418 | 32.5978 | 29.5541 | 25.8409 | 21.0567 | 14.3109 | 6.8449 | -1.1786 | -9.6506 | -35.771 | -95.0924 | -125.7818 | -137.9698 | 42.2695 | 40.5251 | 38.9496 | 37.0391 | 34.6479 | 31.5049 | 26.8929 | 21.7356 | 15.6999 | 6.904 | -13.8639 | -58.4377 | -81.3601 | -90.6513 | 28.3237 | 25.9122 | 23.7772 | 20.78 | 17.1794 | 12.6687 | 6.387 | -0.53329 | -7.971 | -15.8469 | -32.184 | -84.687 | -113.951 | -125.5662
|  |  | CT |  |  | 38.4616 | 36.286 | 34.3285 | 32.0003 | 29.3351 | 25.1029 | 20.2395 | 14.193 | 6.4526 | -1.075 | -14.7785 | -47.0389 | -62.5933 | -68.6454 | 42.543 | 40.7777 | 39.0232 | 37.3819 | 35.4996 | 32.2832 | 28.5873 | 23.963 | 18.4898 | 13.1842 | 3.3129 | -20.6025 | -35.325 | -49.1011 | 29.3855 | 27.4408 | 25.6251 | 23.4438 | 20.9624 | 16.9729 | 12.3782 | 6.7895 | -0.31619 | -7.1799 | -19.8239 | -50.3449 | -64.6809 | -70.1158
|  |  | LW |  |  | 37.4963 | 34.8418 | 32.5978 | 29.5541 | 25.8409 | 21.0567 | 14.3109 | 6.8449 | -1.1786 | -9.6506 | -35.771 | -95.0924 | -125.7818 | -137.9698 | 42.2695 | 40.5251 | 38.9496 | 37.0391 | 34.6479 | 31.5049 | 26.8929 | 21.7356 | 15.6999 | 6.904 | -13.8639 | -58.4377 | -81.3601 | -90.6513 | 28.3237 | 25.9122 | 23.7772 | 20.78 | 17.1794 | 12.6687 | 6.387 | -0.53329 | -7.971 | -15.8469 | -32.184 | -84.687 | -113.951 | -125.5662
|  |  | ST |  |  | 39.1949 | 37.7259 | 36.5486 | 35.6586 | 34.4841 | 32.4982 | 29.9556 | 27.2315 | 24.4485 | 21.25 | 13.4274 | -12.7699 | -31.6198 | -41.5363 | 43.0447 | 41.7977 | 40.6205 | 39.7511 | 38.6798 | 36.8527 | 34.557 | 32.1096 | 29.5939 | 26.7193 | 19.6509 | -3.2944 | -22.1297 | -37.8263 | 30.0642 | 28.7585 | 27.6436 | 26.8533 | 25.8418 | 24.0226 | 21.704 | 19.2579 | 16.7875 | 13.9706 | 7.0857 | -18.2023 | -36.2293 | -45.6706
|  |  | FS |  |  | 38.4616 | 36.286 | 34.3285 | 32.0003 | 29.3351 | 25.1029 | 20.2395 | 14.193 | 6.4526 | -1.075 | -14.7785 | -47.0389 | -62.5933 | -68.6454 | 42.9916 | 41.9705 | 40.9421 | 39.886 | 38.5848 | 36.6103 | 34.1054 | 31.2415 | 28.0814 | 24.5897 | 16.1292 | -11.0956 | -42.7652 | -75.9282 | 30.038 | 29.0517 | 28.1409 | 27.1026 | 25.8057 | 23.8045 | 21.2424 | 18.3216 | 15.0349 | 11.4558 | 2.9363 | -25.0786 | -53.1436 | -70.6869
IVER 132KV | CHALVEY BSP | CHALVEY BSP | MINIMUM HEADROOM | SU 96669 79364 | YES | 34.5748 | 31.991 | 29.1941 | 25.0723 | 20.7306 | 14.2979 | 6.4975 | -4.4743 | -19.9086 | -37.5754 | -79.066 | -152.5054 | -179.1632 | -195.6546 | 40.845 | 39.3947 | 37.8116 | 35.5132 | 33.0271 | 26.6806 | 16.1005 | 4.4585 | -7.8823 | -21.8248 | -54.3179 | -111.6007 | -132.2521 | -145.1921 | 30.1045 | 28.0593 | 25.8222 | 22.4301 | 18.8266 | 12.6547 | 2.3341 | -11.5889 | -26.687 | -43.8689 | -83.9948 | -155.0136 | -180.7463 | -196.633
|  |  | CT |  |  | 35.7845 | 34.232 | 32.3444 | 29.2499 | 26.1408 | 21.0339 | 14.9803 | 9.3857 | 3.8957 | -0.85286 | -9.3237 | -34.8873 | -48.0893 | -50.5649 | 41.1571 | 40.0387 | 38.6126 | 36.4917 | 34.3267 | 29.643 | 23.8977 | 18.6766 | 13.9524 | 9.7578 | 1.9939 | -18.469 | -40.3357 | -72.9217 | 31.1168 | 29.9256 | 28.4233 | 25.8908 | 23.3313 | 18.3073 | 12.289 | 6.8601 | 1.6774 | -2.7995 | -11.8476 | -41.4939 | -54.0253 | -56.298
|  |  | LW |  |  | 34.5748 | 31.991 | 29.1941 | 25.0723 | 20.7306 | 14.2979 | 6.4975 | -4.4743 | -19.9086 | -37.5754 | -79.066 | -152.5054 | -179.1632 | -195.6546 | 40.845 | 39.3947 | 37.8116 | 35.5132 | 33.0271 | 26.6806 | 16.1005 | 4.4585 | -7.8823 | -21.8248 | -54.3179 | -111.6007 | -132.2521 | -145.1921 | 30.1045 | 28.0593 | 25.8222 | 22.4301 | 18.8266 | 12.6547 | 2.3341 | -11.5889 | -26.687 | -43.8689 | -83.9948 | -155.0136 | -180.7463 | -196.633
|  |  | ST |  |  | 36.3732 | 35.1504 | 33.6006 | 31.7642 | 30.0886 | 26.8498 | 22.8912 | 19.487 | 16.9758 | 15.0531 | 12.0494 | 4.8558 | -0.90665 | -7.3449 | 41.4539 | 40.5151 | 39.2769 | 37.5962 | 35.9901 | 32.2667 | 27.6337 | 23.4843 | 20.1229 | 17.2282 | 11.9842 | -2.3574 | -22.6188 | -56.7893 | 31.6452 | 30.7528 | 29.5581 | 28.0613 | 26.7075 | 23.3545 | 19.2159 | 15.6985 | 13.0771 | 11.0228 | 7.8099 | 0.75573 | -4.616 | -10.0918
|  |  | FS |  |  | 35.7845 | 34.232 | 32.3444 | 29.2499 | 26.1408 | 21.0339 | 14.9803 | 9.3857 | 3.8957 | -0.85286 | -9.3237 | -34.8873 | -48.0893 | -50.5649 | 41.5874 | 40.4924 | 39.2668 | 37.6617 | 35.9362 | 32.1841 | 27.7889 | 23.3289 | 19.1345 | 15.1746 | 6.9018 | -16.5191 | -54.8308 | -124.699 | 31.7894 | 30.9286 | 29.973 | 28.7096 | 27.4174 | 24.1928 | 20.4686 | 16.8095 | 13.6629 | 10.9865 | 4.5116 | -20.9197 | -39.2372 | -49.4891
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER & HUNSTON | MINIMUM HEADROOM | SU 92282 07416 | YES | 108.1995 | 102.9436 | 96.4194 | 86.4619 | 75.0343 | 63.4292 | 49.3822 | 32.7624 | 13.1937 | -8.3447 | -54.0442 | -138.2984 | -180.2478 | -207.7709 | 132.5248 | 129.1499 | 125.4733 | 120.3052 | 113.9927 | 107.4685 | 98.7942 | 88.2352 | 75.8201 | 62.1 | 32.4173 | -24.9269 | -68.2616 | -142.6276 | 108.634 | 103.5623 | 98.0495 | 89.5195 | 79.5756 | 69.2753 | 56.2121 | 40.6766 | 22.3894 | 2.4268 | -40.2542 | -118.5747 | -165.4376 | -192.3696
|  |  | CT |  |  | 111.8078 | 108.7163 | 103.9007 | 95.975 | 86.8566 | 76.5732 | 65.3305 | 50.4407 | 30.0477 | 8.7638 | -32.9402 | -122.243 | -173.6956 | -202.5619 | 133.3809 | 130.6952 | 127.3201 | 122.568 | 116.9003 | 110.297 | 102.7867 | 92.6209 | 79.2896 | 65.333 | 37.6315 | -24.9269 | -68.2616 | -111.0408 | 111.7273 | 108.4182 | 104.2389 | 97.3578 | 89.324 | 80.0963 | 69.8127 | 56.1344 | 37.3004 | 17.7366 | -20.7181 | -103.6611 | -150.3793 | -176.3753
|  |  | LW |  |  | 108.1995 | 102.9436 | 96.4194 | 86.4619 | 75.0343 | 63.4292 | 49.3822 | 32.7624 | 13.1937 | -8.3447 | -54.0442 | -138.2984 | -180.2478 | -207.7709 | 132.5248 | 129.1499 | 125.4733 | 120.3052 | 113.9927 | 107.4685 | 98.7942 | 88.2352 | 75.8201 | 62.1 | 32.4173 | -20.8996 | -61.3228 | -82.9467 | 108.634 | 103.5623 | 98.0495 | 89.5195 | 79.5756 | 69.2753 | 56.2121 | 40.6766 | 22.3894 | 2.4268 | -40.2542 | -118.5747 | -165.4376 | -192.3696
|  |  | ST |  |  | 113.623 | 111.8785 | 108.9127 | 104.8037 | 99.9571 | 95.19 | 89.7715 | 82.9472 | 74.8119 | 65.4465 | 43.6151 | -23.1864 | -73.7132 | -106.5428 | 134.448 | 132.7107 | 130.4196 | 127.4499 | 123.8195 | 120.1757 | 115.793 | 110.3819 | 103.6814 | 96.0968 | 78.0471 | 21.076 | -28.1273 | -71.9577 | 113.4944 | 111.5772 | 108.9614 | 105.5039 | 101.324 | 97.1662 | 92.2317 | 86.0859 | 78.5314 | 69.9292 | 49.4552 | -14.6733 | -62.5556 | -92.1342
|  |  | FS |  |  | 111.8078 | 108.7163 | 103.9007 | 95.975 | 86.8566 | 76.5732 | 65.3305 | 50.4407 | 30.0477 | 8.7638 | -32.9402 | -122.243 | -173.6956 | -202.5619 | 134.4602 | 132.5479 | 130.2207 | 127.2486 | 123.7114 | 119.957 | 115.4712 | 110.1133 | 103.5836 | 96.1912 | 78.4714 | 19.0288 | -56.6061 | -142.6276 | 113.5585 | 111.6056 | 109.1785 | 105.7525 | 101.7335 | 97.5356 | 92.5824 | 86.6727 | 79.4418 | 71.3628 | 52.3303 | -9.3292 | -74.5307 | -120.0674
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL BSP | MINIMUM HEADROOM | SY 65479 80511 | YES | 3.9835 | 0.37607 | -3.4962 | -8.7703 | -15.0464 | -22.0199 | -31.1103 | -41.4596 | -53.6023 | -67.7173 | -98.9908 | -158.2601 | -205.2096 | -230.2908 | 16.8032 | 14.7778 | 12.5881 | 9.758 | 6.2245 | 2.218 | -3.3943 | -10.0806 | -19.2288 | -29.4309 | -50.3046 | -100.4214 | -132.9414 | -176.1567 | 1.2975 | -1.9142 | -5.3547 | -10.0583 | -15.7113 | -21.9953 | -30.387 | -40.0652 | -51.4602 | -64.3067 | -93.87 | -150.3634 | -196.9559 | -220.8998
|  |  | CT |  |  | 5.8758 | 3.4819 | 0.5394 | -4.0007 | -9.1595 | -15.9714 | -23.5455 | -33.1717 | -46.7896 | -61.1826 | -90.4211 | -158.2601 | -205.2096 | -230.2908 | 17.168 | 15.3968 | 13.1733 | 10.2409 | 6.8562 | 2.218 | -3.0557 | -10.0287 | -19.2288 | -29.4309 | -50.3046 | -100.4214 | -132.9414 | -162.8909 | 2.9192 | 0.76218 | -1.9217 | -6.019 | -10.6897 | -16.939 | -23.9476 | -33.0116 | -45.3211 | -58.7473 | -86.355 | -150.3634 | -196.9559 | -220.8998
|  |  | LW |  |  | 3.9835 | 0.37607 | -3.4962 | -8.7703 | -15.0464 | -22.0199 | -31.1103 | -41.4596 | -53.6023 | -67.7173 | -98.9908 | -157.3148 | -179.7132 | -183.3789 | 16.8032 | 14.7778 | 12.5881 | 9.758 | 6.2245 | 2.2518 | -3.3943 | -10.0806 | -17.9674 | -27.5649 | -48.8332 | -86.7483 | -100.4008 | -102.4104 | 1.2975 | -1.9142 | -5.3547 | -10.0583 | -15.7113 | -21.9953 | -30.387 | -40.0652 | -51.4602 | -64.3067 | -93.87 | -148.5185 | -169.2908 | -172.6028
|  |  | ST |  |  | 7.4913 | 6.3351 | 4.7603 | 2.7716 | 0.4108 | -2.5173 | -5.9541 | -9.8434 | -14.5952 | -20.738 | -36.6999 | -89.6975 | -127.316 | -148.0636 | 18.1255 | 17.1748 | 15.8853 | 14.2329 | 12.2988 | 9.9183 | 7.0405 | 3.7527 | -0.21563 | -5.0754 | -18.6015 | -64.2769 | -101.878 | -132.6508 | 4.4288 | 3.4521 | 2.0794 | 0.28772 | -1.8332 | -4.472 | -7.6418 | -11.2758 | -15.6097 | -20.9538 | -36.2767 | -87.9971 | -124.7797 | -143.299
|  |  | FS |  |  | 5.8758 | 3.4819 | 0.5394 | -4.0007 | -9.1595 | -15.9714 | -23.5455 | -33.1717 | -46.7896 | -61.1826 | -90.4211 | -158.2601 | -205.2096 | -230.2908 | 18.0727 | 17.0649 | 15.7952 | 14.1555 | 12.2262 | 9.8769 | 7.127 | 3.8941 | -0.070091 | -4.63 | -16.0412 | -59.1843 | -114.1424 | -176.1567 | 4.4281 | 3.4849 | 2.2733 | 0.49757 | -1.5635 | -4.0798 | -6.9891 | -10.3972 | -14.602 | -19.3826 | -31.3588 | -75.8893 | -122.6023 | -154.1145
MELKSHAM GSP | CHIPPENHAM | CHIPPENHAM | MINIMUM HEADROOM | ST 92629 74275 | YES | 7.733 | 4.3927 | 0.91345 | -3.6867 | -8.8545 | -14.5371 | -21.9297 | -32.1374 | -44.366 | -57.9331 | -87.4086 | -144.5542 | -187.245 | -200.3857 | 33.5645 | 32.5458 | 31.1871 | 28.6472 | 25.0708 | 20.9677 | 15.1632 | 7.9124 | -1.2936 | -11.2493 | -31.2323 | -80.1408 | -113.3951 | -126.4313 | 12.5762 | 9.2568 | 5.8075 | 1.3267 | -3.8857 | -9.623 | -17.6538 | -27.7153 | -39.3557 | -52.3212 | -80.6225 | -136.151 | -169.6811 | -182.5248
|  |  | CT |  |  | 9.5985 | 7.3242 | 4.6101 | 0.56259 | -3.6 | -9.1102 | -15.7568 | -25.7879 | -39.0333 | -52.8157 | -80.2753 | -144.5542 | -187.245 | -200.3857 | 33.5645 | 32.5458 | 31.1871 | 28.9335 | 25.6572 | 20.9677 | 15.5348 | 8.0922 | -1.2936 | -11.2493 | -31.2323 | -80.1408 | -113.3951 | -126.4313 | 14.0718 | 11.6754 | 8.7883 | 4.6957 | 0.3975 | -5.6643 | -12.7593 | -22.3754 | -35.0094 | -48.2301 | -74.5686 | -136.151 | -169.6811 | -182.5248
|  |  | LW |  |  | 7.733 | 4.3927 | 0.91345 | -3.6867 | -8.8545 | -14.5371 | -21.9297 | -32.1374 | -44.366 | -57.9331 | -87.4086 | -139.0583 | -160.1381 | -163.6964 | 33.6415 | 32.6744 | 31.5787 | 28.6472 | 25.0708 | 21.1063 | 15.1632 | 7.9124 | -0.42408 | -9.8261 | -30.5939 | -65.9824 | -80.1182 | -83.035 | 12.5762 | 9.2568 | 5.8075 | 1.3267 | -3.8857 | -9.623 | -17.6538 | -27.7153 | -39.3557 | -52.3212 | -80.6225 | -129.9341 | -150.0596 | -153.7577
|  |  | ST |  |  | 10.9075 | 9.5996 | 7.9539 | 5.4426 | 3.1098 | 0.2665 | -3.1702 | -7.7082 | -13.9752 | -21.2697 | -39.7803 | -99.4346 | -141.0747 | -160.1726 | 34.0039 | 33.3644 | 32.4472 | 30.8306 | 29.7364 | 26.8966 | 23.2011 | 18.9705 | 13.7946 | 7.7766 | -7.8572 | -58.401 | -95.7918 | -118.0694 | 15.3649 | 14.0199 | 12.3045 | 9.5965 | 6.9826 | 3.7532 | -0.52568 | -5.5684 | -11.6888 | -18.8103 | -37.011 | -95.3907 | -136.2934 | -154.8486
|  |  | FS |  |  | 9.5985 | 7.3242 | 4.6101 | 0.56259 | -3.6 | -9.1102 | -15.7568 | -25.7879 | -39.0333 | -52.8157 | -80.2753 | -144.5542 | -187.245 | -200.3857 | 34.0712 | 33.5294 | 32.8261 | 31.8596 | 30.9057 | 28.9393 | 26.0109 | 22.4764 | 18.2655 | 13.4838 | 1.5915 | -38.4306 | -84.355 | -125.5869 | 15.6202 | 14.5161 | 13.1961 | 11.1386 | 8.8951 | 6.2014 | 2.966 | -1.1857 | -6.1942 | -11.8234 | -25.6538 | -71.7101 | -118.8517 | -148.9797
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ 15716 93165 | YES | 29.2054 | 27.0833 | 24.769 | 20.766 | 16.1371 | 11.1942 | 4.9051 | -1.9612 | -9.9978 | -18.8509 | -38.8886 | -76.9589 | -97.3719 | -105.6459 | 38.565 | 38.0634 | 37.5009 | 36.784 | 35.8296 | 34.7037 | 33.0857 | 29.5896 | 24.3034 | 18.2094 | 4.9442 | -27.7483 | -61.0081 | -124.1702 | 25.2908 | 23.3835 | 21.3205 | 17.7487 | 13.5886 | 9.1145 | 3.3398 | -3.0668 | -10.8635 | -19.5373 | -38.6566 | -74.6633 | -93.5343 | -101.9707
|  |  | CT |  |  | 30.774 | 29.5782 | 28.0692 | 24.8705 | 21.298 | 16.9382 | 12.0697 | 6.025 | -2.5886 | -11.55 | -29.5009 | -71.1781 | -92.2435 | -103.0091 | 38.5788 | 38.0946 | 37.5085 | 36.8418 | 36.0576 | 35.0145 | 33.8408 | 30.0145 | 24.3034 | 18.2094 | 4.9442 | -27.7483 | -52.3271 | -81.2978 | 26.6565 | 25.5573 | 24.1795 | 21.3036 | 18.0685 | 13.9265 | 9.2688 | 3.4383 | -4.6539 | -13.108 | -30.0879 | -69.2491 | -88.6811 | -98.6094
|  |  | LW |  |  | 29.2054 | 27.0833 | 24.769 | 20.766 | 16.1371 | 11.1942 | 4.9051 | -1.9612 | -9.9978 | -18.8509 | -38.8886 | -76.9589 | -97.3719 | -105.6459 | 38.565 | 38.0634 | 37.5009 | 36.784 | 35.8296 | 34.7037 | 33.0857 | 29.5896 | 24.5506 | 18.865 | 5.7132 | -26.2183 | -46.6255 | -53.644 | 25.2908 | 23.3835 | 21.3205 | 17.7487 | 13.5886 | 9.1145 | 3.3398 | -3.0668 | -10.8635 | -19.5373 | -38.6566 | -74.6633 | -93.5343 | -101.9707
|  |  | ST |  |  | 31.742 | 31.2692 | 30.5547 | 29.6171 | 28.4365 | 27.0475 | 25.3003 | 23.2687 | 20.644 | 17.4606 | 9.0594 | -22.0219 | -46.1051 | -61.1286 | 38.7353 | 38.4202 | 38.0231 | 37.506 | 36.9043 | 36.2147 | 35.4172 | 34.5635 | 33.4304 | 32.1317 | 25.9924 | -3.9879 | -33.5202 | -64.4786 | 27.5524 | 27.1386 | 26.5192 | 25.6781 | 24.6144 | 23.2209 | 21.4535 | 19.4248 | 16.8882 | 13.8012 | 5.5601 | -24.6688 | -47.9042 | -61.7773
|  |  | FS |  |  | 30.774 | 29.5782 | 28.0692 | 24.8705 | 21.298 | 16.9382 | 12.0697 | 6.025 | -2.5886 | -11.55 | -29.5009 | -71.1781 | -92.2435 | -103.0091 | 38.6666 | 38.2956 | 37.8206 | 37.2313 | 36.5114 | 35.6352 | 34.5766 | 33.3287 | 31.7629 | 29.4031 | 20.2512 | -13.6831 | -61.0081 | -124.1702 | 27.3004 | 26.7445 | 25.9964 | 24.853 | 23.4235 | 21.6232 | 19.4512 | 16.8104 | 13.456 | 9.7701 | 1.0083 | -28.8648 | -60.6189 | -83.0161
IVER 132KV | CIPPENHAM | CIPPENHAM | MINIMUM HEADROOM | SU 96266 79634 | YES | 26.6495 | 26.1162 | 25.5738 | 24.5261 | 23.3251 | 22.042 | 20.5303 | 18.8835 | 16.9173 | 12.1555 | -0.85715 | -30.6807 | -51.242 | -63.0985 | 38.0703 | 37.825 | 37.5848 | 37.0597 | 36.4085 | 35.5775 | 34.5916 | 33.1738 | 29.8323 | 25.8527 | 16.1407 | -5.5489 | -20.4255 | -29.2164 | 28.8612 | 28.3818 | 27.8984 | 26.9623 | 25.8944 | 24.7545 | 23.3936 | 21.9052 | 18.3108 | 13.1278 | 0.64608 | -27.6576 | -47.1352 | -58.3898
|  |  | CT |  |  | 27.1832 | 26.9266 | 26.6161 | 25.7869 | 24.7994 | 23.5842 | 22.2222 | 20.5564 | 17.0403 | 12.1555 | -0.85715 | -30.6807 | -51.242 | -63.0985 | 38.1495 | 37.9012 | 37.5995 | 37.0597 | 36.4085 | 35.5775 | 34.5916 | 33.1738 | 29.8323 | 25.8527 | 16.1407 | -5.5489 | -20.4255 | -29.2164 | 29.3241 | 29.0848 | 28.7958 | 28.0562 | 27.1704 | 26.0702 | 24.8248 | 22.6461 | 18.3108 | 13.1278 | 0.64608 | -27.6576 | -47.1352 | -58.3898
|  |  | LW |  |  | 26.6495 | 26.1162 | 25.5738 | 24.5261 | 23.3251 | 22.042 | 20.5303 | 18.8835 | 16.9173 | 14.8612 | 10.9033 | 1.9427 | -2.7666 | -4.1105 | 38.0703 | 37.825 | 37.5848 | 37.1365 | 36.6124 | 36.0443 | 35.3439 | 34.5747 | 33.6733 | 32.7172 | 30.6618 | 25.7641 | 23.4575 | 23.1017 | 28.8612 | 28.3818 | 27.8984 | 26.9623 | 25.8944 | 24.7545 | 23.3936 | 21.9052 | 20.1178 | 18.2262 | 14.5463 | 6.3802 | 2.1719 | 1.1708
|  |  | ST |  |  | 27.4913 | 27.4489 | 27.3751 | 27.2244 | 27.0055 | 26.7212 | 26.3749 | 25.9803 | 25.5173 | 24.9589 | 23.7209 | 18.3383 | 13.164 | 7.9581 | 38.3465 | 38.2404 | 38.1042 | 37.8838 | 37.6299 | 37.3276 | 36.9627 | 36.5757 | 36.1307 | 35.6186 | 33.958 | 27.4725 | 19.4657 | 7.9331 | 29.6071 | 29.568 | 29.5005 | 29.3441 | 29.1358 | 28.8683 | 28.5333 | 28.1594 | 27.7219 | 27.1949 | 25.9734 | 20.8776 | 16.1329 | 11.5203
|  |  | FS |  |  | 27.1832 | 26.9266 | 26.6161 | 25.7869 | 24.7994 | 23.5842 | 22.2222 | 20.5564 | 17.0403 | 12.1555 | -0.85715 | -30.6807 | -51.242 | -63.0985 | 38.2738 | 38.0946 | 37.8775 | 37.5848 | 37.2274 | 36.7814 | 36.2407 | 35.239 | 34.0194 | 32.7143 | 29.8521 | 20.016 | 6.8946 | -13.4665 | 29.4438 | 29.2752 | 29.0622 | 28.7369 | 28.333 | 27.7701 | 27.1267 | 26.2477 | 25.1348 | 23.9878 | 21.6573 | 14.1979 | 7.5923 | 2.3396
MINETY GSP | CIRENCESTER BSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP 02701 00368 | NO | 31.7564 | 27.4961 | 22.0909 | 18.649 | 14.1912 | 9.0966 | 1.0666 | -8.6327 | -19.7859 | -32.2207 | -59.4146 | -115.2176 | -158.8922 | -171.4252 | 50.4151 | 46.691 | 41.6508 | 39.3686 | 36.3077 | 32.7369 | 27.0098 | 19.9718 | 11.833 | 2.6474 | -17.6492 | -62.3969 | -95.4753 | -105.3743 | 27.2318 | 22.7349 | 16.7845 | 13.4453 | 9.1044 | 4.3602 | -3.2839 | -12.6135 | -23.3856 | -35.4387 | -61.8638 | -113.9594 | -156.0089 | -168.417
|  |  | CT |  |  | 33.7565 | 31.6608 | 28.9619 | 25.6574 | 21.5078 | 15.5605 | 8.8009 | -0.55 | -12.3683 | -24.5396 | -48.3509 | -115.2176 | -158.8922 | -171.4252 | 51.7842 | 50.021 | 47.7021 | 45.2544 | 42.2392 | 37.8315 | 32.7914 | 25.6978 | 16.9069 | 7.7338 | -10.2066 | -62.3969 | -95.4753 | -105.3743 | 29.313 | 27.128 | 24.276 | 20.9895 | 17.1173 | 11.4735 | 4.9904 | -4.0481 | -15.4597 | -27.2645 | -50.3469 | -113.9594 | -156.0089 | -168.417
|  |  | LW |  |  | 31.7564 | 27.4961 | 22.0909 | 18.649 | 14.1912 | 9.0966 | 1.0666 | -8.6327 | -19.7859 | -32.2207 | -59.4146 | -106.3657 | -123.0785 | -122.8245 | 50.4151 | 46.691 | 41.6508 | 39.3686 | 36.3077 | 32.7369 | 27.0098 | 19.9718 | 11.833 | 2.6474 | -17.6492 | -52.2008 | -64.0892 | -69.4314 | 27.2318 | 22.7349 | 16.7845 | 13.4453 | 9.1044 | 4.3602 | -3.2839 | -12.6135 | -23.3856 | -35.4387 | -61.8638 | -107.3281 | -123.6918 | -123.8729
|  |  | ST |  |  | 34.2063 | 32.4617 | 29.4057 | 27.3919 | 24.9673 | 22.0555 | 17.9624 | 13.1573 | 7.3773 | 0.5223 | -16.9104 | -70.4544 | -107.3914 | -120.812 | 51.616 | 49.8138 | 46.4974 | 44.7768 | 42.7247 | 40.3267 | 37.0708 | 33.2688 | 28.5357 | 22.8883 | 8.1517 | -37.4565 | -69.7087 | -84.8832 | 29.488 | 27.5925 | 24.0668 | 21.9959 | 19.516 | 16.6235 | 12.7499 | 8.1145 | 2.461 | -4.251 | -21.4342 | -75.7197 | -112.7356 | -126.2586
|  |  | FS |  |  | 33.7565 | 31.6608 | 28.9619 | 25.6574 | 21.5078 | 15.5605 | 8.8009 | -0.55 | -12.3683 | -24.5396 | -48.3509 | -115.2176 | -158.8922 | -171.4252 | 52.8636 | 52.0681 | 51.0597 | 49.706 | 48.0222 | 45.9657 | 43.4583 | 40.2128 | 36.4259 | 32.0039 | 20.5079 | -20.1708 | -63.7745 | -94.0455 | 30.8248 | 29.9978 | 28.8754 | 27.1885 | 25.123 | 22.6208 | 19.5989 | 15.7161 | 11.0956 | 5.7359 | -8.1282 | -56.7265 | -105.2864 | -133.1399
EALING GSP | COPLEY DENE | COPLEY DENE | MINIMUM HEADROOM | TQ 17445 80798 | YES | 6.8104 | 6.4707 | 6.146 | 5.3555 | 4.5234 | 3.6609 | 2.6656 | 1.5808 | 0.45186 | -0.75681 | -5.8959 | -18.7887 | -23.0873 | -25.6039 | 12.1782 | 11.8086 | 11.3523 | 10.7213 | 9.9994 | 9.1873 | 8.2383 | 7.1652 | 5.8362 | 4.3189 | 0.56502 | -16.2169 | -49.8328 | -114.0919 | 4.9388 | 4.6385 | 4.3484 | 3.6415 | 2.8936 | 2.1141 | 1.2117 | 0.22764 | -0.78723 | -1.8775 | -8.0309 | -20.1373 | -24.0903 | -26.4256
|  |  | CT |  |  | 7.2396 | 7.1228 | 7.0024 | 6.389 | 5.7471 | 5.0374 | 4.2551 | 3.3595 | 2.0942 | 0.77564 | -5.8959 | -18.7887 | -23.0873 | -25.6039 | 12.1782 | 11.8086 | 11.3841 | 10.742 | 10.0274 | 9.1992 | 8.2611 | 7.1841 | 5.8693 | 4.4337 | 0.56502 | -12.3378 | -30.8972 | -62.6699 | 5.3135 | 5.2085 | 5.0966 | 4.5492 | 3.9743 | 3.3333 | 2.6248 | 1.8088 | 0.66802 | -1.6161 | -8.0309 | -20.1373 | -24.0903 | -26.4256
|  |  | LW |  |  | 6.8104 | 6.4707 | 6.146 | 5.3555 | 4.5234 | 3.6609 | 2.6656 | 1.5808 | 0.45186 | -0.75681 | -4.3237 | -13.727 | -16.1574 | -17.7249 | 12.3462 | 12.2116 | 12.0834 | 11.7955 | 11.4822 | 11.1399 | 10.7113 | 10.2329 | 9.7244 | 9.1633 | 4.8857 | -1.7478 | -3.3941 | -4.5435 | 4.9388 | 4.6385 | 4.3484 | 3.6415 | 2.8936 | 2.1141 | 1.2117 | 0.22764 | -0.78723 | -1.8775 | -6.4741 | -15.3337 | -17.593 | -19.0585
|  |  | ST |  |  | 7.4059 | 7.3902 | 7.3873 | 7.3475 | 7.2983 | 7.2393 | 7.1413 | 7.0323 | 6.8841 | 6.7072 | 6.2348 | 3.3567 | 0.49705 | -2.3734 | 12.248 | 11.9272 | 11.56 | 11.0943 | 10.5742 | 9.9804 | 9.2938 | 8.5394 | 7.6705 | 6.6891 | 4.3056 | -5.5871 | -24.2552 | -56.3944 | 5.4543 | 5.4406 | 5.4353 | 5.3897 | 5.3381 | 5.277 | 5.1799 | 5.0756 | 4.9432 | 4.7832 | 4.354 | 1.7921 | -0.71231 | -3.1813
|  |  | FS |  |  | 7.2396 | 7.1228 | 7.0024 | 6.389 | 5.7471 | 5.0374 | 4.2551 | 3.3595 | 2.0942 | 0.77564 | -5.8959 | -18.7887 | -23.0873 | -25.6039 | 12.2145 | 11.8117 | 11.3523 | 10.7213 | 9.9994 | 9.1873 | 8.2383 | 7.1652 | 5.8362 | 4.3189 | 0.5823 | -16.2169 | -49.8328 | -114.0919 | 5.4611 | 5.4413 | 5.4321 | 5.3536 | 5.2621 | 5.1618 | 5.0496 | 4.9198 | 4.6762 | 4.4167 | 3.8164 | 1.2324 | -2.3517 | -5.9359
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES & WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ 50519 94250 | YES | 67.9958 | 64.2606 | 60.2885 | 54.2935 | 47.3949 | 40.0522 | 30.5693 | 20.0459 | 7.8714 | -5.2277 | -33.382 | -86.9431 | -120.2281 | -139.0821 | 85.5012 | 83.3662 | 81.1186 | 78.0533 | 74.3314 | 70.2706 | 64.3132 | 57.4539 | 49.5922 | 40.8803 | 21.7432 | -22.6247 | -53.3998 | -106.5605 | 59.9804 | 56.5997 | 53.052 | 47.7863 | 41.6249 | 35.0276 | 26.1007 | 16.0136 | 4.3337 | -8.3752 | -35.8957 | -86.7736 | -116.9616 | -133.779
|  |  | CT |  |  | 70.5881 | 68.502 | 65.8881 | 61.1096 | 55.8074 | 49.1006 | 41.6397 | 32.4242 | 19.3687 | 5.9716 | -20.457 | -84.2817 | -120.2281 | -139.0821 | 86.108 | 84.459 | 82.3878 | 79.4071 | 76.0568 | 71.4703 | 66.1519 | 59.2807 | 50.3844 | 41.087 | 22.5315 | -22.6247 | -53.3998 | -84.4647 | 61.7902 | 59.8238 | 57.3689 | 53.2425 | 48.4457 | 42.1448 | 35.0319 | 25.9938 | 13.4981 | 0.64213 | -24.6555 | -84.7115 | -116.9616 | -133.779
|  |  | LW |  |  | 67.9958 | 64.2606 | 60.2885 | 54.2935 | 47.3949 | 40.0522 | 30.5693 | 20.0459 | 7.8714 | -5.2277 | -33.382 | -86.9431 | -112.7324 | -121.1501 | 85.5012 | 83.3662 | 81.1186 | 78.0533 | 74.3314 | 70.2706 | 64.3132 | 57.4539 | 49.5922 | 40.8803 | 21.7432 | -12.3269 | -27.1976 | -35.3381 | 59.9804 | 56.5997 | 53.052 | 47.7863 | 41.6249 | 35.0276 | 26.1007 | 16.0136 | 4.3337 | -8.3752 | -35.8957 | -86.7736 | -109.9228 | -116.6015
|  |  | ST |  |  | 72.3386 | 71.5065 | 70.2563 | 68.5854 | 66.6002 | 64.1041 | 60.9235 | 57.3769 | 53.3093 | 48.5108 | 35.6863 | -13.0517 | -51.2208 | -76.8041 | 87.0524 | 86.2075 | 85.0387 | 83.4306 | 81.5782 | 79.2228 | 76.1399 | 72.7127 | 68.6421 | 63.8491 | 51.5128 | 9.0704 | -28.9645 | -63.5402 | 63.288 | 62.491 | 61.327 | 59.6712 | 57.7037 | 55.1962 | 51.8906 | 48.1451 | 43.7422 | 38.4964 | 24.8572 | -23.1554 | -59.8881 | -82.2604
|  |  | FS |  |  | 70.5881 | 68.502 | 65.8881 | 61.1096 | 55.8074 | 49.1006 | 41.6397 | 32.4242 | 19.3687 | 5.9716 | -20.457 | -84.2817 | -120.2281 | -139.0821 | 87.1005 | 86.1109 | 84.8736 | 83.2658 | 81.3442 | 79.0209 | 76.1942 | 72.86 | 68.7558 | 64.1254 | 52.6094 | 12.0869 | -41.4786 | -106.5605 | 63.3384 | 62.4595 | 61.3168 | 59.63 | 57.6039 | 55.1581 | 52.2058 | 48.71 | 44.4471 | 39.7017 | 28.0143 | -12.5719 | -56.6266 | -89.337
COWLEY GSP | COWLEY LOCAL (2 X 45) | COWLEY LOCAL (2 X 45) | MINIMUM HEADROOM | SP 56113 03074 | NO | 65.8724 | 64.5992 | 63.1763 | 61.1578 | 58.3959 | 55.027 | 50.5515 | 45.4759 | 40.1581 | 34.5185 | 22.3406 | 2.0596 | -4.3397 | -7.3738 | 66.0443 | 65.5562 | 65.072 | 64.2002 | 62.7494 | 60.7693 | 58.1713 | 54.7414 | 51.1091 | 47.1366 | 39.4247 | 24.9484 | 17.7771 | 9.314 | 60.2085 | 59.0442 | 57.7838 | 56.0199 | 53.618 | 50.5633 | 46.4093 | 41.6952 | 36.774 | 31.5471 | 20.3049 | 1.6125 | -5.1785 | -8.1491
|  |  | CT |  |  | 66.1691 | 65.2285 | 64.0102 | 62.0844 | 59.629 | 56.1641 | 52.3353 | 47.4238 | 41.6099 | 35.7233 | 24.0612 | 3.5013 | -4.3397 | -7.3738 | 66.1417 | 65.8315 | 65.4631 | 64.6752 | 63.3281 | 61.2546 | 58.5797 | 55.0832 | 51.1091 | 47.1366 | 39.4808 | 24.9484 | 18.9905 | 15.5862 | 60.4633 | 59.6108 | 58.5199 | 56.8128 | 54.6713 | 51.4563 | 47.8603 | 43.2432 | 37.8137 | 32.3498 | 21.656 | 2.2244 | -5.1785 | -7.9995
|  |  | LW |  |  | 65.8724 | 64.5992 | 63.1763 | 61.1578 | 58.3959 | 55.027 | 50.5515 | 45.4759 | 40.1581 | 34.5185 | 22.3406 | 2.0596 | -2.7037 | -0.68717 | 66.0443 | 65.5562 | 65.072 | 64.2002 | 62.7494 | 60.7693 | 58.1713 | 54.7414 | 51.2229 | 47.4717 | 39.4247 | 26.1841 | 23.1588 | 24.9652 | 60.2085 | 59.0442 | 57.7838 | 56.0199 | 53.618 | 50.5633 | 46.4093 | 41.6952 | 36.774 | 31.5471 | 20.3049 | 1.6125 | -2.8274 | -0.73976
|  |  | ST |  |  | 66.6464 | 66.152 | 65.444 | 64.2565 | 62.694 | 60.7118 | 58.4708 | 55.9574 | 53.2634 | 50.2087 | 42.8497 | 25.351 | 14.3053 | 9.8383 | 66.2879 | 66.1103 | 65.9009 | 65.3902 | 64.7836 | 63.5407 | 62.021 | 60.3564 | 58.6176 | 56.3657 | 50.9836 | 37.1462 | 27.8321 | 23.7789 | 60.9282 | 60.5144 | 59.9259 | 58.9051 | 57.5921 | 55.7872 | 53.6943 | 51.3633 | 48.8823 | 46.0782 | 39.3223 | 22.4593 | 11.6692 | 7.4957
|  |  | FS |  |  | 66.1691 | 65.2285 | 64.0102 | 62.0844 | 59.629 | 56.1641 | 52.3353 | 47.4238 | 41.6099 | 35.7233 | 24.0612 | 3.5013 | -4.3397 | -7.3738 | 66.383 | 66.053 | 65.6898 | 65.1976 | 64.4895 | 63.031 | 61.2907 | 58.9275 | 56.336 | 53.5893 | 47.4068 | 31.4156 | 17.7771 | 9.314 | 60.8774 | 60.2141 | 59.4093 | 58.305 | 56.8845 | 54.8454 | 52.3659 | 49.4383 | 46.2573 | 42.8829 | 35.2906 | 15.769 | 0.11613 | -8.1491
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL (2 X 90) | MINIMUM HEADROOM | SP 56113 03074 | NO | 23.5045 | 21.3141 | 18.715 | 14.6659 | 10.0725 | 4.8206 | -1.2536 | -8.5884 | -16.6266 | -27.2717 | -59.1673 | -126.6324 | -157.5602 | -170.9077 | 31.7788 | 30.7833 | 29.4639 | 26.906 | 23.7967 | 19.6114 | 14.2907 | 7.0322 | -1.7248 | -11.7198 | -35.4905 | -85.3247 | -107.8447 | -145.0622 | 21.894 | 19.9327 | 17.6461 | 14.0251 | 9.8595 | 5.0675 | -0.74885 | -7.8298 | -15.4839 | -23.6558 | -49.5703 | -113.8737 | -143.3061 | -156.1147
|  |  | CT |  |  | 24.7161 | 23.2779 | 21.2467 | 17.687 | 13.8294 | 8.9365 | 3.5802 | -3.6444 | -13.7542 | -27.2717 | -59.1673 | -126.6324 | -157.5602 | -170.9077 | 31.7788 | 30.7833 | 29.4639 | 26.906 | 23.7967 | 19.6114 | 14.2907 | 7.0322 | -1.7248 | -11.7198 | -35.4905 | -85.3247 | -107.8447 | -118.0723 | 22.8603 | 21.522 | 19.6652 | 16.4407 | 12.9397 | 8.4189 | 3.3276 | -3.5773 | -12.3238 | -21.5557 | -49.5703 | -113.8737 | -143.3061 | -156.1147
|  |  | LW |  |  | 23.5045 | 21.3141 | 18.715 | 14.6659 | 10.0725 | 4.8206 | -1.2536 | -8.5884 | -16.6266 | -25.2625 | -44.5932 | -77.5208 | -88.7844 | -91.435 | 31.843 | 30.8759 | 29.7752 | 27.6196 | 25.0999 | 22.1936 | 18.1324 | 13.0208 | 7.6224 | 1.8402 | -11.3799 | -33.6961 | -42.1503 | -48.4707 | 21.894 | 19.9327 | 17.6461 | 14.0251 | 9.8595 | 5.0675 | -0.74885 | -7.8298 | -15.4839 | -23.6558 | -42.046 | -73.5091 | -84.3363 | -87.056
|  |  | ST |  |  | 25.3292 | 24.378 | 22.9313 | 20.8905 | 18.7642 | 16.1769 | 13.1136 | 9.1438 | 4.8267 | 0.11897 | -11.7029 | -48.4065 | -72.2571 | -81.8727 | 32.1496 | 31.5153 | 30.6626 | 29.2076 | 27.3956 | 24.9404 | 21.9117 | 18.1662 | 14.0739 | 9.6253 | -1.5377 | -37.8469 | -69.3006 | -100.5881 | 23.3854 | 22.4948 | 21.1845 | 19.183 | 17.1489 | 14.7639 | 11.8147 | 8.0237 | 3.8474 | -0.76092 | -12.6008 | -50.0274 | -73.5065 | -81.7579
|  |  | FS |  |  | 24.7161 | 23.2779 | 21.2467 | 17.687 | 13.8294 | 8.9365 | 3.5802 | -3.6444 | -13.7542 | -27.2717 | -59.1673 | -126.6324 | -157.5602 | -170.9077 | 32.3959 | 31.8359 | 31.1288 | 30.2013 | 28.3145 | 26.0213 | 23.4398 | 20.2624 | 16.5721 | 12.5195 | 2.7095 | -32.0522 | -80.2651 | -145.0622 | 23.6461 | 22.871 | 21.8188 | 20.3489 | 18.6916 | 16.6741 | 14.4698 | 11.6634 | 8.3595 | 4.7942 | -3.7278 | -32.3388 | -62.3172 | -80.9945
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU 78324 50817 | YES | 22.7342 | 20.7167 | 18.6301 | 15.6285 | 12.1137 | 8.3291 | 2.8941 | -3.6901 | -11.5811 | -22.0792 | -56.3757 | -142.4416 | -184.0604 | -189.7374 | 36.3024 | 35.02 | 33.6922 | 31.883 | 29.6698 | 27.2212 | 23.4501 | 18.7654 | 13.2175 | 6.8562 | -18.8643 | -82.7272 | -114.7 | -122.2592 | 25.2362 | 23.3542 | 21.417 | 18.6235 | 15.3191 | 11.7366 | 6.518 | 0.16443 | -7.4371 | -16.1194 | -48.9565 | -131.0947 | -171.2818 | -177.7876
|  |  | CT |  |  | 23.6462 | 22.3238 | 20.7043 | 18.1019 | 15.3432 | 11.6035 | 7.299 | 1.4158 | -6.7977 | -15.3932 | -32.8043 | -91.5708 | -114.829 | -116.7971 | 36.4768 | 35.403 | 34.0679 | 32.219 | 30.2246 | 27.4008 | 24.0704 | 19.4766 | 13.5645 | 7.2494 | -5.5699 | -48.5593 | -67.8103 | -62.9926 | 26.0345 | 24.7884 | 23.2519 | 20.7884 | 18.1655 | 14.5522 | 10.3594 | 4.6137 | -3.3061 | -11.6439 | -28.4793 | -84.6462 | -106.5764 | -107.2956
|  |  | LW |  |  | 22.7342 | 20.7167 | 18.6301 | 15.6285 | 12.1137 | 8.3291 | 2.8941 | -3.6901 | -11.5811 | -22.0792 | -56.3757 | -142.4416 | -184.0604 | -189.7374 | 36.3024 | 35.02 | 33.6922 | 31.883 | 29.6698 | 27.2212 | 23.4501 | 18.7654 | 13.2175 | 6.8562 | -18.8643 | -82.7272 | -114.7 | -122.2592 | 25.2362 | 23.3542 | 21.417 | 18.6235 | 15.3191 | 11.7366 | 6.518 | 0.16443 | -7.4371 | -16.1194 | -48.9565 | -131.0947 | -171.2818 | -177.7876
|  |  | ST |  |  | 24.3857 | 23.7066 | 22.8459 | 21.4289 | 19.977 | 18.2111 | 15.8458 | 13.0133 | 9.5678 | 5.5112 | -5.0144 | -48.831 | -76.8661 | -74.6543 | 36.9879 | 36.3825 | 35.6055 | 34.259 | 32.9296 | 31.3282 | 29.185 | 26.7224 | 23.7377 | 20.2702 | 11.3683 | -26.6806 | -52.1367 | -50.9651 | 26.761 | 26.1374 | 25.3369 | 23.8881 | 22.4369 | 20.656 | 18.2481 | 15.4104 | 11.9246 | 7.8398 | -2.7156 | -46.1161 | -73.7018 | -71.4386
|  |  | FS |  |  | 23.6462 | 22.3238 | 20.7043 | 18.1019 | 15.3432 | 11.6035 | 7.299 | 1.4158 | -6.7977 | -15.3932 | -32.8043 | -91.5708 | -114.829 | -116.7971 | 37.0753 | 36.4518 | 35.7169 | 34.7755 | 33.7105 | 32.4201 | 30.8157 | 28.8412 | 26.5081 | 23.8094 | 16.8045 | -21.8094 | -56.7993 | -56.8863 | 26.9006 | 26.3153 | 25.6308 | 24.5841 | 23.4112 | 21.9902 | 20.2236 | 18.0246 | 15.2579 | 12.0757 | 3.8719 | -39.5276 | -76.7887 | -86.4376
IVER 132KV | DENHAM | DENHAM | MINIMUM HEADROOM | TQ 01785 87618 | YES | 37.2522 | 36.2824 | 35.3031 | 33.7267 | 31.7618 | 29.6688 | 26.6991 | 23.182 | 19.2168 | 14.8112 | 5.1681 | -70.9437 | -85.9441 | -21.651 | 43.3526 | 42.7225 | 42.0897 | 41.1223 | 39.8513 | 38.4747 | 36.3847 | 33.8713 | 31.1247 | 28.028 | 21.1677 | -37.1405 | -62.1486 | -18.0195 | 32.2383 | 31.3314 | 30.4158 | 28.9357 | 27.0713 | 25.0804 | 22.2103 | 18.8035 | 14.9985 | 10.7584 | 1.4584 | -73.831 | -91.3887 | -34.5845
|  |  | CT |  |  | 37.6944 | 37.0407 | 36.2796 | 35.004 | 33.5446 | 31.5993 | 29.526 | 26.6352 | 22.7001 | 18.8188 | 11.2763 | -67.4986 | -85.9441 | -21.651 | 43.4218 | 42.8735 | 42.2262 | 41.3446 | 40.3034 | 38.8796 | 37.3152 | 35.0979 | 32.3346 | 29.5941 | 24.2594 | -36.9299 | -51.6302 | -2.6845 | 32.5966 | 31.9643 | 31.2216 | 30.0531 | 28.677 | 26.8218 | 24.8218 | 22.0169 | 18.256 | 14.5472 | 7.3593 | -70.1256 | -87.4412 | -23.636
|  |  | LW |  |  | 37.2522 | 36.2824 | 35.3031 | 33.7267 | 31.7618 | 29.6688 | 26.6991 | 23.182 | 19.2168 | 14.8112 | 5.1681 | -70.9437 | -80.5798 | -19.7367 | 43.3526 | 42.7225 | 42.0897 | 41.1223 | 39.8513 | 38.4747 | 36.3847 | 33.8713 | 31.1247 | 28.028 | 21.1677 | -37.1405 | -43.0892 | 5.1561 | 32.2383 | 31.3314 | 30.4158 | 28.9357 | 27.0713 | 25.0804 | 22.2103 | 18.8035 | 14.9985 | 10.7584 | 1.4584 | -73.831 | -82.6214 | -22.1547
|  |  | ST |  |  | 38.0951 | 37.834 | 37.4891 | 36.9039 | 36.163 | 35.3096 | 34.2437 | 32.9793 | 31.5421 | 29.7483 | 24.9369 | -38.1706 | -66.664 | -8.1561 | 43.7164 | 43.4622 | 43.1356 | 42.5742 | 41.8905 | 41.1196 | 40.1387 | 39.0158 | 37.7704 | 36.2338 | 32.1271 | -20.4195 | -44.4165 | 2.9606 | 32.9855 | 32.7394 | 32.4107 | 31.8139 | 31.0623 | 30.208 | 29.1166 | 27.8365 | 26.3848 | 24.5731 | 19.6956 | -43.0834 | -71.1255 | -12.3059
|  |  | FS |  |  | 37.6944 | 37.0407 | 36.2796 | 35.004 | 33.5446 | 31.5993 | 29.526 | 26.6352 | 22.7001 | 18.8188 | 11.2763 | -67.4986 | -85.9441 | -21.651 | 43.4672 | 42.9835 | 42.4172 | 41.7293 | 40.8468 | 39.7451 | 38.3117 | 36.4534 | 34.326 | 31.9534 | 26.2782 | -25.7779 | -62.1486 | -18.0195 | 32.6814 | 32.1626 | 31.5559 | 30.7646 | 29.7356 | 28.4438 | 26.7499 | 24.5338 | 21.926 | 19.0341 | 12.159 | -49.6137 | -91.3887 | -34.5845
COWLEY GSP | DRAYTON BSP | DRAYTON BSP | MINIMUM HEADROOM | SU 46684 92706 | YES | 76.7807 | 66.1679 | 55.3145 | 46.8368 | 36.7994 | 24.6498 | 10.055 | -5.8193 | -22.4986 | -39.3093 | -74.7028 | -136.6455 | -162.9405 | -180.2408 | 82.8572 | 73.3594 | 63.7615 | 58.2917 | 51.7654 | 43.1695 | 32.2583 | 20.4658 | 8.6213 | -3.4692 | -29.3248 | -73.6499 | -105.406 | -127.6857 | 85.2009 | 74.2896 | 63.2033 | 55.6858 | 46.6711 | 35.3247 | 21.0523 | 5.4213 | -10.4912 | -26.6859 | -60.9828 | -120.646 | -147.5966 | -164.024
|  |  | CT |  |  | 78.5625 | 68.9595 | 59.0408 | 51.5185 | 43.2799 | 31.8579 | 20.1304 | 5.3364 | -11.9237 | -28.0495 | -57.4771 | -120.9552 | -150.4499 | -164.3636 | 83.3292 | 73.9993 | 64.4494 | 59.0746 | 53.3369 | 44.507 | 35.4882 | 24.3767 | 11.8936 | 0.17752 | -21.4069 | -68.7052 | -92.9213 | -111.9723 | 86.5832 | 76.4986 | 66.0769 | 59.2296 | 51.7616 | 40.6916 | 29.3323 | 15.1958 | -1.2344 | -16.6525 | -44.8764 | -105.693 | -133.0682 | -145.5812
|  |  | LW |  |  | 76.7807 | 66.1679 | 55.3145 | 46.8368 | 36.7994 | 24.6498 | 10.055 | -5.8193 | -22.4986 | -39.3093 | -74.7028 | -136.6455 | -162.9405 | -180.2408 | 82.8572 | 73.3594 | 63.7615 | 58.2917 | 51.7654 | 43.1695 | 32.2583 | 20.4658 | 8.6213 | -3.4692 | -29.3248 | -73.6499 | -105.406 | -118.3789 | 85.2009 | 74.2896 | 63.2033 | 55.6858 | 46.6711 | 35.3247 | 21.0523 | 5.4213 | -10.4912 | -26.6859 | -60.9828 | -120.646 | -147.5966 | -164.024
|  |  | ST |  |  | 80.1365 | 71.8772 | 63.4445 | 58.3625 | 52.864 | 45.6975 | 38.616 | 30.8614 | 22.5545 | 13.9104 | -6.5391 | -69.4904 | -111.3685 | -128.8772 | 84.388 | 76.0937 | 67.7125 | 63.7562 | 59.5354 | 53.4677 | 47.2364 | 40.5178 | 33.6352 | 26.4339 | 9.2828 | -42.9981 | -80.1763 | -100.7089 | 88.1441 | 79.4677 | 70.618 | 66.0818 | 61.1615 | 54.2664 | 47.1651 | 39.4173 | 31.4561 | 23.0682 | 2.9983 | -59.5214 | -101.4052 | -116.0782
|  |  | FS |  |  | 78.5625 | 68.9595 | 59.0408 | 51.5185 | 43.2799 | 31.8579 | 20.1304 | 5.3364 | -11.9237 | -28.0495 | -57.4771 | -120.9552 | -150.4499 | -164.3636 | 84.9206 | 77.3844 | 69.5758 | 66.3647 | 62.7558 | 57.4713 | 51.7276 | 45.4595 | 39.1343 | 32.6835 | 17.6685 | -29.7658 | -82.4357 | -127.6857 | 88.7958 | 81.0231 | 72.9439 | 69.2103 | 65.0028 | 59.0309 | 52.5677 | 45.4904 | 38.2829 | 30.9744 | 14.0341 | -39.6321 | -94.3813 | -128.2191
EALING GSP | EALING | EALING | MINIMUM HEADROOM | TQ 18371 79475 | YES | 8.9595 | 7.8133 | 6.7604 | 5.5668 | 4.4498 | 3.3329 | 2.0704 | 0.81461 | -0.41486 | -2.4913 | -11.7199 | -27.8379 | -32.6968 | -35.6978 | 14.2059 | 13.4481 | 12.8138 | 12.137 | 11.2431 | 10.132 | 8.7768 | 7.353 | 5.7328 | 3.9791 | -1.8397 | -15.7992 | -32.8111 | -67.655 | 9.8013 | 8.8225 | 7.9317 | 6.8639 | 5.8441 | 4.8178 | 3.6459 | 2.5356 | 1.4697 | -2.1929 | -10.9479 | -26.6728 | -47.7241 | -55.5032
|  |  | CT |  |  | 9.5613 | 8.8605 | 8.1137 | 7.1708 | 6.2018 | 5.0185 | 3.5962 | 2.0485 | 0.14381 | -2.4913 | -11.7199 | -27.8379 | -32.6968 | -35.6978 | 14.3685 | 13.7038 | 12.9641 | 12.137 | 11.2431 | 10.132 | 8.7768 | 7.353 | 5.7328 | 3.9791 | -1.8397 | -13.5297 | -20.6271 | -38.4993 | 10.353 | 9.7691 | 9.1376 | 8.2845 | 7.4016 | 6.3162 | 5.0015 | 3.6105 | 1.633 | -2.1929 | -10.9479 | -26.1949 | -30.7212 | -33.5455
|  |  | LW |  |  | 8.9595 | 7.8133 | 6.7604 | 5.5668 | 4.4498 | 3.3329 | 2.0704 | 0.81461 | -0.41486 | -1.6661 | -4.2167 | -8.0656 | -9.3134 | -9.6474 | 14.2059 | 13.4481 | 12.8138 | 12.1469 | 11.5243 | 10.8985 | 10.1607 | 9.5065 | 8.8904 | 8.2614 | 6.9673 | 5.0849 | 4.5091 | 4.4222 | 9.8013 | 8.8225 | 7.9317 | 6.8639 | 5.8441 | 4.8178 | 3.6459 | 2.5356 | 1.4697 | 0.38646 | -1.822 | -5.2352 | -6.2897 | -6.5042
|  |  | ST |  |  | 9.7604 | 9.1928 | 8.5867 | 8.2005 | 7.8587 | 7.4146 | 6.8223 | 6.286 | 5.7315 | 5.1391 | 3.9839 | 0.58213 | -2.0868 | -4.3285 | 14.4766 | 13.8917 | 13.2354 | 12.6305 | 12.0099 | 11.2521 | 10.3073 | 9.4324 | 8.5399 | 7.5724 | 5.5499 | -1.639 | -12.8166 | -31.3779 | 10.5427 | 10.0868 | 9.5924 | 9.2389 | 8.9178 | 8.5029 | 7.9436 | 7.4911 | 7.0401 | 6.5652 | 5.5764 | 2.4446 | 0.055447 | -1.8752
|  |  | FS |  |  | 9.5613 | 8.8605 | 8.1137 | 7.1708 | 6.2018 | 5.0185 | 3.5962 | 2.0485 | 0.14381 | -2.4913 | -11.7199 | -27.8379 | -32.6968 | -35.6978 | 14.6197 | 13.9015 | 13.1935 | 12.4517 | 11.6337 | 10.7347 | 9.6626 | 8.5045 | 7.1874 | 5.6716 | 1.9946 | -15.7992 | -32.8111 | -67.655 | 10.7446 | 10.2545 | 9.8109 | 9.3953 | 8.9691 | 8.5071 | 7.9531 | 7.3687 | 6.5186 | 4.5146 | -1.4305 | -26.6728 | -47.7241 | -55.5032
EALING GSP | EALING (D) | EALING (D) | MINIMUM HEADROOM | TQ 18371 79475 | YES | 25.4686 | 22.337 | 19.7553 | 16.7223 | 13.6544 | 10.5063 | 5.8723 | 0.47519 | -5.2334 | -11.4234 | -24.761 | -47.3164 | -56.2315 | -60.2766 | 38.8944 | 36.9968 | 34.9935 | 32.6882 | 30.2889 | 26.9245 | 23.081 | 17.9718 | 12.0702 | 6.2485 | -5.0533 | -47.4724 | -119.881 | -235.9791 | 31.755 | 29.0169 | 26.7532 | 24.0197 | 21.1568 | 18.2114 | 13.7878 | 8.5937 | 3.1079 | -2.8785 | -15.8039 | -37.5154 | -45.6569 | -61.0217
|  |  | CT |  |  | 26.3544 | 24.1407 | 22.0342 | 19.4181 | 16.9373 | 13.4216 | 9.4305 | 4.1217 | -2.2173 | -8.2064 | -19.0861 | -44.7224 | -56.2315 | -60.2766 | 38.8944 | 36.9968 | 34.9935 | 32.6882 | 30.2889 | 26.9245 | 23.081 | 17.9718 | 12.0702 | 6.2485 | -5.0533 | -38.3226 | -74.804 | -129.6298 | 32.529 | 30.6487 | 28.7886 | 26.4216 | 24.1181 | 20.7995 | 17.0191 | 11.9124 | 5.8323 | 0.070232 | -10.3541 | -34.9113 | -45.6569 | -49.3157
|  |  | LW |  |  | 25.4686 | 22.337 | 19.7553 | 16.7223 | 13.6544 | 10.5063 | 5.8723 | 0.47519 | -5.2334 | -11.4234 | -24.761 | -47.3164 | -52.7843 | -48.5253 | 39.0979 | 37.2181 | 35.6954 | 33.9829 | 32.0875 | 30.1193 | 26.891 | 23.0008 | 18.849 | 14.2482 | 4.2478 | -12.0787 | -15.4253 | -11.1069 | 31.755 | 29.0169 | 26.7532 | 24.0197 | 21.1568 | 18.2114 | 13.7878 | 8.5937 | 3.1079 | -2.8785 | -15.8039 | -37.5154 | -42.5466 | -38.0239
|  |  | ST |  |  | 27.1958 | 25.7026 | 24.4002 | 23.1485 | 22.0063 | 20.4536 | 18.3658 | 15.9878 | 13.41 | 10.3802 | 2.3691 | -24.4013 | -42.3561 | -48.9238 | 39.4649 | 38.1125 | 36.7212 | 35.1055 | 33.3797 | 31.2083 | 28.4654 | 25.3419 | 21.9108 | 17.9049 | 7.8824 | -27.3228 | -69.2862 | -125.5315 | 33.3348 | 32.1567 | 31.0811 | 29.9593 | 28.8825 | 27.411 | 25.4083 | 23.1082 | 20.6122 | 17.5698 | 9.7716 | -16.5781 | -34.0671 | -40.121
|  |  | FS |  |  | 26.3544 | 24.1407 | 22.0342 | 19.4181 | 16.9373 | 13.4216 | 9.4305 | 4.1217 | -2.2173 | -8.2064 | -19.0861 | -44.7224 | -56.2315 | -60.2766 | 39.4558 | 37.7803 | 36.0986 | 34.0737 | 31.7916 | 29.1199 | 25.8441 | 21.9954 | 17.4024 | 12.1205 | -0.83588 | -47.4724 | -119.881 | -235.9791 | 33.4702 | 32.1737 | 31.036 | 29.7488 | 28.3737 | 26.7065 | 24.5944 | 22.041 | 19.0458 | 15.673 | 7.4596 | -18.616 | -45.0501 | -61.0217
LALEHAM | EAST BEDFONT B | EAST BEDFONT B | MINIMUM HEADROOM | TQ 08394 73826 | YES | 1.7363 | 1.2212 | 0.70157 | -0.127 | -1.1021 | -2.9411 | -5.4457 | -10.0401 | -15.3804 | -21.6184 | -36.1705 | -60.0456 | -66.8377 | -71.6714 | 4.506 | 4.1966 | 3.8895 | 3.4191 | 2.8444 | 1.2485 | -1.2356 | -4.6238 | -8.6241 | -13.5904 | -25.0499 | -43.9549 | -49.6208 | -53.9105 | 2.9375 | 2.4767 | 2.0116 | 1.2306 | 0.22475 | -2.3861 | -5.8131 | -10.2235 | -15.4775 | -21.5637 | -35.6606 | -58.8999 | -65.6981 | -70.6444
|  |  | CT |  |  | 2.0195 | 1.7318 | 1.3692 | 0.71091 | 0.00036233 | -1.7219 | -3.678 | -6.0838 | -8.7683 | -11.381 | -17.0173 | -37.2353 | -50.5296 | -55.5013 | 4.6177 | 4.4109 | 4.1537 | 3.7313 | 3.2565 | 1.6837 | -0.15015 | -2.137 | -4.2239 | -6.2605 | -10.2016 | -25.777 | -36.1985 | -40.2777 | 3.2283 | 2.9943 | 2.7001 | 2.1118 | 1.4586 | -0.36887 | -2.4732 | -4.9176 | -7.5759 | -10.1365 | -17.234 | -36.813 | -49.6993 | -54.6011
|  |  | LW |  |  | 1.7363 | 1.2212 | 0.70157 | -0.127 | -1.1021 | -2.9411 | -5.4457 | -10.0401 | -15.3804 | -21.6184 | -36.1705 | -60.0456 | -66.8377 | -71.6714 | 4.506 | 4.1966 | 3.8895 | 3.4191 | 2.8444 | 1.2485 | -1.2356 | -4.6238 | -8.6241 | -13.5904 | -25.0499 | -43.9549 | -49.6208 | -53.9105 | 2.9375 | 2.4767 | 2.0116 | 1.2306 | 0.22475 | -2.3861 | -5.8131 | -10.2235 | -15.4775 | -21.5637 | -35.6606 | -58.8999 | -65.6981 | -70.6444
|  |  | ST |  |  | 2.2769 | 2.1942 | 2.0592 | 1.8678 | 1.6356 | 0.64432 | -0.5634 | -1.9361 | -3.3013 | -4.7208 | -7.8747 | -15.5819 | -21.2462 | -24.171 | 4.7637 | 4.6744 | 4.5506 | 4.3716 | 4.1577 | 3.0476 | 1.7145 | 0.35279 | -0.99264 | -2.3183 | -5.1954 | -12.9036 | -20.5055 | -28.1663 | 3.4648 | 3.4097 | 3.3148 | 3.1662 | 2.9836 | 1.8529 | 0.47485 | -0.99146 | -2.4275 | -3.8866 | -7.0379 | -14.7684 | -20.5304 | -23.3944
|  |  | FS |  |  | 2.0195 | 1.7318 | 1.3692 | 0.71091 | 0.00036233 | -1.7219 | -3.678 | -6.0838 | -8.7683 | -11.381 | -17.0173 | -37.2353 | -50.5296 | -55.5013 | 4.7265 | 4.5383 | 4.3224 | 4.0317 | 3.6658 | 2.4461 | 0.96422 | -0.72569 | -2.6237 | -5.2649 | -11.4247 | -24.4819 | -32.6689 | -46.0897 | 3.4144 | 3.2561 | 3.0706 | 2.792 | 2.4452 | 1.2126 | -0.65316 | -2.9909 | -5.9768 | -9.3843 | -17.4671 | -33.7661 | -43.9898 | -50.8109
LALEHAM | EAST BEDFONT A | EAST BEDFONT A | MINIMUM HEADROOM | TQ 08394 73826 | YES | 3.1244 | 1.7632 | 0.42859 | 31.8815 | 28.6975 | 25.0358 | 19.6652 | 13.5627 | 6.6199 | -1.1952 | -18.3604 | -47.7567 | -72.3822 | -83.9342 | 13.0842 | 11.6352 | 10.1281 | 45.5164 | 43.1062 | 40.2436 | 36.5268 | 31.6937 | 25.5134 | 19.3575 | 7.5098 | -20.5517 | -57.6603 | -109.4724 | 1.6966 | -0.45071 | -2.5749 | 31.9522 | 28.6175 | 25.1549 | 20.0043 | 14.1923 | 7.8605 | 0.89395 | -15.4542 | -43.8267 | -65.3041 | -76.3042
|  |  | CT |  |  | 3.4495 | 2.3461 | 1.123 | 32.7057 | 31.2352 | 27.377 | 22.8767 | 16.8379 | 8.9355 | 1.1333 | -13.7522 | -45.9385 | -59.1857 | -64.8921 | 13.5143 | 12.3023 | 10.604 | 45.8285 | 43.4915 | 40.2436 | 36.5268 | 31.6937 | 25.5134 | 19.3575 | 7.5098 | -20.5517 | -39.192 | -59.9218 | 2.5022 | 0.94006 | -0.86051 | 33.9026 | 31.1305 | 27.3033 | 22.966 | 17.2571 | 10.1356 | 3.0691 | -11.1193 | -42.0727 | -54.5726 | -58.9392
|  |  | LW |  |  | 3.1244 | 1.7632 | 0.42859 | 31.8815 | 28.6975 | 25.0358 | 19.6652 | 13.5627 | 6.6199 | -1.1952 | -18.3604 | -47.7567 | -72.3822 | -83.9342 | 13.0842 | 11.6352 | 10.1281 | 45.5164 | 43.1062 | 40.5836 | 36.6829 | 32.3666 | 27.3148 | 21.693 | 9.2349 | -13.3495 | -34.5449 | -43.4631 | 1.6966 | -0.45071 | -2.5749 | 31.9522 | 28.6175 | 25.1549 | 20.0043 | 14.1923 | 7.8605 | 0.89395 | -15.4542 | -43.8267 | -65.3041 | -76.3042
|  |  | ST |  |  | 3.7591 | 2.9953 | 2.1844 | 34.2243 | 33.3294 | 32.2284 | 30.8367 | 29.6889 | 27.4475 | 23.6869 | 13.8997 | -16.5691 | -36.7471 | -43.2352 | 13.8489 | 12.9942 | 12.1387 | 48.395 | 47.0088 | 45.1519 | 42.8087 | 40.4249 | 37.6457 | 34.2822 | 25.2527 | -3.335 | -27.7092 | -49.4231 | 3.2631 | 2.4052 | 1.4069 | 37.6664 | 36.3776 | 34.605 | 32.3159 | 29.9175 | 27.1636 | 23.8354 | 14.7699 | -15.4092 | -34.7824 | -40.9405
|  |  | FS |  |  | 3.4495 | 2.3461 | 1.123 | 32.7057 | 31.2352 | 27.377 | 22.8767 | 16.8379 | 8.9355 | 1.1333 | -13.7522 | -45.9385 | -59.1857 | -64.8921 | 14.0917 | 13.2203 | 12.2483 | 48.3328 | 46.6347 | 44.6845 | 42.1879 | 39.2936 | 35.9031 | 31.9798 | 21.6409 | -13.151 | -57.6603 | -109.4724 | 3.3955 | 2.4914 | 1.4745 | 37.6535 | 36.1691 | 34.3817 | 32.034 | 29.2377 | 26.0276 | 22.3128 | 12.9276 | -19.492 | -52.2794 | -70.2629
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | FAREHAM T1A T2A (90MVAS) | MINIMUM HEADROOM | SU 56534 04031 | YES | 51.6001 | 48.8473 | 46.0376 | 42.0146 | 37.3906 | 32.0516 | 25.5123 | 18.355 | 9.893 | 0.96541 | -17.8816 | -73.2126 | -100.9681 | -114.4988 | 50.7213 | 49.6444 | 48.3809 | 46.9078 | 45.2126 | 43.0187 | 40.3008 | 35.7763 | 28.9891 | 21.3562 | 2.4812 | -36.5096 | -55.6726 | -65.7619 | 20.1069 | 17.5771 | 14.9676 | 11.014 | 6.5578 | 1.7412 | -4.2971 | -10.9444 | -18.8346 | -27.1901 | -44.8633 | -95.9662 | -122.3138 | -135.4399
|  |  | CT |  |  | 52.8389 | 50.8706 | 48.6399 | 45.2991 | 41.6762 | 37.0663 | 32.1732 | 25.9812 | 17.1882 | 7.9492 | -17.6088 | -73.2126 | -100.9681 | -114.4988 | 50.7804 | 49.6818 | 48.3809 | 46.9078 | 45.2204 | 43.0187 | 40.511 | 37.0606 | 29.7172 | 21.4211 | 2.4812 | -36.5096 | -55.6726 | -65.7619 | 21.4452 | 19.7042 | 17.7052 | 14.4864 | 10.9883 | 6.5934 | 1.8875 | -3.9704 | -12.4076 | -20.995 | -43.3668 | -95.9662 | -122.3138 | -135.4399
|  |  | LW |  |  | 51.6001 | 48.8473 | 46.0376 | 42.0146 | 37.3906 | 32.0516 | 25.5123 | 18.355 | 9.893 | 0.96541 | -17.8816 | -59.9274 | -78.1538 | -88.0615 | 50.7213 | 49.6444 | 48.4732 | 46.993 | 45.2126 | 43.1181 | 40.3008 | 35.7763 | 28.9891 | 21.3562 | 4.0515 | -26.4303 | -39.9814 | -48.8286 | 20.1069 | 17.5771 | 14.9676 | 11.014 | 6.5578 | 1.7412 | -4.2971 | -10.9444 | -18.8346 | -27.1901 | -44.8633 | -83.4142 | -101.1841 | -111.4994
|  |  | ST |  |  | 53.7035 | 52.4348 | 50.9756 | 49.4655 | 47.7443 | 45.6586 | 43.2992 | 40.6124 | 37.3757 | 33.7473 | 24.7184 | -3.2363 | -25.6476 | -41.1119 | 51.1309 | 50.3462 | 49.4151 | 48.4134 | 47.3313 | 46.0658 | 44.6718 | 43.2812 | 41.494 | 39.7132 | 35.5491 | 13.1493 | -11.0607 | -35.5232 | 22.3029 | 21.2321 | 19.9708 | 18.6174 | 17.0894 | 15.2507 | 13.0913 | 10.5015 | 7.3246 | 3.7474 | -5.2196 | -32.7018 | -54.4693 | -68.6547
|  |  | FS |  |  | 52.8389 | 50.8706 | 48.6399 | 45.2991 | 41.6762 | 37.0663 | 32.1732 | 25.9812 | 17.1882 | 7.9492 | -17.6088 | -73.2126 | -100.9681 | -114.4988 | 51.2374 | 50.6306 | 49.9161 | 49.1212 | 48.2251 | 47.1694 | 45.9901 | 44.6707 | 42.9997 | 41.1828 | 36.8625 | 15.689 | -18.8453 | -64.0546 | 22.4441 | 21.6052 | 20.6541 | 19.4329 | 18.0633 | 16.4716 | 14.6956 | 12.6636 | 9.9839 | 7.0462 | -0.25991 | -24.0112 | -49.3165 | -68.0525
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | FAREHAM T1B T2B (1X90, 1X60MVA) | MINIMUM HEADROOM | SU 56534 04031 | YES | 23.4259 | 22.4069 | 21.3275 | 19.032 | 16.5938 | 14.1319 | 11.1255 | 7.6378 | 3.5947 | -0.91431 | -10.7707 | -29.7841 | -48.2303 | -55.5656 | 29.5652 | 28.951 | 28.3059 | 27.1318 | 25.8191 | 24.4719 | 22.6747 | 20.517 | 17.95 | 15.1056 | 8.67 | -7.8029 | -20.5762 | -50.7028 | 20.3602 | 19.4291 | 18.4512 | 16.4316 | 14.2586 | 12.0594 | 9.2924 | 6.0395 | 2.2279 | -1.9128 | -10.9936 | -29.1778 | -46.8029 | -54.3488
|  |  | CT |  |  | 24.2809 | 23.6759 | 22.9575 | 21.1069 | 19.236 | 17.1253 | 14.8663 | 11.8202 | 7.569 | 3.2174 | -5.4332 | -26.5545 | -37.1226 | -41.7044 | 29.7323 | 29.1373 | 28.4702 | 27.3066 | 26.1029 | 24.6603 | 23.0857 | 20.9666 | 18.1258 | 15.1265 | 8.9235 | -7.8029 | -20.5762 | -35.0187 | 21.1059 | 20.5492 | 19.9266 | 18.303 | 16.6254 | 14.6868 | 12.6287 | 9.905 | 6.0533 | 2.0787 | -6.0138 | -25.9806 | -35.9444 | -40.3811
|  |  | LW |  |  | 23.4259 | 22.4069 | 21.3275 | 19.032 | 16.5938 | 14.1319 | 11.1255 | 7.6378 | 3.5947 | -0.91431 | -10.7707 | -29.7841 | -48.2303 | -55.5656 | 29.5652 | 28.951 | 28.3059 | 27.1318 | 25.8191 | 24.4719 | 22.6747 | 20.517 | 17.95 | 15.1056 | 8.67 | -4.0926 | -18.2718 | -24.7775 | 20.3602 | 19.4291 | 18.4512 | 16.4316 | 14.2586 | 12.0594 | 9.2924 | 6.0395 | 2.2279 | -1.9128 | -10.9936 | -29.1778 | -46.8029 | -54.3488
|  |  | ST |  |  | 24.953 | 24.7696 | 24.5214 | 23.9678 | 23.3646 | 22.7364 | 21.9379 | 20.8758 | 19.5132 | 17.8927 | 13.6305 | -1.8744 | -14.1135 | -21.6764 | 30.0644 | 29.7169 | 29.3286 | 28.7387 | 28.1189 | 27.4601 | 26.6438 | 25.6259 | 24.2845 | 22.7252 | 18.6577 | 3.3569 | -12.0579 | -28.0753 | 21.7154 | 21.5507 | 21.3539 | 20.9077 | 20.4095 | 19.8976 | 19.2276 | 18.3383 | 17.1497 | 15.6515 | 11.3906 | -3.879 | -15.9605 | -23.235
|  |  | FS |  |  | 24.2809 | 23.6759 | 22.9575 | 21.1069 | 19.236 | 17.1253 | 14.8663 | 11.8202 | 7.569 | 3.2174 | -5.4332 | -26.5545 | -37.1226 | -41.7044 | 30.0202 | 29.7366 | 29.3776 | 28.7784 | 28.125 | 27.413 | 26.5864 | 25.6076 | 24.3004 | 22.8151 | 19.0145 | 3.9001 | -19.2556 | -50.7028 | 21.6216 | 21.5336 | 21.3879 | 20.9065 | 20.3772 | 19.7877 | 19.1118 | 18.2986 | 17.2478 | 16.0723 | 12.9752 | 0.12533 | -15.2733 | -26.6165
BRAMLEY (FLEE) | FERNHURST | FERNHURST | MINIMUM HEADROOM | SU 72730 39772 | YES | 93.15 | 93.15 | 93.15 | 92.8805 | 92.6982 | 92.534 | 92.2843 | 92.1692 | 92.0167 | 91.8868 | 91.601 | 93.15 | 93.15 | 88.2488 | 86.4 | 86.4 | 86.4 | 86.0631 | 85.8352 | 85.63 | 85.3178 | 85.174 | 84.9833 | 84.8209 | 84.4638 | 86.4 | 86.4 | 80.2735 | 86.4 | 86.4 | 86.4 | 86.0631 | 85.8352 | 85.63 | 85.3178 | 85.174 | 84.9833 | 84.8209 | 84.4638 | 86.4 | 86.4 | 80.2735
|  |  | CT |  |  | 93.15 | 93.15 | 93.15 | 93.1137 | 93.0491 | 92.9724 | 92.8344 | 92.7505 | 92.6787 | 92.519 | 92.2292 | 93.15 | 93.15 | 89.8428 | 86.4 | 86.4 | 86.4 | 86.3546 | 86.2739 | 86.178 | 86.0055 | 85.9006 | 85.8109 | 85.6113 | 85.249 | 86.4 | 86.4 | 82.2661 | 86.4 | 86.4 | 86.4 | 86.3546 | 86.2739 | 86.178 | 86.0055 | 85.9006 | 85.8109 | 85.6113 | 85.249 | 86.4 | 86.4 | 82.2661
|  |  | LW |  |  | 93.15 | 93.15 | 93.15 | 93.031 | 92.8983 | 92.7194 | 92.5248 | 92.3619 | 92.274 | 92.1828 | 92.0234 | 93.15 | 93.15 | 88.8576 | 86.4 | 86.4 | 86.4 | 86.2513 | 86.0853 | 85.8618 | 85.6184 | 85.4148 | 85.305 | 85.191 | 84.9918 | 86.4 | 86.4 | 81.0345 | 86.4 | 86.4 | 86.4 | 86.2513 | 86.0853 | 85.8618 | 85.6184 | 85.4148 | 85.305 | 85.191 | 84.9918 | 86.4 | 86.4 | 81.0345
|  |  | ST |  |  | 93.15 | 93.15 | 93.15 | 92.8805 | 92.6982 | 92.534 | 92.2843 | 92.1692 | 92.0167 | 91.8868 | 91.601 | 93.15 | 93.15 | 88.2488 | 86.4 | 86.4 | 86.4 | 86.0631 | 85.8352 | 85.63 | 85.3178 | 85.174 | 84.9833 | 84.8209 | 84.4638 | 86.4 | 86.4 | 80.2735 | 86.4 | 86.4 | 86.4 | 86.0631 | 85.8352 | 85.63 | 85.3178 | 85.174 | 84.9833 | 84.8209 | 84.4638 | 86.4 | 86.4 | 80.2735
|  |  | FS |  |  | 93.15 | 93.15 | 93.15 | 93.1137 | 93.0491 | 92.9724 | 92.8344 | 92.7505 | 92.6787 | 92.519 | 92.2292 | 93.15 | 93.15 | 89.8428 | 86.4 | 86.4 | 86.4 | 86.3265 | 86.2529 | 86.1641 | 86.0753 | 86.0018 | 85.9281 | 85.8571 | 85.7149 | 86.4 | 86.4 | 85.0428 | 86.4 | 86.4 | 86.4 | 86.3265 | 86.2529 | 86.1641 | 86.0753 | 86.0018 | 85.9281 | 85.8571 | 85.7149 | 86.4 | 86.4 | 85.0428
LOVEDEAN GSP | FORT WIDLEY | FORT WIDLEY | MINIMUM HEADROOM | SU 64948 05441 | YES | 31.8284 | 30.7008 | 29.4769 | 27.6581 | 25.5875 | 23.2524 | 20.3939 | 17.3049 | 13.3065 | 9.1586 | -2.0414 | -24.4808 | -33.1927 | -38.9854 | 35.3908 | 34.7105 | 33.967 | 33.0464 | 31.9853 | 30.765 | 29.1821 | 27.3993 | 24.9469 | 22.2899 | 13.9391 | -2.2461 | -8.6766 | -13.6896 | 28.7224 | 27.7372 | 26.6642 | 25.0789 | 23.2767 | 21.2402 | 18.7077 | 15.933 | 12.2795 | 8.439 | -2.921 | -24.2231 | -32.6912 | -38.6345
|  |  | CT |  |  | 32.6554 | 31.9419 | 31.2018 | 30.0284 | 28.618 | 26.9088 | 24.765 | 22.3618 | 18.4839 | 14.4044 | 6.6569 | -10.581 | -20.5896 | -26.457 | 35.6691 | 35.0818 | 34.4877 | 33.8503 | 33.0539 | 32.0451 | 30.6946 | 29.1575 | 26.721 | 24.0326 | 19.0403 | 7.7985 | 0.27425 | -7.2244 | 29.4171 | 28.7847 | 28.1271 | 27.1136 | 25.8807 | 24.366 | 22.4187 | 20.2326 | 16.6964 | 12.9172 | 5.7414 | -10.1535 | -19.2869 | -24.7397
|  |  | LW |  |  | 31.8284 | 30.7008 | 29.4769 | 27.6581 | 25.5875 | 23.2524 | 20.3939 | 17.3049 | 13.3065 | 9.1586 | -2.0414 | -24.4808 | -33.1927 | -38.9854 | 35.3908 | 34.7105 | 33.967 | 33.0464 | 31.9853 | 30.765 | 29.1821 | 27.3993 | 24.9469 | 22.2899 | 13.9391 | -2.2461 | -8.6766 | -13.6896 | 28.7224 | 27.7372 | 26.6642 | 25.0789 | 23.2767 | 21.2402 | 18.7077 | 15.933 | 12.2795 | 8.439 | -2.921 | -24.2231 | -32.6912 | -38.6345
|  |  | ST |  |  | 32.8212 | 32.1982 | 31.5495 | 30.9669 | 30.2626 | 29.3763 | 28.1634 | 26.8418 | 24.9254 | 22.7927 | 18.5088 | 4.3923 | -6.424 | -13.5328 | 35.7022 | 35.1336 | 34.5719 | 34.0981 | 33.5498 | 32.871 | 31.893 | 30.8249 | 29.185 | 27.4298 | 23.9258 | 12.2175 | 2.4699 | -5.3608 | 29.5341 | 28.9642 | 28.3867 | 27.8629 | 27.2446 | 26.4677 | 25.3548 | 24.1324 | 22.2907 | 20.249 | 16.1178 | 2.4494 | -8.0007 | -14.6204
|  |  | FS |  |  | 32.6554 | 31.9419 | 31.2018 | 30.0284 | 28.618 | 26.9088 | 24.765 | 22.3618 | 18.4839 | 14.4044 | 6.6569 | -10.581 | -20.5896 | -26.457 | 35.802 | 35.3257 | 34.7918 | 34.2629 | 33.6715 | 32.9381 | 32.0596 | 30.9849 | 29.5362 | 28.0183 | 24.8313 | 14.8214 | 3.0749 | -10.1307 | 29.6394 | 29.176 | 28.6467 | 28.0439 | 27.3635 | 26.5091 | 25.4998 | 24.2615 | 22.5257 | 20.7281 | 17.0976 | 6.1504 | -4.7869 | -12.9466
MELKSHAM GSP | FROME BSP | FROME BSP | MINIMUM HEADROOM | ST 78803 48019 | YES | -5.2203 | -9.5722 | -14.1096 | -19.7364 | -26.5088 | -33.5513 | -43.9788 | -56.2217 | -70.0577 | -85.2912 | -118.5263 | -176.7077 | -198.551 | -219.3077 | 15.8953 | 13.4644 | 10.9049 | 7.754 | 3.8269 | -0.87193 | -8.3471 | -17.2601 | -27.1655 | -38.1355 | -62.2505 | -103.6249 | -130.8764 | -158.3356 | -16.0965 | -19.988 | -24.0535 | -29.1415 | -35.2475 | -41.6474 | -51.116 | -62.3763 | -75.7577 | -90.4594 | -122.5807 | -178.5686 | -198.8878 | -215.4251
|  |  | CT |  |  | -3.8919 | -7.198 | -11.1275 | -16.1182 | -21.4935 | -28.7424 | -36.8009 | -47.828 | -61.9919 | -76.0532 | -102.6704 | -164.2709 | -194.8108 | -208.255 | 16.4094 | 14.332 | 11.9166 | 9.083 | 5.372 | 0.1142 | -5.9079 | -14.2761 | -24.5671 | -34.825 | -54.2206 | -99.9996 | -124.3541 | -141.5021 | -14.8056 | -17.7306 | -21.2126 | -25.623 | -30.3889 | -36.8169 | -44.0895 | -54.8183 | -68.4993 | -82.058 | -107.6723 | -167.0603 | -195.9712 | -208.6935
|  |  | LW |  |  | -5.2203 | -9.5722 | -14.1096 | -19.7364 | -26.5088 | -33.5513 | -43.9788 | -56.2217 | -70.0577 | -85.2912 | -118.5263 | -176.7077 | -198.551 | -219.3077 | 15.8953 | 13.4644 | 10.9049 | 7.754 | 3.8269 | -0.87193 | -8.3471 | -17.2601 | -27.1655 | -38.1355 | -62.2505 | -103.6249 | -130.8764 | -148.109 | -16.0965 | -19.988 | -24.0535 | -29.1415 | -35.2475 | -41.6474 | -51.116 | -62.3763 | -75.7577 | -90.4594 | -122.5807 | -178.5686 | -198.8878 | -215.4251
|  |  | ST |  |  | -2.0743 | -3.81 | -5.9874 | -8.9639 | -12.1616 | -15.8192 | -20.4634 | -25.6599 | -31.7281 | -38.8814 | -57.8074 | -117.9345 | -159.4609 | -177.4904 | 17.3295 | 16.0482 | 14.5245 | 12.4075 | 10.3155 | 7.9877 | 4.4288 | 0.18452 | -4.8481 | -10.6921 | -25.9836 | -74.5568 | -111.1307 | -130.8872 | -13.1588 | -14.6926 | -16.619 | -19.3487 | -22.2029 | -25.4591 | -29.7172 | -34.3594 | -40.0563 | -47.1812 | -65.8931 | -125.3555 | -166.3725 | -183.7344
|  |  | FS |  |  | -3.8919 | -7.198 | -11.1275 | -16.1182 | -21.4935 | -28.7424 | -36.8009 | -47.828 | -61.9919 | -76.0532 | -102.6704 | -164.2709 | -194.8108 | -208.255 | 17.4848 | 16.3849 | 15.0644 | 13.3672 | 11.473 | 9.3097 | 6.5183 | 2.6961 | -1.7842 | -6.8701 | -19.8772 | -64.6643 | -115.7192 | -158.3356 | -12.962 | -14.2915 | -15.9107 | -18.2093 | -20.8064 | -23.8049 | -27.3897 | -31.6187 | -36.651 | -42.2923 | -57.7582 | -110.9883 | -166.8756 | -201.3039
MINETY GSP | GALILEO | GALILEO | MINIMUM HEADROOM | SU 10596 83733 | NO | 26.5001 | 25.5682 | 24.5837 | 23.3123 | 21.7768 | 19.715 | 16.9809 | 13.0778 | 8.7378 | 3.8544 | -7.073 | -25.0221 | -30.2864 | -32.7325 | 24.5483 | 23.8396 | 22.985 | 21.9948 | 20.9052 | 19.1607 | 17.2527 | 14.1513 | 10.3518 | 6.5142 | -2.3387 | -16.4171 | -27.3587 | -40.2981 | 25.8282 | 25.0038 | 24.1594 | 23.0028 | 21.556 | 19.2733 | 16.6085 | 12.5449 | 8.0337 | 2.9536 | -8.1305 | -25.895 | -35.5683 | -48.0378
|  |  | CT |  |  | 26.5001 | 25.6309 | 24.5837 | 23.3123 | 21.9187 | 19.715 | 17.3135 | 13.5672 | 9.0182 | 4.6603 | -3.5658 | -22.9849 | -30.2864 | -32.7325 | 24.5483 | 23.8396 | 22.985 | 21.9948 | 20.9052 | 19.1607 | 17.2527 | 14.1513 | 10.3518 | 6.7112 | 0.084675 | -15.4642 | -21.771 | -24.8974 | 25.8282 | 25.0746 | 24.1672 | 23.0028 | 21.5677 | 19.2733 | 16.7685 | 12.8375 | 8.1012 | 3.5691 | -4.6643 | -23.8844 | -31.0959 | -33.5276
|  |  | LW |  |  | 26.555 | 25.5682 | 24.6014 | 23.4074 | 21.7768 | 20.0795 | 16.9809 | 13.0778 | 8.7378 | 3.8544 | -7.073 | -25.0221 | -28.5071 | -23.2467 | 24.6567 | 23.8867 | 23.1371 | 22.2465 | 21.0045 | 19.7045 | 17.2767 | 14.1625 | 10.5681 | 6.5142 | -2.3387 | -16.4171 | -19.1165 | -14.9807 | 25.8689 | 25.0038 | 24.1594 | 23.1029 | 21.556 | 19.824 | 16.6085 | 12.5449 | 8.0337 | 2.9536 | -8.1305 | -25.895 | -29.3589 | -24.1948
|  |  | ST |  |  | 27.0351 | 26.7929 | 26.4117 | 25.8686 | 25.1484 | 24.1821 | 22.9084 | 21.2658 | 19.3478 | 16.9303 | 10.2038 | -13.1062 | -28.3076 | -32.1446 | 25.0018 | 24.7624 | 24.4374 | 23.977 | 23.3724 | 22.5706 | 21.5146 | 20.164 | 18.5699 | 16.5611 | 10.6789 | -8.4803 | -21.3149 | -25.5103 | 26.3295 | 26.0884 | 25.7574 | 25.2817 | 24.655 | 23.815 | 22.5067 | 20.763 | 18.7244 | 16.1554 | 9.0108 | -14.3209 | -29.4724 | -33.2964
|  |  | FS |  |  | 26.5001 | 25.6309 | 24.5837 | 23.3123 | 21.9187 | 19.715 | 17.3135 | 13.5672 | 9.0182 | 4.6603 | -3.5658 | -22.9849 | -30.2864 | -32.7325 | 24.9278 | 24.6371 | 24.2627 | 23.77 | 23.1124 | 22.2699 | 21.1264 | 19.6603 | 17.941 | 14.8685 | 6.4662 | -9.3772 | -27.3587 | -40.2981 | 26.2396 | 25.9376 | 25.5437 | 25.0075 | 24.2838 | 23.351 | 22.0793 | 19.8243 | 16.6693 | 12.7424 | 2.8142 | -16.663 | -35.5683 | -48.0378
WILLESDEN GSP | GREENFORD | GREENFORD | MINIMUM HEADROOM | TQ 14695 83785 | YES | 56.7 | 56.7 | 56.7 | 56.6439 | 56.5973 | 56.5243 | 56.4449 | 56.3785 | 56.3638 | 56.3485 | 56.3219 | 56.2477 | 56.2324 | 56.2324 | 53.4 | 53.4 | 53.4 | 53.3299 | 53.2716 | 53.1804 | 53.0811 | 52.9981 | 52.9797 | 52.9607 | 52.9274 | 52.8347 | 52.8154 | 52.8154 | 53.4 | 53.4 | 53.4 | 53.3299 | 53.2716 | 53.1804 | 53.0811 | 52.9981 | 52.9797 | 52.9607 | 52.9274 | 52.8347 | 52.8154 | 52.8154
|  |  | CT |  |  | 56.7 | 56.7 | 56.7 | 56.6924 | 56.679 | 56.6631 | 56.6343 | 56.6169 | 56.6169 | 56.6169 | 56.6169 | 56.6169 | 56.6169 | 56.6169 | 53.4 | 53.4 | 53.4 | 53.3905 | 53.3738 | 53.3538 | 53.3179 | 53.2961 | 53.2961 | 53.2961 | 53.2961 | 53.2961 | 53.2961 | 53.2961 | 53.4 | 53.4 | 53.4 | 53.3905 | 53.3738 | 53.3538 | 53.3179 | 53.2961 | 53.2961 | 53.2961 | 53.2961 | 53.2961 | 53.2961 | 53.2961
|  |  | LW |  |  | 56.7 | 56.7 | 56.7 | 56.6515 | 56.5973 | 56.5243 | 56.4449 | 56.3785 | 56.3638 | 56.3485 | 56.3219 | 56.2477 | 56.2324 | 56.2324 | 53.4 | 53.4 | 53.4 | 53.3393 | 53.2716 | 53.1804 | 53.0811 | 52.9981 | 52.9797 | 52.9607 | 52.9274 | 52.8347 | 52.8154 | 52.8154 | 53.4 | 53.4 | 53.4 | 53.3393 | 53.2716 | 53.1804 | 53.0811 | 52.9981 | 52.9797 | 52.9607 | 52.9274 | 52.8347 | 52.8154 | 52.8154
|  |  | ST |  |  | 56.7 | 56.7 | 56.7 | 56.6439 | 56.606 | 56.5718 | 56.5199 | 56.4959 | 56.4959 | 56.4959 | 56.4959 | 56.4959 | 56.4959 | 56.4959 | 53.4 | 53.4 | 53.4 | 53.3299 | 53.2825 | 53.2398 | 53.1749 | 53.1449 | 53.1449 | 53.1449 | 53.1449 | 53.1449 | 53.1449 | 53.1449 | 53.4 | 53.4 | 53.4 | 53.3299 | 53.2825 | 53.2398 | 53.1749 | 53.1449 | 53.1449 | 53.1449 | 53.1449 | 53.1449 | 53.1449 | 53.1449
|  |  | FS |  |  | 56.7 | 56.7 | 56.7 | 56.6924 | 56.679 | 56.6631 | 56.6343 | 56.6169 | 56.6169 | 56.6169 | 56.6169 | 56.6169 | 56.6169 | 56.6169 | 53.4 | 53.4 | 53.4 | 53.3847 | 53.3694 | 53.3509 | 53.3325 | 53.3172 | 53.3172 | 53.3172 | 53.3172 | 53.3172 | 53.3172 | 53.3172 | 53.4 | 53.4 | 53.4 | 53.3847 | 53.3694 | 53.3509 | 53.3325 | 53.3172 | 53.3172 | 53.3172 | 53.3172 | 53.3172 | 53.3172 | 53.3172
LOVEDEAN GSP | HAVANT | HAVANT | MINIMUM HEADROOM | SU 70625 05720 | YES | 5.0456 | 0.41364 | -4.3121 | -11.2567 | -19.7447 | -28.3153 | -40.8817 | -55.7455 | -73.7638 | -93.5801 | -136.3742 | -210.5712 | -250.8931 | -269.4661 | 36.5333 | 33.2607 | 29.903 | 25.4512 | 19.9329 | 13.3385 | 4.818 | -6.5481 | -20.2892 | -34.4244 | -64.71 | -124.9887 | -159.999 | -226.4432 | 2.8809 | -1.1106 | -5.197 | -11.3157 | -18.7871 | -26.3898 | -38.2481 | -53.5473 | -70.9216 | -90.0355 | -131.373 | -202.4019 | -240.3063 | -257.5541
|  |  | CT |  |  | 6.5542 | 3.0589 | -1.043 | -7.2888 | -14.332 | -23.2989 | -33.2809 | -47.8853 | -67.5101 | -86.9549 | -124.2787 | -210.2966 | -250.8931 | -269.4661 | 36.5678 | 33.5126 | 29.903 | 25.4512 | 20.3236 | 13.3385 | 5.4891 | -6.0033 | -20.2892 | -34.4244 | -61.636 | -124.9887 | -158.9448 | -185.5619 | 4.2919 | 1.2926 | -2.23 | -7.6707 | -13.8439 | -22.1706 | -32.314 | -46.8178 | -65.6583 | -84.3353 | -120.1119 | -202.2378 | -240.3063 | -257.5541
|  |  | LW |  |  | 5.0456 | 0.41364 | -4.3121 | -11.2567 | -19.7447 | -28.3153 | -40.8817 | -55.7455 | -73.7638 | -93.5801 | -136.3742 | -210.5712 | -236.0455 | -230.4044 | 36.5333 | 33.2607 | 29.9483 | 25.5896 | 19.9329 | 14.1683 | 4.818 | -6.5481 | -19.3376 | -33.5354 | -64.71 | -116.3115 | -132.492 | -134.5474 | 2.8809 | -1.1106 | -5.197 | -11.3157 | -18.7871 | -26.3898 | -38.2481 | -53.5473 | -70.9216 | -90.0355 | -131.373 | -202.4019 | -226.3002 | -220.3191
|  |  | ST |  |  | 8.6313 | 7.0035 | 5.0221 | 2.3374 | -1.0622 | -4.6525 | -9.2612 | -14.838 | -21.548 | -30.4562 | -54.103 | -131.3857 | -186.8377 | -210.5934 | 38.1771 | 36.7042 | 34.899 | 32.4826 | 29.4324 | 26.049 | 21.6126 | 16.2189 | 9.7679 | 1.9472 | -18.8879 | -84.781 | -134.1895 | -162.8811 | 6.1326 | 4.7706 | 3.1134 | 0.83482 | -2.0426 | -5.0615 | -8.9892 | -14.694 | -21.8682 | -30.5964 | -53.8813 | -129.0846 | -183.596 | -206.2323
|  |  | FS |  |  | 6.5542 | 3.0589 | -1.043 | -7.2888 | -14.332 | -23.2989 | -33.2809 | -47.8853 | -67.5101 | -86.9549 | -124.2787 | -210.2966 | -250.8931 | -269.4661 | 37.9607 | 36.4246 | 34.5232 | 32.0889 | 29.0855 | 25.4871 | 20.999 | 15.3457 | 8.5568 | -0.47457 | -24.6742 | -85.1592 | -159.999 | -226.4432 | 5.9229 | 4.564 | 2.8634 | 0.43059 | -2.5511 | -6.0848 | -10.4861 | -16.142 | -23.9739 | -32.9329 | -55.6093 | -130.1533 | -206.1075 | -253.428
NORTH HYDE GSP | HAYES | HAYES | MINIMUM HEADROOM | TQ 09519 79541 | YES | 20.1448 | 19.0471 | 17.2866 | 16.2468 | 15.0124 | 11.401 | 7.1686 | 3.5293 | 0.29016 | -2.6263 | -7.7127 | -17.8858 | -22.5796 | -24.7136 | 24.6538 | 24.35 | 23.7911 | 23.5821 | 23.2484 | 19.9776 | 15.9881 | 12.7729 | 10.08 | 7.3105 | 2.7367 | -8.0799 | -26.6975 | -61.0387 | 20.8582 | 20.4322 | 19.3236 | 18.5404 | 17.5795 | 13.5334 | 8.7516 | 4.731 | 1.2625 | -1.7968 | -6.9898 | -17.2406 | -21.7806 | -23.6112
|  |  | CT |  |  | 20.287 | 19.8448 | 18.5716 | 17.8921 | 17.0427 | 13.8069 | 9.9917 | 6.6403 | 3.373 | 0.47217 | -4.3563 | -15.0768 | -21.3837 | -24.7136 | 24.6538 | 24.3782 | 23.7911 | 23.6491 | 23.4039 | 20.2428 | 16.4914 | 13.2542 | 10.08 | 7.3105 | 2.7367 | -8.0799 | -19.1732 | -35.1188 | 20.8736 | 20.5124 | 19.738 | 19.6097 | 19.0779 | 15.4843 | 11.2364 | 7.5849 | 4.1316 | 1.1293 | -3.7153 | -14.0051 | -19.8388 | -22.8227
|  |  | LW |  |  | 20.1448 | 19.0471 | 17.2866 | 16.2468 | 15.0124 | 11.401 | 7.1686 | 3.5293 | 0.29016 | -2.6263 | -7.7127 | -17.8858 | -22.5796 | -24.5284 | 24.6624 | 24.35 | 23.8036 | 23.5821 | 23.2484 | 19.9776 | 15.9881 | 12.7729 | 10.0935 | 7.5987 | 3.17 | -4.366 | -7.212 | -8.4781 | 20.8582 | 20.4322 | 19.3236 | 18.5404 | 17.5795 | 13.5334 | 8.7516 | 4.731 | 1.2625 | -1.7968 | -6.9898 | -17.2406 | -21.7806 | -23.6112
|  |  | ST |  |  | 20.3536 | 19.9626 | 19.0769 | 18.9062 | 18.6298 | 16.29 | 13.4993 | 11.0292 | 9.0164 | 7.302 | 4.5702 | -1.1322 | -5.735 | -10.1784 | 24.72 | 24.495 | 23.955 | 23.7732 | 23.5203 | 20.722 | 17.4178 | 14.5326 | 12.1377 | 10.1021 | 6.4955 | -2.1213 | -12.994 | -29.1743 | 20.9432 | 20.6258 | 19.8976 | 19.7281 | 19.4856 | 16.6864 | 13.3741 | 10.4796 | 8.1111 | 6.1077 | 2.9561 | -2.4071 | -6.3383 | -10.3088
|  |  | FS |  |  | 20.287 | 19.8448 | 18.5716 | 17.8921 | 17.0427 | 13.8069 | 9.9917 | 6.6403 | 3.373 | 0.47217 | -4.3563 | -15.0768 | -21.3837 | -24.7136 | 24.7373 | 24.5206 | 24.1005 | 23.9654 | 23.7613 | 21.1788 | 18.1984 | 15.3352 | 12.6653 | 9.9557 | 4.7058 | -7.2202 | -26.6975 | -61.0387 | 20.9699 | 20.6701 | 20.0761 | 19.9612 | 19.7836 | 17.2225 | 14.2729 | 11.4517 | 9.1339 | 7.0013 | 3.2091 | -2.7101 | -8.0352 | -12.6073
COWLEY GSP | HEADINGTON BSP | HEADINGTON BSP | MINIMUM HEADROOM | SP 54454 08145 | NO | 15.5374 | 13.5748 | 11.0421 | 7.3411 | 3.2283 | -0.5651 | -5.1081 | -9.9549 | -15.5288 | -21.4603 | -38.807 | -117.0973 | -131.032 | -99.3839 | 29.055 | 27.7524 | 26.0749 | 23.6993 | 20.9726 | 18.3867 | 15.1218 | 11.6413 | 7.5028 | 1.1391 | -14.4196 | -71.7973 | -111.6654 | -82.5766 | 27.8791 | 26.1703 | 23.9873 | 20.8027 | 17.0771 | 13.2425 | 7.8186 | 1.5634 | -5.9001 | -14.3847 | -33.993 | -102.9756 | -130.4257 | -93.75
|  |  | CT |  |  | 16.1984 | 15.2149 | 13.2254 | 10.3013 | 7.0229 | 4.1087 | 0.54176 | -3.5583 | -9.729 | -16.3509 | -29.0249 | -105.1151 | -122.6439 | -71.7827 | 29.4063 | 28.2562 | 26.6502 | 24.6243 | 22.2522 | 20.087 | 17.1695 | 13.614 | 9.0071 | 4.0827 | -5.7614 | -66.9642 | -85.1167 | -53.9124 | 28.5693 | 27.3221 | 25.4788 | 22.8919 | 19.9085 | 16.9684 | 13.2933 | 8.8472 | 2.9055 | -3.4181 | -15.703 | -90.7216 | -107.6305 | -57.4623
|  |  | LW |  |  | 15.5374 | 13.5748 | 11.0421 | 7.3411 | 3.2283 | -0.5651 | -5.1081 | -9.9549 | -15.5288 | -21.4603 | -38.807 | -117.0973 | -131.032 | -99.3839 | 29.055 | 27.7524 | 26.0749 | 23.6993 | 20.9726 | 18.3867 | 15.1218 | 11.6413 | 7.5028 | 1.1391 | -14.4196 | -71.7973 | -83.0672 | -62.9408 | 27.8791 | 26.1703 | 23.9873 | 20.8027 | 17.0771 | 13.2425 | 7.8186 | 1.5634 | -5.9001 | -14.3847 | -33.993 | -102.9756 | -117.1942 | -93.75
|  |  | ST |  |  | 16.3224 | 15.5812 | 14.4594 | 12.3526 | 10.2571 | 8.824 | 6.8942 | 5.1509 | 2.8523 | 0.56994 | -5.8095 | -74.3443 | -102.9517 | -49.5599 | 29.6498 | 28.764 | 27.4759 | 25.5918 | 23.7036 | 22.3233 | 20.3952 | 18.6857 | 16.3424 | 13.8358 | 7.8702 | -51.0612 | -79.7857 | -44.1812 | 28.6766 | 27.9601 | 26.7979 | 24.7716 | 22.7547 | 21.2008 | 19.0694 | 17.0463 | 14.4082 | 11.6424 | 5.0873 | -66.141 | -95.6076 | -39.0169
|  |  | FS |  |  | 16.1984 | 15.2149 | 13.2254 | 10.3013 | 7.0229 | 4.1087 | 0.54176 | -3.5583 | -9.729 | -16.3509 | -29.0249 | -105.1151 | -122.6439 | -71.7827 | 29.8435 | 28.774 | 27.3675 | 25.567 | 23.5371 | 21.3965 | 18.7163 | 15.448 | 11.641 | 7.5763 | -1.4926 | -66.0626 | -111.6654 | -82.5766 | 28.9905 | 27.7458 | 26.1142 | 24.0316 | 21.7169 | 19.2814 | 16.2177 | 12.3995 | 7.9676 | 3.2685 | -7.0326 | -83.4244 | -130.4257 | -72.0592
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU 84773 92191 | YES | -0.19068 | -2.1595 | -3.8352 | -6.4884 | -9.4065 | -12.4832 | -16.0428 | -20.0014 | -28.0589 | -39.2264 | -66.0628 | -114.318 | -133.1776 | -141.9746 | 15.5159 | 14.7001 | 13.9005 | 12.7839 | 11.1623 | 9.1216 | 4.8698 | -0.79263 | -7.5801 | -15.7338 | -35.5731 | -70.7277 | -84.1412 | -112.8043 | 3.2134 | 1.5451 | 0.060342 | -2.3437 | -5.0082 | -7.8387 | -11.1458 | -15.3413 | -24.285 | -34.8986 | -60.4469 | -106.2913 | -124.1943 | -132.7195
|  |  | CT |  |  | 1.5004 | 0.5205 | -0.2494 | -2.1191 | -4.2335 | -6.5409 | -9.0951 | -11.9971 | -16.6838 | -21.5481 | -37.778 | -75.596 | -95.6935 | -103.9202 | 15.6339 | 15.1367 | 14.5439 | 13.7959 | 12.7339 | 11.3043 | 9.4756 | 6.8992 | 2.5637 | -2.6349 | -14.4379 | -40.3554 | -53.4858 | -65.2724 | 4.6248 | 3.7871 | 3.0876 | 1.4447 | -0.43176 | -2.5081 | -4.8667 | -7.5646 | -11.8501 | -17.5284 | -33.4094 | -69.017 | -87.7901 | -95.4949
|  |  | LW |  |  | -0.19068 | -2.1595 | -3.8352 | -6.4884 | -9.4065 | -12.4832 | -16.0428 | -20.0014 | -28.0589 | -39.2264 | -66.0628 | -114.318 | -133.1776 | -141.9746 | 15.5159 | 14.7001 | 13.9005 | 12.7839 | 11.1623 | 9.1216 | 4.8698 | -0.79263 | -7.5801 | -15.7338 | -35.5731 | -70.7277 | -84.1412 | -90.9476 | 3.2134 | 1.5451 | 0.060342 | -2.3437 | -5.0082 | -7.8387 | -11.1458 | -15.3413 | -24.285 | -34.8986 | -60.4469 | -106.2913 | -124.1943 | -132.7195
|  |  | ST |  |  | 2.1743 | 1.5898 | 1.214 | 0.52536 | -0.31499 | -1.2097 | -2.3395 | -3.5886 | -5.0489 | -6.7068 | -10.7428 | -25.131 | -36.6638 | -46.6139 | 15.9703 | 15.7508 | 15.5704 | 15.1151 | 14.5465 | 13.9876 | 13.1691 | 12.3002 | 11.2715 | 10.0616 | 6.9825 | -8.768 | -27.0482 | -52.4356 | 5.2106 | 4.7223 | 4.3721 | 3.6756 | 2.8529 | 1.9764 | 0.85738 | -0.36623 | -1.7941 | -3.4169 | -7.3733 | -21.1801 | -31.9299 | -40.8089
|  |  | FS |  |  | 1.5004 | 0.5205 | -0.2494 | -2.1191 | -4.2335 | -6.5409 | -9.0951 | -11.9971 | -16.6838 | -21.5481 | -37.778 | -75.596 | -95.6935 | -103.9202 | 15.8795 | 15.5022 | 15.1452 | 14.6532 | 13.9205 | 12.9861 | 11.7429 | 10.1679 | 8.2783 | 4.7314 | -3.9131 | -31.5909 | -65.9655 | -112.8043 | 4.9785 | 4.185 | 3.5085 | 2.4449 | 1.1256 | -0.35974 | -2.4192 | -4.9723 | -8.0843 | -11.5662 | -19.6916 | -49.2667 | -80.4433 | -96.2782
IVER 66KV | HILLINGDON | HILLINGDON | MINIMUM HEADROOM | TQ 07470 82827 | YES | -1.3936 | -2.2802 | -3.6504 | -4.9802 | -6.5609 | -8.9809 | -11.7917 | -14.5376 | -17.3566 | -20.1458 | -25.6098 | -36.4359 | -42.6881 | -46.8777 | 0.5475 | 0.098842 | -0.5779 | -1.1816 | -1.9294 | -3.6601 | -5.7607 | -7.7163 | -9.5444 | -11.3745 | -15.0967 | -25.047 | -36.542 | -62.6349 | -4.2658 | -4.9961 | -6.0745 | -7.213 | -8.564 | -10.9215 | -13.7208 | -16.4114 | -19.0885 | -21.7205 | -26.8381 | -36.7531 | -41.8244 | -45.4351
|  |  | CT |  |  | -0.72995 | -1.2362 | -2.185 | -3.1401 | -4.2727 | -6.2949 | -8.4847 | -10.761 | -13.647 | -16.4298 | -21.6449 | -34.6746 | -42.6881 | -46.8777 | 0.66849 | 0.25301 | -0.38906 | -0.96707 | -1.6558 | -3.3961 | -5.3442 | -7.2777 | -9.3799 | -11.3745 | -15.0967 | -25.047 | -34.689 | -47.1359 | -3.7329 | -4.1559 | -4.9038 | -5.7242 | -6.687 | -8.7168 | -10.9522 | -13.2246 | -15.948 | -18.5338 | -23.2911 | -34.8849 | -41.8244 | -45.4351
|  |  | LW |  |  | -1.3936 | -2.2802 | -3.6504 | -4.9802 | -6.5609 | -8.9809 | -11.7917 | -14.5376 | -17.3566 | -20.1458 | -25.6098 | -36.4359 | -41.5334 | -43.2582 | 0.5475 | 0.098842 | -0.5779 | -1.1816 | -1.9294 | -3.6601 | -5.7607 | -7.7163 | -9.5444 | -11.3106 | -14.6745 | -20.9112 | -23.3995 | -23.8956 | -4.2658 | -4.9961 | -6.0745 | -7.213 | -8.564 | -10.9215 | -13.7208 | -16.4114 | -19.0885 | -21.7205 | -26.8381 | -36.7531 | -41.1002 | -42.3494
|  |  | ST |  |  | -0.46771 | -0.80213 | -1.575 | -1.7697 | -2.0879 | -3.1029 | -4.2544 | -5.3739 | -6.3765 | -7.3754 | -9.4001 | -16.2252 | -22.4062 | -28.1614 | 0.80516 | 0.49394 | -0.037779 | -0.35435 | -0.7461 | -2.003 | -3.4472 | -4.8206 | -6.1061 | -7.3785 | -9.9906 | -17.8003 | -27.0458 | -39.9555 | -3.4995 | -3.7612 | -4.3417 | -4.543 | -4.8348 | -5.9775 | -7.2963 | -8.5453 | -9.6499 | -10.7291 | -12.8859 | -19.4529 | -25.0981 | -29.8642
|  |  | FS |  |  | -0.72995 | -1.2362 | -2.185 | -3.1401 | -4.2727 | -6.2949 | -8.4847 | -10.761 | -13.647 | -16.4298 | -21.6449 | -34.6746 | -42.6881 | -46.8777 | 0.80067 | 0.49314 | -0.028737 | -0.35141 | -0.76138 | -1.9729 | -3.3713 | -4.7992 | -6.2969 | -7.7844 | -11.0279 | -20.9184 | -36.542 | -62.6349 | -3.4909 | -3.7164 | -4.2123 | -4.4181 | -4.7071 | -5.7853 | -7.021 | -8.2611 | -9.5016 | -10.6739 | -13.091 | -19.5494 | -26.5822 | -32.5671
EALING GSP | IRONBRIDGE | IRONBRIDGE | MINIMUM HEADROOM | TQ 14226 80171 | YES | 11.1103 | 9.8718 | 8.8112 | 7.2913 | 5.7084 | 4.1052 | 1.6965 | -1.3948 | -4.6836 | -8.6771 | -19.8113 | -42.7379 | -49.1708 | -53.1286 | 15.6219 | 14.6789 | 13.7777 | 12.5832 | 11.3004 | 9.4491 | 7.2913 | 4.3194 | 0.73952 | -2.8928 | -10.0655 | -28.4541 | -50.5693 | -97.0748 | 10.5782 | 9.4096 | 8.4066 | 6.9519 | 5.3597 | 3.7327 | 1.2023 | -1.8251 | -5.0265 | -8.9232 | -19.2906 | -41.1599 | -47.2318 | -50.9878
|  |  | CT |  |  | 11.5002 | 10.5995 | 9.7857 | 8.4488 | 7.1056 | 5.1745 | 2.8836 | -0.43827 | -4.5686 | -8.6771 | -19.8113 | -42.7379 | -49.1708 | -53.1286 | 15.6219 | 14.6789 | 13.7777 | 12.5832 | 11.3004 | 9.4491 | 7.2913 | 4.3194 | 0.73952 | -2.8928 | -10.0655 | -28.4541 | -43.7492 | -64.7017 | 10.9257 | 10.059 | 9.2122 | 7.9126 | 6.5727 | 4.5948 | 2.3086 | -0.93568 | -4.9402 | -8.9232 | -19.2906 | -41.1599 | -47.2318 | -50.9878
|  |  | LW |  |  | 11.1103 | 9.8718 | 8.8112 | 7.2913 | 5.7084 | 4.1052 | 1.6965 | -1.3948 | -4.6836 | -8.3157 | -16.1189 | -28.775 | -31.1313 | -28.0007 | 15.6749 | 14.7348 | 13.9538 | 12.9511 | 11.8289 | 10.6737 | 8.7909 | 6.518 | 4.1193 | 1.4052 | -4.4814 | -13.7863 | -15.3296 | -12.5541 | 10.5782 | 9.4096 | 8.4066 | 6.9519 | 5.3597 | 3.7327 | 1.2023 | -1.8251 | -5.0265 | -8.5694 | -16.1888 | -28.4763 | -30.6801 | -27.4738
|  |  | ST |  |  | 11.9874 | 11.5204 | 11.1994 | 10.7088 | 10.2442 | 9.5867 | 8.642 | 7.4653 | 6.0042 | 4.2204 | -0.48879 | -16.6889 | -27.3927 | -30.8282 | 15.9858 | 15.394 | 14.8955 | 14.163 | 13.3772 | 12.3746 | 11.061 | 9.5506 | 7.8159 | 5.7568 | 0.57154 | -17.3792 | -35.7954 | -57.4211 | 11.394 | 10.9644 | 10.6715 | 10.1623 | 9.6246 | 8.8795 | 7.8223 | 6.5673 | 5.1229 | 3.356 | -1.231 | -16.9516 | -27.4266 | -30.6338
|  |  | FS |  |  | 11.5002 | 10.5995 | 9.7857 | 8.4488 | 7.1056 | 5.1745 | 2.8836 | -0.43827 | -4.5686 | -8.6771 | -19.8113 | -42.7379 | -49.1708 | -53.1286 | 16.1148 | 15.4758 | 14.8372 | 14.0083 | 13.0848 | 12.0059 | 10.7034 | 9.1788 | 7.4199 | 5.3871 | 0.25479 | -19.4011 | -50.5693 | -97.0748 | 11.5655 | 11.1487 | 10.7784 | 10.297 | 9.7625 | 9.1126 | 8.3074 | 7.3266 | 6.1865 | 4.8656 | 1.4679 | -11.0333 | -25.6971 | -34.7046
FAWLEY GSP | LANGLEY BSP | LANGLEY BSP | MINIMUM HEADROOM | SU 45185 01376 | YES | 20.6017 | 18.4715 | 15.353 | 4.2256 | -8.3617 | -24.909 | -43.0651 | -59.1533 | -68.542 | -78.3655 | -96.4454 | -146.1776 | -162.1458 | -163.4357 | 25.8106 | 23.6061 | 20.1623 | 7.164 | -7.4534 | -26.956 | -48.3604 | -67.3111 | -77.8657 | -89.1338 | -110.4821 | -166.3465 | -181.3636 | -182.3723 | 17.8671 | 15.4128 | 11.7215 | -1.7905 | -16.993 | -37.1028 | -59.164 | -78.5301 | -89.2494 | -100.4525 | -120.8626 | -180.5591 | -197.768 | -199.0696
|  |  | CT |  |  | 22.2145 | 21.7527 | 21.1057 | 18.9901 | 15.6409 | 11.6807 | 5.4045 | 0.49975 | -3.707 | -9.6421 | -20.6689 | -48.339 | -59.0993 | -62.9626 | 27.1585 | 26.6974 | 25.9955 | 23.9122 | 20.4283 | 16.2453 | 9.196 | 4.079 | 0.73546 | -4.7128 | -14.643 | -40.5998 | -48.7706 | -52.9709 | 19.5975 | 19.0833 | 18.3423 | 15.9843 | 12.1771 | 7.6389 | 0.22126 | -5.3879 | -9.6524 | -16.0492 | -27.8615 | -57.9293 | -68.365 | -71.7196
|  |  | LW |  |  | 20.6017 | 18.4715 | 15.353 | 4.2256 | -8.3617 | -24.909 | -43.0651 | -59.1533 | -68.542 | -78.3655 | -96.4454 | -146.1776 | -162.1458 | -163.4357 | 25.8106 | 23.6061 | 20.1623 | 7.164 | -7.4534 | -26.956 | -48.3604 | -67.3111 | -77.8657 | -89.1338 | -110.4821 | -166.3465 | -181.3636 | -182.3723 | 17.8671 | 15.4128 | 11.7215 | -1.7905 | -16.993 | -37.1028 | -59.164 | -78.5301 | -89.2494 | -100.4525 | -120.8626 | -180.5591 | -197.768 | -199.0696
|  |  | ST |  |  | 21.6321 | 20.682 | 18.6838 | 8.6221 | 1.6109 | -4.7958 | -14.3838 | -19.4326 | -23.2341 | -26.75 | -34.3314 | -56.2443 | -66.3972 | -72.6457 | 26.2651 | 25.0895 | 22.6106 | 10.0887 | 1.4712 | -6.3676 | -18.1858 | -24.2138 | -28.5877 | -32.541 | -41.1366 | -65.6348 | -75.3812 | -80.4227 | 18.7934 | 17.6217 | 15.1451 | 2.6056 | -6.0497 | -13.9361 | -25.8006 | -31.9474 | -36.4042 | -40.4645 | -49.3157 | -74.9351 | -85.5815 | -90.8911
|  |  | FS |  |  | 22.2145 | 21.7527 | 21.1057 | 18.9901 | 15.6409 | 11.6807 | 5.4045 | 0.49975 | -3.707 | -9.6421 | -20.6689 | -48.339 | -59.0993 | -62.9626 | 27.347 | 27.2246 | 27.0573 | 24.1705 | 21.1775 | 17.5646 | 13.8805 | 10.5378 | 8.3203 | 6.0081 | 1.0224 | -7.8044 | -16.3354 | -25.0377 | 19.8801 | 19.7671 | 19.6094 | 16.6719 | 13.6161 | 9.9302 | 6.1695 | 2.7081 | 0.31562 | -2.1806 | -7.5591 | -17.5784 | -26.0592 | -31.9667
IVER 132KV | LONGFORD | LONGFORD | MINIMUM HEADROOM | TQ 03910 76751 | YES | 51.7767 | 51.0182 | 50.1331 | 48.8354 | 47.0201 | 44.6341 | 40.91 | 35.8641 | 29.772 | 22.3668 | 3.9357 | -32.3796 | -48.9521 | -56.7285 | 52.4601 | 51.8498 | 51.1019 | 49.9397 | 48.3377 | 46.2335 | 43.2123 | 39.3951 | 34.9148 | 29.4523 | 15.4172 | -12.9991 | -26.1546 | -32.6627 | 45.8792 | 45.4823 | 44.789 | 43.4953 | 41.6983 | 39.0678 | 35.1611 | 30.2105 | 24.3394 | 17.2042 | -0.52342 | -35.5085 | -51.5991 | -59.336
|  |  | CT |  |  | 52.0841 | 51.6881 | 51.1591 | 50.5905 | 49.9006 | 48.8674 | 47.6137 | 45.9099 | 43.8474 | 41.485 | 36.2347 | 26.8777 | 23.4256 | 21.3626 | 52.5744 | 52.3951 | 51.97 | 51.4854 | 50.8937 | 50.0158 | 48.9406 | 47.5124 | 45.8 | 43.9355 | 40.0409 | 33.4929 | 31.1436 | 29.5501 | 46.0228 | 45.8054 | 45.4744 | 45.1452 | 44.5407 | 43.5321 | 42.2976 | 40.6399 | 38.4756 | 35.9847 | 30.7774 | 21.8005 | 18.4385 | 16.3538
|  |  | LW |  |  | 51.7767 | 51.0182 | 50.1331 | 48.8354 | 47.0201 | 44.6341 | 40.91 | 35.8641 | 29.772 | 22.3668 | 3.9357 | -32.3796 | -48.9521 | -56.7285 | 52.4601 | 51.8498 | 51.1019 | 49.9397 | 48.3377 | 46.2335 | 43.2123 | 39.3951 | 34.9148 | 29.4523 | 15.4172 | -12.9991 | -26.1546 | -32.6627 | 45.8792 | 45.4823 | 44.789 | 43.4953 | 41.6983 | 39.0678 | 35.1611 | 30.2105 | 24.3394 | 17.2042 | -0.52342 | -35.5085 | -51.5991 | -59.336
|  |  | ST |  |  | 52.3021 | 52.2159 | 52.0231 | 51.5791 | 51.0961 | 50.5201 | 49.7542 | 48.9255 | 47.9503 | 46.7744 | 43.5905 | 32.519 | 25.511 | 23.4145 | 52.7119 | 52.6415 | 52.4672 | 52.0915 | 51.7476 | 51.3064 | 50.6154 | 49.9185 | 49.1155 | 48.1558 | 45.5695 | 36.8085 | 30.6555 | 28.1905 | 46.1916 | 46.1079 | 45.9134 | 45.5091 | 45.1262 | 44.692 | 44.0958 | 43.406 | 42.4468 | 41.2958 | 38.1935 | 27.4917 | 20.4467 | 18.3151
|  |  | FS |  |  | 52.0841 | 51.6881 | 51.1591 | 50.5905 | 49.9006 | 48.8674 | 47.6137 | 45.9099 | 43.8474 | 41.485 | 36.2347 | 26.8777 | 23.4256 | 21.3626 | 52.7273 | 52.6767 | 52.5809 | 52.4276 | 52.245 | 52.0257 | 51.7283 | 51.3091 | 50.85 | 50.3151 | 48.8427 | 43.0222 | 35.1195 | 29.3622 | 46.2106 | 46.1519 | 46.0438 | 45.8717 | 45.6638 | 45.4128 | 45.1109 | 44.7617 | 44.39 | 43.7864 | 42.0217 | 34.8294 | 25.968 | 20.7028
AMERSHAM | LOUDWATER BSP | LOUDWATER BSP | MINIMUM HEADROOM | SU 90644 91247 | YES | 37.0097 | 34.6476 | 125.5708 | 122.4162 | 118.8208 | 115.0728 | 110.0404 | 104.1895 | 97.3675 | 89.776 | 72.8012 | 39.9769 | 13.2822 | 4.0216 | 46.54 | 45.1963 | 130.3198 | 128.6654 | 126.6454 | 124.4723 | 121.2179 | 117.2693 | 112.7606 | 107.6242 | 95.913 | 73.0147 | 49.4952 | 37.461 | 33.0729 | 31.0095 | 115.4356 | 112.5777 | 109.2701 | 105.7885 | 101.0128 | 95.4086 | 88.9018 | 81.6308 | 65.3157 | 34.0068 | 9.2897 | 0.49267
|  |  | CT |  |  | 38.1397 | 36.5887 | 128.1209 | 125.5723 | 122.8076 | 119.2523 | 115.3093 | 110.124 | 102.8472 | 95.4803 | 80.7954 | 45.7091 | 29.3165 | 23.1055 | 46.7372 | 45.5909 | 130.7275 | 129.1184 | 127.3201 | 124.84 | 122.0233 | 118.1327 | 113.1556 | 108.063 | 97.7867 | 73.0147 | 59.3176 | 47.3412 | 34.036 | 32.6652 | 117.5898 | 115.2901 | 112.7394 | 109.3966 | 105.6666 | 100.6856 | 93.7755 | 86.7692 | 72.7916 | 39.6262 | 24.5124 | 18.9032
|  |  | LW |  |  | 37.0097 | 34.6476 | 125.5708 | 122.4162 | 118.8208 | 115.0728 | 110.0404 | 104.1895 | 97.3675 | 89.776 | 72.8012 | 39.9769 | 13.2822 | 4.0216 | 46.54 | 45.1963 | 130.3198 | 128.6654 | 126.6454 | 124.4723 | 121.2179 | 117.2693 | 112.7606 | 107.6242 | 95.913 | 74.1255 | 49.4952 | 42.5137 | 33.0729 | 31.0095 | 115.4356 | 112.5777 | 109.2701 | 105.7885 | 101.0128 | 95.4086 | 88.9018 | 81.6308 | 65.3157 | 34.0068 | 9.2897 | 0.49267
|  |  | ST |  |  | 38.8823 | 37.94 | 130.1416 | 129.1915 | 128.046 | 126.6253 | 124.7359 | 122.3888 | 119.6839 | 116.3298 | 107.2482 | 75.8849 | 54.3635 | 44.9319 | 47.1761 | 46.444 | 132.0517 | 131.173 | 130.1112 | 128.7955 | 127.0788 | 124.9909 | 122.588 | 119.6187 | 111.6515 | 84.9552 | 65.1895 | 52.508 | 34.7069 | 33.9129 | 119.4796 | 118.5697 | 117.4573 | 116.0601 | 114.2057 | 111.9215 | 109.3045 | 106.0559 | 97.2549 | 66.4332 | 45.6255 | 37.1178
|  |  | FS |  |  | 38.1397 | 36.5887 | 128.1209 | 125.5723 | 122.8076 | 119.2523 | 115.3093 | 110.124 | 102.8472 | 95.4803 | 80.7954 | 45.7091 | 29.3165 | 23.1055 | 47.2533 | 46.5537 | 132.206 | 131.4275 | 130.5169 | 129.4213 | 128.1125 | 126.5382 | 124.6317 | 122.3982 | 116.4736 | 93.4999 | 65.0364 | 37.461 | 34.8215 | 34.1284 | 119.8187 | 118.9734 | 117.9992 | 116.8226 | 115.4332 | 113.7604 | 111.6846 | 109.272 | 102.8918 | 78.258 | 50.6774 | 33.1333
MANNINGTON GSP | LYTCHETT | LYTCHETT | MINIMUM HEADROOM | SY 97796 94214 | YES | 35.1834 | 33.5843 | 31.8641 | 28.1629 | 23.1105 | 17.7165 | 9.0559 | -3.0616 | -17.5702 | -35.0723 | -77.2375 | -152.1331 | -177.4945 | -192.818 | 43.9655 | 42.1716 | 40.4298 | 38.0364 | 34.8688 | 31.3139 | 25.4053 | 16.2097 | 5.2868 | -8.0008 | -40.2224 | -97.162 | -117.4445 | -131.5872 | 30.68 | 28.1095 | 25.6035 | 22.0578 | 17.4813 | 12.5561 | 5.0333 | -4.4473 | -15.087 | -27.6902 | -68.1284 | -139.9402 | -165.0655 | -181.1846
|  |  | CT |  |  | 35.4196 | 34.2007 | 32.9506 | 31.0373 | 26.954 | 21.6122 | 15.3552 | 6.5338 | -4.4811 | -15.978 | -38.6643 | -107.0427 | -149.8437 | -165.8593 | 44.2627 | 42.7475 | 41.1487 | 38.8378 | 35.9684 | 32.0703 | 27.444 | 20.7931 | 12.784 | 4.2472 | -12.7133 | -62.8609 | -95.3518 | -108.2118 | 31.4019 | 29.4725 | 27.3716 | 24.2077 | 20.4446 | 15.3782 | 9.4278 | 0.95986 | -9.5509 | -20.5813 | -42.2879 | -97.3436 | -138.6992 | -154.6266
|  |  | LW |  |  | 35.1834 | 33.5843 | 31.8641 | 28.1629 | 23.1105 | 17.7165 | 9.0559 | -3.0616 | -17.5702 | -35.0723 | -77.2375 | -152.1331 | -177.4945 | -192.818 | 43.9655 | 42.1716 | 40.4298 | 38.0364 | 34.8688 | 31.3139 | 25.4053 | 16.2097 | 5.2868 | -8.0008 | -40.2224 | -97.162 | -117.4445 | -131.5872 | 30.68 | 28.1095 | 25.6035 | 22.0578 | 17.4813 | 12.5561 | 5.0333 | -4.4473 | -15.087 | -27.6902 | -68.1284 | -139.9402 | -165.0655 | -181.1846
|  |  | ST |  |  | 36.2036 | 35.6425 | 35.2167 | 34.2181 | 33.081 | 30.9864 | 27.6165 | 23.4297 | 18.7509 | 13.2854 | -0.66792 | -46.7066 | -79.7211 | -95.5472 | 44.9661 | 44.1172 | 43.2908 | 41.684 | 39.8629 | 37.7623 | 34.8946 | 31.4252 | 27.4058 | 22.7603 | 10.8689 | -27.9659 | -58.1779 | -75.4956 | 32.4327 | 31.46 | 30.4632 | 28.5596 | 26.343 | 23.8153 | 20.4448 | 16.3307 | 11.5787 | 6.035 | -8.2336 | -55.0582 | -88.536 | -103.8753
|  |  | FS |  |  | 35.4196 | 34.2007 | 32.9506 | 31.0373 | 26.954 | 21.6122 | 15.3552 | 6.5338 | -4.4811 | -15.978 | -38.6643 | -107.0427 | -149.8437 | -165.8593 | 44.9759 | 44.1373 | 43.2272 | 41.9642 | 40.3893 | 38.4259 | 35.9453 | 32.8359 | 29.2009 | 25.0157 | 14.3313 | -23.1211 | -65.5325 | -100.4567 | 32.4213 | 31.4797 | 30.4359 | 28.8663 | 26.8937 | 24.5358 | 21.5954 | 17.9067 | 13.5905 | 8.6334 | -4.0007 | -48.3834 | -94.9766 | -123.2453
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD BSP | MINIMUM HEADROOM | SU 86592 79883 | YES | 24.7323 | 22.2814 | 19.7119 | 16.1202 | 11.655 | 6.818 | -0.25076 | -8.6462 | -18.0954 | -28.4876 | -50.3168 | -98.4758 | -132.7934 | -150.3126 | 37.1011 | 35.5845 | 33.9513 | 31.772 | 29.1245 | 25.5926 | 21.2908 | 15.4638 | 8.2182 | 0.75332 | -14.0284 | -56.959 | -81.7345 | -94.6238 | 23.2066 | 21.0599 | 18.8099 | 15.5062 | 11.373 | 6.8685 | 0.20023 | -7.7657 | -16.6839 | -26.5524 | -47.5327 | -97.2864 | -129.8084 | -146.4235
|  |  | CT |  |  | 25.5504 | 23.7516 | 21.5476 | 18.3755 | 14.7005 | 9.6773 | 3.8669 | -4.0513 | -14.3136 | -24.8193 | -45.1585 | -98.4758 | -132.7934 | -150.3126 | 37.1015 | 35.6874 | 33.9513 | 31.772 | 29.2274 | 25.5926 | 21.3572 | 15.4638 | 8.2182 | 0.75332 | -14.0284 | -56.959 | -81.7345 | -94.6238 | 23.9931 | 22.4147 | 20.388 | 17.4611 | 14.0666 | 9.3543 | 3.8865 | -3.6444 | -13.349 | -23.2921 | -42.6545 | -97.2864 | -129.8084 | -146.4235
|  |  | LW |  |  | 24.7323 | 22.2814 | 19.7119 | 16.1202 | 11.655 | 6.818 | -0.25076 | -8.6462 | -18.0954 | -28.4876 | -50.3168 | -88.5405 | -101.2373 | -100.2521 | 37.1011 | 35.5845 | 34.0074 | 31.8816 | 29.1245 | 26.0702 | 21.2908 | 15.5087 | 9.1347 | 1.9678 | -13.6083 | -40.1537 | -52.5517 | -57.2587 | 23.2066 | 21.0599 | 18.8099 | 15.5062 | 11.373 | 6.8685 | 0.20023 | -7.7657 | -16.6839 | -26.5524 | -47.5327 | -84.1619 | -95.9349 | -98.9725
|  |  | ST |  |  | 26.5023 | 25.5468 | 24.3062 | 22.6942 | 20.7505 | 18.3539 | 15.2564 | 11.5864 | 7.4131 | 2.3934 | -10.113 | -49.9072 | -75.8115 | -86.0794 | 37.7418 | 36.9489 | 35.9356 | 34.5234 | 32.8734 | 30.8377 | 28.1977 | 25.1047 | 21.6011 | 17.41 | 6.7563 | -27.5471 | -52.857 | -69.7121 | 24.8711 | 24.0962 | 23.061 | 21.5348 | 19.721 | 17.4748 | 14.5377 | 11.0585 | 7.0993 | 2.3609 | -9.8637 | -49.4053 | -74.8811 | -83.8271
|  |  | FS |  |  | 25.5504 | 23.7516 | 21.5476 | 18.3755 | 14.7005 | 9.6773 | 3.8669 | -4.0513 | -14.3136 | -24.8193 | -45.1585 | -98.4758 | -132.7934 | -150.3126 | 37.7643 | 36.9657 | 35.9936 | 34.8198 | 33.386 | 31.6596 | 29.4888 | 26.8647 | 23.8368 | 20.3927 | 11.8358 | -18.9812 | -57.0161 | -94.0653 | 24.9487 | 24.2441 | 23.3558 | 22.0873 | 20.5408 | 18.6831 | 16.3353 | 13.4942 | 10.1519 | 6.4033 | -2.7334 | -35.2798 | -70.9074 | -92.2942
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON BSP | MINIMUM HEADROOM | SU 07523 05221 | YES | 29.2266 | 24.61 | 19.7295 | 13.0788 | 5.3165 | -3.5937 | -17.0811 | -33.3912 | -52.2584 | -73.2303 | -119.9182 | -199.978 | -267.4757 | -291.7807 | 53.2459 | 50.1199 | 46.8324 | 42.6099 | 37.3788 | 31.2996 | 21.2141 | 9.1617 | -4.2953 | -19.4384 | -53.6001 | -114.0716 | -163.3777 | -181.5502 | 26.0025 | 21.6915 | 17.0306 | 10.7436 | 3.1885 | -5.4638 | -18.9698 | -34.9956 | -53.1033 | -73.3089 | -118.4438 | -195.3879 | -261.7949 | -285.1681
|  |  | CT |  |  | 30.8829 | 27.4371 | 23.3271 | 17.3698 | 11.1677 | 2.1732 | -8.9957 | -24.3684 | -43.9124 | -63.905 | -104.3286 | -196.7816 | -267.4757 | -291.7807 | 53.4165 | 50.5957 | 47.192 | 42.8852 | 38.3269 | 31.3421 | 22.7946 | 11.1613 | -2.9524 | -17.468 | -46.8376 | -114.0716 | -163.3777 | -181.5502 | 27.3695 | 23.9162 | 19.7787 | 13.9683 | 7.821 | -1.274 | -12.2475 | -27.0501 | -45.8031 | -65.0383 | -103.9136 | -194.282 | -261.7949 | -285.1681
|  |  | LW |  |  | 29.2266 | 24.61 | 19.7295 | 13.0788 | 5.3165 | -3.5937 | -17.0811 | -33.3912 | -52.2584 | -73.2303 | -119.9182 | -199.978 | -225.9235 | -241.646 | 53.2459 | 50.1199 | 46.8324 | 42.6099 | 37.3788 | 31.2996 | 21.2141 | 9.1617 | -4.2953 | -19.4384 | -53.6001 | -110.5349 | -132.0131 | -145.029 | 26.0025 | 21.6915 | 17.0306 | 10.7436 | 3.1885 | -5.4638 | -18.9698 | -34.9956 | -53.1033 | -73.3089 | -118.4438 | -195.3879 | -222.0264 | -237.703
|  |  | ST |  |  | 32.6944 | 30.8314 | 28.5411 | 25.4422 | 22.3752 | 18.132 | 12.2123 | 5.3064 | -2.8766 | -12.4613 | -37.5541 | -118.1028 | -171.3637 | -191.0845 | 54.7229 | 53.1741 | 51.2626 | 48.5202 | 45.7343 | 41.9444 | 36.6139 | 30.5832 | 23.7935 | 15.8556 | -5.0874 | -71.8928 | -116.9424 | -136.9531 | 29.1454 | 27.402 | 25.1893 | 22.0269 | 18.7931 | 14.372 | 8.213 | 1.1384 | -6.8273 | -16.1861 | -40.8317 | -119.9424 | -172.7888 | -190.8398
|  |  | FS |  |  | 30.8829 | 27.4371 | 23.3271 | 17.3698 | 11.1677 | 2.1732 | -8.9957 | -24.3684 | -43.9124 | -63.905 | -104.3286 | -196.7816 | -267.4757 | -291.7807 | 54.8211 | 53.4793 | 51.8259 | 49.7445 | 47.3606 | 44.3305 | 40.377 | 35.6492 | 30.2562 | 24.077 | 7.9544 | -50.0984 | -115.8961 | -164.4573 | 29.323 | 27.8916 | 26.0713 | 23.5936 | 20.7757 | 17.1973 | 12.5861 | 7.067 | 0.61837 | -6.7196 | -25.6751 | -93.6752 | -166.8184 | -210.6702
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU 47559 12003 | YES | -13.6296 | 76.4851 | 73.6032 | 68.4706 | 63.1126 | 57.3899 | 50.4957 | 42.4989 | 32.8427 | 22.2135 | -2.2729 | -76.0968 | -114.812 | -135.8489 | 3.1036 | 87.8847 | 86.3394 | 83.7412 | 80.934 | 77.7774 | 73.609 | 68.5624 | 61.8744 | 53.7107 | 32.8742 | -21.5269 | -48.6514 | -100.2912 | -15.9333 | 67.8137 | 65.262 | 60.5915 | 55.7194 | 50.4998 | 44.239 | 37.0215 | 28.2239 | 18.3424 | -4.5588 | -77.4395 | -114.2467 | -134.6159
|  |  | CT |  |  | -11.2988 | 80.101 | 78.4037 | 74.2613 | 70.0689 | 64.9973 | 59.2636 | 51.9362 | 41.1487 | 29.5007 | 0.78842 | -76.0968 | -114.812 | -135.8489 | 3.6427 | 88.688 | 87.2982 | 84.6663 | 82.028 | 78.6016 | 74.535 | 69.2286 | 61.8744 | 53.7107 | 32.8742 | -21.5269 | -48.6514 | -67.9073 | -13.807 | 71.1186 | 69.6848 | 65.8535 | 62.0475 | 57.4369 | 52.1929 | 45.6463 | 35.7541 | 24.8513 | -4.5588 | -77.4395 | -114.2467 | -134.6159
|  |  | LW |  |  | -13.6296 | 76.4851 | 73.6032 | 68.4706 | 63.1126 | 57.3899 | 50.4957 | 42.4989 | 32.8427 | 22.2135 | -2.2729 | -50.4763 | -72.6582 | -82.4248 | 3.1036 | 87.8847 | 86.3394 | 83.7412 | 80.934 | 77.7774 | 73.609 | 68.5624 | 62.3739 | 55.3665 | 39.1738 | 8.3729 | -14.6426 | -27.0715 | -15.9333 | 67.8137 | 65.262 | 60.5915 | 55.7194 | 50.4998 | 44.239 | 37.0215 | 28.2239 | 18.3424 | -4.2402 | -49.3406 | -70.6195 | -85.0423
|  |  | ST |  |  | -9.9939 | 82.2819 | 81.5698 | 80.1412 | 78.896 | 77.3656 | 75.3115 | 72.7026 | 69.3104 | 65.3012 | 54.6801 | 16.0439 | -13.623 | -33.3739 | 4.2918 | 89.8326 | 89.0302 | 87.5258 | 86.1993 | 84.5899 | 82.4768 | 79.9375 | 76.509 | 72.5522 | 62.2976 | 26.9205 | -6.0344 | -38.7839 | -12.5036 | 73.2734 | 72.7884 | 71.5689 | 70.5923 | 69.4042 | 67.7824 | 65.5069 | 62.2535 | 58.2739 | 47.7356 | 10.1389 | -18.6348 | -37.1454
|  |  | FS |  |  | -11.2988 | 80.101 | 78.4037 | 74.2613 | 70.0689 | 64.9973 | 59.2636 | 51.9362 | 41.1487 | 29.5007 | 0.78842 | -76.0968 | -114.812 | -135.8489 | 4.2758 | 89.7236 | 88.7292 | 87.3195 | 85.8042 | 83.9539 | 81.7682 | 79.0253 | 75.2701 | 70.9488 | 59.9681 | 19.2665 | -34.4637 | -100.2912 | -12.5292 | 73.1893 | 72.5415 | 71.1987 | 69.798 | 68.1039 | 66.1292 | 63.618 | 60.1224 | 56.0007 | 45.4891 | -15.3448 | -63.9314 | -89.9107
MELKSHAM GSP | NORRINGTON | NORRINGTON | MINIMUM HEADROOM | ST 88273 64983 | YES | 30.8476 | 23.6157 | 16.5185 | 3.7651 | -1.7099 | -8.586 | -17.2282 | -26.4094 | -36.4837 | -47.1117 | -69.3468 | -169.986 | -202.5462 | -161.4615 | 38.54 | 31.6015 | 24.7363 | 11.8643 | 8.5652 | 3.6104 | -2.7326 | -9.2578 | -16.035 | -23.148 | -37.918 | -112.3489 | -144.2893 | -123.3327 | 21.4398 | 13.5123 | 5.6423 | -8.9107 | -13.9657 | -20.7827 | -28.8591 | -37.0869 | -46.1303 | -55.5426 | -75.0781 | -148.2471 | -181.4522 | -177.3596
|  |  | CT |  |  | 32.7631 | 26.6256 | 20.4764 | 8.6448 | 4.2703 | -2.0299 | -9.056 | -17.1271 | -27.7859 | -38.6289 | -59.716 | -165.5319 | -202.5462 | -151.4738 | 39.1602 | 32.4838 | 25.7809 | 13.1863 | 10.1988 | 5.2028 | -0.52185 | -6.8153 | -14.3591 | -22.1762 | -37.3915 | -112.3489 | -144.2893 | -123.3327 | 23.6397 | 16.8634 | 10.0899 | -3.3331 | -7.2468 | -13.0785 | -19.6836 | -26.679 | -36.1561 | -46.0552 | -65.7388 | -144.9022 | -181.4522 | -156.1198
|  |  | LW |  |  | 30.8476 | 23.6157 | 16.5185 | 3.7651 | -1.7099 | -8.586 | -17.2282 | -26.4094 | -36.4837 | -47.1117 | -69.3468 | -169.986 | -196.3569 | -161.4615 | 38.54 | 31.6015 | 24.7363 | 11.8643 | 8.5652 | 3.6104 | -2.7326 | -9.2578 | -16.035 | -23.148 | -37.918 | -103.7514 | -121.9872 | -88.9722 | 21.4398 | 13.5123 | 5.6423 | -8.9107 | -13.9657 | -20.7827 | -28.8591 | -37.0869 | -46.1303 | -55.5426 | -75.0781 | -148.2471 | -175.8928 | -177.3596
|  |  | ST |  |  | 34.0248 | 28.762 | 23.586 | 13.2692 | 10.7299 | 7.0442 | 2.6715 | -1.7459 | -6.5426 | -11.6756 | -23.5285 | -104.1418 | -149.0247 | -109.1271 | 39.871 | 33.7368 | 27.6431 | 15.5128 | 13.3388 | 9.8168 | 5.6018 | 1.5611 | -2.7587 | -7.2464 | -17.3431 | -78.8135 | -118.3652 | -102.6079 | 24.916 | 18.9211 | 13.0166 | 1.027 | -0.97249 | -4.2113 | -8.0112 | -11.4543 | -15.0711 | -18.697 | -26.4176 | -85.2849 | -129.2562 | -94.4181
|  |  | FS |  |  | 32.7631 | 26.6256 | 20.4764 | 8.6448 | 4.2703 | -2.0299 | -9.056 | -17.1271 | -27.7859 | -38.6289 | -59.716 | -165.5319 | -202.5462 | -151.4738 | 39.9802 | 33.9944 | 27.9562 | 16.2989 | 14.579 | 11.5155 | 7.9524 | 4.1744 | 0.15522 | -4.0049 | -13.4221 | -67.9121 | -119.2339 | -121.221 | 25.1176 | 19.396 | 13.6733 | 2.056 | 0.45067 | -2.4147 | -5.6264 | -8.897 | -12.4842 | -16.0396 | -23.5844 | -65.594 | -117.7612 | -84.7321
NORTH HYDE GSP | NORTH HYDE (D) | NORTH HYDE (D) | MINIMUM HEADROOM | TQ 10367 79001 | YES | 10.9201 | 10.0392 | 9.2544 | 7.7932 | -26.5773 | -29.5992 | -33.2316 | -36.8395 | -40.4863 | -44.3358 | -55.6597 | -107.7765 | -146.6721 | -159.0457 | 17.3209 | 16.8153 | 16.2451 | 15.3985 | -26.4228 | -29.0467 | -32.1372 | -35.3691 | -38.7874 | -42.2892 | -52.9862 | -93.3344 | -123.5094 | -133.3579 | 12.2507 | 11.534 | 10.8689 | 9.5568 | -32.855 | -36.0413 | -39.9492 | -43.7864 | -47.5865 | -51.5656 | -61.6463 | -111.8646 | -149.2329 | -161.1547
|  |  | CT |  |  | 11.3481 | 10.7682 | 10.1882 | 9.0315 | -24.9617 | -27.7034 | -30.8161 | -34.0267 | -37.7648 | -41.7809 | -55.6597 | -107.7765 | -146.6721 | -159.0457 | 17.3209 | 16.8153 | 16.2451 | 15.3985 | -26.4228 | -29.0467 | -32.1372 | -35.3691 | -38.7874 | -42.2892 | -52.9862 | -93.3344 | -123.5094 | -133.3579 | 12.6152 | 12.1509 | 11.6509 | 10.5957 | -31.455 | -34.3793 | -37.7577 | -41.2084 | -45.0746 | -49.0552 | -61.6463 | -111.8646 | -149.2329 | -161.1547
|  |  | LW |  |  | 10.9201 | 10.0392 | 9.2544 | 7.7932 | -26.5773 | -29.5992 | -33.2316 | -36.8395 | -40.4863 | -44.3358 | -55.0234 | -85.8447 | -100.6743 | -105.8213 | 17.3318 | 16.8613 | 16.4197 | 15.6055 | -26.1993 | -28.7371 | -31.8632 | -34.8854 | -37.9051 | -41.8231 | -52.4565 | -76.7518 | -88.5231 | -92.7655 | 12.2507 | 11.534 | 10.8689 | 9.5568 | -32.855 | -36.0413 | -39.9492 | -43.7864 | -47.5865 | -51.5656 | -61.2358 | -91.2827 | -105.7358 | -110.8364
|  |  | ST |  |  | 11.5824 | 11.1728 | 10.8059 | 10.3179 | -22.8963 | -24.5019 | -26.5961 | -28.6403 | -30.676 | -32.8335 | -37.7108 | -52.1533 | -61.9471 | -65.8801 | 17.4725 | 17.0856 | 16.6688 | 16.0678 | -25.4811 | -27.5532 | -30.0699 | -32.5066 | -34.9007 | -37.3691 | -42.8036 | -58.6983 | -73.964 | -91.075 | 12.8418 | 12.5407 | 12.2256 | 11.7161 | -29.6759 | -31.5429 | -33.8701 | -36.1473 | -38.3627 | -40.6572 | -45.7202 | -60.194 | -69.9264 | -73.4589
|  |  | FS |  |  | 11.3481 | 10.7682 | 10.1882 | 9.0315 | -24.9617 | -27.7034 | -30.8161 | -34.0267 | -37.7648 | -41.7809 | -55.6597 | -107.7765 | -146.6721 | -159.0457 | 17.4018 | 16.9021 | 16.2902 | 15.4706 | -26.3047 | -28.6236 | -31.3452 | -34.4025 | -37.5103 | -40.6117 | -47.179 | -65.7343 | -90.0407 | -127.1248 | 12.7895 | 12.3858 | 11.9364 | 11.3616 | -30.1704 | -32.2806 | -34.7533 | -37.5611 | -40.4189 | -43.2014 | -48.8493 | -63.0723 | -75.2132 | -82.2851
NORTH HYDE GSP | NORTH HYDE 11 | NORTH HYDE 11 | MINIMUM HEADROOM | TQ 10367 79001 | YES | 14.6599 | -9.8041 | -27.198 | -40.0769 | -42.9691 | -48.2493 | -55.1248 | -61.2963 | -67.6363 | -76.7729 | -99.0779 | -154.1759 | -185.6531 | -196.3926 | 19.6671 | -8.7327 | -29.5768 | -44.0705 | -46.1108 | -51.7741 | -59.227 | -66.052 | -72.9566 | -80.5297 | -98.5218 | -142.5568 | -167.5298 | -191.4363 | 15.55 | -13.9821 | -35.2492 | -50.4717 | -53.2792 | -59.0297 | -66.7081 | -73.722 | -80.4323 | -88.2302 | -110.1512 | -163.959 | -194.4844 | -204.8791
|  |  | CT |  |  | 15.2395 | -8.6811 | -25.7533 | -38.1276 | -40.4287 | -45.3448 | -50.9888 | -56.2172 | -62.5319 | -68.2572 | -78.1856 | -100.0834 | -109.2886 | -112.6416 | 19.8059 | -8.5495 | -29.4562 | -43.8897 | -45.8581 | -50.819 | -56.7182 | -62.5064 | -68.414 | -73.7935 | -83.1962 | -105.6506 | -123.3011 | -145.7491 | 15.9373 | -13.1723 | -34.249 | -49.1187 | -51.4163 | -57.0503 | -63.5217 | -69.7158 | -76.2453 | -82.1193 | -92.158 | -113.903 | -122.8148 | -125.9667
|  |  | LW |  |  | 14.6599 | -9.8041 | -27.198 | -40.0769 | -42.9691 | -48.2493 | -55.1248 | -61.2963 | -67.6363 | -76.7729 | -99.0779 | -154.1759 | -185.6531 | -196.3926 | 19.6671 | -8.7327 | -29.5768 | -44.0705 | -46.1108 | -51.7741 | -59.227 | -66.052 | -72.9566 | -80.5297 | -98.5218 | -142.5568 | -167.5298 | -176.0768 | 15.55 | -13.9821 | -35.2492 | -50.4717 | -53.2792 | -59.0297 | -66.7081 | -73.722 | -80.4323 | -88.2302 | -110.1512 | -163.959 | -194.4844 | -204.8791
|  |  | ST |  |  | 15.8553 | -7.6651 | -24.3071 | -35.7743 | -37.2161 | -40.655 | -44.7887 | -48.1133 | -51.3297 | -54.6565 | -62.789 | -85.2375 | -99.8838 | -104.7806 | 20.1059 | -8.0634 | -28.5236 | -42.5706 | -44.1586 | -48.1824 | -52.9273 | -56.8172 | -60.6128 | -64.805 | -73.6439 | -97.5088 | -119.7068 | -143.0202 | 16.6206 | -11.997 | -32.5363 | -46.5426 | -48.0269 | -52.0669 | -56.9308 | -61.0809 | -65.0603 | -69.0628 | -77.5771 | -99.6798 | -113.7617 | -118.5611
|  |  | FS |  |  | 15.2395 | -8.6811 | -25.7533 | -38.1276 | -40.4287 | -45.3448 | -50.9888 | -56.2172 | -62.5319 | -68.2572 | -78.1856 | -100.0834 | -109.2886 | -112.6416 | 20.2779 | -7.6396 | -28.0027 | -41.9685 | -43.3424 | -47.1005 | -51.4483 | -55.6893 | -59.7269 | -64.0454 | -73.5862 | -101.279 | -139.418 | -191.4363 | 16.7356 | -11.5544 | -31.9202 | -45.727 | -46.8939 | -50.4821 | -54.6663 | -58.8117 | -62.624 | -66.3264 | -74.3961 | -95.8189 | -117.382 | -130.2969
IVER 66KV | NORTHOLT | NORTHOLT | MINIMUM HEADROOM | TQ 11550 83230 | YES | 8.7603 | 8.2941 | 7.8249 | 6.6224 | 5.3594 | 4.0441 | 2.6338 | 1.1609 | -0.41423 | -3.0804 | -13.3496 | -32.319 | -38.55 | -42.315 | 12.0372 | 11.8994 | 11.6962 | 11.2425 | 10.7163 | 10.1016 | 9.2948 | 8.2194 | 6.7601 | 4.0191 | -3.3865 | -16.4823 | -22.9309 | -57.7943 | 7.5095 | 7.1138 | 6.7136 | 5.6845 | 4.601 | 3.4633 | 2.2176 | 0.90583 | -0.47894 | -3.3252 | -13.0399 | -30.8478 | -36.5808 | -40.08
|  |  | CT |  |  | 9.4221 | 9.2772 | 9.1138 | 8.182 | 7.1632 | 6.0652 | 4.8526 | 3.4886 | 1.3254 | -3.0804 | -13.3496 | -32.319 | -38.55 | -42.315 | 12.0859 | 11.9064 | 11.6962 | 11.2425 | 10.7163 | 10.1016 | 9.2948 | 8.2194 | 6.7601 | 4.0191 | -3.3865 | -16.4823 | -20.4201 | -34.9607 | 8.0671 | 7.9434 | 7.803 | 7.0169 | 6.1561 | 5.2245 | 4.1568 | 2.9242 | 0.83327 | -3.3252 | -13.0399 | -30.8478 | -36.5808 | -40.08
|  |  | LW |  |  | 8.7603 | 8.2941 | 7.8249 | 6.6224 | 5.3594 | 4.0441 | 2.6338 | 1.1609 | -0.41423 | -2.0347 | -5.3688 | -12.0419 | -14.5239 | -15.6548 | 12.0372 | 11.8994 | 11.7569 | 11.3821 | 10.9719 | 10.5174 | 10.0043 | 9.4547 | 8.7596 | 8.0325 | 6.5193 | 3.6119 | 2.555 | 2.0345 | 7.5095 | 7.1138 | 6.7136 | 5.6845 | 4.601 | 3.4633 | 2.2176 | 0.90583 | -0.47894 | -1.9068 | -4.8497 | -10.6732 | -12.7446 | -13.628
|  |  | ST |  |  | 9.7026 | 9.7202 | 9.7377 | 9.6838 | 9.6129 | 9.5369 | 9.4329 | 9.3262 | 9.1833 | 9.007 | 8.5314 | 5.0301 | 1.193 | -3.0352 | 12.1716 | 12.0455 | 11.8973 | 11.6562 | 11.3948 | 11.0941 | 10.7279 | 10.3422 | 9.8746 | 9.3436 | 8.0417 | 2.3974 | -7.3482 | -24.4916 | 8.3011 | 8.3135 | 8.3253 | 8.2608 | 8.1881 | 8.1108 | 8.004 | 7.9021 | 7.7785 | 7.6296 | 7.2295 | 4.1743 | 0.9341 | -2.6321
|  |  | FS |  |  | 9.4221 | 9.2772 | 9.1138 | 8.182 | 7.1632 | 6.0652 | 4.8526 | 3.4886 | 1.3254 | -3.0804 | -13.3496 | -32.319 | -38.55 | -42.315 | 12.1157 | 11.9288 | 11.7087 | 11.3794 | 10.9864 | 10.5197 | 9.9642 | 9.3136 | 8.4313 | 7.4416 | 5.0752 | -4.1868 | -22.9309 | -57.7943 | 8.2463 | 8.2294 | 8.1994 | 8.0481 | 7.8702 | 7.6685 | 7.4354 | 7.1486 | 6.707 | 6.244 | 5.24 | 1.5337 | -3.1916 | -8.0161
COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD (OSNEY) BSP | MINIMUM HEADROOM | SP 50054 05983 | NO | 88.9581 | 85.1196 | 80.2183 | 76.6482 | 72.2495 | 67.4456 | 60.6648 | 52.8943 | 44.7333 | 35.5915 | 15.1392 | -29.1118 | -53.4838 | -64.0843 | 35.1636 | 31.7693 | 27.0299 | 24.884 | 22.1196 | 19.0847 | 14.5016 | 9.1579 | 3.3263 | -3.3023 | -18.2148 | -47.4499 | -93.6222 | -151.4386 | 9.3699 | 5.9443 | 0.56565 | -2.6898 | -6.743 | -11.1738 | -17.5425 | -24.9053 | -32.7949 | -41.6617 | -61.4954 | -97.0794 | -119.5785 | -130.5936
|  |  | CT |  |  | 90.6891 | 88.8131 | 86.393 | 83.3451 | 79.7834 | 75.0953 | 69.714 | 62.7267 | 54.2353 | 45.5665 | 28.3795 | -11.189 | -29.8924 | -39.4919 | 36.2995 | 34.5271 | 32.128 | 29.8514 | 27.1476 | 23.5487 | 19.3381 | 13.8335 | 7.2869 | 0.43044 | -13.4388 | -47.4139 | -71.6955 | -100.0139 | 10.8196 | 9.7566 | 7.3502 | 4.6674 | 1.4416 | -2.9168 | -7.9541 | -14.5871 | -22.7296 | -31.1 | -47.6928 | -85.6349 | -103.3804 | -112.6076
|  |  | LW |  |  | 88.9581 | 85.1196 | 80.2183 | 76.6482 | 72.2495 | 67.4456 | 60.6648 | 52.8943 | 44.7333 | 35.5915 | 15.1392 | -29.1118 | -53.4838 | -64.0843 | 35.1636 | 31.7693 | 27.0299 | 24.884 | 22.1196 | 19.0847 | 14.5016 | 9.1579 | 3.3263 | -3.3023 | -18.2148 | -47.4499 | -66.5316 | -76.0052 | 9.3699 | 5.9443 | 0.56565 | -2.6898 | -6.743 | -11.1738 | -17.5425 | -24.9053 | -32.7949 | -41.6617 | -61.4954 | -97.0794 | -119.5785 | -130.5936
|  |  | ST |  |  | 90.8506 | 89.1529 | 86.1669 | 84.7698 | 83.0154 | 80.9822 | 78.3732 | 75.4742 | 72.3348 | 68.5219 | 58.0784 | 21.6666 | -4.3943 | -16.2158 | 35.9266 | 33.9373 | 30.3314 | 28.9009 | 27.1648 | 25.1739 | 22.6251 | 19.8411 | 16.7028 | 12.9931 | 3.0468 | -31.8007 | -63.4104 | -93.2493 | 10.1481 | 8.59 | 5.5155 | 4.7542 | 3.2981 | 1.3527 | -1.1842 | -4.0339 | -7.2166 | -11.0565 | -21.4926 | -57.5864 | -83.5858 | -95.2755
|  |  | FS |  |  | 90.6891 | 88.8131 | 86.393 | 83.3451 | 79.7834 | 75.0953 | 69.714 | 62.7267 | 54.2353 | 45.5665 | 28.3795 | -11.189 | -29.8924 | -39.4919 | 36.714 | 35.532 | 34.0846 | 32.3556 | 30.2298 | 27.7198 | 24.5501 | 20.7661 | 16.603 | 11.8233 | -0.30225 | -42.4001 | -93.6222 | -151.4386 | 11.2187 | 10.6863 | 10.01 | 8.3844 | 6.3467 | 3.8904 | 0.72842 | -3.1256 | -7.3482 | -12.153 | -24.3941 | -65.3424 | -106.2018 | -129.6249
WILLESDEN GSP | PERIVALE | PERIVALE | MINIMUM HEADROOM | TQ 17544 82947 | YES | 78.126 | 76.6071 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 72.6575 | 70.7588 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 72.6575 | 70.7588 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175
|  |  | CT |  |  | 79.0628 | 78.8387 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 73.8285 | 73.5484 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.8285 | 73.5484 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738 | 73.0738
|  |  | LW |  |  | 78.126 | 76.6071 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 74.094 | 72.6575 | 70.7588 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 72.6575 | 70.7588 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175 | 67.6175
|  |  | ST |  |  | 78.2523 | 77.3747 | 75.473 | 75.473 | 75.473 | 75.473 | 75.473 | 75.473 | 75.473 | 75.473 | 75.473 | 75.473 | 75.473 | 75.473 | 72.8154 | 71.7184 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 72.8154 | 71.7184 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413 | 69.3413
|  |  | FS |  |  | 79.0628 | 78.8387 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 78.459 | 73.9314 | 73.9141 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.9314 | 73.9141 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796 | 73.8796
MANNINGTON GSP | POOLE PS (HAMWORTHY) | POOLE PS (HAMWORTHY) | MINIMUM HEADROOM | SZ 00203 90789 | YES | 27.8882 | 26.9304 | 26.1916 | 24.7737 | 23.1369 | 21.4128 | 19.4831 | 17.4218 | 15.1195 | 12.5878 | 8.6098 | 0.098917 | -5.9066 | -9.3082 | 28.6924 | 28.4167 | 28.1326 | 27.7498 | 27.3049 | 26.7651 | 26.1926 | 25.4975 | 24.1818 | 22.6408 | 19.3251 | 11.7807 | 5.5373 | -6.8615 | 24.4268 | 23.6534 | 23.0284 | 21.8412 | 20.4578 | 18.9903 | 17.3082 | 15.5061 | 13.4633 | 11.1891 | 7.416 | -0.56075 | -6.1424 | -9.3851
|  |  | CT |  |  | 28.2812 | 27.596 | 27.0349 | 25.8474 | 24.4839 | 22.9068 | 21.2963 | 19.4434 | 16.9477 | 14.2493 | 10.0286 | 0.098917 | -5.9066 | -9.3082 | 28.6924 | 28.4167 | 28.1326 | 27.7498 | 27.3049 | 26.7651 | 26.1926 | 25.4975 | 24.1818 | 22.6408 | 19.3251 | 12.0026 | 7.0546 | -0.028695 | 24.763 | 24.2153 | 23.7321 | 22.7299 | 21.5751 | 20.217 | 18.814 | 17.1837 | 14.9708 | 12.5744 | 8.6459 | -0.56075 | -6.1424 | -9.3851
|  |  | LW |  |  | 27.8882 | 26.9304 | 26.1916 | 24.7737 | 23.1369 | 21.4128 | 19.4831 | 17.4218 | 15.1195 | 12.5878 | 8.6098 | 1.0167 | -2.7782 | -4.2796 | 28.7158 | 28.4356 | 28.2142 | 27.8761 | 27.469 | 27.0411 | 26.5202 | 26.016 | 25.2987 | 24.299 | 22.2945 | 17.6618 | 15.0948 | 13.2499 | 24.4268 | 23.6534 | 23.0284 | 21.8412 | 20.4578 | 18.9903 | 17.3082 | 15.5061 | 13.4633 | 11.1891 | 7.416 | 0.57844 | -3.1358 | -4.9059
|  |  | ST |  |  | 28.4835 | 27.9556 | 27.5566 | 26.8486 | 26.062 | 25.2486 | 24.4376 | 23.6366 | 22.6866 | 21.5717 | 19.6816 | 12.021 | 5.6135 | 1.1965 | 28.7735 | 28.5677 | 28.3639 | 28.0293 | 27.6694 | 27.2914 | 26.9096 | 26.5774 | 26.1225 | 25.613 | 24.6208 | 19.0983 | 11.6735 | 3.4857 | 24.9508 | 24.5516 | 24.2225 | 23.6395 | 22.9951 | 22.3233 | 21.6362 | 20.9653 | 20.1382 | 19.1727 | 17.3939 | 10.5872 | 4.2711 | -0.011806
|  |  | FS |  |  | 28.2812 | 27.596 | 27.0349 | 25.8474 | 24.4839 | 22.9068 | 21.2963 | 19.4434 | 16.9477 | 14.2493 | 10.0286 | 0.098917 | -5.9066 | -9.3082 | 28.7645 | 28.5552 | 28.3693 | 28.064 | 27.7058 | 27.2992 | 26.8497 | 26.3384 | 25.7213 | 24.8173 | 22.0005 | 11.7807 | 5.5373 | -6.8615 | 25.0081 | 24.6583 | 24.3953 | 23.8851 | 23.3096 | 22.6939 | 22.044 | 21.3348 | 20.4635 | 19.4722 | 17.4731 | 6.9239 | -1.0809 | -3.3877
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ 63405 99685 | YES | -9.4694 | -11.5181 | -13.7418 | -17.7987 | -22.2715 | -26.6096 | -31.8612 | -37.8591 | -44.0683 | -50.6861 | -64.5123 | -89.9408 | -99.7049 | -111.3516 | 17.0047 | 15.0222 | 12.6784 | 9.361 | 5.6906 | 1.4002 | -3.3201 | -9.119 | -15.8952 | -23.0759 | -40.64 | -108.3407 | -230.086 | -457.5358 | -5.0389 | -6.8661 | -8.8098 | -12.3067 | -16.2413 | -20.1338 | -25.0494 | -30.6879 | -36.5688 | -42.8893 | -56.162 | -80.341 | -94.2147 | -109.2797
|  |  | CT |  |  | -8.1762 | -9.4714 | -11.0493 | -14.2503 | -17.6606 | -21.3643 | -25.2419 | -30.1963 | -36.3966 | -42.6336 | -54.5715 | -81.4178 | -93.448 | -97.2171 | 17.0047 | 15.0222 | 12.6784 | 9.361 | 5.6906 | 1.4002 | -3.3201 | -9.119 | -15.8952 | -23.0759 | -38.2463 | -86.049 | -151.3998 | -258.5304 | -4.1471 | -5.3158 | -6.7368 | -9.4467 | -12.4206 | -15.8116 | -19.4096 | -24.1042 | -29.9456 | -35.827 | -47.0059 | -72.3998 | -83.7185 | -87.6311
|  |  | LW |  |  | -9.4694 | -11.5181 | -13.7418 | -17.7987 | -22.2715 | -26.6096 | -31.8612 | -37.8591 | -44.0683 | -50.6861 | -64.5123 | -89.9408 | -99.7049 | -111.3516 | 17.7022 | 16.523 | 15.2793 | 13.1654 | 10.7323 | 8.2637 | 4.9646 | 1.1575 | -2.884 | -7.2877 | -16.6078 | -33.6938 | -47.0243 | -59.7922 | -5.0389 | -6.8661 | -8.8098 | -12.3067 | -16.2413 | -20.1338 | -25.0494 | -30.6879 | -36.5688 | -42.8893 | -56.162 | -80.341 | -94.2147 | -109.2797
|  |  | ST |  |  | -7.0917 | -7.6694 | -8.4802 | -9.7712 | -11.1278 | -12.3844 | -13.8417 | -15.5624 | -17.6332 | -20.0492 | -26.3349 | -47.3899 | -63.1148 | -72.6014 | 17.571 | 16.0344 | 14.1771 | 11.55 | 8.6818 | 5.5488 | 1.922 | -2.1101 | -6.7419 | -12.0002 | -24.8879 | -72.0177 | -141.6862 | -251.6469 | -3.2283 | -3.7334 | -4.4361 | -5.6446 | -6.9148 | -8.1704 | -9.6933 | -11.4524 | -13.5917 | -16.1051 | -22.507 | -43.2636 | -58.9 | -67.8351
|  |  | FS |  |  | -8.1762 | -9.4714 | -11.0493 | -14.2503 | -17.6606 | -21.3643 | -25.2419 | -30.1963 | -36.3966 | -42.6336 | -54.5715 | -81.4178 | -93.448 | -97.2171 | 17.3896 | 15.5289 | 13.3337 | 9.9742 | 6.1196 | 1.8464 | -3.1927 | -8.9979 | -15.3892 | -22.6853 | -40.64 | -108.3407 | -230.086 | -457.5358 | -3.2836 | -3.8285 | -4.5048 | -5.6767 | -7.0152 | -8.4106 | -10.0821 | -12.1279 | -14.462 | -17.0916 | -23.484 | -43.2622 | -64.2389 | -80.2226
BRAMLEY (FLEE) | PYESTOCK BSP | PYESTOCK BSP | MINIMUM HEADROOM | SU 82940 54553 | YES | 53.999 | 53.6133 | 53.1677 | 52.3903 | 51.643 | 50.4537 | 49.1353 | 47.865 | 46.4774 | 45.1219 | 42.6443 | 37.8681 | 35.035 | 33.4435 | 56.4437 | 56.2696 | 56.0528 | 55.6942 | 55.3659 | 54.5531 | 53.6194 | 52.7803 | 51.9569 | 51.1815 | 49.6367 | 45.7778 | 42.4055 | 35.3354 | 53.768 | 53.4575 | 53.1029 | 52.4635 | 51.85 | 50.7223 | 49.4545 | 48.264 | 47.0054 | 45.7924 | 43.589 | 39.3478 | 36.8796 | 35.5657
|  |  | CT |  |  | 54.3567 | 54.1808 | 53.94 | 53.3775 | 52.8639 | 51.9088 | 50.8499 | 49.817 | 48.3719 | 46.9606 | 44.4081 | 38.6267 | 35.0668 | 33.4435 | 56.5199 | 56.378 | 56.1943 | 55.8785 | 55.5865 | 54.7949 | 53.8897 | 53.0535 | 52.1216 | 51.2328 | 49.6367 | 45.7778 | 42.4055 | 38.5162 | 54.0668 | 53.9302 | 53.7439 | 53.2744 | 52.8537 | 51.9196 | 50.8687 | 49.8733 | 48.5608 | 47.2951 | 45.0215 | 39.9121 | 36.8796 | 35.5657
|  |  | LW |  |  | 53.999 | 53.6133 | 53.1677 | 52.3903 | 51.643 | 50.4537 | 49.1353 | 47.865 | 46.4774 | 45.1219 | 42.6443 | 37.8681 | 35.035 | 34.0141 | 56.4437 | 56.2696 | 56.0528 | 55.6942 | 55.3659 | 54.5531 | 53.6194 | 52.7803 | 51.9569 | 51.1815 | 49.7993 | 47.1077 | 45.6752 | 45.1807 | 53.768 | 53.4575 | 53.1029 | 52.4635 | 51.85 | 50.7223 | 49.4545 | 48.264 | 47.0054 | 45.7924 | 43.589 | 39.3478 | 36.9277 | 36.0851
|  |  | ST |  |  | 54.4384 | 54.3116 | 54.1165 | 53.8733 | 53.6975 | 53.1569 | 52.5528 | 51.9775 | 51.4389 | 50.9255 | 50.0722 | 47.9557 | 45.5246 | 42.5269 | 56.5496 | 56.4261 | 56.2597 | 56.0501 | 55.8818 | 55.2844 | 54.5991 | 53.9511 | 53.3595 | 52.7993 | 51.7977 | 49.3847 | 46.3589 | 41.9081 | 54.1351 | 54.0398 | 53.8919 | 53.6898 | 53.5519 | 52.9814 | 52.3331 | 51.7273 | 51.1709 | 50.6496 | 49.7769 | 47.8365 | 45.7248 | 43.2289
|  |  | FS |  |  | 54.3567 | 54.1808 | 53.94 | 53.3775 | 52.8639 | 51.9088 | 50.8499 | 49.817 | 48.3719 | 46.9606 | 44.4081 | 38.6267 | 35.0668 | 33.4435 | 56.5201 | 56.3495 | 56.1377 | 55.8951 | 55.6599 | 55.0128 | 54.2764 | 53.493 | 52.7094 | 51.9583 | 50.501 | 46.8961 | 42.4954 | 35.3354 | 54.1103 | 53.9837 | 53.8094 | 53.5736 | 53.3616 | 52.7351 | 52.0317 | 51.2798 | 50.4943 | 49.7607 | 48.4214 | 45.5517 | 43.2532 | 41.1587
BRAMLEY (FLEE) | READING BSP | READING BSP | MINIMUM HEADROOM | SU 74642 73856 | YES | 53.7984 | 50.7494 | 47.6598 | 42.1517 | 35.3862 | 28.082 | 18.2605 | 6.8102 | -6.4301 | -20.7664 | -51.8703 | -111.3853 | -159.5572 | -183.6013 | 72.5949 | 70.7662 | 68.6698 | 65.4483 | 61.665 | 56.5132 | 50.6134 | 42.6413 | 32.495 | 21.9458 | 0.34877 | -53.8273 | -96.8009 | -186.9871 | 50.3005 | 47.4493 | 44.58 | 39.5425 | 33.3514 | 26.6429 | 17.459 | 6.6935 | -5.7576 | -19.3123 | -48.8205 | -105.0584 | -152.3387 | -175.2424
|  |  | CT |  |  | 55.7616 | 53.972 | 51.7478 | 47.1927 | 41.8682 | 34.927 | 27.1542 | 16.8624 | 2.4744 | -12.2475 | -41.9067 | -111.3853 | -159.5572 | -183.6013 | 72.6796 | 70.876 | 68.6698 | 65.4483 | 61.665 | 56.5132 | 50.6134 | 42.6413 | 32.495 | 21.9458 | 0.34877 | -53.8273 | -96.8009 | -145.0311 | 51.9997 | 50.2734 | 48.1357 | 43.9453 | 39.0684 | 32.6039 | 25.315 | 15.5628 | 2.041 | -11.8295 | -39.7382 | -105.0584 | -152.3387 | -175.2424
|  |  | LW |  |  | 53.7984 | 50.7494 | 47.6598 | 42.1517 | 35.3862 | 28.082 | 18.2605 | 6.8102 | -6.4301 | -20.7664 | -51.8703 | -107.721 | -131.068 | -134.114 | 72.5949 | 70.7662 | 68.9418 | 66.0209 | 62.2528 | 58.0975 | 51.9424 | 44.5488 | 36.0978 | 26.7286 | 6.0408 | -29.7896 | -43.2382 | -44.1443 | 50.3005 | 47.4493 | 44.58 | 39.5425 | 33.3514 | 26.6429 | 17.459 | 6.6935 | -5.7576 | -19.3123 | -48.8205 | -101.611 | -123.2415 | -125.821
|  |  | ST |  |  | 57.1549 | 56.513 | 55.6057 | 53.8752 | 51.5856 | 48.7531 | 45.1496 | 40.7702 | 35.6291 | 29.58 | 13.8223 | -39.0017 | -78.8508 | -102.6396 | 73.5252 | 72.5158 | 71.2291 | 69.2519 | 66.8563 | 63.9258 | 60.2359 | 55.8719 | 50.7584 | 44.7868 | 29.3924 | -22.4341 | -70.8045 | -119.2943 | 53.3126 | 52.6909 | 51.8226 | 50.1539 | 48.0149 | 45.3471 | 41.897 | 37.717 | 32.7579 | 26.9028 | 11.5607 | -40.0209 | -78.4644 | -99.9509
|  |  | FS |  |  | 55.7616 | 53.972 | 51.7478 | 47.1927 | 41.8682 | 34.927 | 27.1542 | 16.8624 | 2.4744 | -12.2475 | -41.9067 | -111.3853 | -159.5572 | -183.6013 | 73.4331 | 72.2414 | 70.7976 | 68.873 | 66.493 | 63.6172 | 60.1434 | 55.9414 | 50.8993 | 45.2143 | 31.0133 | -21.137 | -92.8561 | -186.9871 | 53.2556 | 52.5728 | 51.6904 | 50.1444 | 48.1643 | 45.7159 | 42.7496 | 39.0821 | 34.4359 | 29.3003 | 16.6031 | -28.3657 | -77.3434 | -111.4003
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN BSP | MINIMUM HEADROOM | SU 71580 74111 | YES | 34.5177 | 32.1828 | 29.8437 | 26.7694 | 23.4162 | 19.8776 | 15.514 | 11.0568 | 6.0745 | 0.27277 | -11.6095 | -31.1838 | -45.883 | -54.2826 | 43.891 | 42.3161 | 40.7095 | 38.9789 | 37.1338 | 35.0493 | 32.3664 | 30.1222 | 26.5924 | 21.9056 | 13.0221 | -8.8888 | -36.3263 | -84.8743 | 29.8137 | 27.7548 | 25.6838 | 22.9764 | 19.9753 | 16.6968 | 12.4854 | 8.3253 | 3.6836 | -1.5665 | -12.238 | -30.7153 | -45.6349 | -53.7601
|  |  | CT |  |  | 35.3032 | 33.4183 | 31.4364 | 28.9658 | 26.3426 | 22.9766 | 19.355 | 15.157 | 9.6147 | 3.6445 | -7.5038 | -31.1838 | -45.883 | -54.2826 | 44.1221 | 42.5083 | 40.7889 | 39.2693 | 37.614 | 35.2297 | 32.6077 | 30.1222 | 26.5924 | 21.9056 | 13.0221 | -8.8888 | -27.9239 | -52.3783 | 30.5041 | 28.8661 | 27.1 | 24.9305 | 22.5847 | 19.3881 | 15.9 | 12.0517 | 7.0283 | 1.5738 | -8.563 | -30.7153 | -45.6349 | -53.7601
|  |  | LW |  |  | 34.5177 | 32.1828 | 29.8437 | 26.7694 | 23.4162 | 19.8776 | 15.514 | 11.0568 | 6.0745 | 0.27277 | -11.6095 | -30.7203 | -36.9789 | -37.8198 | 43.891 | 42.3161 | 40.7095 | 38.9789 | 37.1338 | 35.0493 | 32.3664 | 30.1676 | 27.6606 | 24.4847 | 16.4283 | 3.5509 | -0.69275 | -1.5256 | 29.8137 | 27.7548 | 25.6838 | 22.9764 | 19.9753 | 16.6968 | 12.4854 | 8.3253 | 3.6836 | -1.5665 | -12.238 | -30.3764 | -36.4229 | -37.4027
|  |  | ST |  |  | 36.0032 | 34.612 | 33.1689 | 31.9374 | 30.6414 | 28.9914 | 27.1089 | 25.2627 | 22.9996 | 20.1289 | 13.8969 | -5.2653 | -18.2423 | -24.7922 | 44.4653 | 43.0958 | 41.6448 | 40.6308 | 39.5482 | 37.9386 | 36.1485 | 34.8193 | 33.1065 | 30.8492 | 24.765 | 3.7217 | -17.57 | -42.0758 | 31.1496 | 29.977 | 28.7213 | 27.6605 | 26.5094 | 24.8857 | 23.0409 | 21.4396 | 19.4496 | 16.904 | 11.4092 | -7.316 | -20.0914 | -26.3279
|  |  | FS |  |  | 35.3032 | 33.4183 | 31.4364 | 28.9658 | 26.3426 | 22.9766 | 19.355 | 15.157 | 9.6147 | 3.6445 | -7.5038 | -31.1838 | -45.883 | -54.2826 | 44.6991 | 43.6212 | 42.4563 | 41.2855 | 40.0357 | 38.5962 | 36.9604 | 35.2984 | 33.21 | 30.1395 | 22.8755 | -1.6577 | -36.3263 | -84.8743 | 31.2634 | 30.2907 | 29.2606 | 28.0691 | 26.7779 | 25.294 | 23.584 | 21.7208 | 19.6398 | 17.2598 | 11.6717 | -6.6722 | -25.7782 | -38.0508
MANNINGTON GSP | REDHILL BSP | REDHILL BSP | MINIMUM HEADROOM | SZ 08581 96162 | YES | 30.7343 | 28.5962 | 26.2833 | 22.1896 | 17.4112 | 12.2568 | 6.0918 | -1.034 | -8.9497 | -17.5916 | -36.8951 | -114.0547 | -166.4713 | -183.5957 | 41.118 | 39.7752 | 38.3483 | 36.1025 | 33.405 | 30.4523 | 26.8219 | 22.4946 | 17.7779 | 12.1864 | -6.5795 | -65.8966 | -105.6531 | -118.9211 | 40.261 | 38.3856 | 36.37 | 32.9293 | 28.6618 | 24.0161 | 18.2407 | 11.4496 | 3.8894 | -4.4754 | -28.9707 | -104.4942 | -154.5825 | -171.0256
|  |  | CT |  |  | 32.1296 | 30.724 | 29.1639 | 25.8846 | 22.0517 | 17.5155 | 12.5862 | 6.2544 | -2.387 | -11.4364 | -30.2454 | -100.9121 | -144.1177 | -161.7173 | 41.5482 | 40.3549 | 39.1121 | 37.1124 | 34.712 | 31.8234 | 28.6526 | 24.4456 | 18.7204 | 12.3853 | -3.8016 | -55.2428 | -86.5578 | -99.2695 | 41.2283 | 39.882 | 38.374 | 35.564 | 32.2501 | 28.1622 | 23.5076 | 17.3599 | 9.1152 | 0.44019 | -24.3915 | -91.6982 | -132.6613 | -149.3132
|  |  | LW |  |  | 30.7343 | 28.5962 | 26.2833 | 22.1896 | 17.4112 | 12.2568 | 6.0918 | -1.034 | -8.9497 | -17.5916 | -36.8951 | -114.0547 | -166.4713 | -183.5957 | 41.118 | 39.7752 | 38.3483 | 36.1025 | 33.405 | 30.4523 | 26.8219 | 22.4946 | 17.7779 | 12.1864 | -6.5795 | -65.8966 | -105.6531 | -118.9211 | 40.261 | 38.3856 | 36.37 | 32.9293 | 28.6618 | 24.0161 | 18.2407 | 11.4496 | 3.8894 | -4.4754 | -28.9707 | -104.4942 | -154.5825 | -171.0256
|  |  | ST |  |  | 32.7026 | 31.7639 | 30.7435 | 29.3632 | 27.5801 | 25.6439 | 23.3806 | 20.5484 | 17.4119 | 13.2836 | 2.7027 | -32.7694 | -57.9888 | -70.3422 | 41.8792 | 40.9813 | 40.096 | 38.9435 | 37.503 | 35.9631 | 34.1991 | 31.909 | 28.9101 | 25.3181 | 16.0718 | -14.4098 | -38.0157 | -54.6686 | 41.7001 | 40.779 | 39.7738 | 38.4092 | 36.6465 | 34.6707 | 32.2473 | 29.19 | 25.7793 | 21.6631 | 10.9847 | -24.4494 | -48.959 | -59.2001
|  |  | FS |  |  | 32.1296 | 30.724 | 29.1639 | 25.8846 | 22.0517 | 17.5155 | 12.5862 | 6.2544 | -2.387 | -11.4364 | -30.2454 | -100.9121 | -144.1177 | -161.7173 | 42.094 | 41.4123 | 40.6323 | 39.6604 | 38.5071 | 37.2102 | 35.757 | 34.0255 | 31.8665 | 29.4453 | 22.5907 | -2.4424 | -35.73 | -73.255 | 41.9548 | 41.3138 | 40.5386 | 39.4461 | 38.1215 | 36.5942 | 34.8335 | 32.6902 | 30.1175 | 27.246 | 20.113 | -5.5238 | -34.3462 | -53.5341
NURSLING GSP | ROWNHAMS | ROWNHAMS | MINIMUM HEADROOM | SU 37168 16854 | YES | -0.67027 | -3.1024 | -5.4421 | 77.4118 | 72.7014 | 67.5989 | 60.6888 | 52.9158 | 44.0601 | 34.3437 | -2.0054 | -76.5206 | -105.624 | -122.9098 | 25.2954 | 23.64 | 22.1289 | 105.8956 | 102.7697 | 99.3079 | 94.5362 | 89.238 | 80.5126 | 67.6114 | 38.2106 | -15.1843 | -35.0579 | -48.1493 | 14.7155 | 12.1927 | 9.7911 | 91.8609 | 86.8895 | 81.4939 | 74.492 | 66.776 | 57.9386 | 44.5458 | 6.541 | -64.2745 | -91.9508 | -108.8012
|  |  | CT |  |  | 0.7954 | -0.85436 | -2.4948 | 81.2157 | 77.5376 | 72.9268 | 67.3766 | 60.4325 | 50.9582 | 37.8965 | -2.0054 | -76.5206 | -105.624 | -122.9098 | 25.899 | 24.4007 | 23.029 | 107.1247 | 104.3342 | 100.8624 | 96.481 | 91.1339 | 80.5126 | 67.6114 | 38.2106 | -15.1843 | -35.0579 | -48.1493 | 16.5782 | 14.9747 | 13.4683 | 96.6039 | 92.783 | 88.1343 | 82.4568 | 75.5902 | 61.2814 | 44.5458 | 6.541 | -64.2745 | -91.9508 | -108.8012
|  |  | LW |  |  | -0.67027 | -3.1024 | -5.4421 | 77.4118 | 72.7014 | 67.5989 | 60.6888 | 52.9158 | 44.0601 | 34.3437 | 13.4415 | -44.9417 | -76.5553 | -94.1729 | 25.2954 | 23.64 | 22.1289 | 105.8956 | 102.7697 | 99.3079 | 94.5362 | 89.238 | 83.3531 | 75.0105 | 52.3682 | 9.1783 | -14.9639 | -30.3815 | 14.7155 | 12.1927 | 9.7911 | 91.8609 | 86.8895 | 81.4939 | 74.492 | 66.776 | 57.9386 | 48.3608 | 22.3767 | -34.2831 | -65.1022 | -83.1846
|  |  | ST |  |  | 1.9316 | 1.1044 | 0.37839 | 85.7339 | 83.974 | 81.974 | 79.1587 | 76.1243 | 72.6242 | 68.6008 | 58.7193 | 27.7429 | 2.515 | -15.4298 | 26.6326 | 25.677 | 24.9249 | 109.7861 | 108.0976 | 106.2644 | 103.677 | 101.0576 | 98.0142 | 94.6762 | 86.5456 | 58.0785 | 30.4072 | 1.0666 | 17.8177 | 17.0568 | 16.4804 | 101.4709 | 99.8926 | 98.1575 | 95.6452 | 92.9712 | 89.7449 | 86.1357 | 77.3773 | 47.3656 | 22.1269 | 3.1153
|  |  | FS |  |  | 0.7954 | -0.85436 | -2.4948 | 81.2157 | 77.5376 | 72.9268 | 67.3766 | 60.4325 | 50.9582 | 37.8965 | -2.0054 | -76.5206 | -105.624 | -122.9098 | 26.6108 | 25.7129 | 24.8021 | 109.8785 | 108.3235 | 106.513 | 104.2811 | 101.6522 | 98.3958 | 94.8475 | 86.254 | 56.3757 | 18.5916 | -33.9251 | 17.7762 | 17.0947 | 16.4202 | 101.5269 | 100.0168 | 98.2553 | 96.0427 | 93.2125 | 89.697 | 85.9281 | 77.3885 | 48.4858 | 19.6404 | -2.2542
MANNINGTON GSP | SALISBURY | SALISBURY | MINIMUM HEADROOM | SU 11049 31395 | YES | 35.0832 | 32.2519 | 29.6244 | 26.2029 | 21.968 | 17.1549 | 11.1458 | 4.4829 | -5.568 | -17.2922 | -45.4307 | -107.8382 | -143.4294 | -160.0845 | 47.742 | 46.0412 | 44.6113 | 42.6822 | 40.0845 | 37.1569 | 33.454 | 29.2529 | 24.6878 | 19.5789 | 0.78521 | -45.3994 | -72.195 | -85.6224 | 42.9921 | 40.384 | 38.0186 | 34.8622 | 30.8969 | 26.4587 | 20.8964 | 14.6718 | 7.7706 | -1.6714 | -28.4843 | -87.936 | -122.1135 | -138.5161
|  |  | CT |  |  | 36.7901 | 34.8531 | 33.198 | 30.5113 | 26.9068 | 22.5648 | 17.7536 | 11.9219 | 4.2031 | -4.6219 | -27.3824 | -81.6745 | -107.1722 | -114.9443 | 48.2793 | 46.6783 | 45.5329 | 43.8127 | 41.2178 | 38.2669 | 34.9804 | 30.7942 | 25.6293 | 20.1762 | 8.4903 | -25.3683 | -42.6476 | -56.8122 | 44.4831 | 42.5933 | 41.1004 | 38.621 | 35.1922 | 31.2029 | 26.696 | 21.1498 | 13.8921 | 6.3417 | -11.4341 | -63.0439 | -87.1053 | -94.504
|  |  | LW |  |  | 35.0832 | 32.2519 | 29.6244 | 26.2029 | 21.968 | 17.1549 | 11.1458 | 4.4829 | -5.568 | -17.2922 | -45.4307 | -107.8382 | -143.4294 | -160.0845 | 47.742 | 46.0412 | 44.6113 | 42.6822 | 40.0845 | 37.1569 | 33.454 | 29.2529 | 24.6878 | 19.5789 | 0.78521 | -45.3994 | -72.195 | -85.6224 | 42.9921 | 40.384 | 38.0186 | 34.8622 | 30.8969 | 26.4587 | 20.8964 | 14.6718 | 7.7706 | -1.6714 | -28.4843 | -87.936 | -122.1135 | -138.5161
|  |  | ST |  |  | 37.7558 | 36.4549 | 35.5453 | 34.0736 | 31.9432 | 29.5684 | 26.9215 | 24.0808 | 21.03 | 17.7629 | 9.5443 | -18.7018 | -39.9484 | -53.3312 | 48.7889 | 47.5652 | 46.8666 | 45.5684 | 43.6392 | 41.7397 | 39.6398 | 37.4209 | 34.8841 | 32.2001 | 25.1814 | 0.50556 | -20.9777 | -40.4119 | 45.3683 | 44.0762 | 43.2713 | 41.7811 | 39.6321 | 37.4363 | 34.9448 | 32.2779 | 29.3342 | 26.1629 | 18.1324 | -9.3697 | -29.7204 | -42.06
|  |  | FS |  |  | 36.7901 | 34.8531 | 33.198 | 30.5113 | 26.9068 | 22.5648 | 17.7536 | 11.9219 | 4.2031 | -4.6219 | -27.3824 | -81.6745 | -107.1722 | -114.9443 | 48.8624 | 47.8815 | 46.9639 | 45.7156 | 44.0592 | 42.1249 | 39.813 | 37.1405 | 34.005 | 30.4482 | 11.19 | -32.4402 | -52.0885 | -71.2825 | 45.5408 | 44.5799 | 43.6805 | 42.2818 | 40.4628 | 38.3345 | 35.8071 | 31.1774 | 23.2237 | 13.5398 | -10.7812 | -65.6693 | -91.2332 | -105.5672
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST 85442 23791 | YES | 30.7153 | 27.8546 | 24.8372 | 21.4152 | 17.1682 | 12.3126 | 6.2538 | -6.7209 | -23.7944 | -44.4432 | -94.0963 | -199.2831 | -246.9041 | -268.4677 | 41.8065 | 40.0999 | 38.2875 | 36.3109 | 33.7703 | 30.7621 | 26.7175 | 19.6336 | 6.7793 | -8.9133 | -46.8211 | -126.9536 | -162.3552 | -178.7299 | 26.9696 | 24.3903 | 21.6789 | 18.6429 | 14.9083 | 10.5896 | 3.7789 | -8.7691 | -25.0541 | -44.7949 | -92.3087 | -192.9942 | -238.4646 | -259.1918
|  |  | CT |  |  | 32.1113 | 30.1123 | 27.7257 | 24.6322 | 20.7985 | 15.4942 | 6.4205 | -6.7209 | -23.7944 | -44.4432 | -94.0963 | -199.2831 | -246.9041 | -268.4677 | 42.2143 | 40.8105 | 39.0959 | 37.1392 | 34.6827 | 30.9881 | 26.8878 | 19.6336 | 6.7793 | -8.9133 | -46.8211 | -126.9536 | -162.3552 | -178.7299 | 28.2482 | 26.4509 | 24.3056 | 21.5464 | 18.1282 | 13.1516 | 3.7789 | -8.7691 | -25.0541 | -44.7949 | -92.3087 | -192.9942 | -238.4646 | -259.1918
|  |  | LW |  |  | 30.7153 | 27.8546 | 24.8372 | 21.4152 | 17.1682 | 12.3126 | 6.2538 | -0.8254 | -9.1047 | -20.2875 | -51.5442 | -114.1871 | -138.6318 | -148.4199 | 41.8065 | 40.0999 | 38.2875 | 36.3109 | 33.7703 | 30.7621 | 26.7175 | 21.8149 | 16.0602 | 9.4096 | -12.1827 | -59.1841 | -77.5664 | -85.6204 | 26.9696 | 24.3903 | 21.6789 | 18.6429 | 14.9083 | 10.5896 | 5.2047 | -1.3703 | -9.1476 | -21.2711 | -51.0932 | -110.8254 | -134.34 | -144.1008
|  |  | ST |  |  | 33.1131 | 31.8953 | 30.4475 | 28.7108 | 26.5815 | 23.7674 | 20.8557 | 17.532 | 13.56 | 8.6675 | -3.4732 | -40.8986 | -65.7255 | -76.5839 | 42.7799 | 41.8949 | 40.8216 | 39.568 | 38.0624 | 35.9389 | 33.6539 | 31.003 | 27.7595 | 23.9439 | 14.478 | -15.6126 | -36.1881 | -46.2108 | 29.1954 | 28.1319 | 26.874 | 25.3554 | 23.5512 | 21.1065 | 18.4121 | 15.2999 | 11.3091 | 6.5496 | -5.1938 | -41.7781 | -66.0533 | -76.2208
|  |  | FS |  |  | 32.1113 | 30.1123 | 27.7257 | 24.6322 | 20.7985 | 15.4942 | 6.4205 | -6.7209 | -23.7944 | -44.4432 | -94.0963 | -199.2831 | -246.9041 | -268.4677 | 42.7312 | 41.6039 | 40.3161 | 38.7843 | 36.888 | 34.5096 | 31.5951 | 27.9334 | 23.6697 | 18.8223 | 7.1895 | -28.7175 | -61.4484 | -82.8345 | 29.3176 | 28.0992 | 26.7321 | 24.9008 | 22.6666 | 19.785 | 16.3312 | 11.7619 | 6.3666 | 0.27914 | -14.1609 | -61.4572 | -99.5998 | -117.0545
IVER 132KV | SLOUGH | SLOUGH | MINIMUM HEADROOM | SU 95574 81752 | YES | 1.3052 | 0.12773 | -0.93109 | -11.1952 | -21.7676 | -27.242 | -33.8717 | -40.1727 | -48.007 | -58.6703 | -83.208 | -135.5664 | -164.4986 | -179.1238 | 7.6169 | 7.2428 | 6.865 | -3.9517 | -14.985 | -19.6934 | -25.6032 | -30.915 | -35.7064 | -42.963 | -61.5085 | -102.94 | -125.7736 | -137.5319 | 3.0797 | 2.5387 | 1.9877 | -9.0782 | -20.9501 | -26.9704 | -34.8748 | -44.1787 | -53.8827 | -64.5496 | -88.701 | -140.0407 | -168.213 | -182.4776
|  |  | CT |  |  | 2.194 | 1.5834 | 1.0438 | -8.5958 | -18.3876 | -23.1539 | -28.6419 | -33.8586 | -39.575 | -44.9776 | -54.9833 | -78.146 | -90.6693 | -96.8339 | 7.6804 | 7.4244 | 7.1759 | -3.3563 | -13.9826 | -18.1583 | -23.1472 | -27.4264 | -31.1179 | -34.9136 | -43.0707 | -61.5319 | -73.8235 | -85.7377 | 3.2469 | 2.9312 | 2.6328 | -7.9828 | -18.7199 | -23.1035 | -29.2588 | -34.897 | -40.7764 | -46.2388 | -56.1417 | -81.7356 | -96.2588 | -102.1924
|  |  | LW |  |  | 1.3052 | 0.12773 | -0.93109 | -11.1952 | -21.7676 | -27.242 | -33.8717 | -40.1727 | -48.007 | -58.6703 | -83.208 | -135.5664 | -164.4986 | -179.1238 | 7.6169 | 7.2428 | 6.865 | -3.9517 | -14.985 | -19.6934 | -25.6032 | -30.915 | -35.7064 | -42.963 | -61.5085 | -102.94 | -125.7736 | -137.5319 | 3.0797 | 2.5387 | 1.9877 | -9.0782 | -20.9501 | -26.9704 | -34.8748 | -44.1787 | -53.8827 | -64.5496 | -88.701 | -140.0407 | -168.213 | -182.4776
|  |  | ST |  |  | 2.6195 | 2.3168 | 2.111 | -6.5053 | -15.1877 | -18.2922 | -21.9918 | -25.3588 | -28.3808 | -31.1904 | -36.5952 | -51.898 | -62.9066 | -69.5122 | 7.81 | 7.6631 | 7.5427 | -3.0013 | -13.5327 | -17.077 | -21.2642 | -24.9089 | -28.0001 | -30.6692 | -35.1012 | -47.9618 | -60.5592 | -72.4134 | 3.4417 | 3.2861 | 3.175 | -7.3717 | -17.9153 | -21.4701 | -25.6748 | -29.3464 | -32.4682 | -35.1804 | -40.0699 | -55.8198 | -66.6364 | -72.3899
|  |  | FS |  |  | 2.194 | 1.5834 | 1.0438 | -8.5958 | -18.3876 | -23.1539 | -28.6419 | -33.8586 | -39.575 | -44.9776 | -54.9833 | -78.146 | -90.6693 | -96.8339 | 7.8072 | 7.6227 | 7.4506 | -2.9948 | -13.4941 | -16.7825 | -20.604 | -24.3475 | -27.4913 | -30.27 | -35.5796 | -50.8431 | -71.0391 | -95.6814 | 3.4224 | 3.2321 | 3.0675 | -7.3904 | -17.9172 | -21.2403 | -25.1106 | -28.9275 | -32.1451 | -35.0267 | -40.8952 | -58.0279 | -74.1966 | -83.9301
NURSLING GSP | SOUTHAMPTON (2 X 60) | SOUTHAMPTON (2 X 60) | MINIMUM HEADROOM | SU 41425 11999 | YES | 12.5726 | 10.8976 | 9.038 | 7.4111 | 6.2724 | 4.9646 | 3.3525 | 0.74606 | -1.4523 | -3.72 | -9.6252 | -23.4302 | -28.0001 | -31.3941 | 21.1096 | 19.9897 | 18.8477 | 17.734 | 16.8509 | 15.5245 | 13.9145 | 11.3336 | 8.9718 | 6.2317 | -0.85825 | -29.6856 | -78.8969 | -164.5152 | 9.9362 | 8.4414 | 7.0039 | 5.6533 | 4.6675 | 3.5217 | 2.1192 | -0.23684 | -2.1658 | -4.1682 | -10.886 | -25.3438 | -36.2355 | -40.7292
|  |  | CT |  |  | 12.7361 | 11.4709 | 9.9247 | 8.4877 | 7.5841 | 6.2052 | 4.6419 | 1.9905 | -0.46566 | -2.8599 | -9.6252 | -23.4302 | -28.0001 | -31.3941 | 21.1096 | 19.9897 | 18.8477 | 17.734 | 16.8509 | 15.5245 | 13.9145 | 11.3336 | 8.9718 | 6.2317 | 0.20904 | -18.0326 | -43.1432 | -84.6415 | 10.1696 | 8.923 | 7.6678 | 6.454 | 5.6805 | 4.4792 | 3.145 | 0.74949 | -1.4074 | -3.558 | -10.886 | -25.3438 | -29.9593 | -33.3761
|  |  | LW |  |  | 12.5726 | 10.8976 | 9.038 | 7.4111 | 6.2724 | 4.9646 | 3.3525 | 0.74606 | -1.4523 | -3.72 | -8.2682 | -15.4154 | -18.1573 | -19.323 | 21.276 | 20.2633 | 19.326 | 18.5023 | 17.884 | 17.1554 | 16.1697 | 14.4728 | 13.0564 | 11.5725 | 8.5202 | 3.6408 | 1.4196 | -0.50687 | 9.9362 | 8.4414 | 7.0039 | 5.6533 | 4.6675 | 3.5217 | 2.1192 | -0.23684 | -2.1658 | -4.1682 | -8.2369 | -15.4331 | -18.6742 | -21.5885
|  |  | ST |  |  | 13.3144 | 12.3902 | 11.4248 | 10.6777 | 10.4607 | 9.9893 | 9.4306 | 8.2261 | 7.3831 | 6.5335 | 4.5353 | -1.0472 | -5.4898 | -8.3089 | 21.3777 | 20.4507 | 19.5227 | 18.6697 | 18.0453 | 17.1834 | 16.2122 | 14.4785 | 13.0027 | 11.1609 | 6.2541 | -11.0961 | -36.6909 | -78.4734 | 10.7695 | 9.8834 | 9.0259 | 8.422 | 8.2652 | 7.884 | 7.4671 | 6.3931 | 5.7069 | 5.0044 | 3.2957 | -1.5954 | -5.7689 | -9.0439
|  |  | FS |  |  | 12.7361 | 11.4709 | 9.9247 | 8.4877 | 7.5841 | 6.2052 | 4.6419 | 1.9905 | -0.46566 | -2.8599 | -9.6252 | -23.4302 | -28.0001 | -31.3941 | 21.3386 | 20.4229 | 19.4788 | 18.4122 | 17.4052 | 16.0613 | 14.353 | 12.1426 | 9.6206 | 6.6135 | -0.85825 | -29.6856 | -78.8969 | -164.5152 | 10.7546 | 10.048 | 9.3693 | 8.718 | 8.2702 | 7.6645 | 6.9929 | 5.9185 | 4.9713 | 3.8874 | 0.95627 | -21.2078 | -36.2355 | -40.7292
NURSLING GSP | SOUTHAMPTON (2 X 90) | SOUTHAMPTON (2 X 90) | MINIMUM HEADROOM | SU 41425 11999 | YES | 34.4545 | 32.8349 | 30.7022 | 28.1091 | 24.497 | 21.0442 | 17.0626 | 12.8629 | 8.6674 | 3.7721 | -6.6165 | -31.0748 | -43.4648 | -47.6112 | 38.0289 | 36.8989 | 35.2248 | 33.4644 | 31.0208 | 28.6243 | 25.8513 | 22.6254 | 19.5715 | 16.1804 | 9.2312 | -10.1895 | -31.089 | -81.6468 | 27.9039 | 26.425 | 24.4656 | 21.97 | 18.5302 | 15.1133 | 11.1019 | 6.787 | 2.4453 | -2.0186 | -11.4311 | -31.8495 | -43.9945 | -48.4785
|  |  | CT |  |  | 35.3809 | 34.0735 | 32.273 | 30.1988 | 27.2406 | 24.4927 | 21.5489 | 18.2041 | 14.1047 | 9.2355 | -0.57103 | -21.9676 | -32.2845 | -38.1422 | 38.1182 | 36.8989 | 35.2248 | 33.4644 | 31.0208 | 28.6243 | 25.9473 | 22.8555 | 19.5715 | 16.1804 | 9.2312 | -10.1895 | -28.5378 | -53.9375 | 28.7403 | 27.5232 | 25.8552 | 23.8254 | 20.9776 | 18.2496 | 15.2075 | 11.6896 | 7.5745 | 3.2354 | -5.4093 | -24.7514 | -34.5859 | -39.9803
|  |  | LW |  |  | 34.4545 | 32.8349 | 30.7022 | 28.1091 | 24.497 | 21.0442 | 17.0626 | 12.8629 | 8.6674 | 3.7721 | -6.6165 | -31.0748 | -43.4648 | -47.6112 | 38.0289 | 36.9766 | 35.5501 | 33.8392 | 31.4021 | 28.9022 | 25.8513 | 22.6254 | 19.5922 | 16.6208 | 10.403 | -8.821 | -18.5108 | -22.4839 | 27.9039 | 26.425 | 24.4656 | 21.97 | 18.5302 | 15.1133 | 11.1019 | 6.787 | 2.4453 | -2.0186 | -11.4311 | -31.8495 | -43.9945 | -48.4785
|  |  | ST |  |  | 36.0938 | 35.1697 | 33.778 | 32.7845 | 30.8834 | 29.1397 | 27.0977 | 24.5872 | 21.9937 | 19.2961 | 13.4395 | -5.608 | -16.7347 | -21.8923 | 38.3229 | 37.2392 | 35.7004 | 34.2878 | 32.3184 | 30.4634 | 28.3609 | 25.9617 | 23.6571 | 21.4367 | 16.175 | -3.7222 | -23.7731 | -48.2806 | 29.2559 | 28.2916 | 26.9056 | 25.8102 | 24.0962 | 22.569 | 20.7889 | 18.6734 | 16.6144 | 14.1582 | 8.2548 | -10.7209 | -21.7532 | -26.3455
|  |  | FS |  |  | 35.3809 | 34.0735 | 32.273 | 30.1988 | 27.2406 | 24.4927 | 21.5489 | 18.2041 | 14.1047 | 9.2355 | -0.57103 | -21.9676 | -32.2845 | -38.1422 | 38.3567 | 37.7581 | 36.7321 | 35.6346 | 34.1316 | 32.6519 | 31.0167 | 29.1864 | 27.1417 | 25.003 | 20.2441 | 1.1089 | -31.089 | -81.6468 | 29.3407 | 28.9019 | 28.1679 | 27.3862 | 26.198 | 25.1214 | 23.9734 | 22.6861 | 21.3288 | 19.9548 | 17.0654 | 5.7251 | -9.5842 | -21.0677
EALING GSP | SOUTHFIELD ROAD | SOUTHFIELD ROAD | MINIMUM HEADROOM | TQ 20533 79746 | YES | 31.1211 | 31.0784 | 31.0222 | 30.9416 | 30.8368 | 30.6998 | 30.5248 | 30.2929 | 30.0306 | 29.7022 | 26.9574 | 21.2568 | 19.7395 | 18.6131 | 34.0406 | 33.8941 | 33.7304 | 33.5337 | 33.2972 | 33.0047 | 32.6151 | 32.1015 | 31.5151 | 30.8886 | 29.5425 | 25.9283 | 21.7012 | 14.4916 | 31.693 | 31.584 | 31.4658 | 31.3293 | 31.1621 | 30.9408 | 30.6238 | 30.1739 | 29.656 | 29.119 | 28.0431 | 22.5619 | 21.1147 | 20.0375
|  |  | CT |  |  | 31.1647 | 31.1413 | 31.1081 | 31.0343 | 30.9421 | 30.8195 | 30.6545 | 30.4395 | 30.1546 | 29.8089 | 26.9574 | 21.2568 | 19.7395 | 18.6131 | 34.1184 | 34.0551 | 33.9773 | 33.8752 | 33.7468 | 33.5844 | 33.3829 | 33.1368 | 32.8413 | 32.491 | 31.6399 | 27.2918 | 26.0958 | 23.0502 | 31.7807 | 31.7609 | 31.7324 | 31.673 | 31.5974 | 31.4958 | 31.3584 | 31.1787 | 30.9392 | 30.6296 | 28.056 | 22.5619 | 21.1147 | 20.0375
|  |  | LW |  |  | 31.1628 | 31.1432 | 31.1236 | 31.0835 | 31.0419 | 30.9994 | 30.9465 | 30.8915 | 30.8237 | 30.753 | 30.5882 | 30.1441 | 29.7751 | 29.5622 | 34.1643 | 34.1569 | 34.1493 | 34.1349 | 34.1199 | 34.1035 | 34.0823 | 34.0595 | 34.0302 | 33.9983 | 33.922 | 33.7045 | 33.4937 | 33.3713 | 31.7831 | 31.7692 | 31.7549 | 31.7263 | 31.6962 | 31.6651 | 31.6258 | 31.5843 | 31.5325 | 31.4778 | 31.3492 | 31.0001 | 30.691 | 30.514
|  |  | ST |  |  | 31.1211 | 31.0784 | 31.0222 | 30.9416 | 30.8368 | 30.6998 | 30.5248 | 30.2929 | 30.0306 | 29.7022 | 28.7886 | 25.495 | 22.6397 | 21.4309 | 34.0745 | 33.9906 | 33.8868 | 33.7583 | 33.5948 | 33.3919 | 33.1438 | 32.8401 | 32.5027 | 32.0969 | 31.0134 | 27.0439 | 22.4878 | 17.561 | 31.7278 | 31.6827 | 31.6228 | 31.5386 | 31.4283 | 31.2835 | 31.0972 | 30.8526 | 30.5751 | 30.2286 | 29.2615 | 25.84 | 22.9278 | 21.7145
|  |  | FS |  |  | 31.1647 | 31.1413 | 31.1081 | 31.0343 | 30.9421 | 30.8195 | 30.6545 | 30.4395 | 30.1546 | 29.8089 | 26.9574 | 21.2568 | 19.7395 | 18.6131 | 34.0406 | 33.8941 | 33.7304 | 33.5337 | 33.2972 | 33.0047 | 32.6151 | 32.1015 | 31.5151 | 30.8886 | 29.5425 | 25.9283 | 21.7012 | 14.4916 | 31.693 | 31.584 | 31.4658 | 31.3293 | 31.1621 | 30.9408 | 30.6238 | 30.1739 | 29.656 | 29.119 | 28.0431 | 25.9668 | 25.324 | 25.4148
LALEHAM | STAINES | STAINES | MINIMUM HEADROOM | TQ 04585 72135 | YES | 68.7024 | 66.0278 | 63.507 | 59.399 | 54.7198 | 48.6364 | 41.7465 | 34.1755 | 25.8072 | 13.7629 | -22.9209 | -100.9967 | -142.3739 | -162.1912 | 79.1591 | 77.763 | 76.4378 | 74.4724 | 72.1161 | 68.1848 | 63.2527 | 54.8574 | 44.1276 | 32.1501 | 4.6222 | -52.8457 | -82.7565 | -97.3097 | 67.5895 | 65.3169 | 63.1381 | 59.4623 | 55.2908 | 49.4668 | 42.7733 | 35.5956 | 27.7875 | 19.5641 | -11.2557 | -85.7003 | -124.9713 | -143.7737
|  |  | CT |  |  | 70.1055 | 68.4448 | 66.6806 | 63.3651 | 59.5284 | 53.7023 | 47.5127 | 40.0858 | 29.7039 | 13.7629 | -22.9209 | -100.9967 | -142.3739 | -162.1912 | 79.2817 | 78.0625 | 76.7044 | 74.785 | 72.518 | 68.199 | 63.3161 | 54.8574 | 44.1276 | 32.1501 | 4.6222 | -52.8457 | -82.7565 | -97.3097 | 68.8571 | 67.5109 | 66.0372 | 63.1166 | 59.7282 | 54.1696 | 48.1099 | 41.0243 | 31.7344 | 22.1686 | -11.2557 | -85.7003 | -124.9713 | -143.7737
|  |  | LW |  |  | 68.7024 | 66.0278 | 63.507 | 59.399 | 54.7198 | 48.6364 | 41.7465 | 34.1755 | 25.8072 | 16.9133 | -1.9032 | -32.7332 | -44.8037 | -46.8859 | 79.1591 | 77.763 | 76.4378 | 74.4724 | 72.1161 | 68.1848 | 63.2527 | 57.9696 | 52.4636 | 46.7041 | 33.3279 | 7.5033 | -2.3826 | -5.5123 | 67.5895 | 65.3169 | 63.1381 | 59.4623 | 55.2908 | 49.4668 | 42.7733 | 35.5956 | 27.7875 | 19.5641 | 1.8842 | -27.3595 | -38.4974 | -40.2052
|  |  | ST |  |  | 71.139 | 70.2143 | 69.2889 | 68.0339 | 66.5533 | 63.8928 | 61.031 | 57.8826 | 54.4416 | 50.6851 | 41.7642 | 16.254 | -2.5561 | -14.6968 | 79.827 | 79.0717 | 78.2531 | 77.043 | 75.6819 | 72.9107 | 69.696 | 66.3198 | 62.6979 | 58.8668 | 49.8778 | 24.7415 | 2.9018 | -18.7013 | 69.8298 | 69.1718 | 68.4844 | 67.4186 | 66.2032 | 63.62 | 60.7218 | 57.6529 | 54.1426 | 50.4401 | 41.7433 | 16.1608 | -1.7269 | -12.5503
|  |  | FS |  |  | 70.1055 | 68.4448 | 66.6806 | 63.3651 | 59.5284 | 53.7023 | 47.5127 | 40.0858 | 29.7039 | 13.7629 | -22.9209 | -100.9967 | -142.3739 | -162.1912 | 79.7651 | 78.6926 | 77.5652 | 76.207 | 74.5986 | 71.5908 | 68.1012 | 64.0456 | 59.7023 | 55.0914 | 44.5114 | 14.1068 | -22.9986 | -71.1893 | 69.865 | 68.9545 | 68.056 | 66.8019 | 65.3347 | 62.5014 | 59.3274 | 55.4018 | 51.0931 | 46.5399 | 36.1508 | 6.9273 | -21.2349 | -39.5117
MINETY GSP | STRATTON (2 X 60) | STRATTON (2 X 60) | MINIMUM HEADROOM | SU 17028 88748 | NO | 13.826 | 9.7272 | 4.7146 | 1.3703 | -2.1044 | -5.8031 | -10.2091 | -15.2848 | -20.9879 | -31.7452 | -58.0707 | -119.0471 | -154.4575 | -170.8177 | 24.166 | 20.9627 | 16.5546 | 14.9061 | 12.783 | 9.6468 | 5.3662 | -0.1217 | -6.8101 | -14.8391 | -34.6617 | -81.0088 | -109.4678 | -124.463 | 10.3057 | 6.2925 | 1.0844 | -1.7298 | -4.7177 | -7.9346 | -11.8647 | -16.4398 | -24.2372 | -34.5325 | -59.699 | -118.1352 | -152.9737 | -170.1508
|  |  | CT |  |  | 15.9543 | 13.9924 | 11.7948 | 9.0572 | 6.2672 | 2.9742 | -0.8227 | -5.3873 | -11.2889 | -17.7006 | -36.5047 | -87.5885 | -122.9061 | -140.7708 | 25.6223 | 24.2706 | 22.6261 | 21.0513 | 19.3836 | 17.293 | 14.389 | 10.0585 | 4.6637 | -1.8267 | -16.8989 | -55.2229 | -82.1005 | -96.4844 | 12.4577 | 10.754 | 8.7601 | 6.4199 | 3.9747 | 1.0244 | -2.4332 | -6.632 | -12.0945 | -18.7598 | -38.1486 | -87.2637 | -121.4482 | -139.1619
|  |  | LW |  |  | 13.826 | 9.7272 | 4.7146 | 1.3703 | -2.1044 | -5.8031 | -10.2091 | -15.2848 | -20.9879 | -31.7452 | -58.0707 | -119.0471 | -154.4575 | -170.8177 | 24.166 | 20.9627 | 16.5546 | 14.9061 | 12.783 | 9.6468 | 5.3662 | -0.1217 | -6.8101 | -14.8391 | -34.6617 | -81.0088 | -109.4678 | -124.463 | 10.3057 | 6.2925 | 1.0844 | -1.7298 | -4.7177 | -7.9346 | -11.8647 | -16.4398 | -24.2372 | -34.5325 | -59.699 | -118.1352 | -152.9737 | -170.1508
|  |  | ST |  |  | 15.7089 | 13.5083 | 10.242 | 8.3831 | 6.7854 | 5.0762 | 3.0242 | 0.85577 | -1.5988 | -4.2039 | -10.3359 | -30.3073 | -47.5553 | -60.2748 | 24.8871 | 22.9697 | 19.7125 | 18.2862 | 17.0407 | 15.6754 | 13.993 | 12.277 | 10.1471 | 7.8649 | 2.4111 | -15.0091 | -32.1262 | -47.8081 | 11.9433 | 9.8077 | 6.3373 | 4.65 | 3.191 | 1.6188 | -0.27538 | -2.2142 | -4.5488 | -7.0621 | -13.2128 | -32.8792 | -50.2591 | -63.0468
|  |  | FS |  |  | 15.9543 | 13.9924 | 11.7948 | 9.0572 | 6.2672 | 2.9742 | -0.8227 | -5.3873 | -11.2889 | -17.7006 | -36.5047 | -87.5885 | -122.9061 | -140.7708 | 25.7239 | 24.5298 | 23.2747 | 21.8019 | 20.198 | 18.3117 | 15.9199 | 12.9082 | 9.4373 | 5.7421 | -2.2303 | -22.2259 | -39.912 | -58.352 | 12.8614 | 11.5296 | 10.1641 | 8.4211 | 6.5506 | 4.2764 | 1.4179 | -2.1848 | -6.3473 | -10.7426 | -20.0531 | -42.7067 | -59.3642 | -70.2297
MINETY GSP | STRATTON (2 X 90) | STRATTON (2 X 90) | MINIMUM HEADROOM | SU 17028 88748 | NO | 39.6295 | 38.9173 | 38.3867 | 37.5406 | 36.281 | 33.9313 | 31.4746 | 28.8787 | 26.1327 | 23.0756 | 17.3733 | -2.2497 | -11.3775 | -17.0902 | 36.4438 | 35.8397 | 35.3059 | 34.1194 | 32.8074 | 31.324 | 29.7174 | 27.9997 | 26.3012 | 23.2665 | 16.4641 | 2.7691 | -3.7102 | -23.0174 | 36.8854 | 35.929 | 35.0473 | 33.079 | 30.9857 | 28.6948 | 26.2707 | 23.6676 | 20.9137 | 17.7823 | 11.7075 | -7.204 | -15.7685 | -21.2827
|  |  | CT |  |  | 39.6301 | 38.9173 | 38.3867 | 37.5406 | 36.616 | 35.4817 | 34.3543 | 32.4894 | 29.256 | 25.4231 | 18.1895 | -2.2497 | -11.3775 | -17.0902 | 36.7335 | 36.1136 | 35.6433 | 34.5656 | 33.3416 | 32.0025 | 30.61 | 28.9217 | 26.7107 | 23.2665 | 16.4641 | 2.7691 | -3.7102 | -15.9297 | 37.7292 | 37.0526 | 36.5434 | 34.9778 | 33.2939 | 31.4723 | 29.6063 | 27.3781 | 24.2199 | 20.5066 | 12.1518 | -7.204 | -15.7685 | -21.2827
|  |  | LW |  |  | 39.6295 | 39.0916 | 38.6467 | 37.8644 | 36.281 | 33.9313 | 31.4746 | 28.8787 | 26.1327 | 23.0756 | 17.3733 | 4.0719 | -4.1186 | -9.7224 | 36.4438 | 35.8397 | 35.3059 | 34.1194 | 32.8074 | 31.324 | 29.7174 | 27.9997 | 26.3012 | 24.2329 | 20.2299 | 12.0593 | 7.0794 | 2.7997 | 36.8854 | 35.929 | 35.0473 | 33.079 | 30.9857 | 28.6948 | 26.2707 | 23.6676 | 20.9137 | 17.7823 | 11.7075 | -1.5011 | -9.1522 | -14.5735
|  |  | ST |  |  | 39.7822 | 39.1996 | 38.8232 | 38.0801 | 37.3551 | 36.571 | 35.8957 | 35.0208 | 34.2505 | 33.1243 | 31.2847 | 25.4568 | 15.7845 | 7.6997 | 36.8685 | 36.3482 | 35.9949 | 35.2239 | 34.4287 | 33.5936 | 32.7745 | 31.804 | 30.7792 | 29.3874 | 26.6875 | 17.1081 | 6.3695 | -6.5321 | 38.0051 | 37.5082 | 37.1996 | 36.454 | 35.6876 | 34.8961 | 34.1573 | 33.246 | 32.3614 | 31.1152 | 28.803 | 19.5567 | 10.6446 | 2.5335
|  |  | FS |  |  | 39.6301 | 38.9173 | 38.3867 | 37.5406 | 36.616 | 35.4817 | 34.3543 | 32.4894 | 29.256 | 25.4231 | 18.1895 | -2.2497 | -11.3775 | -17.0902 | 36.9202 | 36.5909 | 36.2866 | 35.7721 | 35.1987 | 34.5631 | 33.8965 | 33.142 | 32.0914 | 30.8585 | 28.1177 | 18.1058 | 1.9066 | -23.0174 | 38.0669 | 37.803 | 37.5822 | 37.0741 | 36.5139 | 35.9088 | 35.2993 | 34.6189 | 33.6966 | 32.6405 | 30.4454 | 22.5944 | 12.9815 | 3.956
MINETY GSP | SWINDON BSP | SWINDON BSP | MINIMUM HEADROOM | SU 12447 87062 | NO | 23.928 | 22.1567 | 20.4377 | 17.7382 | 14.8713 | 11.7654 | 8.3097 | 4.5481 | -0.34213 | -5.7133 | -30.4022 | -86.6936 | -124.0341 | -145.69 | 29.4543 | 28.4467 | 27.4777 | 26.1845 | 24.7864 | 23.205 | 21.1585 | 18.5864 | 14.825 | 10.3861 | -7.6147 | -47.7517 | -74.5093 | -96.1682 | 13.6452 | 12.0335 | 10.4599 | 7.9744 | 5.3365 | 2.4826 | -0.70015 | -4.1772 | -8.708 | -14.46 | -37.9246 | -91.2328 | -126.6354 | -147.3326
|  |  | CT |  |  | 25.4669 | 24.5523 | 23.607 | 21.647 | 19.5002 | 16.8643 | 13.9574 | 10.6283 | 4.8123 | -5.7133 | -30.4022 | -86.6936 | -124.0341 | -145.69 | 29.858 | 29.0019 | 28.0705 | 26.7746 | 25.2942 | 23.3453 | 21.1585 | 18.5864 | 14.825 | 10.3861 | -7.6147 | -47.7517 | -74.5093 | -90.7474 | 15.0693 | 14.2675 | 13.4193 | 11.6163 | 9.6331 | 7.1744 | 4.4443 | 1.2982 | -4.488 | -14.46 | -37.9246 | -91.2328 | -126.6354 | -147.3326
|  |  | LW |  |  | 23.928 | 22.1567 | 20.4377 | 17.7382 | 14.8713 | 11.7654 | 8.3097 | 4.5481 | -0.34213 | -5.672 | -17.9626 | -58.5131 | -81.6344 | -92.8155 | 29.4543 | 28.4467 | 27.4777 | 26.1845 | 24.7864 | 23.205 | 21.3841 | 19.3395 | 16.6384 | 13.6178 | 3.617 | -25.1181 | -42.2372 | -51.3513 | 13.6452 | 12.0335 | 10.4599 | 7.9744 | 5.3365 | 2.4826 | -0.70015 | -4.1772 | -8.708 | -13.6459 | -25.674 | -64.0062 | -86.198 | -97.3358
|  |  | ST |  |  | 26.0908 | 25.5539 | 25.0302 | 24.5669 | 24.0394 | 23.2708 | 22.3983 | 21.4367 | 20.0736 | 18.4905 | 14.9408 | -0.50966 | -14.6016 | -27.4183 | 30.1705 | 29.5266 | 28.8431 | 28.1727 | 27.432 | 26.4121 | 25.2857 | 24.0582 | 22.3986 | 20.5459 | 16.3162 | -0.086724 | -21.0501 | -50.865 | 15.6723 | 15.2403 | 14.8062 | 14.3868 | 13.9207 | 13.2292 | 12.4375 | 11.5761 | 10.3207 | 8.8489 | 5.5456 | -8.5474 | -21.7068 | -33.982
|  |  | FS |  |  | 25.4669 | 24.5523 | 23.607 | 21.647 | 19.5002 | 16.8643 | 13.9574 | 10.6283 | 4.8123 | -5.7133 | -30.4022 | -86.6936 | -124.0341 | -145.69 | 30.2687 | 29.5684 | 28.8394 | 27.9916 | 27.0417 | 25.9339 | 24.6755 | 23.2559 | 21.314 | 19.1123 | 13.9374 | -5.8718 | -39.5067 | -96.1682 | 15.8035 | 15.383 | 14.9963 | 14.4086 | 13.7727 | 13.0397 | 12.2286 | 11.3215 | 9.9351 | 8.3426 | 4.8057 | -8.4263 | -23.8075 | -37.774
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM BSP | MINIMUM HEADROOM | SU 52824 66435 | YES | 5.5424 | -0.025751 | -5.4319 | -12.288 | -21.1086 | -30.9826 | -45.5064 | -63.9815 | -84.8252 | -108.1561 | -160.9433 | -333.2861 | -416.9089 | -438.8141 | 38.0646 | 34.2667 | 30.5819 | 25.2711 | 19.1711 | 9.9276 | 0.11327 | -14.0275 | -31.2697 | -48.797 | -95.1979 | -226.2545 | -288.6091 | -304.7075 | 2.657 | -2.8183 | -8.1519 | -14.9079 | -23.7085 | -33.5791 | -48.4856 | -66.5288 | -86.8162 | -109.5679 | -160.7208 | -320.1552 | -399.9124 | -420.7568
|  |  | CT |  |  | 7.243 | 3.0209 | -1.7949 | -8.6277 | -16.4244 | -27.7246 | -40.4289 | -58.4347 | -81.1581 | -104.1885 | -160.9433 | -333.2861 | -416.9089 | -438.8141 | 38.1281 | 34.6816 | 30.6217 | 25.2711 | 19.1711 | 9.9276 | 0.11327 | -14.0275 | -31.2697 | -48.797 | -95.1979 | -226.2545 | -288.6091 | -304.7075 | 3.8894 | -0.41528 | -5.419 | -12.3181 | -20.1356 | -31.7483 | -44.0806 | -61.6936 | -83.7901 | -106.1838 | -155.1906 | -320.1552 | -399.9124 | -420.7568
|  |  | LW |  |  | 5.5424 | -0.025751 | -5.4319 | -12.288 | -21.1086 | -30.9826 | -45.5064 | -63.9815 | -84.8252 | -108.1561 | -160.6811 | -266.5444 | -309.3217 | -328.0593 | 38.0646 | 34.2667 | 30.5819 | 25.8215 | 19.4408 | 12.1496 | 0.80789 | -13.0592 | -28.5293 | -45.9639 | -86.9682 | -173.5878 | -205.4658 | -220.0188 | 2.657 | -2.8183 | -8.1519 | -14.9079 | -23.7085 | -33.5791 | -48.4856 | -66.5288 | -86.8162 | -109.5679 | -160.7208 | -256.1066 | -296.9819 | -315.017
|  |  | ST |  |  | 10.3168 | 8.5604 | 6.5612 | 3.1238 | -1.0072 | -6.406 | -12.2485 | -19.4539 | -28.2564 | -38.9896 | -68.6808 | -165.2488 | -227.5521 | -247.4334 | 40.374 | 38.8907 | 37.0952 | 34.0141 | 30.3726 | 25.529 | 20.1855 | 13.8163 | 6.5581 | -2.2703 | -26.3028 | -105.4379 | -161.3453 | -186.9076 | 6.9787 | 5.2615 | 3.2178 | -0.36276 | -4.633 | -10.2945 | -16.5711 | -24.0998 | -32.7421 | -43.3 | -72.0866 | -165.4329 | -226.6673 | -245.3371
|  |  | FS |  |  | 7.243 | 3.0209 | -1.7949 | -8.6277 | -16.4244 | -27.7246 | -40.4289 | -58.4347 | -81.1581 | -104.1885 | -160.9433 | -333.2861 | -416.9089 | -438.8141 | 40.7236 | 39.0589 | 37.1593 | 34.563 | 31.3332 | 27.252 | 22.4193 | 16.5388 | 9.8754 | 2.2468 | -17.6841 | -89.9377 | -171.3437 | -233.3781 | 7.5768 | 5.7844 | 3.7713 | 0.67846 | -3.1413 | -7.9298 | -13.581 | -20.4518 | -28.3834 | -37.4118 | -60.8574 | -145.1269 | -232.5659 | -282.5894
MINETY GSP | TOOTHILL BSP | TOOTHILL BSP | MINIMUM HEADROOM | SU 13191 83945 | NO | 38.0585 | 31.8304 | 21.3138 | 17.934 | 11.9482 | 93.2997 | 86.6157 | 79.626 | 72.49 | 65.0709 | 49.3484 | 12.8655 | -9.6212 | -23.5464 | 40.07 | 33.7228 | 22.1435 | 20.2743 | 15.5241 | 98.0697 | 93.2564 | 88.4773 | 83.7006 | 78.774 | 66.7163 | 35.9043 | 18.9208 | 7.8238 | 31.9668 | 25.0185 | 12.7937 | 9.9032 | 3.9251 | 85.0881 | 78.5241 | 71.7405 | 64.799 | 57.551 | 42.1956 | 6.7222 | -15.0647 | -28.7843
|  |  | CT |  |  | 38.8483 | 33.1913 | 27.1843 | 24.3665 | 21.1611 | 102.9439 | 93.0808 | 86.6067 | 79.192 | 71.5147 | 54.0635 | 12.8655 | -9.6212 | -23.5464 | 40.2521 | 34.0345 | 27.5724 | 25.8193 | 23.8536 | 106.3917 | 96.8432 | 92.1303 | 87.0343 | 81.7402 | 66.7163 | 35.9043 | 18.9208 | 7.8238 | 32.5659 | 26.0683 | 19.2632 | 16.8061 | 14.022 | 95.4768 | 84.7206 | 78.4638 | 71.3645 | 64.0385 | 46.3496 | 6.7222 | -15.0647 | -28.7843
|  |  | LW |  |  | 38.0585 | 31.8304 | 21.3138 | 17.934 | 11.9482 | 93.2997 | 86.6157 | 79.626 | 72.49 | 65.0709 | 49.3484 | 21.3194 | 0.062818 | -10.4456 | 40.07 | 33.7228 | 22.1435 | 20.2743 | 15.5241 | 98.0697 | 93.2564 | 88.4773 | 83.7006 | 78.774 | 67.8177 | 41.1586 | 23.9114 | 14.3069 | 31.9668 | 25.0185 | 12.7937 | 9.9032 | 3.9251 | 85.0881 | 78.5241 | 71.7405 | 64.799 | 57.551 | 42.1956 | 13.976 | -7.102 | -18.125
|  |  | ST |  |  | 39.3881 | 34.1452 | 28.615 | 26.9707 | 21.1287 | 104.9834 | 99.4701 | 95.9888 | 92.5457 | 88.8714 | 80.0143 | 55.7434 | 37.7877 | 27.6464 | 40.5586 | 34.6084 | 28.4608 | 27.2187 | 20.8227 | 104.5265 | 98.8875 | 95.9003 | 92.9323 | 89.6894 | 82.0466 | 60.7027 | 42.5016 | 28.4648 | 33.0502 | 26.9494 | 20.6109 | 19.1226 | 12.4269 | 95.7447 | 89.6571 | 86.1148 | 82.5326 | 78.7226 | 69.9818 | 45.8069 | 27.6664 | 17.9063
|  |  | FS |  |  | 38.8483 | 33.1913 | 27.1843 | 24.3665 | 21.1611 | 102.9439 | 93.0808 | 86.6067 | 79.192 | 71.5147 | 54.0635 | 12.8655 | -9.6212 | -23.5464 | 40.5449 | 34.6263 | 28.5598 | 27.4098 | 26.105 | 109.9008 | 106.9055 | 103.7519 | 100.4126 | 96.9661 | 89.2165 | 68.0818 | 44.8389 | 21.5492 | 33.0097 | 26.9567 | 20.7342 | 19.3154 | 17.6854 | 101.0838 | 97.6065 | 93.8607 | 90.1047 | 86.2758 | 77.6852 | 54.9385 | 33.1794 | 19.2319
IVER 132KV | UPTON BSP | UPTON BSP | MINIMUM HEADROOM | TQ 00838 79445 | YES | 24.0737 | 23.4972 | 22.8135 | 20.7538 | 18.3594 | 14.5661 | 9.9709 | 5.0367 | -0.68435 | -9.0805 | -28.9198 | -70.7117 | -88.4191 | -95.7174 | 28.891 | 28.6538 | 28.3672 | 27.0045 | 25.3911 | 21.7546 | 16.3242 | 10.452 | 4.5692 | -2.2353 | -18.0788 | -51.6179 | -65.5659 | -71.2912 | 22.2157 | 21.7121 | 21.1012 | 19.0358 | 16.6017 | 12.4528 | 7.444 | 0.80487 | -6.3383 | -14.6303 | -34.0456 | -75.0349 | -92.2209 | -99.2518
|  |  | CT |  |  | 24.5873 | 24.3152 | 23.9507 | 22.8256 | 21.4918 | 19.0731 | 15.9571 | 12.5656 | 8.5698 | 4.096 | -5.7081 | -25.7303 | -33.2792 | -37.3028 | 28.9626 | 28.8082 | 28.6117 | 28.1534 | 27.5609 | 25.2682 | 22.2632 | 19.2009 | 15.9043 | 12.1735 | 4.0771 | -12.9721 | -22.1661 | -32.4782 | 22.6258 | 22.3706 | 22.0205 | 21.0016 | 19.7336 | 17.1848 | 13.8579 | 10.3584 | 6.4056 | 1.9276 | -7.822 | -27.5117 | -34.6828 | -38.4646
|  |  | LW |  |  | 24.0737 | 23.4972 | 22.8135 | 20.7538 | 18.3594 | 14.5661 | 9.9709 | 5.0367 | -0.68435 | -9.0805 | -28.9198 | -70.7117 | -88.4191 | -95.7174 | 28.891 | 28.6538 | 28.3672 | 27.0045 | 25.3911 | 21.7546 | 16.3242 | 10.452 | 4.5692 | -2.2353 | -18.0788 | -51.6179 | -65.5659 | -71.2912 | 22.2157 | 21.7121 | 21.1012 | 19.0358 | 16.6017 | 12.4528 | 7.444 | 0.80487 | -6.3383 | -14.6303 | -34.0456 | -75.0349 | -92.2209 | -99.2518
|  |  | ST |  |  | 24.8384 | 24.7555 | 24.6192 | 23.6037 | 22.8041 | 21.2674 | 19.2145 | 17.3641 | 15.5308 | 13.5448 | 8.4445 | -9.8584 | -20.3037 | -22.7327 | 29.0576 | 28.9867 | 28.8955 | 27.7702 | 26.9878 | 25.3987 | 23.2184 | 21.1221 | 19.1097 | 16.9938 | 11.8639 | -5.5816 | -17.513 | -25.9907 | 22.832 | 22.7423 | 22.5999 | 21.4109 | 20.4787 | 18.6546 | 16.2249 | 14.125 | 12.0891 | 9.8912 | 4.3616 | -14.6996 | -25.1055 | -27.0069
|  |  | FS |  |  | 24.5873 | 24.3152 | 23.9507 | 22.8256 | 21.4918 | 19.0731 | 15.9571 | 12.5656 | 8.5698 | 4.096 | -5.7081 | -25.7303 | -33.2792 | -37.3028 | 29.0398 | 28.9497 | 28.8407 | 28.476 | 28.1045 | 26.5472 | 24.6394 | 22.5458 | 20.4423 | 18.3255 | 13.5523 | -1.6396 | -21.4125 | -43.7543 | 22.6954 | 22.4927 | 22.2492 | 21.6609 | 21.0088 | 19.4026 | 17.523 | 15.4133 | 13.3248 | 11.2373 | 6.5325 | -8.2607 | -24.1892 | -33.4596
IVER 66KV | UXBRIDGE | UXBRIDGE | MINIMUM HEADROOM | TQ 04984 83484 | YES | 14.5684 | 14.2227 | 13.8479 | 13.2508 | 12.1056 | 9.0422 | 5.0722 | 0.76654 | -3.972 | -9.2988 | -20.9415 | -43.8281 | -51.9459 | -54.0929 | 20.3618 | 20.0052 | 19.6395 | 19.0831 | 18.2476 | 15.3476 | 11.3669 | 7.2406 | 3.0672 | -1.3349 | -10.68 | -28.8766 | -35.1623 | -37.1416 | 12.7645 | 12.2607 | 11.7508 | 10.6905 | 9.4272 | 6.1276 | 2.2192 | -2.0126 | -6.6543 | -11.9706 | -23.4222 | -45.8914 | -53.8143 | -55.9098
|  |  | CT |  |  | 14.6412 | 14.2832 | 13.9106 | 13.4845 | 12.9524 | 10.7947 | 8.3829 | 5.8763 | 3.3434 | 0.76852 | -4.7715 | -18.224 | -26.1198 | -29.1874 | 20.3962 | 20.0052 | 19.6395 | 19.1893 | 18.6492 | 16.1132 | 13.345 | 11.07 | 8.977 | 6.6749 | 2.0419 | -8.0503 | -13.7273 | -23.2998 | 13.0436 | 12.6736 | 12.2993 | 11.7594 | 10.8963 | 8.0783 | 5.0507 | 2.5293 | -0.033751 | -2.3754 | -7.7034 | -20.8078 | -28.3584 | -31.2555
|  |  | LW |  |  | 14.5684 | 14.2227 | 13.8479 | 13.2508 | 12.1056 | 9.0422 | 5.0722 | 0.76654 | -3.972 | -9.2988 | -20.9415 | -43.8281 | -51.9459 | -54.0929 | 20.3618 | 20.0365 | 19.6998 | 19.0831 | 18.2476 | 15.3476 | 11.3669 | 7.2406 | 3.0672 | -1.3349 | -10.68 | -28.8766 | -35.1623 | -36.8224 | 12.7645 | 12.2607 | 11.7508 | 10.6905 | 9.4272 | 6.1276 | 2.2192 | -2.0126 | -6.6543 | -11.9706 | -23.4222 | -45.8914 | -53.8143 | -55.9098
|  |  | ST |  |  | 14.7574 | 14.4863 | 14.201 | 13.753 | 13.2536 | 11.3632 | 9.3895 | 7.7779 | 6.3916 | 5.1322 | 2.2783 | -4.3249 | -6.8629 | -8.5528 | 20.4945 | 20.1767 | 19.8847 | 19.3743 | 18.8409 | 16.5777 | 14.1646 | 12.2149 | 10.5708 | 9.1072 | 6.5968 | 1.1469 | -5.8212 | -16.7756 | 13.2148 | 12.9725 | 12.7264 | 12.2786 | 11.797 | 9.6122 | 7.2082 | 5.2107 | 3.4808 | 1.8015 | -1.2865 | -7.8965 | -10.4889 | -11.8623
|  |  | FS |  |  | 14.6412 | 14.2832 | 13.9106 | 13.4845 | 12.9524 | 10.7947 | 8.3829 | 5.8763 | 3.3434 | 0.76852 | -4.7715 | -18.224 | -26.1198 | -29.1874 | 20.4996 | 20.3309 | 20.1381 | 19.8439 | 19.5021 | 17.6458 | 15.551 | 13.5506 | 11.8815 | 10.3707 | 6.6934 | -2.4842 | -15.3297 | -37.1416 | 13.2341 | 13.0981 | 12.9364 | 12.6928 | 12.3604 | 10.4826 | 8.3417 | 6.2292 | 4.3272 | 2.6444 | -0.43798 | -5.7922 | -9.8467 | -13.2351
NURSLING GSP | VELMORE BSP | VELMORE BSP | MINIMUM HEADROOM | SU 42855 19215 | YES | -7.4658 | -12.7116 | 69.4214 | 62.9364 | 55.4302 | 47.547 | 36.2133 | 23.0071 | 8.0193 | -8.5533 | -44.9914 | -110.8325 | -159.1791 | -178.741 | 14.1855 | 10.6745 | 93.9808 | 90.0221 | 85.1494 | 79.9983 | 72.0227 | 62.5607 | 51.7465 | 39.2639 | 13.6439 | -41.982 | -83.0683 | -149.659 | -9.9448 | -14.6438 | 67.4979 | 61.5767 | 54.4612 | 47.0539 | 36.1843 | 23.4327 | 9.0022 | -7.0167 | -42.2813 | -105.5414 | -153.4278 | -172.9088
|  |  | CT |  |  | -5.8559 | -9.7455 | 73.4149 | 67.9077 | 61.7942 | 53.5115 | 44.2415 | 31.703 | 15.1067 | -1.5733 | -33.9841 | -107.0687 | -140.0254 | -155.2503 | 14.4987 | 11.4197 | 94.8995 | 91.1252 | 86.8542 | 80.7403 | 73.7098 | 64.0163 | 51.7465 | 39.2639 | 14.8422 | -41.6688 | -74.0125 | -104.0979 | -8.568 | -12.0746 | 70.8351 | 65.7589 | 60.0899 | 52.2491 | 43.3995 | 31.285 | 15.3676 | -0.66589 | -31.7912 | -101.7262 | -132.7853 | -147.0822
|  |  | LW |  |  | -7.4658 | -12.7116 | 69.4214 | 62.9364 | 55.4302 | 47.547 | 36.2133 | 23.0071 | 8.0193 | -8.5533 | -44.9914 | -110.8325 | -159.1791 | -178.741 | 14.1855 | 10.6745 | 93.9808 | 90.0221 | 85.1494 | 79.9983 | 72.0227 | 62.5607 | 51.9609 | 40.0559 | 13.6439 | -41.982 | -83.0683 | -99.3226 | -9.9448 | -14.6438 | 67.4979 | 61.5767 | 54.4612 | 47.0539 | 36.1843 | 23.4327 | 9.0022 | -7.0167 | -42.2813 | -105.5414 | -153.4278 | -172.9088
|  |  | ST |  |  | -4.1729 | -6.592 | 78.4387 | 76.0187 | 73.0042 | 69.4093 | 64.7686 | 59.4245 | 53.0775 | 45.4647 | 25.8054 | -38.6757 | -84.8275 | -105.7419 | 15.6348 | 13.6321 | 98.5128 | 96.3887 | 93.8607 | 90.6968 | 86.5351 | 81.7718 | 76.0463 | 69.2089 | 51.5854 | -5.5594 | -51.3766 | -84.0006 | -6.9568 | -9.0289 | 75.7994 | 73.4637 | 70.6446 | 67.2279 | 62.7293 | 57.5297 | 51.3242 | 43.8555 | 24.4613 | -39.2938 | -85.3364 | -104.3685
|  |  | FS |  |  | -5.8559 | -9.7455 | 73.4149 | 67.9077 | 61.7942 | 53.5115 | 44.2415 | 31.703 | 15.1067 | -1.5733 | -33.9841 | -107.0687 | -140.0254 | -155.2503 | 16.0106 | 14.0102 | 98.4538 | 96.1754 | 93.5056 | 90.3211 | 86.3035 | 81.3953 | 75.4982 | 64.4909 | 36.0414 | -24.8658 | -78.5982 | -149.659 | -6.5485 | -8.5165 | 75.9856 | 73.5711 | 70.6376 | 67.0811 | 62.6913 | 57.3593 | 50.9665 | 38.8236 | 3.9698 | -71.844 | -116.8929 | -147.3396
NORTH HYDE GSP | VICARAGE FARM ROAD | VICARAGE FARM ROAD | MINIMUM HEADROOM | TQ 12358 76435 | YES | 13.0931 | 12.3234 | 11.335 | 10.0519 | 8.7721 | 7.4662 | 6.0627 | 4.7482 | 3.408 | 2.028 | -0.83549 | -6.2333 | -8.5379 | -10.4146 | 16.1014 | 15.7403 | 15.3159 | 14.8117 | 14.3113 | 13.7889 | 13.213 | 12.6739 | 11.9435 | 11.0399 | 8.8378 | 2.8459 | -8.1228 | -30.6895 | 11.4366 | 10.7881 | 9.998 | 8.8998 | 7.7975 | 6.667 | 5.4428 | 4.2802 | 3.1083 | 1.8966 | -0.62728 | -5.4111 | -7.3773 | -8.8569
|  |  | CT |  |  | 13.8993 | 13.5557 | 12.9245 | 11.9855 | 11.04 | 9.9688 | 8.7597 | 7.5578 | 6.002 | 4.4132 | 1.3855 | -4.9313 | -8.5238 | -10.4146 | 16.3641 | 16.1259 | 15.7457 | 15.2878 | 14.8029 | 14.2201 | 13.5176 | 12.7927 | 11.9435 | 11.0399 | 8.8378 | 2.8459 | -4.4499 | -15.7036 | 12.1731 | 11.9065 | 11.4129 | 10.6363 | 9.8363 | 8.9191 | 7.87 | 6.8162 | 5.4531 | 4.0601 | 1.4112 | -4.1872 | -7.2771 | -8.8569
|  |  | LW |  |  | 13.0931 | 12.3234 | 11.335 | 10.0519 | 8.7721 | 7.4662 | 6.0627 | 4.7482 | 3.408 | 2.028 | -0.83549 | -6.2333 | -8.5379 | -9.5087 | 16.1014 | 15.7403 | 15.3159 | 14.8117 | 14.3113 | 13.7889 | 13.213 | 12.6739 | 12.1538 | 11.6003 | 10.4045 | 7.8794 | 6.761 | 6.2815 | 11.4366 | 10.7881 | 9.998 | 8.8998 | 7.7975 | 6.667 | 5.4428 | 4.2802 | 3.1083 | 1.8966 | -0.62728 | -5.4111 | -7.3773 | -8.1394
|  |  | ST |  |  | 14.0084 | 13.7808 | 13.2579 | 12.8885 | 12.5393 | 12.1083 | 11.5664 | 11.0542 | 10.5389 | 9.9519 | 8.6641 | 4.1485 | 0.14384 | -3.0665 | 16.3594 | 16.1539 | 15.8028 | 15.4567 | 15.1117 | 14.691 | 14.1534 | 13.6188 | 13.0727 | 12.423 | 10.8066 | 4.9632 | -3.0997 | -14.8154 | 12.2528 | 12.0841 | 11.6884 | 11.3771 | 11.0878 | 10.7166 | 10.2349 | 9.7752 | 9.3166 | 8.7894 | 7.6103 | 3.3553 | -0.30003 | -3.0072
|  |  | FS |  |  | 13.8993 | 13.5557 | 12.9245 | 11.9855 | 11.04 | 9.9688 | 8.7597 | 7.5578 | 6.002 | 4.4132 | 1.3855 | -4.9313 | -8.5238 | -10.4146 | 16.4923 | 16.2223 | 15.8738 | 15.534 | 15.1571 | 14.752 | 14.2817 | 13.8216 | 13.2735 | 12.5798 | 10.9325 | 4.3495 | -8.1228 | -30.6895 | 12.4562 | 12.2508 | 11.9406 | 11.6548 | 11.353 | 11.0398 | 10.6909 | 10.3953 | 10.0117 | 9.6039 | 8.7877 | 6.3965 | 2.8523 | -0.84515
MANNINGTON GSP | WAREHAM | WAREHAM | MINIMUM HEADROOM | SY 91548 88451 | YES | 4.3399 | 3.1052 | 17.1657 | 15.2041 | 12.5377 | 9.5922 | 5.5058 | 0.60758 | -5.0252 | -11.4948 | -28.9159 | -64.3257 | -76.9974 | -84.5482 | 5.9184 | 5.1967 | 18.5123 | 17.3563 | 15.6682 | 13.4148 | 10.54 | 6.5637 | 1.3551 | -4.8042 | -18.6838 | -45.1033 | -54.2491 | -60.1737 | 1.9038 | 0.74327 | 13.7727 | 11.9587 | 9.4955 | 6.7663 | 2.9092 | -1.7469 | -7.1553 | -13.3677 | -29.6195 | -63.5522 | -75.7682 | -83.2424
|  |  | CT |  |  | 4.8514 | 3.854 | 17.9764 | 16.1834 | 13.8145 | 10.7543 | 7.2312 | 2.4917 | -3.7323 | -10.5917 | -28.9159 | -64.3257 | -76.9974 | -84.5482 | 5.9184 | 5.1967 | 18.5123 | 17.3563 | 15.6682 | 13.4148 | 10.54 | 6.5637 | 1.3551 | -4.8042 | -18.6838 | -45.1033 | -54.2491 | -60.1737 | 2.3386 | 1.3843 | 14.4428 | 12.7585 | 10.5486 | 7.6596 | 4.3083 | -0.23766 | -6.1517 | -12.6685 | -29.6195 | -63.5522 | -75.7682 | -83.2424
|  |  | LW |  |  | 4.3399 | 3.1052 | 17.1657 | 15.2041 | 12.5377 | 9.5922 | 5.5058 | 0.60758 | -5.0252 | -11.4948 | -26.3477 | -52.8149 | -63.105 | -69.4838 | 5.9225 | 5.3229 | 18.9288 | 17.9978 | 16.6419 | 15.0166 | 12.7758 | 9.9222 | 6.2051 | 1.3596 | -9.5946 | -28.5712 | -40.4482 | -49.7137 | 1.9038 | 0.74327 | 13.7727 | 11.9587 | 9.4955 | 6.7663 | 2.9092 | -1.7469 | -7.1553 | -13.3677 | -27.8273 | -53.1756 | -62.9308 | -69.256
|  |  | ST |  |  | 5.4558 | 5.0003 | 19.7466 | 18.9539 | 17.7589 | 16.4048 | 14.8089 | 12.8758 | 10.4724 | 7.4834 | -0.45037 | -27.2818 | -45.3326 | -52.5813 | 6.3559 | 6.0371 | 19.8988 | 19.4394 | 18.7925 | 18.1339 | 17.4213 | 16.623 | 15.3996 | 12.8925 | 6.2884 | -15.7895 | -31.7126 | -39.5653 | 2.9145 | 2.4839 | 16.1486 | 15.3782 | 14.2554 | 12.9798 | 11.4482 | 9.5978 | 7.3439 | 4.4716 | -3.4121 | -30.0217 | -48.037 | -55.2532
|  |  | FS |  |  | 4.8514 | 3.854 | 17.9764 | 16.1834 | 13.8145 | 10.7543 | 7.2312 | 2.4917 | -3.7323 | -10.5917 | -28.9159 | -64.3257 | -76.9974 | -84.5482 | 6.3375 | 6.1611 | 20.2614 | 19.9142 | 19.4346 | 18.9039 | 18.2959 | 17.5783 | 16.5709 | 14.4762 | 9.0343 | -10.5267 | -33.2814 | -50.6659 | 2.8498 | 2.4918 | 16.3649 | 15.6596 | 14.6957 | 13.5857 | 12.2019 | 10.5458 | 8.5549 | 6.264 | -0.15449 | -23.2871 | -48.6848 | -63.8921
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON | MINIMUM HEADROOM | SU 24302 59215 | YES | 26.0089 | 24.9143 | 23.7839 | 22.3703 | 20.7146 | 18.8145 | 16.316 | 13.2391 | 9.5307 | 5.2765 | -4.7845 | -23.1382 | -32.0556 | -37.0079 | 33.2536 | 32.6921 | 32.1012 | 31.3161 | 30.3595 | 29.2164 | 27.6505 | 25.6647 | 22.822 | 19.5398 | 12.2001 | -2.8646 | -10.2219 | -19.2508 | 28.215 | 27.2408 | 26.231 | 24.9643 | 23.4744 | 21.7618 | 19.5214 | 16.6005 | 13.0508 | 8.946 | -0.8133 | -18.5741 | -26.8813 | -31.5126
|  |  | CT |  |  | 26.5845 | 25.8362 | 24.9977 | 23.716 | 22.2413 | 20.3927 | 18.0851 | 15.0826 | 11.0685 | 6.6158 | -3.1941 | -23.1382 | -32.0556 | -37.0079 | 33.4092 | 32.927 | 32.3653 | 31.5648 | 30.6086 | 29.3617 | 27.7742 | 25.692 | 22.822 | 19.5398 | 12.2001 | -2.8646 | -10.2219 | -16.8658 | 28.7524 | 28.0948 | 27.352 | 26.2083 | 24.8821 | 23.2175 | 21.0995 | 18.216 | 14.3798 | 10.084 | 0.59103 | -18.5741 | -26.8813 | -31.5126
|  |  | LW |  |  | 26.0089 | 24.9143 | 23.7839 | 22.3703 | 20.7146 | 18.8145 | 16.316 | 13.2391 | 9.5307 | 5.2765 | -4.7845 | -22.7099 | -29.6175 | -32.944 | 33.2536 | 32.6921 | 32.1012 | 31.3161 | 30.3595 | 29.2164 | 27.6505 | 25.6647 | 23.0973 | 20.0698 | 12.7618 | 0.10529 | -4.4318 | -6.7895 | 28.215 | 27.2408 | 26.231 | 24.9643 | 23.4744 | 21.7618 | 19.5214 | 16.6005 | 13.0508 | 8.946 | -0.8133 | -18.0631 | -24.5774 | -27.7539
|  |  | ST |  |  | 27.0297 | 26.5702 | 26.0908 | 25.3037 | 24.4647 | 23.4703 | 22.2104 | 20.6677 | 18.7767 | 16.5522 | 10.6477 | -9.375 | -21.2232 | -24.8847 | 33.6267 | 33.3059 | 32.9517 | 32.3649 | 31.7398 | 30.9969 | 30.037 | 28.8958 | 27.4938 | 25.6857 | 20.8419 | 4.2882 | -6.4245 | -11.7194 | 29.1802 | 28.796 | 28.391 | 27.6852 | 26.9402 | 26.0573 | 24.8969 | 23.4105 | 21.5805 | 19.4093 | 13.5039 | -6.5718 | -18.242 | -21.2939
|  |  | FS |  |  | 26.5845 | 25.8362 | 24.9977 | 23.716 | 22.2413 | 20.3927 | 18.0851 | 15.0826 | 11.0685 | 6.6158 | -3.1941 | -23.1382 | -32.0556 | -37.0079 | 33.6453 | 33.3487 | 33.0175 | 32.5354 | 32.005 | 31.3925 | 30.6524 | 29.7648 | 28.7299 | 27.5474 | 24.2238 | 10.827 | -5.5926 | -19.2508 | 29.2367 | 28.9237 | 28.584 | 27.976 | 27.3254 | 26.5913 | 25.7235 | 24.651 | 23.3119 | 21.7935 | 17.8664 | 2.233 | -15.4717 | -26.0246
NURSLING GSP | WINCHESTER | WINCHESTER | MINIMUM HEADROOM | SU 44965 26671 | YES | 7.5567 | 5.9638 | 4.0935 | 1.3161 | -1.7322 | -5.0836 | -8.721 | -12.5334 | -16.9077 | -21.685 | -39.431 | -76.4471 | -92.593 | -105.5916 | 30.0248 | 29.2133 | 28.1432 | 26.4525 | 24.6179 | 21.503 | 17.457 | 12.1691 | 5.5437 | -2.6647 | -25.5889 | -76.8194 | -98.2314 | -109.1112 | 12.6246 | 11.1899 | 9.4693 | 6.8456 | 3.9778 | 0.82857 | -2.4957 | -5.994 | -14.6208 | -25.303 | -52.6583 | -114.1496 | -141.4439 | -155.6361
|  |  | CT |  |  | 8.6853 | 7.6982 | 6.2206 | 3.876 | 1.4379 | -1.387 | -4.2992 | -7.5878 | -12.6471 | -20.8473 | -39.431 | -76.4471 | -92.5745 | -101.1406 | 30.1508 | 29.402 | 28.1432 | 26.4525 | 24.7012 | 22.4513 | 19.8168 | 16.4548 | 12.2785 | 7.2079 | -5.7711 | -32.4211 | -43.4154 | -55.5905 | 13.7253 | 12.8512 | 11.4586 | 9.2437 | 6.9275 | 4.2925 | 1.5813 | -1.4852 | -7.4258 | -14.4432 | -30.4259 | -64.7837 | -80.2448 | -88.7645
|  |  | LW |  |  | 7.5567 | 5.9638 | 4.0935 | 1.3161 | -1.7322 | -5.0836 | -8.721 | -12.5334 | -16.9077 | -21.685 | -35.0668 | -69.2745 | -92.593 | -105.5916 | 30.0248 | 29.2133 | 28.1749 | 26.5952 | 24.8403 | 22.8718 | 20.4651 | 17.4588 | 14.0071 | 9.9395 | -1.0096 | -25.6996 | -43.8262 | -55.434 | 12.6246 | 11.1899 | 9.4693 | 6.8456 | 3.9778 | 0.82857 | -2.4957 | -5.9427 | -9.935 | -14.2551 | -25.3999 | -57.3231 | -80.184 | -93.694
|  |  | ST |  |  | 9.3288 | 8.7087 | 7.6124 | 5.8436 | 4.2798 | 2.6408 | 0.96445 | -0.59733 | -2.4975 | -4.6085 | -9.7698 | -26.7591 | -41.4858 | -53.9385 | 30.5378 | 29.967 | 28.9336 | 27.1693 | 25.6503 | 24.0724 | 22.36 | 20.7978 | 18.8591 | 16.7379 | 11.512 | -5.8542 | -24.7215 | -47.1618 | 14.3925 | 13.893 | 12.8918 | 11.1537 | 9.69 | 8.2317 | 6.7823 | 5.553 | 3.9726 | 2.2864 | -2.6097 | -19.2605 | -33.7958 | -45.8473
|  |  | FS |  |  | 8.6853 | 7.6982 | 6.2206 | 3.876 | 1.4379 | -1.387 | -4.2992 | -7.5878 | -12.6471 | -20.8473 | -39.431 | -76.4471 | -92.5745 | -101.1406 | 30.3229 | 29.5132 | 28.4534 | 26.9558 | 24.6179 | 21.503 | 17.457 | 12.1691 | 5.5437 | -2.6647 | -25.5889 | -76.8194 | -98.2314 | -109.1112 | 14.2282 | 13.6242 | 12.749 | 11.2746 | 9.5658 | 6.0241 | 0.82851 | -5.994 | -14.6208 | -25.303 | -52.6583 | -114.1496 | -141.4439 | -155.6361
MANNINGTON GSP | WINFRITH HEATH | WINFRITH HEATH | MINIMUM HEADROOM | SY 80748 86538 | YES | 17.3721 | 16.7667 | 15.9609 | 15.0446 | 13.7577 | 12.2426 | 10.7992 | 9.4224 | 7.9317 | 6.2489 | 1.8881 | -13.5543 | -25.7496 | -29.9591 | 15.3218 | 14.6056 | 13.6398 | 12.7257 | 11.6387 | 10.5852 | 9.9145 | 9.2179 | 8.5865 | 8.0577 | 6.7425 | -0.20159 | -9.8555 | -13.4364 | 15.6144 | 15.0059 | 14.1502 | 13.3045 | 12.2244 | 11.1208 | 9.9931 | 9.0659 | 8.1307 | 7.1886 | 5.2334 | -7.1321 | -18.9376 | -23.1627
|  |  | CT |  |  | 17.5802 | 16.8242 | 15.9609 | 15.1286 | 14.1022 | 13.079 | 12.5113 | 12.0237 | 11.4756 | 10.8913 | 9.2435 | 6.4469 | 4.9618 | 4.0885 | 15.3679 | 14.6056 | 13.6398 | 12.7508 | 11.6794 | 10.6267 | 10.1121 | 9.8026 | 9.4918 | 9.2155 | 8.6564 | 7.6526 | 7.017 | 6.3976 | 15.7419 | 15.0059 | 14.1502 | 13.3045 | 12.2244 | 11.1208 | 10.4704 | 9.9103 | 9.236 | 8.4717 | 7.0147 | 4.5264 | 3.1345 | 2.2601
|  |  | LW |  |  | 17.3721 | 16.7667 | 16.0114 | 15.0446 | 13.7577 | 12.2426 | 10.7992 | 9.4224 | 7.9317 | 6.2489 | 1.8881 | -13.5543 | -25.7496 | -29.9591 | 15.3218 | 14.8495 | 14.1788 | 13.3329 | 12.2331 | 10.9615 | 9.9145 | 9.2179 | 8.5865 | 8.0577 | 6.7425 | -0.20159 | -9.8555 | -13.4364 | 15.6144 | 15.0786 | 14.4218 | 13.5828 | 12.4472 | 11.13 | 9.9931 | 9.0659 | 8.1307 | 7.1886 | 5.2334 | -7.1321 | -18.9376 | -23.1627
|  |  | ST |  |  | 17.6206 | 16.8906 | 16.0355 | 15.1894 | 14.1893 | 13.2302 | 12.7417 | 12.4086 | 12.0647 | 11.7638 | 11.1008 | 9.3311 | 7.7511 | 6.5257 | 15.3782 | 14.6233 | 13.6643 | 12.7257 | 11.6387 | 10.5852 | 10.0673 | 9.7869 | 9.4859 | 9.2828 | 8.8157 | 7.7964 | 6.8533 | 5.9787 | 15.7747 | 15.0584 | 14.2184 | 13.3735 | 12.3565 | 11.3519 | 10.8163 | 10.4423 | 10.0303 | 9.6445 | 8.8299 | 7.0235 | 5.4966 | 4.1969
|  |  | FS |  |  | 17.5802 | 16.8242 | 15.9609 | 15.1286 | 14.1022 | 13.079 | 12.5113 | 12.0237 | 11.4756 | 10.8913 | 9.2435 | 6.4469 | 4.9618 | 4.0885 | 15.3736 | 15.0845 | 14.6574 | 14.1145 | 13.4661 | 12.7776 | 12.2368 | 11.7763 | 11.3204 | 10.8875 | 9.9754 | 7.9336 | 7.0923 | 6.4634 | 15.7725 | 15.4644 | 15.0554 | 14.5226 | 13.8666 | 13.1443 | 12.5446 | 11.9718 | 11.3441 | 10.6937 | 9.3186 | 5.7709 | 3.7454 | 2.5793
COWLEY GSP | WITNEY BSP | WITNEY BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | 3.0502 | 0.63504 | -1.8763 | -5.2364 | -9.2406 | -13.4524 | -18.9871 | -25.5047 | -33.1378 | -41.3839 | -71.175 | -130.8272 | -156.3486 | -169.0425 | 27.4412 | 26.6328 | 25.2762 | 23.3806 | 21.1198 | 18.6628 | 15.3215 | 11.2924 | 6.4239 | -1.0728 | -24.3033 | -69.0025 | -88.2067 | -98.4597 | 10.5504 | 8.3965 | 6.1654 | 3.1252 | -0.48443 | -4.3295 | -9.399 | -15.5539 | -22.7933 | -31.0322 | -60.4749 | -117.398 | -141.922 | -154.4408
|  |  | CT |  |  | 4.2916 | 2.7499 | 0.92945 | -1.9185 | -5.0574 | -8.8501 | -13.1406 | -18.6723 | -26.1187 | -33.6541 | -48.2078 | -82.0689 | -100.2271 | -109.3708 | 27.6002 | 27.1644 | 26.2347 | 24.4621 | 22.5669 | 20.2015 | 17.4451 | 13.8795 | 9.149 | 4.2575 | -5.7825 | -30.6217 | -45.6702 | -58.8992 | 11.717 | 10.3373 | 8.7031 | 6.1389 | 3.3127 | -0.19627 | -4.2067 | -9.4373 | -16.4606 | -23.6289 | -37.5346 | -69.6646 | -86.4687 | -94.8779
|  |  | LW |  |  | 3.0502 | 0.63504 | -1.8763 | -5.2364 | -9.2406 | -13.4524 | -18.9871 | -25.5047 | -33.1378 | -41.3839 | -71.175 | -130.8272 | -156.3486 | -169.0425 | 27.4412 | 26.6328 | 25.2762 | 23.3806 | 21.1198 | 18.6628 | 15.3215 | 11.2924 | 6.4239 | -1.0728 | -24.3033 | -69.0025 | -88.2067 | -98.4597 | 10.5504 | 8.3965 | 6.1654 | 3.1252 | -0.48443 | -4.3295 | -9.399 | -15.5539 | -22.7933 | -31.0322 | -60.4749 | -117.398 | -141.922 | -154.4408
|  |  | ST |  |  | 5.0405 | 4.066 | 2.8837 | 0.98596 | -1.035 | -3.2029 | -5.8436 | -8.9098 | -12.5551 | -16.5635 | -26.0599 | -57.4181 | -79.8651 | -91.61 | 27.8225 | 27.5897 | 27.2993 | 25.942 | 24.5698 | 23.0743 | 21.2113 | 19.1228 | 16.4876 | 13.6749 | 6.359 | -19.8088 | -40.4035 | -55.1511 | 12.4095 | 11.5681 | 10.5416 | 8.7854 | 6.9474 | 4.9313 | 2.4224 | -0.48317 | -3.9929 | -7.8809 | -17.2273 | -47.7263 | -69.4767 | -80.5466
|  |  | FS |  |  | 4.2916 | 2.7499 | 0.92945 | -1.9185 | -5.0574 | -8.8501 | -13.1406 | -18.6723 | -26.1187 | -33.6541 | -48.2078 | -82.0689 | -100.2271 | -109.3708 | 27.8028 | 27.4667 | 27.0796 | 26.0715 | 24.7106 | 23.2125 | 21.3668 | 19.198 | 16.5607 | 13.6358 | 6.6382 | -19.8859 | -48.5159 | -74.5367 | 12.5095 | 11.6429 | 10.6364 | 9.1218 | 7.3332 | 5.3673 | 2.9154 | 0.01173 | -3.4814 | -7.3383 | -16.6074 | -46.8957 | -75.5601 | -92.8178
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM BSP | MINIMUM HEADROOM | SU 79589 67665 | YES | 61.6198 | 59.5674 | 56.387 | 53.9986 | 51.0955 | 47.3145 | 42.4402 | 37.0659 | 31.4532 | 25.4134 | 12.4941 | -11.6545 | -40.5331 | -56.4668 | 63.3242 | 61.5612 | 58.4933 | 57.107 | 55.3569 | 52.5894 | 48.9758 | 45.0656 | 40.9427 | 36.4073 | 27.3862 | 8.0807 | -12.893 | -25.7405 | 57.1598 | 55.0303 | 51.56 | 49.4382 | 46.8327 | 43.1719 | 38.3959 | 33.1872 | 27.76 | 21.933 | 9.4767 | -14.2428 | -42.1363 | -57.7203
|  |  | CT |  |  | 62.1465 | 60.4806 | 57.5658 | 55.434 | 52.9812 | 49.438 | 45.3641 | 40.4141 | 34.386 | 28.2037 | 15.9193 | -10.9823 | -21.3748 | -27.3537 | 63.3822 | 61.6774 | 58.5558 | 57.1083 | 55.4283 | 52.5894 | 49.2724 | 45.3686 | 40.9427 | 36.4073 | 27.3862 | 8.0807 | -2.3845 | -12.0495 | 57.6115 | 55.8171 | 52.5624 | 50.6565 | 48.4523 | 44.9756 | 40.9447 | 36.1144 | 30.3091 | 24.3748 | 12.6316 | -13.3651 | -22.7685 | -28.799
|  |  | LW |  |  | 61.6198 | 59.5674 | 56.387 | 53.9986 | 51.0955 | 47.3145 | 42.4402 | 37.0659 | 31.4532 | 25.4134 | 12.4941 | -11.6545 | -40.5331 | -56.4668 | 63.3242 | 61.5612 | 58.4933 | 57.107 | 55.3569 | 52.6153 | 48.9758 | 45.0656 | 41.0623 | 36.7602 | 27.5222 | 9.5197 | -12.893 | -25.7405 | 57.1598 | 55.0303 | 51.56 | 49.4382 | 46.8327 | 43.1719 | 38.3959 | 33.1872 | 27.76 | 21.933 | 9.4767 | -14.2428 | -42.1363 | -57.7203
|  |  | ST |  |  | 62.6601 | 61.4324 | 59.0323 | 57.8544 | 56.5087 | 54.6333 | 52.4198 | 50.0457 | 47.6571 | 44.9931 | 38.5777 | 18.7456 | 4.7598 | -2.7136 | 63.7249 | 62.3403 | 59.5988 | 58.6431 | 57.5635 | 55.7858 | 53.6581 | 51.4601 | 49.2571 | 46.8632 | 41.1928 | 23.954 | 10.3433 | 0.17319 | 58.1019 | 56.7334 | 53.9799 | 52.9359 | 51.7456 | 49.8536 | 47.5915 | 45.216 | 42.8215 | 40.1596 | 33.7153 | 13.9012 | 0.14079 | -6.481
|  |  | FS |  |  | 62.1465 | 60.4806 | 57.5658 | 55.434 | 52.9812 | 49.438 | 45.3641 | 40.4141 | 34.386 | 28.2037 | 15.9193 | -10.9823 | -21.3748 | -27.3537 | 63.708 | 62.3202 | 59.5954 | 58.8771 | 58.0196 | 56.3849 | 54.4877 | 52.4706 | 50.4961 | 48.4346 | 43.5877 | 28.0503 | 9.3365 | -9.1267 | 58.1013 | 56.7704 | 54.0997 | 53.3244 | 52.3988 | 50.6957 | 48.7278 | 46.626 | 44.512 | 42.3095 | 37.1218 | 20.4577 | 2.3548 | -9.4343
LOVEDEAN GSP | WYMERING BSP | WYMERING BSP | MINIMUM HEADROOM | SU 64948 05441 | YES | 47.6982 | 45.5904 | 43.1574 | 38.2544 | 33.0298 | 27.3791 | 20.9517 | 14.1446 | 6.933 | -3.8482 | -33.1872 | -82.0946 | -97.5389 | -109.0826 | 68.9319 | 67.6071 | 65.8224 | 63.1726 | 59.9573 | 56.2962 | 51.9559 | 47.3709 | 42.6516 | 34.337 | 12.1756 | -24.7762 | -76.7809 | -198.1752 | 53.7773 | 51.875 | 49.6965 | 45.1413 | 40.2513 | 34.8696 | 28.6686 | 22.102 | 15.2385 | 6.5988 | -21.5478 | -68.689 | -84.1846 | -96.3029
|  |  | CT |  |  | 49.3918 | 48.1069 | 46.5277 | 43.1942 | 39.7854 | 36.0135 | 31.9061 | 27.3372 | 21.1404 | 14.5366 | 1.3137 | -28.5313 | -43.6745 | -50.7163 | 69.1243 | 67.6071 | 65.8224 | 63.2252 | 60.4844 | 57.2935 | 53.617 | 49.4898 | 44.3539 | 38.6329 | 26.5321 | -6.4144 | -43.3223 | -99.3359 | 55.2605 | 54.0691 | 52.6183 | 49.5919 | 46.4729 | 42.9479 | 39.0157 | 34.6092 | 28.7116 | 22.3448 | 9.5453 | -19.2259 | -33.3764 | -40.2499
|  |  | LW |  |  | 47.6982 | 45.5904 | 43.1574 | 38.2544 | 33.0298 | 27.3791 | 20.9517 | 14.1446 | 6.933 | -3.8482 | -33.1872 | -82.0946 | -97.5389 | -109.0826 | 68.9319 | 67.634 | 66.1383 | 63.1726 | 59.9573 | 56.2962 | 51.9559 | 47.3709 | 42.6516 | 34.337 | 12.1756 | -24.7762 | -37.4878 | -48.1367 | 53.7773 | 51.875 | 49.6965 | 45.1413 | 40.2513 | 34.8696 | 28.6686 | 22.102 | 15.2385 | 6.5988 | -21.5478 | -68.689 | -84.1846 | -96.3029
|  |  | ST |  |  | 50.0347 | 49.1765 | 48.0332 | 46.2697 | 44.7981 | 43.2725 | 41.4384 | 39.7214 | 37.7049 | 35.4254 | 29.8849 | 8.9507 | -9.7467 | -20.4858 | 69.4392 | 68.1657 | 66.6421 | 64.2435 | 62.0857 | 59.7572 | 56.9253 | 54.1892 | 50.9458 | 47.3258 | 38.5549 | 7.5332 | -32.9878 | -92.7275 | 55.8369 | 55.0437 | 54.0063 | 52.1869 | 50.7016 | 49.1466 | 47.1953 | 45.412 | 43.3027 | 40.915 | 34.998 | 12.4557 | -6.221 | -17.4253
|  |  | FS |  |  | 49.3918 | 48.1069 | 46.5277 | 43.1942 | 39.7854 | 36.0135 | 31.9061 | 27.3372 | 21.1404 | 14.5366 | 1.3137 | -28.5313 | -43.6745 | -50.7163 | 69.4051 | 68.2039 | 66.7535 | 64.6055 | 62.2736 | 59.6695 | 56.6692 | 53.3069 | 49.243 | 44.6621 | 33.5816 | -6.6048 | -76.7809 | -198.1752 | 55.8443 | 55.2447 | 54.4759 | 53.1715 | 51.8278 | 50.3387 | 48.6555 | 46.7754 | 44.4049 | 41.7993 | 35.714 | 15.6416 | -8.9145 | -27.4233
COWLEY GSP | YARNTON BSP | YARNTON BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | 12.4641 | 8.364 | 4.0424 | -1.7433 | -8.781 | -16.2044 | -26.4104 | -38.8179 | -52.7342 | -67.915 | -100.6677 | -156.5874 | -181.2445 | -193.4915 | 36.2338 | 33.7024 | 31.0501 | 27.6145 | 23.3508 | 18.7852 | 11.8347 | 2.7896 | -7.174 | -18.1304 | -43.9534 | -130.4547 | -182.6794 | -206.8526 | 16.9076 | 13.03 | 8.9992 | 3.6759 | -2.9389 | -9.9709 | -20.1743 | -32.1829 | -45.5376 | -60.1698 | -91.8931 | -187.719 | -253.067 | -284.1759
|  |  | CT |  |  | 13.6835 | 10.5251 | 6.835 | 1.6152 | -4.2536 | -11.8832 | -20.4632 | -32.2768 | -47.1512 | -61.7512 | -89.4492 | -152.2942 | -181.2445 | -193.4915 | 36.553 | 34.3288 | 31.7354 | 28.4197 | 24.6537 | 19.4886 | 13.1934 | 4.1874 | -6.6602 | -17.3455 | -37.7355 | -84.5258 | -107.6807 | -123.1074 | 17.7934 | 14.7016 | 11.0819 | 6.1312 | 0.56786 | -6.9823 | -15.1272 | -26.4714 | -40.6963 | -54.7079 | -81.3761 | -141.9299 | -169.3869 | -180.9539
|  |  | LW |  |  | 12.4641 | 8.364 | 4.0424 | -1.7433 | -8.781 | -16.2044 | -26.4104 | -38.8179 | -52.7342 | -67.915 | -100.6677 | -156.5874 | -175.336 | -174.3656 | 36.2338 | 33.7024 | 31.0501 | 27.6145 | 23.3508 | 18.7852 | 11.8347 | 2.7896 | -7.174 | -18.1304 | -42.2645 | -82.6563 | -95.6809 | -108.6571 | 16.9076 | 13.03 | 8.9992 | 3.6759 | -2.9389 | -9.9709 | -20.1743 | -32.1829 | -45.5376 | -60.1698 | -91.8931 | -145.8994 | -163.807 | -168.3758
|  |  | ST |  |  | 15.1316 | 13.2674 | 11.0336 | 7.9599 | 4.4149 | 0.39907 | -4.2074 | -9.8505 | -16.5372 | -24.1731 | -43.5431 | -104.7993 | -146.3957 | -161.3219 | 37.4603 | 36.0842 | 34.4588 | 32.2525 | 29.7265 | 26.8418 | 23.4446 | 19.1417 | 13.6478 | 7.2928 | -9.2035 | -60.8532 | -96.5357 | -113.1121 | 19.2827 | 17.5729 | 15.5155 | 12.6067 | 9.2211 | 5.2546 | 0.53679 | -5.0758 | -11.5011 | -18.9034 | -37.9262 | -98.2122 | -139.1986 | -153.6139
|  |  | FS |  |  | 13.6835 | 10.5251 | 6.835 | 1.6152 | -4.2536 | -11.8832 | -20.4632 | -32.2768 | -47.1512 | -61.7512 | -89.4492 | -152.2942 | -181.2445 | -193.4915 | 37.3881 | 35.9311 | 34.1535 | 31.872 | 29.1013 | 25.7833 | 21.6936 | 14.5162 | 3.7943 | -9.4152 | -43.9534 | -130.4547 | -182.6794 | -206.8526 | 19.1788 | 17.4298 | 15.278 | 12.3103 | 8.7145 | 4.3945 | -0.95358 | -9.042 | -22.1617 | -38.3613 | -80.7336 | -187.719 | -253.067 | -284.1759
AXMINSTER | YEOVIL BSP | YEOVIL BSP | MINIMUM HEADROOM | ST 57586 16894 | YES | 19.3073 | 17.6403 | 13.6886 | 8.7475 | 2.7247 | -3.7628 | -13.1855 | -25.0573 | -39.0057 | -54.314 | -88.687 | -147.9891 | -178.3664 | -193.7519 | 35.1362 | 32.5986 | 30.0108 | 26.9521 | 23.0232 | 18.7075 | 11.895 | 3.449 | -6.3675 | -17.314 | -42.0754 | -89.9645 | -117.0137 | -154.0784 | 12.4218 | 8.7144 | 4.8455 | 0.23108 | -5.5272 | -11.7791 | -21.209 | -32.6914 | -46.0337 | -60.7648 | -93.8634 | -150.773 | -180.7392 | -195.5789
|  |  | CT |  |  | 19.4762 | 18.3015 | 16.7517 | 13.2759 | 8.2252 | 1.3938 | -6.9657 | -18.4435 | -33.274 | -48.4533 | -79.0433 | -145.5711 | -178.3664 | -193.7519 | 35.5422 | 33.543 | 31.1063 | 28.0006 | 24.3964 | 19.2198 | 13.0874 | 4.5679 | -6.1486 | -17.2995 | -39.7207 | -89.9645 | -117.0137 | -137.4303 | 13.8154 | 11.1916 | 8.0315 | 3.7406 | -1.1695 | -8.0212 | -16.0391 | -27.0537 | -41.2446 | -55.8661 | -85.2464 | -149.5077 | -180.7392 | -195.5789
|  |  | LW |  |  | 19.3073 | 17.6403 | 13.6886 | 8.7475 | 2.7247 | -3.7628 | -13.1855 | -25.0573 | -39.0057 | -54.314 | -88.687 | -147.9891 | -169.843 | -188.464 | 35.1362 | 32.5986 | 30.0108 | 26.9521 | 23.0232 | 18.7075 | 11.895 | 3.449 | -6.3675 | -17.314 | -42.0754 | -83.9488 | -104.8466 | -122.5185 | 12.4218 | 8.7144 | 4.8455 | 0.23108 | -5.5272 | -11.7791 | -21.209 | -32.6914 | -46.0337 | -60.7648 | -93.8634 | -150.773 | -171.8966 | -188.0428
|  |  | ST |  |  | 20.1822 | 19.6878 | 19.0379 | 17.7864 | 15.4673 | 11.5846 | 6.3103 | -0.27115 | -8.1285 | -17.0754 | -39.8599 | -109.0748 | -155.5231 | -173.5102 | 36.405 | 35.2184 | 33.7265 | 31.2969 | 28.5825 | 25.2669 | 20.8423 | 15.6365 | 9.2456 | 1.9877 | -16.541 | -73.7563 | -114.5379 | -136.5985 | 15.1557 | 13.6732 | 11.8198 | 8.8839 | 5.5665 | 1.5389 | -3.7895 | -10.1252 | -17.7778 | -26.5171 | -48.8486 | -117.2818 | -162.7522 | -180.721
|  |  | FS |  |  | 19.4762 | 18.3015 | 16.7517 | 13.2759 | 8.2252 | 1.3938 | -6.9657 | -18.4435 | -33.274 | -48.4533 | -79.0433 | -145.5711 | -178.3664 | -193.7519 | 36.6534 | 35.4269 | 33.9896 | 32.1074 | 29.8292 | 27.0779 | 23.6219 | 19.4099 | 14.4079 | 8.7559 | -5.5402 | -54.0867 | -108.707 | -154.0784 | 15.528 | 14.1176 | 12.4618 | 10.1232 | 7.3204 | 3.9692 | -0.20553 | -5.2771 | -11.2881 | -18.0343 | -34.9542 | -91.982 | -149.9018 | -184.2991
IVER 66KV | YIEWSLEY | YIEWSLEY | MINIMUM HEADROOM | TQ 05643 80961 | YES | 28.7554 | 28.0558 | 27.6357 | 26.6961 | 25.6275 | 23.8942 | 21.9212 | 19.9792 | 17.8088 | 15.6918 | 9.9068 | -9.1666 | -17.4936 | -18.2981 | 33.4444 | 33.1799 | 33.0392 | 32.6933 | 32.3117 | 31.1981 | 29.7078 | 28.2949 | 26.0226 | 23.4552 | 17.8284 | 3.5552 | -2.5582 | -3.0256 | 27.0025 | 26.4377 | 26.067 | 25.2134 | 24.2729 | 22.5388 | 20.5437 | 18.6245 | 16.5316 | 14.531 | 9.2643 | -9.0303 | -16.9648 | -17.6943
|  |  | CT |  |  | 29.2733 | 28.9091 | 28.7917 | 28.0954 | 27.3797 | 26.0097 | 24.5708 | 23.2177 | 21.2726 | 19.4368 | 16.143 | 8.145 | 3.0564 | 0.18639 | 33.5325 | 33.323 | 33.2136 | 32.8663 | 32.5455 | 31.4719 | 30.3005 | 29.2235 | 27.9503 | 26.7235 | 24.6007 | 19.0147 | 13.5604 | 6.0994 | 27.4468 | 27.1641 | 27.0611 | 26.4356 | 25.8208 | 24.4082 | 22.9138 | 21.5339 | 19.6615 | 17.9357 | 14.9027 | 7.6996 | 3.2381 | 0.77023
|  |  | LW |  |  | 28.7554 | 28.0558 | 27.6357 | 26.6961 | 25.6275 | 23.8942 | 21.9212 | 19.9792 | 17.8088 | 15.6918 | 9.9068 | -9.1666 | -17.4936 | -18.2981 | 33.4444 | 33.1799 | 33.0392 | 32.6933 | 32.3117 | 31.1981 | 29.7078 | 28.2949 | 26.0226 | 23.4552 | 17.8284 | 3.5552 | -2.5582 | -3.0256 | 27.0025 | 26.4377 | 26.067 | 25.2134 | 24.2729 | 22.5388 | 20.5437 | 18.6245 | 16.5316 | 14.531 | 9.2643 | -9.0303 | -16.9648 | -17.6943
|  |  | ST |  |  | 29.53 | 29.3047 | 29.3123 | 29.1455 | 28.9852 | 28.2616 | 27.5025 | 26.8066 | 26.0028 | 25.2791 | 24.0728 | 19.9866 | 16.3796 | 12.6043 | 33.5996 | 33.4291 | 33.3552 | 33.1249 | 32.9425 | 32.0907 | 31.1686 | 30.3092 | 29.366 | 28.5149 | 27.0078 | 22.4901 | 17.1932 | 9.9705 | 27.6572 | 27.4891 | 27.4894 | 27.2989 | 27.1642 | 26.332 | 25.4539 | 24.6559 | 23.7914 | 23.0447 | 21.8168 | 17.9628 | 14.6928 | 11.4332
|  |  | FS |  |  | 29.2733 | 28.9091 | 28.7917 | 28.0954 | 27.3797 | 26.0097 | 24.5708 | 23.2177 | 21.2726 | 19.4368 | 16.143 | 8.145 | 3.0564 | 0.18639 | 33.6079 | 33.4346 | 33.343 | 33.1804 | 32.9961 | 32.2658 | 31.4421 | 30.6111 | 29.7164 | 28.8689 | 27.178 | 22.147 | 13.8046 | -1.1273 | 27.6577 | 27.5066 | 27.4968 | 27.3607 | 27.2035 | 26.4943 | 25.7113 | 24.9332 | 24.1405 | 23.4356 | 22.1569 | 18.9632 | 15.3163 | 11.6891

## Primary Headroom Gen
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Generation Headroom Winter MVA | [13 empty] | Generation Headroom Summer MVA | [13 empty] | Generation Headroom Spring/Autumn MVA
[6 empty] | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH | ALDERNEY | MINIMUM HEADROOM | SZ 04270 95141 | NO | 23.6592 | 23.6486 | 23.6234 | 23.593 | 23.5579 | 23.5195 | 23.4784 | 23.436 | 23.3895 | 23.3392 | 23.225 | 22.8989 | 22.5528 | 22.2052 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 23.9742 | 23.9735 | 23.9715 | 23.9693 | 23.9666 | 23.9637 | 23.9606 | 23.9574 | 23.9539 | 23.9501 | 23.9414 | 23.9168 | 23.8907 | 23.8644
|  | ALDERNEY | CT |  |  | 23.6592 | 23.6486 | 23.6234 | 23.593 | 23.5579 | 23.5195 | 23.4784 | 23.436 | 23.3895 | 23.3413 | 23.2446 | 22.8989 | 22.5528 | 22.2052 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 23.9743 | 23.9735 | 23.9716 | 23.9694 | 23.9669 | 23.9642 | 23.9612 | 23.9583 | 23.955 | 23.9516 | 23.9448 | 23.9234 | 23.9019 | 23.8804
|  | ALDERNEY | LW |  |  | 23.6592 | 23.6486 | 23.6234 | 23.593 | 23.5579 | 23.5195 | 23.4784 | 23.436 | 23.3895 | 23.3413 | 23.2446 | 22.8989 | 22.5528 | 22.2052 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 23.9742 | 23.9735 | 23.9715 | 23.9693 | 23.9666 | 23.9637 | 23.9606 | 23.9574 | 23.9539 | 23.9502 | 23.9429 | 23.9168 | 23.8907 | 23.8644
|  | ALDERNEY | ST |  |  | 23.8553 | 23.6581 | 23.6471 | 23.6298 | 23.607 | 23.5566 | 23.5051 | 23.4533 | 23.3967 | 23.3392 | 23.225 | 22.948 | 22.6814 | 22.4177 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 23.9891 | 23.9742 | 23.9733 | 23.972 | 23.9703 | 23.9665 | 23.9626 | 23.9587 | 23.9544 | 23.9501 | 23.9414 | 23.9205 | 23.9004 | 23.8804
|  | ALDERNEY | FS |  |  | 23.999 | 23.8102 | 23.8083 | 23.8027 | 23.7954 | 23.782 | 23.7683 | 23.7516 | 23.7347 | 23.7173 | 23.6828 | 23.5978 | 23.5142 | 23.4298 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 30.9309 | 23.9999 | 23.9857 | 23.9855 | 23.9851 | 23.9845 | 23.9835 | 23.9825 | 23.9812 | 23.98 | 23.9786 | 23.976 | 23.9696 | 23.9633 | 23.9569
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT | MINIMUM HEADROOM | SU 85976 48834 | NO | 23.6 | 23.5948 | 23.5824 | 23.569 | 23.5553 | 23.5416 | 23.5278 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 21.9111 | 21.8759 | 21.8116 | 21.7431 | 21.6737 | 21.6048 | 21.5364 | 21.469 | 21.3942 | 21.3191 | 21.1712 | 20.9333 | 20.9242 | 20.9242 | 23.1468 | 23.1357 | 23.1093 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062
|  | ALDERSHOT | CT |  |  | 23.6 | 23.5948 | 23.5824 | 23.569 | 23.5553 | 23.5416 | 23.5278 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 21.9111 | 21.8759 | 21.8116 | 21.7431 | 21.6737 | 21.6048 | 21.5364 | 21.469 | 21.3942 | 21.3191 | 21.1712 | 20.9333 | 20.9242 | 20.9242 | 23.1468 | 23.1357 | 23.1093 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062
|  | ALDERSHOT | LW |  |  | 23.6 | 23.5948 | 23.5824 | 23.569 | 23.5553 | 23.5416 | 23.5278 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 21.9135 | 21.8819 | 21.8228 | 21.7614 | 21.6987 | 21.6358 | 21.5726 | 21.5103 | 21.4411 | 21.3715 | 21.2349 | 20.942 | 20.9242 | 20.9242 | 23.1475 | 23.1376 | 23.114 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062
|  | ALDERSHOT | ST |  |  | 23.6023 | 23.6005 | 23.5964 | 23.5904 | 23.5829 | 23.5733 | 23.5638 | 23.5545 | 23.5442 | 23.5338 | 23.5233 | 23.5233 | 23.5233 | 23.5233 | 21.9276 | 21.9164 | 21.8921 | 21.8593 | 21.8248 | 21.781 | 21.7376 | 21.695 | 21.6476 | 21.6002 | 21.5077 | 21.279 | 21.0425 | 20.9333 | 23.152 | 23.1484 | 23.1408 | 23.1292 | 23.1149 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062 | 23.1062
|  | ALDERSHOT | FS |  |  | 23.6033 | 23.603 | 23.6027 | 23.6008 | 23.5985 | 23.5954 | 23.5922 | 23.5882 | 23.5841 | 23.58 | 23.5722 | 23.5529 | 23.5333 | 23.5233 | 21.9334 | 21.9317 | 21.9297 | 21.9184 | 21.9047 | 21.8855 | 21.8676 | 21.8491 | 21.8305 | 21.8119 | 21.7759 | 21.6877 | 21.5978 | 21.5099 | 23.1538 | 23.1533 | 23.1526 | 23.1491 | 23.1447 | 23.1387 | 23.1327 | 23.125 | 23.1172 | 23.1095 | 23.1062 | 23.1062 | 23.1062 | 23.1062
MELKSHAM GSP | CHIPPENHAM | ALDERTON | MINIMUM HEADROOM | ST 84609 84059 | YES | 6.0534 | 6.0519 | 8.9 | 8.8974 | 8.8943 | 8.8904 | 8.8858 | 8.8803 | 8.8735 | 8.8657 | 8.8468 | 5.5499 | 5.195 | 4.7921 | 5.9817 | 5.9736 | 8.8072 | 8.789 | 8.7704 | 5.6583 | 5.5727 | 5.4872 | 5.3931 | 5.2983 | 5.1059 | 4.7023 | 4.248 | 3.7666 | 2.8437 | 2.8391 | 5.6824 | 5.6746 | 5.666 | 5.6568 | 5.6469 | 5.6364 | 5.6231 | 5.6083 | 5.5738 | 5.4553 | 5.1422 | 4.6011
|  | ALDERTON | CT |  |  | 6.0534 | 6.0519 | 8.9 | 8.8974 | 8.8943 | 8.8904 | 8.8858 | 8.8803 | 8.8735 | 8.8657 | 8.8468 | 5.5499 | 5.195 | 4.7921 | 5.9817 | 5.9736 | 8.8072 | 8.789 | 8.7704 | 5.6583 | 5.5727 | 5.4872 | 5.3931 | 5.2983 | 5.1059 | 4.7023 | 4.248 | 3.7666 | 2.8437 | 2.8391 | 5.6824 | 5.6746 | 5.666 | 5.6568 | 5.6469 | 5.6364 | 5.6231 | 5.6083 | 5.5738 | 5.4553 | 5.1422 | 4.6011
|  | ALDERTON | LW |  |  | 6.0534 | 6.0519 | 8.9 | 8.8974 | 8.8943 | 8.8904 | 8.8858 | 8.8803 | 8.8735 | 8.8657 | 8.8468 | 5.5499 | 5.195 | 4.7921 | 5.985 | 5.9796 | 8.8177 | 8.8045 | 8.7909 | 8.7769 | 5.6389 | 5.564 | 5.4821 | 5.3998 | 5.2335 | 4.9003 | 4.5273 | 4.1204 | 2.8478 | 2.8464 | 5.6946 | 5.6921 | 5.6891 | 5.6854 | 5.681 | 5.6758 | 5.6694 | 5.6619 | 5.6439 | 5.5798 | 5.4788 | 5.0302
|  | ALDERTON | ST |  |  | 6.0548 | 6.0543 | 8.9036 | 8.9028 | 8.9019 | 8.9006 | 8.8991 | 8.8975 | 8.8957 | 8.8937 | 8.8895 | 8.8732 | 8.8468 | 5.6843 | 5.9873 | 5.9843 | 8.828 | 8.8186 | 8.8073 | 8.8011 | 8.7949 | 8.7886 | 8.7818 | 5.6897 | 5.618 | 5.4343 | 5.2429 | 5.0455 | 2.8492 | 2.8487 | 5.698 | 5.6973 | 5.6964 | 5.6951 | 5.6937 | 5.6922 | 5.6905 | 5.6886 | 5.6845 | 5.6691 | 5.6439 | 5.6103
|  | ALDERTON | FS |  |  | 6.055 | 6.0546 | 8.9043 | 8.9037 | 8.9032 | 8.9025 | 8.9019 | 8.9012 | 8.9004 | 8.8996 | 8.898 | 8.8917 | 8.8835 | 8.8746 | 5.9889 | 5.9884 | 8.8378 | 8.8356 | 8.8329 | 8.8306 | 8.8284 | 8.8256 | 8.8228 | 8.82 | 8.8144 | 8.7992 | 8.7832 | 8.767 | 2.8493 | 2.849 | 5.6987 | 5.6982 | 5.6976 | 5.697 | 5.6964 | 5.6957 | 5.695 | 5.6942 | 5.6927 | 5.6867 | 5.6789 | 5.6704
BRAMLEY (FLEE) | ALTON | ALRESFORD | MINIMUM HEADROOM | SU 59684 32511 | YES | 17.3901 | 17.3901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 15.0207 | 14.9924 | 24.4248 | 24.3499 | 24.2745 | 24.1984 | 24.1222 | 24.0469 | 23.9995 | 23.9533 | 23.863 | 23.7809 | 18.0352 | 16.8341 | 15.6862 | 15.6862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 18.9711 | 17.7646
|  | ALRESFORD | CT |  |  | 17.3901 | 17.3901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 15.0207 | 14.9924 | 24.4248 | 24.3499 | 24.2745 | 24.1984 | 24.1222 | 24.0469 | 23.9995 | 23.9533 | 23.863 | 23.7809 | 18.0352 | 16.8341 | 15.6862 | 15.6862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 18.9711 | 17.7646
|  | ALRESFORD | LW |  |  | 17.3901 | 17.3901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 15.0256 | 15.0042 | 24.4535 | 24.3964 | 24.3382 | 24.279 | 24.219 | 24.1581 | 24.1021 | 24.0486 | 23.9812 | 23.8027 | 18.8663 | 17.7199 | 15.6862 | 15.6862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 18.6544
|  | ALRESFORD | ST |  |  | 17.3901 | 17.3901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 15.0328 | 15.0224 | 24.4996 | 24.4652 | 24.4237 | 24.3864 | 24.349 | 24.3106 | 24.2738 | 24.2382 | 24.1697 | 24.0146 | 23.9022 | 23.7904 | 15.6862 | 15.6862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862
|  | ALRESFORD | FS |  |  | 17.3901 | 17.3901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 26.8901 | 15.0376 | 15.0357 | 24.5328 | 24.5225 | 24.5105 | 24.4972 | 24.4837 | 24.4669 | 24.4521 | 24.4381 | 24.4105 | 24.342 | 24.2721 | 24.2028 | 15.6862 | 15.6862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862 | 25.1862
BRAMLEY (FLEE) | ALTON | ALTON LOCAL | MINIMUM HEADROOM | SU 72434 39606 | NO | 18.7799 | 18.5869 | 18.213 | 36.8373 | 36.4798 | 36.1219 | 35.7634 | 35.4064 | 35.0181 | 34.6312 | 33.8453 | 31.7635 | 29.5642 | 27.3163 | 37.1927 | 47.4267 | 46.8776 | 46.3159 | 45.7726 | 45.2289 | 44.6798 | 44.1347 | 43.5497 | 42.9776 | 41.833 | 39.4215 | 36.8442 | 34.2363 | 47.6893 | 47.4208 | 46.8674 | 46.3011 | 45.753 | 45.2044 | 44.6501 | 44.0996 | 43.5079 | 42.9289 | 41.7686 | 39.31 | 36.6674 | 33.9818
|  | ALTON LOCAL | CT |  |  | 18.7799 | 18.5869 | 18.213 | 36.8373 | 36.4798 | 36.1219 | 35.7634 | 35.4064 | 35.0181 | 34.6312 | 33.8453 | 31.7635 | 29.5642 | 27.3163 | 37.1927 | 47.4267 | 46.8776 | 46.3159 | 45.7726 | 45.2289 | 44.6798 | 44.1347 | 43.5497 | 42.9776 | 41.833 | 39.4215 | 36.8442 | 34.2363 | 47.6893 | 47.4208 | 46.8674 | 46.3011 | 45.753 | 45.2044 | 44.6501 | 44.0996 | 43.5079 | 42.9289 | 41.7686 | 39.31 | 36.6674 | 33.9818
|  | ALTON LOCAL | LW |  |  | 18.7799 | 18.5869 | 18.213 | 36.8373 | 36.4798 | 36.1219 | 35.7634 | 35.4064 | 35.0181 | 34.6312 | 33.8453 | 31.7635 | 29.5642 | 27.3163 | 37.2263 | 47.5012 | 47.0648 | 46.6265 | 46.2098 | 45.7929 | 45.3757 | 44.9606 | 44.5097 | 44.061 | 43.1508 | 40.7481 | 38.228 | 35.6742 | 47.7242 | 47.4977 | 47.0589 | 46.6181 | 46.1987 | 45.779 | 45.3588 | 44.9404 | 44.4856 | 44.0327 | 43.113 | 40.6801 | 38.1169 | 35.5054
|  | ALTON LOCAL | ST |  |  | 18.9861 | 18.7406 | 18.5589 | 37.3194 | 37.0422 | 36.8134 | 36.5816 | 36.3523 | 36.1071 | 35.8706 | 35.3995 | 34.127 | 32.8264 | 31.5184 | 37.4668 | 47.6799 | 47.4678 | 47.1879 | 46.8642 | 46.5972 | 46.3268 | 46.0593 | 45.7734 | 45.4976 | 44.9486 | 43.4682 | 41.9598 | 40.4477 | 47.964 | 47.6778 | 47.4646 | 47.1834 | 46.858 | 46.5895 | 46.3176 | 46.0485 | 45.7609 | 45.4833 | 44.9308 | 43.4393 | 41.9166 | 40.3871
|  | ALTON LOCAL | FS |  |  | 19.172 | 18.9532 | 18.8344 | 37.7712 | 37.7058 | 37.6284 | 37.5517 | 37.4551 | 37.3598 | 37.2661 | 37.079 | 36.5869 | 36.087 | 35.5896 | 38.3406 | 47.9284 | 47.7896 | 47.716 | 47.6397 | 47.5495 | 47.46 | 47.3474 | 47.2363 | 47.127 | 46.9089 | 46.3362 | 45.7554 | 45.1779 | 48.2198 | 47.9259 | 47.788 | 47.7139 | 47.6371 | 47.5464 | 47.4563 | 47.3431 | 47.2312 | 47.1213 | 46.9019 | 46.3249 | 45.7393 | 45.1567
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER | MINIMUM HEADROOM | SU 35240 46643 | YES | 16.5646 | 16.5646 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 31.4798 | 31.4543 | 31.3872 | 31.3153 | 31.2369 | 31.1578 | 31.0726 | 31.003 | 30.9663 | 30.9297 | 30.8542 | 30.727 | 30.727 | 30.727 | 31.9261 | 31.92 | 31.9038 | 31.8865 | 31.8677 | 31.8486 | 31.8282 | 31.8074 | 31.7854 | 31.7636 | 31.7184 | 31.6896 | 31.6896 | 31.6896
|  | ANDOVER | CT |  |  | 16.5646 | 16.5646 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 31.4833 | 31.463 | 31.4091 | 31.3515 | 31.2884 | 31.2249 | 31.1552 | 31.0851 | 31.0135 | 30.9848 | 30.9255 | 30.727 | 30.727 | 30.727 | 31.927 | 31.9221 | 31.9091 | 31.8952 | 31.8801 | 31.8648 | 31.848 | 31.8312 | 31.8137 | 31.7965 | 31.761 | 31.6896 | 31.6896 | 31.6896
|  | ANDOVER | LW |  |  | 16.5646 | 16.5646 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 31.4798 | 31.4543 | 31.3872 | 31.3153 | 31.2369 | 31.1578 | 31.0726 | 31.003 | 30.9663 | 30.9297 | 30.8542 | 30.727 | 30.727 | 30.727 | 31.9261 | 31.92 | 31.9038 | 31.8865 | 31.8677 | 31.8486 | 31.8282 | 31.8074 | 31.7854 | 31.7636 | 31.7184 | 31.6896 | 31.6896 | 31.6896
|  | ANDOVER | ST |  |  | 16.5646 | 16.5646 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 31.4869 | 31.4709 | 31.4323 | 31.376 | 31.3047 | 31.2452 | 31.182 | 31.1189 | 31.0524 | 31.0033 | 30.9497 | 30.8023 | 30.727 | 30.727 | 31.9278 | 31.924 | 31.9147 | 31.9011 | 31.884 | 31.8697 | 31.8545 | 31.8393 | 31.8233 | 31.8076 | 31.7755 | 31.6896 | 31.6896 | 31.6896
|  | ANDOVER | FS |  |  | 16.5646 | 16.5646 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 25.6421 | 31.4958 | 31.4943 | 31.4911 | 31.4793 | 31.4636 | 31.4441 | 31.4237 | 31.3984 | 31.3735 | 31.3488 | 31.2985 | 31.1613 | 31.0185 | 30.9569 | 31.93 | 31.9296 | 31.9288 | 31.926 | 31.9222 | 31.9175 | 31.9126 | 31.9065 | 31.9005 | 31.8946 | 31.8825 | 31.8495 | 31.8151 | 31.7798
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST | MINIMUM HEADROOM | SU 37953 46433 | YES | 22.0002 | 21.9933 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 36.1305 | 36.1084 | 36.0581 | 36.0026 | 35.9441 | 35.8851 | 35.8249 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 39.2444 | 39.2154 | 39.1491 | 39.0761 | 38.9992 | 38.9214 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639
|  | ANDOVER EAST | CT |  |  | 22.0002 | 21.9933 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 36.1319 | 36.1113 | 36.0642 | 36.0124 | 35.9576 | 35.9022 | 35.8461 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 39.2463 | 39.2192 | 39.1572 | 39.0891 | 39.0169 | 38.9439 | 38.8701 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639
|  | ANDOVER EAST | LW |  |  | 22.0002 | 21.9933 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 36.1305 | 36.1084 | 36.0581 | 36.0026 | 35.9441 | 35.8851 | 35.8249 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 35.8161 | 39.2444 | 39.2154 | 39.1491 | 39.0761 | 38.9992 | 38.9214 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639 | 38.8639
|  | ANDOVER EAST | ST |  |  | 22.0412 | 21.9992 | 31.4899 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 31.4852 | 36.2614 | 36.1273 | 36.0977 | 36.0536 | 35.9988 | 35.9748 | 35.9503 | 35.9271 | 35.9024 | 35.878 | 35.8284 | 35.8161 | 35.8161 | 35.8161 | 39.4167 | 39.2402 | 39.2013 | 39.1433 | 39.071 | 39.0395 | 39.0073 | 38.9767 | 38.9442 | 38.9122 | 38.8639 | 38.8639 | 38.8639 | 38.8639
|  | ANDOVER EAST | FS |  |  | 22.0449 | 22.0311 | 31.5303 | 31.5271 | 31.5233 | 31.5208 | 31.5183 | 31.5154 | 31.5125 | 31.5097 | 31.504 | 31.4881 | 31.4852 | 31.4852 | 36.273 | 36.2291 | 36.2264 | 36.2164 | 36.2042 | 36.1962 | 36.1882 | 36.179 | 36.1699 | 36.1609 | 36.1426 | 36.092 | 36.0386 | 35.9828 | 39.432 | 39.3743 | 39.3707 | 39.3575 | 39.3414 | 39.331 | 39.3204 | 39.3082 | 39.2963 | 39.2845 | 39.2604 | 39.1938 | 39.1235 | 39.05
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER TOWN | MINIMUM HEADROOM | SU 36207 45078 | YES | 34.2577 | 34.2486 | 34.2187 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 14.5716 | 14.5673 | 14.5539 | 14.5349 | 14.5102 | 14.4805 | 14.4409 | 14.3991 | 14.3545 | 14.3103 | 14.2209 | 13.957 | 13.6201 | 13.6201 | 14.0594 | 14.0576 | 14.052 | 14.0441 | 14.0338 | 14.0215 | 14.0049 | 13.9876 | 13.969 | 13.9505 | 13.9433 | 13.9433 | 13.9433 | 13.9433
|  | ANDOVER TOWN | CT |  |  | 34.2577 | 34.2486 | 34.2187 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 14.5716 | 14.5673 | 14.5539 | 14.5349 | 14.5113 | 14.484 | 14.4616 | 14.4382 | 14.4138 | 14.3895 | 14.3384 | 14.0205 | 13.6866 | 13.6201 | 14.0594 | 14.0576 | 14.052 | 14.0441 | 14.0343 | 14.0229 | 14.0136 | 14.0038 | 13.9937 | 13.9835 | 13.9622 | 13.9433 | 13.9433 | 13.9433
|  | ANDOVER TOWN | LW |  |  | 34.2577 | 34.2486 | 34.2187 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 14.5718 | 14.5678 | 14.5547 | 14.5353 | 14.5102 | 14.4805 | 14.4567 | 14.4318 | 14.4064 | 14.381 | 14.3251 | 13.957 | 13.6201 | 13.6201 | 14.0595 | 14.0578 | 14.0524 | 14.0443 | 14.0338 | 14.0215 | 14.0115 | 14.0012 | 13.9906 | 13.98 | 13.9567 | 13.9433 | 13.9433 | 13.9433
|  | ANDOVER TOWN | ST |  |  | 34.2599 | 34.2535 | 34.2346 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 14.5728 | 14.57 | 14.5617 | 14.5471 | 14.5276 | 14.4823 | 14.4409 | 14.3991 | 14.3545 | 14.3103 | 14.2209 | 13.9807 | 13.7403 | 13.6201 | 14.0599 | 14.0587 | 14.0553 | 14.0492 | 14.0411 | 14.0222 | 14.0049 | 13.9876 | 13.969 | 13.9505 | 13.9433 | 13.9433 | 13.9433 | 13.9433
|  | ANDOVER TOWN | FS |  |  | 34.2636 | 34.263 | 34.2601 | 62.9512 | 62.9388 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 62.9132 | 14.5744 | 14.5742 | 14.5729 | 14.569 | 14.5635 | 14.5483 | 14.5348 | 14.5181 | 14.5017 | 14.4855 | 14.4525 | 14.3637 | 14.2718 | 14.1771 | 14.0606 | 14.0605 | 14.0599 | 14.0583 | 14.056 | 14.0497 | 14.0441 | 14.0371 | 14.0303 | 14.0235 | 14.0098 | 13.9728 | 13.9433 | 13.9433
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD | MINIMUM HEADROOM | SU 75949 65766 | YES | 32.3845 | 32.3845 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 33.964 | 33.3856 | 32.7759 | 23.6843 | 23.6437 | 23.546 | 23.4393 | 23.3597 | 23.2928 | 23.2623 | 23.2533 | 23.2436 | 23.234 | 23.215 | 23.1966 | 23.1966 | 23.1966 | 25.1359 | 25.1299 | 25.1154 | 25.0995 | 25.0834 | 25.0672 | 25.0509 | 25.0348 | 25.0175 | 25.0004 | 24.9667 | 24.9431 | 24.9431 | 24.9431
|  | ARBORFIELD | CT |  |  | 32.3845 | 32.3845 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 33.964 | 33.3856 | 32.7759 | 23.6843 | 23.6437 | 23.546 | 23.4393 | 23.3597 | 23.2928 | 23.2623 | 23.2533 | 23.2436 | 23.234 | 23.215 | 23.1966 | 23.1966 | 23.1966 | 25.1359 | 25.1299 | 25.1154 | 25.0995 | 25.0834 | 25.0672 | 25.0509 | 25.0348 | 25.0175 | 25.0004 | 24.9667 | 24.9431 | 24.9431 | 24.9431
|  | ARBORFIELD | LW |  |  | 32.3845 | 32.3845 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 33.964 | 33.3856 | 32.7759 | 23.6851 | 23.6457 | 23.5509 | 23.4474 | 23.3663 | 23.3005 | 23.2635 | 23.2544 | 23.2448 | 23.2352 | 23.2164 | 23.1966 | 23.1966 | 23.1966 | 25.136 | 25.1302 | 25.1161 | 25.1007 | 25.085 | 25.069 | 25.053 | 25.0369 | 25.0197 | 25.0027 | 24.9691 | 24.9431 | 24.9431 | 24.9431
|  | ARBORFIELD | ST |  |  | 32.3845 | 32.3845 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 34.2654 | 23.7 | 23.6817 | 23.6412 | 23.5795 | 23.5031 | 23.4547 | 23.406 | 23.3764 | 23.3446 | 23.3134 | 23.2659 | 23.2443 | 23.2222 | 23.2002 | 25.1382 | 25.1355 | 25.1295 | 25.1203 | 25.109 | 25.1018 | 25.0946 | 25.0874 | 25.0797 | 25.0721 | 25.0573 | 25.0187 | 24.9794 | 24.9431
|  | ARBORFIELD | FS |  |  | 32.3845 | 32.3845 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 43.252 | 23.7095 | 23.7073 | 23.7046 | 23.6878 | 23.667 | 23.6507 | 23.6341 | 23.613 | 23.5922 | 23.5718 | 23.532 | 23.4293 | 23.3568 | 23.2943 | 25.1396 | 25.1393 | 25.1389 | 25.1364 | 25.1333 | 25.1309 | 25.1284 | 25.1253 | 25.1222 | 25.1192 | 25.1133 | 25.098 | 25.0827 | 25.0675
LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD | MINIMUM HEADROOM | SZ 93193 99152 | YES | -2.2877 | -2.2988 | 7.1014 | 7.073 | 7.0428 | 7.0128 | 6.983 | 6.9524 | 6.9191 | 6.8731 | 6.7831 | 6.4337 | 5.8088 | 5.1669 | 16.2064 | 16.1884 | 16.148 | 16.1016 | 16.0524 | 16.0035 | 15.9549 | 15.905 | 15.8508 | 15.7759 | 15.6292 | 15.0597 | 14.0415 | 12.9954 | 17.4321 | 17.4147 | 17.3759 | 17.3314 | 17.2841 | 17.2372 | 17.1905 | 17.1426 | 17.0905 | 17.0186 | 16.8776 | 16.3306 | 15.3526 | 14.3478
|  | ARGYLE ROAD | CT |  |  | -2.2877 | -2.2988 | 7.1014 | 7.073 | 7.0428 | 7.0128 | 6.983 | 6.9524 | 6.9195 | 6.8861 | 6.8201 | 6.4337 | 5.8088 | 5.1669 | 16.2066 | 16.1892 | 16.1498 | 16.1048 | 16.0574 | 16.01 | 15.9627 | 15.9133 | 15.8592 | 15.8036 | 15.694 | 15.1593 | 14.2834 | 13.3564 | 17.4322 | 17.4155 | 17.3776 | 17.3345 | 17.2889 | 17.2434 | 17.198 | 17.1505 | 17.0986 | 17.0451 | 16.9399 | 16.4263 | 15.585 | 14.6945
|  | ARGYLE ROAD | LW |  |  | -2.2877 | -2.2988 | 7.1014 | 7.073 | 7.0428 | 7.0128 | 6.983 | 6.9524 | 6.9195 | 6.8861 | 6.8201 | 6.4337 | 5.8088 | 5.1669 | 16.2064 | 16.1884 | 16.148 | 16.1016 | 16.0524 | 16.0035 | 15.9549 | 15.905 | 15.8514 | 15.797 | 15.6895 | 15.0597 | 14.0415 | 12.9954 | 17.4321 | 17.4147 | 17.3759 | 17.3314 | 17.2841 | 17.2372 | 17.1905 | 17.1426 | 17.0911 | 17.0388 | 16.9356 | 16.3306 | 15.3526 | 14.3478
|  | ARGYLE ROAD | ST |  |  | -2.1777 | -2.2891 | 7.1252 | 7.1093 | 7.0897 | 7.0478 | 7.0065 | 6.9647 | 6.9191 | 6.8731 | 6.7831 | 6.5156 | 6.1175 | 5.7131 | 16.3857 | 16.2041 | 16.1867 | 16.1608 | 16.1288 | 16.0606 | 15.9932 | 15.9251 | 15.8508 | 15.7759 | 15.6292 | 15.1933 | 14.5445 | 13.8855 | 17.6043 | 17.4298 | 17.4131 | 17.3883 | 17.3575 | 17.292 | 17.2273 | 17.1619 | 17.0905 | 17.0186 | 16.8776 | 16.4589 | 15.8358 | 15.2027
|  | ARGYLE ROAD | FS |  |  | -2.1753 | -2.2829 | 7.1402 | 7.1352 | 7.1292 | 7.1176 | 7.1062 | 7.0918 | 7.0773 | 7.0628 | 7.0341 | 6.9685 | 6.8678 | 6.7059 | 16.3896 | 16.2142 | 16.2111 | 16.2029 | 16.1932 | 16.1744 | 16.1557 | 16.1322 | 16.1087 | 16.085 | 16.0383 | 15.9314 | 15.7672 | 15.5034 | 17.608 | 17.4395 | 17.4366 | 17.4287 | 17.4193 | 17.4013 | 17.3834 | 17.3608 | 17.3382 | 17.3154 | 17.2706 | 17.1679 | 17.0102 | 16.7568
COWLEY GSP | HEADINGTON BSP | ARNCOTT | MINIMUM HEADROOM | SP 60730 18095 | YES | 7.052 | 6.986 | 13.8737 | 13.6873 | 13.4939 | 13.3358 | 13.2 | 13.0612 | 12.9104 | 12.7883 | 12.5461 | 12.1167 | 11.6338 | 11.1015 | 12.6297 | 12.5427 | 12.3284 | 12.0823 | 11.8271 | 11.6193 | 11.4413 | 11.2598 | 11.0634 | 10.9057 | 10.5949 | 10.0623 | 9.4836 | 8.8674 | 13.0585 | 12.9674 | 12.743 | 12.4853 | 12.2181 | 12.0002 | 11.8134 | 11.6228 | 11.4164 | 11.2502 | 10.922 | 10.354 | 9.7303 | 9.0591
|  | ARNCOTT | CT |  |  | 7.052 | 6.986 | 13.8737 | 13.6873 | 13.4939 | 13.3358 | 13.2 | 13.0612 | 12.9104 | 12.7883 | 12.5461 | 12.1167 | 11.6338 | 11.1015 | 12.6322 | 12.556 | 12.367 | 12.1526 | 11.9315 | 11.7505 | 11.5869 | 11.403 | 11.1966 | 11.028 | 10.7257 | 10.1907 | 9.6021 | 8.9818 | 13.0606 | 12.9801 | 12.7815 | 12.5561 | 12.3236 | 12.1329 | 11.9603 | 11.7663 | 11.5482 | 11.3693 | 11.0472 | 10.4669 | 9.8204 | 9.1334
|  | ARNCOTT | LW |  |  | 7.052 | 6.986 | 13.8737 | 13.6873 | 13.4939 | 13.3358 | 13.2 | 13.0612 | 12.9104 | 12.7883 | 12.5461 | 12.1167 | 11.6338 | 11.1015 | 12.6297 | 12.5427 | 12.3284 | 12.0823 | 11.8271 | 11.6193 | 11.4413 | 11.2598 | 11.0634 | 10.9057 | 10.5949 | 10.0623 | 9.4836 | 8.8674 | 13.0585 | 12.9674 | 12.743 | 12.4853 | 12.2181 | 12.0002 | 11.8134 | 11.6228 | 11.4164 | 11.2502 | 10.922 | 10.354 | 9.7303 | 9.0591
|  | ARNCOTT | ST |  |  | 15.1676 | 7.0309 | 13.9884 | 13.8624 | 13.7173 | 13.6423 | 13.5761 | 13.4999 | 13.4136 | 13.347 | 13.2337 | 12.9793 | 12.7225 | 12.4566 | 13.0775 | 12.6012 | 12.4788 | 12.3119 | 12.1198 | 12.021 | 11.9339 | 11.8335 | 11.7199 | 11.6325 | 11.4843 | 11.1555 | 10.8295 | 10.4977 | 19.7539 | 13.029 | 12.9008 | 12.7263 | 12.5252 | 12.4217 | 12.3304 | 12.2252 | 12.1061 | 12.0144 | 11.8589 | 11.5124 | 11.1672 | 10.8139
|  | ARNCOTT | FS |  |  | 15.1949 | 7.0756 | 14.099 | 14.0565 | 14.0108 | 13.9796 | 13.9533 | 13.9223 | 13.8905 | 13.8672 | 13.8214 | 13.7213 | 13.6272 | 13.5349 | 13.3247 | 12.6604 | 12.6252 | 12.5691 | 12.5087 | 12.4677 | 12.433 | 12.3922 | 12.3504 | 12.32 | 12.2599 | 12.1302 | 12.0098 | 11.8922 | 19.7541 | 13.0909 | 13.054 | 12.9953 | 12.932 | 12.8891 | 12.8527 | 12.81 | 12.7661 | 12.7342 | 12.6712 | 12.5346 | 12.4073 | 12.283
BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT | MINIMUM HEADROOM | SU 91615 68855 | NO | 14.0855 | 13.9331 | 27.8533 | 27.4975 | 27.1582 | 26.8259 | 26.4958 | 26.1677 | 25.8137 | 25.4622 | 24.7936 | 23.8752 | 22.8668 | 21.8681 | 34.5754 | 34.5467 | 34.4845 | 34.4175 | 34.3536 | 34.291 | 34.2288 | 34.1669 | 34.1002 | 34.0673 | 34.0673 | 34.0673 | 34.0673 | 26.0373 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 26.5409
|  | ASCOT | CT |  |  | 14.0855 | 13.9331 | 27.8533 | 27.4975 | 27.1582 | 26.8259 | 26.4958 | 26.1677 | 25.8137 | 25.4622 | 24.7936 | 23.8752 | 22.8668 | 21.8681 | 34.5764 | 34.5496 | 34.491 | 34.428 | 34.3675 | 34.3078 | 34.2478 | 34.1878 | 34.1232 | 34.0673 | 34.0673 | 34.0673 | 34.0673 | 26.2431 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048
|  | ASCOT | LW |  |  | 14.0855 | 13.9331 | 27.8533 | 27.4975 | 27.1582 | 26.8259 | 26.4958 | 26.1677 | 25.8137 | 25.4622 | 24.7936 | 23.8752 | 22.8668 | 21.8681 | 34.5754 | 34.5467 | 34.4845 | 34.4175 | 34.3536 | 34.291 | 34.2288 | 34.1669 | 34.1002 | 34.0673 | 34.0673 | 34.0673 | 34.0673 | 26.0373 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 26.5409
|  | ASCOT | ST |  |  | 14.1871 | 14.0652 | 28.167 | 27.9519 | 27.7032 | 27.5903 | 27.4756 | 27.3604 | 27.2358 | 27.114 | 26.8927 | 26.3393 | 25.743 | 25.1492 | 34.5945 | 34.5716 | 34.5436 | 34.5031 | 34.4562 | 34.435 | 34.4134 | 34.3917 | 34.3682 | 34.3452 | 34.3035 | 34.1993 | 34.0869 | 34.0673 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048
|  | ASCOT | FS |  |  | 14.2255 | 14.2081 | 28.4393 | 28.3755 | 28.3052 | 28.2641 | 28.2231 | 28.1716 | 28.1206 | 28.0701 | 27.9772 | 27.7567 | 27.5274 | 27.2955 | 34.6018 | 34.5985 | 34.5949 | 34.5829 | 34.5697 | 34.5619 | 34.5542 | 34.5445 | 34.5349 | 34.5254 | 34.5079 | 34.4663 | 34.4231 | 34.3794 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048 | 35.5048
LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD | MINIMUM HEADROOM | SU 84085 06737 | YES | 26.4067 | 26.4067 | 26.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 36.7161 | 34.6171 | 32.5267 | 25.952 | 25.889 | 25.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 37.4754 | 36.1594 | 33.3158 | 30.8432 | 28.3806 | 25.465 | 25.2982 | 25.2119 | 44.1066 | 44.0664 | 44.0664 | 44.0664 | 37.6802 | 37.1402 | 36.5378 | 35.2812 | 32.5207 | 30.1204 | 27.7298
|  | ASHLING ROAD | CT |  |  | 26.4067 | 26.4067 | 26.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 36.7161 | 34.6171 | 32.5267 | 25.9528 | 25.8907 | 25.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 37.8266 | 36.5374 | 33.7818 | 31.3028 | 28.8621 | 25.4669 | 25.3057 | 25.228 | 44.1258 | 44.0664 | 44.0664 | 44.0664 | 37.9811 | 37.4533 | 36.8623 | 35.6482 | 32.9731 | 30.5666 | 28.1972
|  | ASHLING ROAD | LW |  |  | 26.4067 | 26.4067 | 26.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 36.7161 | 34.6171 | 32.5267 | 25.952 | 25.889 | 25.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 37.4754 | 36.1594 | 33.3158 | 30.8432 | 28.3806 | 25.465 | 25.2982 | 25.2119 | 44.1066 | 44.0664 | 44.0664 | 44.0664 | 37.6802 | 37.1402 | 36.5378 | 35.2812 | 32.5207 | 30.1204 | 27.7298
|  | ASHLING ROAD | ST |  |  | 26.5206 | 26.4067 | 26.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 37.1625 | 26.0218 | 25.9491 | 25.9351 | 44.9119 | 44.8886 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 36.8483 | 35.3245 | 33.8416 | 25.6407 | 25.4574 | 25.4223 | 44.3636 | 44.2963 | 44.2149 | 44.1336 | 44.0773 | 44.0664 | 44.0664 | 37.6262 | 35.95 | 34.4707 | 33.0312
|  | ASHLING ROAD | FS |  |  | 26.5322 | 26.4067 | 26.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 45.4067 | 26.0248 | 25.9824 | 25.9782 | 44.9681 | 44.9571 | 44.9448 | 44.9325 | 44.9178 | 44.9025 | 44.8889 | 44.8816 | 44.8816 | 44.8816 | 44.8816 | 25.6483 | 25.5414 | 25.5309 | 44.5055 | 44.4776 | 44.4466 | 44.4157 | 44.3786 | 44.3401 | 44.2975 | 44.2113 | 44.0732 | 44.0664 | 44.0664
MELKSHAM GSP | NORRINGTON | ASHTON PARK | MINIMUM HEADROOM | ST 87141 57741 | YES | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 22.4375 | 20.9793 | 30.2615 | 30.2479 | 30.2242 | 30.1883 | 30.1482 | 30.1069 | 30.0631 | 30.0178 | 29.9729 | 29.9272 | 23.4129 | 20.4766 | 18.384 | 16.5377 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 20.8606 | 18.7744 | 16.9337
|  | ASHTON PARK | CT |  |  | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 22.4375 | 20.9793 | 30.2626 | 30.2513 | 30.2317 | 30.2015 | 30.1679 | 30.1331 | 30.0969 | 30.0584 | 30.018 | 29.9757 | 29.8859 | 21.9899 | 20.2769 | 18.5915 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 22.3693 | 20.6615 | 18.9813
|  | ASHTON PARK | LW |  |  | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 22.4375 | 20.9793 | 30.2615 | 30.2479 | 30.2242 | 30.1883 | 30.1482 | 30.1069 | 30.0631 | 30.0178 | 29.9729 | 29.9272 | 23.4129 | 20.4766 | 18.384 | 16.5377 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 20.8606 | 18.7744 | 16.9337
|  | ASHTON PARK | ST |  |  | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 30.2715 | 30.2561 | 30.2426 | 30.2172 | 30.1861 | 30.1585 | 30.1301 | 30.1003 | 30.0683 | 30.0348 | 29.9633 | 23.3728 | 22.1458 | 20.9568 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 22.5247 | 21.3394
|  | ASHTON PARK | FS |  |  | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 33.3958 | 30.2883 | 30.2652 | 30.263 | 30.2551 | 30.2458 | 30.2358 | 30.2255 | 30.2135 | 30.2018 | 30.1897 | 30.1638 | 30.095 | 30.0399 | 29.9965 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363 | 30.6363
BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT | MINIMUM HEADROOM | SU 91122 63523 | NO | 97.7062 | 97.7062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 30.8344 | 30.7939 | 30.6974 | 30.619 | 30.5942 | 30.5696 | 30.5452 | 30.5211 | 30.4952 | 30.4714 | 30.4428 | 30.3837 | 30.3207 | 30.298 | 32.2743 | 32.2645 | 32.2412 | 32.2158 | 32.1908 | 32.166 | 32.1414 | 32.1171 | 32.091 | 32.0651 | 32.0386 | 32.0386 | 32.0386 | 32.0386
|  | BAGSHOT | CT |  |  | 97.7062 | 97.7062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 30.837 | 30.8003 | 30.713 | 30.6251 | 30.6026 | 30.5804 | 30.5583 | 30.5364 | 30.5129 | 30.4896 | 30.4569 | 30.3969 | 30.3319 | 30.298 | 32.275 | 32.2661 | 32.2449 | 32.222 | 32.1993 | 32.1769 | 32.1546 | 32.1326 | 32.1089 | 32.0854 | 32.0392 | 32.0386 | 32.0386 | 32.0386
|  | BAGSHOT | LW |  |  | 97.7062 | 97.7062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 30.8344 | 30.7939 | 30.6974 | 30.619 | 30.5942 | 30.5696 | 30.5452 | 30.5211 | 30.4952 | 30.4714 | 30.4428 | 30.3837 | 30.3207 | 30.298 | 32.2743 | 32.2645 | 32.2412 | 32.2158 | 32.1908 | 32.166 | 32.1414 | 32.1171 | 32.091 | 32.0651 | 32.0386 | 32.0386 | 32.0386 | 32.0386
|  | BAGSHOT | ST |  |  | 97.7062 | 97.7062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 30.8515 | 30.8356 | 30.8008 | 30.7483 | 30.6851 | 30.6329 | 30.6162 | 30.604 | 30.5909 | 30.578 | 30.5528 | 30.4896 | 30.445 | 30.4075 | 32.2785 | 32.2746 | 32.2662 | 32.2535 | 32.2382 | 32.2255 | 32.213 | 32.2007 | 32.1875 | 32.1745 | 32.1491 | 32.0853 | 32.0386 | 32.0386
|  | BAGSHOT | FS |  |  | 97.7062 | 97.7062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 183.2062 | 30.8596 | 30.857 | 30.854 | 30.8366 | 30.8159 | 30.7981 | 30.7804 | 30.7576 | 30.7354 | 30.7135 | 30.671 | 30.6128 | 30.5872 | 30.5626 | 32.2804 | 32.2798 | 32.2791 | 32.2749 | 32.2698 | 32.2655 | 32.2613 | 32.2557 | 32.2504 | 32.2451 | 32.2348 | 32.2095 | 32.1838 | 32.159
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL | MINIMUM HEADROOM | SU 42417 63142 | YES | 89.8168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 16.422 | 16.4048 | 16.3634 | 16.3185 | 16.2741 | 16.2301 | 16.1865 | 16.1434 | 16.0968 | 16.0875 | 16.0875 | 16.0875 | 12.9477 | 12.5243 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 13.0376
|  | BALL HILL | CT |  |  | 89.8168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 16.423 | 16.4073 | 16.3695 | 16.3285 | 16.288 | 16.2478 | 16.2079 | 16.1685 | 16.126 | 16.0875 | 16.0875 | 16.0875 | 13.0508 | 12.5979 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 13.1115
|  | BALL HILL | LW |  |  | 89.8168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 16.422 | 16.4048 | 16.3634 | 16.3185 | 16.2741 | 16.2301 | 16.1865 | 16.1434 | 16.0968 | 16.0875 | 16.0875 | 16.0875 | 12.9477 | 12.5243 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 13.0376
|  | BALL HILL | ST |  |  | 89.8168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 16.4272 | 16.4171 | 16.3947 | 16.3609 | 16.3202 | 16.3081 | 16.2961 | 16.2842 | 16.2714 | 16.2588 | 16.2341 | 16.1715 | 16.1081 | 16.0875 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094
|  | BALL HILL | FS |  |  | 89.8168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 175.3168 | 16.4327 | 16.4317 | 16.4305 | 16.4231 | 16.4143 | 16.41 | 16.4057 | 16.4002 | 16.3947 | 16.3893 | 16.3789 | 16.353 | 16.3278 | 16.3037 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094 | 16.8094
BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY | MINIMUM HEADROOM | SU 42075 42720 | YES | 5.6972 | 5.693 | 5.6819 | 5.6698 | 5.6569 | 5.6437 | 5.613 | 5.5818 | 5.5483 | 5.5154 | 5.4505 | 5.2766 | 4.9873 | 4.7007 | 5.6966 | 5.6915 | 5.6781 | 5.6634 | 5.648 | 5.6324 | 5.5975 | 5.5607 | 5.5213 | 5.4825 | 5.4061 | 5.1895 | 4.8345 | 4.4829 | 5.6967 | 5.6915 | 5.6782 | 5.6635 | 5.6482 | 5.6327 | 5.5978 | 5.5612 | 5.5218 | 5.4832 | 5.407 | 5.1911 | 4.8371 | 4.4866
|  | BARTON STACEY | CT |  |  | 5.6972 | 5.693 | 5.6819 | 5.6698 | 5.6569 | 5.6437 | 5.63 | 5.6161 | 5.6013 | 5.586 | 5.5547 | 5.2766 | 4.9873 | 4.7007 | 5.6966 | 5.6915 | 5.6781 | 5.6634 | 5.648 | 5.6324 | 5.6161 | 5.5997 | 5.5824 | 5.5652 | 5.5303 | 5.1895 | 4.8345 | 4.4829 | 5.6967 | 5.6915 | 5.6782 | 5.6635 | 5.6482 | 5.6327 | 5.6164 | 5.6 | 5.5827 | 5.5656 | 5.5309 | 5.1911 | 4.8371 | 4.4866
|  | BARTON STACEY | LW |  |  | 5.6972 | 5.693 | 5.6819 | 5.6698 | 5.6569 | 5.6437 | 5.63 | 5.6161 | 5.6013 | 5.586 | 5.5547 | 5.2766 | 4.9873 | 4.7007 | 5.6968 | 5.6918 | 5.6787 | 5.6644 | 5.6492 | 5.6337 | 5.6175 | 5.6012 | 5.5837 | 5.5658 | 5.5288 | 5.2012 | 4.8605 | 4.5228 | 5.6968 | 5.6918 | 5.6788 | 5.6645 | 5.6493 | 5.6339 | 5.6178 | 5.6015 | 5.584 | 5.5662 | 5.5293 | 5.2027 | 4.863 | 4.5264
|  | BARTON STACEY | ST |  |  | 5.6988 | 5.6969 | 5.6921 | 5.685 | 5.676 | 5.6445 | 5.613 | 5.5818 | 5.5483 | 5.5154 | 5.4505 | 5.2843 | 5.1169 | 4.9503 | 5.6986 | 5.6963 | 5.6907 | 5.6823 | 5.6717 | 5.6346 | 5.5975 | 5.5607 | 5.5213 | 5.4825 | 5.4061 | 5.2103 | 5.0131 | 4.8168 | 5.6986 | 5.6963 | 5.6908 | 5.6824 | 5.6718 | 5.6348 | 5.5978 | 5.5612 | 5.5218 | 5.4832 | 5.407 | 5.2118 | 5.0152 | 4.8195
|  | BARTON STACEY | FS |  |  | 5.6999 | 5.6997 | 5.6993 | 5.6975 | 5.6952 | 5.6842 | 5.6731 | 5.659 | 5.645 | 5.6313 | 5.6044 | 5.5374 | 5.4712 | 5.4072 | 5.6998 | 5.6996 | 5.6992 | 5.6971 | 5.6943 | 5.6813 | 5.6683 | 5.6516 | 5.6352 | 5.6191 | 5.5874 | 5.5085 | 5.4305 | 5.3551 | 5.6998 | 5.6996 | 5.6992 | 5.6971 | 5.6944 | 5.6814 | 5.6684 | 5.6518 | 5.6354 | 5.6194 | 5.5877 | 5.5091 | 5.4313 | 5.3561
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE | MINIMUM HEADROOM | SU 65155 52705 | YES | 37.8735 | 37.8077 | 37.6142 | 37.399 | 37.1767 | 37.0068 | 36.8392 | 36.6738 | 36.4953 | 36.3183 | 35.9696 | 35.1403 | 34.2811 | 33.4244 | 34.244 | 34.1563 | 33.9088 | 33.6362 | 33.3586 | 33.1372 | 32.9136 | 32.6816 | 32.429 | 32.1801 | 31.7919 | 31.1077 | 30.7856 | 30.7751 | 30.4619 | 30.3774 | 30.1388 | 29.8762 | 29.6086 | 29.4141 | 29.3376 | 29.267 | 29.267 | 29.267 | 29.267 | 29.267 | 25.7349 | 24.7231
|  | BASINGSTOKE | CT |  |  | 37.8735 | 37.8077 | 37.6142 | 37.399 | 37.1767 | 37.0068 | 36.8392 | 36.6738 | 36.4953 | 36.3183 | 35.9696 | 35.1403 | 34.2811 | 33.4244 | 34.244 | 34.1563 | 33.9088 | 33.6362 | 33.3586 | 33.1372 | 32.9136 | 32.6816 | 32.429 | 32.1801 | 31.7919 | 31.1077 | 30.7856 | 30.7751 | 30.4619 | 30.3774 | 30.1388 | 29.8762 | 29.6086 | 29.4141 | 29.3376 | 29.267 | 29.267 | 29.267 | 29.267 | 29.267 | 25.7349 | 24.7231
|  | BASINGSTOKE | LW |  |  | 37.8735 | 37.8077 | 37.6142 | 37.399 | 37.1767 | 37.0068 | 36.8392 | 36.6738 | 36.4953 | 36.3183 | 35.9696 | 35.1403 | 34.2811 | 33.4244 | 34.251 | 34.1738 | 33.9465 | 33.6939 | 33.4329 | 33.2335 | 33.0367 | 32.8425 | 32.633 | 32.4252 | 32.0213 | 31.3019 | 30.8368 | 30.7751 | 30.4687 | 30.3943 | 30.1752 | 29.9318 | 29.6803 | 29.4881 | 29.3797 | 29.3133 | 29.267 | 29.267 | 29.267 | 29.267 | 26.0495 | 25.0572
|  | BASINGSTOKE | ST |  |  | 37.8993 | 37.8704 | 37.7851 | 37.6636 | 37.5185 | 37.4223 | 37.325 | 37.223 | 37.1113 | 37.0018 | 36.8027 | 36.2945 | 35.7744 | 35.2532 | 34.2814 | 34.2474 | 34.1473 | 34.0046 | 33.8342 | 33.7213 | 33.607 | 33.4873 | 33.3561 | 33.2276 | 32.9939 | 32.3972 | 31.8464 | 31.389 | 30.4979 | 30.4652 | 30.3687 | 30.2312 | 30.067 | 29.9582 | 29.848 | 29.7327 | 29.6062 | 29.4824 | 29.3651 | 29.267 | 29.267 | 29.267
|  | BASINGSTOKE | FS |  |  | 37.9142 | 37.9101 | 37.8931 | 37.8519 | 37.8044 | 37.7701 | 37.7354 | 37.6915 | 37.6485 | 37.6067 | 37.5249 | 37.3272 | 37.13 | 36.9366 | 34.2988 | 34.294 | 34.274 | 34.2257 | 34.1699 | 34.1296 | 34.0889 | 34.0373 | 33.9869 | 33.9377 | 33.8418 | 33.6096 | 33.3781 | 33.1511 | 30.5148 | 30.5101 | 30.4908 | 30.4443 | 30.3905 | 30.3517 | 30.3124 | 30.2627 | 30.2141 | 30.1668 | 30.0743 | 29.8505 | 29.6274 | 29.4188
NURSLING GSP | VELMORE BSP | BASSETT | MINIMUM HEADROOM | SU 42193 15958 | YES | 31.1586 | 31.1358 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 27.9395 | 27.1213 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 26.3452 | 25.3705 | 24.3932 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 26.56 | 26.2452 | 25.2946 | 24.33 | 23.369
|  | BASSETT | CT |  |  | 31.1586 | 31.1358 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 27.9395 | 27.1213 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 26.3738 | 25.3847 | 24.3932 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 26.56 | 26.2452 | 25.3231 | 24.3439 | 23.369
|  | BASSETT | LW |  |  | 31.1586 | 31.1358 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 27.9395 | 27.1213 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 26.3452 | 25.3705 | 24.402 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 26.5862 | 26.2562 | 25.2946 | 24.33 | 23.3776
|  | BASSETT | ST |  |  | 31.1667 | 31.1552 | 31.1309 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 26.3071 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 26.3506 | 25.801 | 25.2566
|  | BASSETT | FS |  |  | 31.1728 | 31.1711 | 31.1691 | 31.1611 | 31.1516 | 31.1393 | 31.1271 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 31.1225 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.1328 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142 | 29.142
NORTH HYDE GSP | NORTH HYDE (D) | BATH ROAD EAST | MINIMUM HEADROOM | TQ 09097 76885 | NO | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 15.9207 | 15.9164 | 15.9138 | 15.9111 | 15.9082 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 16.2369 | 16.1837 | 16.151 | 16.1167 | 16.0803 | 16.0419 | 16.002 | 15.9611 | 15.9169 | 15.8965 | 15.8965 | 15.8965 | 15.8965 | 15.8965
|  | BATH ROAD EAST | CT |  |  | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 15.9209 | 15.9171 | 15.9146 | 15.912 | 15.909 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 16.2395 | 16.1926 | 16.1614 | 16.1285 | 16.0904 | 16.0476 | 16.0038 | 15.9647 | 15.9208 | 15.8965 | 15.8965 | 15.8965 | 15.8965 | 15.8965
|  | BATH ROAD EAST | LW |  |  | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 15.9207 | 15.9164 | 15.9138 | 15.9111 | 15.9082 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 16.2369 | 16.1837 | 16.151 | 16.1167 | 16.0803 | 16.0419 | 16.002 | 15.9611 | 15.9169 | 15.8965 | 15.8965 | 15.8965 | 15.8965 | 15.8965
|  | BATH ROAD EAST | ST |  |  | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 15.9302 | 15.9202 | 15.9191 | 15.9176 | 15.9155 | 15.9129 | 15.9103 | 15.9079 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 15.9063 | 16.3572 | 16.2314 | 16.2177 | 16.1987 | 16.1727 | 16.1401 | 16.107 | 16.0772 | 16.0437 | 16.0112 | 15.9443 | 15.8965 | 15.8965 | 15.8965
|  | BATH ROAD EAST | FS |  |  | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 15.9318 | 15.9228 | 15.9225 | 15.922 | 15.9213 | 15.9205 | 15.9198 | 15.9188 | 15.9178 | 15.9169 | 15.915 | 15.9107 | 15.9063 | 15.9063 | 16.3772 | 16.2643 | 16.2607 | 16.2534 | 16.2452 | 16.2353 | 16.2257 | 16.2138 | 16.2017 | 16.1898 | 16.1664 | 16.1114 | 16.0445 | 15.9688
IVER 132KV | LONGFORD | BATH ROAD WEST | MINIMUM HEADROOM | TQ 05814 76820 | NO | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 44.5294 | 44.525 | 44.5143 | 44.5024 | 44.4896 | 44.4763 | 44.4627 | 44.449 | 44.4342 | 44.4195 | 44.3897 | 44.3108 | 44.2307 | 44.1511 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548
|  | BATH ROAD WEST | CT |  |  | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 44.5294 | 44.525 | 44.5143 | 44.5024 | 44.4897 | 44.477 | 44.4646 | 44.4521 | 44.438 | 44.4237 | 44.3948 | 44.3229 | 44.2499 | 44.1774 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548
|  | BATH ROAD WEST | LW |  |  | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 44.5294 | 44.525 | 44.5143 | 44.5025 | 44.4896 | 44.4763 | 44.4627 | 44.449 | 44.4342 | 44.4195 | 44.3897 | 44.3108 | 44.2307 | 44.1511 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548
|  | BATH ROAD WEST | ST |  |  | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 44.5312 | 44.5292 | 44.5248 | 44.518 | 44.5094 | 44.4993 | 44.4895 | 44.4796 | 44.4686 | 44.4574 | 44.435 | 44.3798 | 44.3257 | 44.2722 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548
|  | BATH ROAD WEST | FS |  |  | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 50.8856 | 44.5322 | 44.5319 | 44.5316 | 44.5298 | 44.5275 | 44.5246 | 44.5216 | 44.5179 | 44.5141 | 44.5103 | 44.5027 | 44.4836 | 44.465 | 44.4468 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548 | 43.9548
IVER 132KV | UPTON BSP | BEACONSFIELD (END B/B) | MINIMUM HEADROOM | SU 93668 91219 | NO | 6.1976 | 6.1976 | 6.1976 | 6.1733 | 6.1487 | 6.1235 | 6.0974 | 6.0569 | 6.043 | 5.9984 | 5.854 | 6.1733 | 6.043 | 6.1976 | 4.5859 | 4.4949 | 4.3022 | 4.115 | 3.9294 | 3.7806 | 3.7168 | 3.6454 | 3.5863 | 3.3998 | 2.7617 | 4.115 | 3.5863 | 4.5859 | 5.1725 | 5.1674 | 5.1565 | 5.025 | 4.8528 | 4.7044 | 4.6408 | 4.5696 | 4.5106 | 4.3247 | 3.6882 | 5.025 | 4.5106 | 5.1725
|  | BEACONSFIELD (END B/B) | CT |  |  | 6.1976 | 6.1976 | 6.1976 | 6.1973 | 6.1968 | 6.1961 | 6.1951 | 6.193 | 6.1926 | 6.1908 | 6.1067 | 6.1973 | 6.1926 | 6.1976 | 4.5979 | 4.5135 | 4.3349 | 4.1506 | 3.9677 | 3.7806 | 3.7168 | 3.6454 | 3.5863 | 3.3998 | 2.7617 | 4.1506 | 3.5863 | 4.5979 | 5.1732 | 5.1684 | 5.1583 | 5.057 | 4.8872 | 4.7044 | 4.6408 | 4.5696 | 4.5106 | 4.3247 | 3.6882 | 5.057 | 4.5106 | 5.1732
|  | BEACONSFIELD (END B/B) | LW |  |  | 6.1976 | 6.1976 | 6.1976 | 6.1973 | 6.1968 | 6.1961 | 6.1951 | 6.193 | 6.1926 | 6.1908 | 6.1067 | 6.1973 | 6.1926 | 6.1976 | 4.5859 | 4.4949 | 4.3022 | 4.115 | 3.9294 | 3.8776 | 3.8248 | 3.77 | 3.713 | 3.5325 | 2.9695 | 4.115 | 3.713 | 4.5859 | 5.1725 | 5.1674 | 5.1565 | 5.025 | 4.8528 | 4.8012 | 4.7486 | 4.6939 | 4.6371 | 4.4572 | 3.8958 | 5.025 | 4.6371 | 5.1725
|  | BEACONSFIELD (END B/B) | ST |  |  | 6.1976 | 6.1976 | 6.1976 | 6.1733 | 6.1487 | 6.1235 | 6.0974 | 6.0569 | 6.043 | 5.9984 | 5.854 | 6.1733 | 6.043 | 6.1976 | 4.6291 | 4.57 | 4.4688 | 4.3201 | 4.1452 | 4.0705 | 3.9946 | 3.9182 | 3.8657 | 3.6988 | 3.1892 | 4.3201 | 3.8657 | 4.6291 | 5.1749 | 5.1716 | 5.1659 | 5.1347 | 5.0481 | 4.9782 | 4.9061 | 4.8324 | 4.7828 | 4.6223 | 4.1139 | 5.1347 | 4.7828 | 5.1749
|  | BEACONSFIELD (END B/B) | FS |  |  | 6.1976 | 6.1976 | 6.1976 | 6.1866 | 6.1755 | 6.164 | 6.152 | 6.1333 | 6.1309 | 6.123 | 5.9088 | 6.1866 | 6.1309 | 6.1976 | 4.5979 | 4.5135 | 4.3349 | 4.1506 | 3.9677 | 3.7806 | 3.7168 | 3.6454 | 3.5863 | 3.3998 | 2.7617 | 4.1506 | 3.5863 | 4.5979 | 5.1732 | 5.1684 | 5.1583 | 5.057 | 4.8872 | 4.7044 | 4.6408 | 4.5696 | 4.5106 | 4.3247 | 3.6882 | 5.057 | 4.5106 | 5.1732
IVER 132KV | DENHAM | BEACONSFIELD (MIDDLE B/B) | MINIMUM HEADROOM | SU 93668 91219 | NO | 34.3779 | 34.3779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 27.7444 | 27.7231 | 31.9746 | 31.9217 | 31.871 | 31.8206 | 31.7704 | 31.7206 | 31.6669 | 31.6137 | 31.5084 | 31.3973 | 31.2825 | 31.1684 | 27.1883 | 27.1883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883
|  | BEACONSFIELD (MIDDLE B/B) | CT |  |  | 34.3779 | 34.3779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 27.7454 | 27.7259 | 31.9811 | 31.9323 | 31.8854 | 31.8388 | 31.7922 | 31.7457 | 31.6957 | 31.6464 | 31.5492 | 31.4275 | 31.3019 | 31.1776 | 27.1883 | 27.1883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883
|  | BEACONSFIELD (MIDDLE B/B) | LW |  |  | 34.3779 | 34.3779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 27.7444 | 27.7231 | 31.9746 | 31.9217 | 31.871 | 31.8206 | 31.7704 | 31.7206 | 31.6669 | 31.6137 | 31.5084 | 31.3973 | 31.2825 | 31.1684 | 27.1883 | 27.1883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883
|  | BEACONSFIELD (MIDDLE B/B) | ST |  |  | 34.3779 | 34.3779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 27.7517 | 27.7405 | 32.0171 | 31.9821 | 31.9413 | 31.9284 | 31.9155 | 31.9023 | 31.8882 | 31.8744 | 31.8473 | 31.7804 | 31.714 | 31.6479 | 27.1883 | 27.1883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883
|  | BEACONSFIELD (MIDDLE B/B) | FS |  |  | 34.3779 | 34.3779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 39.8779 | 27.7576 | 27.7557 | 32.0536 | 32.0445 | 32.0343 | 32.0297 | 32.025 | 32.0191 | 32.0133 | 32.0075 | 31.9962 | 31.9688 | 31.9424 | 31.9168 | 27.1883 | 27.1883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883 | 31.4883
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM | MINIMUM HEADROOM | SU 58204 69025 | YES | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 12.9303 | 12.8942 | 12.808 | 12.7148 | 12.6224 | 12.531 | 12.4406 | 12.3512 | 12.2547 | 12.1592 | 12.1285 | 12.1196 | 12.1196 | 12.1196 | 12.0957 | 12.0874 | 12.0676 | 12.0461 | 12.0249 | 12.0039 | 11.9957 | 11.9957 | 11.9957 | 11.9957 | 11.9957 | 11.9957 | 9.3773 | 8.9669
|  | BEENHAM | CT |  |  | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 12.9303 | 12.8942 | 12.808 | 12.7148 | 12.6224 | 12.531 | 12.4406 | 12.3512 | 12.2547 | 12.1592 | 12.1285 | 12.1196 | 12.1196 | 12.1196 | 12.0957 | 12.0874 | 12.0676 | 12.0461 | 12.0249 | 12.0039 | 11.9957 | 11.9957 | 11.9957 | 11.9957 | 11.9957 | 11.9957 | 9.3773 | 8.9669
|  | BEENHAM | LW |  |  | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 12.9307 | 12.8952 | 12.8104 | 12.7187 | 12.6279 | 12.538 | 12.449 | 12.3611 | 12.2661 | 12.1719 | 12.1293 | 12.1196 | 12.1196 | 12.1196 | 12.0957 | 12.0876 | 12.0681 | 12.047 | 12.0262 | 12.0055 | 11.9957 | 11.9957 | 11.9957 | 11.9957 | 11.9957 | 11.9957 | 9.438 | 9.0513
|  | BEENHAM | ST |  |  | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 12.9414 | 12.9203 | 12.8742 | 12.8047 | 12.7209 | 12.6743 | 12.6284 | 12.5833 | 12.5345 | 12.4866 | 12.3931 | 12.1609 | 12.1263 | 12.1196 | 12.0982 | 12.0934 | 12.0828 | 12.0668 | 12.0475 | 12.0368 | 12.0263 | 12.0159 | 12.0047 | 11.9957 | 11.9957 | 11.9957 | 11.9957 | 11.9957
|  | BEENHAM | FS |  |  | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 12.9528 | 12.9507 | 12.9482 | 12.933 | 12.915 | 12.8988 | 12.8827 | 12.8621 | 12.8418 | 12.8219 | 12.7832 | 12.6894 | 12.5994 | 12.5141 | 12.1008 | 12.1004 | 12.0998 | 12.0963 | 12.0921 | 12.0884 | 12.0847 | 12.08 | 12.0753 | 12.0708 | 12.0619 | 12.0403 | 12.0196 | 12
MANNINGTON GSP | SALISBURY | BEMERTON | MINIMUM HEADROOM | SU 11583 31233 | YES | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 40.1513 | 40.132 | 40.0992 | 40.0642 | 40.0205 | 39.9833 | 39.9542 | 39.9225 | 39.8867 | 39.8505 | 39.7822 | 39.5349 | 39.2745 | 39.0128 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635
|  | BEMERTON | CT |  |  | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 40.1513 | 40.132 | 40.0992 | 40.0642 | 40.0205 | 39.9833 | 39.9542 | 39.9225 | 39.8867 | 39.8505 | 39.7822 | 39.5349 | 39.2745 | 39.0128 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635
|  | BEMERTON | LW |  |  | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 40.1523 | 40.1336 | 40.1056 | 40.0748 | 40.0352 | 40.0037 | 39.9836 | 39.9619 | 39.9365 | 39.9095 | 39.8514 | 39.5889 | 39.3101 | 39.0271 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635
|  | BEMERTON | ST |  |  | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 40.2464 | 40.1516 | 40.1369 | 40.1197 | 40.0955 | 40.0597 | 40.0294 | 39.9977 | 39.962 | 39.926 | 39.8571 | 39.675 | 39.4927 | 39.3134 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635
|  | BEMERTON | FS |  |  | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 46.0143 | 40.2546 | 40.1642 | 40.1573 | 40.1491 | 40.1394 | 40.127 | 40.1176 | 40.1059 | 40.0937 | 40.0815 | 40.0567 | 39.9936 | 39.9269 | 39.8562 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635 | 39.7635
COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD | MINIMUM HEADROOM | SU 58382 95467 | YES | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 32.6482 | 32.617 | 32.5291 | 32.3837 | 32.1671 | 31.9205 | 31.6793 | 31.4209 | 31.1411 | 30.8505 | 30.5407 | 20.81 | 19.781 | 18.9595 | 32.8999 | 32.8901 | 32.8624 | 32.8166 | 32.7483 | 32.6604 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 21.1758 | 20.1841 | 19.393
|  | BERINSFIELD | CT |  |  | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 32.6482 | 32.617 | 32.5291 | 32.3837 | 32.1671 | 31.9349 | 31.7285 | 31.495 | 31.224 | 30.9177 | 30.5543 | 30.2036 | 30.0671 | 20.5402 | 32.8999 | 32.8901 | 32.8624 | 32.8166 | 32.7483 | 32.6664 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 20.9158
|  | BERINSFIELD | LW |  |  | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 32.6503 | 32.6224 | 32.5416 | 32.3959 | 32.1682 | 31.9205 | 31.6793 | 31.4209 | 31.1411 | 30.8505 | 30.5407 | 20.81 | 19.781 | 18.9595 | 32.9006 | 32.8918 | 32.8663 | 32.8204 | 32.7486 | 32.6604 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 21.1758 | 20.1841 | 19.393
|  | BERINSFIELD | ST |  |  | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 32.6674 | 32.654 | 32.6148 | 32.5353 | 32.4053 | 32.2211 | 32.0286 | 31.863 | 31.669 | 31.446 | 30.9138 | 30.614 | 30.5219 | 30.4397 | 32.906 | 32.9018 | 32.8894 | 32.8644 | 32.8234 | 32.7653 | 32.7046 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567
|  | BERINSFIELD | FS |  |  | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 37.5478 | 32.6792 | 32.672 | 32.6536 | 32.6144 | 32.5556 | 32.4795 | 32.396 | 32.3044 | 32.2019 | 32.0916 | 31.8804 | 31.4693 | 31.2855 | 31.2001 | 32.9097 | 32.9074 | 32.9016 | 32.8893 | 32.8707 | 32.8467 | 32.8204 | 32.7916 | 32.7592 | 32.7245 | 32.6567 | 32.6567 | 32.6567 | 32.6567
NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY | MINIMUM HEADROOM | SU 42648 13187 | YES | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 34.1268 | 34.0496 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 35.5234 | 35.5136 | 35.4944 | 35.4766 | 35.4688 | 35.4612 | 35.4539 | 35.4465 | 35.4385 | 35.4306 | 35.4146 | 35.3523 | 35.2891 | 35.2269
|  | BEVOIS VALLEY | CT |  |  | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 34.1284 | 34.0625 | 33.9288 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 35.5236 | 35.5153 | 35.4984 | 35.4832 | 35.4769 | 35.47 | 35.461 | 35.4507 | 35.4408 | 35.4329 | 35.4189 | 35.3653 | 35.309 | 35.2532
|  | BEVOIS VALLEY | LW |  |  | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 34.1268 | 34.0496 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 35.5234 | 35.5136 | 35.4944 | 35.4766 | 35.4688 | 35.4612 | 35.4539 | 35.4465 | 35.4385 | 35.4306 | 35.4146 | 35.3523 | 35.2891 | 35.2269
|  | BEVOIS VALLEY | ST |  |  | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 34.1344 | 34.0905 | 34.0072 | 33.9233 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 35.5244 | 35.5188 | 35.5083 | 35.4977 | 35.492 | 35.4848 | 35.4763 | 35.4669 | 35.4576 | 35.4497 | 35.4353 | 35.3986 | 35.3613 | 35.3243
|  | BEVOIS VALLEY | FS |  |  | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 37.6772 | 34.1406 | 34.1196 | 34.085 | 34.0511 | 34.0367 | 34.0124 | 33.988 | 33.9592 | 33.9314 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 33.9096 | 35.5252 | 35.5225 | 35.5181 | 35.5138 | 35.512 | 35.5089 | 35.5059 | 35.5022 | 35.4987 | 35.4952 | 35.4885 | 35.4734 | 35.4585 | 35.4439
EAST CLAYDON GSP | BICESTER NORTH | BICESTER | MINIMUM HEADROOM | SP 58381 21988 | YES | 56.7 | 56.7 | 56.7 | 56.3287 | 55.9265 | 55.508 | 55.09 | 54.6563 | 54.1886 | 53.8168 | 53.0595 | 51.3997 | 49.6768 | 47.9571 | 51.4457 | 51.1978 | 50.7801 | 50.3046 | 49.8431 | 49.363 | 48.8832 | 48.3857 | 47.849 | 47.4224 | 46.5534 | 44.6773 | 42.7515 | 40.8291 | 52.973 | 52.7193 | 52.292 | 51.8055 | 51.3335 | 50.8422 | 50.3515 | 49.8424 | 49.2934 | 48.857 | 47.968 | 46.0487 | 44.0785 | 42.1019
|  | BICESTER | CT |  |  | 56.7 | 56.7 | 56.7 | 56.3287 | 55.9265 | 55.508 | 55.09 | 54.6563 | 54.1886 | 53.8168 | 53.0595 | 51.3997 | 49.6768 | 47.9571 | 51.4634 | 51.2555 | 50.9037 | 50.5063 | 50.1178 | 49.7015 | 49.2774 | 48.8281 | 48.3345 | 47.9896 | 47.3031 | 45.6892 | 43.9895 | 42.2901 | 52.9911 | 52.7784 | 52.4185 | 52.012 | 51.6144 | 51.1886 | 50.7547 | 50.295 | 49.7901 | 49.4372 | 48.7349 | 47.0839 | 45.345 | 43.6065
|  | BICESTER | LW |  |  | 56.7 | 56.7 | 56.7 | 56.3287 | 55.9265 | 55.508 | 55.09 | 54.6563 | 54.1886 | 53.8168 | 53.0595 | 51.3997 | 49.6768 | 47.9571 | 51.4457 | 51.1978 | 50.7801 | 50.3046 | 49.8431 | 49.363 | 48.8832 | 48.3857 | 47.849 | 47.4224 | 46.5534 | 44.6773 | 42.7515 | 40.8291 | 52.973 | 52.7193 | 52.292 | 51.8055 | 51.3335 | 50.8422 | 50.3515 | 49.8424 | 49.2934 | 48.857 | 47.968 | 46.0487 | 44.0785 | 42.1019
|  | BICESTER | ST |  |  | 56.7 | 56.7 | 56.7 | 56.7 | 56.4462 | 56.2036 | 55.957 | 55.6964 | 55.406 | 55.2047 | 54.8041 | 53.742 | 52.6762 | 51.6082 | 53.2513 | 51.3682 | 51.1378 | 50.8108 | 50.4394 | 50.1611 | 49.8781 | 49.5791 | 49.2459 | 49.0149 | 48.5553 | 47.3366 | 46.1136 | 44.9104 | 56.3039 | 52.8937 | 52.658 | 52.3234 | 51.9435 | 51.6588 | 51.3693 | 51.0633 | 50.7225 | 50.4862 | 50.0159 | 48.7692 | 47.518 | 46.2872
|  | BICESTER | FS |  |  | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.6982 | 56.5522 | 56.1655 | 55.758 | 55.3476 | 53.318 | 51.5266 | 51.4748 | 51.3728 | 51.2663 | 51.1632 | 51.061 | 50.9398 | 50.8134 | 50.7286 | 50.5611 | 50.1173 | 49.6498 | 49.1789 | 56.3039 | 53.0557 | 53.0027 | 52.8984 | 52.7895 | 52.6839 | 52.5794 | 52.4554 | 52.3261 | 52.2394 | 52.068 | 51.614 | 51.1357 | 50.6539
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST | MINIMUM HEADROOM | TQ 08305 26315 | YES | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 20.1286 | 20.1123 | 20.0736 | 20.0287 | 19.9849 | 19.9451 | 19.908 | 19.8707 | 19.8305 | 19.7845 | 19.6953 | 19.5237 | 19.348 | 19.1751 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493
|  | BILLINGSHURST | CT |  |  | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 20.1286 | 20.1123 | 20.0736 | 20.0287 | 19.9849 | 19.9451 | 19.908 | 19.8707 | 19.8305 | 19.7845 | 19.6953 | 19.5426 | 19.377 | 19.2098 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493
|  | BILLINGSHURST | LW |  |  | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 20.129 | 20.1135 | 20.0766 | 20.0332 | 19.9907 | 19.9529 | 19.9181 | 19.8831 | 19.8453 | 19.7973 | 19.6958 | 19.5237 | 19.348 | 19.1751 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493
|  | BILLINGSHURST | ST |  |  | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 20.1318 | 20.1196 | 20.0928 | 20.0517 | 20.0036 | 19.981 | 19.9602 | 19.9394 | 19.9168 | 19.8903 | 19.828 | 19.6836 | 19.5772 | 19.4721 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493
|  | BILLINGSHURST | FS |  |  | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 21.2226 | 20.1383 | 20.1368 | 20.1343 | 20.1262 | 20.1175 | 20.1102 | 20.1033 | 20.0945 | 20.0857 | 20.0759 | 20.0526 | 19.9905 | 19.9213 | 19.8495 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493 | 20.7493
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM | MINIMUM HEADROOM | SU 97366 01594 | YES | 38.2642 | 38.2638 | 38.2634 | 38.2627 | 38.262 | 38.261 | 38.2599 | 38.2585 | 38.2566 | 38.2544 | 38.249 | 38.2298 | 27.8865 | 26.638 | 34.698 | 34.5496 | 34.3861 | 34.2017 | 34.0762 | 34.0746 | 34.0731 | 34.0715 | 34.0693 | 34.0667 | 34.0608 | 24.1733 | 22.7232 | 21.2851 | 33.0605 | 33.0595 | 33.058 | 33.0562 | 33.0542 | 33.0521 | 33.0498 | 33.0473 | 33.0438 | 33.0399 | 26.4671 | 22.9525 | 21.4779 | 20.0122
|  | BILSHAM | CT |  |  | 38.2642 | 38.2638 | 38.2634 | 38.2627 | 38.262 | 38.261 | 38.2599 | 38.2585 | 38.2566 | 38.2544 | 38.249 | 38.2298 | 27.8865 | 26.638 | 34.703 | 34.5765 | 34.4154 | 34.2562 | 34.0762 | 34.0746 | 34.0731 | 34.0715 | 34.0693 | 34.0667 | 34.0608 | 26.0267 | 24.6623 | 23.3199 | 33.0605 | 33.0595 | 33.058 | 33.0562 | 33.0542 | 33.0521 | 33.0498 | 33.0473 | 33.0438 | 33.0399 | 33.0307 | 24.8198 | 23.4269 | 22.0536
|  | BILSHAM | LW |  |  | 38.2642 | 38.2638 | 38.2634 | 38.2627 | 38.262 | 38.261 | 38.2599 | 38.2585 | 38.2566 | 38.2544 | 38.249 | 38.2298 | 27.8865 | 26.638 | 34.698 | 34.5496 | 34.3861 | 34.2017 | 34.0794 | 34.0789 | 34.0782 | 34.0774 | 34.0763 | 34.0751 | 34.072 | 24.1733 | 22.7232 | 21.2851 | 33.0615 | 33.0612 | 33.0607 | 33.0602 | 33.0595 | 33.0587 | 33.0577 | 33.0565 | 33.0548 | 33.0528 | 26.4671 | 22.9525 | 21.4779 | 20.0122
|  | BILSHAM | ST |  |  | 38.2645 | 38.2644 | 38.2642 | 38.2641 | 38.2638 | 38.2635 | 38.2631 | 38.2627 | 38.2623 | 38.2618 | 38.2607 | 38.2562 | 38.2486 | 38.2375 | 34.8012 | 34.6382 | 34.4903 | 34.3772 | 34.2417 | 34.113 | 34.0801 | 34.0798 | 34.0796 | 34.0793 | 34.0787 | 34.0761 | 34.0718 | 26.0051 | 33.0618 | 33.0617 | 33.0615 | 33.0613 | 33.0611 | 33.0609 | 33.0605 | 33.0602 | 33.0598 | 33.0594 | 33.0584 | 33.0544 | 25.7593 | 24.8078
|  | BILSHAM | FS |  |  | 38.2646 | 38.2645 | 38.2644 | 38.2643 | 38.2641 | 38.264 | 38.2638 | 38.2636 | 38.2635 | 38.2633 | 38.2629 | 38.2613 | 38.2591 | 38.2565 | 34.8249 | 34.7085 | 34.6421 | 34.5425 | 34.4721 | 34.4208 | 34.3661 | 34.3039 | 34.2384 | 34.1683 | 34.0799 | 34.079 | 34.0778 | 34.0763 | 33.0618 | 33.0617 | 33.0617 | 33.0616 | 33.0614 | 33.0613 | 33.0611 | 33.061 | 33.0608 | 33.0607 | 33.0603 | 33.0589 | 33.057 | 33.0547
FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD | MINIMUM HEADROOM | SZ 56409 91399 | YES | 27.038 | 27.0364 | 27.0342 | 27.0314 | 27.028 | 27.0237 | 27.0186 | 27.0126 | 27.0078 | 27.0023 | 26.989 | 26.9416 | 26.8984 | 26.845 | 20.6197 | 20.6095 | 20.5892 | 20.5669 | 20.544 | 20.5206 | 20.4968 | 20.4724 | 20.4486 | 20.424 | 20.3725 | 20.1746 | 19.9674 | 19.7567 | 22.0891 | 22.0812 | 22.0673 | 22.052 | 22.0359 | 22.0191 | 22.0015 | 21.9832 | 21.9666 | 21.9489 | 21.9103 | 21.7697 | 21.6334 | 21.4927
|  | BINSTEAD | CT |  |  | 27.038 | 27.0364 | 27.0342 | 27.0314 | 27.028 | 27.0237 | 27.0186 | 27.0126 | 27.0078 | 27.0023 | 26.989 | 26.9416 | 26.8984 | 26.845 | 20.6197 | 20.6095 | 20.5892 | 20.5669 | 20.544 | 20.5206 | 20.4968 | 20.4724 | 20.4486 | 20.424 | 20.3725 | 20.1746 | 19.9674 | 19.7567 | 22.0891 | 22.0812 | 22.0673 | 22.052 | 22.0359 | 22.0191 | 22.0015 | 21.9832 | 21.9666 | 21.9489 | 21.9103 | 21.7697 | 21.6334 | 21.4927
|  | BINSTEAD | LW |  |  | 27.038 | 27.0364 | 27.0342 | 27.0314 | 27.028 | 27.0237 | 27.0186 | 27.0126 | 27.0078 | 27.0023 | 26.989 | 26.9416 | 26.8984 | 26.845 | 20.6229 | 20.6148 | 20.597 | 20.5773 | 20.557 | 20.5363 | 20.515 | 20.4932 | 20.4705 | 20.4469 | 20.3965 | 20.207 | 19.9965 | 19.7754 | 22.0938 | 22.0893 | 22.0803 | 22.0702 | 22.0593 | 22.0477 | 22.0353 | 22.0221 | 22.0093 | 21.9956 | 21.9654 | 21.8534 | 21.7356 | 21.6063
|  | BINSTEAD | ST |  |  | 27.0396 | 27.039 | 27.0382 | 27.0374 | 27.0363 | 27.0349 | 27.0333 | 27.0315 | 27.0296 | 27.0275 | 27.023 | 27.0108 | 26.9926 | 26.978 | 20.6278 | 20.6261 | 20.6228 | 20.618 | 20.6123 | 20.5882 | 20.5643 | 20.5407 | 20.5151 | 20.4899 | 20.4403 | 20.2893 | 20.126 | 19.9679 | 22.0969 | 22.0958 | 22.0939 | 22.0913 | 22.0882 | 22.0772 | 22.0661 | 22.055 | 22.043 | 22.0311 | 22.0073 | 21.9358 | 21.8551 | 21.7791
|  | BINSTEAD | FS |  |  | 27.0398 | 27.0394 | 27.039 | 27.0384 | 27.0377 | 27.037 | 27.0363 | 27.0355 | 27.0347 | 27.0339 | 27.032 | 27.0251 | 27.0186 | 27.0122 | 20.6284 | 20.6277 | 20.6268 | 20.6234 | 20.6194 | 20.6138 | 20.6083 | 20.6014 | 20.5946 | 20.5878 | 20.5745 | 20.5355 | 20.4898 | 20.4403 | 22.0973 | 22.0967 | 22.0961 | 22.0942 | 22.0921 | 22.0893 | 22.0865 | 22.0831 | 22.0797 | 22.0763 | 22.0695 | 22.0484 | 22.0248 | 21.9997
LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM | MINIMUM HEADROOM | SZ 81965 99422 | YES | 21.5194 | 21.5194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 21.3149 | 21.2725 | 30.6718 | 30.5624 | 30.4608 | 30.4532 | 30.4456 | 30.4359 | 30.4254 | 30.4147 | 30.3927 | 30.3347 | 30.2787 | 30.2229 | 22.1845 | 22.1635 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297
|  | BIRDHAM | CT |  |  | 21.5194 | 21.5194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 21.3194 | 21.2837 | 30.699 | 30.6069 | 30.5156 | 30.4588 | 30.4524 | 30.4442 | 30.4354 | 30.4264 | 30.4073 | 30.3521 | 30.2967 | 30.2416 | 22.1868 | 22.1691 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297
|  | BIRDHAM | LW |  |  | 21.5194 | 21.5194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 21.3149 | 21.2725 | 30.6718 | 30.5624 | 30.4608 | 30.4532 | 30.4456 | 30.4359 | 30.4254 | 30.4147 | 30.3927 | 30.3347 | 30.2787 | 30.2229 | 22.1845 | 22.1635 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297
|  | BIRDHAM | ST |  |  | 21.5194 | 21.5194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 21.3271 | 21.3014 | 30.745 | 30.6601 | 30.5579 | 30.475 | 30.4565 | 30.4496 | 30.442 | 30.4344 | 30.4183 | 30.3803 | 30.3438 | 30.3078 | 22.1906 | 22.1778 | 31.6499 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297
|  | BIRDHAM | FS |  |  | 21.5194 | 21.5194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 31.0194 | 21.3411 | 21.3384 | 30.8352 | 30.8169 | 30.7953 | 30.7705 | 30.7459 | 30.7074 | 30.6685 | 30.6291 | 30.548 | 30.4536 | 30.4403 | 30.4273 | 22.1975 | 22.1962 | 31.6946 | 31.6856 | 31.6748 | 31.6625 | 31.6503 | 31.6313 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297 | 31.6297
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM | MINIMUM HEADROOM | SU 56691 16683 | YES | 33.9774 | 33.949 | 33.8811 | 33.8073 | 33.7346 | 33.6621 | 33.5935 | 33.5257 | 22.3388 | 21.9698 | 21.2373 | 19.9871 | 18.6476 | 17.3178 | 19.4956 | 19.2959 | 18.8171 | 18.2982 | 17.7868 | 17.2768 | 16.7876 | 16.3004 | 15.7752 | 15.2554 | 14.2379 | 12.592 | 10.828 | 9.0749 | 20.7031 | 20.5186 | 20.0762 | 19.5968 | 19.1242 | 18.653 | 18.201 | 17.7509 | 17.2657 | 16.7853 | 15.8453 | 14.3246 | 12.5718 | 10.824
|  | BISHOPS WALTHAM | CT |  |  | 33.9774 | 33.949 | 33.8811 | 33.8073 | 33.7346 | 33.6621 | 33.5935 | 33.5257 | 22.3388 | 21.9698 | 21.2373 | 19.9871 | 18.6476 | 17.3178 | 19.4956 | 19.2959 | 18.8171 | 18.2982 | 17.7868 | 17.2768 | 16.7876 | 16.3004 | 15.7752 | 15.2554 | 14.2379 | 12.592 | 10.828 | 9.0749 | 20.7031 | 20.5186 | 20.0762 | 19.5968 | 19.1242 | 18.653 | 18.201 | 17.7509 | 17.2657 | 16.7853 | 15.8453 | 14.3246 | 12.5718 | 10.824
|  | BISHOPS WALTHAM | LW |  |  | 33.9774 | 33.949 | 33.8811 | 33.8073 | 33.7346 | 33.6621 | 33.5935 | 33.5257 | 22.3388 | 21.9698 | 21.2373 | 19.9871 | 18.6476 | 17.3178 | 19.5077 | 19.3252 | 18.8881 | 18.4134 | 17.9457 | 17.4792 | 17.0375 | 16.6011 | 16.1314 | 15.6563 | 14.7135 | 13.1041 | 11.3799 | 9.6681 | 20.7143 | 20.5457 | 20.1418 | 19.7032 | 19.2711 | 18.84 | 18.432 | 18.0287 | 17.5948 | 17.1558 | 16.2847 | 14.7977 | 13.122 | 11.4154
|  | BISHOPS WALTHAM | ST |  |  | 33.9957 | 33.9752 | 33.9463 | 33.9034 | 33.8525 | 33.822 | 33.7936 | 33.7652 | 33.7345 | 33.7043 | 33.6463 | 22.5387 | 21.7403 | 20.9461 | 19.6256 | 19.4935 | 19.3074 | 19.0318 | 18.7041 | 18.508 | 18.3248 | 18.1421 | 17.9448 | 17.7507 | 17.377 | 16.3887 | 15.361 | 14.3386 | 20.8232 | 20.7011 | 20.5293 | 20.2746 | 19.9718 | 19.7906 | 19.6213 | 19.4525 | 19.2702 | 19.091 | 18.7457 | 17.8325 | 16.883 | 15.9383
|  | BISHOPS WALTHAM | FS |  |  | 34.0025 | 33.9929 | 33.99 | 33.9777 | 33.9634 | 33.9528 | 33.943 | 33.9305 | 33.9182 | 33.9062 | 33.8828 | 33.8242 | 33.7634 | 33.7034 | 19.6692 | 19.6078 | 19.5888 | 19.5095 | 19.4175 | 19.3494 | 19.2865 | 19.2061 | 19.1271 | 19.0496 | 18.8991 | 18.5223 | 18.1308 | 17.7448 | 20.8635 | 20.8068 | 20.7892 | 20.716 | 20.6309 | 20.568 | 20.5099 | 20.4357 | 20.3627 | 20.2911 | 20.152 | 19.8038 | 19.4421 | 19.0854
NURSLING GSP | VELMORE BSP | BISHOPSTOKE | MINIMUM HEADROOM | SU 46463 18472 | YES | 15.9688 | 15.9687 | 15.9684 | 15.9682 | 15.9679 | 15.9677 | 15.9674 | 15.9671 | 15.9668 | 15.9666 | 15.9659 | 15.9633 | 15.9606 | 15.9579 | 16.054 | 16.0528 | 16.05 | 16.0469 | 16.0439 | 16.0409 | 16.0378 | 16.0345 | 16.031 | 16.0275 | 16.0196 | 15.9886 | 15.9561 | 15.9241 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496
|  | BISHOPSTOKE | CT |  |  | 15.9688 | 15.9687 | 15.9684 | 15.9682 | 15.9679 | 15.9677 | 15.9674 | 15.9671 | 15.9668 | 15.9666 | 15.966 | 15.9633 | 15.9606 | 15.9579 | 16.054 | 16.0528 | 16.05 | 16.0469 | 16.0439 | 16.0409 | 16.0379 | 16.0348 | 16.0314 | 16.028 | 16.0211 | 16.0039 | 15.9861 | 15.9686 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496
|  | BISHOPSTOKE | LW |  |  | 15.9688 | 15.9687 | 15.9684 | 15.9682 | 15.9679 | 15.9677 | 15.9674 | 15.9671 | 15.9668 | 15.9666 | 15.966 | 15.9633 | 15.9606 | 15.9579 | 16.054 | 16.0528 | 16.05 | 16.0469 | 16.0439 | 16.0409 | 16.0378 | 16.0345 | 16.031 | 16.0275 | 16.0204 | 15.9886 | 15.9561 | 15.9241 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496
|  | BISHOPSTOKE | ST |  |  | 15.9688 | 15.9688 | 15.9687 | 15.9685 | 15.9683 | 15.968 | 15.9677 | 15.9673 | 15.967 | 15.9666 | 15.9659 | 15.9641 | 15.9624 | 15.9607 | 16.0544 | 16.0539 | 16.0527 | 16.051 | 16.0489 | 16.0449 | 16.0409 | 16.0368 | 16.0325 | 16.0281 | 16.0196 | 15.9984 | 15.9775 | 15.9568 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496
|  | BISHOPSTOKE | FS |  |  | 15.9688 | 15.9688 | 15.9688 | 15.9688 | 15.9687 | 15.9686 | 15.9685 | 15.9684 | 15.9682 | 15.9681 | 15.9678 | 15.9672 | 15.9665 | 15.966 | 16.0547 | 16.0546 | 16.0545 | 16.0541 | 16.0535 | 16.0522 | 16.0509 | 16.0493 | 16.0476 | 16.046 | 16.0427 | 16.0349 | 16.0274 | 16.0203 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496 | 14.8496
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE | MINIMUM HEADROOM | SU 45116 13082 | YES | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 15.467 | 15.4606 | 15.4476 | 15.4291 | 15.4066 | 15.3726 | 15.3388 | 15.3049 | 15.2686 | 15.2328 | 15.1605 | 14.9572 | 14.7492 | 14.546 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692
|  | BITTERNE | CT |  |  | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 15.4684 | 15.4646 | 15.4571 | 15.4499 | 15.4423 | 15.435 | 15.4272 | 15.4187 | 15.4099 | 15.401 | 15.3801 | 15.13 | 14.8615 | 14.5928 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692
|  | BITTERNE | LW |  |  | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 15.4683 | 15.4643 | 15.4565 | 15.4491 | 15.4413 | 15.4339 | 15.4262 | 15.4176 | 15.4086 | 15.3995 | 15.3703 | 15.0639 | 14.758 | 14.546 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692
|  | BITTERNE | ST |  |  | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 15.467 | 15.4606 | 15.4476 | 15.4291 | 15.4066 | 15.3726 | 15.3388 | 15.3049 | 15.2686 | 15.2328 | 15.1605 | 14.9572 | 14.7492 | 14.5746 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692
|  | BITTERNE | FS |  |  | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 17.0068 | 15.4706 | 15.4699 | 15.469 | 15.4677 | 15.4661 | 15.4559 | 15.4458 | 15.4328 | 15.4199 | 15.4073 | 15.383 | 15.3146 | 15.2413 | 15.1674 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692 | 15.692
MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON | MINIMUM HEADROOM | SP 28349 03818 | YES | 18.3832 | 18.3795 | 18.3752 | 18.3706 | 18.366 | 18.3615 | 18.3571 | 18.3526 | 18.3479 | 18.3432 | 18.3311 | 18.314 | 18.314 | 18.314 | 17.2301 | 17.226 | 17.2213 | 17.2162 | 17.2112 | 17.2063 | 17.2013 | 17.1965 | 17.1913 | 17.1861 | 17.1728 | 17.1316 | 17.0881 | 17.064 | 19.7408 | 19.7159 | 19.6871 | 19.656 | 19.6254 | 19.5951 | 19.565 | 19.5353 | 19.5033 | 19.4719 | 19.3903 | 19.1381 | 18.8723 | 18.6223
|  | BLACK BOURTON | CT |  |  | 18.3832 | 18.3795 | 18.3752 | 18.3706 | 18.366 | 18.3615 | 18.3571 | 18.3526 | 18.3479 | 18.3432 | 18.3311 | 18.314 | 18.314 | 18.314 | 17.2303 | 17.2268 | 17.2228 | 17.2184 | 17.2139 | 17.2093 | 17.2045 | 17.2001 | 17.1954 | 17.1908 | 17.1808 | 17.1428 | 17.1007 | 17.064 | 19.7423 | 19.7209 | 19.6961 | 19.6694 | 19.6421 | 19.6136 | 19.5845 | 19.5576 | 19.5285 | 19.5007 | 19.4394 | 19.2069 | 18.9495 | 18.686
|  | BLACK BOURTON | LW |  |  | 18.3832 | 18.3795 | 18.3752 | 18.3706 | 18.366 | 18.3615 | 18.3571 | 18.3526 | 18.3479 | 18.3432 | 18.3311 | 18.314 | 18.314 | 18.314 | 17.2301 | 17.226 | 17.2213 | 17.2162 | 17.2112 | 17.2063 | 17.2013 | 17.1965 | 17.1913 | 17.1861 | 17.1728 | 17.1316 | 17.0881 | 17.064 | 19.7408 | 19.7159 | 19.6871 | 19.656 | 19.6254 | 19.5951 | 19.565 | 19.5353 | 19.5033 | 19.4719 | 19.3903 | 19.1381 | 18.8723 | 18.6223
|  | BLACK BOURTON | ST |  |  | 18.3843 | 18.3821 | 18.3799 | 18.3765 | 18.3724 | 18.3689 | 18.3654 | 18.3621 | 18.3585 | 18.3551 | 18.3477 | 18.3255 | 18.314 | 18.314 | 17.2313 | 17.2289 | 17.2264 | 17.2228 | 17.2183 | 17.2144 | 17.2105 | 17.2069 | 17.2029 | 17.1992 | 17.191 | 17.1666 | 17.1406 | 17.1143 | 19.7483 | 19.7337 | 19.7185 | 19.696 | 19.6685 | 19.6449 | 19.621 | 19.5987 | 19.5747 | 19.5516 | 19.5019 | 19.3525 | 19.1933 | 19.0328
|  | BLACK BOURTON | FS |  |  | 18.3853 | 18.3845 | 18.3843 | 18.3834 | 18.3824 | 18.3813 | 18.3801 | 18.3787 | 18.3772 | 18.3758 | 18.373 | 18.3648 | 18.3554 | 18.3455 | 17.2325 | 17.2315 | 17.2313 | 17.2303 | 17.2293 | 17.228 | 17.2267 | 17.2251 | 17.2235 | 17.222 | 17.2189 | 17.2099 | 17.1995 | 17.1886 | 19.7553 | 19.7496 | 19.748 | 19.7424 | 19.7358 | 19.7279 | 19.7201 | 19.7104 | 19.7007 | 19.6914 | 19.6725 | 19.617 | 19.5535 | 19.487
MANNINGTON GSP | LYTCHETT | BLANDFORD | MINIMUM HEADROOM | ST 88810 05536 | YES | 125.4935 | 125.492 | 125.4901 | 125.4876 | 125.4845 | 125.4807 | 125.4761 | 125.4708 | 125.4643 | 125.4569 | 125.439 | 125.3752 | 125.2795 | 125.1661 | 98.7035 | 98.6837 | 98.6454 | 98.5934 | 98.5362 | 98.4894 | 98.4321 | 98.3728 | 98.3091 | 98.2436 | 98.1371 | 97.7851 | 97.4043 | 97.008 | 108.8265 | 108.8118 | 108.7849 | 108.7516 | 108.715 | 108.6835 | 108.6458 | 108.6061 | 108.5611 | 108.5144 | 108.4315 | 108.1595 | 107.8545 | 107.5215
|  | BLANDFORD | CT |  |  | 125.4935 | 125.492 | 125.4901 | 125.4876 | 125.4845 | 125.4807 | 125.4761 | 125.4708 | 125.4643 | 125.4569 | 125.439 | 125.3752 | 125.2795 | 125.1661 | 98.7035 | 98.6837 | 98.6456 | 98.5971 | 98.5437 | 98.4994 | 98.4455 | 98.3886 | 98.3252 | 98.2602 | 98.152 | 97.7923 | 97.4101 | 97.008 | 108.8265 | 108.8118 | 108.7849 | 108.7516 | 108.715 | 108.6835 | 108.6458 | 108.6061 | 108.5611 | 108.5144 | 108.4315 | 108.1595 | 107.8545 | 107.5215
|  | BLANDFORD | LW |  |  | 125.4935 | 125.492 | 125.4901 | 125.4876 | 125.4845 | 125.4807 | 125.4761 | 125.4708 | 125.4643 | 125.4569 | 125.439 | 125.3752 | 125.2795 | 125.1661 | 98.705 | 98.6848 | 98.6454 | 98.5934 | 98.5362 | 98.4894 | 98.4321 | 98.3728 | 98.3091 | 98.2436 | 98.1371 | 97.7851 | 97.4043 | 97.008 | 108.8299 | 108.817 | 108.7922 | 108.7596 | 108.7236 | 108.6933 | 108.6563 | 108.6176 | 108.5757 | 108.5321 | 108.4576 | 108.209 | 107.9241 | 107.6194
|  | BLANDFORD | ST |  |  | 125.4948 | 125.4943 | 125.4937 | 125.4929 | 125.4919 | 125.4907 | 125.4892 | 125.4876 | 125.4861 | 125.4844 | 125.4807 | 125.4655 | 125.4427 | 125.4137 | 98.7127 | 98.7012 | 98.6802 | 98.646 | 98.6042 | 98.5631 | 98.516 | 98.4675 | 98.414 | 98.3598 | 98.2692 | 98.0501 | 97.8352 | 97.617 | 108.8354 | 108.8282 | 108.8152 | 108.7943 | 108.7687 | 108.7433 | 108.7143 | 108.6843 | 108.6514 | 108.6179 | 108.5615 | 108.4214 | 108.2792 | 108.1313
|  | BLANDFORD | FS |  |  | 125.495 | 125.4947 | 125.4943 | 125.4938 | 125.4932 | 125.4926 | 125.4919 | 125.4912 | 125.4905 | 125.4898 | 125.4881 | 125.4819 | 125.4734 | 125.4639 | 98.7441 | 98.7153 | 98.7108 | 98.6995 | 98.6865 | 98.6719 | 98.655 | 98.635 | 98.6147 | 98.5941 | 98.5589 | 98.4741 | 98.3918 | 98.3091 | 108.8497 | 108.8368 | 108.8339 | 108.8268 | 108.8187 | 108.8096 | 108.7991 | 108.7867 | 108.7741 | 108.7614 | 108.7393 | 108.6848 | 108.6305 | 108.5754
COWLEY GSP | WITNEY BSP | BLEDDINGTON | MINIMUM HEADROOM | SP 25641 22580 | YES | 9.398 | 9.3926 | 9.3798 | 9.3659 | 9.3522 | 9.3385 | 9.325 | 9.3116 | 9.2972 | 9.2829 | 9.2535 | 9.2076 | 9.1598 | 9.1122 | 6.7365 | 6.7064 | 6.6348 | 6.5848 | 6.5472 | 6.5099 | 6.4729 | 6.4364 | 6.3971 | 6.3645 | 6.3645 | 6.3645 | 6.3645 | 4.7596 | 6.8477 | 6.8184 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 4.8645
|  | BLEDDINGTON | CT |  |  | 9.398 | 9.3926 | 9.3798 | 9.3659 | 9.3522 | 9.3385 | 9.325 | 9.3116 | 9.2972 | 9.2829 | 9.2535 | 9.2076 | 9.1598 | 9.1122 | 6.7394 | 6.7137 | 6.6524 | 6.601 | 6.5667 | 6.5348 | 6.5031 | 6.4718 | 6.4382 | 6.4048 | 6.3645 | 6.3645 | 6.3645 | 4.8766 | 6.8506 | 6.8255 | 6.7658 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 4.9781
|  | BLEDDINGTON | LW |  |  | 9.398 | 9.3926 | 9.3798 | 9.3659 | 9.3522 | 9.3385 | 9.325 | 9.3116 | 9.2972 | 9.2829 | 9.2535 | 9.2076 | 9.1598 | 9.1122 | 6.7365 | 6.7064 | 6.6348 | 6.5848 | 6.5472 | 6.5099 | 6.4729 | 6.4364 | 6.3971 | 6.3645 | 6.3645 | 6.3645 | 6.3645 | 4.7596 | 6.8477 | 6.8184 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 4.8645
|  | BLEDDINGTON | ST |  |  | 9.3996 | 9.3963 | 9.3892 | 9.3785 | 9.3656 | 9.3603 | 9.355 | 9.3497 | 9.3441 | 9.3386 | 9.3275 | 9.2981 | 9.2682 | 9.2382 | 6.7453 | 6.7272 | 6.6875 | 6.6277 | 6.584 | 6.5693 | 6.5548 | 6.5406 | 6.5252 | 6.5101 | 6.4799 | 6.3997 | 6.3645 | 6.3645 | 6.8564 | 6.8387 | 6.8 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568 | 6.7568
|  | BLEDDINGTON | FS |  |  | 9.4013 | 9.401 | 9.4006 | 9.3983 | 9.3956 | 9.3938 | 9.3921 | 9.3899 | 9.3878 | 9.3857 | 9.3815 | 9.3707 | 9.3596 | 9.3487 | 6.7553 | 6.7534 | 6.7512 | 6.7383 | 6.7229 | 6.7133 | 6.7036 | 6.6914 | 6.6794 | 6.6676 | 6.6442 | 6.5995 | 6.5675 | 6.5377 | 6.866 | 6.8642 | 6.862 | 6.8495 | 6.8345 | 6.8251 | 6.8157 | 6.8038 | 6.7921 | 6.7806 | 6.7579 | 6.7568 | 6.7568 | 6.7568
BRAMLEY (FLEE) | ALTON | BORDON | MINIMUM HEADROOM | SU 82256 35269 | YES | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 39.3559 | 39.2197 | 39.0009 | 38.7743 | 38.5223 | 38.3038 | 38.1017 | 37.9334 | 37.7683 | 37.6092 | 37.3171 | 37.1429 | 37.1429 | 37.1429 | 39.773 | 39.7079 | 39.6031 | 39.5067 | 39.4222 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148
|  | BORDON | CT |  |  | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 39.3584 | 39.2323 | 39.02 | 38.8016 | 38.558 | 38.3345 | 38.1425 | 37.972 | 37.8122 | 37.6543 | 37.3588 | 37.1429 | 37.1429 | 37.1429 | 39.7742 | 39.7139 | 39.6123 | 39.5159 | 39.4342 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148
|  | BORDON | LW |  |  | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 39.3559 | 39.2197 | 39.0009 | 38.7743 | 38.5223 | 38.3038 | 38.1017 | 37.9334 | 37.7683 | 37.6092 | 37.3171 | 37.1429 | 37.1429 | 37.1429 | 39.773 | 39.7079 | 39.6031 | 39.5067 | 39.4222 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148
|  | BORDON | ST |  |  | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 39.4049 | 39.3323 | 39.2291 | 39.097 | 38.9265 | 38.7342 | 38.5308 | 38.3508 | 38.1954 | 38.0458 | 37.8255 | 37.3594 | 37.1429 | 37.1429 | 39.7965 | 39.7618 | 39.7124 | 39.6492 | 39.5676 | 39.4933 | 39.4251 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148 | 39.4148
|  | BORDON | FS |  |  | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 48.5314 | 39.442 | 39.4108 | 39.384 | 39.3373 | 39.282 | 39.2161 | 39.1463 | 39.0635 | 38.9799 | 38.898 | 38.7447 | 38.4143 | 38.1993 | 38.0042 | 39.8143 | 39.7994 | 39.7865 | 39.7642 | 39.7377 | 39.7062 | 39.6727 | 39.6331 | 39.5931 | 39.5539 | 39.4968 | 39.4148 | 39.4148 | 39.4148
MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN | MINIMUM HEADROOM | SU 17186 41044 | YES | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 29.2482 | 29.2467 | 29.2455 | 29.2443 | 29.2429 | 29.2413 | 29.2397 | 29.2379 | 29.2358 | 29.2333 | 29.2282 | 29.2093 | 26.5341 | 26.115 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 26.3899
|  | BOSCOMBE DOWN | CT |  |  | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 29.2483 | 29.247 | 29.246 | 29.245 | 29.2437 | 29.2422 | 29.2405 | 29.239 | 29.2373 | 29.2356 | 29.232 | 29.2138 | 26.6621 | 26.2854 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 26.5597
|  | BOSCOMBE DOWN | LW |  |  | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 29.2482 | 29.2467 | 29.2455 | 29.2443 | 29.2429 | 29.2413 | 29.2397 | 29.2379 | 29.2359 | 29.2338 | 29.2293 | 29.2093 | 26.5341 | 26.115 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 26.3899
|  | BOSCOMBE DOWN | ST |  |  | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 29.2489 | 29.248 | 29.2474 | 29.2465 | 29.2453 | 29.243 | 29.2406 | 29.2383 | 29.2358 | 29.2333 | 29.2282 | 29.2145 | 29.2007 | 26.5128 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237
|  | BOSCOMBE DOWN | FS |  |  | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 32.2486 | 29.2496 | 29.2491 | 29.249 | 29.2488 | 29.2485 | 29.2478 | 29.2472 | 29.2463 | 29.2454 | 29.2445 | 29.2427 | 29.238 | 29.2331 | 29.228 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237 | 29.5237
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST | MINIMUM HEADROOM | SZ 11636 92447 | YES | 25.5535 | 25.5338 | 25.4858 | 25.4298 | 25.3675 | 25.3012 | 25.2097 | 25.0864 | 24.952 | 24.8186 | 24.5622 | 23.9466 | 23.0683 | 22.1575 | 25.5694 | 25.5443 | 25.4836 | 25.4144 | 25.34 | 25.2626 | 25.1839 | 25.1047 | 24.9844 | 24.8537 | 24.6027 | 23.9962 | 23.0773 | 22.0542 | 25.4194 | 25.3902 | 25.3196 | 25.2393 | 25.153 | 25.063 | 24.9717 | 24.8797 | 24.74 | 24.5882 | 24.2968 | 23.5924 | 22.5982 | 21.5626
|  | BOSCOMBE EAST | CT |  |  | 25.5535 | 25.5338 | 25.4858 | 25.4298 | 25.3675 | 25.3012 | 25.2332 | 25.1643 | 25.0884 | 25.0116 | 24.868 | 23.9845 | 23.0683 | 22.1575 | 25.5694 | 25.5443 | 25.4836 | 25.4144 | 25.34 | 25.2626 | 25.1839 | 25.1047 | 25.0179 | 24.9305 | 24.7649 | 23.9962 | 23.1451 | 22.2362 | 25.4194 | 25.3902 | 25.3196 | 25.2393 | 25.153 | 25.063 | 24.9717 | 24.8797 | 24.7789 | 24.6774 | 24.4851 | 23.5924 | 22.6668 | 21.7468
|  | BOSCOMBE EAST | LW |  |  | 25.5535 | 25.5338 | 25.4858 | 25.4298 | 25.3675 | 25.3012 | 25.2332 | 25.1643 | 25.0884 | 25.0116 | 24.868 | 23.9845 | 23.0683 | 22.1575 | 25.5733 | 25.554 | 25.507 | 25.4522 | 25.3911 | 25.3262 | 25.2596 | 25.1922 | 25.1179 | 25.0427 | 24.9021 | 24.037 | 23.0773 | 22.0542 | 25.4239 | 25.4014 | 25.3469 | 25.2832 | 25.2123 | 25.1369 | 25.0596 | 24.9813 | 24.895 | 24.8077 | 24.6444 | 23.6399 | 22.5982 | 21.5626
|  | BOSCOMBE EAST | ST |  |  | 25.7235 | 25.552 | 25.5319 | 25.5002 | 25.4589 | 25.3341 | 25.2097 | 25.0864 | 24.952 | 24.8186 | 24.5622 | 23.9466 | 23.3323 | 22.7208 | 25.7397 | 25.5718 | 25.5522 | 25.5211 | 25.4807 | 25.3584 | 25.2367 | 25.1159 | 24.9844 | 24.8537 | 24.6027 | 23.9999 | 23.3738 | 22.6869 | 25.6171 | 25.4222 | 25.3993 | 25.3632 | 25.3163 | 25.1743 | 25.0329 | 24.8927 | 24.74 | 24.5882 | 24.2968 | 23.5967 | 22.8983 | 22.203
|  | BOSCOMBE EAST | FS |  |  | 26.499 | 25.5639 | 25.5616 | 25.5522 | 25.5399 | 25.4991 | 25.4584 | 25.4073 | 25.3562 | 25.3055 | 25.208 | 24.9766 | 24.7515 | 24.5345 | 26.499 | 25.5835 | 25.5812 | 25.572 | 25.56 | 25.52 | 25.4802 | 25.4301 | 25.3801 | 25.3304 | 25.235 | 25.0084 | 24.7881 | 24.5755 | 26.4988 | 25.4357 | 25.4331 | 25.4224 | 25.4084 | 25.362 | 25.3157 | 25.2576 | 25.1995 | 25.1418 | 25.031 | 24.7679 | 24.512 | 24.2652
MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY | MINIMUM HEADROOM | SZ 06207 92415 | NO | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 28.1315 | 26.698 | 25.2691 | 31.2295 | 31.1619 | 31.001 | 30.9586 | 26.6662 | 26.4685 | 26.2652 | 26.0593 | 25.8354 | 25.608 | 25.1607 | 23.7871 | 22.3931 | 20.7464 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 26.4257 | 25.2121 | 23.9804 | 22.3703
|  | BOURNE VALLEY | CT |  |  | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 28.1315 | 26.698 | 25.2691 | 31.2295 | 31.1619 | 31.001 | 30.9586 | 26.6662 | 26.4685 | 26.2652 | 26.0593 | 25.8354 | 25.608 | 25.1607 | 23.7871 | 22.3931 | 21.0027 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 26.4257 | 25.2121 | 23.9804 | 22.6277
|  | BOURNE VALLEY | LW |  |  | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 28.1315 | 26.698 | 25.2691 | 31.2457 | 31.2025 | 31.0997 | 30.9779 | 30.9586 | 30.9586 | 26.5831 | 26.4282 | 26.2589 | 26.0846 | 25.7422 | 24.0915 | 22.4162 | 20.7464 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 25.481 | 24.0009 | 22.3703
|  | BOURNE VALLEY | ST |  |  | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 28.1679 | 27.1945 | 26.2302 | 31.4919 | 31.2242 | 31.1561 | 31.0507 | 30.9586 | 30.9586 | 26.5027 | 26.2774 | 26.0318 | 25.7852 | 25.3016 | 24.134 | 22.9965 | 21.8696 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 26.5502 | 25.5186 | 24.5136 | 23.4986
|  | BOURNE VALLEY | FS |  |  | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 35.4895 | 31.5077 | 31.3664 | 31.3587 | 31.331 | 31.2957 | 31.2226 | 31.1489 | 31.0575 | 30.9656 | 30.9586 | 30.9586 | 26.3143 | 25.9058 | 25.5048 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468 | 31.7468
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON | MINIMUM HEADROOM | ST 77363 30262 | YES | 9.331 | 9.323 | 9.3042 | 9.2809 | 9.2512 | 9.217 | 9.1558 | 9.0887 | 9.0163 | 8.944 | 8.797 | 8.4239 | 7.9311 | 7.398 | 9.3009 | 9.2915 | 9.2694 | 9.2419 | 9.2069 | 9.1666 | 9.0945 | 9.0155 | 8.9302 | 8.845 | 8.6719 | 8.2324 | 7.6518 | 7.0238 | 9.33 | 9.3219 | 9.3031 | 9.2797 | 9.2498 | 9.2153 | 9.1538 | 9.0863 | 9.0134 | 8.9407 | 8.7929 | 8.4176 | 7.9218 | 7.3856
|  | BOURTON | CT |  |  | 9.331 | 9.323 | 9.3042 | 9.2809 | 9.2512 | 9.217 | 9.1799 | 9.1413 | 9.0993 | 9.0561 | 8.9637 | 8.4573 | 7.9311 | 7.398 | 9.3011 | 9.2921 | 9.2707 | 9.2446 | 9.2119 | 9.1749 | 9.1349 | 9.0939 | 9.0501 | 9.0056 | 8.91 | 8.3402 | 7.7492 | 7.1535 | 9.3302 | 9.3225 | 9.3042 | 9.2819 | 9.254 | 9.2224 | 9.1882 | 9.1532 | 9.1158 | 9.0779 | 8.9962 | 8.5096 | 8.005 | 7.4964
|  | BOURTON | LW |  |  | 9.331 | 9.323 | 9.3042 | 9.2809 | 9.2512 | 9.217 | 9.1799 | 9.1413 | 9.0993 | 9.0561 | 8.9637 | 8.4573 | 7.9311 | 7.398 | 9.3009 | 9.2915 | 9.2694 | 9.2419 | 9.2069 | 9.1666 | 9.1229 | 9.0774 | 9.0279 | 8.9771 | 8.8682 | 8.2717 | 7.6518 | 7.0238 | 9.33 | 9.3219 | 9.3031 | 9.2797 | 9.2498 | 9.2153 | 9.178 | 9.1391 | 9.0969 | 9.0535 | 8.9605 | 8.4512 | 7.9218 | 7.3856
|  | BOURTON | ST |  |  | 9.4972 | 9.33 | 9.3217 | 9.3083 | 9.2894 | 9.223 | 9.1558 | 9.0887 | 9.0163 | 8.944 | 8.797 | 8.4239 | 8.0546 | 7.6875 | 9.4967 | 9.2998 | 9.2899 | 9.2742 | 9.2519 | 9.1737 | 9.0945 | 9.0155 | 8.9302 | 8.845 | 8.6719 | 8.2324 | 7.7973 | 7.3648 | 9.4972 | 9.329 | 9.3206 | 9.3072 | 9.2881 | 9.2214 | 9.1538 | 9.0863 | 9.0134 | 8.9407 | 8.7929 | 8.4176 | 8.0461 | 7.6768
|  | BOURTON | FS |  |  | 9.499 | 9.3347 | 9.333 | 9.3286 | 9.3224 | 9.3027 | 9.2829 | 9.2585 | 9.234 | 9.2094 | 9.1595 | 9.0333 | 8.9043 | 8.7721 | 9.4988 | 9.3053 | 9.3033 | 9.2981 | 9.2908 | 9.2676 | 9.2442 | 9.2155 | 9.1866 | 9.1577 | 9.0989 | 8.9502 | 8.7982 | 8.6426 | 9.499 | 9.3337 | 9.332 | 9.3276 | 9.3214 | 9.3016 | 9.2816 | 9.2571 | 9.2324 | 9.2077 | 9.1575 | 9.0306 | 8.9008 | 8.7679
MANNINGTON GSP | WAREHAM | BOVINGTON | MINIMUM HEADROOM | SY 83933 87831 | YES | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 20.4014 | 20.399 | 20.3932 | 20.3857 | 20.355 | 20.3195 | 20.2793 | 20.235 | 20.2015 | 20.1853 | 20.1375 | 19.9801 | 19.9096 | 19.8413 | 19.6955 | 19.6948 | 19.6929 | 19.6906 | 19.6809 | 19.6697 | 19.657 | 19.6431 | 19.6325 | 19.6274 | 19.6085 | 19.5767 | 19.5767 | 19.5767
|  | BOVINGTON | CT |  |  | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 20.4015 | 20.3992 | 20.3937 | 20.3867 | 20.3591 | 20.3279 | 20.2953 | 20.259 | 20.229 | 20.2078 | 20.1468 | 20.0618 | 20.0043 | 19.9482 | 19.6955 | 19.6948 | 19.6931 | 19.6909 | 19.6822 | 19.6724 | 19.6621 | 19.6506 | 19.6412 | 19.6345 | 19.6141 | 19.5767 | 19.5767 | 19.5767
|  | BOVINGTON | LW |  |  | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 20.4014 | 20.399 | 20.3932 | 20.3857 | 20.355 | 20.3195 | 20.2793 | 20.235 | 20.2015 | 20.1853 | 20.1375 | 19.9801 | 19.9096 | 19.8413 | 19.6955 | 19.6948 | 19.6929 | 19.6906 | 19.6809 | 19.6697 | 19.657 | 19.6431 | 19.6325 | 19.6274 | 19.6085 | 19.5767 | 19.5767 | 19.5767
|  | BOVINGTON | ST |  |  | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 20.4022 | 20.401 | 20.3983 | 20.394 | 20.3756 | 20.3445 | 20.3127 | 20.2786 | 20.2474 | 20.2222 | 20.1552 | 20.0846 | 20.0384 | 19.9938 | 19.6958 | 19.6954 | 19.6945 | 19.6932 | 19.6874 | 19.6776 | 19.6676 | 19.6568 | 19.647 | 19.639 | 19.6179 | 19.5769 | 19.5767 | 19.5767
|  | BOVINGTON | FS |  |  | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 23.5696 | 20.4028 | 20.4024 | 20.4016 | 20.4001 | 20.3924 | 20.3809 | 20.3688 | 20.3548 | 20.3427 | 20.3342 | 20.3105 | 20.233 | 20.1869 | 20.153 | 19.6959 | 19.6958 | 19.6956 | 19.6951 | 19.6927 | 19.6891 | 19.6853 | 19.6808 | 19.677 | 19.6743 | 19.6669 | 19.6424 | 19.6279 | 19.6172
AMERSHAM | LOUDWATER BSP | BOWERDEAN | MINIMUM HEADROOM | SU 87718 93880 | NO | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 18.9638 | 18.9434 | 18.9073 | 18.8711 | 18.8344 | 18.7973 | 18.7614 | 18.7271 | 18.6905 | 18.6545 | 18.5843 | 18.4216 | 18.2516 | 17.3557 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 17.7616
|  | BOWERDEAN | CT |  |  | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 18.9638 | 18.9434 | 18.9073 | 18.8711 | 18.8344 | 18.7973 | 18.7614 | 18.7271 | 18.6905 | 18.6545 | 18.5843 | 18.4216 | 18.2516 | 17.3557 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 17.7616
|  | BOWERDEAN | LW |  |  | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 18.9644 | 18.9441 | 18.9105 | 18.8771 | 18.8437 | 18.8107 | 18.7802 | 18.7509 | 18.7188 | 18.6868 | 18.6237 | 18.4678 | 18.3044 | 18.0094 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 18.4139
|  | BOWERDEAN | ST |  |  | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 18.9884 | 18.959 | 18.9416 | 18.9186 | 18.8906 | 18.8684 | 18.8471 | 18.8268 | 18.8052 | 18.7842 | 18.7435 | 18.644 | 18.5434 | 18.4435 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367
|  | BOWERDEAN | FS |  |  | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 35.2216 | 18.994 | 18.9901 | 18.9872 | 18.981 | 18.9738 | 18.9661 | 18.959 | 18.9503 | 18.9417 | 18.9333 | 18.9172 | 18.8786 | 18.841 | 18.8053 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367 | 30.2367
BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL | MINIMUM HEADROOM | SU 86075 69397 | NO | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 110.9883 | 110.8711 | 110.6082 | 110.2706 | 109.9594 | 109.6882 | 109.4092 | 109.088 | 109.0176 | 108.9547 | 108.8126 | 108.6461 | 108.5088 | 108.3731 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412
|  | BRACKNELL | CT |  |  | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 110.9993 | 110.9 | 110.6752 | 110.3867 | 110.1217 | 109.8905 | 109.6499 | 109.3613 | 109.0722 | 109.0145 | 108.8856 | 108.7182 | 108.5824 | 108.4498 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412
|  | BRACKNELL | LW |  |  | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 110.9883 | 110.8711 | 110.6082 | 110.2706 | 109.9594 | 109.6882 | 109.4092 | 109.088 | 109.0176 | 108.9547 | 108.8126 | 108.6461 | 108.5088 | 108.3731 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412
|  | BRACKNELL | ST |  |  | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 111.1683 | 110.9796 | 110.8581 | 110.6594 | 110.4484 | 110.3444 | 110.2338 | 110.0909 | 109.9214 | 109.7581 | 109.3712 | 109.0219 | 108.9374 | 108.8556 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412
|  | BRACKNELL | FS |  |  | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 125.539 | 111.2292 | 111.1249 | 111.0314 | 110.9631 | 110.898 | 110.8572 | 110.8134 | 110.7529 | 110.6879 | 110.6248 | 110.4744 | 110.2149 | 110.0221 | 109.844 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412 | 115.412
MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON | MINIMUM HEADROOM | ST 81260 60564 | YES | 31.8334 | 31.8321 | 31.8304 | 31.8281 | 31.8254 | 31.822 | 31.8179 | 31.8131 | 31.8081 | 31.8023 | 31.7884 | 21.5828 | 20.3563 | 19.1392 | 30.9206 | 30.9133 | 30.8983 | 30.8826 | 30.866 | 30.8488 | 30.8309 | 30.8125 | 30.7927 | 30.7722 | 30.7285 | 21.3596 | 19.9225 | 18.4863 | 15.0123 | 14.973 | 14.8449 | 14.7064 | 14.5613 | 14.4125 | 14.2589 | 14.1033 | 13.9334 | 13.7619 | 13.4059 | 11.9945 | 10.5215 | 9.0476
|  | BRADFORD-ON-AVON | CT |  |  | 31.8334 | 31.8321 | 31.8304 | 31.8281 | 31.8254 | 31.822 | 31.8179 | 31.8131 | 31.8081 | 31.8023 | 31.7884 | 21.5828 | 20.3563 | 19.1392 | 30.9206 | 30.9133 | 30.8983 | 30.8826 | 30.866 | 30.8488 | 30.8309 | 30.8125 | 30.7927 | 30.7722 | 30.7285 | 21.3596 | 19.9225 | 18.4863 | 15.0123 | 14.973 | 14.8449 | 14.7064 | 14.5613 | 14.4125 | 14.2589 | 14.1033 | 13.9334 | 13.7619 | 13.4059 | 11.9945 | 10.5215 | 9.0476
|  | BRADFORD-ON-AVON | LW |  |  | 31.8334 | 31.8321 | 31.8304 | 31.8281 | 31.8254 | 31.822 | 31.8179 | 31.8131 | 31.8081 | 31.8023 | 31.7884 | 21.5828 | 20.3563 | 19.1392 | 30.9238 | 30.9196 | 30.9102 | 30.8998 | 30.8884 | 30.876 | 30.8628 | 30.8487 | 30.8331 | 30.8167 | 30.7813 | 21.7277 | 20.3217 | 18.9234 | 15.0192 | 15.0019 | 14.9096 | 14.8083 | 14.6988 | 14.5833 | 14.4621 | 14.3356 | 14.1933 | 14.0469 | 13.7404 | 12.3776 | 10.9356 | 9.5029
|  | BRADFORD-ON-AVON | ST |  |  | 31.8346 | 31.8342 | 31.8336 | 31.8329 | 31.832 | 31.8309 | 31.8296 | 31.8282 | 31.8269 | 31.8255 | 31.8226 | 31.8107 | 21.2695 | 20.5425 | 30.9686 | 30.9234 | 30.9187 | 30.9117 | 30.9028 | 30.8889 | 30.8747 | 30.8605 | 30.8451 | 30.8297 | 30.7985 | 30.7135 | 21.3383 | 20.496 | 15.1942 | 15.0163 | 14.9834 | 14.9103 | 14.8174 | 14.671 | 14.5228 | 14.3746 | 14.2129 | 14.0519 | 13.7256 | 12.8608 | 11.9911 | 11.1311
|  | BRADFORD-ON-AVON | FS |  |  | 31.8348 | 31.8345 | 31.8342 | 31.8337 | 31.8332 | 31.8326 | 31.832 | 31.8314 | 31.8308 | 31.8301 | 31.8286 | 31.8231 | 31.8157 | 31.8076 | 30.9805 | 30.9264 | 30.926 | 30.9243 | 30.9221 | 30.9175 | 30.9129 | 30.907 | 30.9011 | 30.8951 | 30.8831 | 30.851 | 30.8174 | 30.7831 | 15.2409 | 15.0278 | 15.0265 | 15.0204 | 15.0127 | 14.9763 | 14.9288 | 14.8678 | 14.8063 | 14.7447 | 14.6208 | 14.3012 | 13.9746 | 13.6465
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN | MINIMUM HEADROOM | SU 67431 58511 | YES | 18.1397 | 18.1389 | 18.1378 | 18.1363 | 18.1345 | 18.1323 | 18.1296 | 18.1265 | 18.122 | 18.1168 | 18.1042 | 13.7515 | 13.2231 | 12.6599 | 15.7741 | 15.7728 | 15.771 | 15.7688 | 15.7664 | 15.7638 | 15.7611 | 15.7581 | 15.7538 | 13.081 | 12.4576 | 11.9141 | 11.3273 | 10.7157 | 16.863 | 16.8603 | 16.8563 | 16.8516 | 16.8464 | 16.8408 | 16.8349 | 16.8284 | 16.8192 | 13.1848 | 12.5597 | 12.0053 | 11.3988 | 10.758
|  | BRAMLEY GREEN | CT |  |  | 18.1397 | 18.1389 | 18.1378 | 18.1363 | 18.1345 | 18.1323 | 18.1296 | 18.1265 | 18.122 | 18.1168 | 18.1042 | 13.7515 | 13.2231 | 12.6599 | 15.7741 | 15.7728 | 15.771 | 15.7688 | 15.7664 | 15.7638 | 15.7611 | 15.7581 | 15.7538 | 13.277 | 12.6981 | 12.1107 | 11.4618 | 10.7915 | 16.863 | 16.8603 | 16.8563 | 16.8516 | 16.8464 | 16.8408 | 16.8349 | 16.8284 | 16.8192 | 16.8089 | 12.7865 | 12.1774 | 11.4946 | 10.782
|  | BRAMLEY GREEN | LW |  |  | 18.1397 | 18.1389 | 18.1378 | 18.1363 | 18.1345 | 18.1323 | 18.1296 | 18.1265 | 18.122 | 18.1168 | 18.1042 | 13.7515 | 13.2231 | 12.6599 | 15.7752 | 15.7748 | 15.7743 | 15.7737 | 15.7728 | 15.7718 | 15.7706 | 15.7692 | 15.7671 | 13.081 | 12.4576 | 11.9141 | 11.3273 | 10.7157 | 16.8655 | 16.8647 | 16.8636 | 16.8621 | 16.8603 | 16.8581 | 16.8555 | 16.8524 | 16.8479 | 13.1848 | 12.5597 | 12.0053 | 11.3988 | 10.758
|  | BRAMLEY GREEN | ST |  |  | 18.1405 | 18.1402 | 18.1398 | 18.1394 | 18.1388 | 18.1381 | 18.1373 | 18.1363 | 18.1353 | 18.1341 | 18.1317 | 18.121 | 18.1033 | 18.0775 | 15.7756 | 15.7755 | 15.7753 | 15.7751 | 15.7748 | 15.7745 | 15.7741 | 15.7737 | 15.7732 | 15.7727 | 15.7715 | 15.7667 | 15.7586 | 15.7468 | 16.8663 | 16.866 | 16.8656 | 16.8652 | 16.8646 | 16.8639 | 16.8631 | 16.8622 | 16.8611 | 16.86 | 16.8575 | 16.847 | 16.8295 | 16.8039
|  | BRAMLEY GREEN | FS |  |  | 18.1406 | 18.1404 | 18.1402 | 18.1399 | 18.1396 | 18.1392 | 18.1388 | 18.1384 | 18.138 | 18.1376 | 18.1366 | 18.133 | 18.1278 | 18.1219 | 15.7756 | 15.7756 | 15.7755 | 15.7753 | 15.7752 | 15.775 | 15.7748 | 15.7746 | 15.7744 | 15.7742 | 15.7738 | 15.7722 | 15.7698 | 15.7671 | 16.8664 | 16.8662 | 16.866 | 16.8657 | 16.8654 | 16.865 | 16.8646 | 16.8642 | 16.8638 | 16.8634 | 16.8624 | 16.8589 | 16.8537 | 16.8478
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD | MINIMUM HEADROOM | SZ 64712 98665 | NO | 4.6358 | 4.5426 | 4.3482 | 4.1438 | 3.9391 | 3.7343 | 3.5288 | 3.3437 | 3.1444 | 2.947 | 2.5574 | 1.0608 | -0.59491 | -2.2311 | 14.2119 | 14.1186 | 13.9242 | 13.7198 | 13.5151 | 13.3102 | 13.1047 | 12.9195 | 12.7202 | 12.5227 | 12.1175 | 10.3343 | 8.3618 | 6.4124 | 12.2527 | 12.1432 | 11.9151 | 11.6751 | 11.4349 | 11.1945 | 10.9532 | 10.7359 | 10.502 | 10.2702 | 9.813 | 8.0561 | 6.1125 | 4.1918
|  | BRANDON ROAD | CT |  |  | 4.6358 | 4.5426 | 4.3482 | 4.1438 | 3.9391 | 3.7343 | 3.5288 | 3.3437 | 3.1444 | 2.947 | 2.5574 | 1.0608 | -0.59491 | -2.2311 | 14.2214 | 14.1442 | 13.9833 | 13.8152 | 13.6458 | 13.474 | 13.3 | 13.1418 | 12.9717 | 12.8023 | 12.4733 | 10.8461 | 9.0416 | 7.2579 | 12.2639 | 12.1732 | 11.9844 | 11.7872 | 11.5883 | 11.3867 | 11.1825 | 10.9969 | 10.7972 | 10.5983 | 10.2123 | 8.5603 | 6.7824 | 5.0249
|  | BRANDON ROAD | LW |  |  | 4.6358 | 4.5426 | 4.3482 | 4.1438 | 3.9391 | 3.7343 | 3.5288 | 3.3437 | 3.1444 | 2.947 | 2.5574 | 1.0608 | -0.59491 | -2.2311 | 14.2119 | 14.1186 | 13.9242 | 13.7198 | 13.5151 | 13.3102 | 13.1047 | 12.9195 | 12.7202 | 12.5227 | 12.1175 | 10.3343 | 8.3618 | 6.4124 | 12.2527 | 12.1432 | 11.9151 | 11.6751 | 11.4349 | 11.1945 | 10.9532 | 10.7359 | 10.502 | 10.2702 | 9.813 | 8.0561 | 6.1125 | 4.1918
|  | BRANDON ROAD | ST |  |  | 4.7125 | 4.6282 | 4.5492 | 4.4391 | 4.3064 | 4.1094 | 3.9127 | 3.7282 | 3.5295 | 3.3335 | 2.9549 | 2.0216 | 1.0494 | 0.08429 | 14.2886 | 14.2043 | 14.1253 | 14.0152 | 13.8824 | 13.6854 | 13.4886 | 13.3041 | 13.1054 | 12.9093 | 12.5306 | 11.4791 | 10.3208 | 9.171 | 12.3427 | 12.2438 | 12.151 | 12.0218 | 11.866 | 11.6347 | 11.4038 | 11.1873 | 10.9541 | 10.724 | 10.2795 | 9.184 | 8.0427 | 6.9098
|  | BRANDON ROAD | FS |  |  | 4.9317 | 4.7209 | 4.7086 | 4.6722 | 4.6294 | 4.557 | 4.4848 | 4.398 | 4.3125 | 4.2284 | 4.0654 | 3.6841 | 3.3108 | 2.9374 | 14.5079 | 14.297 | 14.2847 | 14.2482 | 14.2055 | 14.133 | 14.0609 | 13.974 | 13.8885 | 13.8044 | 13.6413 | 13.26 | 12.8866 | 12.5131 | 12.6001 | 12.3525 | 12.3382 | 12.2954 | 12.2452 | 12.1602 | 12.0755 | 11.9735 | 11.8731 | 11.7745 | 11.5831 | 11.1355 | 10.6973 | 10.2589
BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD | MINIMUM HEADROOM | SU 88887 80726 | YES | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 22.6314 | 22.572 | 22.4496 | 22.3134 | 22.1734 | 21.8917 | 21.5412 | 21.1784 | 20.7666 | 20.3443 | 19.5397 | 18.512 | 17.5972 | 16.6861 | 13.9565 | 13.831 | 13.5728 | 13.2853 | 12.9898 | 12.6848 | 12.3691 | 12.0424 | 11.6715 | 11.2912 | 10.5666 | 9.6411 | 8.8173 | 7.9969
|  | BRAYWICK ROAD | CT |  |  | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 22.6337 | 22.5804 | 22.4687 | 22.3454 | 22.219 | 22.0283 | 21.7078 | 21.369 | 20.9812 | 20.5766 | 19.7948 | 18.6501 | 17.6945 | 16.7632 | 13.9613 | 13.8487 | 13.6131 | 13.3529 | 13.086 | 12.8078 | 12.5192 | 12.2141 | 11.8647 | 11.5004 | 10.7964 | 9.7656 | 8.905 | 8.0663
|  | BRAYWICK ROAD | LW |  |  | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 22.6314 | 22.572 | 22.4496 | 22.3134 | 22.1734 | 21.8917 | 21.5412 | 21.1784 | 20.7666 | 20.3443 | 19.5397 | 18.512 | 17.5972 | 16.6861 | 13.9565 | 13.831 | 13.5728 | 13.2853 | 12.9898 | 12.6848 | 12.3691 | 12.0424 | 11.6715 | 11.2912 | 10.5666 | 9.6411 | 8.8173 | 7.9969
|  | BRAYWICK ROAD | ST |  |  | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 22.67 | 22.6238 | 22.5749 | 22.5065 | 22.4252 | 22.3583 | 22.288 | 22.2124 | 22.1125 | 21.8886 | 21.4526 | 20.7377 | 20.1882 | 19.6541 | 14.0379 | 13.9403 | 13.8372 | 13.6928 | 13.5212 | 13.38 | 13.2316 | 13.0721 | 12.8836 | 12.6819 | 12.2893 | 11.6455 | 11.1506 | 10.6697
|  | BRAYWICK ROAD | FS |  |  | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 80.9607 | 22.6789 | 22.6498 | 22.6378 | 22.611 | 22.5801 | 22.5535 | 22.526 | 22.4932 | 22.4569 | 22.4188 | 22.3454 | 22.2184 | 22.1037 | 21.8953 | 14.0567 | 13.9953 | 13.9699 | 13.9133 | 13.8482 | 13.7921 | 13.7339 | 13.6648 | 13.5882 | 13.5077 | 13.3529 | 13.0847 | 12.8757 | 12.6879
EALING GSP | EALING (D) | BRENTFORD | MINIMUM HEADROOM | TQ 17659 78277 | YES | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 52.0501 | 51.5851 | 50.985 | 50.6895 | 50.5696 | 50.528 | 50.4859 | 50.4402 | 50.3897 | 50.3453 | 50.2591 | 50.2039 | 50.2039 | 50.2039 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976
|  | BRENTFORD | CT |  |  | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 52.0601 | 51.6416 | 51.0713 | 50.7204 | 50.601 | 50.5364 | 50.4881 | 50.4402 | 50.3897 | 50.3453 | 50.2591 | 50.2039 | 50.2039 | 50.2039 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976
|  | BRENTFORD | LW |  |  | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 52.0501 | 51.5851 | 50.985 | 50.6895 | 50.5696 | 50.528 | 50.4859 | 50.4431 | 50.3965 | 50.354 | 50.27 | 50.2039 | 50.2039 | 50.2039 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976
|  | BRENTFORD | ST |  |  | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 52.1887 | 51.9504 | 51.6989 | 51.4238 | 51.1659 | 50.9089 | 50.7451 | 50.671 | 50.5928 | 50.5549 | 50.5109 | 50.4145 | 50.3153 | 50.2161 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976
|  | BRENTFORD | FS |  |  | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 57.9113 | 52.2753 | 52.1521 | 52.0627 | 51.9401 | 51.8358 | 51.7329 | 51.6313 | 51.5095 | 51.3861 | 51.2735 | 51.0545 | 50.7417 | 50.6262 | 50.5495 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976 | 52.8976
LOVEDEAN GSP | HAVANT | BROCKHAMPTON | MINIMUM HEADROOM | SU 70868 05828 | NO | 139.9663 | 139.9655 | 139.9643 | 139.9628 | 139.9609 | 139.9586 | 139.9558 | 139.9525 | 139.948 | 139.9428 | 139.9304 | 139.8858 | 139.8123 | 139.706 | 24.407 | 24.3897 | 24.348 | 24.3011 | 24.2534 | 24.205 | 24.1553 | 24.1064 | 24.0517 | 23.9963 | 23.8781 | 23.4345 | 22.9313 | 22.407 | 23.1913 | 23.1736 | 23.1318 | 23.0848 | 23.0368 | 22.988 | 22.9379 | 22.8883 | 22.8323 | 22.7754 | 22.6533 | 22.1972 | 21.6709 | 21.1155
|  | BROCKHAMPTON | CT |  |  | 139.9663 | 139.9655 | 139.9643 | 139.9628 | 139.9609 | 139.9586 | 139.9558 | 139.9525 | 139.948 | 139.9428 | 139.9304 | 139.8858 | 139.8123 | 139.706 | 24.407 | 24.3897 | 24.348 | 24.3011 | 24.2534 | 24.205 | 24.1553 | 24.1064 | 24.0517 | 23.9963 | 23.8781 | 23.4345 | 22.9313 | 22.407 | 23.1913 | 23.1736 | 23.1318 | 23.0848 | 23.0368 | 22.988 | 22.9379 | 22.8883 | 22.8323 | 22.7754 | 22.6533 | 22.1972 | 21.6709 | 21.1155
|  | BROCKHAMPTON | LW |  |  | 139.9663 | 139.9655 | 139.9643 | 139.9628 | 139.9609 | 139.9586 | 139.9558 | 139.9525 | 139.948 | 139.9428 | 139.9304 | 139.8858 | 139.8123 | 139.706 | 24.4103 | 24.3962 | 24.3609 | 24.3211 | 24.2803 | 24.2387 | 24.196 | 24.1534 | 24.1049 | 24.055 | 23.9463 | 23.5095 | 23.0272 | 22.5224 | 23.1953 | 23.1814 | 23.1467 | 23.1076 | 23.0674 | 23.0263 | 22.984 | 22.9416 | 22.8932 | 22.8431 | 22.7338 | 22.2961 | 21.8054 | 21.2827
|  | BROCKHAMPTON | ST |  |  | 139.9672 | 139.9669 | 139.9665 | 139.966 | 139.9654 | 139.9646 | 139.9638 | 139.9628 | 139.9617 | 139.9605 | 139.9579 | 139.9473 | 139.9297 | 139.9048 | 24.638 | 24.4172 | 24.4129 | 24.4056 | 24.396 | 24.3564 | 24.3163 | 24.2771 | 24.2345 | 24.1922 | 24.105 | 23.8441 | 23.5694 | 23.2921 | 23.4166 | 23.2021 | 23.1978 | 23.1906 | 23.1812 | 23.1425 | 23.1033 | 23.0649 | 23.0232 | 22.9818 | 22.8963 | 22.6398 | 22.3678 | 22.0909
|  | BROCKHAMPTON | FS |  |  | 139.9673 | 139.9671 | 139.9669 | 139.9665 | 139.9662 | 139.9658 | 139.9654 | 139.965 | 139.9646 | 139.9641 | 139.9631 | 139.9593 | 139.954 | 139.9482 | 24.6383 | 24.6378 | 24.6371 | 24.6313 | 24.6243 | 24.6122 | 24.6 | 24.5841 | 24.5684 | 24.5528 | 24.521 | 24.4281 | 24.327 | 24.2242 | 23.417 | 23.4164 | 23.4156 | 23.4099 | 23.403 | 23.3911 | 23.3791 | 23.3636 | 23.3482 | 23.3329 | 23.3017 | 23.2104 | 23.1106 | 23.009
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST | MINIMUM HEADROOM | SU 59381 02061 | NO | 35.114 | 35.111 | 35.1055 | 35.0985 | 35.0906 | 35.0819 | 35.0769 | 35.0659 | 35.0529 | 35.039 | 35.0107 | 34.9614 | 34.9614 | 34.9614 | 31.6048 | 31.599 | 31.5881 | 31.5743 | 31.5587 | 31.5416 | 31.5317 | 31.5102 | 31.4846 | 31.4572 | 31.4013 | 31.3126 | 31.3126 | 31.3126 | 32.428 | 32.4223 | 32.4118 | 32.3984 | 32.3833 | 32.3667 | 32.3572 | 32.3363 | 32.3115 | 32.285 | 32.2309 | 32.1156 | 32.1148 | 32.1148
|  | BROCKHURST | CT |  |  | 35.114 | 35.111 | 35.1055 | 35.0985 | 35.0906 | 35.0819 | 35.0769 | 35.0724 | 35.0664 | 35.0591 | 35.042 | 34.9614 | 34.9614 | 34.9614 | 31.605 | 31.5998 | 31.5897 | 31.5772 | 31.5631 | 31.5474 | 31.5378 | 31.5279 | 31.5147 | 31.4987 | 31.4648 | 31.3443 | 31.3126 | 31.3126 | 32.4281 | 32.4231 | 32.4133 | 32.4013 | 32.3876 | 32.3724 | 32.363 | 32.3534 | 32.3407 | 32.3252 | 32.2923 | 32.1757 | 32.1148 | 32.1148
|  | BROCKHURST | LW |  |  | 35.114 | 35.111 | 35.1055 | 35.0985 | 35.0906 | 35.0819 | 35.0769 | 35.0724 | 35.0664 | 35.0591 | 35.042 | 34.9614 | 34.9614 | 34.9614 | 31.6048 | 31.599 | 31.5881 | 31.5743 | 31.5587 | 31.5416 | 31.5317 | 31.5228 | 31.5112 | 31.4968 | 31.463 | 31.3126 | 31.3126 | 31.3126 | 32.428 | 32.4223 | 32.4118 | 32.3984 | 32.3833 | 32.3667 | 32.3572 | 32.3486 | 32.3373 | 32.3233 | 32.2906 | 32.116 | 32.1148 | 32.1148
|  | BROCKHURST | ST |  |  | 35.1266 | 35.1133 | 35.1105 | 35.1065 | 35.1018 | 35.0884 | 35.0771 | 35.0659 | 35.0529 | 35.039 | 35.0107 | 34.9614 | 34.9614 | 34.9614 | 31.6297 | 31.6034 | 31.5979 | 31.5902 | 31.5808 | 31.5544 | 31.5322 | 31.5102 | 31.4846 | 31.4572 | 31.4013 | 31.3126 | 31.3126 | 31.3126 | 32.452 | 32.4266 | 32.4213 | 32.4138 | 32.4047 | 32.3791 | 32.3577 | 32.3363 | 32.3115 | 32.285 | 32.2309 | 32.1156 | 32.1148 | 32.1148
|  | BROCKHURST | FS |  |  | 35.1273 | 35.1147 | 35.1136 | 35.1119 | 35.1099 | 35.1059 | 35.1027 | 35.0989 | 35.0949 | 35.0905 | 35.0815 | 35.0582 | 35.0397 | 35.0233 | 31.631 | 31.6063 | 31.6041 | 31.6007 | 31.5969 | 31.5889 | 31.5826 | 31.5752 | 31.5672 | 31.5586 | 31.5408 | 31.4949 | 31.4586 | 31.4262 | 32.4533 | 32.4294 | 32.4272 | 32.424 | 32.4203 | 32.4125 | 32.4065 | 32.3993 | 32.3915 | 32.3832 | 32.366 | 32.3215 | 32.2863 | 32.255
MELKSHAM GSP | NORRINGTON | BROMHAM | MINIMUM HEADROOM | ST 98670 65994 | YES | -2.4201 | -2.4374 | -2.4786 | -2.5233 | -2.5684 | -2.6136 | -2.659 | -2.7046 | -2.7543 | -2.8041 | -2.9038 | -3.1338 | -3.3723 | -3.609 | -14.8352 | -14.8569 | -14.9087 | -14.9649 | -15.0215 | -15.0784 | -15.1355 | -15.1927 | -15.2552 | -15.3178 | -15.4431 | -15.7322 | -16.032 | -16.3295 | -22.7711 | -22.7924 | -22.8431 | -22.898 | -22.9534 | -23.009 | -23.0648 | -23.1208 | -23.1819 | -23.2431 | -23.3656 | -23.6483 | -23.9415 | -24.2324
|  | BROMHAM | CT |  |  | -2.4201 | -2.4374 | -2.4786 | -2.5233 | -2.5684 | -2.6136 | -2.659 | -2.7046 | -2.7543 | -2.8041 | -2.9038 | -3.1338 | -3.3723 | -3.609 | -14.8323 | -14.8498 | -14.8914 | -14.9365 | -14.9821 | -15.0279 | -15.0738 | -15.1197 | -15.1696 | -15.2192 | -15.3189 | -15.6129 | -15.9169 | -16.2173 | -22.7683 | -22.7854 | -22.8261 | -22.8702 | -22.9148 | -22.9595 | -23.0045 | -23.0494 | -23.0981 | -23.1466 | -23.2442 | -23.5316 | -23.8289 | -24.1227
|  | BROMHAM | LW |  |  | -2.4201 | -2.4374 | -2.4786 | -2.5233 | -2.5684 | -2.6136 | -2.659 | -2.7046 | -2.7543 | -2.8041 | -2.9038 | -3.1338 | -3.3723 | -3.609 | -14.8352 | -14.8569 | -14.9087 | -14.9649 | -15.0215 | -15.0784 | -15.1355 | -15.1927 | -15.2552 | -15.3178 | -15.4431 | -15.7322 | -16.032 | -16.3295 | -22.7711 | -22.7924 | -22.8431 | -22.898 | -22.9534 | -23.009 | -23.0648 | -23.1208 | -23.1819 | -23.2431 | -23.3656 | -23.6483 | -23.9415 | -24.2324
|  | BROMHAM | ST |  |  | -2.4153 | -2.4263 | -2.4503 | -2.4865 | -2.5305 | -2.5578 | -2.5851 | -2.6121 | -2.6415 | -2.6707 | -2.7287 | -2.877 | -3.0245 | -3.1704 | -14.8291 | -14.8429 | -14.8731 | -14.9186 | -14.9739 | -15.0082 | -15.0425 | -15.0765 | -15.1135 | -15.1501 | -15.2231 | -15.4094 | -15.5948 | -15.7782 | -22.7652 | -22.7787 | -22.8082 | -22.8527 | -22.9068 | -22.9403 | -22.9739 | -23.0071 | -23.0433 | -23.0791 | -23.1505 | -23.3327 | -23.514 | -23.6933
|  | BROMHAM | FS |  |  | -2.4093 | -2.4104 | -2.4116 | -2.4192 | -2.4282 | -2.4372 | -2.4463 | -2.4579 | -2.4695 | -2.4809 | -2.5036 | -2.56 | -2.6154 | -2.6694 | -14.8216 | -14.8229 | -14.8245 | -14.834 | -14.8453 | -14.8567 | -14.8681 | -14.8826 | -14.8972 | -14.9116 | -14.9401 | -15.011 | -15.0807 | -15.1485 | -22.7578 | -22.7591 | -22.7607 | -22.7699 | -22.7811 | -22.7922 | -22.8033 | -22.8175 | -22.8318 | -22.8459 | -22.8738 | -22.943 | -23.0112 | -23.0775
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET | MINIMUM HEADROOM | SU 63480 52228 | YES | 35.7778 | 35.7516 | 35.6893 | 35.6218 | 35.555 | 35.4889 | 35.3628 | 35.2785 | 35.2518 | 35.2305 | 35.2035 | 35.1309 | 35.0608 | 35.0608 | 34.2927 | 34.2586 | 34.1773 | 34.0893 | 34.0021 | 33.9159 | 33.7629 | 33.5915 | 33.4051 | 33.2564 | 33.068 | 32.5469 | 32.0366 | 31.8318 | 34.0681 | 34.0351 | 33.9564 | 33.8712 | 33.7869 | 33.7034 | 33.5555 | 33.4173 | 33.2937 | 33.1951 | 33.0915 | 32.8295 | 32.6035 | 32.5387
|  | BROOK STREET | CT |  |  | 35.7778 | 35.7516 | 35.6893 | 35.6218 | 35.555 | 35.4889 | 35.3628 | 35.2785 | 35.2518 | 35.2305 | 35.2035 | 35.1309 | 35.0608 | 35.0608 | 34.2927 | 34.2586 | 34.1773 | 34.0893 | 34.0021 | 33.9159 | 33.7674 | 33.6103 | 33.4392 | 33.294 | 33.0829 | 32.5469 | 32.0366 | 31.8318 | 34.0681 | 34.0351 | 33.9564 | 33.8712 | 33.7869 | 33.7034 | 33.5598 | 33.4297 | 33.3162 | 33.22 | 33.0996 | 32.8295 | 32.6035 | 32.5387
|  | BROOK STREET | LW |  |  | 35.7778 | 35.7516 | 35.6893 | 35.6218 | 35.555 | 35.4889 | 35.3628 | 35.2785 | 35.2518 | 35.2305 | 35.2035 | 35.1309 | 35.0608 | 35.0608 | 34.2932 | 34.2598 | 34.1802 | 34.0939 | 34.0086 | 33.9241 | 33.7629 | 33.5915 | 33.4051 | 33.2564 | 33.068 | 32.5609 | 32.0509 | 31.8318 | 34.0685 | 34.0362 | 33.9592 | 33.8757 | 33.7931 | 33.7114 | 33.5555 | 33.4173 | 33.2937 | 33.1951 | 33.0915 | 32.8357 | 32.6098 | 32.5387
|  | BROOK STREET | ST |  |  | 35.7891 | 35.7793 | 35.7578 | 35.7255 | 35.6868 | 35.6462 | 35.5734 | 35.4961 | 35.4105 | 35.3385 | 35.2802 | 35.2342 | 35.1927 | 35.1516 | 34.3077 | 34.2951 | 34.2677 | 34.2265 | 34.1769 | 34.1251 | 34.032 | 33.9333 | 33.8239 | 33.7319 | 33.6037 | 33.2821 | 32.9925 | 32.7059 | 34.0826 | 34.0704 | 34.0439 | 34.004 | 33.9561 | 33.9059 | 33.8158 | 33.7203 | 33.6145 | 33.5254 | 33.4253 | 33.2121 | 33.0499 | 32.8999
|  | BROOK STREET | FS |  |  | 35.7939 | 35.7923 | 35.7903 | 35.7792 | 35.7661 | 35.7512 | 35.7225 | 35.6884 | 35.6526 | 35.6221 | 35.579 | 35.4738 | 35.3805 | 35.2903 | 34.3139 | 34.3118 | 34.3092 | 34.295 | 34.2783 | 34.2592 | 34.2226 | 34.179 | 34.1332 | 34.0943 | 34.0392 | 33.9047 | 33.7856 | 33.6703 | 34.0885 | 34.0865 | 34.084 | 34.0703 | 34.0541 | 34.0357 | 34.0002 | 33.9581 | 33.9137 | 33.8761 | 33.8228 | 33.6927 | 33.5774 | 33.4695
MELKSHAM GSP | FROME BSP | BRUTON | MINIMUM HEADROOM | ST 69094 35148 | YES | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 16.3618 | 16.3444 | 16.3029 | 16.2579 | 16.2132 | 16.1689 | 16.125 | 16.0814 | 16.0345 | 16.0104 | 15.9956 | 15.96 | 15.9229 | 15.8862 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733
|  | BRUTON | CT |  |  | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 16.3634 | 16.3484 | 16.3126 | 16.2738 | 16.2352 | 16.1968 | 16.1589 | 16.1211 | 16.0805 | 16.0402 | 16.0059 | 15.9706 | 15.9328 | 15.8953 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733
|  | BRUTON | LW |  |  | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 16.3618 | 16.3444 | 16.3029 | 16.2579 | 16.2132 | 16.1689 | 16.125 | 16.0814 | 16.0345 | 16.0104 | 15.9956 | 15.96 | 15.9229 | 15.8862 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733
|  | BRUTON | ST |  |  | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 16.3714 | 16.3682 | 16.3613 | 16.3508 | 16.3381 | 16.3109 | 16.2839 | 16.2574 | 16.2287 | 16.2005 | 16.1454 | 16.0126 | 15.9887 | 15.965 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733
|  | BRUTON | FS |  |  | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 20.002 | 16.3725 | 16.3715 | 16.3702 | 16.3628 | 16.3541 | 16.3456 | 16.3372 | 16.3264 | 16.3157 | 16.3052 | 16.2848 | 16.2333 | 16.1809 | 16.1295 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733 | 16.3733
COWLEY GSP | WITNEY BSP | BURFORD | MINIMUM HEADROOM | SP 25671 12529 | YES | 16.9487 | 16.9469 | 16.9461 | 16.9452 | 16.9444 | 16.9435 | 16.9427 | 16.9419 | 16.941 | 16.9401 | 16.9379 | 16.9291 | 16.9198 | 16.9105 | 14.7492 | 14.728 | 14.7175 | 14.7066 | 14.6963 | 14.6861 | 14.6736 | 14.6625 | 14.6505 | 14.6397 | 14.6167 | 14.493 | 14.3611 | 14.2378 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627
|  | BURFORD | CT |  |  | 16.9487 | 16.9469 | 16.9461 | 16.9452 | 16.9444 | 16.9435 | 16.9427 | 16.9419 | 16.941 | 16.9401 | 16.9379 | 16.9291 | 16.9198 | 16.9105 | 14.75 | 14.7315 | 14.7215 | 14.7114 | 14.7003 | 14.6875 | 14.6736 | 14.6625 | 14.6505 | 14.6397 | 14.6167 | 14.493 | 14.3611 | 14.2378 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627
|  | BURFORD | LW |  |  | 16.9487 | 16.9469 | 16.9461 | 16.9452 | 16.9444 | 16.9435 | 16.9427 | 16.9419 | 16.941 | 16.9401 | 16.9379 | 16.9291 | 16.9198 | 16.9105 | 14.7492 | 14.728 | 14.7175 | 14.7066 | 14.6963 | 14.6861 | 14.6759 | 14.6658 | 14.6549 | 14.6441 | 14.6178 | 14.5095 | 14.3963 | 14.2825 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627
|  | BURFORD | ST |  |  | 16.9493 | 16.9484 | 16.948 | 16.9475 | 16.9469 | 16.9458 | 16.9447 | 16.9437 | 16.9427 | 16.9417 | 16.9397 | 16.9343 | 16.9286 | 16.923 | 14.7572 | 14.7451 | 14.7408 | 14.735 | 14.7273 | 14.7141 | 14.7004 | 14.6885 | 14.6757 | 14.6639 | 14.6396 | 14.573 | 14.5039 | 14.4347 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627
|  | BURFORD | FS |  |  | 16.9499 | 16.9493 | 16.9492 | 16.949 | 16.9488 | 16.9485 | 16.9481 | 16.9477 | 16.9473 | 16.9469 | 16.9461 | 16.9441 | 16.9419 | 16.9398 | 14.7637 | 14.7568 | 14.7558 | 14.7534 | 14.7509 | 14.7465 | 14.7424 | 14.7373 | 14.7321 | 14.7272 | 14.7177 | 14.6929 | 14.6665 | 14.6399 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627 | 16.0627
MANNINGTON GSP | WAREHAM | BUSHEY | MINIMUM HEADROOM | SY 97671 83532 | YES | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 38.3527 | 38.3514 | 38.3481 | 38.3445 | 38.3408 | 38.337 | 38.3332 | 38.3294 | 38.3253 | 38.3212 | 38.313 | 38.2869 | 38.2603 | 38.2341 | 44.5717 | 44.5713 | 44.5701 | 44.5689 | 44.5676 | 44.5663 | 44.565 | 44.5636 | 44.5622 | 44.5608 | 44.5579 | 44.5488 | 44.5396 | 44.5305
|  | BUSHEY | CT |  |  | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 38.3527 | 38.3514 | 38.3482 | 38.3446 | 38.3409 | 38.3372 | 38.3335 | 38.3297 | 38.3257 | 38.3216 | 38.3136 | 38.2936 | 38.2733 | 38.2533 | 44.5717 | 44.5713 | 44.5701 | 44.5689 | 44.5676 | 44.5663 | 44.565 | 44.5637 | 44.5623 | 44.5609 | 44.5581 | 44.5512 | 44.5441 | 44.5371
|  | BUSHEY | LW |  |  | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 38.3527 | 38.3514 | 38.3481 | 38.3445 | 38.3408 | 38.337 | 38.3332 | 38.3294 | 38.3253 | 38.3212 | 38.313 | 38.2869 | 38.2603 | 38.2341 | 44.5717 | 44.5713 | 44.5701 | 44.5689 | 44.5676 | 44.5663 | 44.565 | 44.5636 | 44.5622 | 44.5608 | 44.5579 | 44.5488 | 44.5396 | 44.5305
|  | BUSHEY | ST |  |  | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 38.3533 | 38.3527 | 38.3513 | 38.3493 | 38.3467 | 38.3434 | 38.34 | 38.3367 | 38.3331 | 38.3296 | 38.3226 | 38.3054 | 38.2886 | 38.272 | 44.5719 | 44.5717 | 44.5712 | 44.5705 | 44.5697 | 44.5685 | 44.5673 | 44.5662 | 44.5649 | 44.5637 | 44.5612 | 44.5553 | 44.5494 | 44.5437
|  | BUSHEY | FS |  |  | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 50.9924 | 38.3917 | 38.3535 | 38.3534 | 38.3528 | 38.3521 | 38.351 | 38.3499 | 38.3485 | 38.3472 | 38.3458 | 38.3432 | 38.3368 | 38.3306 | 38.3248 | 44.5853 | 44.572 | 44.572 | 44.5718 | 44.5715 | 44.5711 | 44.5707 | 44.5703 | 44.5698 | 44.5693 | 44.5684 | 44.5662 | 44.5641 | 44.562
FAWLEY GSP | LANGLEY BSP | BUTTS ASH | MINIMUM HEADROOM | SU 41923 05772 | YES | 35.0524 | 35.0497 | 35.0431 | 35.0358 | 35.0286 | 35.0213 | 35.0068 | 34.9924 | 34.9768 | 34.9614 | 34.9313 | 34.8507 | 34.7508 | 34.7325 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.1807 | 39.1772 | 39.1689 | 39.1597 | 39.1505 | 39.1413 | 39.1229 | 39.1046 | 39.0848 | 39.0653 | 39.0271 | 38.925 | 38.7983 | 38.6368
|  | BUTTS ASH | CT |  |  | 35.0524 | 35.0497 | 35.0431 | 35.0358 | 35.0286 | 35.0213 | 35.014 | 35.0067 | 34.9988 | 34.991 | 34.9755 | 34.8731 | 34.7508 | 34.7325 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.1819 | 39.18 | 39.1755 | 39.1706 | 39.1656 | 39.1605 | 39.1554 | 39.1502 | 39.1446 | 39.1389 | 39.1276 | 39.0116 | 38.8725 | 38.7296
|  | BUTTS ASH | LW |  |  | 35.0524 | 35.0497 | 35.0431 | 35.0358 | 35.0286 | 35.0213 | 35.014 | 35.0067 | 34.9988 | 34.991 | 34.9755 | 34.8731 | 34.7508 | 34.7325 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.1807 | 39.1772 | 39.1689 | 39.1597 | 39.1505 | 39.1413 | 39.132 | 39.1227 | 39.1128 | 39.1029 | 39.0832 | 38.9533 | 38.7983 | 38.6368
|  | BUTTS ASH | ST |  |  | 35.0534 | 35.0518 | 35.0482 | 35.0428 | 35.0363 | 35.0215 | 35.0068 | 34.9924 | 34.9768 | 34.9614 | 34.9313 | 34.8507 | 34.7605 | 34.7325 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.1819 | 39.1799 | 39.1754 | 39.1686 | 39.1603 | 39.1415 | 39.1229 | 39.1046 | 39.0848 | 39.0653 | 39.0271 | 38.925 | 38.8106 | 38.695
|  | BUTTS ASH | FS |  |  | 35.0627 | 35.0541 | 35.0539 | 35.0527 | 35.0513 | 35.0472 | 35.0431 | 35.0379 | 35.0328 | 35.0278 | 35.0179 | 34.9936 | 34.9659 | 34.9349 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.9836 | 39.1938 | 39.1829 | 39.1826 | 39.1811 | 39.1793 | 39.1741 | 39.169 | 39.1624 | 39.1559 | 39.1495 | 39.137 | 39.1062 | 39.071 | 39.0318
MELKSHAM GSP | CHIPPENHAM | CALNE | MINIMUM HEADROOM | SU 00521 72497 | YES | 17.7028 | 17.6608 | 17.56 | 17.45 | 17.3308 | 17.2053 | 17.0738 | 16.9369 | 16.7821 | 16.6232 | 16.2922 | 15.1625 | 13.9739 | 12.7784 | 17.1263 | 17.0757 | 16.9548 | 16.8227 | 16.6797 | 16.5291 | 16.3711 | 16.2068 | 16.021 | 15.8303 | 15.4329 | 14.0769 | 12.65 | 11.215 | 16.7409 | 16.6943 | 16.5827 | 16.4555 | 16.3171 | 16.1714 | 16.0185 | 15.8595 | 15.6798 | 15.4953 | 15.1107 | 13.7987 | 12.4181 | 11.0296
|  | CALNE | CT |  |  | 17.7028 | 17.6608 | 17.56 | 17.45 | 17.3308 | 17.2053 | 17.0738 | 16.9369 | 16.7821 | 16.6232 | 16.2922 | 15.1625 | 13.9739 | 12.7784 | 17.1317 | 17.0892 | 16.9875 | 16.8762 | 16.7555 | 16.6294 | 16.4964 | 16.3605 | 16.2106 | 16.0591 | 15.7396 | 14.4862 | 13.1738 | 11.863 | 16.7459 | 16.7067 | 16.6128 | 16.5072 | 16.3904 | 16.2684 | 16.1398 | 16.0083 | 15.8632 | 15.7166 | 15.4075 | 14.1947 | 12.9248 | 11.6566
|  | CALNE | LW |  |  | 17.7028 | 17.6608 | 17.56 | 17.45 | 17.3308 | 17.2053 | 17.0738 | 16.9369 | 16.7821 | 16.6232 | 16.2922 | 15.1625 | 13.9739 | 12.7784 | 17.1263 | 17.0757 | 16.9548 | 16.8227 | 16.6797 | 16.5291 | 16.3711 | 16.2068 | 16.021 | 15.8303 | 15.4329 | 14.0769 | 12.65 | 11.215 | 16.7409 | 16.6943 | 16.5827 | 16.4555 | 16.3171 | 16.1714 | 16.0185 | 15.8595 | 15.6798 | 15.4953 | 15.1107 | 13.7987 | 12.4181 | 11.0296
|  | CALNE | ST |  |  | 17.7898 | 17.6901 | 17.6349 | 17.5512 | 17.4446 | 17.3217 | 17.196 | 17.0698 | 16.9312 | 16.7925 | 16.5077 | 15.7375 | 14.9674 | 14.2084 | 17.2882 | 17.1109 | 17.0447 | 16.9442 | 16.8162 | 16.6687 | 16.5178 | 16.3663 | 16.1999 | 16.0335 | 15.6917 | 14.7671 | 13.8427 | 12.9316 | 16.9053 | 16.7268 | 16.6656 | 16.5729 | 16.4492 | 16.3065 | 16.1605 | 16.0139 | 15.8529 | 15.6919 | 15.3611 | 14.4665 | 13.572 | 12.6905
|  | CALNE | FS |  |  | 17.7898 | 17.7898 | 17.7233 | 17.7053 | 17.6825 | 17.6449 | 17.6066 | 17.5576 | 17.5074 | 17.4568 | 17.3536 | 17.0816 | 16.7986 | 16.5089 | 17.3019 | 17.2994 | 17.1509 | 17.1292 | 17.1019 | 17.0567 | 17.0108 | 16.9519 | 16.8916 | 16.8309 | 16.7071 | 16.3805 | 16.0408 | 15.6931 | 16.9204 | 16.9176 | 16.7636 | 16.7436 | 16.7184 | 16.6767 | 16.6343 | 16.58 | 16.5222 | 16.4634 | 16.3436 | 16.0276 | 15.6989 | 15.3625
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY | MINIMUM HEADROOM | SU 86584 59452 | NO | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 121.1341 | 121.0984 | 121.0132 | 120.9206 | 120.8288 | 120.7377 | 120.6474 | 120.558 | 120.462 | 120.367 | 120.1793 | 119.8161 | 119.42 | 119.0295 | 136.2225 | 136.21 | 136.1804 | 136.1482 | 136.1162 | 136.0846 | 136.0531 | 136.0221 | 135.9886 | 135.9556 | 135.8903 | 135.764 | 135.6262 | 135.4903
|  | CAMBERLEY | CT |  |  | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 121.1374 | 121.1065 | 121.0328 | 120.9527 | 120.8733 | 120.7945 | 120.7165 | 120.6391 | 120.5559 | 120.4734 | 120.3105 | 119.9518 | 119.5562 | 119.1639 | 136.2236 | 136.2129 | 136.1872 | 136.1594 | 136.1317 | 136.1043 | 136.0772 | 136.0503 | 136.0213 | 135.9926 | 135.9359 | 135.8112 | 135.6736 | 135.5371
|  | CAMBERLEY | LW |  |  | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 121.1341 | 121.0984 | 121.0132 | 120.9206 | 120.8288 | 120.7377 | 120.6474 | 120.558 | 120.462 | 120.367 | 120.1793 | 119.8161 | 119.42 | 119.0295 | 136.2225 | 136.21 | 136.1804 | 136.1482 | 136.1162 | 136.0846 | 136.0531 | 136.0221 | 135.9886 | 135.9556 | 135.8903 | 135.764 | 135.6262 | 135.4903
|  | CAMBERLEY | ST |  |  | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 121.1505 | 121.1383 | 121.1116 | 121.0713 | 121.0227 | 120.9781 | 120.934 | 120.8906 | 120.8438 | 120.7978 | 120.7078 | 120.4805 | 120.2368 | 119.9947 | 136.2282 | 136.2239 | 136.2146 | 136.2006 | 136.1837 | 136.1682 | 136.1529 | 136.1377 | 136.1215 | 136.1055 | 136.0742 | 135.9951 | 135.9103 | 135.8261
|  | CAMBERLEY | FS |  |  | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 137.1411 | 121.1564 | 121.1542 | 121.1516 | 121.1361 | 121.1178 | 121.1029 | 121.0882 | 121.0693 | 121.0507 | 121.0325 | 120.9969 | 120.9103 | 120.8203 | 120.7307 | 136.2302 | 136.2294 | 136.2285 | 136.2232 | 136.2168 | 136.2116 | 136.2065 | 136.1999 | 136.1934 | 136.1871 | 136.1747 | 136.1446 | 136.1133 | 136.0821
WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV | MINIMUM HEADROOM | TQ 20927 83082 | NO | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 76.0026 | 75.995 | 75.9769 | 75.9572 | 75.9378 | 75.9199 | 75.9138 | 75.9078 | 75.9012 | 75.8946 | 75.8815 | 75.8647 | 75.8475 | 75.8306 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705
|  | CANAL BANK 11kV | CT |  |  | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 76.0036 | 75.9974 | 75.9827 | 75.9667 | 75.9509 | 75.9353 | 75.9202 | 75.9153 | 75.91 | 75.9047 | 75.8941 | 75.8783 | 75.8621 | 75.8461 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705
|  | CANAL BANK 11kV | LW |  |  | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 76.0026 | 75.995 | 75.9769 | 75.9572 | 75.9378 | 75.9199 | 75.9138 | 75.9078 | 75.9012 | 75.8946 | 75.8815 | 75.8647 | 75.8475 | 75.8306 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705
|  | CANAL BANK 11kV | ST |  |  | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 76.3132 | 76.0009 | 75.9917 | 75.9778 | 75.961 | 75.955 | 75.9489 | 75.9429 | 75.9362 | 75.9296 | 75.9192 | 75.9088 | 75.8985 | 75.8884 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705
|  | CANAL BANK 11kV | FS |  |  | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 83.1638 | 76.3245 | 76.0069 | 76.0063 | 76.003 | 75.9991 | 75.9971 | 75.995 | 75.9923 | 75.9896 | 75.9869 | 75.9816 | 75.9685 | 75.9559 | 75.9439 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705 | 78.3705
WILLESDEN GSP | ACTON LANE | CANAL BANK 6.6kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 15.8107 | 39.7107 | 39.7107 | 39.7082 | 39.7056 | 39.7031 | 39.7004 | 39.6962 | 39.6948 | 39.6903 | 39.6764 | 39.7082 | 39.6948 | 39.7107 | 15.6991 | 37.5991 | 37.5991 | 37.5966 | 37.594 | 37.5914 | 37.5887 | 37.5846 | 37.5832 | 37.5787 | 37.5396 | 37.5966 | 37.5832 | 37.5991 | 15.5823 | 37.4819 | 37.481 | 37.4786 | 37.4753 | 37.4725 | 37.4695 | 37.4651 | 37.4635 | 37.4581 | 37.4388 | 37.4786 | 37.4635 | 37.4823
|  | CANAL BANK 6.6kV | CT |  |  | 15.8107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 15.6991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5473 | 37.5991 | 37.5991 | 37.5991 | 15.5824 | 37.4821 | 37.4814 | 37.4807 | 37.48 | 37.4793 | 37.479 | 37.4786 | 37.4782 | 37.477 | 37.4496 | 37.4807 | 37.4782 | 37.4824
|  | CANAL BANK 6.6kV | LW |  |  | 15.8107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 15.6991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5977 | 37.5453 | 37.5991 | 37.5991 | 37.5991 | 15.5823 | 37.4819 | 37.481 | 37.4802 | 37.4794 | 37.479 | 37.4787 | 37.4783 | 37.4779 | 37.4767 | 37.4462 | 37.4802 | 37.4779 | 37.4823
|  | CANAL BANK 6.6kV | ST |  |  | 15.8107 | 39.7107 | 39.7107 | 39.7082 | 39.7056 | 39.7031 | 39.7004 | 39.6962 | 39.6948 | 39.6903 | 39.6764 | 39.7082 | 39.6948 | 39.7107 | 15.6991 | 37.5991 | 37.5991 | 37.5966 | 37.594 | 37.5914 | 37.5887 | 37.5846 | 37.5832 | 37.5787 | 37.5396 | 37.5966 | 37.5832 | 37.5991 | 15.5854 | 37.4821 | 37.4817 | 37.4786 | 37.4753 | 37.4725 | 37.4695 | 37.4651 | 37.4635 | 37.4581 | 37.4388 | 37.4786 | 37.4635 | 37.4854
|  | CANAL BANK 6.6kV | FS |  |  | 15.8107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 15.6991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5473 | 37.5991 | 37.5991 | 37.5991 | 15.5824 | 37.4821 | 37.4814 | 37.4807 | 37.48 | 37.4793 | 37.479 | 37.4786 | 37.4782 | 37.477 | 37.4496 | 37.4807 | 37.4782 | 37.4824
COWLEY GSP | WITNEY BSP | CARTERTON | MINIMUM HEADROOM | SP 28261 07823 | YES | 27.9816 | 27.9411 | 27.8902 | 27.8289 | 27.7492 | 27.7238 | 27.7089 | 27.6951 | 27.6805 | 27.6665 | 27.5957 | 27.338 | 27.0572 | 26.757 | 24.2122 | 24.1617 | 24.0981 | 24.0217 | 23.9222 | 23.8905 | 23.8719 | 23.8547 | 23.8297 | 23.7934 | 23.7307 | 23.4093 | 23.0572 | 22.6785 | 24.6366 | 24.5868 | 24.5242 | 24.4488 | 24.3509 | 24.3196 | 24.3013 | 24.2844 | 24.2597 | 24.2239 | 24.1622 | 23.8455 | 23.5003 | 23.1314
|  | CARTERTON | CT |  |  | 27.9816 | 27.9411 | 27.8902 | 27.8289 | 27.7492 | 27.7238 | 27.7089 | 27.6951 | 27.6805 | 27.6665 | 27.5957 | 27.338 | 27.0572 | 26.757 | 24.2141 | 24.171 | 24.1148 | 24.049 | 23.9612 | 23.9303 | 23.9022 | 23.8692 | 23.8297 | 23.7934 | 23.7328 | 23.4882 | 23.1824 | 22.8471 | 24.6385 | 24.596 | 24.5406 | 24.4758 | 24.3893 | 24.3588 | 24.3311 | 24.2986 | 24.2597 | 24.2239 | 24.1643 | 23.9232 | 23.6222 | 23.2957
|  | CARTERTON | LW |  |  | 27.9816 | 27.9411 | 27.8902 | 27.8289 | 27.7492 | 27.7238 | 27.7089 | 27.6951 | 27.6805 | 27.6665 | 27.5957 | 27.338 | 27.0572 | 26.757 | 24.2122 | 24.1617 | 24.0981 | 24.0217 | 23.9222 | 23.8905 | 23.8719 | 23.8547 | 23.8366 | 23.819 | 23.7307 | 23.4093 | 23.0572 | 22.6785 | 24.6366 | 24.5868 | 24.5242 | 24.4488 | 24.3509 | 24.3196 | 24.3013 | 24.2844 | 24.2665 | 24.2492 | 24.1622 | 23.8455 | 23.5003 | 23.1314
|  | CARTERTON | ST |  |  | 27.9937 | 27.9702 | 27.9419 | 27.9079 | 27.8611 | 27.8388 | 27.8181 | 27.7949 | 27.7671 | 27.7409 | 27.6949 | 27.5354 | 27.3518 | 27.1635 | 24.2273 | 24.1979 | 24.1627 | 24.1202 | 24.0619 | 24.0341 | 24.0082 | 23.9792 | 23.9446 | 23.9119 | 23.8545 | 23.6555 | 23.4264 | 23.1914 | 24.6514 | 24.6225 | 24.5878 | 24.5459 | 24.4885 | 24.4611 | 24.4356 | 24.407 | 24.3729 | 24.3407 | 24.2841 | 24.088 | 23.8624 | 23.631
|  | CARTERTON | FS |  |  | 28.0039 | 27.9895 | 27.9743 | 27.9566 | 27.9352 | 27.9265 | 27.9202 | 27.9129 | 27.9057 | 27.8993 | 27.8851 | 27.836 | 27.7659 | 27.6835 | 24.24 | 24.222 | 24.203 | 24.181 | 24.1542 | 24.1435 | 24.1355 | 24.1264 | 24.1174 | 24.1095 | 24.0917 | 24.0305 | 23.9431 | 23.8402 | 24.664 | 24.6463 | 24.6275 | 24.6059 | 24.5795 | 24.5689 | 24.561 | 24.5521 | 24.5432 | 24.5354 | 24.5179 | 24.4575 | 24.3714 | 24.2701
AXMINSTER | YEOVIL BSP | CASTLE CARY | MINIMUM HEADROOM | ST 64534 31039 | YES | 11.3322 | 11.3291 | 11.3213 | 11.3118 | 11.2807 | 11.2452 | 11.2053 | 11.1613 | 11.1406 | 11.1236 | 11.0681 | 10.8313 | 10.5437 | 10.2303 | 10.0473 | 10.0431 | 10.0333 | 10.0216 | 9.9895 | 9.954 | 9.9175 | 9.8729 | 9.8526 | 9.8273 | 9.772 | 9.4982 | 9.1901 | 8.8665 | 10.2288 | 10.2235 | 10.2117 | 10.1977 | 10.1617 | 10.1218 | 10.0807 | 10.0352 | 10.0074 | 9.9766 | 9.9146 | 9.5941 | 9.2315 | 8.8454
|  | CASTLE CARY | CT |  |  | 11.3322 | 11.3291 | 11.3213 | 11.3118 | 11.2807 | 11.2452 | 11.2053 | 11.1613 | 11.1406 | 11.1236 | 11.0884 | 10.8313 | 10.5437 | 10.2303 | 10.0473 | 10.0431 | 10.0333 | 10.0216 | 9.9895 | 9.954 | 9.9175 | 9.877 | 9.8535 | 9.8273 | 9.7756 | 9.4982 | 9.1901 | 8.8665 | 10.2288 | 10.2235 | 10.2117 | 10.1977 | 10.1617 | 10.1218 | 10.0807 | 10.0352 | 10.0074 | 9.9766 | 9.9146 | 9.5941 | 9.2315 | 8.8454
|  | CASTLE CARY | LW |  |  | 11.3322 | 11.3291 | 11.3213 | 11.3118 | 11.2807 | 11.2452 | 11.2053 | 11.1613 | 11.1406 | 11.1236 | 11.0884 | 10.8313 | 10.5437 | 10.2303 | 10.0491 | 10.0461 | 10.0383 | 10.0287 | 9.9964 | 9.9596 | 9.9183 | 9.8729 | 9.8526 | 9.8364 | 9.8033 | 9.5462 | 9.2656 | 8.9682 | 10.2314 | 10.228 | 10.2192 | 10.2085 | 10.1731 | 10.1328 | 10.0876 | 10.0377 | 10.0146 | 9.9957 | 9.9569 | 9.6681 | 9.3473 | 9.0006
|  | CASTLE CARY | ST |  |  | 11.4501 | 11.3327 | 11.3299 | 11.3255 | 11.3074 | 11.2696 | 11.2314 | 11.1912 | 11.1607 | 11.1292 | 11.0681 | 10.9163 | 10.7582 | 10.5948 | 10.1738 | 10.0493 | 10.0466 | 10.0421 | 10.0231 | 9.9833 | 9.9431 | 9.9008 | 9.8689 | 9.8359 | 9.772 | 9.6148 | 9.4532 | 9.2883 | 10.3661 | 10.2319 | 10.2288 | 10.2238 | 10.2032 | 10.16 | 10.1165 | 10.0706 | 10.0359 | 9.9999 | 9.9304 | 9.7581 | 9.5793 | 9.3952
|  | CASTLE CARY | FS |  |  | 11.4506 | 11.3341 | 11.3339 | 11.3328 | 11.326 | 11.3129 | 11.2993 | 11.2827 | 11.2712 | 11.2605 | 11.239 | 11.1844 | 11.1292 | 11.0729 | 10.1742 | 10.0508 | 10.0507 | 10.0497 | 10.0425 | 10.0288 | 10.0145 | 9.9971 | 9.985 | 9.9738 | 9.9514 | 9.895 | 9.8383 | 9.7805 | 10.3666 | 10.2335 | 10.2333 | 10.2321 | 10.2243 | 10.2094 | 10.1939 | 10.175 | 10.1619 | 10.1496 | 10.1252 | 10.0633 | 10.0008 | 9.937
LALEHAM | STAINES | CAUSEWAY | MINIMUM HEADROOM | TQ 02763 71680 | YES | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 79.3725 | 79.3293 | 79.2797 | 79.226 | 79.1508 | 79.0528 | 78.949 | 78.8954 | 78.8314 | 78.7682 | 78.6611 | 78.3858 | 78.1011 | 78.0483 | 81.7674 | 81.6689 | 81.5559 | 81.4335 | 81.2623 | 81.0389 | 80.8455 | 80.7599 | 80.676 | 80.5933 | 43.0633 | 42.0889 | 41.0812 | 40.0771
|  | CAUSEWAY | CT |  |  | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 79.3749 | 79.3384 | 79.2971 | 79.2525 | 79.1877 | 79.1009 | 79.0116 | 78.966 | 78.9151 | 78.8584 | 78.7463 | 78.4636 | 78.1866 | 78.0483 | 81.7728 | 81.6897 | 81.5956 | 81.4939 | 81.3464 | 81.1485 | 80.949 | 80.8736 | 80.7894 | 80.7114 | 80.5645 | 42.3643 | 41.3841 | 40.4073
|  | CAUSEWAY | LW |  |  | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 79.3725 | 79.3293 | 79.2797 | 79.226 | 79.1508 | 79.0528 | 78.949 | 78.8954 | 78.8314 | 78.7682 | 78.6611 | 78.3858 | 78.1011 | 78.0483 | 81.7674 | 81.6689 | 81.5559 | 81.4335 | 81.2623 | 81.0389 | 80.8455 | 80.7599 | 80.676 | 80.5933 | 43.0633 | 42.0889 | 41.0812 | 40.0771
|  | CAUSEWAY | ST |  |  | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 79.3812 | 79.3566 | 79.3319 | 79.295 | 79.2371 | 79.1633 | 79.0883 | 79.0429 | 78.9927 | 78.9387 | 78.8326 | 78.6145 | 78.4379 | 78.2621 | 81.7872 | 81.731 | 81.6747 | 81.5908 | 81.4589 | 81.2908 | 81.12 | 81.0165 | 80.9177 | 80.8285 | 80.6776 | 42.8984 | 42.2734 | 41.6512
|  | CAUSEWAY | FS |  |  | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 84.8105 | 79.389 | 79.3794 | 79.3771 | 79.3679 | 79.3508 | 79.3239 | 79.2966 | 79.2761 | 79.2555 | 79.2347 | 79.1954 | 79.0971 | 79.0015 | 78.9075 | 81.8048 | 81.7829 | 81.7779 | 81.7567 | 81.7178 | 81.6565 | 81.5944 | 81.5478 | 81.5007 | 81.4534 | 81.3639 | 81.1398 | 80.9323 | 80.7769
BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM | MINIMUM HEADROOM | SU 71512 75747 | YES | 28.142 | 27.9488 | 27.4911 | 26.9957 | 26.506 | 26.0221 | 25.5437 | 25.0704 | 24.5604 | 24.0555 | 23.0598 | 21.6902 | 20.2583 | 18.8505 | 32.3096 | 32.2667 | 32.2185 | 32.1664 | 32.1149 | 32.064 | 32.0137 | 31.9639 | 31.9367 | 26.3444 | 25.1728 | 23.5613 | 21.8764 | 20.1523 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 26.5739 | 25.4045 | 23.7961 | 22.1144 | 20.3935
|  | CAVERSHAM | CT |  |  | 28.142 | 27.9488 | 27.4911 | 26.9957 | 26.506 | 26.0221 | 25.5437 | 25.0704 | 24.5604 | 24.0555 | 23.0598 | 21.6902 | 20.2583 | 18.8505 | 32.3104 | 32.2673 | 32.22 | 32.1688 | 32.1182 | 32.0681 | 32.0186 | 31.9696 | 31.9367 | 26.4277 | 25.2748 | 23.6504 | 21.892 | 20.1523 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 26.657 | 25.5063 | 23.885 | 22.13 | 20.3935
|  | CAVERSHAM | LW |  |  | 28.142 | 27.9488 | 27.4911 | 26.9957 | 26.506 | 26.0221 | 25.5437 | 25.0704 | 24.5604 | 24.0555 | 23.0598 | 21.6902 | 20.2583 | 18.8505 | 32.3096 | 32.2667 | 32.2185 | 32.1664 | 32.1149 | 32.064 | 32.0137 | 31.9639 | 31.9367 | 26.3444 | 25.1728 | 23.5613 | 21.8764 | 20.22 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 26.5739 | 25.4045 | 23.7961 | 22.1144 | 20.4611
|  | CAVERSHAM | ST |  |  | 28.2968 | 28.1356 | 27.9537 | 27.68 | 27.3508 | 27.2004 | 27.0521 | 26.9057 | 26.7479 | 26.5925 | 26.2893 | 25.4949 | 24.6573 | 23.8281 | 32.3569 | 32.3077 | 32.2672 | 32.2384 | 32.2038 | 32.188 | 32.1724 | 32.157 | 32.1404 | 32.124 | 32.0921 | 32.0085 | 31.9367 | 26.0769 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 26.3069
|  | CAVERSHAM | FS |  |  | 28.3399 | 28.3279 | 28.3136 | 28.2325 | 28.1361 | 28.0837 | 28.0317 | 27.965 | 27.8995 | 27.8352 | 27.71 | 27.3929 | 27.069 | 26.7495 | 32.37 | 32.3663 | 32.362 | 32.3373 | 32.3079 | 32.2919 | 32.276 | 32.2684 | 32.2615 | 32.2547 | 32.2416 | 32.2082 | 32.1741 | 32.1405 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811 | 32.6811
MANNINGTON GSP | BOURNEMOUTH | CENTRAL | MINIMUM HEADROOM | SZ 10293 91931 | NO | 34.0681 | 34.0663 | 34.0639 | 34.0609 | 34.0571 | 34.0524 | 34.0468 | 34.0403 | 34.0351 | 34.0293 | 34.0151 | 33.9645 | 27.3567 | 25.7696 | 32.7148 | 32.6754 | 32.5822 | 32.4723 | 32.3743 | 32.282 | 32.1876 | 32.0915 | 31.9887 | 31.9652 | 31.919 | 26.6888 | 24.805 | 22.9346 | 33.577 | 33.5569 | 33.5125 | 33.4572 | 33.3982 | 33.3488 | 33.3072 | 33.2647 | 33.2506 | 33.2395 | 33.2137 | 33.1306 | 25.3034 | 23.4007
|  | CENTRAL | CT |  |  | 34.0681 | 34.0663 | 34.0639 | 34.0609 | 34.0571 | 34.0524 | 34.0468 | 34.0403 | 34.0351 | 34.0293 | 34.0151 | 33.9645 | 27.3567 | 25.7696 | 32.7164 | 32.6825 | 32.6051 | 32.5138 | 32.4167 | 32.3375 | 32.2579 | 32.1763 | 32.0897 | 32.0066 | 31.919 | 31.8725 | 25.6084 | 23.9245 | 33.577 | 33.5569 | 33.5138 | 33.4636 | 33.4101 | 33.3541 | 33.3072 | 33.2647 | 33.2506 | 33.2395 | 33.2137 | 33.1306 | 26.0907 | 24.3729
|  | CENTRAL | LW |  |  | 34.0681 | 34.0663 | 34.0639 | 34.0609 | 34.0571 | 34.0524 | 34.0468 | 34.0403 | 34.0351 | 34.0293 | 34.0151 | 33.9645 | 27.3567 | 25.7696 | 32.7148 | 32.6754 | 32.5822 | 32.4723 | 32.3743 | 32.282 | 32.1876 | 32.0915 | 31.9887 | 31.9652 | 31.957 | 26.6888 | 24.805 | 22.9346 | 33.5796 | 33.5593 | 33.5125 | 33.4572 | 33.3982 | 33.3488 | 33.3143 | 33.3075 | 33.3022 | 33.2962 | 33.2815 | 33.2292 | 25.3034 | 23.4007
|  | CENTRAL | ST |  |  | 34.0698 | 34.0691 | 34.0683 | 34.0673 | 34.0662 | 34.0646 | 34.0629 | 34.0609 | 34.0589 | 34.0567 | 34.052 | 34.039 | 34.0204 | 28.0481 | 32.7361 | 32.727 | 32.707 | 32.6729 | 32.6292 | 32.5081 | 32.3989 | 32.3071 | 32.2067 | 32.11 | 31.9783 | 31.9708 | 31.9601 | 25.5892 | 33.591 | 33.5862 | 33.576 | 33.5588 | 33.5369 | 33.477 | 33.4172 | 33.3652 | 33.3268 | 33.3245 | 33.3197 | 33.3062 | 33.287 | 26.1164
|  | CENTRAL | FS |  |  | 34.07 | 34.0696 | 34.0691 | 34.0685 | 34.0678 | 34.067 | 34.0662 | 34.0654 | 34.0645 | 34.0635 | 34.0615 | 34.0539 | 34.0467 | 34.0394 | 32.7394 | 32.7361 | 32.7318 | 32.7098 | 32.6829 | 32.6412 | 32.5996 | 32.5474 | 32.4951 | 32.4451 | 32.3694 | 32.1939 | 32.0252 | 31.971 | 33.5927 | 33.5909 | 33.5885 | 33.5774 | 33.5639 | 33.5432 | 33.5224 | 33.4965 | 33.4706 | 33.4457 | 33.3975 | 33.3216 | 33.3141 | 33.3066
NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE | MINIMUM HEADROOM | SU 42591 11255 | YES | 43.5825 | 43.5371 | 43.4905 | 43.4507 | 43.4134 | 43.3696 | 43.3236 | 43.2505 | 43.1976 | 43.147 | 37.7824 | 37.1671 | 36.5716 | 35.9848 | 35.33 | 35.0528 | 34.7687 | 34.5253 | 34.2979 | 34.0301 | 33.7491 | 33.303 | 32.9802 | 32.6712 | 32.1892 | 31.4831 | 30.7998 | 30.1265 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 34.8808 | 34.1629 | 33.4556
|  | CENTRAL BRIDGE | CT |  |  | 43.5825 | 43.5371 | 43.4905 | 43.4507 | 43.4134 | 43.3696 | 43.3236 | 43.2505 | 43.1976 | 43.147 | 37.7824 | 37.1671 | 36.5716 | 35.9848 | 35.3479 | 35.1174 | 34.8858 | 34.6972 | 34.509 | 34.262 | 33.9861 | 33.5885 | 33.2947 | 33.0155 | 32.5536 | 31.7538 | 31.0595 | 30.3875 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 35.1653 | 34.4358 | 33.7298
|  | CENTRAL BRIDGE | LW |  |  | 43.5825 | 43.5371 | 43.4905 | 43.4507 | 43.4134 | 43.3696 | 43.3236 | 43.2505 | 43.1976 | 43.147 | 37.7824 | 37.1671 | 36.5716 | 35.9848 | 35.33 | 35.0528 | 34.7687 | 34.5253 | 34.2979 | 34.0301 | 33.7491 | 33.303 | 32.9802 | 32.6712 | 32.1892 | 31.4831 | 30.7998 | 30.1265 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 34.8808 | 34.1629 | 33.4556
|  | CENTRAL BRIDGE | ST |  |  | 43.5969 | 43.5723 | 43.5514 | 43.5319 | 43.5098 | 43.4844 | 43.456 | 43.4142 | 43.3835 | 43.3539 | 43.3056 | 43.2244 | 43.1586 | 43.0948 | 35.4182 | 35.2677 | 35.1401 | 35.0215 | 34.8862 | 34.7315 | 34.5577 | 34.3028 | 34.1149 | 33.9346 | 33.6396 | 33.1437 | 32.7419 | 32.3521 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25
|  | CENTRAL BRIDGE | FS |  |  | 43.6074 | 43.5937 | 43.5852 | 43.576 | 43.5667 | 43.5564 | 43.546 | 43.5288 | 43.516 | 43.5036 | 43.4834 | 43.4486 | 43.4219 | 43.3975 | 35.4824 | 35.3983 | 35.3469 | 35.2906 | 35.2339 | 35.1708 | 35.1076 | 35.0024 | 34.9243 | 34.8482 | 34.7248 | 34.5127 | 34.3497 | 34.2003 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25 | 40.25
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS | MINIMUM HEADROOM | ST 66140 01039 | YES | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 1.8992 | 1.8981 | 1.8956 | 1.8923 | 1.8882 | 1.8837 | 1.877 | 1.8687 | 1.8598 | 1.8509 | 1.8331 | 1.7848 | 1.7169 | 1.6492 | 1.8996 | 1.899 | 1.8976 | 1.8958 | 1.8935 | 1.8911 | 1.8875 | 1.8829 | 1.878 | 1.8731 | 1.8635 | 1.8371 | 1.8 | 1.763
|  | CERNE ABBAS | CT |  |  | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 1.8993 | 1.8982 | 1.8957 | 1.8926 | 1.8888 | 1.8847 | 1.8802 | 1.8754 | 1.8705 | 1.8655 | 1.8554 | 1.7883 | 1.7201 | 1.652 | 1.8996 | 1.899 | 1.8977 | 1.896 | 1.8939 | 1.8916 | 1.8892 | 1.8866 | 1.8839 | 1.8811 | 1.8756 | 1.839 | 1.8017 | 1.7645
|  | CERNE ABBAS | LW |  |  | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 1.8992 | 1.8981 | 1.8956 | 1.8923 | 1.8882 | 1.8837 | 1.8787 | 1.8736 | 1.8682 | 1.8627 | 1.8516 | 1.7848 | 1.7169 | 1.6492 | 1.8996 | 1.899 | 1.8976 | 1.8958 | 1.8935 | 1.8911 | 1.8884 | 1.8856 | 1.8826 | 1.8796 | 1.8736 | 1.8371 | 1.8 | 1.763
|  | CERNE ABBAS | ST |  |  | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 1.8996 | 1.8991 | 1.8979 | 1.896 | 1.8935 | 1.8853 | 1.877 | 1.8687 | 1.8598 | 1.8509 | 1.8331 | 1.7899 | 1.7479 | 1.7063 | 1.8998 | 1.8995 | 1.8989 | 1.8978 | 1.8964 | 1.892 | 1.8875 | 1.8829 | 1.878 | 1.8731 | 1.8635 | 1.8399 | 1.8169 | 1.7942
|  | CERNE ABBAS | FS |  |  | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 7.4993 | 1.8999 | 1.8997 | 1.8994 | 1.8988 | 1.8979 | 1.8951 | 1.8923 | 1.8889 | 1.8855 | 1.8821 | 1.8754 | 1.859 | 1.8428 | 1.8268 | 1.8999 | 1.8998 | 1.8997 | 1.8993 | 1.8988 | 1.8973 | 1.8958 | 1.8939 | 1.8921 | 1.8902 | 1.8866 | 1.8776 | 1.8688 | 1.86
IVER 132KV | CHALVEY BSP | CHALVEY | MINIMUM HEADROOM | SU 96669 79364 | NO | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 89.8079 | 89.678 | 89.4635 | 89.2244 | 88.9769 | 88.74 | 88.4916 | 88.209 | 87.9429 | 87.8268 | 87.6228 | 87.012 | 86.6821 | 86.4717 | 89.6463 | 89.5832 | 89.479 | 89.3629 | 89.2427 | 89.1276 | 89.0069 | 88.8697 | 88.7392 | 88.6321 | 88.6258 | 88.6258 | 88.6258 | 88.6258
|  | CHALVEY | CT |  |  | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 89.8125 | 89.6969 | 89.4999 | 89.2834 | 89.0571 | 88.834 | 88.5959 | 88.3217 | 88.0493 | 87.8833 | 87.6808 | 87.1031 | 86.7278 | 86.5322 | 89.6485 | 89.5924 | 89.4967 | 89.3915 | 89.2816 | 89.1732 | 89.0576 | 88.9244 | 88.7921 | 88.6842 | 88.6258 | 88.6258 | 88.6258 | 88.6258
|  | CHALVEY | LW |  |  | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 89.8079 | 89.678 | 89.4635 | 89.2244 | 88.9769 | 88.74 | 88.4916 | 88.209 | 87.9429 | 87.8268 | 87.6228 | 87.012 | 86.6821 | 86.4717 | 89.6463 | 89.5832 | 89.479 | 89.3629 | 89.2427 | 89.1276 | 89.0069 | 88.8697 | 88.7392 | 88.6321 | 88.6258 | 88.6258 | 88.6258 | 88.6258
|  | CHALVEY | ST |  |  | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 89.8553 | 89.7938 | 89.7078 | 89.598 | 89.4703 | 89.2843 | 89.0894 | 88.8713 | 88.6489 | 88.4608 | 88.128 | 87.6435 | 87.2646 | 86.8912 | 89.6693 | 89.6394 | 89.5977 | 89.5444 | 89.4823 | 89.392 | 89.2973 | 89.1914 | 89.0833 | 88.9919 | 88.8303 | 88.6258 | 88.6258 | 88.6258
|  | CHALVEY | FS |  |  | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 96.4133 | 89.882 | 89.85 | 89.8163 | 89.7638 | 89.7069 | 89.636 | 89.5632 | 89.4715 | 89.3841 | 89.3116 | 89.1796 | 88.8837 | 88.6064 | 88.3372 | 89.6823 | 89.6667 | 89.6504 | 89.6249 | 89.5973 | 89.5628 | 89.5274 | 89.4829 | 89.4405 | 89.4052 | 89.3411 | 89.1974 | 89.0627 | 88.9319
NURSLING GSP | VELMORE BSP | CHANDLERSFORD | MINIMUM HEADROOM | SU 43494 21552 | YES | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 42.9061 | 42.8264 | 42.633 | 42.4203 | 42.2418 | 42.1096 | 41.9819 | 41.8463 | 41.6992 | 41.5494 | 41.2431 | 40.801 | 40.801 | 40.801 | 39.9547 | 39.9233 | 39.8472 | 39.7635 | 39.6772 | 39.5923 | 39.5157 | 39.5157 | 39.5157 | 39.5157 | 39.5157 | 39.5157 | 39.5157 | 39.5157
|  | CHANDLERSFORD | CT |  |  | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 42.9061 | 42.8264 | 42.633 | 42.4203 | 42.2418 | 42.1096 | 41.9819 | 41.8463 | 41.6992 | 41.5494 | 41.2431 | 40.801 | 40.801 | 40.801 | 39.9547 | 39.9233 | 39.8472 | 39.7635 | 39.6772 | 39.5923 | 39.5157 | 39.5157 | 39.5157 | 39.5157 | 39.5157 | 39.5157 | 39.5157 | 39.5157
|  | CHANDLERSFORD | LW |  |  | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 42.9212 | 42.8639 | 42.724 | 42.5682 | 42.404 | 42.2671 | 42.1665 | 42.0555 | 41.9343 | 41.8102 | 41.5591 | 40.9383 | 40.801 | 40.801 | 39.9606 | 39.9381 | 39.883 | 39.8217 | 39.7571 | 39.6935 | 39.6289 | 39.5576 | 39.5157 | 39.5157 | 39.5157 | 39.5157 | 39.5157 | 39.5157
|  | CHANDLERSFORD | ST |  |  | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 42.9881 | 42.9142 | 42.8512 | 42.7556 | 42.636 | 42.5194 | 42.4078 | 42.2949 | 42.2146 | 42.1323 | 41.9623 | 41.5299 | 41.1084 | 40.8472 | 39.9869 | 39.9579 | 39.9331 | 39.8954 | 39.8484 | 39.8025 | 39.7586 | 39.7114 | 39.6598 | 39.6069 | 39.5157 | 39.5157 | 39.5157 | 39.5157
|  | CHANDLERSFORD | FS |  |  | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 49.4505 | 43.0026 | 42.9527 | 42.9466 | 42.9203 | 42.8872 | 42.8474 | 42.8108 | 42.7606 | 42.7099 | 42.6584 | 42.5541 | 42.2935 | 42.129 | 41.9662 | 39.9926 | 39.973 | 39.9706 | 39.9602 | 39.9472 | 39.9316 | 39.9171 | 39.8974 | 39.8775 | 39.8572 | 39.8162 | 39.7104 | 39.6048 | 39.5157
NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL | MINIMUM HEADROOM | SU 42849 11983 | YES | 27.975 | 27.9708 | 27.9636 | 27.9592 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 24.4818 | 24.4563 | 24.4127 | 24.3861 | 24.3694 | 24.3535 | 24.3377 | 24.3168 | 24.2762 | 24.2362 | 24.1402 | 24.0002 | 23.8978 | 23.7989 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031
|  | CHAPEL | CT |  |  | 27.975 | 27.9708 | 27.9636 | 27.9592 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 24.4826 | 24.4602 | 24.4203 | 24.3965 | 24.3804 | 24.3625 | 24.3403 | 24.3168 | 24.2762 | 24.2362 | 24.1479 | 24.0002 | 23.8978 | 23.7999 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031
|  | CHAPEL | LW |  |  | 27.975 | 27.9708 | 27.9636 | 27.9592 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 24.4818 | 24.4563 | 24.4127 | 24.3861 | 24.3694 | 24.3535 | 24.3377 | 24.3218 | 24.2806 | 24.2372 | 24.1402 | 24.0008 | 23.8993 | 23.7989 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031
|  | CHAPEL | ST |  |  | 27.985 | 27.9741 | 27.9703 | 27.9679 | 27.9661 | 27.964 | 27.9614 | 27.9587 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 27.9566 | 24.5421 | 24.4762 | 24.4532 | 24.4388 | 24.4279 | 24.4149 | 24.3993 | 24.3828 | 24.3542 | 24.3258 | 24.262 | 24.1578 | 24.0899 | 24.0252 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031
|  | CHAPEL | FS |  |  | 27.9861 | 27.9848 | 27.9831 | 27.9821 | 27.9814 | 27.9806 | 27.9798 | 27.9789 | 27.9771 | 27.9752 | 27.9711 | 27.9646 | 27.9599 | 27.9566 | 24.549 | 24.5412 | 24.5308 | 24.5245 | 24.5205 | 24.5155 | 24.5106 | 24.505 | 24.4941 | 24.4826 | 24.4578 | 24.4184 | 24.3901 | 24.3664 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031 | 24.0031
COWLEY GSP | YARNTON BSP | CHARLBURY | MINIMUM HEADROOM | SP 36034 18376 | YES | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 19.5156 | 19.5034 | 19.4738 | 19.4414 | 19.4089 | 19.3767 | 19.3581 | 19.3538 | 19.3492 | 19.3445 | 19.335 | 19.3063 | 19.2756 | 19.2447 | 20.0419 | 20.039 | 20.0318 | 20.024 | 20.0161 | 20.0083 | 20.0006 | 19.9929 | 19.9846 | 19.9763 | 19.9593 | 19.9215 | 19.9215 | 19.9215
|  | CHARLBURY | CT |  |  | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 19.5156 | 19.5034 | 19.4738 | 19.4414 | 19.4089 | 19.3767 | 19.3581 | 19.3538 | 19.3492 | 19.3445 | 19.335 | 19.3063 | 19.2756 | 19.2447 | 20.0419 | 20.039 | 20.0318 | 20.024 | 20.0161 | 20.0083 | 20.0006 | 19.9929 | 19.9846 | 19.9763 | 19.9593 | 19.9215 | 19.9215 | 19.9215
|  | CHARLBURY | LW |  |  | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 19.5178 | 19.5088 | 19.4868 | 19.4627 | 19.4384 | 19.4143 | 19.3903 | 19.3665 | 19.3576 | 19.3541 | 19.346 | 19.3175 | 19.2879 | 19.258 | 20.0425 | 20.0403 | 20.035 | 20.0291 | 20.0233 | 20.0174 | 20.0116 | 20.0058 | 19.9996 | 19.9934 | 19.9789 | 19.9282 | 19.9215 | 19.9215
|  | CHARLBURY | ST |  |  | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 19.5233 | 19.5227 | 19.5213 | 19.5189 | 19.5157 | 19.4947 | 19.474 | 19.4535 | 19.4313 | 19.4094 | 19.3644 | 19.3439 | 19.3265 | 19.3089 | 20.0438 | 20.0437 | 20.0433 | 20.0427 | 20.042 | 20.0369 | 20.0319 | 20.0269 | 20.0215 | 20.0162 | 20.0053 | 19.9753 | 19.9441 | 19.9215
|  | CHARLBURY | FS |  |  | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 22.0172 | 19.5235 | 19.5232 | 19.5229 | 19.5206 | 19.518 | 19.5109 | 19.5039 | 19.4949 | 19.486 | 19.4772 | 19.4596 | 19.4121 | 19.3616 | 19.3535 | 20.0439 | 20.0438 | 20.0437 | 20.0432 | 20.0425 | 20.0408 | 20.0391 | 20.0369 | 20.0348 | 20.0326 | 20.0284 | 20.0169 | 20.0046 | 19.9923
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER | MINIMUM HEADROOM | SY 67309 93186 | YES | 16.8405 | 16.8405 | 11.9475 | 11.8744 | 11.8011 | 11.6925 | 11.5958 | 11.517 | 11.4306 | 11.2809 | 10.7784 | 9.1759 | 8.449 | 7.9747 | 16.2321 | 16.2259 | 11.9506 | 11.8816 | 11.8125 | 11.71 | 11.6187 | 11.5443 | 11.4627 | 11.3186 | 10.8039 | 9.1622 | 8.4176 | 7.9317 | 11.9662 | 11.9282 | 11.874 | 11.827 | 11.7798 | 11.7099 | 11.6477 | 11.597 | 11.5414 | 11.445 | 11.1217 | 9.804 | 8.9728 | 8.4304
|  | CHARMINSTER | CT |  |  | 16.8405 | 16.8405 | 11.9475 | 11.8744 | 11.8011 | 11.6925 | 11.5958 | 11.517 | 11.4306 | 11.2809 | 10.7784 | 9.1759 | 8.449 | 7.9747 | 16.2323 | 16.2269 | 11.9681 | 11.9081 | 11.8465 | 11.7507 | 11.6603 | 11.5808 | 11.4963 | 11.3614 | 10.8893 | 10.083 | 9.5877 | 9.1117 | 11.9674 | 11.9345 | 11.8859 | 11.845 | 11.803 | 11.7377 | 11.6761 | 11.6219 | 11.5642 | 11.4723 | 11.1753 | 10.6687 | 10.279 | 9.7476
|  | CHARMINSTER | LW |  |  | 16.8405 | 16.8405 | 11.9475 | 11.8744 | 11.8011 | 11.6925 | 11.5958 | 11.517 | 11.4306 | 11.2809 | 10.7784 | 9.1759 | 8.449 | 7.9747 | 16.2321 | 16.2259 | 11.9506 | 11.8816 | 11.8125 | 11.71 | 11.6187 | 11.5443 | 11.4627 | 11.3186 | 10.8039 | 9.1622 | 8.4176 | 7.9317 | 11.9662 | 11.9282 | 11.874 | 11.827 | 11.7798 | 11.7099 | 11.6477 | 11.597 | 11.5414 | 11.445 | 11.1217 | 9.804 | 8.9728 | 8.4304
|  | CHARMINSTER | ST |  |  | 16.8405 | 16.8405 | 16.8405 | 11.985 | 11.9403 | 11.8434 | 11.751 | 11.6668 | 11.5754 | 11.4458 | 11.0544 | 10.5128 | 10.2112 | 9.9257 | 16.2337 | 16.2301 | 16.2253 | 11.986 | 11.9439 | 11.8524 | 11.7652 | 11.6857 | 11.5995 | 11.4771 | 11.0865 | 10.5318 | 10.2228 | 9.9303 | 11.9757 | 11.9539 | 11.9245 | 11.8982 | 11.8694 | 11.8071 | 11.7476 | 11.6934 | 11.6346 | 11.5511 | 11.2992 | 10.9507 | 10.7566 | 10.5728
|  | CHARMINSTER | FS |  |  | 16.8405 | 16.8405 | 16.8405 | 16.8405 | 16.8405 | 11.9993 | 11.965 | 11.9315 | 11.8959 | 11.8453 | 11.6992 | 11.2887 | 11.0065 | 10.8623 | 16.2349 | 16.2329 | 16.2306 | 16.2285 | 16.2265 | 11.9995 | 11.9672 | 11.9356 | 11.902 | 11.8542 | 11.7163 | 11.3266 | 11.0375 | 10.8898 | 11.9833 | 11.9709 | 11.9567 | 11.9443 | 11.932 | 11.9074 | 11.8853 | 11.8638 | 11.8408 | 11.8082 | 11.7142 | 11.4501 | 11.2684 | 11.1756
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER | MINIMUM HEADROOM | SU 92198 07420 | YES | 26.2117 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 21.7043 | 20.7877 | 19.5669 | 18.3406 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 20.1485 | 19.677 | 19.1692 | 18.632 | 17.6637 | 16.4425 | 15.0528 | 13.6566 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 20.1411 | 19.6992 | 18.7003 | 17.4405 | 16.0068 | 14.5666
|  | CHICHESTER | CT |  |  | 26.2117 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 21.7043 | 20.7877 | 19.5669 | 18.3406 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 20.389 | 19.9692 | 19.4948 | 18.9612 | 17.9566 | 16.5115 | 15.1748 | 13.8713 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 20.3899 | 19.9822 | 19.0024 | 17.5116 | 16.1327 | 14.788
|  | CHICHESTER | LW |  |  | 26.2117 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 21.7043 | 20.7877 | 19.5669 | 18.3406 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 20.1485 | 19.677 | 19.1692 | 18.632 | 17.6637 | 16.4425 | 15.0528 | 13.6566 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 20.1411 | 19.6992 | 18.7003 | 17.4405 | 16.0068 | 14.5666
|  | CHICHESTER | ST |  |  | 26.2286 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 21.6662 | 20.9678 | 20.1935 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 20.3368 | 19.9316 | 19.4792 | 18.6055 | 17.5645 | 16.6476 | 15.7661 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 20.378 | 19.6719 | 18.598 | 17.652 | 16.7427
|  | CHICHESTER | FS |  |  | 26.2312 | 26.2147 | 26.2114 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.2112 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 26.9677 | 20.2863 | 19.9725 | 19.6405 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767 | 23.767
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL | MINIMUM HEADROOM | SY 65479 80511 | YES | -0.98491 | -1.0154 | -1.0577 | -1.0958 | -1.1382 | -1.1859 | -1.232 | -1.2618 | -1.2925 | -1.3238 | -1.3853 | -1.6065 | -1.8278 | -2.0506 | 1.0353 | 0.9727 | 0.88569 | 0.80733 | 0.72029 | 0.62216 | 0.52758 | 0.46626 | 0.40315 | 0.3389 | 0.21239 | -0.24209 | -0.69688 | -1.1547 | -39.7648 | -39.8008 | -39.8509 | -39.8961 | -39.9462 | -40.0027 | -40.0571 | -40.0924 | -40.1288 | -40.1658 | -40.2386 | -40.5002 | -40.7621 | -41.0257
|  | CHICKERELL | CT |  |  | -0.98491 | -1.0154 | -1.0577 | -1.0958 | -1.1382 | -1.1859 | -1.232 | -1.2618 | -1.2925 | -1.3238 | -1.3853 | -1.6065 | -1.8278 | -2.0506 | 1.0378 | 0.98365 | 0.90574 | 0.83759 | 0.75943 | 0.66632 | 0.57057 | 0.49861 | 0.42575 | 0.35173 | 0.22089 | -0.14121 | -0.49659 | -0.85549 | -39.7634 | -39.7945 | -39.8394 | -39.8786 | -39.9236 | -39.9772 | -40.0324 | -40.0738 | -40.1157 | -40.1584 | -40.2337 | -40.4422 | -40.6468 | -40.8534
|  | CHICKERELL | LW |  |  | -0.98491 | -1.0154 | -1.0577 | -1.0958 | -1.1382 | -1.1859 | -1.232 | -1.2618 | -1.2925 | -1.3238 | -1.3853 | -1.6065 | -1.8278 | -2.0506 | 1.0353 | 0.9727 | 0.88569 | 0.80733 | 0.72029 | 0.62216 | 0.52758 | 0.46626 | 0.40315 | 0.3389 | 0.21239 | -0.24209 | -0.69688 | -1.1547 | -39.7648 | -39.8008 | -39.8509 | -39.8961 | -39.9462 | -40.0027 | -40.0571 | -40.0924 | -40.1288 | -40.1658 | -40.2386 | -40.5002 | -40.7621 | -41.0257
|  | CHICKERELL | ST |  |  | -0.97609 | -0.99356 | -1.0164 | -1.0373 | -1.0626 | -1.1092 | -1.1564 | -1.1956 | -1.2368 | -1.2786 | -1.3561 | -1.5306 | -1.696 | -1.8593 | 1.0534 | 1.0175 | 0.97056 | 0.92766 | 0.87561 | 0.77983 | 0.68285 | 0.60232 | 0.51758 | 0.43182 | 0.27255 | -0.086145 | -0.42609 | -0.7616 | -39.7544 | -39.7751 | -39.8021 | -39.8268 | -39.8567 | -39.9119 | -39.9677 | -40.0141 | -40.0629 | -40.1123 | -40.2039 | -40.4105 | -40.6062 | -40.7994
|  | CHICKERELL | FS |  |  | -0.96896 | -0.97914 | -0.99053 | -1.0007 | -1.0116 | -1.0277 | -1.0429 | -1.0559 | -1.0691 | -1.0825 | -1.1083 | -1.166 | -1.2211 | -1.2775 | 1.068 | 1.0471 | 1.0237 | 1.0029 | 0.98051 | 0.94729 | 0.916 | 0.8894 | 0.86223 | 0.8348 | 0.78166 | 0.66314 | 0.54986 | 0.43403 | -39.7459 | -39.758 | -39.7715 | -39.7835 | -39.7963 | -39.8155 | -39.8335 | -39.8488 | -39.8644 | -39.8802 | -39.9108 | -39.9791 | -40.0443 | -40.111
AXMINSTER | YEOVIL BSP | CHILTON CANTELLO | MINIMUM HEADROOM | ST 57910 21616 | YES | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 9.6996 | 9.5566 | 9.4488 | 9.2108 | 8.9572 | 8.7562 | 8.5573 | 14.4409 | 14.436 | 14.429 | 14.4207 | 14.4111 | 14.4001 | 9.6274 | 9.4494 | 9.2799 | 9.1522 | 8.8702 | 8.5052 | 8.2443 | 8.0031 | 9.6771 | 9.6347 | 9.5754 | 9.5043 | 9.4224 | 9.329 | 9.2096 | 9.0712 | 8.9394 | 8.8402 | 8.6209 | 8.2823 | 8.0219 | 7.7811
|  | CHILTON CANTELLO | CT |  |  | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 9.6996 | 9.5566 | 9.4488 | 9.2108 | 8.9572 | 8.7562 | 8.5573 | 14.4411 | 14.4368 | 14.4306 | 14.4235 | 14.4151 | 14.4052 | 9.7001 | 9.5349 | 9.3688 | 9.2267 | 8.9164 | 8.5052 | 8.2443 | 8.0031 | 9.6781 | 9.6418 | 9.5893 | 9.5281 | 9.4567 | 9.3725 | 9.2661 | 9.1377 | 9.0085 | 8.8981 | 8.6568 | 8.2823 | 8.0219 | 7.7811
|  | CHILTON CANTELLO | LW |  |  | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 9.6996 | 9.5566 | 9.4488 | 9.2108 | 8.9572 | 8.7562 | 8.5573 | 14.4409 | 14.436 | 14.429 | 14.4207 | 14.4111 | 14.4001 | 9.6274 | 9.4494 | 9.2799 | 9.1522 | 8.8702 | 8.5648 | 8.322 | 8.0818 | 9.6771 | 9.6347 | 9.5754 | 9.5043 | 9.4224 | 9.329 | 9.2096 | 9.0712 | 8.9394 | 8.8402 | 8.6209 | 8.3418 | 8.0994 | 7.8597
|  | CHILTON CANTELLO | ST |  |  | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 9.7044 | 9.478 | 9.2382 | 9.0968 | 8.9663 | 14.5173 | 14.439 | 14.4351 | 14.4304 | 14.4248 | 14.4163 | 14.406 | 9.714 | 9.5772 | 9.4551 | 9.1868 | 8.9027 | 8.7335 | 8.5758 | 15.1407 | 9.6609 | 9.6277 | 9.5876 | 9.5398 | 9.4666 | 9.379 | 9.2769 | 9.1706 | 9.0756 | 8.8671 | 8.6462 | 8.5101 | 8.3528
|  | CHILTON CANTELLO | FS |  |  | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 15.7022 | 14.5218 | 14.441 | 14.439 | 14.4366 | 14.4339 | 14.4304 | 14.4262 | 14.4213 | 14.4165 | 14.4123 | 14.4031 | 9.6956 | 9.6273 | 9.5733 | 15.1407 | 9.6779 | 9.6603 | 9.6399 | 9.6174 | 9.5869 | 9.5511 | 9.5099 | 9.4686 | 9.4331 | 9.3547 | 9.2626 | 9.2095 | 9.1676
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM | MINIMUM HEADROOM | SU 65105 55805 | YES | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 32.896 | 32.6967 | 32.5201 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 26.3784 | 25.4104 | 24.4409 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 26.3616
|  | CHINEHAM | CT |  |  | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 32.9068 | 32.7324 | 32.5517 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 25.7479 | 24.7517 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 26.6644
|  | CHINEHAM | LW |  |  | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 32.896 | 32.6967 | 32.5201 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 26.3784 | 25.4104 | 24.4409 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 26.3616
|  | CHINEHAM | ST |  |  | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 32.9567 | 32.861 | 32.6787 | 32.5882 | 32.4881 | 32.4336 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 32.4286 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195
|  | CHINEHAM | FS |  |  | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 38.5831 | 33.484 | 32.9599 | 32.9178 | 32.8422 | 32.7537 | 32.6966 | 32.6631 | 32.6442 | 32.6253 | 32.6068 | 32.5718 | 32.489 | 32.4286 | 32.4286 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195 | 35.195
COWLEY GSP | YARNTON BSP | CHIPPING NORTON | MINIMUM HEADROOM | SP 31382 26792 | YES | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 14.1592 | 13.6348 | 13.0935 | 12.5458 | 17.8951 | 17.877 | 17.8526 | 17.8237 | 17.7913 | 17.7604 | 17.7306 | 17.7034 | 17.6825 | 17.6755 | 17.6655 | 17.6648 | 13.1062 | 12.6597 | 17.3423 | 17.3379 | 17.3318 | 17.3247 | 17.3167 | 17.3091 | 13.3017 | 13.1972 | 13.1167 | 13.0765 | 12.965 | 12.3031 | 11.6198 | 10.9285
|  | CHIPPING NORTON | CT |  |  | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 14.1592 | 13.6348 | 13.0935 | 12.5458 | 17.8956 | 17.8799 | 17.858 | 17.8328 | 17.8041 | 17.7756 | 17.7469 | 17.7185 | 17.6933 | 17.6766 | 17.6655 | 17.6648 | 13.1166 | 12.6768 | 17.3424 | 17.3386 | 17.3332 | 17.327 | 17.3199 | 17.3129 | 17.3058 | 13.2554 | 13.1579 | 13.0887 | 12.9652 | 12.3092 | 11.636 | 10.955
|  | CHIPPING NORTON | LW |  |  | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 14.1592 | 13.6348 | 13.0935 | 12.5458 | 17.8951 | 17.877 | 17.8526 | 17.8237 | 17.7913 | 17.7604 | 17.7306 | 17.7034 | 17.6825 | 17.6755 | 17.6655 | 17.6648 | 13.1062 | 12.6597 | 17.3423 | 17.3379 | 17.3318 | 17.3247 | 17.3167 | 17.3091 | 13.3017 | 13.1972 | 13.1167 | 13.0765 | 12.965 | 12.3031 | 11.6198 | 10.9285
|  | CHIPPING NORTON | ST |  |  | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 14.173 | 13.841 | 13.5152 | 13.1885 | 17.8989 | 17.8885 | 17.8753 | 17.8589 | 17.8392 | 17.8085 | 17.7777 | 17.7474 | 17.7179 | 17.6935 | 17.6671 | 17.6648 | 17.6648 | 13.1836 | 17.3432 | 17.3407 | 17.3374 | 17.3334 | 17.3285 | 17.321 | 17.3134 | 17.3059 | 13.2528 | 13.1588 | 12.9825 | 12.5634 | 12.1521 | 11.7397
|  | CHIPPING NORTON | FS |  |  | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 15.9376 | 17.9018 | 17.896 | 17.8898 | 17.882 | 17.8734 | 17.8611 | 17.8492 | 17.8364 | 17.8249 | 17.8157 | 17.7975 | 17.7545 | 17.7124 | 17.6746 | 17.344 | 17.3425 | 17.341 | 17.3391 | 17.337 | 17.3339 | 17.331 | 17.3278 | 17.325 | 17.3227 | 17.3182 | 17.3076 | 13.2316 | 13.0664
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE | MINIMUM HEADROOM | SU 80226 89155 | YES | 11.0134 | 11.012 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 10.764 | 10.7556 | 10.7356 | 10.714 | 10.6926 | 10.6715 | 10.6505 | 10.6298 | 10.6075 | 10.5854 | 10.5418 | 10.4615 | 10.3789 | 10.3186 | 10.8407 | 10.8372 | 10.8289 | 10.8199 | 10.811 | 10.8021 | 10.7934 | 10.7848 | 10.7755 | 10.7663 | 10.7481 | 10.7146 | 10.6802 | 10.6553
|  | CHISBRIDGE | CT |  |  | 11.0134 | 11.012 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 10.764 | 10.7556 | 10.7356 | 10.714 | 10.6926 | 10.6715 | 10.6505 | 10.6298 | 10.6075 | 10.5854 | 10.5418 | 10.4615 | 10.3789 | 10.3186 | 10.8407 | 10.8372 | 10.8289 | 10.8199 | 10.811 | 10.8021 | 10.7934 | 10.7848 | 10.7755 | 10.7663 | 10.7481 | 10.7146 | 10.6802 | 10.6553
|  | CHISBRIDGE | LW |  |  | 11.0134 | 11.012 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 10.7652 | 10.7587 | 10.7432 | 10.7265 | 10.7099 | 10.6935 | 10.6773 | 10.6612 | 10.6438 | 10.6266 | 10.5926 | 10.5186 | 10.4424 | 10.3675 | 10.8412 | 10.8385 | 10.8321 | 10.8251 | 10.8182 | 10.8113 | 10.8046 | 10.7979 | 10.7906 | 10.7834 | 10.7693 | 10.7384 | 10.7067 | 10.6755
|  | CHISBRIDGE | ST |  |  | 11.014 | 11.0133 | 11.0119 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 10.7677 | 10.7647 | 10.7582 | 10.7483 | 10.7364 | 10.7274 | 10.7185 | 10.7097 | 10.7003 | 10.691 | 10.6729 | 10.6286 | 10.5845 | 10.5406 | 10.8423 | 10.841 | 10.8383 | 10.8342 | 10.8292 | 10.8254 | 10.8217 | 10.8181 | 10.8142 | 10.8103 | 10.8027 | 10.7843 | 10.7659 | 10.7476
|  | CHISBRIDGE | FS |  |  | 11.0143 | 11.0143 | 11.0142 | 11.0137 | 11.0131 | 11.0124 | 11.0117 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 11.0113 | 10.7693 | 10.769 | 10.7686 | 10.7662 | 10.7634 | 10.7602 | 10.7571 | 10.753 | 10.749 | 10.7451 | 10.7375 | 10.7192 | 10.702 | 10.6858 | 10.8429 | 10.8428 | 10.8426 | 10.8416 | 10.8405 | 10.8391 | 10.8378 | 10.8361 | 10.8345 | 10.8328 | 10.8296 | 10.8221 | 10.8149 | 10.8081
MINETY GSP | TOOTHILL BSP | CHISLEDON | MINIMUM HEADROOM | SU 18894 79934 | YES | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 13.8887 | 13.5568 | 13.227 | 19.2267 | 19.1259 | 18.9751 | 18.789 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 12.218 | 11.1403 | 10.6503 | 10.2505 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 11.9247 | 10.8749 | 10.3976 | 10.0082
|  | CHISLEDON | CT |  |  | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 13.8887 | 13.5568 | 13.227 | 19.2297 | 19.1443 | 19.0135 | 18.8553 | 18.6563 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 12.5977 | 11.1404 | 10.6503 | 10.2505 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 12.2945 | 10.875 | 10.3976 | 10.0082
|  | CHISLEDON | LW |  |  | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 13.8887 | 13.5568 | 13.227 | 19.2267 | 19.1259 | 18.9751 | 18.789 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 12.218 | 11.1403 | 10.7506 | 10.3635 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 11.9247 | 10.8749 | 10.4953 | 10.1183
|  | CHISLEDON | ST |  |  | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 19.3121 | 19.1853 | 19.1046 | 18.9993 | 18.8616 | 18.7076 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 13.3354 | 13.0445 | 12.8156 | 18.232 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 13.013 | 12.7297 | 12.5068
|  | CHISLEDON | FS |  |  | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 21.5808 | 19.324 | 19.2228 | 19.1847 | 19.135 | 19.0737 | 19.0058 | 18.9324 | 18.8512 | 18.7604 | 18.6602 | 18.5867 | 18.5867 | 18.5867 | 18.5867 | 18.2398 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888 | 18.1888
BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM | MINIMUM HEADROOM | SU 97173 63223 | NO | 23.3113 | 23.2621 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36
|  | CHOBHAM | CT |  |  | 23.3113 | 23.2621 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36
|  | CHOBHAM | LW |  |  | 23.3113 | 23.2621 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36
|  | CHOBHAM | ST |  |  | 23.4144 | 23.3161 | 35.5671 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 34.2649 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36
|  | CHOBHAM | FS |  |  | 23.421 | 23.3356 | 35.615 | 35.5984 | 35.5825 | 35.5613 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 35.5471 | 34.2733 | 34.1649 | 34.1578 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 34.1469 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36 | 21.36
COWLEY GSP | DRAYTON BSP | CHOLSEY | MINIMUM HEADROOM | SU 58223 84685 | YES | 16.3516 | 16.3326 | 16.2966 | 16.2577 | 16.2189 | 16.1803 | 16.1419 | 16.1037 | 16.0627 | 16.0207 | 15.9355 | 14.116 | 13.6521 | 13.1815 | 13.1173 | 13.0776 | 12.9964 | 12.9088 | 12.8206 | 12.7322 | 12.6448 | 12.5588 | 12.4662 | 12.3746 | 12.1917 | 11.6862 | 11.1149 | 10.5391 | 13.118 | 13.0785 | 12.9975 | 12.9101 | 12.8222 | 12.734 | 12.6469 | 12.5612 | 12.4689 | 12.3776 | 12.1952 | 11.6912 | 11.1217 | 10.5476
|  | CHOLSEY | CT |  |  | 16.3516 | 16.3326 | 16.2966 | 16.2577 | 16.2189 | 16.1803 | 16.1419 | 16.1037 | 16.0627 | 16.0207 | 15.9355 | 14.116 | 13.6521 | 13.1815 | 13.1173 | 13.0776 | 12.9964 | 12.9088 | 12.8206 | 12.7322 | 12.6448 | 12.5588 | 12.4662 | 12.3746 | 12.1917 | 11.6862 | 11.1149 | 10.5391 | 13.118 | 13.0785 | 12.9975 | 12.9101 | 12.8222 | 12.734 | 12.6469 | 12.5612 | 12.4689 | 12.3776 | 12.1952 | 11.6912 | 11.1217 | 10.5476
|  | CHOLSEY | LW |  |  | 16.3516 | 16.3326 | 16.2966 | 16.2577 | 16.2189 | 16.1803 | 16.1419 | 16.1037 | 16.0627 | 16.0207 | 15.9355 | 14.116 | 13.6521 | 13.1815 | 13.1221 | 13.0898 | 13.0285 | 12.9622 | 12.8961 | 12.8303 | 12.7649 | 12.6998 | 12.63 | 12.5584 | 12.4132 | 11.9413 | 11.3921 | 10.8351 | 13.1228 | 13.0906 | 13.0295 | 12.9634 | 12.8975 | 12.8319 | 12.7667 | 12.7018 | 12.6322 | 12.5608 | 12.416 | 11.9456 | 11.3981 | 10.8427
|  | CHOLSEY | ST |  |  | 16.4931 | 16.3604 | 16.3566 | 16.3512 | 16.3442 | 16.3125 | 16.2812 | 16.2506 | 16.2177 | 16.1853 | 16.121 | 15.9591 | 15.7783 | 14.0259 | 13.3267 | 13.1371 | 13.1306 | 13.1215 | 13.1096 | 13.0555 | 13.0022 | 12.9502 | 12.894 | 12.8388 | 12.7293 | 12.4534 | 12.1454 | 11.8346 | 13.3268 | 13.1377 | 13.1313 | 13.1222 | 13.1103 | 13.0564 | 13.0033 | 12.9514 | 12.8954 | 12.8404 | 12.7312 | 12.4561 | 12.1491 | 11.8392
|  | CHOLSEY | FS |  |  | 16.4974 | 16.4942 | 16.4923 | 16.4841 | 16.4747 | 16.4607 | 16.4469 | 16.4293 | 16.4119 | 16.3949 | 16.3618 | 16.294 | 16.2254 | 16.1506 | 13.3329 | 13.3283 | 13.3256 | 13.3139 | 13.3004 | 13.2804 | 13.2607 | 13.2355 | 13.2107 | 13.1864 | 13.139 | 13.0241 | 12.9072 | 12.7798 | 13.333 | 13.3284 | 13.3257 | 13.314 | 13.3005 | 13.2806 | 13.2609 | 13.2358 | 13.2111 | 13.1869 | 13.1397 | 13.0251 | 12.9085 | 12.7815
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH | MINIMUM HEADROOM | SZ 15698 93141 | YES | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 35.696 | 35.6745 | 35.6314 | 35.5912 | 35.5551 | 35.519 | 35.5107 | 35.5018 | 35.4895 | 35.4772 | 35.4532 | 35.3799 | 35.2908 | 27.0458 | 36.4531 | 36.4442 | 36.4262 | 36.4069 | 36.3853 | 36.3628 | 36.3374 | 36.3101 | 36.2941 | 36.2941 | 36.2941 | 36.2941 | 36.2941 | 36.2941
|  | CHRISTCHURCH | CT |  |  | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 35.6966 | 35.6765 | 35.6352 | 35.5954 | 35.5613 | 35.5252 | 35.5125 | 35.5043 | 35.4957 | 35.487 | 35.47 | 35.3884 | 35.304 | 27.4008 | 36.4533 | 36.445 | 36.4277 | 36.4094 | 36.389 | 36.3674 | 36.3428 | 36.3177 | 36.2941 | 36.2941 | 36.2941 | 36.2941 | 36.2941 | 36.2941
|  | CHRISTCHURCH | LW |  |  | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 35.696 | 35.6745 | 35.6314 | 35.5912 | 35.5551 | 35.519 | 35.5107 | 35.5023 | 35.4934 | 35.4841 | 35.4659 | 35.3799 | 35.2908 | 27.0458 | 36.4531 | 36.4442 | 36.4262 | 36.4069 | 36.3853 | 36.3628 | 36.3374 | 36.3116 | 36.2941 | 36.2941 | 36.2941 | 36.2941 | 36.2941 | 36.2941
|  | CHRISTCHURCH | ST |  |  | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 35.7022 | 35.6902 | 35.6681 | 35.6389 | 35.6027 | 35.5469 | 35.5133 | 35.5018 | 35.4895 | 35.4772 | 35.4532 | 35.394 | 35.3355 | 35.277 | 36.4557 | 36.4507 | 36.4415 | 36.4293 | 36.4138 | 36.3803 | 36.3452 | 36.3101 | 36.2941 | 36.2941 | 36.2941 | 36.2941 | 36.2941 | 36.2941
|  | CHRISTCHURCH | FS |  |  | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 40.4436 | 35.7073 | 35.7032 | 35.6977 | 35.6886 | 35.6776 | 35.6522 | 35.6258 | 35.5973 | 35.5751 | 35.5526 | 35.5172 | 35.4962 | 35.4749 | 35.4534 | 36.4578 | 36.4561 | 36.4538 | 36.45 | 36.4454 | 36.4349 | 36.4239 | 36.4106 | 36.3973 | 36.3838 | 36.3574 | 36.2941 | 36.2941 | 36.2941
LALEHAM | EAST BEDFONT A | CHURCH ROAD | MINIMUM HEADROOM | TQ 06820 71722 | NO | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 26.2315 | 26.2282 | 26.2093 | 26.1872 | 26.178 | 26.1681 | 26.1328 | 26.0963 | 26.0573 | 26.02 | 25.9482 | 25.762 | 25.6198 | 25.4428 | 27.1869 | 27.1745 | 27.1367 | 27.129 | 27.1258 | 27.1224 | 27.1101 | 27.0974 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094
|  | CHURCH ROAD | CT |  |  | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 26.2315 | 26.2283 | 26.2107 | 26.1905 | 26.1822 | 26.1739 | 26.1644 | 26.1524 | 26.1402 | 26.1295 | 26.11 | 25.9037 | 25.6976 | 25.5561 | 27.187 | 27.1747 | 27.1372 | 27.1302 | 27.1273 | 27.1244 | 27.1211 | 27.1169 | 27.1127 | 27.109 | 27.1022 | 27.094 | 27.094 | 27.094
|  | CHURCH ROAD | LW |  |  | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 26.2315 | 26.2282 | 26.2093 | 26.1872 | 26.178 | 26.1689 | 26.1601 | 26.1514 | 26.1419 | 26.1322 | 26.113 | 25.8381 | 25.6198 | 25.4428 | 27.1869 | 27.1745 | 27.1367 | 27.129 | 27.1258 | 27.1227 | 27.1196 | 27.1166 | 27.1133 | 27.1099 | 27.1032 | 27.094 | 27.094 | 27.094
|  | CHURCH ROAD | ST |  |  | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 26.2328 | 26.2313 | 26.2215 | 26.2088 | 26.2032 | 26.1681 | 26.1328 | 26.0963 | 26.0573 | 26.02 | 25.9482 | 25.762 | 25.6301 | 25.5097 | 27.1919 | 27.1862 | 27.1489 | 27.1366 | 27.1346 | 27.1224 | 27.1101 | 27.0974 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094
|  | CHURCH ROAD | FS |  |  | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 30.6242 | 26.2336 | 26.2333 | 26.2293 | 26.224 | 26.2222 | 26.211 | 26.1998 | 26.1857 | 26.172 | 26.1584 | 26.1317 | 26.0662 | 25.9988 | 25.9309 | 27.1949 | 27.1939 | 27.1788 | 27.1584 | 27.1515 | 27.1373 | 27.1334 | 27.1285 | 27.1237 | 27.119 | 27.1097 | 27.094 | 27.094 | 27.094
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN | MINIMUM HEADROOM | SP 02761 00827 | YES | 23.4206 | 23.3805 | 23.3736 | 23.3659 | 23.3567 | 23.3468 | 23.3363 | 23.3262 | 23.3157 | 23.3045 | 23.2827 | 23.1969 | 19.6505 | 18.6773 | 21.3945 | 21.2667 | 21.2446 | 21.2201 | 21.1906 | 21.159 | 21.1447 | 21.1447 | 21.1447 | 21.1447 | 21.1447 | 18.6197 | 17.4774 | 16.3309 | 18.6633 | 18.1712 | 18.0861 | 17.9916 | 17.8782 | 17.7565 | 17.6282 | 17.5039 | 17.3757 | 17.2371 | 16.9694 | 15.9167 | 14.7779 | 13.6349
|  | CIRENCESTER TOWN | CT |  |  | 23.4206 | 23.3805 | 23.3736 | 23.3659 | 23.3567 | 23.3468 | 23.3363 | 23.3262 | 23.3157 | 23.3045 | 23.2827 | 23.1969 | 19.6505 | 18.6773 | 21.3955 | 21.2689 | 21.2497 | 21.2283 | 21.2025 | 21.1749 | 21.1454 | 21.1447 | 21.1447 | 21.1447 | 21.1447 | 21.1447 | 17.8528 | 16.7766 | 18.6672 | 18.1798 | 18.1056 | 18.0233 | 17.924 | 17.8176 | 17.704 | 17.5988 | 17.4937 | 17.3844 | 17.1768 | 16.2141 | 15.1522 | 14.0793
|  | CIRENCESTER TOWN | LW |  |  | 23.4206 | 23.3805 | 23.3736 | 23.3659 | 23.3567 | 23.3468 | 23.3363 | 23.3262 | 23.3157 | 23.3045 | 23.2827 | 23.1969 | 19.6505 | 18.6773 | 21.3945 | 21.2667 | 21.2446 | 21.2201 | 21.1906 | 21.159 | 21.1447 | 21.1447 | 21.1447 | 21.1447 | 21.1447 | 18.6197 | 17.4774 | 16.3309 | 18.6633 | 18.1712 | 18.0861 | 17.9916 | 17.8782 | 17.7565 | 17.6282 | 17.5039 | 17.3757 | 17.2371 | 16.9694 | 15.9167 | 14.7779 | 13.6349
|  | CIRENCESTER TOWN | ST |  |  | 23.4216 | 23.4199 | 23.4163 | 23.4108 | 23.4031 | 23.3955 | 23.3875 | 23.38 | 23.3723 | 23.3645 | 23.3494 | 23.2977 | 23.2431 | 23.1892 | 21.3977 | 21.3923 | 21.3807 | 21.3631 | 21.3388 | 21.3144 | 21.2889 | 21.265 | 21.2406 | 21.2155 | 21.1676 | 21.1447 | 21.1447 | 18.5239 | 18.6757 | 18.6548 | 18.6104 | 18.5425 | 18.4489 | 18.355 | 18.2568 | 18.1647 | 18.0706 | 17.9739 | 17.7896 | 17.1539 | 16.4832 | 15.8212
|  | CIRENCESTER TOWN | FS |  |  | 23.4225 | 23.4224 | 23.4222 | 23.4209 | 23.4192 | 23.4167 | 23.4142 | 23.4112 | 23.4083 | 23.4053 | 23.3996 | 23.3806 | 23.3587 | 23.3353 | 21.4007 | 21.4001 | 21.3995 | 21.3956 | 21.39 | 21.382 | 21.374 | 21.3644 | 21.3553 | 21.3457 | 21.3275 | 21.2669 | 21.197 | 21.1447 | 18.6873 | 18.685 | 18.6826 | 18.6677 | 18.646 | 18.6154 | 18.5844 | 18.5477 | 18.5124 | 18.4756 | 18.4053 | 18.1719 | 17.9027 | 17.6163
IVER 132KV | CIPPENHAM | CLARENCE ROAD | MINIMUM HEADROOM | SU 95654 76652 | NO | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 40.1544 | 37.8406 | 35.3758 | 32.9147 | 46.3442 | 46.2526 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 40.7773 | 39.8386 | 38.828 | 37.8209 | 35.9802 | 33.2577 | 30.3574 | 27.4615 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 40.1914 | 39.2126 | 37.4236 | 34.7776 | 31.9588 | 29.0944
|  | CLARENCE ROAD | CT |  |  | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 40.1544 | 37.8406 | 35.3758 | 32.9147 | 46.3454 | 46.2558 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 39.9921 | 39.0088 | 38.0196 | 36.1859 | 33.4806 | 30.5546 | 27.6291 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 40.3671 | 39.4056 | 37.6235 | 34.9943 | 32.1505 | 29.2617
|  | CLARENCE ROAD | LW |  |  | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 40.1544 | 37.8406 | 35.3758 | 32.9147 | 46.3442 | 46.2526 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 40.7773 | 39.8386 | 38.828 | 37.8209 | 35.9802 | 33.2577 | 30.3574 | 27.4615 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 40.1914 | 39.2126 | 37.4236 | 34.7776 | 31.9588 | 29.0944
|  | CLARENCE ROAD | ST |  |  | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 46.3856 | 46.3545 | 46.2873 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 40.5869 | 38.8887 | 37.1916 | 47.4197 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 40.2504 | 38.601
|  | CLARENCE ROAD | FS |  |  | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 49.0708 | 46.4001 | 46.3942 | 46.3869 | 46.3491 | 46.3024 | 46.2715 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 46.2407 | 47.4759 | 47.453 | 47.4247 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301 | 47.3301
MELKSHAM GSP | CHIPPENHAM | COCKLEBURY | MINIMUM HEADROOM | ST 92447 73890 | YES | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 34.7165 | 41.8888 | 41.7747 | 41.6147 | 41.4904 | 41.3537 | 41.1986 | 41.0635 | 40.9905 | 40.9105 | 40.8284 | 40.6789 | 35.2655 | 33.7461 | 32.2199 | 42.5678 | 42.5573 | 42.5322 | 42.5021 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 35.0016 | 33.5204 | 32.0207
|  | COCKLEBURY | CT |  |  | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 34.7165 | 41.8929 | 41.7849 | 41.624 | 41.507 | 41.3795 | 41.2368 | 41.0939 | 41.0221 | 40.9496 | 40.8735 | 40.7303 | 35.489 | 33.9673 | 32.4645 | 42.5682 | 42.5583 | 42.5345 | 42.5061 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 35.2218 | 33.7359 | 32.2654
|  | COCKLEBURY | LW |  |  | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 34.7165 | 41.8888 | 41.7747 | 41.6147 | 41.4904 | 41.3537 | 41.1986 | 41.0635 | 40.9905 | 40.9105 | 40.8284 | 40.6789 | 35.2655 | 33.7461 | 32.2199 | 42.5678 | 42.5573 | 42.5322 | 42.5021 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 35.0016 | 33.5204 | 32.0207
|  | COCKLEBURY | ST |  |  | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 41.9302 | 41.8744 | 41.7517 | 41.6338 | 41.5328 | 41.4545 | 41.3746 | 41.2904 | 41.1951 | 41.095 | 41.0056 | 40.8389 | 40.6856 | 40.6612 | 42.5716 | 42.5665 | 42.5552 | 42.5365 | 42.5124 | 42.4934 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796 | 42.4796
|  | COCKLEBURY | FS |  |  | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 43.578 | 41.9598 | 41.9535 | 41.9459 | 41.8908 | 41.8198 | 41.7469 | 41.6956 | 41.649 | 41.6063 | 41.567 | 41.4955 | 41.3469 | 41.2086 | 41.0802 | 42.5743 | 42.5738 | 42.5731 | 42.568 | 42.5615 | 42.5548 | 42.5478 | 42.5392 | 42.5302 | 42.5207 | 42.5033 | 42.4796 | 42.4796 | 42.4796
MELKSHAM GSP | FROME BSP | CODFORD | MINIMUM HEADROOM | ST 97372 39559 | YES | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.8349 | 18.8324 | 18.8269 | 18.8186 | 18.8086 | 18.8053 | 18.802 | 18.7988 | 18.7952 | 18.7917 | 18.7848 | 18.7671 | 18.7496 | 18.731 | 16.1403 | 16.1391 | 16.1363 | 16.1321 | 16.1271 | 16.1255 | 16.1238 | 16.1222 | 16.1204 | 16.1187 | 16.1152 | 16.1063 | 16.0975 | 16.0882
|  | CODFORD | CT |  |  | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.836 | 18.8354 | 18.834 | 18.8324 | 18.8307 | 18.829 | 18.8273 | 18.8255 | 18.8236 | 18.8216 | 18.8176 | 18.7893 | 18.76 | 18.731 | 16.1409 | 16.1406 | 16.1398 | 16.139 | 16.1382 | 16.1374 | 16.1365 | 16.1356 | 16.1346 | 16.1337 | 16.1317 | 16.1174 | 16.1027 | 16.0882
|  | CODFORD | LW |  |  | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.836 | 18.8354 | 18.834 | 18.8324 | 18.8307 | 18.829 | 18.8272 | 18.8253 | 18.8233 | 18.8212 | 18.817 | 18.789 | 18.7601 | 18.7314 | 16.1409 | 16.1406 | 16.1398 | 16.139 | 16.1382 | 16.1373 | 16.1364 | 16.1355 | 16.1345 | 16.1335 | 16.1313 | 16.1173 | 16.1028 | 16.0884
|  | CODFORD | ST |  |  | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.8349 | 18.8324 | 18.8269 | 18.8186 | 18.8086 | 18.8053 | 18.802 | 18.7988 | 18.7952 | 18.7917 | 18.7848 | 18.7671 | 18.7496 | 18.7322 | 16.1403 | 16.1391 | 16.1363 | 16.1321 | 16.1271 | 16.1255 | 16.1238 | 16.1222 | 16.1204 | 16.1187 | 16.1152 | 16.1063 | 16.0975 | 16.0888
|  | CODFORD | FS |  |  | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.3444 | 18.8364 | 18.8364 | 18.8363 | 18.8361 | 18.8358 | 18.8347 | 18.8336 | 18.8321 | 18.8307 | 18.8293 | 18.8265 | 18.8197 | 18.813 | 18.8065 | 16.1411 | 16.1411 | 16.141 | 16.1409 | 16.1408 | 16.1402 | 16.1396 | 16.1389 | 16.1382 | 16.1375 | 16.1361 | 16.1327 | 16.1293 | 16.1261
IVER 132KV | DENHAM | COKES LANE | MINIMUM HEADROOM | SU 99240 97483 | NO | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.6326 | 23.5593 | 23.4071 | 23.2398 | 23.0698 | 22.8966 | 22.7675 | 22.6571 | 22.5389 | 22.4215 | 22.1907 | 21.9575 | 21.7166 | 11.0331 | 9.5613 | 9.557 | 9.5479 | 9.538 | 9.5279 | 9.5176 | 9.509 | 9.5006 | 9.4917 | 9.4828 | 9.4654 | 9.4478 | 9.4296 | 9.411
|  | COKES LANE | CT |  |  | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.6368 | 23.5715 | 23.4344 | 23.2844 | 23.1315 | 22.9743 | 22.8392 | 22.7332 | 22.6206 | 22.5082 | 22.293 | 22.0227 | 21.7451 | 11.0331 | 9.5616 | 9.5577 | 9.5496 | 9.5407 | 9.5316 | 9.5222 | 9.5142 | 9.5064 | 9.4979 | 9.4894 | 9.4731 | 9.4527 | 9.4317 | 9.411
|  | COKES LANE | LW |  |  | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.6326 | 23.5593 | 23.4071 | 23.2398 | 23.0698 | 22.8966 | 22.7675 | 22.6571 | 22.5389 | 22.4215 | 22.1907 | 21.9575 | 21.7166 | 11.0413 | 9.5613 | 9.557 | 9.5479 | 9.538 | 9.5279 | 9.5176 | 9.509 | 9.5006 | 9.4917 | 9.4828 | 9.4654 | 9.4478 | 9.4296 | 9.4115
|  | COKES LANE | ST |  |  | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.6555 | 23.6156 | 23.5398 | 23.4298 | 23.2974 | 23.242 | 23.201 | 23.1613 | 23.1177 | 23.0738 | 22.9932 | 22.8161 | 22.6757 | 22.5359 | 9.5627 | 9.5603 | 9.5558 | 9.5493 | 9.5414 | 9.5381 | 9.5357 | 9.5333 | 9.5308 | 9.5282 | 9.5234 | 9.5126 | 9.502 | 9.4915
|  | COKES LANE | FS |  |  | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.0227 | 23.6745 | 23.6643 | 23.653 | 23.6215 | 23.585 | 23.5633 | 23.5481 | 23.5302 | 23.5124 | 23.4949 | 23.4615 | 23.3863 | 23.3162 | 23.2492 | 9.5638 | 9.5632 | 9.5625 | 9.5607 | 9.5585 | 9.5572 | 9.5563 | 9.5552 | 9.5542 | 9.5531 | 9.5512 | 9.5467 | 9.5425 | 9.5386
LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK | MINIMUM HEADROOM | SU 65893 02686 | NO | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 14.8542 | 14.8532 | 14.8511 | 14.8487 | 14.8463 | 14.841 | 14.8319 | 14.8228 | 14.8131 | 14.8035 | 14.7847 | 14.7369 | 14.6848 | 14.6332 | 15.9109 | 15.9084 | 15.9026 | 15.8963 | 15.8898 | 15.8756 | 15.8512 | 15.8271 | 15.8011 | 15.7755 | 15.7253 | 15.5973 | 15.4721 | 15.42
|  | COLLEGE PARK | CT |  |  | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 14.8542 | 14.8533 | 14.8511 | 14.8488 | 14.8464 | 14.8441 | 14.8417 | 14.8393 | 14.8368 | 14.8342 | 14.8289 | 14.7898 | 14.7428 | 14.6956 | 15.9109 | 15.9084 | 15.9027 | 15.8964 | 15.8901 | 15.8838 | 15.8776 | 15.8712 | 15.8643 | 15.8574 | 15.8434 | 15.7389 | 15.6132 | 15.4871
|  | COLLEGE PARK | LW |  |  | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 14.8542 | 14.8532 | 14.8511 | 14.8487 | 14.8463 | 14.8439 | 14.8416 | 14.8392 | 14.8366 | 14.834 | 14.8288 | 14.7766 | 14.7118 | 14.6472 | 15.9109 | 15.9084 | 15.9026 | 15.8963 | 15.8898 | 15.8835 | 15.8772 | 15.8708 | 15.8639 | 15.857 | 15.8431 | 15.7035 | 15.5304 | 15.4342
|  | COLLEGE PARK | ST |  |  | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 14.9529 | 14.8541 | 14.8532 | 14.8519 | 14.8502 | 14.841 | 14.8319 | 14.8228 | 14.8131 | 14.8035 | 14.7847 | 14.7369 | 14.6848 | 14.6332 | 15.9647 | 15.9107 | 15.9083 | 15.9047 | 15.9003 | 15.8756 | 15.8512 | 15.8271 | 15.8011 | 15.7755 | 15.7253 | 15.5973 | 15.4721 | 15.42
|  | COLLEGE PARK | FS |  |  | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 16.3988 | 14.9541 | 14.8547 | 14.8546 | 14.8542 | 14.8537 | 14.8514 | 14.849 | 14.846 | 14.8431 | 14.8402 | 14.8345 | 14.8211 | 14.8069 | 14.7913 | 15.9653 | 15.9122 | 15.912 | 15.9109 | 15.9097 | 15.9034 | 15.8971 | 15.8891 | 15.8812 | 15.8734 | 15.8582 | 15.8224 | 15.7844 | 15.7427
BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS | MINIMUM HEADROOM | SU 88285 81857 | YES | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 26.4237 | 25.0303 | 23.6298 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 25.7274 | 24.3264
|  | CORDWALLIS | CT |  |  | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 26.4237 | 25.0303 | 23.6298 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 25.7274 | 24.3264
|  | CORDWALLIS | LW |  |  | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 26.5268 | 25.178 | 23.8253 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 25.8751 | 24.522
|  | CORDWALLIS | ST |  |  | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 33.0535 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305
|  | CORDWALLIS | FS |  |  | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 37.37 | 33.0894 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.0444 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305
MANNINGTON GSP | LYTCHETT | CORFE MULLEN | MINIMUM HEADROOM | SY 98583 96071 | YES | 41.7733 | 41.7699 | 41.7657 | 41.7607 | 41.7532 | 41.7436 | 41.7306 | 41.7165 | 41.7051 | 41.6919 | 41.6656 | 41.5834 | 41.4862 | 41.4024 | 37.5167 | 37.4746 | 37.4242 | 37.3632 | 37.2711 | 37.154 | 37.0068 | 36.9217 | 36.8524 | 36.7725 | 36.6134 | 36.2137 | 36.2137 | 36.2137 | 38.7124 | 38.6762 | 38.6431 | 38.6222 | 38.5906 | 38.5504 | 38.4956 | 38.4366 | 38.3885 | 38.3332 | 38.2229 | 38.0986 | 38.0986 | 38.0986
|  | CORFE MULLEN | CT |  |  | 41.7733 | 41.7699 | 41.7657 | 41.7607 | 41.7532 | 41.7436 | 41.7306 | 41.7165 | 41.7079 | 41.6997 | 41.6834 | 41.5834 | 41.4862 | 41.4024 | 37.5177 | 37.4794 | 37.4308 | 37.3727 | 37.2861 | 37.1758 | 37.0328 | 36.9515 | 36.9019 | 36.851 | 36.748 | 36.2137 | 36.2137 | 36.2137 | 38.7133 | 38.6803 | 38.6454 | 38.6255 | 38.5957 | 38.5579 | 38.5088 | 38.4573 | 38.4229 | 38.3876 | 38.3162 | 38.0986 | 38.0986 | 38.0986
|  | CORFE MULLEN | LW |  |  | 41.7733 | 41.7699 | 41.7657 | 41.7607 | 41.7532 | 41.7436 | 41.7306 | 41.7165 | 41.7079 | 41.6997 | 41.6834 | 41.5834 | 41.4862 | 41.4024 | 37.5167 | 37.4746 | 37.4242 | 37.3632 | 37.2711 | 37.154 | 37.0068 | 36.9217 | 36.8693 | 36.8198 | 36.7215 | 36.2137 | 36.2137 | 36.2137 | 38.7124 | 38.6762 | 38.6431 | 38.6222 | 38.5906 | 38.5504 | 38.4956 | 38.4366 | 38.4003 | 38.366 | 38.2978 | 38.0986 | 38.0986 | 38.0986
|  | CORFE MULLEN | ST |  |  | 41.7742 | 41.7722 | 41.7701 | 41.7669 | 41.7616 | 41.7483 | 41.7334 | 41.7182 | 41.7051 | 41.6919 | 41.6656 | 41.6044 | 41.5463 | 41.4887 | 37.5274 | 37.5033 | 37.4778 | 37.4382 | 37.3732 | 37.2109 | 37.0283 | 36.9317 | 36.8524 | 36.7725 | 36.6134 | 36.2428 | 36.2137 | 36.2137 | 38.7217 | 38.7009 | 38.6789 | 38.648 | 38.6256 | 38.57 | 38.5073 | 38.4435 | 38.3885 | 38.3332 | 38.2229 | 38.0986 | 38.0986 | 38.0986
|  | CORFE MULLEN | FS |  |  | 41.7749 | 41.7741 | 41.7737 | 41.7727 | 41.7709 | 41.7663 | 41.7611 | 41.7548 | 41.7497 | 41.7447 | 41.7348 | 41.7095 | 41.6852 | 41.6628 | 37.5365 | 37.5262 | 37.5215 | 37.5092 | 37.4878 | 37.4315 | 37.3672 | 37.2903 | 37.2283 | 37.1673 | 37.0462 | 36.8793 | 36.7319 | 36.5962 | 38.7295 | 38.7206 | 38.7165 | 38.706 | 38.6875 | 38.6457 | 38.6236 | 38.5972 | 38.5759 | 38.555 | 38.5134 | 38.4072 | 38.305 | 38.2109
MELKSHAM GSP | NORRINGTON | CORSHAM | MINIMUM HEADROOM | ST 86766 69583 | YES | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 8.944 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 9.493 | 8.5412 | 7.5385 | 6.5292 | 9.4803 | 9.4416 | 9.3492 | 9.2488 | 9.1436 | 9.0352 | 8.9237 | 8.8096 | 8.6825 | 8.5535 | 8.2888 | 7.6622 | 7.0022 | 6.3378
|  | CORSHAM | CT |  |  | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 8.944 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 8.684 | 7.7061 | 6.7299 | 9.4813 | 9.4441 | 9.3552 | 9.2586 | 9.158 | 9.0554 | 8.95 | 8.8437 | 8.7274 | 8.6109 | 8.3712 | 7.7563 | 7.1125 | 6.4699
|  | CORSHAM | LW |  |  | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 8.944 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 9.493 | 8.5412 | 7.5385 | 6.5292 | 9.4803 | 9.4416 | 9.3492 | 9.2488 | 9.1436 | 9.0352 | 8.9237 | 8.8096 | 8.6825 | 8.5535 | 8.2888 | 7.6622 | 7.0022 | 6.3378
|  | CORSHAM | ST |  |  | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 8.9736 | 8.3643 | 9.4918 | 9.4689 | 9.4186 | 9.3426 | 9.2478 | 9.1845 | 9.1196 | 9.0542 | 8.9822 | 8.9101 | 8.7611 | 8.3541 | 7.9469 | 7.5458
|  | CORSHAM | FS |  |  | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 15.9048 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 12.7713 | 13.5944 | 13.5944 | 9.4992 | 9.4827 | 9.4622 | 9.4419 | 9.4213 | 9.3948 | 9.3676 | 9.3402 | 9.2842 | 9.1356 | 8.9802 | 8.8204
EAST CLAYDON GSP | BICESTER NORTH | COTTISFORD | MINIMUM HEADROOM | SP 59021 31128 | YES | 438.9985 | 438.9971 | 438.9953 | 438.9929 | 438.9899 | 438.9863 | 438.982 | 438.9769 | 438.9708 | 438.9638 | 438.947 | 438.8868 | 438.7973 | 438.6927 | 338.9165 | 338.914 | 338.9103 | 338.9066 | 338.9024 | 338.898 | 338.8932 | 338.8881 | 338.882 | 338.8751 | 338.8592 | 338.8098 | 338.7439 | 338.6645 | 360.8381 | 360.8336 | 360.8271 | 360.8203 | 360.813 | 360.8051 | 360.7966 | 360.7875 | 360.7765 | 360.7643 | 360.7359 | 360.6477 | 360.5304 | 360.3887
|  | COTTISFORD | CT |  |  | 438.9985 | 438.9971 | 438.9953 | 438.9929 | 438.9899 | 438.9863 | 438.982 | 438.9769 | 438.9708 | 438.9638 | 438.947 | 438.8868 | 438.7973 | 438.6927 | 338.9165 | 338.914 | 338.9103 | 338.9066 | 338.9024 | 338.898 | 338.8932 | 338.8881 | 338.882 | 338.8751 | 338.8592 | 338.8098 | 338.7439 | 338.6645 | 360.8381 | 360.8336 | 360.8271 | 360.8203 | 360.813 | 360.8051 | 360.7966 | 360.7875 | 360.7765 | 360.7643 | 360.7359 | 360.6477 | 360.5304 | 360.3887
|  | COTTISFORD | LW |  |  | 438.9985 | 438.9971 | 438.9953 | 438.9929 | 438.9899 | 438.9863 | 438.982 | 438.9769 | 438.9708 | 438.9638 | 438.947 | 438.8868 | 438.7973 | 438.6927 | 338.9188 | 338.918 | 338.917 | 338.9157 | 338.914 | 338.912 | 338.9096 | 338.9067 | 338.9033 | 338.8994 | 338.89 | 338.8564 | 338.8064 | 338.748 | 360.8422 | 360.8408 | 360.8389 | 360.8366 | 360.8336 | 360.83 | 360.8257 | 360.8206 | 360.8146 | 360.8076 | 360.7908 | 360.7309 | 360.6417 | 360.5376
|  | COTTISFORD | ST |  |  | 438.9998 | 438.9993 | 438.9987 | 438.9979 | 438.9971 | 438.9958 | 438.9945 | 438.993 | 438.9915 | 438.9899 | 438.9864 | 438.972 | 438.9507 | 438.9238 | 338.9196 | 338.9193 | 338.9189 | 338.9185 | 338.918 | 338.9173 | 338.9166 | 338.9157 | 338.9149 | 338.914 | 338.912 | 338.904 | 338.8921 | 338.8771 | 360.8435 | 360.843 | 360.8424 | 360.8416 | 360.8407 | 360.8395 | 360.8382 | 360.8367 | 360.8352 | 360.8336 | 360.8301 | 360.8158 | 360.7946 | 360.7677
|  | COTTISFORD | FS |  |  | 439 | 438.9997 | 438.9993 | 438.9988 | 438.9983 | 438.9977 | 438.997 | 438.9964 | 438.9957 | 438.995 | 438.9934 | 438.9875 | 438.9794 | 438.9704 | 338.9196 | 338.9195 | 338.9193 | 338.919 | 338.9187 | 338.9184 | 338.918 | 338.9176 | 338.9172 | 338.9168 | 338.916 | 338.9127 | 338.9081 | 338.9031 | 360.8436 | 360.8433 | 360.843 | 360.8425 | 360.8419 | 360.8413 | 360.8407 | 360.8401 | 360.8394 | 360.8386 | 360.8371 | 360.8312 | 360.8231 | 360.8142
BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES | MINIMUM HEADROOM | SU 70990 69570 | YES | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 32.0454 | 32.0433 | 32.0382 | 32.0327 | 32.0271 | 32.0215 | 32.0159 | 32.0104 | 32.0044 | 31.9985 | 31.9868 | 31.9376 | 31.8865 | 31.8342 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083
|  | COURAGES | CT |  |  | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 32.0455 | 32.0435 | 32.0387 | 32.0335 | 32.0283 | 32.0231 | 32.0179 | 32.0127 | 32.0072 | 32.0016 | 31.9907 | 31.9402 | 31.8869 | 31.8342 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083
|  | COURAGES | LW |  |  | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 32.0454 | 32.0433 | 32.0382 | 32.0327 | 32.0271 | 32.0215 | 32.0159 | 32.0104 | 32.0044 | 31.9985 | 31.9868 | 31.9376 | 31.8865 | 31.8361 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083
|  | COURAGES | ST |  |  | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 32.0461 | 32.0451 | 32.0427 | 32.0391 | 32.0347 | 32.029 | 32.0234 | 32.0178 | 32.0118 | 32.0059 | 31.9943 | 31.9649 | 31.9348 | 31.9048 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083
|  | COURAGES | FS |  |  | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 36.4571 | 32.1147 | 32.0466 | 32.0464 | 32.0455 | 32.0445 | 32.0425 | 32.0405 | 32.038 | 32.0356 | 32.0331 | 32.0284 | 32.0166 | 32.0049 | 31.9936 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083 | 33.4083
BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE | MINIMUM HEADROOM | SU 85415 55937 | NO | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 58.0385 | 58.0253 | 58.0074 | 57.9874 | 57.9675 | 57.9479 | 57.928 | 57.9082 | 57.8869 | 57.8659 | 57.8259 | 57.6659 | 57.4941 | 57.3231 | 66.3513 | 66.3467 | 66.3405 | 66.3336 | 66.3266 | 66.3198 | 66.3129 | 66.306 | 66.2986 | 66.2913 | 66.2774 | 66.2562 | 66.2562 | 66.2562
|  | COVE | CT |  |  | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 58.0394 | 58.0282 | 58.0129 | 57.9959 | 57.9785 | 57.9608 | 57.9424 | 57.9249 | 57.906 | 57.8875 | 57.853 | 57.7158 | 57.5567 | 57.3962 | 66.3517 | 66.3477 | 66.3424 | 66.3365 | 66.3305 | 66.3243 | 66.3179 | 66.3118 | 66.3052 | 66.2988 | 66.2868 | 66.2562 | 66.2562 | 66.2562
|  | COVE | LW |  |  | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 58.0385 | 58.0253 | 58.0074 | 57.9874 | 57.9675 | 57.9479 | 57.928 | 57.9082 | 57.8869 | 57.8659 | 57.8259 | 57.6659 | 57.4941 | 57.3231 | 66.3513 | 66.3467 | 66.3405 | 66.3336 | 66.3266 | 66.3198 | 66.3129 | 66.306 | 66.2986 | 66.2913 | 66.2774 | 66.2562 | 66.2562 | 66.2562
|  | COVE | ST |  |  | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 58.0446 | 58.0402 | 58.038 | 58.0346 | 58.0301 | 58.0104 | 57.9904 | 57.9713 | 57.9505 | 57.9302 | 57.892 | 57.7982 | 57.6929 | 57.5866 | 66.3535 | 66.3519 | 66.3512 | 66.35 | 66.3484 | 66.3416 | 66.3346 | 66.328 | 66.3207 | 66.3137 | 66.3004 | 66.2678 | 66.2562 | 66.2562
|  | COVE | FS |  |  | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 69.7229 | 58.0464 | 58.0437 | 58.043 | 58.0395 | 58.0354 | 58.029 | 58.0226 | 58.0144 | 58.0063 | 57.9984 | 57.9835 | 57.9481 | 57.9088 | 57.8696 | 66.3541 | 66.3532 | 66.3529 | 66.3517 | 66.3503 | 66.348 | 66.3458 | 66.343 | 66.3401 | 66.3374 | 66.3322 | 66.3199 | 66.3062 | 66.2926
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL | MINIMUM HEADROOM | SP 56113 03074 | NO | 47.4383 | 47.4378 | 47.4371 | 47.4363 | 47.4353 | 47.4341 | 47.4326 | 47.4308 | 47.4283 | 47.4254 | 47.4183 | 47.3932 | 47.3505 | 47.2884 | 17.812 | 17.7269 | 17.5316 | 17.3344 | 17.1165 | 16.8392 | 16.6198 | 16.4308 | 16.2302 | 16.0222 | 15.625 | 14.5673 | 13.4465 | 12.3161 | 17.2418 | 17.1714 | 17.0103 | 16.8475 | 16.6676 | 16.439 | 16.2577 | 16.1013 | 15.9347 | 15.7618 | 15.4309 | 14.5454 | 13.5989 | 12.6382
|  | COWLEY LOCAL | CT |  |  | 47.4383 | 47.4378 | 47.4371 | 47.4363 | 47.4353 | 47.4341 | 47.4326 | 47.4308 | 47.4283 | 47.4254 | 47.4183 | 47.3932 | 47.3505 | 47.2884 | 17.812 | 17.7269 | 17.5316 | 17.3344 | 17.1165 | 16.8392 | 16.6198 | 16.4308 | 16.2302 | 16.0222 | 15.625 | 14.5673 | 13.4465 | 12.3161 | 17.2418 | 17.1714 | 17.0103 | 16.8475 | 16.6676 | 16.439 | 16.2577 | 16.1013 | 15.9347 | 15.7618 | 15.4309 | 14.5454 | 13.5989 | 12.6382
|  | COWLEY LOCAL | LW |  |  | 47.4383 | 47.4378 | 47.4371 | 47.4363 | 47.4353 | 47.4341 | 47.4326 | 47.4308 | 47.4283 | 47.4254 | 47.4183 | 47.3932 | 47.3505 | 47.2884 | 17.829 | 17.7652 | 17.6227 | 17.483 | 17.3189 | 17.0888 | 16.9224 | 16.7986 | 16.6727 | 16.5513 | 16.3139 | 15.2773 | 14.1795 | 13.0693 | 17.2563 | 17.2037 | 17.0866 | 16.9716 | 16.8367 | 16.6474 | 16.5103 | 16.4081 | 16.3039 | 16.2032 | 16.0057 | 15.1458 | 14.2291 | 13.2949
|  | COWLEY LOCAL | ST |  |  | 47.4387 | 47.4385 | 47.4383 | 47.4381 | 47.4378 | 47.4373 | 47.4369 | 47.4364 | 47.4358 | 47.4351 | 47.4337 | 47.4278 | 47.4178 | 47.4034 | 17.8998 | 17.8277 | 17.7793 | 17.7267 | 17.6521 | 17.4545 | 17.2964 | 17.1594 | 17.0143 | 16.8649 | 16.5827 | 15.9559 | 15.3206 | 14.6785 | 17.3145 | 17.2553 | 17.2155 | 17.1722 | 17.1109 | 16.9486 | 16.8188 | 16.7062 | 16.5869 | 16.4641 | 16.2321 | 15.7156 | 15.1906 | 14.6584
|  | COWLEY LOCAL | FS |  |  | 47.4388 | 47.4386 | 47.4385 | 47.4384 | 47.4382 | 47.438 | 47.4378 | 47.4375 | 47.4373 | 47.437 | 47.4365 | 47.4345 | 47.4315 | 47.4282 | 17.9056 | 17.8957 | 17.8791 | 17.8558 | 17.8237 | 17.7481 | 17.6888 | 17.6267 | 17.5651 | 17.5048 | 17.3899 | 17.1299 | 16.8903 | 16.6542 | 17.3193 | 17.3111 | 17.2975 | 17.2783 | 17.2519 | 17.1898 | 17.1411 | 17.09 | 17.0394 | 16.9898 | 16.8954 | 16.6813 | 16.4836 | 16.2886
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD | MINIMUM HEADROOM | SU 78275 50779 | YES | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 15.442 | 15.4226 | 15.4106 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 9.2929 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312
|  | COXMOOR WOOD | CT |  |  | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 15.446 | 15.424 | 15.414 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312
|  | COXMOOR WOOD | LW |  |  | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 15.442 | 15.4226 | 15.4106 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 9.2929 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312
|  | COXMOOR WOOD | ST |  |  | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 15.4582 | 15.4394 | 15.4232 | 15.4166 | 15.4096 | 15.4062 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 15.4041 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312
|  | COXMOOR WOOD | FS |  |  | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 18.4364 | 15.4929 | 15.4621 | 15.4562 | 15.4416 | 15.4277 | 15.4251 | 15.4238 | 15.4223 | 15.4208 | 15.4193 | 15.4164 | 15.409 | 15.4041 | 15.4041 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312 | 16.8312
MANNINGTON GSP | LYTCHETT | CREEKMOOR | MINIMUM HEADROOM | SZ 00552 94121 | YES | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 30.8118 | 30.7894 | 30.7467 | 30.6988 | 30.6474 | 30.5933 | 30.5377 | 30.4822 | 30.4736 | 30.4653 | 30.4489 | 30.4094 | 30.3697 | 30.3301 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056
|  | CREEKMOOR | CT |  |  | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 30.8118 | 30.7894 | 30.7467 | 30.6988 | 30.6474 | 30.5933 | 30.5377 | 30.4822 | 30.4736 | 30.4653 | 30.4489 | 30.4094 | 30.3697 | 30.3301 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056
|  | CREEKMOOR | LW |  |  | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 30.8156 | 30.7986 | 30.7711 | 30.7391 | 30.7035 | 30.6654 | 30.6252 | 30.584 | 30.5391 | 30.4928 | 30.4707 | 30.426 | 30.3812 | 30.3364 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056
|  | CREEKMOOR | ST |  |  | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 31.0926 | 30.8162 | 30.8052 | 30.7884 | 30.7662 | 30.7181 | 30.6693 | 30.6209 | 30.5682 | 30.5151 | 30.472 | 30.4373 | 30.4039 | 30.3709 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056
|  | CREEKMOOR | FS |  |  | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 35.5393 | 31.0988 | 30.8271 | 30.825 | 30.8187 | 30.811 | 30.7969 | 30.7826 | 30.7652 | 30.7475 | 30.7297 | 30.6946 | 30.6092 | 30.526 | 30.4765 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056 | 31.7056
MINETY GSP | CIRENCESTER BSP | CRICKLADE | MINIMUM HEADROOM | SU 09400 93270 | YES | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 17.9156 | 17.8812 | 17.7984 | 17.7085 | 17.6737 | 17.6441 | 17.6143 | 17.5845 | 17.552 | 17.5195 | 17.4543 | 17.3449 | 17.3449 | 12.8458 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434
|  | CRICKLADE | CT |  |  | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 17.9163 | 17.8828 | 17.8024 | 17.715 | 17.6767 | 17.6481 | 17.6193 | 17.5907 | 17.5597 | 17.5288 | 17.467 | 17.3449 | 17.3449 | 12.8546 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434
|  | CRICKLADE | LW |  |  | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 17.9156 | 17.8812 | 17.7984 | 17.7085 | 17.6737 | 17.6441 | 17.6143 | 17.5845 | 17.552 | 17.5195 | 17.4543 | 17.3449 | 17.3449 | 12.8458 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434
|  | CRICKLADE | ST |  |  | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 17.9236 | 17.8994 | 17.8461 | 17.7656 | 17.6899 | 17.676 | 17.6621 | 17.6482 | 17.6331 | 17.6181 | 17.588 | 17.5104 | 17.433 | 17.3564 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434
|  | CRICKLADE | FS |  |  | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 21.154 | 17.9371 | 17.9351 | 17.9327 | 17.918 | 17.9002 | 17.8861 | 17.8719 | 17.8536 | 17.8352 | 17.817 | 17.7807 | 17.6971 | 17.6677 | 17.6388 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434 | 18.2434
MELKSHAM GSP | FROME BSP | CROCKERTON | MINIMUM HEADROOM | ST 87736 43371 | NO | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 13.2004 | 12.9916 | 12.2932 | 11.5537 | 10.8061 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 11.7401 | 10.8982 | 10.047 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 11.7914 | 10.9229 | 10.0448
|  | CROCKERTON | CT |  |  | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 13.2004 | 12.9916 | 12.2932 | 11.5537 | 10.8061 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 11.8996 | 11.1012 | 10.3011 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 11.9559 | 11.1323 | 10.3069
|  | CROCKERTON | LW |  |  | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 13.2004 | 12.9916 | 12.2932 | 11.5537 | 10.8061 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 11.7401 | 10.8982 | 10.047 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 11.7914 | 10.9229 | 10.0448
|  | CROCKERTON | ST |  |  | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 13.1669 | 12.7011 | 12.2335 | 11.7733 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 12.2044 | 11.6721 | 11.1482 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 12.2704 | 11.7212 | 11.1807
|  | CROCKERTON | FS |  |  | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 16.2141 | 13.1236 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.3853 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965 | 14.0965
BRAMLEY (FLEE) | PYESTOCK BSP | Crookham (Church) | MINIMUM HEADROOM | SU 81702 53403 | YES | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 32.4569 | 32.3862 | 32.2279 | 32.1056 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 20.1971 | 34.7102 | 34.6807 | 34.6141 | 34.5409 | 34.4691 | 34.394 | 34.3192 | 34.274 | 34.2307 | 34.2307 | 34.2307 | 34.2307 | 34.2307 | 34.2307
|  | Crookham (Church) | CT |  |  | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 32.4569 | 32.3862 | 32.2279 | 32.1056 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 20.1971 | 34.7102 | 34.6807 | 34.6141 | 34.5409 | 34.4691 | 34.394 | 34.3192 | 34.274 | 34.2307 | 34.2307 | 34.2307 | 34.2307 | 34.2307 | 34.2307
|  | Crookham (Church) | LW |  |  | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 32.4604 | 32.3935 | 32.2452 | 32.1265 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 20.7599 | 34.7117 | 34.6838 | 34.622 | 34.5534 | 34.4863 | 34.4154 | 34.343 | 34.2909 | 34.2447 | 34.2307 | 34.2307 | 34.2307 | 34.2307 | 34.2307
|  | Crookham (Church) | ST |  |  | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 32.4842 | 32.4509 | 32.3831 | 32.2851 | 32.1899 | 32.1364 | 32.0818 | 32.0248 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 32.0235 | 34.7216 | 34.7077 | 34.6794 | 34.6386 | 34.5914 | 34.5594 | 34.5267 | 34.4926 | 34.4551 | 34.4164 | 34.3442 | 34.2477 | 34.2307 | 34.2307
|  | Crookham (Church) | FS |  |  | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 39.4407 | 32.5009 | 32.4924 | 32.4808 | 32.4516 | 32.4204 | 32.3917 | 32.3623 | 32.327 | 32.2907 | 32.2537 | 32.1991 | 32.0973 | 32.0235 | 32.0235 | 34.7285 | 34.725 | 34.7201 | 34.708 | 34.695 | 34.683 | 34.6708 | 34.6561 | 34.641 | 34.6255 | 34.5969 | 34.536 | 34.4786 | 34.4224
BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE | MINIMUM HEADROOM | SU 84470 64352 | NO | 42.9747 | 42.9409 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 27.8645 | 25.871 | 37.6511 | 37.5434 | 37.3281 | 37.1206 | 36.9728 | 36.821 | 36.7394 | 36.6613 | 36.6515 | 36.6515 | 25.3734 | 23.0297 | 20.6618 | 18.31 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 24.412 | 22.0433 | 19.6908
|  | CROWTHORNE | CT |  |  | 42.9747 | 42.9409 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 27.8645 | 25.871 | 37.6568 | 37.5609 | 37.3667 | 37.162 | 37.0257 | 36.8823 | 36.7836 | 36.7106 | 36.6515 | 36.6515 | 26.0907 | 23.6131 | 21.172 | 18.753 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 24.9956 | 22.5537 | 20.1339
|  | CROWTHORNE | LW |  |  | 42.9747 | 42.9409 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 27.8645 | 25.871 | 37.6511 | 37.5434 | 37.3281 | 37.1206 | 36.9728 | 36.821 | 36.7394 | 36.6613 | 36.6515 | 36.6515 | 25.3734 | 23.0297 | 20.6618 | 18.31 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 24.412 | 22.0433 | 19.6908
|  | CROWTHORNE | ST |  |  | 42.9865 | 42.9698 | 42.9399 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 37.6888 | 37.6355 | 37.54 | 37.4099 | 37.2495 | 37.149 | 37.0911 | 37.0352 | 36.9782 | 36.9193 | 36.8147 | 36.6806 | 36.6515 | 26.3491 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623
|  | CROWTHORNE | FS |  |  | 42.9944 | 42.9891 | 42.9832 | 42.9706 | 42.9555 | 42.9429 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 42.9345 | 37.714 | 37.697 | 37.6782 | 37.6379 | 37.5898 | 37.5497 | 37.5145 | 37.4754 | 37.438 | 37.4004 | 37.3258 | 37.1686 | 37.0738 | 36.9863 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623 | 37.7623
EALING GSP | EALING (D) | DEAN GARDENS | MINIMUM HEADROOM | TQ 16546 80368 | YES | 27.4131 | 27.4112 | 27.4084 | 27.4056 | 27.4028 | 27.4 | 27.3972 | 27.3943 | 27.391 | 27.3877 | 27.3809 | 27.3541 | 27.3269 | 27.3222 | 23.6847 | 23.6706 | 23.6445 | 23.6168 | 23.5888 | 23.5606 | 23.5326 | 23.5054 | 23.4754 | 23.4457 | 23.3863 | 23.2656 | 23.1424 | 23.021 | 23.9811 | 23.9463 | 23.8821 | 23.8139 | 23.7448 | 23.6752 | 23.6064 | 23.5499 | 23.5426 | 23.5355 | 23.5211 | 23.4918 | 23.4717 | 23.4717
|  | DEAN GARDENS | CT |  |  | 27.4131 | 27.4112 | 27.4084 | 27.4056 | 27.4028 | 27.4 | 27.3972 | 27.3943 | 27.391 | 27.3877 | 27.3809 | 27.3541 | 27.3269 | 27.3222 | 23.6847 | 23.6706 | 23.6445 | 23.6168 | 23.5888 | 23.5606 | 23.5326 | 23.5054 | 23.4754 | 23.4457 | 23.3863 | 23.2656 | 23.1424 | 23.021 | 23.9811 | 23.9463 | 23.8821 | 23.8139 | 23.7448 | 23.6752 | 23.6064 | 23.5499 | 23.5426 | 23.5355 | 23.5211 | 23.4918 | 23.4717 | 23.4717
|  | DEAN GARDENS | LW |  |  | 27.4131 | 27.4112 | 27.4084 | 27.4056 | 27.4028 | 27.4 | 27.3972 | 27.3943 | 27.391 | 27.3877 | 27.3809 | 27.3541 | 27.3269 | 27.3222 | 23.6879 | 23.679 | 23.6665 | 23.6535 | 23.6407 | 23.628 | 23.615 | 23.6018 | 23.5867 | 23.5714 | 23.5404 | 23.4176 | 23.2929 | 23.17 | 23.989 | 23.967 | 23.9363 | 23.9042 | 23.8727 | 23.8415 | 23.8094 | 23.7768 | 23.7396 | 23.7019 | 23.6256 | 23.5286 | 23.4984 | 23.4717
|  | DEAN GARDENS | ST |  |  | 27.4148 | 27.4141 | 27.4137 | 27.4131 | 27.4123 | 27.4094 | 27.4066 | 27.4038 | 27.4007 | 27.3977 | 27.3917 | 27.3765 | 27.3617 | 27.347 | 23.6957 | 23.6925 | 23.6905 | 23.6878 | 23.6842 | 23.671 | 23.6579 | 23.6453 | 23.6312 | 23.6174 | 23.5898 | 23.5204 | 23.4523 | 23.385 | 24.0082 | 24.0004 | 23.9953 | 23.9888 | 23.9799 | 23.9473 | 23.9151 | 23.884 | 23.8494 | 23.8154 | 23.7473 | 23.5762 | 23.537 | 23.5207
|  | DEAN GARDENS | FS |  |  | 27.4158 | 27.4154 | 27.4152 | 27.4146 | 27.414 | 27.413 | 27.4119 | 27.4105 | 27.4092 | 27.4078 | 27.4051 | 27.3986 | 27.3923 | 27.3863 | 23.7002 | 23.6981 | 23.6974 | 23.6948 | 23.6921 | 23.6872 | 23.6824 | 23.6761 | 23.6697 | 23.6635 | 23.6513 | 23.6212 | 23.5924 | 23.5649 | 24.0195 | 24.0143 | 24.0124 | 24.0061 | 23.9995 | 23.9873 | 23.9754 | 23.9599 | 23.9443 | 23.9289 | 23.8988 | 23.8247 | 23.7537 | 23.6858
COWLEY GSP | YARNTON BSP | DEDDINGTON | MINIMUM HEADROOM | SP 46729 30325 | YES | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 4.347 | 4.3229 | 4.2656 | 4.2035 | 4.1419 | 4.0809 | 4.0206 | 3.9606 | 3.8959 | 3.8325 | 3.705 | 3.4092 | 3.0964 | 2.7869
|  | DEDDINGTON | CT |  |  | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 4.347 | 4.3229 | 4.2656 | 4.2035 | 4.1419 | 4.0809 | 4.0206 | 3.9606 | 3.8959 | 3.8325 | 3.705 | 3.4092 | 3.0964 | 2.7869
|  | DEDDINGTON | LW |  |  | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 4.3476 | 4.3242 | 4.269 | 4.209 | 4.1496 | 4.0907 | 4.0324 | 3.9746 | 3.9122 | 3.8461 | 3.7127 | 3.4257 | 3.1293 | 2.8362
|  | DEDDINGTON | ST |  |  | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 4.3581 | 4.3499 | 4.3322 | 4.3054 | 4.2733 | 4.2423 | 4.2118 | 4.1816 | 4.149 | 4.1173 | 4.0538 | 3.8846 | 3.7112 | 3.5394
|  | DEDDINGTON | FS |  |  | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.2413 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 14.1679 | 4.3987 | 4.3606 | 4.3587 | 4.3488 | 4.3369 | 4.3264 | 4.316 | 4.3027 | 4.2895 | 4.2768 | 4.2519 | 4.1869 | 4.1199 | 4.0548
IVER 132KV | DENHAM | DENHAM AVENUE | MINIMUM HEADROOM | TQ 03761 86587 | NO | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 17.5916 | 17.5878 | 17.5792 | 17.5691 | 17.556 | 17.5426 | 17.5352 | 17.5248 | 17.5113 | 17.4976 | 17.4705 | 17.4249 | 17.363 | 17.3298 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332
|  | DENHAM AVENUE | CT |  |  | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 17.5916 | 17.5878 | 17.5792 | 17.5691 | 17.556 | 17.5426 | 17.5352 | 17.5277 | 17.5193 | 17.5106 | 17.4919 | 17.4249 | 17.3638 | 17.3307 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332
|  | DENHAM AVENUE | LW |  |  | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 17.5921 | 17.5891 | 17.5825 | 17.5748 | 17.5632 | 17.5503 | 17.5387 | 17.5309 | 17.5225 | 17.5141 | 17.4963 | 17.4259 | 17.363 | 17.3298 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332
|  | DENHAM AVENUE | ST |  |  | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 17.5954 | 17.594 | 17.5913 | 17.5869 | 17.5795 | 17.5562 | 17.5372 | 17.5248 | 17.5113 | 17.4976 | 17.4705 | 17.4273 | 17.3848 | 17.3433 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332
|  | DENHAM AVENUE | FS |  |  | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 21.4575 | 17.5979 | 17.5973 | 17.5971 | 17.596 | 17.5938 | 17.5866 | 17.5792 | 17.57 | 17.5607 | 17.5515 | 17.5369 | 17.5117 | 17.4866 | 17.4655 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332 | 17.6332
MELKSHAM GSP | NORRINGTON | DEVIZES | MINIMUM HEADROOM | SU 00106 60986 | YES | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 34.5354 | 34.4764 | 34.3339 | 34.1776 | 34.0083 | 33.83 | 33.6429 | 33.4483 | 33.2283 | 33.1311 | 32.955 | 32.4026 | 32.3246 | 32.3246 | 35.7463 | 35.7371 | 35.7149 | 35.6905 | 35.6641 | 35.6362 | 35.6071 | 35.5767 | 35.5437 | 35.5309 | 35.5309 | 35.5309 | 35.5309 | 35.5309
|  | DEVIZES | CT |  |  | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 34.5489 | 34.5098 | 34.4152 | 34.3109 | 34.1949 | 34.072 | 33.9408 | 33.8057 | 33.6559 | 33.5038 | 33.1973 | 32.6822 | 32.3484 | 32.3246 | 35.7484 | 35.7423 | 35.7276 | 35.7113 | 35.6932 | 35.674 | 35.6535 | 35.6325 | 35.6091 | 35.5854 | 35.5393 | 35.5309 | 35.5309 | 35.5309
|  | DEVIZES | LW |  |  | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 34.5354 | 34.4764 | 34.3339 | 34.1776 | 34.0083 | 33.83 | 33.6429 | 33.4483 | 33.2283 | 33.1311 | 32.955 | 32.4026 | 32.3246 | 32.3246 | 35.7463 | 35.7371 | 35.7149 | 35.6905 | 35.6641 | 35.6362 | 35.6071 | 35.5767 | 35.5437 | 35.5309 | 35.5309 | 35.5309 | 35.5309 | 35.5309
|  | DEVIZES | ST |  |  | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 34.598 | 34.5175 | 34.4397 | 34.3213 | 34.1704 | 34.0175 | 33.8603 | 33.7019 | 33.5274 | 33.3525 | 33.1266 | 32.7562 | 32.3851 | 32.3318 | 35.7561 | 35.7435 | 35.7314 | 35.7129 | 35.6894 | 35.6655 | 35.641 | 35.6163 | 35.589 | 35.5617 | 35.5309 | 35.5309 | 35.5309 | 35.5309
|  | DEVIZES | FS |  |  | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 39.6286 | 34.6761 | 34.6138 | 34.6098 | 34.5846 | 34.5527 | 34.507 | 34.4603 | 34.4004 | 34.3385 | 34.276 | 34.1475 | 33.804 | 33.4422 | 33.1556 | 35.7683 | 35.7586 | 35.7579 | 35.754 | 35.749 | 35.7419 | 35.7346 | 35.7253 | 35.7156 | 35.7059 | 35.6858 | 35.6322 | 35.5757 | 35.5309
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH | MINIMUM HEADROOM | SU 19288 83540 | YES | 21.9983 | 21.996 | 21.991 | 21.9855 | 21.98 | 21.9726 | 21.9562 | 21.94 | 21.9226 | 21.9055 | 21.8721 | 21.7565 | 21.5647 | 21.3711 | 21.3582 | 21.3559 | 21.3508 | 21.3452 | 21.3395 | 21.3319 | 21.3152 | 21.2986 | 21.2808 | 21.2631 | 21.2289 | 21.1105 | 20.9141 | 20.7158 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872
|  | DORCAN SOUTH | CT |  |  | 21.9983 | 21.996 | 21.991 | 21.9855 | 21.98 | 21.9744 | 21.9687 | 21.963 | 21.957 | 21.951 | 21.9378 | 21.7575 | 21.5647 | 21.3711 | 21.3583 | 21.356 | 21.3509 | 21.3454 | 21.3399 | 21.3343 | 21.3285 | 21.3227 | 21.3165 | 21.3103 | 21.2982 | 21.1721 | 21.0218 | 20.8679 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872
|  | DORCAN SOUTH | LW |  |  | 21.9983 | 21.996 | 21.991 | 21.9855 | 21.98 | 21.9744 | 21.9687 | 21.963 | 21.957 | 21.951 | 21.9378 | 21.7575 | 21.5647 | 21.3711 | 21.3582 | 21.3559 | 21.3508 | 21.3452 | 21.3395 | 21.3338 | 21.328 | 21.3221 | 21.316 | 21.3098 | 21.2963 | 21.1116 | 20.9141 | 20.7158 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872
|  | DORCAN SOUTH | ST |  |  | 21.9991 | 21.998 | 21.9959 | 21.9928 | 21.9891 | 21.9726 | 21.9562 | 21.94 | 21.9226 | 21.9055 | 21.8721 | 21.7565 | 21.6295 | 21.5036 | 21.3591 | 21.358 | 21.3558 | 21.3526 | 21.3488 | 21.3319 | 21.3152 | 21.2986 | 21.2808 | 21.2631 | 21.2289 | 21.1105 | 20.9805 | 20.8514 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872
|  | DORCAN SOUTH | FS |  |  | 21.9996 | 21.9993 | 21.999 | 21.9981 | 21.997 | 21.9921 | 21.9873 | 21.9811 | 21.975 | 21.969 | 21.9575 | 21.9191 | 21.8726 | 21.8228 | 21.3596 | 21.3593 | 21.359 | 21.358 | 21.3569 | 21.3519 | 21.3469 | 21.3406 | 21.3344 | 21.3283 | 21.3164 | 21.2771 | 21.2295 | 21.1785 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872 | 28.3872
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER TOWN | MINIMUM HEADROOM | SY 69113 90401 | YES | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 28.0608 | 26.2044 | 24.4324 | 22.6505 | 29.5439 | 29.523 | 29.4791 | 29.4258 | 29.3673 | 29.3021 | 26.429 | 26.1691 | 25.8964 | 25.6203 | 25.0744 | 23.0574 | 21.0008 | 18.9326 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 26.5272 | 26.2514 | 25.972 | 25.4196 | 23.3787 | 21.2976 | 19.205
|  | DORCHESTER TOWN | CT |  |  | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 28.0608 | 26.2044 | 24.4324 | 22.6505 | 29.5439 | 29.523 | 29.4791 | 29.4258 | 29.3673 | 29.3021 | 26.429 | 26.1691 | 25.8964 | 25.6203 | 25.0744 | 23.1965 | 21.2983 | 19.3877 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 26.5272 | 26.2514 | 25.972 | 25.4196 | 23.5194 | 21.5987 | 19.6655
|  | DORCHESTER TOWN | LW |  |  | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 28.0608 | 26.2044 | 24.4324 | 22.6505 | 29.5454 | 29.5259 | 29.4866 | 29.4372 | 29.3816 | 29.3184 | 26.4996 | 26.2537 | 25.9978 | 25.7366 | 25.2121 | 23.0574 | 21.0008 | 18.9326 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 26.6128 | 26.3539 | 26.0896 | 25.5589 | 23.3787 | 21.2976 | 19.205
|  | DORCHESTER TOWN | ST |  |  | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 28.1547 | 27.0177 | 25.9244 | 24.8447 | 29.5492 | 29.5365 | 29.5121 | 29.4755 | 29.4306 | 29.3644 | 26.6748 | 26.4193 | 26.1459 | 25.8696 | 25.3211 | 24.0015 | 22.7325 | 21.4793 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 26.5038 | 26.2242 | 25.6692 | 24.3339 | 23.0499 | 21.7819
|  | DORCHESTER TOWN | FS |  |  | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 32.742 | 28.1314 | 29.5543 | 29.5502 | 29.5444 | 29.5337 | 29.5211 | 29.4978 | 29.4736 | 29.4471 | 29.4204 | 29.3934 | 29.3397 | 26.3214 | 25.8088 | 25.2941 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 29.8887 | 26.6813 | 26.1627 | 25.6418
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE | MINIMUM HEADROOM | SU 61604 50238 | YES | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 26.5891 | 26.4598 | 26.1949 | 25.9028 | 25.6056 | 25.301 | 24.99 | 24.6682 | 24.3174 | 23.9584 | 23.4018 | 21.7033 | 19.8739 | 18.0218 | 26.5895 | 26.4606 | 26.1965 | 25.9052 | 25.6089 | 25.3053 | 24.9952 | 24.6744 | 24.3246 | 23.9667 | 23.4119 | 21.7185 | 19.8947 | 18.0482
|  | DOWN GRANGE | CT |  |  | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 26.5891 | 26.4618 | 26.195 | 25.903 | 25.6058 | 25.301 | 24.99 | 24.6682 | 24.3174 | 23.9584 | 23.4018 | 21.7112 | 19.9243 | 18.1144 | 26.5895 | 26.4625 | 26.1965 | 25.9055 | 25.6092 | 25.3053 | 24.9952 | 24.6744 | 24.3246 | 23.9667 | 23.4119 | 21.7263 | 19.945 | 18.1405
|  | DOWN GRANGE | LW |  |  | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 26.5898 | 26.4598 | 26.1949 | 25.9028 | 25.6056 | 25.3027 | 24.9929 | 24.6756 | 24.3334 | 23.9871 | 23.4699 | 21.7033 | 19.8739 | 18.0218 | 26.5901 | 26.4606 | 26.1965 | 25.9052 | 25.6089 | 25.307 | 24.9981 | 24.6817 | 24.3406 | 23.9953 | 23.4797 | 21.7185 | 19.8947 | 18.0482
|  | DOWN GRANGE | ST |  |  | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 26.6357 | 26.5695 | 26.4473 | 26.2725 | 26.0632 | 25.8398 | 25.6132 | 25.3803 | 25.1247 | 24.863 | 24.4569 | 23.3463 | 22.219 | 21.0852 | 26.6359 | 26.5699 | 26.4481 | 26.2738 | 26.0652 | 25.8424 | 25.6165 | 25.3843 | 25.1295 | 24.8686 | 24.4638 | 23.3565 | 22.2327 | 21.1023
|  | DOWN GRANGE | FS |  |  | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 43.7387 | 26.6689 | 26.6492 | 26.6272 | 26.5736 | 26.5123 | 26.4335 | 26.3536 | 26.2551 | 26.1551 | 26.0537 | 25.8946 | 25.4785 | 25.0489 | 24.6097 | 26.669 | 26.6493 | 26.6275 | 26.574 | 26.5128 | 26.4343 | 26.3546 | 26.2565 | 26.1567 | 26.0557 | 25.897 | 25.4822 | 25.0539 | 24.6161
MINETY GSP | STRATTON (2 X 90) | DRAKES WAY | MINIMUM HEADROOM | SU 16899 85647 | NO | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 24.5828 | 24.5772 | 24.5642 | 24.5501 | 24.536 | 24.5219 | 24.5077 | 24.4878 | 24.4624 | 24.4373 | 24.3885 | 24.1923 | 24.0632 | 24.0403 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872
|  | DRAKES WAY | CT |  |  | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 24.5828 | 24.5773 | 24.5644 | 24.5504 | 24.5364 | 24.5224 | 24.5083 | 24.4942 | 24.479 | 24.4639 | 24.4341 | 24.2208 | 24.0671 | 24.0454 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872
|  | DRAKES WAY | LW |  |  | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 24.5828 | 24.5772 | 24.5642 | 24.5501 | 24.536 | 24.5219 | 24.5077 | 24.4936 | 24.4785 | 24.4634 | 24.4323 | 24.1923 | 24.0632 | 24.0403 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872
|  | DRAKES WAY | ST |  |  | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 24.5849 | 24.5823 | 24.577 | 24.569 | 24.5594 | 24.5352 | 24.5114 | 24.4878 | 24.4624 | 24.4373 | 24.3885 | 24.2349 | 24.0751 | 24.0604 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872
|  | DRAKES WAY | FS |  |  | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 26.8071 | 24.5862 | 24.5857 | 24.5852 | 24.5829 | 24.5802 | 24.573 | 24.5659 | 24.5567 | 24.5477 | 24.5389 | 24.5216 | 24.4696 | 24.4102 | 24.3481 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872 | 23.3872
NURSLING GSP | WINCHESTER | DUNBRIDGE | MINIMUM HEADROOM | SU 31520 26244 | YES | 19.3211 | 26.3708 | 26.3704 | 26.3698 | 26.3692 | 26.3683 | 26.3673 | 26.3661 | 26.3644 | 26.3625 | 26.3577 | 26.3408 | 26.312 | 26.2702 | 6.8478 | 13.0211 | 12.896 | 12.7599 | 12.6235 | 12.4878 | 12.3519 | 12.2169 | 12.0708 | 11.9258 | 11.6371 | 10.9987 | 10.329 | 9.659 | 19.7588 | 25.9306 | 25.8022 | 25.6623 | 25.5908 | 25.5199 | 25.4489 | 25.3782 | 25.3012 | 25.2245 | 25.0788 | 24.8204 | 24.7666 | 24.705
|  | DUNBRIDGE | CT |  |  | 19.3211 | 26.3708 | 26.3704 | 26.3698 | 26.3692 | 26.3683 | 26.3673 | 26.3661 | 26.3644 | 26.3625 | 26.3577 | 26.3408 | 26.312 | 26.2702 | 6.8478 | 13.0211 | 12.896 | 12.7599 | 12.6235 | 12.4878 | 12.3519 | 12.2169 | 12.0708 | 11.9258 | 11.6371 | 10.9987 | 10.329 | 9.659 | 19.7588 | 25.9306 | 25.8022 | 25.6623 | 25.5908 | 25.5199 | 25.4489 | 25.3782 | 25.3012 | 25.2245 | 25.0788 | 24.8204 | 24.7666 | 24.705
|  | DUNBRIDGE | LW |  |  | 19.3211 | 26.3708 | 26.3704 | 26.3698 | 26.3692 | 26.3683 | 26.3673 | 26.3661 | 26.3644 | 26.3625 | 26.3577 | 26.3408 | 26.312 | 26.2702 | 6.8512 | 13.0293 | 12.9147 | 12.79 | 12.6648 | 12.5399 | 12.4147 | 12.29 | 12.1551 | 12.021 | 11.7539 | 11.1675 | 10.5548 | 9.9392 | 19.7627 | 25.9395 | 25.8222 | 25.6945 | 25.615 | 25.5505 | 25.4856 | 25.421 | 25.3508 | 25.2808 | 25.141 | 24.9045 | 24.8199 | 24.7766
|  | DUNBRIDGE | ST |  |  | 19.3214 | 26.3713 | 26.3712 | 26.371 | 26.3708 | 26.3705 | 26.3702 | 26.3699 | 26.3694 | 26.369 | 26.3681 | 26.3641 | 26.3574 | 26.3476 | 7.0501 | 13.0923 | 13.0704 | 13.0371 | 12.9958 | 12.9282 | 12.8604 | 12.7933 | 12.721 | 12.6497 | 12.5091 | 12.1561 | 11.8025 | 11.4485 | 19.9663 | 26.0042 | 25.9817 | 25.9476 | 25.9053 | 25.836 | 25.7666 | 25.6979 | 25.644 | 25.6072 | 25.5345 | 25.3511 | 25.1657 | 25.0135
|  | DUNBRIDGE | FS |  |  | 19.3215 | 26.3714 | 26.3713 | 26.3712 | 26.3711 | 26.3709 | 26.3708 | 26.3706 | 26.3705 | 26.3703 | 26.37 | 26.3686 | 26.3666 | 26.3644 | 7.1236 | 13.1037 | 13.1009 | 13.0839 | 13.0632 | 13.0403 | 13.0172 | 12.9876 | 12.9583 | 12.9294 | 12.8726 | 12.7328 | 12.5974 | 12.4677 | 20.0414 | 26.0159 | 26.013 | 25.9955 | 25.9744 | 25.9508 | 25.9272 | 25.8968 | 25.8668 | 25.8373 | 25.7789 | 25.6496 | 25.579 | 25.5112
MANNINGTON GSP | REDHILL BSP | EAST HOWE | MINIMUM HEADROOM | SZ 06789 95116 | YES | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 28.0131 | 30.5759 | 30.5537 | 30.5163 | 30.4686 | 30.4084 | 30.3388 | 30.3037 | 30.2865 | 30.2697 | 30.252 | 30.2159 | 30.1341 | 26.0568 | 24.9023 | 30.5764 | 30.558 | 30.5269 | 30.4872 | 30.4372 | 30.3793 | 30.316 | 30.2483 | 30.185 | 30.1403 | 26.3453 | 25.4988 | 24.4678 | 23.4011
|  | EAST HOWE | CT |  |  | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 28.0131 | 30.5775 | 30.5582 | 30.5249 | 30.4831 | 30.4294 | 30.3664 | 30.3112 | 30.2956 | 30.2798 | 30.2669 | 30.244 | 30.1662 | 26.6546 | 25.7628 | 30.5778 | 30.5618 | 30.534 | 30.4993 | 30.4546 | 30.4022 | 30.3457 | 30.284 | 30.2216 | 30.1779 | 26.6359 | 25.8312 | 25.0201 | 24.1962
|  | EAST HOWE | LW |  |  | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 28.0131 | 30.5759 | 30.5537 | 30.5163 | 30.4686 | 30.4084 | 30.3388 | 30.3037 | 30.2865 | 30.2697 | 30.257 | 30.2342 | 30.1362 | 26.0568 | 24.9023 | 30.5764 | 30.558 | 30.5269 | 30.4872 | 30.4372 | 30.3793 | 30.316 | 30.2483 | 30.185 | 30.1529 | 26.5347 | 25.5204 | 24.4678 | 23.4011
|  | EAST HOWE | ST |  |  | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 30.6849 | 30.5734 | 30.5535 | 30.525 | 30.4861 | 30.3965 | 30.3125 | 30.2924 | 30.2712 | 30.252 | 30.2159 | 30.1341 | 26.2854 | 25.4024 | 30.6671 | 30.5744 | 30.5578 | 30.5342 | 30.5018 | 30.4273 | 30.3507 | 30.2714 | 30.1887 | 30.1403 | 26.3453 | 25.4988 | 24.679 | 23.8632
|  | EAST HOWE | FS |  |  | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 33.4873 | 30.6936 | 30.6368 | 30.6292 | 30.6174 | 30.603 | 30.5751 | 30.5464 | 30.5128 | 30.4794 | 30.4504 | 30.395 | 30.305 | 30.2791 | 30.2528 | 30.6743 | 30.6271 | 30.6208 | 30.611 | 30.599 | 30.5758 | 30.5519 | 30.5239 | 30.4962 | 30.4721 | 30.4261 | 30.321 | 30.2188 | 30.1424
MELKSHAM GSP | NORRINGTON | EASTERTON | MINIMUM HEADROOM | SU 01568 54730 | YES | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | -2.2037 | -2.2256 | -2.278 | -2.3347 | -2.3925 | -2.4506 | -2.5095 | -2.5683 | -2.6323 | -2.6962 | -2.8254 | -3.3019 | -3.7947 | -4.2819 | 3.1841 | 3.1674 | 3.1275 | 3.0843 | 3.0403 | 2.996 | 2.9512 | 2.9064 | 2.8576 | 2.809 | 2.7106 | 2.3476 | 1.9723 | 1.6011
|  | EASTERTON | CT |  |  | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | -2.2037 | -2.2256 | -2.278 | -2.3347 | -2.3925 | -2.4506 | -2.5095 | -2.5683 | -2.6323 | -2.6962 | -2.8254 | -3.3019 | -3.7947 | -4.2819 | 3.1841 | 3.1674 | 3.1275 | 3.0843 | 3.0403 | 2.996 | 2.9512 | 2.9064 | 2.8576 | 2.809 | 2.7106 | 2.3476 | 1.9723 | 1.6011
|  | EASTERTON | LW |  |  | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | -2.2007 | -2.2182 | -2.2598 | -2.305 | -2.3516 | -2.3992 | -2.4476 | -2.4968 | -2.5512 | -2.6061 | -2.7177 | -3.1711 | -3.6417 | -4.1088 | 3.1864 | 3.1731 | 3.1414 | 3.1069 | 3.0714 | 3.0352 | 2.9983 | 2.9609 | 2.9194 | 2.8776 | 2.7926 | 2.4472 | 2.0888 | 1.733
|  | EASTERTON | ST |  |  | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | -2.1913 | -2.1949 | -2.2029 | -2.215 | -2.2306 | -2.2822 | -2.3337 | -2.385 | -2.4407 | -2.4959 | -2.6062 | -2.8886 | -3.1699 | -3.4481 | 3.1936 | 3.1908 | 3.1847 | 3.1755 | 3.1636 | 3.1244 | 3.0851 | 3.046 | 3.0036 | 2.9615 | 2.8775 | 2.6624 | 2.4482 | 2.2363
|  | EASTERTON | FS |  |  | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | 83.3076 | -2.1898 | -2.1909 | -2.1921 | -2.1996 | -2.2086 | -2.2262 | -2.2438 | -2.2665 | -2.2891 | -2.3114 | -2.3559 | -2.4664 | -2.5754 | -2.682 | 3.1947 | 3.1939 | 3.1929 | 3.1873 | 3.1804 | 3.167 | 3.1535 | 3.1363 | 3.1191 | 3.1021 | 3.0682 | 2.984 | 2.901 | 2.8198
BRAMLEY (FLEE) | BRACKNELL RESERVE | EASTHAMPSTEAD | MINIMUM HEADROOM | SU 86148 67194 | NO | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 37.2447 | 37.2289 | 37.1909 | 37.1477 | 37.0976 | 37.0268 | 36.9518 | 36.8881 | 36.8563 | 36.817 | 36.7395 | 36.508 | 36.2892 | 36.0725 | 39.4751 | 39.4674 | 39.449 | 39.428 | 39.4037 | 39.3693 | 39.3384 | 39.3161 | 39.2971 | 39.2736 | 39.2272 | 39.0835 | 38.8716 | 38.7364
|  | EASTHAMPSTEAD | CT |  |  | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 37.2471 | 37.235 | 37.2057 | 37.1722 | 37.1325 | 37.0745 | 37.016 | 36.9604 | 36.9204 | 36.8857 | 36.8394 | 36.6016 | 36.3839 | 36.1937 | 39.4763 | 39.4704 | 39.4562 | 39.4399 | 39.4206 | 39.3924 | 39.3641 | 39.3411 | 39.3285 | 39.3147 | 39.287 | 39.1447 | 38.9633 | 38.7792
|  | EASTHAMPSTEAD | LW |  |  | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 37.2447 | 37.2289 | 37.1909 | 37.1477 | 37.0976 | 37.0268 | 36.9518 | 36.8881 | 36.862 | 36.8366 | 36.7863 | 36.508 | 36.2892 | 36.0725 | 39.4751 | 39.4674 | 39.449 | 39.428 | 39.4037 | 39.3693 | 39.3384 | 39.3161 | 39.3005 | 39.2853 | 39.2552 | 39.0835 | 38.8716 | 38.7364
|  | EASTHAMPSTEAD | ST |  |  | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 37.2492 | 37.2392 | 37.2173 | 37.1834 | 37.1385 | 37.0557 | 36.9733 | 36.8946 | 36.8563 | 36.817 | 36.7395 | 36.5415 | 36.3887 | 36.244 | 39.4773 | 39.4725 | 39.4618 | 39.4453 | 39.4236 | 39.3833 | 39.3452 | 39.32 | 39.2971 | 39.2736 | 39.2272 | 39.1087 | 38.968 | 38.8278
|  | EASTHAMPSTEAD | FS |  |  | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 40.6146 | 37.2549 | 37.254 | 37.2527 | 37.2468 | 37.2382 | 37.2116 | 37.1845 | 37.1531 | 37.1269 | 37.1007 | 37.0496 | 36.9264 | 36.8337 | 36.7457 | 39.4801 | 39.4796 | 39.479 | 39.4762 | 39.4719 | 39.459 | 39.4459 | 39.4307 | 39.4179 | 39.4052 | 39.3803 | 39.3304 | 39.2836 | 39.2309
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH | MINIMUM HEADROOM | SU 45426 18958 | NO | 37.6 | 37.4437 | 37.2217 | 36.9809 | 36.7377 | 36.4914 | 36.2805 | 36.055 | 35.8011 | 35.5688 | 35.1002 | 33.4399 | 31.7631 | 30.0958 | 35.3705 | 35.1912 | 34.9364 | 34.6601 | 34.381 | 34.0985 | 33.8565 | 33.5977 | 33.3064 | 33.0399 | 32.5021 | 30.597 | 28.6731 | 26.76 | 46.0102 | 45.981 | 45.9394 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 33.8979
|  | EASTLEIGH NORTH | CT |  |  | 37.6 | 37.4437 | 37.2217 | 36.9809 | 36.7377 | 36.4914 | 36.2805 | 36.055 | 35.8011 | 35.5688 | 35.1002 | 33.4399 | 31.7631 | 30.0958 | 35.3793 | 35.2253 | 35.002 | 34.7638 | 34.5185 | 34.2594 | 34.0382 | 33.8011 | 33.5354 | 33.2912 | 32.8065 | 31.102 | 29.3857 | 27.6803 | 46.0117 | 45.9865 | 45.9501 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 34.8395
|  | EASTLEIGH NORTH | LW |  |  | 37.6 | 37.4437 | 37.2217 | 36.9809 | 36.7377 | 36.4914 | 36.2805 | 36.055 | 35.8011 | 35.5688 | 35.1002 | 33.4399 | 31.7631 | 30.0958 | 35.3705 | 35.1912 | 34.9364 | 34.6601 | 34.381 | 34.0985 | 33.8565 | 33.5977 | 33.3064 | 33.0399 | 32.5021 | 30.597 | 28.6731 | 26.76 | 46.0102 | 45.981 | 45.9394 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 33.8979
|  | EASTLEIGH NORTH | ST |  |  | 37.7155 | 37.5488 | 37.4277 | 37.2716 | 37.0907 | 36.8506 | 36.6344 | 36.4107 | 36.1614 | 35.9257 | 35.4588 | 34.3282 | 33.239 | 32.1691 | 35.5031 | 35.3118 | 35.1729 | 34.9936 | 34.7862 | 34.5107 | 34.2625 | 34.0058 | 33.7198 | 33.4493 | 32.9136 | 31.6163 | 30.3666 | 29.1388 | 46.0319 | 46.0007 | 45.978 | 45.9487 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194 | 45.9194
|  | EASTLEIGH NORTH | FS |  |  | 37.7515 | 37.7093 | 37.6715 | 37.6134 | 37.5515 | 37.4661 | 37.3959 | 37.3087 | 37.2177 | 37.1322 | 36.9619 | 36.5472 | 36.1435 | 35.743 | 35.5443 | 35.496 | 35.4526 | 35.3859 | 35.3149 | 35.2169 | 35.1364 | 35.0362 | 34.9318 | 34.8338 | 34.6383 | 34.1625 | 33.6993 | 33.2397 | 46.0386 | 46.0307 | 46.0237 | 46.0128 | 46.0012 | 45.9852 | 45.972 | 45.9557 | 45.9386 | 45.9226 | 45.9194 | 45.9194 | 45.9194 | 45.9194
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY | MINIMUM HEADROOM | SZ 66357 99040 | NO | 50.7578 | 50.7568 | 50.7544 | 50.7518 | 50.7484 | 50.7417 | 50.7351 | 50.7285 | 50.7215 | 50.7146 | 50.701 | 50.6669 | 50.623 | 50.5661 | 46.2099 | 46.2023 | 46.1844 | 46.1649 | 46.1395 | 46.0894 | 46.04 | 45.9912 | 45.9386 | 45.8868 | 45.7855 | 45.5306 | 45.2022 | 44.7771 | 43.4938 | 43.4919 | 43.4873 | 43.4823 | 43.4759 | 43.4631 | 43.4504 | 43.438 | 43.4246 | 43.4113 | 43.3855 | 43.3204 | 43.2365 | 43.128
|  | EASTNEY | CT |  |  | 50.7578 | 50.7568 | 50.7544 | 50.7518 | 50.7492 | 50.7466 | 50.744 | 50.7415 | 50.7387 | 50.736 | 50.7305 | 50.6803 | 50.623 | 50.5661 | 46.2112 | 46.2054 | 46.1919 | 46.1772 | 46.1624 | 46.1478 | 46.1332 | 46.1186 | 46.1027 | 46.0869 | 46.0551 | 45.7307 | 45.3703 | 45.0127 | 43.4942 | 43.4927 | 43.4892 | 43.4855 | 43.4817 | 43.478 | 43.4743 | 43.4705 | 43.4665 | 43.4624 | 43.4543 | 43.3715 | 43.2794 | 43.1881
|  | EASTNEY | LW |  |  | 50.7578 | 50.7568 | 50.7544 | 50.7518 | 50.7492 | 50.7466 | 50.744 | 50.7415 | 50.7387 | 50.736 | 50.7305 | 50.6803 | 50.623 | 50.5661 | 46.2099 | 46.2023 | 46.1844 | 46.1649 | 46.1454 | 46.1262 | 46.1071 | 46.088 | 46.0673 | 46.0468 | 46.0058 | 45.6311 | 45.2022 | 44.7771 | 43.4938 | 43.4919 | 43.4873 | 43.4823 | 43.4774 | 43.4725 | 43.4676 | 43.4627 | 43.4574 | 43.4522 | 43.4417 | 43.346 | 43.2365 | 43.128
|  | EASTNEY | ST |  |  | 50.7579 | 50.757 | 50.755 | 50.752 | 50.7484 | 50.7417 | 50.7351 | 50.7285 | 50.7215 | 50.7146 | 50.701 | 50.6669 | 50.6306 | 50.5946 | 46.2108 | 46.2039 | 46.189 | 46.1665 | 46.1395 | 46.0894 | 46.04 | 45.9912 | 45.9386 | 45.8868 | 45.7855 | 45.5306 | 45.2595 | 44.9906 | 43.4941 | 43.4923 | 43.4885 | 43.4828 | 43.4759 | 43.4631 | 43.4504 | 43.438 | 43.4246 | 43.4113 | 43.3855 | 43.3204 | 43.2512 | 43.1825
|  | EASTNEY | FS |  |  | 50.7584 | 50.7584 | 50.7583 | 50.7578 | 50.7573 | 50.7551 | 50.7529 | 50.7501 | 50.7474 | 50.7447 | 50.7394 | 50.7269 | 50.7144 | 50.7014 | 46.2148 | 46.2142 | 46.2135 | 46.2102 | 46.2064 | 46.1899 | 46.1736 | 46.1527 | 46.1321 | 46.1119 | 46.0724 | 45.9793 | 45.8854 | 45.7886 | 43.4951 | 43.4949 | 43.4947 | 43.4939 | 43.4929 | 43.4887 | 43.4846 | 43.4792 | 43.474 | 43.4688 | 43.4587 | 43.4349 | 43.411 | 43.3862
LALEHAM | STAINES | EGHAM | MINIMUM HEADROOM | TQ 01030 71404 | YES | 171.1925 | 171.1763 | 171.1519 | 199.8246 | 199.7966 | 199.7678 | 199.7506 | 199.7338 | 199.7137 | 199.6936 | 199.6541 | 199.5425 | 199.4268 | 199.3915 | 159.1837 | 158.9848 | 158.6872 | 185.0528 | 184.7113 | 184.3579 | 184.1418 | 183.8939 | 183.624 | 183.3574 | 182.8571 | 181.507 | 180.1017 | 178.7697 | 150.9336 | 150.7411 | 150.4532 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1
|  | EGHAM | CT |  |  | 171.1925 | 171.1763 | 171.1519 | 199.8246 | 199.7966 | 199.7678 | 199.7506 | 199.7338 | 199.7137 | 199.6936 | 199.6541 | 199.5425 | 199.4268 | 199.3915 | 159.1858 | 159.0006 | 158.7066 | 185.0814 | 184.7448 | 184.3876 | 184.1418 | 183.8939 | 183.624 | 183.3574 | 182.8571 | 181.507 | 180.1017 | 178.7697 | 150.9356 | 150.7564 | 150.4719 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1
|  | EGHAM | LW |  |  | 171.1925 | 171.1763 | 171.1519 | 199.8246 | 199.7966 | 199.7678 | 199.7506 | 199.7338 | 199.7137 | 199.6936 | 199.6541 | 199.5425 | 199.4268 | 199.3915 | 159.1837 | 158.9848 | 158.6872 | 185.0528 | 184.7113 | 184.3579 | 184.1478 | 183.9431 | 183.6972 | 183.451 | 182.9683 | 181.6034 | 180.1882 | 178.8152 | 150.9336 | 150.7411 | 150.4532 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1
|  | EGHAM | ST |  |  | 171.1989 | 171.1909 | 171.1808 | 199.8675 | 199.852 | 199.8314 | 199.817 | 199.8024 | 199.7866 | 199.7709 | 199.7417 | 199.671 | 199.6003 | 199.5301 | 159.2623 | 159.1636 | 159.0402 | 185.5778 | 185.3887 | 185.1366 | 184.9597 | 184.7822 | 184.5881 | 184.3966 | 184.0388 | 183.1753 | 182.3101 | 181.4512 | 151.0096 | 150.9142 | 150.7947 | 177.3376 | 177.1547 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1
|  | EGHAM | FS |  |  | 171.2031 | 171.1989 | 171.1952 | 199.8889 | 199.8822 | 199.8741 | 199.8688 | 199.8623 | 199.8558 | 199.8496 | 199.8377 | 199.8092 | 199.7812 | 199.754 | 159.3128 | 159.2613 | 159.216 | 185.8394 | 185.7571 | 185.6582 | 185.5936 | 185.514 | 185.4352 | 185.3592 | 185.2137 | 184.8651 | 184.5228 | 184.1896 | 151.0585 | 151.0086 | 150.9649 | 177.5907 | 177.5111 | 177.4154 | 177.3529 | 177.2758 | 177.1996 | 177.126 | 177.1 | 177.1 | 177.1 | 177.1
MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE | MINIMUM HEADROOM | SZ 08757 91379 | NO | 12.9066 | 12.9066 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 18.6379 | 17.9432 | 12.8499 | 12.8094 | 22.3901 | 22.2947 | 22.2194 | 22.141 | 22.0607 | 21.9782 | 21.9084 | 21.8648 | 21.8523 | 21.8088 | 18.6464 | 17.7963 | 12.856 | 12.7817 | 22.368 | 22.3238 | 22.2922 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 18.1466
|  | ELECTRIC HOUSE | CT |  |  | 12.9066 | 12.9066 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 18.6379 | 17.9432 | 12.8515 | 12.815 | 22.4012 | 22.3143 | 22.245 | 22.1713 | 22.0936 | 22.011 | 21.9364 | 21.8673 | 21.8548 | 21.8165 | 18.905 | 18.1663 | 12.8588 | 12.7919 | 22.3753 | 22.332 | 22.3029 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 18.5183
|  | ELECTRIC HOUSE | LW |  |  | 12.9066 | 12.9066 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 18.6379 | 17.9432 | 12.8499 | 12.8094 | 22.3901 | 22.2947 | 22.2194 | 22.141 | 22.0607 | 21.9782 | 21.9084 | 21.8648 | 21.8523 | 21.8088 | 18.6464 | 17.7963 | 12.856 | 12.7817 | 22.368 | 22.3238 | 22.2922 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 18.1466
|  | ELECTRIC HOUSE | ST |  |  | 12.9066 | 12.9066 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 18.9593 | 12.9239 | 12.8456 | 22.4714 | 22.4248 | 22.3848 | 22.3135 | 22.2401 | 22.164 | 22.0912 | 22.021 | 21.889 | 21.8409 | 21.8126 | 21.7846 | 12.9917 | 12.848 | 22.4496 | 22.3909 | 22.3645 | 22.3317 | 22.3009 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729 | 22.2729
|  | ELECTRIC HOUSE | FS |  |  | 12.9066 | 12.9066 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 21.9841 | 12.931 | 12.863 | 22.5088 | 22.488 | 22.4716 | 22.4456 | 22.4192 | 22.387 | 22.3589 | 22.331 | 22.2773 | 22.156 | 22.0424 | 21.9334 | 13.0048 | 12.88 | 22.5181 | 22.4799 | 22.4499 | 22.4046 | 22.3872 | 22.366 | 22.3508 | 22.3391 | 22.3165 | 22.2729 | 22.2729 | 22.2729
BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD | MINIMUM HEADROOM | SU 81057 68532 | YES | 39.6986 | 39.6523 | 39.6498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 55.9632 | 54.1082 | 32.7101 | 32.6189 | 32.5177 | 59.0981 | 59.0826 | 59.0826 | 59.0826 | 59.0826 | 52.7385 | 51.9842 | 50.5397 | 48.4401 | 46.2213 | 43.9648 | 33.9137 | 33.8254 | 33.7273 | 60.3587 | 60.3587 | 60.3587 | 60.3587 | 60.3587 | 53.2001 | 52.4378 | 50.996 | 48.9004 | 46.6858 | 44.4336
|  | ELMS ROAD | CT |  |  | 39.6986 | 39.6523 | 39.6498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 55.9632 | 54.1082 | 32.7105 | 32.6202 | 32.5206 | 59.1041 | 59.0826 | 59.0826 | 59.0826 | 59.0826 | 52.9044 | 52.1456 | 50.6926 | 48.4891 | 46.2213 | 43.9648 | 33.914 | 33.8266 | 33.7302 | 60.3587 | 60.3587 | 60.3587 | 60.3587 | 60.3587 | 53.368 | 52.6002 | 51.1486 | 48.9493 | 46.6858 | 44.4336
|  | ELMS ROAD | LW |  |  | 39.6986 | 39.6523 | 39.6498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 55.9632 | 54.1082 | 32.7101 | 32.6189 | 32.5177 | 59.0981 | 59.0826 | 59.0826 | 59.0826 | 59.0826 | 52.7385 | 51.9842 | 50.5397 | 48.4401 | 46.2524 | 44.0697 | 33.9137 | 33.8254 | 33.7273 | 60.3587 | 60.3587 | 60.3587 | 60.3587 | 60.3587 | 53.2001 | 52.4378 | 50.996 | 48.9004 | 46.7168 | 44.5383
|  | ELMS ROAD | ST |  |  | 39.7062 | 39.6951 | 39.6709 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 32.7251 | 32.7032 | 32.6555 | 59.2797 | 59.1881 | 59.1417 | 59.0942 | 59.0826 | 59.0826 | 59.0826 | 59.0826 | 59.0826 | 52.659 | 51.4234 | 33.9282 | 33.907 | 33.8608 | 60.4874 | 60.3987 | 60.3587 | 60.3587 | 60.3587 | 60.3587 | 60.3587 | 60.3587 | 60.3587 | 53.1197 | 51.8781
|  | ELMS ROAD | FS |  |  | 39.7119 | 39.71 | 39.7073 | 68.3961 | 68.383 | 68.3741 | 68.3648 | 68.3536 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 68.3498 | 32.7367 | 32.7326 | 32.7272 | 59.4052 | 59.3793 | 59.3618 | 59.3436 | 59.3215 | 59.3025 | 59.2835 | 59.248 | 59.1634 | 59.0826 | 59.0826 | 33.9391 | 33.9355 | 33.9303 | 60.6089 | 60.5839 | 60.5669 | 60.5492 | 60.5279 | 60.5094 | 60.491 | 60.4567 | 60.3748 | 60.3587 | 60.3587
LOVEDEAN GSP | HAVANT | EMSWORTH | MINIMUM HEADROOM | SU 74861 05807 | NO | 13.7599 | 13.7599 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 13.2744 | 13.2695 | 22.9164 | 22.9083 | 22.9007 | 22.8929 | 22.8864 | 22.8799 | 22.8731 | 22.865 | 22.8442 | 22.7597 | 22.6567 | 18.4064 | 15.1191 | 15.0998 | 24.7226 | 24.6908 | 24.6607 | 24.6298 | 24.6043 | 24.5787 | 24.5515 | 24.5197 | 24.4375 | 24.1039 | 23.6969 | 23.3605
|  | EMSWORTH | CT |  |  | 13.7599 | 13.7599 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 13.2744 | 13.2695 | 22.9164 | 22.9083 | 22.9007 | 22.8929 | 22.8864 | 22.8799 | 22.8731 | 22.8664 | 22.8535 | 22.7597 | 22.6567 | 18.4064 | 15.1191 | 15.0998 | 24.7226 | 24.6908 | 24.6607 | 24.6298 | 24.6043 | 24.5787 | 24.5515 | 24.5254 | 24.4743 | 24.1039 | 23.6969 | 23.3605
|  | EMSWORTH | LW |  |  | 13.7599 | 13.7599 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 13.275 | 13.2707 | 22.9195 | 22.9135 | 22.9081 | 22.9029 | 22.8999 | 22.8971 | 22.8938 | 22.8902 | 22.8819 | 22.7836 | 22.6774 | 18.6092 | 15.1215 | 15.1043 | 24.7349 | 24.7113 | 24.69 | 24.6692 | 24.6576 | 24.6463 | 24.6332 | 24.6192 | 24.5864 | 24.1982 | 23.7784 | 23.3868
|  | EMSWORTH | ST |  |  | 13.7599 | 13.7599 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 13.2815 | 13.2735 | 22.9252 | 22.9219 | 22.9186 | 22.9072 | 22.8969 | 22.8867 | 22.8757 | 22.865 | 22.8442 | 22.7827 | 22.7177 | 22.6535 | 15.1472 | 15.1154 | 24.7576 | 24.7444 | 24.7312 | 24.6865 | 24.6457 | 24.6053 | 24.562 | 24.5197 | 24.4375 | 24.1946 | 23.9377 | 23.684
|  | EMSWORTH | FS |  |  | 13.7599 | 13.7599 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 22.8374 | 13.2822 | 13.2753 | 22.9289 | 22.9274 | 22.926 | 22.9221 | 22.9187 | 22.9145 | 22.9103 | 22.9062 | 22.8982 | 22.8759 | 22.8512 | 22.8258 | 15.15 | 15.1227 | 24.772 | 24.7661 | 24.7608 | 24.7451 | 24.7319 | 24.7152 | 24.6987 | 24.6825 | 24.6507 | 24.5627 | 24.4653 | 24.365
MELKSHAM GSP | AMESBURY | ENFORD | MINIMUM HEADROOM | SU 13728 51712 | YES | 33.5725 | 33.5725 | 33.5725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 31.6666 | 31.6666 | 31.6666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 32.1887 | 32.1869 | 32.1828 | 58.8784 | 58.873 | 58.8671 | 58.8595 | 58.8488 | 58.8369 | 58.8251 | 58.8006 | 58.712 | 58.601 | 58.4894
|  | ENFORD | CT |  |  | 33.5725 | 33.5725 | 33.5725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 31.6666 | 31.6666 | 31.6666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 32.1887 | 32.1869 | 32.1829 | 58.8784 | 58.8732 | 58.8676 | 58.8614 | 58.8549 | 58.8477 | 58.8404 | 58.8243 | 58.7203 | 58.6116 | 58.5033
|  | ENFORD | LW |  |  | 33.5725 | 33.5725 | 33.5725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 31.6666 | 31.6666 | 31.6666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 32.1887 | 32.1869 | 32.1828 | 58.8784 | 58.873 | 58.8671 | 58.8605 | 58.8534 | 58.8451 | 58.8364 | 58.8176 | 58.712 | 58.601 | 58.4894
|  | ENFORD | ST |  |  | 33.5725 | 33.5725 | 33.5725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 31.6666 | 31.6666 | 31.6666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 32.1893 | 32.1886 | 32.1869 | 58.8843 | 58.8808 | 58.8703 | 58.8595 | 58.8488 | 58.8369 | 58.8251 | 58.8006 | 58.7343 | 58.668 | 58.6026
|  | ENFORD | FS |  |  | 33.5725 | 33.5725 | 33.5725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 62.2725 | 31.6666 | 31.6666 | 31.6666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 58.3666 | 32.1897 | 32.1896 | 32.1895 | 58.8888 | 58.8878 | 58.8843 | 58.8807 | 58.8761 | 58.8714 | 58.8666 | 58.857 | 58.8317 | 58.8056 | 58.7788
COWLEY GSP | YARNTON BSP | EYNSHAM | MINIMUM HEADROOM | SP 42236 10266 | YES | 16.4711 | 16.4711 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 13.9664 | 13.8967 | 23.411 | 23.3398 | 23.2704 | 23.2112 | 23.1495 | 23.1495 | 23.1495 | 23.1495 | 23.1495 | 23.1495 | 18.3984 | 17.6303 | 15.3061 | 15.3061 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 18.9635 | 18.2165
|  | EYNSHAM | CT |  |  | 16.4711 | 16.4711 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 13.9664 | 13.8967 | 23.411 | 23.3398 | 23.2704 | 23.2128 | 23.1557 | 23.1495 | 23.1495 | 23.1495 | 23.1495 | 23.1495 | 18.3984 | 17.6303 | 15.3061 | 15.3061 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 18.9635 | 18.2165
|  | EYNSHAM | LW |  |  | 16.4711 | 16.4711 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 13.9711 | 13.9032 | 23.4244 | 23.3447 | 23.2717 | 23.2112 | 23.1495 | 23.1495 | 23.1495 | 23.1495 | 23.1495 | 23.1495 | 18.7695 | 18.0035 | 15.3061 | 15.3061 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 18.5789
|  | EYNSHAM | ST |  |  | 16.4711 | 16.4711 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 13.9843 | 13.944 | 23.5153 | 23.398 | 23.3443 | 23.2822 | 23.2421 | 23.2028 | 23.1556 | 23.1495 | 23.1495 | 23.1495 | 23.1495 | 23.1495 | 15.3061 | 15.3061 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611
|  | EYNSHAM | FS |  |  | 16.4711 | 16.4711 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 25.5486 | 13.9972 | 13.9795 | 23.6025 | 23.5456 | 23.474 | 23.3976 | 23.37 | 23.343 | 23.3127 | 23.2853 | 23.2605 | 23.2181 | 23.1873 | 23.1581 | 15.3061 | 15.3061 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611 | 24.9611
MINETY GSP | CIRENCESTER BSP | FAIRFORD | MINIMUM HEADROOM | SP 14418 00559 | YES | 31.5118 | 31.5111 | 31.51 | 60.2086 | 60.2069 | 60.2049 | 56.687 | 56.6299 | 56.5698 | 56.5066 | 56.3815 | 55.8701 | 55.3156 | 54.7605 | 33.6388 | 33.6126 | 33.5528 | 60.1881 | 60.1188 | 53.3748 | 53.3171 | 53.2614 | 53.2031 | 53.1437 | 53.0268 | 52.5713 | 52.0804 | 51.5592 | 34.1924 | 34.1645 | 34.1014 | 60.7333 | 60.6602 | 60.5852 | 60.508 | 60.4335 | 60.3554 | 53.3899 | 53.357 | 53.2403 | 52.9393 | 52.4657
|  | FAIRFORD | CT |  |  | 31.5118 | 31.5111 | 31.51 | 60.2086 | 60.2069 | 60.2049 | 56.687 | 56.6299 | 56.5698 | 56.5066 | 56.3815 | 55.8701 | 55.3156 | 54.7605 | 33.6388 | 33.6126 | 33.5528 | 60.1881 | 60.1188 | 53.3748 | 53.3171 | 53.2614 | 53.2031 | 53.1437 | 53.0268 | 52.5713 | 52.0804 | 51.5592 | 34.1924 | 34.1645 | 34.1014 | 60.7333 | 60.6602 | 60.5852 | 60.508 | 60.4335 | 60.3554 | 53.3899 | 53.357 | 53.2403 | 52.9393 | 52.4657
|  | FAIRFORD | LW |  |  | 31.5118 | 31.5111 | 31.51 | 60.2086 | 60.2069 | 60.2049 | 56.687 | 56.6299 | 56.5698 | 56.5066 | 56.3815 | 55.8701 | 55.3156 | 54.7605 | 33.6428 | 33.6215 | 33.5723 | 60.2185 | 60.1594 | 60.0978 | 53.3651 | 53.316 | 53.2642 | 53.2099 | 53.103 | 52.6643 | 52.1921 | 51.7092 | 34.1972 | 34.1749 | 34.1236 | 60.7675 | 60.7057 | 60.6413 | 60.5748 | 60.5093 | 60.4403 | 60.3679 | 53.3947 | 53.2906 | 53.0637 | 52.6208
|  | FAIRFORD | ST |  |  | 31.5126 | 31.5123 | 31.512 | 60.2115 | 60.211 | 60.2103 | 60.2095 | 60.2087 | 56.6575 | 56.6061 | 56.5068 | 56.2136 | 55.9085 | 55.6041 | 33.6501 | 33.6378 | 33.6116 | 60.2722 | 60.2215 | 60.166 | 60.1096 | 53.3821 | 53.3375 | 53.2927 | 53.2062 | 52.9513 | 52.687 | 52.424 | 34.205 | 34.1922 | 34.165 | 60.824 | 60.7713 | 60.7135 | 60.6549 | 60.5986 | 60.5395 | 60.4802 | 60.3656 | 53.3801 | 53.3246 | 53.2675
|  | FAIRFORD | FS |  |  | 31.5127 | 31.5125 | 31.5123 | 60.212 | 60.2117 | 60.2114 | 60.211 | 60.2106 | 60.2102 | 60.2098 | 60.2089 | 60.2056 | 56.5836 | 56.4597 | 33.6568 | 33.6553 | 33.6536 | 60.3447 | 60.3331 | 60.3139 | 60.2947 | 60.2711 | 60.2481 | 60.2249 | 60.1801 | 53.3805 | 53.2748 | 53.1676 | 34.212 | 34.2104 | 34.2086 | 60.8993 | 60.8871 | 60.8671 | 60.8472 | 60.8225 | 60.7986 | 60.7744 | 60.7278 | 60.5958 | 60.4553 | 60.3128
MINETY GSP | STRATTON (2 X 60) | FARINGDON | MINIMUM HEADROOM | SU 28819 94924 | YES | 9.7871 | 9.6886 | 18.5817 | 18.3839 | 18.1837 | 17.9808 | 17.7753 | 17.589 | 17.3984 | 17.1902 | 16.7435 | 15.7512 | 14.6651 | 13.5696 | 9.1803 | 9.0602 | 18.4802 | 18.2297 | 17.9758 | 17.7164 | 17.4536 | 17.21 | 16.9561 | 16.7038 | 16.1879 | 15.0291 | 13.7798 | 12.5191 | 9.1776 | 9.0556 | 18.4726 | 18.2191 | 17.9619 | 17.6992 | 17.4328 | 17.1855 | 16.9277 | 16.671 | 16.1456 | 14.9608 | 13.6818 | 12.3872
|  | FARINGDON | CT |  |  | 9.7871 | 9.6886 | 18.5817 | 18.3839 | 18.1837 | 17.9808 | 17.7753 | 17.589 | 17.3984 | 17.1902 | 16.7435 | 15.7512 | 14.6651 | 13.5696 | 9.1803 | 9.0602 | 18.4802 | 18.2297 | 17.9758 | 17.7164 | 17.4536 | 17.21 | 16.9561 | 16.7038 | 16.1879 | 15.0291 | 13.7798 | 12.5191 | 9.1776 | 9.0556 | 18.4726 | 18.2191 | 17.9619 | 17.6992 | 17.4328 | 17.1855 | 16.9277 | 16.671 | 16.1456 | 14.9608 | 13.6818 | 12.3872
|  | FARINGDON | LW |  |  | 9.7871 | 9.6886 | 18.5817 | 18.3839 | 18.1837 | 17.9808 | 17.7753 | 17.589 | 17.3984 | 17.1902 | 16.7435 | 15.7512 | 14.6651 | 13.5696 | 9.1878 | 9.0732 | 18.5135 | 18.2833 | 18.0508 | 17.8152 | 17.577 | 17.3618 | 17.1417 | 16.9013 | 16.3866 | 15.2533 | 14.0203 | 12.7746 | 9.1864 | 9.0709 | 18.5097 | 18.2779 | 18.0434 | 17.8057 | 17.5652 | 17.3474 | 17.1246 | 16.8813 | 16.3596 | 15.2045 | 13.9431 | 12.6699
|  | FARINGDON | ST |  |  | 9.8689 | 9.7705 | 18.761 | 18.6375 | 18.488 | 18.3869 | 18.2836 | 18.1913 | 18.0967 | 18.0033 | 17.8102 | 17.2447 | 16.6538 | 16.067 | 9.2827 | 9.1679 | 18.7215 | 18.5774 | 18.403 | 18.2854 | 18.1653 | 18.0581 | 17.9482 | 17.8397 | 17.6155 | 16.9607 | 16.2787 | 15.6025 | 9.2822 | 9.1668 | 18.7197 | 18.5747 | 18.3994 | 18.2808 | 18.1599 | 18.0517 | 17.9409 | 17.8314 | 17.6053 | 16.9436 | 16.2531 | 15.5677
|  | FARINGDON | FS |  |  | 9.8955 | 9.88 | 18.8983 | 18.8639 | 18.8239 | 18.7849 | 18.7458 | 18.7023 | 18.661 | 18.6206 | 18.5399 | 18.3213 | 18.0803 | 17.8292 | 9.3138 | 9.2958 | 18.8817 | 18.8418 | 18.7952 | 18.7499 | 18.7045 | 18.6539 | 18.606 | 18.5591 | 18.4655 | 18.2128 | 17.935 | 17.6456 | 9.3134 | 9.2953 | 18.8808 | 18.8405 | 18.7936 | 18.7479 | 18.7021 | 18.6511 | 18.6028 | 18.5555 | 18.461 | 18.2054 | 17.9239 | 17.6306
LOVEDEAN GSP | WYMERING BSP | FARLINGTON | MINIMUM HEADROOM | SU 67400 04843 | NO | 28.1698 | 28.1689 | 28.1677 | 28.1662 | 28.1643 | 28.162 | 28.1592 | 28.156 | 28.1517 | 28.1469 | 28.1351 | 28.0932 | 28.0267 | 27.9396 | 25.623 | 25.6181 | 25.6072 | 25.5898 | 25.5696 | 25.5494 | 25.5284 | 25.5152 | 25.4984 | 25.4789 | 25.4329 | 25.2497 | 25.0572 | 24.8595 | 25.4308 | 25.4273 | 25.4211 | 25.4131 | 25.4041 | 25.3947 | 25.3848 | 25.3765 | 25.3656 | 25.3535 | 25.3271 | 25.2227 | 25.0829 | 24.9206
|  | FARLINGTON | CT |  |  | 28.1698 | 28.1689 | 28.1677 | 28.1662 | 28.1643 | 28.162 | 28.1592 | 28.156 | 28.1517 | 28.1469 | 28.1351 | 28.0932 | 28.0267 | 27.9396 | 25.623 | 25.6181 | 25.6072 | 25.5898 | 25.5696 | 25.5494 | 25.5284 | 25.5152 | 25.4984 | 25.4798 | 25.4429 | 25.2497 | 25.0572 | 24.8595 | 25.4308 | 25.4273 | 25.4211 | 25.4131 | 25.4041 | 25.3947 | 25.3848 | 25.3765 | 25.3656 | 25.3535 | 25.3271 | 25.2227 | 25.0829 | 24.9206
|  | FARLINGTON | LW |  |  | 28.1698 | 28.1689 | 28.1677 | 28.1662 | 28.1643 | 28.162 | 28.1592 | 28.156 | 28.1517 | 28.1469 | 28.1351 | 28.0932 | 28.0267 | 27.9396 | 25.625 | 25.6216 | 25.6128 | 25.5969 | 25.5775 | 25.5579 | 25.5363 | 25.5258 | 25.514 | 25.5019 | 25.4757 | 25.3068 | 25.1247 | 24.9446 | 25.4335 | 25.432 | 25.4288 | 25.4237 | 25.4175 | 25.4108 | 25.4033 | 25.398 | 25.3917 | 25.3847 | 25.3686 | 25.2929 | 25.1841 | 25.0544
|  | FARLINGTON | ST |  |  | 28.1706 | 28.1703 | 28.1699 | 28.1694 | 28.1689 | 28.1681 | 28.1672 | 28.1663 | 28.1652 | 28.1641 | 28.1617 | 28.1518 | 28.1361 | 28.1149 | 25.6267 | 25.6253 | 25.6214 | 25.6125 | 25.601 | 25.5745 | 25.5479 | 25.5268 | 25.5032 | 25.4789 | 25.4329 | 25.3168 | 25.2134 | 25.1164 | 25.4346 | 25.434 | 25.4327 | 25.4302 | 25.4269 | 25.4199 | 25.4127 | 25.4068 | 25.4002 | 25.3934 | 25.3803 | 25.3439 | 25.2993 | 25.2491
|  | FARLINGTON | FS |  |  | 28.1707 | 28.1705 | 28.1703 | 28.17 | 28.1696 | 28.1693 | 28.1689 | 28.1684 | 28.168 | 28.1675 | 28.1665 | 28.1628 | 28.1575 | 28.1515 | 25.6275 | 25.6271 | 25.6261 | 25.6224 | 25.6179 | 25.6093 | 25.6003 | 25.5922 | 25.5842 | 25.5762 | 25.5605 | 25.5235 | 25.4838 | 25.4393 | 25.4349 | 25.4346 | 25.4342 | 25.4331 | 25.4317 | 25.4293 | 25.4268 | 25.4245 | 25.4221 | 25.4198 | 25.4152 | 25.4031 | 25.3891 | 25.3734
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH | MINIMUM HEADROOM | SU 88404 53930 | NO | 34.4311 | 34.4035 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 27.8511 | 31.8772 | 31.7817 | 31.6544 | 31.5366 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 25.9696 | 24.5321 | 32.5206 | 32.4905 | 32.4503 | 32.4132 | 32.3666 | 32.3174 | 32.2572 | 32.2051 | 32.1617 | 32.1307 | 32.0736 | 32.0736 | 26.5389 | 25.1057
|  | FARNBOROUGH | CT |  |  | 34.4311 | 34.4035 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 27.8511 | 31.8821 | 31.8011 | 31.6923 | 31.5938 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 26.2661 | 24.8661 | 32.5221 | 32.4966 | 32.4623 | 32.4312 | 32.3909 | 32.3465 | 32.2922 | 32.2445 | 32.2031 | 32.169 | 32.107 | 32.0736 | 32.0736 | 25.4387
|  | FARNBOROUGH | LW |  |  | 34.4311 | 34.4035 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 27.8511 | 31.8772 | 31.7817 | 31.6544 | 31.5366 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 25.9696 | 24.5321 | 32.5206 | 32.4905 | 32.4503 | 32.4132 | 32.3666 | 32.3174 | 32.2572 | 32.2051 | 32.1617 | 32.1307 | 32.0736 | 32.0736 | 26.5389 | 25.1057
|  | FARNBOROUGH | ST |  |  | 34.4564 | 34.4236 | 34.4063 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 31.9646 | 31.8511 | 31.7914 | 31.7264 | 31.6315 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 31.5227 | 32.5481 | 32.5123 | 32.4935 | 32.4731 | 32.4431 | 32.4018 | 32.3541 | 32.3112 | 32.2712 | 32.2364 | 32.1717 | 32.0736 | 32.0736 | 32.0736
|  | FARNBOROUGH | FS |  |  | 34.4617 | 34.4544 | 34.4489 | 34.4418 | 34.4315 | 34.4174 | 34.4013 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 34.3968 | 31.9829 | 31.9577 | 31.9388 | 31.914 | 31.8786 | 31.8297 | 31.7741 | 31.7166 | 31.6657 | 31.6232 | 31.5414 | 31.5227 | 31.5227 | 31.5227 | 32.5539 | 32.546 | 32.54 | 32.5322 | 32.521 | 32.5056 | 32.4881 | 32.47 | 32.4539 | 32.4405 | 32.4147 | 32.3582 | 32.306 | 32.2555
BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM | MINIMUM HEADROOM | SU 84517 47217 | NO | 14.9476 | 14.7777 | 14.3695 | 13.9106 | 13.4468 | 12.9799 | 12.5105 | 12.0412 | 11.5605 | 11.0969 | 10.1863 | 8.978 | 7.7184 | 6.4652 | 17.4837 | 17.2717 | 16.7874 | 16.2522 | 15.7112 | 15.1667 | 14.6193 | 14.07 | 13.5029 | 12.956 | 11.8817 | 10.4562 | 8.9702 | 7.4918 | 18.1627 | 17.9482 | 17.4582 | 16.9167 | 16.3693 | 15.8183 | 15.2644 | 14.7105 | 14.1433 | 13.5962 | 12.5215 | 11.0956 | 9.6091 | 8.1302
|  | FARNHAM | CT |  |  | 14.9476 | 14.7777 | 14.3695 | 13.9106 | 13.4468 | 12.9799 | 12.5105 | 12.0412 | 11.5605 | 11.0969 | 10.1863 | 8.978 | 7.7184 | 6.4652 | 17.4912 | 17.2888 | 16.8239 | 16.3119 | 15.7933 | 15.2727 | 14.7556 | 14.2367 | 13.6895 | 13.1551 | 12.1074 | 10.6183 | 9.0853 | 7.5639 | 18.1704 | 17.9656 | 17.4952 | 16.977 | 16.4523 | 15.9256 | 15.4023 | 14.8773 | 14.3299 | 13.7953 | 12.7473 | 11.2577 | 9.7242 | 8.2023
|  | FARNHAM | LW |  |  | 14.9476 | 14.7777 | 14.3695 | 13.9106 | 13.4468 | 12.9799 | 12.5105 | 12.0412 | 11.5605 | 11.0969 | 10.1863 | 8.978 | 7.7184 | 6.4652 | 17.4837 | 17.2717 | 16.7874 | 16.2522 | 15.7112 | 15.1667 | 14.6193 | 14.07 | 13.5029 | 12.956 | 11.8817 | 10.4562 | 8.9702 | 7.4918 | 18.1627 | 17.9482 | 17.4582 | 16.9167 | 16.3693 | 15.8183 | 15.2644 | 14.7105 | 14.1433 | 13.5962 | 12.5215 | 11.0956 | 9.6091 | 8.1302
|  | FARNHAM | ST |  |  | 15.0306 | 14.957 | 14.8046 | 14.5668 | 14.2661 | 14.1041 | 13.943 | 13.7799 | 13.6139 | 13.4543 | 13.1449 | 12.4115 | 11.6841 | 10.9588 | 17.5872 | 17.4954 | 17.3053 | 17.0175 | 16.6669 | 16.4779 | 16.29 | 16.0998 | 15.9061 | 15.72 | 15.3592 | 14.5038 | 13.6487 | 12.793 | 18.2674 | 18.1746 | 17.9823 | 17.6911 | 17.3362 | 17.145 | 16.9549 | 16.7624 | 16.5665 | 16.3781 | 16.013 | 15.1475 | 14.2891 | 13.4331
|  | FARNHAM | FS |  |  | 15.0806 | 15.0647 | 15.0477 | 14.972 | 14.8832 | 14.8283 | 14.7726 | 14.7034 | 14.6364 | 14.5713 | 14.4441 | 14.1427 | 13.8546 | 13.5768 | 17.6495 | 17.6298 | 17.6085 | 17.5141 | 17.4033 | 17.3348 | 17.2654 | 17.179 | 17.0987 | 17.0227 | 16.8744 | 16.5229 | 16.1869 | 15.8629 | 18.3305 | 18.3106 | 18.2891 | 18.1935 | 18.0814 | 18.0121 | 17.9418 | 17.8545 | 17.7732 | 17.6963 | 17.5463 | 17.1906 | 16.8506 | 16.5228
IVER 132KV | SLOUGH | FARNHAM ROYAL | MINIMUM HEADROOM | SU 95597 82844 | NO | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 36.9829 | 36.2987 | 34.7171 | 33.1059 | 31.5037 | 40.2751 | 40.2068 | 40.1519 | 40.0913 | 40.0282 | 39.9698 | 39.9132 | 39.8569 | 36.6981 | 36.2991 | 35.4901 | 33.6202 | 31.7151 | 29.8207 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 36.6962 | 36.298 | 35.4905 | 33.6241 | 31.7226 | 29.8318
|  | FARNHAM ROYAL | CT |  |  | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 36.9829 | 36.2987 | 34.7171 | 33.1059 | 31.5037 | 40.2791 | 40.2138 | 40.1577 | 40.1012 | 40.0429 | 39.9891 | 39.9369 | 39.8836 | 36.881 | 36.5246 | 35.8191 | 34.0768 | 32.2514 | 30.4351 | 39.831 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 36.8787 | 36.523 | 35.8189 | 34.0798 | 32.2579 | 30.445
|  | FARNHAM ROYAL | LW |  |  | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 36.9829 | 36.2987 | 34.7171 | 33.1059 | 31.5037 | 40.2751 | 40.2068 | 40.1519 | 40.0913 | 40.0282 | 39.9698 | 39.9132 | 39.8569 | 36.6981 | 36.2991 | 35.4901 | 33.6202 | 31.7151 | 29.8207 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 36.6962 | 36.298 | 35.4905 | 33.6241 | 31.7226 | 29.8318
|  | FARNHAM ROYAL | ST |  |  | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 36.839 | 35.8094 | 34.79 | 40.3703 | 40.2865 | 40.2269 | 40.1857 | 40.1528 | 40.1172 | 40.0829 | 40.048 | 40.0101 | 39.9728 | 39.8994 | 36.129 | 34.9116 | 33.7063 | 39.8616 | 39.8335 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 36.1281 | 34.9131 | 33.71
|  | FARNHAM ROYAL | FS |  |  | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.4871 | 40.3861 | 40.3799 | 40.3677 | 40.3234 | 40.2698 | 40.2333 | 40.2031 | 40.1887 | 40.1745 | 40.1607 | 40.1335 | 40.0627 | 39.9903 | 39.919 | 39.8669 | 39.8648 | 39.8607 | 39.8458 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308 | 39.8308
LALEHAM | EAST BEDFONT A | FELTHAM | MINIMUM HEADROOM | TQ 10628 72811 | NO | 36.1473 | 36.1421 | 36.1303 | 36.1173 | 36.1038 | 36.0897 | 36.0751 | 36.0527 | 36.0284 | 36.003 | 35.9476 | 35.9001 | 35.8542 | 35.8083 | 35.5116 | 35.4952 | 35.4576 | 35.4159 | 35.3729 | 35.328 | 35.2814 | 35.2099 | 35.1323 | 35.096 | 35.0616 | 35.032 | 35.0034 | 34.9748 | 23.6987 | 23.6404 | 23.5074 | 23.36 | 23.2076 | 23.0489 | 22.8838 | 22.6307 | 22.3564 | 22.0698 | 21.4453 | 20.9092 | 20.3906 | 19.8735
|  | FELTHAM | CT |  |  | 36.1473 | 36.1421 | 36.1303 | 36.1173 | 36.1038 | 36.0897 | 36.0751 | 36.0527 | 36.0284 | 36.003 | 35.9476 | 35.9001 | 35.8542 | 35.8083 | 35.5127 | 35.4982 | 35.4647 | 35.4279 | 35.3899 | 35.35 | 35.3087 | 35.2456 | 35.1763 | 35.106 | 35.0735 | 35.0449 | 35.0198 | 34.9955 | 23.7023 | 23.651 | 23.5325 | 23.4024 | 23.2677 | 23.1265 | 22.9804 | 22.7572 | 22.5121 | 22.2517 | 21.6622 | 21.1429 | 20.6893 | 20.2478
|  | FELTHAM | LW |  |  | 36.1473 | 36.1421 | 36.1303 | 36.1173 | 36.1038 | 36.0897 | 36.0751 | 36.0527 | 36.0284 | 36.003 | 35.9476 | 35.9001 | 35.8542 | 35.8083 | 35.5116 | 35.4952 | 35.4576 | 35.4159 | 35.3729 | 35.328 | 35.2814 | 35.2099 | 35.1323 | 35.096 | 35.0616 | 35.032 | 35.0034 | 34.9748 | 23.6987 | 23.6404 | 23.5074 | 23.36 | 23.2076 | 23.0489 | 22.8838 | 22.6307 | 22.3564 | 22.0698 | 21.4453 | 20.9092 | 20.3906 | 19.8735
|  | FELTHAM | ST |  |  | 36.1493 | 36.147 | 36.1421 | 36.1353 | 36.1271 | 36.1199 | 36.1123 | 36.1002 | 36.0865 | 36.0718 | 36.0371 | 36.0024 | 35.9733 | 35.9452 | 35.5182 | 35.5107 | 35.4949 | 35.4732 | 35.4474 | 35.4241 | 35.4 | 35.3613 | 35.3179 | 35.2708 | 35.1603 | 35.0956 | 35.0775 | 35.06 | 23.7218 | 23.6955 | 23.6396 | 23.5627 | 23.4712 | 23.3889 | 23.3035 | 23.1666 | 23.0131 | 22.8463 | 22.4553 | 22.0634 | 21.7346 | 21.4175
|  | FELTHAM | FS |  |  | 36.1539 | 36.1497 | 36.1484 | 36.1458 | 36.1428 | 36.14 | 36.137 | 36.132 | 36.1266 | 36.1208 | 36.1077 | 36.0935 | 36.0817 | 36.0706 | 35.5219 | 35.5193 | 35.5152 | 35.5068 | 35.4972 | 35.4883 | 35.4789 | 35.4628 | 35.4455 | 35.427 | 35.3853 | 35.3402 | 35.3023 | 35.2669 | 23.7349 | 23.7259 | 23.7114 | 23.6816 | 23.6477 | 23.6159 | 23.5829 | 23.5259 | 23.4647 | 23.3991 | 23.2516 | 23.092 | 22.9579 | 22.8327
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN | MINIMUM HEADROOM | SU 06593 00685 | YES | 30.3443 | 30.3111 | 30.2311 | 30.1331 | 30.0138 | 29.8771 | 29.6757 | 29.475 | 29.241 | 28.9989 | 28.5043 | 26.747 | 25.0334 | 23.4875 | 31.4776 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 30.3177 | 30.0983 | 29.8423 | 29.5776 | 29.0092 | 26.939 | 24.9203 | 23.0992 | 30.3346 | 30.2956 | 30.2017 | 30.0866 | 29.9464 | 29.7859 | 29.5493 | 29.3137 | 29.0388 | 28.7546 | 28.1737 | 26.1099 | 24.0973 | 22.2817
|  | FERNDOWN | CT |  |  | 30.3443 | 30.3111 | 30.2311 | 30.1331 | 30.0138 | 29.8848 | 29.7463 | 29.6055 | 29.424 | 29.2277 | 28.8211 | 26.747 | 25.0334 | 23.4875 | 31.4799 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 30.385 | 30.3173 | 30.1417 | 29.9524 | 29.554 | 27.93 | 26.3334 | 24.7286 | 30.3369 | 30.3009 | 30.2142 | 30.1086 | 29.9814 | 29.8444 | 29.6978 | 29.5489 | 29.3604 | 29.157 | 28.7292 | 27.0978 | 25.506 | 23.9062
|  | FERNDOWN | LW |  |  | 30.3443 | 30.3111 | 30.2311 | 30.1331 | 30.0138 | 29.8848 | 29.7463 | 29.6055 | 29.424 | 29.2277 | 28.8211 | 26.747 | 25.0334 | 23.4875 | 31.4776 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 30.3713 | 30.241 | 30.0425 | 29.8278 | 29.3823 | 26.939 | 24.9203 | 23.0992 | 30.3346 | 30.2956 | 30.2017 | 30.0866 | 29.9464 | 29.7949 | 29.6323 | 29.4669 | 29.2538 | 29.0232 | 28.5457 | 26.1099 | 24.0973 | 22.2817
|  | FERNDOWN | ST |  |  | 30.3511 | 30.3265 | 30.272 | 30.187 | 30.0752 | 29.8771 | 29.6757 | 29.475 | 29.241 | 28.9989 | 28.5043 | 27.3911 | 26.3477 | 25.3113 | 31.4856 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 30.3177 | 30.0983 | 29.8423 | 29.5776 | 29.0092 | 27.6978 | 26.4686 | 25.2477 | 30.3426 | 30.3137 | 30.2497 | 30.1499 | 30.0185 | 29.7859 | 29.5493 | 29.3137 | 29.0388 | 28.7546 | 28.1737 | 26.8663 | 25.6408 | 24.4236
|  | FERNDOWN | FS |  |  | 30.3641 | 30.3604 | 30.354 | 30.3358 | 30.3108 | 30.2499 | 30.188 | 30.1127 | 30.0301 | 29.9445 | 29.7714 | 29.2643 | 28.7925 | 28.3985 | 31.5009 | 31.4965 | 31.489 | 31.4676 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 31.4589 | 30.3775 | 29.8678 | 29.3487 | 28.8845 | 30.3578 | 30.3535 | 30.346 | 30.3246 | 30.2953 | 30.2237 | 30.1511 | 30.0626 | 29.9656 | 29.8651 | 29.6618 | 29.0662 | 28.5121 | 28.0494
BRAMLEY (FLEE) | FERNHURST | FIVE OAKS | MINIMUM HEADROOM | TQ 10647 29057 | YES | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 24.4337 | 24.3757 | 24.2532 | 24.143 | 24.0181 | 23.8762 | 23.7023 | 23.4983 | 23.2827 | 23.1643 | 23.1525 | 23.1525 | 23.1525 | 23.1525 | 24.8463 | 24.8277 | 24.7834 | 24.7343 | 24.6787 | 24.6155 | 24.538 | 24.4472 | 24.4336 | 24.4336 | 24.4336 | 24.4336 | 24.4336 | 24.4336
|  | FIVE OAKS | CT |  |  | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 24.4401 | 24.3915 | 24.2808 | 24.1884 | 24.083 | 23.9628 | 23.8206 | 23.6534 | 23.4698 | 23.3371 | 23.1525 | 23.1525 | 23.1525 | 23.1525 | 24.8484 | 24.8328 | 24.7957 | 24.7545 | 24.7076 | 24.654 | 24.5907 | 24.5163 | 24.4345 | 24.4336 | 24.4336 | 24.4336 | 24.4336 | 24.4336
|  | FIVE OAKS | LW |  |  | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 24.4337 | 24.3757 | 24.2532 | 24.143 | 24.0181 | 23.8762 | 23.7023 | 23.4983 | 23.2827 | 23.1643 | 23.1525 | 23.1525 | 23.1525 | 23.1525 | 24.8463 | 24.8277 | 24.7834 | 24.7343 | 24.6787 | 24.6155 | 24.538 | 24.4472 | 24.4336 | 24.4336 | 24.4336 | 24.4336 | 24.4336 | 24.4336
|  | FIVE OAKS | ST |  |  | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 24.4841 | 24.4138 | 24.3341 | 24.2361 | 24.123 | 24.0562 | 23.9748 | 23.8767 | 23.7668 | 23.6912 | 23.5574 | 23.2639 | 23.1525 | 23.1525 | 24.8624 | 24.8399 | 24.8144 | 24.7757 | 24.7254 | 24.6957 | 24.6594 | 24.6157 | 24.5668 | 24.5331 | 24.4735 | 24.4336 | 24.4336 | 24.4336
|  | FIVE OAKS | FS |  |  | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 25.9748 | 24.5036 | 24.4995 | 24.4938 | 24.4673 | 24.4307 | 24.397 | 24.3533 | 24.2952 | 24.2499 | 24.2206 | 24.169 | 24.048 | 23.944 | 23.8432 | 24.8687 | 24.8674 | 24.8656 | 24.8571 | 24.8453 | 24.8345 | 24.8206 | 24.8019 | 24.7819 | 24.7688 | 24.7459 | 24.692 | 24.6457 | 24.6008
AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH | MINIMUM HEADROOM | SU 90667 89318 | NO | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 23.9961 | 23.9904 | 23.9769 | 23.9623 | 23.9477 | 23.9331 | 23.9186 | 23.9043 | 23.8885 | 23.8728 | 23.8415 | 23.7492 | 23.6528 | 23.5574 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 23.1721 | 22.1071
|  | FLACKWELL HEATH | CT |  |  | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 23.9962 | 23.9906 | 23.9774 | 23.9631 | 23.9488 | 23.9345 | 23.9204 | 23.9064 | 23.8913 | 23.8763 | 23.8463 | 23.7525 | 23.6547 | 23.5581 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 23.1941 | 22.115
|  | FLACKWELL HEATH | LW |  |  | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 23.9961 | 23.9904 | 23.9769 | 23.9623 | 23.9477 | 23.9331 | 23.9186 | 23.9043 | 23.8885 | 23.8728 | 23.8415 | 23.7492 | 23.6528 | 23.5574 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 23.1721 | 22.1071
|  | FLACKWELL HEATH | ST |  |  | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 23.9979 | 23.9946 | 23.9874 | 23.9766 | 23.9635 | 23.9521 | 23.9408 | 23.9297 | 23.9177 | 23.9059 | 23.8825 | 23.824 | 23.7651 | 23.7065 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 23.7721
|  | FLACKWELL HEATH | FS |  |  | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 34.1122 | 23.9997 | 23.9993 | 23.9989 | 23.9965 | 23.9935 | 23.9897 | 23.9859 | 23.981 | 23.9762 | 23.9715 | 23.9623 | 23.9395 | 23.9172 | 23.8959 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705 | 27.705
NURSLING GSP | ROWNHAMS | FLETCHWOOD | MINIMUM HEADROOM | SU 33800 12142 | NO | 35.1102 | 35.1049 | 35.0941 | 35.081 | 35.0664 | 35.0501 | 35.0329 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 33.4465 | 33.4221 | 33.3727 | 33.3124 | 33.2458 | 33.171 | 33.0926 | 33.0106 | 32.9223 | 32.8316 | 32.6391 | 32.4002 | 26.145 | 24.6412 | 33.3412 | 33.3311 | 33.3105 | 33.2854 | 33.2576 | 33.2264 | 33.1938 | 33.1596 | 33.1228 | 33.085 | 33.0048 | 32.7723 | 32.694 | 25.7106
|  | FLETCHWOOD | CT |  |  | 35.1102 | 35.1049 | 35.0941 | 35.081 | 35.0664 | 35.0501 | 35.0329 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 33.4468 | 33.4233 | 33.3743 | 33.3154 | 33.2508 | 33.179 | 33.106 | 33.029 | 32.9435 | 32.8527 | 32.6579 | 32.4038 | 26.232 | 24.7493 | 33.3414 | 33.3315 | 33.3111 | 33.2866 | 33.2597 | 33.2298 | 33.1993 | 33.1672 | 33.1316 | 33.0938 | 33.0126 | 32.7784 | 32.694 | 25.8169
|  | FLETCHWOOD | LW |  |  | 35.1102 | 35.1049 | 35.0941 | 35.081 | 35.0664 | 35.0501 | 35.0329 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 33.4465 | 33.4221 | 33.3727 | 33.3124 | 33.2458 | 33.171 | 33.0926 | 33.0106 | 32.9223 | 32.8316 | 32.6391 | 32.4002 | 26.145 | 24.6412 | 33.3412 | 33.3311 | 33.3105 | 33.2854 | 33.2576 | 33.2264 | 33.1938 | 33.1596 | 33.1228 | 33.085 | 33.0048 | 32.7723 | 32.694 | 25.7106
|  | FLETCHWOOD | ST |  |  | 35.112 | 35.1092 | 35.1042 | 35.0959 | 35.0854 | 35.068 | 35.0504 | 35.0325 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 35.0242 | 33.4547 | 33.442 | 33.4187 | 33.3811 | 33.333 | 33.253 | 33.1727 | 33.0905 | 32.9995 | 32.905 | 32.7067 | 32.4599 | 32.3715 | 26.3948 | 33.3446 | 33.3394 | 33.3297 | 33.314 | 33.2939 | 33.2606 | 33.2272 | 33.1929 | 33.155 | 33.1156 | 33.033 | 32.8733 | 32.7224 | 32.694
|  | FLETCHWOOD | FS |  |  | 35.1134 | 35.1127 | 35.1121 | 35.1098 | 35.1069 | 35.101 | 35.0949 | 35.0875 | 35.0798 | 35.0721 | 35.056 | 35.0242 | 35.0242 | 35.0242 | 33.461 | 33.4579 | 33.455 | 33.4445 | 33.4313 | 33.4041 | 33.3765 | 33.3423 | 33.3074 | 33.2717 | 33.1982 | 33.0525 | 32.9152 | 32.7849 | 33.3473 | 33.346 | 33.3448 | 33.3404 | 33.3349 | 33.3236 | 33.312 | 33.2978 | 33.2832 | 33.2684 | 33.2378 | 33.177 | 33.1199 | 33.0655
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE | MINIMUM HEADROOM | SU 14069 15523 | YES | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 21.7423 | 21.732 | 21.7114 | 21.6947 | 21.6817 | 21.6632 | 21.6398 | 21.6052 | 21.5689 | 21.5392 | 21.4807 | 21.3266 | 21.184 | 21.1409 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019
|  | FORDINGBRIDGE | CT |  |  | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 21.7423 | 21.733 | 21.7138 | 21.6979 | 21.6854 | 21.6681 | 21.6465 | 21.615 | 21.5819 | 21.5527 | 21.4912 | 21.3266 | 21.184 | 21.1409 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019
|  | FORDINGBRIDGE | LW |  |  | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 21.7423 | 21.732 | 21.7114 | 21.6947 | 21.6817 | 21.6632 | 21.6398 | 21.6052 | 21.5689 | 21.5392 | 21.4807 | 21.3297 | 21.1929 | 21.1409 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019
|  | FORDINGBRIDGE | ST |  |  | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 21.7436 | 21.738 | 21.7275 | 21.718 | 21.7067 | 21.68 | 21.6539 | 21.6214 | 21.5864 | 21.5539 | 21.4863 | 21.3728 | 21.2794 | 21.1877 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019
|  | FORDINGBRIDGE | FS |  |  | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 25.9402 | 21.7443 | 21.7417 | 21.7374 | 21.7336 | 21.7292 | 21.7175 | 21.7043 | 21.689 | 21.6756 | 21.6635 | 21.6387 | 21.5951 | 21.5615 | 21.5297 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019 | 22.1019
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK | MINIMUM HEADROOM | SU 66139 00180 | NO | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 32.0059 | 31.9307 | 31.8185 | 31.694 | 31.5583 | 31.3765 | 31.1992 | 31.0181 | 30.9331 | 30.9331 | 30.9331 | 30.9331 | 30.9331 | 30.9331 | 31.9887 | 31.9555 | 31.906 | 31.8511 | 31.7882 | 31.6759 | 31.5664 | 31.4546 | 31.376 | 31.3085 | 31.1721 | 30.9607 | 30.9607 | 24.3189
|  | FRATTON PARK | CT |  |  | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 32.0087 | 31.9418 | 31.8375 | 31.7241 | 31.5983 | 31.4993 | 31.4105 | 31.3131 | 31.2053 | 31.0914 | 30.9331 | 30.9331 | 30.9331 | 30.9331 | 31.9899 | 31.9604 | 31.9144 | 31.8644 | 31.8089 | 31.7518 | 31.697 | 31.6368 | 31.5702 | 31.4999 | 31.3872 | 31.0899 | 30.9607 | 30.9607
|  | FRATTON PARK | LW |  |  | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 32.0059 | 31.9307 | 31.8185 | 31.694 | 31.5634 | 31.4671 | 31.3772 | 31.2814 | 31.1784 | 31.0712 | 30.9331 | 30.9331 | 30.9331 | 30.9331 | 31.9887 | 31.9555 | 31.906 | 31.8511 | 31.7914 | 31.7319 | 31.6763 | 31.6172 | 31.5536 | 31.4874 | 31.3827 | 31.0528 | 30.9607 | 24.3189
|  | FRATTON PARK | ST |  |  | 34.2051 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 32.4538 | 31.9602 | 31.8583 | 31.7193 | 31.5583 | 31.3765 | 31.1992 | 31.0181 | 30.9331 | 30.9331 | 30.9331 | 30.9331 | 30.9331 | 30.9331 | 32.1863 | 31.9686 | 31.9236 | 31.8623 | 31.7882 | 31.6759 | 31.5664 | 31.4546 | 31.376 | 31.3085 | 31.1721 | 30.9607 | 30.9607 | 24.6211
|  | FRATTON PARK | FS |  |  | 34.222 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 34.098 | 32.4902 | 32.0369 | 32.0146 | 31.9842 | 31.951 | 31.8703 | 31.7928 | 31.6971 | 31.6001 | 31.5233 | 31.3816 | 31.1164 | 30.9331 | 30.9331 | 32.2023 | 32.0024 | 31.9926 | 31.9792 | 31.9645 | 31.9289 | 31.8947 | 31.8525 | 31.8097 | 31.7666 | 31.6791 | 31.5153 | 31.3871 | 31.2914
COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD | MINIMUM HEADROOM | SP 50426 08256 | NO | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 14.1389 | 21.2628 | 21.1977 | 21.0572 | 21.0225 | 20.9945 | 20.9669 | 20.9396 | 20.9107 | 20.8788 | 20.8492 | 20.7926 | 13.3713 | 12.264 | 11.1763 | 22.1415 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 13.3028 | 12.2392 | 11.1944
|  | FRENCHAY ROAD | CT |  |  | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 14.1389 | 21.2631 | 21.2001 | 21.0617 | 21.0237 | 20.9961 | 20.9686 | 20.9411 | 20.9123 | 20.881 | 20.8517 | 20.7951 | 13.3713 | 12.264 | 11.1763 | 22.1417 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 13.3028 | 12.2392 | 11.1944
|  | FRENCHAY ROAD | LW |  |  | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 14.1389 | 21.2628 | 21.1977 | 21.0572 | 21.0225 | 20.9945 | 20.9669 | 20.9396 | 20.9107 | 20.8788 | 20.8492 | 20.7926 | 13.4608 | 12.4879 | 11.5296 | 22.1415 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 13.3888 | 12.4543 | 11.5338
|  | FRENCHAY ROAD | ST |  |  | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 21.29 | 21.2682 | 21.228 | 21.1728 | 21.1073 | 21.08 | 21.0519 | 21.0436 | 21.0363 | 21.0304 | 21.0196 | 20.9937 | 20.9688 | 20.944 | 22.1578 | 22.1447 | 22.1207 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175
|  | FRENCHAY ROAD | FS |  |  | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 23.77 | 21.2978 | 21.2913 | 21.2849 | 21.261 | 21.233 | 21.2217 | 21.2107 | 21.1945 | 21.1775 | 21.163 | 21.1362 | 21.0742 | 21.0433 | 21.0329 | 22.1624 | 22.1585 | 22.1547 | 22.1404 | 22.1237 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175 | 22.1175
FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER | MINIMUM HEADROOM | SZ 34325 86965 | YES | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 13.1319 | 12.7664 | 12.3062 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 12.9587
|  | FRESHWATER | CT |  |  | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 13.2598 | 12.8492 | 12.4388 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 13.1012
|  | FRESHWATER | LW |  |  | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 13.2208 | 12.7664 | 12.3062 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 12.9587
|  | FRESHWATER | ST |  |  | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 13.1319 | 12.7823 | 12.4383 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 13.1006
|  | FRESHWATER | FS |  |  | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 16.0723 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 15.0514 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842 | 14.6842
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY | MINIMUM HEADROOM | SU 87745 57942 | NO | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 34.213 | 34.1849 | 34.1216 | 34.0475 | 33.973 | 33.8981 | 33.8227 | 33.7682 | 33.7542 | 33.7404 | 33.7132 | 33.639 | 33.5778 | 25.9927 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601
|  | FRIMLEY | CT |  |  | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 34.2153 | 34.1889 | 34.1311 | 34.0637 | 33.9961 | 33.9283 | 33.8608 | 33.7924 | 33.764 | 33.751 | 33.7254 | 33.6537 | 33.5778 | 26.3313 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601
|  | FRIMLEY | LW |  |  | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 34.213 | 34.1849 | 34.1216 | 34.0475 | 33.973 | 33.8981 | 33.8227 | 33.7682 | 33.7542 | 33.7404 | 33.7132 | 33.639 | 33.5778 | 25.9927 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601
|  | FRIMLEY | ST |  |  | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 34.2293 | 34.2143 | 34.1898 | 34.1523 | 34.1073 | 34.0571 | 34.0075 | 33.9574 | 33.9079 | 33.8588 | 33.7715 | 33.7256 | 33.6769 | 33.6287 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601
|  | FRIMLEY | FS |  |  | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 41.8455 | 34.2369 | 34.2344 | 34.2314 | 34.2126 | 34.196 | 34.1787 | 34.1613 | 34.1393 | 34.1195 | 34.1001 | 34.0622 | 33.9704 | 33.8763 | 33.7847 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601 | 37.2601
MELKSHAM GSP | FROME BSP | FROME | MINIMUM HEADROOM | ST 78850 48051 | NO | 63.9072 | 63.8913 | 63.8605 | 63.8255 | 63.7895 | 63.7569 | 63.7257 | 56.4641 | 56.2051 | 55.9396 | 55.385 | 53.9844 | 52.6005 | 50.7451 | 57.5933 | 57.4016 | 57.0282 | 56.6044 | 53.1004 | 52.7127 | 52.3437 | 51.962 | 51.5503 | 51.1287 | 50.2485 | 48.0308 | 45.9247 | 43.8082 | 53.3984 | 53.3972 | 53.3955 | 53.1573 | 52.73 | 52.3455 | 51.9794 | 51.6007 | 51.1922 | 50.7736 | 49.8901 | 47.6582 | 45.534 | 43.3946
|  | FROME | CT |  |  | 63.9072 | 63.8913 | 63.8605 | 63.8255 | 63.7895 | 63.7569 | 63.7257 | 56.4641 | 56.2051 | 55.9396 | 55.385 | 53.9844 | 52.6005 | 50.7451 | 57.6011 | 57.4327 | 57.0985 | 56.7239 | 53.269 | 52.9187 | 52.5724 | 52.195 | 51.7782 | 51.3497 | 50.4873 | 48.4669 | 46.4662 | 44.4603 | 53.3984 | 53.3972 | 53.3955 | 53.2737 | 52.8948 | 52.5468 | 52.2027 | 51.8278 | 51.4133 | 50.9871 | 50.1234 | 48.0841 | 46.0587 | 44.0238
|  | FROME | LW |  |  | 63.9072 | 63.8913 | 63.8605 | 63.8255 | 63.7895 | 63.7569 | 63.7257 | 56.4641 | 56.2051 | 55.9396 | 55.385 | 53.9844 | 52.6005 | 50.7451 | 57.5933 | 57.4016 | 57.0282 | 56.6044 | 53.1004 | 52.7127 | 52.3437 | 51.962 | 51.5503 | 51.1287 | 50.2485 | 48.0308 | 45.9247 | 43.8082 | 53.3995 | 53.3991 | 53.3986 | 53.1573 | 52.73 | 52.3455 | 51.9794 | 51.6007 | 51.1922 | 50.7736 | 49.8901 | 47.6582 | 45.534 | 43.3946
|  | FROME | ST |  |  | 63.9244 | 63.9019 | 63.8846 | 63.861 | 63.8336 | 63.8094 | 63.7855 | 63.76 | 63.7317 | 56.5133 | 56.069 | 55.1516 | 54.2875 | 53.433 | 57.8002 | 57.5247 | 57.3136 | 57.0253 | 56.6918 | 53.3257 | 53.0374 | 52.7299 | 52.3884 | 52.0375 | 51.3291 | 49.8687 | 48.4965 | 47.1428 | 53.3998 | 53.3997 | 53.3995 | 53.3993 | 53.2437 | 52.9538 | 52.668 | 52.3632 | 52.0246 | 51.6767 | 50.9745 | 49.5112 | 48.1316 | 46.7695
|  | FROME | FS |  |  | 63.9282 | 63.9116 | 63.9069 | 63.8991 | 63.8907 | 63.8819 | 63.8736 | 63.8635 | 63.8532 | 63.8426 | 63.8207 | 63.7721 | 63.7284 | 56.4101 | 57.8467 | 57.6435 | 57.586 | 57.4918 | 57.3904 | 57.2846 | 57.1832 | 57.0614 | 56.9363 | 56.8086 | 56.5439 | 52.8947 | 52.3864 | 51.8778 | 53.3998 | 53.3998 | 53.3997 | 53.3995 | 53.3994 | 53.3992 | 53.3991 | 53.3989 | 53.3987 | 53.3586 | 53.0977 | 52.5259 | 52.0215 | 51.5166
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE | MINIMUM HEADROOM | SU 84935 93873 | NO | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 26.2816 | 26.2178 | 26.1304 | 26.0363 | 25.9441 | 25.8528 | 25.7625 | 25.6731 | 25.5743 | 25.4756 | 25.3124 | 25.076 | 25.076 | 18.9019 | 27.4356 | 27.4239 | 27.4079 | 27.3906 | 27.3737 | 27.357 | 27.3405 | 27.3241 | 27.306 | 27.2879 | 27.252 | 27.1537 | 27.1537 | 19.1597
|  | FRYERS LANE | CT |  |  | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 26.2862 | 26.2327 | 26.1602 | 26.0823 | 26.0043 | 25.9241 | 25.8421 | 25.7654 | 25.6827 | 25.6026 | 25.4415 | 25.1004 | 25.076 | 25.076 | 27.4364 | 27.4266 | 27.4133 | 27.399 | 27.3847 | 27.3701 | 27.355 | 27.341 | 27.3258 | 27.3112 | 27.2816 | 27.183 | 27.1537 | 27.1537
|  | FRYERS LANE | LW |  |  | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 26.2816 | 26.2178 | 26.1304 | 26.0363 | 25.9441 | 25.8528 | 25.7625 | 25.6731 | 25.5743 | 25.4756 | 25.3124 | 25.076 | 25.076 | 18.9019 | 27.4356 | 27.4239 | 27.4079 | 27.3906 | 27.3737 | 27.357 | 27.3405 | 27.3241 | 27.306 | 27.2879 | 27.252 | 27.1537 | 27.1537 | 19.1597
|  | FRYERS LANE | ST |  |  | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 26.296 | 26.2579 | 26.2098 | 26.1381 | 26.0512 | 25.979 | 25.9062 | 25.8373 | 25.763 | 25.6912 | 25.5491 | 25.2464 | 25.0768 | 25.076 | 27.4382 | 27.4312 | 27.4224 | 27.4093 | 27.3934 | 27.3801 | 27.3668 | 27.3542 | 27.3406 | 27.3274 | 27.3013 | 27.236 | 27.1697 | 27.1537
|  | FRYERS LANE | FS |  |  | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 29.7166 | 26.3112 | 26.2989 | 26.2954 | 26.2793 | 26.2601 | 26.2359 | 26.2124 | 26.1822 | 26.1524 | 26.1233 | 26.067 | 25.929 | 25.793 | 25.6633 | 27.441 | 27.4387 | 27.4381 | 27.4351 | 27.4316 | 27.4272 | 27.4229 | 27.4173 | 27.4119 | 27.4066 | 27.3962 | 27.371 | 27.346 | 27.3223
COWLEY GSP | DRAYTON BSP | FULSCOT | MINIMUM HEADROOM | SU 54413 89511 | YES | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 19.7391 | 23.2498 | 23.2154 | 23.1595 | 23.0999 | 23.0313 | 22.9573 | 22.8843 | 22.8213 | 22.7747 | 22.7361 | 18.1599 | 16.9547 | 15.5862 | 14.1828 | 23.7938 | 23.7767 | 23.7489 | 23.7193 | 23.6852 | 23.6484 | 23.6121 | 23.5808 | 23.5496 | 18.6512 | 18.0301 | 16.8245 | 15.4555 | 14.0516
|  | FULSCOT | CT |  |  | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 19.7391 | 23.2501 | 23.2181 | 23.1635 | 23.106 | 23.0397 | 22.9671 | 22.8952 | 22.8291 | 22.7757 | 22.7361 | 18.1599 | 16.9547 | 15.5862 | 14.1828 | 23.7939 | 23.778 | 23.7509 | 23.7223 | 23.6893 | 23.6533 | 23.6175 | 23.5847 | 23.5504 | 18.6512 | 18.0301 | 16.8245 | 15.4555 | 14.0516
|  | FULSCOT | LW |  |  | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 19.7391 | 23.2498 | 23.2154 | 23.1595 | 23.0999 | 23.0313 | 22.9573 | 22.8843 | 22.8213 | 22.7747 | 22.7405 | 18.338 | 17.2917 | 15.9257 | 14.505 | 23.7938 | 23.7767 | 23.7489 | 23.7193 | 23.6852 | 23.6484 | 23.6121 | 23.5808 | 23.5496 | 23.5191 | 18.2082 | 17.1615 | 15.7951 | 14.374
|  | FULSCOT | ST |  |  | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 23.277 | 23.2443 | 23.2198 | 23.1901 | 23.1513 | 23.1055 | 23.0603 | 23.019 | 22.9753 | 22.9297 | 22.8682 | 22.7678 | 18.2973 | 17.4458 | 23.8127 | 23.7911 | 23.7789 | 23.7641 | 23.7448 | 23.7221 | 23.6996 | 23.6791 | 23.6573 | 23.6347 | 23.6041 | 23.5434 | 18.1676 | 17.3157
|  | FULSCOT | FS |  |  | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 28.1076 | 23.3414 | 23.2603 | 23.2508 | 23.2375 | 23.2213 | 23.2029 | 23.185 | 23.1675 | 23.15 | 23.1325 | 23.1078 | 23.0573 | 23.0136 | 22.9598 | 23.8295 | 23.7992 | 23.7943 | 23.7877 | 23.7796 | 23.7705 | 23.7616 | 23.7529 | 23.7442 | 23.7355 | 23.7232 | 23.6981 | 23.6764 | 23.6496
COWLEY GSP | WITNEY BSP | FYFIELD | MINIMUM HEADROOM | SU 42256 99551 | YES | 24.9269 | 24.9159 | 24.89 | 24.861 | 24.8307 | 24.7993 | 24.7666 | 24.7388 | 24.7157 | 24.6919 | 24.6438 | 24.5697 | 24.5196 | 24.49 | 21.756 | 21.6741 | 21.4787 | 21.4475 | 21.4184 | 21.3882 | 21.3572 | 21.3288 | 21.3027 | 21.276 | 21.225 | 21.1405 | 21.0544 | 20.9689 | 13.3232 | 13.2399 | 13.041 | 12.8212 | 12.5952 | 12.3613 | 12.1209 | 11.9008 | 11.6981 | 11.4919 | 11.096 | 10.4411 | 9.7736 | 9.1114
|  | FYFIELD | CT |  |  | 24.9269 | 24.9159 | 24.89 | 24.861 | 24.8307 | 24.7993 | 24.7666 | 24.7388 | 24.7157 | 24.6919 | 24.6438 | 24.5697 | 24.5196 | 24.49 | 21.756 | 21.6741 | 21.4787 | 21.4475 | 21.4184 | 21.3882 | 21.3572 | 21.3288 | 21.3027 | 21.276 | 21.225 | 21.1405 | 21.0544 | 20.9689 | 13.3232 | 13.2399 | 13.041 | 12.8212 | 12.5952 | 12.3613 | 12.1209 | 11.9008 | 11.6981 | 11.4919 | 11.096 | 10.4411 | 9.7736 | 9.1114
|  | FYFIELD | LW |  |  | 24.9269 | 24.9159 | 24.89 | 24.861 | 24.8307 | 24.7993 | 24.7666 | 24.7388 | 24.7157 | 24.6919 | 24.6438 | 24.5697 | 24.5196 | 24.49 | 21.7622 | 21.6865 | 21.5077 | 21.4534 | 21.4261 | 21.3976 | 21.3681 | 21.3429 | 21.322 | 21.3005 | 21.2569 | 21.1812 | 21.1018 | 21.0224 | 13.3295 | 13.2525 | 13.0706 | 12.8671 | 12.655 | 12.4343 | 12.2052 | 12.0105 | 11.8482 | 11.6814 | 11.3438 | 10.7565 | 10.1412 | 9.5255
|  | FYFIELD | ST |  |  | 24.931 | 24.9272 | 24.9187 | 24.907 | 24.8931 | 24.8782 | 24.8627 | 24.849 | 24.8374 | 24.8255 | 24.803 | 24.7497 | 24.6977 | 24.6462 | 21.7907 | 21.7644 | 21.7058 | 21.6254 | 21.5296 | 21.4691 | 21.455 | 21.4426 | 21.4322 | 21.4213 | 21.401 | 21.3528 | 21.3058 | 21.2592 | 23.6733 | 13.3317 | 13.2721 | 13.1903 | 13.0928 | 12.9883 | 12.879 | 12.783 | 12.7021 | 12.6181 | 12.4603 | 12.0867 | 11.7222 | 11.3612
|  | FYFIELD | FS |  |  | 24.9321 | 24.9307 | 24.9281 | 24.9229 | 24.9169 | 24.911 | 24.9048 | 24.8989 | 24.8943 | 24.8896 | 24.8806 | 24.8596 | 24.8395 | 24.8194 | 21.7979 | 21.7883 | 21.7706 | 21.7348 | 21.6932 | 21.6526 | 21.6102 | 21.5693 | 21.5374 | 21.5055 | 21.4712 | 21.4522 | 21.434 | 21.4158 | 23.674 | 23.6731 | 13.3381 | 13.3016 | 13.2593 | 13.218 | 13.1748 | 13.1332 | 13.1007 | 13.0683 | 13.0047 | 12.8575 | 12.7164 | 12.5755
LOVEDEAN GSP | HAVANT | GABLE HEAD | MINIMUM HEADROOM | SZ 72204 99904 | NO | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 74.5413 | 74.5389 | 74.5327 | 74.5254 | 74.5168 | 74.5104 | 74.5026 | 74.4933 | 74.4829 | 74.4724 | 74.4515 | 74.3982 | 74.3982 | 74.3982 | 48.2806 | 48.2703 | 48.2442 | 48.2131 | 48.1764 | 48.149 | 48.1161 | 48.0764 | 48.0323 | 47.9875 | 47.8988 | 47.6429 | 47.3227 | 47.0055
|  | GABLE HEAD | CT |  |  | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 74.5418 | 74.5403 | 74.5364 | 74.5315 | 74.5256 | 74.5215 | 74.517 | 74.5119 | 74.5061 | 74.5 | 74.4878 | 74.4194 | 74.3982 | 74.3982 | 48.2829 | 48.2765 | 48.2596 | 48.239 | 48.2137 | 48.1966 | 48.1771 | 48.1555 | 48.131 | 48.1049 | 48.0532 | 47.7621 | 47.4605 | 47.1618
|  | GABLE HEAD | LW |  |  | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 74.5413 | 74.5389 | 74.5327 | 74.5254 | 74.5168 | 74.5104 | 74.5036 | 74.4966 | 74.4889 | 74.4807 | 74.4634 | 74.3982 | 74.3982 | 74.3982 | 48.2806 | 48.2703 | 48.2442 | 48.2131 | 48.1764 | 48.149 | 48.1201 | 48.0906 | 48.0576 | 48.0228 | 47.9494 | 47.6429 | 47.3227 | 47.0055
|  | GABLE HEAD | ST |  |  | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 74.5415 | 74.5397 | 74.5352 | 74.5288 | 74.5206 | 74.5118 | 74.5026 | 74.4933 | 74.4829 | 74.4724 | 74.4515 | 74.4015 | 74.3982 | 74.3982 | 48.2817 | 48.2736 | 48.2547 | 48.2273 | 48.1926 | 48.155 | 48.1161 | 48.0764 | 48.0323 | 47.9875 | 47.8988 | 47.6859 | 47.4749 | 47.2682
|  | GABLE HEAD | FS |  |  | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 83.6852 | 74.5424 | 74.542 | 74.5411 | 74.5395 | 74.5375 | 74.5345 | 74.5315 | 74.5278 | 74.524 | 74.5202 | 74.5126 | 74.4948 | 74.4766 | 74.4585 | 48.2853 | 48.2835 | 48.2797 | 48.2729 | 48.2643 | 48.2517 | 48.2389 | 48.223 | 48.207 | 48.1909 | 48.1586 | 48.0827 | 48.0054 | 47.9282
LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD | MINIMUM HEADROOM | SU 64771 01769 | NO | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 30.7403 | 30.6916 | 30.6179 | 30.5315 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 26.4902 | 25.7993 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 26.326
|  | GAMBLE ROAD | CT |  |  | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 30.7417 | 30.6959 | 30.6277 | 30.5495 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 26.2336 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326
|  | GAMBLE ROAD | LW |  |  | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 30.7403 | 30.6916 | 30.6179 | 30.5315 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 26.4902 | 25.7993 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 26.326
|  | GAMBLE ROAD | ST |  |  | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 30.8168 | 30.7275 | 30.6788 | 30.6299 | 30.5714 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 26.5354 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326
|  | GAMBLE ROAD | FS |  |  | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 33.159 | 30.8276 | 30.7527 | 30.7285 | 30.696 | 30.6723 | 30.64 | 30.6059 | 30.5611 | 30.5127 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 30.4934 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326 | 31.3326
IVER 132KV | DENHAM | GERRARDS CROSS | MINIMUM HEADROOM | SU 99973 87964 | NO | 23.072 | 23.0274 | 22.921 | 22.8058 | 22.6905 | 22.576 | 22.4616 | 22.3535 | 22.3035 | 22.2539 | 22.1558 | 22.0548 | 21.9503 | 21.8465 | 13.4076 | 13.4076 | 13.4076 | 12.2266 | 11.7668 | 11.3104 | 10.8544 | 10.4013 | 9.9132 | 9.4295 | 8.4717 | 7.4849 | 6.4645 | 5.4509 | 13.4076 | 13.4076 | 13.4076 | 12.2302 | 11.7718 | 11.3168 | 10.8622 | 10.4104 | 9.9239 | 9.4416 | 8.4867 | 7.5029 | 6.4857 | 5.4751
|  | GERRARDS CROSS | CT |  |  | 23.072 | 23.0274 | 22.921 | 22.8058 | 22.6905 | 22.576 | 22.4616 | 22.3535 | 22.3035 | 22.2539 | 22.1558 | 22.0548 | 21.9503 | 21.8465 | 13.4076 | 13.4076 | 13.4076 | 12.3257 | 11.9048 | 11.4881 | 11.0736 | 10.6615 | 10.2178 | 9.777 | 8.903 | 7.8274 | 6.7172 | 5.6173 | 13.4076 | 13.4076 | 13.4076 | 12.329 | 11.9094 | 11.4939 | 11.0808 | 10.6699 | 10.2275 | 9.788 | 8.9167 | 7.8444 | 6.7375 | 5.641
|  | GERRARDS CROSS | LW |  |  | 23.072 | 23.0274 | 22.921 | 22.8058 | 22.6905 | 22.576 | 22.4616 | 22.3535 | 22.3035 | 22.2539 | 22.1558 | 22.0548 | 21.9503 | 21.8465 | 13.4076 | 13.4076 | 13.4076 | 12.2266 | 11.7668 | 11.3104 | 10.8544 | 10.4013 | 9.9132 | 9.4295 | 8.4717 | 7.4849 | 6.4645 | 5.4509 | 13.4076 | 13.4076 | 13.4076 | 12.2302 | 11.7718 | 11.3168 | 10.8622 | 10.4104 | 9.9239 | 9.4416 | 8.4867 | 7.5029 | 6.4857 | 5.4751
|  | GERRARDS CROSS | ST |  |  | 23.0935 | 23.0799 | 23.0501 | 23.005 | 22.9501 | 22.9219 | 22.8938 | 22.8657 | 22.8354 | 22.8053 | 22.7455 | 22.5971 | 22.4495 | 22.335 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 12.3446 | 12.2247 | 11.9862 | 11.3945 | 10.8062 | 10.2214 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 12.3479 | 12.2283 | 11.9905 | 11.4006 | 10.8142 | 10.2311
|  | GERRARDS CROSS | FS |  |  | 23.1 | 23.0975 | 23.0946 | 23.0768 | 23.0554 | 23.0454 | 23.0353 | 23.0224 | 23.0097 | 22.9971 | 22.9723 | 22.9115 | 22.8524 | 22.7955 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 12.1856 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 13.4076 | 12.1893
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM | MINIMUM HEADROOM | ST 80185 25765 | YES | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 31.3643 | 31.3622 | 31.3576 | 31.3486 | 31.3366 | 31.3243 | 31.3101 | 31.2958 | 31.2781 | 31.2561 | 31.2186 | 31.1213 | 26.6127 | 26.2527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 26.4831
|  | GILLINGHAM | CT |  |  | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 31.3644 | 31.3625 | 31.3584 | 31.3503 | 31.3398 | 31.329 | 31.3171 | 31.3043 | 31.2875 | 31.2662 | 31.2283 | 31.1685 | 31.1356 | 31.1043 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527
|  | GILLINGHAM | LW |  |  | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 31.3643 | 31.3622 | 31.3576 | 31.3486 | 31.3366 | 31.3243 | 31.3101 | 31.2958 | 31.2781 | 31.2561 | 31.2186 | 31.1213 | 26.6127 | 26.2527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 26.4831
|  | GILLINGHAM | ST |  |  | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 31.4027 | 31.3638 | 31.3614 | 31.3562 | 31.3491 | 31.3402 | 31.3307 | 31.3205 | 31.3072 | 31.2905 | 31.2597 | 31.2163 | 31.194 | 31.1732 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527
|  | GILLINGHAM | FS |  |  | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 33.9814 | 31.4032 | 31.3648 | 31.3637 | 31.3613 | 31.3582 | 31.3547 | 31.3508 | 31.3467 | 31.3416 | 31.3355 | 31.3243 | 31.2968 | 31.2827 | 31.2737 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527 | 31.3527
BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING | MINIMUM HEADROOM | SU 96743 44375 | YES | 28.1699 | 28.0359 | 27.7248 | 27.3976 | 27.0689 | 26.7413 | 26.4151 | 26.0928 | 25.7395 | 25.3863 | 24.6912 | 23.6015 | 22.4348 | 20.8617 | 26.5142 | 26.3705 | 26.0349 | 25.6802 | 25.3249 | 24.9719 | 24.6208 | 24.2746 | 23.8968 | 23.5202 | 22.7777 | 21.5876 | 19.6052 | 17.6362 | 26.6816 | 26.6674 | 26.6341 | 26.599 | 26.5638 | 26.5288 | 26.494 | 26.3208 | 25.7001 | 25.0812 | 23.8611 | 21.9724 | 19.996 | 18.0331
|  | GODALMING | CT |  |  | 28.1699 | 28.0359 | 27.7248 | 27.3976 | 27.0689 | 26.7413 | 26.4151 | 26.0928 | 25.7395 | 25.3863 | 24.6912 | 23.6015 | 22.4348 | 20.8617 | 26.5142 | 26.3705 | 26.0349 | 25.6802 | 25.3249 | 24.9719 | 24.6208 | 24.2746 | 23.8968 | 23.5202 | 22.7777 | 21.5876 | 19.6052 | 17.6362 | 26.6816 | 26.6674 | 26.6341 | 26.599 | 26.5638 | 26.5288 | 26.494 | 26.3208 | 25.7001 | 25.0812 | 23.8611 | 21.9724 | 19.996 | 18.0331
|  | GODALMING | LW |  |  | 28.1699 | 28.0359 | 27.7248 | 27.3976 | 27.0689 | 26.7413 | 26.4151 | 26.0928 | 25.7395 | 25.3863 | 24.6912 | 23.6015 | 22.4348 | 20.8617 | 26.522 | 26.3894 | 26.0819 | 25.7584 | 25.4335 | 25.1096 | 24.7871 | 24.4684 | 24.1191 | 23.77 | 23.0827 | 22.0054 | 20.3482 | 18.495 | 26.6824 | 26.6692 | 26.6388 | 26.6067 | 26.5745 | 26.5425 | 26.5105 | 26.4789 | 26.0654 | 25.4916 | 24.3622 | 22.5919 | 20.7368 | 18.8893
|  | GODALMING | ST |  |  | 28.3103 | 28.1719 | 28.0575 | 27.893 | 27.6918 | 27.5686 | 27.4459 | 27.3256 | 27.1926 | 27.0597 | 26.7996 | 26.1576 | 25.507 | 24.8576 | 26.6608 | 26.524 | 26.4108 | 26.2482 | 26.0492 | 25.9274 | 25.8061 | 25.6872 | 25.5557 | 25.4244 | 25.1672 | 24.5325 | 23.8892 | 23.2473 | 26.6961 | 26.6826 | 26.6714 | 26.6552 | 26.6355 | 26.6235 | 26.6115 | 26.5997 | 26.5867 | 26.5736 | 26.5482 | 26.4853 | 25.6876 | 24.6327
|  | GODALMING | FS |  |  | 28.3377 | 28.2712 | 28.2311 | 28.1769 | 28.112 | 28.0684 | 28.0249 | 27.9695 | 27.9137 | 27.858 | 27.7495 | 27.4856 | 27.2247 | 26.9722 | 26.6879 | 26.6221 | 26.5824 | 26.5289 | 26.4647 | 26.4216 | 26.3786 | 26.3239 | 26.2686 | 26.2136 | 26.1064 | 25.8454 | 25.5875 | 25.3378 | 26.6988 | 26.6923 | 26.6884 | 26.6831 | 26.6767 | 26.6724 | 26.6682 | 26.6627 | 26.6573 | 26.6518 | 26.6412 | 26.6153 | 26.5898 | 26.5651
WILLESDEN GSP | ACTON LANE | GOLDSMITHS | MINIMUM HEADROOM | TQ 21089 80758 | NO | 15.3738 | 15.3679 | 15.3561 | 15.3427 | 15.3285 | 15.3136 | 15.3024 | 15.2926 | 15.2808 | 15.2687 | 15.2436 | 15.1349 | 15.0254 | 14.9171 | 14.2391 | 14.198 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 10.85 | 14.357 | 14.3191 | 14.2432 | 14.157 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 10.5309
|  | GOLDSMITHS | CT |  |  | 15.3738 | 15.3679 | 15.3561 | 15.3427 | 15.3285 | 15.3136 | 15.3024 | 15.2926 | 15.2808 | 15.2687 | 15.2436 | 15.1349 | 15.0254 | 14.9171 | 14.2399 | 14.2025 | 14.1254 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.3578 | 14.3232 | 14.2521 | 14.1724 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 10.689
|  | GOLDSMITHS | LW |  |  | 15.3738 | 15.3679 | 15.3561 | 15.3427 | 15.3285 | 15.3136 | 15.3024 | 15.2926 | 15.2808 | 15.2687 | 15.2436 | 15.1349 | 15.0254 | 14.9171 | 14.2391 | 14.198 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 10.85 | 14.357 | 14.3191 | 14.2432 | 14.157 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 10.5309
|  | GOLDSMITHS | ST |  |  | 15.3787 | 15.3728 | 15.3672 | 15.3595 | 15.3503 | 15.3359 | 15.3236 | 15.3119 | 15.2984 | 15.2846 | 15.2579 | 15.1929 | 15.13 | 15.068 | 14.2534 | 14.2321 | 14.193 | 14.1395 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.3702 | 14.3506 | 14.3145 | 14.2651 | 14.206 | 14.1129 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977 | 14.0977
|  | GOLDSMITHS | FS |  |  | 15.3823 | 15.3793 | 15.3754 | 15.3716 | 15.3685 | 15.3628 | 15.3582 | 15.3528 | 15.3471 | 15.3414 | 15.3302 | 15.3028 | 15.2767 | 15.2512 | 14.2637 | 14.2551 | 14.2438 | 14.2242 | 14.2019 | 14.1622 | 14.1301 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.1242 | 14.3797 | 14.3718 | 14.3614 | 14.3433 | 14.3227 | 14.2861 | 14.2564 | 14.2216 | 14.185 | 14.1485 | 14.0977 | 14.0977 | 14.0977 | 14.0977
NURSLING GSP | WINCHESTER | GORDON ROAD | MINIMUM HEADROOM | SU 48217 29991 | NO | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 28.2786 | 27.6723 | 26.4176 | 25.0556 | 23.6977 | 26.5985 | 26.4488 | 26.0846 | 25.667 | 25.2324 | 24.7762 | 24.339 | 23.9347 | 23.5179 | 23.0952 | 22.2745 | 20.8044 | 19.2255 | 17.6495 | 30.1429 | 29.9914 | 29.8893 | 29.8606 | 29.8606 | 26.6035 | 26.2133 | 25.8524 | 25.4805 | 25.1033 | 24.3708 | 23.0587 | 21.6496 | 20.243
|  | GORDON ROAD | CT |  |  | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 28.2786 | 27.6723 | 26.4176 | 25.0556 | 23.6977 | 26.5985 | 26.4488 | 26.0846 | 25.667 | 25.2324 | 24.7762 | 24.339 | 23.9347 | 23.5179 | 23.0952 | 22.2745 | 20.8044 | 19.2255 | 17.6495 | 30.1429 | 29.9914 | 29.8893 | 29.8606 | 29.8606 | 26.6035 | 26.2133 | 25.8524 | 25.4805 | 25.1033 | 24.3708 | 23.0587 | 21.6496 | 20.243
|  | GORDON ROAD | LW |  |  | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 28.2786 | 27.6723 | 26.4176 | 25.0556 | 23.6977 | 26.6092 | 26.4755 | 26.149 | 25.7688 | 25.3675 | 24.9392 | 24.5235 | 24.1538 | 23.7898 | 23.4185 | 22.6784 | 21.2759 | 19.7533 | 18.2354 | 30.1538 | 30.0185 | 29.8947 | 29.8628 | 29.8606 | 29.8606 | 26.3779 | 26.048 | 25.7232 | 25.3917 | 24.7312 | 23.4795 | 22.1207 | 20.7659
|  | GORDON ROAD | ST |  |  | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 28.127 | 27.4001 | 26.6684 | 26.6196 | 26.5081 | 26.3269 | 26.099 | 25.9052 | 25.7235 | 25.5631 | 25.4025 | 25.2371 | 24.9219 | 24.0957 | 23.2332 | 22.3741 | 30.2137 | 30.1643 | 30.0514 | 29.9096 | 29.8905 | 29.8743 | 29.8606 | 29.8606 | 29.8606 | 29.8606 | 29.8606 | 25.9962 | 25.2264 | 24.4597
|  | GORDON ROAD | FS |  |  | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 32.9546 | 26.6926 | 26.6842 | 26.6714 | 26.6044 | 26.521 | 26.4478 | 26.3777 | 26.3026 | 26.2341 | 26.1665 | 26.0356 | 25.7062 | 25.3601 | 25.0115 | 30.2382 | 30.2297 | 30.2168 | 30.1489 | 30.0645 | 29.9904 | 29.9194 | 29.9075 | 29.9018 | 29.8961 | 29.8852 | 29.8606 | 29.8606 | 29.8606
BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING | MINIMUM HEADROOM | SU 60305 82895 | YES | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 17.7285 | 17.7048 | 17.6477 | 17.5853 | 17.5231 | 17.4611 | 17.3996 | 17.3384 | 17.2723 | 17.241 | 17.2318 | 17.214 | 17.1935 | 17.1813 | 18.903 | 18.8784 | 18.8192 | 18.7545 | 18.6899 | 18.6256 | 18.5734 | 18.5347 | 18.5019 | 18.4693 | 18.4051 | 18.2869 | 18.2341 | 18.1806
|  | GORING | CT |  |  | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 17.7285 | 17.7048 | 17.6477 | 17.5853 | 17.5231 | 17.4611 | 17.3996 | 17.3384 | 17.2723 | 17.241 | 17.2318 | 17.214 | 17.1935 | 17.1813 | 18.903 | 18.8784 | 18.8192 | 18.7545 | 18.6899 | 18.6256 | 18.5734 | 18.5347 | 18.5019 | 18.4693 | 18.4051 | 18.2869 | 18.2341 | 18.1806
|  | GORING | LW |  |  | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 17.7365 | 17.7248 | 17.6962 | 17.6645 | 17.6326 | 17.6005 | 17.5685 | 17.5365 | 17.502 | 17.4678 | 17.4002 | 17.2394 | 17.2207 | 17.2017 | 18.9113 | 18.8991 | 18.8695 | 18.8366 | 18.8035 | 18.7702 | 18.737 | 18.7039 | 18.6681 | 18.6325 | 18.5738 | 18.4579 | 18.3276 | 18.2551
|  | GORING | ST |  |  | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 17.7417 | 17.7375 | 17.7281 | 17.7135 | 17.6956 | 17.6701 | 17.6448 | 17.6196 | 17.5922 | 17.5651 | 17.5121 | 17.3843 | 17.2431 | 17.2324 | 18.9167 | 18.9123 | 18.9026 | 18.8875 | 18.8689 | 18.8424 | 18.8161 | 18.79 | 18.7616 | 18.7335 | 18.6785 | 18.563 | 18.4839 | 18.409
|  | GORING | FS |  |  | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 18.5938 | 17.7439 | 17.7435 | 17.7429 | 17.7392 | 17.7348 | 17.7256 | 17.7165 | 17.7048 | 17.6932 | 17.6817 | 17.6593 | 17.6064 | 17.5532 | 17.4929 | 18.919 | 18.9185 | 18.9179 | 18.9141 | 18.9095 | 18.9 | 18.8906 | 18.8784 | 18.8663 | 18.8544 | 18.8312 | 18.7763 | 18.7211 | 18.6586
IVER 132KV | DENHAM | GRASSINGHAM ROAD | MINIMUM HEADROOM | TQ 00165 90988 | NO | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 248.8186 | 248.7718 | 248.6603 | 248.5395 | 248.42 | 248.3017 | 248.1796 | 248.0573 | 247.926 | 247.795 | 247.5354 | 247.1289 | 246.9392 | 246.7577 | 319.487 | 319.4756 | 319.4486 | 319.4194 | 319.3904 | 319.3618 | 319.3322 | 319.3026 | 319.2708 | 319.239 | 319.1762 | 319.0777 | 318.9752 | 318.8731
|  | GRASSINGHAM ROAD | CT |  |  | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 248.82 | 248.7754 | 248.6689 | 248.5536 | 248.4395 | 248.3266 | 248.2114 | 248.0968 | 247.9742 | 247.8521 | 247.6081 | 247.1921 | 246.9623 | 246.7774 | 319.4873 | 319.4765 | 319.4507 | 319.4228 | 319.3952 | 319.3678 | 319.3399 | 319.3121 | 319.2824 | 319.2529 | 319.1938 | 319.093 | 318.9883 | 318.8841
|  | GRASSINGHAM ROAD | LW |  |  | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 248.8186 | 248.7718 | 248.6603 | 248.5395 | 248.42 | 248.3017 | 248.1796 | 248.0573 | 247.926 | 247.795 | 247.5354 | 247.1289 | 246.9392 | 246.7577 | 319.487 | 319.4756 | 319.4486 | 319.4194 | 319.3904 | 319.3618 | 319.3322 | 319.3026 | 319.2708 | 319.239 | 319.1762 | 319.0777 | 318.9752 | 318.8731
|  | GRASSINGHAM ROAD | ST |  |  | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 248.8931 | 248.8147 | 248.7671 | 248.6953 | 248.6089 | 248.5632 | 248.5158 | 248.4686 | 248.4183 | 248.3683 | 248.2681 | 248.0162 | 247.7639 | 247.5124 | 319.505 | 319.486 | 319.4745 | 319.4571 | 319.4362 | 319.4251 | 319.4136 | 319.4022 | 319.39 | 319.3779 | 319.3536 | 319.2926 | 319.2315 | 319.1706
|  | GRASSINGHAM ROAD | FS |  |  | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 331.2344 | 248.9045 | 248.9017 | 248.8417 | 248.8224 | 248.7993 | 248.7836 | 248.7675 | 248.7466 | 248.7262 | 248.7058 | 248.6656 | 248.566 | 248.4678 | 248.3724 | 319.5078 | 319.5071 | 319.4926 | 319.4879 | 319.4823 | 319.4785 | 319.4746 | 319.4695 | 319.4646 | 319.4597 | 319.4499 | 319.4258 | 319.402 | 319.3789
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET | MINIMUM HEADROOM | SU 64445 00178 | NO | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 26.6386 | 26.6226 | 26.5711 | 26.5127 | 26.4431 | 26.3785 | 26.311 | 26.2666 | 26.219 | 26.1719 | 26.0732 | 25.7943 | 25.4407 | 25.087 | 26.6388 | 26.6228 | 26.5715 | 26.5132 | 26.4439 | 26.3795 | 26.3122 | 26.2679 | 26.2205 | 26.1736 | 26.0751 | 25.7971 | 25.4445 | 25.0919
|  | GREETHAM STREET | CT |  |  | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 26.6387 | 26.6227 | 26.5727 | 26.5166 | 26.4511 | 26.3906 | 26.3284 | 26.2814 | 26.2291 | 26.1741 | 26.0732 | 25.7997 | 25.4844 | 25.1687 | 26.6389 | 26.6229 | 26.5731 | 26.5172 | 26.4519 | 26.3915 | 26.3295 | 26.2827 | 26.2305 | 26.1757 | 26.0751 | 25.8024 | 25.4881 | 25.1734
|  | GREETHAM STREET | LW |  |  | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 26.6386 | 26.6226 | 26.5711 | 26.5127 | 26.4431 | 26.3785 | 26.311 | 26.2666 | 26.219 | 26.1719 | 26.0788 | 25.7943 | 25.4407 | 25.087 | 26.6388 | 26.6228 | 26.5715 | 26.5132 | 26.4439 | 26.3795 | 26.3122 | 26.2679 | 26.2205 | 26.1736 | 26.0807 | 25.7971 | 25.4445 | 25.0919
|  | GREETHAM STREET | ST |  |  | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 26.6449 | 26.6378 | 26.6144 | 26.5813 | 26.5369 | 26.4873 | 26.437 | 26.397 | 26.3526 | 26.3066 | 26.2216 | 26.0161 | 25.7893 | 25.5636 | 26.6451 | 26.638 | 26.6147 | 26.5817 | 26.5374 | 26.488 | 26.4378 | 26.3979 | 26.3537 | 26.3078 | 26.223 | 26.0181 | 25.7921 | 25.5671
|  | GREETHAM STREET | FS |  |  | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 39.3721 | 26.699 | 26.6477 | 26.6423 | 26.631 | 26.6161 | 26.5988 | 26.5809 | 26.5647 | 26.5485 | 26.5325 | 26.5011 | 26.4307 | 26.358 | 26.2765 | 26.699 | 26.6479 | 26.6424 | 26.6313 | 26.6163 | 26.5991 | 26.5812 | 26.5651 | 26.549 | 26.533 | 26.5017 | 26.4315 | 26.359 | 26.2778
COWLEY GSP | DRAYTON BSP | GROVE | MINIMUM HEADROOM | SU 39515 89611 | NO | 14.0702 | 13.9651 | 13.8145 | 13.6583 | 13.4888 | 13.2884 | 13.0695 | 12.7579 | 12.5409 | 12.3335 | 11.8568 | 10.2875 | 9.1924 | 8.2296 | 13.2265 | 13.1027 | 12.9253 | 12.7413 | 12.5416 | 12.3056 | 12.0477 | 11.6806 | 11.425 | 11.1807 | 10.6191 | 8.7704 | 7.4804 | 6.3462 | 13.2269 | 13.1034 | 12.9266 | 12.7432 | 12.5441 | 12.3087 | 12.0517 | 11.6857 | 11.4309 | 11.1873 | 10.6274 | 8.7844 | 7.4983 | 6.3675
|  | GROVE | CT |  |  | 14.0702 | 13.9651 | 13.8145 | 13.6583 | 13.4888 | 13.2884 | 13.0695 | 12.7579 | 12.5409 | 12.3335 | 11.8568 | 10.2875 | 9.1924 | 8.2296 | 13.227 | 13.1134 | 12.9397 | 12.7627 | 12.5685 | 12.334 | 12.0789 | 11.7256 | 11.4525 | 11.1989 | 10.6334 | 9.2802 | 8.1567 | 7.0477 | 13.2274 | 13.1142 | 12.9409 | 12.7645 | 12.5709 | 12.3371 | 12.0828 | 11.7306 | 11.4583 | 11.2054 | 10.6417 | 9.2926 | 8.1725 | 7.0669
|  | GROVE | LW |  |  | 14.0702 | 13.9651 | 13.8145 | 13.6583 | 13.4888 | 13.2884 | 13.0695 | 12.7579 | 12.5409 | 12.3335 | 11.8568 | 10.2875 | 9.1924 | 8.2296 | 13.2265 | 13.1027 | 12.9253 | 12.7413 | 12.5416 | 12.3056 | 12.0477 | 11.6806 | 11.425 | 11.1807 | 10.6191 | 8.7704 | 7.4804 | 6.3462 | 13.2269 | 13.1034 | 12.9266 | 12.7432 | 12.5441 | 12.3087 | 12.0517 | 11.6857 | 11.4309 | 11.1873 | 10.6274 | 8.7844 | 7.4983 | 6.3675
|  | GROVE | ST |  |  | 14.1017 | 14.0435 | 13.9671 | 13.8819 | 13.7803 | 13.6198 | 13.4483 | 13.2219 | 13.0355 | 12.8587 | 12.4646 | 11.7111 | 11.1336 | 10.5749 | 13.2636 | 13.1951 | 13.105 | 13.0048 | 12.8851 | 12.696 | 12.494 | 12.2272 | 12.0076 | 11.7994 | 11.3351 | 10.4475 | 9.7672 | 9.109 | 13.2639 | 13.1955 | 13.1058 | 13.0058 | 12.8865 | 12.698 | 12.4966 | 12.2306 | 12.0117 | 11.8041 | 11.3412 | 10.4563 | 9.7781 | 9.1219
|  | GROVE | FS |  |  | 14.1256 | 14.0934 | 14.059 | 14.0189 | 13.9752 | 13.91 | 13.8421 | 13.7479 | 13.6729 | 13.6038 | 13.4535 | 13.0504 | 12.7265 | 12.473 | 13.2918 | 13.2538 | 13.2134 | 13.1662 | 13.1146 | 13.0379 | 12.9578 | 12.8469 | 12.7586 | 12.6772 | 12.5 | 12.0252 | 11.6437 | 11.345 | 13.292 | 13.2541 | 13.2138 | 13.1667 | 13.1153 | 13.0388 | 12.959 | 12.8484 | 12.7604 | 12.6792 | 12.5026 | 12.0292 | 11.6489 | 11.3511
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL | MINIMUM HEADROOM | ST 98638 11417 | YES | 2.9994 | 2.9986 | 2.9965 | 2.9942 | 2.9919 | 2.9895 | 2.9871 | 2.9846 | 2.9821 | 2.9794 | 2.9743 | 2.9563 | 2.9378 | 2.9194 | 2.9993 | 2.9983 | 2.9959 | 2.9932 | 2.9904 | 2.9875 | 2.9847 | 2.9818 | 2.9788 | 2.9757 | 2.9695 | 2.9483 | 2.9264 | 2.9045 | 2.9993 | 2.9983 | 2.9959 | 2.9932 | 2.9904 | 2.9876 | 2.9847 | 2.9819 | 2.9788 | 2.9757 | 2.9696 | 2.9484 | 2.9266 | 2.9048
|  | GUSSAGE ST MICHAEL | CT |  |  | 2.9994 | 2.9986 | 2.9965 | 2.9942 | 2.9919 | 2.9895 | 2.9871 | 2.9846 | 2.9821 | 2.9794 | 2.9743 | 2.9563 | 2.9378 | 2.9194 | 2.9993 | 2.9983 | 2.9959 | 2.9932 | 2.9905 | 2.9877 | 2.9848 | 2.982 | 2.979 | 2.976 | 2.97 | 2.9485 | 2.9264 | 2.9045 | 2.9993 | 2.9983 | 2.9959 | 2.9932 | 2.9905 | 2.9877 | 2.9849 | 2.9821 | 2.9791 | 2.9761 | 2.9701 | 2.9487 | 2.9267 | 2.9048
|  | GUSSAGE ST MICHAEL | LW |  |  | 2.9994 | 2.9986 | 2.9965 | 2.9942 | 2.9919 | 2.9895 | 2.9871 | 2.9846 | 2.9821 | 2.9794 | 2.9743 | 2.9563 | 2.9378 | 2.9194 | 2.9993 | 2.9983 | 2.9959 | 2.9932 | 2.9904 | 2.9875 | 2.9847 | 2.9818 | 2.9788 | 2.9757 | 2.9695 | 2.9483 | 2.9264 | 2.9046 | 2.9993 | 2.9983 | 2.9959 | 2.9932 | 2.9904 | 2.9876 | 2.9847 | 2.9819 | 2.9788 | 2.9757 | 2.9696 | 2.9484 | 2.9266 | 2.9049
|  | GUSSAGE ST MICHAEL | ST |  |  | 2.9998 | 2.9994 | 2.9985 | 2.9972 | 2.9956 | 2.9934 | 2.9911 | 2.9889 | 2.9865 | 2.9841 | 2.9793 | 2.9678 | 2.9564 | 2.945 | 2.9997 | 2.9993 | 2.9983 | 2.9967 | 2.9948 | 2.9921 | 2.9895 | 2.9868 | 2.984 | 2.9811 | 2.9755 | 2.9619 | 2.9484 | 2.9349 | 2.9997 | 2.9993 | 2.9983 | 2.9967 | 2.9948 | 2.9922 | 2.9895 | 2.9869 | 2.984 | 2.9812 | 2.9756 | 2.962 | 2.9485 | 2.9351
|  | GUSSAGE ST MICHAEL | FS |  |  | 3 | 2.9999 | 2.9998 | 2.9995 | 2.999 | 2.9983 | 2.9975 | 2.9966 | 2.9956 | 2.9947 | 2.9929 | 2.9885 | 2.9843 | 2.9801 | 2.9999 | 2.9999 | 2.9998 | 2.9994 | 2.9988 | 2.9979 | 2.9971 | 2.9959 | 2.9948 | 2.9937 | 2.9916 | 2.9864 | 2.9814 | 2.9765 | 2.9999 | 2.9999 | 2.9998 | 2.9994 | 2.9988 | 2.9979 | 2.9971 | 2.996 | 2.9949 | 2.9938 | 2.9916 | 2.9864 | 2.9814 | 2.9766
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE | MINIMUM HEADROOM | SU 47370 08794 | NO | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 39.6539 | 39.6324 | 39.6276 | 39.6223 | 39.617 | 39.6118 | 39.6064 | 39.6005 | 39.5939 | 39.5869 | 39.5728 | 39.5451 | 39.5451 | 39.5451 | 39.2731 | 39.259 | 39.2339 | 39.2177 | 39.2016 | 39.1857 | 39.169 | 39.1511 | 39.1307 | 39.1093 | 39.0661 | 38.9359 | 38.8037 | 38.6727
|  | HAMBLE | CT |  |  | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 39.6539 | 39.6324 | 39.6276 | 39.6223 | 39.617 | 39.6118 | 39.6064 | 39.6005 | 39.5942 | 39.5878 | 39.5744 | 39.5451 | 39.5451 | 39.5451 | 39.2731 | 39.259 | 39.2339 | 39.2177 | 39.2016 | 39.1857 | 39.169 | 39.1511 | 39.1318 | 39.1121 | 39.0709 | 38.9463 | 38.819 | 38.6928
|  | HAMBLE | LW |  |  | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 39.6547 | 39.6325 | 39.6278 | 39.6227 | 39.6176 | 39.6126 | 39.6069 | 39.6007 | 39.5939 | 39.5869 | 39.5728 | 39.5451 | 39.5451 | 39.5451 | 39.2734 | 39.2597 | 39.2347 | 39.219 | 39.2034 | 39.1881 | 39.1707 | 39.1516 | 39.1307 | 39.1093 | 39.0661 | 38.9359 | 38.8037 | 38.6727
|  | HAMBLE | ST |  |  | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 39.9068 | 39.6429 | 39.6314 | 39.6275 | 39.6228 | 39.6185 | 39.614 | 39.6092 | 39.6041 | 39.5989 | 39.5881 | 39.5607 | 39.5451 | 39.5451 | 39.3594 | 39.2693 | 39.2519 | 39.2338 | 39.2195 | 39.2061 | 39.1922 | 39.1777 | 39.1619 | 39.146 | 39.113 | 39.0289 | 38.9467 | 38.8658
|  | HAMBLE | FS |  |  | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 38.1718 | 39.9196 | 39.6766 | 39.6734 | 39.6565 | 39.6365 | 39.6322 | 39.6308 | 39.6288 | 39.6268 | 39.6248 | 39.6208 | 39.6105 | 39.6002 | 39.5902 | 39.3637 | 39.2808 | 39.2797 | 39.274 | 39.2672 | 39.2575 | 39.2478 | 39.2378 | 39.2317 | 39.2256 | 39.2132 | 39.1816 | 39.1502 | 39.1194
MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY | MINIMUM HEADROOM | SZ 00104 90800 | NO | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 22.7816 | 26.5698 | 26.4357 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 22.7422 | 21.4979 | 20.3605 | 19.2269 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 22.8519 | 22.7356 | 22.6088 | 22.4764 | 22.3179 | 22.1758 | 21.7519 | 21.3643 | 20.9781
|  | HAMWORTHY | CT |  |  | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 22.7816 | 26.5751 | 26.459 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 22.859 | 21.6674 | 20.7095 | 19.7813 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 22.8964 | 22.7896 | 22.6725 | 22.5405 | 22.3827 | 22.2156 | 21.8096 | 21.4832 | 21.167
|  | HAMWORTHY | LW |  |  | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 22.7816 | 26.5698 | 26.4357 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 22.7422 | 21.4979 | 20.3605 | 19.2269 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 22.8519 | 22.7356 | 22.6088 | 22.4764 | 22.3179 | 22.1758 | 21.7519 | 21.3643 | 20.9781
|  | HAMWORTHY | ST |  |  | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 26.6117 | 26.528 | 26.462 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 22.2106 | 21.3696 | 20.5624 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 22.8958 | 22.7896 | 22.6689 | 22.5285 | 22.3516 | 21.9947 | 21.7081 | 21.4331
|  | HAMWORTHY | FS |  |  | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 31.4439 | 26.6558 | 26.6001 | 26.5724 | 26.5121 | 26.4428 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 26.3955 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 31.0419 | 22.8206 | 22.7216 | 22.6266
IVER 132KV | DENHAM | HAREFIELD | MINIMUM HEADROOM | TQ 04001 91227 | NO | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.474 | -9.4981 | -9.2527 | -9.2533 | -9.2545 | -9.256 | -9.258 | -9.2602 | -9.2627 | -9.2652 | -9.2679 | -9.2706 | -9.2762 | -9.3004 | -9.3246 | -9.3488
|  | HAREFIELD | CT |  |  | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4963 | -9.2527 | -9.2532 | -9.2545 | -9.256 | -9.2579 | -9.2599 | -9.2617 | -9.2636 | -9.2659 | -9.2684 | -9.2736 | -9.298 | -9.3225 | -9.347
|  | HAREFIELD | LW |  |  | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.474 | -9.4981 | -9.2527 | -9.2533 | -9.2545 | -9.256 | -9.258 | -9.2602 | -9.2627 | -9.2652 | -9.2679 | -9.2706 | -9.2762 | -9.3004 | -9.3246 | -9.3488
|  | HAREFIELD | ST |  |  | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.2525 | -9.2527 | -9.2533 | -9.2542 | -9.2555 | -9.2581 | -9.2606 | -9.2632 | -9.2662 | -9.2692 | -9.2755 | -9.291 | -9.3058 | -9.3204
|  | HAREFIELD | FS |  |  | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -3.9407 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.4737 | -9.2523 | -9.2524 | -9.2525 | -9.2527 | -9.253 | -9.2539 | -9.2548 | -9.2559 | -9.257 | -9.2582 | -9.2605 | -9.2664 | -9.2722 | -9.278
NURSLING GSP | WINCHESTER | HARESTOCK | MINIMUM HEADROOM | SU 45908 31300 | NO | 24.2285 | 24.0764 | 23.764 | 23.4199 | 23.0686 | 22.7094 | 22.3423 | 21.9677 | 21.5631 | 21.1497 | 20.2963 | 19.1061 | 18.0329 | 16.9177 | 24.1235 | 23.8916 | 23.4093 | 22.8789 | 22.3375 | 21.7842 | 21.2193 | 20.638 | 20.0034 | 19.362 | 18.0517 | 16.2332 | 14.5372 | 12.8357 | 27.5966 | 27.5933 | 27.5883 | 27.5825 | 27.5761 | 27.5693 | 24.125 | 23.512 | 22.8421 | 22.1646 | 20.7795 | 18.8401 | 17.0141 | 15.172
|  | HARESTOCK | CT |  |  | 24.2285 | 24.0764 | 23.764 | 23.4199 | 23.0686 | 22.7094 | 22.3423 | 21.9677 | 21.5631 | 21.1497 | 20.2963 | 19.1061 | 18.0329 | 16.9177 | 24.1235 | 23.8934 | 23.4093 | 22.8797 | 22.3394 | 21.7843 | 21.2193 | 20.638 | 20.0034 | 19.362 | 18.0517 | 16.2332 | 14.5372 | 12.8357 | 27.5966 | 27.5933 | 27.5883 | 27.5825 | 27.5761 | 27.5693 | 24.125 | 23.512 | 22.8421 | 22.1646 | 20.7795 | 18.8401 | 17.0141 | 15.172
|  | HARESTOCK | LW |  |  | 24.2285 | 24.0764 | 23.764 | 23.4199 | 23.0686 | 22.7094 | 22.3423 | 21.9677 | 21.5631 | 21.1497 | 20.2963 | 19.1061 | 18.0329 | 16.9177 | 24.1259 | 23.8916 | 23.4096 | 22.8789 | 22.3375 | 21.7842 | 21.2193 | 20.6431 | 20.0219 | 19.3878 | 18.0808 | 16.2851 | 14.7016 | 13.0878 | 27.5997 | 27.5986 | 27.5973 | 27.5955 | 27.5933 | 27.5906 | 24.1322 | 23.5257 | 22.8716 | 22.2036 | 20.826 | 18.924 | 17.2339 | 15.5001
|  | HARESTOCK | ST |  |  | 24.2794 | 24.1984 | 24.0462 | 23.8264 | 23.5618 | 23.427 | 23.2871 | 23.1394 | 22.9753 | 22.8059 | 22.4482 | 21.756 | 21.1627 | 20.5724 | 24.2039 | 24.0789 | 23.8439 | 23.5045 | 23.0958 | 22.8881 | 22.6726 | 22.4451 | 22.1924 | 21.9316 | 21.3809 | 20.3212 | 19.4214 | 18.5344 | 27.6006 | 27.6003 | 27.5998 | 27.5992 | 27.5986 | 27.5977 | 27.5967 | 27.5955 | 27.5942 | 27.5928 | 27.5898 | 23.1857 | 22.2342 | 21.2934
|  | HARESTOCK | FS |  |  | 27.9664 | 24.2973 | 24.2729 | 24.2075 | 24.1316 | 24.0786 | 24.0242 | 23.9591 | 23.8916 | 23.8232 | 23.6807 | 23.3788 | 23.123 | 22.8851 | 24.2657 | 24.2316 | 24.1941 | 24.0933 | 23.9762 | 23.8947 | 23.8108 | 23.7106 | 23.6066 | 23.5013 | 23.282 | 22.8187 | 22.4283 | 22.0663 | 27.6008 | 27.6005 | 27.6003 | 27.5999 | 27.5995 | 27.599 | 27.5986 | 27.5981 | 27.5976 | 27.597 | 27.5959 | 27.5915 | 27.5851 | 27.5779
EALING GSP | EALING (D) | HARVARD LANE | MINIMUM HEADROOM | TQ 20021 78030 | YES | 41.7478 | 41.7478 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 37.5183 | 37.3763 | 47.447 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 32.1864 | 29.6783 | 39.7979 | 39.7979 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 30.5679
|  | HARVARD LANE | CT |  |  | 41.7478 | 41.7478 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 37.5183 | 37.3763 | 47.447 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 32.1864 | 29.6783 | 39.7979 | 39.7979 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 30.5679
|  | HARVARD LANE | LW |  |  | 41.7478 | 41.7478 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 37.5267 | 37.3889 | 47.4544 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 30.4117 | 39.7979 | 39.7979 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 31.3141
|  | HARVARD LANE | ST |  |  | 41.7478 | 41.7478 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 38.0631 | 37.5651 | 47.6877 | 47.5565 | 47.4754 | 47.4502 | 47.4248 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 47.4057 | 39.7979 | 39.7979 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329
|  | HARVARD LANE | FS |  |  | 41.7478 | 41.7478 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 52.6153 | 38.1174 | 37.6485 | 47.8606 | 47.7715 | 47.6959 | 47.6557 | 47.6151 | 47.5675 | 47.5199 | 47.493 | 47.4703 | 47.4221 | 47.4057 | 47.4057 | 39.7979 | 39.7979 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329 | 50.0329
BRAMLEY (FLEE) | FERNHURST | HASLEMERE | MINIMUM HEADROOM | SU 89300 31710 | YES | 4.6776 | 4.5818 | 13.7873 | 13.5649 | 13.3407 | 13.1169 | 12.8934 | 12.6717 | 12.4282 | 12.1841 | 11.6999 | 10.595 | 9.3904 | 8.1533 | 22.6084 | 22.5598 | 22.4489 | 22.3354 | 22.221 | 22.1774 | 22.147 | 22.1166 | 22.0823 | 22.0475 | 18.6134 | 17.1452 | 15.5508 | 13.9381 | 18.9059 | 18.7833 | 18.5013 | 18.2132 | 17.9232 | 17.6342 | 17.3451 | 17.0584 | 16.7458 | 16.4332 | 15.8129 | 14.3806 | 12.8165 | 11.2274
|  | HASLEMERE | CT |  |  | 4.6776 | 4.5818 | 13.7873 | 13.5649 | 13.3407 | 13.1169 | 12.8934 | 12.6717 | 12.4282 | 12.1841 | 11.6999 | 10.595 | 9.3904 | 8.1533 | 22.6084 | 22.5598 | 22.4489 | 22.3354 | 22.221 | 22.1774 | 22.147 | 22.1166 | 22.0823 | 22.0475 | 18.6134 | 17.1452 | 15.5508 | 13.9381 | 18.9059 | 18.7833 | 18.5013 | 18.2132 | 17.9232 | 17.6342 | 17.3451 | 17.0584 | 16.7458 | 16.4332 | 15.8129 | 14.3806 | 12.8165 | 11.2274
|  | HASLEMERE | LW |  |  | 4.6776 | 4.5818 | 13.7873 | 13.5649 | 13.3407 | 13.1169 | 12.8934 | 12.6717 | 12.4282 | 12.1841 | 11.6999 | 10.595 | 9.3904 | 8.1533 | 22.6114 | 22.5653 | 22.46 | 22.3531 | 22.2453 | 22.1931 | 22.166 | 22.1388 | 22.1084 | 22.0776 | 18.7454 | 17.3507 | 15.8457 | 14.3192 | 18.9109 | 18.7928 | 18.5218 | 18.2472 | 17.9707 | 17.6947 | 17.4193 | 17.1463 | 16.8466 | 16.5466 | 15.952 | 14.6006 | 13.1355 | 11.641
|  | HASLEMERE | ST |  |  | 4.7227 | 4.6907 | 14.0497 | 13.9636 | 13.8576 | 13.7362 | 13.615 | 13.4954 | 13.3654 | 13.2365 | 12.984 | 12.3229 | 11.633 | 10.9371 | 22.6332 | 22.6178 | 22.5861 | 22.5448 | 22.4939 | 22.4356 | 22.3773 | 22.3198 | 22.2574 | 22.2079 | 22.1775 | 22.0959 | 18.6597 | 17.7793 | 18.9664 | 18.927 | 18.8455 | 18.7392 | 18.6083 | 18.4585 | 18.3088 | 18.1613 | 18.001 | 17.8419 | 17.5306 | 16.7168 | 15.8695 | 15.0173
|  | HASLEMERE | FS |  |  | 4.738 | 4.7293 | 14.1431 | 14.1081 | 14.0663 | 14.0247 | 13.9834 | 13.931 | 13.8786 | 13.8265 | 13.725 | 13.4685 | 13.2039 | 12.9414 | 22.6406 | 22.6363 | 22.6309 | 22.6141 | 22.594 | 22.574 | 22.5541 | 22.5289 | 22.5037 | 22.4787 | 22.4298 | 22.306 | 22.2008 | 22.1675 | 18.9853 | 18.9746 | 18.9608 | 18.9177 | 18.8661 | 18.8148 | 18.7639 | 18.6992 | 18.6345 | 18.5703 | 18.4451 | 18.1292 | 17.8038 | 17.4812
BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE | MINIMUM HEADROOM | SU 98188 20276 | YES | 15.5801 | 15.5801 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 15.9587 | 27.8124 | 27.7973 | 27.7807 | 27.764 | 27.7475 | 27.731 | 27.7144 | 27.6873 | 27.6602 | 27.6074 | 27.3863 | 27.1051 | 26.9476 | 16.4587 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187
|  | HASLINGBOURNE | CT |  |  | 15.5801 | 15.5801 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 15.9588 | 27.8125 | 27.7974 | 27.7808 | 27.7642 | 27.7477 | 27.7313 | 27.7147 | 27.6968 | 27.6789 | 27.6434 | 27.3907 | 27.1123 | 26.9511 | 16.4587 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187
|  | HASLINGBOURNE | LW |  |  | 15.5801 | 15.5801 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 15.9587 | 27.8124 | 27.7973 | 27.7807 | 27.764 | 27.7475 | 27.731 | 27.7144 | 27.6965 | 27.6786 | 27.6431 | 27.3863 | 27.1051 | 26.9476 | 16.4587 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187
|  | HASLINGBOURNE | ST |  |  | 15.5801 | 15.5801 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 15.9612 | 27.8184 | 27.8122 | 27.8028 | 27.7915 | 27.7656 | 27.74 | 27.7147 | 27.6873 | 27.6602 | 27.6074 | 27.4579 | 27.2972 | 27.1374 | 16.4587 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187
|  | HASLINGBOURNE | FS |  |  | 15.5801 | 15.5801 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 22.6301 | 15.9626 | 27.8222 | 27.8218 | 27.8192 | 27.8161 | 27.8069 | 27.7978 | 27.786 | 27.7744 | 27.7629 | 27.7406 | 27.6819 | 27.6179 | 27.5528 | 16.4587 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187 | 28.3187
MELKSHAM GSP | FROME BSP | HAWKERIDGE | MINIMUM HEADROOM | ST 86422 53026 | YES | 22.145 | 22.1434 | 36.3895 | 36.3853 | 36.3811 | 36.377 | 36.3729 | 36.3688 | 36.3644 | 36.36 | 36.3514 | 36.3387 | 36.335 | 36.335 | 19.9692 | 19.9594 | 19.9359 | 19.9105 | 19.8864 | 19.8782 | 19.8701 | 19.8621 | 19.8534 | 19.8448 | 19.8277 | 19.8027 | 19.777 | 19.7515 | 20.5643 | 20.5625 | 20.5582 | 20.5535 | 20.5489 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466
|  | HAWKERIDGE | CT |  |  | 22.145 | 22.1434 | 36.3895 | 36.3853 | 36.3811 | 36.377 | 36.3729 | 36.3688 | 36.3644 | 36.36 | 36.3514 | 36.3387 | 36.335 | 36.335 | 19.9705 | 19.9625 | 19.9434 | 19.9228 | 19.9023 | 19.8853 | 19.8787 | 19.8722 | 19.8651 | 19.8581 | 19.8443 | 19.8191 | 19.7931 | 19.7676 | 20.5645 | 20.5631 | 20.5596 | 20.5558 | 20.552 | 20.5483 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466
|  | HAWKERIDGE | LW |  |  | 22.145 | 22.1434 | 36.3895 | 36.3853 | 36.3811 | 36.377 | 36.3729 | 36.3688 | 36.3644 | 36.36 | 36.3514 | 36.3387 | 36.335 | 36.335 | 19.9692 | 19.9594 | 19.9359 | 19.9105 | 19.8864 | 19.8782 | 19.8701 | 19.8621 | 19.8534 | 19.8448 | 19.8277 | 19.8027 | 19.777 | 19.7515 | 20.5643 | 20.5625 | 20.5582 | 20.5535 | 20.5489 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466
|  | HAWKERIDGE | ST |  |  | 22.1533 | 22.1445 | 36.3923 | 36.389 | 36.385 | 36.3833 | 36.3817 | 36.3801 | 36.3783 | 36.3766 | 36.3732 | 36.3648 | 36.3564 | 36.3481 | 20.0193 | 19.966 | 19.9528 | 19.9328 | 19.9087 | 19.8987 | 19.8888 | 19.8843 | 19.8808 | 19.8774 | 19.8707 | 19.8542 | 19.8377 | 19.8213 | 20.5735 | 20.5637 | 20.5613 | 20.5576 | 20.5532 | 20.5514 | 20.5496 | 20.5478 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466 | 20.5466
|  | HAWKERIDGE | FS |  |  | 22.1538 | 22.1459 | 36.3958 | 36.3951 | 36.3943 | 36.3937 | 36.3932 | 36.3925 | 36.3919 | 36.3912 | 36.3899 | 36.3868 | 36.3838 | 36.381 | 20.0226 | 19.9748 | 19.9741 | 19.9699 | 19.9649 | 19.9617 | 19.9585 | 19.9544 | 19.9503 | 19.9463 | 19.9385 | 19.9196 | 19.9016 | 19.8861 | 20.5741 | 20.5653 | 20.5652 | 20.5644 | 20.5635 | 20.5629 | 20.5623 | 20.5616 | 20.5609 | 20.5601 | 20.5587 | 20.5552 | 20.5519 | 20.5488
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY | MINIMUM HEADROOM | SU 85973 57691 | YES | 21.7855 | 21.7855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 32.1353 | 32.1283 | 32.12 | 32.1106 | 32.1007 | 32.0886 | 32.07 | 32.052 | 32.0325 | 32.0135 | 31.9775 | 31.8873 | 31.7597 | 31.6021 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541
|  | HAWLEY | CT |  |  | 21.7855 | 21.7855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 32.1353 | 32.1283 | 32.12 | 32.1106 | 32.1007 | 32.0906 | 32.0799 | 32.0698 | 32.059 | 32.0485 | 32.0293 | 31.9069 | 31.7597 | 31.6098 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541
|  | HAWLEY | LW |  |  | 21.7855 | 21.7855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 32.136 | 32.1299 | 32.125 | 32.1191 | 32.1131 | 32.1071 | 32.1006 | 32.094 | 32.0871 | 32.0805 | 32.0684 | 31.9218 | 31.7621 | 31.6021 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541
|  | HAWLEY | ST |  |  | 21.7855 | 21.7855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 32.1375 | 32.1325 | 32.1267 | 32.1179 | 32.1071 | 32.0886 | 32.07 | 32.052 | 32.0325 | 32.0135 | 31.9775 | 31.8873 | 31.7835 | 31.6787 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541
|  | HAWLEY | FS |  |  | 21.7855 | 21.7855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 27.2855 | 32.1405 | 32.1388 | 32.1383 | 32.1371 | 32.1357 | 32.1301 | 32.1244 | 32.1172 | 32.1101 | 32.1032 | 32.0902 | 32.0586 | 32.0215 | 31.9836 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541 | 32.5541
COWLEY GSP | HEADINGTON BSP | HEADINGTON | MINIMUM HEADROOM | SP 54440 08085 | YES | 64.0976 | 63.9979 | 149.2379 | 148.8908 | 148.5332 | 148.1908 | 147.8454 | 147.4866 | 147.0952 | 146.7004 | 146.2227 | 145.4521 | 144.7 | 143.9565 | 1.7263 | 1.5912 | 1.2419 | 0.79263 | 0.33575 | -0.10161 | -0.53663 | -1.0089 | -1.5437 | -2.0941 | -2.8475 | -4.0099 | -5.068 | -6.0948 | 5.4927 | 5.3578 | 5.0092 | 4.5608 | 4.1048 | 3.6682 | 3.234 | 2.7627 | 2.2288 | 1.6796 | 0.92752 | -0.23266 | -1.2888 | -2.3136
|  | HEADINGTON | CT |  |  | 64.0976 | 63.9979 | 149.2379 | 148.8908 | 148.5332 | 148.1908 | 147.8454 | 147.4866 | 147.0952 | 146.7004 | 146.2227 | 145.4521 | 144.7 | 143.9565 | 1.7263 | 1.5912 | 1.2419 | 0.79263 | 0.33575 | -0.10161 | -0.53663 | -1.0089 | -1.5437 | -2.0941 | -2.8475 | -4.0099 | -5.068 | -6.0948 | 5.4927 | 5.3578 | 5.0092 | 4.5608 | 4.1048 | 3.6682 | 3.234 | 2.7627 | 2.2288 | 1.6796 | 0.92752 | -0.23266 | -1.2888 | -2.3136
|  | HEADINGTON | LW |  |  | 64.0976 | 63.9979 | 149.2379 | 148.8908 | 148.5332 | 148.1908 | 147.8454 | 147.4866 | 147.0952 | 146.7004 | 146.2227 | 145.4521 | 144.7 | 143.9565 | 1.7337 | 1.6077 | 1.2788 | 0.83989 | 0.38767 | -0.045425 | -0.48225 | -0.93596 | -1.431 | -1.9303 | -2.5345 | -3.509 | -4.4601 | -5.4005 | 5.5001 | 5.3743 | 5.046 | 4.6079 | 4.1566 | 3.7243 | 3.2883 | 2.8355 | 2.3414 | 1.843 | 1.24 | 0.26728 | -0.68202 | -1.6206
|  | HEADINGTON | ST |  |  | 64.1468 | 64.1182 | 149.5406 | 149.4019 | 149.245 | 149.0849 | 148.9256 | 148.7462 | 148.5356 | 148.3128 | 148.0583 | 147.5526 | 147.1263 | 146.7102 | 1.796 | 1.7598 | 1.6617 | 1.4862 | 1.2878 | 1.0853 | 0.88388 | 0.65702 | 0.3906 | 0.1089 | -0.21301 | -0.85259 | -1.3916 | -1.9179 | 5.5622 | 5.5261 | 5.4282 | 5.2531 | 5.055 | 4.8529 | 4.6519 | 4.4254 | 4.1595 | 3.8783 | 3.557 | 2.9187 | 2.3807 | 1.8554
|  | HEADINGTON | FS |  |  | 64.1887 | 64.149 | 149.623 | 149.5537 | 149.4783 | 149.4124 | 149.3452 | 149.2658 | 149.1813 | 149.0944 | 148.9873 | 148.7641 | 148.5931 | 148.436 | 1.8489 | 1.7987 | 1.7659 | 1.6782 | 1.5829 | 1.4995 | 1.4145 | 1.3141 | 1.2073 | 1.0973 | 0.96194 | 0.67968 | 0.46336 | 0.26469 | 5.6151 | 5.565 | 5.5322 | 5.4446 | 5.3496 | 5.2663 | 5.1815 | 5.0813 | 4.9746 | 4.8649 | 4.7298 | 4.448 | 4.2321 | 4.0338
NURSLING GSP | VELMORE BSP | HEDGE END | MINIMUM HEADROOM | SU 49035 15685 | NO | 92.0272 | 177.5093 | 177.4799 | 177.4465 | 177.4121 | 177.3802 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 20.1735 | 20.0165 | 19.7583 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 14.0735 | 13.3409 | 22.42 | 22.3674 | 22.2808 | 22.1827 | 22.0815 | 21.9878 | 21.8962 | 21.83 | 21.764 | 21.6997 | 21.5739 | 21.3982 | 13.9304 | 13.2101
|  | HEDGE END | CT |  |  | 92.0272 | 177.5093 | 177.4799 | 177.4465 | 177.4121 | 177.3802 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 20.1821 | 20.0486 | 19.8256 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 13.5955 | 22.4229 | 22.3782 | 22.3034 | 22.2198 | 22.1327 | 22.0498 | 21.9668 | 21.9006 | 21.8315 | 21.763 | 21.6415 | 21.4598 | 14.182 | 13.4605
|  | HEDGE END | LW |  |  | 92.0272 | 177.5093 | 177.4799 | 177.4465 | 177.4121 | 177.3802 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 177.3693 | 20.1735 | 20.0165 | 19.7583 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 14.0735 | 13.3409 | 22.42 | 22.3674 | 22.2808 | 22.1827 | 22.0815 | 21.9878 | 21.8962 | 21.83 | 21.764 | 21.6997 | 21.5739 | 21.3982 | 13.9304 | 13.2101
|  | HEDGE END | ST |  |  | 92.0319 | 177.5217 | 177.5061 | 177.4852 | 177.4609 | 177.4463 | 177.4316 | 177.4207 | 177.4093 | 177.3979 | 177.3786 | 177.3693 | 177.3693 | 177.3693 | 20.2147 | 20.1253 | 19.9884 | 19.8048 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 19.6298 | 22.4339 | 22.4039 | 22.358 | 22.2964 | 22.225 | 22.1819 | 22.1387 | 22.1067 | 22.0732 | 22.0397 | 21.9829 | 21.8683 | 21.7626 | 21.6585
|  | HEDGE END | FS |  |  | 92.036 | 177.5315 | 177.5266 | 177.5191 | 177.5109 | 177.5047 | 177.4988 | 177.4942 | 177.4899 | 177.4857 | 177.4777 | 177.4613 | 177.4469 | 177.4329 | 20.2501 | 20.211 | 20.1684 | 20.1021 | 20.0306 | 19.9757 | 19.9242 | 19.8842 | 19.8463 | 19.8094 | 19.7389 | 19.6298 | 19.6298 | 19.6298 | 22.4457 | 22.4326 | 22.4183 | 22.3961 | 22.3721 | 22.3537 | 22.3364 | 22.323 | 22.3103 | 22.298 | 22.2743 | 22.2261 | 22.184 | 22.1427
BRAMLEY (FLEE) | READING BSP | HENLEY | MINIMUM HEADROOM | SU 76070 82422 | YES | 23.3929 | 23.2904 | 23.0278 | 22.6943 | 22.3216 | 21.9322 | 21.5271 | 21.1061 | 20.6527 | 20.1893 | 19.2157 | 18.1588 | 16.8773 | 15.5594 | 20.6562 | 20.5198 | 20.1758 | 19.7535 | 19.2944 | 18.8223 | 18.3482 | 17.8477 | 17.2904 | 16.7039 | 15.4731 | 13.9634 | 12.3867 | 10.8069 | 21.0896 | 20.956 | 20.6187 | 20.2047 | 19.7547 | 19.2918 | 18.827 | 18.3363 | 17.79 | 17.2022 | 15.9671 | 14.4519 | 12.8695 | 11.284
|  | HENLEY | CT |  |  | 23.3929 | 23.2904 | 23.0278 | 22.6943 | 22.3216 | 21.9322 | 21.5271 | 21.1061 | 20.6527 | 20.1893 | 19.2157 | 18.1588 | 16.8773 | 15.5594 | 20.6562 | 20.5198 | 20.1758 | 19.7535 | 19.2944 | 18.8223 | 18.3482 | 17.8477 | 17.2904 | 16.7039 | 15.4731 | 13.9634 | 12.3867 | 10.8069 | 21.0896 | 20.956 | 20.6187 | 20.2047 | 19.7547 | 19.2918 | 18.827 | 18.3363 | 17.79 | 17.2022 | 15.9671 | 14.4519 | 12.8695 | 11.284
|  | HENLEY | LW |  |  | 23.3929 | 23.2904 | 23.0278 | 22.6943 | 22.3216 | 21.9322 | 21.5271 | 21.1061 | 20.6527 | 20.1893 | 19.2157 | 18.1588 | 16.8773 | 15.5594 | 20.6682 | 20.5499 | 20.2469 | 19.8619 | 19.4318 | 18.9823 | 18.5148 | 18.0288 | 17.5055 | 16.9708 | 15.847 | 14.6271 | 13.148 | 11.6269 | 21.1015 | 20.9855 | 20.6884 | 20.311 | 19.8894 | 19.4487 | 18.9903 | 18.5139 | 18.0009 | 17.4701 | 16.3423 | 15.118 | 13.6336 | 12.107
|  | HENLEY | ST |  |  | 23.5515 | 23.4087 | 23.3265 | 23.179 | 22.9864 | 22.7908 | 22.5937 | 22.381 | 22.1378 | 21.8736 | 21.2992 | 20.5404 | 19.7797 | 19.0208 | 20.8513 | 20.6865 | 20.5917 | 20.4214 | 20.199 | 19.9733 | 19.7459 | 19.5003 | 19.2197 | 18.9148 | 18.2517 | 17.376 | 16.498 | 15.6221 | 21.281 | 21.1194 | 21.0264 | 20.8595 | 20.6415 | 20.4202 | 20.1972 | 19.9565 | 19.6814 | 19.3825 | 18.7324 | 17.8739 | 16.9957 | 16.1166
|  | HENLEY | FS |  |  | 23.5678 | 23.452 | 23.439 | 23.3818 | 23.3083 | 23.2327 | 23.1539 | 23.059 | 22.9595 | 22.8555 | 22.6339 | 22.3109 | 22.0367 | 21.7345 | 20.8701 | 20.7364 | 20.7215 | 20.6554 | 20.5706 | 20.4834 | 20.3924 | 20.2829 | 20.1681 | 20.0481 | 19.7923 | 19.4195 | 19.103 | 18.7542 | 21.2994 | 21.1684 | 21.1537 | 21.0889 | 21.0058 | 20.9203 | 20.8311 | 20.7237 | 20.6112 | 20.4935 | 20.2428 | 19.8773 | 19.567 | 19.225
AXMINSTER | YEOVIL BSP | HENSTRIDGE | MINIMUM HEADROOM | ST 72676 19263 | YES | 22.5473 | 22.5259 | 22.4869 | 22.4486 | 22.4219 | 22.4007 | 22.3429 | 22.2832 | 22.2187 | 22.1512 | 22.0286 | 21.7579 | 21.4639 | 21.1698 | 26.7993 | 21.3453 | 21.2968 | 21.2492 | 21.2159 | 21.1896 | 21.1177 | 21.0434 | 20.9632 | 20.8792 | 20.7267 | 20.3899 | 20.0242 | 19.6583 | 21.337 | 21.3103 | 21.2616 | 21.2137 | 21.1803 | 21.1539 | 21.0816 | 21.007 | 20.9264 | 20.842 | 20.6888 | 20.3506 | 19.9832 | 19.6156
|  | HENSTRIDGE | CT |  |  | 22.5473 | 22.5259 | 22.4869 | 22.4486 | 22.4219 | 22.4007 | 22.3429 | 22.2832 | 22.2187 | 22.1512 | 22.0516 | 21.7579 | 21.4639 | 21.1698 | 26.7993 | 21.3492 | 21.3048 | 21.262 | 21.2316 | 21.2052 | 21.137 | 21.0638 | 20.9866 | 20.9078 | 20.7811 | 20.4054 | 20.0541 | 19.7084 | 21.3378 | 21.3142 | 21.2696 | 21.2266 | 21.1961 | 21.1695 | 21.101 | 21.0275 | 20.95 | 20.8708 | 20.7435 | 20.3661 | 20.0132 | 19.666
|  | HENSTRIDGE | LW |  |  | 22.5473 | 22.5259 | 22.4869 | 22.4486 | 22.4219 | 22.4007 | 22.3429 | 22.2832 | 22.2187 | 22.1512 | 22.0516 | 21.7579 | 21.4639 | 21.1698 | 26.7993 | 21.3453 | 21.2968 | 21.2492 | 21.2159 | 21.1896 | 21.1177 | 21.0434 | 20.9632 | 20.8792 | 20.7552 | 20.3899 | 20.0242 | 19.6583 | 21.337 | 21.3103 | 21.2616 | 21.2137 | 21.1803 | 21.1539 | 21.0816 | 21.007 | 20.9264 | 20.842 | 20.7175 | 20.3506 | 19.9832 | 19.6156
|  | HENSTRIDGE | ST |  |  | 27.7195 | 22.5414 | 22.5208 | 22.4992 | 22.4825 | 22.439 | 22.3735 | 22.3059 | 22.233 | 22.1589 | 22.0286 | 21.782 | 21.5584 | 21.339 | 26.7993 | 26.7993 | 21.339 | 21.3121 | 21.2913 | 21.2372 | 21.1558 | 21.0717 | 20.9809 | 20.8887 | 20.7267 | 20.4199 | 20.1418 | 19.8687 | 26.9719 | 21.3296 | 21.3039 | 21.2769 | 21.2561 | 21.2016 | 21.1199 | 21.0354 | 20.9442 | 20.8516 | 20.6888 | 20.3807 | 20.1013 | 19.8271
|  | HENSTRIDGE | FS |  |  | 27.7195 | 22.5517 | 22.5425 | 22.5328 | 22.5263 | 22.5134 | 22.4922 | 22.4684 | 22.4437 | 22.4178 | 22.373 | 22.2916 | 22.2199 | 22.1512 | 26.7993 | 26.7993 | 26.7993 | 21.3539 | 21.3458 | 21.3298 | 21.3034 | 21.2737 | 21.2431 | 21.2108 | 21.1551 | 21.0538 | 20.9646 | 20.8792 | 26.9728 | 21.3425 | 21.331 | 21.3189 | 21.3108 | 21.2947 | 21.2682 | 21.2384 | 21.2076 | 21.1752 | 21.1192 | 21.0174 | 20.9279 | 20.8421
BRAMLEY (FLEE) | ALTON | HERRIARD | MINIMUM HEADROOM | SU 66770 44972 | YES | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 13.3087 | 13.3045 | 13.2945 | 13.2836 | 13.2729 | 13.2623 | 13.2519 | 13.2426 | 13.2357 | 13.2288 | 13.2153 | 13.2011 | 13.1864 | 13.1719 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073
|  | HERRIARD | CT |  |  | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 13.3091 | 13.3056 | 13.2972 | 13.2881 | 13.2791 | 13.2702 | 13.2614 | 13.2527 | 13.2437 | 13.2379 | 13.2266 | 13.2115 | 13.1959 | 13.1805 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073
|  | HERRIARD | LW |  |  | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 13.3087 | 13.3045 | 13.2945 | 13.2836 | 13.2729 | 13.2623 | 13.2519 | 13.2426 | 13.2357 | 13.2288 | 13.2153 | 13.2011 | 13.1864 | 13.1719 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073
|  | HERRIARD | ST |  |  | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 13.3104 | 13.3086 | 13.3048 | 13.299 | 13.292 | 13.2891 | 13.2863 | 13.2835 | 13.2805 | 13.2775 | 13.2718 | 13.2575 | 13.2437 | 13.2349 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073
|  | HERRIARD | FS |  |  | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 16.9823 | 13.3113 | 13.311 | 13.3107 | 13.3089 | 13.3068 | 13.3058 | 13.3049 | 13.3036 | 13.3024 | 13.3012 | 13.2988 | 13.2932 | 13.2878 | 13.2827 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073 | 14.1073
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE | MINIMUM HEADROOM | SU 84733 92200 | NO | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 79.1256 | 79.1202 | 79.1076 | 79.0939 | 79.0804 | 79.0671 | 79.0538 | 79.0407 | 79.0264 | 79.0121 | 78.9837 | 78.9146 | 78.8423 | 78.7708
|  | HIGH WYCOMBE | CT |  |  | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 79.1257 | 79.1205 | 79.1082 | 79.0949 | 79.0817 | 79.0686 | 79.0557 | 79.0429 | 79.0292 | 79.0155 | 78.9883 | 78.9189 | 78.8463 | 78.7746
|  | HIGH WYCOMBE | LW |  |  | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 79.1256 | 79.1202 | 79.1076 | 79.0939 | 79.0804 | 79.0671 | 79.0538 | 79.0407 | 79.0264 | 79.0121 | 78.9837 | 78.9146 | 78.8423 | 78.7708
|  | HIGH WYCOMBE | ST |  |  | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 79.1274 | 79.1245 | 79.1181 | 79.1086 | 79.0972 | 79.088 | 79.079 | 79.0701 | 79.0606 | 79.0512 | 79.0326 | 78.9864 | 78.9397 | 78.8933
|  | HIGH WYCOMBE | FS |  |  | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 94.2073 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 76.7266 | 79.129 | 79.1286 | 79.1282 | 79.1259 | 79.1233 | 79.1203 | 79.1173 | 79.1135 | 79.1098 | 79.1061 | 79.0989 | 79.0814 | 79.0642 | 79.0479
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN | MINIMUM HEADROOM | SU 86304 92972 | NO | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 46.0515 | 45.2832 | 48.3354 | 48.3273 | 48.3123 | 48.2961 | 48.2798 | 48.2635 | 48.2472 | 48.2313 | 48.2142 | 48.1974 | 48.1635 | 45.4801 | 44.5191 | 43.5696 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 45.3907 | 44.4409
|  | HIGH WYCOMBE TOWN | CT |  |  | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 46.0515 | 45.2832 | 48.3354 | 48.3274 | 48.3123 | 48.2961 | 48.2798 | 48.2635 | 48.2472 | 48.2313 | 48.2142 | 48.1974 | 48.1635 | 45.4818 | 44.5528 | 43.6355 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 45.4244 | 44.5068
|  | HIGH WYCOMBE TOWN | LW |  |  | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 46.0515 | 45.2832 | 48.3354 | 48.3273 | 48.3127 | 48.297 | 48.2814 | 48.266 | 48.2507 | 48.2355 | 48.2186 | 48.2018 | 48.1681 | 45.4801 | 44.5191 | 43.5696 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 45.3907 | 44.4409
|  | HIGH WYCOMBE TOWN | ST |  |  | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 46.206 | 48.3394 | 48.3351 | 48.3284 | 48.3184 | 48.3062 | 48.2877 | 48.2695 | 48.2517 | 48.2325 | 48.2138 | 48.1767 | 45.8766 | 45.2937 | 44.7139 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 46.1655 | 45.5856
|  | HIGH WYCOMBE TOWN | FS |  |  | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 49.4689 | 48.3425 | 48.3413 | 48.3407 | 48.3381 | 48.335 | 48.3288 | 48.3227 | 48.3148 | 48.307 | 48.2994 | 48.2846 | 48.2483 | 48.2129 | 48.1792 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005 | 49.0005
LOVEDEAN GSP | WYMERING BSP | HILSEA | MINIMUM HEADROOM | SU 66394 03806 | NO | 41.2218 | 41.2162 | 41.2028 | 41.1883 | 41.1738 | 41.1594 | 41.1451 | 41.1308 | 41.1154 | 41.1 | 41.0674 | 40.9304 | 40.7731 | 40.6169 | 34.1112 | 34.1067 | 34.0958 | 34.0839 | 34.0721 | 34.0604 | 34.0487 | 34.0371 | 34.0245 | 34.012 | 33.9853 | 33.8737 | 33.7454 | 33.6181 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43
|  | HILSEA | CT |  |  | 41.2218 | 41.2162 | 41.2028 | 41.1883 | 41.1738 | 41.1594 | 41.1451 | 41.1308 | 41.1154 | 41.1 | 41.0695 | 40.9304 | 40.7731 | 40.6169 | 34.1112 | 34.1067 | 34.0958 | 34.084 | 34.0722 | 34.0605 | 34.0488 | 34.0372 | 34.0246 | 34.0121 | 33.9872 | 33.8803 | 33.7632 | 33.647 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43
|  | HILSEA | LW |  |  | 41.2218 | 41.2162 | 41.2028 | 41.1883 | 41.1738 | 41.1594 | 41.1451 | 41.1308 | 41.1154 | 41.1 | 41.0695 | 40.9304 | 40.7731 | 40.6169 | 34.1112 | 34.1067 | 34.0958 | 34.0839 | 34.0721 | 34.0604 | 34.0487 | 34.0371 | 34.0245 | 34.012 | 33.9871 | 33.8737 | 33.7454 | 33.6181 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43
|  | HILSEA | ST |  |  | 41.224 | 41.2215 | 41.216 | 41.2078 | 41.1978 | 41.1794 | 41.1612 | 41.1433 | 41.1239 | 41.1048 | 41.0674 | 40.9732 | 40.8736 | 40.7747 | 34.113 | 34.111 | 34.1065 | 34.0998 | 34.0917 | 34.0767 | 34.0619 | 34.0472 | 34.0314 | 34.0159 | 33.9853 | 33.9086 | 33.8274 | 33.7467 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43
|  | HILSEA | FS |  |  | 41.2253 | 41.2249 | 41.2245 | 41.2222 | 41.2195 | 41.2136 | 41.2077 | 41.2002 | 41.1928 | 41.1855 | 41.1712 | 41.1372 | 41.103 | 41.0681 | 34.1141 | 34.1138 | 34.1135 | 34.1116 | 34.1094 | 34.1046 | 34.0998 | 34.0937 | 34.0876 | 34.0816 | 34.07 | 34.0422 | 34.0144 | 33.9859 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43 | 34.43
MANNINGTON GSP | ARNEWOOD | HINCHELSEA | MINIMUM HEADROOM | SU 27805 00447 | YES | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 16.4798 | 16.477 | 16.4702 | 16.4628 | 16.4555 | 16.4483 | 16.4411 | 16.4339 | 16.4262 | 16.4164 | 16.3968 | 16.3251 | 16.2411 | 16.1574 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777
|  | HINCHELSEA | CT |  |  | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 16.4798 | 16.477 | 16.4702 | 16.4628 | 16.4555 | 16.4483 | 16.4411 | 16.4339 | 16.4262 | 16.4185 | 16.4033 | 16.3251 | 16.2411 | 16.1574 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777
|  | HINCHELSEA | LW |  |  | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 16.4799 | 16.4773 | 16.4709 | 16.4641 | 16.4572 | 16.4505 | 16.4437 | 16.437 | 16.4297 | 16.4226 | 16.4084 | 16.3345 | 16.2547 | 16.1745 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777
|  | HINCHELSEA | ST |  |  | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 16.4808 | 16.4794 | 16.4762 | 16.4713 | 16.4655 | 16.4558 | 16.4462 | 16.4367 | 16.4265 | 16.4164 | 16.3968 | 16.3474 | 16.2959 | 16.2443 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777
|  | HINCHELSEA | FS |  |  | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 18.5132 | 16.4816 | 16.4814 | 16.4813 | 16.4801 | 16.4788 | 16.4757 | 16.4727 | 16.4688 | 16.4649 | 16.4611 | 16.4537 | 16.436 | 16.4181 | 16.4002 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777 | 16.777
BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD | MINIMUM HEADROOM | SU 88631 36479 | YES | 38.3351 | 38.3333 | 38.3308 | 38.3277 | 38.3237 | 38.3189 | 38.3131 | 38.3062 | 38.2994 | 38.2915 | 38.2724 | 38.2042 | 38.1172 | 38.0094 | 32.0237 | 32.0091 | 31.9777 | 31.9436 | 31.9087 | 31.8903 | 31.8835 | 31.8763 | 31.869 | 31.8608 | 31.8418 | 31.7797 | 31.7082 | 31.625 | 33.517 | 33.5109 | 33.5019 | 33.492 | 33.4813 | 33.4697 | 33.4573 | 33.444 | 33.4304 | 33.4153 | 33.3801 | 33.2652 | 33.133 | 32.9791
|  | HINDHEAD | CT |  |  | 38.3351 | 38.3333 | 38.3308 | 38.3277 | 38.3237 | 38.3189 | 38.3131 | 38.3062 | 38.2994 | 38.2915 | 38.2724 | 38.2042 | 38.1172 | 38.0094 | 32.0237 | 32.0091 | 31.9777 | 31.9436 | 31.9087 | 31.8903 | 31.8835 | 31.8763 | 31.869 | 31.8608 | 31.8418 | 31.7797 | 31.7082 | 31.625 | 33.517 | 33.5109 | 33.5019 | 33.492 | 33.4813 | 33.4697 | 33.4573 | 33.444 | 33.4304 | 33.4153 | 33.3801 | 33.2652 | 33.133 | 32.9791
|  | HINDHEAD | LW |  |  | 38.3351 | 38.3333 | 38.3308 | 38.3277 | 38.3237 | 38.3189 | 38.3131 | 38.3062 | 38.2994 | 38.2915 | 38.2724 | 38.2042 | 38.1172 | 38.0094 | 32.0282 | 32.0175 | 31.9934 | 31.9669 | 31.9393 | 31.9112 | 31.9067 | 31.9029 | 31.8991 | 31.8947 | 31.8841 | 31.8463 | 31.7982 | 31.7385 | 33.5227 | 33.5208 | 33.5182 | 33.515 | 33.5109 | 33.506 | 33.5 | 33.493 | 33.486 | 33.4779 | 33.4583 | 33.3885 | 33.2994 | 33.1889
|  | HINDHEAD | ST |  |  | 38.3369 | 38.3363 | 38.3354 | 38.3344 | 38.3332 | 38.3316 | 38.3298 | 38.3277 | 38.3256 | 38.3233 | 38.3183 | 38.3015 | 38.2762 | 38.2484 | 32.0326 | 32.0274 | 32.0162 | 31.9996 | 31.9792 | 31.9604 | 31.9417 | 31.9232 | 31.9136 | 31.9123 | 31.9096 | 31.9003 | 31.8862 | 31.8709 | 33.5245 | 33.5238 | 33.5229 | 33.5219 | 33.5207 | 33.519 | 33.5171 | 33.5151 | 33.5129 | 33.5105 | 33.5054 | 33.4882 | 33.4622 | 33.4338
|  | HINDHEAD | FS |  |  | 38.3371 | 38.3367 | 38.3363 | 38.3356 | 38.3348 | 38.334 | 38.3332 | 38.3323 | 38.3314 | 38.3304 | 38.3283 | 38.3205 | 38.3114 | 38.3017 | 32.0353 | 32.0345 | 32.0335 | 32.0291 | 32.0238 | 32.017 | 32.0102 | 32.0016 | 31.993 | 31.9844 | 31.9675 | 31.9238 | 31.9057 | 31.9004 | 33.5247 | 33.5242 | 33.5238 | 33.5231 | 33.5223 | 33.5215 | 33.5207 | 33.5198 | 33.5188 | 33.5178 | 33.5157 | 33.5076 | 33.4983 | 33.4884
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL | MINIMUM HEADROOM | SU 00702 06030 | YES | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 13.9552 | 13.9535 | 13.9495 | 13.9452 | 13.9408 | 13.9364 | 13.9321 | 13.9278 | 13.9232 | 13.9186 | 13.9096 | 13.8884 | 13.8666 | 13.8451 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914
|  | HINTON MARTELL | CT |  |  | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 13.9554 | 13.954 | 13.9506 | 13.947 | 13.9433 | 13.9396 | 13.936 | 13.9324 | 13.9285 | 13.9247 | 13.917 | 13.8944 | 13.8712 | 13.8483 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914
|  | HINTON MARTELL | LW |  |  | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 13.9552 | 13.9535 | 13.9495 | 13.9452 | 13.9408 | 13.9364 | 13.9321 | 13.9278 | 13.9232 | 13.9186 | 13.9096 | 13.8884 | 13.8666 | 13.8451 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914
|  | HINTON MARTELL | ST |  |  | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 13.9557 | 13.9547 | 13.9524 | 13.9489 | 13.9447 | 13.942 | 13.9394 | 13.9367 | 13.9339 | 13.9311 | 13.9256 | 13.9124 | 13.8992 | 13.8861 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914
|  | HINTON MARTELL | FS |  |  | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 17.6882 | 13.9563 | 13.9562 | 13.956 | 13.9553 | 13.9544 | 13.9535 | 13.9526 | 13.9514 | 13.9503 | 13.9492 | 13.9469 | 13.9417 | 13.9367 | 13.932 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914 | 15.6914
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE | MINIMUM HEADROOM | SU 79461 54769 | YES | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 37.7387 | 36.0125 | 34.2885 | 43.9393 | 43.914 | 43.8562 | 43.7935 | 43.7307 | 43.6705 | 43.6107 | 43.5518 | 43.4885 | 43.426 | 35.3015 | 33.3605 | 31.327 | 29.296 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 34.0013 | 31.974 | 29.9492
|  | HITCHES LANE | CT |  |  | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 37.7387 | 36.0125 | 34.2885 | 43.9409 | 43.9183 | 43.8666 | 43.8104 | 43.7541 | 43.7002 | 43.6466 | 43.5937 | 43.5368 | 43.4808 | 43.3685 | 34.0342 | 31.8891 | 29.7496 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 34.6731 | 32.5345 | 30.4014
|  | HITCHES LANE | LW |  |  | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 37.7387 | 36.0125 | 34.2885 | 43.9393 | 43.914 | 43.8562 | 43.7935 | 43.7307 | 43.6705 | 43.6107 | 43.5518 | 43.4885 | 43.426 | 35.3015 | 33.3605 | 31.327 | 29.296 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 34.0013 | 31.974 | 29.9492
|  | HITCHES LANE | ST |  |  | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 43.9629 | 43.9363 | 43.9105 | 43.8722 | 43.826 | 43.8068 | 43.7877 | 43.7689 | 43.7487 | 43.729 | 43.6892 | 43.585 | 43.4789 | 43.3731 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702
|  | HITCHES LANE | FS |  |  | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 47.0048 | 43.9694 | 43.953 | 43.9505 | 43.94 | 43.9276 | 43.9208 | 43.9142 | 43.9057 | 43.8974 | 43.8894 | 43.873 | 43.831 | 43.7887 | 43.7471 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702 | 44.6702
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD | MINIMUM HEADROOM | SU 57855 04433 | NO | 18.954 | 18.954 | 14.2091 | 14.1749 | 14.1468 | 14.1192 | 14.0922 | 14.0581 | 13.9977 | 13.9402 | 13.8303 | 13.5274 | 13.1949 | 12.7976 | 20.4809 | 20.4777 | 14.2132 | 14.18 | 14.1525 | 14.1256 | 14.0975 | 14.0645 | 14.0073 | 13.9513 | 13.8441 | 13.549 | 13.225 | 12.8378 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 13.845
|  | HOEFORD | CT |  |  | 18.954 | 18.954 | 14.2091 | 14.1749 | 14.1468 | 14.1192 | 14.0922 | 14.0651 | 14.0358 | 14.0068 | 13.9468 | 13.6206 | 13.2128 | 12.7976 | 20.4811 | 20.4783 | 14.2245 | 14.194 | 14.1655 | 14.1332 | 14.0975 | 14.0645 | 14.0319 | 14.0025 | 13.9471 | 13.671 | 13.3391 | 12.9973 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 14.0372
|  | HOEFORD | LW |  |  | 18.954 | 18.954 | 14.2091 | 14.1749 | 14.1468 | 14.1192 | 14.0922 | 14.0651 | 14.0358 | 14.0068 | 13.9468 | 13.6206 | 13.2128 | 12.7976 | 20.4809 | 20.4777 | 14.2132 | 14.18 | 14.1525 | 14.1256 | 14.0994 | 14.073 | 14.0444 | 14.0161 | 13.9577 | 13.6398 | 13.2424 | 12.8378 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 13.845
|  | HOEFORD | ST |  |  | 18.954 | 18.954 | 18.954 | 18.954 | 14.235 | 14.1763 | 14.1159 | 14.0581 | 13.9977 | 13.9402 | 13.8303 | 13.5274 | 13.1949 | 12.8602 | 20.4822 | 20.4804 | 20.4788 | 20.4776 | 14.2385 | 14.1813 | 14.1225 | 14.0661 | 14.0073 | 13.9513 | 13.8441 | 13.549 | 13.225 | 12.8989 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 13.9186
|  | HOEFORD | FS |  |  | 18.954 | 18.954 | 18.954 | 18.954 | 18.954 | 18.954 | 18.954 | 18.954 | 14.2327 | 14.2149 | 14.1811 | 14.0987 | 14.0002 | 13.8932 | 20.4832 | 20.4822 | 20.4815 | 20.481 | 20.4806 | 20.4795 | 20.4786 | 20.4773 | 14.2362 | 14.2189 | 14.186 | 14.1057 | 14.0097 | 13.9054 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641 | 20.3641
MANNINGTON GSP | LYTCHETT | HOLES BAY | MINIMUM HEADROOM | SZ 00725 91955 | YES | 17.6599 | 17.6515 | 17.6296 | 17.6037 | 17.5754 | 17.5455 | 17.5142 | 17.4823 | 17.4474 | 17.4071 | 17.3187 | 17.0312 | 16.7172 | 16.4053 | 7.9033 | 7.8917 | 7.8615 | 7.8257 | 7.7866 | 7.7453 | 7.7021 | 7.658 | 7.6097 | 7.5541 | 7.4321 | 7.0349 | 6.6012 | 6.1703 | 3.1131 | 3.1016 | 3.0718 | 3.0366 | 2.9981 | 2.9573 | 2.9148 | 2.8713 | 2.8238 | 2.769 | 2.6487 | 2.2574 | 1.8301 | 1.4056
|  | HOLES BAY | CT |  |  | 17.6599 | 17.6515 | 17.6296 | 17.6037 | 17.5754 | 17.5455 | 17.5142 | 17.4823 | 17.4474 | 17.4116 | 17.3402 | 17.0312 | 16.7172 | 16.4053 | 7.9034 | 7.8918 | 7.8619 | 7.8267 | 7.7887 | 7.7486 | 7.707 | 7.6646 | 7.6182 | 7.5709 | 7.4762 | 7.1107 | 6.7392 | 6.3698 | 3.1131 | 3.1017 | 3.0722 | 3.0376 | 3.0001 | 2.9606 | 2.9196 | 2.8778 | 2.8321 | 2.7855 | 2.6922 | 2.3321 | 1.966 | 1.6021
|  | HOLES BAY | LW |  |  | 17.6599 | 17.6515 | 17.6296 | 17.6037 | 17.5754 | 17.5455 | 17.5142 | 17.4823 | 17.4474 | 17.4116 | 17.3402 | 17.0312 | 16.7172 | 16.4053 | 7.9033 | 7.8917 | 7.8615 | 7.8257 | 7.7866 | 7.7453 | 7.7021 | 7.658 | 7.6097 | 7.5604 | 7.4617 | 7.0349 | 6.6012 | 6.1703 | 3.1131 | 3.1016 | 3.0718 | 3.0366 | 2.9981 | 2.9573 | 2.9148 | 2.8713 | 2.8238 | 2.7752 | 2.6779 | 2.2574 | 1.8301 | 1.4056
|  | HOLES BAY | ST |  |  | 17.9032 | 17.6594 | 17.6507 | 17.6366 | 17.6183 | 17.5779 | 17.5371 | 17.4963 | 17.4518 | 17.4071 | 17.3187 | 17.1029 | 16.8914 | 16.6814 | 8.2394 | 7.9027 | 7.8906 | 7.8711 | 7.8459 | 7.7901 | 7.7337 | 7.6774 | 7.6158 | 7.5541 | 7.4321 | 7.134 | 6.8418 | 6.5517 | 3.4442 | 3.1124 | 3.1005 | 3.0813 | 3.0564 | 3.0014 | 2.9459 | 2.8904 | 2.8298 | 2.769 | 2.6487 | 2.355 | 2.0672 | 1.7813
|  | HOLES BAY | FS |  |  | 17.9702 | 17.6645 | 17.6637 | 17.6598 | 17.6549 | 17.6429 | 17.6308 | 17.6155 | 17.6 | 17.5845 | 17.5537 | 17.4785 | 17.4055 | 17.3344 | 8.3319 | 7.9097 | 7.9086 | 7.9033 | 7.8964 | 7.8799 | 7.8631 | 7.842 | 7.8206 | 7.7992 | 7.7567 | 7.6527 | 7.552 | 7.4537 | 3.5353 | 3.1193 | 3.1182 | 3.113 | 3.1062 | 3.09 | 3.0735 | 3.0526 | 3.0316 | 3.0105 | 2.9686 | 2.8662 | 2.7669 | 2.67
MELKSHAM GSP | FROME BSP | HOLWELL | MINIMUM HEADROOM | ST 72191 44633 | YES | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 6.2698 | 6.2698 | 6.2698 | 13.8918 | 13.886 | 13.8732 | 13.8539 | 13.8307 | 13.8243 | 13.8181 | 13.8119 | 13.8053 | 13.7948 | 13.7709 | 13.0298 | 13.0069 | 12.9843 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 14.1727 | 14.1727 | 14.1727
|  | HOLWELL | CT |  |  | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 6.2698 | 6.2698 | 6.2698 | 13.8928 | 13.8889 | 13.8795 | 13.8693 | 13.8593 | 13.8493 | 13.8395 | 13.8297 | 13.8192 | 13.8088 | 13.7882 | 13.045 | 13.0133 | 12.9901 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 14.1727 | 14.1727 | 14.1727
|  | HOLWELL | LW |  |  | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 6.2698 | 6.2698 | 6.2698 | 13.8924 | 13.8878 | 13.8769 | 13.8651 | 13.8534 | 13.8418 | 13.8304 | 13.8191 | 13.8069 | 13.7948 | 13.7709 | 13.0298 | 13.0069 | 12.9843 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 14.1727 | 14.1727 | 14.1727
|  | HOLWELL | ST |  |  | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 6.6974 | 6.6974 | 6.6974 | 13.8918 | 13.886 | 13.8732 | 13.8539 | 13.8307 | 13.8243 | 13.8181 | 13.8119 | 13.8053 | 13.7987 | 13.7859 | 13.4078 | 13.3748 | 13.3419 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 14.6277 | 14.6277 | 14.6277
|  | HOLWELL | FS |  |  | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 7.125 | 13.8953 | 13.895 | 13.8946 | 13.8927 | 13.8904 | 13.8883 | 13.8862 | 13.8835 | 13.8809 | 13.8783 | 13.8733 | 13.8611 | 13.849 | 13.8373 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827 | 15.0827
MANNINGTON GSP | SALISBURY | HOMINGTON | MINIMUM HEADROOM | SU 11742 26037 | YES | 19.312 | 19.3117 | 19.3109 | 19.31 | 19.3091 | 19.3081 | 19.3065 | 19.3045 | 19.3023 | 19.3002 | 19.2959 | 19.2842 | 19.2664 | 19.2487 | 17.5677 | 17.5655 | 17.5603 | 17.5545 | 17.5485 | 17.5422 | 17.5314 | 17.5182 | 17.5039 | 17.4897 | 17.4621 | 17.3986 | 17.3013 | 17.2051 | 17.3263 | 17.3248 | 17.3214 | 17.3176 | 17.3136 | 17.3094 | 17.3024 | 17.2937 | 17.2843 | 17.2749 | 17.2564 | 17.2037 | 17.1664 | 17.1664
|  | HOMINGTON | CT |  |  | 19.312 | 19.3117 | 19.3109 | 19.31 | 19.3091 | 19.3081 | 19.3071 | 19.3061 | 19.305 | 19.3038 | 19.3014 | 19.2842 | 19.2664 | 19.2487 | 17.5677 | 17.5655 | 17.5603 | 17.5546 | 17.5485 | 17.5424 | 17.536 | 17.5295 | 17.5225 | 17.5153 | 17.5006 | 17.3986 | 17.3013 | 17.2051 | 17.3263 | 17.3248 | 17.3214 | 17.3176 | 17.3136 | 17.3096 | 17.3054 | 17.3011 | 17.2965 | 17.2918 | 17.2821 | 17.2037 | 17.1664 | 17.1664
|  | HOMINGTON | LW |  |  | 19.312 | 19.3117 | 19.3109 | 19.31 | 19.3091 | 19.3081 | 19.3071 | 19.3061 | 19.305 | 19.3038 | 19.3014 | 19.2842 | 19.2664 | 19.2487 | 17.5677 | 17.5655 | 17.5603 | 17.5545 | 17.5485 | 17.5422 | 17.5356 | 17.5289 | 17.5214 | 17.5137 | 17.4978 | 17.4008 | 17.3076 | 17.2152 | 17.3263 | 17.3248 | 17.3214 | 17.3176 | 17.3136 | 17.3094 | 17.3051 | 17.3007 | 17.2958 | 17.2907 | 17.2803 | 17.2054 | 17.1664 | 17.1664
|  | HOMINGTON | ST |  |  | 19.3121 | 19.312 | 19.3117 | 19.3112 | 19.3105 | 19.3085 | 19.3065 | 19.3045 | 19.3023 | 19.3002 | 19.2959 | 19.2851 | 19.2744 | 19.2637 | 17.5686 | 17.5676 | 17.5655 | 17.5622 | 17.5581 | 17.5447 | 17.5314 | 17.5182 | 17.5039 | 17.4897 | 17.4621 | 17.4056 | 17.3494 | 17.2937 | 17.3269 | 17.3262 | 17.3248 | 17.3227 | 17.3199 | 17.3111 | 17.3024 | 17.2937 | 17.2843 | 17.2749 | 17.2564 | 17.2094 | 17.1668 | 17.1664
|  | HOMINGTON | FS |  |  | 19.3122 | 19.3122 | 19.3122 | 19.312 | 19.3119 | 19.3112 | 19.3105 | 19.3096 | 19.3088 | 19.3079 | 19.3062 | 19.302 | 19.2979 | 19.294 | 17.5691 | 17.569 | 17.5688 | 17.5679 | 17.5668 | 17.5623 | 17.5579 | 17.5521 | 17.5464 | 17.5407 | 17.5295 | 17.5018 | 17.4748 | 17.4518 | 17.3272 | 17.3271 | 17.327 | 17.3264 | 17.3257 | 17.3227 | 17.3198 | 17.316 | 17.3122 | 17.3085 | 17.3011 | 17.2829 | 17.2651 | 17.2479
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK | MINIMUM HEADROOM | SU 72602 53780 | YES | 28.3363 | 28.3248 | 28.2977 | 28.2683 | 28.2389 | 28.2093 | 28.1797 | 28.1503 | 28.013 | 27.7056 | 27.0856 | 26.1985 | 25.2614 | 24.3145 | 26.5368 | 26.3966 | 26.0628 | 25.7016 | 25.3424 | 24.9839 | 24.6296 | 24.2806 | 23.9047 | 23.5327 | 22.7844 | 21.6475 | 20.446 | 19.2431 | 26.5396 | 26.4019 | 26.0743 | 25.7196 | 25.367 | 25.0149 | 24.667 | 24.3241 | 23.9547 | 23.5889 | 22.8528 | 21.7297 | 20.5121 | 19.2705
|  | HOOK | CT |  |  | 28.3363 | 28.3248 | 28.2977 | 28.2683 | 28.2389 | 28.2093 | 28.1797 | 28.1503 | 28.013 | 27.7056 | 27.0856 | 26.1985 | 25.2614 | 24.3145 | 26.5368 | 26.3966 | 26.0628 | 25.7016 | 25.3424 | 24.9839 | 24.6296 | 24.2806 | 23.9047 | 23.5327 | 22.7844 | 21.6475 | 20.446 | 19.2431 | 26.5396 | 26.4019 | 26.0743 | 25.7196 | 25.367 | 25.0149 | 24.667 | 24.3241 | 23.9547 | 23.5889 | 22.8528 | 21.7297 | 20.5121 | 19.2705
|  | HOOK | LW |  |  | 28.3363 | 28.3248 | 28.2977 | 28.2683 | 28.2389 | 28.2093 | 28.1797 | 28.1503 | 28.013 | 27.7056 | 27.0856 | 26.1985 | 25.2614 | 24.3145 | 26.5403 | 26.405 | 26.0825 | 25.7335 | 25.3862 | 25.0377 | 24.692 | 24.3502 | 23.9823 | 23.6191 | 22.887 | 21.8447 | 20.7492 | 19.6489 | 26.5433 | 26.4105 | 26.0943 | 25.752 | 25.4113 | 25.0695 | 24.7302 | 24.3949 | 24.0338 | 23.6771 | 22.9581 | 21.9317 | 20.8358 | 19.7039
|  | HOOK | ST |  |  | 28.3415 | 28.3356 | 28.3228 | 28.3036 | 28.2804 | 28.2707 | 28.2611 | 28.2518 | 28.2417 | 28.2318 | 28.2115 | 28.1572 | 27.8847 | 27.3554 | 26.5991 | 26.5294 | 26.3767 | 26.1466 | 25.8684 | 25.7548 | 25.643 | 25.5339 | 25.4167 | 25.3018 | 25.0672 | 24.4556 | 23.8339 | 23.2118 | 26.601 | 26.5327 | 26.3829 | 26.1573 | 25.8845 | 25.773 | 25.6634 | 25.5563 | 25.4414 | 25.3286 | 25.0983 | 24.4976 | 23.8864 | 23.2738
|  | HOOK | FS |  |  | 28.3454 | 28.3446 | 28.3437 | 28.3388 | 28.3329 | 28.3295 | 28.3261 | 28.3217 | 28.3175 | 28.3133 | 28.3049 | 28.2829 | 28.2604 | 28.2382 | 26.6464 | 26.6369 | 26.627 | 26.569 | 26.5 | 26.4599 | 26.4203 | 26.3696 | 26.32 | 26.2715 | 26.1736 | 25.9232 | 25.6734 | 25.4295 | 26.6475 | 26.6381 | 26.6284 | 26.5714 | 26.5038 | 26.4644 | 26.4255 | 26.3758 | 26.3271 | 26.2795 | 26.1835 | 25.9376 | 25.6922 | 25.4525
LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR | MINIMUM HEADROOM | TQ 12710 72057 | NO | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.6829 | 15.6812 | 15.678 | 15.6746 | 15.6715 | 15.6681 | 15.6647 | 15.6611 | 15.6571 | 15.6531 | 15.6448 | 15.5895 | 15.529 | 15.4675 | 6.8734 | 6.8707 | 6.8653 | 6.8599 | 6.8546 | 6.8492 | 6.8436 | 6.8376 | 6.8311 | 6.8245 | 6.8109 | 6.7199 | 6.6205 | 6.5194
|  | HOPE AND ANCHOR | CT |  |  | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.6829 | 15.6814 | 15.6782 | 15.6751 | 15.672 | 15.6687 | 15.6653 | 15.6616 | 15.6576 | 15.6536 | 15.6453 | 15.6223 | 15.5797 | 15.5321 | 6.8735 | 6.8709 | 6.8658 | 6.8606 | 6.8555 | 6.8501 | 6.8445 | 6.8385 | 6.8319 | 6.8253 | 6.8116 | 6.7738 | 6.7039 | 6.6256
|  | HOPE AND ANCHOR | LW |  |  | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.6829 | 15.6812 | 15.678 | 15.6746 | 15.6715 | 15.6681 | 15.6647 | 15.6611 | 15.6571 | 15.6531 | 15.6448 | 15.5895 | 15.529 | 15.4675 | 6.8734 | 6.8707 | 6.8653 | 6.8599 | 6.8546 | 6.8492 | 6.8436 | 6.8376 | 6.8311 | 6.8245 | 6.8109 | 6.7199 | 6.6205 | 6.5194
|  | HOPE AND ANCHOR | ST |  |  | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.7589 | 15.6827 | 15.6812 | 15.6793 | 15.6772 | 15.6733 | 15.6693 | 15.6652 | 15.6608 | 15.6563 | 15.6472 | 15.6246 | 15.5898 | 15.5528 | 6.9983 | 6.873 | 6.8706 | 6.8675 | 6.864 | 6.8577 | 6.8512 | 6.8444 | 6.8371 | 6.8297 | 6.8148 | 6.7777 | 6.7204 | 6.6597
|  | HOPE AND ANCHOR | FS |  |  | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.9524 | 15.7593 | 15.759 | 15.7586 | 15.7579 | 15.7573 | 15.756 | 15.7547 | 15.7531 | 15.7515 | 15.7499 | 15.7466 | 15.74 | 15.7276 | 15.7113 | 6.9991 | 6.9985 | 6.9978 | 6.9968 | 6.9957 | 6.9936 | 6.9915 | 6.9889 | 6.9862 | 6.9836 | 6.9782 | 6.9673 | 6.9469 | 6.9202
LOVEDEAN GSP | HAVANT | HORNDEAN | MINIMUM HEADROOM | SU 70271 12802 | NO | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 27.4555 | 32.5554 | 32.5024 | 32.4319 | 32.3586 | 32.28 | 32.246 | 32.2447 | 32.2447 | 32.2447 | 32.2447 | 32.2447 | 25.2191 | 22.8851 | 20.549 | 34.3579 | 34.3201 | 34.255 | 34.1874 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 25.7254 | 23.3637 | 21
|  | HORNDEAN | CT |  |  | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 27.4555 | 32.5597 | 32.5117 | 32.4519 | 32.3903 | 32.3235 | 32.2651 | 32.2447 | 32.2447 | 32.2447 | 32.2447 | 32.2447 | 25.8652 | 23.6452 | 21.4258 | 34.3606 | 34.3287 | 34.2735 | 34.2167 | 34.1551 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 26.3792 | 24.1328 | 21.8872
|  | HORNDEAN | LW |  |  | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 27.4555 | 32.5554 | 32.5024 | 32.4319 | 32.3586 | 32.28 | 32.246 | 32.2447 | 32.2447 | 32.2447 | 32.2447 | 32.2447 | 25.2191 | 22.8851 | 20.549 | 34.3579 | 34.3201 | 34.255 | 34.1874 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 25.7254 | 23.3637 | 21
|  | HORNDEAN | ST |  |  | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 32.6204 | 32.5463 | 32.5085 | 32.4712 | 32.4237 | 32.3558 | 32.2863 | 32.2523 | 32.2447 | 32.2447 | 32.2447 | 32.2447 | 25.5469 | 24.0929 | 34.3996 | 34.352 | 34.3257 | 34.2913 | 34.2475 | 34.1849 | 34.1208 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 34.1186 | 26.0571 | 24.5858
|  | HORNDEAN | FS |  |  | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 38.5859 | 32.6312 | 32.6199 | 32.6104 | 32.5904 | 32.5665 | 32.5343 | 32.5061 | 32.4781 | 32.4498 | 32.4212 | 32.3614 | 32.2514 | 32.2447 | 32.2447 | 34.4066 | 34.3993 | 34.3932 | 34.3803 | 34.365 | 34.3443 | 34.3234 | 34.2977 | 34.2715 | 34.2452 | 34.19 | 34.1186 | 34.1186 | 34.1186
NURSLING GSP | WINCHESTER | HOUGHTON | MINIMUM HEADROOM | SU 33784 31741 | YES | -2.6298 | -2.6545 | -2.7139 | -2.7781 | -2.8424 | -2.9062 | -2.9701 | -3.0335 | -3.1017 | -3.1693 | -3.3035 | -3.5399 | -3.7834 | -4.0517 | -3.9503 | -4.0001 | -4.1199 | -4.2494 | -4.3784 | -4.5062 | -4.6338 | -4.7603 | -4.8961 | -5.0304 | -5.2965 | -5.7072 | -6.131 | -6.5502 | -3.0703 | -3.1134 | -3.217 | -3.3289 | -3.4404 | -3.5509 | -3.6612 | -3.7705 | -3.8879 | -4.004 | -4.234 | -4.589 | -4.9553 | -5.3177
|  | HOUGHTON | CT |  |  | -2.6298 | -2.6545 | -2.7139 | -2.7781 | -2.8424 | -2.9062 | -2.9701 | -3.0335 | -3.1017 | -3.1693 | -3.3035 | -3.5399 | -3.7834 | -4.0517 | -3.9503 | -4.0001 | -4.1199 | -4.2494 | -4.3784 | -4.5062 | -4.6338 | -4.7603 | -4.8961 | -5.0304 | -5.2965 | -5.7072 | -6.131 | -6.5502 | -3.0703 | -3.1134 | -3.217 | -3.3289 | -3.4404 | -3.5509 | -3.6612 | -3.7705 | -3.8879 | -4.004 | -4.234 | -4.589 | -4.9553 | -5.3177
|  | HOUGHTON | LW |  |  | -2.6298 | -2.6545 | -2.7139 | -2.7781 | -2.8424 | -2.9062 | -2.9701 | -3.0335 | -3.1017 | -3.1693 | -3.3035 | -3.5399 | -3.7834 | -4.0517 | -3.9433 | -3.9826 | -4.0775 | -4.1801 | -4.2827 | -4.3846 | -4.4866 | -4.5878 | -4.6968 | -4.8047 | -5.019 | -5.3964 | -5.7852 | -6.1702 | -3.0643 | -3.0983 | -3.1803 | -3.269 | -3.3577 | -3.4458 | -3.5339 | -3.6214 | -3.7156 | -3.8089 | -3.9941 | -4.3203 | -4.6564 | -4.9892
|  | HOUGHTON | ST |  |  | -2.6224 | -2.6369 | -2.6692 | -2.7177 | -2.7764 | -2.804 | -2.8319 | -2.8593 | -2.8888 | -2.9178 | -2.9749 | -3.1188 | -3.262 | -3.4046 | -3.9314 | -3.9546 | -4.0062 | -4.0835 | -4.1772 | -4.2214 | -4.2658 | -4.3097 | -4.3568 | -4.403 | -4.4943 | -4.7239 | -4.9527 | -5.1803 | -3.054 | -3.0741 | -3.1187 | -3.1855 | -3.2665 | -3.3047 | -3.3431 | -3.381 | -3.4217 | -3.4617 | -3.5406 | -3.7391 | -3.9368 | -4.1335
|  | HOUGHTON | FS |  |  | -2.6144 | -2.6159 | -2.6178 | -2.6284 | -2.6412 | -2.6509 | -2.6605 | -2.6729 | -2.685 | -2.6969 | -2.7204 | -2.7782 | -2.8341 | -2.8878 | -3.9187 | -3.9211 | -3.9241 | -3.9411 | -3.9615 | -3.9769 | -3.9923 | -4.012 | -4.0314 | -4.0504 | -4.0879 | -4.1802 | -4.2694 | -4.3552 | -3.0431 | -3.0451 | -3.0478 | -3.0624 | -3.08 | -3.0933 | -3.1067 | -3.1237 | -3.1404 | -3.1569 | -3.1893 | -3.2691 | -3.3462 | -3.4204
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS | MINIMUM HEADROOM | SU 62187 52886 | YES | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 44.913 | 44.8401 | 44.7004 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 47.0261 | 47.0152 | 46.9945 | 46.966 | 46.9416 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269
|  | HOUNDMILLS | CT |  |  | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 44.9141 | 44.8513 | 44.7272 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 47.0262 | 47.0169 | 46.9985 | 46.9736 | 46.9528 | 46.9289 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269
|  | HOUNDMILLS | LW |  |  | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 44.913 | 44.8401 | 44.7004 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 47.0261 | 47.0152 | 46.9945 | 46.966 | 46.9416 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269
|  | HOUNDMILLS | ST |  |  | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 44.9902 | 44.8778 | 44.799 | 44.6844 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 47.0375 | 47.0208 | 47.0091 | 46.9921 | 46.977 | 46.9591 | 46.9393 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269 | 46.9269
|  | HOUNDMILLS | FS |  |  | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 48.3247 | 44.9967 | 44.9049 | 44.8691 | 44.8176 | 44.7747 | 44.7229 | 44.667 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 44.6166 | 47.0385 | 47.0249 | 47.0195 | 47.0119 | 47.0055 | 46.9978 | 46.9895 | 46.9803 | 46.9702 | 46.9592 | 46.9386 | 46.9269 | 46.9269 | 46.9269
BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD | MINIMUM HEADROOM | SU 34066 68957 | YES | 14.1166 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 14.3448 | 18.1702 | 18.111 | 18.0466 | 17.9822 | 17.9183 | 17.8549 | 17.7923 | 17.7246 | 17.6647 | 17.5468 | 17.4158 | 17.2841 | 17.1939 | 14.6166 | 18.4406 | 18.3781 | 18.313 | 18.2777 | 18.2426 | 18.2079 | 18.1735 | 18.1363 | 18.0994 | 18.0266 | 17.8979 | 17.8979 | 17.8979
|  | HUNGERFORD | CT |  |  | 14.1166 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 14.3448 | 18.1702 | 18.111 | 18.0466 | 17.9822 | 17.9183 | 17.8549 | 17.7923 | 17.7246 | 17.6647 | 17.5468 | 17.4158 | 17.2841 | 17.1939 | 14.6166 | 18.4406 | 18.3781 | 18.313 | 18.2777 | 18.2426 | 18.2079 | 18.1735 | 18.1363 | 18.0994 | 18.0266 | 17.8979 | 17.8979 | 17.8979
|  | HUNGERFORD | LW |  |  | 14.1166 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 14.3466 | 18.1749 | 18.1224 | 18.0651 | 18.0079 | 17.951 | 17.8944 | 17.8386 | 17.7778 | 17.7182 | 17.6102 | 17.4308 | 17.2925 | 17.1943 | 14.6185 | 18.4455 | 18.3901 | 18.3296 | 18.2918 | 18.2606 | 18.2295 | 18.1989 | 18.1656 | 18.1324 | 18.0657 | 17.8979 | 17.8979 | 17.8979
|  | HUNGERFORD | ST |  |  | 14.1166 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 14.3588 | 18.2051 | 18.1968 | 18.1839 | 18.168 | 18.1219 | 18.0765 | 18.0318 | 17.9834 | 17.9358 | 17.8427 | 17.6146 | 17.4847 | 17.4046 | 14.6315 | 18.4775 | 18.4687 | 18.4551 | 18.4382 | 18.3896 | 18.3415 | 18.3049 | 18.2784 | 18.2522 | 18.2012 | 18.0684 | 17.9323 | 17.8979
|  | HUNGERFORD | FS |  |  | 14.1166 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 18.7916 | 14.3604 | 18.2094 | 18.2082 | 18.2007 | 18.1915 | 18.1757 | 18.1599 | 18.1397 | 18.1197 | 18.1001 | 18.0617 | 17.9649 | 17.8684 | 17.7742 | 14.6331 | 18.482 | 18.4808 | 18.4728 | 18.4632 | 18.4464 | 18.4297 | 18.4083 | 18.3872 | 18.3665 | 18.326 | 18.2682 | 18.2152 | 18.1636
LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON | MINIMUM HEADROOM | SU 86949 02632 | YES | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 35.7012 | 35.4541 | 35.414 | 35.3685 | 35.3202 | 35.2692 | 35.2153 | 35.1412 | 35.0609 | 34.9768 | 34.7936 | 34.4186 | 34.2626 | 34.2626 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846
|  | HUNSTON | CT |  |  | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 35.7022 | 35.4577 | 35.4213 | 35.3804 | 35.3368 | 35.2897 | 35.2402 | 35.1727 | 35.0982 | 35.0189 | 34.8415 | 34.4563 | 34.2626 | 34.2626 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846
|  | HUNSTON | LW |  |  | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 35.7012 | 35.4541 | 35.414 | 35.3685 | 35.3202 | 35.2692 | 35.2153 | 35.1412 | 35.0609 | 34.9768 | 34.7936 | 34.4186 | 34.2626 | 34.2626 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846
|  | HUNSTON | ST |  |  | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 35.7087 | 35.6961 | 35.6756 | 35.6471 | 35.6127 | 35.5681 | 35.5222 | 35.4645 | 35.4002 | 35.332 | 35.1806 | 34.9194 | 34.6996 | 34.4861 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846
|  | HUNSTON | FS |  |  | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 38.8448 | 35.7151 | 35.71 | 35.7046 | 35.695 | 35.6841 | 35.6679 | 35.6512 | 35.6273 | 35.6021 | 35.5757 | 35.5185 | 35.4166 | 35.3278 | 35.2429 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846 | 34.9846
BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT | MINIMUM HEADROOM | SU 39384 52476 | YES | 7.3005 | 7.3002 | 7.2998 | 7.2992 | 7.2986 | 7.2978 | 7.2968 | 7.2957 | 7.294 | 7.2921 | 7.2875 | 7.2712 | 7.2434 | 7.203 | 6.8827 | 6.8815 | 6.8787 | 6.8753 | 6.8716 | 6.8677 | 6.8635 | 6.8591 | 6.8522 | 6.8445 | 6.8293 | 6.7498 | 6.666 | 6.6072 | 7.091 | 7.09 | 7.0886 | 7.0868 | 7.0849 | 7.0829 | 7.0807 | 7.0783 | 7.0749 | 7.0711 | 7.0623 | 7.0319 | 6.9855 | 4.6473
|  | HURSTBOURNE TARRANT | CT |  |  | 7.3005 | 7.3002 | 7.2998 | 7.2992 | 7.2986 | 7.2978 | 7.2968 | 7.2957 | 7.294 | 7.2921 | 7.2875 | 7.2712 | 7.2434 | 7.203 | 6.8827 | 6.8815 | 6.8787 | 6.8753 | 6.8716 | 6.8677 | 6.8635 | 6.8591 | 6.8538 | 6.8482 | 6.836 | 6.7498 | 6.666 | 6.6072 | 7.091 | 7.09 | 7.0886 | 7.0868 | 7.0849 | 7.0829 | 7.0807 | 7.0783 | 7.0749 | 7.0711 | 7.0623 | 7.0319 | 6.9855 | 4.6473
|  | HURSTBOURNE TARRANT | LW |  |  | 7.3005 | 7.3002 | 7.2998 | 7.2992 | 7.2986 | 7.2978 | 7.2968 | 7.2957 | 7.294 | 7.2921 | 7.2875 | 7.2712 | 7.2434 | 7.203 | 6.8835 | 6.8831 | 6.8816 | 6.8798 | 6.8776 | 6.8751 | 6.8724 | 6.8695 | 6.866 | 6.8623 | 6.8541 | 6.7778 | 6.6992 | 6.6511 | 7.0919 | 7.0916 | 7.0912 | 7.0907 | 7.09 | 7.0892 | 7.0883 | 7.0871 | 7.0855 | 7.0836 | 7.079 | 7.0627 | 7.0351 | 4.7419
|  | HURSTBOURNE TARRANT | ST |  |  | 7.3008 | 7.3007 | 7.3005 | 7.3004 | 7.3002 | 7.2999 | 7.2996 | 7.2993 | 7.2989 | 7.2984 | 7.2975 | 7.2937 | 7.2872 | 7.2778 | 6.8838 | 6.8837 | 6.8832 | 6.8824 | 6.8813 | 6.8742 | 6.8671 | 6.8599 | 6.8522 | 6.8445 | 6.8293 | 6.7897 | 6.7481 | 6.7169 | 7.0922 | 7.0921 | 7.092 | 7.0918 | 7.0916 | 7.0913 | 7.091 | 7.0907 | 7.0903 | 7.0899 | 7.089 | 7.0851 | 7.0787 | 7.0693
|  | HURSTBOURNE TARRANT | FS |  |  | 7.3008 | 7.3007 | 7.3007 | 7.3006 | 7.3004 | 7.3003 | 7.3002 | 7.3 | 7.2999 | 7.2997 | 7.2994 | 7.298 | 7.2961 | 7.294 | 6.8839 | 6.8839 | 6.8839 | 6.8837 | 6.8835 | 6.881 | 6.8784 | 6.8751 | 6.8719 | 6.8687 | 6.8623 | 6.846 | 6.8297 | 6.8138 | 7.0922 | 7.0922 | 7.0921 | 7.092 | 7.0919 | 7.0917 | 7.0916 | 7.0915 | 7.0913 | 7.0911 | 7.0908 | 7.0895 | 7.0876 | 7.0854
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE | MINIMUM HEADROOM | SU 63055 50105 | YES | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 48.0616 | 48.0494 | 48.0199 | 47.9875 | 47.9554 | 47.9236 | 47.8919 | 47.8604 | 47.8224 | 47.78 | 47.6975 | 47.3954 | 47.3954 | 47.3954 | 50.6737 | 50.6625 | 50.6354 | 50.6058 | 50.5763 | 50.5658 | 50.5581 | 50.5505 | 50.5413 | 50.531 | 50.5271 | 50.5271 | 50.5271 | 50.5271
|  | JAYS CLOSE | CT |  |  | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 48.0634 | 48.0537 | 48.0305 | 48.0049 | 47.9795 | 47.9543 | 47.929 | 47.9038 | 47.8764 | 47.8492 | 47.7961 | 47.4515 | 47.3954 | 47.3954 | 50.6753 | 50.6665 | 50.6451 | 50.6217 | 50.5984 | 50.5753 | 50.5671 | 50.561 | 50.5544 | 50.5478 | 50.5349 | 50.5271 | 50.5271 | 50.5271
|  | JAYS CLOSE | LW |  |  | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 48.0616 | 48.0494 | 48.0199 | 47.9875 | 47.9554 | 47.9236 | 47.8919 | 47.8604 | 47.8262 | 47.7924 | 47.7241 | 47.3954 | 47.3954 | 47.3954 | 50.6737 | 50.6625 | 50.6354 | 50.6058 | 50.5763 | 50.5658 | 50.5581 | 50.5505 | 50.5422 | 50.534 | 50.5271 | 50.5271 | 50.5271 | 50.5271
|  | JAYS CLOSE | ST |  |  | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 48.2893 | 48.0576 | 48.0412 | 48.0164 | 47.9866 | 47.9458 | 47.9055 | 47.8656 | 47.8224 | 47.78 | 47.6975 | 47.4713 | 47.3954 | 47.3954 | 50.8824 | 50.67 | 50.655 | 50.6322 | 50.6049 | 50.5712 | 50.5614 | 50.5518 | 50.5413 | 50.531 | 50.5271 | 50.5271 | 50.5271 | 50.5271
|  | JAYS CLOSE | FS |  |  | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 52.4448 | 48.2933 | 48.0683 | 48.0672 | 48.062 | 48.0557 | 48.0423 | 48.0289 | 48.0117 | 47.9947 | 47.978 | 47.9457 | 47.8606 | 47.7715 | 47.682 | 50.886 | 50.6798 | 50.6788 | 50.674 | 50.6683 | 50.656 | 50.6437 | 50.6279 | 50.6124 | 50.5971 | 50.5712 | 50.5506 | 50.529 | 50.5271
COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON | MINIMUM HEADROOM | SP 52881 01094 | NO | 11.1552 | 11.1513 | 11.1463 | 11.1432 | 11.1408 | 11.1384 | 11.1361 | 11.1337 | 11.1313 | 11.1278 | 11.1189 | 11.0939 | 11.0939 | 11.0939 | 10.6887 | 10.6844 | 10.6789 | 10.6755 | 10.6725 | 10.669 | 10.665 | 10.6611 | 10.6574 | 10.6541 | 10.6467 | 10.599 | 10.5467 | 10.5075 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809
|  | KENNINGTON | CT |  |  | 11.1552 | 11.1513 | 11.1463 | 11.1432 | 11.1408 | 11.1384 | 11.1361 | 11.1337 | 11.1313 | 11.1278 | 11.1189 | 11.0939 | 11.0939 | 11.0939 | 10.6887 | 10.6847 | 10.6792 | 10.6756 | 10.6725 | 10.669 | 10.665 | 10.6611 | 10.6574 | 10.6541 | 10.6467 | 10.599 | 10.5467 | 10.5075 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809
|  | KENNINGTON | LW |  |  | 11.1552 | 11.1513 | 11.1463 | 11.1432 | 11.1408 | 11.1384 | 11.1361 | 11.1337 | 11.1313 | 11.1278 | 11.1189 | 11.0939 | 11.0939 | 11.0939 | 10.6887 | 10.6844 | 10.6789 | 10.6755 | 10.6728 | 10.6702 | 10.6676 | 10.665 | 10.6623 | 10.6584 | 10.6487 | 10.601 | 10.5489 | 10.5084 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809
|  | KENNINGTON | ST |  |  | 11.1567 | 11.1548 | 11.1528 | 11.1521 | 11.1515 | 11.1474 | 11.143 | 11.1388 | 11.1345 | 11.1305 | 11.122 | 11.0951 | 11.0939 | 11.0939 | 10.6903 | 10.6882 | 10.6861 | 10.6852 | 10.6846 | 10.6801 | 10.6753 | 10.6705 | 10.6658 | 10.6614 | 10.6521 | 10.6225 | 10.5913 | 10.5604 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809
|  | KENNINGTON | FS |  |  | 11.1577 | 11.1565 | 11.1554 | 11.1549 | 11.1546 | 11.1531 | 11.1517 | 11.1499 | 11.1481 | 11.1465 | 11.1431 | 11.1336 | 11.1225 | 11.1107 | 10.6914 | 10.69 | 10.6889 | 10.6884 | 10.688 | 10.6864 | 10.6848 | 10.6828 | 10.6809 | 10.679 | 10.6753 | 10.6649 | 10.6527 | 10.6397 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809 | 11.1809
BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL | MINIMUM HEADROOM | SU 67102 74048 | NO | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 20.8088 | 26.341 | 26.3161 | 26.2723 | 26.2268 | 26.2117 | 26.1964 | 26.1779 | 26.1465 | 26.1128 | 26.0796 | 26.0151 | 25.836 | 20.7943 | 19.0283 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 20.7016 | 18.8798
|  | KENTWOOD HILL | CT |  |  | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 20.8088 | 26.341 | 26.3161 | 26.2723 | 26.2268 | 26.2117 | 26.1964 | 26.1809 | 26.166 | 26.1501 | 26.1343 | 26.1032 | 25.8502 | 20.9606 | 19.2629 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 20.873 | 19.1218
|  | KENTWOOD HILL | LW |  |  | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 20.8088 | 26.3415 | 26.3166 | 26.2755 | 26.2329 | 26.2149 | 26.2011 | 26.1874 | 26.1739 | 26.1591 | 26.1443 | 26.1136 | 25.836 | 20.7943 | 19.0283 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 20.7016 | 18.8798
|  | KENTWOOD HILL | ST |  |  | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 26.374 | 26.3397 | 26.3236 | 26.3016 | 26.2745 | 26.21 | 26.1779 | 26.1465 | 26.1128 | 26.0796 | 26.0151 | 25.8383 | 21.4443 | 20.3087 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 21.3721 | 20.2006
|  | KENTWOOD HILL | FS |  |  | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 27.8522 | 26.3803 | 26.3758 | 26.3732 | 26.3658 | 26.357 | 26.3258 | 26.2951 | 26.2558 | 26.2238 | 26.2114 | 26.1875 | 26.1239 | 26.0563 | 25.9876 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083 | 26.4083
COWLEY GSP | YARNTON BSP | KIDDINGTON | MINIMUM HEADROOM | SP 43362 24301 | YES | 25.1391 | 25.1354 | 25.1268 | 25.1173 | 25.1077 | 25.0929 | 25.083 | 25.0801 | 25.077 | 25.074 | 25.0679 | 25.0517 | 25.0227 | 24.9938 | 24.1797 | 24.1765 | 24.1689 | 24.1606 | 24.1523 | 24.1441 | 24.136 | 24.128 | 24.1193 | 24.1107 | 24.0929 | 24.0003 | 23.9663 | 23.9327 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195
|  | KIDDINGTON | CT |  |  | 25.1391 | 25.1354 | 25.1268 | 25.1173 | 25.1077 | 25.0982 | 25.0888 | 25.0846 | 25.0837 | 25.0827 | 25.0799 | 25.0518 | 25.0227 | 24.9938 | 24.1797 | 24.1765 | 24.1689 | 24.1606 | 24.1523 | 24.1441 | 24.136 | 24.128 | 24.1193 | 24.1107 | 24.0929 | 24.0003 | 23.9663 | 23.9327 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195
|  | KIDDINGTON | LW |  |  | 25.1391 | 25.1354 | 25.1268 | 25.1173 | 25.1077 | 25.0982 | 25.0888 | 25.0846 | 25.0837 | 25.0827 | 25.0799 | 25.0518 | 25.0227 | 24.9938 | 24.1811 | 24.18 | 24.1773 | 24.1744 | 24.1715 | 24.1686 | 24.1657 | 24.1628 | 24.1597 | 24.1565 | 24.1474 | 24.0567 | 23.9872 | 23.9548 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195
|  | KIDDINGTON | ST |  |  | 25.2787 | 25.1389 | 25.1355 | 25.1303 | 25.1241 | 25.0929 | 25.083 | 25.0801 | 25.077 | 25.074 | 25.0679 | 25.0517 | 25.0351 | 25.0186 | 24.2239 | 24.1811 | 24.18 | 24.1784 | 24.1765 | 24.167 | 24.1576 | 24.1483 | 24.1383 | 24.1285 | 24.1087 | 24.0563 | 24.0027 | 23.9825 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195
|  | KIDDINGTON | FS |  |  | 25.2795 | 25.1411 | 25.1407 | 25.1392 | 25.1374 | 25.1262 | 25.1151 | 25.1008 | 25.0867 | 25.084 | 25.0814 | 25.0748 | 25.0681 | 25.0615 | 24.2242 | 24.1817 | 24.1816 | 24.1812 | 24.1806 | 24.1772 | 24.1738 | 24.1694 | 24.1651 | 24.1609 | 24.1526 | 24.1312 | 24.1094 | 24.088 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195 | 23.9195
BRAMLEY (FLEE) | READING BSP | KIDMORE END | MINIMUM HEADROOM | SU 69953 78205 | YES | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 20.2901 | 20.2553 | 20.1723 | 20.0823 | 19.9931 | 19.9047 | 19.8172 | 19.7304 | 19.6367 | 19.5438 | 19.3608 | 19.0735 | 19.0515 | 19.0515 | 20.2054 | 20.1131 | 19.8937 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639
|  | KIDMORE END | CT |  |  | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 20.2901 | 20.2553 | 20.1723 | 20.0823 | 19.9931 | 19.9047 | 19.8172 | 19.7304 | 19.6367 | 19.5438 | 19.3608 | 19.0735 | 19.0515 | 19.0515 | 20.2054 | 20.1131 | 19.8937 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639
|  | KIDMORE END | LW |  |  | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 20.297 | 20.2724 | 20.2141 | 20.1506 | 20.0876 | 20.025 | 19.9629 | 19.9014 | 19.8351 | 19.7694 | 19.6401 | 19.3801 | 19.0775 | 19.0515 | 20.2236 | 20.1585 | 20.0042 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639
|  | KIDMORE END | ST |  |  | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 20.3084 | 20.3002 | 20.2824 | 20.2554 | 20.2229 | 20.1907 | 20.159 | 20.1276 | 20.0937 | 20.0601 | 19.9948 | 19.8354 | 19.6573 | 19.4776 | 20.2537 | 20.232 | 20.1848 | 20.1135 | 20.0275 | 19.9424 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639 | 19.8639
|  | KIDMORE END | FS |  |  | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 22.8234 | 20.3124 | 20.3109 | 20.3091 | 20.299 | 20.287 | 20.2756 | 20.2642 | 20.2497 | 20.2354 | 20.2214 | 20.1941 | 20.129 | 20.0642 | 19.9941 | 20.2643 | 20.2604 | 20.2555 | 20.2288 | 20.197 | 20.1668 | 20.1369 | 20.0985 | 20.0607 | 20.0236 | 19.9513 | 19.8639 | 19.8639 | 19.8639
BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE | MINIMUM HEADROOM | SU 87551 61530 | YES | 26.316 | 26.3006 | 26.2637 | 26.2149 | 26.1646 | 26.1129 | 26.1017 | 26.1017 | 23.9287 | 23.6172 | 22.9743 | 22.1817 | 21.4726 | 20.7737 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 23.697 | 23.347 | 22.9843 | 22.6174 | 21.86 | 20.8713 | 19.9388 | 19.0334 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 23.9182 | 23.574 | 23.2173 | 22.8566 | 22.1118 | 21.1396 | 20.2227 | 19.3324
|  | KINGS RIDE | CT |  |  | 26.316 | 26.3006 | 26.2637 | 26.2149 | 26.1646 | 26.1129 | 26.1017 | 26.1017 | 23.9287 | 23.6172 | 22.9743 | 22.1817 | 21.4726 | 20.7737 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 23.7695 | 23.4406 | 23.0848 | 22.717 | 21.9564 | 20.8713 | 19.9388 | 19.0334 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 23.9894 | 23.6661 | 23.3162 | 22.9545 | 22.2066 | 21.1396 | 20.2227 | 19.3324
|  | KINGS RIDE | LW |  |  | 26.316 | 26.3006 | 26.2637 | 26.2149 | 26.1646 | 26.1129 | 26.1017 | 26.1017 | 23.9287 | 23.6172 | 22.9743 | 22.1817 | 21.4726 | 20.7737 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 23.697 | 23.347 | 22.9843 | 22.6174 | 21.86 | 20.9263 | 20.091 | 19.2677 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 23.9182 | 23.574 | 23.2173 | 22.8566 | 22.1118 | 21.1937 | 20.3724 | 19.5628
|  | KINGS RIDE | ST |  |  | 26.323 | 26.3176 | 26.3057 | 26.2825 | 26.2548 | 26.2333 | 26.2119 | 26.189 | 26.1638 | 26.1371 | 26.1017 | 26.1017 | 23.6659 | 23.2478 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 23.8255 | 23.1818 | 22.6747 | 22.1822 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 23.4116 | 22.913 | 22.4287
|  | KINGS RIDE | FS |  |  | 26.3257 | 26.3248 | 26.3238 | 26.315 | 26.3048 | 26.2968 | 26.2885 | 26.2783 | 26.2682 | 26.2578 | 26.2357 | 26.1951 | 26.163 | 26.1344 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.829 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488 | 25.7488
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE | MINIMUM HEADROOM | SU 51982 59358 | YES | 10.9662 | 10.9284 | 10.8384 | 10.7409 | 10.6446 | 10.6211 | 10.6105 | 10.6 | 10.5887 | 10.5775 | 10.5554 | 10.5171 | 10.4942 | 7.0012 | 10.5726 | 10.5699 | 10.5634 | 10.5564 | 10.5495 | 10.5427 | 10.5359 | 10.5292 | 10.522 | 10.5148 | 10.5007 | 10.4757 | 6.8574 | 6.3932 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 6.859 | 6.345
|  | KINGSCLERE | CT |  |  | 10.9662 | 10.9284 | 10.8384 | 10.7409 | 10.6446 | 10.6211 | 10.6105 | 10.6 | 10.5887 | 10.5775 | 10.5554 | 10.5171 | 10.4942 | 7.0012 | 10.5726 | 10.5699 | 10.5634 | 10.5564 | 10.5495 | 10.5427 | 10.5359 | 10.5292 | 10.522 | 10.5148 | 10.5007 | 10.4757 | 6.8574 | 6.3932 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 6.859 | 6.345
|  | KINGSCLERE | LW |  |  | 10.9662 | 10.9284 | 10.8384 | 10.7409 | 10.6446 | 10.6211 | 10.6105 | 10.6 | 10.5887 | 10.5775 | 10.5554 | 10.5171 | 10.4942 | 7.0012 | 10.5726 | 10.5699 | 10.5636 | 10.5567 | 10.5498 | 10.5431 | 10.5364 | 10.5298 | 10.5227 | 10.5156 | 10.5016 | 10.4774 | 6.9088 | 6.4661 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 6.916 | 6.4258
|  | KINGSCLERE | ST |  |  | 10.9785 | 10.9576 | 10.9118 | 10.8428 | 10.7598 | 10.72 | 10.6808 | 10.6421 | 10.6268 | 10.6222 | 10.6132 | 10.5901 | 10.5666 | 10.5432 | 10.5735 | 10.572 | 10.5688 | 10.5639 | 10.558 | 10.5552 | 10.5524 | 10.5497 | 10.5467 | 10.5438 | 10.5381 | 10.5235 | 10.5087 | 10.4939 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177
|  | KINGSCLERE | FS |  |  | 10.9897 | 10.9874 | 10.9846 | 10.9683 | 10.9489 | 10.9352 | 10.9216 | 10.904 | 10.8869 | 10.87 | 10.8372 | 10.7557 | 10.6748 | 10.6264 | 10.5743 | 10.5741 | 10.5739 | 10.5728 | 10.5714 | 10.5704 | 10.5695 | 10.5682 | 10.567 | 10.5658 | 10.5635 | 10.5577 | 10.552 | 10.5464 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177 | 10.3177
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY | MINIMUM HEADROOM | SU 37657 67143 | YES | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124
|  | KINTBURY | CT |  |  | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124
|  | KINTBURY | LW |  |  | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124
|  | KINTBURY | ST |  |  | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124
|  | KINTBURY | FS |  |  | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 13.9637 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.3114 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124 | 11.4124
BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL | MINIMUM HEADROOM | SU 82849 79105 | YES | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 17.6175 | 17.6113 | 17.5965 | 17.5805 | 17.5646 | 17.5488 | 17.5332 | 17.5177 | 17.501 | 17.4844 | 17.4518 | 17.3509 | 17.2451 | 17.1405 | 18.6066 | 18.6036 | 18.5964 | 18.5886 | 18.5809 | 18.5732 | 18.5656 | 18.5581 | 18.55 | 18.542 | 18.5261 | 18.4771 | 18.4257 | 18.3749
|  | KNOWL HILL | CT |  |  | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 17.6175 | 17.6113 | 17.5965 | 17.5805 | 17.5646 | 17.5488 | 17.5332 | 17.5177 | 17.501 | 17.4844 | 17.4518 | 17.3509 | 17.2451 | 17.1405 | 18.6066 | 18.6036 | 18.5964 | 18.5886 | 18.5809 | 18.5732 | 18.5656 | 18.5581 | 18.55 | 18.542 | 18.5261 | 18.4771 | 18.4257 | 18.3749
|  | KNOWL HILL | LW |  |  | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 17.62 | 17.6175 | 17.6115 | 17.605 | 17.5985 | 17.592 | 17.5856 | 17.5792 | 17.5723 | 17.5655 | 17.5519 | 17.4546 | 17.3533 | 17.2535 | 18.6078 | 18.6066 | 18.6037 | 18.6005 | 18.5974 | 18.5942 | 18.5911 | 18.588 | 18.5846 | 18.5813 | 18.5748 | 18.5275 | 18.4783 | 18.4298
|  | KNOWL HILL | ST |  |  | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 17.621 | 17.62 | 17.6178 | 17.6145 | 17.6105 | 17.5992 | 17.588 | 17.577 | 17.5651 | 17.5534 | 17.5306 | 17.4738 | 17.416 | 17.3583 | 18.6083 | 18.6078 | 18.6068 | 18.6052 | 18.6032 | 18.5977 | 18.5923 | 18.5869 | 18.5811 | 18.5754 | 18.5644 | 18.5368 | 18.5087 | 18.4807
|  | KNOWL HILL | FS |  |  | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 19.4214 | 17.6216 | 17.6214 | 17.6213 | 17.6204 | 17.6193 | 17.6152 | 17.6112 | 17.606 | 17.6009 | 17.5959 | 17.5862 | 17.5626 | 17.5396 | 17.5176 | 18.6086 | 18.6085 | 18.6084 | 18.608 | 18.6075 | 18.6055 | 18.6035 | 18.601 | 18.5985 | 18.5961 | 18.5914 | 18.5799 | 18.5688 | 18.5581
BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD | MINIMUM HEADROOM | SU 86017 50475 | YES | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 35.8047 | 40.3251 | 40.3176 | 40.3078 | 40.2863 | 40.2619 | 40.2493 | 40.2324 | 40.2135 | 40.194 | 40.1746 | 40.1631 | 35.4404 | 34.5745 | 33.6939 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 36.0636 | 35.1704 | 34.2838
|  | LABURNAM ROAD | CT |  |  | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 35.8047 | 40.3254 | 40.3189 | 40.3103 | 40.2914 | 40.2701 | 40.2592 | 40.2443 | 40.226 | 40.2045 | 40.1829 | 40.1659 | 35.5742 | 34.8808 | 34.2026 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 36.2016 | 35.4863 | 34.7909
|  | LABURNAM ROAD | LW |  |  | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 35.8047 | 40.3251 | 40.3176 | 40.3078 | 40.2863 | 40.2619 | 40.2493 | 40.2324 | 40.2135 | 40.194 | 40.1746 | 40.1631 | 35.4404 | 34.5745 | 33.6939 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 36.0636 | 35.1704 | 34.2838
|  | LABURNAM ROAD | ST |  |  | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 40.3268 | 40.3225 | 40.3172 | 40.3044 | 40.2895 | 40.2786 | 40.2652 | 40.2495 | 40.2311 | 40.2123 | 40.1934 | 36.1828 | 35.5677 | 34.9669 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 36.1949 | 35.5751
|  | LABURNAM ROAD | FS |  |  | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 42.6849 | 40.3283 | 40.3259 | 40.3237 | 40.3179 | 40.3114 | 40.3071 | 40.3018 | 40.2953 | 40.2888 | 40.2822 | 40.2749 | 40.2606 | 40.2497 | 40.2393 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721 | 42.5721
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN | MINIMUM HEADROOM | SU 33280 78217 | YES | 12.213 | 12.2107 | 12.2052 | 12.1992 | 12.1932 | 12.1873 | 12.1813 | 12.1755 | 12.1691 | 12.1627 | 12.1484 | 12.0806 | 12.0086 | 11.9372 | 9.781 | 9.7771 | 9.768 | 9.758 | 9.7481 | 9.7381 | 9.7283 | 9.7185 | 9.7079 | 9.6973 | 9.6734 | 9.5748 | 9.5514 | 7.0769 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609
|  | LAMBOURN | CT |  |  | 12.213 | 12.2107 | 12.2052 | 12.1992 | 12.1932 | 12.1873 | 12.1813 | 12.1755 | 12.1691 | 12.1627 | 12.1498 | 12.0806 | 12.0086 | 11.9372 | 9.7811 | 9.7775 | 9.7688 | 9.7593 | 9.7499 | 9.7405 | 9.7311 | 9.7219 | 9.7119 | 9.7019 | 9.6822 | 9.5794 | 9.5574 | 9.5364 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609
|  | LAMBOURN | LW |  |  | 12.213 | 12.2107 | 12.2052 | 12.1992 | 12.1932 | 12.1873 | 12.1813 | 12.1755 | 12.1691 | 12.1627 | 12.1498 | 12.0806 | 12.0086 | 11.9372 | 9.781 | 9.7771 | 9.768 | 9.758 | 9.7481 | 9.7381 | 9.7283 | 9.7185 | 9.7079 | 9.6973 | 9.6758 | 9.5748 | 9.5514 | 7.0769 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609
|  | LAMBOURN | ST |  |  | 12.2141 | 12.2135 | 12.212 | 12.2098 | 12.2072 | 12.1988 | 12.1906 | 12.1825 | 12.1738 | 12.1652 | 12.1484 | 12.1055 | 12.0618 | 12.0183 | 9.7829 | 9.7818 | 9.7794 | 9.7757 | 9.7713 | 9.7574 | 9.7437 | 9.7302 | 9.7156 | 9.7013 | 9.6734 | 9.6019 | 9.5687 | 9.5545 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609
|  | LAMBOURN | FS |  |  | 12.2145 | 12.2144 | 12.2143 | 12.2137 | 12.2129 | 12.2102 | 12.2075 | 12.204 | 12.2006 | 12.1972 | 12.1907 | 12.1744 | 12.1583 | 12.1427 | 9.7835 | 9.7833 | 9.7831 | 9.7821 | 9.7809 | 9.7763 | 9.7718 | 9.766 | 9.7603 | 9.7547 | 9.7438 | 9.7167 | 9.6899 | 9.6639 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609 | 11.5609
FAWLEY GSP | LANGLEY BSP | LANGLEY | MINIMUM HEADROOM | SU 45158 01418 | YES | 31.7517 | 31.7508 | 31.7484 | 31.7457 | 31.738 | 31.7294 | 31.7198 | 31.7059 | 31.6909 | 31.6737 | 31.6361 | 31.562 | 31.5166 | 31.4838 | 26.1153 | 26.1084 | 26.0905 | 26.0704 | 26.0128 | 25.9485 | 25.8772 | 25.7734 | 25.661 | 25.5823 | 25.4104 | 25.071 | 24.863 | 24.6478 | 28.1588 | 28.1561 | 28.149 | 28.1411 | 28.1184 | 28.0931 | 28.0651 | 28.0242 | 27.98 | 27.9294 | 27.819 | 27.6011 | 27.4675 | 27.3294
|  | LANGLEY | CT |  |  | 31.7517 | 31.7508 | 31.7484 | 31.7457 | 31.738 | 31.7294 | 31.7198 | 31.7059 | 31.6909 | 31.6737 | 31.6361 | 31.562 | 31.5166 | 31.4838 | 26.1154 | 26.1085 | 26.0906 | 26.0704 | 26.0171 | 25.9587 | 25.8992 | 25.8124 | 25.7141 | 25.6194 | 25.4501 | 25.1586 | 24.9656 | 24.7782 | 28.1588 | 28.1561 | 28.149 | 28.1411 | 28.1201 | 28.0972 | 28.0737 | 28.0396 | 28.0009 | 27.9533 | 27.8445 | 27.6573 | 27.5334 | 27.4131
|  | LANGLEY | LW |  |  | 31.7517 | 31.7508 | 31.7484 | 31.7457 | 31.738 | 31.7294 | 31.7198 | 31.7059 | 31.6909 | 31.6737 | 31.6361 | 31.562 | 31.5166 | 31.4838 | 26.1153 | 26.1084 | 26.0905 | 26.0704 | 26.0128 | 25.9485 | 25.8772 | 25.7734 | 25.661 | 25.5823 | 25.4104 | 25.071 | 24.863 | 24.6478 | 28.1588 | 28.1561 | 28.149 | 28.1411 | 28.1184 | 28.0931 | 28.0651 | 28.0242 | 27.98 | 27.9294 | 27.819 | 27.6011 | 27.4675 | 27.3294
|  | LANGLEY | ST |  |  | 31.7521 | 31.7517 | 31.7507 | 31.7493 | 31.7445 | 31.7356 | 31.7267 | 31.7154 | 31.7025 | 31.6875 | 31.6536 | 31.6016 | 31.567 | 31.5334 | 26.1182 | 26.1153 | 26.1083 | 26.0972 | 26.0616 | 25.9952 | 25.9285 | 25.844 | 25.7482 | 25.6454 | 25.4902 | 25.2524 | 25.0936 | 24.9399 | 28.1599 | 28.1588 | 28.156 | 28.1517 | 28.1376 | 28.1115 | 28.0852 | 28.052 | 28.0143 | 27.97 | 27.8703 | 27.7176 | 27.6156 | 27.5169
|  | LANGLEY | FS |  |  | 31.7523 | 31.7523 | 31.7522 | 31.7519 | 31.7501 | 31.7472 | 31.7442 | 31.7399 | 31.7351 | 31.7298 | 31.7181 | 31.696 | 31.683 | 31.672 | 26.1198 | 26.1197 | 26.1194 | 26.1166 | 26.1035 | 26.0822 | 26.0598 | 26.0272 | 25.9918 | 25.9519 | 25.8648 | 25.6994 | 25.625 | 25.5745 | 28.1606 | 28.1605 | 28.1604 | 28.1593 | 28.1541 | 28.1457 | 28.1369 | 28.1241 | 28.1102 | 28.0945 | 28.0602 | 27.9951 | 27.9568 | 27.9244
BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT | MINIMUM HEADROOM | SU 80847 29056 | YES | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 36.6522 | 36.6119 | 36.5359 | 36.4623 | 36.3871 | 36.3122 | 36.2454 | 36.1984 | 36.1492 | 36.1003 | 36.0019 | 35.7441 | 35.5791 | 35.4607 | 38.7386 | 38.7227 | 38.6928 | 38.6638 | 38.6342 | 38.6048 | 38.5754 | 38.5585 | 38.5466 | 38.5347 | 38.5109 | 38.4485 | 38.3818 | 38.3152
|  | LANGLEY COURT | CT |  |  | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 36.6527 | 36.6141 | 36.5391 | 36.4659 | 36.3907 | 36.3153 | 36.2468 | 36.1993 | 36.1506 | 36.1028 | 36.0072 | 35.7451 | 35.5791 | 35.4607 | 38.7387 | 38.7236 | 38.694 | 38.6652 | 38.6356 | 38.606 | 38.576 | 38.5587 | 38.5469 | 38.5353 | 38.5122 | 38.4487 | 38.3818 | 38.3152
|  | LANGLEY COURT | LW |  |  | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 36.6522 | 36.6119 | 36.5359 | 36.4623 | 36.3871 | 36.3122 | 36.2454 | 36.1984 | 36.1492 | 36.1003 | 36.0019 | 35.7441 | 35.5819 | 35.4669 | 38.7386 | 38.7227 | 38.6928 | 38.6638 | 38.6342 | 38.6048 | 38.5754 | 38.5585 | 38.5466 | 38.5347 | 38.5109 | 38.4485 | 38.3834 | 38.3187
|  | LANGLEY COURT | ST |  |  | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 36.6701 | 36.6559 | 36.6355 | 36.6122 | 36.5822 | 36.5348 | 36.4871 | 36.4405 | 36.3909 | 36.3425 | 36.2527 | 36.0919 | 35.9316 | 35.7719 | 38.7456 | 38.74 | 38.732 | 38.7228 | 38.711 | 38.6923 | 38.6736 | 38.6553 | 38.6357 | 38.6167 | 38.5789 | 38.5327 | 38.4939 | 38.4552
|  | LANGLEY COURT | FS |  |  | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 36.6764 | 36.6703 | 36.6655 | 36.6543 | 36.641 | 36.625 | 36.6091 | 36.5891 | 36.5693 | 36.5498 | 36.5113 | 36.4112 | 36.31 | 36.227 | 38.7481 | 38.7457 | 38.7438 | 38.7394 | 38.7341 | 38.7278 | 38.7216 | 38.7137 | 38.7059 | 38.6983 | 38.6831 | 38.6437 | 38.6039 | 38.5654
AXMINSTER | YEOVIL BSP | LARKHILL | MINIMUM HEADROOM | ST 53677 16914 | YES | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 27.6247 | 27.6214 | 27.6136 | 27.6049 | 27.5961 | 27.5871 | 27.5717 | 27.5549 | 27.5368 | 27.5189 | 27.4923 | 27.4923 | 27.4923 | 27.4923 | 29.4077 | 29.4047 | 29.3975 | 29.3895 | 29.3813 | 29.3731 | 29.3589 | 29.3434 | 29.3267 | 29.3102 | 29.2779 | 29.1826 | 29.0366 | 28.8903
|  | LARKHILL | CT |  |  | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 27.625 | 27.6221 | 27.6154 | 27.6079 | 27.6002 | 27.5925 | 27.5846 | 27.5767 | 27.5682 | 27.5598 | 27.5429 | 27.4923 | 27.4923 | 27.4923 | 29.408 | 29.4054 | 29.3992 | 29.3923 | 29.3852 | 29.378 | 29.3708 | 29.3635 | 29.3556 | 29.3478 | 29.3323 | 29.2205 | 29.0901 | 28.958
|  | LARKHILL | LW |  |  | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 27.6247 | 27.6214 | 27.6136 | 27.6049 | 27.5961 | 27.5871 | 27.5781 | 27.5691 | 27.5595 | 27.55 | 27.5311 | 27.4923 | 27.4923 | 27.4923 | 29.4077 | 29.4047 | 29.3975 | 29.3895 | 29.3813 | 29.3731 | 29.3648 | 29.3564 | 29.3476 | 29.3389 | 29.3215 | 29.183 | 29.0366 | 28.8903
|  | LARKHILL | ST |  |  | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 27.6516 | 27.6237 | 27.6196 | 27.6134 | 27.6058 | 27.5887 | 27.5717 | 27.5549 | 27.5368 | 27.5189 | 27.4923 | 27.4923 | 27.4923 | 27.4923 | 29.4326 | 29.4068 | 29.403 | 29.3973 | 29.3903 | 29.3745 | 29.3589 | 29.3434 | 29.3267 | 29.3102 | 29.2779 | 29.1826 | 29.0782 | 28.9742
|  | LARKHILL | FS |  |  | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 30.8294 | 27.6526 | 27.6523 | 27.626 | 27.6246 | 27.623 | 27.6186 | 27.6142 | 27.6086 | 27.603 | 27.5976 | 27.5869 | 27.556 | 27.5193 | 27.4923 | 29.4335 | 29.4332 | 29.4089 | 29.4077 | 29.4061 | 29.4021 | 29.398 | 29.3929 | 29.3878 | 29.3828 | 29.3729 | 29.3444 | 29.3105 | 29.2748
COWLEY GSP | WITNEY BSP | LEAFIELD | MINIMUM HEADROOM | SP 30282 15270 | YES | 18.2613 | 18.2599 | 18.258 | 18.2556 | 18.2526 | 18.2489 | 18.2445 | 18.2393 | 18.2337 | 18.2274 | 18.212 | 18.1571 | 18.0829 | 18.0135 | 14.4722 | 14.4583 | 14.4284 | 14.3967 | 14.3648 | 14.3327 | 14.3005 | 14.2681 | 14.2333 | 14.1979 | 14.1237 | 13.9731 | 13.8265 | 13.6987 | 16.4116 | 16.407 | 16.4 | 16.3934 | 16.3863 | 16.3786 | 16.3703 | 16.3614 | 16.352 | 16.3415 | 16.317 | 16.2482 | 16.1696 | 16.0777
|  | LEAFIELD | CT |  |  | 18.2613 | 18.2599 | 18.258 | 18.2556 | 18.2526 | 18.2489 | 18.2445 | 18.2393 | 18.2337 | 18.2274 | 18.212 | 18.1571 | 18.0829 | 18.0135 | 14.4722 | 14.4583 | 14.4284 | 14.3967 | 14.3648 | 14.3327 | 14.3005 | 14.2681 | 14.2333 | 14.1979 | 14.1237 | 13.9731 | 13.8265 | 13.6987 | 16.4116 | 16.407 | 16.4 | 16.3934 | 16.3863 | 16.3786 | 16.3703 | 16.3614 | 16.352 | 16.3415 | 16.317 | 16.2482 | 16.1696 | 16.0777
|  | LEAFIELD | LW |  |  | 18.2613 | 18.2599 | 18.258 | 18.2556 | 18.2526 | 18.2489 | 18.2445 | 18.2393 | 18.2337 | 18.2274 | 18.212 | 18.1571 | 18.0829 | 18.0135 | 14.4765 | 14.4665 | 14.444 | 14.4194 | 14.3944 | 14.3691 | 14.3435 | 14.3175 | 14.2896 | 14.2613 | 14.1981 | 14.0415 | 13.8989 | 13.771 | 16.416 | 16.4145 | 16.4126 | 16.4101 | 16.407 | 16.4032 | 16.3986 | 16.3932 | 16.3875 | 16.3809 | 16.365 | 16.3083 | 16.2316 | 16.1599
|  | LEAFIELD | ST |  |  | 18.2626 | 18.2621 | 18.2615 | 18.2607 | 18.2598 | 18.2586 | 18.2572 | 18.2557 | 18.2542 | 18.2527 | 18.2494 | 18.2363 | 18.2183 | 18.1983 | 15.0484 | 14.482 | 14.4801 | 14.4774 | 14.4741 | 14.4597 | 14.4453 | 14.4311 | 14.4159 | 14.4009 | 14.3701 | 14.2834 | 14.1907 | 14.0962 | 16.4174 | 16.4168 | 16.4162 | 16.4154 | 16.4145 | 16.4132 | 16.4117 | 16.4101 | 16.4087 | 16.4071 | 16.4037 | 16.3902 | 16.3716 | 16.3509
|  | LEAFIELD | FS |  |  | 18.2628 | 18.2625 | 18.2621 | 18.2616 | 18.261 | 18.2604 | 18.2598 | 18.2591 | 18.2584 | 18.2577 | 18.2561 | 18.2501 | 18.2421 | 18.2332 | 15.049 | 14.4828 | 14.4822 | 14.4798 | 14.477 | 14.472 | 14.4671 | 14.461 | 14.4548 | 14.4488 | 14.4367 | 14.4033 | 14.3669 | 14.3299 | 16.4175 | 16.4172 | 16.4168 | 16.4163 | 16.4157 | 16.4151 | 16.4144 | 16.4137 | 16.413 | 16.4123 | 16.4106 | 16.4044 | 16.3961 | 16.3869
WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK | MINIMUM HEADROOM | TQ 20539 81536 | NO | 29.5232 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 27.7486 | 40.3144 | 40.2804 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 28.4804 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604
|  | LEAMINGTON PARK | CT |  |  | 29.5232 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 27.75 | 40.3177 | 40.2882 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 28.4804 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604
|  | LEAMINGTON PARK | LW |  |  | 29.5232 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 27.7486 | 40.3144 | 40.2804 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 28.4804 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604
|  | LEAMINGTON PARK | ST |  |  | 29.5232 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 27.7536 | 40.3261 | 40.3099 | 40.2853 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 28.4804 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604
|  | LEAMINGTON PARK | FS |  |  | 29.5232 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 27.7575 | 40.3367 | 40.3357 | 40.3297 | 40.3225 | 40.3096 | 40.2968 | 40.28 | 40.2626 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 40.2581 | 28.4804 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604 | 41.0604
MINETY GSP | STRATTON (2 X 60) | LECHLADE | MINIMUM HEADROOM | SP 22074 00496 | YES | 10.2429 | 10.2415 | 11.3946 | 11.3922 | 11.3891 | 11.3854 | 11.381 | 11.3757 | 11.3701 | 11.3636 | 11.348 | 11.2923 | 11.2165 | 11.1445 | 9.2922 | 9.2744 | 9.79 | 9.7467 | 9.7107 | 9.6785 | 9.6691 | 9.6599 | 9.6502 | 9.6398 | 9.6172 | 9.5764 | 7.5872 | 7.1048 | 7.0997 | 7.0679 | 7.5467 | 7.4605 | 7.3694 | 7.2767 | 7.1824 | 7.0889 | 6.9895 | 6.8875 | 6.6824 | 6.2321 | 5.7363 | 5.2457
|  | LECHLADE | CT |  |  | 10.2429 | 10.2415 | 11.3946 | 11.3922 | 11.3891 | 11.3854 | 11.381 | 11.3757 | 11.3701 | 11.3636 | 11.348 | 11.2923 | 11.2165 | 11.1445 | 9.2922 | 9.2744 | 9.7906 | 9.7493 | 9.7132 | 9.6785 | 9.6691 | 9.6599 | 9.6502 | 9.6398 | 9.6172 | 9.5764 | 7.6749 | 7.1601 | 7.0997 | 7.0682 | 7.5533 | 7.4771 | 7.3953 | 7.312 | 7.2273 | 7.1443 | 7.0567 | 6.9677 | 6.7891 | 6.3153 | 5.8018 | 5.2734
|  | LECHLADE | LW |  |  | 10.2429 | 10.2415 | 11.3946 | 11.3922 | 11.3891 | 11.3854 | 11.381 | 11.3757 | 11.3701 | 11.3636 | 11.348 | 11.2923 | 11.2165 | 11.1445 | 9.2938 | 9.276 | 9.79 | 9.7467 | 9.7107 | 9.6895 | 9.6821 | 9.6743 | 9.666 | 9.6572 | 9.6393 | 9.609 | 7.5872 | 7.1048 | 7.1009 | 7.0679 | 7.5467 | 7.4605 | 7.3694 | 7.2767 | 7.1824 | 7.0889 | 6.9895 | 6.8875 | 6.6824 | 6.2321 | 5.7363 | 5.2457
|  | LECHLADE | ST |  |  | 10.2443 | 10.2438 | 11.3981 | 11.3973 | 11.3965 | 11.3952 | 11.3938 | 11.3922 | 11.3908 | 11.3893 | 11.3859 | 11.3726 | 11.3543 | 11.3337 | 9.2999 | 9.2893 | 9.8216 | 9.7876 | 9.7476 | 9.7314 | 9.715 | 9.699 | 9.6933 | 9.6903 | 9.6842 | 9.6638 | 9.6427 | 9.6315 | 7.1117 | 7.092 | 7.6046 | 7.541 | 7.4587 | 7.4178 | 7.3761 | 7.3359 | 7.294 | 7.2518 | 7.1695 | 6.9205 | 6.6583 | 6.3959
|  | LECHLADE | FS |  |  | 10.2444 | 10.2441 | 11.3988 | 11.3983 | 11.3977 | 11.3971 | 11.3964 | 11.3958 | 11.3951 | 11.3943 | 11.3927 | 11.3866 | 11.3785 | 11.3695 | 9.3057 | 9.3043 | 9.8578 | 9.8503 | 9.8409 | 9.8336 | 9.8262 | 9.8172 | 9.8085 | 9.7996 | 9.7824 | 9.7357 | 9.6923 | 9.6779 | 7.1224 | 7.1201 | 7.6724 | 7.6584 | 7.6411 | 7.6276 | 7.6141 | 7.5975 | 7.5813 | 7.565 | 7.5332 | 7.437 | 7.3317 | 7.2236
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD | MINIMUM HEADROOM | SU 43962 77635 | YES | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.0667 | 8.0601 | 8.0445 | 8.0275 | 8.0108 | 7.9943 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711
|  | LECKHAMPSTEAD | CT |  |  | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.0667 | 8.0601 | 8.0445 | 8.0275 | 8.0108 | 7.9943 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711
|  | LECKHAMPSTEAD | LW |  |  | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.069 | 8.0659 | 8.0586 | 8.0507 | 8.0429 | 8.0351 | 8.0274 | 8.0198 | 8.0116 | 8.0035 | 7.9908 | 7.9908 | 7.9908 | 7.9908 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711
|  | LECKHAMPSTEAD | ST |  |  | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.07 | 8.0684 | 8.0648 | 8.0593 | 8.0528 | 8.0472 | 8.0416 | 8.0362 | 8.0303 | 8.0245 | 8.0132 | 7.9908 | 7.9908 | 7.9908 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711
|  | LECKHAMPSTEAD | FS |  |  | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.2475 | 8.0709 | 8.0708 | 8.0706 | 8.0693 | 8.0679 | 8.0659 | 8.064 | 8.0614 | 8.059 | 8.0565 | 8.0518 | 8.0404 | 8.0295 | 8.0192 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711 | 8.0711
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT | MINIMUM HEADROOM | SU 56858 00293 | NO | 34.1952 | 34.1616 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 30.4599 | 30.4252 | 30.3407 | 30.2494 | 30.1558 | 30.0595 | 29.9624 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 31.5127 | 31.499 | 31.4657 | 31.4298 | 31.393 | 31.3551 | 31.3169 | 31.2761 | 31.2299 | 31.1831 | 31.1022 | 30.8659 | 30.7639 | 30.7148
|  | LEE-ON-SOLENT | CT |  |  | 34.1952 | 34.1616 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 30.4632 | 30.4337 | 30.3614 | 30.2837 | 30.204 | 30.1217 | 30.0392 | 29.9501 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 31.5139 | 31.5023 | 31.4739 | 31.4433 | 31.4119 | 31.3796 | 31.3471 | 31.312 | 31.2721 | 31.2311 | 31.1589 | 30.9147 | 30.7828 | 30.7148
|  | LEE-ON-SOLENT | LW |  |  | 34.1952 | 34.1616 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 30.4599 | 30.4252 | 30.3407 | 30.2494 | 30.1558 | 30.0595 | 29.9624 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 31.5127 | 31.499 | 31.4657 | 31.4298 | 31.393 | 31.3551 | 31.3169 | 31.2761 | 31.2299 | 31.1831 | 31.1022 | 30.8659 | 30.7639 | 30.7148
|  | LEE-ON-SOLENT | ST |  |  | 34.2119 | 34.2026 | 34.1812 | 34.1509 | 34.1135 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 30.4772 | 30.4676 | 30.4455 | 30.4141 | 30.3755 | 30.2834 | 30.1921 | 30.0971 | 29.9906 | 29.8825 | 29.8702 | 29.8702 | 29.8702 | 29.8702 | 31.5194 | 31.5157 | 31.507 | 31.4946 | 31.4794 | 31.4432 | 31.4073 | 31.3699 | 31.328 | 31.2855 | 31.2084 | 31.0293 | 30.8547 | 30.7863
|  | LEE-ON-SOLENT | FS |  |  | 34.2159 | 34.2132 | 34.2086 | 34.1931 | 34.1744 | 34.1468 | 34.1192 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 34.1003 | 30.4813 | 30.4785 | 30.4738 | 30.4578 | 30.4384 | 30.4099 | 30.3814 | 30.3443 | 30.3058 | 30.267 | 30.1975 | 30.0417 | 29.8856 | 29.8702 | 31.5211 | 31.52 | 31.5181 | 31.5118 | 31.5042 | 31.493 | 31.4818 | 31.4672 | 31.452 | 31.4367 | 31.4094 | 31.3481 | 31.2867 | 31.2256
LOVEDEAN GSP | HAVANT | LEIGH PARK | MINIMUM HEADROOM | SU 72144 07875 | NO | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 37.8555 | 37.8222 | 37.7846 | 37.7765 | 37.7696 | 37.7626 | 37.7553 | 37.7482 | 37.7399 | 37.731 | 37.7097 | 37.6092 | 37.5005 | 37.3918 | 38.6027 | 38.5995 | 38.5941 | 38.5896 | 38.5857 | 38.5817 | 38.5776 | 38.5736 | 38.569 | 38.564 | 38.552 | 38.4954 | 38.4342 | 38.373
|  | LEIGH PARK | CT |  |  | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 37.8563 | 37.827 | 37.7863 | 37.7791 | 37.7729 | 37.7663 | 37.7586 | 37.7514 | 37.744 | 37.7371 | 37.721 | 37.6352 | 37.5384 | 37.4404 | 38.6027 | 38.6 | 38.5951 | 38.5911 | 38.5876 | 38.5839 | 38.5795 | 38.5754 | 38.5713 | 38.5674 | 38.5583 | 38.51 | 38.4555 | 38.4004
|  | LEIGH PARK | LW |  |  | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 37.8555 | 37.8222 | 37.7846 | 37.7765 | 37.7696 | 37.7626 | 37.7553 | 37.7482 | 37.7399 | 37.731 | 37.7097 | 37.6092 | 37.5005 | 37.3918 | 38.6027 | 38.5995 | 38.5941 | 38.5896 | 38.5857 | 38.5817 | 38.5776 | 38.5736 | 38.569 | 38.564 | 38.552 | 38.4954 | 38.4342 | 38.373
|  | LEIGH PARK | ST |  |  | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 37.863 | 37.8482 | 37.8273 | 37.8096 | 37.7932 | 37.7825 | 37.7751 | 37.768 | 37.7607 | 37.7537 | 37.7383 | 37.6781 | 37.6137 | 37.5506 | 38.6034 | 38.602 | 38.6 | 38.5983 | 38.5968 | 38.593 | 38.5888 | 38.5848 | 38.5807 | 38.5768 | 38.5681 | 38.5342 | 38.4979 | 38.4624
|  | LEIGH PARK | FS |  |  | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 43.8612 | 37.8647 | 37.8572 | 37.8489 | 37.8397 | 37.8311 | 37.8173 | 37.8037 | 37.7882 | 37.7854 | 37.7826 | 37.7767 | 37.7553 | 37.7293 | 37.7011 | 38.6035 | 38.6028 | 38.602 | 38.6012 | 38.6004 | 38.599 | 38.5978 | 38.5962 | 38.5946 | 38.593 | 38.5897 | 38.5777 | 38.563 | 38.5471
BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD | MINIMUM HEADROOM | SU 75372 72019 | YES | 38.9352 | 38.6795 | 38.0711 | 37.4099 | 36.7225 | 36.0248 | 35.3165 | 34.6067 | 33.8492 | 33.1017 | 31.634 | 29.1665 | 26.5584 | 23.9392 | 36.4718 | 36.1602 | 35.4184 | 34.6112 | 33.7799 | 32.9437 | 32.1029 | 31.2674 | 30.3755 | 29.4962 | 27.7651 | 24.8825 | 21.7906 | 18.6959 | 36.5699 | 36.2635 | 35.534 | 34.7404 | 33.9229 | 33.1007 | 32.274 | 31.4523 | 30.5754 | 29.7108 | 28.0085 | 25.1741 | 22.1338 | 19.0908
|  | LITTLE HUNGERFORD | CT |  |  | 38.9352 | 38.6795 | 38.0711 | 37.4099 | 36.7225 | 36.0248 | 35.3165 | 34.6067 | 33.8492 | 33.1017 | 31.634 | 29.1665 | 26.5584 | 23.9392 | 36.4718 | 36.1602 | 35.4184 | 34.6112 | 33.7799 | 32.9437 | 32.1029 | 31.2674 | 30.3755 | 29.4962 | 27.7651 | 24.8825 | 21.7906 | 18.6959 | 36.5699 | 36.2635 | 35.534 | 34.7404 | 33.9229 | 33.1007 | 32.274 | 31.4523 | 30.5754 | 29.7108 | 28.0085 | 25.1741 | 22.1338 | 19.0908
|  | LITTLE HUNGERFORD | LW |  |  | 38.9352 | 38.6795 | 38.0711 | 37.4099 | 36.7225 | 36.0248 | 35.3165 | 34.6067 | 33.8492 | 33.1017 | 31.634 | 29.1665 | 26.5584 | 23.9392 | 36.4777 | 36.175 | 35.4549 | 34.6722 | 33.8585 | 33.0326 | 32.1942 | 31.3539 | 30.4573 | 29.5725 | 27.8351 | 24.9142 | 21.83 | 18.7446 | 36.5756 | 36.278 | 35.5699 | 34.8003 | 34.0002 | 33.1881 | 32.3637 | 31.5374 | 30.6558 | 29.7858 | 28.0774 | 25.2053 | 22.1726 | 19.1387
|  | LITTLE HUNGERFORD | ST |  |  | 39.5474 | 38.9181 | 38.6642 | 38.2795 | 37.7984 | 37.5343 | 37.2662 | 36.9996 | 36.7161 | 36.4382 | 35.8944 | 34.42 | 32.8951 | 31.3816 | 37.2024 | 36.4574 | 36.157 | 35.7015 | 35.1321 | 34.8195 | 34.5021 | 34.1865 | 33.8509 | 33.522 | 32.8782 | 31.133 | 29.3279 | 27.5363 | 37.2632 | 36.5557 | 36.2603 | 35.8124 | 35.2525 | 34.9451 | 34.633 | 34.3227 | 33.9927 | 33.6693 | 33.0363 | 31.3202 | 29.5453 | 27.7836
|  | LITTLE HUNGERFORD | FS |  |  | 42.0381 | 39.1556 | 39.0593 | 38.9491 | 38.8112 | 38.72 | 38.627 | 38.5099 | 38.3952 | 38.2829 | 38.0648 | 37.4777 | 36.8651 | 36.246 | 40.5547 | 36.7386 | 36.6246 | 36.4941 | 36.331 | 36.223 | 36.1129 | 35.9743 | 35.8385 | 35.7056 | 35.4474 | 34.7525 | 34.0273 | 33.2945 | 39.196 | 36.8288 | 36.7193 | 36.5918 | 36.4314 | 36.3252 | 36.2169 | 36.0807 | 35.9471 | 35.8165 | 35.5626 | 34.8793 | 34.1662 | 33.4456
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW | MINIMUM HEADROOM | SU 86037 87794 | NO | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 27.3851 | 26.2362 | 25.1011 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 26.6837 | 26.5696 | 26.4567 | 26.2259 | 25.8466 | 25.4711 | 24.7251 | 23.3296 | 21.8721 | 20.4342 | 26.6062 | 26.4608 | 26.1167 | 25.7448 | 25.3769 | 25.0127 | 24.6525 | 24.2964 | 23.9126 | 23.5326 | 22.7777 | 21.3657 | 19.8909 | 18.436
|  | LITTLE MARLOW | CT |  |  | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 27.3851 | 26.2362 | 25.1011 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 26.6837 | 26.5696 | 26.4567 | 26.2259 | 25.8466 | 25.4711 | 24.7251 | 23.3296 | 21.8721 | 20.4342 | 26.6062 | 26.4608 | 26.1167 | 25.7448 | 25.3769 | 25.0127 | 24.6525 | 24.2964 | 23.9126 | 23.5326 | 22.7777 | 21.3657 | 19.8909 | 18.436
|  | LITTLE MARLOW | LW |  |  | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 27.3851 | 26.2362 | 25.1011 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 26.6667 | 26.5747 | 26.4837 | 26.3487 | 26.036 | 25.4171 | 24.1437 | 22.8102 | 21.4928 | 26.6238 | 26.5047 | 26.2237 | 25.9202 | 25.6199 | 25.3228 | 25.0292 | 24.7386 | 24.4206 | 24.1042 | 23.478 | 22.1895 | 20.8402 | 19.5072
|  | LITTLE MARLOW | ST |  |  | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 28.0216 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 26.6533 | 26.4103 | 25.6545 | 24.8825 | 26.6837 | 26.6519 | 26.5839 | 26.482 | 26.3592 | 26.2062 | 26.0555 | 25.9072 | 25.7473 | 25.5903 | 25.2798 | 24.5042 | 23.7181 | 22.937
|  | LITTLE MARLOW | FS |  |  | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 32.2262 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 29.4005 | 26.6413 | 26.6988 | 26.6923 | 26.685 | 26.6438 | 26.5948 | 26.5412 | 26.4881 | 26.4198 | 26.3528 | 26.2869 | 26.1586 | 25.8434 | 25.5348 | 25.2416
NURSLING GSP | ROWNHAMS | LORDSHILL | MINIMUM HEADROOM | SU 38746 16055 | NO | 28.3384 | 28.3222 | 28.2838 | 28.2435 | 28.2014 | 28.1596 | 28.1164 | 28.0625 | 28.0026 | 27.9432 | 27.8063 | 27.316 | 26.8202 | 26.3243 | 28.5369 | 28.5369 | 28.5369 | 26.6434 | 26.5732 | 26.5035 | 26.4312 | 26.3583 | 26.2816 | 26.2059 | 26.049 | 25.4662 | 24.8711 | 24.2758 | 26.6834 | 26.6603 | 26.5998 | 26.5318 | 26.4614 | 26.3914 | 26.3188 | 26.2455 | 26.1685 | 26.0924 | 25.9349 | 25.3496 | 24.7519 | 24.1541
|  | LORDSHILL | CT |  |  | 28.3384 | 28.3222 | 28.2838 | 28.2435 | 28.2014 | 28.1596 | 28.1164 | 28.0625 | 28.0026 | 27.9432 | 27.8063 | 27.316 | 26.8202 | 26.3243 | 28.5369 | 28.5369 | 28.5369 | 26.6434 | 26.5732 | 26.5035 | 26.4312 | 26.3583 | 26.2816 | 26.2059 | 26.049 | 25.5287 | 24.9706 | 24.4081 | 26.6834 | 26.6603 | 26.5998 | 26.5318 | 26.4614 | 26.3914 | 26.3188 | 26.2455 | 26.1685 | 26.0924 | 25.9349 | 25.4123 | 24.8519 | 24.287
|  | LORDSHILL | LW |  |  | 28.3384 | 28.3222 | 28.2838 | 28.2435 | 28.2014 | 28.1596 | 28.1164 | 28.0625 | 28.0026 | 27.9432 | 27.8063 | 27.316 | 26.8202 | 26.3243 | 28.5369 | 28.5369 | 28.5369 | 26.6498 | 26.5816 | 26.514 | 26.4441 | 26.373 | 26.2977 | 26.223 | 26.0548 | 25.4662 | 24.8711 | 24.2758 | 26.684 | 26.6616 | 26.6037 | 26.5383 | 26.4698 | 26.4019 | 26.3317 | 26.2603 | 26.1847 | 26.1096 | 25.9407 | 25.3496 | 24.7519 | 24.1541
|  | LORDSHILL | ST |  |  | 28.3418 | 28.3299 | 28.3037 | 28.2659 | 28.2194 | 28.1827 | 28.1452 | 28.1076 | 28.0565 | 28.0061 | 27.903 | 27.5915 | 27.2715 | 26.9539 | 28.5369 | 28.5369 | 28.5369 | 26.686 | 26.6108 | 26.5514 | 26.4907 | 26.4299 | 26.3655 | 26.3021 | 26.1724 | 25.797 | 25.4128 | 25.0315 | 26.6887 | 26.6722 | 26.636 | 26.5747 | 26.4991 | 26.4395 | 26.3785 | 26.3174 | 26.2527 | 26.1891 | 26.0589 | 25.6818 | 25.2959 | 24.9131
|  | LORDSHILL | FS |  |  | 28.3481 | 28.3463 | 28.3438 | 28.3347 | 28.3234 | 28.3118 | 28.3 | 28.2851 | 28.2705 | 28.2561 | 28.2278 | 28.1459 | 28.0427 | 27.9247 | 28.5369 | 28.5369 | 28.5369 | 28.5369 | 28.5369 | 28.5369 | 28.5369 | 28.5369 | 26.6934 | 26.6702 | 26.6243 | 26.4919 | 26.3481 | 26.1998 | 26.6974 | 26.695 | 26.6915 | 26.6789 | 26.6632 | 26.6472 | 26.63 | 26.6058 | 26.5821 | 26.5587 | 26.5127 | 26.3797 | 26.2353 | 26.0864
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE | MINIMUM HEADROOM | SU 47334 68495 | YES | 52.3697 | 52.3599 | 52.3382 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 46.5049 | 46.445 | 46.3137 | 46.1568 | 45.9824 | 45.8164 | 45.7053 | 45.6616 | 45.6305 | 45.6052 | 45.5541 | 45.4509 | 45.4509 | 34.7092 | 48.9846 | 48.931 | 48.8135 | 48.6732 | 48.5172 | 48.3895 | 48.3584 | 48.3338 | 48.308 | 48.2824 | 48.231 | 48.2104 | 48.2104 | 48.2104
|  | LOVE LANE | CT |  |  | 52.3697 | 52.3599 | 52.3382 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 46.5062 | 46.4491 | 46.3223 | 46.1722 | 46.0068 | 45.849 | 45.7194 | 45.6762 | 45.638 | 45.6113 | 45.5608 | 45.4509 | 45.4509 | 34.786 | 48.9857 | 48.9347 | 48.8212 | 48.687 | 48.539 | 48.3978 | 48.3663 | 48.342 | 48.3156 | 48.2886 | 48.2377 | 48.2104 | 48.2104 | 48.2104
|  | LOVE LANE | LW |  |  | 52.3697 | 52.3599 | 52.3382 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 46.5049 | 46.445 | 46.3137 | 46.1568 | 45.9824 | 45.8164 | 45.7053 | 45.6616 | 45.6305 | 45.6052 | 45.5541 | 45.4509 | 45.4509 | 34.7092 | 48.9846 | 48.931 | 48.8135 | 48.6732 | 48.5172 | 48.3895 | 48.3584 | 48.3338 | 48.308 | 48.2824 | 48.231 | 48.2104 | 48.2104 | 48.2104
|  | LOVE LANE | ST |  |  | 52.3746 | 52.3699 | 52.3607 | 52.3459 | 52.3268 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 52.3196 | 46.534 | 46.5059 | 46.4503 | 46.3608 | 46.2449 | 46.1538 | 46.0618 | 45.9876 | 45.9068 | 45.8239 | 45.7131 | 45.6131 | 45.5388 | 45.4642 | 49.0107 | 48.9855 | 48.9358 | 48.8557 | 48.752 | 48.6706 | 48.5882 | 48.5219 | 48.4495 | 48.3909 | 48.3628 | 48.2905 | 48.2156 | 48.2104
|  | LOVE LANE | FS |  |  | 52.3779 | 52.3767 | 52.3755 | 52.371 | 52.365 | 52.3595 | 52.3539 | 52.3484 | 52.3431 | 52.3378 | 52.3277 | 52.3196 | 52.3196 | 52.3196 | 46.5543 | 46.5471 | 46.5399 | 46.5122 | 46.4764 | 46.4432 | 46.4091 | 46.3758 | 46.3436 | 46.3118 | 46.2505 | 46.0952 | 45.9378 | 45.7792 | 49.0288 | 49.0223 | 49.016 | 48.9912 | 48.9591 | 48.9294 | 48.8989 | 48.8691 | 48.8403 | 48.8118 | 48.7571 | 48.6181 | 48.4773 | 48.3827
COWLEY GSP | YARNTON BSP | LOVELACE ROAD | MINIMUM HEADROOM | SP 50395 10376 | YES | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 29.2382 | 29.2024 | 29.121 | 29.0219 | 28.931 | 28.8494 | 28.7715 | 28.7149 | 28.649 | 28.5837 | 28.4483 | 28.2832 | 28.1189 | 27.9959 | 31.1522 | 31.1193 | 31.0448 | 30.9539 | 30.8706 | 30.7958 | 30.7223 | 30.6478 | 30.5612 | 30.4752 | 30.4625 | 30.4625 | 30.4625 | 30.4625
|  | LOVELACE ROAD | CT |  |  | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 29.2382 | 29.2024 | 29.121 | 29.0219 | 28.931 | 28.8494 | 28.7715 | 28.7149 | 28.649 | 28.5837 | 28.4483 | 28.2832 | 28.1189 | 27.9959 | 31.1522 | 31.1193 | 31.0448 | 30.9539 | 30.8706 | 30.7958 | 30.7223 | 30.6478 | 30.5612 | 30.4752 | 30.4625 | 30.4625 | 30.4625 | 30.4625
|  | LOVELACE ROAD | LW |  |  | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 29.2462 | 29.2216 | 29.168 | 29.0973 | 29.0349 | 28.9827 | 28.9335 | 28.8851 | 28.8264 | 28.7691 | 28.6758 | 28.5322 | 28.3873 | 28.2448 | 31.1595 | 31.137 | 31.0879 | 31.0231 | 30.9658 | 30.918 | 30.8729 | 30.8285 | 30.7748 | 30.7192 | 30.5964 | 30.4625 | 30.4625 | 30.4625
|  | LOVELACE ROAD | ST |  |  | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 29.2557 | 29.2465 | 29.2289 | 29.197 | 29.1659 | 29.1413 | 29.1175 | 29.0927 | 29.0611 | 29.0296 | 28.9607 | 28.8447 | 28.7476 | 28.6724 | 31.1682 | 31.1598 | 31.1437 | 31.1144 | 31.0859 | 31.0634 | 31.0416 | 31.0188 | 30.9899 | 30.961 | 30.8978 | 30.7915 | 30.691 | 30.5919
|  | LOVELACE ROAD | FS |  |  | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 30.1468 | 29.259 | 29.2563 | 29.2527 | 29.2407 | 29.23 | 29.2198 | 29.21 | 29.1976 | 29.1842 | 29.1704 | 29.1401 | 29.0862 | 29.038 | 28.9942 | 31.1713 | 31.1687 | 31.1654 | 31.1545 | 31.1447 | 31.1353 | 31.1263 | 31.115 | 31.1027 | 31.09 | 31.0623 | 31.0129 | 30.9687 | 30.9286
MANNINGTON GSP | ARNEWOOD | LYMINGTON | MINIMUM HEADROOM | SZ 31720 96856 | YES | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 27.6763 | 26.7888 | -9.7033 | -9.7475 | -9.8613 | -9.9954 | -10.1321 | -10.2837 | -10.4525 | -10.6002 | -10.7328 | -10.8701 | -11.1369 | -12.3985 | -13.7797 | -15.1693 | 23.3784 | 23.3358 | 23.2261 | 23.0969 | 22.9652 | 22.819 | 22.6564 | 22.514 | 22.3862 | 22.2539 | 21.9967 | 20.7809 | 19.4497 | 18.1104
|  | LYMINGTON | CT |  |  | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 27.6763 | 26.7888 | -9.7033 | -9.7475 | -9.8613 | -9.9954 | -10.1321 | -10.2837 | -10.4525 | -10.6002 | -10.7328 | -10.8701 | -11.1369 | -12.3985 | -13.7797 | -15.1693 | 23.3784 | 23.3358 | 23.2261 | 23.0969 | 22.9652 | 22.819 | 22.6564 | 22.514 | 22.3862 | 22.2539 | 21.9967 | 20.7809 | 19.4497 | 18.1104
|  | LYMINGTON | LW |  |  | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 27.6763 | 26.7888 | -9.6993 | -9.7369 | -9.8361 | -9.9559 | -10.0796 | -10.2212 | -10.3885 | -10.5256 | -10.636 | -10.7448 | -10.9586 | -12.2333 | -13.6513 | -15.0928 | 23.3823 | 23.346 | 23.2505 | 23.135 | 23.0157 | 22.8792 | 22.718 | 22.5859 | 22.4795 | 22.3747 | 22.1686 | 20.94 | 19.5734 | 18.1841
|  | LYMINGTON | ST |  |  | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 28.1881 | 27.6493 | -9.6856 | -9.705 | -9.753 | -9.8303 | -9.9233 | -10.1015 | -10.2896 | -10.462 | -10.6303 | -10.8002 | -11.1292 | -11.9497 | -12.82 | -13.6951 | 23.3955 | 23.3768 | 23.3305 | 23.256 | 23.1664 | 22.9947 | 22.8134 | 22.6472 | 22.485 | 22.3213 | 22.0042 | 21.2134 | 20.3746 | 19.5312
|  | LYMINGTON | FS |  |  | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | 89.6313 | -9.6749 | -9.677 | -9.6826 | -9.7044 | -9.73 | -9.7922 | -9.8597 | -9.9351 | -10.0024 | -10.0693 | -10.1995 | -10.5082 | -10.8243 | -11.1535 | 23.4058 | 23.4037 | 23.3984 | 23.3773 | 23.3527 | 23.2927 | 23.2276 | 23.155 | 23.0902 | 23.0257 | 22.9002 | 22.6027 | 22.298 | 21.9807
MELKSHAM GSP | CHIPPENHAM | LYNEHAM | MINIMUM HEADROOM | ST 99348 80481 | YES | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | -15.3252 | -15.3511 | -15.4288 | -15.5149 | -15.6052 | -15.6989 | -15.7696 | -15.8445 | -15.9268 | -16.0105 | -16.1708 | -16.5712 | -16.9852 | -17.3955 | -155.5938 | -155.6242 | -155.7155 | -155.8165 | -155.9224 | -156.0325 | -156.1154 | -156.2033 | -156.2999 | -156.3981 | -156.5863 | -157.0562 | -157.5421 | -158.0236
|  | LYNEHAM | CT |  |  | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | -15.3252 | -15.3511 | -15.4288 | -15.5149 | -15.6052 | -15.6989 | -15.7696 | -15.8445 | -15.9268 | -16.0105 | -16.1708 | -16.5712 | -16.9852 | -17.3955 | -155.5938 | -155.6242 | -155.7155 | -155.8165 | -155.9224 | -156.0325 | -156.1154 | -156.2033 | -156.2999 | -156.3981 | -156.5863 | -157.0562 | -157.5421 | -158.0236
|  | LYNEHAM | LW |  |  | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | -15.3179 | -15.333 | -15.3868 | -15.4478 | -15.5149 | -15.5871 | -15.6322 | -15.678 | -15.7282 | -15.7791 | -15.8821 | -16.2707 | -16.6749 | -17.0776 | -155.5853 | -155.603 | -155.6661 | -155.7377 | -155.8164 | -155.9012 | -155.9542 | -156.0079 | -156.0668 | -156.1266 | -156.2475 | -156.7036 | -157.1779 | -157.6505
|  | LYNEHAM | ST |  |  | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | -15.3099 | -15.3131 | -15.3308 | -15.3541 | -15.3829 | -15.4427 | -15.4869 | -15.5337 | -15.5855 | -15.6383 | -15.7386 | -15.9822 | -16.2241 | -16.4632 | -155.5758 | -155.5796 | -155.6004 | -155.6278 | -155.6616 | -155.7318 | -155.7836 | -155.8386 | -155.8994 | -155.9613 | -156.079 | -156.3649 | -156.6488 | -156.9294
|  | LYNEHAM | FS |  |  | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | 287.2569 | -15.3083 | -15.3088 | -15.3153 | -15.3252 | -15.3366 | -15.359 | -15.3751 | -15.3953 | -15.4158 | -15.436 | -15.476 | -15.572 | -15.6657 | -15.7584 | -155.574 | -155.5746 | -155.5822 | -155.5938 | -155.6072 | -155.6335 | -155.6524 | -155.6761 | -155.7002 | -155.7239 | -155.7708 | -155.8835 | -155.9935 | -156.1022
BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E | MINIMUM HEADROOM | SU 98120 65945 | NO | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 69.1894 | 69.1697 | 69.1384 | 69.1033 | 69.0665 | 69.026 | 68.9828 | 68.9435 | 68.9179 | 68.8914 | 68.8454 | 68.7662 | 68.6937 | 68.6218 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959
|  | M V E E | CT |  |  | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 69.1894 | 69.1697 | 69.1384 | 69.1033 | 69.0665 | 69.026 | 68.9828 | 68.9435 | 68.9179 | 68.8914 | 68.8454 | 68.7662 | 68.6937 | 68.6218 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959
|  | M V E E | LW |  |  | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 69.1907 | 69.1724 | 69.1474 | 69.1183 | 69.0882 | 69.0553 | 69.019 | 68.9901 | 68.9803 | 68.9709 | 68.954 | 68.8852 | 68.8164 | 68.7481 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959
|  | M V E E | ST |  |  | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 69.2017 | 69.1916 | 69.179 | 69.1642 | 69.1479 | 69.1232 | 69.0966 | 69.0727 | 69.0579 | 69.0423 | 69.0159 | 68.9683 | 68.9275 | 68.8871 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959
|  | M V E E | FS |  |  | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 76.9737 | 69.2105 | 69.2038 | 69.1967 | 69.1881 | 69.1798 | 69.1694 | 69.1583 | 69.1482 | 69.1424 | 69.1367 | 69.1257 | 69.1051 | 69.0893 | 69.074 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959 | 66.959
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON | MINIMUM HEADROOM | SY 59138 97747 | YES | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 9.4907 | 9.2159 | 8.9348 | 8.6551 | 9.4888 | 9.4706 | 9.4244 | 9.3716 | 9.3157 | 9.2583 | 9.1993 | 9.1398 | 9.0759 | 9.0119 | 8.8844 | 8.5641 | 8.2364 | 7.9101 | 9.4886 | 9.47 | 9.4231 | 9.3693 | 9.3124 | 9.254 | 9.194 | 9.1334 | 9.0685 | 9.0033 | 8.8736 | 8.5493 | 8.2177 | 7.8875
|  | MAIDEN NEWTON | CT |  |  | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 9.4907 | 9.2159 | 8.9348 | 8.6551 | 9.4906 | 9.4749 | 9.4352 | 9.3896 | 9.3412 | 9.2915 | 9.2404 | 9.1887 | 9.1333 | 9.0777 | 8.9669 | 8.6466 | 8.3181 | 7.9918 | 9.4904 | 9.4745 | 9.4341 | 9.3877 | 9.3385 | 9.2879 | 9.2358 | 9.1833 | 9.1269 | 9.0703 | 8.9575 | 8.6328 | 8.3004 | 7.9702
|  | MAIDEN NEWTON | LW |  |  | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 9.4907 | 9.2159 | 8.9348 | 8.6551 | 9.4888 | 9.4706 | 9.4244 | 9.3716 | 9.3157 | 9.2583 | 9.1993 | 9.1398 | 9.0759 | 9.0119 | 8.8844 | 8.5641 | 8.2364 | 7.9101 | 9.4886 | 9.47 | 9.4231 | 9.3693 | 9.3124 | 9.254 | 9.194 | 9.1334 | 9.0685 | 9.0033 | 8.8736 | 8.5493 | 8.2177 | 7.8875
|  | MAIDEN NEWTON | ST |  |  | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 9.4713 | 9.2898 | 9.1096 | 9.494 | 9.4832 | 9.4583 | 9.4196 | 9.3712 | 9.3316 | 9.2913 | 9.2507 | 9.2069 | 9.163 | 9.0758 | 8.862 | 8.6503 | 8.4402 | 9.4938 | 9.4829 | 9.4575 | 9.4182 | 9.3689 | 9.3287 | 9.2876 | 9.2463 | 9.2017 | 9.1571 | 9.0684 | 8.8508 | 8.6366 | 8.4239
|  | MAIDEN NEWTON | FS |  |  | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 11.0968 | 9.4997 | 9.4988 | 9.4972 | 9.4889 | 9.4785 | 9.4666 | 9.4544 | 9.4389 | 9.4235 | 9.408 | 9.3772 | 9.3012 | 9.2263 | 9.1528 | 9.4997 | 9.4988 | 9.4972 | 9.4887 | 9.4781 | 9.466 | 9.4536 | 9.4379 | 9.4222 | 9.4064 | 9.3751 | 9.2977 | 9.2215 | 9.1467
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD | MINIMUM HEADROOM | SU 86485 79800 | YES | 35.9796 | 35.8102 | 35.4194 | 34.9955 | 34.5351 | 34.0643 | 33.5396 | 32.9836 | 32.4001 | 31.8399 | 30.9532 | 29.4372 | 27.8388 | 26.2409 | 42.9879 | 42.8253 | 42.6815 | 42.577 | 42.5285 | 42.479 | 42.4238 | 42.3653 | 42.3075 | 42.3075 | 42.3075 | 34.5136 | 32.6307 | 30.7484 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 34.44 | 32.6121 | 30.7848
|  | MAIDENHEAD | CT |  |  | 35.9796 | 35.8102 | 35.4194 | 34.9955 | 34.5351 | 34.0643 | 33.5396 | 32.9836 | 32.4001 | 31.8399 | 30.9532 | 29.4372 | 27.8388 | 26.2409 | 42.9994 | 42.8379 | 42.7059 | 42.5884 | 42.5447 | 42.5002 | 42.4516 | 42.4001 | 42.3453 | 42.3075 | 42.3075 | 34.9932 | 33.0614 | 31.1379 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 34.9055 | 33.0302 | 31.1629
|  | MAIDENHEAD | LW |  |  | 35.9796 | 35.8102 | 35.4194 | 34.9955 | 34.5351 | 34.0643 | 33.5396 | 32.9836 | 32.4001 | 31.8399 | 30.9532 | 29.4372 | 27.8388 | 26.2409 | 42.9879 | 42.8253 | 42.6815 | 42.577 | 42.5285 | 42.479 | 42.4238 | 42.3653 | 42.3075 | 42.3075 | 42.3075 | 34.5136 | 32.6307 | 30.7484 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 34.44 | 32.6121 | 30.7848
|  | MAIDENHEAD | ST |  |  | 36.0539 | 35.9909 | 35.8594 | 35.6642 | 35.4065 | 35.2033 | 34.9742 | 34.7264 | 34.461 | 34.196 | 33.7927 | 32.8406 | 31.8907 | 30.9471 | 43.0708 | 42.9998 | 42.8604 | 42.7716 | 42.6768 | 42.602 | 42.5747 | 42.5486 | 42.5207 | 42.4928 | 42.4504 | 42.3502 | 42.3075 | 42.3075 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645
|  | MAIDENHEAD | FS |  |  | 36.0853 | 36.0724 | 36.0574 | 35.9911 | 35.9026 | 35.8282 | 35.7418 | 35.6324 | 35.5225 | 35.4158 | 35.2525 | 34.8656 | 34.4904 | 34.1189 | 43.1076 | 43.0925 | 43.075 | 43.0001 | 42.9062 | 42.8319 | 42.8001 | 42.7599 | 42.7195 | 42.6802 | 42.6201 | 42.5633 | 42.5238 | 42.4847 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645 | 43.2645
MELKSHAM GSP | CHIPPENHAM | MALMESBURY | MINIMUM HEADROOM | ST 92288 87493 | YES | 9.4352 | 9.3265 | 9.0908 | 8.8323 | 8.5987 | 8.3652 | 8.1318 | 7.8983 | 7.6438 | 7.3897 | 6.8837 | 6.104 | 5.2922 | 4.4844 | 21.406 | 21.3233 | 21.2627 | 21.247 | 21.2327 | 21.2183 | 21.2036 | 21.1889 | 21.1731 | 21.1576 | 21.127 | 21.0775 | 21.0262 | 9.2232 | 20.0747 | 20.058 | 20.0211 | 19.9808 | 19.944 | 19.9069 | 19.8692 | 19.8314 | 19.7907 | 19.7544 | 19.7544 | 19.7544 | 8.9654 | 8.2231
|  | MALMESBURY | CT |  |  | 9.4352 | 9.3265 | 9.0908 | 8.8323 | 8.5987 | 8.3652 | 8.1318 | 7.8983 | 7.6438 | 7.3897 | 6.8837 | 6.104 | 5.2922 | 4.4844 | 21.406 | 21.3233 | 21.2627 | 21.247 | 21.2327 | 21.2183 | 21.2036 | 21.1889 | 21.1731 | 21.1576 | 21.127 | 21.0775 | 21.0262 | 9.2232 | 20.0747 | 20.058 | 20.0211 | 19.9808 | 19.944 | 19.9069 | 19.8692 | 19.8314 | 19.7907 | 19.7544 | 19.7544 | 19.7544 | 8.9654 | 8.2231
|  | MALMESBURY | LW |  |  | 9.4352 | 9.3265 | 9.0908 | 8.8323 | 8.5987 | 8.3652 | 8.1318 | 7.8983 | 7.6438 | 7.3897 | 6.8837 | 6.104 | 5.2922 | 4.4844 | 21.408 | 21.3249 | 21.2632 | 21.2478 | 21.2339 | 21.22 | 21.2061 | 21.1922 | 21.177 | 21.1619 | 21.1318 | 21.0854 | 21.0371 | 9.3857 | 20.075 | 20.0584 | 20.0223 | 19.9828 | 19.947 | 19.9113 | 19.8756 | 19.8399 | 19.8009 | 19.7621 | 19.7544 | 19.7544 | 9.1237 | 8.4209
|  | MALMESBURY | ST |  |  | 9.4659 | 9.4056 | 9.2854 | 9.1082 | 8.9114 | 8.8278 | 8.7407 | 8.6525 | 8.5573 | 8.466 | 8.2854 | 7.8188 | 7.3531 | 6.8925 | 21.438 | 21.3792 | 21.2989 | 21.2642 | 21.2525 | 21.2475 | 21.2423 | 21.2371 | 21.2314 | 21.226 | 21.2152 | 21.1875 | 21.1597 | 21.1323 | 20.0814 | 20.0705 | 20.0521 | 20.025 | 19.9949 | 19.9821 | 19.9687 | 19.9553 | 19.9407 | 19.9267 | 19.8991 | 19.8277 | 19.7565 | 19.7544
|  | MALMESBURY | FS |  |  | 9.4935 | 9.4811 | 9.4672 | 9.4207 | 9.3738 | 9.3432 | 9.3124 | 9.2735 | 9.2347 | 9.1961 | 9.1194 | 8.9312 | 8.7441 | 8.5599 | 21.4648 | 21.4528 | 21.4392 | 21.3939 | 21.3547 | 21.3354 | 21.316 | 21.2914 | 21.2718 | 21.2695 | 21.2649 | 21.2537 | 21.2425 | 21.2316 | 20.0991 | 20.0911 | 20.0822 | 20.0728 | 20.0656 | 20.0609 | 20.0562 | 20.0503 | 20.0443 | 20.0384 | 20.0267 | 19.9979 | 19.9693 | 19.9411
MINETY GSP | SWINDON BSP | MANCHESTER ROAD | MINIMUM HEADROOM | SU 15254 85130 | YES | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 36.2041 | 34.9673 | 33.7087 | 39.9939 | 39.9691 | 39.9288 | 39.8909 | 39.8537 | 39.816 | 36.7867 | 36.5622 | 36.2604 | 35.9291 | 35.4641 | 34.0111 | 32.4956 | 30.9849 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 36.6732 | 36.2061 | 34.7469 | 33.225 | 31.7078
|  | MANCHESTER ROAD | CT |  |  | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 36.2041 | 34.9673 | 33.7087 | 39.995 | 39.973 | 39.9363 | 39.9022 | 39.8678 | 39.8316 | 36.8848 | 36.66 | 36.374 | 36.0654 | 35.6188 | 34.2926 | 32.8811 | 31.473 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 36.81 | 36.3615 | 35.0297 | 33.6121 | 32.198
|  | MANCHESTER ROAD | LW |  |  | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 36.2041 | 34.9673 | 33.7087 | 39.9939 | 39.9691 | 39.9288 | 39.8909 | 39.8537 | 39.816 | 36.7867 | 36.5622 | 36.2604 | 35.9291 | 35.4641 | 34.0111 | 32.4956 | 30.9849 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 36.6732 | 36.2061 | 34.7469 | 33.225 | 31.7078
|  | MANCHESTER ROAD | ST |  |  | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 36.5769 | 35.8452 | 40.0019 | 39.9885 | 39.969 | 39.9462 | 39.9191 | 39.8916 | 39.8629 | 39.8356 | 36.933 | 36.7028 | 36.3652 | 35.4357 | 34.4875 | 33.5525 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 36.1777 | 35.2254 | 34.2864
|  | MANCHESTER ROAD | FS |  |  | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 41.1233 | 40.0081 | 40.0026 | 39.9978 | 39.9906 | 39.9826 | 39.9732 | 39.9637 | 39.9527 | 39.9395 | 39.9252 | 39.9043 | 39.8496 | 36.8782 | 36.5171 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039 | 39.9039
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON | MINIMUM HEADROOM | SU 07592 05256 | YES | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 18.7891 | 18.7876 | 18.7839 | 18.7798 | 18.7755 | 18.771 | 18.7664 | 18.7606 | 18.7529 | 18.7453 | 18.7303 | 18.6895 | 18.6352 | 18.5814 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407
|  | MANNINGTON | CT |  |  | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 18.7892 | 18.7876 | 18.784 | 18.7799 | 18.7756 | 18.7713 | 18.7668 | 18.7624 | 18.7576 | 18.7528 | 18.7433 | 18.6904 | 18.6361 | 18.5822 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407
|  | MANNINGTON | LW |  |  | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 18.7891 | 18.7876 | 18.7839 | 18.7798 | 18.7755 | 18.771 | 18.7664 | 18.7619 | 18.757 | 18.7521 | 18.7422 | 18.6895 | 18.6352 | 18.5814 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407
|  | MANNINGTON | ST |  |  | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 18.8361 | 18.789 | 18.7875 | 18.7852 | 18.7822 | 18.775 | 18.7678 | 18.7606 | 18.7529 | 18.7453 | 18.7303 | 18.6938 | 18.6576 | 18.6215 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407
|  | MANNINGTON | FS |  |  | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 22.1006 | 18.8368 | 18.8366 | 18.7898 | 18.7891 | 18.7883 | 18.7861 | 18.7838 | 18.781 | 18.7782 | 18.7755 | 18.77 | 18.757 | 18.7444 | 18.7324 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407 | 18.7407
LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET | MINIMUM HEADROOM | SU 86479 04732 | YES | 32.2469 | 32.2296 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 30.2088 | 30.1571 | 30.0478 | 29.9387 | 29.838 | 29.7372 | 29.6361 | 29.5304 | 29.4164 | 29.3017 | 29.1205 | 28.8379 | 18.7895 | 17.5083 | 31.09 | 31.0626 | 31.0046 | 30.9467 | 30.8933 | 30.8398 | 30.7861 | 30.7301 | 30.6696 | 30.6087 | 30.4861 | 30.3779 | 18.7003 | 17.2515
|  | MARKET | CT |  |  | 32.2469 | 32.2296 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 30.2138 | 30.1712 | 30.0806 | 29.9915 | 29.9092 | 29.8248 | 29.7374 | 29.6444 | 29.5457 | 29.4475 | 29.2499 | 28.9393 | 28.6465 | 18.0671 | 31.0927 | 31.0701 | 31.022 | 30.9748 | 30.931 | 30.8863 | 30.8399 | 30.7905 | 30.7382 | 30.6861 | 30.5812 | 30.4164 | 30.3051 | 17.8834
|  | MARKET | LW |  |  | 32.2469 | 32.2296 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 30.2088 | 30.1571 | 30.0478 | 29.9387 | 29.838 | 29.7372 | 29.6361 | 29.5304 | 29.4164 | 29.3017 | 29.1205 | 28.8379 | 18.7895 | 17.5083 | 31.09 | 31.0626 | 31.0046 | 30.9467 | 30.8933 | 30.8398 | 30.7861 | 30.7301 | 30.6696 | 30.6087 | 30.4861 | 30.3779 | 18.7003 | 17.2515
|  | MARKET | ST |  |  | 32.2658 | 32.2435 | 32.2255 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 30.265 | 30.1986 | 30.1447 | 30.0755 | 29.9982 | 29.9313 | 29.8627 | 29.7908 | 29.714 | 29.6376 | 29.4845 | 29.1451 | 28.9573 | 28.7715 | 31.1199 | 31.0846 | 31.056 | 31.0193 | 30.9783 | 30.9428 | 30.9064 | 30.8683 | 30.8275 | 30.7869 | 30.7057 | 30.5125 | 30.4232 | 30.3526
|  | MARKET | FS |  |  | 32.2704 | 32.2676 | 32.264 | 32.257 | 32.2498 | 32.2418 | 32.2338 | 32.2236 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 32.2197 | 30.2789 | 30.2706 | 30.2597 | 30.2388 | 30.2174 | 30.1935 | 30.1696 | 30.1391 | 30.1086 | 30.0779 | 30.0165 | 29.879 | 29.732 | 29.5832 | 31.1272 | 31.1228 | 31.1171 | 31.106 | 31.0946 | 31.082 | 31.0693 | 31.0531 | 31.0369 | 31.0206 | 30.988 | 30.915 | 30.8371 | 30.7581
MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH | MINIMUM HEADROOM | SU 19293 68264 | YES | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 18.7984 | 18.7473 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375
|  | MARLBOROUGH SOUTH | CT |  |  | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 18.7984 | 18.7473 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375
|  | MARLBOROUGH SOUTH | LW |  |  | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 18.7991 | 18.7491 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375
|  | MARLBOROUGH SOUTH | ST |  |  | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 18.9053 | 18.792 | 18.7368 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375
|  | MARLBOROUGH SOUTH | FS |  |  | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 19.8424 | 18.9185 | 18.9158 | 18.824 | 18.8029 | 18.7771 | 18.752 | 18.7267 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 18.7178 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375 | 19.5375
NURSLING GSP | ROWNHAMS | MAYBUSH | MINIMUM HEADROOM | SU 38426 14930 | NO | 210.6056 | 210.605 | 210.6043 | 210.6034 | 210.6022 | 210.6008 | 210.5991 | 210.597 | 210.5946 | 210.5918 | 210.585 | 210.5609 | 210.5247 | 210.4817 | 160.1443 | 160.1366 | 160.1211 | 160.1057 | 160.0896 | 160.0737 | 160.0573 | 160.0401 | 160.0216 | 160.0028 | 159.957 | 159.7527 | 159.5435 | 159.3296 | 137.6975 | 137.6956 | 137.6929 | 137.6901 | 137.6871 | 137.6838 | 137.6803 | 137.6765 | 137.6719 | 137.6668 | 18.9429 | 18.4906 | 18.0351 | 17.5738
|  | MAYBUSH | CT |  |  | 210.6056 | 210.605 | 210.6043 | 210.6034 | 210.6022 | 210.6008 | 210.5991 | 210.597 | 210.5946 | 210.5918 | 210.585 | 210.5609 | 210.5247 | 210.4817 | 160.1443 | 160.1366 | 160.1211 | 160.1057 | 160.0896 | 160.0737 | 160.0573 | 160.0401 | 160.0216 | 160.0028 | 159.9608 | 159.7915 | 159.5941 | 159.3856 | 137.6975 | 137.6956 | 137.6929 | 137.6901 | 137.6871 | 137.6838 | 137.6803 | 137.6765 | 137.6719 | 137.6668 | 18.9672 | 18.6034 | 18.1838 | 17.7457
|  | MAYBUSH | LW |  |  | 210.6056 | 210.605 | 210.6043 | 210.6034 | 210.6022 | 210.6008 | 210.5991 | 210.597 | 210.5946 | 210.5918 | 210.585 | 210.5609 | 210.5247 | 210.4817 | 160.1452 | 160.1377 | 160.1224 | 160.107 | 160.091 | 160.0753 | 160.0594 | 160.0426 | 160.0248 | 160.0068 | 159.957 | 159.7527 | 159.5435 | 159.3296 | 137.6991 | 137.6986 | 137.6978 | 137.6968 | 137.6956 | 137.6942 | 137.6924 | 137.6903 | 137.6878 | 137.6849 | 18.9429 | 18.4906 | 18.0351 | 17.5738
|  | MAYBUSH | ST |  |  | 210.6061 | 210.6059 | 210.6057 | 210.6054 | 210.605 | 210.6045 | 210.604 | 210.6034 | 210.6028 | 210.6022 | 210.6008 | 210.595 | 210.5864 | 210.5754 | 160.1714 | 160.144 | 160.1366 | 160.1269 | 160.115 | 160.1008 | 160.0866 | 160.072 | 160.0566 | 160.0413 | 160.0086 | 159.8948 | 159.7717 | 159.6479 | 137.6997 | 137.6995 | 137.6992 | 137.6989 | 137.6985 | 137.698 | 137.6975 | 137.6969 | 137.6963 | 137.6956 | 137.6941 | 18.7932 | 18.5163 | 18.2398
|  | MAYBUSH | FS |  |  | 210.6062 | 210.606 | 210.6059 | 210.6057 | 210.6055 | 210.6053 | 210.605 | 210.6048 | 210.6045 | 210.6042 | 210.6036 | 210.6012 | 210.598 | 210.5944 | 160.1954 | 160.1487 | 160.1474 | 160.1447 | 160.1414 | 160.137 | 160.1326 | 160.127 | 160.1215 | 160.1161 | 160.1057 | 160.0681 | 160.0214 | 159.9709 | 137.6997 | 137.6996 | 137.6995 | 137.6993 | 137.699 | 137.6988 | 137.6985 | 137.6983 | 137.698 | 137.6977 | 137.6971 | 137.6946 | 137.6913 | 18.9684
MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN | MINIMUM HEADROOM | ST 90170 64096 | YES | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 28.3188 | 28.0764 | 27.8336 | 27.5993 | 27.3379 | 27.0721 | 26.5254 | 25.1235 | 23.5502 | 21.9533 | 26.7 | 26.7 | 26.7 | 26.4461 | 26.1529 | 25.846 | 25.5386 | 25.2419 | 24.9109 | 24.5745 | 23.8823 | 22.1072 | 20.2379 | 18.3567 | 26.7 | 26.7 | 26.7 | 26.4968 | 26.2045 | 25.8986 | 25.5921 | 25.2963 | 24.9664 | 24.6309 | 23.9408 | 22.1711 | 20.3076 | 18.4321
|  | MELKSHAM TOWN | CT |  |  | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 28.3188 | 28.0764 | 27.8336 | 27.5993 | 27.3379 | 27.0721 | 26.5254 | 25.1235 | 23.5502 | 21.9533 | 26.7 | 26.7 | 26.7 | 26.5494 | 26.2962 | 26.0303 | 25.7635 | 25.5109 | 25.2297 | 24.9468 | 24.3672 | 22.7701 | 21.0991 | 19.428 | 26.7 | 26.7 | 26.7 | 26.5999 | 26.3474 | 26.0823 | 25.8164 | 25.5645 | 25.2842 | 25.0022 | 24.4243 | 22.8321 | 21.1662 | 19.5001
|  | MELKSHAM TOWN | LW |  |  | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 28.3188 | 28.0764 | 27.8336 | 27.5993 | 27.3379 | 27.0721 | 26.5254 | 25.1235 | 23.5502 | 21.9533 | 26.7 | 26.7 | 26.7 | 26.4461 | 26.1529 | 25.846 | 25.5386 | 25.2419 | 24.9109 | 24.5745 | 23.8823 | 22.1072 | 20.2379 | 18.3567 | 26.7 | 26.7 | 26.7 | 26.4968 | 26.2045 | 25.8986 | 25.5921 | 25.2963 | 24.9664 | 24.6309 | 23.9408 | 22.1711 | 20.3076 | 18.4321
|  | MELKSHAM TOWN | ST |  |  | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 28.2559 | 28.0962 | 27.9185 | 27.7403 | 27.3775 | 26.4091 | 25.4425 | 24.4559 | 26.7 | 26.7 | 26.7 | 26.7 | 26.4995 | 26.2861 | 26.0733 | 25.8711 | 25.646 | 25.4205 | 24.9611 | 23.735 | 22.5111 | 21.3049 | 26.7 | 26.7 | 26.7 | 26.7 | 26.5501 | 26.3374 | 26.1252 | 25.9236 | 25.6992 | 25.4744 | 25.0163 | 23.794 | 22.5739 | 21.3713
|  | MELKSHAM TOWN | FS |  |  | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 29.7137 | 28.26 | 27.9062 | 27.543 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.6764 | 26.511 | 26.0785 | 25.6304 | 25.1706 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.5615 | 26.1303 | 25.6837 | 25.2253
LOVEDEAN GSP | HAVANT | MEYRICK ROAD | MINIMUM HEADROOM | SU 70849 06469 | NO | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 28.5823 | 28.5595 | 28.5092 | 28.4159 | 28.3069 | 28.2344 | 28.1695 | 28.1012 | 28.0984 | 28.0984 | 28.0984 | 28.0984 | 20.8213 | 19.1746 | 31.9571 | 31.9499 | 31.934 | 31.9046 | 31.8702 | 31.8374 | 31.7985 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723
|  | MEYRICK ROAD | CT |  |  | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 28.5823 | 28.5595 | 28.5092 | 28.4159 | 28.3069 | 28.2344 | 28.1699 | 28.1026 | 28.0984 | 28.0984 | 28.0984 | 28.0984 | 20.9694 | 19.4624 | 31.9571 | 31.9499 | 31.934 | 31.9046 | 31.8702 | 31.8374 | 31.7988 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723
|  | MEYRICK ROAD | LW |  |  | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 28.5845 | 28.564 | 28.5207 | 28.4295 | 28.3191 | 28.2397 | 28.1695 | 28.1012 | 28.0984 | 28.0984 | 28.0984 | 28.0984 | 20.8213 | 19.1746 | 31.9577 | 31.9513 | 31.9376 | 31.9089 | 31.8741 | 31.8405 | 31.7985 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723
|  | MEYRICK ROAD | ST |  |  | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 28.6637 | 28.5838 | 28.5664 | 28.5191 | 28.4588 | 28.3412 | 28.2394 | 28.1664 | 28.0988 | 28.0984 | 28.0984 | 28.0984 | 28.0984 | 21.0786 | 31.9827 | 31.9575 | 31.9521 | 31.9371 | 31.9181 | 31.8811 | 31.8404 | 31.7967 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723 | 31.7723
|  | MEYRICK ROAD | FS |  |  | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 35.344 | 28.668 | 28.5926 | 28.5857 | 28.5627 | 28.5352 | 28.4929 | 28.4448 | 28.3876 | 28.3303 | 28.2724 | 28.2132 | 28.0992 | 28.0984 | 28.0984 | 31.9841 | 31.9603 | 31.9581 | 31.9509 | 31.9422 | 31.9289 | 31.9137 | 31.8957 | 31.8776 | 31.8594 | 31.8247 | 31.7723 | 31.7723 | 31.7723
BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP | MINIMUM HEADROOM | SU 30984 40155 | YES | 4.7991 | 4.7867 | 4.7569 | 4.7246 | 4.6915 | 4.6584 | 4.6245 | 4.5904 | 4.5534 | 4.5165 | 4.4414 | 4.2616 | 4.0635 | 3.8515 | 5.1006 | 5.0803 | 5.0317 | 4.9792 | 4.926 | 4.873 | 4.8191 | 4.7654 | 4.7073 | 4.6495 | 4.5328 | 4.2734 | 3.9906 | 3.6989 | 4.5141 | 4.4938 | 4.4455 | 4.3933 | 4.3404 | 4.2875 | 4.2338 | 4.1802 | 4.1219 | 4.0639 | 3.9464 | 3.682 | 3.39 | 3.0861
|  | MIDDLE WALLOP | CT |  |  | 4.7991 | 4.7867 | 4.7569 | 4.7246 | 4.6915 | 4.6584 | 4.6245 | 4.5904 | 4.5534 | 4.5165 | 4.4414 | 4.2616 | 4.0635 | 3.8515 | 5.1006 | 5.0803 | 5.0317 | 4.9792 | 4.926 | 4.873 | 4.8191 | 4.7654 | 4.7073 | 4.6495 | 4.5328 | 4.2734 | 3.9906 | 3.6989 | 4.5141 | 4.4938 | 4.4455 | 4.3933 | 4.3404 | 4.2875 | 4.2338 | 4.1802 | 4.1219 | 4.0639 | 3.9464 | 3.682 | 3.39 | 3.0861
|  | MIDDLE WALLOP | LW |  |  | 4.7991 | 4.7867 | 4.7569 | 4.7246 | 4.6915 | 4.6584 | 4.6245 | 4.5904 | 4.5534 | 4.5165 | 4.4414 | 4.2616 | 4.0635 | 3.8515 | 5.1033 | 5.0865 | 5.0455 | 5.0013 | 4.956 | 4.9108 | 4.8645 | 4.8183 | 4.7683 | 4.7185 | 4.6178 | 4.3802 | 4.1247 | 3.8582 | 4.517 | 4.5004 | 4.4599 | 4.4161 | 4.3713 | 4.3265 | 4.2807 | 4.2348 | 4.1851 | 4.1354 | 4.0349 | 3.7961 | 3.5364 | 3.2623
|  | MIDDLE WALLOP | ST |  |  | 4.8031 | 4.796 | 4.7801 | 4.7564 | 4.7274 | 4.7097 | 4.6916 | 4.6736 | 4.6544 | 4.6354 | 4.5976 | 4.4976 | 4.3947 | 4.2889 | 5.1087 | 5.099 | 5.077 | 5.0444 | 5.0046 | 4.9803 | 4.9554 | 4.9308 | 4.9045 | 4.8786 | 4.8269 | 4.6913 | 4.5535 | 4.4135 | 4.5224 | 4.5128 | 4.4912 | 4.459 | 4.4197 | 4.3957 | 4.3711 | 4.3467 | 4.3207 | 4.2951 | 4.2438 | 4.1091 | 3.9715 | 3.8308
|  | MIDDLE WALLOP | FS |  |  | 4.807 | 4.8062 | 4.805 | 4.7997 | 4.7931 | 4.7867 | 4.7802 | 4.7721 | 4.764 | 4.7561 | 4.7404 | 4.6999 | 4.6591 | 4.6187 | 5.114 | 5.1129 | 5.1114 | 5.1041 | 5.0951 | 5.0864 | 5.0775 | 5.0663 | 5.0553 | 5.0445 | 5.023 | 4.9679 | 4.9129 | 4.8584 | 4.5277 | 4.5266 | 4.525 | 4.5178 | 4.5089 | 4.5003 | 4.4915 | 4.4804 | 4.4696 | 4.4589 | 4.4376 | 4.3829 | 4.3281 | 4.2739
BRAMLEY (FLEE) | FERNHURST | MIDHURST | MINIMUM HEADROOM | SU 88127 19555 | NO | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 33.3882 | 33.3863 | 33.3816 | 33.3765 | 33.3713 | 33.3662 | 33.3612 | 33.3561 | 33.3505 | 33.3437 | 33.3282 | 33.259 | 33.1745 | 33.0903 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208
|  | MIDHURST | CT |  |  | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 33.3883 | 33.3864 | 33.382 | 33.3771 | 33.3722 | 33.3673 | 33.3625 | 33.3576 | 33.3523 | 33.347 | 33.3365 | 33.2624 | 33.1783 | 33.0937 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208
|  | MIDHURST | LW |  |  | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 33.3882 | 33.3863 | 33.3816 | 33.3765 | 33.3713 | 33.3662 | 33.3612 | 33.3561 | 33.3505 | 33.345 | 33.3341 | 33.259 | 33.1745 | 33.0903 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208
|  | MIDHURST | ST |  |  | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 33.3995 | 33.3885 | 33.387 | 33.3848 | 33.3822 | 33.3746 | 33.3671 | 33.3597 | 33.3516 | 33.3437 | 33.3282 | 33.2817 | 33.2306 | 33.1797 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208
|  | MIDHURST | FS |  |  | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 37.0393 | 33.3998 | 33.3894 | 33.3892 | 33.3885 | 33.3877 | 33.3852 | 33.3828 | 33.3796 | 33.3765 | 33.3734 | 33.3674 | 33.3507 | 33.3314 | 33.3112 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208 | 33.7208
AXMINSTER | YEOVIL BSP | MILBORNE PORT | MINIMUM HEADROOM | ST 67929 19741 | YES | 2.048 | 2.0463 | 2.0426 | 2.0385 | 2.0344 | 2.0217 | 2.0026 | 1.9838 | 1.9634 | 1.9435 | 1.9046 | 1.7997 | 1.675 | 1.5086 | 1.5053 | 1.5032 | 1.4985 | 1.4934 | 1.4881 | 1.4722 | 1.4481 | 1.4243 | 1.3986 | 1.3735 | 1.3243 | 1.192 | 1.0346 | 0.82469 | 0.74114 | 0.73905 | 0.73435 | 0.72921 | 0.72398 | 0.70802 | 0.68388 | 0.66008 | 0.63443 | 0.60926 | 0.5601 | 0.42777 | 0.27033 | 0.060316
|  | MILBORNE PORT | CT |  |  | 2.048 | 2.0463 | 2.0426 | 2.0385 | 2.0344 | 2.0302 | 2.026 | 2.0218 | 2.0174 | 2.013 | 2.0043 | 1.843 | 1.675 | 1.5086 | 1.5053 | 1.5033 | 1.4986 | 1.4935 | 1.4884 | 1.4832 | 1.4779 | 1.4727 | 1.467 | 1.4614 | 1.4503 | 1.2567 | 1.0462 | 0.83643 | 0.74114 | 0.7391 | 0.73444 | 0.72937 | 0.72421 | 0.719 | 0.71378 | 0.7085 | 0.70286 | 0.69727 | 0.68612 | 0.49246 | 0.28187 | 0.072056
|  | MILBORNE PORT | LW |  |  | 2.048 | 2.0463 | 2.0426 | 2.0385 | 2.0344 | 2.0302 | 2.026 | 2.0218 | 2.0174 | 2.013 | 2.0043 | 1.843 | 1.675 | 1.5086 | 1.5053 | 1.5032 | 1.4985 | 1.4934 | 1.4881 | 1.4829 | 1.4776 | 1.4723 | 1.4666 | 1.4611 | 1.4501 | 1.2466 | 1.0346 | 0.82469 | 0.74114 | 0.73905 | 0.73435 | 0.72921 | 0.72398 | 0.71871 | 0.71342 | 0.7081 | 0.70248 | 0.69698 | 0.68595 | 0.48234 | 0.27033 | 0.060316
|  | MILBORNE PORT | ST |  |  | 2.0486 | 2.0478 | 2.0462 | 2.0439 | 2.0411 | 2.0217 | 2.0026 | 1.9838 | 1.9634 | 1.9435 | 1.9046 | 1.7997 | 1.6898 | 1.5804 | 1.506 | 1.5051 | 1.5031 | 1.5002 | 1.4966 | 1.4722 | 1.4481 | 1.4243 | 1.3986 | 1.3735 | 1.3243 | 1.192 | 1.0533 | 0.9153 | 0.74188 | 0.74092 | 0.73894 | 0.73603 | 0.73249 | 0.70802 | 0.68388 | 0.66008 | 0.63443 | 0.60926 | 0.5601 | 0.42777 | 0.28902 | 0.15095
|  | MILBORNE PORT | FS |  |  | 2.0489 | 2.0488 | 2.0486 | 2.0479 | 2.0471 | 2.0412 | 2.0353 | 2.0277 | 2.0203 | 2.013 | 1.9989 | 1.9621 | 1.9234 | 1.8848 | 1.5065 | 1.5063 | 1.506 | 1.5052 | 1.5042 | 1.4967 | 1.4893 | 1.4797 | 1.4704 | 1.4612 | 1.4433 | 1.397 | 1.3481 | 1.2993 | 0.74233 | 0.74213 | 0.74189 | 0.74104 | 0.74003 | 0.73255 | 0.72511 | 0.71558 | 0.70622 | 0.69702 | 0.67914 | 0.63279 | 0.58388 | 0.53513
BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD | MINIMUM HEADROOM | SU 94719 43018 | NO | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 25.3733 | 25.3295 | 25.242 | 25.1593 | 25.0809 | 25.0014 | 24.9196 | 24.8405 | 24.7804 | 24.7666 | 24.7666 | 20.9396 | 19.982 | 19.0315 | 25.9324 | 25.9141 | 25.8777 | 25.8432 | 25.8105 | 25.7855 | 25.7855 | 25.7855 | 25.7855 | 25.7855 | 25.7855 | 21.3513 | 20.4078 | 19.4713
|  | MILFORD | CT |  |  | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 25.3733 | 25.3295 | 25.242 | 25.1593 | 25.0809 | 25.0014 | 24.9196 | 24.8405 | 24.7804 | 24.7666 | 24.7666 | 20.9396 | 19.982 | 19.0315 | 25.9324 | 25.9141 | 25.8777 | 25.8432 | 25.8105 | 25.7855 | 25.7855 | 25.7855 | 25.7855 | 25.7855 | 25.7855 | 21.3513 | 20.4078 | 19.4713
|  | MILFORD | LW |  |  | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 25.3804 | 25.3455 | 25.2829 | 25.228 | 25.1782 | 25.1285 | 25.0788 | 25.0298 | 24.9752 | 24.9203 | 24.8224 | 24.7666 | 20.9122 | 20.0157 | 25.9353 | 25.9208 | 25.8947 | 25.8718 | 25.8511 | 25.8304 | 25.8097 | 25.7892 | 25.7855 | 25.7855 | 25.7855 | 25.7855 | 21.3243 | 20.441
|  | MILFORD | ST |  |  | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 25.3917 | 25.3738 | 25.3451 | 25.3144 | 25.2804 | 25.2412 | 25.2005 | 25.1605 | 25.1178 | 25.0764 | 24.9969 | 24.8144 | 24.7666 | 24.7666 | 25.94 | 25.9326 | 25.9206 | 25.9078 | 25.8937 | 25.8773 | 25.8604 | 25.8437 | 25.8259 | 25.8087 | 25.7855 | 25.7855 | 25.7855 | 25.7855
|  | MILFORD | FS |  |  | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 28.4914 | 25.3994 | 25.3922 | 25.3847 | 25.3743 | 25.3639 | 25.3496 | 25.3355 | 25.318 | 25.3003 | 25.2828 | 25.2489 | 25.169 | 25.0905 | 25.0146 | 25.9433 | 25.9403 | 25.9371 | 25.9328 | 25.9285 | 25.9225 | 25.9166 | 25.9093 | 25.902 | 25.8947 | 25.8805 | 25.8473 | 25.8145 | 25.7855
MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA | MINIMUM HEADROOM | SZ 28252 93347 | YES | 12.5644 | 12.5644 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 22.0979 | 11.8209 | 11.8106 | 23.6345 | 23.5731 | 23.5082 | 23.4973 | 23.4889 | 23.4836 | 23.4716 | 23.4589 | 23.4357 | 23.4296 | 20.5651 | 19.6248 | 12.0483 | 12.0433 | 23.8858 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 20.9908 | 20.0876
|  | MILFORD-ON-SEA | CT |  |  | 12.5644 | 12.5644 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 22.0979 | 11.821 | 11.8109 | 23.6364 | 23.5795 | 23.5137 | 23.5009 | 23.4934 | 23.4874 | 23.4799 | 23.4721 | 23.459 | 23.4296 | 20.573 | 19.6641 | 12.0484 | 12.0434 | 23.8867 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 20.9984 | 20.1254
|  | MILFORD-ON-SEA | LW |  |  | 12.5644 | 12.5644 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 22.0979 | 11.8209 | 11.8106 | 23.6345 | 23.5731 | 23.5082 | 23.4973 | 23.4889 | 23.4836 | 23.4778 | 23.4722 | 23.461 | 23.4296 | 20.5651 | 19.6248 | 12.0483 | 12.0433 | 23.8858 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 20.9908 | 20.0876
|  | MILFORD-ON-SEA | ST |  |  | 12.5644 | 12.5644 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 22.4972 | 11.8236 | 11.8177 | 23.6581 | 23.619 | 23.5701 | 23.5072 | 23.4951 | 23.4841 | 23.4716 | 23.4589 | 23.4357 | 23.4296 | 20.7553 | 20.0952 | 12.0496 | 12.0468 | 23.8972 | 23.8782 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 21.1735 | 20.5395
|  | MILFORD-ON-SEA | FS |  |  | 12.5644 | 12.5644 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 25.7444 | 11.8263 | 11.8255 | 23.6806 | 23.6667 | 23.65 | 23.6257 | 23.6044 | 23.5818 | 23.5593 | 23.5372 | 23.507 | 23.4891 | 23.4709 | 23.4517 | 12.051 | 12.0505 | 23.9082 | 23.9014 | 23.8933 | 23.8815 | 23.8712 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628 | 23.8628
MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood | MINIMUM HEADROOM | SU 14691 05633 | YES | 37.7079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 35.7857 | 35.7576 | 49.5895 | 49.5144 | 49.4378 | 49.3395 | 49.2215 | 49.0976 | 48.9782 | 48.8377 | 48.5525 | 48.2365 | 48.1181 | 48.1022 | 35.4797 | 35.4708 | 49.3494 | 49.3257 | 49.3016 | 49.2706 | 49.2334 | 49.1943 | 49.1567 | 49.1124 | 49.0225 | 48.8045 | 48.5991 | 48.3946
|  | Mill Lane, Ringwood | CT |  |  | 37.7079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 35.7857 | 35.7576 | 49.5895 | 49.5144 | 49.4378 | 49.3395 | 49.2215 | 49.0976 | 48.9782 | 48.8377 | 48.5525 | 48.2365 | 48.1181 | 48.1022 | 35.4797 | 35.4708 | 49.3494 | 49.3257 | 49.3016 | 49.2706 | 49.2334 | 49.1943 | 49.1567 | 49.1124 | 49.0225 | 48.8045 | 48.5991 | 48.3946
|  | Mill Lane, Ringwood | LW |  |  | 37.7079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 35.7922 | 35.774 | 49.6295 | 49.5798 | 49.528 | 49.4513 | 49.3469 | 49.2353 | 49.1332 | 49.0108 | 48.7768 | 48.2778 | 48.1566 | 48.1022 | 35.4817 | 35.476 | 49.362 | 49.3463 | 49.33 | 49.3058 | 49.2729 | 49.2377 | 49.2055 | 49.167 | 49.0932 | 48.8762 | 48.6659 | 48.4518
|  | Mill Lane, Ringwood | ST |  |  | 37.7079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 35.7983 | 35.7883 | 49.6659 | 49.6316 | 49.589 | 49.499 | 49.3964 | 49.2905 | 49.1848 | 49.0643 | 48.8195 | 48.3725 | 48.2439 | 48.1657 | 35.4837 | 35.4805 | 49.3735 | 49.3626 | 49.3492 | 49.3209 | 49.2885 | 49.2551 | 49.2218 | 49.1838 | 49.1067 | 48.9544 | 48.8174 | 48.6817
|  | Mill Lane, Ringwood | FS |  |  | 37.7079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 53.6079 | 35.8345 | 35.8027 | 49.7011 | 49.6931 | 49.6832 | 49.6527 | 49.6164 | 49.5724 | 49.5309 | 49.484 | 49.3926 | 49.2062 | 49.0433 | 48.8828 | 35.4951 | 35.4851 | 49.3846 | 49.382 | 49.3789 | 49.3693 | 49.3579 | 49.344 | 49.3309 | 49.3161 | 49.2873 | 49.2286 | 49.1772 | 49.1266
COWLEY GSP | DRAYTON BSP | MILTON | MINIMUM HEADROOM | SU 49992 92060 | YES | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 46.2342 | 45.4719 | 44.7847 | 44.3448 | 43.7473 | 42.5876 | 41.2949 | 39.9718 | 49.6876 | 49.6088 | 49.6088 | 46.2844 | 45.6263 | 44.8551 | 43.9986 | 43.1006 | 42.2911 | 41.6412 | 40.5944 | 38.8769 | 37.3249 | 35.7788 | 50.443 | 50.443 | 50.443 | 46.3614 | 45.7225 | 44.9739 | 44.1424 | 43.2706 | 42.4848 | 41.8539 | 40.8377 | 39.1703 | 37.649 | 36.1076
|  | MILTON | CT |  |  | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 46.2342 | 45.4719 | 44.7847 | 44.3448 | 43.7473 | 42.5876 | 41.2949 | 39.9718 | 49.6876 | 49.6088 | 49.6088 | 46.2844 | 45.6263 | 44.8654 | 44.0563 | 43.1761 | 42.3197 | 41.6412 | 40.5944 | 38.8769 | 37.3249 | 35.7788 | 50.443 | 50.443 | 50.443 | 46.3614 | 45.7225 | 44.9839 | 44.1984 | 43.344 | 42.5126 | 41.8539 | 40.8377 | 39.1703 | 37.649 | 36.1076
|  | MILTON | LW |  |  | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 46.2342 | 45.4719 | 44.7847 | 44.3448 | 43.7473 | 42.5876 | 41.2949 | 39.9718 | 49.6888 | 49.6088 | 49.6088 | 46.3034 | 45.6328 | 44.8551 | 43.9986 | 43.1006 | 42.2911 | 41.7729 | 41.069 | 39.7028 | 38.1801 | 36.6214 | 50.443 | 50.443 | 50.443 | 46.3799 | 45.7288 | 44.9739 | 44.1424 | 43.2706 | 42.4848 | 41.9817 | 41.2984 | 39.9722 | 38.4939 | 36.9476
|  | MILTON | ST |  |  | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 46.2592 | 45.3039 | 44.4912 | 43.688 | 49.7609 | 49.6774 | 49.6407 | 49.6088 | 49.6088 | 49.6088 | 46.2905 | 45.7224 | 45.1593 | 44.712 | 44.0281 | 42.9027 | 41.9453 | 40.9991 | 50.443 | 50.443 | 50.443 | 50.443 | 50.443 | 50.443 | 46.3674 | 45.8158 | 45.2692 | 44.835 | 44.171 | 43.0785 | 42.1491 | 41.2306
|  | MILTON | FS |  |  | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 51.6463 | 49.7689 | 49.6966 | 49.6821 | 49.6616 | 49.6344 | 49.6088 | 49.6088 | 49.6088 | 49.6088 | 49.6088 | 49.6088 | 46.2001 | 45.8681 | 45.5064 | 50.443 | 50.443 | 50.443 | 50.443 | 50.443 | 50.443 | 50.443 | 50.443 | 50.443 | 50.443 | 50.443 | 46.2796 | 45.9572 | 45.6061
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON | MINIMUM HEADROOM | ST 96164 14520 | NO | 4.7483 | 4.7459 | 4.74 | 4.7334 | 4.7265 | 4.7194 | 4.7121 | 4.7017 | 4.6891 | 4.6765 | 4.6519 | 4.5645 | 4.4524 | 4.3414 | 4.748 | 4.7452 | 4.7382 | 4.7305 | 4.7223 | 4.7139 | 4.7054 | 4.6931 | 4.6782 | 4.6635 | 4.6344 | 4.5282 | 4.3909 | 4.2552 | 4.7481 | 4.7452 | 4.7383 | 4.7305 | 4.7224 | 4.714 | 4.7055 | 4.6933 | 4.6785 | 4.6637 | 4.6348 | 4.5289 | 4.3919 | 4.2567
|  | MINCHINGTON | CT |  |  | 4.7483 | 4.7459 | 4.74 | 4.7334 | 4.7265 | 4.7194 | 4.7121 | 4.7049 | 4.6971 | 4.6892 | 4.6735 | 4.5645 | 4.4524 | 4.3414 | 4.7481 | 4.7452 | 4.7383 | 4.7307 | 4.7226 | 4.7144 | 4.7061 | 4.6978 | 4.6889 | 4.6799 | 4.6619 | 4.5282 | 4.3909 | 4.2552 | 4.7481 | 4.7452 | 4.7384 | 4.7307 | 4.7227 | 4.7145 | 4.7062 | 4.6979 | 4.689 | 4.6801 | 4.6622 | 4.5289 | 4.3919 | 4.2567
|  | MINCHINGTON | LW |  |  | 4.7483 | 4.7459 | 4.74 | 4.7334 | 4.7265 | 4.7194 | 4.7121 | 4.7049 | 4.6971 | 4.6892 | 4.6735 | 4.5645 | 4.4524 | 4.3414 | 4.748 | 4.7452 | 4.7382 | 4.7305 | 4.7223 | 4.7139 | 4.7054 | 4.6968 | 4.6877 | 4.6784 | 4.6599 | 4.5314 | 4.3994 | 4.2686 | 4.7481 | 4.7452 | 4.7383 | 4.7305 | 4.7224 | 4.714 | 4.7055 | 4.697 | 4.6879 | 4.6786 | 4.6602 | 4.5321 | 4.4005 | 4.2701
|  | MINCHINGTON | ST |  |  | 4.7493 | 4.7482 | 4.7457 | 4.742 | 4.7373 | 4.7254 | 4.7135 | 4.7017 | 4.6891 | 4.6765 | 4.6519 | 4.5918 | 4.5321 | 4.4728 | 4.7492 | 4.7479 | 4.745 | 4.7406 | 4.7351 | 4.721 | 4.707 | 4.6931 | 4.6782 | 4.6635 | 4.6344 | 4.5636 | 4.4933 | 4.4235 | 4.7492 | 4.7479 | 4.745 | 4.7406 | 4.7351 | 4.7211 | 4.7071 | 4.6933 | 4.6785 | 4.6637 | 4.6348 | 4.5642 | 4.4941 | 4.4245
|  | MINCHINGTON | FS |  |  | 4.7499 | 4.7497 | 4.7494 | 4.7484 | 4.747 | 4.7424 | 4.7377 | 4.7319 | 4.7261 | 4.7204 | 4.7092 | 4.6822 | 4.6565 | 4.6319 | 4.7498 | 4.7496 | 4.7493 | 4.7481 | 4.7465 | 4.741 | 4.7356 | 4.7287 | 4.7218 | 4.7151 | 4.7019 | 4.6702 | 4.6399 | 4.6109 | 4.7498 | 4.7496 | 4.7493 | 4.7481 | 4.7465 | 4.741 | 4.7356 | 4.7287 | 4.7219 | 4.7152 | 4.702 | 4.6704 | 4.6402 | 4.6113
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE | MINIMUM HEADROOM | SU 01647 91932 | YES | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 19.3328 | 19.2626 | 19.095 | 18.8961 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 13.2727 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 12.8819 | 12.4613 | 12.0457
|  | MINETY VILLAGE | CT |  |  | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 19.34 | 19.2822 | 19.1431 | 18.978 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 13.309 | 12.8388 | 12.4051
|  | MINETY VILLAGE | LW |  |  | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 19.3328 | 19.2626 | 19.095 | 18.8961 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 13.2727 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 12.8819 | 12.4613 | 12.0457
|  | MINETY VILLAGE | ST |  |  | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 19.3537 | 19.3144 | 19.2268 | 19.0947 | 18.9296 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.8562 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733
|  | MINETY VILLAGE | FS |  |  | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 22.1199 | 19.3723 | 19.3632 | 19.3468 | 19.3063 | 19.2567 | 19.2202 | 19.1796 | 19.1322 | 19.0798 | 19.0285 | 18.9178 | 18.8562 | 18.8562 | 18.8562 | 18.0765 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733 | 18.0733
BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER | MINIMUM HEADROOM | SU 62236 64103 | YES | 14.1343 | 14.0731 | 13.9517 | 13.8203 | 13.6901 | 13.561 | 13.4328 | 13.3058 | 13.168 | 13.031 | 12.7573 | 12.1686 | 11.5425 | 10.9023 | 14.258 | 14.223 | 14.2139 | 14.2128 | 14.2116 | 13.2356 | 13.0533 | 12.8746 | 12.681 | 12.4896 | 12.1116 | 11.4016 | 10.6347 | 9.8584 | 14.5456 | 14.5372 | 14.5203 | 14.5019 | 14.4834 | 13.1792 | 12.9993 | 12.823 | 12.6316 | 12.4423 | 12.0681 | 11.3612 | 10.5936 | 9.8137
|  | MORTIMER | CT |  |  | 14.1343 | 14.0731 | 13.9517 | 13.8203 | 13.6901 | 13.561 | 13.4328 | 13.3058 | 13.168 | 13.031 | 12.7573 | 12.1686 | 11.5425 | 10.9023 | 14.258 | 14.223 | 14.2139 | 14.2128 | 14.2116 | 13.2356 | 13.0533 | 12.8746 | 12.681 | 12.4896 | 12.1116 | 11.4016 | 10.6347 | 9.8584 | 14.5456 | 14.5372 | 14.5203 | 14.5019 | 14.4834 | 13.1792 | 12.9993 | 12.823 | 12.6316 | 12.4423 | 12.0681 | 11.3612 | 10.5936 | 9.8137
|  | MORTIMER | LW |  |  | 14.1343 | 14.0731 | 13.9517 | 13.8203 | 13.6901 | 13.561 | 13.4328 | 13.3058 | 13.168 | 13.031 | 12.7573 | 12.1686 | 11.5425 | 10.9023 | 14.2629 | 14.2304 | 14.2156 | 14.2153 | 14.2148 | 14.2143 | 13.2217 | 13.0727 | 12.9111 | 12.7507 | 12.4306 | 11.7454 | 11.0218 | 10.2881 | 14.5472 | 14.5404 | 14.5271 | 14.5127 | 14.4982 | 13.3153 | 13.1671 | 13.0203 | 12.8609 | 12.7026 | 12.3866 | 11.7081 | 10.9886 | 10.2555
|  | MORTIMER | ST |  |  | 14.1538 | 14.1236 | 14.0652 | 13.9775 | 13.8713 | 13.8082 | 13.7456 | 13.6848 | 13.6191 | 13.5547 | 13.4294 | 13.0929 | 12.7426 | 12.3879 | 14.2787 | 14.2552 | 14.227 | 14.216 | 14.2159 | 14.2157 | 14.2155 | 14.2153 | 14.215 | 14.2148 | 13.2173 | 12.8228 | 12.4135 | 12.0004 | 14.5499 | 14.5463 | 14.5399 | 14.5305 | 14.519 | 14.512 | 14.5051 | 14.4983 | 14.4909 | 13.3079 | 13.163 | 12.774 | 12.3697 | 11.9607
|  | MORTIMER | FS |  |  | 14.1663 | 14.1613 | 14.1583 | 14.141 | 14.1149 | 14.0927 | 14.0709 | 14.0428 | 14.0151 | 13.988 | 13.9355 | 13.8006 | 13.6626 | 13.5261 | 14.2917 | 14.2865 | 14.2835 | 14.2676 | 14.249 | 14.239 | 14.2294 | 14.2208 | 14.2157 | 14.2156 | 14.2153 | 14.2145 | 14.2133 | 13.333 | 14.5518 | 14.551 | 14.5505 | 14.548 | 14.5451 | 14.5426 | 14.5402 | 14.537 | 14.534 | 14.5309 | 14.525 | 14.5094 | 14.4928 | 13.2758
MANNINGTON GSP | SALISBURY | NETHERHAMPTON | MINIMUM HEADROOM | SU 12478 29102 | NO | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 17.6276 | 9.443 | 9.294 | 9.1422 | 8.9818 | 8.8126 | 8.6341 | 8.4463 | 8.2787 | 8.1472 | 7.8876 | 7.4409 | 6.9811 | 6.5203 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291
|  | NETHERHAMPTON | CT |  |  | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 17.6282 | 9.462 | 9.3342 | 9.2061 | 9.069 | 8.9198 | 8.7584 | 8.5877 | 8.4321 | 8.3033 | 8.056 | 7.5837 | 7.1247 | 6.669 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291
|  | NETHERHAMPTON | LW |  |  | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 17.6276 | 9.443 | 9.294 | 9.1422 | 8.9818 | 8.8126 | 8.6341 | 8.4463 | 8.2787 | 8.1472 | 7.8876 | 7.4409 | 6.9811 | 6.5203 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291
|  | NETHERHAMPTON | ST |  |  | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 17.6305 | 17.6245 | 9.4455 | 9.3657 | 9.2679 | 9.184 | 9.0919 | 8.9936 | 8.9053 | 8.8349 | 8.7005 | 8.3927 | 8.1086 | 7.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291
|  | NETHERHAMPTON | FS |  |  | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 27.1292 | 17.6323 | 17.6297 | 17.6272 | 17.6235 | 9.4701 | 9.4373 | 9.4033 | 9.3636 | 9.3294 | 9.3028 | 9.2494 | 9.1302 | 9.0218 | 8.9127 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291 | 21.8291
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV | MINIMUM HEADROOM | SU 47615 12025 | NO | 48.4071 | 48.3814 | 48.335 | 48.2844 | 48.233 | 48.1812 | 48.1292 | 48.071 | 48.0074 | 47.9421 | 47.8036 | 47.7127 | 47.7127 | 47.7127 | 43.6218 | 43.5542 | 43.4318 | 43.3093 | 43.1995 | 43.0888 | 42.9778 | 42.8533 | 42.7174 | 42.599 | 42.375 | 42.2348 | 42.1365 | 42.0388 | 43.5761 | 43.5495 | 43.5014 | 43.4488 | 43.3955 | 43.3417 | 43.2878 | 43.2305 | 43.2305 | 43.2305 | 43.2305 | 43.2305 | 43.2305 | 43.2305
|  | NETLEY COMMON 11kV | CT |  |  | 48.4071 | 48.3814 | 48.335 | 48.2844 | 48.233 | 48.1812 | 48.1292 | 48.071 | 48.0074 | 47.9421 | 47.8036 | 47.7127 | 47.7127 | 47.7127 | 43.6279 | 43.5709 | 43.4676 | 43.3556 | 43.2618 | 43.1653 | 43.0733 | 42.9721 | 42.8625 | 42.7504 | 42.5497 | 42.2701 | 42.1807 | 42.0914 | 43.5785 | 43.5561 | 43.5155 | 43.4713 | 43.4257 | 43.3788 | 43.3342 | 43.285 | 43.2318 | 43.2305 | 43.2305 | 43.2305 | 43.2305 | 43.2305
|  | NETLEY COMMON 11kV | LW |  |  | 48.4071 | 48.3814 | 48.335 | 48.2844 | 48.233 | 48.1812 | 48.1292 | 48.071 | 48.0074 | 47.9421 | 47.8036 | 47.7127 | 47.7127 | 47.7127 | 43.6218 | 43.5542 | 43.4318 | 43.3093 | 43.1995 | 43.0888 | 42.9778 | 42.8533 | 42.7174 | 42.599 | 42.375 | 42.2348 | 42.1365 | 42.0388 | 43.5761 | 43.5495 | 43.5014 | 43.4488 | 43.3955 | 43.3417 | 43.2878 | 43.2305 | 43.2305 | 43.2305 | 43.2305 | 43.2305 | 43.2305 | 43.2305
|  | NETLEY COMMON 11kV | ST |  |  | 48.4159 | 48.4006 | 48.3751 | 48.3379 | 48.2927 | 48.243 | 48.1951 | 48.1446 | 48.0899 | 48.0346 | 47.9203 | 47.7127 | 47.7127 | 47.7127 | 43.6452 | 43.6048 | 43.5375 | 43.4395 | 43.3271 | 43.2208 | 43.1184 | 43.0107 | 42.8937 | 42.7755 | 42.5637 | 42.2913 | 42.2251 | 42.1599 | 43.5853 | 43.5695 | 43.543 | 43.5044 | 43.4574 | 43.4058 | 43.3561 | 43.3037 | 43.2469 | 43.2305 | 43.2305 | 43.2305 | 43.2305 | 43.2305
|  | NETLEY COMMON 11kV | FS |  |  | 48.4249 | 48.4207 | 48.4176 | 48.4093 | 48.3997 | 48.3845 | 48.3706 | 48.3517 | 48.3326 | 48.3133 | 48.2746 | 48.1702 | 48.0616 | 47.952 | 43.6689 | 43.6577 | 43.6497 | 43.6277 | 43.6024 | 43.5623 | 43.5256 | 43.4758 | 43.4254 | 43.3744 | 43.2884 | 43.0653 | 42.8333 | 42.615 | 43.5947 | 43.5903 | 43.5871 | 43.5785 | 43.5685 | 43.5527 | 43.5383 | 43.5187 | 43.4989 | 43.4788 | 43.4386 | 43.3303 | 43.2305 | 43.2305
MANNINGTON GSP | ARNEWOOD | NEW MILTON | MINIMUM HEADROOM | SZ 23049 94942 | YES | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 32.0096 | 32.0085 | 32.0058 | 32.0028 | 31.9997 | 31.9929 | 31.9841 | 31.9753 | 31.9658 | 31.9568 | 31.94 | 31.8959 | 31.8481 | 31.7999 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597
|  | NEW MILTON | CT |  |  | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 32.0097 | 32.0086 | 32.006 | 32.0031 | 32.0001 | 31.9964 | 31.992 | 31.9875 | 31.9826 | 31.9784 | 31.9709 | 31.9249 | 31.8711 | 31.816 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597
|  | NEW MILTON | LW |  |  | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 32.0096 | 32.0085 | 32.0058 | 32.0028 | 31.9997 | 31.9957 | 31.9908 | 31.9858 | 31.9803 | 31.976 | 31.9689 | 31.92 | 31.8619 | 31.8012 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597
|  | NEW MILTON | ST |  |  | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 32.0099 | 32.0091 | 32.0073 | 32.0046 | 32.0013 | 31.9929 | 31.9841 | 31.9753 | 31.9658 | 31.9568 | 31.94 | 31.8959 | 31.8481 | 31.7999 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597
|  | NEW MILTON | FS |  |  | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 36.5323 | 32.0104 | 32.0103 | 32.0102 | 32.0097 | 32.0091 | 32.0071 | 32.0049 | 32.0021 | 31.9994 | 31.9968 | 31.9921 | 31.9807 | 31.9678 | 31.9533 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597 | 32.4597
FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT | MINIMUM HEADROOM | SZ 50076 89544 | YES | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 37.0729 | 35.7839 | 41.7795 | 41.7676 | 41.7364 | 41.7094 | 41.7061 | 41.7061 | 41.7061 | 41.7061 | 37.7929 | 37.5866 | 37.2172 | 36.0754 | 34.5361 | 32.9773 | 42.3301 | 42.3271 | 42.3191 | 42.3095 | 42.2965 | 42.2809 | 42.2638 | 42.2464 | 42.2286 | 37.8071 | 37.4485 | 36.3401 | 34.8457 | 33.3325
|  | NEWPORT | CT |  |  | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 37.0729 | 35.7839 | 41.7796 | 41.7679 | 41.7374 | 41.7107 | 41.7061 | 41.7061 | 41.7061 | 41.7061 | 37.9331 | 37.7709 | 37.5013 | 36.2211 | 34.8559 | 33.496 | 42.3301 | 42.3271 | 42.3194 | 42.3102 | 42.2979 | 42.2845 | 42.2699 | 42.2546 | 42.2398 | 37.986 | 37.7242 | 36.4815 | 35.1562 | 33.836
|  | NEWPORT | LW |  |  | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 37.0729 | 35.7839 | 41.7795 | 41.7676 | 41.7364 | 41.7094 | 41.7061 | 41.7061 | 41.7061 | 41.7061 | 37.8458 | 37.694 | 37.4374 | 36.0754 | 34.5361 | 32.9773 | 42.3301 | 42.3271 | 42.3191 | 42.3095 | 42.2965 | 42.282 | 42.2655 | 42.2485 | 42.2328 | 37.9113 | 37.6622 | 36.3401 | 34.8457 | 33.3325
|  | NEWPORT | ST |  |  | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 37.4785 | 36.6726 | 41.7802 | 41.7693 | 41.7437 | 41.7125 | 41.7061 | 41.7061 | 41.7061 | 41.7061 | 37.7929 | 37.5866 | 37.2172 | 36.1656 | 35.0983 | 34.0521 | 42.3303 | 42.3275 | 42.321 | 42.311 | 42.2973 | 42.2809 | 42.2638 | 42.2464 | 42.2286 | 37.8071 | 37.4485 | 36.4276 | 35.3915 | 34.3758
|  | NEWPORT | FS |  |  | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 43.134 | 41.7856 | 41.784 | 41.7808 | 41.7706 | 41.7557 | 41.7351 | 41.7167 | 41.7061 | 41.7061 | 41.7061 | 41.7061 | 41.7061 | 37.8346 | 37.4593 | 42.3316 | 42.3312 | 42.3304 | 42.3278 | 42.324 | 42.3188 | 42.3132 | 42.3065 | 42.3003 | 42.2948 | 42.285 | 42.2596 | 42.2319 | 37.6835
BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY | MINIMUM HEADROOM | SU 93221 52894 | NO | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.4257 | 11.4037 | 11.3602 | 11.3107 | 11.2579 | 11.2013 | 11.1415 | 11.0781 | 11.0098 | 10.939 | 10.8185 | 10.7078 | 10.6059 | 10.5101 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347
|  | NORMANDY | CT |  |  | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.4259 | 11.4058 | 11.3652 | 11.3195 | 11.2713 | 11.2189 | 11.1636 | 11.1029 | 11.0359 | 10.9644 | 10.8379 | 10.7078 | 10.6059 | 10.5101 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347
|  | NORMANDY | LW |  |  | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.4257 | 11.4037 | 11.3602 | 11.3107 | 11.2579 | 11.2013 | 11.1415 | 11.0781 | 11.0098 | 10.939 | 10.8185 | 10.7174 | 10.6236 | 10.5311 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347
|  | NORMANDY | ST |  |  | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.4289 | 11.4155 | 11.3906 | 11.3561 | 11.3151 | 11.287 | 11.2569 | 11.2232 | 11.185 | 11.143 | 11.0691 | 10.9849 | 10.924 | 10.8666 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347
|  | NORMANDY | FS |  |  | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.1123 | 11.4326 | 11.4281 | 11.4217 | 11.4108 | 11.3983 | 11.3867 | 11.3746 | 11.3606 | 11.3456 | 11.3295 | 11.3013 | 11.2653 | 11.2411 | 11.2207 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347 | 10.5347
NURSLING GSP | ROWNHAMS | NORTH BADDESLEY | MINIMUM HEADROOM | SU 38080 20568 | NO | 24.7703 | 24.7273 | 24.6565 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 22.5142 | 22.4185 | 22.2892 | 22.2016 | 22.1234 | 22.0451 | 21.9634 | 21.8813 | 21.7939 | 21.7071 | 21.5307 | 21.4731 | 21.4731 | 21.4731 | 24.7289 | 24.7139 | 24.6892 | 24.6629 | 24.6356 | 24.6082 | 24.5797 | 24.551 | 24.5205 | 24.4902 | 24.4285 | 24.2848 | 24.1357 | 23.9854
|  | NORTH BADDESLEY | CT |  |  | 24.7703 | 24.7273 | 24.6565 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 22.5266 | 22.4508 | 22.3305 | 22.2551 | 22.1897 | 22.1268 | 22.0598 | 21.9952 | 21.9274 | 21.8617 | 21.7278 | 21.4731 | 21.4731 | 21.4731 | 24.7309 | 24.719 | 24.7001 | 24.6802 | 24.6588 | 24.6368 | 24.6134 | 24.5908 | 24.5671 | 24.5442 | 24.4974 | 24.3584 | 24.213 | 24.0667
|  | NORTH BADDESLEY | LW |  |  | 24.7703 | 24.7273 | 24.6565 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 22.5142 | 22.4185 | 22.2892 | 22.2016 | 22.1234 | 22.0451 | 21.9634 | 21.8813 | 21.7939 | 21.7071 | 21.5307 | 21.4731 | 21.4731 | 21.4731 | 24.7289 | 24.7139 | 24.6892 | 24.6629 | 24.6356 | 24.6082 | 24.5797 | 24.551 | 24.5205 | 24.4902 | 24.4285 | 24.2848 | 24.1357 | 23.9854
|  | NORTH BADDESLEY | ST |  |  | 24.8294 | 24.7746 | 24.7537 | 24.7244 | 24.6863 | 24.6411 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 24.5981 | 22.6458 | 22.5238 | 22.4773 | 22.412 | 22.3286 | 22.2688 | 22.2135 | 22.1675 | 22.119 | 22.072 | 21.9767 | 21.7183 | 21.4731 | 21.4731 | 24.7496 | 24.7304 | 24.7232 | 24.7129 | 24.6996 | 24.6838 | 24.6671 | 24.651 | 24.6341 | 24.6177 | 24.5844 | 24.4941 | 24.4037 | 24.3136
|  | NORTH BADDESLEY | FS |  |  | 24.8408 | 24.8333 | 24.8299 | 24.8185 | 24.8045 | 24.7894 | 24.7739 | 24.7547 | 24.7358 | 24.7173 | 24.6801 | 24.5981 | 24.5981 | 24.5981 | 22.6713 | 22.6546 | 22.6469 | 22.6216 | 22.5904 | 22.5567 | 22.5222 | 22.4795 | 22.4374 | 22.3961 | 22.3204 | 22.2017 | 22.1004 | 21.9975 | 24.7536 | 24.751 | 24.7498 | 24.7458 | 24.7409 | 24.7356 | 24.7302 | 24.7235 | 24.7169 | 24.7104 | 24.6974 | 24.663 | 24.6276 | 24.5916
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM | MINIMUM HEADROOM | SU 56427 07430 | NO | 22.4434 | 22.4388 | 22.4305 | 22.423 | 22.4164 | 22.403 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 20.1847 | 20.1559 | 20.0991 | 20.0461 | 19.9964 | 19.9454 | 19.8594 | 19.7601 | 19.6573 | 19.6093 | 19.5392 | 19.3636 | 19.094 | 18.9207 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147
|  | NORTH FAREHAM | CT |  |  | 22.4434 | 22.4388 | 22.4305 | 22.423 | 22.4164 | 22.4097 | 22.4031 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 20.1847 | 20.1559 | 20.0991 | 20.0461 | 19.9964 | 19.9454 | 19.8926 | 19.8399 | 19.7847 | 19.7312 | 19.6447 | 19.3787 | 19.094 | 18.9218 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147
|  | NORTH FAREHAM | LW |  |  | 22.4434 | 22.4388 | 22.4305 | 22.423 | 22.4164 | 22.4097 | 22.4031 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 20.1875 | 20.1616 | 20.1147 | 20.0728 | 20.0353 | 19.9978 | 19.9604 | 19.9231 | 19.8829 | 19.8409 | 19.7568 | 19.3987 | 19.1003 | 18.9207 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147
|  | NORTH FAREHAM | ST |  |  | 22.4444 | 22.4412 | 22.4355 | 22.4287 | 22.4209 | 22.403 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 20.193 | 20.1751 | 20.1434 | 20.1047 | 20.0606 | 19.96 | 19.8594 | 19.7601 | 19.6573 | 19.6093 | 19.5392 | 19.3636 | 19.1712 | 19.0051 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147
|  | NORTH FAREHAM | FS |  |  | 22.4459 | 22.445 | 22.4439 | 22.4426 | 22.4412 | 22.4356 | 22.4299 | 22.4228 | 22.4158 | 22.4089 | 22.3981 | 22.3981 | 22.3981 | 22.3981 | 20.2018 | 20.1964 | 20.1907 | 20.1829 | 20.1753 | 20.1434 | 20.1118 | 20.0716 | 20.032 | 19.9932 | 19.9177 | 19.7211 | 19.5897 | 19.5185 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147 | 20.147
LALEHAM | EAST BEDFONT A | NORTH FELTHAM | MINIMUM HEADROOM | TQ 10987 74875 | NO | 28.3624 | 28.3611 | 28.3582 | 28.3551 | 28.3521 | 28.349 | 28.3459 | 28.3367 | 28.3268 | 28.3162 | 28.2928 | 28.2562 | 28.2188 | 28.1812 | 26.5913 | 26.5853 | 26.5766 | 26.5706 | 26.5646 | 26.5585 | 26.5524 | 26.5344 | 26.5148 | 26.494 | 26.4478 | 26.3757 | 26.3088 | 26.3071 | 27.5492 | 27.5412 | 27.5239 | 27.5054 | 27.4872 | 27.4688 | 27.4501 | 27.3953 | 27.3356 | 27.2724 | 27.1315 | 27.092 | 27.092 | 27.092
|  | NORTH FELTHAM | CT |  |  | 28.3624 | 28.3611 | 28.3582 | 28.3551 | 28.3521 | 28.349 | 28.3459 | 28.3367 | 28.3268 | 28.3162 | 28.2928 | 28.2562 | 28.2188 | 28.1812 | 26.5914 | 26.5856 | 26.5769 | 26.5709 | 26.565 | 26.559 | 26.5529 | 26.537 | 26.5198 | 26.5014 | 26.4576 | 26.4021 | 26.3411 | 26.3071 | 27.5493 | 27.5416 | 27.5246 | 27.5064 | 27.4885 | 27.4701 | 27.4514 | 27.4033 | 27.3507 | 27.2949 | 27.1614 | 27.092 | 27.092 | 27.092
|  | NORTH FELTHAM | LW |  |  | 28.3624 | 28.3611 | 28.3582 | 28.3551 | 28.3521 | 28.349 | 28.3459 | 28.3367 | 28.3268 | 28.3162 | 28.2928 | 28.2562 | 28.2188 | 28.1812 | 26.5913 | 26.5853 | 26.5766 | 26.5706 | 26.5646 | 26.5585 | 26.5524 | 26.5344 | 26.5148 | 26.494 | 26.4478 | 26.3757 | 26.3088 | 26.3071 | 27.5492 | 27.5412 | 27.5239 | 27.5054 | 27.4872 | 27.4688 | 27.4501 | 27.3953 | 27.3356 | 27.2724 | 27.1315 | 27.092 | 27.092 | 27.092
|  | NORTH FELTHAM | ST |  |  | 28.3629 | 28.3622 | 28.361 | 28.3593 | 28.3573 | 28.3538 | 28.3504 | 28.3437 | 28.3363 | 28.3284 | 28.3099 | 28.2866 | 28.2624 | 28.2381 | 26.5936 | 26.5908 | 26.5851 | 26.5789 | 26.5749 | 26.5681 | 26.5613 | 26.5481 | 26.5335 | 26.5181 | 26.4815 | 26.4356 | 26.3879 | 26.3401 | 27.5522 | 27.5484 | 27.541 | 27.5306 | 27.5184 | 27.4978 | 27.4772 | 27.4371 | 27.3927 | 27.3456 | 27.2341 | 27.1059 | 27.092 | 27.092
|  | NORTH FELTHAM | FS |  |  | 28.3632 | 28.363 | 28.3628 | 28.3623 | 28.3617 | 28.3607 | 28.3597 | 28.3571 | 28.3544 | 28.3515 | 28.3448 | 28.3369 | 28.3283 | 28.319 | 26.5951 | 26.5943 | 26.5934 | 26.5911 | 26.5884 | 26.5838 | 26.5797 | 26.5746 | 26.5692 | 26.5634 | 26.5503 | 26.5348 | 26.5177 | 26.4994 | 27.5541 | 27.5531 | 27.5519 | 27.5488 | 27.5453 | 27.5393 | 27.5332 | 27.5177 | 27.5012 | 27.4836 | 27.4438 | 27.3963 | 27.3445 | 27.2887
COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY | MINIMUM HEADROOM | SP 48645 04403 | NO | 7.0779 | 7.0092 | 6.8474 | 6.6723 | 6.4985 | 6.326 | 6.1554 | 5.9864 | 5.8062 | 5.6097 | 5.1895 | 4.4654 | 3.6755 | 2.8701 | 9.45 | 9.4245 | 9.3642 | 9.299 | 9.2344 | 9.1703 | 9.1305 | 6.9871 | 6.7278 | 6.4717 | 5.9442 | 5.0747 | 4.1239 | 3.1695 | 7.058 | 6.9598 | 6.7276 | 6.4766 | 6.2276 | 5.9806 | 5.7363 | 5.4942 | 5.2348 | 4.9787 | 4.451 | 3.5812 | 2.6301 | 1.6754
|  | NORTH HINKSEY | CT |  |  | 7.0779 | 7.0092 | 6.8474 | 6.6723 | 6.4985 | 6.326 | 6.1554 | 5.9864 | 5.8062 | 5.6097 | 5.1895 | 4.4654 | 3.6755 | 2.8701 | 9.45 | 9.4245 | 9.3642 | 9.299 | 9.2344 | 9.1703 | 9.1305 | 6.9871 | 6.7278 | 6.4717 | 5.9442 | 5.0747 | 4.1239 | 3.1695 | 7.058 | 6.9598 | 6.7276 | 6.4766 | 6.2276 | 5.9806 | 5.7363 | 5.4942 | 5.2348 | 4.9787 | 4.451 | 3.5812 | 2.6301 | 1.6754
|  | NORTH HINKSEY | LW |  |  | 7.0779 | 7.0092 | 6.8474 | 6.6723 | 6.4985 | 6.326 | 6.1554 | 5.9864 | 5.8062 | 5.6097 | 5.1895 | 4.4654 | 3.6755 | 2.8701 | 9.453 | 9.4321 | 9.3827 | 9.3294 | 9.2763 | 9.2237 | 9.1717 | 9.1305 | 7.069 | 6.8383 | 6.3449 | 5.4949 | 4.5675 | 3.622 | 7.0697 | 6.989 | 6.799 | 6.5934 | 6.3892 | 6.1866 | 5.9862 | 5.7878 | 5.5762 | 5.3454 | 4.8518 | 4.0015 | 3.0738 | 2.128
|  | NORTH HINKSEY | ST |  |  | 7.1051 | 7.0748 | 7.0093 | 6.9113 | 6.7932 | 6.732 | 6.6716 | 6.6118 | 6.5481 | 6.4859 | 6.3501 | 5.9179 | 5.4616 | 5.0113 | 9.4613 | 9.4521 | 9.4321 | 9.4022 | 9.3662 | 9.3475 | 9.3291 | 9.3109 | 9.2915 | 9.2725 | 9.2311 | 9.1305 | 6.6645 | 6.1357 | 7.1016 | 7.066 | 6.9891 | 6.874 | 6.7353 | 6.6634 | 6.5925 | 6.5222 | 6.4475 | 6.3745 | 6.2149 | 5.7074 | 5.1715 | 4.6426
|  | NORTH HINKSEY | FS |  |  | 7.1208 | 7.1162 | 7.1108 | 7.0828 | 7.0495 | 7.027 | 7.0048 | 6.9765 | 6.949 | 6.9222 | 6.8675 | 6.7085 | 6.5244 | 6.329 | 9.4661 | 9.4647 | 9.4631 | 9.4545 | 9.4444 | 9.4375 | 9.4307 | 9.4221 | 9.4137 | 9.4055 | 9.3889 | 9.3404 | 9.2842 | 9.2246 | 7.12 | 7.1147 | 7.1084 | 7.0755 | 7.0363 | 7.0099 | 6.9838 | 6.9506 | 6.9183 | 6.8868 | 6.8226 | 6.6358 | 6.4196 | 6.1901
MINETY GSP | CIRENCESTER BSP | NORTHLEACH | MINIMUM HEADROOM | SP 10557 14251 | YES | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031
|  | NORTHLEACH | CT |  |  | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031
|  | NORTHLEACH | LW |  |  | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031
|  | NORTHLEACH | ST |  |  | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031
|  | NORTHLEACH | FS |  |  | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 13.2823 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 15.0983 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031 | 14.3031
BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE | MINIMUM HEADROOM | SU 72207 71092 | YES | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 19.5007 | 19.2331 | 18.9691 | 19.67 | 19.6558 | 19.6497 | 19.6375 | 19.6218 | 19.6117 | 19.6117 | 19.6117 | 19.6117 | 18.5575 | 18.2267 | 17.6546 | 17.225 | 16.8012 | 18.6674 | 18.6445 | 18.6061 | 18.5303 | 18.4324 | 18.323 | 18.2022 | 18.07 | 17.9286 | 17.7793 | 17.4446 | 16.8658 | 16.4311 | 16.0022
|  | NORTHUMBERLAND AVENUE | CT |  |  | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 19.5007 | 19.2331 | 18.9691 | 19.6706 | 19.6562 | 19.6504 | 19.6392 | 19.625 | 19.6117 | 19.6117 | 19.6117 | 19.6117 | 18.6265 | 18.2895 | 17.6765 | 17.2554 | 16.8519 | 18.668 | 18.647 | 18.6106 | 18.5411 | 18.4527 | 18.3545 | 18.2524 | 18.1357 | 18.0006 | 17.8492 | 17.5082 | 16.888 | 16.4618 | 16.0535
|  | NORTHUMBERLAND AVENUE | LW |  |  | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 19.5007 | 19.2331 | 18.9691 | 19.67 | 19.6558 | 19.6497 | 19.6375 | 19.6218 | 19.6117 | 19.6117 | 19.6117 | 19.6117 | 18.5575 | 18.2267 | 17.6546 | 17.225 | 16.8012 | 18.6674 | 18.6445 | 18.6061 | 18.5303 | 18.4324 | 18.323 | 18.2022 | 18.07 | 17.9286 | 17.7793 | 17.4446 | 16.8658 | 16.4311 | 16.0022
|  | NORTHUMBERLAND AVENUE | ST |  |  | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 19.7809 | 19.6171 | 19.4624 | 19.6777 | 19.6656 | 19.6559 | 19.6489 | 19.6393 | 19.6255 | 19.6117 | 19.6117 | 19.6117 | 19.6117 | 18.5227 | 18.1045 | 17.8415 | 17.5932 | 18.6752 | 18.663 | 18.6449 | 18.6011 | 18.5415 | 18.4555 | 18.3673 | 18.2697 | 18.1562 | 18.0295 | 17.7441 | 17.321 | 17.0549 | 16.8036
|  | NORTHUMBERLAND AVENUE | FS |  |  | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 21.839 | 19.6834 | 19.6779 | 19.6723 | 19.6568 | 19.6529 | 19.6474 | 19.6416 | 19.6348 | 19.6275 | 19.6197 | 19.6117 | 19.6117 | 19.6117 | 19.6117 | 18.6809 | 18.6754 | 18.6697 | 18.6508 | 18.6265 | 18.5922 | 18.5558 | 18.5133 | 18.4678 | 18.4191 | 18.312 | 18.1392 | 18.022 | 17.9196
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD | MINIMUM HEADROOM | SU 68329 86784 | YES | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 16.851 | 16.8371 | 16.8039 | 16.7678 | 16.7319 | 16.6963 | 16.6611 | 16.6261 | 16.5884 | 16.5509 | 16.4771 | 16.3111 | 16.2031 | 16.1632 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184
|  | NUFFIELD | CT |  |  | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 16.851 | 16.8371 | 16.8039 | 16.7678 | 16.7319 | 16.6963 | 16.6611 | 16.6261 | 16.5884 | 16.5509 | 16.4771 | 16.3111 | 16.2031 | 16.1632 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184
|  | NUFFIELD | LW |  |  | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 16.8584 | 16.8555 | 16.8485 | 16.8408 | 16.8329 | 16.825 | 16.8171 | 16.8092 | 16.8006 | 16.7921 | 16.7753 | 16.6213 | 16.4529 | 16.2851 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184
|  | NUFFIELD | ST |  |  | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 16.8596 | 16.8584 | 16.8558 | 16.8518 | 16.8469 | 16.8279 | 16.8091 | 16.7906 | 16.7705 | 16.7507 | 16.7122 | 16.619 | 16.521 | 16.4227 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184
|  | NUFFIELD | FS |  |  | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 20.2175 | 16.8602 | 16.86 | 16.8598 | 16.8586 | 16.8572 | 16.8505 | 16.8439 | 16.8354 | 16.827 | 16.8188 | 16.8027 | 16.7647 | 16.7282 | 16.6913 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184 | 19.4184
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE | MINIMUM HEADROOM | SU 63496 53664 | YES | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 32.9494 | 32.9408 | 32.9247 | 32.907 | 32.8911 | 32.8743 | 32.8607 | 32.8467 | 32.8316 | 32.817 | 32.7901 | 32.7017 | 32.6041 | 32.5044 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774
|  | OAKRIDGE | CT |  |  | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 32.9494 | 32.9408 | 32.9247 | 32.907 | 32.8911 | 32.8743 | 32.8607 | 32.8467 | 32.8316 | 32.817 | 32.7901 | 32.7017 | 32.6041 | 32.5044 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774
|  | OAKRIDGE | LW |  |  | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 32.9503 | 32.9428 | 32.9302 | 32.916 | 32.9038 | 32.8911 | 32.8828 | 32.8747 | 32.8659 | 32.8573 | 32.8399 | 32.7411 | 32.6377 | 32.5327 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774
|  | OAKRIDGE | ST |  |  | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 32.9531 | 32.9496 | 32.9447 | 32.9384 | 32.9327 | 32.9184 | 32.9063 | 32.894 | 32.8807 | 32.8679 | 32.8441 | 32.7786 | 32.7095 | 32.6396 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774
|  | OAKRIDGE | FS |  |  | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 35.1185 | 32.9545 | 32.9527 | 32.9507 | 32.948 | 32.9459 | 32.9411 | 32.9374 | 32.9328 | 32.9282 | 32.9237 | 32.9153 | 32.8931 | 32.869 | 32.8439 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774 | 33.0774
COWLEY GSP | HEADINGTON BSP | OLD ROAD | MINIMUM HEADROOM | SP 55274 06426 | NO | 28.2932 | 28.2055 | 28.0382 | 27.8521 | 27.6985 | 27.5592 | 27.4225 | 27.2874 | 27.1425 | 27.0007 | 26.7248 | 26.1867 | 25.6414 | 25.1026 | 26.6331 | 26.5297 | 26.3327 | 26.1135 | 25.9325 | 25.7684 | 25.6074 | 25.4482 | 25.2776 | 25.1105 | 24.7855 | 24.1516 | 23.5092 | 22.8529 | 26.6333 | 26.5302 | 26.3338 | 26.1153 | 25.9348 | 25.7713 | 25.6107 | 25.4521 | 25.2819 | 25.1154 | 24.7913 | 24.1593 | 23.5189 | 22.8646
|  | OLD ROAD | CT |  |  | 28.2932 | 28.2055 | 28.0382 | 27.8521 | 27.6985 | 27.5592 | 27.4225 | 27.2874 | 27.1425 | 27.0007 | 26.7248 | 26.1867 | 25.6414 | 25.1026 | 26.6367 | 26.5429 | 26.3602 | 26.1588 | 25.9905 | 25.833 | 25.6697 | 25.5037 | 25.3267 | 25.1612 | 24.8487 | 24.1923 | 23.5184 | 22.8529 | 26.6368 | 26.5434 | 26.3612 | 26.1604 | 25.9927 | 25.8357 | 25.6728 | 25.5073 | 25.3308 | 25.1659 | 24.8543 | 24.2 | 23.5281 | 22.8646
|  | OLD ROAD | LW |  |  | 28.2932 | 28.2055 | 28.0382 | 27.8521 | 27.6985 | 27.5592 | 27.4225 | 27.2874 | 27.1425 | 27.0007 | 26.7248 | 26.1867 | 25.6414 | 25.1026 | 26.6331 | 26.5297 | 26.3327 | 26.1135 | 25.9325 | 25.7684 | 25.6074 | 25.4482 | 25.2776 | 25.1105 | 24.7855 | 24.1516 | 23.5092 | 22.8745 | 26.6333 | 26.5302 | 26.3338 | 26.1153 | 25.9348 | 25.7713 | 25.6107 | 25.4521 | 25.2819 | 25.1154 | 24.7913 | 24.1593 | 23.5189 | 22.8862
|  | OLD ROAD | ST |  |  | 28.32 | 28.2758 | 28.2001 | 28.0943 | 27.9904 | 27.921 | 27.8484 | 27.7742 | 27.695 | 27.6227 | 27.4896 | 27.1768 | 26.8662 | 26.5557 | 26.6647 | 26.6125 | 26.5234 | 26.3987 | 26.2764 | 26.1947 | 26.1091 | 26.0217 | 25.9284 | 25.8432 | 25.6864 | 25.3179 | 24.952 | 24.5863 | 26.6648 | 26.6128 | 26.524 | 26.3997 | 26.2777 | 26.1962 | 26.1109 | 26.0237 | 25.9308 | 25.8458 | 25.6895 | 25.3221 | 24.9573 | 24.5927
|  | OLD ROAD | FS |  |  | 28.3374 | 28.3214 | 28.3036 | 28.2654 | 28.2319 | 28.2048 | 28.178 | 28.1447 | 28.1125 | 28.0813 | 28.0213 | 27.8878 | 27.7638 | 27.6466 | 26.6852 | 26.6663 | 26.6453 | 26.6003 | 26.5608 | 26.529 | 26.4973 | 26.4582 | 26.4202 | 26.3835 | 26.3128 | 26.1556 | 26.0094 | 25.8714 | 26.6852 | 26.6664 | 26.6455 | 26.6006 | 26.5613 | 26.5295 | 26.4979 | 26.4589 | 26.421 | 26.3844 | 26.3139 | 26.1572 | 26.0115 | 25.8739
COWLEY GSP | OXFORD (OSNEY) BSP | OSNEY | MINIMUM HEADROOM | SP 50148 05901 | NO | 28.2711 | 28.1864 | 27.984 | 27.7306 | 27.4403 | 27.1325 | 26.8061 | 26.4832 | 26.2197 | 25.9815 | 25.508 | 24.7623 | 23.9988 | 23.2409 | 26.6071 | 26.5073 | 26.2688 | 25.9703 | 25.6284 | 25.2657 | 24.8812 | 24.5009 | 24.1905 | 23.9098 | 23.3521 | 22.4561 | 21.5055 | 20.5664 | 26.6073 | 26.5079 | 26.2701 | 25.9725 | 25.6317 | 25.2701 | 24.8868 | 24.5076 | 24.1982 | 23.9183 | 23.3623 | 22.469 | 21.5213 | 20.5851
|  | OSNEY | CT |  |  | 28.2711 | 28.1864 | 27.984 | 27.7306 | 27.4403 | 27.1325 | 26.8061 | 26.4832 | 26.2197 | 25.9815 | 25.508 | 24.7623 | 23.9988 | 23.2409 | 26.6084 | 26.5105 | 26.2764 | 25.9871 | 25.6607 | 25.3184 | 24.9691 | 24.6181 | 24.3068 | 24.007 | 23.4212 | 22.4561 | 21.5055 | 20.5664 | 26.6086 | 26.5111 | 26.2777 | 25.9893 | 25.6638 | 25.3226 | 24.9744 | 24.6245 | 24.3141 | 24.0152 | 23.4312 | 22.469 | 21.5213 | 20.5851
|  | OSNEY | LW |  |  | 28.2711 | 28.1864 | 27.984 | 27.7306 | 27.4403 | 27.1325 | 26.8061 | 26.4832 | 26.2197 | 25.9815 | 25.508 | 24.7623 | 23.9988 | 23.2409 | 26.6071 | 26.5073 | 26.2688 | 25.9703 | 25.6284 | 25.2657 | 24.8812 | 24.5009 | 24.1905 | 23.9098 | 23.3521 | 22.4736 | 21.5742 | 20.6814 | 26.6073 | 26.5079 | 26.2701 | 25.9725 | 25.6317 | 25.2701 | 24.8868 | 24.5076 | 24.1982 | 23.9183 | 23.3623 | 22.4865 | 21.5898 | 20.6997
|  | OSNEY | ST |  |  | 28.3125 | 28.2823 | 28.2158 | 28.0955 | 27.9321 | 27.8023 | 27.6681 | 27.5326 | 27.4235 | 27.3205 | 27.1207 | 26.6775 | 26.2629 | 25.8509 | 26.6559 | 26.6202 | 26.5419 | 26.4001 | 26.2077 | 26.0548 | 25.8967 | 25.737 | 25.6086 | 25.4872 | 25.2518 | 24.7298 | 24.2413 | 23.7561 | 26.656 | 26.6205 | 26.5424 | 26.4011 | 26.2092 | 26.0567 | 25.8992 | 25.74 | 25.6119 | 25.4909 | 25.2562 | 24.7358 | 24.2488 | 23.765
|  | OSNEY | FS |  |  | 28.3312 | 28.3262 | 28.3207 | 28.279 | 28.2219 | 28.17 | 28.1142 | 28.0505 | 28.0023 | 27.9598 | 27.8754 | 27.6812 | 27.5081 | 27.3406 | 26.6778 | 26.672 | 26.6655 | 26.6164 | 26.5491 | 26.4879 | 26.4222 | 26.3472 | 26.2904 | 26.2403 | 26.1409 | 25.9121 | 25.7082 | 25.5109 | 26.6779 | 26.6721 | 26.6656 | 26.6167 | 26.5496 | 26.4886 | 26.4231 | 26.3482 | 26.2917 | 26.2417 | 26.1426 | 25.9145 | 25.7112 | 25.5145
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON | MINIMUM HEADROOM | SU 52061 50913 | YES | 29.4943 | 29.4911 | 29.4835 | 29.4752 | 29.467 | 29.459 | 29.451 | 29.443 | 29.4345 | 29.426 | 29.4093 | 29.3717 | 29.3328 | 29.2942 | 27.0986 | 27.0986 | 27.0986 | 21.7896 | 21.6732 | 21.558 | 21.444 | 21.3311 | 21.2093 | 21.0887 | 20.8515 | 20.3651 | 19.8553 | 19.3486 | 26.4425 | 26.4032 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 21.6935 | 21.1911 | 20.6919
|  | OVERTON | CT |  |  | 29.4943 | 29.4911 | 29.4835 | 29.4752 | 29.467 | 29.459 | 29.451 | 29.443 | 29.4345 | 29.426 | 29.4093 | 29.3717 | 29.3328 | 29.2942 | 27.0986 | 27.0986 | 27.0986 | 21.7896 | 21.6732 | 21.558 | 21.444 | 21.3311 | 21.2093 | 21.0887 | 20.8515 | 20.3651 | 19.8553 | 19.3486 | 26.4425 | 26.4032 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 21.6935 | 21.1911 | 20.6919
|  | OVERTON | LW |  |  | 29.4943 | 29.4911 | 29.4835 | 29.4752 | 29.467 | 29.459 | 29.451 | 29.443 | 29.4345 | 29.426 | 29.4093 | 29.3717 | 29.3328 | 29.2942 | 27.0986 | 27.0986 | 27.0986 | 21.8345 | 21.7352 | 21.6371 | 21.54 | 21.4438 | 21.3402 | 21.2375 | 21.0342 | 20.5777 | 20.106 | 19.6374 | 26.4463 | 26.4128 | 26.3331 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 21.4382 | 20.9765
|  | OVERTON | ST |  |  | 29.4955 | 29.494 | 29.4906 | 29.4856 | 29.4795 | 29.4751 | 29.4708 | 29.4666 | 29.462 | 29.4575 | 29.4487 | 29.426 | 29.403 | 29.3799 | 27.0986 | 27.0986 | 27.0986 | 27.0986 | 21.8865 | 21.8334 | 21.781 | 21.7294 | 21.6736 | 21.6188 | 21.5123 | 21.2371 | 20.9574 | 20.6777 | 26.4587 | 26.4427 | 26.4077 | 26.3549 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134 | 26.3134
|  | OVERTON | FS |  |  | 29.4963 | 29.4961 | 29.4959 | 29.4945 | 29.4929 | 29.4914 | 29.4899 | 29.488 | 29.4861 | 29.4842 | 29.4806 | 29.4717 | 29.4628 | 29.4541 | 27.0986 | 27.0986 | 27.0986 | 27.0986 | 27.0986 | 27.0986 | 27.0986 | 27.0986 | 27.0986 | 27.0986 | 27.0986 | 21.7913 | 21.6833 | 21.5785 | 26.4671 | 26.465 | 26.4625 | 26.4481 | 26.4311 | 26.4154 | 26.3998 | 26.3798 | 26.3601 | 26.3407 | 26.3134 | 26.3134 | 26.3134 | 26.3134
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH | MINIMUM HEADROOM | SU 62243 66052 | YES | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 4.993 | 4.9826 | 4.9578 | 4.9309 | 4.9043 | 4.878 | 4.8519 | 4.8262 | 4.7984 | 4.7708 | 4.7162 | 4.6215 | 4.5236 | 4.4271 | 4.9993 | 4.9983 | 4.9958 | 4.9932 | 4.9905 | 4.9879 | 4.9853 | 4.9828 | 4.98 | 4.9773 | 4.9719 | 4.9625 | 4.9528 | 4.9432
|  | PADWORTH | CT |  |  | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 4.994 | 4.9851 | 4.9639 | 4.9408 | 4.918 | 4.8955 | 4.8731 | 4.851 | 4.8272 | 4.8035 | 4.7569 | 4.6584 | 4.5564 | 4.4558 | 4.9994 | 4.9985 | 4.9964 | 4.9941 | 4.9919 | 4.9896 | 4.9874 | 4.9852 | 4.9829 | 4.9805 | 4.9759 | 4.9662 | 4.9561 | 4.9461
|  | PADWORTH | LW |  |  | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 4.993 | 4.9826 | 4.9578 | 4.9309 | 4.9043 | 4.878 | 4.8519 | 4.8262 | 4.7984 | 4.7708 | 4.7162 | 4.6215 | 4.5236 | 4.4271 | 4.9993 | 4.9983 | 4.9958 | 4.9932 | 4.9905 | 4.9879 | 4.9853 | 4.9828 | 4.98 | 4.9773 | 4.9719 | 4.9625 | 4.9528 | 4.9432
|  | PADWORTH | ST |  |  | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 4.9967 | 4.9914 | 4.9797 | 4.9621 | 4.9409 | 4.929 | 4.9172 | 4.9057 | 4.8932 | 4.8809 | 4.8569 | 4.7974 | 4.7378 | 4.6785 | 4.9997 | 4.9991 | 4.998 | 4.9962 | 4.9941 | 4.993 | 4.9918 | 4.9907 | 4.9894 | 4.9882 | 4.9858 | 4.9799 | 4.974 | 4.9682
|  | PADWORTH | FS |  |  | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 4.9995 | 4.9989 | 4.9981 | 4.9937 | 4.9885 | 4.9844 | 4.9805 | 4.9754 | 4.9703 | 4.9654 | 4.9558 | 4.9325 | 4.9102 | 4.8891 | 5 | 4.9999 | 4.9998 | 4.9994 | 4.9989 | 4.9985 | 4.9981 | 4.9976 | 4.9971 | 4.9966 | 4.9956 | 4.9933 | 4.9911 | 4.989
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE | MINIMUM HEADROOM | SU 62960 76144 | NO | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 28.264 | 27.6932 | 29.0172 | 28.9703 | 28.8807 | 28.8432 | 28.8332 | 28.8233 | 28.8135 | 28.8038 | 28.7934 | 28.783 | 26.4713 | 25.7792 | 25.0555 | 24.3397 | 29.2158 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 26.321 | 25.6116 | 24.9099
|  | PANGBOURNE | CT |  |  | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 28.264 | 27.6932 | 29.0172 | 28.9703 | 28.8807 | 28.8432 | 28.8332 | 28.8233 | 28.8135 | 28.8038 | 28.7934 | 28.783 | 26.4713 | 25.7792 | 25.0555 | 24.3397 | 29.2158 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 26.321 | 25.6116 | 24.9099
|  | PANGBOURNE | LW |  |  | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 28.264 | 27.6932 | 29.023 | 28.9848 | 28.9023 | 28.848 | 28.8398 | 28.8317 | 28.8237 | 28.8159 | 28.8073 | 28.7989 | 28.7821 | 26.2069 | 25.5379 | 24.8759 | 29.2252 | 29.1925 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 26.0845 | 25.4355
|  | PANGBOURNE | ST |  |  | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 29.0387 | 29.0227 | 28.9876 | 28.9346 | 28.8884 | 28.861 | 28.8469 | 28.8433 | 28.8394 | 28.8356 | 28.8281 | 28.8094 | 28.7904 | 26.6407 | 29.2506 | 29.2246 | 29.1941 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19
|  | PANGBOURNE | FS |  |  | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 31.071 | 29.0469 | 29.0446 | 29.0419 | 29.0257 | 29.0063 | 28.9898 | 28.9734 | 28.9523 | 28.9316 | 28.9132 | 28.889 | 28.8463 | 28.8385 | 28.831 | 29.2639 | 29.2602 | 29.2558 | 29.2295 | 29.2046 | 29.1953 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19 | 29.19
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE | MINIMUM HEADROOM | SU 51369 08259 | NO | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 37.0644 | 37.0161 | 36.9007 | 36.7755 | 36.6513 | 36.515 | 36.419 | 36.3434 | 36.2618 | 36.1798 | 36.0133 | 35.7573 | 35.7573 | 35.7573 | 35.9603 | 35.9451 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412
|  | PARK GATE | CT |  |  | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 37.0707 | 37.0319 | 36.9389 | 36.8379 | 36.7376 | 36.6264 | 36.5119 | 36.431 | 36.3649 | 36.2972 | 36.1565 | 35.8255 | 35.7573 | 35.7573 | 35.9623 | 35.9501 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412
|  | PARK GATE | LW |  |  | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 37.0644 | 37.0161 | 36.9007 | 36.7755 | 36.6513 | 36.515 | 36.419 | 36.3434 | 36.2618 | 36.1798 | 36.0133 | 35.7573 | 35.7573 | 35.7573 | 35.9603 | 35.9451 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412
|  | PARK GATE | ST |  |  | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 37.1397 | 37.0537 | 36.9956 | 36.908 | 36.8021 | 36.7232 | 36.6424 | 36.561 | 36.4723 | 36.4236 | 36.3244 | 36.102 | 35.8853 | 35.7573 | 35.9841 | 35.9569 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412
|  | PARK GATE | FS |  |  | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 40.431 | 37.1542 | 37.1279 | 37.1248 | 37.106 | 37.0836 | 37.0575 | 37.0302 | 36.9959 | 36.9612 | 36.9261 | 36.8549 | 36.694 | 36.5397 | 36.4273 | 35.9886 | 35.9803 | 35.9793 | 35.9734 | 35.9664 | 35.9581 | 35.9495 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412 | 35.9412
MELKSHAM GSP | AMESBURY | PARK HOUSE | MINIMUM HEADROOM | SU 23138 43780 | YES | 12.0265 | 12.0255 | 12.0229 | 12.0202 | 12.0174 | 12.0146 | 12.0118 | 12.0091 | 12.0061 | 12.0031 | 11.9972 | 11.9884 | 11.9792 | 11.9701 | 9.5864 | 9.5772 | 9.5547 | 9.5324 | 9.5236 | 9.5147 | 9.5058 | 9.497 | 9.4874 | 9.478 | 9.4591 | 9.431 | 9.4018 | 9.3727 | 9.9723 | 9.9703 | 9.9654 | 9.9601 | 9.9548 | 9.9495 | 9.9442 | 9.9389 | 9.9332 | 9.9275 | 9.9163 | 9.8994 | 9.882 | 9.8646
|  | PARK HOUSE | CT |  |  | 12.0265 | 12.0255 | 12.0229 | 12.0202 | 12.0174 | 12.0146 | 12.0118 | 12.0091 | 12.0061 | 12.0031 | 11.9972 | 11.9884 | 11.9792 | 11.9701 | 9.5875 | 9.5798 | 9.5611 | 9.5409 | 9.5288 | 9.5215 | 9.514 | 9.5067 | 9.4988 | 9.491 | 9.4754 | 9.4472 | 9.4179 | 9.3887 | 9.9725 | 9.9708 | 9.9668 | 9.9624 | 9.958 | 9.9536 | 9.9491 | 9.9447 | 9.94 | 9.9353 | 9.926 | 9.9091 | 9.8916 | 9.8741
|  | PARK HOUSE | LW |  |  | 12.0265 | 12.0255 | 12.0229 | 12.0202 | 12.0174 | 12.0146 | 12.0118 | 12.0091 | 12.0061 | 12.0031 | 11.9972 | 11.9884 | 11.9792 | 11.9701 | 9.5864 | 9.5772 | 9.5547 | 9.5324 | 9.5236 | 9.5147 | 9.5058 | 9.497 | 9.4874 | 9.478 | 9.4591 | 9.431 | 9.4018 | 9.3727 | 9.9723 | 9.9703 | 9.9654 | 9.9601 | 9.9548 | 9.9495 | 9.9442 | 9.9389 | 9.9332 | 9.9275 | 9.9163 | 9.8994 | 9.882 | 9.8646
|  | PARK HOUSE | ST |  |  | 12.0272 | 12.0272 | 12.027 | 12.0268 | 12.0266 | 12.0254 | 12.0242 | 12.0231 | 12.0218 | 12.0206 | 12.0182 | 12.0119 | 12.0057 | 11.9995 | 9.5923 | 9.5919 | 9.5907 | 9.589 | 9.5867 | 9.5766 | 9.5663 | 9.5561 | 9.5453 | 9.5346 | 9.5261 | 9.5062 | 9.4863 | 9.4666 | 9.9736 | 9.9735 | 9.9732 | 9.9728 | 9.9723 | 9.9701 | 9.9679 | 9.9657 | 9.9633 | 9.961 | 9.9564 | 9.9444 | 9.9325 | 9.9207
|  | PARK HOUSE | FS |  |  | 12.0272 | 12.0271 | 12.0271 | 12.0266 | 12.026 | 12.0257 | 12.0253 | 12.0249 | 12.0245 | 12.0241 | 12.0232 | 12.0211 | 12.0189 | 12.0168 | 9.5922 | 9.5917 | 9.5909 | 9.5869 | 9.582 | 9.579 | 9.5759 | 9.5721 | 9.5683 | 9.5646 | 9.5572 | 9.5383 | 9.5284 | 9.5217 | 9.9736 | 9.9734 | 9.9733 | 9.9724 | 9.9713 | 9.9707 | 9.97 | 9.9692 | 9.9684 | 9.9675 | 9.9659 | 9.9618 | 9.9577 | 9.9537
MINETY GSP | STRATTON (2 X 90) | PARK NORTH | MINIMUM HEADROOM | SU 18052 84542 | YES | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 31.4276 | 31.4028 | 31.3472 | 31.2871 | 31.2271 | 31.1672 | 31.1073 | 31.0474 | 30.9837 | 30.9206 | 30.7887 | 30.0894 | 30.0894 | 26.6261 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 26.1633
|  | PARK NORTH | CT |  |  | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 31.4303 | 31.4089 | 31.3609 | 31.3091 | 31.2568 | 31.2042 | 31.1522 | 31.0998 | 31.0439 | 30.988 | 30.879 | 30.2637 | 30.0894 | 30.0894 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 26.5664
|  | PARK NORTH | LW |  |  | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 31.4276 | 31.4028 | 31.3472 | 31.2871 | 31.2271 | 31.1672 | 31.1073 | 31.0474 | 30.9837 | 30.9206 | 30.7887 | 30.0894 | 30.0894 | 26.6261 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 26.1633
|  | PARK NORTH | ST |  |  | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 31.4462 | 31.4349 | 31.4122 | 31.3789 | 31.3387 | 31.2802 | 31.2227 | 31.1654 | 31.104 | 31.0431 | 30.925 | 30.4511 | 30.0894 | 30.0894 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501
|  | PARK NORTH | FS |  |  | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 33.7893 | 31.4597 | 31.4563 | 31.4534 | 31.4426 | 31.4302 | 31.4152 | 31.4001 | 31.381 | 31.3623 | 31.3439 | 31.3082 | 31.1645 | 30.9732 | 30.7595 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501 | 31.9501
WILLESDEN GSP | ACTON LANE | PARK ROYAL | MINIMUM HEADROOM | TQ 20137 82215 | NO | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 110.4922 | 110.4861 | 110.4716 | 110.4558 | 110.4401 | 110.4245 | 110.4088 | 110.3929 | 110.3752 | 110.3574 | 110.3217 | 110.2075 | 110.0888 | 109.9716 | 108.0418 | 108.0394 | 108.0337 | 108.0275 | 108.0213 | 108.0152 | 108.009 | 108.0027 | 107.9957 | 107.9887 | 107.9747 | 107.9297 | 107.883 | 107.8369
|  | PARK ROYAL | CT |  |  | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 110.4922 | 110.4861 | 110.4716 | 110.4559 | 110.4402 | 110.4246 | 110.4089 | 110.3932 | 110.3759 | 110.3585 | 110.3236 | 110.2076 | 110.0888 | 109.9716 | 108.0418 | 108.0394 | 108.0337 | 108.0275 | 108.0213 | 108.0152 | 108.009 | 108.0028 | 107.996 | 107.9892 | 107.9755 | 107.9298 | 107.883 | 107.8369
|  | PARK ROYAL | LW |  |  | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 110.4922 | 110.4861 | 110.4716 | 110.4558 | 110.4401 | 110.4245 | 110.4088 | 110.3929 | 110.3752 | 110.3574 | 110.3217 | 110.2075 | 110.0908 | 109.9757 | 108.0418 | 108.0394 | 108.0337 | 108.0275 | 108.0213 | 108.0152 | 108.009 | 108.0027 | 107.9957 | 107.9887 | 107.9747 | 107.9297 | 107.8838 | 107.8386
|  | PARK ROYAL | ST |  |  | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 110.5243 | 110.4919 | 110.486 | 110.477 | 110.4662 | 110.453 | 110.4399 | 110.4268 | 110.4125 | 110.3982 | 110.3699 | 110.2992 | 110.2293 | 110.1599 | 108.0544 | 108.0417 | 108.0393 | 108.0358 | 108.0316 | 108.0264 | 108.0212 | 108.0161 | 108.0104 | 108.0048 | 107.9937 | 107.9659 | 107.9383 | 107.911
|  | PARK ROYAL | FS |  |  | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 116.7646 | 110.5257 | 110.4956 | 110.4952 | 110.4928 | 110.4899 | 110.4854 | 110.481 | 110.4752 | 110.4695 | 110.4638 | 110.4524 | 110.4246 | 110.398 | 110.3725 | 108.055 | 108.0431 | 108.043 | 108.042 | 108.0409 | 108.0391 | 108.0374 | 108.0351 | 108.0329 | 108.0306 | 108.0261 | 108.0152 | 108.0047 | 107.9947
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH | MINIMUM HEADROOM | SZ 03222 92233 | NO | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 28.2633 | 34.8892 | 34.7642 | 34.6144 | 34.3708 | 34.0916 | 33.7801 | 33.5011 | 33.4685 | 33.4332 | 33.3956 | 33.3518 | 33.1731 | 32.9961 | 25.084 | 35.5109 | 35.3953 | 35.2567 | 35.044 | 34.9488 | 34.8425 | 34.7265 | 34.6023 | 34.4675 | 34.3241 | 34.1571 | 34.0993 | 34.0993 | 26.2974
|  | PARKSTONE NORTH | CT |  |  | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 28.2633 | 34.8939 | 34.7837 | 34.6469 | 34.4275 | 34.175 | 33.8895 | 33.583 | 33.4846 | 33.4513 | 33.4153 | 33.3693 | 33.1951 | 33.0297 | 25.6072 | 35.5152 | 35.4134 | 35.2867 | 35.0838 | 34.9772 | 34.8799 | 34.7753 | 34.6637 | 34.5366 | 34.3993 | 34.2236 | 34.0993 | 34.0993 | 34.0993
|  | PARKSTONE NORTH | LW |  |  | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 28.2633 | 34.8892 | 34.7642 | 34.6144 | 34.3708 | 34.0916 | 33.7801 | 33.5011 | 33.4685 | 33.4332 | 33.3956 | 33.3518 | 33.1731 | 32.9961 | 25.084 | 35.5109 | 35.3953 | 35.2567 | 35.044 | 34.9488 | 34.8425 | 34.7265 | 34.6023 | 34.4675 | 34.3241 | 34.1571 | 34.0993 | 34.0993 | 26.2974
|  | PARKSTONE NORTH | ST |  |  | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 34.9225 | 34.8547 | 34.7868 | 34.6473 | 34.4711 | 34.1268 | 33.7712 | 33.4979 | 33.4609 | 33.4219 | 33.3625 | 33.2262 | 33.1015 | 32.979 | 35.5417 | 35.479 | 35.4162 | 35.2871 | 35.1242 | 34.9608 | 34.8395 | 34.7144 | 34.5733 | 34.4245 | 34.1979 | 34.0993 | 34.0993 | 34.0993
|  | PARKSTONE NORTH | FS |  |  | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 36.5664 | 35.0678 | 34.9144 | 34.8971 | 34.8416 | 34.7758 | 34.663 | 34.5463 | 34.407 | 34.2612 | 34.1081 | 33.8808 | 33.493 | 33.4505 | 33.4088 | 35.6761 | 35.5343 | 35.5182 | 35.4669 | 35.406 | 35.3017 | 35.1937 | 35.0648 | 35.0066 | 34.9544 | 34.8769 | 34.6955 | 34.5334 | 34.3745
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH | MINIMUM HEADROOM | SZ 04762 89848 | NO | 48.345 | 48.3424 | 48.3389 | 48.3345 | 48.329 | 48.3223 | 48.3142 | 48.3046 | 48.2955 | 48.285 | 48.2595 | 48.1687 | 48.0589 | 47.9188 | 44.8484 | 44.7319 | 44.4599 | 44.1493 | 43.8361 | 43.5199 | 43.2027 | 42.8822 | 42.5344 | 42.2384 | 42.131 | 41.888 | 41.6342 | 41.3663 | 43.6659 | 43.6205 | 43.52 | 43.4055 | 43.2892 | 43.1711 | 43.0517 | 42.9302 | 42.8 | 42.7506 | 42.7027 | 42.5435 | 42.3676 | 42.1655
|  | PARKSTONE SOUTH | CT |  |  | 48.345 | 48.3424 | 48.3389 | 48.3345 | 48.329 | 48.3223 | 48.3142 | 48.3046 | 48.2955 | 48.285 | 48.2595 | 48.1687 | 48.0589 | 47.9188 | 44.8484 | 44.7319 | 44.4599 | 44.1493 | 43.8361 | 43.5199 | 43.2027 | 42.8822 | 42.5344 | 42.2384 | 42.131 | 41.888 | 41.6342 | 41.3663 | 43.6659 | 43.6205 | 43.52 | 43.4055 | 43.2892 | 43.1711 | 43.0517 | 42.9302 | 42.8 | 42.7506 | 42.7027 | 42.5435 | 42.3676 | 42.1655
|  | PARKSTONE SOUTH | LW |  |  | 48.345 | 48.3424 | 48.3389 | 48.3345 | 48.329 | 48.3223 | 48.3142 | 48.3046 | 48.2955 | 48.285 | 48.2595 | 48.1687 | 48.0589 | 47.9188 | 44.8672 | 44.774 | 44.554 | 44.2971 | 44.036 | 43.77 | 43.4998 | 43.2265 | 42.9321 | 42.6349 | 42.2589 | 42.0611 | 41.8496 | 41.6207 | 43.678 | 43.6448 | 43.5684 | 43.4789 | 43.3872 | 43.2929 | 43.1962 | 43.0973 | 42.9916 | 42.884 | 42.8133 | 42.7202 | 42.6074 | 42.4637
|  | PARKSTONE SOUTH | ST |  |  | 48.3474 | 48.3465 | 48.3453 | 48.3439 | 48.3423 | 48.34 | 48.3375 | 48.3346 | 48.3316 | 48.3284 | 48.3213 | 48.2987 | 48.2643 | 48.2284 | 44.9117 | 44.8814 | 44.8153 | 44.7065 | 44.5752 | 44.4253 | 44.2751 | 44.1232 | 43.9559 | 43.7864 | 43.48 | 42.7446 | 42.2531 | 42.1449 | 43.6948 | 43.6839 | 43.6609 | 43.6233 | 43.578 | 43.526 | 43.4738 | 43.4207 | 43.3623 | 43.303 | 43.1949 | 42.9312 | 42.8183 | 42.7814
|  | PARKSTONE SOUTH | FS |  |  | 48.3477 | 48.3471 | 48.3465 | 48.3456 | 48.3445 | 48.3434 | 48.3423 | 48.341 | 48.3397 | 48.3384 | 48.3355 | 48.3245 | 48.3125 | 48.2999 | 44.9259 | 44.9194 | 44.9111 | 44.8657 | 44.8121 | 44.7595 | 44.7064 | 44.6402 | 44.5735 | 44.5065 | 44.385 | 44.0926 | 43.8182 | 43.5551 | 43.6997 | 43.6971 | 43.6939 | 43.6779 | 43.6592 | 43.6407 | 43.622 | 43.5989 | 43.5756 | 43.552 | 43.5091 | 43.4027 | 43.3016 | 43.2039
BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM | MINIMUM HEADROOM | SU 84770 68709 | NO | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 25.7212 | 25.7185 | 25.7119 | 25.7048 | 25.6978 | 25.6907 | 25.6838 | 25.6769 | 25.6695 | 25.6622 | 25.6477 | 25.6122 | 25.5725 | 25.5334 | 25.0514 | 25.0504 | 25.0482 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457
|  | PEACOCK FARM | CT |  |  | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 25.7215 | 25.7191 | 25.7136 | 25.7075 | 25.7014 | 25.6954 | 25.6895 | 25.6836 | 25.6772 | 25.6709 | 25.6585 | 25.6232 | 25.5836 | 25.5442 | 25.0515 | 25.0507 | 25.0487 | 25.0466 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457
|  | PEACOCK FARM | LW |  |  | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 25.7212 | 25.7185 | 25.7119 | 25.7048 | 25.6978 | 25.6907 | 25.6838 | 25.6769 | 25.6695 | 25.6622 | 25.6477 | 25.6122 | 25.5725 | 25.5334 | 25.0514 | 25.0504 | 25.0482 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457
|  | PEACOCK FARM | ST |  |  | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 25.7603 | 25.7228 | 25.7225 | 25.7221 | 25.7215 | 25.7172 | 25.713 | 25.7088 | 25.7043 | 25.6999 | 25.6913 | 25.6694 | 25.6456 | 25.6218 | 25.065 | 25.0519 | 25.0518 | 25.0517 | 25.0515 | 25.05 | 25.0485 | 25.0471 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457 | 25.0457
|  | PEACOCK FARM | FS |  |  | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 28.2668 | 25.7603 | 25.7228 | 25.7226 | 25.7214 | 25.7199 | 25.7185 | 25.7171 | 25.7152 | 25.7134 | 25.7116 | 25.7082 | 25.6999 | 25.6911 | 25.6821 | 25.065 | 25.0519 | 25.0518 | 25.0514 | 25.0509 | 25.0504 | 25.0499 | 25.0493 | 25.0487 | 25.048 | 25.0468 | 25.0457 | 25.0457 | 25.0457
BRAMLEY (FLEE) | FERNHURST | PETERSFIELD | MINIMUM HEADROOM | SU 74173 23420 | NO | 31.601 | 31.5685 | 31.4913 | 31.4078 | 31.3213 | 31.2348 | 31.1482 | 31.0623 | 31.0454 | 31.0454 | 28.0629 | 26.4882 | 24.8562 | 23.2263 | 28.9782 | 28.9782 | 28.9782 | 26.666 | 26.3722 | 26.0476 | 25.7026 | 25.3607 | 24.9897 | 24.6217 | 23.8804 | 22.2584 | 20.4105 | 18.5628 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 26.3571 | 25.9751 | 25.5965 | 25.1856 | 24.7781 | 23.9572 | 22.1718 | 20.2914 | 18.4114
|  | PETERSFIELD | CT |  |  | 31.601 | 31.5685 | 31.4913 | 31.4078 | 31.3213 | 31.2348 | 31.1482 | 31.0623 | 31.0454 | 31.0454 | 28.0629 | 26.4882 | 24.8562 | 23.2263 | 28.9782 | 28.9782 | 28.9782 | 26.666 | 26.3722 | 26.0476 | 25.7026 | 25.3607 | 24.9897 | 24.6217 | 23.8804 | 22.2584 | 20.4105 | 18.5628 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 26.3571 | 25.9751 | 25.5965 | 25.1856 | 24.7781 | 23.9572 | 22.1718 | 20.2914 | 18.4114
|  | PETERSFIELD | LW |  |  | 31.601 | 31.5685 | 31.4913 | 31.4078 | 31.3213 | 31.2348 | 31.1482 | 31.0623 | 31.0454 | 31.0454 | 28.0629 | 26.4882 | 24.8562 | 23.2263 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 26.51 | 26.253 | 25.9427 | 25.6344 | 25.3005 | 24.9689 | 24.2965 | 22.6265 | 20.7647 | 18.8835 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 26.585 | 26.241 | 25.8996 | 25.5298 | 25.1626 | 24.4179 | 22.5685 | 20.6519 | 18.7377
|  | PETERSFIELD | ST |  |  | 31.6142 | 31.6004 | 31.5704 | 31.5254 | 31.4691 | 31.419 | 31.3699 | 31.3214 | 31.2685 | 31.2164 | 31.1114 | 31.0454 | 27.5522 | 26.579 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 26.6544 | 26.5102 | 26.3533 | 26.1876 | 25.8106 | 24.79 | 23.7549 | 22.7228 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 26.5122 | 26.0946 | 24.9644 | 23.8182 | 22.6752
|  | PETERSFIELD | FS |  |  | 31.6213 | 31.6194 | 31.6173 | 31.6047 | 31.5895 | 31.573 | 31.5565 | 31.5353 | 31.5145 | 31.4939 | 31.4527 | 31.3421 | 31.23 | 31.1184 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 28.9782 | 26.5718 | 26.2362 | 25.8359 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 28.5611 | 26.566 | 26.1227
IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE | MINIMUM HEADROOM | SU 98108 80286 | NO | 59.7679 | 59.6776 | 59.5555 | 59.4019 | 59.2401 | 59.0713 | 58.9017 | 58.7911 | 58.7539 | 58.7303 | 58.6855 | 58.5983 | 58.5187 | 58.4534 | 59.0208 | 58.7777 | 58.4491 | 58.0355 | 57.87 | 57.7524 | 57.6341 | 57.5324 | 57.4705 | 57.4311 | 57.3566 | 57.3109 | 57.3109 | 57.3109 | 64.3566 | 64.2071 | 64.005 | 63.7506 | 63.4828 | 63.2033 | 62.9225 | 62.6809 | 62.5337 | 62.44 | 62.2631 | 61.9707 | 61.7856 | 61.602
|  | PETERSFIELD AVENUE | CT |  |  | 59.7679 | 59.6776 | 59.5555 | 59.4019 | 59.2401 | 59.0713 | 58.9017 | 58.7911 | 58.7539 | 58.7303 | 58.6855 | 58.5983 | 58.5187 | 58.4534 | 59.0283 | 58.8209 | 58.5328 | 58.1775 | 57.9219 | 57.816 | 57.7067 | 57.6032 | 57.5243 | 57.4631 | 57.3644 | 57.3109 | 57.3109 | 57.3109 | 64.3611 | 64.2336 | 64.0564 | 63.838 | 63.6061 | 63.3546 | 63.0949 | 62.849 | 62.6616 | 62.5163 | 62.2818 | 61.9731 | 61.7992 | 61.6269
|  | PETERSFIELD AVENUE | LW |  |  | 59.7679 | 59.6776 | 59.5555 | 59.4019 | 59.2401 | 59.0713 | 58.9017 | 58.7911 | 58.7539 | 58.7303 | 58.6855 | 58.5983 | 58.5187 | 58.4534 | 59.0208 | 58.7777 | 58.4491 | 58.0355 | 57.87 | 57.7524 | 57.6341 | 57.5324 | 57.4705 | 57.4311 | 57.3566 | 57.3109 | 57.3109 | 57.3109 | 64.3566 | 64.2071 | 64.005 | 63.7506 | 63.4828 | 63.2033 | 62.9225 | 62.6809 | 62.5337 | 62.44 | 62.2631 | 61.9707 | 61.7856 | 61.602
|  | PETERSFIELD AVENUE | ST |  |  | 59.806 | 59.7339 | 59.6671 | 59.5785 | 59.48 | 59.3662 | 59.2494 | 59.1385 | 59.0485 | 58.9754 | 58.8524 | 58.7364 | 58.6653 | 58.6128 | 59.1233 | 58.9292 | 58.7496 | 58.5108 | 58.2458 | 57.9579 | 57.8765 | 57.7992 | 57.7365 | 57.6855 | 57.5998 | 57.4412 | 57.3109 | 57.3109 | 64.4196 | 64.3002 | 64.1898 | 64.0429 | 63.88 | 63.6915 | 63.4982 | 63.3145 | 63.1656 | 63.0445 | 62.841 | 62.4642 | 62.1441 | 62.0025
|  | PETERSFIELD AVENUE | FS |  |  | 59.8208 | 59.7716 | 59.7399 | 59.698 | 59.6547 | 59.6062 | 59.5584 | 59.5133 | 59.4797 | 59.4543 | 59.4054 | 59.3127 | 59.2406 | 59.17 | 59.1634 | 59.0308 | 58.9455 | 58.8327 | 58.7162 | 58.5856 | 58.4568 | 58.3353 | 58.245 | 58.1765 | 58.0451 | 57.9206 | 57.8703 | 57.8211 | 64.4442 | 64.3627 | 64.3102 | 64.2408 | 64.1692 | 64.0889 | 64.0097 | 63.935 | 63.8795 | 63.8373 | 63.7565 | 63.6029 | 63.4836 | 63.3666
MANNINGTON GSP | SALISBURY | PETERSFINGER | MINIMUM HEADROOM | SU 15608 29334 | YES | 13.9562 | 13.9192 | 13.8299 | 13.7322 | 13.6299 | 13.5244 | 13.4159 | 13.3049 | 13.1813 | 13.0558 | 12.7987 | 11.3105 | 10.5077 | 9.7045 | 13.9117 | 13.8651 | 13.7525 | 13.6296 | 13.5023 | 13.3726 | 13.2398 | 13.1061 | 12.96 | 12.8136 | 12.5141 | 11.0346 | 10.067 | 9.1046 | 13.912 | 13.8655 | 13.7533 | 13.6308 | 13.5038 | 13.3745 | 13.2421 | 13.1088 | 12.9631 | 12.8172 | 12.5186 | 10.864 | 9.8961 | 8.9341
|  | PETERSFINGER | CT |  |  | 13.9562 | 13.9192 | 13.8299 | 13.7322 | 13.6299 | 13.5244 | 13.4159 | 13.3049 | 13.1813 | 13.0558 | 12.7987 | 11.3105 | 10.5077 | 9.7045 | 13.9117 | 13.8651 | 13.7525 | 13.6296 | 13.5023 | 13.3726 | 13.2398 | 13.1061 | 12.96 | 12.8136 | 12.5141 | 11.0346 | 10.067 | 9.1046 | 13.912 | 13.8655 | 13.7533 | 13.6308 | 13.5038 | 13.3745 | 13.2421 | 13.1088 | 12.9631 | 12.8172 | 12.5186 | 10.864 | 9.8961 | 8.9341
|  | PETERSFINGER | LW |  |  | 13.9562 | 13.9192 | 13.8299 | 13.7322 | 13.6299 | 13.5244 | 13.4159 | 13.3049 | 13.1813 | 13.0558 | 12.7987 | 11.3105 | 10.5077 | 9.7045 | 13.9138 | 13.8702 | 13.765 | 13.6499 | 13.5294 | 13.4051 | 13.2774 | 13.1466 | 13.0009 | 12.8531 | 12.5503 | 11.0998 | 10.1574 | 9.2138 | 13.914 | 13.8706 | 13.7657 | 13.651 | 13.5308 | 13.4069 | 13.2796 | 13.1492 | 13.004 | 12.8566 | 12.5547 | 10.9292 | 9.9864 | 9.043
|  | PETERSFINGER | ST |  |  | 13.9944 | 13.9437 | 13.8932 | 13.8164 | 13.7207 | 13.6417 | 13.5613 | 13.4806 | 13.3923 | 13.304 | 13.1241 | 12.2838 | 11.8043 | 11.3312 | 13.9837 | 13.8991 | 13.8395 | 13.7492 | 13.6364 | 13.5433 | 13.4486 | 13.3536 | 13.2495 | 13.1455 | 12.9336 | 12.0966 | 11.5332 | 10.9758 | 13.9837 | 13.8994 | 13.84 | 13.7499 | 13.6375 | 13.5447 | 13.4503 | 13.3556 | 13.2518 | 13.1481 | 12.9369 | 12.0111 | 11.448 | 10.8923
|  | PETERSFINGER | FS |  |  | 13.9994 | 13.977 | 13.9745 | 13.9586 | 13.939 | 13.9135 | 13.8876 | 13.8543 | 13.8204 | 13.7864 | 13.7177 | 13.5396 | 13.3573 | 13.1733 | 13.9984 | 13.9382 | 13.9353 | 13.9167 | 13.8936 | 13.8635 | 13.833 | 13.7938 | 13.7538 | 13.7138 | 13.6328 | 13.4231 | 13.2083 | 12.9916 | 13.9984 | 13.9384 | 13.9355 | 13.9169 | 13.8939 | 13.8639 | 13.8335 | 13.7944 | 13.7546 | 13.7147 | 13.634 | 13.4248 | 13.2107 | 12.9947
MELKSHAM GSP | AMESBURY | PEWSEY | MINIMUM HEADROOM | SU 14710 59252 | YES | 26.6804 | 26.68 | 26.6795 | 26.6789 | 26.6781 | 26.6771 | 26.676 | 26.6746 | 26.6726 | 26.6703 | 26.6647 | 26.645 | 26.6114 | 26.5626 | 24.8708 | 24.8441 | 24.7873 | 24.7255 | 24.6627 | 24.5993 | 24.5353 | 24.4708 | 24.3997 | 24.3282 | 24.1979 | 23.9787 | 23.7401 | 23.6113 | 24.7249 | 24.7201 | 24.7135 | 24.7113 | 24.7089 | 24.7064 | 24.7036 | 24.7007 | 24.6964 | 24.6917 | 24.6806 | 24.6424 | 24.5843 | 24.5124
|  | PEWSEY | CT |  |  | 26.6804 | 26.68 | 26.6795 | 26.6789 | 26.6781 | 26.6771 | 26.676 | 26.6746 | 26.6726 | 26.6703 | 26.6647 | 26.645 | 26.6114 | 26.5626 | 24.873 | 24.8488 | 24.7997 | 24.7463 | 24.6919 | 24.6371 | 24.5817 | 24.5262 | 24.465 | 24.4036 | 24.2787 | 24.0343 | 23.7794 | 23.6113 | 24.7249 | 24.7201 | 24.7135 | 24.7113 | 24.7089 | 24.7064 | 24.7036 | 24.7007 | 24.6964 | 24.6917 | 24.6806 | 24.6424 | 24.5843 | 24.5124
|  | PEWSEY | LW |  |  | 26.6804 | 26.68 | 26.6795 | 26.6789 | 26.6781 | 26.6771 | 26.676 | 26.6746 | 26.6726 | 26.6703 | 26.6647 | 26.645 | 26.6114 | 26.5626 | 24.8708 | 24.8441 | 24.7873 | 24.7255 | 24.6627 | 24.5993 | 24.5353 | 24.4708 | 24.3997 | 24.3282 | 24.1979 | 23.9787 | 23.7401 | 23.6406 | 24.7256 | 24.7209 | 24.7168 | 24.7162 | 24.7153 | 24.7143 | 24.7131 | 24.7117 | 24.7096 | 24.7073 | 24.7016 | 24.6811 | 24.6464 | 24.596
|  | PEWSEY | ST |  |  | 26.6808 | 26.6806 | 26.6805 | 26.6803 | 26.68 | 26.6797 | 26.6793 | 26.6789 | 26.6784 | 26.6779 | 26.6768 | 26.6722 | 26.6643 | 26.653 | 24.8796 | 24.8619 | 24.8292 | 24.7816 | 24.7234 | 24.6931 | 24.6626 | 24.6321 | 24.5988 | 24.5656 | 24.4986 | 24.3227 | 24.168 | 24.0305 | 24.7272 | 24.7245 | 24.7186 | 24.7176 | 24.7173 | 24.717 | 24.7166 | 24.7162 | 24.7157 | 24.7152 | 24.7141 | 24.7092 | 24.7011 | 24.6894
|  | PEWSEY | FS |  |  | 26.6808 | 26.6807 | 26.6806 | 26.6805 | 26.6803 | 26.6802 | 26.68 | 26.6798 | 26.6796 | 26.6795 | 26.679 | 26.6774 | 26.6751 | 26.6725 | 24.8892 | 24.8874 | 24.8853 | 24.8728 | 24.8576 | 24.8473 | 24.8373 | 24.8244 | 24.8114 | 24.7985 | 24.7726 | 24.7065 | 24.6395 | 24.573 | 24.7287 | 24.7284 | 24.728 | 24.726 | 24.7236 | 24.7216 | 24.7197 | 24.7171 | 24.717 | 24.7168 | 24.7163 | 24.7147 | 24.7123 | 24.7096
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE | MINIMUM HEADROOM | SY 70169 99809 | YES | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 11.3326 | 11.3299 | 11.3236 | 11.3164 | 11.3087 | 11.3007 | 11.2877 | 11.2716 | 11.2541 | 11.2369 | 11.203 | 11.1035 | 10.9529 | 10.8078 | 4.7488 | 4.747 | 4.7427 | 4.7378 | 4.7325 | 4.727 | 4.7182 | 4.7072 | 4.6953 | 4.6835 | 4.6604 | 4.5926 | 4.4899 | 4.3885
|  | PIDDLETRENTHIDE | CT |  |  | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 11.3326 | 11.33 | 11.3238 | 11.3167 | 11.3091 | 11.3014 | 11.2934 | 11.2853 | 11.2767 | 11.268 | 11.2508 | 11.1035 | 10.9529 | 10.8078 | 4.7488 | 4.747 | 4.7428 | 4.7379 | 4.7328 | 4.7275 | 4.7221 | 4.7165 | 4.7107 | 4.7048 | 4.693 | 4.5926 | 4.4899 | 4.3885
|  | PIDDLETRENTHIDE | LW |  |  | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 11.3326 | 11.3299 | 11.3236 | 11.3164 | 11.3087 | 11.3007 | 11.2924 | 11.284 | 11.275 | 11.2661 | 11.2481 | 11.1039 | 10.9564 | 10.8127 | 4.7488 | 4.747 | 4.7427 | 4.7378 | 4.7325 | 4.727 | 4.7214 | 4.7156 | 4.7095 | 4.7034 | 4.6912 | 4.5929 | 4.4923 | 4.3929
|  | PIDDLETRENTHIDE | ST |  |  | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 11.3336 | 11.3324 | 11.3297 | 11.3256 | 11.3205 | 11.3041 | 11.2877 | 11.2716 | 11.2541 | 11.2369 | 11.203 | 11.1207 | 11.0395 | 10.9589 | 4.7495 | 4.7486 | 4.7468 | 4.744 | 4.7405 | 4.7293 | 4.7182 | 4.7072 | 4.6953 | 4.6835 | 4.6604 | 4.6043 | 4.5489 | 4.494
|  | PIDDLETRENTHIDE | FS |  |  | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 11.3342 | 11.334 | 11.3336 | 11.3324 | 11.3309 | 11.3254 | 11.3199 | 11.313 | 11.3061 | 11.2993 | 11.286 | 11.2541 | 11.2236 | 11.1945 | 4.7499 | 4.7497 | 4.7495 | 4.7487 | 4.7476 | 4.7439 | 4.7401 | 4.7354 | 4.7307 | 4.7261 | 4.717 | 4.6953 | 4.6745 | 4.6546
BRAMLEY (FLEE) | FERNHURST | PLAISTOW | MINIMUM HEADROOM | TQ 02071 29626 | NO | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 15.6639 | 15.6212 | 15.5977 | 15.5801 | 15.5626 | 15.5454 | 15.5284 | 15.5115 | 15.4933 | 15.4752 | 15.4393 | 15.411 | 15.3884 | 13.0705 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 13.227 | 12.8355 | 12.3936 | 11.9489
|  | PLAISTOW | CT |  |  | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 15.6643 | 15.6223 | 15.5981 | 15.5807 | 15.5635 | 15.5465 | 15.5297 | 15.5131 | 15.4951 | 15.4773 | 15.442 | 15.4111 | 15.3884 | 13.0705 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 13.2413 | 12.8379 | 12.3936 | 11.9489
|  | PLAISTOW | LW |  |  | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 15.6639 | 15.6212 | 15.5977 | 15.5801 | 15.5626 | 15.5454 | 15.5284 | 15.5115 | 15.4933 | 15.4752 | 15.4393 | 15.411 | 15.3891 | 13.102 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 13.227 | 12.8355 | 12.408 | 11.981
|  | PLAISTOW | ST |  |  | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 15.7335 | 15.6493 | 15.6092 | 15.5951 | 15.5782 | 15.5705 | 15.5629 | 15.5555 | 15.5474 | 15.5395 | 15.5238 | 15.4833 | 15.4415 | 15.4193 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 13.2387 | 12.9936
|  | PLAISTOW | FS |  |  | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 17.1271 | 15.7481 | 15.6878 | 15.6846 | 15.6662 | 15.6444 | 15.6281 | 15.6125 | 15.6092 | 15.606 | 15.6027 | 15.5965 | 15.5808 | 15.565 | 15.5495 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469 | 15.1469
MINETY GSP | STRATTON (2 X 90) | PLESSEY Swindon | MINIMUM HEADROOM | SU 16381 86720 | NO | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 21.1698 | 20.5151 | 20.5026 | 20.4889 | 20.4753 | 20.4617 | 20.4481 | 20.4345 | 20.42 | 20.4055 | 20.3949 | 20.3949 | 20.3949 | 20.3949 | 21.7346 | 21.634 | 21.6296 | 21.6249 | 21.6201 | 21.6154 | 21.6107 | 21.6059 | 21.6009 | 21.5959 | 21.5855 | 21.5431 | 21.5431 | 21.5431
|  | PLESSEY Swindon | CT |  |  | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 21.1706 | 20.5159 | 20.5045 | 20.492 | 20.4795 | 20.467 | 20.4545 | 20.442 | 20.4285 | 20.4151 | 20.3949 | 20.3949 | 20.3949 | 20.3949 | 21.7347 | 21.6343 | 21.6303 | 21.6259 | 21.6216 | 21.6173 | 21.6129 | 21.6085 | 21.6039 | 21.5992 | 21.59 | 21.5474 | 21.5431 | 21.5431
|  | PLESSEY Swindon | LW |  |  | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 21.1698 | 20.5151 | 20.5026 | 20.4889 | 20.4753 | 20.4617 | 20.4481 | 20.4345 | 20.42 | 20.4055 | 20.3949 | 20.3949 | 20.3949 | 20.3949 | 21.7346 | 21.634 | 21.6296 | 21.6249 | 21.6201 | 21.6154 | 21.6107 | 21.6059 | 21.6009 | 21.5959 | 21.5855 | 21.5431 | 21.5431 | 21.5431
|  | PLESSEY Swindon | ST |  |  | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 21.1748 | 21.1668 | 21.1502 | 21.1253 | 21.0954 | 21.057 | 21.019 | 20.9813 | 20.9407 | 20.9005 | 20.8224 | 20.5761 | 20.4629 | 20.3949 | 21.7353 | 21.7343 | 21.7322 | 21.729 | 21.7252 | 21.7204 | 21.7156 | 21.7108 | 21.7057 | 21.7006 | 21.6907 | 21.6552 | 21.6158 | 21.5768
|  | PLESSEY Swindon | FS |  |  | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 23.6006 | 21.1789 | 21.1776 | 21.1761 | 21.1698 | 21.1625 | 21.1506 | 21.1388 | 21.1237 | 21.1088 | 21.0942 | 21.0658 | 20.9694 | 20.8516 | 20.7244 | 21.7358 | 21.7356 | 21.7354 | 21.7346 | 21.7337 | 21.7322 | 21.7307 | 21.7288 | 21.7269 | 21.7251 | 21.7215 | 21.7093 | 21.6944 | 21.6783
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSY TITCHFIELD | MINIMUM HEADROOM | SZ 01091 90595 | NO | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 82.2486 | 82.1528 | 81.9466 | 81.7363 | 81.5331 | 81.3322 | 81.1335 | 80.9368 | 80.7246 | 80.5145 | 80.101 | 79.4281 | 78.7033 | 77.9809 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
|  | PLESSY TITCHFIELD | CT |  |  | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 82.2574 | 82.1758 | 81.9995 | 81.8208 | 81.6469 | 81.4729 | 81.2985 | 81.1259 | 80.9421 | 80.7617 | 80.408 | 79.7806 | 79.0829 | 78.3846 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
|  | PLESSY TITCHFIELD | LW |  |  | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 82.2486 | 82.1528 | 81.9466 | 81.7363 | 81.5331 | 81.3322 | 81.1335 | 80.9368 | 80.7246 | 80.5145 | 80.101 | 79.4281 | 78.7033 | 77.9809 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
|  | PLESSY TITCHFIELD | ST |  |  | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 82.5161 | 82.2211 | 82.1031 | 81.9375 | 81.7408 | 81.6621 | 81.5828 | 81.5047 | 81.422 | 81.3416 | 81.1861 | 80.7807 | 80.3433 | 79.9059 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
|  | PLESSY TITCHFIELD | FS |  |  | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 95.5068 | 82.7123 | 82.4368 | 82.4249 | 82.3878 | 82.3457 | 82.3184 | 82.2915 | 82.2573 | 82.2236 | 82.1907 | 82.1269 | 81.9668 | 81.7997 | 81.6324 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
LOVEDEAN GSP | WYMERING BSP | PORTCHESTER | MINIMUM HEADROOM | SU 62043 05575 | NO | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 13.7885 | 16.3674 | 16.3485 | 16.3136 | 16.2764 | 16.2395 | 16.203 | 16.1667 | 16.1307 | 16.1151 | 16.1151 | 14.0443 | 12.9283 | 11.6409 | 10.3488 | 14.1415 | 14.0689 | 13.9345 | 13.791 | 13.6492 | 13.5084 | 13.3689 | 13.2301 | 13.0804 | 12.9318 | 12.6375 | 11.525 | 10.2415 | 8.9533
|  | PORTCHESTER | CT |  |  | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 13.7885 | 16.3711 | 16.3575 | 16.3335 | 16.3081 | 16.2822 | 16.2559 | 16.2301 | 16.205 | 16.1778 | 16.151 | 16.1151 | 13.5204 | 12.3515 | 11.1716 | 14.1559 | 14.1033 | 14.0111 | 13.9135 | 13.8135 | 13.7121 | 13.6128 | 13.516 | 13.4115 | 13.3084 | 13.1039 | 12.1152 | 10.9499 | 9.7736
|  | PORTCHESTER | LW |  |  | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 13.7885 | 16.3674 | 16.3485 | 16.3136 | 16.2764 | 16.2395 | 16.203 | 16.1667 | 16.1307 | 16.1151 | 16.1151 | 14.0443 | 12.9283 | 11.6409 | 10.3488 | 14.1415 | 14.0689 | 13.9345 | 13.791 | 13.6492 | 13.5084 | 13.3689 | 13.2301 | 13.0804 | 12.9318 | 12.6375 | 11.525 | 10.2415 | 8.9533
|  | PORTCHESTER | ST |  |  | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 16.3797 | 16.3715 | 16.3591 | 16.3412 | 16.319 | 16.2819 | 16.2454 | 16.2098 | 16.1714 | 16.1337 | 16.1151 | 13.6034 | 12.7487 | 11.8944 | 14.1889 | 14.1574 | 14.1098 | 14.0406 | 13.9554 | 13.8122 | 13.6719 | 13.5349 | 13.3868 | 13.2417 | 12.9578 | 12.198 | 11.3459 | 10.4942
|  | PORTCHESTER | FS |  |  | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 19.2918 | 16.3878 | 16.3848 | 16.3832 | 16.377 | 16.3701 | 16.3589 | 16.3479 | 16.3337 | 16.3198 | 16.3061 | 16.2797 | 16.2117 | 16.1366 | 16.1151 | 14.22 | 14.2087 | 14.2026 | 14.1788 | 14.1521 | 14.109 | 14.0664 | 14.0119 | 13.9582 | 13.9057 | 13.8038 | 13.5419 | 13.2527 | 12.9447
CHICKERELL GSP | CHICKERELL BSP | PORTLAND | MINIMUM HEADROOM | SY 68307 73941 | YES | 20.2685 | 20.2664 | 20.2613 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 18.0064 | 17.4072 | 16.817 | 16.2306 | 19.2104 | 19.2006 | 19.1769 | 19.1529 | 19.1529 | 19.1529 | 18.0889 | 17.9859 | 17.8779 | 17.7676 | 17.5457 | 16.8358 | 16.1365 | 15.4419 | 18.0863 | 18.0663 | 18.0178 | 17.9597 | 17.893 | 17.82 | 17.7452 | 17.6651 | 17.5812 | 17.4954 | 17.3229 | 16.771 | 16.2274 | 15.6873
|  | PORTLAND | CT |  |  | 20.2685 | 20.2664 | 20.2613 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 18.0064 | 17.4072 | 16.817 | 16.2306 | 19.2106 | 19.201 | 19.1778 | 19.1529 | 19.1529 | 19.1529 | 19.1529 | 18.0114 | 17.9099 | 17.8064 | 17.5985 | 16.9737 | 16.3575 | 15.7453 | 18.0867 | 18.0671 | 18.0196 | 17.9634 | 17.8997 | 17.8306 | 17.7601 | 17.685 | 17.6061 | 17.5256 | 17.364 | 16.8782 | 16.3992 | 15.9232
|  | PORTLAND | LW |  |  | 20.2685 | 20.2664 | 20.2613 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 18.0064 | 17.4072 | 16.817 | 16.2306 | 19.2104 | 19.2006 | 19.1769 | 19.1529 | 19.1529 | 19.1529 | 18.0889 | 17.9859 | 17.8779 | 17.7676 | 17.5457 | 16.8358 | 16.1365 | 15.4419 | 18.0863 | 18.0663 | 18.0178 | 17.9597 | 17.893 | 17.82 | 17.7452 | 17.6651 | 17.5812 | 17.4954 | 17.3229 | 16.771 | 16.2274 | 15.6873
|  | PORTLAND | ST |  |  | 20.2693 | 20.2683 | 20.2661 | 20.2626 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 18.0658 | 17.5901 | 17.1374 | 16.6925 | 19.214 | 19.2095 | 19.1993 | 19.1833 | 19.1621 | 19.1529 | 19.1529 | 18.0819 | 17.9661 | 17.8492 | 17.6161 | 17.0524 | 16.5162 | 15.9891 | 18.0938 | 18.0845 | 18.0636 | 18.0308 | 17.9875 | 17.9059 | 17.824 | 17.7398 | 17.6497 | 17.5589 | 17.3777 | 16.9395 | 16.5225 | 16.1127
|  | PORTLAND | FS |  |  | 20.2697 | 20.2695 | 20.2692 | 20.2681 | 20.2667 | 20.2643 | 20.2619 | 20.2589 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 20.2586 | 19.2162 | 19.2153 | 19.2136 | 19.2086 | 19.202 | 19.1908 | 19.1797 | 19.1659 | 19.1529 | 19.1529 | 19.1529 | 18.0832 | 17.9093 | 17.7363 | 18.0983 | 18.0964 | 18.093 | 18.0826 | 18.0691 | 18.0462 | 18.0234 | 17.9951 | 17.9669 | 17.9383 | 17.881 | 17.7408 | 17.6056 | 17.4711
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH | MINIMUM HEADROOM | SZ 63405 99685 | NO | 37.6961 | 37.6187 | 37.4926 | 37.2783 | 37.0247 | 36.8282 | 36.6167 | 36.2648 | 35.8911 | 35.4897 | 34.6436 | 32.6151 | 32.038 | 31.5611 | 35.5614 | 35.5331 | 35.4866 | 35.4076 | 35.2411 | 35.0223 | 34.7868 | 34.3947 | 33.9784 | 33.5314 | 32.5896 | 30.2955 | 29.6382 | 29.1049 | 35.4781 | 35.3874 | 35.2395 | 34.9879 | 34.6904 | 34.46 | 34.2119 | 33.7992 | 33.3609 | 32.8902 | 31.8981 | 29.5215 | 28.8527 | 28.3039
|  | PORTSMOUTH | CT |  |  | 37.6961 | 37.6187 | 37.4926 | 37.2783 | 37.0247 | 36.8282 | 36.6167 | 36.2648 | 35.8911 | 35.4897 | 34.6436 | 32.6151 | 32.038 | 31.5611 | 35.5614 | 35.5344 | 35.4881 | 35.4139 | 35.2865 | 35.0782 | 34.8584 | 34.4872 | 34.0656 | 33.6049 | 32.6271 | 31.4737 | 31.0001 | 30.5572 | 35.4784 | 35.3935 | 35.2474 | 35.0124 | 34.735 | 34.515 | 34.2827 | 33.8913 | 33.4466 | 32.9606 | 31.9286 | 30.702 | 30.1911 | 29.7259
|  | PORTSMOUTH | LW |  |  | 37.6961 | 37.6187 | 37.4926 | 37.2783 | 37.0247 | 36.8282 | 36.6167 | 36.2648 | 35.8911 | 35.4897 | 34.6436 | 32.6151 | 32.038 | 31.5611 | 35.5616 | 35.5331 | 35.4866 | 35.4076 | 35.2411 | 35.0223 | 34.7868 | 34.3947 | 33.9784 | 33.5314 | 32.5896 | 30.2955 | 29.6382 | 29.1049 | 35.4781 | 35.3874 | 35.2395 | 34.9879 | 34.6904 | 34.46 | 34.2119 | 33.7992 | 33.3609 | 32.8902 | 31.8981 | 29.5215 | 28.8527 | 28.3039
|  | PORTSMOUTH | ST |  |  | 37.7274 | 37.6829 | 37.6133 | 37.4904 | 37.3406 | 37.1988 | 37.0506 | 36.8125 | 36.5365 | 36.2304 | 35.5658 | 34.8062 | 34.5174 | 34.2625 | 35.5733 | 35.5569 | 35.5312 | 35.486 | 35.4308 | 35.3786 | 35.2691 | 35.0033 | 34.6951 | 34.3532 | 33.6112 | 32.7655 | 32.448 | 32.17 | 35.5148 | 35.4626 | 35.3809 | 35.2366 | 35.0608 | 34.8944 | 34.7205 | 34.441 | 34.117 | 33.7576 | 32.9774 | 32.0866 | 31.7497 | 31.4531
|  | PORTSMOUTH | FS |  |  | 37.7526 | 37.7258 | 37.6892 | 37.6246 | 37.5538 | 37.4916 | 37.4259 | 37.3252 | 37.2168 | 37.1 | 36.8475 | 36.2591 | 35.9865 | 35.8666 | 35.5825 | 35.5727 | 35.5592 | 35.5354 | 35.5093 | 35.4864 | 35.4622 | 35.4251 | 35.3852 | 35.3242 | 35.0422 | 34.3859 | 34.083 | 33.951 | 35.5444 | 35.513 | 35.47 | 35.3942 | 35.3111 | 35.2381 | 35.161 | 35.0428 | 34.9156 | 34.7784 | 34.482 | 33.7915 | 33.4721 | 33.3321
BRAMLEY (ANDO-THAT) | ANDOVER BSP | PORTWAY | MINIMUM HEADROOM | SU 34402 46001 | YES | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 25.9552 | 25.8967 | 25.8379 | 25.7753 | 25.7131 | 25.5864 | 25.2057 | 24.8115 | 24.4102 | 31.7624 | 31.7604 | 31.7553 | 25.9979 | 25.8873 | 25.7764 | 25.6603 | 25.5436 | 25.4192 | 25.2958 | 25.0443 | 24.2887 | 23.5062 | 22.7207 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 25.9615 | 25.8662 | 25.7664 | 25.6661 | 25.5592 | 25.4482 | 25.1971 | 24.4431 | 23.6621 | 22.8783
|  | PORTWAY | CT |  |  | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 25.9552 | 25.8967 | 25.8379 | 25.7753 | 25.7131 | 25.5864 | 25.2057 | 24.8115 | 24.4102 | 31.7627 | 31.7612 | 31.7575 | 31.7535 | 25.9836 | 25.9006 | 25.812 | 25.7233 | 25.6305 | 25.5392 | 25.3525 | 24.6649 | 23.9473 | 23.2275 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 25.9729 | 25.8968 | 25.8205 | 25.7407 | 25.6623 | 25.5018 | 24.8185 | 24.1024 | 23.384
|  | PORTWAY | LW |  |  | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 25.9552 | 25.8967 | 25.8379 | 25.7753 | 25.7131 | 25.5864 | 25.2057 | 24.8115 | 24.4102 | 31.7624 | 31.7604 | 31.7553 | 25.9979 | 25.8873 | 25.7764 | 25.6603 | 25.5436 | 25.4192 | 25.2958 | 25.0443 | 24.2887 | 23.5062 | 22.7207 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 25.9615 | 25.8662 | 25.7664 | 25.6661 | 25.5592 | 25.4482 | 25.1971 | 24.4431 | 23.6621 | 22.8783
|  | PORTWAY | ST |  |  | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 25.9827 | 25.9371 | 25.8888 | 25.8413 | 25.7458 | 25.4936 | 25.2414 | 24.9905 | 31.763 | 31.7619 | 31.7593 | 31.7554 | 31.7506 | 25.9222 | 25.831 | 25.7405 | 25.6445 | 25.5503 | 25.3608 | 24.8601 | 24.3596 | 23.8616 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 25.9915 | 25.9131 | 25.8353 | 25.7528 | 25.6718 | 25.509 | 25.0133 | 24.5138 | 24.0169
|  | PORTWAY | FS |  |  | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 34.5698 | 25.9649 | 25.8706 | 25.7761 | 31.7636 | 31.7635 | 31.7633 | 31.7624 | 31.7612 | 31.7598 | 31.7583 | 31.7564 | 31.7546 | 31.7527 | 25.9811 | 25.7956 | 25.6084 | 25.421 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 32.6501 | 25.8827 | 25.7218 | 25.5607
IVER 132KV | LONGFORD | POYLE | MINIMUM HEADROOM | TQ 03425 75555 | NO | 116.5347 | 116.5128 | 116.4931 | 116.4835 | 116.4738 | 116.4641 | 116.4545 | 116.445 | 116.4346 | 116.4241 | 116.3866 | 116.2968 | 116.204 | 116.1465 | 116.2547 | 116.2306 | 116.1843 | 116.1508 | 116.1173 | 116.084 | 116.0507 | 116.0176 | 115.982 | 115.9456 | 115.816 | 115.5055 | 115.1846 | 114.8654 | 111.5564 | 111.545 | 111.5176 | 111.4877 | 111.4577 | 111.4279 | 111.3981 | 111.3685 | 111.3366 | 111.3041 | 111.1882 | 110.9103 | 110.7772 | 110.7772
|  | POYLE | CT |  |  | 116.5347 | 116.5128 | 116.4931 | 116.4835 | 116.4738 | 116.4641 | 116.4545 | 116.445 | 116.4346 | 116.4241 | 116.3866 | 116.2968 | 116.204 | 116.1465 | 116.2557 | 116.2332 | 116.1875 | 116.1562 | 116.1248 | 116.0935 | 116.0623 | 116.0313 | 115.9978 | 115.9644 | 115.8499 | 115.5842 | 115.3077 | 115.033 | 111.5568 | 111.5462 | 111.5205 | 111.4924 | 111.4644 | 111.4364 | 111.4085 | 111.3808 | 111.3508 | 111.3209 | 111.2185 | 110.9808 | 110.7772 | 110.7772
|  | POYLE | LW |  |  | 116.5347 | 116.5128 | 116.4931 | 116.4835 | 116.4738 | 116.4641 | 116.4545 | 116.445 | 116.4346 | 116.4241 | 116.3866 | 116.2968 | 116.204 | 116.1465 | 116.2547 | 116.2306 | 116.1843 | 116.1508 | 116.1173 | 116.084 | 116.0507 | 116.0176 | 115.982 | 115.9456 | 115.816 | 115.5055 | 115.1846 | 114.8654 | 111.5564 | 111.545 | 111.5176 | 111.4877 | 111.4577 | 111.4279 | 111.3981 | 111.3685 | 111.3366 | 111.3041 | 111.1882 | 110.9103 | 110.7772 | 110.7772
|  | POYLE | ST |  |  | 116.8267 | 116.5375 | 116.5214 | 116.4993 | 116.4943 | 116.4822 | 116.4703 | 116.4586 | 116.4459 | 116.4333 | 116.3986 | 116.3328 | 116.267 | 116.2017 | 116.5755 | 116.2577 | 116.24 | 116.2132 | 116.1883 | 116.1466 | 116.1054 | 116.0648 | 116.0208 | 115.9775 | 115.8572 | 115.6297 | 115.4024 | 115.1766 | 111.7737 | 111.5578 | 111.5494 | 111.5367 | 111.5212 | 111.4839 | 111.447 | 111.4107 | 111.3714 | 111.3326 | 111.225 | 111.0215 | 110.8182 | 110.7772
|  | POYLE | FS |  |  | 116.8302 | 116.7477 | 116.5455 | 116.5364 | 116.5257 | 116.5051 | 116.4972 | 116.4928 | 116.4884 | 116.4841 | 116.4719 | 116.4496 | 116.4272 | 116.4057 | 116.5794 | 116.4887 | 116.2665 | 116.2566 | 116.2447 | 116.2221 | 116.1995 | 116.1831 | 116.1679 | 116.153 | 116.1109 | 116.0336 | 115.9561 | 115.8821 | 111.7769 | 111.7025 | 111.5619 | 111.5573 | 111.5517 | 111.5409 | 111.5303 | 111.5165 | 111.503 | 111.4896 | 111.452 | 111.3828 | 111.3135 | 111.2473
MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON SE | MINIMUM HEADROOM | SU 16963 86368 | NO | 9.4922 | 9.4813 | 9.4568 | 9.4301 | 9.4034 | 9.3737 | 9.3127 | 9.2522 | 9.1872 | 9.1231 | 8.9985 | 8.5988 | 8.0641 | 7.4737 | 9.4915 | 9.4795 | 9.4528 | 9.4235 | 9.3943 | 9.3619 | 9.2951 | 9.229 | 9.1579 | 9.0878 | 8.9515 | 8.5144 | 7.9295 | 7.2838 | 13.7574 | 13.7544 | 13.7475 | 13.74 | 13.7325 | 13.7241 | 13.7069 | 13.69 | 13.6717 | 13.6536 | 13.62 | 13.547 | 13.4588 | 13.4588
|  | PRESSED STEEL SWINDON SE | CT |  |  | 9.4922 | 9.4813 | 9.4568 | 9.4301 | 9.4034 | 9.3766 | 9.3498 | 9.3229 | 9.2943 | 9.266 | 9.2063 | 8.6534 | 8.0641 | 7.4737 | 9.4924 | 9.4819 | 9.4584 | 9.4328 | 9.4071 | 9.3813 | 9.3553 | 9.3291 | 9.301 | 9.273 | 9.2183 | 8.739 | 8.1843 | 7.6207 | 13.7577 | 13.755 | 13.7489 | 13.7423 | 13.7357 | 13.7291 | 13.7224 | 13.7157 | 13.7085 | 13.7013 | 13.6872 | 13.5845 | 13.492 | 13.4588
|  | PRESSED STEEL SWINDON SE | LW |  |  | 9.4922 | 9.4813 | 9.4568 | 9.4301 | 9.4034 | 9.3766 | 9.3498 | 9.3229 | 9.2943 | 9.266 | 9.2063 | 8.6534 | 8.0641 | 7.4737 | 9.4915 | 9.4795 | 9.4528 | 9.4235 | 9.3943 | 9.365 | 9.3357 | 9.3063 | 9.2751 | 9.2441 | 9.1787 | 8.5741 | 7.9295 | 7.2838 | 13.7574 | 13.7544 | 13.7475 | 13.74 | 13.7325 | 13.7249 | 13.7174 | 13.7098 | 13.7018 | 13.6938 | 13.677 | 13.557 | 13.4588 | 13.4588
|  | PRESSED STEEL SWINDON SE | ST |  |  | 9.4956 | 9.4895 | 9.4768 | 9.4581 | 9.4356 | 9.3737 | 9.3127 | 9.2522 | 9.1872 | 9.1231 | 8.9985 | 8.5988 | 8.1678 | 7.7401 | 9.4952 | 9.4885 | 9.4747 | 9.4541 | 9.4295 | 9.3619 | 9.2951 | 9.229 | 9.1579 | 9.0878 | 8.9515 | 8.5144 | 8.0429 | 7.5751 | 13.7584 | 13.7567 | 13.7531 | 13.7478 | 13.7415 | 13.7241 | 13.7069 | 13.69 | 13.6717 | 13.6536 | 13.62 | 13.547 | 13.4684 | 13.4588
|  | PRESSED STEEL SWINDON SE | FS |  |  | 9.4988 | 9.4977 | 9.4965 | 9.4918 | 9.4864 | 9.4706 | 9.455 | 9.435 | 9.4153 | 9.3959 | 9.3584 | 9.2386 | 9.0968 | 8.9463 | 9.4987 | 9.4975 | 9.4961 | 9.4911 | 9.4851 | 9.4679 | 9.4508 | 9.4289 | 9.4074 | 9.3862 | 9.3451 | 9.2141 | 9.059 | 8.8945 | 13.7593 | 13.759 | 13.7586 | 13.7573 | 13.7558 | 13.7514 | 13.747 | 13.7413 | 13.7358 | 13.7304 | 13.7198 | 13.6861 | 13.6462 | 13.6105
BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER | MINIMUM HEADROOM | SU 60879 41131 | NO | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 38.8943 | 38.8546 | 38.7813 | 38.6995 | 38.6233 | 38.5655 | 38.5086 | 38.4506 | 38.39 | 38.3299 | 38.2124 | 38.0992 | 38.0992 | 38.0992 | 41.7617 | 41.7452 | 41.7146 | 41.6805 | 41.6488 | 41.6247 | 41.601 | 41.5814 | 41.5667 | 41.5522 | 41.5237 | 41.4889 | 41.4528 | 41.4172
|  | PRESTON CANDOVER | CT |  |  | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 38.8974 | 38.864 | 38.8019 | 38.7333 | 38.6689 | 38.6193 | 38.567 | 38.5118 | 38.4536 | 38.3986 | 38.2982 | 38.1439 | 38.0992 | 38.0992 | 41.763 | 41.7491 | 41.7232 | 41.6946 | 41.6678 | 41.6471 | 41.6253 | 41.6023 | 41.5821 | 41.5688 | 41.5445 | 41.5071 | 41.4684 | 41.4303
|  | PRESTON CANDOVER | LW |  |  | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 38.8943 | 38.8546 | 38.7813 | 38.6995 | 38.6233 | 38.5655 | 38.5086 | 38.4506 | 38.39 | 38.3299 | 38.2124 | 38.0992 | 38.0992 | 38.0992 | 41.7617 | 41.7452 | 41.7146 | 41.6805 | 41.6488 | 41.6247 | 41.601 | 41.5814 | 41.5667 | 41.5522 | 41.5237 | 41.4889 | 41.4528 | 41.4172
|  | PRESTON CANDOVER | ST |  |  | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 38.9235 | 38.8828 | 38.8416 | 38.7836 | 38.7191 | 38.7014 | 38.6816 | 38.6599 | 38.6372 | 38.6165 | 38.5815 | 38.4997 | 38.4176 | 38.3358 | 41.7739 | 41.7569 | 41.7397 | 41.7156 | 41.6887 | 41.6813 | 41.6731 | 41.664 | 41.6546 | 41.6459 | 41.6314 | 41.5973 | 41.5734 | 41.5536
|  | PRESTON CANDOVER | FS |  |  | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 44.3645 | 38.9358 | 38.9278 | 38.9193 | 38.9021 | 38.885 | 38.8775 | 38.8699 | 38.8603 | 38.8513 | 38.8426 | 38.8259 | 38.7901 | 38.7565 | 38.7245 | 41.779 | 41.7757 | 41.7721 | 41.765 | 41.7578 | 41.7547 | 41.7515 | 41.7475 | 41.7438 | 41.7402 | 41.7332 | 41.7183 | 41.7043 | 41.6909
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN | MINIMUM HEADROOM | SY 74226 95039 | YES | 13.796 | 13.7945 | 13.7925 | 13.7899 | 13.7866 | 13.7827 | 13.7779 | 13.7723 | 13.766 | 13.7589 | 13.7415 | 13.6794 | 13.5916 | 13.4798 | 10.9804 | 10.9669 | 10.9381 | 10.9063 | 10.8723 | 10.8377 | 10.8024 | 10.7666 | 10.728 | 10.6888 | 10.6089 | 10.4575 | 10.2719 | 10.1283 | 5.9789 | 5.9746 | 5.9681 | 5.9611 | 5.9535 | 5.9453 | 5.9364 | 5.927 | 5.9162 | 5.9042 | 5.8764 | 5.7854 | 5.6692 | 5.5305
|  | PUDDLETOWN | CT |  |  | 13.796 | 13.7945 | 13.7925 | 13.7899 | 13.7866 | 13.7827 | 13.7779 | 13.7723 | 13.766 | 13.7589 | 13.7415 | 13.6794 | 13.5916 | 13.4798 | 10.9804 | 10.9669 | 10.9381 | 10.9065 | 10.8741 | 10.8411 | 10.8074 | 10.7733 | 10.7362 | 10.6982 | 10.6194 | 10.4575 | 10.2719 | 10.1283 | 5.9789 | 5.9746 | 5.9681 | 5.9611 | 5.9535 | 5.9453 | 5.9364 | 5.927 | 5.9162 | 5.9042 | 5.8764 | 5.7854 | 5.6692 | 5.5305
|  | PUDDLETOWN | LW |  |  | 13.796 | 13.7945 | 13.7925 | 13.7899 | 13.7866 | 13.7827 | 13.7779 | 13.7723 | 13.766 | 13.7589 | 13.7415 | 13.6794 | 13.5916 | 13.4798 | 10.9824 | 10.9693 | 10.9394 | 10.9063 | 10.8723 | 10.8377 | 10.8024 | 10.7666 | 10.728 | 10.6888 | 10.6089 | 10.4786 | 10.3367 | 10.228 | 5.9829 | 5.9816 | 5.9798 | 5.9775 | 5.9746 | 5.9711 | 5.9668 | 5.9619 | 5.9563 | 5.9499 | 5.9344 | 5.8792 | 5.8011 | 5.7016
|  | PUDDLETOWN | ST |  |  | 13.7974 | 13.7969 | 13.7962 | 13.7954 | 13.7944 | 13.7931 | 13.7916 | 13.7899 | 13.7882 | 13.7863 | 13.7822 | 13.7672 | 13.7441 | 13.716 | 11.0172 | 10.9786 | 10.9612 | 10.935 | 10.9033 | 10.8929 | 10.8821 | 10.8713 | 10.8596 | 10.8479 | 10.8245 | 10.7634 | 10.6972 | 10.6275 | 5.9842 | 5.9837 | 5.9831 | 5.9824 | 5.9815 | 5.9803 | 5.979 | 5.9775 | 5.976 | 5.9743 | 5.9707 | 5.9573 | 5.9367 | 5.9118
|  | PUDDLETOWN | FS |  |  | 13.7976 | 13.7973 | 13.7969 | 13.7963 | 13.7957 | 13.7951 | 13.7944 | 13.7937 | 13.7929 | 13.7921 | 13.7904 | 13.784 | 13.7759 | 13.7671 | 11.0216 | 11.0205 | 11.0192 | 11.0134 | 11.0065 | 11.0026 | 10.9986 | 10.9937 | 10.9888 | 10.984 | 10.9742 | 10.9489 | 10.9229 | 10.8969 | 5.9844 | 5.9841 | 5.9837 | 5.9832 | 5.9827 | 5.9821 | 5.9815 | 5.9809 | 5.9802 | 5.9795 | 5.978 | 5.9722 | 5.965 | 5.9572
AXMINSTER | YEOVIL BSP | PULHAM | MINIMUM HEADROOM | ST 71579 09451 | YES | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 4.6397 | 4.4548 | 4.2552 | 4.7383 | 4.7209 | 4.6794 | 4.6337 | 4.5873 | 4.5406 | 4.4937 | 4.447 | 4.3969 | 4.3471 | 4.2482 | 4.0159 | 3.7779 | 3.5419 | 4.7383 | 4.721 | 4.6796 | 4.6341 | 4.5878 | 4.5412 | 4.4945 | 4.4479 | 4.398 | 4.3483 | 4.2497 | 4.0182 | 3.7809 | 3.5456
|  | PULHAM | CT |  |  | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 4.6397 | 4.4548 | 4.2552 | 4.7403 | 4.7259 | 4.6914 | 4.6535 | 4.6148 | 4.5759 | 4.5369 | 4.4979 | 4.4562 | 4.4146 | 4.3321 | 4.0987 | 3.8594 | 3.6224 | 4.7403 | 4.726 | 4.6916 | 4.6538 | 4.6153 | 4.5765 | 4.5375 | 4.4987 | 4.4571 | 4.4157 | 4.3334 | 4.1007 | 3.8621 | 3.6258
|  | PULHAM | LW |  |  | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 4.6397 | 4.4548 | 4.2552 | 4.7383 | 4.7209 | 4.6794 | 4.6337 | 4.5873 | 4.5406 | 4.4937 | 4.447 | 4.3969 | 4.3471 | 4.2482 | 4.0159 | 3.7779 | 3.5419 | 4.7383 | 4.721 | 4.6796 | 4.6341 | 4.5878 | 4.5412 | 4.4945 | 4.4479 | 4.398 | 4.3483 | 4.2497 | 4.0182 | 3.7809 | 3.5456
|  | PULHAM | ST |  |  | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 4.6836 | 4.5593 | 4.7432 | 4.7323 | 4.7084 | 4.6722 | 4.6281 | 4.5958 | 4.5635 | 4.5316 | 4.4973 | 4.4633 | 4.3963 | 4.2334 | 4.0724 | 3.9124 | 4.7432 | 4.7323 | 4.7085 | 4.6724 | 4.6285 | 4.5962 | 4.5641 | 4.5323 | 4.498 | 4.4641 | 4.3974 | 4.235 | 4.0745 | 3.915
|  | PULHAM | FS |  |  | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 7.1967 | 4.7491 | 4.7479 | 4.7463 | 4.7386 | 4.7292 | 4.7194 | 4.7095 | 4.6971 | 4.6848 | 4.6727 | 4.6489 | 4.5915 | 4.5364 | 4.4833 | 4.7491 | 4.7479 | 4.7463 | 4.7386 | 4.7293 | 4.7194 | 4.7096 | 4.6973 | 4.685 | 4.6729 | 4.6492 | 4.592 | 4.537 | 4.4841
LOVEDEAN GSP | FORT WIDLEY | PURBROOK | MINIMUM HEADROOM | SU 67047 07819 | NO | 22.1149 | 22.1121 | 22.1064 | 22.0951 | 22.0738 | 22.0494 | 22.0123 | 21.9703 | 21.9233 | 21.8733 | 21.7631 | 21.4298 | 21.0459 | 20.6363 | 8.3284 | 8.3273 | 8.3258 | 8.324 | 8.322 | 8.3198 | 8.3175 | 8.3151 | 8.3117 | 8.308 | 8.2993 | 8.2694 | 7.8776 | 7.1629 | 8.4343 | 8.4317 | 8.4273 | 8.4217 | 8.4148 | 8.4072 | 8.3992 | 8.3907 | 8.3799 | 8.3678 | 8.3395 | 8.2416 | 8.1201 | 7.9796
|  | PURBROOK | CT |  |  | 22.1149 | 22.1121 | 22.1064 | 22.0951 | 22.0738 | 22.0494 | 22.0215 | 21.9913 | 21.9566 | 21.9183 | 21.8246 | 21.4298 | 21.0459 | 20.6363 | 8.3284 | 8.3273 | 8.3258 | 8.324 | 8.322 | 8.3198 | 8.3175 | 8.3151 | 8.3117 | 8.308 | 8.2993 | 8.2694 | 7.8787 | 7.2171 | 8.4343 | 8.4317 | 8.4273 | 8.4217 | 8.4148 | 8.4072 | 8.3992 | 8.3907 | 8.3799 | 8.3678 | 8.3395 | 8.2416 | 8.1201 | 7.9796
|  | PURBROOK | LW |  |  | 22.1149 | 22.1121 | 22.1064 | 22.0951 | 22.0738 | 22.0494 | 22.0215 | 21.9913 | 21.9566 | 21.9183 | 21.8246 | 21.4298 | 21.0459 | 20.6363 | 8.3293 | 8.329 | 8.3286 | 8.328 | 8.3273 | 8.3265 | 8.3255 | 8.3243 | 8.3226 | 8.3208 | 8.3163 | 8.3002 | 7.8776 | 7.1629 | 8.4364 | 8.4355 | 8.4341 | 8.4317 | 8.4278 | 8.4233 | 8.418 | 8.4121 | 8.405 | 8.397 | 8.3775 | 8.3001 | 8.2075 | 8.0927
|  | PURBROOK | ST |  |  | 22.1164 | 22.1152 | 22.1129 | 22.1066 | 22.0942 | 22.0535 | 22.0123 | 21.9703 | 21.9233 | 21.8733 | 21.7631 | 21.5099 | 21.2818 | 21.0536 | 8.3296 | 8.3295 | 8.3294 | 8.3292 | 8.329 | 8.3287 | 8.3284 | 8.328 | 8.3276 | 8.3272 | 8.3262 | 8.3224 | 8.2312 | 7.7978 | 8.4371 | 8.4368 | 8.4362 | 8.4351 | 8.4332 | 8.4274 | 8.4215 | 8.4155 | 8.4087 | 8.4015 | 8.3856 | 8.3465 | 8.3065 | 8.2624
|  | PURBROOK | FS |  |  | 22.1169 | 22.1166 | 22.1162 | 22.1136 | 22.1085 | 22.095 | 22.0812 | 22.0643 | 22.0468 | 22.0288 | 21.9901 | 21.896 | 21.8104 | 21.7269 | 8.3297 | 8.3296 | 8.3295 | 8.3294 | 8.3293 | 8.3291 | 8.329 | 8.3288 | 8.3287 | 8.3285 | 8.3281 | 8.3268 | 8.3248 | 8.3227 | 8.4372 | 8.4371 | 8.4369 | 8.4363 | 8.4355 | 8.4335 | 8.4315 | 8.429 | 8.4265 | 8.4239 | 8.4182 | 8.4038 | 8.3895 | 8.3752
MINETY GSP | TOOTHILL BSP | QUARRY ROAD | MINIMUM HEADROOM | SU 15334 83380 | YES | 15.0047 | 14.9154 | 14.7282 | 14.5217 | 14.3114 | 14.097 | 13.8783 | 13.6554 | 13.4524 | 13.2637 | 12.8896 | 11.6122 | 10.2772 | 8.951 | 15.4982 | 15.393 | 15.1725 | 14.9292 | 14.6815 | 14.4289 | 14.1713 | 13.9087 | 13.6696 | 13.4473 | 13.0066 | 11.5018 | 9.9292 | 8.3668 | 15.6682 | 15.5672 | 15.3554 | 15.1217 | 14.8837 | 14.6411 | 14.3937 | 14.1415 | 13.9117 | 13.6982 | 13.2749 | 11.8295 | 10.319 | 8.8183
|  | QUARRY ROAD | CT |  |  | 15.0047 | 14.9154 | 14.7282 | 14.5217 | 14.3114 | 14.097 | 13.8783 | 13.6554 | 13.4524 | 13.2637 | 12.8896 | 11.6122 | 10.2772 | 8.951 | 15.5022 | 15.4054 | 15.1993 | 14.9731 | 14.7422 | 14.505 | 14.2635 | 14.0147 | 13.7794 | 13.5543 | 13.12 | 11.644 | 10.0642 | 8.4867 | 15.6721 | 15.5791 | 15.3811 | 15.1638 | 14.9421 | 14.7142 | 14.4822 | 14.2433 | 14.0172 | 13.801 | 13.3839 | 11.9661 | 10.4486 | 8.9335
|  | QUARRY ROAD | LW |  |  | 15.0047 | 14.9154 | 14.7282 | 14.5217 | 14.3114 | 14.097 | 13.8783 | 13.6554 | 13.4524 | 13.2637 | 12.8896 | 11.6122 | 10.2772 | 8.951 | 15.4982 | 15.393 | 15.1725 | 14.9292 | 14.6815 | 14.4289 | 14.1713 | 13.9087 | 13.6696 | 13.4473 | 13.0066 | 11.5018 | 9.9292 | 8.3668 | 15.6682 | 15.5672 | 15.3554 | 15.1217 | 14.8837 | 14.6411 | 14.3937 | 14.1415 | 13.9117 | 13.6982 | 13.2749 | 11.8295 | 10.319 | 8.8183
|  | QUARRY ROAD | ST |  |  | 15.0409 | 15.0025 | 14.9318 | 14.8298 | 14.7067 | 14.5604 | 14.4123 | 14.2607 | 14.1153 | 13.9765 | 13.7107 | 12.9666 | 12.1965 | 11.432 | 15.5409 | 15.4957 | 15.4123 | 15.2922 | 15.1472 | 14.9749 | 14.8004 | 14.6218 | 14.4505 | 14.287 | 13.9738 | 13.0973 | 12.1901 | 11.2895 | 15.7092 | 15.6658 | 15.5857 | 15.4703 | 15.331 | 15.1655 | 14.9979 | 14.8264 | 14.6618 | 14.5048 | 14.204 | 13.3621 | 12.4907 | 11.6257
|  | QUARRY ROAD | FS |  |  | 15.0597 | 15.0473 | 15.0338 | 14.9954 | 14.9507 | 14.8967 | 14.842 | 14.774 | 14.7136 | 14.6566 | 14.5454 | 14.2502 | 13.942 | 13.6306 | 15.563 | 15.5485 | 15.5325 | 15.4872 | 15.4346 | 15.371 | 15.3065 | 15.2265 | 15.1553 | 15.0881 | 14.9572 | 14.6094 | 14.2463 | 13.8795 | 15.7304 | 15.7165 | 15.7012 | 15.6577 | 15.6071 | 15.546 | 15.4841 | 15.4072 | 15.3388 | 15.2743 | 15.1485 | 14.8144 | 14.4657 | 14.1134
BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD | MINIMUM HEADROOM | SU 87062 55683 | NO | 9.4717 | 9.3885 | 9.3171 | 9.2388 | 9.1628 | 8.9996 | 8.7846 | 8.5507 | 8.3042 | 8.0649 | 7.8634 | 7.3 | 6.7419 | 6.1898 | 10.8497 | 10.8447 | 10.8405 | 10.8358 | 10.8313 | 10.8216 | 10.8088 | 10.7948 | 9.4426 | 9.1608 | 8.9234 | 8.2597 | 7.6023 | 6.9519 | 9.4668 | 9.369 | 9.2852 | 9.1933 | 9.104 | 8.9123 | 8.6598 | 8.3851 | 8.0956 | 7.8146 | 7.5779 | 6.9163 | 6.2608 | 5.6124
|  | QUEENSMEAD | CT |  |  | 9.4717 | 9.3885 | 9.3171 | 9.2388 | 9.1628 | 8.9996 | 8.7846 | 8.5507 | 8.3042 | 8.0649 | 7.8634 | 7.3 | 6.7419 | 6.1898 | 10.8498 | 10.8456 | 10.8419 | 10.8379 | 10.8339 | 10.8249 | 10.8137 | 10.8019 | 10.7926 | 9.3717 | 9.0974 | 8.3262 | 7.632 | 6.9587 | 9.4698 | 9.3862 | 9.3139 | 9.2349 | 9.1558 | 8.9792 | 8.7566 | 8.5254 | 8.2784 | 8.0249 | 7.7514 | 6.9826 | 6.2905 | 5.6192
|  | QUEENSMEAD | LW |  |  | 9.4717 | 9.3885 | 9.3171 | 9.2388 | 9.1628 | 8.9996 | 8.7846 | 8.5507 | 8.3042 | 8.0649 | 7.8634 | 7.3 | 6.7419 | 6.1898 | 10.8497 | 10.8447 | 10.8405 | 10.8358 | 10.8313 | 10.8216 | 10.8088 | 10.7948 | 9.4426 | 9.1608 | 8.9234 | 8.2597 | 7.6023 | 6.9519 | 9.4668 | 9.369 | 9.2852 | 9.1933 | 9.104 | 8.9123 | 8.6598 | 8.3851 | 8.0956 | 7.8146 | 7.5779 | 6.9163 | 6.2608 | 5.6124
|  | QUEENSMEAD | ST |  |  | 9.4834 | 9.4356 | 9.4006 | 9.3475 | 9.2833 | 9.158 | 9.0071 | 8.852 | 8.6832 | 8.5085 | 8.3 | 7.8724 | 7.5077 | 7.1528 | 10.8504 | 10.8475 | 10.8454 | 10.8423 | 10.8384 | 10.831 | 10.822 | 10.8128 | 10.8027 | 10.7926 | 9.4377 | 8.934 | 8.5044 | 8.0863 | 9.4805 | 9.4244 | 9.3832 | 9.3209 | 9.2455 | 9.0983 | 8.9212 | 8.739 | 8.5407 | 8.3356 | 8.0907 | 7.5885 | 7.1602 | 6.7434
|  | QUEENSMEAD | FS |  |  | 9.4938 | 9.4727 | 9.4697 | 9.4561 | 9.4395 | 9.3939 | 9.3384 | 9.2738 | 9.2053 | 9.1353 | 9.0569 | 8.8887 | 8.7544 | 8.6298 | 10.851 | 10.8497 | 10.8495 | 10.8487 | 10.8477 | 10.845 | 10.8417 | 10.8379 | 10.8338 | 10.8296 | 10.825 | 10.815 | 10.807 | 10.7995 | 9.4928 | 9.468 | 9.4644 | 9.4485 | 9.429 | 9.3754 | 9.3102 | 9.2343 | 9.1539 | 9.0717 | 8.9796 | 8.7821 | 8.6243 | 8.478
MELKSHAM GSP | WEST GRAFTON | RAMSBURY | MINIMUM HEADROOM | SU 27380 72108 | YES | 14.0971 | 14.0934 | 14.0846 | 14.0751 | 14.0654 | 14.0556 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 14.0987 | 14.0882 | 14.0633 | 14.0364 | 14.009 | 13.9814 | 13.9768 | 13.9733 | 13.9694 | 13.9694 | 13.9694 | 13.9694 | 13.9694 | 13.9694
|  | RAMSBURY | CT |  |  | 14.0971 | 14.0934 | 14.0846 | 14.0751 | 14.0654 | 14.0556 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 14.0997 | 14.0907 | 14.0692 | 14.046 | 14.0225 | 13.9988 | 13.9796 | 13.9765 | 13.9732 | 13.9699 | 13.9694 | 13.9694 | 13.9694 | 13.9694
|  | RAMSBURY | LW |  |  | 14.0971 | 14.0934 | 14.0846 | 14.0751 | 14.0654 | 14.0556 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 14.0987 | 14.0882 | 14.0633 | 14.0364 | 14.009 | 13.9814 | 13.9768 | 13.9733 | 13.9694 | 13.9694 | 13.9694 | 13.9694 | 13.9694 | 13.9694
|  | RAMSBURY | ST |  |  | 14.0987 | 14.0974 | 14.0944 | 14.0899 | 14.0844 | 14.0788 | 14.0732 | 14.0677 | 14.0616 | 14.0556 | 14.0496 | 14.0496 | 14.0496 | 14.0496 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 14.1033 | 14.0994 | 14.091 | 14.0784 | 14.0627 | 14.047 | 14.0311 | 14.0154 | 13.9982 | 13.9812 | 13.976 | 13.9694 | 13.9694 | 13.9694
|  | RAMSBURY | FS |  |  | 14.1136 | 14.0992 | 14.0989 | 14.0973 | 14.0954 | 14.0935 | 14.0916 | 14.0891 | 14.0867 | 14.0842 | 14.0793 | 14.067 | 14.0548 | 14.0496 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 13.6806 | 14.1454 | 14.1046 | 14.1038 | 14.0993 | 14.0939 | 14.0885 | 14.0831 | 14.0761 | 14.0691 | 14.0622 | 14.0484 | 14.0136 | 13.9801 | 13.9757
BRAMLEY (FLEE) | READING BSP | READING | MINIMUM HEADROOM | SU 74591 73788 | NO | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 39.5581 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 34.9488 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 34.9908
|  | READING | CT |  |  | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 39.5581 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 34.9488 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 34.9908
|  | READING | LW |  |  | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 39.5581 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 35.2008 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 35.2421
|  | READING | ST |  |  | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484
|  | READING | FS |  |  | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 51.0584 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484 | 48.7484
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN | MINIMUM HEADROOM | SU 71540 74122 | NO | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 91.7731 | 91.6358 | 91.3977 | 91.122 | 90.8408 | 90.5943 | 90.4808 | 90.4085 | 90.3374 | 90.2656 | 90.2259 | 78.6756 | 77.0365 | 75.4513 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 78.4799 | 76.8942
|  | READING TOWN | CT |  |  | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 91.7731 | 91.6424 | 91.4057 | 91.1359 | 90.8601 | 90.6025 | 90.4862 | 90.4086 | 90.3374 | 90.2656 | 90.2259 | 78.6756 | 77.0365 | 75.4513 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 78.4799 | 76.8942
|  | READING TOWN | LW |  |  | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 91.7734 | 91.6358 | 91.3977 | 91.122 | 90.8408 | 90.5943 | 90.4808 | 90.4085 | 90.3426 | 90.2769 | 90.2259 | 79.1686 | 77.6761 | 76.209 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 79.1197 | 77.6522
|  | READING TOWN | ST |  |  | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 91.8536 | 91.7746 | 91.7064 | 91.6112 | 91.5016 | 91.3878 | 91.2759 | 91.1578 | 91.0311 | 90.9006 | 90.6341 | 90.4537 | 90.3794 | 90.3075 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283
|  | READING TOWN | FS |  |  | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 101.9785 | 91.8714 | 91.8164 | 91.7888 | 91.7339 | 91.6732 | 91.625 | 91.5794 | 91.5269 | 91.4747 | 91.422 | 91.3123 | 91.131 | 90.995 | 90.8747 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283 | 93.283
MANNINGTON GSP | REDHILL BSP | REDHILL | MINIMUM HEADROOM | SZ 08512 96149 | YES | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 69.4877 | 69.4747 | 69.441 | 69.3965 | 69.3417 | 69.2856 | 69.229 | 69.1554 | 69.071 | 68.9854 | 68.8266 | 68.4634 | 67.9846 | 67.4611 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
|  | REDHILL | CT |  |  | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 69.4879 | 69.4759 | 69.4445 | 69.404 | 69.3551 | 69.3049 | 69.2539 | 69.2018 | 69.156 | 69.1078 | 69.026 | 68.5844 | 68.1306 | 67.6758 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
|  | REDHILL | LW |  |  | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 69.4877 | 69.4747 | 69.441 | 69.3965 | 69.3417 | 69.2856 | 69.229 | 69.1752 | 69.132 | 69.0877 | 69.009 | 68.5068 | 67.9846 | 67.4611 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
|  | REDHILL | ST |  |  | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 69.7263 | 69.4836 | 69.4665 | 69.4412 | 69.4083 | 69.3237 | 69.2395 | 69.1554 | 69.071 | 68.9854 | 68.8266 | 68.4634 | 68.1054 | 67.7486 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
|  | REDHILL | FS |  |  | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 75.1862 | 70.089 | 69.4891 | 69.4826 | 69.4721 | 69.4591 | 69.431 | 69.4033 | 69.3713 | 69.3419 | 69.3125 | 69.2565 | 69.1286 | 69.0047 | 68.8823 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
CHICKERELL GSP | CHICKERELL BSP | REDLANDS | MINIMUM HEADROOM | SY 67131 82321 | YES | 32.359 | 32.359 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 27.6691 | 27.6612 | 35.4723 | 35.4461 | 35.4102 | 35.3673 | 35.2851 | 35.1992 | 35.1181 | 35.0393 | 34.882 | 34.5029 | 34.0629 | 33.6208 | 14.2371 | 14.2311 | 22.0466 | 22.0265 | 21.9989 | 21.966 | 21.9029 | 21.837 | 21.7666 | 21.6956 | 21.5539 | 21.2125 | 20.8163 | 20.3693
|  | REDLANDS | CT |  |  | 32.359 | 32.359 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 27.6695 | 27.6621 | 35.4744 | 35.4502 | 35.4177 | 35.3792 | 35.3387 | 35.2931 | 35.2463 | 35.1977 | 35.1108 | 34.6573 | 34.211 | 33.784 | 14.2374 | 14.2318 | 22.0482 | 22.0296 | 22.0047 | 21.9751 | 21.944 | 21.909 | 21.8732 | 21.8358 | 21.76 | 21.3516 | 20.9496 | 20.5508
|  | REDLANDS | LW |  |  | 32.359 | 32.359 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 27.6691 | 27.6612 | 35.4723 | 35.4461 | 35.4102 | 35.3673 | 35.3221 | 35.271 | 35.2186 | 35.1664 | 35.0719 | 34.563 | 34.0629 | 33.6208 | 14.2371 | 14.2311 | 22.0466 | 22.0265 | 21.9989 | 21.966 | 21.9313 | 21.8921 | 21.8519 | 21.8101 | 21.7249 | 21.2667 | 20.8163 | 20.3693
|  | REDLANDS | ST |  |  | 32.359 | 32.359 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 27.7287 | 27.6678 | 35.4887 | 35.4737 | 35.4517 | 35.3686 | 35.2851 | 35.1992 | 35.1181 | 35.0393 | 34.882 | 34.5029 | 34.1444 | 33.8042 | 32.2747 | 14.2361 | 22.0591 | 22.0476 | 22.0308 | 21.967 | 21.9029 | 21.837 | 21.7666 | 21.6956 | 21.5539 | 21.2125 | 20.8897 | 20.5733
|  | REDLANDS | FS |  |  | 32.359 | 32.359 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 41.389 | 27.7304 | 27.6721 | 35.4992 | 35.4934 | 35.4852 | 35.4599 | 35.4347 | 35.4034 | 35.3723 | 35.3409 | 35.2783 | 35.1337 | 35.0088 | 34.8848 | 32.2753 | 14.2394 | 22.0672 | 22.0628 | 22.0565 | 22.037 | 22.0177 | 21.9937 | 21.9698 | 21.9457 | 21.8977 | 21.7806 | 21.6681 | 21.5564
MANNINGTON GSP | SALISBURY | REDLYNCH | MINIMUM HEADROOM | SU 19073 20576 | YES | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 24.518 | 24.4996 | 24.4557 | 24.4081 | 24.3593 | 24.3098 | 24.2595 | 24.209 | 24.154 | 24.0989 | 23.9861 | 23.4849 | 23.119 | 22.8591 | 24.5758 | 24.5718 | 24.5623 | 24.5519 | 24.5413 | 24.5305 | 24.5196 | 24.5086 | 24.4966 | 24.4846 | 24.4601 | 24.351 | 24.2377 | 24.1256
|  | REDLYNCH | CT |  |  | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 24.518 | 24.4996 | 24.4557 | 24.4081 | 24.3593 | 24.3098 | 24.2595 | 24.209 | 24.154 | 24.0989 | 23.9869 | 23.4849 | 23.119 | 22.8591 | 24.5758 | 24.5718 | 24.5623 | 24.5519 | 24.5413 | 24.5305 | 24.5196 | 24.5086 | 24.4966 | 24.4846 | 24.4602 | 24.351 | 24.2377 | 24.1256
|  | REDLYNCH | LW |  |  | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 24.5183 | 24.5005 | 24.4578 | 24.4116 | 24.3638 | 24.315 | 24.2652 | 24.2145 | 24.1584 | 24.1016 | 23.9861 | 23.5188 | 23.1543 | 22.9012 | 24.5759 | 24.572 | 24.5627 | 24.5527 | 24.5423 | 24.5316 | 24.5208 | 24.5098 | 24.4976 | 24.4852 | 24.4601 | 24.3584 | 24.2524 | 24.147
|  | REDLYNCH | ST |  |  | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 24.5268 | 24.5212 | 24.5089 | 24.4903 | 24.4667 | 24.4132 | 24.3597 | 24.3064 | 24.2485 | 24.1912 | 24.0764 | 23.7812 | 23.4862 | 23.2391 | 24.5777 | 24.5765 | 24.5738 | 24.5698 | 24.5647 | 24.553 | 24.5414 | 24.5298 | 24.5172 | 24.5047 | 24.4797 | 24.4155 | 24.3513 | 24.2878
|  | REDLYNCH | FS |  |  | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 25.8139 | 24.5295 | 24.5284 | 24.5271 | 24.5195 | 24.5101 | 24.4922 | 24.4743 | 24.4513 | 24.4283 | 24.4054 | 24.36 | 24.2467 | 24.1342 | 24.0236 | 24.5783 | 24.5781 | 24.5778 | 24.5761 | 24.5741 | 24.5702 | 24.5663 | 24.5613 | 24.5563 | 24.5513 | 24.5414 | 24.5168 | 24.4923 | 24.4682
NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK | MINIMUM HEADROOM | SU 39267 13050 | NO | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278
|  | REGENTS PARK | CT |  |  | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278
|  | REGENTS PARK | LW |  |  | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278
|  | REGENTS PARK | ST |  |  | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278
|  | REGENTS PARK | FS |  |  | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 38.2073 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.6075 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278 | 35.4278
COWLEY GSP | WITNEY BSP | RISSINGTON | MINIMUM HEADROOM | SP 19225 19563 | YES | 22.94 | 22.9373 | 22.931 | 22.9242 | 22.9166 | 22.9087 | 22.9006 | 22.8926 | 22.8844 | 22.8757 | 22.8588 | 22.8015 | 22.8015 | 22.8015 | 18.0552 | 18.0481 | 18.0316 | 18.0137 | 17.9938 | 17.9732 | 17.9553 | 17.9464 | 17.9371 | 17.9273 | 17.9083 | 17.8415 | 17.7704 | 17.6994 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983
|  | RISSINGTON | CT |  |  | 22.94 | 22.9373 | 22.931 | 22.9242 | 22.9166 | 22.9087 | 22.9006 | 22.8926 | 22.8844 | 22.8757 | 22.8588 | 22.8015 | 22.8015 | 22.8015 | 18.0558 | 18.0495 | 18.0349 | 18.0189 | 18.0012 | 17.9829 | 17.964 | 17.9528 | 17.9448 | 17.9367 | 17.921 | 17.8575 | 17.789 | 17.7204 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983
|  | RISSINGTON | LW |  |  | 22.94 | 22.9373 | 22.931 | 22.9242 | 22.9166 | 22.9087 | 22.9006 | 22.8926 | 22.8844 | 22.8757 | 22.8588 | 22.8015 | 22.8015 | 22.8015 | 18.0552 | 18.0481 | 18.0316 | 18.0137 | 17.9938 | 17.9732 | 17.9553 | 17.9464 | 17.9371 | 17.9273 | 17.9083 | 17.8415 | 17.7704 | 17.6994 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983
|  | RISSINGTON | ST |  |  | 22.9416 | 22.941 | 22.9399 | 22.9382 | 22.9358 | 22.9296 | 22.9233 | 22.9173 | 22.911 | 22.9047 | 22.8926 | 22.8556 | 22.8172 | 22.8015 | 18.0592 | 18.0577 | 18.0549 | 18.0505 | 18.044 | 18.0279 | 18.0114 | 17.9957 | 17.9793 | 17.9628 | 17.9464 | 17.9047 | 17.8615 | 17.8189 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983
|  | RISSINGTON | FS |  |  | 22.962 | 22.9418 | 22.9417 | 22.9412 | 22.9405 | 22.9385 | 22.9365 | 22.9341 | 22.9317 | 22.9293 | 22.9246 | 22.911 | 22.8961 | 22.8808 | 18.1126 | 18.0597 | 18.0595 | 18.0583 | 18.0564 | 18.0512 | 18.0459 | 18.0395 | 18.0333 | 18.027 | 18.0149 | 17.9791 | 17.9503 | 17.9331 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983 | 18.4983
BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE | MINIMUM HEADROOM | SU 47846 67187 | NO | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 18.1505 | 17.469 | 23.5794 | 23.492 | 23.3407 | 23.1914 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 17.7898 | 16.6499 | 15.8448 | 15.0446 | 25.9551 | 25.8686 | 25.7186 | 25.5707 | 25.4251 | 25.2812 | 25.141 | 25.0754 | 25.0046 | 24.9353 | 24.7462 | 24.4822 | 24.3004 | 24.2751
|  | RIVERSIDE | CT |  |  | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 18.1505 | 17.469 | 23.5817 | 23.4994 | 23.3513 | 23.2047 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 17.8291 | 16.8447 | 16.0143 | 15.1961 | 25.9575 | 25.8759 | 25.7292 | 25.5839 | 25.4377 | 25.2898 | 25.142 | 25.0754 | 25.0046 | 24.9353 | 24.7554 | 24.5262 | 24.3386 | 24.2751
|  | RIVERSIDE | LW |  |  | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 18.1505 | 17.469 | 23.5794 | 23.492 | 23.3407 | 23.1914 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 17.7898 | 16.6499 | 15.8448 | 15.0446 | 25.9551 | 25.8686 | 25.7186 | 25.5707 | 25.4251 | 25.2812 | 25.141 | 25.0759 | 25.0055 | 24.9358 | 24.7462 | 24.4822 | 24.3004 | 24.2751
|  | RIVERSIDE | ST |  |  | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.6186 | 23.5665 | 23.483 | 23.3698 | 23.232 | 23.1847 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 23.1713 | 18.111 | 25.9941 | 25.9424 | 25.8597 | 25.7475 | 25.6109 | 25.564 | 25.5161 | 25.471 | 25.4236 | 25.3782 | 25.221 | 25.0356 | 24.9278 | 24.821
|  | RIVERSIDE | FS |  |  | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.5178 | 23.6569 | 23.6408 | 23.631 | 23.6046 | 23.574 | 23.5573 | 23.5411 | 23.5207 | 23.5005 | 23.4809 | 23.418 | 23.2687 | 23.1713 | 23.1713 | 26.032 | 26.016 | 26.0063 | 25.9802 | 25.9499 | 25.9333 | 25.9172 | 25.897 | 25.877 | 25.8576 | 25.7952 | 25.6473 | 25.5436 | 25.4556
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE | MINIMUM HEADROOM | SU 11617 17810 | YES | -1.1143 | -1.1161 | -1.1202 | -1.1248 | -1.1293 | -1.1338 | -1.1383 | -1.1455 | -1.1539 | -1.1621 | -1.1783 | -1.2252 | -1.2918 | -1.358 | -18.7034 | -18.7055 | -18.7106 | -18.7162 | -18.7217 | -18.7272 | -18.7326 | -18.7408 | -18.7509 | -18.7608 | -18.7802 | -18.8416 | -18.9257 | -19.0088 | -26.3317 | -26.3339 | -26.3391 | -26.3448 | -26.3505 | -26.3561 | -26.3617 | -26.37 | -26.3803 | -26.3905 | -26.4103 | -26.4731 | -26.5591 | -26.6442
|  | ROCKBOURNE | CT |  |  | -1.1143 | -1.1161 | -1.1202 | -1.1248 | -1.1293 | -1.1338 | -1.1383 | -1.1427 | -1.1475 | -1.1523 | -1.1618 | -1.2252 | -1.2918 | -1.358 | -18.7034 | -18.7055 | -18.7106 | -18.7162 | -18.7217 | -18.7272 | -18.7326 | -18.7381 | -18.744 | -18.7498 | -18.7614 | -18.8416 | -18.9257 | -19.0088 | -26.3317 | -26.3339 | -26.3391 | -26.3448 | -26.3505 | -26.3561 | -26.3617 | -26.3672 | -26.3733 | -26.3792 | -26.3911 | -26.4731 | -26.5591 | -26.6442
|  | ROCKBOURNE | LW |  |  | -1.1143 | -1.1161 | -1.1202 | -1.1248 | -1.1293 | -1.1338 | -1.1383 | -1.1427 | -1.1475 | -1.1523 | -1.1618 | -1.2252 | -1.2918 | -1.358 | -18.7034 | -18.7055 | -18.7105 | -18.7159 | -18.7213 | -18.7268 | -18.7321 | -18.7375 | -18.7433 | -18.749 | -18.7604 | -18.8365 | -18.9166 | -18.9962 | -26.3317 | -26.3339 | -26.339 | -26.3446 | -26.3501 | -26.3557 | -26.3612 | -26.3666 | -26.3726 | -26.3784 | -26.3901 | -26.468 | -26.5499 | -26.6313
|  | ROCKBOURNE | ST |  |  | -1.1136 | -1.1144 | -1.1161 | -1.1187 | -1.1218 | -1.1298 | -1.1377 | -1.1455 | -1.1539 | -1.1621 | -1.1783 | -1.2182 | -1.2589 | -1.2995 | -18.7025 | -18.7035 | -18.7055 | -18.7086 | -18.7123 | -18.722 | -18.7314 | -18.7408 | -18.7509 | -18.7608 | -18.7802 | -18.8282 | -18.8771 | -18.9259 | -26.3309 | -26.3318 | -26.3339 | -26.3371 | -26.3409 | -26.3507 | -26.3604 | -26.37 | -26.3803 | -26.3905 | -26.4103 | -26.4594 | -26.5095 | -26.5594
|  | ROCKBOURNE | FS |  |  | -1.1132 | -1.1133 | -1.1134 | -1.1141 | -1.115 | -1.1177 | -1.1203 | -1.1237 | -1.1271 | -1.1304 | -1.1368 | -1.1522 | -1.1673 | -1.1818 | -18.702 | -18.7022 | -18.7023 | -18.7032 | -18.7042 | -18.7074 | -18.7106 | -18.7147 | -18.7187 | -18.7227 | -18.7304 | -18.7489 | -18.767 | -18.7844 | -26.3304 | -26.3305 | -26.3306 | -26.3315 | -26.3325 | -26.3358 | -26.3391 | -26.3433 | -26.3474 | -26.3515 | -26.3594 | -26.3783 | -26.3968 | -26.4146
NURSLING GSP | ROWNHAMS | ROMSEY | MINIMUM HEADROOM | SU 36092 21110 | NO | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 19.7899 | 18.448 | 17.1328 | 15.8191 | 24.7813 | 24.7535 | 24.6991 | 24.6386 | 24.5689 | 24.4938 | 24.4109 | 24.3425 | 24.2846 | 24.2489 | 18.5537 | 16.9329 | 15.3445 | 13.7577 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 18.5416 | 18.1699 | 17.4752 | 15.8575 | 14.272 | 12.6883
|  | ROMSEY | CT |  |  | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 19.7899 | 18.448 | 17.1328 | 15.8191 | 24.7813 | 24.7535 | 24.6991 | 24.6386 | 24.5716 | 24.5012 | 24.426 | 24.3554 | 24.2993 | 24.2574 | 18.6383 | 16.9637 | 15.3703 | 13.7895 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 18.6333 | 18.2648 | 17.5596 | 15.8882 | 14.2978 | 12.72
|  | ROMSEY | LW |  |  | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 19.7899 | 18.448 | 17.1328 | 15.8191 | 24.7822 | 24.7557 | 24.7008 | 24.639 | 24.5689 | 24.4938 | 24.4109 | 24.3425 | 24.2846 | 24.2489 | 18.5537 | 16.9329 | 15.3445 | 13.7577 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 18.5416 | 18.1699 | 17.4752 | 15.8575 | 14.272 | 12.6883
|  | ROMSEY | ST |  |  | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 19.5948 | 18.777 | 17.9744 | 24.8159 | 24.7832 | 24.7501 | 24.7078 | 24.6664 | 24.6073 | 24.5453 | 24.479 | 24.405 | 24.3449 | 24.2637 | 18.3181 | 17.3303 | 16.361 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 18.3345 | 17.2401 | 16.2541 | 15.2866
|  | ROMSEY | FS |  |  | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 25.2541 | 24.8212 | 24.8199 | 24.7906 | 24.7665 | 24.7372 | 24.7131 | 24.6906 | 24.6638 | 24.636 | 24.6072 | 24.5516 | 24.44 | 24.3526 | 24.2924 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 23.4046 | 18.5904
LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN | MINIMUM HEADROOM | SZ 89974 99335 | YES | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 28.664 | 28.6145 | 28.5521 | 28.4884 | 28.4159 | 28.3554 | 28.3357 | 28.3158 | 28.2944 | 28.2343 | 28.1303 | 27.9431 | 27.6985 | 27.3998 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867
|  | ROSE GREEN | CT |  |  | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 28.666 | 28.6236 | 28.5685 | 28.5141 | 28.4502 | 28.3929 | 28.3646 | 28.3316 | 28.2951 | 28.2587 | 28.2068 | 28.0014 | 27.7599 | 27.5 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867
|  | ROSE GREEN | LW |  |  | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 28.664 | 28.6145 | 28.5521 | 28.4884 | 28.4159 | 28.3554 | 28.3357 | 28.3158 | 28.2956 | 28.2746 | 28.2361 | 27.9867 | 27.6985 | 27.3998 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867
|  | ROSE GREEN | ST |  |  | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 28.6761 | 28.6472 | 28.6121 | 28.5765 | 28.5337 | 28.4616 | 28.4094 | 28.3546 | 28.2944 | 28.2343 | 28.1303 | 27.9431 | 27.7258 | 27.5052 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867
|  | ROSE GREEN | FS |  |  | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 29.6149 | 28.6862 | 28.6688 | 28.6497 | 28.6307 | 28.6103 | 28.5882 | 28.5757 | 28.5613 | 28.5465 | 28.5323 | 28.5056 | 28.4567 | 28.3734 | 28.2241 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867 | 28.5867
COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL | MINIMUM HEADROOM | SP 53637 03027 | NO | 30.8528 | 30.8289 | 30.7819 | 30.7195 | 30.6419 | 30.581 | 30.5271 | 30.4538 | 30.3748 | 30.2928 | 30.1136 | 29.8922 | 29.7761 | 29.661 | 30.2222 | 30.1189 | 29.9157 | 29.6468 | 29.3098 | 28.8845 | 28.529 | 28.3366 | 28.2168 | 28.1245 | 27.9229 | 27.6738 | 27.5987 | 27.5264 | 30.37 | 30.2677 | 30.0665 | 29.8129 | 29.7318 | 29.6295 | 29.539 | 29.4184 | 29.3684 | 29.3164 | 29.3162 | 29.3162 | 29.3162 | 29.3162
|  | ROSE HILL | CT |  |  | 30.8528 | 30.8289 | 30.7819 | 30.7195 | 30.6419 | 30.581 | 30.5271 | 30.4538 | 30.3748 | 30.2928 | 30.1136 | 29.8922 | 29.7761 | 29.661 | 30.2239 | 30.1219 | 29.9157 | 29.6492 | 29.3205 | 28.9151 | 28.5713 | 28.3672 | 28.2418 | 28.1515 | 27.9485 | 27.6922 | 27.6025 | 27.5286 | 30.3717 | 30.2707 | 30.0665 | 29.8134 | 29.7344 | 29.6369 | 29.5542 | 29.4441 | 29.3824 | 29.3316 | 29.3162 | 29.3162 | 29.3162 | 29.3162
|  | ROSE HILL | LW |  |  | 30.8528 | 30.8289 | 30.7819 | 30.7195 | 30.6419 | 30.581 | 30.5271 | 30.4538 | 30.3748 | 30.2928 | 30.1136 | 29.8922 | 29.7761 | 29.661 | 30.2222 | 30.1189 | 29.9159 | 29.6468 | 29.3098 | 28.8845 | 28.529 | 28.3366 | 28.2168 | 28.1245 | 27.9229 | 27.6738 | 27.5987 | 27.5264 | 30.37 | 30.2677 | 30.0666 | 29.8129 | 29.7318 | 29.6295 | 29.539 | 29.4184 | 29.3684 | 29.3164 | 29.3162 | 29.3162 | 29.3162 | 29.3162
|  | ROSE HILL | ST |  |  | 30.9198 | 30.8582 | 30.8438 | 30.8157 | 30.7736 | 30.7202 | 30.6764 | 30.6255 | 30.5818 | 30.5326 | 30.4175 | 30.2628 | 30.1861 | 30.1147 | 30.4884 | 30.2451 | 30.183 | 30.062 | 29.8801 | 29.6498 | 29.4607 | 29.1954 | 28.8899 | 28.5527 | 28.2705 | 28.0907 | 28.0045 | 27.9241 | 30.6337 | 30.3927 | 30.3312 | 30.2113 | 30.0312 | 29.8136 | 29.7681 | 29.7043 | 29.6308 | 29.5483 | 29.3954 | 29.3162 | 29.3162 | 29.3162
|  | ROSE HILL | FS |  |  | 30.9313 | 30.9263 | 30.8695 | 30.8571 | 30.8395 | 30.8188 | 30.8012 | 30.7743 | 30.7451 | 30.714 | 30.6449 | 30.5714 | 30.5345 | 30.5085 | 30.5217 | 30.5073 | 30.294 | 30.2407 | 30.1645 | 30.0753 | 29.9991 | 29.8831 | 29.7571 | 29.623 | 29.3245 | 28.8178 | 28.5607 | 28.4498 | 30.6667 | 30.6525 | 30.4412 | 30.3884 | 30.3129 | 30.2245 | 30.1491 | 30.0341 | 29.9122 | 29.8071 | 29.7353 | 29.6135 | 29.5515 | 29.5078
MELKSHAM GSP | CHIPPENHAM | ROWDEN | MINIMUM HEADROOM | ST 90805 72608 | YES | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 21.6327 | 21.0006 | 19.7398 | 18.4291 | 17.1061 | 25.6603 | 25.6603 | 25.6603 | 20.204 | 19.9037 | 19.5826 | 19.2411 | 18.8799 | 18.509 | 18.134 | 17.3808 | 15.8787 | 14.3171 | 12.7409 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 20.2849 | 19.9685 | 19.632 | 19.2762 | 18.9107 | 18.5412 | 17.7992 | 16.3192 | 14.7805 | 13.2275
|  | ROWDEN | CT |  |  | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 21.6327 | 21.0006 | 19.7398 | 18.4291 | 17.1061 | 25.6603 | 25.6603 | 25.6603 | 20.3048 | 20.0447 | 19.7638 | 19.4632 | 19.1442 | 18.8142 | 18.479 | 17.8035 | 16.2944 | 14.7994 | 13.3149 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 20.4238 | 20.1471 | 19.8508 | 19.5366 | 19.2114 | 18.8812 | 18.2156 | 16.7287 | 15.2558 | 13.7931
|  | ROWDEN | LW |  |  | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 21.6327 | 21.0006 | 19.7398 | 18.4291 | 17.1061 | 25.6603 | 25.6603 | 25.6603 | 20.204 | 19.9037 | 19.5826 | 19.2411 | 18.8799 | 18.509 | 18.134 | 17.3808 | 15.8787 | 14.3171 | 12.7409 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 20.2849 | 19.9685 | 19.632 | 19.2762 | 18.9107 | 18.5412 | 17.7992 | 16.3192 | 14.7805 | 13.2275
|  | ROWDEN | ST |  |  | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 21.2771 | 20.4728 | 19.6882 | 25.6603 | 25.6603 | 25.6603 | 25.6603 | 20.2941 | 20.0992 | 19.8918 | 19.6727 | 19.4427 | 19.2076 | 18.7293 | 17.7103 | 16.752 | 15.8173 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 20.2731 | 20.0573 | 19.8307 | 19.599 | 19.1278 | 18.1237 | 17.1796 | 16.2586
|  | ROWDEN | FS |  |  | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 29.1301 | 25.6603 | 25.6603 | 25.6603 | 25.6603 | 25.6603 | 25.6603 | 25.6603 | 25.6603 | 25.6603 | 25.6603 | 20.3607 | 19.9773 | 19.603 | 19.2217 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 26.0048 | 20.3574 | 19.9887 | 19.613
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK | MINIMUM HEADROOM | SU 58018 00782 | NO | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 30.7385 | 30.7337 | 30.7223 | 30.7097 | 30.6972 | 30.6848 | 30.6727 | 30.6606 | 30.6475 | 30.6345 | 30.5977 | 30.4929 | 30.42 | 30.3706 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684
|  | ROWNER PARK | CT |  |  | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 30.7385 | 30.7337 | 30.7223 | 30.7097 | 30.6972 | 30.6848 | 30.6727 | 30.6606 | 30.6475 | 30.6345 | 30.6089 | 30.4929 | 30.42 | 30.3706 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684
|  | ROWNER PARK | LW |  |  | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 30.7405 | 30.7386 | 30.7342 | 30.7291 | 30.7239 | 30.7188 | 30.714 | 30.7091 | 30.7038 | 30.6986 | 30.6868 | 30.5517 | 30.44 | 30.3746 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684
|  | ROWNER PARK | ST |  |  | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 30.7412 | 30.7403 | 30.7385 | 30.7356 | 30.7321 | 30.713 | 30.6942 | 30.6757 | 30.6556 | 30.6359 | 30.5977 | 30.4962 | 30.4371 | 30.3904 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684
|  | ROWNER PARK | FS |  |  | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 34.5572 | 30.7416 | 30.7415 | 30.7413 | 30.7404 | 30.7394 | 30.7335 | 30.7277 | 30.7203 | 30.7129 | 30.7057 | 30.6917 | 30.6578 | 30.6192 | 30.5785 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684 | 31.1684
FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE | MINIMUM HEADROOM | SZ 59554 91973 | YES | 38.1849 | 38.1522 | 38.1398 | 38.1251 | 38.1075 | 38.0894 | 38.0707 | 38.0532 | 38.0446 | 38.0393 | 38.0266 | 37.9812 | 37.9415 | 37.8933 | 33.815 | 33.5505 | 33.5467 | 33.5424 | 33.5377 | 33.5326 | 33.5272 | 33.5214 | 33.5167 | 33.5116 | 33.4995 | 25.8898 | 24.519 | 23.1982 | 33.5441 | 33.539 | 33.5314 | 33.5229 | 33.5138 | 33.5038 | 33.4932 | 33.4818 | 33.4727 | 33.4625 | 33.4389 | 26.0444 | 24.6876 | 23.3845
|  | RYDE | CT |  |  | 38.1849 | 38.1522 | 38.1398 | 38.1251 | 38.1075 | 38.0894 | 38.0707 | 38.0532 | 38.0446 | 38.0393 | 38.0266 | 37.9812 | 37.9415 | 37.8933 | 33.815 | 33.5505 | 33.5467 | 33.5424 | 33.5377 | 33.5326 | 33.5272 | 33.5214 | 33.5167 | 33.5116 | 33.4995 | 26.2035 | 25.03 | 23.8538 | 33.5441 | 33.539 | 33.5314 | 33.5229 | 33.5138 | 33.5038 | 33.4932 | 33.4818 | 33.4727 | 33.4625 | 33.4389 | 26.3283 | 25.1549 | 23.9852
|  | RYDE | LW |  |  | 38.1849 | 38.1522 | 38.1398 | 38.1251 | 38.1075 | 38.0894 | 38.0707 | 38.0532 | 38.0446 | 38.0393 | 38.0266 | 37.9812 | 37.9415 | 37.8933 | 33.8177 | 33.5547 | 33.5536 | 33.5523 | 33.5505 | 33.5484 | 33.5459 | 33.5429 | 33.5406 | 33.5379 | 33.5314 | 25.8898 | 24.519 | 23.1982 | 33.5488 | 33.5472 | 33.5451 | 33.5423 | 33.539 | 33.5348 | 33.5299 | 33.524 | 33.5194 | 33.5142 | 33.5015 | 26.0444 | 24.6876 | 23.3845
|  | RYDE | ST |  |  | 38.188 | 38.1839 | 38.1781 | 38.1707 | 38.161 | 38.1441 | 38.1272 | 38.111 | 38.0926 | 38.0734 | 38.0593 | 38.0476 | 38.0302 | 38.0168 | 33.8323 | 33.8009 | 33.7561 | 33.6976 | 33.6209 | 33.554 | 33.5532 | 33.5523 | 33.5513 | 33.5503 | 33.5481 | 33.5421 | 25.788 | 24.8435 | 33.5503 | 33.5497 | 33.549 | 33.5481 | 33.5471 | 33.5457 | 33.5441 | 33.5424 | 33.5405 | 33.5385 | 33.5342 | 33.5224 | 25.9568 | 25.0251
|  | RYDE | FS |  |  | 38.1892 | 38.1871 | 38.1848 | 38.1815 | 38.1774 | 38.1719 | 38.1665 | 38.1608 | 38.1547 | 38.1485 | 38.1359 | 38.1003 | 38.0653 | 38.0489 | 33.8418 | 33.8262 | 33.8091 | 33.7843 | 33.7536 | 33.7108 | 33.6691 | 33.6251 | 33.5783 | 33.5535 | 33.5526 | 33.5491 | 33.5459 | 33.5428 | 33.5504 | 33.5501 | 33.5497 | 33.5491 | 33.5485 | 33.5478 | 33.5471 | 33.5463 | 33.5455 | 33.5447 | 33.5429 | 33.5362 | 33.53 | 33.5238
MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL | MINIMUM HEADROOM | SU 14215 30481 | YES | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 37.561 | 35.7877 | 34.0074 | 45.1126 | 45.0875 | 45.0278 | 45.0001 | 45.0001 | 45.0001 | 37.6766 | 37.3304 | 37.0292 | 36.7251 | 36.1015 | 34.2931 | 32.4033 | 30.5062 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 37.9476 | 37.6046 | 37.164 | 36.7798 | 36.4462 | 36.1095 | 35.4189 | 33.4162 | 31.3234 | 29.2225
|  | SALISBURY CENTRAL | CT |  |  | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 37.561 | 35.7877 | 34.0074 | 45.1134 | 45.0895 | 45.0324 | 45.0001 | 45.0001 | 45.0001 | 37.7732 | 37.4727 | 37.2004 | 36.9167 | 36.3262 | 34.539 | 32.7131 | 30.8928 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 37.9905 | 37.672 | 37.2804 | 36.9373 | 36.6358 | 36.3216 | 35.6677 | 33.6885 | 31.6664 | 29.6506
|  | SALISBURY CENTRAL | LW |  |  | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 37.561 | 35.7877 | 34.0074 | 45.1126 | 45.0875 | 45.0278 | 45.0001 | 45.0001 | 45.0001 | 37.6766 | 37.3304 | 37.0292 | 36.7251 | 36.1015 | 34.2931 | 32.4033 | 30.5062 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 37.9476 | 37.6046 | 37.164 | 36.7798 | 36.4462 | 36.1095 | 35.4189 | 33.4162 | 31.3234 | 29.2225
|  | SALISBURY CENTRAL | ST |  |  | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 37.0946 | 45.1444 | 45.1161 | 45.0983 | 45.0712 | 45.0362 | 45.0001 | 45.0001 | 45.0001 | 37.9215 | 37.719 | 37.2674 | 36.086 | 34.9329 | 33.7961 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 37.9552 | 37.695 | 37.4591 | 37.215 | 36.7099 | 35.4017 | 34.1247 | 32.8658
|  | SALISBURY CENTRAL | FS |  |  | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 48.2279 | 45.1483 | 45.1468 | 45.145 | 45.1344 | 45.1213 | 45.0994 | 45.0723 | 45.0443 | 45.0203 | 45.0001 | 45.0001 | 45.0001 | 37.6777 | 37.2271 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 44.9309 | 37.6563 | 37.1653 | 36.6654
BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST | MINIMUM HEADROOM | SU 83597 60930 | NO | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 34.471 | 34.4665 | 34.4557 | 34.444 | 34.4321 | 34.4197 | 34.4072 | 34.395 | 34.3819 | 34.3691 | 34.3418 | 34.2406 | 26.66 | 24.5416 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 25.1698
|  | SANDHURST | CT |  |  | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 34.4718 | 34.4684 | 34.4604 | 34.4517 | 34.4427 | 34.4334 | 34.4243 | 34.4154 | 34.406 | 34.3967 | 34.3766 | 34.2791 | 34.2406 | 25.423 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 26.0494
|  | SANDHURST | LW |  |  | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 34.471 | 34.4665 | 34.4557 | 34.444 | 34.4321 | 34.4197 | 34.4072 | 34.395 | 34.3819 | 34.3691 | 34.3418 | 34.2406 | 26.66 | 24.5416 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 25.1698
|  | SANDHURST | ST |  |  | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 34.4959 | 34.4708 | 34.4664 | 34.4597 | 34.4515 | 34.4397 | 34.428 | 34.4167 | 34.4045 | 34.3926 | 34.368 | 34.3027 | 34.2406 | 34.2406 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749
|  | SANDHURST | FS |  |  | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 37.8239 | 34.497 | 34.4736 | 34.4733 | 34.4716 | 34.4695 | 34.4657 | 34.462 | 34.4573 | 34.4526 | 34.4481 | 34.4388 | 34.4146 | 34.3893 | 34.3638 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749 | 35.0749
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN | MINIMUM HEADROOM | SZ 59877 85052 | YES | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 18.6785 | 18.6718 | 18.6554 | 18.6373 | 18.6188 | 18.6001 | 18.5815 | 18.5576 | 18.5251 | 18.4929 | 18.4301 | 18.323 | 18.3 | 18.3 | 19.5452 | 19.5278 | 19.4855 | 19.4387 | 19.3908 | 19.3426 | 19.2944 | 19.2328 | 19.1487 | 19.0927 | 19.0927 | 19.0927 | 19.0927 | 19.0927
|  | SANDOWN | CT |  |  | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 18.6785 | 18.6718 | 18.6556 | 18.6376 | 18.6192 | 18.6007 | 18.5822 | 18.5637 | 18.5437 | 18.5237 | 18.4841 | 18.343 | 18.3 | 18.3 | 19.5452 | 19.5279 | 19.4859 | 19.4394 | 19.3919 | 19.3441 | 19.2963 | 19.2484 | 19.1968 | 19.1451 | 19.0927 | 19.0927 | 19.0927 | 19.0927
|  | SANDOWN | LW |  |  | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 18.6785 | 18.6718 | 18.6554 | 18.6373 | 18.6188 | 18.6001 | 18.5815 | 18.5629 | 18.5417 | 18.52 | 18.4732 | 18.3301 | 18.3 | 18.3 | 19.5452 | 19.5278 | 19.4855 | 19.4387 | 19.3908 | 19.3426 | 19.2944 | 19.2464 | 19.1917 | 19.1355 | 19.0927 | 19.0927 | 19.0927 | 19.0927
|  | SANDOWN | ST |  |  | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 18.681 | 18.678 | 18.6714 | 18.6614 | 18.649 | 18.6182 | 18.5877 | 18.5576 | 18.5251 | 18.4929 | 18.4301 | 18.323 | 18.3 | 18.3 | 19.5517 | 19.544 | 19.5268 | 19.5009 | 19.4688 | 19.3893 | 19.3106 | 19.2328 | 19.1487 | 19.0927 | 19.0927 | 19.0927 | 19.0927 | 19.0927
|  | SANDOWN | FS |  |  | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 21.72 | 18.6825 | 18.6821 | 18.6815 | 18.6788 | 18.6755 | 18.6683 | 18.6612 | 18.652 | 18.643 | 18.6341 | 18.6166 | 18.5649 | 18.4997 | 18.427 | 19.5554 | 19.5543 | 19.5529 | 19.5458 | 19.5373 | 19.5188 | 19.5004 | 19.4768 | 19.4535 | 19.4305 | 19.3853 | 19.2516 | 19.093 | 19.0927
LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY | MINIMUM HEADROOM | SZ 85667 94289 | YES | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 23.2935 | 23.2546 | 23.1819 | 23.0926 | 22.9981 | 22.901 | 22.8016 | 22.6995 | 22.5889 | 22.4886 | 22.3141 | 21.6702 | 21.258 | 21.258 | 25.6687 | 25.6588 | 25.6402 | 25.6174 | 25.5933 | 25.5685 | 25.5431 | 25.517 | 25.4888 | 25.4632 | 25.4186 | 25.239 | 25.0352 | 25.0059
|  | SELSEY | CT |  |  | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 23.2942 | 23.2567 | 23.1844 | 23.0968 | 23.0039 | 22.9082 | 22.8118 | 22.7134 | 22.6042 | 22.5013 | 22.3173 | 21.7338 | 21.258 | 21.258 | 25.6689 | 25.6593 | 25.6409 | 25.6185 | 25.5948 | 25.5703 | 25.5457 | 25.5206 | 25.4927 | 25.4664 | 25.4195 | 25.259 | 25.0758 | 25.0059
|  | SELSEY | LW |  |  | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 23.2935 | 23.2546 | 23.1819 | 23.0926 | 22.9981 | 22.901 | 22.8016 | 22.6995 | 22.5889 | 22.4886 | 22.3141 | 21.6702 | 21.258 | 21.258 | 25.6687 | 25.6588 | 25.6402 | 25.6174 | 25.5933 | 25.5685 | 25.5431 | 25.517 | 25.4888 | 25.4632 | 25.4186 | 25.239 | 25.0352 | 25.0059
|  | SELSEY | ST |  |  | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 23.3097 | 23.2911 | 23.2617 | 23.2115 | 23.1483 | 23.0584 | 22.9688 | 22.8785 | 22.7784 | 22.6832 | 22.5101 | 22.0068 | 21.5496 | 21.258 | 25.6729 | 25.6681 | 25.6606 | 25.6478 | 25.6316 | 25.6087 | 25.5858 | 25.5627 | 25.5372 | 25.5129 | 25.4687 | 25.3402 | 25.2009 | 25.0625
|  | SELSEY | FS |  |  | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 28.515 | 23.3206 | 23.3152 | 23.3127 | 23.2974 | 23.2787 | 23.253 | 23.2271 | 23.1944 | 23.1612 | 23.1303 | 23.0745 | 22.9188 | 22.7374 | 22.5439 | 25.6756 | 25.6743 | 25.6736 | 25.6697 | 25.6649 | 25.6584 | 25.6518 | 25.6434 | 25.6349 | 25.627 | 25.6128 | 25.573 | 25.5267 | 25.4773
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY | MINIMUM HEADROOM | ST 85605 23325 | YES | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.8929 | 31.8929 | 31.8929 | 28.0261 | 28.0153 | 28.0009 | 27.9838 | 27.9548 | 27.9221 | 27.8866 | 27.8368 | 27.7954 | 27.7465 | 27.6592 | 27.5397 | 27.5272 | 27.5272 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1505 | 28.1505 | 28.1505
|  | SHAFTESBURY | CT |  |  | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.8929 | 31.8929 | 31.8929 | 28.0265 | 28.0166 | 28.0027 | 27.9863 | 27.9591 | 27.9284 | 27.8962 | 27.853 | 27.8154 | 27.7731 | 27.715 | 27.5417 | 27.5272 | 27.5272 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1505 | 28.1505 | 28.1505
|  | SHAFTESBURY | LW |  |  | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.8929 | 31.8929 | 31.8929 | 28.0261 | 28.0153 | 28.0009 | 27.9838 | 27.9548 | 27.9221 | 27.8866 | 27.8368 | 27.7954 | 27.7508 | 27.6959 | 27.5397 | 27.5272 | 27.5272 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1505 | 28.1505 | 28.1505
|  | SHAFTESBURY | ST |  |  | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9151 | 31.9151 | 31.9151 | 28.1375 | 28.0248 | 28.0186 | 28.0089 | 27.9905 | 27.9463 | 27.9017 | 27.85 | 27.7999 | 27.7465 | 27.6592 | 27.5576 | 27.5401 | 27.5401 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1726 | 28.1726 | 28.1726
|  | SHAFTESBURY | FS |  |  | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 31.9373 | 28.1407 | 28.0923 | 28.091 | 28.0877 | 28.081 | 28.0669 | 28.0527 | 28.0328 | 28.0148 | 27.996 | 27.966 | 27.894 | 27.8272 | 27.7608 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947 | 28.1947
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET | MINIMUM HEADROOM | SZ 40828 88643 | YES | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.1152 | 22.1018 | 22.0696 | 22.0344 | 21.9932 | 21.9476 | 21.8928 | 21.8355 | 21.7732 | 21.709 | 21.6236 | 21.4729 | 21.4729 | 21.4729 | 21.834 | 21.821 | 21.7897 | 21.7555 | 21.7155 | 21.6713 | 21.6181 | 21.5625 | 21.5019 | 21.4397 | 21.3347 | 21.1154 | 21.1079 | 21.1079
|  | SHALFLEET | CT |  |  | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.329 | 22.316 | 22.2846 | 22.2504 | 22.2108 | 22.1675 | 22.1178 | 22.0659 | 22.009 | 21.9483 | 21.8404 | 21.6215 | 21.6215 | 21.6215 | 22.1232 | 22.1105 | 22.0801 | 22.0468 | 22.0084 | 21.9663 | 21.9181 | 21.8678 | 21.8125 | 21.7535 | 21.6488 | 21.384 | 21.3828 | 21.3828
|  | SHALFLEET | LW |  |  | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.4833 | 22.1152 | 22.1018 | 22.0696 | 22.0344 | 21.9932 | 21.9476 | 21.8928 | 21.8355 | 21.7732 | 21.709 | 21.6236 | 21.4729 | 21.4729 | 21.4729 | 21.834 | 21.821 | 21.7897 | 21.7555 | 21.7155 | 21.6713 | 21.6181 | 21.5625 | 21.5019 | 21.4397 | 21.3347 | 21.1154 | 21.1079 | 21.1079
|  | SHALFLEET | ST |  |  | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.3337 | 22.3274 | 22.3134 | 22.2923 | 22.263 | 22.1993 | 22.1321 | 22.0641 | 21.9897 | 21.9131 | 21.771 | 21.6215 | 21.6215 | 21.6215 | 22.1277 | 22.1216 | 22.108 | 22.0875 | 22.0591 | 21.9973 | 21.932 | 21.866 | 21.7938 | 21.7194 | 21.5815 | 21.4081 | 21.3828 | 21.3828
|  | SHALFLEET | FS |  |  | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.7311 | 22.337 | 22.3363 | 22.3353 | 22.3299 | 22.3218 | 22.3017 | 22.2798 | 22.2524 | 22.2246 | 22.1964 | 22.145 | 22.0337 | 21.9294 | 21.8294 | 22.1309 | 22.1302 | 22.1293 | 22.124 | 22.1162 | 22.0967 | 22.0754 | 22.0488 | 22.0218 | 21.9944 | 21.9445 | 21.8365 | 21.7352 | 21.6382
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN | MINIMUM HEADROOM | SZ 57809 81912 | YES | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 28.2618 | 26.6777 | 26.6427 | 26.5786 | 26.5227 | 26.4664 | 26.4104 | 26.3178 | 26.2161 | 26.108 | 26.0019 | 25.7961 | 25.15 | 24.363 | 23.4534 | 26.6764 | 26.6427 | 26.5809 | 26.527 | 26.4727 | 26.4187 | 26.3295 | 26.2315 | 26.1273 | 26.0251 | 25.8267 | 25.204 | 24.4455 | 23.5689
|  | SHANKLIN | CT |  |  | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 28.2618 | 26.6783 | 26.6456 | 26.5836 | 26.529 | 26.4731 | 26.4157 | 26.3562 | 26.2974 | 26.2364 | 26.1764 | 26.0594 | 25.3476 | 24.5437 | 23.7394 | 26.677 | 26.6455 | 26.5857 | 26.5331 | 26.4792 | 26.4239 | 26.3666 | 26.3099 | 26.2511 | 26.1932 | 26.0805 | 25.3945 | 24.6197 | 23.8445
|  | SHANKLIN | LW |  |  | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 28.2618 | 26.6777 | 26.6427 | 26.5786 | 26.5227 | 26.4664 | 26.4104 | 26.3545 | 26.299 | 26.2363 | 26.1719 | 26.0352 | 25.2591 | 24.363 | 23.4534 | 26.6764 | 26.6427 | 26.5809 | 26.527 | 26.4727 | 26.4187 | 26.3649 | 26.3114 | 26.2509 | 26.1889 | 26.0572 | 25.3091 | 24.4455 | 23.5689
|  | SHANKLIN | ST |  |  | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 26.6861 | 26.664 | 26.6256 | 26.58 | 26.5243 | 26.4211 | 26.3178 | 26.2161 | 26.108 | 26.0019 | 25.7961 | 25.15 | 24.4651 | 23.7913 | 26.6844 | 26.6631 | 26.6261 | 26.5823 | 26.5286 | 26.4291 | 26.3295 | 26.2315 | 26.1273 | 26.0251 | 25.8267 | 25.204 | 24.5439 | 23.8945
|  | SHANKLIN | FS |  |  | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 32.122 | 26.6962 | 26.6896 | 26.6829 | 26.6735 | 26.6624 | 26.6369 | 26.6117 | 26.5798 | 26.5485 | 26.5176 | 26.4575 | 26.2893 | 26.0862 | 25.8643 | 26.6942 | 26.6879 | 26.6814 | 26.6723 | 26.6617 | 26.637 | 26.6127 | 26.5821 | 26.5518 | 26.5221 | 26.4642 | 26.302 | 26.1063 | 25.8924
AXMINSTER | YEOVIL BSP | SHERBORNE | MINIMUM HEADROOM | ST 63978 18163 | YES | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.1733 | 14.165 | 14.1444 | 14.1164 | 14.0776 | 14.0358 | 13.9879 | 13.9372 | 13.8596 | 13.7782 | 13.6033 | 13.411 | 13.2832 | 9.1699 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 9.4897
|  | SHERBORNE | CT |  |  | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.1737 | 14.1659 | 14.1465 | 14.1205 | 14.0861 | 14.0476 | 14.0042 | 13.9586 | 13.891 | 13.82 | 13.6275 | 13.4739 | 13.3498 | 13.256 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345
|  | SHERBORNE | LW |  |  | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.1733 | 14.165 | 14.1444 | 14.1164 | 14.0786 | 14.0361 | 13.9879 | 13.9372 | 13.8596 | 13.7782 | 13.6033 | 13.411 | 13.2832 | 9.1699 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 9.4897
|  | SHERBORNE | ST |  |  | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.1758 | 14.1673 | 14.148 | 14.1178 | 14.0776 | 14.0358 | 13.991 | 13.945 | 13.882 | 13.816 | 13.6373 | 13.5315 | 13.4521 | 13.3755 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345
|  | SHERBORNE | FS |  |  | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.964 | 14.1823 | 14.1806 | 14.1778 | 14.172 | 14.1638 | 14.1489 | 14.1332 | 14.1149 | 14.0908 | 14.0656 | 13.9905 | 13.8325 | 13.7141 | 13.6364 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345 | 14.2345
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE | MINIMUM HEADROOM | SP 03884 19102 | YES | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 9.1734 | 9.1698 | 9.1612 | 9.1519 | 9.1425 | 9.1333 | 9.124 | 9.115 | 9.1052 | 9.0956 | 9.0766 | 9.0486 | 9.0194 | 8.9906 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45
|  | SHIPTON OLIFFE | CT |  |  | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 9.1734 | 9.1698 | 9.1612 | 9.1519 | 9.1425 | 9.1333 | 9.124 | 9.115 | 9.1052 | 9.0956 | 9.0766 | 9.0486 | 9.0194 | 8.9906 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45
|  | SHIPTON OLIFFE | LW |  |  | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 9.1742 | 9.1717 | 9.1657 | 9.1593 | 9.1528 | 9.1463 | 9.1399 | 9.1335 | 9.1267 | 9.1199 | 9.1065 | 9.0798 | 9.052 | 9.0246 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45
|  | SHIPTON OLIFFE | ST |  |  | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 9.1749 | 9.1734 | 9.1702 | 9.1653 | 9.1593 | 9.1562 | 9.1531 | 9.1501 | 9.1468 | 9.1436 | 9.1374 | 9.1211 | 9.1047 | 9.0884 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45
|  | SHIPTON OLIFFE | FS |  |  | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 13.3572 | 9.1757 | 9.1756 | 9.1754 | 9.1743 | 9.173 | 9.172 | 9.1709 | 9.1695 | 9.1682 | 9.1669 | 9.1644 | 9.1579 | 9.1515 | 9.1454 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45
NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY | MINIMUM HEADROOM | SU 39988 13808 | NO | 70.296 | 70.2895 | 70.2744 | 70.2584 | 70.2424 | 70.2267 | 70.2112 | 70.1957 | 70.179 | 70.1625 | 70.1273 | 70.0227 | 69.9173 | 69.8134 | 52.6454 | 52.568 | 52.3889 | 52.198 | 52.0082 | 51.8213 | 51.6363 | 51.4589 | 51.2941 | 51.1304 | 50.7838 | 50.2854 | 49.9493 | 49.6179 | 84.0077 | 83.955 | 83.833 | 83.703 | 83.5737 | 83.4464 | 83.3203 | 83.1943 | 83.0589 | 82.9244 | 82.6397 | 81.7916 | 80.937 | 80.0942
|  | SHIRLEY | CT |  |  | 70.296 | 70.2895 | 70.2744 | 70.2584 | 70.2424 | 70.2267 | 70.2112 | 70.1957 | 70.179 | 70.1625 | 70.1273 | 70.0227 | 69.9173 | 69.8134 | 52.6455 | 52.5689 | 52.3902 | 52.1998 | 52.0103 | 51.8232 | 51.6373 | 51.4591 | 51.2941 | 51.1304 | 50.8009 | 50.311 | 49.9803 | 49.6519 | 84.0078 | 83.9556 | 83.8339 | 83.7042 | 83.5751 | 83.4476 | 83.321 | 83.1945 | 83.0589 | 82.9244 | 82.6537 | 81.8568 | 81.0159 | 80.1807
|  | SHIRLEY | LW |  |  | 70.296 | 70.2895 | 70.2744 | 70.2584 | 70.2424 | 70.2267 | 70.2112 | 70.1957 | 70.179 | 70.1625 | 70.1273 | 70.0227 | 69.9173 | 69.8134 | 52.6454 | 52.568 | 52.3889 | 52.198 | 52.0082 | 51.8213 | 51.6363 | 51.4589 | 51.2944 | 51.1314 | 50.7838 | 50.2854 | 49.9493 | 49.6179 | 84.0077 | 83.955 | 83.833 | 83.703 | 83.5737 | 83.4464 | 83.3203 | 83.1943 | 83.0592 | 82.9252 | 82.6397 | 81.7916 | 80.937 | 80.0942
|  | SHIRLEY | ST |  |  | 70.2986 | 70.2959 | 70.2903 | 70.282 | 70.272 | 70.2608 | 70.2498 | 70.2388 | 70.227 | 70.2153 | 70.1922 | 70.1294 | 70.0655 | 70.0022 | 52.677 | 52.6451 | 52.5777 | 52.4794 | 52.3607 | 52.2274 | 52.0956 | 51.9646 | 51.8241 | 51.6857 | 51.4245 | 50.8047 | 50.422 | 50.2201 | 84.0293 | 84.0075 | 83.9616 | 83.8947 | 83.8138 | 83.723 | 83.6332 | 83.544 | 83.4483 | 83.354 | 83.1661 | 82.6569 | 82.139 | 81.6256
|  | SHIRLEY | FS |  |  | 70.3 | 70.2995 | 70.2989 | 70.2964 | 70.2935 | 70.2896 | 70.2858 | 70.2809 | 70.276 | 70.2713 | 70.2621 | 70.2378 | 70.2129 | 70.1884 | 52.6931 | 52.6874 | 52.6807 | 52.6512 | 52.6161 | 52.5701 | 52.5245 | 52.4657 | 52.4081 | 52.3514 | 52.2421 | 51.9532 | 51.6569 | 51.3877 | 84.0402 | 84.0363 | 84.0318 | 84.0117 | 83.9878 | 83.9564 | 83.9254 | 83.8853 | 83.846 | 83.8075 | 83.733 | 83.5362 | 83.3344 | 83.1358
MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM | MINIMUM HEADROOM | SU 23782 87902 | YES | -7.5994 | -7.6503 | -7.7445 | -7.8204 | -7.8952 | -7.9688 | -8.0418 | -8.1141 | -8.1916 | -8.2736 | -8.4435 | -8.8132 | -9.2063 | -9.6011 | -2.0563 | -2.1184 | -2.2403 | -2.344 | -2.4482 | -2.5542 | -2.6636 | -2.7714 | -2.8822 | -2.9902 | -3.2062 | -3.6605 | -4.1442 | -4.6255 | 1.0839 | 1.0217 | 0.89982 | 0.79606 | 0.69185 | 0.58583 | 0.4764 | 0.3685 | 0.25769 | 0.14966 | -0.066447 | -0.52084 | -1.0048 | -1.4862
|  | SHRIVENHAM | CT |  |  | -7.5994 | -7.6503 | -7.7445 | -7.8204 | -7.8952 | -7.9688 | -8.0418 | -8.1141 | -8.1916 | -8.2736 | -8.4435 | -8.8132 | -9.2063 | -9.6011 | -2.0563 | -2.1184 | -2.2403 | -2.344 | -2.4482 | -2.5542 | -2.6636 | -2.7714 | -2.8822 | -2.9902 | -3.2062 | -3.6605 | -4.1442 | -4.6255 | 1.0839 | 1.0217 | 0.89982 | 0.79606 | 0.69185 | 0.58583 | 0.4764 | 0.3685 | 0.25769 | 0.14966 | -0.066447 | -0.52084 | -1.0048 | -1.4862
|  | SHRIVENHAM | LW |  |  | -7.5994 | -7.6503 | -7.7445 | -7.8204 | -7.8952 | -7.9688 | -8.0418 | -8.1141 | -8.1916 | -8.2736 | -8.4435 | -8.8132 | -9.2063 | -9.6011 | -2.0533 | -2.113 | -2.2236 | -2.3128 | -2.4006 | -2.487 | -2.5727 | -2.6576 | -2.7485 | -2.8448 | -3.0443 | -3.4783 | -3.9398 | -4.4034 | 1.0869 | 1.0271 | 0.9165 | 0.8273 | 0.7395 | 0.65301 | 0.56733 | 0.48237 | 0.39141 | 0.29515 | 0.095556 | -0.33856 | -0.80025 | -1.2639
|  | SHRIVENHAM | ST |  |  | -7.5365 | -7.5975 | -7.6323 | -7.6622 | -7.6991 | -7.7384 | -7.7798 | -7.8204 | -7.861 | -7.9001 | -7.9783 | -8.1989 | -8.4262 | -8.6513 | -1.9795 | -2.051 | -2.0919 | -2.127 | -2.1703 | -2.2165 | -2.2651 | -2.3127 | -2.3605 | -2.4063 | -2.4981 | -2.7571 | -3.024 | -3.2883 | 1.1607 | 1.0891 | 1.0483 | 1.0131 | 0.96983 | 0.92362 | 0.87503 | 0.82739 | 0.77962 | 0.73377 | 0.64191 | 0.38281 | 0.11585 | -0.14852
|  | SHRIVENHAM | FS |  |  | -7.5227 | -7.5329 | -7.5434 | -7.5543 | -7.5669 | -7.5816 | -7.5959 | -7.6137 | -7.6311 | -7.6481 | -7.6815 | -7.7666 | -7.857 | -7.9484 | -1.9633 | -1.9752 | -1.9876 | -2.0003 | -2.0151 | -2.0324 | -2.0492 | -2.07 | -2.0905 | -2.1105 | -2.1496 | -2.2496 | -2.3557 | -2.463 | 1.177 | 1.165 | 1.1526 | 1.1398 | 1.1251 | 1.1078 | 1.091 | 1.0701 | 1.0496 | 1.0297 | 0.99051 | 0.89054 | 0.7844 | 0.67701
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON | MINIMUM HEADROOM | ST 85356 13659 | YES | 27.2117 | 27.2032 | 27.1825 | 27.1586 | 27.1242 | 27.087 | 27.0492 | 27.0203 | 26.9898 | 26.9594 | 26.8975 | 26.7031 | 22.4011 | 21.9034 | 25.3368 | 25.3275 | 25.3051 | 25.2791 | 25.2417 | 25.2013 | 25.1662 | 25.1443 | 25.1212 | 25.0983 | 25.0514 | 24.9043 | 24.7932 | 20.9215 | 25.0439 | 25.0417 | 25.0362 | 25.0299 | 25.0209 | 25.0111 | 25.0011 | 24.9935 | 24.9855 | 24.9775 | 24.9612 | 21.0404 | 20.4737 | 19.9019
|  | SHROTON | CT |  |  | 27.2117 | 27.2032 | 27.1825 | 27.1586 | 27.1242 | 27.087 | 27.0492 | 27.0203 | 26.9898 | 26.9594 | 26.8975 | 26.7031 | 22.4011 | 21.9034 | 25.3374 | 25.3291 | 25.3088 | 25.2853 | 25.2518 | 25.2158 | 25.1804 | 25.1609 | 25.1398 | 25.1173 | 25.073 | 24.9296 | 24.8119 | 21.0521 | 25.0441 | 25.042 | 25.0371 | 25.0314 | 25.0233 | 25.0146 | 25.006 | 24.9993 | 24.992 | 24.9841 | 24.9687 | 21.1353 | 20.5871 | 20.0355
|  | SHROTON | LW |  |  | 27.2117 | 27.2032 | 27.1825 | 27.1586 | 27.1242 | 27.087 | 27.0492 | 27.0203 | 26.9898 | 26.9594 | 26.8975 | 26.7031 | 22.4011 | 21.9034 | 25.3368 | 25.3275 | 25.3051 | 25.2791 | 25.2417 | 25.2013 | 25.1662 | 25.1443 | 25.1212 | 25.0983 | 25.0514 | 24.9043 | 24.7932 | 20.9215 | 25.0439 | 25.0417 | 25.0362 | 25.0299 | 25.0209 | 25.0111 | 25.0011 | 24.9935 | 24.9855 | 24.9775 | 24.9612 | 21.0404 | 20.4737 | 19.9019
|  | SHROTON | ST |  |  | 27.2514 | 27.2097 | 27.199 | 27.1826 | 27.1569 | 27.1254 | 27.0945 | 27.0685 | 27.0401 | 27.0105 | 26.9522 | 26.8153 | 26.6815 | 22.5107 | 25.3771 | 25.3346 | 25.323 | 25.3052 | 25.2772 | 25.243 | 25.2095 | 25.1812 | 25.1594 | 25.1369 | 25.0928 | 24.9892 | 24.888 | 24.8139 | 25.0537 | 25.0434 | 25.0406 | 25.0363 | 25.0295 | 25.0212 | 25.0131 | 25.0062 | 24.9987 | 24.9909 | 24.9756 | 21.3588 | 20.9791 | 20.5997
|  | SHROTON | FS |  |  | 27.2548 | 27.2538 | 27.2524 | 27.2469 | 27.238 | 27.2276 | 27.2174 | 27.2072 | 27.197 | 27.1867 | 27.1664 | 27.1174 | 27.0697 | 27.0219 | 25.3798 | 25.3791 | 25.3779 | 25.3734 | 25.3654 | 25.3541 | 25.343 | 25.3319 | 25.3208 | 25.3097 | 25.2876 | 25.2343 | 25.1825 | 25.1456 | 25.0543 | 25.0542 | 25.0539 | 25.0528 | 25.0508 | 25.0481 | 25.0454 | 25.0427 | 25.04 | 25.0373 | 25.032 | 25.0191 | 25.0065 | 24.9939
LALEHAM | STAINES | SIDNEY ROAD | MINIMUM HEADROOM | TQ 04100 71760 | YES | 41.6422 | 41.632 | 41.6107 | 41.5873 | 41.563 | 41.5434 | 41.5267 | 41.4968 | 41.4644 | 41.4153 | 41.3038 | 41.1394 | 40.9755 | 40.9725 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 41.9833 | 41.9748 | 41.957 | 41.9375 | 41.9171 | 41.9007 | 41.8866 | 41.8618 | 41.8347 | 41.7937 | 41.7005 | 41.5614 | 41.4227 | 41.2876
|  | SIDNEY ROAD | CT |  |  | 41.6422 | 41.632 | 41.6107 | 41.5873 | 41.563 | 41.5434 | 41.5267 | 41.4968 | 41.4644 | 41.4153 | 41.3038 | 41.1394 | 40.9755 | 40.9725 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 41.9839 | 41.9757 | 41.9581 | 41.9391 | 41.9187 | 41.9016 | 41.8866 | 41.8621 | 41.8352 | 41.7971 | 41.7093 | 41.5614 | 41.4227 | 41.2876
|  | SIDNEY ROAD | LW |  |  | 41.6422 | 41.632 | 41.6107 | 41.5873 | 41.563 | 41.5434 | 41.5267 | 41.4968 | 41.4644 | 41.4153 | 41.3038 | 41.1394 | 40.9755 | 40.9725 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 41.9833 | 41.9748 | 41.957 | 41.9375 | 41.9171 | 41.9007 | 41.8868 | 41.8618 | 41.8347 | 41.7937 | 41.7005 | 41.5631 | 41.4261 | 41.2896
|  | SIDNEY ROAD | ST |  |  | 41.6873 | 41.6441 | 41.6326 | 41.617 | 41.5977 | 41.5773 | 41.5588 | 41.5328 | 41.5041 | 41.4658 | 41.3783 | 41.2641 | 41.1623 | 41.0634 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 42.021 | 41.9849 | 41.9753 | 41.9623 | 41.9461 | 41.9291 | 41.9136 | 41.8919 | 41.8679 | 41.8359 | 41.7628 | 41.6673 | 41.5823 | 41.4996
|  | SIDNEY ROAD | FS |  |  | 41.6942 | 41.6547 | 41.6519 | 41.6467 | 41.6411 | 41.6339 | 41.6273 | 41.616 | 41.6045 | 41.5893 | 41.5557 | 41.5095 | 41.4686 | 41.4312 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 40.7154 | 42.0268 | 41.9937 | 41.9914 | 41.9871 | 41.9824 | 41.9764 | 41.9708 | 41.9614 | 41.9518 | 41.9391 | 41.911 | 41.8725 | 41.8382 | 41.807
NURSLING GSP | ROWNHAMS | SILKSTEAD | MINIMUM HEADROOM | SU 44578 24565 | NO | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 9.2977 | 9.0715 | 8.848 | 8.6073 | 8.3649 | 7.8842 | 7.3105 | 6.6911 | 6.0752 | 12.2437 | 9.475 | 9.2205 | 8.9452 | 8.6729 | 8.4035 | 8.137 | 7.8737 | 7.5901 | 7.3046 | 6.7383 | 6.0625 | 5.3328 | 4.6073 | 12.5047 | 12.494 | 12.4737 | 12.4518 | 12.4302 | 12.4088 | 12.3876 | 12.3666 | 12.3539 | 9.386 | 8.8672 | 8.2481 | 7.5797 | 6.915
|  | SILKSTEAD | CT |  |  | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 9.2977 | 9.0715 | 8.848 | 8.6073 | 8.3649 | 7.8842 | 7.3105 | 6.6911 | 6.0752 | 12.2437 | 9.4949 | 9.2688 | 9.0242 | 8.7823 | 8.5428 | 8.3059 | 8.0716 | 7.8193 | 7.5696 | 7.0778 | 6.372 | 5.6105 | 4.8527 | 12.51 | 12.4955 | 12.4776 | 12.4581 | 12.4389 | 12.4198 | 12.401 | 12.3824 | 12.3623 | 9.4996 | 9.1783 | 8.5317 | 7.8341 | 7.1398
|  | SILKSTEAD | LW |  |  | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 9.2977 | 9.0715 | 8.848 | 8.6073 | 8.3649 | 7.8842 | 7.3105 | 6.6911 | 6.0752 | 12.2437 | 9.475 | 9.2205 | 8.9452 | 8.6729 | 8.4035 | 8.137 | 7.8737 | 7.5901 | 7.3046 | 6.7383 | 6.0625 | 5.3328 | 4.6073 | 12.5047 | 12.494 | 12.4737 | 12.4518 | 12.4302 | 12.4088 | 12.3876 | 12.3666 | 12.3539 | 9.386 | 8.8672 | 8.2481 | 7.5797 | 6.915
|  | SILKSTEAD | ST |  |  | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 9.3857 | 9.0483 | 8.6939 | 8.3412 | 12.2437 | 12.2437 | 9.4343 | 9.2446 | 9.0165 | 8.9441 | 8.8727 | 8.8023 | 8.7266 | 8.6521 | 8.5072 | 8.1097 | 7.6921 | 7.2767 | 12.5283 | 12.5007 | 12.4907 | 12.4756 | 12.4575 | 12.4517 | 12.4461 | 12.4405 | 12.4345 | 12.4285 | 12.417 | 12.3854 | 12.3539 | 9.3605
|  | SILKSTEAD | FS |  |  | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 11.1198 | 12.2437 | 12.2437 | 12.2437 | 12.2437 | 12.2437 | 12.2437 | 9.4824 | 9.45 | 9.4182 | 9.3871 | 9.3266 | 9.1715 | 9.007 | 8.8434 | 12.5486 | 12.5442 | 12.539 | 12.5087 | 12.4986 | 12.4966 | 12.4945 | 12.492 | 12.4894 | 12.487 | 12.4822 | 12.4698 | 12.4568 | 12.4437
BRAMLEY (FLEE) | READING BSP | SILVER STREET | MINIMUM HEADROOM | SU 71957 72821 | NO | 32.5684 | 32.5508 | 32.5089 | 32.4635 | 32.4185 | 32.374 | 32.33 | 32.2864 | 32.2767 | 32.2767 | 32.2767 | 32.2767 | 26.3549 | 25.2783 | 29.2451 | 29.2088 | 29.1224 | 29.0287 | 28.9361 | 28.8444 | 28.7536 | 28.6638 | 28.5823 | 24.7577 | 24.1227 | 22.9229 | 21.6537 | 20.2682 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 24.1855 | 22.7991 | 21.4318
|  | SILVER STREET | CT |  |  | 32.5684 | 32.5508 | 32.5089 | 32.4635 | 32.4185 | 32.374 | 32.33 | 32.2864 | 32.2767 | 32.2767 | 32.2767 | 32.2767 | 26.3549 | 25.2783 | 29.2451 | 29.2088 | 29.1224 | 29.0287 | 28.9361 | 28.8444 | 28.7536 | 28.6638 | 28.5823 | 24.7577 | 24.1227 | 22.9229 | 21.6537 | 20.2682 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 24.1855 | 22.7991 | 21.4318
|  | SILVER STREET | LW |  |  | 32.5684 | 32.5508 | 32.5089 | 32.4635 | 32.4185 | 32.374 | 32.33 | 32.2864 | 32.2767 | 32.2767 | 32.2767 | 32.2767 | 26.3549 | 25.2783 | 29.2479 | 29.2159 | 29.1396 | 29.0568 | 28.9749 | 28.8939 | 28.8138 | 28.7344 | 28.6489 | 28.5817 | 24.5214 | 23.3189 | 22.0695 | 20.7559 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 24.618 | 23.2534 | 21.9129
|  | SILVER STREET | ST |  |  | 32.5762 | 32.5698 | 32.5559 | 32.5349 | 32.5096 | 32.4906 | 32.472 | 32.4536 | 32.4337 | 32.4141 | 32.376 | 32.2786 | 32.2767 | 32.2767 | 29.2621 | 29.2505 | 29.2252 | 29.1869 | 29.1408 | 29.1063 | 29.0723 | 29.0388 | 29.0026 | 28.967 | 28.8975 | 28.7202 | 28.5765 | 24.3807 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806
|  | SILVER STREET | FS |  |  | 32.5794 | 32.5784 | 32.5772 | 32.5702 | 32.5618 | 32.5541 | 32.5465 | 32.5367 | 32.5271 | 32.5176 | 32.4992 | 32.4539 | 32.4093 | 32.3663 | 29.2679 | 29.2661 | 29.2639 | 29.2511 | 29.2359 | 29.2219 | 29.208 | 29.1902 | 29.1727 | 29.1555 | 29.122 | 29.0394 | 28.9582 | 28.8799 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806 | 30.0806
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD | MINIMUM HEADROOM | SZ 18262 93590 | YES | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 25.5878 | 25.5622 | 25.5136 | 25.4554 | 25.389 | 25.321 | 25.244 | 25.1927 | 25.1391 | 25.0837 | 24.9755 | 24.7285 | 18.5999 | 16.8724 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 18.0829 | 16.348
|  | SOMERFORD | CT |  |  | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 25.59 | 25.5694 | 25.53 | 25.4832 | 25.4291 | 25.3727 | 25.3076 | 25.2604 | 25.2099 | 25.1564 | 25.0598 | 24.7285 | 24.7285 | 17.6811 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 18.7196 | 17.1601
|  | SOMERFORD | LW |  |  | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 25.5878 | 25.5622 | 25.5136 | 25.4554 | 25.389 | 25.321 | 25.244 | 25.1927 | 25.1391 | 25.0837 | 24.9755 | 24.7285 | 18.5999 | 16.8724 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 18.0829 | 16.348
|  | SOMERFORD | ST |  |  | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 25.6232 | 25.5785 | 25.552 | 25.5155 | 25.4703 | 25.3994 | 25.3233 | 25.2598 | 25.1909 | 25.1201 | 24.9866 | 24.7285 | 24.7285 | 18.3686 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 17.8506
|  | SOMERFORD | FS |  |  | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 27.7568 | 25.628 | 25.5918 | 25.583 | 25.5693 | 25.5533 | 25.5298 | 25.5048 | 25.4823 | 25.4596 | 25.4364 | 25.3914 | 25.2852 | 25.1794 | 25.0692 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997 | 25.4997
LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTEAD | MINIMUM HEADROOM | SU 94025 00705 | YES | 29.4554 | 29.4533 | 29.4489 | 29.4438 | 29.4384 | 29.4331 | 29.4259 | 29.4155 | 29.4042 | 29.3931 | 29.3931 | 29.3931 | 29.3931 | 29.3931 | 25.8254 | 25.8097 | 25.7766 | 25.7388 | 25.6985 | 25.6587 | 25.6048 | 25.5271 | 25.4427 | 25.358 | 25.2069 | 25.2046 | 25.2046 | 25.2046 | 26.1077 | 26.1037 | 26.0953 | 26.0872 | 26.0812 | 26.0753 | 26.0673 | 26.0558 | 26.0433 | 26.0307 | 26.0267 | 26.0267 | 26.0267 | 26.0267
|  | SOUTH BERSTEAD | CT |  |  | 29.4554 | 29.4533 | 29.4489 | 29.4438 | 29.4384 | 29.4331 | 29.4278 | 29.4224 | 29.4166 | 29.4107 | 29.399 | 29.3931 | 29.3931 | 29.3931 | 25.8255 | 25.8107 | 25.7785 | 25.7421 | 25.7036 | 25.6652 | 25.6272 | 25.587 | 25.5431 | 25.4976 | 25.4084 | 25.2046 | 25.2046 | 25.2046 | 26.1078 | 26.104 | 26.0957 | 26.0877 | 26.082 | 26.0763 | 26.0707 | 26.0647 | 26.0582 | 26.0514 | 26.0382 | 26.0267 | 26.0267 | 26.0267
|  | SOUTH BERSTEAD | LW |  |  | 29.4554 | 29.4533 | 29.4489 | 29.4438 | 29.4384 | 29.4331 | 29.4278 | 29.4224 | 29.4166 | 29.4107 | 29.399 | 29.3931 | 29.3931 | 29.3931 | 25.8254 | 25.8097 | 25.7766 | 25.7388 | 25.6985 | 25.6587 | 25.6193 | 25.5787 | 25.5354 | 25.4912 | 25.4042 | 25.2046 | 25.2046 | 25.2046 | 26.1077 | 26.1037 | 26.0953 | 26.0872 | 26.0812 | 26.0753 | 26.0695 | 26.0635 | 26.057 | 26.0505 | 26.0376 | 26.0267 | 26.0267 | 26.0267
|  | SOUTH BERSTEAD | ST |  |  | 29.4795 | 29.4551 | 29.4531 | 29.4502 | 29.4467 | 29.4362 | 29.4259 | 29.4155 | 29.4042 | 29.3931 | 29.3931 | 29.3931 | 29.3931 | 29.3931 | 26.0057 | 25.823 | 25.8082 | 25.7867 | 25.7604 | 25.682 | 25.6048 | 25.5271 | 25.4427 | 25.358 | 25.2069 | 25.2046 | 25.2046 | 25.2046 | 26.1538 | 26.1071 | 26.1033 | 26.0978 | 26.0911 | 26.0788 | 26.0673 | 26.0558 | 26.0433 | 26.0307 | 26.0267 | 26.0267 | 26.0267 | 26.0267
|  | SOUTH BERSTEAD | FS |  |  | 29.48 | 29.4562 | 29.4558 | 29.4548 | 29.4537 | 29.4508 | 29.4479 | 29.4443 | 29.4407 | 29.4371 | 29.4301 | 29.414 | 29.3931 | 29.3931 | 26.0091 | 25.8316 | 25.8284 | 25.8211 | 25.8125 | 25.7908 | 25.7693 | 25.7424 | 25.7155 | 25.6887 | 25.6361 | 25.5159 | 25.339 | 25.2046 | 26.1546 | 26.1093 | 26.1085 | 26.1066 | 26.1044 | 26.0989 | 26.0934 | 26.0878 | 26.0838 | 26.0798 | 26.072 | 26.0541 | 26.0279 | 26.0267
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE | MINIMUM HEADROOM | SZ 13563 92074 | YES | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 14.1365 | 12.9567 | 11.7332 | 10.4924 | 16.1935 | 16.1616 | 16.1298 | 16.1209 | 16.1115 | 16.1017 | 16.0918 | 16.0819 | 16.071 | 14.2174 | 13.8081 | 12.3194 | 10.7754 | 9.2389 | 16.6142 | 16.5988 | 16.5615 | 16.5194 | 16.4747 | 16.464 | 16.464 | 16.464 | 16.464 | 16.464 | 16.464 | 13.1044 | 11.5599 | 10.0229
|  | SOUTHBOURNE | CT |  |  | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 14.1365 | 12.9567 | 11.7332 | 10.4924 | 16.1951 | 16.1655 | 16.1308 | 16.1226 | 16.1139 | 16.1049 | 16.0958 | 16.0867 | 16.0768 | 16.0669 | 13.9741 | 12.6033 | 11.1825 | 9.7695 | 16.615 | 16.6007 | 16.5661 | 16.5272 | 16.4861 | 16.464 | 16.464 | 16.464 | 16.464 | 16.464 | 16.464 | 13.3884 | 11.9671 | 10.5536
|  | SOUTHBOURNE | LW |  |  | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 14.1365 | 12.9567 | 11.7332 | 10.4924 | 16.1935 | 16.1616 | 16.1298 | 16.1209 | 16.1115 | 16.1017 | 16.0918 | 16.0819 | 16.071 | 14.2174 | 13.8081 | 12.3194 | 10.7754 | 9.2389 | 16.6142 | 16.5988 | 16.5615 | 16.5194 | 16.4747 | 16.464 | 16.464 | 16.464 | 16.464 | 16.464 | 16.464 | 13.1044 | 11.5599 | 10.0229
|  | SOUTHBOURNE | ST |  |  | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 13.5638 | 12.7864 | 12.0125 | 16.2053 | 16.1903 | 16.1568 | 16.1319 | 16.1253 | 16.1152 | 16.1051 | 16.0951 | 16.0843 | 16.0734 | 14.0694 | 13.0854 | 12.1045 | 11.1279 | 16.6218 | 16.6127 | 16.5964 | 16.5714 | 16.5399 | 16.4923 | 16.464 | 16.464 | 16.464 | 16.464 | 16.464 | 13.8632 | 12.8894 | 11.9125
|  | SOUTHBOURNE | FS |  |  | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.1913 | 16.2129 | 16.2107 | 16.2076 | 16.1926 | 16.1738 | 16.1417 | 16.1324 | 16.1282 | 16.1241 | 16.12 | 16.1121 | 16.0933 | 16.075 | 14.1586 | 16.6372 | 16.6327 | 16.6263 | 16.6138 | 16.6047 | 16.5891 | 16.5735 | 16.5539 | 16.5344 | 16.5149 | 16.4776 | 16.464 | 16.464 | 16.464
BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE | MINIMUM HEADROOM | SU 68199 71325 | NO | 22.0753 | 22.0637 | 22.0369 | 22.0077 | 21.9781 | 21.9487 | 21.8936 | 21.839 | 21.78 | 21.7218 | 21.6084 | 21.2855 | 20.828 | 20.828 | 20.0493 | 20.037 | 20.0085 | 19.9774 | 19.9459 | 19.9375 | 19.9262 | 19.9149 | 19.9028 | 19.8908 | 19.8675 | 19.801 | 19.7247 | 19.6668 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675
|  | SOUTHCOTE | CT |  |  | 22.0753 | 22.0637 | 22.0369 | 22.0077 | 21.9781 | 21.9487 | 21.9196 | 21.891 | 21.8596 | 21.8281 | 21.7631 | 21.2855 | 20.828 | 20.828 | 20.0508 | 20.0407 | 20.0175 | 19.9921 | 19.9664 | 19.9426 | 19.9377 | 19.9329 | 19.9276 | 19.9224 | 19.9121 | 19.8257 | 19.7434 | 19.6901 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675
|  | SOUTHCOTE | LW |  |  | 22.0753 | 22.0637 | 22.0369 | 22.0077 | 21.9781 | 21.9487 | 21.9196 | 21.891 | 21.8596 | 21.8281 | 21.7631 | 21.2855 | 20.828 | 20.828 | 20.0493 | 20.037 | 20.0085 | 19.9774 | 19.9459 | 19.9375 | 19.9315 | 19.9256 | 19.9192 | 19.9127 | 19.8993 | 19.801 | 19.7247 | 19.6668 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675
|  | SOUTHCOTE | ST |  |  | 22.1384 | 22.0715 | 22.0563 | 22.0334 | 22.0056 | 21.9491 | 21.8936 | 21.839 | 21.78 | 21.7218 | 21.6084 | 21.3018 | 20.9776 | 20.828 | 20.1166 | 20.0453 | 20.0291 | 20.0048 | 19.9751 | 19.9376 | 19.9262 | 19.9149 | 19.9028 | 19.8908 | 19.8675 | 19.8043 | 19.7473 | 19.7102 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675
|  | SOUTHCOTE | FS |  |  | 22.1423 | 22.0816 | 22.0806 | 22.0756 | 22.0696 | 22.0518 | 22.0341 | 22.0116 | 21.9894 | 21.9676 | 21.9251 | 21.8135 | 21.6963 | 21.5783 | 20.1207 | 20.0561 | 20.055 | 20.0497 | 20.0433 | 20.0243 | 20.0055 | 19.9815 | 19.9579 | 19.9414 | 19.9327 | 19.9097 | 19.8855 | 19.8613 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675 | 20.6675
AXMINSTER | YEOVIL BSP | SPARKFORD | MINIMUM HEADROOM | ST 60767 25496 | YES | 7.4784 | 7.4772 | 7.4754 | 7.4727 | 7.4695 | 7.4681 | 7.4668 | 7.4655 | 7.464 | 7.4627 | 7.4599 | 7.453 | 7.446 | 7.4345 | 6.6241 | 6.6204 | 6.6147 | 6.606 | 6.5956 | 6.5913 | 6.587 | 6.5828 | 6.5783 | 6.5739 | 6.5652 | 6.5432 | 6.5208 | 4.6845 | 7.2896 | 7.2883 | 4.7286 | 4.6952 | 4.655 | 4.6385 | 4.6222 | 4.606 | 4.5886 | 4.5715 | 4.5381 | 4.4534 | 4.3671 | 4.2147
|  | SPARKFORD | CT |  |  | 7.4784 | 7.4782 | 7.4775 | 7.4769 | 7.4762 | 7.4755 | 7.4748 | 7.4742 | 7.4735 | 7.4728 | 7.4714 | 7.4593 | 7.4468 | 7.4345 | 6.6241 | 6.6233 | 6.6213 | 6.6192 | 6.617 | 6.6149 | 6.6128 | 6.6107 | 6.6084 | 6.6061 | 6.6016 | 6.5625 | 6.5216 | 4.6845 | 7.2896 | 7.2893 | 7.2886 | 4.746 | 4.7377 | 4.7295 | 4.7214 | 4.7132 | 4.7044 | 4.6957 | 4.6784 | 4.5279 | 4.3703 | 4.2147
|  | SPARKFORD | LW |  |  | 7.4784 | 7.4782 | 7.4775 | 7.4769 | 7.4762 | 7.4755 | 7.4748 | 7.4742 | 7.4735 | 7.4728 | 7.4714 | 7.4593 | 7.4468 | 7.4345 | 6.6241 | 6.6233 | 6.6213 | 6.6192 | 6.617 | 6.6149 | 6.6127 | 6.6106 | 6.6084 | 6.6061 | 6.6016 | 6.5631 | 6.5233 | 4.6957 | 7.2896 | 7.2893 | 7.2886 | 4.7459 | 4.7377 | 4.7294 | 4.7213 | 4.7131 | 4.7043 | 4.6956 | 4.6784 | 4.5299 | 4.3767 | 4.2258
|  | SPARKFORD | ST |  |  | 7.5036 | 7.4772 | 7.4754 | 7.4727 | 7.4695 | 7.4681 | 7.4668 | 7.4655 | 7.464 | 7.4627 | 7.4599 | 7.453 | 7.446 | 7.439 | 6.7044 | 6.6204 | 6.6147 | 6.606 | 6.5956 | 6.5913 | 6.587 | 6.5828 | 6.5783 | 6.5739 | 6.5652 | 6.5432 | 6.5208 | 6.4985 | 7.3175 | 7.2883 | 4.7286 | 4.6952 | 4.655 | 4.6385 | 4.6222 | 4.606 | 4.5886 | 4.5715 | 4.5381 | 4.4534 | 4.3671 | 4.2814
|  | SPARKFORD | FS |  |  | 7.5041 | 7.4885 | 7.4885 | 7.4884 | 7.4882 | 7.4878 | 7.4873 | 7.4866 | 7.486 | 7.4854 | 7.4842 | 7.4813 | 7.4785 | 7.4758 | 6.706 | 6.6563 | 6.6562 | 6.6559 | 6.6555 | 6.6539 | 6.6523 | 6.6503 | 6.6484 | 6.6464 | 6.6426 | 6.6334 | 6.6243 | 6.6156 | 7.318 | 7.3007 | 7.3007 | 7.3006 | 7.3005 | 7.2999 | 7.2994 | 7.2987 | 7.298 | 7.2973 | 7.296 | 7.2928 | 7.2896 | 4.7324
MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST | MINIMUM HEADROOM | ST 84368 68717 | YES | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 32.3572 | 32.3451 | 32.3149 | 32.2814 | 32.2466 | 32.2205 | 32.1927 | 32.1635 | 32.1314 | 32.0998 | 32.0399 | 31.8486 | 31.8049 | 31.8049 | 33.0813 | 33.0783 | 33.071 | 33.0629 | 33.0545 | 33.0481 | 33.0414 | 33.0344 | 33.0266 | 33.0189 | 33.0044 | 32.9581 | 32.91 | 32.8623
|  | SPRING QUARRY WEST | CT |  |  | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 32.3572 | 32.3451 | 32.3149 | 32.2814 | 32.2466 | 32.2205 | 32.1927 | 32.1635 | 32.1314 | 32.0998 | 32.0399 | 31.8486 | 31.8049 | 31.8049 | 33.0813 | 33.0783 | 33.071 | 33.0629 | 33.0545 | 33.0481 | 33.0414 | 33.0344 | 33.0266 | 33.0189 | 33.0044 | 32.9581 | 32.91 | 32.8623
|  | SPRING QUARRY WEST | LW |  |  | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 32.358 | 32.3466 | 32.3183 | 32.2864 | 32.2528 | 32.2288 | 32.2044 | 32.1798 | 32.1525 | 32.1248 | 32.069 | 31.8736 | 31.8049 | 31.8049 | 33.0814 | 33.0787 | 33.0719 | 33.0641 | 33.056 | 33.0502 | 33.0443 | 33.0383 | 33.0317 | 33.025 | 33.0114 | 32.9641 | 32.9148 | 32.8657
|  | SPRING QUARRY WEST | ST |  |  | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 32.3606 | 32.3541 | 32.3388 | 32.3171 | 32.2913 | 32.269 | 32.2459 | 32.2218 | 32.1953 | 32.1694 | 32.1201 | 31.9951 | 31.8704 | 31.8049 | 33.0821 | 33.0805 | 33.0768 | 33.0716 | 33.0653 | 33.0599 | 33.0543 | 33.0485 | 33.0421 | 33.0358 | 33.0238 | 32.9935 | 32.9634 | 32.9335
|  | SPRING QUARRY WEST | FS |  |  | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 33.6006 | 32.3632 | 32.3617 | 32.3584 | 32.3519 | 32.3445 | 32.3366 | 32.3287 | 32.3186 | 32.3086 | 32.2987 | 32.2789 | 32.231 | 32.1835 | 32.1365 | 33.0827 | 33.0823 | 33.0816 | 33.08 | 33.0782 | 33.0763 | 33.0744 | 33.0719 | 33.0695 | 33.0671 | 33.0623 | 33.0507 | 33.0392 | 33.0278
NORTH HYDE GSP | NORTH HYDE (D) | SPRINGFIELD ROAD | MINIMUM HEADROOM | TQ 11409 80620 | NO | 30.2583 | 30.2571 | 30.2545 | 30.2514 | 30.2471 | 30.2424 | 30.2372 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 28.0798 | 28.0743 | 28.0622 | 28.0476 | 28.0286 | 28.0069 | 27.983 | 27.9575 | 27.9287 | 27.8991 | 27.8367 | 27.6588 | 27.4841 | 27.4412 | 28.502 | 28.4985 | 28.4907 | 28.4813 | 28.4691 | 28.4552 | 28.4398 | 28.4234 | 28.4049 | 28.386 | 28.3459 | 28.2317 | 28.1194 | 28.0698
|  | SPRINGFIELD ROAD | CT |  |  | 30.2583 | 30.2571 | 30.2545 | 30.2514 | 30.2471 | 30.2424 | 30.2372 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 28.0799 | 28.0745 | 28.0624 | 28.0476 | 28.0292 | 28.0105 | 27.9927 | 27.9733 | 27.9491 | 27.9232 | 27.867 | 27.7105 | 27.5557 | 27.4633 | 28.502 | 28.4986 | 28.4908 | 28.4813 | 28.4695 | 28.4575 | 28.446 | 28.4336 | 28.4181 | 28.4014 | 28.3653 | 28.2648 | 28.1654 | 28.0698
|  | SPRINGFIELD ROAD | LW |  |  | 30.2583 | 30.2571 | 30.2545 | 30.2514 | 30.2471 | 30.2424 | 30.2372 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 28.0798 | 28.0743 | 28.0622 | 28.0479 | 28.0286 | 28.0069 | 27.983 | 27.9575 | 27.9287 | 27.8991 | 27.8367 | 27.6588 | 27.4841 | 27.4412 | 28.502 | 28.4985 | 28.4907 | 28.4815 | 28.4691 | 28.4552 | 28.4398 | 28.4234 | 28.4049 | 28.386 | 28.3459 | 28.2317 | 28.1194 | 28.0698
|  | SPRINGFIELD ROAD | ST |  |  | 30.2588 | 30.2582 | 30.2571 | 30.2552 | 30.2525 | 30.2488 | 30.2452 | 30.2415 | 30.2369 | 30.232 | 30.2316 | 30.2316 | 30.2316 | 30.2316 | 28.0819 | 28.0793 | 28.0742 | 28.0656 | 28.053 | 28.0361 | 28.0198 | 28.0026 | 27.9817 | 27.9594 | 27.9115 | 27.789 | 27.6738 | 27.561 | 28.5033 | 28.5017 | 28.4984 | 28.4929 | 28.4848 | 28.4739 | 28.4635 | 28.4524 | 28.439 | 28.4247 | 28.3939 | 28.3152 | 28.2413 | 28.1689
|  | SPRINGFIELD ROAD | FS |  |  | 30.259 | 30.2589 | 30.2588 | 30.2584 | 30.2576 | 30.2565 | 30.2554 | 30.254 | 30.2525 | 30.251 | 30.2476 | 30.2383 | 30.2316 | 30.2316 | 28.0831 | 28.0826 | 28.082 | 28.0799 | 28.0765 | 28.0717 | 28.0666 | 28.0601 | 28.0532 | 28.0461 | 28.0307 | 27.988 | 27.9447 | 27.8994 | 28.5041 | 28.5038 | 28.5034 | 28.5021 | 28.4998 | 28.4968 | 28.4935 | 28.4893 | 28.4849 | 28.4803 | 28.4705 | 28.4431 | 28.4152 | 28.3862
NURSLING GSP | WINCHESTER | ST CROSS | MINIMUM HEADROOM | SU 47287 28156 | NO | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 31.4202 | 31.327 | 31.1054 | 30.8653 | 30.6274 | 30.3915 | 30.2108 | 30.0364 | 29.8488 | 29.6567 | 29.321 | 29.321 | 29.321 | 29.321 | 31.8203 | 31.775 | 31.6674 | 31.5507 | 31.4352 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656
|  | ST CROSS | CT |  |  | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 31.4215 | 31.3303 | 31.1132 | 30.878 | 30.645 | 30.4139 | 30.2313 | 30.0603 | 29.8761 | 29.6938 | 29.3348 | 29.321 | 29.321 | 29.321 | 31.8209 | 31.7766 | 31.6712 | 31.5569 | 31.4437 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656
|  | ST CROSS | LW |  |  | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 31.4202 | 31.327 | 31.1054 | 30.8653 | 30.6274 | 30.3915 | 30.2108 | 30.0364 | 29.8488 | 29.6567 | 29.321 | 29.321 | 29.321 | 29.321 | 31.8203 | 31.775 | 31.6674 | 31.5507 | 31.4352 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656 | 31.3656
|  | ST CROSS | ST |  |  | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 31.5121 | 31.4393 | 31.3786 | 31.2871 | 31.1768 | 31.1062 | 31.0365 | 30.9678 | 30.8939 | 30.8212 | 30.6797 | 30.2857 | 29.9378 | 29.5914 | 31.8649 | 31.8296 | 31.8 | 31.7556 | 31.7021 | 31.6678 | 31.6339 | 31.6006 | 31.5646 | 31.5293 | 31.4606 | 31.3656 | 31.3656 | 31.3656
|  | ST CROSS | FS |  |  | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 33.4223 | 31.5274 | 31.522 | 31.5156 | 31.4802 | 31.438 | 31.4123 | 31.3867 | 31.3541 | 31.3221 | 31.2908 | 31.2297 | 31.065 | 30.8772 | 30.6841 | 31.8724 | 31.8697 | 31.8666 | 31.8494 | 31.8289 | 31.8164 | 31.804 | 31.7882 | 31.7726 | 31.7574 | 31.7278 | 31.6477 | 31.5565 | 31.4627
COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES | MINIMUM HEADROOM | SP 51259 05741 | NO | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 27.9719 | 27.1549 | 26.3507 | 26.6215 | 26.4936 | 26.2043 | 25.9083 | 25.6219 | 25.3362 | 25.0493 | 24.7643 | 24.4607 | 24.163 | 23.5803 | 22.5799 | 21.5522 | 20.5406 | 31.9325 | 31.8882 | 31.7882 | 31.6858 | 26.6667 | 26.4211 | 26.1745 | 25.9295 | 25.6686 | 25.4127 | 24.9119 | 24.052 | 23.1686 | 22.2991
|  | ST EBBES | CT |  |  | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 27.9719 | 27.1549 | 26.3507 | 26.6215 | 26.4936 | 26.2043 | 25.9083 | 25.6219 | 25.3362 | 25.0493 | 24.7643 | 24.4607 | 24.163 | 23.5803 | 22.5799 | 21.5522 | 20.5406 | 31.9325 | 31.8882 | 31.7882 | 31.6858 | 26.6667 | 26.4211 | 26.1745 | 25.9295 | 25.6686 | 25.4127 | 24.9119 | 24.052 | 23.1686 | 22.2991
|  | ST EBBES | LW |  |  | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 27.9719 | 27.1549 | 26.3507 | 26.6242 | 26.4983 | 26.2176 | 25.9321 | 25.6579 | 25.3868 | 25.1186 | 24.8531 | 24.5671 | 24.2847 | 23.7297 | 22.798 | 21.8452 | 20.9072 | 31.9334 | 31.8899 | 31.7928 | 31.6941 | 26.6976 | 26.4646 | 26.2341 | 26.0059 | 25.76 | 25.5173 | 25.0402 | 24.2394 | 23.4205 | 22.6142
|  | ST EBBES | ST |  |  | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 26.6756 | 26.6267 | 26.5293 | 26.4009 | 26.2517 | 26.1452 | 26.0373 | 25.9302 | 25.8171 | 25.7078 | 25.4976 | 24.9882 | 24.4815 | 23.9763 | 31.9512 | 31.9343 | 31.9006 | 31.8562 | 31.8046 | 31.7677 | 31.7305 | 31.6934 | 31.6543 | 31.6165 | 26.5598 | 26.122 | 25.6865 | 25.2523
|  | ST EBBES | FS |  |  | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 32.1617 | 26.6967 | 26.6831 | 26.6663 | 26.6176 | 26.5627 | 26.521 | 26.4798 | 26.4276 | 26.3762 | 26.3259 | 26.2284 | 26.0001 | 25.7852 | 25.5834 | 31.9585 | 31.9538 | 31.948 | 31.9311 | 31.9122 | 31.8977 | 31.8835 | 31.8654 | 31.8477 | 31.8303 | 31.7966 | 31.7176 | 31.6433 | 26.6336
BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS | MINIMUM HEADROOM | SU 47113 66363 | NO | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926
|  | ST JOHNS | CT |  |  | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926
|  | ST JOHNS | LW |  |  | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926
|  | ST JOHNS | ST |  |  | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926
|  | ST JOHNS | FS |  |  | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 39.3864 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 24.92 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926 | 35.926
COWLEY GSP | WITNEY BSP | STANDLAKE | MINIMUM HEADROOM | SP 38923 02349 | YES | 10.975 | 10.975 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 9.7973 | 9.7759 | 18.326 | 18.2922 | 18.2587 | 18.2256 | 18.1929 | 18.1605 | 18.1257 | 18.0911 | 18.02 | 17.9 | 17.7757 | 17.724 | 9.7075 | 9.7075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075
|  | STANDLAKE | CT |  |  | 10.975 | 10.975 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 9.7997 | 9.782 | 18.3398 | 18.3071 | 18.2793 | 18.2519 | 18.2247 | 18.1978 | 18.1689 | 18.1402 | 18.0826 | 17.9604 | 17.8321 | 17.7311 | 9.7075 | 9.7075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075
|  | STANDLAKE | LW |  |  | 10.975 | 10.975 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 9.7973 | 9.7759 | 18.326 | 18.2922 | 18.2587 | 18.2256 | 18.1929 | 18.1605 | 18.1257 | 18.0911 | 18.02 | 17.9 | 17.7757 | 17.724 | 9.7075 | 9.7075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075
|  | STANDLAKE | ST |  |  | 10.975 | 10.975 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 9.8435 | 9.7899 | 18.3606 | 18.3208 | 18.2883 | 18.2738 | 18.2594 | 18.2453 | 18.2301 | 18.2151 | 18.1851 | 18.1078 | 18.0293 | 17.9509 | 9.7075 | 9.7075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075
|  | STANDLAKE | FS |  |  | 10.975 | 10.975 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 9.8508 | 9.8093 | 18.4077 | 18.3985 | 18.3875 | 18.3798 | 18.3723 | 18.3625 | 18.3529 | 18.3435 | 18.326 | 18.2974 | 18.2686 | 18.2406 | 9.7075 | 9.7075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075 | 18.3075
MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN | MINIMUM HEADROOM | SU 17585 90987 | YES | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 12.8069 | 12.1911 | 11.5776 | -12.4085 | -12.588 | -12.8156 | -13.111 | -13.3675 | -13.6065 | -13.8319 | -14.0768 | -14.3405 | -14.6672 | -15.1295 | -16.085 | -16.9329 | -17.7584 | -8.5129 | -8.6924 | -8.0301 | -9.2156 | -9.4722 | -9.7112 | -9.9368 | -10.1817 | -10.4455 | -10.7723 | -11.2347 | -12.1906 | -13.0388 | -13.8646
|  | STANTON FITZWARREN | CT |  |  | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 12.8069 | 12.1911 | 11.5776 | -12.4069 | -12.5658 | -12.7795 | -13.0485 | -13.285 | -13.5192 | -13.7593 | -14.0349 | -14.3405 | -14.6672 | -15.1295 | -16.085 | -16.9329 | -17.7584 | -8.5112 | -8.6702 | -7.994 | -9.1531 | -9.3897 | -9.624 | -9.8641 | -10.1398 | -10.4455 | -10.7723 | -11.2347 | -12.1906 | -13.0388 | -13.8646
|  | STANTON FITZWARREN | LW |  |  | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 12.8069 | 12.1911 | 11.5776 | -12.4085 | -12.588 | -12.8156 | -13.111 | -13.3675 | -13.6065 | -13.8319 | -14.0768 | -14.3366 | -14.627 | -15.0118 | -15.8967 | -16.7572 | -17.6143 | -8.5129 | -8.6924 | -8.0301 | -9.2156 | -9.4722 | -9.7112 | -9.9368 | -10.1817 | -10.4416 | -10.7321 | -11.117 | -12.0022 | -12.863 | -13.7204
|  | STANTON FITZWARREN | ST |  |  | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 12.9963 | 12.6202 | -11.5191 | -12.4671 | -12.5852 | -12.7432 | -12.8836 | -13.0808 | -13.281 | -13.5041 | -13.7553 | -14.0248 | -14.4331 | -15.0854 | -15.632 | -16.1576 | -7.6231 | -8.5715 | -7.7997 | -8.8477 | -8.9881 | -9.1854 | -9.3857 | -9.6088 | -9.8601 | -10.1297 | -10.5382 | -11.1906 | -11.7374 | -12.2632
|  | STANTON FITZWARREN | FS |  |  | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | 46.6274 | -11.4423 | -12.3958 | -12.4588 | -12.5418 | -12.612 | -12.6951 | -12.7746 | -12.8649 | -12.9596 | -13.0627 | -13.2256 | -13.4908 | -13.7081 | -13.9154 | -7.5464 | -8.5002 | -7.6732 | -8.6462 | -8.7164 | -8.7996 | -8.879 | -8.9695 | -9.0642 | -9.1673 | -9.3302 | -9.5955 | -9.8129 | -10.0203
LALEHAM | STAINES | STANWELL | MINIMUM HEADROOM | TQ 06003 72766 | YES | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3668 | 26.3621 | 26.3527 | 26.3516 | 26.3505 | 26.3493 | 26.3463 | 26.331 | 26.312 | 26.2914 | 26.2742 | 26.2742 | 26.2742 | 26.2742 | 19.5964 | 19.5919 | 19.5817 | 19.5705 | 19.5594 | 19.5472 | 19.5167 | 19.3593 | 19.1647 | 18.9532 | 18.4648 | 18.2385 | 18.0493 | 17.8562
|  | STANWELL | CT |  |  | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3668 | 26.3622 | 26.3527 | 26.3516 | 26.3505 | 26.3494 | 26.3483 | 26.3341 | 26.3184 | 26.3012 | 26.2742 | 26.2742 | 26.2742 | 26.2742 | 19.5964 | 19.592 | 19.5819 | 19.5708 | 19.5598 | 19.5487 | 19.5376 | 19.3913 | 19.2303 | 19.0544 | 18.6011 | 18.266 | 18.0643 | 17.8865
|  | STANWELL | LW |  |  | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3668 | 26.3621 | 26.3527 | 26.3516 | 26.3505 | 26.3494 | 26.3483 | 26.331 | 26.312 | 26.2914 | 26.2742 | 26.2742 | 26.2742 | 26.2742 | 19.5964 | 19.5919 | 19.5817 | 19.5705 | 19.5594 | 19.5482 | 19.537 | 19.3593 | 19.1647 | 18.9532 | 18.4648 | 18.2385 | 18.0493 | 17.8562
|  | STANWELL | ST |  |  | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3686 | 26.3665 | 26.3622 | 26.3557 | 26.3523 | 26.3493 | 26.3463 | 26.3346 | 26.3214 | 26.307 | 26.2742 | 26.2742 | 26.2742 | 26.2742 | 19.5982 | 19.5962 | 19.592 | 19.5857 | 19.5782 | 19.5472 | 19.5167 | 19.3963 | 19.2612 | 19.1133 | 18.7369 | 18.4265 | 18.2215 | 18.0356
|  | STANWELL | FS |  |  | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3223 | 26.3698 | 26.3694 | 26.3689 | 26.3671 | 26.3649 | 26.3581 | 26.3526 | 26.3483 | 26.3435 | 26.3382 | 26.3255 | 26.315 | 26.3081 | 26.3029 | 19.5993 | 19.5989 | 19.5985 | 19.5967 | 19.5946 | 19.5881 | 19.5816 | 19.5371 | 19.4878 | 19.4333 | 19.3028 | 19.1956 | 19.1248 | 19.0717
MANNINGTON GSP | SALISBURY | STAPLEFORD | MINIMUM HEADROOM | SU 06871 37078 | YES | 9.4792 | 9.4754 | 9.4661 | 9.456 | 9.4455 | 9.4348 | 9.4239 | 9.4129 | 9.4007 | 9.3885 | 9.3636 | 9.2838 | 9.2008 | 9.1183 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 9.4214 | 9.0618 | 8.7042 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 9.4725 | 9.1241
|  | STAPLEFORD | CT |  |  | 9.4792 | 9.4754 | 9.4661 | 9.456 | 9.4455 | 9.4348 | 9.4239 | 9.4129 | 9.4007 | 9.3885 | 9.3636 | 9.2838 | 9.2008 | 9.1183 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 9.4921 | 9.1266 | 8.7647 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 9.1831
|  | STAPLEFORD | LW |  |  | 9.4792 | 9.4754 | 9.4661 | 9.456 | 9.4455 | 9.4348 | 9.4239 | 9.4129 | 9.4007 | 9.3885 | 9.3636 | 9.2838 | 9.2008 | 9.1183 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 9.4214 | 9.0618 | 8.7042 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 9.4725 | 9.1241
|  | STAPLEFORD | ST |  |  | 9.4804 | 9.4781 | 9.4731 | 9.4655 | 9.4561 | 9.4465 | 9.4368 | 9.4272 | 9.4167 | 9.4063 | 9.3854 | 9.3318 | 9.2782 | 9.2252 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 9.3973 | 9.1677 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742
|  | STAPLEFORD | FS |  |  | 9.4999 | 9.4814 | 9.4812 | 9.4795 | 9.4776 | 9.4745 | 9.4715 | 9.4675 | 9.4635 | 9.4596 | 9.4517 | 9.432 | 9.4124 | 9.3931 | 11.3609 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.345 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742 | 11.7742
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH | MINIMUM HEADROOM | SU 77124 94355 | YES | 16.6871 | 16.6871 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 14.3509 | 14.3473 | 20.5636 | 20.5543 | 20.5451 | 20.536 | 20.527 | 20.518 | 20.5084 | 20.4988 | 20.4797 | 20.3933 | 20.3361 | 20.3082 | 15.0827 | 15.0827 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077
|  | STOKENCHURCH | CT |  |  | 16.6871 | 16.6871 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 14.3509 | 14.3473 | 20.5636 | 20.5543 | 20.5451 | 20.536 | 20.527 | 20.518 | 20.5084 | 20.4988 | 20.4797 | 20.3933 | 20.3361 | 20.3082 | 15.0827 | 15.0827 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077
|  | STOKENCHURCH | LW |  |  | 16.6871 | 16.6871 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 14.3514 | 14.3485 | 20.5667 | 20.5593 | 20.552 | 20.5447 | 20.5376 | 20.5305 | 20.5226 | 20.5148 | 20.4991 | 20.4152 | 20.3438 | 20.3166 | 15.0827 | 15.0827 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077
|  | STOKENCHURCH | ST |  |  | 16.6871 | 16.6871 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 14.3603 | 14.3522 | 20.5758 | 20.5737 | 20.5711 | 20.5604 | 20.5498 | 20.5395 | 20.5283 | 20.5173 | 20.4957 | 20.4423 | 20.3885 | 20.3461 | 15.0827 | 15.0827 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077
|  | STOKENCHURCH | FS |  |  | 16.6871 | 16.6871 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 23.7371 | 14.3606 | 14.3605 | 20.5854 | 20.5848 | 20.5841 | 20.5805 | 20.577 | 20.5724 | 20.568 | 20.5636 | 20.5551 | 20.5343 | 20.5142 | 20.4952 | 15.0827 | 15.0827 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077 | 21.3077
MINETY GSP | STRATTON (2 X 60) | STRATTON | MINIMUM HEADROOM | SU 16998 88837 | YES | 52.4414 | 52.4317 | 52.4162 | 52.411 | 52.4102 | 52.4091 | 52.4079 | 52.4064 | 52.4042 | 52.4018 | 52.3959 | 52.3747 | 52.3387 | 52.2865 | 46.9467 | 46.8649 | 46.7335 | 46.5842 | 46.4236 | 46.2506 | 46.0372 | 45.7834 | 45.5783 | 45.4076 | 45.0563 | 44.1982 | 43.3498 | 42.5893 | 46.0716 | 46.0703 | 46.0684 | 46.0662 | 46.0637 | 46.061 | 46.0582 | 46.0552 | 46.0508 | 46.0459 | 46.0345 | 45.995 | 45.935 | 45.8609
|  | STRATTON | CT |  |  | 52.4414 | 52.4317 | 52.4162 | 52.411 | 52.4102 | 52.4091 | 52.4079 | 52.4064 | 52.4042 | 52.4018 | 52.3959 | 52.3747 | 52.3387 | 52.2865 | 46.9488 | 46.8758 | 46.755 | 46.6198 | 46.473 | 46.3114 | 46.1159 | 45.8812 | 45.6773 | 45.4922 | 45.1143 | 44.2681 | 43.4407 | 42.7211 | 46.0716 | 46.0703 | 46.0684 | 46.0662 | 46.0637 | 46.061 | 46.0582 | 46.0552 | 46.0508 | 46.0459 | 46.0345 | 45.995 | 45.935 | 45.8609
|  | STRATTON | LW |  |  | 52.4414 | 52.4317 | 52.4162 | 52.411 | 52.4102 | 52.4091 | 52.4079 | 52.4064 | 52.4042 | 52.4018 | 52.3959 | 52.3747 | 52.3387 | 52.2865 | 46.9467 | 46.8649 | 46.7335 | 46.5842 | 46.4236 | 46.2506 | 46.0372 | 45.7834 | 45.5783 | 45.4076 | 45.0563 | 44.1982 | 43.3498 | 42.5893 | 46.0728 | 46.0724 | 46.0718 | 46.0712 | 46.0703 | 46.0693 | 46.068 | 46.0666 | 46.0644 | 46.062 | 46.0561 | 46.035 | 45.9992 | 45.9471
|  | STRATTON | ST |  |  | 52.445 | 52.44 | 52.4328 | 52.4235 | 52.4124 | 52.4119 | 52.4115 | 52.411 | 52.4105 | 52.41 | 52.4088 | 52.4038 | 52.3954 | 52.3832 | 46.9748 | 46.9322 | 46.8711 | 46.7914 | 46.6956 | 46.5635 | 46.4096 | 46.2301 | 46.0674 | 45.9169 | 45.6085 | 45.0219 | 44.4848 | 43.957 | 46.0732 | 46.073 | 46.0728 | 46.0726 | 46.0724 | 46.072 | 46.0716 | 46.0712 | 46.0707 | 46.0701 | 46.069 | 46.064 | 46.0556 | 46.0435
|  | STRATTON | FS |  |  | 52.4862 | 52.4447 | 52.442 | 52.4378 | 52.4331 | 52.4272 | 52.4203 | 52.412 | 52.4118 | 52.4116 | 52.4112 | 52.4095 | 52.407 | 52.4042 | 47.3365 | 46.9726 | 46.9498 | 46.9144 | 46.8748 | 46.8241 | 46.7649 | 46.691 | 46.6275 | 46.5704 | 46.4525 | 46.2278 | 46.0176 | 45.8069 | 46.0732 | 46.0731 | 46.073 | 46.0729 | 46.0727 | 46.0725 | 46.0724 | 46.0722 | 46.072 | 46.0718 | 46.0713 | 46.0696 | 46.0671 | 46.0644
LALEHAM | STAINES | SUNBURY CROSS | MINIMUM HEADROOM | TQ 10053 69996 | YES | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 66.9552 | 66.9227 | 66.8432 | 66.7543 | 66.6611 | 66.5628 | 66.4598 | 66.352 | 66.2357 | 66.1154 | 65.8587 | 65.0861 | 64.2933 | 63.9424 | 65.0109 | 65.003 | 64.9837 | 64.9622 | 64.9396 | 64.9158 | 64.8909 | 64.8864 | 64.8864 | 64.8864 | 64.8864 | 64.8864 | 64.8864 | 64.8864
|  | SUNBURY CROSS | CT |  |  | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 66.9591 | 66.9333 | 66.8692 | 66.798 | 66.7231 | 66.6431 | 66.5597 | 66.4678 | 66.3664 | 66.258 | 66.0253 | 65.3772 | 64.705 | 64.0295 | 65.0118 | 65.0055 | 64.99 | 64.9728 | 64.9546 | 64.9353 | 64.9151 | 64.8928 | 64.8864 | 64.8864 | 64.8864 | 64.8864 | 64.8864 | 64.8864
|  | SUNBURY CROSS | LW |  |  | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 66.9552 | 66.9227 | 66.8432 | 66.7543 | 66.6611 | 66.5628 | 66.4598 | 66.352 | 66.2357 | 66.1154 | 65.8587 | 65.0861 | 64.2933 | 63.9424 | 65.0109 | 65.003 | 64.9837 | 64.9622 | 64.9396 | 64.9158 | 64.8909 | 64.8864 | 64.8864 | 64.8864 | 64.8864 | 64.8864 | 64.8864 | 64.8864
|  | SUNBURY CROSS | ST |  |  | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 66.9685 | 66.9524 | 66.9151 | 66.8638 | 66.8027 | 66.6908 | 66.5777 | 66.4599 | 66.3303 | 66.1961 | 65.9171 | 65.3979 | 64.8816 | 64.3663 | 65.0141 | 65.0102 | 65.0011 | 64.9887 | 64.9739 | 64.9468 | 64.9194 | 64.8909 | 64.8864 | 64.8864 | 64.8864 | 64.8864 | 64.8864 | 64.8864
|  | SUNBURY CROSS | FS |  |  | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 73.5436 | 66.9778 | 66.9726 | 66.9627 | 66.9441 | 66.923 | 66.8842 | 66.8447 | 66.7962 | 66.7467 | 66.6961 | 66.5915 | 66.3985 | 66.2098 | 66.0214 | 65.0163 | 65.0151 | 65.0127 | 65.0082 | 65.003 | 64.9937 | 64.9841 | 64.9723 | 64.9603 | 64.9481 | 64.9228 | 64.8864 | 64.8864 | 64.8864
BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL | MINIMUM HEADROOM | SU 93757 67606 | NO | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 22.6265 | 22.2196 | 21.5745 | 20.8926 | 20.2152 | 21.2696 | 21.1723 | 20.9532 | 20.7166 | 20.4825 | 20.2508 | 20.0212 | 19.7938 | 19.5486 | 19.3056 | 18.8275 | 18.0694 | 17.211 | 16.3554 | 22.6572 | 22.6445 | 22.6158 | 21.301 | 21.0659 | 20.8332 | 20.6027 | 20.3743 | 20.128 | 19.884 | 19.4039 | 18.6425 | 17.7804 | 16.9212
|  | SUNNINGHILL | CT |  |  | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 22.6265 | 22.2196 | 21.5745 | 20.8926 | 20.2152 | 21.2716 | 21.1769 | 20.9618 | 20.7296 | 20.4989 | 20.2698 | 20.0432 | 19.8195 | 19.5783 | 19.3396 | 18.8704 | 18.0709 | 17.211 | 16.3554 | 22.6575 | 22.6451 | 22.617 | 21.3141 | 21.0824 | 20.8523 | 20.6247 | 20.4002 | 20.1579 | 19.9182 | 19.4469 | 18.644 | 17.7804 | 16.9212
|  | SUNNINGHILL | LW |  |  | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 22.6265 | 22.2196 | 21.5745 | 20.8926 | 20.2152 | 21.2696 | 21.1723 | 20.9532 | 20.7166 | 20.4825 | 20.2508 | 20.0212 | 19.7938 | 19.5486 | 19.3056 | 18.8275 | 18.0694 | 17.2681 | 16.4722 | 22.6572 | 22.6445 | 22.6158 | 21.301 | 21.0659 | 20.8332 | 20.6027 | 20.3743 | 20.128 | 19.884 | 19.4039 | 18.6425 | 17.8378 | 17.0384
|  | SUNNINGHILL | ST |  |  | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 22.3593 | 21.3174 | 21.2814 | 21.2095 | 21.1018 | 20.9713 | 20.8848 | 20.7995 | 20.7157 | 20.6253 | 20.5365 | 20.3641 | 19.9214 | 19.4564 | 18.9917 | 22.6635 | 22.6588 | 22.6494 | 22.6353 | 22.6182 | 22.6075 | 22.6007 | 21.3002 | 21.2093 | 21.1202 | 20.947 | 20.5024 | 20.0355 | 19.5688
|  | SUNNINGHILL | FS |  |  | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 24.4865 | 21.3402 | 21.3332 | 21.3273 | 21.2953 | 21.2577 | 21.2274 | 21.1974 | 21.1588 | 21.1207 | 21.0834 | 21.0114 | 20.8321 | 20.6493 | 20.4703 | 22.6665 | 22.6656 | 22.6648 | 22.6606 | 22.6557 | 22.6517 | 22.6478 | 22.6427 | 22.6378 | 22.6329 | 22.6235 | 22.6033 | 21.2334 | 21.0537
MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER | MINIMUM HEADROOM | ST 93394 80051 | YES | 17.1437 | 17.1406 | 17.1332 | 17.1252 | 17.1173 | 17.1093 | 17.1014 | 17.0936 | 17.085 | 17.0765 | 17.0597 | 17.0398 | 17.0192 | 17.003 | 16.1005 | 16.0944 | 16.0799 | 16.0641 | 16.0485 | 16.0328 | 16.0173 | 16.0018 | 15.985 | 15.9682 | 15.935 | 15.8959 | 15.8552 | 15.8149 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939
|  | SUTTON BENGER | CT |  |  | 17.1437 | 17.1406 | 17.1332 | 17.1252 | 17.1173 | 17.1093 | 17.1014 | 17.0936 | 17.085 | 17.0765 | 17.0597 | 17.0398 | 17.0192 | 17.003 | 16.1012 | 16.0961 | 16.0839 | 16.0708 | 16.0576 | 16.0445 | 16.0315 | 16.0186 | 16.0046 | 15.9907 | 15.9631 | 15.9216 | 15.8787 | 15.8362 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939
|  | SUTTON BENGER | LW |  |  | 17.1437 | 17.1406 | 17.1332 | 17.1252 | 17.1173 | 17.1093 | 17.1014 | 17.0936 | 17.085 | 17.0765 | 17.0597 | 17.0398 | 17.0192 | 17.003 | 16.1005 | 16.0944 | 16.0799 | 16.0641 | 16.0485 | 16.0328 | 16.0173 | 16.0018 | 15.985 | 15.9682 | 15.935 | 15.8959 | 15.8552 | 15.8149 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939
|  | SUTTON BENGER | ST |  |  | 17.1589 | 17.1453 | 17.1446 | 17.1436 | 17.1424 | 17.1402 | 17.1381 | 17.1359 | 17.1336 | 17.1313 | 17.1266 | 17.1148 | 17.1031 | 17.0914 | 16.1305 | 16.1036 | 16.1024 | 16.1004 | 16.098 | 16.0937 | 16.0895 | 16.0852 | 16.0806 | 16.076 | 16.0669 | 16.0437 | 16.0205 | 15.9975 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939
|  | SUTTON BENGER | FS |  |  | 17.159 | 17.1589 | 17.1588 | 17.158 | 17.157 | 17.1562 | 17.1555 | 17.1545 | 17.1535 | 17.1525 | 17.1505 | 17.1457 | 17.1409 | 17.1363 | 16.1307 | 16.1305 | 16.1302 | 16.1287 | 16.1268 | 16.1253 | 16.1237 | 16.1218 | 16.1198 | 16.1179 | 16.114 | 16.1045 | 16.0951 | 16.086 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939 | 16.9939
IVER 132KV | UPTON BSP | SUTTON LANE | MINIMUM HEADROOM | TQ 02185 78595 | NO | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 21.1192 | 20.658 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968
|  | SUTTON LANE | CT |  |  | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 21.2022 | 20.7737 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968
|  | SUTTON LANE | LW |  |  | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 21.1192 | 20.658 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968
|  | SUTTON LANE | ST |  |  | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 21.2376 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968
|  | SUTTON LANE | FS |  |  | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 27.4538 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.8927 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968 | 26.6968
MANNINGTON GSP | WAREHAM | SWANAGE | MINIMUM HEADROOM | SZ 02010 79296 | YES | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 9.3759 | 8.7841 | 11.3441 | 11.3429 | 11.3397 | 11.3359 | 11.3314 | 11.3266 | 11.3215 | 11.3162 | 11.3107 | 11.305 | 9.3948 | 8.6788 | 7.9058 | 7.2087 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 8.9568 | 8.1862 | 7.4912
|  | SWANAGE | CT |  |  | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 9.3759 | 8.7841 | 11.3442 | 11.3429 | 11.3399 | 11.3362 | 11.332 | 11.3274 | 11.3226 | 11.3177 | 11.3125 | 11.3072 | 9.4542 | 8.7029 | 7.9589 | 7.2227 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 8.9809 | 8.2392 | 7.5052
|  | SWANAGE | LW |  |  | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 9.3759 | 8.7841 | 11.3441 | 11.3429 | 11.3397 | 11.3359 | 11.3314 | 11.3266 | 11.3215 | 11.3162 | 11.3107 | 11.305 | 9.3948 | 8.6788 | 7.9058 | 7.2087 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 8.9568 | 8.1862 | 7.4912
|  | SWANAGE | ST |  |  | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 9.4248 | 11.3446 | 11.344 | 11.3426 | 11.3405 | 11.3376 | 11.3326 | 11.3275 | 11.3224 | 11.3168 | 11.3112 | 11.3 | 8.9799 | 8.466 | 7.9634 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 9.2571 | 8.7447 | 8.2436
|  | SWANAGE | FS |  |  | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 13.3986 | 11.3449 | 11.3448 | 11.3445 | 11.3438 | 11.3429 | 11.3415 | 11.34 | 11.3383 | 11.3365 | 11.3347 | 11.3312 | 11.3222 | 11.3126 | 11.3037 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051 | 12.051
MINETY GSP | SWINDON BSP | SWINDON | MINIMUM HEADROOM | SU 12449 86967 | YES | 21.7257 | 21.6687 | 21.5376 | 21.3946 | 21.2505 | 21.1058 | 20.9603 | 20.8142 | 20.6571 | 20.5004 | 20.1767 | 18.2503 | 16.1991 | 14.1437 | 11.6439 | 11.5641 | 11.3803 | 11.1798 | 10.9778 | 10.7749 | 10.5709 | 10.3662 | 10.1459 | 9.9262 | 9.4724 | 6.7716 | 3.8958 | 1.0143 | 14.8924 | 14.8149 | 14.6365 | 14.4418 | 14.2457 | 14.0488 | 13.8507 | 13.6519 | 13.4381 | 13.2249 | 12.7843 | 10.1624 | 7.3707 | 4.5734
|  | SWINDON | CT |  |  | 21.7257 | 21.6687 | 21.5376 | 21.3946 | 21.2505 | 21.1058 | 20.9603 | 20.8142 | 20.6571 | 20.5004 | 20.1767 | 18.2503 | 16.1991 | 14.1437 | 11.6469 | 11.5722 | 11.3992 | 11.2107 | 11.0209 | 10.8302 | 10.6383 | 10.4457 | 10.2384 | 10.0316 | 9.6224 | 7.288 | 4.6327 | 1.9449 | 14.8953 | 14.8227 | 14.6548 | 14.4718 | 14.2876 | 14.1024 | 13.9162 | 13.7292 | 13.528 | 13.3271 | 12.9299 | 10.6638 | 8.086 | 5.4768
|  | SWINDON | LW |  |  | 21.7257 | 21.6687 | 21.5376 | 21.3946 | 21.2505 | 21.1058 | 20.9603 | 20.8142 | 20.6571 | 20.5004 | 20.1767 | 18.2503 | 16.1991 | 14.1437 | 11.6439 | 11.5641 | 11.3803 | 11.1798 | 10.9778 | 10.7749 | 10.5709 | 10.3662 | 10.1459 | 9.9262 | 9.4724 | 6.7716 | 3.8958 | 1.0143 | 14.8924 | 14.8149 | 14.6365 | 14.4418 | 14.2457 | 14.0488 | 13.8507 | 13.6519 | 13.4381 | 13.2249 | 12.7843 | 10.1624 | 7.3707 | 4.5734
|  | SWINDON | ST |  |  | 21.7974 | 21.7179 | 21.6588 | 21.5706 | 21.4635 | 21.2896 | 21.1168 | 20.9453 | 20.7604 | 20.5776 | 20.22 | 19.031 | 17.7407 | 16.4614 | 11.7444 | 11.633 | 11.5502 | 11.4265 | 11.2763 | 11.0325 | 10.7903 | 10.5499 | 10.2907 | 10.0343 | 9.533 | 7.8661 | 6.0571 | 4.2636 | 14.99 | 14.8818 | 14.8014 | 14.6813 | 14.5355 | 14.2988 | 14.0637 | 13.8303 | 13.5787 | 13.3298 | 12.8432 | 11.225 | 9.4688 | 7.7277
|  | SWINDON | FS |  |  | 21.8118 | 21.7559 | 21.7507 | 21.7279 | 21.7009 | 21.6462 | 21.5917 | 21.5219 | 21.453 | 21.3851 | 21.2524 | 20.836 | 20.3478 | 19.8307 | 11.7647 | 11.6863 | 11.6791 | 11.6471 | 11.6092 | 11.5326 | 11.4561 | 11.3582 | 11.2617 | 11.1664 | 10.9805 | 10.3966 | 9.7122 | 8.9873 | 15.0096 | 14.9335 | 14.9265 | 14.8955 | 14.8587 | 14.7843 | 14.71 | 14.615 | 14.5213 | 14.4288 | 14.2483 | 13.6815 | 13.0171 | 12.3134
BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY | MINIMUM HEADROOM | SU 57753 62717 | NO | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 25.7101 | 25.7048 | 25.6922 | 25.6786 | 25.6651 | 25.6518 | 25.6386 | 25.6255 | 25.6114 | 25.5974 | 25.5731 | 25.5313 | 25.4872 | 21.3439 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 21.1539
|  | TADLEY | CT |  |  | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 25.7106 | 25.7061 | 25.6954 | 25.6837 | 25.6723 | 25.6609 | 25.6496 | 25.6384 | 25.6262 | 25.6141 | 25.5906 | 25.5402 | 25.4971 | 25.4538 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448
|  | TADLEY | LW |  |  | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 25.7101 | 25.7048 | 25.6922 | 25.6786 | 25.6651 | 25.6518 | 25.6386 | 25.6255 | 25.6114 | 25.5974 | 25.5737 | 25.5313 | 25.4872 | 21.3439 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 21.1539
|  | TADLEY | ST |  |  | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 25.738 | 25.7085 | 25.7016 | 25.6913 | 25.6789 | 25.6631 | 25.6475 | 25.6321 | 25.6154 | 25.5991 | 25.5731 | 25.5461 | 25.5182 | 25.4902 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448
|  | TADLEY | FS |  |  | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 27.9263 | 25.7397 | 25.7393 | 25.7388 | 25.7365 | 25.7338 | 25.7287 | 25.7236 | 25.717 | 25.7106 | 25.7043 | 25.692 | 25.6602 | 25.6274 | 25.5948 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448 | 26.0448
IVER 132KV | SLOUGH | TAPLOW | MINIMUM HEADROOM | SU 91721 81234 | NO | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 32.9935 | 32.8835 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737
|  | TAPLOW | CT |  |  | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 33.0005 | 32.8997 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737
|  | TAPLOW | LW |  |  | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 32.9935 | 32.8835 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737
|  | TAPLOW | ST |  |  | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 33.0802 | 32.9786 | 32.9567 | 32.922 | 32.8839 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737
|  | TAPLOW | FS |  |  | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 36.8072 | 33.0836 | 33.0034 | 32.9986 | 32.973 | 32.9393 | 32.899 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 32.8805 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737 | 33.6737
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON | MINIMUM HEADROOM | ST 94510 07307 | YES | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 10.7636 | 10.7618 | 10.7554 | 10.7368 | 10.7119 | 10.6835 | 10.6517 | 10.6169 | 10.5795 | 10.5398 | 10.4501 | 10.2727 | 10.1995 | 10.1545 | 10.7622 | 10.7617 | 10.7601 | 10.7553 | 10.749 | 10.7417 | 10.7336 | 10.7247 | 10.7151 | 10.705 | 10.6821 | 10.6276 | 10.6046 | 10.5904
|  | TARRANT RUSHTON | CT |  |  | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 10.7637 | 10.7618 | 10.7558 | 10.7388 | 10.7167 | 10.692 | 10.6664 | 10.6365 | 10.6014 | 10.5616 | 10.4709 | 10.3755 | 10.3435 | 10.3148 | 10.7622 | 10.7617 | 10.7602 | 10.7558 | 10.7502 | 10.7439 | 10.7373 | 10.7297 | 10.7207 | 10.7106 | 10.6874 | 10.6601 | 10.65 | 10.6409
|  | TARRANT RUSHTON | LW |  |  | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 10.7636 | 10.7618 | 10.7554 | 10.7368 | 10.7119 | 10.6835 | 10.6517 | 10.6169 | 10.5795 | 10.5398 | 10.4501 | 10.2727 | 10.1995 | 10.1545 | 10.7622 | 10.7617 | 10.7601 | 10.7553 | 10.749 | 10.7417 | 10.7336 | 10.7247 | 10.7151 | 10.705 | 10.6821 | 10.6276 | 10.6046 | 10.5904
|  | TARRANT RUSHTON | ST |  |  | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 10.7644 | 10.7635 | 10.7605 | 10.7496 | 10.7347 | 10.7156 | 10.6959 | 10.6734 | 10.6466 | 10.616 | 10.5452 | 10.4556 | 10.4191 | 10.391 | 10.7624 | 10.7621 | 10.7614 | 10.7586 | 10.7548 | 10.7499 | 10.7449 | 10.7391 | 10.7323 | 10.7245 | 10.7064 | 10.6835 | 10.6738 | 10.665
|  | TARRANT RUSHTON | FS |  |  | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 11.031 | 10.7648 | 10.7646 | 10.7637 | 10.7589 | 10.7527 | 10.7445 | 10.7357 | 10.7256 | 10.7145 | 10.7026 | 10.6758 | 10.6116 | 10.5723 | 10.5531 | 10.7625 | 10.7624 | 10.7622 | 10.761 | 10.7594 | 10.7573 | 10.755 | 10.7524 | 10.7496 | 10.7466 | 10.7397 | 10.7233 | 10.7133 | 10.7084
MANNINGTON GSP | SALISBURY | TEFFONT | MINIMUM HEADROOM | ST 99837 30994 | YES | 1.5877 | 1.5841 | 1.5757 | 1.5666 | 1.5571 | 1.5474 | 1.5375 | 1.5246 | 1.5075 | 1.4906 | 1.4571 | 1.3623 | 1.2386 | 1.1159 | -2.6019 | -2.606 | -2.6158 | -2.6264 | -2.6374 | -2.6485 | -2.6599 | -2.6736 | -2.6931 | -2.7123 | -2.7504 | -2.8584 | -2.9992 | -3.1389 | -8.4738 | -8.4781 | -8.4882 | -8.4992 | -8.5105 | -8.522 | -8.5337 | -8.5479 | -8.5679 | -8.5877 | -8.6271 | -8.7384 | -8.8837 | -9.0279
|  | TEFFONT | CT |  |  | 1.5877 | 1.5841 | 1.5757 | 1.5666 | 1.5571 | 1.5474 | 1.5375 | 1.5273 | 1.5161 | 1.5048 | 1.4817 | 1.3623 | 1.2386 | 1.1159 | -2.6019 | -2.606 | -2.6158 | -2.6264 | -2.6374 | -2.6485 | -2.6599 | -2.6713 | -2.6838 | -2.6962 | -2.7217 | -2.8567 | -2.9964 | -3.1344 | -8.4738 | -8.4781 | -8.4882 | -8.4992 | -8.5105 | -8.522 | -8.5337 | -8.5454 | -8.5583 | -8.5712 | -8.5974 | -8.7367 | -8.8808 | -9.0231
|  | TEFFONT | LW |  |  | 1.5877 | 1.5841 | 1.5757 | 1.5666 | 1.5571 | 1.5474 | 1.5375 | 1.5273 | 1.5161 | 1.5048 | 1.4817 | 1.3623 | 1.2386 | 1.1159 | -2.6018 | -2.6058 | -2.6154 | -2.6258 | -2.6366 | -2.6477 | -2.659 | -2.6705 | -2.6832 | -2.6961 | -2.7225 | -2.8584 | -2.9992 | -3.1389 | -8.4738 | -8.4779 | -8.4878 | -8.4985 | -8.5097 | -8.5211 | -8.5327 | -8.5446 | -8.5578 | -8.5711 | -8.5982 | -8.7384 | -8.8837 | -9.0279
|  | TEFFONT | ST |  |  | 1.589 | 1.5874 | 1.584 | 1.5787 | 1.5721 | 1.5562 | 1.5403 | 1.5246 | 1.5075 | 1.4906 | 1.4571 | 1.3726 | 1.2884 | 1.205 | -2.6003 | -2.6021 | -2.606 | -2.612 | -2.6195 | -2.6376 | -2.6557 | -2.6736 | -2.6931 | -2.7123 | -2.7504 | -2.8467 | -2.9425 | -3.0375 | -8.4722 | -8.474 | -8.4781 | -8.4843 | -8.492 | -8.5107 | -8.5294 | -8.5479 | -8.5679 | -8.5877 | -8.6271 | -8.7263 | -8.8252 | -8.9232
|  | TEFFONT | FS |  |  | 1.5898 | 1.5896 | 1.5894 | 1.588 | 1.5862 | 1.5815 | 1.5768 | 1.5707 | 1.5647 | 1.5587 | 1.5469 | 1.5177 | 1.4891 | 1.4614 | -2.5993 | -2.5996 | -2.5998 | -2.6015 | -2.6035 | -2.6088 | -2.6142 | -2.6211 | -2.6279 | -2.6347 | -2.6482 | -2.6815 | -2.714 | -2.7456 | -8.4712 | -8.4714 | -8.4717 | -8.4734 | -8.4755 | -8.481 | -8.4865 | -8.4936 | -8.5007 | -8.5077 | -8.5216 | -8.5559 | -8.5895 | -8.6221
BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM | MINIMUM HEADROOM | SU 84178 83872 | YES | 15.3504 | 15.3487 | 15.3447 | 15.3404 | 15.3361 | 15.3318 | 15.3276 | 15.3234 | 15.3188 | 15.3143 | 15.3023 | 15.2545 | 15.2018 | 15.1498 | 15.2059 | 15.1981 | 15.1794 | 15.1592 | 15.1392 | 15.1194 | 15.0998 | 15.0804 | 15.0595 | 15.0387 | 14.9978 | 14.896 | 14.79 | 14.6854 | 15.0248 | 15.0161 | 14.9953 | 14.9727 | 14.9504 | 14.9283 | 14.9064 | 14.8847 | 14.8614 | 14.8382 | 14.7925 | 14.6788 | 14.5605 | 14.4438
|  | TEMPLE FARM | CT |  |  | 15.3504 | 15.3487 | 15.3447 | 15.3404 | 15.3361 | 15.3318 | 15.3276 | 15.3234 | 15.3188 | 15.3143 | 15.3054 | 15.2545 | 15.2018 | 15.1498 | 15.2059 | 15.1981 | 15.1794 | 15.1592 | 15.1392 | 15.1194 | 15.0998 | 15.0804 | 15.0595 | 15.0387 | 14.9978 | 14.896 | 14.79 | 14.6854 | 15.0248 | 15.0161 | 14.9953 | 14.9727 | 14.9504 | 14.9283 | 14.9064 | 14.8847 | 14.8614 | 14.8382 | 14.7925 | 14.6788 | 14.5605 | 14.4438
|  | TEMPLE FARM | LW |  |  | 15.3504 | 15.3487 | 15.3447 | 15.3404 | 15.3361 | 15.3318 | 15.3276 | 15.3234 | 15.3188 | 15.3143 | 15.3054 | 15.2545 | 15.2018 | 15.1498 | 15.209 | 15.2059 | 15.1984 | 15.1902 | 15.1821 | 15.1741 | 15.1661 | 15.1582 | 15.1496 | 15.1411 | 15.1243 | 15.0284 | 14.9291 | 14.8313 | 15.0283 | 15.0248 | 15.0164 | 15.0073 | 14.9982 | 14.9893 | 14.9803 | 14.9715 | 14.9619 | 14.9525 | 14.9337 | 14.8267 | 14.7158 | 14.6066
|  | TEMPLE FARM | ST |  |  | 15.3512 | 15.3508 | 15.3497 | 15.3481 | 15.3462 | 15.34 | 15.3338 | 15.3278 | 15.3212 | 15.3148 | 15.3023 | 15.2714 | 15.2401 | 15.2091 | 15.2106 | 15.2097 | 15.2077 | 15.2048 | 15.2012 | 15.1894 | 15.1778 | 15.1664 | 15.1541 | 15.142 | 15.1184 | 15.0602 | 15.0014 | 14.9428 | 15.03 | 15.029 | 15.0268 | 15.0235 | 15.0195 | 15.0064 | 14.9935 | 14.9807 | 14.967 | 14.9534 | 14.9271 | 14.8621 | 14.7965 | 14.7311
|  | TEMPLE FARM | FS |  |  | 15.3515 | 15.3514 | 15.3513 | 15.3509 | 15.3504 | 15.3483 | 15.3461 | 15.3434 | 15.3407 | 15.3381 | 15.3329 | 15.3206 | 15.3086 | 15.2973 | 15.211 | 15.2109 | 15.2108 | 15.21 | 15.209 | 15.205 | 15.201 | 15.1958 | 15.1908 | 15.1858 | 15.1761 | 15.1528 | 15.1303 | 15.109 | 15.0305 | 15.0304 | 15.0303 | 15.0293 | 15.0283 | 15.0238 | 15.0193 | 15.0135 | 15.0079 | 15.0023 | 14.9915 | 14.9655 | 14.9404 | 14.9166
MELKSHAM GSP | CHIPPENHAM | TETBURY | MINIMUM HEADROOM | ST 89708 93444 | YES | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.2294 | 14.2014 | 14.1358 | 14.0643 | 13.9865 | 13.9064 | 13.8237 | 13.7448 | 13.6632 | 13.5802 | 13.4197 | 13.1253 | 13.1253 | 13.1253 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824
|  | TETBURY | CT |  |  | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.2294 | 14.2014 | 14.1358 | 14.0643 | 13.9865 | 13.9064 | 13.8237 | 13.7448 | 13.6632 | 13.5802 | 13.4197 | 13.1253 | 13.1253 | 13.1253 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824
|  | TETBURY | LW |  |  | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.2326 | 14.2098 | 14.1567 | 14.0986 | 14.0331 | 13.9646 | 13.8936 | 13.8244 | 13.7521 | 13.6758 | 13.5275 | 13.1253 | 13.1253 | 13.1253 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824
|  | TETBURY | ST |  |  | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.2426 | 14.2334 | 14.2142 | 14.185 | 14.1452 | 14.1003 | 14.0539 | 14.01 | 13.9648 | 13.9188 | 13.8305 | 13.5402 | 13.2364 | 13.1253 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824
|  | TETBURY | FS |  |  | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.1314 | 14.2473 | 14.2458 | 14.2442 | 14.2347 | 14.2218 | 14.2083 | 14.1947 | 14.1784 | 14.1628 | 14.1466 | 14.1157 | 14.0154 | 13.9009 | 13.7798 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824 | 12.0824
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM | MINIMUM HEADROOM | SU 52758 66466 | NO | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 27.7977 | 37.505 | 37.3807 | 37.1051 | 36.9672 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 26.5558 | 24.3145 | 21.9717 | 19.6401 | 39.8364 | 39.7565 | 39.5662 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 25.1202 | 22.7765 | 20.4442
|  | THATCHAM | CT |  |  | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 27.7977 | 37.5182 | 37.4133 | 37.1633 | 37.0227 | 36.9074 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 25.7667 | 23.4076 | 21.0595 | 39.8448 | 39.7775 | 39.6169 | 39.4464 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 26.565 | 24.213 | 21.8641
|  | THATCHAM | LW |  |  | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 27.7977 | 37.505 | 37.3807 | 37.1051 | 36.9672 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 26.5558 | 24.3145 | 21.9717 | 19.6401 | 39.8364 | 39.7565 | 39.5662 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 25.1202 | 22.7765 | 20.4442
|  | THATCHAM | ST |  |  | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 37.6104 | 37.4697 | 37.3093 | 37.0979 | 36.9725 | 36.9292 | 36.8864 | 36.8445 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 39.8898 | 39.8137 | 39.7107 | 39.5554 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145 | 39.4145
|  | THATCHAM | FS |  |  | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 45.2019 | 37.6633 | 37.5935 | 37.5818 | 37.5142 | 37.4516 | 37.4176 | 37.384 | 37.341 | 37.2987 | 37.2572 | 37.1765 | 37.0573 | 36.97 | 36.885 | 39.9155 | 39.8816 | 39.876 | 39.8422 | 39.802 | 39.7802 | 39.7587 | 39.731 | 39.7039 | 39.6772 | 39.6254 | 39.4948 | 39.4145 | 39.4145
NORTH HYDE GSP | NORTH HYDE (D) | THE GREEN | MINIMUM HEADROOM | TQ 12414 79503 | NO | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 18.7765 | 18.7425 | 18.6957 | 18.6421 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142
|  | THE GREEN | CT |  |  | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 18.7784 | 18.7469 | 18.7034 | 18.6546 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142
|  | THE GREEN | LW |  |  | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 18.7765 | 18.7425 | 18.6957 | 18.6421 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142
|  | THE GREEN | ST |  |  | 19.9207 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 18.8 | 18.7715 | 18.7467 | 18.7166 | 18.68 | 18.6354 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142 | 18.6142
|  | THE GREEN | FS |  |  | 19.9253 | 19.9215 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 19.9178 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 17.488 | 18.8189 | 18.8035 | 18.7878 | 18.7667 | 18.7523 | 18.7349 | 18.7214 | 18.7097 | 18.6979 | 18.686 | 18.6627 | 18.6142 | 18.6142 | 18.6142
BRAMLEY (FLEE) | READING TOWN BSP | THE MALL | MINIMUM HEADROOM | SU 71319 73293 | YES | 30.8056 | 30.7951 | 30.7726 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 26.1995 | 25.489 | 24.7911 | 30.0419 | 30.0236 | 30.0096 | 29.9941 | 29.9784 | 29.9626 | 29.9465 | 29.9303 | 29.9128 | 29.8951 | 26.4917 | 25.6335 | 24.7257 | 23.8405 | 32.3351 | 32.2784 | 32.1566 | 32.0219 | 31.9082 | 31.8012 | 31.693 | 31.5835 | 31.4654 | 31.3465 | 31.1078 | 31.1078 | 31.1078 | 26.1487
|  | THE MALL | CT |  |  | 30.8056 | 30.7951 | 30.7726 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 26.1995 | 25.489 | 24.7911 | 30.0425 | 30.0241 | 30.0106 | 29.9957 | 29.9807 | 29.9654 | 29.95 | 29.9343 | 29.9171 | 29.8997 | 29.8884 | 25.634 | 24.7257 | 23.8405 | 32.3364 | 32.2825 | 32.1651 | 32.036 | 31.9234 | 31.8202 | 31.7164 | 31.6103 | 31.4948 | 31.3774 | 31.1381 | 31.1078 | 31.1078 | 26.1487
|  | THE MALL | LW |  |  | 30.8056 | 30.7951 | 30.7726 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 26.1995 | 25.489 | 24.7911 | 30.0419 | 30.0236 | 30.0096 | 29.9941 | 29.9784 | 29.9626 | 29.9465 | 29.9303 | 29.9128 | 29.8951 | 26.4917 | 25.6335 | 24.7953 | 23.972 | 32.3351 | 32.2784 | 32.1566 | 32.0219 | 31.9082 | 31.8012 | 31.693 | 31.5835 | 31.4654 | 31.3465 | 31.1078 | 31.1078 | 31.1078 | 26.2803
|  | THE MALL | ST |  |  | 30.8225 | 30.8082 | 30.8035 | 30.7968 | 30.7887 | 30.7792 | 30.7696 | 30.7595 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.7484 | 30.2031 | 30.0535 | 30.0378 | 30.0247 | 30.0196 | 30.0137 | 30.0077 | 30.0014 | 29.9945 | 29.9873 | 29.9722 | 29.9459 | 29.9227 | 29.9 | 32.4894 | 32.3494 | 32.324 | 32.2876 | 32.2437 | 32.1923 | 32.1401 | 32.0858 | 32.0255 | 31.9681 | 31.866 | 31.6891 | 31.5323 | 31.3793
|  | THE MALL | FS |  |  | 30.8236 | 30.8108 | 30.8094 | 30.8051 | 30.8001 | 30.7963 | 30.7924 | 30.7877 | 30.7829 | 30.778 | 30.7678 | 30.7491 | 30.7484 | 30.7484 | 30.2155 | 30.0728 | 30.0591 | 30.041 | 30.0311 | 30.0243 | 30.0219 | 30.019 | 30.016 | 30.0129 | 30.0066 | 29.995 | 29.9849 | 29.9757 | 32.5011 | 32.3658 | 32.356 | 32.3327 | 32.3055 | 32.285 | 32.264 | 32.2385 | 32.2123 | 32.1856 | 32.1304 | 32.0294 | 31.9519 | 31.8895
BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE | MINIMUM HEADROOM | SU 64755 71015 | NO | 22.6508 | 22.6179 | 22.5713 | 22.5407 | 22.4824 | 22.3901 | 22.2883 | 22.2142 | 22.1346 | 22.0524 | 21.9663 | 21.6518 | 21.336 | 21.0224 | 28.822 | 28.8029 | 28.776 | 28.7583 | 28.7245 | 28.6711 | 28.6122 | 28.5692 | 28.5232 | 28.4756 | 28.4257 | 28.2509 | 28.1535 | 28.058 | 30.5595 | 30.5535 | 30.545 | 30.5394 | 30.5287 | 30.5119 | 30.4933 | 30.4798 | 30.4653 | 30.4503 | 30.4346 | 30.3741 | 30.3158 | 30.2587
|  | THEALE | CT |  |  | 22.6508 | 22.6179 | 22.5713 | 22.5407 | 22.4824 | 22.3901 | 22.2883 | 22.2142 | 22.1346 | 22.0524 | 21.9663 | 21.6518 | 21.336 | 21.0224 | 28.8225 | 28.8054 | 28.78 | 28.7631 | 28.7311 | 28.6806 | 28.6274 | 28.5875 | 28.5445 | 28.4945 | 28.4322 | 28.2509 | 28.1535 | 28.058 | 30.5596 | 30.5542 | 30.5462 | 30.5409 | 30.5308 | 30.5149 | 30.4981 | 30.4856 | 30.472 | 30.4563 | 30.4366 | 30.3741 | 30.3158 | 30.2587
|  | THEALE | LW |  |  | 22.6508 | 22.6179 | 22.5713 | 22.5407 | 22.4824 | 22.3901 | 22.2883 | 22.2142 | 22.1346 | 22.0524 | 21.9663 | 21.6518 | 21.336 | 21.0224 | 28.822 | 28.8029 | 28.776 | 28.7583 | 28.7245 | 28.6711 | 28.6122 | 28.5692 | 28.5232 | 28.4756 | 28.4257 | 28.2561 | 28.1598 | 28.0641 | 30.5595 | 30.5535 | 30.545 | 30.5394 | 30.5287 | 30.5119 | 30.4933 | 30.4798 | 30.4653 | 30.4503 | 30.4346 | 30.3772 | 30.3195 | 30.2623
|  | THEALE | ST |  |  | 22.6606 | 22.6428 | 22.6205 | 22.6039 | 22.5664 | 22.49 | 22.4108 | 22.3474 | 22.2781 | 22.2 | 22.0901 | 21.8649 | 21.6646 | 21.4676 | 28.8277 | 28.8174 | 28.8045 | 28.7949 | 28.7732 | 28.7289 | 28.683 | 28.6463 | 28.6062 | 28.561 | 28.4974 | 28.367 | 28.26 | 28.1999 | 30.5613 | 30.558 | 30.554 | 30.5509 | 30.5441 | 30.5301 | 30.5157 | 30.5041 | 30.4915 | 30.4772 | 30.4572 | 30.4161 | 30.3795 | 30.3436
|  | THEALE | FS |  |  | 22.668 | 22.6592 | 22.6517 | 22.6462 | 22.6323 | 22.6034 | 22.5735 | 22.5466 | 22.5179 | 22.4877 | 22.4462 | 22.3568 | 22.2827 | 22.2127 | 28.8319 | 28.8269 | 28.8225 | 28.8193 | 28.8113 | 28.7945 | 28.7772 | 28.7617 | 28.7451 | 28.7276 | 28.7035 | 28.6518 | 28.6089 | 28.5684 | 30.5626 | 30.561 | 30.5596 | 30.5586 | 30.5561 | 30.5508 | 30.5454 | 30.5405 | 30.5352 | 30.5297 | 30.5221 | 30.5058 | 30.4923 | 30.4795
BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON | MINIMUM HEADROOM | SU 29134 45674 | YES | 4.8646 | 4.8643 | 4.864 | 4.7246 | 4.6697 | 4.6149 | 4.5598 | 4.5048 | 4.4451 | 4.3858 | 4.2667 | 4.0198 | 3.7537 | 3.4762 | 7.4594 | 7.4554 | 7.4458 | 7.4352 | 7.4246 | 7.4139 | 7.4031 | 7.3922 | 7.3802 | 7.3682 | 7.3517 | 7.3245 | 7.2976 | 7.2644 | 4.8835 | 4.8826 | 4.8814 | 4.7047 | 4.6419 | 4.5794 | 4.5165 | 4.4538 | 4.3858 | 4.3181 | 4.1826 | 3.8973 | 3.5899 | 3.2713
|  | THRUXTON | CT |  |  | 4.8646 | 4.8643 | 4.864 | 4.7246 | 4.6697 | 4.6149 | 4.5598 | 4.5048 | 4.4451 | 4.3858 | 4.2667 | 4.0198 | 3.7537 | 3.4762 | 7.4594 | 7.4555 | 7.4468 | 7.4372 | 7.4275 | 7.4177 | 7.4078 | 7.3979 | 7.3866 | 7.3752 | 7.3517 | 7.3245 | 7.2976 | 7.2644 | 4.8835 | 4.8826 | 4.8814 | 4.7278 | 4.6744 | 4.6211 | 4.5674 | 4.5139 | 4.4555 | 4.3974 | 4.2803 | 3.9753 | 3.6392 | 3.2943
|  | THRUXTON | LW |  |  | 4.8646 | 4.8643 | 4.864 | 4.7246 | 4.6697 | 4.6149 | 4.5598 | 4.5048 | 4.4451 | 4.3858 | 4.2667 | 4.0198 | 3.7537 | 3.4762 | 7.4595 | 7.4554 | 7.4458 | 7.4352 | 7.4246 | 7.4139 | 7.4031 | 7.3922 | 7.3802 | 7.3682 | 7.3519 | 7.3424 | 7.3264 | 7.303 | 4.8842 | 4.884 | 4.8836 | 4.7047 | 4.6419 | 4.5794 | 4.5165 | 4.4538 | 4.3858 | 4.3181 | 4.1826 | 3.8973 | 3.5899 | 3.2713
|  | THRUXTON | ST |  |  | 4.8649 | 4.8648 | 4.8647 | 4.8645 | 4.8643 | 4.7453 | 4.7171 | 4.6892 | 4.6593 | 4.6298 | 4.5715 | 4.4229 | 4.272 | 4.1188 | 7.4614 | 7.4598 | 7.4563 | 7.4511 | 7.4448 | 7.4394 | 7.434 | 7.4286 | 7.4228 | 7.417 | 7.4056 | 7.3759 | 7.3517 | 7.3463 | 4.8845 | 4.8844 | 4.8843 | 4.8841 | 4.884 | 4.7282 | 4.696 | 4.6642 | 4.63 | 4.5964 | 4.5298 | 4.3604 | 4.1887 | 4.0125
|  | THRUXTON | FS |  |  | 4.8649 | 4.8649 | 4.8648 | 4.8647 | 4.8646 | 4.8645 | 4.8643 | 4.8642 | 4.8641 | 4.8639 | 4.8636 | 4.7051 | 4.6484 | 4.5934 | 7.4622 | 7.4619 | 7.4616 | 7.4598 | 7.4577 | 7.4558 | 7.4539 | 7.4516 | 7.4493 | 7.447 | 7.4425 | 7.431 | 7.4195 | 7.4081 | 4.8845 | 4.8845 | 4.8844 | 4.8843 | 4.8842 | 4.8841 | 4.884 | 4.8839 | 4.8837 | 4.8836 | 4.7483 | 4.6825 | 4.618 | 4.5554
MELKSHAM GSP | WEST GRAFTON | TIDWORTH | MINIMUM HEADROOM | SU 24088 49593 | YES | 13.2031 | 13.1559 | 13.0999 | 13.0153 | 12.9444 | 12.8845 | 12.8181 | 12.745 | 12.6619 | 12.5967 | 12.4799 | 11.9186 | 11.3183 | 10.6981 | 16.1108 | 16.0559 | 15.9977 | 15.9823 | 15.9772 | 15.9725 | 15.9671 | 15.961 | 15.9537 | 15.9476 | 15.9359 | 15.9126 | 15.889 | 15.8597 | 14.7757 | 14.7315 | 14.7298 | 14.7277 | 14.7255 | 14.7232 | 14.7206 | 14.7179 | 14.714 | 14.7096 | 14.6994 | 14.6641 | 12.0849 | 11.4221
|  | TIDWORTH | CT |  |  | 13.2031 | 13.1559 | 13.0999 | 13.0153 | 12.9444 | 12.8845 | 12.8181 | 12.745 | 12.6619 | 12.5967 | 12.4806 | 11.9186 | 11.3183 | 10.6981 | 16.1114 | 16.0631 | 16.0079 | 15.9823 | 15.9772 | 15.9725 | 15.9671 | 15.961 | 15.9537 | 15.9476 | 15.9359 | 15.9126 | 15.889 | 15.8597 | 14.7759 | 14.7315 | 14.7298 | 14.7277 | 14.7255 | 14.7232 | 14.7206 | 14.7179 | 14.714 | 14.7096 | 14.6994 | 14.6641 | 12.3504 | 11.8298
|  | TIDWORTH | LW |  |  | 13.2031 | 13.1559 | 13.0999 | 13.0153 | 12.9444 | 12.8845 | 12.8181 | 12.745 | 12.6619 | 12.5967 | 12.4806 | 11.9186 | 11.3183 | 10.6981 | 16.1108 | 16.0559 | 15.9977 | 15.9827 | 15.9778 | 15.9735 | 15.9687 | 15.9634 | 15.9572 | 15.9521 | 15.9425 | 15.9284 | 15.9143 | 15.8937 | 14.7757 | 14.7333 | 14.7328 | 14.7322 | 14.7315 | 14.7305 | 14.7294 | 14.7281 | 14.7262 | 14.724 | 14.7187 | 14.6998 | 12.0849 | 11.4221
|  | TIDWORTH | ST |  |  | 13.2126 | 13.1859 | 13.1568 | 13.1084 | 13.0652 | 12.989 | 12.9065 | 12.8191 | 12.7202 | 12.6349 | 12.4799 | 12.0855 | 11.7008 | 11.3194 | 16.1218 | 16.0906 | 16.0566 | 16.0057 | 15.9864 | 15.9813 | 15.9757 | 15.9698 | 15.9631 | 15.9573 | 15.9466 | 15.9398 | 15.9365 | 15.9317 | 14.7865 | 14.756 | 14.7337 | 14.7335 | 14.7333 | 14.733 | 14.7326 | 14.7322 | 14.7318 | 14.7313 | 14.7303 | 14.7258 | 14.7183 | 12.0804
|  | TIDWORTH | FS |  |  | 13.2198 | 13.2053 | 13.1926 | 13.1703 | 13.1527 | 13.1262 | 13.0987 | 13.0655 | 13.0309 | 13.0006 | 12.9433 | 12.8039 | 12.6654 | 12.5224 | 16.1302 | 16.1132 | 16.0985 | 16.0724 | 16.0519 | 16.0232 | 15.9963 | 15.9864 | 15.984 | 15.982 | 15.978 | 15.9683 | 15.9583 | 15.9479 | 14.7948 | 14.7782 | 14.7637 | 14.7382 | 14.7336 | 14.7334 | 14.7333 | 14.7331 | 14.7329 | 14.7328 | 14.7323 | 14.7308 | 14.7286 | 14.7261
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY | MINIMUM HEADROOM | ST 93438 29127 | YES | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.5875 | 7.5532 | 7.5193 | 7.4514 | 7.2775 | 7.0071 | 6.7311 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 7.5833 | 7.543 | 7.503 | 7.4231 | 7.2186 | 6.9004 | 6.5756 | 7.5968 | 7.5921 | 7.581 | 7.5688 | 7.5554 | 7.5413 | 7.5076 | 7.4736 | 7.4366 | 7.3999 | 7.3267 | 7.1391 | 6.8472 | 6.5493
|  | TISBURY | CT |  |  | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.5883 | 7.5527 | 7.285 | 7.0071 | 6.7311 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 7.5903 | 7.5525 | 7.2511 | 6.9389 | 6.63 | 7.5969 | 7.5922 | 7.581 | 7.5689 | 7.5557 | 7.542 | 7.5275 | 7.5128 | 7.4965 | 7.48 | 7.4453 | 7.1688 | 6.8826 | 6.5992
|  | TISBURY | LW |  |  | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.5883 | 7.5527 | 7.285 | 7.0071 | 6.7311 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 7.5843 | 7.5423 | 7.2274 | 6.9004 | 6.5756 | 7.5968 | 7.5921 | 7.581 | 7.5688 | 7.5554 | 7.5413 | 7.5263 | 7.5106 | 7.4928 | 7.4745 | 7.436 | 7.1471 | 6.8472 | 6.5493
|  | TISBURY | ST |  |  | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.5875 | 7.5532 | 7.5193 | 7.4514 | 7.2775 | 7.1044 | 6.9329 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 7.5833 | 7.543 | 7.503 | 7.4231 | 7.2186 | 7.0149 | 6.8131 | 7.5987 | 7.5966 | 7.592 | 7.5851 | 7.5761 | 7.5419 | 7.5076 | 7.4736 | 7.4366 | 7.3999 | 7.3267 | 7.1391 | 6.9522 | 6.7672
|  | TISBURY | FS |  |  | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.936 | 7.5479 | 7.4834 | 7.4202 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 7.5367 | 7.4608 | 7.3865 | 7.5998 | 7.5995 | 7.5991 | 7.5972 | 7.5948 | 7.5836 | 7.5725 | 7.5581 | 7.5438 | 7.5296 | 7.5013 | 7.4308 | 7.3612 | 7.293
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD | MINIMUM HEADROOM | SU 54104 05695 | NO | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 37.7376 | 37.6128 | 37.424 | 37.2079 | 37.0034 | 36.7999 | 36.6461 | 36.5216 | 36.3874 | 36.2464 | 35.9361 | 35.429 | 35.0408 | 34.6571 | 31.6634 | 31.6419 | 31.6094 | 31.5723 | 31.5317 | 31.4874 | 31.4393 | 31.3875 | 31.3316 | 31.2728 | 31.1435 | 30.9322 | 30.7704 | 30.6105
|  | TITCHFIELD | CT |  |  | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 37.7438 | 37.6365 | 37.4704 | 37.2836 | 37.0859 | 36.9015 | 36.7103 | 36.5941 | 36.465 | 36.3252 | 36.0186 | 35.4405 | 35.0408 | 34.6571 | 31.6645 | 31.646 | 31.6174 | 31.5853 | 31.5496 | 31.5095 | 31.4661 | 31.4177 | 31.3639 | 31.3056 | 31.1779 | 30.937 | 30.7704 | 30.6105
|  | TITCHFIELD | LW |  |  | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 37.7376 | 37.6128 | 37.424 | 37.2079 | 37.0034 | 36.7999 | 36.6461 | 36.5216 | 36.3874 | 36.2464 | 35.9361 | 35.429 | 35.0431 | 34.6592 | 31.6634 | 31.6419 | 31.6094 | 31.5723 | 31.5317 | 31.4874 | 31.4393 | 31.3875 | 31.3316 | 31.2728 | 31.1435 | 30.9322 | 30.7714 | 30.6114
|  | TITCHFIELD | ST |  |  | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 37.8404 | 37.7189 | 37.6335 | 37.5258 | 37.3963 | 37.1942 | 37.01 | 36.8263 | 36.6673 | 36.5507 | 36.2942 | 35.9105 | 35.6697 | 35.4394 | 31.6811 | 31.6602 | 31.6455 | 31.627 | 31.6047 | 31.5699 | 31.5331 | 31.4931 | 31.4482 | 31.3996 | 31.2927 | 31.1328 | 31.0325 | 30.9365
|  | TITCHFIELD | FS |  |  | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 30.7363 | 37.8711 | 37.7781 | 37.7403 | 37.6875 | 37.6292 | 37.5482 | 37.4636 | 37.3651 | 37.2604 | 37.1499 | 36.9552 | 36.6852 | 36.5807 | 36.493 | 31.6864 | 31.6704 | 31.6639 | 31.6548 | 31.6448 | 31.6308 | 31.6163 | 31.5993 | 31.5813 | 31.5623 | 31.5212 | 31.4556 | 31.4121 | 31.3756
BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM | MINIMUM HEADROOM | SU 88310 49487 | YES | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 26.1479 | 25.2667 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 26.4076 | 25.5394
|  | TONGHAM | CT |  |  | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 26.3438 | 25.5317 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 26.6006 | 25.8005
|  | TONGHAM | LW |  |  | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 26.1479 | 25.2667 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 26.4076 | 25.5394
|  | TONGHAM | ST |  |  | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 26.5527 | 25.9686 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 26.231
|  | TONGHAM | FS |  |  | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 35.5841 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.3049 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958 | 31.4958
MINETY GSP | TOOTHILL BSP | TOOTHILL | MINIMUM HEADROOM | SU 13215 83986 | YES | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 57.2615 | 57.2482 | 57.2294 | 57.2077 | 57.1836 | 57.1569 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 52.9124 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 53.312
|  | TOOTHILL | CT |  |  | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 57.262 | 57.2504 | 57.2335 | 57.2143 | 57.1927 | 57.168 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 53.209 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639
|  | TOOTHILL | LW |  |  | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 57.2615 | 57.2482 | 57.2294 | 57.2077 | 57.1836 | 57.1569 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 52.9124 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 53.312
|  | TOOTHILL | ST |  |  | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 57.4484 | 57.2589 | 57.2496 | 57.2381 | 57.2242 | 57.1933 | 57.161 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 57.1436 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639
|  | TOOTHILL | FS |  |  | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 64.3707 | 57.4519 | 57.2654 | 57.261 | 57.2553 | 57.2491 | 57.2379 | 57.2263 | 57.2126 | 57.2022 | 57.1931 | 57.1754 | 57.1436 | 57.1436 | 57.1436 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639 | 58.3639
NURSLING GSP | ROWNHAMS | TOTTON | MINIMUM HEADROOM | SU 35835 13428 | NO | 37.4933 | 37.475 | 37.4301 | 37.3807 | 37.324 | 37.2577 | 37.2341 | 37.2182 | 37.2008 | 37.18 | 37.1304 | 36.9621 | 36.8254 | 36.7047 | 34.1639 | 34.143 | 34.0916 | 34.0351 | 33.9701 | 33.8942 | 33.8122 | 33.7224 | 33.6245 | 33.5071 | 33.2279 | 32.7435 | 32.4667 | 32.4238 | 36.7716 | 36.7462 | 36.6839 | 36.6154 | 36.5367 | 36.4447 | 36.4086 | 36.3704 | 36.3288 | 36.2788 | 36.1601 | 36.0606 | 36.0606 | 36.0606
|  | TOTTON | CT |  |  | 37.4933 | 37.475 | 37.4301 | 37.3807 | 37.3311 | 37.2813 | 37.241 | 37.2259 | 37.2094 | 37.187 | 37.1318 | 36.9621 | 36.8254 | 36.7047 | 34.1659 | 34.1474 | 34.1019 | 34.0518 | 34.0014 | 33.9507 | 33.8898 | 33.816 | 33.7358 | 33.6271 | 33.3488 | 32.942 | 32.672 | 32.4686 | 36.7739 | 36.7515 | 36.6964 | 36.6356 | 36.5746 | 36.5132 | 36.4416 | 36.4102 | 36.3761 | 36.3299 | 36.2115 | 36.0606 | 36.0606 | 36.0606
|  | TOTTON | LW |  |  | 37.4933 | 37.475 | 37.4301 | 37.3807 | 37.3311 | 37.2813 | 37.241 | 37.2259 | 37.2094 | 37.187 | 37.1318 | 36.9621 | 36.8254 | 36.7047 | 34.1639 | 34.143 | 34.0916 | 34.0351 | 33.9782 | 33.9211 | 33.8513 | 33.7658 | 33.6732 | 33.5468 | 33.2355 | 32.7435 | 32.4667 | 32.4238 | 36.7716 | 36.7462 | 36.6839 | 36.6154 | 36.5465 | 36.4774 | 36.4252 | 36.3888 | 36.3494 | 36.2957 | 36.1633 | 36.0606 | 36.0606 | 36.0606
|  | TOTTON | ST |  |  | 37.7986 | 37.4798 | 37.4441 | 37.3898 | 37.324 | 37.2577 | 37.2341 | 37.2182 | 37.2008 | 37.18 | 37.1304 | 37.0351 | 36.9511 | 36.8675 | 34.5744 | 34.1486 | 34.1076 | 34.0455 | 33.9701 | 33.8942 | 33.8122 | 33.7224 | 33.6245 | 33.5071 | 33.2279 | 32.9344 | 32.7148 | 32.4962 | 37.1953 | 36.7529 | 36.7033 | 36.628 | 36.5367 | 36.4447 | 36.4086 | 36.3704 | 36.3288 | 36.2788 | 36.1601 | 36.0606 | 36.0606 | 36.0606
|  | TOTTON | FS |  |  | 37.808 | 37.5043 | 37.5031 | 37.4954 | 37.486 | 37.4676 | 37.4467 | 37.4175 | 37.388 | 37.3515 | 37.267 | 37.2077 | 37.17 | 37.1393 | 34.5872 | 34.1766 | 34.1752 | 34.1664 | 34.1557 | 34.1346 | 34.1106 | 34.0772 | 34.0434 | 34.0016 | 33.9048 | 33.6633 | 33.4506 | 33.278 | 37.2083 | 36.7869 | 36.7852 | 36.7745 | 36.7615 | 36.736 | 36.7069 | 36.6665 | 36.6255 | 36.5749 | 36.4576 | 36.3453 | 36.2548 | 36.1814
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK | MINIMUM HEADROOM | SU 45156 14783 | NO | 42.5946 | 42.5512 | 42.5504 | 42.5493 | 42.548 | 42.5464 | 42.5444 | 42.5421 | 42.5388 | 42.535 | 42.5258 | 42.493 | 42.4372 | 42.3562 | 37.5254 | 37.155 | 37.0873 | 37.0192 | 36.9567 | 36.9006 | 36.8374 | 36.7658 | 36.7273 | 36.7251 | 36.7003 | 36.6648 | 36.6107 | 36.544 | 36.6484 | 36.6465 | 36.6436 | 36.6401 | 36.6364 | 36.6324 | 36.628 | 36.6234 | 36.6167 | 36.6092 | 36.5919 | 36.5318 | 36.4404 | 36.3275
|  | TOWNHILL PARK | CT |  |  | 42.5946 | 42.5512 | 42.5504 | 42.5493 | 42.548 | 42.5464 | 42.5444 | 42.5421 | 42.5388 | 42.535 | 42.5258 | 42.493 | 42.4372 | 42.3562 | 37.5307 | 37.1708 | 37.1253 | 37.0809 | 37.0403 | 37.0033 | 36.9602 | 36.9099 | 36.8558 | 36.8015 | 36.7003 | 36.6648 | 36.6107 | 36.544 | 36.6484 | 36.6465 | 36.6436 | 36.6401 | 36.6364 | 36.6324 | 36.628 | 36.6234 | 36.6167 | 36.6092 | 36.5919 | 36.5318 | 36.4404 | 36.3275
|  | TOWNHILL PARK | LW |  |  | 42.5946 | 42.5512 | 42.5504 | 42.5493 | 42.548 | 42.5464 | 42.5444 | 42.5421 | 42.5388 | 42.535 | 42.5258 | 42.493 | 42.4372 | 42.3562 | 37.5254 | 37.155 | 37.0873 | 37.0192 | 36.9567 | 36.9006 | 36.8374 | 36.7658 | 36.7273 | 36.7251 | 36.7198 | 36.7008 | 36.6685 | 36.6216 | 36.6502 | 36.6496 | 36.6488 | 36.6478 | 36.6465 | 36.6449 | 36.643 | 36.6408 | 36.6375 | 36.6338 | 36.6248 | 36.5927 | 36.5381 | 36.4588
|  | TOWNHILL PARK | ST |  |  | 42.5971 | 42.5942 | 42.5897 | 42.5841 | 42.5779 | 42.5633 | 42.55 | 42.5493 | 42.5486 | 42.5477 | 42.5459 | 42.5381 | 42.5252 | 42.5062 | 37.5397 | 37.5198 | 37.4877 | 37.4479 | 37.4043 | 37.2994 | 37.1919 | 37.081 | 36.9622 | 36.8449 | 36.7314 | 36.7269 | 36.7194 | 36.7085 | 36.6508 | 36.6506 | 36.6503 | 36.65 | 36.6496 | 36.6491 | 36.6485 | 36.6478 | 36.647 | 36.6462 | 36.6444 | 36.6368 | 36.6242 | 36.6056
|  | TOWNHILL PARK | FS |  |  | 42.5986 | 42.5974 | 42.5961 | 42.5941 | 42.592 | 42.5877 | 42.5833 | 42.5776 | 42.5719 | 42.5662 | 42.555 | 42.5469 | 42.5431 | 42.5387 | 37.5502 | 37.5421 | 37.5338 | 37.5201 | 37.5066 | 37.4758 | 37.4448 | 37.4042 | 37.3638 | 37.3236 | 37.2444 | 37.0265 | 36.795 | 36.7273 | 36.6509 | 36.6507 | 36.6506 | 36.6504 | 36.6501 | 36.6499 | 36.6496 | 36.6493 | 36.649 | 36.6487 | 36.648 | 36.6454 | 36.6417 | 36.6374
MINETY GSP | SWINDON BSP | TRADING ESTATE | MINIMUM HEADROOM | SU 13490 85868 | YES | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 21.4901 | 21.1174 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 21.4223 | 21.1058 | 20.7831
|  | TRADING ESTATE | CT |  |  | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 21.2764 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 21.477 | 21.2018 | 20.9247
|  | TRADING ESTATE | LW |  |  | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 21.4901 | 21.1174 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 21.4223 | 21.1058 | 20.7831
|  | TRADING ESTATE | ST |  |  | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 24.8076 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 21.4308 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 21.5232 | 21.2886 | 21.0555
|  | TRADING ESTATE | FS |  |  | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 26.6772 | 24.8085 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 24.6884 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912 | 25.6912
BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN | MINIMUM HEADROOM | SU 66254 68745 | YES | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 21.33 | 21.2819 | 21.1852 | 21.0785 | 20.9682 | 20.8665 | 20.7937 | 20.7717 | 20.7479 | 20.7242 | 20.6797 | 20.6208 | 20.5581 | 20.4989 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222
|  | TRASH GREEN | CT |  |  | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 21.33 | 21.2831 | 21.1863 | 21.0803 | 20.9708 | 20.8679 | 20.7937 | 20.7717 | 20.7479 | 20.7242 | 20.6797 | 20.6208 | 20.5581 | 20.4989 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222
|  | TRASH GREEN | LW |  |  | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 21.33 | 21.2819 | 21.1852 | 21.0785 | 20.9682 | 20.8665 | 20.7946 | 20.7744 | 20.7526 | 20.731 | 20.6883 | 20.6278 | 20.5644 | 20.5022 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222
|  | TRASH GREEN | ST |  |  | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 21.3491 | 21.3272 | 21.2886 | 21.2337 | 21.167 | 21.1284 | 21.0975 | 21.0662 | 21.0316 | 20.9975 | 20.9364 | 20.7963 | 20.7594 | 20.7227 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222
|  | TRASH GREEN | FS |  |  | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 22.93 | 21.3599 | 21.3523 | 21.344 | 21.3232 | 21.299 | 21.2839 | 21.2725 | 21.2582 | 21.2441 | 21.2305 | 21.2044 | 21.1429 | 21.0824 | 21.0231 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222 | 21.7222
MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN | MINIMUM HEADROOM | ST 84668 58036 | YES | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 40.1696 | 40.155 | 40.1192 | 40.0791 | 40.0308 | 39.9765 | 39.9166 | 39.8516 | 39.7757 | 39.6958 | 39.5181 | 38.8058 | 38.0793 | 37.7503 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724
|  | TROWBRIDGE TOWN | CT |  |  | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 40.1702 | 40.1564 | 40.1226 | 40.0848 | 40.0399 | 39.9907 | 39.9363 | 39.8793 | 39.8155 | 39.7502 | 39.6069 | 38.9586 | 38.2747 | 37.8844 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724
|  | TROWBRIDGE TOWN | LW |  |  | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 40.1696 | 40.155 | 40.1192 | 40.0791 | 40.0308 | 39.9765 | 39.9166 | 39.8516 | 39.7757 | 39.6958 | 39.5236 | 38.8058 | 38.0793 | 37.7503 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724
|  | TROWBRIDGE TOWN | ST |  |  | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 40.3742 | 40.1675 | 40.1515 | 40.1266 | 40.0916 | 40.0187 | 39.9431 | 39.8665 | 39.7818 | 39.6965 | 39.5181 | 39.0199 | 38.52 | 38.0723 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724
|  | TROWBRIDGE TOWN | FS |  |  | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 48.3469 | 40.378 | 40.1777 | 40.1769 | 40.1709 | 40.1627 | 40.1419 | 40.1205 | 40.093 | 40.0643 | 40.035 | 39.974 | 39.8064 | 39.6262 | 39.4367 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724 | 41.7724
BRAMLEY (FLEE) | READING BSP | TWYFORD | MINIMUM HEADROOM | SU 78430 76339 | YES | 16.6744 | 16.6722 | 16.6692 | 16.6654 | 14.0116 | 13.7023 | 13.3881 | 13.0725 | 12.737 | 12.4044 | 11.747 | 10.5649 | 9.3245 | 8.0831 | 15.3981 | 15.2616 | 15.0511 | 15.0448 | 15.0379 | 13.238 | 12.7695 | 12.3038 | 11.8076 | 11.3163 | 10.3442 | 8.9034 | 7.3826 | 5.8603 | 16.0085 | 15.9854 | 15.9367 | 15.9246 | 15.9118 | 15.8981 | 13.3032 | 12.8351 | 12.3371 | 11.8437 | 10.8663 | 9.4152 | 7.8739 | 6.3254
|  | TWYFORD | CT |  |  | 16.6744 | 16.6722 | 16.6692 | 16.6654 | 14.0116 | 13.7023 | 13.3881 | 13.0725 | 12.737 | 12.4044 | 11.747 | 10.5649 | 9.3245 | 8.0831 | 15.3981 | 15.2616 | 15.0511 | 15.0448 | 15.0379 | 13.238 | 12.7695 | 12.3038 | 11.8076 | 11.3163 | 10.3442 | 8.9034 | 7.3826 | 5.8603 | 16.0085 | 15.9854 | 15.9367 | 15.9246 | 15.9118 | 15.8981 | 13.3032 | 12.8351 | 12.3371 | 11.8437 | 10.8663 | 9.4152 | 7.8739 | 6.3254
|  | TWYFORD | LW |  |  | 16.6744 | 16.6722 | 16.6692 | 16.6654 | 14.0116 | 13.7023 | 13.3881 | 13.0725 | 12.737 | 12.4044 | 11.747 | 10.5649 | 9.3245 | 8.0831 | 15.4307 | 15.3064 | 15.1487 | 15.0597 | 15.057 | 15.0538 | 15.0499 | 13.0366 | 12.648 | 12.2633 | 11.5042 | 10.1525 | 8.7185 | 7.2846 | 16.024 | 16.0036 | 15.9722 | 15.9522 | 15.9473 | 15.9413 | 15.934 | 15.9255 | 13.1892 | 12.8035 | 12.0417 | 10.6778 | 9.2463 | 7.7955
|  | TWYFORD | ST |  |  | 16.6765 | 16.6757 | 16.6747 | 16.6735 | 16.6721 | 16.6701 | 16.6679 | 14.0882 | 13.9587 | 13.8314 | 13.5816 | 12.914 | 12.2201 | 11.5346 | 15.4774 | 15.4168 | 15.2959 | 15.1893 | 15.0635 | 15.0624 | 15.0611 | 15.0598 | 15.0584 | 15.0569 | 15.0536 | 12.8528 | 12.0533 | 11.2622 | 16.0709 | 16.0178 | 16.0039 | 15.9833 | 15.9592 | 15.9571 | 15.9549 | 15.9524 | 15.9498 | 15.947 | 15.9409 | 15.9227 | 12.5912 | 11.7971
|  | TWYFORD | FS |  |  | 16.6768 | 16.6763 | 16.6757 | 16.6749 | 16.674 | 16.6731 | 16.6721 | 16.671 | 16.6699 | 16.6687 | 16.6662 | 16.6567 | 14.0446 | 13.7639 | 15.5095 | 15.502 | 15.4931 | 15.4424 | 15.3795 | 15.3329 | 15.2957 | 15.2637 | 15.2323 | 15.2014 | 15.1412 | 15.0549 | 15.0493 | 15.0436 | 16.1029 | 16.0954 | 16.0864 | 16.0358 | 16.0125 | 16.0071 | 16.0016 | 15.9948 | 15.9881 | 15.9814 | 15.9682 | 15.9433 | 15.933 | 15.9224
COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET | MINIMUM HEADROOM | SP 52865 05849 | NO | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 35.2214 | 35.1762 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 38.0935 | 37.9819 | 37.6426 | 37.3219 | 37.1196 | 37.0133 | 36.9084 | 36.8045 | 36.6927 | 36.5887 | 36.4706 | 36.2914 | 36.1085 | 36.0865
|  | UNION STREET | CT |  |  | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 35.2269 | 35.1899 | 35.075 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 38.107 | 38.0157 | 37.7327 | 37.4699 | 37.2356 | 37.1087 | 37.0205 | 36.9286 | 36.8334 | 36.7411 | 36.5752 | 36.3788 | 36.1929 | 36.0865
|  | UNION STREET | LW |  |  | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 35.2214 | 35.1762 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 38.0935 | 37.9819 | 37.6426 | 37.3219 | 37.1196 | 37.0133 | 36.9084 | 36.8045 | 36.6927 | 36.5887 | 36.4706 | 36.2914 | 36.1085 | 36.0865
|  | UNION STREET | ST |  |  | 37.317 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 35.5197 | 35.2467 | 35.2224 | 35.2053 | 35.1933 | 35.1425 | 35.0905 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 38.5201 | 38.1558 | 38.0959 | 38.0538 | 38.0243 | 37.8991 | 37.7708 | 37.6362 | 37.4978 | 37.3651 | 37.1501 | 36.9258 | 36.7029 | 36.5223
|  | UNION STREET | FS |  |  | 37.3166 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 37.0329 | 35.5192 | 35.2469 | 35.2339 | 35.2116 | 35.1892 | 35.1691 | 35.1489 | 35.1237 | 35.0991 | 35.0749 | 35.0436 | 35.0436 | 35.0436 | 35.0436 | 38.5197 | 38.1562 | 38.1242 | 38.0693 | 38.0141 | 37.9645 | 37.9148 | 37.8528 | 37.792 | 37.7325 | 37.6166 | 37.3499 | 37.1446 | 37.0571
EAST CLAYDON GSP | BICESTER NORTH | UPPER HEYFORD | MINIMUM HEADROOM | SP 51750 25667 | YES | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 19.1578 | 19.0473 | 18.8544 | 18.6713 | 18.5211 | 18.3621 | 18.1943 | 18.0175 | 17.8268 | 17.7217 | 17.5372 | 17.5254 | 17.5254 | 17.5254 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 13.269 | 12.8754 | 12.4863
|  | UPPER HEYFORD | CT |  |  | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 19.1655 | 19.0718 | 18.9066 | 18.7274 | 18.5985 | 18.4589 | 18.3116 | 18.1521 | 17.9761 | 17.867 | 17.6611 | 17.5254 | 17.5254 | 17.5254 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 13.0174 | 12.6178
|  | UPPER HEYFORD | LW |  |  | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 19.1578 | 19.0473 | 18.8544 | 18.6713 | 18.5211 | 18.3621 | 18.1943 | 18.0175 | 17.8268 | 17.7217 | 17.5372 | 17.5254 | 17.5254 | 17.5254 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 13.269 | 12.8754 | 12.4863
|  | UPPER HEYFORD | ST |  |  | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 19.1961 | 19.1362 | 19.0409 | 18.9108 | 18.7544 | 18.6756 | 18.5978 | 18.5118 | 18.4144 | 18.3624 | 18.2658 | 18.0747 | 17.915 | 17.7584 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146
|  | UPPER HEYFORD | FS |  |  | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 23.4844 | 19.2266 | 19.2019 | 19.1757 | 19.1321 | 19.0831 | 19.0378 | 18.9901 | 18.9355 | 18.8767 | 18.8472 | 18.7881 | 18.6909 | 18.6297 | 18.5716 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146 | 16.5146
IVER 132KV | UPTON BSP | UPTON | MINIMUM HEADROOM | TQ 00800 79434 | NO | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 92.2736 | 92.23 | 92.1281 | 92.0171 | 91.906 | 91.7959 | 91.6864 | 91.5512 | 91.4063 | 91.2754 | 91.0088 | 90.5126 | 90.2961 | 90.0819 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609
|  | UPTON | CT |  |  | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 92.2816 | 92.2496 | 92.175 | 92.0937 | 92.0118 | 91.9305 | 91.8502 | 91.7485 | 91.639 | 91.5531 | 91.3745 | 90.6219 | 90.4128 | 90.206 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609
|  | UPTON | LW |  |  | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 92.2736 | 92.23 | 92.1281 | 92.0171 | 91.906 | 91.7959 | 91.6864 | 91.5512 | 91.4063 | 91.2754 | 91.0088 | 90.5126 | 90.2961 | 90.0819 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609
|  | UPTON | ST |  |  | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 92.392 | 92.2634 | 92.2063 | 92.1205 | 92.0167 | 91.9264 | 91.8375 | 91.7352 | 91.6243 | 91.5307 | 91.3412 | 90.8302 | 90.5465 | 90.4143 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609
|  | UPTON | FS |  |  | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 110.6181 | 92.4096 | 92.3039 | 92.2999 | 92.2809 | 92.2585 | 92.2283 | 92.1983 | 92.1542 | 92.1101 | 92.0732 | 92.0001 | 91.8078 | 91.6132 | 91.4242 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609 | 94.0609
NURSLING GSP | VELMORE BSP | VELMORE | MINIMUM HEADROOM | SU 42935 19205 | NO | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 26.5122 | 26.2879 | 25.8746 | 25.4329 | 24.9904 | 24.5512 | 24.0968 | 23.6328 | 23.1322 | 22.632 | 21.6289 | 20.121 | 18.5751 | 17.0302 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875
|  | VELMORE | CT |  |  | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 26.5197 | 26.3123 | 25.9214 | 25.5037 | 25.0823 | 24.6584 | 24.2213 | 23.7874 | 23.323 | 22.8643 | 21.9381 | 20.4702 | 18.9523 | 17.4374 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875
|  | VELMORE | LW |  |  | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 26.5122 | 26.2879 | 25.8746 | 25.4329 | 24.9904 | 24.5512 | 24.0968 | 23.6328 | 23.1322 | 22.632 | 21.6289 | 20.121 | 18.5751 | 17.0302 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875
|  | VELMORE | ST |  |  | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 26.5852 | 26.4611 | 26.2558 | 25.9529 | 25.5833 | 25.4287 | 25.2643 | 25.1011 | 24.9265 | 24.7546 | 24.4011 | 23.4682 | 22.5449 | 21.6313 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875
|  | VELMORE | FS |  |  | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 83.1075 | 26.6487 | 26.6171 | 26.6004 | 26.5253 | 26.4349 | 26.3818 | 26.3282 | 26.2585 | 26.1889 | 26.1193 | 25.9801 | 25.6179 | 25.2515 | 24.8855 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875 | 69.5875
FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR | MINIMUM HEADROOM | SZ 56148 77857 | YES | 28.3438 | 28.3336 | 28.3088 | 28.2812 | 28.253 | 28.2072 | 28.1603 | 28.1103 | 28.0554 | 28.0013 | 27.8954 | 27.5661 | 27.2094 | 26.7662 | 32.4228 | 32.4194 | 32.4111 | 32.4019 | 32.3925 | 32.3773 | 32.3616 | 32.3461 | 32.3294 | 32.3129 | 32.2806 | 32.1802 | 32.0715 | 31.9724 | 26.6929 | 26.681 | 26.6516 | 26.6191 | 26.5859 | 26.5319 | 26.4765 | 26.4217 | 26.3625 | 26.3041 | 26.1899 | 25.8344 | 25.4496 | 24.9713
|  | VENTNOR | CT |  |  | 28.3438 | 28.3336 | 28.3088 | 28.2812 | 28.253 | 28.2247 | 28.1964 | 28.1681 | 28.1348 | 28.0992 | 28.0237 | 27.6461 | 27.2094 | 26.7662 | 32.4228 | 32.4194 | 32.4112 | 32.402 | 32.3927 | 32.3833 | 32.374 | 32.3646 | 32.3544 | 32.3443 | 32.3242 | 32.2056 | 32.0727 | 31.9747 | 26.6929 | 26.681 | 26.6518 | 26.6194 | 26.5865 | 26.5533 | 26.5201 | 26.4869 | 26.451 | 26.4151 | 26.344 | 25.9241 | 25.4542 | 24.9845
|  | VENTNOR | LW |  |  | 28.3438 | 28.3336 | 28.3088 | 28.2812 | 28.253 | 28.2247 | 28.1964 | 28.1681 | 28.1348 | 28.0992 | 28.0237 | 27.6461 | 27.2094 | 26.7662 | 32.4228 | 32.4194 | 32.4111 | 32.4019 | 32.3925 | 32.3831 | 32.3737 | 32.3643 | 32.3536 | 32.3428 | 32.3197 | 32.2046 | 32.0715 | 31.9724 | 26.6929 | 26.681 | 26.6516 | 26.6191 | 26.5859 | 26.5525 | 26.5191 | 26.4858 | 26.4482 | 26.4098 | 26.3283 | 25.9208 | 25.4496 | 24.9713
|  | VENTNOR | ST |  |  | 28.3451 | 28.3367 | 28.3179 | 28.2894 | 28.2547 | 28.2072 | 28.1603 | 28.1103 | 28.0554 | 28.0013 | 27.8954 | 27.5661 | 27.2174 | 26.874 | 32.4232 | 32.4204 | 32.4141 | 32.4047 | 32.3931 | 32.3773 | 32.3616 | 32.3461 | 32.3294 | 32.3129 | 32.2806 | 32.1802 | 32.0739 | 31.9927 | 26.6945 | 26.6845 | 26.6624 | 26.6288 | 26.5878 | 26.5319 | 26.4765 | 26.4217 | 26.3625 | 26.3041 | 26.1899 | 25.8344 | 25.4581 | 25.0876
|  | VENTNOR | FS |  |  | 28.3498 | 28.3492 | 28.3485 | 28.3444 | 28.3394 | 28.329 | 28.3187 | 28.3054 | 28.2923 | 28.2793 | 28.2538 | 28.1807 | 28.0859 | 27.9789 | 32.4248 | 32.4246 | 32.4243 | 32.423 | 32.4213 | 32.4179 | 32.4144 | 32.41 | 32.4056 | 32.4013 | 32.3928 | 32.3684 | 32.3387 | 32.3061 | 26.7 | 26.6993 | 26.6984 | 26.6936 | 26.6878 | 26.6755 | 26.6634 | 26.6477 | 26.6322 | 26.6169 | 26.5869 | 26.5006 | 26.3954 | 26.2799
MANNINGTON GSP | MANNINGTON BSP | VERWOOD | MINIMUM HEADROOM | SU 07716 10226 | YES | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 16.7575 | 16.7061 | 16.6119 | 16.5288 | 16.4489 | 16.3672 | 16.2838 | 16.2004 | 16.0923 | 15.981 | 15.8003 | 15.4635 | 15.4635 | 15.4635 | 17.1555 | 17.1375 | 17.0986 | 17.0545 | 17.0121 | 16.9687 | 16.9245 | 16.8802 | 16.8228 | 16.7637 | 16.6679 | 16.425 | 16.1759 | 15.9678
|  | VERWOOD | CT |  |  | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 16.7632 | 16.7211 | 16.635 | 16.567 | 16.5017 | 16.434 | 16.3636 | 16.2925 | 16.2016 | 16.1095 | 15.9589 | 15.4969 | 15.4635 | 15.4635 | 17.1575 | 17.1427 | 17.1108 | 17.0747 | 17.0401 | 17.0042 | 16.9668 | 16.9291 | 16.8809 | 16.832 | 16.752 | 16.5069 | 16.2582 | 16.0099
|  | VERWOOD | LW |  |  | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 16.7575 | 16.7061 | 16.6119 | 16.5288 | 16.4489 | 16.3672 | 16.2838 | 16.2004 | 16.0923 | 15.981 | 15.8003 | 15.4635 | 15.4635 | 15.4635 | 17.1555 | 17.1375 | 17.0986 | 17.0545 | 17.0121 | 16.9687 | 16.9245 | 16.8802 | 16.8228 | 16.7637 | 16.6679 | 16.425 | 16.1759 | 15.9678
|  | VERWOOD | ST |  |  | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 16.8918 | 16.7448 | 16.6862 | 16.6147 | 16.5488 | 16.489 | 16.4276 | 16.3662 | 16.2898 | 16.2125 | 16.0821 | 15.7648 | 15.4635 | 15.4635 | 17.2024 | 17.151 | 17.1305 | 17.1001 | 17.0651 | 17.0333 | 17.0008 | 16.9682 | 16.9277 | 16.8866 | 16.8174 | 16.6491 | 16.4856 | 16.3234
|  | VERWOOD | FS |  |  | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 17.1188 | 16.9073 | 16.7831 | 16.7751 | 16.7532 | 16.7301 | 16.7008 | 16.671 | 16.6383 | 16.6103 | 16.5817 | 16.5339 | 16.4184 | 16.3063 | 16.195 | 17.2078 | 17.1644 | 17.1616 | 17.154 | 17.1459 | 17.1356 | 17.1252 | 17.1126 | 17.0977 | 17.0825 | 17.0572 | 16.9959 | 16.9364 | 16.8774
COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD | MINIMUM HEADROOM | SU 59847 89486 | YES | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 14.0221 | 13.0018 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 13.877 | 12.6615 | 11.4218 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 13.889 | 12.6772 | 11.4414
|  | WALLINGFORD | CT |  |  | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 14.0221 | 13.0018 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 13.877 | 12.6615 | 11.4218 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 13.889 | 12.6772 | 11.4414
|  | WALLINGFORD | LW |  |  | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 14.0221 | 13.0018 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 13.3446 | 12.1427 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 13.3583 | 12.16
|  | WALLINGFORD | ST |  |  | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278
|  | WALLINGFORD | FS |  |  | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278 | 17.8278
COWLEY GSP | DRAYTON BSP | WANTAGE | MINIMUM HEADROOM | SU 41290 88304 | YES | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 13.8909 | 12.8931 | 11.8762 | 17.4837 | 17.4413 | 17.3845 | 17.3204 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 13.2906 | 12.117 | 10.9174 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 13.4004 | 12.2227 | 11.0228
|  | WANTAGE | CT |  |  | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 13.8909 | 12.8931 | 11.8762 | 17.4847 | 17.4448 | 17.3908 | 17.3307 | 17.2664 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 13.346 | 12.187 | 11.0185 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 13.4565 | 12.2928 | 11.1239
|  | WANTAGE | LW |  |  | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 13.8909 | 12.8931 | 11.8762 | 17.4837 | 17.4413 | 17.3845 | 17.3204 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 13.2906 | 12.117 | 10.9174 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 13.4004 | 12.2227 | 11.0228
|  | WANTAGE | ST |  |  | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 13.7238 | 17.5001 | 17.4746 | 17.4408 | 17.4037 | 17.3591 | 17.3174 | 17.2878 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 17.2611 | 13.801 | 13.0956 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 13.9169 | 13.2031
|  | WANTAGE | FS |  |  | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.4007 | 17.5359 | 17.5011 | 17.489 | 17.4685 | 17.4478 | 17.4318 | 17.4213 | 17.4083 | 17.3954 | 17.3831 | 17.3587 | 17.2951 | 17.2611 | 17.2611 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577 | 17.6577
MANNINGTON GSP | WAREHAM | WAREHAM TOWN | MINIMUM HEADROOM | SY 92036 87463 | YES | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 18.8959 | 18.8863 | 18.8621 | 18.8331 | 18.7993 | 18.7628 | 18.7243 | 18.6845 | 18.6427 | 18.5996 | 18.5131 | 18.1884 | 18.015 | 17.8922 | 20.0717 | 20.0686 | 20.061 | 20.0519 | 20.0412 | 20.0297 | 20.0175 | 20.005 | 19.9919 | 19.9783 | 19.9709 | 19.9709 | 19.9709 | 19.9709
|  | WAREHAM TOWN | CT |  |  | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 18.8961 | 18.8867 | 18.8631 | 18.8351 | 18.8029 | 18.7684 | 18.7322 | 18.6949 | 18.6557 | 18.6153 | 18.5342 | 18.2482 | 18.0666 | 17.9363 | 20.0717 | 20.0687 | 20.0613 | 20.0525 | 20.0423 | 20.0315 | 20.0201 | 20.0083 | 19.9959 | 19.9832 | 19.9709 | 19.9709 | 19.9709 | 19.9709
|  | WAREHAM TOWN | LW |  |  | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 18.8959 | 18.8863 | 18.8621 | 18.8331 | 18.7993 | 18.7628 | 18.7243 | 18.6845 | 18.6427 | 18.5996 | 18.5131 | 18.1884 | 18.015 | 17.8922 | 20.0717 | 20.0686 | 20.061 | 20.0519 | 20.0412 | 20.0297 | 20.0175 | 20.005 | 19.9919 | 19.9783 | 19.9709 | 19.9709 | 19.9709 | 19.9709
|  | WAREHAM TOWN | ST |  |  | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 18.8995 | 18.8951 | 18.8847 | 18.8685 | 18.8468 | 18.8048 | 18.7621 | 18.719 | 18.6729 | 18.626 | 18.5327 | 18.305 | 18.1317 | 18.0195 | 20.0728 | 20.0714 | 20.0681 | 20.063 | 20.0562 | 20.0429 | 20.0295 | 20.0159 | 20.0013 | 19.9866 | 19.9709 | 19.9709 | 19.9709 | 19.9709
|  | WAREHAM TOWN | FS |  |  | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 22.8342 | 18.9017 | 18.9007 | 18.899 | 18.8939 | 18.8872 | 18.8742 | 18.861 | 18.8449 | 18.8288 | 18.8125 | 18.7799 | 18.6995 | 18.6218 | 18.5452 | 20.0735 | 20.0732 | 20.0726 | 20.071 | 20.0689 | 20.0648 | 20.0607 | 20.0556 | 20.0505 | 20.0454 | 20.0351 | 20.0097 | 19.9853 | 19.9709
BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD | MINIMUM HEADROOM | SU 86960 71382 | YES | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 35.8457 | 35.8354 | 35.8117 | 35.7828 | 35.7479 | 35.7064 | 35.6602 | 35.616 | 35.5684 | 35.5236 | 35.4364 | 35.3246 | 21.7283 | 20.1962 | 21.8716 | 21.6668 | 21.1994 | 20.6306 | 19.9417 | 19.122 | 18.2122 | 17.3393 | 16.4008 | 15.5157 | 13.7967 | 11.5902 | 10.037 | 8.5045
|  | WARFIELD | CT |  |  | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 35.8464 | 35.837 | 35.8154 | 35.7894 | 35.7579 | 35.7208 | 35.6815 | 35.6431 | 35.6001 | 35.5565 | 35.4694 | 35.3603 | 35.278 | 20.8018 | 21.8837 | 21.6986 | 21.2738 | 20.7594 | 20.1392 | 19.4064 | 18.6318 | 17.8729 | 17.0258 | 16.1647 | 14.4471 | 12.294 | 10.6713 | 9.1103
|  | WARFIELD | LW |  |  | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 35.8457 | 35.8354 | 35.8117 | 35.7828 | 35.7479 | 35.7064 | 35.6602 | 35.616 | 35.5684 | 35.5236 | 35.4364 | 35.3246 | 21.7283 | 20.1962 | 21.8716 | 21.6668 | 21.1994 | 20.6306 | 19.9417 | 19.122 | 18.2122 | 17.3393 | 16.4008 | 15.5157 | 13.7967 | 11.5902 | 10.037 | 8.5045
|  | WARFIELD | ST |  |  | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 35.8535 | 35.8453 | 35.8356 | 35.8197 | 35.7973 | 35.7786 | 35.7585 | 35.7388 | 35.7162 | 35.6928 | 35.6449 | 35.5743 | 35.5259 | 35.4796 | 22.0239 | 21.8632 | 21.6725 | 21.3575 | 20.9164 | 20.5477 | 20.1503 | 19.7627 | 19.317 | 18.8536 | 17.9092 | 16.5161 | 15.5611 | 14.6491
|  | WARFIELD | FS |  |  | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 37.4352 | 35.8559 | 35.8549 | 35.8537 | 35.8483 | 35.8407 | 35.8334 | 35.8251 | 35.8165 | 35.8072 | 35.7981 | 35.7801 | 35.7465 | 35.7251 | 35.7071 | 22.0727 | 22.053 | 22.0282 | 21.9228 | 21.7724 | 21.6273 | 21.4643 | 21.2945 | 21.1107 | 20.9314 | 20.5771 | 19.9147 | 19.4908 | 19.136
MELKSHAM GSP | FROME BSP | WARMINSTER | MINIMUM HEADROOM | ST 84936 44551 | NO | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 14.0768 | 13.7108 | 13.3472 | 12.9784 | 15.5815 | 15.52 | 15.5072 | 15.4879 | 15.4651 | 13.3104 | 13.1065 | 12.9342 | 12.7462 | 12.5502 | 12.1714 | 11.7293 | 11.2902 | 10.8447 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 12.989 | 12.5538 | 12.1216 | 11.683
|  | WARMINSTER | CT |  |  | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 14.0768 | 13.7108 | 13.3472 | 12.9784 | 15.5824 | 15.5217 | 15.5111 | 15.4949 | 15.4759 | 15.4547 | 13.2519 | 13.103 | 12.9302 | 12.7405 | 12.3759 | 11.8758 | 11.4428 | 11.0223 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 13.2002 | 12.6981 | 12.2718 | 11.8578
|  | WARMINSTER | LW |  |  | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 14.0768 | 13.7108 | 13.3472 | 12.9784 | 15.5815 | 15.52 | 15.5072 | 15.4879 | 15.4651 | 13.3104 | 13.1065 | 12.9342 | 12.7462 | 12.5502 | 12.1714 | 11.7293 | 11.2902 | 10.8447 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 12.989 | 12.5538 | 12.1216 | 11.683
|  | WARMINSTER | ST |  |  | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 14.0437 | 15.5834 | 15.5746 | 15.5593 | 15.5321 | 15.5148 | 15.5007 | 15.4856 | 15.4721 | 15.4562 | 13.2993 | 13.0424 | 12.6894 | 12.4049 | 12.1314 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 13.2302 | 12.9497
|  | WARMINSTER | FS |  |  | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 17.6366 | 15.5859 | 15.583 | 15.5796 | 15.5706 | 15.5596 | 15.5485 | 15.5365 | 15.5286 | 15.5227 | 15.5163 | 15.5039 | 15.4856 | 15.4709 | 15.4567 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091 | 16.3091
LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE | MINIMUM HEADROOM | SU 67988 09282 | NO | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 108.3012 | 108.2119 | 108.0247 | 107.8084 | 107.573 | 107.306 | 106.9993 | 106.7024 | 106.3898 | 106.1179 | 105.6151 | 104.3978 | 103.1194 | 101.8474 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181
|  | WATERLOOVILLE | CT |  |  | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 108.3087 | 108.2333 | 108.0739 | 107.8907 | 107.6899 | 107.4599 | 107.2001 | 106.9432 | 106.6681 | 106.4183 | 105.9546 | 104.7348 | 103.5113 | 102.2987 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181
|  | WATERLOOVILLE | LW |  |  | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 108.3012 | 108.2119 | 108.0247 | 107.8084 | 107.573 | 107.306 | 106.9993 | 106.7024 | 106.3898 | 106.1179 | 105.6151 | 104.3978 | 103.1194 | 101.8474 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181
|  | WATERLOOVILLE | ST |  |  | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 108.3706 | 108.2883 | 108.2016 | 108.0747 | 107.9164 | 107.7341 | 107.5328 | 107.3342 | 107.1185 | 106.9193 | 106.545 | 105.6927 | 104.8779 | 104.0823 | 107.352 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181
|  | WATERLOOVILLE | FS |  |  | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 102.3967 | 108.394 | 108.3798 | 108.3613 | 108.3213 | 108.2731 | 108.2076 | 108.1341 | 108.0528 | 107.9699 | 107.896 | 107.7587 | 107.4477 | 107.1409 | 106.8314 | 107.3651 | 107.3572 | 107.3468 | 107.3243 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181 | 107.3181
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON | MINIMUM HEADROOM | SU 69106 94287 | YES | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 11.8602 | 11.8238 | 11.7508 | 11.7057 | 11.6948 | 11.6838 | 11.673 | 11.6623 | 11.6508 | 11.6395 | 11.6171 | 11.5756 | 11.5287 | 11.4813 | 13.0171 | 13.012 | 13.0017 | 12.9907 | 12.9797 | 12.9686 | 12.9577 | 12.9469 | 12.9354 | 12.9239 | 12.9014 | 12.8595 | 12.8122 | 12.7645
|  | WATLINGTON | CT |  |  | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 11.8602 | 11.8238 | 11.7508 | 11.7057 | 11.6948 | 11.6838 | 11.673 | 11.6623 | 11.6508 | 11.6395 | 11.6171 | 11.5756 | 11.5287 | 11.4813 | 13.0171 | 13.012 | 13.0017 | 12.9907 | 12.9797 | 12.9686 | 12.9577 | 12.9469 | 12.9354 | 12.9239 | 12.9014 | 12.8595 | 12.8122 | 12.7645
|  | WATLINGTON | LW |  |  | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 11.8627 | 11.8296 | 11.7671 | 11.7096 | 11.7003 | 11.691 | 11.6819 | 11.6728 | 11.663 | 11.6533 | 11.6342 | 11.5959 | 11.551 | 11.5055 | 13.0174 | 13.0128 | 13.004 | 12.9946 | 12.9852 | 12.9759 | 12.9667 | 12.9575 | 12.9476 | 12.9379 | 12.9186 | 12.88 | 12.8347 | 12.7888
|  | WATLINGTON | ST |  |  | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 11.8769 | 11.8605 | 11.8337 | 11.7935 | 11.7446 | 11.7108 | 11.7058 | 11.701 | 11.6958 | 11.6907 | 11.6807 | 11.6568 | 11.6302 | 11.6032 | 13.0194 | 13.0171 | 13.0133 | 13.0077 | 13.0009 | 12.9958 | 12.9908 | 12.9859 | 12.9807 | 12.9755 | 12.9655 | 12.9414 | 12.9145 | 12.8873
|  | WATLINGTON | FS |  |  | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 13.1767 | 11.887 | 11.8825 | 11.8801 | 11.8684 | 11.8546 | 11.8421 | 11.8297 | 11.814 | 11.7984 | 11.7831 | 11.7536 | 11.7075 | 11.6981 | 11.6879 | 13.0208 | 13.0202 | 13.0198 | 13.0182 | 13.0163 | 13.0145 | 13.0128 | 13.0106 | 13.0084 | 13.0063 | 13.0021 | 12.9925 | 12.983 | 12.9727
AMERSHAM | LOUDWATER BSP | WELL END | MINIMUM HEADROOM | SU 88511 87957 | NO | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 21.2653 | 21.2476 | 21.2107 | 21.1736 | 21.1366 | 21.099 | 21.0606 | 21.0238 | 20.9864 | 20.9497 | 20.8787 | 20.7788 | 20.6745 | 20.5712 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319
|  | WELL END | CT |  |  | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 21.2653 | 21.2476 | 21.2107 | 21.1736 | 21.1366 | 21.099 | 21.0606 | 21.0238 | 20.9864 | 20.9497 | 20.8787 | 20.7788 | 20.6745 | 20.5712 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319
|  | WELL END | LW |  |  | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 21.2661 | 21.2492 | 21.2154 | 21.1815 | 21.1481 | 21.1144 | 21.0805 | 21.0488 | 21.0167 | 20.9854 | 20.9241 | 20.8278 | 20.727 | 20.6273 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319
|  | WELL END | ST |  |  | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 21.3531 | 21.2629 | 21.247 | 21.2264 | 21.2019 | 21.1876 | 21.1727 | 21.1588 | 21.1453 | 21.1321 | 21.1074 | 21.0482 | 20.9885 | 20.929 | 30.5397 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319
|  | WELL END | FS |  |  | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 33.7382 | 21.3571 | 21.3545 | 21.27 | 21.2637 | 21.2566 | 21.2513 | 21.2459 | 21.2399 | 21.2344 | 21.229 | 21.2187 | 21.1948 | 21.1718 | 21.1496 | 30.5615 | 30.5469 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319 | 30.1319
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END | MINIMUM HEADROOM | SU 57216 06147 | NO | 40.3516 | 40.3488 | 40.3429 | 40.3376 | 40.331 | 40.3231 | 40.3155 | 40.3035 | 40.2902 | 40.2772 | 40.2536 | 40.1923 | 40.0946 | 39.9967 | 35.8937 | 35.8663 | 35.8085 | 35.7564 | 35.7246 | 26.6702 | 26.5657 | 26.3997 | 26.2158 | 26.0368 | 25.7113 | 24.8664 | 23.5181 | 22.1682 | 37.3466 | 37.3406 | 37.328 | 37.3189 | 37.3137 | 37.3074 | 37.3013 | 37.2917 | 37.2811 | 37.2707 | 37.2519 | 37.203 | 37.125 | 37.0469
|  | WEST END | CT |  |  | 40.3516 | 40.3488 | 40.3429 | 40.3376 | 40.331 | 40.3231 | 40.3168 | 40.3096 | 40.3013 | 40.2939 | 40.2823 | 40.1923 | 40.0946 | 39.9967 | 35.8947 | 35.8704 | 35.818 | 35.7711 | 35.7246 | 35.7246 | 26.6266 | 26.534 | 26.4283 | 26.3274 | 26.163 | 25.0246 | 23.7498 | 22.4687 | 37.3468 | 37.3415 | 37.3301 | 37.3201 | 37.3154 | 37.3096 | 37.3048 | 37.2995 | 37.2934 | 37.2875 | 37.278 | 37.2122 | 37.1384 | 37.0643
|  | WEST END | LW |  |  | 40.3516 | 40.3488 | 40.3429 | 40.3376 | 40.331 | 40.3231 | 40.3168 | 40.3096 | 40.3013 | 40.2939 | 40.2823 | 40.1923 | 40.0946 | 39.9967 | 35.8937 | 35.8663 | 35.8085 | 35.7564 | 35.7246 | 26.6702 | 26.5825 | 26.4837 | 26.3695 | 26.267 | 26.1071 | 24.8664 | 23.5181 | 22.1682 | 37.3466 | 37.3406 | 37.328 | 37.3189 | 37.3137 | 37.3074 | 37.3023 | 37.2966 | 37.29 | 37.284 | 37.2748 | 37.203 | 37.125 | 37.0469
|  | WEST END | ST |  |  | 40.3522 | 40.3507 | 40.3478 | 40.3446 | 40.3399 | 40.3272 | 40.3155 | 40.3035 | 40.2902 | 40.2772 | 40.2536 | 40.1934 | 40.1286 | 40.0639 | 35.8996 | 35.8849 | 35.8566 | 35.8246 | 35.7785 | 35.7246 | 26.5657 | 26.3997 | 26.2158 | 26.0368 | 25.7113 | 24.8808 | 23.9878 | 23.0949 | 37.3479 | 37.3447 | 37.3385 | 37.3315 | 37.3215 | 37.3106 | 37.3013 | 37.2917 | 37.2811 | 37.2707 | 37.2519 | 37.2038 | 37.1522 | 37.1005
|  | WEST END | FS |  |  | 40.3527 | 40.3522 | 40.3516 | 40.3508 | 40.3496 | 40.3456 | 40.342 | 40.3373 | 40.3324 | 40.3278 | 40.3193 | 40.2978 | 40.2753 | 40.2522 | 35.9043 | 35.8999 | 35.8938 | 35.8863 | 35.8743 | 35.8348 | 35.7995 | 35.7532 | 35.7246 | 35.7246 | 26.6179 | 26.3217 | 26.0101 | 25.6924 | 37.3489 | 37.3479 | 37.3466 | 37.345 | 37.3424 | 37.3338 | 37.3261 | 37.3187 | 37.3148 | 37.3111 | 37.3043 | 37.2872 | 37.2692 | 37.2508
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE | MINIMUM HEADROOM | SU 24639 60279 | YES | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 7.11 | 9.4218 | 9.4078 | 9.3935 | 9.386 | 9.3784 | 9.3708 | 9.3632 | 9.3556 | 9.3474 | 9.3393 | 9.323 | 6.8916 | 6.5483 | 6.2083 | 7.1031 | 7.0704 | 6.9924 | 6.908 | 6.8232 | 6.7385 | 6.6537 | 6.5692 | 6.4777 | 6.3867 | 6.2047 | 5.8695 | 5.5221 | 5.1781
|  | WEST GRAFTON VILLAGE | CT |  |  | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 7.11 | 9.4218 | 9.4078 | 9.3935 | 9.386 | 9.3784 | 9.3708 | 9.3632 | 9.3556 | 9.3474 | 9.3393 | 9.323 | 6.8916 | 6.5483 | 6.2083 | 7.1031 | 7.0704 | 6.9924 | 6.908 | 6.8232 | 6.7385 | 6.6537 | 6.5692 | 6.4777 | 6.3867 | 6.2047 | 5.8695 | 5.5221 | 5.1781
|  | WEST GRAFTON VILLAGE | LW |  |  | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 7.11 | 9.4223 | 9.4093 | 9.3942 | 9.3872 | 9.38 | 9.3728 | 9.3656 | 9.3584 | 9.3505 | 9.3426 | 9.3268 | 6.9371 | 6.5953 | 6.2552 | 7.1044 | 7.0737 | 7.0006 | 6.9214 | 6.8416 | 6.7614 | 6.681 | 6.6004 | 6.5123 | 6.4243 | 6.2479 | 5.9155 | 5.5696 | 5.2255
|  | WEST GRAFTON VILLAGE | ST |  |  | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 9.4268 | 9.4199 | 9.4049 | 9.3951 | 9.3893 | 9.386 | 9.3827 | 9.3795 | 9.3759 | 9.3724 | 9.3653 | 9.347 | 9.3287 | 7.0877 | 7.1149 | 7.0988 | 7.0635 | 7.0102 | 6.9452 | 6.9087 | 6.8721 | 6.8357 | 6.796 | 6.7566 | 6.6776 | 6.4731 | 6.2693 | 6.0679
|  | WEST GRAFTON VILLAGE | FS |  |  | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 10.6356 | 9.4305 | 9.4297 | 9.4287 | 9.4231 | 9.4163 | 9.411 | 9.4057 | 9.3989 | 9.3972 | 9.3958 | 9.3929 | 9.3858 | 9.3787 | 9.3718 | 7.1235 | 7.1216 | 7.1194 | 7.1062 | 7.0902 | 7.0778 | 7.0654 | 7.0494 | 7.0333 | 7.0174 | 6.9858 | 6.9063 | 6.8274 | 6.7497
AXMINSTER | YEOVIL BSP | WEST HENDFORD | MINIMUM HEADROOM | ST 55000 15442 | YES | 54.6881 | 54.6425 | 54.5801 | 54.5794 | 54.5786 | 54.5776 | 54.5763 | 54.5749 | 54.5727 | 54.5703 | 54.5644 | 54.5434 | 54.5078 | 54.456 | 54.0128 | 53.9633 | 53.8691 | 53.7602 | 53.6421 | 53.5762 | 53.5187 | 53.4569 | 53.3968 | 53.3478 | 53.2407 | 53.1646 | 53.0987 | 53.0251 | 54.0804 | 54.0748 | 54.0646 | 54.0528 | 54.0401 | 54.0262 | 54.0112 | 53.9945 | 53.9863 | 53.9813 | 53.9695 | 53.929 | 53.8673 | 53.7911
|  | WEST HENDFORD | CT |  |  | 54.6881 | 54.6425 | 54.5801 | 54.5794 | 54.5786 | 54.5776 | 54.5763 | 54.5749 | 54.5727 | 54.5703 | 54.5644 | 54.5434 | 54.5078 | 54.456 | 54.0134 | 53.9699 | 53.8854 | 53.7891 | 53.6853 | 53.5957 | 53.5432 | 53.4847 | 53.4191 | 53.3647 | 53.2552 | 53.1646 | 53.0987 | 53.0251 | 54.0804 | 54.0748 | 54.0646 | 54.0528 | 54.0401 | 54.0262 | 54.0112 | 53.9945 | 53.9863 | 53.9813 | 53.9695 | 53.929 | 53.8673 | 53.7911
|  | WEST HENDFORD | LW |  |  | 54.6881 | 54.6425 | 54.5801 | 54.5794 | 54.5786 | 54.5776 | 54.5763 | 54.5749 | 54.5727 | 54.5703 | 54.5644 | 54.5434 | 54.5078 | 54.456 | 54.0128 | 53.9633 | 53.8691 | 53.7602 | 53.6421 | 53.5762 | 53.5187 | 53.4569 | 53.3968 | 53.3478 | 53.2407 | 53.1832 | 53.1298 | 53.0669 | 54.0814 | 54.0761 | 54.0662 | 54.0547 | 54.042 | 54.0283 | 54.0133 | 54.0025 | 54.0004 | 53.9978 | 53.9918 | 53.9701 | 53.9333 | 53.8797
|  | WEST HENDFORD | ST |  |  | 54.7399 | 54.6682 | 54.6208 | 54.5809 | 54.5806 | 54.5803 | 54.5799 | 54.5795 | 54.579 | 54.5784 | 54.5773 | 54.5723 | 54.564 | 54.5519 | 54.069 | 53.9911 | 53.9396 | 53.8696 | 53.7864 | 53.6857 | 53.6041 | 53.5562 | 53.5026 | 53.4451 | 53.3489 | 53.2294 | 53.204 | 53.1771 | 54.0874 | 54.0795 | 54.0742 | 54.067 | 54.0584 | 54.048 | 54.037 | 54.025 | 54.0116 | 54.0062 | 54.005 | 53.9999 | 53.9913 | 53.9788
|  | WEST HENDFORD | FS |  |  | 54.7458 | 54.7354 | 54.7209 | 54.6983 | 54.6724 | 54.637 | 54.5998 | 54.5804 | 54.5802 | 54.58 | 54.5796 | 54.5779 | 54.5754 | 54.5727 | 54.0755 | 54.0642 | 54.0484 | 54.0239 | 53.9958 | 53.9573 | 53.9169 | 53.8694 | 53.8193 | 53.7665 | 53.6531 | 53.5627 | 53.5019 | 53.4454 | 54.0881 | 54.0869 | 54.0852 | 54.0826 | 54.0797 | 54.0757 | 54.0714 | 54.0665 | 54.0613 | 54.0558 | 54.0441 | 54.0253 | 54.0085 | 54.0003
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR | MINIMUM HEADROOM | ST 77699 22040 | YES | 7.7235 | 7.7223 | 7.7207 | 7.7186 | 7.1222 | 7.1188 | 7.1147 | 7.1099 | 7.1048 | 7.0989 | 7.0846 | 7.0337 | 6.8473 | 6.551 | 7.5607 | 7.5585 | 7.5552 | 7.5516 | 7.5478 | 7.5436 | 7.5391 | 7.5344 | 7.095 | 7.0597 | 6.9897 | 6.7064 | 6.3615 | 6.0053 | 7.0537 | 7.0459 | 7.0301 | 7.0121 | 6.9925 | 6.9716 | 6.9496 | 6.9269 | 6.9025 | 6.8741 | 6.8034 | 6.4753 | 6.1048 | 5.7183
|  | WEST STOUR | CT |  |  | 7.7235 | 7.7223 | 7.7207 | 7.7186 | 7.1222 | 7.1188 | 7.1147 | 7.1099 | 7.1048 | 7.0989 | 7.0846 | 7.0337 | 6.8473 | 6.551 | 7.5607 | 7.5585 | 7.5552 | 7.5516 | 7.5478 | 7.5436 | 7.5391 | 7.5344 | 7.105 | 7.0812 | 7.0304 | 6.7064 | 6.3615 | 6.0053 | 7.0537 | 7.0459 | 7.0301 | 7.0121 | 6.9925 | 6.9716 | 6.9496 | 6.9269 | 6.9025 | 6.8769 | 6.8203 | 6.4753 | 6.1048 | 5.7183
|  | WEST STOUR | LW |  |  | 7.7235 | 7.7223 | 7.7207 | 7.7186 | 7.1222 | 7.1188 | 7.1147 | 7.1099 | 7.1048 | 7.0989 | 7.0846 | 7.0337 | 6.8473 | 6.551 | 7.5628 | 7.5621 | 7.5611 | 7.56 | 7.5585 | 7.5567 | 7.5545 | 7.5519 | 7.5492 | 7.1119 | 7.0685 | 6.7834 | 6.4773 | 6.1613 | 7.0579 | 7.0531 | 7.0421 | 7.0288 | 7.0136 | 6.997 | 6.9793 | 6.9607 | 6.9407 | 6.9198 | 6.8728 | 6.5748 | 6.2511 | 5.9134
|  | WEST STOUR | ST |  |  | 7.7247 | 7.7243 | 7.7237 | 7.723 | 7.7223 | 7.7212 | 7.72 | 7.7187 | 7.1236 | 7.122 | 7.1186 | 7.1062 | 7.0308 | 6.8732 | 7.5634 | 7.5632 | 7.5629 | 7.5625 | 7.562 | 7.5614 | 7.5607 | 7.56 | 7.095 | 7.0597 | 6.9897 | 6.8155 | 6.6374 | 6.4576 | 7.1236 | 7.0586 | 7.0544 | 7.0478 | 7.0392 | 7.0082 | 6.9771 | 6.9456 | 6.9097 | 6.8741 | 6.8034 | 6.6263 | 6.4438 | 6.2587
|  | WEST STOUR | FS |  |  | 7.7248 | 7.7245 | 7.7243 | 7.7238 | 7.7233 | 7.7228 | 7.7223 | 7.7217 | 7.7211 | 7.7204 | 7.7191 | 7.12 | 7.1132 | 7.1058 | 7.5635 | 7.5633 | 7.5632 | 7.5629 | 7.5626 | 7.5623 | 7.562 | 7.5617 | 7.5614 | 7.561 | 7.5602 | 7.0975 | 7.0346 | 6.9734 | 7.1244 | 7.0609 | 7.0603 | 7.0583 | 7.0557 | 7.046 | 7.0361 | 7.0238 | 7.0114 | 6.9992 | 6.9749 | 6.9113 | 6.8467 | 6.7837
MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE | MINIMUM HEADROOM | SZ 07642 91485 | NO | 28.0062 | 27.9406 | 27.7812 | 27.5834 | 27.3763 | 27.1619 | 26.9425 | 26.719 | 26.4766 | 26.231 | 25.8264 | 24.7603 | 23.5781 | 22.3953 | 24.986 | 24.9058 | 24.7111 | 24.4695 | 24.2149 | 23.9444 | 23.6677 | 23.386 | 23.0801 | 22.7705 | 22.2602 | 20.9155 | 19.5397 | 18.1745 | 26.3199 | 26.2477 | 26.0725 | 25.8551 | 25.6275 | 25.3918 | 25.1478 | 24.865 | 24.5581 | 24.2473 | 23.7351 | 22.3856 | 21.0049 | 19.6348
|  | WESTBOURNE | CT |  |  | 28.0062 | 27.9406 | 27.7812 | 27.5834 | 27.3763 | 27.1619 | 26.9425 | 26.719 | 26.4766 | 26.231 | 25.8264 | 24.7603 | 23.5781 | 22.3953 | 24.9913 | 24.9187 | 24.7426 | 24.5246 | 24.2972 | 24.0563 | 23.8125 | 23.5616 | 23.2835 | 22.9983 | 22.5179 | 21.1677 | 19.81 | 18.4689 | 26.3246 | 26.2593 | 26.1009 | 25.9047 | 25.7001 | 25.4893 | 25.2768 | 25.0413 | 24.7621 | 24.4759 | 23.9938 | 22.6387 | 21.2762 | 19.9302
|  | WESTBOURNE | LW |  |  | 28.0062 | 27.9406 | 27.7812 | 27.5834 | 27.3763 | 27.1619 | 26.9425 | 26.719 | 26.4766 | 26.231 | 25.8264 | 24.7603 | 23.5781 | 22.3953 | 24.986 | 24.9058 | 24.7111 | 24.4695 | 24.2149 | 23.9444 | 23.6677 | 23.386 | 23.0801 | 22.7705 | 22.2602 | 20.9155 | 19.5397 | 18.1745 | 26.3199 | 26.2477 | 26.0725 | 25.8551 | 25.6275 | 25.3918 | 25.1478 | 24.865 | 24.5581 | 24.2473 | 23.7351 | 22.3856 | 21.0049 | 19.6348
|  | WESTBOURNE | ST |  |  | 28.0248 | 27.9845 | 27.8948 | 27.7457 | 27.5632 | 27.4121 | 27.2607 | 27.1063 | 26.9346 | 26.7588 | 26.4597 | 25.7559 | 25.0753 | 24.3774 | 25.0086 | 24.9594 | 24.8499 | 24.6677 | 24.4448 | 24.26 | 24.0691 | 23.8744 | 23.6578 | 23.4361 | 23.0589 | 22.1712 | 21.3129 | 20.4622 | 26.3402 | 26.296 | 26.1974 | 26.0335 | 25.8329 | 25.6668 | 25.5004 | 25.3307 | 25.1377 | 24.9153 | 24.5367 | 23.6458 | 22.7844 | 21.9307
|  | WESTBOURNE | FS |  |  | 28.0466 | 28.0426 | 28.0372 | 28.0021 | 27.9598 | 27.9079 | 27.8551 | 27.7895 | 27.7227 | 27.6551 | 27.5395 | 27.2664 | 27.0112 | 26.7663 | 25.0353 | 25.0304 | 25.0238 | 24.981 | 24.9293 | 24.8659 | 24.8013 | 24.7212 | 24.6397 | 24.5571 | 24.4159 | 24.0763 | 23.7544 | 23.4456 | 26.3642 | 26.3598 | 26.3539 | 26.3154 | 26.2689 | 26.2118 | 26.1537 | 26.0816 | 26.0083 | 25.9339 | 25.8069 | 25.5067 | 25.2262 | 24.9248
MELKSHAM GSP | FROME BSP | WESTBURY | MINIMUM HEADROOM | ST 87654 51530 | YES | 25.747 | 25.6981 | 25.5814 | 25.4546 | 25.3195 | 25.1786 | 25.0321 | 24.8808 | 24.7109 | 24.5373 | 24.1783 | 23.1748 | 22.1169 | 21.0514 | 27.4149 | 27.4 | 27.3644 | 27.3258 | 27.2846 | 27.2571 | 25.9187 | 25.7405 | 25.5403 | 25.3358 | 24.9129 | 23.7308 | 22.4845 | 21.2294 | 28.7006 | 28.6954 | 28.683 | 28.6716 | 28.6716 | 28.6716 | 28.6716 | 28.6716 | 25.887 | 25.6997 | 25.3122 | 24.2293 | 23.0876 | 21.9378
|  | WESTBURY | CT |  |  | 25.747 | 25.6981 | 25.5814 | 25.4546 | 25.3195 | 25.1786 | 25.0321 | 24.8808 | 24.7109 | 24.5373 | 24.1783 | 23.1748 | 22.1169 | 21.0514 | 27.4183 | 27.4081 | 27.3838 | 27.3574 | 27.3284 | 27.298 | 27.2724 | 27.2523 | 25.9232 | 25.7833 | 25.4883 | 24.3601 | 23.1778 | 21.9963 | 28.7018 | 28.6982 | 28.6898 | 28.6806 | 28.6716 | 28.6716 | 28.6716 | 28.6716 | 28.6716 | 28.6716 | 25.8394 | 24.8058 | 23.7227 | 22.6403
|  | WESTBURY | LW |  |  | 25.747 | 25.6981 | 25.5814 | 25.4546 | 25.3195 | 25.1786 | 25.0321 | 24.8808 | 24.7109 | 24.5373 | 24.1783 | 23.1748 | 22.1169 | 21.0514 | 27.4149 | 27.4 | 27.3644 | 27.3258 | 27.2846 | 27.2571 | 25.9187 | 25.7405 | 25.5403 | 25.3358 | 24.9129 | 23.7308 | 22.4845 | 21.2294 | 28.7006 | 28.6954 | 28.683 | 28.6716 | 28.6716 | 28.6716 | 28.6716 | 28.6716 | 25.887 | 25.6997 | 25.3122 | 24.2293 | 23.0876 | 21.9378
|  | WESTBURY | ST |  |  | 25.9608 | 25.7436 | 25.6859 | 25.599 | 25.4883 | 25.3763 | 25.2623 | 25.1476 | 25.0216 | 24.8953 | 24.6355 | 23.93 | 23.2241 | 22.5284 | 27.4801 | 27.4139 | 27.3963 | 27.3698 | 27.336 | 27.3019 | 27.2729 | 27.2512 | 25.9063 | 25.7576 | 25.4515 | 24.6204 | 23.7889 | 22.9693 | 28.7369 | 28.7002 | 28.6941 | 28.6849 | 28.6732 | 28.6716 | 28.6716 | 28.6716 | 28.6716 | 28.6716 | 25.8056 | 25.0443 | 24.2825 | 23.5317
|  | WESTBURY | FS |  |  | 25.9811 | 25.7871 | 25.7837 | 25.7654 | 25.743 | 25.7107 | 25.6778 | 25.6356 | 25.5922 | 25.5485 | 25.459 | 25.2206 | 24.9705 | 24.7128 | 27.4863 | 27.4271 | 27.4261 | 27.4205 | 27.4137 | 27.4039 | 27.3938 | 27.381 | 27.3677 | 27.3544 | 27.3271 | 27.265 | 25.8461 | 25.5425 | 28.7406 | 28.7052 | 28.7045 | 28.7026 | 28.7002 | 28.6968 | 28.6933 | 28.6888 | 28.6842 | 28.6796 | 28.6716 | 28.6716 | 28.6716 | 25.889
NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE | MINIMUM HEADROOM | SU 41618 12009 | NO | 59.7464 | 59.6387 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 56.597 | 56.1456 | 55.6801 | 55.0205 | 53.9215 | 52.8507 | 51.7956 | 57.609 | 57.4588 | 57.2924 | 57.1787 | 56.9832 | 56.8307 | 56.6819 | 56.5267 | 56.3599 | 52.872 | 52.0921 | 50.7927 | 49.5267 | 48.2792 | 57.3506 | 57.237 | 57.0983 | 57.0164 | 56.8754 | 56.8063 | 56.7684 | 56.7289 | 53.1464 | 52.5971 | 51.8187 | 50.5217 | 49.2581 | 48.0129
|  | WESTERN ESPLANADE | CT |  |  | 59.7464 | 59.6387 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 56.597 | 56.1456 | 55.6801 | 55.0205 | 53.9215 | 52.8507 | 51.7956 | 57.622 | 57.499 | 57.3382 | 57.2494 | 57.0857 | 56.9576 | 56.8285 | 56.6866 | 56.5346 | 56.3655 | 52.6944 | 51.3979 | 50.238 | 49.116 | 57.3604 | 57.2674 | 57.1314 | 57.0673 | 56.9493 | 56.857 | 56.8057 | 56.7696 | 56.7309 | 53.1646 | 52.4198 | 51.1257 | 49.9681 | 48.8482
|  | WESTERN ESPLANADE | LW |  |  | 59.7464 | 59.6387 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 56.597 | 56.1456 | 55.6801 | 55.0205 | 53.9215 | 52.8507 | 51.7956 | 57.609 | 57.4588 | 57.2924 | 57.1787 | 56.9832 | 56.8307 | 56.6819 | 56.5267 | 56.3599 | 52.872 | 52.0921 | 50.7927 | 49.5267 | 48.2792 | 57.3506 | 57.237 | 57.0983 | 57.0164 | 56.8754 | 56.8063 | 56.7684 | 56.7289 | 53.1464 | 52.5971 | 51.8187 | 50.5217 | 49.2581 | 48.0129
|  | WESTERN ESPLANADE | ST |  |  | 59.8272 | 59.7195 | 59.5986 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 55.9352 | 55.275 | 54.6345 | 57.7677 | 57.5714 | 57.4227 | 57.3555 | 57.2276 | 57.1398 | 57.0515 | 56.9549 | 56.8496 | 56.7311 | 56.5671 | 53.1737 | 52.3931 | 51.6357 | 57.4358 | 57.3222 | 57.1947 | 57.1438 | 57.0516 | 56.9883 | 56.9247 | 56.855 | 56.8111 | 56.7809 | 56.7392 | 52.8982 | 52.119 | 51.3632
|  | WESTERN ESPLANADE | FS |  |  | 59.8515 | 59.7768 | 59.7324 | 59.6941 | 59.6201 | 59.5651 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 59.5357 | 57.8176 | 57.6642 | 57.5894 | 57.536 | 57.4373 | 57.4001 | 57.3647 | 57.3232 | 57.279 | 57.2336 | 57.1659 | 57.0417 | 56.9419 | 56.8496 | 57.4614 | 57.3826 | 57.3358 | 57.2954 | 57.2174 | 57.1759 | 57.1504 | 57.1205 | 57.0887 | 57.056 | 57.0071 | 56.9176 | 56.8457 | 56.8111
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON | MINIMUM HEADROOM | SU 45207 09912 | NO | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 25.3566 | 25.3496 | 25.3355 | 25.3215 | 25.307 | 25.2921 | 25.2481 | 25.2017 | 25.1517 | 25.1012 | 24.9947 | 24.7019 | 24.4003 | 24.1045 | 24.8615 | 24.86 | 24.857 | 24.8539 | 24.8507 | 24.8475 | 24.8379 | 24.8278 | 24.817 | 24.806 | 24.7828 | 24.7167 | 24.6791 | 24.6791
|  | WESTON | CT |  |  | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 25.3566 | 25.3496 | 25.3355 | 25.3215 | 25.307 | 25.2927 | 25.2756 | 25.2539 | 25.2309 | 25.2066 | 25.1483 | 24.7808 | 24.4857 | 24.2145 | 24.8615 | 24.86 | 24.857 | 24.8539 | 24.8507 | 24.8476 | 24.8439 | 24.8392 | 24.8342 | 24.8289 | 24.8162 | 24.7363 | 24.6791 | 24.6791
|  | WESTON | LW |  |  | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 25.3571 | 25.3504 | 25.3379 | 25.3255 | 25.3127 | 25.3004 | 25.2823 | 25.2579 | 25.2311 | 25.2027 | 25.1297 | 24.7071 | 24.4003 | 24.1045 | 24.8616 | 24.8602 | 24.8575 | 24.8548 | 24.852 | 24.8493 | 24.8454 | 24.8401 | 24.8342 | 24.8281 | 24.8122 | 24.718 | 24.6791 | 24.6791
|  | WESTON | ST |  |  | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 25.3593 | 25.3559 | 25.3503 | 25.3433 | 25.3348 | 25.2921 | 25.2481 | 25.2017 | 25.1517 | 25.1012 | 24.9947 | 24.7019 | 24.4817 | 24.2737 | 24.8621 | 24.8614 | 24.8602 | 24.8587 | 24.8568 | 24.8475 | 24.8379 | 24.8278 | 24.817 | 24.806 | 24.7828 | 24.7167 | 24.6791 | 24.6791
|  | WESTON | FS |  |  | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 27.2356 | 25.3608 | 25.3595 | 25.3582 | 25.356 | 25.3533 | 25.3423 | 25.3312 | 25.3159 | 25.3005 | 25.2849 | 25.2536 | 25.16 | 25.0563 | 24.9486 | 24.8625 | 24.8622 | 24.8619 | 24.8614 | 24.8608 | 24.8584 | 24.856 | 24.8527 | 24.8493 | 24.8459 | 24.8391 | 24.8188 | 24.7962 | 24.7728
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH | MINIMUM HEADROOM | SY 67443 79096 | YES | 28.0942 | 28.0601 | 57.8272 | 57.7216 | 57.5902 | 57.4404 | 57.2843 | 57.113 | 56.9354 | 56.7523 | 56.366 | 54.9324 | 53.5097 | 52.0938 | 26.637 | 26.6286 | 55.1081 | 55.0821 | 55.0497 | 55.0128 | 54.9744 | 54.9321 | 54.8884 | 54.8432 | 54.7481 | 54.3948 | 53.8246 | 52.323 | 26.7 | 26.7 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.1102 | 54.8951 | 54.4414 | 52.7579 | 51.087 | 49.4241
|  | WEYMOUTH | CT |  |  | 28.0942 | 28.0601 | 57.8272 | 57.7216 | 57.5902 | 57.4404 | 57.2843 | 57.113 | 56.9354 | 56.7523 | 56.3817 | 54.9324 | 53.5097 | 52.0938 | 26.6372 | 26.6291 | 55.1095 | 55.0848 | 55.0546 | 55.0206 | 54.9852 | 54.9466 | 54.9064 | 54.8652 | 54.7817 | 54.4553 | 54.134 | 52.8359 | 26.7 | 26.7 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.1963 | 54.9995 | 54.6018 | 53.0461 | 51.5149 | 49.9921
|  | WEYMOUTH | LW |  |  | 28.0942 | 28.0601 | 57.8272 | 57.7216 | 57.5902 | 57.4404 | 57.2843 | 57.113 | 56.9354 | 56.7523 | 56.3817 | 54.9324 | 53.5097 | 52.0938 | 26.637 | 26.6286 | 55.1081 | 55.0821 | 55.0497 | 55.0128 | 54.9744 | 54.9321 | 54.8884 | 54.8432 | 54.7519 | 54.3948 | 53.8246 | 52.323 | 26.7 | 26.7 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.1102 | 54.8951 | 54.4599 | 52.7579 | 51.087 | 49.4241
|  | WEYMOUTH | ST |  |  | 28.1066 | 28.0902 | 57.9029 | 57.8431 | 57.7604 | 57.5767 | 57.3911 | 57.1984 | 56.9929 | 56.7843 | 56.366 | 55.3563 | 54.4061 | 53.4754 | 26.64 | 26.636 | 55.1268 | 55.1121 | 55.0917 | 55.0464 | 55.0007 | 54.9532 | 54.9025 | 54.8511 | 54.7481 | 54.4993 | 54.2651 | 53.7883 | 26.7 | 26.7 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.1777 | 54.9328 | 54.4414 | 53.2557 | 52.1398 | 51.0467
|  | WEYMOUTH | FS |  |  | 28.346 | 28.1096 | 57.9512 | 57.9307 | 57.9028 | 57.8451 | 57.7875 | 57.7166 | 57.6457 | 57.5738 | 57.4293 | 57.0747 | 56.731 | 56.3862 | 26.699 | 26.6408 | 55.1387 | 55.1336 | 55.1268 | 55.1126 | 55.0984 | 55.0809 | 55.0634 | 55.0457 | 55.0101 | 54.9227 | 54.838 | 54.753 | 26.7 | 26.7 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 54.8702 | 54.4652
COWLEY GSP | HEADINGTON BSP | WHEATLEY | MINIMUM HEADROOM | SP 60777 05379 | NO | 21.2376 | 21.2281 | 21.2098 | 21.1894 | 21.1683 | 21.1511 | 21.1337 | 21.116 | 21.0962 | 21.076 | 21.0345 | 20.9939 | 20.9341 | 20.8482 | 19.1202 | 19.067 | 18.9624 | 18.846 | 18.7275 | 18.6344 | 18.605 | 18.59 | 18.576 | 18.5618 | 18.5329 | 18.4585 | 18.3605 | 18.2866 | 20.0181 | 20.0155 | 20.0115 | 20.0069 | 20.0018 | 19.9964 | 19.9906 | 19.9843 | 19.9762 | 19.9672 | 19.9461 | 19.8737 | 19.7702 | 19.6439
|  | WHEATLEY | CT |  |  | 21.2376 | 21.2281 | 21.2098 | 21.1894 | 21.1683 | 21.1511 | 21.1337 | 21.116 | 21.0962 | 21.076 | 21.0345 | 20.9939 | 20.9341 | 20.8482 | 19.1227 | 19.0762 | 18.9849 | 18.8841 | 18.7805 | 18.6981 | 18.6128 | 18.59 | 18.576 | 18.5618 | 18.5329 | 18.4585 | 18.3605 | 18.2866 | 20.0181 | 20.0155 | 20.0115 | 20.0069 | 20.0018 | 19.9964 | 19.9906 | 19.9843 | 19.9762 | 19.9672 | 19.9461 | 19.8737 | 19.7702 | 19.6439
|  | WHEATLEY | LW |  |  | 21.2376 | 21.2281 | 21.2098 | 21.1894 | 21.1683 | 21.1511 | 21.1337 | 21.116 | 21.0962 | 21.076 | 21.0345 | 20.9939 | 20.9341 | 20.8482 | 19.1202 | 19.067 | 18.9624 | 18.846 | 18.7275 | 18.6344 | 18.605 | 18.594 | 18.5818 | 18.5694 | 18.5438 | 18.4912 | 18.419 | 18.3703 | 20.0206 | 20.0198 | 20.0187 | 20.0172 | 20.0155 | 20.0133 | 20.0107 | 20.0076 | 20.0037 | 19.9992 | 19.9882 | 19.9491 | 19.8873 | 19.7986
|  | WHEATLEY | ST |  |  | 21.2413 | 21.2366 | 21.2284 | 21.2168 | 21.203 | 21.1957 | 21.1881 | 21.1803 | 21.1717 | 21.1632 | 21.1476 | 21.1079 | 21.0577 | 21.0113 | 19.1391 | 19.1121 | 19.0643 | 18.9963 | 18.9153 | 18.8753 | 18.8334 | 18.7906 | 18.7435 | 18.698 | 18.6159 | 18.5891 | 18.5582 | 18.5237 | 20.0214 | 20.0211 | 20.0207 | 20.0202 | 20.0197 | 20.019 | 20.0182 | 20.0173 | 20.0162 | 20.0151 | 20.0128 | 20.0034 | 19.988 | 19.967
|  | WHEATLEY | FS |  |  | 21.2436 | 21.242 | 21.2403 | 21.2368 | 21.2329 | 21.2302 | 21.2275 | 21.2241 | 21.2208 | 21.2175 | 21.2111 | 21.1956 | 21.1792 | 21.1608 | 19.1522 | 19.1437 | 19.1345 | 19.1148 | 19.0928 | 19.0782 | 19.0635 | 19.0452 | 19.0272 | 19.0097 | 18.9758 | 18.9 | 18.8246 | 18.7395 | 20.0215 | 20.0213 | 20.0211 | 20.0208 | 20.0204 | 20.0201 | 20.0197 | 20.0193 | 20.0189 | 20.0185 | 20.0175 | 20.014 | 20.0093 | 20.0042
BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH | MINIMUM HEADROOM | SU 45924 48466 | YES | 8.5908 | 8.5788 | 8.5506 | 8.5199 | 8.4894 | 8.459 | 8.4287 | 8.3983 | 8.365 | 8.3316 | 8.2853 | 8.205 | 8.1061 | 4.677 | 7.8955 | 7.8772 | 7.8344 | 7.7879 | 7.7417 | 7.6958 | 7.6501 | 7.6046 | 7.5545 | 7.5044 | 7.4041 | 7.2285 | 7.1837 | 4.6059 | 4.717 | 4.6694 | 4.557 | 4.4351 | 4.3141 | 4.1942 | 4.0752 | 3.957 | 3.828 | 3.6996 | 3.4447 | 3.0225 | 2.5521 | 2.064
|  | WHITCHURCH | CT |  |  | 8.5908 | 8.5788 | 8.5506 | 8.5199 | 8.4894 | 8.459 | 8.4287 | 8.3983 | 8.365 | 8.3316 | 8.2853 | 8.205 | 8.1061 | 4.677 | 7.8955 | 7.8772 | 7.8344 | 7.7879 | 7.7417 | 7.6958 | 7.6501 | 7.6046 | 7.5545 | 7.5044 | 7.4041 | 7.2285 | 7.1837 | 4.6059 | 4.717 | 4.6694 | 4.557 | 4.4351 | 4.3141 | 4.1942 | 4.0752 | 3.957 | 3.828 | 3.6996 | 3.4447 | 3.0225 | 2.5521 | 2.064
|  | WHITCHURCH | LW |  |  | 8.5908 | 8.5788 | 8.5506 | 8.5199 | 8.4894 | 8.459 | 8.4287 | 8.3983 | 8.365 | 8.3316 | 8.2853 | 8.205 | 8.1061 | 4.677 | 7.8967 | 7.8792 | 7.8378 | 7.7929 | 7.7483 | 7.704 | 7.66 | 7.6161 | 7.5684 | 7.5207 | 7.4254 | 7.2705 | 7.2286 | 4.7359 | 4.7186 | 4.6723 | 4.562 | 4.4423 | 4.3238 | 4.2063 | 4.0897 | 3.974 | 3.8484 | 3.7236 | 3.4753 | 3.0859 | 2.6642 | 2.2223
|  | WHITCHURCH | ST |  |  | 8.5957 | 8.5905 | 8.5791 | 8.562 | 8.5415 | 8.531 | 8.5205 | 8.5101 | 8.4988 | 8.4876 | 8.4658 | 8.4058 | 8.3408 | 8.2842 | 7.9038 | 7.8961 | 7.8794 | 7.8543 | 7.824 | 7.8086 | 7.7934 | 7.7783 | 7.7619 | 7.7458 | 7.7143 | 7.6292 | 7.539 | 7.4449 | 4.7372 | 4.7168 | 4.6722 | 4.6051 | 4.5243 | 4.4834 | 4.443 | 4.403 | 4.3598 | 4.3171 | 4.2341 | 4.0122 | 3.7804 | 3.543
|  | WHITCHURCH | FS |  |  | 8.5984 | 8.5976 | 8.5966 | 8.5915 | 8.5854 | 8.5817 | 8.578 | 8.5733 | 8.5687 | 8.5641 | 8.5552 | 8.5319 | 8.5075 | 8.4831 | 7.9077 | 7.9066 | 7.9052 | 7.8977 | 7.8888 | 7.8835 | 7.8781 | 7.8713 | 7.8646 | 7.858 | 7.8451 | 7.8119 | 7.7775 | 7.7435 | 4.7476 | 4.7447 | 4.7412 | 4.7213 | 4.6976 | 4.6834 | 4.6694 | 4.6513 | 4.6336 | 4.6161 | 4.5821 | 4.4951 | 4.406 | 4.3181
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY | MINIMUM HEADROOM | SU 52936 08794 | NO | 39.6582 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 36.4859 | 35.8207 | 35.6428 | 35.5239 | 35.4798 | 35.4339 | 35.3878 | 35.3438 | 35.3011 | 35.2617 | 35.1861 | 35.0818 | 34.9863 | 26.6903 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.3883
|  | WHITELEY | CT |  |  | 39.6582 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 36.5026 | 35.8587 | 35.6774 | 35.5724 | 35.5059 | 35.4661 | 35.4256 | 35.3858 | 35.3461 | 35.3084 | 35.2378 | 35.1296 | 35.0309 | 34.9667 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
|  | WHITELEY | LW |  |  | 39.6582 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 36.4859 | 35.8207 | 35.6428 | 35.5239 | 35.4798 | 35.4339 | 35.3878 | 35.3438 | 35.3011 | 35.2617 | 35.1861 | 35.0818 | 34.9863 | 26.6903 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.3883
|  | WHITELEY | ST |  |  | 39.6663 | 39.6555 | 39.6386 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 36.5658 | 36.4586 | 36.2921 | 36.121 | 35.9236 | 35.7822 | 35.6809 | 35.6207 | 35.561 | 35.5198 | 35.4839 | 35.4172 | 35.3601 | 35.3039 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
|  | WHITELEY | FS |  |  | 39.6722 | 39.6676 | 39.663 | 39.6547 | 39.6456 | 39.638 | 39.6304 | 39.6223 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 39.6203 | 36.6241 | 36.5787 | 36.5332 | 36.451 | 36.3615 | 36.2861 | 36.2279 | 36.1676 | 36.1111 | 36.0594 | 35.9603 | 35.7615 | 35.6669 | 35.605 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITELEY WOOD | MINIMUM HEADROOM | SU 72812 69667 | NO | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 34.4795 | 34.4391 | 34.3651 | 34.3451 | 34.3245 | 34.3035 | 34.2836 | 34.2641 | 34.2433 | 34.2226 | 34.1823 | 34.1443 | 34.1443 | 25.7326 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 26.644
|  | WHITELEY WOOD | CT |  |  | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 34.4795 | 34.4391 | 34.3651 | 34.3451 | 34.3245 | 34.3035 | 34.2836 | 34.2641 | 34.2433 | 34.2226 | 34.1823 | 34.1443 | 34.1443 | 25.7585 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 26.6695
|  | WHITELEY WOOD | LW |  |  | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 34.4798 | 34.4398 | 34.3656 | 34.3459 | 34.3254 | 34.3045 | 34.2847 | 34.2656 | 34.2451 | 34.225 | 34.1854 | 34.1443 | 34.1443 | 25.7326 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 26.644
|  | WHITELEY WOOD | ST |  |  | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 34.4993 | 34.4752 | 34.4324 | 34.3695 | 34.3541 | 34.346 | 34.3385 | 34.3312 | 34.3235 | 34.3158 | 34.3011 | 34.2626 | 34.2227 | 34.1831 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006
|  | WHITELEY WOOD | FS |  |  | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 39.0159 | 34.5166 | 34.5112 | 34.5046 | 34.4819 | 34.4609 | 34.4459 | 34.4323 | 34.4161 | 34.4001 | 34.3846 | 34.3668 | 34.3516 | 34.3358 | 34.32 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006 | 36.3006
MINETY GSP | CIRENCESTER BSP | WHITEWAY | MINIMUM HEADROOM | SP 02076 03059 | YES | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 26.6172 | 26.5899 | 26.5151 | 26.4273 | 26.3431 | 26.2607 | 26.1728 | 26.0868 | 25.9991 | 25.9109 | 25.732 | 24.9876 | 24.1886 | 23.3892 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649
|  | WHITEWAY | CT |  |  | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 26.6172 | 26.5899 | 26.5151 | 26.4273 | 26.3431 | 26.2607 | 26.1728 | 26.0868 | 25.9991 | 25.9115 | 25.7481 | 25.0308 | 24.2502 | 23.4655 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649
|  | WHITEWAY | LW |  |  | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 26.6173 | 26.591 | 26.5174 | 26.4294 | 26.3446 | 26.2614 | 26.1747 | 26.0908 | 26.004 | 25.9109 | 25.732 | 24.9876 | 24.1886 | 23.3892 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649
|  | WHITEWAY | ST |  |  | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 26.6942 | 26.6108 | 26.5706 | 26.5091 | 26.4396 | 26.3668 | 26.2909 | 26.2166 | 26.1397 | 26.0631 | 25.9195 | 25.4599 | 24.98 | 24.5063 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649
|  | WHITEWAY | FS |  |  | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 34.2303 | 32.4637 | 32.4613 | 26.6264 | 26.6092 | 26.5918 | 26.5674 | 26.5426 | 26.513 | 26.4847 | 26.4557 | 26.4 | 26.2306 | 26.0417 | 25.8442 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649 | 32.3649
BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD | MINIMUM HEADROOM | SU 69235 73304 | NO | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 39.9178 | 39.8992 | 39.861 | 39.8243 | 39.7893 | 39.7538 | 39.7174 | 39.6812 | 39.6431 | 39.6059 | 39.5333 | 39.3937 | 39.3937 | 39.3937 | 44.1851 | 44.1806 | 44.1713 | 44.1625 | 44.154 | 44.1454 | 44.1366 | 44.1278 | 44.1186 | 44.1095 | 44.092 | 44.0389 | 44.0389 | 44.0389
|  | WILSON ROAD | CT |  |  | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 39.9178 | 39.8992 | 39.861 | 39.8243 | 39.7893 | 39.7538 | 39.7174 | 39.6812 | 39.6431 | 39.6059 | 39.5333 | 39.3937 | 39.3937 | 39.3937 | 44.1851 | 44.1806 | 44.1713 | 44.1625 | 44.154 | 44.1454 | 44.1366 | 44.1278 | 44.1186 | 44.1095 | 44.092 | 44.0389 | 44.0389 | 44.0389
|  | WILSON ROAD | LW |  |  | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 39.9188 | 39.901 | 39.8661 | 39.8334 | 39.8028 | 39.7725 | 39.7425 | 39.7127 | 39.6805 | 39.6485 | 39.5855 | 39.3937 | 39.3937 | 39.3937 | 44.1853 | 44.181 | 44.1726 | 44.1646 | 44.1572 | 44.1499 | 44.1426 | 44.1354 | 44.1276 | 44.1199 | 44.1046 | 44.0389 | 44.0389 | 44.0389
|  | WILSON ROAD | ST |  |  | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 39.9244 | 39.9142 | 39.8958 | 39.8731 | 39.8468 | 39.8038 | 39.7606 | 39.7179 | 39.6724 | 39.6281 | 39.5421 | 39.3937 | 39.3937 | 39.3937 | 44.1867 | 44.1842 | 44.1798 | 44.1743 | 44.1679 | 44.1575 | 44.147 | 44.1367 | 44.1257 | 44.1149 | 44.0941 | 44.0401 | 44.0389 | 44.0389
|  | WILSON ROAD | FS |  |  | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 46.655 | 39.9297 | 39.9266 | 39.9232 | 39.9175 | 39.9113 | 39.8961 | 39.8811 | 39.8619 | 39.8431 | 39.8245 | 39.7885 | 39.6989 | 39.6083 | 39.5196 | 44.188 | 44.1872 | 44.1864 | 44.185 | 44.1835 | 44.1798 | 44.1762 | 44.1716 | 44.167 | 44.1625 | 44.1538 | 44.1321 | 44.1101 | 44.0886
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE | MINIMUM HEADROOM | SZ 02014 99989 | YES | -1.9578 | -2.083 | 11.9787 | 11.8071 | 11.6508 | 11.482 | 11.3002 | 11.1166 | 10.9764 | 10.8317 | 10.4617 | 8.9417 | 7.6101 | 6.3065 | -3.0816 | -3.2281 | 10.7991 | 10.5963 | 10.4101 | 10.194 | 9.9485 | 9.6957 | 9.4873 | 9.2814 | 8.8074 | 7.2057 | 5.6339 | 4.0926 | -3.0429 | -3.1784 | 10.8656 | 10.6779 | 10.5057 | 10.3058 | 10.0787 | 9.8449 | 9.6521 | 9.4616 | 9.0232 | 7.5416 | 6.0877 | 4.6619
|  | WIMBORNE | CT |  |  | -1.9578 | -2.083 | 11.9787 | 11.8071 | 11.6508 | 11.482 | 11.3002 | 11.1166 | 10.9764 | 10.8317 | 10.4617 | 8.9417 | 7.6101 | 6.3065 | -3.0816 | -3.2204 | 10.8056 | 10.6016 | 10.4101 | 10.194 | 9.9485 | 9.6957 | 9.4873 | 9.2814 | 8.8074 | 7.2057 | 5.6667 | 4.1291 | -3.0429 | -3.1713 | 10.8715 | 10.6828 | 10.5057 | 10.3058 | 10.0787 | 9.8449 | 9.6521 | 9.4616 | 9.0232 | 7.5416 | 6.118 | 4.6957
|  | WIMBORNE | LW |  |  | -1.9578 | -2.083 | 11.9787 | 11.8071 | 11.6508 | 11.482 | 11.3002 | 11.1166 | 10.9764 | 10.8317 | 10.4617 | 8.9417 | 7.6101 | 6.3065 | -3.0801 | -3.2281 | 10.7991 | 10.5963 | 10.4115 | 10.2119 | 9.997 | 9.7799 | 9.6141 | 9.443 | 9.0056 | 7.2083 | 5.6339 | 4.0926 | -3.0415 | -3.1784 | 10.8656 | 10.6779 | 10.507 | 10.3224 | 10.1235 | 9.9227 | 9.7694 | 9.6111 | 9.2065 | 7.544 | 6.0877 | 4.6619
|  | WIMBORNE | ST |  |  | -1.9236 | -1.9926 | 12.1622 | 12.0702 | 11.9764 | 11.785 | 11.5782 | 11.3687 | 11.1774 | 10.9879 | 10.572 | 9.6803 | 8.866 | 8.0567 | -3.0397 | -3.1213 | 11.0162 | 10.9074 | 10.7965 | 10.5701 | 10.3257 | 10.078 | 9.8518 | 9.6277 | 9.1359 | 8.0817 | 7.1188 | 6.162 | -3.0041 | -3.0796 | 11.0664 | 10.9657 | 10.8631 | 10.6537 | 10.4276 | 10.1985 | 9.9892 | 9.782 | 9.3271 | 8.3519 | 7.4612 | 6.5761
|  | WIMBORNE | FS |  |  | -1.898 | -1.9351 | 12.2736 | 12.2349 | 12.2001 | 12.1304 | 12.0594 | 11.9776 | 11.9066 | 11.8349 | 11.6747 | 11.2931 | 10.956 | 10.6451 | -3.0094 | -3.0533 | 11.1478 | 11.1021 | 11.0609 | 10.9786 | 10.8946 | 10.7979 | 10.714 | 10.6292 | 10.4397 | 9.9886 | 9.59 | 9.2223 | -2.9761 | -3.0166 | 11.1881 | 11.1458 | 11.1077 | 11.0316 | 10.9539 | 10.8644 | 10.7868 | 10.7083 | 10.5331 | 10.1158 | 9.747 | 9.407
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES | MINIMUM HEADROOM | SU 03028 12678 | YES | 5.7494 | 5.7487 | 5.7475 | 5.746 | 5.7443 | 5.7422 | 1.4985 | 1.4939 | 1.4888 | 1.4832 | 1.4705 | 1.4153 | 1.3455 | 1.2693 | 4.4177 | 4.4166 | 4.4148 | 4.4131 | 4.4112 | 4.4091 | 4.4069 | 4.4045 | 4.4017 | 4.3986 | 4.3912 | 4.3686 | 4.3387 | 4.3026 | 3.8011 | 3.7989 | 3.7956 | 3.7923 | 3.7886 | 3.7846 | 3.7804 | 3.7759 | 3.7704 | 3.7644 | 3.7503 | 3.7069 | 3.6495 | 3.5803
|  | WIMBORNE ST GILES | CT |  |  | 5.7494 | 5.7487 | 5.7475 | 5.746 | 5.7443 | 5.7422 | 1.4985 | 1.4939 | 1.4888 | 1.4832 | 1.4705 | 1.4153 | 1.3455 | 1.2693 | 4.4177 | 4.4166 | 4.4148 | 4.4131 | 4.4112 | 4.4091 | 4.4069 | 4.4045 | 4.4017 | 4.3986 | 4.3912 | 4.3686 | 4.3387 | 4.3026 | 3.8011 | 3.7989 | 3.7956 | 3.7923 | 3.7886 | 3.7846 | 3.7804 | 3.7759 | 3.7704 | 3.7644 | 3.7503 | 3.7069 | 3.6495 | 3.5803
|  | WIMBORNE ST GILES | LW |  |  | 5.7494 | 5.7487 | 5.7475 | 5.746 | 5.7443 | 5.7422 | 1.4985 | 1.4939 | 1.4888 | 1.4832 | 1.4705 | 1.4153 | 1.3455 | 1.2693 | 4.4188 | 4.4184 | 4.4179 | 4.4173 | 4.4166 | 4.4156 | 4.4145 | 4.4132 | 4.4116 | 4.4098 | 4.4054 | 4.3899 | 4.3668 | 4.3403 | 3.8032 | 3.8025 | 3.8016 | 3.8004 | 3.7989 | 3.7971 | 3.7949 | 3.7924 | 3.7894 | 3.7859 | 3.7775 | 3.7477 | 3.7035 | 3.6525
|  | WIMBORNE ST GILES | ST |  |  | 5.7501 | 5.7498 | 5.7494 | 5.7488 | 5.7481 | 5.7471 | 5.746 | 5.7448 | 5.7436 | 1.4973 | 1.4906 | 1.4714 | 1.4491 | 1.4242 | 4.4191 | 4.419 | 4.4188 | 4.4186 | 4.4184 | 4.4181 | 4.4177 | 4.4173 | 4.417 | 4.4165 | 4.4156 | 4.4119 | 4.4064 | 4.3996 | 3.8039 | 3.8036 | 3.8033 | 3.8029 | 3.8025 | 3.8019 | 3.8012 | 3.8004 | 3.7997 | 3.7989 | 3.7971 | 3.79 | 3.7795 | 3.7663
|  | WIMBORNE ST GILES | FS |  |  | 5.7502 | 5.75 | 5.7499 | 5.7496 | 5.7492 | 5.7488 | 5.7482 | 5.7477 | 5.7471 | 5.7464 | 5.7452 | 1.4956 | 1.4855 | 1.4751 | 4.4192 | 4.4191 | 4.419 | 4.4189 | 4.4187 | 4.4186 | 4.4184 | 4.4182 | 4.4181 | 4.4179 | 4.4175 | 4.4159 | 4.4138 | 4.4115 | 3.8039 | 3.8038 | 3.8036 | 3.8034 | 3.8031 | 3.8028 | 3.8025 | 3.8021 | 3.8018 | 3.8014 | 3.8007 | 3.7977 | 3.7937 | 3.7892
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON | MINIMUM HEADROOM | ST 71286 27802 | YES | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.5701 | 24.5701 | 24.5701 | 26.1841 | 26.1746 | 26.157 | 26.1361 | 26.113 | 26.0876 | 26.0725 | 26.0509 | 26.0196 | 25.9882 | 25.9298 | 25.7354 | 25.6161 | 25.498 | 29.0304 | 29.0274 | 29.0219 | 29.0153 | 29.008 | 29 | 28.9953 | 28.9884 | 28.9786 | 28.9687 | 28.9502 | 28.8097 | 28.7383 | 28.6676
|  | WINCANTON | CT |  |  | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.5701 | 24.5701 | 24.5701 | 26.1841 | 26.1756 | 26.1593 | 26.1403 | 26.1194 | 26.096 | 26.0809 | 26.0677 | 26.0529 | 26.0377 | 26.0116 | 25.7381 | 25.6202 | 25.5028 | 29.0304 | 29.0277 | 29.0226 | 29.0166 | 29.01 | 29.0027 | 28.9979 | 28.9937 | 28.9891 | 28.9843 | 28.9761 | 28.8113 | 28.7408 | 28.6705
|  | WINCANTON | LW |  |  | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.5701 | 24.5701 | 24.5701 | 26.1841 | 26.1746 | 26.157 | 26.1361 | 26.113 | 26.0876 | 26.0725 | 26.0617 | 26.0504 | 26.0392 | 26.0174 | 25.7354 | 25.6161 | 25.498 | 29.0304 | 29.0274 | 29.0219 | 29.0153 | 29.008 | 29 | 28.9953 | 28.9918 | 28.9883 | 28.9847 | 28.9779 | 28.8097 | 28.7383 | 28.6676
|  | WINCANTON | ST |  |  | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6189 | 24.6189 | 24.6189 | 26.1853 | 26.1802 | 26.1714 | 26.1598 | 26.1459 | 26.1099 | 26.0796 | 26.0509 | 26.0196 | 25.9882 | 25.9298 | 25.761 | 25.6802 | 25.5998 | 29.0308 | 29.0292 | 29.0264 | 29.0228 | 29.0184 | 29.007 | 28.9975 | 28.9884 | 28.9786 | 28.9687 | 28.9502 | 28.854 | 28.8057 | 28.7576
|  | WINCANTON | FS |  |  | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 24.6676 | 26.2171 | 26.1836 | 26.1802 | 26.1755 | 26.1701 | 26.158 | 26.1486 | 26.1377 | 26.127 | 26.1164 | 26.096 | 26.0459 | 25.9942 | 25.9426 | 29.0408 | 29.0302 | 29.0292 | 29.0277 | 29.026 | 29.0222 | 29.0192 | 29.0158 | 29.0124 | 29.0091 | 29.0026 | 28.9869 | 28.9706 | 28.9543
COWLEY GSP | WITNEY BSP | WINDRUSH PARK | MINIMUM HEADROOM | SP 33366 09758 | YES | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 36.4373 | 36.4118 | 36.3515 | 36.286 | 36.2198 | 36.1538 | 36.0881 | 36.0229 | 35.9525 | 35.8833 | 35.7881 | 35.7564 | 35.7232 | 35.6893 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777
|  | WINDRUSH PARK | CT |  |  | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 36.4416 | 36.4202 | 36.3694 | 36.3144 | 36.2568 | 36.1991 | 36.1435 | 36.0881 | 36.0281 | 35.9687 | 35.8368 | 35.7663 | 35.7348 | 35.7026 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777
|  | WINDRUSH PARK | LW |  |  | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 36.4373 | 36.4118 | 36.3515 | 36.286 | 36.2198 | 36.1538 | 36.0881 | 36.0229 | 35.9525 | 35.8833 | 35.7881 | 35.7564 | 35.7232 | 35.6893 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777
|  | WINDRUSH PARK | ST |  |  | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 36.7333 | 36.4473 | 36.4171 | 36.3722 | 36.3161 | 36.2585 | 36.2026 | 36.1473 | 36.0872 | 36.0282 | 35.9021 | 35.7793 | 35.7592 | 35.739 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777
|  | WINDRUSH PARK | FS |  |  | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 39.5759 | 36.7546 | 36.5881 | 36.4764 | 36.4649 | 36.4521 | 36.4335 | 36.415 | 36.3912 | 36.3676 | 36.3448 | 36.298 | 36.1612 | 36.0064 | 35.8454 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777 | 36.4777
COWLEY GSP | DRAYTON BSP | WINSMORE LANE | MINIMUM HEADROOM | SU 49513 96982 | NO | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 18.7724 | 18.4499 | 18.1305 | 17.8142 | 17.476 | 17.1132 | 16.3471 | 15.1035 | 13.7544 | 12.3838 | -12.0189 | -12.1961 | -12.6161 | -13.0713 | -13.5237 | -13.9726 | -14.417 | -14.8573 | -15.328 | -15.8329 | -16.8991 | -18.6298 | -20.5074 | -22.415 | 12.6949 | 12.5217 | 12.1109 | 11.6658 | 11.2234 | 10.7844 | 10.3498 | 9.9192 | 9.459 | 8.9652 | 7.9225 | 6.2301 | 4.394 | 2.5285
|  | WINSMORE LANE | CT |  |  | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 18.7724 | 18.4499 | 18.1305 | 17.8142 | 17.476 | 17.1132 | 16.3471 | 15.1035 | 13.7544 | 12.3838 | -12.0153 | -12.1868 | -12.5942 | -13.0356 | -13.4742 | -13.9096 | -14.3408 | -14.7684 | -15.2267 | -15.6794 | -16.6139 | -18.3144 | -20.1672 | -22.0249 | 12.6985 | 12.5307 | 12.1324 | 11.7007 | 11.2718 | 10.846 | 10.4244 | 10.0062 | 9.558 | 9.1153 | 8.2015 | 6.5385 | 4.7267 | 2.91
|  | WINSMORE LANE | LW |  |  | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 18.7724 | 18.4499 | 18.1305 | 17.8142 | 17.476 | 17.1132 | 16.3471 | 15.1035 | 13.7544 | 12.3838 | -12.0189 | -12.1961 | -12.6161 | -13.0713 | -13.5237 | -13.9726 | -14.417 | -14.8573 | -15.328 | -15.8329 | -16.8991 | -18.6298 | -20.5074 | -22.415 | 12.6949 | 12.5217 | 12.1109 | 11.6658 | 11.2234 | 10.7844 | 10.3498 | 9.9192 | 9.459 | 8.9652 | 7.9225 | 6.2301 | 4.394 | 2.5285
|  | WINSMORE LANE | ST |  |  | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 18.9048 | 18.7919 | 18.6714 | 18.5533 | 18.3004 | 17.5274 | 16.7172 | 15.9164 | -11.6549 | -12.0652 | -12.2865 | -12.6193 | -13.0206 | -13.181 | -13.3395 | -13.4965 | -13.6643 | -13.8286 | -14.1806 | -15.2564 | -16.384 | -17.4985 | 13.0509 | 12.6496 | 12.4332 | 12.1078 | 11.7153 | 11.5585 | 11.4035 | 11.25 | 11.0859 | 10.9252 | 10.581 | 9.5289 | 8.4262 | 7.3364
|  | WINSMORE LANE | FS |  |  | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 80.5555 | 18.8664 | 18.5326 | -11.6 | -11.8751 | -11.9343 | -12.0096 | -12.0992 | -12.1555 | -12.2113 | -12.2828 | -12.3524 | -12.4204 | -12.5585 | -12.95 | -13.3928 | -13.8575 | 13.1046 | 12.8356 | 12.7777 | 12.7041 | 12.6164 | 12.5613 | 12.5068 | 12.4369 | 12.3688 | 12.3023 | 12.1673 | 11.7844 | 11.3514 | 10.897
MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON | MINIMUM HEADROOM | SY 84631 98138 | YES | 42.3353 | 42.3307 | 42.3246 | 42.3167 | 42.3069 | 42.295 | 42.2806 | 42.2637 | 42.2447 | 42.2228 | 42.17 | 41.5604 | 41.2929 | 40.9507 | 36.702 | 36.6895 | 36.6686 | 36.6453 | 36.6198 | 36.5923 | 36.5631 | 36.5323 | 36.4978 | 36.4601 | 36.3752 | 35.7435 | 35.3748 | 34.9924 | 35.9237 | 35.9093 | 35.8879 | 35.8645 | 35.8391 | 35.8117 | 35.7822 | 35.7507 | 35.7148 | 35.6748 | 35.5818 | 6.678 | 5.8203 | 4.8825
|  | WINTERBOURNE KINGSTON | CT |  |  | 42.3353 | 42.3307 | 42.3246 | 42.3167 | 42.3069 | 42.295 | 42.2806 | 42.2637 | 42.2447 | 42.2228 | 42.17 | 41.5604 | 41.2929 | 40.9507 | 36.702 | 36.6895 | 36.6686 | 36.6453 | 36.6198 | 36.5923 | 36.5631 | 36.5323 | 36.4978 | 36.4601 | 36.3752 | 35.7435 | 35.3748 | 34.9924 | 35.9237 | 35.9093 | 35.8879 | 35.8645 | 35.8391 | 35.8117 | 35.7822 | 35.7507 | 35.7148 | 35.6748 | 35.5818 | 6.678 | 5.8203 | 4.8825
|  | WINTERBOURNE KINGSTON | LW |  |  | 42.3353 | 42.3307 | 42.3246 | 42.3167 | 42.3069 | 42.295 | 42.2806 | 42.2637 | 42.2447 | 42.2228 | 42.17 | 41.5604 | 41.2929 | 40.9507 | 36.7116 | 36.7062 | 36.6963 | 36.684 | 36.6695 | 36.653 | 36.6345 | 36.6139 | 36.5914 | 36.5667 | 36.5106 | 35.967 | 35.6696 | 35.3764 | 35.937 | 35.9325 | 35.9266 | 35.9189 | 35.9093 | 35.8976 | 35.8836 | 35.867 | 35.8484 | 35.827 | 35.7754 | 7.0092 | 6.2978 | 5.5093
|  | WINTERBOURNE KINGSTON | ST |  |  | 42.3396 | 42.338 | 42.3359 | 42.3334 | 42.3305 | 42.3265 | 42.3219 | 42.3169 | 42.3116 | 42.306 | 42.2936 | 42.0374 | 41.9671 | 41.8815 | 36.7154 | 36.7133 | 36.7093 | 36.7036 | 36.6965 | 36.6799 | 36.663 | 36.6458 | 36.6273 | 36.6086 | 36.5707 | 36.3175 | 36.1978 | 36.0678 | 35.9413 | 35.9397 | 35.9376 | 35.9352 | 35.9324 | 35.9284 | 35.924 | 35.9191 | 35.9139 | 35.9084 | 35.8963 | 35.6456 | 35.5768 | 6.88
|  | WINTERBOURNE KINGSTON | FS |  |  | 42.3402 | 42.3391 | 42.338 | 42.3363 | 42.3345 | 42.3325 | 42.3305 | 42.3283 | 42.326 | 42.3236 | 42.3184 | 42.2989 | 42.2744 | 42.2478 | 36.7163 | 36.7154 | 36.7144 | 36.7122 | 36.7095 | 36.7037 | 36.6977 | 36.6906 | 36.6833 | 36.6761 | 36.6614 | 36.6207 | 36.5774 | 36.5334 | 35.9418 | 35.9408 | 35.9397 | 35.938 | 35.9363 | 35.9343 | 35.9323 | 35.9302 | 35.9279 | 35.9256 | 35.9205 | 35.9014 | 35.8775 | 35.8514
MANNINGTON GSP | REDHILL BSP | WINTON | MINIMUM HEADROOM | SZ 09349 93822 | YES | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 18.983 | 17.6753 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 18.4129
|  | WINTON | CT |  |  | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 18.3272 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871
|  | WINTON | LW |  |  | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 18.983 | 17.6753 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 18.4129
|  | WINTON | ST |  |  | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 18.4204 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871
|  | WINTON | FS |  |  | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 34.2697 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 28.5294 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871 | 30.1871
COWLEY GSP | WITNEY BSP | WITNEY TOWN | MINIMUM HEADROOM | SP 35844 09625 | YES | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 19.8903 | 24.2903 | 24.2407 | 24.1236 | 23.9782 | 23.8422 | 23.7374 | 23.6808 | 23.6808 | 23.6808 | 23.6808 | 23.6808 | 18.9052 | 17.1067 | 15.2829 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 19.2353 | 17.38 | 15.4986
|  | WITNEY TOWN | CT |  |  | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 19.8903 | 24.2903 | 24.2407 | 24.1236 | 23.9782 | 23.8422 | 23.7374 | 23.6808 | 23.6808 | 23.6808 | 23.6808 | 23.6808 | 18.9052 | 17.1067 | 15.2829 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 19.2353 | 17.38 | 15.4986
|  | WITNEY TOWN | LW |  |  | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 19.8903 | 24.2945 | 24.2494 | 24.1447 | 24.0093 | 23.8633 | 23.7605 | 23.6808 | 23.6808 | 23.6808 | 23.6808 | 23.6808 | 19.0299 | 17.1826 | 15.3024 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 19.364 | 17.4583 | 15.5187
|  | WITNEY TOWN | ST |  |  | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 24.3092 | 24.2883 | 24.2429 | 24.1697 | 24.0702 | 23.9041 | 23.8008 | 23.6972 | 23.6808 | 23.6808 | 23.6808 | 23.6808 | 18.8901 | 17.7421 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 19.2198 | 18.0354
|  | WITNEY TOWN | FS |  |  | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 28.4435 | 24.3174 | 24.3107 | 24.2986 | 24.2714 | 24.2351 | 24.1746 | 24.112 | 24.0367 | 23.9614 | 23.8944 | 23.8297 | 23.6808 | 23.6808 | 23.6808 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517 | 24.4517
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM | MINIMUM HEADROOM | SU 79589 67665 | YES | 28.1976 | 28.0356 | 27.6708 | 27.2691 | 26.8546 | 26.4306 | 25.9967 | 25.5551 | 25.0809 | 24.6042 | 23.6347 | 22.6889 | 21.8488 | 21.0117 | 26.5483 | 26.3891 | 26.0285 | 25.6314 | 25.2216 | 24.8024 | 24.3735 | 23.7498 | 22.977 | 22.2002 | 20.6201 | 18.9708 | 17.5291 | 16.1171 | 26.4507 | 26.1891 | 25.5965 | 24.944 | 24.2705 | 23.5815 | 22.8767 | 22.1592 | 21.3888 | 20.6144 | 19.0392 | 17.3949 | 15.9575 | 14.5498
|  | WOKINGHAM | CT |  |  | 28.1976 | 28.0356 | 27.6708 | 27.2691 | 26.8546 | 26.4306 | 25.9967 | 25.5551 | 25.0809 | 24.6042 | 23.6347 | 22.6889 | 21.8488 | 21.0117 | 26.5483 | 26.3906 | 26.0311 | 25.6371 | 25.2333 | 24.821 | 24.401 | 23.8055 | 23.0375 | 22.2583 | 20.673 | 18.9708 | 17.5291 | 16.1171 | 26.4507 | 26.1915 | 25.6008 | 24.9532 | 24.2897 | 23.6121 | 22.922 | 22.2148 | 21.4491 | 20.6723 | 19.0919 | 17.3949 | 15.9575 | 14.5498
|  | WOKINGHAM | LW |  |  | 28.1976 | 28.0356 | 27.6708 | 27.2691 | 26.8546 | 26.4306 | 25.9967 | 25.5551 | 25.0809 | 24.6042 | 23.6347 | 22.6889 | 21.8488 | 21.0117 | 26.5493 | 26.3891 | 26.0285 | 25.6314 | 25.2216 | 24.8024 | 24.3735 | 23.7498 | 22.977 | 22.2002 | 20.6201 | 19.0789 | 17.7097 | 16.3457 | 26.4523 | 26.1891 | 25.5965 | 24.944 | 24.2705 | 23.5815 | 22.8767 | 22.1592 | 21.3888 | 20.6144 | 19.0392 | 17.5026 | 16.1376 | 14.7777
|  | WOKINGHAM | ST |  |  | 28.3175 | 28.1881 | 28.0497 | 27.8478 | 27.6013 | 27.4736 | 27.3394 | 27.1968 | 27.0394 | 26.874 | 26.5221 | 25.8811 | 25.3836 | 24.8996 | 26.6679 | 26.54 | 26.4031 | 26.2035 | 25.9598 | 25.8336 | 25.7009 | 25.5599 | 25.4043 | 25.2408 | 24.8929 | 24.2591 | 23.4702 | 22.6815 | 26.6473 | 26.437 | 26.2122 | 25.884 | 25.4836 | 25.2762 | 25.0581 | 24.8264 | 24.5707 | 24.302 | 23.7303 | 22.6888 | 21.8805 | 21.0942
|  | WOKINGHAM | FS |  |  | 28.3439 | 28.3267 | 28.3038 | 28.2324 | 28.1468 | 28.0977 | 28.0465 | 27.9853 | 27.922 | 27.8565 | 27.7193 | 27.457 | 27.2464 | 27.0533 | 26.694 | 26.6769 | 26.6543 | 26.5837 | 26.4991 | 26.4505 | 26.3999 | 26.3394 | 26.2769 | 26.2122 | 26.0764 | 25.8171 | 25.609 | 25.4181 | 26.6901 | 26.6621 | 26.6249 | 26.5089 | 26.3698 | 26.2901 | 26.2069 | 26.1075 | 26.0046 | 25.8983 | 25.6752 | 25.2491 | 24.9071 | 24.5934
BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE | MINIMUM HEADROOM | SU 64425 81624 | NO | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 12.9548 | 12.9507 | 12.9407 | 12.9299 | 12.9191 | 12.9082 | 12.8975 | 12.8868 | 12.8752 | 12.8636 | 12.8408 | 12.7625 | 12.6704 | 12.5767 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481
|  | WOODCOTE | CT |  |  | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 12.9548 | 12.9507 | 12.9407 | 12.9299 | 12.9191 | 12.9082 | 12.8975 | 12.8868 | 12.8752 | 12.8636 | 12.8408 | 12.7625 | 12.6704 | 12.5767 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481
|  | WOODCOTE | LW |  |  | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 12.9569 | 12.9558 | 12.9533 | 12.9504 | 12.9474 | 12.9444 | 12.9412 | 12.9381 | 12.9347 | 12.9313 | 12.9247 | 12.8529 | 12.7641 | 12.6733 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481
|  | WOODCOTE | ST |  |  | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 12.9573 | 12.9568 | 12.9558 | 12.9541 | 12.9521 | 12.9428 | 12.9336 | 12.9245 | 12.9146 | 12.9048 | 12.8857 | 12.8402 | 12.7873 | 12.7333 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481
|  | WOODCOTE | FS |  |  | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 14.2541 | 12.9576 | 12.9575 | 12.9574 | 12.9569 | 12.9563 | 12.9531 | 12.9499 | 12.9458 | 12.9418 | 12.9378 | 12.9302 | 12.9122 | 12.8941 | 12.8734 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481 | 13.5481
NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE | MINIMUM HEADROOM | SU 43733 15470 | NO | 22.8954 | 22.8954 | 22.8954 | 22.6748 | 22.6528 | 22.6306 | 22.6072 | 22.565 | 22.5199 | 22.4754 | 22.385 | 22.0149 | 21.5599 | 21.1097 | 21.7392 | 21.7292 | 21.7081 | 21.6869 | 21.6653 | 21.3423 | 21.3193 | 21.278 | 21.2339 | 21.1903 | 21.1017 | 20.6648 | 20.1261 | 19.5933 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.3437 | 21.3201 | 21.2774 | 21.2318 | 21.1869 | 21.0955 | 20.7214 | 20.194 | 19.6628
|  | WOODMILL LANE | CT |  |  | 22.8954 | 22.8954 | 22.8954 | 22.6748 | 22.6528 | 22.6306 | 22.6086 | 22.5856 | 22.5614 | 22.5372 | 22.4712 | 22.0149 | 21.5599 | 21.1097 | 21.7393 | 21.7297 | 21.709 | 21.6882 | 21.6669 | 21.3439 | 21.3219 | 21.2991 | 21.2751 | 21.2512 | 21.1992 | 20.7627 | 20.269 | 19.7744 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.3454 | 21.3227 | 21.2992 | 21.2744 | 21.2497 | 21.196 | 20.8051 | 20.3365 | 19.8434
|  | WOODMILL LANE | LW |  |  | 22.8954 | 22.8954 | 22.8954 | 22.6748 | 22.6528 | 22.6306 | 22.6086 | 22.5856 | 22.5614 | 22.5372 | 22.4712 | 22.0149 | 21.5599 | 21.1097 | 21.7392 | 21.7292 | 21.7081 | 21.6869 | 21.6653 | 21.3423 | 21.3207 | 21.2981 | 21.2744 | 21.2508 | 21.1861 | 20.6648 | 20.1261 | 19.5933 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.3437 | 21.3214 | 21.2982 | 21.2737 | 21.2493 | 21.1826 | 20.7214 | 20.194 | 19.6628
|  | WOODMILL LANE | ST |  |  | 22.8954 | 22.8954 | 22.8954 | 22.8954 | 22.8954 | 22.6493 | 22.6072 | 22.565 | 22.5199 | 22.4754 | 22.385 | 22.12 | 21.846 | 21.5745 | 21.7428 | 21.738 | 21.7288 | 21.7169 | 21.7022 | 21.662 | 21.3193 | 21.278 | 21.2339 | 21.1903 | 21.1017 | 20.7892 | 20.4648 | 20.1435 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.3201 | 21.2774 | 21.2318 | 21.1869 | 21.0955 | 20.8276 | 20.5317 | 20.2113
|  | WOODMILL LANE | FS |  |  | 22.8954 | 22.8954 | 22.8954 | 22.8954 | 22.8954 | 22.8954 | 22.8954 | 22.6763 | 22.6587 | 22.6405 | 22.6055 | 22.5052 | 22.3963 | 22.2858 | 21.7451 | 21.7437 | 21.7421 | 21.7386 | 21.7343 | 21.7202 | 21.7064 | 21.6884 | 21.6709 | 21.3519 | 21.3176 | 21.2194 | 21.1128 | 20.9854 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.5852 | 21.3537 | 21.3183 | 21.2169 | 21.1069 | 20.9952
COWLEY GSP | YARNTON BSP | WOODSTOCK | MINIMUM HEADROOM | SP 44795 17462 | YES | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 19.5631 | 19.5419 | 19.5073 | 19.4778 | 19.4638 | 19.4523 | 19.4411 | 19.4296 | 19.4178 | 19.4064 | 19.3851 | 19.3343 | 19.3343 | 19.3343 | 20.5148 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141
|  | WOODSTOCK | CT |  |  | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 19.5631 | 19.5422 | 19.5073 | 19.4778 | 19.4638 | 19.4523 | 19.4411 | 19.4296 | 19.4178 | 19.4064 | 19.3851 | 19.3343 | 19.3343 | 19.3343 | 20.5148 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141
|  | WOODSTOCK | LW |  |  | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 19.5634 | 19.5419 | 19.5088 | 19.4807 | 19.4667 | 19.4575 | 19.4497 | 19.4421 | 19.4339 | 19.4255 | 19.4059 | 19.3343 | 19.3343 | 19.3343 | 20.5149 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141
|  | WOODSTOCK | ST |  |  | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 19.5716 | 19.5597 | 19.5427 | 19.5265 | 19.5065 | 19.4797 | 19.4677 | 19.4563 | 19.4444 | 19.4329 | 19.411 | 19.354 | 19.3343 | 19.3343 | 20.5169 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141
|  | WOODSTOCK | FS |  |  | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 24.1863 | 19.5783 | 19.5721 | 19.5657 | 19.5591 | 19.5519 | 19.5416 | 19.5322 | 19.5205 | 19.509 | 19.4979 | 19.4775 | 19.4543 | 19.4306 | 19.407 | 20.5185 | 20.517 | 20.5154 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141 | 20.5141
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON | MINIMUM HEADROOM | SU 44145 11242 | YES | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775
|  | WOOLSTON | CT |  |  | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775
|  | WOOLSTON | LW |  |  | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775
|  | WOOLSTON | ST |  |  | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775
|  | WOOLSTON | FS |  |  | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 21.9827 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 22.7143 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775 | 24.1775
MINETY GSP | SWINDON BSP | WOOTTON BASSETT | MINIMUM HEADROOM | SU 07587 81123 | YES | 48.8787 | 48.8782 | 48.8775 | 48.8766 | 48.8755 | 48.8741 | 48.8725 | 48.8706 | 48.8678 | 48.8646 | 48.8568 | 48.8292 | 48.7823 | 48.7141 | 45.2866 | 45.248 | 45.1571 | 45.0582 | 44.9551 | 44.8498 | 44.7447 | 44.6533 | 44.5526 | 44.4511 | 44.2414 | 43.6076 | 43.1945 | 42.9433 | 46.9153 | 46.9136 | 46.9111 | 46.908 | 46.9047 | 46.9012 | 46.8973 | 46.8933 | 46.8873 | 46.8807 | 46.8654 | 46.8124 | 46.7318 | 46.6321
|  | WOOTTON BASSETT | CT |  |  | 48.8787 | 48.8782 | 48.8775 | 48.8766 | 48.8755 | 48.8741 | 48.8725 | 48.8706 | 48.8678 | 48.8646 | 48.8568 | 48.8292 | 48.7823 | 48.7141 | 45.2866 | 45.248 | 45.1571 | 45.0582 | 44.9551 | 44.8498 | 44.7447 | 44.6533 | 44.5526 | 44.4511 | 44.2414 | 43.6076 | 43.1945 | 42.9433 | 46.9153 | 46.9136 | 46.9111 | 46.908 | 46.9047 | 46.9012 | 46.8973 | 46.8933 | 46.8873 | 46.8807 | 46.8654 | 46.8124 | 46.7318 | 46.6321
|  | WOOTTON BASSETT | LW |  |  | 48.8787 | 48.8782 | 48.8775 | 48.8766 | 48.8755 | 48.8741 | 48.8725 | 48.8706 | 48.8678 | 48.8646 | 48.8568 | 48.8292 | 48.7823 | 48.7141 | 45.2903 | 45.2563 | 45.1761 | 45.0888 | 44.9964 | 44.9004 | 44.8009 | 44.7096 | 44.6134 | 44.5152 | 44.312 | 43.6718 | 43.2525 | 43.0116 | 46.9169 | 46.9164 | 46.9157 | 46.9148 | 46.9136 | 46.9122 | 46.9106 | 46.9086 | 46.9057 | 46.9024 | 46.8945 | 46.8661 | 46.818 | 46.748
|  | WOOTTON BASSETT | ST |  |  | 48.8792 | 48.879 | 48.8788 | 48.8785 | 48.8782 | 48.8777 | 48.8772 | 48.8766 | 48.876 | 48.8753 | 48.8737 | 48.8672 | 48.8563 | 48.8404 | 45.3005 | 45.2803 | 45.2364 | 45.17 | 45.0869 | 45.0032 | 44.918 | 44.8327 | 44.744 | 44.6663 | 44.5075 | 44.0817 | 43.6538 | 43.352 | 46.9304 | 46.9173 | 46.917 | 46.9167 | 46.9164 | 46.9159 | 46.9154 | 46.9148 | 46.9141 | 46.9134 | 46.9118 | 46.9051 | 46.8939 | 46.8776
|  | WOOTTON BASSETT | FS |  |  | 48.8793 | 48.8791 | 48.879 | 48.8788 | 48.8786 | 48.8784 | 48.8782 | 48.8779 | 48.8777 | 48.8774 | 48.8768 | 48.8746 | 48.8713 | 48.8677 | 45.3115 | 45.3093 | 45.3067 | 45.2922 | 45.2742 | 45.2483 | 45.222 | 45.1885 | 45.1543 | 45.1201 | 45.0507 | 44.8694 | 44.6961 | 44.5374 | 46.9469 | 46.9436 | 46.9397 | 46.9178 | 46.9168 | 46.9166 | 46.9164 | 46.9161 | 46.9159 | 46.9156 | 46.915 | 46.9127 | 46.9094 | 46.9056
COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD | MINIMUM HEADROOM | SU 49244 98269 | NO | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 21.5833 | 21.4884 | 21.3295 | 21.2108 | 21.1488 | 21.0819 | 21.0121 | 21.0002 | 21.0002 | 21.0002 | 21.0002 | 21.0002 | 21.0002 | 10.7106 | 24.4811 | 24.4569 | 24.4115 | 24.3556 | 24.2956 | 24.2308 | 24.1632 | 24.0975 | 24.0644 | 24.0362 | 23.9796 | 23.9602 | 23.9602 | 23.9602
|  | WOOTTON ROAD | CT |  |  | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 21.5833 | 21.4884 | 21.3295 | 21.2108 | 21.1488 | 21.0819 | 21.0121 | 21.0002 | 21.0002 | 21.0002 | 21.0002 | 21.0002 | 21.0002 | 10.7106 | 24.4811 | 24.4569 | 24.4115 | 24.3556 | 24.2956 | 24.2308 | 24.1632 | 24.0975 | 24.0644 | 24.0362 | 23.9796 | 23.9602 | 23.9602 | 23.9602
|  | WOOTTON ROAD | LW |  |  | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 21.5902 | 21.5006 | 21.3584 | 21.2253 | 21.168 | 21.1059 | 21.0392 | 21.0002 | 21.0002 | 21.0002 | 21.0002 | 21.0002 | 21.0002 | 11.0379 | 24.4829 | 24.46 | 24.4206 | 24.3697 | 24.3142 | 24.254 | 24.1894 | 24.1303 | 24.0999 | 24.071 | 24.0201 | 23.9602 | 23.9602 | 23.9602
|  | WOOTTON ROAD | ST |  |  | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 21.6868 | 21.5872 | 21.5327 | 21.4488 | 21.3599 | 21.2333 | 21.1863 | 21.1408 | 21.1081 | 21.074 | 21.0054 | 21.0002 | 21.0002 | 21.0002 | 24.5076 | 24.4821 | 24.4682 | 24.4468 | 24.4211 | 24.3774 | 24.3319 | 24.2878 | 24.2561 | 24.2231 | 24.1566 | 24.0194 | 23.9602 | 23.9602
|  | WOOTTON ROAD | FS |  |  | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 25.7057 | 21.7036 | 21.6822 | 21.6581 | 21.6152 | 21.5674 | 21.5001 | 21.4296 | 21.3661 | 21.3267 | 21.2877 | 21.2291 | 21.1617 | 21.0881 | 21.0083 | 24.5128 | 24.5064 | 24.5002 | 24.4893 | 24.4771 | 24.4599 | 24.4419 | 24.4231 | 24.4106 | 24.3983 | 24.3734 | 24.3081 | 24.2368 | 24.1595
BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM | MINIMUM HEADROOM | SU 82093 44312 | YES | 29.0219 | 29.0212 | 28.2577 | 27.9481 | 27.638 | 27.3292 | 27.0221 | 26.7182 | 26.3867 | 26.0559 | 25.4019 | 24.4296 | 23.4015 | 22.372 | 27.2288 | 26.6626 | 26.2697 | 25.8453 | 25.422 | 25.0028 | 24.5878 | 24.1778 | 23.7308 | 23.2855 | 22.4045 | 21.1875 | 19.9085 | 18.6304 | 26.5865 | 26.4206 | 26.0275 | 25.603 | 25.1794 | 24.7599 | 24.3444 | 23.9339 | 23.4861 | 23.0399 | 22.1565 | 20.9289 | 19.6353 | 18.3389
|  | WRECCLESHAM | CT |  |  | 29.0219 | 29.0212 | 28.2577 | 27.9481 | 27.638 | 27.3292 | 27.0221 | 26.7182 | 26.3867 | 26.0559 | 25.4019 | 24.4296 | 23.4015 | 22.372 | 27.2288 | 26.6626 | 26.2697 | 25.8453 | 25.422 | 25.0028 | 24.5878 | 24.1778 | 23.7308 | 23.2855 | 22.4045 | 21.1875 | 19.9085 | 18.6304 | 26.5865 | 26.4206 | 26.0275 | 25.603 | 25.1794 | 24.7599 | 24.3444 | 23.9339 | 23.4861 | 23.0399 | 22.1565 | 20.9289 | 19.6353 | 18.3389
|  | WRECCLESHAM | LW |  |  | 29.0219 | 29.0212 | 28.2577 | 27.9481 | 27.638 | 27.3292 | 27.0221 | 26.7182 | 26.3867 | 26.0559 | 25.4019 | 24.4296 | 23.4015 | 22.372 | 27.2314 | 27.2183 | 26.364 | 25.9985 | 25.6325 | 25.2683 | 24.9061 | 24.548 | 24.1573 | 23.7678 | 22.9985 | 21.8625 | 20.6675 | 19.4742 | 26.6033 | 26.4612 | 26.1234 | 25.7582 | 25.3925 | 25.0284 | 24.6663 | 24.3082 | 23.9174 | 23.5276 | 22.7573 | 21.6148 | 20.4091 | 19.2029
|  | WRECCLESHAM | ST |  |  | 29.0225 | 29.0223 | 29.022 | 28.2922 | 28.0372 | 27.9251 | 27.8144 | 27.7056 | 27.5857 | 27.4663 | 27.2318 | 26.6485 | 26.0571 | 25.4647 | 27.2362 | 27.2293 | 26.6525 | 26.4042 | 26.1029 | 25.9706 | 25.84 | 25.7118 | 25.5704 | 25.4296 | 25.1531 | 24.4667 | 23.7723 | 23.078 | 26.6521 | 26.5768 | 26.4118 | 26.1638 | 25.863 | 25.7308 | 25.6003 | 25.472 | 25.3307 | 25.1899 | 24.9135 | 24.2263 | 23.5302 | 22.8333
|  | WRECCLESHAM | FS |  |  | 29.0226 | 29.0224 | 29.0223 | 29.022 | 29.0218 | 29.0215 | 29.0212 | 29.0209 | 29.0206 | 29.0202 | 28.2911 | 28.0542 | 27.8214 | 27.597 | 27.2398 | 27.239 | 27.238 | 27.2326 | 27.2261 | 27.2218 | 26.6936 | 26.6348 | 26.576 | 26.5177 | 26.4039 | 26.1252 | 25.8518 | 25.5885 | 26.6927 | 26.6842 | 26.674 | 26.6152 | 26.5448 | 26.4986 | 26.4526 | 26.3938 | 26.3351 | 26.2767 | 26.1629 | 25.8839 | 25.6099 | 25.3458
MINETY GSP | TOOTHILL BSP | WROUGHTON | MINIMUM HEADROOM | SU 14446 81504 | YES | 41.4324 | 41.4243 | 41.4098 | 41.393 | 41.3753 | 41.3567 | 41.3388 | 41.3232 | 41.3105 | 41.2984 | 41.2745 | 41.2259 | 41.1752 | 41.1248 | 35.8045 | 35.7505 | 35.6534 | 35.5406 | 35.4223 | 35.2978 | 35.1776 | 35.0733 | 35.0136 | 34.9661 | 34.8855 | 34.7951 | 34.7674 | 34.7674 | 37.6223 | 37.6158 | 37.6043 | 37.5908 | 37.5767 | 37.5619 | 37.5476 | 37.5352 | 37.5251 | 37.5154 | 37.4964 | 37.4576 | 37.4172 | 37.377
|  | WROUGHTON | CT |  |  | 41.4324 | 41.4243 | 41.4098 | 41.393 | 41.3753 | 41.3567 | 41.3388 | 41.3232 | 41.3105 | 41.2984 | 41.2745 | 41.2259 | 41.1752 | 41.1248 | 35.8085 | 35.7634 | 35.682 | 35.5879 | 35.4886 | 35.382 | 35.2783 | 35.1844 | 35.1021 | 35.0315 | 34.9435 | 34.8285 | 34.7674 | 34.7674 | 37.6227 | 37.6174 | 37.6077 | 37.5965 | 37.5846 | 37.5719 | 37.5596 | 37.5484 | 37.5386 | 37.5288 | 37.5108 | 37.4742 | 37.4357 | 37.3971
|  | WROUGHTON | LW |  |  | 41.4324 | 41.4243 | 41.4098 | 41.393 | 41.3753 | 41.3567 | 41.3388 | 41.3232 | 41.3105 | 41.2984 | 41.2745 | 41.2259 | 41.1752 | 41.1248 | 35.8045 | 35.7505 | 35.6534 | 35.5406 | 35.4223 | 35.2978 | 35.1776 | 35.0733 | 35.0136 | 34.9661 | 34.8855 | 34.7951 | 34.7674 | 34.7674 | 37.6223 | 37.6158 | 37.6043 | 37.5908 | 37.5767 | 37.5619 | 37.5476 | 37.5352 | 37.5251 | 37.5154 | 37.4964 | 37.4576 | 37.4172 | 37.377
|  | WROUGHTON | ST |  |  | 41.4641 | 41.431 | 41.4251 | 41.4165 | 41.4063 | 41.3972 | 41.3883 | 41.3804 | 41.3738 | 41.367 | 41.355 | 41.3251 | 41.2949 | 41.265 | 36.1522 | 35.7953 | 35.7555 | 35.6985 | 35.6302 | 35.5689 | 35.5095 | 35.4567 | 35.412 | 35.3667 | 35.2862 | 35.0859 | 34.9527 | 34.8606 | 37.6475 | 37.6212 | 37.6164 | 37.6096 | 37.6015 | 37.5942 | 37.5871 | 37.5808 | 37.5755 | 37.5701 | 37.5605 | 37.5367 | 37.5126 | 37.4888
|  | WROUGHTON | FS |  |  | 41.4653 | 41.4345 | 41.4327 | 41.4292 | 41.425 | 41.4214 | 41.418 | 41.4146 | 41.4121 | 41.4095 | 41.4047 | 41.3931 | 41.3815 | 41.3697 | 36.1665 | 35.8192 | 35.807 | 35.783 | 35.7555 | 35.7312 | 35.7082 | 35.6858 | 35.6685 | 35.6516 | 35.6195 | 35.5416 | 35.4641 | 35.3846 | 37.6486 | 37.6239 | 37.6226 | 37.6197 | 37.6164 | 37.6135 | 37.6108 | 37.6081 | 37.6061 | 37.6041 | 37.6002 | 37.591 | 37.5817 | 37.5723
AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH | MINIMUM HEADROOM | SU 88582 91845 | NO | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 22.0331 | 22.0008 | 21.9383 | 21.8723 | 21.8097 | 21.7726 | 21.7361 | 21.7 | 21.6604 | 21.634 | 21.5859 | 21.4691 | 21.3463 | 16.9003 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 17.1703
|  | WYCOMBE MARSH | CT |  |  | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 22.0378 | 22.0133 | 21.9667 | 21.9184 | 21.8721 | 21.833 | 21.7978 | 21.7694 | 21.7389 | 21.7098 | 21.6548 | 21.5422 | 21.424 | 21.3072 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287
|  | WYCOMBE MARSH | LW |  |  | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 22.0331 | 22.0008 | 21.9383 | 21.8723 | 21.8097 | 21.7726 | 21.7361 | 21.7 | 21.6604 | 21.634 | 21.5859 | 21.4691 | 21.3463 | 16.9003 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 17.1703
|  | WYCOMBE MARSH | ST |  |  | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 22.0712 | 22.0243 | 21.9885 | 21.9393 | 21.8825 | 21.8456 | 21.8086 | 21.7825 | 21.7544 | 21.7274 | 21.6762 | 21.5904 | 21.5113 | 21.4328 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287
|  | WYCOMBE MARSH | FS |  |  | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 24.6621 | 22.0822 | 22.0762 | 22.0697 | 22.0545 | 22.0382 | 22.0256 | 22.013 | 21.9971 | 21.9816 | 21.9666 | 21.9373 | 21.8679 | 21.8031 | 21.7582 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287 | 22.287
LOVEDEAN GSP | WYMERING BSP | WYMERING | MINIMUM HEADROOM | SU 64974 05375 | NO | 69.6057 | 69.5977 | 69.5795 | 69.5563 | 69.5323 | 69.5092 | 69.4871 | 69.4677 | 69.4496 | 69.4496 | 69.4496 | 69.4496 | 69.4496 | 69.4496 | 64.0102 | 63.9505 | 63.8146 | 63.668 | 63.5229 | 63.3825 | 63.249 | 63.1313 | 63.005 | 62.8768 | 62.6429 | 62.2959 | 62.1756 | 62.0736 | 62.9093 | 62.8858 | 62.8324 | 62.7642 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153
|  | WYMERING | CT |  |  | 69.6057 | 69.5977 | 69.5795 | 69.5563 | 69.5323 | 69.5092 | 69.4871 | 69.4677 | 69.4496 | 69.4496 | 69.4496 | 69.4496 | 69.4496 | 69.4496 | 64.0152 | 63.9648 | 63.8487 | 63.7165 | 63.5932 | 63.4735 | 63.3601 | 63.2516 | 63.1292 | 63.0018 | 62.776 | 62.3645 | 62.2139 | 62.1092 | 62.9113 | 62.8915 | 62.8458 | 62.7877 | 62.7278 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153
|  | WYMERING | LW |  |  | 69.6057 | 69.5977 | 69.5795 | 69.5563 | 69.5323 | 69.5092 | 69.4871 | 69.4677 | 69.4496 | 69.4496 | 69.4496 | 69.4496 | 69.4496 | 69.4496 | 64.0102 | 63.9505 | 63.8146 | 63.668 | 63.5229 | 63.3825 | 63.249 | 63.1313 | 63.005 | 62.8768 | 62.6429 | 62.2959 | 62.1756 | 62.0736 | 62.9093 | 62.8858 | 62.8324 | 62.7642 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153
|  | WYMERING | ST |  |  | 69.6957 | 69.6048 | 69.5967 | 69.5841 | 69.5695 | 69.5536 | 69.5386 | 69.5241 | 69.5078 | 69.4908 | 69.4602 | 69.4496 | 69.4496 | 69.4496 | 64.6833 | 64.0037 | 63.9434 | 63.8486 | 63.7475 | 63.6517 | 63.5605 | 63.4731 | 63.3742 | 63.2714 | 63.0864 | 62.697 | 62.3561 | 62.2384 | 63.1742 | 62.9068 | 62.883 | 62.8458 | 62.8028 | 62.7563 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153 | 62.7153
|  | WYMERING | FS |  |  | 69.6975 | 69.609 | 69.6067 | 69.6016 | 69.596 | 69.5903 | 69.5849 | 69.5791 | 69.5732 | 69.5672 | 69.5561 | 69.5346 | 69.5127 | 69.4865 | 64.6964 | 64.0351 | 64.0179 | 63.9797 | 63.9382 | 63.8955 | 63.8548 | 63.8118 | 63.7704 | 63.734 | 63.6664 | 63.5364 | 63.4039 | 63.2454 | 63.1794 | 62.9191 | 62.9123 | 62.8973 | 62.881 | 62.8642 | 62.8482 | 62.8312 | 62.8139 | 62.7962 | 62.7634 | 62.7153 | 62.7153 | 62.7153
COWLEY GSP | YARNTON BSP | YARNTON | MINIMUM HEADROOM | SP 48277 12108 | NO | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 74.7279 | 74.7241 | 74.7151 | 74.7039 | 74.6918 | 74.6793 | 74.6687 | 74.6587 | 74.6476 | 74.6325 | 74.6027 | 74.5058 | 74.4055 | 74.3052 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149
|  | YARNTON | CT |  |  | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 74.7279 | 74.7243 | 74.7155 | 74.7047 | 74.6932 | 74.6814 | 74.6713 | 74.6614 | 74.6499 | 74.6384 | 74.6159 | 74.5288 | 74.4333 | 74.3378 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149
|  | YARNTON | LW |  |  | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 74.7279 | 74.7241 | 74.7151 | 74.7039 | 74.6918 | 74.6793 | 74.6687 | 74.6587 | 74.6476 | 74.6325 | 74.6027 | 74.5058 | 74.4055 | 74.3052 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149
|  | YARNTON | ST |  |  | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 74.7334 | 74.7283 | 74.7254 | 74.7207 | 74.7148 | 74.7036 | 74.6938 | 74.6841 | 74.673 | 74.662 | 74.6406 | 74.581 | 74.5185 | 74.4571 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149
|  | YARNTON | FS |  |  | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 91.6809 | 74.7339 | 74.7296 | 74.7289 | 74.7267 | 74.7241 | 74.7202 | 74.7168 | 74.7127 | 74.7085 | 74.7044 | 74.6968 | 74.6752 | 74.6508 | 74.6262 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149 | 80.9149
BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON | MINIMUM HEADROOM | SU 53699 74307 | YES | 19.5833 | 19.572 | 19.5474 | 19.5168 | 19.4856 | 19.455 | 19.4288 | 19.403 | 19.3753 | 19.3477 | 19.2932 | 19.2252 | 12.8412 | 12.3647 | 17.4745 | 17.4556 | 17.4146 | 17.3807 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 12.8387 | 18.7375 | 18.7309 | 18.7167 | 18.6989 | 18.6809 | 18.6631 | 18.648 | 18.633 | 18.6314 | 18.6314 | 18.6314 | 18.6314 | 18.6314 | 18.6314
|  | YATTENDON | CT |  |  | 19.5833 | 19.572 | 19.5474 | 19.5168 | 19.4856 | 19.455 | 19.4288 | 19.403 | 19.3753 | 19.3477 | 19.2932 | 19.2252 | 12.8412 | 12.3647 | 17.4747 | 17.456 | 17.4151 | 17.3814 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 12.8387 | 18.7376 | 18.7311 | 18.7168 | 18.6993 | 18.6816 | 18.6641 | 18.649 | 18.634 | 18.6314 | 18.6314 | 18.6314 | 18.6314 | 18.6314 | 18.6314
|  | YATTENDON | LW |  |  | 19.5833 | 19.572 | 19.5474 | 19.5168 | 19.4856 | 19.455 | 19.4288 | 19.403 | 19.3753 | 19.3477 | 19.2932 | 19.2252 | 12.8412 | 12.3647 | 17.4745 | 17.4556 | 17.4146 | 17.3807 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 12.9623 | 18.7375 | 18.7309 | 18.7167 | 18.6989 | 18.6809 | 18.6631 | 18.648 | 18.633 | 18.6314 | 18.6314 | 18.6314 | 18.6314 | 18.6314 | 18.6314
|  | YATTENDON | ST |  |  | 19.5883 | 19.5831 | 19.5731 | 19.5557 | 19.5348 | 19.5201 | 19.5081 | 19.4961 | 19.4827 | 19.4693 | 19.444 | 19.3834 | 19.3225 | 19.2628 | 17.4827 | 17.4741 | 17.4575 | 17.4285 | 17.3992 | 17.3841 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 18.7403 | 18.7373 | 18.7316 | 18.7215 | 18.7094 | 18.7008 | 18.6939 | 18.687 | 18.6792 | 18.6714 | 18.6568 | 18.6314 | 18.6314 | 18.6314
|  | YATTENDON | FS |  |  | 19.5914 | 19.5903 | 19.5895 | 19.5839 | 19.5774 | 19.5719 | 19.5674 | 19.5616 | 19.5559 | 19.5504 | 19.5396 | 19.514 | 19.4897 | 19.4665 | 17.4879 | 17.4861 | 17.4848 | 17.4754 | 17.4646 | 17.4554 | 17.4479 | 17.4383 | 17.4288 | 17.4196 | 17.4042 | 17.38 | 17.38 | 17.38 | 18.7422 | 18.7415 | 18.7411 | 18.7378 | 18.734 | 18.7309 | 18.7283 | 18.7249 | 18.7216 | 18.7184 | 18.7122 | 18.6973 | 18.6832 | 18.6698
MELKSHAM GSP | CHIPPENHAM | YATTON KEYNALL | MINIMUM HEADROOM | ST 87300 75782 | YES | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | -2.4144 | -2.4795 | -2.6346 | -2.8025 | -2.9698 | -3.1362 | -3.3018 | -3.4664 | -3.6449 | -3.8224 | -4.1744 | -4.5698 | -4.9799 | -5.3865 | -2.5139 | -2.579 | -2.7342 | -2.9021 | -3.0694 | -3.2359 | -3.4015 | -3.5662 | -3.7448 | -3.9223 | -4.2745 | -4.67 | -5.0802 | -5.487
|  | YATTON KEYNALL | CT |  |  | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | -2.4106 | -2.47 | -2.6117 | -2.765 | -2.9177 | -3.0694 | -3.2203 | -3.3701 | -3.5319 | -3.6925 | -4.0112 | -4.4273 | -4.8574 | -5.2823 | -2.51 | -2.5695 | -2.7112 | -2.8646 | -3.0173 | -3.1691 | -3.3201 | -3.4699 | -3.6318 | -3.7924 | -4.1112 | -4.5274 | -4.9577 | -5.3827
|  | YATTON KEYNALL | LW |  |  | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | -2.4144 | -2.4795 | -2.6346 | -2.8025 | -2.9698 | -3.1362 | -3.3018 | -3.4664 | -3.6449 | -3.8224 | -4.1744 | -4.5698 | -4.9799 | -5.3865 | -2.5139 | -2.579 | -2.7342 | -2.9021 | -3.0694 | -3.2359 | -3.4015 | -3.5662 | -3.7448 | -3.9223 | -4.2745 | -4.67 | -5.0802 | -5.487
|  | YATTON KEYNALL | ST |  |  | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | -2.392 | -2.4259 | -2.5003 | -2.6125 | -2.7483 | -2.7923 | -2.8364 | -2.8801 | -2.9276 | -2.9746 | -3.0683 | -3.3067 | -3.5441 | -3.7789 | -2.4914 | -2.5254 | -2.5998 | -2.712 | -2.8479 | -2.8919 | -2.936 | -2.9797 | -3.0272 | -3.0743 | -3.168 | -3.4064 | -3.6439 | -3.8788
|  | YATTON KEYNALL | FS |  |  | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | 46.5336 | -2.3739 | -2.3777 | -2.3824 | -2.4103 | -2.4436 | -2.4592 | -2.4748 | -2.4949 | -2.5148 | -2.5346 | -2.5736 | -2.6701 | -2.7645 | -2.8561 | -2.4733 | -2.4772 | -2.4819 | -2.5098 | -2.5431 | -2.5587 | -2.5743 | -2.5944 | -2.6143 | -2.6341 | -2.6731 | -2.7697 | -2.8641 | -2.9557
AXMINSTER | YEOVIL BSP | YEOVIL | MINIMUM HEADROOM | ST 57690 16833 | YES | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 28.1806 | 28.1711 | 28.1519 | 28.1303 | 28.1074 | 28.0834 | 28.0642 | 28.0467 | 28.0198 | 27.9888 | 27.9292 | 27.7096 | 27.4259 | 27.1407 | 27.1467 | 27.1438 | 27.1377 | 27.1309 | 27.1237 | 27.1161 | 27.11 | 27.1045 | 27.0961 | 27.0863 | 27.0675 | 26.9983 | 26.9088 | 26.8213
|  | YEOVIL | CT |  |  | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 28.1806 | 28.1718 | 28.1533 | 28.1328 | 28.1112 | 28.0884 | 28.0693 | 28.0509 | 28.0311 | 28.0111 | 27.9733 | 27.7708 | 27.5223 | 27.2674 | 27.1468 | 27.144 | 27.1381 | 27.1317 | 27.1249 | 27.1177 | 27.1116 | 27.1059 | 27.0996 | 27.0933 | 27.0814 | 27.0176 | 26.9392 | 26.8589
|  | YEOVIL | LW |  |  | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 28.1806 | 28.1711 | 28.1519 | 28.1303 | 28.1074 | 28.0834 | 28.0642 | 28.0467 | 28.0284 | 28.0106 | 27.975 | 27.7096 | 27.4259 | 27.1407 | 27.1467 | 27.1438 | 27.1377 | 27.1309 | 27.1237 | 27.1161 | 27.11 | 27.1045 | 27.0988 | 27.0932 | 27.0819 | 26.9983 | 26.9088 | 26.8213
|  | YEOVIL | ST |  |  | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 28.2153 | 28.1782 | 28.1693 | 28.157 | 28.1422 | 28.1097 | 28.0799 | 28.051 | 28.0198 | 27.9888 | 27.9292 | 27.7443 | 27.5353 | 27.327 | 27.1577 | 27.146 | 27.1432 | 27.1393 | 27.1346 | 27.1244 | 27.115 | 27.1059 | 27.0961 | 27.0863 | 27.0675 | 27.0092 | 26.9433 | 26.8777
|  | YEOVIL | FS |  |  | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 26.8695 | 28.2167 | 28.1827 | 28.1805 | 28.1762 | 28.1712 | 28.1627 | 28.1553 | 28.1466 | 28.1379 | 28.1295 | 28.1129 | 28.0617 | 27.9957 | 27.9231 | 27.1581 | 27.1474 | 27.1467 | 27.1454 | 27.1438 | 27.1411 | 27.1388 | 27.136 | 27.1333 | 27.1306 | 27.1254 | 27.1093 | 27.0885 | 27.0656
AXMINSTER | YEOVIL BSP | YETMINSTER | MINIMUM HEADROOM | ST 60294 10206 | YES | 17.1387 | 17.1369 | 17.1345 | 17.1315 | 17.1277 | 17.123 | 17.1174 | 17.1109 | 17.1031 | 17.0941 | 17.0724 | 16.9951 | 16.8802 | 16.7278 | 13.743 | 13.7397 | 13.7348 | 13.7294 | 13.7236 | 13.7172 | 13.7104 | 13.7031 | 13.6944 | 13.6846 | 13.6619 | 13.5866 | 10.3279 | 9.7432 | 15.1631 | 15.1555 | 15.1423 | 15.1275 | 15.1116 | 15.0948 | 15.077 | 15.0583 | 15.0367 | 15.0134 | 14.9615 | 14.7828 | 10.6771 | 10.0407
|  | YETMINSTER | CT |  |  | 17.1387 | 17.1369 | 17.1345 | 17.1315 | 17.1277 | 17.123 | 17.1174 | 17.1109 | 17.1031 | 17.0941 | 17.0724 | 16.9951 | 16.8802 | 16.7278 | 13.743 | 13.7397 | 13.7348 | 13.7294 | 13.7236 | 13.7172 | 13.7104 | 13.7031 | 13.6944 | 13.6846 | 13.6619 | 13.5866 | 10.3279 | 9.7432 | 15.1631 | 15.1555 | 15.1423 | 15.1275 | 15.1116 | 15.0948 | 15.077 | 15.0583 | 15.0367 | 15.0134 | 14.9615 | 14.7828 | 10.6771 | 10.0407
|  | YETMINSTER | LW |  |  | 17.1387 | 17.1369 | 17.1345 | 17.1315 | 17.1277 | 17.123 | 17.1174 | 17.1109 | 17.1031 | 17.0941 | 17.0724 | 16.9951 | 16.8802 | 16.7278 | 13.746 | 13.745 | 13.7436 | 13.7419 | 13.7397 | 13.737 | 13.7339 | 13.7301 | 13.7256 | 13.7205 | 13.7081 | 13.6639 | 10.3665 | 9.8576 | 15.1689 | 15.1662 | 15.1615 | 15.1557 | 15.1487 | 15.1407 | 15.1315 | 15.1213 | 15.1096 | 15.0968 | 15.0675 | 14.9108 | 14.7306 | 10.215
|  | YETMINSTER | ST |  |  | 17.1404 | 17.1398 | 17.1389 | 17.138 | 17.1368 | 17.1353 | 17.1335 | 17.1316 | 17.1295 | 17.1272 | 17.1223 | 17.1037 | 17.0745 | 17.0371 | 13.747 | 13.7466 | 13.7461 | 13.7456 | 13.745 | 13.744 | 13.743 | 13.7419 | 13.7407 | 13.7395 | 13.7367 | 13.726 | 13.7093 | 13.6879 | 15.1709 | 15.1699 | 15.168 | 15.1654 | 15.1622 | 15.1541 | 15.1456 | 15.1371 | 15.1279 | 15.1185 | 15.0997 | 15.0472 | 14.9853 | 14.9158
|  | YETMINSTER | FS |  |  | 17.1406 | 17.1402 | 17.1398 | 17.1391 | 17.1384 | 17.1376 | 17.1368 | 17.136 | 17.1351 | 17.1342 | 17.1321 | 17.1246 | 17.1147 | 17.104 | 13.7471 | 13.7469 | 13.7466 | 13.7462 | 13.7458 | 13.7454 | 13.7449 | 13.7445 | 13.7439 | 13.7434 | 13.7423 | 13.7379 | 13.7323 | 13.7262 | 15.1714 | 15.1708 | 15.1703 | 15.1691 | 15.1677 | 15.165 | 15.1621 | 15.1588 | 15.1554 | 15.1519 | 15.1451 | 15.119 | 15.0896 | 15.0656
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD | MINIMUM HEADROOM | SU 60592 00043 | NO | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  | ZETLAND ROAD | CT |  |  | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  | ZETLAND ROAD | LW |  |  | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  | ZETLAND ROAD | ST |  |  | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  | ZETLAND ROAD | FS |  |  | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 27.2016 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 25.1608 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
[6 empty] | 30.6384 | 30.6372 | 30.6348 | 30.6306 | 30.6079 | 30.5845 | 30.5535 | 30.5163 | 30.468 | 30.4416 | 30.3521 | 30.1853 | 29.5117 | 28.1517 | 22.551 | 22.551 | 22.551 | 22.551 | 22.5329 | 22.5145 | 22.4958 | 22.4762 | 22.4461 | 22.4423 | 22.3199 | 22.0406 | 20.4125 | 18.8268 | 22.4015 | 22.4006 | 22.3987 | 22.3953 | 22.3736 | 22.3512 | 22.3237 | 22.2903 | 22.2462 | 22.2244 | 22.1406 | 21.6634 | 20.0385 | 18.456
[6 empty] | 30.6384 | 30.6372 | 30.6348 | 30.6306 | 30.6079 | 30.5845 | 30.5606 | 30.5219 | 30.4711 | 30.4447 | 30.356 | 30.1853 | 29.5683 | 28.1948 | 22.551 | 22.551 | 22.551 | 22.551 | 22.5329 | 22.5145 | 22.4958 | 22.4762 | 22.4461 | 22.4423 | 22.43 | 22.0969 | 20.4921 | 18.8929 | 22.4015 | 22.4006 | 22.3987 | 22.3953 | 22.3736 | 22.3512 | 22.3284 | 22.2935 | 22.2469 | 22.225 | 22.1518 | 21.7755 | 20.1178 | 18.5218
[6 empty] | 30.6384 | 30.6372 | 30.6348 | 30.6306 | 30.6098 | 30.5881 | 30.5535 | 30.5163 | 30.468 | 30.4416 | 30.3521 | 30.2223 | 29.5117 | 28.1517 | 22.551 | 22.551 | 22.551 | 22.551 | 22.5348 | 22.518 | 22.5005 | 22.4824 | 22.4549 | 22.4511 | 22.4381 | 22.0406 | 20.4125 | 18.8268 | 22.4015 | 22.4006 | 22.3987 | 22.3953 | 22.3754 | 22.3547 | 22.3237 | 22.2903 | 22.2462 | 22.2244 | 22.1503 | 21.6634 | 20.0385 | 18.456
[6 empty] | 30.6436 | 30.638 | 30.6365 | 30.6342 | 30.6313 | 30.6279 | 30.6219 | 30.6145 | 30.6004 | 30.5849 | 30.5318 | 30.4561 | 30.3794 | 30.3047 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.5363 | 22.315 | 21.4931 | 22.4057 | 22.4013 | 22.4 | 22.3982 | 22.3959 | 22.3932 | 22.3884 | 22.3825 | 22.3712 | 22.3589 | 22.3165 | 22.2561 | 22.0686 | 21.1173
[6 empty] | 30.6442 | 30.6391 | 30.6384 | 30.6376 | 30.6266 | 30.6157 | 30.6043 | 30.5922 | 30.5739 | 30.5254 | 30.3699 | 30.2755 | 30.0411 | 29.8393 | 22.551 | 22.551 | 22.551 | 22.551 | 22.5412 | 22.5316 | 22.522 | 22.5122 | 22.4969 | 22.4545 | 22.3199 | 22.2558 | 22.0539 | 21.885 | 22.4062 | 22.4021 | 22.4016 | 22.4009 | 22.3902 | 22.3795 | 22.3685 | 22.3568 | 22.3392 | 22.2919 | 22.1406 | 22.0523 | 21.8245 | 21.6294
[6 empty] | 13.3938 | 13.3938 | 13.3938 | 13.3938 | 13.3028 | 13.2064 | 13.1045 | 12.9907 | 12.8044 | 12.7791 | 12.6858 | 11.7947 | 10.7815 | 10.2143 | 8.443 | 8.4288 | 8.41 | 8.3702 | 8.2182 | 8.0572 | 7.8891 | 7.6486 | 7.3293 | 7.1586 | 6.5887 | 5.4556 | 4.3665 | 3.7254 | 8.7899 | 8.7759 | 8.7574 | 8.7183 | 8.5673 | 8.4074 | 8.2404 | 8.002 | 7.6849 | 7.5167 | 6.9547 | 5.8315 | 4.7508 | 4.1178
[6 empty] | 13.3938 | 13.3938 | 13.3938 | 13.3938 | 13.3028 | 13.2064 | 13.1045 | 12.9907 | 12.8044 | 12.7791 | 12.6858 | 11.7947 | 10.7815 | 10.2143 | 8.443 | 8.4288 | 8.41 | 8.3702 | 8.2182 | 8.0572 | 7.8891 | 7.6486 | 7.3293 | 7.1586 | 6.5887 | 5.4556 | 4.3665 | 3.7254 | 8.7899 | 8.7759 | 8.7574 | 8.7183 | 8.5673 | 8.4074 | 8.2404 | 8.002 | 7.6849 | 7.5167 | 6.9547 | 5.8315 | 4.7508 | 4.1178
[6 empty] | 13.3938 | 13.3938 | 13.3938 | 13.3938 | 13.3651 | 13.3201 | 13.2554 | 13.1699 | 13.0152 | 12.9903 | 12.8754 | 12.3066 | 11.3922 | 10.9446 | 8.4542 | 8.4481 | 8.44 | 8.423 | 8.3551 | 8.2672 | 8.0806 | 7.8683 | 7.5807 | 7.4104 | 6.8187 | 5.9736 | 4.9832 | 4.4618 | 8.8009 | 8.7949 | 8.7869 | 8.7702 | 8.7029 | 8.6158 | 8.4312 | 8.221 | 7.9356 | 7.7678 | 7.1841 | 6.3488 | 5.3668 | 4.8535
[6 empty] | 13.3938 | 13.3938 | 13.3938 | 13.3938 | 13.3907 | 13.3845 | 13.3746 | 13.3598 | 13.3294 | 13.316 | 13.25 | 13.1678 | 12.7975 | 12.4323 | 8.4572 | 8.4534 | 8.4489 | 8.4413 | 8.4136 | 8.3785 | 8.3048 | 8.2231 | 8.1025 | 7.9898 | 7.5933 | 7.109 | 6.5047 | 6.0912 | 8.8039 | 8.8001 | 8.7957 | 8.7882 | 8.7609 | 8.7263 | 8.6537 | 8.5731 | 8.454 | 8.3429 | 7.9519 | 7.4744 | 6.8755 | 6.4674
[6 empty] | 13.3938 | 13.3938 | 13.3938 | 13.3938 | 13.3937 | 13.3934 | 13.3929 | 13.3922 | 13.3906 | 13.3842 | 13.3478 | 13.3191 | 13.1835 | 13.0518 | 8.4613 | 8.4607 | 8.46 | 8.4595 | 8.4487 | 8.4368 | 8.4149 | 8.3918 | 8.3623 | 8.3169 | 8.151 | 7.9673 | 7.7138 | 7.4724 | 8.8079 | 8.8072 | 8.8066 | 8.8061 | 8.7955 | 8.7838 | 8.7622 | 8.7395 | 8.7104 | 8.6657 | 8.502 | 8.3209 | 8.0693 | 7.8298
[6 empty] | 32.6383 | 32.6236 | 32.6088 | 31.7082 | 31.6344 | 31.5606 | 31.4868 | 31.4129 | 31.3391 | 31.3096 | 31.221 | 30.9675 | 28.9927 | 26.9667 | 24.3028 | 24.2881 | 24.2733 | 23.3727 | 23.2989 | 23.2251 | 23.1513 | 23.0775 | 23.0036 | 22.9741 | 22.8855 | 21.3793 | 19.1328 | 16.8385 | 24.6384 | 24.6215 | 24.6041 | 23.696 | 23.6123 | 23.5269 | 23.4304 | 23.3338 | 23.2345 | 23.1784 | 23.0198 | 22.0147 | 19.7 | 17.3384
[6 empty] | 32.7092 | 32.7003 | 32.6915 | 32.1511 | 32.1068 | 32.0625 | 32.0182 | 31.974 | 31.9297 | 31.9119 | 31.8588 | 31.137 | 29.0231 | 26.9973 | 24.3737 | 24.3648 | 24.356 | 23.8156 | 23.7713 | 23.7271 | 23.6828 | 23.6385 | 23.5942 | 23.5765 | 23.5233 | 21.5531 | 19.1676 | 16.8735 | 24.7083 | 24.6965 | 24.684 | 24.1341 | 24.0779 | 24.02 | 23.9641 | 23.8971 | 23.8273 | 23.7831 | 23.6599 | 22.1896 | 19.7359 | 17.3744
[6 empty] | 32.6383 | 32.6236 | 32.6088 | 31.7082 | 31.6344 | 31.5606 | 31.4868 | 31.4129 | 31.3391 | 31.3096 | 31.221 | 30.9675 | 28.9927 | 26.9667 | 24.3028 | 24.2881 | 24.2733 | 23.3727 | 23.2989 | 23.2251 | 23.1513 | 23.0775 | 23.0036 | 22.9741 | 22.8855 | 21.3793 | 19.1328 | 16.8385 | 24.6384 | 24.6215 | 24.6041 | 23.696 | 23.6123 | 23.5269 | 23.4304 | 23.3338 | 23.2345 | 23.1784 | 23.0198 | 22.0147 | 19.7 | 17.3384
[6 empty] | 32.7446 | 32.7387 | 32.7328 | 32.3726 | 32.343 | 32.3135 | 32.284 | 32.2545 | 32.2249 | 32.2131 | 32.1777 | 32.1186 | 32.0832 | 30.9386 | 24.4091 | 24.4032 | 24.3973 | 24.0371 | 24.0076 | 23.978 | 23.9485 | 23.919 | 23.8895 | 23.8776 | 23.8422 | 23.7832 | 22.6402 | 21.2101 | 24.7454 | 24.738 | 24.7305 | 24.3661 | 24.3302 | 24.2929 | 24.2498 | 24.2068 | 24.16 | 24.13 | 24.0465 | 23.901 | 23.2836 | 21.8103
[6 empty] | 32.78 | 32.7771 | 32.7741 | 32.594 | 32.5769 | 32.5598 | 32.5427 | 32.5255 | 32.507 | 32.4908 | 32.4402 | 32.3951 | 32.3281 | 32.2544 | 24.4446 | 24.4416 | 24.4387 | 24.2585 | 24.2414 | 24.2243 | 24.2072 | 24.19 | 24.1716 | 24.1553 | 24.1047 | 24.0596 | 23.9926 | 23.919 | 24.7817 | 24.7781 | 24.7746 | 24.5928 | 24.5728 | 24.5524 | 24.5307 | 24.509 | 24.4845 | 24.4611 | 24.3918 | 24.312 | 24.2052 | 24.0912

## BSP Headroom Gen
Grid Supply Point | Bulk Supply Point |  | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Generation Headroom Winter MVA | [13 empty] | Generation Headroom Summer MVA | [13 empty] | Generation Headroom Spring/Autumn MVA
[6 empty] | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050
WILLESDEN GSP | ACTON LANE | ACTON LANE | MINIMUM HEADROOM | TQ 20805 83142 | YES | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 113.9962 | 113.6921 | 112.4968 | 111.2903 | 110.0981 | 115.841 | 115.7724 | 115.6242 | 115.5628 | 115.5355 | 115.5247 | 115.5247 | 115.5247 | 115.5247 | 115.5247 | 113.9215 | 112.5133 | 111.0921 | 109.6876 | 115.4309 | 115.4246 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 113.9005 | 113.5483 | 112.1637 | 110.7479 | 109.3477
|  |  | CT |  |  | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 113.9962 | 113.6921 | 112.4968 | 111.2903 | 110.0981 | 115.8435 | 115.7809 | 115.6436 | 115.568 | 115.5428 | 115.5251 | 115.5247 | 115.5247 | 115.5247 | 115.5247 | 115.5247 | 112.6902 | 111.3211 | 109.9682 | 115.4311 | 115.4254 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 113.9904 | 113.6637 | 112.3377 | 110.9763 | 109.6275
|  |  | LW |  |  | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 113.9962 | 113.6921 | 112.4968 | 111.2903 | 110.0981 | 115.841 | 115.7724 | 115.6242 | 115.5628 | 115.5355 | 115.5247 | 115.5247 | 115.5247 | 115.5247 | 115.5247 | 113.9215 | 112.5133 | 111.0921 | 109.6876 | 115.4309 | 115.4246 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 113.9005 | 113.5483 | 112.1637 | 110.7479 | 109.3477
|  |  | ST |  |  | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 113.9253 | 113.2054 | 112.5041 | 111.8123 | 115.9139 | 115.8304 | 115.7614 | 115.6628 | 115.5765 | 115.5494 | 115.5296 | 115.5247 | 115.5247 | 115.5247 | 115.5247 | 113.348 | 112.5219 | 111.707 | 115.4801 | 115.4299 | 115.4237 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 113.8184 | 112.9845 | 112.1722 | 111.3609
|  |  | FS |  |  | 115.3682 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 115.366 | 113.8642 | 115.9315 | 115.8726 | 115.8593 | 115.8283 | 115.7924 | 115.7295 | 115.6742 | 115.6063 | 115.5751 | 115.5637 | 115.5411 | 115.5247 | 115.5247 | 115.5247 | 115.4952 | 115.4445 | 115.4331 | 115.4297 | 115.4265 | 115.4208 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 115.416 | 113.7476
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT BSP | MINIMUM HEADROOM | SU 85922 48779 | YES | 170.8057 | 170.6317 | 170.6477 | 170.2402 | 169.7718 | 168.9785 | 167.9169 | 167.1287 | 165.6918 | 164.2945 | 160.9968 | 155.1232 | 149.2558 | 145.182 | 232.4856 | 232.2778 | 231.8194 | 231.1802 | 230.9332 | 230.9293 | 230.8911 | 230.1386 | 229.4385 | 228.6939 | 226.5659 | 222.5804 | 218.6339 | 161.9713 | 233.9955 | 233.9894 | 233.9804 | 233.9706 | 233.96 | 233.7237 | 233.7826 | 233.4084 | 232.6335 | 231.7961 | 229.5785 | 225.4981 | 221.4998 | 163.7844
|  |  | CT |  |  | 170.8057 | 170.6317 | 255.404 | 170.7331 | 170.1989 | 168.9785 | 167.9169 | 167.1287 | 165.6918 | 164.2945 | 160.9968 | 155.1232 | 149.2558 | 145.182 | 232.4856 | 232.2778 | 231.8194 | 231.1802 | 230.9332 | 231.6766 | 230.8911 | 230.1386 | 229.4385 | 228.7519 | 227.5117 | 224.4595 | 221.5371 | 161.9713 | 233.9955 | 233.9894 | 233.9804 | 233.9706 | 233.96 | 234.959 | 234.1265 | 233.4084 | 232.7795 | 232.1753 | 231.0218 | 227.6845 | 224.6607 | 163.7844
|  |  | LW |  |  | 170.8057 | 170.6317 | 255.404 | 170.7331 | 170.1989 | 168.9785 | 167.9169 | 167.1287 | 165.6918 | 164.2945 | 160.9968 | 155.1232 | 149.2558 | 145.182 | 232.4974 | 232.3024 | 232.8899 | 232.292 | 232.0536 | 231.4275 | 230.8967 | 230.5323 | 229.5999 | 228.6939 | 226.5659 | 222.5804 | 218.6339 | 162.6698 | 234.0011 | 233.9992 | 235.0072 | 235.004 | 234.9999 | 234.3156 | 233.7826 | 233.5203 | 232.6335 | 231.7961 | 229.5785 | 225.4981 | 221.4998 | 164.5575
|  |  | ST |  |  | 170.9114 | 170.8012 | 170.6477 | 170.2402 | 169.7718 | 169.0476 | 169.3067 | 168.4888 | 167.7056 | 167.0663 | 165.9459 | 163.5907 | 160.8551 | 158.0794 | 232.6156 | 232.4918 | 232.3194 | 231.8612 | 231.3345 | 230.9293 | 231.5909 | 231.2227 | 230.7997 | 230.4685 | 229.8447 | 228.4065 | 226.594 | 224.7178 | 234.0029 | 234.0022 | 234.0013 | 234.0003 | 233.9991 | 233.7237 | 234.4775 | 234.2502 | 233.8689 | 233.6495 | 233.1078 | 231.8273 | 230.2189 | 228.5473
|  |  | FS |  |  | 170.9556 | 170.9139 | 170.8808 | 170.7805 | 170.6538 | 170.5338 | 170.2822 | 169.9821 | 169.6275 | 169.2551 | 168.629 | 168.6163 | 167.8107 | 167.121 | 232.6653 | 232.6185 | 232.5814 | 232.4688 | 232.3266 | 232.1918 | 231.9598 | 231.6767 | 231.3464 | 230.9944 | 230.6693 | 231.2262 | 230.883 | 230.5832 | 234.0031 | 234.0026 | 234.0022 | 234.0015 | 234.0007 | 233.9999 | 233.8813 | 233.7545 | 233.5951 | 233.4394 | 233.2854 | 234.0428 | 233.9064 | 233.7629
BRAMLEY (FLEE) | ALTON | ALTON | MINIMUM HEADROOM | SU 72730 39772 | YES | 187.4622 | 187.4608 | 187.459 | 187.4567 | 187.4539 | 84.5805 | 80.6979 | 76.9919 | 71.935 | 66.6317 | 55.9644 | 41.3295 | 25.4799 | 17.5981 | 139.1639 | 139.0805 | 138.9226 | 45.6959 | 41.6506 | 37.0902 | 32.6631 | 28.3666 | 22.6598 | 16.6437 | 4.7455 | -11.3193 | -28.6541 | -37.1702 | 152.9886 | 152.9872 | 152.9854 | 53.967 | 49.9196 | 45.2385 | 40.7171 | 36.3734 | 30.5659 | 24.4602 | 12.2585 | -4.2778 | -22.1904 | -30.9874
|  |  | CT |  |  | 187.4622 | 187.4608 | 187.459 | 187.4567 | 187.4539 | 84.5805 | 80.6979 | 76.9919 | 71.935 | 66.6317 | 55.9644 | 41.3295 | 25.4799 | 17.5981 | 140.8384 | 140.7452 | 140.5587 | 139.6045 | 85.0669 | 78.3426 | 69.945 | 59.3792 | 52.0896 | 44.6619 | 36.6048 | 24.7962 | 10.868 | 1.1401 | 154.6687 | 154.6643 | 154.6577 | 154.65 | 154.6415 | 154.6324 | 78.0516 | 67.3416 | 59.9322 | 52.391 | 44.1232 | 31.6228 | 16.9361 | 6.9394
|  |  | LW |  |  | 187.4622 | 187.4608 | 187.459 | 187.4567 | 187.4539 | 84.5805 | 80.6979 | 76.9919 | 71.935 | 66.6317 | 55.9644 | 41.3295 | 25.4799 | 17.5981 | 139.1639 | 139.0805 | 138.9226 | 45.6959 | 41.6506 | 37.0902 | 32.6631 | 28.3666 | 22.6598 | 16.6437 | 4.7455 | -11.3193 | -28.6541 | -37.1702 | 152.9886 | 152.9872 | 152.9854 | 53.967 | 49.9196 | 45.2385 | 40.7171 | 36.3734 | 30.5659 | 24.4602 | 12.2585 | -4.2778 | -22.1904 | -30.9874
|  |  | ST |  |  | 189.1477 | 189.1472 | 189.1466 | 189.1458 | 189.145 | 188.9544 | 188.7769 | 188.6196 | 188.2888 | 188.084 | 187.5943 | 83.9387 | 75.0115 | 68.0693 | 140.904 | 140.8337 | 140.7595 | 139.9592 | 139.177 | 80.9688 | 73.5095 | 63.8313 | 57.6015 | 50.9369 | 44.6411 | 36.7464 | 26.6734 | 19.011 | 154.6741 | 154.6737 | 154.673 | 154.6723 | 154.6714 | 154.4758 | 81.6974 | 71.9764 | 65.6871 | 58.9944 | 52.6248 | 44.5833 | 34.3575 | 26.5127
|  |  | FS |  |  | 189.1478 | 189.1475 | 189.1472 | 189.1467 | 189.1462 | 189.1456 | 154.3267 | 154.2389 | 154.1287 | 154.021 | 82.6068 | 73.9246 | 66.8585 | 62.1233 | 140.9255 | 140.9013 | 140.8707 | 140.7211 | 140.5049 | 140.287 | 58.3002 | 55.8804 | 52.8848 | 49.3307 | 41.2104 | 30.5383 | 22.2466 | 16.7091 | 154.6743 | 154.674 | 154.6737 | 154.6731 | 154.6726 | 154.672 | 65.4897 | 63.3822 | 60.5852 | 57.255 | 49.3675 | 38.6478 | 30.3264 | 24.7576
MELKSHAM GSP | AMESBURY | AMESBURY | MINIMUM HEADROOM | SU 15842 42724 | YES | 83.5962 | 83.4962 | 20.724 | 18.8174 | 16.8929 | 14.9041 | 12.9522 | 10.9857 | 8.6459 | 6.0987 | 1.2512 | -3.0857 | -7.2788 | -9.1808 | 75.0598 | 74.9431 | 2.2129 | 0.044814 | -2.1435 | -4.4049 | -6.6243 | -8.8598 | -11.52 | -14.4164 | -19.9281 | -24.8353 | -29.5878 | -31.75 | 76.7579 | 76.6405 | 3.5825 | 1.4045 | -0.79375 | -3.0655 | -5.295 | -7.5409 | -10.2134 | -13.1232 | -18.6609 | -23.5937 | -28.3745 | -30.5575
|  |  | CT |  |  | 83.5962 | 83.4962 | 20.724 | 18.8174 | 16.8929 | 14.9041 | 12.9522 | 10.9857 | 8.6459 | 6.0987 | 1.2512 | -3.0857 | -7.2788 | -9.1808 | 78.583 | 78.4827 | 41.1053 | 37.8804 | 34.8616 | 31.1299 | 26.6801 | 20.8207 | 17.1759 | 13.4169 | 10.0443 | 6.8319 | 2.7784 | -0.74957 | 80.2968 | 80.1957 | 42.6494 | 39.4097 | 36.3767 | 32.6278 | 28.1574 | 22.2711 | 18.609 | 14.8322 | 11.4422 | 8.208 | 4.1243 | 0.56476
|  |  | LW |  |  | 83.5962 | 83.4962 | 20.724 | 18.8174 | 16.8929 | 14.9041 | 12.9522 | 10.9857 | 8.6459 | 6.0987 | 1.2512 | -3.0857 | -7.2788 | -9.1808 | 75.0598 | 74.9431 | 2.2129 | 0.044814 | -2.1435 | -4.4049 | -6.6243 | -8.8598 | -11.52 | -14.4164 | -19.9281 | -24.8353 | -29.5878 | -31.75 | 76.7579 | 76.6405 | 3.5825 | 1.4045 | -0.79375 | -3.0655 | -5.295 | -7.5409 | -10.2134 | -13.1232 | -18.6609 | -23.5937 | -28.3745 | -30.5575
|  |  | ST |  |  | 98.9044 | 98.9043 | 54.6799 | 52.1651 | 49.4073 | 46.2533 | 42.4898 | 37.4166 | 34.3675 | 31.0181 | 28.1738 | 25.8847 | 22.8609 | 20.178 | 78.6178 | 78.5561 | 41.268 | 38.3308 | 35.1098 | 31.4257 | 27.0293 | 21.2235 | 17.7537 | 13.9416 | 10.7054 | 8.106 | 4.6685 | 1.6193 | 80.332 | 80.27 | 42.8138 | 39.8633 | 36.6278 | 32.9271 | 28.5108 | 22.6787 | 19.1933 | 15.3639 | 12.1129 | 9.501 | 6.0464 | 2.981
|  |  | FS |  |  | 98.9045 | 98.9044 | 98.9043 | 54.4328 | 53.8263 | 53.2206 | 52.4306 | 51.3514 | 49.9914 | 48.3534 | 44.5236 | 39.5519 | 35.6534 | 33.1355 | 78.6538 | 78.6398 | 78.6317 | 40.9797 | 40.2714 | 39.5641 | 38.6414 | 37.3805 | 35.7918 | 33.8778 | 29.4026 | 23.652 | 19.2151 | 16.35 | 80.3681 | 80.354 | 80.346 | 42.5242 | 41.8126 | 41.1021 | 40.1753 | 38.9087 | 37.3128 | 35.3901 | 30.8946 | 25.1178 | 20.6604 | 17.7819
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER BSP | MINIMUM HEADROOM | SU 35334 46598 | YES | 32.9068 | -28.7892 | -107.1458 | -29.4672 | -31.7477 | -34.0954 | -36.4034 | -34.8986 | -39.57 | -44.4874 | -54.0331 | -82.9692 | -116.4967 | -126.2235 | 9.4073 | -63.1872 | -155.3854 | -79.0874 | -81.7693 | -84.53 | -87.2436 | -86.1445 | -91.381 | -96.9064 | -107.6155 | -140.4737 | -178.7416 | -189.2335 | 21.0805 | -48.7294 | -138.0793 | -61.6387 | -64.2796 | -66.9984 | -69.671 | -68.531 | -73.7107 | -79.1751 | -89.7684 | -122.2373 | -160.0433 | -170.4988
|  |  | CT |  |  | 32.9068 | -28.7892 | -107.1458 | -29.4672 | -31.7477 | -34.0954 | -36.4034 | -34.8986 | -39.57 | -44.4874 | -54.0331 | -82.9692 | -116.4967 | -126.2235 | 9.4212 | 9.1731 | -32.5029 | 18.0759 | -47.372 | -51.5673 | -56.4754 | -62.7876 | -68.3606 | -74.0724 | -80.2228 | -98.1815 | -120.2868 | -130.3468 | 21.0928 | 20.853 | -19.226 | 32.6903 | -30.4243 | -34.5568 | -39.3913 | -45.6082 | -51.1073 | -56.7433 | -62.8261 | -80.586 | -102.448 | -112.4659
|  |  | LW |  |  | 32.9068 | -28.7892 | -107.1458 | -29.4672 | -31.7477 | -34.0954 | -36.4034 | -34.8986 | -39.57 | -44.4874 | -54.0331 | -82.9692 | -116.4967 | -126.2235 | 9.4073 | -63.1872 | -155.3854 | -79.0874 | -81.7693 | -84.53 | -87.2436 | -86.1445 | -91.381 | -96.9064 | -107.6155 | -140.4737 | -178.7416 | -189.2335 | 21.0805 | -48.7294 | -138.0793 | -61.6387 | -64.2796 | -66.9984 | -69.671 | -68.531 | -73.7107 | -79.1751 | -89.7684 | -122.2373 | -160.0433 | -170.4988
|  |  | ST |  |  | 43.9167 | 32.8681 | -2.3263 | 53.8235 | -1.9379 | -5.3629 | -9.3893 | -14.6077 | -18.8824 | -23.5239 | -28.0628 | -37.8194 | -55.9608 | -64.0929 | 20.502 | 9.3613 | -32.0501 | 18.9151 | -46.6968 | -50.7262 | -55.4633 | -61.6028 | -66.5824 | -71.9935 | -77.2335 | -89.0333 | -109.7973 | -118.7278 | 32.1538 | 21.0365 | -18.7865 | 33.5034 | -29.7511 | -33.7182 | -38.3819 | -44.4263 | -49.3332 | -54.665 | -59.8332 | -71.4252 | -91.9243 | -100.782
|  |  | FS |  |  | 75.0236 | 33.3198 | 33.2935 | 83.4258 | 57.7315 | 18.332 | 17.4573 | 16.2767 | 14.827 | 13.1072 | 9.1268 | 3.6909 | -0.47399 | -3.5146 | 56.592 | 9.8927 | 9.862 | 53.7464 | 23.5132 | -22.8463 | -23.8752 | -25.2641 | -26.9695 | -28.9928 | -33.6756 | -40.069 | -44.9983 | -48.5714 | 62.387 | 21.5476 | 21.518 | 66.9987 | 37.9252 | -6.656 | -7.6456 | -8.9814 | -10.6215 | -12.5674 | -17.071 | -23.2292 | -28.0813 | -31.6015
MANNINGTON GSP | ARNEWOOD | ARNEWOOD | MINIMUM HEADROOM | SZ 26094 97294 | YES | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 64.7067 | 63.6808 | 56.4437 | 45.4543 | 37.8284 | 32.1057 | 63.9207 | 63.9036 | 63.8607 | 63.7752 | 63.7296 | 63.7101 | 63.6874 | 63.6571 | 62.6423 | 61.5987 | 55.9388 | 43.824 | 35.652 | 29.5359 | 65.4163 | 65.4103 | 65.3954 | 65.3656 | 65.3365 | 65.3016 | 65.2611 | 65.2072 | 64.2011 | 63.1438 | 56.8584 | 44.7412 | 36.5681 | 30.4511
|  |  | CT |  |  | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 64.7067 | 63.6808 | 56.4437 | 45.4543 | 37.8284 | 32.1057 | 63.9207 | 63.9036 | 63.8607 | 63.7752 | 63.7296 | 63.7101 | 63.6874 | 63.6623 | 63.2557 | 62.8604 | 62.0909 | 51.2195 | 46.2459 | 41.7371 | 65.4163 | 65.4103 | 65.3954 | 65.3656 | 65.3365 | 65.3016 | 65.2611 | 65.2164 | 64.7928 | 64.3694 | 63.5969 | 52.1375 | 47.1629 | 42.6532
|  |  | LW |  |  | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 64.7067 | 63.6808 | 56.4437 | 45.4543 | 37.8284 | 32.1057 | 63.9214 | 63.9059 | 63.8662 | 63.7969 | 63.7364 | 63.7206 | 63.7028 | 63.6863 | 62.6423 | 61.5987 | 55.9388 | 43.824 | 35.652 | 29.5359 | 65.4165 | 65.4111 | 65.3973 | 65.3732 | 65.3485 | 65.3204 | 65.2887 | 65.2593 | 64.2011 | 63.1438 | 56.8584 | 44.7412 | 36.5681 | 30.4511
|  |  | ST |  |  | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.5351 | 65.3374 | 64.9421 | 53.7175 | 49.3813 | 45.2643 | 63.9266 | 63.9174 | 63.8958 | 63.8288 | 63.7518 | 63.7158 | 63.6877 | 63.6571 | 63.4322 | 63.2346 | 62.8393 | 52.386 | 47.6907 | 43.287 | 65.4183 | 65.4151 | 65.4076 | 65.3843 | 65.3575 | 65.3118 | 65.2617 | 65.2072 | 64.9598 | 64.7405 | 64.3452 | 53.3039 | 48.6078 | 44.2035
|  |  | FS |  |  | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 65.7327 | 63.9318 | 63.9308 | 63.9289 | 63.9156 | 63.8982 | 63.864 | 63.825 | 63.7775 | 63.7368 | 63.7267 | 63.7055 | 63.6662 | 63.6299 | 63.6299 | 65.4201 | 65.4198 | 65.4191 | 65.4145 | 65.4084 | 65.3965 | 65.383 | 65.3664 | 65.3492 | 65.3312 | 65.2934 | 65.2234 | 65.1556 | 65.1358
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE T1A & T2A | MINIMUM HEADROOM | SU 65132 52710 | YES | 83.3083 | 83.2994 | 83.2744 | 83.2351 | 83.2209 | 83.2209 | 83.2209 | 83.2209 | 82.5427 | 81.8645 | 80.5081 | 77.4563 | 75.154 | 53.795 | 74.9891 | 74.9597 | 74.8792 | 74.7486 | 74.7486 | 74.7486 | 74.7486 | 74.7486 | 74.0704 | 73.3922 | 72.0358 | 56.562 | 52.02 | 47.6698 | 54.2986 | 54.2145 | 53.9849 | 53.5649 | 53.1372 | 52.6308 | 52.0733 | 51.4104 | 50.6307 | 49.8471 | 47.6449 | 42.5927 | 38.0795 | 33.7286
|  |  | CT |  |  | 83.3083 | 83.2994 | 83.2744 | 83.2351 | 83.2209 | 83.2209 | 83.2209 | 83.2209 | 82.5427 | 81.8645 | 80.5081 | 77.4563 | 75.154 | 53.795 | 74.9891 | 74.9597 | 74.8792 | 74.7486 | 74.7486 | 74.7486 | 74.7486 | 74.7486 | 74.4943 | 74.24 | 73.7313 | 72.4597 | 56.6217 | 53.1905 | 54.2986 | 54.2145 | 53.9849 | 53.5649 | 53.1372 | 52.6308 | 52.0733 | 51.4104 | 50.6307 | 49.8471 | 48.5927 | 45.4683 | 42.681 | 39.2491
|  |  | LW |  |  | 83.3083 | 83.2994 | 83.2744 | 83.2351 | 83.2209 | 83.2209 | 83.2209 | 83.2209 | 82.5427 | 81.8645 | 80.5081 | 77.4563 | 75.154 | 53.795 | 74.9898 | 74.9612 | 74.8816 | 74.7563 | 74.7486 | 74.7486 | 74.7486 | 74.7486 | 74.0704 | 73.3922 | 72.0358 | 56.562 | 52.02 | 47.6698 | 54.3004 | 54.2188 | 53.9918 | 53.6342 | 53.2706 | 52.8838 | 52.492 | 52.1026 | 50.9922 | 49.8683 | 47.6449 | 42.5927 | 38.0795 | 33.7286
|  |  | ST |  |  | 83.3605 | 83.3072 | 83.2954 | 83.2614 | 83.2226 | 83.2209 | 83.2209 | 83.2209 | 83.0902 | 82.9596 | 82.6983 | 81.7837 | 80.2812 | 78.6481 | 75.1562 | 74.986 | 74.9486 | 74.8402 | 74.7486 | 74.7486 | 74.7486 | 74.7486 | 74.618 | 74.4873 | 74.226 | 73.3115 | 71.809 | 56.0549 | 54.7752 | 54.2898 | 54.1829 | 53.8736 | 53.5203 | 53.1468 | 52.6527 | 52.0569 | 51.4814 | 50.8867 | 50.0212 | 47.9121 | 45.1231 | 42.1146
|  |  | FS |  |  | 83.3628 | 83.3133 | 83.3114 | 83.3037 | 83.2938 | 83.2836 | 83.2721 | 83.2569 | 83.2398 | 83.2209 | 83.2209 | 83.2209 | 83.2209 | 83.2209 | 75.1635 | 75.0055 | 74.9996 | 74.975 | 74.9434 | 74.9109 | 74.8742 | 74.8257 | 74.7713 | 74.7486 | 74.7486 | 74.7486 | 74.7486 | 74.7486 | 54.7961 | 54.3454 | 54.3285 | 54.2583 | 54.168 | 54.0754 | 53.9707 | 53.8323 | 53.677 | 53.505 | 53.1058 | 52.3152 | 51.6073 | 51.0123
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BASINGSTOKE T1B & T2B | MINIMUM HEADROOM | SU 65132 52711 | YES | 72.1794 | -33.4504 | -49.2253 | -51.4191 | -53.6244 | -56.2124 | -58.6374 | -60.93 | -64.5643 | -68.3201 | -75.8231 | -85.6962 | -100.8555 | -107.8426 | 63.2612 | -42.4523 | -61.0349 | -63.6186 | -67.372 | -71.0082 | -75.431 | -80.7803 | -85.3096 | -89.9174 | -95.4883 | -103.6059 | -118.1576 | -125.6514 | 69.6505 | -36.047 | -54.0869 | -56.5955 | -60.2442 | -63.7759 | -68.204 | -73.513 | -78.0437 | -82.7235 | -88.4387 | -97.0642 | -111.8653 | -119.5625
|  |  | CT |  |  | 72.1794 | -33.4504 | -49.2253 | -51.4191 | -53.6244 | -56.2124 | -58.6374 | -60.93 | -64.5643 | -68.3201 | -75.8231 | -85.6962 | -100.8555 | -107.8426 | 81.544 | -42.4152 | -43.5904 | -46.8727 | -67.372 | -71.0082 | -75.431 | -80.7803 | -85.3096 | -89.9174 | -95.4883 | -103.6059 | -115.7789 | -123.6228 | 127.1528 | -36.0124 | -37.1545 | -40.3424 | -60.2442 | -63.7759 | -68.204 | -73.513 | -78.0437 | -82.7235 | -88.4387 | -97.0642 | -109.7952 | -117.8286
|  |  | LW |  |  | 72.1794 | -33.4504 | -49.2253 | -51.4191 | -53.6244 | -56.2124 | -58.6374 | -60.93 | -64.5643 | -68.3201 | -75.8231 | -85.6962 | -100.8555 | -107.8426 | 63.2612 | -42.4523 | -61.0349 | -63.6186 | -66.2156 | -69.1183 | -71.8612 | -74.5059 | -78.5508 | -82.7533 | -90.9891 | -101.5293 | -118.1576 | -125.6514 | 69.6505 | -36.047 | -54.0869 | -56.5955 | -59.1172 | -62.0328 | -64.7718 | -67.3767 | -71.4061 | -75.5789 | -83.9551 | -94.8297 | -111.8653 | -119.5625
|  |  | ST |  |  | 123.8953 | 72.0953 | 71.6122 | 69.3311 | 52.0359 | 49.3995 | 46.3859 | 42.5606 | 39.5432 | 36.3762 | 33.1555 | 28.7156 | 20.5947 | 14.9886 | 81.7176 | 63.1618 | 62.5929 | 59.9059 | 39.5321 | 36.4852 | 32.9899 | 28.5322 | 25.0696 | 21.3919 | 17.7286 | 12.8286 | 3.697 | -2.4067 | 127.1562 | 69.5542 | 69.0018 | 66.3932 | 46.6146 | 43.6174 | 40.1876 | 35.8277 | 32.4153 | 28.8158 | 25.1098 | 20.1128 | 10.8898 | 4.6587
|  |  | FS |  |  | 123.8954 | 123.8952 | 123.895 | 123.8947 | 123.8944 | 56.0078 | 55.2966 | 54.3565 | 53.2131 | 51.8846 | 48.9806 | 44.9242 | 43.7934 | 41.4388 | 85.0936 | 84.5261 | 84.4455 | 83.9312 | 83.2242 | 44.2109 | 43.3984 | 42.3181 | 41.0051 | 39.4734 | 36.0853 | 31.3607 | 29.6837 | 26.9476 | 127.1563 | 127.1561 | 127.1559 | 127.1555 | 127.1552 | 51.1569 | 50.3511 | 49.2842 | 47.9869 | 46.4776 | 43.1665 | 38.5439 | 36.9554 | 34.274
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BASINGSTOKE T3 & T4 | MINIMUM HEADROOM | SU 65132 52712 | YES | 109.8095 | 64.804 | 64.4754 | 63.8241 | 63.2223 | 62.5849 | 61.8866 | 61.1514 | 60.2916 | 59.412 | 57.8615 | 55.9761 | 54.1348 | 52.6221 | 106.835 | 62.1874 | 61.7985 | 61.0275 | 60.3151 | 59.5607 | 58.734 | 57.8637 | 56.8459 | 55.8047 | 53.9694 | 51.7376 | 49.558 | 47.7674 | 109.2219 | 63.0833 | 62.6956 | 61.9269 | 61.2168 | 60.4646 | 59.6404 | 58.7728 | 57.7581 | 56.7201 | 54.8903 | 52.6653 | 50.4924 | 48.7072
|  |  | CT |  |  | 109.8095 | 64.804 | 64.4754 | 63.8241 | 63.2223 | 62.5849 | 61.8866 | 61.1514 | 60.2916 | 59.412 | 57.8615 | 55.9761 | 54.1348 | 52.6221 | 106.835 | 71.4693 | 71.3884 | 71.1971 | 71.0244 | 70.8223 | 70.5826 | 70.2853 | 69.9314 | 69.4062 | 68.4007 | 66.7792 | 64.7242 | 62.7565 | 109.2219 | 72.3666 | 72.3359 | 72.2632 | 72.1976 | 72.1208 | 72.0297 | 71.9167 | 71.8196 | 71.3904 | 69.7731 | 67.6612 | 65.6124 | 63.6507
|  |  | LW |  |  | 109.8095 | 64.804 | 64.4754 | 63.8241 | 63.2223 | 62.5849 | 61.8866 | 61.1514 | 60.2916 | 59.412 | 57.8615 | 55.9761 | 54.1348 | 52.6221 | 106.835 | 62.1874 | 61.7985 | 61.0275 | 60.3151 | 59.5607 | 58.734 | 57.8637 | 56.8459 | 55.8047 | 53.9694 | 51.7376 | 49.558 | 47.7674 | 109.2219 | 63.0833 | 62.6956 | 61.9269 | 61.2168 | 60.4646 | 59.6404 | 58.7728 | 57.7581 | 56.7201 | 54.8903 | 52.6653 | 50.4924 | 48.7072
|  |  | ST |  |  | 109.8095 | 109.8095 | 73.1231 | 73.054 | 72.9829 | 72.8959 | 72.7932 | 72.6647 | 72.5598 | 72.4485 | 71.9599 | 70.661 | 69.4119 | 68.2349 | 106.835 | 106.835 | 71.4582 | 71.3171 | 71.172 | 70.9942 | 70.7844 | 70.5221 | 70.3078 | 70.0337 | 69.4649 | 68.5668 | 67.4652 | 66.2486 | 109.2219 | 109.2219 | 72.3625 | 72.3088 | 72.2537 | 72.1861 | 72.1064 | 72.0067 | 71.9252 | 71.8388 | 71.5282 | 69.9954 | 68.5212 | 67.1322
|  |  | FS |  |  | 109.8095 | 109.8095 | 109.8095 | 73.1248 | 73.1047 | 73.0814 | 73.053 | 73.0174 | 72.9759 | 72.9292 | 72.8305 | 72.6979 | 72.5943 | 72.5166 | 106.835 | 106.835 | 106.835 | 71.4618 | 71.4207 | 71.373 | 71.3151 | 71.2424 | 71.1576 | 71.0624 | 70.8606 | 70.5899 | 70.3783 | 70.2195 | 109.2219 | 109.2219 | 109.2219 | 72.3638 | 72.3482 | 72.3301 | 72.308 | 72.2804 | 72.2482 | 72.212 | 72.1353 | 72.0325 | 71.952 | 71.8917
EAST CLAYDON GSP | BICESTER NORTH | BICESTER NORTH | MINIMUM HEADROOM | SP5972023735 | YES | 1.1402 | -38.0923 | -38.8633 | -40.1425 | -41.4502 | -43.5952 | -45.5945 | -5.2501 | -7.4954 | -9.2435 | -13.3135 | -21.4461 | -27.6324 | -31.8028 | -7.9324 | -54.1483 | -55.0558 | -56.5615 | -58.1007 | -60.3045 | -62.4083 | -22.2542 | -24.6872 | -26.5588 | -30.7107 | -39.2959 | -45.552 | -50.0785 | -7.7954 | -53.871 | -54.7762 | -56.2781 | -57.8134 | -60.2045 | -62.4528 | -22.3668 | -24.9197 | -26.8983 | -31.4235 | -40.5802 | -47.4368 | -52.1816
|  |  | CT |  |  | 1.1402 | -38.0923 | -38.8633 | -40.1425 | -41.4502 | -43.5952 | -45.5945 | -5.2501 | -7.4954 | -9.2435 | -13.3135 | -21.4461 | -27.6324 | -31.8028 | 37.2155 | 37.2115 | 37.2056 | 37.1998 | 37.1935 | 28.3004 | 25.7254 | 22.8638 | 20.2996 | 18.2794 | 77.8751 | 76.8405 | 75.9151 | 75.5782 | 37.2105 | 37.2029 | 37.1917 | 37.1806 | 37.1686 | 28.3062 | 25.5195 | 22.4771 | 19.7941 | 17.6599 | 76.5617 | 74.5907 | 72.8276 | 72.1858
|  |  | LW |  |  | 1.1402 | -38.0923 | -38.8633 | -40.1425 | -41.4502 | -43.5952 | -45.5945 | -5.2501 | -7.4954 | -9.2435 | -13.3135 | -21.4461 | -27.6324 | -31.8028 | -7.9324 | -54.1483 | -55.0558 | -56.5615 | -58.1007 | -60.3045 | -62.4083 | -22.2542 | -24.6872 | -26.5588 | -30.7107 | -39.2959 | -45.552 | -50.0785 | -7.7954 | -53.871 | -54.7762 | -56.2781 | -57.8134 | -60.2045 | -62.4528 | -22.3668 | -24.9197 | -26.8983 | -31.4235 | -40.5802 | -47.4368 | -52.1816
|  |  | ST |  |  | 39.4703 | 39.4699 | 39.4693 | 39.4686 | 39.4678 | 39.2092 | 38.9684 | 29.2953 | 27.4264 | 25.9721 | 79.6043 | 77.9828 | 75.7905 | 73.4686 | 37.2207 | 37.2205 | 37.2202 | 37.2199 | 37.2195 | 37.0939 | 27.6489 | 25.594 | 23.5457 | 21.9152 | 78.0748 | 76.7728 | 74.8628 | 72.8163 | 37.2204 | 37.22 | 37.2194 | 37.2188 | 37.2181 | 36.9789 | 27.5261 | 25.4131 | 23.2938 | 21.6335 | 77.4595 | 75.8847 | 73.7336 | 71.452
|  |  | FS |  |  | 39.4705 | 39.4702 | 39.4699 | 39.4694 | 39.4689 | 39.4684 | 39.357 | 39.238 | 39.0884 | 38.9423 | 38.7979 | 30.549 | 80.5305 | 80.3817 | 37.2208 | 37.2206 | 37.2205 | 37.2203 | 37.22 | 37.2197 | 37.1657 | 37.1079 | 37.0353 | 36.9643 | 36.8943 | 27.168 | 78.8186 | 78.7464 | 37.2205 | 37.2202 | 37.22 | 37.2195 | 37.2191 | 37.2186 | 37.1156 | 37.0055 | 36.8671 | 36.732 | 36.5985 | 26.924 | 78.3591 | 78.2215
EALING GSP | BOSTON MANOR ROAD | BOSTON MANOR ROAD | MINIMUM HEADROOM | TQ 17043 78092 | YES | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757
|  |  | CT |  |  | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757
|  |  | LW |  |  | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757
|  |  | ST |  |  | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757
|  |  | FS |  |  | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 53.5229 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.7399 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757 | 48.6757
BOTLEY WOOD GSP | BOTLEY WOOD BSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU 54073 09759 | NO | 87.9477 | 87.9477 | 87.9477 | 87.7935 | 101.8223 | 101.6623 | 101.4971 | 101.2414 | 101.1547 | 100.8778 | 99.9772 | 87.7935 | 101.1547 | 87.9477 | 76.2148 | 76.1641 | 76.1031 | 75.9119 | 92.0327 | 91.8251 | 91.6082 | 91.3136 | 91.214 | 90.8583 | 89.5928 | 75.9119 | 91.214 | 76.2148 | 79.6147 | 79.591 | 79.5625 | 79.4065 | 94.0956 | 93.9222 | 93.7418 | 93.4718 | 93.3632 | 93.0219 | 91.9508 | 79.4065 | 93.3632 | 79.6147
|  |  | CT |  |  | 87.9477 | 87.9477 | 102.1333 | 102.0004 | 101.8632 | 101.7199 | 101.5714 | 101.3458 | 101.3146 | 101.2075 | 100.7585 | 102.0004 | 101.3146 | 87.9477 | 76.2268 | 76.1827 | 76.1031 | 75.9119 | 92.1379 | 91.936 | 91.7475 | 91.4933 | 91.4014 | 91.127 | 89.8409 | 75.9119 | 91.4014 | 76.2268 | 79.6203 | 79.5997 | 79.5625 | 79.4139 | 94.1691 | 94.0135 | 93.8614 | 93.6439 | 93.5885 | 93.4201 | 92.4249 | 79.4139 | 93.5885 | 79.6203
|  |  | LW |  |  | 87.9477 | 87.9477 | 102.1333 | 102.0004 | 101.8632 | 101.7199 | 101.5714 | 101.3458 | 101.3146 | 101.2075 | 100.7585 | 102.0004 | 101.3146 | 87.9477 | 76.2148 | 76.1641 | 92.4921 | 92.2657 | 92.0327 | 91.8251 | 91.6082 | 91.3136 | 91.214 | 90.9078 | 89.9129 | 92.2657 | 91.214 | 76.2148 | 79.6147 | 79.591 | 94.4542 | 94.2776 | 94.0956 | 93.9222 | 93.7418 | 93.484 | 93.4208 | 93.2207 | 92.5166 | 94.2776 | 93.4208 | 79.6147
|  |  | ST |  |  | 87.9477 | 87.9477 | 87.9477 | 87.7935 | 101.8223 | 101.6623 | 101.4971 | 101.2414 | 101.1547 | 100.8778 | 99.9772 | 87.7935 | 101.1547 | 87.9477 | 76.2463 | 76.2078 | 76.1587 | 75.945 | 92.1385 | 91.9276 | 91.7089 | 91.4066 | 91.273 | 90.8583 | 89.5928 | 75.945 | 91.273 | 76.2463 | 79.6294 | 79.6115 | 79.5885 | 79.4065 | 94.1233 | 93.9395 | 93.7493 | 93.4718 | 93.3632 | 93.0219 | 91.9508 | 79.4065 | 93.3632 | 79.6294
|  |  | FS |  |  | 87.9477 | 87.9477 | 87.9477 | 87.8365 | 101.9088 | 101.7938 | 101.6736 | 101.4884 | 101.4649 | 101.3895 | 100.6494 | 87.8365 | 101.4649 | 87.9477 | 76.2268 | 76.1827 | 76.1031 | 75.9119 | 92.1379 | 91.936 | 91.7475 | 91.4933 | 91.4014 | 91.127 | 89.8409 | 75.9119 | 91.4014 | 76.2268 | 79.6203 | 79.5997 | 79.5625 | 79.4139 | 94.1691 | 94.0135 | 93.8614 | 93.6439 | 93.5885 | 93.4201 | 92.4249 | 79.4139 | 93.5885 | 79.6203
MANNINGTON GSP | BOURNEMOUTH | BOURNEMOUTH | MINIMUM HEADROOM | SZ 06265 92437 | YES | 117.1336 | 88.1938 | 87.2391 | 86.0354 | 84.7885 | 81.4507 | 78.5155 | 76.3501 | 73.457 | 70.6544 | 64.3449 | 49.4929 | 36.0484 | 24.9796 | 117.342 | 88.3418 | 87.1442 | 85.7051 | 84.2241 | 81.2803 | 78.4917 | 75.8568 | 73.1238 | 70.4074 | 64.4048 | 49.1965 | 35.0558 | 22.8162 | 116.814 | 87.8297 | 86.6539 | 85.2498 | 83.7809 | 80.3414 | 77.1632 | 74.2264 | 71.2394 | 68.281 | 61.7718 | 45.4557 | 30.5324 | 18.0023
|  |  | CT |  |  | 117.1336 | 88.1938 | 87.2391 | 86.0354 | 84.7885 | 81.4507 | 78.5155 | 76.3501 | 73.457 | 70.6544 | 64.3449 | 49.4929 | 36.0484 | 24.9796 | 117.342 | 116.7847 | 87.1442 | 85.7051 | 84.2241 | 82.6716 | 79.1682 | 75.8568 | 73.1238 | 70.4074 | 65.5615 | 51.1134 | 38.3456 | 27.7568 | 116.814 | 116.2665 | 86.6539 | 85.2498 | 83.7809 | 82.2257 | 78.0713 | 74.2264 | 71.2394 | 68.281 | 62.9855 | 47.1262 | 33.4227 | 22.4928
|  |  | LW |  |  | 117.1336 | 88.1938 | 87.2391 | 86.0354 | 84.7885 | 81.4507 | 78.5155 | 76.3501 | 73.457 | 70.6544 | 64.3449 | 49.4929 | 36.0484 | 24.9796 | 117.3611 | 88.3418 | 87.2198 | 85.8053 | 84.3407 | 81.2803 | 78.4917 | 76.2722 | 73.3487 | 70.4892 | 64.4048 | 49.1965 | 35.0558 | 22.8162 | 116.8362 | 87.8297 | 86.7388 | 85.3633 | 83.916 | 80.3414 | 77.1632 | 74.752 | 71.5971 | 68.53 | 61.7718 | 45.4557 | 30.5324 | 18.0023
|  |  | ST |  |  | 117.7949 | 117.0918 | 88.2365 | 87.5857 | 86.805 | 84.7834 | 82.8029 | 80.8908 | 78.5426 | 76.6811 | 72.9534 | 64.9257 | 57.0505 | 49.6016 | 118.1271 | 117.3116 | 88.3898 | 87.6243 | 86.7058 | 84.6753 | 82.6691 | 80.7062 | 78.3449 | 76.3424 | 72.468 | 63.8508 | 55.3418 | 47.1538 | 117.5919 | 116.7881 | 87.8779 | 87.134 | 86.2415 | 84.0353 | 81.8485 | 79.7177 | 77.1297 | 75.0284 | 70.874 | 61.8441 | 53.0071 | 44.6083
|  |  | FS |  |  | 118.1339 | 117.5683 | 89.0359 | 88.7963 | 88.5207 | 88.1168 | 87.3554 | 86.4758 | 85.4976 | 84.5266 | 83.1699 | 80.2972 | 77.9821 | 75.7454 | 118.5203 | 117.8642 | 89.3225 | 89.0451 | 88.7252 | 88.2503 | 87.5045 | 86.629 | 85.6729 | 84.7209 | 83.3192 | 80.2682 | 77.6802 | 75.1757 | 117.9795 | 117.3328 | 88.7919 | 88.5181 | 88.2031 | 87.7415 | 86.9162 | 85.9589 | 84.9014 | 83.8507 | 82.3582 | 79.1247 | 76.4604 | 73.8852
BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL MAIN | MINIMUM HEADROOM | SU 86026 69422 | YES | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.8472 | 129.8472 | 129.8472 | 129.8472 | 129.8472 | 129.8472 | 129.8472 | 113.2304 | 112.7231 | 112.7231 | 112.7231 | 85.4836 | 83.3316 | 80.8696 | 77.9824 | 75.1652 | 72.3324 | 67.7217 | 62.3561 | 57.51 | 52.8288 | 84.6351 | 84.599 | 84.5185 | 84.3974 | 84.2736 | 84.1465 | 84.0011 | 82.8732 | 80.2391 | 77.5904 | 73.2793 | 68.2626 | 63.7314 | 59.388
|  |  | CT |  |  | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 147.0417 | 147.0417 | 147.0417 | 147.0417 | 147.0417 | 147.0417 | 147.0417 | 113.2659 | 112.7831 | 112.7231 | 112.7231 | 112.7231 | 83.3748 | 80.8696 | 77.9824 | 75.1652 | 72.3324 | 67.7217 | 62.3561 | 57.51 | 52.8288 | 84.6375 | 84.6053 | 84.533 | 84.4085 | 84.2844 | 84.1491 | 84.0011 | 82.8732 | 80.2391 | 77.5904 | 73.2793 | 68.2626 | 63.7314 | 59.388
|  |  | LW |  |  | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 147.0417 | 147.0417 | 147.0417 | 147.0417 | 147.0417 | 147.0417 | 147.0417 | 113.2304 | 112.7231 | 112.7231 | 112.7231 | 85.4836 | 83.3316 | 81.0895 | 130.4494 | 130.4494 | 130.4494 | 130.4494 | 79.9674 | 75.0203 | 70.7681 | 84.6351 | 84.599 | 84.5185 | 84.3974 | 84.2736 | 84.1465 | 84.0141 | 140.0823 | 140.0823 | 140.0823 | 140.0823 | 140.0823 | 81.2558 | 77.3109
|  |  | ST |  |  | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.8472 | 129.8472 | 129.8472 | 129.8472 | 147.5735 | 147.5735 | 147.5735 | 113.786 | 113.187 | 112.7231 | 112.7231 | 112.7231 | 112.7231 | 84.5401 | 83.0744 | 81.2557 | 79.3385 | 76.6153 | 130.9812 | 130.9812 | 84.6031 | 84.672 | 84.6322 | 84.5967 | 84.5054 | 84.4 | 84.3147 | 84.2179 | 84.6318 | 84.5244 | 84.1758 | 81.6295 | 140.6142 | 140.6142 | 140.6142
|  |  | FS |  |  | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.3154 | 129.8472 | 129.8472 | 129.8472 | 129.8472 | 129.8472 | 129.8472 | 129.8472 | 113.9755 | 113.7559 | 113.5498 | 113.1913 | 112.7506 | 112.7231 | 112.7231 | 113.2549 | 113.2549 | 113.2549 | 113.2549 | 84.4856 | 82.5833 | 81.1089 | 84.6847 | 84.6701 | 84.6563 | 84.6325 | 84.6032 | 84.5791 | 84.5511 | 85.0478 | 85.0073 | 84.9632 | 84.865 | 84.7151 | 84.6028 | 84.5157
BRAMLEY (FLEE) | BRACKNELL RESERVE | BRACKNELL RESERVE | MINIMUM HEADROOM | SU 86026 69422 | YES | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 791.9344 | 791.8813 | 791.7595 | 791.4974 | 791.2333 | 790.9278 | 790.5862 | 790.1738 | 789.836 | 789.4914 | 789.0679 | 788.2847 | 787.4688 | 786.6781 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002
|  |  | CT |  |  | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 791.9369 | 791.8878 | 791.7748 | 791.4974 | 791.2333 | 790.9278 | 790.5862 | 790.1738 | 789.836 | 789.4914 | 789.0679 | 788.2847 | 787.4688 | 786.6781 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002
|  |  | LW |  |  | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 791.9344 | 791.8813 | 791.7595 | 791.5289 | 791.3001 | 791.0625 | 790.8274 | 790.5944 | 790.3137 | 790.0201 | 789.4556 | 788.4621 | 787.6031 | 786.9057 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002
|  |  | ST |  |  | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 791.979 | 791.9363 | 791.8934 | 791.6866 | 791.4552 | 791.1964 | 790.9016 | 790.5356 | 790.2527 | 789.9489 | 789.6214 | 789.0538 | 788.4927 | 787.9568 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002
|  |  | FS |  |  | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 863.9258 | 791.9898 | 791.964 | 791.9599 | 791.9189 | 791.8636 | 791.8039 | 791.7333 | 791.6398 | 791.5319 | 791.4079 | 791.1288 | 790.7131 | 790.3553 | 790.0755 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002 | 741.4002
EALING GSP | BRIDGE ROAD | BRIDGE ROAD | MINIMUM HEADROOM | TQ 14778 75741 | YES | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 86.7532 | 86.7106 | 86.6107 | 86.5015 | 86.3911 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 68.3164 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 70.0638
|  |  | CT |  |  | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 86.7562 | 86.7188 | 86.6303 | 86.5341 | 86.437 | 86.3327 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 69.4165 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 71.1617
|  |  | LW |  |  | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 86.7532 | 86.7106 | 86.6107 | 86.5015 | 86.3911 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 68.3164 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 70.0638
|  |  | ST |  |  | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 86.8069 | 86.7534 | 86.7164 | 86.6638 | 86.6011 | 86.5346 | 86.4672 | 86.4068 | 86.3407 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 86.2925 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385
|  |  | FS |  |  | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 96.1272 | 101.0114 | 101.0114 | 86.8146 | 86.8099 | 86.8026 | 86.7826 | 86.7596 | 86.7347 | 86.7092 | 86.6822 | 86.6549 | 86.6274 | 86.5727 | 86.4633 | 91.2323 | 91.1767 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 88.8385 | 93.7227 | 93.7227
BRAMLEY (FLEE) | BURGHFIELD MAIN | BURGHFIELD MAIN | MINIMUM HEADROOM | SU 69442 70509 | YES | 125.5788 | 125.5788 | 125.5788 | 67.3643 | 67.054 | 66.74 | 66.4315 | 64.354 | 63.9944 | 63.616 | 62.8805 | 60.1911 | 57.3881 | 54.8175 | 119.6055 | 119.5299 | 119.3842 | 57.3573 | 56.9927 | 56.6237 | 56.2612 | 54.5956 | 54.1729 | 53.7283 | 52.864 | 49.7038 | 46.41 | 43.3893 | 116.6336 | 116.6171 | 116.5854 | 53.2097 | 52.8486 | 52.4831 | 52.1241 | 49.9957 | 49.5771 | 49.1367 | 48.2806 | 45.1503 | 41.8877 | 38.8956
|  |  | CT |  |  | 125.5788 | 125.5788 | 125.5788 | 67.3643 | 67.054 | 66.74 | 66.4315 | 64.354 | 63.9944 | 63.616 | 62.8805 | 60.1911 | 57.3881 | 54.8175 | 119.6055 | 119.5299 | 119.3842 | 119.0336 | 118.6999 | 118.3165 | 117.8828 | 115.9581 | 115.5653 | 115.1669 | 114.672 | 112.6682 | 110.8658 | 110.2157 | 116.6336 | 116.6171 | 116.5854 | 116.5091 | 116.4365 | 116.3531 | 116.3044 | 114.5753 | 114.5753 | 114.5753 | 114.5753 | 114.5753 | 114.5753 | 83.1127
|  |  | LW |  |  | 125.5788 | 125.5788 | 125.5788 | 67.3643 | 67.054 | 66.74 | 66.4315 | 64.354 | 63.9944 | 63.616 | 62.8805 | 60.1911 | 57.3881 | 54.8175 | 119.6079 | 119.5336 | 119.3977 | 57.3573 | 56.9927 | 56.6237 | 56.2612 | 54.5956 | 54.1729 | 53.7283 | 52.864 | 49.7038 | 46.41 | 43.3893 | 116.6341 | 116.6179 | 116.5883 | 53.2097 | 52.8486 | 52.4831 | 52.1241 | 49.9957 | 49.5771 | 49.1367 | 48.2806 | 45.1503 | 41.8877 | 38.8956
|  |  | ST |  |  | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 124.7365 | 124.7365 | 124.7365 | 124.7365 | 124.7365 | 124.7365 | 124.7365 | 119.6672 | 119.5959 | 119.5328 | 119.2619 | 118.9589 | 118.4841 | 117.9623 | 116.6499 | 116.1713 | 115.6731 | 115.0025 | 113.6395 | 112.1415 | 111.1414 | 116.647 | 116.6315 | 116.6178 | 116.5588 | 116.4929 | 116.3896 | 116.3044 | 115.4398 | 115.4398 | 115.4398 | 115.4398 | 115.4398 | 115.4398 | 115.4398
|  |  | FS |  |  | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 125.5788 | 119.8177 | 119.6748 | 119.6644 | 119.6116 | 119.5405 | 119.4187 | 119.2832 | 119.1045 | 118.9053 | 118.6855 | 118.2075 | 117.3696 | 116.6022 | 115.9426 | 116.6797 | 116.6486 | 116.6464 | 116.6349 | 116.6194 | 116.5929 | 116.5634 | 116.5246 | 116.4812 | 116.4334 | 116.3294 | 116.3044 | 116.3044 | 116.3044
BRAMLEY (FLEE) | BURGHFIELD RESERVE | BURGHFIELD RESERVE | MINIMUM HEADROOM | SU 69442 70509 | YES | 83.7529 | 73.2168 | 45.0583 | 29.8063 | 27.3062 | 24.5382 | 21.3107 | 17.1498 | 14.1691 | 10.91 | 7.9543 | 4.696 | -5.632 | -9.0202 | 80.6038 | 68.3084 | 45.5494 | 24.6767 | 20.0374 | 16.356 | 12.1475 | 6.8579 | 2.8083 | -1.3549 | -5.6965 | -11.0123 | -24.774 | -30.4141 | 78.4124 | 66.0646 | 43.3886 | 22.4264 | 17.765 | 14.0671 | 9.8399 | 4.5269 | 0.4588 | -3.7234 | -8.0865 | -13.4352 | -27.2711 | -32.9542
|  |  | CT |  |  | 83.7529 | 73.2168 | 72.5965 | 70.655 | 68.6758 | 66.6419 | 64.674 | 62.7369 | 60.2153 | 57.5124 | 52.4303 | 46.393 | 27.6141 | 24.0728 | 80.6038 | 80.2152 | 68.5003 | 65.2523 | 20.0374 | 16.356 | 12.1475 | 6.8579 | 2.8083 | -1.3549 | -5.6965 | -11.0123 | -24.774 | -30.4141 | 78.4124 | 78.0219 | 66.2563 | 62.9938 | 17.765 | 14.0671 | 9.8399 | 4.5269 | 0.4588 | -3.7234 | -8.0865 | -13.4352 | -27.2711 | -32.9542
|  |  | LW |  |  | 83.7529 | 73.2168 | 72.5965 | 70.655 | 68.6758 | 66.6419 | 64.674 | 62.7369 | 60.2153 | 57.5124 | 52.4303 | 46.393 | 27.6141 | 24.0728 | 80.6331 | 68.3084 | 67.5833 | 65.3131 | 62.9989 | 60.6209 | 58.3201 | 56.0553 | 53.1074 | 49.9476 | 44.0069 | 36.9554 | 15.0094 | 10.8894 | 78.4421 | 66.0646 | 65.3362 | 63.0561 | 60.7319 | 58.3433 | 56.0324 | 53.7576 | 50.7965 | 47.6225 | 41.6549 | 34.5678 | 12.5188 | 8.3679
|  |  | ST |  |  | 83.9307 | 83.7221 | 74.1531 | 29.8063 | 27.3062 | 24.5382 | 21.3107 | 17.1498 | 14.1691 | 10.91 | 7.9543 | 4.696 | -5.632 | -9.0202 | 80.8419 | 80.5969 | 69.4032 | 24.6767 | 21.7532 | 18.5163 | 14.7422 | 9.8765 | 6.391 | 2.5799 | -0.87608 | -4.6843 | -16.7587 | -20.716 | 78.6519 | 78.4058 | 67.1642 | 22.4264 | 19.4903 | 16.2395 | 12.4491 | 7.5625 | 4.062 | 0.23441 | -3.2367 | -7.0625 | -19.1908 | -23.1681
|  |  | FS |  |  | 90.2317 | 90.1438 | 45.0583 | 37.9461 | 37.3656 | 30.8888 | 30.1713 | 29.2105 | 28.0322 | 26.637 | 23.4432 | 19.1411 | 15.7403 | 13.3986 | 91.8231 | 91.7626 | 45.5494 | 34.1956 | 33.5167 | 25.9427 | 25.1037 | 23.9801 | 22.6023 | 20.9708 | 17.2361 | 12.2058 | 8.2299 | 5.4926 | 94.0176 | 94.0175 | 43.3886 | 31.9861 | 31.3043 | 23.6978 | 22.8552 | 21.7267 | 20.343 | 18.7044 | 14.9536 | 9.9014 | 5.9078 | 3.158
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY MAIN | MINIMUM HEADROOM | SU 86530 59483 | YES | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 126.2058 | 83.7779 | 76.2618 | 63.7655 | 51.2665 | 40.9592 | 113.0311 | 113.0311 | 113.0311 | 113.0311 | 84.5798 | 81.6106 | 78.4272 | 74.7377 | 71.0516 | 67.2971 | 59.7777 | 45.903 | 32.0705 | 20.6836 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 82.7597 | 79.5861 | 75.9078 | 72.2314 | 68.4868 | 60.9773 | 47.127 | 33.319 | 21.9534
|  |  | CT |  |  | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 126.2058 | 83.7779 | 76.2618 | 63.7655 | 51.2665 | 40.9592 | 115.8795 | 113.0311 | 113.0311 | 113.0311 | 84.5971 | 81.6106 | 78.4272 | 74.7377 | 71.0516 | 67.2971 | 61.619 | 51.69 | 41.2732 | 31.0756 | 116.1707 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 82.7597 | 79.5861 | 75.9078 | 72.2314 | 68.4868 | 62.8231 | 52.9168 | 42.5242 | 32.3502
|  |  | LW |  |  | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 126.2058 | 83.7779 | 76.2618 | 63.7655 | 51.2665 | 40.9592 | 113.0311 | 113.0311 | 113.0311 | 113.0311 | 84.5798 | 81.9348 | 79.3763 | 76.8521 | 72.6313 | 68.3169 | 59.7777 | 45.903 | 32.0705 | 20.6836 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 83.083 | 80.5323 | 78.0158 | 73.8038 | 69.4986 | 60.9773 | 47.127 | 33.319 | 21.9534
|  |  | ST |  |  | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.2658 | 127.0128 | 126.507 | 79.9267 | 72.7515 | 65.4928 | 116.2213 | 113.0311 | 113.0311 | 113.0311 | 113.0311 | 84.8388 | 82.3915 | 79.4338 | 76.8089 | 74.0164 | 70.3618 | 63.6926 | 55.6249 | 47.5089 | 116.3368 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 83.5383 | 80.5896 | 77.9719 | 75.1871 | 71.5422 | 64.8879 | 56.8359 | 48.735
|  |  | FS |  |  | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 127.5187 | 116.2995 | 116.0328 | 115.9857 | 113.0311 | 113.0311 | 113.0311 | 113.0311 | 113.0311 | 113.0311 | 113.0311 | 84.8528 | 81.2317 | 78.1675 | 75.7136 | 116.3747 | 116.2452 | 116.2223 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 116.0779 | 82.382 | 79.3271 | 76.8807
BRAMLEY (FLEE) | CAMBERLEY RESERVE | CAMBERLEY RESERVE | MINIMUM HEADROOM | SU 86530 59483 | YES | 92.7986 | 92.4577 | 92.3043 | 92.3043 | 92.3043 | 92.3043 | 92.3043 | 85.2133 | 84.4279 | 83.7215 | 82.6137 | 79.083 | 75.3854 | 71.7313 | 91.4924 | 90.9319 | 90.4556 | 90.1138 | 89.836 | 84.8053 | 83.7987 | 82.8207 | 81.8941 | 81.0608 | 79.7539 | 75.6031 | 71.2619 | 66.9719 | 91.7601 | 91.3789 | 91.1663 | 91.1037 | 91.0931 | 91.0931 | 84.6295 | 83.6968 | 82.7942 | 81.9825 | 80.7094 | 76.6663 | 72.3413 | 68.0498
|  |  | CT |  |  | 92.7986 | 92.4577 | 92.3043 | 92.3043 | 92.3043 | 92.3043 | 92.3043 | 85.2133 | 84.4279 | 83.7215 | 82.6137 | 79.083 | 75.3854 | 71.7313 | 92.295 | 91.8197 | 91.4003 | 91.1026 | 90.7744 | 90.6596 | 85.1864 | 84.3181 | 83.474 | 82.673 | 81.3632 | 77.2668 | 73.0079 | 68.7945 | 92.5535 | 92.2334 | 92.0452 | 91.9906 | 91.9572 | 91.9572 | 91.9572 | 85.174 | 84.3555 | 83.5753 | 82.2994 | 78.3093 | 74.0876 | 69.8728
|  |  | LW |  |  | 92.7986 | 92.4577 | 92.3043 | 92.3043 | 92.3043 | 92.3043 | 92.3043 | 85.2133 | 84.4279 | 83.7215 | 82.6137 | 79.083 | 75.3854 | 71.7313 | 91.4924 | 90.9319 | 90.4556 | 90.1138 | 89.836 | 84.8053 | 83.7987 | 82.8207 | 81.8941 | 81.0608 | 79.7539 | 75.6031 | 71.2619 | 66.9719 | 91.7601 | 91.3789 | 91.1663 | 91.1037 | 91.0931 | 91.0931 | 84.6295 | 83.6968 | 82.7942 | 81.9825 | 80.7094 | 76.6663 | 72.3413 | 68.0498
|  |  | ST |  |  | 93.6932 | 93.5007 | 93.4157 | 93.4157 | 93.4157 | 93.4157 | 93.4157 | 93.4157 | 93.4157 | 93.4157 | 93.4157 | 83.6112 | 81.3159 | 79.0341 | 92.5144 | 92.1523 | 91.9401 | 91.7666 | 91.5407 | 91.2045 | 90.9436 | 90.8787 | 85.2952 | 84.5992 | 83.4245 | 80.731 | 78.0312 | 75.3523 | 92.678 | 92.4544 | 92.3461 | 92.3143 | 92.2729 | 92.2113 | 92.2045 | 92.2045 | 92.2045 | 85.4527 | 84.3137 | 81.69 | 79.0603 | 76.4327
|  |  | FS |  |  | 93.9022 | 93.8432 | 93.8174 | 93.8174 | 93.8174 | 93.8174 | 93.8174 | 93.8174 | 93.8174 | 93.8174 | 93.8174 | 93.8174 | 93.8174 | 93.8174 | 92.761 | 92.6563 | 92.6044 | 92.5404 | 92.4584 | 92.338 | 92.205 | 92.0528 | 91.9094 | 91.7744 | 91.5472 | 91.3079 | 91.2667 | 84.748 | 92.8939 | 92.8265 | 92.796 | 92.7842 | 92.7692 | 92.7471 | 92.7228 | 92.6949 | 92.6686 | 92.6439 | 92.6063 | 92.6063 | 92.6063 | 92.6063
IVER 132KV | CHALVEY BSP | CHALVEY BSP | MINIMUM HEADROOM | SU 96669 79364 | YES | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 85.4706 | 84.6081 | 83.7257 | 82.8386 | 81.5848 | 80.4766 | 78.3808 | 73.3717 | 68.4385 | 64.1238 | 88.6317 | 88.5464 | 88.5464 | 84.6105 | 83.6418 | 82.673 | 81.6819 | 80.6854 | 79.3363 | 78.1508 | 75.9153 | 70.5557 | 65.1422 | 60.3331 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 84.9573 | 83.9611 | 82.9198 | 81.8728 | 80.4799 | 79.2587 | 76.9587 | 71.4374 | 65.9947 | 61.1953
|  |  | CT |  |  | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 85.4706 | 84.6081 | 83.7257 | 82.8386 | 81.5848 | 80.4766 | 78.3808 | 73.3717 | 68.4385 | 64.1238 | 88.6361 | 88.5464 | 88.5464 | 84.8146 | 83.9071 | 82.9467 | 81.9161 | 80.7795 | 79.6072 | 78.5906 | 76.9799 | 73.068 | 69.0984 | 65.1408 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 85.2287 | 84.2462 | 83.1658 | 81.9717 | 80.7492 | 79.6903 | 78.0163 | 73.952 | 69.95 | 66.0017
|  |  | LW |  |  | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 85.4706 | 84.6081 | 83.7257 | 82.8386 | 81.5848 | 80.4766 | 78.3808 | 73.3717 | 68.4385 | 64.1238 | 88.6317 | 88.5464 | 88.5464 | 84.6105 | 83.6418 | 82.673 | 81.6819 | 80.6854 | 79.3363 | 78.1508 | 75.9153 | 70.5557 | 65.1422 | 60.3331 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 84.9573 | 83.9611 | 82.9198 | 81.8728 | 80.4799 | 79.2587 | 76.9587 | 71.4374 | 65.9947 | 61.1953
|  |  | ST |  |  | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 85.3366 | 84.5067 | 83.6751 | 82.9244 | 81.7575 | 79.2296 | 76.3856 | 73.4908 | 88.6832 | 88.6006 | 88.5464 | 88.5464 | 85.1274 | 84.3362 | 83.4913 | 82.5591 | 81.6365 | 80.8047 | 79.5168 | 76.7572 | 73.6941 | 70.5807 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 84.8033 | 83.8414 | 82.8768 | 82.0075 | 80.6638 | 77.7974 | 74.6331 | 71.4256
|  |  | FS |  |  | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 89.7156 | 85.0184 | 85.247 | 84.5385 | 88.7077 | 88.6565 | 88.6167 | 88.5551 | 88.5464 | 88.5464 | 88.5464 | 85.2989 | 84.9843 | 84.7059 | 84.1542 | 83.1339 | 83.2661 | 82.4703 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 89.4943 | 85.4815 | 84.4377 | 84.533 | 83.6969
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER & HUNSTON | MINIMUM HEADROOM | SU 92282 07416 | YES | 253.1896 | 234.2127 | 232.4605 | 182.4648 | 180.474 | 178.2899 | 175.9843 | 173.2747 | 170.5866 | 167.6909 | 162.8396 | 148.1477 | 127.3306 | 118.7138 | 238.542 | 216.1668 | 214.1285 | 165.943 | 163.5913 | 161.0112 | 158.2874 | 155.0866 | 151.9407 | 148.5499 | 142.8743 | 125.689 | 101.3457 | 91.3894 | 239.728 | 217.3944 | 215.3596 | 167.152 | 164.8047 | 162.2293 | 159.5106 | 156.3157 | 153.1755 | 149.7908 | 144.1253 | 126.9821 | 102.7078 | 92.7757
|  |  | CT |  |  | 253.1896 | 234.2127 | 232.4605 | 230.1732 | 227.7384 | 225.318 | 222.9068 | 220.3076 | 216.9711 | 213.4448 | 206.5123 | 179.2611 | 141.2832 | 128.3844 | 256.2624 | 228.357 | 226.5326 | 223.8769 | 221.1116 | 218.1968 | 215.125 | 211.474 | 207.7406 | 203.7707 | 196.9368 | 175.9391 | 147.8349 | 134.0281 | 256.7459 | 229.5627 | 227.741 | 225.0897 | 222.3289 | 219.419 | 216.3522 | 212.7073 | 208.9796 | 205.0156 | 198.1914 | 177.245 | 149.209 | 135.4233
|  |  | LW |  |  | 253.1896 | 234.2127 | 232.4605 | 230.1732 | 227.7384 | 225.318 | 222.9068 | 220.3076 | 216.9711 | 213.4448 | 206.5123 | 179.2611 | 141.2832 | 128.3844 | 238.542 | 216.1668 | 214.1285 | 211.441 | 208.5801 | 205.7363 | 202.9034 | 199.8499 | 196.006 | 191.9352 | 183.9347 | 152.228 | 107.8597 | 92.9635 | 239.728 | 217.3944 | 215.3596 | 212.6769 | 209.8213 | 206.9825 | 204.1547 | 201.1065 | 197.2691 | 193.2087 | 185.2283 | 153.6063 | 109.3583 | 94.4899
|  |  | ST |  |  | 269.6665 | 246.1384 | 245.2234 | 182.4648 | 180.474 | 178.2899 | 175.9843 | 173.2747 | 170.5866 | 167.6909 | 162.8396 | 148.1477 | 127.3306 | 118.7138 | 257.8507 | 230.0768 | 229.0106 | 165.943 | 163.5913 | 161.0112 | 158.2874 | 155.0866 | 151.9407 | 148.5499 | 142.8743 | 125.689 | 101.3457 | 91.3894 | 258.1171 | 231.2803 | 230.2159 | 167.152 | 164.8047 | 162.2293 | 159.5106 | 156.3157 | 153.1755 | 149.7908 | 144.1253 | 126.9821 | 102.7078 | 92.7757
|  |  | FS |  |  | 274.7141 | 269.3173 | 247.2572 | 217.2812 | 216.6826 | 216.0104 | 215.3042 | 214.42 | 213.4503 | 212.3871 | 210.1473 | 206.139 | 202.7686 | 199.5809 | 262.8787 | 257.262 | 231.188 | 201.1211 | 200.4139 | 199.6198 | 198.7854 | 197.7404 | 196.5945 | 195.3376 | 192.6897 | 187.9534 | 183.9872 | 180.2384 | 263.7526 | 257.8028 | 232.5311 | 202.4653 | 201.7594 | 200.9667 | 200.1339 | 199.0909 | 197.9471 | 196.6925 | 194.0495 | 189.3216 | 185.3624 | 181.62
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL BSP | MINIMUM HEADROOM | SY 65479 80511 | YES | 66.8879 | 66.9672 | 66.9327 | 66.7466 | 50.4826 | 50.1729 | 49.6917 | 49.0933 | 48.3651 | 47.5371 | 45.8137 | 43.2428 | 24.7304 | 18.2533 | 65.868 | 65.6473 | 65.2003 | 45.5314 | 43.2716 | 40.4925 | 36.7392 | 32.2122 | 29.0703 | 25.8143 | 21.4748 | 10.9987 | -8.0576 | -16.2898 | 28.2465 | 28.1137 | 27.852 | 16.512 | 11.7687 | 11.4032 | 10.8589 | 7.9599 | 5.7628 | 3.5156 | 0.30235 | -7.7687 | -19.2329 | -24.4839
|  |  | CT |  |  | 66.8879 | 78.5354 | 78.2964 | 73.0175 | 71.8985 | 70.0483 | 68.3631 | 66.9441 | 64.519 | 62.0153 | 56.4186 | 44.075 | 24.7304 | 18.2533 | 65.877 | 65.6473 | 65.2003 | 45.5314 | 43.2716 | 40.4925 | 36.7392 | 32.2122 | 29.0703 | 25.8143 | 21.4748 | 10.9987 | -6.0584 | -13.5632 | 28.2489 | 28.1137 | 27.852 | 16.512 | 15.1931 | 13.5743 | 10.9592 | 7.9599 | 5.7628 | 3.5156 | 0.30235 | -7.7687 | -19.2329 | -24.4839
|  |  | LW |  |  | 66.8879 | 78.5354 | 78.2964 | 73.0175 | 71.8985 | 70.0483 | 68.3631 | 66.9441 | 64.519 | 62.0153 | 56.4186 | 44.075 | 24.7304 | 18.2533 | 65.868 | 68.4833 | 67.9952 | 57.6098 | 55.8225 | 53.4633 | 51.2355 | 49.1978 | 46.1572 | 42.9413 | 36.0727 | 19.9197 | -8.0576 | -16.2898 | 28.2465 | 38.3258 | 38.0436 | 32.0504 | 31.0066 | 29.2721 | 27.6934 | 26.3662 | 24.0495 | 21.6606 | 16.3262 | 4.5652 | -13.6998 | -19.917
|  |  | ST |  |  | 67.0013 | 173.6084 | 173.6077 | 77.5141 | 76.4064 | 74.7557 | 72.7534 | 69.9796 | 67.9665 | 65.9646 | 63.2966 | 57.8408 | 47.9144 | 42.9335 | 66.0991 | 151.6127 | 151.5702 | 66.3999 | 64.1423 | 61.1193 | 57.6778 | 53.4076 | 50.5114 | 47.4845 | 43.6812 | 36.1119 | 21.2662 | 14.733 | 28.3804 | 48.4206 | 48.2763 | 37.1201 | 35.8128 | 33.9189 | 31.7943 | 29.2076 | 27.3186 | 25.4427 | 22.9332 | 17.7737 | 8.4121 | 3.645
|  |  | FS |  |  | 67.1575 | 66.9672 | 66.9327 | 66.7466 | 50.4826 | 50.1729 | 49.6917 | 49.0933 | 48.3651 | 47.5371 | 45.8137 | 43.2428 | 41.2648 | 39.8252 | 66.4197 | 66.0293 | 65.9588 | 65.582 | 49.045 | 48.4142 | 47.5816 | 46.5168 | 45.228 | 43.726 | 40.3826 | 35.4339 | 31.5557 | 28.7971 | 28.5651 | 28.3401 | 28.2992 | 28.0801 | 11.7687 | 11.4032 | 10.8589 | 10.1773 | 9.3489 | 8.4011 | 6.3936 | 3.4054 | 1.095 | -0.57627
MELKSHAM GSP | CHIPPENHAM | CHIPPENHAM | MINIMUM HEADROOM | ST 92629 74275 | YES | 36.8188 | -15.8993 | -88.5641 | -94.0763 | -99.643 | -123.8208 | -129.9331 | -135.8761 | -137.7393 | -144.9403 | -159.1931 | -199.3323 | -217.7669 | -228.2285 | 35.6622 | -31.1143 | -116.7138 | -123.204 | -138.7788 | -157.9998 | -165.0125 | -179.8433 | -190.1536 | -200.751 | -206.6712 | -245.7149 | -266.3797 | -278.1933 | 35.7474 | -30.1335 | -115.4729 | -121.9441 | -137.519 | -156.7779 | -163.8807 | -178.8238 | -189.2358 | -199.9269 | -206.0501 | -245.4607 | -266.6909 | -278.772
|  |  | CT |  |  | 40.5648 | -15.8993 | -88.5641 | -94.0763 | -99.643 | -123.8208 | -129.9331 | -135.8761 | -137.7393 | -144.9403 | -159.1931 | -199.3323 | -217.7669 | -228.2285 | 35.6622 | 35.3146 | -36.8251 | -45.5718 | -138.7788 | -149.5755 | -162.8408 | -179.8433 | -190.1536 | -200.751 | -206.6712 | -234.661 | -251.8353 | -265.138 | 35.7474 | 35.7133 | -35.8772 | -44.5932 | -137.519 | -148.2857 | -161.7052 | -178.8238 | -189.2358 | -199.9269 | -206.0501 | -234.7334 | -252.6842 | -266.2359
|  |  | LW |  |  | 40.5648 | -15.8993 | -88.5641 | -94.0763 | -99.643 | -123.8208 | -129.9331 | -135.8761 | -137.7393 | -144.9403 | -159.1931 | -199.3323 | -217.7669 | -228.2285 | 39.4113 | -31.1143 | -116.7138 | -123.204 | -129.7581 | -157.9998 | -165.0125 | -171.9197 | -174.7938 | -183.1084 | -199.3271 | -245.7149 | -266.3797 | -278.1933 | 39.4984 | -30.1335 | -115.4729 | -121.9441 | -128.4792 | -156.7779 | -163.8807 | -170.8218 | -173.7848 | -182.1737 | -198.6837 | -245.4607 | -266.6909 | -278.772
|  |  | ST |  |  | 36.8188 | 36.8183 | -24.2132 | -30.3444 | -94.0993 | -102.9547 | -113.4095 | -127.0683 | -134.9366 | -143.3994 | -151.1718 | -166.6567 | -177.5466 | -186.5684 | 35.7039 | 35.6596 | -37.8271 | -45.4393 | -123.3154 | -133.6503 | -145.8758 | -161.8858 | -171.0394 | -180.9568 | -189.9689 | -208.7979 | -221.3422 | -231.64 | 35.7916 | 35.747 | -36.8778 | -44.4606 | -122.0525 | -132.4134 | -144.6554 | -160.6641 | -169.8585 | -179.7765 | -188.8469 | -207.7706 | -220.4467 | -230.9109
|  |  | FS |  |  | 36.819 | 36.8186 | 36.8183 | -24.4668 | -27.5484 | -101.0082 | -103.4715 | -106.7935 | -110.949 | -113.807 | -123.0731 | -137.8137 | -144.3023 | -151.7851 | 35.7114 | 35.7081 | 35.695 | -38.127 | -41.7715 | -128.3078 | -131.168 | -135.037 | -139.8766 | -143.5639 | -154.8006 | -172.0762 | -180.5367 | -189.2951 | 35.7981 | 35.7958 | 35.7825 | -37.1768 | -40.8103 | -127.0833 | -129.9595 | -133.8433 | -138.7015 | -142.4036 | -153.6319 | -170.908 | -179.3589 | -188.1243
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ 15716 93165 | YES | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.5487 | 108.4471 | 107.6015 | 88.8982 | 72.749 | 65.7639 | 97.2048 | 97.1137 | 96.9216 | 96.6573 | 96.3685 | 96.1795 | 96.1795 | 96.1795 | 95.9817 | 95.7839 | 84.9103 | 77.1073 | 58.6315 | 50.6973 | 97.9567 | 97.9346 | 97.8881 | 97.824 | 97.759 | 97.759 | 97.759 | 97.759 | 97.5611 | 85.8397 | 83.7939 | 75.753 | 57.5396 | 49.7783
|  |  | CT |  |  | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 109.7114 | 109.1839 | 108.6564 | 107.6015 | 88.8982 | 72.749 | 65.7639 | 97.208 | 97.1246 | 96.9457 | 96.6728 | 96.384 | 96.1795 | 96.1795 | 96.1795 | 95.9817 | 95.7839 | 85.1715 | 79.1399 | 67.5148 | 60.8375 | 97.9574 | 97.9372 | 97.8939 | 97.8278 | 97.759 | 97.759 | 97.759 | 97.759 | 97.5611 | 85.935 | 84.1056 | 77.7798 | 66.3113 | 59.739
|  |  | LW |  |  | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 109.7114 | 109.1839 | 108.6564 | 107.6015 | 88.8982 | 72.749 | 65.7639 | 97.2048 | 97.1137 | 96.9216 | 96.6573 | 96.3685 | 96.1795 | 96.1795 | 97.2406 | 96.7131 | 96.1856 | 85.0735 | 77.1073 | 58.6315 | 50.6973 | 97.9567 | 97.9346 | 97.8881 | 97.824 | 97.759 | 97.759 | 97.759 | 98.82 | 98.2925 | 97.765 | 84.0201 | 75.753 | 57.5396 | 49.7783
|  |  | ST |  |  | 108.6614 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.5487 | 108.4471 | 108.2439 | 93.0945 | 84.0976 | 79.2941 | 97.3455 | 97.1826 | 97.0883 | 96.889 | 96.6496 | 96.2574 | 96.1795 | 96.1795 | 96.0779 | 95.9763 | 84.9103 | 81.4418 | 71.1431 | 65.752 | 97.9907 | 97.9513 | 97.9284 | 97.8802 | 97.8222 | 97.759 | 97.759 | 97.759 | 97.6573 | 85.8397 | 83.7939 | 80.0732 | 69.9089 | 64.5784
|  |  | FS |  |  | 108.7398 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 108.6503 | 109.5368 | 109.5368 | 97.8482 | 97.2353 | 97.2137 | 97.1596 | 97.0908 | 96.9745 | 96.8501 | 96.7055 | 96.5531 | 96.3924 | 96.1795 | 96.1795 | 97.066 | 97.066 | 98.0942 | 97.964 | 97.9588 | 97.9457 | 97.929 | 97.9009 | 97.8707 | 97.8357 | 97.7988 | 97.7599 | 97.759 | 97.759 | 98.6454 | 85.8608
IVER 132KV | CIPPENHAM | CIPPENHAM | MINIMUM HEADROOM | SU 96266 79634 | YES | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8053 | 102.7721 | 102.7388 | 102.6724 | 102.5063 | 102.3401 | 102.174 | 86.5462 | 86.4896 | 86.3558 | 86.1856 | 86.0106 | 85.8266 | 85.7182 | 85.6011 | 85.4847 | 85.4245 | 85.3342 | 85.1083 | 84.8824 | 84.6566 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 88.9437 | 88.877 | 88.8103 | 88.6768 | 88.3432 | 88.0096 | 87.676
|  |  | CT |  |  | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8053 | 102.7721 | 102.7388 | 102.6724 | 102.5063 | 102.3401 | 102.174 | 86.5469 | 86.4916 | 86.3605 | 86.1856 | 86.0106 | 85.8266 | 85.7182 | 85.6011 | 85.4847 | 85.4245 | 85.3342 | 85.1083 | 84.8824 | 84.6566 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 88.9437 | 88.877 | 88.8103 | 88.6768 | 88.3432 | 88.0096 | 87.676
|  |  | LW |  |  | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8053 | 102.7721 | 102.7388 | 102.6724 | 102.5063 | 102.3401 | 102.174 | 86.5462 | 86.4896 | 86.3558 | 86.1899 | 86.0211 | 85.8499 | 85.7319 | 85.652 | 85.5646 | 85.4923 | 85.4471 | 85.3342 | 85.2212 | 85.1083 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 88.9771 | 88.9437 | 88.9104 | 88.8437 | 88.6768 | 88.51 | 88.3432
|  |  | ST |  |  | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 86.5718 | 86.5526 | 86.5111 | 86.4185 | 86.3081 | 86.2169 | 86.1179 | 86.0026 | 85.898 | 85.7873 | 85.7211 | 85.6333 | 85.56 | 85.56 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105
|  |  | FS |  |  | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 102.8385 | 86.5808 | 86.5771 | 86.5726 | 86.5446 | 86.5086 | 86.4825 | 86.4539 | 86.4167 | 86.3759 | 86.3315 | 86.2419 | 86.0787 | 85.9273 | 85.7938 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105 | 89.0105
MINETY GSP | CIRENCESTER BSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP 02701 00368 | YES | -86.204 | -187.3899 | -353.881 | -357.5704 | -361.3183 | -365.1966 | -369.0319 | -372.8949 | -377.1216 | -381.6782 | -390.3641 | -405.0991 | -451.6634 | -455.9409 | -106.8693 | -226.0676 | -392.6681 | -397.0093 | -401.419 | -405.9821 | -410.4944 | -415.0383 | -420.0104 | -425.3711 | -435.5894 | -452.9007 | -507.7197 | -512.7228 | -106.8392 | -225.6748 | -392.2734 | -396.6018 | -400.9987 | -405.5486 | -410.0479 | -414.5789 | -419.5369 | -424.8825 | -435.0725 | -452.3412 | -507.007 | -512.0096
|  |  | CT |  |  | -86.204 | -187.3899 | -353.881 | -357.5704 | -361.3183 | -365.1966 | -369.0319 | -372.8949 | -377.1216 | -381.6782 | -390.3641 | -405.0991 | -451.6634 | -455.9409 | -39.3405 | -85.6766 | -303.074 | -352.3212 | -358.2691 | -365.5395 | -374.1455 | -385.358 | -392.0104 | -398.8597 | -405.5575 | -416.4151 | -447.3032 | -454.3025 | -39.5168 | -85.7125 | -302.9541 | -352.0525 | -357.9835 | -365.2332 | -373.8144 | -384.9943 | -391.6282 | -398.4585 | -405.1405 | -415.9784 | -446.7886 | -453.7859
|  |  | LW |  |  | -86.204 | -187.3899 | -353.881 | -357.5704 | -361.3183 | -365.1966 | -369.0319 | -372.8949 | -377.1216 | -381.6782 | -390.3641 | -405.0991 | -451.6634 | -455.9409 | -106.8693 | -226.0676 | -392.6681 | -397.0093 | -401.419 | -405.9821 | -410.4944 | -415.0383 | -420.0104 | -425.3711 | -435.5894 | -452.9007 | -507.7197 | -512.7228 | -106.8392 | -225.6748 | -392.2734 | -396.6018 | -400.9987 | -405.5486 | -410.0479 | -414.5789 | -419.5369 | -424.8825 | -435.0725 | -452.3412 | -507.007 | -512.0096
|  |  | ST |  |  | 28.6352 | 23.1421 | -277.0297 | -318.3211 | -323.6568 | -329.539 | -336.5422 | -345.7534 | -350.9096 | -356.5607 | -361.5911 | -369.2538 | -393.8814 | -398.2044 | 18.2004 | 12.6664 | -302.1369 | -350.7764 | -357.0592 | -363.9856 | -372.2327 | -383.0806 | -389.1517 | -395.8067 | -401.7289 | -410.7445 | -439.7479 | -444.8325 | 18.0245 | 12.4913 | -302.0173 | -350.5088 | -356.7727 | -363.6783 | -371.9005 | -382.7156 | -388.7686 | -395.4036 | -401.3083 | -410.2989 | -439.2173 | -444.2904
|  |  | FS |  |  | 70.2106 | 51.9614 | -204.836 | -246.5388 | -262.5784 | -297.2179 | -298.8872 | -301.152 | -303.9886 | -307.3942 | -315.3326 | -325.577 | -333.4576 | -338.561 | 67.1769 | 45.6791 | -218.0286 | -267.1544 | -286.0485 | -326.8536 | -328.8192 | -331.4865 | -334.8273 | -338.8389 | -348.1897 | -360.2544 | -369.535 | -375.5438 | 66.8518 | 45.4195 | -218.149 | -267.1253 | -285.962 | -326.6429 | -328.6026 | -331.2619 | -334.5927 | -338.5922 | -347.9148 | -359.9438 | -369.1974 | -375.1894
EALING GSP | COPLEY DENE | COPLEY DENE | MINIMUM HEADROOM | TQ 17445 80798 | YES | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 34.8228 | 34.0166 | 33.2074 | 32.3982 | 31.5033 | 30.6093 | 28.8261 | 26.1351 | 23.4081 | 20.719 | 34.4473 | 34.4473 | 32.3868 | 31.2877 | 30.1997 | 29.1228 | 28.0502 | 26.9802 | 25.7876 | 24.6019 | 22.2372 | 18.8624 | 15.4196 | 12.0263 | 32.9378 | 32.4996 | 31.4646 | 30.3462 | 29.2391 | 28.1434 | 27.052 | 25.9674 | 24.7784 | 23.5963 | 21.2388 | 17.8743 | 14.442 | 11.0591
|  |  | CT |  |  | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 34.8228 | 34.0166 | 33.2074 | 32.3982 | 31.5033 | 30.6093 | 28.8261 | 26.1351 | 23.4081 | 20.719 | 34.4473 | 34.4473 | 32.3868 | 31.2877 | 30.1997 | 29.1228 | 28.0502 | 26.9802 | 25.7876 | 24.6019 | 22.2372 | 18.8624 | 15.4196 | 12.0263 | 32.9378 | 32.4996 | 31.4646 | 30.3462 | 29.2391 | 28.1434 | 27.052 | 25.9674 | 24.7784 | 23.5963 | 21.2388 | 17.8743 | 14.442 | 11.0591
|  |  | LW |  |  | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 34.8228 | 34.0166 | 33.2074 | 32.3982 | 31.5033 | 30.6093 | 28.8261 | 26.1351 | 23.4081 | 20.719 | 34.4473 | 34.4473 | 32.6096 | 31.6536 | 30.7084 | 29.7735 | 28.8349 | 27.8965 | 26.8518 | 25.7935 | 23.6827 | 20.4973 | 17.2693 | 14.0861 | 32.974 | 32.5916 | 31.6913 | 30.7185 | 29.7568 | 28.8054 | 27.8504 | 26.8955 | 25.8394 | 24.7843 | 22.6799 | 19.5042 | 16.2861 | 13.1126
|  |  | ST |  |  | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 34.9742 | 33.4693 | 31.9975 | 30.5453 | 34.4473 | 34.4473 | 34.4473 | 34.4473 | 33.1808 | 32.8739 | 32.5665 | 32.2602 | 31.9163 | 31.5739 | 30.8841 | 29.1387 | 27.4317 | 25.7178 | 33.1863 | 33.0962 | 32.9052 | 32.6186 | 32.2725 | 31.9603 | 31.6474 | 31.3357 | 30.9858 | 30.6375 | 29.9355 | 28.1595 | 26.4226 | 24.7088
|  |  | FS |  |  | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 38.8746 | 35.3361 | 34.7338 | 34.4473 | 34.4473 | 34.4473 | 34.4473 | 34.4473 | 34.4473 | 34.4473 | 34.4473 | 33.2463 | 33.0932 | 32.789 | 32.0323 | 31.3038 | 30.6052 | 33.3286 | 33.2148 | 33.1905 | 33.0511 | 32.886 | 32.7671 | 32.6491 | 32.4957 | 32.3391 | 32.1833 | 31.8738 | 31.1039 | 30.3626 | 29.6518
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES & WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ 50519 94250 | YES | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -188.4057 | -195.8051 | -200.9406 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -242.7454 | -261.9219 | -272.5338 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -325.9915 | -343.423 | -353.2426
|  |  | CT |  |  | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -188.4057 | -195.8051 | -200.9406 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -174.1087 | -185.9045 | -194.4635 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -270.7736 | -281.6747 | -289.6663
|  |  | LW |  |  | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -188.4057 | -195.8051 | -200.9406 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -242.7454 | -261.9219 | -272.5338 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -325.9915 | -343.423 | -353.2426
|  |  | ST |  |  | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -176.2796 | -180.2803 | -184.011 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -127.5237 | -138.7465 | -146.8855 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -224.0539 | -234.4373 | -242.0659
|  |  | FS |  |  | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -139.639 | -140.1325 | -140.5315 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -72.5279 | -75.7455 | -78.3325 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | -171.2114 | -174.1122 | -176.4455
COWLEY GSP | COWLEY LOCAL (2 X 45) | COWLEY LOCAL (2 X 45) | MINIMUM HEADROOM | SP 56113 03074 | NO | 126.5086 | 126.5086 | 126.5086 | 80.6098 | 79.8277 | 78.9444 | 77.8113 | 76.3446 | 75.07 | 73.6505 | 71.6516 | 66.5512 | 62.8124 | 61.5145 | 116.7012 | 116.7012 | 116.7012 | 64.1581 | 63.2475 | 61.4891 | 59.9763 | 58.0855 | 56.3698 | 54.533 | 51.7574 | 47.7469 | 43.3428 | 41.8181 | 125.8729 | 125.8691 | 125.8625 | 59.3265 | 58.4052 | 56.626 | 55.0954 | 53.1823 | 51.4464 | 49.5879 | 46.7796 | 42.7667 | 38.3612 | 36.836
|  |  | CT |  |  | 137.456 | 137.456 | 137.456 | 80.6098 | 79.8277 | 78.9444 | 78.0038 | 77.022 | 75.7898 | 74.4661 | 71.6516 | 66.5512 | 62.8124 | 61.5145 | 127.6486 | 127.6486 | 127.6486 | 127.6404 | 127.6311 | 61.4891 | 59.9763 | 58.0855 | 56.3698 | 54.533 | 51.7574 | 48.1058 | 44.9642 | 43.0023 | 136.8082 | 136.7942 | 136.7629 | 136.6251 | 134.8511 | 56.626 | 55.0954 | 53.1823 | 51.4464 | 49.5879 | 46.7796 | 43.1258 | 39.9831 | 38.0206
|  |  | LW |  |  | 137.456 | 137.456 | 137.456 | 80.6098 | 79.8277 | 78.9444 | 78.0038 | 77.022 | 75.7898 | 74.4661 | 71.6516 | 66.5512 | 62.8124 | 61.5145 | 127.6486 | 127.6486 | 127.6486 | 64.1581 | 63.2475 | 62.2189 | 61.1235 | 59.9802 | 58.545 | 57.003 | 53.7236 | 47.7469 | 43.3428 | 41.8181 | 136.8087 | 136.7951 | 135.1425 | 59.3265 | 58.4052 | 57.3645 | 56.2562 | 55.0995 | 53.6474 | 52.0872 | 48.7692 | 42.7667 | 38.3612 | 36.836
|  |  | ST |  |  | 137.456 | 137.456 | 137.456 | 137.4511 | 137.446 | 78.9745 | 77.8113 | 76.3446 | 75.07 | 73.6505 | 71.6771 | 69.3535 | 67.1963 | 66.029 | 127.6486 | 127.6486 | 127.6486 | 127.6437 | 127.6385 | 62.2518 | 60.8961 | 59.1864 | 57.7007 | 56.0457 | 53.7452 | 51.031 | 48.4877 | 47.1114 | 136.8157 | 136.809 | 136.7955 | 136.689 | 134.939 | 57.3977 | 56.0259 | 54.2961 | 52.7928 | 51.1182 | 48.7904 | 46.0519 | 43.5077 | 42.131
|  |  | FS |  |  | 126.5086 | 126.5086 | 126.5086 | 126.5073 | 126.5059 | 126.5045 | 137.4504 | 137.4495 | 137.4482 | 137.4479 | 137.4474 | 137.4421 | 85.1884 | 84.4308 | 116.7012 | 116.7012 | 116.7012 | 116.6998 | 116.6984 | 116.697 | 76.4398 | 75.9809 | 75.4306 | 74.7964 | 73.3184 | 70.9735 | 69.4992 | 68.6161 | 125.8729 | 125.8691 | 125.8625 | 125.8379 | 125.802 | 125.76 | 71.7537 | 71.2894 | 70.7326 | 70.0909 | 68.5953 | 66.2227 | 64.731 | 63.8374
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL (2 X 90) | MINIMUM HEADROOM | SP 56113 03074 | NO | 48.1411 | 47.5093 | 46.7562 | 45.5211 | 44.23 | 42.8274 | 41.5338 | 40.6599 | 38.959 | 37.1744 | 33.6739 | 27.5002 | 22.4384 | 18.6358 | 39.997 | 39.2098 | 38.2641 | 36.443 | 34.6233 | 32.5058 | 30.3082 | 27.6263 | 25.1804 | 22.6632 | 19.0592 | 12.9031 | 7.315 | 2.2293 | 40.1387 | 39.3531 | 38.4097 | 36.5935 | 34.7785 | 32.6665 | 30.4748 | 27.8001 | 25.3601 | 22.8491 | 19.2523 | 13.1023 | 7.5119 | 2.4178
|  |  | CT |  |  | 48.1411 | 47.5093 | 46.7562 | 45.5211 | 44.23 | 42.8274 | 41.5338 | 40.6599 | 38.959 | 37.1744 | 33.6739 | 27.5002 | 22.4384 | 18.6358 | 88.0179 | 39.2098 | 38.2641 | 36.443 | 34.6233 | 32.5058 | 30.3082 | 27.6263 | 25.1804 | 22.6632 | 19.0592 | 12.9031 | 7.315 | 2.2293 | 88.0221 | 39.3531 | 38.4097 | 36.5935 | 34.7785 | 32.6665 | 30.4748 | 27.8001 | 25.3601 | 22.8491 | 19.2523 | 13.1023 | 7.5119 | 2.4178
|  |  | LW |  |  | 48.1411 | 47.5093 | 46.7562 | 45.5211 | 44.23 | 42.8274 | 41.5338 | 40.6599 | 38.959 | 37.1744 | 33.6739 | 27.5002 | 22.4384 | 18.6358 | 39.997 | 39.2332 | 38.3228 | 36.8298 | 35.2691 | 33.5736 | 32.0101 | 30.8503 | 28.8245 | 26.7236 | 22.6031 | 15.3417 | 9.398 | 4.9463 | 40.1387 | 39.3772 | 38.4694 | 36.9806 | 35.4244 | 33.7338 | 32.1746 | 31.0194 | 28.9991 | 26.9038 | 22.7939 | 15.5478 | 9.6107 | 5.1558
|  |  | ST |  |  | 87.9865 | 48.2253 | 48.0354 | 47.179 | 46.2027 | 44.8311 | 43.3641 | 41.5263 | 39.943 | 38.2064 | 35.9848 | 32.899 | 29.8046 | 27.1105 | 88.0188 | 40.0986 | 39.869 | 38.8336 | 37.6533 | 35.9949 | 34.2212 | 31.9992 | 30.085 | 28.0234 | 25.4068 | 21.6859 | 18.0452 | 14.878 | 88.0681 | 40.2401 | 40.0112 | 38.9789 | 37.802 | 36.1486 | 34.3802 | 32.1647 | 30.2562 | 28.2007 | 25.5918 | 21.8821 | 18.2498 | 15.0884
|  |  | FS |  |  | 87.9866 | 87.9865 | 87.9864 | 87.9862 | 47.7212 | 47.3494 | 46.9553 | 46.4333 | 45.8328 | 45.1598 | 43.6668 | 41.4072 | 39.6864 | 40.8917 | 88.0188 | 88.0187 | 88.0187 | 85.4717 | 39.4893 | 39.0398 | 38.5632 | 37.9321 | 37.2061 | 36.3925 | 34.5875 | 31.8561 | 29.7768 | 30.734 | 88.073 | 88.0332 | 88.0238 | 85.4584 | 39.6325 | 39.1843 | 38.7092 | 38.08 | 37.3561 | 36.5449 | 34.7452 | 32.0216 | 29.9479 | 30.9091
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU 78324 50817 | YES | 91.2723 | 63.6613 | 9.6019 | -99.4143 | -103.1517 | -106.9413 | -214.8694 | -218.5773 | -223.2138 | -228.1498 | -237.6219 | -246.0702 | -259.8008 | -264.9114 | 84.6348 | 60.7765 | -6.4869 | -116.1705 | -120.5722 | -125.0352 | -233.6236 | -237.9899 | -243.4496 | -249.2618 | -260.4141 | -270.3449 | -286.4862 | -292.4637 | 84.6368 | 60.7804 | -6.2785 | -115.9491 | -120.338 | -124.7881 | -233.3641 | -237.7181 | -243.1625 | -248.9585 | -260.0804 | -269.9939 | -286.1062 | -292.0912
|  |  | CT |  |  | 91.2723 | 63.6613 | 9.6019 | -99.4143 | -103.1517 | -106.9413 | -214.8694 | -218.5773 | -223.2138 | -228.1498 | -237.6219 | -246.0702 | -259.8008 | -264.9114 | 84.6415 | 60.8004 | 13.6636 | 7.7052 | 2.0879 | -109.7728 | -117.3769 | -231.1903 | -238.2993 | -245.5696 | -253.3872 | -261.0363 | -273.4372 | -281.9849 | 84.6428 | 60.8028 | 13.8083 | 7.8666 | 2.2648 | -109.5775 | -117.1602 | -230.9463 | -238.0361 | -245.287 | -253.0872 | -260.7338 | -273.1263 | -281.6838
|  |  | LW |  |  | 91.2723 | 63.6613 | 9.6019 | -99.4143 | -103.1517 | -106.9413 | -214.8694 | -218.5773 | -223.2138 | -228.1498 | -237.6219 | -246.0702 | -259.8008 | -264.9114 | 84.6348 | 60.7765 | -6.4869 | -116.1705 | -120.5722 | -125.0352 | -233.6236 | -237.9899 | -243.4496 | -249.2618 | -260.4141 | -270.3449 | -286.4862 | -292.4637 | 84.6368 | 60.7804 | -6.2785 | -115.9491 | -120.338 | -124.7881 | -233.3641 | -237.7181 | -243.1625 | -248.9585 | -260.0804 | -269.9939 | -286.1062 | -292.0912
|  |  | ST |  |  | 91.2732 | 63.6628 | 27.8996 | 23.6238 | 18.8801 | 14.1405 | 8.5418 | 1.2376 | -3.7256 | -9.1494 | -13.9814 | -18.485 | -26.7977 | -31.8397 | 85.0577 | 61.3853 | 15.0669 | 10.0302 | 4.4423 | -1.1406 | -7.7355 | -16.3394 | -22.1857 | -28.5745 | -34.2654 | -39.5656 | -49.3503 | -55.2792 | 85.0587 | 61.3878 | 15.2104 | 10.1888 | 4.6178 | -0.94834 | -7.5234 | -16.1015 | -21.9303 | -28.2999 | -33.9742 | -39.2613 | -49.021 | -54.9383
|  |  | FS |  |  | 91.2733 | 63.6631 | 63.6628 | 28.0899 | 26.9801 | 25.98 | 24.707 | 22.9755 | 20.8319 | 18.2755 | 12.3406 | 4.4864 | -1.688 | -5.8181 | 85.325 | 61.8749 | 61.8094 | 15.291 | 13.9839 | 12.8059 | 11.3065 | 9.267 | 6.742 | 3.7308 | -3.2601 | -12.5105 | -19.7813 | -24.6435 | 85.3253 | 61.876 | 61.8106 | 15.4338 | 14.1305 | 12.9561 | 11.4611 | 9.4277 | 6.9102 | 3.908 | -3.0619 | -12.2853 | -19.5356 | -24.3849
IVER 132KV | DENHAM | DENHAM | MINIMUM HEADROOM | TQ 01785 87618 | YES | 96.1631 | 68.1578 | 68.1578 | 67.5585 | 65.6412 | 63.7054 | 61.7999 | 59.9004 | 57.5722 | 55.1616 | 50.4826 | 45.6881 | 40.8402 | 36.9836 | 92.1458 | 67.2091 | 66.6772 | 64.3002 | 61.8367 | 59.1233 | 56.1765 | 52.7219 | 49.6075 | 46.4489 | 42.115 | 36.9141 | 31.1707 | 25.6337 | 93.5572 | 67.546 | 66.9798 | 64.6917 | 62.2674 | 59.5531 | 56.6054 | 53.1496 | 50.0342 | 46.8746 | 42.5393 | 37.3367 | 31.5913 | 26.0525
|  |  | CT |  |  | 96.1631 | 68.1578 | 68.1578 | 67.5585 | 65.6412 | 63.7054 | 61.7999 | 59.9004 | 57.5722 | 55.1616 | 50.4826 | 45.6881 | 40.8402 | 36.9836 | 92.1534 | 67.2091 | 66.8555 | 64.3002 | 61.8367 | 59.1233 | 56.1765 | 52.7219 | 49.6075 | 46.4489 | 42.115 | 36.9141 | 31.1707 | 25.6337 | 93.5572 | 67.546 | 67.1452 | 64.6917 | 62.2674 | 59.5531 | 56.6054 | 53.1496 | 50.0342 | 46.8746 | 42.5393 | 37.3367 | 31.5913 | 26.0525
|  |  | LW |  |  | 96.1631 | 68.1578 | 68.1578 | 67.5585 | 65.6412 | 63.7054 | 61.7999 | 59.9004 | 57.5722 | 55.1616 | 50.4826 | 45.6881 | 40.8402 | 36.9836 | 92.1458 | 67.2091 | 66.6772 | 64.407 | 62.145 | 59.8613 | 57.6133 | 55.3724 | 52.6258 | 49.7819 | 44.2619 | 38.6056 | 32.8864 | 28.3365 | 93.5572 | 67.546 | 66.9798 | 64.7958 | 62.5758 | 60.2914 | 58.0427 | 55.801 | 53.0535 | 50.2086 | 44.6869 | 39.0287 | 33.3077 | 28.7563
|  |  | ST |  |  | 96.1631 | 96.1631 | 96.1631 | 68.1578 | 67.2656 | 65.7607 | 64.0488 | 61.9027 | 60.1507 | 58.2638 | 56.2482 | 53.4663 | 50.3633 | 47.4186 | 92.2496 | 92.1362 | 92.1036 | 66.225 | 64.0614 | 62.2861 | 60.2664 | 57.7346 | 55.6677 | 53.4416 | 51.0638 | 47.7819 | 44.1211 | 40.6471 | 93.5572 | 93.5572 | 93.5572 | 66.5606 | 64.4592 | 62.7169 | 60.6966 | 58.164 | 56.0964 | 53.8696 | 51.491 | 48.208 | 44.5461 | 41.0709
|  |  | FS |  |  | 96.1631 | 96.1631 | 96.1631 | 96.1631 | 96.1631 | 68.1578 | 68.1578 | 68.1578 | 68.1578 | 67.9978 | 66.3299 | 63.8289 | 61.7522 | 60.1784 | 92.2883 | 92.2753 | 92.221 | 92.1132 | 92.1036 | 67.2091 | 67.199 | 66.5545 | 65.7969 | 64.9252 | 62.9575 | 60.007 | 57.5571 | 55.7004 | 93.5572 | 93.5572 | 93.5572 | 93.5572 | 93.5572 | 67.546 | 67.4636 | 66.8661 | 66.1496 | 65.3006 | 63.3839 | 60.4371 | 57.9864 | 56.1291
COWLEY GSP | DRAYTON BSP | DRAYTON BSP | MINIMUM HEADROOM | SU 46684 92706 | YES | 164.6337 | 164.6337 | 157.8968 | 157.8947 | 157.8927 | 156.6496 | 154.1708 | 156.0911 | 152.8847 | 149.8038 | 144.1282 | 110.9909 | 93.1411 | 84.7621 | 169.0596 | 159.6141 | 157.945 | 155.4412 | 152.6946 | 149.7686 | 146.8609 | 148.34 | 144.6613 | 141.1297 | 134.6368 | 96.0249 | 74.2444 | 64.6692 | 169.7292 | 159.8526 | 158.183 | 155.6783 | 152.9309 | 150.0039 | 147.0953 | 148.5734 | 144.8936 | 141.361 | 134.8664 | 96.3463 | 74.645 | 65.094
|  |  | CT |  |  | 185.158 | 165.0418 | 163.6202 | 161.4855 | 159.144 | 156.6496 | 154.1708 | 156.0911 | 152.8847 | 149.8038 | 144.1282 | 110.9909 | 93.1411 | 84.7621 | 182.6835 | 182.6808 | 170.6074 | 166.5116 | 163.5075 | 160.0906 | 156.44 | 152.1726 | 148.1866 | 144.3438 | 139.0105 | 116.1334 | 98.0925 | 95.0526 | 184.1744 | 184.1744 | 170.8823 | 166.7524 | 163.7473 | 160.3293 | 156.6775 | 152.4087 | 148.4214 | 144.5775 | 139.2426 | 116.3874 | 98.3987 | 95.3847
|  |  | LW |  |  | 185.158 | 165.0418 | 163.6202 | 161.4855 | 159.144 | 156.6496 | 154.1708 | 156.0911 | 152.8847 | 149.8038 | 144.1282 | 110.9909 | 93.1411 | 84.7621 | 182.6838 | 159.6141 | 157.945 | 155.4412 | 152.6946 | 149.7686 | 146.8609 | 148.34 | 144.6613 | 141.1297 | 134.6368 | 96.0249 | 74.2444 | 64.6692 | 184.1744 | 159.8526 | 158.183 | 155.6783 | 152.9309 | 150.0039 | 147.0953 | 148.5734 | 144.8936 | 141.361 | 134.8664 | 96.3463 | 74.645 | 65.094
|  |  | ST |  |  | 185.2153 | 185.158 | 169.3579 | 169.3505 | 169.3427 | 169.3348 | 167.0608 | 164.2111 | 161.688 | 159.1393 | 155.9944 | 143.5232 | 130.4757 | 131.0956 | 182.8735 | 182.6808 | 176.3145 | 169.6791 | 167.2991 | 164.7618 | 161.9898 | 158.6455 | 155.7006 | 152.7252 | 149.0663 | 133.7631 | 118.5955 | 118.3975 | 184.1744 | 184.1744 | 177.8081 | 169.9431 | 167.5402 | 165.0021 | 162.2291 | 158.8838 | 155.9379 | 152.9616 | 149.3015 | 133.992 | 118.8548 | 118.6732
|  |  | FS |  |  | 164.6337 | 164.6337 | 157.8968 | 157.8947 | 157.8927 | 157.8906 | 162.6126 | 162.6112 | 162.6092 | 162.6088 | 162.5844 | 159.3435 | 156.6506 | 154.3626 | 169.0596 | 169.0111 | 162.2616 | 162.1187 | 160.1938 | 159.466 | 163.3901 | 162.3996 | 161.3374 | 160.2299 | 157.9038 | 154.1001 | 150.9391 | 148.2534 | 169.7292 | 169.7292 | 162.9923 | 162.4858 | 160.5001 | 159.7494 | 163.6594 | 162.6572 | 161.5824 | 160.4709 | 158.1439 | 154.3391 | 151.177 | 148.4905
EALING GSP | EALING | EALING | MINIMUM HEADROOM | TQ 18371 79475 | YES | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 65.0186 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438
|  |  | CT |  |  | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 65.0186 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438
|  |  | LW |  |  | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 65.035 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438
|  |  | ST |  |  | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 65.2323 | 65.075 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438
|  |  | FS |  |  | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 70.5836 | 65.3341 | 65.2663 | 65.1955 | 65.0524 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 64.9234 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438 | 65.9438
EALING GSP | EALING (D) | EALING (D) | MINIMUM HEADROOM | TQ 18371 79475 | YES | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 209.3756 | 208.7847 | 207.6932 | 206.751 | 206.1952 | 205.6265 | 205.0422 | 204.4691 | 203.8542 | 203.2649 | 202.1053 | 201.2872 | 200.5188 | 200.2307 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096
|  |  | CT |  |  | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 209.3756 | 208.7849 | 207.6932 | 206.751 | 206.1952 | 205.6265 | 205.0422 | 204.4691 | 203.8542 | 203.2649 | 202.1053 | 201.2872 | 200.5188 | 200.2307 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096
|  |  | LW |  |  | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 209.3844 | 208.7847 | 207.7325 | 206.7931 | 206.2695 | 205.7453 | 205.2185 | 204.7024 | 204.143 | 203.6023 | 202.5285 | 201.4451 | 200.6806 | 200.2307 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096
|  |  | ST |  |  | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 209.9576 | 209.3669 | 209.0106 | 208.557 | 208.064 | 207.6529 | 207.2198 | 206.8732 | 206.6366 | 206.416 | 205.984 | 205.0344 | 204.0463 | 203.0556 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096
|  |  | FS |  |  | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 234.6421 | 210.0675 | 209.6202 | 209.5278 | 209.3302 | 209.1277 | 208.9675 | 208.8076 | 208.6171 | 208.4252 | 208.2416 | 207.8803 | 207.1321 | 206.6401 | 206.2394 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096 | 205.096
LALEHAM | EAST BEDFONT B | EAST BEDFONT B | MINIMUM HEADROOM | TQ 08394 73826 | NO | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 27.1654 | 27.1654 | 27.1654 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 26.5705 | 26.5705 | 26.5705 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 26.4339 | 26.4339 | 26.4339
|  |  | CT |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 27.1654 | 27.1654 | 27.1654 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 26.5705 | 26.5705 | 26.5705 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 26.4339 | 26.4339 | 26.4339
|  |  | LW |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 27.1654 | 27.1654 | 27.1654 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 26.5705 | 26.5705 | 26.5705 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 26.4339 | 26.4339 | 26.4339
|  |  | ST |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 27.1654 | 27.1654 | 27.1654 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 26.5705 | 26.5705 | 26.5705 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 26.4339 | 26.4339 | 26.4339
|  |  | FS |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 27.1654 | 27.1654 | 27.1654 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 26.5705 | 26.5705 | 26.5705 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 26.4339 | 26.4339 | 26.4339
LALEHAM | EAST BEDFONT A | EAST BEDFONT A | MINIMUM HEADROOM | TQ 08394 73826 | NO | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 91.1929 | 89.3062 | 87.4177 | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 89.8443 | 87.863 | 85.6301 | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 88.7947 | 86.5681 | 84.3395
|  |  | CT |  |  | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 91.1929 | 89.3062 | 87.4177 | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 90.4463 | 88.9407 | 87.168 | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 89.5202 | 87.7056 | 85.8744
|  |  | LW |  |  | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 91.1929 | 89.3062 | 87.4177 | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 89.8443 | 87.863 | 85.6301 | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 88.7947 | 86.5681 | 84.3395
|  |  | ST |  |  | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 92.3743 | 91.138 | 89.9062 | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 91.001 | 89.7905 | 88.5724 | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 90.1888 | 88.7298 | 87.2762
|  |  | FS |  |  | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 96.7758 | 94.5493 | 94.0926 | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 93.5719 | 93.1306 | 92.6834 | 57 | 57 | 57 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 93.2876 | 92.7556 | 92.2167
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | FAREHAM T1A T2A (90MVAS) | MINIMUM HEADROOM | SU 56534 04031 | YES | 16.6245 | 8.2644 | -34.2414 | -53.3551 | -53.9769 | -54.6481 | -55.2772 | -55.9323 | -57.7877 | -59.6879 | -63.5132 | -87.7123 | -96.8923 | -104.7438 | 5.5316 | -4.0773 | -46.6561 | -69.2555 | -69.9907 | -70.7842 | -71.5281 | -72.3026 | -74.2967 | -76.3436 | -80.4669 | -108.18 | -118.1601 | -126.7691 | 8.1893 | -1.1925 | -43.7531 | -65.4856 | -66.1926 | -66.9557 | -67.671 | -68.4158 | -70.3754 | -72.3858 | -76.4349 | -103.2741 | -113.0552 | -121.4758
|  |  | CT |  |  | 16.6245 | 8.2644 | -34.2414 | -53.3551 | -53.9769 | -54.6481 | -55.2772 | -55.9323 | -57.7877 | -59.6879 | -63.5132 | -87.7123 | -96.8923 | -104.7438 | 58.0654 | 57.8208 | -37.2105 | -47.364 | -48.1593 | -49.0934 | -50.076 | -51.2517 | -52.692 | -54.1813 | -56.719 | -72.3114 | -79.1562 | -85.9409 | 60.7233 | 60.4744 | -34.564 | -44.4339 | -45.1986 | -46.0969 | -47.0418 | -48.1724 | -49.5732 | -51.0211 | -53.493 | -68.5661 | -75.2271 | -81.8304
|  |  | LW |  |  | 16.6245 | 8.2644 | -34.2414 | -53.3551 | -53.9769 | -54.6481 | -55.2772 | -55.9323 | -57.7877 | -59.6879 | -63.5132 | -87.7123 | -96.8923 | -104.7438 | 5.5316 | -4.0773 | -46.6561 | -69.2555 | -69.9907 | -70.7842 | -71.5281 | -72.3026 | -74.2967 | -76.3436 | -80.4669 | -108.18 | -118.1601 | -126.7691 | 8.1893 | -1.1925 | -43.7531 | -65.4856 | -66.1926 | -66.9557 | -67.671 | -68.4158 | -70.3754 | -72.3858 | -76.4349 | -103.2741 | -113.0552 | -121.4758
|  |  | ST |  |  | 69.4102 | 69.0943 | -25.7369 | -34.3326 | -34.8989 | -35.8572 | -36.8585 | -38.006 | -39.2405 | -40.5284 | -42.6942 | -54.6887 | -60.1611 | -65.7835 | 58.3343 | 57.9977 | -36.8467 | -46.7639 | -47.4335 | -48.5666 | -49.7505 | -51.1073 | -52.5283 | -54.0126 | -56.4965 | -70.4089 | -76.4367 | -82.6033 | 60.9969 | 60.6544 | -34.1938 | -43.8568 | -44.5007 | -45.5903 | -46.7289 | -48.0336 | -49.4082 | -50.8436 | -53.2484 | -66.6838 | -72.5734 | -78.6047
|  |  | FS |  |  | 69.4762 | 69.2325 | 27.0571 | 26.9258 | -25.7639 | -26.0366 | -26.317 | -26.6716 | -27.0656 | -27.4939 | -28.4148 | -30.0364 | -31.4142 | -32.6087 | 58.4046 | 58.1448 | 15.9649 | 15.8249 | -36.8754 | -37.1661 | -37.4649 | -37.8427 | -38.2627 | -38.7191 | -39.767 | -41.6843 | -43.3134 | -44.7257 | 61.0684 | 60.8041 | 18.6228 | 18.4805 | -34.223 | -34.5188 | -34.8228 | -35.2073 | -35.6346 | -36.0991 | -37.1283 | -38.9721 | -40.5387 | -41.8968
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | FAREHAM T1B T2B (1X90, 1X60MVA) | MINIMUM HEADROOM | SU 56534 04031 | YES | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 69.4401 | 69.3944 | 69.2869 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946
|  |  | CT |  |  | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 69.4401 | 69.3944 | 69.2869 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946
|  |  | LW |  |  | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 69.4513 | 69.4215 | 69.3534 | 69.2246 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946
|  |  | ST |  |  | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 69.4622 | 69.4479 | 69.4177 | 69.3262 | 69.2427 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946
|  |  | FS |  |  | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 75.2015 | 69.4693 | 69.4651 | 69.4586 | 69.4206 | 69.3838 | 69.3131 | 69.251 | 69.2067 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 69.1915 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946 | 71.6946
BRAMLEY (FLEE) | FERNHURST | FERNHURST | MINIMUM HEADROOM | SU 72730 39772 | YES | 104.4541 | 104.4532 | 9.4818 | 7.4145 | 5.3212 | 2.8684 | 0.47211 | -1.8329 | -4.8678 | -7.8923 | -14.055 | -24.855 | -36.7471 | -43.7855 | 99.6668 | 82.3556 | -9.7622 | -12.2004 | -14.6691 | -17.4247 | -20.1442 | -22.8107 | -26.2749 | -29.7402 | -36.659 | -48.8322 | -62.0902 | -70.0107 | 100.9273 | 83.1999 | -8.9756 | -11.415 | -13.885 | -16.7251 | -19.5105 | -22.2099 | -25.7455 | -29.2741 | -36.408 | -48.9162 | -62.5877 | -70.71
|  |  | CT |  |  | 104.4541 | 104.4532 | 9.4818 | 7.4145 | 5.3212 | 2.8684 | 0.47211 | -1.8329 | -4.8678 | -7.8923 | -14.055 | -24.855 | -36.7471 | -43.7855 | 99.6668 | 99.4539 | 98.9795 | 0.85966 | -2.0926 | -5.4249 | -9.5717 | -14.5146 | -18.732 | -22.9067 | -28.1672 | -38.6755 | -50.6078 | -59.6765 | 100.9273 | 100.8365 | 100.6907 | 1.6464 | -1.3083 | -4.6432 | -8.9059 | -13.9492 | -18.2513 | -22.5063 | -27.9161 | -38.9163 | -51.3909 | -60.6528
|  |  | LW |  |  | 104.4541 | 104.4532 | 9.4818 | 7.4145 | 5.3212 | 2.8684 | 0.47211 | -1.8329 | -4.8678 | -7.8923 | -14.055 | -24.855 | -36.7471 | -43.7855 | 99.6679 | 82.3556 | -9.7622 | -12.2004 | -14.6691 | -17.4247 | -20.1442 | -22.8107 | -26.2749 | -29.7402 | -36.659 | -48.8322 | -62.0902 | -70.0107 | 100.9296 | 83.1999 | -8.9756 | -11.415 | -13.885 | -16.7251 | -19.5105 | -22.2099 | -25.7455 | -29.2741 | -36.408 | -48.9162 | -62.5877 | -70.71
|  |  | ST |  |  | 104.455 | 104.4547 | 104.4542 | 20.1408 | 17.8895 | 15.412 | 12.5803 | 9.0589 | 6.1641 | 3.2182 | -0.017516 | -5.7517 | -12.3219 | -17.5254 | 99.8485 | 99.6495 | 99.4485 | 2.8119 | 0.15624 | -2.711 | -6 | -10.1084 | -13.4568 | -16.9022 | -20.6362 | -27.2324 | -34.8079 | -40.7338 | 101.0055 | 100.9224 | 100.8383 | 3.603 | 0.94637 | -1.9554 | -5.2768 | -9.4144 | -12.8042 | -16.2689 | -20.0545 | -26.7549 | -34.4392 | -40.4958
|  |  | FS |  |  | 104.4551 | 104.4549 | 104.4547 | 104.4543 | 21.9695 | 21.435 | 20.7282 | 19.7953 | 18.6897 | 17.4591 | 14.7899 | 10.7608 | 7.3972 | 4.7863 | 99.9001 | 99.8132 | 99.7881 | 99.6145 | 4.9692 | 4.3388 | 3.5289 | 2.4538 | 1.1817 | -0.2387 | -3.3566 | -8.0588 | -11.9956 | -15.0411 | 101.0271 | 100.9907 | 100.9801 | 100.9075 | 5.7611 | 5.1304 | 4.3058 | 3.2149 | 1.9228 | 0.483 | -2.6548 | -7.3893 | -11.3465 | -14.4139
LOVEDEAN GSP | FORT WIDLEY | FORT WIDLEY | MINIMUM HEADROOM | SU 64948 05441 | YES | 68.9034 | 68.9027 | 68.9018 | 68.9006 | 68.8991 | 68.6501 | 68.4562 | 68.3608 | 67.7359 | 67.1348 | 65.6717 | 51.4056 | 29.0356 | 24.5712 | 67.8576 | 67.8103 | 67.8083 | 67.806 | 67.8034 | 67.663 | 67.5482 | 67.4247 | 66.9515 | 56.2875 | 54.0396 | 48.2283 | 22.9982 | 18.2612 | 69.19 | 69.1877 | 69.1843 | 69.1803 | 69.1759 | 68.9341 | 68.7366 | 68.5241 | 68.0106 | 55.7607 | 53.4251 | 47.398 | 22.0377 | 17.1489
|  |  | CT |  |  | 68.9034 | 68.9027 | 68.9018 | 68.9006 | 68.8991 | 68.6501 | 68.4562 | 68.3608 | 67.7359 | 67.1348 | 65.6717 | 51.4056 | 29.0356 | 24.5712 | 67.8602 | 67.8103 | 67.8083 | 67.806 | 67.8034 | 67.8007 | 67.5988 | 67.4247 | 67.1226 | 56.2875 | 54.0396 | 49.0874 | 34.4028 | 30.1792 | 69.19 | 69.1877 | 69.1843 | 69.1803 | 69.1759 | 69.1711 | 68.8238 | 68.5241 | 68.117 | 55.7607 | 53.4251 | 48.1502 | 33.2487 | 28.8902
|  |  | LW |  |  | 68.9034 | 68.9027 | 68.9018 | 68.9006 | 68.8991 | 68.6501 | 68.4562 | 68.3608 | 67.7359 | 67.1348 | 65.6717 | 51.4056 | 29.0356 | 24.5712 | 67.8576 | 67.8125 | 67.8119 | 67.8112 | 67.8103 | 67.663 | 67.5482 | 67.4917 | 66.9515 | 66.4253 | 54.323 | 48.2283 | 22.9982 | 18.2612 | 69.1922 | 69.1915 | 69.1905 | 69.1893 | 69.1877 | 68.9341 | 68.7366 | 68.6394 | 68.0106 | 67.406 | 53.6912 | 47.398 | 22.0377 | 17.1489
|  |  | ST |  |  | 68.9041 | 68.9038 | 68.9035 | 68.9031 | 68.9027 | 68.8025 | 68.7091 | 68.6264 | 68.4258 | 68.2914 | 67.9805 | 56.4845 | 45.1028 | 41.8428 | 67.9153 | 67.8473 | 67.8129 | 67.8127 | 67.8124 | 67.7531 | 67.6979 | 67.6489 | 67.4973 | 67.385 | 56.0394 | 53.0186 | 40.0865 | 36.6207 | 69.1929 | 69.1926 | 69.1923 | 69.1919 | 69.1914 | 69.0894 | 68.9942 | 68.91 | 68.7071 | 68.5717 | 55.6582 | 52.5929 | 39.754 | 36.2236
|  |  | FS |  |  | 68.9042 | 68.904 | 68.9038 | 68.9036 | 68.9033 | 68.903 | 68.8598 | 68.8137 | 68.7557 | 68.6991 | 68.6431 | 68.5509 | 68.4947 | 68.4328 | 67.9347 | 67.9229 | 67.9076 | 67.8321 | 67.8128 | 67.8126 | 67.7871 | 67.7598 | 67.7255 | 67.6919 | 67.6588 | 67.6042 | 67.5709 | 67.5343 | 69.1929 | 69.1928 | 69.1926 | 69.1923 | 69.1921 | 69.1917 | 69.1478 | 69.1008 | 69.0417 | 68.984 | 68.9269 | 68.8331 | 68.7758 | 68.7127
MELKSHAM GSP | FROME BSP | FROME BSP | MINIMUM HEADROOM | ST 78803 48019 | YES | 65.902 | 57.6642 | 56.9831 | 51.0501 | 5.864 | -5.3056 | -15.8444 | -29.7741 | -37.1316 | -45.1973 | -52.5367 | -65.0284 | -83.7953 | -91.716 | 61.7632 | 52.0233 | 51.2183 | 42.2205 | -2.5056 | -15.2869 | -27.7447 | -44.1681 | -52.7886 | -62.2434 | -70.8082 | -85.052 | -106.7375 | -115.6269 | 60.7165 | 50.9949 | 50.1913 | 41.2089 | -3.5004 | -16.2621 | -28.6964 | -45.0888 | -53.6935 | -63.1309 | -71.6805 | -86.027 | -107.6779 | -116.5585
|  |  | CT |  |  | 65.902 | 57.6642 | 56.9831 | 51.6544 | 46.2658 | 40.7376 | 35.3233 | 29.9009 | 22.6226 | 14.8638 | -0.14245 | -29.204 | -65.986 | -76.3645 | 73.2659 | 61.2429 | 60.5625 | 42.2205 | 33.5774 | 22.9664 | 10.3516 | -6.2358 | -15.768 | -25.6008 | -35.4708 | -53.5991 | -78.0111 | -88.9555 | 72.2103 | 60.1965 | 59.5168 | 41.2089 | 32.5815 | 21.9897 | 9.3981 | -7.1589 | -16.6756 | -26.4924 | -36.3495 | -54.7121 | -79.101 | -90.051
|  |  | LW |  |  | 65.902 | 57.6642 | 56.9831 | 51.6544 | 46.2658 | 40.7376 | 35.3233 | 29.9009 | 22.6226 | 14.8638 | -0.14245 | -29.204 | -65.986 | -76.3645 | 61.7632 | 52.0233 | 51.2183 | 44.9228 | 38.5568 | 32.0259 | 25.6298 | 19.225 | 10.9428 | 2.0924 | -14.947 | -47.2992 | -89.2046 | -100.4354 | 60.7165 | 50.9949 | 50.1913 | 43.9075 | 37.5533 | 31.0344 | 24.6501 | 18.2569 | 9.9864 | 1.1488 | -15.8667 | -48.4298 | -90.2805 | -101.515
|  |  | ST |  |  | 76.1889 | 66.3168 | 65.9243 | 51.0501 | 5.864 | -5.3056 | -15.8444 | -29.7741 | -37.1316 | -45.1973 | -52.5367 | -65.0284 | -83.7953 | -91.716 | 73.8132 | 62.1566 | 61.6925 | 44.1085 | -2.5056 | -15.2869 | -27.7447 | -44.1681 | -52.7886 | -62.2434 | -70.8082 | -85.052 | -106.7375 | -115.6269 | 72.7604 | 61.1102 | 60.647 | 43.0962 | -3.5004 | -16.2621 | -28.6964 | -45.0888 | -53.6935 | -63.1309 | -71.6805 | -86.027 | -107.6779 | -116.5585
|  |  | FS |  |  | 79.1395 | 75.8218 | 75.7534 | 74.4256 | 18.1401 | 13.8682 | 11.3279 | 7.8785 | 3.5345 | -1.702 | -13.9372 | -29.5536 | -41.5094 | -49.1415 | 77.2805 | 73.3818 | 73.3016 | 71.7421 | 12.0052 | 7.3774 | 4.3747 | 0.29684 | -4.8387 | -11.0298 | -25.4958 | -43.9143 | -57.9802 | -66.9583 | 76.2426 | 72.3272 | 72.2466 | 70.6804 | 10.983 | 6.3595 | 3.3625 | -0.70772 | -5.8336 | -12.013 | -26.4517 | -44.8359 | -58.8758 | -67.8377
MINETY GSP | GALILEO | GALILEO | MINIMUM HEADROOM | SU 10596 83733 | YES | 42.3671 | 42.3501 | 42.3102 | 42.267 | 42.2241 | 42.1814 | 42.139 | 42.0969 | 42.0517 | 42.0069 | 41.9164 | 41.4663 | 40.9924 | 40.5206 | 43.5718 | 43.5521 | 43.5389 | 43.5282 | 43.5176 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 39.9147 | 39.4056
|  |  | CT |  |  | 42.3671 | 42.3501 | 42.3102 | 42.267 | 42.2241 | 42.1814 | 42.139 | 42.0969 | 42.0517 | 42.0069 | 41.9164 | 41.4663 | 40.9924 | 40.5206 | 43.5735 | 43.5564 | 43.541 | 43.5318 | 43.5226 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 39.6283
|  |  | LW |  |  | 42.3671 | 42.3501 | 42.3102 | 42.267 | 42.2241 | 42.1814 | 42.139 | 42.0969 | 42.0517 | 42.0069 | 41.9164 | 41.4663 | 40.9924 | 40.5206 | 43.5718 | 43.5521 | 43.5389 | 43.5282 | 43.5176 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 39.9147 | 39.4056
|  |  | ST |  |  | 42.3764 | 42.3731 | 42.3662 | 42.356 | 42.3438 | 42.2983 | 42.2533 | 42.2089 | 42.1611 | 42.114 | 42.0223 | 41.7463 | 41.4534 | 41.1627 | 43.5825 | 43.5787 | 43.5708 | 43.559 | 43.5471 | 43.5359 | 43.5249 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.5165 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442
|  |  | FS |  |  | 49.087 | 42.3756 | 42.3737 | 42.3635 | 42.3514 | 42.3366 | 42.3219 | 42.3031 | 42.2846 | 42.2664 | 42.2311 | 42.1304 | 42.0197 | 41.9063 | 43.7608 | 43.5816 | 43.5794 | 43.5676 | 43.5537 | 43.5454 | 43.5418 | 43.5371 | 43.5326 | 43.5281 | 43.5194 | 43.5165 | 43.5165 | 43.5165 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442 | 43.7442
WILLESDEN GSP | GREENFORD | GREENFORD | MINIMUM HEADROOM | TQ 14695 83785 | NO | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 66.1432 | 65.7749 | 65.6817 | 65.5778 | 65.4644 | 65.3389 | 65.1748 | 65.0426 | 65.0075 | 64.9767 | 64.9178 | 64.9034 | 64.9034 | 64.9034 | 67.0935 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645
|  |  | CT |  |  | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 66.1468 | 65.7852 | 65.7002 | 65.6075 | 65.5045 | 65.3864 | 65.2371 | 65.0729 | 65.027 | 64.9938 | 64.9304 | 64.9034 | 64.9034 | 64.9034 | 67.097 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645
|  |  | LW |  |  | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 66.1432 | 65.7749 | 65.6817 | 65.5778 | 65.4644 | 65.3389 | 65.1748 | 65.0426 | 65.0075 | 64.9767 | 64.9178 | 64.9034 | 64.9034 | 64.9034 | 67.0935 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645
|  |  | ST |  |  | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 66.2703 | 66.1177 | 66.0379 | 65.9795 | 65.9103 | 65.7655 | 65.601 | 65.4277 | 65.2678 | 65.1129 | 64.9934 | 64.9034 | 64.9034 | 64.9034 | 67.2185 | 67.0684 | 66.9899 | 66.8957 | 66.7836 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645
|  |  | FS |  |  | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 70.0003 | 66.299 | 66.1734 | 66.1374 | 66.0932 | 66.0455 | 65.989 | 65.9297 | 65.8609 | 65.8013 | 65.7447 | 65.6329 | 65.3882 | 65.1702 | 65.0317 | 67.2467 | 67.1231 | 67.0878 | 67.0443 | 66.9974 | 66.9113 | 66.8152 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645 | 66.7645
LOVEDEAN GSP | HAVANT | HAVANT | MINIMUM HEADROOM | SU 70625 05720 | YES | 102.4685 | 102.4676 | 102.4664 | 102.4649 | 102.463 | 84.5554 | 83.5675 | 103.5493 | 103.3969 | 85.4443 | 83.5233 | 103.4537 | 78.9262 | 72.1581 | 97.7418 | 83.7523 | 83.1207 | 82.2746 | 81.3591 | 80.2185 | 79.0893 | 81.2063 | 79.8547 | 78.4881 | 76.0255 | 66.3817 | 57.3667 | 49.4856 | 85.4964 | 85.4939 | 85.4901 | 85.4856 | 84.7115 | 83.5109 | 82.3412 | 84.3281 | 82.9224 | 81.5068 | 78.95 | 69.0335 | 59.6763 | 51.7963
|  |  | CT |  |  | 102.4685 | 102.4676 | 102.4664 | 102.4649 | 102.463 | 84.5554 | 83.5675 | 119.5077 | 119.2429 | 119.0084 | 118.2065 | 116.9588 | 78.9262 | 72.1581 | 97.7432 | 97.6267 | 97.4811 | 97.4032 | 84.8241 | 83.9294 | 82.5972 | 81.2063 | 79.8547 | 78.4881 | 76.0255 | 66.3817 | 57.3667 | 49.4856 | 85.4964 | 85.4939 | 85.4901 | 85.4856 | 85.4807 | 85.4755 | 85.0878 | 84.3281 | 82.9224 | 81.5068 | 78.95 | 69.0335 | 59.6763 | 51.7963
|  |  | LW |  |  | 102.4685 | 102.4676 | 102.4664 | 102.4649 | 102.463 | 84.5554 | 83.5675 | 119.5077 | 119.2429 | 119.0084 | 118.2065 | 116.9588 | 78.9262 | 72.1581 | 97.7418 | 83.7523 | 83.1207 | 82.2746 | 81.3591 | 80.2185 | 79.0893 | 114.17 | 114.0168 | 113.8811 | 113.4171 | 79.5826 | 70.4899 | 62.2295 | 85.4988 | 85.498 | 85.4969 | 85.4956 | 84.7115 | 83.5109 | 82.3412 | 116.6298 | 116.3581 | 116.1173 | 115.2944 | 82.5231 | 73.2287 | 64.9694
|  |  | ST |  |  | 102.4693 | 102.469 | 102.4686 | 102.4681 | 102.4676 | 102.3407 | 102.2224 | 103.5493 | 103.3969 | 85.4443 | 83.5233 | 120.4796 | 120.0791 | 119.5943 | 97.9833 | 97.7148 | 97.6078 | 97.4845 | 97.4251 | 84.7368 | 83.5449 | 83.7083 | 82.3849 | 81.0951 | 78.7377 | 115.3356 | 84.8063 | 79.5478 | 85.4995 | 85.4993 | 85.4989 | 85.4985 | 85.498 | 85.3841 | 85.2781 | 100.6803 | 100.5239 | 84.3306 | 81.9803 | 117.5896 | 117.1785 | 82.8683
|  |  | FS |  |  | 102.4694 | 102.4692 | 102.469 | 102.4687 | 102.4683 | 102.468 | 102.4133 | 103.7865 | 103.713 | 103.6413 | 103.5704 | 103.4537 | 103.3821 | 84.0324 | 98.0069 | 97.9038 | 97.8736 | 97.8057 | 97.7244 | 97.6026 | 97.4677 | 98.8244 | 98.7388 | 98.6526 | 98.523 | 83.4208 | 81.3372 | 79.2979 | 85.4996 | 85.4994 | 85.4993 | 85.499 | 85.4986 | 85.4983 | 85.4493 | 100.9238 | 100.8484 | 100.7748 | 100.7019 | 100.5822 | 84.5817 | 82.5729
NORTH HYDE GSP | HAYES | HAYES | MINIMUM HEADROOM | TQ 09519 79541 | NO | 78.3167 | 78.2858 | 78.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 70.438 | 70.427 | 70.4034 | 70.3968 | 70.3882 | 70.3789 | 70.3689 | 70.3585 | 70.3474 | 70.336 | 70.3134 | 70.2467 | 70.1807 | 70.1141 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182
|  |  | CT |  |  | 78.3167 | 78.2858 | 78.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 70.4382 | 70.4287 | 70.4074 | 70.4015 | 70.3937 | 70.385 | 70.3741 | 70.3619 | 70.3511 | 70.3402 | 70.3193 | 70.2593 | 70.1998 | 70.1399 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182
|  |  | LW |  |  | 78.3167 | 78.2858 | 78.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 70.438 | 70.427 | 70.4034 | 70.3968 | 70.3882 | 70.3789 | 70.3689 | 70.3585 | 70.3474 | 70.336 | 70.3134 | 70.2467 | 70.1807 | 70.1141 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182
|  |  | ST |  |  | 78.379 | 78.3072 | 78.2705 | 116.2609 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 70.5801 | 70.4346 | 70.4216 | 70.4182 | 70.4129 | 70.4046 | 70.395 | 70.3845 | 70.3747 | 70.3647 | 70.3454 | 70.2977 | 70.2526 | 70.2081 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182
|  |  | FS |  |  | 78.3854 | 78.3213 | 78.3031 | 116.2995 | 116.2941 | 116.286 | 116.2777 | 116.2686 | 116.2592 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 116.2542 | 70.6252 | 70.4396 | 70.4332 | 70.4319 | 70.43 | 70.4271 | 70.4242 | 70.4209 | 70.4176 | 70.4142 | 70.4072 | 70.3908 | 70.3745 | 70.3576 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182 | 72.8182
COWLEY GSP | HEADINGTON BSP | HEADINGTON BSP | MINIMUM HEADROOM | SP 54454 08145 | YES | 36.9546 | 36.5882 | -39.8571 | -42.7089 | -45.834 | -49.9613 | -54.7563 | -60.9397 | -64.6064 | -68.3443 | -71.8873 | -85.0172 | -96.1983 | -100.5814 | 28.6154 | 28.1847 | -61.8679 | -65.2257 | -70.6069 | -75.5803 | -82.1537 | -90.3124 | -95.4124 | -100.5559 | -106.0893 | -117.8627 | -128.1284 | -133.6411 | 26.1543 | 25.7244 | -64.0548 | -67.4033 | -72.7787 | -77.7408 | -84.5694 | -92.9406 | -98.2233 | -103.5387 | -109.4067 | -122.3058 | -133.8142 | -139.7593
|  |  | CT |  |  | 36.9546 | 36.5882 | -39.8571 | -42.7089 | -45.5571 | -49.1259 | -52.4413 | -55.4666 | -59.0238 | -62.6701 | -70.1645 | -85.0172 | -96.1983 | -100.5814 | 74.3057 | 28.2187 | 27.3013 | 22.7538 | -70.6069 | -75.5803 | -82.1537 | -90.3124 | -95.4124 | -100.5559 | -106.0893 | -117.8627 | -128.1284 | -133.6411 | 71.7038 | 25.7553 | 24.8379 | 20.3011 | -72.7787 | -77.7408 | -84.5694 | -92.9406 | -98.2233 | -103.5387 | -109.4067 | -122.3058 | -133.8142 | -139.7593
|  |  | LW |  |  | 36.9546 | 36.5882 | -39.8571 | -42.7089 | -45.5571 | -49.1259 | -52.4413 | -55.4666 | -59.0238 | -62.6701 | -70.1645 | -85.0172 | -96.1983 | -100.5814 | 28.6154 | 28.1847 | -61.8679 | -65.2257 | -68.5789 | -72.4484 | -76.0935 | -79.529 | -83.441 | -87.4897 | -95.4752 | -111.6598 | -123.2205 | -127.6 | 26.1543 | 25.7244 | -64.0548 | -67.4033 | -70.7475 | -74.8062 | -78.5967 | -82.0988 | -86.1662 | -90.3506 | -98.8182 | -115.7415 | -128.2345 | -133.0714
|  |  | ST |  |  | 76.1133 | 36.9192 | 36.5656 | 33.3256 | -45.834 | -49.9613 | -54.7563 | -60.9397 | -64.6064 | -68.3443 | -71.8873 | -78.941 | -84.4056 | -88.1 | 74.913 | 28.5732 | 28.1571 | 24.3409 | -68.9099 | -73.6374 | -79.1605 | -86.3334 | -90.4913 | -94.8221 | -98.7941 | -106.6976 | -112.7139 | -116.5589 | 72.3115 | 26.1126 | 25.6975 | 21.8926 | -71.0746 | -75.8686 | -81.4502 | -88.668 | -92.9104 | -97.2715 | -101.3525 | -109.4758 | -115.7266 | -119.8645
|  |  | FS |  |  | 97.2896 | 97.2891 | 37.0128 | 36.3276 | 35.3764 | -41.1372 | -42.4029 | -44.075 | -46.1587 | -48.5996 | -53.9573 | -60.8826 | -66.1083 | -69.5421 | 99.1285 | 98.3842 | 28.6834 | 27.8766 | 26.7565 | -63.3775 | -64.8105 | -66.7182 | -69.0949 | -71.8943 | -78.1304 | -86.1647 | -92.2452 | -96.2071 | 95.5023 | 95.425 | 26.2225 | 25.4179 | 24.3009 | -65.5588 | -67.0223 | -68.9614 | -71.3777 | -74.2143 | -80.4766 | -88.5608 | -94.6681 | -98.6679
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU 84773 92191 | YES | 98.1667 | 57.9732 | 57.2274 | 56.0482 | 54.8769 | 53.7013 | 52.5438 | 51.3906 | 48.9959 | 46.5484 | 41.7459 | 31.9375 | 13.9141 | 5.6715 | 96.9466 | 50.6354 | 49.7556 | 48.3667 | 46.9873 | 45.6029 | 44.2398 | 42.8822 | 40.233 | 37.5213 | 32.2066 | 21.4434 | 1.025 | -8.0777 | 98.4342 | 52.365 | 51.4849 | 50.0956 | 48.7157 | 47.3308 | 45.9673 | 44.6093 | 41.9595 | 39.2472 | 33.9314 | 23.1662 | 2.7425 | -6.3621
|  |  | CT |  |  | 98.1667 | 57.9732 | 57.2274 | 56.0482 | 54.8769 | 53.7013 | 52.5438 | 51.3906 | 48.9959 | 46.5484 | 41.7459 | 31.9375 | 13.9141 | 5.6715 | 96.9466 | 77.8922 | 76.904 | 75.1544 | 73.4593 | 71.6077 | 69.6012 | 67.3029 | 64.8421 | 62.3647 | 58.6298 | 50.7184 | 37.5546 | 29.3561 | 98.4342 | 79.6307 | 78.6422 | 76.892 | 75.1964 | 73.3442 | 71.3371 | 69.0379 | 66.5765 | 64.0983 | 60.3625 | 52.4491 | 39.2817 | 31.0811
|  |  | LW |  |  | 98.1667 | 57.9732 | 57.2274 | 56.0482 | 54.8769 | 53.7013 | 52.5438 | 51.3906 | 48.9959 | 46.5484 | 41.7459 | 31.9375 | 13.9141 | 5.6715 | 96.9744 | 50.6354 | 49.7556 | 48.3667 | 46.9873 | 45.6029 | 44.2398 | 42.8822 | 40.233 | 37.5213 | 32.2066 | 21.4434 | 1.025 | -8.0777 | 98.4554 | 52.365 | 51.4849 | 50.0956 | 48.7157 | 47.3308 | 45.9673 | 44.6093 | 41.9595 | 39.2472 | 33.9314 | 23.1662 | 2.7425 | -6.3621
|  |  | ST |  |  | 98.1979 | 81.481 | 81.1849 | 80.2097 | 79.0957 | 77.8437 | 76.4625 | 74.8285 | 73.2308 | 71.5636 | 69.3306 | 64.7696 | 55.0548 | 49.3261 | 97.1937 | 78.3683 | 78.0191 | 76.8699 | 75.557 | 74.0813 | 72.4531 | 70.5269 | 68.6767 | 66.744 | 64.1778 | 59.0354 | 47.9601 | 41.6193 | 98.6225 | 80.107 | 79.7576 | 78.6081 | 77.2947 | 75.8186 | 74.1899 | 72.263 | 70.4123 | 68.479 | 65.9121 | 60.7684 | 49.6902 | 43.3481
|  |  | FS |  |  | 98.2131 | 98.2056 | 98.2016 | 98.1654 | 81.2426 | 80.922 | 80.5641 | 80.0913 | 79.5614 | 78.9767 | 77.7004 | 75.5557 | 73.6901 | 72.1616 | 97.3003 | 97.2479 | 97.2197 | 96.9773 | 78.0879 | 77.71 | 77.2882 | 76.7306 | 76.1057 | 75.4161 | 73.9106 | 71.3818 | 69.1813 | 67.3787 | 98.7036 | 98.6638 | 98.6423 | 98.4571 | 79.8264 | 79.4484 | 79.0265 | 78.4687 | 77.8437 | 77.1538 | 75.6478 | 73.1181 | 70.917 | 69.1138
IVER 66KV | HILLINGDON | HILLINGDON | MINIMUM HEADROOM | TQ 07470 82827 | NO | 61.5739 | 61.5637 | 61.536 | 61.5251 | 61.5094 | 61.4916 | 61.4724 | 61.4719 | 61.4444 | 61.4162 | 61.3597 | 61.4511 | 61.4023 | 61.3532 | 54.7612 | 54.6605 | 54.3869 | 54.2795 | 54.124 | 54.0754 | 54.0374 | 54.0106 | 53.9714 | 53.9267 | 53.8154 | 53.5099 | 53.4888 | 53.4888 | 55.1988 | 55.1436 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379
|  |  | CT |  |  | 61.5739 | 61.5637 | 61.536 | 61.5251 | 61.5094 | 61.4916 | 61.4724 | 65.6627 | 65.641 | 65.6191 | 65.5741 | 65.3863 | 65.3863 | 65.3863 | 54.763 | 54.6699 | 54.4126 | 54.3004 | 54.1491 | 54.0832 | 54.0495 | 54.0106 | 53.9714 | 53.9299 | 53.846 | 53.5099 | 53.4888 | 53.4888 | 55.1998 | 55.1487 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379
|  |  | LW |  |  | 61.5739 | 61.5637 | 61.536 | 61.5251 | 61.5094 | 61.4916 | 61.4724 | 65.6627 | 65.641 | 65.6191 | 65.5741 | 65.3863 | 65.3863 | 65.3863 | 54.7612 | 54.6605 | 54.3869 | 54.2795 | 54.124 | 54.0754 | 54.0374 | 58.2081 | 58.1654 | 58.1222 | 58.0337 | 57.6994 | 57.6994 | 57.6994 | 55.1988 | 55.1436 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 59.2484 | 59.2484 | 59.2484 | 59.2484 | 59.2484 | 59.2484 | 59.2484
|  |  | ST |  |  | 61.5858 | 61.5729 | 61.5592 | 61.5549 | 61.5472 | 61.5228 | 61.4981 | 61.4719 | 61.4444 | 61.4162 | 61.3597 | 65.4311 | 65.3863 | 65.3863 | 54.8779 | 54.7514 | 54.6161 | 54.5729 | 54.4974 | 54.2567 | 54.0881 | 54.0366 | 53.9823 | 53.9267 | 53.8154 | 57.7519 | 57.6994 | 57.6994 | 55.2629 | 55.1934 | 55.1192 | 55.0955 | 55.0541 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 59.2484 | 59.2484 | 59.2484
|  |  | FS |  |  | 61.5883 | 61.5776 | 61.5708 | 61.5691 | 61.5662 | 61.5584 | 61.5503 | 61.5406 | 61.5308 | 61.5209 | 61.5009 | 61.4511 | 61.4023 | 61.3532 | 54.9026 | 54.7979 | 54.7299 | 54.7132 | 54.6847 | 54.6074 | 54.5278 | 54.4321 | 54.3351 | 54.2379 | 54.0937 | 53.9955 | 53.8993 | 53.8026 | 55.2764 | 55.2189 | 55.1817 | 55.1725 | 55.1568 | 55.1145 | 55.0708 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379 | 55.0379
EALING GSP | IRONBRIDGE | IRONBRIDGE | MINIMUM HEADROOM | TQ 14226 80171 | YES | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 49.82 | 49.7884 | 49.7221 | 49.6493 | 49.587 | 49.5253 | 49.4626 | 49.4209 | 49.352 | 49.2849 | 49.1599 | 49.0369 | 49.0369 | 49.0369 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011
|  |  | CT |  |  | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 61.3733 | 61.3733 | 61.3733 | 61.3733 | 61.3733 | 61.3733 | 61.3733 | 49.8212 | 49.792 | 49.7299 | 49.662 | 49.6032 | 49.544 | 49.4829 | 49.4209 | 49.352 | 49.2849 | 49.1599 | 49.0369 | 49.0369 | 49.0369 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011
|  |  | LW |  |  | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 61.3733 | 61.3733 | 61.3733 | 61.3733 | 61.3733 | 61.3733 | 61.3733 | 49.82 | 49.7884 | 49.7221 | 49.6493 | 49.587 | 49.5253 | 49.4626 | 52.9444 | 52.8726 | 52.8002 | 52.6885 | 52.5822 | 52.5822 | 52.5822 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 57.1464 | 57.1464 | 57.1464 | 57.1464 | 57.1464 | 57.1464 | 57.1464
|  |  | ST |  |  | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 61.3733 | 61.3733 | 61.3733 | 49.8337 | 49.8213 | 49.7989 | 49.7668 | 49.7352 | 49.6953 | 49.6543 | 49.6129 | 49.5667 | 49.5219 | 49.4327 | 52.7528 | 52.6455 | 52.5822 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 57.1464 | 57.1464 | 57.1464
|  |  | FS |  |  | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 57.828 | 49.8397 | 49.8355 | 49.8308 | 49.8181 | 49.8063 | 49.7921 | 49.778 | 49.7599 | 49.7415 | 49.723 | 49.6863 | 49.5965 | 49.5088 | 49.4235 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011 | 53.6011
FAWLEY GSP | LANGLEY BSP | LANGLEY BSP | MINIMUM HEADROOM | SU 45185 01376 | YES | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 54.8637 | 54.8495 | 54.8145 | 54.7441 | 54.6507 | 54.523 | 54.359 | 54.1611 | 53.9755 | 53.7728 | 53.4483 | 52.7413 | 41.1894 | 39.3521 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 41.2564 | 39.4728
|  |  | CT |  |  | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 54.8671 | 54.8575 | 54.8336 | 54.757 | 54.6635 | 54.5551 | 54.4339 | 54.2722 | 54.1232 | 53.9576 | 53.6958 | 52.7413 | 52.7413 | 41.8317 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 41.8799
|  |  | LW |  |  | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 54.8637 | 54.8495 | 54.8145 | 54.7441 | 54.6507 | 54.5519 | 54.4496 | 54.3271 | 54.1796 | 54.0173 | 53.6852 | 52.7413 | 41.1894 | 39.3521 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 41.2564 | 39.4728
|  |  | ST |  |  | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 54.8689 | 54.8612 | 54.844 | 54.7715 | 54.6757 | 54.523 | 54.359 | 54.1611 | 53.9755 | 53.7728 | 53.4483 | 52.7413 | 52.7413 | 42.0004 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 42.0437
|  |  | FS |  |  | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 56.3277 | 54.9038 | 54.8725 | 54.8715 | 54.8585 | 54.8344 | 54.796 | 54.7534 | 54.6951 | 54.6301 | 54.5571 | 54.3972 | 54.1206 | 53.8949 | 53.6927 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267 | 53.4267
IVER 132KV | LONGFORD | LONGFORD | MINIMUM HEADROOM | TQ 03910 76751 | YES | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 139.985 | 139.9595 | 139.934 | 139.883 | 139.7555 | 139.6279 | 139.5004 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1596 | 135.1439 | 135.1283 | 135.097 | 135.0188 | 134.9406 | 134.8624 | 135.6409 | 135.6058 | 135.5218 | 135.4295 | 135.3346 | 135.2388 | 135.1425 | 135.0234 | 134.8899 | 134.7457 | 134.3668 | 133.7648 | 133.4074 | 133.0505
|  |  | CT |  |  | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 139.985 | 139.9595 | 139.934 | 139.883 | 139.7555 | 139.6279 | 139.5004 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1596 | 135.1439 | 135.1283 | 135.097 | 135.0188 | 134.9406 | 134.8624 | 135.6419 | 135.6084 | 135.5281 | 135.4393 | 135.3488 | 135.2584 | 135.1691 | 135.0337 | 134.8899 | 134.7457 | 134.3668 | 133.7648 | 133.4074 | 133.0505
|  |  | LW |  |  | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 139.985 | 139.9595 | 139.934 | 139.883 | 139.7555 | 139.6279 | 139.5004 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1674 | 135.1596 | 135.1517 | 135.1361 | 135.097 | 135.0579 | 135.0188 | 135.6409 | 135.6058 | 135.5218 | 135.4295 | 135.3346 | 135.2388 | 135.1425 | 135.0234 | 134.8967 | 134.7686 | 134.4051 | 134.0364 | 133.8137 | 133.5914
|  |  | ST |  |  | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.9645 | 135.6432 | 135.6149 | 135.5713 | 135.5172 | 135.4136 | 135.3118 | 135.2108 | 135.1008 | 134.9917 | 134.7099 | 134.365 | 134.3102 | 134.2559
|  |  | FS |  |  | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 140.0105 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.1752 | 135.9709 | 135.8799 | 135.6579 | 135.6437 | 135.6262 | 135.5964 | 135.5666 | 135.5284 | 135.4905 | 135.453 | 135.355 | 135.1621 | 134.9704 | 134.786
AMERSHAM | LOUDWATER BSP | LOUDWATER BSP | MINIMUM HEADROOM | SU 90644 91247 | NO | 126.481 | -34.7831 | -36.5826 | -37.398 | -38.3116 | -39.201 | -40.0656 | -40.8964 | -41.7823 | -42.659 | -44.3857 | -48.2619 | -52.3212 | -56.3352 | 115.0517 | -53.9891 | -55.9908 | -56.0885 | -56.1851 | -56.2791 | -56.3705 | -56.4583 | -56.552 | -56.6447 | -56.8272 | -57.5628 | -62.3678 | -67.1193 | 114.7302 | -38.6429 | -44.3304 | -45.3923 | -46.4421 | -47.4642 | -48.4577 | -49.4124 | -50.4304 | -51.4378 | -53.4221 | -57.8764 | -62.541 | -67.1536
|  |  | CT |  |  | 126.481 | -34.7831 | -36.5826 | -37.398 | -38.3116 | -39.201 | -40.0656 | -40.8964 | -41.7823 | -42.659 | -44.3857 | -48.2619 | -52.3212 | -56.3352 | 115.0517 | -46.4092 | -3.1118 | -55.1114 | -55.2105 | -55.3089 | -55.407 | -55.5019 | -55.6016 | -55.6993 | -55.8896 | -56.3089 | -56.747 | -57.18 | 114.7302 | -31.0634 | 12.2683 | -39.6963 | -39.7605 | -39.8243 | -39.8878 | -39.9493 | -40.0995 | -41.1613 | -43.2299 | -47.7875 | -52.5502 | -57.2572
|  |  | LW |  |  | 126.481 | -34.7831 | -36.5826 | -37.398 | -38.3116 | -39.201 | -40.0656 | -40.8964 | -41.7823 | -42.659 | -44.3857 | -48.2619 | -52.3212 | -56.3352 | 115.0521 | -53.9891 | -55.9908 | -56.0885 | -56.1851 | -56.2791 | -56.3705 | -56.4583 | -56.552 | -56.6447 | -56.8272 | -57.5628 | -62.3678 | -67.1193 | 114.7302 | -38.6429 | -44.3304 | -45.3923 | -46.4421 | -47.4642 | -48.4577 | -49.4124 | -50.4304 | -51.4378 | -53.4221 | -57.8764 | -62.541 | -67.1536
|  |  | ST |  |  | 126.481 | 126.481 | 148.0766 | 8.5491 | 8.4849 | 8.4387 | 8.3929 | 8.3488 | 8.3026 | 8.2577 | 8.1714 | 7.9597 | 7.7459 | 5.454 | 115.2705 | 115.0301 | 128.8686 | -10.6713 | -10.7505 | -10.8073 | -10.8638 | -10.918 | -10.9749 | -11.0302 | -11.1366 | -11.3972 | -11.6606 | -11.9225 | 114.7302 | 114.7302 | 144.2186 | 4.702 | 4.6507 | 4.6139 | 4.5773 | 4.5421 | 4.5053 | 4.4695 | 4.4006 | 2.9503 | 0.087241 | -2.7593
|  |  | FS |  |  | 126.481 | 126.481 | 148.1575 | 148.1425 | 148.1253 | 140.5302 | 140.5145 | 140.4955 | 140.4771 | 140.4592 | 140.4245 | 140.3417 | 140.2612 | 140.1843 | 115.2957 | 115.2805 | 128.9683 | 128.9498 | 128.9287 | 121.3297 | 121.3105 | 121.2871 | 121.2644 | 121.2423 | 121.1996 | 121.0977 | 120.9985 | 120.9038 | 114.7302 | 114.7302 | 144.2831 | 144.2711 | 144.2575 | 136.6656 | 136.6531 | 136.6379 | 136.6232 | 136.6089 | 136.5813 | 136.5152 | 136.451 | 136.3896
MANNINGTON GSP | LYTCHETT | LYTCHETT | MINIMUM HEADROOM | SY 97796 94214 | YES | 600.0179 | 545.1688 | 545.1669 | 545.1644 | 545.1613 | 82.7539 | 78.473 | 75.0042 | 69.5193 | 63.6415 | 52.4739 | 32.1013 | 6.7654 | -0.70531 | 437.8311 | 141.4893 | 141.1521 | 133.6629 | 34.9478 | 29.8479 | 24.7824 | 20.524 | 14.2472 | 7.5057 | -5.2798 | -28.4089 | -57.4256 | -65.5 | 461.7701 | 121.6121 | 121.272 | 113.8037 | 15.3931 | 10.3076 | 5.2563 | 1.0119 | -5.2511 | -11.9776 | -24.7361 | -47.8282 | -76.7983 | -84.8913
|  |  | CT |  |  | 600.0179 | 545.1688 | 545.1669 | 545.1644 | 545.1613 | 82.7539 | 78.473 | 75.0042 | 69.5193 | 63.6415 | 52.4739 | 32.1013 | 6.7654 | -0.70531 | 440.0198 | 468.4491 | 141.1521 | 133.6629 | 126.6418 | 117.9589 | 107.5265 | 93.7364 | 86.0891 | 78.2023 | 70.8296 | 58.3629 | 41.2643 | 32.7986 | 461.7701 | 165.6489 | 121.272 | 113.8037 | 106.8017 | 98.143 | 87.7399 | 73.9891 | 66.3606 | 58.4928 | 51.1316 | 38.67 | 21.5816 | 13.0924
|  |  | LW |  |  | 600.0179 | 545.1688 | 545.1669 | 545.1644 | 545.1613 | 82.7539 | 78.473 | 75.0042 | 69.5193 | 63.6415 | 52.4739 | 32.1013 | 6.7654 | -0.70531 | 437.8311 | 141.4893 | 141.185 | 136.3045 | 34.9478 | 29.8479 | 24.7824 | 20.524 | 14.2472 | 7.5057 | -5.2798 | -28.4089 | -57.4256 | -65.5 | 461.7744 | 121.6121 | 121.3083 | 116.4419 | 15.3931 | 10.3076 | 5.2563 | 1.0119 | -5.2511 | -11.9776 | -24.7361 | -47.8282 | -76.7983 | -84.8913
|  |  | ST |  |  | 600.0193 | 600.0188 | 600.0181 | 545.1697 | 545.1688 | 545.1675 | 545.1661 | 545.1645 | 544.9396 | 544.7145 | 544.2642 | 543.5277 | 540.9367 | 538.116 | 440.2037 | 523.327 | 520.6469 | 134.7059 | 127.2823 | 118.5455 | 108.0883 | 94.2838 | 87.0407 | 79.1019 | 72.0684 | 61.9627 | 45.5023 | 37.486 | 461.7758 | 547.2753 | 547.2746 | 114.8496 | 107.4484 | 98.7378 | 88.3121 | 74.5492 | 67.3271 | 59.4113 | 52.3969 | 42.3155 | 25.8911 | 17.8828
|  |  | FS |  |  | 600.0195 | 600.0191 | 600.0188 | 600.0183 | 600.0177 | 545.1694 | 545.1688 | 545.1681 | 545.1673 | 545.1666 | 545.1649 | 545.1588 | 545.1502 | 545.1407 | 440.2375 | 525.5372 | 520.6473 | 520.647 | 520.6466 | 136.7973 | 134.3369 | 130.9847 | 126.7829 | 121.7137 | 109.8912 | 94.8676 | 83.4023 | 76.1687 | 461.7759 | 547.2756 | 547.2753 | 547.2747 | 547.2741 | 116.9346 | 114.4815 | 111.1393 | 106.9502 | 101.8961 | 90.1092 | 75.1296 | 63.6969 | 56.4827
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD BSP | MINIMUM HEADROOM | SU 86592 79883 | YES | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 83.7602 | 79.851 | 74.8568 | 69.8858 | 65.5477 | 98.0602 | 97.9617 | 97.7482 | 97.5394 | 97.5394 | 97.5394 | 84.9647 | 82.1087 | 79.3878 | 76.6119 | 72.6399 | 66.9903 | 61.1773 | 55.5181 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 83.7114 | 80.9583 | 78.1495 | 74.1304 | 68.4138 | 62.5319 | 56.8056
|  |  | CT |  |  | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 83.7602 | 79.851 | 74.8568 | 69.8858 | 65.5477 | 98.0622 | 97.969 | 97.7641 | 97.5394 | 97.5394 | 97.5394 | 84.9647 | 82.1087 | 79.3878 | 76.6119 | 72.6399 | 66.9903 | 61.1773 | 55.5181 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 83.7114 | 80.9583 | 78.1495 | 74.1304 | 68.4138 | 62.5319 | 56.8056
|  |  | LW |  |  | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 83.7602 | 79.851 | 74.8568 | 69.8858 | 65.5477 | 98.0602 | 97.9617 | 97.7482 | 97.5394 | 97.5394 | 97.5394 | 97.5394 | 83.8322 | 81.3571 | 78.8237 | 74.2644 | 68.4397 | 62.642 | 57.5825 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 85.4554 | 82.9509 | 80.3874 | 75.7741 | 69.8804 | 64.0139 | 58.8945
|  |  | ST |  |  | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 82.458 | 79.3558 | 76.3746 | 98.1289 | 98.0576 | 97.979 | 97.7641 | 97.5394 | 97.5394 | 97.5394 | 97.5394 | 85.1894 | 83.2407 | 80.8793 | 77.3049 | 73.6868 | 70.2098 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 84.8569 | 82.4675 | 78.8506 | 75.1897 | 71.6715
|  |  | FS |  |  | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 102.5859 | 98.1876 | 98.104 | 98.0898 | 98.0339 | 97.9612 | 97.8966 | 97.8211 | 97.7233 | 97.6112 | 97.5394 | 97.5394 | 97.5394 | 97.5394 | 84.18 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593 | 99.3593
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON BSP | MINIMUM HEADROOM | SU 07523 05221 | YES | 109.6597 | 54.5511 | 38.6115 | 36.0147 | 33.4078 | 30.6871 | 27.9815 | 25.2286 | 20.0901 | 14.6935 | 4.2191 | -17.432 | -56.5264 | -67.9097 | 103.7096 | 48.5523 | 29.6846 | 26.6112 | 23.5259 | 20.3061 | 17.1043 | 13.8468 | 8.1142 | 2.0764 | -9.6213 | -33.6681 | -78.4004 | -90.6763 | 104.2337 | 49.0772 | 30.2667 | 27.2023 | 24.1261 | 20.9156 | 17.723 | 14.4747 | 8.753 | 2.7268 | -8.949 | -32.9566 | -77.5897 | -89.8613
|  |  | CT |  |  | 109.6597 | 54.5511 | 38.6115 | 36.0147 | 33.4078 | 30.6871 | 27.9815 | 25.2286 | 20.0901 | 14.6935 | 4.2191 | -17.432 | -56.5264 | -67.9097 | 103.7189 | 103.4336 | 102.8827 | 43.6015 | 39.443 | 34.3134 | 28.2064 | 20.2247 | 14.3674 | 8.3594 | 1.7341 | -11.7068 | -37.002 | -48.2363 | 104.2425 | 103.9574 | 103.4073 | 44.1388 | 39.9919 | 34.8769 | 28.7874 | 20.8287 | 14.9856 | 8.9922 | 2.379 | -11.0434 | -36.2876 | -47.517
|  |  | LW |  |  | 109.6597 | 54.5511 | 38.6115 | 36.0147 | 33.4078 | 30.6871 | 27.9815 | 25.2286 | 20.0901 | 14.6935 | 4.2191 | -17.432 | -56.5264 | -67.9097 | 103.7096 | 48.5523 | 29.6846 | 26.6112 | 23.5259 | 20.3061 | 17.1043 | 13.8468 | 8.1142 | 2.0764 | -9.6213 | -33.6681 | -78.4004 | -90.6763 | 104.2337 | 49.0772 | 30.2667 | 27.2023 | 24.1261 | 20.9156 | 17.723 | 14.4747 | 8.753 | 2.7268 | -8.949 | -32.9566 | -77.5897 | -89.8613
|  |  | ST |  |  | 109.9866 | 109.5779 | 109.3073 | 51.1002 | 47.4174 | 42.9831 | 37.746 | 30.9446 | 26.2874 | 21.2509 | 15.9942 | 6.4565 | -14.6359 | -24.1956 | 104.0962 | 103.6126 | 103.2923 | 44.4672 | 40.1079 | 34.8593 | 28.6602 | 20.6095 | 15.1641 | 9.2698 | 3.1825 | -7.6342 | -31.8246 | -42.2953 | 104.6194 | 104.1371 | 103.8178 | 45.0046 | 40.6585 | 35.4257 | 29.2454 | 21.2189 | 15.7888 | 9.9112 | 3.8397 | -6.9537 | -31.0861 | -41.5424
|  |  | FS |  |  | 127.4213 | 127.4212 | 109.6711 | 109.1008 | 108.2768 | 52.5186 | 51.3623 | 49.8052 | 47.8866 | 45.6096 | 40.3517 | 33.2004 | 27.622 | 23.89 | 123.6078 | 123.4563 | 103.7229 | 103.0479 | 102.0726 | 46.1463 | 44.7777 | 42.9346 | 40.6636 | 37.9685 | 31.7448 | 23.2809 | 16.6793 | 12.2637 | 123.6766 | 123.6516 | 104.2471 | 103.5741 | 102.6017 | 46.6786 | 45.314 | 43.4765 | 41.2123 | 38.5253 | 32.3204 | 23.8815 | 17.2989 | 12.8955
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU 47559 12003 | NO | 160.0921 | 245.5915 | 245.5906 | 245.5896 | 245.5883 | 245.36 | 245.1823 | 245.0948 | 244.8972 | 244.7221 | 244.1234 | 243.192 | 163.0404 | 155.52 | 152.4662 | 235.2001 | 235.1365 | 235.0342 | 234.9331 | 234.6902 | 234.4791 | 234.3216 | 234.0727 | 233.8667 | 233.3535 | 232.2909 | 155.0289 | 145.8091 | 145.5675 | 231.0636 | 231.0605 | 231.0569 | 231.053 | 230.8293 | 230.6469 | 230.4484 | 230.2076 | 229.9796 | 229.5527 | 164.5842 | 139.6599 | 130.5167
|  |  | CT |  |  | 160.0921 | 245.5915 | 245.5906 | 245.5896 | 245.5883 | 245.36 | 245.1823 | 245.0948 | 244.8972 | 244.7221 | 244.1234 | 243.192 | 163.0404 | 155.52 | 159.2021 | 237.7303 | 237.544 | 235.3867 | 235.2671 | 235.1349 | 234.7955 | 234.4557 | 234.1602 | 233.8703 | 233.4705 | 232.2909 | 168.1972 | 160.3023 | 152.3025 | 231.0636 | 231.0605 | 231.0569 | 231.053 | 231.0488 | 230.7264 | 230.4484 | 230.2076 | 229.9796 | 229.5527 | 168.52 | 152.2533 | 144.408
|  |  | LW |  |  | 160.0921 | 245.5915 | 245.5906 | 245.5896 | 245.5883 | 245.36 | 245.1823 | 245.0948 | 244.8972 | 244.7221 | 244.1234 | 243.192 | 163.0404 | 155.52 | 152.4662 | 235.2001 | 235.1365 | 235.0342 | 234.9331 | 234.6902 | 234.4791 | 234.3216 | 234.0727 | 233.8667 | 233.3535 | 232.3343 | 155.0289 | 145.8091 | 145.5675 | 231.0669 | 231.066 | 231.0649 | 231.0636 | 230.8293 | 230.6469 | 230.5571 | 230.3543 | 230.1745 | 229.56 | 164.5842 | 139.6599 | 130.5167
|  |  | ST |  |  | 166.8295 | 252.3293 | 252.329 | 252.3287 | 252.3283 | 252.2364 | 252.1508 | 252.075 | 251.9642 | 251.9145 | 251.7763 | 251.4916 | 251.1924 | 250.824 | 159.3125 | 244.6878 | 244.6 | 242.2668 | 242.1607 | 241.9789 | 241.7885 | 241.5777 | 241.3696 | 241.1926 | 240.913 | 240.4308 | 239.5746 | 239.1961 | 152.305 | 237.8047 | 237.8044 | 237.8041 | 237.8037 | 237.7094 | 237.6216 | 237.5437 | 237.43 | 237.379 | 237.2372 | 236.945 | 167.6748 | 161.6787
|  |  | FS |  |  | 165.8191 | 251.3189 | 251.3188 | 251.3186 | 252.3288 | 252.3286 | 252.289 | 252.2467 | 252.1936 | 252.1416 | 252.0903 | 252.0059 | 251.953 | 251.8941 | 158.3295 | 243.741 | 243.7294 | 243.6727 | 244.6104 | 244.5224 | 244.3968 | 244.2361 | 244.0514 | 243.851 | 243.4568 | 242.7647 | 242.3497 | 242.1405 | 151.2945 | 236.7944 | 236.7942 | 236.794 | 237.8043 | 237.804 | 237.7634 | 237.72 | 237.6654 | 237.6121 | 237.5594 | 237.4728 | 237.4185 | 237.3581
MELKSHAM GSP | NORRINGTON | NORRINGTON | MINIMUM HEADROOM | ST 88273 64983 | YES | -89.5372 | -111.6744 | -300.3195 | -362.1469 | -367.8444 | -373.7156 | -379.5067 | -385.3367 | -392.7447 | -400.6827 | -416.0277 | -442.3165 | -518.8934 | -530.402 | -98.1052 | -125.8396 | -325.4019 | -398.2336 | -404.9431 | -411.8572 | -418.677 | -425.5423 | -434.0857 | -443.2537 | -460.9646 | -491.0989 | -580.509 | -593.4482 | -97.3782 | -124.9999 | -324.3422 | -396.9521 | -403.6412 | -410.5343 | -417.3333 | -424.1777 | -432.6983 | -441.8415 | -459.5048 | -489.5615 | -578.713 | -591.6234
|  |  | CT |  |  | -89.5372 | -111.6744 | -300.3195 | -362.1469 | -367.8444 | -373.7156 | -379.5067 | -385.3367 | -392.7447 | -400.6827 | -416.0277 | -442.3165 | -518.8934 | -530.402 | 13.4964 | -98.4945 | -263.2419 | -272.7416 | -327.3924 | -338.3525 | -351.342 | -368.3149 | -378.7023 | -389.4112 | -400.2182 | -418.1739 | -468.1738 | -482.3177 | 13.9278 | -97.7663 | -262.3998 | -271.8706 | -326.355 | -337.2817 | -350.2318 | -367.153 | -377.5099 | -388.1874 | -398.9639 | -416.8711 | -466.7246 | -480.8313
|  |  | LW |  |  | -89.5372 | -111.6744 | -300.3195 | -362.1469 | -367.8444 | -373.7156 | -379.5067 | -385.3367 | -392.7447 | -400.6827 | -416.0277 | -442.3165 | -518.8934 | -530.402 | -98.1052 | -125.8396 | -325.4019 | -398.2336 | -404.9431 | -411.8572 | -418.677 | -425.5423 | -434.0857 | -443.2537 | -460.9646 | -491.0989 | -580.509 | -593.4482 | -97.3782 | -124.9999 | -324.3422 | -396.9521 | -403.6412 | -410.5343 | -417.3333 | -424.1777 | -432.6983 | -441.8415 | -459.5048 | -489.5615 | -578.713 | -591.6234
|  |  | ST |  |  | 174.6464 | -89.657 | -226.2917 | -233.6237 | -263.8707 | -273.0418 | -283.9172 | -288.8574 | -297.1244 | -306.161 | -314.6919 | -327.6525 | -368.5295 | -379.1043 | 172.8056 | -98.2462 | -240.4843 | -249.1204 | -280.8057 | -291.6082 | -304.4184 | -311.8933 | -321.5959 | -332.2055 | -342.1842 | -357.2038 | -404.9554 | -416.9768 | 174.1911 | -97.5188 | -239.644 | -248.2538 | -279.9102 | -290.6797 | -303.451 | -310.8748 | -320.5484 | -331.1264 | -341.0759 | -356.054 | -403.6671 | -415.6593
|  |  | FS |  |  | 174.6464 | 174.6464 | 66.2512 | -6.894 | -8.8127 | -10.7604 | -66.451 | -69.8506 | -74.0922 | -79.1792 | -91.0382 | -137.7253 | -146.6596 | -154.6616 | 172.9242 | 172.7957 | 66.3641 | -10.1378 | -12.3976 | -14.6918 | -76.351 | -80.3555 | -85.3519 | -91.3444 | -105.3144 | -160.3114 | -171.41 | -180.836 | 174.1911 | 174.1911 | 66.6647 | -9.5181 | -11.7711 | -14.0583 | -75.5972 | -79.5895 | -84.5707 | -90.5449 | -104.4724 | -159.302 | -170.3569 | -179.7542
NORTH HYDE GSP | NORTH HYDE (D) | NORTH HYDE (D) | MINIMUM HEADROOM | TQ 10367 79001 | NO | 42.5095 | 42.4957 | 42.368 | 42.2236 | 42.0585 | 41.8779 | 41.7119 | 41.5662 | 41.4086 | 41.2477 | 40.9153 | 39.9627 | 39.0097 | 38.0526 | 39.854 | 39.7459 | 39.6144 | 39.4658 | 39.2958 | 39.1099 | 38.939 | 38.7891 | 38.6268 | 38.4612 | 38.119 | 37.0491 | 35.9223 | 34.7907 | 40.0345 | 40.0345 | 39.8929 | 39.7288 | 39.541 | 39.3356 | 39.1469 | 38.9813 | 38.802 | 38.6192 | 38.2411 | 37.1581 | 36.0745 | 34.9667
|  |  | CT |  |  | 42.5095 | 42.4957 | 42.368 | 42.2236 | 42.0585 | 41.8779 | 41.7119 | 41.5662 | 41.4086 | 41.2477 | 40.9153 | 39.9627 | 39.0097 | 38.0526 | 39.858 | 39.7611 | 39.6364 | 39.4954 | 39.333 | 39.1555 | 38.9972 | 38.8565 | 38.6948 | 38.5271 | 38.1918 | 37.2708 | 36.25 | 35.2165 | 40.0345 | 40.0345 | 39.9173 | 39.7614 | 39.5821 | 39.3861 | 39.2112 | 39.0557 | 38.8772 | 38.6919 | 38.3216 | 37.3712 | 36.3896 | 35.3917
|  |  | LW |  |  | 42.5095 | 42.4957 | 42.368 | 42.2236 | 42.0585 | 41.8779 | 41.7119 | 41.5662 | 41.4086 | 41.2477 | 40.9153 | 39.9627 | 39.0097 | 38.0526 | 39.854 | 39.7459 | 39.6144 | 39.4658 | 39.2958 | 39.1099 | 38.939 | 38.7891 | 38.6268 | 38.4612 | 38.119 | 37.0491 | 35.9223 | 34.7907 | 40.0345 | 40.0345 | 39.8929 | 39.7288 | 39.541 | 39.3356 | 39.1469 | 38.9813 | 38.802 | 38.6192 | 38.2411 | 37.1581 | 36.0745 | 34.9667
|  |  | ST |  |  | 42.5095 | 42.5095 | 42.5095 | 42.4485 | 42.3414 | 42.2063 | 42.0843 | 41.9742 | 41.8479 | 41.717 | 41.4545 | 40.82 | 40.1963 | 39.5788 | 39.9858 | 39.8433 | 39.782 | 39.6972 | 39.587 | 39.4479 | 39.3223 | 39.2091 | 39.079 | 38.9443 | 38.6741 | 38.021 | 37.3253 | 36.5952 | 40.0345 | 40.0345 | 40.0345 | 39.9844 | 39.8627 | 39.7091 | 39.5703 | 39.4452 | 39.3016 | 39.1527 | 38.8543 | 38.1329 | 37.4237 | 36.7216
|  |  | FS |  |  | 42.5095 | 42.5095 | 42.5095 | 42.5095 | 42.5095 | 42.5095 | 42.481 | 42.4382 | 42.394 | 42.3493 | 42.2586 | 42.033 | 41.8026 | 41.5606 | 40.0235 | 39.9096 | 39.8903 | 39.8583 | 39.82 | 39.7726 | 39.7307 | 39.6867 | 39.6412 | 39.5951 | 39.5018 | 39.2696 | 39.0324 | 38.7833 | 40.0345 | 40.0345 | 40.0345 | 40.0345 | 40.0345 | 40.0345 | 40.0214 | 39.9728 | 39.9225 | 39.8716 | 39.7686 | 39.512 | 39.2501 | 38.9749
NORTH HYDE GSP | NORTH HYDE 11 | NORTH HYDE 11 | MINIMUM HEADROOM | TQ 10367 79001 | NO | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.4744 | 86.4744 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.3081 | 83.3081 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329
|  |  | CT |  |  | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.4744 | 86.4744 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.4379 | 83.4379 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329
|  |  | LW |  |  | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.4744 | 86.4744 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.3081 | 83.3081 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329
|  |  | ST |  |  | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5033 | 86.5033 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.4379 | 83.4379 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329
|  |  | FS |  |  | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 83.7762 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329 | 84.6329
IVER 66KV | NORTHOLT | NORTHOLT | MINIMUM HEADROOM | TQ 11550 83230 | NO | 42.0055 | 41.9862 | 41.942 | 41.8929 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 37.0117 | 36.0035 | 40.7152 | 40.6783 | 40.5938 | 40.4999 | 40.3958 | 40.2871 | 40.1613 | 40.0239 | 39.8489 | 39.665 | 39.2706 | 34.3996 | 32.9856 | 31.5738 | 39.5549 | 39.522 | 39.4466 | 35.5715 | 35.4661 | 35.3561 | 35.2288 | 35.0896 | 34.9126 | 34.7263 | 34.3272 | 32.9497 | 31.5899 | 30.2323
|  |  | CT |  |  | 42.0055 | 41.9862 | 41.942 | 41.8929 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 37.0117 | 36.0035 | 40.7176 | 40.6845 | 40.6084 | 40.5223 | 40.4288 | 40.3349 | 40.2355 | 40.128 | 39.9875 | 39.8394 | 39.5111 | 34.8516 | 33.6175 | 32.3841 | 39.557 | 39.5275 | 39.4596 | 35.5942 | 35.4996 | 35.4045 | 35.3038 | 35.195 | 35.0528 | 34.9029 | 34.5706 | 33.3844 | 32.1976 | 31.0115
|  |  | LW |  |  | 42.0055 | 41.9862 | 41.942 | 41.8929 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 37.0117 | 36.0035 | 40.7152 | 40.6783 | 40.5938 | 40.4999 | 40.3958 | 40.2871 | 40.1613 | 40.0239 | 39.8489 | 39.665 | 39.2706 | 34.3996 | 32.9856 | 31.5738 | 39.5549 | 39.522 | 39.4466 | 35.5715 | 35.4661 | 35.3561 | 35.2288 | 35.0896 | 34.9126 | 34.7263 | 34.3272 | 32.9497 | 31.5899 | 30.2323
|  |  | ST |  |  | 42.0122 | 42.0021 | 41.981 | 41.9482 | 41.9064 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 37.5617 | 36.8347 | 40.728 | 40.7087 | 40.6684 | 40.6058 | 40.5259 | 40.3795 | 40.2311 | 40.0788 | 39.8972 | 39.711 | 39.3178 | 34.7955 | 33.7558 | 32.7378 | 39.5663 | 39.5491 | 39.5131 | 39.4573 | 35.5978 | 35.4496 | 35.2994 | 35.1453 | 34.9614 | 34.773 | 34.375 | 33.3304 | 32.3306 | 31.3516
|  |  | FS |  |  | 42.0175 | 42.0159 | 42.0141 | 42.0063 | 41.9958 | 41.9758 | 41.9555 | 41.9288 | 41.8991 | 41.8685 | 41.8591 | 41.8591 | 41.8591 | 41.8591 | 40.7382 | 40.7351 | 40.7317 | 40.7167 | 40.6967 | 40.6585 | 40.6197 | 40.5687 | 40.5119 | 40.4534 | 40.3305 | 39.994 | 39.6549 | 39.3105 | 39.5754 | 39.5727 | 39.5696 | 39.5563 | 39.5384 | 39.5043 | 39.4696 | 39.4241 | 35.5837 | 35.5244 | 35.4 | 35.0594 | 34.7162 | 34.3675
COWLEY GSP | OXFORD (OSNEY) BSP | OXFORD (OSNEY) BSP | MINIMUM HEADROOM | SP 50054 05983 | YES | 92.2839 | 92.2839 | 92.2839 | 85.1278 | 83.2768 | 81.3813 | 79.4628 | 78.4302 | 76.4471 | 74.4215 | 70.4025 | 64.8322 | 59.044 | 53.7989 | 90.5839 | 90.5839 | 84.1374 | 81.6841 | 79.2379 | 76.602 | 73.7927 | 70.6597 | 67.8602 | 65.0801 | 60.7131 | 54.2118 | 47.2571 | 40.4348 | 95.716 | 95.716 | 85.477 | 83.227 | 80.9834 | 78.566 | 75.9894 | 73.0957 | 70.5079 | 67.9379 | 63.8922 | 57.8283 | 51.3487 | 44.4467
|  |  | CT |  |  | 92.2839 | 92.2839 | 92.2839 | 85.1278 | 83.2768 | 81.3813 | 79.4628 | 78.4302 | 76.4471 | 74.4215 | 70.4025 | 64.8322 | 59.044 | 53.7989 | 90.5839 | 90.5839 | 84.1374 | 81.6841 | 79.2379 | 76.602 | 73.7927 | 70.6597 | 67.8602 | 65.0801 | 60.7131 | 54.2118 | 47.2571 | 40.4348 | 95.716 | 95.716 | 85.477 | 83.227 | 80.9834 | 78.566 | 75.9894 | 73.0957 | 70.5079 | 67.9379 | 63.8922 | 57.8283 | 51.3487 | 44.4467
|  |  | LW |  |  | 92.2839 | 92.2839 | 92.2839 | 85.1278 | 83.2768 | 81.3813 | 79.4628 | 78.4302 | 76.4471 | 74.4215 | 70.4025 | 64.8322 | 59.044 | 53.7989 | 90.5839 | 90.5839 | 84.2712 | 82.1303 | 79.9417 | 77.7005 | 75.4321 | 74.0586 | 71.7239 | 69.3392 | 64.6075 | 58.072 | 51.279 | 45.1281 | 95.716 | 95.716 | 95.716 | 83.6362 | 81.6289 | 79.5734 | 77.493 | 76.2971 | 74.1457 | 71.9484 | 67.5886 | 61.5439 | 55.2631 | 49.3189
|  |  | ST |  |  | 92.2839 | 92.2839 | 92.2839 | 92.2839 | 92.2839 | 84.748 | 83.3492 | 81.69 | 80.3505 | 78.9565 | 77.2072 | 74.9338 | 71.5829 | 68.3437 | 90.5839 | 90.5839 | 90.5839 | 84.7279 | 83.1659 | 81.6812 | 80.0273 | 78.0655 | 76.4818 | 74.8335 | 72.7652 | 69.9145 | 65.9525 | 62.1226 | 95.716 | 95.716 | 95.716 | 95.716 | 84.586 | 83.2243 | 81.7074 | 79.9081 | 78.4556 | 76.9439 | 75.047 | 72.5064 | 68.8727 | 65.3601
|  |  | FS |  |  | 92.2839 | 92.2839 | 92.2839 | 92.2839 | 92.2839 | 92.2839 | 92.2839 | 92.2839 | 92.2839 | 92.2839 | 84.8198 | 82.7233 | 80.8557 | 79.2553 | 90.6084 | 90.5839 | 90.5839 | 90.5839 | 90.5839 | 90.5839 | 85.1025 | 84.4966 | 83.8815 | 83.2178 | 81.766 | 79.2872 | 77.079 | 75.1868 | 95.716 | 95.716 | 95.716 | 95.716 | 95.716 | 95.716 | 95.716 | 95.716 | 85.2423 | 84.6336 | 83.3021 | 81.0287 | 79.0034 | 77.268
WILLESDEN GSP | PERIVALE | PERIVALE | MINIMUM HEADROOM | TQ 17544 82947 | NO | 93.9401 | 93.934 | 93.9195 | 93.9037 | 93.8882 | 93.8728 | 93.8571 | 93.8412 | 93.8232 | 93.805 | 93.7684 | 93.7517 | 93.7517 | 93.7517 | 85.2014 | 85.1873 | 85.1713 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821
|  |  | CT |  |  | 93.9401 | 93.934 | 93.9195 | 93.9037 | 93.8882 | 93.8728 | 93.8571 | 93.8412 | 93.8232 | 93.805 | 93.7684 | 93.7517 | 93.7517 | 93.7517 | 85.2022 | 85.188 | 85.173 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821
|  |  | LW |  |  | 93.9401 | 93.934 | 93.9195 | 93.9037 | 93.8882 | 93.8728 | 93.8571 | 93.8412 | 93.8232 | 93.805 | 93.7684 | 93.7517 | 93.7517 | 93.7517 | 85.2014 | 85.1873 | 85.1713 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821
|  |  | ST |  |  | 93.943 | 93.941 | 93.9366 | 93.9301 | 93.9222 | 93.9146 | 93.9069 | 93.8992 | 93.8905 | 93.8817 | 93.8639 | 93.8182 | 93.7737 | 93.7517 | 85.2105 | 85.2042 | 85.1903 | 85.183 | 85.1743 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 85.1665 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821
|  |  | FS |  |  | 93.9439 | 93.9435 | 93.9431 | 93.9405 | 93.9374 | 93.9349 | 93.9324 | 93.9292 | 93.9258 | 93.9224 | 93.9156 | 93.8983 | 93.8813 | 93.8649 | 85.2136 | 85.2124 | 85.2109 | 85.2027 | 85.1928 | 85.1883 | 85.1856 | 85.182 | 85.1783 | 85.1746 | 85.1671 | 85.1665 | 85.1665 | 85.1665 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821 | 86.4821
MANNINGTON GSP | POOLE PS (HAMWORTHY) | POOLE PS (HAMWORTHY) | MINIMUM HEADROOM | SZ 00203 90789 | YES | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.6791 | 70.4689 | 70.367 | 56.5102 | 55.3815 | 52.3974 | 47.2954 | 32.2341 | 28.8148 | 65.4096 | 65.3273 | 65.2581 | 65.0204 | 64.7987 | 56.4333 | 54.9625 | 53.2109 | 51.7207 | 50.1424 | 48.3113 | 43.5752 | 26.4768 | 22.9993 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.0217 | 56.0244 | 54.3339 | 52.8824 | 51.3544 | 49.5218 | 44.5757 | 27.3082 | 23.6941
|  |  | CT |  |  | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.6791 | 70.4689 | 70.367 | 56.9632 | 55.3815 | 52.3974 | 47.2954 | 32.2341 | 28.8148 | 65.4128 | 65.3417 | 65.2794 | 65.0204 | 64.7987 | 56.4333 | 54.9625 | 53.2109 | 51.7207 | 50.1424 | 48.3113 | 44.6466 | 34.957 | 32.2508 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 56.0244 | 54.3339 | 52.8824 | 51.3544 | 49.5218 | 45.6467 | 35.5626 | 32.7374
|  |  | LW |  |  | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.6791 | 70.4689 | 70.367 | 56.9632 | 55.3815 | 52.3974 | 47.2954 | 32.2341 | 28.8148 | 65.4096 | 65.3273 | 65.2581 | 65.0599 | 64.8764 | 56.8039 | 55.8987 | 55.0478 | 53.4527 | 51.7535 | 48.7118 | 43.5752 | 26.4768 | 22.9993 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.0217 | 56.8509 | 56.0437 | 54.4769 | 52.8218 | 49.7634 | 44.5757 | 27.3082 | 23.6941
|  |  | ST |  |  | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.8409 | 70.7393 | 70.6494 | 56.5102 | 55.3869 | 54.0954 | 51.9139 | 44.3009 | 41.583 | 65.4336 | 65.3839 | 65.3435 | 65.0839 | 64.869 | 56.6375 | 55.3983 | 53.8581 | 52.6235 | 51.317 | 49.8826 | 47.5622 | 38.776 | 35.9596 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.1815 | 56.4661 | 55.0307 | 53.8552 | 52.6336 | 51.2575 | 48.9831 | 40.2792 | 37.3657
|  |  | FS |  |  | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.9501 | 70.9031 | 70.8529 | 70.7897 | 70.728 | 70.6674 | 70.5697 | 70.5139 | 56.3047 | 65.4557 | 65.4278 | 65.4112 | 65.3306 | 65.2216 | 65.1482 | 65.042 | 64.9124 | 64.7545 | 64.5751 | 55.9133 | 54.3636 | 53.2072 | 52.3861 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.2894 | 66.243 | 66.1934 | 66.131 | 66.07 | 56.9183 | 55.4721 | 54.3975 | 53.6288
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ 63405 99685 | YES | 85.3178 | 85.1286 | 84.7742 | 84.3277 | 83.6623 | 83.0591 | 82.4453 | 81.7248 | 80.9544 | 80.1539 | 78.4957 | 72.9918 | 68.3746 | 63.8854 | 85.3779 | 85.086 | 84.5387 | 83.8606 | 83.1175 | 82.444 | 81.7588 | 80.9546 | 80.0949 | 79.2017 | 77.3522 | 71.214 | 65.9878 | 60.7413 | 85.438 | 85.1392 | 84.5791 | 83.8849 | 83.1242 | 82.4346 | 81.7329 | 80.9094 | 80.0288 | 79.1139 | 77.2188 | 70.9289 | 65.6556 | 60.5304
|  |  | CT |  |  | 85.3178 | 85.1286 | 84.7742 | 84.3277 | 83.6623 | 83.0591 | 82.4453 | 81.7248 | 80.9544 | 80.1539 | 78.4957 | 72.9918 | 68.3746 | 63.8854 | 85.3943 | 85.1375 | 84.6471 | 84.0472 | 83.3848 | 82.7759 | 82.1565 | 81.4065 | 80.5715 | 79.6877 | 77.8695 | 73.1526 | 68.7676 | 64.2979 | 85.4541 | 85.1908 | 84.688 | 84.0731 | 83.3942 | 82.77 | 82.1348 | 81.366 | 80.5098 | 79.6034 | 77.7382 | 72.8963 | 68.3874 | 63.9574
|  |  | LW |  |  | 85.3178 | 85.1286 | 84.7742 | 84.3277 | 83.6623 | 83.0591 | 82.4453 | 81.7248 | 80.9544 | 80.1539 | 78.4957 | 72.9918 | 68.3746 | 63.8854 | 85.3779 | 85.086 | 84.5387 | 83.8606 | 83.1175 | 82.444 | 81.7588 | 80.9546 | 80.0949 | 79.2017 | 77.3522 | 71.214 | 65.9878 | 60.7413 | 85.438 | 85.1392 | 84.5791 | 83.8849 | 83.1242 | 82.4346 | 81.7329 | 80.9094 | 80.0288 | 79.1139 | 77.2188 | 70.9289 | 65.6556 | 60.5304
|  |  | ST |  |  | 86.7061 | 85.2681 | 85.0668 | 84.7676 | 84.4027 | 83.7475 | 83.0741 | 82.3287 | 81.5009 | 80.6418 | 78.89 | 75.656 | 72.762 | 69.9277 | 88.102 | 85.3007 | 84.9897 | 84.5273 | 83.9634 | 83.2113 | 82.459 | 81.626 | 80.7011 | 79.7411 | 77.7837 | 74.172 | 70.9422 | 67.7481 | 88.0822 | 85.3592 | 85.0409 | 84.5678 | 83.9907 | 83.2212 | 82.4512 | 81.5988 | 80.6523 | 79.67 | 77.6669 | 73.9696 | 70.6616 | 67.4225
|  |  | FS |  |  | 86.9855 | 85.4315 | 85.3781 | 85.2754 | 85.1589 | 84.9832 | 84.8069 | 84.5796 | 84.344 | 84.0157 | 83.345 | 81.859 | 80.6961 | 79.6478 | 88.4909 | 87.7033 | 85.4708 | 85.3123 | 85.1323 | 84.8608 | 84.5885 | 84.2372 | 83.8782 | 83.5114 | 82.762 | 81.1022 | 79.8041 | 78.6344 | 88.3484 | 87.9917 | 87.9721 | 85.371 | 85.1868 | 84.909 | 84.6302 | 84.2708 | 83.9033 | 83.528 | 82.7611 | 81.0621 | 79.7328 | 78.5346
BRAMLEY (FLEE) | PYESTOCK BSP | PYESTOCK BSP | MINIMUM HEADROOM | SU 82940 54553 | YES | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.5303 | 54.5303 | 54.5303 | 54.3981 | 54.2757 | 54.1223 | 53.9377 | 53.6909 | 53.4992 | 53.3008 | 53.1426 | 53.0673 | 52.9433 | 52.8393 | 54.6835 | 54.6835 | 54.6835 | 54.636 | 54.5921 | 54.537 | 54.4707 | 54.3821 | 54.3133 | 54.242 | 54.1852 | 54.1582 | 54.1136 | 54.0766
|  |  | CT |  |  | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.5303 | 54.5303 | 54.5303 | 54.3981 | 54.2757 | 54.1224 | 53.9378 | 53.6909 | 53.4992 | 53.3008 | 53.1426 | 53.0674 | 52.9433 | 52.8394 | 54.6835 | 54.6835 | 54.6835 | 54.636 | 54.5921 | 54.537 | 54.4707 | 54.3821 | 54.3133 | 54.242 | 54.1852 | 54.1582 | 54.1137 | 54.0766
|  |  | LW |  |  | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.5303 | 54.5303 | 54.5303 | 54.4464 | 54.3623 | 54.2754 | 54.1907 | 54.1059 | 53.9737 | 53.8282 | 53.5544 | 53.3903 | 53.2356 | 53.2209 | 54.6835 | 54.6835 | 54.6835 | 54.6534 | 54.6232 | 54.592 | 54.5616 | 54.5311 | 54.4836 | 54.4314 | 54.3331 | 54.2742 | 54.2186 | 54.2133
|  |  | ST |  |  | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.5303 | 54.5303 | 54.5303 | 54.4083 | 54.2757 | 54.1223 | 53.9377 | 53.6909 | 53.5057 | 53.3008 | 53.1426 | 53.0673 | 52.9433 | 52.8393 | 54.6835 | 54.6835 | 54.6835 | 54.6397 | 54.5921 | 54.537 | 54.4707 | 54.3821 | 54.3156 | 54.242 | 54.1852 | 54.1582 | 54.1136 | 54.0766
|  |  | FS |  |  | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.0245 | 54.5303 | 54.5303 | 54.5303 | 54.5117 | 54.4833 | 54.4554 | 54.4182 | 54.367 | 54.3017 | 54.2223 | 54.0354 | 53.8056 | 53.6333 | 53.5298 | 54.6835 | 54.6835 | 54.6835 | 54.6768 | 54.6666 | 54.6566 | 54.6432 | 54.6249 | 54.6014 | 54.5729 | 54.5058 | 54.4233 | 54.3614 | 54.3242
BRAMLEY (FLEE) | READING BSP | READING BSP | MINIMUM HEADROOM | SU 74642 73856 | YES | 190.8664 | 190.8642 | 190.8612 | 190.8574 | 190.8527 | 190.8469 | 190.84 | 170.139 | 166.7039 | 163.2338 | 156.3324 | 144.616 | 132.4334 | 121.1501 | 186.6674 | 186.6635 | 186.6577 | 186.6516 | 186.645 | 170.2802 | 166.4199 | 162.2526 | 158.0739 | 153.8552 | 146.2678 | 134.0495 | 121.1309 | 108.316 | 189.4091 | 189.4018 | 189.3908 | 189.3792 | 189.3665 | 189.3529 | 167.4353 | 163.2765 | 159.1063 | 154.896 | 147.3212 | 135.1078 | 122.1996 | 109.3927
|  |  | CT |  |  | 190.8664 | 190.8642 | 190.8612 | 190.8574 | 190.8527 | 190.8469 | 190.84 | 170.139 | 166.7039 | 163.2338 | 156.3324 | 144.616 | 132.4334 | 121.1501 | 186.6674 | 186.6635 | 186.6577 | 186.6516 | 186.645 | 170.2802 | 166.4199 | 162.2526 | 158.0739 | 153.8552 | 146.2678 | 134.0495 | 121.1309 | 108.316 | 189.4091 | 189.4018 | 189.3908 | 189.3792 | 189.3665 | 189.3529 | 167.4353 | 163.2765 | 159.1063 | 154.896 | 147.3212 | 135.1078 | 122.1996 | 109.3927
|  |  | LW |  |  | 190.8664 | 190.8642 | 190.8612 | 190.8574 | 190.8527 | 190.8469 | 190.84 | 170.139 | 166.7039 | 163.2338 | 156.3324 | 144.616 | 132.4334 | 121.1501 | 186.6709 | 186.6697 | 186.6681 | 186.6661 | 186.6635 | 186.6603 | 169.2984 | 166.1002 | 162.125 | 158.1088 | 150.1238 | 136.6808 | 122.676 | 109.6495 | 189.416 | 189.4137 | 189.4106 | 189.4067 | 189.4018 | 189.3958 | 170.3185 | 167.1277 | 163.1612 | 159.1536 | 151.1846 | 137.7568 | 123.7686 | 110.756
|  |  | ST |  |  | 190.8685 | 190.8678 | 190.8667 | 190.8655 | 190.8641 | 190.8622 | 190.86 | 190.8576 | 190.7629 | 190.6681 | 169.2354 | 162.844 | 155.8317 | 148.837 | 186.6721 | 186.6717 | 186.6711 | 186.6704 | 186.6697 | 186.6686 | 186.6674 | 186.6661 | 186.5726 | 168.7849 | 165.0917 | 157.6523 | 149.5574 | 141.4988 | 189.4181 | 189.4173 | 189.4163 | 189.415 | 189.4136 | 189.4115 | 189.4093 | 189.4068 | 189.3121 | 169.8095 | 166.1253 | 158.7018 | 150.6213 | 142.5778
|  |  | FS |  |  | 190.8688 | 190.8683 | 190.8678 | 190.8669 | 190.866 | 190.8651 | 190.8641 | 190.863 | 190.8619 | 190.8608 | 190.8583 | 190.8488 | 190.839 | 190.9175 | 186.6722 | 186.6719 | 186.6717 | 186.6712 | 186.6707 | 186.6702 | 186.6697 | 186.6691 | 186.6685 | 186.6679 | 186.6665 | 186.6614 | 186.656 | 168.1229 | 189.4184 | 189.4179 | 189.4173 | 189.4165 | 189.4156 | 189.4146 | 189.4135 | 189.4125 | 189.4113 | 189.4101 | 189.4075 | 189.3977 | 189.3876 | 169.1438
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN BSP | MINIMUM HEADROOM | SU 71580 74111 | YES | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 82.8817 | 79.4646 | 76.106 | 99.7027 | 99.5864 | 99.3534 | 99.0925 | 98.8867 | 98.7762 | 98.7762 | 98.7762 | 98.7762 | 98.7762 | 82.3437 | 77.8193 | 73.5074 | 69.287 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 82.7628 | 78.2989 | 74.0545 | 69.9046
|  |  | CT |  |  | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 82.8817 | 79.4646 | 76.106 | 99.7051 | 99.5919 | 99.3626 | 99.1078 | 98.8986 | 98.7762 | 98.7762 | 98.7762 | 98.7762 | 98.7762 | 82.3437 | 77.8193 | 73.5074 | 69.287 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 82.7628 | 78.2989 | 74.0545 | 69.9046
|  |  | LW |  |  | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 82.8817 | 79.4646 | 76.106 | 99.7027 | 99.5864 | 99.3534 | 99.0925 | 98.8867 | 98.7762 | 98.7762 | 98.7762 | 98.7762 | 98.7762 | 82.365 | 78.2228 | 74.2034 | 70.2469 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 82.7837 | 78.697 | 74.7389 | 70.8485
|  |  | ST |  |  | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 100.3069 | 99.7285 | 99.6343 | 99.5285 | 99.4034 | 99.3074 | 99.2123 | 99.1142 | 99.008 | 98.9259 | 98.8032 | 98.7762 | 98.7762 | 98.7762 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226
|  |  | FS |  |  | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 102.7772 | 100.419 | 100.0988 | 99.9912 | 99.7018 | 99.6477 | 99.6096 | 99.5726 | 99.5281 | 99.4838 | 99.4393 | 99.3484 | 99.1739 | 99.0225 | 98.9156 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226 | 101.1226
MANNINGTON GSP | REDHILL BSP | REDHILL BSP | MINIMUM HEADROOM | SZ 08581 96162 | YES | 83.8468 | 81.8765 | 50.7499 | 50.484 | 50.1559 | 49.7968 | 49.4196 | 50.8882 | 50.5206 | 50.1869 | 49.5883 | 17.5731 | 10.7013 | 7.3994 | 83.564 | 81.6172 | 44.9074 | 44.5942 | 44.2077 | 43.7846 | 43.3403 | 44.7405 | 44.3075 | 43.9144 | 43.2092 | 5.4948 | -2.6003 | -6.49 | 83.7564 | 81.8097 | 45.1949 | 44.8827 | 44.4973 | 44.0756 | 43.6326 | 45.0342 | 44.6025 | 44.2106 | 43.5075 | 5.908 | -2.1625 | -6.0403
|  |  | CT |  |  | 83.8468 | 81.9818 | 50.7499 | 50.484 | 50.1559 | 49.7968 | 49.4196 | 50.8882 | 50.5206 | 50.1869 | 49.5883 | 17.5731 | 10.7013 | 7.3994 | 83.5644 | 83.455 | 81.4456 | 81.145 | 80.78 | 80.3808 | 79.964 | 79.5278 | 79.0934 | 78.6824 | 77.9532 | 57.8809 | 52.6028 | 49.417 | 83.7569 | 83.6473 | 81.6379 | 81.3372 | 80.972 | 80.5728 | 80.1558 | 79.7195 | 79.2849 | 78.8738 | 78.1444 | 58.1289 | 52.8669 | 49.6907
|  |  | LW |  |  | 83.8468 | 81.9818 | 50.7499 | 50.484 | 50.1559 | 49.7968 | 49.4196 | 50.8882 | 50.5206 | 50.1869 | 49.5883 | 17.5731 | 10.7013 | 7.3994 | 83.564 | 81.6822 | 44.9074 | 44.5942 | 44.2077 | 43.7846 | 43.3403 | 44.7405 | 44.3075 | 43.9144 | 43.2092 | 5.4948 | -2.6003 | -6.49 | 83.7564 | 81.8746 | 45.1949 | 44.8827 | 44.4973 | 44.0756 | 43.6326 | 45.0342 | 44.6025 | 44.2106 | 43.5075 | 5.908 | -2.1625 | -6.0403
|  |  | ST |  |  | 84.8925 | 83.833 | 83.7344 | 83.5866 | 83.3872 | 82.8561 | 82.3202 | 81.7784 | 81.2101 | 80.6581 | 79.621 | 64.6461 | 60.491 | 58.1395 | 84.7918 | 83.5478 | 83.4321 | 83.2586 | 83.0244 | 82.401 | 81.7717 | 81.1357 | 80.4684 | 79.8204 | 78.6028 | 60.6327 | 55.738 | 52.9679 | 84.9729 | 83.7402 | 83.6245 | 83.4509 | 83.2167 | 82.593 | 81.9635 | 81.3273 | 80.6598 | 80.0116 | 78.7935 | 60.8834 | 56.0035 | 53.2419
|  |  | FS |  |  | 86.5157 | 81.8765 | 81.8423 | 81.7785 | 81.6979 | 81.5288 | 81.3587 | 81.1571 | 80.9616 | 80.7745 | 80.4179 | 79.5933 | 78.7858 | 77.9818 | 86.3815 | 81.6172 | 81.5771 | 81.5021 | 81.4076 | 81.209 | 81.0093 | 80.7726 | 80.5431 | 80.3234 | 79.9048 | 78.9367 | 77.9886 | 77.0447 | 86.4834 | 81.8097 | 81.7696 | 81.6945 | 81.6 | 81.4013 | 81.2016 | 80.9648 | 80.7352 | 80.5154 | 80.0967 | 79.1283 | 78.1799 | 77.2356
NURSLING GSP | ROWNHAMS | ROWNHAMS | MINIMUM HEADROOM | SU 37168 16854 | YES | 85.5 | 85.5 | 85.5 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 90 | 90 | 90 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 26.239 | 19.5823 | -97.6733 | -50.5868 | -52.8449 | -55.1778 | -57.5438 | -57.8573 | -62.5341 | -67.4472 | -77.1552 | -93.5306 | -117.2864 | -129.6524
|  |  | CT |  |  | 85.5 | 85.5 | 85.5 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 90 | 90 | 90 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 65.4069 | 26.3929 | -27.2042 | 37.5366 | -17.773 | -20.9085 | -24.5163 | -28.6912 | -33.0799 | -37.6174 | -43.5859 | -54.1914 | -69.393 | -80.413
|  |  | LW |  |  | 85.5 | 85.5 | 85.5 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 90 | 90 | 90 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 26.239 | 19.5823 | -97.6733 | -50.5868 | -52.8449 | -55.1778 | -57.5438 | -57.8573 | -62.5341 | -67.4472 | -77.1552 | -93.5306 | -117.2864 | -129.6524
|  |  | ST |  |  | 85.5 | 85.5 | 85.5 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 90 | 90 | 90 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 66.2822 | 26.8842 | -26.2565 | 38.9195 | -16.3386 | -19.2575 | -22.6288 | -26.5472 | -30.2925 | -34.3467 | -39.1465 | -45.0271 | -58.4029 | -67.8478
|  |  | FS |  |  | 85.5 | 85.5 | 85.5 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 90 | 90 | 90 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 66.6682 | 66.0107 | -25.0938 | 41.9661 | 41.3513 | 40.694 | 39.8979 | 39.1682 | -14.7179 | -16.1799 | -19.4955 | -24.4049 | -28.4791 | -31.552
MANNINGTON GSP | SALISBURY | SALISBURY | MINIMUM HEADROOM | SU 11049 31395 | YES | 108.8756 | 94.8712 | 78.7812 | 75.9406 | 73.0452 | 70.0144 | 66.974 | 64.1596 | 60.7623 | 57.1224 | 50.1545 | 38.7837 | 27.0801 | 21.9373 | 105.8277 | 90.6736 | 71.7832 | 68.4501 | 65.0527 | 61.4964 | 57.9288 | 54.5917 | 50.6054 | 46.3343 | 38.1577 | 25.1131 | 11.3777 | 5.3448 | 106.6809 | 90.419 | 71.5225 | 68.1883 | 64.7898 | 61.2323 | 57.6636 | 54.3252 | 50.3377 | 46.0651 | 37.8859 | 24.6674 | 10.9275 | 4.8927
|  |  | CT |  |  | 108.8756 | 94.8712 | 78.7812 | 75.9406 | 73.0452 | 70.0144 | 66.974 | 64.1596 | 60.7623 | 57.1224 | 50.1545 | 38.7837 | 27.0801 | 21.9373 | 105.8277 | 105.8277 | 105.8277 | 99.0659 | 94.5105 | 88.9286 | 82.3121 | 73.8024 | 68.4486 | 62.9539 | 57.5386 | 48.1121 | 37.3598 | 29.3432 | 106.6813 | 106.6576 | 106.6576 | 98.8141 | 94.2571 | 88.6735 | 82.0548 | 73.5423 | 68.1867 | 62.6903 | 57.2732 | 47.674 | 36.9182 | 28.8989
|  |  | LW |  |  | 108.8756 | 94.8712 | 78.7812 | 75.9406 | 73.0452 | 70.0144 | 66.974 | 64.1596 | 60.7623 | 57.1224 | 50.1545 | 38.7837 | 27.0801 | 21.9373 | 105.8277 | 90.6736 | 71.7832 | 68.4501 | 65.0527 | 61.4964 | 57.9288 | 54.5917 | 50.6054 | 46.3343 | 38.1577 | 25.1131 | 11.3777 | 5.3448 | 106.6809 | 90.419 | 71.5225 | 68.1883 | 64.7898 | 61.2323 | 57.6636 | 54.3252 | 50.3377 | 46.0651 | 37.8859 | 24.6674 | 10.9275 | 4.8927
|  |  | ST |  |  | 108.8756 | 108.8756 | 108.8756 | 108.8697 | 99.2072 | 94.5834 | 89.1016 | 82.0011 | 77.7042 | 73.0227 | 68.6821 | 62.6378 | 55.2945 | 50.3011 | 105.9699 | 105.8277 | 105.8277 | 105.8218 | 95.7664 | 90.3388 | 83.9041 | 75.5689 | 70.5252 | 65.0296 | 59.9348 | 52.9525 | 44.3323 | 38.4705 | 106.7249 | 106.6784 | 106.6576 | 106.6517 | 95.5135 | 90.0842 | 83.6473 | 75.3094 | 70.264 | 64.7666 | 59.6702 | 52.6007 | 43.9777 | 38.114
|  |  | FS |  |  | 108.8756 | 108.8756 | 108.8756 | 108.8739 | 108.8722 | 108.8706 | 108.8689 | 108.8678 | 108.8662 | 97.4809 | 92.0217 | 84.7296 | 78.9845 | 75.0693 | 106.1011 | 105.8748 | 105.8557 | 105.826 | 105.8244 | 105.8227 | 105.821 | 98.8255 | 96.5019 | 93.7392 | 87.33 | 78.7695 | 72.0247 | 67.4284 | 106.739 | 106.7019 | 106.6973 | 106.6559 | 106.6543 | 106.6526 | 106.6509 | 98.5735 | 96.2493 | 93.4856 | 87.0743 | 78.511 | 71.764 | 67.1662
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST 85442 23791 | YES | 98.4515 | 75.4785 | 75.265 | 73.5548 | -33.4216 | -35.861 | -38.1586 | -40.262 | -42.8335 | -45.5827 | -51.1831 | -71.7327 | -84.8345 | -88.8481 | 84.0999 | 70.7285 | 70.4766 | 68.4599 | -38.8424 | -41.4947 | -44.0296 | -46.424 | -49.3128 | -52.4292 | -58.5993 | -82.1239 | -96.9206 | -101.3739 | 83.5741 | 70.243 | 69.9914 | 67.9801 | -39.3165 | -42.1033 | -44.7414 | -47.1832 | -50.1549 | -53.343 | -59.772 | -83.6955 | -98.8848 | -103.4993
|  |  | CT |  |  | 98.4515 | 75.4785 | 75.265 | 73.5548 | -33.4216 | -35.861 | -38.1586 | -40.262 | -42.8335 | -45.5827 | -51.1831 | -71.7327 | -84.8345 | -88.8481 | 95.1625 | 83.9856 | 83.7459 | 80.8219 | 77.9769 | 74.495 | -35.2417 | -40.9816 | -44.7401 | -48.6567 | -52.7535 | -67.0217 | -77.462 | -82.9965 | 95.857 | 83.4579 | 83.2172 | 80.3002 | 77.4618 | 73.9883 | -35.9035 | -41.7717 | -45.6135 | -49.6079 | -53.8602 | -68.6271 | -79.4835 | -85.1498
|  |  | LW |  |  | 98.4515 | 75.4785 | 75.265 | 73.5548 | -33.4216 | -35.861 | -38.1586 | -40.262 | -42.8335 | -45.5827 | -51.1831 | -71.7327 | -84.8345 | -88.8481 | 84.0999 | 70.7285 | 70.4766 | 68.4599 | -38.8424 | -41.4947 | -44.0296 | -46.424 | -49.3128 | -52.4292 | -58.5993 | -82.1239 | -96.9206 | -101.3739 | 83.5741 | 70.243 | 69.9914 | 67.9801 | -39.3165 | -42.1033 | -44.7414 | -47.1832 | -50.1549 | -53.343 | -59.772 | -83.6955 | -98.8848 | -103.4993
|  |  | ST |  |  | 98.4527 | 98.4522 | 98.4516 | 84.4578 | 82.0097 | 78.7697 | 75.0363 | 70.2965 | 67.1363 | 63.8099 | 60.3522 | 50.0757 | 42.7978 | 38.9893 | 95.7615 | 84.075 | 83.954 | 81.361 | 78.4673 | 74.7277 | 70.3979 | 64.867 | 61.2256 | 57.3334 | 53.364 | 41.4648 | 33.0541 | 28.7422 | 96.0336 | 83.5494 | 83.4286 | 80.8433 | 77.9581 | 74.1725 | 69.8024 | 64.241 | 60.551 | 56.6439 | 52.6122 | 40.5905 | 32.0806 | 27.6607
|  |  | FS |  |  | 98.4528 | 98.4525 | 98.4522 | 98.4462 | 98.44 | 85.4231 | 84.5367 | 83.3835 | 81.9625 | 80.2994 | 76.6592 | 71.626 | 67.8246 | 65.2374 | 95.8172 | 95.3163 | 84.3792 | 83.9306 | 83.2564 | 82.5031 | 81.4945 | 80.1725 | 78.5444 | 76.6279 | 72.3707 | 66.4996 | 62.0474 | 59.0357 | 96.0479 | 95.9092 | 83.8527 | 83.4053 | 82.733 | 81.9818 | 80.9516 | 79.6072 | 77.9509 | 76.0078 | 71.7315 | 65.8257 | 61.358 | 58.3244
IVER 132KV | SLOUGH | SLOUGH | MINIMUM HEADROOM | SU 95574 81752 | YES | 90.144 | 28.3642 | 28.3642 | 28.0465 | 27.5505 | 26.8666 | 26.1972 | 25.5033 | 24.1002 | 22.6385 | 19.7464 | 14.2352 | 17.0875 | 13.8908 | 90.6488 | 28.1066 | 28.0449 | 27.9411 | 27.788 | 27.1426 | 26.1054 | 24.847 | 23.515 | 22.1701 | 19.5534 | 13.6417 | 11.7235 | 12.9131 | 91.8967 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 26.818 | 25.4411 | 24.0511 | 21.4325 | 15.3976 | 13.1703 | 14.8136
|  |  | CT |  |  | 90.144 | 28.3642 | 28.3642 | 28.0465 | 27.5505 | 26.8666 | 26.1972 | 25.5033 | 24.1002 | 22.6385 | 19.7464 | 14.2352 | 67.9998 | 63.4652 | 90.6494 | 28.112 | 28.0566 | 27.9411 | 27.788 | 27.1426 | 26.1054 | 24.847 | 23.515 | 22.1701 | 20.2202 | 16.1115 | 11.7235 | 66.6155 | 91.9045 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 26.818 | 25.4411 | 24.0511 | 22.0239 | 17.7353 | 13.1703 | 67.9215
|  |  | LW |  |  | 90.144 | 28.3642 | 28.3642 | 28.0465 | 27.5505 | 26.8666 | 26.1972 | 25.5033 | 24.1002 | 22.6385 | 19.7464 | 14.2352 | 67.9998 | 63.4652 | 90.6488 | 28.1066 | 28.0449 | 27.9419 | 27.8174 | 27.3647 | 26.5921 | 25.8046 | 24.2836 | 22.6948 | 19.5534 | 13.6417 | 66.9584 | 62.03 | 91.8967 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.4898 | 26.2544 | 24.6348 | 21.4325 | 15.3976 | 68.6333 | 63.6372
|  |  | ST |  |  | 90.144 | 90.144 | 28.3642 | 28.3642 | 28.1193 | 27.6671 | 26.8796 | 25.9272 | 25.0098 | 24.0452 | 22.7961 | 20.2485 | 17.0875 | 13.8908 | 90.66 | 90.6489 | 28.1228 | 28.0473 | 27.9608 | 27.8537 | 27.3797 | 26.2805 | 25.2379 | 24.141 | 22.7321 | 19.9061 | 16.4428 | 12.9131 | 92.0327 | 91.8973 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.2429 | 26.1286 | 24.6987 | 21.8362 | 18.3366 | 14.8136
|  |  | FS |  |  | 90.144 | 90.144 | 28.3642 | 28.3642 | 28.3642 | 28.3642 | 28.3642 | 28.3411 | 28.1697 | 27.9776 | 27.4034 | 26.2004 | 25.1418 | 24.2769 | 90.6785 | 90.6567 | 28.157 | 28.1381 | 28.1126 | 28.0866 | 28.0572 | 28.0183 | 27.9739 | 27.9241 | 27.7439 | 26.5958 | 25.374 | 24.3757 | 92.0484 | 91.9933 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.5147 | 27.3795 | 26.3637
NURSLING GSP | SOUTHAMPTON (2 X 60) | SOUTHAMPTON (2 X 60) | MINIMUM HEADROOM | SU 41425 11999 | YES | 56.9034 | 56.5195 | 56.0085 | 55.5774 | 55.2711 | 54.9326 | 54.5847 | 54.0884 | 53.6535 | 53.2274 | 52.4776 | 51.0179 | 49.6363 | 48.2738 | 56.8089 | 56.3583 | 55.7583 | 55.2522 | 54.8925 | 54.4951 | 54.0867 | 53.504 | 52.9934 | 52.4931 | 51.6129 | 49.8991 | 48.277 | 46.6773 | 56.8445 | 56.4268 | 55.8706 | 55.4013 | 55.0679 | 54.6994 | 54.3209 | 53.7807 | 53.3073 | 52.8435 | 52.0274 | 50.4386 | 48.8494 | 47.2712
|  |  | CT |  |  | 56.9034 | 56.5195 | 56.0085 | 55.5774 | 55.2711 | 54.9326 | 54.5847 | 54.0884 | 53.6535 | 53.2274 | 52.4776 | 51.0179 | 49.6363 | 48.2738 | 56.8317 | 56.4519 | 55.9407 | 55.5262 | 55.2265 | 54.8542 | 54.4198 | 53.8403 | 53.3403 | 52.8782 | 52.0593 | 50.3268 | 48.7668 | 47.2444 | 56.8657 | 56.5135 | 56.0397 | 55.6554 | 55.3776 | 55.0324 | 54.6297 | 54.0924 | 53.6289 | 53.2005 | 52.4413 | 50.8351 | 49.3326 | 47.8307
|  |  | LW |  |  | 56.9034 | 56.5195 | 56.0085 | 55.5774 | 55.2711 | 54.9326 | 54.5847 | 54.0884 | 53.6535 | 53.2274 | 52.4776 | 51.0179 | 49.6363 | 48.2738 | 56.8089 | 56.3583 | 55.7583 | 55.2522 | 54.8925 | 54.4951 | 54.0867 | 53.504 | 52.9934 | 52.4931 | 51.6129 | 49.8991 | 48.277 | 46.6773 | 56.8445 | 56.4268 | 55.8706 | 55.4013 | 55.0679 | 54.6994 | 54.3209 | 53.7807 | 53.3073 | 52.8435 | 52.0274 | 50.4386 | 48.8494 | 47.2712
|  |  | ST |  |  | 57.6832 | 56.7948 | 56.5417 | 56.3107 | 56.1175 | 55.8887 | 55.6256 | 55.2809 | 54.9757 | 54.6906 | 54.1813 | 53.2109 | 52.3832 | 51.5742 | 59.7778 | 56.6815 | 56.3843 | 56.1131 | 55.8862 | 55.6176 | 55.3088 | 54.904 | 54.5457 | 54.211 | 53.613 | 52.4738 | 51.502 | 50.5522 | 58.7425 | 56.7264 | 56.4509 | 56.1994 | 55.9891 | 55.7401 | 55.4538 | 55.0786 | 54.7464 | 54.4361 | 53.8817 | 52.8256 | 51.9246 | 51.0441
|  |  | FS |  |  | 57.6832 | 57.6832 | 56.9533 | 56.8518 | 56.7771 | 56.6829 | 56.5887 | 56.4506 | 56.3288 | 56.2078 | 55.9914 | 55.5916 | 55.2558 | 54.944 | 59.868 | 56.9911 | 56.8676 | 56.7483 | 56.6606 | 56.5501 | 56.4395 | 56.2773 | 56.1343 | 55.9923 | 55.7382 | 55.2688 | 54.8746 | 54.5086 | 58.8326 | 58.699 | 56.8989 | 56.7884 | 56.707 | 56.6046 | 56.5021 | 56.3517 | 56.2191 | 56.0874 | 55.8519 | 55.4167 | 55.0513 | 54.7119
NURSLING GSP | SOUTHAMPTON (2 X 90) | SOUTHAMPTON (2 X 90) | MINIMUM HEADROOM | SU 41425 11999 | YES | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 55.737 | 54.9027 | 54.0356 | 52.4978 | 48.2059 | 42.4818 | 36.4502 | 80.3389 | 80.0118 | 79.2911 | 78.6894 | 77.8391 | 77.1238 | 76.4222 | 45.2172 | 44.3215 | 43.3892 | 41.745 | 37.215 | 31.2634 | 25.008 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 54.3323 | 53.4238 | 52.4777 | 50.8112 | 46.2313 | 40.1755 | 33.8168
|  |  | CT |  |  | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 83.9792 | 81.5257 | 76.8394 | 65.9503 | 55.2992 | 46.4385 | 80.3592 | 80.0749 | 79.4388 | 78.9172 | 78.1682 | 77.5302 | 76.8901 | 76.2098 | 74.8249 | 73.3905 | 70.83 | 64.3918 | 57.9628 | 51.5777 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 85.2945 | 83.8928 | 82.4405 | 79.8513 | 73.2601 | 66.6717 | 60.1296
|  |  | LW |  |  | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 83.9792 | 81.5257 | 76.8394 | 65.9503 | 55.2992 | 46.4385 | 80.3389 | 80.0118 | 79.2911 | 78.6894 | 77.8391 | 77.1238 | 76.4222 | 75.6995 | 73.1731 | 70.633 | 65.8006 | 54.5403 | 43.5203 | 34.2957 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 84.7724 | 82.2281 | 79.6698 | 74.7955 | 63.364 | 52.1738 | 42.7813
|  |  | ST |  |  | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 55.737 | 54.9027 | 54.0356 | 52.4978 | 48.2059 | 42.4818 | 36.4502 | 80.5461 | 80.2783 | 79.9331 | 79.5895 | 79.0319 | 78.5394 | 78.0478 | 45.2172 | 44.3215 | 43.3892 | 41.745 | 37.215 | 31.2634 | 25.008 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 54.3323 | 53.4238 | 52.4777 | 50.8112 | 46.2313 | 40.1755 | 33.8168
|  |  | FS |  |  | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 96.9715 | 98.3411 | 98.3411 | 98.3411 | 98.3411 | 98.3411 | 98.3411 | 98.3411 | 80.6194 | 80.4572 | 80.3556 | 80.2367 | 80.0366 | 79.848 | 79.6656 | 80.8123 | 80.5835 | 80.3522 | 79.9665 | 79.1019 | 78.2895 | 77.5026 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 96.2426 | 97.6121 | 97.6121 | 97.6121 | 97.6121 | 97.6121 | 97.6121 | 97.6121
EALING GSP | SOUTHFIELD ROAD | SOUTHFIELD ROAD | MINIMUM HEADROOM | TQ 20533 79746 | YES | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 58.5511 | 58.5322 | 58.4872 | 58.4385 | 58.3904 | 58.3428 | 58.2948 | 58.2467 | 58.1931 | 58.1525 | 58.0868 | 58.0616 | 55.1699 | 54.9406 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 55.1558
|  |  | CT |  |  | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 58.5512 | 58.5325 | 58.488 | 58.4398 | 58.3921 | 58.345 | 58.2978 | 58.2508 | 58.1988 | 58.1571 | 58.0935 | 58.0626 | 55.17 | 54.9406 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 55.1558
|  |  | LW |  |  | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 58.5511 | 58.5322 | 58.4872 | 58.4385 | 58.3904 | 58.3428 | 58.2948 | 58.2467 | 58.1931 | 58.1525 | 58.0868 | 58.0616 | 55.1699 | 54.9503 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 55.1641
|  |  | ST |  |  | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 58.5575 | 58.5475 | 58.5257 | 58.4927 | 58.4531 | 58.4405 | 58.4278 | 58.415 | 58.4002 | 58.3855 | 58.3552 | 58.2771 | 58.2011 | 58.1445 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351
|  |  | FS |  |  | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 62.7779 | 58.5629 | 58.5618 | 58.5605 | 58.5527 | 58.5435 | 58.5389 | 58.5343 | 58.5284 | 58.5221 | 58.5158 | 58.5032 | 58.4709 | 58.4394 | 58.4087 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351 | 58.4351
LALEHAM | STAINES | STAINES | MINIMUM HEADROOM | TQ 04585 72135 | NO | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
|  |  | CT |  |  | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
|  |  | LW |  |  | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
|  |  | ST |  |  | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
|  |  | FS |  |  | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
MINETY GSP | STRATTON (2 X 60) | STRATTON (2 X 60) | MINIMUM HEADROOM | SU 17028 88748 | YES | 52.6342 | -3.0679 | -3.7602 | -6.3015 | -8.8332 | -11.6368 | -16.374 | -22.5506 | -27.3697 | -32.6265 | -38.8949 | -77.9489 | -107.1517 | -113.2106 | 40.1447 | -25.5528 | -26.4261 | -29.6371 | -33.3662 | -38.4237 | -44.3771 | -52.0555 | -58.3685 | -64.8444 | -73.5461 | -112.8336 | -146.8953 | -153.6755 | 38.9922 | -26.8689 | -27.7418 | -30.9483 | -34.6826 | -39.7356 | -45.6832 | -53.3529 | -59.661 | -66.1323 | -75.6103 | -114.6824 | -148.7373 | -155.5641
|  |  | CT |  |  | 52.6342 | -3.0679 | -3.7602 | -6.3015 | -8.8332 | -11.5175 | -14.2781 | -17.0876 | -21.3704 | -25.9555 | -36.9591 | -77.9489 | -107.1517 | -113.2106 | 40.1447 | 24.376 | -21.776 | -29.1661 | -33.3662 | -38.4237 | -44.3771 | -52.0555 | -58.3685 | -64.8444 | -73.5461 | -99.5539 | -119.9935 | -128.318 | 38.9922 | 23.2113 | -23.1054 | -30.4858 | -34.6826 | -39.7356 | -45.6832 | -53.3529 | -59.661 | -66.1323 | -75.6103 | -101.6211 | -122.0864 | -130.4715
|  |  | LW |  |  | 52.6342 | -3.0679 | -3.7602 | -6.3015 | -8.8332 | -11.5175 | -14.2781 | -17.0876 | -21.3704 | -25.9555 | -36.9591 | -77.9489 | -107.1517 | -113.2106 | 40.1468 | -25.5528 | -26.4261 | -29.6371 | -32.8354 | -36.1107 | -39.3702 | -42.6866 | -47.6571 | -52.9842 | -64.8214 | -112.8336 | -146.8953 | -153.6755 | 38.9973 | -26.8689 | -27.7418 | -30.9483 | -34.1425 | -37.4141 | -40.6702 | -43.9838 | -48.9496 | -54.2719 | -66.7191 | -114.6824 | -148.7373 | -155.5641
|  |  | ST |  |  | 110.4686 | 37.2771 | 36.9442 | -4.3927 | -7.6887 | -11.6368 | -16.374 | -22.5506 | -27.3697 | -32.6265 | -38.8949 | -59.3316 | -75.3311 | -81.1329 | 100.3408 | 24.7661 | 24.354 | -27.6749 | -31.8423 | -36.5691 | -42.1687 | -49.4701 | -55.1497 | -61.3466 | -68.1074 | -92.139 | -110.8426 | -117.4682 | 98.2536 | 23.6151 | 23.1953 | -28.9832 | -33.1433 | -37.862 | -43.4519 | -50.7405 | -56.4104 | -62.5968 | -69.7349 | -93.7313 | -112.4143 | -119.0448
|  |  | FS |  |  | 110.4689 | 110.4682 | 95.2043 | 0.87332 | -2.2083 | -2.9934 | -3.9811 | -5.3013 | -6.9088 | -8.8413 | -14.9527 | -21.1124 | -25.9604 | -29.2656 | 100.7395 | 99.8227 | 47.1324 | -21.0162 | -24.9127 | -25.905 | -27.1533 | -28.8222 | -30.8543 | -33.2628 | -39.8734 | -47.1502 | -52.8738 | -56.7724 | 98.254 | 98.2533 | 45.985 | -22.3365 | -26.2261 | -27.2169 | -28.4632 | -30.1294 | -32.1581 | -34.5625 | -41.5492 | -48.8161 | -54.5342 | -58.4313
MINETY GSP | STRATTON (2 X 90) | STRATTON (2 X 90) | MINIMUM HEADROOM | SU 17028 88748 | YES | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 93.0209 | 93.0104 | 92.9868 | 92.9613 | 92.9358 | 92.9103 | 92.8849 | 92.8594 | 92.8323 | 92.8054 | 92.7494 | 92.4219 | 92.2925 | 92.2925 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885
|  |  | CT |  |  | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 93.0219 | 93.0126 | 92.9919 | 92.9694 | 92.9467 | 92.9239 | 92.9013 | 92.8786 | 92.8543 | 92.8301 | 92.7827 | 92.5033 | 92.2925 | 92.2925 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885
|  |  | LW |  |  | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 93.0209 | 93.0104 | 92.9868 | 92.9613 | 92.9358 | 92.9103 | 92.8849 | 92.8594 | 92.8323 | 92.8054 | 92.7494 | 92.4219 | 92.2925 | 92.2925 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885
|  |  | ST |  |  | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 93.0282 | 93.0234 | 93.0138 | 92.9996 | 92.9824 | 92.9549 | 92.9278 | 92.9008 | 92.8718 | 92.8432 | 92.7875 | 92.5751 | 92.3368 | 92.2925 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885
|  |  | FS |  |  | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 92.1461 | 93.0335 | 93.0321 | 93.0309 | 93.0264 | 93.0212 | 93.0138 | 93.0065 | 92.9972 | 92.988 | 92.979 | 92.9615 | 92.8957 | 92.8107 | 92.7168 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885 | 93.1885
MINETY GSP | SWINDON BSP | SWINDON BSP | MINIMUM HEADROOM | SU 12447 87062 | YES | 91.1493 | 91.0364 | 90.8145 | 90.3299 | 90.0011 | 84.5878 | 82.8776 | 80.7682 | 79.1032 | 77.3348 | 74.4813 | 63.6746 | 29.9662 | 20.7924 | 87.7351 | 87.586 | 85.0086 | 83.3954 | 81.8126 | 79.9678 | 77.8571 | 75.2634 | 72.9874 | 70.6512 | 67.5226 | 57.3483 | 18.3964 | 8.321 | 89.0712 | 89.0026 | 88.8679 | 85.4072 | 83.8284 | 81.9882 | 79.8828 | 77.2959 | 75.0239 | 72.6917 | 69.5658 | 59.4026 | 20.5409 | 10.4654
|  |  | CT |  |  | 91.1493 | 91.0364 | 90.8145 | 90.3299 | 90.0011 | 84.7918 | 83.6993 | 84.1854 | 81.7704 | 79.2658 | 74.4813 | 63.6746 | 29.9662 | 20.7924 | 88.9998 | 87.5948 | 85.046 | 83.3954 | 81.8126 | 79.9678 | 77.8571 | 75.2634 | 72.9874 | 70.6512 | 67.5226 | 59.7063 | 37.6965 | 29.2342 | 90.3342 | 89.0051 | 88.8729 | 85.4072 | 83.8284 | 81.9882 | 79.8828 | 77.2959 | 75.0239 | 72.6917 | 69.5658 | 61.7523 | 39.7812 | 31.3113
|  |  | LW |  |  | 91.1493 | 91.0364 | 90.8145 | 90.3299 | 90.0011 | 84.7918 | 83.6993 | 84.1854 | 81.7704 | 79.2658 | 74.4813 | 63.6746 | 29.9662 | 20.7924 | 87.7351 | 87.586 | 85.0086 | 83.7223 | 82.4286 | 81.1032 | 79.7852 | 80.0471 | 77.3722 | 74.589 | 69.2946 | 57.3483 | 18.3964 | 8.321 | 89.0712 | 89.0026 | 88.8679 | 88.7677 | 84.4449 | 83.1231 | 81.8086 | 82.0739 | 79.4029 | 76.6237 | 71.3362 | 59.4026 | 20.5409 | 10.4654
|  |  | ST |  |  | 92.9176 | 91.1267 | 91.0197 | 90.5097 | 90.0131 | 84.5878 | 82.8776 | 80.7682 | 79.1032 | 77.3348 | 75.1109 | 71.7199 | 54.0094 | 47.4893 | 89.6663 | 87.705 | 87.5637 | 84.1951 | 82.6638 | 80.8518 | 78.7852 | 76.2361 | 74.2707 | 72.18 | 69.586 | 65.4894 | 44.9029 | 37.7247 | 90.6406 | 89.0576 | 88.9927 | 88.7741 | 84.6801 | 82.8735 | 80.813 | 78.2715 | 76.3112 | 74.226 | 71.6381 | 67.5522 | 47.0175 | 39.8484
|  |  | FS |  |  | 92.9471 | 92.6659 | 92.4469 | 91.0869 | 90.9543 | 90.799 | 90.6155 | 90.3739 | 90.0844 | 90.0144 | 84.0466 | 81.4369 | 80.1153 | 78.1985 | 89.7054 | 89.3335 | 89.0436 | 87.653 | 85.3879 | 84.9727 | 84.482 | 83.8336 | 83.0573 | 82.1616 | 80.1963 | 77.043 | 75.2356 | 72.9201 | 90.6586 | 90.4881 | 90.3553 | 89.0328 | 88.9518 | 88.8569 | 88.773 | 88.7717 | 85.0722 | 84.1792 | 82.2198 | 79.0755 | 77.2757 | 74.9662
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM BSP | MINIMUM HEADROOM | SU 52824 66435 | YES | 249.9051 | 239.3788 | 239.3788 | 239.3586 | 239.3375 | 239.3165 | 239.2949 | 239.2703 | 238.5524 | 237.8358 | 236.4065 | 233.0835 | 135.3205 | 125.0208 | 214.1069 | 203.3506 | 203.2407 | 203.031 | 202.8161 | 202.5998 | 202.3237 | 201.9852 | 142.4264 | 137.0601 | 129.4198 | 116.1934 | 101.9587 | 90.3485 | 222.382 | 211.8557 | 211.8557 | 211.8354 | 211.8144 | 211.7934 | 211.7717 | 211.7472 | 211.0293 | 140.322 | 132.7859 | 119.4691 | 105.1026 | 93.3834
|  |  | CT |  |  | 249.9051 | 239.3788 | 239.3788 | 239.3586 | 239.3375 | 239.3165 | 239.2949 | 239.2703 | 238.5524 | 237.8358 | 236.4065 | 233.0835 | 135.3205 | 125.0208 | 214.1096 | 214.0268 | 213.8911 | 203.1226 | 202.882 | 202.6155 | 202.3237 | 201.9852 | 142.4264 | 137.0601 | 129.4198 | 117.7788 | 105.6107 | 93.786 | 222.382 | 222.382 | 222.382 | 211.8375 | 211.8166 | 211.795 | 211.7721 | 211.7503 | 211.4675 | 140.322 | 132.7859 | 121.0307 | 108.7343 | 96.7853
|  |  | LW |  |  | 249.9051 | 239.3788 | 239.3788 | 239.3586 | 239.3375 | 239.3165 | 239.2949 | 239.2703 | 238.5524 | 237.8358 | 236.4065 | 233.0835 | 135.3205 | 125.0208 | 214.1069 | 203.3506 | 203.2407 | 203.031 | 202.8161 | 202.5998 | 202.3861 | 202.1735 | 201.2365 | 141.2811 | 130.965 | 116.1934 | 101.9587 | 90.3485 | 222.382 | 211.8557 | 211.8557 | 211.8354 | 211.8144 | 211.7934 | 211.7717 | 211.7472 | 211.0293 | 210.3127 | 134.2827 | 119.4691 | 105.1026 | 93.3834
|  |  | ST |  |  | 249.9051 | 249.9051 | 249.9051 | 239.3679 | 239.3563 | 239.3447 | 239.3332 | 239.321 | 239.1757 | 239.0348 | 238.7547 | 237.7763 | 236.2214 | 234.5431 | 214.1827 | 214.0929 | 213.9973 | 203.2601 | 203.038 | 202.8426 | 202.6227 | 202.3531 | 202.0206 | 201.6783 | 141.2976 | 133.637 | 124.9763 | 116.4922 | 222.382 | 222.382 | 222.382 | 211.8448 | 211.8332 | 211.8215 | 211.81 | 211.7979 | 211.6526 | 211.5117 | 211.2316 | 136.9355 | 128.3189 | 119.7541
|  |  | FS |  |  | 249.9051 | 249.9051 | 249.9051 | 249.9021 | 249.899 | 239.3695 | 239.3663 | 239.3643 | 239.3614 | 239.3608 | 239.3596 | 239.3477 | 239.343 | 239.3382 | 214.2111 | 214.1749 | 214.1676 | 214.1016 | 214.0127 | 203.4128 | 203.3587 | 203.2899 | 203.2086 | 203.118 | 202.9117 | 202.5907 | 202.3333 | 202.138 | 222.382 | 222.382 | 222.382 | 222.3789 | 222.3758 | 211.8464 | 211.8432 | 211.8411 | 211.8382 | 211.8376 | 211.8365 | 211.8246 | 211.8199 | 211.8151
MINETY GSP | TOOTHILL BSP | TOOTHILL BSP | MINIMUM HEADROOM | SU 13191 83945 | YES | 94.6926 | 67.6792 | 67.078 | 66.0494 | 64.9332 | 149.1743 | 147.8441 | 147.1161 | 145.899 | 144.5854 | 142.6229 | 141.4488 | 129.8447 | 126.7478 | 92.1073 | 65.5228 | 64.777 | 63.4841 | 62.0596 | 145.8294 | 143.8932 | 141.5735 | 139.8177 | 137.9864 | 135.0746 | 128.1026 | 119.3382 | 115.5141 | 92.3057 | 64.504 | 63.7839 | 62.5123 | 61.0847 | 144.8598 | 142.9295 | 140.6168 | 138.8664 | 137.0407 | 134.1377 | 127.1869 | 118.4492 | 114.6368
|  |  | CT |  |  | 94.6926 | 67.6792 | 67.078 | 66.0494 | 64.9332 | 149.1743 | 147.8441 | 154.9897 | 153.653 | 152.2825 | 149.5103 | 141.4488 | 129.8447 | 126.7478 | 92.1082 | 65.5245 | 64.9435 | 63.5288 | 62.0596 | 145.8294 | 143.8932 | 141.5735 | 139.8177 | 137.9864 | 135.0746 | 128.1026 | 119.3382 | 115.5141 | 92.3057 | 64.5774 | 63.9467 | 62.5572 | 61.0847 | 144.8598 | 142.9295 | 140.6168 | 138.8664 | 137.0407 | 134.1377 | 127.1869 | 118.4492 | 114.6368
|  |  | LW |  |  | 94.6926 | 67.6792 | 67.078 | 66.0494 | 64.9332 | 149.1743 | 147.8441 | 154.9897 | 153.653 | 152.2825 | 149.5103 | 141.4488 | 129.8447 | 126.7478 | 92.1073 | 65.5228 | 64.777 | 63.4841 | 62.0783 | 146.0576 | 144.483 | 151.3773 | 149.7949 | 148.1726 | 144.8911 | 135.3485 | 121.6123 | 117.9465 | 92.3057 | 64.504 | 63.7839 | 62.5123 | 61.1034 | 145.0873 | 143.5175 | 150.4167 | 148.8392 | 147.2217 | 143.9502 | 134.4367 | 120.7424 | 117.0877
|  |  | ST |  |  | 94.6926 | 67.9483 | 67.6747 | 66.8304 | 65.8536 | 150.1966 | 148.8111 | 147.1161 | 145.899 | 144.5854 | 142.6229 | 146.4222 | 140.1191 | 137.9876 | 92.174 | 65.5245 | 65.5173 | 64.4658 | 63.2381 | 147.2788 | 145.6277 | 143.6212 | 142.1805 | 140.6256 | 138.3025 | 141.2356 | 133.7745 | 131.2513 | 92.3057 | 64.8188 | 64.4988 | 63.4795 | 62.2653 | 146.3048 | 144.6587 | 142.6583 | 141.222 | 139.6718 | 137.3558 | 140.3059 | 132.8675 | 130.352
|  |  | FS |  |  | 94.6926 | 68.1006 | 68.0013 | 67.765 | 67.4601 | 152.6247 | 152.2444 | 151.7783 | 151.2669 | 150.6934 | 149.37 | 147.3924 | 145.8765 | 144.7084 | 92.1778 | 65.5245 | 65.5245 | 65.5245 | 65.2547 | 150.3357 | 149.8578 | 149.2719 | 148.6291 | 147.9078 | 146.2892 | 143.9483 | 142.1539 | 140.7711 | 92.3057 | 64.9971 | 64.8809 | 64.6044 | 64.2477 | 149.3413 | 148.8739 | 148.3009 | 147.6557 | 146.9318 | 145.3182 | 142.9844 | 141.1954 | 139.8169
IVER 132KV | UPTON BSP | UPTON BSP | MINIMUM HEADROOM | TQ 00838 79445 | YES | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 73.4745 | 73.4664 | 73.4474 | 73.4267 | 73.4059 | 73.3853 | 73.3647 | 73.3404 | 73.3144 | 73.3111 | 73.3111 | 73.3111 | 73.3111 | 73.3111 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968
|  |  | CT |  |  | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 73.4756 | 73.4691 | 73.4538 | 73.4372 | 73.4205 | 73.4038 | 73.3873 | 73.3677 | 73.3466 | 73.3291 | 73.3111 | 73.3111 | 73.3111 | 73.3111 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968
|  |  | LW |  |  | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 73.4745 | 73.4664 | 73.4474 | 73.4267 | 73.4059 | 73.3853 | 73.3647 | 73.3404 | 73.3144 | 73.3111 | 73.3111 | 73.3111 | 73.3111 | 73.3111 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968
|  |  | ST |  |  | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 73.4925 | 73.4726 | 73.462 | 73.4462 | 73.427 | 73.4092 | 73.3916 | 73.372 | 73.3508 | 73.3323 | 73.3111 | 73.3111 | 73.3111 | 73.3111 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968
|  |  | FS |  |  | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 78.9947 | 73.4956 | 73.4799 | 73.4792 | 73.4756 | 73.4714 | 73.4655 | 73.4597 | 73.4513 | 73.443 | 73.4358 | 73.4216 | 73.3839 | 73.3454 | 73.3111 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968 | 74.4968
IVER 66KV | UXBRIDGE | UXBRIDGE | MINIMUM HEADROOM | TQ 04984 83484 | NO | 64.9204 | 64.9137 | 64.8986 | 64.8733 | 64.8694 | 64.8694 | 64.8694 | 64.8694 | 64.1854 | 63.5014 | 62.1335 | 52.7662 | 47.7439 | 43.5647 | 60.2614 | 60.2158 | 60.111 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 59.3599 | 58.6759 | 57.3079 | 47.1551 | 41.768 | 37.2526 | 63.2361 | 63.1855 | 63.102 | 63.0053 | 62.9046 | 62.8072 | 62.7318 | 62.6431 | 61.9864 | 61.2295 | 59.8589 | 49.6772 | 44.2893 | 39.7731
|  |  | CT |  |  | 64.9204 | 64.9137 | 64.8986 | 64.8733 | 64.8694 | 64.8694 | 64.8694 | 64.8694 | 64.1854 | 63.5014 | 62.1335 | 52.7662 | 47.7439 | 43.5647 | 60.2614 | 60.2158 | 60.111 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 59.7874 | 59.5309 | 59.0179 | 57.7354 | 46.7852 | 43.3492 | 63.2361 | 63.1855 | 63.102 | 63.0053 | 62.9046 | 62.8072 | 62.7318 | 62.6431 | 62.3383 | 62.0818 | 61.5688 | 60.2864 | 49.3065 | 45.8697
|  |  | LW |  |  | 64.9204 | 64.9137 | 64.8986 | 64.8733 | 64.8694 | 64.8694 | 64.8694 | 64.8694 | 64.1854 | 63.5014 | 62.1335 | 52.7662 | 47.7439 | 43.5647 | 60.2622 | 60.2219 | 60.1303 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 59.3599 | 58.6759 | 57.3079 | 47.1551 | 41.768 | 37.2526 | 63.2371 | 63.1923 | 63.1113 | 63.0371 | 62.9549 | 62.8686 | 62.7985 | 62.7407 | 61.9864 | 61.2295 | 59.8589 | 49.6772 | 44.2893 | 39.7731
|  |  | ST |  |  | 64.9321 | 64.9227 | 64.9163 | 64.894 | 64.8694 | 64.8694 | 64.8694 | 64.8694 | 64.7376 | 64.6059 | 64.3423 | 63.42 | 61.9047 | 52.1732 | 60.3331 | 60.2765 | 60.2378 | 60.1024 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 59.9121 | 59.7803 | 59.5168 | 58.5944 | 49.3431 | 46.2396 | 63.3159 | 63.2529 | 63.2098 | 63.0978 | 63.0183 | 62.9112 | 62.8095 | 62.7231 | 62.5126 | 62.3313 | 62.0677 | 61.1454 | 59.6301 | 48.7609
|  |  | FS |  |  | 64.9362 | 64.9291 | 64.9283 | 64.9236 | 64.917 | 64.9073 | 64.8965 | 64.8824 | 64.8694 | 64.8694 | 64.8694 | 64.8694 | 64.8694 | 64.8694 | 60.358 | 60.3154 | 60.3105 | 60.2816 | 60.2416 | 60.183 | 60.1178 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 60.0439 | 63.3435 | 63.2961 | 63.2907 | 63.2586 | 63.2141 | 63.149 | 63.1052 | 63.0639 | 63.0183 | 62.9688 | 62.861 | 62.7219 | 62.607 | 62.5948
NURSLING GSP | VELMORE BSP | VELMORE BSP | MINIMUM HEADROOM | SU 42855 19215 | YES | 81.0281 | 80.978 | 166.4143 | 165.7988 | 164.7833 | 163.968 | 163.1191 | 162.1509 | 161.2281 | 160.2895 | 158.8623 | 155.8655 | 151.575 | 150.5361 | 80.2612 | 80.2312 | 164.9274 | 163.5529 | 162.0894 | 160.5669 | 159.0093 | 157.3859 | 155.7862 | 154.2056 | 151.5702 | 146.36 | 139.4353 | 144.2637 | 80.2073 | 80.1718 | 165.1145 | 163.6613 | 162.2023 | 160.6844 | 159.1316 | 157.5131 | 155.9182 | 154.3424 | 151.7151 | 146.5208 | 139.6171 | 144.4693
|  |  | CT |  |  | 96.3861 | 96.3861 | 181.8861 | 181.8861 | 181.8861 | 181.8861 | 181.8861 | 181.8861 | 181.8861 | 169.9196 | 167.3568 | 162.5554 | 155.1295 | 150.5361 | 80.2612 | 80.2312 | 164.9274 | 163.5529 | 162.0894 | 160.5669 | 159.0093 | 157.3859 | 155.7862 | 154.2056 | 151.5702 | 146.36 | 139.4353 | 146.7247 | 80.2073 | 80.1718 | 165.1145 | 163.6613 | 162.2023 | 160.6844 | 159.1316 | 157.5131 | 155.9182 | 154.3424 | 151.7151 | 146.5208 | 139.6171 | 146.9228
|  |  | LW |  |  | 96.3861 | 96.3861 | 181.8861 | 181.8861 | 181.8861 | 181.8861 | 181.8861 | 181.8861 | 181.8861 | 169.9196 | 167.3568 | 162.5554 | 155.1295 | 150.5361 | 94.9943 | 94.881 | 180.3769 | 180.3769 | 180.3769 | 180.3769 | 180.3769 | 170.1807 | 168.6494 | 167.1268 | 164.0932 | 158.4227 | 149.6747 | 144.2637 | 95.0317 | 95.0317 | 180.5317 | 180.5317 | 180.5317 | 180.5317 | 180.5317 | 170.3074 | 168.7807 | 167.2628 | 164.2384 | 158.5851 | 149.8639 | 144.4693
|  |  | ST |  |  | 81.0281 | 80.978 | 166.4143 | 165.7988 | 164.7833 | 163.968 | 163.1191 | 162.1509 | 161.2281 | 160.2895 | 158.8623 | 155.8655 | 151.575 | 161.2582 | 80.274 | 80.2507 | 165.7212 | 164.7405 | 163.5171 | 162.4848 | 161.41 | 160.2516 | 159.1592 | 158.0482 | 156.3587 | 152.8114 | 147.7361 | 156.8945 | 80.2224 | 80.1949 | 165.6599 | 164.9075 | 163.6256 | 162.5965 | 161.5249 | 160.37 | 159.281 | 158.1734 | 156.489 | 152.9525 | 147.8927 | 157.0616
|  |  | FS |  |  | 81.0463 | 81.0315 | 166.5184 | 166.4875 | 166.4514 | 166.418 | 166.3791 | 166.1445 | 165.8219 | 165.4842 | 164.7719 | 163.3802 | 162.0357 | 160.7843 | 80.2824 | 80.2755 | 165.7694 | 165.7551 | 165.7384 | 165.7229 | 165.4768 | 165.1345 | 164.7668 | 164.3818 | 163.5027 | 161.7406 | 160.1152 | 158.6339 | 80.2324 | 80.2243 | 165.7171 | 165.7001 | 165.6802 | 165.6619 | 165.6438 | 165.3439 | 164.9367 | 164.5103 | 163.6112 | 161.8546 | 160.2341 | 158.7572
NORTH HYDE GSP | VICARAGE FARM ROAD | VICARAGE FARM ROAD | MINIMUM HEADROOM | TQ 12358 76435 | NO | 36.844 | 36.7498 | 36.5316 | 36.3418 | 36.1457 | 35.9341 | 35.7071 | 35.5154 | 35.3094 | 35.098 | 34.651 | 33.1938 | 31.6814 | 30.1709 | 34.5598 | 34.4485 | 34.1904 | 33.966 | 33.7342 | 33.4852 | 33.2181 | 32.9925 | 32.7502 | 32.5014 | 31.9755 | 30.2608 | 28.4813 | 26.7039 | 34.4955 | 34.3844 | 34.1268 | 33.9029 | 33.6715 | 33.423 | 33.1564 | 32.9312 | 32.6894 | 32.4411 | 31.9161 | 30.2047 | 28.4286 | 26.6545
|  |  | CT |  |  | 36.844 | 36.7498 | 36.5316 | 36.3418 | 36.1457 | 35.9341 | 35.7071 | 35.5154 | 35.3094 | 35.098 | 34.651 | 33.1938 | 31.6814 | 30.1709 | 34.5643 | 34.466 | 34.2326 | 34.0338 | 33.8268 | 33.5982 | 33.347 | 33.1102 | 32.86 | 32.5953 | 32.0573 | 30.7251 | 29.2008 | 27.6356 | 34.5 | 34.4019 | 34.1689 | 33.9705 | 33.764 | 33.5358 | 33.2851 | 33.0487 | 32.799 | 32.5348 | 31.9977 | 30.6681 | 29.1467 | 27.5844
|  |  | LW |  |  | 36.844 | 36.7498 | 36.5316 | 36.3418 | 36.1457 | 35.9341 | 35.7071 | 35.5154 | 35.3094 | 35.098 | 34.651 | 33.1938 | 31.6814 | 30.1709 | 34.5598 | 34.4485 | 34.1904 | 33.966 | 33.7342 | 33.4852 | 33.2181 | 32.9925 | 32.7502 | 32.5014 | 31.9755 | 30.2608 | 28.4813 | 26.7039 | 34.4955 | 34.3844 | 34.1268 | 33.9029 | 33.6715 | 33.423 | 33.1564 | 32.9312 | 32.6894 | 32.4411 | 31.9161 | 30.2047 | 28.4286 | 26.6545
|  |  | ST |  |  | 37.5641 | 36.8336 | 36.7303 | 36.6382 | 36.5331 | 36.3225 | 36.1006 | 35.8875 | 35.6583 | 35.4201 | 34.938 | 34.1018 | 33.1883 | 32.2626 | 35.3726 | 34.5475 | 34.4253 | 34.3164 | 34.1922 | 33.9432 | 33.6811 | 33.4304 | 33.1607 | 32.8805 | 32.3131 | 31.3292 | 30.2544 | 29.1651 | 35.3523 | 34.4833 | 34.3613 | 34.2526 | 34.1286 | 33.8802 | 33.6185 | 33.3683 | 33.0991 | 32.8194 | 32.2531 | 31.2711 | 30.1983 | 29.1111
|  |  | FS |  |  | 37.5726 | 36.8787 | 36.8326 | 36.7919 | 36.7493 | 36.6694 | 36.5869 | 36.5004 | 36.4115 | 36.3205 | 36.1336 | 35.8198 | 35.4796 | 35.1143 | 35.3726 | 34.6009 | 34.5464 | 34.4982 | 34.4479 | 34.3534 | 34.2559 | 34.1536 | 34.0485 | 33.9408 | 33.72 | 33.3508 | 32.9504 | 32.5206 | 35.3726 | 34.5365 | 34.4821 | 34.434 | 34.3838 | 34.2896 | 34.1922 | 34.0901 | 33.9852 | 33.8778 | 33.6573 | 33.2888 | 32.8892 | 32.4602
MANNINGTON GSP | WAREHAM | WAREHAM | MINIMUM HEADROOM | SY 91548 88451 | YES | 12.3302 | 12.2834 | 30.243 | 29.0115 | 27.5157 | 25.7095 | 23.576 | 20.7938 | 18.7802 | 16.6048 | 14.3708 | -1.9816 | -11.3849 | -16.4449 | 11.8854 | 11.8311 | 26.3971 | 24.6492 | 22.9458 | 20.8475 | 18.3591 | 15.103 | 12.5409 | 9.9247 | 7.0313 | -9.9029 | -20.1572 | -25.4918 | 10.0969 | 10.0419 | 24.6064 | 22.8512 | 21.1472 | 19.0483 | 16.5591 | 13.3019 | 10.7391 | 8.1221 | 5.228 | -11.7093 | -21.9655 | -27.3008
|  |  | CT |  |  | 12.3302 | 12.2834 | 30.243 | 29.2374 | 28.1694 | 27.0534 | 25.9444 | 24.821 | 22.4267 | 19.944 | 15.0756 | -1.9816 | -11.3849 | -16.4449 | 11.8866 | 11.8336 | 26.4031 | 24.6492 | 22.9458 | 20.8475 | 18.3591 | 15.103 | 12.5409 | 9.9247 | 7.0313 | -2.8163 | -8.8066 | -13.3693 | 10.0981 | 10.0445 | 24.6125 | 22.8512 | 21.1472 | 19.0483 | 16.5591 | 13.3019 | 10.7391 | 8.1221 | 5.228 | -4.6222 | -10.6138 | -15.1774
|  |  | LW |  |  | 12.3302 | 12.2834 | 30.243 | 29.2374 | 28.1694 | 27.0534 | 25.9444 | 24.821 | 22.4267 | 19.944 | 15.0756 | -1.9816 | -11.3849 | -16.4449 | 11.8854 | 11.8311 | 26.3971 | 25.2233 | 23.9694 | 22.6591 | 21.3571 | 20.0382 | 17.4067 | 14.6715 | 9.3149 | -9.9029 | -20.1572 | -25.4918 | 10.0969 | 10.0419 | 24.6064 | 23.4254 | 22.1711 | 20.8604 | 19.558 | 18.2387 | 15.6067 | 12.8709 | 7.5133 | -11.7093 | -21.9655 | -27.3008
|  |  | ST |  |  | 12.3478 | 12.3258 | 30.3506 | 29.0115 | 27.5157 | 25.7095 | 23.576 | 20.7938 | 18.7802 | 16.6048 | 14.3708 | 6.5805 | 1.1993 | -3.159 | 11.9058 | 11.8804 | 26.5221 | 24.958 | 23.2018 | 21.0813 | 18.5765 | 15.31 | 12.9805 | 10.4612 | 7.9075 | -0.99644 | -6.9164 | -11.6008 | 10.1175 | 10.0918 | 24.7328 | 23.1601 | 21.4034 | 19.2821 | 16.7765 | 13.5089 | 11.1788 | 8.6587 | 6.1043 | -2.8021 | -8.7233 | -13.4084
|  |  | FS |  |  | 21.5218 | 12.3533 | 30.4193 | 30.1996 | 29.8598 | 29.4976 | 29.036 | 28.4142 | 27.6478 | 26.7381 | 24.6147 | 21.763 | 19.5631 | 18.1192 | 22.8656 | 11.9122 | 26.6018 | 26.3467 | 25.9524 | 25.5287 | 24.9868 | 24.2567 | 23.3569 | 22.2889 | 19.7959 | 16.4479 | 13.8651 | 12.1699 | 21.0045 | 10.124 | 24.8135 | 24.5554 | 24.1563 | 23.731 | 23.1889 | 22.4586 | 21.5585 | 20.4901 | 17.9963 | 14.6472 | 12.0636 | 10.3678
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON | MINIMUM HEADROOM | SU 24302 59215 | YES | 67.9185 | 67.9182 | 67.9177 | 67.9087 | 67.8992 | 67.8896 | 67.8796 | 67.8681 | 58.4728 | 57.3464 | 56.197 | 50.6325 | 47.9737 | 45.9049 | 67.7473 | 67.5782 | 67.2392 | 65.904 | 65.221 | 65.2107 | 65.1998 | 57.8932 | 56.534 | 55.1664 | 53.6079 | 48.8453 | 45.8766 | 43.5748 | 65.8623 | 65.7048 | 65.4629 | 57.8195 | 56.5912 | 55.1522 | 53.4798 | 51.3637 | 49.9871 | 48.6016 | 47.0216 | 42.202 | 39.189 | 36.8492
|  |  | CT |  |  | 67.9185 | 67.9182 | 67.9177 | 67.9087 | 67.8992 | 67.8896 | 67.8796 | 67.8681 | 67.8558 | 67.8438 | 57.3507 | 50.6325 | 47.9737 | 45.9049 | 67.7479 | 67.5854 | 67.2515 | 65.904 | 65.221 | 65.2107 | 65.1998 | 57.8932 | 56.534 | 55.1664 | 53.6079 | 48.9125 | 46.2422 | 43.6761 | 65.8625 | 65.7108 | 65.4695 | 57.8195 | 56.5912 | 55.1522 | 53.4798 | 51.3637 | 49.9871 | 48.6016 | 47.0216 | 42.2605 | 39.5437 | 36.9297
|  |  | LW |  |  | 67.9185 | 67.9182 | 67.9177 | 67.9087 | 67.8992 | 67.8896 | 67.8796 | 67.8681 | 67.8558 | 67.8438 | 57.3507 | 50.6325 | 47.9737 | 45.9049 | 67.7473 | 67.5782 | 67.2392 | 66.2293 | 65.2274 | 65.2141 | 65.2045 | 65.1936 | 65.1821 | 65.1709 | 56.3731 | 48.8453 | 45.8766 | 43.5748 | 65.8623 | 65.7048 | 65.4629 | 58.1354 | 57.1655 | 56.185 | 55.2098 | 54.2215 | 53.1329 | 51.9984 | 49.8258 | 42.202 | 39.189 | 36.8492
|  |  | ST |  |  | 67.9188 | 67.9187 | 67.9185 | 67.9138 | 67.9088 | 67.9037 | 67.8986 | 67.8932 | 58.4728 | 57.3464 | 56.197 | 52.6307 | 50.9045 | 49.2861 | 67.9066 | 67.7146 | 67.5602 | 66.4364 | 65.2322 | 65.2272 | 65.2222 | 65.217 | 57.6213 | 56.3567 | 55.0667 | 51.065 | 49.1303 | 47.3174 | 66.0107 | 65.832 | 65.6882 | 58.3363 | 57.1394 | 55.8218 | 54.2772 | 52.2925 | 51.092 | 49.8118 | 48.5059 | 44.4542 | 42.4939 | 40.6562
|  |  | FS |  |  | 67.9189 | 67.9188 | 67.9187 | 67.9173 | 67.9159 | 67.9144 | 67.9129 | 67.9119 | 67.9106 | 67.9101 | 67.9093 | 67.9029 | 67.8988 | 57.6109 | 68.0344 | 67.9201 | 67.7913 | 67.5782 | 67.2878 | 66.9951 | 66.6318 | 66.1436 | 65.5487 | 65.2337 | 65.233 | 65.2272 | 57.8946 | 56.6541 | 66.1297 | 66.0233 | 65.9033 | 65.7048 | 65.4948 | 65.3001 | 65.0586 | 58.0528 | 57.4771 | 56.8061 | 55.2679 | 53.1114 | 51.3676 | 50.1113
NURSLING GSP | WINCHESTER | WINCHESTER | MINIMUM HEADROOM | SU 44965 26671 | YES | 66.115 | 65.2101 | 48.8318 | 42.6369 | -41.1263 | -47.9722 | -92.9088 | -99.3512 | -106.3087 | -113.7633 | -128.4696 | -141.3522 | -173.2907 | -179.712 | 50.638 | 49.6623 | 36.5984 | 26.2183 | -69.3577 | -77.2414 | -129.9827 | -137.497 | -145.5345 | -154.1756 | -171.0557 | -185.5361 | -222.2829 | -229.4055 | 52.0677 | 51.0921 | 38.0411 | 27.6674 | -67.7157 | -75.6887 | -128.4115 | -135.9518 | -144.0648 | -152.768 | -169.8635 | -184.7175 | -221.8793 | -229.2455
|  |  | CT |  |  | 66.115 | 65.2101 | 48.8318 | 42.6369 | -41.1263 | -47.9722 | -92.9088 | -99.3512 | -106.3087 | -113.7633 | -128.4696 | -141.3522 | -173.2907 | -179.712 | 50.638 | 49.6623 | 36.8577 | 26.2183 | 11.6513 | -0.47193 | -15.0761 | -33.7858 | -44.6634 | -55.8295 | -67.2956 | -78.4817 | -102.9605 | -113.1522 | 52.0677 | 51.0921 | 38.2887 | 27.6674 | 13.1257 | 1.023 | -13.6975 | -32.496 | -43.4611 | -54.7085 | -66.3452 | -78.1474 | -103.2958 | -113.7307
|  |  | LW |  |  | 66.115 | 65.2101 | 48.8318 | 42.6369 | -41.1263 | -47.9722 | -92.9088 | -99.3512 | -106.3087 | -113.7633 | -128.4696 | -141.3522 | -173.2907 | -179.712 | 54.9212 | 53.914 | 36.5984 | 29.2747 | -69.3577 | -77.2414 | -129.9827 | -137.497 | -145.5345 | -154.1756 | -171.0557 | -185.5361 | -222.2829 | -229.4055 | 56.352 | 55.3457 | 38.0411 | 30.7307 | -67.7157 | -75.6887 | -128.4115 | -135.9518 | -144.0648 | -152.768 | -169.8635 | -184.7175 | -221.8793 | -229.2455
|  |  | ST |  |  | 67.4776 | 66.8222 | 55.1797 | 47.5228 | 35.2497 | 25.7656 | 14.4926 | -0.30977 | -8.2356 | -16.8278 | -24.3848 | -30.6988 | -47.9678 | -54.2883 | 56.3686 | 55.629 | 43.8998 | 34.8468 | 20.336 | 9.2208 | -3.9793 | -21.3396 | -30.5823 | -40.6549 | -49.4427 | -56.6567 | -76.7487 | -83.9048 | 57.7987 | 57.06 | 45.3317 | 36.2957 | 21.8121 | 10.676 | -2.5382 | -19.9003 | -29.1762 | -39.2525 | -48.087 | -55.4184 | -75.6107 | -82.9242
|  |  | FS |  |  | 74.182 | 73.8556 | 62.6887 | 61.2067 | 59.0253 | 53.0868 | 50.3208 | 46.5778 | 41.8788 | 36.2368 | 23.1317 | 0.023252 | -12.8028 | -21.0065 | 64.2575 | 63.8825 | 52.7045 | 50.9526 | 48.3735 | 41.3523 | 38.1106 | 33.7156 | 28.1982 | 21.5649 | 6.1606 | -20.9662 | -36.0175 | -45.6253 | 65.6731 | 65.2986 | 54.1207 | 52.3719 | 49.7976 | 42.7895 | 39.5359 | 35.1299 | 29.5986 | 22.9541 | 7.5555 | -19.5588 | -34.6063 | -44.2234
MANNINGTON GSP | WINFRITH HEATH | WINFRITH HEATH | MINIMUM HEADROOM | SY 80748 86538 | YES | 26.1296 | 2.7701 | -11.8596 | -12.4229 | -13.483 | -14.5042 | -15.7175 | -17.3273 | -18.2423 | -19.282 | -20.2473 | -21.9194 | -28.0605 | -28.4669 | 25.2091 | -2.0906 | -19.3243 | -19.9873 | -21.3032 | -22.5327 | -23.989 | -25.9204 | -27.0755 | -28.326 | -29.5646 | -31.6778 | -38.369 | -38.8275 | 25.2366 | -2.0897 | -19.2711 | -19.9324 | -21.2473 | -22.474 | -23.9269 | -25.8535 | -27.0064 | -28.2546 | -29.4929 | -31.6102 | -38.282 | -38.7513
|  |  | CT |  |  | 26.1296 | 2.7701 | -11.8596 | -12.4229 | -13.0302 | -13.675 | -14.3116 | -14.976 | -15.7223 | -16.5774 | -18.1487 | -21.5683 | -28.0605 | -28.4669 | 25.2091 | -2.0848 | -2.1271 | -3.1346 | -21.3032 | -22.5327 | -23.989 | -25.9204 | -27.0755 | -28.326 | -29.5646 | -31.6778 | -35.8654 | -36.7568 | 25.2366 | -2.0848 | -2.1278 | -3.1331 | -21.2473 | -22.474 | -23.9269 | -25.8535 | -27.0064 | -28.2546 | -29.4929 | -31.6102 | -35.7986 | -36.7038
|  |  | LW |  |  | 26.1296 | 2.7701 | -11.8596 | -12.4229 | -13.0302 | -13.675 | -14.3116 | -14.976 | -15.7223 | -16.5774 | -18.1487 | -21.5683 | -28.0605 | -28.4669 | 25.2095 | -2.0906 | -19.3243 | -19.9873 | -20.7022 | -21.461 | -22.21 | -22.9917 | -23.8695 | -24.8755 | -26.7231 | -30.739 | -38.369 | -38.8275 | 25.2385 | -2.0897 | -19.2711 | -19.9324 | -20.6455 | -21.4024 | -22.1497 | -22.9296 | -23.8055 | -24.8093 | -26.6533 | -30.6645 | -38.282 | -38.7513
|  |  | ST |  |  | 26.1302 | 2.795 | 2.7731 | 1.9882 | -13.483 | -14.5042 | -15.7175 | -17.3273 | -18.2423 | -19.282 | -20.2473 | -21.9194 | -25.3861 | -26.0539 | 25.2281 | -2.0618 | -2.0874 | -3.0119 | -21.2371 | -22.4397 | -23.8688 | -25.7648 | -26.8424 | -28.0669 | -29.2033 | -31.1702 | -35.2497 | -36.0311 | 25.2391 | -2.0607 | -2.0863 | -3.0081 | -21.1779 | -22.377 | -23.8019 | -25.6923 | -26.7668 | -27.9877 | -29.1212 | -31.0838 | -35.1535 | -35.9357
|  |  | FS |  |  | 26.1303 | 26.1301 | 2.8135 | 2.6872 | 2.4871 | 2.2846 | 2.0233 | 1.6661 | 1.2123 | 0.65609 | -0.61916 | -2.2828 | -3.5138 | -4.2538 | 25.2324 | 25.2153 | -2.04 | -2.1886 | -2.4242 | -2.6627 | -2.9704 | -3.391 | -3.9255 | -4.5805 | -6.0825 | -8.041 | -9.4895 | -10.3594 | 25.2392 | 25.239 | -2.0389 | -2.1872 | -2.4222 | -2.6599 | -2.9668 | -3.3862 | -3.9192 | -4.5723 | -6.0699 | -8.0232 | -9.4682 | -10.3366
COWLEY GSP | WITNEY BSP | WITNEY BSP | MINIMUM HEADROOM | SP 35605 08274 | YES | 55.1417 | 29.3952 | 12.9779 | 11.1025 | 9.1523 | 6.4566 | 3.2874 | -0.78144 | -4.1437 | -7.7703 | -11.2977 | -21.4991 | -36.6996 | -43.9874 | 44.7122 | 14.2711 | -5.1041 | -7.3082 | -11.0582 | -14.4845 | -18.4528 | -23.4825 | -27.9201 | -32.4338 | -37.2619 | -45.0354 | -61.5206 | -69.5546 | 44.6546 | 14.2709 | -5.0681 | -7.2687 | -11.0094 | -14.4293 | -18.3901 | -23.4102 | -27.84 | -32.3458 | -37.166 | -44.9279 | -61.4483 | -69.4921
|  |  | CT |  |  | 55.1417 | 29.3952 | 12.9779 | 11.1025 | 9.1523 | 7.1956 | 5.2588 | 3.3339 | -0.11016 | -3.6939 | -10.6541 | -21.4991 | -36.6996 | -43.9874 | 96.0264 | 44.3928 | 43.7188 | 10.5811 | -11.0582 | -14.4845 | -18.4528 | -23.4825 | -27.9201 | -32.4338 | -37.2619 | -45.0354 | -56.4667 | -64.6009 | 96.877 | 44.3365 | 43.6638 | 10.5889 | -11.0094 | -14.4293 | -18.3901 | -23.4102 | -27.84 | -32.3458 | -37.166 | -44.9279 | -56.3406 | -64.4624
|  |  | LW |  |  | 55.1417 | 29.3952 | 12.9779 | 11.1025 | 9.1523 | 7.1956 | 5.2588 | 3.3339 | -0.11016 | -3.6939 | -10.6541 | -21.4991 | -36.6996 | -43.9874 | 44.7122 | 14.2711 | -5.1041 | -7.3082 | -9.5999 | -11.8989 | -14.1742 | -16.4349 | -20.3339 | -24.3969 | -32.2783 | -44.3275 | -61.5206 | -69.5546 | 44.6546 | 14.2709 | -5.0681 | -7.2687 | -9.557 | -11.8527 | -14.125 | -16.3828 | -20.2776 | -24.3364 | -32.2104 | -44.2597 | -61.4483 | -69.4921
|  |  | ST |  |  | 100.4201 | 55.1357 | 54.9149 | 27.364 | 9.1707 | 6.4566 | 3.2874 | -0.78144 | -4.1437 | -7.7703 | -11.2977 | -16.3399 | -25.0786 | -31.1266 | 96.5721 | 44.7048 | 44.444 | 11.87 | -9.583 | -12.7751 | -16.5027 | -21.2887 | -25.2147 | -29.4519 | -33.5425 | -39.2651 | -49.2076 | -55.9552 | 96.9763 | 44.6475 | 44.387 | 11.8745 | -9.5381 | -12.7245 | -16.4454 | -21.2228 | -25.1421 | -29.372 | -33.4564 | -39.174 | -49.1064 | -55.8507
|  |  | FS |  |  | 100.4202 | 100.4199 | 82.2372 | 81.8508 | 81.2969 | 53.7029 | 52.9889 | 52.0449 | 50.9066 | 49.5785 | 46.554 | 42.3329 | 38.8887 | 36.4001 | 97.1281 | 96.1585 | 76.7486 | 76.2922 | 75.6378 | 43.0121 | 42.1685 | 41.0527 | 39.7074 | 38.1375 | 34.5623 | 29.575 | 25.5067 | 22.5687 | 97.0783 | 96.9004 | 76.6306 | 76.1749 | 75.5216 | 42.9576 | 42.1153 | 41.0015 | 39.6585 | 38.0915 | 34.5225 | 29.543 | 25.4801 | 22.5451
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM BSP | MINIMUM HEADROOM | SU 79589 67665 | YES | 91.9015 | 56.4533 | 56.4533 | 55.1775 | 53.8172 | 52.4341 | 51.0264 | 49.5951 | 47.7197 | 45.8338 | 42.1267 | 36.8858 | 31.7635 | 27.2 | 90.9211 | 56.3261 | 55.9266 | 54.3567 | 52.7405 | 51.0604 | 49.314 | 47.4335 | 45.511 | 43.549 | 39.3419 | 33.5157 | 27.8197 | 22.7071 | 91.03 | 56.3087 | 55.3798 | 54.0184 | 52.4017 | 50.721 | 48.974 | 47.093 | 45.1698 | 43.2074 | 38.9992 | 33.1718 | 27.4745 | 22.3607
|  |  | CT |  |  | 91.9015 | 56.4533 | 56.4533 | 55.1775 | 53.8172 | 52.4341 | 51.0264 | 49.5951 | 47.7197 | 45.8338 | 42.1267 | 36.8858 | 31.7635 | 27.2 | 90.9219 | 56.3271 | 55.9555 | 54.3567 | 52.7405 | 51.0604 | 49.314 | 47.4335 | 45.511 | 43.5683 | 40.0026 | 35.1065 | 30.3356 | 25.6294 | 91.0302 | 56.3095 | 55.4046 | 54.0184 | 52.4017 | 50.721 | 48.974 | 47.093 | 45.1698 | 43.2266 | 39.6598 | 34.7624 | 29.9902 | 25.2827
|  |  | LW |  |  | 91.9015 | 56.4533 | 56.4533 | 55.1775 | 53.8172 | 52.4341 | 51.0264 | 49.5951 | 47.7197 | 45.8338 | 42.1267 | 36.8858 | 31.7635 | 27.2 | 90.9211 | 56.3261 | 55.9266 | 54.3737 | 52.7766 | 51.1527 | 49.5 | 47.8197 | 45.6905 | 43.549 | 39.3419 | 33.5157 | 27.8197 | 22.7071 | 91.03 | 56.3087 | 55.3798 | 54.0353 | 52.4378 | 50.8133 | 49.1601 | 47.4792 | 45.3495 | 43.2074 | 38.9992 | 33.1718 | 27.4745 | 22.3607
|  |  | ST |  |  | 91.9015 | 91.9015 | 56.4533 | 56.4533 | 55.9477 | 55.3112 | 54.6202 | 53.823 | 53.0878 | 52.3193 | 51.0338 | 48.3599 | 45.4849 | 42.5787 | 91.1375 | 90.8955 | 56.3473 | 56.2686 | 55.2778 | 54.5306 | 53.7194 | 52.7834 | 51.9341 | 51.0459 | 49.5647 | 46.5233 | 43.3089 | 40.0718 | 91.0697 | 91.0253 | 56.3242 | 55.8311 | 54.824 | 54.1838 | 53.3808 | 52.4445 | 51.5951 | 50.7066 | 49.2249 | 46.1827 | 42.9675 | 39.7297
|  |  | FS |  |  | 91.9015 | 91.9015 | 91.9015 | 56.4533 | 56.4533 | 56.4533 | 56.4533 | 56.4533 | 56.4533 | 56.4533 | 56.0593 | 54.9152 | 53.9317 | 53.0658 | 91.1933 | 91.0967 | 91.0614 | 56.3929 | 56.365 | 56.346 | 56.3253 | 56.2996 | 56.2733 | 56.1511 | 55.4088 | 54.0657 | 52.911 | 51.8944 | 91.0799 | 91.0622 | 91.0557 | 56.3575 | 56.3372 | 56.3233 | 56.3082 | 56.1645 | 55.8817 | 55.5773 | 54.9362 | 53.7273 | 52.5722 | 51.5553
LOVEDEAN GSP | WYMERING BSP | WYMERING BSP | MINIMUM HEADROOM | SU 64948 05441 | YES | 146.6365 | 146.422 | 145.9602 | 145.2109 | 144.4326 | 143.219 | 142.1016 | 183.8451 | 183.4682 | 183.1715 | 182.5858 | 183.7611 | 153.7028 | 147.3611 | 150.9784 | 150.7262 | 150.1827 | 149.3007 | 148.3847 | 147.138 | 145.9639 | 180.1092 | 179.7529 | 179.4062 | 178.7345 | 153.4243 | 146.8146 | 141.1442 | 152.9427 | 152.6976 | 152.1696 | 151.313 | 150.4032 | 149.0505 | 147.7945 | 182.1078 | 181.6116 | 181.1326 | 180.2134 | 154.4619 | 147.4115 | 141.5976
|  |  | CT |  |  | 146.6365 | 146.422 | 145.9602 | 145.2109 | 144.4326 | 143.219 | 142.1016 | 197.6311 | 196.7751 | 195.945 | 193.9461 | 190.0657 | 153.7028 | 147.3611 | 159.774 | 150.7881 | 150.3272 | 149.4184 | 148.5041 | 147.4982 | 146.0281 | 180.1092 | 179.7529 | 179.4062 | 178.7345 | 153.4243 | 146.8146 | 141.1442 | 162.0045 | 152.7562 | 152.3075 | 151.4239 | 150.5184 | 149.5141 | 147.916 | 182.1078 | 181.6116 | 181.1326 | 180.2134 | 154.4619 | 147.4115 | 141.5976
|  |  | LW |  |  | 146.6365 | 146.422 | 145.9602 | 145.2109 | 144.4326 | 143.219 | 142.1016 | 197.6311 | 196.7751 | 195.945 | 193.9461 | 190.0657 | 153.7028 | 147.3611 | 150.9784 | 150.7262 | 150.1827 | 149.3007 | 148.3847 | 147.138 | 145.9639 | 194.3213 | 193.6779 | 193.0539 | 191.5943 | 188.6658 | 185.6977 | 149.6138 | 152.9427 | 152.6976 | 152.1696 | 151.313 | 150.4032 | 149.0505 | 147.7945 | 196.3442 | 195.5689 | 194.828 | 192.9687 | 189.4199 | 185.7539 | 150.1048
|  |  | ST |  |  | 151.3866 | 146.6285 | 146.4273 | 145.8489 | 145.1889 | 144.0744 | 142.9069 | 183.8451 | 183.4682 | 183.1715 | 182.5858 | 195.3736 | 193.5689 | 191.6499 | 159.9054 | 150.9688 | 150.7319 | 150.0508 | 149.2736 | 148.0343 | 146.7275 | 180.3855 | 180.1955 | 180.0599 | 179.7541 | 193.0489 | 191.7629 | 190.3649 | 162.0081 | 152.9335 | 152.7035 | 152.0421 | 151.2874 | 150.0109 | 148.6669 | 182.6011 | 182.3339 | 182.1636 | 181.7614 | 194.8636 | 193.3947 | 191.7976
|  |  | FS |  |  | 151.4465 | 150.2589 | 146.6973 | 146.5369 | 146.3407 | 146.0871 | 145.7389 | 184.5344 | 184.402 | 184.2672 | 184.0754 | 183.7611 | 183.5252 | 183.2914 | 159.9117 | 159.7861 | 151.0498 | 150.861 | 150.6301 | 150.3315 | 149.953 | 180.5592 | 180.5054 | 180.4529 | 180.4009 | 180.3159 | 180.2652 | 180.2096 | 162.0082 | 162.008 | 153.0122 | 152.8288 | 152.6045 | 152.3146 | 151.9258 | 182.9114 | 182.8153 | 182.7214 | 182.6287 | 182.4768 | 182.3863 | 182.2871
COWLEY GSP | YARNTON BSP | YARNTON BSP | MINIMUM HEADROOM | SP 35605 08274 | YES | 70.3384 | 33.5192 | 32.8316 | 26.8362 | 25.4175 | 23.9736 | 22.5823 | 21.2452 | 19.0914 | 16.8568 | 12.6312 | -0.30855 | -24.4371 | -31.2541 | 62.2815 | 18.9306 | 18.1216 | 11.067 | 9.3976 | 7.6987 | 6.0616 | 4.4884 | 2.041 | -0.50122 | -5.2993 | -20.1333 | -48.1436 | -55.8711 | 63.4006 | 20.6154 | 19.8079 | 12.7667 | 11.1005 | 9.4048 | 7.7708 | 6.2005 | 3.7569 | 1.2185 | -3.5723 | -18.3824 | -46.3437 | -54.0597
|  |  | CT |  |  | 70.3384 | 33.5192 | 32.8316 | 26.8362 | 25.4175 | 23.9736 | 22.5823 | 21.2452 | 19.0914 | 16.8568 | 12.6312 | -0.30855 | -24.4371 | -31.2541 | 66.8074 | 61.8048 | 18.9874 | 15.9083 | 13.8803 | 11.6225 | 9.1923 | 6.3386 | 3.5879 | 0.82694 | -2.812 | -12.994 | -30.2193 | -37.8494 | 67.856 | 62.9312 | 20.6721 | 17.5988 | 15.5747 | 13.3212 | 10.8956 | 8.0472 | 5.3014 | 2.5453 | -1.0874 | -11.2519 | -28.4463 | -36.0636
|  |  | LW |  |  | 70.3384 | 33.5192 | 32.8316 | 26.8362 | 25.4175 | 23.9736 | 22.5823 | 21.2452 | 19.0914 | 16.8568 | 12.6312 | -0.30855 | -24.4371 | -31.2541 | 62.2815 | 18.9306 | 18.1216 | 11.067 | 9.3976 | 7.6987 | 6.0616 | 4.4884 | 2.041 | -0.50122 | -5.2993 | -20.1333 | -48.1436 | -55.8711 | 63.4006 | 20.6154 | 19.8079 | 12.7667 | 11.1005 | 9.4048 | 7.7708 | 6.2005 | 3.7569 | 1.2185 | -3.5723 | -18.3824 | -46.3437 | -54.0597
|  |  | ST |  |  | 74.5187 | 70.3034 | 34.4511 | 32.4176 | 31.1299 | 29.4907 | 27.6953 | 25.5403 | 23.5985 | 21.5601 | 19.0896 | 12.4729 | -0.37548 | -5.152 | 67.2242 | 62.2402 | 20.0272 | 17.6344 | 16.1192 | 14.1905 | 12.0779 | 9.5422 | 7.2741 | 4.8924 | 2.019 | -5.6493 | -20.5746 | -25.9853 | 68.2663 | 63.3599 | 21.7099 | 19.3216 | 17.8094 | 15.8843 | 13.7757 | 11.2448 | 8.9808 | 6.6035 | 3.7351 | -3.9199 | -18.819 | -24.2217
|  |  | FS |  |  | 102.2109 | 74.3088 | 74.2212 | 38.3765 | 37.1046 | 32.7809 | 32.2914 | 31.6846 | 30.9845 | 30.2157 | 28.5773 | 25.992 | 23.7645 | 21.959 | 97.633 | 66.976 | 66.8724 | 24.646 | 23.1494 | 18.0619 | 17.486 | 16.772 | 15.9481 | 15.0436 | 13.1157 | 10.0736 | 7.4526 | 5.3282 | 99.6894 | 68.022 | 67.92 | 26.32 | 24.8262 | 19.7484 | 19.1735 | 18.4608 | 17.6386 | 16.7357 | 14.8115 | 11.7752 | 9.1592 | 7.0388
AXMINSTER | YEOVIL BSP | YEOVIL BSP | MINIMUM HEADROOM | ST 57586 16894 | YES | 180.8917 | 48.8588 | 48.5609 | 43.8774 | 39.1385 | 33.4472 | 27.9916 | 22.8163 | 17.1778 | 11.1424 | -1.2229 | -16.2579 | -41.9434 | -47.4234 | 105.2956 | 10.524 | 10.1821 | 1.7896 | -6.0602 | -15.8098 | -28.2544 | -44.3807 | -53.1723 | -62.2247 | -70.8952 | -82.3241 | -101.7025 | -109.858 | 104.911 | 10.5889 | 10.2487 | 2.0563 | -5.5958 | -15.0989 | -27.4856 | -43.4474 | -52.3894 | -61.5849 | -70.5221 | -82.7812 | -102.9953 | -111.4728
|  |  | CT |  |  | 180.8917 | 48.8588 | 48.5609 | 43.8774 | 39.1385 | 33.4472 | 27.9916 | 22.8163 | 17.1778 | 11.1424 | -1.2229 | -16.2579 | -41.9434 | -47.4234 | 105.5556 | 41.2411 | 40.9025 | 1.7896 | -6.0602 | -15.8098 | -28.2544 | -44.3807 | -53.1723 | -62.2247 | -70.8952 | -82.3241 | -101.7025 | -109.858 | 105.1679 | 41.0186 | 40.678 | 2.0563 | -5.5958 | -15.0989 | -27.4856 | -43.4474 | -52.3894 | -61.5849 | -70.5221 | -82.7812 | -102.9953 | -111.4728
|  |  | LW |  |  | 180.8917 | 48.8588 | 48.5609 | 43.8774 | 39.1385 | 33.4472 | 27.9916 | 22.8163 | 17.1778 | 11.1424 | -1.2229 | -16.2579 | -41.9434 | -47.4234 | 105.2956 | 10.524 | 10.1821 | 4.6954 | -0.86024 | -7.2147 | -13.363 | -19.3083 | -25.6914 | -32.5666 | -46.3756 | -62.894 | -91.8104 | -97.6543 | 104.911 | 10.5889 | 10.2487 | 4.8974 | -0.51672 | -6.9185 | -13.0731 | -18.9469 | -25.3165 | -32.1486 | -46.0586 | -63.2162 | -92.8546 | -99.0355
|  |  | ST |  |  | 181.1605 | 75.8218 | 75.6374 | 69.0854 | 61.9261 | 53.2296 | 42.9204 | 29.4306 | 22.1726 | 14.4209 | 7.2849 | 0.021114 | -13.97 | -19.8584 | 106.5372 | 41.6009 | 41.3887 | 33.8296 | 25.5699 | 15.679 | 3.7784 | -11.9491 | -20.3261 | -29.3612 | -37.5589 | -45.733 | -61.8226 | -68.3734 | 106.1761 | 41.3846 | 41.1738 | 33.6834 | 25.4988 | 15.5972 | 3.8485 | -11.5418 | -19.7946 | -28.6375 | -36.7392 | -44.9735 | -61.2621 | -68.0247
|  |  | FS |  |  | 181.1609 | 181.1602 | 76.0409 | 74.8569 | 73.0742 | 71.2511 | 68.7249 | 65.3257 | 61.0378 | 55.907 | 44.1206 | 29.0838 | 17.6676 | 10.4034 | 160.6202 | 105.875 | 41.8538 | 40.4884 | 38.4322 | 36.3292 | 33.4762 | 29.6197 | 24.7545 | 18.9142 | 5.2667 | -12.2646 | -25.5956 | -34.0462 | 167.5257 | 105.4985 | 41.6351 | 40.2818 | 38.244 | 36.1599 | 33.2894 | 29.4216 | 24.5424 | 18.6984 | 5.243 | -11.913 | -24.9451 | -33.2271
IVER 66KV | YIEWSLEY | YIEWSLEY | MINIMUM HEADROOM | TQ 05643 80961 | NO | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 56.6294 | 59.6514 | 59.5708 | 59.4922 | 59.4354 | 59.4186 | 59.4 | 59.3803 | 59.36 | 59.3382 | 59.3163 | 59.271 | 59.1224 | 52.6189 | 50.9487 | 52.9415 | 52.8198 | 52.7011 | 52.5649 | 52.3923 | 52.202 | 52.0003 | 51.792 | 51.5686 | 51.3436 | 50.8791 | 49.3547 | 47.8291 | 46.2991
|  |  | CT |  |  | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 56.6294 | 59.6553 | 59.5875 | 59.5228 | 59.4444 | 59.4273 | 59.412 | 59.3969 | 59.382 | 59.3644 | 59.3462 | 59.3078 | 59.1784 | 59.0489 | 52.007 | 52.9475 | 52.8451 | 52.7473 | 52.629 | 52.4815 | 52.3248 | 52.1703 | 52.0173 | 51.8371 | 51.6506 | 51.2558 | 49.9289 | 48.6006 | 47.2686
|  |  | LW |  |  | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 56.6294 | 59.6514 | 59.5708 | 59.4922 | 59.4354 | 59.4186 | 59.4 | 59.3803 | 59.36 | 59.3382 | 59.3163 | 59.271 | 59.1224 | 52.6189 | 50.9487 | 52.9415 | 52.8198 | 52.7011 | 52.5649 | 52.3923 | 52.202 | 52.0003 | 51.792 | 51.5686 | 51.3436 | 50.8791 | 49.3547 | 47.8291 | 46.2991
|  |  | ST |  |  | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 59.9358 | 59.6188 | 59.58 | 59.5171 | 59.4394 | 59.4222 | 59.4053 | 59.3887 | 59.3695 | 59.35 | 59.3096 | 59.2097 | 59.1141 | 53.1366 | 53.371 | 52.8923 | 52.8337 | 52.7387 | 52.6065 | 52.43 | 52.2566 | 52.0856 | 51.8895 | 51.6894 | 51.2749 | 50.2496 | 49.2694 | 48.3035
|  |  | FS |  |  | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 65.3736 | 59.9477 | 59.6571 | 59.6528 | 59.6384 | 59.6154 | 59.5777 | 59.5391 | 59.4909 | 59.4422 | 59.4341 | 59.4195 | 59.3817 | 59.3445 | 59.307 | 53.3889 | 52.9501 | 52.9437 | 52.922 | 52.8871 | 52.8302 | 52.772 | 52.6992 | 52.6256 | 52.5516 | 52.4017 | 52.0145 | 51.633 | 51.2479

## LEP Reference
LEP | Local Authority | Grid Supply Point | Bulk Supply Point | Primary Substation
Buckinghamshire Thames Valley | Chiltern | AMERSHAM | LOUDWATER BSP | BOWERDEAN
Buckinghamshire Thames Valley | Chiltern | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | DENHAM | COKES LANE
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | DENHAM | GERRARDS CROSS
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Buckinghamshire Thames Valley | South Bucks | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Buckinghamshire Thames Valley | South Bucks | AMERSHAM | LOUDWATER BSP | WELL END
Buckinghamshire Thames Valley | South Bucks | BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD
Buckinghamshire Thames Valley | South Bucks | BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | CHALVEY BSP | CHALVEY
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | DENHAM | DENHAM AVENUE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | DENHAM | GERRARDS CROSS
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | LONGFORD | POYLE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | SLOUGH | FARNHAM ROYAL
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | SLOUGH | TAPLOW
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | UPTON BSP | SUTTON LANE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | UPTON BSP | UPTON
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | BOWERDEAN
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | WELL END
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH
Buckinghamshire Thames Valley | Wycombe | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Buckinghamshire Thames Valley | Wycombe | BRAMLEY (FLEE) | READING BSP | HENLEY
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON
Buckinghamshire Thames Valley | Wycombe | IVER 132KV | SLOUGH | TAPLOW
Buckinghamshire Thames Valley | Wycombe | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Coast to Capital | Arun | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTEAD
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | MIDHURST
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | EMSWORTH
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | GABLE HEAD
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | HORNDEAN
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | LEIGH PARK
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Coast to Capital | Horsham | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Coast to Capital | Horsham | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Coast to Capital | Horsham | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Coast to Capital | Horsham | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST
Coast to Capital | Mole Valley | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Coventry and Warwickshire | Stratford-on-Avon | COWLEY GSP | WITNEY BSP | BLEDDINGTON
Coventry and Warwickshire | Stratford-on-Avon | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | ALDERNEY
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | CENTRAL
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE
Dorset | Bournemouth | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | Bournemouth | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Dorset | Bournemouth | MANNINGTON GSP | REDHILL BSP | REDHILL
Dorset | Bournemouth | MANNINGTON GSP | REDHILL BSP | WINTON
Dorset | Christchurch | MANNINGTON GSP | ARNEWOOD | NEW MILTON
Dorset | Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Dorset | Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Dorset | Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE
Dorset | Christchurch | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | Christchurch | MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood
Dorset | Christchurch | MANNINGTON GSP | REDHILL BSP | REDHILL
Dorset | Christchurch | MANNINGTON GSP | REDHILL BSP | WINTON
Dorset | East Dorset | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | BLANDFORD
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | MANNINGTON
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | VERWOOD
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES
Dorset | East Dorset | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Dorset | East Dorset | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Dorset | East Dorset | MANNINGTON GSP | REDHILL BSP | REDHILL
Dorset | East Dorset | MANNINGTON GSP | SALISBURY | HOMINGTON
Dorset | East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL
Dorset | East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Dorset | East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | PULHAM
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | SHERBORNE
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | YETMINSTER
Dorset | North Dorset | CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE
Dorset | North Dorset | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
Dorset | North Dorset | MANNINGTON GSP | LYTCHETT | BLANDFORD
Dorset | North Dorset | MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON
Dorset | North Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | ALDERNEY
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE
Dorset | Poole | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Dorset | Poole | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Dorset | Poole | MANNINGTON GSP | LYTCHETT | HOLES BAY
Dorset | Poole | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | Poole | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
Dorset | Poole | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Dorset | Poole | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Dorset | Poole | MANNINGTON GSP | REDHILL BSP | WINTON
Dorset | Purbeck | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
Dorset | Purbeck | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | BLANDFORD
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON
Dorset | Purbeck | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | BOVINGTON
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | BUSHEY
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | SWANAGE
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | WAREHAM TOWN
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | CHILTON CANTELLO
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | MILBORNE PORT
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | PULHAM
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | SHERBORNE
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | WEST HENDFORD
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | YEOVIL
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | YETMINSTER
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | CHICKERELL
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | DORCHESTER TOWN
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | REDLANDS
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH
Dorset | West Dorset | MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON
Dorset | West Dorset | MANNINGTON GSP | WAREHAM | BOVINGTON
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | CHICKERELL
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | DORCHESTER TOWN
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | PORTLAND
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | REDLANDS
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | ALRESFORD
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | HERRIARD
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Enterprise M3 | Elmbridge | LALEHAM | STAINES | SUNBURY CROSS
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Enterprise M3 | Guildford | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Enterprise M3 | Guildford | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Enterprise M3 | Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Enterprise M3 | Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN
Enterprise M3 | Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM
Enterprise M3 | Hart | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Enterprise M3 | Hart | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Enterprise M3 | Hart | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Enterprise M3 | Hart | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Enterprise M3 | Hart | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Enterprise M3 | Hart | BRAMLEY (FLEE) | PYESTOCK BSP | Crookham (Church)
Enterprise M3 | Runnymede | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Enterprise M3 | Runnymede | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Enterprise M3 | Runnymede | IVER 132KV | CHALVEY BSP | CHALVEY
Enterprise M3 | Runnymede | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Enterprise M3 | Runnymede | LALEHAM | STAINES | CAUSEWAY
Enterprise M3 | Runnymede | LALEHAM | STAINES | EGHAM
Enterprise M3 | Runnymede | LALEHAM | STAINES | SIDNEY ROAD
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | PYESTOCK BSP | Crookham (Church)
Enterprise M3 | Spelthorne | IVER 132KV | CHALVEY BSP | CHALVEY
Enterprise M3 | Spelthorne | IVER 132KV | LONGFORD | POYLE
Enterprise M3 | Spelthorne | LALEHAM | EAST BEDFONT A | CHURCH ROAD
Enterprise M3 | Spelthorne | LALEHAM | STAINES | CAUSEWAY
Enterprise M3 | Spelthorne | LALEHAM | STAINES | SIDNEY ROAD
Enterprise M3 | Spelthorne | LALEHAM | STAINES | STANWELL
Enterprise M3 | Spelthorne | LALEHAM | STAINES | SUNBURY CROSS
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALTON | BORDON
Enterprise M3 | Waverley | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Enterprise M3 | Waverley | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Enterprise M3 | Waverley | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Enterprise M3 | Waverley | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Enterprise M3 | Woking | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Gloucestershire | Cheltenham | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Gloucestershire | Cotswold | BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITELEY WOOD
Gloucestershire | Cotswold | COWLEY GSP | WITNEY BSP | BLEDDINGTON
Gloucestershire | Cotswold | COWLEY GSP | WITNEY BSP | RISSINGTON
Gloucestershire | Cotswold | MELKSHAM GSP | CHIPPENHAM | ALDERTON
Gloucestershire | Cotswold | MELKSHAM GSP | CHIPPENHAM | MALMESBURY
Gloucestershire | Cotswold | MELKSHAM GSP | CHIPPENHAM | TETBURY
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Gloucestershire | Cotswold | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Gloucestershire | Cotswold | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Gloucestershire | Tewkesbury | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Gloucestershire | Tewkesbury | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Heart of the South West | Mendip | AXMINSTER | YEOVIL BSP | SPARKFORD
Heart of the South West | Mendip | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | BRUTON
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | CROCKERTON
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | FROME
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | HAWKERIDGE
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | HOLWELL
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | WESTBURY
Heart of the South West | Mendip | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
Heart of the South West | Mendip | MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | CASTLE CARY
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | CHILTON CANTELLO
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | LARKHILL
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | MILBORNE PORT
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | SHERBORNE
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | SPARKFORD
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | WEST HENDFORD
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | YEOVIL
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | YETMINSTER
Heart of the South West | South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Heart of the South West | South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR
Heart of the South West | South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON
Heart of the South West | South Somerset | MELKSHAM GSP | FROME BSP | BRUTON
Heart of the South West | South Somerset | MELKSHAM GSP | FROME BSP | HOLWELL
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | COKES LANE
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | DENHAM AVENUE
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | HAREFIELD
London | Brent | WILLESDEN GSP | ACTON LANE | PARK ROYAL
London | Brent | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
London | Ealing | EALING GSP | EALING (D) | BRENTFORD
London | Ealing | EALING GSP | EALING (D) | DEAN GARDENS
London | Ealing | EALING GSP | EALING (D) | HARVARD LANE
London | Ealing | NORTH HYDE GSP | NORTH HYDE (D) | SPRINGFIELD ROAD
London | Ealing | NORTH HYDE GSP | NORTH HYDE (D) | THE GREEN
London | Ealing | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
London | Ealing | WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK
London | Ealing | WILLESDEN GSP | ACTON LANE | PARK ROYAL
London | Ealing | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
London | Hammersmith and Fulham | EALING GSP | EALING (D) | HARVARD LANE
London | Hammersmith and Fulham | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
London | Hammersmith and Fulham | WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK
London | Hammersmith and Fulham | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
London | Hillingdon | IVER 132KV | DENHAM | DENHAM AVENUE
London | Hillingdon | IVER 132KV | DENHAM | HAREFIELD
London | Hillingdon | IVER 132KV | LONGFORD | BATH ROAD WEST
London | Hillingdon | IVER 132KV | LONGFORD | POYLE
London | Hillingdon | IVER 132KV | UPTON BSP | UPTON
London | Hillingdon | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
London | Hillingdon | NORTH HYDE GSP | NORTH HYDE (D) | BATH ROAD EAST
London | Hillingdon | NORTH HYDE GSP | NORTH HYDE (D) | SPRINGFIELD ROAD
London | Hounslow | EALING GSP | EALING (D) | BRENTFORD
London | Hounslow | EALING GSP | EALING (D) | HARVARD LANE
London | Hounslow | LALEHAM | EAST BEDFONT A | CHURCH ROAD
London | Hounslow | LALEHAM | EAST BEDFONT A | FELTHAM
London | Hounslow | LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR
London | Hounslow | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
London | Hounslow | LALEHAM | STAINES | STANWELL
London | Hounslow | LALEHAM | STAINES | SUNBURY CROSS
London | Hounslow | NORTH HYDE GSP | NORTH HYDE (D) | BATH ROAD EAST
London | Hounslow | NORTH HYDE GSP | NORTH HYDE (D) | THE GREEN
London | Hounslow | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
London | Richmond upon Thames | EALING GSP | EALING (D) | BRENTFORD
London | Richmond upon Thames | EALING GSP | EALING (D) | HARVARD LANE
London | Richmond upon Thames | LALEHAM | EAST BEDFONT A | FELTHAM
London | Richmond upon Thames | LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR
London | Richmond upon Thames | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
London | Richmond upon Thames | LALEHAM | STAINES | SUNBURY CROSS
Oxfordshire LEP | Cherwell | COWLEY GSP | HEADINGTON BSP | ARNCOTT
Oxfordshire LEP | Cherwell | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | Cherwell | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | DEDDINGTON
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | KIDDINGTON
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | WOODSTOCK
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | Cherwell | EAST CLAYDON GSP | BICESTER NORTH | BICESTER
Oxfordshire LEP | Cherwell | EAST CLAYDON GSP | BICESTER NORTH | COTTISFORD
Oxfordshire LEP | Cherwell | EAST CLAYDON GSP | BICESTER NORTH | UPPER HEYFORD
Oxfordshire LEP | Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Oxfordshire LEP | Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET
Oxfordshire LEP | Oxford | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | Oxford | COWLEY GSP | HEADINGTON BSP | OLD ROAD
Oxfordshire LEP | Oxford | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | OSNEY
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES
Oxfordshire LEP | Oxford | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Oxfordshire LEP | Oxford | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | South Oxfordshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | HENLEY
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | KIDMORE END
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | READING
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | TWYFORD
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | CHOLSEY
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | FULSCOT
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | MILTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | WINSMORE LANE
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | ARNCOTT
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | OLD ROAD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | Vale of White Horse | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Oxfordshire LEP | Vale of White Horse | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | CHOLSEY
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | FULSCOT
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | GROVE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | MILTON
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | WANTAGE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | WINSMORE LANE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | OSNEY
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | WITNEY BSP | FYFIELD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | WITNEY BSP | STANDLAKE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | YARNTON BSP | EYNSHAM
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Oxfordshire LEP | Vale of White Horse | MINETY GSP | TOOTHILL BSP | CHISLEDON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | BLEDDINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | BURFORD
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | CARTERTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | FYFIELD
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | LEAFIELD
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | RISSINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | STANDLAKE
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | WINDRUSH PARK
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | WITNEY TOWN
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | CHARLBURY
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | DEDDINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | EYNSHAM
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | KIDDINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | WOODSTOCK
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | West Oxfordshire | EAST CLAYDON GSP | BICESTER NORTH | UPPER HEYFORD
Oxfordshire LEP | West Oxfordshire | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Oxfordshire LEP | West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON
Oxfordshire LEP | West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Oxfordshire LEP | West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Solent | East Hampshire | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Solent | East Hampshire | BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | ALRESFORD
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | BORDON
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | HERRIARD
Solent | East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD
Solent | East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Solent | East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Solent | East Hampshire | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Solent | East Hampshire | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Solent | East Hampshire | LOVEDEAN GSP | HAVANT | EMSWORTH
Solent | East Hampshire | LOVEDEAN GSP | HAVANT | HORNDEAN
Solent | East Hampshire | LOVEDEAN GSP | HAVANT | LEIGH PARK
Solent | Eastleigh | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON
Solent | Eastleigh | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Eastleigh | NURSLING GSP | ROWNHAMS | SILKSTEAD
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | BASSETT
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | BISHOPSTOKE
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | CHANDLERSFORD
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | HEDGE END
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | VELMORE
Solent | Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE
Solent | Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY
Solent | Fareham | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSY TITCHFIELD
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK
Solent | Fareham | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Solent | Fareham | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD
Solent | Havant | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Solent | Havant | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Solent | Havant | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Solent | Havant | LOVEDEAN GSP | HAVANT | BROCKHAMPTON
Solent | Havant | LOVEDEAN GSP | HAVANT | EMSWORTH
Solent | Havant | LOVEDEAN GSP | HAVANT | GABLE HEAD
Solent | Havant | LOVEDEAN GSP | HAVANT | HORNDEAN
Solent | Havant | LOVEDEAN GSP | HAVANT | LEIGH PARK
Solent | Havant | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Solent | Havant | LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK
Solent | Havant | LOVEDEAN GSP | WYMERING BSP | FARLINGTON
Solent | Havant | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR
Solent | Isle of Wight | LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET
Solent | New Forest | BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE
Solent | New Forest | FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER
Solent | New Forest | FAWLEY GSP | LANGLEY BSP | BUTTS ASH
Solent | New Forest | FAWLEY GSP | LANGLEY BSP | LANGLEY
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | HINCHELSEA
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | LYMINGTON
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | NEW MILTON
Solent | New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Solent | New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | MANNINGTON
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | VERWOOD
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES
Solent | New Forest | MANNINGTON GSP | SALISBURY | HOMINGTON
Solent | New Forest | MANNINGTON GSP | SALISBURY | REDLYNCH
Solent | New Forest | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Solent | New Forest | NURSLING GSP | ROWNHAMS | FLETCHWOOD
Solent | New Forest | NURSLING GSP | ROWNHAMS | LORDSHILL
Solent | New Forest | NURSLING GSP | ROWNHAMS | ROMSEY
Solent | New Forest | NURSLING GSP | ROWNHAMS | TOTTON
Solent | New Forest | NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE
Solent | New Forest | NURSLING GSP | WINCHESTER | DUNBRIDGE
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD
Solent | Portsmouth | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Solent | Portsmouth | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | FARLINGTON
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | HILSEA
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON
Solent | Southampton | NURSLING GSP | ROWNHAMS | LORDSHILL
Solent | Southampton | NURSLING GSP | ROWNHAMS | MAYBUSH
Solent | Southampton | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE
Solent | Southampton | NURSLING GSP | VELMORE BSP | BASSETT
Solent | Southampton | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Solent | Southampton | NURSLING GSP | VELMORE BSP | VELMORE
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER TOWN
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | PORTWAY
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH
Solent | Test Valley | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Solent | Test Valley | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Solent | Test Valley | MANNINGTON GSP | SALISBURY | PETERSFINGER
Solent | Test Valley | MELKSHAM GSP | AMESBURY | PARK HOUSE
Solent | Test Valley | MELKSHAM GSP | WEST GRAFTON | TIDWORTH
Solent | Test Valley | MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE
Solent | Test Valley | NURSLING GSP | ROWNHAMS | FLETCHWOOD
Solent | Test Valley | NURSLING GSP | ROWNHAMS | LORDSHILL
Solent | Test Valley | NURSLING GSP | ROWNHAMS | MAYBUSH
Solent | Test Valley | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Test Valley | NURSLING GSP | ROWNHAMS | ROMSEY
Solent | Test Valley | NURSLING GSP | ROWNHAMS | SILKSTEAD
Solent | Test Valley | NURSLING GSP | ROWNHAMS | TOTTON
Solent | Test Valley | NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK
Solent | Test Valley | NURSLING GSP | VELMORE BSP | BASSETT
Solent | Test Valley | NURSLING GSP | VELMORE BSP | CHANDLERSFORD
Solent | Test Valley | NURSLING GSP | VELMORE BSP | VELMORE
Solent | Test Valley | NURSLING GSP | WINCHESTER | DUNBRIDGE
Solent | Test Valley | NURSLING GSP | WINCHESTER | HARESTOCK
Solent | Test Valley | NURSLING GSP | WINCHESTER | HOUGHTON
Solent | Winchester | BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE
Solent | Winchester | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY
Solent | Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM
Solent | Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV
Solent | Winchester | BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY
Solent | Winchester | BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH
Solent | Winchester | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON
Solent | Winchester | BRAMLEY (FLEE) | ALTON | ALRESFORD
Solent | Winchester | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Solent | Winchester | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Solent | Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM
Solent | Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSY TITCHFIELD
Solent | Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD
Solent | Winchester | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Solent | Winchester | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Solent | Winchester | LOVEDEAN GSP | HAVANT | HORNDEAN
Solent | Winchester | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Solent | Winchester | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Winchester | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Winchester | NURSLING GSP | ROWNHAMS | SILKSTEAD
Solent | Winchester | NURSLING GSP | VELMORE BSP | CHANDLERSFORD
Solent | Winchester | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Solent | Winchester | NURSLING GSP | VELMORE BSP | HEDGE END
Solent | Winchester | NURSLING GSP | WINCHESTER | DUNBRIDGE
Solent | Winchester | NURSLING GSP | WINCHESTER | GORDON ROAD
Solent | Winchester | NURSLING GSP | WINCHESTER | HARESTOCK
Solent | Winchester | NURSLING GSP | WINCHESTER | HOUGHTON
Solent | Winchester | NURSLING GSP | WINCHESTER | ST CROSS
South East Midlands | Aylesbury Vale | COWLEY GSP | HEADINGTON BSP | ARNCOTT
South East Midlands | Aylesbury Vale | COWLEY GSP | HEADINGTON BSP | WHEATLEY
South East Midlands | Aylesbury Vale | EAST CLAYDON GSP | BICESTER NORTH | BICESTER
South East Midlands | Aylesbury Vale | EAST CLAYDON GSP | BICESTER NORTH | COTTISFORD
South East Midlands | South Northamptonshire | COWLEY GSP | YARNTON BSP | DEDDINGTON
South East Midlands | South Northamptonshire | EAST CLAYDON GSP | BICESTER NORTH | COTTISFORD
Swindon and Wiltshire | Swindon | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Swindon and Wiltshire | Swindon | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Swindon and Wiltshire | Swindon | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Swindon and Wiltshire | Swindon | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | STRATTON
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | DRAKES WAY
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | PARK NORTH
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | PLESSEY Swindon
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON SE
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | MANCHESTER ROAD
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | SWINDON
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | TRADING ESTATE
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | WOOTTON BASSETT
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | CHISLEDON
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | DORCAN SOUTH
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | QUARRY ROAD
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | TOOTHILL
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | WROUGHTON
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | BEMERTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | HOMINGTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | NETHERHAMPTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | PETERSFINGER
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | REDLYNCH
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | STAPLEFORD
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | TEFFONT
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | TISBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | ENFORD
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | PARK HOUSE
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | PEWSEY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | ALDERTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | CALNE
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | COCKLEBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | LYNEHAM
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | MALMESBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | ROWDEN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | TETBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | YATTON KEYNALL
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | BRUTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | CODFORD
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | CROCKERTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | FROME
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | HAWKERIDGE
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | HOLWELL
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | WARMINSTER
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | WESTBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | ASHTON PARK
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | BROMHAM
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | CORSHAM
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | DEVIZES
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | EASTERTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | TIDWORTH
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE
Swindon and Wiltshire | Wiltshire | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Swindon and Wiltshire | Wiltshire | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Swindon and Wiltshire | Wiltshire | MINETY GSP | SWINDON BSP | SWINDON
Swindon and Wiltshire | Wiltshire | MINETY GSP | SWINDON BSP | WOOTTON BASSETT
Swindon and Wiltshire | Wiltshire | MINETY GSP | TOOTHILL BSP | CHISLEDON
Swindon and Wiltshire | Wiltshire | MINETY GSP | TOOTHILL BSP | TOOTHILL
Swindon and Wiltshire | Wiltshire | MINETY GSP | TOOTHILL BSP | WROUGHTON
Swindon and Wiltshire | Wiltshire | NURSLING GSP | ROWNHAMS | ROMSEY
Swindon and Wiltshire | Wiltshire | NURSLING GSP | WINCHESTER | DUNBRIDGE
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | EASTHAMPSTEAD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM
Thames Valley Berkshire | Bracknell Forest | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Thames Valley Berkshire | Bracknell Forest | LALEHAM | STAINES | EGHAM
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | KIDMORE END
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | READING
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | SILVER STREET
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING TOWN BSP | THE MALL
Thames Valley Berkshire | Reading | MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN
Thames Valley Berkshire | Reading | MINETY GSP | CIRENCESTER BSP | WHITEWAY
Thames Valley Berkshire | Slough | IVER 132KV | CHALVEY BSP | CHALVEY
Thames Valley Berkshire | Slough | IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE
Thames Valley Berkshire | Slough | IVER 132KV | LONGFORD | POYLE
Thames Valley Berkshire | Slough | IVER 132KV | SLOUGH | FARNHAM ROYAL
Thames Valley Berkshire | Slough | IVER 132KV | SLOUGH | TAPLOW
Thames Valley Berkshire | Slough | IVER 132KV | UPTON BSP | SUTTON LANE
Thames Valley Berkshire | Slough | IVER 132KV | UPTON BSP | UPTON
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON
Thames Valley Berkshire | West Berkshire | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
Thames Valley Berkshire | West Berkshire | COWLEY GSP | DRAYTON BSP | CHOLSEY
Thames Valley Berkshire | West Berkshire | COWLEY GSP | DRAYTON BSP | WANTAGE
Thames Valley Berkshire | West Berkshire | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Thames Valley Berkshire | West Berkshire | MINETY GSP | CIRENCESTER BSP | WHITEWAY
Thames Valley Berkshire | Windsor and Maidenhead | AMERSHAM | LOUDWATER BSP | WELL END
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | READING BSP | HENLEY
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | READING BSP | TWYFORD
Thames Valley Berkshire | Windsor and Maidenhead | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Thames Valley Berkshire | Windsor and Maidenhead | COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | CHALVEY BSP | CHALVEY
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | LONGFORD | POYLE
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | SLOUGH | TAPLOW
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | UPTON BSP | SUTTON LANE
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | UPTON BSP | UPTON
Thames Valley Berkshire | Windsor and Maidenhead | LALEHAM | STAINES | CAUSEWAY
Thames Valley Berkshire | Windsor and Maidenhead | LALEHAM | STAINES | EGHAM
Thames Valley Berkshire | Wokingham | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | HENLEY
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | READING
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | SILVER STREET
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | TWYFORD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM
Thames Valley Berkshire | Wokingham | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Thames Valley Berkshire | Wokingham | MINETY GSP | CIRENCESTER BSP | WHITEWAY
West of England | Bath and North East Somerset | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
West of England | Bath and North East Somerset | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
West of England | South Gloucestershire | MELKSHAM GSP | CHIPPENHAM | ALDERTON
West of England | South Gloucestershire | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
| Data Centre ESA | BRAMLEY (FLEE) | READING BSP | HENLEY
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Solent | Southampton | FAWLEY GSP | LANGLEY BSP | BUTTS ASH
| BSP ESA | MELKSHAM GSP | FROME BSP | FROME
| BSP ESA | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | Cherwell | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
Oxfordshire LEP | Cherwell | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | Cherwell | COWLEY GSP | WITNEY BSP | WINDRUSH PARK

## EISD
| GSPs in November 2022 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Acton Lane | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Amersham Main | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Axminster | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Botley Wood | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Bramley | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Chickerell | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Cowley | 2029 | Under active review | 2029 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Ealing | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| East Claydon | 2034 | Under active review | 2034 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Fawley | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Fleet | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Iver | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Laleham | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Lovedean | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Mannington | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Melksham | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Minety | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| North Hyde | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Nursling | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Tynemouth | 2032 | Under active review | 2032 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Willesden | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.nationalgrid.com/electricity-transmission/connections/regional-customer-connections-update
2023-01-31 | Transmission Owner's freeze date
Southern Electric Power Distribution | DNO Licence area
NGET | Transmision Owner providing
2023-03-01 | Last update (version, date)
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 For storage, both the demand and generation EISDs may be relevant.
3 Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
4 Where the tranmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
5 The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
6 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
7 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.

## Do not delete (hidden)
6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70